## Info
Date: | 2017-02-16
Time: | 10:09
Program Version: | MIDAS.exe Ver. 2.124.0.680
File Name: | CLT_Room_Test_1-1
Test Series information: | Furnished room witth 3 layers of type X gypsum on all walls and ceiling. The compartment had a rough opening in Wall W2 (front) of 1.8 m wide x 2.0 m high.
Hardware Configuration: | NRCC_TallWoodBuildings_PhaseII_20170215-TEST-1-1.xlsx

## Channels
Index | Legend/ID | Range/Type | Scaled Units | Notes
0 | TC_Ceiling_Center_020 | Thermocouple | °C | At the centre of the ceiling in panel 20 mm from interface
1 | TC_Ceiling_Center_035 | Thermocouple | °C | At the centre of the ceiling in panel 35 mm from interface
2 | TC_Ceiling_Center_050 | Thermocouple | °C | At the centre of the ceiling in panel 50 mm from interface
3 | TC_Ceiling_Center_065 | Thermocouple | °C | At the centre of the ceiling in panel 65 mm from interface
4 | TC_Ceiling_Center_090 | Thermocouple | °C | At the centre of the ceiling in panel 90 mm from interface
5 | TC_Ceiling_Center_115 | Thermocouple | °C | At the centre of the ceiling in panel 115 mm from interface
6 | TC_Ceiling_Center_140 | Thermocouple | °C | At the centre of the ceiling in panel 140 mm from interface
7 | TC_W3_Middle_180_020 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 20 mm from interface
8 | TC_W3_Middle_180_035 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 35 mm from interface
9 | TC_W3_Middle_180_050 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 50 mm from interface
10 | TC_W3_Middle_180_065 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 65 mm from interface
11 | TC_W3_Middle_180_090 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 90 mm from interface
12 | TC_W3_Middle_180_115 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 115 mm from interface
13 | TC_W3_Middle_180_140 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 140 mm from interface
14 | TC_W3_Middle_060_CLT | Thermocouple | °C | W3 on the surface of CLT
15 | TC_W3_Middle_120_CLT | Thermocouple | °C | W3 on the surface of CLT
16 | TC_W3_Middle_180_CLT | Thermocouple | °C | W3 on the surface of CLT
17 | TC_W3_Middle_060_1GB | Thermocouple | °C | W3 on the surface of 1st GB
18 | TC_W3_Middle_120_1GB | Thermocouple | °C | W3 on the surface of 1st GB
19 | TC_W3_Middle_180_1GB | Thermocouple | °C | W3 on the surface of 1st GB
20 | TC_W3_Middle_060_2GB | Thermocouple | °C | W3 on the surface of 2nd GB
21 | TC_W3_Middle_120_2GB | Thermocouple | °C | W3 on the surface of 2nd GB
22 | TC_W3_Middle_180_2GB | Thermocouple | °C | W3 on the surface of 2nd GB
23 | TC_Ceiling_Tr4_CLT | Thermocouple | °C | Ceiling above Tr4 on the surface of CLT
24 | TC_Ceiling_Tr4_1GB | Thermocouple | °C | Ceiling above Tr4 on the surface of 1st GB
25 | TC_Ceiling_Tr4_2GB | Thermocouple | °C | Ceiling above Tr4 on the surface of 2nd GB
26 | STE_6 | Thermocouple | °C | 12" below ceiling (see "Drawings")
27 | STE_10 | Thermocouple | °C | 12" below ceiling (see "Drawings")
28 | TC_V_c | Thermocouple | °C | Temperature co-located with V_c
29 | TC_Ceiling_Tr3_CLT | Thermocouple | °C | Ceiling above Tr3 on the surface of CLT
30 | TC_Ceiling_Tr3_1GB | Thermocouple | °C | Ceiling above Tr3 on the surface of 1st GB
31 | TC_Ceiling_Tr3_2GB | Thermocouple | °C | Ceiling above Tr3 on the surface of 2nd GB
32 | TC_Ceiling_Center_CLT | Thermocouple | °C | Ceiling at the centre on the surface of CLT
33 | TC_Ceiling_Center_1GB | Thermocouple | °C | Ceiling at the centre on the surface of 1st GB
34 | TC_Ceiling_Center_2GB | Thermocouple | °C | Ceiling at the centre on the surface of 2nd GB
35 | DFT_W3_Middle_180_Px | Thermocouple | °C | DFT on W3 at the mid length at h=1.8 m (Back plate)
36 | PT_Ceiling_Center_SPy | Thermocouple | °C | Temperature for plate thermometer
37 | DFT_Ceiling_Center_Px | Thermocouple | °C | DFT at the centre of the ceiling (Back plate)
38 | PT_Ceiling_Center_SPx | Thermocouple | °C | At the centre of the ceiling
39 | STE_5 | Thermocouple | °C | 12" below ceiling (see "Drawings")
40 | STE_9 | Thermocouple | °C | 12" below ceiling (see "Drawings")
41 | DFT_W3_Middle_180_Py | Thermocouple | °C | DFT on W3 at the mid length at h=1.8 m (Front plate)
42 | DFT_Ceiling_Center_Py | Thermocouple | °C | DFT at the centre of the ceiling (Front plate)
43 | Door_TC_1 | Thermocouple | °C | At the centreline of the opening
44 | Door_TC_2 | Thermocouple | °C | At the centreline of the opening
45 | Door_TC_3 | Thermocouple | °C | At the centreline of the opening
46 | Door_TC_4 | Thermocouple | °C | At the centreline of the opening
47 | Door_TC_5 | Thermocouple | °C | At the centreline of the opening
48 | Door_TC_6 | Thermocouple | °C | At the centreline of the opening
49 | Door_TC_7 | Thermocouple | °C | At the centreline of the opening
50 | PT_Front_a480_SPy | Thermocouple | °C | Facing the centre of the opening (offset 150 from centerline)
51 | PT_Front_a480_SPx | Thermocouple | °C | Facing the centre of the opening (offset 150 from centerline)
52 | PT_Front_a240_SPy | Thermocouple | °C | Facing the centre of the opening (offset 150 from centerline)
53 | PT_Front_a240_SPx | Thermocouple | °C | Facing the centre of the opening (offset 150 from centerline)
54 | TC_Smoke | Thermocouple | °C | Gas temperature at SMOKE2 outflow (for shutoff)
55 | TC_HFGtower | Thermocouple | °C | H2O outflow temperatures of heat flux gages on roof tower
56 | TC_HFGfloor | Thermocouple | °C | H2O outflow temperatures of heat flux gages on floor
57 | TC_HFGw1 | Thermocouple | °C | H2O outflow temperatures of heat flux gages on W1
58 | TC_GoPro | Thermocouple | °C | H2O outflow temperatures of GoPro water bath
59 | TC_TreeSteel | Thermocouple | °C | Temperature of steel behind thermal insulation in Tree 03 at 2.1 m height
60 | TC_TBD | Thermocouple | °C | Extra TC location TBD
61 | dP_c | ±10V default | Pa | 5/8" diameter bidirectional probe on ceiling near STE 6, Direction normal to the opening
62 | dP_o1 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (low, long side)
63 | dP_o2 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (low, middle)
64 | dP_o3 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (low, short side)
65 | dP_o4 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (high, long side)
66 | dP_o5 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (high, middle)
67 | dP_o6 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (high, short side)
68 | dP_r | ±10V default | Pa | On smoke sample line near gas analyzer sample line at 2.1m 1/4" SS tube
69 | Gardon_Front_a480 | ±0.2V default | kW/m2 | facing the centre of the opening
70 | Gardon_Front_a240 | ±0.2V default | kW/m2 | facing the centre of the opening
71 | Gardon_Floor_Center | ±0.2V default | kW/m2 | At the center of the floor
72 | SmokeAlarm | ±10V default | V | Smoke detector at the centre of the ceiling
73 | HeatAlarm | ±10V default | V | Heat detector at the centre of the ceiling
74 | SMOKE | ±10V default | V | at the centre of the room, 1.6 m high
75 | TC_W1_Middle_180_020 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 20 mm from interface
76 | TC_W1_Middle_180_035 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 35 mm from interface
77 | TC_W1_Middle_180_050 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 50 mm from interface
78 | TC_W1_Middle_180_065 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 65 mm from interface
79 | TC_W1_Middle_180_090 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 90 mm from interface
80 | TC_W1_Middle_180_115 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 115 mm from interface
81 | TC_W1_Middle_180_140 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 140 mm from interface
82 | TC_W4_Middle_180_020 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 20 mm from interface
83 | TC_W4_Middle_180_035 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 35 mm from interface
84 | TC_W4_Middle_180_050 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 50 mm from interface
85 | TC_W4_Middle_180_065 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 65 mm from interface
86 | TC_W4_Middle_180_090 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 90 mm from interface
87 | TC_W4_Middle_180_115 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 115 mm from interface
88 | TC_W4_Middle_180_140 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 140 mm from interface
89 | Roof_TC_350 | Thermocouple | °C | 3.5 m above ground
90 | Roof_TC_450 | Thermocouple | °C | 4.5 m above ground
91 | Roof_TC_550 | Thermocouple | °C | 5.5 m above ground
92 | Roof_TC_650 | Thermocouple | °C | 6.5 m above ground
93 | Roof_TC_750 | Thermocouple | °C | 7.5 m above ground
94 | PT_Front_e350_SPx | Thermocouple | °C | 3.5 m above ground
95 | PT_Front_e550_SPx | Thermocouple | °C | 5.5 m above the top of the opening
96 | TC_W4_Middle_060_CLT | Thermocouple | °C | W4 on the surface of CLT
97 | TC_W4_Middle_120_CLT | Thermocouple | °C | W4 on the surface of CLT
98 | TC_W4_Middle_180_CLT | Thermocouple | °C | W4 on the surface of CLT
99 | TC_W4_Middle_060_1GB | Thermocouple | °C | W4 on the surface of 1st GB
100 | TC_W4_Middle_120_1GB | Thermocouple | °C | W4 on the surface of 1st GB
101 | TC_W4_Middle_180_1GB | Thermocouple | °C | W4 on the surface of 1st GB
102 | TC_W4_Middle_060_2GB | Thermocouple | °C | W4 on the surface of 2nd GB
103 | TC_W4_Middle_120_2GB | Thermocouple | °C | W4 on the surface of 2nd GB
104 | TC_W4_Middle_180_2GB | Thermocouple | °C | W4 on the surface of 2nd GB
105 | DFT_W4_Middle_180_Px | Thermocouple | °C | DFT on W4 at the mid length at h=1.8 m (Front plate)
106 | STE_7 | Thermocouple | °C | 12" below ceiling (see "Drawings")
107 | STE_8 | Thermocouple | °C | 18" below ceiling (see "Drawings")
108 | DFT_W4_Middle_180_Py | Thermocouple | °C | DFT on W4 at the mid length at h=1.8 m (Back plate)
109 | Gardon_Front_e350 | ±0.2V default | kW/m2 | 3.5 m above ground
110 | Gardon_Front_e550 | ±0.2V default | kW/m2 | 5.5 m above ground
111 | TC_W1_Front_180_CLT | Thermocouple | °C | W1 at the front at h=1.8 m on the surface of CLT
112 | TC_W1_Front_180_1GB | Thermocouple | °C | W1 at the front at h=1.8 m on the surface of 1st GB
113 | TC_W1_Front_180_2GB | Thermocouple | °C | W1 at the front at h=1.8 m on the surface of 2st GB
114 | TC_W1_Front_060_CLT | Thermocouple | °C | W1 at the front at h=0.6 m on the surface of CLT
115 | TC_W1_Front_060_1GB | Thermocouple | °C | W1 at the front at h=0.6 m on the surface of 1st GB
116 | TC_W1_Front_060_2GB | Thermocouple | °C | W1 at the front at h=0.6 m on the surface of 2st GB
117 | TC_Ceiling_Tr1_CLT | Thermocouple | °C | ceiling above Tr1 on the surface of CLT
118 | TC_Ceiling_Tr1_1GB | Thermocouple | °C | ceiling above Tr1 on the surface of 1st GB
119 | TC_Ceiling_Tr1_2GB | Thermocouple | °C | ceiling above Tr1 on the surface of 2nd GB
120 | TC_Ceiling_Tr2_CLT | Thermocouple | °C | ceiling above Tr2 on the surface of CLT
121 | TC_Ceiling_Tr2_1GB | Thermocouple | °C | ceiling above Tr2 on the surface of 1st GB
122 | TC_Ceiling_Tr2_2GB | Thermocouple | °C | ceiling above Tr2 on the surface of 2nd GB
123 | STE_1 | Thermocouple | °C | 12" below ceiling (see "Drawings")
124 | STE_2 | Thermocouple | °C | 12" below ceiling (see "Drawings")
125 | STE_3 | Thermocouple | °C | 12" below ceiling (see "Drawings")
126 | STE_4 | Thermocouple | °C | 18" below ceiling (see "Drawings")
127 | PT_W1_Middle_180_SPy | Thermocouple | °C | Temperature for plate thermometer on W1 at the mid length at h=1.8 m
128 | DFT_W1_Middle_180_Px | Thermocouple | °C | DFT on W1 at the mid length at h=1.8 m (Front plate)
129 | PT_W1_Middle_180_SPx | Thermocouple | °C | W1 at the mid length at h=1.8 m (SP model 5928060-001)
130 | PT_W1_Front_180_SPy | Thermocouple | °C | Temperature for plate thermometer on W1 at front
131 | PT_W1_Front_180_SPx | Thermocouple | °C | W1 in the front of the compartment at h=1.8 m
132 | PT_W1_Rear_180_SPy | Thermocouple | °C | Temperature for plate thermometer on W1 in the rear of the compartment at h=1.8 m
133 | PT_W1_Rear_180_SPx | Thermocouple | °C | W1 in the rear of the compartment at h=1.8 m
134 | PT_Ceiling_Bed_SPy | Thermocouple | °C | Temperature for plate thermometer on ceiling above the bed
135 | DFT_Ceiling_Bed_Px | Thermocouple | °C | DFT on the ceiling above the bed (Back plate)
136 | PT_Ceiling_Bed_SPx | Thermocouple | °C | on the ceiling above the bed
137 | DFT_W1_Middle_180_Py | Thermocouple | °C | Temperature for plate thermometer on W1 at the mid length at h=1.8 m
138 | DFT_Ceiling_Bed_Py | Thermocouple | °C | DFT on the ceiling above the bed (Front plate)
139 | TC_W1_Middle_060_CLT | Thermocouple | °C | W1 at the mid length at h=0.6 m on the surface of CLT
140 | TC_W1_Middle_120_CLT | Thermocouple | °C | W1 at the mid length at h=1.2 m on the surface of CLT
141 | TC_W1_Middle_180_CLT | Thermocouple | °C | W1 at the mid length at h=1.8 m on the surface of CLT
142 | TC_W1_Middle_060_1GB | Thermocouple | °C | W1 at the mid length at h=0.6 m on the surface of 1st GB
143 | TC_W1_Middle_120_1GB | Thermocouple | °C | W1 at the mid length at h=1.2 m on the surface of 1st GB
144 | TC_W1_Middle_180_1GB | Thermocouple | °C | W1 at the mid length at h=1.8 m on the surface of 1st GB
145 | TC_W1_Middle_060_2GB | Thermocouple | °C | W1 at the mid length at h=0.6 m on the surface of 2nd GB
146 | TC_W1_Middle_120_2GB | Thermocouple | °C | W1 at the mid length at h=1.2 m on the surface of 2nd GB
147 | TC_W1_Middle_180_2GB | Thermocouple | °C | W1 at the mid length at h=1.8 m on the surface of 2nd GB
148 | TC_W1_Rear_180_CLT | Thermocouple | °C | W1 at the rear at h=1.8 m on the surface of CLT
149 | TC_W1_Rear_180_1GB | Thermocouple | °C | W1 at the rear at h=1.8 m on the surface of 1st GB
150 | TC_W1_Rear_180_2GB | Thermocouple | °C | W1 at the rear at h=1.8 m on the surface of 2st GB
151 | TC_W1_Rear_060_CLT | Thermocouple | °C | W1 at the rear at h=0.6 m on the surface of CLT
152 | TC_W1_Rear_060_1GB | Thermocouple | °C | W1 at the rear at h=0.6 m on the surface of 1st GB
153 | TC_W1_Rear_060_2GB | Thermocouple | °C | W1 at the rear at h=0.6 m on the surface of 2st GB
154 | TC_Tree_Tr1_060 | Thermocouple | °C | Tree Tr1 at h=0.6 m
155 | TC_Tree_Tr1_160 | Thermocouple | °C | Tree Tr1 at h=1.6 m
156 | TC_Tree_Tr1_260 | Thermocouple | °C | Tree Tr1 at h=2.6 m
157 | TC_Tree_Tr2_060 | Thermocouple | °C | Tree Tr2 at h=0.6 m
158 | TC_Tree_Tr2_160 | Thermocouple | °C | Tree Tr2 at h=1.6 m
159 | TC_Tree_Tr2_260 | Thermocouple | °C | Tree Tr2 at h=2.6 m
160 | TC_Tree_Tr5_060 | Thermocouple | °C | Tree Tr5 at h=0.6 m
161 | TC_Tree_Tr5_160 | Thermocouple | °C | Tree Tr5 at h=1.6 m
162 | TC_Tree_Tr5_260 | Thermocouple | °C | Tree Tr5 at h=2.6 m
163 | TC_Tree_Tr1_110 | Thermocouple | °C | Tree Tr1 at h=1.1 m
164 | TC_Tree_Tr1_210 | Thermocouple | °C | Tree Tr1 at h=2.1 m
165 | TC_Tree_Tr2_110 | Thermocouple | °C | Tree Tr2 at h=1.1 m
166 | TC_Tree_Tr2_210 | Thermocouple | °C | Tree Tr2 at h=2.1 m
167 | TC_Tree_Tr5_110 | Thermocouple | °C | Tree Tr5 at h=1.1 m
168 | TC_Tree_Tr5_210 | Thermocouple | °C | Tree Tr5 at h=2.1 m
169 | TC_Tree_Tr3_060 | Thermocouple | °C | Tree Tr3 at h=0.6 m
170 | TC_Tree_Tr3_160 | Thermocouple | °C | Tree Tr3 at h=1.6 m
171 | TC_Tree_Tr3_260 | Thermocouple | °C | Tree Tr3 at h=2.6 m
172 | TC_Tree_Tr4_060 | Thermocouple | °C | Tree Tr4 at h=0.6 m
173 | TC_Tree_Tr4_160 | Thermocouple | °C | Tree Tr4 at h=1.6 m
174 | TC_Tree_Tr4_260 | Thermocouple | °C | Tree Tr4 at h=2.6 m
175 | TC_Tree_Tr6_060 | Thermocouple | °C | Tree Tr6 at h=0.6 m
176 | TC_Tree_Tr6_160 | Thermocouple | °C | Tree Tr6 at h=1.6 m
177 | TC_Tree_Tr6_260 | Thermocouple | °C | Tree Tr6 at h=2.6 m
178 | TC_Tree_Tr3_110 | Thermocouple | °C | Tree Tr3 at h=1.1 m
179 | TC_Tree_Tr3_210 | Thermocouple | °C | Tree Tr3 at h=2.1 m
180 | TC_Tree_Tr4_110 | Thermocouple | °C | Tree Tr4 at h=1.1 m
181 | TC_Tree_Tr4_210 | Thermocouple | °C | Tree Tr4 at h=2.1 m
182 | TC_Tree_Tr6_110 | Thermocouple | °C | Tree Tr6 at h=1.1 m
183 | TC_Tree_Tr6_210 | Thermocouple | °C | Tree Tr6 at h=2.1 m
184 | Gardon_W1_Middle_180 | ±0.2V default | kW/m2 | W1 at the mid length at h=1.8 m
185 | O2_room | ±10V default | % | At the centre of the room, 2.1 m high
186 | CO2_room | ±10V default | % | At the centre of the room, 2.1 m high
187 | CO_room | ±10V default | % | At the centre of the room, 2.1 m high
188 | DEWpt_rack | ±10V default | °C | Gas rack dew point measurement
189 | VI | ±10V default | V | Internal heartbeat
190 | HRR | N/A | kW | globdata(r,HRR) [!!! updated from "86: HRR (kW)" on BONICHI on 03/07/2018 by MSH]
191 | HRRburner | N/A | kW | globdata(r,HRRburner) [!!! updated from "85: HRRburner (kW)" on BONICHI on 03/07/2018 by MSH]
192 | VelCeiling | N/A | m/s | sign(scaledata(r,dP_c))*1/1.08*(2*abs(scaledata(r,dP_c))*(scaledata(r,TC_V_c)+273.15)/353.06)^(1/2)
193 | VelDoor1 | N/A | m/s | sign(scaledata(r,dP_o1))*1/1.08*(2*abs(scaledata(r,dP_o1))*(scaledata(r,Door_TC_2)+273.15)/353.06)^(1/2)
194 | VelDoor2 | N/A | m/s | sign(scaledata(r,dP_o2))*1/1.08*(2*abs(scaledata(r,dP_o2))*(scaledata(r,Door_TC_2)+273.15)/353.06)^(1/2)
195 | VelDoor3 | N/A | m/s | sign(scaledata(r,dP_o3))*1/1.08*(2*abs(scaledata(r,dP_o3))*(scaledata(r,Door_TC_2)+273.15)/353.06)^(1/2)
196 | VelDoor4 | N/A | m/s | sign(scaledata(r,dP_o4))*1/1.08*(2*abs(scaledata(r,dP_o4))*(scaledata(r,Door_TC_6)+273.15)/353.06)^(1/2)
197 | VelDoor5 | N/A | m/s | sign(scaledata(r,dP_o5))*1/1.08*(2*abs(scaledata(r,dP_o5))*(scaledata(r,Door_TC_6)+273.15)/353.06)^(1/2)
198 | VelDoor6 | N/A | m/s | sign(scaledata(r,dP_o6))*1/1.08*(2*abs(scaledata(r,dP_o6))*(scaledata(r,Door_TC_6)+273.15)/353.06)^(1/2)
199 | HFPT_W1_Mid_180 | N/A | kW/m^2 | globdata(r,HFPT_W1_Mid_180)
200 | HFPT_W1_Front_180 | N/A | kW/m^2 | globdata(r,HFPT_W1_Front_180)
201 | HFPT_W1_Rear_180 | N/A | kW/m^2 | globdata(r,HFPT_W1_Rear_180)
202 | HFPT_Front_e350 | N/A | kW/m^2 | globdata(r,HFPT_Front_e350)
203 | HFPT_Front_e550 | N/A | kW/m^2 | globdata(r,HFPT_Front_e550)

## User Events
Event Count | Time (s) | Time Stamp | Event Description
1 | 0 | 2017-02-16 10:30 | Ignition
2 | 890 | 2017-02-16 10:44 | Room Flashover
3 | 8036 | 2017-02-16 12:44 | Start fire hose suppression
4 | 8102 | 2017-02-16 12:45 | Fire Out