## Info
Date: | 2017-03-16
Time: | 10:20
Program Version: | MIDAS.exe Ver. 2.124.0.680
File Name: | CLT_Room_Test_1-3
Test Series information: | Furnished room witth 2 layers of type X gypsum on all walls and 3 layers on ceiling. Wall 1 is exposed CLT. The compartment had a rough opening in Wall W2 (front) of 3.6 m wide x 2.0 m high.
Hardware Configuration: | NRCC_TallWoodBuildings_PhaseII_20170310-TEST-1-3.xlsx

## Channels
Index | Legend/ID | Range/Type | Scaled Units | Notes
0 | TC_Ceiling_Center_020 | Thermocouple | °C | At the centre of the ceiling in panel 20 mm from interface
1 | TC_Ceiling_Center_035 | Thermocouple | °C | At the centre of the ceiling in panel 35 mm from interface
2 | TC_Ceiling_Center_050 | Thermocouple | °C | At the centre of the ceiling in panel 50 mm from interface
3 | TC_Ceiling_Center_065 | Thermocouple | °C | At the centre of the ceiling in panel 65 mm from interface
4 | TC_Ceiling_Center_090 | Thermocouple | °C | At the centre of the ceiling in panel 90 mm from interface
5 | TC_Ceiling_Center_115 | Thermocouple | °C | At the centre of the ceiling in panel 115 mm from interface
6 | TC_Ceiling_Center_140 | Thermocouple | °C | At the centre of the ceiling in panel 140 mm from interface
7 | TC_W3_Middle_180_020 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 20 mm from interface
8 | TC_W3_Middle_180_035 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 35 mm from interface
9 | TC_W3_Middle_180_050 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 50 mm from interface
10 | TC_W3_Middle_180_065 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 65 mm from interface
11 | TC_W3_Middle_180_090 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 90 mm from interface
12 | TC_W3_Middle_180_115 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 115 mm from interface
13 | TC_W3_Middle_180_140 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 140 mm from interface
14 | TC_W3_Middle_060_CLT | Thermocouple | °C | W3 on the surface of CLT
15 | TC_W3_Middle_120_CLT | Thermocouple | °C | W3 on the surface of CLT
16 | TC_W3_Middle_180_CLT | Thermocouple | °C | W3 on the surface of CLT
17 | TC_W3_Middle_060_1GB | Thermocouple | °C | W3 on the surface of 1st GB
18 | TC_W3_Middle_120_1GB | Thermocouple | °C | W3 on the surface of 1st GB
19 | TC_W3_Middle_180_1GB | Thermocouple | °C | W3 on the surface of 1st GB
20 | TC_W3_Middle_060_2GB | Thermocouple | °C | W3 on the surface of 2nd GB
21 | TC_W3_Middle_120_2GB | Thermocouple | °C | W3 on the surface of 2nd GB
22 | TC_W3_Middle_180_2GB | Thermocouple | °C | W3 on the surface of 2nd GB
23 | TC_Ceiling_Tr4_CLT | Thermocouple | °C | Ceiling above Tr4 on the surface of CLT
24 | TC_Ceiling_Tr4_1GB | Thermocouple | °C | Ceiling above Tr4 on the surface of 1st GB
25 | TC_Ceiling_Tr4_2GB | Thermocouple | °C | Ceiling above Tr4 on the surface of 2nd GB
26 | STE_6 | Thermocouple | °C | 12" below ceiling (see "Drawings")
27 | STE_10 | Thermocouple | °C | 12" below ceiling (see "Drawings")
28 | TC_V_c | Thermocouple | °C | Temperature co-located with V_c
29 | TC_Ceiling_Tr3_CLT | Thermocouple | °C | Ceiling above Tr3 on the surface of CLT
30 | TC_Ceiling_Tr3_1GB | Thermocouple | °C | Ceiling above Tr3 on the surface of 1st GB
31 | TC_Ceiling_Tr3_2GB | Thermocouple | °C | Ceiling above Tr3 on the surface of 2nd GB
32 | TC_Ceiling_Center_CLT | Thermocouple | °C | Ceiling at the centre on the surface of CLT
33 | TC_Ceiling_Center_1GB | Thermocouple | °C | Ceiling at the centre on the surface of 1st GB
34 | TC_Ceiling_Center_2GB | Thermocouple | °C | Ceiling at the centre on the surface of 2nd GB
35 | PT_W3_Middle_180_SPx | Thermocouple | °C | Plate thermometer on W3 at the mid length at h=1.8 m
36 | PT_Ceiling_Center_SPy | Thermocouple | °C | Temperature for plate thermometer at the centre of the ceiling
37 | DFT_Ceiling_Center_Px | Thermocouple | °C | DFT at the centre of the ceiling (Back plate)
38 | PT_Ceiling_Center_SPx | Thermocouple | °C | Plate thermometer at the centre of the ceiling
39 | STE_5 | Thermocouple | °C | 12" below ceiling (see "Drawings")
40 | STE_9 | Thermocouple | °C | 12" below ceiling (see "Drawings")
41 | PT_W3_Middle_180_SPy | Thermocouple | °C | Temperature for plate thermometer on W3 at the mid length at h=1.8 m
42 | DFT_Ceiling_Center_Py | Thermocouple | °C | DFT at the centre of the ceiling (Front plate)
43 | Door_TC_1 | Thermocouple | °C | At the centreline of the opening
44 | Door_TC_2 | Thermocouple | °C | At the centreline of the opening
45 | Door_TC_3 | Thermocouple | °C | At the centreline of the opening
46 | Door_TC_4 | Thermocouple | °C | At the centreline of the opening
47 | Door_TC_5 | Thermocouple | °C | At the centreline of the opening
48 | Door_TC_6 | Thermocouple | °C | At the centreline of the opening
49 | Door_TC_7 | Thermocouple | °C | At the centreline of the opening
50 | PT_Front_a480_SPy | Thermocouple | °C | Facing the centre of the opening (offset 150 from centerline)
51 | PT_Front_a480_SPx | Thermocouple | °C | Facing the centre of the opening (offset 150 from centerline)
52 | PT_Front_a240_SPy | Thermocouple | °C | Facing the centre of the opening (offset 150 from centerline)
53 | PT_Front_a240_SPx | Thermocouple | °C | Facing the centre of the opening (offset 150 from centerline)
54 | TC_Smoke | Thermocouple | °C | Gas temperature at SMOKE2 outflow (for shutoff)
55 | TC_HFGtower | Thermocouple | °C | H2O outflow temperatures of heat flux gages on roof tower
56 | TC_HFGfloor | Thermocouple | °C | H2O outflow temperatures of heat flux gages on floor
57 | TC_HFGw1 | Thermocouple | °C | H2O outflow temperatures of heat flux gages on W1
58 | TC_GoPro | Thermocouple | °C | H2O outflow temperatures of GoPro water bath
59 | TC_TreeSteel | Thermocouple | °C | Temperature of steel behind thermal insulation in Tree 03 at 2.1 m height
60 | TC_TBD | Thermocouple | °C | Extra TC location TBD
61 | dP_c | ±10V default | Pa | 5/8" diameter bidirectional probe on ceiling near STE 6, Direction normal to the opening
62 | dP_o1 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (low, long side)
63 | dP_o2 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (low, middle)
64 | dP_o3 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (low, short side)
65 | dP_o4 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (high, long side)
66 | dP_o5 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (high, middle)
67 | dP_o6 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (high, short side)
68 | dP_r | ±10V default | Pa | On smoke sample line near gas analyzer sample line at 2.1m 1/4" SS tube
69 | Gardon_Front_a480 | ±0.2V default | kW/m2 | facing the centre of the opening
70 | Gardon_Front_a240 | ±0.2V default | kW/m2 | facing the centre of the opening
71 | Gardon_Floor_Center | ±0.2V default | kW/m2 | At the center of the floor
72 | SmokeAlarm | ±10V default | V | Smoke detector at the centre of the ceiling
73 | HeatAlarm | ±10V default | V | Heat detector at the centre of the ceiling
74 | SMOKE | ±10V default | V | at the centre of the room, 1.6 m high
75 | TC_W1_Middle_180_020 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 20 mm from interface
76 | TC_W1_Middle_180_035 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 35 mm from interface
77 | TC_W1_Middle_180_050 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 50 mm from interface
78 | TC_W1_Middle_180_065 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 65 mm from interface
79 | TC_W1_Middle_180_090 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 90 mm from interface
80 | TC_W1_Middle_180_115 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 115 mm from interface
81 | TC_W1_Middle_180_140 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 140 mm from interface
82 | TC_W4_Middle_180_020 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 20 mm from interface
83 | TC_W4_Middle_180_035 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 35 mm from interface
84 | TC_W4_Middle_180_050 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 50 mm from interface
85 | TC_W4_Middle_180_065 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 65 mm from interface
86 | TC_W4_Middle_180_090 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 90 mm from interface
87 | TC_W4_Middle_180_115 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 115 mm from interface
88 | TC_W4_Middle_180_140 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 140 mm from interface
89 | Roof_TC_350 | Thermocouple | °C | 3.5 m above ground
90 | Roof_TC_450 | Thermocouple | °C | 4.5 m above ground
91 | Roof_TC_550 | Thermocouple | °C | 5.5 m above ground
92 | Roof_TC_650 | Thermocouple | °C | 6.5 m above ground
93 | Roof_TC_750 | Thermocouple | °C | 7.5 m above ground
94 | PT_Front_e350_SPx | Thermocouple | °C | 3.5 m above ground
95 | PT_Front_e550_SPx | Thermocouple | °C | 5.5 m above the top of the opening
96 | TC_W4_Middle_060_CLT | Thermocouple | °C | W4 on the surface of CLT
97 | TC_W4_Middle_120_CLT | Thermocouple | °C | W4 on the surface of CLT
98 | TC_W4_Middle_180_CLT | Thermocouple | °C | W4 on the surface of CLT
99 | TC_W4_Middle_060_1GB | Thermocouple | °C | W4 on the surface of 1st GB
100 | TC_W4_Middle_120_1GB | Thermocouple | °C | W4 on the surface of 1st GB
101 | TC_W4_Middle_180_1GB | Thermocouple | °C | W4 on the surface of 1st GB
102 | TC_W4_Middle_060_2GB | Thermocouple | °C | W4 on the surface of 2nd GB
103 | TC_W4_Middle_120_2GB | Thermocouple | °C | W4 on the surface of 2nd GB
104 | TC_W4_Middle_180_2GB | Thermocouple | °C | W4 on the surface of 2nd GB
105 | PT_W4_Middle_180_SPx | Thermocouple | °C | Plate thermometer on W4 at the mid length at h=1.8 m
106 | STE_7 | Thermocouple | °C | 12" below ceiling (see "Drawings")
107 | STE_8 | Thermocouple | °C | 18" below ceiling (see "Drawings")
108 | PT_W4_Middle_180_SPy | Thermocouple | °C | Temperature for plate thermometer on W4 at the mid length at h=1.8 m
109 | Gardon_Front_e350 | ±0.2V default | kW/m2 | 3.5 m above ground
110 | Gardon_Front_e550 | ±0.2V default | kW/m2 | 5.5 m above ground
111 | TC_W1_Front_180_CLT | Thermocouple | °C | W1 at the front at h=1.8 m on the surface of CLT
112 | TC_W1_Front_180_1GB | Thermocouple | °C | W1 at the front at h=1.8 m on the surface of 1st GB
113 | TC_W1_Front_180_2GB | Thermocouple | °C | W1 at the front at h=1.8 m on the surface of 2st GB
114 | TC_W1_Front_060_CLT | Thermocouple | °C | W1 at the front at h=0.6 m on the surface of CLT
115 | TC_W1_Front_060_1GB | Thermocouple | °C | W1 at the front at h=0.6 m on the surface of 1st GB
116 | TC_W1_Front_060_2GB | Thermocouple | °C | W1 at the front at h=0.6 m on the surface of 2st GB
117 | TC_Ceiling_Tr1_CLT | Thermocouple | °C | ceiling above Tr1 on the surface of CLT
118 | TC_Ceiling_Tr1_1GB | Thermocouple | °C | ceiling above Tr1 on the surface of 1st GB
119 | TC_Ceiling_Tr1_2GB | Thermocouple | °C | ceiling above Tr1 on the surface of 2nd GB
120 | TC_Ceiling_Tr2_CLT | Thermocouple | °C | ceiling above Tr2 on the surface of CLT
121 | TC_Ceiling_Tr2_1GB | Thermocouple | °C | ceiling above Tr2 on the surface of 1st GB
122 | TC_Ceiling_Tr2_2GB | Thermocouple | °C | ceiling above Tr2 on the surface of 2nd GB
123 | STE_1 | Thermocouple | °C | 12" below ceiling (see "Drawings")
124 | STE_2 | Thermocouple | °C | 12" below ceiling (see "Drawings")
125 | STE_3 | Thermocouple | °C | 12" below ceiling (see "Drawings")
126 | STE_4 | Thermocouple | °C | 18" below ceiling (see "Drawings")
127 | PT_W1_Middle_180_SPy | Thermocouple | °C | Temperature for plate thermometer on W1 at the mid length at h=1.8 m
128 | DFT_W1_Middle_180_Px | Thermocouple | °C | DFT on W1 at the mid length at h=1.8 m (Front plate)
129 | PT_W1_Middle_180_SPx | Thermocouple | °C | Plate thermometer on W1 at the mid length at h=1.8 m
130 | PT_W1_Front_180_SPy | Thermocouple | °C | Temperature for plate thermometer on W1 at front
131 | PT_W1_Front_180_SPx | Thermocouple | °C | Plate thermometer on W1 in the front of the compartment at h=1.8 m
132 | PT_W1_Rear_180_SPy | Thermocouple | °C | Temperature for plate thermometer on W1 in the rear of the compartment at h=1.8 m
133 | PT_W1_Rear_180_SPx | Thermocouple | °C | plate thermometer on W1 in the rear of the compartment at h=1.8 m
134 | PT_Ceiling_Bed_SPy | Thermocouple | °C | Temperature for plate thermometer on ceiling above the bed
135 | DFT_Ceiling_Bed_Px | Thermocouple | °C | DFT on the ceiling above the bed (Back plate)
136 | PT_Ceiling_Bed_SPx | Thermocouple | °C | Plate thermometer on the ceiling above the bed
137 | DFT_W1_Middle_180_Py | Thermocouple | °C | DFT on W1 at the mid length at h=1.8 m
138 | DFT_Ceiling_Bed_Py | Thermocouple | °C | DFT on the ceiling above the bed (Front plate)
139 | TC_W1_Middle_060_CLT | Thermocouple | °C | W1 at the mid length at h=0.6 m on the surface of CLT
140 | TC_W1_Middle_120_CLT | Thermocouple | °C | W1 at the mid length at h=1.2 m on the surface of CLT
141 | TC_W1_Middle_180_CLT | Thermocouple | °C | W1 at the mid length at h=1.8 m on the surface of CLT
142 | TC_W1_Middle_060_1GB | Thermocouple | °C | W1 at the mid length at h=0.6 m on the surface of 1st GB
143 | TC_W1_Middle_120_1GB | Thermocouple | °C | W1 at the mid length at h=1.2 m on the surface of 1st GB
144 | TC_W1_Middle_180_1GB | Thermocouple | °C | W1 at the mid length at h=1.8 m on the surface of 1st GB
145 | TC_W1_Middle_060_2GB | Thermocouple | °C | W1 at the mid length at h=0.6 m on the surface of 2nd GB
146 | TC_W1_Middle_120_2GB | Thermocouple | °C | W1 at the mid length at h=1.2 m on the surface of 2nd GB
147 | TC_W1_Middle_180_2GB | Thermocouple | °C | W1 at the mid length at h=1.8 m on the surface of 2nd GB
148 | TC_W1_Rear_180_CLT | Thermocouple | °C | W1 at the rear at h=1.8 m on the surface of CLT
149 | TC_W1_Rear_180_1GB | Thermocouple | °C | W1 at the rear at h=1.8 m on the surface of 1st GB
150 | TC_W1_Rear_180_2GB | Thermocouple | °C | W1 at the rear at h=1.8 m on the surface of 2st GB
151 | TC_W1_Rear_060_CLT | Thermocouple | °C | W1 at the rear at h=0.6 m on the surface of CLT
152 | TC_W1_Rear_060_1GB | Thermocouple | °C | W1 at the rear at h=0.6 m on the surface of 1st GB
153 | TC_W1_Rear_060_2GB | Thermocouple | °C | W1 at the rear at h=0.6 m on the surface of 2st GB
154 | TC_Tree_Tr1_060 | Thermocouple | °C | Tree Tr1 at h=0.6 m
155 | TC_Tree_Tr1_160 | Thermocouple | °C | Tree Tr1 at h=1.6 m
156 | TC_Tree_Tr1_260 | Thermocouple | °C | Tree Tr1 at h=2.6 m
157 | TC_Tree_Tr2_060 | Thermocouple | °C | Tree Tr2 at h=0.6 m
158 | TC_Tree_Tr2_160 | Thermocouple | °C | Tree Tr2 at h=1.6 m
159 | TC_Tree_Tr2_260 | Thermocouple | °C | Tree Tr2 at h=2.6 m
160 | TC_Tree_Tr5_060 | Thermocouple | °C | Tree Tr5 at h=0.6 m
161 | TC_Tree_Tr5_160 | Thermocouple | °C | Tree Tr5 at h=1.6 m
162 | TC_Tree_Tr5_260 | Thermocouple | °C | Tree Tr5 at h=2.6 m
163 | TC_Tree_Tr1_110 | Thermocouple | °C | Tree Tr1 at h=1.1 m
164 | TC_Tree_Tr1_210 | Thermocouple | °C | Tree Tr1 at h=2.1 m
165 | TC_Tree_Tr2_110 | Thermocouple | °C | Tree Tr2 at h=1.1 m
166 | TC_Tree_Tr2_210 | Thermocouple | °C | Tree Tr2 at h=2.1 m
167 | TC_Tree_Tr5_110 | Thermocouple | °C | Tree Tr5 at h=1.1 m
168 | TC_Tree_Tr5_210 | Thermocouple | °C | Tree Tr5 at h=2.1 m
169 | TC_Tree_Tr3_060 | Thermocouple | °C | Tree Tr3 at h=0.6 m
170 | TC_Tree_Tr3_160 | Thermocouple | °C | Tree Tr3 at h=1.6 m
171 | TC_Tree_Tr3_260 | Thermocouple | °C | Tree Tr3 at h=2.6 m
172 | TC_Tree_Tr4_060 | Thermocouple | °C | Tree Tr4 at h=0.6 m
173 | TC_Tree_Tr4_160 | Thermocouple | °C | Tree Tr4 at h=1.6 m
174 | TC_Tree_Tr4_260 | Thermocouple | °C | Tree Tr4 at h=2.6 m
175 | TC_Tree_Tr6_060 | Thermocouple | °C | Tree Tr6 at h=0.6 m
176 | TC_Tree_Tr6_160 | Thermocouple | °C | Tree Tr6 at h=1.6 m
177 | TC_Tree_Tr6_260 | Thermocouple | °C | Tree Tr6 at h=2.6 m
178 | TC_Tree_Tr3_110 | Thermocouple | °C | Tree Tr3 at h=1.1 m
179 | TC_Tree_Tr3_210 | Thermocouple | °C | Tree Tr3 at h=2.1 m
180 | TC_Tree_Tr4_110 | Thermocouple | °C | Tree Tr4 at h=1.1 m
181 | TC_Tree_Tr4_210 | Thermocouple | °C | Tree Tr4 at h=2.1 m
182 | TC_Tree_Tr6_110 | Thermocouple | °C | Tree Tr6 at h=1.1 m
183 | TC_Tree_Tr6_210 | Thermocouple | °C | Tree Tr6 at h=2.1 m
184 | Gardon_W1_Middle_180 | ±0.2V default | kW/m2 | W1 at the mid length at h=1.8 m
185 | O2_room | ±10V default | % | At the centre of the room, 2.1 m high
186 | CO2_room | ±10V default | % | At the centre of the room, 2.1 m high
187 | CO_room | ±10V default | % | At the centre of the room, 2.1 m high
188 | DEWpt_rack | ±10V default | °C | Gas rack dew point measurement
189 | VI | ±10V default | V | Internal heartbeat
190 | HRR | N/A | kW | globdata(r,HRR) [!!! updated from "86: HRR (kW)" on BONICHI on 03/07/2018 by MSH]
191 | HRRburner | N/A | kW | globdata(r,HRRburner) [!!! updated from "85: HRRburner (kW)" on BONICHI on 03/07/2018 by MSH]
192 | VelCeiling | N/A | m/s | sign(scaledata(r,dP_c))*1/1.08*(2*abs(scaledata(r,dP_c))*(scaledata(r,TC_V_c)+273.15)/353.06)^(1/2)
193 | VelDoor1 | N/A | m/s | sign(scaledata(r,dP_o1))*1/1.08*(2*abs(scaledata(r,dP_o1))*(scaledata(r,Door_TC_2)+273.15)/353.06)^(1/2)
194 | VelDoor2 | N/A | m/s | sign(scaledata(r,dP_o2))*1/1.08*(2*abs(scaledata(r,dP_o2))*(scaledata(r,Door_TC_2)+273.15)/353.06)^(1/2)
195 | VelDoor3 | N/A | m/s | sign(scaledata(r,dP_o3))*1/1.08*(2*abs(scaledata(r,dP_o3))*(scaledata(r,Door_TC_2)+273.15)/353.06)^(1/2)
196 | VelDoor4 | N/A | m/s | sign(scaledata(r,dP_o4))*1/1.08*(2*abs(scaledata(r,dP_o4))*(scaledata(r,Door_TC_6)+273.15)/353.06)^(1/2)
197 | VelDoor5 | N/A | m/s | sign(scaledata(r,dP_o5))*1/1.08*(2*abs(scaledata(r,dP_o5))*(scaledata(r,Door_TC_6)+273.15)/353.06)^(1/2)
198 | VelDoor6 | N/A | m/s | sign(scaledata(r,dP_o6))*1/1.08*(2*abs(scaledata(r,dP_o6))*(scaledata(r,Door_TC_6)+273.15)/353.06)^(1/2)
199 | HFPT_W1_Mid_180 | N/A | kW/m^2 | globdata(r,HFPT_W1_Mid_180)
200 | HFPT_W1_Front_180 | N/A | kW/m^2 | globdata(r,HFPT_W1_Front_180)
201 | HFPT_W1_Rear_180 | N/A | kW/m^2 | globdata(r,HFPT_W1_Rear_180)
202 | HFPT_Front_e350 | N/A | kW/m^2 | globdata(r,HFPT_Front_e350)
203 | HFPT_Front_e550 | N/A | kW/m^2 | globdata(r,HFPT_Front_e550)
204 | HFPT_W3_Mid_180 | N/A | kW/m^2 | globdata(r,HFPT_W3_Mid_180)
205 | HFPT_W4_Mid_180 | N/A | kW/m^2 | globdata(r,HFPT_W4_Mid_180)

## User Events
Event Count | Time (s) | Time Stamp | Event Description
1 | 0 | 2017-03-16 10:34 | Ignition
2 | 760 | 2017-03-16 10:46 | flashover
3 | 1991 | 2017-03-16 11:07 | lost flow to the gas rack for several minutes. blow out with air to restore flow
4 | 5367 | 2017-03-16 12:03 | delamination of first layer of CLT in progress
5 | 10080 | 2017-03-16 13:22 | start of delamination on second layer of CLT
6 | 14524 | 2017-03-16 14:36 | Start water suppression
7 | 14847 | 2017-03-16 14:41 | Fire Out

## Scaled Data
Time Stamp | Time (s) | 0: TC_Ceiling_Center_020 (°C) | 1: TC_Ceiling_Center_035 (°C) | 2: TC_Ceiling_Center_050 (°C) | 3: TC_Ceiling_Center_065 (°C) | 4: TC_Ceiling_Center_090 (°C) | 5: TC_Ceiling_Center_115 (°C) | 6: TC_Ceiling_Center_140 (°C) | 7: TC_W3_Middle_180_020 (°C) | 8: TC_W3_Middle_180_035 (°C) | 9: TC_W3_Middle_180_050 (°C) | 10: TC_W3_Middle_180_065 (°C) | 11: TC_W3_Middle_180_090 (°C) | 12: TC_W3_Middle_180_115 (°C) | 13: TC_W3_Middle_180_140 (°C) | 14: TC_W3_Middle_060_CLT (°C) | 15: TC_W3_Middle_120_CLT (°C) | 16: TC_W3_Middle_180_CLT (°C) | 17: TC_W3_Middle_060_1GB (°C) | 18: TC_W3_Middle_120_1GB (°C) | 19: TC_W3_Middle_180_1GB (°C) | 20: TC_W3_Middle_060_2GB (°C) | 21: TC_W3_Middle_120_2GB (°C) | 22: TC_W3_Middle_180_2GB (°C) | 23: TC_Ceiling_Tr4_CLT (°C) | 24: TC_Ceiling_Tr4_1GB (°C) | 25: TC_Ceiling_Tr4_2GB (°C) | 26: STE_6 (°C) | 27: STE_10 (°C) | 28: TC_V_c (°C) | 29: TC_Ceiling_Tr3_CLT (°C) | 30: TC_Ceiling_Tr3_1GB (°C) | 31: TC_Ceiling_Tr3_2GB (°C) | 32: TC_Ceiling_Center_CLT (°C) | 33: TC_Ceiling_Center_1GB (°C) | 34: TC_Ceiling_Center_2GB (°C) | 35: PT_W3_Middle_180_SPx (°C) | 36: PT_Ceiling_Center_SPy (°C) | 37: DFT_Ceiling_Center_Px (°C) | 38: PT_Ceiling_Center_SPx (°C) | 39: STE_5 (°C) | 40: STE_9 (°C) | 41: PT_W3_Middle_180_SPy (°C) | 42: DFT_Ceiling_Center_Py (°C) | 43: Door_TC_1 (°C) | 44: Door_TC_2 (°C) | 45: Door_TC_3 (°C) | 46: Door_TC_4 (°C) | 47: Door_TC_5 (°C) | 48: Door_TC_6 (°C) | 49: Door_TC_7 (°C) | 50: PT_Front_a480_SPy (°C) | 51: PT_Front_a480_SPx (°C) | 52: PT_Front_a240_SPy (°C) | 53: PT_Front_a240_SPx (°C) | 54: TC_Smoke (°C) | 55: TC_HFGtower (°C) | 56: TC_HFGfloor (°C) | 57: TC_HFGw1 (°C) | 58: TC_GoPro (°C) | 59: TC_TreeSteel (°C) | 60: TC_TBD (°C) | 61: dP_c (Pa) | 62: dP_o1 (Pa) | 63: dP_o2 (Pa) | 64: dP_o3 (Pa) | 65: dP_o4 (Pa) | 66: dP_o5 (Pa) | 67: dP_o6 (Pa) | 68: dP_r (Pa) | 69: Gardon_Front_a480 (kW/m2) | 70: Gardon_Front_a240 (kW/m2) | 71: Gardon_Floor_Center (kW/m2) | 72: SmokeAlarm (V) | 73: HeatAlarm (V) | 74: SMOKE (V) | 75: TC_W1_Middle_180_020 (°C) | 76: TC_W1_Middle_180_035 (°C) | 77: TC_W1_Middle_180_050 (°C) | 78: TC_W1_Middle_180_065 (°C) | 79: TC_W1_Middle_180_090 (°C) | 80: TC_W1_Middle_180_115 (°C) | 81: TC_W1_Middle_180_140 (°C) | 82: TC_W4_Middle_180_020 (°C) | 83: TC_W4_Middle_180_035 (°C) | 84: TC_W4_Middle_180_050 (°C) | 85: TC_W4_Middle_180_065 (°C) | 86: TC_W4_Middle_180_090 (°C) | 87: TC_W4_Middle_180_115 (°C) | 88: TC_W4_Middle_180_140 (°C) | 89: Roof_TC_350 (°C) | 90: Roof_TC_450 (°C) | 91: Roof_TC_550 (°C) | 92: Roof_TC_650 (°C) | 93: Roof_TC_750 (°C) | 94: PT_Front_e350_SPx (°C) | 95: PT_Front_e550_SPx (°C) | 96: TC_W4_Middle_060_CLT (°C) | 97: TC_W4_Middle_120_CLT (°C) | 98: TC_W4_Middle_180_CLT (°C) | 99: TC_W4_Middle_060_1GB (°C) | 100: TC_W4_Middle_120_1GB (°C) | 101: TC_W4_Middle_180_1GB (°C) | 102: TC_W4_Middle_060_2GB (°C) | 103: TC_W4_Middle_120_2GB (°C) | 104: TC_W4_Middle_180_2GB (°C) | 105: PT_W4_Middle_180_SPx (°C) | 106: STE_7 (°C) | 107: STE_8 (°C) | 108: PT_W4_Middle_180_SPy (°C) | 109: Gardon_Front_e350 (kW/m2) | 110: Gardon_Front_e550 (kW/m2) | 111: TC_W1_Front_180_CLT (°C) | 112: TC_W1_Front_180_1GB (°C) | 113: TC_W1_Front_180_2GB (°C) | 114: TC_W1_Front_060_CLT (°C) | 115: TC_W1_Front_060_1GB (°C) | 116: TC_W1_Front_060_2GB (°C) | 117: TC_Ceiling_Tr1_CLT (°C) | 118: TC_Ceiling_Tr1_1GB (°C) | 119: TC_Ceiling_Tr1_2GB (°C) | 120: TC_Ceiling_Tr2_CLT (°C) | 121: TC_Ceiling_Tr2_1GB (°C) | 122: TC_Ceiling_Tr2_2GB (°C) | 123: STE_1 (°C) | 124: STE_2 (°C) | 125: STE_3 (°C) | 126: STE_4 (°C) | 127: PT_W1_Middle_180_SPy (°C) | 128: DFT_W1_Middle_180_Px (°C) | 129: PT_W1_Middle_180_SPx (°C) | 130: PT_W1_Front_180_SPy (°C) | 131: PT_W1_Front_180_SPx (°C) | 132: PT_W1_Rear_180_SPy (°C) | 133: PT_W1_Rear_180_SPx (°C) | 134: PT_Ceiling_Bed_SPy (°C) | 135: DFT_Ceiling_Bed_Px (°C) | 136: PT_Ceiling_Bed_SPx (°C) | 137: DFT_W1_Middle_180_Py (°C) | 138: DFT_Ceiling_Bed_Py (°C) | 139: TC_W1_Middle_060_CLT (°C) | 140: TC_W1_Middle_120_CLT (°C) | 141: TC_W1_Middle_180_CLT (°C) | 142: TC_W1_Middle_060_1GB (°C) | 143: TC_W1_Middle_120_1GB (°C) | 144: TC_W1_Middle_180_1GB (°C) | 145: TC_W1_Middle_060_2GB (°C) | 146: TC_W1_Middle_120_2GB (°C) | 147: TC_W1_Middle_180_2GB (°C) | 148: TC_W1_Rear_180_CLT (°C) | 149: TC_W1_Rear_180_1GB (°C) | 150: TC_W1_Rear_180_2GB (°C) | 151: TC_W1_Rear_060_CLT (°C) | 152: TC_W1_Rear_060_1GB (°C) | 153: TC_W1_Rear_060_2GB (°C) | 154: TC_Tree_Tr1_060 (°C) | 155: TC_Tree_Tr1_160 (°C) | 156: TC_Tree_Tr1_260 (°C) | 157: TC_Tree_Tr2_060 (°C) | 158: TC_Tree_Tr2_160 (°C) | 159: TC_Tree_Tr2_260 (°C) | 160: TC_Tree_Tr5_060 (°C) | 161: TC_Tree_Tr5_160 (°C) | 162: TC_Tree_Tr5_260 (°C) | 163: TC_Tree_Tr1_110 (°C) | 164: TC_Tree_Tr1_210 (°C) | 165: TC_Tree_Tr2_110 (°C) | 166: TC_Tree_Tr2_210 (°C) | 167: TC_Tree_Tr5_110 (°C) | 168: TC_Tree_Tr5_210 (°C) | 169: TC_Tree_Tr3_060 (°C) | 170: TC_Tree_Tr3_160 (°C) | 171: TC_Tree_Tr3_260 (°C) | 172: TC_Tree_Tr4_060 (°C) | 173: TC_Tree_Tr4_160 (°C) | 174: TC_Tree_Tr4_260 (°C) | 175: TC_Tree_Tr6_060 (°C) | 176: TC_Tree_Tr6_160 (°C) | 177: TC_Tree_Tr6_260 (°C) | 178: TC_Tree_Tr3_110 (°C) | 179: TC_Tree_Tr3_210 (°C) | 180: TC_Tree_Tr4_110 (°C) | 181: TC_Tree_Tr4_210 (°C) | 182: TC_Tree_Tr6_110 (°C) | 183: TC_Tree_Tr6_210 (°C) | 184: Gardon_W1_Middle_180 (kW/m2) | 185: O2_room (%) | 186: CO2_room (%) | 187: CO_room (%) | 188: DEWpt_rack (°C) | 189: VI (V) | 190: HRR (kW) | 191: HRRburner (kW) | 192: VelCeiling (m/s) | 193: VelDoor1 (m/s) | 194: VelDoor2 (m/s) | 195: VelDoor3 (m/s) | 196: VelDoor4 (m/s) | 197: VelDoor5 (m/s) | 198: VelDoor6 (m/s) | 199: HFPT_W1_Mid_180 (kW/m^2) | 200: HFPT_W1_Front_180 (kW/m^2) | 201: HFPT_W1_Rear_180 (kW/m^2) | 202: HFPT_Front_e350 (kW/m^2) | 203: HFPT_Front_e550 (kW/m^2) | 204: HFPT_W3_Mid_180 (kW/m^2) | 205: HFPT_W4_Mid_180 (kW/m^2)
42810.4311 | -773 | 18.5304 | 18.6033 | 18.6075 | 18.6384 | 18.0406 | 16.7163 | 14.8097 | 16.7766 | 17.27 | 17.3672 | 17.397 | 16.9569 | 16.0329 | 14.6594 | 14.9894 | 14.9834 | 15.5339 | 13.4195 | 13.5639 | 14.1517 |  |  |  | 16.6862 | 16.0442 | 15.1749 | 10.7351 | 10.1343 | 9.8398 | 17.2326 | 16.3599 | 15.1923 | 16.8978 | 16.2036 | 15.2294 | 11.0246 | 11.7404 |  | 12.5011 | 11.0941 | 11.0217 | 8.8192 |  | 6.2047 | 6.1732 | 5.6411 | 5.7192 | 5.7649 | 6.302 | 7.0546 | 4.3395 | 6.3921 | 4.5123 | 6.6758 | 8.1011 | 43.1279 | 47.3109 | 43.6965 | 15.3074 |  |  | 0.24401 | -0.064965 | -0.000776 | 0.15902 | 0.18678 | 0.20325 | 0.52296 | 0.42105 | -0.67272 | -0.24585 | -0.36293 | 8.8774 | 8.8785 | 2.0083 | 15.9016 | 16.7855 | 17.33 | 17.66 | 17.6322 | 16.6547 | 15.0193 | 16.9297 | 17.2559 | 17.5516 | 17.6069 | 17.3608 | 16.5974 | 14.8553 | 6.137 | 8.342 | 5.2811 | 5.7108 | 5.9943 | 6.7865 | 7.7092 | 15.95 | 15.5786 | 15.4551 | 14.4063 | 14.3048 | 14.2505 |  |  |  | 10.9826 | 9.791 | 9.2455 | 9.2263 | -0.0583 | -0.034039 | 12.9789 |  |  | 10.7997 |  |  | 16.9972 | 16.2025 | 15.2079 | 16.4995 | 15.792 | 14.9159 | 10.7909 | 11.1026 | 11.6606 | 11.6662 | 9.2532 |  | 10.9501 | 8.6953 | 10.3606 | 9.5474 | 11.3258 | 12.4846 |  | 12.5136 |  |  | 11.8692 | 12.7511 | 12.7349 | [6 empty] | 12.7057 |  |  | 11.4068 |  |  | 9.5956 | 10.5788 | 12.8416 | 7.7874 | 9.6508 | 13.1246 | 8.1412 | 9.8319 | 13.1091 | 9.4754 | 10.7494 | 7.8876 | 10.6593 | 8.6203 | 10.4158 | 7.8482 | 10.0957 | 13.6813 | 10.8006 | 10.5687 | 12.3694 | 8.1619 | 10.0022 | 13.1934 | 8.1735 | 10.771 | 9.9945 | 10.0882 | 8.4433 | 10.4822 | -0.30991 | 20.9527 | 0.034262 | 0.051598 | -38.2152 | 0.38586 | -1.25 | 0.3 | 0.5791 | -0.29687 | -0.032445 | 0.46446 | 0.50349 | 0.52521 | 0.84247 | 0.41651 | 0.41258 | 0.42073 | 0.42035 | 0.6226 | 0.43102 | 0.41833
42810.4311 | -772 | 18.5309 | 18.609 | 18.6058 | 18.6391 | 18.0403 | 16.7201 | 14.8062 | 16.7782 | 17.2663 | 17.3624 | 17.39 | 16.9595 | 16.0371 | 14.6664 | 14.9918 | 14.9859 | 15.532 | 13.4231 | 13.5601 | 14.1511 |  |  |  | 16.6795 | 16.0478 | 15.1794 | 10.7241 | 10.1309 | 9.8605 | 17.2281 | 16.3615 | 15.1819 | 16.9019 | 16.1995 | 15.2253 | 11.0215 | 11.7115 |  | 12.4927 | 11.0954 | 11.0216 | 8.8168 |  | 6.2098 | 6.1739 | 5.6429 | 5.7141 | 5.768 | 6.2983 | 7.0442 | 4.2889 | 6.398 | 4.4511 | 6.6809 | 8.0996 | 43.1022 | 47.2987 | 43.6759 | 15.2999 |  |  | 0.22955 | -0.089281 | 0.25024 | -0.033514 | 0.45226 | 0.12045 | 0.19506 | 0.10695 | -0.50419 | -1.4069 | -0.23338 | 8.8851 | 8.8866 | 2.0088 | 15.8925 | 16.7838 | 17.336 | 17.6613 | 17.6493 | 16.65 | 15.0129 | 16.9373 | 17.2716 | 17.56 | 17.5986 | 17.3594 | 16.6018 | 14.8516 | 6.0823 | 8.3494 | 5.3193 | 5.6653 | 5.9582 | 6.7871 | 7.7073 | 15.9441 | 15.5745 | 15.4602 | 14.4014 | 14.3006 | 14.2434 |  |  |  | 10.9845 | 9.7819 | 9.2431 | 9.217 | 0.076632 | -0.12268 | 12.9901 |  |  | 10.7847 |  |  | 17.0064 | 16.2187 | 15.2031 | 16.5005 | 15.7959 | 14.9305 | 10.7948 | 11.0952 | 11.6673 | 11.6635 | 9.2816 |  | 10.9579 | 8.7996 | 10.3638 | 9.5453 | 11.3151 | 12.4904 |  | 12.5241 |  |  | 11.8797 | 12.756 | 12.7476 | [6 empty] | 12.7 |  |  | 11.4013 |  |  | 9.5941 | 10.5669 | 12.8216 | 7.7681 | 9.6466 | 13.1158 | 8.1402 | 9.831 | 13.1036 | 9.4717 | 10.7396 | 7.8841 | 10.6567 | 8.6141 | 10.4165 | 7.8467 | 10.1012 | 13.6705 | 10.8061 | 10.5655 | 12.3675 | 8.1692 | 10.02 | 13.2046 | 8.1839 | 10.7678 | 9.9996 | 10.0768 | 8.4538 | 10.4945 | -0.18972 | 20.9539 | 0.033545 | 0.05107 | -38.1202 | 0.39956 | -1.34 | 0.28 | 0.5617 | -0.34802 | 0.58264 | -0.21322 | 0.78345 | 0.40431 | 0.51452 | 0.41598 | 0.40979 | 0.42044 | 0.42651 | 0.61813 | 0.43099 | 0.41865
42810.4311 | -771 | 18.5409 | 18.6166 | 18.6115 | 18.6451 | 18.0386 | 16.7224 | 14.81 | 16.7827 | 17.2722 | 17.3696 | 17.3939 | 16.9665 | 16.04 | 14.6715 | 14.9939 | 14.987 | 15.5339 | 13.4255 | 13.56 | 14.1487 |  |  |  | 16.6888 | 16.0354 | 15.1763 | 10.7215 | 10.1263 | 9.8829 | 17.2246 | 16.3564 | 15.1744 | 16.8909 | 16.1923 | 15.2189 | 11.0134 | 11.6818 |  | 12.4809 | 11.0898 | 11.0175 | 8.8325 |  | 6.2073 | 6.1677 | 5.638 | 5.712 | 5.7597 | 6.2797 | 7.0226 | 4.3 | 6.3894 | 4.4217 | 6.6674 | 8.1042 | 43.0815 | 47.2991 | 43.665 | 15.2968 |  |  | 0.1599 | 0.028343 | 0.069532 | -0.068338 | 0.37669 | -0.0228 | -0.21826 | 0.14374 | -0.28546 | 0.010527 | -0.30551 | 8.8992 | 8.9002 | 2.0086 | 15.9018 | 16.7815 | 17.3319 | 17.6688 | 17.6423 | 16.6515 | 15.018 | 16.9357 | 17.2601 | 17.5562 | 17.598 | 17.3611 | 16.597 | 14.8456 | 6.0739 | 8.3615 | 5.3063 | 5.6586 | 5.976 | 6.7857 | 7.7167 | 15.9543 | 15.5792 | 15.4567 | 14.4112 | 14.3105 | 14.2522 |  |  |  | 10.9809 | 9.7785 | 9.2473 | 9.2451 | -0.19323 | 0.019786 | 12.9877 |  |  | 10.7837 |  |  | 17.0097 | 16.2147 | 15.2167 | 16.5046 | 15.803 | 14.9264 | 10.803 | 11.098 | 11.6712 | 11.665 | 9.3163 |  | 10.9508 | 8.9012 | 10.3582 | 9.5413 | 11.31 | 12.4883 |  | 12.5154 |  |  | 11.8961 | 12.7569 | 12.7449 | [6 empty] | 12.6927 |  |  | 11.4034 |  |  | 9.5831 | 10.5627 | 12.8099 | 7.7697 | 9.6433 | 13.1122 | 8.1412 | 9.8344 | 13.0978 | 9.4701 | 10.7331 | 7.89 | 10.6464 | 8.6139 | 10.4091 | 7.8535 | 10.0998 | 13.6684 | 10.8084 | 10.5493 | 12.3569 | 8.1701 | 10.0197 | 13.2047 | 8.1861 | 10.7733 | 9.9947 | 10.0744 | 8.4599 | 10.4944 | -0.055096 | 20.9527 | 0.033814 | 0.050201 | -38.1578 | 0.41326 | -1.49 | 0.3 | 0.46882 | 0.19608 | 0.30712 | -0.30447 | 0.71498 | -0.1759 | -0.54424 | 0.41478 | 0.40678 | 0.42038 | 0.42728 | 0.62066 | 0.43029 | 0.41775
42810.4311 | -770 | 18.5415 | 18.6152 | 18.6106 | 18.6499 | 18.0362 | 16.7184 | 14.8059 | 16.7846 | 17.2744 | 17.3756 | 17.39 | 16.9613 | 16.0438 | 14.6638 | 14.9916 | 14.9899 | 15.5369 | 13.4265 | 13.5578 | 14.1513 |  |  |  | 16.6919 | 16.0356 | 15.1759 | 10.718 | 10.1197 | 9.9075 | 17.233 | 16.3635 | 15.1777 | 16.8991 | 16.1982 | 15.2226 | 11.0213 | 11.6493 |  | 12.4827 | 11.1013 | 11.0214 | 8.834 |  | 6.2115 | 6.1671 | 5.6352 | 5.7112 | 5.7586 | 6.2663 | 6.9979 | 4.3665 | 6.3933 | 4.4894 | 6.6739 | 8.1124 | 43.0704 | 47.2926 | 43.6658 | 15.2946 |  |  | -0.070093 | -0.071537 | 0.032736 | -0.04797 | -0.018236 | -0.37764 | 0.1563 | -0.14473 | -0.60733 | -0.15542 | -0.44679 | 8.8864 | 8.8873 | 2.0083 | 15.9055 | 16.7791 | 17.3276 | 17.6624 | 17.6388 | 16.6505 | 15.0191 | 16.9357 | 17.2642 | 17.5459 | 17.5956 | 17.3564 | 16.5921 | 14.8373 | 6.0585 | 8.334 | 5.3086 | 5.624 | 5.8964 | 6.7927 | 7.7078 | 15.9439 | 15.5746 | 15.4519 | 14.4054 | 14.3048 | 14.2489 |  |  |  | 10.9838 | 9.7748 | 9.2536 | 9.2821 | -0.21126 | 0.11106 | 12.9903 |  |  | 10.7788 |  |  | 17.0039 | 16.2114 | 15.2097 | 16.5049 | 15.7952 | 14.9248 | 10.8052 | 11.1009 | 11.6735 | 11.6658 | 9.3074 |  | 10.95 | 8.9488 | 10.3484 | 9.5266 | 11.3125 | 12.4933 |  | 12.5171 |  |  | 11.9065 | 12.7587 | 12.7345 | [6 empty] | 12.6921 |  |  | 11.4092 |  |  | 9.5786 | 10.5596 | 12.7986 | 7.7791 | 9.6446 | 13.1042 | 8.1346 | 9.8263 | 13.0914 | 9.4634 | 10.735 | 7.8887 | 10.6449 | 8.6161 | 10.4079 | 7.8655 | 10.0927 | 13.6657 | 10.8072 | 10.5489 | 12.3556 | 8.1574 | 10.0106 | 13.1983 | 8.1895 | 10.7753 | 9.9921 | 10.0778 | 8.4595 | 10.4919 | -0.19935 | 20.9532 | 0.034153 | 0.049543 | -38.1466 | 0.4269 | -1.39 | 0.31 | -0.31041 | -0.31152 | 0.21073 | -0.25509 | -0.15731 | -0.71587 | 0.46054 | 0.415 | 0.40513 | 0.42087 | 0.4298 | 0.61937 | 0.4305 | 0.41682
42810.4311 | -769 | 18.5404 | 18.6087 | 18.6147 | 18.6461 | 18.0402 | 16.724 | 14.8047 | 16.7812 | 17.2717 | 17.3709 | 17.394 | 16.9664 | 16.0292 | 14.6625 | 14.9983 | 14.9959 | 15.5418 | 13.4317 | 13.5613 | 14.1517 |  |  |  | 16.6885 | 16.0506 | 15.1807 | 10.7117 | 10.1167 | 9.9213 | 17.232 | 16.3623 | 15.1798 | 16.8984 | 16.1979 | 15.2268 | 11.0214 | 11.6259 |  | 12.478 | 11.1082 | 11.0194 | 8.8304 |  | 6.2068 | 6.1743 | 5.6371 | 5.7065 | 5.7538 | 6.2514 | 6.961 | 4.3295 | 6.3873 | 4.4811 | 6.666 | 8.1173 | 43.0527 | 47.2855 | 43.6561 | 15.2886 |  |  | 0.033731 | 0.046087 | 0.25484 | -0.3049 | -0.068176 | -0.53141 | 0.0689 | -0.32478 | -0.42849 | -0.43865 | -0.088728 | 8.8844 | 8.8856 | 2.0086 | 15.9131 | 16.7856 | 17.3297 | 17.6662 | 17.6445 | 16.6529 | 15.0264 | 16.9394 | 17.2625 | 17.5563 | 17.6021 | 17.3604 | 16.5934 | 14.8498 | 6.0182 | 8.3177 | 5.256 | 5.5675 | 5.8071 | 6.782 | 7.714 | 15.9559 | 15.5749 | 15.4606 | 14.3995 | 14.2947 | 14.2373 |  |  |  | 10.98 | 9.7712 | 9.2555 | 9.3244 | -0.20377 | -0.036674 | 12.9799 |  |  | 10.7608 |  |  | 16.9978 | 16.2009 | 15.1957 | 16.4918 | 15.7828 | 14.9193 | 10.7982 | 11.0854 | 11.6651 | 11.6485 | 9.3075 |  | 10.9569 | 8.9522 | 10.3583 | 9.5274 | 11.3142 | 12.493 |  | 12.5206 |  |  | 11.9101 | 12.7585 | 12.7297 | [6 empty] | 12.6886 |  |  | 11.3983 |  |  | 9.5737 | 10.5481 | 12.7854 | 7.7726 | 9.6421 | 13.1021 | 8.1322 | 9.8158 | 13.0889 | 9.4705 | 10.7279 | 7.8878 | 10.6416 | 8.6163 | 10.4098 | 7.8827 | 10.0946 | 13.6568 | 10.8018 | 10.5484 | 12.3547 | 8.1599 | 10.0115 | 13.1908 | 8.2032 | 10.781 | 9.995 | 10.0752 | 8.4676 | 10.4955 | -0.17335 | 20.9556 | 0.034285 | 0.048826 | -38.0912 | 0.44062 | -0.98 | 0.33 | 0.21534 | 0.25004 | 0.58797 | -0.64313 | -0.30416 | -0.84917 | 0.30577 | 0.41523 | 0.40537 | 0.42091 | 0.43304 | 0.62595 | 0.43061 | 0.41552
42810.4311 | -768 | 18.5395 | 18.6141 | 18.6112 | 18.645 | 18.0462 | 16.7237 | 14.8028 | 16.7837 | 17.2671 | 17.3738 | 17.3957 | 16.9661 | 16.0372 | 14.6574 | 15.0053 | 14.9955 | 15.5406 | 13.4298 | 13.5612 | 14.1502 |  |  |  | 16.688 | 16.049 | 15.1812 | 10.7117 | 10.1096 | 9.9003 | 17.2378 | 16.376 | 15.1803 | 16.9042 | 16.1871 | 15.2262 | 11.0325 | 11.6033 |  | 12.4779 | 11.1238 | 11.0286 | 8.8289 |  | 6.2083 | 6.1648 | 5.6287 | 5.7044 | 5.7426 | 6.2377 | 6.914 | 4.3033 | 6.3772 | 4.4356 | 6.6663 | 8.1224 | 43.0344 | 47.2939 | 43.6485 | 15.2773 |  |  | 0.069215 | -0.062997 | 0.19767 | 0.063082 | -0.12666 | -0.52024 | 0.3508 | -0.18613 | 0.43825 | -0.74559 | -0.28504 | 8.8945 | 8.8956 | 2.0084 | 15.9126 | 16.7875 | 17.327 | 17.6692 | 17.6416 | 16.6606 | 15.0249 | 16.9357 | 17.2632 | 17.5577 | 17.6102 | 17.3642 | 16.5907 | 14.8464 | 6.029 | 8.302 | 5.2143 | 5.5607 | 5.7333 | 6.7923 | 7.7071 | 15.9554 | 15.5824 | 15.4615 | 14.4082 | 14.3133 | 14.2598 |  |  |  | 10.9882 | 9.7775 | 9.2532 | 9.377 | -0.14035 | -0.092946 | 12.9879 |  |  | 10.7566 |  |  | 17.0048 | 16.2098 | 15.2072 | 16.4991 | 15.7944 | 14.9239 | 10.8041 | 11.094 | 11.6748 | 11.6547 | 9.2912 |  | 10.9597 | 8.9249 | 10.3524 | 9.5139 | 11.3167 | 12.4724 |  | 12.5159 |  |  | 11.9209 | 12.7624 | 12.7419 | [6 empty] | 12.6769 |  |  | 11.3941 |  |  | 9.5677 | 10.5432 | 12.7801 | 7.7682 | 9.6372 | 13.1043 | 8.1313 | 9.8193 | 13.0935 | 9.4796 | 10.7296 | 7.8923 | 10.6536 | 8.6231 | 10.4151 | 7.8893 | 10.093 | 13.6515 | 10.7973 | 10.5403 | 12.3461 | 8.1667 | 10.0132 | 13.1793 | 8.2142 | 10.7875 | 9.9933 | 10.0653 | 8.4775 | 10.4882 | -0.11865 | 20.9529 | 0.034865 | 0.049897 | -38.1183 | 0.45423 | -0.82 | 0.31 | 0.30846 | -0.29233 | 0.51783 | 0.29253 | -0.41456 | -0.84018 | 0.68992 | 0.41577 | 0.40593 | 0.42137 | 0.43304 | 0.62977 | 0.43102 | 0.41433
42810.4312 | -767 | 18.5465 | 18.6116 | 18.6176 | 18.6464 | 18.0355 | 16.7238 | 14.8044 | 16.7808 | 17.2674 | 17.3733 | 17.3973 | 16.9674 | 16.0438 | 14.6595 | 15.0041 | 14.9906 | 15.5398 | 13.4279 | 13.5639 | 14.1476 |  |  |  | 16.6889 | 16.0376 | 15.1728 | 10.7038 | 10.0904 | 9.9064 | 17.2488 | 16.365 | 15.1914 | 16.9101 | 16.2051 | 15.2299 | 11.0271 | 11.6141 |  | 12.4873 | 11.1295 | 11.028 | 8.8072 |  | 6.2138 | 6.1717 | 5.6312 | 5.701 | 5.7325 | 6.2355 | 6.8817 | 4.3762 | 6.3846 | 4.4125 | 6.6632 | 8.1126 | 43.0064 | 47.2834 | 43.6257 | 15.2702 |  |  | -0.011609 | -0.058397 | 0.22198 | 0.062426 | -0.00772 | -0.00506 | 0.33437 | -0.17627 | -0.52852 | -0.19487 | -0.41678 | 8.8963 | 8.8972 | 2.0087 | 15.9099 | 16.7879 | 17.3304 | 17.6714 | 17.6453 | 16.6596 | 15.0279 | 16.9388 | 17.2689 | 17.556 | 17.6054 | 17.3597 | 16.5914 | 14.8442 | 5.9857 | 8.2889 | 5.1652 | 5.5665 | 5.671 | 6.7827 | 7.7053 | 15.9631 | 15.5855 | 15.4675 | 14.4132 | 14.3077 | 14.2611 |  |  |  | 10.9934 | 9.7698 | 9.2406 | 9.3909 | -0.01697 | -0.085606 | 12.9858 |  |  | 10.7634 |  |  | 17.0002 | 16.2097 | 15.2102 | 16.5048 | 15.7885 | 14.9216 | 10.7975 | 11.0931 | 11.6813 | 11.6571 | 9.2843 |  | 10.9554 | 8.8837 | 10.3484 | 9.5104 | 11.3142 | 12.4279 |  | 12.5153 |  |  | 11.921 | 12.7557 | 12.75 | [6 empty] | 12.6866 |  |  | 11.3993 |  |  | 9.5615 | 10.5445 | 12.7774 | 7.7628 | 9.6436 | 13.1024 | 8.1245 | 9.8316 | 13.0981 | 9.4792 | 10.7378 | 7.8995 | 10.6648 | 8.633 | 10.4238 | 7.8906 | 10.0836 | 13.6409 | 10.7898 | 10.526 | 12.3407 | 8.1671 | 10.0017 | 13.1644 | 8.2115 | 10.7749 | 9.986 | 10.0541 | 8.4816 | 10.4861 | -0.19107 | 20.9533 | 0.03522 | 0.049419 | -38.1893 | 0.46782 | -0.69 | 0.33 | -0.12633 | -0.28146 | 0.54876 | 0.29101 | -0.10235 | -0.08286 | 0.67357 | 0.41582 | 0.40694 | 0.42138 | 0.43673 | 0.63502 | 0.43144 | 0.41412
42810.4312 | -766 | 18.5381 | 18.612 | 18.6134 | 18.6465 | 18.0353 | 16.719 | 14.795 | 16.7759 | 17.2583 | 17.3677 | 17.3892 | 16.9644 | 16.0332 | 14.6606 | 15.0046 | 14.992 | 15.5421 | 13.4312 | 13.5596 | 14.1421 |  |  |  | 16.6869 | 16.032 | 15.1797 | 10.697 | 10.0867 | 9.9355 | 17.2459 | 16.3665 | 15.1886 | 16.8977 | 16.1982 | 15.2245 | 11.0165 | 11.6168 |  | 12.4829 | 11.1233 | 11.0179 | 8.8071 |  | 6.2098 | 6.1811 | 5.641 | 5.703 | 5.7317 | 6.2259 | 6.8593 | 4.5014 | 6.3792 | 4.4178 | 6.6551 | 8.1206 | 42.9904 | 47.272 | 43.6187 | 15.2618 |  |  | -0.070749 | 0.042799 | 0.080704 | 0.048626 | 0.003448 | 0.3787 | 0.35934 | 0.001152 | -0.4425 | -0.59139 | -0.36115 | 8.8977 | 8.8991 | 2.0085 | 15.9032 | 16.7893 | 17.3331 | 17.6722 | 17.6446 | 16.653 | 15.0169 | 16.9378 | 17.2701 | 17.5579 | 17.5943 | 17.3597 | 16.5924 | 14.8439 | 5.9761 | 8.2784 | 5.1836 | 5.5321 | 5.6287 | 6.7775 | 7.7028 | 15.9675 | 15.5906 | 15.4664 | 14.4163 | 14.3021 | 14.2538 |  |  |  | 10.9948 | 9.7608 | 9.2398 | 9.3787 | -0.014944 | -0.095581 | 12.9845 |  |  | 10.7582 |  |  | 17.0017 | 16.214 | 15.2006 | 16.5018 | 15.7911 | 14.9146 | 10.7937 | 11.0875 | 11.6836 | 11.6519 | 9.2772 |  | 10.9414 | 8.9027 | 10.3474 | 9.495 | 11.3168 | 12.3995 |  | 12.5044 |  |  | 11.9213 | 12.7535 | 12.7475 | [6 empty] | 12.6831 |  |  | 11.3913 |  |  | 9.5513 | 10.5324 | 12.7705 | 7.7578 | 9.6286 | 13.0984 | 8.1152 | 9.8278 | 13.099 | 9.4671 | 10.7366 | 7.8979 | 10.6616 | 8.6245 | 10.4232 | 7.9098 | 10.0954 | 13.6391 | 10.7903 | 10.52 | 12.3487 | 8.1797 | 9.9999 | 13.1618 | 8.221 | 10.774 | 9.9926 | 10.0567 | 8.4934 | 10.4989 | -0.33648 | 20.9536 | 0.035404 | 0.048421 | -38.1725 | 0.4814 | -0.67 | 0.4 | -0.31188 | 0.24096 | 0.33088 | 0.25684 | 0.068398 | 0.71681 | 0.69826 | 0.41556 | 0.40638 | 0.42189 | 0.43719 | 0.63269 | 0.43109 | 0.4145
42810.4312 | -765 | 18.5437 | 18.6176 | 18.6118 | 18.6554 | 18.0392 | 16.7192 | 14.803 | 16.7806 | 17.264 | 17.3722 | 17.39 | 16.9631 | 16.0403 | 14.6599 | 15.0059 | 14.9933 | 15.5432 | 13.433 | 13.5532 | 14.1423 |  |  |  | 16.6939 | 16.0352 | 15.1906 | 10.6977 | 10.0759 | 9.9544 | 17.2451 | 16.3686 | 15.1877 | 16.901 | 16.2058 | 15.2319 | 11.0182 | 11.5976 |  | 12.4881 | 11.1279 | 11.015 | 8.8114 |  | 6.2158 | 6.2026 | 5.6628 | 5.7305 | 5.7413 | 6.228 | 6.8257 | 4.6395 | 6.3877 | 4.4122 | 6.6719 | 8.1147 | 42.9657 | 47.2452 | 43.6098 | 15.2463 |  |  | 0.12573 | -0.26078 | 0.17533 | -0.049282 | -0.039264 | 0.46149 | 0.46317 | -0.02382 | -0.19964 | -0.53076 | -0.32836 | 8.8928 | 8.8939 | 2.0085 | 15.9043 | 16.7898 | 17.3308 | 17.6691 | 17.6389 | 16.652 | 15.0204 | 16.9365 | 17.2684 | 17.5574 | 17.6033 | 17.3623 | 16.5956 | 14.8517 | 5.9672 | 8.3093 | 5.2692 | 5.5038 | 5.5596 | 6.7763 | 7.695 | 15.9663 | 15.583 | 15.4615 | 14.4165 | 14.303 | 14.2501 |  |  |  | 10.991 | 9.7621 | 9.236 | 9.3656 | 0.10317 | -0.022371 | 12.993 |  |  | 10.7693 |  |  | 17.0055 | 16.2208 | 15.2087 | 16.5121 | 15.8038 | 14.9241 | 10.8121 | 11.0932 | 11.6825 | 11.6718 | 9.2924 |  | 10.9591 | 8.8959 | 10.3493 | 9.4909 | 11.3115 | 12.4004 |  | 12.5166 |  |  | 11.9258 | 12.7614 | 12.7473 | [6 empty] | 12.676 |  |  | 11.3871 |  |  | 9.5401 | 10.5269 | 12.7496 | 7.7593 | 9.6172 | 13.0916 | 8.1146 | 9.8233 | 13.0954 | 9.4513 | 10.7305 | 7.9012 | 10.6587 | 8.6021 | 10.4181 | 7.9136 | 10.0887 | 13.6381 | 10.7848 | 10.4964 | 12.3415 | 8.1813 | 9.9963 | 13.1561 | 8.2179 | 10.768 | 9.9814 | 10.0506 | 8.4892 | 10.4918 | -0.32705 | 20.9532 | 0.035324 | 0.048008 | -38.2702 | 0.49494 | -0.93 | 0.37 | 0.41577 | -0.59482 | 0.48772 | -0.25858 | -0.23081 | 0.79131 | 0.79274 | 0.41572 | 0.40663 | 0.42183 | 0.43805 | 0.62227 | 0.43103 | 0.41474
42810.4312 | -764 | 18.5561 | 18.6187 | 18.62 | 18.6557 | 18.0449 | 16.7233 | 14.8057 | 16.7818 | 17.2718 | 17.3724 | 17.3961 | 16.9724 | 16.0431 | 14.6683 | 15.0133 | 15.0016 | 15.553 | 13.4339 | 13.5591 | 14.1546 |  |  |  | 16.6894 | 16.0488 | 15.1855 | 10.6907 | 10.0724 | 9.9432 | 17.2498 | 16.3688 | 15.1942 | 16.9057 | 16.2053 | 15.2316 | 11.0199 | 11.5647 |  | 12.4918 | 11.124 | 11.0169 | 8.8067 |  | 6.2374 | 6.2104 | 5.6828 | 5.7504 | 5.7465 | 6.2188 | 6.805 | 4.6858 | 6.389 | 4.4346 | 6.6733 | 8.1195 | 42.9441 | 47.2372 | 43.6098 | 15.2416 |  |  | -0.024753 | -0.24173 | 0.097788 | -0.091998 | 0.030392 | -0.20088 | 0.45134 | -0.04682 | -0.59254 | -0.49194 | -0.33094 | 8.8929 | 8.8942 | 2.0087 | 15.9103 | 16.7871 | 17.3315 | 17.6615 | 17.6383 | 16.6526 | 15.0113 | 16.9347 | 17.2645 | 17.5488 | 17.6046 | 17.3478 | 16.5863 | 14.8357 | 5.9847 | 8.3146 | 5.3624 | 5.518 | 5.5253 | 6.7875 | 7.703 | 15.968 | 15.5835 | 15.4691 | 14.4146 | 14.3045 | 14.2569 |  |  |  | 10.9884 | 9.7504 | 9.2289 | 9.3588 | 0.17064 | -0.22205 | 12.9847 |  |  | 10.761 |  |  | 17.0024 | 16.2112 | 15.1975 | 16.504 | 15.7901 | 14.9208 | 10.8091 | 11.0901 | 11.6859 | 11.6616 | 9.296 |  | 10.9534 | 8.832 | 10.3412 | 9.4884 | 11.3124 | 12.3914 |  | 12.5063 |  |  | 11.9193 | 12.7646 | 12.7402 | [6 empty] | 12.6886 |  |  | 11.3995 |  |  | 9.5199 | 10.5228 | 12.7379 | 7.729 | 9.6114 | 13.0849 | 8.1004 | 9.8035 | 13.0921 | 9.4459 | 10.7145 | 7.9009 | 10.6488 | 8.6001 | 10.4133 | 7.9301 | 10.0946 | 13.6435 | 10.7852 | 10.4863 | 12.3356 | 8.1826 | 9.9964 | 13.1384 | 8.2111 | 10.7629 | 9.9734 | 10.0488 | 8.4973 | 10.4972 | -0.15043 | 20.9543 | 0.035226 | 0.04782 | -38.14 | 0.50827 | -0.93 | 0.31 | -0.18448 | -0.57268 | 0.36424 | -0.3533 | 0.20307 | -0.52206 | 0.78254 | 0.41543 | 0.40814 | 0.42193 | 0.4374 | 0.61284 | 0.43122 | 0.41484
42810.4312 | -763 | 18.5472 | 18.6173 | 18.6138 | 18.6394 | 18.0402 | 16.7234 | 14.7954 | 16.7806 | 17.269 | 17.369 | 17.3887 | 16.9616 | 16.0331 | 14.6609 | 15.0131 | 14.9901 | 15.5493 | 13.4277 | 13.564 | 14.1544 |  |  |  | 16.6815 | 16.0394 | 15.1915 | 10.6798 | 10.0673 | 9.9571 | 17.2504 | 16.3778 | 15.1972 | 16.9096 | 16.2002 | 15.2349 | 11.0275 | 11.5437 |  | 12.4889 | 11.1241 | 11.0208 | 8.8118 |  | 6.2324 | 6.2064 | 5.6827 | 5.7503 | 5.7511 | 6.2076 | 6.7781 | 4.7345 | 6.374 | 4.4241 | 6.662 | 8.1222 | 42.9285 | 47.2537 | 43.607 | 15.2339 |  |  | 0.019275 | -0.10571 | 0.16022 | -0.084766 | 0.1053 | -0.11414 | 0.29495 | 0.083948 | -0.59702 | -0.28047 | -0.18689 | 8.8896 | 8.8908 | 2.0084 | 15.911 | 16.7975 | 17.3398 | 17.6691 | 17.6426 | 16.6567 | 15.0198 | 16.9384 | 17.2668 | 17.5591 | 17.6068 | 17.3564 | 16.59 | 14.8466 | 6.0079 | 8.2821 | 5.4314 | 5.5674 | 5.5284 | 6.7804 | 7.6934 | 15.9629 | 15.5752 | 15.4553 | 14.4076 | 14.3057 | 14.2501 |  |  |  | 10.9836 | 9.7412 | 9.2251 | 9.3436 | 0.20204 | -0.13642 | 12.978 |  |  | 10.7494 |  |  | 16.9993 | 16.2071 | 15.1956 | 16.5003 | 15.7848 | 14.9116 | 10.803 | 11.0749 | 11.6736 | 11.6532 | 9.2871 |  | 10.946 | 8.753 | 10.3332 | 9.4799 | 11.3036 | 12.3835 |  | 12.4983 |  |  | 11.9138 | 12.7741 | 12.7388 | [6 empty] | 12.6931 |  |  | 11.4004 |  |  | 9.5059 | 10.5146 | 12.7214 | 7.6833 | 9.5859 | 13.0806 | 8.1053 | 9.7875 | 13.0911 | 9.4325 | 10.711 | 7.8694 | 10.6237 | 8.6028 | 10.3984 | 7.9323 | 10.0926 | 13.6487 | 10.7767 | 10.4754 | 12.3257 | 8.1733 | 10.0033 | 13.1255 | 8.2107 | 10.7619 | 9.9784 | 10.0362 | 8.5024 | 10.4982 | -0.17335 | 20.9533 | 0.035083 | 0.048565 | -38.1898 | 0.5214 | -0.92 | 0.26 | 0.16279 | -0.37871 | 0.46623 | -0.33912 | 0.37798 | -0.39352 | 0.63259 | 0.41543 | 0.41007 | 0.42188 | 0.434 | 0.60406 | 0.43133 | 0.4151
42810.4312 | -762 | 18.5543 | 18.624 | 18.6137 | 18.6502 | 18.0458 | 16.7264 | 14.8085 | 16.7859 | 17.2739 | 17.3735 | 17.3956 | 16.9622 | 16.0408 | 14.6709 | 15.0134 | 14.9936 | 15.5508 | 13.4228 | 13.5638 | 14.1443 |  |  |  | 16.6869 | 16.0375 | 15.1729 | 10.6792 | 10.064 | 9.9731 | 17.2516 | 16.3763 | 15.1929 | 16.9144 | 16.2024 | 15.2296 | 11.0226 | 11.5413 |  | 12.492 | 11.1182 | 11.0256 | 8.8358 |  | 6.24 | 6.2109 | 5.6861 | 5.7484 | 5.7514 | 6.2219 | 6.8249 | 4.6606 | 6.3803 | 4.3897 | 6.6663 | 8.1253 | 42.9136 | 47.2568 | 43.6051 | 15.2245 |  |  | 0.090903 | -0.12345 | 0.19044 | -0.028914 | 0.018564 | 0.18419 | 0.498 | 0.13717 | -0.4355 | 1.2834 | -0.37148 | 8.8871 | 8.8884 | 2.0085 | 15.9233 | 16.7981 | 17.3424 | 17.6693 | 17.6483 | 16.6616 | 15.0247 | 16.9372 | 17.2649 | 17.5605 | 17.6071 | 17.3621 | 16.5915 | 14.8512 | 6.0298 | 8.2975 | 5.5064 | 5.5998 | 5.5539 | 6.7804 | 7.6865 | 15.9785 | 15.5819 | 15.469 | 14.4127 | 14.3135 | 14.2625 |  |  |  | 10.9895 | 9.7458 | 9.2362 | 9.3411 | 0.12931 | -0.070738 | 12.974 |  |  | 10.7476 |  |  | 17.0116 | 16.2046 | 15.1952 | 16.4983 | 15.7933 | 14.9098 | 10.806 | 11.0754 | 11.6865 | 11.6481 | 9.3109 |  | 10.9484 | 8.6999 | 10.3349 | 9.481 | 11.3049 | 12.3872 |  | 12.5025 |  |  | 11.9313 | 12.7713 | 12.7338 | [6 empty] | 12.6882 |  |  | 11.3868 |  |  | 9.5225 | 10.5129 | 12.7156 | 7.6887 | 9.5531 | 13.0717 | 8.1095 | 9.7809 | 13.1021 | 9.4393 | 10.7203 | 7.8596 | 10.6141 | 8.6073 | 10.4166 | 7.9424 | 10.0863 | 13.6431 | 10.7717 | 10.4593 | 12.3075 | 8.175 | 10.0044 | 13.1048 | 8.2061 | 10.7533 | 9.9702 | 10.0323 | 8.5091 | 10.4971 | 0.005188 | 20.9539 | 0.034268 | 0.047632 | -38.147 | 0.53983 | -0.56 | 0.28 | 0.35354 | -0.40925 | 0.50832 | -0.19806 | 0.15871 | 0.49991 | 0.822 | 0.41485 | 0.41161 | 0.42189 | 0.43157 | 0.59493 | 0.4305 | 0.41537
42810.4312 | -761 | 18.5566 | 18.6151 | 18.6171 | 18.6485 | 18.041 | 16.7241 | 14.803 | 16.7905 | 17.2684 | 17.3711 | 17.3959 | 16.9617 | 16.0417 | 14.6664 | 15.0109 | 15.0019 | 15.5557 | 13.4286 | 13.5664 | 14.1485 |  |  |  | 16.6858 | 16.0435 | 15.1868 | 10.6663 | 10.0617 | 10.0102 | 17.2563 | 16.3741 | 15.1918 | 16.9041 | 16.2046 | 15.2333 | 11.0208 | 11.5241 |  | 12.4841 | 11.1121 | 11.0189 | 8.8395 |  | 6.2391 | 6.2036 | 5.6756 | 5.7539 | 5.7873 | 6.3032 | 6.8767 | 4.4647 | 6.3817 | 4.3998 | 6.6683 | 8.1345 | 42.9195 | 47.2832 | 43.6099 | 15.2266 |  |  | -0.1956 | 0.094711 | 0.33041 | 0.095282 | 0.34844 | 0.32218 | 0.452 | 0.35271 | -0.33548 | -0.6986 | -0.23676 | 8.8905 | 8.892 | 2.0084 | 15.9178 | 16.7939 | 17.3389 | 17.667 | 17.6472 | 16.6566 | 15.0236 | 16.9386 | 17.2664 | 17.5656 | 17.6039 | 17.3622 | 16.5928 | 14.8495 | 6.0803 | 8.3033 | 5.4891 | 5.6067 | 5.5885 | 6.7833 | 7.6825 | 15.9673 | 15.5861 | 15.4673 | 14.4123 | 14.302 | 14.2625 |  |  |  | 10.9834 | 9.7318 | 9.2372 | 9.3387 | 0.069135 | -0.14941 | 12.9736 |  |  | 10.7529 |  |  | 16.9929 | 16.2089 | 15.1961 | 16.5033 | 15.7893 | 14.9129 | 10.8169 | 11.0709 | 11.6763 | 11.6411 | 9.3361 |  | 10.9461 | 8.61 | 10.3341 | 9.475 | 11.3078 | 12.4106 |  | 12.502 |  |  | 11.9365 | 12.779 | 12.7353 | [6 empty] | 12.6905 |  |  | 11.4025 |  |  | 9.5185 | 10.5079 | 12.7185 | 7.6929 | 9.5211 | 13.0658 | 8.1017 | 9.7847 | 13.1033 | 9.4414 | 10.7297 | 7.8521 | 10.609 | 8.6259 | 10.4144 | 7.9492 | 10.093 | 13.645 | 10.7734 | 10.4575 | 12.2957 | 8.1694 | 9.9994 | 13.1034 | 8.2063 | 10.7464 | 9.964 | 10.0261 | 8.5041 | 10.4891 | -0.086875 | 20.9548 | 0.033034 | 0.047292 | -38.1782 | 0.65836 | -0.5 | 0.41 | -0.51864 | 0.35846 | 0.66953 | 0.35954 | 0.68767 | 0.66126 | 0.78323 | 0.41408 | 0.41408 | 0.42215 | 0.42629 | 0.59639 | 0.43034 | 0.41524
42810.4312 | -760 | 18.5514 | 18.6055 | 18.611 | 18.6456 | 18.0301 | 16.7137 | 14.796 | 16.7829 | 17.2627 | 17.3659 | 17.3807 | 16.9627 | 16.0334 | 14.6645 | 15.0169 | 14.9896 | 15.5504 | 13.433 | 13.5591 | 14.1487 |  |  |  | 16.6798 | 16.0377 | 15.1779 | 10.6632 | 10.0616 | 10.0019 | 17.2645 | 16.3814 | 15.199 | 16.9124 | 16.2095 | 15.2403 | 11.0234 | 11.5289 |  | 12.4928 | 11.1034 | 11.0233 | 8.8348 |  | 6.2294 | 6.2038 | 5.6781 | 5.7534 | 5.8443 | 6.3832 | 6.9708 | 4.4478 | 6.377 | 4.4672 | 6.651 | 8.1357 | 42.9158 | 47.2893 | 43.6067 | 15.2305 |  |  | 0.010735 | 0.048059 | 0.1221 | -0.18991 | 0.33266 | 0.19996 | 0.46185 | 0.18646 | -0.48999 | -0.54041 | -0.35717 | 8.8918 | 8.8927 | 2.0086 | 15.9133 | 16.7893 | 17.3394 | 17.6666 | 17.6482 | 16.6526 | 15.0221 | 16.9355 | 17.263 | 17.5626 | 17.5991 | 17.3587 | 16.5897 | 14.8449 | 6.1075 | 8.3055 | 5.4565 | 5.606 | 5.6171 | 6.7777 | 7.6815 | 15.9771 | 15.5986 | 15.4691 | 14.4178 | 14.3092 | 14.2583 |  |  |  | 10.9854 | 9.7292 | 9.2476 | 9.3235 | -0.078357 | -0.097275 | 12.9714 |  |  | 10.7447 |  |  | 16.9919 | 16.2115 | 15.1947 | 16.4932 | 15.794 | 14.9107 | 10.8099 | 11.0609 | 11.6732 | 11.6221 | 9.3498 |  | 10.9476 | 8.4532 | 10.3387 | 9.4846 | 11.3085 | 12.4526 |  | 12.5008 |  |  | 11.9248 | 12.791 | 12.7409 | [6 empty] | 12.7019 |  |  | 11.4269 |  |  | 9.5161 | 10.5124 | 12.7174 | 7.6986 | 9.4901 | 13.0624 | 8.1009 | 9.7821 | 13.1005 | 9.4394 | 10.7278 | 7.8649 | 10.6086 | 8.6195 | 10.4098 | 7.9478 | 10.0804 | 13.6413 | 10.7494 | 10.4411 | 12.281 | 8.1597 | 9.9755 | 13.0765 | 8.1855 | 10.7329 | 9.9417 | 10.0137 | 8.4942 | 10.4818 | -0.31356 | 20.9547 | 0.032988 | 0.046952 | -38.1617 | 0.81162 | -0.82 | 0.3 | 0.1215 | 0.25535 | 0.40701 | -0.50759 | 0.67203 | 0.52102 | 0.79184 | 0.41374 | 0.41858 | 0.42191 | 0.42262 | 0.59989 | 0.43055 | 0.41572
42810.4313 | -759 | 18.5534 | 18.6136 | 18.613 | 18.6456 | 18.0385 | 16.7108 | 14.7986 | 16.7835 | 17.2689 | 17.3668 | 17.3884 | 16.9578 | 16.0448 | 14.6721 | 15.0157 | 15.0019 | 15.5494 | 13.4343 | 13.5635 | 14.1545 |  |  |  | 16.6805 | 16.0423 | 15.1839 | 10.6633 | 10.0738 | 9.9894 | 17.2676 | 16.3841 | 15.198 | 16.9105 | 16.2119 | 15.242 | 11.023 | 11.5405 |  | 12.4835 | 11.1026 | 11.0247 | 8.8266 |  | 6.2327 | 6.1968 | 5.6799 | 5.7661 | 5.8738 | 6.4445 | 7.0657 | 4.4695 | 6.3833 | 4.364 | 6.6641 | 8.1332 | 42.929 | 47.2893 | 43.615 | 15.2424 |  |  | -0.002409 | -0.13331 | 0.19504 | 0.13602 | 0.072448 | 0.2039 | 0.51508 | 0.24494 | -0.51062 | -0.36334 | -0.32439 | 8.8902 | 8.8917 | 2.0087 | 15.9216 | 16.7898 | 17.3409 | 17.6703 | 17.648 | 16.6523 | 15.0239 | 16.9363 | 17.2651 | 17.5613 | 17.6049 | 17.3625 | 16.5928 | 14.8518 | 6.1708 | 8.3068 | 5.3862 | 5.6064 | 5.6188 | 6.7715 | 7.6775 | 15.9742 | 15.5856 | 15.4604 | 14.4036 | 14.302 | 14.2528 |  |  |  | 10.9766 | 9.7082 | 9.2353 | 9.2714 | -0.07775 | 0.0099994 | 12.9796 |  |  | 10.7509 |  |  | 16.9988 | 16.2151 | 15.1943 | 16.498 | 15.7965 | 14.9105 | 10.8183 | 11.058 | 11.6798 | 11.6067 | 9.3501 |  | 10.937 | 8.3037 | 10.3319 | 9.48 | 11.3035 | 12.4629 |  | 12.501 |  |  | 11.8819 | 12.7871 | 12.7469 | [6 empty] | 12.7029 |  |  | 11.4052 |  |  | 9.4988 | 10.4985 | 12.7044 | 7.7021 | 9.4643 | 13.045 | 8.0897 | 9.7661 | 13.1077 | 9.4267 | 10.7157 | 7.8551 | 10.5921 | 8.6079 | 10.4107 | 7.9687 | 10.0894 | 13.6286 | 10.7544 | 10.4355 | 12.2736 | 8.1548 | 9.992 | 13.0791 | 8.1778 | 10.74 | 9.9314 | 10.0084 | 8.4952 | 10.4877 | -0.18472 | 20.9548 | 0.03382 | 0.048435 | -38.2161 | 0.96386 | -0.71 | 0.33 | -0.057555 | -0.42527 | 0.5144 | 0.42958 | 0.31365 | 0.52619 | 0.83631 | 0.41339 | 0.42251 | 0.42187 | 0.41487 | 0.60724 | 0.43076 | 0.41688
42810.4313 | -758 | 18.566 | 18.6207 | 18.6264 | 18.6578 | 18.0435 | 16.725 | 14.8059 | 16.7931 | 17.2737 | 17.3698 | 17.4007 | 16.9672 | 16.0423 | 14.6728 | 15.0271 | 15.0086 | 15.5603 | 13.4394 | 13.571 | 14.1585 |  |  |  | 16.6885 | 16.0503 | 15.1894 | 10.6584 | 10.0836 | 9.9888 | 17.2627 | 16.3811 | 15.195 | 16.912 | 16.2082 | 15.2391 | 11.0253 | 11.5938 |  | 12.4824 | 11.0991 | 11.0232 | 8.8035 |  | 6.2305 | 6.1913 | 5.6766 | 5.7617 | 5.8909 | 6.4743 | 7.1386 | 4.4597 | 6.3799 | 4.3047 | 6.6575 | 8.1313 | 42.9378 | 47.277 | 43.6172 | 15.269 |  |  | 0.006791 | -0.12937 | 0.03602 | 0.030886 | 0.28798 | -0.099028 | 0.56436 | 0.057004 | 0.080385 | -0.56789 | -0.21172 | 8.8878 | 8.8888 | 2.0084 | 15.9217 | 16.7918 | 17.3371 | 17.6724 | 17.6493 | 16.6567 | 15.0254 | 16.9336 | 17.2653 | 17.5583 | 17.604 | 17.3613 | 16.5894 | 14.8425 | 6.2603 | 8.3489 | 5.3572 | 5.6147 | 5.6254 | 6.7726 | 7.6751 | 15.9777 | 15.5915 | 15.4578 | 14.4083 | 14.31 | 14.2564 |  |  |  | 10.9824 | 9.7096 | 9.2445 | 9.2367 | -0.040269 | -0.13341 | 12.9782 |  |  | 10.7526 |  |  | 16.9968 | 16.2098 | 15.2026 | 16.4998 | 15.7833 | 14.9173 | 10.8161 | 11.058 | 11.6811 | 11.592 | 9.3346 |  | 10.9443 | 8.2268 | 10.3231 | 9.4758 | 11.305 | 12.4688 |  | 12.501 |  |  | 11.8666 | 12.7979 | 12.7512 | [6 empty] | 12.7066 |  |  | 11.4041 |  |  | 9.4843 | 10.494 | 12.6915 | 7.697 | 9.4512 | 13.0345 | 8.0737 | 9.7464 | 13.0971 | 9.4145 | 10.7077 | 7.8406 | 10.5753 | 8.5833 | 10.4059 | 7.9763 | 10.076 | 13.6143 | 10.734 | 10.4238 | 12.2415 | 8.1425 | 9.9877 | 13.0651 | 8.1721 | 10.7247 | 9.9155 | 10.0049 | 8.5007 | 10.4772 | -0.25328 | 20.9551 | 0.034876 | 0.050121 | -38.2112 | 1.1085 | -0.57 | 0.3 | 0.096635 | -0.41893 | 0.22106 | 0.2047 | 0.62537 | -0.36672 | 0.87546 | 0.41406 | 0.42436 | 0.42204 | 0.40505 | 0.61018 | 0.43148 | 0.41804
42810.4313 | -757 | 18.5641 | 18.6248 | 18.6211 | 18.6583 | 18.0422 | 16.7259 | 14.808 | 16.7891 | 17.2702 | 17.3729 | 17.3942 | 16.9636 | 16.0441 | 14.6696 | 15.0219 | 15.0009 | 15.5572 | 13.4323 | 13.5686 | 14.1541 |  |  |  | 16.6845 | 16.04 | 15.1819 | 10.6501 | 10.1027 | 9.9979 | 17.2643 | 16.3869 | 15.1994 | 16.9103 | 16.2073 | 15.2429 | 11.0286 | 11.6792 |  | 12.4895 | 11.0963 | 11.0221 | 8.7877 |  | 6.2189 | 6.1909 | 5.6716 | 5.7692 | 5.9385 | 6.5337 | 7.2111 | 4.4494 | 6.3729 | 4.3037 | 6.6553 | 8.1303 | 42.945 | 47.2786 | 43.6221 | 15.2986 |  |  | 0.071843 | -0.070225 | 0.22461 | 0.03417 | 0.36946 | 0.048824 | 0.45068 | 0.16477 | -0.67466 | -0.29767 | -0.33949 | 8.892 | 8.8932 | 2.0088 | 15.9151 | 16.7974 | 17.338 | 17.6743 | 17.6544 | 16.6596 | 15.0211 | 16.9383 | 17.2693 | 17.559 | 17.6009 | 17.3646 | 16.5841 | 14.8443 | 6.3304 | 8.3901 | 5.4352 | 5.6002 | 5.6562 | 6.7732 | 7.679 | 15.9846 | 15.592 | 15.4626 | 14.4169 | 14.311 | 14.2601 |  |  |  | 10.9768 | 9.7089 | 9.2392 | 9.1927 | -0.17378 | -0.055118 | 12.9753 |  |  | 10.7587 |  |  | 16.999 | 16.2076 | 15.2002 | 16.4948 | 15.7847 | 14.9222 | 10.8189 | 11.0566 | 11.6713 | 11.5784 | 9.3314 |  | 10.9362 | 8.1797 | 10.3193 | 9.4674 | 11.3024 | 12.4839 |  | 12.502 |  |  | 11.876 | 12.7967 | 12.7677 | [6 empty] | 12.7093 |  |  | 11.3998 |  |  | 9.4929 | 10.4887 | 12.6985 | 7.7053 | 9.4514 | 13.0373 | 8.072 | 9.7467 | 13.0962 | 9.4119 | 10.7098 | 7.8361 | 10.5837 | 8.5738 | 10.4217 | 7.9905 | 10.0818 | 13.6155 | 10.7381 | 10.4247 | 12.2342 | 8.1506 | 9.9962 | 13.0565 | 8.177 | 10.7249 | 9.9107 | 10.0127 | 8.5048 | 10.4861 | -0.088223 | 20.9546 | 0.035576 | 0.051272 | -38.2522 | 1.2418 | -0.66 | 0.26 | 0.31432 | -0.30866 | 0.55201 | 0.21531 | 0.70841 | 0.25752 | 0.78241 | 0.41388 | 0.42554 | 0.42218 | 0.39733 | 0.60197 | 0.43203 | 0.41907
42810.4313 | -756 | 18.561 | 18.6196 | 18.611 | 18.6514 | 18.0326 | 16.7224 | 14.8025 | 16.776 | 17.2673 | 17.3649 | 17.3893 | 16.9593 | 16.0343 | 14.6625 | 15.0277 | 15.006 | 15.5569 | 13.4377 | 13.5648 | 14.1557 |  |  |  | 16.6888 | 16.0413 | 15.1775 | 10.6492 | 10.1373 | 10.003 | 17.2671 | 16.3879 | 15.2048 | 16.9151 | 16.2046 | 15.2416 | 11.0294 | 11.7591 |  | 12.4869 | 11.0992 | 11.029 | 8.7807 |  | 6.2325 | 6.1918 | 5.6829 | 5.7894 | 5.9638 | 6.6158 | 7.245 | 4.4094 | 6.376 | 4.3181 | 6.6557 | 8.1367 | 42.947 | 47.2624 | 43.6171 | 15.3273 |  |  | 0.087615 | 0.097999 | 0.084648 | 0.19976 | -0.083288 | 0.20982 | 0.5164 | 0.21997 | -0.53358 | 0.048501 | -0.28186 | 8.8862 | 8.8877 | 2.0085 | 15.9229 | 16.7971 | 17.3426 | 17.6759 | 17.6483 | 16.6553 | 15.0225 | 16.9409 | 17.2704 | 17.5544 | 17.5987 | 17.3598 | 16.5961 | 14.8505 | 6.2795 | 8.3409 | 5.5392 | 5.5742 | 5.6803 | 6.7633 | 7.6636 | 15.9848 | 15.5947 | 15.4648 | 14.4211 | 14.3081 | 14.2598 |  |  |  | 10.9745 | 9.6978 | 9.2365 | 9.1507 | 0.047255 | -0.0067504 | 12.987 |  |  | 10.7708 |  |  | 17.0012 | 16.219 | 15.209 | 16.5084 | 15.7996 | 14.9278 | 10.8399 | 11.0685 | 11.6733 | 11.5739 | 9.325 |  | 10.9357 | 8.135 | 10.319 | 9.4697 | 11.3008 | 12.5128 |  | 12.5123 |  |  | 11.8735 | 12.791 | 12.76 | [6 empty] | 12.698 |  |  | 11.3917 |  |  | 9.4903 | 10.4914 | 12.6955 | 7.7283 | 9.4495 | 13.0362 | 8.0752 | 9.7474 | 13.1069 | 9.4061 | 10.7115 | 7.8507 | 10.5957 | 8.5646 | 10.4169 | 8.0013 | 10.0878 | 13.6234 | 10.7404 | 10.4334 | 12.2221 | 8.1663 | 9.9966 | 13.0549 | 8.1882 | 10.7396 | 9.9041 | 10.0186 | 8.5106 | 10.4864 | -0.080519 | 20.9545 | 0.035622 | 0.049854 | -38.2312 | 1.3708 | -0.74 | 0.34 | 0.34711 | 0.36462 | 0.33888 | 0.52058 | -0.3364 | 0.53393 | 0.83764 | 0.41404 | 0.42677 | 0.42207 | 0.40184 | 0.58862 | 0.43225 | 0.42016
42810.4313 | -755 | 18.5732 | 18.6303 | 18.6211 | 18.6514 | 18.0417 | 16.7203 | 14.8129 | 16.7839 | 17.267 | 17.3703 | 17.3907 | 16.9693 | 16.0367 | 14.6677 | 15.0233 | 15.0069 | 15.5494 | 13.4324 | 13.5618 | 14.1501 |  |  |  | 16.6805 | 16.0399 | 15.175 | 10.6396 | 10.1569 | 9.9926 | 17.2677 | 16.3852 | 15.2019 | 16.9126 | 16.2064 | 15.2447 | 11.0253 | 11.8309 |  | 12.4875 | 11.1015 | 11.0258 | 8.7731 |  | 6.237 | 6.1978 | 5.6891 | 5.7939 | 5.9794 | 6.6676 | 7.3044 | 4.3519 | 6.37 | 4.2285 | 6.6588 | 8.138 | 42.9468 | 47.2061 | 43.614 | 15.3539 |  |  | 0.13493 | 0.082883 | 0.31858 | -0.004598 | 0.15393 | 0.28538 | 0.32714 | 0.22654 | -0.40864 | -0.54104 | -0.25703 | 8.8866 | 8.8877 | 2.0085 | 15.9277 | 16.7998 | 17.3468 | 17.6691 | 17.65 | 16.6568 | 15.0244 | 16.9387 | 17.2685 | 17.561 | 17.6046 | 17.3595 | 16.5882 | 14.8486 | 6.2341 | 8.3126 | 5.475 | 5.5663 | 5.7201 | 6.7697 | 7.6652 | 15.9773 | 15.5999 | 15.467 | 14.4099 | 14.3104 | 14.251 |  |  |  | 10.9729 | 9.6858 | 9.2239 | 9.1049 | -0.026897 | 0.02976 | 12.976 |  |  | 10.7673 |  |  | 16.9973 | 16.209 | 15.2001 | 16.4937 | 15.7911 | 14.9202 | 10.8303 | 11.0506 | 11.658 | 11.5582 | 9.316 |  | 10.9412 | 8.092 | 10.3221 | 9.4761 | 11.2967 | 12.5419 |  | 12.5045 |  |  | 11.9 | 12.7906 | 12.756 | [6 empty] | 12.6943 |  |  | 11.3878 |  |  | 9.4771 | 10.4919 | 12.6828 | 7.7361 | 9.4358 | 13.0191 | 8.0633 | 9.7336 | 13.1122 | 9.407 | 10.706 | 7.8438 | 10.5933 | 8.5451 | 10.4104 | 8.0036 | 10.0819 | 13.6248 | 10.7367 | 10.4344 | 12.1994 | 8.1689 | 9.9942 | 13.0581 | 8.1864 | 10.7346 | 9.8923 | 10.0125 | 8.5107 | 10.4867 | -0.11172 | 20.9554 | 0.035674 | 0.049912 | -38.152 | 1.4961 | -0.43 | 0.25 | 0.43074 | 0.33533 | 0.65743 | -0.078981 | 0.45737 | 0.62276 | 0.66677 | 0.41448 | 0.42807 | 0.42175 | 0.40762 | 0.59593 | 0.43233 | 0.42138
42810.4313 | -754 | 18.5611 | 18.6165 | 18.6227 | 18.6502 | 18.0431 | 16.723 | 14.7964 | 16.7752 | 17.2593 | 17.3586 | 17.3821 | 16.9557 | 16.0311 | 14.662 | 15.0263 | 15.0035 | 15.5461 | 13.4309 | 13.5614 | 14.151 |  |  |  | 16.6789 | 16.0363 | 15.1782 | 10.6319 | 10.1756 | 9.9825 | 17.2737 | 16.3912 | 15.1991 | 16.9173 | 16.2057 | 15.2352 | 11.0309 | 11.8866 |  | 12.4841 | 11.0972 | 11.0165 | 8.7512 |  | 6.2436 | 6.2089 | 5.7275 | 5.8237 | 6.012 | 6.7031 | 7.3586 | 4.3019 | 6.3764 | 4.1746 | 6.6637 | 8.1442 | 42.9361 | 47.15 | 43.6164 | 15.3815 |  |  | 0.039647 | -0.009769 | 0.21541 | 0.27007 | 0.20453 | -0.50644 | 0.52954 | 0.1674 | 0.18119 | -0.40152 | -0.31465 | 8.8788 | 8.88 | 2.0085 | 15.9274 | 16.7992 | 17.3399 | 17.6658 | 17.6487 | 16.6609 | 15.028 | 16.9363 | 17.2666 | 17.5568 | 17.6012 | 17.357 | 16.5883 | 14.8439 | 6.2074 | 8.3139 | 5.4257 | 5.4857 | 5.7297 | 6.7544 | 7.66 | 15.9798 | 15.5974 | 15.4585 | 14.4013 | 14.2996 | 14.2548 |  |  |  | 10.9656 | 9.673 | 9.2202 | 9.0803 | -0.001572 | -0.087488 | 12.9724 |  |  | 10.7619 |  |  | 16.9995 | 16.2061 | 15.1999 | 16.4929 | 15.7892 | 14.9196 | 10.8385 | 11.0542 | 11.6462 | 11.5496 | 9.3103 |  | 10.9405 | 8.0698 | 10.3273 | 9.4663 | 11.2985 | 12.5517 |  | 12.5156 |  |  | 11.9213 | 12.789 | 12.7512 | [6 empty] | 12.7095 |  |  | 11.3891 |  |  | 9.4758 | 10.493 | 12.6813 | 7.7451 | 9.438 | 13.0077 | 8.0637 | 9.7298 | 13.1117 | 9.4108 | 10.7081 | 7.8504 | 10.6 | 8.5424 | 10.4122 | 7.9944 | 10.0798 | 13.6263 | 10.7316 | 10.44 | 12.1714 | 8.1614 | 9.9962 | 13.0527 | 8.1829 | 10.7292 | 9.878 | 10.0084 | 8.5129 | 10.4791 | -0.18414 | 20.9554 | 0.035433 | 0.048913 | -38.1966 | 1.6189 | -0.51 | 0.35 | 0.23349 | -0.11513 | 0.54061 | 0.60533 | 0.52724 | -0.82965 | 0.84836 | 0.41461 | 0.42885 | 0.42209 | 0.4088 | 0.60081 | 0.43312 | 0.42183
42810.4313 | -753 | 18.5687 | 18.6345 | 18.6237 | 18.6638 | 18.0509 | 16.7277 | 14.8122 | 16.7916 | 17.2763 | 17.3792 | 17.4027 | 16.9748 | 16.052 | 14.6772 | 15.0372 | 15.006 | 15.5523 | 13.4341 | 13.5637 | 14.1561 |  |  |  | 16.6867 | 16.0448 | 15.1823 | 10.6304 | 10.1928 | 9.9941 | 17.2708 | 16.3932 | 15.199 | 16.9169 | 16.2111 | 15.2463 | 11.0323 | 11.918 |  | 12.4842 | 11.0946 | 11.0068 | 8.7384 |  | 6.2369 | 6.2164 | 5.7522 | 5.8496 | 6.0241 | 6.6712 | 7.3769 | 4.2563 | 6.3821 | 4.2153 | 6.6589 | 8.1391 | 42.9319 | 47.1076 | 43.6205 | 15.4006 |  |  | 0.21576 | -0.045253 | 0.32712 | 0.07557 | 0.2111 | 0.10928 | 0.52099 | 0.24034 | -1.4657 | 0.10032 | -0.22106 | 8.8818 | 8.8831 | 2.0083 | 15.9316 | 16.8043 | 17.3437 | 17.6712 | 17.6528 | 16.6564 | 15.0333 | 16.94 | 17.2671 | 17.5568 | 17.6 | 17.3566 | 16.5918 | 14.8437 | 6.2488 | 8.2866 | 5.4029 | 5.4186 | 5.7419 | 6.7575 | 7.6642 | 15.9854 | 15.5947 | 15.4664 | 14.4107 | 14.3042 | 14.2554 |  |  |  | 10.9756 | 9.6746 | 9.2285 | 9.0744 | 0.081291 | -0.17481 | 12.9704 |  |  | 10.7614 |  |  | 16.9993 | 16.206 | 15.1975 | 16.4943 | 15.7897 | 14.9184 | 10.8398 | 11.0534 | 11.6375 | 11.5439 | 9.3246 |  | 10.934 | 8.0657 | 10.3183 | 9.439 | 11.2985 | 12.5556 |  | 12.508 |  |  | 11.9416 | 12.7772 | 12.7321 | [6 empty] | 12.7109 |  |  | 11.3955 |  |  | 9.4716 | 10.4856 | 12.6832 | 7.7639 | 9.4424 | 13.0027 | 8.0625 | 9.7272 | 13.1115 | 9.4107 | 10.7148 | 7.8591 | 10.6093 | 8.5486 | 10.409 | 7.9977 | 10.0882 | 13.6352 | 10.7397 | 10.4483 | 12.1446 | 8.1612 | 9.9927 | 13.0544 | 8.1869 | 10.7307 | 9.8753 | 10.0154 | 8.5055 | 10.4822 | -0.23421 | 20.9542 | 0.033608 | 0.048913 | -38.1748 | 1.7388 | -0.57 | 0.35 | 0.54469 | -0.24779 | 0.66621 | 0.32021 | 0.53561 | 0.38537 | 0.84144 | 0.414 | 0.42867 | 0.42285 | 0.40458 | 0.60384 | 0.43352 | 0.42232
42810.4313 | -752 | 18.5883 | 18.6377 | 18.6311 | 18.6653 | 18.0546 | 16.7319 | 14.8134 | 16.7968 | 17.2783 | 17.3875 | 17.4071 | 16.9745 | 16.0497 | 14.6783 | 15.0383 | 15.0102 | 15.5635 | 13.436 | 13.5696 | 14.1621 |  |  |  | 16.6953 | 16.0469 | 15.1836 | 10.6272 | 10.2092 | 10.0139 | 17.2775 | 16.397 | 15.2094 | 16.9245 | 16.2106 | 15.2506 | 11.0338 | 11.9321 |  | 12.4908 | 11.1028 | 11.0108 | 8.7502 |  | 6.2197 | 6.2106 | 5.7663 | 5.8731 | 6.0195 | 6.6675 | 7.4104 | 4.2778 | 6.364 | 4.2698 | 6.6449 | 8.1442 | 42.9401 | 47.0918 | 43.6365 | 15.4219 |  |  | -0.006353 | 0.21693 | 0.27784 | 0.082798 | 0.26564 | 0.2223 | 0.39023 | 0.03072 | -0.5509 | -1.8798 | -0.4899 | 8.8809 | 8.8819 | 2.0087 | 15.9378 | 16.8073 | 17.3463 | 17.6728 | 17.6572 | 16.6647 | 15.0263 | 16.9387 | 17.2663 | 17.5594 | 17.603 | 17.3574 | 16.5902 | 14.8471 | 6.2695 | 8.2687 | 5.4392 | 5.354 | 5.7074 | 6.7529 | 7.6627 | 15.9917 | 15.5976 | 15.4687 | 14.4167 | 14.3047 | 14.2633 |  |  |  | 10.972 | 9.6793 | 9.2327 | 9.0706 | 0.095271 | -0.068292 | 12.9752 |  |  | 10.7724 |  |  | 17.0052 | 16.2104 | 15.1999 | 16.4997 | 15.7913 | 14.9152 | 10.8453 | 11.0565 | 11.635 | 11.5442 | 9.3454 |  | 10.9292 | 8.106 | 10.3162 | 9.4157 | 11.2994 | 12.5594 |  | 12.5082 |  |  | 11.9548 | 12.7757 | 12.7195 | [6 empty] | 12.7101 |  |  | 11.4042 |  |  | 9.4696 | 10.4731 | 12.6785 | 7.7743 | 9.4402 | 12.9969 | 8.0522 | 9.7198 | 13.1002 | 9.403 | 10.7131 | 7.8564 | 10.6067 | 8.5455 | 10.4077 | 8.0069 | 10.0908 | 13.6483 | 10.7427 | 10.4475 | 12.1227 | 8.165 | 9.9886 | 13.0607 | 8.1855 | 10.7225 | 9.87 | 10.0092 | 8.508 | 10.4836 | -0.012531 | 20.9557 | 0.034038 | 0.049 | -38.1518 | 1.8614 | -0.9 | 0.34 | -0.093471 | 0.54252 | 0.61397 | 0.33517 | 0.60083 | 0.54964 | 0.72822 | 0.41326 | 0.42749 | 0.42352 | 0.40173 | 0.59964 | 0.43324 | 0.42231
42810.4313 | -751 | 18.5842 | 18.6314 | 18.6281 | 18.6557 | 18.0429 | 16.7298 | 14.8118 | 16.789 | 17.2745 | 17.3736 | 17.3935 | 16.9688 | 16.045 | 14.6707 | 15.0355 | 15.006 | 15.5643 | 13.4358 | 13.5653 | 14.16 |  |  |  | 16.6878 | 16.0377 | 15.184 | 10.626 | 10.2101 | 10.0057 | 17.2824 | 16.3963 | 15.2084 | 16.9197 | 16.2118 | 15.2431 | 11.0324 | 11.9251 |  | 12.4898 | 11.1081 | 11.0119 | 8.7529 |  | 6.2141 | 6.2193 | 5.7793 | 5.895 | 6.0286 | 6.6861 | 7.4032 | 4.3605 | 6.3744 | 4.2627 | 6.6544 | 8.1476 | 42.9537 | 47.0942 | 43.6427 | 15.4436 |  |  | -0.061549 | 0.078283 | 0.20687 | 0.31279 | 0.15262 | 0.13228 | 0.14052 | 0.092488 | -0.22533 | -0.38558 | -0.39055 | 8.8898 | 8.891 | 2.0084 | 15.9338 | 16.7918 | 17.336 | 17.6682 | 17.6516 | 16.6539 | 15.017 | 16.9304 | 17.255 | 17.5485 | 17.5986 | 17.3506 | 16.5824 | 14.8362 | 6.2938 | 8.2556 | 5.4505 | 5.3401 | 5.6163 | 6.7521 | 7.6593 | 15.9925 | 15.6015 | 15.4667 | 14.4182 | 14.3114 | 14.2658 |  |  |  | 10.9763 | 9.6757 | 9.2272 | 9.0656 | 0.055156 | -0.055871 | 12.9701 |  |  | 10.7693 |  |  | 17.004 | 16.2003 | 15.1954 | 16.4968 | 15.784 | 14.9101 | 10.8548 | 11.0542 | 11.6266 | 11.5302 | 9.3677 |  | 10.9331 | 8.2157 | 10.317 | 9.3946 | 11.295 | 12.5347 |  | 12.4997 |  |  | 11.9531 | 12.7782 | 12.7171 | [6 empty] | 12.7016 |  |  | 11.4028 |  |  | 9.4714 | 10.4702 | 12.6831 | 7.7805 | 9.4357 | 12.9908 | 8.05 | 9.7093 | 13.0953 | 9.3998 | 10.7071 | 7.851 | 10.6159 | 8.5445 | 10.4061 | 8.0083 | 10.0928 | 13.6472 | 10.741 | 10.4465 | 12.1016 | 8.1655 | 9.9933 | 13.0656 | 8.1808 | 10.7118 | 9.8612 | 10.0039 | 8.5064 | 10.4825 | -0.146 | 20.9551 | 0.035502 | 0.051895 | -38.1616 | 2.0052 | -0.86 | 0.32 | -0.29093 | 0.3259 | 0.52979 | 0.65145 | 0.45543 | 0.42399 | 0.43701 | 0.41277 | 0.42446 | 0.42396 | 0.39895 | 0.59798 | 0.43313 | 0.42259
42810.4314 | -750 | 18.5803 | 18.6324 | 18.6256 | 18.6625 | 18.0469 | 16.7249 | 14.8134 | 16.7844 | 17.2731 | 17.372 | 17.3968 | 16.9742 | 16.0417 | 14.6706 | 15.0402 | 15.0162 | 15.5709 | 13.4363 | 13.575 | 14.169 |  |  |  | 16.692 | 16.0448 | 15.1919 | 10.6234 | 10.2154 | 10.0008 | 17.2836 | 16.4012 | 15.2037 | 16.922 | 16.2105 | 15.2453 | 11.03 | 11.9247 |  | 12.4871 | 11.1066 | 11.0118 | 8.7491 |  | 6.2063 | 6.2115 | 5.7759 | 5.9002 | 6.0281 | 6.6627 | 7.3478 | 4.4427 | 6.3637 | 4.1979 | 6.6548 | 8.1522 | 42.9703 | 47.0957 | 43.6463 | 15.4661 |  |  | 0.1047 | -0.11622 | 0.26601 | 0.12748 | 0.015276 | -0.28828 | 0.35474 | 0.096432 | -0.31368 | -0.29767 | -0.18232 | 8.8854 | 8.8869 | 2.0088 | 15.9399 | 16.799 | 17.3367 | 17.6766 | 17.6461 | 16.6556 | 15.0277 | 16.9343 | 17.2678 | 17.5575 | 17.594 | 17.3617 | 16.5828 | 14.8514 | 6.2683 | 8.2296 | 5.4382 | 5.3541 | 5.5444 | 6.7534 | 7.6545 | 15.9853 | 15.5999 | 15.4648 | 14.4168 | 14.3061 | 14.2612 |  |  |  | 10.9622 | 9.6652 | 9.2237 | 9.0497 | 0.081899 | -0.093699 | 12.9762 |  |  | 10.767 |  |  | 17.0025 | 16.2017 | 15.1938 | 16.4984 | 15.7877 | 14.9109 | 10.8715 | 11.0521 | 11.6225 | 11.5299 | 9.3889 |  | 10.9344 | 8.3584 | 10.3204 | 9.3935 | 11.2926 | 12.5092 |  | 12.5083 |  |  | 11.9706 | 12.7839 | 12.735 | [6 empty] | 12.6932 |  |  | 11.4181 |  |  | 9.4846 | 10.4741 | 12.6892 | 7.7971 | 9.4436 | 12.99 | 8.0562 | 9.7207 | 13.1141 | 9.4109 | 10.7114 | 7.8651 | 10.6285 | 8.5463 | 10.414 | 8.0076 | 10.0966 | 13.6453 | 10.7361 | 10.4471 | 12.1142 | 8.1719 | 9.9949 | 13.0669 | 8.183 | 10.6901 | 9.8656 | 10.0049 | 8.501 | 10.4878 | -0.23306 | 20.9548 | 0.03557 | 0.051692 | -38.1596 | 2.1474 | -0.98 | 0.31 | 0.37944 | -0.39709 | 0.60076 | 0.41589 | 0.14408 | -0.6259 | 0.69432 | 0.41223 | 0.42061 | 0.42391 | 0.40193 | 0.59879 | 0.43315 | 0.42256
42810.4314 | -749 | 18.5812 | 18.6292 | 18.6265 | 18.6676 | 18.0495 | 16.7248 | 14.8073 | 16.7843 | 17.2724 | 17.3738 | 17.3963 | 16.9755 | 16.0395 | 14.6684 | 15.0288 | 15.0109 | 15.5564 | 13.4273 | 13.5662 | 14.1506 |  |  |  | 16.6825 | 16.0381 | 15.1848 | 10.6008 | 10.2089 | 9.9859 | 17.2878 | 16.405 | 15.2172 | 16.9224 | 16.2124 | 15.2438 | 11.038 | 11.9418 |  | 12.4922 | 11.0983 | 11.0112 | 8.7525 |  | 6.2169 | 6.2066 | 5.7944 | 5.907 | 6.0191 | 6.6431 | 7.3085 | 4.5121 | 6.3672 | 4.1959 | 6.6566 | 8.1509 | 42.9659 | 47.0761 | 43.6387 | 15.4758 |  |  | 0.010735 | -0.041969 | 0.23907 | 0.033514 | 0.28207 | 0.061308 | 0.56699 | 0.13783 | -0.9111 | -0.45124 | -0.291 | 8.8891 | 8.8904 | 2.0085 | 15.9372 | 16.8071 | 17.3442 | 17.6767 | 17.6476 | 16.6606 | 15.0261 | 16.9366 | 17.2678 | 17.5584 | 17.6074 | 17.3507 | 16.5848 | 14.8392 | 6.2727 | 8.242 | 5.4301 | 5.3889 | 5.5128 | 6.7539 | 7.6567 | 16.001 | 15.6106 | 15.4737 | 14.424 | 14.3184 | 14.2649 |  |  |  | 10.9714 | 9.6686 | 9.2274 | 9.07 | -0.0042058 | -0.061328 | 12.9789 |  |  | 10.7771 |  |  | 17.0053 | 16.2075 | 15.1959 | 16.4957 | 15.7897 | 14.9131 | 10.8884 | 11.0449 | 11.6186 | 11.5256 | 9.4038 |  | 10.9337 | 8.5194 | 10.3233 | 9.3786 | 11.2899 | 12.4855 |  | 12.5008 |  |  | 11.9695 | 12.7944 | 12.7535 | [6 empty] | 12.6895 |  |  | 11.4354 |  |  | 9.4688 | 10.459 | 12.6809 | 7.7979 | 9.4439 | 12.9809 | 8.0546 | 9.7117 | 13.1123 | 9.4038 | 10.6998 | 7.8664 | 10.6283 | 8.5419 | 10.3968 | 8.0175 | 10.0778 | 13.6488 | 10.7308 | 10.4458 | 12.1215 | 8.1786 | 9.9883 | 13.0725 | 8.1724 | 10.6705 | 9.8608 | 9.9983 | 8.5023 | 10.4789 | -0.31934 | 20.9542 | 0.035048 | 0.051316 | -38.1477 | 2.2891 | -1.27 | 0.31 | 0.1215 | -0.23862 | 0.56952 | 0.21324 | 0.6191 | 0.28863 | 0.87776 | 0.41179 | 0.41623 | 0.42424 | 0.4015 | 0.59995 | 0.43332 | 0.4223
42810.4314 | -748 | 18.5878 | 18.6337 | 18.6279 | 18.6653 | 18.0572 | 16.7264 | 14.8056 | 16.7876 | 17.2733 | 17.381 | 17.3979 | 16.9794 | 16.0489 | 14.6739 | 15.0364 | 15.0171 | 15.5557 | 13.4292 | 13.5651 | 14.1674 |  |  |  | 16.6836 | 16.0417 | 15.1795 | 10.597 | 10.2055 | 10.009 | 17.2792 | 16.3975 | 15.2121 | 16.9214 | 16.2116 | 15.2433 | 11.0322 | 11.9525 |  | 12.4904 | 11.0825 | 11.0091 | 8.7507 |  | 6.2226 | 6.2094 | 5.8141 | 5.9213 | 6.0305 | 6.631 | 7.2817 | 4.5048 | 6.3705 | 4.2416 | 6.6626 | 8.1511 | 42.9622 | 47.0661 | 43.6236 | 15.479 |  |  | 0.10207 | -0.12279 | 0.19242 | -0.057826 | 0.19927 | 0.10599 | 0.49274 | 0.2364 | -0.75484 | -0.15123 | -0.19483 | 8.8803 | 8.8817 | 2.0083 | 15.9432 | 16.8075 | 17.3482 | 17.6747 | 17.6563 | 16.6631 | 15.028 | 16.9457 | 17.2743 | 17.5651 | 17.6101 | 17.3511 | 16.5934 | 14.8416 | 6.2374 | 8.2649 | 5.3968 | 5.4172 | 5.4964 | 6.7495 | 7.6505 | 15.9962 | 15.6118 | 15.4788 | 14.4229 | 14.3199 | 14.2676 |  |  |  | 10.9635 | 9.6638 | 9.2182 | 9.0656 | -0.017577 | 0.031078 | 12.9851 |  |  | 10.7814 |  |  | 16.995 | 16.2068 | 15.1957 | 16.4942 | 15.7843 | 14.9201 | 10.9001 | 11.0471 | 11.6155 | 11.5304 | 9.4161 |  | 10.9347 | 8.6674 | 10.3182 | 9.359 | 11.2849 | 12.4701 |  | 12.5067 |  |  | 11.9798 | 12.7902 | 12.7464 | [6 empty] | 12.6862 |  |  | 11.4341 |  |  | 9.4721 | 10.4572 | 12.6792 | 7.8009 | 9.4444 | 12.9786 | 8.0496 | 9.7032 | 13.1169 | 9.4003 | 10.6906 | 7.8616 | 10.6324 | 8.5447 | 10.398 | 8.0174 | 10.0669 | 13.6504 | 10.7434 | 10.4564 | 12.1494 | 8.1876 | 10.0022 | 13.0863 | 8.1778 | 10.6713 | 9.8682 | 10.0137 | 8.5119 | 10.4849 | -0.13965 | 20.9537 | 0.0351 | 0.050483 | -38.1785 | 2.4317 | -1.62 | 0.33 | 0.37466 | -0.40816 | 0.51094 | -0.2801 | 0.52035 | 0.3795 | 0.81824 | 0.41148 | 0.41196 | 0.42462 | 0.40491 | 0.60291 | 0.43318 | 0.42216
42810.4314 | -747 | 18.5903 | 18.6344 | 18.6301 | 18.6602 | 18.0506 | 16.7284 | 14.8132 | 16.7889 | 17.2738 | 17.3728 | 17.3965 | 16.9686 | 16.0448 | 14.6719 | 15.044 | 15.0011 | 15.5619 | 13.4314 | 13.5638 | 14.1481 |  |  |  | 16.6837 | 16.0287 | 15.1772 | 10.5933 | 10.2144 | 10.0543 | 17.2858 | 16.3956 | 15.2093 | 16.9188 | 16.215 | 15.2461 | 11.0339 | 11.9652 |  | 12.4831 | 11.0869 | 10.9959 | 8.7448 |  | 6.225 | 6.2179 | 5.8205 | 5.933 | 6.0408 | 6.6016 | 7.2489 | 4.5045 | 6.3654 | 4.2779 | 6.6474 | 8.151 | 42.96 | 47.0631 | 43.6247 | 15.4746 |  |  | 0.001535 | 0.017175 | 0.30675 | -0.028914 | 0.20124 | 0.3419 | 0.50916 | 0.23048 | -0.49699 | -1.0712 | -0.30352 | 8.8797 | 8.881 | 2.0088 | 15.9418 | 16.8008 | 17.3464 | 17.6745 | 17.6507 | 16.6546 | 15.0217 | 16.9402 | 17.2623 | 17.5535 | 17.5951 | 17.3491 | 16.5854 | 14.8336 | 6.2026 | 8.2539 | 5.3686 | 5.4548 | 5.4888 | 6.7491 | 7.6509 | 15.9978 | 15.6048 | 15.474 | 14.4179 | 14.3143 | 14.2622 |  |  |  | 10.9674 | 9.6566 | 9.2139 | 9.0301 | -0.13772 | -0.045331 | 12.9953 |  |  | 10.7917 |  |  | 16.9953 | 16.2126 | 15.2039 | 16.5033 | 15.7863 | 14.9243 | 10.9185 | 11.0579 | 11.6105 | 11.5316 | 9.4178 |  | 10.9374 | 8.7928 | 10.3199 | 9.3409 | 11.2867 | 12.4533 |  | 12.5034 |  |  | 11.9941 | 12.7922 | 12.7325 | [6 empty] | 12.6802 |  |  | 11.4296 |  |  | 9.4733 | 10.457 | 12.6756 | 7.8137 | 9.437 | 12.9854 | 8.0549 | 9.7064 | 13.1272 | 9.4115 | 10.6967 | 7.8723 | 10.625 | 8.5456 | 10.4038 | 7.9973 | 10.0473 | 13.6407 | 10.7418 | 10.4534 | 12.1643 | 8.1905 | 9.992 | 13.0869 | 8.1576 | 10.6607 | 9.8816 | 10.0166 | 8.5089 | 10.4831 | -0.12809 | 20.9551 | 0.034233 | 0.048211 | -38.2053 | 2.5723 | -1.55 | 0.33 | 0.045948 | 0.15265 | 0.64513 | -0.19807 | 0.52289 | 0.68155 | 0.83173 | 0.41152 | 0.40853 | 0.42518 | 0.40874 | 0.6061 | 0.4334 | 0.42328
42810.4314 | -746 | 18.5869 | 18.6349 | 18.6351 | 18.6621 | 18.0403 | 16.7212 | 14.809 | 16.7851 | 17.2661 | 17.3663 | 17.4007 | 16.9618 | 16.0347 | 14.6646 | 15.0494 | 15.018 | 15.5607 | 13.4355 | 13.5709 | 14.1569 |  |  |  | 16.6907 | 16.0509 | 15.1856 | 10.6067 | 10.2145 | 10.1152 | 17.2865 | 16.3964 | 15.2102 | 16.9199 | 16.2185 | 15.255 | 11.0312 | 11.9924 |  | 12.4893 | 11.075 | 11.0076 | 8.7233 |  | 6.2368 | 6.2353 | 5.8255 | 5.931 | 6.0305 | 6.5793 | 7.2393 | 4.5227 | 6.3632 | 4.3077 | 6.6435 | 8.1571 | 42.9442 | 47.0539 | 43.6197 | 15.4795 |  |  | 0.094187 | -0.19705 | 0.27455 | 0.019714 | 0.23672 | 0.003484 | 0.64716 | 0.29028 | -0.50089 | -0.083463 | -0.27789 | 8.8813 | 8.8824 | 2.0083 | 15.9416 | 16.7999 | 17.3415 | 17.6665 | 17.6443 | 16.6494 | 15.0255 | 16.936 | 17.2552 | 17.5471 | 17.5932 | 17.3488 | 16.583 | 14.834 | 6.1668 | 8.2759 | 5.3414 | 5.4586 | 5.5035 | 6.7424 | 7.6539 | 15.9996 | 15.6053 | 15.4733 | 14.4181 | 14.3209 | 14.2608 |  |  |  | 10.9595 | 9.6482 | 9.2107 | 9.0005 | -0.092945 | -0.1048 | 12.9935 |  |  | 10.7949 |  |  | 16.9976 | 16.2107 | 15.2052 | 16.5006 | 15.7895 | 14.9148 | 10.9309 | 11.0509 | 11.607 | 11.5259 | 9.4254 |  | 10.9337 | 8.8991 | 10.327 | 9.3299 | 11.2868 | 12.4173 |  | 12.5023 |  |  | 12.0072 | 12.7887 | 12.7435 | [6 empty] | 12.6645 |  |  | 11.433 |  |  | 9.4653 | 10.4577 | 12.6734 | 7.8206 | 9.4306 | 12.9895 | 8.0537 | 9.7134 | 13.1187 | 9.4229 | 10.685 | 7.8713 | 10.624 | 8.5534 | 10.3958 | 7.9816 | 10.0457 | 13.6366 | 10.7314 | 10.4523 | 12.1614 | 8.1977 | 9.994 | 13.0852 | 8.1372 | 10.6466 | 9.8681 | 10.0282 | 8.5012 | 10.4625 | -0.19935 | 20.9544 | 0.033809 | 0.047719 | -38.2002 | 2.7089 | -1.28 | 0.34 | 0.35996 | -0.51707 | 0.61035 | 0.16355 | 0.5671 | 0.068798 | 0.93765 | 0.41119 | 0.40581 | 0.42549 | 0.41193 | 0.60947 | 0.43391 | 0.42384
42810.4314 | -745 | 18.5899 | 18.6284 | 18.63 | 18.6531 | 18.0453 | 16.722 | 14.8014 | 16.7855 | 17.268 | 17.3639 | 17.3901 | 16.9621 | 16.0417 | 14.6575 | 15.0438 | 15.0165 | 15.5593 | 13.4379 | 13.5688 | 14.1628 |  |  |  | 16.6889 | 16.0445 | 15.1809 | 10.6036 | 10.2004 | 10.1272 | 17.2823 | 16.3892 | 15.2072 | 16.9172 | 16.2049 | 15.2492 | 11.0301 | 11.9855 |  | 12.486 | 11.0606 | 11.0003 | 8.7201 |  | 6.2685 | 6.2634 | 5.844 | 5.9473 | 6.031 | 6.5683 | 7.264 | 4.5967 | 6.3805 | 4.3531 | 6.6502 | 8.1605 | 42.9276 | 47.0574 | 43.6181 | 15.4696 |  |  | 0.12113 | 0.042143 | 0.21738 | -0.036142 | 0.10728 | -0.13188 | 0.6005 | 0.22654 | -0.23681 | -0.38201 | -0.1543 | 8.8816 | 8.8826 | 2.0088 | 15.9477 | 16.803 | 17.3431 | 17.6627 | 17.6453 | 16.6482 | 15.0252 | 16.934 | 17.2616 | 17.5448 | 17.5988 | 17.3519 | 16.5843 | 14.8353 | 6.1081 | 8.2668 | 5.3021 | 5.4172 | 5.5211 | 6.7485 | 7.6492 | 16.0035 | 15.6162 | 15.4797 | 14.4215 | 14.318 | 14.2628 |  |  |  | 10.972 | 9.6584 | 9.2088 | 8.9921 | -0.055058 | -0.064528 | 12.9921 |  |  | 10.7867 |  |  | 16.9958 | 16.2036 | 15.2017 | 16.5003 | 15.7871 | 14.9118 | 10.9308 | 11.0492 | 11.6066 | 11.5146 | 9.4136 |  | 10.9335 | 9.0033 | 10.3231 | 9.3159 | 11.2933 | 12.3591 |  | 12.493 |  |  | 12.0045 | 12.7963 | 12.7338 | [6 empty] | 12.6665 |  |  | 11.4462 |  |  | 9.464 | 10.4665 | 12.6772 | 7.8134 | 9.44 | 12.9984 | 8.0609 | 9.7129 | 13.1248 | 9.4296 | 10.6953 | 7.8852 | 10.6158 | 8.5598 | 10.3991 | 7.9821 | 10.0317 | 13.6126 | 10.7208 | 10.4415 | 12.1693 | 8.194 | 9.9925 | 13.0888 | 8.1416 | 10.6345 | 9.8702 | 10.0348 | 8.5074 | 10.4641 | -0.17258 | 20.955 | 0.034865 | 0.04989 | -38.1603 | 2.8403 | -1.11 | 0.26 | 0.40822 | 0.23914 | 0.54313 | -0.22146 | 0.38175 | -0.42328 | 0.9032 | 0.41151 | 0.40279 | 0.42609 | 0.41916 | 0.6133 | 0.43396 | 0.42449
42810.4314 | -744 | 18.5965 | 18.6323 | 18.6284 | 18.6624 | 18.0465 | 16.7292 | 14.8081 | 16.7838 | 17.2736 | 17.3719 | 17.3971 | 16.9642 | 16.0416 | 14.6656 | 15.0509 | 15.0211 | 15.5567 | 13.4491 | 13.5742 | 14.1577 |  |  |  | 16.6801 | 16.0482 | 15.1849 | 10.6111 | 10.2033 | 10.2171 | 17.2837 | 16.4002 | 15.2094 | 16.9161 | 16.2096 | 15.2395 | 11.0309 | 11.9996 |  | 12.4858 | 11.0523 | 10.9868 | 8.7284 |  | 6.278 | 6.2779 | 5.8505 | 5.9467 | 6.0246 | 6.5552 | 7.2859 | 4.6655 | 6.3788 | 4.3616 | 6.6522 | 8.1594 | 42.9171 | 47.0667 | 43.6283 | 15.4761 |  |  | 0.019931 | 0.30236 | 0.26535 | 0.12354 | 0.11713 | 0.19273 | 0.45988 | 0.13586 | -0.56432 | -0.15752 | -0.17655 | 8.8745 | 8.876 | 2.0084 | 15.9467 | 16.8067 | 17.3408 | 17.6657 | 17.6445 | 16.6493 | 15.0169 | 16.9283 | 17.2667 | 17.5453 | 17.5934 | 17.3555 | 16.5863 | 14.8287 | 6.0551 | 8.2434 | 5.2544 | 5.3604 | 5.5116 | 6.7447 | 7.6536 | 16.0053 | 15.6182 | 15.4798 | 14.4251 | 14.3118 | 14.2645 |  |  |  | 10.9668 | 9.6496 | 9.2019 | 8.9866 | -0.082409 | -0.14639 | 12.9895 |  |  | 10.7946 |  |  | 16.9961 | 16.2054 | 15.1955 | 16.4971 | 15.7807 | 14.9145 | 10.9424 | 11.0441 | 11.6056 | 11.5166 | 9.4112 |  | 10.9272 | 9.0821 | 10.3245 | 9.3091 | 11.2855 | 12.324 |  | 12.5059 |  |  | 12.021 | 12.7955 | 12.7297 | [6 empty] | 12.6755 |  |  | 11.4422 |  |  | 9.4628 | 10.4507 | 12.6706 | 7.8019 | 9.4321 | 12.9942 | 8.071 | 9.6981 | 13.1194 | 9.4302 | 10.6811 | 7.8829 | 10.609 | 8.5597 | 10.3835 | 7.9692 | 10.0184 | 13.6036 | 10.7151 | 10.4531 | 12.174 | 8.2033 | 10.001 | 13.0804 | 8.1459 | 10.6362 | 9.8679 | 10.0339 | 8.5006 | 10.4521 | -0.13194 | 20.9541 | 0.035748 | 0.050968 | -38.1938 | 2.9643 | -1.12 | 0.27 | 0.16562 | 0.64057 | 0.60009 | 0.40945 | 0.39889 | 0.51167 | 0.79039 | 0.41137 | 0.40064 | 0.42602 | 0.42461 | 0.61911 | 0.43376 | 0.42447
42810.4314 | -743 | 18.5964 | 18.6379 | 18.6345 | 18.673 | 18.0522 | 16.7286 | 14.8138 | 16.7876 | 17.2783 | 17.379 | 17.4048 | 16.9738 | 16.0422 | 14.6735 | 15.0485 | 15.0192 | 15.5664 | 13.4465 | 13.5693 | 14.1605 |  |  |  | 16.6866 | 16.0354 | 15.1762 | 10.6203 | 10.1945 | 10.3004 | 17.2804 | 16.4003 | 15.2092 | 16.915 | 16.2111 | 15.2416 | 11.0291 | 11.9862 |  | 12.4896 | 11.0415 | 10.977 | 8.7485 |  | 6.2902 | 6.2927 | 5.862 | 5.9477 | 6.0256 | 6.5457 | 7.27 | 4.5821 | 6.3755 | 4.4028 | 6.6521 | 8.1601 | 42.9114 | 47.0579 | 43.6348 | 15.4847 |  |  | 0.005475 | -0.17536 | 0.12539 | 0.4061 | 0.31426 | -0.27645 | 0.42177 | 0.26662 | -0.56179 | -0.85888 | -0.16463 | 8.8796 | 8.8806 | 2.0086 | 15.9422 | 16.7987 | 17.3336 | 17.6665 | 17.6401 | 16.6508 | 15.0132 | 16.9315 | 17.2654 | 17.5497 | 17.5968 | 17.3515 | 16.5866 | 14.8301 | 6.0386 | 8.2417 | 5.2345 | 5.3209 | 5.5376 | 6.7455 | 7.6538 | 16.0016 | 15.6087 | 15.4673 | 14.4225 | 14.3036 | 14.2605 |  |  |  | 10.9596 | 9.6543 | 9.1886 | 8.9834 | 0.16922 | -0.025382 | 12.9922 |  |  | 10.7983 |  |  | 16.9977 | 16.2112 | 15.1907 | 16.496 | 15.7865 | 14.9155 | 10.9583 | 11.0497 | 11.6046 | 11.5104 | 9.4239 |  | 10.9266 | 9.1243 | 10.3267 | 9.3152 | 11.287 | 12.2968 |  | 12.5097 |  |  | 12.0334 | 12.7961 | 12.7394 | [6 empty] | 12.6752 |  |  | 11.4507 |  |  | 9.4636 | 10.455 | 12.6716 | 7.795 | 9.4429 | 13.0084 | 8.0703 | 9.6986 | 13.1284 | 9.4298 | 10.6945 | 7.8858 | 10.602 | 8.5598 | 10.3892 | 7.9596 | 10.0215 | 13.5928 | 10.7183 | 10.44 | 12.1847 | 8.2068 | 9.9951 | 13.0785 | 8.1458 | 10.6322 | 9.8617 | 10.0323 | 8.4939 | 10.4382 | -0.15428 | 20.9543 | 0.035129 | 0.050628 | -38.1345 | 3.0623 | -0.75 | 0.25 | 0.086816 | -0.48784 | 0.41252 | 0.74238 | 0.65337 | -0.6128 | 0.75691 | 0.41099 | 0.39954 | 0.42591 | 0.42653 | 0.62134 | 0.43314 | 0.42432
42810.4314 | -742 | 18.598 | 18.6368 | 18.6363 | 18.6752 | 18.0552 | 16.7341 | 14.8127 | 16.788 | 17.2778 | 17.3786 | 17.4014 | 16.9735 | 16.0494 | 14.6768 | 15.0478 | 15.0166 | 15.5557 | 13.4314 | 13.5612 | 14.1479 |  |  |  | 16.6809 | 16.0286 | 15.1672 | 10.6213 | 10.1877 | 10.3306 | 17.2853 | 16.4048 | 15.2084 | 16.9186 | 16.2115 | 15.2417 | 11.0293 | 11.9592 |  | 12.4875 | 11.036 | 10.9856 | 8.747 |  | 6.3073 | 6.3024 | 5.8683 | 5.9493 | 6.0315 | 6.5428 | 7.2547 | 4.4988 | 6.3702 | 4.4454 | 6.6601 | 8.1613 | 42.9011 | 47.0501 | 43.6342 | 15.4859 |  |  | 0.11456 | -0.032769 | 0.098448 | -0.038114 | 0.14144 | 0.033712 | 0.0459 | 0.44273 | -0.64002 | -0.042762 | -0.26617 | 8.8959 | 8.8972 | 2.0085 | 15.9424 | 16.7942 | 17.3413 | 17.6637 | 17.6427 | 16.6517 | 15.012 | 16.9345 | 17.2634 | 17.5427 | 17.603 | 17.3515 | 16.583 | 14.8347 | 6.0541 | 8.2561 | 5.277 | 5.3503 | 5.5029 | 6.7467 | 7.6529 | 16.0062 | 15.6095 | 15.4773 | 14.4294 | 14.3146 | 14.2611 |  |  |  | 10.9709 | 9.6585 | 9.1967 | 8.9948 | -0.061744 | -0.10857 | 12.9796 |  |  | 10.7883 |  |  | 16.9902 | 16.1969 | 15.1881 | 16.4876 | 15.7787 | 14.8982 | 10.9527 | 11.0414 | 11.5857 | 11.4953 | 9.4217 |  | 10.9245 | 9.1031 | 10.3204 | 9.3126 | 11.2875 | 12.26 |  | 12.5129 |  |  | 12.0395 | 12.7953 | 12.7581 | [6 empty] | 12.6877 |  |  | 11.4469 |  |  | 9.4638 | 10.4512 | 12.6578 | 7.7976 | 9.4424 | 13.0065 | 8.0698 | 9.7028 | 13.1263 | 9.4293 | 10.6931 | 7.8805 | 10.6026 | 8.5575 | 10.3881 | 7.9622 | 10.0336 | 13.5915 | 10.7247 | 10.4385 | 12.2077 | 8.214 | 10.0035 | 13.0924 | 8.1506 | 10.6439 | 9.871 | 10.0409 | 8.5042 | 10.4475 | -0.50424 | 20.9542 | 0.035163 | 0.050042 | -38.2115 | 3.0909 | -0.6 | 0.28 | 0.39714 | -0.21089 | 0.36553 | -0.22744 | 0.43833 | 0.21399 | 0.2497 | 0.41099 | 0.39992 | 0.42599 | 0.42495 | 0.61651 | 0.43318 | 0.42438
42810.4315 | -741 | 18.5921 | 18.6373 | 18.6377 | 18.6715 | 18.0492 | 16.7288 | 14.8074 | 16.792 | 17.2748 | 17.3761 | 17.3984 | 16.9731 | 16.0463 | 14.6812 | 15.0527 | 15.0134 | 15.5559 | 13.433 | 13.5618 | 14.1483 |  |  |  | 16.6835 | 16.0312 | 15.1692 | 10.6226 | 10.1897 | 10.3518 | 17.2929 | 16.4072 | 15.2136 | 16.9268 | 16.2208 | 15.2435 | 11.0286 | 11.9494 |  | 12.4895 | 11.03 | 10.9868 | 8.7482 |  | 6.3028 | 6.3055 | 5.8649 | 5.9526 | 6.0256 | 6.5215 | 7.2292 | 4.4807 | 6.3665 | 4.3824 | 6.6561 | 8.1589 | 42.8755 | 47.0437 | 43.6327 | 15.4962 |  |  | 0.068559 | 0.003375 | 0.23381 | -0.21816 | 0.14539 | 0.11191 | -0.49754 | 0.39936 | -0.50419 | -0.26536 | -0.52726 | 8.8898 | 8.891 | 2.0083 | 15.9389 | 16.7905 | 17.3371 | 17.6594 | 17.6338 | 16.6386 | 15.0079 | 16.9273 | 17.2618 | 17.5445 | 17.5932 | 17.3436 | 16.5809 | 14.8282 | 6.059 | 8.2672 | 5.2928 | 5.3243 | 5.4515 | 6.742 | 7.6545 | 16.011 | 15.6197 | 15.4851 | 14.4257 | 14.3147 | 14.2663 |  |  |  | 10.9709 | 9.6616 | 9.2044 | 9.0083 | -0.092945 | -0.18422 | 12.9851 |  |  | 10.7947 |  |  | 16.9902 | 16.1976 | 15.1937 | 16.4842 | 15.7803 | 14.9019 | 10.9601 | 11.0331 | 11.5863 | 11.492 | 9.416 |  | 10.9282 | 9.0252 | 10.3277 | 9.308 | 11.2892 | 12.2336 |  | 12.5107 |  |  | 12.0267 | 12.8003 | 12.7685 | [6 empty] | 12.6816 |  |  | 11.4474 |  |  | 9.457 | 10.4464 | 12.6492 | 7.7971 | 9.4395 | 13.0127 | 8.0684 | 9.7 | 13.13 | 9.4246 | 10.6832 | 7.8852 | 10.6013 | 8.555 | 10.3737 | 7.9621 | 10.0316 | 13.5882 | 10.7153 | 10.4265 | 12.205 | 8.213 | 9.9884 | 13.0941 | 8.1371 | 10.6458 | 9.8626 | 10.0365 | 8.4898 | 10.4249 | -0.22343 | 20.9548 | 0.034583 | 0.048913 | -38.1443 | 3.0985 | -0.5 | 0.25 | 0.30724 | 0.06768 | 0.56332 | -0.54414 | 0.44438 | 0.38987 | -0.82206 | 0.41127 | 0.40233 | 0.42618 | 0.42386 | 0.61495 | 0.43313 | 0.424
42810.4315 | -740 | 18.5915 | 18.6366 | 18.6345 | 18.6659 | 18.0424 | 16.7192 | 14.8074 | 16.7859 | 17.2727 | 17.3718 | 17.3983 | 16.9712 | 16.0459 | 14.6775 | 15.0531 | 15.0232 | 15.5664 | 13.441 | 13.5694 | 14.1569 |  |  |  | 16.6879 | 16.0373 | 15.1811 | 10.6288 | 10.185 | 10.3686 | 17.2947 | 16.4089 | 15.2161 | 16.9267 | 16.2169 | 15.2505 | 11.0308 | 11.9379 |  | 12.4943 | 11.0257 | 10.9763 | 8.7608 |  | 6.3149 | 6.3209 | 5.8869 | 5.9547 | 6.0137 | 6.5029 | 7.1851 | 4.552 | 6.3629 | 4.3551 | 6.6569 | 8.1679 | 42.8704 | 47.0363 | 43.6262 | 15.5128 |  |  | 0.019931 | 0.092083 | 0.18584 | 0.090026 | 0.19533 | -0.44204 | -0.24455 | 0.45193 | -0.54 | -0.28529 | -0.28127 | 8.8831 | 8.8844 | 2.0086 | 15.9437 | 16.7988 | 17.3399 | 17.6604 | 17.6379 | 16.6475 | 15.0157 | 16.9336 | 17.2582 | 17.5482 | 17.591 | 17.3514 | 16.5827 | 14.8314 | 6.0639 | 8.29 | 5.2696 | 5.3302 | 5.4359 | 6.7455 | 7.6548 | 16.0127 | 15.6127 | 15.4782 | 14.428 | 14.3183 | 14.2638 |  |  |  | 10.9712 | 9.6505 | 9.2031 | 9.0045 | 0.0016696 | -0.24934 | 12.9891 |  |  | 10.8011 |  |  | 16.9932 | 16.2019 | 15.2003 | 16.4933 | 15.7822 | 14.9137 | 10.9706 | 11.0354 | 11.5918 | 11.5004 | 9.392 |  | 10.9248 | 8.8877 | 10.3271 | 9.3042 | 11.2925 | 12.2176 |  | 12.5056 |  |  | 12.0118 | 12.8069 | 12.7777 | [6 empty] | 12.6906 |  |  | 11.4342 |  |  | 9.4632 | 10.4543 | 12.6534 | 7.8019 | 9.4384 | 13.0179 | 8.0789 | 9.7084 | 13.1404 | 9.4241 | 10.6854 | 7.8877 | 10.6048 | 8.552 | 10.3761 | 7.9864 | 10.0397 | 13.5858 | 10.7202 | 10.4263 | 12.2078 | 8.2099 | 9.9788 | 13.087 | 8.1378 | 10.6379 | 9.8596 | 10.0393 | 8.4914 | 10.4262 | -0.071082 | 20.9543 | 0.033998 | 0.049231 | -38.1647 | 3.1084 | -0.87 | 0.3 | 0.16566 | 0.35353 | 0.50224 | 0.34956 | 0.51506 | -0.77483 | -0.57631 | 0.41182 | 0.40613 | 0.42639 | 0.42372 | 0.61756 | 0.43285 | 0.42412
42810.4315 | -739 | 18.6085 | 18.6539 | 18.6393 | 18.67 | 18.0558 | 16.7305 | 14.808 | 16.7965 | 17.2763 | 17.3802 | 17.4039 | 16.9813 | 16.0523 | 14.6827 | 15.0586 | 15.0296 | 15.5651 | 13.4409 | 13.5733 | 14.1572 |  |  |  | 16.6862 | 16.0364 | 15.1816 | 10.637 | 10.1792 | 10.3679 | 17.2898 | 16.4014 | 15.2057 | 16.9194 | 16.2181 | 15.241 | 11.0198 | 11.9279 |  | 12.4811 | 11.0092 | 10.9668 | 8.7658 |  | 6.3156 | 6.3179 | 5.884 | 5.9275 | 5.9747 | 6.468 | 7.1106 | 4.528 | 6.3513 | 4.4029 | 6.6481 | 8.1606 | 42.864 | 47.0186 | 43.6195 | 15.52 |  |  | 0.12902 | -0.20624 | 0.32975 | 0.23656 | -0.1766 | -0.0918 | -0.39634 | 0.37045 | -0.61064 | -0.32893 | -0.057333 | 8.8826 | 8.8836 | 2.0084 | 15.9464 | 16.8038 | 17.3406 | 17.6643 | 17.6413 | 16.6516 | 15.0166 | 16.9393 | 17.2591 | 17.5502 | 17.5955 | 17.3444 | 16.5799 | 14.8394 | 6.0581 | 8.27 | 5.2599 | 5.3489 | 5.413 | 6.7384 | 7.6553 | 16.0135 | 15.6113 | 15.474 | 14.4275 | 14.3188 | 14.2623 |  |  |  | 10.9677 | 9.6535 | 9.2094 | 8.9943 | -0.070253 | 0.012446 | 12.9923 |  |  | 10.8062 |  |  | 16.9931 | 16.2004 | 15.1982 | 16.4973 | 15.7801 | 14.9104 | 10.9708 | 11.0392 | 11.596 | 11.5018 | 9.3695 |  | 10.9166 | 8.7489 | 10.3225 | 9.314 | 11.2786 | 12.2071 |  | 12.4957 |  |  | 12.0071 | 12.8113 | 12.7869 | [6 empty] | 12.6844 |  |  | 11.4028 |  |  | 9.469 | 10.4586 | 12.6579 | 7.8098 | 9.4342 | 13.0305 | 8.086 | 9.7151 | 13.135 | 9.4302 | 10.6863 | 7.8992 | 10.6152 | 8.5591 | 10.3764 | 8.0047 | 10.0343 | 13.5864 | 10.7227 | 10.4337 | 12.2103 | 8.2039 | 9.9746 | 13.0801 | 8.1131 | 10.6232 | 9.856 | 10.0408 | 8.4965 | 10.4247 | -0.099009 | 20.9551 | 0.035226 | 0.051359 | -38.1007 | 3.116 | -0.84 | 0.36 | 0.42148 | -0.52908 | 0.669 | 0.56664 | -0.48972 | -0.35308 | -0.73364 | 0.41218 | 0.40983 | 0.42566 | 0.42354 | 0.61869 | 0.43235 | 0.42428
42810.4315 | -738 | 18.5956 | 18.6404 | 18.6309 | 18.6619 | 18.0421 | 16.7276 | 14.7995 | 16.787 | 17.2656 | 17.3652 | 17.3922 | 16.9639 | 16.0349 | 14.6692 | 15.0645 | 15.0229 | 15.5651 | 13.4439 | 13.5716 | 14.1587 |  |  |  | 16.6864 | 16.0361 | 15.1811 | 10.6378 | 10.1784 | 10.3756 | 17.2938 | 16.4013 | 15.2189 | 16.9204 | 16.2212 | 15.2508 | 11.0255 | 11.9211 |  | 12.4839 | 11.0063 | 10.9584 | 8.7523 |  | 6.3334 | 6.3312 | 5.8917 | 5.9153 | 5.9441 | 6.4454 | 7.0445 | 4.4309 | 6.3606 | 4.4421 | 6.6472 | 8.1645 | 42.8465 | 47.0057 | 43.6054 | 15.5228 |  |  | 0.12507 | 0.005343 | 0.41386 | 0.059142 | -0.055692 | 0.21244 | 0.18455 | 0.52159 | -0.1111 | -0.6944 | -0.2767 | 8.8823 | 8.8832 | 2.0088 | 15.9558 | 16.8107 | 17.3478 | 17.6689 | 17.6494 | 16.6558 | 15.0219 | 16.9352 | 17.2679 | 17.5561 | 17.5992 | 17.3504 | 16.5924 | 14.8405 | 6.0702 | 8.262 | 5.1934 | 5.3324 | 5.4166 | 6.7392 | 7.6516 | 16.0197 | 15.6149 | 15.4784 | 14.4298 | 14.3176 | 14.2698 |  |  |  | 10.9649 | 9.649 | 9.2066 | 8.9753 | -0.064986 | -0.098592 | 12.9956 |  |  | 10.8064 |  |  | 16.9937 | 16.2039 | 15.1926 | 16.4964 | 15.7826 | 14.907 | 10.9714 | 11.0393 | 11.5999 | 11.5046 | 9.3406 |  | 10.9213 | 8.6324 | 10.3286 | 9.3164 | 11.288 | 12.2191 |  | 12.4988 |  |  | 12.0192 | 12.8135 | 12.7939 | [6 empty] | 12.6752 |  |  | 11.3929 |  |  | 9.4694 | 10.4616 | 12.6592 | 7.8201 | 9.4429 | 13.0382 | 8.0931 | 9.7163 | 13.1319 | 9.4312 | 10.6826 | 7.8939 | 10.6279 | 8.5615 | 10.3713 | 8.0035 | 10.0136 | 13.5913 | 10.7206 | 10.4404 | 12.2092 | 8.2074 | 9.9661 | 13.081 | 8.0618 | 10.5937 | 9.8583 | 10.0486 | 8.4938 | 10.4171 | 0.005188 | 20.9539 | 0.036081 | 0.052336 | -38.2234 | 3.1195 | -1.01 | 0.37 | 0.41499 | 0.08516 | 0.7495 | 0.28333 | -0.275 | 0.5371 | 0.5006 | 0.41313 | 0.41327 | 0.4259 | 0.42229 | 0.62565 | 0.43291 | 0.42472
42810.4315 | -737 | 18.597 | 18.6368 | 18.6274 | 18.6638 | 18.0437 | 16.7247 | 14.802 | 16.7855 | 17.2673 | 17.3692 | 17.3927 | 16.961 | 16.0399 | 14.6715 | 15.062 | 15.0161 | 15.5687 | 13.4455 | 13.5699 | 14.1604 |  |  |  | 16.6817 | 16.0309 | 15.1804 | 10.6378 | 10.1713 | 10.383 | 17.2951 | 16.4055 | 15.2142 | 16.9241 | 16.2237 | 15.2499 | 11.0291 | 11.9145 |  | 12.4926 | 10.998 | 10.964 | 8.7537 |  | 6.3452 | 6.3332 | 5.8935 | 5.9061 | 5.9268 | 6.4105 | 6.9614 | 4.2582 | 6.3428 | 4.4321 | 6.6411 | 8.1637 | 42.8315 | 46.9989 | 43.5706 | 15.5171 |  |  | 0.035047 | 0.039515 | 0.29427 | -0.036798 | -0.12732 | 0.03568 | 0.47631 | 0.32051 | -0.38432 | -0.52027 | -0.39632 | 8.8798 | 8.881 | 2.0085 | 15.9579 | 16.8078 | 17.3467 | 17.6699 | 17.6474 | 16.6537 | 15.0185 | 16.934 | 17.26 | 17.5515 | 17.5978 | 17.3553 | 16.5867 | 14.8325 | 6.057 | 8.2443 | 5.1653 | 5.4205 | 5.3933 | 6.7361 | 7.6478 | 16.028 | 15.6272 | 15.4869 | 14.4302 | 14.3302 | 14.2774 |  |  |  | 10.9738 | 9.6497 | 9.2239 | 8.954 | -0.2299 | 0.047075 | 12.9902 |  |  | 10.8026 |  |  | 16.9897 | 16.2083 | 15.1935 | 16.4934 | 15.7817 | 14.9076 | 10.9635 | 11.0325 | 11.6061 | 11.5115 | 9.3257 |  | 10.9196 | 8.5593 | 10.3301 | 9.3316 | 11.2886 | 12.2331 |  | 12.4901 |  |  | 12.0262 | 12.8097 | 12.798 | [6 empty] | 12.6749 |  |  | 11.3904 |  |  | 9.4683 | 10.4595 | 12.6559 | 7.8133 | 9.444 | 13.0337 | 8.0891 | 9.703 | 13.1207 | 9.4266 | 10.6791 | 7.8934 | 10.631 | 8.5504 | 10.3589 | 7.9963 | 9.9412 | 13.5905 | 10.7136 | 10.4379 | 12.202 | 8.2043 | 9.9703 | 13.0784 | 7.9715 | 10.5287 | 9.853 | 10.0528 | 8.4854 | 10.4074 | -0.21206 | 20.9537 | 0.035771 | 0.052162 | -38.2745 | 3.1206 | -0.96 | 0.36 | 0.21968 | 0.23159 | 0.632 | -0.22349 | -0.41576 | 0.2201 | 0.80418 | 0.41349 | 0.41535 | 0.4255 | 0.42341 | 0.62834 | 0.43299 | 0.4256
42810.4315 | -736 | 18.6022 | 18.6397 | 18.6257 | 18.6652 | 18.0446 | 16.7179 | 14.802 | 16.7836 | 17.2701 | 17.3698 | 17.3942 | 16.9638 | 16.0455 | 14.6611 | 15.0697 | 15.0329 | 15.5729 | 13.4447 | 13.5765 | 14.1641 |  |  |  | 16.6916 | 16.0455 | 15.1832 | 10.644 | 10.1713 | 10.3922 | 17.3006 | 16.407 | 15.2246 | 16.9322 | 16.2235 | 15.2535 | 11.0348 | 11.8802 |  | 12.491 | 10.985 | 10.9577 | 8.7608 |  | 6.3661 | 6.3511 | 5.9029 | 5.907 | 5.9275 | 6.3991 | 6.9198 | 4.1408 | 6.3454 | 4.3547 | 6.6466 | 8.1708 | 42.8239 | 46.9787 | 43.5374 | 15.515 |  |  | -0.10098 | 0.035571 | 0.12144 | 0.092654 | -0.04912 | -0.13254 | 0.33897 | 0.27582 | -0.44523 | 0.37873 | -0.061307 | 8.88 | 8.8813 | 2.0086 | 15.9527 | 16.8094 | 17.3435 | 17.6784 | 17.6504 | 16.656 | 15.0227 | 16.9325 | 17.2627 | 17.5454 | 17.5907 | 17.353 | 16.5915 | 14.8333 | 6.0182 | 8.2448 | 5.1377 | 5.4194 | 5.4292 | 6.7365 | 7.6442 | 16.0158 | 15.6156 | 15.4744 | 14.4138 | 14.3169 | 14.2666 |  |  |  | 10.9569 | 9.625 | 9.2035 | 8.9332 | -0.028923 | -0.03291 | 12.9914 |  |  | 10.7988 |  |  | 16.9926 | 16.2088 | 15.1949 | 16.4938 | 15.7781 | 14.9089 | 10.9519 | 11.0336 | 11.6169 | 11.5255 | 9.3281 |  | 10.9277 | 8.4471 | 10.3299 | 9.3604 | 11.2882 | 12.2559 |  | 12.4947 |  |  | 12.0355 | 12.8069 | 12.7913 | [6 empty] | 12.6668 |  |  | 11.395 |  |  | 9.4685 | 10.4612 | 12.6428 | 7.7946 | 9.436 | 13.028 | 8.0924 | 9.6996 | 13.1128 | 9.4123 | 10.6724 | 7.8831 | 10.6243 | 8.5384 | 10.3514 | 7.9659 | 9.8715 | 13.5848 | 10.7235 | 10.439 | 12.1935 | 8.201 | 9.9751 | 13.0761 | 7.8874 | 10.4818 | 9.849 | 10.0553 | 8.4726 | 10.4004 | 0.078183 | 20.9532 | 0.035553 | 0.051178 | -38.1951 | 3.121 | -1.03 | 0.31 | -0.3729 | 0.21974 | 0.40602 | 0.35464 | -0.25824 | -0.4242 | 0.67839 | 0.41369 | 0.41846 | 0.42469 | 0.42776 | 0.63098 | 0.43298 | 0.42563
42810.4315 | -735 | 18.6027 | 18.6405 | 18.6279 | 18.6632 | 18.0428 | 16.7225 | 14.8034 | 16.7818 | 17.2727 | 17.368 | 17.386 | 16.9615 | 16.0412 | 14.6637 | 15.0677 | 15.0278 | 15.5684 | 13.4456 | 13.5756 | 14.1635 |  |  |  | 16.6932 | 16.0461 | 15.1852 | 10.6369 | 10.1653 | 10.3826 | 17.3055 | 16.4021 | 15.2158 | 16.9301 | 16.2167 | 15.2479 | 11.0289 | 11.8486 |  | 12.4927 | 10.966 | 10.9375 | 8.747 |  | 6.3573 | 6.3296 | 5.897 | 5.8882 | 5.9053 | 6.3681 | 6.8791 | 4.1384 | 6.338 | 4.1605 | 6.6354 | 8.1715 | 42.807 | 46.952 | 43.5024 | 15.5121 |  |  | 0.021903 | 0.046743 | 0.14642 | -0.13142 | -0.13717 | -0.15422 | 0.31006 | 0.20288 | -0.30161 | -0.59223 | -0.36631 | 8.8796 | 8.8807 | 2.0087 | 15.9601 | 16.808 | 17.3509 | 17.6752 | 17.6456 | 16.647 | 15.0172 | 16.931 | 17.2695 | 17.5555 | 17.5876 | 17.3487 | 16.5811 | 14.8345 | 6.031 | 8.226 | 5.1019 | 5.3937 | 5.4375 | 6.7333 | 7.6497 | 16.0144 | 15.6153 | 15.4748 | 14.4255 | 14.3097 | 14.2733 |  |  |  | 10.9531 | 9.6275 | 9.2144 | 8.9216 | -0.06762 | -0.019172 | 12.9917 |  |  | 10.7954 |  |  | 16.9937 | 16.1975 | 15.1874 | 16.4923 | 15.7757 | 14.899 | 10.9325 | 11.0265 | 11.6196 | 11.5335 | 9.3365 |  | 10.9144 | 8.2929 | 10.3156 | 9.3646 | 11.2852 | 12.2812 |  | 12.4985 |  |  | 12.0462 | 12.8067 | 12.7884 | [6 empty] | 12.6683 |  |  | 11.4054 |  |  | 9.4628 | 10.4597 | 12.6503 | 7.7791 | 9.4427 | 13.0244 | 8.0911 | 9.6974 | 13.12 | 9.4111 | 10.674 | 7.8698 | 10.6274 | 8.532 | 10.349 | 7.9268 | 9.8432 | 13.5779 | 10.7211 | 10.4514 | 12.1986 | 8.21 | 9.987 | 13.0877 | 7.8574 | 10.476 | 9.8479 | 10.0661 | 8.4838 | 10.3926 | 0.070672 | 20.9534 | 0.035094 | 0.049521 | -38.2882 | 3.1212 | -1.41 | 0.4 | 0.17367 | 0.25188 | 0.4458 | -0.42235 | -0.43152 | -0.45756 | 0.64878 | 0.41302 | 0.42227 | 0.42447 | 0.42596 | 0.6356 | 0.43317 | 0.42582
42810.4315 | -734 | 18.6038 | 18.6387 | 18.6355 | 18.6667 | 18.0512 | 16.7294 | 14.8012 | 16.7876 | 17.2711 | 17.3701 | 17.3899 | 16.965 | 16.0444 | 14.6717 | 15.064 | 15.0277 | 15.5673 | 13.4458 | 13.564 | 14.1578 |  |  |  | 16.6909 | 16.0434 | 15.1762 | 10.6413 | 10.1561 | 10.3699 | 17.3111 | 16.4104 | 15.219 | 16.9286 | 16.2184 | 15.2521 | 11.0335 | 11.8063 |  | 12.4939 | 10.964 | 10.9282 | 8.7349 |  | 6.3562 | 6.3331 | 5.8913 | 5.8727 | 5.8748 | 6.3426 | 6.8375 | 4.156 | 6.3368 | 4.0403 | 6.6296 | 8.1682 | 42.7958 | 46.9179 | 43.467 | 15.5059 |  |  | 0.14347 | -0.15302 | 0.024192 | -0.032198 | -0.080004 | -0.20022 | 0.47631 | 0.2686 | -0.71942 | -0.26389 | -0.18768 | 8.8812 | 8.8824 | 2.0083 | 15.9561 | 16.8113 | 17.3416 | 17.6684 | 17.6433 | 16.6524 | 15.016 | 16.9321 | 17.2593 | 17.5441 | 17.5873 | 17.3475 | 16.5804 | 14.8283 | 5.9998 | 8.2321 | 5.0476 | 5.3219 | 5.416 | 6.7354 | 7.6487 | 16.0196 | 15.6171 | 15.4803 | 14.4294 | 14.3177 | 14.2649 |  |  |  | 10.9628 | 9.6309 | 9.2151 | 8.9308 | -0.043713 | -0.11214 | 12.9909 |  |  | 10.7937 |  |  | 16.9937 | 16.1975 | 15.1922 | 16.4899 | 15.7794 | 14.9009 | 10.9066 | 11.0263 | 11.6269 | 11.5438 | 9.362 |  | 10.9077 | 8.1579 | 10.3155 | 9.3682 | 11.2776 | 12.2924 |  | 12.5034 |  |  | 12.0325 | 12.7979 | 12.7878 | [6 empty] | 12.6623 |  |  | 11.4224 |  |  | 9.4624 | 10.4647 | 12.655 | 7.7712 | 9.4385 | 13.0266 | 8.0975 | 9.7108 | 13.1173 | 9.4068 | 10.6902 | 7.8439 | 10.6347 | 8.5281 | 10.3442 | 7.8987 | 9.8309 | 13.5855 | 10.7238 | 10.4456 | 12.2024 | 8.2233 | 9.9849 | 13.0882 | 7.8349 | 10.4804 | 9.8508 | 10.066 | 8.4881 | 10.3867 | 0.20723 | 20.9532 | 0.034279 | 0.048037 | -38.3133 | 3.1212 | -1.51 | 0.3 | 0.44447 | -0.45574 | 0.18121 | -0.20905 | -0.32954 | -0.52133 | 0.80408 | 0.41209 | 0.42602 | 0.42412 | 0.42967 | 0.64151 | 0.43366 | 0.42589
42810.4316 | -733 | 18.6153 | 18.6436 | 18.6313 | 18.6712 | 18.0558 | 16.7265 | 14.8066 | 16.7913 | 17.2703 | 17.3766 | 17.3971 | 16.9678 | 16.0453 | 14.6718 | 15.0697 | 15.025 | 15.5671 | 13.4394 | 13.5713 | 14.1625 |  |  |  | 16.6862 | 16.0309 | 15.1752 | 10.6462 | 10.142 | 10.358 | 17.3123 | 16.4195 | 15.2211 | 16.932 | 16.2237 | 15.2554 | 11.0342 | 11.7724 |  | 12.4956 | 10.9684 | 10.9133 | 8.7192 |  | 6.361 | 6.3317 | 5.8819 | 5.8622 | 5.8636 | 6.3194 | 6.803 | 4.1325 | 6.3384 | 3.9839 | 6.6422 | 8.1717 | 42.7846 | 46.8996 | 43.4333 | 15.4925 |  |  | -0.022121 | -0.10965 | 0.053764 | 0.11434 | -0.17003 | -0.083912 | 0.25618 | 0.22851 | -0.64139 | -0.62391 | -0.27392 | 8.8833 | 8.8845 | 2.0087 | 15.9662 | 16.8162 | 17.3462 | 17.6775 | 17.6514 | 16.6637 | 15.0205 | 16.9322 | 17.2634 | 17.5492 | 17.6019 | 17.3522 | 16.5792 | 14.8332 | 6.0025 | 8.2354 | 4.9943 | 5.2968 | 5.3965 | 6.7362 | 7.6495 | 16.0174 | 15.6209 | 15.4813 | 14.4249 | 14.3143 | 14.2662 |  |  |  | 10.9591 | 9.6335 | 9.2134 | 8.936 | -0.088285 | -0.10292 | 12.9913 |  |  | 10.7907 |  |  | 16.9914 | 16.2018 | 15.1963 | 16.4923 | 15.7858 | 14.9088 | 10.8849 | 11.0215 | 11.6299 | 11.5543 | 9.3806 |  | 10.9225 | 8.0792 | 10.3185 | 9.3587 | 11.2862 | 12.3169 |  | 12.513 |  |  | 12.0003 | 12.7953 | 12.7973 | [6 empty] | 12.6671 |  |  | 11.4273 |  |  | 9.4722 | 10.4798 | 12.6617 | 7.7796 | 9.4512 | 13.0197 | 8.1194 | 9.7007 | 13.1331 | 9.4159 | 10.6862 | 7.8337 | 10.6616 | 8.5432 | 10.3554 | 7.891 | 9.8154 | 13.5829 | 10.7208 | 10.4486 | 12.1936 | 8.2132 | 9.9921 | 13.0905 | 7.8288 | 10.4745 | 9.8506 | 10.0554 | 8.4841 | 10.3783 | -0.064726 | 20.9536 | 0.033573 | 0.047299 | -38.2245 | 3.1213 | -1.27 | 0.35 | -0.17452 | -0.38579 | 0.27014 | 0.39395 | -0.48039 | -0.33748 | 0.58966 | 0.41206 | 0.4283 | 0.42467 | 0.42947 | 0.64753 | 0.43412 | 0.42562
42810.4316 | -732 | 18.6026 | 18.6469 | 18.6261 | 18.6595 | 18.0436 | 16.7187 | 14.8038 | 16.7771 | 17.2719 | 17.3682 | 17.3838 | 16.9651 | 16.0356 | 14.6632 | 15.0658 | 15.0327 | 15.5673 | 13.4419 | 13.5711 | 14.1621 |  |  |  | 16.6825 | 16.0325 | 15.1762 | 10.6313 | 10.1278 | 10.3503 | 17.3091 | 16.4142 | 15.2165 | 16.937 | 16.2253 | 15.249 | 11.0344 | 11.7204 |  | 12.4946 | 10.9734 | 10.9039 | 8.6875 |  | 6.358 | 6.3255 | 5.869 | 5.8473 | 5.8492 | 6.2935 | 6.7641 | 4.1075 | 6.3333 | 3.9835 | 6.6465 | 8.1768 | 42.7714 | 46.9035 | 43.3953 | 15.4902 |  |  | -0.035921 | -0.12477 | 0.15102 | 0.25496 | 0.14736 | -0.31259 | 0.35803 | 0.19303 | -0.46897 | -1.3062 | -0.39175 | 8.8825 | 8.8839 | 2.0084 | 15.9642 | 16.8177 | 17.3476 | 17.6752 | 17.6538 | 16.6612 | 15.0274 | 16.9383 | 17.2676 | 17.5528 | 17.6034 | 17.3513 | 16.5893 | 14.8348 | 5.9711 | 8.2277 | 4.9512 | 5.2507 | 5.388 | 6.7295 | 7.6459 | 16.0306 | 15.6231 | 15.4918 | 14.4315 | 14.3143 | 14.2675 |  |  |  | 10.9651 | 9.6319 | 9.2128 | 8.9432 | -0.024871 | -0.13943 | 12.9858 |  |  | 10.7957 |  |  | 16.9859 | 16.1971 | 15.1873 | 16.488 | 15.7799 | 14.9052 | 10.8719 | 11.0119 | 11.6339 | 11.567 | 9.3792 |  | 10.9187 | 7.9817 | 10.3224 | 9.3448 | 11.2974 | 12.3176 |  | 12.5085 |  |  | 11.9599 | 12.802 | 12.799 | [6 empty] | 12.6562 |  |  | 11.4186 |  |  | 9.4733 | 10.4718 | 12.6676 | 7.764 | 9.4486 | 13.0238 | 8.1245 | 9.6968 | 13.1321 | 9.4079 | 10.7 | 7.8399 | 10.6635 | 8.5319 | 10.361 | 7.8876 | 9.8081 | 13.5868 | 10.7192 | 10.4348 | 12.1942 | 8.2145 | 9.9758 | 13.0833 | 7.8401 | 10.4789 | 9.8543 | 10.0546 | 8.4791 | 10.3658 | -0.024087 | 20.9537 | 0.034141 | 0.046221 | -38.1683 | 3.1213 | -1.12 | 0.39 | -0.22239 | -0.41151 | 0.45274 | 0.58827 | 0.4472 | -0.65133 | 0.69706 | 0.41198 | 0.43114 | 0.42542 | 0.43218 | 0.6519 | 0.435 | 0.42562
42810.4316 | -731 | 18.6133 | 18.6434 | 18.6374 | 18.6576 | 18.0456 | 16.7292 | 14.8092 | 16.7904 | 17.2694 | 17.3733 | 17.3896 | 16.9659 | 16.0403 | 14.6638 | 15.0676 | 15.0299 | 15.5692 | 13.445 | 13.577 | 14.1585 |  |  |  | 16.681 | 16.0355 | 15.1713 | 10.6377 | 10.1268 | 10.3506 | 17.3019 | 16.4134 | 15.2159 | 16.9198 | 16.219 | 15.2478 | 11.0302 | 11.6804 |  | 12.4814 | 10.9717 | 10.8879 | 8.6444 |  | 6.3525 | 6.3089 | 5.8652 | 5.844 | 5.8428 | 6.2773 | 6.7327 | 4.1623 | 6.3297 | 4.0223 | 6.6383 | 8.1723 | 42.7487 | 46.9066 | 43.3575 | 15.475 |  |  | 0.004819 | -0.16748 | 0.10896 | -0.41661 | -0.037292 | -0.22782 | 0.40337 | 0.29488 | -0.34131 | -0.57419 | -0.37029 | 8.881 | 8.882 | 2.0087 | 15.9735 | 16.8243 | 17.3503 | 17.674 | 17.6571 | 16.6605 | 15.0275 | 16.9444 | 17.274 | 17.5588 | 17.6041 | 17.3589 | 16.5917 | 14.8377 | 5.9144 | 8.2012 | 4.9096 | 5.1817 | 5.3312 | 6.7102 | 7.6311 | 16.0298 | 15.6187 | 15.4784 | 14.4246 | 14.3119 | 14.2682 |  |  |  | 10.958 | 9.6277 | 9.2121 | 8.9684 | 0.0077476 | -0.027264 | 12.9856 |  |  | 10.801 |  |  | 16.989 | 16.2012 | 15.1891 | 16.4862 | 15.783 | 14.9065 | 10.85 | 11.0137 | 11.6437 | 11.5752 | 9.3665 |  | 10.9162 | 7.9057 | 10.3098 | 9.3375 | 11.2806 | 12.3256 |  | 12.4956 |  |  | 11.9024 | 12.7939 | 12.7989 | [6 empty] | 12.6639 |  |  | 11.4221 |  |  | 9.4707 | 10.4685 | 12.6561 | 7.7484 | 9.4448 | 13.0167 | 8.1204 | 9.6898 | 13.1367 | 9.3988 | 10.6884 | 7.8227 | 10.6623 | 8.5264 | 10.3468 | 7.91 | 9.8335 | 13.5908 | 10.7145 | 10.4382 | 12.1932 | 8.2178 | 9.9743 | 13.0907 | 7.8735 | 10.4883 | 9.8619 | 10.0577 | 8.4891 | 10.3589 | -0.065881 | 20.9509 | 0.034302 | 0.048015 | -38.2164 | 3.1213 | -1 | 0.35 | 0.081456 | -0.47676 | 0.38456 | -0.75195 | -0.22496 | -0.55603 | 0.73987 | 0.41225 | 0.43284 | 0.42507 | 0.43624 | 0.6548 | 0.43607 | 0.42468
42810.4316 | -730 | 18.61 | 18.6442 | 18.6424 | 18.664 | 18.0471 | 16.7276 | 14.8063 | 16.7888 | 17.2747 | 17.3765 | 17.393 | 16.9684 | 16.0509 | 14.666 | 15.0615 | 15.0212 | 15.5704 | 13.4397 | 13.5706 | 14.1528 |  |  |  | 16.681 | 16.0313 | 15.1694 | 10.6381 | 10.1132 | 10.3587 | 17.3044 | 16.4141 | 15.2174 | 16.9294 | 16.2225 | 15.2508 | 11.0306 | 11.6646 |  | 12.4826 | 10.9815 | 10.8796 | 8.6483 |  | 6.3547 | 6.3051 | 5.8514 | 5.838 | 5.8368 | 6.2741 | 6.706 | 4.2213 | 6.3294 | 4.065 | 6.6368 | 8.1825 | 42.7581 | 46.9208 | 43.3432 | 15.476 |  |  | 0.20524 | 0.033599 | 0.091876 | -0.19516 | 0.07442 | -0.10823 | 0.36657 | 0.23903 | -0.922 | -0.23767 | -0.36174 | 8.8795 | 8.8806 | 2.0085 | 15.9772 | 16.8226 | 17.352 | 17.679 | 17.6574 | 16.6579 | 15.0237 | 16.9431 | 17.2671 | 17.5584 | 17.5999 | 17.3602 | 16.5887 | 14.8356 | 5.8907 | 8.1882 | 4.8785 | 5.1424 | 5.2889 | 6.7098 | 7.6278 | 16.0283 | 15.6232 | 15.4784 | 14.4372 | 14.3227 | 14.2736 |  |  |  | 10.9598 | 9.6352 | 9.2097 | 8.9587 | 0.095271 | -0.01729 | 12.9786 |  |  | 10.8034 |  |  | 16.9885 | 16.2001 | 15.1926 | 16.4866 | 15.7781 | 14.9015 | 10.8164 | 11.0122 | 11.635 | 11.5722 | 9.3683 |  | 10.9162 | 7.8764 | 10.3093 | 9.3336 | 11.2827 | 12.3261 |  | 12.4974 |  |  | 11.8595 | 12.8097 | 12.8178 | [6 empty] | 12.6752 |  |  | 11.4235 |  |  | 9.477 | 10.4779 | 12.6789 | 7.7589 | 9.454 | 13.0131 | 8.1208 | 9.6875 | 13.146 | 9.4086 | 10.6948 | 7.8433 | 10.6808 | 8.5321 | 10.3478 | 7.9275 | 9.8554 | 13.602 | 10.7222 | 10.4462 | 12.1946 | 8.216 | 9.9699 | 13.0885 | 7.9068 | 10.4917 | 9.8632 | 10.0649 | 8.4927 | 10.3545 | -0.22035 | 20.9542 | 0.034371 | 0.049354 | -38.1733 | 3.1213 | -1.2 | 0.42 | 0.53159 | 0.21354 | 0.35312 | -0.51466 | 0.31779 | -0.38324 | 0.70531 | 0.4122 | 0.43363 | 0.42525 | 0.43882 | 0.65787 | 0.43597 | 0.42501
42810.4316 | -729 | 18.6179 | 18.6529 | 18.6389 | 18.6719 | 18.0522 | 16.7224 | 14.8118 | 16.7923 | 17.2806 | 17.3845 | 17.3973 | 16.9722 | 16.0464 | 14.6779 | 15.0604 | 15.0193 | 15.5674 | 13.4359 | 13.5669 | 14.1515 |  |  |  | 16.687 | 16.0331 | 15.1685 | 10.6342 | 10.1042 | 10.3812 | 17.2996 | 16.4073 | 15.2108 | 16.9248 | 16.2198 | 15.2468 | 11.0206 | 11.6515 |  | 12.4772 | 10.9766 | 10.8491 | 8.6541 |  | 6.3438 | 6.2938 | 5.8368 | 5.8289 | 5.826 | 6.2508 | 6.6795 | 4.2701 | 6.3248 | 4.1179 | 6.6416 | 8.1778 | 42.7498 | 46.904 | 43.3079 | 15.4539 |  |  | -0.014237 | -0.25553 | 0.074792 | 0.085426 | -0.02152 | 0.14345 | 0.42703 | 0.24822 | -0.27204 | -0.57565 | -0.42592 | 8.8801 | 8.8812 | 2.0085 | 15.9704 | 16.8209 | 17.3541 | 17.6813 | 17.6524 | 16.656 | 15.0147 | 16.9363 | 17.2668 | 17.5478 | 17.5986 | 17.354 | 16.592 | 14.829 | 5.9092 | 8.199 | 4.8759 | 5.1481 | 5.2425 | 6.7148 | 7.6236 | 16.0328 | 15.6344 | 15.4865 | 14.4278 | 14.3181 | 14.273 |  |  |  | 10.954 | 9.6296 | 9.2118 | 8.947 | -0.053032 | -0.10781 | 12.9731 |  |  | 10.8015 |  |  | 16.9906 | 16.1962 | 15.1893 | 16.4907 | 15.7732 | 14.9017 | 10.7975 | 11.0107 | 11.6329 | 11.5784 | 9.3953 |  | 10.9159 | 7.8198 | 10.3122 | 9.3394 | 11.2832 | 12.3356 |  | 12.4966 |  |  | 11.8254 | 12.8033 | 12.8132 | [6 empty] | 12.6915 |  |  | 11.4234 |  |  | 9.4849 | 10.4927 | 12.6965 | 7.7433 | 9.4553 | 13.0171 | 8.1113 | 9.6842 | 13.1562 | 9.4065 | 10.6975 | 7.8454 | 10.6837 | 8.5473 | 10.35 | 7.9307 | 9.8644 | 13.6046 | 10.7149 | 10.4412 | 12.1859 | 8.2006 | 9.9645 | 13.0865 | 7.9138 | 10.4857 | 9.8508 | 10.067 | 8.4779 | 10.3461 | -0.15101 | 20.9528 | 0.03444 | 0.049362 | -38.1659 | 3.1213 | -1.22 | 0.34 | -0.14002 | -0.58889 | 0.3186 | 0.34049 | -0.17088 | 0.44119 | 0.76122 | 0.41144 | 0.43531 | 0.42511 | 0.43735 | 0.65767 | 0.43548 | 0.42514
42810.4316 | -728 | 18.6132 | 18.6485 | 18.6368 | 18.6664 | 18.044 | 16.719 | 14.8032 | 16.7875 | 17.2714 | 17.3735 | 17.3905 | 16.9662 | 16.0383 | 14.6641 | 15.066 | 15.0269 | 15.57 | 13.4373 | 13.5673 | 14.1559 |  |  |  | 16.6854 | 16.0286 | 15.1728 | 10.6429 | 10.1016 | 10.3847 | 17.3063 | 16.4095 | 15.2182 | 16.9217 | 16.2227 | 15.2529 | 11.0224 | 11.6822 |  | 12.4782 | 10.9925 | 10.8356 | 8.6603 |  | 6.3257 | 6.2882 | 5.8292 | 5.8197 | 5.8193 | 6.2272 | 6.6473 | 4.3433 | 6.3228 | 4.1802 | 6.6302 | 8.1798 | 42.7505 | 46.9082 | 43.2842 | 15.4401 |  |  | 0.17435 | -0.012397 | 0.069532 | -0.04337 | -0.034004 | 0.073796 | 0.65044 | 0.22326 | -0.49699 | -0.1506 | -0.19285 | 8.8828 | 8.8835 | 2.0086 | 15.9782 | 16.8244 | 17.355 | 17.6799 | 17.6535 | 16.659 | 15.022 | 16.944 | 17.2681 | 17.5592 | 17.6 | 17.3579 | 16.5876 | 14.834 | 5.9117 | 8.2376 | 4.8582 | 5.1931 | 5.2796 | 6.7108 | 7.6233 | 16.0309 | 15.6371 | 15.485 | 14.4256 | 14.3216 | 14.2731 |  |  |  | 10.9585 | 9.6236 | 9.216 | 8.931 | -0.018996 | -0.03291 | 12.968 |  |  | 10.798 |  |  | 16.9928 | 16.1951 | 15.1886 | 16.4866 | 15.7737 | 14.9037 | 10.7777 | 11.0105 | 11.6403 | 11.5883 | 9.421 |  | 10.9148 | 7.7473 | 10.3074 | 9.3439 | 11.2851 | 12.3468 |  | 12.5088 |  |  | 11.7961 | 12.7803 | 12.8009 | [6 empty] | 12.6777 |  |  | 11.4325 |  |  | 9.4873 | 10.4961 | 12.6986 | 7.7356 | 9.4554 | 13.0196 | 8.0998 | 9.6962 | 13.1682 | 9.4106 | 10.7055 | 7.8536 | 10.6865 | 8.5464 | 10.3518 | 7.9286 | 9.8584 | 13.6142 | 10.7249 | 10.447 | 12.1879 | 8.1875 | 9.9676 | 13.0859 | 7.8776 | 10.4788 | 9.8647 | 10.0645 | 8.4756 | 10.342 | -0.1123 | 20.9524 | 0.034612 | 0.050288 | -38.2125 | 3.1213 | -1.11 | 0.24 | 0.48999 | -0.12971 | 0.30719 | -0.24261 | -0.2148 | 0.31643 | 0.93944 | 0.41069 | 0.43716 | 0.42504 | 0.43661 | 0.65961 | 0.43537 | 0.42574
42810.4316 | -727 | 18.615 | 18.6524 | 18.6359 | 18.665 | 18.0436 | 16.7207 | 14.8017 | 16.7852 | 17.2758 | 17.3734 | 17.3948 | 16.9667 | 16.0409 | 14.6611 | 15.0723 | 15.0289 | 15.5735 | 13.4408 | 13.5786 | 14.1644 |  |  |  | 16.6907 | 16.0343 | 15.1758 | 10.6563 | 10.0957 | 10.3667 | 17.3138 | 16.4142 | 15.2304 | 16.9301 | 16.2257 | 15.2611 | 11.0297 | 11.7227 |  | 12.4952 | 10.9985 | 10.8336 | 8.6738 |  | 6.332 | 6.2955 | 5.8325 | 5.8217 | 5.8226 | 6.2184 | 6.6605 | 4.32 | 6.3293 | 4.2103 | 6.638 | 8.1761 | 42.7427 | 46.9018 | 43.2589 | 15.4447 |  |  | 0.008763 | -0.15039 | 0.19701 | -0.4015 | 0.094132 | -0.40262 | 0.60182 | 0.1766 | -0.38996 | 0.0913 | -0.38141 | 8.8856 | 8.8867 | 2.0082 | 15.9649 | 16.8218 | 17.3499 | 17.6727 | 17.6478 | 16.6494 | 15.0128 | 16.9302 | 17.2585 | 17.5512 | 17.5905 | 17.3443 | 16.5752 | 14.832 | 5.9051 | 8.2219 | 4.8436 | 5.196 | 5.3018 | 6.7023 | 7.612 | 16.0367 | 15.633 | 15.4928 | 14.4291 | 14.3253 | 14.2715 |  |  |  | 10.9562 | 9.6281 | 9.2081 | 8.9272 | 0.10986 | 0.1041 | 12.966 |  |  | 10.7949 |  |  | 16.99 | 16.1939 | 15.1921 | 16.4812 | 15.7805 | 14.9047 | 10.7546 | 11.0095 | 11.6423 | 11.5902 | 9.4281 |  | 10.9046 | 7.6819 | 10.2935 | 9.3384 | 11.2726 | 12.3534 |  | 12.4899 |  |  | 11.7497 | 12.7583 | 12.786 | [6 empty] | 12.6667 |  |  | 11.4293 |  |  | 9.4863 | 10.4919 | 12.6918 | 7.7177 | 9.4576 | 13.0178 | 8.0896 | 9.6853 | 13.1687 | 9.4096 | 10.7057 | 7.8642 | 10.6788 | 8.5485 | 10.3412 | 7.9145 | 9.8175 | 13.6176 | 10.7313 | 10.4415 | 12.1819 | 8.1777 | 9.9543 | 13.068 | 7.8011 | 10.4642 | 9.8659 | 10.0649 | 8.4588 | 10.3307 | 0.0001804 | 20.9524 | 0.034497 | 0.050585 | -38.2298 | 3.1212 | -1.11 | 0.3 | 0.10985 | -0.45178 | 0.51708 | -0.73817 | 0.35738 | -0.7391 | 0.90363 | 0.41015 | 0.43852 | 0.42479 | 0.43635 | 0.65993 | 0.43523 | 0.42577
42810.4316 | -726 | 18.6165 | 18.652 | 18.6351 | 18.6707 | 18.0429 | 16.7179 | 14.8011 | 16.7865 | 17.2797 | 17.3741 | 17.3985 | 16.9658 | 16.0363 | 14.6569 | 15.0766 | 15.036 | 15.5755 | 13.4435 | 13.5801 | 14.1605 |  |  |  | 16.6878 | 16.037 | 15.1785 | 10.6525 | 10.0903 | 10.354 | 17.3165 | 16.416 | 15.2216 | 16.9272 | 16.2254 | 15.2541 | 11.0268 | 11.7456 |  | 12.4807 | 10.9986 | 10.8136 | 8.6941 |  | 6.3246 | 6.2885 | 5.8247 | 5.8156 | 5.812 | 6.2047 | 6.6408 | 4.2852 | 6.3186 | 4.2337 | 6.6364 | 8.1847 | 42.7518 | 46.8978 | 43.2485 | 15.4584 |  |  | -0.058921 | -0.30678 | 0.1129 | -0.14062 | -0.013636 | -0.34807 | 0.52362 | 0.22917 | -0.51431 | -0.61363 | -0.40824 | 8.8784 | 8.8797 | 2.0086 | 15.9768 | 16.824 | 17.3588 | 17.6731 | 17.6551 | 16.6573 | 15.0132 | 16.9336 | 17.2635 | 17.5503 | 17.5982 | 17.3469 | 16.5858 | 14.8327 | 5.9322 | 8.2511 | 4.8458 | 5.2001 | 5.3041 | 6.712 | 7.6102 | 16.0358 | 15.6277 | 15.4864 | 14.4235 | 14.3199 | 14.2729 |  |  |  | 10.9648 | 9.6251 | 9.2105 | 8.9117 | 0.13133 | 0.050839 | 12.971 |  |  | 10.791 |  |  | 16.9906 | 16.1981 | 15.1943 | 16.4903 | 15.7892 | 14.9073 | 10.7372 | 11.0064 | 11.6451 | 11.591 | 9.4234 |  | 10.9102 | 7.6523 | 10.2944 | 9.3404 | 11.2842 | 12.3845 |  | 12.4875 |  |  | 11.7367 | 12.7469 | 12.7819 | [6 empty] | 12.6616 |  |  | 11.4301 |  |  | 9.486 | 10.4992 | 12.6921 | 7.701 | 9.4546 | 13.0178 | 8.0779 | 9.6793 | 13.1722 | 9.4115 | 10.707 | 7.8789 | 10.6642 | 8.5459 | 10.3386 | 7.8801 | 9.7694 | 13.6227 | 10.7216 | 10.4403 | 12.1887 | 8.1689 | 9.947 | 13.0559 | 7.7357 | 10.461 | 9.863 | 10.0534 | 8.4366 | 10.323 | -0.04874 | 20.9517 | 0.034865 | 0.050339 | -38.2296 | 3.1212 | -0.89 | 0.39 | -0.28483 | -0.64525 | 0.39144 | -0.43685 | -0.13602 | -0.68719 | 0.84286 | 0.41047 | 0.43937 | 0.42511 | 0.43446 | 0.65946 | 0.43457 | 0.42648
42810.4316 | -725 | 18.6123 | 18.6478 | 18.6304 | 18.6672 | 18.0484 | 16.7186 | 14.7972 | 16.7833 | 17.2644 | 17.3644 | 17.3964 | 16.9632 | 16.0315 | 14.6538 | 15.0755 | 15.0297 | 15.5742 | 13.4432 | 13.5745 | 14.1584 |  |  |  | 16.6815 | 16.0329 | 15.1698 | 10.6444 | 10.0802 | 10.3607 | 17.325 | 16.4242 | 15.2266 | 16.9319 | 16.2298 | 15.254 | 11.0403 | 11.8065 |  | 12.4873 | 10.9934 | 10.8012 | 8.7341 |  | 6.3297 | 6.2867 | 5.8146 | 5.8096 | 5.8136 | 6.1998 | 6.6091 | 4.2869 | 6.3259 | 4.2838 | 6.6511 | 8.1826 | 42.7348 | 46.8892 | 43.2268 | 15.468 |  |  | 0.15267 | -0.24239 | -0.010636 | -0.078854 | -0.078688 | -0.19825 | 0.31663 | 0.25348 | -0.42596 | -0.62118 | -0.36492 | 8.8779 | 8.8791 | 2.0084 | 15.9846 | 16.8253 | 17.3594 | 17.6802 | 17.6615 | 16.6659 | 15.0237 | 16.9472 | 17.269 | 17.5613 | 17.6016 | 17.3517 | 16.5891 | 14.8336 | 5.9492 | 8.2435 | 4.8502 | 5.1922 | 5.3371 | 6.6992 | 7.6079 | 16.0395 | 15.6307 | 15.4917 | 14.4197 | 14.3196 | 14.2749 |  |  |  | 10.9561 | 9.6204 | 9.212 | 8.9029 | 0.033073 | 0.034654 | 12.9647 |  |  | 10.7805 |  |  | 16.9937 | 16.2067 | 15.1929 | 16.4986 | 15.7892 | 14.9096 | 10.7155 | 11.0037 | 11.6501 | 11.5981 | 9.4267 |  | 10.9151 | 7.6253 | 10.3044 | 9.3528 | 11.289 | 12.4044 |  | 12.5002 |  |  | 11.7487 | 12.7582 | 12.7793 | [6 empty] | 12.6572 |  |  | 11.4198 |  |  | 9.4776 | 10.4931 | 12.6928 | 7.694 | 9.4491 | 13.004 | 8.0662 | 9.669 | 13.175 | 9.4129 | 10.6981 | 7.877 | 10.6471 | 8.5365 | 10.3324 | 7.8567 | 9.7359 | 13.6275 | 10.7203 | 10.4504 | 12.1995 | 8.1656 | 9.9401 | 13.0566 | 7.6788 | 10.4484 | 9.863 | 10.0564 | 8.4226 | 10.316 | -0.060296 | 20.9515 | 0.035215 | 0.050505 | -38.1851 | 3.1212 | -0.91 | 0.31 | 0.45849 | -0.57354 | -0.12014 | -0.32713 | -0.32673 | -0.51862 | 0.65542 | 0.41054 | 0.44045 | 0.42492 | 0.4311 | 0.65871 | 0.43391 | 0.42644
42810.4317 | -724 | 18.6245 | 18.6553 | 18.6501 | 18.6739 | 18.0494 | 16.7283 | 14.8059 | 16.786 | 17.2762 | 17.3761 | 17.3952 | 16.974 | 16.0473 | 14.6603 | 15.0805 | 15.0307 | 15.5791 | 13.4453 | 13.5759 | 14.1618 |  |  |  | 16.6823 | 16.0366 | 15.1742 | 10.645 | 10.0733 | 10.3817 | 17.3115 | 16.4253 | 15.2307 | 16.935 | 16.2259 | 15.255 | 11.0303 | 11.8776 |  | 12.4799 | 10.9842 | 10.793 | 8.7686 |  | 6.3115 | 6.2783 | 5.8016 | 5.8078 | 5.8037 | 6.1818 | 6.5813 | 4.2805 | 6.3161 | 4.2927 | 6.6436 | 8.1911 | 42.7193 | 46.888 | 43.209 | 15.4814 |  |  | 0.22101 | -0.16945 | 0.27652 | -0.10842 | 0.19533 | -0.4657 | -0.22286 | 0.39805 | -0.81633 | -0.27354 | -0.37406 | 8.8889 | 8.8899 | 2.0087 | 15.9835 | 16.8165 | 17.3489 | 17.6787 | 17.6521 | 16.6592 | 15.0188 | 16.9368 | 17.2604 | 17.5554 | 17.6 | 17.3474 | 16.5786 | 14.8275 | 5.9578 | 8.257 | 4.8518 | 5.1562 | 5.3636 | 6.7024 | 7.6094 | 16.0406 | 15.6344 | 15.4889 | 14.4299 | 14.3288 | 14.2791 |  |  |  | 10.9574 | 9.6275 | 9.2124 | 8.915 | 0.14268 | -0.0061858 | 12.9668 |  |  | 10.7736 |  |  | 16.9966 | 16.2097 | 15.2007 | 16.4963 | 15.787 | 14.9136 | 10.692 | 11.0064 | 11.6498 | 11.6162 | 9.4015 |  | 10.9135 | 7.5696 | 10.296 | 9.3604 | 11.2815 | 12.4213 |  | 12.4948 |  |  | 11.7652 | 12.7571 | 12.7792 | [6 empty] | 12.6519 |  |  | 11.411 |  |  | 9.4827 | 10.4916 | 12.6932 | 7.6724 | 9.4448 | 12.9861 | 8.058 | 9.6584 | 13.1801 | 9.4134 | 10.6895 | 7.851 | 10.6336 | 8.5299 | 10.3237 | 7.8567 | 9.7207 | 13.6338 | 10.7244 | 10.4548 | 12.1966 | 8.1668 | 9.9344 | 13.0535 | 7.6499 | 10.4433 | 9.8696 | 10.0672 | 8.401 | 10.3034 | -0.15351 | 20.9529 | 0.034635 | 0.050751 | -38.1138 | 3.1212 | -1.12 | 0.31 | 0.55166 | -0.47954 | 0.61259 | -0.38358 | 0.51477 | -0.79484 | -0.54985 | 0.41119 | 0.44172 | 0.42447 | 0.43051 | 0.6587 | 0.43262 | 0.42615
42810.4317 | -723 | 18.6146 | 18.6537 | 18.6409 | 18.6691 | 18.042 | 16.7172 | 14.8047 | 16.7729 | 17.2704 | 17.3705 | 17.3851 | 16.9619 | 16.0294 | 14.6536 | 15.081 | 15.0371 | 15.5824 | 13.4473 | 13.5812 | 14.1649 |  |  |  | 16.6861 | 16.0441 | 15.1759 | 10.6461 | 10.0653 | 10.3942 | 17.3145 | 16.4199 | 15.227 | 16.9329 | 16.219 | 15.2586 | 11.0263 | 11.9191 |  | 12.4757 | 10.9688 | 10.789 | 8.776 |  | 6.3021 | 6.2716 | 5.7919 | 5.7992 | 5.7933 | 6.1613 | 6.5577 | 4.3427 | 6.3241 | 4.2312 | 6.6455 | 8.1828 | 42.7164 | 46.8707 | 43.1991 | 15.4822 |  |  | 0.11061 | -0.074165 | 0.2739 | -0.51847 | 0.067848 | -0.43678 | -0.36611 | 0.36716 | -0.37148 | -0.74559 | -0.43248 | 8.8842 | 8.8853 | 2.0084 | 15.9781 | 16.8196 | 17.3527 | 17.6797 | 17.6532 | 16.656 | 15.0216 | 16.9327 | 17.2666 | 17.5548 | 17.5965 | 17.3447 | 16.5742 | 14.8315 | 5.9737 | 8.2474 | 4.8628 | 5.1423 | 5.387 | 6.6983 | 7.6064 | 16.0319 | 15.6329 | 15.4804 | 14.4297 | 14.3156 | 14.2705 |  |  |  | 10.9523 | 9.6118 | 9.1952 | 8.9268 | 0.1907 | 0.14268 | 12.9678 |  |  | 10.7781 |  |  | 16.9933 | 16.2072 | 15.1976 | 16.4958 | 15.783 | 14.9108 | 10.6664 | 11.0026 | 11.651 | 11.6216 | 9.4039 |  | 10.9254 | 7.5372 | 10.3014 | 9.3635 | 11.2858 | 12.4528 |  | 12.4959 |  |  | 11.7634 | 12.747 | 12.7625 | [6 empty] | 12.6385 |  |  | 11.4146 |  |  | 9.4881 | 10.4894 | 12.6922 | 7.6707 | 9.4515 | 12.9721 | 8.0539 | 9.6474 | 13.1814 | 9.4116 | 10.6929 | 7.8382 | 10.6218 | 8.5212 | 10.3173 | 7.8498 | 9.7201 | 13.6445 | 10.7309 | 10.4544 | 12.2023 | 8.1703 | 9.9301 | 13.0531 | 7.6386 | 10.4501 | 9.8756 | 10.0772 | 8.3873 | 10.3085 | -0.11731 | 20.9521 | 0.034629 | 0.049658 | -38.089 | 3.1212 | -1.5 | 0.3 | 0.39029 | -0.31725 | 0.60966 | -0.8388 | 0.30338 | -0.76974 | -0.70472 | 0.41151 | 0.4428 | 0.42452 | 0.42827 | 0.65713 | 0.43228 | 0.42565
42810.4317 | -722 | 18.621 | 18.6518 | 18.6384 | 18.67 | 18.0445 | 16.7227 | 14.8108 | 16.7851 | 17.2728 | 17.3688 | 17.3891 | 16.9706 | 16.0315 | 14.6621 | 15.0857 | 15.0312 | 15.5782 | 13.4467 | 13.5795 | 14.1657 |  |  |  | 16.6848 | 16.0397 | 15.1779 | 10.6504 | 10.0526 | 10.3535 | 17.3156 | 16.4246 | 15.2263 | 16.9384 | 16.2315 | 15.2496 | 11.0291 | 11.9647 |  | 12.4847 | 10.9527 | 10.7955 | 8.7869 |  | 6.2972 | 6.2613 | 5.783 | 5.7836 | 5.7684 | 6.1392 | 6.5269 | 4.4165 | 6.321 | 4.2137 | 6.6357 | 8.1859 | 42.7317 | 46.8504 | 43.1943 | 15.4883 |  |  | 0.093531 | -0.25816 | -0.20646 | -0.2589 | 0.58828 | -0.44533 | -0.47454 | 0.32971 | -0.51626 | -0.15605 | -0.34207 | 8.8883 | 8.89 | 2.0089 | 15.9841 | 16.8313 | 17.36 | 17.6836 | 17.6645 | 16.669 | 15.0266 | 16.9401 | 17.2697 | 17.56 | 17.6044 | 17.354 | 16.5831 | 14.8377 | 6.0093 | 8.2796 | 4.895 | 5.2151 | 5.3646 | 6.7023 | 7.6181 | 16.04 | 15.6314 | 15.4898 | 14.4312 | 14.3151 | 14.2732 |  |  |  | 10.9472 | 9.6179 | 9.1969 | 8.9485 | -0.12374 | 0.096195 | 12.9661 |  |  | 10.7757 |  |  | 16.9849 | 16.2019 | 15.1897 | 16.4965 | 15.7805 | 14.902 | 10.6352 | 10.99 | 11.6533 | 11.622 | 9.3937 |  | 10.9129 | 7.5051 | 10.2813 | 9.3478 | 11.2758 | 12.469 |  | 12.4856 |  |  | 11.7764 | 12.7266 | 12.7543 | [6 empty] | 12.6404 |  |  | 11.4208 |  |  | 9.4912 | 10.4862 | 12.6897 | 7.6776 | 9.4566 | 12.9686 | 8.0566 | 9.6519 | 13.1801 | 9.4141 | 10.692 | 7.8377 | 10.6139 | 8.5141 | 10.3086 | 7.8525 | 9.7234 | 13.657 | 10.7381 | 10.4589 | 12.2112 | 8.1682 | 9.9229 | 13.046 | 7.6328 | 10.4508 | 9.8742 | 10.0774 | 8.3792 | 10.3086 | -0.1358 | 20.9527 | 0.034388 | 0.048862 | -38.1286 | 3.1213 | -1.15 | 0.39 | 0.35886 | -0.59188 | -0.5293 | -0.59273 | 0.89328 | -0.7772 | -0.80228 | 0.41138 | 0.44303 | 0.42463 | 0.42477 | 0.65491 | 0.43207 | 0.42488
42810.4317 | -721 | 18.6298 | 18.6584 | 18.643 | 18.6734 | 18.0495 | 16.7241 | 14.8093 | 16.787 | 17.2737 | 17.3703 | 17.3914 | 16.9673 | 16.0384 | 14.6577 | 15.0813 | 15.0328 | 15.5776 | 13.4404 | 13.5705 | 14.17 |  |  |  | 16.6908 | 16.0385 | 15.1787 | 10.6471 | 10.0284 | 10.3498 | 17.3147 | 16.4298 | 15.2311 | 16.9365 | 16.2286 | 15.2538 | 11.0265 | 11.9991 |  | 12.4795 | 10.9382 | 10.7895 | 8.7726 |  | 6.2886 | 6.2534 | 5.7749 | 5.7662 | 5.7572 | 6.1215 | 6.4894 | 4.3657 | 6.3158 | 4.3357 | 6.6379 | 8.185 | 42.7387 | 46.8331 | 43.1954 | 15.4879 |  |  | -0.010293 | -0.25685 | 0.1221 | -0.086082 | 0.10924 | -0.16868 | -0.053324 | 0.29751 | -0.36252 | -0.89413 | -0.3532 | 8.8758 | 8.8771 | 2.0085 | 15.9763 | 16.8175 | 17.3509 | 17.678 | 17.6436 | 16.6462 | 15.0154 | 16.933 | 17.2658 | 17.5465 | 17.5924 | 17.3498 | 16.5792 | 14.8221 | 6.0094 | 8.2766 | 4.8911 | 5.2474 | 5.3476 | 6.6973 | 7.6108 | 16.0477 | 15.6363 | 15.4895 | 14.4388 | 14.3208 | 14.279 |  |  |  | 10.9502 | 9.6208 | 9.1992 | 8.9564 | -0.051614 | -0.01616 | 12.9661 |  |  | 10.7747 |  |  | 16.9837 | 16.1983 | 15.1878 | 16.4853 | 15.7805 | 14.8994 | 10.6108 | 10.9796 | 11.6528 | 11.6286 | 9.4072 |  | 10.9123 | 7.452 | 10.2883 | 9.3619 | 11.2754 | 12.5235 |  | 12.4983 |  |  | 11.7926 | 12.7195 | 12.7642 | [6 empty] | 12.6489 |  |  | 11.4011 |  |  | 9.4941 | 10.483 | 12.6834 | 7.6724 | 9.4544 | 12.9672 | 8.0499 | 9.6489 | 13.1787 | 9.4043 | 10.6797 | 7.8286 | 10.6023 | 8.5039 | 10.3055 | 7.8644 | 9.7358 | 13.6597 | 10.7468 | 10.4622 | 12.2128 | 8.1748 | 9.9164 | 13.041 | 7.6414 | 10.462 | 9.8792 | 10.0706 | 8.371 | 10.2996 | -0.060874 | 20.9523 | 0.034337 | 0.048138 | -38.104 | 3.1212 | -1.41 | 0.34 | -0.11905 | -0.59036 | 0.40705 | -0.34177 | 0.38493 | -0.47831 | -0.26893 | 0.41099 | 0.44473 | 0.42422 | 0.42418 | 0.6545 | 0.43238 | 0.42476
42810.4317 | -720 | 18.6316 | 18.6513 | 18.6386 | 18.6741 | 18.0483 | 16.7205 | 14.8043 | 16.7834 | 17.2687 | 17.3676 | 17.3926 | 16.964 | 16.0324 | 14.6573 | 15.0811 | 15.0387 | 15.5824 | 13.4491 | 13.5717 | 14.1697 |  |  |  | 16.6851 | 16.0486 | 15.1729 | 10.6406 | 10.0204 | 10.3689 | 17.3136 | 16.4277 | 15.232 | 16.9362 | 16.221 | 15.2597 | 11.0247 | 12.0002 |  | 12.48 | 10.9187 | 10.791 | 8.7594 |  | 6.2836 | 6.239 | 5.7565 | 5.7546 | 5.7556 | 6.1083 | 6.4615 | 4.3443 | 6.3151 | 4.5039 | 6.6383 | 8.1855 | 42.7215 | 46.82 | 43.1742 | 15.4856 |  |  | 0.071843 | -0.016341 | 0.21804 | 0.030886 | -0.12534 | -0.61552 | 0.089268 | 0.47362 | -0.63107 | 0.0027646 | -0.38718 | 8.8767 | 8.878 | 2.0082 | 15.9781 | 16.8227 | 17.3416 | 17.6758 | 17.6442 | 16.6483 | 15.0146 | 16.934 | 17.2575 | 17.539 | 17.5951 | 17.342 | 16.5778 | 14.8222 | 5.976 | 8.2575 | 4.9066 | 5.2505 | 5.4588 | 6.6922 | 7.612 | 16.0482 | 15.6458 | 15.4945 | 14.4421 | 14.3368 | 14.2818 |  |  |  | 10.9545 | 9.6169 | 9.2043 | 8.9692 | -0.0048136 | -0.067539 | 12.964 |  |  | 10.7786 |  |  | 16.9907 | 16.2026 | 15.1895 | 16.4851 | 15.7812 | 14.9042 | 10.5921 | 10.9771 | 11.6597 | 11.6362 | 9.431 |  | 10.9281 | 7.3791 | 10.2912 | 9.3699 | 11.279 | 12.568 |  | 12.4969 |  |  | 11.818 | 12.7157 | 12.7685 | [6 empty] | 12.655 |  |  | 11.395 |  |  | 9.5024 | 10.4962 | 12.689 | 7.6763 | 9.4571 | 12.9772 | 8.0535 | 9.6479 | 13.1755 | 9.4125 | 10.6852 | 7.8377 | 10.612 | 8.5091 | 10.3042 | 7.8752 | 9.7474 | 13.6621 | 10.7504 | 10.4692 | 12.2156 | 8.188 | 9.9105 | 13.0385 | 7.6442 | 10.4663 | 9.8784 | 10.0667 | 8.3644 | 10.301 | -0.11923 | 20.9522 | 0.033952 | 0.04866 | -38.0896 | 3.1212 | -1.57 | 0.33 | 0.31452 | -0.14891 | 0.54393 | 0.20472 | -0.41231 | -0.91367 | 0.34795 | 0.41085 | 0.44685 | 0.42412 | 0.42729 | 0.65292 | 0.43269 | 0.42455
42810.4317 | -719 | 18.6279 | 18.6574 | 18.6449 | 18.6718 | 18.0474 | 16.7262 | 14.8055 | 16.7828 | 17.2681 | 17.3658 | 17.3976 | 16.9635 | 16.0374 | 14.6562 | 15.088 | 15.0442 | 15.5812 | 13.4518 | 13.5762 | 14.1733 |  |  |  | 16.6969 | 16.0465 | 15.1776 | 10.6531 | 10.017 | 10.3796 | 17.3223 | 16.4326 | 15.2343 | 16.9306 | 16.2259 | 15.2619 | 11.0215 | 11.9959 |  | 12.4815 | 10.8973 | 10.7883 | 8.739 |  | 6.2742 | 6.2286 | 5.7277 | 5.7498 | 5.7466 | 6.0904 | 6.4311 | 4.3776 | 6.3058 | 4.5358 | 6.6318 | 8.1854 | 42.6996 | 46.8088 | 43.1616 | 15.4766 |  |  | 0.10733 | -0.21282 | 0.1911 | -0.024314 | -0.035976 | -0.33362 | -0.014556 | 0.13257 | -1.4772 | -0.59349 | -0.39771 | 8.8707 | 8.8718 | 2.0086 | 15.9769 | 16.8265 | 17.3569 | 17.6818 | 17.6549 | 16.6533 | 15.0224 | 16.9394 | 17.2642 | 17.5469 | 17.5978 | 17.3474 | 16.5754 | 14.8255 | 5.9744 | 8.2638 | 4.9359 | 5.2559 | 5.4998 | 6.6898 | 7.6161 | 16.0432 | 15.6447 | 15.4955 | 14.4444 | 14.3269 | 14.2833 |  |  |  | 10.9521 | 9.6188 | 9.2018 | 8.985 | -0.099023 | -0.19533 | 12.9632 |  |  | 10.7738 |  |  | 16.991 | 16.1993 | 15.1874 | 16.4888 | 15.7832 | 14.9015 | 10.5674 | 10.9621 | 11.6615 | 11.6389 | 9.4457 |  | 10.926 | 7.3624 | 10.2858 | 9.3756 | 11.278 | 12.6076 |  | 12.5022 |  |  | 11.8103 | 12.6978 | 12.7643 | [6 empty] | 12.6697 |  |  | 11.3686 |  |  | 9.4825 | 10.4952 | 12.677 | 7.6435 | 9.4518 | 12.9643 | 8.0451 | 9.6301 | 13.1591 | 9.4055 | 10.6721 | 7.8247 | 10.5977 | 8.4867 | 10.2979 | 7.8865 | 9.7566 | 13.666 | 10.7562 | 10.4755 | 12.2172 | 8.182 | 9.8982 | 13.0369 | 7.6266 | 10.4741 | 9.8759 | 10.059 | 8.3431 | 10.2956 | -0.32069 | 20.9513 | 0.033768 | 0.047921 | -38.136 | 3.1213 | -1.46 | 0.25 | 0.38444 | -0.53736 | 0.50921 | -0.18163 | -0.22088 | -0.67264 | -0.1405 | 0.41037 | 0.44714 | 0.42393 | 0.4272 | 0.65014 | 0.43315 | 0.42403
42810.4317 | -718 | 18.6133 | 18.6521 | 18.633 | 18.664 | 18.037 | 16.7169 | 14.795 | 16.7736 | 17.2659 | 17.3644 | 17.3907 | 16.9597 | 16.0332 | 14.6453 | 15.0785 | 15.0318 | 15.582 | 13.4434 | 13.5681 | 14.1574 |  |  |  | 16.6795 | 16.0408 | 15.1701 | 10.6372 | 9.9957 | 10.3428 | 17.318 | 16.4254 | 15.2274 | 16.9355 | 16.2298 | 15.2535 | 11.0247 | 11.9605 |  | 12.4698 | 10.8871 | 10.7832 | 8.7541 |  | 6.2563 | 6.224 | 5.7229 | 5.7487 | 5.735 | 6.0741 | 6.3948 | 4.3677 | 6.296 | 4.5817 | 6.6254 | 8.1883 | 42.6645 | 46.8189 | 43.1465 | 15.4643 |  |  | 0.19933 | -0.095193 | 0.17533 | -0.16362 | 0.039592 | -0.22519 | 0.20032 | 0.06686 | -0.59974 | -0.53348 | -0.49189 | 8.8818 | 8.883 | 2.0083 | 15.9856 | 16.8258 | 17.3536 | 17.6841 | 17.648 | 16.6544 | 15.023 | 16.9403 | 17.2611 | 17.5525 | 17.5973 | 17.354 | 16.5831 | 14.823 | 5.979 | 8.2551 | 4.926 | 5.3094 | 5.4637 | 6.6821 | 7.6091 | 16.0486 | 15.6434 | 15.494 | 14.438 | 14.3321 | 14.2816 |  |  |  | 10.9551 | 9.6221 | 9.1968 | 8.9868 | -0.05364 | -0.094263 | 12.961 |  |  | 10.7761 |  |  | 16.9874 | 16.1944 | 15.1883 | 16.4865 | 15.784 | 14.9037 | 10.5379 | 10.9558 | 11.6602 | 11.6479 | 9.4579 |  | 10.9116 | 7.3886 | 10.2822 | 9.3688 | 11.2736 | 12.6333 |  | 12.4932 |  |  | 11.8131 | 12.6945 | 12.7615 | [6 empty] | 12.6607 |  |  | 11.3568 |  |  | 9.4884 | 10.4902 | 12.6669 | 7.6285 | 9.447 | 12.9489 | 8.0397 | 9.6196 | 13.139 | 9.4081 | 10.6754 | 7.813 | 10.5984 | 8.49 | 10.2863 | 7.9053 | 9.7731 | 13.6743 | 10.7741 | 10.482 | 12.229 | 8.1926 | 9.9038 | 13.0412 | 7.6143 | 10.4801 | 9.8802 | 10.0751 | 8.3469 | 10.298 | -0.21649 | 20.9519 | 0.033705 | 0.047986 | -38.1407 | 3.1213 | -1.49 | 0.34 | 0.52387 | -0.35939 | 0.48774 | -0.47117 | 0.23171 | -0.55261 | 0.5212 | 0.40955 | 0.44629 | 0.42397 | 0.4258 | 0.65043 | 0.43284 | 0.42408
42810.4317 | -717 | 18.615 | 18.656 | 18.6291 | 18.6691 | 18.0495 | 16.7212 | 14.8006 | 16.7807 | 17.2703 | 17.3678 | 17.3905 | 16.9631 | 16.0274 | 14.6617 | 15.0869 | 15.0418 | 15.5801 | 13.4456 | 13.578 | 14.157 |  |  |  | 16.6961 | 16.0427 | 15.1674 | 10.6313 | 9.9872 | 10.2853 | 17.3274 | 16.4299 | 15.2236 | 16.9346 | 16.2284 | 15.2566 | 11.0204 | 11.9354 |  | 12.4774 | 10.872 | 10.7867 | 8.7818 |  | 6.2596 | 6.2325 | 5.7336 | 5.7482 | 5.734 | 6.0695 | 6.3709 | 4.3827 | 6.3033 | 4.5816 | 6.6229 | 8.1886 | 42.6374 | 46.8275 | 43.1347 | 15.4662 |  |  | -0.047749 | -0.19179 | 0.076104 | 0.023658 | -0.024808 | -0.34413 | 0.13001 | 0.051092 | -0.42655 | -0.32683 | -0.45473 | 8.885 | 8.8863 | 2.0086 | 15.9766 | 16.8218 | 17.3458 | 17.6736 | 17.6457 | 16.6525 | 15.0163 | 16.9307 | 17.2589 | 17.5486 | 17.588 | 17.3467 | 16.5772 | 14.8233 | 6.0381 | 8.2804 | 4.9416 | 5.3017 | 5.4415 | 6.6892 | 7.6073 | 16.0463 | 15.643 | 15.4836 | 14.4318 | 14.3289 | 14.2762 |  |  |  | 10.9551 | 9.6084 | 9.1915 | 8.9739 | -0.06762 | -0.07375 | 12.9619 |  |  | 10.7748 |  |  | 16.987 | 16.1947 | 15.1928 | 16.4849 | 15.7815 | 14.9051 | 10.5198 | 10.9486 | 11.6596 | 11.6545 | 9.4661 |  | 10.9077 | 7.4163 | 10.278 | 9.3703 | 11.2711 | 12.6507 |  | 12.4925 |  |  | 11.8384 | 12.6775 | 12.7483 | [6 empty] | 12.6708 |  |  | 11.3608 |  |  | 9.4926 | 10.4895 | 12.6648 | 7.6399 | 9.4615 | 12.9646 | 8.0336 | 9.5996 | 13.1185 | 9.4168 | 10.6659 | 7.8366 | 10.6006 | 8.4809 | 10.2872 | 7.8992 | 9.7843 | 13.6791 | 10.778 | 10.4754 | 12.2293 | 8.2025 | 9.9044 | 13.0289 | 7.6245 | 10.4751 | 9.8724 | 10.0747 | 8.3376 | 10.2918 | -0.2215 | 20.9514 | 0.033361 | 0.047429 | -38.1287 | 3.1213 | -1.24 | 0.26 | -0.25638 | -0.51013 | 0.32134 | 0.17917 | -0.18342 | -0.68313 | 0.41988 | 0.4092 | 0.44538 | 0.42385 | 0.42005 | 0.64848 | 0.43192 | 0.42444
42810.4317 | -716 | 18.6176 | 18.6449 | 18.643 | 18.6626 | 18.0403 | 16.7161 | 14.7978 | 16.7813 | 17.2624 | 17.364 | 17.3929 | 16.9641 | 16.0259 | 14.6588 | 15.0783 | 15.0397 | 15.5793 | 13.4484 | 13.5743 | 14.1585 |  |  |  | 16.6848 | 16.0351 | 15.1768 | 10.6211 | 9.9788 | 10.2473 | 17.3191 | 16.4264 | 15.2234 | 16.9309 | 16.2167 | 15.248 | 11.0113 | 11.9148 |  | 12.4776 | 10.861 | 10.7935 | 8.8046 |  | 6.2615 | 6.2362 | 5.7349 | 5.7512 | 5.7409 | 6.0664 | 6.3607 | 4.3467 | 6.3039 | 4.5752 | 6.6323 | 8.1842 | 42.598 | 46.8151 | 43.1119 | 15.4482 |  |  | 0.052787 | -0.19771 | 0.13919 | 0.056514 | -0.041236 | 0.001512 | 0.61168 | 0.19631 | -0.2843 | -0.4097 | -0.45334 | 8.8791 | 8.8806 | 2.0084 | 15.9804 | 16.8223 | 17.3497 | 17.6805 | 17.6525 | 16.6497 | 15.0124 | 16.9333 | 17.2651 | 17.5492 | 17.5902 | 17.3481 | 16.5712 | 14.8241 | 6.0266 | 8.2933 | 5.0126 | 5.2735 | 5.4565 | 6.6916 | 7.612 | 16.0451 | 15.6346 | 15.4898 | 14.4335 | 14.3257 | 14.2627 |  |  |  | 10.9441 | 9.5987 | 9.1958 | 8.9817 | -0.028315 | 0.070035 | 12.9585 |  |  | 10.7607 |  |  | 16.9884 | 16.1998 | 15.1932 | 16.4862 | 15.7785 | 14.9087 | 10.4959 | 10.9423 | 11.6604 | 11.6608 | 9.4296 |  | 10.9103 | 7.4483 | 10.2775 | 9.3892 | 11.268 | 12.6678 |  | 12.4961 |  |  | 11.8746 | 12.6572 | 12.7383 | [6 empty] | 12.6589 |  |  | 11.359 |  |  | 9.4844 | 10.4934 | 12.6565 | 7.6413 | 9.4617 | 12.962 | 8.0277 | 9.5998 | 13.1037 | 9.4051 | 10.6619 | 7.8284 | 10.5957 | 8.4747 | 10.2855 | 7.894 | 9.7881 | 13.6762 | 10.7714 | 10.4715 | 12.2061 | 8.2034 | 9.9035 | 13.0382 | 7.6472 | 10.4846 | 9.8692 | 10.0714 | 8.3395 | 10.2928 | -0.013879 | 20.9529 | 0.033447 | 0.046857 | -38.0708 | 3.1213 | -1.26 | 0.25 | 0.26954 | -0.51794 | 0.43458 | 0.27692 | -0.23647 | 0.045281 | 0.91075 | 0.4103 | 0.44448 | 0.42322 | 0.42162 | 0.64114 | 0.43099 | 0.42385
42810.4318 | -715 | 18.6297 | 18.6574 | 18.646 | 18.6717 | 18.0526 | 16.7272 | 14.8118 | 16.7879 | 17.2775 | 17.3776 | 17.397 | 16.9632 | 16.0362 | 14.6663 | 15.0831 | 15.0412 | 15.5838 | 13.4443 | 13.5751 | 14.1644 |  |  |  | 16.6831 | 16.0357 | 15.175 | 10.6192 | 9.9716 | 10.2108 | 17.3208 | 16.4252 | 15.2245 | 16.9306 | 16.2258 | 15.2502 | 11.0088 | 11.8893 |  | 12.4658 | 10.8465 | 10.7915 | 8.7999 |  | 6.2539 | 6.2175 | 5.7232 | 5.7462 | 5.7326 | 6.0484 | 6.3471 | 4.2943 | 6.3025 | 4.5296 | 6.6205 | 8.1863 | 42.5706 | 46.8014 | 43.1083 | 15.4431 |  |  | -0.051693 | -0.34687 | 0.001192 | 0.059798 | -0.020864 | -0.15488 | 0.51836 | 0.24231 | -0.19906 | -0.7372 | -0.27988 | 8.8798 | 8.8809 | 2.0086 | 15.9862 | 16.8286 | 17.3521 | 17.6768 | 17.6451 | 16.6476 | 15.0111 | 16.9341 | 17.2636 | 17.552 | 17.589 | 17.3445 | 16.5808 | 14.8325 | 6.0074 | 8.2789 | 5.0212 | 5.2742 | 5.4873 | 6.6849 | 7.6079 | 16.0567 | 15.6441 | 15.4974 | 14.4371 | 14.334 | 14.2712 |  |  |  | 10.9552 | 9.5991 | 9.2028 | 9.0033 | 0.059816 | 0.029196 | 12.9612 |  |  | 10.75 |  |  | 16.9875 | 16.2009 | 15.1882 | 16.4904 | 15.7751 | 14.9014 | 10.4735 | 10.9411 | 11.6613 | 11.666 | 9.4126 |  | 10.9054 | 7.4641 | 10.2711 | 9.3803 | 11.2696 | 12.671 |  | 12.4905 |  |  | 11.8839 | 12.6547 | 12.748 | [6 empty] | 12.6647 |  |  | 11.3623 |  |  | 9.4707 | 10.4817 | 12.6473 | 7.6424 | 9.4602 | 12.9556 | 8.0122 | 9.5904 | 13.0854 | 9.3966 | 10.6449 | 7.8097 | 10.6048 | 8.4595 | 10.2724 | 7.9431 | 9.8056 | 13.7029 | 10.7917 | 10.5004 | 12.2139 | 8.2174 | 9.9156 | 13.05 | 7.6805 | 10.4916 | 9.8812 | 10.0835 | 8.3491 | 10.3074 | -0.038725 | 20.9542 | 0.03312 | 0.046756 | -38.1649 | 3.1212 | -1.44 | 0.29 | -0.26672 | -0.68602 | 0.040215 | 0.28484 | -0.1682 | -0.45827 | 0.83838 | 0.41061 | 0.44383 | 0.42352 | 0.42296 | 0.63971 | 0.43104 | 0.42362
42810.4318 | -714 | 18.6241 | 18.6618 | 18.6382 | 18.6687 | 18.0466 | 16.7214 | 14.8066 | 16.7796 | 17.2695 | 17.3735 | 17.3959 | 16.963 | 16.0382 | 14.6625 | 15.089 | 15.0492 | 15.5849 | 13.4521 | 13.5808 | 14.1572 |  |  |  | 16.6849 | 16.0373 | 15.1733 | 10.6042 | 9.9712 | 10.1832 | 17.3281 | 16.4306 | 15.2294 | 16.9401 | 16.2286 | 15.2594 | 11.0146 | 11.8547 |  | 12.4704 | 10.8449 | 10.7856 | 8.8041 |  | 6.2659 | 6.2263 | 5.7317 | 5.7573 | 5.7396 | 6.0538 | 6.3455 | 4.2487 | 6.3044 | 4.4846 | 6.6315 | 8.1882 | 42.5474 | 46.7953 | 43.0962 | 15.4372 |  |  | -0.035265 | -0.046569 | 0.21804 | 0.042054 | 0.05996 | 0.33664 | 0.40403 | 0.12009 | -0.31816 | -0.019894 | -0.48275 | 8.8831 | 8.8843 | 2.0084 | 15.9703 | 16.8189 | 17.3349 | 17.6634 | 17.6465 | 16.6373 | 15.0108 | 16.9256 | 17.2557 | 17.5406 | 17.5813 | 17.3449 | 16.5648 | 14.8213 | 6.0721 | 8.2821 | 5.0263 | 5.3632 | 5.449 | 6.6884 | 7.6096 | 16.0479 | 15.6376 | 15.4932 | 14.4344 | 14.3272 | 14.2745 |  |  |  | 10.9496 | 9.5859 | 9.1941 | 9.0268 | 0.18462 | -0.052107 | 12.9602 |  |  | 10.7523 |  |  | 16.9905 | 16.2034 | 15.1908 | 16.4919 | 15.7774 | 14.9045 | 10.4502 | 10.9324 | 11.6599 | 11.6647 | 9.3834 |  | 10.9071 | 7.4794 | 10.267 | 9.3768 | 11.265 | 12.6582 |  | 12.4839 |  |  | 11.8806 | 12.6529 | 12.7429 | [6 empty] | 12.6485 |  |  | 11.3505 |  |  | 9.4681 | 10.4686 | 12.6336 | 7.6377 | 9.4518 | 12.9543 | 7.9832 | 9.5837 | 13.0712 | 9.3762 | 10.6375 | 7.7883 | 10.5909 | 8.455 | 10.2652 | 7.9725 | 9.8081 | 13.698 | 10.7947 | 10.4993 | 12.209 | 8.2171 | 9.9028 | 13.0601 | 7.6843 | 10.4838 | 9.8725 | 10.084 | 8.3395 | 10.2966 | -0.00059 | 20.9534 | 0.032959 | 0.046597 | -38.134 | 3.1213 | -1.48 | 0.27 | -0.22029 | -0.25137 | 0.54391 | 0.23887 | 0.28514 | 0.67563 | 0.74017 | 0.41148 | 0.44327 | 0.42346 | 0.41618 | 0.63935 | 0.43112 | 0.42278
42810.4318 | -713 | 18.6161 | 18.6524 | 18.6351 | 18.6625 | 18.0404 | 16.7185 | 14.7976 | 16.7775 | 17.2637 | 17.3686 | 17.3857 | 16.9595 | 16.0284 | 14.6507 | 15.0929 | 15.0487 | 15.5841 | 13.4557 | 13.5799 | 14.1642 |  |  |  | 16.6921 | 16.0372 | 15.1784 | 10.5962 | 9.9662 | 10.1484 | 17.3287 | 16.4271 | 15.2355 | 16.9358 | 16.2238 | 15.2554 | 11.0077 | 11.7904 |  | 12.4678 | 10.8307 | 10.7886 | 8.779 |  | 6.2603 | 6.2247 | 5.7362 | 5.7498 | 5.7354 | 6.0489 | 6.3317 | 4.2096 | 6.2983 | 4.502 | 6.6244 | 8.1853 | 42.5148 | 46.7877 | 43.0999 | 15.4246 |  |  | 0.049503 | 0.11903 | 0.21738 | -0.12091 | -0.019548 | -0.064856 | 0.50588 | 0.13126 | -0.61239 | -1.9687 | -0.25305 | 8.8845 | 8.8855 | 2.0085 | 15.9912 | 16.8208 | 17.3493 | 17.6695 | 17.6535 | 16.6566 | 15.0232 | 16.9392 | 17.263 | 17.55 | 17.5947 | 17.3426 | 16.5849 | 14.8289 | 6.1361 | 8.3285 | 5.0769 | 5.4375 | 5.3891 | 6.6791 | 7.6056 | 16.0434 | 15.6354 | 15.4945 | 14.4353 | 14.3255 | 14.272 |  |  |  | 10.9445 | 9.5849 | 9.1944 | 9.0655 | -0.11098 | -0.067539 | 12.9635 |  |  | 10.7501 |  |  | 16.9946 | 16.2062 | 15.1958 | 16.4953 | 15.7852 | 14.9135 | 10.4302 | 10.932 | 11.66 | 11.6534 | 9.3528 |  | 10.9076 | 7.4978 | 10.2638 | 9.3777 | 11.2687 | 12.6591 |  | 12.4846 |  |  | 11.868 | 12.6578 | 12.7374 | [6 empty] | 12.634 |  |  | 11.3474 |  |  | 9.4734 | 10.4743 | 12.6374 | 7.6267 | 9.4578 | 12.9557 | 7.9678 | 9.57 | 13.0763 | 9.3749 | 10.6315 | 7.7807 | 10.5944 | 8.453 | 10.2583 | 7.997 | 9.808 | 13.6963 | 10.7915 | 10.4922 | 12.2021 | 8.211 | 9.8965 | 13.0564 | 7.6577 | 10.4718 | 9.8713 | 10.0751 | 8.3422 | 10.283 | 0.16524 | 20.9541 | 0.033034 | 0.047096 | -38.1406 | 3.1213 | -1.62 | 0.43 | 0.26098 | 0.40187 | 0.54309 | -0.40503 | -0.16281 | -0.29655 | 0.82822 | 0.41234 | 0.44265 | 0.42356 | 0.40799 | 0.63326 | 0.43158 | 0.42154
42810.4318 | -712 | 18.6137 | 18.6455 | 18.6293 | 18.66 | 18.0405 | 16.7185 | 14.7915 | 16.7737 | 17.2573 | 17.3625 | 17.3832 | 16.9529 | 16.0269 | 14.6465 | 15.0996 | 15.0491 | 15.5922 | 13.461 | 13.5821 | 14.1729 |  |  |  | 16.6956 | 16.0486 | 15.1848 | 10.6009 | 9.9579 | 10.1292 | 17.3261 | 16.4273 | 15.2344 | 16.9308 | 16.2303 | 15.2506 | 11.0138 | 11.7288 |  | 12.4732 | 10.83 | 10.7964 | 8.7683 |  | 6.264 | 6.2317 | 5.7437 | 5.7682 | 5.7408 | 6.0523 | 6.3222 | 4.1761 | 6.298 | 4.4802 | 6.6262 | 8.1872 | 42.5027 | 46.7821 | 43.1078 | 15.4204 |  |  | -0.052349 | -0.070225 | 0.11948 | 0.026942 | 0.033676 | 0.030424 | 0.54794 | 0.10103 | -0.41701 | -0.99379 | -0.14774 | 8.8766 | 8.8779 | 2.0086 | 15.9862 | 16.8253 | 17.3607 | 17.6788 | 17.6568 | 16.6574 | 15.0169 | 16.9406 | 17.2686 | 17.551 | 17.5938 | 17.3511 | 16.5809 | 14.8235 | 6.1718 | 8.3707 | 5.1425 | 5.4589 | 5.4122 | 6.6869 | 7.6082 | 16.0587 | 15.6508 | 15.499 | 14.442 | 14.3422 | 14.2825 |  |  |  | 10.9565 | 9.5853 | 9.2008 | 9.0584 | -0.029531 | -0.052671 | 12.9629 |  |  | 10.7461 |  |  | 16.9895 | 16.2044 | 15.1864 | 16.49 | 15.7878 | 14.9051 | 10.4129 | 10.9217 | 11.6554 | 11.6483 | 9.3211 |  | 10.9118 | 7.5603 | 10.2733 | 9.3957 | 11.2702 | 12.6635 |  | 12.4854 |  |  | 11.8586 | 12.6692 | 12.7333 | [6 empty] | 12.6304 |  |  | 11.3301 |  |  | 9.4685 | 10.4716 | 12.6329 | 7.6229 | 9.4519 | 12.9557 | 7.953 | 9.5743 | 13.0761 | 9.3764 | 10.6268 | 7.7825 | 10.5997 | 8.4303 | 10.2605 | 8.0193 | 9.8177 | 13.7027 | 10.7916 | 10.5008 | 12.2116 | 8.2053 | 9.8997 | 13.0705 | 7.6394 | 10.4745 | 9.8769 | 10.0797 | 8.3493 | 10.2791 | -0.029095 | 20.9513 | 0.032982 | 0.047335 | -38.105 | 3.1213 | -1.61 | 0.36 | -0.26837 | -0.30868 | 0.40263 | 0.1912 | 0.21369 | 0.20311 | 0.86197 | 0.41336 | 0.44123 | 0.42311 | 0.40493 | 0.62626 | 0.43208 | 0.42213
42810.4318 | -711 | 18.6208 | 18.6526 | 18.6386 | 18.6629 | 18.0425 | 16.722 | 14.7982 | 16.7806 | 17.2607 | 17.3686 | 17.393 | 16.9603 | 16.0276 | 14.6588 | 15.0895 | 15.0499 | 15.5908 | 13.4564 | 13.5837 | 14.1741 |  |  |  | 16.6891 | 16.0484 | 15.1802 | 10.5906 | 9.9477 | 10.1156 | 17.3236 | 16.433 | 15.2348 | 16.9309 | 16.2309 | 15.2594 | 11.0106 | 11.6821 |  | 12.4697 | 10.8186 | 10.8022 | 8.7823 |  | 6.2697 | 6.2372 | 5.7504 | 5.7666 | 5.7405 | 6.0516 | 6.3294 | 4.1431 | 6.2962 | 4.3813 | 6.623 | 8.1848 | 42.4936 | 46.7697 | 43.1078 | 15.4056 |  |  | -0.010293 | 0.10523 | 0.18124 | 0.08871 | 0.17956 | -0.4289 | 0.43228 | 0.03532 | -0.49193 | -0.38683 | -0.30471 | 8.8741 | 8.8752 | 2.0086 | 15.9912 | 16.8294 | 17.3651 | 17.6784 | 17.6586 | 16.6632 | 15.0205 | 16.9394 | 17.2671 | 17.554 | 17.5945 | 17.35 | 16.5794 | 14.8262 | 6.1658 | 8.3636 | 5.1944 | 5.4595 | 5.4751 | 6.6771 | 7.6012 | 16.0521 | 15.6401 | 15.4975 | 14.4429 | 14.3331 | 14.2779 |  |  |  | 10.9565 | 9.585 | 9.1974 | 9.0711 | 0.018485 | -0.061328 | 12.9624 |  |  | 10.7568 |  |  | 16.9962 | 16.2026 | 15.1889 | 16.4943 | 15.7895 | 14.9071 | 10.4103 | 10.9194 | 11.6518 | 11.6412 | 9.2898 |  | 10.9139 | 7.701 | 10.2663 | 9.4122 | 11.2778 | 12.6628 |  | 12.4902 |  |  | 11.8543 | 12.6759 | 12.7117 | [6 empty] | 12.624 |  |  | 11.3198 |  |  | 9.4687 | 10.4768 | 12.6245 | 7.6176 | 9.4626 | 12.9574 | 7.9501 | 9.5834 | 13.0718 | 9.3811 | 10.6333 | 7.7984 | 10.6019 | 8.4399 | 10.2641 | 8.0169 | 9.8273 | 13.7034 | 10.7948 | 10.4976 | 12.2009 | 8.2018 | 9.8959 | 13.0614 | 7.628 | 10.4702 | 9.8708 | 10.0769 | 8.3523 | 10.2705 | -0.19049 | 20.9501 | 0.033504 | 0.046807 | -38.217 | 3.1212 | -1.84 | 0.31 | -0.119 | 0.37786 | 0.49591 | 0.34694 | 0.49343 | -0.76261 | 0.76562 | 0.4143 | 0.43709 | 0.42291 | 0.40447 | 0.61968 | 0.43159 | 0.42178
42810.4318 | -710 | 18.6287 | 18.6578 | 18.6474 | 18.6688 | 18.0503 | 16.7225 | 14.8012 | 16.7803 | 17.2696 | 17.3722 | 17.4017 | 16.9658 | 16.0397 | 14.661 | 15.0854 | 15.0583 | 15.5864 | 13.4536 | 13.5801 | 14.1707 |  |  |  | 16.6875 | 16.0409 | 15.1787 | 10.5818 | 9.9425 | 10.0897 | 17.3254 | 16.4306 | 15.239 | 16.9464 | 16.2354 | 15.2593 | 11.0097 | 11.6393 |  | 12.4674 | 10.8161 | 10.8128 | 8.7859 |  | 6.2642 | 6.2382 | 5.7568 | 5.7688 | 5.7411 | 6.0477 | 6.3155 | 4.0998 | 6.2876 | 4.3229 | 6.6178 | 8.1808 | 42.4865 | 46.7519 | 43.1143 | 15.4088 |  |  | 0.075787 | 0.050027 | 0.14182 | 0.10579 | -0.11549 | 0.10271 | 0.57159 | 0.32708 | -1.1215 | -0.011712 | -0.19483 | 8.8785 | 8.8795 | 2.0086 | 15.9863 | 16.8325 | 17.3588 | 17.6821 | 17.6502 | 16.6595 | 15.0187 | 16.9371 | 17.2619 | 17.5505 | 17.5969 | 17.3478 | 16.5774 | 14.8208 | 6.1858 | 8.368 | 5.231 | 5.4614 | 5.4913 | 6.683 | 7.5996 | 16.0579 | 15.6518 | 15.5063 | 14.4392 | 14.3401 | 14.279 |  |  |  | 10.9509 | 9.581 | 9.2052 | 9.0717 | 0.021727 | -0.10424 | 12.9664 |  |  | 10.76 |  |  | 16.9997 | 16.2001 | 15.1938 | 16.4963 | 15.7876 | 14.904 | 10.4205 | 10.9158 | 11.6423 | 11.625 | 9.2539 |  | 10.9106 | 7.7801 | 10.2614 | 9.4194 | 11.2737 | 12.6476 |  | 12.4914 |  |  | 11.8582 | 12.6858 | 12.6947 | [6 empty] | 12.626 |  |  | 11.3317 |  |  | 9.4682 | 10.4703 | 12.62 | 7.608 | 9.4653 | 12.9544 | 7.9473 | 9.5783 | 13.0711 | 9.3773 | 10.6369 | 7.807 | 10.602 | 8.442 | 10.2565 | 8.0091 | 9.8375 | 13.7202 | 10.805 | 10.4972 | 12.1953 | 8.2078 | 9.8948 | 13.0639 | 7.637 | 10.4732 | 9.8718 | 10.0831 | 8.3597 | 10.2604 | -0.034873 | 20.953 | 0.03343 | 0.046199 | -38.2322 | 3.1213 | -1.65 | 0.35 | 0.32288 | 0.26054 | 0.43867 | 0.37888 | -0.39572 | 0.37319 | 0.88037 | 0.41519 | 0.43473 | 0.42257 | 0.40292 | 0.61544 | 0.43146 | 0.42158
42810.4318 | -709 | 18.6318 | 18.6553 | 18.6485 | 18.6678 | 18.0515 | 16.725 | 14.8076 | 16.7869 | 17.2645 | 17.3746 | 17.3943 | 16.9683 | 16.0439 | 14.6601 | 15.0918 | 15.0505 | 15.5816 | 13.4572 | 13.586 | 14.1705 |  |  |  | 16.689 | 16.0347 | 15.1789 | 10.5781 | 9.9374 | 10.0675 | 17.3208 | 16.4256 | 15.2327 | 16.9318 | 16.2271 | 15.2522 | 11.0028 | 11.5885 |  | 12.4566 | 10.8062 | 10.8057 | 8.7655 |  | 6.2667 | 6.2313 | 5.7535 | 5.7713 | 5.7326 | 6.034 | 6.3026 | 4.0982 | 6.2786 | 4.2758 | 6.6157 | 8.1922 | 42.488 | 46.7138 | 43.132 | 15.4204 |  |  | -0.075349 | -0.072853 | 0.11159 | 0.10185 | 0.24067 | 0.042252 | 0.53282 | 0.075404 | 0.37151 | -1.0255 | -0.46765 | 8.8765 | 8.8778 | 2.0086 | 15.9862 | 16.8272 | 17.3581 | 17.6821 | 17.6519 | 16.6508 | 15.0216 | 16.9383 | 17.2594 | 17.5502 | 17.5931 | 17.3454 | 16.5715 | 14.8196 | 6.208 | 8.389 | 5.2177 | 5.4524 | 5.5085 | 6.677 | 7.5954 | 16.0696 | 15.6555 | 15.5169 | 14.4471 | 14.3434 | 14.2816 |  |  |  | 10.9566 | 9.5797 | 9.2094 | 9.0665 | 0.077239 | -0.018042 | 12.9637 |  |  | 10.7613 |  |  | 16.9897 | 16.2011 | 15.1906 | 16.495 | 15.78 | 14.9051 | 10.4286 | 10.9088 | 11.6357 | 11.6114 | 9.2359 |  | 10.9133 | 7.8225 | 10.2609 | 9.4146 | 11.2701 | 12.6441 |  | 12.482 |  |  | 11.8535 | 12.677 | 12.6734 | [6 empty] | 12.6256 |  |  | 11.3342 |  |  | 9.4788 | 10.4704 | 12.6178 | 7.6082 | 9.4667 | 12.9612 | 7.9419 | 9.5784 | 13.0629 | 9.3815 | 10.6319 | 7.8108 | 10.6067 | 8.4383 | 10.2552 | 8.0093 | 9.849 | 13.723 | 10.814 | 10.501 | 12.1902 | 8.2066 | 9.903 | 13.0706 | 7.6475 | 10.4743 | 9.8766 | 10.0819 | 8.3587 | 10.2492 | -0.066652 | 20.9549 | 0.033085 | 0.046452 | -38.1326 | 3.1213 | -1.59 | 0.38 | -0.32193 | -0.3144 | 0.38911 | 0.37175 | 0.57124 | 0.23935 | 0.84997 | 0.41578 | 0.43354 | 0.42258 | 0.39976 | 0.61643 | 0.4318 | 0.42191
42810.4318 | -708 | 18.6276 | 18.6603 | 18.6501 | 18.6675 | 18.0373 | 16.7176 | 14.8003 | 16.783 | 17.2621 | 17.373 | 17.3975 | 16.9628 | 16.039 | 14.654 | 15.0969 | 15.0457 | 15.5798 | 13.4527 | 13.5872 | 14.168 |  |  |  | 16.6898 | 16.0346 | 15.177 | 10.5718 | 9.9297 | 10.0409 | 17.3252 | 16.4323 | 15.2319 | 16.9362 | 16.2301 | 15.2587 | 11.0023 | 11.5646 |  | 12.4543 | 10.8095 | 10.8157 | 8.7595 |  | 6.2689 | 6.2322 | 5.7628 | 5.7753 | 5.7317 | 6.0314 | 6.2865 | 4.189 | 6.2727 | 4.2188 | 6.613 | 8.1944 | 42.493 | 46.6848 | 43.1304 | 15.4433 |  |  | -0.083233 | -0.015681 | 0.051136 | -0.18728 | 0.040248 | 0.096792 | 0.52954 | 0.19697 | -0.86304 | 0.8577 | -0.4756 | 8.8849 | 8.8858 | 2.0086 | 15.9863 | 16.8325 | 17.359 | 17.6778 | 17.6562 | 16.654 | 15.0238 | 16.9338 | 17.2644 | 17.5517 | 17.5961 | 17.3466 | 16.5723 | 14.8137 | 6.162 | 8.3694 | 5.2009 | 5.4399 | 5.4922 | 6.6767 | 7.5981 | 16.0607 | 15.6501 | 15.5031 | 14.4438 | 14.3376 | 14.2827 |  |  |  | 10.9492 | 9.5623 | 9.1904 | 9.0662 | -0.064986 | -0.039121 | 12.9597 |  |  | 10.7636 |  |  | 16.9903 | 16.2025 | 15.1925 | 16.4957 | 15.7822 | 14.9019 | 10.4428 | 10.9066 | 11.626 | 11.6 | 9.2276 |  | 10.9079 | 7.8788 | 10.2597 | 9.4262 | 11.2623 | 12.6258 |  | 12.4963 |  |  | 11.8403 | 12.6685 | 12.6619 | [6 empty] | 12.6347 |  |  | 11.3357 |  |  | 9.484 | 10.4638 | 12.6116 | 7.6162 | 9.4706 | 12.9614 | 7.9381 | 9.5773 | 13.0436 | 9.3837 | 10.6275 | 7.8263 | 10.6079 | 8.4223 | 10.2597 | 8.0087 | 9.8556 | 13.7389 | 10.8211 | 10.5069 | 12.1916 | 8.2054 | 9.9022 | 13.073 | 7.6588 | 10.4846 | 9.8863 | 10.0865 | 8.3696 | 10.2452 | -0.044888 | 20.9547 | 0.031961 | 0.046257 | -38.0161 | 3.1213 | -1.15 | 0.35 | -0.33834 | -0.14587 | 0.26341 | -0.50409 | 0.23361 | 0.36227 | 0.84734 | 0.41583 | 0.43194 | 0.42201 | 0.40484 | 0.61862 | 0.43195 | 0.42168
42810.4319 | -707 | 18.6276 | 18.656 | 18.6415 | 18.6704 | 18.0418 | 16.7201 | 14.7955 | 16.7796 | 17.2643 | 17.3688 | 17.3885 | 16.9639 | 16.0327 | 14.6565 | 15.0924 | 15.0452 | 15.5792 | 13.4551 | 13.5863 | 14.1642 |  |  |  | 16.688 | 16.0334 | 15.1755 | 10.5601 | 9.9252 | 10.032 | 17.323 | 16.4331 | 15.2307 | 16.94 | 16.2296 | 15.2558 | 10.9997 | 11.5228 |  | 12.4564 | 10.8072 | 10.8291 | 8.7581 |  | 6.2783 | 6.2425 | 5.7744 | 5.782 | 5.7431 | 6.034 | 6.2857 | 4.2792 | 6.2664 | 4.1537 | 6.611 | 8.19 | 42.4775 | 46.6571 | 43.1212 | 15.448 |  |  | -0.068121 | 0.038199 | 0.08202 | -0.11828 | -0.15623 | -0.03266 | 0.39746 | 0.08066 | -0.46625 | -0.46719 | -0.31922 | 8.8812 | 8.8825 | 2.0084 | 15.9872 | 16.8332 | 17.3577 | 17.6809 | 17.6544 | 16.6533 | 15.0208 | 16.9378 | 17.2669 | 17.5441 | 17.5864 | 17.3422 | 16.5756 | 14.814 | 6.1239 | 8.3477 | 5.2132 | 5.4186 | 5.4748 | 6.6824 | 7.5953 | 16.0593 | 15.6548 | 15.5031 | 14.4388 | 14.3311 | 14.2828 |  |  |  | 10.9424 | 9.5464 | 9.1889 | 9.1174 | -0.03885 | -0.061328 | 12.9531 |  |  | 10.7645 |  |  | 16.9923 | 16.2008 | 15.1915 | 16.4889 | 15.7806 | 14.8953 | 10.4554 | 10.8991 | 11.6187 | 11.5883 | 9.2015 |  | 10.916 | 7.8789 | 10.2534 | 9.4225 | 11.2619 | 12.593 |  | 12.4874 |  |  | 11.8388 | 12.6635 | 12.6621 | [6 empty] | 12.6277 |  |  | 11.3487 |  |  | 9.4827 | 10.475 | 12.6169 | 7.6271 | 9.4833 | 12.9668 | 7.9472 | 9.5848 | 13.0382 | 9.3838 | 10.6226 | 7.8454 | 10.6226 | 8.4198 | 10.249 | 8.0165 | 9.8704 | 13.7441 | 10.8265 | 10.5018 | 12.1865 | 8.2097 | 9.9158 | 13.0698 | 7.6677 | 10.4925 | 9.8862 | 10.0847 | 8.3696 | 10.2363 | -0.15987 | 20.9542 | 0.031874 | 0.045533 | -37.9583 | 3.1213 | -1.02 | 0.34 | -0.30608 | 0.22767 | 0.33361 | -0.40062 | -0.46025 | -0.21044 | 0.7341 | 0.41682 | 0.43173 | 0.42209 | 0.40973 | 0.61692 | 0.4319 | 0.42003
42810.4319 | -706 | 18.6287 | 18.6577 | 18.6462 | 18.6744 | 18.0447 | 16.7298 | 14.7982 | 16.7852 | 17.2687 | 17.3681 | 17.3903 | 16.9589 | 16.0333 | 14.6568 | 15.0917 | 15.0396 | 15.5867 | 13.4601 | 13.5834 | 14.1666 |  |  |  | 16.6867 | 16.0348 | 15.1719 | 10.5503 | 9.9248 | 10.0274 | 17.3268 | 16.4359 | 15.2279 | 16.939 | 16.2282 | 15.255 | 11.0073 | 11.4847 |  | 12.4609 | 10.8096 | 10.831 | 8.7818 |  | 6.2779 | 6.243 | 5.7797 | 5.7938 | 5.7573 | 6.0362 | 6.2791 | 4.3324 | 6.2722 | 4.1408 | 6.6136 | 8.1903 | 42.4795 | 46.6446 | 43.121 | 15.4579 |  |  | 0.015331 | -0.091253 | -0.25048 | -0.11499 | -0.007064 | -0.37567 | 0.40534 | 0.25217 | -0.23487 | -0.30753 | 0.035658 | 8.8829 | 8.8842 | 2.0086 | 15.989 | 16.8436 | 17.3593 | 17.6759 | 17.6539 | 16.6628 | 15.0182 | 16.941 | 17.2699 | 17.5538 | 17.5925 | 17.3464 | 16.5774 | 14.8188 | 6.0881 | 8.3441 | 5.1677 | 5.4207 | 5.443 | 6.6803 | 7.5919 | 16.0697 | 15.6514 | 15.5084 | 14.4454 | 14.3342 | 14.2847 |  |  |  | 10.9476 | 9.5526 | 9.1918 | 9.135 | -0.056274 | -0.041003 | 12.953 |  |  | 10.7561 |  |  | 16.9896 | 16.2014 | 15.1887 | 16.488 | 15.7788 | 14.9 | 10.4665 | 10.8887 | 11.6156 | 11.5826 | 9.1678 |  | 10.9082 | 7.8387 | 10.25 | 9.4028 | 11.2612 | 12.5473 |  | 12.4826 |  |  | 11.85 | 12.6627 | 12.6629 | [6 empty] | 12.6373 |  |  | 11.3516 |  |  | 9.4872 | 10.4757 | 12.6055 | 7.6302 | 9.4878 | 12.9764 | 7.9464 | 9.5805 | 13.0171 | 9.3893 | 10.6174 | 7.8534 | 10.6321 | 8.4139 | 10.2525 | 8.0154 | 9.8833 | 13.7466 | 10.8358 | 10.5124 | 12.1865 | 8.218 | 9.9247 | 13.0607 | 7.6898 | 10.4786 | 9.891 | 10.0795 | 8.3755 | 10.2336 | -0.1643 | 20.9551 | 0.03246 | 0.046264 | -37.9905 | 3.1214 | -1.35 | 0.36 | 0.1452 | -0.35188 | -0.58299 | -0.39501 | -0.097868 | -0.7137 | 0.74135 | 0.4175 | 0.43273 | 0.42262 | 0.41346 | 0.62157 | 0.43149 | 0.41971
42810.4319 | -705 | 18.6312 | 18.662 | 18.6468 | 18.6731 | 18.0514 | 16.7219 | 14.8011 | 16.7824 | 17.2722 | 17.3672 | 17.3908 | 16.9578 | 16.0352 | 14.661 | 15.0903 | 15.0494 | 15.5836 | 13.4531 | 13.5813 | 14.1652 |  |  |  | 16.6903 | 16.032 | 15.1684 | 10.5484 | 9.9172 | 10.0191 | 17.3204 | 16.4347 | 15.2271 | 16.9344 | 16.2306 | 15.254 | 11.0043 | 11.4682 |  | 12.4546 | 10.8085 | 10.8279 | 8.8184 |  | 6.2788 | 6.2447 | 5.7614 | 5.7829 | 5.7792 | 6.0411 | 6.2884 | 4.3554 | 6.2714 | 4.1291 | 6.6102 | 8.1945 | 42.4853 | 46.6351 | 43.1189 | 15.4704 |  |  | 0.062647 | -0.088621 | 0.1497 | -0.37981 | 0.11779 | 0.13228 | 0.37512 | 0.09446 | -0.2086 | -0.53076 | -0.18629 | 8.8851 | 8.8862 | 2.0084 | 15.9901 | 16.8316 | 17.3584 | 17.6762 | 17.6557 | 16.6603 | 15.0217 | 16.9387 | 17.2631 | 17.5438 | 17.5924 | 17.3487 | 16.5704 | 14.8211 | 6.0756 | 8.3651 | 5.1234 | 5.4283 | 5.4815 | 6.6802 | 7.5836 | 16.0683 | 15.649 | 15.5037 | 14.445 | 14.3361 | 14.2747 |  |  |  | 10.9448 | 9.5508 | 9.1892 | 9.1219 | 0.019093 | 0.0081174 | 12.9532 |  |  | 10.7604 |  |  | 16.9941 | 16.2032 | 15.1961 | 16.4918 | 15.784 | 14.9112 | 10.4837 | 10.8865 | 11.6182 | 11.5832 | 9.1676 |  | 10.9124 | 7.8356 | 10.2459 | 9.365 | 11.2599 | 12.5092 |  | 12.4855 |  |  | 11.8597 | 12.6607 | 12.6809 | [6 empty] | 12.6363 |  |  | 11.3576 |  |  | 9.4849 | 10.4782 | 12.6105 | 7.6544 | 9.4904 | 12.9816 | 7.9531 | 9.5878 | 13.014 | 9.3923 | 10.628 | 7.8761 | 10.6303 | 8.4038 | 10.2656 | 8.0312 | 9.8998 | 13.7623 | 10.8584 | 10.518 | 12.1933 | 8.2235 | 9.9327 | 13.0561 | 7.7084 | 10.4825 | 9.8991 | 10.0748 | 8.3821 | 10.2423 | -0.23749 | 20.9558 | 0.031938 | 0.047429 | -37.9603 | 3.1213 | -1.41 | 0.27 | 0.29352 | -0.34677 | 0.4507 | -0.7179 | 0.39964 | 0.4235 | 0.71318 | 0.41765 | 0.43268 | 0.42363 | 0.41484 | 0.62553 | 0.43038 | 0.41998
42810.4319 | -704 | 18.6268 | 18.669 | 18.6418 | 18.6705 | 18.0534 | 16.7206 | 14.7999 | 16.7865 | 17.2716 | 17.3697 | 17.3953 | 16.9641 | 16.0371 | 14.6628 | 15.095 | 15.061 | 15.5965 | 13.4582 | 13.5891 | 14.1734 |  |  |  | 16.6918 | 16.031 | 15.1768 | 10.5492 | 9.9225 | 10.0355 | 17.3306 | 16.4382 | 15.2285 | 16.9334 | 16.2286 | 15.2521 | 10.9951 | 11.4611 |  | 12.4506 | 10.8096 | 10.8294 | 8.8533 |  | 6.2708 | 6.2397 | 5.758 | 5.7767 | 5.7835 | 6.0405 | 6.2807 | 4.3456 | 6.2771 | 4.1014 | 6.6074 | 8.1939 | 42.4903 | 46.6223 | 43.0993 | 15.4657 |  |  | 0.087615 | -0.047881 | 0.041936 | -0.15311 | 0.30112 | -0.13254 | 0.051812 | 0.13652 | -0.24907 | -0.64195 | -0.22623 | 8.8845 | 8.8858 | 2.0086 | 15.9916 | 16.8313 | 17.3585 | 17.6737 | 17.6533 | 16.6575 | 15.0123 | 16.9288 | 17.2616 | 17.544 | 17.5943 | 17.3518 | 16.5785 | 14.8219 | 6.0621 | 8.3651 | 5.094 | 5.4314 | 5.524 | 6.6759 | 7.5819 | 16.0648 | 15.6432 | 15.5022 | 14.4357 | 14.3322 | 14.2695 |  |  |  | 10.9445 | 9.5342 | 9.1821 | 9.117 | -0.09963 | -0.124 | 12.9589 |  |  | 10.7625 |  |  | 16.9984 | 16.2008 | 15.193 | 16.494 | 15.7812 | 14.9015 | 10.4981 | 10.8727 | 11.6193 | 11.5828 | 9.1764 |  | 10.9058 | 7.8444 | 10.2505 | 9.3459 | 11.2669 | 12.5054 |  | 12.5002 |  |  | 11.8683 | 12.6507 | 12.6903 | [6 empty] | 12.6388 |  |  | 11.3486 |  |  | 9.4928 | 10.4819 | 12.6001 | 7.6591 | 9.4985 | 12.9882 | 7.9605 | 9.588 | 12.9951 | 9.3943 | 10.6179 | 7.8804 | 10.6476 | 8.3963 | 10.263 | 8.0457 | 9.9137 | 13.7768 | 10.864 | 10.5313 | 12.2018 | 8.235 | 9.9364 | 13.0639 | 7.7423 | 10.4757 | 9.9055 | 10.0695 | 8.3918 | 10.2485 | 0.0038398 | 20.9553 | 0.032414 | 0.048023 | -38.0116 | 3.1213 | -1.47 | 0.32 | 0.34713 | -0.25489 | 0.23854 | -0.45579 | 0.63898 | -0.42393 | 0.26505 | 0.41718 | 0.43259 | 0.42439 | 0.41584 | 0.6286 | 0.4291 | 0.42011
42810.4319 | -703 | 18.6218 | 18.6632 | 18.6438 | 18.669 | 18.0422 | 16.7178 | 14.7911 | 16.786 | 17.2709 | 17.3653 | 17.3877 | 16.9638 | 16.0336 | 14.646 | 15.0928 | 15.0556 | 15.5878 | 13.4506 | 13.5813 | 14.1612 |  |  |  | 16.6898 | 16.0462 | 15.18 | 10.5412 | 9.916 | 10.0378 | 17.3344 | 16.4352 | 15.2385 | 16.9484 | 16.2337 | 15.2576 | 10.9985 | 11.471 |  | 12.4582 | 10.8175 | 10.8387 | 8.9026 |  | 6.2615 | 6.2338 | 5.7471 | 5.7533 | 5.7634 | 6.0111 | 6.2414 | 4.3771 | 6.2692 | 4.0891 | 6.6026 | 8.1991 | 42.4934 | 46.6191 | 43.0925 | 15.4603 |  |  | 0.046219 | -0.26539 | -0.12234 | 0.003286 | 0.14276 | -0.33822 | 0.20558 | 0.031376 | -0.57152 | -1.3517 | -0.31385 | 8.8795 | 8.881 | 2.0085 | 15.9979 | 16.8305 | 17.3572 | 17.6726 | 17.6534 | 16.6529 | 15.012 | 16.9263 | 17.2627 | 17.5435 | 17.5909 | 17.3521 | 16.5713 | 14.8221 | 6.0408 | 8.3731 | 5.0636 | 5.4269 | 5.5474 | 6.6658 | 7.5776 | 16.068 | 15.6469 | 15.5061 | 14.437 | 14.33 | 14.2708 |  |  |  | 10.9466 | 9.5298 | 9.1784 | 9.0986 | -0.22646 | -0.091064 | 12.9656 |  |  | 10.7674 |  |  | 17.0022 | 16.2056 | 15.197 | 16.4932 | 15.7848 | 14.9046 | 10.5103 | 10.8733 | 11.6253 | 11.5847 | 9.184 |  | 10.9027 | 7.852 | 10.25 | 9.3409 | 11.2661 | 12.4943 |  | 12.5043 |  |  | 11.8481 | 12.6618 | 12.6977 | [6 empty] | 12.6447 |  |  | 11.3461 |  |  | 9.4933 | 10.4865 | 12.5971 | 7.6812 | 9.5057 | 13.0022 | 7.964 | 9.5872 | 12.9669 | 9.3975 | 10.6189 | 7.9001 | 10.6656 | 8.4017 | 10.264 | 8.0382 | 9.8483 | 13.7663 | 10.8573 | 10.5143 | 12.1778 | 8.2306 | 9.9214 | 13.0569 | 7.6971 | 10.4416 | 9.8957 | 10.0689 | 8.3765 | 10.241 | -0.013879 | 20.9563 | 0.032821 | 0.048066 | -38.1345 | 3.1214 | -1.26 | 0.34 | 0.25212 | -0.60008 | -0.40744 | 0.066773 | 0.43994 | -0.67716 | 0.52794 | 0.41687 | 0.43236 | 0.4245 | 0.41704 | 0.63148 | 0.42785 | 0.42069
42810.4319 | -702 | 18.6293 | 18.6561 | 18.6377 | 18.6658 | 18.0378 | 16.718 | 14.7932 | 16.7753 | 17.2633 | 17.3615 | 17.3874 | 16.9553 | 16.0278 | 14.6509 | 15.0969 | 15.0612 | 15.5961 | 13.451 | 13.5741 | 14.1723 |  |  |  | 16.6863 | 16.0444 | 15.18 | 10.5393 | 9.9154 | 10.0655 | 17.3262 | 16.4288 | 15.2345 | 16.9304 | 16.2236 | 15.2488 | 10.9932 | 11.4828 |  | 12.4485 | 10.8018 | 10.8199 | 8.8647 |  | 6.2556 | 6.2276 | 5.729 | 5.7378 | 5.755 | 5.9936 | 6.2124 | 4.4496 | 6.2667 | 4.1152 | 6.6031 | 8.1886 | 42.4874 | 46.6127 | 43.0803 | 15.4588 |  |  | 0.042275 | -0.026853 | 0.22527 | -0.035486 | -0.043204 | -0.074056 | 0.48222 | 0.11089 | -0.32399 | 0.61727 | -0.087536 | 8.8824 | 8.8838 | 2.0086 | 15.9929 | 16.8265 | 17.3551 | 17.6721 | 17.6491 | 16.6457 | 15.0129 | 16.9258 | 17.2615 | 17.5428 | 17.5874 | 17.349 | 16.5715 | 14.8173 | 5.9747 | 8.3578 | 5.0491 | 5.3971 | 5.5371 | 6.6586 | 7.5739 | 16.0687 | 15.6571 | 15.5031 | 14.4388 | 14.3328 | 14.2808 |  |  |  | 10.9515 | 9.5275 | 9.1795 | 9.0667 | -0.0048136 | 0.091114 | 12.961 |  |  | 10.7527 |  |  | 16.9918 | 16.2009 | 15.1905 | 16.4903 | 15.78 | 14.9013 | 10.5201 | 10.8677 | 11.626 | 11.5802 | 9.179 |  | 10.9113 | 7.9143 | 10.2528 | 9.3663 | 11.2638 | 12.4739 |  | 12.5057 |  |  | 11.8268 | 12.6696 | 12.692 | [6 empty] | 12.6356 |  |  | 11.3415 |  |  | 9.4932 | 10.4808 | 12.5964 | 7.6867 | 9.5081 | 12.9856 | 7.9678 | 9.5836 | 12.9585 | 9.3771 | 10.626 | 7.8979 | 10.6659 | 8.3924 | 10.2679 | 8.0525 | 9.7818 | 13.7668 | 10.8449 | 10.5151 | 12.1692 | 8.2245 | 9.9172 | 13.0584 | 7.6421 | 10.3887 | 9.8921 | 10.0707 | 8.3719 | 10.2526 | 0.033693 | 20.956 | 0.032965 | 0.047429 | -38.0303 | 3.1213 | -1.63 | 0.31 | 0.24114 | -0.19088 | 0.55286 | -0.21943 | -0.24202 | -0.31686 | 0.80855 | 0.41729 | 0.43072 | 0.42372 | 0.42354 | 0.63266 | 0.42872 | 0.42174
42810.4319 | -701 | 18.627 | 18.6609 | 18.6454 | 18.6655 | 18.044 | 16.7263 | 14.7991 | 16.7869 | 17.2659 | 17.373 | 17.3927 | 16.9597 | 16.0349 | 14.6539 | 15.1007 | 15.0491 | 15.5996 | 13.4547 | 13.5742 | 14.169 |  |  |  | 16.6906 | 16.0437 | 15.1787 | 10.5434 | 9.9075 | 10.0741 | 17.334 | 16.4378 | 15.2367 | 16.9445 | 16.2267 | 15.2639 | 10.9904 | 11.5124 |  | 12.4522 | 10.7958 | 10.8209 | 8.8719 |  | 6.2566 | 6.2274 | 5.7201 | 5.7272 | 5.734 | 5.9939 | 6.1935 | 4.503 | 6.2704 | 4.1575 | 6.6049 | 8.1902 | 42.4844 | 46.628 | 43.0695 | 15.4522 |  |  | 0.010735 | -0.001885 | 0.20161 | -0.23262 | -0.03532 | 0.16053 | 0.50588 | -0.032364 | -0.57853 | -0.43803 | -0.23219 | 8.8796 | 8.881 | 2.0085 | 15.9926 | 16.8285 | 17.3567 | 17.6754 | 17.642 | 16.6434 | 15.0124 | 16.9317 | 17.2624 | 17.5441 | 17.5841 | 17.3473 | 16.5752 | 14.8155 | 5.9106 | 8.3233 | 5.0694 | 5.3561 | 5.5662 | 6.6587 | 7.573 | 16.0706 | 15.6538 | 15.5055 | 14.4454 | 14.3352 | 14.2805 |  |  |  | 10.9475 | 9.5217 | 9.1814 | 9.0451 | 0.029223 | -0.033475 | 12.9694 |  |  | 10.7502 |  |  | 16.9914 | 16.2017 | 15.1937 | 16.4887 | 15.7767 | 14.9023 | 10.5341 | 10.8505 | 11.6309 | 11.5853 | 9.1695 |  | 10.9004 | 7.9709 | 10.2487 | 9.3562 | 11.262 | 12.448 |  | 12.4929 |  |  | 11.8171 | 12.6718 | 12.6937 | [6 empty] | 12.6579 |  |  | 11.3203 |  |  | 9.4802 | 10.4819 | 12.6013 | 7.6907 | 9.5021 | 12.9875 | 7.9662 | 9.5918 | 12.9488 | 9.3732 | 10.6098 | 7.9063 | 10.6653 | 8.3765 | 10.2484 | 8.052 | 9.7313 | 13.7622 | 10.8509 | 10.5198 | 12.1719 | 8.2388 | 9.9231 | 13.0722 | 7.6114 | 10.3486 | 9.8926 | 10.0768 | 8.3682 | 10.2576 | -0.068578 | 20.9561 | 0.033143 | 0.047342 | -38.1602 | 3.1214 | -1.77 | 0.32 | 0.12152 | -0.050573 | 0.52302 | -0.5618 | -0.21882 | 0.46651 | 0.82814 | 0.4172 | 0.42901 | 0.42394 | 0.43068 | 0.63031 | 0.42844 | 0.42221
42810.4319 | -700 | 18.6308 | 18.6581 | 18.6416 | 18.6672 | 18.0501 | 16.7218 | 14.7958 | 16.7784 | 17.266 | 17.3654 | 17.3907 | 16.9594 | 16.03 | 14.65 | 15.105 | 15.0594 | 15.5975 | 13.4607 | 13.5863 | 14.1727 |  |  |  | 16.6959 | 16.0373 | 15.1765 | 10.5436 | 9.9089 | 10.0543 | 17.3412 | 16.4457 | 15.2444 | 16.9471 | 16.2384 | 15.2628 | 10.9963 | 11.5384 |  | 12.4624 | 10.7905 | 10.8073 | 8.8729 |  | 6.2418 | 6.2082 | 5.7052 | 5.722 | 5.722 | 5.9765 | 6.1714 | 4.5598 | 6.2664 | 4.2272 | 6.5999 | 8.1964 | 42.5012 | 46.6451 | 43.0787 | 15.4471 |  |  | 0.11259 | -0.072193 | -0.002748 | -0.75305 | -0.037292 | -0.19891 | 0.42966 | 0.001808 | -0.54973 | -0.3925 | -0.13125 | 8.8838 | 8.8849 | 2.0083 | 15.9933 | 16.8327 | 17.352 | 17.6801 | 17.6471 | 16.6518 | 15.0145 | 16.9324 | 17.2645 | 17.5427 | 17.5871 | 17.3463 | 16.571 | 14.8094 | 5.8847 | 8.3087 | 5.0343 | 5.3657 | 5.5826 | 6.6586 | 7.5774 | 16.0673 | 15.6483 | 15.5045 | 14.4406 | 14.3351 | 14.2776 |  |  |  | 10.9445 | 9.5169 | 9.1717 | 9.0171 | 0.18057 | 0.013011 | 12.9651 |  |  | 10.7533 |  |  | 16.9979 | 16.2029 | 15.1936 | 16.4862 | 15.7735 | 14.8984 | 10.5539 | 10.8451 | 11.6291 | 11.5906 | 9.1734 |  | 10.9013 | 8.0098 | 10.2489 | 9.3409 | 11.2659 | 12.4335 |  | 12.4896 |  |  | 11.7967 | 12.6645 | 12.704 | [6 empty] | 12.6615 |  |  | 11.3193 |  |  | 9.4849 | 10.4884 | 12.6032 | 7.7195 | 9.5004 | 12.9823 | 7.9647 | 9.5999 | 12.9258 | 9.3689 | 10.6051 | 7.9135 | 10.6543 | 8.3754 | 10.2616 | 8.0413 | 9.6865 | 13.7493 | 10.8417 | 10.5123 | 12.1565 | 8.2257 | 9.9297 | 13.0626 | 7.5886 | 10.3187 | 9.8913 | 10.0662 | 8.3636 | 10.2603 | -0.043155 | 20.9573 | 0.034405 | 0.047096 | -38.1938 | 3.1213 | -1.26 | 0.39 | 0.39351 | -0.31296 | -0.06106 | -1.0108 | -0.22484 | -0.51927 | 0.76318 | 0.41712 | 0.42794 | 0.42449 | 0.43355 | 0.63471 | 0.4286 | 0.42289
42810.4319 | -699 | 18.6301 | 18.6655 | 18.6373 | 18.6645 | 18.0499 | 16.7205 | 14.7946 | 16.7749 | 17.2651 | 17.3683 | 17.3889 | 16.9541 | 16.0289 | 14.6476 | 15.1062 | 15.0622 | 15.5981 | 13.4644 | 13.5882 | 14.1747 |  |  |  | 16.6895 | 16.0453 | 15.179 | 10.534 | 9.9034 | 10.0167 | 17.3436 | 16.4508 | 15.2514 | 16.9488 | 16.2334 | 15.2666 | 10.9932 | 11.5498 |  | 12.4602 | 10.7759 | 10.8002 | 8.8644 |  | 6.2322 | 6.1989 | 5.7033 | 5.7153 | 5.7178 | 5.9668 | 6.179 | 4.65 | 6.2699 | 4.2814 | 6.6061 | 8.188 | 42.4886 | 46.6256 | 43.0624 | 15.432 |  |  | 0.12179 | -0.082709 | -0.084232 | 0.00197 | 0.002136 | -0.1194 | 0.43426 | 0.15754 | -0.18563 | -0.068987 | -0.32836 | 8.8803 | 8.8815 | 2.0087 | 15.9959 | 16.8432 | 17.3626 | 17.6859 | 17.649 | 16.6564 | 15.0165 | 16.9397 | 17.2696 | 17.5572 | 17.5965 | 17.3426 | 16.5842 | 14.8191 | 5.8655 | 8.2864 | 5.0224 | 5.355 | 5.5551 | 6.6555 | 7.5752 | 16.0699 | 15.6533 | 15.5075 | 14.4519 | 14.3342 | 14.281 |  |  |  | 10.949 | 9.5172 | 9.1684 | 8.991 | 0.028413 | 0.13271 | 12.9649 |  |  | 10.7552 |  |  | 16.9964 | 16.2049 | 15.1947 | 16.4872 | 15.7765 | 14.8923 | 10.5628 | 10.8429 | 11.6349 | 11.5916 | 9.2006 |  | 10.8971 | 8.0524 | 10.2525 | 9.3312 | 11.2585 | 12.4283 |  | 12.4933 |  |  | 11.7973 | 12.6644 | 12.7051 | [6 empty] | 12.6479 |  |  | 11.3351 |  |  | 9.4792 | 10.4822 | 12.6082 | 7.7274 | 9.4879 | 12.969 | 7.9696 | 9.5909 | 12.9033 | 9.3556 | 10.6007 | 7.8997 | 10.6362 | 8.3711 | 10.2485 | 8.0351 | 9.6653 | 13.7422 | 10.8342 | 10.5079 | 12.1324 | 8.217 | 9.9241 | 13.0645 | 7.5817 | 10.303 | 9.8891 | 10.0541 | 8.3517 | 10.2603 | 0.036389 | 20.9573 | 0.034337 | 0.047516 | -38.1484 | 3.1214 | -1.38 | 0.43 | 0.40925 | -0.33498 | -0.33805 | 0.051698 | 0.05381 | -0.4023 | 0.76724 | 0.41622 | 0.42688 | 0.42452 | 0.43531 | 0.63578 | 0.42873 | 0.42376
42810.432 | -698 | 18.6399 | 18.6697 | 18.6489 | 18.6739 | 18.045 | 16.7284 | 14.8026 | 16.7756 | 17.2715 | 17.3763 | 17.396 | 16.96 | 16.0365 | 14.6534 | 15.0943 | 15.0595 | 15.5945 | 13.461 | 13.5824 | 14.1716 |  |  |  | 16.684 | 16.0377 | 15.1736 | 10.5211 | 9.896 | 9.9953 | 17.3341 | 16.4473 | 15.2451 | 16.9546 | 16.2349 | 15.2627 | 10.9877 | 11.5533 |  | 12.4533 | 10.7492 | 10.7878 | 8.8606 |  | 6.2386 | 6.1977 | 5.7086 | 5.7126 | 5.7144 | 5.9643 | 6.1769 | 4.6069 | 6.2841 | 4.3239 | 6.6036 | 8.1989 | 42.4897 | 46.6115 | 43.0717 | 15.4238 |  |  | -0.020153 | -0.1287 | 0.056392 | -0.090682 | -0.00838 | -0.44007 | 0.406 | 0.01758 | -0.3092 | 0.76791 | -0.26557 | 8.8812 | 8.8822 | 2.0083 | 16.0003 | 16.8355 | 17.3584 | 17.6796 | 17.6492 | 16.6531 | 15.0032 | 16.9433 | 17.2644 | 17.5492 | 17.5888 | 17.3477 | 16.5748 | 14.8187 | 5.8443 | 8.2923 | 5.032 | 5.3823 | 5.5241 | 6.6491 | 7.5736 | 16.0682 | 15.6577 | 15.5005 | 14.4404 | 14.3267 | 14.2837 |  |  |  | 10.9416 | 9.5099 | 9.1654 | 8.9687 | 0.063868 | 0.008682 | 12.967 |  |  | 10.7301 |  |  | 16.9875 | 16.1974 | 15.1868 | 16.4878 | 15.7778 | 14.903 | 10.5644 | 10.8332 | 11.6326 | 11.5937 | 9.2066 |  | 10.9093 | 8.0371 | 10.259 | 9.3171 | 11.2657 | 12.4199 |  | 12.4992 |  |  | 11.8129 | 12.6799 | 12.7205 | [6 empty] | 12.6474 |  |  | 11.3298 |  |  | 9.481 | 10.4895 | 12.626 | 7.6975 | 9.4679 | 12.9736 | 7.9756 | 9.5923 | 12.9066 | 9.3597 | 10.5981 | 7.8849 | 10.6161 | 8.3836 | 10.2539 | 8.0352 | 9.6607 | 13.7407 | 10.836 | 10.5136 | 12.1306 | 8.2165 | 9.9173 | 13.0719 | 7.5831 | 10.3076 | 9.8858 | 10.0444 | 8.3534 | 10.2645 | -0.14716 | 20.958 | 0.034113 | 0.049275 | -38.1908 | 3.1214 | -1.35 | 0.38 | -0.16647 | -0.41787 | 0.2766 | -0.35075 | -0.10658 | -0.77236 | 0.74186 | 0.41646 | 0.42751 | 0.42515 | 0.43693 | 0.63452 | 0.42866 | 0.42413
42810.432 | -697 | 18.6331 | 18.6694 | 18.647 | 18.6745 | 18.0425 | 16.7215 | 14.7984 | 16.7789 | 17.2699 | 17.3775 | 17.3978 | 16.9626 | 16.0335 | 14.6569 | 15.0911 | 15.0492 | 15.5889 | 13.4553 | 13.5816 | 14.1625 |  |  |  | 16.6778 | 16.0312 | 15.1678 | 10.5071 | 9.8891 | 9.9672 | 17.3326 | 16.4385 | 15.2427 | 16.9454 | 16.2326 | 15.2589 | 10.9878 | 11.5493 |  | 12.4507 | 10.7373 | 10.7818 | 8.86 |  | 6.228 | 6.1934 | 5.6974 | 5.7083 | 5.7098 | 5.9586 | 6.1549 | 4.5244 | 6.2806 | 4.3524 | 6.6055 | 8.1942 | 42.474 | 46.5941 | 43.064 | 15.4131 |  |  | 0.10142 | -0.28707 | 0.10436 | 0.22868 | -0.060948 | -0.035944 | 0.50916 | 0.075404 | -0.58554 | -0.46026 | -0.23795 | 8.8798 | 8.8809 | 2.0087 | 15.9901 | 16.8356 | 17.357 | 17.6785 | 17.6515 | 16.6504 | 15.0052 | 16.9389 | 17.2675 | 17.5467 | 17.5944 | 17.3454 | 16.5744 | 14.8202 | 5.8258 | 8.3075 | 5.039 | 5.4896 | 5.511 | 6.6518 | 7.5712 | 16.0698 | 15.6618 | 15.5089 | 14.4496 | 14.3366 | 14.2807 |  |  |  | 10.9403 | 9.5073 | 9.1723 | 8.9471 | 0.22129 | 0.16809 | 12.959 |  |  | 10.6936 |  |  | 16.9818 | 16.1947 | 15.1813 | 16.4839 | 15.7743 | 14.8953 | 10.5626 | 10.8278 | 11.6311 | 11.5873 | 9.1724 |  | 10.9054 | 7.996 | 10.2511 | 9.2954 | 11.2662 | 12.4343 |  | 12.4955 |  |  | 11.8375 | 12.6996 | 12.7321 | [6 empty] | 12.65 |  |  | 11.3255 |  |  | 9.4874 | 10.4952 | 12.6365 | 7.6622 | 9.4132 | 12.9681 | 7.9792 | 9.5941 | 12.9099 | 9.3635 | 10.6008 | 7.8477 | 10.6049 | 8.3915 | 10.2552 | 8.0432 | 9.6609 | 13.7385 | 10.8371 | 10.506 | 12.1204 | 8.2238 | 9.9206 | 13.0746 | 7.5957 | 10.3185 | 9.8762 | 10.0455 | 8.363 | 10.2699 | -0.10729 | 20.9577 | 0.033963 | 0.04892 | -38.2708 | 3.1213 | -1.12 | 0.37 | 0.37342 | -0.62407 | 0.37627 | 0.55699 | -0.28743 | -0.22073 | 0.83077 | 0.41728 | 0.4284 | 0.42577 | 0.43931 | 0.63348 | 0.42868 | 0.42469
42810.432 | -696 | 18.6341 | 18.6535 | 18.6389 | 18.6608 | 18.0457 | 16.7167 | 14.7911 | 16.776 | 17.2618 | 17.3653 | 17.3792 | 16.961 | 16.0301 | 14.6445 | 15.0963 | 15.0503 | 15.5866 | 13.4558 | 13.5776 | 14.1661 |  |  |  | 16.6835 | 16.028 | 15.1727 | 10.506 | 9.8839 | 9.9771 | 17.3327 | 16.444 | 15.2393 | 16.9461 | 16.2319 | 15.2655 | 10.9888 | 11.5344 |  | 12.451 | 10.7214 | 10.7737 | 8.8393 |  | 6.2237 | 6.1907 | 5.6909 | 5.6991 | 5.6974 | 5.9477 | 6.1484 | 4.4825 | 6.2813 | 4.3763 | 6.6093 | 8.2022 | 42.4589 | 46.6004 | 43.0694 | 15.4103 |  |  | 0.055415 | -0.13134 | 0.24236 | 0.16757 | -0.11418 | -0.16211 | 0.54399 | -0.086904 | 0.018308 | -0.55488 | -0.21768 | 8.8761 | 8.8772 | 2.0084 | 15.9929 | 16.832 | 17.3542 | 17.6759 | 17.6526 | 16.6483 | 15.0109 | 16.9354 | 17.2597 | 17.5481 | 17.5932 | 17.3376 | 16.5673 | 14.8177 | 5.8347 | 8.2919 | 5.0428 | 5.5135 | 5.5414 | 6.6439 | 7.5674 | 16.081 | 15.6668 | 15.5125 | 14.4466 | 14.3447 | 14.2772 |  |  |  | 10.9453 | 9.5122 | 9.1761 | 8.9348 | 0.13599 | 0.11294 | 12.9706 |  |  | 10.684 |  |  | 16.9936 | 16.202 | 15.1935 | 16.4911 | 15.7795 | 14.9014 | 10.5836 | 10.8352 | 11.6491 | 11.6016 | 9.1551 |  | 10.907 | 7.9446 | 10.2412 | 9.2925 | 11.2671 | 12.4509 |  | 12.4847 |  |  | 11.8507 | 12.708 | 12.7314 | [6 empty] | 12.6338 |  |  | 11.3237 |  |  | 9.4879 | 10.4976 | 12.6362 | 7.6508 | 9.3805 | 12.9667 | 7.9707 | 9.5932 | 12.908 | 9.3601 | 10.593 | 7.7975 | 10.5895 | 8.3816 | 10.2479 | 8.0495 | 9.6681 | 13.7381 | 10.8381 | 10.4922 | 12.1025 | 8.2363 | 9.9235 | 13.0729 | 7.6047 | 10.3281 | 9.8744 | 10.0411 | 8.3569 | 10.2759 | -0.20629 | 20.9571 | 0.034021 | 0.048486 | -38.2122 | 3.1214 | -1.02 | 0.29 | 0.27604 | -0.42211 | 0.5734 | 0.47679 | -0.3934 | -0.46876 | 0.8587 | 0.41782 | 0.4295 | 0.42588 | 0.4374 | 0.63261 | 0.42928 | 0.4252
42810.432 | -695 | 18.6275 | 18.6603 | 18.6389 | 18.6657 | 18.0397 | 16.7115 | 14.7947 | 16.7733 | 17.2613 | 17.3571 | 17.3854 | 16.9567 | 16.0263 | 14.6509 | 15.0999 | 15.06 | 15.5993 | 13.4573 | 13.5838 | 14.1722 |  |  |  | 16.6875 | 16.0393 | 15.1753 | 10.5113 | 9.8836 | 9.9916 | 17.3396 | 16.4424 | 15.2374 | 16.944 | 16.2344 | 15.2511 | 10.9873 | 11.54 |  | 12.4482 | 10.7039 | 10.7601 | 8.8043 |  | 6.2219 | 6.1779 | 5.6756 | 5.6819 | 5.6872 | 5.9398 | 6.1267 | 4.4161 | 6.2752 | 4.3963 | 6.5999 | 8.1994 | 42.4421 | 46.6012 | 43.073 | 15.3922 |  |  | -0.15749 | -0.20428 | 0.25221 | 0.040086 | -0.14374 | -0.002432 | 0.61233 | 0.098404 | -1.549 | -0.29158 | -0.30928 | 8.8798 | 8.8808 | 2.0087 | 15.9946 | 16.8279 | 17.3583 | 17.676 | 17.652 | 16.647 | 15.0058 | 16.9305 | 17.265 | 17.5537 | 17.5875 | 17.3402 | 16.5631 | 14.8148 | 5.8911 | 8.2997 | 5.0644 | 5.4925 | 5.5858 | 6.6406 | 7.5663 | 16.0791 | 15.6604 | 15.5038 | 14.4397 | 14.3365 | 14.2732 |  |  |  | 10.9356 | 9.514 | 9.1708 | 8.906 | 0.19475 | 0.11652 | 12.9638 |  |  | 10.6842 |  |  | 16.9904 | 16.2012 | 15.1872 | 16.4839 | 15.7753 | 14.895 | 10.5847 | 10.8233 | 11.6391 | 11.6004 | 9.131 |  | 10.8981 | 7.7553 | 10.2436 | 9.324 | 11.2651 | 12.4786 |  | 12.4941 |  |  | 11.8553 | 12.6971 | 12.7285 | [6 empty] | 12.6282 |  |  | 11.3295 |  |  | 9.4853 | 10.4976 | 12.6368 | 7.6364 | 9.3659 | 12.9685 | 7.9655 | 9.6019 | 12.9167 | 9.3529 | 10.5923 | 7.776 | 10.5782 | 8.3765 | 10.2517 | 8.0795 | 9.6933 | 13.7321 | 10.8462 | 10.4808 | 12.0971 | 8.2459 | 9.9296 | 13.0723 | 7.6128 | 10.3296 | 9.8723 | 10.0358 | 8.3516 | 10.2757 | 0.016551 | 20.9578 | 0.034067 | 0.049579 | -38.1663 | 3.1214 | -1.06 | 0.36 | -0.46537 | -0.52642 | 0.58493 | 0.2332 | -0.4414 | -0.057414 | 0.91103 | 0.41819 | 0.43483 | 0.42494 | 0.43075 | 0.63008 | 0.43021 | 0.42568
42810.432 | -694 | 18.6365 | 18.6656 | 18.644 | 18.6704 | 18.0482 | 16.7249 | 14.791 | 16.78 | 17.2618 | 17.3651 | 17.3878 | 16.9604 | 16.0281 | 14.6503 | 15.103 | 15.0667 | 15.6059 | 13.4583 | 13.5893 | 14.1747 |  |  |  | 16.6875 | 16.0466 | 15.1795 | 10.5137 | 9.8856 | 9.9815 | 17.3359 | 16.4413 | 15.2346 | 16.9334 | 16.2292 | 15.2489 | 10.9771 | 11.5412 |  | 12.4421 | 10.6937 | 10.7401 | 8.7478 |  | 6.2305 | 6.182 | 5.6745 | 5.6855 | 5.6946 | 5.9397 | 6.1419 | 4.4254 | 6.2857 | 4.5082 | 6.6091 | 8.1907 | 42.4311 | 46.5918 | 43.062 | 15.3793 |  |  | 0.050819 | -0.097821 | 0.14576 | 0.11237 | 0.002136 | 0.010056 | 0.41191 | -0.030392 | 0.17282 | -0.16927 | -0.2459 | 8.8782 | 8.8793 | 2.0084 | 15.9915 | 16.8262 | 17.3525 | 17.6739 | 17.6452 | 16.6446 | 15.0065 | 16.9308 | 17.257 | 17.546 | 17.5811 | 17.3363 | 16.5659 | 14.8073 | 5.9284 | 8.3529 | 5.0869 | 5.541 | 5.601 | 6.6474 | 7.5605 | 16.0817 | 15.67 | 15.5136 | 14.443 | 14.3328 | 14.2786 |  |  |  | 10.929 | 9.5067 | 9.1663 | 8.9097 | 0.23466 | 0.017904 | 12.9587 |  |  | 10.6793 |  |  | 16.9935 | 16.2026 | 15.1905 | 16.488 | 15.778 | 14.8989 | 10.5781 | 10.8246 | 11.6522 | 11.6011 | 9.1153 |  | 10.8988 | 7.5473 | 10.2429 | 9.3313 | 11.2621 | 12.476 |  | 12.4953 |  |  | 11.8659 | 12.6964 | 12.7345 | [6 empty] | 12.6296 |  |  | 11.3341 |  |  | 9.4818 | 10.4961 | 12.6187 | 7.6141 | 9.3528 | 12.9695 | 7.9597 | 9.5991 | 12.9082 | 9.3508 | 10.5959 | 7.7677 | 10.5663 | 8.3691 | 10.2448 | 8.0903 | 9.7167 | 13.7342 | 10.8584 | 10.4805 | 12.0926 | 8.2469 | 9.9254 | 13.0773 | 7.6126 | 10.3445 | 9.8806 | 10.0259 | 8.3469 | 10.2794 | 0.026759 | 20.9574 | 0.03351 | 0.050541 | -38.164 | 3.1214 | -1.08 | 0.36 | 0.26435 | -0.36429 | 0.44468 | 0.39043 | 0.053807 | 0.11675 | 0.74721 | 0.41865 | 0.44059 | 0.42463 | 0.42739 | 0.62691 | 0.43144 | 0.42536
42810.432 | -693 | 18.6312 | 18.6612 | 18.6418 | 18.6683 | 18.0434 | 16.7187 | 14.7936 | 16.7752 | 17.2602 | 17.3695 | 17.3892 | 16.9557 | 16.0248 | 14.6405 | 15.1064 | 15.0684 | 15.6052 | 13.4642 | 13.5913 | 14.1749 |  |  |  | 16.6859 | 16.0354 | 15.1724 | 10.5002 | 9.8783 | 9.9587 | 17.3428 | 16.448 | 15.2408 | 16.9426 | 16.236 | 15.2596 | 10.9861 | 11.5514 |  | 12.4515 | 10.6968 | 10.7546 | 8.7121 |  | 6.2249 | 6.179 | 5.6728 | 5.6829 | 5.6882 | 5.9418 | 6.1337 | 4.4195 | 6.2764 | 4.5609 | 6.6008 | 8.1934 | 42.4259 | 46.5944 | 43.0555 | 15.3742 |  |  | 0.015991 | -0.26867 | 0.09122 | -0.026286 | -0.009036 | -0.007032 | 0.41848 | -0.011992 | -0.09203 | 0.024374 | -0.28703 | 8.8766 | 8.8776 | 2.0085 | 15.998 | 16.8383 | 17.3606 | 17.6775 | 17.6431 | 16.6492 | 15.0136 | 16.9377 | 17.2642 | 17.5434 | 17.5896 | 17.3419 | 16.5648 | 14.8128 | 5.9702 | 8.3671 | 5.1035 | 5.5544 | 5.6245 | 6.648 | 7.5569 | 16.0708 | 15.6623 | 15.5104 | 14.4414 | 14.3382 | 14.277 |  |  |  | 10.9258 | 9.4954 | 9.1587 | 8.9327 | 0.21339 | 0.042182 | 12.9669 |  |  | 10.6937 |  |  | 16.9996 | 16.206 | 15.1907 | 16.486 | 15.7834 | 14.8952 | 10.5699 | 10.8267 | 11.6573 | 11.5932 | 9.1138 |  | 10.897 | 7.4481 | 10.2391 | 9.3277 | 11.264 | 12.478 |  | 12.4939 |  |  | 11.891 | 12.7039 | 12.7414 | [6 empty] | 12.6383 |  |  | 11.3384 |  |  | 9.4813 | 10.4984 | 12.6197 | 7.5851 | 9.3566 | 12.9686 | 7.9615 | 9.6017 | 12.9097 | 9.3539 | 10.5979 | 7.7726 | 10.5695 | 8.3686 | 10.246 | 8.097 | 9.7324 | 13.7387 | 10.8598 | 10.4767 | 12.0791 | 8.2526 | 9.9218 | 13.0826 | 7.6164 | 10.3541 | 9.88 | 10.0155 | 8.346 | 10.274 | -0.33648 | 20.9575 | 0.03382 | 0.050954 | -38.117 | 3.1214 | -1.24 | 0.33 | 0.14828 | -0.60372 | 0.35178 | -0.18884 | -0.11067 | -0.097629 | 0.75315 | 0.41863 | 0.44322 | 0.4248 | 0.42282 | 0.62465 | 0.43273 | 0.42462
42810.432 | -692 | 18.639 | 18.6659 | 18.6494 | 18.6693 | 18.0431 | 16.7206 | 14.7978 | 16.7831 | 17.2609 | 17.3673 | 17.3926 | 16.9595 | 16.0254 | 14.6428 | 15.1018 | 15.0655 | 15.5972 | 13.4535 | 13.5813 | 14.1681 |  |  |  | 16.6806 | 16.035 | 15.1648 | 10.491 | 9.8592 | 9.9513 | 17.3453 | 16.4494 | 15.242 | 16.9513 | 16.2327 | 15.2665 | 10.9833 | 11.5466 |  | 12.4487 | 10.6972 | 10.7549 | 8.6778 |  | 6.219 | 6.1753 | 5.6636 | 5.6761 | 5.6749 | 5.9251 | 6.1262 | 4.3651 | 6.2753 | 4.5074 | 6.5938 | 8.1926 | 42.43 | 46.5894 | 43.056 | 15.3652 |  |  | -0.098349 | -0.21742 | 0.10173 | -0.04337 | -0.068176 | -0.057628 | 0.56896 | -0.035648 | -0.34073 | -0.77454 | -0.19344 | 8.875 | 8.8763 | 2.0085 | 15.9956 | 16.8322 | 17.3635 | 17.6745 | 17.6453 | 16.6494 | 15.0125 | 16.94 | 17.2703 | 17.5447 | 17.5927 | 17.3453 | 16.5683 | 14.8119 | 6.0428 | 8.3976 | 5.123 | 5.5329 | 5.608 | 6.6504 | 7.5521 | 16.0749 | 15.6636 | 15.5152 | 14.4455 | 14.3307 | 14.2755 |  |  |  | 10.9337 | 9.4903 | 9.1509 | 8.9115 | 0.14734 | -0.012396 | 12.956 |  |  | 10.6974 |  |  | 16.9913 | 16.2034 | 15.1936 | 16.4938 | 15.7747 | 14.8977 | 10.5446 | 10.8251 | 11.6561 | 11.5898 | 9.1059 |  | 10.9007 | 7.4574 | 10.2349 | 9.3322 | 11.2694 | 12.5278 |  | 12.4958 |  |  | 11.9003 | 12.7064 | 12.7242 | [6 empty] | 12.6288 |  |  | 11.3358 |  |  | 9.4851 | 10.4948 | 12.6181 | 7.5541 | 9.3659 | 12.9689 | 7.9699 | 9.5909 | 12.9148 | 9.3465 | 10.5964 | 7.7666 | 10.5764 | 8.3694 | 10.2411 | 8.0967 | 9.7538 | 13.7532 | 10.8676 | 10.4772 | 12.0745 | 8.2652 | 9.9322 | 13.0878 | 7.6373 | 10.367 | 9.8813 | 10.0206 | 8.351 | 10.2754 | -0.21399 | 20.9574 | 0.033533 | 0.050433 | -38.145 | 3.1214 | -1.27 | 0.39 | -0.36772 | -0.54309 | 0.37149 | -0.24256 | -0.30398 | -0.27948 | 0.87815 | 0.41898 | 0.44282 | 0.42485 | 0.41503 | 0.62192 | 0.43359 | 0.42546
42810.432 | -691 | 18.642 | 18.6662 | 18.6438 | 18.6622 | 18.038 | 16.7109 | 14.7924 | 16.7772 | 17.2585 | 17.3611 | 17.3843 | 16.9533 | 16.023 | 14.6436 | 15.095 | 15.0622 | 15.6025 | 13.4539 | 13.5862 | 14.1672 |  |  |  | 16.6866 | 16.0376 | 15.1657 | 10.4766 | 9.8625 | 9.9439 | 17.3426 | 16.4471 | 15.2423 | 16.9527 | 16.2334 | 15.2604 | 10.9767 | 11.5227 |  | 12.4449 | 10.6912 | 10.7489 | 8.6292 |  | 6.2261 | 6.1755 | 5.6781 | 5.6969 | 5.6984 | 5.9308 | 6.1487 | 4.2712 | 6.2865 | 4.469 | 6.6022 | 8.1956 | 42.4325 | 46.5646 | 43.0621 | 15.3622 |  |  | 0.014675 | -0.13593 | 0.049164 | 0.15705 | -0.12534 | 0.3373 | 0.54268 | -0.15196 | -0.15294 | -0.55971 | -0.34724 | 8.8763 | 8.8773 | 2.0086 | 16.0057 | 16.8453 | 17.3644 | 17.6882 | 17.6576 | 16.657 | 15.0077 | 16.9473 | 17.2681 | 17.5491 | 17.5963 | 17.3487 | 16.5712 | 14.8161 | 6.1161 | 8.4137 | 5.1328 | 5.5456 | 5.6012 | 6.6445 | 7.5449 | 16.0688 | 15.6593 | 15.5057 | 14.4403 | 14.3256 | 14.2723 |  |  |  | 10.9349 | 9.4771 | 9.1406 | 8.8998 | 0.039758 | 0.098642 | 12.9616 |  |  | 10.6969 |  |  | 16.9897 | 16.2074 | 15.1918 | 16.489 | 15.7761 | 14.9056 | 10.4898 | 10.8253 | 11.6561 | 11.5859 | 9.1035 |  | 10.8919 | 7.524 | 10.2384 | 9.3611 | 11.2704 | 12.5775 |  | 12.4858 |  |  | 11.9047 | 12.6929 | 12.723 | [6 empty] | 12.6191 |  |  | 11.3332 |  |  | 9.4849 | 10.499 | 12.6045 | 7.5204 | 9.3684 | 12.9757 | 7.9791 | 9.6105 | 12.9177 | 9.3433 | 10.5966 | 7.771 | 10.5882 | 8.3706 | 10.2452 | 8.1035 | 9.7743 | 13.762 | 10.8656 | 10.4826 | 12.0614 | 8.2704 | 9.9244 | 13.0885 | 7.6519 | 10.3753 | 9.8687 | 10.0145 | 8.3601 | 10.2794 | -0.041806 | 20.958 | 0.033395 | 0.050491 | -38.1398 | 3.1214 | -1.5 | 0.39 | 0.14204 | -0.42942 | 0.25825 | 0.46157 | -0.41218 | 0.67614 | 0.85764 | 0.41875 | 0.44109 | 0.42408 | 0.4062 | 0.61999 | 0.43472 | 0.42583
42810.432 | -690 | 18.6353 | 18.671 | 18.6438 | 18.6611 | 18.0398 | 16.7099 | 14.7955 | 16.7776 | 17.2618 | 17.3577 | 17.3843 | 16.9524 | 16.0226 | 14.6459 | 15.0995 | 15.0653 | 15.6046 | 13.4676 | 13.594 | 14.1764 |  |  |  | 16.6831 | 16.0455 | 15.1692 | 10.4884 | 9.8684 | 9.954 | 17.347 | 16.4488 | 15.245 | 16.9471 | 16.2343 | 15.2541 | 10.9801 | 11.5004 |  | 12.4401 | 10.6918 | 10.743 | 8.6027 |  | 6.2165 | 6.1671 | 5.6711 | 5.6963 | 5.7097 | 5.9322 | 6.154 | 4.1977 | 6.2803 | 4.4138 | 6.6025 | 8.202 | 42.4486 | 46.5479 | 43.0679 | 15.3519 |  |  | 0.001535 | -0.20099 | 0.19898 | 0.045342 | -0.001808 | -0.25739 | 0.44148 | -0.30441 | -1.3707 | -0.62664 | -0.41082 | 8.8849 | 8.8862 | 2.0086 | 15.9973 | 16.8369 | 17.3569 | 17.6758 | 17.6468 | 16.6461 | 15.006 | 16.9336 | 17.2612 | 17.5442 | 17.5967 | 17.3444 | 16.5646 | 14.8127 | 6.1886 | 8.4669 | 5.1393 | 5.5948 | 5.618 | 6.6508 | 7.553 | 16.0787 | 15.6643 | 15.508 | 14.446 | 14.3331 | 14.2775 |  |  |  | 10.9366 | 9.4711 | 9.1383 | 8.8776 | 0.019093 | 0.090549 | 12.9541 |  |  | 10.7033 |  |  | 16.9946 | 16.2019 | 15.1873 | 16.4846 | 15.7739 | 14.8976 | 10.4391 | 10.8159 | 11.6569 | 11.5848 | 9.078 |  | 10.8901 | 7.5846 | 10.2349 | 9.3741 | 11.2638 | 12.6114 |  | 12.485 |  |  | 11.8934 | 12.7159 | 12.7274 | [6 empty] | 12.6398 |  |  | 11.3484 |  |  | 9.4893 | 10.5056 | 12.5997 | 7.5155 | 9.3725 | 12.9848 | 7.9786 | 9.6054 | 12.9209 | 9.3453 | 10.5946 | 7.7844 | 10.5988 | 8.3757 | 10.248 | 8.1111 | 9.7866 | 13.7506 | 10.8623 | 10.4741 | 12.0269 | 8.2744 | 9.9095 | 13.0804 | 7.6544 | 10.3796 | 9.8516 | 10.0028 | 8.3512 | 10.2664 | -0.043732 | 20.9568 | 0.033545 | 0.049919 | -38.1277 | 3.1214 | -1.67 | 0.33 | 0.04594 | -0.52216 | 0.51955 | 0.24801 | -0.049503 | -0.59065 | 0.77355 | 0.4194 | 0.43929 | 0.4235 | 0.39888 | 0.62022 | 0.43557 | 0.4265
42810.4321 | -689 | 18.6415 | 18.6647 | 18.6562 | 18.6792 | 18.0467 | 16.7176 | 14.8008 | 16.7814 | 17.274 | 17.3724 | 17.3913 | 16.9614 | 16.03 | 14.6518 | 15.1022 | 15.0619 | 15.595 | 13.4595 | 13.5879 | 14.1719 |  |  |  | 16.6912 | 16.0394 | 15.1726 | 10.4731 | 9.8596 | 9.964 | 17.3437 | 16.4468 | 15.2475 | 16.9461 | 16.2335 | 15.2515 | 10.9791 | 11.4761 |  | 12.4285 | 10.6934 | 10.7315 | 8.5756 |  | 6.2251 | 6.176 | 5.6762 | 5.7063 | 5.7293 | 5.9475 | 6.1784 | 4.1464 | 6.2862 | 4.3785 | 6.6069 | 8.1933 | 42.4523 | 46.5292 | 43.0641 | 15.3399 |  |  | 0.038987 | -0.10176 | 0.22593 | 0.069654 | -0.047148 | -0.058284 | 0.48945 | -0.081648 | -0.73869 | 0.009688 | -0.39969 | 8.8911 | 8.8923 | 2.0085 | 15.9974 | 16.8291 | 17.3581 | 17.679 | 17.6499 | 16.646 | 15.0113 | 16.9346 | 17.2543 | 17.5434 | 17.5978 | 17.3401 | 16.5713 | 14.8125 | 6.2318 | 8.4644 | 5.1329 | 5.6405 | 5.6563 | 6.6498 | 7.5401 | 16.0723 | 15.6571 | 15.5111 | 14.4408 | 14.3237 | 14.2701 |  |  |  | 10.9195 | 9.4594 | 9.1335 | 8.8695 | 0.097297 | 0.008682 | 12.9474 |  |  | 10.7204 |  |  | 16.9894 | 16.2019 | 15.1875 | 16.4857 | 15.7843 | 14.8976 | 10.3862 | 10.8163 | 11.6512 | 11.6013 | 9.0531 |  | 10.8859 | 7.5808 | 10.2371 | 9.3553 | 11.2602 | 12.6474 |  | 12.4933 |  |  | 11.9198 | 12.7029 | 12.7229 | [6 empty] | 12.6408 |  |  | 11.3549 |  |  | 9.477 | 10.4921 | 12.5896 | 7.5205 | 9.3615 | 12.9736 | 7.9786 | 9.602 | 12.9178 | 9.3445 | 10.6052 | 7.7828 | 10.5992 | 8.3695 | 10.2313 | 8.1186 | 9.806 | 13.7535 | 10.8665 | 10.4785 | 11.9992 | 8.2895 | 9.9088 | 13.0823 | 7.6748 | 10.3875 | 9.8495 | 9.9975 | 8.3485 | 10.2663 | -0.13965 | 20.9575 | 0.03359 | 0.049789 | -38.0737 | 3.1214 | -1.43 | 0.27 | 0.23153 | -0.37155 | 0.55361 | 0.30739 | -0.2528 | -0.28107 | 0.81452 | 0.41995 | 0.43947 | 0.4239 | 0.39395 | 0.61943 | 0.43629 | 0.42616
42810.4321 | -688 | 18.6308 | 18.6695 | 18.6549 | 18.6801 | 18.0412 | 16.7166 | 14.8036 | 16.7836 | 17.2704 | 17.3642 | 17.3897 | 16.9608 | 16.0206 | 14.6445 | 15.0893 | 15.0512 | 15.5892 | 13.4614 | 13.5794 | 14.1607 |  |  |  | 16.6844 | 16.0399 | 15.167 | 10.4808 | 9.8606 | 9.9666 | 17.3343 | 16.4453 | 15.246 | 16.9568 | 16.2415 | 15.261 | 10.9834 | 11.4518 |  | 12.4381 | 10.6957 | 10.7259 | 8.5523 |  | 6.2242 | 6.1812 | 5.681 | 5.7223 | 5.7359 | 5.9563 | 6.1815 | 4.1065 | 6.2762 | 4.3451 | 6.6066 | 8.1971 | 42.4728 | 46.5215 | 43.0692 | 15.3323 |  |  | 0.023219 | -0.084021 | 0.10305 | -0.009198 | 0.007392 | 0.20522 | 0.24566 | -0.19467 | -0.29266 | -0.1313 | -0.45652 | 8.8888 | 8.8903 | 2.0087 | 15.9967 | 16.8384 | 17.3627 | 17.6785 | 17.6536 | 16.6549 | 15.0077 | 16.9336 | 17.2557 | 17.5445 | 17.5892 | 17.3442 | 16.5691 | 14.8125 | 6.2685 | 8.4799 | 5.1567 | 5.6858 | 5.6875 | 6.6535 | 7.5433 | 16.0796 | 15.6639 | 15.5208 | 14.4491 | 14.3378 | 14.287 |  |  |  | 10.9348 | 9.4628 | 9.1455 | 8.8653 | 0.21541 | -0.071303 | 12.934 |  |  | 10.7138 |  |  | 16.9939 | 16.202 | 15.189 | 16.4905 | 15.7746 | 14.8953 | 10.3237 | 10.8126 | 11.6506 | 11.5988 | 9.0445 |  | 10.896 | 7.5497 | 10.2257 | 9.3869 | 11.2617 | 12.6583 |  | 12.4997 |  |  | 11.931 | 12.6812 | 12.7262 | [6 empty] | 12.6301 |  |  | 11.3616 |  |  | 9.4878 | 10.4945 | 12.5819 | 7.5317 | 9.3606 | 12.984 | 7.9669 | 9.5934 | 12.916 | 9.3388 | 10.6062 | 7.7901 | 10.615 | 8.353 | 10.2301 | 8.1269 | 9.8173 | 13.7632 | 10.8708 | 10.4968 | 11.9756 | 8.2936 | 9.9085 | 13.072 | 7.7048 | 10.404 | 9.8497 | 9.9875 | 8.3601 | 10.2683 | -0.15929 | 20.9576 | 0.033671 | 0.049506 | -38.1479 | 3.1214 | -1.27 | 0.29 | 0.17868 | -0.33761 | 0.37389 | -0.11171 | 0.1001 | 0.52742 | 0.57706 | 0.42053 | 0.43995 | 0.42308 | 0.39031 | 0.61715 | 0.43708 | 0.42678
42810.4321 | -687 | 18.6446 | 18.6669 | 18.6564 | 18.6758 | 18.0481 | 16.7185 | 14.7878 | 16.7843 | 17.2712 | 17.3709 | 17.3928 | 16.9603 | 16.0231 | 14.6534 | 15.1104 | 15.0658 | 15.6044 | 13.4628 | 13.5893 | 14.1763 |  |  |  | 16.6927 | 16.0418 | 15.1692 | 10.4767 | 9.8619 | 9.9768 | 17.3485 | 16.4485 | 15.2481 | 16.9484 | 16.2338 | 15.2608 | 10.976 | 11.4205 |  | 12.4378 | 10.6959 | 10.7272 | 8.5165 |  | 6.2151 | 6.1685 | 5.6782 | 5.7084 | 5.7338 | 5.9404 | 6.1749 | 4.0596 | 6.2728 | 4.2839 | 6.5972 | 8.1995 | 42.4792 | 46.5257 | 43.0752 | 15.3331 |  |  | -0.007665 | 0.053971 | 0.042592 | -0.024314 | 0.050764 | -0.099684 | 0.17141 | -0.02382 | -0.28177 | -0.78231 | -0.35121 | 8.8803 | 8.8814 | 2.0083 | 16.0018 | 16.8452 | 17.3587 | 17.6801 | 17.6575 | 16.655 | 15.0067 | 16.9365 | 17.2624 | 17.5487 | 17.5908 | 17.3381 | 16.5673 | 14.8043 | 6.2721 | 8.5083 | 5.1832 | 5.7229 | 5.7255 | 6.6545 | 7.5384 | 16.0746 | 15.6591 | 15.5115 | 14.4368 | 14.3309 | 14.2753 |  |  |  | 10.9208 | 9.4571 | 9.1353 | 8.8371 | 0.11452 | -0.048907 | 12.9335 |  |  | 10.723 |  |  | 16.9987 | 16.2101 | 15.1929 | 16.486 | 15.7754 | 14.8995 | 10.2687 | 10.8156 | 11.6606 | 11.604 | 9.0345 |  | 10.884 | 7.559 | 10.2217 | 9.3891 | 11.2692 | 12.6355 |  | 12.492 |  |  | 11.9301 | 12.6866 | 12.7077 | [6 empty] | 12.6335 |  |  | 11.356 |  |  | 9.4788 | 10.4841 | 12.5757 | 7.5402 | 9.3479 | 12.9858 | 7.9544 | 9.5819 | 12.9222 | 9.331 | 10.5917 | 7.7896 | 10.6259 | 8.3271 | 10.2353 | 8.1479 | 9.8223 | 13.7691 | 10.8766 | 10.5032 | 11.9642 | 8.3016 | 9.9168 | 13.0772 | 7.7146 | 10.4052 | 9.844 | 9.9819 | 8.3603 | 10.272 | -0.027747 | 20.9575 | 0.033229 | 0.050158 | -38.1814 | 3.1214 | -1.24 | 0.38 | -0.10266 | 0.27058 | 0.24037 | -0.18161 | 0.26231 | -0.36758 | 0.48201 | 0.42041 | 0.43957 | 0.42326 | 0.39003 | 0.61364 | 0.43783 | 0.4271
42810.4321 | -686 | 18.6434 | 18.6683 | 18.647 | 18.6708 | 18.0448 | 16.7177 | 14.7966 | 16.783 | 17.2702 | 17.3613 | 17.3897 | 16.9615 | 16.0205 | 14.6529 | 15.1028 | 15.0636 | 15.5975 | 13.4668 | 13.583 | 14.1761 |  |  |  | 16.6822 | 16.0284 | 15.1737 | 10.4722 | 9.8522 | 9.9844 | 17.3469 | 16.454 | 15.2558 | 16.9499 | 16.2438 | 15.2621 | 10.9837 | 11.4284 |  | 12.4427 | 10.7014 | 10.7395 | 8.5199 |  | 6.2228 | 6.1765 | 5.6779 | 5.7171 | 5.7377 | 5.9347 | 6.1825 | 4.0619 | 6.2788 | 4.2717 | 6.6062 | 8.1977 | 42.4591 | 46.5161 | 43.0717 | 15.3166 |  |  | 0.19407 | -0.20231 | 0.070848 | -0.010514 | 0.21767 | -0.078 | 0.58474 | 0.19237 | -0.74958 | -0.369 | -0.14178 | 8.8852 | 8.8862 | 2.0087 | 16.0058 | 16.8415 | 17.3658 | 17.6865 | 17.6521 | 16.6555 | 15.0158 | 16.9329 | 17.2605 | 17.5501 | 17.5894 | 17.3439 | 16.5728 | 14.8025 | 6.2622 | 8.5042 | 5.2112 | 5.7741 | 5.7793 | 6.6513 | 7.5413 | 16.0709 | 15.6642 | 15.5109 | 14.4416 | 14.3281 | 14.2767 |  |  |  | 10.9229 | 9.4562 | 9.1332 | 8.8468 | 0.20467 | 0.058931 | 12.939 |  |  | 10.7262 |  |  | 16.9879 | 16.2003 | 15.1879 | 16.4851 | 15.7794 | 14.8949 | 10.2361 | 10.8057 | 11.6576 | 11.5906 | 9.0388 |  | 10.8848 | 7.5473 | 10.2187 | 9.3543 | 11.2641 | 12.6114 |  | 12.49 |  |  | 11.9121 | 12.6905 | 12.7031 | [6 empty] | 12.6233 |  |  | 11.3715 |  |  | 9.4836 | 10.4867 | 12.5646 | 7.5571 | 9.3582 | 12.9967 | 7.9492 | 9.5926 | 12.9294 | 9.3334 | 10.5978 | 7.7977 | 10.638 | 8.3087 | 10.2207 | 8.163 | 9.8342 | 13.7708 | 10.8797 | 10.5009 | 11.9598 | 8.3104 | 9.9187 | 13.0837 | 7.7371 | 10.419 | 9.854 | 9.982 | 8.3717 | 10.2724 | -0.25771 | 20.9573 | 0.034038 | 0.050273 | -38.1773 | 3.1214 | -1.17 | 0.27 | 0.51658 | -0.52387 | 0.31002 | -0.11943 | 0.54317 | -0.32515 | 0.89026 | 0.42031 | 0.43979 | 0.42406 | 0.39075 | 0.61086 | 0.43799 | 0.4269
42810.4321 | -685 | 18.6449 | 18.6747 | 18.6528 | 18.6716 | 18.0506 | 16.7186 | 14.7919 | 16.7854 | 17.2665 | 17.3679 | 17.3899 | 16.9589 | 16.0307 | 14.654 | 15.1122 | 15.0752 | 15.6038 | 13.4724 | 13.5901 | 14.183 |  |  |  | 16.6971 | 16.0381 | 15.1782 | 10.4787 | 9.8494 | 9.9909 | 17.3493 | 16.4432 | 15.2498 | 16.9627 | 16.2419 | 15.2606 | 10.9791 | 11.4383 |  | 12.4379 | 10.7057 | 10.7448 | 8.5301 |  | 6.2339 | 6.1805 | 5.6702 | 5.7195 | 5.7318 | 5.9354 | 6.1767 | 4.0799 | 6.2796 | 4.2438 | 6.6063 | 8.2025 | 42.42 | 46.4943 | 43.0787 | 15.3127 |  |  | 0.020591 | -0.002541 | 0.1359 | -0.13537 | 0.17956 | -0.2068 | 0.51508 | 0.032692 | -0.45029 | -0.11116 | -0.24709 | 8.8738 | 8.8751 | 2.0084 | 15.9972 | 16.8417 | 17.3668 | 17.6859 | 17.6495 | 16.6627 | 15.0189 | 16.934 | 17.2571 | 17.5436 | 17.5864 | 17.3408 | 16.5668 | 14.8081 | 6.2312 | 8.4691 | 5.2162 | 5.8024 | 5.8193 | 6.6367 | 7.5219 | 16.0636 | 15.667 | 15.5053 | 14.4377 | 14.3253 | 14.2686 |  |  |  | 10.9201 | 9.4494 | 9.1277 | 8.8449 | 0.07258 | 0.055732 | 12.9292 |  |  | 10.7176 |  |  | 16.9855 | 16.189 | 15.182 | 16.4776 | 15.7725 | 14.889 | 10.2331 | 10.8053 | 11.6407 | 11.5791 | 9.0184 |  | 10.8847 | 7.5321 | 10.219 | 9.3226 | 11.2632 | 12.5741 |  | 12.4888 |  |  | 11.9376 | 12.6911 | 12.7133 | [6 empty] | 12.6213 |  |  | 11.3749 |  |  | 9.4905 | 10.4815 | 12.5543 | 7.5678 | 9.3623 | 12.9994 | 7.9326 | 9.5941 | 12.9327 | 9.3283 | 10.5881 | 7.8092 | 10.6504 | 8.2961 | 10.2149 | 8.1696 | 9.8425 | 13.7714 | 10.8833 | 10.5024 | 11.9507 | 8.3101 | 9.92 | 13.0768 | 7.7506 | 10.4213 | 9.8577 | 9.9785 | 8.3673 | 10.2717 | 0.011544 | 20.9577 | 0.033918 | 0.050657 | -38.1149 | 3.1214 | -1.09 | 0.38 | 0.16827 | -0.058712 | 0.42938 | -0.42853 | 0.49333 | -0.52943 | 0.83555 | 0.42088 | 0.44022 | 0.42491 | 0.3925 | 0.60806 | 0.43756 | 0.42686
42810.4321 | -684 | 18.6447 | 18.6686 | 18.6552 | 18.67 | 18.0429 | 16.715 | 14.7928 | 16.7785 | 17.2683 | 17.3666 | 17.3877 | 16.9569 | 16.033 | 14.6579 | 15.1055 | 15.0666 | 15.6002 | 13.4671 | 13.5863 | 14.1704 |  |  |  | 16.6929 | 16.0359 | 15.175 | 10.4699 | 9.833 | 9.9755 | 17.3472 | 16.4481 | 15.2486 | 16.9577 | 16.2382 | 15.2605 | 10.9807 | 11.4486 |  | 12.4347 | 10.7091 | 10.7473 | 8.5541 |  | 6.2338 | 6.1813 | 5.6738 | 5.7162 | 5.7373 | 5.9327 | 6.1679 | 4.0734 | 6.2802 | 4.1686 | 6.604 | 8.1934 | 42.3684 | 46.4772 | 43.0832 | 15.3001 |  |  | 0.003503 | -0.13857 | 0.00382 | -0.06177 | 0.09216 | 0.071824 | 0.19638 | 0.031376 | -0.27846 | 0.18047 | -0.31127 | 8.8738 | 8.875 | 2.0087 | 16.0096 | 16.8545 | 17.3692 | 17.6907 | 17.6642 | 16.6614 | 15.0264 | 16.9461 | 17.2626 | 17.5582 | 17.5917 | 17.3477 | 16.5699 | 14.8125 | 6.2657 | 8.4874 | 5.2155 | 5.849 | 5.8864 | 6.6425 | 7.5234 | 16.0759 | 15.6733 | 15.5198 | 14.447 | 14.3362 | 14.2785 |  |  |  | 10.9284 | 9.457 | 9.1428 | 8.8666 | 0.16659 | -0.11045 | 12.9241 |  |  | 10.7279 |  |  | 16.9889 | 16.2009 | 15.1941 | 16.4791 | 15.773 | 14.9046 | 10.2627 | 10.8007 | 11.6424 | 11.5809 | 8.9736 |  | 10.8827 | 7.5115 | 10.2214 | 9.2868 | 11.2629 | 12.5386 |  | 12.4903 |  |  | 11.9288 | 12.6759 | 12.7077 | [6 empty] | 12.6036 |  |  | 11.3723 |  |  | 9.4867 | 10.4737 | 12.5558 | 7.5807 | 9.3644 | 13.0014 | 7.9142 | 9.5871 | 12.9315 | 9.3276 | 10.581 | 7.8167 | 10.6579 | 8.2758 | 10.2172 | 8.1727 | 9.8379 | 13.7595 | 10.8814 | 10.5 | 11.9218 | 8.2966 | 9.9119 | 13.0554 | 7.7467 | 10.4103 | 9.8406 | 9.9581 | 8.352 | 10.2527 | 0.084539 | 20.957 | 0.033941 | 0.050324 | -38.0902 | 3.1214 | -1.07 | 0.23 | 0.069403 | -0.43356 | 0.071988 | -0.28948 | 0.35343 | 0.31201 | 0.51592 | 0.42206 | 0.44088 | 0.4259 | 0.38935 | 0.60831 | 0.43694 | 0.42653
42810.4321 | -683 | 18.6444 | 18.6714 | 18.6549 | 18.6755 | 18.0444 | 16.7202 | 14.8008 | 16.782 | 17.2661 | 17.3692 | 17.3887 | 16.9593 | 16.0307 | 14.656 | 15.1067 | 15.06 | 15.5947 | 13.4621 | 13.5865 | 14.1671 |  |  |  | 16.6889 | 16.0385 | 15.1699 | 10.4606 | 9.8288 | 9.9474 | 17.3459 | 16.4522 | 15.2525 | 16.9508 | 16.2367 | 15.2583 | 10.9756 | 11.4607 |  | 12.4344 | 10.7179 | 10.7485 | 8.5828 |  | 6.2211 | 6.1723 | 5.6748 | 5.7183 | 5.733 | 5.9201 | 6.1603 | 4.066 | 6.2729 | 4.1127 | 6.5999 | 8.2014 | 42.3271 | 46.4626 | 43.0907 | 15.2965 |  |  | 0.050159 | -0.000569 | 0.01828 | 0.004598 | 0.23476 | -0.46636 | 0.081384 | -0.05076 | -0.38432 | -0.64258 | -0.27392 | 8.8808 | 8.8818 | 2.0085 | 16.0058 | 16.8489 | 17.3648 | 17.6825 | 17.6508 | 16.6483 | 15.0247 | 16.9377 | 17.2671 | 17.5453 | 17.5919 | 17.3449 | 16.569 | 14.8089 | 6.3188 | 8.4835 | 5.222 | 5.8729 | 5.9728 | 6.6441 | 7.515 | 16.0736 | 15.6643 | 15.5113 | 14.4355 | 14.326 | 14.2727 |  |  |  | 10.9138 | 9.4479 | 9.135 | 8.8615 | 0.12262 | -0.032157 | 12.929 |  |  | 10.7259 |  |  | 16.9904 | 16.2056 | 15.187 | 16.4793 | 15.7752 | 14.8994 | 10.2866 | 10.8005 | 11.6207 | 11.5823 | 8.9644 |  | 10.8869 | 7.523 | 10.2298 | 9.2711 | 11.2667 | 12.5075 |  | 12.4955 |  |  | 11.9191 | 12.6734 | 12.7062 | [6 empty] | 12.6097 |  |  | 11.3817 |  |  | 9.4909 | 10.4749 | 12.5602 | 7.6041 | 9.3698 | 13.012 | 7.9122 | 9.5937 | 12.9388 | 9.3338 | 10.5852 | 7.8234 | 10.665 | 8.2641 | 10.2208 | 8.182 | 9.8355 | 13.7481 | 10.8705 | 10.5044 | 11.9005 | 8.2836 | 9.9079 | 13.0485 | 7.7549 | 10.4195 | 9.838 | 9.9464 | 8.3523 | 10.2448 | -0.018309 | 20.9583 | 0.033539 | 0.050223 | -38.2194 | 3.1214 | -0.92 | 0.3 | 0.26261 | -0.027783 | 0.15747 | 0.078978 | 0.56407 | -0.79503 | 0.33212 | 0.42245 | 0.44083 | 0.42646 | 0.38363 | 0.60661 | 0.43597 | 0.4262
42810.4321 | -682 | 18.644 | 18.6703 | 18.6523 | 18.6715 | 18.0476 | 16.716 | 14.7943 | 16.7834 | 17.2586 | 17.3676 | 17.3866 | 16.9629 | 16.0244 | 14.6568 | 15.1057 | 15.06 | 15.5944 | 13.4654 | 13.5851 | 14.1672 |  |  |  | 16.6854 | 16.0415 | 15.1726 | 10.4508 | 9.8255 | 9.9223 | 17.3529 | 16.4588 | 15.2539 | 16.9556 | 16.2479 | 15.2642 | 10.9752 | 11.4888 |  | 12.4351 | 10.7319 | 10.7695 | 8.6105 |  | 6.2205 | 6.1813 | 5.675 | 5.72 | 5.7241 | 5.9122 | 6.1466 | 4.1392 | 6.2724 | 4.0776 | 6.6071 | 8.1954 | 42.2821 | 46.4359 | 43.0802 | 15.2789 |  |  | 0.12573 | -0.10045 | 0.075448 | -0.021686 | 0.1283 | -0.058944 | 0.1103 | -0.021848 | -0.42908 | -0.47201 | -0.27789 | 8.8843 | 8.8856 | 2.0087 | 15.9969 | 16.8361 | 17.365 | 17.6745 | 17.6409 | 16.6506 | 15.0184 | 16.9289 | 17.2557 | 17.54 | 17.5843 | 17.3405 | 16.559 | 14.8016 | 6.3377 | 8.4693 | 5.2843 | 5.8866 | 6.0114 | 6.6447 | 7.5141 | 16.0705 | 15.6671 | 15.5086 | 14.4374 | 14.3256 | 14.278 |  |  |  | 10.916 | 9.4458 | 9.1286 | 8.8479 | -0.035609 | 0.017904 | 12.9315 |  |  | 10.7385 |  |  | 16.9964 | 16.204 | 15.199 | 16.4938 | 15.7853 | 14.9058 | 10.3205 | 10.8125 | 11.6283 | 11.589 | 8.9743 |  | 10.8865 | 7.5578 | 10.2218 | 9.2497 | 11.2653 | 12.4718 |  | 12.5014 |  |  | 11.9048 | 12.6634 | 12.6997 | [6 empty] | 12.6104 |  |  | 11.3761 |  |  | 9.4876 | 10.4698 | 12.548 | 7.6136 | 9.3661 | 13.0126 | 7.9027 | 9.5872 | 12.933 | 9.3336 | 10.5771 | 7.8168 | 10.6662 | 8.2514 | 10.2199 | 8.182 | 9.8342 | 13.7428 | 10.8691 | 10.5099 | 11.8923 | 8.2856 | 9.9055 | 13.047 | 7.7665 | 10.4169 | 9.8399 | 9.9503 | 8.3578 | 10.2419 | -0.13637 | 20.9571 | 0.033745 | 0.049485 | -38.1066 | 3.1214 | -1.05 | 0.37 | 0.41575 | -0.36915 | 0.31993 | -0.17152 | 0.41699 | -0.28264 | 0.38663 | 0.42216 | 0.43961 | 0.42701 | 0.3816 | 0.59959 | 0.43519 | 0.42665
42810.4322 | -681 | 18.6425 | 18.6739 | 18.641 | 18.6765 | 18.0492 | 16.7181 | 14.7919 | 16.7714 | 17.2625 | 17.366 | 17.386 | 16.9607 | 16.0309 | 14.6438 | 15.1114 | 15.0647 | 15.604 | 13.466 | 13.5894 | 14.1733 |  |  |  | 16.6912 | 16.0386 | 15.1746 | 10.4488 | 9.8202 | 9.9069 | 17.3507 | 16.4585 | 15.2547 | 16.9598 | 16.2411 | 15.2668 | 10.9723 | 11.5046 |  | 12.4393 | 10.742 | 10.7733 | 8.6368 |  | 6.2188 | 6.1821 | 5.6663 | 5.7067 | 5.7207 | 5.8994 | 6.1262 | 4.1373 | 6.2678 | 4.0801 | 6.6075 | 8.2043 | 42.279 | 46.4326 | 43.0881 | 15.2758 |  |  | -0.070749 | -0.27262 | 0.00908 | 0.094626 | 0.048132 | -0.17722 | 0.39351 | -0.02842 | -0.57464 | -0.19697 | -0.2916 | 8.8913 | 8.8924 | 2.0084 | 15.9907 | 16.8407 | 17.3592 | 17.674 | 17.6467 | 16.6531 | 15.0173 | 16.9328 | 17.2549 | 17.5411 | 17.587 | 17.3436 | 16.5592 | 14.8078 | 6.3165 | 8.4787 | 5.304 | 5.8196 | 6.0441 | 6.6499 | 7.5217 | 16.0727 | 15.6642 | 15.5068 | 14.4398 | 14.327 | 14.2781 |  |  |  | 10.9147 | 9.4368 | 9.1288 | 8.8413 | 0.0036956 | -0.13077 | 12.9243 |  |  | 10.7368 |  |  | 16.9911 | 16.2042 | 15.1929 | 16.4849 | 15.7692 | 14.8982 | 10.3545 | 10.7874 | 11.6058 | 11.5655 | 9.0228 |  | 10.8799 | 7.67 | 10.215 | 9.2231 | 11.2536 | 12.4341 |  | 12.4904 |  |  | 11.903 | 12.653 | 12.6791 | [6 empty] | 12.606 |  |  | 11.3775 |  |  | 9.4793 | 10.4588 | 12.5387 | 7.6134 | 9.36 | 13.0037 | 7.8969 | 9.5795 | 12.9183 | 9.3316 | 10.5587 | 7.8158 | 10.6554 | 8.2297 | 10.214 | 8.181 | 9.8373 | 13.7377 | 10.8687 | 10.5117 | 11.8799 | 8.2752 | 9.8974 | 13.0455 | 7.7755 | 10.4202 | 9.8413 | 9.9465 | 8.3588 | 10.2365 | -0.051244 | 20.9567 | 0.033608 | 0.049434 | -38.1514 | 3.1214 | -1.12 | 0.33 | -0.31186 | -0.60814 | 0.11099 | 0.35829 | 0.2554 | -0.49008 | 0.73028 | 0.4206 | 0.43626 | 0.42736 | 0.38456 | 0.59827 | 0.43437 | 0.42679
42810.4322 | -680 | 18.6522 | 18.6714 | 18.6432 | 18.6804 | 18.0469 | 16.7153 | 14.7986 | 16.7812 | 17.2722 | 17.3647 | 17.386 | 16.9678 | 16.0256 | 14.6501 | 15.1122 | 15.0681 | 15.6045 | 13.4644 | 13.5845 | 14.1663 |  |  |  | 16.6884 | 16.0362 | 15.1696 | 10.4406 | 9.8188 | 9.8797 | 17.3564 | 16.4518 | 15.2536 | 16.9582 | 16.2496 | 15.2719 | 10.972 | 11.5041 |  | 12.4376 | 10.7603 | 10.789 | 8.6764 |  | 6.2107 | 6.181 | 5.6625 | 5.7097 | 5.701 | 5.8845 | 6.0921 | 4.1538 | 6.2725 | 4.0852 | 6.601 | 8.2102 | 42.2836 | 46.4321 | 43.1001 | 15.271 |  |  | -0.13252 | -0.047225 | 0.062304 | -0.05651 | 0.089532 | -0.39013 | 0.49142 | -0.11516 | -0.095144 | -0.9619 | -0.31723 | 8.8809 | 8.8822 | 2.0086 | 15.996 | 16.8438 | 17.3646 | 17.6782 | 17.6474 | 16.6557 | 15.009 | 16.931 | 17.2572 | 17.545 | 17.5865 | 17.3443 | 16.5604 | 14.8094 | 6.2773 | 8.4325 | 5.2652 | 5.7203 | 6.0661 | 6.6458 | 7.5144 | 16.0689 | 15.6595 | 15.5099 | 14.4429 | 14.3241 | 14.2747 |  |  |  | 10.914 | 9.4388 | 9.1258 | 8.8553 | -0.0088656 | -0.050225 | 12.9218 |  |  | 10.7451 |  |  | 16.9839 | 16.2047 | 15.1922 | 16.4924 | 15.7798 | 14.898 | 10.3835 | 10.7878 | 11.599 | 11.58 | 9.0966 |  | 10.8824 | 7.8158 | 10.2237 | 9.2311 | 11.2649 | 12.4162 |  | 12.4945 |  |  | 11.9232 | 12.6502 | 12.6702 | [6 empty] | 12.61 |  |  | 11.3879 |  |  | 9.4773 | 10.4599 | 12.5404 | 7.6195 | 9.3643 | 13.0043 | 7.8962 | 9.5796 | 12.9174 | 9.3346 | 10.5509 | 7.8187 | 10.6475 | 8.2197 | 10.2081 | 8.1853 | 9.8369 | 13.74 | 10.8748 | 10.5185 | 11.8861 | 8.2752 | 9.9079 | 13.0566 | 7.7936 | 10.4324 | 9.8462 | 9.9449 | 8.3748 | 10.235 | -0.15486 | 20.9554 | 0.033504 | 0.049144 | -38.1234 | 3.1214 | -1.26 | 0.27 | -0.42679 | -0.25311 | 0.29073 | -0.27688 | 0.34833 | -0.72711 | 0.81606 | 0.41863 | 0.4325 | 0.42751 | 0.38844 | 0.60174 | 0.43326 | 0.42637
42810.4322 | -679 | 18.6573 | 18.6782 | 18.6477 | 18.6818 | 18.0463 | 16.7246 | 14.7921 | 16.7911 | 17.2697 | 17.3702 | 17.398 | 16.964 | 16.0354 | 14.657 | 15.1063 | 15.0641 | 15.603 | 13.4642 | 13.587 | 14.1709 |  |  |  | 16.683 | 16.038 | 15.1668 | 10.4284 | 9.8079 | 9.8518 | 17.3582 | 16.4544 | 15.2543 | 16.96 | 16.2501 | 15.2656 | 10.9765 | 11.5071 |  | 12.4342 | 10.7647 | 10.7901 | 8.721 |  | 6.2216 | 6.1892 | 5.6697 | 5.7128 | 5.7064 | 5.8822 | 6.0793 | 4.2602 | 6.2778 | 4.1123 | 6.6109 | 8.2096 | 42.2911 | 46.4418 | 43.1015 | 15.2625 |  |  | -0.22057 | 0.067771 | 0.25812 | -0.01577 | -0.14309 | -0.23308 | 0.55516 | 0.1076 | -0.92531 | 0.10305 | -0.25703 | 8.8781 | 8.8791 | 2.0083 | 16.0004 | 16.84 | 17.3561 | 17.6767 | 17.6422 | 16.6492 | 15.0065 | 16.927 | 17.2565 | 17.5421 | 17.5832 | 17.3342 | 16.5586 | 14.8052 | 6.2886 | 8.4565 | 5.2145 | 5.6678 | 5.9524 | 6.6457 | 7.5215 | 16.0698 | 15.6576 | 15.5039 | 14.4416 | 14.3283 | 14.2722 |  |  |  | 10.9103 | 9.4346 | 9.1228 | 8.9183 | 0.0118 | -0.06321 | 12.9371 |  |  | 10.7469 |  |  | 17 | 16.2046 | 15.1952 | 16.4907 | 15.7746 | 14.8928 | 10.4202 | 10.7943 | 11.5926 | 11.5783 | 9.1687 |  | 10.8749 | 7.9531 | 10.2175 | 9.2289 | 11.2623 | 12.39 |  | 12.4891 |  |  | 11.9169 | 12.6466 | 12.6708 | [6 empty] | 12.611 |  |  | 11.3903 |  |  | 9.4792 | 10.4648 | 12.5285 | 7.6208 | 9.375 | 12.9928 | 7.8959 | 9.5814 | 12.9186 | 9.3386 | 10.5415 | 7.8192 | 10.6422 | 8.2127 | 10.2079 | 8.1926 | 9.8384 | 13.7435 | 10.8776 | 10.5213 | 11.8836 | 8.2659 | 9.9057 | 13.0587 | 7.8086 | 10.4415 | 9.8458 | 9.9475 | 8.373 | 10.2308 | -0.075511 | 20.9569 | 0.033481 | 0.04837 | -38.0499 | 3.1214 | -1.03 | 0.33 | -0.5506 | 0.30322 | 0.59176 | -0.14627 | -0.44035 | -0.56201 | 0.86737 | 0.41638 | 0.42848 | 0.42749 | 0.38717 | 0.6082 | 0.43217 | 0.4245
42810.4322 | -678 | 18.6528 | 18.6683 | 18.6507 | 18.6813 | 18.0459 | 16.721 | 14.7885 | 16.7787 | 17.2628 | 17.371 | 17.3918 | 16.9596 | 16.0364 | 14.6497 | 15.1176 | 15.075 | 15.6081 | 13.4682 | 13.5859 | 14.1784 |  |  |  | 16.6991 | 16.041 | 15.1746 | 10.4292 | 9.8072 | 9.8328 | 17.363 | 16.4584 | 15.2592 | 16.958 | 16.2427 | 15.2631 | 10.9761 | 11.5115 |  | 12.4317 | 10.774 | 10.7948 | 8.7599 |  | 6.2192 | 6.1804 | 5.6596 | 5.692 | 5.686 | 5.8619 | 6.0462 | 4.2682 | 6.2638 | 4.154 | 6.5988 | 8.2118 | 42.3054 | 46.4399 | 43.0903 | 15.2538 |  |  | 0.015331 | -0.066937 | 0.24696 | 0.13931 | -0.1352 | -0.020172 | 0.38431 | 0.01298 | -0.35221 | -0.89287 | -0.37804 | 8.8764 | 8.8778 | 2.0087 | 15.9886 | 16.8376 | 17.3569 | 17.6745 | 17.6407 | 16.6388 | 14.9987 | 16.9328 | 17.2554 | 17.5362 | 17.5786 | 17.3325 | 16.5574 | 14.8063 | 6.2424 | 8.4872 | 5.1729 | 5.6118 | 5.8074 | 6.6465 | 7.5245 | 16.0762 | 15.6606 | 15.5113 | 14.4555 | 14.3305 | 14.2709 |  |  |  | 10.9172 | 9.4372 | 9.1253 | 8.9799 | 0.11249 | -0.0067504 | 12.9297 |  |  | 10.7507 |  |  | 16.9997 | 16.2043 | 15.1892 | 16.4843 | 15.775 | 14.899 | 10.4522 | 10.7916 | 11.5923 | 11.5793 | 9.2421 |  | 10.8818 | 8.1272 | 10.2217 | 9.223 | 11.2675 | 12.3633 |  | 12.4921 |  |  | 11.916 | 12.6469 | 12.663 | [6 empty] | 12.6048 |  |  | 11.3917 |  |  | 9.482 | 10.4768 | 12.523 | 7.6164 | 9.383 | 12.985 | 7.8992 | 9.5821 | 12.9154 | 9.3394 | 10.5283 | 7.8392 | 10.6418 | 8.2098 | 10.2176 | 8.1912 | 9.8313 | 13.7315 | 10.8652 | 10.5048 | 11.8804 | 8.2594 | 9.8911 | 13.0493 | 7.8047 | 10.4337 | 9.8368 | 9.9378 | 8.3763 | 10.2281 | 0.020981 | 20.956 | 0.033969 | 0.04829 | -38.0069 | 3.1214 | -1.15 | 0.27 | 0.14516 | -0.30134 | 0.57881 | 0.43473 | -0.42802 | -0.16533 | 0.72164 | 0.41457 | 0.42378 | 0.42782 | 0.3924 | 0.61317 | 0.43108 | 0.42302
42810.4322 | -677 | 18.6491 | 18.6751 | 18.6505 | 18.6744 | 18.0488 | 16.7178 | 14.7957 | 16.7742 | 17.2685 | 17.3675 | 17.3898 | 16.9628 | 16.0321 | 14.6461 | 15.1267 | 15.0797 | 15.6124 | 13.4719 | 13.5921 | 14.1731 |  |  |  | 16.6937 | 16.0414 | 15.1709 | 10.4135 | 9.8108 | 9.8373 | 17.3606 | 16.4604 | 15.2661 | 16.959 | 16.2473 | 15.2645 | 10.9741 | 11.5298 |  | 12.4273 | 10.7706 | 10.7925 | 8.7836 |  | 6.2438 | 6.1888 | 5.6643 | 5.7006 | 5.6839 | 5.8689 | 6.036 | 4.253 | 6.2642 | 4.1993 | 6.6075 | 8.2075 | 42.2973 | 46.428 | 43.0962 | 15.2436 |  |  | 0.050159 | 0.086171 | 0.13524 | 0.23065 | -0.074748 | 0.18682 | 0.71222 | 0.083948 | -0.68556 | -0.673 | -0.29617 | 8.8752 | 8.8763 | 2.0083 | 15.993 | 16.8373 | 17.3581 | 17.6685 | 17.6509 | 16.6429 | 15.0091 | 16.9304 | 17.2581 | 17.5399 | 17.5775 | 17.3351 | 16.563 | 14.7935 | 6.2037 | 8.4621 | 5.2512 | 5.5336 | 5.7581 | 6.6426 | 7.5226 | 16.0726 | 15.6655 | 15.5048 | 14.4518 | 14.3305 | 14.2758 |  |  |  | 10.9065 | 9.4345 | 9.1124 | 9.002 | 0.17125 | -0.027264 | 12.927 |  |  | 10.7475 |  |  | 16.9888 | 16.1974 | 15.1888 | 16.4858 | 15.7745 | 14.892 | 10.4709 | 10.7829 | 11.5796 | 11.5597 | 9.2857 |  | 10.8786 | 8.2426 | 10.2258 | 9.2052 | 11.267 | 12.3132 |  | 12.4895 |  |  | 11.9144 | 12.6504 | 12.6666 | [6 empty] | 12.5984 |  |  | 11.3812 |  |  | 9.4783 | 10.4728 | 12.5133 | 7.6051 | 9.385 | 12.9681 | 7.8957 | 9.5746 | 12.907 | 9.3325 | 10.5166 | 7.8422 | 10.623 | 8.2108 | 10.2103 | 8.1992 | 9.8186 | 13.7256 | 10.8668 | 10.4989 | 11.8855 | 8.2639 | 9.8911 | 13.0406 | 7.8168 | 10.4307 | 9.8334 | 9.9378 | 8.3617 | 10.2133 | -0.12193 | 20.9563 | 0.03378 | 0.048529 | -38.0949 | 3.1214 | -1.11 | 0.31 | 0.26256 | 0.34191 | 0.42834 | 0.55938 | -0.31826 | 0.50315 | 0.9824 | 0.41325 | 0.42071 | 0.4283 | 0.39625 | 0.60425 | 0.43035 | 0.42205
42810.4322 | -676 | 18.6618 | 18.6829 | 18.6563 | 18.6901 | 18.0554 | 16.7313 | 14.7988 | 16.7877 | 17.2773 | 17.3752 | 17.399 | 16.969 | 16.037 | 14.6564 | 15.1246 | 15.075 | 15.6051 | 13.4683 | 13.587 | 14.1784 |  |  |  | 16.6913 | 16.0416 | 15.1711 | 10.4143 | 9.8162 | 9.8119 | 17.3529 | 16.4547 | 15.2547 | 16.9515 | 16.2393 | 15.2578 | 10.9649 | 11.5406 |  | 12.4156 | 10.76 | 10.7824 | 8.7875 |  | 6.2399 | 6.1932 | 5.6734 | 5.6985 | 5.6829 | 5.8653 | 6.0352 | 4.2079 | 6.2674 | 4.1994 | 6.6054 | 8.2158 | 42.3126 | 46.4332 | 43.1004 | 15.2413 |  |  | -0.020153 | 0.049371 | 0.22264 | 0.050598 | -0.12732 | -0.17591 | 0.69119 | -0.00082 | -0.16637 | -0.31235 | -0.44539 | 8.8753 | 8.8766 | 2.0088 | 16.0021 | 16.8413 | 17.3655 | 17.6765 | 17.6485 | 16.6488 | 15.0125 | 16.9345 | 17.258 | 17.5463 | 17.5858 | 17.3381 | 16.5636 | 14.8081 | 6.1827 | 8.4562 | 5.2739 | 5.5423 | 5.6932 | 6.6458 | 7.5238 | 16.0755 | 15.6724 | 15.5133 | 14.4495 | 14.3365 | 14.2749 |  |  |  | 10.908 | 9.4326 | 9.112 | 9.0119 | 0.11391 | 0.091678 | 12.9395 |  |  | 10.7432 |  |  | 16.9895 | 16.2014 | 15.1954 | 16.4946 | 15.77 | 14.8976 | 10.514 | 10.7786 | 11.5861 | 11.5606 | 9.3476 |  | 10.8815 | 8.2764 | 10.2284 | 9.1896 | 11.2651 | 12.2641 |  | 12.4882 |  |  | 11.9385 | 12.6488 | 12.6733 | [6 empty] | 12.6042 |  |  | 11.3765 |  |  | 9.4766 | 10.4676 | 12.4941 | 7.6021 | 9.3804 | 12.973 | 7.8992 | 9.584 | 12.9025 | 9.3397 | 10.5158 | 7.831 | 10.6213 | 8.2136 | 10.2161 | 8.2148 | 9.8426 | 13.7293 | 10.8777 | 10.5099 | 11.9006 | 8.2746 | 9.8998 | 13.053 | 7.8413 | 10.4456 | 9.8373 | 9.9486 | 8.3724 | 10.2298 | -0.19107 | 20.9556 | 0.034331 | 0.04837 | -38.0836 | 3.1214 | -0.99 | 0.38 | -0.16642 | 0.2588 | 0.54959 | 0.262 | -0.41536 | -0.48823 | 0.96779 | 0.41163 | 0.41986 | 0.42867 | 0.39895 | 0.60186 | 0.42994 | 0.42183
42810.4322 | -675 | 18.6657 | 18.6826 | 18.6499 | 18.6827 | 18.0553 | 16.7258 | 14.7939 | 16.7882 | 17.2741 | 17.3722 | 17.3947 | 16.9614 | 16.0361 | 14.6544 | 15.1264 | 15.0751 | 15.6147 | 13.4695 | 13.5932 | 14.1776 |  |  |  | 16.6866 | 16.0447 | 15.1706 | 10.399 | 9.8147 | 9.7962 | 17.3716 | 16.4593 | 15.2689 | 16.9648 | 16.249 | 15.2714 | 10.971 | 11.5515 |  | 12.4293 | 10.7725 | 10.7929 | 8.8098 |  | 6.2461 | 6.1982 | 5.6831 | 5.7027 | 5.6841 | 5.8575 | 6.0131 | 4.2529 | 6.2696 | 4.2124 | 6.6059 | 8.2105 | 42.324 | 46.426 | 43.0813 | 15.2361 |  |  | 0.022563 | -0.25225 | 0.24696 | 0.10185 | -0.041236 | -0.30273 | 0.52099 | -0.019876 | -0.42655 | -0.1934 | -0.34068 | 8.8789 | 8.8799 | 2.0084 | 15.9873 | 16.8348 | 17.3524 | 17.6663 | 17.6432 | 16.6392 | 14.9931 | 16.9249 | 17.2582 | 17.5331 | 17.5754 | 17.3331 | 16.5564 | 14.8043 | 6.1347 | 8.4588 | 5.2325 | 5.5514 | 5.6157 | 6.6438 | 7.5138 | 16.0815 | 15.6643 | 15.5078 | 14.4475 | 14.3275 | 14.2839 |  |  |  | 10.907 | 9.4237 | 9.1046 | 9.035 | 0.21744 | 0.11031 | 12.9437 |  |  | 10.741 |  |  | 16.9907 | 16.1994 | 15.1971 | 16.4883 | 15.7754 | 14.9017 | 10.525 | 10.7839 | 11.5766 | 11.56 | 9.4083 |  | 10.8857 | 8.3292 | 10.2308 | 9.1916 | 11.2638 | 12.2206 |  | 12.503 |  |  | 11.9319 | 12.656 | 12.6748 | [6 empty] | 12.6022 |  |  | 11.3842 |  |  | 9.4614 | 10.4617 | 12.4869 | 7.5677 | 9.3836 | 12.965 | 7.8999 | 9.5911 | 12.8799 | 9.3273 | 10.5118 | 7.8235 | 10.6012 | 8.1935 | 10.2083 | 8.2306 | 9.8595 | 13.7284 | 10.8849 | 10.5075 | 11.9032 | 8.2742 | 9.8941 | 13.0639 | 7.8523 | 10.4443 | 9.8444 | 9.9462 | 8.3718 | 10.2301 | -0.21457 | 20.9566 | 0.033533 | 0.047892 | -38.1164 | 3.1214 | -1.03 | 0.33 | 0.17608 | -0.58499 | 0.57883 | 0.37173 | -0.23638 | -0.64048 | 0.84022 | 0.41008 | 0.41847 | 0.42857 | 0.40405 | 0.60531 | 0.42952 | 0.42115
42810.4322 | -674 | 18.647 | 18.673 | 18.6423 | 18.6738 | 18.0457 | 16.7185 | 14.7938 | 16.7811 | 17.2702 | 17.3701 | 17.3897 | 16.956 | 16.0238 | 14.6572 | 15.1301 | 15.0729 | 15.6134 | 13.4626 | 13.5901 | 14.1745 |  |  |  | 16.6889 | 16.0375 | 15.1668 | 10.389 | 9.811 | 9.7994 | 17.371 | 16.4558 | 15.2646 | 16.9664 | 16.2589 | 15.2759 | 10.9674 | 11.5527 |  | 12.4252 | 10.7708 | 10.7961 | 8.7945 |  | 6.2517 | 6.2143 | 5.6807 | 5.6995 | 5.6801 | 5.86 | 6.0026 | 4.2996 | 6.2725 | 4.2767 | 6.6116 | 8.2126 | 42.3547 | 46.4183 | 43.0706 | 15.2249 |  |  | 0.10667 | 0.098655 | 0.2739 | 0.16231 | -0.07146 | -0.3737 | 0.58605 | -0.042876 | -0.034234 | -0.90588 | -0.27272 | 8.8799 | 8.8809 | 2.0086 | 15.9929 | 16.834 | 17.3547 | 17.6707 | 17.6467 | 16.6488 | 15.0029 | 16.9325 | 17.2622 | 17.54 | 17.58 | 17.3385 | 16.5625 | 14.8059 | 6.1327 | 8.4635 | 5.2102 | 5.5522 | 5.5717 | 6.6368 | 7.5194 | 16.0743 | 15.6608 | 15.5111 | 14.4446 | 14.3331 | 14.2775 |  |  |  | 10.9107 | 9.4126 | 9.0988 | 9.0905 | 0.056574 | 0.13139 | 12.9383 |  |  | 10.734 |  |  | 16.9909 | 16.2064 | 15.1898 | 16.4883 | 15.7774 | 14.8998 | 10.5369 | 10.7769 | 11.564 | 11.5585 | 9.3946 |  | 10.8882 | 8.3027 | 10.2297 | 9.1898 | 11.2651 | 12.1803 |  | 12.4985 |  |  | 11.9034 | 12.6743 | 12.6911 | [6 empty] | 12.6151 |  |  | 11.3944 |  |  | 9.4822 | 10.4824 | 12.5023 | 7.5583 | 9.3966 | 12.9751 | 7.9034 | 9.6009 | 12.8792 | 9.3312 | 10.5181 | 7.8317 | 10.6048 | 8.206 | 10.215 | 8.2357 | 9.8515 | 13.7133 | 10.8714 | 10.494 | 11.9009 | 8.2633 | 9.8771 | 13.055 | 7.8324 | 10.4369 | 9.8272 | 9.9353 | 8.3568 | 10.2135 | -0.19685 | 20.9561 | 0.033217 | 0.047422 | -38.1132 | 3.1214 | -1.06 | 0.39 | 0.38286 | 0.36586 | 0.6096 | 0.46927 | -0.31118 | -0.7116 | 0.89113 | 0.41054 | 0.41917 | 0.42866 | 0.40346 | 0.60843 | 0.42982 | 0.41973
42810.4322 | -673 | 18.6618 | 18.6766 | 18.6671 | 18.6891 | 18.0576 | 16.7214 | 14.7954 | 16.7847 | 17.2638 | 17.368 | 17.3943 | 16.9639 | 16.0338 | 14.6541 | 15.1336 | 15.0785 | 15.6177 | 13.4706 | 13.5885 | 14.1816 |  |  |  | 16.6981 | 16.0374 | 15.1737 | 10.392 | 9.8143 | 9.8035 | 17.3716 | 16.4666 | 15.2628 | 16.967 | 16.2497 | 15.2798 | 10.9715 | 11.5765 |  | 12.4293 | 10.7708 | 10.7974 | 8.7743 |  | 6.2509 | 6.23 | 5.6883 | 5.6999 | 5.6899 | 5.849 | 5.994 | 4.2973 | 6.2679 | 4.2583 | 6.6096 | 8.2104 | 42.3641 | 46.4213 | 43.0707 | 15.2226 |  |  | 0.031103 | -0.10374 | 0.22067 | 0.26547 | -0.020208 | 0.18616 | 0.67804 | 0.059632 | -0.3561 | -1.0083 | -0.28385 | 8.8788 | 8.8798 | 2.0085 | 16.0051 | 16.8399 | 17.3602 | 17.6756 | 17.6495 | 16.6516 | 15.0128 | 16.9296 | 17.2589 | 17.5439 | 17.5879 | 17.3393 | 16.5622 | 14.8087 | 6.1442 | 8.4681 | 5.1771 | 5.5275 | 5.5497 | 6.6364 | 7.5272 | 16.0703 | 15.6581 | 15.5105 | 14.4437 | 14.3354 | 14.2772 |  |  |  | 10.9061 | 9.4074 | 9.0887 | 9.1182 | 0.029223 | -0.075632 | 12.9461 |  |  | 10.7475 |  |  | 16.9941 | 16.2001 | 15.1973 | 16.4871 | 15.7772 | 14.9021 | 10.5493 | 10.7754 | 11.5651 | 11.5498 | 9.3581 |  | 10.8814 | 8.2367 | 10.2277 | 9.1929 | 11.2659 | 12.1534 |  | 12.495 |  |  | 11.923 | 12.6907 | 12.7083 | [6 empty] | 12.629 |  |  | 11.4041 |  |  | 9.4613 | 10.4764 | 12.4904 | 7.5488 | 9.3969 | 12.9731 | 7.9051 | 9.6069 | 12.8773 | 9.3341 | 10.5148 | 7.84 | 10.6019 | 8.2105 | 10.2156 | 8.2415 | 9.8744 | 13.721 | 10.8802 | 10.5196 | 11.9064 | 8.2679 | 9.8953 | 13.0626 | 7.8399 | 10.4432 | 9.8418 | 9.9468 | 8.3687 | 10.2162 | -0.064726 | 20.9574 | 0.033206 | 0.048059 | -38.1533 | 3.1214 | -1.03 | 0.29 | 0.20674 | -0.37517 | 0.54719 | 0.60017 | -0.16547 | 0.50224 | 0.95851 | 0.41133 | 0.42094 | 0.4286 | 0.40213 | 0.61301 | 0.43052 | 0.41881
42810.4323 | -672 | 18.6518 | 18.6806 | 18.6576 | 18.6768 | 18.0426 | 16.7252 | 14.7933 | 16.7777 | 17.2721 | 17.3659 | 17.3849 | 16.9586 | 16.0243 | 14.6514 | 15.1237 | 15.0768 | 15.6123 | 13.4692 | 13.5944 | 14.1768 |  |  |  | 16.6966 | 16.037 | 15.1712 | 10.381 | 9.8149 | 9.7918 | 17.3694 | 16.469 | 15.2672 | 16.966 | 16.2531 | 15.2769 | 10.9764 | 11.6162 |  | 12.4316 | 10.7696 | 10.8002 | 8.7728 |  | 6.2709 | 6.2384 | 5.702 | 5.7147 | 5.6986 | 5.8627 | 5.9914 | 4.2627 | 6.2677 | 4.2537 | 6.6067 | 8.2125 | 42.375 | 46.4308 | 43.0645 | 15.2193 |  |  | 0.041619 | -0.10637 | 0.17204 | 0.18859 | 0.094788 | -0.21008 | 0.62482 | -0.029076 | -0.47714 | -0.2597 | -0.17655 | 8.8885 | 8.8897 | 2.0085 | 15.9931 | 16.8377 | 17.3553 | 17.6713 | 17.6466 | 16.644 | 15.0056 | 16.9197 | 17.2464 | 17.5392 | 17.585 | 17.328 | 16.5526 | 14.8023 | 6.1477 | 8.4494 | 5.1602 | 5.4722 | 5.5568 | 6.6438 | 7.522 | 16.0735 | 15.6602 | 15.512 | 14.4507 | 14.3295 | 14.2731 |  |  |  | 10.9057 | 9.3999 | 9.0885 | 9.1471 | -0.094971 | -0.088053 | 12.9384 |  |  | 10.7334 |  |  | 16.996 | 16.2058 | 15.1959 | 16.486 | 15.7808 | 14.8976 | 10.5394 | 10.7807 | 11.571 | 11.5459 | 9.3613 |  | 10.8829 | 8.1914 | 10.2313 | 9.1998 | 11.2579 | 12.1332 |  | 12.4923 |  |  | 11.9443 | 12.6879 | 12.7098 | [6 empty] | 12.6308 |  |  | 11.4055 |  |  | 9.4565 | 10.4699 | 12.4972 | 7.5533 | 9.395 | 12.9744 | 7.8933 | 9.604 | 12.8759 | 9.3355 | 10.4945 | 7.8511 | 10.601 | 8.2218 | 10.2144 | 8.2102 | 9.8851 | 13.7265 | 10.8988 | 10.5356 | 11.9118 | 8.2722 | 9.9059 | 13.073 | 7.8479 | 10.4507 | 9.8483 | 9.9551 | 8.3654 | 10.2303 | 0.10361 | 20.9568 | 0.033252 | 0.048044 | -38.0982 | 3.1215 | -0.93 | 0.29 | 0.23915 | -0.3799 | 0.48316 | 0.50587 | 0.35839 | -0.53355 | 0.92015 | 0.41129 | 0.42232 | 0.42815 | 0.4026 | 0.61428 | 0.43072 | 0.41799
42810.4323 | -671 | 18.6613 | 18.6814 | 18.6607 | 18.6874 | 18.0559 | 16.7238 | 14.7945 | 16.782 | 17.2716 | 17.3685 | 17.3948 | 16.9621 | 16.0319 | 14.6539 | 15.1229 | 15.0755 | 15.6052 | 13.4736 | 13.5964 | 14.1794 |  |  |  | 16.6913 | 16.0316 | 15.17 | 10.3685 | 9.8118 | 9.7722 | 17.3732 | 16.4689 | 15.2737 | 16.9665 | 16.2526 | 15.2768 | 10.9711 | 11.6604 |  | 12.4284 | 10.7762 | 10.8004 | 8.7482 |  | 6.28 | 6.2456 | 5.7056 | 5.7317 | 5.7147 | 5.882 | 6.0249 | 4.3284 | 6.2712 | 4.2545 | 6.6074 | 8.2175 | 42.3651 | 46.4116 | 43.0646 | 15.2141 |  |  | 0.081043 | -0.1287 | 0.1635 | -0.036798 | -0.02612 | 0.021884 | 0.57619 | 0.01232 | -0.73557 | -0.24312 | -0.35518 | 8.8797 | 8.8805 | 2.0086 | 15.9844 | 16.8334 | 17.3548 | 17.6755 | 17.6444 | 16.6388 | 15.0013 | 16.9257 | 17.2502 | 17.5402 | 17.5764 | 17.3255 | 16.5509 | 14.7967 | 6.1183 | 8.419 | 5.1412 | 5.4793 | 5.5599 | 6.6415 | 7.5186 | 16.0696 | 15.6589 | 15.5157 | 14.4465 | 14.3322 | 14.2752 |  |  |  | 10.9119 | 9.3962 | 9.0963 | 9.164 | 0.057182 | -0.036674 | 12.9283 |  |  | 10.7339 |  |  | 16.9874 | 16.1922 | 15.1838 | 16.4828 | 15.7719 | 14.8839 | 10.551 | 10.7698 | 11.5565 | 11.5423 | 9.3103 |  | 10.8792 | 8.1555 | 10.2255 | 9.1978 | 11.255 | 12.1255 |  | 12.4847 |  |  | 11.9721 | 12.67 | 12.7136 | [6 empty] | 12.6306 |  |  | 11.4096 |  |  | 9.4527 | 10.4684 | 12.4968 | 7.5724 | 9.3933 | 12.9778 | 7.8965 | 9.6066 | 12.8679 | 9.3307 | 10.4947 | 7.8423 | 10.6084 | 8.2231 | 10.2146 | 8.1679 | 9.8845 | 13.7176 | 10.8967 | 10.529 | 11.9099 | 8.2699 | 9.9066 | 13.0734 | 7.8529 | 10.4543 | 9.8522 | 9.9563 | 8.3582 | 10.2315 | 0.011544 | 20.9578 | 0.033453 | 0.048732 | -38.1303 | 3.1214 | -0.59 | 0.37 | 0.3337 | -0.4179 | 0.47102 | -0.22345 | -0.18814 | 0.17221 | 0.88364 | 0.41259 | 0.42312 | 0.42811 | 0.4056 | 0.616 | 0.43123 | 0.41773
42810.4323 | -670 | 18.6558 | 18.6794 | 18.6619 | 18.6874 | 18.0542 | 16.722 | 14.7912 | 16.7812 | 17.2722 | 17.3682 | 17.3945 | 16.9618 | 16.0338 | 14.6551 | 15.1283 | 15.0822 | 15.6129 | 13.4745 | 13.5932 | 14.1809 |  |  |  | 16.6919 | 16.0375 | 15.1699 | 10.3718 | 9.8103 | 9.7766 | 17.3769 | 16.471 | 15.2797 | 16.9729 | 16.2521 | 15.2778 | 10.9699 | 11.7026 |  | 12.427 | 10.7785 | 10.7994 | 8.742 |  | 6.2883 | 6.2513 | 5.7192 | 5.7562 | 5.7238 | 5.8946 | 6.0505 | 4.354 | 6.2737 | 4.27 | 6.6108 | 8.2161 | 42.3444 | 46.3975 | 43.0648 | 15.2024 |  |  | 0.14215 | -0.016341 | 0.25944 | -0.095282 | 0.035648 | 0.18682 | 0.52888 | 0.032036 | -1.0432 | -0.38285 | -0.16463 | 8.8936 | 8.8947 | 2.0086 | 16.0043 | 16.8373 | 17.364 | 17.6767 | 17.6504 | 16.6465 | 15.0124 | 16.938 | 17.2602 | 17.5392 | 17.5871 | 17.3444 | 16.5607 | 14.8005 | 6.1508 | 8.3626 | 5.1303 | 5.4461 | 5.5669 | 6.637 | 7.5173 | 16.0728 | 15.6657 | 15.5131 | 14.4456 | 14.3412 | 14.2826 |  |  |  | 10.9124 | 9.4019 | 9.0884 | 9.1419 | 0.168 | -0.12155 | 12.937 |  |  | 10.7437 |  |  | 16.9923 | 16.2011 | 15.1921 | 16.4894 | 15.7789 | 14.8962 | 10.5513 | 10.7704 | 11.5583 | 11.5395 | 9.2717 |  | 10.8828 | 8.1387 | 10.236 | 9.2051 | 11.2621 | 12.1664 |  | 12.4973 |  |  | 11.9717 | 12.6591 | 12.7138 | [6 empty] | 12.6112 |  |  | 11.4077 |  |  | 9.4424 | 10.4695 | 12.4879 | 7.5804 | 9.393 | 12.9846 | 7.8937 | 9.5992 | 12.8625 | 9.3235 | 10.4928 | 7.8316 | 10.6124 | 8.2232 | 10.2171 | 8.1172 | 9.888 | 13.7143 | 10.8924 | 10.5292 | 11.9155 | 8.2644 | 9.9014 | 13.0736 | 7.8524 | 10.4561 | 9.842 | 9.9567 | 8.3649 | 10.2283 | 0.16716 | 20.9575 | 0.033791 | 0.048544 | -38.1242 | 3.1215 | -0.52 | 0.38 | 0.44196 | -0.14891 | 0.59333 | -0.35957 | 0.2198 | 0.50317 | 0.84661 | 0.41378 | 0.42394 | 0.42814 | 0.40148 | 0.61707 | 0.43136 | 0.41836
42810.4323 | -669 | 18.6585 | 18.6858 | 18.6618 | 18.6823 | 18.0568 | 16.7247 | 14.7955 | 16.7813 | 17.2754 | 17.3702 | 17.3955 | 16.9522 | 16.0339 | 14.6538 | 15.1265 | 15.0884 | 15.6187 | 13.4765 | 13.5952 | 14.1807 |  |  |  | 16.695 | 16.0393 | 15.1735 | 10.37 | 9.8039 | 9.762 | 17.3761 | 16.462 | 15.2778 | 16.9679 | 16.2518 | 15.2721 | 10.9671 | 11.7275 |  | 12.4249 | 10.7822 | 10.7998 | 8.7463 |  | 6.2913 | 6.2548 | 5.7203 | 5.7552 | 5.7371 | 5.9056 | 6.0335 | 4.3427 | 6.2688 | 4.3265 | 6.6052 | 8.2202 | 42.331 | 46.3892 | 43.0634 | 15.2022 |  |  | 0.083015 | -0.013713 | 0.037992 | 0.091998 | 0.12173 | -0.32245 | 0.36723 | -0.11122 | -0.4425 | -0.66964 | -0.1994 | 8.8829 | 8.8844 | 2.0086 | 15.986 | 16.8325 | 17.3532 | 17.6671 | 17.6409 | 16.6412 | 15.0053 | 16.9262 | 17.2465 | 17.5295 | 17.5749 | 17.3299 | 16.5529 | 14.7949 | 6.1331 | 8.3737 | 5.0861 | 5.3946 | 5.5982 | 6.6254 | 7.5031 | 16.0705 | 15.6618 | 15.5138 | 14.4451 | 14.3327 | 14.2749 |  |  |  | 10.9158 | 9.3998 | 9.0897 | 9.107 | 0.095271 | 0.061378 | 12.9324 |  |  | 10.738 |  |  | 16.9905 | 16.2021 | 15.1892 | 16.4831 | 15.783 | 14.8948 | 10.5555 | 10.7676 | 11.5451 | 11.5362 | 9.2589 |  | 10.8732 | 8.1344 | 10.2336 | 9.1816 | 11.2641 | 12.1909 |  | 12.4885 |  |  | 11.966 | 12.6403 | 12.7256 | [6 empty] | 12.6046 |  |  | 11.4088 |  |  | 9.4338 | 10.4685 | 12.4831 | 7.5957 | 9.4016 | 12.9873 | 7.9078 | 9.6058 | 12.8664 | 9.3313 | 10.494 | 7.837 | 10.6156 | 8.2249 | 10.2255 | 8.0798 | 9.8963 | 13.7089 | 10.8808 | 10.532 | 11.9158 | 8.2641 | 9.9012 | 13.0768 | 7.8413 | 10.4594 | 9.8437 | 9.96 | 8.3666 | 10.2378 | -0.092075 | 20.9571 | 0.034073 | 0.049195 | -38.0375 | 3.1215 | -0.64 | 0.34 | 0.33773 | -0.13641 | 0.22705 | 0.35332 | 0.40618 | -0.66106 | 0.70547 | 0.41382 | 0.42397 | 0.42886 | 0.4021 | 0.62032 | 0.43115 | 0.41944
42810.4323 | -668 | 18.6649 | 18.6895 | 18.6646 | 18.6894 | 18.0623 | 16.7257 | 14.7972 | 16.7896 | 17.2808 | 17.369 | 17.3966 | 16.967 | 16.0369 | 14.6513 | 15.1237 | 15.083 | 15.6185 | 13.4733 | 13.596 | 14.1812 |  |  |  | 16.6936 | 16.035 | 15.1744 | 10.3602 | 9.7989 | 9.7498 | 17.3778 | 16.4692 | 15.2749 | 16.9648 | 16.2534 | 15.282 | 10.9667 | 11.7659 |  | 12.421 | 10.794 | 10.7928 | 8.7573 |  | 6.2883 | 6.255 | 5.7043 | 5.7531 | 5.758 | 5.9103 | 6.0256 | 4.358 | 6.2689 | 4.3978 | 6.5982 | 8.2209 | 42.314 | 46.3972 | 43.0614 | 15.1987 |  |  | 0.023875 | -0.3357 | 0.18847 | 0.15639 | -0.07672 | 0.013996 | 0.452 | -0.06916 | -0.22397 | -2.0988 | -0.31465 | 8.8838 | 8.885 | 2.0084 | 15.9909 | 16.842 | 17.3599 | 17.6761 | 17.648 | 16.6442 | 14.9998 | 16.9291 | 17.2553 | 17.5394 | 17.5833 | 17.3311 | 16.5611 | 14.8026 | 6.1364 | 8.343 | 5.0787 | 5.3607 | 5.6785 | 6.6294 | 7.5077 | 16.0699 | 15.6567 | 15.5069 | 14.4418 | 14.3296 | 14.2695 |  |  |  | 10.9059 | 9.3951 | 9.0892 | 9.1008 | 0.047255 | 0.048957 | 12.9487 |  |  | 10.7363 |  |  | 16.9928 | 16.2033 | 15.1915 | 16.4888 | 15.7822 | 14.8956 | 10.5523 | 10.7645 | 11.5424 | 11.5251 | 9.2575 |  | 10.8757 | 8.1263 | 10.2319 | 9.1677 | 11.2554 | 12.2289 |  | 12.4934 |  |  | 11.9661 | 12.6346 | 12.7452 | [6 empty] | 12.6244 |  |  | 11.4049 |  |  | 9.4292 | 10.4652 | 12.4715 | 7.5958 | 9.4028 | 12.9797 | 7.9146 | 9.6053 | 12.8626 | 9.3275 | 10.4903 | 7.8423 | 10.6166 | 8.2276 | 10.2186 | 8.0573 | 9.9019 | 13.7076 | 10.8785 | 10.541 | 11.9048 | 8.2592 | 9.8965 | 13.0794 | 7.8297 | 10.4691 | 9.8477 | 9.9583 | 8.3654 | 10.2422 | -0.093231 | 20.9573 | 0.033918 | 0.049825 | -38.1403 | 3.1215 | -0.71 | 0.38 | 0.18112 | -0.67493 | 0.50572 | 0.46067 | -0.32246 | 0.13773 | 0.78268 | 0.41394 | 0.42414 | 0.42896 | 0.40219 | 0.62168 | 0.43084 | 0.41929
42810.4323 | -667 | 18.6599 | 18.6772 | 18.6594 | 18.69 | 18.0581 | 16.7282 | 14.8058 | 16.7855 | 17.2794 | 17.3701 | 17.3956 | 16.9722 | 16.0379 | 14.6495 | 15.1239 | 15.08 | 15.6136 | 13.4687 | 13.5955 | 14.1819 |  |  |  | 16.6927 | 16.0313 | 15.1658 | 10.3516 | 9.7962 | 9.745 | 17.3709 | 16.464 | 15.2616 | 16.9575 | 16.2445 | 15.2779 | 10.961 | 11.7899 |  | 12.4119 | 10.7934 | 10.7719 | 8.7488 |  | 6.2862 | 6.2507 | 5.71 | 5.7519 | 5.7645 | 5.911 | 6.0533 | 4.4417 | 6.2623 | 4.4505 | 6.6095 | 8.2335 | 42.3116 | 46.4266 | 43.0697 | 15.2015 |  |  | 0.031759 | -0.13725 | 0.24367 | 0.004598 | -0.04912 | -0.50972 | 0.41651 | -0.083616 | -0.38996 | -0.25214 | -0.26736 | 8.8796 | 8.8808 | 2.0084 | 15.9983 | 16.8398 | 17.3652 | 17.6861 | 17.6466 | 16.6493 | 15.0087 | 16.9281 | 17.2579 | 17.5451 | 17.5882 | 17.3351 | 16.5591 | 14.8045 | 6.1447 | 8.355 | 5.1068 | 5.336 | 5.7092 | 6.6278 | 7.5032 | 16.0603 | 15.6551 | 15.5037 | 14.4413 | 14.3279 | 14.268 |  |  |  | 10.8983 | 9.3894 | 9.0875 | 9.1094 | 0.049078 | 0.07681 | 12.9514 |  |  | 10.739 |  |  | 16.9924 | 16.2075 | 15.1907 | 16.4873 | 15.7764 | 14.8964 | 10.5574 | 10.7751 | 11.5428 | 11.5292 | 9.2701 |  | 10.8787 | 8.1149 | 10.2344 | 9.1648 | 11.2622 | 12.2374 |  | 12.4855 |  |  | 11.964 | 12.6398 | 12.758 | [6 empty] | 12.6405 |  |  | 11.3987 |  |  | 9.4323 | 10.4676 | 12.4647 | 7.6038 | 9.404 | 12.9794 | 7.9104 | 9.6056 | 12.8647 | 9.3226 | 10.486 | 7.8495 | 10.622 | 8.2337 | 10.2103 | 8.0486 | 9.9163 | 13.7113 | 10.8701 | 10.5427 | 11.8932 | 8.2586 | 9.8966 | 13.0768 | 7.825 | 10.4693 | 9.8441 | 9.9599 | 8.3739 | 10.2352 | 0.16466 | 20.9576 | 0.033843 | 0.050693 | -38.1618 | 3.1215 | -0.87 | 0.32 | 0.20889 | -0.43155 | 0.57502 | 0.078989 | -0.25802 | -0.83116 | 0.75133 | 0.41369 | 0.42454 | 0.42926 | 0.40108 | 0.61804 | 0.43088 | 0.4188
42810.4323 | -666 | 18.6665 | 18.6769 | 18.662 | 18.6877 | 18.0584 | 16.7214 | 14.7993 | 16.7884 | 17.2759 | 17.3715 | 17.3967 | 16.9573 | 16.0294 | 14.6556 | 15.1335 | 15.0886 | 15.6225 | 13.4734 | 13.5998 | 14.1851 |  |  |  | 16.6939 | 16.0386 | 15.1694 | 10.3486 | 9.7994 | 9.7586 | 17.3874 | 16.4755 | 15.2777 | 16.9728 | 16.259 | 15.2945 | 10.9769 | 11.8419 |  | 12.43 | 10.7984 | 10.7795 | 8.76 |  | 6.283 | 6.2426 | 5.7033 | 5.7501 | 5.7594 | 5.906 | 6.0479 | 4.5132 | 6.2687 | 4.4956 | 6.6075 | 8.2337 | 42.297 | 46.4365 | 43.0689 | 15.1972 |  |  | 0.004163 | 0.048715 | 0.10633 | -0.36864 | 0.061932 | -0.1884 | 0.64256 | -0.050104 | -0.12083 | -0.44852 | -0.31982 | 8.8778 | 8.8789 | 2.0086 | 15.9936 | 16.8348 | 17.3649 | 17.6836 | 17.6461 | 16.6482 | 15.0081 | 16.9283 | 17.258 | 17.5423 | 17.5886 | 17.3334 | 16.5621 | 14.7981 | 6.1215 | 8.375 | 5.1371 | 5.3491 | 5.6626 | 6.6262 | 7.5026 | 16.0651 | 15.6638 | 15.5081 | 14.4358 | 14.3334 | 14.2736 |  |  |  | 10.8968 | 9.3785 | 9.0845 | 9.1031 | 0.077847 | 0.061943 | 12.9288 |  |  | 10.7315 |  |  | 16.9876 | 16.1981 | 15.1826 | 16.486 | 15.768 | 14.8924 | 10.5528 | 10.7594 | 11.536 | 11.5217 | 9.3117 |  | 10.8729 | 8.123 | 10.2311 | 9.1713 | 11.259 | 12.2372 |  | 12.4899 |  |  | 11.953 | 12.6389 | 12.7559 | [6 empty] | 12.6356 |  |  | 11.382 |  |  | 9.4368 | 10.4685 | 12.4588 | 7.6177 | 9.4072 | 12.9821 | 7.9097 | 9.6094 | 12.8703 | 9.318 | 10.4804 | 7.853 | 10.6255 | 8.2482 | 10.2142 | 8.055 | 9.9223 | 13.7084 | 10.8651 | 10.5486 | 11.8779 | 8.2592 | 9.8882 | 13.0739 | 7.8237 | 10.4476 | 9.8453 | 9.9638 | 8.3669 | 10.238 | 0.022907 | 20.957 | 0.034038 | 0.049948 | -38.0855 | 3.1215 | -1.19 | 0.34 | 0.07563 | 0.2571 | 0.37984 | -0.70726 | 0.28971 | -0.5053 | 0.93319 | 0.41234 | 0.42421 | 0.42897 | 0.40347 | 0.61461 | 0.4311 | 0.41892
42810.4323 | -665 | 18.6704 | 18.6862 | 18.6615 | 18.695 | 18.0526 | 16.7207 | 14.8057 | 16.7823 | 17.282 | 17.3759 | 17.4048 | 16.965 | 16.0365 | 14.6592 | 15.1368 | 15.0916 | 15.6246 | 13.4751 | 13.5982 | 14.1855 |  |  |  | 16.6948 | 16.0458 | 15.176 | 10.3519 | 9.8043 | 9.7566 | 17.3795 | 16.473 | 15.2785 | 16.9645 | 16.2497 | 15.273 | 10.9599 | 11.8784 |  | 12.42 | 10.7897 | 10.7597 | 8.7117 |  | 6.2803 | 6.2353 | 5.6968 | 5.7492 | 5.7588 | 5.8992 | 6.0332 | 4.5257 | 6.2636 | 4.5182 | 6.6005 | 8.2226 | 42.2772 | 46.4311 | 43.0598 | 15.1912 |  |  | 0.031759 | -0.26145 | 0.014992 | 0.044686 | 0.049448 | 0.31824 | 0.31729 | -0.008048 | -0.57269 | 0.0057018 | -0.25107 | 8.8771 | 8.8784 | 2.0085 | 15.9982 | 16.8414 | 17.363 | 17.6785 | 17.6454 | 16.6502 | 15.0081 | 16.931 | 17.257 | 17.5441 | 17.5858 | 17.3315 | 16.5587 | 14.7971 | 6.1144 | 8.3738 | 5.1478 | 5.348 | 5.6192 | 6.6263 | 7.5074 | 16.0808 | 15.6725 | 15.5185 | 14.4503 | 14.3348 | 14.2824 |  |  |  | 10.9026 | 9.3856 | 9.0866 | 9.0914 | -0.042295 | 0.0005894 | 12.9488 |  |  | 10.7384 |  |  | 16.9975 | 16.209 | 15.1965 | 16.4919 | 15.7781 | 14.8994 | 10.5611 | 10.7735 | 11.534 | 11.5333 | 9.332 |  | 10.8727 | 8.2144 | 10.231 | 9.1636 | 11.2541 | 12.237 |  | 12.4853 |  |  | 11.9468 | 12.6327 | 12.7502 | [6 empty] | 12.6254 |  |  | 11.364 |  |  | 9.426 | 10.4765 | 12.4474 | 7.6246 | 9.396 | 12.9684 | 7.9026 | 9.6036 | 12.8677 | 9.3068 | 10.4758 | 7.8424 | 10.621 | 8.2432 | 10.211 | 8.0718 | 9.9304 | 13.7019 | 10.8728 | 10.552 | 11.8711 | 8.2586 | 9.886 | 13.0781 | 7.8341 | 10.4477 | 9.8449 | 9.9596 | 8.3665 | 10.2485 | -0.16623 | 20.9577 | 0.034159 | 0.050208 | -38.07 | 3.1215 | -1.1 | 0.38 | 0.20889 | -0.59561 | 0.14263 | 0.24624 | 0.25887 | 0.65673 | 0.65574 | 0.41177 | 0.42167 | 0.42903 | 0.40427 | 0.61397 | 0.43188 | 0.41944
42810.4323 | -664 | 18.6703 | 18.6774 | 18.6552 | 18.6848 | 18.0578 | 16.7212 | 14.7932 | 16.7723 | 17.2727 | 17.3631 | 17.3883 | 16.9587 | 16.0279 | 14.6512 | 15.146 | 15.0948 | 15.6272 | 13.4802 | 13.6065 | 14.1968 |  |  |  | 16.7058 | 16.0515 | 15.1734 | 10.3495 | 9.8028 | 9.7649 | 17.3924 | 16.4808 | 15.2832 | 16.9801 | 16.2529 | 15.2894 | 10.9738 | 11.9345 |  | 12.4289 | 10.7985 | 10.7709 | 8.6903 |  | 6.2895 | 6.234 | 5.7009 | 5.7558 | 5.7723 | 5.8989 | 6.0307 | 4.5137 | 6.2707 | 4.52 | 6.6081 | 8.2326 | 42.2793 | 46.4284 | 43.067 | 15.1865 |  |  | 0.026503 | -0.27262 | 0.023536 | -0.025626 | 0.05602 | 0.043568 | 0.30743 | -0.035648 | 0.11055 | -0.13465 | -0.3067 | 8.8758 | 8.877 | 2.0086 | 15.9979 | 16.838 | 17.3572 | 17.666 | 17.6456 | 16.6386 | 15.0014 | 16.9313 | 17.2496 | 17.5422 | 17.5787 | 17.3301 | 16.5515 | 14.7895 | 6.1464 | 8.4174 | 5.153 | 5.391 | 5.5787 | 6.6265 | 7.5134 | 16.0722 | 15.6726 | 15.5128 | 14.4561 | 14.3353 | 14.2792 |  |  |  | 10.9067 | 9.3859 | 9.0882 | 9.0655 | 0.14592 | 0.10241 | 12.9454 |  |  | 10.7396 |  |  | 16.995 | 16.1953 | 15.1828 | 16.4853 | 15.7733 | 14.8847 | 10.5657 | 10.7704 | 11.5349 | 11.5262 | 9.3167 |  | 10.871 | 8.3611 | 10.2312 | 9.2007 | 11.2541 | 12.2407 |  | 12.4879 |  |  | 11.9349 | 12.6232 | 12.7309 | [6 empty] | 12.6177 |  |  | 11.3473 |  |  | 9.4281 | 10.4868 | 12.4398 | 7.6289 | 9.394 | 12.9746 | 7.9074 | 9.6103 | 12.869 | 9.3049 | 10.4667 | 7.8427 | 10.627 | 8.2444 | 10.212 | 8.0692 | 9.9349 | 13.7088 | 10.874 | 10.549 | 11.8607 | 8.2544 | 9.8806 | 13.0746 | 7.8441 | 10.4428 | 9.8364 | 9.955 | 8.3682 | 10.2457 | 0.061042 | 20.9569 | 0.033522 | 0.050751 | -38.1054 | 3.1214 | -0.73 | 0.27 | 0.19083 | -0.6082 | 0.1787 | -0.18647 | 0.27554 | 0.24299 | 0.64548 | 0.41214 | 0.4176 | 0.428 | 0.40075 | 0.6141 | 0.43293 | 0.42029
42810.4324 | -663 | 18.6703 | 18.6802 | 18.6684 | 18.6844 | 18.0556 | 16.719 | 14.796 | 16.7819 | 17.2711 | 17.3668 | 17.3933 | 16.9583 | 16.033 | 14.6526 | 15.1468 | 15.0972 | 15.6296 | 13.4839 | 13.6127 | 14.1926 |  |  |  | 16.6979 | 16.0508 | 15.1744 | 10.3471 | 9.7932 | 9.76 | 17.389 | 16.4785 | 15.2832 | 16.9771 | 16.2511 | 15.2815 | 10.9714 | 11.9799 |  | 12.4257 | 10.8043 | 10.7509 | 8.6792 |  | 6.2913 | 6.2413 | 5.6978 | 5.7511 | 5.7739 | 5.8942 | 6.0321 | 4.5377 | 6.2754 | 4.5253 | 6.6161 | 8.2265 | 42.2953 | 46.4326 | 43.0651 | 15.1841 |  |  | 0.14873 | -0.11491 | 0.078076 | 0.11368 | 0.073104 | -0.055 | 0.31729 | -0.036304 | -0.61375 | -0.43865 | -0.3381 | 8.8744 | 8.8757 | 2.0085 | 15.994 | 16.8393 | 17.3594 | 17.6766 | 17.6446 | 16.6431 | 15.0078 | 16.9337 | 17.2544 | 17.5457 | 17.5767 | 17.3313 | 16.555 | 14.809 | 6.1545 | 8.4574 | 5.1778 | 5.437 | 5.5653 | 6.625 | 7.5118 | 16.0758 | 15.6699 | 15.5137 | 14.4524 | 14.3338 | 14.2817 |  |  |  | 10.9071 | 9.3798 | 9.085 | 9.0277 | 0.17003 | 0.25297 | 12.9369 |  |  | 10.7412 |  |  | 16.995 | 16.1961 | 15.1798 | 16.4869 | 15.7736 | 14.8928 | 10.5595 | 10.7669 | 11.5275 | 11.5181 | 9.3402 |  | 10.8797 | 8.522 | 10.2375 | 9.2464 | 11.2577 | 12.2504 |  | 12.4927 |  |  | 11.8831 | 12.6174 | 12.6807 | [6 empty] | 12.604 |  |  | 11.3402 |  |  | 9.4414 | 10.4872 | 12.4627 | 7.6415 | 9.4105 | 12.9901 | 7.9188 | 9.6242 | 12.8919 | 9.3135 | 10.4836 | 7.8607 | 10.635 | 8.2675 | 10.2271 | 8.0805 | 9.9432 | 13.7238 | 10.8947 | 10.5568 | 11.8522 | 8.259 | 9.8831 | 13.09 | 7.845 | 10.4392 | 9.839 | 9.9495 | 8.3651 | 10.2557 | -0.18722 | 20.9564 | 0.033941 | 0.050266 | -38.0487 | 3.1215 | -0.97 | 0.26 | 0.45205 | -0.39487 | 0.32549 | 0.39275 | 0.31476 | -0.27301 | 0.65574 | 0.41177 | 0.41334 | 0.42685 | 0.39968 | 0.61115 | 0.43316 | 0.42136
42810.4324 | -662 | 18.6701 | 18.6799 | 18.6717 | 18.6846 | 18.0615 | 16.7275 | 14.7928 | 16.7799 | 17.2709 | 17.3696 | 17.398 | 16.9633 | 16.0302 | 14.6517 | 15.1419 | 15.0872 | 15.6227 | 13.4793 | 13.6044 | 14.1886 |  |  |  | 16.6971 | 16.038 | 15.1718 | 10.34 | 9.795 | 9.7707 | 17.3931 | 16.4747 | 15.2754 | 16.9745 | 16.2614 | 15.2862 | 10.97 | 12.025 |  | 12.43 | 10.8029 | 10.7421 | 8.6697 |  | 6.2925 | 6.2387 | 5.6876 | 5.743 | 5.7629 | 5.8895 | 6.0425 | 4.5542 | 6.278 | 4.5341 | 6.6195 | 8.2365 | 42.3009 | 46.4302 | 43.0656 | 15.1782 |  |  | 0.057387 | -0.084681 | 0.12473 | -0.31739 | 0.13487 | 0.065908 | 0.4842 | -0.1191 | -0.5221 | -0.47327 | -0.35459 | 8.8761 | 8.8773 | 2.0083 | 15.9891 | 16.8391 | 17.3575 | 17.6697 | 17.6492 | 16.6447 | 15.002 | 16.9298 | 17.2589 | 17.5447 | 17.5789 | 17.3413 | 16.557 | 14.8021 | 6.186 | 8.4785 | 5.1938 | 5.4592 | 5.5576 | 6.6257 | 7.5148 | 16.0822 | 15.6721 | 15.52 | 14.4611 | 14.3356 | 14.2844 |  |  |  | 10.9093 | 9.3788 | 9.0812 | 9.0171 | 0.16132 | 0.28647 | 12.9358 |  |  | 10.7358 |  |  | 16.984 | 16.1859 | 15.1825 | 16.4859 | 15.7637 | 14.891 | 10.5547 | 10.7548 | 11.5243 | 11.5119 | 9.3807 |  | 10.8785 | 8.646 | 10.247 | 9.246 | 11.2537 | 12.282 |  | 12.4946 |  |  | 11.8644 | 12.6449 | 12.6488 | [6 empty] | 12.6134 |  |  | 11.3476 |  |  | 9.4387 | 10.4877 | 12.4673 | 7.654 | 9.4057 | 12.9855 | 7.9298 | 9.6252 | 12.8902 | 9.3107 | 10.4803 | 7.8725 | 10.6313 | 8.2659 | 10.2298 | 8.1067 | 9.9459 | 13.73 | 10.8941 | 10.5612 | 11.8299 | 8.2484 | 9.8893 | 13.0901 | 7.8549 | 10.4389 | 9.8354 | 9.9526 | 8.3732 | 10.2516 | -0.014457 | 20.9578 | 0.033941 | 0.049528 | -38.0508 | 3.1215 | -1.03 | 0.28 | 0.28081 | -0.33897 | 0.4114 | -0.65624 | 0.42752 | 0.29886 | 0.81005 | 0.41061 | 0.41021 | 0.42673 | 0.39624 | 0.60972 | 0.43338 | 0.42173
42810.4324 | -661 | 18.6821 | 18.6847 | 18.6707 | 18.6917 | 18.0688 | 16.7288 | 14.7983 | 16.7901 | 17.2799 | 17.376 | 17.399 | 16.9683 | 16.0307 | 14.6608 | 15.1468 | 15.0878 | 15.6189 | 13.4906 | 13.594 | 14.1875 |  |  |  | 16.6938 | 16.0414 | 15.174 | 10.3497 | 9.7949 | 9.7751 | 17.3998 | 16.4771 | 15.2748 | 16.9704 | 16.2592 | 15.281 | 10.9656 | 12.0652 |  | 12.427 | 10.7977 | 10.7315 | 8.6663 |  | 6.2981 | 6.2476 | 5.6906 | 5.7446 | 5.7554 | 5.8755 | 6.0418 | 4.5779 | 6.2856 | 4.5552 | 6.6222 | 8.2294 | 42.301 | 46.4285 | 43.0597 | 15.1649 |  |  | -0.053009 | -0.11294 | -0.036264 | 0.27665 | 0.11319 | 0.036996 | 0.47828 | -0.2341 | 0.32539 | -0.12228 | -0.21451 | 8.8779 | 8.879 | 2.0087 | 15.9887 | 16.8354 | 17.3597 | 17.6708 | 17.6427 | 16.6465 | 14.9987 | 16.9285 | 17.2527 | 17.538 | 17.5721 | 17.3354 | 16.5558 | 14.792 | 6.2135 | 8.4953 | 5.2079 | 5.4682 | 5.5477 | 6.628 | 7.5201 | 16.0806 | 15.6715 | 15.5121 | 14.4586 | 14.3473 | 14.2797 |  |  |  | 10.9059 | 9.3637 | 9.081 | 8.9827 | 0.1206 | 0.19651 | 12.9458 |  |  | 10.7458 |  |  | 16.9943 | 16.2049 | 15.1949 | 16.4873 | 15.7726 | 14.893 | 10.5516 | 10.7716 | 11.5336 | 11.5292 | 9.4014 |  | 10.8684 | 8.7902 | 10.2402 | 9.23 | 11.2591 | 12.3021 |  | 12.4993 |  |  | 11.8314 | 12.652 | 12.6434 | [6 empty] | 12.6041 |  |  | 11.3451 |  |  | 9.4383 | 10.483 | 12.4599 | 7.6585 | 9.3977 | 12.982 | 7.9328 | 9.625 | 12.8877 | 9.3034 | 10.4737 | 7.8782 | 10.6115 | 8.2517 | 10.2193 | 8.1044 | 9.9583 | 13.7457 | 10.9058 | 10.5702 | 11.8305 | 8.2423 | 9.9004 | 13.1012 | 7.8512 | 10.4335 | 9.8502 | 9.9612 | 8.3782 | 10.2673 | 0.072598 | 20.9591 | 0.03374 | 0.048327 | -38.1635 | 3.1215 | -1.11 | 0.42 | -0.26988 | -0.39147 | -0.22183 | 0.61269 | 0.39164 | 0.22391 | 0.80506 | 0.4097 | 0.40598 | 0.42735 | 0.39347 | 0.60877 | 0.43333 | 0.42257
42810.4324 | -660 | 18.6813 | 18.686 | 18.6682 | 18.6942 | 18.0607 | 16.722 | 14.8072 | 16.7867 | 17.277 | 17.373 | 17.3942 | 16.9625 | 16.0378 | 14.6603 | 15.1506 | 15.0969 | 15.6301 | 13.4871 | 13.6057 | 14.1964 |  |  |  | 16.708 | 16.0413 | 15.176 | 10.3399 | 9.797 | 9.7779 | 17.392 | 16.4704 | 15.2697 | 16.9646 | 16.2473 | 15.2738 | 10.9625 | 12.0914 |  | 12.4148 | 10.7755 | 10.7111 | 8.6886 |  | 6.2972 | 6.2452 | 5.6805 | 5.7273 | 5.7385 | 5.867 | 6.0446 | 4.5587 | 6.277 | 4.552 | 6.6191 | 8.2268 | 42.2989 | 46.4387 | 43.0564 | 15.1622 |  |  | -0.074033 | -0.23187 | 0.10042 | -0.071626 | -0.00378 | -0.01886 | 0.52756 | -0.15393 | 0.31507 | -0.41663 | -0.26478 | 8.8761 | 8.877 | 2.0084 | 15.9961 | 16.8384 | 17.3641 | 17.6785 | 17.6476 | 16.6425 | 15.0041 | 16.9283 | 17.253 | 17.5375 | 17.5825 | 17.3269 | 16.5533 | 14.799 | 6.2182 | 8.4751 | 5.222 | 5.5522 | 5.559 | 6.6272 | 7.5203 | 16.0751 | 15.6659 | 15.5198 | 14.4517 | 14.3333 | 14.2781 |  |  |  | 10.9035 | 9.361 | 9.0814 | 8.9498 | 0.13397 | 0.1519 | 12.9425 |  |  | 10.7498 |  |  | 16.9998 | 16.1984 | 15.1927 | 16.4859 | 15.779 | 14.8977 | 10.5425 | 10.7767 | 11.5348 | 11.529 | 9.4332 |  | 10.8701 | 8.868 | 10.2336 | 9.226 | 11.269 | 12.3123 |  | 12.4945 |  |  | 11.8145 | 12.6829 | 12.6141 | [6 empty] | 12.61 |  |  | 11.3556 |  |  | 9.4329 | 10.4901 | 12.4584 | 7.6441 | 9.3925 | 12.9728 | 7.9364 | 9.6281 | 12.8992 | 9.2996 | 10.476 | 7.8774 | 10.5827 | 8.2466 | 10.2179 | 8.1279 | 9.9528 | 13.7524 | 10.8921 | 10.5744 | 11.8317 | 8.2213 | 9.9005 | 13.1007 | 7.8589 | 10.4347 | 9.8498 | 9.9626 | 8.3705 | 10.2609 | 0.036389 | 20.9587 | 0.033877 | 0.049007 | -38.106 | 3.1215 | -1.27 | 0.33 | -0.31895 | -0.56092 | 0.36913 | -0.31175 | -0.07157 | -0.15986 | 0.84551 | 0.40887 | 0.4036 | 0.42779 | 0.39285 | 0.60723 | 0.43261 | 0.4234
42810.4324 | -659 | 18.6863 | 18.6987 | 18.6779 | 18.6947 | 18.0638 | 16.7334 | 14.8057 | 16.7885 | 17.2808 | 17.375 | 17.4004 | 16.9666 | 16.0417 | 14.6579 | 15.1472 | 15.0828 | 15.628 | 13.477 | 13.6032 | 14.1803 |  |  |  | 16.6885 | 16.0445 | 15.1655 | 10.3332 | 9.788 | 9.7717 | 17.3968 | 16.4798 | 15.2818 | 16.9822 | 16.261 | 15.2845 | 10.975 | 12.127 |  | 12.4263 | 10.775 | 10.7129 | 8.7446 |  | 6.3035 | 6.2541 | 5.6863 | 5.7276 | 5.7426 | 5.8632 | 6.1232 | 4.5816 | 6.2803 | 4.556 | 6.6247 | 8.2299 | 42.2961 | 46.4506 | 43.0439 | 15.1561 |  |  | 0.084331 | -0.10702 | 0.12408 | 0.021026 | -0.18843 | -0.029372 | 0.50785 | -0.12764 | -0.57211 | 0.62419 | -0.34207 | 8.8745 | 8.8755 | 2.0085 | 15.9936 | 16.8433 | 17.363 | 17.6826 | 17.6442 | 16.6423 | 15.0017 | 16.9251 | 17.2615 | 17.5354 | 17.5788 | 17.3285 | 16.552 | 14.7952 | 6.2042 | 8.4754 | 5.2253 | 5.5822 | 5.6452 | 6.6212 | 7.5122 | 16.0805 | 15.6718 | 15.5205 | 14.4543 | 14.3368 | 14.2821 |  |  |  | 10.9104 | 9.3501 | 9.087 | 8.9369 | 0.035909 | 0.016775 | 12.9439 |  |  | 10.7467 |  |  | 16.9898 | 16.1964 | 15.1883 | 16.4884 | 15.7762 | 14.8969 | 10.5477 | 10.7742 | 11.5397 | 11.5149 | 9.439 |  | 10.877 | 8.8053 | 10.2389 | 9.2155 | 11.2703 | 12.3055 |  | 12.489 |  |  | 11.7855 | 12.6714 | 12.5748 | [6 empty] | 12.5991 |  |  | 11.3439 |  |  | 9.443 | 10.4994 | 12.4669 | 7.6415 | 9.4108 | 12.9837 | 7.9392 | 9.6375 | 12.9097 | 9.3098 | 10.4733 | 7.8676 | 10.5562 | 8.2648 | 10.226 | 8.1267 | 9.9571 | 13.7584 | 10.9009 | 10.5839 | 11.8382 | 8.2233 | 9.9115 | 13.1148 | 7.8713 | 10.4302 | 9.8441 | 9.9642 | 8.373 | 10.273 | -0.0011678 | 20.9605 | 0.034394 | 0.049115 | -38.0656 | 3.1215 | -1.56 | 0.39 | 0.3404 | -0.38108 | 0.41032 | 0.16891 | -0.5053 | -0.1995 | 0.82956 | 0.40894 | 0.40551 | 0.42812 | 0.3937 | 0.60592 | 0.43146 | 0.42399
42810.4324 | -658 | 18.6736 | 18.6866 | 18.6634 | 18.6952 | 18.0544 | 16.7228 | 14.7949 | 16.7796 | 17.2714 | 17.3664 | 17.3917 | 16.9549 | 16.0368 | 14.6475 | 15.1454 | 15.0959 | 15.6271 | 13.4735 | 13.6001 | 14.1824 |  |  |  | 16.6954 | 16.0389 | 15.171 | 10.3304 | 9.7747 | 9.7872 | 17.3903 | 16.4875 | 15.2789 | 16.9797 | 16.2603 | 15.2902 | 10.9709 | 12.1588 |  | 12.4218 | 10.7634 | 10.6988 | 8.7868 |  | 6.3016 | 6.2414 | 5.6837 | 5.7292 | 5.734 | 5.8538 | 6.1347 | 4.6353 | 6.2828 | 4.5635 | 6.6282 | 8.2312 | 42.293 | 46.4421 | 43.0345 | 15.1513 |  |  | 0.12179 | 0.17882 | 0.16744 | -0.009858 | 0.11516 | -0.037916 | 0.61168 | -0.093476 | -0.54895 | -1.1182 | -0.38797 | 8.8786 | 8.8796 | 2.0086 | 15.9902 | 16.8444 | 17.3638 | 17.6846 | 17.6493 | 16.6388 | 15.006 | 16.9241 | 17.2545 | 17.5428 | 17.5805 | 17.3318 | 16.5566 | 14.7961 | 6.1838 | 8.5075 | 5.2456 | 5.6383 | 5.8467 | 6.6236 | 7.5201 | 16.0792 | 15.6668 | 15.5264 | 14.4541 | 14.3426 | 14.2774 |  |  |  | 10.9106 | 9.3555 | 9.077 | 8.9313 | -0.048373 | 0.15999 | 12.9385 |  |  | 10.7465 |  |  | 16.9881 | 16.1964 | 15.1842 | 16.4837 | 15.7725 | 14.8858 | 10.5476 | 10.7638 | 11.5462 | 11.508 | 9.4009 |  | 10.876 | 8.6526 | 10.2386 | 9.2061 | 11.2686 | 12.2436 |  | 12.499 |  |  | 11.7666 | 12.6612 | 12.5912 | [6 empty] | 12.5893 |  |  | 11.3374 |  |  | 9.4491 | 10.5014 | 12.4473 | 7.6127 | 9.4118 | 12.9689 | 7.9516 | 9.6436 | 12.9112 | 9.3185 | 10.4811 | 7.832 | 10.5378 | 8.2641 | 10.2403 | 8.1129 | 9.9438 | 13.7514 | 10.9013 | 10.5766 | 11.826 | 8.2148 | 9.9015 | 13.1033 | 7.8646 | 10.4171 | 9.835 | 9.9483 | 8.3772 | 10.2656 | -0.066652 | 20.9597 | 0.034583 | 0.050657 | -38.1402 | 3.1215 | -1.7 | 0.31 | 0.40908 | 0.49259 | 0.47666 | -0.11566 | 0.39502 | -0.22666 | 0.9104 | 0.40997 | 0.40974 | 0.42833 | 0.39625 | 0.60458 | 0.43015 | 0.42415
42810.4324 | -657 | 18.6761 | 18.6933 | 18.6646 | 18.6875 | 18.0641 | 16.7174 | 14.7946 | 16.779 | 17.2742 | 17.3699 | 17.3922 | 16.9544 | 16.0312 | 14.6597 | 15.1464 | 15.0866 | 15.6212 | 13.4765 | 13.6042 | 14.1831 |  |  |  | 16.6864 | 16.0399 | 15.1683 | 10.3275 | 9.7634 | 9.8063 | 17.3909 | 16.4812 | 15.2825 | 16.9714 | 16.2651 | 15.2848 | 10.9694 | 12.1809 |  | 12.419 | 10.7469 | 10.6918 | 8.8026 |  | 6.3052 | 6.2447 | 5.6848 | 5.7321 | 5.7325 | 5.8462 | 6.126 | 4.7267 | 6.2828 | 4.5505 | 6.6312 | 8.236 | 42.2808 | 46.4199 | 43.0268 | 15.1464 |  |  | -0.031981 | -0.085993 | 0.14444 | -0.10119 | -0.089204 | 0.033052 | 0.59853 | -0.38129 | -0.15742 | -0.24459 | -0.34604 | 8.8843 | 8.8854 | 2.0086 | 15.9979 | 16.8309 | 17.3595 | 17.6806 | 17.646 | 16.6398 | 15.0007 | 16.9276 | 17.2515 | 17.5398 | 17.5794 | 17.3289 | 16.554 | 14.7938 | 6.1473 | 8.473 | 5.237 | 5.6514 | 6.023 | 6.6207 | 7.5213 | 16.0776 | 15.6659 | 15.5198 | 14.4486 | 14.3387 | 14.2729 |  |  |  | 10.9041 | 9.3549 | 9.0747 | 8.9103 | 0.098512 | 0.050274 | 12.9412 |  |  | 10.7417 |  |  | 16.9858 | 16.1961 | 15.1848 | 16.4831 | 15.7756 | 14.8913 | 10.5572 | 10.7763 | 11.5483 | 11.499 | 9.3779 |  | 10.8784 | 8.5081 | 10.2416 | 9.2111 | 11.2672 | 12.2046 |  | 12.4944 |  |  | 11.783 | 12.6715 | 12.6171 | [6 empty] | 12.6108 |  |  | 11.3499 |  |  | 9.455 | 10.5168 | 12.4471 | 7.5753 | 9.3822 | 12.9498 | 7.9507 | 9.6442 | 12.9031 | 9.3179 | 10.48 | 7.8005 | 10.5143 | 8.2624 | 10.2293 | 8.104 | 9.9564 | 13.7612 | 10.9149 | 10.5792 | 11.8306 | 8.2182 | 9.8971 | 13.1069 | 7.8573 | 10.4212 | 9.8491 | 9.9552 | 8.3798 | 10.2701 | -0.15794 | 20.9584 | 0.034262 | 0.049593 | -38.1478 | 3.1215 | -1.63 | 0.36 | -0.20964 | -0.34159 | 0.44272 | -0.37056 | -0.34766 | 0.21162 | 0.90055 | 0.41068 | 0.41386 | 0.42814 | 0.39997 | 0.60568 | 0.42966 | 0.42452
42810.4324 | -656 | 18.6816 | 18.6933 | 18.6689 | 18.6899 | 18.0638 | 16.7242 | 14.8009 | 16.7908 | 17.2765 | 17.3716 | 17.3927 | 16.9621 | 16.0346 | 14.6647 | 15.1453 | 15.0987 | 15.6307 | 13.482 | 13.6112 | 14.1875 |  |  |  | 16.69 | 16.0407 | 15.1692 | 10.3272 | 9.7664 | 9.81 | 17.3947 | 16.4791 | 15.278 | 16.9731 | 16.2593 | 15.2848 | 10.9672 | 12.1879 |  | 12.4218 | 10.7387 | 10.7068 | 8.8026 |  | 6.3008 | 6.2409 | 5.6804 | 5.7326 | 5.7393 | 5.851 | 6.1365 | 4.8202 | 6.282 | 4.5429 | 6.6319 | 8.2338 | 42.2629 | 46.4139 | 43.0139 | 15.137 |  |  | 0.043587 | -0.047881 | 0.001852 | -0.082798 | 0.01922 | 0.006768 | 0.58014 | -0.34975 | 0.091283 | -0.34131 | -0.18629 | 8.8843 | 8.8856 | 2.0083 | 15.994 | 16.8364 | 17.3554 | 17.6765 | 17.6334 | 16.6408 | 14.9913 | 16.9203 | 17.2485 | 17.5325 | 17.5708 | 17.3297 | 16.5514 | 14.7908 | 6.1271 | 8.4573 | 5.2297 | 5.6241 | 6.1623 | 6.6204 | 7.5189 | 16.0796 | 15.6764 | 15.5191 | 14.4509 | 14.344 | 14.2755 |  |  |  | 10.9051 | 9.3643 | 9.0662 | 8.8973 | 0.091219 | 0.13402 | 12.9513 |  |  | 10.7368 |  |  | 16.9937 | 16.2019 | 15.1974 | 16.4932 | 15.7831 | 14.8964 | 10.5682 | 10.7841 | 11.5557 | 11.5021 | 9.3237 |  | 10.8704 | 8.3828 | 10.2457 | 9.2018 | 11.2555 | 12.1487 |  | 12.4883 |  |  | 11.8005 | 12.6526 | 12.6358 | [6 empty] | 12.6147 |  |  | 11.3421 |  |  | 9.4502 | 10.5232 | 12.4555 | 7.5632 | 9.3661 | 12.9416 | 7.9463 | 9.646 | 12.8981 | 9.3249 | 10.4906 | 7.7737 | 10.5006 | 8.2666 | 10.222 | 8.1024 | 9.9525 | 13.7504 | 10.9088 | 10.5739 | 11.8226 | 8.2138 | 9.8984 | 13.0999 | 7.8562 | 10.4116 | 9.8457 | 9.9568 | 8.372 | 10.262 | -0.11365 | 20.9593 | 0.034325 | 0.050035 | -38.1547 | 3.1215 | -1.41 | 0.36 | 0.24474 | -0.25489 | 0.05013 | -0.33518 | 0.16138 | 0.095764 | 0.88661 | 0.41193 | 0.41747 | 0.42801 | 0.40218 | 0.6062 | 0.42959 | 0.42491
42810.4325 | -655 | 18.6921 | 18.6963 | 18.6694 | 18.6945 | 18.0634 | 16.7249 | 14.7999 | 16.7945 | 17.279 | 17.3757 | 17.3949 | 16.9639 | 16.0366 | 14.6566 | 15.1536 | 15.1105 | 15.6385 | 13.4835 | 13.6104 | 14.1895 |  |  |  | 16.6989 | 16.0495 | 15.1765 | 10.3364 | 9.7687 | 9.8357 | 17.4073 | 16.4898 | 15.2842 | 16.9798 | 16.2658 | 15.2939 | 10.9702 | 12.1703 |  | 12.4279 | 10.7278 | 10.7176 | 8.8082 |  | 6.3077 | 6.2556 | 5.6813 | 5.7459 | 5.7341 | 5.8531 | 6.2222 | 4.9034 | 6.2939 | 4.5656 | 6.6319 | 8.2416 | 42.2651 | 46.4216 | 43.0134 | 15.1325 |  |  | 0.065931 | -0.089281 | 0.07742 | -0.099226 | -0.037948 | 0.2591 | 0.66359 | -0.37735 | -1.0689 | 0.03885 | -0.27928 | 8.8797 | 8.8809 | 2.0087 | 15.9948 | 16.8356 | 17.3597 | 17.6672 | 17.6437 | 16.6333 | 14.9993 | 16.9239 | 17.2509 | 17.5322 | 17.5794 | 17.331 | 16.5531 | 14.7908 | 6.1204 | 8.461 | 5.2179 | 5.6077 | 6.1923 | 6.6143 | 7.5283 | 16.0699 | 15.6711 | 15.5231 | 14.4486 | 14.3364 | 14.2729 |  |  |  | 10.8975 | 9.3544 | 9.0605 | 8.8802 | 0.1986 | 0.21326 | 12.9567 |  |  | 10.7351 |  |  | 16.9972 | 16.2039 | 15.1983 | 16.4884 | 15.777 | 14.8954 | 10.5662 | 10.7838 | 11.5582 | 11.4883 | 9.2807 |  | 10.8753 | 8.2719 | 10.252 | 9.2014 | 11.2695 | 12.1419 |  | 12.4938 |  |  | 11.8279 | 12.6366 | 12.6515 | [6 empty] | 12.6284 |  |  | 11.3416 |  |  | 9.4464 | 10.5224 | 12.4553 | 7.5606 | 9.3526 | 12.9212 | 7.9318 | 9.6389 | 12.8816 | 9.3143 | 10.4843 | 7.7406 | 10.4865 | 8.2498 | 10.2152 | 8.1176 | 9.9636 | 13.7565 | 10.9078 | 10.5951 | 11.8253 | 8.2117 | 9.9076 | 13.1038 | 7.8578 | 10.4231 | 9.8494 | 9.9708 | 8.3759 | 10.2676 | 0.10996 | 20.9578 | 0.034302 | 0.04926 | -38.1845 | 3.1215 | -1.61 | 0.26 | 0.30102 | -0.34807 | 0.32412 | -0.36694 | -0.22676 | 0.59252 | 0.94825 | 0.41328 | 0.42076 | 0.42848 | 0.40221 | 0.60861 | 0.42954 | 0.42514
42810.4325 | -654 | 18.6934 | 18.7012 | 18.6736 | 18.6994 | 18.0708 | 16.7355 | 14.8042 | 16.7964 | 17.2829 | 17.3775 | 17.4027 | 16.9735 | 16.0481 | 14.6635 | 15.1514 | 15.0969 | 15.6345 | 13.4766 | 13.6043 | 14.1884 |  |  |  | 16.6962 | 16.0455 | 15.1632 | 10.3267 | 9.756 | 9.828 | 17.4026 | 16.4891 | 15.2817 | 16.9789 | 16.266 | 15.2929 | 10.9692 | 12.1182 |  | 12.428 | 10.7046 | 10.7222 | 8.7915 |  | 6.3071 | 6.2583 | 5.6891 | 5.7442 | 5.7359 | 5.8808 | 6.2937 | 4.933 | 6.2982 | 4.5904 | 6.6434 | 8.2376 | 42.2681 | 46.4193 | 43.0064 | 15.1316 |  |  | -0.000437 | -0.059709 | 0.14313 | 0.013798 | 0.10793 | -0.055 | 0.53348 | -0.36552 | 0.049638 | 0.52181 | -0.2157 | 8.8864 | 8.8872 | 2.0085 | 15.996 | 16.8435 | 17.3551 | 17.6802 | 17.648 | 16.6397 | 14.9974 | 16.9284 | 17.2449 | 17.5393 | 17.5839 | 17.3312 | 16.5656 | 14.7918 | 6.1231 | 8.4668 | 5.235 | 5.6085 | 6.1088 | 6.6201 | 7.5287 | 16.0741 | 15.6748 | 15.5294 | 14.4516 | 14.3356 | 14.2794 |  |  |  | 10.9055 | 9.354 | 9.0619 | 8.8998 | 0.099931 | 0.18051 | 12.9466 |  |  | 10.7249 |  |  | 16.9915 | 16.1951 | 15.1851 | 16.4877 | 15.7679 | 14.8923 | 10.5592 | 10.7691 | 11.5573 | 11.4638 | 9.2752 |  | 10.8715 | 8.1501 | 10.2385 | 9.2 | 11.2608 | 12.1858 |  | 12.4937 |  |  | 11.8561 | 12.6506 | 12.6701 | [6 empty] | 12.6409 |  |  | 11.3369 |  |  | 9.4468 | 10.5315 | 12.458 | 7.5661 | 9.3391 | 12.9067 | 7.9316 | 9.6375 | 12.8779 | 9.3195 | 10.4877 | 7.7292 | 10.4817 | 8.2428 | 10.2093 | 8.1199 | 9.971 | 13.7588 | 10.9039 | 10.6009 | 11.8247 | 8.2109 | 9.9162 | 13.1107 | 7.8687 | 10.4238 | 9.8541 | 9.9752 | 8.3768 | 10.2643 | 0.081458 | 20.9599 | 0.033458 | 0.04816 | -38.1609 | 3.1215 | -1.83 | 0.28 | -0.024507 | -0.28465 | 0.44071 | 0.13683 | 0.38244 | -0.27301 | 0.85026 | 0.41331 | 0.4237 | 0.42824 | 0.40259 | 0.60676 | 0.42997 | 0.42486
42810.4325 | -653 | 18.6912 | 18.7006 | 18.6679 | 18.693 | 18.0703 | 16.7313 | 14.8042 | 16.7983 | 17.2789 | 17.3818 | 17.3998 | 16.9696 | 16.0406 | 14.6641 | 15.1538 | 15.0927 | 15.6342 | 13.4722 | 13.6007 | 14.185 |  |  |  | 16.6897 | 16.0381 | 15.1659 | 10.3258 | 9.7456 | 9.8229 | 17.4024 | 16.4892 | 15.2799 | 16.9809 | 16.2641 | 15.2921 | 10.9674 | 12.0753 |  | 12.4307 | 10.6794 | 10.7209 | 8.7719 |  | 6.3122 | 6.2529 | 5.6989 | 5.7489 | 5.7381 | 5.8976 | 6.3277 | 4.942 | 6.2992 | 4.6168 | 6.6451 | 8.2456 | 42.2715 | 46.4152 | 43.0091 | 15.1303 |  |  | -0.027381 | -0.046569 | 0.1589 | 0.091338 | -0.010348 | -0.24096 | 0.56108 | -0.4562 | -0.24771 | 0.24068 | -0.47242 | 8.8766 | 8.878 | 2.0085 | 15.9908 | 16.837 | 17.3591 | 17.6788 | 17.6421 | 16.6319 | 15.0052 | 16.9236 | 17.2548 | 17.5361 | 17.5796 | 17.3292 | 16.5476 | 14.7924 | 6.1123 | 8.484 | 5.2419 | 5.6279 | 6.0233 | 6.6189 | 7.5288 | 16.074 | 15.6684 | 15.5146 | 14.4467 | 14.3279 | 14.2734 |  |  |  | 10.8991 | 9.344 | 9.047 | 8.8816 | 0.10986 | 0.16056 | 12.9492 |  |  | 10.72 |  |  | 16.9872 | 16.198 | 15.1865 | 16.4885 | 15.7737 | 14.8945 | 10.5697 | 10.7695 | 11.5527 | 11.4422 | 9.2471 |  | 10.8697 | 8.0411 | 10.2366 | 9.2124 | 11.2667 | 12.2365 |  | 12.5042 |  |  | 11.8581 | 12.6545 | 12.6806 | [6 empty] | 12.6366 |  |  | 11.338 |  |  | 9.454 | 10.5357 | 12.4676 | 7.5696 | 9.3439 | 12.901 | 7.9346 | 9.6348 | 12.8732 | 9.3309 | 10.4977 | 7.7277 | 10.4838 | 8.2508 | 10.2001 | 8.1152 | 9.9725 | 13.7596 | 10.9 | 10.599 | 11.8182 | 8.212 | 9.9165 | 13.1122 | 7.88 | 10.4304 | 9.8537 | 9.9696 | 8.3703 | 10.2543 | 0.080109 | 20.9588 | 0.032994 | 0.048233 | -38.1428 | 3.1215 | -1.85 | 0.32 | -0.19398 | -0.25138 | 0.46435 | 0.35205 | -0.11842 | -0.57146 | 0.872 | 0.41403 | 0.42667 | 0.42809 | 0.40365 | 0.60599 | 0.43045 | 0.42515
42810.4325 | -652 | 18.6793 | 18.697 | 18.6639 | 18.6937 | 18.056 | 16.7242 | 14.796 | 16.7885 | 17.2748 | 17.376 | 17.4022 | 16.9677 | 16.033 | 14.6594 | 15.1532 | 15.0977 | 15.6298 | 13.4755 | 13.5977 | 14.1827 |  |  |  | 16.6844 | 16.0367 | 15.1697 | 10.3213 | 9.7388 | 9.8238 | 17.4089 | 16.4849 | 15.2799 | 16.9789 | 16.2724 | 15.2953 | 10.9688 | 12.0413 |  | 12.4307 | 10.6752 | 10.721 | 8.7745 |  | 6.3093 | 6.2508 | 5.6908 | 5.7511 | 5.7394 | 5.8927 | 6.3593 | 4.963 | 6.2999 | 4.6347 | 6.6313 | 8.2392 | 42.2683 | 46.4004 | 43.0089 | 15.1144 |  |  | 0.1093 | -0.044597 | 0.15102 | 0.095938 | 0.057992 | -0.24228 | 0.59196 | -0.447 | -0.5112 | -0.41117 | -0.25504 | 8.8804 | 8.8818 | 2.0085 | 15.9924 | 16.8408 | 17.3645 | 17.6737 | 17.6364 | 16.6369 | 15.0006 | 16.9254 | 17.2535 | 17.5385 | 17.5799 | 17.3261 | 16.5483 | 14.7856 | 6.1101 | 8.5101 | 5.2691 | 5.657 | 5.9932 | 6.6305 | 7.5359 | 16.0768 | 15.6736 | 15.5199 | 14.4477 | 14.34 | 14.2752 |  |  |  | 10.8976 | 9.3469 | 9.0524 | 8.8729 | 0.22878 | 0.16677 | 12.9406 |  |  | 10.731 |  |  | 16.9925 | 16.1973 | 15.1823 | 16.4905 | 15.7783 | 14.8979 | 10.5791 | 10.7781 | 11.5377 | 11.4198 | 9.2196 |  | 10.8758 | 7.9544 | 10.2332 | 9.2209 | 11.2665 | 12.2709 |  | 12.5017 |  |  | 11.8547 | 12.6606 | 12.6762 | [6 empty] | 12.6314 |  |  | 11.3302 |  |  | 9.4544 | 10.5323 | 12.4579 | 7.5692 | 9.3491 | 12.8842 | 7.93 | 9.6261 | 12.8544 | 9.3361 | 10.495 | 7.721 | 10.4775 | 8.248 | 10.1835 | 8.113 | 9.9734 | 13.7584 | 10.8896 | 10.5927 | 11.8108 | 8.2017 | 9.9067 | 13.1057 | 7.8894 | 10.4359 | 9.8462 | 9.9694 | 8.3691 | 10.2482 | -0.078015 | 20.9586 | 0.033085 | 0.049115 | -38.1154 | 3.1215 | -1.93 | 0.33 | 0.38757 | -0.246 | 0.45268 | 0.36081 | 0.28034 | -0.57301 | 0.89567 | 0.41499 | 0.42896 | 0.42785 | 0.40524 | 0.60381 | 0.43042 | 0.42534
42810.4325 | -651 | 18.7017 | 18.702 | 18.6697 | 18.6956 | 18.062 | 16.7389 | 14.8063 | 16.7932 | 17.2826 | 17.3807 | 17.4066 | 16.9648 | 16.0383 | 14.6619 | 15.1545 | 15.1002 | 15.6254 | 13.4857 | 13.5988 | 14.1861 |  |  |  | 16.6893 | 16.0416 | 15.1656 | 10.3155 | 9.7384 | 9.8109 | 17.406 | 16.484 | 15.2845 | 16.9746 | 16.2672 | 15.2866 | 10.9682 | 12.031 |  | 12.4289 | 10.6567 | 10.7359 | 8.7888 |  | 6.3085 | 6.2557 | 5.6958 | 5.7532 | 5.7458 | 5.9021 | 6.3752 | 4.9594 | 6.3076 | 4.6559 | 6.6441 | 8.2422 | 42.2692 | 46.3994 | 42.999 | 15.1201 |  |  | -0.014893 | -0.10637 | 0.19373 | -0.044026 | 0.000164 | -0.34019 | 0.40074 | -0.45554 | -0.1401 | -0.24669 | -0.20596 | 8.8827 | 8.8837 | 2.0086 | 15.9927 | 16.8403 | 17.3582 | 17.6787 | 17.6364 | 16.6386 | 15.0068 | 16.9264 | 17.2516 | 17.5395 | 17.5841 | 17.3298 | 16.5467 | 14.7834 | 6.0972 | 8.5153 | 5.2893 | 5.6722 | 5.9923 | 6.6197 | 7.5309 | 16.0717 | 15.6638 | 15.5083 | 14.444 | 14.3317 | 14.2722 |  |  |  | 10.8913 | 9.3355 | 9.045 | 8.859 | 0.23 | 0.2492 | 12.9431 |  |  | 10.7356 |  |  | 17.0005 | 16.2018 | 15.1876 | 16.4897 | 15.7756 | 14.8978 | 10.5809 | 10.7744 | 11.5298 | 11.3941 | 9.2022 |  | 10.8769 | 7.9244 | 10.2341 | 9.2438 | 11.2656 | 12.3122 |  | 12.5096 |  |  | 11.8498 | 12.6488 | 12.6756 | [6 empty] | 12.633 |  |  | 11.3116 |  |  | 9.4601 | 10.5448 | 12.4552 | 7.5856 | 9.3494 | 12.877 | 7.9221 | 9.6215 | 12.8456 | 9.3354 | 10.4857 | 7.7296 | 10.4903 | 8.2493 | 10.1793 | 8.1192 | 9.9903 | 13.7637 | 10.8933 | 10.6021 | 11.8141 | 8.209 | 9.9146 | 13.112 | 7.901 | 10.4483 | 9.8565 | 9.9732 | 8.3726 | 10.2579 | -0.046814 | 20.9579 | 0.033636 | 0.048117 | -38.0992 | 3.1215 | -1.78 | 0.33 | -0.14306 | -0.37991 | 0.51272 | -0.24442 | 0.014908 | -0.679 | 0.73696 | 0.41551 | 0.42982 | 0.42718 | 0.40542 | 0.60099 | 0.43001 | 0.42552
42810.4325 | -650 | 18.6944 | 18.6967 | 18.6724 | 18.6967 | 18.0623 | 16.7266 | 14.8048 | 16.7845 | 17.2775 | 17.3724 | 17.4038 | 16.9665 | 16.0337 | 14.6582 | 15.1609 | 15.0947 | 15.6383 | 13.4884 | 13.6079 | 14.1908 |  |  |  | 16.6951 | 16.0396 | 15.1774 | 10.3208 | 9.747 | 9.8158 | 17.4147 | 16.4872 | 15.2861 | 16.986 | 16.2607 | 15.2916 | 10.9758 | 12.0157 |  | 12.4214 | 10.6543 | 10.7339 | 8.8077 |  | 6.3098 | 6.2603 | 5.7049 | 5.7562 | 5.7463 | 5.911 | 6.3936 | 5.0044 | 6.3229 | 4.6992 | 6.6509 | 8.2486 | 42.2741 | 46.4119 | 43.0008 | 15.1239 |  |  | 0.1047 | -0.13725 | 0.12736 | 0.042714 | 0.10202 | -0.47293 | 0.4382 | -0.5114 | -0.025866 | -0.45942 | -0.31664 | 8.8783 | 8.8792 | 2.0083 | 15.9972 | 16.845 | 17.3668 | 17.6828 | 17.6425 | 16.636 | 15.0061 | 16.9335 | 17.2524 | 17.5376 | 17.5797 | 17.3288 | 16.556 | 14.7892 | 6.0904 | 8.4889 | 5.3208 | 5.7035 | 6.013 | 6.6194 | 7.5372 | 16.0736 | 15.6645 | 15.5141 | 14.4529 | 14.3363 | 14.274 |  |  |  | 10.8929 | 9.3426 | 9.0526 | 8.8726 | 0.15402 | 0.14513 | 12.9412 |  |  | 10.7256 |  |  | 16.9874 | 16.1877 | 15.1881 | 16.4883 | 15.7731 | 14.8942 | 10.5718 | 10.7738 | 11.5197 | 11.3716 | 9.1592 |  | 10.8649 | 7.9148 | 10.2295 | 9.2346 | 11.2622 | 12.3135 |  | 12.4993 |  |  | 11.8551 | 12.6266 | 12.6653 | [6 empty] | 12.6237 |  |  | 11.3003 |  |  | 9.469 | 10.5425 | 12.457 | 7.5994 | 9.3487 | 12.8822 | 7.9166 | 9.6138 | 12.8377 | 9.3294 | 10.4812 | 7.7278 | 10.4914 | 8.2474 | 10.1742 | 8.1248 | 9.9876 | 13.7659 | 10.8881 | 10.6014 | 11.8242 | 8.2122 | 9.921 | 13.1109 | 7.908 | 10.4556 | 9.8547 | 9.9772 | 8.3749 | 10.252 | 0.028107 | 20.9591 | 0.034159 | 0.048898 | -38.1939 | 3.1215 | -1.68 | 0.22 | 0.37932 | -0.43156 | 0.41572 | 0.24075 | 0.37184 | -0.8006 | 0.77064 | 0.41631 | 0.42994 | 0.42732 | 0.40615 | 0.5982 | 0.42974 | 0.4252
42810.4325 | -649 | 18.7039 | 18.7001 | 18.6802 | 18.7 | 18.0646 | 16.7271 | 14.7991 | 16.7967 | 17.282 | 17.3763 | 17.4035 | 16.967 | 16.0389 | 14.6628 | 15.1577 | 15.0987 | 15.6383 | 13.4826 | 13.6055 | 14.1917 |  |  |  | 16.7019 | 16.0417 | 15.1768 | 10.3142 | 9.7525 | 9.8195 | 17.4 | 16.4901 | 15.2869 | 16.9767 | 16.2701 | 15.2941 | 10.9742 | 12.0133 |  | 12.4304 | 10.644 | 10.7297 | 8.8294 |  | 6.3064 | 6.2534 | 5.6917 | 5.7544 | 5.737 | 5.9023 | 6.3832 | 4.9913 | 6.3133 | 4.7247 | 6.6445 | 8.2506 | 42.2774 | 46.4126 | 42.997 | 15.1189 |  |  | -0.11083 | -0.012397 | 0.2279 | 0.13602 | -0.07672 | 0.04948 | 0.54531 | -0.28798 | -0.38043 | -0.17473 | -0.47878 | 8.8818 | 8.8829 | 2.0087 | 15.9935 | 16.8409 | 17.363 | 17.6796 | 17.6452 | 16.6417 | 15.0049 | 16.9365 | 17.2585 | 17.5368 | 17.5852 | 17.3363 | 16.5536 | 14.7855 | 6.1292 | 8.4646 | 5.3507 | 5.7173 | 6.0383 | 6.626 | 7.5448 | 16.0777 | 15.6753 | 15.516 | 14.4523 | 14.3341 | 14.2747 |  |  |  | 10.8943 | 9.3397 | 9.0565 | 8.8727 | 0.090611 | 0.26106 | 12.9304 |  |  | 10.7191 |  |  | 16.9834 | 16.1952 | 15.1873 | 16.4861 | 15.7654 | 14.8936 | 10.5664 | 10.7626 | 11.5141 | 11.3503 | 9.1568 |  | 10.8728 | 7.9725 | 10.2301 | 9.23 | 11.2653 | 12.2992 |  | 12.4928 |  |  | 11.8737 | 12.6051 | 12.655 | [6 empty] | 12.6169 |  |  | 11.297 |  |  | 9.4608 | 10.5421 | 12.457 | 7.6055 | 9.3398 | 12.8893 | 7.9012 | 9.608 | 12.8257 | 9.3287 | 10.4847 | 7.7241 | 10.5059 | 8.242 | 10.1764 | 8.1284 | 9.9876 | 13.7705 | 10.8868 | 10.5966 | 11.8352 | 8.2183 | 9.9239 | 13.1209 | 7.9181 | 10.4648 | 9.858 | 9.9767 | 8.3779 | 10.2574 | -0.029673 | 20.9599 | 0.034526 | 0.049108 | -38.1377 | 3.1215 | -1.44 | 0.35 | -0.39028 | -0.1297 | 0.5561 | 0.42962 | -0.32245 | 0.25896 | 0.85967 | 0.41664 | 0.42836 | 0.42755 | 0.4026 | 0.59577 | 0.42908 | 0.42524
42810.4325 | -648 | 18.6927 | 18.6919 | 18.6727 | 18.6933 | 18.0666 | 16.7226 | 14.7996 | 16.7878 | 17.276 | 17.3694 | 17.3934 | 16.9636 | 16.0273 | 14.6553 | 15.1588 | 15.1037 | 15.6407 | 13.4817 | 13.6113 | 14.1974 |  |  |  | 16.7008 | 16.0533 | 15.178 | 10.3166 | 9.7592 | 9.8268 | 17.4014 | 16.4932 | 15.293 | 16.9832 | 16.2729 | 15.296 | 10.9759 | 11.9917 |  | 12.4308 | 10.6348 | 10.7327 | 8.8357 |  | 6.317 | 6.2618 | 5.7112 | 5.7687 | 5.7563 | 5.9181 | 6.3995 | 5.0389 | 6.3263 | 4.795 | 6.6549 | 8.2492 | 42.2761 | 46.3906 | 42.9918 | 15.1218 |  |  | 0.089587 | -0.030141 | 0.15364 | -0.026942 | 0.093476 | -0.57346 | 0.55648 | -0.24921 | -0.26756 | -0.27627 | -0.088728 | 8.8878 | 8.8888 | 2.0085 | 16.0033 | 16.8486 | 17.3664 | 17.6767 | 17.6509 | 16.6415 | 15.0074 | 16.9299 | 17.2564 | 17.5377 | 17.584 | 17.3327 | 16.5546 | 14.7916 | 6.1819 | 8.4516 | 5.385 | 5.7326 | 6.0603 | 6.6232 | 7.5382 | 16.0806 | 15.673 | 15.5198 | 14.4533 | 14.3323 | 14.2768 |  |  |  | 10.8982 | 9.3454 | 9.0561 | 8.8771 | 0.027805 | 0.17787 | 12.936 |  |  | 10.7282 |  |  | 16.981 | 16.2028 | 15.1857 | 16.4843 | 15.7678 | 14.8915 | 10.572 | 10.7726 | 11.506 | 11.3325 | 9.1455 |  | 10.868 | 8.0565 | 10.224 | 9.2119 | 11.2624 | 12.2497 |  | 12.4883 |  |  | 11.8997 | 12.617 | 12.6627 | [6 empty] | 12.6215 |  |  | 11.3182 |  |  | 9.4736 | 10.5586 | 12.4649 | 7.6217 | 9.3592 | 12.9133 | 7.8854 | 9.6146 | 12.8293 | 9.3421 | 10.4913 | 7.7373 | 10.5188 | 8.2399 | 10.1807 | 8.1465 | 10.0196 | 13.782 | 10.8982 | 10.6124 | 11.8445 | 8.2279 | 9.941 | 13.1296 | 7.9505 | 10.4841 | 9.8599 | 9.9961 | 8.3867 | 10.2677 | -0.080519 | 20.9613 | 0.034549 | 0.049579 | -38.2168 | 3.1215 | -1.28 | 0.33 | 0.35089 | -0.20224 | 0.45661 | -0.19121 | 0.35594 | -0.88161 | 0.86845 | 0.4168 | 0.42582 | 0.42796 | 0.39642 | 0.59119 | 0.42896 | 0.42525
42810.4325 | -647 | 18.6965 | 18.694 | 18.6722 | 18.6953 | 18.0609 | 16.7285 | 14.7969 | 16.79 | 17.2769 | 17.3685 | 17.3948 | 16.9592 | 16.0285 | 14.6536 | 15.1626 | 15.1064 | 15.642 | 13.5008 | 13.6216 | 14.2025 |  |  |  | 16.705 | 16.0491 | 15.1815 | 10.3126 | 9.765 | 9.8309 | 17.3953 | 16.4869 | 15.2868 | 16.9815 | 16.2719 | 15.2898 | 10.9683 | 11.9562 |  | 12.4262 | 10.6283 | 10.7311 | 8.8226 |  | 6.3006 | 6.2429 | 5.6936 | 5.7632 | 5.7533 | 5.9092 | 6.3883 | 5.0712 | 6.3098 | 4.86 | 6.6451 | 8.2457 | 42.2571 | 46.3705 | 42.9892 | 15.1105 |  |  | 0.090903 | -0.090593 | 0.10568 | -0.20305 | -0.03532 | 0.31496 | 0.62219 | -0.27812 | 0.11775 | -0.10423 | -0.17059 | 8.8797 | 8.8808 | 2.0085 | 15.9977 | 16.8455 | 17.3586 | 17.6825 | 17.6398 | 16.647 | 15.0017 | 16.9294 | 17.2543 | 17.541 | 17.5838 | 17.3267 | 16.5505 | 14.7957 | 6.2275 | 8.4799 | 5.4167 | 5.7606 | 6.0849 | 6.6255 | 7.5414 | 16.0747 | 15.6738 | 15.5215 | 14.4468 | 14.3365 | 14.2844 |  |  |  | 10.8978 | 9.3482 | 9.057 | 8.8686 | 0.059208 | 0.10843 | 12.9382 |  |  | 10.7356 |  |  | 16.9975 | 16.2002 | 15.1896 | 16.4889 | 15.7718 | 14.8967 | 10.5787 | 10.7732 | 11.5072 | 11.3219 | 9.128 |  | 10.8678 | 8.1255 | 10.2293 | 9.198 | 11.2673 | 12.2084 |  | 12.487 |  |  | 11.9328 | 12.6134 | 12.6566 | [6 empty] | 12.6138 |  |  | 11.3107 |  |  | 9.4659 | 10.5579 | 12.4545 | 7.6192 | 9.3626 | 12.9097 | 7.87 | 9.6056 | 12.8124 | 9.3253 | 10.4878 | 7.7223 | 10.5166 | 8.2322 | 10.1598 | 8.1395 | 10.0071 | 13.7714 | 10.8889 | 10.5995 | 11.8306 | 8.2153 | 9.9328 | 13.1172 | 7.959 | 10.4726 | 9.8584 | 9.9941 | 8.3702 | 10.26 | -0.075511 | 20.9605 | 0.034646 | 0.050158 | -38.0696 | 3.1215 | -1.21 | 0.33 | 0.35346 | -0.35061 | 0.37867 | -0.5249 | -0.21879 | 0.65334 | 0.91828 | 0.41728 | 0.42408 | 0.42851 | 0.39162 | 0.58804 | 0.42907 | 0.42547
42810.4326 | -646 | 18.6979 | 18.6999 | 18.6796 | 18.7009 | 18.0626 | 16.7302 | 14.8062 | 16.7953 | 17.2852 | 17.3756 | 17.3948 | 16.964 | 16.0365 | 14.6577 | 15.1608 | 15.0997 | 15.6382 | 13.4888 | 13.6095 | 14.1955 |  |  |  | 16.6955 | 16.0315 | 15.1783 | 10.307 | 9.7605 | 9.8103 | 17.4058 | 16.4933 | 15.2847 | 16.9878 | 16.2736 | 15.2877 | 10.9724 | 11.9074 |  | 12.429 | 10.6396 | 10.7309 | 8.8512 |  | 6.3057 | 6.2523 | 5.6977 | 5.7706 | 5.7527 | 5.9107 | 6.387 | 5.0887 | 6.3203 | 4.9199 | 6.647 | 8.2578 | 42.2396 | 46.3745 | 42.99 | 15.1093 |  |  | -0.029353 | 0.090111 | 0.051792 | -0.44027 | 0.13619 | -0.093112 | 0.47302 | -0.26695 | -1.0201 | -0.24396 | -0.3224 | 8.8783 | 8.8794 | 2.0086 | 15.9869 | 16.831 | 17.3541 | 17.6722 | 17.6443 | 16.6388 | 14.9943 | 16.9186 | 17.2465 | 17.5317 | 17.5689 | 17.323 | 16.548 | 14.7842 | 6.2623 | 8.5035 | 5.4408 | 5.8442 | 6.1348 | 6.6253 | 7.536 | 16.0748 | 15.6708 | 15.518 | 14.4442 | 14.3301 | 14.2774 |  |  |  | 10.8941 | 9.3575 | 9.0417 | 8.8636 | 0.14389 | 0.098642 | 12.9238 |  |  | 10.7338 |  |  | 16.9923 | 16.1966 | 15.1852 | 16.478 | 15.772 | 14.886 | 10.5708 | 10.7746 | 11.51 | 11.3187 | 9.0564 |  | 10.8627 | 8.1867 | 10.2211 | 9.1894 | 11.2684 | 12.1746 |  | 12.4885 |  |  | 11.9412 | 12.6076 | 12.6293 | [6 empty] | 12.6064 |  |  | 11.2661 |  |  | 9.4702 | 10.5641 | 12.4568 | 7.6342 | 9.3622 | 12.9183 | 7.8733 | 9.6201 | 12.8246 | 9.3235 | 10.5001 | 7.7341 | 10.524 | 8.2412 | 10.1674 | 8.1504 | 10.0157 | 13.7713 | 10.8789 | 10.6032 | 11.8246 | 8.2015 | 9.9307 | 13.1179 | 7.9688 | 10.4727 | 9.8548 | 9.9925 | 8.3755 | 10.2671 | 0.00904 | 20.9599 | 0.03483 | 0.051019 | -38.0779 | 3.1216 | -0.93 | 0.26 | -0.20084 | 0.34968 | 0.2651 | -0.77293 | 0.42962 | -0.35524 | 0.80068 | 0.4191 | 0.42211 | 0.42878 | 0.38773 | 0.58474 | 0.42841 | 0.42549
42810.4326 | -645 | 18.697 | 18.7064 | 18.6765 | 18.7102 | 18.0698 | 16.7321 | 14.813 | 16.7898 | 17.2848 | 17.3734 | 17.4105 | 16.9631 | 16.0382 | 14.6628 | 15.1629 | 15.1086 | 15.645 | 13.4995 | 13.6023 | 14.193 |  |  |  | 16.6995 | 16.0427 | 15.1693 | 10.3061 | 9.7584 | 9.8108 | 17.4109 | 16.494 | 15.2861 | 16.9857 | 16.2766 | 15.2879 | 10.9585 | 11.84 |  | 12.4251 | 10.6399 | 10.7221 | 8.8685 |  | 6.3105 | 6.2557 | 5.707 | 5.7773 | 5.7628 | 5.9156 | 6.392 | 5.1075 | 6.3255 | 4.9892 | 6.6541 | 8.2507 | 42.2158 | 46.3747 | 42.982 | 15.1044 |  |  | 0.027159 | -0.22202 | -0.046776 | -0.19188 | 0.21636 | 0.082996 | 0.48354 | -0.24855 | -0.23681 | 0.21571 | -0.34604 | 8.8786 | 8.8796 | 2.0087 | 15.9947 | 16.8398 | 17.3596 | 17.6766 | 17.6469 | 16.6371 | 15.0005 | 16.9235 | 17.25 | 17.5333 | 17.5737 | 17.328 | 16.545 | 14.7829 | 6.3028 | 8.5272 | 5.4524 | 6.0549 | 6.2249 | 6.6331 | 7.545 | 16.0739 | 15.667 | 15.5172 | 14.4468 | 14.3309 | 14.2741 |  |  |  | 10.8899 | 9.3653 | 9.04 | 8.8552 | 0.086559 | 0.042746 | 12.9135 |  |  | 10.7346 |  |  | 16.9871 | 16.1946 | 15.1907 | 16.4746 | 15.7656 | 14.8793 | 10.5635 | 10.7788 | 11.5043 | 11.3089 | 8.9845 |  | 10.8554 | 8.2147 | 10.2085 | 9.1885 | 11.2588 | 12.1407 |  | 12.4804 |  |  | 11.9349 | 12.6065 | 12.6304 | [6 empty] | 12.6133 |  |  | 11.2561 |  |  | 9.4656 | 10.5685 | 12.4432 | 7.6446 | 9.3623 | 12.9177 | 7.8544 | 9.6091 | 12.81 | 9.3146 | 10.4824 | 7.7238 | 10.526 | 8.2324 | 10.1501 | 8.1601 | 10.0145 | 13.7714 | 10.8757 | 10.6032 | 11.8231 | 8.2127 | 9.9381 | 13.115 | 7.9875 | 10.4749 | 9.8516 | 10.0004 | 8.3638 | 10.2552 | -0.079941 | 20.9603 | 0.034704 | 0.051222 | -38.1878 | 3.1216 | -0.95 | 0.39 | 0.19319 | -0.54888 | -0.25194 | -0.51027 | 0.54151 | 0.33539 | 0.80954 | 0.42085 | 0.42092 | 0.42849 | 0.38413 | 0.58449 | 0.42748 | 0.42558
42810.4326 | -644 | 18.6904 | 18.6987 | 18.6753 | 18.7034 | 18.0643 | 16.7211 | 14.7999 | 16.79 | 17.2748 | 17.374 | 17.3978 | 16.9597 | 16.0315 | 14.657 | 15.1739 | 15.1117 | 15.6498 | 13.494 | 13.6091 | 14.1952 |  |  |  | 16.7114 | 16.051 | 15.1833 | 10.3109 | 9.7727 | 9.8377 | 17.412 | 16.4899 | 15.288 | 16.9847 | 16.2758 | 15.2867 | 10.964 | 11.7857 |  | 12.4294 | 10.6513 | 10.7266 | 8.8627 |  | 6.3173 | 6.254 | 5.7065 | 5.7715 | 5.767 | 5.9197 | 6.4023 | 5.1136 | 6.3301 | 4.9956 | 6.6622 | 8.2431 | 42.1966 | 46.3759 | 42.9765 | 15.0952 |  |  | -0.059577 | -0.059709 | 0.21476 | 0.07031 | 0.086248 | 0.053424 | 0.3692 | -0.46934 | -0.30726 | -0.52593 | -0.28445 | 8.893 | 8.8944 | 2.0084 | 15.9886 | 16.8436 | 17.3607 | 17.6746 | 17.6488 | 16.6398 | 15.0038 | 16.9215 | 17.2486 | 17.5323 | 17.5774 | 17.3224 | 16.5456 | 14.7855 | 6.3577 | 8.5222 | 5.4619 | 6.1944 | 6.2824 | 6.6281 | 7.5408 | 16.0751 | 15.6693 | 15.5187 | 14.4443 | 14.3307 | 14.2723 |  |  |  | 10.8877 | 9.3646 | 9.0408 | 8.8459 | 0.056574 | 0.031642 | 12.9179 |  |  | 10.7372 |  |  | 16.9957 | 16.1989 | 15.1864 | 16.4836 | 15.7658 | 14.886 | 10.5604 | 10.7787 | 11.5077 | 11.3125 | 8.8926 |  | 10.8551 | 8.2355 | 10.2166 | 9.1966 | 11.2666 | 12.1017 |  | 12.4802 |  |  | 11.9165 | 12.6077 | 12.6132 | [6 empty] | 12.6201 |  |  | 11.2446 |  |  | 9.4598 | 10.5641 | 12.4471 | 7.6519 | 9.3657 | 12.9202 | 7.8398 | 9.6037 | 12.8024 | 9.3188 | 10.481 | 7.7282 | 10.5323 | 8.2223 | 10.1448 | 8.173 | 10.0104 | 13.7522 | 10.8704 | 10.5995 | 11.8126 | 8.2063 | 9.9416 | 13.1161 | 8.001 | 10.4765 | 9.8432 | 9.9805 | 8.3637 | 10.2542 | -0.11923 | 20.9602 | 0.033786 | 0.049608 | -38.1508 | 3.1215 | -0.78 | 0.42 | -0.28615 | -0.28464 | 0.53983 | 0.30888 | 0.3419 | 0.26909 | 0.70738 | 0.4234 | 0.4206 | 0.42852 | 0.37745 | 0.58295 | 0.42782 | 0.42577
42810.4326 | -643 | 18.697 | 18.7076 | 18.6804 | 18.7016 | 18.0688 | 16.7367 | 14.8029 | 16.7879 | 17.2846 | 17.3794 | 17.4007 | 16.9653 | 16.0404 | 14.6661 | 15.1714 | 15.104 | 15.6466 | 13.4965 | 13.6133 | 14.1927 |  |  |  | 16.703 | 16.0436 | 15.1689 | 10.3093 | 9.77 | 9.852 | 17.4205 | 16.4972 | 15.2955 | 16.9945 | 16.2786 | 15.3 | 10.9625 | 11.7329 |  | 12.4329 | 10.6675 | 10.7139 | 8.8697 |  | 6.3096 | 6.2612 | 5.7025 | 5.7762 | 5.7658 | 5.9126 | 6.3941 | 5.1161 | 6.3283 | 4.9654 | 6.6517 | 8.2416 | 42.1702 | 46.3839 | 42.9686 | 15.0902 |  |  | 0.052131 | -0.20099 | 0.22133 | -0.14851 | 0.21373 | -0.42036 | 0.337 | -0.25841 | -0.19381 | -0.64132 | -0.29697 | 8.8866 | 8.8882 | 2.0085 | 15.9923 | 16.8432 | 17.3626 | 17.6781 | 17.6543 | 16.6376 | 14.9999 | 16.9224 | 17.2539 | 17.538 | 17.5832 | 17.3221 | 16.549 | 14.7916 | 6.3946 | 8.5284 | 5.4834 | 6.2788 | 6.3509 | 6.6339 | 7.5357 | 16.0655 | 15.66 | 15.5119 | 14.4383 | 14.3313 | 14.27 |  |  |  | 10.8854 | 9.359 | 9.0337 | 8.8245 | 0.076632 | 0.024867 | 12.9249 |  |  | 10.7378 |  |  | 17.0033 | 16.203 | 15.1884 | 16.4915 | 15.7746 | 14.8949 | 10.5711 | 10.7853 | 11.5084 | 11.3171 | 8.7932 |  | 10.861 | 8.3198 | 10.219 | 9.1913 | 11.2647 | 12.067 |  | 12.4835 |  |  | 11.9242 | 12.6004 | 12.624 | [6 empty] | 12.6111 |  |  | 11.2421 |  |  | 9.4589 | 10.5666 | 12.4572 | 7.6693 | 9.3756 | 12.9295 | 7.8263 | 9.5961 | 12.8056 | 9.3205 | 10.4854 | 7.74 | 10.5429 | 8.2229 | 10.1405 | 8.1788 | 10.0082 | 13.746 | 10.8645 | 10.5961 | 11.8112 | 8.2026 | 9.9348 | 13.1112 | 8.0075 | 10.4721 | 9.84 | 9.9824 | 8.35 | 10.2478 | -0.1383 | 20.9598 | 0.032305 | 0.047748 | -38.1258 | 3.1216 | -1.02 | 0.2 | 0.26768 | -0.52225 | 0.54803 | -0.44892 | 0.53821 | -0.75479 | 0.67582 | 0.42635 | 0.41834 | 0.42861 | 0.37403 | 0.57998 | 0.42757 | 0.42629
42810.4326 | -642 | 18.6982 | 18.704 | 18.6776 | 18.7044 | 18.0684 | 16.7365 | 14.8001 | 16.7915 | 17.2796 | 17.3818 | 17.4041 | 16.9674 | 16.0397 | 14.6618 | 15.1727 | 15.1056 | 15.6406 | 13.4912 | 13.6087 | 14.1976 |  |  |  | 16.6986 | 16.0497 | 15.1737 | 10.301 | 9.7697 | 9.8736 | 17.4159 | 16.5003 | 15.2969 | 16.995 | 16.2679 | 15.296 | 10.9573 | 11.6902 |  | 12.4208 | 10.6731 | 10.707 | 8.8694 |  | 6.3101 | 6.259 | 5.7037 | 5.7702 | 5.7684 | 5.9096 | 6.372 | 5.1198 | 6.325 | 4.9828 | 6.6595 | 8.2515 | 42.1487 | 46.4129 | 42.9731 | 15.096 |  |  | 0.035703 | -0.21611 | 0.15956 | 0.23788 | -0.01232 | -0.0504 | 0.37774 | -0.35961 | -0.5797 | -0.53558 | -0.16463 | 8.879 | 8.8801 | 2.0084 | 15.9921 | 16.8358 | 17.3624 | 17.6762 | 17.6504 | 16.63 | 14.9912 | 16.9225 | 17.2478 | 17.5372 | 17.5779 | 17.3173 | 16.5402 | 14.7838 | 6.4237 | 8.5433 | 5.5458 | 6.3438 | 6.4093 | 6.6324 | 7.5317 | 16.059 | 15.6589 | 15.5114 | 14.443 | 14.3347 | 14.2651 |  |  |  | 10.876 | 9.3602 | 9.0323 | 8.8136 | -0.046347 | 0.044064 | 12.9241 |  |  | 10.7428 |  |  | 16.9999 | 16.2021 | 15.1977 | 16.4886 | 15.7765 | 14.8915 | 10.5912 | 10.7869 | 11.5106 | 11.3224 | 8.7716 |  | 10.8607 | 8.4065 | 10.2225 | 9.2008 | 11.2697 | 12.0291 |  | 12.4838 |  |  | 11.9409 | 12.5981 | 12.6339 | [6 empty] | 12.6166 |  |  | 11.2565 |  |  | 9.4441 | 10.5711 | 12.457 | 7.6753 | 9.374 | 12.9254 | 7.8163 | 9.5933 | 12.8048 | 9.3121 | 10.4829 | 7.7393 | 10.5299 | 8.2176 | 10.1373 | 8.1937 | 10.0142 | 13.741 | 10.8476 | 10.5996 | 11.8074 | 8.1975 | 9.9368 | 13.1032 | 8.0143 | 10.4646 | 9.8388 | 9.975 | 8.3422 | 10.2467 | -0.2215 | 20.9601 | 0.033114 | 0.047393 | -38.0656 | 3.1216 | -1.04 | 0.32 | 0.22153 | -0.54153 | 0.46532 | 0.56815 | -0.12922 | -0.26135 | 0.71551 | 0.42694 | 0.41605 | 0.42851 | 0.37063 | 0.57258 | 0.42741 | 0.42628
42810.4326 | -641 | 18.6947 | 18.7044 | 18.6742 | 18.7072 | 18.0662 | 16.7299 | 14.7966 | 16.7898 | 17.273 | 17.3807 | 17.403 | 16.968 | 16.0357 | 14.6492 | 15.1731 | 15.1095 | 15.6461 | 13.4884 | 13.61 | 14.1929 |  |  |  | 16.6934 | 16.0486 | 15.1692 | 10.3059 | 9.774 | 9.8896 | 17.4094 | 16.4962 | 15.2865 | 16.9836 | 16.2694 | 15.2892 | 10.9541 | 11.6441 |  | 12.4128 | 10.6704 | 10.7065 | 8.8322 |  | 6.3175 | 6.2624 | 5.7096 | 5.7785 | 5.7698 | 5.8973 | 6.356 | 5.1313 | 6.3339 | 5.0619 | 6.6597 | 8.2518 | 42.1355 | 46.4283 | 42.9799 | 15.1006 |  |  | 0.037019 | -0.078109 | 0.1405 | 0.14062 | -0.026776 | -0.24556 | 0.54268 | -0.23147 | 1.1145 | -0.46782 | -0.29816 | 8.8779 | 8.8793 | 2.0086 | 15.9911 | 16.8427 | 17.3712 | 17.6797 | 17.6524 | 16.643 | 14.9981 | 16.9259 | 17.2519 | 17.5346 | 17.5792 | 17.3277 | 16.5439 | 14.7888 | 6.4334 | 8.5471 | 5.6361 | 6.3246 | 6.4641 | 6.6274 | 7.5337 | 16.074 | 15.6685 | 15.5178 | 14.4498 | 14.336 | 14.271 |  |  |  | 10.8759 | 9.3611 | 9.0295 | 8.8089 | 0.033073 | 0.050274 | 12.9182 |  |  | 10.7394 |  |  | 16.9943 | 16.2005 | 15.1946 | 16.4801 | 15.7665 | 14.8908 | 10.5975 | 10.7824 | 11.5115 | 11.3213 | 8.7415 |  | 10.8461 | 8.4596 | 10.2175 | 9.1729 | 11.2573 | 11.9625 |  | 12.4799 |  |  | 11.9475 | 12.6004 | 12.638 | [6 empty] | 12.6208 |  |  | 11.264 |  |  | 9.4487 | 10.5707 | 12.4612 | 7.6841 | 9.3678 | 12.9191 | 7.8135 | 9.6032 | 12.7897 | 9.3121 | 10.4827 | 7.75 | 10.5259 | 8.2169 | 10.1363 | 8.2129 | 10.0136 | 13.7383 | 10.8524 | 10.6051 | 11.8148 | 8.2101 | 9.9409 | 13.1118 | 8.0306 | 10.4669 | 9.8435 | 9.9755 | 8.3466 | 10.2599 | 0.074524 | 20.9602 | 0.033453 | 0.049282 | -38.1347 | 3.1216 | -0.88 | 0.34 | 0.22558 | -0.32557 | 0.43664 | 0.43683 | -0.19049 | -0.57688 | 0.85759 | 0.4273 | 0.41441 | 0.42887 | 0.36896 | 0.56277 | 0.42834 | 0.42641
42810.4326 | -640 | 18.7043 | 18.7067 | 18.6758 | 18.7039 | 18.0677 | 16.7361 | 14.7968 | 16.7934 | 17.2792 | 17.3815 | 17.403 | 16.9649 | 16.0348 | 14.6574 | 15.1733 | 15.1164 | 15.6459 | 13.4972 | 13.615 | 14.1974 |  |  |  | 16.6953 | 16.0438 | 15.1721 | 10.3137 | 9.7813 | 9.8981 | 17.4079 | 16.4912 | 15.2851 | 16.9833 | 16.2675 | 15.2914 | 10.9609 | 11.6291 |  | 12.4139 | 10.6742 | 10.6964 | 8.8133 |  | 6.3197 | 6.2702 | 5.7153 | 5.784 | 5.7788 | 5.9076 | 6.3483 | 5.1577 | 6.3371 | 5.1325 | 6.6582 | 8.25 | 42.1151 | 46.4451 | 42.98 | 15.0898 |  |  | 0.085643 | -0.16353 | 0.007764 | -0.29439 | -0.11483 | -0.040544 | 0.4474 | -0.29127 | -0.76243 | -0.21836 | -0.39175 | 8.8792 | 8.8803 | 2.0087 | 15.9869 | 16.8417 | 17.362 | 17.6811 | 17.6509 | 16.6414 | 15.0049 | 16.9263 | 17.2469 | 17.5326 | 17.5714 | 17.3196 | 16.5527 | 14.7846 | 6.4391 | 8.5012 | 5.6792 | 6.2966 | 6.5319 | 6.6256 | 7.5346 | 16.0681 | 15.6682 | 15.5094 | 14.445 | 14.3332 | 14.2697 |  |  |  | 10.8819 | 9.3545 | 9.0245 | 8.8209 | -0.030341 | 0.036536 | 12.9219 |  |  | 10.7388 |  |  | 16.9941 | 16.2009 | 15.189 | 16.4826 | 15.7744 | 14.8912 | 10.6087 | 10.7778 | 11.5049 | 11.3298 | 8.747 |  | 10.8507 | 8.5031 | 10.2166 | 9.17 | 11.2639 | 11.9353 |  | 12.479 |  |  | 11.9631 | 12.6129 | 12.6318 | [6 empty] | 12.6347 |  |  | 11.2659 |  |  | 9.4489 | 10.5691 | 12.4639 | 7.6888 | 9.3737 | 12.9161 | 7.8201 | 9.6033 | 12.7717 | 9.3016 | 10.4885 | 7.7559 | 10.5187 | 8.2166 | 10.1371 | 8.216 | 10.0179 | 13.7322 | 10.8459 | 10.6001 | 11.8046 | 8.207 | 9.9336 | 13.1077 | 8.0331 | 10.4492 | 9.844 | 9.9655 | 8.3441 | 10.2595 | 0.069324 | 20.9606 | 0.033711 | 0.04934 | -38.1527 | 3.1216 | -0.82 | 0.28 | 0.34312 | -0.47108 | 0.10265 | -0.63205 | -0.3945 | -0.23441 | 0.77868 | 0.4273 | 0.41317 | 0.42917 | 0.36811 | 0.55809 | 0.42909 | 0.42627
42810.4326 | -639 | 18.7112 | 18.7063 | 18.6796 | 18.7049 | 18.0699 | 16.7293 | 14.7977 | 16.7885 | 17.2841 | 17.3835 | 17.3991 | 16.9726 | 16.034 | 14.6596 | 15.1682 | 15.1062 | 15.6348 | 13.491 | 13.6094 | 14.1939 |  |  |  | 16.6976 | 16.0394 | 15.1699 | 10.3071 | 9.78 | 9.9054 | 17.4098 | 16.4848 | 15.2913 | 16.9825 | 16.2653 | 15.2887 | 10.9536 | 11.6264 |  | 12.4129 | 10.6835 | 10.6945 | 8.8093 |  | 6.3224 | 6.2791 | 5.7321 | 5.8001 | 5.8032 | 5.9149 | 6.3802 | 5.1518 | 6.3436 | 5.165 | 6.6694 | 8.2526 | 42.1022 | 46.4591 | 42.9839 | 15.0875 |  |  | 0.023875 | -0.030141 | 0.00448 | 0.026942 | -0.028748 | -0.14568 | 0.36 | -0.20518 | -0.35221 | 1.3207 | -0.26557 | 8.8777 | 8.8789 | 2.0086 | 15.9945 | 16.8457 | 17.3617 | 17.6787 | 17.6502 | 16.6482 | 14.9959 | 16.9307 | 17.2568 | 17.5288 | 17.5803 | 17.3244 | 16.5457 | 14.7926 | 6.4458 | 8.503 | 5.6294 | 6.2783 | 6.5439 | 6.6259 | 7.527 | 16.0616 | 15.6702 | 15.5124 | 14.4464 | 14.3311 | 14.271 |  |  |  | 10.8733 | 9.3492 | 9.0268 | 8.8244 | -0.034191 | 0.18973 | 12.926 |  |  | 10.7441 |  |  | 16.995 | 16.1966 | 15.187 | 16.4839 | 15.7701 | 14.8863 | 10.6231 | 10.7723 | 11.5013 | 11.3277 | 8.7696 |  | 10.8521 | 8.5763 | 10.2154 | 9.1692 | 11.2621 | 11.9082 |  | 12.4836 |  |  | 11.9782 | 12.6274 | 12.6213 | [6 empty] | 12.6417 |  |  | 11.2677 |  |  | 9.4415 | 10.5659 | 12.4537 | 7.6836 | 9.3768 | 12.9119 | 7.816 | 9.5905 | 12.7477 | 9.3014 | 10.4931 | 7.7456 | 10.5063 | 8.2005 | 10.1277 | 8.2093 | 10.0175 | 13.7262 | 10.8386 | 10.5946 | 11.7947 | 8.201 | 9.9313 | 13.1031 | 8.0419 | 10.4325 | 9.8427 | 9.9588 | 8.3335 | 10.2521 | -0.12193 | 20.9596 | 0.033969 | 0.049 | -38.1857 | 3.1216 | -0.75 | 0.38 | 0.18117 | -0.20225 | 0.077973 | 0.19121 | -0.19739 | -0.44435 | 0.69851 | 0.42672 | 0.4111 | 0.42914 | 0.36741 | 0.56274 | 0.42896 | 0.42589
42810.4327 | -638 | 18.7049 | 18.7086 | 18.6805 | 18.7023 | 18.0709 | 16.7271 | 14.8021 | 16.7939 | 17.2845 | 17.3846 | 17.3936 | 16.972 | 16.0437 | 14.6578 | 15.1669 | 15.1055 | 15.6375 | 13.4878 | 13.6099 | 14.1908 |  |  |  | 16.701 | 16.045 | 15.1736 | 10.3093 | 9.7862 | 9.9385 | 17.4156 | 16.4904 | 15.287 | 16.9854 | 16.274 | 15.2864 | 10.9454 | 11.6171 |  | 12.4101 | 10.674 | 10.6928 | 8.7953 |  | 6.3172 | 6.2701 | 5.7301 | 5.8051 | 5.8118 | 5.9126 | 6.3735 | 5.0872 | 6.3407 | 5.1316 | 6.6713 | 8.2589 | 42.1049 | 46.4694 | 42.9879 | 15.0846 |  |  | -0.082577 | -0.47829 | -0.17886 | -0.065054 | -0.074748 | -0.43481 | 0.50062 | -0.13553 | -0.14574 | -1.1291 | -0.43765 | 8.8764 | 8.8778 | 2.0084 | 15.9893 | 16.8389 | 17.3616 | 17.6806 | 17.6451 | 16.6379 | 14.9958 | 16.9203 | 17.2435 | 17.5299 | 17.5782 | 17.3267 | 16.547 | 14.7816 | 6.4543 | 8.5186 | 5.5895 | 6.2641 | 6.5327 | 6.6273 | 7.539 | 16.0668 | 15.6747 | 15.5182 | 14.451 | 14.3274 | 14.2731 |  |  |  | 10.8725 | 9.3481 | 9.0283 | 8.8371 | 0.081899 | 0.16677 | 12.9286 |  |  | 10.7457 |  |  | 16.9991 | 16.1975 | 15.1877 | 16.4856 | 15.7718 | 14.8911 | 10.6329 | 10.7736 | 11.5026 | 11.3168 | 8.8212 |  | 10.8469 | 8.626 | 10.2132 | 9.1791 | 11.256 | 11.8732 |  | 12.4849 |  |  | 11.9958 | 12.6287 | 12.6191 | [6 empty] | 12.6435 |  |  | 11.2644 |  |  | 9.4369 | 10.5549 | 12.4441 | 7.6614 | 9.3778 | 12.9127 | 7.8113 | 9.5894 | 12.7282 | 9.3057 | 10.497 | 7.7244 | 10.4966 | 8.19 | 10.1225 | 8.1998 | 10.0108 | 13.7174 | 10.8385 | 10.5975 | 11.7865 | 8.2085 | 9.9382 | 13.111 | 8.0475 | 10.4298 | 9.8384 | 9.9569 | 8.333 | 10.2533 | -0.20956 | 20.9604 | 0.034245 | 0.048609 | -38.1154 | 3.1217 | -0.71 | 0.3 | -0.33694 | -0.80564 | -0.49266 | -0.29712 | -0.31829 | -0.76766 | 0.82371 | 0.42511 | 0.40965 | 0.42866 | 0.36661 | 0.56856 | 0.42908 | 0.42551
42810.4327 | -637 | 18.6956 | 18.7029 | 18.6708 | 18.7042 | 18.068 | 16.7314 | 14.7917 | 16.788 | 17.2765 | 17.3768 | 17.3946 | 16.9614 | 16.031 | 14.65 | 15.1756 | 15.1195 | 15.644 | 13.4921 | 13.6181 | 14.1899 |  |  |  | 16.7027 | 16.0441 | 15.1731 | 10.3154 | 9.7902 | 9.9477 | 17.4101 | 16.4912 | 15.2834 | 16.9899 | 16.2724 | 15.2858 | 10.9442 | 11.6159 |  | 12.4081 | 10.6751 | 10.6868 | 8.7699 |  | 6.3122 | 6.2644 | 5.7271 | 5.8041 | 5.7987 | 5.9196 | 6.3622 | 5.034 | 6.3425 | 5.0597 | 6.6661 | 8.2603 | 42.1072 | 46.4837 | 42.9827 | 15.0882 |  |  | -0.072065 | -0.23647 | 0.25747 | 0.12748 | 0.14867 | -0.51432 | 0.41783 | -0.2019 | 0.32013 | -0.33858 | -0.46248 | 8.8812 | 8.8827 | 2.0085 | 15.9934 | 16.8462 | 17.365 | 17.681 | 17.6567 | 16.6435 | 15.0053 | 16.9312 | 17.2567 | 17.5391 | 17.5815 | 17.3293 | 16.547 | 14.7945 | 6.4786 | 8.5397 | 5.5524 | 6.2295 | 6.5313 | 6.6317 | 7.5471 | 16.068 | 15.6683 | 15.5151 | 14.4521 | 14.3266 | 14.2732 |  |  |  | 10.8767 | 9.347 | 9.0293 | 8.8726 | 0.1674 | 0.049521 | 12.9224 |  |  | 10.7414 |  |  | 16.9965 | 16.2024 | 15.1858 | 16.4832 | 15.7685 | 14.8893 | 10.6383 | 10.7682 | 11.4993 | 11.3063 | 8.9016 |  | 10.856 | 8.6499 | 10.2192 | 9.1733 | 11.2688 | 11.8389 |  | 12.4831 |  |  | 11.9945 | 12.6272 | 12.6216 | [6 empty] | 12.633 |  |  | 11.2569 |  |  | 9.4267 | 10.539 | 12.4331 | 7.6301 | 9.3688 | 12.9067 | 7.7979 | 9.5895 | 12.7184 | 9.2937 | 10.4892 | 7.7143 | 10.4904 | 8.1753 | 10.1166 | 8.2047 | 10.0023 | 13.7126 | 10.8375 | 10.5982 | 11.7801 | 8.2129 | 9.9331 | 13.1156 | 8.0587 | 10.4284 | 9.8414 | 9.9541 | 8.3397 | 10.2609 | 0.025604 | 20.9596 | 0.033975 | 0.048985 | -38.1089 | 3.1216 | -1.02 | 0.26 | -0.31477 | -0.56648 | 0.59109 | 0.41593 | 0.44889 | -0.83491 | 0.75253 | 0.42318 | 0.40918 | 0.42925 | 0.36444 | 0.57363 | 0.42974 | 0.42466
42810.4327 | -636 | 18.6938 | 18.7025 | 18.6679 | 18.704 | 18.0669 | 16.7308 | 14.7927 | 16.7882 | 17.2729 | 17.3807 | 17.402 | 16.9659 | 16.0344 | 14.657 | 15.1723 | 15.1159 | 15.6423 | 13.489 | 13.6169 | 14.1888 |  |  |  | 16.7015 | 16.0415 | 15.167 | 10.3119 | 9.7911 | 9.9395 | 17.4191 | 16.5036 | 15.2952 | 16.9912 | 16.2799 | 15.2868 | 10.9486 | 11.6236 |  | 12.4234 | 10.6784 | 10.6882 | 8.7394 |  | 6.307 | 6.263 | 5.7201 | 5.7946 | 5.789 | 5.9072 | 6.3402 | 5.016 | 6.3437 | 5.0806 | 6.6684 | 8.2541 | 42.1154 | 46.4985 | 42.9763 | 15.0999 |  |  | -0.064837 | -0.28181 | 0.058364 | -0.12748 | 0.020536 | -0.15554 | 0.38037 | -0.27155 | -0.95995 | -0.37655 | -0.28703 | 8.8787 | 8.8796 | 2.0086 | 15.9935 | 16.8498 | 17.3716 | 17.6824 | 17.6572 | 16.6513 | 15.0024 | 16.9352 | 17.2567 | 17.5431 | 17.5841 | 17.3374 | 16.5496 | 14.7978 | 6.5153 | 8.5577 | 5.5359 | 6.2195 | 6.4833 | 6.6339 | 7.5539 | 16.0649 | 15.663 | 15.5032 | 14.4442 | 14.324 | 14.274 |  |  |  | 10.8703 | 9.344 | 9.0288 | 8.9173 | 0.043203 | 0.18728 | 12.9237 |  |  | 10.7405 |  |  | 16.9969 | 16.2016 | 15.1876 | 16.4788 | 15.7651 | 14.8896 | 10.644 | 10.761 | 11.4896 | 11.2998 | 8.9396 |  | 10.8493 | 8.5673 | 10.2106 | 9.167 | 11.2539 | 11.7679 |  | 12.4762 |  |  | 11.9878 | 12.6412 | 12.6253 | [6 empty] | 12.6189 |  |  | 11.2513 |  |  | 9.4265 | 10.5403 | 12.4532 | 7.6181 | 9.3755 | 12.9023 | 7.7984 | 9.5972 | 12.6977 | 9.2841 | 10.4909 | 7.7096 | 10.4772 | 8.1717 | 10.1175 | 8.1812 | 9.988 | 13.7079 | 10.8325 | 10.5865 | 11.7774 | 8.203 | 9.9154 | 13.1092 | 8.0593 | 10.4155 | 9.8403 | 9.9474 | 8.3298 | 10.2537 | -0.0042494 | 20.9598 | 0.03386 | 0.047118 | -38.0882 | 3.1217 | -1.15 | 0.38 | -0.29857 | -0.6184 | 0.28143 | -0.41592 | 0.16683 | -0.45913 | 0.71799 | 0.4219 | 0.41119 | 0.42893 | 0.36061 | 0.57625 | 0.43074 | 0.42321
42810.4327 | -635 | 18.6908 | 18.706 | 18.6763 | 18.6963 | 18.0665 | 16.7186 | 14.796 | 16.7889 | 17.2789 | 17.3691 | 17.4033 | 16.9647 | 16.0357 | 14.6628 | 15.1736 | 15.1148 | 15.6451 | 13.4939 | 13.6176 | 14.1951 |  |  |  | 16.6993 | 16.0398 | 15.1705 | 10.3173 | 9.7969 | 9.9648 | 17.4189 | 16.5028 | 15.2971 | 16.9955 | 16.2804 | 15.2958 | 10.9667 | 11.6117 |  | 12.4278 | 10.6822 | 10.6946 | 8.7196 |  | 6.3112 | 6.2645 | 5.7124 | 5.7877 | 5.7839 | 5.8995 | 6.3264 | 5.0667 | 6.346 | 5.1493 | 6.6675 | 8.2514 | 42.1184 | 46.519 | 42.9681 | 15.1265 |  |  | 0.032419 | -0.044597 | 0.01828 | 0.17873 | -0.12403 | -0.13517 | 0.39351 | -0.16116 | -0.35474 | -0.73531 | -0.44023 | 8.881 | 8.8824 | 2.0085 | 15.9956 | 16.842 | 17.3766 | 17.6847 | 17.6505 | 16.6439 | 15.0036 | 16.9309 | 17.2539 | 17.5409 | 17.5846 | 17.3317 | 16.5448 | 14.7902 | 6.5047 | 8.5551 | 5.5331 | 6.1528 | 6.4376 | 6.6269 | 7.548 | 16.0695 | 15.6654 | 15.5065 | 14.4438 | 14.3222 | 14.2707 |  |  |  | 10.8783 | 9.3384 | 9.032 | 8.9499 | 0.022537 | 0.1073 | 12.9197 |  |  | 10.7443 |  |  | 16.9936 | 16.197 | 15.1863 | 16.4859 | 15.7697 | 14.896 | 10.6519 | 10.7645 | 11.4854 | 11.2925 | 8.9988 |  | 10.848 | 8.4419 | 10.2107 | 9.1693 | 11.2627 | 11.6994 |  | 12.4784 |  |  | 11.9596 | 12.6469 | 12.6332 | [6 empty] | 12.6069 |  |  | 11.2554 |  |  | 9.4135 | 10.5383 | 12.4717 | 7.6199 | 9.3707 | 12.8946 | 7.7975 | 9.5878 | 12.6804 | 9.2789 | 10.4978 | 7.714 | 10.4767 | 8.1553 | 10.1164 | 8.1689 | 9.986 | 13.7049 | 10.8252 | 10.5713 | 11.7821 | 8.1984 | 9.9072 | 13.1019 | 8.0485 | 10.4017 | 9.8367 | 9.9396 | 8.32 | 10.2467 | 0.014048 | 20.9588 | 0.032833 | 0.047357 | -38.0831 | 3.1216 | -1.22 | 0.39 | 0.21113 | -0.24601 | 0.1575 | 0.49249 | -0.40999 | -0.428 | 0.73028 | 0.42021 | 0.41468 | 0.42915 | 0.36098 | 0.57587 | 0.43188 | 0.42257
42810.4327 | -634 | 18.7043 | 18.7131 | 18.6869 | 18.7064 | 18.0716 | 16.7265 | 14.802 | 16.7894 | 17.279 | 17.381 | 17.3995 | 16.9693 | 16.0386 | 14.6587 | 15.1712 | 15.117 | 15.6516 | 13.4932 | 13.6193 | 14.2045 |  |  |  | 16.6996 | 16.0427 | 15.1717 | 10.3211 | 9.8025 | 9.9999 | 17.4226 | 16.5036 | 15.2993 | 16.9992 | 16.2861 | 15.2979 | 10.9582 | 11.6165 |  | 12.4223 | 10.6728 | 10.7024 | 8.6968 |  | 6.3187 | 6.2618 | 5.7186 | 5.7882 | 5.7855 | 5.8991 | 6.3064 | 5.1337 | 6.3466 | 5.1452 | 6.6726 | 8.2533 | 42.1213 | 46.5341 | 42.9603 | 15.1589 |  |  | -0.034609 | -0.091253 | 0.17599 | 0.11762 | 0.021848 | -0.012288 | 0.51771 | -0.24527 | -0.29383 | -0.77811 | -0.35002 | 8.8864 | 8.888 | 2.0086 | 15.9969 | 16.8411 | 17.3774 | 17.6873 | 17.6522 | 16.6494 | 15.0065 | 16.925 | 17.2538 | 17.5362 | 17.5871 | 17.3331 | 16.5485 | 14.7895 | 6.481 | 8.5334 | 5.5499 | 6.1723 | 6.4068 | 6.6262 | 7.5634 | 16.0625 | 15.6594 | 15.5098 | 14.447 | 14.3294 | 14.273 |  |  |  | 10.8679 | 9.3343 | 9.0335 | 8.9297 | -0.0009642 | 0.027878 | 12.919 |  |  | 10.7469 |  |  | 16.9921 | 16.1949 | 15.1851 | 16.4873 | 15.7682 | 14.8914 | 10.6565 | 10.7695 | 11.4803 | 11.2857 | 9.035 |  | 10.8528 | 8.3009 | 10.2113 | 9.1587 | 11.2533 | 11.6727 |  | 12.4716 |  |  | 11.9375 | 12.6463 | 12.6287 | [6 empty] | 12.6195 |  |  | 11.2575 |  |  | 9.4025 | 10.5358 | 12.4766 | 7.6392 | 9.3679 | 12.9001 | 7.7924 | 9.5919 | 12.6672 | 9.2772 | 10.5011 | 7.729 | 10.4652 | 8.1511 | 10.1122 | 8.1713 | 9.9881 | 13.6954 | 10.8332 | 10.5683 | 11.7976 | 8.202 | 9.9108 | 13.1072 | 8.0496 | 10.4121 | 9.836 | 9.9321 | 8.3277 | 10.2515 | -0.10093 | 20.9592 | 0.032982 | 0.046749 | -38.179 | 3.1216 | -1.36 | 0.31 | -0.21816 | -0.35189 | 0.48869 | 0.39952 | 0.17207 | -0.12905 | 0.83763 | 0.41936 | 0.41861 | 0.42914 | 0.36352 | 0.5758 | 0.43224 | 0.42279
42810.4327 | -633 | 18.7085 | 18.7121 | 18.6806 | 18.7046 | 18.0699 | 16.7273 | 14.8029 | 16.7881 | 17.2766 | 17.3799 | 17.3997 | 16.9683 | 16.0385 | 14.6559 | 15.1725 | 15.1163 | 15.6489 | 13.4863 | 13.6051 | 14.1935 |  |  |  | 16.695 | 16.0338 | 15.167 | 10.3121 | 9.8005 | 9.9946 | 17.4211 | 16.5026 | 15.2946 | 16.9993 | 16.2775 | 15.2893 | 10.9482 | 11.6063 |  | 12.4151 | 10.6601 | 10.7029 | 8.6797 |  | 6.3111 | 6.2642 | 5.717 | 5.7857 | 5.7749 | 5.8909 | 6.2885 | 5.1527 | 6.3443 | 5.178 | 6.6688 | 8.2522 | 42.1294 | 46.5507 | 42.9493 | 15.1997 |  |  | 0.010735 | -0.36855 | 0.000536 | -0.045998 | -0.10694 | -0.17591 | 0.55319 | -0.24527 | -0.25277 | -0.082834 | -0.58488 | 8.8837 | 8.8845 | 2.0084 | 15.9864 | 16.8398 | 17.3609 | 17.6749 | 17.6525 | 16.6395 | 14.9937 | 16.93 | 17.2544 | 17.5249 | 17.5752 | 17.3194 | 16.5393 | 14.7821 | 6.4538 | 8.4879 | 5.541 | 6.1355 | 6.3749 | 6.6241 | 7.5604 | 16.0628 | 15.6589 | 15.5104 | 14.4445 | 14.3284 | 14.2792 |  |  |  | 10.8675 | 9.3371 | 9.0286 | 8.8991 | 0.11918 | 0.045946 | 12.9264 |  |  | 10.7475 |  |  | 16.9965 | 16.1957 | 15.1851 | 16.4851 | 15.7659 | 14.89 | 10.6625 | 10.7722 | 11.4782 | 11.2781 | 9.0362 |  | 10.8487 | 8.1993 | 10.211 | 9.1636 | 11.2582 | 11.6838 |  | 12.4801 |  |  | 11.9293 | 12.6512 | 12.6346 | [6 empty] | 12.5839 |  |  | 11.2657 |  |  | 9.3996 | 10.5321 | 12.4839 | 7.6412 | 9.3669 | 12.8936 | 7.7849 | 9.5888 | 12.6476 | 9.277 | 10.5095 | 7.722 | 10.4523 | 8.1413 | 10.0977 | 8.1611 | 9.9798 | 13.6902 | 10.8339 | 10.552 | 11.8102 | 8.2035 | 9.9033 | 13.0923 | 8.0588 | 10.4087 | 9.8347 | 9.926 | 8.3378 | 10.2476 | 0.085887 | 20.9587 | 0.033246 | 0.047834 | -38.0986 | 3.1217 | -1.31 | 0.27 | 0.1215 | -0.7072 | 0.02697 | -0.24984 | -0.3807 | -0.48825 | 0.86584 | 0.4192 | 0.42143 | 0.42916 | 0.36631 | 0.57643 | 0.43238 | 0.42363
42810.4327 | -632 | 18.7035 | 18.71 | 18.6742 | 18.7043 | 18.0633 | 16.7253 | 14.7933 | 16.7866 | 17.2728 | 17.373 | 17.3963 | 16.963 | 16.0291 | 14.6586 | 15.1749 | 15.113 | 15.6547 | 13.4956 | 13.6171 | 14.1939 |  |  |  | 16.6962 | 16.0448 | 15.1705 | 10.3215 | 9.8074 | 10.0098 | 17.4225 | 16.5052 | 15.2951 | 16.996 | 16.28 | 15.2926 | 10.9581 | 11.6088 |  | 12.4196 | 10.6609 | 10.7104 | 8.6689 |  | 6.3078 | 6.2583 | 5.7212 | 5.7833 | 5.7809 | 5.8951 | 6.287 | 5.166 | 6.3453 | 5.1845 | 6.6729 | 8.2579 | 42.1364 | 46.5441 | 42.9477 | 15.2306 |  |  | -0.026721 | -0.19376 | 0.15167 | -0.13799 | -0.1168 | 0.001512 | 0.33897 | -0.26235 | -0.61823 | -0.35306 | -0.34346 | 8.8813 | 8.8825 | 2.0085 | 15.9885 | 16.8529 | 17.367 | 17.6824 | 17.6522 | 16.6455 | 15.0044 | 16.923 | 17.2491 | 17.5319 | 17.5818 | 17.3223 | 16.5439 | 14.7938 | 6.4326 | 8.4727 | 5.4919 | 6.0608 | 6.3769 | 6.6253 | 7.5638 | 16.0548 | 15.6598 | 15.5064 | 14.4418 | 14.3229 | 14.2619 |  |  |  | 10.8694 | 9.3333 | 9.0203 | 8.8695 | 0.0586 | 0.14889 | 12.9252 |  |  | 10.7429 |  |  | 16.9962 | 16.1984 | 15.1806 | 16.4847 | 15.7597 | 14.8848 | 10.6604 | 10.7657 | 11.4747 | 11.2743 | 9.0463 |  | 10.8546 | 8.126 | 10.2127 | 9.1676 | 11.2581 | 11.7107 |  | 12.4814 |  |  | 11.9537 | 12.6561 | 12.6574 | [6 empty] | 12.604 |  |  | 11.2685 |  |  | 9.4097 | 10.5369 | 12.4838 | 7.6295 | 9.3733 | 12.898 | 7.7856 | 9.6017 | 12.6475 | 9.2652 | 10.5166 | 7.7127 | 10.4605 | 8.1356 | 10.112 | 8.1695 | 9.9885 | 13.6981 | 10.8424 | 10.555 | 11.8138 | 8.2112 | 9.9128 | 13.0994 | 8.0534 | 10.4077 | 9.8466 | 9.9346 | 8.3436 | 10.275 | 0.014818 | 20.9591 | 0.033315 | 0.04824 | -38.1165 | 3.1217 | -1.21 | 0.35 | -0.19169 | -0.51277 | 0.45367 | -0.43273 | -0.39786 | 0.045267 | 0.67778 | 0.41911 | 0.42352 | 0.42905 | 0.3688 | 0.58229 | 0.43301 | 0.42451
42810.4327 | -631 | 18.7053 | 18.7134 | 18.6799 | 18.7054 | 18.0604 | 16.7265 | 14.7952 | 16.7949 | 17.2789 | 17.377 | 17.3969 | 16.9593 | 16.0327 | 14.6578 | 15.1732 | 15.1237 | 15.6542 | 13.4946 | 13.6137 | 14.2063 |  |  |  | 16.6978 | 16.0384 | 15.1806 | 10.3283 | 9.8179 | 10.0493 | 17.4155 | 16.5044 | 15.294 | 16.9945 | 16.2813 | 15.2922 | 10.956 | 11.6141 |  | 12.413 | 10.6592 | 10.715 | 8.6656 |  | 6.311 | 6.2593 | 5.7207 | 5.7905 | 5.7857 | 5.8917 | 6.3125 | 5.0346 | 6.3555 | 5.1174 | 6.6795 | 8.2581 | 42.1456 | 46.5422 | 42.9536 | 15.2742 |  |  | -0.035265 | -0.038025 | 0.19636 | -0.082798 | 0.026448 | -0.17591 | 0.56174 | -0.14473 | -0.63555 | -0.26872 | -0.38857 | 8.8787 | 8.8798 | 2.0084 | 15.9851 | 16.8472 | 17.367 | 17.6832 | 17.6553 | 16.6388 | 15.0021 | 16.9291 | 17.2558 | 17.5304 | 17.5754 | 17.3243 | 16.5443 | 14.7883 | 6.4327 | 8.4723 | 5.5075 | 6.0787 | 6.3514 | 6.6271 | 7.5725 | 16.0634 | 15.6666 | 15.5138 | 14.4419 | 14.3292 | 14.2637 |  |  |  | 10.8644 | 9.3311 | 9.0171 | 8.8504 | 0.064476 | 0.10975 | 12.9135 |  |  | 10.7398 |  |  | 16.9907 | 16.1998 | 15.1782 | 16.4818 | 15.7631 | 14.8852 | 10.6596 | 10.7623 | 11.4722 | 11.2703 | 9.0582 |  | 10.8583 | 7.9852 | 10.2135 | 9.1666 | 11.2593 | 11.7521 |  | 12.4815 |  |  | 11.9391 | 12.6612 | 12.6653 | [6 empty] | 12.6026 |  |  | 11.2609 |  |  | 9.4069 | 10.5359 | 12.4773 | 7.6119 | 9.3843 | 12.8982 | 7.8028 | 9.605 | 12.6127 | 9.2659 | 10.5193 | 7.7146 | 10.4648 | 8.1289 | 10.1154 | 8.1695 | 9.9903 | 13.6931 | 10.8318 | 10.5452 | 11.818 | 8.2183 | 9.9076 | 13.1001 | 8.0611 | 10.409 | 9.839 | 9.9416 | 8.3428 | 10.2847 | 0.04833 | 20.957 | 0.03347 | 0.049043 | -38.1598 | 3.1217 | -1.18 | 0.39 | -0.22023 | -0.22715 | 0.51619 | -0.33519 | 0.18932 | -0.48825 | 0.8725 | 0.4189 | 0.42746 | 0.42912 | 0.36901 | 0.58156 | 0.43303 | 0.42487
42810.4327 | -630 | 18.6964 | 18.699 | 18.6689 | 18.7013 | 18.0548 | 16.7167 | 14.7857 | 16.785 | 17.2711 | 17.3631 | 17.3947 | 16.954 | 16.0253 | 14.6486 | 15.1717 | 15.1181 | 15.6557 | 13.4983 | 13.6257 | 14.1909 |  |  |  | 16.6962 | 16.0425 | 15.1741 | 10.3307 | 9.82 | 10.0495 | 17.4179 | 16.5095 | 15.2891 | 16.9943 | 16.2791 | 15.2884 | 10.9526 | 11.6269 |  | 12.4133 | 10.6478 | 10.7172 | 8.6601 |  | 6.2999 | 6.2509 | 5.7172 | 5.7929 | 5.7787 | 5.8924 | 6.3335 | 4.8774 | 6.3522 | 5.0826 | 6.6744 | 8.2587 | 42.1482 | 46.526 | 42.9506 | 15.2938 |  |  | 0.061987 | -0.11294 | 0.074132 | -0.036142 | -0.074748 | -0.45124 | 0.38563 | -0.11779 | -0.15547 | -0.4139 | -0.45195 | 8.8828 | 8.884 | 2.0087 | 15.9857 | 16.8464 | 17.3596 | 17.6837 | 17.6428 | 16.6379 | 15.0012 | 16.9249 | 17.2531 | 17.5309 | 17.5784 | 17.3165 | 16.5419 | 14.7799 | 6.4505 | 8.4908 | 5.5217 | 6.0544 | 6.3015 | 6.6274 | 7.5689 | 16.0648 | 15.6653 | 15.5101 | 14.4432 | 14.3266 | 14.2629 |  |  |  | 10.8663 | 9.3309 | 9.0122 | 8.8265 | 0.099323 | 0.13572 | 12.9091 |  |  | 10.7427 |  |  | 16.992 | 16.2023 | 15.1803 | 16.4796 | 15.7708 | 14.892 | 10.6575 | 10.7621 | 11.4666 | 11.2688 | 9.0741 |  | 10.8567 | 7.9173 | 10.214 | 9.1724 | 11.2588 | 11.7687 |  | 12.4766 |  |  | 11.9071 | 12.6783 | 12.677 | [6 empty] | 12.5952 |  |  | 11.2624 |  |  | 9.3965 | 10.5272 | 12.4552 | 7.5869 | 9.3806 | 12.8848 | 7.7927 | 9.5963 | 12.594 | 9.257 | 10.5128 | 7.7 | 10.4637 | 8.1248 | 10.1106 | 8.1673 | 9.9795 | 13.6759 | 10.8224 | 10.5337 | 11.8254 | 8.2264 | 9.8981 | 13.0854 | 8.0581 | 10.4096 | 9.8355 | 9.9324 | 8.3367 | 10.2736 | -0.016961 | 20.9591 | 0.033642 | 0.04858 | -38.1533 | 3.1217 | -1.27 | 0.27 | 0.29199 | -0.39147 | 0.31716 | -0.22146 | -0.31827 | -0.782 | 0.72291 | 0.41841 | 0.42936 | 0.42894 | 0.36706 | 0.57956 | 0.43307 | 0.4256
42810.4328 | -629 | 18.7034 | 18.7198 | 18.6802 | 18.7046 | 18.0619 | 16.722 | 14.7896 | 16.7952 | 17.2842 | 17.376 | 17.4066 | 16.9618 | 16.0359 | 14.646 | 15.1887 | 15.1358 | 15.6626 | 13.5061 | 13.6295 | 14.2005 |  |  |  | 16.7003 | 16.051 | 15.1787 | 10.3388 | 9.8319 | 10.0626 | 17.4223 | 16.51 | 15.2996 | 16.9991 | 16.2806 | 15.2944 | 10.9588 | 11.6535 |  | 12.4109 | 10.65 | 10.7279 | 8.6505 |  | 6.3001 | 6.2488 | 5.7256 | 5.7861 | 5.7765 | 5.8911 | 6.3343 | 4.8627 | 6.3491 | 5.073 | 6.6678 | 8.2631 | 42.1706 | 46.5131 | 42.9595 | 15.3303 |  |  | -0.12069 | 0.018487 | 0.31727 | -0.039426 | -0.047804 | -0.36187 | 0.49602 | -0.3077 | -0.32594 | -0.43047 | -0.40029 | 8.8812 | 8.8822 | 2.0085 | 15.9926 | 16.8492 | 17.3662 | 17.6843 | 17.644 | 16.6422 | 14.9999 | 16.9219 | 17.2526 | 17.5304 | 17.584 | 17.3182 | 16.5373 | 14.7809 | 6.4503 | 8.4823 | 5.5012 | 6.0523 | 6.3694 | 6.6259 | 7.566 | 16.0629 | 15.6637 | 15.5143 | 14.4447 | 14.3307 | 14.2633 |  |  |  | 10.8629 | 9.3304 | 9.0149 | 8.8193 | 0.13599 | 0.22323 | 12.9091 |  |  | 10.7448 |  |  | 16.9922 | 16.1956 | 15.1808 | 16.48 | 15.7697 | 14.8903 | 10.6474 | 10.7579 | 11.4643 | 11.274 | 9.0902 |  | 10.8444 | 7.8956 | 10.2036 | 9.1751 | 11.2585 | 11.7828 |  | 12.4754 |  |  | 11.9103 | 12.6939 | 12.6768 | [6 empty] | 12.6044 |  |  | 11.2796 |  |  | 9.3942 | 10.5147 | 12.4337 | 7.5796 | 9.3848 | 12.8743 | 7.7949 | 9.5955 | 12.574 | 9.2521 | 10.5047 | 7.6916 | 10.4654 | 8.1239 | 10.112 | 8.1586 | 9.9742 | 13.6668 | 10.808 | 10.5247 | 11.8215 | 8.2235 | 9.8931 | 13.0857 | 8.0521 | 10.4074 | 9.8325 | 9.9245 | 8.3305 | 10.2763 | -0.092075 | 20.9588 | 0.033803 | 0.048471 | -38.163 | 3.1217 | -0.8 | 0.36 | -0.40743 | 0.15838 | 0.65613 | -0.2313 | -0.25453 | -0.70029 | 0.81988 | 0.41755 | 0.42962 | 0.42886 | 0.36691 | 0.58152 | 0.43354 | 0.42569
42810.4328 | -628 | 18.7011 | 18.7112 | 18.6769 | 18.7042 | 18.0618 | 16.7227 | 14.7961 | 16.798 | 17.2731 | 17.3733 | 17.3873 | 16.9585 | 16.029 | 14.6437 | 15.1771 | 15.1308 | 15.654 | 13.4985 | 13.6113 | 14.1949 |  |  |  | 16.697 | 16.0382 | 15.1702 | 10.3286 | 9.8232 | 10.0285 | 17.4067 | 16.4913 | 15.2918 | 16.9858 | 16.2687 | 15.2906 | 10.9433 | 11.6701 |  | 12.3964 | 10.6316 | 10.7286 | 8.6158 |  | 6.3108 | 6.2632 | 5.7385 | 5.7985 | 5.7949 | 5.8938 | 6.322 | 4.8819 | 6.356 | 5.1524 | 6.6846 | 8.2597 | 42.1904 | 46.4996 | 42.9672 | 15.3555 |  |  | 0.038987 | -0.047225 | -0.04152 | -0.11237 | -0.17003 | -0.38553 | 0.50456 | 0.06686 | -0.23817 | -0.46635 | -0.29041 | 8.875 | 8.876 | 2.0088 | 15.991 | 16.8519 | 17.3718 | 17.6828 | 17.6496 | 16.6402 | 14.9984 | 16.9239 | 17.2459 | 17.5304 | 17.5762 | 17.3203 | 16.5378 | 14.7819 | 6.4914 | 8.4898 | 5.4829 | 6.027 | 6.3483 | 6.6328 | 7.572 | 16.059 | 15.6623 | 15.5104 | 14.4402 | 14.3268 | 14.2597 |  |  |  | 10.8578 | 9.3161 | 9.0131 | 8.8139 | 0.1366 | 0.092431 | 12.9059 |  |  | 10.7452 |  |  | 16.9925 | 16.1979 | 15.1829 | 16.484 | 15.7705 | 14.887 | 10.6205 | 10.7593 | 11.4639 | 11.2798 | 9.1249 |  | 10.8401 | 7.9003 | 10.2001 | 9.1797 | 11.2573 | 11.7908 |  | 12.4676 |  |  | 11.9387 | 12.7104 | 12.6788 | [6 empty] | 12.6161 |  |  | 11.2996 |  |  | 9.3926 | 10.5084 | 12.4285 | 7.5991 | 9.4 | 12.8733 | 7.7883 | 9.579 | 12.5632 | 9.249 | 10.5014 | 7.6967 | 10.4671 | 8.1266 | 10.1244 | 8.1582 | 9.9723 | 13.6572 | 10.8012 | 10.5248 | 11.8176 | 8.2258 | 9.8982 | 13.0763 | 8.0508 | 10.4105 | 9.8194 | 9.9092 | 8.329 | 10.2853 | -0.026591 | 20.9588 | 0.033545 | 0.048138 | -38.1296 | 3.1217 | -0.68 | 0.29 | 0.23156 | -0.25315 | -0.23737 | -0.39049 | -0.48002 | -0.72282 | 0.82692 | 0.41645 | 0.42937 | 0.42869 | 0.36314 | 0.58424 | 0.43399 | 0.42567
42810.4328 | -627 | 18.7036 | 18.7093 | 18.6817 | 18.7003 | 18.0659 | 16.7246 | 14.8001 | 16.7939 | 17.2805 | 17.3742 | 17.4024 | 16.9721 | 16.0349 | 14.6521 | 15.1741 | 15.1232 | 15.651 | 13.4968 | 13.6203 | 14.1941 |  |  |  | 16.6999 | 16.0424 | 15.1676 | 10.3322 | 9.8213 | 9.9863 | 17.4181 | 16.502 | 15.298 | 16.9952 | 16.2841 | 15.2975 | 10.953 | 11.7029 |  | 12.4032 | 10.6348 | 10.7401 | 8.6149 |  | 6.3037 | 6.2548 | 5.7325 | 5.7894 | 5.7876 | 5.8936 | 6.2972 | 4.8715 | 6.3576 | 5.1933 | 6.666 | 8.2635 | 42.2026 | 46.4955 | 42.9732 | 15.3856 |  |  | 0.14215 | -0.046569 | 0.31792 | 0.065054 | -0.10366 | -0.193 | 0.58408 | -0.004764 | -0.63049 | -0.56453 | -0.36572 | 8.8769 | 8.8779 | 2.0082 | 15.9961 | 16.8422 | 17.3697 | 17.687 | 17.6446 | 16.6453 | 14.9959 | 16.9266 | 17.2517 | 17.5319 | 17.5805 | 17.3261 | 16.5471 | 14.7814 | 6.5357 | 8.5183 | 5.4688 | 5.9791 | 6.2996 | 6.6264 | 7.5784 | 16.0657 | 15.6754 | 15.516 | 14.4545 | 14.3307 | 14.2794 |  |  |  | 10.8745 | 9.3268 | 9.0191 | 8.8565 | 0.098512 | 0.057049 | 12.91 |  |  | 10.75 |  |  | 16.9993 | 16.2015 | 15.1871 | 16.4852 | 15.7714 | 14.887 | 10.585 | 10.7571 | 11.4688 | 11.2882 | 9.1417 |  | 10.8445 | 7.9413 | 10.1987 | 9.1826 | 11.2532 | 11.806 |  | 12.4665 |  |  | 11.9565 | 12.7038 | 12.6767 | [6 empty] | 12.6206 |  |  | 11.2932 |  |  | 9.3796 | 10.5066 | 12.4234 | 7.6063 | 9.4109 | 12.871 | 7.795 | 9.5804 | 12.5713 | 9.2469 | 10.5012 | 7.6981 | 10.4747 | 8.1215 | 10.1281 | 8.171 | 9.9797 | 13.6688 | 10.7992 | 10.5225 | 11.823 | 8.2308 | 9.9119 | 13.101 | 8.0772 | 10.4167 | 9.8231 | 9.9255 | 8.3429 | 10.3041 | -0.15294 | 20.959 | 0.032471 | 0.047719 | -38.0876 | 3.1217 | -0.72 | 0.28 | 0.44213 | -0.25138 | 0.65682 | 0.29711 | -0.37481 | -0.51142 | 0.88969 | 0.41613 | 0.42819 | 0.42847 | 0.35747 | 0.58656 | 0.43434 | 0.42504
42810.4328 | -626 | 18.7034 | 18.7077 | 18.6797 | 18.6954 | 18.0624 | 16.7206 | 14.7973 | 16.7888 | 17.2813 | 17.3717 | 17.394 | 16.9641 | 16.0332 | 14.6498 | 15.1807 | 15.135 | 15.6577 | 13.4988 | 13.6218 | 14.1992 |  |  |  | 16.7023 | 16.0499 | 15.1699 | 10.3399 | 9.8254 | 9.9673 | 17.4232 | 16.5086 | 15.3017 | 16.9969 | 16.2811 | 15.3014 | 10.9525 | 11.7281 |  | 12.4156 | 10.642 | 10.7385 | 8.6187 |  | 6.3045 | 6.2558 | 5.7319 | 5.7918 | 5.7868 | 5.8936 | 6.2894 | 4.8447 | 6.3575 | 5.1528 | 6.6692 | 8.2642 | 42.209 | 46.5107 | 42.9732 | 15.4056 |  |  | -0.045777 | -0.1425 | 0.16219 | 0.07097 | 0.025792 | 0.02254 | 0.5775 | -0.039592 | -0.76885 | -0.006047 | -0.35836 | 8.8744 | 8.8758 | 2.0086 | 15.9852 | 16.84 | 17.3619 | 17.6786 | 17.6341 | 16.646 | 14.9926 | 16.9193 | 17.238 | 17.5224 | 17.5694 | 17.3215 | 16.5331 | 14.7761 | 6.5309 | 8.5078 | 5.4867 | 5.9375 | 6.2591 | 6.6353 | 7.5851 | 16.0638 | 15.6683 | 15.517 | 14.4478 | 14.3304 | 14.2704 |  |  |  | 10.8681 | 9.3224 | 9.0103 | 8.8678 | -0.0021798 | 0.047075 | 12.9106 |  |  | 10.7488 |  |  | 16.9987 | 16.1996 | 15.1858 | 16.4815 | 15.7648 | 14.8822 | 10.5566 | 10.7439 | 11.4687 | 11.2934 | 9.1427 |  | 10.8474 | 7.9377 | 10.2048 | 9.1778 | 11.257 | 11.8188 |  | 12.4686 |  |  | 11.9723 | 12.6995 | 12.6785 | [6 empty] | 12.6251 |  |  | 11.2728 |  |  | 9.3758 | 10.4998 | 12.4104 | 7.607 | 9.4173 | 12.8689 | 7.8022 | 9.5768 | 12.5757 | 9.246 | 10.4966 | 7.6987 | 10.4787 | 8.119 | 10.1358 | 8.1746 | 9.9668 | 13.658 | 10.7893 | 10.5095 | 11.8142 | 8.2251 | 9.9064 | 13.1012 | 8.0669 | 10.4108 | 9.8161 | 9.9237 | 8.3487 | 10.3092 | -0.10151 | 20.9586 | 0.03157 | 0.04693 | -38.129 | 3.1217 | -0.83 | 0.32 | -0.25088 | -0.43974 | 0.46913 | 0.31033 | 0.18696 | 0.17478 | 0.88467 | 0.4162 | 0.42849 | 0.42873 | 0.35904 | 0.58534 | 0.43422 | 0.42451
42810.4328 | -625 | 18.71 | 18.7151 | 18.6788 | 18.7089 | 18.0681 | 16.7285 | 14.8023 | 16.79 | 17.2834 | 17.3771 | 17.3993 | 16.9692 | 16.0295 | 14.652 | 15.1787 | 15.1327 | 15.6618 | 13.5061 | 13.6198 | 14.1991 |  |  |  | 16.6994 | 16.0459 | 15.1674 | 10.3296 | 9.8291 | 9.9474 | 17.4191 | 16.5084 | 15.2961 | 16.9927 | 16.2736 | 15.2926 | 10.9479 | 11.7562 |  | 12.4068 | 10.6348 | 10.7334 | 8.6128 |  | 6.3088 | 6.2638 | 5.7412 | 5.7998 | 5.7989 | 5.8988 | 6.3002 | 4.881 | 6.3586 | 5.0277 | 6.6703 | 8.2633 | 42.1957 | 46.5198 | 42.9839 | 15.4189 |  |  | 0.10996 | -0.15039 | 0.06822 | -0.28913 | 0.016592 | -0.35727 | 0.56042 | 0.29882 | -0.37459 | -0.21899 | -0.23795 | 8.8726 | 8.874 | 2.0084 | 15.9936 | 16.8523 | 17.3611 | 17.6764 | 17.6443 | 16.6436 | 14.9932 | 16.9182 | 17.2404 | 17.5237 | 17.5839 | 17.318 | 16.54 | 14.7807 | 6.4919 | 8.497 | 5.5076 | 5.9024 | 6.1873 | 6.6356 | 7.5853 | 16.0543 | 15.6658 | 15.5116 | 14.4433 | 14.3304 | 14.2666 |  |  |  | 10.861 | 9.3082 | 9.0038 | 8.8483 | 0.10925 | -0.031028 | 12.9143 |  |  | 10.7463 |  |  | 16.994 | 16.2052 | 15.1889 | 16.4852 | 15.7672 | 14.8875 | 10.5456 | 10.748 | 11.4758 | 11.3074 | 9.1182 |  | 10.8343 | 7.917 | 10.1947 | 9.1717 | 11.247 | 11.8196 |  | 12.4616 |  |  | 11.9878 | 12.6793 | 12.6829 | [6 empty] | 12.6281 |  |  | 11.2781 |  |  | 9.3725 | 10.4925 | 12.4035 | 7.6082 | 9.4164 | 12.8622 | 7.8059 | 9.5806 | 12.5871 | 9.2466 | 10.49 | 7.7057 | 10.486 | 8.1245 | 10.1423 | 8.1739 | 9.9584 | 13.6462 | 10.7829 | 10.5012 | 11.8137 | 8.2296 | 9.9057 | 13.0952 | 8.04 | 10.4045 | 9.8212 | 9.9179 | 8.3488 | 10.3066 | -0.081097 | 20.9586 | 0.03242 | 0.047451 | -38.2086 | 3.1217 | -0.59 | 0.36 | 0.38882 | -0.45176 | 0.30426 | -0.62638 | 0.14995 | -0.69584 | 0.87149 | 0.41644 | 0.42873 | 0.42857 | 0.36341 | 0.58304 | 0.43423 | 0.42482
42810.4328 | -624 | 18.7121 | 18.7109 | 18.6804 | 18.7056 | 18.064 | 16.7265 | 14.7981 | 16.7893 | 17.2818 | 17.3783 | 17.3966 | 16.9675 | 16.0285 | 14.644 | 15.174 | 15.1198 | 15.6564 | 13.5056 | 13.6141 | 14.1969 |  |  |  | 16.6971 | 16.0437 | 15.1685 | 10.3263 | 9.8265 | 9.9178 | 17.4136 | 16.512 | 15.2928 | 16.9972 | 16.2782 | 15.2962 | 10.9577 | 11.7962 |  | 12.4023 | 10.633 | 10.7295 | 8.6032 |  | 6.3115 | 6.2631 | 5.7467 | 5.8022 | 5.7925 | 5.895 | 6.2902 | 4.8805 | 6.3489 | 4.9363 | 6.6666 | 8.2603 | 42.1917 | 46.5387 | 42.9825 | 15.444 |  |  | -0.11478 | -0.18325 | -0.000776 | 0.059142 | -0.06226 | -0.16671 | 0.36526 | 0.095776 | -0.40359 | -0.6986 | -0.018786 | 8.8689 | 8.8702 | 2.0086 | 15.9938 | 16.8455 | 17.3669 | 17.683 | 17.6509 | 16.6464 | 15.0024 | 16.9191 | 17.2454 | 17.5296 | 17.5774 | 17.3237 | 16.5439 | 14.7775 | 6.4844 | 8.5232 | 5.514 | 5.909 | 6.1503 | 6.6386 | 7.5901 | 16.0617 | 15.6668 | 15.5128 | 14.4483 | 14.3323 | 14.2725 |  |  |  | 10.8645 | 9.306 | 9.0112 | 8.8447 | 0.1133 | -0.071303 | 12.9175 |  |  | 10.7379 |  |  | 16.9911 | 16.2024 | 15.1853 | 16.4852 | 15.7652 | 14.8827 | 10.5429 | 10.7532 | 11.4764 | 11.3113 | 9.085 |  | 10.831 | 7.9554 | 10.1916 | 9.1853 | 11.2565 | 11.8335 |  | 12.462 |  |  | 12.003 | 12.6691 | 12.692 | [6 empty] | 12.6317 |  |  | 11.2898 |  |  | 9.3618 | 10.4846 | 12.3988 | 7.6111 | 9.4156 | 12.8533 | 7.8032 | 9.5749 | 12.5983 | 9.2417 | 10.4963 | 7.7116 | 10.4851 | 8.1255 | 10.1453 | 8.1517 | 9.938 | 13.6346 | 10.7745 | 10.4895 | 11.8068 | 8.228 | 9.8986 | 13.0916 | 8.0194 | 10.3995 | 9.8134 | 9.9157 | 8.3423 | 10.3026 | -0.055866 | 20.9578 | 0.033441 | 0.048008 | -38.192 | 3.1217 | -0.45 | 0.37 | -0.39723 | -0.49867 | -0.03245 | 0.28329 | -0.29047 | -0.47532 | 0.70356 | 0.41726 | 0.42757 | 0.4285 | 0.36459 | 0.58288 | 0.43482 | 0.42504
42810.4328 | -623 | 18.7143 | 18.7119 | 18.6778 | 18.7081 | 18.0626 | 16.733 | 14.8038 | 16.7856 | 17.2763 | 17.375 | 17.3975 | 16.9696 | 16.0354 | 14.651 | 15.1795 | 15.1277 | 15.6539 | 13.4993 | 13.614 | 14.195 |  |  |  | 16.6927 | 16.045 | 15.1708 | 10.3188 | 9.8253 | 9.886 | 17.4145 | 16.5025 | 15.2931 | 16.9941 | 16.2792 | 15.292 | 10.9536 | 11.8255 |  | 12.4044 | 10.6343 | 10.7236 | 8.5854 |  | 6.3029 | 6.2712 | 5.7436 | 5.8078 | 5.7988 | 5.896 | 6.2908 | 4.8176 | 6.3444 | 4.9057 | 6.6672 | 8.2575 | 42.1847 | 46.5564 | 42.9742 | 15.4564 |  |  | -0.010293 | -0.17011 | 0.14247 | 0.055198 | 0.11319 | -0.10428 | 0.009756 | 0.24757 | -0.26756 | -0.54104 | -0.39632 | 8.8731 | 8.874 | 2.0085 | 15.9954 | 16.8493 | 17.3657 | 17.6857 | 17.6507 | 16.6463 | 15.0014 | 16.9249 | 17.2477 | 17.5365 | 17.5785 | 17.3251 | 16.5517 | 14.7852 | 6.5017 | 8.5285 | 5.5418 | 5.9191 | 6.1018 | 6.6359 | 7.5924 | 16.0517 | 15.6562 | 15.5202 | 14.431 | 14.3232 | 14.2729 |  |  |  | 10.8573 | 9.3071 | 8.9963 | 8.8374 | 0.1753 | 0.022985 | 12.9179 |  |  | 10.7391 |  |  | 16.9951 | 16.1986 | 15.1841 | 16.4837 | 15.7666 | 14.886 | 10.5507 | 10.7498 | 11.4791 | 11.3174 | 9.0575 |  | 10.8347 | 8.0172 | 10.1943 | 9.1864 | 11.2537 | 11.8611 |  | 12.4654 |  |  | 12.0085 | 12.6725 | 12.6996 | [6 empty] | 12.6421 |  |  | 11.2996 |  |  | 9.3593 | 10.4799 | 12.3954 | 7.597 | 9.4102 | 12.8424 | 7.801 | 9.5781 | 12.6041 | 9.2372 | 10.4942 | 7.694 | 10.4701 | 8.1397 | 10.1493 | 8.1441 | 9.9144 | 13.6359 | 10.7722 | 10.4922 | 11.8001 | 8.238 | 9.9054 | 13.0962 | 8.0116 | 10.3957 | 9.8148 | 9.9253 | 8.3448 | 10.3084 | -0.17894 | 20.9574 | 0.033768 | 0.048551 | -38.1356 | 3.1217 | -0.38 | 0.43 | -0.11895 | -0.48046 | 0.43971 | 0.27369 | 0.39166 | -0.37594 | 0.11498 | 0.41814 | 0.42594 | 0.42838 | 0.36236 | 0.58006 | 0.43518 | 0.425
42810.4328 | -622 | 18.7098 | 18.7119 | 18.6778 | 18.7098 | 18.0634 | 16.7293 | 14.7955 | 16.7973 | 17.274 | 17.3733 | 17.3966 | 16.965 | 16.0436 | 14.651 | 15.1776 | 15.1236 | 15.6566 | 13.5013 | 13.618 | 14.1928 |  |  |  | 16.6999 | 16.0406 | 15.166 | 10.3175 | 9.8287 | 9.8723 | 17.4169 | 16.5039 | 15.2944 | 17.0004 | 16.2811 | 15.3018 | 10.96 | 11.8497 |  | 12.4052 | 10.6259 | 10.7313 | 8.59 |  | 6.3144 | 6.2758 | 5.755 | 5.8163 | 5.8029 | 5.8937 | 6.3003 | 4.7866 | 6.3509 | 4.8735 | 6.6637 | 8.2585 | 42.1808 | 46.5869 | 42.9741 | 15.4723 |  |  | 0.13099 | -0.068253 | 0.074792 | -0.057826 | 0.10136 | -0.54455 | 0.40468 | 0.26465 | -0.14652 | -0.24522 | -0.2916 | 8.8844 | 8.8854 | 2.0087 | 15.981 | 16.8405 | 17.3569 | 17.6785 | 17.6419 | 16.6421 | 14.9955 | 16.9165 | 17.2403 | 17.5284 | 17.5665 | 17.3214 | 16.5397 | 14.7782 | 6.5286 | 8.5591 | 5.646 | 5.8718 | 6.0919 | 6.6382 | 7.5915 | 16.0667 | 15.6685 | 15.5161 | 14.4422 | 14.3341 | 14.2797 |  |  |  | 10.8571 | 9.3252 | 9.0044 | 8.8371 | 0.086559 | 0.20592 | 12.9234 |  |  | 10.7358 |  |  | 17.0008 | 16.2049 | 15.1922 | 16.4841 | 15.7753 | 14.8967 | 10.5622 | 10.7557 | 11.4903 | 11.3327 | 9.0647 |  | 10.8464 | 8.0902 | 10.2005 | 9.1992 | 11.2625 | 11.9092 |  | 12.4714 |  |  | 12.0038 | 12.6527 | 12.6962 | [6 empty] | 12.6339 |  |  | 11.2957 |  |  | 9.3608 | 10.478 | 12.3905 | 7.5878 | 9.4051 | 12.8315 | 7.7899 | 9.577 | 12.6064 | 9.2325 | 10.4908 | 7.6581 | 10.4529 | 8.1498 | 10.1569 | 8.1406 | 9.8904 | 13.6273 | 10.7803 | 10.4902 | 11.7963 | 8.2465 | 9.9004 | 13.0948 | 8.0104 | 10.3866 | 9.8147 | 9.9325 | 8.3512 | 10.3106 | -0.0576 | 20.9571 | 0.033476 | 0.048493 | -38.0526 | 3.1217 | -0.39 | 0.26 | 0.42432 | -0.30434 | 0.31859 | -0.28013 | 0.37063 | -0.85906 | 0.74056 | 0.41833 | 0.42411 | 0.42832 | 0.35963 | 0.56838 | 0.43526 | 0.425
42810.4328 | -621 | 18.7052 | 18.7143 | 18.6822 | 18.7019 | 18.0662 | 16.7256 | 14.7926 | 16.7965 | 17.283 | 17.3784 | 17.3989 | 16.9618 | 16.0248 | 14.6458 | 15.1637 | 15.1139 | 15.6477 | 13.4936 | 13.6127 | 14.1851 |  |  |  | 16.6916 | 16.0332 | 15.1628 | 10.3051 | 9.819 | 9.8503 | 17.4034 | 16.4946 | 15.2931 | 16.99 | 16.2733 | 15.2876 | 10.9525 | 11.8462 |  | 12.4035 | 10.6215 | 10.7142 | 8.6087 |  | 6.3171 | 6.2776 | 5.7552 | 5.8179 | 5.8021 | 5.8876 | 6.2666 | 4.7971 | 6.3494 | 4.8374 | 6.6663 | 8.2589 | 42.1884 | 46.6139 | 42.9701 | 15.4859 |  |  | -0.054321 | -0.14513 | 0.037992 | 0.068998 | 0.19796 | -0.17197 | 0.48748 | 0.074092 | -1.1637 | -0.8977 | -0.16801 | 8.8828 | 8.8839 | 2.0084 | 15.9779 | 16.8425 | 17.3652 | 17.6891 | 17.6515 | 16.6428 | 15.0015 | 16.9248 | 17.2507 | 17.5332 | 17.5771 | 17.3275 | 16.5398 | 14.7822 | 6.5367 | 8.5627 | 5.8763 | 5.8505 | 6.0605 | 6.6443 | 7.5987 | 16.0573 | 15.6749 | 15.5179 | 14.4535 | 14.3383 | 14.2741 |  |  |  | 10.8631 | 9.3206 | 9.0055 | 8.8304 | 0.019701 | 0.16432 | 12.9194 |  |  | 10.7192 |  |  | 16.9963 | 16.1991 | 15.1867 | 16.4801 | 15.772 | 14.8912 | 10.5626 | 10.7489 | 11.4881 | 11.3399 | 9.0413 |  | 10.8363 | 8.086 | 10.1816 | 9.1936 | 11.2477 | 11.9129 |  | 12.4494 |  |  | 11.9975 | 12.6236 | 12.682 | [6 empty] | 12.6288 |  |  | 11.3069 |  |  | 9.3505 | 10.4655 | 12.3684 | 7.5772 | 9.3909 | 12.8243 | 7.7898 | 9.5751 | 12.6087 | 9.2269 | 10.4907 | 7.6326 | 10.425 | 8.1571 | 10.1543 | 8.1296 | 9.8715 | 13.613 | 10.7677 | 10.4784 | 11.7806 | 8.2437 | 9.8887 | 13.092 | 8.0049 | 10.3838 | 9.8064 | 9.9258 | 8.3418 | 10.3014 | 0.13288 | 20.957 | 0.034021 | 0.049115 | -38.0932 | 3.1217 | -0.82 | 0.23 | -0.27324 | -0.4438 | 0.22706 | 0.306 | 0.51794 | -0.48275 | 0.81279 | 0.41865 | 0.42361 | 0.42798 | 0.35945 | 0.54363 | 0.43449 | 0.42539
42810.4329 | -620 | 18.7039 | 18.7172 | 18.6801 | 18.7002 | 18.0638 | 16.7249 | 14.7995 | 16.7914 | 17.2793 | 17.3816 | 17.399 | 16.9633 | 16.031 | 14.646 | 15.1732 | 15.1211 | 15.6517 | 13.4994 | 13.6128 | 14.1939 |  |  |  | 16.7014 | 16.0379 | 15.165 | 10.3088 | 9.8187 | 9.8552 | 17.4046 | 16.5 | 15.2943 | 16.9869 | 16.2764 | 15.2914 | 10.9558 | 11.8465 |  | 12.3999 | 10.6232 | 10.7161 | 8.6323 |  | 6.3142 | 6.2729 | 5.7529 | 5.8176 | 5.7963 | 5.8838 | 6.2347 | 4.8103 | 6.3454 | 4.7682 | 6.6574 | 8.2545 | 42.1946 | 46.6337 | 42.967 | 15.4914 |  |  | -0.15092 | 0.10128 | 0.14576 | 0.23328 | -0.069492 | -0.35464 | 0.61759 | -0.088876 | -0.5688 | 0.95442 | -0.3218 | 8.8807 | 8.8818 | 2.0084 | 15.9815 | 16.8417 | 17.3641 | 17.6881 | 17.6422 | 16.6389 | 15.0025 | 16.921 | 17.2485 | 17.5325 | 17.5798 | 17.3232 | 16.5371 | 14.7764 | 6.5158 | 8.5711 | 6.0429 | 5.8542 | 6.0182 | 6.6406 | 7.5975 | 16.059 | 15.6692 | 15.5125 | 14.4487 | 14.329 | 14.2696 |  |  |  | 10.8551 | 9.3149 | 8.9998 | 8.8174 | -0.067012 | 0.17298 | 12.9121 |  |  | 10.7181 |  |  | 16.9996 | 16.1997 | 15.1788 | 16.4863 | 15.7698 | 14.891 | 10.5711 | 10.7418 | 11.4936 | 11.3419 | 9.0332 |  | 10.8398 | 8.0601 | 10.1819 | 9.1994 | 11.2459 | 11.9253 |  | 12.4498 |  |  | 11.995 | 12.626 | 12.6769 | [6 empty] | 12.6236 |  |  | 11.3183 |  |  | 9.3449 | 10.4591 | 12.3608 | 7.5709 | 9.3634 | 12.8075 | 7.7842 | 9.5744 | 12.6123 | 9.2287 | 10.4813 | 7.612 | 10.4092 | 8.1603 | 10.1452 | 8.1359 | 9.8696 | 13.61 | 10.768 | 10.4717 | 11.7678 | 8.236 | 9.8836 | 13.1029 | 7.9982 | 10.3939 | 9.8104 | 9.935 | 8.3528 | 10.3031 | 0.032537 | 20.9567 | 0.03308 | 0.048131 | -38.1659 | 3.1217 | -0.97 | 0.26 | -0.45544 | 0.37074 | 0.44475 | 0.56265 | -0.30688 | -0.69325 | 0.91484 | 0.41898 | 0.42434 | 0.42776 | 0.36134 | 0.52498 | 0.43395 | 0.42549
42810.4329 | -619 | 18.6961 | 18.7124 | 18.6742 | 18.7005 | 18.0555 | 16.7192 | 14.7948 | 16.783 | 17.268 | 17.3803 | 17.3894 | 16.9577 | 16.0203 | 14.6371 | 15.1664 | 15.1194 | 15.6449 | 13.494 | 13.6118 | 14.1947 |  |  |  | 16.6873 | 16.036 | 15.1565 | 10.2997 | 9.8014 | 9.8732 | 17.4105 | 16.5031 | 15.2965 | 16.993 | 16.274 | 15.2926 | 10.9517 | 11.8137 |  | 12.4027 | 10.616 | 10.7059 | 8.6536 |  | 6.3257 | 6.2845 | 5.7667 | 5.8206 | 5.7951 | 5.8888 | 6.2116 | 4.8233 | 6.352 | 4.7339 | 6.6606 | 8.2538 | 42.2052 | 46.6388 | 42.9628 | 15.4938 |  |  | -0.047093 | -0.071537 | 0.02748 | -0.28782 | -0.068176 | -0.40524 | 0.50851 | -0.21504 | -0.40222 | -0.125 | -0.20993 | 8.8819 | 8.8831 | 2.0085 | 15.9821 | 16.8428 | 17.3577 | 17.6743 | 17.6409 | 16.639 | 15.009 | 16.9241 | 17.2398 | 17.5269 | 17.5707 | 17.3194 | 16.5344 | 14.7692 | 6.4468 | 8.5256 | 6.1714 | 5.9331 | 5.97 | 6.6426 | 7.6001 | 16.0572 | 15.6631 | 15.5051 | 14.4461 | 14.3289 | 14.2651 |  |  |  | 10.8444 | 9.3136 | 8.9931 | 8.8057 | -0.097604 | -0.13077 | 12.9149 |  |  | 10.718 |  |  | 17.0032 | 16.2057 | 15.1824 | 16.4929 | 15.7764 | 14.8979 | 10.5792 | 10.738 | 11.5063 | 11.3609 | 9.0363 |  | 10.8361 | 7.9932 | 10.1895 | 9.2136 | 11.2521 | 11.9339 |  | 12.4528 |  |  | 11.9553 | 12.6374 | 12.681 | [6 empty] | 12.6081 |  |  | 11.3183 |  |  | 9.3262 | 10.451 | 12.3619 | 7.5671 | 9.3334 | 12.7955 | 7.7824 | 9.5675 | 12.6092 | 9.2182 | 10.4804 | 7.6203 | 10.4023 | 8.1721 | 10.1448 | 8.1364 | 9.869 | 13.6144 | 10.7613 | 10.465 | 11.7528 | 8.2306 | 9.8923 | 13.0907 | 7.999 | 10.3991 | 9.8148 | 9.93 | 8.3633 | 10.3098 | -0.14851 | 20.9581 | 0.032075 | 0.047784 | -38.1708 | 3.1218 | -0.98 | 0.28 | -0.25442 | -0.31158 | 0.19311 | -0.62498 | -0.30396 | -0.74107 | 0.83013 | 0.41878 | 0.42644 | 0.42757 | 0.36923 | 0.511 | 0.43322 | 0.42546
42810.4329 | -618 | 18.7036 | 18.7166 | 18.6819 | 18.7045 | 18.0619 | 16.7229 | 14.7958 | 16.7911 | 17.2756 | 17.3779 | 17.3953 | 16.9587 | 16.0227 | 14.6445 | 15.1785 | 15.1289 | 15.6522 | 13.5049 | 13.6258 | 14.1999 |  |  |  | 16.695 | 16.0462 | 15.1683 | 10.3058 | 9.8181 | 9.8803 | 17.4131 | 16.5019 | 15.2992 | 16.993 | 16.2791 | 15.2943 | 10.95 | 11.7794 |  | 12.3991 | 10.6184 | 10.7095 | 8.6524 |  | 6.3207 | 6.2752 | 5.7684 | 5.829 | 5.7951 | 5.888 | 6.1977 | 4.9083 | 6.3524 | 4.7116 | 6.6561 | 8.2622 | 42.2097 | 46.6368 | 42.9637 | 15.5078 |  |  | 0.075131 | -0.091253 | 0.080704 | -0.040742 | 0.05536 | -0.51761 | 0.57948 | -0.12896 | -0.16306 | -0.33795 | -0.16006 | 8.8867 | 8.8879 | 2.0086 | 15.9853 | 16.8484 | 17.3648 | 17.6951 | 17.6516 | 16.6379 | 15.0013 | 16.9154 | 17.2449 | 17.5356 | 17.5721 | 17.3238 | 16.5382 | 14.7708 | 6.4194 | 8.4833 | 6.159 | 6.0685 | 5.9576 | 6.6422 | 7.6015 | 16.0539 | 15.6645 | 15.5143 | 14.4467 | 14.3247 | 14.2675 |  |  |  | 10.8452 | 9.3063 | 9.003 | 8.7822 | 0.1052 | -0.036674 | 12.9161 |  |  | 10.7144 |  |  | 17.001 | 16.2016 | 15.1862 | 16.4837 | 15.7733 | 14.8933 | 10.5789 | 10.7355 | 11.506 | 11.3716 | 9.0605 |  | 10.8422 | 7.911 | 10.1916 | 9.2372 | 11.2492 | 11.9636 |  | 12.4565 |  |  | 11.943 | 12.6627 | 12.677 | [6 empty] | 12.577 |  |  | 11.3095 |  |  | 9.3299 | 10.4522 | 12.3665 | 7.5588 | 9.3262 | 12.7973 | 7.7783 | 9.5667 | 12.6138 | 9.2176 | 10.4778 | 7.6226 | 10.4022 | 8.1767 | 10.1443 | 8.1088 | 9.8665 | 13.6075 | 10.7518 | 10.4455 | 11.7397 | 8.2176 | 9.8832 | 13.0882 | 7.9926 | 10.3961 | 9.802 | 9.9286 | 8.3538 | 10.3111 | -0.081097 | 20.9577 | 0.033217 | 0.047661 | -38.1634 | 3.1217 | -1.19 | 0.23 | 0.32136 | -0.3519 | 0.33094 | -0.23514 | 0.2739 | -0.83753 | 0.88617 | 0.41831 | 0.4288 | 0.42682 | 0.37223 | 0.51254 | 0.4332 | 0.42614
42810.4329 | -617 | 18.7071 | 18.7088 | 18.678 | 18.7016 | 18.0575 | 16.7214 | 14.7894 | 16.7858 | 17.2756 | 17.3786 | 17.3924 | 16.9587 | 16.0248 | 14.6401 | 15.1622 | 15.1129 | 15.6451 | 13.4905 | 13.6178 | 14.1923 |  |  |  | 16.6886 | 16.0342 | 15.1591 | 10.3046 | 9.8094 | 9.8865 | 17.404 | 16.5031 | 15.295 | 16.9959 | 16.2772 | 15.2922 | 10.951 | 11.782 |  | 12.398 | 10.6146 | 10.7049 | 8.6675 |  | 6.326 | 6.2858 | 5.7768 | 5.8382 | 5.81 | 5.8821 | 6.1853 | 5.0016 | 6.3559 | 4.7277 | 6.6602 | 8.2541 | 42.2045 | 46.6058 | 42.9527 | 15.5151 |  |  | -0.025409 | -0.20691 | 0.012364 | 0.13142 | -0.042548 | -0.48278 | 0.4566 | -0.21307 | 0.62274 | -0.46991 | -0.23736 | 8.8802 | 8.8815 | 2.0087 | 15.9775 | 16.8374 | 17.3616 | 17.6841 | 17.6451 | 16.6295 | 14.9927 | 16.9134 | 17.2335 | 17.5283 | 17.5747 | 17.3188 | 16.5274 | 14.7697 | 6.452 | 8.4428 | 6.1037 | 6.1684 | 5.9305 | 6.6394 | 7.6034 | 16.059 | 15.6622 | 15.509 | 14.4514 | 14.3363 | 14.2701 |  |  |  | 10.8405 | 9.2924 | 8.9997 | 8.7516 | -0.071672 | -0.085606 | 12.912 |  |  | 10.712 |  |  | 17.0011 | 16.2008 | 15.1873 | 16.4802 | 15.7622 | 14.8844 | 10.5814 | 10.7355 | 11.5075 | 11.3673 | 9.0968 |  | 10.845 | 7.8539 | 10.1883 | 9.2283 | 11.2604 | 12.0447 |  | 12.4585 |  |  | 11.9185 | 12.6601 | 12.6687 | [6 empty] | 12.5778 |  |  | 11.3141 |  |  | 9.3289 | 10.44 | 12.3531 | 7.5514 | 9.3274 | 12.7774 | 7.7773 | 9.5749 | 12.6235 | 9.2193 | 10.47 | 7.5974 | 10.4006 | 8.1731 | 10.1479 | 8.1115 | 9.8575 | 13.6062 | 10.7373 | 10.4535 | 11.7404 | 8.2203 | 9.8842 | 13.0854 | 8.0082 | 10.3999 | 9.8016 | 9.9246 | 8.3623 | 10.3137 | -0.064726 | 20.9574 | 0.033441 | 0.049861 | -38.1806 | 3.1217 | -1.13 | 0.29 | -0.18689 | -0.5299 | 0.12954 | 0.42232 | -0.24012 | -0.80885 | 0.78661 | 0.41739 | 0.43027 | 0.42744 | 0.36828 | 0.51891 | 0.43281 | 0.42683
42810.4329 | -616 | 18.7029 | 18.7068 | 18.6763 | 18.7003 | 18.0589 | 16.7221 | 14.7882 | 16.7872 | 17.2763 | 17.379 | 17.3919 | 16.9519 | 16.0219 | 14.6363 | 15.164 | 15.1162 | 15.6386 | 13.4981 | 13.5996 | 14.1807 |  |  |  | 16.6924 | 16.0338 | 15.1515 | 10.3053 | 9.8074 | 9.8717 | 17.3979 | 16.4996 | 15.2872 | 16.9944 | 16.2697 | 15.285 | 10.9444 | 11.7913 |  | 12.3962 | 10.6021 | 10.6916 | 8.7034 |  | 6.3188 | 6.2786 | 5.7672 | 5.8301 | 5.807 | 5.8797 | 6.1653 | 5.0032 | 6.3503 | 4.7533 | 6.6539 | 8.2604 | 42.23 | 46.5817 | 42.9573 | 15.5264 |  |  | -0.021465 | -0.083365 | 0.062304 | 0.049942 | -0.078032 | -0.25345 | 0.51836 | -0.15722 | -0.30726 | -0.23284 | -0.31465 | 8.8764 | 8.8775 | 2.0085 | 15.9799 | 16.8477 | 17.3669 | 17.6877 | 17.6508 | 16.6433 | 14.9958 | 16.9249 | 17.2477 | 17.5431 | 17.5796 | 17.3264 | 16.5346 | 14.7734 | 6.4653 | 8.4621 | 6.014 | 6.1661 | 6.0214 | 6.6415 | 7.5983 | 16.0594 | 15.6621 | 15.5105 | 14.4458 | 14.3321 | 14.2622 |  |  |  | 10.8425 | 9.2923 | 8.9918 | 8.7338 | 0.021119 | -0.0012926 | 12.921 |  |  | 10.7231 |  |  | 17.0037 | 16.2011 | 15.1886 | 16.4811 | 15.7678 | 14.8891 | 10.5908 | 10.738 | 11.5183 | 11.3794 | 9.1222 |  | 10.8487 | 7.7918 | 10.1853 | 9.2083 | 11.251 | 12.1083 |  | 12.4562 |  |  | 11.9159 | 12.6744 | 12.6671 | [6 empty] | 12.5965 |  |  | 11.2935 |  |  | 9.3095 | 10.4376 | 12.3393 | 7.5364 | 9.3111 | 12.7766 | 7.7618 | 9.5726 | 12.6162 | 9.2049 | 10.4632 | 7.5992 | 10.4056 | 8.1502 | 10.1352 | 8.1048 | 9.8295 | 13.5925 | 10.7321 | 10.4407 | 11.7288 | 8.2113 | 9.8834 | 13.0817 | 8.0055 | 10.3877 | 9.789 | 9.9199 | 8.3618 | 10.2888 | -0.14408 | 20.9571 | 0.033579 | 0.050404 | -38.0469 | 3.1217 | -1.03 | 0.28 | -0.17177 | -0.33635 | 0.29078 | 0.26034 | -0.32518 | -0.58605 | 0.83813 | 0.41681 | 0.4319 | 0.42769 | 0.36705 | 0.52829 | 0.4316 | 0.42739
42810.4329 | -615 | 18.6904 | 18.7134 | 18.6708 | 18.6948 | 18.057 | 16.7188 | 14.7887 | 16.7878 | 17.2704 | 17.3761 | 17.387 | 16.9503 | 16.0224 | 14.6274 | 15.1564 | 15.1188 | 15.6446 | 13.498 | 13.6065 | 14.184 |  |  |  | 16.6906 | 16.033 | 15.1577 | 10.2927 | 9.8207 | 9.8669 | 17.3987 | 16.4958 | 15.2813 | 16.9916 | 16.2717 | 15.287 | 10.9402 | 11.8185 |  | 12.3941 | 10.6039 | 10.6824 | 8.721 |  | 6.3309 | 6.284 | 5.7697 | 5.8385 | 5.8074 | 5.8812 | 6.1618 | 4.9674 | 6.3625 | 4.7996 | 6.6618 | 8.254 | 42.2388 | 46.5592 | 42.9454 | 15.5283 |  |  | 0.090243 | -0.10439 | 0.1589 | 0.11565 | -0.12009 | -0.071428 | 0.51508 | -0.36815 | -0.18816 | -0.0020608 | -0.39969 | 8.878 | 8.8787 | 2.0086 | 15.9769 | 16.8509 | 17.3668 | 17.6845 | 17.6531 | 16.6422 | 14.9986 | 16.9213 | 17.248 | 17.5334 | 17.5745 | 17.319 | 16.5327 | 14.776 | 6.4343 | 8.4563 | 5.9519 | 6.1925 | 6.154 | 6.637 | 7.5994 | 16.0575 | 15.6591 | 15.5114 | 14.4432 | 14.3291 | 14.2642 |  |  |  | 10.8366 | 9.2823 | 8.999 | 8.7232 | 0.091827 | -0.032157 | 12.9185 |  |  | 10.7272 |  |  | 16.9994 | 16.2001 | 15.187 | 16.4835 | 15.7714 | 14.8905 | 10.5973 | 10.7493 | 11.5292 | 11.3937 | 9.1371 |  | 10.8412 | 7.7377 | 10.1812 | 9.1853 | 11.2462 | 12.1904 |  | 12.4579 |  |  | 11.9221 | 12.66 | 12.6689 | [6 empty] | 12.5957 |  |  | 11.2908 |  |  | 9.3099 | 10.4335 | 12.3431 | 7.5453 | 9.2886 | 12.7653 | 7.7733 | 9.5762 | 12.6149 | 9.2077 | 10.4569 | 7.6149 | 10.3972 | 8.1335 | 10.1376 | 8.0991 | 9.7863 | 13.5861 | 10.719 | 10.4356 | 11.739 | 8.2167 | 9.885 | 13.085 | 8.0064 | 10.387 | 9.7956 | 9.9224 | 8.3674 | 10.2971 | -0.0069458 | 20.9563 | 0.033458 | 0.050672 | -38.0538 | 3.1217 | -1.12 | 0.37 | 0.35219 | -0.37639 | 0.46437 | 0.39617 | -0.40341 | -0.31112 | 0.83547 | 0.41615 | 0.43327 | 0.42816 | 0.36998 | 0.53531 | 0.43097 | 0.42749
42810.4329 | -614 | 18.6946 | 18.7116 | 18.675 | 18.6979 | 18.0596 | 16.7239 | 14.7933 | 16.7888 | 17.2718 | 17.3715 | 17.3921 | 16.9561 | 16.0276 | 14.64 | 15.1583 | 15.1222 | 15.6504 | 13.4948 | 13.6149 | 14.1937 |  |  |  | 16.6915 | 16.0399 | 15.1559 | 10.2987 | 9.8174 | 9.9038 | 17.4013 | 16.4969 | 15.2898 | 16.9905 | 16.2762 | 15.2794 | 10.9406 | 11.93 |  | 12.3976 | 10.6102 | 10.6822 | 8.7381 |  | 6.3331 | 6.2805 | 5.7745 | 5.833 | 5.8024 | 5.8745 | 6.1575 | 4.9431 | 6.3577 | 4.8522 | 6.6666 | 8.2484 | 42.2549 | 46.5576 | 42.9356 | 15.5274 |  |  | -0.072065 | -0.092565 | 0.029448 | 0.12419 | -0.15229 | -0.007032 | 0.47302 | -0.29915 | -0.09203 | 0.14795 | -0.19801 | 8.883 | 8.8841 | 2.0082 | 15.9777 | 16.8477 | 17.3681 | 17.6855 | 17.6509 | 16.6419 | 14.9955 | 16.9213 | 17.253 | 17.5334 | 17.5749 | 17.3185 | 16.5313 | 14.7758 | 6.3701 | 8.4581 | 5.8492 | 6.1695 | 6.1862 | 6.6373 | 7.5981 | 16.0509 | 15.6644 | 15.5142 | 14.4462 | 14.3333 | 14.2651 |  |  |  | 10.8392 | 9.2796 | 8.9977 | 8.7133 | 0.22615 | 0.073799 | 12.9081 |  |  | 10.7158 |  |  | 16.9959 | 16.2028 | 15.176 | 16.4835 | 15.7631 | 14.886 | 10.5947 | 10.7584 | 11.5283 | 11.3904 | 9.1378 |  | 10.8377 | 7.735 | 10.1754 | 9.1828 | 11.2497 | 12.2527 |  | 12.4581 |  |  | 11.9273 | 12.6574 | 12.6751 | [6 empty] | 12.6137 |  |  | 11.2895 |  |  | 9.3122 | 10.4337 | 12.3373 | 7.5524 | 9.2929 | 12.7583 | 7.7747 | 9.5754 | 12.628 | 9.2161 | 10.4558 | 7.6168 | 10.4076 | 8.1275 | 10.1454 | 8.0766 | 9.7489 | 13.5819 | 10.7178 | 10.4321 | 11.742 | 8.2206 | 9.8836 | 13.0733 | 7.9638 | 10.382 | 9.7935 | 9.9369 | 8.3685 | 10.2899 | -0.041229 | 20.9571 | 0.033986 | 0.050983 | -38.1165 | 3.1217 | -0.92 | 0.34 | -0.31475 | -0.35443 | 0.19991 | 0.41054 | -0.45428 | -0.097617 | 0.80063 | 0.41601 | 0.43315 | 0.42835 | 0.37715 | 0.54658 | 0.43051 | 0.42785
42810.4329 | -613 | 18.6836 | 18.6984 | 18.6772 | 18.6898 | 18.0517 | 16.7089 | 14.7895 | 16.7871 | 17.2664 | 17.36 | 17.3923 | 16.956 | 16.0165 | 14.6282 | 15.1731 | 15.1191 | 15.644 | 13.4989 | 13.6136 | 14.1913 |  |  |  | 16.7042 | 16.0427 | 15.1621 | 10.3037 | 9.8254 | 9.9342 | 17.4027 | 16.496 | 15.2891 | 16.9887 | 16.2752 | 15.2897 | 10.9456 | 12.0169 |  | 12.4056 | 10.5902 | 10.6759 | 8.7363 |  | 6.3375 | 6.2804 | 5.7694 | 5.838 | 5.8033 | 5.8835 | 6.1502 | 4.9608 | 6.3619 | 4.867 | 6.6681 | 8.2585 | 42.2752 | 46.5704 | 42.9292 | 15.5245 |  |  | 0.2381 | -0.12542 | 0.05902 | 0.15902 | -0.097088 | -0.030028 | 0.58079 | -0.34318 | -0.56705 | -0.41725 | -0.061307 | 8.8765 | 8.8778 | 2.0086 | 15.9825 | 16.842 | 17.37 | 17.683 | 17.6463 | 16.6393 | 14.9916 | 16.9216 | 17.252 | 17.54 | 17.5754 | 17.3211 | 16.536 | 14.7736 | 6.3156 | 8.4693 | 5.781 | 6.1167 | 6.257 | 6.6429 | 7.607 | 16.056 | 15.6631 | 15.5136 | 14.4493 | 14.3239 | 14.2643 |  |  |  | 10.8319 | 9.2738 | 9.005 | 8.7058 | 0.099931 | -0.070738 | 12.9051 |  |  | 10.7141 |  |  | 16.9892 | 16.2023 | 15.1803 | 16.477 | 15.7639 | 14.8812 | 10.591 | 10.7613 | 11.5384 | 11.3997 | 9.1349 |  | 10.8296 | 7.7741 | 10.1729 | 9.1681 | 11.2398 | 12.2848 |  | 12.4378 |  |  | 11.9449 | 12.6424 | 12.6741 | [6 empty] | 12.615 |  |  | 11.2847 |  |  | 9.3178 | 10.4302 | 12.3302 | 7.5475 | 9.2884 | 12.7512 | 7.7681 | 9.574 | 12.631 | 9.215 | 10.4495 | 7.6194 | 10.4099 | 8.1283 | 10.1317 | 8.0525 | 9.7226 | 13.5869 | 10.7177 | 10.4282 | 11.742 | 8.2193 | 9.8784 | 13.0602 | 7.9222 | 10.3764 | 9.7924 | 9.9429 | 8.3734 | 10.2853 | -0.069156 | 20.9566 | 0.033648 | 0.049087 | -38.0231 | 3.1217 | -1.01 | 0.29 | 0.57214 | -0.41256 | 0.28301 | 0.46455 | -0.36273 | -0.20172 | 0.88717 | 0.41583 | 0.43198 | 0.42843 | 0.38384 | 0.55519 | 0.43072 | 0.42782
42810.433 | -612 | 18.6896 | 18.7122 | 18.6779 | 18.7007 | 18.0594 | 16.7212 | 14.7973 | 16.7894 | 17.2778 | 17.369 | 17.3968 | 16.9565 | 16.0207 | 14.6329 | 15.1703 | 15.1144 | 15.6422 | 13.4914 | 13.6126 | 14.1886 |  |  |  | 16.701 | 16.0308 | 15.1618 | 10.3015 | 9.8236 | 9.9546 | 17.4065 | 16.5008 | 15.2899 | 16.9954 | 16.2767 | 15.2873 | 10.9463 | 12.0946 |  | 12.4038 | 10.5871 | 10.6705 | 8.7297 |  | 6.3335 | 6.2799 | 5.7777 | 5.8367 | 5.8062 | 5.8671 | 6.1711 | 5.0308 | 6.3581 | 4.8655 | 6.6629 | 8.2548 | 42.2917 | 46.5653 | 42.9223 | 15.5176 |  |  | 0.081043 | 0.092083 | -0.099344 | 0.24445 | 0.067848 | 0.000196 | 0.38694 | -0.42269 | -0.17143 | -0.24732 | -0.18689 | 8.8788 | 8.8801 | 2.0085 | 15.9825 | 16.8486 | 17.373 | 17.6888 | 17.6517 | 16.6458 | 15.0006 | 16.9297 | 17.2578 | 17.544 | 17.5831 | 17.3225 | 16.5417 | 14.7823 | 6.2821 | 8.4505 | 5.7809 | 6.0558 | 6.3062 | 6.6398 | 7.5994 | 16.0491 | 15.662 | 15.5116 | 14.4502 | 14.3222 | 14.2695 |  |  |  | 10.8353 | 9.2749 | 9.0141 | 8.7162 | 0.027805 | -0.04025 | 12.9065 |  |  | 10.7102 |  |  | 16.9917 | 16.2016 | 15.1822 | 16.4789 | 15.7664 | 14.8809 | 10.6039 | 10.7574 | 11.5468 | 11.4105 | 9.152 |  | 10.8362 | 7.8072 | 10.1758 | 9.1653 | 11.2415 | 12.3176 |  | 12.4423 |  |  | 11.9572 | 12.6315 | 12.6862 | [6 empty] | 12.6074 |  |  | 11.2928 |  |  | 9.3161 | 10.4277 | 12.32 | 7.5439 | 9.2897 | 12.7379 | 7.764 | 9.5724 | 12.6322 | 9.2099 | 10.4374 | 7.6277 | 10.4164 | 8.1309 | 10.1246 | 8.0356 | 9.7014 | 13.5703 | 10.7168 | 10.4195 | 11.7381 | 8.2103 | 9.8575 | 13.0444 | 7.8785 | 10.3623 | 9.7815 | 9.9435 | 8.3672 | 10.275 | -0.25463 | 20.957 | 0.032621 | 0.048066 | -38.1472 | 3.1217 | -1.02 | 0.35 | 0.33381 | 0.3535 | -0.36718 | 0.57596 | 0.30322 | 0.016297 | 0.72411 | 0.41557 | 0.43116 | 0.42857 | 0.38721 | 0.55431 | 0.43093 | 0.42764
42810.433 | -611 | 18.6928 | 18.7171 | 18.6751 | 18.6963 | 18.0558 | 16.7187 | 14.7905 | 16.7792 | 17.271 | 17.3654 | 17.3896 | 16.9506 | 16.015 | 14.6324 | 15.1657 | 15.1115 | 15.6491 | 13.4951 | 13.609 | 14.1885 |  |  |  | 16.6924 | 16.0357 | 15.1605 | 10.3018 | 9.836 | 9.9432 | 17.4046 | 16.5083 | 15.2922 | 16.9925 | 16.274 | 15.2961 | 10.9451 | 12.1484 |  | 12.3963 | 10.5778 | 10.6675 | 8.7439 |  | 6.3369 | 6.2822 | 5.7719 | 5.8434 | 5.813 | 5.8712 | 6.1709 | 5.0343 | 6.3512 | 4.8521 | 6.6559 | 8.2466 | 42.3025 | 46.5584 | 42.9097 | 15.5055 |  |  | 0.036359 | 0.10851 | 0.16284 | 0.18071 | 0.12633 | 0.027796 | 0.17666 | -0.31689 | 0.34018 | -0.71664 | -0.37148 | 8.8781 | 8.8791 | 2.0086 | 15.9796 | 16.8489 | 17.3594 | 17.6771 | 17.6544 | 16.6399 | 15 | 16.9227 | 17.2475 | 17.5297 | 17.5777 | 17.3277 | 16.5353 | 14.7746 | 6.3004 | 8.4711 | 5.8027 | 6.015 | 6.3021 | 6.6371 | 7.5998 | 16.0419 | 15.6479 | 15.4971 | 14.4416 | 14.3178 | 14.2633 |  |  |  | 10.8231 | 9.268 | 9.0096 | 8.7103 | 0.0091658 | -0.10349 | 12.9095 |  |  | 10.7148 |  |  | 17.0009 | 16.2048 | 15.1819 | 16.4835 | 15.7663 | 14.889 | 10.6101 | 10.7635 | 11.5512 | 11.4235 | 9.1412 |  | 10.8281 | 7.8154 | 10.1714 | 9.1597 | 11.2457 | 12.3587 |  | 12.451 |  |  | 11.9631 | 12.64 | 12.6913 | [6 empty] | 12.5847 |  |  | 11.3111 |  |  | 9.3118 | 10.4189 | 12.3067 | 7.5436 | 9.2783 | 12.7248 | 7.7506 | 9.5724 | 12.6346 | 9.2024 | 10.4323 | 7.6287 | 10.4137 | 8.1225 | 10.1261 | 8.0138 | 9.693 | 13.56 | 10.7037 | 10.4198 | 11.7287 | 8.208 | 9.8465 | 13.0326 | 7.8625 | 10.3561 | 9.7789 | 9.9413 | 8.3653 | 10.2663 | -0.1148 | 20.957 | 0.032764 | 0.048775 | -38.1122 | 3.1217 | -1.04 | 0.31 | 0.22358 | 0.38374 | 0.4701 | 0.49521 | 0.41375 | 0.19408 | 0.48928 | 0.4156 | 0.43079 | 0.42886 | 0.38486 | 0.55194 | 0.43049 | 0.4274
42810.433 | -610 | 18.6907 | 18.713 | 18.6736 | 18.6947 | 18.048 | 16.7113 | 14.7881 | 16.7772 | 17.2694 | 17.3713 | 17.3868 | 16.9521 | 16.0161 | 14.6311 | 15.1721 | 15.1202 | 15.6543 | 13.4953 | 13.6211 | 14.1995 |  |  |  | 16.6963 | 16.0386 | 15.1678 | 10.3092 | 9.8397 | 9.9153 | 17.4004 | 16.5032 | 15.2887 | 16.9951 | 16.2755 | 15.2909 | 10.9448 | 12.1421 |  | 12.3951 | 10.5759 | 10.6554 | 8.7654 |  | 6.3428 | 6.2923 | 5.7877 | 5.8569 | 5.8218 | 5.8791 | 6.1706 | 5.1093 | 6.3573 | 4.8383 | 6.6644 | 8.2427 | 42.3209 | 46.5749 | 42.8941 | 15.4996 |  |  | 0.004163 | -0.074825 | -0.13089 | 0.11565 | -0.19631 | -0.15554 | 0.47368 | -0.50154 | -0.28935 | 0.96554 | -0.30154 | 8.8774 | 8.8786 | 2.0084 | 15.9892 | 16.8592 | 17.3761 | 17.6827 | 17.6551 | 16.6356 | 15.0039 | 16.9272 | 17.2594 | 17.5386 | 17.5854 | 17.3197 | 16.5456 | 14.7772 | 6.311 | 8.4958 | 5.8056 | 5.9918 | 6.289 | 6.6427 | 7.6012 | 16.0489 | 15.6585 | 15.5046 | 14.4496 | 14.326 | 14.2672 |  |  |  | 10.8281 | 9.2782 | 9.0138 | 8.715 | -0.11847 | 0.12461 | 12.9071 |  |  | 10.7094 |  |  | 17.0033 | 16.2031 | 15.1768 | 16.4786 | 15.7626 | 14.8871 | 10.6161 | 10.7638 | 11.5606 | 11.4282 | 9.1573 |  | 10.8306 | 7.7947 | 10.1699 | 9.1587 | 11.2445 | 12.3785 |  | 12.456 |  |  | 11.9725 | 12.6474 | 12.6868 | [6 empty] | 12.5657 |  |  | 11.3163 |  |  | 9.3059 | 10.4074 | 12.3012 | 7.5305 | 9.2751 | 12.7183 | 7.7423 | 9.5705 | 12.6293 | 9.2012 | 10.4318 | 7.6217 | 10.4117 | 8.1178 | 10.1257 | 7.9954 | 9.6878 | 13.5573 | 10.7061 | 10.4211 | 11.7297 | 8.21 | 9.8451 | 13.0344 | 7.8594 | 10.3529 | 9.7791 | 9.9494 | 8.3644 | 10.2549 | -0.043155 | 20.9551 | 0.033413 | 0.048638 | -38.166 | 3.1217 | -1.25 | 0.35 | 0.075651 | -0.31867 | -0.42147 | 0.39618 | -0.51578 | -0.45911 | 0.80119 | 0.41524 | 0.43131 | 0.42885 | 0.38434 | 0.55177 | 0.42989 | 0.42744
42810.433 | -609 | 18.6894 | 18.7113 | 18.6682 | 18.6923 | 18.0457 | 16.717 | 14.79 | 16.7801 | 17.2749 | 17.3696 | 17.3851 | 16.955 | 16.0143 | 14.6314 | 15.1729 | 15.1161 | 15.6537 | 13.4885 | 13.6212 | 14.1921 |  |  |  | 16.6911 | 16.0339 | 15.1627 | 10.2984 | 9.8364 | 9.8885 | 17.3998 | 16.4977 | 15.2923 | 17 | 16.2781 | 15.2867 | 10.937 | 12.0955 |  | 12.4031 | 10.5715 | 10.6395 | 8.763 |  | 6.3359 | 6.2937 | 5.7887 | 5.8615 | 5.8249 | 5.8846 | 6.1629 | 5.1702 | 6.3665 | 4.8051 | 6.6717 | 8.2462 | 42.3367 | 46.5965 | 42.8857 | 15.4869 |  |  | 0.054759 | -0.21611 | 0.019592 | -0.028254 | -0.10038 | -0.085884 | 0.61628 | -0.29127 | -0.57522 | 0.43202 | -0.50898 | 8.8773 | 8.8786 | 2.0087 | 15.9772 | 16.8467 | 17.3588 | 17.6791 | 17.6449 | 16.646 | 14.9972 | 16.9192 | 17.2503 | 17.5314 | 17.5803 | 17.3171 | 16.5403 | 14.775 | 6.3455 | 8.4981 | 5.8056 | 5.9879 | 6.2344 | 6.6371 | 7.5984 | 16.049 | 15.6573 | 15.5138 | 14.4472 | 14.3228 | 14.2691 |  |  |  | 10.8234 | 9.2729 | 9.0087 | 8.7247 | 0.081291 | 0.16621 | 12.8964 |  |  | 10.6841 |  |  | 16.9914 | 16.1949 | 15.1746 | 16.4741 | 15.7554 | 14.8796 | 10.6132 | 10.75 | 11.5564 | 11.4234 | 9.1571 |  | 10.8335 | 7.7797 | 10.1683 | 9.1704 | 11.2475 | 12.3951 |  | 12.4477 |  |  | 11.9864 | 12.6385 | 12.6877 | [6 empty] | 12.5712 |  |  | 11.3197 |  |  | 9.302 | 10.3955 | 12.2942 | 7.5062 | 9.2693 | 12.7099 | 7.7418 | 9.5722 | 12.6258 | 9.1941 | 10.4243 | 7.6004 | 10.412 | 8.1215 | 10.1161 | 7.9776 | 9.6868 | 13.5509 | 10.7081 | 10.414 | 11.7235 | 8.212 | 9.8379 | 13.0324 | 7.861 | 10.3563 | 9.7818 | 9.9431 | 8.363 | 10.2435 | -0.11615 | 20.9557 | 0.033849 | 0.047979 | -38.1227 | 3.1217 | -1.45 | 0.31 | 0.27436 | -0.54156 | 0.16306 | -0.19582 | -0.36882 | -0.34116 | 0.91387 | 0.41533 | 0.43168 | 0.42862 | 0.37985 | 0.55145 | 0.4297 | 0.42701
42810.433 | -608 | 18.6922 | 18.7161 | 18.6695 | 18.7028 | 18.0467 | 16.7196 | 14.7873 | 16.779 | 17.2749 | 17.3758 | 17.3843 | 16.9543 | 16.0223 | 14.6303 | 15.1664 | 15.1138 | 15.6557 | 13.4925 | 13.6153 | 14.1881 |  |  |  | 16.6952 | 16.0347 | 15.1594 | 10.2928 | 9.8335 | 9.8639 | 17.4023 | 16.5001 | 15.2961 | 16.9903 | 16.2796 | 15.2864 | 10.9399 | 12.0604 |  | 12.4072 | 10.5671 | 10.6315 | 8.7675 |  | 6.3538 | 6.3041 | 5.8028 | 5.878 | 5.839 | 5.8942 | 6.1622 | 5.1665 | 6.373 | 4.7761 | 6.6795 | 8.251 | 42.3538 | 46.6327 | 42.8852 | 15.4883 |  |  | 0.055415 | -0.007797 | 0.11816 | -0.14917 | -0.047804 | -0.30602 | 0.43688 | -0.30901 | -0.32263 | -0.27627 | 0.050561 | 8.8793 | 8.8808 | 2.0084 | 15.9763 | 16.8452 | 17.3638 | 17.6799 | 17.6514 | 16.6416 | 14.9957 | 16.9237 | 17.2461 | 17.5299 | 17.5744 | 17.3149 | 16.5394 | 14.771 | 6.3881 | 8.5137 | 5.7973 | 6.0289 | 6.1733 | 6.6441 | 7.6036 | 16.0486 | 15.6662 | 15.5099 | 14.4524 | 14.329 | 14.2751 |  |  |  | 10.8237 | 9.2689 | 9.0075 | 8.7066 | 0.12465 | 0.075117 | 12.896 |  |  | 10.6728 |  |  | 16.9812 | 16.1881 | 15.1699 | 16.4724 | 15.7637 | 14.8778 | 10.6202 | 10.7462 | 11.5617 | 11.4311 | 9.1785 |  | 10.8297 | 7.7935 | 10.174 | 9.1886 | 11.2498 | 12.4339 |  | 12.4564 |  |  | 11.9877 | 12.6419 | 12.6877 | [6 empty] | 12.5874 |  |  | 11.323 |  |  | 9.3064 | 10.3922 | 12.2816 | 7.4995 | 9.2605 | 12.7122 | 7.7432 | 9.5745 | 12.6179 | 9.1892 | 10.4243 | 7.5779 | 10.4167 | 8.1162 | 10.116 | 7.978 | 9.6954 | 13.5475 | 10.7082 | 10.4149 | 11.7227 | 8.2179 | 9.8356 | 13.0244 | 7.8742 | 10.3711 | 9.7855 | 9.9363 | 8.3634 | 10.2408 | -0.17894 | 20.9556 | 0.033981 | 0.047654 | -38.1126 | 3.1218 | -1.31 | 0.32 | 0.27598 | -0.10287 | 0.40046 | -0.44994 | -0.25453 | -0.64399 | 0.76946 | 0.41462 | 0.43148 | 0.42819 | 0.37592 | 0.55297 | 0.42967 | 0.42753
42810.433 | -607 | 18.6892 | 18.7054 | 18.6683 | 18.6931 | 18.0578 | 16.7198 | 14.7884 | 16.7729 | 17.2714 | 17.3705 | 17.3873 | 16.9533 | 16.015 | 14.6234 | 15.1665 | 15.1177 | 15.6489 | 13.499 | 13.6077 | 14.1907 |  |  |  | 16.6924 | 16.0438 | 15.1593 | 10.2863 | 9.8312 | 9.845 | 17.4053 | 16.5112 | 15.3017 | 16.996 | 16.2834 | 15.2982 | 10.9466 | 12.0469 |  | 12.4001 | 10.5642 | 10.6093 | 8.7599 |  | 6.3475 | 6.2971 | 5.7964 | 5.8689 | 5.8285 | 5.8848 | 6.1938 | 5.0833 | 6.3602 | 4.7233 | 6.6649 | 8.2475 | 42.3707 | 46.6458 | 42.8816 | 15.4719 |  |  | 0.32418 | -0.057737 | 0.074132 | -0.30556 | -0.06226 | 0.04554 | 0.60313 | -0.22621 | -0.50283 | -0.172 | -0.28246 | 8.8765 | 8.8777 | 2.0087 | 15.9727 | 16.8465 | 17.3647 | 17.6767 | 17.6472 | 16.6401 | 14.9979 | 16.9243 | 17.246 | 17.5297 | 17.5697 | 17.3167 | 16.5332 | 14.7722 | 6.3753 | 8.5377 | 5.7915 | 6.06 | 6.1365 | 6.6498 | 7.6092 | 16.047 | 15.661 | 15.5061 | 14.4506 | 14.3246 | 14.2658 |  |  |  | 10.822 | 9.2577 | 8.9917 | 8.6927 | 0.12728 | 0.028443 | 12.9059 |  |  | 10.6684 |  |  | 16.9919 | 16.1959 | 15.1794 | 16.4825 | 15.7706 | 14.8794 | 10.6363 | 10.7598 | 11.5759 | 11.4448 | 9.1821 |  | 10.8305 | 7.8001 | 10.1674 | 9.1773 | 11.2403 | 12.451 |  | 12.4501 |  |  | 11.9806 | 12.645 | 12.6753 | [6 empty] | 12.59 |  |  | 11.3234 |  |  | 9.3013 | 10.3949 | 12.2818 | 7.488 | 9.2534 | 12.714 | 7.7413 | 9.5704 | 12.6026 | 9.1842 | 10.4278 | 7.5864 | 10.4181 | 8.1159 | 10.1174 | 7.9614 | 9.7076 | 13.5418 | 10.7122 | 10.4188 | 11.7282 | 8.235 | 9.8375 | 13.0144 | 7.8884 | 10.3748 | 9.7847 | 9.9454 | 8.3612 | 10.2415 | 0.0007582 | 20.9565 | 0.033992 | 0.047965 | -38.1649 | 3.1217 | -1.5 | 0.27 | 0.6675 | -0.27993 | 0.31719 | -0.64397 | -0.29047 | 0.24842 | 0.90407 | 0.41454 | 0.43108 | 0.42819 | 0.37801 | 0.55428 | 0.4301 | 0.42786
42810.433 | -606 | 18.6931 | 18.7096 | 18.6802 | 18.6886 | 18.0497 | 16.721 | 14.7904 | 16.7843 | 17.2834 | 17.3685 | 17.3907 | 16.9494 | 16.0149 | 14.6248 | 15.1613 | 15.1241 | 15.6498 | 13.4966 | 13.6065 | 14.1866 |  |  |  | 16.6918 | 16.0378 | 15.162 | 10.2824 | 9.8205 | 9.826 | 17.3975 | 16.5077 | 15.2913 | 16.9955 | 16.2781 | 15.2961 | 10.935 | 12.0443 |  | 12.3942 | 10.5637 | 10.5848 | 8.6981 |  | 6.3513 | 6.3056 | 5.8109 | 5.8701 | 5.8443 | 5.8899 | 6.2364 | 4.9973 | 6.3678 | 4.7334 | 6.6734 | 8.2448 | 42.379 | 46.6538 | 42.8859 | 15.4686 |  |  | 0.17501 | -0.10242 | 0.14444 | -0.12025 | -0.19894 | -0.13977 | 0.49865 | -0.21307 | -0.66493 | -0.22592 | -0.36234 | 8.8793 | 8.8804 | 2.0087 | 15.9672 | 16.8428 | 17.3647 | 17.6797 | 17.6425 | 16.6321 | 15.0007 | 16.9169 | 17.2375 | 17.5239 | 17.5689 | 17.311 | 16.5294 | 14.7698 | 6.3859 | 8.557 | 5.7874 | 6.0257 | 6.1339 | 6.6537 | 7.6069 | 16.0361 | 15.6564 | 15.5012 | 14.449 | 14.3178 | 14.2705 |  |  |  | 10.815 | 9.2559 | 8.9911 | 8.6743 | 0.11918 | 0.066271 | 12.9114 |  |  | 10.6679 |  |  | 16.996 | 16.1986 | 15.1799 | 16.4862 | 15.7696 | 14.8762 | 10.6466 | 10.7619 | 11.5811 | 11.4572 | 9.1583 |  | 10.8342 | 7.8203 | 10.1715 | 9.1743 | 11.2457 | 12.4786 |  | 12.4623 |  |  | 11.9812 | 12.6408 | 12.6479 | [6 empty] | 12.6 |  |  | 11.3197 |  |  | 9.2942 | 10.3913 | 12.2687 | 7.4852 | 9.2558 | 12.709 | 7.74 | 9.5646 | 12.5857 | 9.1816 | 10.4241 | 7.5895 | 10.4193 | 8.1176 | 10.1188 | 7.9316 | 9.7006 | 13.5205 | 10.7 | 10.4043 | 11.7107 | 8.2151 | 9.8321 | 12.9955 | 7.8826 | 10.3676 | 9.7652 | 9.9304 | 8.3456 | 10.2162 | 0.039471 | 20.9561 | 0.033935 | 0.048435 | -38.1513 | 3.1218 | -1.49 | 0.33 | 0.49043 | -0.37284 | 0.44276 | -0.40399 | -0.51923 | -0.43522 | 0.82205 | 0.41533 | 0.43066 | 0.42846 | 0.37728 | 0.55446 | 0.43144 | 0.42814
42810.433 | -605 | 18.6841 | 18.7091 | 18.6786 | 18.6875 | 18.0474 | 16.7212 | 14.7863 | 16.7845 | 17.2766 | 17.3636 | 17.3932 | 16.9478 | 16.0144 | 14.6359 | 15.1635 | 15.12 | 15.6503 | 13.4989 | 13.6104 | 14.1986 |  |  |  | 16.6887 | 16.032 | 15.1692 | 10.2844 | 9.8313 | 9.8135 | 17.3972 | 16.5005 | 15.2923 | 16.9923 | 16.2745 | 15.2926 | 10.9359 | 12.027 |  | 12.3964 | 10.5684 | 10.5586 | 8.655 |  | 6.3609 | 6.3147 | 5.8196 | 5.8752 | 5.8539 | 5.8995 | 6.271 | 4.9232 | 6.3727 | 4.7609 | 6.6792 | 8.2455 | 42.3802 | 46.6652 | 42.9021 | 15.4581 |  |  | -0.10952 | -0.19639 | 0.080704 | 0.032854 | -0.070804 | -0.089828 | 0.58605 | -0.29784 | -0.331 | -0.33858 | -0.32697 | 8.8763 | 8.8773 | 2.0084 | 15.9769 | 16.8426 | 17.3686 | 17.6867 | 17.6458 | 16.6372 | 14.9962 | 16.9172 | 17.2421 | 17.5341 | 17.572 | 17.3148 | 16.5361 | 14.7709 | 6.3994 | 8.6014 | 5.7884 | 5.9999 | 6.1879 | 6.653 | 7.6118 | 16.0385 | 15.6527 | 15.4997 | 14.4415 | 14.3125 | 14.2617 |  |  |  | 10.8154 | 9.2589 | 8.9887 | 8.674 | 0.21805 | 0.13139 | 12.9129 |  |  | 10.6689 |  |  | 16.9887 | 16.2016 | 15.1763 | 16.4813 | 15.7694 | 14.8837 | 10.6512 | 10.7544 | 11.5821 | 11.463 | 9.1662 |  | 10.824 | 7.8015 | 10.1518 | 9.1695 | 11.2355 | 12.495 |  | 12.4493 |  |  | 11.9865 | 12.6373 | 12.6383 | [6 empty] | 12.5902 |  |  | 11.3118 |  |  | 9.277 | 10.3774 | 12.2578 | 7.4696 | 9.2473 | 12.6949 | 7.7373 | 9.5689 | 12.5645 | 9.1701 | 10.4142 | 7.5854 | 10.4062 | 8.1166 | 10.1084 | 7.9114 | 9.7007 | 13.5118 | 10.6937 | 10.4062 | 11.7092 | 8.1954 | 9.8247 | 12.9791 | 7.8847 | 10.3563 | 9.7548 | 9.9256 | 8.3485 | 10.2015 | -0.06723 | 20.9566 | 0.033768 | 0.049398 | -38.1236 | 3.1218 | -1.4 | 0.44 | -0.38795 | -0.51628 | 0.33096 | 0.21117 | -0.30977 | -0.34891 | 0.8912 | 0.41477 | 0.43053 | 0.42825 | 0.37571 | 0.55492 | 0.43266 | 0.42816
42810.433 | -604 | 18.6847 | 18.7046 | 18.6778 | 18.6961 | 18.0455 | 16.718 | 14.7827 | 16.7777 | 17.2659 | 17.3662 | 17.3892 | 16.9533 | 16.008 | 14.6262 | 15.1523 | 15.1076 | 15.644 | 13.4909 | 13.6092 | 14.1985 |  |  |  | 16.6854 | 16.0302 | 15.1499 | 10.2697 | 9.8221 | 9.8032 | 17.3878 | 16.4891 | 15.2858 | 16.986 | 16.2728 | 15.2875 | 10.9272 | 11.9831 |  | 12.3885 | 10.5625 | 10.5262 | 8.6066 |  | 6.361 | 6.3255 | 5.8242 | 5.8883 | 5.8539 | 5.9123 | 6.2701 | 4.8859 | 6.375 | 4.7584 | 6.6753 | 8.2451 | 42.3795 | 46.6769 | 42.915 | 15.4464 |  |  | 0.021903 | -0.005825 | 0.094504 | 0.13011 | -0.005092 | -0.068144 | 0.48748 | -0.10267 | -0.27651 | -0.6088 | -0.22285 | 8.8772 | 8.8786 | 2.0086 | 15.9719 | 16.8463 | 17.3676 | 17.6916 | 17.6529 | 16.6376 | 15.0031 | 16.9283 | 17.2507 | 17.5346 | 17.5725 | 17.3199 | 16.5355 | 14.7648 | 6.4131 | 8.6007 | 5.7778 | 5.9658 | 6.1749 | 6.6442 | 7.6105 | 16.0409 | 15.6533 | 15.5047 | 14.4432 | 14.315 | 14.2626 |  |  |  | 10.8093 | 9.2555 | 8.9855 | 8.6716 | 0.029831 | 0.084338 | 12.9079 |  |  | 10.6703 |  |  | 16.9874 | 16.1977 | 15.1742 | 16.4741 | 15.76 | 14.8824 | 10.6457 | 10.7563 | 11.5892 | 11.463 | 9.1459 |  | 10.8312 | 7.8286 | 10.1619 | 9.1492 | 11.2298 | 12.5163 |  | 12.4469 |  |  | 11.9504 | 12.6265 | 12.6513 | [6 empty] | 12.5727 |  |  | 11.2964 |  |  | 9.2677 | 10.3811 | 12.2646 | 7.4499 | 9.2557 | 12.7027 | 7.7387 | 9.5744 | 12.572 | 9.1713 | 10.423 | 7.5962 | 10.418 | 8.1354 | 10.1115 | 7.9151 | 9.7183 | 13.5195 | 10.69 | 10.4123 | 11.7243 | 8.1988 | 9.842 | 12.9999 | 7.8928 | 10.3756 | 9.7606 | 9.9547 | 8.361 | 10.2162 | -0.14908 | 20.9559 | 0.033137 | 0.048935 | -38.1203 | 3.1218 | -1.39 | 0.38 | 0.17349 | -0.088917 | 0.35815 | 0.42024 | -0.083073 | -0.3039 | 0.81282 | 0.41557 | 0.43011 | 0.42863 | 0.37317 | 0.55595 | 0.43372 | 0.42802
42810.4331 | -603 | 18.6871 | 18.7039 | 18.6755 | 18.6946 | 18.0555 | 16.7179 | 14.7855 | 16.7788 | 17.2689 | 17.3707 | 17.3874 | 16.9551 | 16.0085 | 14.6274 | 15.1608 | 15.1109 | 15.6469 | 13.4892 | 13.617 | 14.189 |  |  |  | 16.6981 | 16.0331 | 15.1537 | 10.2702 | 9.8148 | 9.7948 | 17.3933 | 16.4975 | 15.2871 | 16.9866 | 16.2784 | 15.2884 | 10.9363 | 11.9575 |  | 12.3919 | 10.5717 | 10.5059 | 8.5745 |  | 6.3694 | 6.3253 | 5.8334 | 5.8927 | 5.85 | 5.9046 | 6.256 | 4.9179 | 6.3717 | 4.7696 | 6.6714 | 8.2445 | 42.3813 | 46.694 | 42.9332 | 15.441 |  |  | 0.005475 | -0.32781 | 0.088588 | -0.14391 | -0.17726 | -0.028716 | 0.63205 | 0.01298 | -0.62854 | -0.35578 | -0.16344 | 8.8784 | 8.8796 | 2.0084 | 15.9746 | 16.8381 | 17.3597 | 17.6808 | 17.6441 | 16.6371 | 14.9886 | 16.9151 | 17.2415 | 17.5235 | 17.563 | 17.3144 | 16.5347 | 14.7663 | 6.4492 | 8.5767 | 5.7475 | 5.9237 | 6.1424 | 6.6464 | 7.6174 | 16.0464 | 15.6608 | 15.5084 | 14.4438 | 14.3244 | 14.2705 |  |  |  | 10.8184 | 9.2754 | 8.9937 | 8.6776 | -0.0062318 | 0.008682 | 12.9084 |  |  | 10.6753 |  |  | 16.9997 | 16.2029 | 15.1747 | 16.483 | 15.7643 | 14.8808 | 10.6566 | 10.7585 | 11.5992 | 11.4683 | 9.1211 |  | 10.8245 | 7.8363 | 10.159 | 9.1351 | 11.232 | 12.5269 |  | 12.4434 |  |  | 11.9201 | 12.6509 | 12.6399 | [6 empty] | 12.5858 |  |  | 11.3017 |  |  | 9.2532 | 10.3703 | 12.2542 | 7.4461 | 9.2609 | 12.7089 | 7.7213 | 9.5666 | 12.5652 | 9.1734 | 10.4054 | 7.5939 | 10.4257 | 8.1295 | 10.0931 | 7.9179 | 9.7265 | 13.5184 | 10.6826 | 10.4178 | 11.7367 | 8.1997 | 9.8224 | 12.9896 | 7.9036 | 10.3809 | 9.7678 | 9.9525 | 8.367 | 10.2085 | 0.019826 | 20.9562 | 0.033258 | 0.048783 | -38.1213 | 3.1218 | -1.46 | 0.26 | 0.086738 | -0.66704 | 0.34676 | -0.44196 | -0.49013 | -0.19728 | 0.92552 | 0.41604 | 0.4298 | 0.42909 | 0.36942 | 0.56012 | 0.43491 | 0.42816
42810.4331 | -602 | 18.6881 | 18.7082 | 18.6792 | 18.6984 | 18.054 | 16.7172 | 14.7891 | 16.7844 | 17.277 | 17.3719 | 17.3883 | 16.9517 | 16.0184 | 14.6254 | 15.1589 | 15.1145 | 15.6464 | 13.4972 | 13.6024 | 14.1937 |  |  |  | 16.6942 | 16.03 | 15.158 | 10.2669 | 9.8136 | 9.7753 | 17.4026 | 16.4965 | 15.2963 | 16.9969 | 16.2765 | 15.298 | 10.9397 | 11.9451 |  | 12.3943 | 10.5766 | 10.5032 | 8.5409 |  | 6.3784 | 6.3289 | 5.8434 | 5.8952 | 5.873 | 5.9068 | 6.2646 | 5.0067 | 6.3737 | 4.7734 | 6.68 | 8.2394 | 42.384 | 46.7189 | 42.9494 | 15.4315 |  |  | 0.11784 | -0.23319 | 0.076104 | 0.15639 | -0.1904 | -0.14305 | 0.40074 | -0.06522 | 1.2151 | -0.32473 | -0.21709 | 8.8758 | 8.8772 | 2.0087 | 15.9676 | 16.8412 | 17.3591 | 17.6802 | 17.6385 | 16.6382 | 14.9894 | 16.9115 | 17.243 | 17.5275 | 17.5667 | 17.3107 | 16.5269 | 14.7668 | 6.477 | 8.5807 | 5.7263 | 5.8872 | 6.1108 | 6.6502 | 7.6217 | 16.0383 | 15.6536 | 15.4998 | 14.4412 | 14.3186 | 14.2666 |  |  |  | 10.8089 | 9.2741 | 8.9888 | 8.6781 | 0.15463 | 0.070035 | 12.9016 |  |  | 10.6629 |  |  | 17 | 16.1992 | 15.1776 | 16.4812 | 15.7694 | 14.884 | 10.6569 | 10.7614 | 11.5978 | 11.4649 | 9.0989 |  | 10.8164 | 7.8657 | 10.1527 | 9.1204 | 11.2293 | 12.5077 |  | 12.444 |  |  | 11.9052 | 12.646 | 12.6588 | [6 empty] | 12.5712 |  |  | 11.2747 |  |  | 9.2575 | 10.3725 | 12.2627 | 7.4372 | 9.2684 | 12.7227 | 7.7037 | 9.577 | 12.5616 | 9.171 | 10.4008 | 7.5945 | 10.4358 | 8.148 | 10.0999 | 7.9304 | 9.7388 | 13.5163 | 10.6858 | 10.4131 | 11.7442 | 8.1926 | 9.8283 | 12.9844 | 7.9142 | 10.3869 | 9.7567 | 9.9533 | 8.3633 | 10.2091 | 0.07125 | 20.9565 | 0.033527 | 0.049477 | -38.1845 | 3.1218 | -1.45 | 0.31 | 0.4024 | -0.56259 | 0.3214 | 0.46074 | -0.50798 | -0.44031 | 0.73696 | 0.41639 | 0.42877 | 0.42941 | 0.36675 | 0.56296 | 0.43595 | 0.42783
42810.4331 | -601 | 18.6862 | 18.7123 | 18.6799 | 18.6991 | 18.0538 | 16.7212 | 14.7897 | 16.7864 | 17.2778 | 17.3689 | 17.3865 | 16.9548 | 16.0152 | 14.6263 | 15.1522 | 15.1066 | 15.6496 | 13.4945 | 13.6042 | 14.1916 |  |  |  | 16.6912 | 16.0336 | 15.1511 | 10.2673 | 9.8071 | 9.7949 | 17.3985 | 16.5038 | 15.3007 | 16.9933 | 16.2747 | 15.2939 | 10.9302 | 11.9195 |  | 12.3937 | 10.5782 | 10.4933 | 8.5043 |  | 6.3688 | 6.3229 | 5.8338 | 5.8915 | 5.8605 | 5.9012 | 6.2939 | 5.0878 | 6.3722 | 4.7939 | 6.6665 | 8.2396 | 42.392 | 46.7341 | 42.9608 | 15.4188 |  |  | 0.040303 | 0.059227 | 0.08136 | 0.09331 | -0.030064 | -0.13122 | 0.32189 | -0.098732 | -0.68225 | -0.45544 | -0.16086 | 8.8797 | 8.8808 | 2.0085 | 15.9718 | 16.8445 | 17.3669 | 17.6808 | 17.6489 | 16.6373 | 14.9931 | 16.9175 | 17.2408 | 17.5292 | 17.5726 | 17.3148 | 16.5336 | 14.7763 | 6.5294 | 8.5431 | 5.7251 | 5.8531 | 6.0764 | 6.6542 | 7.6237 | 16.0311 | 15.6528 | 15.4958 | 14.444 | 14.3202 | 14.2685 |  |  |  | 10.8024 | 9.2723 | 8.9871 | 8.6682 | 0.14795 | -0.01729 | 12.8996 |  |  | 10.6587 |  |  | 16.9955 | 16.1976 | 15.1773 | 16.4786 | 15.7647 | 14.8799 | 10.6437 | 10.7575 | 11.5977 | 11.4621 | 9.0879 |  | 10.8242 | 7.9513 | 10.1621 | 9.1143 | 11.2332 | 12.4993 |  | 12.4555 |  |  | 11.8978 | 12.6407 | 12.6586 | [6 empty] | 12.5781 |  |  | 11.2767 |  |  | 9.2603 | 10.3747 | 12.2698 | 7.4369 | 9.2797 | 12.7249 | 7.711 | 9.5878 | 12.555 | 9.173 | 10.4117 | 7.5948 | 10.4455 | 8.1702 | 10.1093 | 7.9428 | 9.7404 | 13.5132 | 10.6842 | 10.4102 | 11.7413 | 8.1923 | 9.8174 | 12.9839 | 7.9201 | 10.3992 | 9.7618 | 9.9579 | 8.3784 | 10.2135 | 0.079532 | 20.9566 | 0.034268 | 0.048645 | -38.154 | 3.1218 | -1.41 | 0.4 | 0.23534 | 0.28353 | 0.33231 | 0.35588 | -0.20185 | -0.42171 | 0.66048 | 0.41695 | 0.42671 | 0.42971 | 0.3614 | 0.56333 | 0.43666 | 0.42789
42810.4331 | -600 | 18.6876 | 18.712 | 18.6743 | 18.7043 | 18.051 | 16.716 | 14.7914 | 16.7863 | 17.2747 | 17.3773 | 17.3925 | 16.954 | 16.0172 | 14.6316 | 15.1553 | 15.1117 | 15.6514 | 13.4909 | 13.6058 | 14.1894 |  |  |  | 16.6871 | 16.0285 | 15.154 | 10.2626 | 9.8116 | 9.8052 | 17.3986 | 16.4968 | 15.2884 | 16.9923 | 16.2853 | 15.2961 | 10.9342 | 11.8687 |  | 12.3864 | 10.5834 | 10.4773 | 8.4757 |  | 6.3846 | 6.3356 | 5.8413 | 5.9074 | 5.8687 | 5.9083 | 6.342 | 5.1491 | 6.3801 | 4.8175 | 6.6685 | 8.2404 | 42.4033 | 46.7541 | 42.9703 | 15.4136 |  |  | 0.054103 | -0.21939 | -0.01852 | 0.15639 | -0.12994 | 0.008084 | 0.39483 | -0.13553 | -0.51509 | 1.0644 | -0.21768 | 8.8724 | 8.8737 | 2.0086 | 15.9669 | 16.8358 | 17.3564 | 17.6731 | 17.6421 | 16.6348 | 14.9873 | 16.9178 | 17.2372 | 17.5252 | 17.5674 | 17.3117 | 16.5296 | 14.7706 | 6.5493 | 8.5263 | 5.6992 | 5.82 | 6.0284 | 6.6531 | 7.6211 | 16.0285 | 15.6534 | 15.5015 | 14.4412 | 14.3193 | 14.2616 |  |  |  | 10.7972 | 9.266 | 8.991 | 8.6607 | -0.015551 | -0.0012926 | 12.9009 |  |  | 10.6654 |  |  | 16.9909 | 16.1952 | 15.1796 | 16.4708 | 15.7651 | 14.8806 | 10.6406 | 10.7605 | 11.596 | 11.4596 | 9.0788 |  | 10.8221 | 7.9777 | 10.1549 | 9.1244 | 11.2342 | 12.4855 |  | 12.4417 |  |  | 11.8592 | 12.6313 | 12.6543 | [6 empty] | 12.562 |  |  | 11.2736 |  |  | 9.2381 | 10.3635 | 12.2674 | 7.4343 | 9.2785 | 12.725 | 7.7003 | 9.5855 | 12.5481 | 9.1683 | 10.4022 | 7.5988 | 10.4488 | 8.1637 | 10.1015 | 7.9455 | 9.7409 | 13.5108 | 10.675 | 10.3997 | 11.7547 | 8.1808 | 9.8058 | 12.9792 | 7.9259 | 10.3973 | 9.7556 | 9.9651 | 8.3802 | 10.2086 | -0.031599 | 20.9556 | 0.034451 | 0.048761 | -38.0976 | 3.1217 | -1.33 | 0.31 | 0.27267 | -0.5457 | -0.15855 | 0.46074 | -0.41966 | 0.10467 | 0.73151 | 0.41713 | 0.42573 | 0.42946 | 0.35906 | 0.56591 | 0.43758 | 0.42793
42810.4331 | -599 | 18.6797 | 18.7059 | 18.6756 | 18.6997 | 18.0569 | 16.7229 | 14.7905 | 16.7839 | 17.2672 | 17.3693 | 17.3876 | 16.95 | 16.0094 | 14.626 | 15.1459 | 15.1063 | 15.6347 | 13.4792 | 13.5973 | 14.1863 |  |  |  | 16.6796 | 16.0237 | 15.1507 | 10.2499 | 9.7983 | 9.8091 | 17.384 | 16.4909 | 15.2913 | 16.9861 | 16.2697 | 15.2906 | 10.9233 | 11.8054 |  | 12.3771 | 10.5729 | 10.4675 | 8.456 |  | 6.3941 | 6.3367 | 5.8437 | 5.9054 | 5.8788 | 5.9239 | 6.3572 | 5.1697 | 6.3778 | 4.8178 | 6.6687 | 8.2405 | 42.3908 | 46.7719 | 42.973 | 15.4058 |  |  | 0.14544 | -0.085993 | 0.15759 | -0.15705 | -0.05832 | -0.45913 | 0.27523 | -0.1927 | -0.70677 | -0.18585 | -0.19086 | 8.8758 | 8.877 | 2.0083 | 15.9618 | 16.8383 | 17.358 | 17.6783 | 17.6401 | 16.6373 | 14.9959 | 16.9212 | 17.2417 | 17.5295 | 17.5684 | 17.3158 | 16.5369 | 14.7781 | 6.5371 | 8.5201 | 5.6601 | 5.8016 | 5.9685 | 6.6459 | 7.6214 | 16.029 | 15.656 | 15.5084 | 14.4331 | 14.3239 | 14.2603 |  |  |  | 10.7942 | 9.271 | 8.99 | 8.6596 | 0.024563 | -0.13153 | 12.9022 |  |  | 10.6671 |  |  | 16.9962 | 16.1876 | 15.1772 | 16.4719 | 15.7638 | 14.8807 | 10.6348 | 10.752 | 11.5888 | 11.4526 | 9.0762 |  | 10.8182 | 8.003 | 10.1553 | 9.1253 | 11.2333 | 12.4771 |  | 12.4515 |  |  | 11.8768 | 12.6565 | 12.659 | [6 empty] | 12.5771 |  |  | 11.2684 |  |  | 9.2356 | 10.3664 | 12.2749 | 7.4454 | 9.2886 | 12.7389 | 7.7022 | 9.5913 | 12.5521 | 9.1774 | 10.4064 | 7.6077 | 10.457 | 8.1715 | 10.103 | 7.9477 | 9.7313 | 13.5015 | 10.6616 | 10.3887 | 11.765 | 8.1781 | 9.7985 | 12.9689 | 7.9324 | 10.3933 | 9.7579 | 9.9744 | 8.3769 | 10.2147 | 0.050834 | 20.9546 | 0.034113 | 0.04816 | -38.1272 | 3.1218 | -1.07 | 0.33 | 0.44707 | -0.34165 | 0.4625 | -0.46171 | -0.28115 | -0.78885 | 0.61077 | 0.41708 | 0.42505 | 0.42941 | 0.35958 | 0.57029 | 0.43777 | 0.42786
42810.4331 | -598 | 18.6751 | 18.699 | 18.6677 | 18.6858 | 18.0442 | 16.7089 | 14.7843 | 16.7748 | 17.264 | 17.3652 | 17.3794 | 16.948 | 15.9965 | 14.6182 | 15.1469 | 15.1109 | 15.6435 | 13.491 | 13.6044 | 14.1874 |  |  |  | 16.6848 | 16.0243 | 15.1459 | 10.2564 | 9.7988 | 9.8139 | 17.3935 | 16.4979 | 15.2897 | 16.9834 | 16.2714 | 15.2906 | 10.9252 | 11.7508 |  | 12.3752 | 10.5682 | 10.4661 | 8.4811 |  | 6.4102 | 6.3467 | 5.8377 | 5.9093 | 5.8812 | 5.9266 | 6.3433 | 5.156 | 6.374 | 4.7987 | 6.6569 | 8.2399 | 42.3814 | 46.7716 | 42.9702 | 15.4019 |  |  | 0.048187 | -0.063653 | 0.01368 | -0.034826 | -0.025464 | -0.16934 | 0.47237 | -0.1835 | -0.0021252 | -0.073812 | -0.28842 | 8.8789 | 8.8804 | 2.0086 | 15.9617 | 16.8296 | 17.3545 | 17.6809 | 17.6435 | 16.6375 | 14.9904 | 16.9144 | 17.2379 | 17.5232 | 17.5664 | 17.3163 | 16.5363 | 14.767 | 6.5421 | 8.5325 | 5.666 | 5.7902 | 5.9449 | 6.653 | 7.6258 | 16.0299 | 15.6563 | 15.5022 | 14.4361 | 14.317 | 14.2646 |  |  |  | 10.8025 | 9.2626 | 8.9868 | 8.6334 | 0.0057216 | -0.1351 | 12.9045 |  |  | 10.6743 |  |  | 16.9925 | 16.1971 | 15.174 | 16.484 | 15.7652 | 14.8826 | 10.6364 | 10.7572 | 11.5864 | 11.4421 | 9.0782 |  | 10.8114 | 8.0485 | 10.1586 | 9.1046 | 11.2336 | 12.4584 |  | 12.4405 |  |  | 11.892 | 12.6533 | 12.6574 | [6 empty] | 12.588 |  |  | 11.2623 |  |  | 9.2185 | 10.3599 | 12.2782 | 7.4537 | 9.2775 | 12.7342 | 7.6943 | 9.5813 | 12.5416 | 9.1672 | 10.3935 | 7.6091 | 10.4519 | 8.1648 | 10.1085 | 7.9441 | 9.7204 | 13.5064 | 10.6556 | 10.3872 | 11.7513 | 8.1743 | 9.7881 | 12.9603 | 7.9319 | 10.3925 | 9.7508 | 9.9796 | 8.3753 | 10.208 | 0.034463 | 20.955 | 0.033602 | 0.048204 | -38.153 | 3.1217 | -0.85 | 0.32 | 0.25733 | -0.29394 | 0.13627 | -0.21742 | -0.18578 | -0.47908 | 0.80015 | 0.4168 | 0.42389 | 0.42999 | 0.35986 | 0.57014 | 0.43714 | 0.42886
42810.4331 | -597 | 18.682 | 18.7076 | 18.6702 | 18.6872 | 18.0463 | 16.7069 | 14.7835 | 16.7779 | 17.2673 | 17.3672 | 17.3835 | 16.9554 | 16.0064 | 14.6134 | 15.1474 | 15.1108 | 15.6412 | 13.4888 | 13.6051 | 14.184 |  |  |  | 16.6817 | 16.0247 | 15.1492 | 10.2485 | 9.802 | 9.8232 | 17.3903 | 16.4998 | 15.2873 | 16.9852 | 16.2732 | 15.2869 | 10.926 | 11.6987 |  | 12.3822 | 10.5695 | 10.4744 | 8.5132 |  | 6.4327 | 6.3631 | 5.8429 | 5.9179 | 5.8766 | 5.9177 | 6.3452 | 5.1101 | 6.3811 | 4.7934 | 6.6715 | 8.2431 | 42.3725 | 46.7711 | 42.958 | 15.3914 |  |  | -0.2692 | 0.024403 | 0.25944 | 0.13208 | -0.27517 | -0.39144 | 0.15958 | -0.25118 | -0.6805 | -0.48082 | -0.22484 | 8.889 | 8.8902 | 2.0085 | 15.9717 | 16.8447 | 17.3627 | 17.6814 | 17.6444 | 16.6419 | 14.9981 | 16.9149 | 17.2412 | 17.5336 | 17.568 | 17.3182 | 16.53 | 14.7729 | 6.5261 | 8.5346 | 5.6692 | 5.7884 | 5.9218 | 6.655 | 7.6249 | 16.037 | 15.6541 | 15.4998 | 14.4451 | 14.312 | 14.2628 |  |  |  | 10.8032 | 9.2692 | 8.9778 | 8.6165 | 0.1907 | -0.045896 | 12.9011 |  |  | 10.6667 |  |  | 16.99 | 16.1943 | 15.1736 | 16.4684 | 15.765 | 14.8724 | 10.6365 | 10.7499 | 11.5791 | 11.4339 | 9.0856 |  | 10.8194 | 8.0307 | 10.1501 | 9.083 | 11.2326 | 12.439 |  | 12.4458 |  |  | 11.8852 | 12.6497 | 12.6556 | [6 empty] | 12.5925 |  |  | 11.2634 |  |  | 9.2085 | 10.3556 | 12.2781 | 7.462 | 9.2746 | 12.7385 | 7.7003 | 9.5797 | 12.532 | 9.1737 | 10.3912 | 7.6169 | 10.4529 | 8.1647 | 10.1096 | 7.9449 | 9.7199 | 13.4986 | 10.6514 | 10.3911 | 11.7459 | 8.167 | 9.7931 | 12.9653 | 7.9401 | 10.3919 | 9.7462 | 9.9811 | 8.3709 | 10.2106 | -0.18086 | 20.9543 | 0.033797 | 0.047813 | -38.1206 | 3.1218 | -0.82 | 0.26 | -0.60824 | 0.18201 | 0.59345 | 0.42344 | -0.61069 | -0.72838 | 0.46506 | 0.41686 | 0.42411 | 0.43056 | 0.36187 | 0.56969 | 0.43627 | 0.42935
42810.4331 | -596 | 18.68 | 18.7059 | 18.6728 | 18.6877 | 18.0484 | 16.7116 | 14.7894 | 16.7804 | 17.2717 | 17.3669 | 17.393 | 16.9448 | 16.0083 | 14.6195 | 15.1491 | 15.1128 | 15.6425 | 13.4892 | 13.6094 | 14.1865 |  |  |  | 16.6832 | 16.0241 | 15.1538 | 10.2525 | 9.8028 | 9.8417 | 17.3897 | 16.5008 | 15.2927 | 16.9908 | 16.2773 | 15.2922 | 10.9345 | 11.6592 |  | 12.3801 | 10.5743 | 10.4746 | 8.5599 |  | 6.4456 | 6.3646 | 5.8555 | 5.9204 | 5.8718 | 5.9214 | 6.3227 | 5.074 | 6.3886 | 4.7797 | 6.6692 | 8.2426 | 42.3574 | 46.7795 | 42.9389 | 15.3836 |  |  | -0.066805 | -0.23056 | 0.099104 | 0.032854 | -0.089204 | -0.3001 | 0.44477 | -0.1881 | -0.72273 | -0.52992 | -0.15231 | 8.8819 | 8.8831 | 2.0086 | 15.9667 | 16.8336 | 17.3542 | 17.6744 | 17.6394 | 16.6279 | 14.9872 | 16.9112 | 17.2363 | 17.5217 | 17.5658 | 17.3122 | 16.5304 | 14.761 | 6.5202 | 8.5333 | 5.6498 | 5.7987 | 5.9064 | 6.6549 | 7.6228 | 16.0383 | 15.6589 | 15.502 | 14.4429 | 14.3149 | 14.2642 |  |  |  | 10.7951 | 9.2753 | 8.9808 | 8.6085 | 0.23466 | 0.054603 | 12.904 |  |  | 10.6772 |  |  | 16.9915 | 16.1987 | 15.1763 | 16.4779 | 15.768 | 14.8846 | 10.6371 | 10.7562 | 11.5768 | 11.4367 | 9.0914 |  | 10.8097 | 8.0394 | 10.1444 | 9.0722 | 11.2264 | 12.4076 |  | 12.4407 |  |  | 11.8551 | 12.6441 | 12.663 | [6 empty] | 12.5843 |  |  | 11.2692 |  |  | 9.2028 | 10.3552 | 12.2826 | 7.4828 | 9.2875 | 12.7491 | 7.7068 | 9.5828 | 12.5339 | 9.1856 | 10.3902 | 7.6356 | 10.4574 | 8.1649 | 10.1112 | 7.9454 | 9.727 | 13.4951 | 10.6503 | 10.385 | 11.7449 | 8.1626 | 9.7866 | 12.9667 | 7.9491 | 10.3873 | 9.7487 | 9.9827 | 8.37 | 10.2229 | -0.016961 | 20.9541 | 0.033665 | 0.048356 | -38.1707 | 3.1218 | -0.71 | 0.42 | -0.30301 | -0.55945 | 0.36679 | 0.21119 | -0.34771 | -0.63776 | 0.77641 | 0.41638 | 0.42368 | 0.43065 | 0.36251 | 0.5716 | 0.43525 | 0.42931
42810.4331 | -595 | 18.6778 | 18.7044 | 18.6722 | 18.6917 | 18.0442 | 16.7139 | 14.7896 | 16.7785 | 17.2687 | 17.3656 | 17.3882 | 16.9438 | 16.0017 | 14.6273 | 15.1452 | 15.1179 | 15.6512 | 13.4956 | 13.6105 | 14.1896 |  |  |  | 16.6874 | 16.0346 | 15.1535 | 10.2533 | 9.7942 | 9.8577 | 17.3912 | 16.4968 | 15.287 | 16.9935 | 16.2726 | 15.2883 | 10.9238 | 11.6353 |  | 12.3752 | 10.5729 | 10.4748 | 8.6112 |  | 6.4355 | 6.3623 | 5.8633 | 5.9191 | 5.8754 | 5.9132 | 6.2887 | 4.9998 | 6.3903 | 4.8144 | 6.6731 | 8.2363 | 42.354 | 46.7971 | 42.9175 | 15.3766 |  |  | -0.079293 | -0.3541 | 0.15102 | 0.16034 | -0.020864 | -0.1378 | 0.4796 | -0.11122 | -0.65092 | 0.55643 | -0.28584 | 8.8815 | 8.8827 | 2.0087 | 15.9643 | 16.8341 | 17.3682 | 17.6838 | 17.6453 | 16.6358 | 14.9961 | 16.9241 | 17.237 | 17.5285 | 17.5737 | 17.3161 | 16.532 | 14.7703 | 6.5113 | 8.5242 | 5.6462 | 5.8103 | 5.9111 | 6.6574 | 7.622 | 16.0362 | 15.6438 | 15.4992 | 14.4347 | 14.31 | 14.2564 |  |  |  | 10.7881 | 9.274 | 8.9712 | 8.6185 | 0.027197 | -0.0093852 | 12.901 |  |  | 10.6802 |  |  | 16.9923 | 16.1888 | 15.1732 | 16.4797 | 15.7663 | 14.8786 | 10.6475 | 10.7501 | 11.5646 | 11.4326 | 9.1192 |  | 10.8074 | 8.0751 | 10.1442 | 9.0743 | 11.224 | 12.392 |  | 12.4363 |  |  | 11.8536 | 12.6455 | 12.6707 | [6 empty] | 12.5665 |  |  | 11.2613 |  |  | 9.197 | 10.3601 | 12.2825 | 7.4975 | 9.2962 | 12.7491 | 7.7045 | 9.5823 | 12.5345 | 9.1908 | 10.3838 | 7.6499 | 10.4596 | 8.1608 | 10.1186 | 7.9438 | 9.7266 | 13.4868 | 10.6475 | 10.3771 | 11.7313 | 8.1423 | 9.7746 | 12.9582 | 7.9515 | 10.3877 | 9.7422 | 9.9783 | 8.3678 | 10.2227 | -0.028517 | 20.9559 | 0.033883 | 0.047733 | -38.1413 | 3.1217 | -0.59 | 0.25 | -0.33013 | -0.69331 | 0.45277 | 0.46654 | -0.16816 | -0.43215 | 0.80622 | 0.41553 | 0.42268 | 0.43052 | 0.36378 | 0.5719 | 0.43348 | 0.4288
42810.4332 | -594 | 18.6722 | 18.7094 | 18.671 | 18.6878 | 18.0409 | 16.7058 | 14.7805 | 16.7776 | 17.2608 | 17.3546 | 17.3848 | 16.9407 | 15.998 | 14.6181 | 15.1474 | 15.1178 | 15.6519 | 13.4936 | 13.6061 | 14.1949 |  |  |  | 16.6941 | 16.0399 | 15.1604 | 10.2582 | 9.784 | 9.8515 | 17.3877 | 16.4975 | 15.289 | 16.9914 | 16.2737 | 15.285 | 10.925 | 11.5932 |  | 12.3749 | 10.5768 | 10.4695 | 8.6703 |  | 6.436 | 6.3645 | 5.8597 | 5.9252 | 5.8747 | 5.9166 | 6.2701 | 4.9209 | 6.3778 | 4.8139 | 6.6669 | 8.2419 | 42.3443 | 46.8078 | 42.8944 | 15.3741 |  |  | -0.008981 | -0.098481 | 0.15562 | -0.017742 | 0.011336 | 0.14608 | 0.5821 | -0.38195 | -0.43492 | -0.85343 | -0.28643 | 8.8856 | 8.8869 | 2.0085 | 15.9578 | 16.8385 | 17.362 | 17.6787 | 17.6419 | 16.6339 | 14.9949 | 16.9176 | 17.2415 | 17.5278 | 17.5707 | 17.3111 | 16.5328 | 14.7663 | 6.4916 | 8.5144 | 5.6457 | 5.8141 | 5.8974 | 6.6544 | 7.6214 | 16.031 | 15.6454 | 15.4982 | 14.4429 | 14.3147 | 14.2539 |  |  |  | 10.7893 | 9.2747 | 8.9704 | 8.6361 | 0.025171 | -0.10725 | 12.8921 |  |  | 10.6741 |  |  | 16.9921 | 16.1901 | 15.1734 | 16.4769 | 15.7603 | 14.8741 | 10.6494 | 10.749 | 11.5615 | 11.4194 | 9.0903 |  | 10.8106 | 8.12 | 10.1501 | 9.0742 | 11.2279 | 12.3789 |  | 12.4339 |  |  | 11.8677 | 12.6408 | 12.6709 | [6 empty] | 12.5506 |  |  | 11.2655 |  |  | 9.1896 | 10.3707 | 12.2892 | 7.5123 | 9.2994 | 12.7453 | 7.7063 | 9.5844 | 12.5289 | 9.1986 | 10.3937 | 7.6634 | 10.4612 | 8.1653 | 10.1179 | 7.9326 | 9.7285 | 13.4815 | 10.6455 | 10.3813 | 11.7294 | 8.134 | 9.7794 | 12.9614 | 7.9643 | 10.3943 | 9.7385 | 9.9778 | 8.3748 | 10.226 | 0.05719 | 20.9536 | 0.033895 | 0.048276 | -38.1743 | 3.1218 | -0.75 | 0.37 | -0.1111 | -0.36563 | 0.45962 | -0.15519 | 0.12395 | 0.44495 | 0.88822 | 0.41644 | 0.42163 | 0.43065 | 0.36563 | 0.57189 | 0.43187 | 0.42835
42810.4332 | -593 | 18.6716 | 18.7075 | 18.674 | 18.6843 | 18.0502 | 16.7069 | 14.7826 | 16.7796 | 17.2648 | 17.3643 | 17.3836 | 16.9542 | 16.0044 | 14.6225 | 15.1537 | 15.1086 | 15.6509 | 13.491 | 13.6076 | 14.1963 |  |  |  | 16.6891 | 16.0246 | 15.1557 | 10.2551 | 9.7745 | 9.8417 | 17.391 | 16.498 | 15.2869 | 16.9923 | 16.279 | 15.2909 | 10.9315 | 11.571 |  | 12.3799 | 10.5865 | 10.4824 | 8.7133 |  | 6.425 | 6.3597 | 5.8671 | 5.9275 | 5.8764 | 5.9135 | 6.247 | 4.9107 | 6.3742 | 4.8349 | 6.664 | 8.2348 | 42.342 | 46.7981 | 42.8523 | 15.3622 |  |  | -0.008981 | -0.1517 | -0.065832 | 0.12222 | 0.036304 | -0.46241 | 0.73127 | -0.11187 | -0.72331 | -0.22718 | -0.18629 | 8.8859 | 8.8871 | 2.0085 | 15.96 | 16.8424 | 17.3652 | 17.6809 | 17.6435 | 16.6394 | 14.9951 | 16.9131 | 17.2426 | 17.5267 | 17.5667 | 17.3096 | 16.5282 | 14.7624 | 6.4912 | 8.5238 | 5.618 | 5.8201 | 5.9079 | 6.6539 | 7.6256 | 16.0261 | 15.6455 | 15.4945 | 14.44 | 14.3138 | 14.2567 |  |  |  | 10.7852 | 9.2717 | 8.976 | 8.643 | 0.052522 | -0.10349 | 12.8963 |  |  | 10.6747 |  |  | 16.9944 | 16.1924 | 15.1734 | 16.4768 | 15.7624 | 14.8781 | 10.6662 | 10.7498 | 11.5537 | 11.4167 | 9.0644 |  | 10.8078 | 8.1566 | 10.1356 | 9.1075 | 11.2248 | 12.3512 |  | 12.4304 |  |  | 11.8669 | 12.6336 | 12.6516 | [6 empty] | 12.5609 |  |  | 11.2688 |  |  | 9.1888 | 10.3621 | 12.2866 | 7.5293 | 9.3112 | 12.7499 | 7.7112 | 9.5771 | 12.5137 | 9.1989 | 10.3998 | 7.6748 | 10.4655 | 8.1746 | 10.1164 | 7.9216 | 9.7313 | 13.4752 | 10.6377 | 10.3709 | 11.7242 | 8.1372 | 9.7787 | 12.9509 | 7.973 | 10.3924 | 9.7302 | 9.9776 | 8.3844 | 10.2269 | 0.032537 | 20.9577 | 0.0339 | 0.048037 | -38.1416 | 3.1218 | -0.89 | 0.37 | -0.1111 | -0.4538 | -0.29894 | 0.40732 | 0.22182 | -0.79165 | 0.99554 | 0.41706 | 0.42013 | 0.42962 | 0.36562 | 0.57545 | 0.43089 | 0.42803
42810.4332 | -592 | 18.6734 | 18.7159 | 18.6798 | 18.6981 | 18.0545 | 16.7099 | 14.78 | 16.7785 | 17.2708 | 17.3623 | 17.3758 | 16.9467 | 16.0061 | 14.6194 | 15.1472 | 15.1051 | 15.6515 | 13.4842 | 13.6008 | 14.1905 |  |  |  | 16.6857 | 16.0209 | 15.1532 | 10.2547 | 9.7623 | 9.8509 | 17.383 | 16.4956 | 15.2862 | 16.993 | 16.2715 | 15.2891 | 10.9301 | 11.565 |  | 12.3765 | 10.5922 | 10.4849 | 8.6958 |  | 6.4477 | 6.3763 | 5.8764 | 5.9523 | 5.8864 | 5.9183 | 6.2484 | 4.8622 | 6.3863 | 4.8187 | 6.6764 | 8.2336 | 42.3387 | 46.7928 | 42.8214 | 15.3567 |  |  | 0.056731 | -0.003197 | 0.19767 | 0.050598 | 0.007392 | -0.28762 | 0.36657 | -0.059304 | 1.3677 | -0.37509 | -0.11158 | 8.8865 | 8.888 | 2.0084 | 15.9601 | 16.8427 | 17.3594 | 17.6758 | 17.6456 | 16.6307 | 14.994 | 16.91 | 17.24 | 17.5322 | 17.5674 | 17.3107 | 16.5248 | 14.7581 | 6.4918 | 8.5233 | 5.5846 | 5.8148 | 5.8981 | 6.6524 | 7.6337 | 16.0306 | 15.6472 | 15.4951 | 14.4381 | 14.3095 | 14.2566 |  |  |  | 10.7834 | 9.2724 | 8.9769 | 8.6501 | -0.06296 | 0.025996 | 12.9067 |  |  | 10.6836 |  |  | 16.995 | 16.1901 | 15.1809 | 16.482 | 15.7643 | 14.8843 | 10.6822 | 10.7588 | 11.5571 | 11.4274 | 9.069 |  | 10.8011 | 8.19 | 10.1455 | 9.1091 | 11.2239 | 12.3171 |  | 12.4335 |  |  | 11.8615 | 12.64 | 12.6251 | [6 empty] | 12.5702 |  |  | 11.2604 |  |  | 9.1908 | 10.3672 | 12.2864 | 7.5494 | 9.3169 | 12.7576 | 7.7216 | 9.5837 | 12.5173 | 9.2058 | 10.3954 | 7.6943 | 10.4767 | 8.19 | 10.1234 | 7.9205 | 9.7286 | 13.4765 | 10.6402 | 10.37 | 11.7163 | 8.1294 | 9.7741 | 12.9445 | 7.977 | 10.4051 | 9.7299 | 9.9763 | 8.3853 | 10.2321 | -0.032947 | 20.9545 | 0.033418 | 0.048421 | -38.1247 | 3.1218 | -0.65 | 0.32 | 0.27924 | -0.065879 | 0.51803 | 0.26209 | 0.10009 | -0.62436 | 0.70486 | 0.41671 | 0.41953 | 0.42955 | 0.36537 | 0.58011 | 0.43134 | 0.42777
42810.4332 | -591 | 18.6765 | 18.7111 | 18.6756 | 18.6844 | 18.0447 | 16.7044 | 14.7859 | 16.7872 | 17.2747 | 17.37 | 17.3832 | 16.9427 | 16.0101 | 14.6206 | 15.1462 | 15.1093 | 15.6415 | 13.488 | 13.6021 | 14.1811 |  |  |  | 16.6832 | 16.0277 | 15.1521 | 10.2412 | 9.7584 | 9.8433 | 17.3829 | 16.4984 | 15.2874 | 16.9845 | 16.2755 | 15.2933 | 10.9314 | 11.585 |  | 12.3742 | 10.5984 | 10.4943 | 8.7097 |  | 6.4517 | 6.3871 | 5.8789 | 5.9586 | 5.8909 | 5.925 | 6.2451 | 4.8171 | 6.3809 | 4.7915 | 6.6697 | 8.2351 | 42.3413 | 46.8078 | 42.8018 | 15.3618 |  |  | -0.10558 | -0.14973 | 0.21278 | -0.045998 | -0.053064 | 0.068536 | 0.51442 | -0.097416 | 0.075909 | -0.52027 | -0.22682 | 8.8789 | 8.8799 | 2.0088 | 15.9629 | 16.8403 | 17.3541 | 17.6788 | 17.6524 | 16.6433 | 14.9976 | 16.9179 | 17.2422 | 17.5356 | 17.5755 | 17.3149 | 16.533 | 14.7655 | 6.5053 | 8.5181 | 5.5735 | 5.8074 | 5.889 | 6.6604 | 7.6367 | 16.028 | 15.6462 | 15.4923 | 14.4387 | 14.3148 | 14.2613 |  |  |  | 10.782 | 9.2717 | 8.9754 | 8.6944 | 0.06245 | 0.037853 | 12.8856 |  |  | 10.6757 |  |  | 16.986 | 16.1781 | 15.1684 | 16.4635 | 15.7591 | 14.8793 | 10.6732 | 10.7504 | 11.5396 | 11.4002 | 9.0831 |  | 10.8089 | 8.2812 | 10.1479 | 9.1216 | 11.2203 | 12.2819 |  | 12.4362 |  |  | 11.8646 | 12.6584 | 12.6265 | [6 empty] | 12.5808 |  |  | 11.2695 |  |  | 9.1797 | 10.3516 | 12.2811 | 7.5522 | 9.316 | 12.7533 | 7.7218 | 9.5901 | 12.4961 | 9.197 | 10.3948 | 7.6899 | 10.468 | 8.1927 | 10.1121 | 7.9096 | 9.7149 | 13.4612 | 10.6264 | 10.3627 | 11.7104 | 8.122 | 9.7631 | 12.9313 | 7.9704 | 10.3997 | 9.711 | 9.9703 | 8.3831 | 10.2225 | 0.19837 | 20.953 | 0.03343 | 0.048319 | -38.1446 | 3.1218 | -0.42 | 0.25 | -0.38093 | -0.45086 | 0.53747 | -0.24989 | -0.26818 | 0.30478 | 0.835 | 0.41658 | 0.41708 | 0.42908 | 0.3648 | 0.58169 | 0.43099 | 0.42649
42810.4332 | -590 | 18.6718 | 18.6987 | 18.6705 | 18.6891 | 18.0464 | 16.6986 | 14.7803 | 16.7829 | 17.2706 | 17.3599 | 17.3803 | 16.945 | 15.9981 | 14.6182 | 15.1459 | 15.1108 | 15.6478 | 13.4924 | 13.6066 | 14.1906 |  |  |  | 16.685 | 16.03 | 15.1487 | 10.2457 | 9.7556 | 9.821 | 17.381 | 16.4926 | 15.2764 | 16.9839 | 16.2677 | 15.2856 | 10.9193 | 11.5904 |  | 12.3578 | 10.5844 | 10.4864 | 8.719 |  | 6.453 | 6.3817 | 5.8873 | 5.9647 | 5.902 | 5.9374 | 6.2669 | 4.8195 | 6.3831 | 4.7441 | 6.6703 | 8.2329 | 42.3305 | 46.8253 | 42.7805 | 15.37 |  |  | 0.14478 | -0.22859 | 0.10896 | -0.088054 | -0.1444 | -0.21139 | 0.42374 | -0.048792 | -0.51626 | -0.1485 | -0.26418 | 8.8814 | 8.8822 | 2.0085 | 15.9579 | 16.8325 | 17.3596 | 17.6821 | 17.6501 | 16.6398 | 15 | 16.9157 | 17.24 | 17.5276 | 17.5625 | 17.3098 | 16.5348 | 14.7595 | 6.5182 | 8.5143 | 5.5519 | 5.7863 | 5.8897 | 6.6642 | 7.6471 | 16.0239 | 15.6417 | 15.4933 | 14.435 | 14.3144 | 14.2552 |  |  |  | 10.7885 | 9.2748 | 8.9796 | 8.7196 | 0.26545 | 0.092431 | 12.8969 |  |  | 10.6847 |  |  | 16.9942 | 16.196 | 15.1782 | 16.4656 | 15.7572 | 14.8808 | 10.7022 | 10.7548 | 11.5401 | 11.4016 | 9.0952 |  | 10.7985 | 8.393 | 10.1409 | 9.1268 | 11.221 | 12.2513 |  | 12.4292 |  |  | 11.8528 | 12.6594 | 12.6221 | [6 empty] | 12.555 |  |  | 11.2614 |  |  | 9.1618 | 10.3488 | 12.2665 | 7.5504 | 9.3141 | 12.7419 | 7.7287 | 9.595 | 12.4775 | 9.2018 | 10.3919 | 7.6918 | 10.4691 | 8.1956 | 10.1105 | 7.9104 | 9.72 | 13.4575 | 10.6234 | 10.3563 | 11.7133 | 8.112 | 9.755 | 12.934 | 7.976 | 10.4049 | 9.7061 | 9.9567 | 8.3809 | 10.214 | 0.045249 | 20.9559 | 0.033401 | 0.048898 | -38.1546 | 3.1218 | -0.35 | 0.38 | 0.44606 | -0.55707 | 0.38461 | -0.34575 | -0.44241 | -0.53528 | 0.75786 | 0.4159 | 0.41374 | 0.42896 | 0.36381 | 0.58529 | 0.43033 | 0.42601
42810.4332 | -589 | 18.6681 | 18.708 | 18.6655 | 18.6883 | 18.0468 | 16.7042 | 14.7809 | 16.7848 | 17.2636 | 17.3627 | 17.3827 | 16.949 | 16.0039 | 14.6194 | 15.1476 | 15.1073 | 15.6431 | 13.4879 | 13.6009 | 14.1879 |  |  |  | 16.6791 | 16.0242 | 15.1439 | 10.2469 | 9.7469 | 9.8103 | 17.3836 | 16.4863 | 15.2814 | 16.9865 | 16.2731 | 15.2814 | 10.9171 | 11.611 |  | 12.3585 | 10.5888 | 10.4923 | 8.7415 |  | 6.4539 | 6.3855 | 5.8876 | 5.9611 | 5.9074 | 5.9367 | 6.2589 | 4.8087 | 6.3845 | 4.7251 | 6.671 | 8.2334 | 42.3282 | 46.8455 | 42.7669 | 15.3858 |  |  | -0.056949 | -0.042625 | 0.00382 | 0.15245 | 0.050104 | -0.16868 | 0.48288 | -0.20847 | -0.39269 | -0.25571 | -0.20258 | 8.8773 | 8.8784 | 2.0087 | 15.9556 | 16.8329 | 17.3543 | 17.6801 | 17.6472 | 16.6348 | 14.9944 | 16.909 | 17.2436 | 17.5278 | 17.5684 | 17.3122 | 16.5296 | 14.7658 | 6.5809 | 8.5292 | 5.5556 | 5.7535 | 5.8899 | 6.6675 | 7.6376 | 16.0284 | 15.6581 | 15.504 | 14.4344 | 14.3173 | 14.2597 |  |  |  | 10.7826 | 9.2932 | 8.9797 | 8.7297 | 0.17793 | -0.014843 | 12.8873 |  |  | 10.6789 |  |  | 16.9805 | 16.1872 | 15.1708 | 16.4656 | 15.753 | 14.863 | 10.6978 | 10.742 | 11.5265 | 11.3869 | 9.1316 |  | 10.7929 | 8.4748 | 10.1415 | 9.1384 | 11.215 | 12.2147 |  | 12.4309 |  |  | 11.8625 | 12.6589 | 12.6303 | [6 empty] | 12.5684 |  |  | 11.2706 |  |  | 9.1373 | 10.3485 | 12.268 | 7.5625 | 9.3155 | 12.7521 | 7.7211 | 9.5846 | 12.4673 | 9.194 | 10.3906 | 7.7038 | 10.4644 | 8.2006 | 10.1125 | 7.9055 | 9.7208 | 13.4652 | 10.6326 | 10.3624 | 11.7106 | 8.1143 | 9.7632 | 12.9367 | 7.9913 | 10.4072 | 9.7173 | 9.971 | 8.3929 | 10.2263 | -0.0055976 | 20.9546 | 0.033246 | 0.049419 | -38.1256 | 3.1218 | -0.31 | 0.31 | -0.27975 | -0.24056 | 0.072014 | 0.45493 | 0.2606 | -0.47815 | 0.80901 | 0.41471 | 0.41149 | 0.42844 | 0.35722 | 0.58378 | 0.42964 | 0.42553
42810.4332 | -588 | 18.669 | 18.7083 | 18.6703 | 18.6846 | 18.0407 | 16.7086 | 14.7774 | 16.7821 | 17.2637 | 17.3653 | 17.3805 | 16.9416 | 16.001 | 14.6167 | 15.1425 | 15.1097 | 15.6418 | 13.4895 | 13.6028 | 14.187 |  |  |  | 16.6828 | 16.0216 | 15.1471 | 10.2261 | 9.7435 | 9.852 | 17.3814 | 16.4883 | 15.2821 | 16.9913 | 16.2693 | 15.2819 | 10.9208 | 11.617 |  | 12.3636 | 10.5974 | 10.4898 | 8.7727 |  | 6.4479 | 6.3807 | 5.8872 | 5.942 | 5.9021 | 5.9322 | 6.2515 | 4.776 | 6.387 | 4.7354 | 6.6702 | 8.2385 | 42.3184 | 46.8677 | 42.7577 | 15.4041 |  |  | -0.001097 | -0.055765 | 0.04062 | 0.09791 | -0.01232 | -0.067484 | 0.54531 | -0.077048 | -0.59585 | 0.16809 | -0.30213 | 8.8793 | 8.8804 | 2.0082 | 15.9381 | 16.8315 | 17.3565 | 17.6761 | 17.6358 | 16.6285 | 14.9901 | 16.9053 | 17.2381 | 17.5236 | 17.565 | 17.3089 | 16.5235 | 14.7544 | 6.6542 | 8.5374 | 5.548 | 5.7316 | 5.9029 | 6.6634 | 7.6368 | 16.0308 | 15.6568 | 15.5046 | 14.4328 | 14.3177 | 14.2653 |  |  |  | 10.7838 | 9.2959 | 8.98 | 8.7317 | 0.043203 | 0.069471 | 12.8827 |  |  | 10.6882 |  |  | 16.9825 | 16.1881 | 15.1693 | 16.4681 | 15.7568 | 14.8705 | 10.7195 | 10.7501 | 11.5266 | 11.3972 | 9.1373 |  | 10.7933 | 8.5277 | 10.1488 | 9.1454 | 11.2159 | 12.1705 |  | 12.433 |  |  | 11.8628 | 12.6652 | 12.6245 | [6 empty] | 12.5763 |  |  | 11.2733 |  |  | 9.1398 | 10.3385 | 12.2659 | 7.5744 | 9.3149 | 12.7558 | 7.734 | 9.5807 | 12.453 | 9.1996 | 10.4044 | 7.7063 | 10.4652 | 8.2172 | 10.1134 | 7.9033 | 9.727 | 13.4694 | 10.6303 | 10.3572 | 11.7067 | 8.1207 | 9.7529 | 12.9361 | 7.9964 | 10.4112 | 9.7206 | 9.9729 | 8.4185 | 10.2367 | -0.25771 | 20.955 | 0.033062 | 0.04926 | -38.0272 | 3.1218 | -0.43 | 0.35 | -0.03883 | -0.27515 | 0.23483 | 0.36458 | -0.12922 | -0.30244 | 0.85971 | 0.41456 | 0.41026 | 0.42828 | 0.3486 | 0.58453 | 0.42889 | 0.42551
42810.4332 | -587 | 18.6755 | 18.7095 | 18.6797 | 18.6908 | 18.0445 | 16.7087 | 14.7793 | 16.775 | 17.2644 | 17.3621 | 17.3816 | 16.9469 | 15.9968 | 14.6136 | 15.1396 | 15.1072 | 15.6437 | 13.4924 | 13.6008 | 14.183 |  |  |  | 16.6917 | 16.0197 | 15.1428 | 10.2372 | 9.7399 | 9.8841 | 17.3812 | 16.4885 | 15.2868 | 16.9896 | 16.2757 | 15.2889 | 10.9238 | 11.6249 |  | 12.3661 | 10.5921 | 10.4883 | 8.8119 |  | 6.4461 | 6.3774 | 5.8759 | 5.9536 | 5.9009 | 5.9264 | 6.265 | 4.7313 | 6.3784 | 4.7631 | 6.6718 | 8.2284 | 42.3113 | 46.8757 | 42.748 | 15.4189 |  |  | 0.094843 | -0.10834 | 0.076104 | 0.12222 | -0.028748 | -0.077344 | 0.49537 | -0.24067 | -0.14516 | -0.32201 | -0.21172 | 8.8783 | 8.8791 | 2.0085 | 15.958 | 16.8377 | 17.3668 | 17.6839 | 17.6468 | 16.6388 | 14.9909 | 16.9138 | 17.2445 | 17.5276 | 17.5752 | 17.3172 | 16.5309 | 14.7592 | 6.6155 | 8.5447 | 5.5716 | 5.7087 | 5.9117 | 6.6645 | 7.6332 | 16.0217 | 15.6454 | 15.4934 | 14.4297 | 14.3107 | 14.2549 |  |  |  | 10.7791 | 9.291 | 8.9705 | 8.7331 | 0.043203 | -0.046461 | 12.8851 |  |  | 10.6922 |  |  | 16.9764 | 16.1853 | 15.1759 | 16.4674 | 15.755 | 14.8765 | 10.7314 | 10.7476 | 11.5177 | 11.3857 | 9.1464 |  | 10.8008 | 8.5026 | 10.1525 | 9.1502 | 11.2173 | 12.1354 |  | 12.4325 |  |  | 11.8136 | 12.6746 | 12.6235 | [6 empty] | 12.5881 |  |  | 11.2784 |  |  | 9.1377 | 10.342 | 12.2727 | 7.5855 | 9.3259 | 12.7577 | 7.7459 | 9.5895 | 12.4503 | 9.2076 | 10.4032 | 7.7071 | 10.4686 | 8.2237 | 10.1394 | 7.8813 | 9.7201 | 13.4606 | 10.6183 | 10.338 | 11.6941 | 8.1137 | 9.7451 | 12.9375 | 7.9995 | 10.4117 | 9.7164 | 9.9572 | 8.4181 | 10.2252 | -0.033525 | 20.9533 | 0.031978 | 0.04913 | -38.1867 | 3.1218 | -0.58 | 0.29 | 0.36107 | -0.3835 | 0.32143 | 0.40734 | -0.19739 | -0.32377 | 0.81939 | 0.41456 | 0.41108 | 0.42819 | 0.35303 | 0.58149 | 0.4279 | 0.42532
42810.4333 | -586 | 18.6712 | 18.7089 | 18.6765 | 18.6886 | 18.0398 | 16.7044 | 14.7784 | 16.778 | 17.2685 | 17.3591 | 17.3816 | 16.942 | 16.0017 | 14.6152 | 15.1396 | 15.1115 | 15.6459 | 13.4929 | 13.608 | 14.1837 |  |  |  | 16.6928 | 16.0317 | 15.1495 | 10.2403 | 9.7359 | 9.88 | 17.3766 | 16.4875 | 15.2834 | 16.9935 | 16.2747 | 15.2897 | 10.9153 | 11.6521 |  | 12.3586 | 10.6018 | 10.4831 | 8.842 |  | 6.4471 | 6.3886 | 5.8806 | 5.956 | 5.9033 | 5.9353 | 6.3067 | 4.7203 | 6.379 | 4.8091 | 6.6639 | 8.2294 | 42.3073 | 46.8921 | 42.7482 | 15.4426 |  |  | -0.24817 | -0.12805 | 0.14642 | 0.059798 | -0.024808 | -0.30142 | 0.62482 | -0.18284 | 0.51181 | -1.2749 | -0.12608 | 8.8805 | 8.8818 | 2.0086 | 15.9499 | 16.8331 | 17.3603 | 17.6782 | 17.6486 | 16.6323 | 14.9844 | 16.9166 | 17.2412 | 17.5257 | 17.5678 | 17.3138 | 16.5265 | 14.7537 | 6.5254 | 8.5408 | 5.612 | 5.7028 | 5.9422 | 6.6687 | 7.6351 | 16.0271 | 15.6413 | 15.4989 | 14.4318 | 14.3098 | 14.2556 |  |  |  | 10.7764 | 9.2915 | 8.9755 | 8.7333 | 0.015852 | -0.0080678 | 12.8951 |  |  | 10.7024 |  |  | 16.9859 | 16.1947 | 15.1801 | 16.4729 | 15.747 | 14.8831 | 10.7517 | 10.7448 | 11.5173 | 11.3789 | 9.1355 |  | 10.7836 | 8.4499 | 10.144 | 9.1526 | 11.2113 | 12.0921 |  | 12.4328 |  |  | 11.7928 | 12.6699 | 12.6351 | [6 empty] | 12.5884 |  |  | 11.2817 |  |  | 9.1353 | 10.3311 | 12.2578 | 7.5978 | 9.3227 | 12.7558 | 7.747 | 9.5936 | 12.4344 | 9.2075 | 10.4073 | 7.7147 | 10.469 | 8.2378 | 10.1412 | 7.8695 | 9.7111 | 13.4403 | 10.613 | 10.3306 | 11.6848 | 8.1091 | 9.7344 | 12.9274 | 7.9901 | 10.4099 | 9.7147 | 9.9586 | 8.4254 | 10.2218 | 0.003262 | 20.9534 | 0.031897 | 0.048725 | -38.1467 | 3.1218 | -0.55 | 0.28 | -0.58406 | -0.41694 | 0.44584 | 0.28493 | -0.18337 | -0.63918 | 0.92027 | 0.41429 | 0.41226 | 0.42792 | 0.36353 | 0.57722 | 0.42679 | 0.42523
42810.4333 | -585 | 18.6676 | 18.7003 | 18.6764 | 18.6894 | 18.0373 | 16.7037 | 14.7775 | 16.7728 | 17.2583 | 17.3555 | 17.3771 | 16.9361 | 15.9978 | 14.6049 | 15.1421 | 15.117 | 15.6539 | 13.4951 | 13.6093 | 14.19 |  |  |  | 16.6897 | 16.027 | 15.1493 | 10.2424 | 9.7427 | 9.8809 | 17.3816 | 16.4932 | 15.2848 | 16.9962 | 16.285 | 15.2986 | 10.9312 | 11.692 |  | 12.3618 | 10.6057 | 10.4887 | 8.8666 |  | 6.4396 | 6.3887 | 5.8805 | 5.9537 | 5.91 | 5.9492 | 6.3638 | 4.7468 | 6.3771 | 4.7919 | 6.6644 | 8.2261 | 42.3031 | 46.9237 | 42.7453 | 15.4595 |  |  | -0.001097 | -0.077453 | -0.05926 | 0.19385 | 0.061932 | -0.23176 | 0.49208 | -0.31689 | -0.19575 | -1.1451 | -0.080979 | 8.8786 | 8.8801 | 2.0083 | 15.9408 | 16.8331 | 17.3573 | 17.6718 | 17.6383 | 16.6309 | 14.9879 | 16.91 | 17.2375 | 17.5262 | 17.558 | 17.3076 | 16.5254 | 14.7583 | 6.4877 | 8.5293 | 5.6074 | 5.7178 | 5.9514 | 6.6652 | 7.6346 | 16.0173 | 15.6314 | 15.4993 | 14.4351 | 14.3089 | 14.2537 |  |  |  | 10.7688 | 9.286 | 8.9689 | 8.7579 | 0.0077476 | -0.019924 | 12.8993 |  |  | 10.6988 |  |  | 16.991 | 16.1965 | 15.1835 | 16.4733 | 15.7563 | 14.8772 | 10.7583 | 10.7464 | 11.5233 | 11.387 | 9.1227 |  | 10.7905 | 8.4191 | 10.1353 | 9.17 | 11.2043 | 12.0467 |  | 12.4242 |  |  | 11.8111 | 12.6804 | 12.6416 | [6 empty] | 12.5887 |  |  | 11.281 |  |  | 9.1276 | 10.3279 | 12.2486 | 7.5874 | 9.3048 | 12.7543 | 7.7407 | 9.5876 | 12.4253 | 9.2032 | 10.4022 | 7.7221 | 10.4571 | 8.2428 | 10.1259 | 7.8649 | 9.7062 | 13.4473 | 10.5995 | 10.3214 | 11.6886 | 8.1198 | 9.7402 | 12.924 | 8.0066 | 10.4168 | 9.7166 | 9.9548 | 8.4431 | 10.231 | -0.13772 | 20.9529 | 0.032948 | 0.049441 | -38.1628 | 3.1218 | -0.6 | 0.34 | -0.038832 | -0.32427 | -0.28364 | 0.513 | 0.28974 | -0.56049 | 0.8167 | 0.41487 | 0.41283 | 0.42721 | 0.36731 | 0.57767 | 0.42663 | 0.42429
42810.4333 | -584 | 18.6571 | 18.7003 | 18.6709 | 18.6821 | 18.0317 | 16.6947 | 14.7791 | 16.768 | 17.2543 | 17.355 | 17.3712 | 16.9313 | 15.9898 | 14.6037 | 15.1353 | 15.108 | 15.6472 | 13.4898 | 13.5995 | 14.1791 |  |  |  | 16.6761 | 16.0236 | 15.1414 | 10.2269 | 9.7293 | 9.8671 | 17.3728 | 16.486 | 15.2828 | 16.9865 | 16.2734 | 15.2859 | 10.9226 | 11.713 |  | 12.366 | 10.6019 | 10.4815 | 8.8905 |  | 6.4404 | 6.3885 | 5.8806 | 5.9451 | 5.9077 | 5.993 | 6.4099 | 4.7962 | 6.378 | 4.811 | 6.6636 | 8.2213 | 42.3089 | 46.9451 | 42.7455 | 15.4736 |  |  | -0.054977 | -0.2943 | -0.18411 | -0.071626 | -0.1168 | 0.00414 | 0.58014 | -0.26235 | -0.36175 | -0.30816 | -0.43109 | 8.8773 | 8.8784 | 2.0088 | 15.9454 | 16.8317 | 17.3582 | 17.666 | 17.6426 | 16.628 | 14.988 | 16.9121 | 17.2359 | 17.5245 | 17.563 | 17.3074 | 16.5256 | 14.7607 | 6.4874 | 8.5447 | 5.6489 | 5.7144 | 5.9584 | 6.6693 | 7.6406 | 16.0162 | 15.6407 | 15.4969 | 14.4321 | 14.3056 | 14.2519 |  |  |  | 10.7682 | 9.291 | 8.9702 | 8.7748 | 0.074606 | 0.042182 | 12.8897 |  |  | 10.6926 |  |  | 16.983 | 16.1804 | 15.1789 | 16.4563 | 15.7492 | 14.8667 | 10.7589 | 10.734 | 11.5058 | 11.3732 | 9.1172 |  | 10.7915 | 8.4674 | 10.1337 | 9.1826 | 11.2128 | 12.0075 |  | 12.4346 |  |  | 11.7994 | 12.678 | 12.6358 | [6 empty] | 12.5771 |  |  | 11.2742 |  |  | 9.1176 | 10.3181 | 12.24 | 7.5722 | 9.2852 | 12.7499 | 7.7496 | 9.5816 | 12.4124 | 9.2004 | 10.4009 | 7.7244 | 10.4515 | 8.2465 | 10.1218 | 7.8334 | 9.6982 | 13.4345 | 10.5836 | 10.3077 | 11.6835 | 8.1172 | 9.7338 | 12.9206 | 8.0048 | 10.4025 | 9.7099 | 9.9459 | 8.4386 | 10.2357 | -0.041229 | 20.9539 | 0.033545 | 0.049998 | -38.1127 | 3.1217 | -0.93 | 0.29 | -0.27489 | -0.6321 | -0.49995 | -0.31183 | -0.39793 | 0.074917 | 0.88684 | 0.41506 | 0.41143 | 0.42714 | 0.36782 | 0.57377 | 0.42568 | 0.4238
42810.4333 | -583 | 18.6578 | 18.7003 | 18.67 | 18.6848 | 18.0407 | 16.703 | 14.7796 | 16.7715 | 17.2575 | 17.3539 | 17.3708 | 16.9415 | 15.9939 | 14.6097 | 15.1358 | 15.109 | 15.6429 | 13.4837 | 13.5985 | 14.1772 |  |  |  | 16.671 | 16.0172 | 15.1376 | 10.2332 | 9.7182 | 9.8653 | 17.3728 | 16.4842 | 15.2887 | 16.9874 | 16.2782 | 15.29 | 10.9258 | 11.7397 |  | 12.3699 | 10.6059 | 10.4781 | 8.9159 |  | 6.4441 | 6.3845 | 5.8693 | 5.9436 | 5.9191 | 6.01 | 6.4288 | 4.8861 | 6.3771 | 4.8489 | 6.6657 | 8.2231 | 42.3126 | 46.9639 | 42.7568 | 15.4814 |  |  | -0.14369 | -0.039337 | 0.093848 | 0.16165 | -0.009692 | 0.042252 | 0.22989 | -0.33726 | -0.50341 | -0.26599 | -0.17457 | 8.875 | 8.8763 | 2.0082 | 15.9531 | 16.8345 | 17.3671 | 17.6767 | 17.6482 | 16.6346 | 14.994 | 16.9173 | 17.2459 | 17.5354 | 17.5711 | 17.3167 | 16.5291 | 14.766 | 6.4813 | 8.5486 | 5.77 | 5.7044 | 5.9507 | 6.6705 | 7.6354 | 16.021 | 15.638 | 15.492 | 14.4248 | 14.307 | 14.2487 |  |  |  | 10.7656 | 9.2925 | 8.9634 | 8.7988 | 0.20467 | 0.16997 | 12.8908 |  |  | 10.6932 |  |  | 16.9793 | 16.1886 | 15.1669 | 16.4693 | 15.7577 | 14.8731 | 10.7615 | 10.7385 | 11.5137 | 11.3634 | 9.0965 |  | 10.7888 | 8.4908 | 10.1385 | 9.182 | 11.209 | 12.0014 |  | 12.438 |  |  | 11.8117 | 12.6752 | 12.6461 | [6 empty] | 12.5827 |  |  | 11.2835 |  |  | 9.1096 | 10.319 | 12.2312 | 7.5409 | 9.2751 | 12.746 | 7.7532 | 9.577 | 12.4061 | 9.2 | 10.4013 | 7.7232 | 10.4526 | 8.2495 | 10.1254 | 7.8281 | 9.7046 | 13.4347 | 10.5865 | 10.3031 | 11.6906 | 8.1303 | 9.7379 | 12.9241 | 8.0178 | 10.4072 | 9.7087 | 9.946 | 8.4454 | 10.2448 | -0.15236 | 20.9529 | 0.03417 | 0.050621 | -38.1864 | 3.1217 | -1.1 | 0.39 | -0.44441 | -0.23109 | 0.35694 | 0.46846 | -0.11463 | 0.23934 | 0.55828 | 0.41554 | 0.41094 | 0.42703 | 0.36864 | 0.55971 | 0.42508 | 0.42305
42810.4333 | -582 | 18.665 | 18.7064 | 18.6765 | 18.6854 | 18.0388 | 16.7036 | 14.7789 | 16.7748 | 17.2531 | 17.3577 | 17.3745 | 16.9434 | 15.9932 | 14.6071 | 15.1314 | 15.1097 | 15.6395 | 13.4792 | 13.6001 | 14.1779 |  |  |  | 16.6721 | 16.0172 | 15.1382 | 10.2351 | 9.7114 | 9.8955 | 17.3638 | 16.4819 | 15.2822 | 16.9847 | 16.2757 | 15.2883 | 10.9194 | 11.7523 |  | 12.3617 | 10.6061 | 10.4712 | 8.904 |  | 6.4363 | 6.3766 | 5.8536 | 5.932 | 5.9125 | 6.0152 | 6.4135 | 4.9897 | 6.3697 | 4.8354 | 6.668 | 8.2214 | 42.3227 | 46.9729 | 42.7675 | 15.4857 |  |  | -0.10032 | -0.090593 | 0.24564 | 0.10448 | 0.1283 | 0.27487 | 0.49208 | -0.45029 | -0.11752 | -0.75881 | -0.26279 | 8.8781 | 8.8794 | 2.0087 | 15.9438 | 16.8344 | 17.3606 | 17.6668 | 17.6336 | 16.6259 | 14.9907 | 16.9081 | 17.2357 | 17.5234 | 17.5599 | 17.3155 | 16.5275 | 14.7626 | 6.486 | 8.5095 | 5.7875 | 5.7655 | 5.9069 | 6.6626 | 7.6361 | 16.0193 | 15.6351 | 15.4954 | 14.4296 | 14.3142 | 14.252 |  |  |  | 10.7689 | 9.2983 | 8.967 | 8.8375 | 0.027805 | 0.12348 | 12.8915 |  |  | 10.7 |  |  | 16.9822 | 16.1808 | 15.1676 | 16.4668 | 15.7497 | 14.8759 | 10.7652 | 10.7425 | 11.5119 | 11.3729 | 9.1089 |  | 10.7904 | 8.5018 | 10.1379 | 9.1812 | 11.2091 | 11.9806 |  | 12.4319 |  |  | 11.8359 | 12.6837 | 12.6583 | [6 empty] | 12.6017 |  |  | 11.302 |  |  | 9.1026 | 10.3207 | 12.2306 | 7.5272 | 9.2637 | 12.7454 | 7.7509 | 9.5752 | 12.4067 | 9.2081 | 10.4014 | 7.7165 | 10.454 | 8.25 | 10.1293 | 7.8285 | 9.7009 | 13.4322 | 10.5827 | 10.299 | 11.6954 | 8.1422 | 9.7417 | 12.9336 | 8.0236 | 10.4028 | 9.7081 | 9.9357 | 8.456 | 10.2478 | -0.13637 | 20.9537 | 0.033573 | 0.050918 | -38.0681 | 3.1217 | -0.87 | 0.26 | -0.37136 | -0.35069 | 0.57747 | 0.37662 | 0.41707 | 0.61047 | 0.8168 | 0.41526 | 0.41062 | 0.42705 | 0.3672 | 0.55784 | 0.4252 | 0.42209
42810.4333 | -581 | 18.6619 | 18.7025 | 18.676 | 18.6864 | 18.0403 | 16.7028 | 14.7787 | 16.7763 | 17.2651 | 17.3628 | 17.3824 | 16.9393 | 15.9986 | 14.6052 | 15.137 | 15.1084 | 15.6403 | 13.4836 | 13.5997 | 14.1841 |  |  |  | 16.6791 | 16.0167 | 15.1391 | 10.2444 | 9.7072 | 9.9329 | 17.3676 | 16.484 | 15.2797 | 16.9871 | 16.2714 | 15.2833 | 10.9175 | 11.7435 |  | 12.3616 | 10.6057 | 10.4674 | 8.881 |  | 6.4488 | 6.3782 | 5.8505 | 5.935 | 5.9136 | 6.0317 | 6.4059 | 5.019 | 6.3759 | 4.8246 | 6.6774 | 8.2278 | 42.3359 | 46.9802 | 42.7841 | 15.5002 |  |  | 0.11719 | 8.7e-05 | 0.083988 | -0.014458 | -0.05372 | -0.35793 | 0.51376 | -0.49169 | 0.055476 | 0.70224 | -0.2916 | 8.885 | 8.8863 | 2.0085 | 15.9461 | 16.8183 | 17.3503 | 17.6727 | 17.6278 | 16.6202 | 14.9824 | 16.9069 | 17.2331 | 17.5118 | 17.5592 | 17.2969 | 16.5125 | 14.7496 | 6.4795 | 8.5136 | 5.7107 | 5.8957 | 5.8706 | 6.6701 | 7.6407 | 16.0172 | 15.6387 | 15.4949 | 14.4319 | 14.3071 | 14.2468 |  |  |  | 10.7653 | 9.2929 | 8.9638 | 8.8893 | -0.067012 | 0.043311 | 12.8835 |  |  | 10.6992 |  |  | 16.979 | 16.1812 | 15.162 | 16.4559 | 15.7462 | 14.8636 | 10.7626 | 10.7341 | 11.5044 | 11.363 | 9.0968 |  | 10.7859 | 8.5475 | 10.1436 | 9.1888 | 11.2027 | 11.9647 |  | 12.4294 |  |  | 11.8566 | 12.6705 | 12.665 | [6 empty] | 12.5969 |  |  | 11.2907 |  |  | 9.095 | 10.3112 | 12.217 | 7.5167 | 9.2527 | 12.7355 | 7.7502 | 9.5754 | 12.4114 | 9.2075 | 10.4027 | 7.7002 | 10.4591 | 8.2409 | 10.1266 | 7.827 | 9.6956 | 13.4253 | 10.5735 | 10.2954 | 11.6894 | 8.14 | 9.7314 | 12.9292 | 8.0211 | 10.3939 | 9.7064 | 9.9197 | 8.469 | 10.2494 | 0.030033 | 20.9538 | 0.033556 | 0.049926 | -38.0743 | 3.1217 | -0.82 | 0.45 | 0.40139 | 0.010868 | 0.33767 | -0.1401 | -0.26988 | -0.69664 | 0.83463 | 0.41544 | 0.40954 | 0.42663 | 0.36879 | 0.56691 | 0.42578 | 0.42053
42810.4333 | -580 | 18.6597 | 18.7052 | 18.6801 | 18.6859 | 18.041 | 16.704 | 14.7804 | 16.7844 | 17.2667 | 17.3603 | 17.3847 | 16.9395 | 16.0031 | 14.6081 | 15.1352 | 15.1099 | 15.6439 | 13.4907 | 13.6027 | 14.1861 |  |  |  | 16.6798 | 16.0176 | 15.1413 | 10.253 | 9.7092 | 9.9444 | 17.3682 | 16.4833 | 15.2777 | 16.9839 | 16.27 | 15.283 | 10.9155 | 11.7332 |  | 12.3634 | 10.6113 | 10.4596 | 8.8547 |  | 6.4519 | 6.3836 | 5.8574 | 5.945 | 5.9165 | 6.0287 | 6.3858 | 5.01 | 6.379 | 4.8282 | 6.6744 | 8.2234 | 42.3422 | 46.9912 | 42.8004 | 15.5067 |  |  | -0.049065 | 0.002059 | 0.07282 | -0.048626 | 0.022508 | 0.043568 | 0.61496 | -0.34449 | -0.24187 | -0.95707 | -0.29756 | 8.8811 | 8.8826 | 2.0085 | 15.9449 | 16.8241 | 17.3554 | 17.6755 | 17.6416 | 16.626 | 14.993 | 16.9151 | 17.2369 | 17.5218 | 17.5637 | 17.309 | 16.5243 | 14.7549 | 6.4597 | 8.5437 | 5.6433 | 5.9971 | 5.8866 | 6.6595 | 7.6359 | 16.0176 | 15.6416 | 15.4932 | 14.4351 | 14.314 | 14.2511 |  |  |  | 10.7698 | 9.2885 | 8.9692 | 8.9399 | 0.081291 | 0.099206 | 12.8894 |  |  | 10.7023 |  |  | 16.9919 | 16.1805 | 15.1698 | 16.4715 | 15.7627 | 14.8721 | 10.7772 | 10.7279 | 11.5105 | 11.3763 | 9.1044 |  | 10.7924 | 8.6082 | 10.1377 | 9.1983 | 11.2144 | 11.9539 |  | 12.4277 |  |  | 11.8741 | 12.6573 | 12.6723 | [6 empty] | 12.5797 |  |  | 11.2721 |  |  | 9.0913 | 10.3109 | 12.2119 | 7.5097 | 9.2502 | 12.7296 | 7.759 | 9.5699 | 12.4262 | 9.2084 | 10.4004 | 7.6913 | 10.4656 | 8.2337 | 10.1256 | 7.8251 | 9.6955 | 13.4252 | 10.5733 | 10.292 | 11.6799 | 8.1452 | 9.7328 | 12.9332 | 8.0134 | 10.3905 | 9.7063 | 9.9131 | 8.4831 | 10.2526 | 0.080687 | 20.9531 | 0.033424 | 0.049586 | -38.0435 | 3.1217 | -0.62 | 0.3 | -0.25973 | 0.05287 | 0.31442 | -0.25693 | 0.17469 | 0.24305 | 0.91313 | 0.41545 | 0.40766 | 0.42676 | 0.36976 | 0.57384 | 0.42644 | 0.41927
42810.4333 | -579 | 18.6569 | 18.7006 | 18.6743 | 18.6835 | 18.0409 | 16.7 | 14.7759 | 16.7768 | 17.2584 | 17.3591 | 17.3775 | 16.9391 | 15.9956 | 14.6049 | 15.1329 | 15.1074 | 15.6462 | 13.4918 | 13.6026 | 14.185 |  |  |  | 16.6824 | 16.0199 | 15.1447 | 10.2552 | 9.7089 | 9.956 | 17.3582 | 16.4749 | 15.2687 | 16.9793 | 16.2601 | 15.2735 | 10.9062 | 11.7461 |  | 12.3567 | 10.6009 | 10.4506 | 8.8203 |  | 6.4529 | 6.383 | 5.8575 | 5.9422 | 5.9161 | 6.0225 | 6.3808 | 5.0365 | 6.3834 | 4.8632 | 6.6661 | 8.2209 | 42.3422 | 47.0014 | 42.8171 | 15.5191 |  |  | 0.054103 | 0.10063 | 0.10436 | 0.22999 | -0.032692 | -0.077344 | 0.55319 | -0.24921 | -0.057975 | 0.036752 | -0.22166 | 8.8769 | 8.8781 | 2.0085 | 15.9426 | 16.8281 | 17.3533 | 17.6713 | 17.6382 | 16.622 | 14.9896 | 16.9149 | 17.2416 | 17.5239 | 17.5639 | 17.3066 | 16.5276 | 14.7604 | 6.3955 | 8.5208 | 5.5925 | 6.011 | 5.9695 | 6.6616 | 7.6342 | 16.009 | 15.6399 | 15.4919 | 14.433 | 14.3071 | 14.2526 |  |  |  | 10.764 | 9.2916 | 8.9661 | 8.9607 | 0.073795 | 0.12706 | 12.883 |  |  | 10.709 |  |  | 16.9834 | 16.1908 | 15.1685 | 16.4718 | 15.7485 | 14.875 | 10.7693 | 10.7312 | 11.5046 | 11.3777 | 9.1134 |  | 10.7831 | 8.6397 | 10.1367 | 9.1907 | 11.2123 | 11.9625 |  | 12.4338 |  |  | 11.887 | 12.6614 | 12.6809 | [6 empty] | 12.5703 |  |  | 11.2737 |  |  | 9.0912 | 10.3106 | 12.2035 | 7.5006 | 9.2532 | 12.7223 | 7.76 | 9.5663 | 12.4361 | 9.2093 | 10.3996 | 7.6884 | 10.4679 | 8.2331 | 10.1309 | 7.8131 | 9.6961 | 13.4157 | 10.5679 | 10.2826 | 11.6671 | 8.1462 | 9.736 | 12.9333 | 8.0017 | 10.3877 | 9.7004 | 9.9145 | 8.4809 | 10.2546 | -0.040458 | 20.9531 | 0.032953 | 0.048978 | -38.1949 | 3.1218 | -0.54 | 0.32 | 0.27274 | 0.36961 | 0.3764 | 0.55878 | -0.21053 | -0.32383 | 0.86605 | 0.41489 | 0.40675 | 0.4269 | 0.37714 | 0.57929 | 0.42709 | 0.4185
42810.4333 | -578 | 18.6573 | 18.6982 | 18.6738 | 18.6863 | 18.0366 | 16.6978 | 14.7756 | 16.7796 | 17.2596 | 17.3577 | 17.3753 | 16.932 | 15.9923 | 14.6073 | 15.1262 | 15.0977 | 15.6358 | 13.4844 | 13.593 | 14.1756 |  |  |  | 16.6789 | 16.0176 | 15.1402 | 10.2442 | 9.6893 | 9.9207 | 17.3669 | 16.4775 | 15.2784 | 16.9786 | 16.272 | 15.2884 | 10.9193 | 11.7806 |  | 12.3572 | 10.6167 | 10.4617 | 8.7947 |  | 6.4615 | 6.394 | 5.8722 | 5.9395 | 5.9222 | 6.0217 | 6.4086 | 5.0371 | 6.3926 | 4.8946 | 6.6746 | 8.2267 | 42.327 | 47.0239 | 42.8427 | 15.5286 |  |  | 0.002191 | -0.022913 | 0.02682 | -0.18793 | -0.15886 | -0.099028 | 0.56371 | -0.30506 | -0.1471 | -0.36208 | -0.30412 | 8.88 | 8.8811 | 2.0085 | 15.9399 | 16.8219 | 17.3501 | 17.6645 | 17.6301 | 16.6184 | 14.9852 | 16.9024 | 17.2346 | 17.5186 | 17.5576 | 17.3071 | 16.5221 | 14.7545 | 6.3699 | 8.5149 | 5.5585 | 6.0511 | 6.0898 | 6.6659 | 7.6456 | 16.0048 | 15.6328 | 15.4916 | 14.4286 | 14.3069 | 14.2479 |  |  |  | 10.7598 | 9.2929 | 8.9586 | 8.9873 | 0.11796 | 0.048957 | 12.8874 |  |  | 10.7034 |  |  | 16.9875 | 16.1857 | 15.1683 | 16.4672 | 15.7529 | 14.8649 | 10.7774 | 10.7143 | 11.5027 | 11.3755 | 9.1072 |  | 10.7812 | 8.6394 | 10.1335 | 9.1836 | 11.2114 | 11.9401 |  | 12.4248 |  |  | 11.8864 | 12.6682 | 12.682 | [6 empty] | 12.5758 |  |  | 11.2795 |  |  | 9.0919 | 10.3133 | 12.2072 | 7.5075 | 9.2541 | 12.715 | 7.7645 | 9.562 | 12.4505 | 9.2192 | 10.4054 | 7.7001 | 10.4724 | 8.2451 | 10.1406 | 7.8091 | 9.6912 | 13.4096 | 10.5666 | 10.2781 | 11.6526 | 8.1468 | 9.7309 | 12.9359 | 8.0043 | 10.3807 | 9.6959 | 9.9125 | 8.474 | 10.2571 | -0.12 | 20.9533 | 0.032282 | 0.048855 | -38.2143 | 3.1217 | -0.63 | 0.32 | 0.054883 | -0.17637 | 0.19082 | -0.50512 | -0.46409 | -0.36642 | 0.87424 | 0.415 | 0.40665 | 0.42706 | 0.38048 | 0.58439 | 0.42823 | 0.41763
42810.4334 | -577 | 18.6651 | 18.7044 | 18.6772 | 18.6929 | 18.0376 | 16.7142 | 14.7842 | 16.779 | 17.2642 | 17.3674 | 17.3819 | 16.9471 | 16.0048 | 14.6088 | 15.1354 | 15.1072 | 15.6498 | 13.4879 | 13.6106 | 14.1915 |  |  |  | 16.6891 | 16.0314 | 15.1468 | 10.2478 | 9.6952 | 9.8737 | 17.3657 | 16.4753 | 15.2764 | 16.9723 | 16.2673 | 15.2833 | 10.914 | 11.8041 |  | 12.3532 | 10.6142 | 10.4617 | 8.7491 |  | 6.4528 | 6.3875 | 5.8614 | 5.9373 | 5.9214 | 6.0172 | 6.4255 | 5.1008 | 6.3919 | 4.8923 | 6.6695 | 8.2218 | 42.3091 | 47.0322 | 42.8596 | 15.5288 |  |  | 0.017963 | -0.23319 | 0.17204 | -0.094626 | -0.073432 | -0.026088 | 0.55911 | -0.50417 | -0.59001 | 0.016611 | -0.19682 | 8.8765 | 8.8776 | 2.0085 | 15.947 | 16.8194 | 17.3534 | 17.6725 | 17.6359 | 16.6239 | 14.9868 | 16.9115 | 17.2367 | 17.525 | 17.5603 | 17.3107 | 16.5204 | 14.7523 | 6.3051 | 8.4566 | 5.5322 | 6.0446 | 6.1564 | 6.6684 | 7.6517 | 16.0097 | 15.6316 | 15.4969 | 14.4307 | 14.306 | 14.2509 |  |  |  | 10.7531 | 9.2918 | 8.9623 | 9.0034 | 0.35359 | 0.14193 | 12.8872 |  |  | 10.7074 |  |  | 16.9881 | 16.1778 | 15.1687 | 16.4656 | 15.7574 | 14.8696 | 10.7719 | 10.7204 | 11.5016 | 11.3789 | 9.1174 |  | 10.7865 | 8.6257 | 10.1336 | 9.1807 | 11.2144 | 11.9264 |  | 12.4272 |  |  | 11.8883 | 12.6617 | 12.6885 | [6 empty] | 12.5873 |  |  | 11.277 |  |  | 9.0891 | 10.304 | 12.192 | 7.5197 | 9.2608 | 12.7032 | 7.7642 | 9.5566 | 12.4518 | 9.2188 | 10.3958 | 7.7046 | 10.4746 | 8.2539 | 10.1227 | 7.7984 | 9.6869 | 13.407 | 10.5674 | 10.2702 | 11.6406 | 8.1445 | 9.7318 | 12.9305 | 8.0067 | 10.3751 | 9.6929 | 9.8996 | 8.4642 | 10.2532 | -0.16372 | 20.9537 | 0.031737 | 0.048739 | -38.1756 | 3.1217 | -0.73 | 0.27 | 0.15713 | -0.56265 | 0.48329 | -0.35842 | -0.31553 | -0.18807 | 0.87066 | 0.41489 | 0.40703 | 0.42724 | 0.38797 | 0.58801 | 0.42932 | 0.41695
42810.4334 | -576 | 18.6528 | 18.6892 | 18.666 | 18.6834 | 18.0345 | 16.7037 | 14.782 | 16.7723 | 17.2556 | 17.3599 | 17.3742 | 16.94 | 15.9923 | 14.6016 | 15.1305 | 15.1058 | 15.6441 | 13.4911 | 13.6093 | 14.1934 |  |  |  | 16.6871 | 16.026 | 15.147 | 10.2487 | 9.7015 | 9.8587 | 17.363 | 16.4721 | 15.2714 | 16.9863 | 16.2643 | 15.2794 | 10.9094 | 11.8402 |  | 12.3531 | 10.6199 | 10.4635 | 8.719 |  | 6.4459 | 6.3882 | 5.8607 | 5.9371 | 5.9105 | 6.0094 | 6.4248 | 5.1869 | 6.3975 | 4.8742 | 6.6661 | 8.2224 | 42.2924 | 47.057 | 42.8893 | 15.5421 |  |  | -0.094405 | 0.050687 | 0.09122 | -0.16428 | -0.059632 | -0.22979 | 0.59459 | -0.35566 | 0.18761 | 0.51971 | -0.2 | 8.8831 | 8.8843 | 2.0084 | 15.936 | 16.814 | 17.3505 | 17.6714 | 17.6288 | 16.6225 | 14.9794 | 16.9111 | 17.232 | 17.5231 | 17.5594 | 17.306 | 16.5186 | 14.7558 | 6.3004 | 8.4527 | 5.5664 | 6.0446 | 6.2236 | 6.6728 | 7.6529 | 16.0048 | 15.6331 | 15.4902 | 14.4264 | 14.3066 | 14.2504 |  |  |  | 10.7579 | 9.2883 | 8.9586 | 8.9936 | 0.13518 | 0.054038 | 12.8695 |  |  | 10.7053 |  |  | 16.975 | 16.1726 | 15.1521 | 16.455 | 15.7449 | 14.8634 | 10.762 | 10.7157 | 11.5047 | 11.3686 | 9.165 |  | 10.789 | 8.5955 | 10.1371 | 9.1828 | 11.2112 | 11.9438 |  | 12.4234 |  |  | 11.9167 | 12.6696 | 12.697 | [6 empty] | 12.6001 |  |  | 11.2882 |  |  | 9.0906 | 10.2995 | 12.1755 | 7.5145 | 9.2625 | 12.6885 | 7.7588 | 9.5402 | 12.4603 | 9.2193 | 10.3938 | 7.7061 | 10.4781 | 8.2554 | 10.1187 | 7.8083 | 9.698 | 13.4145 | 10.5714 | 10.2662 | 11.6339 | 8.1454 | 9.7322 | 12.9325 | 8.012 | 10.3771 | 9.6899 | 9.8921 | 8.4674 | 10.2609 | 0.0084622 | 20.9538 | 0.032064 | 0.048978 | -38.1132 | 3.1217 | -0.63 | 0.3 | -0.36022 | 0.26232 | 0.35191 | -0.47226 | -0.28434 | -0.55816 | 0.89785 | 0.41365 | 0.40799 | 0.42708 | 0.389 | 0.58436 | 0.43001 | 0.41739
42810.4334 | -575 | 18.653 | 18.6912 | 18.6659 | 18.6773 | 18.0377 | 16.6954 | 14.7768 | 16.7688 | 17.2555 | 17.3516 | 17.3762 | 16.933 | 15.9887 | 14.6007 | 15.1218 | 15.0972 | 15.6356 | 13.4825 | 13.6002 | 14.1793 |  |  |  | 16.6793 | 16.0141 | 15.1391 | 10.2329 | 9.6877 | 9.8597 | 17.3573 | 16.4754 | 15.2787 | 16.9835 | 16.2674 | 15.2876 | 10.919 | 11.8544 |  | 12.3609 | 10.6229 | 10.471 | 8.7036 |  | 6.4593 | 6.3869 | 5.875 | 5.9369 | 5.9205 | 6.018 | 6.4452 | 5.2292 | 6.4087 | 4.844 | 6.6693 | 8.2123 | 42.2742 | 47.0714 | 42.9165 | 15.5329 |  |  | -0.19757 | -0.14317 | 0.18124 | -0.023658 | 0.1329 | -0.23899 | 0.64256 | -0.31098 | -0.26055 | -0.43047 | -0.17258 | 8.8808 | 8.8819 | 2.0087 | 15.926 | 16.8194 | 17.3485 | 17.6653 | 17.6361 | 16.6245 | 14.981 | 16.9116 | 17.2304 | 17.5214 | 17.5609 | 17.2972 | 16.5177 | 14.7541 | 6.2766 | 8.4691 | 5.6011 | 5.9897 | 6.2659 | 6.6642 | 7.6471 | 15.9986 | 15.6367 | 15.4935 | 14.4297 | 14.3146 | 14.2512 |  |  |  | 10.7623 | 9.2952 | 8.9703 | 9.0276 | 0.025171 | 0.055167 | 12.8872 |  |  | 10.7052 |  |  | 16.98 | 16.1835 | 15.1646 | 16.4684 | 15.7527 | 14.8726 | 10.7702 | 10.7261 | 11.5119 | 11.3763 | 9.2065 |  | 10.7852 | 8.5812 | 10.1303 | 9.182 | 11.2067 | 11.9662 |  | 12.4253 |  |  | 11.9442 | 12.668 | 12.7093 | [6 empty] | 12.6108 |  |  | 11.318 |  |  | 9.097 | 10.3035 | 12.1576 | 7.5278 | 9.2524 | 12.6841 | 7.7622 | 9.5342 | 12.4683 | 9.2234 | 10.3984 | 7.7164 | 10.4779 | 8.2572 | 10.1099 | 7.826 | 9.7048 | 13.4103 | 10.5687 | 10.2585 | 11.6336 | 8.1505 | 9.7275 | 12.9293 | 8.0282 | 10.3697 | 9.6924 | 9.9036 | 8.4729 | 10.2753 | 0.018477 | 20.9537 | 0.03308 | 0.049738 | -38.0204 | 3.1218 | -0.55 | 0.29 | -0.52111 | -0.44086 | 0.49604 | -0.17922 | 0.42448 | -0.56923 | 0.93338 | 0.41237 | 0.40816 | 0.42696 | 0.39066 | 0.57983 | 0.43075 | 0.41658
42810.4334 | -574 | 18.659 | 18.7019 | 18.6724 | 18.6843 | 18.0423 | 16.7041 | 14.7852 | 16.7825 | 17.2617 | 17.3586 | 17.3805 | 16.933 | 15.9954 | 14.6064 | 15.1225 | 15.0969 | 15.6363 | 13.4866 | 13.5965 | 14.1766 |  |  |  | 16.6757 | 16.0121 | 15.1414 | 10.227 | 9.6844 | 9.8687 | 17.3538 | 16.4707 | 15.2767 | 16.9796 | 16.2634 | 15.2804 | 10.9131 | 11.858 |  | 12.3549 | 10.6244 | 10.4647 | 8.6861 |  | 6.4542 | 6.3871 | 5.8584 | 5.95 | 5.9145 | 6.0167 | 6.4878 | 5.1994 | 6.4003 | 4.7793 | 6.6641 | 8.2183 | 42.2501 | 47.0856 | 42.9469 | 15.5301 |  |  | -0.082577 | -0.099137 | 0.16153 | 0.027598 | -0.014292 | -0.25871 | 0.58014 | -0.34186 | -0.25608 | -0.6365 | -0.3983 | 8.8796 | 8.8806 | 2.0085 | 15.943 | 16.8354 | 17.3531 | 17.6706 | 17.6443 | 16.636 | 14.9889 | 16.9179 | 17.2494 | 17.5279 | 17.5664 | 17.316 | 16.5312 | 14.7754 | 6.2751 | 8.4467 | 5.6691 | 5.981 | 6.2802 | 6.6777 | 7.649 | 15.9989 | 15.6316 | 15.4898 | 14.4255 | 14.3021 | 14.2425 |  |  |  | 10.7552 | 9.2918 | 8.9683 | 9.0151 | 0.065083 | 0.15435 | 12.8796 |  |  | 10.7086 |  |  | 16.9746 | 16.1852 | 15.1656 | 16.4658 | 15.7513 | 14.8641 | 10.766 | 10.7107 | 11.504 | 11.3747 | 9.2174 |  | 10.7775 | 8.5506 | 10.1232 | 9.1787 | 11.2075 | 11.9613 |  | 12.4145 |  |  | 11.9379 | 12.6788 | 12.7075 | [6 empty] | 12.5962 |  |  | 11.3256 |  |  | 9.1014 | 10.3054 | 12.161 | 7.5285 | 9.2591 | 12.689 | 7.7812 | 9.5371 | 12.4912 | 9.2266 | 10.3915 | 7.7297 | 10.4872 | 8.2757 | 10.1095 | 7.8365 | 9.6892 | 13.4113 | 10.5506 | 10.2503 | 11.6185 | 8.1373 | 9.7246 | 12.9256 | 8.0235 | 10.3664 | 9.681 | 9.899 | 8.4686 | 10.2836 | -0.14408 | 20.954 | 0.03316 | 0.049709 | -38.0577 | 3.1217 | -0.55 | 0.32 | -0.3369 | -0.36686 | 0.46829 | 0.19356 | -0.1392 | -0.59225 | 0.88688 | 0.41182 | 0.40878 | 0.42707 | 0.39239 | 0.57249 | 0.43104 | 0.4167
42810.4334 | -573 | 18.6543 | 18.7023 | 18.6729 | 18.6811 | 18.0378 | 16.7013 | 14.7844 | 16.7774 | 17.2644 | 17.3583 | 17.3794 | 16.94 | 15.9923 | 14.6103 | 15.1125 | 15.0874 | 15.6364 | 13.4792 | 13.5914 | 14.166 |  |  |  | 16.676 | 16.012 | 15.1325 | 10.2188 | 9.6764 | 9.8674 | 17.3535 | 16.4704 | 15.2711 | 16.9808 | 16.2635 | 15.2748 | 10.9076 | 11.8792 |  | 12.3551 | 10.6352 | 10.4763 | 8.6812 |  | 6.4532 | 6.3862 | 5.8636 | 5.9538 | 5.9243 | 6.038 | 6.5642 | 5.1406 | 6.4178 | 4.7418 | 6.6692 | 8.221 | 42.2337 | 47.1 | 42.9831 | 15.5217 |  |  | -0.16012 | -0.10045 | 0.023536 | 0.033514 | 0.17693 | 0.10139 | 0.68659 | -0.27615 | -0.63944 | -0.12773 | -0.2465 | 8.8776 | 8.8791 | 2.0085 | 15.9335 | 16.8225 | 17.3516 | 17.6688 | 17.6329 | 16.6208 | 14.9776 | 16.9168 | 17.2339 | 17.5185 | 17.5621 | 17.3043 | 16.5182 | 14.7584 | 6.311 | 8.4621 | 5.7021 | 5.985 | 6.2427 | 6.6777 | 7.6403 | 16.0041 | 15.6375 | 15.4864 | 14.4255 | 14.3017 | 14.2475 |  |  |  | 10.759 | 9.2924 | 8.9712 | 8.9909 | 0.059816 | 0.16677 | 12.8874 |  |  | 10.7164 |  |  | 16.9782 | 16.1872 | 15.1596 | 16.4664 | 15.7551 | 14.8606 | 10.7703 | 10.7098 | 11.5079 | 11.3742 | 9.1996 |  | 10.7858 | 8.5203 | 10.1263 | 9.183 | 11.1993 | 11.955 |  | 12.4233 |  |  | 11.9437 | 12.661 | 12.7061 | [6 empty] | 12.5619 |  |  | 11.3379 |  |  | 9.104 | 10.3145 | 12.1448 | 7.5465 | 9.2553 | 12.6665 | 7.7712 | 9.5312 | 12.476 | 9.2186 | 10.3869 | 7.7334 | 10.4728 | 8.2759 | 10.1159 | 7.8333 | 9.6791 | 13.396 | 10.543 | 10.2382 | 11.5877 | 8.1323 | 9.7124 | 12.9239 | 7.9957 | 10.3457 | 9.6795 | 9.893 | 8.4596 | 10.2806 | -0.081867 | 20.9537 | 0.033596 | 0.050129 | -38.0694 | 3.1217 | -0.53 | 0.3 | -0.46913 | -0.36928 | 0.17875 | 0.2133 | 0.48979 | 0.37078 | 0.96486 | 0.41258 | 0.40972 | 0.42668 | 0.38841 | 0.56782 | 0.431 | 0.4175
42810.4334 | -572 | 18.6407 | 18.7021 | 18.6752 | 18.675 | 18.0304 | 16.6968 | 14.7752 | 16.7729 | 17.2633 | 17.3552 | 17.374 | 16.9296 | 15.9869 | 14.602 | 15.1238 | 15.0978 | 15.6343 | 13.4808 | 13.5919 | 14.1742 |  |  |  | 16.6799 | 16.0183 | 15.1313 | 10.2224 | 9.6807 | 9.9126 | 17.3566 | 16.4721 | 15.2807 | 16.9864 | 16.2685 | 15.2841 | 10.912 | 11.9014 |  | 12.3611 | 10.6389 | 10.4837 | 8.7004 |  | 6.4503 | 6.3855 | 5.8619 | 5.9442 | 5.9243 | 6.0699 | 6.6387 | 5.1874 | 6.4133 | 4.7244 | 6.671 | 8.2041 | 42.2042 | 47.0956 | 43.0233 | 15.5144 |  |  | 0.019275 | -0.11885 | 0.17139 | 0.29965 | 0.14802 | -0.17394 | 0.46842 | -0.43518 | -0.055446 | -0.68958 | -0.24053 | 8.8765 | 8.8776 | 2.0084 | 15.9305 | 16.8148 | 17.3492 | 17.6654 | 17.6326 | 16.621 | 14.9811 | 16.9121 | 17.2339 | 17.5213 | 17.5576 | 17.3026 | 16.5203 | 14.7517 | 6.3463 | 8.493 | 5.7554 | 5.9943 | 6.1978 | 6.6818 | 7.6369 | 15.997 | 15.6324 | 15.482 | 14.4299 | 14.3062 | 14.2542 |  |  |  | 10.768 | 9.288 | 8.9674 | 8.9657 | 0.070554 | 0.14268 | 12.8879 |  |  | 10.7126 |  |  | 16.9821 | 16.186 | 15.1652 | 16.464 | 15.7538 | 14.8616 | 10.7632 | 10.7084 | 11.4979 | 11.3647 | 9.1762 |  | 10.7776 | 8.495 | 10.1273 | 9.1846 | 11.1986 | 11.942 |  | 12.4148 |  |  | 11.9546 | 12.6446 | 12.698 | [6 empty] | 12.5736 |  |  | 11.3379 |  |  | 9.0976 | 10.3029 | 12.1335 | 7.5426 | 9.2615 | 12.6597 | 7.7626 | 9.5244 | 12.4885 | 9.2174 | 10.3845 | 7.7397 | 10.4748 | 8.2813 | 10.1139 | 7.8383 | 9.6835 | 13.3967 | 10.5474 | 10.2279 | 11.5776 | 8.137 | 9.721 | 12.9337 | 7.9863 | 10.3413 | 9.6789 | 9.893 | 8.4727 | 10.2893 | -0.033525 | 20.9538 | 0.034595 | 0.050968 | -38.1004 | 3.1217 | -0.57 | 0.31 | 0.16278 | -0.40168 | 0.48236 | 0.63781 | 0.44802 | -0.48567 | 0.797 | 0.41296 | 0.41046 | 0.42661 | 0.38495 | 0.5615 | 0.43061 | 0.41849
42810.4334 | -571 | 18.6394 | 18.6853 | 18.6613 | 18.6671 | 18.0201 | 16.6907 | 14.7563 | 16.7675 | 17.2529 | 17.3455 | 17.3655 | 16.9277 | 15.9842 | 14.5933 | 15.1283 | 15.1005 | 15.6428 | 13.4826 | 13.5918 | 14.1846 |  |  |  | 16.6782 | 16.0213 | 15.1388 | 10.2262 | 9.6852 | 9.9228 | 17.3537 | 16.4805 | 15.2821 | 16.9888 | 16.276 | 15.2836 | 10.914 | 11.9138 |  | 12.3604 | 10.6385 | 10.4856 | 8.7389 |  | 6.4542 | 6.3931 | 5.8679 | 5.9586 | 5.9602 | 6.1202 | 6.7108 | 5.2047 | 6.4232 | 4.7495 | 6.6753 | 8.2145 | 42.1939 | 47.0999 | 43.0727 | 15.506 |  |  | 0.011391 | -0.2805 | 0.043248 | 0.24905 | 0.031048 | -0.047772 | 0.61825 | -0.23016 | -0.44834 | 2.1293 | -0.28127 | 8.8785 | 8.8794 | 2.0085 | 15.9243 | 16.8105 | 17.3415 | 17.6714 | 17.6349 | 16.6208 | 14.9759 | 16.9008 | 17.239 | 17.5193 | 17.5563 | 17.3084 | 16.5222 | 14.7487 | 6.3611 | 8.5154 | 5.8081 | 6.0023 | 6.2022 | 6.6806 | 7.647 | 15.9954 | 15.6273 | 15.4906 | 14.4237 | 14.307 | 14.2537 |  |  |  | 10.7596 | 9.2843 | 8.9642 | 8.9577 | 0.12789 | 0.074364 | 12.8911 |  |  | 10.7112 |  |  | 16.9791 | 16.1783 | 15.1653 | 16.4627 | 15.7501 | 14.8759 | 10.7607 | 10.7009 | 11.4996 | 11.356 | 9.1884 |  | 10.7814 | 8.443 | 10.1236 | 9.189 | 11.1985 | 11.899 |  | 12.4156 |  |  | 11.9496 | 12.6296 | 12.697 | [6 empty] | 12.5915 |  |  | 11.3462 |  |  | 9.1057 | 10.3024 | 12.1252 | 7.5507 | 9.2589 | 12.6507 | 7.7585 | 9.5252 | 12.4895 | 9.2198 | 10.3943 | 7.7418 | 10.4582 | 8.2817 | 10.1104 | 7.8106 | 9.6752 | 13.3777 | 10.5492 | 10.2159 | 11.5666 | 8.1319 | 9.7176 | 12.9362 | 7.9648 | 10.3299 | 9.6629 | 9.8918 | 8.4732 | 10.2924 | 0.005188 | 20.9535 | 0.034159 | 0.050179 | -38.1174 | 3.1217 | -0.78 | 0.32 | 0.12514 | -0.6171 | 0.24231 | 0.58148 | 0.20521 | -0.25455 | 0.91572 | 0.41275 | 0.41178 | 0.42649 | 0.38316 | 0.55681 | 0.42961 | 0.41844
42810.4334 | -570 | 18.6495 | 18.7034 | 18.6701 | 18.6808 | 18.0444 | 16.7034 | 14.7748 | 16.7791 | 17.2638 | 17.3596 | 17.3851 | 16.9434 | 15.9854 | 14.5981 | 15.1248 | 15.1029 | 15.6353 | 13.4808 | 13.5956 | 14.1848 |  |  |  | 16.6813 | 16.0188 | 15.1368 | 10.2227 | 9.6922 | 9.9165 | 17.3455 | 16.4692 | 15.2774 | 16.9751 | 16.2578 | 15.267 | 10.904 | 11.9569 |  | 12.3422 | 10.633 | 10.488 | 8.759 |  | 6.4482 | 6.3919 | 5.8572 | 5.9638 | 5.9846 | 6.143 | 6.7158 | 5.1303 | 6.4143 | 4.7702 | 6.6644 | 8.2106 | 42.2106 | 47.1026 | 43.1075 | 15.4998 |  |  | -0.009637 | -0.074825 | 0.21278 | -0.019714 | -0.015608 | -0.28302 | 0.61102 | -0.29455 | -0.26114 | -1.9102 | -0.28902 | 8.8782 | 8.8794 | 2.0086 | 15.9169 | 16.806 | 17.3441 | 17.6628 | 17.634 | 16.611 | 14.9736 | 16.9054 | 17.2337 | 17.5157 | 17.5544 | 17.3002 | 16.514 | 14.7465 | 6.4767 | 8.5171 | 5.8193 | 6.0036 | 6.1574 | 6.6771 | 7.6417 | 15.9902 | 15.6273 | 15.4823 | 14.424 | 14.3021 | 14.2476 |  |  |  | 10.7607 | 9.2792 | 8.9548 | 8.9333 | 0.0036956 | 0.075117 | 12.8942 |  |  | 10.7119 |  |  | 16.9774 | 16.1786 | 15.1628 | 16.4618 | 15.749 | 14.8669 | 10.7495 | 10.7092 | 11.4939 | 11.3555 | 9.2017 |  | 10.7849 | 8.4512 | 10.132 | 9.1968 | 11.2068 | 11.8908 |  | 12.4292 |  |  | 11.9333 | 12.6281 | 12.6995 | [6 empty] | 12.6074 |  |  | 11.3475 |  |  | 9.0956 | 10.3031 | 12.1166 | 7.5585 | 9.2542 | 12.638 | 7.7544 | 9.5279 | 12.4886 | 9.2214 | 10.3905 | 7.7389 | 10.4486 | 8.2857 | 10.1133 | 7.8002 | 9.6712 | 13.3822 | 10.5468 | 10.2205 | 11.5723 | 8.1305 | 9.7177 | 12.9323 | 7.9702 | 10.3335 | 9.6667 | 9.8921 | 8.4746 | 10.304 | -0.018309 | 20.9526 | 0.033711 | 0.049391 | -38.1265 | 3.1217 | -0.86 | 0.23 | -0.1151 | -0.31872 | 0.53748 | -0.1636 | -0.1455 | -0.61959 | 0.91038 | 0.4125 | 0.41183 | 0.42654 | 0.36991 | 0.55496 | 0.42872 | 0.41915
42810.4334 | -569 | 18.6388 | 18.6917 | 18.6508 | 18.6664 | 18.0277 | 16.6831 | 14.7707 | 16.7631 | 17.2515 | 17.3497 | 17.3682 | 16.9234 | 15.975 | 14.5867 | 15.1145 | 15.0921 | 15.6323 | 13.4768 | 13.5937 | 14.1777 |  |  |  | 16.6699 | 16.012 | 15.1374 | 10.2191 | 9.6903 | 9.915 | 17.3566 | 16.4785 | 15.2728 | 16.978 | 16.2739 | 15.2816 | 10.906 | 12.0069 |  | 12.3566 | 10.6478 | 10.4889 | 8.7557 |  | 6.4574 | 6.4007 | 5.8827 | 5.9869 | 6.0317 | 6.1774 | 6.771 | 5.0864 | 6.4325 | 4.809 | 6.6783 | 8.2022 | 42.2386 | 47.1166 | 43.1417 | 15.4822 |  |  | -0.006353 | -0.2667 | -0.002092 | 0.053882 | -0.014948 | -0.15225 | 0.6097 | -0.27352 | -0.20276 | -0.20368 | -0.11953 | 8.8845 | 8.8859 | 2.0086 | 15.9163 | 16.8117 | 17.3462 | 17.6664 | 17.6333 | 16.6243 | 14.9775 | 16.9085 | 17.2357 | 17.5188 | 17.5585 | 17.2968 | 16.5185 | 14.7448 | 6.5813 | 8.5338 | 5.8319 | 6.0173 | 6.1539 | 6.6945 | 7.6532 | 15.9861 | 15.6266 | 15.4828 | 14.4179 | 14.3017 | 14.2442 |  |  |  | 10.7535 | 9.2832 | 8.9607 | 8.9114 | 0.047255 | 0.075117 | 12.8862 |  |  | 10.714 |  |  | 16.9768 | 16.1777 | 15.1603 | 16.4587 | 15.7525 | 14.8637 | 10.758 | 10.7054 | 11.4895 | 11.3521 | 9.2027 |  | 10.7704 | 8.4762 | 10.1238 | 9.1868 | 11.1934 | 11.8583 |  | 12.4088 |  |  | 11.9071 | 12.6054 | 12.6895 | [6 empty] | 12.6106 |  |  | 11.3352 |  |  | 9.0947 | 10.294 | 12.1127 | 7.5643 | 9.2516 | 12.6353 | 7.7562 | 9.5285 | 12.4944 | 9.2168 | 10.3909 | 7.7445 | 10.4468 | 8.2926 | 10.1171 | 7.793 | 9.6652 | 13.3809 | 10.5454 | 10.2209 | 11.5756 | 8.1337 | 9.7141 | 12.9234 | 7.9751 | 10.3321 | 9.6525 | 9.8933 | 8.47 | 10.3068 | -0.11557 | 20.9527 | 0.033476 | 0.050737 | -38.0615 | 3.1217 | -0.8 | 0.3 | -0.093454 | -0.60174 | -0.053294 | 0.27047 | -0.1424 | -0.45447 | 0.90946 | 0.41199 | 0.41086 | 0.42638 | 0.36031 | 0.55489 | 0.42888 | 0.41952
42810.4335 | -568 | 18.6464 | 18.6946 | 18.6658 | 18.6742 | 18.0304 | 16.696 | 14.7738 | 16.7748 | 17.2556 | 17.3515 | 17.3678 | 16.9267 | 15.9832 | 14.5936 | 15.1115 | 15.0881 | 15.6255 | 13.4759 | 13.5942 | 14.1723 |  |  |  | 16.6656 | 16.0021 | 15.1357 | 10.2131 | 9.6898 | 9.9472 | 17.3455 | 16.4715 | 15.2659 | 16.9745 | 16.2674 | 15.2815 | 10.9022 | 12.0269 |  | 12.3547 | 10.6397 | 10.4899 | 8.7398 |  | 6.4567 | 6.3996 | 5.8846 | 5.9985 | 6.0401 | 6.1891 | 6.8 | 5.0633 | 6.4308 | 4.7865 | 6.6789 | 8.2054 | 42.281 | 47.1154 | 43.1823 | 15.4757 |  |  | 0.076443 | -0.051169 | -0.047432 | -0.013142 | -0.11089 | -0.035288 | 0.6281 | -0.17627 | 0.20104 | -0.28676 | -0.34267 | 8.8822 | 8.8834 | 2.0086 | 15.9256 | 16.8225 | 17.3465 | 17.6675 | 17.6454 | 16.6313 | 14.9783 | 16.9128 | 17.2421 | 17.5174 | 17.5633 | 17.3064 | 16.5259 | 14.7546 | 6.644 | 8.5545 | 5.8543 | 6.025 | 6.1622 | 6.6919 | 7.6449 | 15.9914 | 15.6315 | 15.4847 | 14.4216 | 14.3002 | 14.2434 |  |  |  | 10.7518 | 9.292 | 8.9713 | 8.9008 | 0.20933 | 0.041617 | 12.8863 |  |  | 10.6996 |  |  | 16.9755 | 16.1806 | 15.1648 | 16.4656 | 15.7447 | 14.8685 | 10.7558 | 10.699 | 11.4769 | 11.3404 | 9.2309 |  | 10.7761 | 8.5046 | 10.1179 | 9.2198 | 11.1983 | 11.8181 |  | 12.4017 |  |  | 11.8747 | 12.6213 | 12.6641 | [6 empty] | 12.6079 |  |  | 11.3289 |  |  | 9.0964 | 10.2857 | 12.1184 | 7.5671 | 9.2542 | 12.6371 | 7.7551 | 9.5227 | 12.5061 | 9.2182 | 10.3965 | 7.7586 | 10.4532 | 8.302 | 10.1182 | 7.7849 | 9.6556 | 13.3727 | 10.5431 | 10.2159 | 11.5811 | 8.1348 | 9.7141 | 12.9216 | 7.9695 | 10.3273 | 9.6382 | 9.8825 | 8.4698 | 10.3082 | -0.21014 | 20.9517 | 0.033895 | 0.051193 | -37.9941 | 3.1217 | -0.49 | 0.3 | 0.32419 | -0.26357 | -0.25377 | -0.13358 | -0.38786 | -0.2188 | 0.9231 | 0.41139 | 0.40988 | 0.42563 | 0.35305 | 0.55144 | 0.42919 | 0.41976
42810.4335 | -567 | 18.6396 | 18.6895 | 18.6603 | 18.669 | 18.0233 | 16.6896 | 14.7679 | 16.77 | 17.248 | 17.3465 | 17.3654 | 16.9204 | 15.9773 | 14.5871 | 15.1078 | 15.0886 | 15.6255 | 13.4811 | 13.5932 | 14.1716 |  |  |  | 16.6696 | 16.0061 | 15.1317 | 10.2144 | 9.6953 | 9.9811 | 17.3511 | 16.4694 | 15.2655 | 16.9769 | 16.2629 | 15.2754 | 10.9033 | 12.0622 |  | 12.3426 | 10.6435 | 10.4873 | 8.7433 |  | 6.4556 | 6.41 | 5.8936 | 6.0076 | 6.0483 | 6.1969 | 6.8185 | 5.0703 | 6.4306 | 4.7786 | 6.6709 | 8.2102 | 42.3043 | 47.1213 | 43.2249 | 15.4744 |  |  | 0.081043 | -0.35804 | 0.052448 | -0.089366 | -0.086576 | 0.069852 | 0.5867 | -0.20518 | -0.71767 | 0.37474 | -0.37744 | 8.8739 | 8.8752 | 2.0085 | 15.9351 | 16.8168 | 17.3518 | 17.6836 | 17.636 | 16.6227 | 14.9837 | 16.9164 | 17.2372 | 17.5279 | 17.5687 | 17.3066 | 16.5167 | 14.7614 | 6.7241 | 8.5553 | 5.8843 | 6.0297 | 6.2074 | 6.6877 | 7.6433 | 15.9922 | 15.633 | 15.4854 | 14.4249 | 14.3012 | 14.2543 |  |  |  | 10.7523 | 9.3031 | 8.9756 | 8.8965 | 0.22615 | 0.0092466 | 12.8756 |  |  | 10.6898 |  |  | 16.9702 | 16.1815 | 15.1614 | 16.4602 | 15.7429 | 14.8563 | 10.7431 | 10.6971 | 11.4684 | 11.3366 | 9.2694 |  | 10.7629 | 8.529 | 10.1191 | 9.2301 | 11.1862 | 11.7904 |  | 12.4037 |  |  | 11.8496 | 12.6331 | 12.6648 | [6 empty] | 12.6119 |  |  | 11.3235 |  |  | 9.1043 | 10.2838 | 12.1224 | 7.5624 | 9.25 | 12.6259 | 7.7632 | 9.5186 | 12.5223 | 9.2219 | 10.397 | 7.7706 | 10.4475 | 8.3079 | 10.1248 | 7.7827 | 9.6515 | 13.3664 | 10.5411 | 10.2049 | 11.5807 | 8.1304 | 9.7112 | 12.9133 | 7.9703 | 10.3363 | 9.6276 | 9.8778 | 8.472 | 10.3058 | 0.00904 | 20.9532 | 0.033286 | 0.051156 | -38.0423 | 3.1217 | -0.63 | 0.27 | 0.33382 | -0.69722 | 0.26685 | -0.34833 | -0.34272 | 0.30784 | 0.89217 | 0.40989 | 0.40924 | 0.42494 | 0.34366 | 0.54792 | 0.42913 | 0.4199
42810.4335 | -566 | 18.6357 | 18.6844 | 18.652 | 18.6602 | 18.0191 | 16.6864 | 14.7625 | 16.7633 | 17.2455 | 17.3421 | 17.3636 | 16.9208 | 15.9746 | 14.5801 | 15.1097 | 15.092 | 15.6287 | 13.4835 | 13.5965 | 14.1776 |  |  |  | 16.6752 | 16.0141 | 15.1328 | 10.2331 | 9.6971 | 10.0224 | 17.345 | 16.4675 | 15.2684 | 16.9727 | 16.2568 | 15.2692 | 10.8946 | 12.0784 |  | 12.3423 | 10.646 | 10.4872 | 8.7409 |  | 6.4591 | 6.4117 | 5.8902 | 6.0044 | 6.0489 | 6.1982 | 6.8552 | 5.1123 | 6.4337 | 4.8073 | 6.6788 | 8.2056 | 42.337 | 47.1269 | 43.2649 | 15.4868 |  |  | 0.006135 | -0.15039 | 0.17862 | 0.17413 | 0.03762 | 0.079052 | 0.44806 | -0.19993 | -0.086192 | -2.2163 | -0.21172 | 8.8773 | 8.8787 | 2.0084 | 15.9127 | 16.8145 | 17.3429 | 17.6613 | 17.6289 | 16.6213 | 14.9746 | 16.905 | 17.2255 | 17.514 | 17.5532 | 17.2981 | 16.5109 | 14.746 | 6.7894 | 8.5841 | 5.9166 | 6.0527 | 6.2362 | 6.6948 | 7.64 | 15.9931 | 15.6242 | 15.483 | 14.4224 | 14.3064 | 14.256 |  |  |  | 10.7554 | 9.3069 | 8.9696 | 8.9039 | 0.23466 | 0.022232 | 12.878 |  |  | 10.6909 |  |  | 16.9703 | 16.1717 | 15.1538 | 16.4517 | 15.7469 | 14.8538 | 10.7375 | 10.6926 | 11.4583 | 11.3281 | 9.3001 |  | 10.7718 | 8.5315 | 10.125 | 9.2367 | 11.1914 | 11.7845 |  | 12.4062 |  |  | 11.8512 | 12.6586 | 12.6752 | [6 empty] | 12.6077 |  |  | 11.3267 |  |  | 9.1027 | 10.284 | 12.1319 | 7.5488 | 9.2537 | 12.6169 | 7.7648 | 9.5179 | 12.5252 | 9.218 | 10.3984 | 7.7787 | 10.4445 | 8.3151 | 10.1293 | 7.7959 | 9.6566 | 13.3636 | 10.5433 | 10.1976 | 11.5785 | 8.1337 | 9.7086 | 12.8997 | 7.9712 | 10.3441 | 9.6228 | 9.8864 | 8.4764 | 10.3107 | 0.06682 | 20.9537 | 0.033131 | 0.05036 | -38.1176 | 3.1217 | -0.26 | 0.39 | 0.091854 | -0.45188 | 0.49245 | 0.48624 | 0.22592 | 0.32749 | 0.77966 | 0.40933 | 0.40937 | 0.42493 | 0.33722 | 0.54395 | 0.42891 | 0.4198
42810.4335 | -565 | 18.6306 | 18.6861 | 18.6647 | 18.6646 | 18.0217 | 16.6905 | 14.7619 | 16.77 | 17.2461 | 17.3453 | 17.3651 | 16.9208 | 15.9794 | 14.5848 | 15.1046 | 15.0887 | 15.6285 | 13.4814 | 13.5942 | 14.1737 |  |  |  | 16.6777 | 16.0198 | 15.1384 | 10.2465 | 9.7036 | 10.0836 | 17.3434 | 16.4658 | 15.2745 | 16.9745 | 16.265 | 15.2737 | 10.8939 | 12.0844 |  | 12.3531 | 10.6488 | 10.4962 | 8.7227 |  | 6.4561 | 6.4107 | 5.883 | 5.9987 | 6.0352 | 6.1836 | 6.8429 | 5.1278 | 6.4366 | 4.8617 | 6.6761 | 8.2059 | 42.3747 | 47.1363 | 43.2936 | 15.4903 |  |  | 0.004163 | -0.17076 | -0.035604 | 0.019714 | -0.077376 | -0.02806 | 0.47762 | -0.084932 | -0.2374 | -0.80769 | -0.40287 | 8.8757 | 8.8768 | 2.0086 | 15.9209 | 16.814 | 17.3488 | 17.6691 | 17.6284 | 16.6221 | 14.9796 | 16.9097 | 17.2349 | 17.5261 | 17.5604 | 17.3021 | 16.5178 | 14.754 | 6.8414 | 8.6089 | 5.9903 | 6.0783 | 6.3324 | 6.698 | 7.6488 | 15.9836 | 15.6215 | 15.4856 | 14.4235 | 14.3035 | 14.2476 |  |  |  | 10.7498 | 9.3026 | 8.9675 | 8.9126 | 0.12465 | 0.017904 | 12.8767 |  |  | 10.6852 |  |  | 16.9767 | 16.1706 | 15.1594 | 16.4534 | 15.7464 | 14.852 | 10.736 | 10.6848 | 11.4508 | 11.323 | 9.2922 |  | 10.7814 | 8.5282 | 10.1248 | 9.2394 | 11.1981 | 11.7673 |  | 12.4072 |  |  | 11.8334 | 12.6593 | 12.6817 | [6 empty] | 12.6005 |  |  | 11.3215 |  |  | 9.097 | 10.2803 | 12.139 | 7.5457 | 9.258 | 12.6128 | 7.7601 | 9.5151 | 12.5263 | 9.2158 | 10.3971 | 7.7697 | 10.4442 | 8.3229 | 10.1331 | 7.8051 | 9.6561 | 13.3605 | 10.5391 | 10.1874 | 11.5751 | 8.132 | 9.7065 | 12.886 | 7.9794 | 10.345 | 9.6285 | 9.8863 | 8.4841 | 10.3158 | -0.13522 | 20.9532 | 0.032431 | 0.049427 | -38.15 | 3.1216 | -0.24 | 0.28 | 0.075673 | -0.4815 | -0.21986 | 0.1636 | -0.32399 | -0.19511 | 0.80496 | 0.40987 | 0.40945 | 0.42508 | 0.33182 | 0.53678 | 0.4294 | 0.41937
42810.4335 | -564 | 18.6296 | 18.6889 | 18.6586 | 18.6617 | 18.0283 | 16.6994 | 14.7631 | 16.7642 | 17.2518 | 17.3442 | 17.3601 | 16.9288 | 15.9808 | 14.5829 | 15.1046 | 15.09 | 15.6256 | 13.4769 | 13.5953 | 14.1685 |  |  |  | 16.6741 | 16.0142 | 15.128 | 10.2522 | 9.7103 | 10.1248 | 17.3437 | 16.4636 | 15.2684 | 16.9721 | 16.2618 | 15.2639 | 10.8999 | 12.0917 |  | 12.3482 | 10.6502 | 10.4987 | 8.6952 |  | 6.4526 | 6.4105 | 5.8881 | 6.0048 | 6.0352 | 6.1737 | 6.819 | 5.1261 | 6.4378 | 4.842 | 6.6783 | 8.2056 | 42.4061 | 47.1502 | 43.33 | 15.4976 |  |  | -0.10886 | 0.061199 | 0.019592 | 0.005914 | 0.018564 | 0.15462 | 0.65373 | -0.17496 | -0.62212 | -0.24249 | -0.23676 | 8.8733 | 8.8743 | 2.0083 | 15.9228 | 16.8065 | 17.3439 | 17.6651 | 17.6266 | 16.6237 | 14.9737 | 16.9071 | 17.2283 | 17.5179 | 17.5567 | 17.3023 | 16.5106 | 14.7475 | 6.8517 | 8.5853 | 6.116 | 6.087 | 6.3711 | 6.6931 | 7.6381 | 15.987 | 15.6216 | 15.4906 | 14.4199 | 14.306 | 14.2448 |  |  |  | 10.7547 | 9.3075 | 8.9681 | 8.9372 | 0.18259 | -0.0018572 | 12.8734 |  |  | 10.6819 |  |  | 16.9701 | 16.1704 | 15.1607 | 16.4517 | 15.7387 | 14.8472 | 10.7368 | 10.6969 | 11.4481 | 11.33 | 9.293 |  | 10.7768 | 8.5599 | 10.1313 | 9.2402 | 11.2084 | 11.7556 |  | 12.408 |  |  | 11.825 | 12.6596 | 12.6789 | [6 empty] | 12.6063 |  |  | 11.3029 |  |  | 9.0875 | 10.2735 | 12.1462 | 7.5465 | 9.2477 | 12.6027 | 7.7601 | 9.5165 | 12.5202 | 9.2154 | 10.3956 | 7.7639 | 10.4322 | 8.3255 | 10.13 | 7.8082 | 9.6506 | 13.362 | 10.5327 | 10.1831 | 11.5872 | 8.134 | 9.7044 | 12.8793 | 7.986 | 10.3618 | 9.6377 | 9.8855 | 8.4817 | 10.3214 | -0.04874 | 20.9535 | 0.03172 | 0.048725 | -38.1245 | 3.1217 | -0.43 | 0.4 | -0.387 | 0.28826 | 0.1631 | 0.089608 | 0.15869 | 0.45799 | 0.94172 | 0.40969 | 0.40879 | 0.42539 | 0.3301 | 0.52156 | 0.43036 | 0.41885
42810.4335 | -563 | 18.6418 | 18.6905 | 18.6632 | 18.6699 | 18.0326 | 16.7022 | 14.7676 | 16.7698 | 17.2596 | 17.3502 | 17.3665 | 16.9263 | 15.9839 | 14.5917 | 15.1053 | 15.0787 | 15.6249 | 13.4733 | 13.5932 | 14.1657 |  |  |  | 16.6701 | 16.0077 | 15.1245 | 10.2564 | 9.7025 | 10.1403 | 17.3412 | 16.4677 | 15.2698 | 16.9747 | 16.2607 | 15.2821 | 10.8938 | 12.1086 |  | 12.3537 | 10.6578 | 10.5114 | 8.6798 |  | 6.454 | 6.4039 | 5.892 | 6.0032 | 6.0356 | 6.1772 | 6.7985 | 5.0817 | 6.4394 | 4.7592 | 6.6735 | 8.2016 | 42.4477 | 47.184 | 43.3559 | 15.497 |  |  | 0.092871 | -0.028825 | 0.038648 | -0.095282 | -0.097088 | -0.060916 | 0.51836 | -0.14539 | -0.16442 | -0.1934 | -0.291 | 8.8722 | 8.8732 | 2.0088 | 15.9248 | 16.8106 | 17.3474 | 17.6674 | 17.631 | 16.6204 | 14.9765 | 16.9087 | 17.2319 | 17.5191 | 17.5637 | 17.3015 | 16.5139 | 14.7445 | 6.8425 | 8.5638 | 6.1764 | 6.0802 | 6.3551 | 6.6958 | 7.6412 | 15.9846 | 15.6308 | 15.4832 | 14.4223 | 14.3094 | 14.2489 |  |  |  | 10.7524 | 9.3157 | 8.9738 | 8.9449 | 0.061234 | 0.037288 | 12.8778 |  |  | 10.6935 |  |  | 16.9706 | 16.1718 | 15.1556 | 16.4535 | 15.7421 | 14.863 | 10.7329 | 10.7019 | 11.4454 | 11.3225 | 9.2978 |  | 10.777 | 8.6371 | 10.1308 | 9.2397 | 11.1988 | 11.7461 |  | 12.4082 |  |  | 11.8375 | 12.6676 | 12.6833 | [6 empty] | 12.6084 |  |  | 11.2945 |  |  | 9.088 | 10.2708 | 12.1436 | 7.5442 | 9.2503 | 12.6119 | 7.7666 | 9.5193 | 12.5206 | 9.2219 | 10.4017 | 7.755 | 10.4378 | 8.334 | 10.1464 | 7.8148 | 9.6462 | 13.3613 | 10.5311 | 10.1762 | 11.6042 | 8.1189 | 9.6882 | 12.8717 | 8.0024 | 10.3737 | 9.6395 | 9.8851 | 8.4797 | 10.3124 | -0.0030938 | 20.9536 | 0.032385 | 0.048073 | -38.1664 | 3.1216 | -0.43 | 0.36 | 0.35746 | -0.19783 | 0.22907 | -0.35967 | -0.36292 | -0.28747 | 0.83857 | 0.40956 | 0.40662 | 0.42509 | 0.33143 | 0.51522 | 0.43058 | 0.41856
42810.4335 | -562 | 18.6387 | 18.6918 | 18.663 | 18.6683 | 18.0287 | 16.7036 | 14.7642 | 16.765 | 17.2559 | 17.3579 | 17.3645 | 16.9213 | 15.9821 | 14.583 | 15.088 | 15.0704 | 15.6203 | 13.4588 | 13.5878 | 14.159 |  |  |  | 16.6585 | 15.9989 | 15.1167 | 10.2531 | 9.6975 | 10.1572 | 17.3347 | 16.4621 | 15.2572 | 16.9721 | 16.2594 | 15.269 | 10.8891 | 12.1246 |  | 12.3456 | 10.654 | 10.5126 | 8.6813 |  | 6.4477 | 6.4133 | 5.9061 | 6.0136 | 6.0442 | 6.1706 | 6.8084 | 5.0045 | 6.4481 | 4.7315 | 6.6903 | 8.2069 | 42.4853 | 47.2133 | 43.3861 | 15.5026 |  |  | 0.14938 | -0.17931 | -0.019176 | -0.030226 | 0.004764 | 0.009396 | 0.58736 | -0.21241 | -1.2478 | -1.0746 | -0.28902 | 8.8883 | 8.8893 | 2.0082 | 15.923 | 16.8153 | 17.3479 | 17.6735 | 17.6379 | 16.6307 | 14.9826 | 16.9185 | 17.2391 | 17.5188 | 17.564 | 17.3117 | 16.5245 | 14.7502 | 6.8389 | 8.5344 | 6.1133 | 6.0024 | 6.3408 | 6.6938 | 7.6466 | 15.9675 | 15.6198 | 15.4659 | 14.4074 | 14.2871 | 14.2334 |  |  |  | 10.7477 | 9.3121 | 8.9581 | 8.936 | 0.047862 | 0.14701 | 12.8767 |  |  | 10.686 |  |  | 16.9763 | 16.1672 | 15.1643 | 16.458 | 15.7418 | 14.8639 | 10.741 | 10.6991 | 11.4414 | 11.3263 | 9.2927 |  | 10.7671 | 8.6861 | 10.1199 | 9.2257 | 11.1835 | 11.7456 |  | 12.3851 |  |  | 11.8244 | 12.6767 | 12.6888 | [6 empty] | 12.6135 |  |  | 11.3004 |  |  | 9.0863 | 10.2665 | 12.1386 | 7.5567 | 9.2486 | 12.6132 | 7.7731 | 9.5153 | 12.5214 | 9.2202 | 10.4014 | 7.7557 | 10.4374 | 8.3405 | 10.1494 | 7.8168 | 9.6382 | 13.3653 | 10.5303 | 10.1664 | 11.6181 | 8.1197 | 9.6947 | 12.875 | 8.0036 | 10.372 | 9.6492 | 9.8793 | 8.477 | 10.3166 | -0.17836 | 20.9532 | 0.033206 | 0.048681 | -38.0696 | 3.1216 | -0.14 | 0.24 | 0.45336 | -0.4934 | -0.16136 | -0.20258 | 0.08039 | 0.1129 | 0.89263 | 0.40938 | 0.4049 | 0.42497 | 0.33161 | 0.52286 | 0.43039 | 0.41865
42810.4335 | -561 | 18.6378 | 18.685 | 18.6587 | 18.6705 | 18.0251 | 16.6929 | 14.764 | 16.7664 | 17.2508 | 17.3479 | 17.3682 | 16.9191 | 15.9774 | 14.5833 | 15.0897 | 15.079 | 15.623 | 13.4772 | 13.589 | 14.1591 |  |  |  | 16.6639 | 16.0033 | 15.1298 | 10.2616 | 9.7003 | 10.1896 | 17.3297 | 16.4585 | 15.2556 | 16.9704 | 16.2597 | 15.2696 | 10.8967 | 12.1438 |  | 12.3504 | 10.6588 | 10.5118 | 8.7043 |  | 6.4429 | 6.4112 | 5.8949 | 6.0142 | 6.0378 | 6.1688 | 6.7909 | 4.9346 | 6.4438 | 4.7655 | 6.6797 | 8.1978 | 42.4983 | 47.2209 | 43.3966 | 15.4946 |  |  | 0.018619 | -0.3173 | 0.082676 | -0.092654 | 0.002792 | 0.079708 | 0.66884 | -0.28601 | -0.30862 | 1.8425 | -0.23736 | 8.883 | 8.8844 | 2.0087 | 15.9145 | 16.8141 | 17.3455 | 17.6653 | 17.6276 | 16.6115 | 14.9714 | 16.9122 | 17.2365 | 17.5229 | 17.5602 | 17.3005 | 16.5182 | 14.7562 | 6.819 | 8.5053 | 6.0647 | 5.9392 | 6.3417 | 6.7007 | 7.649 | 15.9753 | 15.6202 | 15.4776 | 14.4213 | 14.2993 | 14.2378 |  |  |  | 10.7502 | 9.3283 | 8.9798 | 8.954 | -0.010284 | -0.090499 | 12.8805 |  |  | 10.6896 |  |  | 16.9754 | 16.1801 | 15.1561 | 16.466 | 15.7444 | 14.8651 | 10.7464 | 10.6999 | 11.4383 | 11.3277 | 9.2824 |  | 10.7661 | 8.7074 | 10.1205 | 9.2175 | 11.181 | 11.7787 |  | 12.3898 |  |  | 11.8236 | 12.6761 | 12.6801 | [6 empty] | 12.5894 |  |  | 11.2922 |  |  | 9.0725 | 10.2517 | 12.1272 | 7.5567 | 9.238 | 12.6006 | 7.7674 | 9.5045 | 12.5117 | 9.2171 | 10.3907 | 7.7446 | 10.4291 | 8.3363 | 10.1378 | 7.8237 | 9.6368 | 13.3663 | 10.5271 | 10.1629 | 11.6199 | 8.1279 | 9.6928 | 12.8697 | 8.0088 | 10.3751 | 9.65 | 9.8737 | 8.4799 | 10.3149 | -0.073008 | 20.9536 | 0.033326 | 0.049977 | -38.0807 | 3.1216 | -0.15 | 0.32 | 0.16007 | -0.65635 | 0.33504 | -0.35468 | 0.061542 | 0.32883 | 0.95253 | 0.40963 | 0.40434 | 0.42512 | 0.33463 | 0.52854 | 0.43 | 0.41823
42810.4336 | -560 | 18.6241 | 18.6833 | 18.6556 | 18.6642 | 18.0259 | 16.6847 | 14.7566 | 16.762 | 17.2488 | 17.3454 | 17.3652 | 16.9165 | 15.975 | 14.5772 | 15.0922 | 15.0863 | 15.626 | 13.4719 | 13.5998 | 14.1775 |  |  |  | 16.6747 | 16.013 | 15.1367 | 10.27 | 9.7094 | 10.2112 | 17.3339 | 16.4632 | 15.2582 | 16.9727 | 16.2581 | 15.2681 | 10.8877 | 12.1473 |  | 12.3468 | 10.662 | 10.5168 | 8.7222 |  | 6.4562 | 6.418 | 5.9039 | 6.0214 | 6.0474 | 6.1725 | 6.7918 | 4.91 | 6.4502 | 4.76 | 6.6918 | 8.2044 | 42.5216 | 47.2556 | 43.4155 | 15.4932 |  |  | 0.071187 | 0.033599 | 0.1175 | -0.001314 | -0.029408 | -0.012944 | 0.53414 | -0.26432 | -0.41954 | 0.25851 | -0.18768 | 8.8895 | 8.8907 | 2.0084 | 15.9092 | 16.8082 | 17.3391 | 17.6625 | 17.6293 | 16.6182 | 14.9733 | 16.9112 | 17.244 | 17.5225 | 17.5664 | 17.3005 | 16.517 | 14.7478 | 6.7376 | 8.507 | 5.9802 | 5.9015 | 6.3401 | 6.6948 | 7.6487 | 15.9747 | 15.6159 | 15.4761 | 14.4109 | 14.2965 | 14.2415 |  |  |  | 10.7542 | 9.3341 | 8.9782 | 8.9536 | -0.066404 | -0.0012926 | 12.8789 |  |  | 10.6797 |  |  | 16.9697 | 16.1665 | 15.1462 | 16.4576 | 15.7489 | 14.868 | 10.7468 | 10.7013 | 11.4286 | 11.32 | 9.2482 |  | 10.7639 | 8.6896 | 10.1216 | 9.2298 | 11.1888 | 11.8132 |  | 12.3934 |  |  | 11.8322 | 12.6844 | 12.6741 | [6 empty] | 12.583 |  |  | 11.2827 |  |  | 9.0835 | 10.2528 | 12.1259 | 7.5471 | 9.2463 | 12.5997 | 7.771 | 9.5081 | 12.5051 | 9.215 | 10.3974 | 7.7564 | 10.4364 | 8.3425 | 10.1565 | 7.8237 | 9.6351 | 13.3561 | 10.519 | 10.1495 | 11.6231 | 8.1232 | 9.6838 | 12.8787 | 8.0112 | 10.3645 | 9.6594 | 9.8766 | 8.4773 | 10.3103 | -0.095157 | 20.9532 | 0.033831 | 0.051026 | -38.0458 | 3.1217 | -0.15 | 0.37 | 0.313 | 0.21359 | 0.39943 | -0.042238 | -0.19973 | -0.13251 | 0.85123 | 0.41051 | 0.40487 | 0.42504 | 0.34299 | 0.53789 | 0.42921 | 0.41838
42810.4336 | -559 | 18.6258 | 18.6861 | 18.6609 | 18.6674 | 18.0269 | 16.6886 | 14.7609 | 16.7632 | 17.2482 | 17.3503 | 17.3655 | 16.9238 | 15.9767 | 14.581 | 15.0854 | 15.0819 | 15.618 | 13.4743 | 13.5894 | 14.1614 |  |  |  | 16.6662 | 16.013 | 15.1288 | 10.2723 | 9.7033 | 10.2068 | 17.3293 | 16.4592 | 15.2537 | 16.9735 | 16.2528 | 15.2668 | 10.8842 | 12.1572 |  | 12.343 | 10.6602 | 10.5227 | 8.7316 |  | 6.4669 | 6.4281 | 5.9194 | 6.0299 | 6.0663 | 6.1917 | 6.8364 | 4.9317 | 6.4542 | 4.7338 | 6.6975 | 8.1953 | 42.5352 | 47.2865 | 43.4313 | 15.4869 |  |  | 0.14282 | -0.34359 | 0.041936 | -0.2773 | -0.028092 | -0.18051 | 0.52822 | -0.33004 | -0.12141 | -0.42292 | -0.37744 | 8.8852 | 8.8864 | 2.0086 | 15.903 | 16.7974 | 17.3304 | 17.6534 | 17.628 | 16.6129 | 14.9688 | 16.9074 | 17.2333 | 17.5148 | 17.5465 | 17.2961 | 16.5045 | 14.7405 | 6.6272 | 8.507 | 5.9227 | 5.8758 | 6.2885 | 6.6932 | 7.6436 | 15.9738 | 15.6148 | 15.4786 | 14.414 | 14.2958 | 14.2412 |  |  |  | 10.7532 | 9.34 | 8.9766 | 8.9761 | 0.12262 | 0.044628 | 12.8818 |  |  | 10.6859 |  |  | 16.9678 | 16.1702 | 15.153 | 16.4648 | 15.7447 | 14.8621 | 10.7567 | 10.7001 | 11.4254 | 11.3165 | 9.235 |  | 10.7624 | 8.6466 | 10.1143 | 9.2222 | 11.1799 | 11.8313 |  | 12.3904 |  |  | 11.8659 | 12.6885 | 12.6803 | [6 empty] | 12.5993 |  |  | 11.2738 |  |  | 9.0875 | 10.2436 | 12.1203 | 7.5656 | 9.2478 | 12.5916 | 7.7826 | 9.508 | 12.4981 | 9.2287 | 10.4067 | 7.7614 | 10.4486 | 8.3433 | 10.1614 | 7.8358 | 9.628 | 13.3529 | 10.5253 | 10.1555 | 11.639 | 8.1214 | 9.6938 | 12.8812 | 8.0029 | 10.3711 | 9.6506 | 9.8774 | 8.4773 | 10.3092 | 0.021752 | 20.9538 | 0.033969 | 0.052003 | -38.0228 | 3.1217 | -0.33 | 0.35 | 0.44332 | -0.68302 | 0.23862 | -0.61361 | -0.19522 | -0.49486 | 0.84653 | 0.41083 | 0.40582 | 0.42496 | 0.35506 | 0.54368 | 0.42883 | 0.41772
42810.4336 | -558 | 18.624 | 18.6853 | 18.6553 | 18.6647 | 18.0256 | 16.6852 | 14.7624 | 16.7585 | 17.2473 | 17.3413 | 17.3624 | 16.9282 | 15.97 | 14.5751 | 15.1022 | 15.0858 | 15.6243 | 13.4771 | 13.5977 | 14.1712 |  |  |  | 16.6699 | 16.0065 | 15.1326 | 10.2772 | 9.7103 | 10.2266 | 17.327 | 16.4544 | 15.2531 | 16.9629 | 16.2505 | 15.2647 | 10.8858 | 12.134 |  | 12.3373 | 10.6581 | 10.5206 | 8.7213 |  | 6.4586 | 6.4297 | 5.9141 | 6.0305 | 6.0549 | 6.2264 | 6.8852 | 4.9933 | 6.4524 | 4.7456 | 6.6912 | 8.191 | 42.547 | 47.3069 | 43.4358 | 15.4774 |  |  | -0.041837 | -0.21085 | -0.014576 | -0.004598 | 0.075732 | 0.21244 | 0.72996 | -0.11844 | -1.2227 | -0.3946 | -0.32439 | 8.8804 | 8.8816 | 2.0086 | 15.8985 | 16.7997 | 17.3306 | 17.6572 | 17.6201 | 16.6075 | 14.9619 | 16.9045 | 17.2284 | 17.5109 | 17.5534 | 17.3 | 16.5062 | 14.7536 | 6.6015 | 8.5001 | 5.8509 | 5.8647 | 6.1889 | 6.6899 | 7.6469 | 15.9703 | 15.6171 | 15.4793 | 14.4147 | 14.306 | 14.2378 |  |  |  | 10.7548 | 9.3349 | 8.9732 | 9.0247 | 0.11391 | 0.010564 | 12.8797 |  |  | 10.6848 |  |  | 16.9717 | 16.1803 | 15.158 | 16.4573 | 15.7383 | 14.854 | 10.759 | 10.704 | 11.4168 | 11.3107 | 9.2402 |  | 10.7596 | 8.6388 | 10.1139 | 9.2413 | 11.1877 | 11.8482 |  | 12.3941 |  |  | 11.8858 | 12.688 | 12.6746 | [6 empty] | 12.592 |  |  | 11.2759 |  |  | 9.0721 | 10.2434 | 12.1204 | 7.5666 | 9.2505 | 12.5769 | 7.7643 | 9.5084 | 12.4976 | 9.2303 | 10.4063 | 7.7716 | 10.4463 | 8.3609 | 10.1649 | 7.8219 | 9.5898 | 13.3429 | 10.5049 | 10.1308 | 11.6284 | 8.1135 | 9.6755 | 12.8756 | 7.9788 | 10.3588 | 9.6608 | 9.8743 | 8.4675 | 10.302 | 0.087043 | 20.9539 | 0.033338 | 0.051077 | -38.0019 | 3.1217 | -0.48 | 0.36 | -0.23995 | -0.53506 | -0.14068 | -0.079014 | 0.32055 | 0.53689 | 0.9952 | 0.41059 | 0.40602 | 0.42468 | 0.35754 | 0.55205 | 0.42917 | 0.41642
42810.4336 | -557 | 18.6193 | 18.6831 | 18.657 | 18.6581 | 18.0206 | 16.6838 | 14.7564 | 16.7623 | 17.2487 | 17.3514 | 17.3588 | 16.9187 | 15.9671 | 14.5733 | 15.0978 | 15.085 | 15.6217 | 13.4688 | 13.5911 | 14.1689 |  |  |  | 16.6676 | 16.0116 | 15.1261 | 10.2772 | 9.71 | 10.2331 | 17.3259 | 16.4521 | 15.2546 | 16.9581 | 16.244 | 15.2607 | 10.8832 | 12.096 |  | 12.3317 | 10.6474 | 10.5183 | 8.7164 |  | 6.4559 | 6.4307 | 5.9199 | 6.0331 | 6.0622 | 6.2735 | 6.9549 | 5.0786 | 6.4525 | 4.8112 | 6.6925 | 8.1945 | 42.552 | 47.3184 | 43.4532 | 15.4692 |  |  | -0.005037 | -0.020281 | 0.041936 | 0.13405 | -0.17463 | -0.024772 | 0.60642 | -0.23936 | 0.059952 | 0.27718 | -0.28842 | 8.8901 | 8.8913 | 2.0084 | 15.9053 | 16.8043 | 17.3377 | 17.6607 | 17.6266 | 16.6157 | 14.9762 | 16.9073 | 17.2366 | 17.5213 | 17.5639 | 17.3044 | 16.5151 | 14.7524 | 6.6332 | 8.5363 | 5.7987 | 5.8927 | 6.1577 | 6.7002 | 7.6572 | 15.9704 | 15.611 | 15.4732 | 14.4118 | 14.2948 | 14.2328 |  |  |  | 10.7492 | 9.3326 | 8.9697 | 9.0296 | 0.092637 | 0.071353 | 12.8752 |  |  | 10.6753 |  |  | 16.96 | 16.1703 | 15.1418 | 16.4519 | 15.7327 | 14.8493 | 10.7613 | 10.6933 | 11.4122 | 11.2967 | 9.2402 |  | 10.7588 | 8.6564 | 10.1143 | 9.2351 | 11.186 | 11.8293 |  | 12.3853 |  |  | 11.8992 | 12.6936 | 12.6935 | [6 empty] | 12.5876 |  |  | 11.2996 |  |  | 9.0774 | 10.2347 | 12.1193 | 7.5824 | 9.2374 | 12.5727 | 7.7597 | 9.5085 | 12.5143 | 9.2361 | 10.4077 | 7.7824 | 10.4363 | 8.3732 | 10.1729 | 7.8172 | 9.5649 | 13.3393 | 10.5047 | 10.1419 | 11.6406 | 8.1261 | 9.6837 | 12.8809 | 7.9772 | 10.3654 | 9.6636 | 9.8791 | 8.4768 | 10.3091 | -0.18857 | 20.9536 | 0.032953 | 0.051127 | -38.1481 | 3.1217 | -0.82 | 0.34 | -0.083261 | -0.16595 | 0.23862 | 0.42663 | -0.48681 | -0.18335 | 0.90716 | 0.41057 | 0.40554 | 0.4248 | 0.35521 | 0.55904 | 0.42922 | 0.4161
42810.4336 | -556 | 18.6265 | 18.6848 | 18.6636 | 18.667 | 18.0283 | 16.6925 | 14.7569 | 16.7757 | 17.259 | 17.3551 | 17.3708 | 16.9241 | 15.9749 | 14.5793 | 15.0911 | 15.0787 | 15.6252 | 13.4711 | 13.5916 | 14.1683 |  |  |  | 16.6707 | 16.0105 | 15.1269 | 10.2823 | 9.7019 | 10.2453 | 17.319 | 16.46 | 15.256 | 16.9565 | 16.2466 | 15.2612 | 10.8837 | 12.0789 |  | 12.3336 | 10.6503 | 10.5298 | 8.7314 |  | 6.4593 | 6.4422 | 5.917 | 6.0378 | 6.0777 | 6.3041 | 6.9817 | 5.0778 | 6.4613 | 4.8748 | 6.6938 | 8.1964 | 42.5622 | 47.3173 | 43.4688 | 15.4545 |  |  | 0.056731 | -0.072193 | 0.064276 | -0.26679 | 0.13159 | 0.15462 | 0.56765 | -0.11384 | -0.48162 | -2.3067 | -0.29041 | 8.8801 | 8.8812 | 2.0085 | 15.9061 | 16.8048 | 17.3349 | 17.6607 | 17.6241 | 16.6114 | 14.9684 | 16.9046 | 17.2361 | 17.5203 | 17.562 | 17.3038 | 16.5172 | 14.7528 | 6.6743 | 8.5609 | 5.7895 | 5.9118 | 6.1399 | 6.7041 | 7.6616 | 15.9643 | 15.6102 | 15.4648 | 14.4037 | 14.2939 | 14.2294 |  |  |  | 10.7473 | 9.3264 | 8.9655 | 9.0428 | 0.043203 | 0.089232 | 12.8727 |  |  | 10.6827 |  |  | 16.9695 | 16.1744 | 15.1464 | 16.4562 | 15.7363 | 14.857 | 10.7649 | 10.6985 | 11.4158 | 11.3059 | 9.2413 |  | 10.7545 | 8.6833 | 10.1158 | 9.2412 | 11.1851 | 11.8229 |  | 12.3908 |  |  | 11.8947 | 12.6748 | 12.6893 | [6 empty] | 12.5968 |  |  | 11.3091 |  |  | 9.0752 | 10.232 | 12.1096 | 7.5934 | 9.2321 | 12.5711 | 7.7626 | 9.5163 | 12.5094 | 9.2323 | 10.4148 | 7.7893 | 10.4249 | 8.3751 | 10.1808 | 7.8179 | 9.5509 | 13.3347 | 10.5025 | 10.1464 | 11.6411 | 8.1283 | 9.6817 | 12.8909 | 7.9605 | 10.3613 | 9.6691 | 9.8869 | 8.4901 | 10.3214 | 0.0001804 | 20.9527 | 0.033137 | 0.050787 | -38.0401 | 3.1217 | -0.73 | 0.39 | 0.27943 | -0.3131 | 0.29543 | -0.60189 | 0.4226 | 0.45809 | 0.87773 | 0.41039 | 0.40485 | 0.4246 | 0.3511 | 0.56058 | 0.42882 | 0.41567
42810.4336 | -555 | 18.6087 | 18.6723 | 18.6453 | 18.6509 | 18.0196 | 16.6809 | 14.7534 | 16.7558 | 17.2397 | 17.3381 | 17.358 | 16.9174 | 15.9609 | 14.5772 | 15.0838 | 15.0749 | 15.6197 | 13.4707 | 13.5847 | 14.1638 |  |  |  | 16.6677 | 16.0021 | 15.1283 | 10.2893 | 9.7066 | 10.2582 | 17.3195 | 16.448 | 15.2499 | 16.9637 | 16.2457 | 15.265 | 10.8756 | 12.0508 |  | 12.3335 | 10.6319 | 10.5415 | 8.7347 |  | 6.4507 | 6.4398 | 5.9172 | 6.0455 | 6.0821 | 6.3017 | 6.9611 | 5.0164 | 6.458 | 4.9818 | 6.6917 | 8.1884 | 42.5783 | 47.3136 | 43.4846 | 15.4487 |  |  | -0.081265 | -0.093881 | 0.22198 | -0.30096 | 0.007392 | -0.44598 | 0.56305 | -0.12239 | -0.29578 | 0.41062 | -0.28127 | 8.8816 | 8.883 | 2.0086 | 15.9028 | 16.8065 | 17.3337 | 17.6622 | 17.6268 | 16.6196 | 14.9714 | 16.9021 | 17.2362 | 17.5238 | 17.5649 | 17.3015 | 16.5191 | 14.7591 | 6.6428 | 8.5291 | 5.8005 | 5.9031 | 6.1251 | 6.7082 | 7.6615 | 15.964 | 15.615 | 15.4687 | 14.4124 | 14.2966 | 14.2441 |  |  |  | 10.7527 | 9.3364 | 8.9681 | 9.0531 | 0.11594 | 0.060813 | 12.871 |  |  | 10.6732 |  |  | 16.9668 | 16.1665 | 15.1495 | 16.4556 | 15.7323 | 14.8511 | 10.7651 | 10.6962 | 11.405 | 11.3078 | 9.2519 |  | 10.7605 | 8.7468 | 10.1202 | 9.2521 | 11.1847 | 11.8044 |  | 12.3962 |  |  | 11.8782 | 12.6566 | 12.6852 | [6 empty] | 12.5875 |  |  | 11.3063 |  |  | 9.0683 | 10.2293 | 12.105 | 7.6031 | 9.2104 | 12.5594 | 7.765 | 9.5207 | 12.506 | 9.2397 | 10.4234 | 7.7662 | 10.4154 | 8.3804 | 10.1878 | 7.809 | 9.5436 | 13.3367 | 10.5007 | 10.1389 | 11.6361 | 8.1349 | 9.6879 | 12.8898 | 7.9555 | 10.3668 | 9.6745 | 9.8904 | 8.4982 | 10.3282 | -0.062222 | 20.9537 | 0.033194 | 0.0507 | -38.0872 | 3.1217 | -0.89 | 0.35 | -0.33445 | -0.35704 | 0.54902 | -0.63926 | 0.10016 | -0.778 | 0.87416 | 0.4103 | 0.40323 | 0.42428 | 0.35507 | 0.55934 | 0.42846 | 0.41556
42810.4336 | -554 | 18.6121 | 18.6819 | 18.656 | 18.6505 | 18.018 | 16.683 | 14.757 | 16.7623 | 17.2371 | 17.3393 | 17.3593 | 16.9099 | 15.966 | 14.5735 | 15.0877 | 15.0796 | 15.6213 | 13.4709 | 13.5821 | 14.1623 |  |  |  | 16.6701 | 16.0036 | 15.1312 | 10.3028 | 9.7151 | 10.271 | 17.3172 | 16.4467 | 15.2548 | 16.9529 | 16.2506 | 15.2615 | 10.8637 | 12.0138 |  | 12.3357 | 10.6255 | 10.5317 | 8.7552 |  | 6.4565 | 6.4371 | 5.9257 | 6.042 | 6.0757 | 6.277 | 6.9875 | 4.9217 | 6.4641 | 5.0158 | 6.6949 | 8.1901 | 42.5966 | 47.3075 | 43.4975 | 15.4439 |  |  | 0.084331 | -0.18391 | -0.011948 | -0.06637 | 0.11516 | -0.40524 | 0.45528 | -0.082304 | -0.90215 | -0.2148 | -0.44361 | 8.8846 | 8.8855 | 2.0085 | 15.897 | 16.7992 | 17.3393 | 17.6659 | 17.6253 | 16.6129 | 14.9705 | 16.9079 | 17.2384 | 17.5225 | 17.5562 | 17.3023 | 16.5181 | 14.7472 | 6.6238 | 8.5094 | 5.7477 | 5.877 | 6.1171 | 6.7103 | 7.6693 | 15.959 | 15.6063 | 15.4752 | 14.416 | 14.2944 | 14.2475 |  |  |  | 10.7521 | 9.3274 | 8.9712 | 9.0519 | 0.051104 | 0.004918 | 12.8757 |  |  | 10.6768 |  |  | 16.9725 | 16.1702 | 15.1462 | 16.4496 | 15.7403 | 14.8566 | 10.7728 | 10.6945 | 11.407 | 11.3031 | 9.2311 |  | 10.7545 | 8.7301 | 10.1173 | 9.2373 | 11.1808 | 11.758 |  | 12.4032 |  |  | 11.866 | 12.6552 | 12.6951 | [6 empty] | 12.5823 |  |  | 11.3051 |  |  | 9.066 | 10.2231 | 12.0913 | 7.5988 | 9.1635 | 12.5379 | 7.7722 | 9.5144 | 12.4986 | 9.2394 | 10.424 | 7.752 | 10.3934 | 8.3767 | 10.1898 | 7.8034 | 9.5332 | 13.3264 | 10.4873 | 10.1396 | 11.6288 | 8.142 | 9.6858 | 12.8792 | 7.9456 | 10.3736 | 9.6786 | 9.9065 | 8.5081 | 10.3283 | -0.055866 | 20.9532 | 0.033246 | 0.050881 | -38.1585 | 3.1216 | -0.84 | 0.31 | 0.3407 | -0.49971 | -0.12737 | -0.3002 | 0.39532 | -0.74158 | 0.78604 | 0.41068 | 0.4036 | 0.42456 | 0.35742 | 0.56611 | 0.4275 | 0.41558
42810.4336 | -553 | 18.6162 | 18.6817 | 18.658 | 18.6621 | 18.0206 | 16.6873 | 14.7671 | 16.7646 | 17.2456 | 17.3515 | 17.3652 | 16.9124 | 15.969 | 14.5812 | 15.0869 | 15.0856 | 15.6218 | 13.4725 | 13.5824 | 14.1624 |  |  |  | 16.675 | 16.0141 | 15.1353 | 10.314 | 9.718 | 10.2897 | 17.3208 | 16.4497 | 15.2489 | 16.953 | 16.25 | 15.261 | 10.8718 | 11.975 |  | 12.3244 | 10.6173 | 10.534 | 8.7598 |  | 6.4548 | 6.4403 | 5.9261 | 6.0441 | 6.0717 | 6.2663 | 6.9976 | 4.8391 | 6.4675 | 5.0299 | 6.6959 | 8.1936 | 42.6152 | 47.3046 | 43.5021 | 15.4295 |  |  | -0.072721 | -0.19836 | 0.00842 | -0.057826 | 0.11253 | -0.24294 | 0.51836 | -0.11713 | 0.57798 | -0.18228 | -0.37287 | 8.8879 | 8.8892 | 2.0087 | 15.8948 | 16.7953 | 17.3367 | 17.6595 | 17.6216 | 16.6157 | 14.9739 | 16.9109 | 17.2316 | 17.5115 | 17.5554 | 17.3029 | 16.52 | 14.7415 | 6.6086 | 8.5003 | 5.6643 | 5.846 | 6.0695 | 6.705 | 7.66 | 15.9621 | 15.6018 | 15.473 | 14.4155 | 14.3004 | 14.24 |  |  |  | 10.7532 | 9.3273 | 8.9725 | 9.0755 | 0.10196 | 0.073235 | 12.8692 |  |  | 10.689 |  |  | 16.9754 | 16.1726 | 15.1588 | 16.455 | 15.7369 | 14.8575 | 10.7691 | 10.6937 | 11.4068 | 11.2995 | 9.2004 |  | 10.7528 | 8.6644 | 10.1171 | 9.2342 | 11.174 | 11.7746 |  | 12.3959 |  |  | 11.8491 | 12.6617 | 12.7009 | [6 empty] | 12.593 |  |  | 11.3015 |  |  | 9.066 | 10.2259 | 12.0906 | 7.5943 | 9.1407 | 12.5277 | 7.7764 | 9.5104 | 12.5015 | 9.2354 | 10.4306 | 7.753 | 10.3818 | 8.3856 | 10.1905 | 7.796 | 9.526 | 13.312 | 10.4802 | 10.1468 | 11.6163 | 8.1349 | 9.6893 | 12.8837 | 7.9392 | 10.3663 | 9.6815 | 9.9025 | 8.5106 | 10.3282 | -0.083023 | 20.9547 | 0.033303 | 0.050722 | -38.0939 | 3.1216 | -0.61 | 0.31 | -0.31639 | -0.51899 | 0.10693 | -0.28021 | 0.39078 | -0.57417 | 0.83871 | 0.41147 | 0.40542 | 0.42443 | 0.35851 | 0.5743 | 0.42763 | 0.41496
42810.4336 | -552 | 18.6139 | 18.68 | 18.6547 | 18.6637 | 18.0205 | 16.6853 | 14.7575 | 16.7629 | 17.2523 | 17.3539 | 17.3621 | 16.916 | 15.9646 | 14.5743 | 15.0797 | 15.0796 | 15.6197 | 13.467 | 13.5831 | 14.1596 |  |  |  | 16.6774 | 16.0136 | 15.132 | 10.3185 | 9.7115 | 10.3165 | 17.3147 | 16.4503 | 15.24 | 16.9595 | 16.2499 | 15.2648 | 10.8777 | 11.9538 |  | 12.3283 | 10.6074 | 10.5446 | 8.775 |  | 6.444 | 6.4276 | 5.9123 | 6.0356 | 6.0633 | 6.2406 | 6.947 | 4.779 | 6.4657 | 5.0346 | 6.6934 | 8.1917 | 42.6305 | 47.2968 | 43.5013 | 15.4178 |  |  | -0.092433 | 0.009287 | 0.11422 | 0.009858 | 0.11647 | 0.089564 | 0.54728 | -0.06982 | -1.2131 | -0.87902 | -0.28047 | 8.8927 | 8.8942 | 2.0084 | 15.8978 | 16.794 | 17.3255 | 17.6493 | 17.6207 | 16.6065 | 14.9676 | 16.904 | 17.2318 | 17.5138 | 17.5551 | 17.2944 | 16.5167 | 14.7453 | 6.5803 | 8.5072 | 5.6377 | 5.7806 | 6.0353 | 6.708 | 7.658 | 15.9619 | 15.6074 | 15.4691 | 14.414 | 14.296 | 14.2419 |  |  |  | 10.7516 | 9.3211 | 8.9764 | 9.0712 | 0.037732 | 0.1551 | 12.8636 |  |  | 10.693 |  |  | 16.9734 | 16.1673 | 15.1612 | 16.4587 | 15.7412 | 14.8533 | 10.7816 | 10.6991 | 11.4017 | 11.2986 | 9.1767 |  | 10.7505 | 8.5609 | 10.1171 | 9.2303 | 11.1773 | 11.8165 |  | 12.3886 |  |  | 11.8488 | 12.6645 | 12.7024 | [6 empty] | 12.609 |  |  | 11.3006 |  |  | 9.0679 | 10.2211 | 12.0911 | 7.5901 | 9.1334 | 12.5205 | 7.784 | 9.5098 | 12.5087 | 9.2392 | 10.443 | 7.7663 | 10.3903 | 8.3975 | 10.2014 | 7.786 | 9.5214 | 13.3086 | 10.4838 | 10.15 | 11.6079 | 8.1241 | 9.6925 | 12.8909 | 7.9412 | 10.3687 | 9.685 | 9.9073 | 8.5084 | 10.3342 | -0.21765 | 20.9533 | 0.032816 | 0.050389 | -38.2532 | 3.1216 | -0.68 | 0.35 | -0.35672 | 0.11229 | 0.39381 | 0.11569 | 0.39754 | 0.34861 | 0.86174 | 0.41205 | 0.40829 | 0.42464 | 0.36199 | 0.57703 | 0.42741 | 0.41502
42810.4337 | -551 | 18.6174 | 18.6846 | 18.6592 | 18.6626 | 18.0257 | 16.6865 | 14.7617 | 16.773 | 17.257 | 17.3509 | 17.36 | 16.9206 | 15.9689 | 14.5802 | 15.0644 | 15.063 | 15.6116 | 13.4582 | 13.5769 | 14.149 |  |  |  | 16.6573 | 15.9978 | 15.1232 | 10.3153 | 9.6968 | 10.3255 | 17.3145 | 16.4504 | 15.2501 | 16.962 | 16.2512 | 15.2617 | 10.8766 | 11.9227 |  | 12.339 | 10.5885 | 10.5444 | 8.7896 |  | 6.4403 | 6.4274 | 5.9165 | 6.0194 | 6.0606 | 6.2276 | 6.9314 | 4.7377 | 6.4694 | 4.9945 | 6.6901 | 8.1861 | 42.6349 | 47.2749 | 43.4975 | 15.4088 |  |  | 0.008763 | -0.082709 | 0.20161 | -0.11105 | 0.19861 | -0.0688 | 0.53348 | -0.23476 | -0.33548 | -0.68055 | -0.32498 | 8.8887 | 8.8902 | 2.0085 | 15.8938 | 16.7956 | 17.3284 | 17.6506 | 17.618 | 16.6097 | 14.9695 | 16.9054 | 17.2234 | 17.5149 | 17.5528 | 17.2985 | 16.5151 | 14.7493 | 6.5345 | 8.5032 | 5.6434 | 5.7422 | 6.0098 | 6.7035 | 7.6567 | 15.9607 | 15.604 | 15.4722 | 14.4141 | 14.2985 | 14.2457 |  |  |  | 10.758 | 9.3218 | 8.9736 | 9.0702 | 0.075821 | 0.21326 | 12.8707 |  |  | 10.6908 |  |  | 16.9717 | 16.1685 | 15.1624 | 16.4553 | 15.7398 | 14.8582 | 10.7948 | 10.7022 | 11.401 | 11.298 | 9.1876 |  | 10.7502 | 8.4487 | 10.1201 | 9.2343 | 11.1831 | 11.8524 |  | 12.3935 |  |  | 11.8654 | 12.665 | 12.7029 | [6 empty] | 12.6152 |  |  | 11.2963 |  |  | 9.0688 | 10.2224 | 12.0902 | 7.5835 | 9.1212 | 12.5146 | 7.7927 | 9.5118 | 12.5132 | 9.2554 | 10.4525 | 7.7764 | 10.3943 | 8.4077 | 10.2083 | 7.7754 | 9.5292 | 13.3089 | 10.4806 | 10.1537 | 11.6101 | 8.1226 | 9.6964 | 12.895 | 7.9494 | 10.381 | 9.6839 | 9.9255 | 8.5132 | 10.3386 | 0.061042 | 20.9539 | 0.032816 | 0.049217 | -38.2072 | 3.1216 | -0.56 | 0.23 | 0.10984 | -0.33512 | 0.52321 | -0.38832 | 0.51912 | -0.30553 | 0.85079 | 0.41174 | 0.4115 | 0.42472 | 0.36656 | 0.57625 | 0.42697 | 0.41526
42810.4337 | -550 | 18.6067 | 18.6719 | 18.6527 | 18.6587 | 18.0133 | 16.6853 | 14.7593 | 16.7654 | 17.2444 | 17.3427 | 17.3584 | 16.918 | 15.9651 | 14.5685 | 15.0709 | 15.0696 | 15.6102 | 13.4605 | 13.5846 | 14.1534 |  |  |  | 16.6616 | 16.005 | 15.1276 | 10.3233 | 9.6984 | 10.3262 | 17.3123 | 16.4483 | 15.2507 | 16.9592 | 16.2507 | 15.256 | 10.8754 | 11.8727 |  | 12.3359 | 10.5821 | 10.5497 | 8.7934 |  | 6.4307 | 6.4238 | 5.9124 | 6.0175 | 6.0564 | 6.2104 | 6.9147 | 4.7194 | 6.47 | 4.9265 | 6.6902 | 8.1857 | 42.6455 | 47.2685 | 43.5097 | 15.3962 |  |  | -0.078633 | 0.017831 | 0.18782 | 0.33579 | 0.4562 | -0.21665 | 0.62285 | -0.077704 | -0.56569 | -0.0020608 | -0.24789 | 8.8799 | 8.8812 | 2.0084 | 15.8929 | 16.7957 | 17.3345 | 17.6632 | 17.6238 | 16.6185 | 14.9722 | 16.9079 | 17.2295 | 17.5212 | 17.5616 | 17.3075 | 16.5179 | 14.7538 | 6.4853 | 8.5084 | 5.6261 | 5.7578 | 5.9773 | 6.7045 | 7.6698 | 15.9519 | 15.596 | 15.4674 | 14.4057 | 14.2917 | 14.2363 |  |  |  | 10.7558 | 9.3199 | 8.9724 | 9.0638 | -0.020211 | 0.22944 | 12.8646 |  |  | 10.6912 |  |  | 16.9739 | 16.1792 | 15.1541 | 16.4584 | 15.7422 | 14.858 | 10.7817 | 10.6979 | 11.401 | 11.2974 | 9.1683 |  | 10.7481 | 8.3384 | 10.1154 | 9.2392 | 11.1769 | 11.881 |  | 12.3944 |  |  | 11.8718 | 12.6672 | 12.7033 | [6 empty] | 12.6178 |  |  | 11.284 |  |  | 9.0557 | 10.2195 | 12.0868 | 7.5685 | 9.1022 | 12.509 | 7.7905 | 9.4992 | 12.5034 | 9.2597 | 10.454 | 7.7688 | 10.3861 | 8.4101 | 10.2091 | 7.7737 | 9.5427 | 13.3004 | 10.4819 | 10.1534 | 11.605 | 8.1319 | 9.7014 | 12.8955 | 7.9557 | 10.3835 | 9.6862 | 9.93 | 8.5148 | 10.3445 | 0.043901 | 20.9544 | 0.033126 | 0.048385 | -38.0868 | 3.1216 | -0.5 | 0.26 | -0.32902 | 0.1556 | 0.50499 | 0.67522 | 0.78674 | -0.54216 | 0.91926 | 0.41221 | 0.41442 | 0.42438 | 0.37215 | 0.57969 | 0.42682 | 0.41537
42810.4337 | -549 | 18.6088 | 18.6719 | 18.6521 | 18.6572 | 18.0253 | 16.6914 | 14.7639 | 16.7713 | 17.2565 | 17.3472 | 17.36 | 16.9135 | 15.9786 | 14.5782 | 15.0641 | 15.0691 | 15.6087 | 13.4531 | 13.5746 | 14.1462 |  |  |  | 16.658 | 15.9994 | 15.1249 | 10.324 | 9.7011 | 10.3053 | 17.3097 | 16.4413 | 15.2523 | 16.9492 | 16.2472 | 15.2561 | 10.8706 | 11.8437 |  | 12.331 | 10.5744 | 10.5468 | 8.7859 |  | 6.4202 | 6.4175 | 5.9102 | 6.0057 | 6.0459 | 6.1946 | 6.9003 | 4.6786 | 6.4712 | 4.8056 | 6.6851 | 8.1844 | 42.6422 | 47.2744 | 43.5156 | 15.389 |  |  | 0.080387 | 0.21233 | 0.2325 | -0.027598 | -0.12206 | -0.37699 | 0.43688 | -0.18284 | 0.14207 | -0.26536 | -0.43248 | 8.8875 | 8.8888 | 2.0087 | 15.8838 | 16.7912 | 17.326 | 17.6587 | 17.6174 | 16.6105 | 14.9652 | 16.9006 | 17.23 | 17.5143 | 17.5581 | 17.303 | 16.5186 | 14.7507 | 6.4413 | 8.5083 | 5.5935 | 5.7712 | 5.9365 | 6.7029 | 7.6718 | 15.9458 | 15.5953 | 15.4647 | 14.4038 | 14.2785 | 14.2296 |  |  |  | 10.7506 | 9.3157 | 8.9654 | 9.0602 | -0.055058 | 0.20516 | 12.8615 |  |  | 10.6838 |  |  | 16.975 | 16.1742 | 15.1469 | 16.4537 | 15.743 | 14.8512 | 10.7751 | 10.694 | 11.3963 | 11.2952 | 9.1788 |  | 10.7453 | 8.2524 | 10.1092 | 9.2479 | 11.1687 | 11.9322 |  | 12.3901 |  |  | 11.8874 | 12.6791 | 12.7076 | [6 empty] | 12.6232 |  |  | 11.272 |  |  | 9.0511 | 10.2115 | 12.0788 | 7.5549 | 9.0962 | 12.4887 | 7.7924 | 9.4956 | 12.4978 | 9.258 | 10.4499 | 7.766 | 10.3878 | 8.4093 | 10.2029 | 7.7846 | 9.5392 | 13.2902 | 10.4704 | 10.1464 | 11.6026 | 8.1445 | 9.7085 | 12.8891 | 7.9592 | 10.3952 | 9.6938 | 9.9354 | 8.5174 | 10.3464 | 0.076257 | 20.9546 | 0.033814 | 0.048023 | -38.0209 | 3.1216 | -0.52 | 0.4 | 0.33266 | 0.53693 | 0.56185 | -0.19357 | -0.40693 | -0.71516 | 0.76988 | 0.41182 | 0.4166 | 0.42387 | 0.37685 | 0.58354 | 0.42687 | 0.4153
42810.4337 | -548 | 18.6001 | 18.6647 | 18.6358 | 18.6603 | 18.0101 | 16.6752 | 14.7567 | 16.7557 | 17.2416 | 17.33 | 17.3475 | 16.9138 | 15.9601 | 14.5635 | 15.0844 | 15.0836 | 15.6192 | 13.4719 | 13.59 | 14.1667 |  |  |  | 16.6754 | 16.0171 | 15.135 | 10.3344 | 9.7282 | 10.3023 | 17.3093 | 16.4428 | 15.2504 | 16.9601 | 16.2465 | 15.2649 | 10.8713 | 11.8486 |  | 12.3377 | 10.5814 | 10.5579 | 8.7738 |  | 6.4121 | 6.4078 | 5.9059 | 6.0073 | 6.0482 | 6.196 | 6.8962 | 4.6872 | 6.4682 | 4.7091 | 6.6898 | 8.1836 | 42.6559 | 47.2935 | 43.5206 | 15.3783 |  |  | -0.042493 | -0.059709 | 0.10239 | 0.08477 | 0.039592 | -0.12466 | 0.55254 | -0.1007 | -2.2484 | -0.51125 | -0.35916 | 8.8892 | 8.8906 | 2.0085 | 15.8751 | 16.7895 | 17.3341 | 17.6529 | 17.6211 | 16.6062 | 14.9615 | 16.8956 | 17.2286 | 17.5123 | 17.5576 | 17.2988 | 16.5174 | 14.7486 | 6.3731 | 8.496 | 5.58 | 5.7493 | 5.9019 | 6.7066 | 7.6723 | 15.9514 | 15.6012 | 15.4618 | 14.4113 | 14.2918 | 14.2362 |  |  |  | 10.763 | 9.3236 | 8.9762 | 9.0735 | 0.093245 | 0.094878 | 12.8674 |  |  | 10.6795 |  |  | 16.9702 | 16.1682 | 15.1513 | 16.4498 | 15.7388 | 14.8502 | 10.7728 | 10.6944 | 11.4095 | 11.2939 | 9.1775 |  | 10.7547 | 8.1942 | 10.1163 | 9.2509 | 11.1709 | 11.9909 |  | 12.3948 |  |  | 11.895 | 12.6832 | 12.7255 | [6 empty] | 12.6429 |  |  | 11.2765 |  |  | 9.0418 | 10.2035 | 12.0787 | 7.5307 | 9.0913 | 12.4882 | 7.7898 | 9.4823 | 12.4892 | 9.2502 | 10.4418 | 7.7653 | 10.3878 | 8.405 | 10.1934 | 7.7808 | 9.538 | 13.2816 | 10.4576 | 10.1431 | 11.5779 | 8.1391 | 9.7028 | 12.8838 | 7.9687 | 10.3925 | 9.6854 | 9.934 | 8.5091 | 10.3441 | 0.073754 | 20.9545 | 0.034027 | 0.047588 | -37.9711 | 3.1216 | -0.58 | 0.28 | -0.24186 | -0.28472 | 0.37284 | 0.33925 | 0.23176 | -0.41124 | 0.8658 | 0.41217 | 0.41845 | 0.42386 | 0.38485 | 0.5851 | 0.42723 | 0.41534
42810.4337 | -547 | 18.6059 | 18.6789 | 18.654 | 18.6637 | 18.0187 | 16.6812 | 14.7602 | 16.7617 | 17.2468 | 17.3406 | 17.358 | 16.9142 | 15.9674 | 14.5673 | 15.0726 | 15.0727 | 15.6143 | 13.4678 | 13.5768 | 14.1606 |  |  |  | 16.667 | 16.003 | 15.1248 | 10.3326 | 9.7254 | 10.2543 | 17.2976 | 16.4412 | 15.2462 | 16.9581 | 16.2321 | 15.2486 | 10.8644 | 11.8334 |  | 12.3224 | 10.5811 | 10.5436 | 8.7611 |  | 6.4008 | 6.4002 | 5.9022 | 6.0047 | 6.0389 | 6.1835 | 6.8812 | 4.7243 | 6.4672 | 4.6392 | 6.6869 | 8.1784 | 42.6608 | 47.3021 | 43.5217 | 15.3686 |  |  | 0.067903 | -0.12148 | 0.17664 | 0.10974 | 0.070476 | -0.22388 | 0.40008 | -0.17233 | -0.35999 | -0.20305 | -0.2459 | 8.8833 | 8.8843 | 2.0085 | 15.8784 | 16.7828 | 17.3346 | 17.6499 | 17.6172 | 16.6047 | 14.969 | 16.8999 | 17.2284 | 17.5118 | 17.5546 | 17.2969 | 16.5146 | 14.7523 | 6.3038 | 8.4701 | 5.6356 | 5.7359 | 5.8514 | 6.7018 | 7.675 | 15.9472 | 15.6036 | 15.4584 | 14.4012 | 14.2897 | 14.2316 |  |  |  | 10.7563 | 9.3177 | 8.973 | 9.0857 | 0.18867 | 0.032207 | 12.853 |  |  | 10.6757 |  |  | 16.9671 | 16.1609 | 15.1503 | 16.447 | 15.7289 | 14.8501 | 10.7644 | 10.6928 | 11.4074 | 11.3001 | 9.1647 |  | 10.7447 | 8.0958 | 10.1103 | 9.2566 | 11.1701 | 12.0145 |  | 12.39 |  |  | 11.8645 | 12.6712 | 12.7066 | [6 empty] | 12.6271 |  |  | 11.2649 |  |  | 9.0377 | 10.2136 | 12.0917 | 7.5112 | 9.0962 | 12.5006 | 7.8016 | 9.4955 | 12.4865 | 9.2593 | 10.445 | 7.7597 | 10.4126 | 8.4155 | 10.2066 | 7.7707 | 9.5394 | 13.2765 | 10.4586 | 10.1258 | 11.5844 | 8.1357 | 9.6951 | 12.8778 | 7.9717 | 10.4037 | 9.6871 | 9.9213 | 8.517 | 10.3501 | -0.073008 | 20.9553 | 0.033935 | 0.047234 | -38.1307 | 3.1216 | -0.69 | 0.4 | 0.30571 | -0.40611 | 0.48972 | 0.38599 | 0.30921 | -0.55111 | 0.73672 | 0.4122 | 0.42099 | 0.42367 | 0.39199 | 0.57924 | 0.42735 | 0.41477
42810.4337 | -546 | 18.6035 | 18.676 | 18.6529 | 18.6588 | 18.0204 | 16.6803 | 14.754 | 16.7574 | 17.24 | 17.3396 | 17.3544 | 16.9129 | 15.9641 | 14.5705 | 15.0682 | 15.0691 | 15.6133 | 13.4533 | 13.5806 | 14.1493 |  |  |  | 16.6603 | 16.0038 | 15.1184 | 10.3278 | 9.7325 | 10.2443 | 17.3086 | 16.4413 | 15.2558 | 16.9639 | 16.2384 | 15.2615 | 10.8734 | 11.8089 |  | 12.33 | 10.5896 | 10.5405 | 8.7547 |  | 6.3997 | 6.3921 | 5.9051 | 6.0061 | 6.0498 | 6.1817 | 6.8531 | 4.792 | 6.4666 | 4.6338 | 6.6932 | 8.185 | 42.6878 | 47.3048 | 43.5282 | 15.3559 |  |  | 0.016647 | 0.051343 | 0.13787 | -0.078198 | 0.1605 | -0.52615 | 0.39746 | -0.41415 | -0.36895 | -1.828 | -0.22762 | 8.8816 | 8.883 | 2.0086 | 15.8781 | 16.7871 | 17.3331 | 17.6575 | 17.6175 | 16.6121 | 14.9734 | 16.9065 | 17.2272 | 17.5215 | 17.5612 | 17.2981 | 16.5161 | 14.7509 | 6.2539 | 8.4561 | 5.6065 | 5.7795 | 5.839 | 6.702 | 7.6788 | 15.9452 | 15.5978 | 15.4639 | 14.4006 | 14.2852 | 14.2306 |  |  |  | 10.7564 | 9.3171 | 8.9806 | 9.1086 | 0.0057216 | 0.075117 | 12.8482 |  |  | 10.6733 |  |  | 16.9607 | 16.1643 | 15.142 | 16.4442 | 15.7268 | 14.8492 | 10.7532 | 10.693 | 11.4083 | 11.312 | 9.163 |  | 10.7547 | 8.0222 | 10.1087 | 9.2685 | 11.1711 | 12.0211 |  | 12.3894 |  |  | 11.8734 | 12.6817 | 12.7221 | [6 empty] | 12.6422 |  |  | 11.2835 |  |  | 9.0294 | 10.206 | 12.1077 | 7.5072 | 9.1092 | 12.5034 | 7.787 | 9.4843 | 12.4819 | 9.261 | 10.4413 | 7.7577 | 10.4095 | 8.4062 | 10.2124 | 7.7725 | 9.5505 | 13.2745 | 10.4558 | 10.1272 | 11.5918 | 8.1368 | 9.6962 | 12.8845 | 7.988 | 10.4109 | 9.6958 | 9.9316 | 8.519 | 10.3539 | -0.04874 | 20.9542 | 0.033963 | 0.047907 | -38.0861 | 3.1216 | -0.67 | 0.39 | 0.15137 | 0.26402 | 0.43264 | -0.32583 | 0.46662 | -0.84486 | 0.7343 | 0.41258 | 0.42298 | 0.42338 | 0.39757 | 0.58291 | 0.42783 | 0.41414
42810.4337 | -545 | 18.5906 | 18.669 | 18.6495 | 18.654 | 18.0137 | 16.6767 | 14.7522 | 16.7545 | 17.2366 | 17.3374 | 17.3509 | 16.9094 | 15.9587 | 14.5609 | 15.0662 | 15.067 | 15.6087 | 13.4555 | 13.5788 | 14.1511 |  |  |  | 16.6558 | 15.9948 | 15.1258 | 10.3205 | 9.7491 | 10.2438 | 17.2998 | 16.4406 | 15.2526 | 16.9554 | 16.2378 | 15.2623 | 10.8712 | 11.7936 |  | 12.3296 | 10.5946 | 10.5349 | 8.7498 |  | 6.4005 | 6.3893 | 5.8988 | 6.0051 | 6.0347 | 6.1735 | 6.8321 | 4.8524 | 6.463 | 4.6194 | 6.6887 | 8.1776 | 42.7032 | 47.3025 | 43.5233 | 15.3456 |  |  | -0.11018 | 0.029003 | 0.057048 | -0.56972 | -0.001152 | -0.29879 | 0.26209 | -0.38129 | -0.13873 | -0.56244 | -0.45334 | 8.8811 | 8.882 | 2.0083 | 15.8889 | 16.7968 | 17.3406 | 17.6622 | 17.6347 | 16.6182 | 14.9729 | 16.9057 | 17.235 | 17.5206 | 17.5651 | 17.3122 | 16.5225 | 14.7673 | 6.2473 | 8.4147 | 5.5986 | 5.8101 | 5.8082 | 6.7003 | 7.6816 | 15.9416 | 15.5956 | 15.4604 | 14.4052 | 14.2803 | 14.2351 |  |  |  | 10.7568 | 9.3168 | 8.9856 | 9.1388 | 0.019093 | 0.11219 | 12.8399 |  |  | 10.6757 |  |  | 16.9646 | 16.161 | 15.1428 | 16.447 | 15.7271 | 14.8466 | 10.7398 | 10.6905 | 11.4131 | 11.3167 | 9.1511 |  | 10.7499 | 7.9601 | 10.1114 | 9.2765 | 11.1735 | 12.0319 |  | 12.3951 |  |  | 11.8796 | 12.6895 | 12.7187 | [6 empty] | 12.6416 |  |  | 11.3032 |  |  | 9.0292 | 10.2152 | 12.0969 | 7.5213 | 9.1283 | 12.5155 | 7.7827 | 9.4797 | 12.4681 | 9.267 | 10.4361 | 7.7801 | 10.4197 | 8.397 | 10.2045 | 7.7916 | 9.5646 | 13.2739 | 10.4647 | 10.1295 | 11.6075 | 8.1645 | 9.7148 | 12.899 | 8.0112 | 10.4175 | 9.7173 | 9.9443 | 8.5429 | 10.3638 | -0.17066 | 20.9551 | 0.033929 | 0.048066 | -38.0692 | 3.1215 | -0.15 | 0.31 | -0.38941 | 0.19843 | 0.2783 | -0.87946 | -0.039532 | -0.63666 | 0.59628 | 0.41275 | 0.42479 | 0.42323 | 0.3981 | 0.58412 | 0.42789 | 0.41332
42810.4337 | -544 | 18.5906 | 18.6685 | 18.6524 | 18.6549 | 18.0154 | 16.6807 | 14.7582 | 16.7542 | 17.2395 | 17.34 | 17.359 | 16.9102 | 15.9622 | 14.5683 | 15.0567 | 15.0667 | 15.6124 | 13.4622 | 13.5798 | 14.1552 |  |  |  | 16.6587 | 16.0037 | 15.1238 | 10.3322 | 9.7634 | 10.255 | 17.2943 | 16.4289 | 15.2367 | 16.9475 | 16.2332 | 15.2571 | 10.8678 | 11.803 |  | 12.3214 | 10.5955 | 10.5166 | 8.73 |  | 6.3965 | 6.3901 | 5.8988 | 6.0114 | 6.0329 | 6.1638 | 6.8308 | 4.883 | 6.4743 | 4.5986 | 6.6839 | 8.1785 | 42.7239 | 47.3116 | 43.507 | 15.3394 |  |  | 0.031103 | -0.042625 | -0.021148 | -0.41661 | -0.21931 | -0.31128 | 0.49011 | -0.40429 | -0.48804 | -0.3455 | -0.23795 | 8.8796 | 8.8809 | 2.0087 | 15.8766 | 16.7849 | 17.3308 | 17.6552 | 17.6274 | 16.615 | 14.9668 | 16.9002 | 17.2343 | 17.522 | 17.5704 | 17.3094 | 16.5224 | 14.7582 | 6.2458 | 8.4057 | 5.5793 | 5.8853 | 5.7733 | 6.6872 | 7.6858 | 15.9379 | 15.5831 | 15.4587 | 14.394 | 14.2795 | 14.2278 |  |  |  | 10.7519 | 9.3182 | 8.9907 | 9.1534 | 0.031857 | 0.086785 | 12.8414 |  |  | 10.682 |  |  | 16.9778 | 16.1609 | 15.1461 | 16.452 | 15.7355 | 14.849 | 10.7412 | 10.6977 | 11.4162 | 11.3292 | 9.1434 |  | 10.7355 | 7.9579 | 10.1042 | 9.2601 | 11.1616 | 12.0188 |  | 12.3866 |  |  | 11.8932 | 12.6924 | 12.7208 | [6 empty] | 12.6332 |  |  | 11.3146 |  |  | 9.0218 | 10.222 | 12.106 | 7.5099 | 9.1473 | 12.5328 | 7.7706 | 9.4916 | 12.4748 | 9.2823 | 10.4532 | 7.8036 | 10.4377 | 8.4049 | 10.2161 | 7.7876 | 9.563 | 13.2623 | 10.4393 | 10.1187 | 11.6025 | 8.1595 | 9.7087 | 12.8853 | 8.0164 | 10.4081 | 9.7051 | 9.9243 | 8.5382 | 10.3463 | 0.084539 | 20.9541 | 0.033958 | 0.048334 | -38.0255 | 3.1215 | -0.11 | 0.4 | 0.20691 | -0.24056 | -0.16944 | -0.75206 | -0.54544 | -0.64981 | 0.81538 | 0.41249 | 0.42461 | 0.4233 | 0.39674 | 0.58675 | 0.42833 | 0.41275
42810.4337 | -543 | 18.5828 | 18.6692 | 18.6437 | 18.6523 | 18.0163 | 16.6743 | 14.7538 | 16.7498 | 17.2419 | 17.3399 | 17.3599 | 16.9107 | 15.9565 | 14.5634 | 15.0706 | 15.061 | 15.6091 | 13.4624 | 13.5757 | 14.155 |  |  |  | 16.6594 | 16 | 15.1241 | 10.3349 | 9.7712 | 10.2691 | 17.2968 | 16.4284 | 15.2357 | 16.9497 | 16.2371 | 15.2496 | 10.87 | 11.8186 |  | 12.3217 | 10.6014 | 10.5081 | 8.7019 |  | 6.4 | 6.399 | 5.898 | 6.015 | 6.0352 | 6.1706 | 6.8172 | 4.8711 | 6.4846 | 4.621 | 6.6905 | 8.1706 | 42.7527 | 47.3238 | 43.4886 | 15.3288 |  |  | 0.068559 | -0.045253 | -0.13746 | -0.12945 | 0.05602 | -0.14371 | 0.53676 | -0.11187 | 0.38552 | -0.57775 | -0.34922 | 8.8812 | 8.8825 | 2.0084 | 15.8751 | 16.7858 | 17.3269 | 17.6569 | 17.6202 | 16.6101 | 14.9695 | 16.9055 | 17.2312 | 17.5169 | 17.5655 | 17.3003 | 16.5245 | 14.7546 | 6.249 | 8.4134 | 5.5674 | 5.959 | 5.7734 | 6.6943 | 7.6842 | 15.9272 | 15.5854 | 15.4545 | 14.3963 | 14.2773 | 14.2189 |  |  |  | 10.7501 | 9.3212 | 8.9855 | 9.166 | 0.071161 | 0.12894 | 12.8354 |  |  | 10.6762 |  |  | 16.9646 | 16.1565 | 15.1386 | 16.4492 | 15.7312 | 14.8463 | 10.7296 | 10.6984 | 11.4185 | 11.3338 | 9.1608 |  | 10.7422 | 7.9458 | 10.0966 | 9.2392 | 11.1705 | 12.0298 |  | 12.3872 |  |  | 11.9016 | 12.6894 | 12.7238 | [6 empty] | 12.6167 |  |  | 11.3087 |  |  | 9.0211 | 10.2177 | 12.1086 | 7.5006 | 9.1435 | 12.5388 | 7.7679 | 9.492 | 12.4542 | 9.2763 | 10.4447 | 7.7611 | 10.4448 | 8.4091 | 10.2164 | 7.787 | 9.567 | 13.245 | 10.4405 | 10.1133 | 11.5885 | 8.1613 | 9.7099 | 12.8897 | 8.0207 | 10.4143 | 9.7153 | 9.9212 | 8.5454 | 10.3492 | -0.074741 | 20.9546 | 0.034187 | 0.048109 | -38.0673 | 3.1216 | -0.16 | 0.32 | 0.30719 | -0.24787 | -0.432 | -0.41922 | 0.27567 | -0.44153 | 0.85332 | 0.41222 | 0.4247 | 0.42417 | 0.39721 | 0.58787 | 0.42918 | 0.41234
42810.4338 | -542 | 18.5815 | 18.6634 | 18.6472 | 18.654 | 18.0195 | 16.6746 | 14.7467 | 16.7523 | 17.2313 | 17.339 | 17.3517 | 16.91 | 15.9587 | 14.5662 | 15.06 | 15.0635 | 15.6034 | 13.4592 | 13.5707 | 14.1474 |  |  |  | 16.6553 | 15.9954 | 15.1217 | 10.3302 | 9.7713 | 10.2556 | 17.2915 | 16.4379 | 15.2379 | 16.9538 | 16.2329 | 15.253 | 10.8592 | 11.835 |  | 12.3284 | 10.6078 | 10.5082 | 8.6665 |  | 6.3892 | 6.3931 | 5.8865 | 5.9936 | 6.0175 | 6.1406 | 6.7955 | 4.8585 | 6.4827 | 4.6261 | 6.6867 | 8.173 | 42.7786 | 47.3305 | 43.4692 | 15.3138 |  |  | 0.22692 | -0.4934 | 0.051136 | 0.015114 | -0.12074 | -0.084572 | 0.49602 | -0.11976 | -0.39969 | 0.13137 | -0.29697 | 8.8812 | 8.8823 | 2.0087 | 15.8738 | 16.7849 | 17.327 | 17.6573 | 17.616 | 16.6051 | 14.9629 | 16.9025 | 17.2282 | 17.5161 | 17.5589 | 17.2975 | 16.5208 | 14.746 | 6.2393 | 8.4218 | 5.5466 | 5.9723 | 5.7732 | 6.6932 | 7.6859 | 15.9406 | 15.5899 | 15.4514 | 14.4027 | 14.2884 | 14.226 |  |  |  | 10.7632 | 9.3371 | 8.9946 | 9.1779 | 0.14389 | 0.07681 | 12.8295 |  |  | 10.6562 |  |  | 16.9629 | 16.1569 | 15.14 | 16.4448 | 15.7313 | 14.8452 | 10.7225 | 10.7022 | 11.4256 | 11.3321 | 9.181 |  | 10.7383 | 7.9285 | 10.0972 | 9.2076 | 11.1672 | 12.0415 |  | 12.3858 |  |  | 11.9026 | 12.6957 | 12.722 | [6 empty] | 12.617 |  |  | 11.3159 |  |  | 9.0148 | 10.2147 | 12.117 | 7.4866 | 9.125 | 12.5417 | 7.7683 | 9.4842 | 12.4631 | 9.2886 | 10.4543 | 7.7366 | 10.4431 | 8.4197 | 10.2154 | 7.7955 | 9.5772 | 13.2521 | 10.4382 | 10.1295 | 11.5985 | 8.1717 | 9.7119 | 12.8816 | 8.042 | 10.4181 | 9.7247 | 9.9326 | 8.5578 | 10.3515 | -0.15621 | 20.9543 | 0.034664 | 0.047965 | -38.0009 | 3.1216 | -0.46 | 0.33 | 0.55887 | -0.81845 | 0.26348 | 0.14325 | -0.4047 | -0.33869 | 0.82025 | 0.41154 | 0.4252 | 0.42494 | 0.39817 | 0.59039 | 0.42981 | 0.41244
42810.4338 | -541 | 18.5824 | 18.6625 | 18.6482 | 18.6552 | 18.0103 | 16.6792 | 14.7497 | 16.7576 | 17.2429 | 17.3386 | 17.3511 | 16.9132 | 15.9583 | 14.5634 | 15.0542 | 15.0552 | 15.6027 | 13.4631 | 13.5673 | 14.1437 |  |  |  | 16.6562 | 15.9974 | 15.1238 | 10.3345 | 9.7788 | 10.2366 | 17.2864 | 16.4197 | 15.2366 | 16.9414 | 16.2321 | 15.2453 | 10.8515 | 11.851 |  | 12.3158 | 10.6134 | 10.487 | 8.628 |  | 6.3762 | 6.3883 | 5.8762 | 5.9835 | 5.9995 | 6.1285 | 6.7712 | 4.8717 | 6.4814 | 4.6258 | 6.6814 | 8.1728 | 42.8103 | 47.341 | 43.4675 | 15.3097 |  |  | -0.025409 | -0.26407 | 0.052448 | 0.014458 | 0.1283 | -0.011632 | 0.52691 | -0.19138 | -0.19128 | -0.38495 | -0.34724 | 8.8893 | 8.8907 | 2.0084 | 15.8716 | 16.7801 | 17.3276 | 17.6503 | 17.618 | 16.5995 | 14.9648 | 16.9014 | 17.2258 | 17.5158 | 17.5597 | 17.3056 | 16.5133 | 14.7527 | 6.2454 | 8.4022 | 5.5091 | 5.9136 | 5.915 | 6.6921 | 7.6902 | 15.9318 | 15.5886 | 15.4537 | 14.3979 | 14.2818 | 14.2306 |  |  |  | 10.7596 | 9.3324 | 9.0046 | 9.1844 | 0.037732 | 0.12518 | 12.8239 |  |  | 10.6342 |  |  | 16.9667 | 16.158 | 15.1486 | 16.4443 | 15.7397 | 14.8511 | 10.7203 | 10.6988 | 11.4294 | 11.3419 | 9.1966 |  | 10.736 | 7.94 | 10.0967 | 9.2056 | 11.156 | 12.0627 |  | 12.3804 |  |  | 11.9087 | 12.7022 | 12.721 | [6 empty] | 12.6101 |  |  | 11.3283 |  |  | 9.0148 | 10.2165 | 12.1166 | 7.4505 | 9.1112 | 12.5566 | 7.7565 | 9.4889 | 12.4605 | 9.2918 | 10.4508 | 7.7219 | 10.4381 | 8.42 | 10.2136 | 7.8029 | 9.5747 | 13.2507 | 10.4332 | 10.1332 | 11.5967 | 8.1624 | 9.7012 | 12.8751 | 8.04 | 10.4121 | 9.7227 | 9.9279 | 8.5577 | 10.3465 | -0.12 | 20.9546 | 0.035151 | 0.048537 | -37.9287 | 3.1215 | -0.52 | 0.31 | -0.187 | -0.59876 | 0.26684 | 0.1401 | 0.41716 | -0.12561 | 0.84538 | 0.41102 | 0.42487 | 0.42462 | 0.39735 | 0.59506 | 0.43063 | 0.41214
42810.4338 | -540 | 18.5801 | 18.6691 | 18.6408 | 18.6557 | 18.0121 | 16.6753 | 14.7514 | 16.7506 | 17.236 | 17.3318 | 17.3456 | 16.9007 | 15.9581 | 14.5543 | 15.0491 | 15.0532 | 15.5993 | 13.4601 | 13.5733 | 14.1501 |  |  |  | 16.655 | 15.9997 | 15.1222 | 10.3343 | 9.7824 | 10.2192 | 17.2867 | 16.436 | 15.2382 | 16.9559 | 16.2251 | 15.2534 | 10.8644 | 11.8644 |  | 12.3189 | 10.6213 | 10.4809 | 8.5758 |  | 6.388 | 6.3869 | 5.8898 | 5.9881 | 6.004 | 6.1372 | 6.7697 | 4.8984 | 6.4899 | 4.6793 | 6.6897 | 8.1684 | 42.8368 | 47.3411 | 43.4602 | 15.2997 |  |  | 0.14347 | -0.058397 | -0.04546 | -0.33381 | -0.032692 | -0.26462 | 0.52559 | -0.26432 | -0.54331 | 0.18676 | -0.32836 | 8.8722 | 8.8734 | 2.0084 | 15.8624 | 16.782 | 17.3218 | 17.6478 | 17.6175 | 16.5987 | 14.968 | 16.8981 | 17.2247 | 17.5167 | 17.5537 | 17.3054 | 16.5096 | 14.7473 | 6.2325 | 8.3846 | 5.4921 | 5.8543 | 6.02 | 6.6892 | 7.6875 | 15.9292 | 15.5852 | 15.4547 | 14.3919 | 14.281 | 14.2249 |  |  |  | 10.7579 | 9.3354 | 9.0002 | 9.1904 | 0.10783 | -0.033475 | 12.8244 |  |  | 10.6281 |  |  | 16.9588 | 16.1546 | 15.1476 | 16.4495 | 15.7339 | 14.8464 | 10.7132 | 10.6956 | 11.4276 | 11.3519 | 9.2101 |  | 10.7308 | 7.9265 | 10.0931 | 9.2065 | 11.1574 | 12.0802 |  | 12.38 |  |  | 11.8943 | 12.7011 | 12.715 | [6 empty] | 12.6072 |  |  | 11.3315 |  |  | 9.0188 | 10.2143 | 12.1183 | 7.4375 | 9.0979 | 12.5662 | 7.7489 | 9.4961 | 12.4658 | 9.2915 | 10.4544 | 7.7103 | 10.4406 | 8.4119 | 10.213 | 7.806 | 9.5663 | 13.2346 | 10.4316 | 10.1348 | 11.5979 | 8.1551 | 9.6949 | 12.8694 | 8.0393 | 10.4039 | 9.7177 | 9.9235 | 8.5566 | 10.3455 | 0.0026842 | 20.9539 | 0.034933 | 0.049868 | -38.0001 | 3.1215 | -0.38 | 0.37 | 0.44435 | -0.28157 | -0.24843 | -0.67319 | -0.21058 | -0.59911 | 0.84434 | 0.41048 | 0.42512 | 0.42465 | 0.39845 | 0.59664 | 0.4325 | 0.41192
42810.4338 | -539 | 18.5926 | 18.6615 | 18.6431 | 18.6498 | 18.0117 | 16.6762 | 14.7548 | 16.7469 | 17.2399 | 17.3361 | 17.3439 | 16.9106 | 15.9517 | 14.556 | 15.0478 | 15.0563 | 15.5972 | 13.4554 | 13.5818 | 14.1542 |  |  |  | 16.6593 | 15.9996 | 15.1238 | 10.3392 | 9.785 | 10.1849 | 17.2927 | 16.4345 | 15.2339 | 16.9534 | 16.2295 | 15.2426 | 10.8646 | 11.8844 |  | 12.3305 | 10.6227 | 10.4655 | 8.5234 |  | 6.3772 | 6.3903 | 5.8753 | 5.9836 | 5.9889 | 6.1143 | 6.7574 | 4.925 | 6.4941 | 4.7215 | 6.6905 | 8.1647 | 42.8705 | 47.3548 | 43.4594 | 15.2852 |  |  | 0.17764 | -0.25422 | -0.026404 | -0.4153 | -0.027436 | -0.20285 | 0.42177 | -0.44766 | 0.1843 | -0.32201 | -0.44619 | 8.8743 | 8.8753 | 2.0086 | 15.8663 | 16.7824 | 17.3244 | 17.6462 | 17.6167 | 16.6056 | 14.965 | 16.903 | 17.2239 | 17.5176 | 17.5567 | 17.3035 | 16.5154 | 14.7524 | 6.1822 | 8.3855 | 5.5095 | 5.8126 | 5.9973 | 6.6852 | 7.6809 | 15.9239 | 15.5797 | 15.452 | 14.3898 | 14.2752 | 14.2162 |  |  |  | 10.7536 | 9.3275 | 8.9956 | 9.1833 | 0.073795 | 0.031078 | 12.8275 |  |  | 10.6294 |  |  | 16.9604 | 16.1552 | 15.141 | 16.4511 | 15.7378 | 14.8393 | 10.7133 | 10.6989 | 11.429 | 11.3563 | 9.2343 |  | 10.7301 | 7.8162 | 10.0902 | 9.2159 | 11.1614 | 12.1126 |  | 12.3785 |  |  | 11.8849 | 12.6895 | 12.712 | [6 empty] | 12.6185 |  |  | 11.3377 |  |  | 9.0162 | 10.2023 | 12.1097 | 7.4258 | 9.0967 | 12.5649 | 7.7471 | 9.4981 | 12.4672 | 9.2938 | 10.4612 | 7.7144 | 10.4382 | 8.4037 | 10.2104 | 7.798 | 9.5717 | 13.2299 | 10.4344 | 10.1409 | 11.6022 | 8.1571 | 9.6956 | 12.8781 | 8.0447 | 10.4047 | 9.7177 | 9.9193 | 8.5639 | 10.3557 | 0.014818 | 20.9571 | 0.034583 | 0.049448 | -38.0694 | 3.1215 | -0.36 | 0.37 | 0.49441 | -0.58748 | -0.18933 | -0.75088 | -0.1929 | -0.52452 | 0.75633 | 0.40978 | 0.42809 | 0.42452 | 0.40357 | 0.59394 | 0.43396 | 0.41197
42810.4338 | -538 | 18.5772 | 18.6553 | 18.6386 | 18.6461 | 18.0038 | 16.6692 | 14.7508 | 16.7519 | 17.2339 | 17.328 | 17.3416 | 16.8988 | 15.9521 | 14.5561 | 15.0481 | 15.0594 | 15.6011 | 13.4564 | 13.5792 | 14.1533 |  |  |  | 16.6566 | 16.0016 | 15.1222 | 10.3421 | 9.7952 | 10.1581 | 17.2823 | 16.429 | 15.2306 | 16.9447 | 16.2285 | 15.2414 | 10.8598 | 11.8987 |  | 12.32 | 10.6285 | 10.4557 | 8.486 |  | 6.3784 | 6.3863 | 5.8792 | 5.9744 | 5.9802 | 6.1101 | 6.7673 | 4.9823 | 6.4929 | 4.811 | 6.6945 | 8.1653 | 42.9107 | 47.3675 | 43.4657 | 15.2795 |  |  | 0.077103 | -0.10176 | 0.028136 | 0.11237 | 0.084276 | -0.14634 | 0.56436 | -0.26038 | -0.45418 | 0.068432 | -0.43963 | 8.8814 | 8.8823 | 2.0084 | 15.864 | 16.7783 | 17.3231 | 17.6464 | 17.6125 | 16.6133 | 14.962 | 16.8938 | 17.2273 | 17.5133 | 17.5521 | 17.2983 | 16.515 | 14.7587 | 6.1702 | 8.393 | 5.543 | 5.7949 | 5.947 | 6.6909 | 7.6894 | 15.9233 | 15.5896 | 15.4556 | 14.395 | 14.2868 | 14.225 |  |  |  | 10.7625 | 9.3375 | 8.9955 | 9.1656 | 0.18057 | 0.060813 | 12.8179 |  |  | 10.6288 |  |  | 16.957 | 16.1476 | 15.1379 | 16.4401 | 15.7266 | 14.8403 | 10.7112 | 10.6948 | 11.4318 | 11.3541 | 9.2259 |  | 10.7275 | 7.6821 | 10.0906 | 9.2133 | 11.1581 | 12.1465 |  | 12.3781 |  |  | 11.8662 | 12.6812 | 12.7182 | [6 empty] | 12.6185 |  |  | 11.3364 |  |  | 9.0084 | 10.195 | 12.1035 | 7.417 | 9.0942 | 12.5626 | 7.7448 | 9.4953 | 12.4677 | 9.2829 | 10.4594 | 7.7087 | 10.4294 | 8.4009 | 10.2151 | 7.7862 | 9.5707 | 13.2255 | 10.4323 | 10.1432 | 11.6157 | 8.1566 | 9.7049 | 12.8829 | 8.0477 | 10.3988 | 9.7156 | 9.9203 | 8.5648 | 10.3635 | -0.016961 | 20.9546 | 0.03471 | 0.049977 | -38.0624 | 3.1216 | -0.37 | 0.35 | 0.32571 | -0.37169 | 0.19544 | 0.39057 | 0.33808 | -0.44551 | 0.87489 | 0.40993 | 0.43183 | 0.42448 | 0.40558 | 0.5912 | 0.43485 | 0.41276
42810.4338 | -537 | 18.5698 | 18.6562 | 18.6347 | 18.6426 | 18.0013 | 16.6749 | 14.7408 | 16.7558 | 17.2354 | 17.3256 | 17.3441 | 16.8975 | 15.9521 | 14.5548 | 15.045 | 15.0568 | 15.5976 | 13.4579 | 13.5786 | 14.1521 |  |  |  | 16.659 | 15.9957 | 15.1203 | 10.3416 | 9.7997 | 10.1331 | 17.289 | 16.4288 | 15.2369 | 16.9474 | 16.2354 | 15.252 | 10.8561 | 11.8913 |  | 12.3221 | 10.635 | 10.4488 | 8.4553 |  | 6.3876 | 6.3939 | 5.8885 | 5.9822 | 5.9801 | 6.1268 | 6.8207 | 5.0168 | 6.4994 | 5.0174 | 6.699 | 8.1635 | 42.9422 | 47.3546 | 43.473 | 15.2694 |  |  | 0.20195 | 0.010603 | 0.17796 | -0.22999 | 0.071132 | -0.45584 | 0.43557 | -0.32544 | -0.18485 | -0.53558 | -0.48811 | 8.8881 | 8.8896 | 2.0086 | 15.8499 | 16.7748 | 17.3084 | 17.6396 | 17.614 | 16.5955 | 14.9518 | 16.8915 | 17.2198 | 17.503 | 17.549 | 17.2884 | 16.5109 | 14.7485 | 6.1862 | 8.4156 | 5.5335 | 5.7971 | 5.9216 | 6.6993 | 7.686 | 15.9263 | 15.5863 | 15.4459 | 14.3874 | 14.2706 | 14.2209 |  |  |  | 10.7509 | 9.3379 | 8.9911 | 9.1323 | 0.19799 | 0.088667 | 12.8196 |  |  | 10.6325 |  |  | 16.9592 | 16.1525 | 15.1475 | 16.4414 | 15.7259 | 14.8488 | 10.7031 | 10.6896 | 11.4378 | 11.3678 | 9.1956 |  | 10.7351 | 7.57 | 10.0894 | 9.2234 | 11.1657 | 12.1646 |  | 12.3879 |  |  | 11.8527 | 12.6718 | 12.7243 | [6 empty] | 12.6149 |  |  | 11.3364 |  |  | 9.0132 | 10.1953 | 12.0971 | 7.4095 | 9.0964 | 12.5673 | 7.7477 | 9.498 | 12.4704 | 9.2907 | 10.4562 | 7.7108 | 10.4237 | 8.3993 | 10.2133 | 7.7783 | 9.5755 | 13.2119 | 10.4334 | 10.1422 | 11.6139 | 8.1551 | 9.704 | 12.8766 | 8.0531 | 10.3994 | 9.7191 | 9.9245 | 8.566 | 10.3683 | 0.029263 | 20.9544 | 0.033567 | 0.048609 | -38.0493 | 3.1215 | -0.67 | 0.31 | 0.52711 | 0.11998 | 0.49153 | -0.55879 | 0.31061 | -0.7863 | 0.76862 | 0.41102 | 0.4349 | 0.42445 | 0.40477 | 0.59186 | 0.43558 | 0.4133
42810.4338 | -536 | 18.5764 | 18.6567 | 18.6362 | 18.6439 | 18.0054 | 16.6771 | 14.7421 | 16.7532 | 17.2364 | 17.3232 | 17.3449 | 16.8981 | 15.9515 | 14.5572 | 15.0409 | 15.0518 | 15.5921 | 13.4527 | 13.5738 | 14.1439 |  |  |  | 16.663 | 15.9915 | 15.1197 | 10.3353 | 9.791 | 10.117 | 17.2864 | 16.4305 | 15.2324 | 16.9497 | 16.2311 | 15.2488 | 10.8543 | 11.8864 |  | 12.3153 | 10.6245 | 10.4316 | 8.4303 |  | 6.3839 | 6.3857 | 5.8824 | 5.9683 | 5.9737 | 6.1527 | 6.8419 | 5.008 | 6.4987 | 5.1179 | 6.6941 | 8.1649 | 42.9698 | 47.3489 | 43.4791 | 15.2579 |  |  | 0.014675 | -0.24239 | 0.085304 | 0.068998 | 0.047476 | -0.03266 | 0.33963 | -0.2065 | -0.55421 | -0.20515 | -0.37406 | 8.879 | 8.8804 | 2.0082 | 15.8633 | 16.7853 | 17.3268 | 17.6522 | 17.6221 | 16.613 | 14.9698 | 16.9004 | 17.2285 | 17.523 | 17.5575 | 17.3029 | 16.5245 | 14.7549 | 6.2513 | 8.4495 | 5.5299 | 5.7978 | 5.8855 | 6.6997 | 7.6911 | 15.9216 | 15.5833 | 15.4505 | 14.3902 | 14.2754 | 14.2212 |  |  |  | 10.7588 | 9.3421 | 8.9894 | 9.1227 | 0.083115 | 0.081139 | 12.8206 |  |  | 10.6413 |  |  | 16.9584 | 16.16 | 15.1502 | 16.4487 | 15.7324 | 14.8536 | 10.6921 | 10.692 | 11.4465 | 11.3848 | 9.1809 |  | 10.726 | 7.4647 | 10.0793 | 9.23 | 11.1552 | 12.1778 |  | 12.3779 |  |  | 11.8542 | 12.6628 | 12.7213 | [6 empty] | 12.6119 |  |  | 11.3333 |  |  | 9.0066 | 10.199 | 12.0851 | 7.3957 | 9.0986 | 12.5628 | 7.7399 | 9.4994 | 12.4593 | 9.287 | 10.4487 | 7.7097 | 10.4146 | 8.3949 | 10.2089 | 7.7706 | 9.5792 | 13.2072 | 10.437 | 10.1507 | 11.6074 | 8.1464 | 9.7016 | 12.8719 | 8.0558 | 10.4035 | 9.7244 | 9.926 | 8.5525 | 10.3617 | 0.12787 | 20.9549 | 0.032276 | 0.049325 | -38.0693 | 3.1215 | -0.88 | 0.35 | 0.14209 | -0.57364 | 0.34031 | 0.30606 | 0.25377 | -0.21048 | 0.67874 | 0.41113 | 0.4375 | 0.42392 | 0.39758 | 0.59285 | 0.43621 | 0.41383
42810.4338 | -535 | 18.5827 | 18.6652 | 18.6452 | 18.6518 | 18.0142 | 16.6743 | 14.7493 | 16.7561 | 17.238 | 17.3318 | 17.3522 | 16.9115 | 15.9577 | 14.561 | 15.0388 | 15.0436 | 15.5897 | 13.4484 | 13.5613 | 14.1369 |  |  |  | 16.6481 | 15.9946 | 15.1104 | 10.333 | 9.7885 | 10.0951 | 17.2819 | 16.4225 | 15.2368 | 16.946 | 16.2283 | 15.2472 | 10.8563 | 11.9079 |  | 12.3103 | 10.6251 | 10.4269 | 8.4318 |  | 6.3824 | 6.3895 | 5.8899 | 5.9723 | 5.9791 | 6.1846 | 6.8934 | 4.9633 | 6.5038 | 5.2282 | 6.6999 | 8.1586 | 42.9843 | 47.3338 | 43.4848 | 15.247 |  |  | 0.098787 | -0.23779 | -0.025092 | -0.2727 | 0.12173 | 0.19273 | 0.2588 | -0.12699 | -0.54136 | -0.3455 | -0.42056 | 8.8831 | 8.8842 | 2.0086 | 15.8541 | 16.7753 | 17.3207 | 17.6488 | 17.6188 | 16.6046 | 14.9582 | 16.9008 | 17.22 | 17.5132 | 17.5642 | 17.3014 | 16.5204 | 14.7496 | 6.3228 | 8.4496 | 5.5353 | 5.8072 | 5.8843 | 6.7014 | 7.6929 | 15.9117 | 15.5756 | 15.4495 | 14.3825 | 14.274 | 14.2143 |  |  |  | 10.7576 | 9.3314 | 8.9937 | 9.0938 | -0.020211 | 0.13948 | 12.8057 |  |  | 10.6482 |  |  | 16.9593 | 16.1599 | 15.143 | 16.4495 | 15.728 | 14.8484 | 10.6792 | 10.6841 | 11.4474 | 11.3922 | 9.169 |  | 10.7195 | 7.4044 | 10.0772 | 9.2172 | 11.1514 | 12.1979 |  | 12.3757 |  |  | 11.8305 | 12.6497 | 12.7258 | [6 empty] | 12.6238 |  |  | 11.3341 |  |  | 8.9991 | 10.1938 | 12.0791 | 7.3826 | 9.1031 | 12.5576 | 7.7476 | 9.497 | 12.4503 | 9.2838 | 10.4505 | 7.6999 | 10.4154 | 8.3872 | 10.2047 | 7.763 | 9.5738 | 13.2004 | 10.4365 | 10.1528 | 11.6122 | 8.1509 | 9.6918 | 12.8656 | 8.0484 | 10.3921 | 9.7267 | 9.9187 | 8.5402 | 10.3503 | -0.055866 | 20.9558 | 0.03289 | 0.049651 | -38.0429 | 3.1215 | -0.58 | 0.32 | 0.36864 | -0.56818 | -0.18457 | -0.60846 | 0.40638 | 0.51134 | 0.59254 | 0.41125 | 0.4391 | 0.42415 | 0.38984 | 0.59246 | 0.43624 | 0.41459
42810.4339 | -534 | 18.5806 | 18.658 | 18.6512 | 18.6494 | 18.0098 | 16.6674 | 14.7527 | 16.7524 | 17.2368 | 17.3363 | 17.3477 | 16.9063 | 15.9614 | 14.5711 | 15.0349 | 15.0466 | 15.5891 | 13.4465 | 13.561 | 14.1388 |  |  |  | 16.6464 | 15.9882 | 15.1132 | 10.3284 | 9.788 | 10.0623 | 17.275 | 16.4201 | 15.2217 | 16.9423 | 16.2187 | 15.241 | 10.849 | 11.9088 |  | 12.3234 | 10.6293 | 10.4185 | 8.4267 |  | 6.3823 | 6.3883 | 5.8836 | 5.9708 | 5.9791 | 6.1837 | 6.9026 | 4.8977 | 6.5133 | 5.2841 | 6.6988 | 8.1588 | 42.996 | 47.3267 | 43.4984 | 15.2436 |  |  | 0.33732 | -0.36855 | -0.094744 | -0.17677 | 0.30966 | -0.31982 | 0.45528 | -0.32478 | -1.2207 | -0.37802 | -0.42652 | 8.8775 | 8.8789 | 2.0085 | 15.8498 | 16.7756 | 17.3224 | 17.6458 | 17.615 | 16.6037 | 14.9588 | 16.9039 | 17.2244 | 17.5171 | 17.5569 | 17.2982 | 16.5222 | 14.7448 | 6.3243 | 8.4569 | 5.522 | 5.8244 | 5.9192 | 6.7021 | 7.6919 | 15.913 | 15.5721 | 15.441 | 14.385 | 14.2728 | 14.2115 |  |  |  | 10.7501 | 9.327 | 8.9913 | 9.0606 | 0.064476 | 0.008682 | 12.7911 |  |  | 10.6512 |  |  | 16.9651 | 16.1576 | 15.1415 | 16.4498 | 15.7263 | 14.8488 | 10.6568 | 10.681 | 11.4486 | 11.4074 | 9.1638 |  | 10.716 | 7.4068 | 10.0763 | 9.202 | 11.1584 | 12.2188 |  | 12.377 |  |  | 11.7818 | 12.6243 | 12.7014 | [6 empty] | 12.621 |  |  | 11.3198 |  |  | 9.0061 | 10.1976 | 12.0843 | 7.3735 | 9.1055 | 12.5581 | 7.7506 | 9.4966 | 12.4551 | 9.2921 | 10.4548 | 7.6931 | 10.4093 | 8.3839 | 10.2066 | 7.7689 | 9.5783 | 13.2061 | 10.4457 | 10.1531 | 11.6112 | 8.1584 | 9.694 | 12.8661 | 8.0556 | 10.3928 | 9.7294 | 9.9165 | 8.5353 | 10.3531 | 0.046404 | 20.9544 | 0.033608 | 0.050078 | -37.9896 | 3.1215 | -0.37 | 0.35 | 0.68115 | -0.70736 | -0.35864 | -0.48988 | 0.64815 | -0.65869 | 0.7859 | 0.41128 | 0.439 | 0.4248 | 0.38975 | 0.59382 | 0.43614 | 0.41527
42810.4339 | -533 | 18.5722 | 18.6563 | 18.6318 | 18.6446 | 18.0049 | 16.6681 | 14.7468 | 16.7553 | 17.2331 | 17.3399 | 17.3495 | 16.9077 | 15.9532 | 14.5572 | 15.0436 | 15.0566 | 15.6016 | 13.4642 | 13.577 | 14.1543 |  |  |  | 16.6635 | 16.0063 | 15.1281 | 10.338 | 9.8058 | 10.0415 | 17.2703 | 16.4179 | 15.2164 | 16.9464 | 16.2227 | 15.2449 | 10.8519 | 11.8929 |  | 12.3118 | 10.6246 | 10.4255 | 8.4498 |  | 6.3831 | 6.3923 | 5.8804 | 5.9547 | 5.9669 | 6.165 | 6.8745 | 4.8567 | 6.5061 | 5.2732 | 6.6981 | 8.1561 | 42.9929 | 47.3239 | 43.503 | 15.2278 |  |  | 0.090243 | -0.2851 | 0.1313 | -0.007886 | -0.19303 | -0.058944 | 0.36723 | -0.27024 | 0.54081 | -0.6709 | -0.3675 | 8.8796 | 8.8808 | 2.0085 | 15.8513 | 16.7807 | 17.3228 | 17.6465 | 17.6145 | 16.6065 | 14.9614 | 16.906 | 17.2272 | 17.5173 | 17.5575 | 17.3061 | 16.5233 | 14.7511 | 6.334 | 8.4371 | 5.5218 | 5.8469 | 5.9577 | 6.7106 | 7.6912 | 15.9112 | 15.5718 | 15.4447 | 14.3791 | 14.2734 | 14.215 |  |  |  | 10.7536 | 9.3154 | 8.9944 | 9.037 | 0.044418 | -0.0037392 | 12.7825 |  |  | 10.6494 |  |  | 16.9633 | 16.1551 | 15.1448 | 16.4461 | 15.7357 | 14.8496 | 10.6424 | 10.6845 | 11.458 | 11.4162 | 9.1272 |  | 10.7155 | 7.4561 | 10.0737 | 9.1896 | 11.1567 | 12.2251 |  | 12.3801 |  |  | 11.734 | 12.6202 | 12.6917 | [6 empty] | 12.6078 |  |  | 11.3071 |  |  | 9.0014 | 10.2015 | 12.0693 | 7.374 | 9.0963 | 12.5549 | 7.7347 | 9.4712 | 12.4484 | 9.2935 | 10.4562 | 7.6959 | 10.4016 | 8.378 | 10.1972 | 7.7365 | 9.5735 | 13.1875 | 10.4443 | 10.151 | 11.6039 | 8.1598 | 9.6774 | 12.8537 | 8.0471 | 10.3872 | 9.7217 | 9.9005 | 8.5319 | 10.3442 | 0.092243 | 20.9543 | 0.033797 | 0.0501 | -37.968 | 3.1215 | -0.59 | 0.29 | 0.3523 | -0.62214 | 0.42221 | -0.10347 | -0.51171 | -0.28277 | 0.7058 | 0.41228 | 0.43755 | 0.4251 | 0.38967 | 0.59376 | 0.43559 | 0.41604
42810.4339 | -532 | 18.564 | 18.6544 | 18.6345 | 18.6426 | 18.0051 | 16.6711 | 14.7441 | 16.749 | 17.2361 | 17.3339 | 17.3504 | 16.9004 | 15.9518 | 14.5587 | 15.0359 | 15.0451 | 15.5936 | 13.4461 | 13.573 | 14.1381 |  |  |  | 16.6522 | 15.995 | 15.1155 | 10.3222 | 9.7954 | 10.0201 | 17.2784 | 16.4228 | 15.2321 | 16.9434 | 16.2281 | 15.2436 | 10.843 | 11.8815 |  | 12.3146 | 10.6381 | 10.4212 | 8.4598 |  | 6.3749 | 6.3909 | 5.8772 | 5.9499 | 5.9554 | 6.1513 | 6.8452 | 4.8243 | 6.5086 | 5.1613 | 6.7018 | 8.1524 | 43.0037 | 47.2971 | 43.513 | 15.2244 |  |  | -0.18969 | -0.21019 | 0.020908 | -0.063082 | 0.057332 | -0.045144 | 0.39023 | -0.11976 | 0.12475 | 0.042836 | -0.3532 | 8.8796 | 8.8807 | 2.0085 | 15.8482 | 16.7719 | 17.3207 | 17.6411 | 17.6129 | 16.6095 | 14.9625 | 16.8928 | 17.2214 | 17.5149 | 17.5613 | 17.3028 | 16.5145 | 14.7526 | 6.3593 | 8.4564 | 5.5105 | 5.8511 | 5.9467 | 6.7025 | 7.6908 | 15.9014 | 15.5659 | 15.4424 | 14.3849 | 14.2652 | 14.2099 |  |  |  | 10.7511 | 9.3103 | 8.9915 | 9.0207 | 0.12586 | 0.16188 | 12.7773 |  |  | 10.6578 |  |  | 16.9633 | 16.1492 | 15.144 | 16.4475 | 15.734 | 14.8503 | 10.6243 | 10.686 | 11.4702 | 11.4265 | 9.0474 |  | 10.7162 | 7.5382 | 10.0682 | 9.189 | 11.1572 | 12.2399 |  | 12.3814 |  |  | 11.6892 | 12.6192 | 12.6621 | [6 empty] | 12.6101 |  |  | 11.3106 |  |  | 9.0023 | 10.1999 | 12.0714 | 7.3767 | 9.1024 | 12.5554 | 7.7307 | 9.458 | 12.4341 | 9.291 | 10.452 | 7.7118 | 10.4026 | 8.3666 | 10.208 | 7.7191 | 9.5715 | 13.1724 | 10.4264 | 10.1462 | 11.5926 | 8.1549 | 9.6613 | 12.8511 | 8.0491 | 10.3767 | 9.7141 | 9.8931 | 8.5125 | 10.3229 | -0.044888 | 20.9551 | 0.033877 | 0.050418 | -37.9817 | 3.1214 | -0.54 | 0.39 | -0.51075 | -0.53419 | 0.16848 | -0.29265 | 0.27887 | -0.24746 | 0.72755 | 0.41451 | 0.43509 | 0.42513 | 0.38591 | 0.59498 | 0.43502 | 0.41641
42810.4339 | -531 | 18.5651 | 18.6599 | 18.6382 | 18.6388 | 18.005 | 16.6722 | 14.7462 | 16.7508 | 17.2292 | 17.3291 | 17.3405 | 16.898 | 15.9491 | 14.5528 | 15.0196 | 15.0409 | 15.5955 | 13.4512 | 13.5692 | 14.1404 |  |  |  | 16.6486 | 15.9818 | 15.1124 | 10.3182 | 9.789 | 10.0021 | 17.2641 | 16.4221 | 15.2309 | 16.9392 | 16.2244 | 15.2397 | 10.837 | 11.8841 |  | 12.3075 | 10.6455 | 10.4153 | 8.4648 |  | 6.3738 | 6.3919 | 5.8709 | 5.9353 | 5.9492 | 6.1455 | 6.8353 | 4.7332 | 6.5104 | 5.0836 | 6.7046 | 8.1522 | 42.9984 | 47.2837 | 43.5204 | 15.2153 |  |  | 0.15661 | -0.086653 | 0.083332 | -0.13602 | -0.040576 | 0.10599 | 0.51771 | -0.2111 | -0.59507 | 0.58202 | -0.36174 | 8.8821 | 8.8836 | 2.0084 | 15.8379 | 16.7733 | 17.3188 | 17.6377 | 17.6137 | 16.6062 | 14.9676 | 16.8968 | 17.2262 | 17.5078 | 17.5519 | 17.3049 | 16.5192 | 14.7514 | 6.4013 | 8.4398 | 5.4878 | 5.831 | 5.9943 | 6.7083 | 7.6875 | 15.9011 | 15.5675 | 15.4416 | 14.3855 | 14.2637 | 14.2097 |  |  |  | 10.7529 | 9.3145 | 8.9963 | 9.0279 | 0.16132 | 0.037288 | 12.7675 |  |  | 10.6605 |  |  | 16.9523 | 16.1434 | 15.1386 | 16.4456 | 15.728 | 14.8489 | 10.5962 | 10.6834 | 11.4797 | 11.4398 | 8.9615 |  | 10.7141 | 7.6429 | 10.0715 | 9.1751 | 11.1576 | 12.2608 |  | 12.3855 |  |  | 11.6875 | 12.6231 | 12.617 | [6 empty] | 12.6198 |  |  | 11.31 |  |  | 8.9899 | 10.1791 | 12.0588 | 7.3508 | 9.0922 | 12.5397 | 7.6975 | 9.4377 | 12.4103 | 9.2728 | 10.4432 | 7.7105 | 10.384 | 8.3367 | 10.1918 | 7.7323 | 9.5841 | 13.1943 | 10.4308 | 10.1605 | 11.6112 | 8.1706 | 9.6719 | 12.851 | 8.0572 | 10.3916 | 9.7308 | 9.8884 | 8.5088 | 10.3358 | -0.20051 | 20.9558 | 0.033809 | 0.049325 | -37.908 | 3.1214 | -0.09 | 0.43 | 0.46407 | -0.34299 | 0.33635 | -0.42973 | -0.2346 | 0.37917 | 0.83799 | 0.41683 | 0.43229 | 0.42553 | 0.38192 | 0.59711 | 0.43468 | 0.41627
42810.4339 | -530 | 18.5606 | 18.6606 | 18.6379 | 18.6398 | 18.0077 | 16.6708 | 14.7489 | 16.7514 | 17.2311 | 17.3311 | 17.3423 | 16.9004 | 15.9488 | 14.5563 | 15.0332 | 15.0397 | 15.5884 | 13.4476 | 13.5644 | 14.1347 |  |  |  | 16.6474 | 15.9869 | 15.1081 | 10.3109 | 9.7855 | 9.9934 | 17.2613 | 16.4142 | 15.2258 | 16.9342 | 16.2236 | 15.233 | 10.8427 | 11.878 |  | 12.3073 | 10.6341 | 10.4246 | 8.4885 |  | 6.3686 | 6.3812 | 5.8625 | 5.9284 | 5.9408 | 6.1355 | 6.8179 | 4.6608 | 6.5093 | 4.9921 | 6.7038 | 8.1493 | 42.9969 | 47.2887 | 43.5244 | 15.2043 |  |  | -0.13514 | -0.15565 | 0.15627 | 0.09791 | -0.045832 | -0.3277 | 0.22135 | 0.078032 | -0.41701 | -0.38075 | -0.414 | 8.8857 | 8.887 | 2.0085 | 15.854 | 16.7717 | 17.313 | 17.6456 | 17.6186 | 16.6041 | 14.9626 | 16.8994 | 17.2239 | 17.517 | 17.5581 | 17.3067 | 16.5205 | 14.7558 | 6.4043 | 8.4449 | 5.4789 | 5.836 | 6.0331 | 6.7002 | 7.6894 | 15.8977 | 15.5669 | 15.4395 | 14.3773 | 14.267 | 14.208 |  |  |  | 10.7505 | 9.309 | 9.0005 | 9.0448 | 0.080481 | 0.0056708 | 12.767 |  |  | 10.6626 |  |  | 16.9532 | 16.1486 | 15.1368 | 16.4426 | 15.7258 | 14.8499 | 10.5804 | 10.6805 | 11.4912 | 11.4555 | 8.9321 |  | 10.7156 | 7.7086 | 10.0637 | 9.1707 | 11.1519 | 12.2916 |  | 12.3842 |  |  | 11.6793 | 12.6274 | 12.6123 | [6 empty] | 12.6251 |  |  | 11.3159 |  |  | 8.9916 | 10.1838 | 12.0485 | 7.3436 | 9.0918 | 12.5367 | 7.6932 | 9.4465 | 12.4017 | 9.2794 | 10.4459 | 7.7092 | 10.3996 | 8.3183 | 10.195 | 7.734 | 9.6011 | 13.1922 | 10.442 | 10.1629 | 11.6136 | 8.174 | 9.6827 | 12.8537 | 8.0588 | 10.4056 | 9.7379 | 9.9064 | 8.5005 | 10.3453 | 0.015396 | 20.9538 | 0.033458 | 0.049666 | -37.8989 | 3.1214 | -0.13 | 0.41 | -0.43109 | -0.45968 | 0.4606 | 0.36458 | -0.24933 | -0.6667 | 0.54793 | 0.4177 | 0.43021 | 0.42546 | 0.38065 | 0.59832 | 0.43421 | 0.41572
42810.4339 | -529 | 18.5684 | 18.6601 | 18.638 | 18.6444 | 18.0084 | 16.6718 | 14.7458 | 16.7573 | 17.2374 | 17.3345 | 17.341 | 16.9053 | 15.9522 | 14.5552 | 15.0227 | 15.0397 | 15.5918 | 13.4538 | 13.5637 | 14.1372 |  |  |  | 16.6473 | 15.9968 | 15.1074 | 10.3121 | 9.7886 | 9.982 | 17.2601 | 16.4096 | 15.2268 | 16.943 | 16.2198 | 15.233 | 10.8414 | 11.8596 |  | 12.3073 | 10.6399 | 10.4285 | 8.511 |  | 6.3626 | 6.3814 | 5.8503 | 5.9303 | 5.9344 | 6.1408 | 6.8305 | 4.6889 | 6.52 | 4.9754 | 6.7107 | 8.1501 | 42.9936 | 47.3042 | 43.5444 | 15.1911 |  |  | -0.018837 | -0.097821 | 0.032736 | 0.022342 | 0.03302 | -0.39079 | 0.27918 | 0.07146 | -0.54525 | -0.24732 | -0.49467 | 8.8835 | 8.8847 | 2.0085 | 15.8363 | 16.7689 | 17.3132 | 17.6327 | 17.6156 | 16.6005 | 14.9555 | 16.8876 | 17.2227 | 17.5106 | 17.557 | 17.2953 | 16.5175 | 14.7452 | 6.4049 | 8.4163 | 5.4966 | 5.8432 | 6.0117 | 6.7128 | 7.6862 | 15.9028 | 15.5712 | 15.4464 | 14.3762 | 14.2642 | 14.2119 |  |  |  | 10.7495 | 9.3166 | 9.0012 | 9.0599 | 0.017067 | -0.042697 | 12.7708 |  |  | 10.6686 |  |  | 16.9624 | 16.1522 | 15.1367 | 16.4476 | 15.7273 | 14.8532 | 10.5826 | 10.6813 | 11.5042 | 11.4631 | 8.8936 |  | 10.7149 | 7.7693 | 10.0622 | 9.1697 | 11.1493 | 12.3107 |  | 12.3814 |  |  | 11.705 | 12.6293 | 12.6015 | [6 empty] | 12.6165 |  |  | 11.3192 |  |  | 8.9856 | 10.1918 | 12.0453 | 7.3501 | 9.0959 | 12.5429 | 7.6909 | 9.456 | 12.3863 | 9.2803 | 10.4554 | 7.7173 | 10.4174 | 8.3177 | 10.2038 | 7.725 | 9.6038 | 13.1806 | 10.4364 | 10.1638 | 11.6081 | 8.1627 | 9.6717 | 12.8437 | 8.0608 | 10.4133 | 9.7296 | 9.8939 | 8.4988 | 10.3446 | 0.012892 | 20.957 | 0.033424 | 0.048906 | -37.9794 | 3.1215 | -0.06 | 0.38 | -0.16094 | -0.36442 | 0.21081 | 0.17416 | 0.21163 | -0.72806 | 0.61537 | 0.41875 | 0.42847 | 0.4254 | 0.38205 | 0.59599 | 0.43354 | 0.41527
42810.4339 | -528 | 18.5594 | 18.6453 | 18.636 | 18.6426 | 17.9947 | 16.6644 | 14.7398 | 16.7493 | 17.2563 | 17.3239 | 17.3276 | 16.9103 | 15.9481 | 14.5472 | 15.0263 | 15.0427 | 15.5923 | 13.4484 | 13.5606 | 14.1425 |  |  |  | 16.6564 | 15.9903 | 15.1176 | 10.3107 | 9.7966 | 10.0283 | 17.2637 | 16.4126 | 15.2242 | 16.9393 | 16.2192 | 15.2417 | 10.8459 | 11.8391 |  | 12.3103 | 10.6534 | 10.4301 | 8.5227 |  | 6.3542 | 6.3766 | 5.8599 | 5.9261 | 5.9419 | 6.1595 | 6.8468 | 4.7181 | 6.51 | 4.9031 | 6.7104 | 8.1511 | 42.9875 | 47.3241 | 43.5323 | 15.1846 |  |  | 0.043587 | -0.29299 | 0.10173 | 0.07491 | 0.14276 | -0.29288 | 0.3738 | 0.089204 | -0.7599 | -0.42628 | -0.41996 | 8.8865 | 8.8877 | 2.0085 | 15.8344 | 16.7683 | 17.3138 | 17.6388 | 17.6081 | 16.6018 | 14.9626 | 16.8948 | 17.2198 | 17.5121 | 17.5551 | 17.3038 | 16.518 | 14.7597 | 6.3876 | 8.3788 | 5.4729 | 5.8119 | 5.9604 | 6.7131 | 7.7053 | 15.8993 | 15.5688 | 15.4374 | 14.3764 | 14.2609 | 14.2086 |  |  |  | 10.7464 | 9.3177 | 8.9918 | 9.0388 | -0.018185 | -0.045331 | 12.7632 |  |  | 10.6637 |  |  | 16.9559 | 16.1545 | 15.1392 | 16.443 | 15.7253 | 14.8434 | 10.5897 | 10.6803 | 11.5033 | 11.4649 | 8.8322 |  | 10.701 | 7.7886 | 10.0651 | 9.1585 | 11.144 | 12.3134 |  | 12.3685 |  |  | 11.7135 | 12.6131 | 12.5736 | [6 empty] | 12.6103 |  |  | 11.315 |  |  | 8.9905 | 10.1902 | 12.044 | 7.3515 | 9.1124 | 12.543 | 7.6848 | 9.4564 | 12.3753 | 9.2842 | 10.4527 | 7.7225 | 10.4256 | 8.3215 | 10.201 | 7.7338 | 9.619 | 13.1877 | 10.4477 | 10.1718 | 11.6176 | 8.1689 | 9.678 | 12.8498 | 8.0742 | 10.4281 | 9.7391 | 9.8969 | 8.5012 | 10.3485 | -0.023317 | 20.9541 | 0.032534 | 0.049021 | -38.0799 | 3.1215 | -0.21 | 0.43 | 0.24484 | -0.63067 | 0.37163 | 0.3189 | 0.44006 | -0.63031 | 0.71208 | 0.41999 | 0.42803 | 0.42554 | 0.38399 | 0.60084 | 0.43337 | 0.41575
42810.4339 | -527 | 18.5559 | 18.6503 | 18.6542 | 18.6396 | 18.0109 | 16.6744 | 14.7461 | 16.778 | 17.2793 | 17.3585 | 17.2271 | 16.9241 | 15.9418 | 14.5416 | 15.0262 | 15.046 | 15.5932 | 13.446 | 13.5564 | 14.1438 |  |  |  | 16.6531 | 15.9948 | 15.1131 | 10.3051 | 9.7927 | 10.0516 | 17.2669 | 16.4089 | 15.2263 | 16.9323 | 16.2188 | 15.2399 | 10.8456 | 11.8398 |  | 12.3099 | 10.6659 | 10.4269 | 8.5366 |  | 6.3607 | 6.3702 | 5.858 | 5.9302 | 5.939 | 6.1571 | 6.8239 | 4.7761 | 6.4984 | 4.8579 | 6.698 | 8.1404 | 42.9803 | 47.3611 | 43.5343 | 15.1791 |  |  | 0.090243 | -0.14842 | 0.039308 | -0.000658 | 0.1697 | -0.71803 | 0.39351 | -0.002792 | -0.81049 | -0.079477 | -0.51216 | 8.8854 | 8.8869 | 2.0087 | 15.8372 | 16.7645 | 17.3105 | 17.6385 | 17.611 | 16.5985 | 14.955 | 16.9009 | 17.2183 | 17.5067 | 17.5504 | 17.3071 | 16.5181 | 14.7611 | 6.3721 | 8.3564 | 5.4314 | 5.8424 | 5.9134 | 6.7041 | 7.7012 | 15.8908 | 15.5599 | 15.437 | 14.3762 | 14.2611 | 14.2038 |  |  |  | 10.7449 | 9.3088 | 8.9824 | 9.0083 | -0.053032 | 0.19839 | 12.7514 |  |  | 10.6573 |  |  | 16.9525 | 16.1541 | 15.1376 | 16.437 | 15.7215 | 14.8389 | 10.6011 | 10.6758 | 11.4983 | 11.4657 | 8.8144 |  | 10.7054 | 7.8265 | 10.0557 | 9.1639 | 11.15 | 12.3136 |  | 12.3731 |  |  | 11.7146 | 12.6044 | 12.5366 | [6 empty] | 12.6055 |  |  | 11.3112 |  |  | 8.9739 | 10.1821 | 12.0394 | 7.3652 | 9.1075 | 12.5381 | 7.6849 | 9.4537 | 12.3685 | 9.2913 | 10.4479 | 7.7159 | 10.4289 | 8.3101 | 10.2039 | 7.7285 | 9.6215 | 13.1868 | 10.4481 | 10.1623 | 11.6155 | 8.1763 | 9.6751 | 12.8459 | 8.0696 | 10.4267 | 9.7313 | 9.9016 | 8.4991 | 10.3508 | -0.14543 | 20.9541 | 0.033407 | 0.0485 | -38.0264 | 3.1214 | -0.21 | 0.35 | 0.35231 | -0.44887 | 0.231 | -0.029887 | 0.47979 | -0.98692 | 0.73061 | 0.42063 | 0.42667 | 0.42559 | 0.38467 | 0.60496 | 0.43297 | 0.41655
42810.4339 | -526 | 18.5431 | 18.6537 | 18.6238 | 18.6409 | 18.006 | 16.6689 | 14.7399 | 16.751 | 17.2554 | 17.3187 | 17.3173 | 16.9116 | 15.9399 | 14.5379 | 15.0196 | 15.0353 | 15.5816 | 13.4383 | 13.5494 | 14.1371 |  |  |  | 16.6442 | 15.9841 | 15.109 | 10.3115 | 9.7798 | 10.0776 | 17.2572 | 16.4167 | 15.2247 | 16.9403 | 16.224 | 15.2379 | 10.847 | 11.8182 |  | 12.3046 | 10.6423 | 10.4239 | 8.5497 |  | 6.3698 | 6.3654 | 5.8552 | 5.923 | 5.9268 | 6.1472 | 6.8013 | 4.7524 | 6.5041 | 4.8717 | 6.7017 | 8.1475 | 42.9895 | 47.3708 | 43.5476 | 15.1712 |  |  | 0.13559 | -0.015025 | 0.2509 | 0.16954 | 0.034336 | -0.39539 | -0.029012 | 0.22194 | -0.64314 | -1.17 | -0.3381 | 8.8806 | 8.8816 | 2.0084 | 15.8318 | 16.764 | 17.3033 | 17.6369 | 17.6111 | 16.6028 | 14.9583 | 16.9005 | 17.223 | 17.5095 | 17.5491 | 17.3056 | 16.5203 | 14.7512 | 6.3536 | 8.3567 | 5.4104 | 5.8229 | 5.8727 | 6.6997 | 7.698 | 15.8933 | 15.5582 | 15.4352 | 14.3873 | 14.2656 | 14.2043 |  |  |  | 10.7558 | 9.3225 | 8.9873 | 8.9936 | 0.011192 | 0.08622 | 12.7479 |  |  | 10.6584 |  |  | 16.949 | 16.1486 | 15.1315 | 16.4385 | 15.7235 | 14.8407 | 10.6268 | 10.6728 | 11.4935 | 11.4632 | 8.8043 |  | 10.6966 | 7.8912 | 10.0553 | 9.1656 | 11.1403 | 12.2988 |  | 12.3769 |  |  | 11.6849 | 12.5978 | 12.5248 | [6 empty] | 12.5907 |  |  | 11.3053 |  |  | 8.9749 | 10.1758 | 12.0403 | 7.3789 | 9.11 | 12.5429 | 7.673 | 9.4614 | 12.3622 | 9.287 | 10.4511 | 7.7233 | 10.4253 | 8.2941 | 10.2014 | 7.7342 | 9.6186 | 13.1814 | 10.4458 | 10.1556 | 11.6054 | 8.1764 | 9.6674 | 12.8418 | 8.0673 | 10.4318 | 9.7302 | 9.8951 | 8.4958 | 10.3431 | 0.098599 | 20.9552 | 0.031708 | 0.04685 | -38.1094 | 3.1214 | -0.28 | 0.38 | 0.43186 | -0.14282 | 0.5836 | 0.47974 | 0.21581 | -0.73234 | -0.19838 | 0.42062 | 0.42486 | 0.42522 | 0.38622 | 0.60693 | 0.43265 | 0.41732
42810.434 | -525 | 18.5552 | 18.6481 | 18.628 | 18.6328 | 17.9991 | 16.6675 | 14.737 | 16.7469 | 17.2319 | 17.3213 | 17.3435 | 16.8859 | 15.9407 | 14.5517 | 15.028 | 15.0376 | 15.5866 | 13.4443 | 13.5559 | 14.1431 |  |  |  | 16.6489 | 15.9921 | 15.1147 | 10.3199 | 9.7914 | 10.1069 | 17.2519 | 16.4095 | 15.2277 | 16.9343 | 16.2182 | 15.2371 | 10.851 | 11.7779 |  | 12.3106 | 10.6256 | 10.4054 | 8.5388 |  | 6.3629 | 6.3657 | 5.8494 | 5.9113 | 5.914 | 6.1347 | 6.7741 | 4.7566 | 6.4935 | 4.8645 | 6.6962 | 8.1453 | 43.0101 | 47.3885 | 43.5561 | 15.1643 |  |  | 0.1093 | -0.17733 | 0.34224 | 0.11171 | -0.19566 | -0.20548 | -0.14532 | 0.039264 | -0.47267 | -0.26872 | -0.40426 | 8.8843 | 8.8856 | 2.0084 | 15.8323 | 16.7636 | 17.3029 | 17.6388 | 17.6092 | 16.6 | 14.9594 | 16.8905 | 17.2237 | 17.5181 | 17.5513 | 17.3059 | 16.52 | 14.7546 | 6.3207 | 8.3513 | 5.3804 | 5.7799 | 5.8419 | 6.7065 | 7.7047 | 15.8987 | 15.558 | 15.4328 | 14.3881 | 14.2618 | 14.2066 |  |  |  | 10.7554 | 9.3288 | 8.9804 | 8.9747 | -0.11381 | 0.048957 | 12.7491 |  |  | 10.6645 |  |  | 16.9459 | 16.1436 | 15.1307 | 16.4357 | 15.7221 | 14.8398 | 10.6515 | 10.6703 | 11.4854 | 11.4584 | 8.7883 |  | 10.692 | 7.9747 | 10.0442 | 9.1746 | 11.1376 | 12.276 |  | 12.3752 |  |  | 11.6651 | 12.6087 | 12.5254 | [6 empty] | 12.5937 |  |  | 11.3065 |  |  | 8.9693 | 10.1697 | 12.0466 | 7.3788 | 9.1114 | 12.5451 | 7.6791 | 9.4623 | 12.3665 | 9.278 | 10.4477 | 7.7239 | 10.4311 | 8.2689 | 10.1979 | 7.7432 | 9.6263 | 13.1776 | 10.4409 | 10.1627 | 11.6012 | 8.1817 | 9.6733 | 12.8346 | 8.0734 | 10.4294 | 9.7343 | 9.8945 | 8.5042 | 10.3438 | -0.046236 | 20.9551 | 0.031909 | 0.046886 | -38.071 | 3.1213 | -0.24 | 0.31 | 0.38776 | -0.49064 | 0.68161 | 0.38942 | -0.51515 | -0.52793 | -0.44397 | 0.42092 | 0.42217 | 0.42488 | 0.39066 | 0.61104 | 0.43309 | 0.41783
42810.434 | -524 | 18.556 | 18.6573 | 18.6286 | 18.6402 | 18.006 | 16.6655 | 14.7434 | 16.7525 | 17.2349 | 17.322 | 17.3428 | 16.896 | 15.9434 | 14.5572 | 15.015 | 15.0355 | 15.5834 | 13.4412 | 13.5508 | 14.1394 |  |  |  | 16.6467 | 15.9907 | 15.1096 | 10.3232 | 9.7843 | 10.1036 | 17.2539 | 16.4085 | 15.222 | 16.9311 | 16.2178 | 15.2379 | 10.8417 | 11.7455 |  | 12.3095 | 10.626 | 10.4065 | 8.5442 |  | 6.3648 | 6.3636 | 5.8456 | 5.8984 | 5.9083 | 6.1143 | 6.7375 | 4.7732 | 6.4917 | 4.8488 | 6.6982 | 8.1389 | 43.0105 | 47.3902 | 43.5665 | 15.1491 |  |  | -0.005693 | -0.082709 | 0.11816 | -0.059142 | 0.03762 | -0.28959 | 0.25486 | -0.099388 | -0.23487 | -0.36145 | -0.18828 | 8.8808 | 8.8819 | 2.0086 | 15.831 | 16.7546 | 17.3058 | 17.6379 | 17.6014 | 16.5797 | 14.9519 | 16.8925 | 17.2179 | 17.5064 | 17.5525 | 17.2991 | 16.5107 | 14.7525 | 6.2056 | 8.3364 | 5.318 | 5.7406 | 5.8242 | 6.7026 | 7.708 | 15.8951 | 15.5644 | 15.4431 | 14.3842 | 14.2638 | 14.2124 |  |  |  | 10.7504 | 9.3191 | 8.991 | 8.9462 | -0.13164 | -0.096145 | 12.75 |  |  | 10.6752 |  |  | 16.9501 | 16.1398 | 15.1372 | 16.4387 | 15.7239 | 14.8433 | 10.6769 | 10.6712 | 11.4871 | 11.458 | 8.8068 |  | 10.7029 | 8.0875 | 10.0601 | 9.2434 | 11.1453 | 12.2757 |  | 12.3775 |  |  | 11.6726 | 12.5952 | 12.5372 | [6 empty] | 12.5982 |  |  | 11.302 |  |  | 8.9612 | 10.1733 | 12.0476 | 7.3831 | 9.1139 | 12.5476 | 7.6741 | 9.4672 | 12.3689 | 9.2633 | 10.4408 | 7.7164 | 10.4327 | 8.2567 | 10.1946 | 7.7551 | 9.6289 | 13.1796 | 10.4337 | 10.1633 | 11.606 | 8.1807 | 9.6728 | 12.8258 | 8.0806 | 10.4359 | 9.7441 | 9.8843 | 8.5065 | 10.3398 | -0.0030938 | 20.9532 | 0.032397 | 0.047907 | -38.0129 | 3.1214 | -0.67 | 0.29 | -0.088496 | -0.33508 | 0.4005 | -0.28335 | 0.22588 | -0.62671 | 0.58793 | 0.42076 | 0.41956 | 0.42322 | 0.403 | 0.61835 | 0.43263 | 0.41846
42810.434 | -523 | 18.5541 | 18.6459 | 18.6217 | 18.6401 | 17.9999 | 16.6653 | 14.7427 | 16.7466 | 17.2298 | 17.327 | 17.3384 | 16.8983 | 15.9411 | 14.5508 | 15.0159 | 15.0323 | 15.5843 | 13.4394 | 13.5524 | 14.1406 |  |  |  | 16.649 | 15.9889 | 15.1141 | 10.3216 | 9.7823 | 10.0929 | 17.2547 | 16.407 | 15.227 | 16.9375 | 16.2138 | 15.2324 | 10.8448 | 11.7072 |  | 12.3026 | 10.6283 | 10.4042 | 8.5408 |  | 6.3707 | 6.3647 | 5.8426 | 5.895 | 5.9053 | 6.1062 | 6.7137 | 4.7945 | 6.4917 | 4.8298 | 6.692 | 8.1386 | 43.0126 | 47.3958 | 43.5765 | 15.144 |  |  | 0.051475 | -0.011741 | 0.1451 | -0.10579 | -0.21603 | -0.16802 | 0.26932 | -0.067848 | -0.33042 | -0.14431 | -0.3369 | 8.879 | 8.8805 | 2.0083 | 15.8216 | 16.754 | 17.305 | 17.6271 | 17.6062 | 16.5901 | 14.9573 | 16.8843 | 17.2152 | 17.508 | 17.5418 | 17.3034 | 16.5267 | 14.7481 | 6.1111 | 8.3247 | 5.2654 | 5.6859 | 5.804 | 6.6953 | 7.6941 | 15.8883 | 15.5564 | 15.4337 | 14.3794 | 14.2589 | 14.1986 |  |  |  | 10.7498 | 9.3109 | 8.9807 | 8.9122 | 0.021119 | 0.014328 | 12.7506 |  |  | 10.6797 |  |  | 16.9542 | 16.141 | 15.1389 | 16.4412 | 15.7269 | 14.842 | 10.6939 | 10.6721 | 11.4832 | 11.457 | 8.8304 |  | 10.6952 | 8.1894 | 10.0407 | 9.2466 | 11.1439 | 12.2535 |  | 12.3688 |  |  | 11.693 | 12.5805 | 12.5399 | [6 empty] | 12.5874 |  |  | 11.2857 |  |  | 8.9584 | 10.1703 | 12.0476 | 7.395 | 9.111 | 12.5573 | 7.6639 | 9.472 | 12.3651 | 9.2618 | 10.4394 | 7.7252 | 10.4366 | 8.2465 | 10.1955 | 7.7627 | 9.6268 | 13.1822 | 10.432 | 10.1561 | 11.6143 | 8.1718 | 9.6723 | 12.8162 | 8.0831 | 10.4319 | 9.7457 | 9.8804 | 8.5101 | 10.3346 | -0.074163 | 20.9517 | 0.032414 | 0.04774 | -38.0872 | 3.1214 | -0.67 | 0.25 | 0.2661 | -0.12625 | 0.44382 | -0.37897 | -0.54128 | -0.47737 | 0.60437 | 0.41985 | 0.41609 | 0.42309 | 0.41265 | 0.62258 | 0.43283 | 0.41938
42810.434 | -522 | 18.5457 | 18.6387 | 18.6335 | 18.6405 | 17.9992 | 16.6612 | 14.7368 | 16.7443 | 17.227 | 17.3296 | 17.334 | 16.8925 | 15.942 | 14.5472 | 15.0154 | 15.0308 | 15.5834 | 13.4478 | 13.5515 | 14.1418 |  |  |  | 16.6455 | 15.9864 | 15.1108 | 10.3174 | 9.782 | 10.0783 | 17.2541 | 16.4094 | 15.2198 | 16.933 | 16.2158 | 15.2304 | 10.8386 | 11.6736 |  | 12.3059 | 10.6214 | 10.4029 | 8.5321 |  | 6.3865 | 6.3779 | 5.8521 | 5.9071 | 5.9076 | 6.1091 | 6.6934 | 4.8145 | 6.5002 | 4.8327 | 6.7013 | 8.1393 | 43.0192 | 47.4019 | 43.5922 | 15.1417 |  |  | 0.003503 | -0.049197 | 0.12933 | -0.12814 | 0.008048 | -0.21731 | 0.39746 | -0.044192 | -0.4464 | 0.19914 | -0.2459 | 8.8797 | 8.8813 | 2.0087 | 15.8327 | 16.758 | 17.3068 | 17.6397 | 17.6069 | 16.5999 | 14.9537 | 16.8969 | 17.2256 | 17.5198 | 17.5521 | 17.3065 | 16.5224 | 14.7566 | 6.1149 | 8.3105 | 5.2491 | 5.6924 | 5.7921 | 6.6933 | 7.6939 | 15.8776 | 15.5547 | 15.4245 | 14.377 | 14.2549 | 14.2073 |  |  |  | 10.7452 | 9.3179 | 8.9723 | 8.898 | -0.1051 | -0.0012926 | 12.7462 |  |  | 10.6771 |  |  | 16.9543 | 16.1464 | 15.1341 | 16.4425 | 15.726 | 14.8426 | 10.702 | 10.6679 | 11.4763 | 11.4508 | 8.8677 |  | 10.6939 | 8.2686 | 10.0457 | 9.2471 | 11.1422 | 12.2461 |  | 12.3634 |  |  | 11.7173 | 12.5643 | 12.5453 | [6 empty] | 12.5748 |  |  | 11.2898 |  |  | 8.9631 | 10.1744 | 12.0523 | 7.4197 | 9.1234 | 12.5681 | 7.6687 | 9.4891 | 12.3761 | 9.2699 | 10.4521 | 7.7424 | 10.4561 | 8.2437 | 10.2049 | 7.776 | 9.6129 | 13.1837 | 10.4408 | 10.1528 | 11.6263 | 8.1666 | 9.6813 | 12.8154 | 8.0838 | 10.4422 | 9.7543 | 9.8862 | 8.5155 | 10.3324 | 0.052182 | 20.9529 | 0.032793 | 0.048869 | -38.0395 | 3.1214 | -0.51 | 0.32 | 0.069415 | -0.25843 | 0.41902 | -0.41708 | 0.10448 | -0.54289 | 0.7342 | 0.41877 | 0.41406 | 0.42302 | 0.41199 | 0.62438 | 0.43286 | 0.41962
42810.434 | -521 | 18.5503 | 18.6424 | 18.6343 | 18.6405 | 18.0038 | 16.666 | 14.7415 | 16.7406 | 17.2318 | 17.3277 | 17.3423 | 16.8993 | 15.9452 | 14.5505 | 15.0213 | 15.036 | 15.591 | 13.4486 | 13.5513 | 14.1455 |  |  |  | 16.6552 | 15.992 | 15.1189 | 10.331 | 9.7921 | 10.0973 | 17.2536 | 16.4113 | 15.2161 | 16.9315 | 16.2134 | 15.2319 | 10.8397 | 11.6339 |  | 12.2986 | 10.6128 | 10.4001 | 8.513 |  | 6.3885 | 6.3784 | 5.8439 | 5.8999 | 5.8911 | 6.0937 | 6.673 | 4.8476 | 6.496 | 4.7734 | 6.6938 | 8.1425 | 43.0249 | 47.3912 | 43.5991 | 15.1328 |  |  | 0.086303 | -0.11228 | 0.011708 | -0.068998 | -0.078688 | -0.35924 | 0.42703 | 0.10235 | -0.54973 | 0.19431 | -0.40883 | 8.8738 | 8.8753 | 2.0083 | 15.8303 | 16.7549 | 17.3092 | 17.6427 | 17.6066 | 16.605 | 14.9586 | 16.8999 | 17.2289 | 17.516 | 17.5603 | 17.3019 | 16.5246 | 14.7549 | 6.0982 | 8.296 | 5.2186 | 5.7952 | 5.7845 | 6.6901 | 7.6946 | 15.8766 | 15.548 | 15.4239 | 14.3731 | 14.255 | 14.2019 |  |  |  | 10.7416 | 9.3213 | 8.9726 | 8.8787 | -0.03885 | -0.034792 | 12.7424 |  |  | 10.6746 |  |  | 16.9459 | 16.1517 | 15.1326 | 16.4352 | 15.7251 | 14.8418 | 10.7071 | 10.6656 | 11.4759 | 11.4548 | 8.8535 |  | 10.6784 | 8.3127 | 10.036 | 9.2546 | 11.1288 | 12.2322 |  | 12.3539 |  |  | 11.7319 | 12.5591 | 12.5516 | [6 empty] | 12.5837 |  |  | 11.2881 |  |  | 8.9663 | 10.17 | 12.0494 | 7.4269 | 9.1206 | 12.5771 | 7.6709 | 9.4859 | 12.3677 | 9.2626 | 10.4482 | 7.7412 | 10.4564 | 8.2366 | 10.2062 | 7.797 | 9.5951 | 13.1841 | 10.4396 | 10.1529 | 11.638 | 8.166 | 9.6823 | 12.8076 | 8.0788 | 10.4366 | 9.7606 | 9.8953 | 8.5175 | 10.3282 | -0.087453 | 20.9527 | 0.032988 | 0.049998 | -38.1151 | 3.1213 | -0.43 | 0.26 | 0.34456 | -0.39041 | 0.12607 | -0.30605 | -0.32667 | -0.698 | 0.761 | 0.41866 | 0.41251 | 0.42237 | 0.41349 | 0.62784 | 0.43343 | 0.42004
42810.434 | -520 | 18.5441 | 18.6443 | 18.6277 | 18.6352 | 17.9941 | 16.6504 | 14.7418 | 16.7371 | 17.2279 | 17.3232 | 17.3377 | 16.8984 | 15.936 | 14.5429 | 15.0169 | 15.0308 | 15.5869 | 13.4355 | 13.5524 | 14.1368 |  |  |  | 16.6483 | 15.9849 | 15.1135 | 10.3203 | 9.7927 | 10.0971 | 17.2509 | 16.4146 | 15.2204 | 16.937 | 16.2159 | 15.239 | 10.8395 | 11.5996 |  | 12.2963 | 10.6158 | 10.4003 | 8.4898 |  | 6.3908 | 6.374 | 5.8331 | 5.8802 | 5.8782 | 6.0932 | 6.6627 | 4.9222 | 6.4995 | 4.7401 | 6.6948 | 8.1364 | 43.0341 | 47.3712 | 43.599 | 15.1251 |  |  | -0.037237 | -0.074165 | 0.12736 | -0.06111 | -0.037292 | 0.030424 | 0.46185 | -0.019876 | -0.057392 | -0.74979 | -0.57574 | 8.8759 | 8.8769 | 2.0085 | 15.8164 | 16.7461 | 17.2992 | 17.6295 | 17.5942 | 16.591 | 14.9481 | 16.8916 | 17.2145 | 17.5108 | 17.5511 | 17.2928 | 16.5114 | 14.7484 | 6.1027 | 8.3117 | 5.2142 | 5.7719 | 5.8269 | 6.6944 | 7.6955 | 15.8753 | 15.5477 | 15.4296 | 14.3722 | 14.2602 | 14.1985 |  |  |  | 10.7507 | 9.3293 | 8.9685 | 8.8621 | 0.097297 | -0.10725 | 12.7394 |  |  | 10.6774 |  |  | 16.9471 | 16.1467 | 15.1362 | 16.437 | 15.7249 | 14.8407 | 10.71 | 10.6663 | 11.4715 | 11.4603 | 8.7986 |  | 10.6867 | 8.352 | 10.0388 | 9.2688 | 11.1339 | 12.2264 |  | 12.3541 |  |  | 11.7388 | 12.575 | 12.559 | [6 empty] | 12.5967 |  |  | 11.2912 |  |  | 8.9638 | 10.1688 | 12.056 | 7.4438 | 9.1266 | 12.5749 | 7.6645 | 9.4805 | 12.3625 | 9.2583 | 10.4363 | 7.7551 | 10.4451 | 8.2228 | 10.2042 | 7.8157 | 9.5939 | 13.1756 | 10.4347 | 10.1492 | 11.6393 | 8.1641 | 9.6786 | 12.806 | 8.079 | 10.4244 | 9.7635 | 9.888 | 8.5199 | 10.3202 | -0.093808 | 20.9529 | 0.033843 | 0.051084 | -37.9678 | 3.1213 | -0.68 | 0.24 | -0.22633 | -0.3173 | 0.41581 | -0.28803 | -0.22489 | 0.20313 | 0.79142 | 0.42046 | 0.41152 | 0.42214 | 0.41348 | 0.62844 | 0.43407 | 0.4208
42810.434 | -519 | 18.5478 | 18.6498 | 18.646 | 18.6443 | 17.9981 | 16.6557 | 14.7387 | 16.7479 | 17.2378 | 17.3303 | 17.3402 | 16.8937 | 15.9416 | 14.5456 | 15.0112 | 15.039 | 15.5906 | 13.4473 | 13.5544 | 14.1358 |  |  |  | 16.6487 | 15.9797 | 15.1112 | 10.3272 | 9.7845 | 10.0955 | 17.2511 | 16.4071 | 15.2187 | 16.9289 | 16.2192 | 15.2368 | 10.8345 | 11.5487 |  | 12.2957 | 10.6056 | 10.3997 | 8.4558 |  | 6.3839 | 6.3685 | 5.8191 | 5.8713 | 5.8583 | 6.086 | 6.666 | 5.0371 | 6.4926 | 4.7369 | 6.6945 | 8.1354 | 43.041 | 47.3662 | 43.608 | 15.1315 |  |  | 0.10667 | -0.009113 | 0.19636 | 0.05257 | -0.041236 | 0.069852 | 0.57159 | -0.16707 | -0.85661 | -0.13046 | -0.48474 | 8.8751 | 8.876 | 2.0086 | 15.8179 | 16.7474 | 17.3014 | 17.6255 | 17.6005 | 16.5869 | 14.9461 | 16.8845 | 17.2197 | 17.5117 | 17.5561 | 17.2929 | 16.5131 | 14.7489 | 6.1468 | 8.3575 | 5.2247 | 5.7425 | 5.8564 | 6.6965 | 7.7017 | 15.8762 | 15.5547 | 15.4384 | 14.3718 | 14.2739 | 14.2027 |  |  |  | 10.7476 | 9.3428 | 8.9824 | 8.8676 | 0.14065 | 0.012446 | 12.7377 |  |  | 10.6772 |  |  | 16.9474 | 16.143 | 15.1379 | 16.4365 | 15.7209 | 14.839 | 10.7144 | 10.6625 | 11.4694 | 11.465 | 8.7626 |  | 10.6837 | 8.3417 | 10.0428 | 9.28 | 11.1281 | 12.2161 |  | 12.3635 |  |  | 11.7371 | 12.5787 | 12.5481 | [6 empty] | 12.6126 |  |  | 11.3048 |  |  | 8.972 | 10.1771 | 12.0577 | 7.4296 | 9.1248 | 12.5754 | 7.6696 | 9.4851 | 12.3711 | 9.2576 | 10.443 | 7.7201 | 10.4379 | 8.2299 | 10.2102 | 7.8279 | 9.5982 | 13.1679 | 10.437 | 10.1545 | 11.6392 | 8.1628 | 9.6892 | 12.8037 | 8.0719 | 10.4005 | 9.7455 | 9.8858 | 8.5305 | 10.3121 | -0.15737 | 20.9534 | 0.033975 | 0.051735 | -38.0762 | 3.1214 | -0.7 | 0.28 | 0.38306 | -0.11123 | 0.51629 | 0.26714 | -0.23648 | 0.30778 | 0.88043 | 0.42136 | 0.41194 | 0.42164 | 0.40883 | 0.62798 | 0.43485 | 0.42054
42810.434 | -518 | 18.5553 | 18.6469 | 18.6452 | 18.646 | 18.0033 | 16.6653 | 14.7487 | 16.7549 | 17.241 | 17.3356 | 17.3379 | 16.9013 | 15.9496 | 14.5529 | 15.0122 | 15.0346 | 15.585 | 13.4396 | 13.5538 | 14.134 |  |  |  | 16.6456 | 15.986 | 15.1065 | 10.3276 | 9.7779 | 10.0963 | 17.2515 | 16.4034 | 15.2195 | 16.9293 | 16.2104 | 15.2301 | 10.8354 | 11.5102 |  | 12.2944 | 10.5988 | 10.3982 | 8.4429 |  | 6.3837 | 6.3666 | 5.8058 | 5.8636 | 5.8536 | 6.0784 | 6.6986 | 5.0594 | 6.4993 | 4.7048 | 6.6973 | 8.1433 | 43.0513 | 47.3704 | 43.6173 | 15.1513 |  |  | 0.080387 | -0.058397 | 0.12342 | 0.090682 | 0.1099 | -0.32902 | 0.40928 | -0.20913 | 0.29133 | -0.17829 | -0.45533 | 8.8801 | 8.8815 | 2.0083 | 15.822 | 16.7477 | 17.2986 | 17.6264 | 17.6033 | 16.5886 | 14.9418 | 16.887 | 17.2192 | 17.5061 | 17.5523 | 17.2954 | 16.5152 | 14.7466 | 6.1554 | 8.3428 | 5.2267 | 5.77 | 5.8967 | 6.6954 | 7.6972 | 15.8658 | 15.5507 | 15.4249 | 14.3752 | 14.2589 | 14.1937 |  |  |  | 10.7419 | 9.3412 | 8.9685 | 8.8397 | 0.018485 | 0.16376 | 12.7406 |  |  | 10.6738 |  |  | 16.945 | 16.1451 | 15.1347 | 16.4302 | 15.7195 | 14.8428 | 10.7227 | 10.6581 | 11.4742 | 11.4719 | 8.7732 |  | 10.6767 | 8.2778 | 10.037 | 9.2873 | 11.1357 | 12.2018 |  | 12.3656 |  |  | 11.726 | 12.5652 | 12.5525 | [6 empty] | 12.6181 |  |  | 11.3013 |  |  | 8.972 | 10.1825 | 12.0475 | 7.3722 | 9.0491 | 12.5617 | 7.663 | 9.4798 | 12.3615 | 9.2478 | 10.4321 | 7.6696 | 10.4029 | 8.2114 | 10.195 | 7.8466 | 9.5881 | 13.1538 | 10.4434 | 10.1513 | 11.6405 | 8.162 | 9.6923 | 12.8133 | 8.071 | 10.3919 | 9.7488 | 9.8916 | 8.5285 | 10.3112 | -0.13637 | 20.9524 | 0.033493 | 0.051453 | -38.0512 | 3.1214 | -0.6 | 0.33 | 0.33254 | -0.28156 | 0.40931 | 0.35086 | 0.38606 | -0.66797 | 0.74501 | 0.42083 | 0.41352 | 0.42169 | 0.40773 | 0.62725 | 0.43524 | 0.42113
42810.4341 | -517 | 18.5413 | 18.6411 | 18.6279 | 18.6328 | 17.9909 | 16.6604 | 14.7349 | 16.7408 | 17.2187 | 17.3185 | 17.3326 | 16.8913 | 15.94 | 14.5383 | 15.0027 | 15.0203 | 15.5802 | 13.4341 | 13.5519 | 14.1318 |  |  |  | 16.6431 | 15.9852 | 15.1085 | 10.3256 | 9.7693 | 10.119 | 17.2439 | 16.406 | 15.2132 | 16.9341 | 16.2135 | 15.2326 | 10.8344 | 11.4882 |  | 12.2977 | 10.5962 | 10.4119 | 8.4314 |  | 6.3793 | 6.3574 | 5.8059 | 5.8584 | 5.8529 | 6.0616 | 6.6813 | 5.0528 | 6.4949 | 4.6633 | 6.6894 | 8.1391 | 43.0626 | 47.3694 | 43.6241 | 15.1775 |  |  | 0.19933 | -0.088621 | -0.042832 | 0.007886 | 0.17562 | 0.04488 | 0.40731 | -0.33004 | -0.042018 | -0.5853 | -0.48076 | 8.8776 | 8.8788 | 2.0088 | 15.8218 | 16.7513 | 17.3048 | 17.6338 | 17.6065 | 16.5974 | 14.9588 | 16.8989 | 17.2283 | 17.512 | 17.5498 | 17.3021 | 16.523 | 14.7577 | 6.1541 | 8.3835 | 5.2328 | 5.7203 | 5.8893 | 6.6948 | 7.7025 | 15.8706 | 15.5461 | 15.4227 | 14.3674 | 14.2545 | 14.1959 |  |  |  | 10.7424 | 9.3583 | 8.9652 | 8.8422 | 0.010381 | -0.022371 | 12.7341 |  |  | 10.6655 |  |  | 16.9441 | 16.1415 | 15.1312 | 16.4323 | 15.7167 | 14.8389 | 10.7237 | 10.6524 | 11.4743 | 11.4672 | 8.8352 |  | 10.6821 | 8.2089 | 10.0401 | 9.3089 | 11.1368 | 12.2085 |  | 12.3643 |  |  | 11.6983 | 12.5778 | 12.5578 | [6 empty] | 12.6258 |  |  | 11.3078 |  |  | 8.9711 | 10.1776 | 12.0413 | 7.3633 | 9.0031 | 12.5612 | 7.6758 | 9.4738 | 12.339 | 9.2525 | 10.4407 | 7.6629 | 10.3904 | 8.2197 | 10.1881 | 7.8567 | 9.5598 | 13.1453 | 10.4395 | 10.1486 | 11.6394 | 8.1562 | 9.6962 | 12.8121 | 8.0809 | 10.3677 | 9.7586 | 9.8919 | 8.5259 | 10.3077 | -0.15929 | 20.9522 | 0.033866 | 0.051844 | -38.0541 | 3.1213 | -0.69 | 0.25 | 0.52366 | -0.34684 | -0.24113 | 0.10346 | 0.488 | 0.24669 | 0.74319 | 0.41929 | 0.41553 | 0.42112 | 0.40782 | 0.62719 | 0.43552 | 0.42108
42810.4341 | -516 | 18.5485 | 18.6476 | 18.6279 | 18.6393 | 17.9955 | 16.6599 | 14.7375 | 16.7397 | 17.2192 | 17.3235 | 17.3437 | 16.8908 | 15.9325 | 14.5453 | 15.0053 | 15.031 | 15.5896 | 13.4374 | 13.5496 | 14.1353 |  |  |  | 16.6467 | 15.9831 | 15.1075 | 10.3312 | 9.7735 | 10.1231 | 17.236 | 16.3992 | 15.2135 | 16.9271 | 16.2093 | 15.2258 | 10.8315 | 11.4588 |  | 12.2919 | 10.5857 | 10.4125 | 8.4193 |  | 6.3819 | 6.3519 | 5.7993 | 5.8547 | 5.8532 | 6.0685 | 6.6805 | 5.0097 | 6.5023 | 4.6272 | 6.6943 | 8.133 | 43.0693 | 47.3802 | 43.6151 | 15.2067 |  |  | -0.067465 | -0.33044 | 0.1221 | -0.068998 | 0.079676 | -0.19956 | 0.61956 | -0.23936 | -0.21366 | -0.74622 | -0.46904 | 8.8751 | 8.8763 | 2.0082 | 15.8105 | 16.7517 | 17.3068 | 17.6304 | 17.5998 | 16.5928 | 14.9473 | 16.8974 | 17.2193 | 17.5049 | 17.555 | 17.2984 | 16.5203 | 14.7499 | 6.1047 | 8.4014 | 5.2611 | 5.733 | 5.8281 | 6.7071 | 7.7198 | 15.87 | 15.5359 | 15.4191 | 14.3612 | 14.2519 | 14.1982 |  |  |  | 10.7429 | 9.3585 | 8.9681 | 8.8429 | 0.05779 | -0.01616 | 12.7324 |  |  | 10.6622 |  |  | 16.94 | 16.1373 | 15.1324 | 16.4348 | 15.7212 | 14.8394 | 10.732 | 10.649 | 11.4829 | 11.4672 | 8.8964 |  | 10.6824 | 8.1611 | 10.0403 | 9.3064 | 11.1381 | 12.2101 |  | 12.368 |  |  | 11.6612 | 12.569 | 12.5458 | [6 empty] | 12.6135 |  |  | 11.2949 |  |  | 8.975 | 10.17 | 12.0407 | 7.3448 | 8.9633 | 12.5437 | 7.6738 | 9.4809 | 12.3457 | 9.2602 | 10.4549 | 7.6482 | 10.3924 | 8.2266 | 10.1971 | 7.8774 | 9.5659 | 13.1483 | 10.4509 | 10.15 | 11.6461 | 8.1754 | 9.7181 | 12.8169 | 8.0876 | 10.3762 | 9.7589 | 9.8936 | 8.5383 | 10.3087 | -0.19049 | 20.9527 | 0.033166 | 0.050324 | -38.0401 | 3.1213 | -0.61 | 0.35 | -0.30466 | -0.66974 | 0.40712 | -0.30604 | 0.3287 | -0.52021 | 0.9166 | 0.4176 | 0.41687 | 0.42123 | 0.41474 | 0.62605 | 0.43577 | 0.42108
42810.4341 | -515 | 18.5371 | 18.6375 | 18.6238 | 18.6355 | 17.9913 | 16.6539 | 14.7329 | 16.7386 | 17.2197 | 17.3231 | 17.3369 | 16.8908 | 15.9325 | 14.5491 | 15.0109 | 15.03 | 15.5935 | 13.4387 | 13.5542 | 14.1383 |  |  |  | 16.6424 | 15.988 | 15.1044 | 10.3364 | 9.7642 | 10.0876 | 17.2388 | 16.3985 | 15.2157 | 16.9268 | 16.2025 | 15.2254 | 10.8323 | 11.4287 |  | 12.2863 | 10.5777 | 10.4194 | 8.4268 |  | 6.3806 | 6.3529 | 5.7946 | 5.8515 | 5.8485 | 6.0678 | 6.6766 | 4.9893 | 6.5072 | 4.6102 | 6.6914 | 8.131 | 43.0657 | 47.3956 | 43.6118 | 15.2313 |  |  | 0.049503 | -0.077453 | 0.065592 | 0.063742 | -0.015608 | -0.26134 | 0.40797 | -0.20387 | -0.63496 | -0.38893 | -0.57316 | 8.8775 | 8.8791 | 2.0086 | 15.8205 | 16.7612 | 17.3125 | 17.6423 | 17.6112 | 16.6036 | 14.9674 | 16.9003 | 17.2368 | 17.5232 | 17.5679 | 17.3226 | 16.5339 | 14.7676 | 6.0139 | 8.3426 | 5.2668 | 5.6735 | 5.7846 | 6.6975 | 7.7079 | 15.8672 | 15.5391 | 15.4228 | 14.3718 | 14.2526 | 14.1984 |  |  |  | 10.7427 | 9.3647 | 8.9686 | 8.8359 | 0.019701 | 0.14701 | 12.7366 |  |  | 10.6717 |  |  | 16.9491 | 16.1432 | 15.1343 | 16.4443 | 15.7307 | 14.8441 | 10.7416 | 10.6517 | 11.4992 | 11.4828 | 8.9404 |  | 10.6835 | 8.1227 | 10.0455 | 9.2938 | 11.1496 | 12.2189 |  | 12.3649 |  |  | 11.6733 | 12.5768 | 12.533 | [6 empty] | 12.632 |  |  | 11.2975 |  |  | 8.9794 | 10.1769 | 12.0332 | 7.3246 | 8.9403 | 12.5624 | 7.6839 | 9.4863 | 12.3208 | 9.2503 | 10.4477 | 7.6474 | 10.3852 | 8.211 | 10.1959 | 7.8757 | 9.5751 | 13.1315 | 10.4448 | 10.1468 | 11.636 | 8.1814 | 9.7233 | 12.8064 | 8.0992 | 10.3653 | 9.7572 | 9.8934 | 8.5412 | 10.3068 | -0.052592 | 20.9524 | 0.034411 | 0.051243 | -38.0904 | 3.1213 | -0.64 | 0.36 | 0.26095 | -0.32425 | 0.29839 | 0.29415 | -0.14548 | -0.5953 | 0.74379 | 0.41641 | 0.41811 | 0.42196 | 0.42371 | 0.62403 | 0.43558 | 0.42127
42810.4341 | -514 | 18.5424 | 18.6378 | 18.628 | 18.6357 | 17.9985 | 16.6591 | 14.7374 | 16.7449 | 17.2223 | 17.321 | 17.3334 | 16.8937 | 15.9333 | 14.5455 | 15.0021 | 15.0183 | 15.5809 | 13.4225 | 13.5431 | 14.1247 |  |  |  | 16.6406 | 15.9816 | 15.0985 | 10.321 | 9.7515 | 10.0697 | 17.2448 | 16.4052 | 15.2134 | 16.9343 | 16.2142 | 15.2406 | 10.8413 | 11.3969 |  | 12.2883 | 10.5839 | 10.4312 | 8.422 |  | 6.3622 | 6.3425 | 5.7799 | 5.8425 | 5.8411 | 6.0544 | 6.644 | 4.8939 | 6.502 | 4.5781 | 6.69 | 8.1304 | 43.072 | 47.4077 | 43.6149 | 15.2695 |  |  | 0.1093 | -0.099137 | 0.14116 | 0.049942 | 0.083616 | -0.0872 | 0.38628 | -0.23081 | -0.52151 | -0.39313 | -0.43625 | 8.8746 | 8.8757 | 2.0087 | 15.8075 | 16.7486 | 17.3009 | 17.6332 | 17.602 | 16.5947 | 14.9534 | 16.8917 | 17.23 | 17.5133 | 17.5599 | 17.31 | 16.523 | 14.7624 | 5.9656 | 8.3153 | 5.2538 | 5.6299 | 5.785 | 6.6951 | 7.7114 | 15.8637 | 15.542 | 15.4227 | 14.3646 | 14.2598 | 14.2008 |  |  |  | 10.7363 | 9.3722 | 8.9772 | 8.8251 | -0.0009642 | 0.14946 | 12.7442 |  |  | 10.6692 |  |  | 16.9517 | 16.1482 | 15.1333 | 16.4388 | 15.7333 | 14.8432 | 10.7424 | 10.6531 | 11.5057 | 11.4941 | 8.9603 |  | 10.6791 | 8.0739 | 10.0405 | 9.2861 | 11.1466 | 12.213 |  | 12.3629 |  |  | 11.6681 | 12.5782 | 12.5427 | [6 empty] | 12.6405 |  |  | 11.2911 |  |  | 8.9926 | 10.1803 | 12.0344 | 7.3217 | 8.9506 | 12.5755 | 7.6961 | 9.5021 | 12.3113 | 9.2523 | 10.4589 | 7.6471 | 10.3964 | 8.2212 | 10.1962 | 7.8846 | 9.5743 | 13.1346 | 10.4463 | 10.1519 | 11.6371 | 8.1836 | 9.7277 | 12.8022 | 8.1157 | 10.3783 | 9.7649 | 9.8909 | 8.5405 | 10.3014 | -0.017731 | 20.9516 | 0.034325 | 0.051236 | -38.1142 | 3.1213 | -0.68 | 0.4 | 0.38774 | -0.36683 | 0.43773 | 0.26037 | 0.33672 | -0.34386 | 0.72374 | 0.41571 | 0.4193 | 0.42208 | 0.4288 | 0.62589 | 0.43601 | 0.42136
42810.4341 | -513 | 18.5436 | 18.6368 | 18.6261 | 18.6286 | 17.9935 | 16.6581 | 14.7327 | 16.741 | 17.221 | 17.3103 | 17.3397 | 16.8894 | 15.9349 | 14.542 | 15.0039 | 15.0284 | 15.596 | 13.4374 | 13.556 | 14.1289 |  |  |  | 16.646 | 15.9975 | 15.1109 | 10.3351 | 9.7545 | 10.0693 | 17.2456 | 16.4119 | 15.2193 | 16.9293 | 16.2133 | 15.2374 | 10.8334 | 11.3793 |  | 12.2855 | 10.5816 | 10.4319 | 8.3912 |  | 6.3687 | 6.3425 | 5.7919 | 5.863 | 5.8551 | 6.0606 | 6.6299 | 4.8491 | 6.5092 | 4.597 | 6.6963 | 8.1349 | 43.0764 | 47.3919 | 43.6196 | 15.2919 |  |  | -0.000437 | -0.16222 | 0.092532 | -0.090682 | -0.097088 | -0.15422 | 0.50851 | -0.26367 | -0.88931 | -0.48082 | -0.42393 | 8.8793 | 8.8806 | 2.0083 | 15.8102 | 16.753 | 17.3075 | 17.6336 | 17.607 | 16.5932 | 14.9554 | 16.9016 | 17.2301 | 17.5169 | 17.5656 | 17.315 | 16.5264 | 14.7642 | 5.9494 | 8.3319 | 5.2423 | 5.5963 | 5.7873 | 6.6919 | 7.7038 | 15.8589 | 15.5374 | 15.415 | 14.3572 | 14.2502 | 14.1932 |  |  |  | 10.7343 | 9.3735 | 8.9661 | 8.8147 | 0.016459 | 0.13835 | 12.7393 |  |  | 10.6737 |  |  | 16.946 | 16.1544 | 15.1331 | 16.4403 | 15.7282 | 14.8387 | 10.7379 | 10.6563 | 11.5064 | 11.4933 | 8.9939 |  | 10.6754 | 8.0739 | 10.0425 | 9.271 | 11.1444 | 12.1985 |  | 12.3697 |  |  | 11.6653 | 12.5924 | 12.5414 | [6 empty] | 12.6302 |  |  | 11.2891 |  |  | 9.0065 | 10.1732 | 12.029 | 7.3395 | 8.9613 | 12.5836 | 7.6975 | 9.4965 | 12.31 | 9.2464 | 10.451 | 7.6654 | 10.4128 | 8.227 | 10.1741 | 7.8994 | 9.585 | 13.1304 | 10.4349 | 10.1468 | 11.6307 | 8.186 | 9.727 | 12.7892 | 8.1216 | 10.3773 | 9.7599 | 9.8907 | 8.5295 | 10.303 | -0.0061754 | 20.9518 | 0.034595 | 0.05256 | -38.1156 | 3.1214 | -0.36 | 0.28 | -0.024517 | -0.46925 | 0.3544 | -0.35084 | -0.36284 | -0.45731 | 0.83039 | 0.41466 | 0.41936 | 0.42243 | 0.43022 | 0.62628 | 0.43661 | 0.42158
42810.4341 | -512 | 18.5341 | 18.6388 | 18.6286 | 18.6256 | 17.9964 | 16.6597 | 14.73 | 16.7389 | 17.2202 | 17.3217 | 17.3321 | 16.8937 | 15.9316 | 14.5368 | 15.0064 | 15.0286 | 15.5934 | 13.4363 | 13.555 | 14.1286 |  |  |  | 16.6418 | 15.9905 | 15.1088 | 10.3327 | 9.7414 | 10.0575 | 17.2459 | 16.4039 | 15.2118 | 16.9278 | 16.2074 | 15.2363 | 10.8382 | 11.3442 |  | 12.2898 | 10.5662 | 10.4224 | 8.3774 |  | 6.351 | 6.3359 | 5.7771 | 5.8505 | 5.8518 | 6.0517 | 6.6038 | 4.8471 | 6.5066 | 4.6191 | 6.6905 | 8.1293 | 43.0786 | 47.3869 | 43.6202 | 15.3085 |  |  | 0.084331 | -0.070881 | 0.06362 | -0.073598 | 0.080988 | -0.29288 | 0.33437 | -0.29784 | -0.42343 | -0.40068 | -0.44877 | 8.8782 | 8.8797 | 2.0088 | 15.8132 | 16.7578 | 17.3138 | 17.637 | 17.6088 | 16.6025 | 14.9579 | 16.9048 | 17.234 | 17.5199 | 17.5683 | 17.3156 | 16.5308 | 14.7658 | 5.9509 | 8.364 | 5.2575 | 5.6031 | 5.8336 | 6.692 | 7.7163 | 15.8564 | 15.5345 | 15.4149 | 14.3625 | 14.247 | 14.1917 |  |  |  | 10.7399 | 9.3701 | 8.9599 | 8.8201 | 0.047862 | 0.13082 | 12.7398 |  |  | 10.666 |  |  | 16.942 | 16.1445 | 15.1317 | 16.4364 | 15.7273 | 14.8432 | 10.7407 | 10.6589 | 11.5175 | 11.4875 | 9.0304 |  | 10.6745 | 8.0768 | 10.0365 | 9.2817 | 11.1396 | 12.1935 |  | 12.3615 |  |  | 11.6647 | 12.5899 | 12.5425 | [6 empty] | 12.6309 |  |  | 11.3041 |  |  | 9.0127 | 10.18 | 12.0263 | 7.3494 | 8.9755 | 12.5896 | 7.7048 | 9.4975 | 12.303 | 9.2508 | 10.4537 | 7.6809 | 10.4294 | 8.2433 | 10.1771 | 7.9077 | 9.5987 | 13.1376 | 10.447 | 10.1502 | 11.6294 | 8.1942 | 9.7317 | 12.776 | 8.1326 | 10.3858 | 9.7674 | 9.8913 | 8.5412 | 10.3054 | 0.05276 | 20.9514 | 0.03343 | 0.050368 | -38.0822 | 3.1214 | -0.08 | 0.29 | 0.34058 | -0.31018 | 0.29386 | -0.31607 | 0.33139 | -0.63018 | 0.67335 | 0.41362 | 0.41908 | 0.42197 | 0.43007 | 0.62605 | 0.43715 | 0.42161
42810.4341 | -511 | 18.5282 | 18.6254 | 18.6224 | 18.6233 | 17.9864 | 16.6519 | 14.7291 | 16.7391 | 17.218 | 17.3194 | 17.3267 | 16.8838 | 15.9338 | 14.5347 | 15.0068 | 15.0223 | 15.5834 | 13.4326 | 13.5563 | 14.1235 |  |  |  | 16.6393 | 15.9842 | 15.0985 | 10.3255 | 9.7364 | 10.025 | 17.2304 | 16.3914 | 15.2118 | 16.9173 | 16.212 | 15.2236 | 10.8345 | 11.3198 |  | 12.2868 | 10.5599 | 10.4124 | 8.3606 |  | 6.3546 | 6.344 | 5.7843 | 5.8596 | 5.8529 | 6.0458 | 6.5834 | 4.7998 | 6.5141 | 4.6267 | 6.7046 | 8.124 | 43.0718 | 47.3927 | 43.6253 | 15.3289 |  |  | 0.13164 | -0.059053 | -0.005376 | 0.13799 | -0.020864 | -0.17262 | 0.3738 | -0.17036 | -0.62329 | -1.2107 | -0.45136 | 8.8815 | 8.8826 | 2.0083 | 15.7977 | 16.7413 | 17.3023 | 17.6201 | 17.5956 | 16.5898 | 14.9448 | 16.8936 | 17.217 | 17.5102 | 17.5578 | 17.2973 | 16.5205 | 14.7522 | 5.9624 | 8.3587 | 5.2562 | 5.6315 | 5.8814 | 6.6855 | 7.709 | 15.8561 | 15.5336 | 15.4158 | 14.3605 | 14.2479 | 14.1897 |  |  |  | 10.7357 | 9.367 | 8.9545 | 8.8204 | 0.027197 | 0.1216 | 12.7421 |  |  | 10.6604 |  |  | 16.9494 | 16.1542 | 15.1337 | 16.4361 | 15.7294 | 14.8496 | 10.7414 | 10.6585 | 11.5401 | 11.4921 | 9.0708 |  | 10.6813 | 8.1069 | 10.0445 | 9.297 | 11.1466 | 12.2449 |  | 12.366 |  |  | 11.6763 | 12.5884 | 12.551 | [6 empty] | 12.6386 |  |  | 11.3165 |  |  | 9.0161 | 10.1893 | 12.0235 | 7.3405 | 8.9885 | 12.5947 | 7.7001 | 9.4948 | 12.3044 | 9.2507 | 10.447 | 7.696 | 10.4392 | 8.2474 | 10.1742 | 7.902 | 9.6061 | 13.1418 | 10.4307 | 10.1469 | 11.6116 | 8.1878 | 9.7346 | 12.7626 | 8.1301 | 10.3944 | 9.7635 | 9.8943 | 8.5503 | 10.299 | 0.085887 | 20.9503 | 0.032477 | 0.049803 | -38.0706 | 3.1214 | 0.01 | 0.29 | 0.42549 | -0.28312 | -0.085425 | 0.4328 | -0.1682 | -0.48381 | 0.71194 | 0.41272 | 0.41851 | 0.42178 | 0.42805 | 0.62534 | 0.43749 | 0.42146
42810.4341 | -510 | 18.5282 | 18.643 | 18.6229 | 18.6316 | 17.9944 | 16.6573 | 14.7288 | 16.741 | 17.2225 | 17.3274 | 17.332 | 16.8858 | 15.9308 | 14.5452 | 15.0002 | 15.0207 | 15.5796 | 13.4363 | 13.5555 | 14.1285 |  |  |  | 16.6414 | 15.9867 | 15.1006 | 10.3203 | 9.7293 | 9.9973 | 17.242 | 16.3999 | 15.221 | 16.9255 | 16.2187 | 15.2332 | 10.8418 | 11.333 |  | 12.2818 | 10.5636 | 10.415 | 8.3615 |  | 6.3385 | 6.32 | 5.7809 | 5.8456 | 5.8378 | 6.036 | 6.5617 | 4.7285 | 6.5026 | 4.6128 | 6.6923 | 8.1266 | 43.0847 | 47.4007 | 43.6298 | 15.3538 |  |  | 0.080387 | -0.13725 | 0.025508 | 0.012486 | -0.172 | -0.52352 | 0.29298 | -0.029076 | -0.28099 | -0.23767 | -0.32955 | 8.8679 | 8.8693 | 2.0085 | 15.796 | 16.7394 | 17.2973 | 17.6247 | 17.5913 | 16.59 | 14.9428 | 16.8881 | 17.2206 | 17.5109 | 17.5438 | 17.2937 | 16.5137 | 14.7581 | 5.9758 | 8.3503 | 5.2232 | 5.6585 | 5.8945 | 6.6901 | 7.7195 | 15.848 | 15.5296 | 15.4114 | 14.3516 | 14.2361 | 14.1931 |  |  |  | 10.7323 | 9.3706 | 8.9529 | 8.82 | -0.032975 | -0.052671 | 12.7391 |  |  | 10.6523 |  |  | 16.9491 | 16.1442 | 15.1327 | 16.432 | 15.7229 | 14.8425 | 10.7222 | 10.6523 | 11.5473 | 11.4836 | 9.077 |  | 10.6761 | 8.1042 | 10.0371 | 9.3007 | 11.1357 | 12.269 |  | 12.3604 |  |  | 11.7038 | 12.5795 | 12.5532 | [6 empty] | 12.6477 |  |  | 11.3311 |  |  | 9.0201 | 10.1921 | 12.0214 | 7.3552 | 9.0125 | 12.6004 | 7.7073 | 9.4956 | 12.31 | 9.252 | 10.4498 | 7.7173 | 10.4531 | 8.2525 | 10.1736 | 7.8877 | 9.618 | 13.1464 | 10.4291 | 10.1512 | 11.6091 | 8.1881 | 9.7397 | 12.7544 | 8.1325 | 10.4035 | 9.762 | 9.8846 | 8.5563 | 10.3021 | 0.0065362 | 20.9502 | 0.03184 | 0.04845 | -38.1125 | 3.1214 | 0.08 | 0.34 | 0.33248 | -0.43161 | 0.18607 | 0.13018 | -0.48292 | -0.84252 | 0.63027 | 0.41237 | 0.41834 | 0.42132 | 0.42707 | 0.63023 | 0.43771 | 0.42136
42810.4341 | -509 | 18.5328 | 18.6413 | 18.631 | 18.6333 | 17.996 | 16.6583 | 14.732 | 16.7449 | 17.2302 | 17.3274 | 17.3367 | 16.8852 | 15.9359 | 14.5411 | 14.997 | 15.0208 | 15.5828 | 13.4412 | 13.5511 | 14.1312 |  |  |  | 16.6402 | 15.9857 | 15.1076 | 10.3184 | 9.7249 | 9.999 | 17.2375 | 16.4 | 15.212 | 16.9315 | 16.2139 | 15.2296 | 10.8371 | 11.3184 |  | 12.2838 | 10.5677 | 10.4167 | 8.373 |  | 6.3438 | 6.3257 | 5.7883 | 5.8574 | 5.8462 | 6.0355 | 6.5544 | 4.6563 | 6.5154 | 4.5511 | 6.6929 | 8.1237 | 43.1003 | 47.3909 | 43.6301 | 15.3718 |  |  | 0.12639 | -0.091253 | 0.05442 | -0.02037 | -0.00312 | -0.25805 | 0.3922 | 0.043204 | -1.1291 | -0.50243 | -0.47699 | 8.8691 | 8.8704 | 2.0086 | 15.7971 | 16.7341 | 17.292 | 17.6279 | 17.596 | 16.5963 | 14.9485 | 16.8895 | 17.2239 | 17.5149 | 17.5571 | 17.3051 | 16.5167 | 14.7617 | 5.9709 | 8.3324 | 5.1844 | 5.723 | 5.9086 | 6.6823 | 7.7161 | 15.8504 | 15.5246 | 15.4198 | 14.3517 | 14.2577 | 14.1951 |  |  |  | 10.7303 | 9.3711 | 8.959 | 8.817 | 0.089801 | 0.0706 | 12.7303 |  |  | 10.6512 |  |  | 16.9442 | 16.1399 | 15.1269 | 16.4297 | 15.7222 | 14.8365 | 10.7119 | 10.6453 | 11.5511 | 11.4811 | 9.0762 |  | 10.6777 | 8.1251 | 10.0431 | 9.3035 | 11.1362 | 12.3136 |  | 12.3624 |  |  | 11.735 | 12.5775 | 12.5499 | [6 empty] | 12.6358 |  |  | 11.3421 |  |  | 9.0197 | 10.2017 | 12.0276 | 7.375 | 9.0457 | 12.6118 | 7.7169 | 9.4954 | 12.3149 | 9.2494 | 10.4569 | 7.7282 | 10.4709 | 8.2544 | 10.1738 | 7.8766 | 9.6176 | 13.1419 | 10.4274 | 10.1486 | 11.6045 | 8.188 | 9.7356 | 12.7442 | 8.1307 | 10.4008 | 9.7635 | 9.8715 | 8.5531 | 10.2967 | -0.036028 | 20.9502 | 0.033774 | 0.049333 | -38.1764 | 3.1213 | 0.02 | 0.28 | 0.41689 | -0.35194 | 0.27178 | -0.16628 | -0.065042 | -0.59151 | 0.72923 | 0.41245 | 0.41796 | 0.42125 | 0.42673 | 0.63414 | 0.43724 | 0.42138
42810.4342 | -508 | 18.5288 | 18.6297 | 18.6222 | 18.6277 | 17.9898 | 16.6489 | 14.7266 | 16.737 | 17.2252 | 17.32 | 17.3302 | 16.8865 | 15.9309 | 14.5417 | 14.9971 | 15.0213 | 15.5849 | 13.4383 | 13.5526 | 14.127 |  |  |  | 16.6419 | 15.9817 | 15.1022 | 10.3201 | 9.7061 | 9.9761 | 17.2311 | 16.3987 | 15.2095 | 16.9266 | 16.2091 | 15.2263 | 10.8304 | 11.2926 |  | 12.2798 | 10.5739 | 10.4068 | 8.3641 |  | 6.3416 | 6.3317 | 5.7899 | 5.863 | 5.8453 | 6.04 | 6.5424 | 4.6147 | 6.5204 | 4.4801 | 6.6948 | 8.1268 | 43.1212 | 47.394 | 43.6309 | 15.3907 |  |  | -0.013581 | -0.080737 | -0.025092 | -0.15837 | -0.064892 | -0.03266 | 0.42703 | 0.020864 | -0.64645 | -0.79594 | -0.29359 | 8.8679 | 8.869 | 2.0082 | 15.799 | 16.7394 | 17.2963 | 17.6219 | 17.603 | 16.5953 | 14.9458 | 16.8929 | 17.2263 | 17.5132 | 17.5543 | 17.3072 | 16.522 | 14.7629 | 5.988 | 8.3423 | 5.16 | 5.8055 | 5.9294 | 6.6798 | 7.7213 | 15.8577 | 15.5361 | 15.4229 | 14.3556 | 14.2468 | 14.1967 |  |  |  | 10.7357 | 9.3782 | 8.9648 | 8.8122 | 0.042392 | -0.0061858 | 12.7315 |  |  | 10.6554 |  |  | 16.9433 | 16.1509 | 15.1298 | 16.4358 | 15.721 | 14.8382 | 10.7036 | 10.6497 | 11.5611 | 11.4971 | 9.0854 |  | 10.6777 | 8.0945 | 10.0368 | 9.3159 | 11.145 | 12.3469 |  | 12.3694 |  |  | 11.7701 | 12.5797 | 12.5579 | [6 empty] | 12.6246 |  |  | 11.354 |  |  | 9.021 | 10.1977 | 12.0255 | 7.3941 | 9.0597 | 12.6137 | 7.7095 | 9.4941 | 12.3081 | 9.248 | 10.4532 | 7.7431 | 10.4841 | 8.2517 | 10.171 | 7.8726 | 9.6239 | 13.1498 | 10.4232 | 10.1518 | 11.591 | 8.1912 | 9.7373 | 12.7316 | 8.1296 | 10.401 | 9.7574 | 9.8724 | 8.5515 | 10.2895 | -0.10093 | 20.9514 | 0.033705 | 0.049477 | -38.0504 | 3.1213 | 0.15 | 0.36 | -0.13665 | -0.33104 | -0.18455 | -0.46363 | -0.29663 | -0.21044 | 0.76093 | 0.41219 | 0.4186 | 0.4212 | 0.42454 | 0.63746 | 0.43726 | 0.42169
42810.4342 | -507 | 18.525 | 18.6255 | 18.6199 | 18.627 | 17.9877 | 16.6468 | 14.7259 | 16.7377 | 17.2153 | 17.3208 | 17.3262 | 16.8852 | 15.9253 | 14.5382 | 14.9923 | 15.0179 | 15.5763 | 13.4359 | 13.5526 | 14.1256 |  |  |  | 16.6378 | 15.9824 | 15.1017 | 10.3112 | 9.6993 | 9.9291 | 17.233 | 16.3988 | 15.2061 | 16.9243 | 16.2118 | 15.222 | 10.8286 | 11.2711 |  | 12.2729 | 10.577 | 10.4048 | 8.3459 |  | 6.3358 | 6.3237 | 5.7824 | 5.8546 | 5.8423 | 6.0325 | 6.5429 | 4.445 | 6.5149 | 4.388 | 6.6917 | 8.1261 | 43.1299 | 47.3944 | 43.6413 | 15.4007 |  |  | -0.029353 | -0.32387 | 0.26798 | -0.03877 | 0.019876 | -0.022144 | 0.49077 | -0.067188 | -0.48687 | -0.14703 | -0.21053 | 8.8684 | 8.8696 | 2.0088 | 15.797 | 16.742 | 17.2975 | 17.6239 | 17.6044 | 16.5937 | 14.9507 | 16.8934 | 17.2248 | 17.5064 | 17.5561 | 17.3031 | 16.5241 | 14.7524 | 6.0396 | 8.3612 | 5.1528 | 5.7563 | 5.8921 | 6.6813 | 7.7142 | 15.8503 | 15.5283 | 15.4159 | 14.3558 | 14.247 | 14.1943 |  |  |  | 10.7349 | 9.3725 | 8.9633 | 8.8079 | 0.084533 | 0.013011 | 12.7423 |  |  | 10.6646 |  |  | 16.9456 | 16.1553 | 15.1331 | 16.4381 | 15.727 | 14.835 | 10.7006 | 10.6535 | 11.5704 | 11.5189 | 9.0743 |  | 10.6709 | 8.1114 | 10.0265 | 9.3306 | 11.1406 | 12.369 |  | 12.3646 |  |  | 11.7691 | 12.5721 | 12.5489 | [6 empty] | 12.6176 |  |  | 11.3589 |  |  | 9.0149 | 10.1996 | 12.0207 | 7.4076 | 9.0729 | 12.6113 | 7.6976 | 9.4855 | 12.3016 | 9.2387 | 10.4483 | 7.7398 | 10.4883 | 8.2423 | 10.1682 | 7.8645 | 9.632 | 13.1558 | 10.4153 | 10.1541 | 11.5791 | 8.1998 | 9.7358 | 12.7176 | 8.1334 | 10.4038 | 9.7535 | 9.8732 | 8.5448 | 10.2838 | -0.11288 | 20.9503 | 0.03417 | 0.049506 | -37.999 | 3.1213 | -0.27 | 0.36 | -0.20088 | -0.66301 | 0.6031 | -0.2294 | 0.16416 | -0.17328 | 0.81574 | 0.41228 | 0.41779 | 0.42065 | 0.41897 | 0.63743 | 0.43771 | 0.42178
42810.4342 | -506 | 18.5274 | 18.6241 | 18.6148 | 18.6252 | 17.9921 | 16.65 | 14.725 | 16.7356 | 17.2184 | 17.3242 | 17.3264 | 16.8845 | 15.9268 | 14.5399 | 14.9912 | 15.0193 | 15.5766 | 13.4289 | 13.5504 | 14.1203 |  |  |  | 16.6334 | 15.9759 | 15.0963 | 10.299 | 9.6945 | 9.8819 | 17.2286 | 16.3968 | 15.2096 | 16.9249 | 16.2106 | 15.2256 | 10.8361 | 11.2481 |  | 12.2811 | 10.5871 | 10.401 | 8.3347 |  | 6.3372 | 6.3189 | 5.7874 | 5.8585 | 5.8437 | 6.0229 | 6.531 | 4.3292 | 6.5183 | 4.2906 | 6.6886 | 8.1203 | 43.1262 | 47.3894 | 43.6312 | 15.4092 |  |  | 0.14282 | -0.15039 | 0.071504 | 0.005914 | -0.10694 | -0.41182 | 0.2956 | 0.099716 | -0.12394 | 0.30215 | 0.01857 | 8.868 | 8.8691 | 2.0082 | 15.794 | 16.7424 | 17.2864 | 17.6269 | 17.5971 | 16.5853 | 14.9486 | 16.8849 | 17.2228 | 17.5101 | 17.5502 | 17.3021 | 16.5154 | 14.7576 | 6.0706 | 8.3891 | 5.1627 | 5.7067 | 5.9473 | 6.685 | 7.7184 | 15.8515 | 15.5294 | 15.4156 | 14.3594 | 14.2534 | 14.1986 |  |  |  | 10.7356 | 9.3822 | 8.9699 | 8.7945 | 0.019093 | 0.091678 | 12.7367 |  |  | 10.6556 |  |  | 16.9394 | 16.1502 | 15.1337 | 16.4355 | 15.7178 | 14.8413 | 10.6836 | 10.6553 | 11.5715 | 11.5255 | 9.0674 |  | 10.6716 | 8.1754 | 10.0273 | 9.329 | 11.1393 | 12.3654 |  | 12.3595 |  |  | 11.7559 | 12.5671 | 12.5519 | [6 empty] | 12.6197 |  |  | 11.3708 |  |  | 9.0243 | 10.2029 | 12.026 | 7.432 | 9.0914 | 12.6201 | 7.6974 | 9.4911 | 12.3207 | 9.2385 | 10.4504 | 7.7568 | 10.4968 | 8.2306 | 10.1765 | 7.857 | 9.6442 | 13.1598 | 10.4189 | 10.1495 | 11.5663 | 8.2019 | 9.744 | 12.6979 | 8.1334 | 10.401 | 9.7635 | 9.8677 | 8.5436 | 10.2872 | 0.007114 | 20.95 | 0.034004 | 0.047711 | -38.0243 | 3.1213 | -0.46 | 0.34 | 0.44307 | -0.4518 | 0.31153 | 0.089593 | -0.38079 | -0.74723 | 0.63308 | 0.41249 | 0.41604 | 0.42065 | 0.41595 | 0.63683 | 0.43827 | 0.42218
42810.4342 | -505 | 18.5317 | 18.6304 | 18.626 | 18.6316 | 17.9965 | 16.6528 | 14.7298 | 16.7277 | 17.2233 | 17.3156 | 17.333 | 16.8937 | 15.9206 | 14.5368 | 14.9967 | 15.0132 | 15.5718 | 13.4246 | 13.5424 | 14.1113 |  |  |  | 16.6309 | 15.9722 | 15.0899 | 10.2944 | 9.6887 | 9.8551 | 17.2286 | 16.3958 | 15.2157 | 16.9252 | 16.2133 | 15.2316 | 10.8339 | 11.2426 |  | 12.2758 | 10.5976 | 10.4025 | 8.337 |  | 6.3377 | 6.3158 | 5.7828 | 5.8573 | 5.8496 | 6.0244 | 6.5166 | 4.3132 | 6.5278 | 4.2466 | 6.6965 | 8.121 | 43.1292 | 47.3775 | 43.6399 | 15.4275 |  |  | 0.083671 | -0.20953 | 0.034048 | -0.13997 | -0.014948 | 0.13491 | 0.47894 | 0.10892 | -0.21366 | -0.37865 | -0.3224 | 8.8663 | 8.8676 | 2.0086 | 15.7982 | 16.7434 | 17.2895 | 17.6344 | 17.5959 | 16.5843 | 14.9552 | 16.8891 | 17.2226 | 17.5133 | 17.5578 | 17.3033 | 16.5215 | 14.7639 | 6.0695 | 8.3901 | 5.1852 | 5.6594 | 6.0597 | 6.6857 | 7.7186 | 15.8525 | 15.5239 | 15.4062 | 14.3546 | 14.2511 | 14.1933 |  |  |  | 10.7272 | 9.3761 | 8.9639 | 8.7755 | -0.038243 | 0.12706 | 12.7304 |  |  | 10.6519 |  |  | 16.938 | 16.1409 | 15.1295 | 16.436 | 15.7192 | 14.842 | 10.6798 | 10.643 | 11.5762 | 11.5297 | 9.0254 |  | 10.6756 | 8.221 | 10.02 | 9.3494 | 11.1353 | 12.3511 |  | 12.3629 |  |  | 11.719 | 12.529 | 12.5546 | [6 empty] | 12.5931 |  |  | 11.3621 |  |  | 9.0225 | 10.2017 | 12.0182 | 7.4536 | 9.1032 | 12.6321 | 7.6986 | 9.4878 | 12.3309 | 9.2436 | 10.4556 | 7.7715 | 10.5055 | 8.2194 | 10.1782 | 7.8636 | 9.654 | 13.1652 | 10.4171 | 10.1506 | 11.5475 | 8.2112 | 9.7451 | 12.6982 | 8.1419 | 10.4078 | 9.7749 | 9.8669 | 8.548 | 10.2847 | -0.11557 | 20.9508 | 0.033487 | 0.048385 | -38.0757 | 3.1213 | -0.75 | 0.36 | 0.33912 | -0.53328 | 0.21497 | -0.43586 | -0.14236 | 0.42768 | 0.80583 | 0.41379 | 0.41453 | 0.41995 | 0.41616 | 0.63435 | 0.43813 | 0.42243
42810.4342 | -504 | 18.5472 | 18.6465 | 18.6277 | 18.6382 | 17.9956 | 16.6627 | 14.7411 | 16.7401 | 17.2364 | 17.327 | 17.3401 | 16.8918 | 15.9343 | 14.5472 | 14.9942 | 15.0099 | 15.5779 | 13.4305 | 13.5396 | 14.1218 |  |  |  | 16.6399 | 15.9695 | 15.0892 | 10.2968 | 9.6873 | 9.865 | 17.2353 | 16.3995 | 15.2153 | 16.9261 | 16.2071 | 15.2294 | 10.8412 | 11.2719 |  | 12.2833 | 10.6014 | 10.3936 | 8.3338 |  | 6.317 | 6.3103 | 5.7759 | 5.8446 | 5.8451 | 6.0172 | 6.4956 | 4.3608 | 6.5285 | 4.2473 | 6.6876 | 8.1243 | 43.1337 | 47.3553 | 43.6592 | 15.4378 |  |  | 0.15596 | -0.082709 | 0.04062 | -0.37915 | -0.024148 | -0.13846 | 0.43557 | -0.14276 | -0.49699 | -0.41327 | -0.18828 | 8.8691 | 8.8703 | 2.0086 | 15.7913 | 16.7396 | 17.2884 | 17.6264 | 17.5953 | 16.5886 | 14.9516 | 16.8875 | 17.2154 | 17.5125 | 17.5572 | 17.3025 | 16.5186 | 14.7601 | 6.0619 | 8.3588 | 5.2131 | 5.6343 | 6.1123 | 6.6884 | 7.7183 | 15.8392 | 15.5128 | 15.4043 | 14.3573 | 14.2391 | 14.1946 |  |  |  | 10.7261 | 9.3659 | 8.9658 | 8.7885 | -0.00765 | -0.0067504 | 12.7221 |  |  | 10.6501 |  |  | 16.944 | 16.1429 | 15.1235 | 16.4384 | 15.7257 | 14.842 | 10.6724 | 10.6411 | 11.5755 | 11.5357 | 8.9928 |  | 10.6734 | 8.2374 | 10.023 | 9.3501 | 11.1404 | 12.331 |  | 12.3648 |  |  | 11.6966 | 12.4914 | 12.5198 | [6 empty] | 12.5783 |  |  | 11.3608 |  |  | 9.027 | 10.2013 | 12.0153 | 7.4767 | 9.1253 | 12.6389 | 7.691 | 9.4886 | 12.3459 | 9.2359 | 10.4629 | 7.7833 | 10.5139 | 8.219 | 10.1751 | 7.8732 | 9.6686 | 13.1732 | 10.4226 | 10.1523 | 11.5351 | 8.2142 | 9.7473 | 12.6989 | 8.1573 | 10.411 | 9.7709 | 9.8588 | 8.5466 | 10.2813 | -0.2762 | 20.9513 | 0.033217 | 0.04719 | -38.0146 | 3.1213 | -0.67 | 0.39 | 0.46299 | -0.33505 | 0.2348 | -0.71736 | -0.18094 | -0.43327 | 0.76847 | 0.41462 | 0.41418 | 0.4201 | 0.41732 | 0.63122 | 0.43846 | 0.42203
42810.4342 | -503 | 18.5309 | 18.6327 | 18.6275 | 18.6265 | 17.9913 | 16.653 | 14.7326 | 16.7386 | 17.2174 | 17.3235 | 17.3241 | 16.8828 | 15.9264 | 14.5377 | 15.001 | 15.0224 | 15.5733 | 13.4391 | 13.5543 | 14.1303 |  |  |  | 16.6373 | 15.9806 | 15.0951 | 10.2903 | 9.6803 | 9.8654 | 17.2431 | 16.4062 | 15.219 | 16.9349 | 16.2218 | 15.2352 | 10.8305 | 11.2988 |  | 12.2843 | 10.6185 | 10.401 | 8.3356 |  | 6.319 | 6.3114 | 5.7811 | 5.8511 | 5.8405 | 6.013 | 6.4842 | 4.451 | 6.5324 | 4.3628 | 6.6962 | 8.1245 | 43.1424 | 47.3362 | 43.6782 | 15.4558 |  |  | -0.041181 | -0.23122 | 0.00842 | 0.23656 | -0.061604 | -0.23374 | 0.40206 | -0.063248 | -0.15547 | 0.025003 | -0.28326 | 8.8698 | 8.871 | 2.0083 | 15.7919 | 16.7317 | 17.286 | 17.6226 | 17.5966 | 16.5994 | 14.9496 | 16.8932 | 17.2199 | 17.5165 | 17.5579 | 17.3074 | 16.5208 | 14.7613 | 6.0451 | 8.368 | 5.2087 | 5.623 | 6.0525 | 6.676 | 7.7149 | 15.8333 | 15.5185 | 15.3973 | 14.3489 | 14.2407 | 14.1861 |  |  |  | 10.7239 | 9.3666 | 8.963 | 8.7824 | -0.03885 | 0.057614 | 12.7269 |  |  | 10.6485 |  |  | 16.9429 | 16.1423 | 15.1188 | 16.4422 | 15.7191 | 14.8422 | 10.664 | 10.6389 | 11.5837 | 11.5345 | 8.9777 |  | 10.6604 | 8.265 | 10.0079 | 9.3352 | 11.1299 | 12.2383 |  | 12.3645 |  |  | 11.7115 | 12.4983 | 12.4876 | [6 empty] | 12.5895 |  |  | 11.3484 |  |  | 9.0101 | 10.1935 | 12.0023 | 7.4786 | 9.1309 | 12.6312 | 7.6759 | 9.4744 | 12.3469 | 9.2317 | 10.4568 | 7.7807 | 10.5007 | 8.2 | 10.1639 | 7.8853 | 9.6746 | 13.1751 | 10.4251 | 10.1476 | 11.5114 | 8.2224 | 9.7531 | 12.7043 | 8.1621 | 10.4147 | 9.7672 | 9.8597 | 8.5474 | 10.2787 | -0.046814 | 20.954 | 0.032523 | 0.046452 | -38.0001 | 3.1213 | -0.63 | 0.31 | -0.23791 | -0.56019 | 0.1069 | 0.56663 | -0.289 | -0.56294 | 0.73831 | 0.41461 | 0.41291 | 0.42016 | 0.41775 | 0.63131 | 0.43806 | 0.42213
42810.4342 | -502 | 18.5325 | 18.6315 | 18.6216 | 18.6252 | 17.9909 | 16.66 | 14.7252 | 16.74 | 17.2162 | 17.3181 | 17.3305 | 16.8813 | 15.9275 | 14.5369 | 14.9945 | 15.0117 | 15.5741 | 13.4296 | 13.5458 | 14.1148 |  |  |  | 16.6294 | 15.9774 | 15.0925 | 10.2809 | 9.6827 | 9.8388 | 17.2334 | 16.3922 | 15.2089 | 16.922 | 16.2129 | 15.2279 | 10.8271 | 11.3234 |  | 12.2717 | 10.62 | 10.39 | 8.3287 |  | 6.3187 | 6.3048 | 5.7797 | 5.8536 | 5.8467 | 6.0125 | 6.47 | 4.5396 | 6.5381 | 4.4029 | 6.6941 | 8.1192 | 43.1584 | 47.3224 | 43.7001 | 15.4557 |  |  | 0.071187 | -0.19508 | 0.11356 | -0.31213 | 0.002792 | -0.026088 | 0.50916 | -0.002136 | -0.26308 | 0.33865 | -0.25703 | 8.8687 | 8.8702 | 2.0088 | 15.7875 | 16.7322 | 17.2913 | 17.6186 | 17.5924 | 16.5882 | 14.9446 | 16.8962 | 17.2188 | 17.5122 | 17.5512 | 17.3073 | 16.5256 | 14.7645 | 6.0153 | 8.3815 | 5.2727 | 5.6055 | 5.9962 | 6.6735 | 7.7154 | 15.8376 | 15.5159 | 15.4001 | 14.3535 | 14.237 | 14.1919 |  |  |  | 10.7306 | 9.3714 | 8.9679 | 8.7712 | -0.030949 | 0.050274 | 12.7277 |  |  | 10.6435 |  |  | 16.9381 | 16.1383 | 15.1224 | 16.4326 | 15.72 | 14.8414 | 10.6598 | 10.6388 | 11.5824 | 11.5311 | 8.9677 |  | 10.6659 | 8.3118 | 10.0164 | 9.3485 | 11.1394 | 12.1472 |  | 12.3577 |  |  | 11.6938 | 12.496 | 12.4744 | [6 empty] | 12.5938 |  |  | 11.3595 |  |  | 9.0307 | 10.1949 | 12.0067 | 7.4836 | 9.1438 | 12.6286 | 7.6968 | 9.4888 | 12.3579 | 9.2282 | 10.457 | 7.792 | 10.5057 | 8.2013 | 10.1672 | 7.9018 | 9.6827 | 13.1805 | 10.4268 | 10.1378 | 11.5034 | 8.2176 | 9.7554 | 12.7032 | 8.1628 | 10.4155 | 9.768 | 9.8578 | 8.5392 | 10.2707 | -0.068578 | 20.9472 | 0.032207 | 0.046908 | -38.0057 | 3.1213 | -0.93 | 0.34 | 0.31279 | -0.51455 | 0.39259 | -0.65086 | 0.061525 | -0.18807 | 0.83085 | 0.41507 | 0.41189 | 0.42011 | 0.42076 | 0.62425 | 0.43813 | 0.42267
42810.4342 | -501 | 18.5312 | 18.6311 | 18.6213 | 18.6248 | 17.989 | 16.6528 | 14.7229 | 16.7378 | 17.2193 | 17.3133 | 17.3304 | 16.8807 | 15.9294 | 14.5381 | 14.9944 | 15.0178 | 15.5759 | 13.4327 | 13.55 | 14.1312 |  |  |  | 16.6356 | 15.9836 | 15.0985 | 10.2935 | 9.6816 | 9.8283 | 17.2326 | 16.3848 | 15.2012 | 16.9274 | 16.2186 | 15.2242 | 10.8311 | 11.3422 |  | 12.2711 | 10.6272 | 10.3873 | 8.3352 |  | 6.3102 | 6.3022 | 5.7855 | 5.8651 | 5.8399 | 6.023 | 6.472 | 4.6427 | 6.5282 | 4.4056 | 6.6929 | 8.1215 | 43.1692 | 47.3217 | 43.7248 | 15.4529 |  |  | -0.15617 | -0.003853 | 0.085304 | -0.22802 | -0.037948 | 0.12374 | 0.49142 | 0.063576 | -0.51431 | -1.7331 | -0.39771 | 8.8706 | 8.8721 | 2.0083 | 15.7842 | 16.7229 | 17.2791 | 17.6172 | 17.5854 | 16.5817 | 14.9454 | 16.8853 | 17.22 | 17.5099 | 17.5523 | 17.2994 | 16.5166 | 14.7608 | 5.9861 | 8.3602 | 5.3054 | 5.6197 | 5.9202 | 6.6703 | 7.7199 | 15.8364 | 15.5074 | 15.4051 | 14.3519 | 14.2485 | 14.1875 |  |  |  | 10.7265 | 9.3669 | 8.9662 | 8.7585 | -0.057692 | 0.0019068 | 12.7242 |  |  | 10.6409 |  |  | 16.9459 | 16.1477 | 15.134 | 16.4367 | 15.7249 | 14.8427 | 10.6693 | 10.6509 | 11.5834 | 11.5191 | 8.8922 |  | 10.6591 | 8.3264 | 10.0084 | 9.3525 | 11.1345 | 12.0479 |  | 12.3535 |  |  | 11.7024 | 12.5062 | 12.4633 | [6 empty] | 12.593 |  |  | 11.372 |  |  | 9.0433 | 10.2076 | 11.9992 | 7.5035 | 9.1677 | 12.6404 | 7.7016 | 9.4809 | 12.3784 | 9.2456 | 10.4671 | 7.815 | 10.5129 | 8.2001 | 10.1759 | 7.9064 | 9.681 | 13.1803 | 10.417 | 10.1359 | 11.4914 | 8.2284 | 9.748 | 12.6913 | 8.1604 | 10.4095 | 9.762 | 9.8474 | 8.5359 | 10.2683 | -0.25213 | 20.952 | 0.033447 | 0.048117 | -37.918 | 3.1213 | -0.73 | 0.29 | -0.46328 | -0.072314 | 0.34026 | -0.5563 | -0.22683 | 0.40959 | 0.81627 | 0.41694 | 0.41122 | 0.41984 | 0.42364 | 0.62114 | 0.43809 | 0.42288
42810.4342 | -500 | 18.5246 | 18.6311 | 18.6158 | 18.6218 | 17.9852 | 16.6478 | 14.7161 | 16.7279 | 17.214 | 17.3065 | 17.3235 | 16.8789 | 15.9279 | 14.5339 | 14.9982 | 15.0165 | 15.569 | 13.4334 | 13.549 | 14.1285 |  |  |  | 16.6357 | 15.9822 | 15.0966 | 10.2726 | 9.6763 | 9.7925 | 17.2289 | 16.3866 | 15.2082 | 16.9306 | 16.216 | 15.2226 | 10.8328 | 11.3509 |  | 12.268 | 10.6387 | 10.3858 | 8.3603 |  | 6.3158 | 6.3094 | 5.7952 | 5.8678 | 5.8514 | 6.042 | 6.4655 | 4.6873 | 6.5298 | 4.4275 | 6.6929 | 8.1219 | 43.1858 | 47.3309 | 43.7445 | 15.4508 |  |  | 0.15727 | -0.27853 | -0.033632 | 0.07097 | 0.1007 | 0.002824 | 0.35474 | -0.025792 | -0.0099092 | -0.35515 | -0.30074 | 8.8664 | 8.8677 | 2.0085 | 15.7845 | 16.7325 | 17.2919 | 17.6266 | 17.5919 | 16.5883 | 14.9426 | 16.8927 | 17.2284 | 17.5107 | 17.5582 | 17.306 | 16.522 | 14.7617 | 5.9781 | 8.3432 | 5.335 | 5.6114 | 5.8669 | 6.667 | 7.715 | 15.8309 | 15.5132 | 15.4077 | 14.3546 | 14.2494 | 14.1903 |  |  |  | 10.73 | 9.3649 | 8.9719 | 8.7588 | 0.011192 | -0.031028 | 12.7246 |  |  | 10.637 |  |  | 16.9498 | 16.1488 | 15.128 | 16.4367 | 15.7269 | 14.8478 | 10.6689 | 10.6478 | 11.5823 | 11.5052 | 8.8876 |  | 10.6552 | 8.2652 | 9.9998 | 9.3281 | 11.1299 | 12.0061 |  | 12.3545 |  |  | 11.6792 | 12.5069 | 12.4524 | [6 empty] | 12.5956 |  |  | 11.3777 |  |  | 9.0317 | 10.1928 | 11.9927 | 7.5063 | 9.1583 | 12.6275 | 7.7085 | 9.468 | 12.3839 | 9.2388 | 10.4691 | 7.81 | 10.4966 | 8.1921 | 10.1562 | 7.9153 | 9.6873 | 13.1859 | 10.4242 | 10.129 | 11.4784 | 8.2289 | 9.7357 | 12.6961 | 8.1663 | 10.412 | 9.7606 | 9.8455 | 8.5337 | 10.2618 | 0.10688 | 20.9524 | 0.033958 | 0.048906 | -37.9704 | 3.1213 | -0.8 | 0.44 | 0.46488 | -0.61484 | -0.21365 | 0.31036 | 0.36952 | 0.06188 | 0.69355 | 0.41695 | 0.41264 | 0.42036 | 0.42414 | 0.61728 | 0.43745 | 0.42299
42810.4343 | -499 | 18.5257 | 18.6305 | 18.6213 | 18.6228 | 17.9934 | 16.6467 | 14.7218 | 16.73 | 17.2129 | 17.3128 | 17.3213 | 16.8855 | 15.934 | 14.5387 | 14.9957 | 15.0125 | 15.5633 | 13.4237 | 13.5443 | 14.1155 |  |  |  | 16.6346 | 15.9753 | 15.0941 | 10.2574 | 9.6681 | 9.7726 | 17.2228 | 16.3792 | 15.1988 | 16.9206 | 16.2096 | 15.2191 | 10.8252 | 11.3502 |  | 12.261 | 10.6313 | 10.3759 | 8.3909 |  | 6.3023 | 6.2938 | 5.7896 | 5.8689 | 5.8802 | 6.0323 | 6.4647 | 4.7219 | 6.53 | 4.4472 | 6.6968 | 8.1085 | 43.192 | 47.3381 | 43.7561 | 15.4463 |  |  | 0.20261 | -0.23845 | 0.096476 | 0.025626 | 0.21373 | -0.27382 | 0.5867 | -0.040904 | -0.94905 | -0.30124 | -0.43427 | 8.8711 | 8.8719 | 2.0087 | 15.7866 | 16.7206 | 17.282 | 17.624 | 17.5949 | 16.5895 | 14.9428 | 16.8811 | 17.2208 | 17.509 | 17.5501 | 17.3042 | 16.5228 | 14.7603 | 5.9799 | 8.3088 | 5.3591 | 5.6109 | 5.8381 | 6.6688 | 7.7119 | 15.8347 | 15.5059 | 15.4048 | 14.3488 | 14.2407 | 14.1895 |  |  |  | 10.7306 | 9.364 | 8.9768 | 8.793 | -0.033583 | -0.060199 | 12.7215 |  |  | 10.6374 |  |  | 16.9481 | 16.1428 | 15.141 | 16.4418 | 15.7274 | 14.8494 | 10.6781 | 10.6482 | 11.5786 | 11.5019 | 8.8856 |  | 10.6529 | 8.1909 | 10.0029 | 9.3087 | 11.1316 | 11.9998 |  | 12.3517 |  |  | 11.6597 | 12.5158 | 12.4557 | [6 empty] | 12.615 |  |  | 11.3803 |  |  | 9.0305 | 10.1931 | 11.9801 | 7.5215 | 9.1656 | 12.6165 | 7.7135 | 9.4496 | 12.3788 | 9.2317 | 10.461 | 7.8156 | 10.4918 | 8.1929 | 10.1545 | 7.9421 | 9.6984 | 13.1961 | 10.4276 | 10.1312 | 11.4826 | 8.2295 | 9.7438 | 12.703 | 8.1783 | 10.4225 | 9.7683 | 9.8541 | 8.5364 | 10.2661 | 0.018477 | 20.9518 | 0.034388 | 0.050462 | -37.8671 | 3.1213 | -0.67 | 0.4 | 0.52763 | -0.56886 | 0.36185 | 0.18649 | 0.53832 | -0.60932 | 0.89191 | 0.41693 | 0.41481 | 0.42096 | 0.42415 | 0.61424 | 0.43635 | 0.42206
42810.4343 | -498 | 18.536 | 18.6283 | 18.6174 | 18.6261 | 17.9983 | 16.6459 | 14.7261 | 16.7401 | 17.2217 | 17.32 | 17.3249 | 16.8891 | 15.9278 | 14.5303 | 14.9939 | 15.0182 | 15.5712 | 13.4313 | 13.5439 | 14.1211 |  |  |  | 16.6379 | 15.9785 | 15.0992 | 10.259 | 9.6685 | 9.7776 | 17.2132 | 16.3754 | 15.1983 | 16.922 | 16.2077 | 15.2121 | 10.8243 | 11.3437 |  | 12.2596 | 10.6254 | 10.3685 | 8.4082 |  | 6.3073 | 6.3008 | 5.7978 | 5.886 | 5.8849 | 6.0309 | 6.4639 | 4.7492 | 6.5372 | 4.4845 | 6.7012 | 8.1148 | 43.21 | 47.334 | 43.7677 | 15.4424 |  |  | 0.090903 | -0.18982 | -0.031664 | -0.082138 | 0.2801 | -0.095084 | 0.42046 | 0.057004 | -1.2869 | -0.68349 | -0.35975 | 8.8722 | 8.8734 | 2.0083 | 15.7871 | 16.7308 | 17.2886 | 17.629 | 17.5977 | 16.5878 | 14.9504 | 16.8923 | 17.2225 | 17.509 | 17.5528 | 17.3084 | 16.5289 | 14.7685 | 5.9824 | 8.3314 | 5.3597 | 5.6184 | 5.8206 | 6.6735 | 7.7263 | 15.8283 | 15.503 | 15.3986 | 14.3445 | 14.2319 | 14.1844 |  |  |  | 10.7203 | 9.3578 | 8.9719 | 8.8301 | 0.064476 | 0.094878 | 12.7162 |  |  | 10.6205 |  |  | 16.9366 | 16.1342 | 15.1252 | 16.4341 | 15.717 | 14.8362 | 10.6627 | 10.6318 | 11.5654 | 11.4772 | 8.8579 |  | 10.6484 | 8.1753 | 9.994 | 9.2992 | 11.1355 | 12.0221 |  | 12.3465 |  |  | 11.6379 | 12.5261 | 12.4727 | [6 empty] | 12.6336 |  |  | 11.3771 |  |  | 9.0226 | 10.1938 | 11.9704 | 7.5293 | 9.1544 | 12.606 | 7.7144 | 9.434 | 12.3838 | 9.2276 | 10.4591 | 7.807 | 10.4764 | 8.1884 | 10.1512 | 7.9523 | 9.6896 | 13.1916 | 10.4361 | 10.1336 | 11.4714 | 8.2343 | 9.7478 | 12.7049 | 8.1838 | 10.4191 | 9.7664 | 9.841 | 8.5488 | 10.2653 | 0.063546 | 20.9519 | 0.034319 | 0.051366 | -38.0647 | 3.1213 | -0.39 | 0.34 | 0.35342 | -0.50756 | -0.2073 | -0.33388 | 0.61626 | -0.35906 | 0.75504 | 0.41755 | 0.41495 | 0.42135 | 0.42442 | 0.61585 | 0.43584 | 0.42069
42810.4343 | -497 | 18.5278 | 18.6268 | 18.6208 | 18.6283 | 17.9917 | 16.6494 | 14.7212 | 16.7349 | 17.2214 | 17.3139 | 17.3291 | 16.8777 | 15.9311 | 14.5422 | 14.9806 | 15.0036 | 15.5574 | 13.4261 | 13.5402 | 14.1112 |  |  |  | 16.628 | 15.9731 | 15.0941 | 10.2576 | 9.6681 | 9.7844 | 17.2288 | 16.3837 | 15.196 | 16.9164 | 16.2082 | 15.2188 | 10.8201 | 11.3577 |  | 12.2682 | 10.6215 | 10.3755 | 8.4343 |  | 6.3055 | 6.296 | 5.7994 | 5.8813 | 5.8786 | 6.0241 | 6.4639 | 4.7699 | 6.5365 | 4.5115 | 6.6982 | 8.1038 | 43.2322 | 47.327 | 43.7824 | 15.4336 |  |  | -0.060893 | 0.034259 | -0.017864 | -0.099226 | 0.2939 | -0.124 | 0.51442 | 0.037948 | -0.37089 | -0.98959 | -0.33293 | 8.8697 | 8.8708 | 2.0087 | 15.7819 | 16.7303 | 17.2863 | 17.6259 | 17.593 | 16.5846 | 14.9495 | 16.8911 | 17.2155 | 17.509 | 17.5554 | 17.3041 | 16.5218 | 14.7665 | 5.9763 | 8.3406 | 5.3488 | 5.6101 | 5.7753 | 6.6715 | 7.7285 | 15.8158 | 15.5024 | 15.3988 | 14.3448 | 14.2337 | 14.181 |  |  |  | 10.7233 | 9.3587 | 8.9769 | 8.8612 | -0.021629 | 0.039735 | 12.7187 |  |  | 10.6208 |  |  | 16.9385 | 16.1408 | 15.1294 | 16.4302 | 15.7178 | 14.8361 | 10.6584 | 10.629 | 11.571 | 11.47 | 8.8562 |  | 10.6529 | 8.194 | 9.988 | 9.2939 | 11.1325 | 12.0075 |  | 12.3565 |  |  | 11.6484 | 12.5138 | 12.4806 | [6 empty] | 12.6385 |  |  | 11.3841 |  |  | 9.029 | 10.195 | 11.9777 | 7.55 | 9.1628 | 12.5974 | 7.7317 | 9.4357 | 12.3887 | 9.2238 | 10.4577 | 7.8227 | 10.4749 | 8.1889 | 10.1595 | 7.9595 | 9.6966 | 13.1867 | 10.436 | 10.1335 | 11.4676 | 8.2387 | 9.7483 | 12.7095 | 8.1875 | 10.4166 | 9.7641 | 9.8338 | 8.5454 | 10.2606 | -0.05317 | 20.9525 | 0.034922 | 0.051924 | -38.0606 | 3.1214 | -0.55 | 0.35 | -0.28926 | 0.21563 | -0.15571 | -0.36697 | 0.63125 | -0.41002 | 0.83515 | 0.41774 | 0.41423 | 0.4214 | 0.42486 | 0.61732 | 0.43497 | 0.41992
42810.4343 | -496 | 18.518 | 18.6201 | 18.6201 | 18.6304 | 17.9896 | 16.6498 | 14.7205 | 16.7328 | 17.2153 | 17.3188 | 17.3255 | 16.8811 | 15.9198 | 14.5344 | 14.9817 | 15.0082 | 15.5628 | 13.4276 | 13.5438 | 14.1155 |  |  |  | 16.6316 | 15.9753 | 15.0896 | 10.2546 | 9.6719 | 9.7922 | 17.2219 | 16.3788 | 15.2049 | 16.9138 | 16.2166 | 15.222 | 10.8279 | 11.3771 |  | 12.2626 | 10.6199 | 10.3738 | 8.4366 |  | 6.3015 | 6.2962 | 5.8017 | 5.8864 | 5.8824 | 6.0187 | 6.4642 | 4.7617 | 6.5378 | 4.5348 | 6.7036 | 8.1103 | 43.2537 | 47.308 | 43.7736 | 15.4208 |  |  | 0.19407 | -0.059053 | -0.008008 | 0.16165 | 0.076388 | -0.35924 | 0.55648 | 0.14309 | -0.36505 | 0.11753 | -0.15748 | 8.8688 | 8.8698 | 2.0084 | 15.77 | 16.7191 | 17.2814 | 17.6154 | 17.5857 | 16.575 | 14.9461 | 16.8843 | 17.2152 | 17.5135 | 17.5515 | 17.303 | 16.5175 | 14.7594 | 5.9626 | 8.3176 | 5.3222 | 5.5924 | 5.7478 | 6.6774 | 7.7274 | 15.814 | 15.505 | 15.4031 | 14.352 | 14.2337 | 14.1844 |  |  |  | 10.7229 | 9.3683 | 8.9722 | 8.8683 | -0.088285 | -0.011079 | 12.7226 |  |  | 10.6327 |  |  | 16.941 | 16.1451 | 15.1281 | 16.4389 | 15.7215 | 14.8438 | 10.6632 | 10.64 | 11.5731 | 11.4691 | 8.8662 |  | 10.6517 | 8.2343 | 9.9872 | 9.2983 | 11.1301 | 12.0034 |  | 12.3527 |  |  | 11.6644 | 12.5078 | 12.4826 | [6 empty] | 12.6414 |  |  | 11.39 |  |  | 9.0329 | 10.1978 | 11.9772 | 7.5609 | 9.1611 | 12.5878 | 7.7394 | 9.4281 | 12.3889 | 9.2256 | 10.4575 | 7.8293 | 10.4653 | 8.1915 | 10.1641 | 7.9693 | 9.7011 | 13.1906 | 10.4416 | 10.1386 | 11.4698 | 8.2449 | 9.7534 | 12.711 | 8.1967 | 10.4191 | 9.7649 | 9.835 | 8.5467 | 10.2609 | 0.0096178 | 20.9524 | 0.033757 | 0.049492 | -37.984 | 3.1213 | -0.66 | 0.27 | 0.51641 | -0.2831 | -0.10425 | 0.46839 | 0.32182 | -0.6979 | 0.86861 | 0.41742 | 0.41309 | 0.4212 | 0.42708 | 0.62013 | 0.43517 | 0.41971
42810.4343 | -495 | 18.5274 | 18.6307 | 18.6175 | 18.6253 | 17.9905 | 16.6505 | 14.7228 | 16.7389 | 17.2199 | 17.3225 | 17.327 | 16.8811 | 15.9305 | 14.5416 | 14.985 | 15.0124 | 15.5658 | 13.4262 | 13.5465 | 14.1203 |  |  |  | 16.6368 | 15.9824 | 15.0939 | 10.2544 | 9.6652 | 9.7994 | 17.2204 | 16.3794 | 15.1981 | 16.9167 | 16.2146 | 15.2164 | 10.8258 | 11.4012 |  | 12.2637 | 10.6072 | 10.381 | 8.4263 |  | 6.2943 | 6.2988 | 5.8012 | 5.8845 | 5.882 | 6.0147 | 6.4415 | 4.7488 | 6.5356 | 4.5691 | 6.7111 | 8.1123 | 43.2683 | 47.2979 | 43.7719 | 15.4148 |  |  | 0.004819 | -0.16156 | 0.01368 | 0.13734 | 0.072448 | -0.13977 | 0.51705 | -0.083616 | -0.69899 | -0.46026 | -0.23934 | 8.8676 | 8.869 | 2.0083 | 15.7688 | 16.7211 | 17.2842 | 17.6107 | 17.5837 | 16.5777 | 14.9389 | 16.881 | 17.2128 | 17.5139 | 17.5461 | 17.301 | 16.525 | 14.7675 | 5.9828 | 8.3108 | 5.2706 | 5.5635 | 5.7526 | 6.6698 | 7.7251 | 15.822 | 15.5038 | 15.4026 | 14.3446 | 14.2349 | 14.1808 |  |  |  | 10.7268 | 9.3696 | 8.9743 | 8.9083 | 0.10256 | -0.030464 | 12.7056 |  |  | 10.6238 |  |  | 16.9374 | 16.1354 | 15.1215 | 16.436 | 15.7149 | 14.8394 | 10.6516 | 10.631 | 11.5582 | 11.4695 | 8.8793 |  | 10.6527 | 8.2727 | 9.991 | 9.2933 | 11.1344 | 12.0077 |  | 12.3537 |  |  | 11.6853 | 12.5156 | 12.4665 | [6 empty] | 12.6328 |  |  | 11.3897 |  |  | 9.0279 | 10.2019 | 11.9746 | 7.5699 | 9.1599 | 12.581 | 7.7385 | 9.4329 | 12.3926 | 9.2248 | 10.4501 | 7.8297 | 10.4575 | 8.1868 | 10.1601 | 7.9768 | 9.6983 | 13.1942 | 10.444 | 10.1287 | 11.4611 | 8.2437 | 9.7535 | 12.7009 | 8.1969 | 10.4082 | 9.7601 | 9.8233 | 8.5423 | 10.2676 | 0.036967 | 20.9531 | 0.033217 | 0.048739 | -38.0183 | 3.1213 | -0.66 | 0.33 | 0.081377 | -0.46826 | 0.13626 | 0.43173 | 0.31341 | -0.43531 | 0.83727 | 0.41709 | 0.41214 | 0.42148 | 0.42395 | 0.62561 | 0.43538 | 0.41873
42810.4343 | -494 | 18.5232 | 18.6229 | 18.6136 | 18.6242 | 17.9831 | 16.6466 | 14.7203 | 16.735 | 17.221 | 17.3069 | 17.3235 | 16.8781 | 15.9235 | 14.5355 | 14.9908 | 15.0069 | 15.564 | 13.4245 | 13.5491 | 14.1215 |  |  |  | 16.6378 | 15.981 | 15.1004 | 10.2565 | 9.6691 | 9.817 | 17.2171 | 16.3777 | 15.1896 | 16.9169 | 16.2017 | 15.219 | 10.8251 | 11.4036 |  | 12.256 | 10.5881 | 10.3902 | 8.4109 |  | 6.2886 | 6.2909 | 5.7982 | 5.884 | 5.8712 | 6.0072 | 6.4262 | 4.7124 | 6.5379 | 4.5581 | 6.7021 | 8.1087 | 43.2705 | 47.283 | 43.7675 | 15.4002 |  |  | 0.19538 | -0.003853 | 0.026164 | 0.25299 | 0.13159 | -0.10428 | 0.57422 | -0.15722 | 0.64064 | -0.55908 | -0.37744 | 8.869 | 8.8703 | 2.0087 | 15.7756 | 16.7181 | 17.2801 | 17.6167 | 17.5946 | 16.586 | 14.9473 | 16.8801 | 17.2161 | 17.5138 | 17.558 | 17.3084 | 16.5324 | 14.7654 | 6.0033 | 8.31 | 5.2767 | 5.5487 | 5.7702 | 6.6718 | 7.7278 | 15.8168 | 15.5025 | 15.397 | 14.3428 | 14.232 | 14.1854 |  |  |  | 10.7217 | 9.3729 | 8.9765 | 8.9407 | 0.0010618 | -0.036674 | 12.7036 |  |  | 10.6292 |  |  | 16.9349 | 16.1412 | 15.1248 | 16.4272 | 15.7179 | 14.8339 | 10.667 | 10.6325 | 11.5589 | 11.4702 | 8.8979 |  | 10.6487 | 8.2903 | 9.9838 | 9.2995 | 11.1342 | 12.0074 |  | 12.3535 |  |  | 11.7048 | 12.5086 | 12.4417 | [6 empty] | 12.6158 |  |  | 11.3911 |  |  | 9.0287 | 10.2201 | 11.9768 | 7.5874 | 9.1675 | 12.5849 | 7.7531 | 9.4392 | 12.4022 | 9.236 | 10.4553 | 7.8297 | 10.4574 | 8.195 | 10.1651 | 7.9857 | 9.6972 | 13.1958 | 10.4386 | 10.1288 | 11.4554 | 8.2509 | 9.7519 | 12.7 | 8.1952 | 10.4056 | 9.7634 | 9.8194 | 8.5381 | 10.2706 | -0.068578 | 20.9528 | 0.032603 | 0.048167 | -38.0893 | 3.1213 | -0.77 | 0.39 | 0.51818 | -0.072312 | 0.18844 | 0.58595 | 0.42238 | -0.37601 | 0.88233 | 0.41645 | 0.41142 | 0.4213 | 0.4219 | 0.62524 | 0.43579 | 0.41766
42810.4343 | -493 | 18.5311 | 18.6259 | 18.6203 | 18.6332 | 17.9881 | 16.6533 | 14.7237 | 16.7373 | 17.2192 | 17.3162 | 17.3315 | 16.8797 | 15.9293 | 14.5432 | 14.9932 | 15.0059 | 15.5664 | 13.4241 | 13.5442 | 14.1172 |  |  |  | 16.6341 | 15.9833 | 15.0936 | 10.2545 | 9.6693 | 9.8269 | 17.2246 | 16.3823 | 15.2028 | 16.9251 | 16.2067 | 15.2301 | 10.8313 | 11.3993 |  | 12.2627 | 10.5827 | 10.3976 | 8.4174 |  | 6.2977 | 6.2914 | 5.8004 | 5.8826 | 5.8738 | 6.0084 | 6.4139 | 4.7875 | 6.5404 | 4.5232 | 6.7059 | 8.1103 | 43.2823 | 47.2747 | 43.768 | 15.3881 |  |  | 0.20327 | -0.11622 | 0.2187 | -0.045342 | 0.05996 | -0.053028 | 0.57488 | -0.24921 | -0.46955 | -1.5611 | -0.31068 | 8.8693 | 8.8701 | 2.0084 | 15.782 | 16.7232 | 17.2917 | 17.6176 | 17.5891 | 16.5812 | 14.9428 | 16.8971 | 17.2264 | 17.5218 | 17.5627 | 17.3128 | 16.5311 | 14.7641 | 5.9805 | 8.2805 | 5.289 | 5.5345 | 5.7862 | 6.6712 | 7.7246 | 15.8174 | 15.5053 | 15.3928 | 14.3438 | 14.2385 | 14.1849 |  |  |  | 10.7287 | 9.3774 | 8.9803 | 8.9454 | -0.018185 | 0.045193 | 12.6838 |  |  | 10.6267 |  |  | 16.9301 | 16.1247 | 15.1175 | 16.4258 | 15.7088 | 14.8297 | 10.6627 | 10.6234 | 11.5555 | 11.4767 | 8.9071 |  | 10.6426 | 8.3139 | 9.9713 | 9.2964 | 11.1253 | 12.0138 |  | 12.3446 |  |  | 11.7302 | 12.4775 | 12.4266 | [6 empty] | 12.6202 |  |  | 11.3993 |  |  | 9.027 | 10.2112 | 11.9607 | 7.593 | 9.1568 | 12.5663 | 7.7517 | 9.4301 | 12.3941 | 9.2237 | 10.4485 | 7.8148 | 10.4345 | 8.19 | 10.1568 | 7.9957 | 9.7018 | 13.2005 | 10.4478 | 10.1401 | 11.4595 | 8.2567 | 9.7547 | 12.7092 | 8.1956 | 10.411 | 9.7636 | 9.8289 | 8.5429 | 10.2747 | 0.040049 | 20.9518 | 0.033516 | 0.048457 | -38.141 | 3.1212 | -0.92 | 0.37 | 0.52854 | -0.39715 | 0.5448 | -0.24806 | 0.28512 | -0.26813 | 0.88283 | 0.41599 | 0.41035 | 0.42109 | 0.42437 | 0.62351 | 0.43581 | 0.41776
42810.4343 | -492 | 18.5281 | 18.6238 | 18.6164 | 18.6318 | 17.9883 | 16.6479 | 14.7186 | 16.7384 | 17.2166 | 17.3167 | 17.3264 | 16.8818 | 15.9307 | 14.5412 | 14.9863 | 15.0105 | 15.5643 | 13.4273 | 13.5397 | 14.1192 |  |  |  | 16.6314 | 15.9813 | 15.0888 | 10.2568 | 9.6624 | 9.8246 | 17.2306 | 16.382 | 15.2034 | 16.9279 | 16.2114 | 15.2272 | 10.8342 | 11.4029 |  | 12.2631 | 10.5666 | 10.3995 | 8.4004 |  | 6.2802 | 6.275 | 5.7994 | 5.8832 | 5.8778 | 6.0067 | 6.397 | 4.7757 | 6.5381 | 4.4774 | 6.704 | 8.1146 | 43.2853 | 47.2625 | 43.7741 | 15.379 |  |  | 0.084987 | 0.12034 | 0.055076 | 0.11039 | 0.1007 | -0.30733 | 0.33437 | -0.1237 | -0.67272 | 1.1978 | -0.32439 | 8.8711 | 8.872 | 2.0086 | 15.7759 | 16.7224 | 17.2853 | 17.6204 | 17.5889 | 16.5828 | 14.94 | 16.8903 | 17.2265 | 17.5102 | 17.5635 | 17.3118 | 16.5259 | 14.7645 | 5.9645 | 8.2801 | 5.3016 | 5.5159 | 5.8026 | 6.6714 | 7.724 | 15.816 | 15.5014 | 15.3971 | 14.3425 | 14.2377 | 14.174 |  |  |  | 10.7221 | 9.374 | 8.9805 | 8.9473 | -0.052222 | 0.057614 | 12.6819 |  |  | 10.6274 |  |  | 16.9283 | 16.1345 | 15.1157 | 16.4209 | 15.7142 | 14.8255 | 10.6704 | 10.6222 | 11.5538 | 11.4896 | 8.8919 |  | 10.6453 | 8.3598 | 9.9681 | 9.2999 | 11.1197 | 12.0555 |  | 12.3555 |  |  | 11.7519 | 12.4523 | 12.4034 | [6 empty] | 12.6167 |  |  | 11.4049 |  |  | 9.0252 | 10.2088 | 11.9503 | 7.6075 | 9.1373 | 12.5608 | 7.7511 | 9.4325 | 12.3897 | 9.2185 | 10.4385 | 7.7945 | 10.4261 | 8.1923 | 10.1533 | 7.9834 | 9.7075 | 13.2035 | 10.4529 | 10.1517 | 11.4589 | 8.262 | 9.7525 | 12.702 | 8.1845 | 10.4159 | 9.763 | 9.8212 | 8.5504 | 10.2831 | -0.084949 | 20.9535 | 0.03409 | 0.04926 | -38.0638 | 3.1212 | -0.82 | 0.39 | 0.34176 | 0.40411 | 0.27339 | 0.38705 | 0.3695 | -0.6455 | 0.6733 | 0.4165 | 0.40897 | 0.42081 | 0.42617 | 0.62204 | 0.43638 | 0.41749
42810.4344 | -491 | 18.5296 | 18.633 | 18.6254 | 18.6361 | 17.9962 | 16.6491 | 14.7235 | 16.7436 | 17.2243 | 17.3209 | 17.3241 | 16.888 | 15.9331 | 14.5385 | 14.9892 | 15.0085 | 15.5661 | 13.4279 | 13.5475 | 14.1193 |  |  |  | 16.6355 | 15.9835 | 15.0919 | 10.2451 | 9.6597 | 9.8032 | 17.2191 | 16.3723 | 15.2039 | 16.915 | 16.2064 | 15.2122 | 10.8277 | 11.406 |  | 12.2545 | 10.5425 | 10.3981 | 8.3765 |  | 6.2717 | 6.2749 | 5.7902 | 5.8817 | 5.867 | 5.9931 | 6.3795 | 4.7602 | 6.5331 | 4.4643 | 6.7066 | 8.1121 | 43.2742 | 47.2458 | 43.7665 | 15.3647 |  |  | 0.058047 | -0.13199 | 0.10699 | 0.041398 | -0.035976 | 0.011368 | 0.4198 | 0.12206 | -0.35474 | -0.23284 | -0.43307 | 8.8698 | 8.8708 | 2.0084 | 15.7698 | 16.7212 | 17.2791 | 17.6161 | 17.5844 | 16.5822 | 14.9455 | 16.8834 | 17.2158 | 17.5071 | 17.5548 | 17.3034 | 16.5199 | 14.7686 | 5.9386 | 8.2864 | 5.3311 | 5.5198 | 5.8166 | 6.6658 | 7.7261 | 15.8134 | 15.5014 | 15.3945 | 14.3424 | 14.2323 | 14.1789 |  |  |  | 10.7331 | 9.3719 | 8.9819 | 8.9799 | -0.1438 | 0.047075 | 12.6893 |  |  | 10.6466 |  |  | 16.9354 | 16.1418 | 15.1305 | 16.4327 | 15.7276 | 14.8367 | 10.6929 | 10.6297 | 11.5714 | 11.5085 | 8.8644 |  | 10.6389 | 8.3955 | 9.9667 | 9.3202 | 11.1156 | 12.0959 |  | 12.3466 |  |  | 11.7279 | 12.4536 | 12.3829 | [6 empty] | 12.6134 |  |  | 11.3938 |  |  | 9.028 | 10.2043 | 11.9457 | 7.5953 | 9.1385 | 12.558 | 7.7638 | 9.4316 | 12.3879 | 9.2229 | 10.4385 | 7.7774 | 10.4193 | 8.2007 | 10.1564 | 7.9689 | 9.7052 | 13.1971 | 10.4461 | 10.1487 | 11.4489 | 8.2615 | 9.7412 | 12.7031 | 8.1518 | 10.4177 | 9.7588 | 9.8271 | 8.5523 | 10.2831 | -0.14215 | 20.9555 | 0.034009 | 0.048688 | -38.0508 | 3.1212 | -0.68 | 0.37 | 0.28243 | -0.42323 | 0.38104 | 0.23702 | -0.22084 | 0.12414 | 0.7544 | 0.41705 | 0.40793 | 0.42011 | 0.4284 | 0.61901 | 0.43683 | 0.41695
42810.4344 | -490 | 18.5194 | 18.6288 | 18.624 | 18.6288 | 17.9898 | 16.6467 | 14.7258 | 16.7346 | 17.224 | 17.3143 | 17.3312 | 16.8863 | 15.9355 | 14.5426 | 14.9817 | 15.0034 | 15.5537 | 13.4222 | 13.539 | 14.1139 |  |  |  | 16.6369 | 15.9694 | 15.0885 | 10.2381 | 9.6514 | 9.7902 | 17.2212 | 16.3847 | 15.1942 | 16.9175 | 16.2121 | 15.2213 | 10.8391 | 11.4218 |  | 12.2644 | 10.5309 | 10.4167 | 8.3741 |  | 6.2692 | 6.2766 | 5.8012 | 5.8853 | 5.8759 | 5.9934 | 6.3809 | 4.7416 | 6.5418 | 4.5321 | 6.7118 | 8.1099 | 43.2748 | 47.2382 | 43.7553 | 15.3598 |  |  | 0.035047 | -0.31796 | 0.074132 | 0.082138 | -0.016264 | -0.11808 | 0.51705 | 0.28831 | -0.66766 | -0.72629 | -0.2759 | 8.8687 | 8.8699 | 2.0084 | 15.7643 | 16.7112 | 17.2723 | 17.6049 | 17.5805 | 16.5748 | 14.9379 | 16.881 | 17.2161 | 17.5068 | 17.554 | 17.2892 | 16.5166 | 14.7605 | 5.9132 | 8.3177 | 5.3226 | 5.566 | 5.8438 | 6.6708 | 7.7244 | 15.8081 | 15.4953 | 15.3892 | 14.3341 | 14.2256 | 14.1717 |  |  |  | 10.7194 | 9.3733 | 8.9645 | 8.9888 | -0.012918 | -0.1016 | 12.6793 |  |  | 10.6411 |  |  | 16.931 | 16.1341 | 15.1217 | 16.4321 | 15.7235 | 14.8331 | 10.6991 | 10.6279 | 11.573 | 11.5121 | 8.8398 |  | 10.6376 | 8.3836 | 9.9642 | 9.3433 | 11.1215 | 12.1058 |  | 12.3546 |  |  | 11.7186 | 12.4873 | 12.3826 | [6 empty] | 12.6202 |  |  | 11.3923 |  |  | 9.0235 | 10.2048 | 11.9357 | 7.547 | 9.1436 | 12.5348 | 7.7673 | 9.4238 | 12.379 | 9.2115 | 10.4485 | 7.7704 | 10.4202 | 8.2038 | 10.1598 | 7.947 | 9.7085 | 13.1841 | 10.4416 | 10.1448 | 11.4365 | 8.2575 | 9.7375 | 12.6963 | 8.1323 | 10.4129 | 9.7391 | 9.8343 | 8.5606 | 10.2811 | -0.14793 | 20.9551 | 0.034296 | 0.049456 | -38.0252 | 3.1213 | -0.9 | 0.38 | 0.21945 | -0.65688 | 0.31718 | 0.33387 | -0.14849 | -0.40011 | 0.83724 | 0.41769 | 0.40818 | 0.41966 | 0.4318 | 0.61975 | 0.43727 | 0.41625
42810.4344 | -489 | 18.5326 | 18.63 | 18.6177 | 18.6392 | 17.9963 | 16.646 | 14.7233 | 16.7393 | 17.2181 | 17.3232 | 17.3251 | 16.8859 | 15.9313 | 14.551 | 14.9808 | 14.9989 | 15.5584 | 13.4283 | 13.541 | 14.1152 |  |  |  | 16.6288 | 15.9734 | 15.0956 | 10.2403 | 9.6523 | 9.7966 | 17.2073 | 16.3782 | 15.1938 | 16.9109 | 16.2026 | 15.2074 | 10.816 | 11.4261 |  | 12.2445 | 10.4957 | 10.3973 | 8.3575 |  | 6.2739 | 6.2834 | 5.8028 | 5.881 | 5.8764 | 5.9923 | 6.3923 | 4.6697 | 6.532 | 4.5448 | 6.7162 | 8.1102 | 43.2635 | 47.2097 | 43.7434 | 15.3475 |  |  | -0.085205 | -0.28445 | 0.039308 | 0.14128 | 0.021848 | -0.36516 | 0.26209 | 0.54524 | -0.2407 | -0.29977 | -0.31127 | 8.8687 | 8.8697 | 2.0084 | 15.769 | 16.7153 | 17.2828 | 17.6118 | 17.588 | 16.5876 | 14.9407 | 16.8885 | 17.2211 | 17.5125 | 17.5636 | 17.3043 | 16.5278 | 14.7724 | 5.8987 | 8.3304 | 5.297 | 5.5998 | 5.8357 | 6.6678 | 7.7247 | 15.8126 | 15.4944 | 15.3965 | 14.3403 | 14.2312 | 14.1823 |  |  |  | 10.7183 | 9.377 | 8.9695 | 8.9888 | 0.049888 | 0.036536 | 12.6746 |  |  | 10.6506 |  |  | 16.9391 | 16.1387 | 15.131 | 16.4391 | 15.7217 | 14.8419 | 10.705 | 10.6275 | 11.573 | 11.5173 | 8.8366 |  | 10.6378 | 8.348 | 9.9668 | 9.319 | 11.1203 | 12.1098 |  | 12.3575 |  |  | 11.7376 | 12.5122 | 12.3836 | [6 empty] | 12.62 |  |  | 11.4099 |  |  | 9.0328 | 10.2181 | 11.9416 | 7.5337 | 9.163 | 12.5299 | 7.7739 | 9.4264 | 12.3793 | 9.2142 | 10.4471 | 7.7577 | 10.4196 | 8.2126 | 10.161 | 7.9459 | 9.7061 | 13.1889 | 10.4475 | 10.1325 | 11.4522 | 8.2645 | 9.7471 | 12.6973 | 8.1277 | 10.4007 | 9.7446 | 9.8362 | 8.5812 | 10.2839 | 0.092821 | 20.9555 | 0.034182 | 0.049962 | -38.1097 | 3.1213 | -0.96 | 0.27 | -0.34218 | -0.62131 | 0.23097 | 0.43787 | 0.1721 | -0.70359 | 0.59608 | 0.41779 | 0.40926 | 0.4203 | 0.43306 | 0.62263 | 0.43697 | 0.41621
42810.4344 | -488 | 18.5298 | 18.6254 | 18.6158 | 18.6292 | 17.9901 | 16.6474 | 14.7229 | 16.7301 | 17.2128 | 17.312 | 17.3262 | 16.8824 | 15.9271 | 14.5449 | 14.9868 | 15.01 | 15.5582 | 13.4239 | 13.5422 | 14.1163 |  |  |  | 16.6381 | 15.9745 | 15.0906 | 10.2226 | 9.6495 | 9.7818 | 17.214 | 16.3824 | 15.1977 | 16.9205 | 16.2127 | 15.2093 | 10.8257 | 11.4387 |  | 12.2463 | 10.485 | 10.3973 | 8.352 |  | 6.2794 | 6.2809 | 5.7971 | 5.8859 | 5.8835 | 5.9894 | 6.3706 | 4.6624 | 6.5302 | 4.521 | 6.728 | 8.1128 | 43.2565 | 47.2069 | 43.7238 | 15.331 |  |  | 0.025847 | 0.12363 | 0.1221 | 0.072942 | 0.2157 | -0.15422 | 0.47828 | 0.55181 | 0.084277 | -0.67867 | -0.3526 | 8.8706 | 8.8716 | 2.0085 | 15.7701 | 16.7161 | 17.2864 | 17.6117 | 17.59 | 16.5876 | 14.9371 | 16.8891 | 17.2237 | 17.5074 | 17.56 | 17.3084 | 16.5296 | 14.7737 | 5.9242 | 8.3507 | 5.2859 | 5.6179 | 5.8191 | 6.6733 | 7.7172 | 15.8217 | 15.4984 | 15.3927 | 14.3397 | 14.234 | 14.1828 |  |  |  | 10.7212 | 9.3835 | 8.9735 | 9.0076 | 0.12323 | -0.0080678 | 12.678 |  |  | 10.6232 |  |  | 16.9415 | 16.1428 | 15.1265 | 16.4389 | 15.7216 | 14.8352 | 10.7036 | 10.6285 | 11.5743 | 11.5201 | 8.838 |  | 10.6389 | 8.3589 | 9.9643 | 9.2958 | 11.119 | 12.1348 |  | 12.3611 |  |  | 11.7559 | 12.5392 | 12.3746 | [6 empty] | 12.617 |  |  | 11.3969 |  |  | 9.0359 | 10.2313 | 11.9475 | 7.5195 | 9.1547 | 12.5239 | 7.7835 | 9.4234 | 12.3901 | 9.2214 | 10.4506 | 7.7332 | 10.4127 | 8.217 | 10.1545 | 7.9268 | 9.7152 | 13.1854 | 10.45 | 10.1273 | 11.4402 | 8.2651 | 9.7418 | 12.6965 | 8.1124 | 10.4115 | 9.7297 | 9.8373 | 8.5904 | 10.2702 | -0.022161 | 20.954 | 0.033108 | 0.047661 | -38.0955 | 3.1212 | -0.89 | 0.36 | 0.18846 | 0.4096 | 0.40707 | 0.31462 | 0.54076 | -0.45725 | 0.80523 | 0.41778 | 0.40887 | 0.4209 | 0.43086 | 0.62298 | 0.43744 | 0.41579
42810.4344 | -487 | 18.5269 | 18.6171 | 18.6167 | 18.6272 | 17.9874 | 16.6448 | 14.7173 | 16.7287 | 17.2188 | 17.3082 | 17.3243 | 16.8814 | 15.9253 | 14.5411 | 14.9883 | 15.0027 | 15.5555 | 13.4209 | 13.5398 | 14.1149 |  |  |  | 16.6332 | 15.969 | 15.0898 | 10.2304 | 9.6391 | 9.7704 | 17.2208 | 16.3877 | 15.199 | 16.9294 | 16.2165 | 15.2237 | 10.834 | 11.4167 |  | 12.252 | 10.4823 | 10.4064 | 8.3554 |  | 6.2691 | 6.2658 | 5.7976 | 5.8769 | 5.8716 | 5.9779 | 6.3394 | 4.7054 | 6.5235 | 4.4625 | 6.7092 | 8.1097 | 43.2494 | 47.2014 | 43.7115 | 15.3238 |  |  | 0.086303 | -0.10176 | 0.10436 | 0.11631 | 0.15656 | 0.12768 | 0.4106 | 0.50253 | -0.5291 | 0.45279 | -0.34147 | 8.8692 | 8.8701 | 2.0085 | 15.7701 | 16.7159 | 17.2796 | 17.6125 | 17.5927 | 16.5773 | 14.9454 | 16.8879 | 17.2196 | 17.5186 | 17.5608 | 17.307 | 16.5251 | 14.7726 | 5.9913 | 8.3504 | 5.2747 | 5.638 | 5.8121 | 6.6726 | 7.7183 | 15.8111 | 15.4998 | 15.3906 | 14.3365 | 14.2275 | 14.176 |  |  |  | 10.7225 | 9.3948 | 8.9739 | 9.0335 | 0.11918 | -0.044579 | 12.6817 |  |  | 10.604 |  |  | 16.9287 | 16.1328 | 15.1243 | 16.4316 | 15.7114 | 14.8393 | 10.6984 | 10.6231 | 11.5756 | 11.5275 | 8.8701 |  | 10.6313 | 8.3261 | 9.9612 | 9.2585 | 11.1064 | 12.2102 |  | 12.3427 |  |  | 11.7389 | 12.5426 | 12.376 | [6 empty] | 12.6275 |  |  | 11.3794 |  |  | 9.0369 | 10.2383 | 11.9657 | 7.5298 | 9.1444 | 12.5151 | 7.7878 | 9.4272 | 12.3766 | 9.2251 | 10.4524 | 7.7199 | 10.3974 | 8.2204 | 10.1541 | 7.925 | 9.7233 | 13.1872 | 10.444 | 10.1317 | 11.4228 | 8.2705 | 9.7537 | 12.7049 | 8.1212 | 10.4105 | 9.7165 | 9.8315 | 8.5959 | 10.2675 | -0.13387 | 20.9545 | 0.032402 | 0.047777 | -38.1185 | 3.1212 | -0.98 | 0.37 | 0.34436 | -0.37161 | 0.37632 | 0.39728 | 0.46068 | 0.41603 | 0.74607 | 0.41664 | 0.40968 | 0.42152 | 0.42333 | 0.62436 | 0.43762 | 0.41511
42810.4344 | -486 | 18.5297 | 18.6233 | 18.6214 | 18.6314 | 17.9912 | 16.651 | 14.7186 | 16.7339 | 17.2199 | 17.3149 | 17.3289 | 16.8826 | 15.9262 | 14.5383 | 14.9755 | 15.0016 | 15.5553 | 13.418 | 13.5402 | 14.113 |  |  |  | 16.6321 | 15.9724 | 15.0892 | 10.2267 | 9.6308 | 9.7737 | 17.2222 | 16.3755 | 15.2004 | 16.9205 | 16.2053 | 15.2175 | 10.8247 | 11.3975 |  | 12.2462 | 10.4609 | 10.3886 | 8.3578 |  | 6.2775 | 6.2763 | 5.7987 | 5.8929 | 5.8864 | 5.9823 | 6.3286 | 4.7655 | 6.5263 | 4.5083 | 6.7109 | 8.1109 | 43.2467 | 47.2199 | 43.6869 | 15.3113 |  |  | -0.009637 | 0.1072 | 0.076104 | 0.14391 | 0.22358 | -0.20351 | 0.452 | 0.1812 | -0.47714 | -0.35369 | -0.2767 | 8.8698 | 8.871 | 2.0083 | 15.7659 | 16.7142 | 17.2739 | 17.6124 | 17.5848 | 16.5833 | 14.9409 | 16.8895 | 17.2204 | 17.5095 | 17.5534 | 17.3049 | 16.5262 | 14.7651 | 6.0252 | 8.3529 | 5.2805 | 5.6271 | 5.7904 | 6.6729 | 7.7249 | 15.8096 | 15.5051 | 15.3976 | 14.3408 | 14.2206 | 14.1783 |  |  |  | 10.7266 | 9.3911 | 8.9721 | 9.0647 | -0.16912 | -0.096145 | 12.6789 |  |  | 10.601 |  |  | 16.9314 | 16.1332 | 15.1209 | 16.4277 | 15.7215 | 14.8319 | 10.6936 | 10.6111 | 11.5808 | 11.5292 | 8.8998 |  | 10.6274 | 8.2281 | 9.9606 | 9.2471 | 11.1189 | 12.2939 |  | 12.3506 |  |  | 11.7358 | 12.495 | 12.369 | [6 empty] | 12.6191 |  |  | 11.3652 |  |  | 9.0531 | 10.2337 | 11.9739 | 7.5485 | 9.1332 | 12.503 | 7.7865 | 9.4224 | 12.3823 | 9.2246 | 10.449 | 7.7203 | 10.3813 | 8.2175 | 10.1495 | 7.9317 | 9.7248 | 13.1788 | 10.4435 | 10.1344 | 11.4225 | 8.2787 | 9.761 | 12.6987 | 8.1211 | 10.4183 | 9.7189 | 9.8305 | 8.6003 | 10.2679 | -0.11673 | 20.9552 | 0.033114 | 0.048066 | -38.0872 | 3.1213 | -0.94 | 0.35 | -0.11507 | 0.38141 | 0.32137 | 0.44192 | 0.55054 | -0.52525 | 0.78278 | 0.41569 | 0.41238 | 0.42225 | 0.4196 | 0.62449 | 0.43725 | 0.41438
42810.4344 | -485 | 18.5325 | 18.6247 | 18.62 | 18.6302 | 17.9898 | 16.6517 | 14.7229 | 16.7358 | 17.213 | 17.3141 | 17.3244 | 16.8833 | 15.9289 | 14.5397 | 14.9735 | 14.9988 | 15.5512 | 13.4197 | 13.5336 | 14.1113 |  |  |  | 16.6298 | 15.9666 | 15.0883 | 10.2211 | 9.6312 | 9.7647 | 17.2186 | 16.3777 | 15.2031 | 16.9153 | 16.2057 | 15.2187 | 10.8215 | 11.421 |  | 12.239 | 10.4503 | 10.3828 | 8.3638 |  | 6.2739 | 6.2735 | 5.8067 | 5.8943 | 5.9053 | 5.9903 | 6.3432 | 4.7923 | 6.5298 | 4.5285 | 6.7148 | 8.1089 | 43.2435 | 47.2291 | 43.668 | 15.2938 |  |  | 0.13427 | 0.087483 | 0.044564 | -0.13274 | 0.19861 | 0.003484 | 0.45528 | -0.1099 | -0.071403 | -0.41243 | -0.43109 | 8.8682 | 8.8694 | 2.0085 | 15.7569 | 16.7015 | 17.2651 | 17.5972 | 17.5753 | 16.5726 | 14.9318 | 16.8756 | 17.2137 | 17.4987 | 17.5459 | 17.2901 | 16.5097 | 14.7554 | 6.0362 | 8.3334 | 5.2809 | 5.6 | 5.7791 | 6.6723 | 7.7176 | 15.8103 | 15.4919 | 15.3869 | 14.3311 | 14.2218 | 14.1735 |  |  |  | 10.7138 | 9.3974 | 8.9684 | 9.0673 | -0.14582 | -0.13153 | 12.6813 |  |  | 10.6022 |  |  | 16.9383 | 16.1407 | 15.1186 | 16.4372 | 15.7179 | 14.8328 | 10.7026 | 10.6087 | 11.574 | 11.5102 | 8.9114 |  | 10.6394 | 8.0802 | 9.9704 | 9.2474 | 11.1145 | 12.3827 |  | 12.3556 |  |  | 11.7494 | 12.5009 | 12.3609 | [6 empty] | 12.5962 |  |  | 11.3641 |  |  | 9.0642 | 10.2454 | 11.9791 | 7.5536 | 9.134 | 12.4907 | 7.7891 | 9.4252 | 12.3762 | 9.2224 | 10.4544 | 7.7185 | 10.387 | 8.2248 | 10.1469 | 7.9367 | 9.7403 | 13.178 | 10.4543 | 10.1369 | 11.4208 | 8.2836 | 9.7683 | 12.703 | 8.1264 | 10.4153 | 9.7196 | 9.8245 | 8.6119 | 10.2658 | -0.15428 | 20.9558 | 0.033407 | 0.048812 | -38.0935 | 3.1213 | -0.9 | 0.28 | 0.42952 | 0.34456 | 0.24592 | -0.42442 | 0.5189 | 0.068725 | 0.78563 | 0.41576 | 0.41681 | 0.4221 | 0.4183 | 0.62359 | 0.43698 | 0.41389
42810.4344 | -484 | 18.5321 | 18.6273 | 18.6202 | 18.6273 | 17.9911 | 16.6478 | 14.7229 | 16.733 | 17.2232 | 17.314 | 17.3218 | 16.8853 | 15.9247 | 14.549 | 14.9759 | 15.0058 | 15.5584 | 13.4222 | 13.537 | 14.1072 |  |  |  | 16.6276 | 15.9683 | 15.089 | 10.2133 | 9.6285 | 9.767 | 17.2247 | 16.3894 | 15.2008 | 16.9224 | 16.2177 | 15.2277 | 10.8202 | 11.4201 |  | 12.2508 | 10.4561 | 10.3786 | 8.3711 |  | 6.2684 | 6.279 | 5.8086 | 5.9008 | 5.9013 | 6.0299 | 6.3424 | 4.8169 | 6.5227 | 4.5919 | 6.7066 | 8.1134 | 43.2335 | 47.2379 | 43.6641 | 15.293 |  |  | 0.042275 | -0.048537 | 0.14576 | 0.17413 | 0.15984 | -0.010972 | 0.41783 | 0.103 | 0.16893 | -0.43949 | -0.31982 | 8.8691 | 8.8703 | 2.0084 | 15.7621 | 16.7057 | 17.2718 | 17.6057 | 17.585 | 16.5776 | 14.9318 | 16.8826 | 17.2149 | 17.5074 | 17.5557 | 17.2939 | 16.5191 | 14.7653 | 6.0654 | 8.32 | 5.3547 | 5.5391 | 5.7725 | 6.6711 | 7.7142 | 15.8046 | 15.4832 | 15.3781 | 14.325 | 14.2239 | 14.1641 |  |  |  | 10.7128 | 9.3964 | 8.9554 | 9.0839 | -0.031557 | -0.045896 | 12.6982 |  |  | 10.6111 |  |  | 16.9417 | 16.138 | 15.1203 | 16.4323 | 15.7245 | 14.8397 | 10.7174 | 10.615 | 11.5801 | 11.5151 | 8.893 |  | 10.6308 | 7.9165 | 9.9727 | 9.2572 | 11.1122 | 12.4447 |  | 12.3413 |  |  | 11.7427 | 12.4939 | 12.3634 | [6 empty] | 12.5935 |  |  | 11.381 |  |  | 9.0656 | 10.2417 | 11.9913 | 7.5609 | 9.146 | 12.4818 | 7.7963 | 9.4343 | 12.3708 | 9.2307 | 10.4502 | 7.7236 | 10.3805 | 8.2309 | 10.1402 | 7.9529 | 9.7446 | 13.1845 | 10.4557 | 10.1397 | 11.4314 | 8.2783 | 9.7775 | 12.6947 | 8.1307 | 10.4071 | 9.7221 | 9.8264 | 8.6191 | 10.2637 | 0.014818 | 20.9566 | 0.033194 | 0.050136 | -38.0446 | 3.1212 | -0.62 | 0.23 | 0.24101 | -0.25665 | 0.44476 | 0.48612 | 0.46554 | -0.12197 | 0.75268 | 0.41599 | 0.42144 | 0.42175 | 0.41493 | 0.61499 | 0.43673 | 0.41339
42810.4344 | -483 | 18.519 | 18.6221 | 18.613 | 18.6245 | 17.9899 | 16.6395 | 14.7136 | 16.724 | 17.2131 | 17.3061 | 17.3213 | 16.8762 | 15.9189 | 14.5461 | 14.9794 | 15.0018 | 15.5567 | 13.422 | 13.5403 | 14.1119 |  |  |  | 16.6321 | 15.9722 | 15.097 | 10.216 | 9.6333 | 9.7868 | 17.2185 | 16.3819 | 15.1957 | 16.9192 | 16.2062 | 15.212 | 10.8208 | 11.3721 |  | 12.2486 | 10.459 | 10.3654 | 8.3417 |  | 6.2745 | 6.2811 | 5.8074 | 5.9005 | 5.9118 | 6.0665 | 6.3309 | 4.8067 | 6.5228 | 4.6293 | 6.7032 | 8.1065 | 43.2059 | 47.2324 | 43.6505 | 15.2687 |  |  | -0.020809 | -0.013053 | 0.04982 | 0.00657 | 0.20518 | -0.10691 | 0.24172 | -0.090844 | -0.61064 | -1.0815 | -0.26815 | 8.8683 | 8.8697 | 2.0085 | 15.7613 | 16.7007 | 17.2701 | 17.6024 | 17.5833 | 16.5721 | 14.9299 | 16.8823 | 17.2133 | 17.5057 | 17.5528 | 17.2975 | 16.5212 | 14.759 | 6.0527 | 8.2951 | 5.4119 | 5.5693 | 5.7428 | 6.6629 | 7.7102 | 15.8022 | 15.4928 | 15.3843 | 14.3267 | 14.2236 | 14.1688 |  |  |  | 10.7138 | 9.3959 | 8.9666 | 9.1182 | -0.023655 | -0.06321 | 12.6708 |  |  | 10.6125 |  |  | 16.9402 | 16.1419 | 15.1182 | 16.4392 | 15.7155 | 14.8326 | 10.7115 | 10.6082 | 11.5761 | 11.5041 | 8.8695 |  | 10.6356 | 7.9233 | 9.9654 | 9.2607 | 11.115 | 12.4609 |  | 12.3538 |  |  | 11.722 | 12.5085 | 12.3654 | [6 empty] | 12.6028 |  |  | 11.392 |  |  | 9.0797 | 10.2539 | 11.9991 | 7.5825 | 9.1663 | 12.4853 | 7.8156 | 9.4414 | 12.3723 | 9.2337 | 10.4541 | 7.731 | 10.3816 | 8.23 | 10.1486 | 7.9554 | 9.7612 | 13.1826 | 10.4492 | 10.1409 | 11.4322 | 8.2735 | 9.7752 | 12.6854 | 8.1366 | 10.4029 | 9.7244 | 9.8355 | 8.6179 | 10.2604 | 0.1246 | 20.957 | 0.033946 | 0.050512 | -38.0057 | 3.1212 | -0.65 | 0.31 | -0.1691 | -0.13309 | 0.26002 | 0.094425 | 0.52748 | -0.38076 | 0.57252 | 0.4168 | 0.42101 | 0.42174 | 0.41538 | 0.60818 | 0.43757 | 0.41247
42810.4345 | -482 | 18.5388 | 18.6217 | 18.6234 | 18.637 | 17.9893 | 16.6508 | 14.7187 | 16.7344 | 17.2258 | 17.3071 | 17.3305 | 16.8767 | 15.9298 | 14.5527 | 14.976 | 15.0016 | 15.559 | 13.4213 | 13.5343 | 14.1102 |  |  |  | 16.6329 | 15.9718 | 15.0888 | 10.2141 | 9.6221 | 9.7982 | 17.2184 | 16.3769 | 15.1963 | 16.9098 | 16.2006 | 15.2181 | 10.8215 | 11.3498 |  | 12.2465 | 10.4449 | 10.3647 | 8.3339 |  | 6.2665 | 6.2792 | 5.8095 | 5.8938 | 5.9196 | 6.0687 | 6.3221 | 4.7887 | 6.5185 | 4.6327 | 6.704 | 8.1104 | 43.1941 | 47.2388 | 43.6489 | 15.2677 |  |  | 0.1691 | 0.021771 | 0.01762 | -0.10645 | 0.15196 | -0.075372 | 0.28969 | -0.15064 | -0.3452 | -0.16235 | -0.25623 | 8.8694 | 8.8706 | 2.0086 | 15.7709 | 16.7112 | 17.276 | 17.6139 | 17.5881 | 16.579 | 14.9382 | 16.8909 | 17.2235 | 17.5102 | 17.5583 | 17.3083 | 16.5236 | 14.7696 | 6.0937 | 8.2904 | 5.4198 | 5.6367 | 5.6989 | 6.674 | 7.7146 | 15.8126 | 15.4951 | 15.3873 | 14.3303 | 14.2294 | 14.1761 |  |  |  | 10.715 | 9.4075 | 8.9738 | 9.144 | -0.19445 | -0.085042 | 12.6854 |  |  | 10.6139 |  |  | 16.9356 | 16.1398 | 15.1266 | 16.4321 | 15.7127 | 14.8293 | 10.6861 | 10.597 | 11.5607 | 11.4946 | 8.8738 |  | 10.6377 | 7.9371 | 9.9594 | 9.2689 | 11.1215 | 12.4791 |  | 12.3557 |  |  | 11.721 | 12.5243 | 12.3526 | [6 empty] | 12.6058 |  |  | 11.4006 |  |  | 9.0803 | 10.2543 | 12 | 7.5933 | 9.1733 | 12.4822 | 7.8119 | 9.4466 | 12.3735 | 9.2329 | 10.448 | 7.7387 | 10.3857 | 8.2218 | 10.1362 | 7.9606 | 9.774 | 13.1716 | 10.4504 | 10.1394 | 11.4352 | 8.278 | 9.7677 | 12.6828 | 8.1463 | 10.4048 | 9.7208 | 9.8387 | 8.6163 | 10.2555 | 0.022907 | 20.957 | 0.031897 | 0.048131 | -38.0181 | 3.1212 | -0.64 | 0.25 | 0.48205 | 0.17189 | 0.15463 | -0.38009 | 0.45394 | -0.3197 | 0.62676 | 0.41675 | 0.42043 | 0.42173 | 0.41211 | 0.60781 | 0.43781 | 0.41179
42810.4345 | -481 | 18.5323 | 18.6181 | 18.6181 | 18.6366 | 17.9953 | 16.6503 | 14.723 | 16.7303 | 17.2189 | 17.3111 | 17.3319 | 16.8781 | 15.9298 | 14.551 | 14.9808 | 14.9995 | 15.5602 | 13.425 | 13.5395 | 14.1131 |  |  |  | 16.633 | 15.9774 | 15.0871 | 10.2172 | 9.62 | 9.8104 | 17.2281 | 16.3825 | 15.1933 | 16.9237 | 16.21 | 15.2225 | 10.8214 | 11.3303 |  | 12.249 | 10.4585 | 10.3672 | 8.3575 |  | 6.2814 | 6.2971 | 5.8197 | 5.893 | 5.9356 | 6.085 | 6.3284 | 4.7303 | 6.5321 | 4.6412 | 6.7127 | 8.1114 | 43.1825 | 47.2511 | 43.6556 | 15.2619 |  |  | 0.067903 | 0.050027 | 0.2647 | 0.050598 | -0.092488 | -0.08654 | 0.31729 | -0.2985 | -0.15099 | -0.52719 | -0.27789 | 8.8683 | 8.8696 | 2.0082 | 15.7659 | 16.7109 | 17.2698 | 17.6073 | 17.5831 | 16.5725 | 14.928 | 16.8783 | 17.2194 | 17.5063 | 17.5582 | 17.3039 | 16.5171 | 14.7656 | 6.1405 | 8.3036 | 5.4144 | 5.7424 | 5.6976 | 6.6699 | 7.7232 | 15.8113 | 15.4969 | 15.3855 | 14.3281 | 14.2267 | 14.1697 |  |  |  | 10.7231 | 9.4187 | 8.9703 | 9.1348 | -0.030949 | -0.086735 | 12.6809 |  |  | 10.6103 |  |  | 16.9416 | 16.1337 | 15.118 | 16.4326 | 15.7172 | 14.8365 | 10.6723 | 10.6015 | 11.5651 | 11.4923 | 8.8882 |  | 10.6233 | 7.9341 | 9.9507 | 9.2669 | 11.1142 | 12.464 |  | 12.3547 |  |  | 11.716 | 12.5241 | 12.3256 | [6 empty] | 12.5935 |  |  | 11.4024 |  |  | 9.0764 | 10.2536 | 12.0122 | 7.6022 | 9.189 | 12.4827 | 7.8023 | 9.4454 | 12.3737 | 9.2304 | 10.4524 | 7.7449 | 10.3878 | 8.2123 | 10.1399 | 7.9693 | 9.7722 | 13.1656 | 10.4498 | 10.1315 | 11.4247 | 8.2725 | 9.768 | 12.6778 | 8.1551 | 10.3959 | 9.7112 | 9.8351 | 8.6083 | 10.2499 | 0.047753 | 20.9573 | 0.03215 | 0.047227 | -37.937 | 3.1212 | -0.69 | 0.35 | 0.30547 | 0.26057 | 0.59936 | 0.26205 | -0.35416 | -0.34258 | 0.65596 | 0.41587 | 0.42022 | 0.42154 | 0.40644 | 0.60942 | 0.43715 | 0.41231
42810.4345 | -480 | 18.5265 | 18.6141 | 18.6153 | 18.6286 | 17.9842 | 16.644 | 14.7122 | 16.7263 | 17.2118 | 17.3067 | 17.319 | 16.8813 | 15.9261 | 14.5436 | 14.9867 | 15.0061 | 15.5571 | 13.4246 | 13.5407 | 14.1173 |  |  |  | 16.6323 | 15.9815 | 15.0905 | 10.2209 | 9.6148 | 9.8132 | 17.2225 | 16.3739 | 15.1921 | 16.9106 | 16.2052 | 15.2154 | 10.822 | 11.2981 |  | 12.2417 | 10.4388 | 10.3599 | 8.3739 |  | 6.2845 | 6.2869 | 5.8039 | 5.8825 | 5.9303 | 6.0798 | 6.3188 | 4.7145 | 6.5334 | 4.6392 | 6.7108 | 8.1093 | 43.1553 | 47.2673 | 43.6644 | 15.2527 |  |  | 0.078415 | -0.18851 | 0.097788 | 0.025626 | 0.11187 | 0.13096 | 0.32517 | -0.21701 | -0.63866 | -0.476 | -0.19801 | 8.8684 | 8.8695 | 2.0084 | 15.763 | 16.7049 | 17.2721 | 17.6084 | 17.5863 | 16.5742 | 14.9304 | 16.8876 | 17.2191 | 17.5107 | 17.5567 | 17.2993 | 16.5247 | 14.7615 | 6.1655 | 8.2918 | 5.4581 | 5.7779 | 5.7805 | 6.6632 | 7.7189 | 15.8105 | 15.4994 | 15.3812 | 14.3321 | 14.2293 | 14.1767 |  |  |  | 10.7304 | 9.4268 | 8.9786 | 9.1299 | -0.032367 | -0.062646 | 12.6803 |  |  | 10.6183 |  |  | 16.9402 | 16.1335 | 15.1324 | 16.4464 | 15.7258 | 14.8401 | 10.6522 | 10.5982 | 11.5633 | 11.5022 | 8.8858 |  | 10.6325 | 7.9624 | 9.9531 | 9.2539 | 11.1112 | 12.4332 |  | 12.3583 |  |  | 11.6998 | 12.4944 | 12.2855 | [6 empty] | 12.5778 |  |  | 11.3954 |  |  | 9.0805 | 10.267 | 12.0173 | 7.6188 | 9.2007 | 12.498 | 7.7976 | 9.4561 | 12.3742 | 9.2286 | 10.4594 | 7.7513 | 10.4042 | 8.2056 | 10.1373 | 7.9872 | 9.7779 | 13.1714 | 10.4594 | 10.1327 | 11.4241 | 8.2775 | 9.7699 | 12.6744 | 8.1656 | 10.3995 | 9.7065 | 9.8273 | 8.6065 | 10.25 | -0.056444 | 20.9568 | 0.031174 | 0.047878 | -37.9242 | 3.1212 | -0.9 | 0.42 | 0.32827 | -0.50579 | 0.36429 | 0.18649 | 0.3895 | 0.42143 | 0.66406 | 0.41625 | 0.41952 | 0.42181 | 0.40288 | 0.60406 | 0.43671 | 0.41269
42810.4345 | -479 | 18.5293 | 18.622 | 18.6153 | 18.637 | 17.9905 | 16.637 | 14.7163 | 16.7308 | 17.2141 | 17.3117 | 17.3204 | 16.8814 | 15.9284 | 14.5396 | 14.9848 | 15.0052 | 15.5546 | 13.426 | 13.5346 | 14.1129 |  |  |  | 16.6344 | 15.9757 | 15.0897 | 10.2201 | 9.6101 | 9.8117 | 17.2209 | 16.3748 | 15.1948 | 16.9113 | 16.2008 | 15.2115 | 10.8179 | 11.2972 |  | 12.2383 | 10.4401 | 10.3529 | 8.3798 |  | 6.2825 | 6.2822 | 5.8035 | 5.8807 | 5.9083 | 6.0606 | 6.3013 | 4.7243 | 6.5275 | 4.6158 | 6.7092 | 8.1114 | 43.1304 | 47.2649 | 43.6663 | 15.2386 |  |  | 0.052131 | -0.031453 | 0.074792 | 0.20239 | 0.16773 | 0.12176 | 0.52231 | -0.013964 | -0.10604 | -0.66482 | -0.34068 | 8.869 | 8.87 | 2.0086 | 15.768 | 16.7022 | 17.2737 | 17.6033 | 17.5805 | 16.5718 | 14.9386 | 16.8829 | 17.2048 | 17.5039 | 17.5435 | 17.3039 | 16.5206 | 14.7643 | 6.1272 | 8.313 | 5.475 | 5.7548 | 5.8034 | 6.6685 | 7.7202 | 15.812 | 15.4953 | 15.3854 | 14.3299 | 14.2284 | 14.1744 |  |  |  | 10.7226 | 9.4351 | 8.9888 | 9.1335 | 0.18138 | -0.13698 | 12.6738 |  |  | 10.6032 |  |  | 16.9322 | 16.1262 | 15.1148 | 16.4193 | 15.7121 | 14.8289 | 10.6218 | 10.5845 | 11.5525 | 11.4926 | 8.8266 |  | 10.6267 | 8.0198 | 9.9537 | 9.2366 | 11.1155 | 12.4209 |  | 12.3551 |  |  | 11.6892 | 12.4666 | 12.2824 | [6 empty] | 12.5768 |  |  | 11.3947 |  |  | 9.0863 | 10.2701 | 12.021 | 7.6237 | 9.2065 | 12.5046 | 7.7928 | 9.4544 | 12.3723 | 9.2271 | 10.461 | 7.7611 | 10.4059 | 8.1976 | 10.1333 | 8.0024 | 9.777 | 13.1692 | 10.4663 | 10.135 | 11.4221 | 8.287 | 9.7668 | 12.6709 | 8.171 | 10.3972 | 9.7045 | 9.827 | 8.6009 | 10.2499 | -0.069733 | 20.9575 | 0.033045 | 0.047502 | -37.925 | 3.1211 | -0.89 | 0.35 | 0.26766 | -0.2066 | 0.31859 | 0.52408 | 0.47691 | 0.40634 | 0.84158 | 0.4177 | 0.41794 | 0.42243 | 0.40775 | 0.60233 | 0.43641 | 0.41234
42810.4345 | -478 | 18.5311 | 18.6249 | 18.6124 | 18.636 | 17.9924 | 16.6409 | 14.7147 | 16.7326 | 17.2088 | 17.3055 | 17.3237 | 16.8799 | 15.9328 | 14.5391 | 14.989 | 15.0087 | 15.559 | 13.4237 | 13.5405 | 14.1152 |  |  |  | 16.6343 | 15.9678 | 15.0886 | 10.2228 | 9.6169 | 9.8189 | 17.2274 | 16.3792 | 15.1973 | 16.918 | 16.2007 | 15.2158 | 10.8228 | 11.2955 |  | 12.2353 | 10.4499 | 10.3588 | 8.3986 |  | 6.2904 | 6.292 | 5.8097 | 5.8847 | 5.9087 | 6.0566 | 6.2912 | 4.7766 | 6.532 | 4.6012 | 6.7171 | 8.1127 | 43.105 | 47.2614 | 43.6575 | 15.2291 |  |  | -0.014237 | 0.15582 | 0.22001 | 0.02497 | 0.045504 | 0.015968 | 0.41848 | -0.024476 | -0.013801 | 0.44586 | -0.23875 | 8.8696 | 8.8708 | 2.0085 | 15.7719 | 16.7124 | 17.2729 | 17.6073 | 17.5852 | 16.5847 | 14.9405 | 16.8862 | 17.2228 | 17.5164 | 17.5613 | 17.3104 | 16.5254 | 14.7742 | 6.1298 | 8.3362 | 5.4436 | 5.7301 | 5.7877 | 6.6763 | 7.7293 | 15.8081 | 15.4928 | 15.3877 | 14.3281 | 14.2233 | 14.1712 |  |  |  | 10.7159 | 9.4444 | 8.9953 | 9.1388 | 0.20467 | -0.058317 | 12.6584 |  |  | 10.6104 |  |  | 16.9348 | 16.1281 | 15.1204 | 16.4287 | 15.7125 | 14.8252 | 10.6228 | 10.5812 | 11.557 | 11.4979 | 8.7739 |  | 10.623 | 8.1049 | 9.9528 | 9.2167 | 11.1143 | 12.3999 |  | 12.3569 |  |  | 11.677 | 12.4352 | 12.2859 | [6 empty] | 12.5844 |  |  | 11.3915 |  |  | 9.092 | 10.2767 | 12.0274 | 7.6345 | 9.2152 | 12.514 | 7.7907 | 9.4616 | 12.3685 | 9.2289 | 10.4579 | 7.7648 | 10.4091 | 8.1844 | 10.1294 | 8.0171 | 9.7553 | 13.1693 | 10.4611 | 10.137 | 11.4197 | 8.287 | 9.7652 | 12.6768 | 8.1527 | 10.3949 | 9.7013 | 9.8199 | 8.5967 | 10.2442 | -0.19935 | 20.9579 | 0.033786 | 0.049666 | -38.0051 | 3.1211 | -0.8 | 0.36 | -0.13988 | 0.45986 | 0.54643 | 0.18409 | 0.2484 | 0.14715 | 0.7533 | 0.41904 | 0.41554 | 0.42294 | 0.40837 | 0.60687 | 0.43605 | 0.41197
42810.4345 | -477 | 18.5278 | 18.628 | 18.6241 | 18.6343 | 17.9891 | 16.6498 | 14.7193 | 16.7309 | 17.218 | 17.3132 | 17.3288 | 16.8784 | 15.941 | 14.5455 | 14.9799 | 15.006 | 15.5542 | 13.4242 | 13.5371 | 14.1098 |  |  |  | 16.6306 | 15.9708 | 15.0873 | 10.2186 | 9.6093 | 9.8248 | 17.2228 | 16.3741 | 15.1949 | 16.9144 | 16.2045 | 15.2192 | 10.8199 | 11.2852 |  | 12.2326 | 10.4374 | 10.3574 | 8.4082 |  | 6.3001 | 6.2946 | 5.8145 | 5.8806 | 5.9082 | 6.0532 | 6.2764 | 4.7939 | 6.5262 | 4.6924 | 6.7185 | 8.1086 | 43.0924 | 47.2334 | 43.6572 | 15.225 |  |  | -0.020809 | -0.11031 | 0.091876 | 0.08871 | 0.021192 | 0.19733 | 0.6051 | 0.013636 | -0.24518 | -1.268 | -0.33293 | 8.8678 | 8.8687 | 2.0087 | 15.7699 | 16.712 | 17.2749 | 17.6146 | 17.5866 | 16.5824 | 14.9338 | 16.8937 | 17.2201 | 17.5188 | 17.5628 | 17.3 | 16.5331 | 14.7773 | 6.1458 | 8.3243 | 5.4118 | 5.7021 | 5.7201 | 6.6689 | 7.719 | 15.8124 | 15.5013 | 15.3861 | 14.3361 | 14.2247 | 14.1711 |  |  |  | 10.7271 | 9.4509 | 9.0057 | 9.1371 | 0.29078 | -0.053236 | 12.6787 |  |  | 10.6087 |  |  | 16.9343 | 16.1228 | 15.1205 | 16.4314 | 15.7199 | 14.8238 | 10.6311 | 10.5733 | 11.5574 | 11.5035 | 8.7545 |  | 10.629 | 8.1749 | 9.9442 | 9.1942 | 11.1134 | 12.3795 |  | 12.3462 |  |  | 11.6894 | 12.4286 | 12.2714 | [6 empty] | 12.5835 |  |  | 11.3916 |  |  | 9.0999 | 10.2828 | 12.0335 | 7.6466 | 9.2195 | 12.5241 | 7.79 | 9.4688 | 12.3614 | 9.2265 | 10.4585 | 7.7715 | 10.4191 | 8.1836 | 10.1267 | 7.9946 | 9.7194 | 13.1672 | 10.4596 | 10.1369 | 11.4242 | 8.2888 | 9.7616 | 12.6787 | 8.1205 | 10.386 | 9.6992 | 9.813 | 8.5841 | 10.2419 | -0.10286 | 20.9593 | 0.033722 | 0.050245 | -38.0479 | 3.1211 | -0.77 | 0.34 | -0.16911 | -0.38692 | 0.35311 | 0.34698 | 0.16952 | 0.51728 | 0.90582 | 0.41978 | 0.41332 | 0.42354 | 0.40572 | 0.60921 | 0.43569 | 0.41239
42810.4345 | -476 | 18.5326 | 18.6282 | 18.6223 | 18.6371 | 17.9892 | 16.6489 | 14.7219 | 16.7319 | 17.2145 | 17.3148 | 17.3368 | 16.8878 | 15.9325 | 14.5534 | 14.981 | 15.0071 | 15.5621 | 13.4278 | 13.5325 | 14.114 |  |  |  | 16.6317 | 15.9729 | 15.0939 | 10.2167 | 9.6149 | 9.8358 | 17.2213 | 16.3794 | 15.2002 | 16.9152 | 16.2052 | 15.2107 | 10.8211 | 11.2933 |  | 12.2332 | 10.4271 | 10.3501 | 8.4342 |  | 6.3076 | 6.3075 | 5.8196 | 5.8852 | 5.9208 | 6.0475 | 6.2671 | 4.7301 | 6.5312 | 4.7245 | 6.7172 | 8.1088 | 43.102 | 47.2126 | 43.6605 | 15.2088 |  |  | 0.15333 | 0.049371 | 0.1175 | 0.021686 | -0.051748 | 0.066568 | 0.41717 | 0.058976 | -0.67466 | -0.22592 | -0.28246 | 8.869 | 8.8701 | 2.0084 | 15.7691 | 16.701 | 17.2742 | 17.607 | 17.5794 | 16.5676 | 14.9275 | 16.8858 | 17.2182 | 17.5096 | 17.5601 | 17.3025 | 16.5209 | 14.7689 | 6.1852 | 8.3428 | 5.4003 | 5.7027 | 5.7053 | 6.6807 | 7.7204 | 15.8082 | 15.4964 | 15.3826 | 14.3294 | 14.2281 | 14.1776 |  |  |  | 10.7236 | 9.4625 | 9.0147 | 9.1081 | 0.10864 | 0.028443 | 12.6754 |  |  | 10.623 |  |  | 16.9303 | 16.1336 | 15.1209 | 16.4209 | 15.7184 | 14.8313 | 10.624 | 10.5811 | 11.55 | 11.4955 | 8.744 |  | 10.6241 | 8.2192 | 9.9419 | 9.1735 | 11.1103 | 12.3605 |  | 12.3394 |  |  | 11.7048 | 12.4332 | 12.2407 | [6 empty] | 12.6032 |  |  | 11.393 |  |  | 9.1031 | 10.2919 | 12.0451 | 7.6672 | 9.2242 | 12.5388 | 7.8031 | 9.4752 | 12.3461 | 9.2427 | 10.4647 | 7.7961 | 10.4354 | 8.1885 | 10.1279 | 7.9867 | 9.6936 | 13.1705 | 10.4645 | 10.1349 | 11.4281 | 8.2951 | 9.7667 | 12.6836 | 8.089 | 10.3804 | 9.696 | 9.8143 | 8.5867 | 10.2498 | 0.15638 | 20.9593 | 0.033303 | 0.050672 | -38.1094 | 3.1211 | -0.67 | 0.35 | 0.45905 | 0.25886 | 0.39935 | 0.17156 | -0.26489 | 0.30044 | 0.7521 | 0.41991 | 0.41201 | 0.42401 | 0.40271 | 0.61065 | 0.43501 | 0.41307
42810.4345 | -475 | 18.5329 | 18.6236 | 18.6183 | 18.6323 | 17.9864 | 16.6495 | 14.7163 | 16.7391 | 17.2154 | 17.3109 | 17.3301 | 16.8782 | 15.9405 | 14.5558 | 15 | 15.0148 | 15.5631 | 13.4271 | 13.5442 | 14.1205 |  |  |  | 16.6391 | 15.976 | 15.0887 | 10.219 | 9.6113 | 9.8591 | 17.2242 | 16.3774 | 15.2046 | 16.9189 | 16.2049 | 15.2185 | 10.8184 | 11.2987 |  | 12.2348 | 10.4338 | 10.3476 | 8.4853 |  | 6.3162 | 6.3053 | 5.819 | 5.8776 | 5.9216 | 6.0448 | 6.2859 | 4.6335 | 6.5292 | 4.7324 | 6.7146 | 8.1107 | 43.1115 | 47.2004 | 43.6541 | 15.1929 |  |  | -0.021465 | -0.039997 | 0.12933 | -0.025626 | -0.045176 | -0.056316 | 0.48617 | -0.11582 | -0.89709 | -0.41033 | -0.21252 | 8.8687 | 8.8696 | 2.0084 | 15.768 | 16.6995 | 17.271 | 17.6046 | 17.5747 | 16.5718 | 14.9311 | 16.8847 | 17.2172 | 17.5099 | 17.5569 | 17.2987 | 16.519 | 14.7733 | 6.1834 | 8.3698 | 5.3874 | 5.6774 | 5.7251 | 6.6741 | 7.7112 | 15.817 | 15.4969 | 15.3863 | 14.3318 | 14.2316 | 14.1788 |  |  |  | 10.7206 | 9.471 | 9.0136 | 9.1191 | 0.025779 | -0.034039 | 12.6928 |  |  | 10.6183 |  |  | 16.9346 | 16.1376 | 15.1279 | 16.4269 | 15.7245 | 14.8277 | 10.6314 | 10.5817 | 11.55 | 11.5083 | 8.7507 |  | 10.6278 | 8.2609 | 9.9412 | 9.1728 | 11.1121 | 12.3602 |  | 12.3482 |  |  | 11.7176 | 12.428 | 12.2484 | [6 empty] | 12.6192 |  |  | 11.3777 |  |  | 9.0986 | 10.3003 | 12.0431 | 7.6864 | 9.229 | 12.5474 | 7.8005 | 9.4862 | 12.3557 | 9.2354 | 10.4604 | 7.7935 | 10.4425 | 8.1895 | 10.1255 | 7.9775 | 9.6702 | 13.1703 | 10.472 | 10.1367 | 11.4194 | 8.2886 | 9.7611 | 12.6927 | 8.0392 | 10.3662 | 9.6999 | 9.8212 | 8.5829 | 10.2526 | -0.198 | 20.9588 | 0.033022 | 0.049267 | -38.1212 | 3.1211 | -0.76 | 0.39 | -0.17176 | -0.23299 | 0.41896 | -0.18649 | -0.2475 | -0.27634 | 0.81192 | 0.41985 | 0.41083 | 0.42409 | 0.40216 | 0.61103 | 0.4335 | 0.41267
42810.4345 | -474 | 18.5394 | 18.6266 | 18.6183 | 18.6416 | 17.994 | 16.645 | 14.7237 | 16.737 | 17.2195 | 17.3102 | 17.3286 | 16.881 | 15.9323 | 14.5554 | 14.9863 | 15.011 | 15.5618 | 13.4192 | 13.5376 | 14.1013 |  |  |  | 16.6329 | 15.9761 | 15.0832 | 10.2218 | 9.6019 | 9.8456 | 17.2238 | 16.3675 | 15.1958 | 16.9111 | 16.2044 | 15.2083 | 10.8139 | 11.3135 |  | 12.2353 | 10.4211 | 10.3395 | 8.4947 |  | 6.3344 | 6.3139 | 5.8229 | 5.8844 | 5.9188 | 6.0991 | 6.3869 | 4.5302 | 6.515 | 4.6925 | 6.722 | 8.1159 | 43.1082 | 47.1992 | 43.6598 | 15.1914 |  |  | 0.056731 | -0.048537 | 0.16876 | 0.10054 | 0.085588 | 0.15725 | 0.44148 | -0.000164 | 0.013248 | -0.95917 | -0.3375 | 8.8699 | 8.8712 | 2.0087 | 15.7684 | 16.701 | 17.2665 | 17.6012 | 17.5722 | 16.5696 | 14.9283 | 16.8791 | 17.2191 | 17.5073 | 17.5578 | 17.2972 | 16.5266 | 14.7661 | 6.1973 | 8.3746 | 5.3922 | 5.668 | 5.7192 | 6.6736 | 7.7116 | 15.8252 | 15.4984 | 15.3966 | 14.3391 | 14.2351 | 14.1765 |  |  |  | 10.7305 | 9.4821 | 9.0209 | 9.1324 | 0.20528 | 0.061943 | 12.6743 |  |  | 10.6256 |  |  | 16.9314 | 16.1361 | 15.1254 | 16.4268 | 15.7169 | 14.834 | 10.6266 | 10.5762 | 11.5447 | 11.5052 | 8.7972 |  | 10.6228 | 8.3231 | 9.9392 | 9.1783 | 11.1073 | 12.351 |  | 12.3468 |  |  | 11.7243 | 12.4265 | 12.2534 | [6 empty] | 12.586 |  |  | 11.3539 |  |  | 9.098 | 10.2777 | 12.032 | 7.6818 | 9.2028 | 12.5507 | 7.7892 | 9.4791 | 12.3384 | 9.2259 | 10.4498 | 7.7862 | 10.4398 | 8.1825 | 10.1162 | 7.9397 | 9.6432 | 13.1561 | 10.4642 | 10.1251 | 11.4128 | 8.2837 | 9.7564 | 12.6823 | 7.9977 | 10.3654 | 9.6961 | 9.8018 | 8.5653 | 10.2303 | -0.11172 | 20.9584 | 0.032047 | 0.047784 | -38.0492 | 3.1211 | -0.64 | 0.33 | 0.27923 | -0.25666 | 0.47859 | 0.3694 | 0.3407 | 0.4618 | 0.77379 | 0.41839 | 0.40904 | 0.42378 | 0.40055 | 0.61053 | 0.43309 | 0.41263
42810.4346 | -473 | 18.5423 | 18.6266 | 18.6247 | 18.6319 | 17.9958 | 16.6538 | 14.7115 | 16.7357 | 17.2216 | 17.3137 | 17.3271 | 16.8867 | 15.9346 | 14.5587 | 14.9853 | 15.0055 | 15.5689 | 13.4262 | 13.541 | 14.1175 |  |  |  | 16.631 | 15.979 | 15.0896 | 10.228 | 9.6048 | 9.866 | 17.2267 | 16.3716 | 15.194 | 16.9179 | 16.205 | 15.2149 | 10.8183 | 11.3311 |  | 12.236 | 10.4179 | 10.3351 | 8.5214 |  | 6.3417 | 6.3202 | 5.819 | 5.8886 | 5.9431 | 6.1503 | 6.465 | 4.4889 | 6.5153 | 4.6142 | 6.7203 | 8.1087 | 43.0879 | 47.1973 | 43.6544 | 15.1852 |  |  | 0.033075 | -0.083365 | 0.047848 | -0.063742 | -0.068832 | -0.0688 | 0.45725 | -0.022504 | -0.58048 | -0.47474 | -0.28703 | 8.8702 | 8.8718 | 2.0085 | 15.7794 | 16.7051 | 17.2649 | 17.6114 | 17.5793 | 16.5757 | 14.9384 | 16.8859 | 17.2213 | 17.5098 | 17.5668 | 17.3079 | 16.5302 | 14.7692 | 6.2568 | 8.3644 | 5.3881 | 5.6701 | 5.7061 | 6.6783 | 7.7157 | 15.8201 | 15.4906 | 15.3897 | 14.3372 | 14.2298 | 14.176 |  |  |  | 10.7274 | 9.4759 | 9.02 | 9.1214 | 0.050496 | -0.11101 | 12.6748 |  |  | 10.6224 |  |  | 16.9266 | 16.1326 | 15.1164 | 16.4239 | 15.7154 | 14.8263 | 10.6247 | 10.5655 | 11.532 | 11.4933 | 8.8808 |  | 10.6206 | 8.3888 | 9.9379 | 9.2008 | 11.1138 | 12.3368 |  | 12.348 |  |  | 11.7394 | 12.4356 | 12.2736 | [6 empty] | 12.6074 |  |  | 11.3476 |  |  | 9.0999 | 10.2937 | 12.0355 | 7.6895 | 9.2044 | 12.5467 | 7.7933 | 9.4812 | 12.3342 | 9.2325 | 10.4445 | 7.8123 | 10.4338 | 8.1778 | 10.1192 | 7.9182 | 9.6429 | 13.1523 | 10.4567 | 10.1321 | 11.4339 | 8.2886 | 9.759 | 12.6855 | 7.9657 | 10.3676 | 9.6982 | 9.8047 | 8.5683 | 10.2386 | -0.074163 | 20.9589 | 0.032965 | 0.047277 | -38.106 | 3.1211 | -0.54 | 0.35 | 0.21322 | -0.33638 | 0.25484 | -0.29414 | -0.30556 | -0.30549 | 0.78755 | 0.41599 | 0.40717 | 0.42337 | 0.39448 | 0.61146 | 0.43249 | 0.41283
42810.4346 | -472 | 18.5433 | 18.6239 | 18.6191 | 18.6376 | 17.9926 | 16.6497 | 14.7128 | 16.7365 | 17.2226 | 17.319 | 17.3273 | 16.8882 | 15.9345 | 14.5569 | 14.9943 | 15.0036 | 15.5619 | 13.4218 | 13.5443 | 14.1152 |  |  |  | 16.6275 | 15.9728 | 15.0867 | 10.2213 | 9.6072 | 9.8719 | 17.2391 | 16.3857 | 15.2104 | 16.9264 | 16.2137 | 15.2221 | 10.8253 | 11.3813 |  | 12.2377 | 10.4218 | 10.3408 | 8.5403 |  | 6.3521 | 6.3327 | 5.8293 | 5.8887 | 5.9713 | 6.1783 | 6.5352 | 4.4905 | 6.5164 | 4.5455 | 6.7184 | 8.107 | 43.072 | 47.189 | 43.6441 | 15.1775 |  |  | 0.10864 | -0.11754 | 0.18782 | 0.036142 | -0.08526 | -0.32968 | 0.55976 | 0.091176 | -0.64061 | -1.1098 | -0.38201 | 8.8695 | 8.8708 | 2.0085 | 15.7785 | 16.7029 | 17.275 | 17.6066 | 17.5751 | 16.5706 | 14.937 | 16.8881 | 17.2198 | 17.5086 | 17.5607 | 17.303 | 16.5252 | 14.7702 | 6.2864 | 8.3541 | 5.3904 | 5.6679 | 5.7051 | 6.6832 | 7.713 | 15.8227 | 15.491 | 15.3922 | 14.3302 | 14.2272 | 14.1713 |  |  |  | 10.7231 | 9.4809 | 9.0258 | 9.0947 | 0.065894 | -0.065092 | 12.6793 |  |  | 10.6285 |  |  | 16.935 | 16.1361 | 15.1225 | 16.4297 | 15.7189 | 14.8424 | 10.6412 | 10.5665 | 11.5392 | 11.4848 | 8.9466 |  | 10.6227 | 8.4626 | 9.9493 | 9.2245 | 11.1138 | 12.3316 |  | 12.3437 |  |  | 11.7662 | 12.4581 | 12.2736 | [6 empty] | 12.6192 |  |  | 11.3382 |  |  | 9.0974 | 10.2924 | 12.0391 | 7.691 | 9.1982 | 12.5577 | 7.7904 | 9.4833 | 12.3257 | 9.225 | 10.4399 | 7.8032 | 10.4327 | 8.1789 | 10.1143 | 7.9086 | 9.6447 | 13.1551 | 10.4738 | 10.1383 | 11.4393 | 8.2889 | 9.762 | 12.685 | 7.9796 | 10.3637 | 9.7056 | 9.8112 | 8.5721 | 10.2225 | -0.1408 | 20.9579 | 0.034078 | 0.049745 | -38.1274 | 3.1211 | -0.52 | 0.33 | 0.38644 | -0.39942 | 0.50491 | 0.22149 | -0.34009 | -0.66876 | 0.87142 | 0.41424 | 0.4055 | 0.42271 | 0.39177 | 0.6109 | 0.4322 | 0.41343
42810.4346 | -471 | 18.54 | 18.6206 | 18.615 | 18.6319 | 17.9884 | 16.6447 | 14.7095 | 16.7264 | 17.2159 | 17.3092 | 17.3266 | 16.881 | 15.932 | 14.5498 | 14.9887 | 14.9993 | 15.5614 | 13.4237 | 13.534 | 14.1133 |  |  |  | 16.629 | 15.9764 | 15.0854 | 10.2223 | 9.6078 | 9.8539 | 17.2385 | 16.3891 | 15.2096 | 16.9238 | 16.2121 | 15.2232 | 10.8214 | 11.4262 |  | 12.2357 | 10.4136 | 10.3299 | 8.5345 |  | 6.3652 | 6.3408 | 5.8284 | 5.9076 | 5.9963 | 6.1901 | 6.5948 | 4.5006 | 6.5179 | 4.4549 | 6.7161 | 8.1178 | 43.062 | 47.1869 | 43.6433 | 15.1754 |  |  | -0.073377 | 0.12954 | 0.083332 | 0.24773 | 0.11384 | -0.46701 | 0.60248 | 0.10892 | -0.21502 | -0.18585 | 0.06904 | 8.8717 | 8.8728 | 2.0086 | 15.7794 | 16.6998 | 17.2663 | 17.604 | 17.5747 | 16.5694 | 14.9373 | 16.885 | 17.2189 | 17.5104 | 17.5538 | 17.306 | 16.527 | 14.7696 | 6.3201 | 8.327 | 5.387 | 5.6352 | 5.7328 | 6.6766 | 7.7003 | 15.8273 | 15.497 | 15.3936 | 14.3304 | 14.2233 | 14.1748 |  |  |  | 10.7245 | 9.4834 | 9.0386 | 9.0739 | -0.038243 | -0.089935 | 12.6803 |  |  | 10.6268 |  |  | 16.9368 | 16.1383 | 15.1208 | 16.4312 | 15.7284 | 14.8409 | 10.6492 | 10.5698 | 11.5315 | 11.4654 | 8.9622 |  | 10.631 | 8.5099 | 9.9438 | 9.2189 | 11.1001 | 12.2719 |  | 12.3511 |  |  | 11.7934 | 12.4559 | 12.2812 | [6 empty] | 12.6026 |  |  | 11.3463 |  |  | 9.0997 | 10.2949 | 12.0458 | 7.7028 | 9.2006 | 12.5697 | 7.8046 | 9.4945 | 12.3107 | 9.2292 | 10.4475 | 7.7993 | 10.4243 | 8.1753 | 10.1177 | 7.8996 | 9.6561 | 13.1555 | 10.4688 | 10.1393 | 11.4501 | 8.3077 | 9.7654 | 12.6709 | 7.9935 | 10.363 | 9.7118 | 9.8037 | 8.5748 | 10.2395 | 0.031189 | 20.9584 | 0.034308 | 0.049608 | -38.0913 | 3.1211 | -0.65 | 0.26 | -0.31757 | 0.41933 | 0.33632 | 0.57989 | 0.393 | -0.79597 | 0.90407 | 0.41407 | 0.404 | 0.42241 | 0.38726 | 0.6098 | 0.43223 | 0.41406
42810.4346 | -470 | 18.5385 | 18.6178 | 18.6166 | 18.6308 | 17.9964 | 16.6435 | 14.7063 | 16.73 | 17.2137 | 17.3067 | 17.3261 | 16.8759 | 15.9311 | 14.5447 | 14.9908 | 14.9988 | 15.5592 | 13.424 | 13.5333 | 14.1167 |  |  |  | 16.6334 | 15.9714 | 15.0855 | 10.2182 | 9.6064 | 9.843 | 17.2375 | 16.3862 | 15.2065 | 16.9209 | 16.2107 | 15.2224 | 10.8213 | 11.4759 |  | 12.2319 | 10.4098 | 10.316 | 8.5278 |  | 6.3761 | 6.3418 | 5.8348 | 5.8955 | 6.0217 | 6.181 | 6.6249 | 4.5364 | 6.5124 | 4.4079 | 6.7135 | 8.1214 | 43.0319 | 47.1907 | 43.6249 | 15.1669 |  |  | -0.13449 | 0.047399 | 0.039308 | 0.10843 | -0.29488 | 0.071824 | 0.67279 | 0.17397 | -0.40806 | -0.60733 | -0.057333 | 8.8699 | 8.871 | 2.0082 | 15.7798 | 16.7054 | 17.2683 | 17.6116 | 17.5783 | 16.5785 | 14.9406 | 16.887 | 17.2166 | 17.51 | 17.5572 | 17.3044 | 16.529 | 14.7701 | 6.3516 | 8.3417 | 5.3713 | 5.6094 | 5.7511 | 6.6847 | 7.7072 | 15.8214 | 15.4943 | 15.3878 | 14.3308 | 14.2302 | 14.1724 |  |  |  | 10.7279 | 9.4838 | 9.0338 | 9.0712 | -0.051614 | 0.015457 | 12.687 |  |  | 10.6057 |  |  | 16.9369 | 16.1403 | 15.117 | 16.4325 | 15.7192 | 14.8385 | 10.6586 | 10.5662 | 11.5283 | 11.4544 | 9.0078 |  | 10.6247 | 8.5404 | 9.9345 | 9.2223 | 11.1053 | 12.1826 |  | 12.3584 |  |  | 11.8107 | 12.4642 | 12.3081 | [6 empty] | 12.6071 |  |  | 11.3504 |  |  | 9.1008 | 10.2918 | 12.0391 | 7.7134 | 9.1996 | 12.5775 | 7.8126 | 9.5062 | 12.3164 | 9.2325 | 10.4458 | 7.7914 | 10.4181 | 8.1747 | 10.1212 | 7.8919 | 9.6569 | 13.141 | 10.466 | 10.1438 | 11.4482 | 8.2956 | 9.7561 | 12.6748 | 7.992 | 10.3619 | 9.7069 | 9.8012 | 8.5653 | 10.2294 | -0.086875 | 20.9585 | 0.033757 | 0.050462 | -38.1488 | 3.121 | -0.37 | 0.37 | -0.42993 | 0.25365 | 0.23099 | 0.38364 | -0.63248 | 0.31215 | 0.95536 | 0.4126 | 0.40285 | 0.42249 | 0.3847 | 0.61234 | 0.43241 | 0.41424
42810.4346 | -469 | 18.542 | 18.622 | 18.6146 | 18.632 | 17.9997 | 16.6439 | 14.7199 | 16.7355 | 17.2157 | 17.3138 | 17.3297 | 16.8727 | 15.9359 | 14.5534 | 14.9924 | 15.0021 | 15.5595 | 13.4264 | 13.5429 | 14.1219 |  |  |  | 16.6371 | 15.9765 | 15.0895 | 10.22 | 9.6122 | 9.8602 | 17.2331 | 16.3826 | 15.1955 | 16.9141 | 16.2053 | 15.2197 | 10.8173 | 11.5074 |  | 12.2218 | 10.4004 | 10.309 | 8.5083 |  | 6.3669 | 6.346 | 5.8503 | 5.9054 | 6.0428 | 6.1796 | 6.6933 | 4.6378 | 6.5063 | 4.3491 | 6.7165 | 8.1184 | 42.9986 | 47.2068 | 43.6059 | 15.1539 |  |  | 0.031103 | 0.11705 | 0.02222 | 0.18662 | 0.15064 | 0.31036 | 0.50982 | 0.092488 | -0.049024 | -0.6344 | -0.21311 | 8.8701 | 8.8716 | 2.0086 | 15.7788 | 16.7115 | 17.2701 | 17.6077 | 17.5773 | 16.5794 | 14.9351 | 16.8831 | 17.2242 | 17.5145 | 17.5634 | 17.3064 | 16.5306 | 14.7667 | 6.3777 | 8.3508 | 5.4308 | 5.5986 | 5.7514 | 6.6811 | 7.7141 | 15.8215 | 15.4956 | 15.3823 | 14.3316 | 14.226 | 14.1711 |  |  |  | 10.7301 | 9.496 | 9.0462 | 9.1027 | 0.16537 | -0.13586 | 12.6946 |  |  | 10.5979 |  |  | 16.9332 | 16.135 | 15.1205 | 16.431 | 15.7142 | 14.8266 | 10.6705 | 10.5567 | 11.4943 | 11.4281 | 9.0306 |  | 10.6244 | 8.6258 | 9.9362 | 9.2438 | 11.1064 | 12.1587 |  | 12.356 |  |  | 11.824 | 12.4824 | 12.3197 | [6 empty] | 12.6199 |  |  | 11.3574 |  |  | 9.1105 | 10.3049 | 12.0424 | 7.7076 | 9.2029 | 12.5826 | 7.8167 | 9.5117 | 12.3256 | 9.235 | 10.4481 | 7.7907 | 10.4014 | 8.1818 | 10.1223 | 7.8761 | 9.656 | 13.1311 | 10.4566 | 10.1531 | 11.452 | 8.2917 | 9.7527 | 12.6705 | 7.9959 | 10.3572 | 9.7076 | 9.8092 | 8.5585 | 10.2154 | -0.084949 | 20.9577 | 0.034302 | 0.049875 | -38.0674 | 3.121 | -0.66 | 0.35 | 0.20676 | 0.39861 | 0.17367 | 0.50331 | 0.45207 | 0.64887 | 0.83164 | 0.41196 | 0.40053 | 0.42193 | 0.38138 | 0.60653 | 0.43283 | 0.41344
42810.4346 | -468 | 18.5478 | 18.6282 | 18.6213 | 18.6374 | 17.9975 | 16.6615 | 14.7185 | 16.7444 | 17.2268 | 17.3229 | 17.3339 | 16.8884 | 15.9468 | 14.5652 | 14.9935 | 15.0079 | 15.5586 | 13.4265 | 13.5359 | 14.1112 |  |  |  | 16.6414 | 15.9762 | 15.0865 | 10.2209 | 9.6142 | 9.8582 | 17.2357 | 16.3891 | 15.1977 | 16.9199 | 16.2081 | 15.2176 | 10.8219 | 11.5504 |  | 12.2328 | 10.4081 | 10.304 | 8.4719 |  | 6.3727 | 6.3489 | 5.8656 | 5.9267 | 6.051 | 6.2207 | 6.7571 | 4.6986 | 6.5142 | 4.3521 | 6.723 | 8.1229 | 42.9682 | 47.2248 | 43.5857 | 15.1482 |  |  | 0.11127 | -0.009769 | 0.26535 | 0.12157 | 0.13882 | 0.21968 | 0.69053 | -0.01002 | -0.064981 | 1.3499 | -0.24987 | 8.8695 | 8.8701 | 2.0087 | 15.7836 | 16.7108 | 17.2716 | 17.6051 | 17.5831 | 16.5861 | 14.9368 | 16.8835 | 17.2217 | 17.5162 | 17.5692 | 17.3167 | 16.5312 | 14.7642 | 6.3833 | 8.3315 | 5.5402 | 5.6061 | 5.7408 | 6.6792 | 7.7098 | 15.8321 | 15.5002 | 15.395 | 14.3358 | 14.2321 | 14.1883 |  |  |  | 10.737 | 9.5071 | 9.0548 | 9.1363 | 0.17935 | -0.062081 | 12.6913 |  |  | 10.6126 |  |  | 16.9392 | 16.1255 | 15.1247 | 16.4274 | 15.7179 | 14.8349 | 10.6784 | 10.564 | 11.4971 | 11.4049 | 9.0267 |  | 10.6325 | 8.6784 | 9.9423 | 9.2782 | 11.1137 | 12.1205 |  | 12.3546 |  |  | 11.8416 | 12.4994 | 12.3315 | [6 empty] | 12.6275 |  |  | 11.3665 |  |  | 9.1089 | 10.3078 | 12.0468 | 7.6972 | 9.208 | 12.578 | 7.818 | 9.519 | 12.3167 | 9.2348 | 10.4533 | 7.7658 | 10.3978 | 8.1806 | 10.1306 | 7.8599 | 9.6623 | 13.1218 | 10.455 | 10.153 | 11.4611 | 8.292 | 9.7488 | 12.6548 | 8.005 | 10.3535 | 9.7012 | 9.8171 | 8.5674 | 10.2196 | 0.005188 | 20.9596 | 0.032316 | 0.047364 | -38.1531 | 3.121 | -0.51 | 0.35 | 0.39107 | -0.11515 | 0.60016 | 0.40622 | 0.43399 | 0.54594 | 0.96794 | 0.41233 | 0.39927 | 0.42121 | 0.38054 | 0.59388 | 0.43399 | 0.41273
42810.4346 | -467 | 18.5402 | 18.6208 | 18.6127 | 18.6336 | 17.9924 | 16.6577 | 14.7136 | 16.7351 | 17.2142 | 17.3152 | 17.3374 | 16.8813 | 15.9321 | 14.547 | 15.003 | 15.0067 | 15.5605 | 13.4235 | 13.5424 | 14.1155 |  |  |  | 16.6413 | 15.9797 | 15.0936 | 10.2247 | 9.6221 | 9.8655 | 17.2331 | 16.3845 | 15.1975 | 16.919 | 16.2132 | 15.225 | 10.8182 | 11.5997 |  | 12.2311 | 10.4118 | 10.3135 | 8.4408 |  | 6.3728 | 6.3452 | 5.8688 | 5.949 | 6.0707 | 6.2801 | 6.8272 | 4.762 | 6.5059 | 4.3827 | 6.7228 | 8.13 | 42.9466 | 47.2462 | 43.5815 | 15.1468 |  |  | -0.024753 | 0.17751 | 0.17599 | 0.039426 | 0.12567 | -0.0642 | 0.6327 | -0.084932 | -0.25355 | -0.3669 | -0.10522 | 8.8669 | 8.8683 | 2.0084 | 15.7839 | 16.7066 | 17.2681 | 17.6017 | 17.5807 | 16.575 | 14.9411 | 16.8828 | 17.2131 | 17.5147 | 17.56 | 17.31 | 16.5249 | 14.7716 | 6.293 | 8.3092 | 5.5413 | 5.6907 | 5.7366 | 6.6789 | 7.708 | 15.8268 | 15.495 | 15.3853 | 14.3229 | 14.2207 | 14.1704 |  |  |  | 10.7272 | 9.4992 | 9.0521 | 9.1195 | 0.051914 | -0.19909 | 12.685 |  |  | 10.6168 |  |  | 16.9302 | 16.128 | 15.1144 | 16.4293 | 15.7226 | 14.8262 | 10.6824 | 10.5636 | 11.4813 | 11.3936 | 9.0111 |  | 10.621 | 8.7646 | 9.9286 | 9.301 | 11.1062 | 12.0692 |  | 12.3504 |  |  | 11.8479 | 12.5174 | 12.3423 | [6 empty] | 12.6149 |  |  | 11.372 |  |  | 9.0964 | 10.2943 | 12.0333 | 7.6648 | 9.1928 | 12.5676 | 7.8074 | 9.5182 | 12.3024 | 9.227 | 10.4402 | 7.7437 | 10.3932 | 8.1748 | 10.1218 | 7.8452 | 9.6596 | 13.1194 | 10.4639 | 10.1516 | 11.4675 | 8.298 | 9.7528 | 12.6593 | 8.0161 | 10.3519 | 9.7039 | 9.8295 | 8.5685 | 10.2203 | 0.12402 | 20.958 | 0.03386 | 0.048392 | -38.2011 | 3.121 | -0.35 | 0.29 | -0.18445 | 0.49087 | 0.48876 | 0.23134 | 0.41297 | -0.29517 | 0.92662 | 0.41239 | 0.39642 | 0.42033 | 0.39054 | 0.59354 | 0.43473 | 0.41288
42810.4346 | -466 | 18.5455 | 18.6234 | 18.6178 | 18.6452 | 17.9966 | 16.6543 | 14.7142 | 16.7389 | 17.2175 | 17.3189 | 17.3346 | 16.8851 | 15.938 | 14.5519 | 15.0042 | 15.0089 | 15.5649 | 13.4259 | 13.5393 | 14.1209 |  |  |  | 16.6353 | 15.9763 | 15.0955 | 10.2196 | 9.622 | 9.8782 | 17.2455 | 16.389 | 15.2038 | 16.9256 | 16.2126 | 15.2249 | 10.8192 | 11.6609 |  | 12.2394 | 10.4234 | 10.3037 | 8.4055 |  | 6.3717 | 6.3596 | 5.8918 | 5.973 | 6.0953 | 6.3 | 6.8715 | 4.7394 | 6.5078 | 4.4025 | 6.7189 | 8.1249 | 42.9252 | 47.2443 | 43.5783 | 15.1322 |  |  | 0.091559 | -0.13922 | 0.02288 | 0.083454 | 0.19007 | 0.42864 | 0.46054 | -0.034332 | -0.94652 | -0.31844 | -0.3369 | 8.8686 | 8.8696 | 2.0084 | 15.7821 | 16.6979 | 17.2641 | 17.6098 | 17.5752 | 16.5739 | 14.9311 | 16.8791 | 17.2132 | 17.5139 | 17.5534 | 17.3 | 16.5167 | 14.7641 | 6.1762 | 8.3424 | 5.5152 | 5.7351 | 5.7354 | 6.6846 | 7.712 | 15.8318 | 15.4871 | 15.384 | 14.327 | 14.2194 | 14.1744 |  |  |  | 10.7261 | 9.503 | 9.0553 | 9.1143 | 0.17469 | -0.077514 | 12.6933 |  |  | 10.6123 |  |  | 16.9298 | 16.1256 | 15.1143 | 16.4265 | 15.7158 | 14.8254 | 10.6895 | 10.5585 | 11.4631 | 11.3746 | 9.0226 |  | 10.6267 | 8.8535 | 9.9387 | 9.3051 | 11.1045 | 12.0527 |  | 12.3488 |  |  | 11.8508 | 12.5195 | 12.3561 | [6 empty] | 12.6088 |  |  | 11.3617 |  |  | 9.1018 | 10.2903 | 12.0256 | 7.6516 | 9.1922 | 12.5618 | 7.8138 | 9.5245 | 12.2946 | 9.2227 | 10.431 | 7.7403 | 10.3789 | 8.1717 | 10.1167 | 7.8476 | 9.6614 | 13.1119 | 10.4581 | 10.1526 | 11.4608 | 8.3074 | 9.7487 | 12.6643 | 8.0234 | 10.3582 | 9.7165 | 9.8311 | 8.5661 | 10.2083 | -0.066652 | 20.9595 | 0.034394 | 0.049412 | -37.9284 | 3.121 | -0.22 | 0.3 | 0.35476 | -0.43473 | 0.17624 | 0.33658 | 0.5079 | 0.76272 | 0.79059 | 0.41225 | 0.39429 | 0.42016 | 0.40419 | 0.59691 | 0.43574 | 0.41298
42810.4347 | -465 | 18.5535 | 18.6268 | 18.6254 | 18.6449 | 18.0028 | 16.6573 | 14.7141 | 16.738 | 17.2284 | 17.3149 | 17.3343 | 16.8817 | 15.9408 | 14.5497 | 15.0056 | 15.013 | 15.5659 | 13.4271 | 13.54 | 14.1171 |  |  |  | 16.6319 | 15.9736 | 15.0933 | 10.2225 | 9.6173 | 9.8874 | 17.2447 | 16.3832 | 15.1917 | 16.9202 | 16.2112 | 15.2211 | 10.8206 | 11.687 |  | 12.2364 | 10.4161 | 10.2976 | 8.3629 |  | 6.386 | 6.3774 | 5.9132 | 6.0151 | 6.1194 | 6.3216 | 6.929 | 4.6683 | 6.5183 | 4.4528 | 6.7296 | 8.131 | 42.9264 | 47.2372 | 43.5914 | 15.1344 |  |  | 0.15596 | 0.099311 | 0.18782 | 0.037454 | 0.18678 | 0.35504 | -0.10327 | 0.069492 | -0.49894 | -0.14305 | -0.11496 | 8.8675 | 8.8691 | 2.0084 | 15.7894 | 16.7085 | 17.2614 | 17.6024 | 17.5778 | 16.5731 | 14.9279 | 16.8852 | 17.2069 | 17.5091 | 17.5535 | 17.3079 | 16.5241 | 14.7687 | 6.0703 | 8.3679 | 5.5163 | 5.7134 | 5.7173 | 6.6891 | 7.7082 | 15.8298 | 15.4952 | 15.381 | 14.3354 | 14.2264 | 14.1762 |  |  |  | 10.7294 | 9.5181 | 9.0616 | 9.1309 | -0.13772 | 0.0081174 | 12.6986 |  |  | 10.6099 |  |  | 16.9293 | 16.1337 | 15.1184 | 16.4241 | 15.7144 | 14.8278 | 10.6894 | 10.5567 | 11.4569 | 11.3583 | 9.0288 |  | 10.6316 | 8.8576 | 9.932 | 9.2975 | 11.1009 | 11.9905 |  | 12.3468 |  |  | 11.8658 | 12.5298 | 12.3838 | [6 empty] | 12.6177 |  |  | 11.3487 |  |  | 9.1145 | 10.2941 | 12.0228 | 7.6611 | 9.1992 | 12.5742 | 7.8211 | 9.5436 | 12.2992 | 9.2308 | 10.4456 | 7.7577 | 10.3834 | 8.1768 | 10.1327 | 7.8531 | 9.6625 | 13.108 | 10.4461 | 10.1414 | 11.4491 | 8.3003 | 9.7406 | 12.6599 | 8.0224 | 10.3569 | 9.7165 | 9.8286 | 8.5605 | 10.1974 | 0.07568 | 20.958 | 0.034635 | 0.050158 | -38.1153 | 3.121 | -0.28 | 0.37 | 0.46301 | 0.36718 | 0.50495 | 0.22549 | 0.50351 | 0.69418 | -0.37439 | 0.41224 | 0.39395 | 0.42026 | 0.41646 | 0.59634 | 0.43697 | 0.41263
42810.4347 | -464 | 18.5452 | 18.6238 | 18.6227 | 18.6394 | 18.0003 | 16.6434 | 14.7183 | 16.7354 | 17.2268 | 17.3158 | 17.3345 | 16.8827 | 15.9396 | 14.5535 | 15.0116 | 15.0151 | 15.5706 | 13.4303 | 13.5521 | 14.1158 |  |  |  | 16.6355 | 15.9742 | 15.095 | 10.2325 | 9.6137 | 9.8985 | 17.2457 | 16.3863 | 15.1994 | 16.9259 | 16.2113 | 15.2213 | 10.8264 | 11.697 |  | 12.2401 | 10.423 | 10.2989 | 8.3408 |  | 6.3887 | 6.3877 | 5.9361 | 6.031 | 6.1136 | 6.2959 | 6.9522 | 4.6513 | 6.5217 | 4.5451 | 6.7273 | 8.1343 | 42.9348 | 47.2481 | 43.5965 | 15.1253 |  |  | 0.001535 | -0.034741 | 0.09976 | 0.14391 | 0.20913 | 0.05474 | 0.33437 | 0.070804 | 0.52096 | -0.80434 | -0.22563 | 8.8686 | 8.8698 | 2.0085 | 15.7956 | 16.7161 | 17.274 | 17.6048 | 17.5804 | 16.5812 | 14.9414 | 16.8909 | 17.2174 | 17.5104 | 17.5572 | 17.3106 | 16.536 | 14.7761 | 6.0364 | 8.3894 | 5.545 | 5.7153 | 5.7182 | 6.6906 | 7.7103 | 15.8318 | 15.4956 | 15.3839 | 14.3386 | 14.232 | 14.1749 |  |  |  | 10.725 | 9.5266 | 9.0713 | 9.135 | -0.18047 | -0.0005398 | 12.6916 |  |  | 10.6126 |  |  | 16.9266 | 16.134 | 15.116 | 16.4314 | 15.7113 | 14.8296 | 10.6977 | 10.5723 | 11.4402 | 11.3506 | 9.0578 |  | 10.6305 | 8.8143 | 9.9306 | 9.3023 | 11.0965 | 11.9354 |  | 12.3456 |  |  | 11.8832 | 12.5479 | 12.3911 | [6 empty] | 12.6111 |  |  | 11.3585 |  |  | 9.1184 | 10.2955 | 12.02 | 7.6755 | 9.1999 | 12.5703 | 7.8242 | 9.5484 | 12.3032 | 9.2312 | 10.45 | 7.7526 | 10.3875 | 8.1861 | 10.1382 | 7.8722 | 9.6691 | 13.1192 | 10.4502 | 10.1417 | 11.4491 | 8.293 | 9.7347 | 12.6567 | 8.0335 | 10.3627 | 9.7091 | 9.833 | 8.5621 | 10.1959 | -0.012531 | 20.9599 | 0.033757 | 0.048609 | -38.0341 | 3.121 | -0.31 | 0.37 | 0.045936 | -0.21717 | 0.36801 | 0.44201 | 0.53275 | 0.27256 | 0.67364 | 0.4114 | 0.39511 | 0.41998 | 0.42041 | 0.5934 | 0.43778 | 0.41237
42810.4347 | -463 | 18.5484 | 18.6192 | 18.6182 | 18.6367 | 17.9976 | 16.6447 | 14.7211 | 16.7359 | 17.2276 | 17.3188 | 17.3417 | 16.887 | 15.9427 | 14.5582 | 15.0111 | 15.0133 | 15.5657 | 13.4324 | 13.5387 | 14.1196 |  |  |  | 16.631 | 15.9728 | 15.0908 | 10.2311 | 9.6013 | 9.8971 | 17.2473 | 16.3886 | 15.2039 | 16.9292 | 16.2142 | 15.2214 | 10.8234 | 11.7089 |  | 12.2327 | 10.425 | 10.2958 | 8.3233 |  | 6.389 | 6.3869 | 5.9402 | 6.0399 | 6.1097 | 6.2737 | 6.9232 | 4.6025 | 6.5197 | 4.544 | 6.7415 | 8.1281 | 42.9492 | 47.254 | 43.6047 | 15.1082 |  |  | 0.050159 | 0.009943 | 0.19636 | 0.17742 | 0.28667 | 0.18813 | 0.39286 | 0.087888 | -0.41623 | -0.28592 | -0.26736 | 8.8712 | 8.8722 | 2.0086 | 15.7822 | 16.7004 | 17.2625 | 17.6038 | 17.5737 | 16.5702 | 14.9293 | 16.8834 | 17.2148 | 17.5077 | 17.5546 | 17.3057 | 16.5204 | 14.7592 | 6.0368 | 8.3702 | 5.5461 | 5.7316 | 5.6628 | 6.6923 | 7.7038 | 15.8434 | 15.5069 | 15.3996 | 14.3463 | 14.2381 | 14.1795 |  |  |  | 10.7335 | 9.5383 | 9.0769 | 9.158 | -0.076939 | -0.1575 | 12.6904 |  |  | 10.6186 |  |  | 16.928 | 16.1325 | 15.1114 | 16.4284 | 15.7046 | 14.8252 | 10.6896 | 10.56 | 11.4349 | 11.3338 | 9.0786 |  | 10.6248 | 8.7502 | 9.9294 | 9.3071 | 11.0944 | 11.9014 |  | 12.3467 |  |  | 11.8876 | 12.5435 | 12.4011 | [6 empty] | 12.6074 |  |  | 11.369 |  |  | 9.1164 | 10.2932 | 12.0036 | 7.6847 | 9.1923 | 12.5593 | 7.8153 | 9.5493 | 12.3039 | 9.2263 | 10.4483 | 7.7352 | 10.3763 | 8.1912 | 10.1257 | 7.8829 | 9.6751 | 13.1301 | 10.4509 | 10.1374 | 11.4381 | 8.2857 | 9.7315 | 12.6482 | 8.0415 | 10.3599 | 9.7145 | 9.8359 | 8.549 | 10.1957 | 0.045827 | 20.9569 | 0.032603 | 0.046105 | -37.9543 | 3.121 | 0.02 | 0.34 | 0.26259 | 0.11618 | 0.51631 | 0.49078 | 0.62372 | 0.50528 | 0.73016 | 0.41064 | 0.39685 | 0.41977 | 0.42055 | 0.59253 | 0.43816 | 0.41202
42810.4347 | -462 | 18.5548 | 18.6288 | 18.6237 | 18.6337 | 18.0015 | 16.6572 | 14.7232 | 16.7411 | 17.2183 | 17.3202 | 17.3345 | 16.8858 | 15.9433 | 14.5584 | 15.0054 | 15.0148 | 15.5663 | 13.4228 | 13.5394 | 14.115 |  |  |  | 16.6261 | 15.973 | 15.0871 | 10.2236 | 9.5927 | 9.8829 | 17.2466 | 16.3889 | 15.2027 | 16.9276 | 16.2129 | 15.2224 | 10.8206 | 11.6826 |  | 12.2329 | 10.4297 | 10.2888 | 8.3062 |  | 6.3731 | 6.3799 | 5.927 | 6.0154 | 6.0939 | 6.2473 | 6.8767 | 4.5528 | 6.5017 | 4.4721 | 6.7198 | 8.1409 | 42.9781 | 47.2707 | 43.6165 | 15.107 |  |  | 0.052787 | 0.17488 | 0.18978 | 0.087398 | 0.20518 | 0.023196 | 0.4336 | 0.24626 | -0.77722 | 0.46516 | -0.27789 | 8.8703 | 8.8718 | 2.0084 | 15.7963 | 16.711 | 17.2665 | 17.6101 | 17.5834 | 16.575 | 14.9339 | 16.8897 | 17.2291 | 17.5069 | 17.5557 | 17.3064 | 16.5263 | 14.7737 | 6.0303 | 8.3582 | 5.5143 | 5.7405 | 5.646 | 6.6868 | 7.6981 | 15.8379 | 15.5056 | 15.3959 | 14.3281 | 14.2332 | 14.1762 |  |  |  | 10.7293 | 9.5368 | 9.0681 | 9.172 | -0.1677 | -0.14884 | 12.6895 |  |  | 10.6083 |  |  | 16.9244 | 16.1206 | 15.1049 | 16.422 | 15.7126 | 14.8197 | 10.6899 | 10.5589 | 11.4205 | 11.3264 | 9.0945 |  | 10.6282 | 8.734 | 9.926 | 9.3278 | 11.093 | 11.8882 |  | 12.3432 |  |  | 11.9064 | 12.5644 | 12.4237 | [6 empty] | 12.6159 |  |  | 11.3834 |  |  | 9.1106 | 10.2961 | 11.9873 | 7.6941 | 9.1847 | 12.5553 | 7.8256 | 9.536 | 12.313 | 9.2263 | 10.4485 | 7.7252 | 10.3701 | 8.2004 | 10.1271 | 7.8863 | 9.6901 | 13.1367 | 10.4524 | 10.1339 | 11.4352 | 8.2853 | 9.725 | 12.6338 | 8.0456 | 10.377 | 9.7037 | 9.8364 | 8.5594 | 10.198 | 0.12961 | 20.9582 | 0.032902 | 0.046517 | -37.9256 | 3.121 | -0.04 | 0.35 | 0.26937 | 0.48725 | 0.50759 | 0.34445 | 0.52765 | 0.17741 | 0.76704 | 0.41031 | 0.39719 | 0.41915 | 0.42063 | 0.5954 | 0.43855 | 0.41149
42810.4347 | -461 | 18.5541 | 18.6305 | 18.6243 | 18.6472 | 18.0048 | 16.657 | 14.7178 | 16.7425 | 17.2194 | 17.3182 | 17.3302 | 16.8847 | 15.9312 | 14.5567 | 15.012 | 15.0029 | 15.569 | 13.4179 | 13.5509 | 14.1164 |  |  |  | 16.6321 | 15.9723 | 15.0818 | 10.2263 | 9.5848 | 9.8733 | 17.2507 | 16.3901 | 15.2068 | 16.9274 | 16.213 | 15.2284 | 10.8193 | 11.6475 |  | 12.2342 | 10.4325 | 10.2817 | 8.2884 |  | 6.3909 | 6.3868 | 5.9551 | 6.0369 | 6.0997 | 6.2519 | 6.8776 | 4.5268 | 6.5079 | 4.3907 | 6.7274 | 8.1331 | 42.9905 | 47.2769 | 43.617 | 15.1012 |  |  | 0.11653 | 0.070399 | 0.11619 | 0.08477 | 0.28141 | 0.04948 | 0.46645 | 0.33168 | -0.13932 | -0.64405 | -0.30014 | 8.8671 | 8.8682 | 2.0086 | 15.7979 | 16.7072 | 17.2684 | 17.6019 | 17.5842 | 16.5742 | 14.9333 | 16.8892 | 17.223 | 17.5074 | 17.5553 | 17.306 | 16.5293 | 14.7747 | 6.038 | 8.3427 | 5.5014 | 5.7231 | 5.6364 | 6.6934 | 7.6872 | 15.8336 | 15.4941 | 15.3865 | 14.3353 | 14.2295 | 14.1723 |  |  |  | 10.7219 | 9.5448 | 9.0636 | 9.2082 | -0.1284 | -0.20022 | 12.6968 |  |  | 10.6221 |  |  | 16.9269 | 16.1225 | 15.1128 | 16.4215 | 15.7125 | 14.8253 | 10.6799 | 10.5534 | 11.411 | 11.3205 | 9.0935 |  | 10.6228 | 8.6967 | 9.9212 | 9.355 | 11.0889 | 11.8565 |  | 12.3394 |  |  | 11.8922 | 12.5803 | 12.4385 | [6 empty] | 12.6275 |  |  | 11.3832 |  |  | 9.0983 | 10.2828 | 11.9732 | 7.6889 | 9.1768 | 12.5528 | 7.82 | 9.5349 | 12.3189 | 9.2303 | 10.4441 | 7.7132 | 10.3664 | 8.204 | 10.1249 | 7.9027 | 9.6973 | 13.1343 | 10.4512 | 10.1396 | 11.4448 | 8.2862 | 9.7225 | 12.6395 | 8.0523 | 10.377 | 9.7069 | 9.8436 | 8.5491 | 10.1991 | -0.0042494 | 20.956 | 0.034032 | 0.047321 | -38.0003 | 3.121 | -0.15 | 0.35 | 0.40021 | 0.30915 | 0.39716 | 0.33924 | 0.61795 | 0.25912 | 0.79558 | 0.41016 | 0.39807 | 0.41826 | 0.42055 | 0.59557 | 0.439 | 0.41024
42810.4347 | -460 | 18.5626 | 18.6364 | 18.6263 | 18.6476 | 18.0078 | 16.6595 | 14.7263 | 16.7433 | 17.2233 | 17.321 | 17.3387 | 16.891 | 15.9338 | 14.5671 | 15.0071 | 15.007 | 15.5629 | 13.4299 | 13.5399 | 14.1144 |  |  |  | 16.6287 | 15.9704 | 15.084 | 10.2222 | 9.5748 | 9.8514 | 17.2472 | 16.3924 | 15.2063 | 16.923 | 16.2074 | 15.2255 | 10.8238 | 11.6178 |  | 12.2429 | 10.4343 | 10.2871 | 8.2771 |  | 6.4071 | 6.3917 | 5.9893 | 6.058 | 6.1039 | 6.2701 | 6.9179 | 4.5041 | 6.5049 | 4.3347 | 6.7288 | 8.1338 | 42.9827 | 47.2835 | 43.6316 | 15.0919 |  |  | 0.1507 | 0.16174 | 0.19307 | 0.10908 | -0.020864 | -0.078 | 0.63665 | 0.23837 | -1.7535 | -0.3455 | -0.33889 | 8.8694 | 8.8707 | 2.0083 | 15.7979 | 16.7025 | 17.265 | 17.5998 | 17.5788 | 16.5661 | 14.9282 | 16.8842 | 17.2193 | 17.5073 | 17.5561 | 17.306 | 16.5226 | 14.7657 | 6.0415 | 8.3561 | 5.5 | 5.6843 | 5.6248 | 6.6967 | 7.6904 | 15.8476 | 15.5033 | 15.3917 | 14.3358 | 14.2364 | 14.1743 |  |  |  | 10.7323 | 9.5597 | 9.0676 | 9.246 | -0.039661 | -0.16804 | 12.6977 |  |  | 10.6208 |  |  | 16.928 | 16.1216 | 15.1139 | 16.4225 | 15.7136 | 14.8262 | 10.6918 | 10.5467 | 11.4145 | 11.3178 | 9.1062 |  | 10.6282 | 8.6156 | 9.915 | 9.3814 | 11.0903 | 11.8408 |  | 12.327 |  |  | 11.8697 | 12.579 | 12.4427 | [6 empty] | 12.6065 |  |  | 11.3803 |  |  | 9.0964 | 10.2821 | 11.9589 | 7.6897 | 9.173 | 12.5532 | 7.821 | 9.5264 | 12.3267 | 9.2202 | 10.4415 | 7.7199 | 10.3639 | 8.2082 | 10.122 | 7.9168 | 9.7002 | 13.1319 | 10.4489 | 10.1444 | 11.4438 | 8.2706 | 9.7172 | 12.6453 | 8.0656 | 10.3736 | 9.7113 | 9.8367 | 8.5546 | 10.2038 | -0.054518 | 20.9591 | 0.033929 | 0.047907 | -38.0731 | 3.121 | -0.14 | 0.39 | 0.45511 | 0.46859 | 0.51198 | 0.38483 | -0.16827 | -0.32534 | 0.92949 | 0.40998 | 0.40012 | 0.41757 | 0.42055 | 0.59609 | 0.43946 | 0.40953
42810.4347 | -459 | 18.566 | 18.6393 | 18.6291 | 18.6516 | 18.0039 | 16.6635 | 14.7307 | 16.7486 | 17.2304 | 17.3317 | 17.3377 | 16.8954 | 15.9496 | 14.5687 | 15.0108 | 15.002 | 15.5622 | 13.4298 | 13.5435 | 14.1086 |  |  |  | 16.6304 | 15.9676 | 15.0847 | 10.2093 | 9.5857 | 9.8327 | 17.246 | 16.3821 | 15.2062 | 16.9193 | 16.209 | 15.2194 | 10.8176 | 11.6195 |  | 12.2335 | 10.4373 | 10.2728 | 8.3016 |  | 6.4151 | 6.4017 | 5.9957 | 6.0579 | 6.1032 | 6.2695 | 6.9233 | 4.535 | 6.4938 | 4.3327 | 6.7177 | 8.1339 | 42.9686 | 47.2852 | 43.6372 | 15.0888 |  |  | 0.019275 | 0.057915 | 0.084648 | 0.072282 | 0.042876 | 0.036996 | 0.36986 | 0.28174 | -0.081133 | -0.028286 | -0.37029 | 8.8684 | 8.87 | 2.0085 | 15.7965 | 16.7057 | 17.268 | 17.607 | 17.5827 | 16.5707 | 14.9364 | 16.8908 | 17.2145 | 17.509 | 17.5598 | 17.3112 | 16.5213 | 14.7712 | 6.0742 | 8.3561 | 5.5425 | 5.6617 | 5.5994 | 6.7008 | 7.6846 | 15.8531 | 15.4963 | 15.3964 | 14.3389 | 14.2366 | 14.1765 |  |  |  | 10.7385 | 9.5675 | 9.0694 | 9.2706 | -0.011499 | -0.34476 | 12.7008 |  |  | 10.6227 |  |  | 16.9256 | 16.1223 | 15.11 | 16.4239 | 15.7173 | 14.8245 | 10.6936 | 10.5488 | 11.4072 | 11.3076 | 9.1479 |  | 10.6357 | 8.5804 | 9.9212 | 9.4075 | 11.0924 | 11.8274 |  | 12.3419 |  |  | 11.8832 | 12.595 | 12.4378 | [6 empty] | 12.61 |  |  | 11.3863 |  |  | 9.1152 | 10.3038 | 11.968 | 7.7138 | 9.1744 | 12.5589 | 7.8471 | 9.5385 | 12.3448 | 9.2298 | 10.4515 | 7.7404 | 10.3679 | 8.2227 | 10.1315 | 7.9281 | 9.7084 | 13.1339 | 10.4436 | 10.1516 | 11.4551 | 8.2857 | 9.7242 | 12.6417 | 8.0823 | 10.3781 | 9.7126 | 9.8382 | 8.5587 | 10.2116 | 0.090317 | 20.9583 | 0.034359 | 0.049564 | -38.0577 | 3.121 | -0.38 | 0.31 | 0.16276 | 0.28041 | 0.33901 | 0.31327 | 0.24121 | 0.22406 | 0.70845 | 0.40907 | 0.4013 | 0.41692 | 0.41739 | 0.5907 | 0.43858 | 0.40905
42810.4347 | -458 | 18.5599 | 18.6265 | 18.6236 | 18.6425 | 17.9987 | 16.6539 | 14.7214 | 16.7417 | 17.225 | 17.3188 | 17.3269 | 16.8875 | 15.9399 | 14.5569 | 15.0099 | 15.0182 | 15.5738 | 13.4229 | 13.5504 | 14.1205 |  |  |  | 16.6325 | 15.9789 | 15.0977 | 10.2275 | 9.5799 | 9.8514 | 17.2502 | 16.3882 | 15.211 | 16.9299 | 16.2149 | 15.2234 | 10.8197 | 11.6444 |  | 12.2351 | 10.4359 | 10.2736 | 8.3509 |  | 6.4141 | 6.4052 | 5.9936 | 6.0701 | 6.1155 | 6.2845 | 6.9491 | 4.5836 | 6.4895 | 4.3186 | 6.7154 | 8.1369 | 42.9545 | 47.2699 | 43.6382 | 15.0847 |  |  | -0.025409 | -0.16616 | 0.2693 | 0.17348 | 0.26827 | 0.29984 | 0.41586 | 0.40002 | -0.43628 | -2.0594 | -0.29756 | 8.8695 | 8.8707 | 2.0088 | 15.8021 | 16.7195 | 17.2687 | 17.6153 | 17.5847 | 16.5797 | 14.9353 | 16.8933 | 17.2216 | 17.5179 | 17.5642 | 17.3108 | 16.5348 | 14.7723 | 6.154 | 8.3775 | 5.5989 | 5.6627 | 5.5804 | 6.7051 | 7.6808 | 15.8527 | 15.499 | 15.3899 | 14.3455 | 14.2317 | 14.186 |  |  |  | 10.7365 | 9.5766 | 9.0814 | 9.3112 | 0.0071398 | -0.090499 | 12.6998 |  |  | 10.6219 |  |  | 16.9209 | 16.1275 | 15.1142 | 16.4279 | 15.7126 | 14.8281 | 10.6854 | 10.545 | 11.4022 | 11.3014 | 9.1769 |  | 10.6306 | 8.5508 | 9.9235 | 9.4257 | 11.0882 | 11.8136 |  | 12.3439 |  |  | 11.8732 | 12.5939 | 12.4447 | [6 empty] | 12.5763 |  |  | 11.3765 |  |  | 9.1084 | 10.2983 | 11.955 | 7.6898 | 9.1686 | 12.5494 | 7.8508 | 9.5441 | 12.3604 | 9.2241 | 10.4523 | 7.7544 | 10.3622 | 8.2347 | 10.1305 | 7.9229 | 9.6896 | 13.1244 | 10.4352 | 10.1365 | 11.4527 | 8.2772 | 9.7107 | 12.6308 | 8.0766 | 10.3606 | 9.692 | 9.8189 | 8.5467 | 10.1923 | -0.026591 | 20.9488 | 0.034124 | 0.049514 | -38.0296 | 3.121 | -0.63 | 0.28 | -0.18688 | -0.47497 | 0.60467 | 0.48531 | 0.60338 | 0.6379 | 0.75124 | 0.4081 | 0.4022 | 0.41628 | 0.40902 | 0.58399 | 0.43728 | 0.40786
42810.4347 | -457 | 18.5638 | 18.6303 | 18.6243 | 18.645 | 17.9999 | 16.6477 | 14.7266 | 16.7435 | 17.2218 | 17.3154 | 17.333 | 16.8825 | 15.9363 | 14.5507 | 15.0086 | 15.0088 | 15.5677 | 13.4285 | 13.5474 | 14.1184 |  |  |  | 16.6359 | 15.9747 | 15.0874 | 10.219 | 9.5656 | 9.8729 | 17.2579 | 16.3888 | 15.2116 | 16.9298 | 16.2108 | 15.2232 | 10.8192 | 11.6827 |  | 12.2394 | 10.4403 | 10.2712 | 8.3823 |  | 6.4276 | 6.4207 | 6.0002 | 6.0866 | 6.124 | 6.3323 | 7.0173 | 4.7061 | 6.4936 | 4.3575 | 6.719 | 8.1365 | 42.9239 | 47.2385 | 43.6352 | 15.081 |  |  | 0.029791 | -0.10242 | 0.22133 | -0.46524 | 0.14539 | 0.007424 | 0.58802 | 0.2916 | -0.2228 | -0.006047 | -0.27471 | 8.8705 | 8.8713 | 2.0082 | 15.8095 | 16.7184 | 17.2782 | 17.6158 | 17.5825 | 16.5845 | 14.9477 | 16.8857 | 17.2295 | 17.5232 | 17.5641 | 17.3076 | 16.5295 | 14.779 | 6.2503 | 8.3792 | 5.6789 | 5.691 | 5.5878 | 6.7094 | 7.6806 | 15.8421 | 15.4976 | 15.3817 | 14.3342 | 14.2265 | 14.1732 |  |  |  | 10.7331 | 9.5737 | 9.0724 | 9.3469 | 0.061842 | -0.022371 | 12.702 |  |  | 10.6375 |  |  | 16.9278 | 16.1364 | 15.1113 | 16.43 | 15.7131 | 14.8291 | 10.6932 | 10.5499 | 11.3989 | 11.3013 | 9.148 |  | 10.6312 | 8.4888 | 9.9117 | 9.436 | 11.0788 | 11.7444 |  | 12.3293 |  |  | 11.8795 | 12.6003 | 12.463 | [6 empty] | 12.5767 |  |  | 11.355 |  |  | 9.1044 | 10.2933 | 11.9434 | 7.6675 | 9.1702 | 12.5351 | 7.848 | 9.535 | 12.3614 | 9.2138 | 10.4424 | 7.7405 | 10.3535 | 8.2376 | 10.1118 | 7.9308 | 9.6965 | 13.1168 | 10.4327 | 10.1383 | 11.4575 | 8.273 | 9.7074 | 12.6334 | 8.0846 | 10.3529 | 9.6817 | 9.8223 | 8.5404 | 10.1995 | 0.0096178 | 20.9534 | 0.033068 | 0.048638 | -37.9715 | 3.121 | -0.58 | 0.27 | 0.20236 | -0.37291 | 0.54819 | -0.79479 | 0.44423 | 0.10038 | 0.89339 | 0.40892 | 0.40353 | 0.41568 | 0.39882 | 0.57508 | 0.43639 | 0.40675
42810.4348 | -456 | 18.572 | 18.6371 | 18.6262 | 18.6489 | 18.0034 | 16.6599 | 14.7303 | 16.75 | 17.2277 | 17.3261 | 17.3381 | 16.8914 | 15.9407 | 14.5574 | 15.0145 | 15.0107 | 15.5731 | 13.4238 | 13.5524 | 14.1155 |  |  |  | 16.6393 | 15.9742 | 15.0918 | 10.2235 | 9.56 | 9.8996 | 17.243 | 16.3783 | 15.1996 | 16.9182 | 16.1998 | 15.2156 | 10.8124 | 11.7225 |  | 12.2275 | 10.4287 | 10.257 | 8.3786 |  | 6.4294 | 6.43 | 6.0171 | 6.1091 | 6.1589 | 6.3633 | 7.0422 | 4.8079 | 6.4924 | 4.4061 | 6.7154 | 8.1424 | 42.9219 | 47.2317 | 43.6226 | 15.0769 |  |  | 0.054759 | -0.018969 | 0.10436 | -0.13734 | 0.057332 | 0.42601 | 0.43228 | 0.16346 | -0.73226 | -0.37173 | -0.17914 | 8.8693 | 8.8708 | 2.0086 | 15.8007 | 16.7074 | 17.2646 | 17.6075 | 17.578 | 16.5823 | 14.9417 | 16.8834 | 17.2248 | 17.5176 | 17.5585 | 17.3084 | 16.5326 | 14.7621 | 6.2898 | 8.3872 | 5.7454 | 5.7413 | 5.5897 | 6.7013 | 7.671 | 15.8532 | 15.5008 | 15.3903 | 14.3382 | 14.2297 | 14.1772 |  |  |  | 10.7368 | 9.5801 | 9.0767 | 9.3866 | -0.20053 | 0.097324 | 12.705 |  |  | 10.6361 |  |  | 16.9333 | 16.1352 | 15.1094 | 16.4245 | 15.7174 | 14.8344 | 10.6901 | 10.5483 | 11.3893 | 11.2928 | 9.137 |  | 10.6275 | 8.4667 | 9.9163 | 9.4537 | 11.083 | 11.6977 |  | 12.3371 |  |  | 11.87 | 12.5984 | 12.4631 | [6 empty] | 12.578 |  |  | 11.351 |  |  | 9.1026 | 10.2963 | 11.9292 | 7.6582 | 9.1735 | 12.5252 | 7.8479 | 9.5378 | 12.3759 | 9.2045 | 10.4459 | 7.746 | 10.351 | 8.2402 | 10.108 | 7.914 | 9.6874 | 13.1146 | 10.4397 | 10.1387 | 11.4635 | 8.2678 | 9.7124 | 12.6281 | 8.0914 | 10.3433 | 9.6705 | 9.8146 | 8.532 | 10.1944 | 0.15445 | 20.9578 | 0.031955 | 0.046228 | -38.0416 | 3.1209 | -0.52 | 0.33 | 0.27436 | -0.16049 | 0.37643 | -0.43183 | 0.27898 | 0.76046 | 0.76604 | 0.4091 | 0.4043 | 0.41533 | 0.39349 | 0.56658 | 0.43627 | 0.40577
42810.4348 | -455 | 18.5657 | 18.6325 | 18.624 | 18.6408 | 17.9956 | 16.6624 | 14.7192 | 16.7388 | 17.2318 | 17.3257 | 17.334 | 16.8869 | 15.9451 | 14.5623 | 15.0188 | 15.0121 | 15.5722 | 13.4264 | 13.5491 | 14.1169 |  |  |  | 16.6421 | 15.9854 | 15.0925 | 10.2309 | 9.5609 | 9.9209 | 17.2444 | 16.3815 | 15.2001 | 16.9205 | 16.2077 | 15.2195 | 10.8077 | 11.7504 |  | 12.232 | 10.4318 | 10.2531 | 8.4046 |  | 6.4336 | 6.4271 | 6.0099 | 6.1106 | 6.1705 | 6.3737 | 7.0551 | 4.8696 | 6.4904 | 4.4376 | 6.7078 | 8.1507 | 42.9052 | 47.2439 | 43.6263 | 15.0755 |  |  | 0.076443 | 0.021771 | -0.031004 | -0.46524 | 0.082304 | -0.0412 | 0.46448 | 0.093804 | -0.1798 | -0.55761 | -0.29498 | 8.871 | 8.8723 | 2.0086 | 15.8127 | 16.7082 | 17.2673 | 17.6144 | 17.5782 | 16.5735 | 14.9388 | 16.8958 | 17.2239 | 17.5192 | 17.5673 | 17.3121 | 16.5392 | 14.7764 | 6.2733 | 8.3673 | 5.7837 | 5.7797 | 5.6135 | 6.7024 | 7.6754 | 15.8598 | 15.5021 | 15.3954 | 14.341 | 14.2337 | 14.1826 |  |  |  | 10.751 | 9.5834 | 9.0797 | 9.4227 | 0.04381 | -0.037239 | 12.7061 |  |  | 10.6191 |  |  | 16.932 | 16.1248 | 15.1092 | 16.4295 | 15.7143 | 14.8327 | 10.6878 | 10.5467 | 11.3838 | 11.2801 | 9.142 |  | 10.6237 | 8.4236 | 9.911 | 9.4587 | 11.0882 | 11.6921 |  | 12.3404 |  |  | 11.8698 | 12.6174 | 12.4808 | [6 empty] | 12.5703 |  |  | 11.3595 |  |  | 9.1116 | 10.2937 | 11.9297 | 7.6569 | 9.1758 | 12.5218 | 7.8559 | 9.5425 | 12.3905 | 9.2179 | 10.4426 | 7.7383 | 10.3514 | 8.2385 | 10.1093 | 7.9135 | 9.6746 | 13.1102 | 10.4341 | 10.1364 | 11.4672 | 8.2632 | 9.7122 | 12.6271 | 8.0992 | 10.3322 | 9.6557 | 9.8113 | 8.5368 | 10.1945 | 0.15253 | 20.9584 | 0.031524 | 0.045627 | -38.0926 | 3.1209 | -0.82 | 0.33 | 0.32418 | 0.17193 | -0.20518 | -0.7948 | 0.33426 | -0.2365 | 0.79407 | 0.40884 | 0.40532 | 0.41536 | 0.39545 | 0.56282 | 0.43539 | 0.40524
42810.4348 | -454 | 18.5628 | 18.6259 | 18.6201 | 18.6432 | 17.9978 | 16.66 | 14.7195 | 16.7397 | 17.22 | 17.3145 | 17.3317 | 16.8795 | 15.9313 | 14.5548 | 15.0091 | 15.011 | 15.5698 | 13.42 | 13.5439 | 14.1189 |  |  |  | 16.6383 | 15.9847 | 15.0924 | 10.2235 | 9.5584 | 9.9284 | 17.2613 | 16.387 | 15.2055 | 16.9333 | 16.2181 | 15.2251 | 10.8206 | 11.7727 |  | 12.2395 | 10.4371 | 10.2591 | 8.4433 |  | 6.4556 | 6.4371 | 6.0094 | 6.1207 | 6.1876 | 6.3737 | 7.055 | 4.9008 | 6.4853 | 4.4951 | 6.7176 | 8.1412 | 42.8712 | 47.262 | 43.6089 | 15.066 |  |  | -0.014237 | 0.055943 | 0.064932 | -0.40675 | -0.072776 | -0.12466 | 0.4566 | -0.030392 | -0.80602 | -0.16843 | -0.24252 | 8.8695 | 8.8708 | 2.0082 | 15.8186 | 16.7132 | 17.2676 | 17.6076 | 17.5802 | 16.5786 | 14.9349 | 16.8901 | 17.224 | 17.5176 | 17.5667 | 17.3108 | 16.5289 | 14.778 | 6.2189 | 8.3171 | 5.7163 | 5.8111 | 5.6418 | 6.7024 | 7.6708 | 15.8616 | 15.4999 | 15.3981 | 14.3363 | 14.2378 | 14.1766 |  |  |  | 10.7425 | 9.5859 | 9.0824 | 9.4281 | 0.017878 | -0.037239 | 12.7139 |  |  | 10.6265 |  |  | 16.9307 | 16.1279 | 15.1104 | 16.4298 | 15.7098 | 14.8332 | 10.6932 | 10.5452 | 11.389 | 11.2766 | 9.1418 |  | 10.6267 | 8.3508 | 9.9181 | 9.4706 | 11.0911 | 11.6977 |  | 12.3395 |  |  | 11.8737 | 12.6157 | 12.496 | [6 empty] | 12.5686 |  |  | 11.3675 |  |  | 9.1087 | 10.2994 | 11.9276 | 7.6533 | 9.1852 | 12.524 | 7.8683 | 9.5492 | 12.4027 | 9.2123 | 10.452 | 7.734 | 10.3479 | 8.2459 | 10.1101 | 7.9063 | 9.6776 | 13.1105 | 10.4332 | 10.137 | 11.4754 | 8.2653 | 9.7154 | 12.628 | 8.1136 | 10.3332 | 9.6555 | 9.8071 | 8.5429 | 10.1969 | -0.012531 | 20.9559 | 0.032133 | 0.045048 | -38.1257 | 3.1209 | -0.72 | 0.31 | -0.1399 | 0.27561 | 0.29693 | -0.74318 | -0.31432 | -0.41137 | 0.7873 | 0.40894 | 0.40757 | 0.41512 | 0.4015 | 0.56978 | 0.43474 | 0.40481
42810.4348 | -453 | 18.5688 | 18.6423 | 18.6293 | 18.6467 | 17.9993 | 16.6631 | 14.7282 | 16.744 | 17.2266 | 17.3233 | 17.3356 | 16.894 | 15.9508 | 14.5664 | 15.0102 | 15.0087 | 15.5662 | 13.4176 | 13.5487 | 14.1181 |  |  |  | 16.636 | 15.9813 | 15.0921 | 10.2254 | 9.5486 | 9.9339 | 17.2618 | 16.3874 | 15.1946 | 16.9281 | 16.2141 | 15.2214 | 10.8232 | 11.7979 |  | 12.2382 | 10.4358 | 10.2587 | 8.4853 |  | 6.4653 | 6.4375 | 6.0155 | 6.1208 | 6.19 | 6.3628 | 7.0475 | 4.8882 | 6.4884 | 4.5523 | 6.724 | 8.1362 | 42.8559 | 47.2855 | 43.5985 | 15.0526 |  |  | 0.014019 | 0.024403 | 0.1819 | -0.20765 | -0.015608 | -0.43284 | 0.40994 | -0.1191 | -0.39638 | -0.10151 | -0.19424 | 8.8689 | 8.8703 | 2.0088 | 15.8134 | 16.7098 | 17.2703 | 17.6047 | 17.5777 | 16.5766 | 14.9378 | 16.881 | 17.2212 | 17.5134 | 17.5622 | 17.3114 | 16.5308 | 14.7727 | 6.1732 | 8.3146 | 5.6034 | 5.8122 | 5.6657 | 6.6982 | 7.6751 | 15.8666 | 15.5019 | 15.4027 | 14.3439 | 14.2394 | 14.1894 |  |  |  | 10.7444 | 9.5891 | 9.0787 | 9.4334 | 0.11067 | 0.10297 | 12.7123 |  |  | 10.6247 |  |  | 16.922 | 16.1274 | 15.1151 | 16.425 | 15.7058 | 14.8263 | 10.6855 | 10.5435 | 11.3808 | 11.2688 | 9.1228 |  | 10.62 | 8.2738 | 9.927 | 9.4772 | 11.0846 | 11.7024 |  | 12.3452 |  |  | 11.8866 | 12.6208 | 12.5011 | [6 empty] | 12.557 |  |  | 11.3817 |  |  | 9.1105 | 10.3071 | 11.918 | 7.6539 | 9.1922 | 12.5223 | 7.8678 | 9.5467 | 12.41 | 9.2158 | 10.4556 | 7.7405 | 10.3528 | 8.2577 | 10.1069 | 7.8998 | 9.6774 | 13.1068 | 10.4351 | 10.1272 | 11.4778 | 8.2657 | 9.7166 | 12.6179 | 8.1186 | 10.3303 | 9.6522 | 9.8007 | 8.542 | 10.1905 | 0.043323 | 20.9567 | 0.032391 | 0.046242 | -38.1684 | 3.1209 | -0.22 | 0.32 | 0.13883 | 0.18203 | 0.49698 | -0.531 | -0.14556 | -0.76653 | 0.74598 | 0.40925 | 0.41001 | 0.41473 | 0.40609 | 0.58284 | 0.43366 | 0.40472
42810.4348 | -452 | 18.5571 | 18.6246 | 18.6155 | 18.6353 | 18.0006 | 16.6512 | 14.7092 | 16.7358 | 17.2212 | 17.3133 | 17.3301 | 16.8848 | 15.9315 | 14.5551 | 15.0122 | 15.0044 | 15.5633 | 13.4246 | 13.5416 | 14.1152 |  |  |  | 16.6361 | 15.9774 | 15.0892 | 10.2289 | 9.5377 | 9.9362 | 17.2637 | 16.3933 | 15.2061 | 16.9338 | 16.214 | 15.2281 | 10.8281 | 11.8205 |  | 12.2432 | 10.4432 | 10.2723 | 8.5189 |  | 6.4644 | 6.4419 | 6.0198 | 6.1294 | 6.196 | 6.3632 | 7.0375 | 4.8742 | 6.4912 | 4.6252 | 6.7223 | 8.1364 | 42.859 | 47.3015 | 43.5867 | 15.0496 |  |  | -0.095721 | -0.25816 | 0.16219 | 0.08017 | -0.060292 | -0.20942 | 0.57094 | 0.17003 | -0.27982 | -0.33166 | -0.14893 | 8.8686 | 8.8699 | 2.0085 | 15.8092 | 16.7142 | 17.2724 | 17.6084 | 17.5838 | 16.577 | 14.9391 | 16.8851 | 17.2215 | 17.5083 | 17.5638 | 17.3073 | 16.5308 | 14.77 | 6.1578 | 8.321 | 5.5135 | 5.7595 | 5.637 | 6.708 | 7.6766 | 15.8665 | 15.5106 | 15.4077 | 14.3462 | 14.2467 | 14.1879 |  |  |  | 10.7479 | 9.5872 | 9.0765 | 9.4482 | 0.015041 | -0.011832 | 12.7156 |  |  | 10.6294 |  |  | 16.9206 | 16.1281 | 15.1154 | 16.4249 | 15.7101 | 14.8244 | 10.6927 | 10.5522 | 11.378 | 11.2702 | 9.1376 |  | 10.6237 | 8.1819 | 9.9206 | 9.4768 | 11.0794 | 11.7278 |  | 12.344 |  |  | 11.8875 | 12.6108 | 12.5025 | [6 empty] | 12.5137 |  |  | 11.3814 |  |  | 9.1034 | 10.2962 | 11.9054 | 7.6565 | 9.1906 | 12.5161 | 7.8567 | 9.5468 | 12.4052 | 9.2091 | 10.4416 | 7.7333 | 10.3423 | 8.2554 | 10.0968 | 7.9049 | 9.6725 | 13.1043 | 10.4327 | 10.1257 | 11.4756 | 8.2678 | 9.7173 | 12.6128 | 8.129 | 10.3241 | 9.6494 | 9.804 | 8.5418 | 10.1883 | -0.078593 | 20.9558 | 0.032735 | 0.048088 | -38.1038 | 3.1209 | -0.21 | 0.27 | -0.36277 | -0.59207 | 0.46929 | 0.32994 | -0.28609 | -0.53319 | 0.88036 | 0.40896 | 0.41235 | 0.41456 | 0.40893 | 0.59298 | 0.43289 | 0.40443
42810.4348 | -451 | 18.5644 | 18.6271 | 18.6206 | 18.6312 | 17.9975 | 16.653 | 14.7132 | 16.7303 | 17.2233 | 17.3147 | 17.3246 | 16.8814 | 15.9368 | 14.5548 | 15.0143 | 15.0102 | 15.5652 | 13.4281 | 13.5473 | 14.1142 |  |  |  | 16.6331 | 15.9858 | 15.094 | 10.2296 | 9.5406 | 9.9323 | 17.2639 | 16.3931 | 15.2037 | 16.9295 | 16.214 | 15.2274 | 10.819 | 11.7908 |  | 12.2379 | 10.4434 | 10.2645 | 8.5452 |  | 6.462 | 6.4408 | 6.0162 | 6.1384 | 6.1955 | 6.3588 | 7.0046 | 4.8772 | 6.4926 | 4.6816 | 6.7279 | 8.1492 | 42.8787 | 47.3194 | 43.5899 | 15.0544 |  |  | 0.11259 | -0.16682 | 0.088588 | 0.11171 | -0.009036 | 0.17368 | 0.51311 | 0.18383 | -0.36817 | -0.83958 | -0.23736 | 8.8666 | 8.8678 | 2.0084 | 15.821 | 16.7193 | 17.2787 | 17.6061 | 17.5856 | 16.5808 | 14.9384 | 16.8891 | 17.227 | 17.516 | 17.5686 | 17.3114 | 16.5306 | 14.7745 | 6.1523 | 8.3316 | 5.4532 | 5.6801 | 5.5775 | 6.7062 | 7.6746 | 15.8732 | 15.5121 | 15.4043 | 14.3454 | 14.242 | 14.1841 |  |  |  | 10.747 | 9.5911 | 9.0693 | 9.4721 | 0.097297 | 0.021668 | 12.7101 |  |  | 10.6259 |  |  | 16.93 | 16.1255 | 15.114 | 16.4225 | 15.715 | 14.8256 | 10.6887 | 10.5503 | 11.3729 | 11.255 | 9.1396 |  | 10.6196 | 8.1041 | 9.924 | 9.4845 | 11.0871 | 11.7493 |  | 12.3438 |  |  | 11.8904 | 12.5947 | 12.5087 | [6 empty] | 12.5203 |  |  | 11.3812 |  |  | 9.1013 | 10.2873 | 11.8943 | 7.655 | 9.1885 | 12.5154 | 7.8432 | 9.5441 | 12.4007 | 9.1987 | 10.4328 | 7.7288 | 10.335 | 8.2421 | 10.0885 | 7.9028 | 9.668 | 13.102 | 10.433 | 10.1237 | 11.473 | 8.2692 | 9.7139 | 12.6096 | 8.1079 | 10.3198 | 9.6501 | 9.8004 | 8.5409 | 10.184 | 0.11189 | 20.9558 | 0.032839 | 0.049231 | -38.1474 | 3.1209 | -0.12 | 0.32 | 0.39343 | -0.47594 | 0.34683 | 0.38947 | -0.11075 | 0.48555 | 0.83458 | 0.40877 | 0.41462 | 0.4146 | 0.40934 | 0.59945 | 0.43186 | 0.40373
42810.4348 | -450 | 18.5714 | 18.6336 | 18.6237 | 18.6396 | 17.9988 | 16.6608 | 14.7168 | 16.7342 | 17.225 | 17.3212 | 17.337 | 16.888 | 15.9466 | 14.5621 | 15.0163 | 15.0118 | 15.5654 | 13.4282 | 13.5456 | 14.1215 |  |  |  | 16.6334 | 15.9859 | 15.0916 | 10.2342 | 9.5347 | 9.9309 | 17.2656 | 16.394 | 15.2072 | 16.9271 | 16.2139 | 15.222 | 10.8177 | 11.7739 |  | 12.2371 | 10.4426 | 10.2677 | 8.5579 |  | 6.4684 | 6.4433 | 6.0167 | 6.1546 | 6.2013 | 6.3525 | 6.9806 | 4.8328 | 6.4943 | 4.7054 | 6.7334 | 8.1469 | 42.8906 | 47.3192 | 43.5823 | 15.0609 |  |  | 0.16778 | -0.10505 | 0.064932 | -0.078854 | -0.005092 | 0.37278 | 0.37183 | 0.35599 | -1.4208 | -0.28802 | -0.32637 | 8.868 | 8.8694 | 2.0085 | 15.8171 | 16.7054 | 17.2699 | 17.6093 | 17.5837 | 16.5768 | 14.933 | 16.8895 | 17.2266 | 17.5137 | 17.5555 | 17.314 | 16.5373 | 14.7706 | 6.1314 | 8.3458 | 5.4229 | 5.6189 | 5.5583 | 6.7065 | 7.6711 | 15.8762 | 15.5112 | 15.4007 | 14.344 | 14.2423 | 14.188 |  |  |  | 10.7465 | 9.5928 | 9.0623 | 9.4795 | 0.13397 | -0.034039 | 12.7159 |  |  | 10.6215 |  |  | 16.9304 | 16.1274 | 15.1126 | 16.4238 | 15.7121 | 14.824 | 10.6864 | 10.5386 | 11.3689 | 11.2557 | 9.1354 |  | 10.6278 | 8.0873 | 9.9264 | 9.4793 | 11.0881 | 11.7766 |  | 12.3461 |  |  | 11.9109 | 12.6059 | 12.5162 | [6 empty] | 12.5458 |  |  | 11.3866 |  |  | 9.1018 | 10.2831 | 11.892 | 7.6696 | 9.19 | 12.5146 | 7.8453 | 9.5415 | 12.408 | 9.2017 | 10.4357 | 7.7373 | 10.3354 | 8.2415 | 10.0909 | 7.8816 | 9.6748 | 13.1018 | 10.4381 | 10.1221 | 11.4881 | 8.2785 | 9.729 | 12.6107 | 8.0633 | 10.3168 | 9.6638 | 9.8067 | 8.5461 | 10.1885 | 0.088969 | 20.9547 | 0.032936 | 0.049629 | -38.181 | 3.1209 | -0.36 | 0.34 | 0.48028 | -0.37768 | 0.29693 | -0.32722 | -0.083139 | 0.71136 | 0.71045 | 0.40916 | 0.41517 | 0.41478 | 0.4117 | 0.60241 | 0.43146 | 0.40351
42810.4348 | -449 | 18.5671 | 18.6342 | 18.6165 | 18.6375 | 17.9939 | 16.649 | 14.7194 | 16.7294 | 17.2296 | 17.3157 | 17.334 | 16.8882 | 15.9397 | 14.5646 | 15.0098 | 15.0121 | 15.558 | 13.4227 | 13.5481 | 14.1204 |  |  |  | 16.6294 | 15.9786 | 15.0876 | 10.2296 | 9.5328 | 9.929 | 17.2668 | 16.3963 | 15.2032 | 16.9298 | 16.2127 | 15.2191 | 10.811 | 11.7591 |  | 12.2316 | 10.44 | 10.2751 | 8.575 |  | 6.4693 | 6.4412 | 6.028 | 6.1659 | 6.1988 | 6.342 | 6.9722 | 4.8214 | 6.4995 | 4.6889 | 6.7367 | 8.1463 | 42.8869 | 47.2993 | 43.5725 | 15.0677 |  |  | 0.16844 | 0.036887 | 0.17467 | -0.33381 | 0.16116 | 0.11125 | -0.13678 | 0.49662 | -0.23681 | -1.3282 | -0.29617 | 8.8676 | 8.8689 | 2.0086 | 15.8204 | 16.7217 | 17.269 | 17.6084 | 17.5803 | 16.5838 | 14.939 | 16.8948 | 17.2224 | 17.5135 | 17.5597 | 17.3193 | 16.5349 | 14.7827 | 6.124 | 8.3358 | 5.4238 | 5.5783 | 5.5555 | 6.705 | 7.6652 | 15.8675 | 15.5101 | 15.3953 | 14.3398 | 14.2361 | 14.18 |  |  |  | 10.7463 | 9.5984 | 9.0609 | 9.4849 | 0.24074 | -0.019924 | 12.7159 |  |  | 10.6244 |  |  | 16.9324 | 16.1249 | 15.1115 | 16.4279 | 15.7133 | 14.824 | 10.6815 | 10.5367 | 11.3689 | 11.2612 | 9.1478 |  | 10.6219 | 8.1029 | 9.9226 | 9.4763 | 11.0856 | 11.8014 |  | 12.3382 |  |  | 11.9125 | 12.609 | 12.5066 | [6 empty] | 12.5513 |  |  | 11.3638 |  |  | 9.1084 | 10.2899 | 11.893 | 7.6895 | 9.1934 | 12.5217 | 7.8525 | 9.5466 | 12.4111 | 9.2036 | 10.4411 | 7.7497 | 10.3411 | 8.2455 | 10.0907 | 7.8524 | 9.6572 | 13.0837 | 10.4339 | 10.1116 | 11.4948 | 8.2758 | 9.7202 | 12.608 | 8.002 | 10.3053 | 9.6644 | 9.7978 | 8.5438 | 10.1773 | 0.096095 | 20.9544 | 0.032976 | 0.049434 | -38.1947 | 3.1209 | -0.55 | 0.36 | 0.48122 | 0.2238 | 0.48701 | -0.67326 | 0.46771 | 0.3886 | -0.43089 | 0.40862 | 0.41461 | 0.41478 | 0.41234 | 0.60163 | 0.43076 | 0.40335
42810.4348 | -448 | 18.5782 | 18.6413 | 18.6238 | 18.6505 | 17.9989 | 16.6579 | 14.7261 | 16.749 | 17.2319 | 17.324 | 17.3359 | 16.8949 | 15.9416 | 14.5618 | 15.014 | 15.0011 | 15.5634 | 13.4279 | 13.5441 | 14.1124 |  |  |  | 16.627 | 15.969 | 15.0892 | 10.2332 | 9.5312 | 9.9332 | 17.2672 | 16.3927 | 15.2046 | 16.9307 | 16.2168 | 15.2259 | 10.8103 | 11.755 |  | 12.2276 | 10.4362 | 10.2896 | 8.5812 |  | 6.4715 | 6.4407 | 6.0182 | 6.1587 | 6.1896 | 6.3317 | 6.9522 | 4.8178 | 6.4946 | 4.6404 | 6.7239 | 8.1389 | 42.8788 | 47.282 | 43.5722 | 15.0952 |  |  | -0.047093 | 0.086171 | 0.085304 | 0.19713 | 0.15853 | -0.70489 | -0.71176 | 0.34745 | -0.5579 | -0.06626 | -0.11496 | 8.8686 | 8.8695 | 2.0086 | 15.823 | 16.7152 | 17.2718 | 17.6086 | 17.5772 | 16.572 | 14.9283 | 16.889 | 17.2254 | 17.5158 | 17.5619 | 17.3072 | 16.533 | 14.7705 | 6.1256 | 8.3499 | 5.44 | 5.5612 | 5.5586 | 6.709 | 7.6693 | 15.8668 | 15.5069 | 15.3953 | 14.3396 | 14.2288 | 14.1775 |  |  |  | 10.7455 | 9.5938 | 9.0624 | 9.4943 | -0.041687 | 0.041617 | 12.712 |  |  | 10.6141 |  |  | 16.9295 | 16.1273 | 15.1098 | 16.4235 | 15.7079 | 14.8279 | 10.6806 | 10.5399 | 11.3649 | 11.2572 | 9.1302 |  | 10.6109 | 8.132 | 9.9227 | 9.4636 | 11.0809 | 11.8166 |  | 12.3274 |  |  | 11.9091 | 12.6084 | 12.5086 | [6 empty] | 12.5466 |  |  | 11.3484 |  |  | 9.1175 | 10.2849 | 11.8888 | 7.7094 | 9.2015 | 12.5316 | 7.8524 | 9.5493 | 12.4129 | 9.2013 | 10.4449 | 7.7553 | 10.3485 | 8.2462 | 10.1003 | 7.8209 | 9.6331 | 13.0718 | 10.4269 | 10.107 | 11.502 | 8.2788 | 9.7147 | 12.6028 | 7.972 | 10.3084 | 9.6659 | 9.7911 | 8.5437 | 10.1803 | 0.15773 | 20.9554 | 0.034629 | 0.052228 | -38.0274 | 3.1209 | -0.88 | 0.32 | -0.25445 | 0.34207 | 0.34034 | 0.51738 | 0.46387 | -0.97815 | -0.9829 | 0.40875 | 0.4138 | 0.41498 | 0.41262 | 0.60031 | 0.43057 | 0.40307
42810.4349 | -447 | 18.5707 | 18.6293 | 18.6219 | 18.6321 | 17.9912 | 16.6492 | 14.713 | 16.7314 | 17.2162 | 17.3099 | 17.329 | 16.8789 | 15.9343 | 14.5528 | 15.0176 | 15.0112 | 15.5715 | 13.4304 | 13.551 | 14.12 |  |  |  | 16.6394 | 15.9788 | 15.0944 | 10.2438 | 9.5392 | 9.9651 | 17.261 | 16.3919 | 15.2019 | 16.9274 | 16.2091 | 15.2262 | 10.8162 | 11.7678 |  | 12.2286 | 10.433 | 10.3002 | 8.5917 |  | 6.469 | 6.4316 | 6.008 | 6.1464 | 6.1748 | 6.3181 | 6.9099 | 4.7883 | 6.5012 | 4.6438 | 6.7331 | 8.14 | 42.8884 | 47.2656 | 43.5771 | 15.1284 |  |  | 0.14544 | -0.17668 | 0.2003 | -0.039426 | 0.077048 | -0.51761 | -0.12758 | 0.38819 | -0.49388 | -0.97155 | -0.40089 | 8.8696 | 8.8708 | 2.0083 | 15.8239 | 16.7079 | 17.2669 | 17.6004 | 17.5739 | 16.5686 | 14.9203 | 16.8896 | 17.2162 | 17.513 | 17.5535 | 17.3008 | 16.5255 | 14.7662 | 6.1382 | 8.3724 | 5.4624 | 5.5702 | 5.5964 | 6.707 | 7.6613 | 15.875 | 15.5105 | 15.3959 | 14.3406 | 14.2381 | 14.1782 |  |  |  | 10.7479 | 9.5878 | 9.0656 | 9.4804 | -0.13772 | 0.04651 | 12.7131 |  |  | 10.623 |  |  | 16.9286 | 16.1302 | 15.1191 | 16.4247 | 15.7192 | 14.8295 | 10.6841 | 10.5424 | 11.3655 | 11.2643 | 9.104 |  | 10.6227 | 8.1486 | 9.9248 | 9.4628 | 11.0889 | 11.8061 |  | 12.333 |  |  | 11.9176 | 12.5864 | 12.4955 | [6 empty] | 12.5643 |  |  | 11.3477 |  |  | 9.1107 | 10.2773 | 11.8777 | 7.714 | 9.1977 | 12.5294 | 7.8407 | 9.5377 | 12.4132 | 9.197 | 10.4322 | 7.728 | 10.3416 | 8.2279 | 10.0887 | 7.8046 | 9.6061 | 13.0645 | 10.4259 | 10.1004 | 11.5066 | 8.2788 | 9.7225 | 12.6066 | 7.9582 | 10.3057 | 9.6711 | 9.7893 | 8.5453 | 10.1921 | 0.076257 | 20.9535 | 0.034968 | 0.05251 | -38.0058 | 3.1209 | -0.52 | 0.24 | 0.44719 | -0.48979 | 0.52151 | -0.23137 | 0.32338 | -0.83817 | -0.41613 | 0.40986 | 0.41341 | 0.41527 | 0.411 | 0.59689 | 0.43047 | 0.40353
42810.4349 | -446 | 18.5608 | 18.6293 | 18.6151 | 18.6407 | 17.9833 | 16.6434 | 14.7096 | 16.7237 | 17.2131 | 17.3139 | 17.3267 | 16.8811 | 15.9295 | 14.554 | 15.0273 | 15.0163 | 15.5688 | 13.4326 | 13.5477 | 14.126 |  |  |  | 16.6401 | 15.9849 | 15.0997 | 10.2525 | 9.5425 | 9.9965 | 17.2565 | 16.387 | 15.1983 | 16.9167 | 16.2079 | 15.2138 | 10.8031 | 11.7599 |  | 12.2215 | 10.4242 | 10.2919 | 8.584 |  | 6.4633 | 6.4215 | 5.9888 | 6.1194 | 6.1546 | 6.3034 | 6.8511 | 4.7614 | 6.5057 | 4.6696 | 6.7312 | 8.1496 | 42.9133 | 47.2496 | 43.5785 | 15.168 |  |  | 0.18553 | -0.064965 | 0.1865 | 0.26482 | -0.20748 | -0.21336 | 0.10832 | 0.27582 | -0.21696 | -0.39103 | -0.53123 | 8.8715 | 8.873 | 2.0084 | 15.8211 | 16.714 | 17.2698 | 17.602 | 17.5723 | 16.5731 | 14.9261 | 16.8865 | 17.2191 | 17.5101 | 17.5605 | 17.305 | 16.5254 | 14.7691 | 6.0891 | 8.3597 | 5.4513 | 5.627 | 5.6344 | 6.7039 | 7.6635 | 15.8778 | 15.5019 | 15.3962 | 14.3349 | 14.2351 | 14.1781 |  |  |  | 10.7484 | 9.5845 | 9.0611 | 9.4677 | -0.017577 | -0.0267 | 12.7214 |  |  | 10.6204 |  |  | 16.9303 | 16.1291 | 15.1188 | 16.4272 | 15.7115 | 14.8355 | 10.6787 | 10.5418 | 11.3719 | 11.2704 | 9.1044 |  | 10.6182 | 8.144 | 9.9249 | 9.4832 | 11.0859 | 11.8065 |  | 12.3206 |  |  | 11.934 | 12.5788 | 12.5036 | [6 empty] | 12.5703 |  |  | 11.3439 |  |  | 9.1221 | 10.2843 | 11.8807 | 7.7066 | 9.1992 | 12.5308 | 7.8437 | 9.5288 | 12.4025 | 9.2056 | 10.4445 | 7.7239 | 10.3471 | 8.2404 | 10.1089 | 7.7987 | 9.5896 | 13.0512 | 10.4254 | 10.0937 | 11.514 | 8.2756 | 9.7161 | 12.6008 | 7.9343 | 10.2946 | 9.6742 | 9.7913 | 8.5366 | 10.1882 | 0.099177 | 20.955 | 0.03405 | 0.050961 | -38.0811 | 3.121 | -0.69 | 0.25 | 0.5051 | -0.297 | 0.50321 | 0.59964 | -0.53066 | -0.53812 | 0.38343 | 0.4097 | 0.41354 | 0.4146 | 0.41609 | 0.59838 | 0.43025 | 0.4039
42810.4349 | -445 | 18.5735 | 18.6393 | 18.6199 | 18.6462 | 17.9941 | 16.6591 | 14.7201 | 16.7447 | 17.2221 | 17.3258 | 17.3342 | 16.8929 | 15.9436 | 14.5543 | 15.0271 | 15.0251 | 15.5833 | 13.4338 | 13.5457 | 14.1208 |  |  |  | 16.6444 | 15.9785 | 15.0919 | 10.252 | 9.5368 | 9.991 | 17.2715 | 16.4103 | 15.2128 | 16.9325 | 16.2222 | 15.2283 | 10.8253 | 11.7372 |  | 12.2331 | 10.4221 | 10.3105 | 8.5791 |  | 6.4539 | 6.404 | 5.9733 | 6.1024 | 6.1305 | 6.2852 | 6.8176 | 4.6804 | 6.4976 | 4.688 | 6.7301 | 8.1475 | 42.9388 | 47.2453 | 43.5836 | 15.1946 |  |  | 0.21378 | 0.20642 | 0.33041 | -0.15442 | 0.009364 | -0.147 | 0.11687 | 0.38162 | -0.49972 | -0.50243 | -0.25166 | 8.8706 | 8.8714 | 2.0088 | 15.8139 | 16.7115 | 17.2676 | 17.5983 | 17.5677 | 16.5714 | 14.9286 | 16.8839 | 17.2218 | 17.5038 | 17.5599 | 17.3015 | 16.5197 | 14.7692 | 6.0064 | 8.3054 | 5.3874 | 5.6649 | 5.6655 | 6.6991 | 7.6678 | 15.8903 | 15.5136 | 15.4005 | 14.3457 | 14.2388 | 14.1827 |  |  |  | 10.7586 | 9.5812 | 9.0701 | 9.4756 | -0.071672 | -0.061328 | 12.7205 |  |  | 10.6045 |  |  | 16.9244 | 16.1209 | 15.1056 | 16.4218 | 15.7034 | 14.8254 | 10.6687 | 10.5315 | 11.3675 | 11.2695 | 9.0934 |  | 10.6161 | 8.113 | 9.9152 | 9.4887 | 11.0727 | 11.7881 |  | 12.3178 |  |  | 11.9361 | 12.5678 | 12.5101 | [6 empty] | 12.5787 |  |  | 11.3483 |  |  | 9.1209 | 10.2913 | 11.9007 | 7.7017 | 9.1832 | 12.5368 | 7.8409 | 9.534 | 12.3956 | 9.2008 | 10.4386 | 7.7052 | 10.3518 | 8.2532 | 10.1077 | 7.7902 | 9.5901 | 13.0285 | 10.4146 | 10.0785 | 11.5149 | 8.2692 | 9.7073 | 12.59 | 7.9294 | 10.296 | 9.6675 | 9.7854 | 8.5362 | 10.1885 | 0.071828 | 20.9559 | 0.032127 | 0.049687 | -38.0483 | 3.121 | -0.63 | 0.27 | 0.54219 | 0.52939 | 0.66977 | -0.45788 | 0.11273 | -0.44664 | 0.39825 | 0.40994 | 0.41408 | 0.41402 | 0.42472 | 0.60598 | 0.43112 | 0.40402
42810.4349 | -444 | 18.5777 | 18.6361 | 18.6172 | 18.6436 | 17.998 | 16.6588 | 14.7183 | 16.733 | 17.2259 | 17.325 | 17.3366 | 16.8864 | 15.9397 | 14.5629 | 15.0181 | 15.0254 | 15.5732 | 13.4281 | 13.5513 | 14.1157 |  |  |  | 16.6302 | 15.9704 | 15.0872 | 10.2518 | 9.5311 | 9.9865 | 17.2711 | 16.3979 | 15.2115 | 16.9339 | 16.2135 | 15.2229 | 10.8116 | 11.6874 |  | 12.2286 | 10.4214 | 10.3058 | 8.5566 |  | 6.4397 | 6.4037 | 5.9748 | 6.1033 | 6.1349 | 6.2732 | 6.8157 | 4.6184 | 6.5007 | 4.7249 | 6.7355 | 8.152 | 42.9621 | 47.2418 | 43.581 | 15.2274 |  |  | 0.28343 | 0.23796 | 0.1221 | -0.22211 | 0.33595 | -0.041856 | -0.15386 | 0.29357 | -0.23876 | -0.96945 | -0.21967 | 8.8658 | 8.867 | 2.0086 | 15.8149 | 16.7024 | 17.2647 | 17.5971 | 17.5744 | 16.5631 | 14.9255 | 16.8785 | 17.2219 | 17.5087 | 17.5574 | 17.2965 | 16.5229 | 14.7627 | 5.9626 | 8.2529 | 5.2761 | 5.597 | 5.7044 | 6.6979 | 7.668 | 15.89 | 15.5199 | 15.4004 | 14.3475 | 14.2479 | 14.1845 |  |  |  | 10.762 | 9.5888 | 9.0703 | 9.4593 | -0.039661 | 0.099771 | 12.7189 |  |  | 10.6021 |  |  | 16.9193 | 16.1201 | 15.1097 | 16.4172 | 15.7082 | 14.8231 | 10.6694 | 10.5332 | 11.3765 | 11.2759 | 9.0812 |  | 10.6267 | 8.1111 | 9.9221 | 9.4948 | 11.0795 | 11.7693 |  | 12.3355 |  |  | 11.9457 | 12.5696 | 12.5071 | [6 empty] | 12.5831 |  |  | 11.3556 |  |  | 9.1083 | 10.2755 | 11.8944 | 7.6858 | 9.1574 | 12.5234 | 7.8263 | 9.534 | 12.3902 | 9.1966 | 10.4309 | 7.6864 | 10.3339 | 8.2397 | 10.1085 | 7.7898 | 9.5923 | 13.0255 | 10.4142 | 10.0837 | 11.5198 | 8.2716 | 9.7247 | 12.5965 | 7.9256 | 10.2988 | 9.6687 | 9.7938 | 8.5431 | 10.1885 | 0.0084622 | 20.9541 | 0.032569 | 0.048963 | -38.0138 | 3.1209 | -0.54 | 0.26 | 0.6243 | 0.5684 | 0.40716 | -0.54914 | 0.67521 | -0.23833 | -0.45695 | 0.41063 | 0.41436 | 0.41407 | 0.42945 | 0.61837 | 0.4313 | 0.40458
42810.4349 | -443 | 18.5737 | 18.6261 | 18.6208 | 18.6414 | 18.0033 | 16.6531 | 14.7061 | 16.7382 | 17.223 | 17.3227 | 17.3317 | 16.8859 | 15.938 | 14.5639 | 15.0206 | 15.0119 | 15.5788 | 13.4313 | 13.5524 | 14.123 |  |  |  | 16.636 | 15.9822 | 15.0934 | 10.2518 | 9.5431 | 9.9663 | 17.2661 | 16.3936 | 15.203 | 16.9251 | 16.2121 | 15.2285 | 10.8089 | 11.6245 |  | 12.2267 | 10.4138 | 10.2988 | 8.5349 |  | 6.4277 | 6.3941 | 5.9705 | 6.096 | 6.1178 | 6.2602 | 6.7874 | 4.6494 | 6.4961 | 4.6452 | 6.7293 | 8.1555 | 42.9832 | 47.2516 | 43.5745 | 15.2524 |  |  | 0.040959 | 0.35361 | 0.080048 | -0.23525 | -0.041236 | -0.31653 | 0.38431 | 0.38425 | -0.29072 | -1.7096 | -0.2924 | 8.8706 | 8.872 | 2.0085 | 15.8254 | 16.713 | 17.2658 | 17.6097 | 17.5761 | 16.5742 | 14.9356 | 16.8893 | 17.2277 | 17.5144 | 17.5683 | 17.3167 | 16.5309 | 14.778 | 5.949 | 8.2878 | 5.2115 | 5.5163 | 5.7128 | 6.6896 | 7.6664 | 15.891 | 15.5071 | 15.4003 | 14.34 | 14.235 | 14.1795 |  |  |  | 10.7625 | 9.5811 | 9.0722 | 9.4495 | 0.0077476 | 0.16131 | 12.7176 |  |  | 10.6058 |  |  | 16.9253 | 16.1194 | 15.1116 | 16.4175 | 15.7089 | 14.8263 | 10.6738 | 10.536 | 11.3866 | 11.2813 | 9.0439 |  | 10.6175 | 8.07 | 9.9223 | 9.4898 | 11.08 | 11.7423 |  | 12.3188 |  |  | 11.9523 | 12.5734 | 12.5203 | [6 empty] | 12.5693 |  |  | 11.363 |  |  | 9.1038 | 10.2707 | 11.8979 | 7.6888 | 9.1351 | 12.5278 | 7.8243 | 9.5285 | 12.3758 | 9.1934 | 10.432 | 7.6691 | 10.3111 | 8.239 | 10.1007 | 7.7813 | 9.5936 | 13.0072 | 10.413 | 10.0838 | 11.5215 | 8.2713 | 9.7277 | 12.6 | 7.9166 | 10.2932 | 9.671 | 9.7988 | 8.5501 | 10.1932 | 0.16774 | 20.9552 | 0.032161 | 0.048044 | -38.0678 | 3.1209 | -0.55 | 0.29 | 0.23731 | 0.69288 | 0.32966 | -0.56514 | -0.23655 | -0.65539 | 0.72215 | 0.41136 | 0.41551 | 0.41423 | 0.43 | 0.62536 | 0.43181 | 0.40487
42810.4349 | -442 | 18.582 | 18.6422 | 18.6288 | 18.6483 | 18.0082 | 16.6581 | 14.7166 | 16.7445 | 17.234 | 17.3306 | 17.3392 | 16.8944 | 15.9452 | 14.5689 | 15.0274 | 15.0187 | 15.5742 | 13.4325 | 13.5533 | 14.1211 |  |  |  | 16.6298 | 15.9796 | 15.0951 | 10.2518 | 9.5381 | 9.9604 | 17.2741 | 16.3953 | 15.2129 | 16.9372 | 16.2155 | 15.2301 | 10.8144 | 11.5803 |  | 12.2331 | 10.4109 | 10.3074 | 8.5189 |  | 6.4217 | 6.3805 | 5.9572 | 6.0859 | 6.0991 | 6.2449 | 6.7361 | 4.6968 | 6.4953 | 4.5529 | 6.7328 | 8.1577 | 42.9813 | 47.2516 | 43.5595 | 15.2755 |  |  | 0.15267 | 0.34376 | 0.046536 | -0.090682 | -0.1122 | -0.51695 | 0.2864 | 0.19434 | -0.42149 | -0.44369 | -0.3375 | 8.8703 | 8.8713 | 2.0086 | 15.8332 | 16.7117 | 17.2688 | 17.6064 | 17.5721 | 16.5757 | 14.9373 | 16.8895 | 17.229 | 17.5209 | 17.5676 | 17.3158 | 16.5245 | 14.7798 | 5.9793 | 8.3104 | 5.2042 | 5.4639 | 5.7584 | 6.6982 | 7.6701 | 15.8878 | 15.515 | 15.4017 | 14.3369 | 14.235 | 14.1812 |  |  |  | 10.7628 | 9.5856 | 9.0656 | 9.4681 | -0.042295 | 0.058367 | 12.7106 |  |  | 10.5845 |  |  | 16.9233 | 16.1194 | 15.1072 | 16.4183 | 15.7039 | 14.8211 | 10.6753 | 10.528 | 11.3904 | 11.2918 | 9.0637 |  | 10.622 | 7.9858 | 9.9205 | 9.4907 | 11.0802 | 11.7201 |  | 12.3229 |  |  | 11.9521 | 12.5527 | 12.529 | [6 empty] | 12.5614 |  |  | 11.3435 |  |  | 9.0937 | 10.2704 | 11.889 | 7.6683 | 9.109 | 12.5173 | 7.8183 | 9.5277 | 12.3636 | 9.1865 | 10.43 | 7.6088 | 10.3002 | 8.2363 | 10.0848 | 7.7823 | 9.6045 | 13.0013 | 10.4034 | 10.083 | 11.5264 | 8.2601 | 9.7249 | 12.5891 | 7.9146 | 10.2972 | 9.6692 | 9.7952 | 8.5413 | 10.1994 | 0.084539 | 20.9544 | 0.031065 | 0.047342 | -38.1053 | 3.1209 | -0.81 | 0.3 | 0.45817 | 0.68314 | 0.25135 | -0.35087 | -0.39019 | -0.83753 | 0.6234 | 0.41096 | 0.41779 | 0.4142 | 0.42762 | 0.6266 | 0.43243 | 0.40436
42810.4349 | -441 | 18.5734 | 18.6355 | 18.6244 | 18.6396 | 18.0015 | 16.6493 | 14.7061 | 16.7385 | 17.2237 | 17.3207 | 17.3317 | 16.888 | 15.9419 | 14.5556 | 15.0256 | 15.0183 | 15.5759 | 13.435 | 13.5564 | 14.1263 |  |  |  | 16.6357 | 15.983 | 15.1003 | 10.2556 | 9.5473 | 9.9487 | 17.2761 | 16.3971 | 15.2145 | 16.9362 | 16.2152 | 15.2265 | 10.8101 | 11.5237 |  | 12.2341 | 10.4047 | 10.3037 | 8.4877 |  | 6.4178 | 6.374 | 5.9543 | 6.073 | 6.0885 | 6.2335 | 6.6959 | 4.6167 | 6.5031 | 4.5079 | 6.7331 | 8.1547 | 42.9803 | 47.2495 | 43.5348 | 15.2998 |  |  | 0.14478 | 0.13217 | 0.1589 | -0.26285 | -0.15163 | -0.58069 | 0.29954 | 0.14637 | -0.12083 | -0.75671 | -0.37287 | 8.8623 | 8.8636 | 2.0083 | 15.8347 | 16.712 | 17.2637 | 17.6037 | 17.5812 | 16.5715 | 14.9254 | 16.8839 | 17.2172 | 17.5147 | 17.5609 | 17.3051 | 16.528 | 14.7746 | 6.0101 | 8.3268 | 5.2568 | 5.4493 | 5.7502 | 6.6992 | 7.6802 | 15.8867 | 15.5124 | 15.3968 | 14.337 | 14.2362 | 14.1799 |  |  |  | 10.7591 | 9.5761 | 9.0586 | 9.5008 | 0.0071398 | -0.11534 | 12.7174 |  |  | 10.5509 |  |  | 16.9215 | 16.1228 | 15.1073 | 16.4167 | 15.705 | 14.8262 | 10.674 | 10.5264 | 11.3946 | 11.3089 | 9.0702 |  | 10.6205 | 7.8884 | 9.922 | 9.4967 | 11.0769 | 11.7465 |  | 12.3273 |  |  | 11.9585 | 12.5606 | 12.5535 | [6 empty] | 12.5827 |  |  | 11.3513 |  |  | 9.0959 | 10.2689 | 11.8952 | 7.6191 | 9.0215 | 12.5018 | 7.8142 | 9.524 | 12.3556 | 9.1908 | 10.4294 | 7.5722 | 10.2941 | 8.2298 | 10.0885 | 7.776 | 9.6064 | 12.9884 | 10.3965 | 10.0788 | 11.5249 | 8.2431 | 9.7199 | 12.5736 | 7.9116 | 10.2924 | 9.6605 | 9.7874 | 8.5453 | 10.2033 | 0.22937 | 20.9528 | 0.031237 | 0.047625 | -37.9664 | 3.1209 | -0.81 | 0.28 | 0.44616 | 0.42358 | 0.46445 | -0.59735 | -0.45358 | -0.88765 | 0.63753 | 0.41073 | 0.42055 | 0.41393 | 0.42433 | 0.62192 | 0.43316 | 0.40334
42810.4349 | -440 | 18.5815 | 18.6285 | 18.6269 | 18.6389 | 18.0024 | 16.6613 | 14.713 | 16.7427 | 17.2294 | 17.3217 | 17.336 | 16.8857 | 15.9477 | 14.5565 | 15.0224 | 15.0126 | 15.5752 | 13.4334 | 13.5549 | 14.1213 |  |  |  | 16.6336 | 15.974 | 15.086 | 10.2541 | 9.5516 | 9.944 | 17.2756 | 16.4018 | 15.2169 | 16.9352 | 16.2259 | 15.2213 | 10.8198 | 11.4674 |  | 12.2252 | 10.4044 | 10.304 | 8.4535 |  | 6.4159 | 6.376 | 5.9515 | 6.0692 | 6.0794 | 6.2151 | 6.661 | 4.5171 | 6.5065 | 4.5213 | 6.7364 | 8.1495 | 43 | 47.2261 | 43.5214 | 15.3199 |  |  | 0.10207 | 0.26359 | 0.050476 | -0.17348 | -0.1812 | -0.22454 | 0.4658 | 0.052404 | 0.54256 | -0.016537 | -0.45732 | 8.8692 | 8.8703 | 2.0085 | 15.8318 | 16.7108 | 17.267 | 17.608 | 17.585 | 16.5729 | 14.9295 | 16.8914 | 17.2256 | 17.5213 | 17.5591 | 17.3087 | 16.5309 | 14.7745 | 6.0366 | 8.2987 | 5.3569 | 5.4477 | 5.7163 | 6.7018 | 7.6729 | 15.8933 | 15.5147 | 15.3962 | 14.3369 | 14.2424 | 14.1848 |  |  |  | 10.7636 | 9.5735 | 9.0589 | 9.5072 | -0.27123 | -0.1097 | 12.7126 |  |  | 10.5389 |  |  | 16.9173 | 16.1176 | 15.1039 | 16.4149 | 15.701 | 14.8222 | 10.6693 | 10.5237 | 11.3934 | 11.3135 | 9.0693 |  | 10.6153 | 7.7861 | 9.9145 | 9.5189 | 11.0832 | 11.7943 |  | 12.3255 |  |  | 11.9623 | 12.5614 | 12.5567 | [6 empty] | 12.5771 |  |  | 11.3582 |  |  | 9.0938 | 10.2807 | 11.8963 | 7.6011 | 8.9638 | 12.508 | 7.8141 | 9.5319 | 12.351 | 9.1901 | 10.4384 | 7.5737 | 10.2879 | 8.2263 | 10.0928 | 7.775 | 9.6148 | 12.9843 | 10.3987 | 10.074 | 11.524 | 8.2374 | 9.7311 | 12.5678 | 7.9111 | 10.289 | 9.6599 | 9.7865 | 8.5415 | 10.2101 | -0.015035 | 20.9535 | 0.031714 | 0.048609 | -38.0427 | 3.1208 | -0.36 | 0.22 | 0.37461 | 0.5982 | 0.26177 | -0.48529 | -0.49583 | -0.55195 | 0.79497 | 0.41058 | 0.42314 | 0.41352 | 0.42168 | 0.60997 | 0.43443 | 0.40331
42810.435 | -439 | 18.5851 | 18.6436 | 18.629 | 18.6501 | 18.0025 | 16.6626 | 14.7264 | 16.7395 | 17.2327 | 17.3213 | 17.3462 | 16.892 | 15.9497 | 14.5709 | 15.0278 | 15.0193 | 15.5766 | 13.4352 | 13.5504 | 14.1183 |  |  |  | 16.6325 | 15.9738 | 15.0836 | 10.2527 | 9.553 | 9.9399 | 17.2769 | 16.3984 | 15.2102 | 16.9312 | 16.2158 | 15.2269 | 10.8154 | 11.419 |  | 12.213 | 10.4072 | 10.2985 | 8.4164 |  | 6.4172 | 6.3644 | 5.9432 | 6.07 | 6.0685 | 6.2111 | 6.6283 | 4.4831 | 6.5004 | 4.4694 | 6.7352 | 8.1573 | 43.0141 | 47.2086 | 43.5079 | 15.3373 |  |  | 0.13099 | 0.17488 | -0.042832 | -0.15574 | -0.073432 | -0.1148 | 0.51508 | 0.11549 | -0.70483 | -0.69167 | -0.30471 | 8.8708 | 8.872 | 2.0086 | 15.8328 | 16.7205 | 17.2723 | 17.6023 | 17.5878 | 16.5795 | 14.937 | 16.8923 | 17.2234 | 17.528 | 17.564 | 17.3111 | 16.5328 | 14.7746 | 5.9887 | 8.2732 | 5.4306 | 5.5072 | 5.702 | 6.6985 | 7.6731 | 15.8954 | 15.5175 | 15.4006 | 14.3472 | 14.2398 | 14.1779 |  |  |  | 10.7661 | 9.5694 | 9.0548 | 9.5132 | -0.057692 | -0.1129 | 12.7067 |  |  | 10.5428 |  |  | 16.9191 | 16.1134 | 15.0998 | 16.4194 | 15.7098 | 14.8175 | 10.665 | 10.5252 | 11.3999 | 11.3156 | 9.0862 |  | 10.6192 | 7.6212 | 9.9174 | 9.5341 | 11.0827 | 11.8313 |  | 12.3205 |  |  | 11.9387 | 12.5554 | 12.5297 | [6 empty] | 12.5807 |  |  | 11.3484 |  |  | 9.0849 | 10.28 | 11.8916 | 7.6129 | 8.9264 | 12.5091 | 7.8137 | 9.5275 | 12.3414 | 9.1926 | 10.4407 | 7.5714 | 10.2851 | 8.2117 | 10.0818 | 7.781 | 9.616 | 12.9812 | 10.4002 | 10.0848 | 11.5229 | 8.2382 | 9.7354 | 12.5667 | 7.9158 | 10.2974 | 9.6659 | 9.7842 | 8.5379 | 10.2088 | 0.11054 | 20.9539 | 0.032775 | 0.048363 | -38.0313 | 3.1208 | -0.21 | 0.32 | 0.42437 | 0.48723 | -0.24113 | -0.4598 | -0.31564 | -0.39465 | 0.83596 | 0.41024 | 0.42782 | 0.41308 | 0.42662 | 0.60179 | 0.43531 | 0.40322
42810.435 | -438 | 18.5803 | 18.6437 | 18.6302 | 18.6501 | 18.0041 | 16.6552 | 14.7196 | 16.742 | 17.2309 | 17.3206 | 17.3345 | 16.8954 | 15.9444 | 14.5709 | 15.0315 | 15.0254 | 15.5768 | 13.4344 | 13.5522 | 14.1125 |  |  |  | 16.6376 | 15.9757 | 15.0907 | 10.2564 | 9.5562 | 9.9385 | 17.2878 | 16.4037 | 15.2129 | 16.9292 | 16.2109 | 15.2315 | 10.8109 | 11.4254 |  | 12.2286 | 10.4009 | 10.2943 | 8.3818 |  | 6.4123 | 6.3586 | 5.9425 | 6.0652 | 6.0648 | 6.2048 | 6.6023 | 4.4663 | 6.4971 | 4.3817 | 6.737 | 8.1623 | 43.0327 | 47.1783 | 43.5038 | 15.3522 |  |  | 0.003503 | 0.011915 | 0.15299 | 0.10119 | 0.01922 | -0.032 | 0.42046 | -0.067848 | -0.4643 | -1.0074 | -0.35181 | 8.869 | 8.8699 | 2.0084 | 15.8271 | 16.7162 | 17.2681 | 17.6075 | 17.5829 | 16.5742 | 14.9308 | 16.8865 | 17.2229 | 17.5165 | 17.5667 | 17.3083 | 16.5332 | 14.7709 | 5.9835 | 8.2706 | 5.5381 | 5.5949 | 5.6757 | 6.6919 | 7.6708 | 15.9024 | 15.5212 | 15.3977 | 14.3475 | 14.2356 | 14.1867 |  |  |  | 10.7587 | 9.5563 | 9.0525 | 9.5243 | 0.0077476 | -0.10104 | 12.7051 |  |  | 10.5459 |  |  | 16.9206 | 16.1134 | 15.1024 | 16.4199 | 15.7115 | 14.8173 | 10.6586 | 10.5181 | 11.4048 | 11.3219 | 9.0987 |  | 10.6117 | 7.4704 | 9.9116 | 9.54 | 11.0739 | 11.8664 |  | 12.3195 |  |  | 11.9341 | 12.5532 | 12.5301 | [6 empty] | 12.5959 |  |  | 11.3481 |  |  | 9.088 | 10.276 | 11.888 | 7.6145 | 8.9096 | 12.514 | 7.8099 | 9.5205 | 12.3348 | 9.1999 | 10.4367 | 7.5834 | 10.2905 | 8.2124 | 10.0804 | 7.7861 | 9.6247 | 12.9799 | 10.4013 | 10.094 | 11.5167 | 8.2382 | 9.7295 | 12.5626 | 7.9316 | 10.3125 | 9.6778 | 9.7867 | 8.542 | 10.2014 | 0.0096178 | 20.9532 | 0.032896 | 0.048667 | -38.0692 | 3.1208 | -0.04 | 0.28 | 0.069398 | 0.12718 | 0.45571 | 0.37063 | 0.16148 | -0.20836 | 0.75528 | 0.40964 | 0.43182 | 0.41263 | 0.42643 | 0.58958 | 0.43613 | 0.40267
42810.435 | -437 | 18.5901 | 18.6456 | 18.6271 | 18.6473 | 18.0081 | 16.6601 | 14.7232 | 16.7415 | 17.2305 | 17.326 | 17.3388 | 16.8945 | 15.9525 | 14.568 | 15.0318 | 15.0234 | 15.5745 | 13.4325 | 13.5512 | 14.121 |  |  |  | 16.6365 | 15.9782 | 15.092 | 10.2584 | 9.5572 | 9.9433 | 17.2857 | 16.4039 | 15.2175 | 16.9268 | 16.2177 | 15.2363 | 10.8201 | 11.4027 |  | 12.2274 | 10.41 | 10.2879 | 8.3769 |  | 6.4089 | 6.3501 | 5.9301 | 6.0505 | 6.0489 | 6.185 | 6.5659 | 4.3756 | 6.4855 | 4.3109 | 6.7308 | 8.156 | 43.0284 | 47.1469 | 43.5065 | 15.3709 |  |  | 0.037675 | -0.002541 | -0.002748 | -0.37455 | -0.1306 | 0.21704 | 0.43163 | 0.26991 | -0.47345 | -0.57481 | -0.7963 | 8.866 | 8.8676 | 2.0086 | 15.8375 | 16.7181 | 17.2732 | 17.6095 | 17.5798 | 16.5732 | 14.9279 | 16.888 | 17.2212 | 17.5175 | 17.5622 | 17.3082 | 16.5301 | 14.7663 | 6.0188 | 8.2586 | 5.5318 | 5.6554 | 5.6782 | 6.6886 | 7.6653 | 15.9096 | 15.5228 | 15.4037 | 14.3404 | 14.2436 | 14.1858 |  |  |  | 10.7636 | 9.5545 | 9.0601 | 9.5304 | 0.012407 | 0.035406 | 12.6936 |  |  | 10.5436 |  |  | 16.9166 | 16.1103 | 15.103 | 16.4171 | 15.7018 | 14.8145 | 10.6472 | 10.5139 | 11.4034 | 11.3235 | 9.1005 |  | 10.6074 | 7.4411 | 9.9029 | 9.5536 | 11.0804 | 11.8974 |  | 12.3168 |  |  | 11.9313 | 12.5618 | 12.5359 | [6 empty] | 12.6092 |  |  | 11.3566 |  |  | 9.0916 | 10.277 | 11.8838 | 7.6147 | 8.8924 | 12.5199 | 7.8116 | 9.5127 | 12.3273 | 9.1987 | 10.4367 | 7.5862 | 10.2962 | 8.2116 | 10.0816 | 7.7898 | 9.6258 | 12.976 | 10.3953 | 10.0836 | 11.5122 | 8.2286 | 9.7279 | 12.5609 | 7.9369 | 10.3167 | 9.6742 | 9.7746 | 8.5456 | 10.1894 | 0.0076918 | 20.952 | 0.033344 | 0.049181 | -38.0434 | 3.1208 | -0.14 | 0.29 | 0.22759 | -0.05873 | -0.061075 | -0.71304 | -0.42092 | 0.54263 | 0.76522 | 0.40946 | 0.43235 | 0.41247 | 0.42212 | 0.58964 | 0.43657 | 0.40266
42810.435 | -436 | 18.5863 | 18.6349 | 18.6325 | 18.6487 | 18.0059 | 16.6522 | 14.7186 | 16.7402 | 17.221 | 17.3218 | 17.3304 | 16.8871 | 15.9479 | 14.5677 | 15.0351 | 15.0243 | 15.5771 | 13.4262 | 13.5492 | 14.1149 |  |  |  | 16.6316 | 15.976 | 15.093 | 10.2464 | 9.5552 | 9.9442 | 17.2675 | 16.4031 | 15.2094 | 16.9304 | 16.2082 | 15.2284 | 10.8146 | 11.4007 |  | 12.2132 | 10.4059 | 10.2847 | 8.3429 |  | 6.407 | 6.3559 | 5.9335 | 6.0423 | 6.0584 | 6.2013 | 6.5772 | 4.2663 | 6.4879 | 4.3221 | 6.7324 | 8.1543 | 43.0376 | 47.1407 | 43.5027 | 15.3812 |  |  | 0.11259 | -0.087965 | 0.069532 | 0.038114 | -0.03532 | -0.3415 | 0.52756 | 0.39345 | -0.74452 | -0.51418 | -0.44023 | 8.8703 | 8.8713 | 2.0084 | 15.8468 | 16.7239 | 17.2779 | 17.6056 | 17.5828 | 16.5703 | 14.9386 | 16.8962 | 17.2248 | 17.5233 | 17.5636 | 17.3162 | 16.5264 | 14.7708 | 6.0037 | 8.2688 | 5.4695 | 5.7181 | 5.7595 | 6.6875 | 7.6679 | 15.9053 | 15.523 | 15.4053 | 14.3442 | 14.24 | 14.1838 |  |  |  | 10.7641 | 9.5491 | 9.0609 | 9.4936 | 0.12201 | 0.0068 | 12.6934 |  |  | 10.5544 |  |  | 16.924 | 16.1182 | 15.1035 | 16.4205 | 15.7044 | 14.8203 | 10.6386 | 10.522 | 11.4187 | 11.316 | 9.0796 |  | 10.6107 | 7.4542 | 9.9041 | 9.55 | 11.0759 | 11.954 |  | 12.3122 |  |  | 11.9248 | 12.5555 | 12.5319 | [6 empty] | 12.6051 |  |  | 11.367 |  |  | 9.0888 | 10.2785 | 11.8784 | 7.6183 | 8.89 | 12.5188 | 7.8005 | 9.5098 | 12.3201 | 9.1934 | 10.4349 | 7.5947 | 10.2968 | 8.1965 | 10.0776 | 7.8035 | 9.6328 | 12.9814 | 10.3921 | 10.0795 | 11.5091 | 8.2347 | 9.7392 | 12.5635 | 7.9489 | 10.3221 | 9.678 | 9.7752 | 8.5456 | 10.1891 | -0.078593 | 20.9545 | 0.033458 | 0.049767 | -38.0225 | 3.1209 | -0.29 | 0.27 | 0.39344 | -0.34556 | 0.30722 | 0.22746 | -0.2189 | -0.68068 | 0.84602 | 0.41015 | 0.43202 | 0.41242 | 0.42369 | 0.59686 | 0.43733 | 0.4037
42810.435 | -435 | 18.5858 | 18.6413 | 18.6284 | 18.6492 | 18.0064 | 16.6585 | 14.7239 | 16.7427 | 17.2188 | 17.3268 | 17.3337 | 16.8898 | 15.9448 | 14.5709 | 15.037 | 15.0203 | 15.571 | 13.422 | 13.5496 | 14.1135 |  |  |  | 16.638 | 15.9795 | 15.0945 | 10.253 | 9.5542 | 9.9563 | 17.2783 | 16.4042 | 15.21 | 16.9389 | 16.2124 | 15.2348 | 10.8164 | 11.4144 |  | 12.2209 | 10.4197 | 10.2902 | 8.3413 |  | 6.4129 | 6.3593 | 5.9376 | 6.0451 | 6.0645 | 6.2271 | 6.6197 | 4.2157 | 6.4791 | 4.3069 | 6.739 | 8.169 | 43.0427 | 47.1376 | 43.5042 | 15.3886 |  |  | 0.020591 | -0.10505 | 0.12473 | -0.10579 | -0.13257 | 0.5042 | 0.48617 | 0.43682 | 1.2869 | -0.29641 | -0.54097 | 8.8697 | 8.8711 | 2.0084 | 15.8459 | 16.7252 | 17.2697 | 17.602 | 17.581 | 16.5777 | 14.9231 | 16.8957 | 17.2161 | 17.5201 | 17.5622 | 17.3076 | 16.5282 | 14.7687 | 5.9542 | 8.2988 | 5.424 | 5.7964 | 5.8276 | 6.6921 | 7.6688 | 15.904 | 15.5129 | 15.3974 | 14.3425 | 14.2403 | 14.1777 |  |  |  | 10.7637 | 9.5564 | 9.0618 | 9.4515 | 0.038543 | -0.13153 | 12.6944 |  |  | 10.5606 |  |  | 16.921 | 16.1177 | 15.1044 | 16.4176 | 15.701 | 14.8221 | 10.6062 | 10.5194 | 11.4253 | 11.305 | 9.0787 |  | 10.6161 | 7.48 | 9.9004 | 9.5406 | 11.0846 | 12.0346 |  | 12.3108 |  |  | 11.9038 | 12.5424 | 12.5163 | [6 empty] | 12.605 |  |  | 11.3728 |  |  | 9.0896 | 10.2805 | 11.8772 | 7.627 | 8.9145 | 12.5231 | 7.7874 | 9.5047 | 12.3059 | 9.195 | 10.436 | 7.614 | 10.3054 | 8.19 | 10.0744 | 7.8106 | 9.6323 | 12.9868 | 10.3858 | 10.0816 | 11.504 | 8.2343 | 9.7474 | 12.5666 | 7.9616 | 10.3212 | 9.677 | 9.7745 | 8.544 | 10.1913 | 0.026181 | 20.9522 | 0.033826 | 0.049977 | -38.0963 | 3.1208 | -0.28 | 0.31 | 0.16826 | -0.37763 | 0.41149 | -0.37896 | -0.42412 | 0.82711 | 0.81219 | 0.41035 | 0.43118 | 0.41296 | 0.42971 | 0.60203 | 0.43743 | 0.40486
42810.435 | -434 | 18.588 | 18.6395 | 18.6308 | 18.65 | 18.0067 | 16.6598 | 14.7267 | 16.7444 | 17.2298 | 17.3253 | 17.3362 | 16.8884 | 15.9414 | 14.5698 | 15.0329 | 15.0271 | 15.5782 | 13.4331 | 13.5476 | 14.1238 |  |  |  | 16.635 | 15.9841 | 15.0951 | 10.2628 | 9.5637 | 9.9663 | 17.2868 | 16.4017 | 15.213 | 16.9446 | 16.2159 | 15.232 | 10.8238 | 11.4458 |  | 12.223 | 10.4268 | 10.2897 | 8.3409 |  | 6.3889 | 6.3319 | 5.9126 | 6.0236 | 6.0388 | 6.212 | 6.6118 | 4.1828 | 6.4644 | 4.2066 | 6.7217 | 8.1605 | 43.0385 | 47.1176 | 43.5186 | 15.4009 |  |  | 0.25584 | -0.042625 | 0.17467 | -0.32199 | 0.11779 | 0.11125 | 0.14052 | 0.61424 | -0.26756 | -1.0414 | -0.34346 | 8.8693 | 8.8706 | 2.0087 | 15.8382 | 16.7231 | 17.2676 | 17.6014 | 17.5732 | 16.5722 | 14.9288 | 16.8837 | 17.2184 | 17.5116 | 17.5544 | 17.3075 | 16.5306 | 14.7708 | 5.9305 | 8.2507 | 5.4041 | 5.7478 | 5.8533 | 6.6907 | 7.6692 | 15.9052 | 15.5231 | 15.398 | 14.3426 | 14.2362 | 14.1753 |  |  |  | 10.7597 | 9.5556 | 9.0745 | 9.4044 | 0.017067 | -0.19476 | 12.6922 |  |  | 10.567 |  |  | 16.9179 | 16.1133 | 15.1046 | 16.4168 | 15.7034 | 14.8168 | 10.5518 | 10.5177 | 11.4211 | 11.2912 | 9.0303 |  | 10.6014 | 7.4504 | 9.8976 | 9.5092 | 11.0758 | 12.0916 |  | 12.3075 |  |  | 11.8826 | 12.5314 | 12.5044 | [6 empty] | 12.6083 |  |  | 11.3692 |  |  | 9.0818 | 10.2752 | 11.8656 | 7.619 | 8.9327 | 12.5323 | 7.7705 | 9.4853 | 12.2834 | 9.1886 | 10.4282 | 7.6246 | 10.3008 | 8.1672 | 10.0705 | 7.8102 | 9.6388 | 12.9805 | 10.3798 | 10.0794 | 11.4964 | 8.2287 | 9.7465 | 12.5758 | 7.9676 | 10.3237 | 9.6785 | 9.7714 | 8.5439 | 10.1872 | 0.17988 | 20.9559 | 0.034199 | 0.050136 | -37.987 | 3.1208 | -0.37 | 0.33 | 0.59311 | -0.24053 | 0.48692 | -0.66109 | 0.39976 | 0.38851 | 0.43664 | 0.41121 | 0.43191 | 0.41354 | 0.43219 | 0.60428 | 0.43769 | 0.40603
42810.435 | -433 | 18.5897 | 18.6451 | 18.6337 | 18.6514 | 18.0048 | 16.6536 | 14.7277 | 16.7374 | 17.2333 | 17.32 | 17.3407 | 16.8932 | 15.9409 | 14.5606 | 15.0373 | 15.0168 | 15.5721 | 13.4269 | 13.5465 | 14.1114 |  |  |  | 16.6304 | 15.9834 | 15.093 | 10.2541 | 9.5574 | 9.974 | 17.2824 | 16.4037 | 15.2133 | 16.939 | 16.2175 | 15.2264 | 10.8176 | 11.4681 |  | 12.2219 | 10.4197 | 10.293 | 8.3384 |  | 6.3873 | 6.336 | 5.9137 | 6.0214 | 6.0331 | 6.2035 | 6.5911 | 4.2314 | 6.4755 | 4.1551 | 6.7182 | 8.1582 | 43.0112 | 47.1 | 43.5156 | 15.401 |  |  | -0.18772 | -0.21347 | 0.071504 | -0.41858 | -0.051092 | -0.0872 | 0.2864 | 0.43813 | -0.69957 | -1.1243 | -0.42056 | 8.8683 | 8.8691 | 2.0082 | 15.8401 | 16.7159 | 17.2601 | 17.6005 | 17.5762 | 16.5685 | 14.9276 | 16.8832 | 17.2189 | 17.5079 | 17.5541 | 17.2998 | 16.5242 | 14.7656 | 5.9603 | 8.2581 | 5.3469 | 5.7503 | 5.8862 | 6.697 | 7.6689 | 15.9023 | 15.5087 | 15.398 | 14.3449 | 14.2325 | 14.1774 |  |  |  | 10.7628 | 9.5506 | 9.0535 | 9.3737 | -0.11239 | -0.17989 | 12.6845 |  |  | 10.5682 |  |  | 16.9157 | 16.1155 | 15.0978 | 16.4191 | 15.71 | 14.8138 | 10.4942 | 10.5129 | 11.4273 | 11.2879 | 8.9982 |  | 10.5942 | 7.4473 | 9.8973 | 9.4933 | 11.0768 | 12.146 |  | 12.3129 |  |  | 11.8572 | 12.5094 | 12.5043 | [6 empty] | 12.6084 |  |  | 11.3684 |  |  | 9.0772 | 10.273 | 11.8624 | 7.5814 | 8.9442 | 12.5402 | 7.7554 | 9.4832 | 12.2566 | 9.1828 | 10.4282 | 7.5895 | 10.2974 | 8.1513 | 10.0663 | 7.8127 | 9.6245 | 12.9755 | 10.3661 | 10.0761 | 11.4839 | 8.2204 | 9.7365 | 12.5602 | 7.9634 | 10.3199 | 9.6615 | 9.7559 | 8.5291 | 10.1619 | 0.10495 | 20.9539 | 0.035444 | 0.051858 | -38.0196 | 3.1208 | -0.76 | 0.26 | -0.50805 | -0.53829 | 0.31154 | -0.75377 | -0.26328 | -0.34396 | 0.62335 | 0.41186 | 0.43199 | 0.41402 | 0.42961 | 0.6106 | 0.43755 | 0.40699
42810.435 | -432 | 18.5898 | 18.6376 | 18.6315 | 18.6489 | 18.0086 | 16.6528 | 14.7185 | 16.7425 | 17.2265 | 17.3204 | 17.3411 | 16.8952 | 15.9518 | 14.5709 | 15.0365 | 15.0225 | 15.5692 | 13.4254 | 13.5473 | 14.109 |  |  |  | 16.6369 | 15.9684 | 15.0933 | 10.2558 | 9.5579 | 9.9527 | 17.2838 | 16.4042 | 15.2111 | 16.937 | 16.219 | 15.2253 | 10.8157 | 11.4791 |  | 12.2182 | 10.4097 | 10.2907 | 8.366 |  | 6.3967 | 6.3425 | 5.9128 | 6.0279 | 6.0345 | 6.1978 | 6.5724 | 4.2477 | 6.4748 | 4.1186 | 6.7241 | 8.1778 | 42.9927 | 47.1065 | 43.5249 | 15.3973 |  |  | 0.045559 | -0.009113 | 0.005792 | -0.11434 | -0.15163 | -0.30865 | 0.63796 | 0.32576 | -0.25355 | -0.42292 | -0.10184 | 8.8686 | 8.8699 | 2.0085 | 15.8464 | 16.7186 | 17.2677 | 17.6048 | 17.5774 | 16.5813 | 14.9343 | 16.8943 | 17.2248 | 17.5128 | 17.5655 | 17.3101 | 16.5291 | 14.773 | 5.9586 | 8.249 | 5.3121 | 5.6849 | 5.8336 | 6.6871 | 7.666 | 15.9094 | 15.5182 | 15.4077 | 14.3456 | 14.2433 | 14.1789 |  |  |  | 10.7639 | 9.5642 | 9.0611 | 9.3436 | -0.009676 | -0.12343 | 12.6857 |  |  | 10.5765 |  |  | 16.9198 | 16.1211 | 15.0998 | 16.4234 | 15.7102 | 14.8179 | 10.4462 | 10.5152 | 11.4362 | 11.2971 | 8.9147 |  | 10.5906 | 7.4186 | 9.8807 | 9.4802 | 11.0647 | 12.1954 |  | 12.3032 |  |  | 11.8359 | 12.4907 | 12.5083 | [6 empty] | 12.5823 |  |  | 11.3557 |  |  | 9.0821 | 10.2778 | 11.8742 | 7.5692 | 8.9658 | 12.5483 | 7.7623 | 9.4778 | 12.2635 | 9.1843 | 10.4306 | 7.5797 | 10.3039 | 8.1467 | 10.0696 | 7.8375 | 9.6259 | 12.9887 | 10.3866 | 10.0893 | 11.4866 | 8.2281 | 9.747 | 12.5715 | 7.9679 | 10.3273 | 9.6752 | 9.7553 | 8.5302 | 10.1567 | 0.14367 | 20.9526 | 0.033613 | 0.050679 | -37.9702 | 3.1207 | -0.9 | 0.37 | 0.25028 | -0.11122 | 0.088668 | -0.39396 | -0.45355 | -0.6471 | 0.93033 | 0.41406 | 0.43224 | 0.41399 | 0.42864 | 0.61413 | 0.43673 | 0.40786
42810.435 | -431 | 18.5927 | 18.6413 | 18.6237 | 18.6441 | 18.0079 | 16.6507 | 14.7212 | 16.7347 | 17.2273 | 17.3169 | 17.3429 | 16.8957 | 15.941 | 14.556 | 15.0346 | 15.012 | 15.5629 | 13.4201 | 13.5404 | 14.1047 |  |  |  | 16.643 | 15.9732 | 15.0809 | 10.2446 | 9.5555 | 9.9066 | 17.2828 | 16.4072 | 15.2105 | 16.9312 | 16.2255 | 15.2287 | 10.812 | 11.4867 |  | 12.2158 | 10.4185 | 10.2883 | 8.3897 |  | 6.3821 | 6.3361 | 5.9156 | 6.0142 | 6.0122 | 6.1771 | 6.5087 | 4.2953 | 6.4681 | 4.1006 | 6.7233 | 8.172 | 42.9523 | 47.1018 | 43.5294 | 15.3948 |  |  | 0.22627 | -0.29299 | 0.057704 | 0.11368 | 0.080988 | 0.3189 | 0.61036 | 0.3987 | -0.86693 | -0.3946 | -0.44361 | 8.8674 | 8.8684 | 2.0085 | 15.8459 | 16.7244 | 17.2758 | 17.6122 | 17.5776 | 16.5772 | 14.934 | 16.8947 | 17.2248 | 17.5111 | 17.5615 | 17.3111 | 16.5314 | 14.7728 | 5.9247 | 8.2038 | 5.2933 | 5.6854 | 5.7871 | 6.6949 | 7.6729 | 15.9045 | 15.5171 | 15.4019 | 14.3389 | 14.2399 | 14.1773 |  |  |  | 10.755 | 9.5612 | 9.0627 | 9.2901 | -0.10307 | -0.22073 | 12.686 |  |  | 10.5767 |  |  | 16.9158 | 16.1198 | 15.0996 | 16.4211 | 15.705 | 14.8174 | 10.3949 | 10.516 | 11.44 | 11.3067 | 8.8757 |  | 10.5941 | 7.3878 | 9.8767 | 9.4856 | 11.0722 | 12.2417 |  | 12.313 |  |  | 11.8375 | 12.507 | 12.4909 | [6 empty] | 12.5757 |  |  | 11.3525 |  |  | 9.0753 | 10.2859 | 11.8608 | 7.5695 | 8.9822 | 12.5517 | 7.7478 | 9.4674 | 12.2502 | 9.1879 | 10.4304 | 7.5646 | 10.3147 | 8.1452 | 10.0651 | 7.852 | 9.6394 | 13.0028 | 10.4 | 10.0923 | 11.4925 | 8.2352 | 9.7566 | 12.5781 | 7.9779 | 10.3363 | 9.6818 | 9.7632 | 8.5416 | 10.154 | -0.043732 | 20.9539 | 0.033527 | 0.050527 | -37.9912 | 3.1207 | -0.6 | 0.36 | 0.55772 | -0.63062 | 0.27987 | 0.39282 | 0.33146 | 0.65773 | 0.90995 | 0.41526 | 0.43296 | 0.41409 | 0.43332 | 0.61702 | 0.43595 | 0.40905
42810.4351 | -430 | 18.591 | 18.6432 | 18.6261 | 18.6486 | 18.004 | 16.6512 | 14.7112 | 16.7395 | 17.229 | 17.3167 | 17.3394 | 16.8914 | 15.9495 | 14.5598 | 15.0347 | 15.0193 | 15.5757 | 13.4284 | 13.5573 | 14.1187 |  |  |  | 16.6347 | 15.9718 | 15.0855 | 10.2389 | 9.5647 | 9.8962 | 17.2939 | 16.4051 | 15.2208 | 16.9349 | 16.223 | 15.235 | 10.8191 | 11.4951 |  | 12.2191 | 10.4224 | 10.2932 | 8.4088 |  | 6.3837 | 6.3468 | 5.9233 | 6.0111 | 6.0125 | 6.1719 | 6.4839 | 4.2934 | 6.4757 | 4.1224 | 6.7332 | 8.1662 | 42.9098 | 47.1171 | 43.5172 | 15.3831 |  |  | 0.24861 | -0.23582 | -0.02772 | -0.078854 | 0.091504 | -0.10823 | 0.52954 | 0.29357 | -1.2388 | -0.13046 | -0.42453 | 8.8695 | 8.8705 | 2.0086 | 15.8543 | 16.7285 | 17.2717 | 17.6069 | 17.578 | 16.5733 | 14.9324 | 16.8861 | 17.2219 | 17.5045 | 17.5553 | 17.3105 | 16.529 | 14.7712 | 5.8849 | 8.1883 | 5.323 | 5.6713 | 5.7536 | 6.6988 | 7.6684 | 15.9276 | 15.5361 | 15.4152 | 14.3454 | 14.2424 | 14.1871 |  |  |  | 10.7625 | 9.5688 | 9.0759 | 9.265 | 0.030439 | -0.059446 | 12.6761 |  |  | 10.5574 |  |  | 16.9063 | 16.1092 | 15.0909 | 16.4148 | 15.6989 | 14.8089 | 10.3404 | 10.5086 | 11.4345 | 11.3085 | 8.8897 |  | 10.6027 | 7.4706 | 9.883 | 9.4963 | 11.0692 | 12.297 |  | 12.3198 |  |  | 11.7361 | 12.4696 | 12.4699 | [6 empty] | 12.5885 |  |  | 11.3439 |  |  | 9.0748 | 10.2984 | 11.8645 | 7.594 | 8.9928 | 12.5634 | 7.7467 | 9.4744 | 12.2526 | 9.1866 | 10.4395 | 7.5724 | 10.3165 | 8.1471 | 10.0636 | 7.8502 | 9.6359 | 13.0034 | 10.397 | 10.0883 | 11.4837 | 8.216 | 9.7518 | 12.5635 | 7.9666 | 10.3294 | 9.6712 | 9.7513 | 8.5234 | 10.1353 | 0.041397 | 20.9527 | 0.031645 | 0.047856 | -37.9585 | 3.1208 | -0.21 | 0.34 | 0.58459 | -0.56577 | -0.19398 | -0.32717 | 0.35232 | -0.38317 | 0.84755 | 0.41516 | 0.43087 | 0.41369 | 0.43819 | 0.61321 | 0.43565 | 0.41
42810.4351 | -429 | 18.5948 | 18.6421 | 18.6302 | 18.6454 | 18.0057 | 16.6499 | 14.7164 | 16.7395 | 17.2262 | 17.3179 | 17.3424 | 16.8879 | 15.9451 | 14.5666 | 15.0392 | 15.0246 | 15.5713 | 13.4377 | 13.5541 | 14.1232 |  |  |  | 16.6397 | 15.9817 | 15.093 | 10.2446 | 9.5617 | 9.8681 | 17.2872 | 16.4054 | 15.2203 | 16.932 | 16.2211 | 15.2311 | 10.824 | 11.4785 |  | 12.2185 | 10.4119 | 10.2936 | 8.3833 |  | 6.3828 | 6.338 | 5.9096 | 5.9939 | 6.0048 | 6.1612 | 6.478 | 4.2209 | 6.4618 | 4.1191 | 6.721 | 8.1664 | 42.8769 | 47.1266 | 43.5128 | 15.3779 |  |  | 0.19604 | -0.085337 | 0.080704 | -0.19582 | 0.052732 | 0.27356 | 0.55122 | 0.07606 | -0.25024 | -1.2376 | -0.36293 | 8.8695 | 8.8708 | 2.0087 | 15.8616 | 16.7239 | 17.2685 | 17.6084 | 17.583 | 16.5697 | 14.9371 | 16.8796 | 17.2171 | 17.5072 | 17.5607 | 17.3112 | 16.5261 | 14.7718 | 5.8943 | 8.1721 | 5.316 | 5.5911 | 5.7975 | 6.6944 | 7.6614 | 15.931 | 15.5416 | 15.4146 | 14.3516 | 14.2499 | 14.1861 |  |  |  | 10.7724 | 9.5597 | 9.0755 | 9.2266 | 0.090611 | -0.012396 | 12.6845 |  |  | 10.5532 |  |  | 16.9109 | 16.1099 | 15.093 | 16.4125 | 15.7019 | 14.8122 | 10.3095 | 10.511 | 11.4461 | 11.3226 | 8.8495 |  | 10.5977 | 7.5218 | 9.8773 | 9.4897 | 11.0708 | 12.325 |  | 12.3209 |  |  | 11.7187 | 12.4623 | 12.4353 | [6 empty] | 12.5952 |  |  | 11.3504 |  |  | 9.0746 | 10.308 | 11.8682 | 7.5974 | 9.0021 | 12.5776 | 7.7545 | 9.4682 | 12.2504 | 9.1944 | 10.4401 | 7.5692 | 10.3255 | 8.1431 | 10.069 | 7.8741 | 9.6534 | 13.0309 | 10.4048 | 10.1013 | 11.5047 | 8.229 | 9.7599 | 12.5709 | 7.991 | 10.3345 | 9.687 | 9.7597 | 8.5355 | 10.1477 | 0.086465 | 20.9537 | 0.032207 | 0.047885 | -38.0053 | 3.1208 | -0.17 | 0.26 | 0.51909 | -0.34034 | 0.33098 | -0.51556 | 0.26745 | 0.60916 | 0.86472 | 0.41611 | 0.42926 | 0.41392 | 0.43665 | 0.61317 | 0.43652 | 0.41139
42810.4351 | -428 | 18.5901 | 18.6442 | 18.6327 | 18.6475 | 18.0042 | 16.6567 | 14.7178 | 16.7421 | 17.2239 | 17.3253 | 17.3432 | 16.8921 | 15.9379 | 14.5662 | 15.0457 | 15.0285 | 15.5783 | 13.4427 | 13.5506 | 14.123 |  |  |  | 16.6403 | 15.9858 | 15.0927 | 10.2392 | 9.5611 | 9.847 | 17.29 | 16.402 | 15.2212 | 16.9353 | 16.2145 | 15.2283 | 10.8177 | 11.462 |  | 12.2211 | 10.4084 | 10.2904 | 8.3827 |  | 6.3799 | 6.3452 | 5.9072 | 5.9888 | 5.9836 | 6.1633 | 6.4939 | 4.1755 | 6.4661 | 4.0916 | 6.7266 | 8.168 | 42.8571 | 47.1301 | 43.5104 | 15.3696 |  |  | -0.031321 | 0.22548 | 0.14116 | 0.019714 | 0.13553 | -0.36384 | 0.50982 | 0.1582 | -0.27398 | -0.82364 | -0.27074 | 8.8676 | 8.8689 | 2.0083 | 15.8524 | 16.7202 | 17.2662 | 17.5954 | 17.5704 | 16.5715 | 14.9282 | 16.8776 | 17.2142 | 17.5082 | 17.5572 | 17.3111 | 16.5297 | 14.7673 | 5.8968 | 8.2053 | 5.2226 | 5.5881 | 5.7872 | 6.6875 | 7.6544 | 15.9283 | 15.5414 | 15.4187 | 14.3482 | 14.2552 | 14.1902 |  |  |  | 10.7767 | 9.5601 | 9.0872 | 9.2024 | -0.053032 | -0.0018572 | 12.6828 |  |  | 10.5535 |  |  | 16.907 | 16.1088 | 15.0931 | 16.4081 | 15.7014 | 14.8104 | 10.2732 | 10.51 | 11.4547 | 11.3265 | 8.7976 |  | 10.6019 | 7.5734 | 9.8787 | 9.5081 | 11.0683 | 12.3509 |  | 12.3217 |  |  | 11.7307 | 12.4189 | 12.4177 | [6 empty] | 12.5955 |  |  | 11.36 |  |  | 9.0884 | 10.3194 | 11.8695 | 7.6179 | 9.0098 | 12.5813 | 7.7648 | 9.4694 | 12.2555 | 9.1837 | 10.4428 | 7.5651 | 10.3398 | 8.1427 | 10.0669 | 7.8854 | 9.6522 | 13.035 | 10.4049 | 10.108 | 11.5024 | 8.2333 | 9.765 | 12.5619 | 7.9995 | 10.3359 | 9.6835 | 9.7494 | 8.533 | 10.144 | -0.047584 | 20.9538 | 0.03324 | 0.048153 | -38.0431 | 3.1208 | -0.01 | 0.4 | -0.20748 | 0.55323 | 0.43773 | 0.16358 | 0.42878 | -0.70254 | 0.83162 | 0.41769 | 0.42787 | 0.41333 | 0.43555 | 0.62273 | 0.43633 | 0.41221
42810.4351 | -427 | 18.5938 | 18.6461 | 18.6338 | 18.6477 | 18.0063 | 16.6606 | 14.7229 | 16.7416 | 17.2264 | 17.329 | 17.3424 | 16.894 | 15.9432 | 14.5662 | 15.0424 | 15.0357 | 15.5835 | 13.4524 | 13.5653 | 14.1248 |  |  |  | 16.6447 | 15.9805 | 15.0973 | 10.2472 | 9.5564 | 9.8731 | 17.2915 | 16.3989 | 15.219 | 16.9322 | 16.2164 | 15.2258 | 10.8199 | 11.4572 |  | 12.2133 | 10.4056 | 10.29 | 8.4162 |  | 6.3756 | 6.3434 | 5.9134 | 5.9782 | 5.9761 | 6.153 | 6.4905 | 4.2109 | 6.4718 | 4.0772 | 6.7309 | 8.1659 | 42.8123 | 47.1391 | 43.5 | 15.3597 |  |  | 0.17435 | 0.082227 | 0.078732 | 0.038114 | 0.018564 | -0.22716 | 0.23449 | 0.070804 | -0.56822 | -0.40152 | -0.32836 | 8.8676 | 8.8687 | 2.0083 | 15.8677 | 16.731 | 17.2754 | 17.6051 | 17.5786 | 16.5696 | 14.9346 | 16.8956 | 17.2311 | 17.5107 | 17.5649 | 17.3137 | 16.5325 | 14.7717 | 5.9052 | 8.2054 | 5.139 | 5.5581 | 5.7397 | 6.6908 | 7.6659 | 15.9246 | 15.5373 | 15.4224 | 14.3533 | 14.2515 | 14.1933 |  |  |  | 10.7672 | 9.5601 | 9.0895 | 9.1916 | -0.041687 | -0.0235 | 12.6733 |  |  | 10.5529 |  |  | 16.9077 | 16.1124 | 15.0953 | 16.4087 | 15.6938 | 14.8121 | 10.2363 | 10.4948 | 11.4548 | 11.3266 | 8.7641 |  | 10.5913 | 7.6417 | 9.8576 | 9.5055 | 11.0615 | 12.333 |  | 12.3193 |  |  | 11.7314 | 12.4141 | 12.4334 | [6 empty] | 12.6073 |  |  | 11.3661 |  |  | 9.0995 | 10.3276 | 11.8855 | 7.6308 | 9.0175 | 12.5873 | 7.764 | 9.472 | 12.2641 | 9.1941 | 10.4613 | 7.5747 | 10.3445 | 8.151 | 10.0694 | 7.9024 | 9.6625 | 13.05 | 10.4079 | 10.1247 | 11.5125 | 8.2446 | 9.7676 | 12.5752 | 8.0099 | 10.3295 | 9.683 | 9.7528 | 8.5376 | 10.144 | -0.046236 | 20.9552 | 0.033487 | 0.048544 | -38.0673 | 3.1207 | -0.05 | 0.32 | 0.48955 | 0.33409 | 0.32691 | 0.22745 | 0.15869 | -0.5551 | 0.56399 | 0.41827 | 0.42528 | 0.41318 | 0.43501 | 0.63335 | 0.43547 | 0.41219
42810.4351 | -426 | 18.5997 | 18.6462 | 18.6278 | 18.6489 | 18.0073 | 16.6541 | 14.7212 | 16.742 | 17.2236 | 17.3236 | 17.3363 | 16.8978 | 15.9444 | 14.5669 | 15.0421 | 15.0208 | 15.5719 | 13.442 | 13.5538 | 14.1184 |  |  |  | 16.6395 | 15.9779 | 15.0901 | 10.2394 | 9.5554 | 9.8806 | 17.299 | 16.408 | 15.222 | 16.9422 | 16.2202 | 15.2389 | 10.8284 | 11.4384 |  | 12.2174 | 10.4163 | 10.3042 | 8.4618 |  | 6.378 | 6.3356 | 5.9127 | 5.9873 | 5.9679 | 6.1608 | 6.4738 | 4.1807 | 6.4733 | 4.073 | 6.7289 | 8.1773 | 42.7875 | 47.1348 | 43.4963 | 15.3519 |  |  | 0.038987 | -0.059053 | 0.050476 | 0.16165 | 0.17758 | -0.60369 | 0.15761 | 0.073432 | 0.19773 | -0.59915 | -0.28961 | 8.8685 | 8.8697 | 2.0088 | 15.8638 | 16.7273 | 17.2668 | 17.6027 | 17.5684 | 16.5679 | 14.924 | 16.8883 | 17.2169 | 17.5101 | 17.5592 | 17.3062 | 16.5255 | 14.7693 | 5.9078 | 8.1774 | 5.0865 | 5.4763 | 5.677 | 6.6875 | 7.665 | 15.9253 | 15.5369 | 15.42 | 14.3516 | 14.2509 | 14.1888 |  |  |  | 10.7662 | 9.5559 | 9.0918 | 9.1704 | -0.064378 | 0.092996 | 12.6715 |  |  | 10.5539 |  |  | 16.9104 | 16.1129 | 15.0917 | 16.4133 | 15.6936 | 14.8112 | 10.2415 | 10.4912 | 11.4603 | 11.3304 | 8.7556 |  | 10.5961 | 7.7005 | 9.8667 | 9.507 | 11.0687 | 12.3302 |  | 12.3231 |  |  | 11.6871 | 12.4262 | 12.4302 | [6 empty] | 12.6025 |  |  | 11.3653 |  |  | 9.0969 | 10.327 | 11.8952 | 7.6416 | 9.0271 | 12.5891 | 7.7629 | 9.4705 | 12.2603 | 9.1929 | 10.4597 | 7.5802 | 10.3445 | 8.145 | 10.0549 | 7.9161 | 9.6632 | 13.046 | 10.414 | 10.1255 | 11.5031 | 8.2485 | 9.7711 | 12.5732 | 8.0153 | 10.3191 | 9.6927 | 9.7486 | 8.5447 | 10.1422 | 0.089739 | 20.9552 | 0.033958 | 0.048826 | -38.0859 | 3.1207 | -0.28 | 0.43 | 0.2315 | -0.28312 | 0.26175 | 0.46842 | 0.49081 | -0.90494 | 0.46238 | 0.41866 | 0.42395 | 0.41337 | 0.43434 | 0.63908 | 0.43448 | 0.41275
42810.4351 | -425 | 18.6017 | 18.6441 | 18.6272 | 18.6482 | 18.0027 | 16.6507 | 14.7189 | 16.7384 | 17.219 | 17.3159 | 17.3353 | 16.8905 | 15.9445 | 14.5656 | 15.0485 | 15.0278 | 15.5765 | 13.4435 | 13.5554 | 14.1212 |  |  |  | 16.6408 | 15.979 | 15.092 | 10.2411 | 9.5577 | 9.8873 | 17.2882 | 16.402 | 15.2138 | 16.9354 | 16.2149 | 15.2261 | 10.8169 | 11.3915 |  | 12.2059 | 10.4089 | 10.2896 | 8.4862 |  | 6.3741 | 6.3352 | 5.9123 | 5.9776 | 5.9651 | 6.149 | 6.457 | 4.1628 | 6.4715 | 4.0639 | 6.7293 | 8.1746 | 42.7602 | 47.1223 | 43.5034 | 15.3493 |  |  | -0.028693 | 0.17094 | 0.053764 | 0.11697 | 0.11713 | -0.0228 | 0.19506 | 0.16674 | 0.17029 | -0.049056 | -0.29359 | 8.8719 | 8.873 | 2.0084 | 15.8629 | 16.7231 | 17.2656 | 17.6056 | 17.5752 | 16.566 | 14.9263 | 16.8917 | 17.2181 | 17.5192 | 17.5614 | 17.308 | 16.5313 | 14.7657 | 5.9039 | 8.1842 | 5.0419 | 5.3625 | 5.5364 | 6.6835 | 7.6506 | 15.9445 | 15.5488 | 15.425 | 14.3574 | 14.2551 | 14.1867 |  |  |  | 10.7751 | 9.5502 | 9.0934 | 9.1634 | 0.076632 | 0.021103 | 12.6704 |  |  | 10.5604 |  |  | 16.9109 | 16.1137 | 15.0944 | 16.4151 | 15.6992 | 14.8091 | 10.2735 | 10.4947 | 11.4711 | 11.3215 | 8.6582 |  | 10.5948 | 7.7846 | 9.8684 | 9.4854 | 11.0672 | 12.3016 |  | 12.3187 |  |  | 11.6898 | 12.4234 | 12.4203 | [6 empty] | 12.6033 |  |  | 11.3711 |  |  | 9.0965 | 10.3349 | 11.9072 | 7.6553 | 9.0366 | 12.5951 | 7.7722 | 9.4792 | 12.2631 | 9.1997 | 10.4625 | 7.5836 | 10.3325 | 8.1381 | 10.0559 | 7.9341 | 9.6709 | 13.0423 | 10.4138 | 10.1329 | 11.5136 | 8.249 | 9.7767 | 12.5781 | 8.0297 | 10.3161 | 9.6974 | 9.7451 | 8.5473 | 10.1461 | -0.055096 | 20.9559 | 0.034646 | 0.049333 | -37.9718 | 3.1208 | -13.55 | 0.38 | -0.1986 | 0.48169 | 0.27014 | 0.39845 | 0.3986 | -0.17586 | 0.51439 | 0.42133 | 0.42166 | 0.41392 | 0.4343 | 0.64237 | 0.43343 | 0.41324
42810.4351 | -424 | 18.6023 | 18.6446 | 18.6336 | 18.6525 | 18.0108 | 16.6646 | 14.72 | 16.7484 | 17.2237 | 17.3303 | 17.3441 | 16.8984 | 15.9515 | 14.5726 | 15.0505 | 15.0296 | 15.5757 | 13.4437 | 13.5564 | 14.1221 |  |  |  | 16.6406 | 15.9744 | 15.0969 | 10.2461 | 9.5542 | 9.8858 | 17.2962 | 16.4183 | 15.2171 | 16.9384 | 16.2249 | 15.2292 | 10.8242 | 11.4087 |  | 12.2121 | 10.3761 | 10.2976 | 8.5129 |  | 6.3604 | 6.3327 | 5.9047 | 5.9687 | 5.9552 | 6.1339 | 6.4298 | 4.1494 | 6.4606 | 4.0997 | 6.7228 | 8.1754 | 42.7339 | 47.1127 | 43.4915 | 15.3204 |  |  | 0.090903 | 0.049371 | 0.27981 | 0.17677 | 0.082304 | -0.37173 | 0.2542 | 0.14046 | -0.85545 | -1.4795 | -0.33353 | 8.8681 | 8.8689 | 2.0084 | 15.8687 | 16.7204 | 17.2716 | 17.6048 | 17.5778 | 16.5694 | 14.9266 | 16.8915 | 17.2204 | 17.5142 | 17.5641 | 17.3087 | 16.5308 | 14.7705 | 5.9487 | 8.2087 | 5.0697 | 5.3142 | 5.4252 | 6.6825 | 7.6561 | 15.9415 | 15.545 | 15.4278 | 14.363 | 14.2548 | 14.1933 |  |  |  | 10.7758 | 9.5511 | 9.0927 | 9.1425 | -0.19323 | 0.1041 | 12.6754 |  |  | 10.5637 |  |  | 16.9095 | 16.1179 | 15.0933 | 16.4147 | 15.7032 | 14.8137 | 10.3059 | 10.4902 | 11.475 | 11.3175 | 8.5408 |  | 10.5917 | 7.8755 | 9.8655 | 9.4789 | 11.0659 | 12.3055 |  | 12.3072 |  |  | 11.7 | 12.4074 | 12.3965 | [6 empty] | 12.6062 |  |  | 11.3763 |  |  | 9.1044 | 10.3384 | 11.9201 | 7.6762 | 9.0498 | 12.602 | 7.7739 | 9.4845 | 12.2604 | 9.2047 | 10.4708 | 7.6023 | 10.3217 | 8.1455 | 10.059 | 7.9431 | 9.6796 | 13.0352 | 10.4159 | 10.1424 | 11.5193 | 8.2489 | 9.7824 | 12.5799 | 8.0351 | 10.3053 | 9.7044 | 9.7472 | 8.5491 | 10.1475 | -0.033525 | 20.9517 | 0.03448 | 0.050121 | -38.0045 | 3.1207 | -9.89 | 0.3 | 0.35349 | 0.25887 | 0.61628 | 0.48983 | 0.33412 | -0.71008 | 0.58719 | 0.42448 | 0.41905 | 0.41406 | 0.42921 | 0.63992 | 0.43292 | 0.41384
42810.4351 | -423 | 18.5988 | 18.6462 | 18.6182 | 18.6439 | 17.999 | 16.6527 | 14.7164 | 16.734 | 17.2235 | 17.319 | 17.337 | 16.8905 | 15.9411 | 14.5669 | 15.05 | 15.0221 | 15.5728 | 13.4328 | 13.5513 | 14.1186 |  |  |  | 16.6382 | 15.9811 | 15.0933 | 10.2373 | 9.554 | 9.8912 | 17.2961 | 16.407 | 15.2203 | 16.9428 | 16.2221 | 15.2355 | 10.8327 | 11.3863 |  | 12.2187 | 10.2932 | 10.3088 | 8.5556 |  | 6.357 | 6.3169 | 5.8946 | 5.9614 | 5.9424 | 6.1186 | 6.3971 | 4.1607 | 6.4614 | 4.143 | 6.7265 | 8.1826 | 42.7326 | 47.1155 | 43.4944 | 15.3172 |  |  | 0.086959 | 0.23665 | 0.15562 | -0.46787 | -0.047148 | 0.09548 | 0.39877 | 0.3895 | -0.60869 | -1.2453 | -0.50043 | 8.8689 | 8.8705 | 2.0084 | 15.8722 | 16.7285 | 17.2813 | 17.6041 | 17.5778 | 16.5756 | 14.9284 | 16.8926 | 17.2278 | 17.5122 | 17.5636 | 17.3119 | 16.5347 | 14.7732 | 5.9303 | 8.1804 | 5.1494 | 5.3322 | 5.3568 | 6.6783 | 7.6624 | 15.942 | 15.5528 | 15.422 | 14.3619 | 14.2515 | 14.1938 |  |  |  | 10.7713 | 9.5475 | 9.095 | 9.1363 | -0.12637 | 0.036536 | 12.6735 |  |  | 10.5688 |  |  | 16.9123 | 16.1124 | 15.0938 | 16.4198 | 15.7072 | 14.8177 | 10.3447 | 10.4869 | 11.4748 | 11.3186 | 8.4802 |  | 10.5985 | 7.9698 | 9.867 | 9.4628 | 11.0673 | 12.2921 |  | 12.3147 |  |  | 11.7085 | 12.4019 | 12.3635 | [6 empty] | 12.5955 |  |  | 11.3755 |  |  | 9.1179 | 10.3437 | 11.9362 | 7.6951 | 9.0612 | 12.6095 | 7.7767 | 9.4913 | 12.2614 | 9.2036 | 10.4771 | 7.6144 | 10.3153 | 8.1497 | 10.0639 | 7.9502 | 9.657 | 13.0264 | 10.4178 | 10.1487 | 11.52 | 8.2489 | 9.7846 | 12.5831 | 8.0211 | 10.2702 | 9.7004 | 9.7521 | 8.5509 | 10.1473 | -0.15236 | 20.9571 | 0.033849 | 0.049405 | -38.0542 | 3.1207 | 0.07 | 0.29 | 0.34574 | 0.56674 | 0.45958 | -0.79688 | -0.25288 | 0.35986 | 0.73543 | 0.42639 | 0.41648 | 0.41456 | 0.43077 | 0.63179 | 0.43202 | 0.41386
42810.4352 | -422 | 18.6044 | 18.641 | 18.6178 | 18.6385 | 18.0043 | 16.6517 | 14.7077 | 16.7442 | 17.2229 | 17.3152 | 17.3326 | 16.889 | 15.9469 | 14.5729 | 15.0546 | 15.0229 | 15.5741 | 13.4333 | 13.5481 | 14.1157 |  |  |  | 16.6396 | 15.9859 | 15.0889 | 10.232 | 9.5513 | 9.8876 | 17.3015 | 16.4178 | 15.2215 | 16.9463 | 16.2235 | 15.2371 | 10.8311 | 11.3411 |  | 12.2139 | 10.2362 | 10.3191 | 8.5903 |  | 6.3589 | 6.3013 | 5.879 | 5.951 | 5.9311 | 6.1086 | 6.3907 | 4.1432 | 6.4582 | 4.1759 | 6.7192 | 8.1729 | 42.7372 | 47.1019 | 43.5085 | 15.2997 |  |  | 0.11456 | 0.007975 | 0.033392 | -0.42515 | 0.044848 | 0.32941 | 0.51705 | 0.30934 | -0.26561 | -0.51334 | -0.40228 | 8.8684 | 8.8696 | 2.0085 | 15.8774 | 16.7368 | 17.279 | 17.6087 | 17.5824 | 16.5725 | 14.9328 | 16.8948 | 17.2304 | 17.5201 | 17.5616 | 17.3093 | 16.532 | 14.7731 | 5.8994 | 8.1767 | 5.1789 | 5.3951 | 5.3532 | 6.6757 | 7.6582 | 15.9362 | 15.5413 | 15.4164 | 14.3463 | 14.2468 | 14.1888 |  |  |  | 10.7658 | 9.5306 | 9.0824 | 9.1443 | 0.0118 | -0.050225 | 12.6639 |  |  | 10.569 |  |  | 16.9051 | 16.1064 | 15.0919 | 16.4151 | 15.702 | 14.8156 | 10.3761 | 10.4807 | 11.4675 | 11.3073 | 8.5459 |  | 10.5985 | 8.0919 | 9.877 | 9.4622 | 11.0628 | 12.2532 |  | 12.3214 |  |  | 11.7096 | 12.3974 | 12.337 | [6 empty] | 12.5904 |  |  | 11.3785 |  |  | 9.1188 | 10.3483 | 11.9494 | 7.7103 | 9.0694 | 12.6092 | 7.7839 | 9.4929 | 12.2666 | 9.2086 | 10.4844 | 7.6356 | 10.3118 | 8.1527 | 10.0701 | 7.9603 | 9.5974 | 13.0183 | 10.4213 | 10.1581 | 11.5194 | 8.2456 | 9.7875 | 12.5933 | 8.0163 | 10.2224 | 9.7096 | 9.7523 | 8.5497 | 10.1496 | -0.11808 | 20.9544 | 0.032902 | 0.047502 | -38.1013 | 3.1207 | 4.03 | 0.27 | 0.39683 | 0.10404 | 0.21288 | -0.75961 | 0.24663 | 0.66841 | 0.83741 | 0.42457 | 0.41341 | 0.41442 | 0.4339 | 0.62803 | 0.431 | 0.41346
42810.4352 | -421 | 18.6111 | 18.6496 | 18.6278 | 18.6512 | 18.0128 | 16.6598 | 14.7119 | 16.7494 | 17.2309 | 17.3254 | 17.3408 | 16.8944 | 15.9505 | 14.5746 | 15.0523 | 15.0264 | 15.5786 | 13.44 | 13.5511 | 14.1185 |  |  |  | 16.6463 | 15.9823 | 15.0895 | 10.2346 | 9.554 | 9.8868 | 17.2952 | 16.4203 | 15.2208 | 16.9338 | 16.223 | 15.2335 | 10.8251 | 11.2973 |  | 12.2156 | 10.1677 | 10.3139 | 8.6125 |  | 6.3504 | 6.3031 | 5.8771 | 5.9465 | 5.9255 | 6.0816 | 6.366 | 4.1348 | 6.4506 | 4.1617 | 6.7241 | 8.1752 | 42.7401 | 47.08 | 43.5169 | 15.2956 |  |  | 0.11784 | 0.038199 | 0.07676 | -0.11105 | 0.066532 | 0.3925 | 0.59853 | 0.19303 | -1.4297 | -0.50369 | -0.5064 | 8.8679 | 8.8691 | 2.0085 | 15.8772 | 16.7286 | 17.2746 | 17.6046 | 17.5796 | 16.5729 | 14.934 | 16.8893 | 17.2271 | 17.5204 | 17.5601 | 17.3032 | 16.5302 | 14.7681 | 5.8949 | 8.1955 | 5.1837 | 5.4082 | 5.3743 | 6.6766 | 7.6621 | 15.9449 | 15.542 | 15.4186 | 14.3457 | 14.2529 | 14.1867 |  |  |  | 10.7689 | 9.5265 | 9.0824 | 9.1873 | -0.031557 | 0.031642 | 12.6644 |  |  | 10.5663 |  |  | 16.9073 | 16.1082 | 15.0976 | 16.4158 | 15.702 | 14.8113 | 10.3879 | 10.4741 | 11.4704 | 11.2996 | 8.642 |  | 10.5841 | 8.2179 | 9.8557 | 9.462 | 11.0595 | 12.1973 |  | 12.3257 |  |  | 11.7064 | 12.3687 | 12.3401 | [6 empty] | 12.5956 |  |  | 11.384 |  |  | 9.1243 | 10.3557 | 11.9512 | 7.7244 | 9.0319 | 12.5991 | 7.8015 | 9.5081 | 12.2751 | 9.2288 | 10.4921 | 7.6412 | 10.3194 | 8.1525 | 10.0841 | 7.9757 | 9.5365 | 13.0054 | 10.426 | 10.1628 | 11.5168 | 8.242 | 9.7818 | 12.5992 | 8.0052 | 10.1739 | 9.7109 | 9.7595 | 8.5522 | 10.1491 | -0.045658 | 20.9555 | 0.032523 | 0.049079 | -38.0737 | 3.1207 | -8.97 | 0.28 | 0.40248 | 0.22769 | 0.32277 | -0.38823 | 0.30038 | 0.72957 | 0.90093 | 0.42142 | 0.40921 | 0.41432 | 0.43451 | 0.62795 | 0.43019 | 0.41237
42810.4352 | -420 | 18.6068 | 18.6406 | 18.6262 | 18.6489 | 18.0027 | 16.6507 | 14.709 | 16.7395 | 17.2244 | 17.3239 | 17.3355 | 16.8966 | 15.9464 | 14.5708 | 15.0467 | 15.0278 | 15.5741 | 13.4387 | 13.5513 | 14.1219 |  |  |  | 16.6433 | 15.9837 | 15.0947 | 10.2388 | 9.5549 | 9.8688 | 17.2994 | 16.4171 | 15.2209 | 16.9416 | 16.2267 | 15.2375 | 10.8257 | 11.2533 |  | 12.2105 | 10.1212 | 10.3125 | 8.6202 |  | 6.3296 | 6.2887 | 5.8633 | 5.9321 | 5.9208 | 6.0543 | 6.3592 | 4.1404 | 6.4364 | 4.1024 | 6.7183 | 8.1777 | 42.7473 | 47.0578 | 43.5259 | 15.2891 |  |  | 0.040303 | -0.13397 | -0.10197 | -0.15705 | -0.08592 | 0.12242 | 0.4658 | 0.23903 | 0.80293 | -0.27501 | -0.2157 | 8.8693 | 8.8703 | 2.0084 | 15.8718 | 16.7371 | 17.2769 | 17.605 | 17.5766 | 16.5719 | 14.9411 | 16.8925 | 17.2246 | 17.5232 | 17.5694 | 17.3156 | 16.5286 | 14.775 | 5.8868 | 8.1914 | 5.1945 | 5.421 | 5.4051 | 6.6781 | 7.6753 | 15.9544 | 15.5474 | 15.421 | 14.3491 | 14.2562 | 14.1956 |  |  |  | 10.772 | 9.5296 | 9.0819 | 9.2138 | -0.094363 | 0.034089 | 12.664 |  |  | 10.5667 |  |  | 16.9092 | 16.106 | 15.0962 | 16.4105 | 15.7021 | 14.8046 | 10.3902 | 10.4664 | 11.4683 | 11.2878 | 8.7859 |  | 10.5881 | 8.3183 | 9.8542 | 9.4458 | 11.0607 | 12.1821 |  | 12.3138 |  |  | 11.709 | 12.3419 | 12.3415 | [6 empty] | 12.5751 |  |  | 11.371 |  |  | 9.1166 | 10.3594 | 11.9458 | 7.7358 | 8.9487 | 12.5748 | 7.809 | 9.5205 | 12.2839 | 9.2305 | 10.4938 | 7.6053 | 10.3069 | 8.1466 | 10.0989 | 7.9882 | 9.5244 | 12.995 | 10.4278 | 10.1688 | 11.5119 | 8.2426 | 9.7809 | 12.6044 | 7.9895 | 10.1418 | 9.7075 | 9.7758 | 8.5489 | 10.164 | 0.029263 | 20.9545 | 0.033797 | 0.049803 | -38.0582 | 3.1207 | -10.49 | 0.32 | 0.23537 | -0.42639 | -0.37201 | -0.46167 | -0.34133 | 0.40743 | 0.79474 | 0.41756 | 0.40637 | 0.41481 | 0.43558 | 0.62828 | 0.42999 | 0.41173
42810.4352 | -419 | 18.6123 | 18.6491 | 18.6318 | 18.6521 | 18.0014 | 16.6481 | 14.718 | 16.7414 | 17.2293 | 17.3255 | 17.344 | 16.903 | 15.9505 | 14.575 | 15.0582 | 15.0382 | 15.5797 | 13.4389 | 13.5542 | 14.1262 |  |  |  | 16.6518 | 15.9879 | 15.0997 | 10.2365 | 9.5654 | 9.8526 | 17.2944 | 16.4125 | 15.214 | 16.939 | 16.2196 | 15.2307 | 10.8176 | 11.2221 |  | 12.2032 | 10.0756 | 10.2941 | 8.6172 |  | 6.3361 | 6.2929 | 5.8656 | 5.9331 | 5.9174 | 6.0463 | 6.3661 | 4.1484 | 6.45 | 4.0523 | 6.7238 | 8.1879 | 42.7438 | 47.0432 | 43.5638 | 15.3049 |  |  | 0.014675 | -0.024225 | 0.028792 | 0.009198 | 0.02382 | 0.10665 | 0.09584 | 0.098404 | -0.65793 | -0.66398 | -0.27213 | 8.871 | 8.8721 | 2.0082 | 15.8768 | 16.7384 | 17.2801 | 17.6091 | 17.5815 | 16.5771 | 14.9316 | 16.8919 | 17.2284 | 17.5181 | 17.5648 | 17.3175 | 16.5333 | 14.7744 | 5.8689 | 8.174 | 5.1826 | 5.4175 | 5.4407 | 6.6707 | 7.6694 | 15.9522 | 15.5486 | 15.4268 | 14.364 | 14.2551 | 14.2023 |  |  |  | 10.7656 | 9.5159 | 9.0684 | 9.236 | -0.18655 | -0.04966 | 12.6701 |  |  | 10.5761 |  |  | 16.9097 | 16.107 | 15.0927 | 16.412 | 15.6991 | 14.8132 | 10.3936 | 10.4736 | 11.4613 | 11.2759 | 8.9174 |  | 10.589 | 8.3541 | 9.8602 | 9.4297 | 11.0675 | 12.1887 |  | 12.3145 |  |  | 11.7037 | 12.3307 | 12.3553 | [6 empty] | 12.5526 |  |  | 11.3605 |  |  | 9.1052 | 10.354 | 11.9391 | 7.7377 | 8.8823 | 12.5385 | 7.8057 | 9.5101 | 12.263 | 9.2163 | 10.4809 | 7.5422 | 10.2674 | 8.1343 | 10.0872 | 7.993 | 9.5091 | 12.9929 | 10.4249 | 10.1841 | 11.51 | 8.2476 | 9.7916 | 12.617 | 7.9792 | 10.1275 | 9.7119 | 9.7905 | 8.5497 | 10.1653 | -0.077437 | 20.955 | 0.034256 | 0.050643 | -38.0569 | 3.1207 | -12.34 | 0.32 | 0.14202 | -0.18132 | 0.19767 | 0.11173 | 0.17972 | 0.38028 | 0.36049 | 0.41394 | 0.40558 | 0.41548 | 0.43671 | 0.62892 | 0.42981 | 0.41091
42810.4352 | -418 | 18.6121 | 18.6502 | 18.6351 | 18.6571 | 18.0069 | 16.6571 | 14.7263 | 16.7462 | 17.2279 | 17.3291 | 17.343 | 16.905 | 15.9526 | 14.5706 | 15.0518 | 15.0224 | 15.5776 | 13.43 | 13.5461 | 14.1159 |  |  |  | 16.6407 | 15.9677 | 15.0914 | 10.225 | 9.5561 | 9.8574 | 17.2984 | 16.408 | 15.2219 | 16.9338 | 16.2168 | 15.2263 | 10.8209 | 11.2118 |  | 12.2069 | 10.0441 | 10.2904 | 8.6218 |  | 6.3328 | 6.2914 | 5.8497 | 5.9162 | 5.9116 | 6.0507 | 6.3722 | 4.114 | 6.4452 | 4.0198 | 6.7216 | 8.1829 | 42.7353 | 47.0333 | 43.5878 | 15.3125 |  |  | -0.000437 | -0.31073 | 0.028792 | -0.18531 | 0.21767 | -0.30536 | 0.13461 | 0.12797 | -0.54253 | -0.69923 | -0.59601 | 8.8695 | 8.8705 | 2.0087 | 15.8851 | 16.7389 | 17.2818 | 17.605 | 17.581 | 16.5728 | 14.9302 | 16.8905 | 17.2254 | 17.5201 | 17.5618 | 17.3127 | 16.5342 | 14.7721 | 5.7834 | 8.1638 | 5.1748 | 5.4356 | 5.5095 | 6.6699 | 7.6736 | 15.9607 | 15.5487 | 15.4302 | 14.3645 | 14.256 | 14.2016 |  |  |  | 10.7755 | 9.519 | 9.0832 | 9.2253 | -0.26657 | -0.20963 | 12.6703 |  |  | 10.5741 |  |  | 16.9049 | 16.1059 | 15.0908 | 16.4103 | 15.696 | 14.8103 | 10.4021 | 10.474 | 11.4577 | 11.255 | 9.0472 |  | 10.586 | 8.313 | 9.8594 | 9.4171 | 11.0653 | 12.2324 |  | 12.3199 |  |  | 11.732 | 12.3346 | 12.3685 | [6 empty] | 12.5302 |  |  | 11.358 |  |  | 9.1088 | 10.3649 | 11.9361 | 7.7436 | 8.8471 | 12.5319 | 7.8175 | 9.5126 | 12.2627 | 9.2218 | 10.4918 | 7.5377 | 10.2555 | 8.1373 | 10.091 | 7.9927 | 9.4863 | 12.9913 | 10.4357 | 10.1921 | 11.5133 | 8.2555 | 9.7872 | 12.6034 | 7.9804 | 10.1205 | 9.709 | 9.7941 | 8.5565 | 10.1739 | -0.078593 | 20.9534 | 0.034004 | 0.050317 | -38.0236 | 3.1206 | 2.77 | 0.4 | -0.024508 | -0.64939 | 0.19767 | -0.50148 | 0.54328 | -0.64347 | 0.42723 | 0.41023 | 0.40669 | 0.41576 | 0.44611 | 0.63027 | 0.42979 | 0.41153
42810.4352 | -417 | 18.615 | 18.6504 | 18.6319 | 18.6487 | 18.004 | 16.655 | 14.7203 | 16.7399 | 17.2295 | 17.3322 | 17.334 | 16.8918 | 15.9457 | 14.5719 | 15.0577 | 15.0272 | 15.58 | 13.4323 | 13.5493 | 14.1277 |  |  |  | 16.6411 | 15.9753 | 15.0916 | 10.225 | 9.5595 | 9.8681 | 17.3049 | 16.4216 | 15.2334 | 16.942 | 16.2234 | 15.2253 | 10.8181 | 11.2122 |  | 12.2072 | 10.0235 | 10.2835 | 8.5995 |  | 6.3181 | 6.2772 | 5.8271 | 5.8956 | 5.8945 | 6.0366 | 6.3349 | 4.1026 | 6.4341 | 3.9766 | 6.7138 | 8.1784 | 42.7317 | 47.023 | 43.6081 | 15.321 |  |  | 0.017963 | -0.21545 | -0.030348 | -0.19648 | 0.072448 | -0.41116 | 0.057728 | 0.29094 | -0.80738 | -0.70489 | -0.51613 | 8.8692 | 8.8704 | 2.0086 | 15.8847 | 16.7376 | 17.2816 | 17.6109 | 17.5877 | 16.5786 | 14.9287 | 16.8942 | 17.2296 | 17.5165 | 17.5631 | 17.3155 | 16.5309 | 14.7706 | 5.7105 | 8.1461 | 5.1143 | 5.3861 | 5.5262 | 6.6677 | 7.6707 | 15.9598 | 15.5488 | 15.4296 | 14.365 | 14.2547 | 14.1989 |  |  |  | 10.7753 | 9.519 | 9.0778 | 9.212 | -0.15109 | -0.091817 | 12.664 |  |  | 10.5729 |  |  | 16.9086 | 16.1111 | 15.0888 | 16.4133 | 15.6956 | 14.8051 | 10.4078 | 10.4687 | 11.4607 | 11.2441 | 9.1758 |  | 10.5955 | 8.1879 | 9.8588 | 9.4235 | 11.0684 | 12.2766 |  | 12.3284 |  |  | 11.7362 | 12.3552 | 12.3825 | [6 empty] | 12.5285 |  |  | 11.351 |  |  | 9.1211 | 10.3729 | 11.9447 | 7.7538 | 8.8381 | 12.5312 | 7.8351 | 9.5299 | 12.2593 | 9.2327 | 10.4998 | 7.5437 | 10.2463 | 8.1444 | 10.1163 | 7.9962 | 9.4613 | 12.9713 | 10.4359 | 10.1938 | 11.5157 | 8.2535 | 9.7808 | 12.5948 | 7.9662 | 10.1148 | 9.7078 | 9.7974 | 8.5487 | 10.1641 | -0.079941 | 20.9538 | 0.034038 | 0.050049 | -38.0552 | 3.1207 | 9.81 | 0.22 | 0.15713 | -0.54072 | -0.20294 | -0.51637 | 0.31342 | -0.74665 | 0.27977 | 0.40697 | 0.41015 | 0.41568 | 0.45396 | 0.63665 | 0.43032 | 0.41189
42810.4352 | -416 | 18.6188 | 18.6541 | 18.6424 | 18.6537 | 18.0185 | 16.6631 | 14.7295 | 16.7464 | 17.2345 | 17.3326 | 17.3469 | 16.8981 | 15.9562 | 14.581 | 15.0602 | 15.0342 | 15.5777 | 13.4302 | 13.5494 | 14.1227 |  |  |  | 16.6423 | 15.9798 | 15.0927 | 10.2354 | 9.5572 | 9.8762 | 17.3053 | 16.4123 | 15.2159 | 16.9297 | 16.2175 | 15.2331 | 10.8149 | 11.1924 |  | 12.1963 | 9.9889 | 10.2643 | 8.5515 |  | 6.3178 | 6.2751 | 5.835 | 5.8772 | 5.8891 | 6.035 | 6.3057 | 4.1677 | 6.4385 | 4.0065 | 6.7119 | 8.1844 | 42.7329 | 47.0161 | 43.6292 | 15.3312 |  |  | 0.027159 | -0.026197 | -0.075032 | 0.01117 | -0.015608 | -0.16342 | -0.034268 | 0.25217 | -0.50341 | -0.34886 | -0.50759 | 8.8687 | 8.8702 | 2.0082 | 15.8897 | 16.7357 | 17.2809 | 17.6111 | 17.5854 | 16.571 | 14.9306 | 16.8908 | 17.2353 | 17.5216 | 17.5663 | 17.3171 | 16.538 | 14.7748 | 5.6385 | 8.1194 | 5.028 | 5.3378 | 5.527 | 6.662 | 7.6658 | 15.9584 | 15.5471 | 15.4245 | 14.3592 | 14.2499 | 14.1902 |  |  |  | 10.7742 | 9.5095 | 9.0675 | 9.187 | 0.069135 | -0.056435 | 12.6719 |  |  | 10.5728 |  |  | 16.9079 | 16.1098 | 15.0944 | 16.4089 | 15.6976 | 14.8043 | 10.4074 | 10.4656 | 11.4478 | 11.2282 | 9.2924 |  | 10.5944 | 8.014 | 9.861 | 9.4165 | 11.0697 | 12.3028 |  | 12.3245 |  |  | 11.745 | 12.3579 | 12.3796 | [6 empty] | 12.5516 |  |  | 11.3595 |  |  | 9.1209 | 10.3804 | 11.9507 | 7.7654 | 8.8205 | 12.5065 | 7.841 | 9.5278 | 12.2382 | 9.2286 | 10.4985 | 7.5519 | 10.2297 | 8.1465 | 10.1028 | 7.9619 | 9.4478 | 12.9769 | 10.4343 | 10.1923 | 11.5216 | 8.2417 | 9.7787 | 12.6069 | 7.9413 | 10.0941 | 9.6987 | 9.7978 | 8.5387 | 10.1589 | 0.014048 | 20.9537 | 0.032936 | 0.048442 | -38.0524 | 3.1206 | 7.83 | 0.35 | 0.19321 | -0.18855 | -0.3191 | 0.12312 | -0.14547 | -0.47073 | -0.21555 | 0.40369 | 0.41505 | 0.41592 | 0.4613 | 0.64568 | 0.43154 | 0.41255
42810.4352 | -415 | 18.611 | 18.6455 | 18.6331 | 18.6494 | 18.0098 | 16.6615 | 14.7168 | 16.7343 | 17.2308 | 17.3207 | 17.3396 | 16.8976 | 15.9553 | 14.5677 | 15.0626 | 15.031 | 15.5774 | 13.4364 | 13.5546 | 14.1213 |  |  |  | 16.6426 | 15.9804 | 15.0949 | 10.2202 | 9.5534 | 9.8807 | 17.3024 | 16.4129 | 15.2254 | 16.9338 | 16.2218 | 15.2317 | 10.8194 | 11.1974 |  | 12.2031 | 9.9817 | 10.2613 | 8.5395 |  | 6.3219 | 6.2757 | 5.8106 | 5.8665 | 5.8829 | 6.0345 | 6.2976 | 4.2501 | 6.4341 | 4.0607 | 6.7026 | 8.1913 | 42.7309 | 47.011 | 43.6354 | 15.3303 |  |  | -0.004381 | -0.16879 | 0.044564 | -0.13602 | -0.069492 | -0.1424 | 0.38891 | 0.31657 | -0.23097 | 0.094028 | -0.36691 | 8.868 | 8.8692 | 2.0086 | 15.8909 | 16.7402 | 17.2854 | 17.6068 | 17.5813 | 16.5736 | 14.9357 | 16.8908 | 17.2308 | 17.5225 | 17.5654 | 17.3116 | 16.5379 | 14.7763 | 5.5864 | 8.0992 | 4.951 | 5.3341 | 5.4737 | 6.6588 | 7.667 | 15.9712 | 15.5703 | 15.4372 | 14.374 | 14.2695 | 14.2108 |  |  |  | 10.7761 | 9.5163 | 9.0757 | 9.17 | 0.061842 | -0.10612 | 12.6627 |  |  | 10.5665 |  |  | 16.896 | 16.1009 | 15.0888 | 16.3991 | 15.6896 | 14.7978 | 10.4 | 10.4562 | 11.4359 | 11.2133 | 9.3735 |  | 10.6011 | 7.8631 | 9.8699 | 9.4322 | 11.0719 | 12.3287 |  | 12.3222 |  |  | 11.7586 | 12.3899 | 12.397 | [6 empty] | 12.5667 |  |  | 11.349 |  |  | 9.1303 | 10.3901 | 11.9571 | 7.7838 | 8.823 | 12.4985 | 7.8394 | 9.542 | 12.2302 | 9.2325 | 10.5088 | 7.5745 | 10.239 | 8.1676 | 10.1178 | 7.9197 | 9.4432 | 12.9822 | 10.4516 | 10.1941 | 11.5256 | 8.2583 | 9.7689 | 12.6003 | 7.9469 | 10.1088 | 9.712 | 9.8172 | 8.528 | 10.1569 | 0.072598 | 20.9527 | 0.033062 | 0.048413 | -38.0909 | 3.1206 | 7.81 | 0.28 | -0.077602 | -0.4786 | 0.24592 | -0.42964 | -0.30696 | -0.4394 | 0.72617 | 0.40166 | 0.41953 | 0.41556 | 0.46671 | 0.65437 | 0.43203 | 0.41309
42810.4352 | -414 | 18.6106 | 18.643 | 18.6319 | 18.6545 | 18.0053 | 16.6574 | 14.7192 | 16.7411 | 17.2303 | 17.3236 | 17.3437 | 16.8978 | 15.9509 | 14.572 | 15.0572 | 15.0329 | 15.5824 | 13.4358 | 13.5451 | 14.1246 |  |  |  | 16.6409 | 15.9795 | 15.0957 | 10.2286 | 9.5524 | 9.8919 | 17.3071 | 16.4131 | 15.2237 | 16.9362 | 16.2159 | 15.2263 | 10.8157 | 11.1932 |  | 12.1966 | 9.9701 | 10.2436 | 8.5184 |  | 6.3178 | 6.2738 | 5.8009 | 5.8536 | 5.8893 | 6.0247 | 6.2801 | 4.3299 | 6.4304 | 4.1256 | 6.7016 | 8.1856 | 42.7289 | 47.0027 | 43.645 | 15.324 |  |  | -0.13186 | 0.011915 | -0.03692 | -0.007886 | -0.15032 | -0.42693 | 0.38694 | 0.2134 | -0.28741 | 0.083747 | -0.20854 | 8.8707 | 8.8717 | 2.0083 | 15.8992 | 16.7473 | 17.2912 | 17.6123 | 17.5851 | 16.5726 | 14.937 | 16.8935 | 17.2275 | 17.5202 | 17.5625 | 17.3187 | 16.5364 | 14.7682 | 5.5995 | 8.1322 | 4.8912 | 5.3114 | 5.428 | 6.6638 | 7.6659 | 15.9553 | 15.5581 | 15.4211 | 14.358 | 14.2564 | 14.1939 |  |  |  | 10.7615 | 9.4952 | 9.0661 | 9.1219 | -0.033583 | -0.078078 | 12.6551 |  |  | 10.5715 |  |  | 16.8985 | 16.0989 | 15.0895 | 16.3968 | 15.684 | 14.8037 | 10.4002 | 10.4523 | 11.4397 | 11.2069 | 9.4096 |  | 10.586 | 7.6966 | 9.8612 | 9.4296 | 11.0696 | 12.3521 |  | 12.3138 |  |  | 11.7715 | 12.4032 | 12.4036 | [6 empty] | 12.5562 |  |  | 11.3252 |  |  | 9.118 | 10.3833 | 11.9404 | 7.7659 | 8.8117 | 12.4789 | 7.8199 | 9.543 | 12.2085 | 9.2145 | 10.4921 | 7.5716 | 10.2224 | 8.1599 | 10.1177 | 7.8914 | 9.439 | 12.9796 | 10.4492 | 10.1914 | 11.5282 | 8.2546 | 9.7765 | 12.594 | 7.9351 | 10.1015 | 9.7057 | 9.8145 | 8.5281 | 10.1626 | 0.14232 | 20.9545 | 0.034067 | 0.04884 | -38.1015 | 3.1207 | 0.37 | 0.27 | -0.42575 | 0.12716 | -0.22384 | -0.10345 | -0.45145 | -0.76082 | 0.72432 | 0.40016 | 0.42387 | 0.41555 | 0.46584 | 0.66089 | 0.43249 | 0.41394
42810.4353 | -413 | 18.6131 | 18.6525 | 18.635 | 18.6536 | 18.0055 | 16.6565 | 14.723 | 16.7371 | 17.2259 | 17.3257 | 17.3413 | 16.8927 | 15.9444 | 14.5717 | 15.0564 | 15.0222 | 15.5785 | 13.4375 | 13.5528 | 14.1224 |  |  |  | 16.6366 | 15.9799 | 15.0983 | 10.2219 | 9.5498 | 9.8938 | 17.3105 | 16.4154 | 15.223 | 16.9388 | 16.2197 | 15.2281 | 10.8157 | 11.1908 |  | 12.1977 | 9.9568 | 10.2367 | 8.4912 |  | 6.3163 | 6.2783 | 5.7909 | 5.8496 | 5.8697 | 6.0117 | 6.2586 | 4.368 | 6.4247 | 4.1713 | 6.6961 | 8.1949 | 42.733 | 47.001 | 43.6572 | 15.328 |  |  | 0.046875 | -0.21873 | 0.003164 | -0.082798 | -0.39673 | -0.29682 | 0.49865 | 0.025464 | -0.54058 | -0.70007 | -0.44082 | 8.8695 | 8.8704 | 2.0084 | 15.8971 | 16.746 | 17.2753 | 17.6152 | 17.5866 | 16.5723 | 14.9385 | 16.89 | 17.2191 | 17.521 | 17.5692 | 17.3178 | 16.5232 | 14.7687 | 5.6264 | 8.1483 | 4.8323 | 5.2667 | 5.3878 | 6.6484 | 7.6523 | 15.969 | 15.5601 | 15.4308 | 14.3588 | 14.26 | 14.1882 |  |  |  | 10.7613 | 9.4977 | 9.0667 | 9.0907 | 0.16334 | -0.03291 | 12.6563 |  |  | 10.586 |  |  | 16.9023 | 16.1074 | 15.0958 | 16.4074 | 15.691 | 14.8092 | 10.4069 | 10.4588 | 11.4447 | 11.1989 | 9.4428 |  | 10.5857 | 7.5536 | 9.8443 | 9.4114 | 11.0628 | 12.3702 |  | 12.2963 |  |  | 11.7921 | 12.4223 | 12.3957 | [6 empty] | 12.5603 |  |  | 11.339 |  |  | 9.1137 | 10.3907 | 11.9408 | 7.79 | 8.8071 | 12.4779 | 7.8353 | 9.556 | 12.2046 | 9.2195 | 10.5029 | 7.5889 | 10.2294 | 8.174 | 10.1214 | 7.893 | 9.4421 | 12.9869 | 10.464 | 10.183 | 11.5272 | 8.2613 | 9.7896 | 12.592 | 7.9293 | 10.1097 | 9.6934 | 9.8154 | 8.5321 | 10.1707 | -0.026591 | 20.9529 | 0.03448 | 0.048732 | -37.9677 | 3.1207 | -8.17 | 0.22 | 0.25384 | -0.54483 | 0.065527 | -0.33521 | -0.7334 | -0.63437 | 0.82223 | 0.39923 | 0.42729 | 0.41583 | 0.46107 | 0.66585 | 0.43325 | 0.4148
42810.4353 | -412 | 18.6189 | 18.6538 | 18.6391 | 18.6565 | 18.0154 | 16.6587 | 14.7281 | 16.7439 | 17.2361 | 17.3301 | 17.345 | 16.8942 | 15.952 | 14.5782 | 15.0541 | 15.0246 | 15.5751 | 13.4305 | 13.5444 | 14.1173 |  |  |  | 16.6384 | 15.9792 | 15.0934 | 10.2258 | 9.5383 | 9.8597 | 17.3164 | 16.4182 | 15.225 | 16.9383 | 16.2246 | 15.2348 | 10.8185 | 11.1836 |  | 12.1944 | 9.9543 | 10.2282 | 8.469 |  | 6.3207 | 6.2653 | 5.7787 | 5.8372 | 5.8528 | 5.9897 | 6.2065 | 4.3856 | 6.4292 | 4.2036 | 6.6974 | 8.188 | 42.7443 | 46.9852 | 43.6536 | 15.3174 |  |  | 0.051475 | -0.11294 | 0.15496 | 0.069654 | -0.15426 | -0.16671 | 0.56765 | 0.00312 | -0.20217 | -0.18648 | -0.2459 | 8.8685 | 8.8693 | 2.0086 | 15.9114 | 16.7412 | 17.2827 | 17.6188 | 17.5939 | 16.5767 | 14.943 | 16.8926 | 17.2329 | 17.5219 | 17.5745 | 17.3215 | 16.5375 | 14.7852 | 5.652 | 8.1802 | 4.803 | 5.2665 | 5.3709 | 6.6455 | 7.6546 | 15.9756 | 15.5671 | 15.4366 | 14.3631 | 14.2573 | 14.1893 |  |  |  | 10.7612 | 9.5006 | 9.0598 | 9.0561 | 0.071161 | 0.0043534 | 12.6501 |  |  | 10.5859 |  |  | 16.9063 | 16.1085 | 15.093 | 16.4035 | 15.6978 | 14.8089 | 10.4084 | 10.4608 | 11.442 | 11.1938 | 9.4376 |  | 10.5866 | 7.5494 | 9.8389 | 9.3937 | 11.062 | 12.4068 |  | 12.3034 |  |  | 11.8116 | 12.4352 | 12.411 | [6 empty] | 12.5646 |  |  | 11.3602 |  |  | 9.1239 | 10.3887 | 11.9301 | 7.8026 | 8.8047 | 12.4737 | 7.8377 | 9.5631 | 12.2014 | 9.2146 | 10.5032 | 7.5927 | 10.2262 | 8.1824 | 10.1228 | 7.8799 | 9.435 | 12.9841 | 10.4656 | 10.1746 | 11.5155 | 8.2594 | 9.7863 | 12.6013 | 7.9021 | 10.1075 | 9.6854 | 9.8152 | 8.5339 | 10.1706 | 0.020981 | 20.952 | 0.034612 | 0.048276 | -37.883 | 3.1207 | -0.75 | 0.29 | 0.26599 | -0.39148 | 0.45857 | 0.30744 | -0.4573 | -0.4754 | 0.87724 | 0.39941 | 0.42723 | 0.4163 | 0.45788 | 0.66938 | 0.43396 | 0.41576
42810.4353 | -411 | 18.6225 | 18.6595 | 18.6445 | 18.6638 | 18.0138 | 16.6644 | 14.7316 | 16.7439 | 17.24 | 17.3378 | 17.3522 | 16.9004 | 15.9573 | 14.5801 | 15.0584 | 15.034 | 15.5768 | 13.4309 | 13.542 | 14.121 |  |  |  | 16.6322 | 15.9804 | 15.0912 | 10.2227 | 9.5342 | 9.8569 | 17.3229 | 16.4269 | 15.2308 | 16.9464 | 16.2303 | 15.24 | 10.8215 | 11.1857 |  | 12.1992 | 9.9535 | 10.2143 | 8.4552 |  | 6.3192 | 6.2633 | 5.7775 | 5.8204 | 5.8434 | 5.9692 | 6.1608 | 4.3786 | 6.4202 | 4.2945 | 6.694 | 8.1853 | 42.7578 | 46.9584 | 43.6507 | 15.3049 |  |  | 0.13099 | -0.039997 | 0.058364 | 0.017086 | -0.093148 | 0.03174 | 0.68264 | 0.006408 | 0.60036 | -0.29431 | -0.21053 | 8.8668 | 8.8678 | 2.0083 | 15.8977 | 16.7415 | 17.2793 | 17.6101 | 17.5819 | 16.5713 | 14.9274 | 16.8918 | 17.2232 | 17.5195 | 17.5626 | 17.3131 | 16.5351 | 14.7659 | 5.7151 | 8.2067 | 4.7961 | 5.2696 | 5.3861 | 6.6477 | 7.648 | 15.9699 | 15.5639 | 15.4333 | 14.3594 | 14.2623 | 14.193 |  |  |  | 10.7667 | 9.5015 | 9.06 | 9.0232 | 0.00248 | 0.042182 | 12.6339 |  |  | 10.5798 |  |  | 16.9018 | 16.1029 | 15.0841 | 16.3994 | 15.6942 | 14.8009 | 10.3954 | 10.4454 | 11.4234 | 11.1779 | 9.3487 |  | 10.5886 | 7.6002 | 9.8381 | 9.3752 | 11.0655 | 12.4218 |  | 12.3092 |  |  | 11.8292 | 12.4383 | 12.4173 | [6 empty] | 12.5523 |  |  | 11.3649 |  |  | 9.1304 | 10.3866 | 11.927 | 7.8082 | 8.8073 | 12.4628 | 7.8423 | 9.5754 | 12.1996 | 9.2087 | 10.497 | 7.5921 | 10.2291 | 8.1776 | 10.126 | 7.8362 | 9.4294 | 12.9701 | 10.4525 | 10.1595 | 11.5027 | 8.2463 | 9.7703 | 12.5873 | 7.8718 | 10.0968 | 9.6726 | 9.8048 | 8.5189 | 10.1559 | 0.015974 | 20.9541 | 0.033435 | 0.047458 | -38.0571 | 3.1206 | -12.62 | 0.29 | 0.42431 | -0.23297 | 0.28143 | 0.15227 | -0.35534 | 0.20743 | 0.96196 | 0.40194 | 0.42579 | 0.41693 | 0.45112 | 0.66938 | 0.43444 | 0.41686
42810.4353 | -410 | 18.6147 | 18.6515 | 18.643 | 18.6621 | 18.0067 | 16.6577 | 14.728 | 16.743 | 17.2312 | 17.3172 | 17.352 | 16.9003 | 15.9544 | 14.5714 | 15.0599 | 15.0351 | 15.5854 | 13.4334 | 13.5464 | 14.1244 |  |  |  | 16.635 | 15.9816 | 15.0991 | 10.2297 | 9.5354 | 9.8603 | 17.3249 | 16.4309 | 15.2296 | 16.9496 | 16.2294 | 15.2317 | 10.8239 | 11.1681 |  | 12.1983 | 9.9436 | 10.2115 | 8.4316 |  | 6.3093 | 6.2531 | 5.7715 | 5.8222 | 5.8257 | 5.9589 | 6.15 | 4.3775 | 6.4179 | 4.4082 | 6.6936 | 8.1969 | 42.7649 | 46.9621 | 43.6589 | 15.3068 |  |  | -0.031321 | -0.10374 | 0.1037 | 0.040086 | -0.15229 | 0.026484 | 0.58079 | -0.11253 | -0.032288 | -0.22445 | -0.36432 | 8.8684 | 8.8697 | 2.0084 | 15.8966 | 16.7368 | 17.2806 | 17.6012 | 17.5817 | 16.5633 | 14.9293 | 16.8987 | 17.2229 | 17.5207 | 17.5642 | 17.3145 | 16.5352 | 14.7725 | 5.7387 | 8.2118 | 4.7884 | 5.2412 | 5.4187 | 6.6418 | 7.6495 | 15.9727 | 15.5606 | 15.4244 | 14.3677 | 14.2554 | 14.1928 |  |  |  | 10.765 | 9.5007 | 9.0594 | 8.9986 | 0.0071398 | 0.053285 | 12.6259 |  |  | 10.5823 |  |  | 16.8963 | 16.1012 | 15.0879 | 16.3977 | 15.6923 | 14.7981 | 10.3935 | 10.4379 | 11.4169 | 11.1633 | 9.2756 |  | 10.5858 | 7.6819 | 9.8381 | 9.3745 | 11.0614 | 12.4226 |  | 12.3124 |  |  | 11.8487 | 12.4177 | 12.4173 | [6 empty] | 12.5596 |  |  | 11.3614 |  |  | 9.1372 | 10.3945 | 11.9137 | 7.7824 | 8.8093 | 12.4607 | 7.8462 | 9.57 | 12.2053 | 9.2111 | 10.4998 | 7.5839 | 10.2342 | 8.1907 | 10.1245 | 7.7964 | 9.4377 | 12.9612 | 10.453 | 10.1448 | 11.493 | 8.2379 | 9.7699 | 12.5752 | 7.8672 | 10.097 | 9.6664 | 9.8001 | 8.5176 | 10.1536 | -0.027169 | 20.9546 | 0.03285 | 0.048008 | -38.0278 | 3.1206 | -2.89 | 0.28 | -0.20748 | -0.37519 | 0.37513 | 0.23323 | -0.45435 | 0.18947 | 0.88729 | 0.40388 | 0.42352 | 0.41681 | 0.44782 | 0.6704 | 0.43517 | 0.41748
42810.4353 | -409 | 18.6271 | 18.6581 | 18.6395 | 18.6577 | 18.0155 | 16.6573 | 14.7258 | 16.7463 | 17.2324 | 17.3272 | 17.3466 | 16.9001 | 15.9539 | 14.5721 | 15.0644 | 15.0338 | 15.589 | 13.4375 | 13.5508 | 14.1307 |  |  |  | 16.637 | 15.981 | 15.0941 | 10.2338 | 9.5364 | 9.8485 | 17.3239 | 16.4269 | 15.2238 | 16.9377 | 16.2164 | 15.236 | 10.8059 | 11.1787 |  | 12.1909 | 9.9277 | 10.1927 | 8.3881 |  | 6.3128 | 6.2456 | 5.7651 | 5.8196 | 5.8256 | 5.9641 | 6.1835 | 4.3819 | 6.4271 | 4.4911 | 6.6928 | 8.1972 | 42.7699 | 46.9526 | 43.6548 | 15.3027 |  |  | 0.098131 | 0.037543 | 0.10239 | -0.082138 | 0.013308 | 0.005456 | 0.35869 | -0.011336 | -0.46955 | 0.34432 | -0.29438 | 8.8693 | 8.8703 | 2.0084 | 15.9003 | 16.7396 | 17.275 | 17.6001 | 17.5804 | 16.5607 | 14.93 | 16.8991 | 17.229 | 17.5251 | 17.5675 | 17.3153 | 16.5241 | 14.7707 | 5.7688 | 8.2042 | 4.8517 | 5.2152 | 5.4418 | 6.6388 | 7.6455 | 15.9786 | 15.5612 | 15.4315 | 14.3595 | 14.258 | 14.1929 |  |  |  | 10.7666 | 9.4986 | 9.0596 | 8.9954 | -0.14299 | 0.15134 | 12.6276 |  |  | 10.5814 |  |  | 16.9029 | 16.0962 | 15.0913 | 16.4002 | 15.6879 | 14.7984 | 10.3971 | 10.4477 | 11.4067 | 11.1497 | 9.2046 |  | 10.5895 | 7.7945 | 9.8372 | 9.398 | 11.0581 | 12.4188 |  | 12.3119 |  |  | 11.8699 | 12.412 | 12.4102 | [6 empty] | 12.5689 |  |  | 11.3616 |  |  | 9.1435 | 10.3951 | 11.9165 | 7.7597 | 8.8124 | 12.4634 | 7.845 | 9.5729 | 12.2089 | 9.2123 | 10.5017 | 7.576 | 10.2443 | 8.2008 | 10.1301 | 7.7811 | 9.4494 | 12.9598 | 10.4624 | 10.1395 | 11.4909 | 8.213 | 9.7629 | 12.5683 | 7.8613 | 10.0967 | 9.669 | 9.7998 | 8.5157 | 10.158 | -0.0069458 | 20.952 | 0.034159 | 0.050693 | -37.9817 | 3.1206 | -8.26 | 0.32 | 0.36725 | 0.22571 | 0.37274 | -0.33385 | 0.13431 | 0.085999 | 0.69729 | 0.40598 | 0.42036 | 0.41605 | 0.44413 | 0.66291 | 0.43579 | 0.41762
42810.4353 | -408 | 18.6292 | 18.6645 | 18.6469 | 18.6593 | 18.0186 | 16.6601 | 14.7282 | 16.7514 | 17.2398 | 17.3314 | 17.3497 | 16.9025 | 15.9599 | 14.5767 | 15.0695 | 15.0287 | 15.5833 | 13.4331 | 13.5529 | 14.1294 |  |  |  | 16.633 | 15.9807 | 15.0914 | 10.2239 | 9.5353 | 9.8286 | 17.3165 | 16.429 | 15.2278 | 16.9536 | 16.222 | 15.2325 | 10.8217 | 11.1914 |  | 12.1864 | 9.9296 | 10.1953 | 8.36 |  | 6.3101 | 6.2431 | 5.7665 | 5.8178 | 5.8699 | 5.9691 | 6.168 | 4.3948 | 6.4174 | 4.4883 | 6.6913 | 8.2006 | 42.7932 | 46.9498 | 43.6629 | 15.3008 |  |  | -0.003725 | -0.049853 | -0.040864 | -0.062426 | 0.008048 | -0.20614 | 0.52691 | -0.18284 | -0.63419 | -0.53265 | -0.41678 | 8.8708 | 8.8719 | 2.0085 | 15.9045 | 16.7513 | 17.2815 | 17.6022 | 17.5767 | 16.5665 | 14.9383 | 16.902 | 17.2333 | 17.5279 | 17.5703 | 17.3209 | 16.5321 | 14.7714 | 5.7499 | 8.21 | 4.9385 | 5.2108 | 5.4411 | 6.639 | 7.6481 | 15.9798 | 15.5651 | 15.4324 | 14.3635 | 14.2604 | 14.1924 |  |  |  | 10.77 | 9.4942 | 9.0573 | 9.0017 | -0.098415 | 0.032207 | 12.6291 |  |  | 10.5884 |  |  | 16.9015 | 16.0975 | 15.0875 | 16.3991 | 15.6881 | 14.7981 | 10.3926 | 10.4527 | 11.3952 | 11.1326 | 9.1605 |  | 10.5934 | 7.9447 | 9.84 | 9.4233 | 11.0637 | 12.3996 |  | 12.3143 |  |  | 11.8768 | 12.4187 | 12.4083 | [6 empty] | 12.5705 |  |  | 11.3622 |  |  | 9.1498 | 10.403 | 11.9221 | 7.7523 | 8.8272 | 12.4635 | 7.8331 | 9.5798 | 12.2226 | 9.2162 | 10.5112 | 7.5927 | 10.2539 | 8.2032 | 10.1357 | 7.773 | 9.4477 | 12.9566 | 10.4608 | 10.1262 | 11.4808 | 8.195 | 9.7525 | 12.5583 | 7.8578 | 10.0955 | 9.6675 | 9.7912 | 8.5083 | 10.1563 | -0.14215 | 20.9522 | 0.034153 | 0.051482 | -37.9937 | 3.1206 | -4.48 | 0.42 | -0.07155 | -0.26009 | -0.23548 | -0.29104 | 0.10445 | -0.52861 | 0.84514 | 0.40733 | 0.41628 | 0.41553 | 0.44624 | 0.65357 | 0.43709 | 0.41756
42810.4353 | -407 | 18.6264 | 18.659 | 18.6379 | 18.6499 | 18.0122 | 16.6589 | 14.7231 | 16.7512 | 17.234 | 17.3344 | 17.3509 | 16.8999 | 15.9569 | 14.5799 | 15.0753 | 15.0369 | 15.5812 | 13.4362 | 13.558 | 14.1168 |  |  |  | 16.6405 | 15.9825 | 15.0955 | 10.2239 | 9.528 | 9.8353 | 17.3149 | 16.4229 | 15.2255 | 16.9422 | 16.2188 | 15.231 | 10.816 | 11.1853 |  | 12.1815 | 9.9331 | 10.1826 | 8.3294 |  | 6.3037 | 6.2421 | 5.7642 | 5.8353 | 5.9082 | 5.9585 | 6.1481 | 4.3558 | 6.4091 | 4.4541 | 6.6976 | 8.1899 | 42.8018 | 46.94 | 43.6639 | 15.2832 |  |  | -0.007665 | -0.027509 | 0.22067 | -0.14128 | -0.15032 | -0.20745 | 0.51771 | -0.029076 | -0.56705 | -0.20368 | -0.4899 | 8.8693 | 8.8705 | 2.0085 | 15.9103 | 16.7467 | 17.2921 | 17.6064 | 17.5802 | 16.5703 | 14.9315 | 16.8943 | 17.2345 | 17.5167 | 17.57 | 17.3188 | 16.5338 | 14.774 | 5.7125 | 8.209 | 5.0122 | 5.3306 | 5.4185 | 6.6343 | 7.6505 | 15.9758 | 15.5753 | 15.4307 | 14.3649 | 14.263 | 14.201 |  |  |  | 10.7714 | 9.4963 | 9.0533 | 9.0091 | 0.11249 | -0.027264 | 12.6233 |  |  | 10.5875 |  |  | 16.898 | 16.0967 | 15.087 | 16.3934 | 15.6923 | 14.7982 | 10.3872 | 10.4514 | 11.3788 | 11.1018 | 9.0964 |  | 10.5779 | 8.1277 | 9.8358 | 9.4025 | 11.0564 | 12.3587 |  | 12.3134 |  |  | 11.8934 | 12.4109 | 12.4266 | [6 empty] | 12.5655 |  |  | 11.3686 |  |  | 9.1459 | 10.3978 | 11.9165 | 7.7484 | 8.8366 | 12.465 | 7.8265 | 9.5812 | 12.2283 | 9.2067 | 10.5191 | 7.6041 | 10.263 | 8.1933 | 10.1318 | 7.7804 | 9.4661 | 12.9666 | 10.473 | 10.1271 | 11.4825 | 8.1863 | 9.758 | 12.5507 | 7.8639 | 10.1088 | 9.6659 | 9.7992 | 8.5156 | 10.1561 | 0.010966 | 20.9515 | 0.034222 | 0.050389 | -37.9873 | 3.1206 | -9.45 | 0.33 | -0.10264 | -0.1932 | 0.5472 | -0.43784 | -0.45139 | -0.53029 | 0.83771 | 0.4086 | 0.41106 | 0.41587 | 0.44986 | 0.64567 | 0.43775 | 0.4174
42810.4353 | -406 | 18.6282 | 18.6612 | 18.6445 | 18.6577 | 18.0121 | 16.6663 | 14.7213 | 16.7495 | 17.2354 | 17.3295 | 17.3535 | 16.904 | 15.9577 | 14.5802 | 15.069 | 15.0386 | 15.585 | 13.4357 | 13.558 | 14.1205 |  |  |  | 16.6398 | 15.9834 | 15.0965 | 10.2151 | 9.5241 | 9.8538 | 17.3341 | 16.4305 | 15.2346 | 16.9477 | 16.2268 | 15.2376 | 10.8166 | 11.2025 |  | 12.1859 | 9.955 | 10.1969 | 8.307 |  | 6.3042 | 6.2411 | 5.771 | 5.8608 | 5.9063 | 5.9548 | 6.1231 | 4.2961 | 6.4084 | 4.4726 | 6.6971 | 8.194 | 42.8115 | 46.9434 | 43.658 | 15.2663 |  |  | 0.057387 | 0.036887 | 0.016308 | -0.019714 | 0.13027 | -0.1286 | 0.48091 | -0.036964 | 1.3099 | -0.56181 | -0.20596 | 8.8688 | 8.87 | 2.0086 | 15.9107 | 16.7503 | 17.2763 | 17.6055 | 17.5832 | 16.5723 | 14.9323 | 16.8954 | 17.2226 | 17.52 | 17.5678 | 17.309 | 16.5309 | 14.7676 | 5.7307 | 8.2011 | 5.1184 | 5.4833 | 5.3729 | 6.636 | 7.6408 | 15.9797 | 15.5814 | 15.4312 | 14.3746 | 14.2639 | 14.1963 |  |  |  | 10.7689 | 9.4931 | 9.0539 | 9.0029 | 0.036517 | -0.039121 | 12.6249 |  |  | 10.5903 |  |  | 16.9034 | 16.102 | 15.0908 | 16.3975 | 15.6982 | 14.8008 | 10.3814 | 10.4562 | 11.3586 | 11.0763 | 9.0701 |  | 10.5844 | 8.1995 | 9.8349 | 9.3754 | 11.0574 | 12.3055 |  | 12.3115 |  |  | 11.9061 | 12.4184 | 12.4487 | [6 empty] | 12.567 |  |  | 11.3816 |  |  | 9.1358 | 10.3924 | 11.8952 | 7.7418 | 8.8327 | 12.4555 | 7.8106 | 9.5779 | 12.2305 | 9.1886 | 10.5124 | 7.6045 | 10.2632 | 8.1583 | 10.1222 | 7.7619 | 9.4747 | 12.9613 | 10.4715 | 10.1215 | 11.4731 | 8.17 | 9.7472 | 12.5483 | 7.8587 | 10.1045 | 9.6432 | 9.7938 | 8.5218 | 10.1536 | -0.14658 | 20.9523 | 0.032471 | 0.048761 | -38.0556 | 3.1206 | -4.47 | 0.31 | 0.28085 | 0.22372 | 0.14876 | -0.16355 | 0.42022 | -0.41751 | 0.80739 | 0.40954 | 0.40904 | 0.41666 | 0.44803 | 0.63273 | 0.4384 | 0.41749
42810.4353 | -405 | 18.6318 | 18.6572 | 18.6363 | 18.6627 | 18.0121 | 16.6605 | 14.7225 | 16.7446 | 17.232 | 17.3295 | 17.3481 | 16.897 | 15.9525 | 14.5721 | 15.0695 | 15.0369 | 15.5862 | 13.4407 | 13.5558 | 14.1262 |  |  |  | 16.6347 | 15.9787 | 15.0967 | 10.2202 | 9.5229 | 9.8653 | 17.3268 | 16.427 | 15.2313 | 16.9473 | 16.2286 | 15.2321 | 10.8165 | 11.2213 |  | 12.1894 | 9.9704 | 10.1967 | 8.3096 |  | 6.3144 | 6.2511 | 5.792 | 5.8723 | 5.9023 | 5.9572 | 6.1212 | 4.2601 | 6.407 | 4.5041 | 6.7014 | 8.1949 | 42.8176 | 46.941 | 43.6628 | 15.2631 |  |  | -0.12726 | -0.082709 | 0.016964 | -0.095282 | -0.16543 | -0.21271 | 0.49208 | 0.16609 | -0.56432 | -0.65706 | -0.2616 | 8.8706 | 8.8717 | 2.0082 | 15.9125 | 16.7394 | 17.284 | 17.6078 | 17.5811 | 16.5743 | 14.9304 | 16.8993 | 17.2327 | 17.521 | 17.5665 | 17.3051 | 16.527 | 14.7686 | 5.7646 | 8.213 | 5.1941 | 5.5526 | 5.3941 | 6.6328 | 7.6478 | 15.9837 | 15.5706 | 15.4303 | 14.3675 | 14.2619 | 14.1934 |  |  |  | 10.763 | 9.4975 | 9.0533 | 9.0057 | 0.036517 | -0.011832 | 12.626 |  |  | 10.5879 |  |  | 16.8979 | 16.0935 | 15.0858 | 16.4008 | 15.692 | 14.7959 | 10.3713 | 10.4546 | 11.3458 | 11.0678 | 9.0571 |  | 10.5829 | 8.256 | 9.8317 | 9.3521 | 11.0543 | 12.2367 |  | 12.3066 |  |  | 11.9047 | 12.4413 | 12.4562 | [6 empty] | 12.5746 |  |  | 11.3808 |  |  | 9.1433 | 10.4018 | 11.8985 | 7.7649 | 8.8552 | 12.4758 | 7.8219 | 9.5864 | 12.2419 | 9.2029 | 10.5185 | 7.6305 | 10.2897 | 8.1574 | 10.1273 | 7.7573 | 9.4829 | 12.9654 | 10.4633 | 10.1163 | 11.4635 | 8.1619 | 9.7482 | 12.5439 | 7.8635 | 10.1146 | 9.6288 | 9.8132 | 8.5228 | 10.1506 | 0.031959 | 20.9508 | 0.033889 | 0.050476 | -38.0924 | 3.1205 | -13.43 | 0.26 | -0.41823 | -0.33501 | 0.15172 | -0.35957 | -0.47354 | -0.53696 | 0.81671 | 0.40985 | 0.40736 | 0.4172 | 0.4439 | 0.62514 | 0.43832 | 0.41722
42810.4354 | -404 | 18.6269 | 18.6582 | 18.635 | 18.6601 | 18.013 | 16.6589 | 14.7252 | 16.7418 | 17.2365 | 17.332 | 17.3424 | 16.8989 | 15.9552 | 14.5725 | 15.075 | 15.0361 | 15.5897 | 13.4352 | 13.5536 | 14.1229 |  |  |  | 16.6333 | 15.9809 | 15.098 | 10.2153 | 9.5283 | 9.8639 | 17.3322 | 16.4404 | 15.2354 | 16.9532 | 16.2281 | 15.2381 | 10.821 | 11.2385 |  | 12.1919 | 9.9906 | 10.1953 | 8.351 |  | 6.3188 | 6.2653 | 5.824 | 5.8767 | 5.9116 | 5.9581 | 6.1298 | 4.2681 | 6.4056 | 4.4737 | 6.6957 | 8.1989 | 42.8098 | 46.9316 | 43.6524 | 15.2583 |  |  | -0.16932 | -0.22136 | -0.13812 | 0.18333 | -0.13126 | 0.13031 | 0.63665 | 0.25546 | -0.38996 | -0.92665 | -0.42135 | 8.8677 | 8.8685 | 2.0085 | 15.9068 | 16.746 | 17.2793 | 17.6062 | 17.5789 | 16.5678 | 14.9273 | 16.8897 | 17.2265 | 17.5184 | 17.5593 | 17.3132 | 16.5213 | 14.7664 | 5.7832 | 8.2326 | 5.2181 | 5.5316 | 5.4522 | 6.629 | 7.6448 | 15.9889 | 15.5744 | 15.4318 | 14.3645 | 14.2595 | 14.1904 |  |  |  | 10.7585 | 9.4966 | 9.0484 | 8.9932 | 0.0083554 | -0.098027 | 12.627 |  |  | 10.5889 |  |  | 16.9046 | 16.0903 | 15.0907 | 16.398 | 15.6847 | 14.7979 | 10.371 | 10.4625 | 11.3452 | 11.0605 | 9.0824 |  | 10.5716 | 8.2991 | 9.8222 | 9.3302 | 11.0569 | 12.1254 |  | 12.3048 |  |  | 11.9112 | 12.4684 | 12.4843 | [6 empty] | 12.59 |  |  | 11.3923 |  |  | 9.1444 | 10.4066 | 11.8967 | 7.7736 | 8.8719 | 12.4771 | 7.8176 | 9.5706 | 12.2466 | 9.208 | 10.5273 | 7.6426 | 10.2902 | 8.1473 | 10.119 | 7.7595 | 9.4873 | 12.9625 | 10.4605 | 10.1145 | 11.4588 | 8.1676 | 9.742 | 12.5377 | 7.8863 | 10.13 | 9.6287 | 9.8147 | 8.5191 | 10.1526 | -0.032947 | 20.9519 | 0.033958 | 0.051439 | -38.1273 | 3.1205 | 19.18 | 0.25 | -0.48242 | -0.54808 | -0.43293 | 0.49879 | -0.42181 | 0.42028 | 0.92897 | 0.40878 | 0.40585 | 0.4179 | 0.44139 | 0.62211 | 0.43732 | 0.41742
42810.4354 | -403 | 18.6373 | 18.6566 | 18.6413 | 18.6646 | 18.0112 | 16.6641 | 14.7265 | 16.7473 | 17.2357 | 17.3317 | 17.3468 | 16.9058 | 15.9645 | 14.5821 | 15.0811 | 15.0365 | 15.5886 | 13.4379 | 13.5565 | 14.1176 |  |  |  | 16.6447 | 15.9835 | 15.0999 | 10.224 | 9.5239 | 9.8454 | 17.3341 | 16.4458 | 15.2328 | 16.9542 | 16.2364 | 15.2425 | 10.8263 | 11.2658 |  | 12.2036 | 10.0123 | 10.1917 | 8.3989 |  | 6.3331 | 6.274 | 5.8165 | 5.8739 | 5.9123 | 5.969 | 6.1566 | 4.3097 | 6.3983 | 4.4477 | 6.6887 | 8.1979 | 42.8049 | 46.9298 | 43.6401 | 15.2461 |  |  | 0.19407 | 0.002059 | 0.01762 | -0.014458 | -0.070804 | -0.32376 | 0.6695 | 0.20748 | -0.86051 | 0.026262 | -0.54296 | 8.8649 | 8.866 | 2.0085 | 15.9118 | 16.7542 | 17.2886 | 17.609 | 17.5825 | 16.5756 | 14.9286 | 16.8983 | 17.2258 | 17.5248 | 17.5657 | 17.3123 | 16.5268 | 14.7643 | 5.7917 | 8.2495 | 5.1889 | 5.5206 | 5.4793 | 6.629 | 7.6453 | 15.9923 | 15.574 | 15.4377 | 14.3685 | 14.2583 | 14.1952 |  |  |  | 10.761 | 9.4992 | 9.0438 | 8.9724 | -0.11564 | 0.035406 | 12.6302 |  |  | 10.5837 |  |  | 16.9041 | 16.0951 | 15.0863 | 16.3996 | 15.6777 | 14.7923 | 10.369 | 10.4519 | 11.3293 | 11.0571 | 9.0932 |  | 10.5754 | 8.3245 | 9.8267 | 9.3119 | 11.0524 | 12.0403 |  | 12.3118 |  |  | 11.9224 | 12.4473 | 12.4817 | [6 empty] | 12.5787 |  |  | 11.3945 |  |  | 9.1371 | 10.3901 | 11.8897 | 7.7787 | 8.8842 | 12.4752 | 7.7929 | 9.5615 | 12.2436 | 9.1912 | 10.5155 | 7.6342 | 10.2987 | 8.1375 | 10.1135 | 7.7646 | 9.4882 | 12.9567 | 10.4529 | 10.0994 | 11.4442 | 8.1587 | 9.732 | 12.528 | 7.8856 | 10.142 | 9.6187 | 9.812 | 8.5174 | 10.1396 | 0.05276 | 20.9525 | 0.034497 | 0.051526 | -38.075 | 3.1205 | 3.46 | 0.31 | 0.51646 | 0.05286 | 0.15463 | -0.14007 | -0.30981 | -0.66248 | 0.95266 | 0.4086 | 0.4053 | 0.41826 | 0.44045 | 0.62542 | 0.43616 | 0.41808
42810.4354 | -402 | 18.6276 | 18.6587 | 18.6369 | 18.6568 | 18.0029 | 16.6481 | 14.7219 | 16.7376 | 17.2297 | 17.3374 | 17.3512 | 16.8986 | 15.9593 | 14.579 | 15.0817 | 15.0476 | 15.5898 | 13.4332 | 13.5605 | 14.1241 |  |  |  | 16.6481 | 15.987 | 15.087 | 10.2236 | 9.5315 | 9.8156 | 17.3286 | 16.4302 | 15.2332 | 16.944 | 16.2301 | 15.2362 | 10.8154 | 11.3122 |  | 12.1943 | 10.0347 | 10.1782 | 8.4274 |  | 6.3396 | 6.2804 | 5.8229 | 5.8776 | 5.9124 | 5.9671 | 6.1567 | 4.2167 | 6.3888 | 4.4198 | 6.6845 | 8.2 | 42.786 | 46.9523 | 43.6316 | 15.235 |  |  | 0.19801 | -0.23253 | -0.06846 | -0.11105 | 0.1513 | 0.10862 | 0.63336 | 0.23771 | -0.86576 | -0.42145 | -0.17655 | 8.8698 | 8.8707 | 2.0084 | 15.9099 | 16.7472 | 17.2883 | 17.6055 | 17.5808 | 16.574 | 14.9309 | 16.8966 | 17.2269 | 17.5191 | 17.5626 | 17.3081 | 16.5264 | 14.7635 | 5.7659 | 8.245 | 5.1193 | 5.522 | 5.4685 | 6.6262 | 7.645 | 15.9887 | 15.5782 | 15.438 | 14.3677 | 14.2648 | 14.1911 |  |  |  | 10.7558 | 9.4951 | 9.0408 | 8.9465 | 0.074606 | 0.17731 | 12.6327 |  |  | 10.595 |  |  | 16.8966 | 16.1015 | 15.0826 | 16.4048 | 15.6905 | 14.7934 | 10.3695 | 10.4604 | 11.3216 | 11.0505 | 9.0882 |  | 10.5752 | 8.3726 | 9.824 | 9.3009 | 11.0467 | 11.9667 |  | 12.3088 |  |  | 11.9302 | 12.4485 | 12.4951 | [6 empty] | 12.5632 |  |  | 11.3914 |  |  | 9.1359 | 10.405 | 11.8833 | 7.7855 | 8.8951 | 12.4855 | 7.7981 | 9.5604 | 12.2407 | 9.1903 | 10.5196 | 7.6476 | 10.3086 | 8.1391 | 10.1197 | 7.7705 | 9.494 | 12.9644 | 10.4538 | 10.1014 | 11.4375 | 8.1555 | 9.7355 | 12.5181 | 7.8932 | 10.1374 | 9.6152 | 9.8203 | 8.5049 | 10.1312 | -0.33456 | 20.9519 | 0.033481 | 0.049463 | -38.1629 | 3.1206 | 13.48 | 0.36 | 0.52165 | -0.56175 | -0.30481 | -0.38821 | 0.45288 | 0.38372 | 0.92659 | 0.40874 | 0.40387 | 0.41837 | 0.44299 | 0.63312 | 0.43501 | 0.41863
42810.4354 | -401 | 18.639 | 18.6656 | 18.6509 | 18.6714 | 18.0216 | 16.6691 | 14.7275 | 16.7485 | 17.2413 | 17.3383 | 17.3556 | 16.908 | 15.9717 | 14.589 | 15.0727 | 15.0409 | 15.5878 | 13.4299 | 13.5574 | 14.1205 |  |  |  | 16.6371 | 15.9801 | 15.081 | 10.2075 | 9.5194 | 9.781 | 17.3378 | 16.4319 | 15.2373 | 16.9469 | 16.2304 | 15.2366 | 10.8143 | 11.3716 |  | 12.1801 | 10.0501 | 10.1889 | 8.4613 |  | 6.3502 | 6.2958 | 5.8434 | 5.8928 | 5.9347 | 5.9832 | 6.1609 | 4.1678 | 6.4043 | 4.3479 | 6.6976 | 8.2022 | 42.7708 | 46.961 | 43.6259 | 15.2277 |  |  | 0.058047 | -0.057081 | 0.034708 | -0.12551 | 0.07442 | -0.029372 | 0.4566 | 0.11352 | -1.6093 | -0.0075156 | -0.35717 | 8.8685 | 8.8699 | 2.0086 | 15.9125 | 16.7475 | 17.2824 | 17.6027 | 17.5785 | 16.5715 | 14.9246 | 16.8906 | 17.2193 | 17.5129 | 17.5572 | 17.3075 | 16.5191 | 14.7589 | 5.7879 | 8.2291 | 5.0635 | 5.524 | 5.4646 | 6.6215 | 7.6422 | 15.9899 | 15.5869 | 15.4343 | 14.3743 | 14.2681 | 14.2021 |  |  |  | 10.7673 | 9.4898 | 9.0522 | 8.9489 | 0.1133 | 0.019786 | 12.6387 |  |  | 10.5947 |  |  | 16.9021 | 16.1001 | 15.085 | 16.4058 | 15.6882 | 14.7967 | 10.3715 | 10.459 | 11.3177 | 11.0475 | 9.0883 |  | 10.5859 | 8.4527 | 9.8218 | 9.3002 | 11.0477 | 11.8927 |  | 12.31 |  |  | 11.9129 | 12.4588 | 12.5191 | [6 empty] | 12.5652 |  |  | 11.3953 |  |  | 9.1341 | 10.3908 | 11.8845 | 7.7924 | 8.9063 | 12.4931 | 7.7977 | 9.544 | 12.2294 | 9.1997 | 10.5188 | 7.6632 | 10.3105 | 8.1204 | 10.1306 | 7.7758 | 9.5056 | 12.9751 | 10.4585 | 10.0988 | 11.4276 | 8.1505 | 9.7298 | 12.5164 | 7.9076 | 10.1327 | 9.6186 | 9.8184 | 8.5015 | 10.1355 | -0.11923 | 20.9521 | 0.032632 | 0.048377 | -38.1775 | 3.1205 | 10.26 | 0.4 | 0.28242 | -0.27833 | 0.21704 | -0.41272 | 0.31763 | -0.19954 | 0.78675 | 0.40908 | 0.40158 | 0.41843 | 0.44 | 0.639 | 0.43403 | 0.41894
42810.4354 | -400 | 18.63 | 18.6653 | 18.64 | 18.6631 | 18.0111 | 16.6567 | 14.7192 | 16.7445 | 17.2338 | 17.3313 | 17.3513 | 16.9054 | 15.9572 | 14.5775 | 15.0846 | 15.0498 | 15.5962 | 13.4355 | 13.5497 | 14.1276 |  |  |  | 16.6441 | 15.9916 | 15.1012 | 10.2107 | 9.5188 | 9.7856 | 17.3305 | 16.4316 | 15.2382 | 16.9463 | 16.2232 | 15.2359 | 10.8166 | 11.4026 |  | 12.1955 | 10.0654 | 10.1789 | 8.4612 |  | 6.3431 | 6.3018 | 5.8399 | 5.8994 | 5.9321 | 5.9812 | 6.1408 | 4.1737 | 6.3964 | 4.2443 | 6.6875 | 8.2039 | 42.7569 | 46.9682 | 43.6233 | 15.2234 |  |  | 0.12967 | -0.11951 | -0.03232 | -0.095938 | 0.092816 | 0.026484 | 0.38563 | -0.044192 | -0.10935 | -1.0399 | -0.45136 | 8.8678 | 8.8692 | 2.0082 | 15.9201 | 16.7557 | 17.2915 | 17.6165 | 17.5908 | 16.5753 | 14.9329 | 16.9014 | 17.23 | 17.5229 | 17.5676 | 17.313 | 16.5302 | 14.765 | 5.8108 | 8.1769 | 5.0426 | 5.4683 | 5.439 | 6.6207 | 7.6394 | 16.0091 | 15.5901 | 15.4443 | 14.3759 | 14.2706 | 14.205 |  |  |  | 10.7711 | 9.5032 | 9.0552 | 8.9692 | -0.075724 | -0.03291 | 12.6313 |  |  | 10.5914 |  |  | 16.9013 | 16.0965 | 15.0831 | 16.4019 | 15.6837 | 14.7889 | 10.3715 | 10.4584 | 11.3186 | 11.0473 | 9.0953 |  | 10.5722 | 8.5447 | 9.8143 | 9.2923 | 11.0491 | 11.8594 |  | 12.3004 |  |  | 11.9019 | 12.4784 | 12.5226 | [6 empty] | 12.5638 |  |  | 11.3653 |  |  | 9.1321 | 10.3883 | 11.8731 | 7.7977 | 8.9165 | 12.4963 | 7.8006 | 9.5384 | 12.2287 | 9.1912 | 10.5143 | 7.6582 | 10.3072 | 8.1152 | 10.1313 | 7.7675 | 9.505 | 12.9739 | 10.4648 | 10.0918 | 11.4143 | 8.1515 | 9.7299 | 12.5068 | 7.9183 | 10.1291 | 9.6177 | 9.8183 | 8.4876 | 10.1273 | 0.04833 | 20.952 | 0.033562 | 0.049998 | -38.1374 | 3.1205 | 6.76 | 0.37 | 0.42212 | -0.40274 | -0.20944 | -0.36084 | 0.35472 | 0.18948 | 0.72303 | 0.40844 | 0.39877 | 0.41869 | 0.43736 | 0.64099 | 0.43411 | 0.4185
42810.4354 | -399 | 18.6373 | 18.6677 | 18.6394 | 18.6646 | 18.0152 | 16.658 | 14.7244 | 16.7463 | 17.2371 | 17.334 | 17.3529 | 16.9048 | 15.9577 | 14.5806 | 15.0756 | 15.0499 | 15.5942 | 13.4352 | 13.552 | 14.1251 |  |  |  | 16.6436 | 15.9803 | 15.0972 | 10.2042 | 9.5043 | 9.7973 | 17.3305 | 16.43 | 15.231 | 16.9436 | 16.2267 | 15.2387 | 10.8182 | 11.4447 |  | 12.1931 | 10.0856 | 10.1735 | 8.4679 |  | 6.3425 | 6.3028 | 5.8366 | 5.8948 | 5.9445 | 5.9937 | 6.1334 | 4.296 | 6.4003 | 4.1732 | 6.6875 | 8.2104 | 42.7532 | 46.952 | 43.6199 | 15.2186 |  |  | 0.12573 | -0.053137 | 0.00382 | 0.10974 | 0.2111 | -0.36582 | 0.13001 | -0.050104 | -0.36953 | 0.86399 | -0.23934 | 8.8803 | 8.8815 | 2.0082 | 15.933 | 16.7689 | 17.3017 | 17.6252 | 17.6002 | 16.5851 | 14.936 | 16.9095 | 17.24 | 17.5292 | 17.581 | 17.3227 | 16.5415 | 14.7763 | 5.7988 | 8.1929 | 5.0095 | 5.4023 | 5.4039 | 6.6178 | 7.641 | 16.0074 | 15.5899 | 15.4433 | 14.3756 | 14.2639 | 14.2092 |  |  |  | 10.7783 | 9.5085 | 9.057 | 8.9661 | -0.13569 | 0.012446 | 12.6324 |  |  | 10.5916 |  |  | 16.8959 | 16.0973 | 15.0798 | 16.4023 | 15.6908 | 14.7974 | 10.3697 | 10.4579 | 11.3094 | 11.0472 | 9.0996 |  | 10.5796 | 8.5858 | 9.824 | 9.3008 | 11.0518 | 11.8225 |  | 12.305 |  |  | 11.8835 | 12.4997 | 12.535 | [6 empty] | 12.5608 |  |  | 11.3548 |  |  | 9.1438 | 10.3996 | 11.8622 | 7.8166 | 8.919 | 12.4975 | 7.8138 | 9.5471 | 12.2265 | 9.1962 | 10.5251 | 7.6785 | 10.3159 | 8.126 | 10.133 | 7.7562 | 9.5033 | 12.9739 | 10.4565 | 10.0898 | 11.4076 | 8.1519 | 9.7278 | 12.5036 | 7.9257 | 10.1224 | 9.6217 | 9.8217 | 8.4882 | 10.1268 | 0.032537 | 20.954 | 0.033906 | 0.050903 | -38.0475 | 3.1205 | -5.57 | 0.23 | 0.41566 | -0.26855 | 0.072003 | 0.38592 | 0.53496 | -0.70423 | 0.41982 | 0.40856 | 0.39795 | 0.41854 | 0.43836 | 0.64485 | 0.43397 | 0.41882
42810.4354 | -398 | 18.6349 | 18.6595 | 18.634 | 18.6588 | 18.0067 | 16.6597 | 14.7192 | 16.7517 | 17.2338 | 17.3352 | 17.3468 | 16.8989 | 15.9581 | 14.5781 | 15.0801 | 15.0411 | 15.5873 | 13.4331 | 13.5479 | 14.1253 |  |  |  | 16.6406 | 15.983 | 15.0914 | 10.1882 | 9.4953 | 9.7953 | 17.3411 | 16.4317 | 15.2341 | 16.9451 | 16.2314 | 15.2381 | 10.8167 | 11.4742 |  | 12.1862 | 10.0987 | 10.1739 | 8.4872 |  | 6.3471 | 6.2987 | 5.8205 | 5.8899 | 5.9392 | 5.9743 | 6.1216 | 4.368 | 6.3959 | 4.1457 | 6.6839 | 8.2065 | 42.734 | 46.92 | 43.624 | 15.2068 |  |  | 0.071843 | 0.046743 | -0.25508 | 0.12091 | 0.19138 | -0.016888 | 0.17141 | -0.077704 | -0.20801 | -0.22592 | -0.56521 | 8.8834 | 8.8842 | 2.0086 | 15.926 | 16.759 | 17.2892 | 17.6218 | 17.5962 | 16.5843 | 14.9321 | 16.8966 | 17.2308 | 17.5249 | 17.5594 | 17.3057 | 16.5285 | 14.7611 | 5.7782 | 8.2052 | 4.9863 | 5.3421 | 5.4325 | 6.6135 | 7.6427 | 16.0043 | 15.5858 | 15.4449 | 14.3751 | 14.2684 | 14.2133 |  |  |  | 10.7732 | 9.5009 | 9.0529 | 8.9424 | -0.17378 | 0.024867 | 12.6424 |  |  | 10.5921 |  |  | 16.897 | 16.1018 | 15.0784 | 16.3997 | 15.6834 | 14.7928 | 10.3679 | 10.4569 | 11.3088 | 11.0397 | 9.1109 |  | 10.5754 | 8.617 | 9.8209 | 9.3098 | 11.0492 | 11.7674 |  | 12.2934 |  |  | 11.8754 | 12.5166 | 12.5507 | [6 empty] | 12.5591 |  |  | 11.3386 |  |  | 9.1452 | 10.3936 | 11.8634 | 7.8197 | 8.9257 | 12.4973 | 7.8099 | 9.5348 | 12.2186 | 9.193 | 10.5106 | 7.6828 | 10.3012 | 8.1133 | 10.122 | 7.762 | 9.5181 | 12.975 | 10.4664 | 10.0945 | 11.3871 | 8.1585 | 9.728 | 12.509 | 7.9291 | 10.1231 | 9.6244 | 9.816 | 8.4898 | 10.1302 | -0.043155 | 20.9527 | 0.033895 | 0.050939 | -38.0646 | 3.1205 | 9.67 | 0.33 | 0.3142 | 0.25187 | -0.58838 | 0.40509 | 0.50935 | -0.15131 | 0.48204 | 0.40811 | 0.39698 | 0.41821 | 0.44015 | 0.64763 | 0.43339 | 0.41931
42810.4354 | -397 | 18.6345 | 18.6609 | 18.6316 | 18.6573 | 18.0109 | 16.6567 | 14.7133 | 16.7493 | 17.2375 | 17.3269 | 17.3492 | 16.8981 | 15.9586 | 14.5744 | 15.074 | 15.0326 | 15.5701 | 13.4276 | 13.5475 | 14.1173 |  |  |  | 16.6326 | 15.9804 | 15.0898 | 10.1832 | 9.4885 | 9.8015 | 17.3358 | 16.4327 | 15.2363 | 16.9514 | 16.232 | 15.2414 | 10.8144 | 11.4689 |  | 12.1795 | 10.0901 | 10.169 | 8.4933 |  | 6.346 | 6.2925 | 5.811 | 5.8723 | 5.9251 | 5.9587 | 6.109 | 4.4246 | 6.3961 | 4.1257 | 6.6836 | 8.1963 | 42.7314 | 46.8771 | 43.6128 | 15.1976 |  |  | 0.12573 | 0.004687 | -0.30371 | 0.074254 | 0.13159 | -0.4565 | 0.28246 | -0.025792 | -0.41507 | -0.34278 | -0.22027 | 8.8941 | 8.8952 | 2.0086 | 15.9338 | 16.7708 | 17.2952 | 17.6118 | 17.5987 | 16.5814 | 14.9407 | 16.8948 | 17.2423 | 17.5271 | 17.5737 | 17.321 | 16.5376 | 14.7711 | 5.7636 | 8.2227 | 4.9478 | 5.3089 | 5.4039 | 6.6123 | 7.6429 | 16.0033 | 15.5783 | 15.4362 | 14.3669 | 14.2605 | 14.2069 |  |  |  | 10.7664 | 9.4945 | 9.0464 | 8.9302 | -0.056274 | 0.11294 | 12.6479 |  |  | 10.6011 |  |  | 16.8993 | 16.1032 | 15.09 | 16.4017 | 15.6874 | 14.8021 | 10.393 | 10.4622 | 11.3152 | 11.0382 | 9.1205 |  | 10.5756 | 8.686 | 9.8232 | 9.312 | 11.0468 | 11.7007 |  | 12.2939 |  |  | 11.8485 | 12.5262 | 12.5478 | [6 empty] | 12.538 |  |  | 11.3143 |  |  | 9.1436 | 10.3962 | 11.8655 | 7.8261 | 8.9253 | 12.4934 | 7.8175 | 9.5267 | 12.207 | 9.1893 | 10.5047 | 7.6914 | 10.2957 | 8.1086 | 10.1215 | 7.7704 | 9.5329 | 12.9855 | 10.4739 | 10.1008 | 11.3851 | 8.1623 | 9.7307 | 12.5117 | 7.9429 | 10.1196 | 9.636 | 9.8187 | 8.4911 | 10.1352 | -0.32628 | 20.9514 | 0.033131 | 0.050339 | -38.167 | 3.1205 | 4.14 | 0.28 | 0.41566 | 0.079756 | -0.64201 | 0.31745 | 0.42234 | -0.78664 | 0.61877 | 0.40785 | 0.39514 | 0.41807 | 0.44163 | 0.65193 | 0.43314 | 0.41942
42810.4355 | -396 | 18.6309 | 18.6613 | 18.6304 | 18.6523 | 18.0071 | 16.6537 | 14.7029 | 16.738 | 17.2336 | 17.3229 | 17.3411 | 16.8936 | 15.9542 | 14.5649 | 15.0866 | 15.0379 | 15.5871 | 13.4405 | 13.5541 | 14.1297 |  |  |  | 16.6443 | 15.9864 | 15.0943 | 10.2 | 9.4904 | 9.8186 | 17.3325 | 16.4362 | 15.236 | 16.9476 | 16.2274 | 15.2376 | 10.8138 | 11.4585 |  | 12.1804 | 10.0877 | 10.1642 | 8.4804 |  | 6.3319 | 6.2781 | 5.7913 | 5.8503 | 5.9096 | 5.9378 | 6.0878 | 4.3607 | 6.3907 | 4.2052 | 6.6714 | 8.2056 | 42.7256 | 46.844 | 43.6176 | 15.2047 |  |  | 0.058703 | -0.1655 | -0.072404 | 0.078854 | 0.22424 | 0.18353 | 0.24435 | 0.13717 | 0.0023506 | -0.92329 | -0.42393 | 8.8948 | 8.8957 | 2.0083 | 15.9333 | 16.7733 | 17.2978 | 17.6267 | 17.5927 | 16.5865 | 14.9411 | 16.9035 | 17.2412 | 17.5332 | 17.5701 | 17.3191 | 16.5394 | 14.7726 | 5.7419 | 8.2364 | 4.9238 | 5.2788 | 5.3523 | 6.6013 | 7.6399 | 16.0137 | 15.5984 | 15.4555 | 14.3787 | 14.2752 | 14.2121 |  |  |  | 10.7738 | 9.5125 | 9.0565 | 8.9227 | -0.012918 | 0.12273 | 12.6403 |  |  | 10.5909 |  |  | 16.8972 | 16.0942 | 15.0896 | 16.404 | 15.6879 | 14.7946 | 10.3983 | 10.4597 | 11.3053 | 11.038 | 9.1222 |  | 10.5749 | 8.7498 | 9.8271 | 9.3039 | 11.0536 | 11.6746 |  | 12.2985 |  |  | 11.8289 | 12.5478 | 12.5463 | [6 empty] | 12.5454 |  |  | 11.3042 |  |  | 9.1411 | 10.3894 | 11.8568 | 7.8236 | 8.9047 | 12.4733 | 7.8114 | 9.5232 | 12.1955 | 9.1886 | 10.5134 | 7.6653 | 10.2807 | 8.1058 | 10.1156 | 7.7736 | 9.5408 | 12.9765 | 10.4768 | 10.0945 | 11.3715 | 8.1604 | 9.7277 | 12.5022 | 7.9364 | 10.1106 | 9.64 | 9.8088 | 8.4886 | 10.1368 | 0.0084622 | 20.9536 | 0.032006 | 0.050237 | -38.1483 | 3.1205 | 8.47 | 0.26 | 0.28403 | -0.47392 | -0.31346 | 0.32713 | 0.55131 | 0.49876 | 0.5755 | 0.40778 | 0.3935 | 0.41852 | 0.44276 | 0.65424 | 0.43348 | 0.41988
42810.4355 | -395 | 18.6393 | 18.6606 | 18.639 | 18.6568 | 18.0078 | 16.6534 | 14.705 | 16.7444 | 17.226 | 17.3285 | 17.3433 | 16.8988 | 15.9521 | 14.5712 | 15.0863 | 15.0436 | 15.5961 | 13.4438 | 13.5544 | 14.1321 |  |  |  | 16.6425 | 15.9871 | 15.0995 | 10.202 | 9.4861 | 9.8228 | 17.329 | 16.435 | 15.2345 | 16.9466 | 16.2294 | 15.2341 | 10.8096 | 11.4483 |  | 12.1846 | 10.0939 | 10.1623 | 8.4616 |  | 6.3316 | 6.28 | 5.7825 | 5.8356 | 5.8902 | 5.9327 | 6.0736 | 4.3135 | 6.3848 | 4.3014 | 6.6732 | 8.2054 | 42.7218 | 46.8414 | 43.6138 | 15.2184 |  |  | -0.053009 | -0.13134 | 0.043248 | 0.042054 | -0.13717 | -0.95459 | 0.15761 | 0.1858 | -0.086192 | 0.28683 | -0.29557 | 8.8919 | 8.893 | 2.0086 | 15.9236 | 16.7652 | 17.2914 | 17.6176 | 17.5836 | 16.5735 | 14.9339 | 16.8946 | 17.2307 | 17.518 | 17.5608 | 17.3139 | 16.5192 | 14.7639 | 5.7364 | 8.2183 | 4.9321 | 5.2838 | 5.375 | 6.6019 | 7.6446 | 16.0018 | 15.58 | 15.4442 | 14.3681 | 14.2611 | 14.2042 |  |  |  | 10.7591 | 9.5001 | 9.0361 | 8.9055 | -0.022237 | 0.057614 | 12.6488 |  |  | 10.6117 |  |  | 16.8984 | 16.0943 | 15.083 | 16.4115 | 15.6948 | 14.8023 | 10.4117 | 10.4721 | 11.3087 | 11.0378 | 9.1206 |  | 10.5824 | 8.8032 | 9.8211 | 9.2969 | 11.0574 | 11.6686 |  | 12.2967 |  |  | 11.8328 | 12.5551 | 12.5399 | [6 empty] | 12.5489 |  |  | 11.2928 |  |  | 9.1418 | 10.3896 | 11.8517 | 7.8112 | 8.8755 | 12.4625 | 7.8136 | 9.5317 | 12.2001 | 9.1902 | 10.5169 | 7.6284 | 10.27 | 8.1037 | 10.1159 | 7.7809 | 9.5525 | 12.971 | 10.4728 | 10.0982 | 11.3604 | 8.1619 | 9.7223 | 12.5 | 7.9345 | 10.1108 | 9.6466 | 9.8039 | 8.4903 | 10.1301 | 0.019248 | 20.9522 | 0.033734 | 0.051837 | -38.1184 | 3.1205 | 1.76 | 0.34 | -0.26991 | -0.42218 | 0.24226 | 0.2389 | -0.43119 | -1.1375 | 0.46219 | 0.40807 | 0.39181 | 0.41884 | 0.44345 | 0.65387 | 0.43387 | 0.41987
42810.4355 | -394 | 18.6476 | 18.6662 | 18.6486 | 18.6708 | 18.0226 | 16.6642 | 14.7276 | 16.7525 | 17.24 | 17.3331 | 17.3564 | 16.9073 | 15.9621 | 14.5845 | 15.0867 | 15.0476 | 15.5864 | 13.4408 | 13.5472 | 14.1279 |  |  |  | 16.6428 | 15.9859 | 15.0895 | 10.2053 | 9.475 | 9.8176 | 17.3491 | 16.44 | 15.2366 | 16.9518 | 16.2264 | 15.2468 | 10.8184 | 11.4494 |  | 12.1933 | 10.0894 | 10.1785 | 8.4595 |  | 6.3246 | 6.2679 | 5.772 | 5.8186 | 5.8681 | 5.9131 | 6.0727 | 4.2436 | 6.3805 | 4.3294 | 6.6621 | 8.2098 | 42.7183 | 46.8483 | 43.6093 | 15.2331 |  |  | 0.28672 | 0.21365 | 0.10173 | -0.019714 | 0.11713 | 0.050796 | 0.18455 | 0.28174 | -0.55927 | -0.11388 | -0.24193 | 8.8974 | 8.8985 | 2.0084 | 15.9286 | 16.7683 | 17.2972 | 17.6211 | 17.5901 | 16.5804 | 14.9372 | 16.8932 | 17.2327 | 17.5234 | 17.5658 | 17.3112 | 16.5271 | 14.7688 | 5.7482 | 8.2265 | 4.9154 | 5.3319 | 5.4462 | 6.6011 | 7.6404 | 16.0105 | 15.5811 | 15.4512 | 14.3729 | 14.2669 | 14.2106 |  |  |  | 10.7651 | 9.4974 | 9.0368 | 8.9066 | -0.049588 | 0.0092466 | 12.6568 |  |  | 10.6105 |  |  | 16.8969 | 16.0932 | 15.0879 | 16.4023 | 15.6902 | 14.8022 | 10.4263 | 10.4776 | 11.3014 | 11.041 | 9.1236 |  | 10.5757 | 8.6803 | 9.8213 | 9.2763 | 11.0566 | 11.7011 |  | 12.3061 |  |  | 11.8395 | 12.5484 | 12.5408 | [6 empty] | 12.5537 |  |  | 11.2903 |  |  | 9.1444 | 10.4021 | 11.8592 | 7.7885 | 8.8597 | 12.4598 | 7.8221 | 9.5321 | 12.1942 | 9.1947 | 10.5155 | 7.592 | 10.2671 | 8.1051 | 10.1173 | 7.7858 | 9.5615 | 12.9724 | 10.4807 | 10.1022 | 11.3548 | 8.1631 | 9.7336 | 12.4928 | 7.9368 | 10.1166 | 9.6486 | 9.7997 | 8.4962 | 10.1337 | 0.066242 | 20.9526 | 0.033986 | 0.05141 | -38.1147 | 3.1205 | -12.9 | 0.33 | 0.62772 | 0.53845 | 0.37155 | -0.16356 | 0.39843 | 0.26238 | 0.50012 | 0.40777 | 0.39523 | 0.41938 | 0.44204 | 0.65524 | 0.43422 | 0.42004
42810.4355 | -393 | 18.6482 | 18.665 | 18.6508 | 18.6739 | 18.0182 | 16.6596 | 14.723 | 16.7498 | 17.2426 | 17.3357 | 17.3558 | 16.9018 | 15.9585 | 14.5838 | 15.0916 | 15.0437 | 15.589 | 13.447 | 13.5537 | 14.1277 |  |  |  | 16.6499 | 15.9855 | 15.0909 | 10.2076 | 9.4746 | 9.8215 | 17.3408 | 16.4387 | 15.2402 | 16.9565 | 16.2358 | 15.2489 | 10.82 | 11.4641 |  | 12.1885 | 10.0861 | 10.1752 | 8.4633 |  | 6.3309 | 6.277 | 5.775 | 5.8116 | 5.8687 | 5.9119 | 6.0722 | 4.2503 | 6.39 | 4.2403 | 6.6788 | 8.2057 | 42.7162 | 46.8701 | 43.6188 | 15.2548 |  |  | 0.12244 | 0.22416 | 0.067564 | -0.010514 | -0.064892 | -0.14305 | 0.48617 | 0.30474 | -0.46255 | -0.30124 | -0.27213 | 8.8914 | 8.8926 | 2.0083 | 15.9366 | 16.767 | 17.3005 | 17.6203 | 17.5941 | 16.5839 | 14.9388 | 16.8938 | 17.2342 | 17.5257 | 17.5645 | 17.312 | 16.5292 | 14.7653 | 5.7566 | 8.2228 | 4.9668 | 5.3215 | 5.4887 | 6.6004 | 7.6399 | 16.0181 | 15.5859 | 15.4491 | 14.3781 | 14.2755 | 14.2147 |  |  |  | 10.7779 | 9.5019 | 9.045 | 8.91 | -0.033583 | -0.071303 | 12.6616 |  |  | 10.6084 |  |  | 16.9004 | 16.1077 | 15.0814 | 16.4074 | 15.693 | 14.8016 | 10.4391 | 10.4767 | 11.2992 | 11.0483 | 9.0982 |  | 10.5685 | 8.4839 | 9.8138 | 9.2667 | 11.0465 | 11.7324 |  | 12.2944 |  |  | 11.8601 | 12.5369 | 12.5342 | [6 empty] | 12.5632 |  |  | 11.2755 |  |  | 9.146 | 10.3987 | 11.8502 | 7.7361 | 8.8452 | 12.4504 | 7.8169 | 9.522 | 12.1701 | 9.1923 | 10.5141 | 7.5527 | 10.2679 | 8.1113 | 10.1196 | 7.7717 | 9.5675 | 12.9769 | 10.4916 | 10.1027 | 11.3522 | 8.1638 | 9.7337 | 12.4952 | 7.9382 | 10.1225 | 9.6449 | 9.8014 | 8.4923 | 10.1356 | 0.18045 | 20.9522 | 0.033791 | 0.04981 | -38.1599 | 3.1205 | -21.94 | 0.34 | 0.41021 | 0.55155 | 0.3028 | -0.11945 | -0.29656 | -0.44032 | 0.81173 | 0.40824 | 0.40044 | 0.41932 | 0.44102 | 0.64947 | 0.43416 | 0.42037
42810.4355 | -392 | 18.6417 | 18.6621 | 18.6382 | 18.6581 | 18.0112 | 16.6567 | 14.7142 | 16.7479 | 17.2324 | 17.3306 | 17.3487 | 16.9022 | 15.9488 | 14.5738 | 15.0922 | 15.0527 | 15.5963 | 13.4556 | 13.5651 | 14.1346 |  |  |  | 16.65 | 15.9887 | 15.0966 | 10.2024 | 9.4765 | 9.8153 | 17.342 | 16.426 | 15.2309 | 16.9484 | 16.2181 | 15.2342 | 10.8079 | 11.4329 |  | 12.1793 | 10.0761 | 10.1754 | 8.4573 |  | 6.3236 | 6.2654 | 5.7564 | 5.7958 | 5.8535 | 5.8961 | 6.0463 | 4.2578 | 6.3759 | 4.1839 | 6.6723 | 8.2103 | 42.7199 | 46.8745 | 43.612 | 15.2748 |  |  | 0.028475 | -0.034081 | 0.18847 | 0.048626 | -0.10366 | 0.24793 | 0.066268 | 0.24954 | -0.4355 | -0.69587 | -0.26358 | 8.9005 | 8.9019 | 2.0086 | 15.927 | 16.7619 | 17.2932 | 17.6082 | 17.5899 | 16.581 | 14.9307 | 16.8906 | 17.2257 | 17.513 | 17.5635 | 17.3062 | 16.5213 | 14.7598 | 5.7301 | 8.2348 | 5.014 | 5.3376 | 5.5096 | 6.587 | 7.6363 | 16.0128 | 15.5872 | 15.4505 | 14.3741 | 14.2684 | 14.2012 |  |  |  | 10.7686 | 9.4852 | 9.0353 | 8.9005 | -0.14116 | 0.021103 | 12.6593 |  |  | 10.6125 |  |  | 16.9046 | 16.1041 | 15.0884 | 16.4064 | 15.6979 | 14.8047 | 10.4502 | 10.4834 | 11.2962 | 11.0494 | 9.0905 |  | 10.5756 | 8.3699 | 9.8173 | 9.2812 | 11.0517 | 11.7798 |  | 12.2956 |  |  | 11.8594 | 12.5458 | 12.5371 | [6 empty] | 12.5699 |  |  | 11.2627 |  |  | 9.1324 | 10.3938 | 11.8476 | 7.6818 | 8.8367 | 12.4303 | 7.8233 | 9.5158 | 12.1546 | 9.1908 | 10.5107 | 7.5399 | 10.261 | 8.1177 | 10.1182 | 7.7356 | 9.5692 | 12.9746 | 10.4813 | 10.1028 | 11.3451 | 8.1607 | 9.7374 | 12.4943 | 7.9309 | 10.1215 | 9.6461 | 9.7982 | 8.4889 | 10.1286 | 0.19259 | 20.9524 | 0.033487 | 0.04913 | -38.0856 | 3.1206 | 13.17 | 0.25 | 0.19782 | -0.21505 | 0.50573 | 0.25688 | -0.37481 | 0.57966 | 0.29968 | 0.40869 | 0.40372 | 0.41909 | 0.44242 | 0.6438 | 0.43393 | 0.42032
42810.4355 | -391 | 18.6388 | 18.6603 | 18.6364 | 18.6528 | 18.0096 | 16.6495 | 14.7072 | 16.7371 | 17.2277 | 17.3285 | 17.342 | 16.8956 | 15.9521 | 14.5698 | 15.0909 | 15.0494 | 15.601 | 13.4501 | 13.565 | 14.1337 |  |  |  | 16.6497 | 15.9936 | 15.1008 | 10.2052 | 9.4777 | 9.8053 | 17.3414 | 16.4319 | 15.2379 | 16.9417 | 16.2163 | 15.2378 | 10.8132 | 11.4155 |  | 12.1803 | 10.0704 | 10.1821 | 8.4722 |  | 6.3134 | 6.2623 | 5.7522 | 5.7909 | 5.8296 | 5.879 | 6.0187 | 4.2782 | 6.3801 | 4.1056 | 6.6669 | 8.2041 | 42.6936 | 46.8558 | 43.6045 | 15.2808 |  |  | -0.038549 | -0.010425 | 0.1635 | -0.062426 | 0.013308 | 0.015968 | -0.15452 | 0.14112 | -1.2176 | -0.48712 | -0.40367 | 8.8954 | 8.8964 | 2.0083 | 15.9171 | 16.7631 | 17.2912 | 17.6146 | 17.5802 | 16.5696 | 14.931 | 16.8838 | 17.2189 | 17.5128 | 17.5569 | 17.3031 | 16.5221 | 14.7584 | 5.6956 | 8.2386 | 5.0764 | 5.3429 | 5.5283 | 6.5783 | 7.6248 | 16.0166 | 15.5984 | 15.4529 | 14.3786 | 14.2724 | 14.2082 |  |  |  | 10.7843 | 9.4834 | 9.0342 | 8.8906 | -0.040269 | 0.028443 | 12.6433 |  |  | 10.603 |  |  | 16.9023 | 16.0962 | 15.0805 | 16.3944 | 15.6797 | 14.7888 | 10.4389 | 10.4679 | 11.2963 | 11.0478 | 9.0526 |  | 10.5762 | 8.2794 | 9.8176 | 9.2939 | 11.0556 | 11.8103 |  | 12.297 |  |  | 11.8366 | 12.5583 | 12.5449 | [6 empty] | 12.5784 |  |  | 11.2773 |  |  | 9.1286 | 10.3844 | 11.8478 | 7.6501 | 8.8484 | 12.4274 | 7.829 | 9.511 | 12.1496 | 9.1957 | 10.5181 | 7.543 | 10.2662 | 8.1213 | 10.1186 | 7.708 | 9.5639 | 12.9699 | 10.4738 | 10.0955 | 11.335 | 8.1533 | 9.7282 | 12.4896 | 7.9259 | 10.1159 | 9.6423 | 9.7929 | 8.4772 | 10.1237 | 0.13288 | 20.9519 | 0.03258 | 0.048602 | -38.0662 | 3.1205 | -9.26 | 0.4 | -0.23016 | -0.11894 | 0.47103 | -0.29105 | 0.13429 | 0.1471 | -0.4576 | 0.40976 | 0.40625 | 0.41886 | 0.44524 | 0.63553 | 0.43369 | 0.42112
42810.4355 | -390 | 18.6507 | 18.6622 | 18.6448 | 18.6625 | 18.0137 | 16.6559 | 14.7138 | 16.7393 | 17.2307 | 17.3295 | 17.3452 | 16.8992 | 15.9538 | 14.575 | 15.0906 | 15.047 | 15.5972 | 13.4432 | 13.5555 | 14.1299 |  |  |  | 16.6435 | 15.9827 | 15.1 | 10.1997 | 9.4776 | 9.7896 | 17.3433 | 16.4438 | 15.2403 | 16.9467 | 16.2253 | 15.2435 | 10.8188 | 11.4066 |  | 12.1805 | 10.0714 | 10.187 | 8.4874 |  | 6.309 | 6.2597 | 5.7428 | 5.7802 | 5.8204 | 5.868 | 5.9888 | 4.288 | 6.3745 | 4.0309 | 6.6581 | 8.2017 | 42.693 | 46.8485 | 43.5872 | 15.2824 |  |  | 0.11784 | -0.20887 | 0.09976 | 0.051914 | -0.061604 | -0.066172 | 0.15958 | 0.26006 | -0.61181 | -0.83119 | -0.41479 | 8.8808 | 8.8821 | 2.0083 | 15.9305 | 16.7739 | 17.2998 | 17.6148 | 17.589 | 16.577 | 14.9318 | 16.8929 | 17.22 | 17.5177 | 17.5619 | 17.3131 | 16.5255 | 14.7626 | 5.6994 | 8.2042 | 5.0387 | 5.3739 | 5.5715 | 6.5784 | 7.6378 | 16.0102 | 15.5911 | 15.4522 | 14.3718 | 14.2639 | 14.2064 |  |  |  | 10.7812 | 9.4699 | 9.0233 | 8.8735 | -0.0583 | -0.058317 | 12.641 |  |  | 10.5731 |  |  | 16.892 | 16.0942 | 15.0797 | 16.3971 | 15.6886 | 14.7836 | 10.439 | 10.4848 | 11.2996 | 11.0469 | 9.0005 |  | 10.5582 | 8.2287 | 9.8121 | 9.2736 | 11.0475 | 11.8566 |  | 12.291 |  |  | 11.8306 | 12.5686 | 12.5288 | [6 empty] | 12.5665 |  |  | 11.2907 |  |  | 9.1301 | 10.3855 | 11.8465 | 7.6452 | 8.8781 | 12.4425 | 7.8412 | 9.5164 | 12.1503 | 9.2035 | 10.5259 | 7.5489 | 10.28 | 8.1202 | 10.1158 | 7.692 | 9.572 | 12.9611 | 10.4685 | 10.0988 | 11.3203 | 8.1517 | 9.721 | 12.4858 | 7.9269 | 10.1143 | 9.6449 | 9.7819 | 8.4807 | 10.1178 | 0.007114 | 20.9519 | 0.033418 | 0.050085 | -38.0431 | 3.1204 | 8.22 | 0.33 | 0.40241 | -0.53239 | 0.36793 | 0.26542 | -0.28893 | -0.29945 | 0.46502 | 0.41061 | 0.40748 | 0.41916 | 0.44482 | 0.64123 | 0.43345 | 0.42149
42810.4355 | -389 | 18.6523 | 18.6689 | 18.6464 | 18.6613 | 18.0215 | 16.6541 | 14.7195 | 16.7476 | 17.2288 | 17.3359 | 17.3493 | 16.9025 | 15.9592 | 14.5739 | 15.0885 | 15.04 | 15.5897 | 13.4403 | 13.5493 | 14.1206 |  |  |  | 16.6413 | 15.9755 | 15.0921 | 10.1955 | 9.4744 | 9.7571 | 17.3468 | 16.4526 | 15.2337 | 16.9523 | 16.2304 | 15.2449 | 10.8189 | 11.4103 |  | 12.1818 | 10.0855 | 10.1955 | 8.5072 |  | 6.316 | 6.2601 | 5.7469 | 5.7833 | 5.8218 | 5.8643 | 5.972 | 4.2472 | 6.3676 | 4.0188 | 6.6577 | 8.2065 | 42.6913 | 46.8507 | 43.5834 | 15.2862 |  |  | 0.10667 | -0.17865 | -0.019176 | -0.045342 | 0.15064 | 0.070508 | 0.54334 | 0.12403 | -0.3131 | -1.0462 | -0.30611 | 8.8702 | 8.8718 | 2.0086 | 15.9336 | 16.7692 | 17.3044 | 17.622 | 17.5937 | 16.5878 | 14.9406 | 16.8934 | 17.2255 | 17.5166 | 17.5658 | 17.3137 | 16.5252 | 14.7654 | 5.7068 | 8.2008 | 4.9874 | 5.3974 | 5.582 | 6.5724 | 7.6261 | 16.0147 | 15.5876 | 15.4554 | 14.3706 | 14.2696 | 14.2141 |  |  |  | 10.78 | 9.4631 | 9.0219 | 8.8729 | -0.27062 | -0.031593 | 12.6489 |  |  | 10.556 |  |  | 16.8914 | 16.0956 | 15.0868 | 16.4007 | 15.6888 | 14.8031 | 10.4438 | 10.4804 | 11.3104 | 11.0553 | 8.9791 |  | 10.5698 | 8.2326 | 9.8203 | 9.2737 | 11.0473 | 11.8902 |  | 12.2828 |  |  | 11.8062 | 12.5749 | 12.5104 | [6 empty] | 12.5602 |  |  | 11.291 |  |  | 9.1286 | 10.3773 | 11.8407 | 7.6552 | 8.8789 | 12.4325 | 7.8411 | 9.5056 | 12.1445 | 9.2041 | 10.5223 | 7.5515 | 10.2835 | 8.0998 | 10.1058 | 7.6921 | 9.5949 | 12.9757 | 10.47 | 10.1183 | 11.3188 | 8.1634 | 9.7287 | 12.4928 | 7.9422 | 10.1225 | 9.6567 | 9.7943 | 8.4902 | 10.1252 | 0.1011 | 20.9522 | 0.033642 | 0.05031 | -38.0251 | 3.1205 | 1.97 | 0.23 | 0.38284 | -0.49237 | -0.16131 | -0.24805 | 0.45181 | 0.3091 | 0.85805 | 0.41159 | 0.40764 | 0.41915 | 0.44331 | 0.64558 | 0.43291 | 0.42147
42810.4355 | -388 | 18.6383 | 18.6589 | 18.642 | 18.6608 | 18.0034 | 16.6516 | 14.7104 | 16.7355 | 17.2287 | 17.3304 | 17.339 | 16.9004 | 15.9614 | 14.5725 | 15.0941 | 15.056 | 15.6037 | 13.4511 | 13.5706 | 14.1312 |  |  |  | 16.6569 | 15.9851 | 15.1016 | 10.1906 | 9.4816 | 9.7552 | 17.3456 | 16.4434 | 15.2399 | 16.9505 | 16.2321 | 15.2375 | 10.8093 | 11.3886 |  | 12.1791 | 10.0854 | 10.204 | 8.5517 |  | 6.3174 | 6.2534 | 5.7458 | 5.7859 | 5.8244 | 5.8573 | 5.9641 | 4.225 | 6.3609 | 4.1123 | 6.6555 | 8.1977 | 42.7069 | 46.8572 | 43.5706 | 15.2821 |  |  | 0.12047 | -0.032109 | 0.10568 | 0.023658 | -0.068176 | -0.1102 | 0.40731 | 0.08986 | -0.37984 | -0.61216 | -0.58091 | 8.867 | 8.8681 | 2.0086 | 15.9363 | 16.7781 | 17.2993 | 17.6295 | 17.5944 | 16.5884 | 14.9383 | 16.8936 | 17.2337 | 17.5215 | 17.575 | 17.3173 | 16.5305 | 14.7665 | 5.6364 | 8.1761 | 4.933 | 5.4125 | 5.5886 | 6.5685 | 7.6191 | 16.0201 | 15.5883 | 15.4492 | 14.3754 | 14.2719 | 14.2058 |  |  |  | 10.7805 | 9.4574 | 9.0233 | 8.88 | -0.1517 | -0.14564 | 12.6358 |  |  | 10.5521 |  |  | 16.8898 | 16.0858 | 15.0805 | 16.3907 | 15.6833 | 14.7877 | 10.4337 | 10.4775 | 11.3094 | 11.0374 | 8.9964 |  | 10.569 | 8.2621 | 9.8248 | 9.2831 | 11.056 | 11.9215 |  | 12.2927 |  |  | 11.7727 | 12.5626 | 12.4935 | [6 empty] | 12.5409 |  |  | 11.2832 |  |  | 9.1412 | 10.3824 | 11.8469 | 7.6628 | 8.9037 | 12.4379 | 7.8438 | 9.5117 | 12.1488 | 9.2127 | 10.5241 | 7.5657 | 10.2907 | 8.1072 | 10.1083 | 7.6974 | 9.6037 | 12.9579 | 10.468 | 10.1169 | 11.3044 | 8.1618 | 9.7356 | 12.4972 | 7.9513 | 10.1375 | 9.6513 | 9.7941 | 8.4868 | 10.1171 | 0.05719 | 20.9535 | 0.034027 | 0.05091 | -38.1151 | 3.1205 | -4.2 | 0.39 | 0.40684 | -0.20874 | 0.37868 | 0.17917 | -0.30394 | -0.38643 | 0.74291 | 0.41108 | 0.40697 | 0.41917 | 0.45068 | 0.65081 | 0.43136 | 0.42129
42810.4356 | -387 | 18.6477 | 18.6717 | 18.6498 | 18.6667 | 18.0133 | 16.6609 | 14.7192 | 16.7467 | 17.238 | 17.3389 | 17.3491 | 16.9081 | 15.9564 | 14.5834 | 15.091 | 15.0408 | 15.5901 | 13.4424 | 13.5609 | 14.1255 |  |  |  | 16.6543 | 15.9833 | 15.0943 | 10.1925 | 9.4707 | 9.7269 | 17.3509 | 16.4349 | 15.2341 | 16.9462 | 16.2291 | 15.2376 | 10.8089 | 11.383 |  | 12.1783 | 10.0827 | 10.1977 | 8.583 |  | 6.3282 | 6.2809 | 5.7716 | 5.8031 | 5.833 | 5.8695 | 5.9659 | 4.2358 | 6.3683 | 4.2478 | 6.6619 | 8.2036 | 42.7196 | 46.8564 | 43.5459 | 15.2852 |  |  | -0.12266 | -0.089281 | 0.22527 | -0.095938 | 0.18613 | -0.085228 | 0.5959 | 0.02612 | -0.83171 | -0.22109 | -0.23736 | 8.8685 | 8.8698 | 2.0083 | 15.9278 | 16.768 | 17.295 | 17.627 | 17.5846 | 16.5775 | 14.9364 | 16.8903 | 17.231 | 17.5155 | 17.5631 | 17.3094 | 16.5209 | 14.7615 | 5.5836 | 8.1835 | 4.876 | 5.4354 | 5.6015 | 6.5623 | 7.6185 | 16.0181 | 15.5902 | 15.4555 | 14.3747 | 14.2692 | 14.2015 |  |  |  | 10.7816 | 9.4541 | 9.0178 | 8.8967 | -0.01231 | -0.15693 | 12.6431 |  |  | 10.5452 |  |  | 16.8923 | 16.0953 | 15.0799 | 16.3932 | 15.6874 | 14.7965 | 10.431 | 10.4829 | 11.3029 | 11.0195 | 8.992 |  | 10.571 | 8.3335 | 9.8098 | 9.2911 | 11.0569 | 11.9207 |  | 12.2936 |  |  | 11.7848 | 12.5893 | 12.5064 | [6 empty] | 12.5329 |  |  | 11.2943 |  |  | 9.1475 | 10.3819 | 11.8428 | 7.6766 | 8.9216 | 12.4391 | 7.8504 | 9.5266 | 12.1378 | 9.2046 | 10.5191 | 7.5738 | 10.2999 | 8.1055 | 10.0943 | 7.7117 | 9.6129 | 12.9695 | 10.4545 | 10.1217 | 11.2911 | 8.1569 | 9.7294 | 12.5004 | 7.9511 | 10.1447 | 9.649 | 9.7874 | 8.4796 | 10.1105 | 0.11516 | 20.9532 | 0.032684 | 0.048985 | -38.1485 | 3.1205 | 2.05 | 0.31 | -0.41051 | -0.34808 | 0.55291 | -0.36083 | 0.50222 | -0.33984 | 0.89861 | 0.41127 | 0.40449 | 0.41898 | 0.45583 | 0.65707 | 0.43047 | 0.42086
42810.4356 | -386 | 18.6423 | 18.6647 | 18.6425 | 18.6616 | 18.0033 | 16.6516 | 14.7149 | 16.7401 | 17.2343 | 17.3217 | 17.3419 | 16.9003 | 15.9574 | 14.5732 | 15.1019 | 15.0538 | 15.5984 | 13.4422 | 13.5595 | 14.1286 |  |  |  | 16.6494 | 15.9838 | 15.1021 | 10.1938 | 9.4703 | 9.7412 | 17.3392 | 16.4381 | 15.2413 | 16.9447 | 16.2276 | 15.2438 | 10.8184 | 11.3857 |  | 12.1727 | 10.1002 | 10.2158 | 8.6055 |  | 6.3143 | 6.2872 | 5.7763 | 5.7923 | 5.8223 | 5.8607 | 5.9474 | 4.2589 | 6.3609 | 4.2762 | 6.6463 | 8.2112 | 42.7283 | 46.8424 | 43.5229 | 15.2783 |  |  | 0.005475 | -0.11557 | 0.096476 | 0.026942 | 0.083616 | -0.066172 | 0.44148 | -0.11516 | -0.20548 | -0.30942 | -0.2759 | 8.871 | 8.8723 | 2.0085 | 15.93 | 16.7665 | 17.2888 | 17.6206 | 17.5804 | 16.5697 | 14.9394 | 16.8902 | 17.226 | 17.5162 | 17.5645 | 17.3049 | 16.5157 | 14.7551 | 5.6569 | 8.1874 | 4.8187 | 5.4248 | 5.6279 | 6.5673 | 7.6148 | 16.0162 | 15.595 | 15.4489 | 14.3747 | 14.2655 | 14.2062 |  |  |  | 10.785 | 9.4511 | 9.0166 | 8.912 | 0.10398 | -0.10668 | 12.6461 |  |  | 10.557 |  |  | 16.8934 | 16.09 | 15.0773 | 16.3968 | 15.6823 | 14.793 | 10.4259 | 10.4761 | 11.3047 | 10.99 | 9.0034 |  | 10.5692 | 8.4081 | 9.8117 | 9.284 | 11.0512 | 11.9145 |  | 12.2883 |  |  | 11.7822 | 12.5712 | 12.4914 | [6 empty] | 12.5234 |  |  | 11.3047 |  |  | 9.1473 | 10.3771 | 11.8453 | 7.69 | 8.9545 | 12.4547 | 7.8498 | 9.5186 | 12.1263 | 9.1995 | 10.5193 | 7.5974 | 10.3164 | 8.1138 | 10.0953 | 7.7242 | 9.6174 | 12.977 | 10.4616 | 10.1256 | 11.2918 | 8.1505 | 9.7269 | 12.5014 | 7.9664 | 10.1434 | 9.6504 | 9.7955 | 8.4997 | 10.1188 | 0.034463 | 20.9529 | 0.032161 | 0.04824 | -38.1394 | 3.1205 | 19.7 | 0.31 | 0.08673 | -0.39602 | 0.36184 | 0.19122 | 0.33661 | -0.29944 | 0.77345 | 0.4109 | 0.40248 | 0.41899 | 0.44825 | 0.663 | 0.43016 | 0.42055
42810.4356 | -385 | 18.6507 | 18.6632 | 18.6453 | 18.6581 | 18.0081 | 16.6626 | 14.7243 | 16.7513 | 17.2326 | 17.3318 | 17.3491 | 16.8958 | 15.9597 | 14.5769 | 15.0895 | 15.0468 | 15.5953 | 13.4442 | 13.5532 | 14.126 |  |  |  | 16.6473 | 15.9829 | 15.0958 | 10.1788 | 9.4703 | 9.7518 | 17.3487 | 16.4446 | 15.2405 | 16.9499 | 16.2383 | 15.2427 | 10.8164 | 11.4004 |  | 12.1711 | 10.0987 | 10.2135 | 8.6334 |  | 6.3267 | 6.2917 | 5.7979 | 5.8036 | 5.8207 | 5.8857 | 5.9441 | 4.3383 | 6.3594 | 4.297 | 6.6523 | 8.2101 | 42.7391 | 46.8337 | 43.5001 | 15.2738 |  |  | -0.029353 | -0.13331 | 0.05442 | 0.074254 | -0.075404 | -0.27842 | 0.58014 | -0.07836 | -0.32905 | 1.5192 | -0.11039 | 8.8688 | 8.8699 | 2.0084 | 15.9352 | 16.7636 | 17.2932 | 17.6228 | 17.5882 | 16.5782 | 14.937 | 16.8896 | 17.2289 | 17.5102 | 17.5605 | 17.3125 | 16.5226 | 14.7622 | 5.7388 | 8.1843 | 4.7775 | 5.3884 | 5.6495 | 6.5686 | 7.6096 | 16.0179 | 15.601 | 15.4533 | 14.3693 | 14.2658 | 14.2113 |  |  |  | 10.7801 | 9.4438 | 9.0156 | 8.9258 | 0.11918 | -0.10104 | 12.6436 |  |  | 10.5586 |  |  | 16.8921 | 16.0918 | 15.0749 | 16.3899 | 15.6768 | 14.7871 | 10.4291 | 10.4812 | 11.3037 | 10.9895 | 9.0387 |  | 10.5627 | 8.4072 | 9.8141 | 9.2745 | 11.0507 | 11.9006 |  | 12.2962 |  |  | 11.7888 | 12.5665 | 12.5133 | [6 empty] | 12.5377 |  |  | 11.3112 |  |  | 9.1546 | 10.3828 | 11.8415 | 7.6953 | 8.963 | 12.4607 | 7.8455 | 9.5209 | 12.1254 | 9.2069 | 10.5349 | 7.6076 | 10.3186 | 8.1135 | 10.0845 | 7.7348 | 9.6183 | 12.9742 | 10.4604 | 10.1227 | 11.2739 | 8.1591 | 9.7243 | 12.502 | 7.9351 | 10.1389 | 9.6508 | 9.7855 | 8.51 | 10.1127 | 0.001336 | 20.9549 | 0.03351 | 0.049796 | -38.0851 | 3.1205 | -12.29 | 0.33 | -0.20082 | -0.42534 | 0.27176 | 0.31745 | -0.31966 | -0.61425 | 0.88667 | 0.4097 | 0.40259 | 0.41924 | 0.43932 | 0.66698 | 0.42932 | 0.42
42810.4356 | -384 | 18.6524 | 18.6765 | 18.6466 | 18.6589 | 18.0128 | 16.6588 | 14.7209 | 16.7482 | 17.2384 | 17.34 | 17.3547 | 16.907 | 15.9623 | 14.5842 | 15.1016 | 15.0552 | 15.6049 | 13.4389 | 13.5535 | 14.1317 |  |  |  | 16.6488 | 15.9861 | 15.1037 | 10.1786 | 9.4692 | 9.7688 | 17.3471 | 16.4453 | 15.2395 | 16.9537 | 16.2323 | 15.2382 | 10.8157 | 11.4226 |  | 12.1711 | 10.1036 | 10.2145 | 8.6429 |  | 6.3349 | 6.3049 | 5.8045 | 5.8031 | 5.8284 | 5.9339 | 5.9665 | 4.3615 | 6.3557 | 4.3063 | 6.6507 | 8.2157 | 42.7369 | 46.8097 | 43.4808 | 15.2714 |  |  | 0.042275 | -0.063653 | 0.09516 | -0.00263 | 0.013308 | -0.099684 | 0.70959 | 0.08066 | -0.38685 | -1.315 | -0.18828 | 8.8691 | 8.8704 | 2.0084 | 15.9335 | 16.7667 | 17.2953 | 17.6286 | 17.5964 | 16.5846 | 14.9331 | 16.9041 | 17.2284 | 17.5185 | 17.5655 | 17.3141 | 16.5247 | 14.7657 | 5.7835 | 8.2062 | 4.7876 | 5.3278 | 5.6565 | 6.5675 | 7.6087 | 16.0142 | 15.5923 | 15.453 | 14.3671 | 14.2661 | 14.2092 |  |  |  | 10.7767 | 9.4347 | 9.0103 | 8.9315 | 0.045836 | -0.11722 | 12.645 |  |  | 10.5615 |  |  | 16.902 | 16.1005 | 15.0897 | 16.4033 | 15.6867 | 14.8004 | 10.4258 | 10.4857 | 11.3042 | 10.9774 | 9.067 |  | 10.5654 | 8.332 | 9.8076 | 9.2713 | 11.0527 | 11.891 |  | 12.2968 |  |  | 11.7841 | 12.5557 | 12.5203 | [6 empty] | 12.5398 |  |  | 11.3227 |  |  | 9.1468 | 10.368 | 11.8356 | 7.6966 | 8.9798 | 12.4545 | 7.8246 | 9.5181 | 12.1114 | 9.2083 | 10.5264 | 7.62 | 10.3173 | 8.1007 | 10.0787 | 7.7324 | 9.6279 | 12.9786 | 10.456 | 10.1233 | 11.2636 | 8.163 | 9.7319 | 12.504 | 7.8915 | 10.1356 | 9.6579 | 9.7893 | 8.5323 | 10.1163 | 0.067398 | 20.9535 | 0.033768 | 0.050129 | -38.0995 | 3.1205 | 11.92 | 0.29 | 0.24101 | -0.29392 | 0.35938 | -0.059745 | 0.1343 | -0.36758 | 0.9807 | 0.409 | 0.40446 | 0.41939 | 0.43422 | 0.66577 | 0.42903 | 0.41973
42810.4356 | -383 | 18.6543 | 18.675 | 18.6495 | 18.6594 | 18.0162 | 16.6596 | 14.7202 | 16.7503 | 17.2373 | 17.3389 | 17.3485 | 16.9061 | 15.9611 | 14.5873 | 15.099 | 15.0523 | 15.6024 | 13.4381 | 13.554 | 14.1239 |  |  |  | 16.6415 | 15.9804 | 15.0951 | 10.1803 | 9.4572 | 9.7606 | 17.3455 | 16.4376 | 15.2424 | 16.9535 | 16.233 | 15.2375 | 10.8098 | 11.4286 |  | 12.1695 | 10.11 | 10.2134 | 8.6536 |  | 6.3381 | 6.3032 | 5.8245 | 5.7996 | 5.8253 | 5.942 | 5.9775 | 4.3824 | 6.3517 | 4.3115 | 6.6419 | 8.1957 | 42.7237 | 46.7757 | 43.4484 | 15.2597 |  |  | -0.090461 | -0.26736 | 0.023536 | -0.062426 | -0.13586 | -0.28302 | 0.51442 | -0.036304 | -0.49077 | -0.32264 | -0.14695 | 8.8688 | 8.8699 | 2.0087 | 15.928 | 16.7649 | 17.2904 | 17.6098 | 17.5725 | 16.5742 | 14.9255 | 16.8797 | 17.2169 | 17.5101 | 17.5572 | 17.2971 | 16.5191 | 14.7483 | 5.8435 | 8.2638 | 4.8236 | 5.2881 | 5.649 | 6.563 | 7.6071 | 16.0066 | 15.5939 | 15.444 | 14.3668 | 14.2604 | 14.202 |  |  |  | 10.7797 | 9.4265 | 8.9953 | 8.9239 | 0.12384 | 0.061378 | 12.6478 |  |  | 10.5592 |  |  | 16.9002 | 16.1091 | 15.0827 | 16.399 | 15.6827 | 14.7916 | 10.407 | 10.4735 | 11.2867 | 10.9598 | 9.0549 |  | 10.5721 | 8.2906 | 9.809 | 9.2534 | 11.0521 | 11.8391 |  | 12.2852 |  |  | 11.7919 | 12.5492 | 12.5246 | [6 empty] | 12.5506 |  |  | 11.3292 |  |  | 9.1489 | 10.368 | 11.8308 | 7.7109 | 8.9901 | 12.4566 | 7.8106 | 9.5155 | 12.0963 | 9.2081 | 10.5264 | 7.6292 | 10.3238 | 8.0892 | 10.0772 | 7.7228 | 9.6339 | 12.9781 | 10.4516 | 10.1142 | 11.2529 | 8.1569 | 9.7299 | 12.5048 | 7.8387 | 10.14 | 9.6626 | 9.8092 | 8.526 | 10.1076 | -0.037954 | 20.9535 | 0.034055 | 0.050614 | -38.098 | 3.1205 | 2.04 | 0.32 | -0.35255 | -0.60238 | 0.17873 | -0.29107 | -0.42913 | -0.61937 | 0.83503 | 0.40956 | 0.40565 | 0.41987 | 0.42703 | 0.66157 | 0.42854 | 0.42004
42810.4356 | -382 | 18.6465 | 18.6753 | 18.6433 | 18.6693 | 18.0099 | 16.6509 | 14.71 | 16.7457 | 17.2352 | 17.3373 | 17.3447 | 16.8964 | 15.9534 | 14.5835 | 15.0949 | 15.0538 | 15.6005 | 13.4428 | 13.559 | 14.1248 |  |  |  | 16.6432 | 15.9874 | 15.0939 | 10.1789 | 9.4603 | 9.7485 | 17.3505 | 16.4439 | 15.2472 | 16.9566 | 16.2334 | 15.2422 | 10.8133 | 11.4427 |  | 12.1745 | 10.1202 | 10.2181 | 8.6573 |  | 6.3393 | 6.2946 | 5.8173 | 5.8005 | 5.8102 | 5.9367 | 5.9955 | 4.3762 | 6.3413 | 4.3377 | 6.6362 | 8.2069 | 42.7244 | 46.7775 | 43.424 | 15.2615 |  |  | 0.13033 | -0.23582 | 0.12999 | -0.030886 | -0.00378 | -0.002432 | 0.54136 | -0.057332 | -0.77333 | -0.38075 | -0.20397 | 8.871 | 8.8721 | 2.0083 | 15.9293 | 16.7697 | 17.2947 | 17.6171 | 17.5865 | 16.5785 | 14.9361 | 16.8857 | 17.2136 | 17.5127 | 17.5584 | 17.3107 | 16.5183 | 14.7567 | 5.9444 | 8.2715 | 4.9188 | 5.2775 | 5.609 | 6.5644 | 7.595 | 16.0126 | 15.5938 | 15.4526 | 14.3821 | 14.2655 | 14.2026 |  |  |  | 10.7865 | 9.4372 | 9.005 | 8.9288 | 0.0030878 | -0.15261 | 12.6386 |  |  | 10.5727 |  |  | 16.895 | 16.1039 | 15.0862 | 16.4005 | 15.6952 | 14.7993 | 10.4266 | 10.4773 | 11.2714 | 10.9454 | 9.0876 |  | 10.5649 | 8.3357 | 9.8089 | 9.2349 | 11.052 | 11.8018 |  | 12.2954 |  |  | 11.7786 | 12.5472 | 12.5147 | [6 empty] | 12.5347 |  |  | 11.3217 |  |  | 9.1515 | 10.3724 | 11.8294 | 7.7206 | 9.0007 | 12.4622 | 7.7959 | 9.5172 | 12.1006 | 9.205 | 10.5288 | 7.6473 | 10.3156 | 8.0666 | 10.0704 | 7.7056 | 9.6314 | 12.9818 | 10.444 | 10.1025 | 11.2315 | 8.1529 | 9.7238 | 12.5039 | 7.8029 | 10.1289 | 9.6525 | 9.7971 | 8.5097 | 10.0931 | 0.05276 | 20.9545 | 0.034337 | 0.050302 | -38.1068 | 3.1205 | -2.15 | 0.37 | 0.42316 | -0.56572 | 0.42002 | -0.20474 | -0.071578 | -0.057414 | 0.85661 | 0.40841 | 0.4044 | 0.42038 | 0.41598 | 0.64959 | 0.42855 | 0.42013
42810.4356 | -381 | 18.6414 | 18.6703 | 18.6502 | 18.6644 | 18.0068 | 16.6522 | 14.7215 | 16.7504 | 17.2333 | 17.3259 | 17.3496 | 16.8965 | 15.9524 | 14.5824 | 15.094 | 15.0473 | 15.5969 | 13.4371 | 13.5544 | 14.1234 |  |  |  | 16.6389 | 15.9812 | 15.0926 | 10.1728 | 9.4599 | 9.7288 | 17.3517 | 16.4451 | 15.2447 | 16.9564 | 16.2387 | 15.2416 | 10.8116 | 11.4532 |  | 12.1714 | 10.1382 | 10.2164 | 8.6526 |  | 6.364 | 6.3179 | 5.8274 | 5.8201 | 5.8234 | 5.9395 | 6.0214 | 4.3517 | 6.3477 | 4.3789 | 6.6383 | 8.2094 | 42.7115 | 46.7674 | 43.4104 | 15.2653 |  |  | 0.10733 | 0.040171 | 0.16744 | -0.044026 | -0.047804 | 0.20916 | 0.53479 | 0.000492 | -0.78948 | 0.057522 | -0.18768 | 8.869 | 8.8706 | 2.0085 | 15.9367 | 16.7846 | 17.3003 | 17.626 | 17.5952 | 16.5812 | 14.9422 | 16.8906 | 17.2272 | 17.5204 | 17.5656 | 17.3143 | 16.5204 | 14.7545 | 5.9981 | 8.2936 | 4.9538 | 5.2861 | 5.5648 | 6.5625 | 7.5957 | 16.0169 | 15.5936 | 15.4541 | 14.3783 | 14.2665 | 14.2056 |  |  |  | 10.7853 | 9.43 | 9.0074 | 8.9662 | 0.085951 | -0.047778 | 12.6494 |  |  | 10.5692 |  |  | 16.8932 | 16.0931 | 15.0779 | 16.3933 | 15.6815 | 14.7959 | 10.4165 | 10.4655 | 11.2576 | 10.9457 | 9.1265 |  | 10.5705 | 8.3634 | 9.8019 | 9.2171 | 11.0472 | 11.7577 |  | 12.2839 |  |  | 11.7903 | 12.567 | 12.5174 | [6 empty] | 12.5356 |  |  | 11.335 |  |  | 9.164 | 10.3749 | 11.8247 | 7.7314 | 9.0091 | 12.4681 | 7.7799 | 9.5183 | 12.1023 | 9.2081 | 10.517 | 7.6573 | 10.3136 | 8.0509 | 10.0657 | 7.6771 | 9.6207 | 12.9818 | 10.4442 | 10.102 | 11.2214 | 8.1505 | 9.7246 | 12.5098 | 7.7893 | 10.1247 | 9.655 | 9.7911 | 8.5174 | 10.0917 | -0.0042494 | 20.955 | 0.032196 | 0.047878 | -38.1433 | 3.1205 | -18.18 | 0.31 | 0.384 | 0.2335 | 0.47672 | -0.24445 | -0.25455 | 0.53245 | 0.8514 | 0.40752 | 0.4034 | 0.42072 | 0.40979 | 0.64579 | 0.42863 | 0.41905
42810.4356 | -380 | 18.6597 | 18.6706 | 18.6533 | 18.6743 | 18.0166 | 16.6644 | 14.7176 | 16.7511 | 17.2421 | 17.3387 | 17.3597 | 16.9102 | 15.9578 | 14.5826 | 15.0945 | 15.0489 | 15.5979 | 13.4353 | 13.5487 | 14.1254 |  |  |  | 16.6379 | 15.9743 | 15.0847 | 10.1656 | 9.4529 | 9.7197 | 17.3481 | 16.4492 | 15.2469 | 16.9528 | 16.2289 | 15.2459 | 10.8113 | 11.4603 |  | 12.1668 | 10.1463 | 10.2205 | 8.6135 |  | 6.3778 | 6.3341 | 5.8356 | 5.8203 | 5.8299 | 5.9415 | 6.0089 | 4.3839 | 6.3466 | 4.4014 | 6.6419 | 8.204 | 42.6913 | 46.7552 | 43.3835 | 15.2619 |  |  | -0.074033 | -0.074165 | 0.11882 | -0.068998 | 0.067188 | -0.079312 | 0.57816 | 0.042548 | -0.19517 | -1.1824 | -0.32776 | 8.8708 | 8.8719 | 2.0086 | 15.9362 | 16.774 | 17.2966 | 17.616 | 17.5863 | 16.5773 | 14.9245 | 16.8929 | 17.2204 | 17.5131 | 17.5641 | 17.3033 | 16.5254 | 14.7542 | 5.9982 | 8.3177 | 4.9698 | 5.3387 | 5.5049 | 6.5638 | 7.5885 | 16.0119 | 15.5907 | 15.4552 | 14.3731 | 14.2618 | 14.1961 |  |  |  | 10.7821 | 9.4151 | 9.0063 | 8.9937 | -0.0082578 | -0.035921 | 12.6493 |  |  | 10.578 |  |  | 16.8989 | 16.1033 | 15.0813 | 16.4004 | 15.6967 | 14.8023 | 10.4383 | 10.4653 | 11.2491 | 10.9421 | 9.1774 |  | 10.567 | 8.3947 | 9.8071 | 9.1922 | 11.0558 | 11.7163 |  | 12.296 |  |  | 11.7915 | 12.5802 | 12.5249 | [6 empty] | 12.5284 |  |  | 11.336 |  |  | 9.1731 | 10.3747 | 11.8216 | 7.7428 | 9.0119 | 12.4687 | 7.7805 | 9.5191 | 12.1033 | 9.2109 | 10.5181 | 7.6747 | 10.3131 | 8.0383 | 10.0637 | 7.6625 | 9.6298 | 12.9917 | 10.4526 | 10.0941 | 11.2187 | 8.1492 | 9.7308 | 12.5176 | 7.785 | 10.137 | 9.6586 | 9.7933 | 8.5194 | 10.0886 | 0.049101 | 20.9541 | 0.032632 | 0.047856 | -38.0733 | 3.1205 | -5.74 | 0.24 | -0.31891 | -0.31728 | 0.40159 | -0.30603 | 0.30178 | -0.32788 | 0.88525 | 0.40599 | 0.4027 | 0.42169 | 0.40993 | 0.64316 | 0.4297 | 0.41818
42810.4356 | -379 | 18.6624 | 18.6812 | 18.66 | 18.6758 | 18.0173 | 16.6637 | 14.7169 | 16.7493 | 17.2356 | 17.3372 | 17.3568 | 16.9093 | 15.9591 | 14.5849 | 15.0989 | 15.0547 | 15.5965 | 13.4348 | 13.5535 | 14.1282 |  |  |  | 16.635 | 15.9774 | 15.0866 | 10.173 | 9.453 | 9.7151 | 17.3544 | 16.4452 | 15.2471 | 16.9552 | 16.2296 | 15.2404 | 10.8214 | 11.462 |  | 12.1743 | 10.1642 | 10.2149 | 8.5731 |  | 6.384 | 6.3448 | 5.828 | 5.8176 | 5.8268 | 5.9477 | 6.0156 | 4.4764 | 6.3471 | 4.4075 | 6.6389 | 8.2121 | 42.68 | 46.7502 | 43.3845 | 15.2716 |  |  | 0.078415 | -0.10308 | 0.19242 | 0.046654 | -0.004436 | 0.00874 | 0.52428 | 0.11943 | -0.37264 | -0.073812 | -0.18112 | 8.8692 | 8.8701 | 2.0087 | 15.9348 | 16.7633 | 17.3006 | 17.61 | 17.5814 | 16.574 | 14.9264 | 16.8883 | 17.2223 | 17.5151 | 17.5594 | 17.3026 | 16.5268 | 14.7542 | 5.9576 | 8.3582 | 4.9957 | 5.3603 | 5.5157 | 6.5607 | 7.5839 | 16.0042 | 15.5819 | 15.4449 | 14.3686 | 14.2531 | 14.1939 |  |  |  | 10.7794 | 9.4137 | 8.9988 | 9.0104 | -0.072279 | -0.085042 | 12.6582 |  |  | 10.583 |  |  | 16.8968 | 16.1083 | 15.0833 | 16.405 | 15.6982 | 14.7932 | 10.443 | 10.4649 | 11.2402 | 10.9296 | 9.2025 |  | 10.5597 | 8.3864 | 9.8032 | 9.1811 | 11.0443 | 11.6632 |  | 12.2805 |  |  | 11.7688 | 12.5566 | 12.5101 | [6 empty] | 12.5162 |  |  | 11.3116 |  |  | 9.1726 | 10.3744 | 11.8077 | 7.7421 | 9.015 | 12.4636 | 7.7725 | 9.505 | 12.103 | 9.1986 | 10.5109 | 7.6865 | 10.3035 | 8.0243 | 10.06 | 7.6504 | 9.641 | 12.9925 | 10.4656 | 10.0926 | 11.2134 | 8.1477 | 9.7274 | 12.515 | 7.7868 | 10.1427 | 9.6537 | 9.7904 | 8.5164 | 10.0883 | 0.058538 | 20.9549 | 0.032919 | 0.047806 | -37.9549 | 3.1205 | -1.69 | 0.38 | 0.32821 | -0.37406 | 0.51106 | 0.25165 | -0.077543 | 0.10884 | 0.843 | 0.40505 | 0.4028 | 0.42162 | 0.41408 | 0.63976 | 0.43116 | 0.41763
42810.4357 | -378 | 18.6621 | 18.6804 | 18.6536 | 18.671 | 18.0179 | 16.6647 | 14.7223 | 16.7448 | 17.2349 | 17.3408 | 17.3578 | 16.9075 | 15.9656 | 14.5844 | 15.1027 | 15.0569 | 15.6036 | 13.4502 | 13.5644 | 14.1273 |  |  |  | 16.6469 | 15.992 | 15.0962 | 10.174 | 9.4528 | 9.7041 | 17.3673 | 16.4483 | 15.2441 | 16.9523 | 16.238 | 15.2398 | 10.8231 | 11.4487 |  | 12.1822 | 10.1734 | 10.2054 | 8.5432 |  | 6.3954 | 6.353 | 5.8242 | 5.8139 | 5.8328 | 5.965 | 6.0772 | 4.5082 | 6.3492 | 4.407 | 6.6376 | 8.2127 | 42.6743 | 46.7545 | 43.3781 | 15.2798 |  |  | 0.053447 | -0.12937 | 0.016308 | 0.17742 | -0.033348 | -0.29616 | 0.31794 | 0.17069 | -0.56374 | -0.47894 | -0.1392 | 8.869 | 8.87 | 2.0084 | 15.9317 | 16.7736 | 17.2932 | 17.6207 | 17.5807 | 16.5738 | 14.9333 | 16.8912 | 17.2244 | 17.5145 | 17.5609 | 17.3029 | 16.5207 | 14.7575 | 5.9662 | 8.3514 | 5.02 | 5.3841 | 5.5359 | 6.5601 | 7.5822 | 16.0125 | 15.5884 | 15.4486 | 14.3714 | 14.2604 | 14.203 |  |  |  | 10.7829 | 9.4285 | 8.9976 | 9.0494 | -0.13569 | -0.055118 | 12.6521 |  |  | 10.5756 |  |  | 16.8928 | 16.0928 | 15.0812 | 16.4019 | 15.6933 | 14.7876 | 10.4457 | 10.4521 | 11.2201 | 10.9271 | 9.2252 |  | 10.5666 | 8.3965 | 9.8059 | 9.178 | 11.0461 | 11.6025 |  | 12.2796 |  |  | 11.7633 | 12.5377 | 12.4987 | [6 empty] | 12.5263 |  |  | 11.3054 |  |  | 9.1766 | 10.3804 | 11.8075 | 7.7546 | 9.0237 | 12.4787 | 7.7789 | 9.5032 | 12.1126 | 9.2024 | 10.5215 | 7.7053 | 10.3191 | 8.0146 | 10.0683 | 7.652 | 9.6554 | 13.0001 | 10.4798 | 10.0969 | 11.216 | 8.1545 | 9.7302 | 12.5252 | 7.7955 | 10.1565 | 9.6547 | 9.7816 | 8.5194 | 10.0902 | -0.043732 | 20.9531 | 0.032982 | 0.048537 | -38.0127 | 3.1205 | 4.53 | 0.39 | 0.27096 | -0.41905 | 0.14879 | 0.49075 | -0.21261 | -0.63361 | 0.6565 | 0.40465 | 0.40261 | 0.42177 | 0.41305 | 0.63686 | 0.43205 | 0.41666
42810.4357 | -377 | 18.6533 | 18.6733 | 18.6411 | 18.6646 | 18.0131 | 16.6572 | 14.7098 | 16.7349 | 17.2309 | 17.33 | 17.3527 | 16.8991 | 15.9575 | 14.5746 | 15.1008 | 15.0559 | 15.6102 | 13.4558 | 13.5618 | 14.1321 |  |  |  | 16.6468 | 15.9896 | 15.0948 | 10.1666 | 9.4528 | 9.6855 | 17.3535 | 16.4493 | 15.2466 | 16.9516 | 16.2356 | 15.2351 | 10.819 | 11.4401 |  | 12.1709 | 10.1752 | 10.1993 | 8.5309 |  | 6.3943 | 6.3448 | 5.8074 | 5.8077 | 5.8223 | 5.9811 | 6.131 | 4.5171 | 6.3449 | 4.4135 | 6.6289 | 8.2136 | 42.6697 | 46.7683 | 43.3705 | 15.2977 |  |  | -0.051037 | -0.006485 | 0.07216 | 0.012486 | 0.049448 | -0.53141 | 0.075468 | 0.01692 | 0.28296 | -0.23494 | -0.23875 | 8.8652 | 8.8666 | 2.0087 | 15.9307 | 16.7709 | 17.2957 | 17.6154 | 17.5804 | 16.5778 | 14.9335 | 16.8949 | 17.2309 | 17.5123 | 17.5569 | 17.3012 | 16.5187 | 14.749 | 5.9816 | 8.3508 | 5.0607 | 5.4249 | 5.554 | 6.5602 | 7.5851 | 16.0074 | 15.585 | 15.4459 | 14.3747 | 14.2539 | 14.1946 |  |  |  | 10.7791 | 9.4271 | 8.9977 | 9.1035 | -0.13103 | -0.044014 | 12.6561 |  |  | 10.5842 |  |  | 16.8973 | 16.1021 | 15.0802 | 16.3996 | 15.6895 | 14.7925 | 10.4531 | 10.4541 | 11.2207 | 10.9224 | 9.2336 |  | 10.5622 | 8.3968 | 9.799 | 9.1595 | 11.0534 | 11.5601 |  | 12.2774 |  |  | 11.7768 | 12.5386 | 12.5078 | [6 empty] | 12.5317 |  |  | 11.2883 |  |  | 9.1796 | 10.3758 | 11.806 | 7.764 | 9.0245 | 12.4802 | 7.7878 | 9.5028 | 12.1075 | 9.1998 | 10.5256 | 7.7184 | 10.3271 | 8.0097 | 10.0737 | 7.6677 | 9.6796 | 13.0176 | 10.4981 | 10.1012 | 11.2235 | 8.155 | 9.7383 | 12.5292 | 7.8042 | 10.1775 | 9.658 | 9.7772 | 8.5172 | 10.0896 | 0.067398 | 20.9537 | 0.032035 | 0.049 | -38.0601 | 3.1205 | 2.87 | 0.3 | -0.26477 | -0.093823 | 0.31297 | 0.13019 | 0.25891 | -0.84876 | 0.31985 | 0.40427 | 0.40237 | 0.42252 | 0.41136 | 0.63268 | 0.43225 | 0.41503
42810.4357 | -376 | 18.6549 | 18.6736 | 18.6381 | 18.6656 | 18.0079 | 16.6521 | 14.7135 | 16.7425 | 17.2316 | 17.3368 | 17.3445 | 16.8982 | 15.957 | 14.5713 | 15.1114 | 15.055 | 15.606 | 13.4506 | 13.5628 | 14.1325 |  |  |  | 16.6428 | 15.9809 | 15.0958 | 10.1666 | 9.4582 | 9.6699 | 17.3515 | 16.4514 | 15.2475 | 16.9494 | 16.2352 | 15.244 | 10.8181 | 11.444 |  | 12.1701 | 10.1959 | 10.1977 | 8.5607 |  | 6.3953 | 6.3432 | 5.7993 | 5.8068 | 5.8246 | 5.9743 | 6.1311 | 4.5322 | 6.3497 | 4.4448 | 6.6353 | 8.2101 | 42.6483 | 46.7652 | 43.3712 | 15.3036 |  |  | 0.066587 | -0.11031 | 0.060992 | 0.10251 | -0.099716 | -0.25805 | 0.13395 | 0.13783 | -0.7599 | -0.49677 | -0.23537 | 8.8698 | 8.8709 | 2.0084 | 15.9378 | 16.7752 | 17.302 | 17.6311 | 17.5892 | 16.5738 | 14.9399 | 16.8995 | 17.2244 | 17.5155 | 17.5652 | 17.3133 | 16.526 | 14.7645 | 6.0579 | 8.3713 | 5.0608 | 5.4265 | 5.5858 | 6.5692 | 7.5848 | 16.0102 | 15.5874 | 15.4443 | 14.3679 | 14.254 | 14.2 |  |  |  | 10.7818 | 9.4273 | 8.9953 | 9.118 | 0.057182 | -0.056435 | 12.6536 |  |  | 10.5836 |  |  | 16.887 | 16.092 | 15.0768 | 16.3922 | 15.6789 | 14.7902 | 10.4448 | 10.4437 | 11.2075 | 10.9071 | 9.2311 |  | 10.5703 | 8.4273 | 9.8118 | 9.1593 | 11.0613 | 11.5388 |  | 12.2851 |  |  | 11.7913 | 12.5491 | 12.5204 | [6 empty] | 12.5381 |  |  | 11.2757 |  |  | 9.1742 | 10.37 | 11.7874 | 7.7702 | 9.0184 | 12.4759 | 7.7913 | 9.5011 | 12.094 | 9.1798 | 10.5149 | 7.7217 | 10.3134 | 8.0015 | 10.069 | 7.6851 | 9.6965 | 13.0201 | 10.5086 | 10.1045 | 11.226 | 8.147 | 9.7386 | 12.5273 | 7.8115 | 10.1851 | 9.6519 | 9.7709 | 8.5151 | 10.0923 | 0.0076918 | 20.9549 | 0.032293 | 0.048963 | -38.0653 | 3.1205 | 29.13 | 0.26 | 0.30242 | -0.38695 | 0.28773 | 0.37302 | -0.36766 | -0.59145 | 0.42613 | 0.40461 | 0.40195 | 0.42279 | 0.40393 | 0.63262 | 0.4314 | 0.41472
42810.4357 | -375 | 18.6555 | 18.6728 | 18.6439 | 18.6662 | 18.0111 | 16.6518 | 14.7187 | 16.752 | 17.2348 | 17.3349 | 17.3506 | 16.9006 | 15.9571 | 14.5801 | 15.1023 | 15.0542 | 15.6059 | 13.4482 | 13.5546 | 14.125 |  |  |  | 16.6491 | 15.9858 | 15.0923 | 10.1542 | 9.4537 | 9.6137 | 17.3503 | 16.4424 | 15.2432 | 16.9533 | 16.2327 | 15.24 | 10.8112 | 11.4536 |  | 12.171 | 10.2043 | 10.1906 | 8.593 |  | 6.3698 | 6.3254 | 5.7872 | 5.7931 | 5.8088 | 5.9601 | 6.1043 | 4.4848 | 6.3435 | 4.4525 | 6.6312 | 8.207 | 42.636 | 46.7599 | 43.3565 | 15.3215 |  |  | 0.051475 | -0.10768 | 0.053104 | 0.057826 | -0.85606 | -0.10034 | 0.12607 | 0.08986 | -0.35279 | 0.73685 | -0.21113 | 8.8691 | 8.8703 | 2.0084 | 15.9253 | 16.7639 | 17.2963 | 17.6214 | 17.5825 | 16.5718 | 14.9318 | 16.8851 | 17.2202 | 17.5169 | 17.5552 | 17.3047 | 16.5226 | 14.755 | 6.1828 | 8.3633 | 5.0863 | 5.405 | 5.5759 | 6.5669 | 7.5748 | 16.0161 | 15.5959 | 15.4455 | 14.3672 | 14.2632 | 14.2026 |  |  |  | 10.7839 | 9.4291 | 8.9974 | 9.1435 | 0.11918 | -0.15185 | 12.6555 |  |  | 10.5913 |  |  | 16.893 | 16.0941 | 15.0694 | 16.398 | 15.6797 | 14.7827 | 10.4434 | 10.4464 | 11.1926 | 10.9079 | 9.2231 |  | 10.5687 | 8.4454 | 9.8073 | 9.141 | 11.0623 | 11.5243 |  | 12.2841 |  |  | 11.7966 | 12.5526 | 12.5206 | [6 empty] | 12.5349 |  |  | 11.2741 |  |  | 9.1818 | 10.3661 | 11.788 | 7.7883 | 9.0166 | 12.4718 | 7.7934 | 9.4966 | 12.0905 | 9.1884 | 10.5228 | 7.73 | 10.3103 | 8.0023 | 10.0692 | 7.7047 | 9.706 | 13.0297 | 10.5085 | 10.0954 | 11.2092 | 8.1307 | 9.7313 | 12.5348 | 7.8369 | 10.1909 | 9.6541 | 9.7609 | 8.5121 | 10.0913 | 0.058538 | 20.9558 | 0.032167 | 0.048457 | -38.0812 | 3.1205 | 17.59 | 0.31 | 0.26587 | -0.3823 | 0.26847 | 0.28016 | -1.0772 | -0.3688 | 0.41339 | 0.40478 | 0.4013 | 0.42333 | 0.38978 | 0.62863 | 0.43027 | 0.41408
42810.4357 | -374 | 18.6509 | 18.6694 | 18.6438 | 18.6617 | 18.0163 | 16.6524 | 14.7139 | 16.7416 | 17.2292 | 17.3311 | 17.356 | 16.9065 | 15.9541 | 14.5667 | 15.1058 | 15.0602 | 15.61 | 13.4448 | 13.5632 | 14.1314 |  |  |  | 16.653 | 15.9848 | 15.0952 | 10.1385 | 9.4545 | 9.5697 | 17.3525 | 16.4462 | 15.2372 | 16.9544 | 16.2329 | 15.236 | 10.809 | 11.4786 |  | 12.1694 | 10.2091 | 10.1907 | 8.6035 |  | 6.3528 | 6.3113 | 5.7792 | 5.7816 | 5.7946 | 5.9492 | 6.0729 | 4.4428 | 6.3507 | 4.4698 | 6.63 | 8.2112 | 42.65 | 46.7597 | 43.3406 | 15.33 |  |  | -0.008981 | -0.11688 | 0.17993 | 0.069654 | -0.33891 | -0.5209 | 0.1241 | -0.052076 | -0.43044 | -0.47054 | -0.54633 | 8.868 | 8.8694 | 2.0087 | 15.9296 | 16.7694 | 17.2953 | 17.6129 | 17.581 | 16.5802 | 14.9334 | 16.895 | 17.2159 | 17.5145 | 17.5543 | 17.3029 | 16.5187 | 14.7599 | 6.2838 | 8.3893 | 5.1284 | 5.3763 | 5.5507 | 6.5624 | 7.5718 | 16.0177 | 15.6041 | 15.4499 | 14.3771 | 14.2661 | 14.2043 |  |  |  | 10.7845 | 9.4355 | 9.0035 | 9.183 | 0.076632 | 0.001154 | 12.656 |  |  | 10.5901 |  |  | 16.8883 | 16.093 | 15.0748 | 16.3974 | 15.6825 | 14.7809 | 10.4546 | 10.4467 | 11.1933 | 10.9076 | 9.213 |  | 10.5649 | 8.4631 | 9.8124 | 9.1304 | 11.0616 | 11.5116 |  | 12.2819 |  |  | 11.8277 | 12.5601 | 12.5238 | [6 empty] | 12.5469 |  |  | 11.2824 |  |  | 9.1829 | 10.3691 | 11.7916 | 7.7843 | 9.0183 | 12.4659 | 7.8 | 9.5003 | 12.0937 | 9.1851 | 10.527 | 7.7398 | 10.3103 | 8.0004 | 10.0769 | 7.7133 | 9.7276 | 13.0391 | 10.5087 | 10.0984 | 11.1953 | 8.1429 | 9.7291 | 12.5322 | 7.8575 | 10.2113 | 9.6515 | 9.7654 | 8.5045 | 10.0988 | 0.058538 | 20.956 | 0.031283 | 0.048283 | -38.1455 | 3.1205 | 6.51 | 0.33 | -0.11105 | -0.39828 | 0.49417 | 0.30747 | -0.67778 | -0.84028 | 0.41013 | 0.40493 | 0.40097 | 0.4236 | 0.37803 | 0.62361 | 0.42991 | 0.413
42810.4357 | -373 | 18.6552 | 18.6757 | 18.6449 | 18.6645 | 18.0171 | 16.6505 | 14.7144 | 16.7463 | 17.2281 | 17.3356 | 17.3468 | 16.897 | 15.9617 | 14.5724 | 15.1153 | 15.065 | 15.6105 | 13.4416 | 13.5639 | 14.1372 |  |  |  | 16.6535 | 15.9852 | 15.0926 | 10.1442 | 9.4453 | 9.5596 | 17.3497 | 16.4486 | 15.242 | 16.9585 | 16.2298 | 15.2426 | 10.8176 | 11.5143 |  | 12.1745 | 10.2183 | 10.1833 | 8.6112 |  | 6.3481 | 6.3149 | 5.7698 | 5.7766 | 5.7863 | 5.9386 | 6.0286 | 4.3929 | 6.3484 | 4.4989 | 6.6242 | 8.2136 | 42.6485 | 46.7699 | 43.3254 | 15.3318 |  |  | 0.049503 | -0.17733 | 0.21081 | -0.036798 | -0.098404 | -0.50907 | 0.48222 | 0.004436 | -0.26756 | -0.53139 | -0.47043 | 8.8706 | 8.8718 | 2.0085 | 15.9289 | 16.773 | 17.2908 | 17.6162 | 17.5846 | 16.5769 | 14.9304 | 16.8883 | 17.2232 | 17.5175 | 17.5627 | 17.3101 | 16.5224 | 14.7539 | 6.2997 | 8.3332 | 5.1471 | 5.3428 | 5.5212 | 6.5606 | 7.5611 | 16.0174 | 15.5886 | 15.4426 | 14.3654 | 14.2649 | 14.202 |  |  |  | 10.7747 | 9.4258 | 8.9887 | 9.1663 | 0.084533 | -0.025382 | 12.66 |  |  | 10.5997 |  |  | 16.8964 | 16.0885 | 15.0789 | 16.3955 | 15.6831 | 14.7873 | 10.4531 | 10.4447 | 11.1836 | 10.9008 | 9.2106 |  | 10.5608 | 8.4919 | 9.8099 | 9.1282 | 11.0586 | 11.4871 |  | 12.2845 |  |  | 11.8343 | 12.5775 | 12.521 | [6 empty] | 12.5422 |  |  | 11.2894 |  |  | 9.1802 | 10.3763 | 11.7792 | 7.785 | 9.0299 | 12.4616 | 7.8016 | 9.5002 | 12.0824 | 9.1704 | 10.5224 | 7.741 | 10.3084 | 7.9966 | 10.0706 | 7.7337 | 9.7386 | 13.051 | 10.5122 | 10.0971 | 11.18 | 8.1415 | 9.7267 | 12.5376 | 7.8738 | 10.224 | 9.6622 | 9.7723 | 8.4835 | 10.0977 | -0.21322 | 20.9564 | 0.032626 | 0.049289 | -38.1357 | 3.1205 | -0.4 | 0.34 | 0.26071 | -0.4906 | 0.53491 | -0.22348 | -0.36521 | -0.83067 | 0.80847 | 0.40486 | 0.40009 | 0.42357 | 0.37606 | 0.62029 | 0.42998 | 0.41314
42810.4357 | -372 | 18.6517 | 18.6816 | 18.6439 | 18.6658 | 18.0074 | 16.6544 | 14.7181 | 16.7464 | 17.2368 | 17.3366 | 17.3512 | 16.9011 | 15.9545 | 14.5749 | 15.1053 | 15.0528 | 15.6086 | 13.4471 | 13.5659 | 14.1321 |  |  |  | 16.647 | 15.9894 | 15.0993 | 10.1356 | 9.445 | 9.556 | 17.3528 | 16.4539 | 15.25 | 16.9703 | 16.2421 | 15.2502 | 10.8118 | 11.5517 |  | 12.1783 | 10.2303 | 10.1857 | 8.6118 |  | 6.3468 | 6.3166 | 5.7739 | 5.7895 | 5.7863 | 5.9314 | 6.0014 | 4.383 | 6.344 | 4.4943 | 6.6236 | 8.2128 | 42.6443 | 46.7894 | 43.3138 | 15.3299 |  |  | 0.079731 | -0.17602 | 0.15364 | -0.11762 | -0.093148 | 0.31167 | 0.4934 | -0.008708 | -0.72779 | -0.41243 | -0.14496 | 8.8676 | 8.869 | 2.0083 | 15.9326 | 16.7737 | 17.2933 | 17.6163 | 17.59 | 16.5736 | 14.9364 | 16.8932 | 17.222 | 17.5137 | 17.5604 | 17.3092 | 16.5188 | 14.7521 | 6.2295 | 8.3096 | 5.1557 | 5.3563 | 5.4599 | 6.564 | 7.5784 | 16.0145 | 15.5965 | 15.4502 | 14.3636 | 14.2599 | 14.2044 |  |  |  | 10.7797 | 9.4141 | 8.9914 | 9.1347 | 0.015852 | 0.013011 | 12.6603 |  |  | 10.6002 |  |  | 16.8991 | 16.0983 | 15.0733 | 16.3948 | 15.6789 | 14.7899 | 10.4627 | 10.4417 | 11.1651 | 10.9027 | 9.1936 |  | 10.5644 | 8.5467 | 9.8068 | 9.1352 | 11.0576 | 11.4817 |  | 12.2862 |  |  | 11.8326 | 12.5857 | 12.5284 | [6 empty] | 12.5328 |  |  | 11.2895 |  |  | 9.1774 | 10.3703 | 11.7738 | 7.7844 | 9.0295 | 12.4585 | 7.7933 | 9.4954 | 12.0875 | 9.1753 | 10.5125 | 7.7547 | 10.2873 | 8.0104 | 10.0658 | 7.7497 | 9.7474 | 13.045 | 10.5084 | 10.0902 | 11.1685 | 8.1265 | 9.7098 | 12.5288 | 7.8725 | 10.2187 | 9.6476 | 9.7617 | 8.4868 | 10.0865 | 0.020403 | 20.9565 | 0.033039 | 0.050107 | -38.1202 | 3.1205 | 7.33 | 0.34 | 0.33086 | -0.48878 | 0.45666 | -0.39955 | -0.35532 | 0.64995 | 0.81777 | 0.40545 | 0.39847 | 0.42334 | 0.38425 | 0.62134 | 0.42977 | 0.41418
42810.4357 | -371 | 18.6619 | 18.6779 | 18.6475 | 18.6668 | 18.0144 | 16.6611 | 14.7197 | 16.7543 | 17.2399 | 17.3325 | 17.352 | 16.9086 | 15.9578 | 14.5786 | 15.1104 | 15.0601 | 15.6043 | 13.4462 | 13.5656 | 14.1324 |  |  |  | 16.6445 | 15.9807 | 15.0974 | 10.1289 | 9.4368 | 9.5605 | 17.3555 | 16.4543 | 15.2495 | 16.9613 | 16.2401 | 15.2405 | 10.8138 | 11.566 |  | 12.1734 | 10.2356 | 10.177 | 8.6321 |  | 6.3503 | 6.3252 | 5.7971 | 5.8059 | 5.7879 | 5.9316 | 5.9892 | 4.4289 | 6.3431 | 4.4287 | 6.621 | 8.2104 | 42.6435 | 46.7914 | 43.2975 | 15.3232 |  |  | 0.006791 | -0.34227 | 0.069532 | 0.065054 | 0.015936 | 0.32876 | 0.65636 | -0.022504 | -0.040656 | 0.41817 | -0.53322 | 8.8688 | 8.8702 | 2.0087 | 15.937 | 16.7795 | 17.299 | 17.6231 | 17.5926 | 16.5757 | 14.9305 | 16.8888 | 17.2225 | 17.5097 | 17.5664 | 17.3114 | 16.5153 | 14.7539 | 6.1988 | 8.3212 | 5.1357 | 5.4228 | 5.4179 | 6.5587 | 7.5677 | 16.02 | 15.5955 | 15.4539 | 14.3696 | 14.2592 | 14.2024 |  |  |  | 10.7831 | 9.4126 | 8.9885 | 9.1145 | -0.060934 | 0.078128 | 12.6682 |  |  | 10.6053 |  |  | 16.8989 | 16.1032 | 15.0788 | 16.3958 | 15.6834 | 14.7944 | 10.4707 | 10.4572 | 11.1685 | 10.8929 | 9.1896 |  | 10.5632 | 8.5756 | 9.7987 | 9.1427 | 11.0511 | 11.4681 |  | 12.2726 |  |  | 11.8319 | 12.5965 | 12.5151 | [6 empty] | 12.5158 |  |  | 11.2627 |  |  | 9.1803 | 10.3654 | 11.7814 | 7.7868 | 9.037 | 12.4635 | 7.8001 | 9.5055 | 12.087 | 9.178 | 10.5099 | 7.7739 | 10.2916 | 8.0151 | 10.0707 | 7.7586 | 9.7569 | 13.0568 | 10.5095 | 10.1 | 11.1909 | 8.1336 | 9.7064 | 12.5339 | 7.8925 | 10.2236 | 9.6575 | 9.7571 | 8.4855 | 10.0926 | 0.042745 | 20.9563 | 0.033303 | 0.049883 | -37.9658 | 3.1205 | -2.55 | 0.32 | 0.096562 | -0.68159 | 0.30721 | 0.29715 | 0.14697 | 0.66753 | 0.9432 | 0.40552 | 0.3974 | 0.42291 | 0.38705 | 0.62232 | 0.42927 | 0.41486
42810.4358 | -370 | 18.6657 | 18.6807 | 18.6549 | 18.6693 | 18.0191 | 16.6584 | 14.7257 | 16.7526 | 17.2455 | 17.3402 | 17.3513 | 16.9101 | 15.9559 | 14.5752 | 15.1053 | 15.064 | 15.6035 | 13.4543 | 13.5675 | 14.1277 |  |  |  | 16.6425 | 15.9818 | 15.0942 | 10.1286 | 9.4346 | 9.576 | 17.355 | 16.4523 | 15.2411 | 16.9612 | 16.2313 | 15.2394 | 10.809 | 11.5664 |  | 12.163 | 10.2362 | 10.166 | 8.6484 |  | 6.3488 | 6.3289 | 5.8091 | 5.8208 | 5.7847 | 5.936 | 5.9877 | 4.5073 | 6.3401 | 4.3772 | 6.6128 | 8.2046 | 42.6397 | 46.7791 | 43.2891 | 15.3189 |  |  | 0.091559 | -0.14973 | 0.20621 | -0.040742 | -0.14703 | 0.10402 | 0.55254 | -0.24198 | -0.74705 | -0.10151 | -0.19682 | 8.8698 | 8.871 | 2.0086 | 15.9258 | 16.7682 | 17.2869 | 17.611 | 17.5789 | 16.5695 | 14.9169 | 16.8814 | 17.2214 | 17.4996 | 17.5499 | 17.2986 | 16.5141 | 14.7475 | 6.1747 | 8.3135 | 5.1105 | 5.4473 | 5.5059 | 6.5576 | 7.5674 | 16.0217 | 15.598 | 15.4511 | 14.3727 | 14.2569 | 14.2036 |  |  |  | 10.7769 | 9.4101 | 8.9867 | 9.087 | 0.17874 | -0.0093852 | 12.6616 |  |  | 10.6135 |  |  | 16.8944 | 16.0995 | 15.0802 | 16.4021 | 15.6816 | 14.7971 | 10.4814 | 10.4453 | 11.1639 | 10.8907 | 9.2191 |  | 10.5589 | 8.6276 | 9.8134 | 9.1661 | 11.0539 | 11.4472 |  | 12.28 |  |  | 11.8451 | 12.6093 | 12.5335 | [6 empty] | 12.531 |  |  | 11.265 |  |  | 9.1753 | 10.374 | 11.7706 | 7.8034 | 9.0331 | 12.456 | 7.8008 | 9.5049 | 12.078 | 9.1702 | 10.5084 | 7.7799 | 10.2861 | 8.0208 | 10.0793 | 7.764 | 9.7715 | 13.0567 | 10.5102 | 10.1102 | 11.1911 | 8.1419 | 9.7042 | 12.5391 | 7.9065 | 10.2393 | 9.6611 | 9.7515 | 8.4909 | 10.0965 | 0.14617 | 20.9561 | 0.033619 | 0.050737 | -37.9638 | 3.1205 | 0.32 | 0.35 | 0.35457 | -0.45082 | 0.52905 | -0.23516 | -0.44641 | 0.37549 | 0.8654 | 0.40456 | 0.39644 | 0.42236 | 0.38959 | 0.62508 | 0.42866 | 0.41542
42810.4358 | -369 | 18.6609 | 18.6764 | 18.6543 | 18.668 | 18.012 | 16.6533 | 14.7179 | 16.7518 | 17.2344 | 17.3343 | 17.349 | 16.9 | 15.9595 | 14.5731 | 15.1069 | 15.0606 | 15.6083 | 13.4447 | 13.5642 | 14.1285 |  |  |  | 16.6435 | 15.9811 | 15.0879 | 10.1237 | 9.4352 | 9.5923 | 17.3554 | 16.4522 | 15.2444 | 16.9542 | 16.237 | 15.2412 | 10.8115 | 11.5709 |  | 12.1659 | 10.2398 | 10.1769 | 8.6797 |  | 6.352 | 6.3401 | 5.8324 | 5.8431 | 5.8097 | 5.985 | 5.9877 | 4.5689 | 6.3416 | 4.346 | 6.6177 | 8.2139 | 42.6393 | 46.7735 | 43.2866 | 15.3181 |  |  | 0.046219 | -0.084681 | 0.093188 | -0.11631 | -0.014948 | -0.32573 | 0.64388 | -0.12962 | -0.49699 | 0.34285 | -0.26875 | 8.8675 | 8.8687 | 2.0083 | 15.9352 | 16.7723 | 17.3046 | 17.6184 | 17.5844 | 16.5685 | 14.9242 | 16.8829 | 17.2244 | 17.5108 | 17.5606 | 17.295 | 16.5138 | 14.7508 | 6.2354 | 8.3096 | 5.0824 | 5.4072 | 5.594 | 6.5641 | 7.5673 | 16.02 | 15.605 | 15.4552 | 14.3785 | 14.2621 | 14.207 |  |  |  | 10.7793 | 9.3957 | 8.9878 | 9.0509 | 0.065083 | -0.10104 | 12.6563 |  |  | 10.6104 |  |  | 16.8822 | 16.0922 | 15.0724 | 16.3878 | 15.6738 | 14.7808 | 10.4726 | 10.4403 | 11.1505 | 10.8824 | 9.2147 |  | 10.5657 | 8.6806 | 9.8111 | 9.1798 | 11.0511 | 11.4059 |  | 12.2759 |  |  | 11.8196 | 12.609 | 12.5323 | [6 empty] | 12.5198 |  |  | 11.2619 |  |  | 9.1778 | 10.3736 | 11.7722 | 7.8133 | 9.0403 | 12.4536 | 7.8033 | 9.509 | 12.0826 | 9.1735 | 10.501 | 7.7815 | 10.2854 | 8.0267 | 10.0884 | 7.7714 | 9.781 | 13.0547 | 10.5045 | 10.1184 | 11.195 | 8.1395 | 9.7025 | 12.5352 | 7.9163 | 10.2468 | 9.667 | 9.7424 | 8.4875 | 10.1053 | -0.095157 | 20.9558 | 0.033981 | 0.050418 | -37.9554 | 3.1205 | 6.04 | 0.27 | 0.25193 | -0.33903 | 0.35566 | -0.39734 | -0.14235 | -0.66451 | 0.93428 | 0.40491 | 0.39489 | 0.42188 | 0.38361 | 0.6282 | 0.42787 | 0.4165
42810.4358 | -368 | 18.6544 | 18.6734 | 18.6457 | 18.6676 | 18.0082 | 16.6518 | 14.7118 | 16.7428 | 17.2308 | 17.3337 | 17.3449 | 16.8937 | 15.951 | 14.5724 | 15.1043 | 15.0569 | 15.6036 | 13.4548 | 13.5563 | 14.1319 |  |  |  | 16.6478 | 15.9836 | 15.0895 | 10.1257 | 9.4349 | 9.6133 | 17.3563 | 16.4504 | 15.244 | 16.9598 | 16.2422 | 15.2424 | 10.8165 | 11.6099 |  | 12.1694 | 10.2526 | 10.1792 | 8.7035 |  | 6.3503 | 6.3394 | 5.8493 | 5.8633 | 5.8251 | 6.0403 | 6.0463 | 4.6417 | 6.3429 | 4.3461 | 6.6192 | 8.2134 | 42.6234 | 46.7484 | 43.2709 | 15.3098 |  |  | 0.008103 | -0.058397 | 0.016964 | 0.22013 | 0.015276 | 0.15856 | 0.59722 | -0.20781 | -0.74842 | -0.30942 | -0.19603 | 8.8694 | 8.8704 | 2.0086 | 15.928 | 16.7698 | 17.2927 | 17.6173 | 17.5815 | 16.567 | 14.9231 | 16.877 | 17.2181 | 17.507 | 17.5538 | 17.2979 | 16.5107 | 14.7493 | 6.3496 | 8.3489 | 5.0741 | 5.3686 | 5.5848 | 6.5627 | 7.5696 | 16.02 | 15.5971 | 15.4507 | 14.3685 | 14.2625 | 14.198 |  |  |  | 10.7745 | 9.3936 | 8.9857 | 9.01 | 0.051914 | -0.07375 | 12.6688 |  |  | 10.6126 |  |  | 16.893 | 16.0899 | 15.0755 | 16.4012 | 15.6835 | 14.7821 | 10.4787 | 10.4546 | 11.146 | 10.8885 | 9.2165 |  | 10.5716 | 8.7411 | 9.8213 | 9.2106 | 11.0548 | 11.4202 |  | 12.2848 |  |  | 11.8078 | 12.6186 | 12.5459 | [6 empty] | 12.5149 |  |  | 11.288 |  |  | 9.1712 | 10.3746 | 11.7718 | 7.8149 | 9.0363 | 12.4571 | 7.8158 | 9.5107 | 12.1006 | 9.1709 | 10.4868 | 7.7836 | 10.2803 | 8.0249 | 10.0841 | 7.7798 | 9.7888 | 13.0589 | 10.4996 | 10.1242 | 11.201 | 8.1378 | 9.6948 | 12.5359 | 7.9249 | 10.2414 | 9.6679 | 9.7371 | 8.4864 | 10.0952 | -0.27928 | 20.956 | 0.03386 | 0.049933 | -38.0027 | 3.1204 | 11.57 | 0.44 | 0.10549 | -0.28154 | 0.15174 | 0.54663 | 0.14392 | 0.46368 | 0.89988 | 0.40506 | 0.39355 | 0.42115 | 0.37077 | 0.62939 | 0.42737 | 0.41748
42810.4358 | -367 | 18.6532 | 18.6748 | 18.649 | 18.6624 | 18.0117 | 16.6524 | 14.7186 | 16.75 | 17.2365 | 17.3379 | 17.3531 | 16.8958 | 15.9508 | 14.5696 | 15.1095 | 15.0605 | 15.605 | 13.4574 | 13.5546 | 14.1374 |  |  |  | 16.6519 | 15.9851 | 15.0927 | 10.1224 | 9.4322 | 9.6346 | 17.3641 | 16.4598 | 15.2478 | 16.9597 | 16.2481 | 15.2488 | 10.8241 | 11.6468 |  | 12.1754 | 10.2741 | 10.1835 | 8.7083 |  | 6.35 | 6.3398 | 5.8563 | 5.8841 | 5.8402 | 6.0914 | 6.1097 | 4.6689 | 6.3381 | 4.3627 | 6.6124 | 8.2065 | 42.6149 | 46.7305 | 43.2473 | 15.2951 |  |  | -0.023437 | -0.068909 | -0.046776 | 0.25299 | -0.011664 | 0.080364 | 0.56896 | -0.17036 | 0.1413 | -0.45124 | -0.3218 | 8.8691 | 8.8706 | 2.0086 | 15.931 | 16.776 | 17.2941 | 17.6131 | 17.5835 | 16.5747 | 14.921 | 16.882 | 17.2207 | 17.5114 | 17.5593 | 17.3003 | 16.5115 | 14.7468 | 6.3802 | 8.3694 | 5.0768 | 5.3415 | 5.5184 | 6.5573 | 7.5524 | 16.0166 | 15.5979 | 15.4525 | 14.3722 | 14.2568 | 14.1994 |  |  |  | 10.7825 | 9.3878 | 8.9865 | 8.9848 | 0.19394 | 0.063825 | 12.668 |  |  | 10.6231 |  |  | 16.8954 | 16.0993 | 15.0691 | 16.4008 | 15.6804 | 14.7853 | 10.4899 | 10.4459 | 11.1407 | 10.8861 | 9.217 |  | 10.5597 | 8.8198 | 9.8187 | 9.228 | 11.0554 | 11.4863 |  | 12.2798 |  |  | 11.7748 | 12.6228 | 12.5406 | [6 empty] | 12.5127 |  |  | 11.3115 |  |  | 9.1818 | 10.3754 | 11.7676 | 7.8273 | 9.0453 | 12.4646 | 7.8289 | 9.515 | 12.1225 | 9.1664 | 10.4768 | 7.7934 | 10.288 | 8.0358 | 10.0902 | 7.7958 | 9.7979 | 13.0642 | 10.5024 | 10.134 | 11.2127 | 8.1391 | 9.6955 | 12.5394 | 7.9415 | 10.2546 | 9.6713 | 9.7473 | 8.4978 | 10.088 | 0.082035 | 20.9563 | 0.033424 | 0.048522 | -37.9995 | 3.1205 | 4.34 | 0.37 | -0.17941 | -0.30584 | -0.25198 | 0.58601 | -0.12577 | 0.33013 | 0.87841 | 0.40465 | 0.39127 | 0.42068 | 0.36673 | 0.62709 | 0.42749 | 0.41844
42810.4358 | -366 | 18.6553 | 18.6782 | 18.6526 | 18.6702 | 18.0123 | 16.6665 | 14.7234 | 16.7531 | 17.2454 | 17.3379 | 17.3514 | 16.9076 | 15.9574 | 14.5759 | 15.1066 | 15.0586 | 15.6058 | 13.4488 | 13.5549 | 14.1295 |  |  |  | 16.6472 | 15.9773 | 15.0944 | 10.1135 | 9.4275 | 9.6264 | 17.3623 | 16.4617 | 15.2406 | 16.9639 | 16.2436 | 15.2471 | 10.8195 | 11.6722 |  | 12.1757 | 10.2818 | 10.1891 | 8.711 |  | 6.3523 | 6.348 | 5.8648 | 5.8904 | 5.8648 | 6.1278 | 6.1667 | 4.7166 | 6.3396 | 4.419 | 6.6201 | 8.2065 | 42.6053 | 46.7233 | 43.2272 | 15.2946 |  |  | 0.029131 | 0.065143 | -0.040864 | 0.21028 | -0.13389 | -0.016888 | 0.54465 | -0.14539 | -0.7023 | -0.30061 | -0.30928 | 8.8688 | 8.8699 | 2.0085 | 15.9279 | 16.7732 | 17.2904 | 17.6182 | 17.5869 | 16.5699 | 14.9234 | 16.8818 | 17.2201 | 17.5141 | 17.5549 | 17.2972 | 16.5073 | 14.7453 | 6.3683 | 8.4002 | 5.0869 | 5.3574 | 5.4803 | 6.5615 | 7.5608 | 16.0194 | 15.6051 | 15.4519 | 14.3815 | 14.2688 | 14.21 |  |  |  | 10.7797 | 9.3894 | 8.9903 | 8.9718 | 0.17874 | 0.29512 | 12.6717 |  |  | 10.6126 |  |  | 16.8917 | 16.0897 | 15.0702 | 16.408 | 15.6759 | 14.7848 | 10.4839 | 10.4461 | 11.14 | 10.8905 | 9.2195 |  | 10.5618 | 8.8786 | 9.8116 | 9.2306 | 11.0548 | 11.5332 |  | 12.2777 |  |  | 11.7611 | 12.6193 | 12.5366 | [6 empty] | 12.5232 |  |  | 11.3042 |  |  | 9.186 | 10.3684 | 11.7645 | 7.8277 | 9.0418 | 12.4607 | 7.8382 | 9.5136 | 12.1314 | 9.1603 | 10.4669 | 7.799 | 10.2832 | 8.0398 | 10.0876 | 7.8065 | 9.8061 | 13.0695 | 10.5052 | 10.1325 | 11.214 | 8.1398 | 9.6987 | 12.5401 | 7.9479 | 10.2587 | 9.6798 | 9.7537 | 8.502 | 10.0933 | -0.0017456 | 20.9558 | 0.032253 | 0.047863 | -38.0501 | 3.1204 | -2.45 | 0.36 | 0.20002 | 0.29737 | -0.23552 | 0.53426 | -0.42614 | -0.15135 | 0.8595 | 0.40465 | 0.38941 | 0.42059 | 0.36854 | 0.62694 | 0.42727 | 0.41871
42810.4358 | -365 | 18.6495 | 18.6722 | 18.6443 | 18.6618 | 18.0056 | 16.6482 | 14.7149 | 16.7346 | 17.2339 | 17.3276 | 17.3448 | 16.8943 | 15.9432 | 14.5613 | 15.1085 | 15.0571 | 15.6035 | 13.4487 | 13.5603 | 14.134 |  |  |  | 16.6469 | 15.9775 | 15.0957 | 10.1156 | 9.4313 | 9.6233 | 17.3554 | 16.4566 | 15.2409 | 16.9607 | 16.2469 | 15.2538 | 10.8165 | 11.6865 |  | 12.1739 | 10.2907 | 10.1861 | 8.7331 |  | 6.3533 | 6.3531 | 5.8736 | 5.8928 | 5.8626 | 6.1576 | 6.1947 | 4.7961 | 6.3426 | 4.4662 | 6.6137 | 8.2148 | 42.5863 | 46.7101 | 43.2145 | 15.2885 |  |  | 0.000219 | -0.17011 | 0.047192 | -0.02957 | -0.087232 | 0.025824 | 0.60642 | -0.14276 | -0.46625 | 0.54678 | -0.34922 | 8.8696 | 8.8707 | 2.0084 | 15.931 | 16.7729 | 17.2911 | 17.6157 | 17.5836 | 16.5688 | 14.9261 | 16.8832 | 17.2175 | 17.5114 | 17.5554 | 17.3053 | 16.5132 | 14.7427 | 6.3551 | 8.4097 | 5.0885 | 5.3795 | 5.4837 | 6.5578 | 7.5637 | 16.0155 | 15.5984 | 15.4496 | 14.38 | 14.2696 | 14.2013 |  |  |  | 10.773 | 9.3769 | 8.9832 | 8.9548 | 0.093853 | 0.27291 | 12.6867 |  |  | 10.6264 |  |  | 16.895 | 16.0953 | 15.0743 | 16.4065 | 15.6886 | 14.7902 | 10.4844 | 10.4546 | 11.1458 | 10.8948 | 9.2129 |  | 10.5637 | 8.9242 | 9.8134 | 9.2413 | 11.0514 | 11.5479 |  | 12.2743 |  |  | 11.7763 | 12.629 | 12.5404 | [6 empty] | 12.538 |  |  | 11.2982 |  |  | 9.199 | 10.3742 | 11.7659 | 7.8388 | 9.0528 | 12.4595 | 7.8538 | 9.5207 | 12.1436 | 9.168 | 10.4693 | 7.8077 | 10.2885 | 8.0521 | 10.0954 | 7.8254 | 9.8135 | 13.0678 | 10.5128 | 10.1418 | 11.2219 | 8.1335 | 9.7014 | 12.5431 | 7.9618 | 10.2781 | 9.6886 | 9.7642 | 8.5047 | 10.0942 | -0.11615 | 20.9559 | 0.032414 | 0.047379 | -38.0819 | 3.1204 | 7.63 | 0.29 | 0.017342 | -0.48053 | 0.2531 | -0.20035 | -0.34399 | 0.18716 | 0.90697 | 0.40489 | 0.3882 | 0.42018 | 0.36958 | 0.62709 | 0.42655 | 0.41896
42810.4358 | -364 | 18.6556 | 18.6755 | 18.6518 | 18.6665 | 18.0122 | 16.6605 | 14.7217 | 16.7452 | 17.2378 | 17.3322 | 17.3559 | 16.9032 | 15.9585 | 14.5701 | 15.1134 | 15.0589 | 15.6068 | 13.4467 | 13.5627 | 14.1361 |  |  |  | 16.6463 | 15.9838 | 15.0959 | 10.115 | 9.4392 | 9.6383 | 17.3587 | 16.4567 | 15.2384 | 16.956 | 16.2343 | 15.2375 | 10.8094 | 11.6988 |  | 12.1731 | 10.2861 | 10.1844 | 8.7576 |  | 6.3592 | 6.3651 | 5.8767 | 5.8963 | 5.8873 | 6.1801 | 6.2202 | 4.9215 | 6.3466 | 4.5607 | 6.617 | 8.2102 | 42.5734 | 46.6985 | 43.1862 | 15.2787 |  |  | 0.015991 | -0.062997 | 0.25747 | -0.040082 | -0.07146 | -0.29288 | 0.62613 | -0.077704 | -0.47208 | -0.6109 | -0.33094 | 8.8662 | 8.8673 | 2.0084 | 15.9245 | 16.7683 | 17.2949 | 17.6134 | 17.5771 | 16.5661 | 14.9221 | 16.8803 | 17.2118 | 17.5047 | 17.5488 | 17.2995 | 16.5036 | 14.7409 | 6.3285 | 8.4052 | 5.0639 | 5.4019 | 5.4929 | 6.5589 | 7.5576 | 16.02 | 15.6129 | 15.4598 | 14.3799 | 14.262 | 14.2124 |  |  |  | 10.7855 | 9.385 | 8.9978 | 8.9553 | 0.099931 | 0.12518 | 12.6867 |  |  | 10.6272 |  |  | 16.8941 | 16.0886 | 15.0727 | 16.3966 | 15.6836 | 14.7896 | 10.4814 | 10.4547 | 11.1468 | 10.8992 | 9.2118 |  | 10.5652 | 8.9438 | 9.813 | 9.2547 | 11.0482 | 11.5444 |  | 12.2675 |  |  | 11.7672 | 12.6317 | 12.545 | [6 empty] | 12.5376 |  |  | 11.3071 |  |  | 9.2004 | 10.3807 | 11.7639 | 7.8431 | 9.0609 | 12.4485 | 7.8552 | 9.5217 | 12.1603 | 9.1688 | 10.4605 | 7.8153 | 10.2878 | 8.0527 | 10.0926 | 7.8367 | 9.8165 | 13.0594 | 10.5158 | 10.1379 | 11.2164 | 8.1234 | 9.7064 | 12.543 | 7.9749 | 10.2719 | 9.6836 | 9.76 | 8.506 | 10.0932 | 0.016551 | 20.9561 | 0.033493 | 0.046771 | -38.0064 | 3.1204 | -8.13 | 0.23 | 0.1482 | -0.29244 | 0.5912 | -0.23326 | -0.31136 | -0.63033 | 0.92163 | 0.40497 | 0.38764 | 0.41971 | 0.37266 | 0.62913 | 0.42564 | 0.41936
42810.4358 | -363 | 18.656 | 18.6838 | 18.6473 | 18.6658 | 18.0075 | 16.6507 | 14.7179 | 16.7447 | 17.2353 | 17.335 | 17.3426 | 16.8948 | 15.9515 | 14.5656 | 15.1016 | 15.0557 | 15.6035 | 13.4429 | 13.5616 | 14.1317 |  |  |  | 16.6405 | 15.9844 | 15.0936 | 10.1125 | 9.4402 | 9.6522 | 17.3578 | 16.4539 | 15.24 | 16.9606 | 16.2398 | 15.2388 | 10.8227 | 11.7238 |  | 12.1694 | 10.3001 | 10.2072 | 8.7904 |  | 6.3661 | 6.3743 | 5.8783 | 5.9094 | 5.8866 | 6.173 | 6.2172 | 4.976 | 6.3416 | 4.6312 | 6.6137 | 8.2008 | 42.5592 | 46.7129 | 43.166 | 15.2692 |  |  | -0.092433 | -0.28839 | -0.034948 | -0.10054 | -0.059632 | -0.067484 | 0.51114 | -0.1053 | -0.26951 | -0.6537 | -0.27332 | 8.8691 | 8.8704 | 2.0084 | 15.9263 | 16.7738 | 17.2934 | 17.6158 | 17.5795 | 16.5673 | 14.9142 | 16.8832 | 17.2153 | 17.5058 | 17.5485 | 17.2995 | 16.5085 | 14.7455 | 6.3456 | 8.4407 | 5.0656 | 5.4231 | 5.5227 | 6.5607 | 7.5723 | 16.0099 | 15.5986 | 15.4545 | 14.3729 | 14.2608 | 14.2033 |  |  |  | 10.7711 | 9.3648 | 8.9815 | 8.9402 | 0.20062 | 0.078692 | 12.6784 |  |  | 10.6217 |  |  | 16.8868 | 16.0918 | 15.0696 | 16.3945 | 15.6827 | 14.7881 | 10.4682 | 10.4567 | 11.1415 | 10.9052 | 9.2099 |  | 10.5602 | 8.9426 | 9.8125 | 9.2372 | 11.056 | 11.5344 |  | 12.2649 |  |  | 11.7651 | 12.6311 | 12.5487 | [6 empty] | 12.5204 |  |  | 11.3188 |  |  | 9.1993 | 10.3877 | 11.7585 | 7.8456 | 9.0709 | 12.4397 | 7.8652 | 9.5248 | 12.1677 | 9.167 | 10.4631 | 7.8171 | 10.2793 | 8.0619 | 10.0981 | 7.847 | 9.8152 | 13.0564 | 10.5116 | 10.1334 | 11.1932 | 8.1228 | 9.7101 | 12.5433 | 7.9785 | 10.2675 | 9.6835 | 9.7557 | 8.4916 | 10.0858 | 0.029263 | 20.9551 | 0.033877 | 0.047683 | -38.0213 | 3.1204 | 16.85 | 0.29 | -0.35631 | -0.6257 | -0.21782 | -0.36944 | -0.28442 | -0.30257 | 0.8327 | 0.40486 | 0.38766 | 0.42045 | 0.37097 | 0.63064 | 0.42517 | 0.41931
42810.4358 | -362 | 18.6577 | 18.6875 | 18.6515 | 18.6656 | 18.0058 | 16.6566 | 14.7118 | 16.7467 | 17.2361 | 17.3369 | 17.3495 | 16.901 | 15.9522 | 14.5656 | 15.1009 | 15.0642 | 15.6108 | 13.446 | 13.5658 | 14.1304 |  |  |  | 16.6472 | 15.981 | 15.0923 | 10.1116 | 9.4388 | 9.6721 | 17.36 | 16.4559 | 15.2446 | 16.9655 | 16.2457 | 15.2444 | 10.8241 | 11.7452 |  | 12.1698 | 10.308 | 10.2244 | 8.8183 |  | 6.3659 | 6.3891 | 5.89 | 5.9469 | 5.8972 | 6.179 | 6.2092 | 5.0239 | 6.3434 | 4.6467 | 6.6116 | 8.2126 | 42.5555 | 46.7198 | 43.1561 | 15.2734 |  |  | 0.077103 | -0.18719 | 0.083332 | -0.12551 | -0.22983 | -0.09114 | 0.52888 | 0.005092 | -0.14379 | -0.59013 | -0.25703 | 8.8676 | 8.8688 | 2.0084 | 15.9249 | 16.7646 | 17.2979 | 17.6167 | 17.5837 | 16.5705 | 14.9312 | 16.8876 | 17.2131 | 17.5125 | 17.5543 | 17.297 | 16.5154 | 14.7462 | 6.3239 | 8.4663 | 5.0676 | 5.4208 | 5.5426 | 6.5614 | 7.5684 | 16.0192 | 15.6076 | 15.4538 | 14.3805 | 14.2676 | 14.21 |  |  |  | 10.774 | 9.3747 | 8.9916 | 8.9692 | 0.18401 | 0.16621 | 12.6774 |  |  | 10.6299 |  |  | 16.8929 | 16.094 | 15.0723 | 16.4043 | 15.6881 | 14.7941 | 10.4692 | 10.4656 | 11.1454 | 10.9142 | 9.2008 |  | 10.5583 | 8.925 | 9.8132 | 9.2333 | 11.0531 | 11.5036 |  | 12.2694 |  |  | 11.7746 | 12.6153 | 12.5464 | [6 empty] | 12.5186 |  |  | 11.3143 |  |  | 9.202 | 10.3801 | 11.7553 | 7.8555 | 9.0888 | 12.434 | 7.8752 | 9.5265 | 12.1798 | 9.1717 | 10.456 | 7.8143 | 10.2767 | 8.069 | 10.095 | 7.8651 | 9.8171 | 13.057 | 10.5128 | 10.1394 | 11.1873 | 8.1221 | 9.7181 | 12.5503 | 7.9915 | 10.2779 | 9.6895 | 9.7686 | 8.4891 | 10.0885 | 0.18488 | 20.9561 | 0.034124 | 0.048348 | -37.9961 | 3.1204 | 6.48 | 0.29 | 0.32543 | -0.50411 | 0.33635 | -0.41279 | -0.55838 | -0.35162 | 0.84704 | 0.40505 | 0.38817 | 0.42046 | 0.37347 | 0.62997 | 0.42444 | 0.41859
42810.4359 | -361 | 18.6543 | 18.6742 | 18.6448 | 18.6642 | 18.003 | 16.6535 | 14.7046 | 16.7399 | 17.2336 | 17.3305 | 17.3528 | 16.8967 | 15.9463 | 14.5632 | 15.1109 | 15.0666 | 15.6076 | 13.4464 | 13.5643 | 14.1318 |  |  |  | 16.6501 | 15.9804 | 15.0878 | 10.1149 | 9.4351 | 9.6859 | 17.3601 | 16.4531 | 15.2436 | 16.9615 | 16.2382 | 15.2413 | 10.8213 | 11.7601 |  | 12.1726 | 10.3174 | 10.228 | 8.8288 |  | 6.3779 | 6.3996 | 5.9084 | 5.9664 | 5.9385 | 6.2169 | 6.1989 | 5.0558 | 6.3556 | 4.6782 | 6.6135 | 8.2084 | 42.5398 | 46.7143 | 43.1386 | 15.2813 |  |  | 0.031759 | 0.027031 | -0.27348 | -0.19451 | -0.12009 | -0.16408 | 0.53874 | 0.21143 | -0.19069 | -0.63775 | -0.28326 | 8.8696 | 8.8709 | 2.0087 | 15.9235 | 16.7719 | 17.2954 | 17.6186 | 17.5718 | 16.5616 | 14.9128 | 16.8827 | 17.2169 | 17.5053 | 17.5518 | 17.2939 | 16.5047 | 14.7385 | 6.3241 | 8.4544 | 5.0709 | 5.4131 | 5.5602 | 6.554 | 7.5747 | 16.0193 | 15.5995 | 15.4454 | 14.3715 | 14.2597 | 14.1956 |  |  |  | 10.7679 | 9.3581 | 8.9939 | 8.9897 | 0.19394 | 0.065142 | 12.694 |  |  | 10.635 |  |  | 16.9005 | 16.0958 | 15.0721 | 16.4022 | 15.6866 | 14.7992 | 10.4708 | 10.4668 | 11.1604 | 10.9309 | 9.1874 |  | 10.5655 | 8.893 | 9.8186 | 9.2416 | 11.0668 | 11.4973 |  | 12.2824 |  |  | 11.7869 | 12.6178 | 12.565 | [6 empty] | 12.5285 |  |  | 11.3261 |  |  | 9.2079 | 10.3818 | 11.7629 | 7.8609 | 9.0989 | 12.432 | 7.877 | 9.5267 | 12.2009 | 9.1781 | 10.4676 | 7.8073 | 10.283 | 8.0854 | 10.0933 | 7.8829 | 9.8232 | 13.0614 | 10.5162 | 10.1452 | 11.1921 | 8.1216 | 9.716 | 12.5521 | 8.0089 | 10.2811 | 9.6942 | 9.769 | 8.4935 | 10.0912 | 0.054108 | 20.9573 | 0.033975 | 0.048935 | -37.9712 | 3.1204 | -7.89 | 0.44 | 0.20887 | 0.19157 | -0.60934 | -0.51388 | -0.40365 | -0.47183 | 0.85495 | 0.40566 | 0.38924 | 0.42068 | 0.37258 | 0.63033 | 0.42405 | 0.41782
42810.4359 | -360 | 18.6531 | 18.6711 | 18.6436 | 18.6619 | 18.0042 | 16.649 | 14.7069 | 16.74 | 17.2343 | 17.3302 | 17.3435 | 16.8914 | 15.9469 | 14.5629 | 15.108 | 15.0652 | 15.6073 | 13.4415 | 13.5586 | 14.1311 |  |  |  | 16.6414 | 15.9826 | 15.0907 | 10.117 | 9.4421 | 9.6838 | 17.3487 | 16.4445 | 15.2326 | 16.9534 | 16.2331 | 15.2352 | 10.8134 | 11.7781 |  | 12.1637 | 10.3234 | 10.2313 | 8.8425 |  | 6.374 | 6.404 | 5.9127 | 5.9816 | 5.9663 | 6.242 | 6.1945 | 5.0694 | 6.3546 | 4.6873 | 6.6136 | 8.213 | 42.5388 | 46.7164 | 43.1334 | 15.2959 |  |  | 0.036359 | -0.26342 | -0.034948 | -0.32724 | 0.1881 | 0.04948 | 0.46711 | 0.15032 | -0.3022 | -0.25487 | -0.25107 | 8.87 | 8.8707 | 2.0084 | 15.9318 | 16.7748 | 17.2972 | 17.6142 | 17.5829 | 16.5664 | 14.9218 | 16.8895 | 17.2163 | 17.5185 | 17.5611 | 17.304 | 16.5201 | 14.7441 | 6.3512 | 8.4331 | 5.0929 | 5.4238 | 5.5678 | 6.5624 | 7.5821 | 16.0187 | 15.598 | 15.4473 | 14.3652 | 14.2613 | 14.1991 |  |  |  | 10.7751 | 9.3618 | 8.9904 | 9.0311 | 0.168 | 0.13327 | 12.7009 |  |  | 10.6477 |  |  | 16.895 | 16.0974 | 15.0753 | 16.3967 | 15.6905 | 14.7921 | 10.4627 | 10.4621 | 11.1635 | 10.9315 | 9.1747 |  | 10.5604 | 8.8284 | 9.8178 | 9.2365 | 11.0548 | 11.4794 |  | 12.2749 |  |  | 11.7907 | 12.6109 | 12.5702 | [6 empty] | 12.5367 |  |  | 11.3351 |  |  | 9.2047 | 10.3782 | 11.7588 | 7.8466 | 9.1093 | 12.4115 | 7.8714 | 9.5168 | 12.1949 | 9.173 | 10.4528 | 7.8089 | 10.2781 | 8.0838 | 10.0956 | 7.8897 | 9.8101 | 13.0482 | 10.5111 | 10.142 | 11.1865 | 8.1089 | 9.7068 | 12.535 | 7.9923 | 10.2573 | 9.694 | 9.76 | 8.4873 | 10.0861 | 0.12961 | 20.9557 | 0.034061 | 0.04824 | -37.9969 | 3.1204 | -1.2 | 0.34 | 0.22348 | -0.59803 | -0.21783 | -0.66655 | 0.50521 | 0.25911 | 0.79613 | 0.40585 | 0.391 | 0.42043 | 0.37054 | 0.62875 | 0.42341 | 0.41691
42810.4359 | -359 | 18.6535 | 18.6692 | 18.6461 | 18.6633 | 18.0081 | 16.652 | 14.7135 | 16.7422 | 17.2284 | 17.3369 | 17.3456 | 16.8965 | 15.9512 | 14.5588 | 15.1012 | 15.0632 | 15.6085 | 13.4432 | 13.5603 | 14.1362 |  |  |  | 16.6486 | 15.978 | 15.0886 | 10.1173 | 9.4339 | 9.6784 | 17.3535 | 16.4463 | 15.2355 | 16.9576 | 16.239 | 15.2365 | 10.8151 | 11.8 |  | 12.1593 | 10.3258 | 10.2396 | 8.849 |  | 6.3835 | 6.4056 | 5.9049 | 5.9864 | 6.0009 | 6.252 | 6.2368 | 5.0519 | 6.359 | 4.6601 | 6.6088 | 8.2047 | 42.532 | 46.7091 | 43.1123 | 15.3092 |  |  | 0.058047 | -0.13462 | -0.14666 | 0.055854 | 0.25512 | 0.002168 | 0.36788 | 0.12469 | -0.029758 | -0.20515 | -0.037066 | 8.8678 | 8.8691 | 2.0083 | 15.9244 | 16.7694 | 17.2913 | 17.6044 | 17.5779 | 16.5589 | 14.916 | 16.8815 | 17.2167 | 17.5073 | 17.5514 | 17.2971 | 16.5125 | 14.741 | 6.4009 | 8.4005 | 5.1067 | 5.4259 | 5.5737 | 6.5598 | 7.5832 | 16.0208 | 15.6008 | 15.4427 | 14.3685 | 14.2626 | 14.2041 |  |  |  | 10.7774 | 9.3534 | 8.9866 | 9.0669 | 0.12323 | 0.0062354 | 12.7024 |  |  | 10.6387 |  |  | 16.897 | 16.0918 | 15.0761 | 16.395 | 15.6916 | 14.7927 | 10.4524 | 10.4693 | 11.1453 | 10.9246 | 9.2073 |  | 10.5635 | 8.7766 | 9.8221 | 9.2429 | 11.0644 | 11.483 |  | 12.2745 |  |  | 11.8005 | 12.6051 | 12.5822 | [6 empty] | 12.5499 |  |  | 11.3425 |  |  | 9.2197 | 10.3748 | 11.7619 | 7.8446 | 9.1128 | 12.4145 | 7.8829 | 9.5333 | 12.2055 | 9.1722 | 10.4669 | 7.8015 | 10.2719 | 8.0954 | 10.0989 | 7.9157 | 9.7887 | 13.0486 | 10.51 | 10.1515 | 11.2003 | 8.1296 | 9.7225 | 12.5579 | 7.9671 | 10.2526 | 9.7054 | 9.7672 | 8.4977 | 10.0931 | -0.090727 | 20.9557 | 0.03405 | 0.047675 | -37.9805 | 3.1205 | 11.78 | 0.33 | 0.28237 | -0.42752 | -0.44622 | 0.27538 | 0.58838 | 0.054239 | 0.70654 | 0.40504 | 0.39258 | 0.42057 | 0.36473 | 0.62735 | 0.42329 | 0.41599
42810.4359 | -358 | 18.6643 | 18.687 | 18.6516 | 18.667 | 18.0168 | 16.6547 | 14.7201 | 16.7463 | 17.2333 | 17.3337 | 17.3452 | 16.9031 | 15.9535 | 14.5617 | 15.1047 | 15.0557 | 15.6008 | 13.4418 | 13.5579 | 14.1387 |  |  |  | 16.6388 | 15.9796 | 15.0839 | 10.1206 | 9.4305 | 9.7244 | 17.351 | 16.4448 | 15.246 | 16.9598 | 16.2451 | 15.2393 | 10.8168 | 11.8381 |  | 12.1705 | 10.3434 | 10.2518 | 8.8412 |  | 6.3788 | 6.4006 | 5.893 | 5.9739 | 6.0088 | 6.2484 | 6.2871 | 5.1025 | 6.3582 | 4.6127 | 6.6085 | 8.2025 | 42.5113 | 46.7063 | 43.0996 | 15.3158 |  |  | 0.048847 | -0.10768 | -0.07766 | 0.008542 | 0.38064 | 0.042252 | 0.15367 | 0.097748 | -0.4715 | -0.48565 | -0.3532 | 8.8687 | 8.8698 | 2.0087 | 15.9191 | 16.7583 | 17.2809 | 17.605 | 17.5757 | 16.5624 | 14.9179 | 16.8795 | 17.212 | 17.5071 | 17.5492 | 17.2915 | 16.5045 | 14.7399 | 6.4142 | 8.3852 | 5.124 | 5.3986 | 5.6038 | 6.5718 | 7.5854 | 16.0146 | 15.5963 | 15.45 | 14.3654 | 14.2614 | 14.1997 |  |  |  | 10.772 | 9.3575 | 9.0054 | 9.1099 | -0.017577 | -0.10537 | 12.6916 |  |  | 10.6397 |  |  | 16.885 | 16.0935 | 15.0731 | 16.3955 | 15.6849 | 14.7885 | 10.431 | 10.4705 | 11.1346 | 10.9153 | 9.2316 |  | 10.5713 | 8.7152 | 9.8231 | 9.2543 | 11.0569 | 11.505 |  | 12.2699 |  |  | 11.7698 | 12.5948 | 12.5744 | [6 empty] | 12.5365 |  |  | 11.3528 |  |  | 9.2214 | 10.3753 | 11.7645 | 7.8452 | 9.1182 | 12.4252 | 7.8897 | 9.5484 | 12.2277 | 9.1761 | 10.4553 | 7.8083 | 10.2772 | 8.0995 | 10.1222 | 7.8779 | 9.7362 | 13.0418 | 10.5029 | 10.1398 | 11.2027 | 8.124 | 9.7178 | 12.5489 | 7.933 | 10.2298 | 9.6861 | 9.7479 | 8.4887 | 10.0802 | -0.0088718 | 20.9566 | 0.034497 | 0.048377 | -37.9983 | 3.1205 | 10.04 | 0.37 | 0.25905 | -0.38235 | -0.32471 | 0.10769 | 0.71868 | 0.23944 | 0.45664 | 0.40462 | 0.39432 | 0.42 | 0.36464 | 0.62567 | 0.42356 | 0.41462
42810.4359 | -357 | 18.6673 | 18.6857 | 18.6528 | 18.6567 | 18.0124 | 16.6542 | 14.7125 | 16.7527 | 17.2432 | 17.3292 | 17.3557 | 16.8931 | 15.9404 | 14.5569 | 15.1053 | 15.0547 | 15.6104 | 13.4443 | 13.5569 | 14.1371 |  |  |  | 16.6418 | 15.9778 | 15.0918 | 10.1132 | 9.436 | 9.7637 | 17.359 | 16.4566 | 15.237 | 16.9575 | 16.2424 | 15.2336 | 10.8294 | 11.868 |  | 12.1685 | 10.3555 | 10.2683 | 8.8355 |  | 6.3829 | 6.4108 | 5.9002 | 5.979 | 6.0082 | 6.2524 | 6.326 | 5.1597 | 6.3696 | 4.6335 | 6.6097 | 8.2116 | 42.5064 | 46.7176 | 43.0879 | 15.3242 |  |  | 0.10799 | -0.11688 | 0.015648 | 0.05257 | 0.24198 | -0.40458 | -0.45088 | 0.051092 | 1.1402 | -0.57146 | -0.13264 | 8.8688 | 8.8701 | 2.0086 | 15.9287 | 16.7661 | 17.2954 | 17.6161 | 17.5772 | 16.5642 | 14.9227 | 16.8918 | 17.2139 | 17.5152 | 17.5559 | 17.2969 | 16.506 | 14.7488 | 6.3895 | 8.4156 | 5.1381 | 5.3806 | 5.6175 | 6.5653 | 7.5782 | 16.0151 | 15.5932 | 15.4409 | 14.3627 | 14.2504 | 14.1925 |  |  |  | 10.7633 | 9.3449 | 8.9892 | 9.1296 | -0.065594 | -0.0061858 | 12.7014 |  |  | 10.6488 |  |  | 16.8891 | 16.0871 | 15.0714 | 16.3991 | 15.6833 | 14.7883 | 10.4166 | 10.4783 | 11.1332 | 10.9075 | 9.2587 |  | 10.5706 | 8.6463 | 9.8118 | 9.2481 | 11.0494 | 11.5269 |  | 12.2514 |  |  | 11.7559 | 12.598 | 12.6029 | [6 empty] | 12.5588 |  |  | 11.3693 |  |  | 9.2215 | 10.3593 | 11.7612 | 7.8387 | 9.0984 | 12.4178 | 7.887 | 9.5537 | 12.2295 | 9.173 | 10.4528 | 7.7911 | 10.2591 | 8.1009 | 10.1127 | 7.8452 | 9.7294 | 13.0436 | 10.5033 | 10.1359 | 11.2089 | 8.1313 | 9.7277 | 12.5556 | 7.937 | 10.2317 | 9.6926 | 9.7552 | 8.4905 | 10.0844 | -0.03988 | 20.9562 | 0.034681 | 0.048725 | -37.9652 | 3.1204 | 8.83 | 0.33 | 0.38519 | -0.39835 | 0.14576 | 0.26716 | 0.57303 | -0.74095 | -0.78219 | 0.40385 | 0.39587 | 0.41993 | 0.36663 | 0.62327 | 0.42414 | 0.41379
42810.4359 | -356 | 18.653 | 18.6817 | 18.651 | 18.6554 | 18.0068 | 16.6514 | 14.714 | 16.7518 | 17.2353 | 17.3351 | 17.3423 | 16.899 | 15.9461 | 14.559 | 15.1091 | 15.0569 | 15.6165 | 13.45 | 13.5637 | 14.135 |  |  |  | 16.6476 | 15.9799 | 15.0918 | 10.1274 | 9.4477 | 9.8347 | 17.3491 | 16.4564 | 15.2437 | 16.9583 | 16.2416 | 15.2418 | 10.8244 | 11.8918 |  | 12.1692 | 10.3519 | 10.273 | 8.8123 |  | 6.3858 | 6.404 | 5.8861 | 5.9668 | 5.9919 | 6.2386 | 6.3094 | 5.1367 | 6.3642 | 4.5591 | 6.6072 | 8.2023 | 42.4859 | 46.7115 | 43.0689 | 15.328 |  |  | 0.033731 | -0.008453 | -0.023776 | -0.021686 | 0.2525 | -0.31588 | -0.28857 | -0.031704 | -0.090084 | -0.053042 | -0.15688 | 8.8677 | 8.8683 | 2.0083 | 15.9269 | 16.7703 | 17.298 | 17.6209 | 17.583 | 16.5639 | 14.9239 | 16.8914 | 17.215 | 17.5114 | 17.554 | 17.2969 | 16.5165 | 14.7413 | 6.3763 | 8.4419 | 5.1624 | 5.3851 | 5.6276 | 6.5705 | 7.5728 | 16.0101 | 15.5953 | 15.444 | 14.3666 | 14.2555 | 14.1952 |  |  |  | 10.768 | 9.3428 | 8.9931 | 9.1447 | -0.20053 | -0.1097 | 12.6981 |  |  | 10.6435 |  |  | 16.8873 | 16.0821 | 15.0739 | 16.3895 | 15.6783 | 14.7878 | 10.4026 | 10.4772 | 11.1278 | 10.8995 | 9.308 |  | 10.5694 | 8.6093 | 9.8137 | 9.2565 | 11.0552 | 11.5396 |  | 12.2594 |  |  | 11.7335 | 12.6092 | 12.6144 | [6 empty] | 12.5667 |  |  | 11.3829 |  |  | 9.2282 | 10.3658 | 11.7694 | 7.8455 | 9.1078 | 12.4294 | 7.9066 | 9.5642 | 12.23 | 9.1811 | 10.4599 | 7.8027 | 10.2649 | 8.1113 | 10.1194 | 7.825 | 9.7164 | 13.0512 | 10.5113 | 10.1414 | 11.2058 | 8.1318 | 9.7294 | 12.5593 | 7.9161 | 10.2327 | 9.6923 | 9.7411 | 8.4882 | 10.0787 | -0.060296 | 20.9566 | 0.034887 | 0.049144 | -37.956 | 3.1204 | -0.64 | 0.34 | 0.21531 | -0.10713 | -0.17967 | -0.17159 | 0.58533 | -0.65468 | -0.62575 | 0.40244 | 0.39695 | 0.41989 | 0.3687 | 0.61995 | 0.42462 | 0.41352
42810.4359 | -355 | 18.6564 | 18.6777 | 18.6517 | 18.6611 | 18.0085 | 16.6548 | 14.7204 | 16.7524 | 17.2374 | 17.3342 | 17.3503 | 16.9017 | 15.9474 | 14.5612 | 15.1045 | 15.063 | 15.6053 | 13.4459 | 13.5586 | 14.1332 |  |  |  | 16.6418 | 15.9838 | 15.0931 | 10.1377 | 9.4435 | 9.8801 | 17.3483 | 16.4598 | 15.2436 | 16.9609 | 16.2398 | 15.2472 | 10.8184 | 11.9154 |  | 12.1665 | 10.3548 | 10.2769 | 8.7868 |  | 6.3916 | 6.4069 | 5.8899 | 5.9625 | 5.9916 | 6.2264 | 6.2839 | 5.0619 | 6.3658 | 4.514 | 6.6155 | 8.2003 | 42.4683 | 46.702 | 43.0602 | 15.329 |  |  | 0.12113 | 0.005343 | 0.098448 | 0.081482 | -0.05372 | -0.21994 | 0.23186 | 0.039264 | -0.31757 | 0.58748 | -0.23338 | 8.8695 | 8.8706 | 2.0085 | 15.9291 | 16.7671 | 17.2962 | 17.6168 | 17.5807 | 16.5668 | 14.9218 | 16.8827 | 17.221 | 17.5089 | 17.5544 | 17.2943 | 16.5125 | 14.7422 | 6.3479 | 8.3853 | 5.1764 | 5.3928 | 5.6386 | 6.562 | 7.5675 | 16.0092 | 15.5945 | 15.4447 | 14.3662 | 14.2523 | 14.2009 |  |  |  | 10.7628 | 9.3512 | 9.0018 | 9.1314 | -0.13043 | -0.13021 | 12.7025 |  |  | 10.6412 |  |  | 16.8903 | 16.0868 | 15.0688 | 16.3857 | 15.6776 | 14.7843 | 10.388 | 10.4733 | 11.1326 | 10.9032 | 9.3583 |  | 10.5701 | 8.5982 | 9.8178 | 9.2632 | 11.0512 | 11.5523 |  | 12.2607 |  |  | 11.7192 | 12.6027 | 12.6172 | [6 empty] | 12.5647 |  |  | 11.3811 |  |  | 9.2287 | 10.3532 | 11.7785 | 7.8387 | 9.0974 | 12.4258 | 7.9053 | 9.548 | 12.2293 | 9.1786 | 10.449 | 7.8041 | 10.2603 | 8.1076 | 10.1192 | 7.8347 | 9.7115 | 13.0476 | 10.5187 | 10.1461 | 11.2137 | 8.1414 | 9.7213 | 12.5682 | 7.9124 | 10.2403 | 9.6985 | 9.7498 | 8.487 | 10.0788 | -0.14157 | 20.955 | 0.034887 | 0.049144 | -37.9839 | 3.1205 | -16.18 | 0.3 | 0.40804 | 0.085172 | 0.3656 | 0.33261 | -0.26998 | -0.54627 | 0.56089 | 0.40107 | 0.3974 | 0.41957 | 0.37086 | 0.61777 | 0.42512 | 0.41372
42810.4359 | -354 | 18.6478 | 18.6753 | 18.6472 | 18.6583 | 18.0022 | 16.6514 | 14.7143 | 16.742 | 17.2343 | 17.329 | 17.3454 | 16.8933 | 15.9365 | 14.5571 | 15.1066 | 15.067 | 15.6039 | 13.4543 | 13.5666 | 14.1278 |  |  |  | 16.6456 | 15.9785 | 15.0862 | 10.1428 | 9.4431 | 9.8789 | 17.3528 | 16.4493 | 15.2387 | 16.9626 | 16.2389 | 15.2441 | 10.8237 | 11.9296 |  | 12.1572 | 10.3556 | 10.2834 | 8.7762 |  | 6.3983 | 6.4131 | 5.8979 | 5.9773 | 5.9926 | 6.2182 | 6.2741 | 4.9665 | 6.3758 | 4.5248 | 6.6151 | 8.1998 | 42.454 | 46.6945 | 43.0412 | 15.3275 |  |  | 0.13033 | -0.15631 | -0.05926 | 0.13208 | -0.16674 | 0.019252 | 0.35803 | -0.04616 | -0.28994 | -0.61426 | -0.43963 | 8.8686 | 8.8696 | 2.0086 | 15.9235 | 16.7672 | 17.2982 | 17.619 | 17.5878 | 16.5703 | 14.925 | 16.881 | 17.214 | 17.5056 | 17.5523 | 17.3007 | 16.5109 | 14.7381 | 6.3311 | 8.3532 | 5.2034 | 5.4125 | 5.6597 | 6.5552 | 7.5623 | 16.0111 | 15.6004 | 15.4451 | 14.3666 | 14.2595 | 14.2015 |  |  |  | 10.7617 | 9.3406 | 8.9979 | 9.1341 | 0.15868 | -0.055118 | 12.7032 |  |  | 10.6465 |  |  | 16.8859 | 16.0969 | 15.0773 | 16.3959 | 15.6755 | 14.7971 | 10.3763 | 10.4814 | 11.1402 | 10.9181 | 9.4148 |  | 10.5705 | 8.5962 | 9.8159 | 9.2639 | 11.0416 | 11.5613 |  | 12.2504 |  |  | 11.6995 | 12.5673 | 12.6264 | [6 empty] | 12.5584 |  |  | 11.3772 |  |  | 9.2401 | 10.356 | 11.7872 | 7.8548 | 9.1035 | 12.4335 | 7.9131 | 9.5483 | 12.2389 | 9.1816 | 10.4435 | 7.81 | 10.2581 | 8.1072 | 10.1297 | 7.8475 | 9.7225 | 13.0495 | 10.5174 | 10.1655 | 11.2276 | 8.1481 | 9.7271 | 12.5734 | 7.9018 | 10.2433 | 9.7025 | 9.7504 | 8.4911 | 10.0874 | -0.097083 | 20.9556 | 0.034658 | 0.048471 | -37.946 | 3.1204 | 0.74 | 0.35 | 0.42325 | -0.46067 | -0.28365 | 0.42348 | -0.47564 | 0.16162 | 0.69697 | 0.39951 | 0.39739 | 0.41923 | 0.37195 | 0.61417 | 0.42559 | 0.41361
42810.4359 | -353 | 18.6506 | 18.6819 | 18.6498 | 18.6573 | 18.0058 | 16.6566 | 14.7138 | 16.7449 | 17.2326 | 17.3331 | 17.3449 | 16.8945 | 15.9342 | 14.5565 | 15.1026 | 15.0622 | 15.5958 | 13.4408 | 13.5569 | 14.1215 |  |  |  | 16.6395 | 15.9687 | 15.083 | 10.1384 | 9.4421 | 9.8737 | 17.3445 | 16.4407 | 15.2337 | 16.9563 | 16.235 | 15.2392 | 10.8159 | 11.9534 |  | 12.16 | 10.3526 | 10.2759 | 8.7468 |  | 6.3888 | 6.4006 | 5.8944 | 5.9774 | 5.9833 | 6.2018 | 6.2476 | 4.9363 | 6.3652 | 4.5153 | 6.6039 | 8.2008 | 42.443 | 46.6829 | 43.0274 | 15.3189 |  |  | -0.10426 | -0.008453 | 0.10239 | -0.53949 | -0.064232 | -0.089828 | 0.59722 | 0.035976 | -0.15469 | -0.25004 | -0.27133 | 8.8697 | 8.8707 | 2.0087 | 15.923 | 16.772 | 17.3026 | 17.6161 | 17.5851 | 16.5673 | 14.9175 | 16.8818 | 17.2159 | 17.5047 | 17.5476 | 17.2978 | 16.5111 | 14.7465 | 6.3561 | 8.3692 | 5.214 | 5.4386 | 5.7047 | 6.5585 | 7.563 | 16.0142 | 15.6037 | 15.4494 | 14.3679 | 14.2707 | 14.2021 |  |  |  | 10.77 | 9.3499 | 8.9925 | 9.1177 | -0.070253 | -0.1097 | 12.7043 |  |  | 10.6414 |  |  | 16.8925 | 16.0944 | 15.0777 | 16.3988 | 15.683 | 14.7936 | 10.3643 | 10.4936 | 11.1457 | 10.9265 | 9.4606 |  | 10.5748 | 8.5798 | 9.8295 | 9.2784 | 11.0602 | 11.5775 |  | 12.2553 |  |  | 11.6937 | 12.5523 | 12.626 | [6 empty] | 12.5566 |  |  | 11.3827 |  |  | 9.2438 | 10.3599 | 11.7984 | 7.8562 | 9.1036 | 12.4422 | 7.9179 | 9.5581 | 12.2421 | 9.1864 | 10.4492 | 7.8143 | 10.2533 | 8.1032 | 10.128 | 7.8396 | 9.7168 | 13.0501 | 10.5175 | 10.1725 | 11.2319 | 8.1506 | 9.7306 | 12.5812 | 7.8671 | 10.238 | 9.6961 | 9.7575 | 8.4904 | 10.0916 | 0.033693 | 20.9577 | 0.034193 | 0.04774 | -37.9092 | 3.1205 | 14.17 | 0.3 | -0.37856 | -0.10713 | 0.37284 | -0.85583 | -0.2952 | -0.3491 | 0.90014 | 0.39838 | 0.3983 | 0.41944 | 0.36955 | 0.61307 | 0.42615 | 0.41434
42810.436 | -352 | 18.6611 | 18.6843 | 18.6469 | 18.6595 | 18.0003 | 16.6516 | 14.71 | 16.7476 | 17.2319 | 17.3361 | 17.3442 | 16.8921 | 15.9417 | 14.5551 | 15.1045 | 15.0662 | 15.606 | 13.4428 | 13.5572 | 14.1332 |  |  |  | 16.6453 | 15.9779 | 15.0844 | 10.1485 | 9.4507 | 9.9038 | 17.3516 | 16.4487 | 15.2434 | 16.9591 | 16.2466 | 15.2436 | 10.8251 | 11.9857 |  | 12.1667 | 10.3607 | 10.2946 | 8.726 |  | 6.4001 | 6.4103 | 5.8996 | 5.9651 | 5.9863 | 6.189 | 6.2407 | 4.9758 | 6.3697 | 4.5267 | 6.6047 | 8.1963 | 42.4309 | 46.6667 | 43.0131 | 15.3127 |  |  | 0.16253 | -0.10571 | -0.31948 | -0.52438 | 0.05536 | 0.19405 | 0.4842 | -0.1881 | -0.37206 | -0.41327 | -0.22682 | 8.8677 | 8.8689 | 2.0085 | 15.9317 | 16.7804 | 17.3044 | 17.6202 | 17.5903 | 16.5776 | 14.9233 | 16.8809 | 17.2251 | 17.5121 | 17.5587 | 17.3024 | 16.5099 | 14.7449 | 6.3736 | 8.4179 | 5.2308 | 5.4585 | 5.7794 | 6.5604 | 7.5643 | 16.0164 | 15.6096 | 15.4521 | 14.3708 | 14.2663 | 14.2042 |  |  |  | 10.7747 | 9.3582 | 9.0017 | 9.1051 | 0.012407 | -0.030464 | 12.7058 |  |  | 10.6506 |  |  | 16.8955 | 16.0965 | 15.0706 | 16.3939 | 15.6827 | 14.7813 | 10.3492 | 10.4967 | 11.1545 | 10.9279 | 9.4649 |  | 10.5726 | 8.5562 | 9.8282 | 9.2737 | 11.0454 | 11.5677 |  | 12.2536 |  |  | 11.6872 | 12.5367 | 12.6152 | [6 empty] | 12.5561 |  |  | 11.3826 |  |  | 9.2515 | 10.3617 | 11.8073 | 7.8561 | 9.1068 | 12.4445 | 7.928 | 9.5688 | 12.2437 | 9.1983 | 10.4498 | 7.82 | 10.2465 | 8.1057 | 10.126 | 7.7889 | 9.6919 | 13.0409 | 10.5135 | 10.1705 | 11.2266 | 8.1461 | 9.7259 | 12.5778 | 7.812 | 10.2241 | 9.6859 | 9.7571 | 8.4746 | 10.0828 | 0.014818 | 20.9565 | 0.034227 | 0.048392 | -37.9115 | 3.1204 | 10.8 | 0.3 | 0.47268 | -0.37884 | -0.65861 | -0.84378 | 0.27405 | 0.51308 | 0.81048 | 0.39819 | 0.39891 | 0.41909 | 0.36782 | 0.61136 | 0.42703 | 0.41484
42810.436 | -351 | 18.6497 | 18.6796 | 18.6548 | 18.6641 | 18.0079 | 16.6555 | 14.7223 | 16.7539 | 17.2341 | 17.3289 | 17.3485 | 16.8926 | 15.946 | 14.5618 | 15.0979 | 15.0592 | 15.6024 | 13.4419 | 13.5501 | 14.1222 |  |  |  | 16.635 | 15.9788 | 15.0805 | 10.1437 | 9.4486 | 9.9159 | 17.3453 | 16.4421 | 15.2347 | 16.9529 | 16.2373 | 15.2396 | 10.8253 | 12.0045 |  | 12.1688 | 10.3592 | 10.2951 | 8.7112 |  | 6.3962 | 6.4034 | 5.8806 | 5.9556 | 5.978 | 6.1946 | 6.2251 | 5.0144 | 6.366 | 4.598 | 6.6063 | 8.1942 | 42.4274 | 46.65 | 42.9976 | 15.3046 |  |  | 0.1323 | -0.10505 | -0.021148 | -0.16165 | -0.10234 | -0.23439 | 0.099784 | -0.18284 | 0.22205 | -1.4394 | -0.22365 | 8.8703 | 8.8711 | 2.0085 | 15.9256 | 16.7733 | 17.302 | 17.6221 | 17.586 | 16.5697 | 14.9244 | 16.8819 | 17.2176 | 17.5085 | 17.5531 | 17.2946 | 16.51 | 14.7402 | 6.3778 | 8.4228 | 5.2336 | 5.4712 | 5.8357 | 6.5604 | 7.5636 | 16.0184 | 15.605 | 15.4513 | 14.3709 | 14.262 | 14.2069 |  |  |  | 10.7756 | 9.3553 | 9.0025 | 9.1103 | 0.065083 | 0.10297 | 12.7072 |  |  | 10.6582 |  |  | 16.8981 | 16.0941 | 15.0773 | 16.3959 | 15.6801 | 14.7847 | 10.3401 | 10.4954 | 11.1604 | 10.9305 | 9.4851 |  | 10.5712 | 8.5436 | 9.8232 | 9.275 | 11.0392 | 11.5617 |  | 12.2468 |  |  | 11.6928 | 12.5352 | 12.6218 | [6 empty] | 12.5661 |  |  | 11.3941 |  |  | 9.2595 | 10.3669 | 11.8119 | 7.8539 | 9.1097 | 12.4486 | 7.9298 | 9.5669 | 12.2436 | 9.2002 | 10.4545 | 7.8233 | 10.2404 | 8.1097 | 10.1283 | 7.7548 | 9.6467 | 13.0339 | 10.508 | 10.1777 | 11.237 | 8.1391 | 9.7173 | 12.5799 | 7.776 | 10.22 | 9.6832 | 9.7585 | 8.4729 | 10.0862 | 0.0076918 | 20.9557 | 0.033849 | 0.048616 | -37.9866 | 3.1204 | 4.52 | 0.29 | 0.42647 | -0.37766 | -0.16945 | -0.46848 | -0.37262 | -0.56391 | 0.36793 | 0.39758 | 0.39909 | 0.41885 | 0.36736 | 0.61096 | 0.42745 | 0.41473
42810.436 | -350 | 18.6398 | 18.6773 | 18.6516 | 18.6552 | 17.9989 | 16.6487 | 14.7103 | 16.7437 | 17.229 | 17.3307 | 17.3392 | 16.897 | 15.9371 | 14.5597 | 15.1035 | 15.0718 | 15.604 | 13.4564 | 13.5626 | 14.1238 |  |  |  | 16.6348 | 15.979 | 15.0839 | 10.1505 | 9.4551 | 9.9594 | 17.3344 | 16.4437 | 15.2368 | 16.957 | 16.2447 | 15.2373 | 10.819 | 12.0159 |  | 12.1657 | 10.351 | 10.2902 | 8.6857 |  | 6.4 | 6.4056 | 5.8749 | 5.9446 | 5.9802 | 6.1922 | 6.229 | 5.045 | 6.3729 | 4.6341 | 6.606 | 8.1979 | 42.4366 | 46.6275 | 42.9858 | 15.2996 |  |  | 0.060675 | 0.009943 | -0.046776 | -0.05717 | -0.001808 | -0.0918 | 0.406 | -0.18876 | -0.56822 | -1.2101 | -0.16463 | 8.8665 | 8.8674 | 2.0084 | 15.9299 | 16.7777 | 17.3024 | 17.6204 | 17.586 | 16.5707 | 14.9286 | 16.8918 | 17.2178 | 17.5091 | 17.5497 | 17.2964 | 16.509 | 14.7378 | 6.3988 | 8.441 | 5.2618 | 5.467 | 5.8828 | 6.563 | 7.5626 | 16.0195 | 15.6049 | 15.4517 | 14.3682 | 14.2616 | 14.2039 |  |  |  | 10.7714 | 9.3503 | 9.0023 | 9.1241 | 0.11452 | -0.01616 | 12.7048 |  |  | 10.6473 |  |  | 16.8877 | 16.0917 | 15.0688 | 16.3944 | 15.675 | 14.7826 | 10.3139 | 10.4912 | 11.1525 | 10.9285 | 9.5565 |  | 10.5808 | 8.5188 | 9.8377 | 9.293 | 11.053 | 11.5773 |  | 12.2637 |  |  | 11.7244 | 12.5488 | 12.6379 | [6 empty] | 12.566 |  |  | 11.3953 |  |  | 9.2606 | 10.3742 | 11.8192 | 7.8444 | 9.1109 | 12.4477 | 7.9377 | 9.5658 | 12.2438 | 9.1968 | 10.4613 | 7.8333 | 10.2382 | 8.1054 | 10.1247 | 7.737 | 9.6239 | 13.0322 | 10.5067 | 10.1782 | 11.245 | 8.136 | 9.7191 | 12.5825 | 7.748 | 10.206 | 9.6957 | 9.7606 | 8.4742 | 10.0944 | 0.22051 | 20.9556 | 0.033757 | 0.047212 | -38.0112 | 3.1204 | -24.63 | 0.29 | 0.28883 | 0.11619 | -0.25201 | -0.2786 | -0.049526 | -0.3529 | 0.74216 | 0.39591 | 0.40026 | 0.4188 | 0.36533 | 0.60771 | 0.42795 | 0.41421
42810.436 | -349 | 18.6478 | 18.6846 | 18.6513 | 18.6639 | 18.0043 | 16.6547 | 14.7123 | 16.7395 | 17.2334 | 17.3278 | 17.348 | 16.8971 | 15.9417 | 14.5606 | 15.1113 | 15.0798 | 15.6152 | 13.4637 | 13.5703 | 14.1336 |  |  |  | 16.6498 | 15.9839 | 15.0891 | 10.1653 | 9.4562 | 9.9911 | 17.3392 | 16.4595 | 15.243 | 16.9682 | 16.2427 | 15.2456 | 10.827 | 12.0365 |  | 12.1622 | 10.352 | 10.2953 | 8.6735 |  | 6.3977 | 6.4082 | 5.8686 | 5.9385 | 5.9806 | 6.1924 | 6.2339 | 5.0264 | 6.3705 | 4.6549 | 6.6056 | 8.1934 | 42.4503 | 46.6149 | 42.982 | 15.2961 |  |  | 0.042275 | -0.26078 | -0.076348 | -0.12551 | 0.040248 | -0.124 | 0.51836 | -0.20387 | -0.38743 | -0.34341 | -0.1535 | 8.8723 | 8.8735 | 2.0085 | 15.9294 | 16.7793 | 17.3018 | 17.6239 | 17.586 | 16.5702 | 14.9231 | 16.8884 | 17.2163 | 17.5095 | 17.5536 | 17.2957 | 16.5062 | 14.7425 | 6.3935 | 8.432 | 5.2852 | 5.4925 | 5.9322 | 6.5616 | 7.5701 | 16.0166 | 15.6 | 15.4406 | 14.3704 | 14.2604 | 14.2073 |  |  |  | 10.7703 | 9.3488 | 8.9942 | 9.0998 | -0.037635 | -0.04966 | 12.7054 |  |  | 10.6472 |  |  | 16.8863 | 16.0894 | 15.0678 | 16.3909 | 15.6775 | 14.7801 | 10.301 | 10.4936 | 11.1641 | 10.9334 | 9.5767 |  | 10.5772 | 8.5293 | 9.8317 | 9.2879 | 11.0538 | 11.5902 |  | 12.2552 |  |  | 11.7423 | 12.5568 | 12.6373 | [6 empty] | 12.5529 |  |  | 11.3958 |  |  | 9.2649 | 10.3741 | 11.821 | 7.8437 | 9.1105 | 12.4416 | 7.9446 | 9.5732 | 12.2421 | 9.1988 | 10.465 | 7.8424 | 10.2235 | 8.106 | 10.1162 | 7.7274 | 9.6059 | 13.0413 | 10.5138 | 10.1771 | 11.2548 | 8.1372 | 9.72 | 12.5918 | 7.7419 | 10.2099 | 9.7077 | 9.7674 | 8.4792 | 10.0984 | 0.0038398 | 20.9552 | 0.033344 | 0.047733 | -37.9997 | 3.1204 | 2.87 | 0.23 | 0.24111 | -0.59504 | -0.32196 | -0.4128 | 0.23367 | -0.41015 | 0.8386 | 0.39523 | 0.39977 | 0.41897 | 0.36576 | 0.60598 | 0.42856 | 0.41485
42810.436 | -348 | 18.6506 | 18.6816 | 18.6484 | 18.6535 | 18.0014 | 16.6487 | 14.7137 | 16.7436 | 17.2315 | 17.3331 | 17.3487 | 16.896 | 15.9361 | 14.5569 | 15.1073 | 15.0675 | 15.6087 | 13.4541 | 13.5673 | 14.1309 |  |  |  | 16.6459 | 15.9854 | 15.0844 | 10.1701 | 9.4535 | 9.9991 | 17.3481 | 16.4532 | 15.2394 | 16.956 | 16.249 | 15.2499 | 10.8304 | 12.0417 |  | 12.1573 | 10.3402 | 10.2795 | 8.6556 |  | 6.3974 | 6.3992 | 5.8659 | 5.9375 | 5.9778 | 6.1881 | 6.2176 | 5.0091 | 6.3653 | 4.6251 | 6.6058 | 8.1916 | 42.4522 | 46.6076 | 42.9671 | 15.2856 |  |  | 0.23415 | -0.10768 | 0.007108 | 0.11959 | 0.14736 | -0.25871 | 0.74836 | -0.10727 | -1.0246 | -0.42502 | -0.18947 | 8.8696 | 8.871 | 2.0087 | 15.9356 | 16.7848 | 17.3035 | 17.6193 | 17.5892 | 16.5725 | 14.9265 | 16.8885 | 17.226 | 17.5098 | 17.5543 | 17.2979 | 16.516 | 14.746 | 6.4017 | 8.4131 | 5.2906 | 5.5059 | 5.9427 | 6.5633 | 7.5683 | 16.01 | 15.61 | 15.4462 | 14.367 | 14.263 | 14.1994 |  |  |  | 10.7712 | 9.3478 | 8.9894 | 9.0858 | 0.038543 | 0.012446 | 12.7072 |  |  | 10.6433 |  |  | 16.8847 | 16.0871 | 15.0682 | 16.388 | 15.673 | 14.782 | 10.2979 | 10.4942 | 11.1694 | 10.9389 | 9.5975 |  | 10.5862 | 8.5476 | 9.8431 | 9.2827 | 11.0599 | 11.624 |  | 12.2606 |  |  | 11.7403 | 12.5603 | 12.6399 | [6 empty] | 12.564 |  |  | 11.3899 |  |  | 9.2719 | 10.3847 | 11.8216 | 7.8483 | 9.1111 | 12.4395 | 7.9569 | 9.5749 | 12.2477 | 9.1956 | 10.4714 | 7.8405 | 10.2158 | 8.1107 | 10.1127 | 7.7181 | 9.6007 | 13.0453 | 10.5197 | 10.1777 | 11.2637 | 8.1344 | 9.7083 | 12.5994 | 7.7471 | 10.2136 | 9.7085 | 9.7652 | 8.4763 | 10.1032 | 0.024255 | 20.9549 | 0.033527 | 0.048001 | -37.9463 | 3.1204 | -11.4 | 0.32 | 0.56744 | -0.38235 | 0.098236 | 0.40295 | 0.44712 | -0.59243 | 1.0076 | 0.39495 | 0.39964 | 0.41931 | 0.36503 | 0.60517 | 0.42917 | 0.41526
42810.436 | -347 | 18.6546 | 18.6812 | 18.6579 | 18.6624 | 18.0046 | 16.6531 | 14.7185 | 16.7442 | 17.2332 | 17.3305 | 17.3447 | 16.8943 | 15.9392 | 14.555 | 15.1083 | 15.0651 | 15.6109 | 13.4507 | 13.5687 | 14.1228 |  |  |  | 16.6484 | 15.9831 | 15.0886 | 10.1706 | 9.4482 | 10.0231 | 17.3493 | 16.4441 | 15.2389 | 16.951 | 16.2452 | 15.242 | 10.8213 | 12.034 |  | 12.1491 | 10.3185 | 10.2594 | 8.6429 |  | 6.401 | 6.402 | 5.8665 | 5.9358 | 5.9807 | 6.1848 | 6.2039 | 5.0109 | 6.3687 | 4.5789 | 6.6028 | 8.1976 | 42.4626 | 46.6039 | 42.9595 | 15.2931 |  |  | -0.073377 | 0.098655 | -0.038232 | 0.02037 | -0.097088 | -0.12926 | 0.40206 | -0.11253 | 1.024 | -0.61426 | -0.31326 | 8.869 | 8.8705 | 2.0085 | 15.9295 | 16.7699 | 17.2955 | 17.6115 | 17.5765 | 16.5684 | 14.9171 | 16.8772 | 17.2138 | 17.4994 | 17.5492 | 17.2914 | 16.5096 | 14.7417 | 6.4054 | 8.4456 | 5.3085 | 5.5372 | 5.8873 | 6.5646 | 7.5723 | 16.0114 | 15.6074 | 15.4407 | 14.3683 | 14.2579 | 14.1986 |  |  |  | 10.7685 | 9.3502 | 8.9873 | 9.0994 | 0.0097736 | -0.0024218 | 12.7096 |  |  | 10.6462 |  |  | 16.885 | 16.0822 | 15.0638 | 16.3847 | 15.6781 | 14.7752 | 10.2778 | 10.4904 | 11.1689 | 10.945 | 9.5886 |  | 10.5839 | 8.5304 | 9.8405 | 9.2845 | 11.0578 | 11.6456 |  | 12.2574 |  |  | 11.7168 | 12.5528 | 12.6376 | [6 empty] | 12.5748 |  |  | 11.3919 |  |  | 9.2746 | 10.3785 | 11.8162 | 7.8165 | 9.1168 | 12.4415 | 7.9642 | 9.5688 | 12.2489 | 9.197 | 10.4806 | 7.8065 | 10.2018 | 8.1116 | 10.1109 | 7.7159 | 9.5757 | 13.0536 | 10.5254 | 10.169 | 11.2716 | 8.129 | 9.7145 | 12.595 | 7.7477 | 10.2127 | 9.7091 | 9.764 | 8.4776 | 10.1129 | -0.075511 | 20.9545 | 0.033654 | 0.048652 | -37.9342 | 3.1204 | -9.07 | 0.25 | -0.31767 | 0.36598 | -0.22783 | 0.1663 | -0.36292 | -0.41875 | 0.73854 | 0.39512 | 0.40003 | 0.4192 | 0.36478 | 0.60365 | 0.42922 | 0.4148
42810.436 | -346 | 18.6506 | 18.6766 | 18.655 | 18.6626 | 18.004 | 16.6508 | 14.7143 | 16.7466 | 17.233 | 17.3312 | 17.341 | 16.8932 | 15.9448 | 14.5551 | 15.0953 | 15.0682 | 15.6093 | 13.4523 | 13.5629 | 14.1252 |  |  |  | 16.6374 | 15.9774 | 15.0867 | 10.1757 | 9.4516 | 10.0668 | 17.3488 | 16.4472 | 15.2408 | 16.954 | 16.2525 | 15.2393 | 10.8248 | 12.0427 |  | 12.1541 | 10.3142 | 10.2512 | 8.6423 |  | 6.4014 | 6.398 | 5.8636 | 5.9433 | 5.9831 | 6.1884 | 6.2772 | 5.0159 | 6.3698 | 4.5366 | 6.6018 | 8.1933 | 42.465 | 46.5852 | 42.9406 | 15.2995 |  |  | 0.16647 | -0.16879 | 0.020248 | -0.084766 | 0.063904 | -0.005716 | 0.46514 | 0.06752 | 0.020838 | -0.64824 | -0.099855 | 8.8678 | 8.8689 | 2.0084 | 15.9231 | 16.77 | 17.2927 | 17.6073 | 17.5763 | 16.5658 | 14.9206 | 16.8786 | 17.2156 | 17.5013 | 17.5531 | 17.2938 | 16.5084 | 14.7371 | 6.3552 | 8.4544 | 5.305 | 5.59 | 5.8469 | 6.5659 | 7.5723 | 16.02 | 15.6068 | 15.4488 | 14.373 | 14.2608 | 14.1993 |  |  |  | 10.7773 | 9.354 | 8.986 | 9.1279 | -0.0029902 | 0.068153 | 12.7177 |  |  | 10.6525 |  |  | 16.8853 | 16.0852 | 15.064 | 16.3884 | 15.6762 | 14.7782 | 10.2596 | 10.4986 | 11.1716 | 10.9506 | 9.573 |  | 10.5756 | 8.5096 | 9.833 | 9.2798 | 11.0531 | 11.6673 |  | 12.2563 |  |  | 11.6898 | 12.5573 | 12.6389 | [6 empty] | 12.5867 |  |  | 11.3978 |  |  | 9.2688 | 10.3751 | 11.8159 | 7.78 | 9.1205 | 12.4355 | 7.9579 | 9.5612 | 12.2326 | 9.1959 | 10.4707 | 7.7921 | 10.1929 | 8.1154 | 10.0926 | 7.7332 | 9.5705 | 13.0546 | 10.5297 | 10.1781 | 11.2836 | 8.1105 | 9.7066 | 12.5881 | 7.7488 | 10.214 | 9.7088 | 9.7637 | 8.4742 | 10.1114 | -0.10209 | 20.9545 | 0.033906 | 0.0485 | -37.9635 | 3.1204 | 5.04 | 0.28 | 0.47852 | -0.4787 | 0.1658 | -0.33924 | 0.29444 | -0.08806 | 0.79437 | 0.39528 | 0.40036 | 0.41917 | 0.37051 | 0.60404 | 0.42935 | 0.41429
42810.436 | -345 | 18.6571 | 18.6812 | 18.6496 | 18.6616 | 18.0062 | 16.6521 | 14.7113 | 16.7534 | 17.2365 | 17.3338 | 17.3436 | 16.8938 | 15.9513 | 14.5549 | 15.0955 | 15.0557 | 15.604 | 13.4431 | 13.558 | 14.1233 |  |  |  | 16.6398 | 15.9692 | 15.0843 | 10.1875 | 9.4523 | 10.0968 | 17.3397 | 16.4532 | 15.2327 | 16.9568 | 16.2415 | 15.2394 | 10.8229 | 12.0445 |  | 12.1563 | 10.3016 | 10.2451 | 8.6501 |  | 6.4018 | 6.4027 | 5.8665 | 5.9525 | 5.9952 | 6.247 | 6.3671 | 4.9836 | 6.3712 | 4.5302 | 6.604 | 8.1993 | 42.4659 | 46.581 | 42.9252 | 15.3155 |  |  | 0.010735 | -0.047881 | 0.024848 | -0.01577 | 0.10004 | 0.41352 | 0.54136 | -0.025136 | -0.31251 | -0.79888 | -0.27988 | 8.8692 | 8.8705 | 2.0084 | 15.9245 | 16.7744 | 17.2944 | 17.6159 | 17.5754 | 16.5649 | 14.9148 | 16.8835 | 17.2218 | 17.4999 | 17.5507 | 17.2941 | 16.5071 | 14.745 | 6.3392 | 8.4441 | 5.3225 | 5.654 | 5.8184 | 6.565 | 7.5711 | 16.0095 | 15.6049 | 15.4461 | 14.372 | 14.2482 | 14.1989 |  |  |  | 10.7687 | 9.3423 | 8.9747 | 9.1434 | 0.041177 | 0.092431 | 12.7136 |  |  | 10.6435 |  |  | 16.8886 | 16.0831 | 15.072 | 16.3906 | 15.6725 | 14.7795 | 10.2371 | 10.4977 | 11.171 | 10.948 | 9.5639 |  | 10.5811 | 8.4656 | 9.837 | 9.2857 | 11.0505 | 11.6967 |  | 12.2557 |  |  | 11.6973 | 12.5654 | 12.6501 | [6 empty] | 12.5887 |  |  | 11.3938 |  |  | 9.2758 | 10.3742 | 11.818 | 7.7517 | 9.1271 | 12.4272 | 7.9639 | 9.5673 | 12.2424 | 9.1869 | 10.4707 | 7.7996 | 10.1807 | 8.1161 | 10.0959 | 7.7325 | 9.5706 | 13.0534 | 10.5272 | 10.1725 | 11.2945 | 8.1109 | 9.6985 | 12.5949 | 7.7495 | 10.2089 | 9.696 | 9.7669 | 8.4644 | 10.1062 | -0.11808 | 20.9555 | 0.033717 | 0.047516 | -38.018 | 3.1204 | 15.93 | 0.33 | 0.12152 | -0.25496 | 0.18367 | -0.14632 | 0.36845 | 0.74908 | 0.85708 | 0.39572 | 0.40171 | 0.41892 | 0.37219 | 0.60195 | 0.42907 | 0.41358
42810.4361 | -344 | 18.653 | 18.6854 | 18.6471 | 18.6569 | 18.0025 | 16.6546 | 14.709 | 16.7475 | 17.2393 | 17.3368 | 17.3439 | 16.8946 | 15.95 | 14.5599 | 15.0964 | 15.0653 | 15.5993 | 13.4472 | 13.5628 | 14.1259 |  |  |  | 16.6424 | 15.9877 | 15.0858 | 10.2037 | 9.4554 | 10.1267 | 17.347 | 16.4518 | 15.2412 | 16.9656 | 16.2497 | 15.2419 | 10.8258 | 12.0621 |  | 12.165 | 10.3004 | 10.2482 | 8.6735 |  | 6.4047 | 6.414 | 5.8792 | 5.9788 | 6.0013 | 6.2875 | 6.4664 | 4.9723 | 6.383 | 4.5554 | 6.6138 | 8.1949 | 42.4671 | 46.5763 | 42.9184 | 15.3284 |  |  | -0.056293 | -0.18391 | 0.085304 | -0.08871 | 0.12633 | 0.098764 | 0.3922 | -0.26038 | -0.40164 | -0.28193 | -0.3381 | 8.8694 | 8.8701 | 2.0088 | 15.9273 | 16.7766 | 17.2976 | 17.6191 | 17.5827 | 16.5722 | 14.9255 | 16.8837 | 17.2185 | 17.51 | 17.5546 | 17.296 | 16.5089 | 14.7406 | 6.3361 | 8.4436 | 5.3534 | 5.6509 | 5.7905 | 6.5685 | 7.578 | 16.0104 | 15.5982 | 15.4472 | 14.3651 | 14.2546 | 14.1985 |  |  |  | 10.7592 | 9.3355 | 8.9802 | 9.1232 | -0.005624 | -0.018607 | 12.7194 |  |  | 10.6525 |  |  | 16.8945 | 16.091 | 15.0758 | 16.3994 | 15.6779 | 14.7879 | 10.2265 | 10.5021 | 11.1777 | 10.9585 | 9.5506 |  | 10.5775 | 8.4274 | 9.832 | 9.292 | 11.0386 | 11.7252 |  | 12.249 |  |  | 11.6884 | 12.5504 | 12.652 | [6 empty] | 12.5936 |  |  | 11.3944 |  |  | 9.2852 | 10.3849 | 11.8145 | 7.7359 | 9.1312 | 12.4301 | 7.9883 | 9.5646 | 12.2381 | 9.1985 | 10.4665 | 7.7987 | 10.1733 | 8.1154 | 10.1041 | 7.7257 | 9.5781 | 13.0585 | 10.516 | 10.1633 | 11.3086 | 8.1063 | 9.6998 | 12.6013 | 7.7425 | 10.2087 | 9.6843 | 9.7622 | 8.462 | 10.1083 | 0.16582 | 20.9556 | 0.034359 | 0.047545 | -37.9787 | 3.1204 | 22.24 | 0.33 | -0.27829 | -0.49969 | 0.34032 | -0.34705 | 0.41406 | 0.36611 | 0.72956 | 0.39597 | 0.40261 | 0.41835 | 0.37293 | 0.59932 | 0.42852 | 0.41383
42810.4361 | -343 | 18.6502 | 18.684 | 18.6508 | 18.6652 | 18.009 | 16.6448 | 14.7168 | 16.7442 | 17.2277 | 17.3348 | 17.3482 | 16.8939 | 15.9358 | 14.5561 | 15.086 | 15.0599 | 15.5959 | 13.4446 | 13.5593 | 14.1266 |  |  |  | 16.6393 | 15.9828 | 15.077 | 10.2031 | 9.4507 | 10.1453 | 17.3406 | 16.4433 | 15.2373 | 16.9518 | 16.24 | 15.2421 | 10.8204 | 12.0745 |  | 12.1572 | 10.2871 | 10.2351 | 8.6854 |  | 6.4101 | 6.4069 | 5.8799 | 5.9832 | 5.9934 | 6.2766 | 6.5012 | 4.9659 | 6.3738 | 4.5588 | 6.606 | 8.1989 | 42.4619 | 46.5792 | 42.9123 | 15.3419 |  |  | -0.054321 | -0.073509 | -0.017204 | 0.005258 | 0.015276 | 0.1717 | 0.46251 | -0.019876 | -0.15352 | -0.49467 | -0.34207 | 8.8694 | 8.8703 | 2.0083 | 15.9329 | 16.778 | 17.3025 | 17.6192 | 17.5862 | 16.5723 | 14.9307 | 16.886 | 17.2151 | 17.5081 | 17.5518 | 17.2954 | 16.5057 | 14.7393 | 6.3284 | 8.4528 | 5.3459 | 5.6408 | 5.7664 | 6.5592 | 7.5696 | 16.0145 | 15.5983 | 15.4529 | 14.3728 | 14.2593 | 14.1962 |  |  |  | 10.7616 | 9.3392 | 8.9806 | 9.1209 | 0.014433 | -0.01729 | 12.719 |  |  | 10.6522 |  |  | 16.8925 | 16.094 | 15.0718 | 16.3901 | 15.6794 | 14.7807 | 10.2071 | 10.4989 | 11.1807 | 10.9619 | 9.5516 |  | 10.5882 | 8.4296 | 9.8432 | 9.3108 | 11.0507 | 11.7525 |  | 12.255 |  |  | 11.6577 | 12.548 | 12.6496 | [6 empty] | 12.5849 |  |  | 11.3835 |  |  | 9.277 | 10.3793 | 11.8196 | 7.7318 | 9.1485 | 12.4302 | 7.9753 | 9.5564 | 12.2271 | 9.1989 | 10.4702 | 7.7906 | 10.1713 | 8.1023 | 10.0887 | 7.7285 | 9.6003 | 13.0712 | 10.5248 | 10.175 | 11.3219 | 8.1158 | 9.7186 | 12.6192 | 7.7613 | 10.2324 | 9.721 | 9.7857 | 8.4716 | 10.1127 | 0.093399 | 20.9545 | 0.032753 | 0.046756 | -38.0014 | 3.1205 | 13.06 | 0.36 | -0.27338 | -0.31592 | -0.15283 | 0.084491 | 0.14398 | 0.48272 | 0.79225 | 0.39629 | 0.40292 | 0.41823 | 0.37271 | 0.59918 | 0.42801 | 0.41397
42810.4361 | -342 | 18.6544 | 18.6801 | 18.6469 | 18.657 | 17.992 | 16.6481 | 14.7145 | 16.74 | 17.2338 | 17.3312 | 17.3414 | 16.8978 | 15.9385 | 14.5489 | 15.09 | 15.0642 | 15.6103 | 13.4463 | 13.5634 | 14.1233 |  |  |  | 16.6415 | 15.9786 | 15.081 | 10.2059 | 9.4471 | 10.1468 | 17.3334 | 16.4428 | 15.2291 | 16.949 | 16.2315 | 15.2369 | 10.8124 | 12.0775 |  | 12.1628 | 10.2759 | 10.2189 | 8.6774 |  | 6.4101 | 6.4111 | 5.8822 | 5.9747 | 5.9938 | 6.2502 | 6.5093 | 4.9545 | 6.3751 | 4.5543 | 6.5995 | 8.1967 | 42.449 | 46.5802 | 42.8956 | 15.3495 |  |  | 0.040959 | 0.008631 | 0.019592 | -0.10842 | 0.22096 | 0.1395 | 0.26866 | -0.19007 | -0.60928 | -0.15396 | -0.16344 | 8.8677 | 8.8691 | 2.0084 | 15.9288 | 16.7772 | 17.3008 | 17.6089 | 17.5803 | 16.5706 | 14.9186 | 16.8844 | 17.2154 | 17.5003 | 17.5498 | 17.2896 | 16.505 | 14.7364 | 6.3229 | 8.4661 | 5.3244 | 5.6643 | 5.744 | 6.5628 | 7.5774 | 16.0071 | 15.5941 | 15.4492 | 14.3654 | 14.2511 | 14.1935 |  |  |  | 10.7602 | 9.3258 | 8.976 | 9.1043 | 0.10783 | 0.045193 | 12.7182 |  |  | 10.6523 |  |  | 16.896 | 16.0939 | 15.069 | 16.3907 | 15.6818 | 14.7843 | 10.1855 | 10.5058 | 11.1784 | 10.9674 | 9.5328 |  | 10.5813 | 8.4003 | 9.8444 | 9.3044 | 11.0452 | 11.7645 |  | 12.2555 |  |  | 11.6502 | 12.5503 | 12.6553 | [6 empty] | 12.5931 |  |  | 11.3685 |  |  | 9.2894 | 10.3889 | 11.8231 | 7.7326 | 9.1617 | 12.4272 | 7.9723 | 9.5605 | 12.2353 | 9.2046 | 10.4702 | 7.7985 | 10.1788 | 8.1259 | 10.0872 | 7.74 | 9.6187 | 13.0849 | 10.5333 | 10.1752 | 11.3319 | 8.1222 | 9.7178 | 12.6334 | 7.7672 | 10.2473 | 9.7293 | 9.7898 | 8.4736 | 10.1216 | 0.036967 | 20.9542 | 0.032282 | 0.047002 | -38.0495 | 3.1204 | 11.46 | 0.34 | 0.23739 | 0.10825 | 0.1631 | -0.38368 | 0.54756 | 0.43508 | 0.60378 | 0.39659 | 0.40377 | 0.41823 | 0.37374 | 0.60248 | 0.42797 | 0.41438
42810.4361 | -341 | 18.6474 | 18.6765 | 18.6477 | 18.6584 | 17.9993 | 16.6427 | 14.7049 | 16.7403 | 17.2258 | 17.3308 | 17.3452 | 16.8893 | 15.9358 | 14.5428 | 15.0926 | 15.0628 | 15.6044 | 13.4501 | 13.5626 | 14.1299 |  |  |  | 16.6465 | 15.9788 | 15.0931 | 10.2227 | 9.4513 | 10.1624 | 17.3343 | 16.4407 | 15.2346 | 16.9595 | 16.2396 | 15.2358 | 10.8217 | 12.0945 |  | 12.161 | 10.2733 | 10.2228 | 8.676 |  | 6.4272 | 6.4208 | 5.8912 | 5.9869 | 5.998 | 6.2446 | 6.5245 | 4.9035 | 6.3831 | 4.6082 | 6.6117 | 8.1918 | 42.4407 | 46.5866 | 42.8889 | 15.3421 |  |  | -0.091121 | 0.12231 | -0.04612 | -0.027598 | 0.24001 | 0.01334 | 0.49931 | -0.13816 | 0.18566 | -0.61845 | -0.24848 | 8.8686 | 8.8699 | 2.0087 | 15.9371 | 16.7761 | 17.3042 | 17.6126 | 17.582 | 16.5702 | 14.9236 | 16.8863 | 17.2249 | 17.5014 | 17.5544 | 17.2929 | 16.5061 | 14.7373 | 6.3172 | 8.4484 | 5.2985 | 5.6513 | 5.7199 | 6.5654 | 7.5714 | 16.0137 | 15.5967 | 15.444 | 14.3656 | 14.2518 | 14.1916 |  |  |  | 10.7623 | 9.3284 | 8.9768 | 9.0871 | -0.0583 | 0.001154 | 12.7227 |  |  | 10.6556 |  |  | 16.8921 | 16.0907 | 15.0724 | 16.3951 | 15.6781 | 14.7877 | 10.1689 | 10.5148 | 11.1819 | 10.9641 | 9.4873 |  | 10.5867 | 8.3044 | 9.8387 | 9.305 | 11.0403 | 11.774 |  | 12.2496 |  |  | 11.6545 | 12.5288 | 12.6391 | [6 empty] | 12.588 |  |  | 11.3537 |  |  | 9.287 | 10.3957 | 11.8221 | 7.7295 | 9.1598 | 12.4372 | 7.9707 | 9.5608 | 12.2131 | 9.2072 | 10.4768 | 7.7909 | 10.1776 | 8.1284 | 10.0846 | 7.7306 | 9.6204 | 13.0822 | 10.5287 | 10.1677 | 11.339 | 8.0979 | 9.7089 | 12.6298 | 7.7737 | 10.2366 | 9.717 | 9.7794 | 8.459 | 10.1077 | 0.091665 | 20.9541 | 0.032282 | 0.046959 | -37.9779 | 3.1204 | 14.45 | 0.31 | -0.35409 | 0.40752 | -0.25024 | -0.19358 | 0.57068 | 0.13454 | 0.82311 | 0.39803 | 0.40625 | 0.41805 | 0.37468 | 0.60466 | 0.42831 | 0.41493
42810.4361 | -340 | 18.6394 | 18.673 | 18.6484 | 18.6577 | 17.9962 | 16.6396 | 14.7045 | 16.7426 | 17.231 | 17.3263 | 17.3362 | 16.889 | 15.9305 | 14.5453 | 15.0834 | 15.0601 | 15.6068 | 13.4504 | 13.564 | 14.1262 |  |  |  | 16.6433 | 15.982 | 15.0868 | 10.2289 | 9.4457 | 10.1887 | 17.327 | 16.4443 | 15.2396 | 16.9519 | 16.2382 | 15.2299 | 10.8158 | 12.122 |  | 12.158 | 10.2686 | 10.2173 | 8.6873 |  | 6.4245 | 6.4168 | 5.8844 | 5.9835 | 5.9969 | 6.2273 | 6.5294 | 4.8826 | 6.3837 | 4.6425 | 6.613 | 8.1895 | 42.4345 | 46.6217 | 42.8853 | 15.3471 |  |  | -0.062205 | -0.15762 | 0.12802 | 0.00197 | 0.16642 | 0.18353 | 0.56108 | -0.24001 | -0.22008 | -0.55488 | -0.29041 | 8.8687 | 8.8698 | 2.0087 | 15.9316 | 16.7738 | 17.3005 | 17.6112 | 17.575 | 16.563 | 14.9236 | 16.8815 | 17.216 | 17.5008 | 17.5475 | 17.2984 | 16.4984 | 14.7338 | 6.294 | 8.4255 | 5.2558 | 5.6255 | 5.6975 | 6.5632 | 7.5712 | 16.0095 | 15.5964 | 15.438 | 14.3646 | 14.2473 | 14.1933 |  |  |  | 10.7574 | 9.3264 | 8.9737 | 9.0656 | 0.017067 | 0.011129 | 12.7306 |  |  | 10.6546 |  |  | 16.8913 | 16.0929 | 15.0728 | 16.3917 | 15.6738 | 14.7773 | 10.152 | 10.5106 | 11.184 | 10.9646 | 9.4356 |  | 10.5899 | 8.215 | 9.8393 | 9.2958 | 11.0342 | 11.7977 |  | 12.2528 |  |  | 11.6798 | 12.5339 | 12.6404 | [6 empty] | 12.5885 |  |  | 11.3448 |  |  | 9.2848 | 10.4061 | 11.8289 | 7.7216 | 9.1617 | 12.4401 | 7.9598 | 9.5619 | 12.2083 | 9.2116 | 10.4743 | 7.7759 | 10.1834 | 8.1248 | 10.0883 | 7.7303 | 9.6327 | 13.0925 | 10.5307 | 10.1706 | 11.3548 | 8.1106 | 9.712 | 12.6352 | 7.7951 | 10.2421 | 9.7216 | 9.7729 | 8.4684 | 10.108 | -0.05837 | 20.9559 | 0.032592 | 0.04698 | -37.976 | 3.1204 | 2.4 | 0.35 | -0.29257 | -0.46261 | 0.41691 | 0.051718 | 0.47518 | 0.49902 | 0.87252 | 0.39957 | 0.40875 | 0.4181 | 0.37699 | 0.60939 | 0.4278 | 0.41537
42810.4361 | -339 | 18.634 | 18.6655 | 18.6415 | 18.643 | 17.9923 | 16.6321 | 14.7018 | 16.7363 | 17.2199 | 17.3208 | 17.33 | 16.88 | 15.9276 | 14.5462 | 15.0822 | 15.0526 | 15.5974 | 13.4402 | 13.5579 | 14.1214 |  |  |  | 16.6406 | 15.9777 | 15.0784 | 10.2267 | 9.4367 | 10.2093 | 17.3301 | 16.4428 | 15.2328 | 16.9525 | 16.2397 | 15.2322 | 10.8146 | 12.1401 |  | 12.1557 | 10.2763 | 10.2218 | 8.6898 |  | 6.4237 | 6.4236 | 5.9024 | 5.987 | 6.0026 | 6.2306 | 6.5123 | 4.9117 | 6.3823 | 4.6556 | 6.6176 | 8.1832 | 42.4207 | 46.6236 | 42.8787 | 15.3402 |  |  | -0.18246 | -0.14053 | 0.23513 | -0.032198 | -0.19106 | -0.075372 | 0.53742 | -0.32346 | -0.15411 | -0.38558 | -0.18569 | 8.868 | 8.8692 | 2.0084 | 15.9236 | 16.7721 | 17.3074 | 17.623 | 17.5868 | 16.5723 | 14.9229 | 16.8803 | 17.2137 | 17.5125 | 17.5515 | 17.2926 | 16.5024 | 14.7341 | 6.3045 | 8.4013 | 5.2376 | 5.5887 | 5.7082 | 6.5675 | 7.5791 | 16.0134 | 15.6146 | 15.4578 | 14.3812 | 14.259 | 14.1951 |  |  |  | 10.761 | 9.3374 | 9 | 9.0828 | -0.085043 | -0.050225 | 12.7324 |  |  | 10.6548 |  |  | 16.8938 | 16.0955 | 15.0711 | 16.3929 | 15.6762 | 14.7798 | 10.1364 | 10.511 | 11.1876 | 10.9728 | 9.3976 |  | 10.582 | 8.1777 | 9.8379 | 9.2769 | 11.0334 | 11.8396 |  | 12.2505 |  |  | 11.6915 | 12.5263 | 12.6567 | [6 empty] | 12.5806 |  |  | 11.3378 |  |  | 9.2821 | 10.4137 | 11.8519 | 7.7356 | 9.1691 | 12.4515 | 7.9624 | 9.5637 | 12.2086 | 9.2081 | 10.478 | 7.7806 | 10.1896 | 8.1175 | 10.0975 | 7.747 | 9.6437 | 13.1037 | 10.5341 | 10.1701 | 11.3804 | 8.118 | 9.7254 | 12.6439 | 7.8088 | 10.246 | 9.7279 | 9.7834 | 8.4792 | 10.1172 | 0.16331 | 20.9559 | 0.032213 | 0.046409 | -38.0356 | 3.1205 | -2.52 | 0.2 | -0.5011 | -0.43682 | 0.56502 | -0.20909 | -0.50915 | -0.31979 | 0.85393 | 0.40037 | 0.40974 | 0.4186 | 0.37632 | 0.61233 | 0.42769 | 0.41501
42810.4361 | -338 | 18.6348 | 18.6699 | 18.6428 | 18.6491 | 17.9926 | 16.6392 | 14.7072 | 16.7388 | 17.2258 | 17.315 | 17.3272 | 16.8823 | 15.9279 | 14.5425 | 15.0913 | 15.0611 | 15.5949 | 13.4469 | 13.5622 | 14.1224 |  |  |  | 16.6431 | 15.982 | 15.0873 | 10.2358 | 9.4425 | 10.2296 | 17.3332 | 16.447 | 15.2298 | 16.9564 | 16.2459 | 15.2449 | 10.8222 | 12.1384 |  | 12.1569 | 10.2855 | 10.2212 | 8.7165 |  | 6.417 | 6.4057 | 5.8953 | 5.9899 | 5.9993 | 6.2182 | 6.4957 | 4.9548 | 6.384 | 4.6517 | 6.6139 | 8.1809 | 42.4031 | 46.6163 | 42.8713 | 15.3321 |  |  | 0.063303 | -0.22596 | 0.011708 | 0.058482 | -0.00838 | 0.12636 | 0.46054 | -0.2893 | 0.35672 | -0.35515 | -0.13204 | 8.8668 | 8.8681 | 2.0087 | 15.9275 | 16.7756 | 17.3 | 17.6119 | 17.5778 | 16.5647 | 14.918 | 16.8804 | 17.2166 | 17.5085 | 17.5535 | 17.2896 | 16.4992 | 14.731 | 6.2985 | 8.3847 | 5.2327 | 5.5473 | 5.7275 | 6.5628 | 7.5664 | 16.011 | 15.5992 | 15.4532 | 14.3704 | 14.2513 | 14.1915 |  |  |  | 10.7593 | 9.3253 | 8.9901 | 9.0897 | 0.0118 | -0.14696 | 12.7294 |  |  | 10.652 |  |  | 16.8902 | 16.0935 | 15.0669 | 16.3912 | 15.6727 | 14.7821 | 10.1221 | 10.5076 | 11.1924 | 10.9714 | 9.3762 |  | 10.5845 | 8.1122 | 9.8364 | 9.2641 | 11.0382 | 11.8607 |  | 12.2473 |  |  | 11.7141 | 12.5034 | 12.6589 | [6 empty] | 12.5818 |  |  | 11.3341 |  |  | 9.284 | 10.4164 | 11.8664 | 7.7438 | 9.1727 | 12.4539 | 7.9563 | 9.5638 | 12.2117 | 9.2105 | 10.4829 | 7.781 | 10.1957 | 8.1182 | 10.0872 | 7.7564 | 9.646 | 13.1053 | 10.5421 | 10.1755 | 11.3955 | 8.1299 | 9.7299 | 12.6562 | 7.8261 | 10.2496 | 9.7338 | 9.7954 | 8.4834 | 10.1225 | 0.010196 | 20.955 | 0.033413 | 0.047357 | -38.1067 | 3.1205 | 3.08 | 0.3 | 0.29516 | -0.55388 | 0.12608 | 0.28178 | -0.10663 | 0.41406 | 0.79048 | 0.40104 | 0.41151 | 0.41912 | 0.37645 | 0.61139 | 0.4272 | 0.41476
42810.4361 | -337 | 18.6438 | 18.6798 | 18.6519 | 18.6582 | 17.998 | 16.6479 | 14.7065 | 16.7478 | 17.2289 | 17.3205 | 17.3347 | 16.8846 | 15.9326 | 14.5447 | 15.0864 | 15.0585 | 15.5995 | 13.4469 | 13.5618 | 14.1213 |  |  |  | 16.6461 | 15.9807 | 15.0879 | 10.2436 | 9.4487 | 10.2527 | 17.3302 | 16.441 | 15.2389 | 16.9548 | 16.2433 | 15.2409 | 10.8153 | 12.1352 |  | 12.1593 | 10.2853 | 10.2292 | 8.7467 |  | 6.4165 | 6.4035 | 5.9067 | 5.9916 | 5.9914 | 6.2086 | 6.5105 | 4.998 | 6.3879 | 4.6577 | 6.6201 | 8.1865 | 42.4106 | 46.6058 | 42.874 | 15.3284 |  |  | -0.072721 | -0.20362 | 0.19044 | -0.050598 | -0.11418 | -0.19431 | 0.49668 | -0.38655 | 0.36508 | -0.75671 | -0.28047 | 8.8703 | 8.8715 | 2.0086 | 15.9269 | 16.7817 | 17.3004 | 17.6112 | 17.5805 | 16.5606 | 14.9123 | 16.879 | 17.2183 | 17.5003 | 17.549 | 17.2914 | 16.498 | 14.7355 | 6.2465 | 8.4065 | 5.2226 | 5.5181 | 5.722 | 6.5616 | 7.5674 | 16.0085 | 15.5927 | 15.4486 | 14.367 | 14.2478 | 14.1897 |  |  |  | 10.7531 | 9.3263 | 8.9945 | 9.1126 | 0.035909 | 0.0037888 | 12.7306 |  |  | 10.6444 |  |  | 16.8928 | 16.0896 | 15.072 | 16.3928 | 15.6796 | 14.7824 | 10.1037 | 10.5097 | 11.1962 | 10.9759 | 9.3759 |  | 10.5937 | 8.0376 | 9.8375 | 9.2562 | 11.0372 | 11.9112 |  | 12.251 |  |  | 11.7219 | 12.5069 | 12.6345 | [6 empty] | 12.5811 |  |  | 11.3323 |  |  | 9.2955 | 10.4191 | 11.8723 | 7.7403 | 9.1767 | 12.4539 | 7.9584 | 9.574 | 12.2186 | 9.2068 | 10.4817 | 7.7862 | 10.2106 | 8.12 | 10.085 | 7.7636 | 9.6545 | 13.1027 | 10.5397 | 10.179 | 11.3982 | 8.1236 | 9.7302 | 12.6501 | 7.8285 | 10.2502 | 9.7283 | 9.7942 | 8.4794 | 10.1073 | -0.065304 | 20.952 | 0.033499 | 0.047791 | -37.9622 | 3.1205 | 4.45 | 0.3 | -0.31637 | -0.52578 | 0.50849 | -0.2621 | -0.39358 | -0.51344 | 0.82089 | 0.40135 | 0.41362 | 0.4193 | 0.38209 | 0.61262 | 0.42614 | 0.41392
42810.4361 | -336 | 18.6471 | 18.6852 | 18.6569 | 18.6592 | 17.995 | 16.6491 | 14.7001 | 16.7438 | 17.2311 | 17.3197 | 17.34 | 16.8843 | 15.9309 | 14.5493 | 15.0838 | 15.0551 | 15.588 | 13.4432 | 13.5544 | 14.1187 |  |  |  | 16.6471 | 15.9747 | 15.0874 | 10.2515 | 9.4518 | 10.2586 | 17.327 | 16.4383 | 15.2352 | 16.9503 | 16.2369 | 15.2317 | 10.8187 | 12.1339 |  | 12.1477 | 10.2978 | 10.2229 | 8.7507 |  | 6.401 | 6.3866 | 5.8989 | 5.9829 | 5.9806 | 6.189 | 6.5045 | 5.0378 | 6.3841 | 4.6928 | 6.6181 | 8.1855 | 42.4045 | 46.601 | 42.8695 | 15.3225 |  |  | 0.1139 | -0.071537 | 0.12999 | -0.069654 | 0.07836 | -0.084572 | 0.53939 | -0.2617 | -0.14769 | 0.71881 | -0.2302 | 8.8674 | 8.8684 | 2.0086 | 15.9211 | 16.7779 | 17.2985 | 17.615 | 17.5748 | 16.557 | 14.9154 | 16.8795 | 17.2174 | 17.5038 | 17.5492 | 17.29 | 16.5022 | 14.7296 | 6.2266 | 8.4364 | 5.2263 | 5.4963 | 5.7258 | 6.5641 | 7.5704 | 16.015 | 15.5949 | 15.4459 | 14.3676 | 14.2412 | 14.1898 |  |  |  | 10.7498 | 9.3296 | 9.0044 | 9.1343 | 0.12992 | 0.0056708 | 12.7327 |  |  | 10.6519 |  |  | 16.8936 | 16.091 | 15.0776 | 16.3993 | 15.6827 | 14.7858 | 10.0825 | 10.5075 | 11.1949 | 10.9859 | 9.3636 |  | 10.5826 | 8.0293 | 9.8424 | 9.2822 | 11.0386 | 11.9735 |  | 12.2491 |  |  | 11.7252 | 12.5172 | 12.6159 | [6 empty] | 12.5841 |  |  | 11.3284 |  |  | 9.2972 | 10.4263 | 11.8756 | 7.7378 | 9.1841 | 12.4606 | 7.9703 | 9.5767 | 12.2332 | 9.2093 | 10.4904 | 7.7955 | 10.2191 | 8.1265 | 10.0912 | 7.7675 | 9.6633 | 13.108 | 10.5391 | 10.1851 | 11.4071 | 8.1231 | 9.7376 | 12.6491 | 7.8358 | 10.2419 | 9.7357 | 9.7995 | 8.4786 | 10.1008 | 0.060464 | 20.9537 | 0.033837 | 0.047921 | -37.8709 | 3.1205 | 1.55 | 0.31 | 0.39594 | -0.31164 | 0.42009 | -0.30751 | 0.32605 | -0.33872 | 0.85543 | 0.40133 | 0.41401 | 0.41862 | 0.38459 | 0.61256 | 0.42614 | 0.41321
42810.4362 | -335 | 18.6382 | 18.6796 | 18.6508 | 18.6577 | 17.9896 | 16.6377 | 14.7039 | 16.739 | 17.2317 | 17.3216 | 17.3349 | 16.8877 | 15.9291 | 14.5431 | 15.0862 | 15.0572 | 15.5924 | 13.4477 | 13.5579 | 14.1231 |  |  |  | 16.6449 | 15.981 | 15.0919 | 10.2594 | 9.4608 | 10.2562 | 17.329 | 16.4387 | 15.2294 | 16.9474 | 16.2412 | 15.234 | 10.823 | 12.1521 |  | 12.1606 | 10.3009 | 10.2304 | 8.7781 |  | 6.3934 | 6.381 | 5.8966 | 5.98 | 5.981 | 6.1823 | 6.5013 | 5.0173 | 6.3809 | 4.704 | 6.6259 | 8.1838 | 42.418 | 46.6041 | 42.8701 | 15.3124 |  |  | 0.063959 | -0.20624 | 0.16482 | 0.10383 | 0.044848 | 0.10665 | 0.58868 | -0.33924 | -0.4643 | -0.78566 | -0.30014 | 8.8705 | 8.8718 | 2.0083 | 15.923 | 16.773 | 17.299 | 17.6121 | 17.5739 | 16.5618 | 14.9185 | 16.874 | 17.2082 | 17.5016 | 17.5466 | 17.2957 | 16.5024 | 14.7342 | 6.1934 | 8.4234 | 5.2347 | 5.4663 | 5.7627 | 6.5651 | 7.5728 | 16.0065 | 15.5986 | 15.4479 | 14.3623 | 14.2487 | 14.1933 |  |  |  | 10.7523 | 9.3264 | 9.0142 | 9.1387 | 0.17935 | 0.22812 | 12.726 |  |  | 10.6495 |  |  | 16.8884 | 16.0858 | 15.0679 | 16.3944 | 15.6769 | 14.7813 | 10.0608 | 10.511 | 11.1941 | 10.9892 | 9.3522 |  | 10.5886 | 8.0557 | 9.8377 | 9.3011 | 11.0374 | 12.0229 |  | 12.2589 |  |  | 11.7251 | 12.5228 | 12.6184 | [6 empty] | 12.5703 |  |  | 11.3161 |  |  | 9.2923 | 10.4199 | 11.871 | 7.7323 | 9.1813 | 12.4627 | 7.9721 | 9.5611 | 12.232 | 9.2034 | 10.4852 | 7.7846 | 10.2087 | 8.1224 | 10.0898 | 7.7537 | 9.6636 | 13.1038 | 10.5411 | 10.1859 | 11.4061 | 8.1141 | 9.7319 | 12.6427 | 7.8425 | 10.2284 | 9.7326 | 9.7905 | 8.4808 | 10.095 | 0.06239 | 20.9534 | 0.034021 | 0.048696 | -37.9272 | 3.1205 | 8.51 | 0.25 | 0.2967 | -0.52914 | 0.47302 | 0.37544 | 0.24666 | 0.38038 | 0.89365 | 0.40184 | 0.41312 | 0.41806 | 0.3884 | 0.61191 | 0.42552 | 0.41317
42810.4362 | -334 | 18.6405 | 18.6811 | 18.6464 | 18.6567 | 17.996 | 16.6432 | 14.7101 | 16.7398 | 17.2291 | 17.3274 | 17.34 | 16.886 | 15.9303 | 14.5517 | 15.0839 | 15.0554 | 15.5907 | 13.4431 | 13.5597 | 14.1239 |  |  |  | 16.6394 | 15.9728 | 15.0846 | 10.26 | 9.4583 | 10.2503 | 17.3278 | 16.4297 | 15.2235 | 16.9447 | 16.227 | 15.2307 | 10.8117 | 12.1332 |  | 12.1435 | 10.3047 | 10.2225 | 8.7628 |  | 6.3894 | 6.3677 | 5.8977 | 5.9842 | 5.9772 | 6.1809 | 6.5252 | 4.9782 | 6.3837 | 4.7175 | 6.6266 | 8.1832 | 42.4309 | 46.6054 | 42.8567 | 15.3042 |  |  | -0.081921 | -0.092565 | 0.11619 | -0.034826 | 0.22884 | -0.14174 | 0.44477 | -0.1697 | 0.065012 | -0.31445 | -0.17 | 8.8693 | 8.8706 | 2.0086 | 15.9297 | 16.7755 | 17.2935 | 17.6156 | 17.581 | 16.5657 | 14.9187 | 16.8774 | 17.2097 | 17.5048 | 17.547 | 17.2927 | 16.5 | 14.7331 | 6.1447 | 8.376 | 5.2784 | 5.4527 | 5.751 | 6.5674 | 7.5773 | 16.0223 | 15.6153 | 15.4582 | 14.3693 | 14.2674 | 14.1984 |  |  |  | 10.7581 | 9.338 | 9.0284 | 9.1565 | 0.14936 | 0.13703 | 12.7268 |  |  | 10.6451 |  |  | 16.8872 | 16.0791 | 15.0585 | 16.3864 | 15.6726 | 14.7735 | 10.0382 | 10.5155 | 11.1953 | 10.9927 | 9.3605 |  | 10.5853 | 8.0432 | 9.8349 | 9.2908 | 11.034 | 12.0543 |  | 12.2557 |  |  | 11.7312 | 12.537 | 12.6106 | [6 empty] | 12.5443 |  |  | 11.3066 |  |  | 9.2882 | 10.4175 | 11.8723 | 7.7294 | 9.179 | 12.461 | 7.9567 | 9.564 | 12.2413 | 9.1968 | 10.4801 | 7.7745 | 10.1987 | 8.1258 | 10.0842 | 7.7363 | 9.6609 | 13.1023 | 10.5354 | 10.1845 | 11.4098 | 8.1117 | 9.7232 | 12.6456 | 7.857 | 10.2207 | 9.7245 | 9.7819 | 8.4783 | 10.0975 | 0.010196 | 20.9542 | 0.03355 | 0.048848 | -38.0109 | 3.1205 | 1.02 | 0.37 | -0.33579 | -0.35448 | 0.39715 | -0.21743 | 0.55718 | -0.4385 | 0.77677 | 0.4015 | 0.41338 | 0.41824 | 0.39407 | 0.60757 | 0.42557 | 0.41287
42810.4362 | -333 | 18.6375 | 18.6771 | 18.6439 | 18.654 | 17.9958 | 16.6462 | 14.7114 | 16.741 | 17.2266 | 17.3293 | 17.3392 | 16.8872 | 15.9275 | 14.5462 | 15.079 | 15.0524 | 15.5904 | 13.4451 | 13.562 | 14.1191 |  |  |  | 16.643 | 15.9812 | 15.0911 | 10.2671 | 9.461 | 10.2414 | 17.3233 | 16.4304 | 15.2229 | 16.9466 | 16.2314 | 15.2354 | 10.8141 | 12.0998 |  | 12.1471 | 10.3135 | 10.222 | 8.7431 |  | 6.3829 | 6.3598 | 5.8948 | 5.9801 | 5.9772 | 6.1804 | 6.5466 | 4.9738 | 6.3862 | 4.7942 | 6.6258 | 8.1867 | 42.4193 | 46.5964 | 42.8423 | 15.2924 |  |  | 0.16055 | -0.16616 | 0.00448 | 0.08017 | 0.21373 | 0.006112 | 0.67804 | -0.25052 | 0.046525 | -0.06563 | -0.12271 | 8.8697 | 8.8708 | 2.0086 | 15.9383 | 16.7841 | 17.2942 | 17.6217 | 17.5797 | 16.5725 | 14.9171 | 16.8822 | 17.212 | 17.5088 | 17.5485 | 17.2917 | 16.5073 | 14.7347 | 6.1124 | 8.335 | 5.3062 | 5.5027 | 5.7135 | 6.5658 | 7.579 | 16.0179 | 15.6087 | 15.4576 | 14.3721 | 14.2688 | 14.1958 |  |  |  | 10.7576 | 9.3407 | 9.0254 | 9.1631 | 0.10581 | 0.094313 | 12.7297 |  |  | 10.6437 |  |  | 16.888 | 16.081 | 15.0577 | 16.3849 | 15.6688 | 14.7736 | 10.0292 | 10.5141 | 11.2007 | 11.0004 | 9.4055 |  | 10.5954 | 8.0538 | 9.843 | 9.2834 | 11.0412 | 12.0638 |  | 12.2532 |  |  | 11.7369 | 12.5517 | 12.6007 | [6 empty] | 12.5417 |  |  | 11.2982 |  |  | 9.2949 | 10.4126 | 11.8739 | 7.7375 | 9.1783 | 12.4607 | 7.9375 | 9.5607 | 12.2672 | 9.1976 | 10.4874 | 7.7577 | 10.195 | 8.1341 | 10.0808 | 7.7178 | 9.6713 | 13.1038 | 10.5361 | 10.199 | 11.4216 | 8.1232 | 9.7387 | 12.6492 | 7.8726 | 10.2216 | 9.732 | 9.7783 | 8.4719 | 10.0933 | 0.020403 | 20.9525 | 0.033401 | 0.049014 | -38.0152 | 3.1205 | 18.99 | 0.24 | 0.47008 | -0.47493 | 0.077984 | 0.32989 | 0.53846 | 0.091058 | 0.95908 | 0.40059 | 0.41335 | 0.41868 | 0.39748 | 0.60469 | 0.4262 | 0.41267
42810.4362 | -332 | 18.6394 | 18.6786 | 18.6511 | 18.6508 | 17.9935 | 16.6383 | 14.7088 | 16.7396 | 17.2245 | 17.3217 | 17.3384 | 16.8873 | 15.9262 | 14.5439 | 15.0767 | 15.055 | 15.5893 | 13.4449 | 13.5577 | 14.1245 |  |  |  | 16.6473 | 15.9748 | 15.0838 | 10.2712 | 9.467 | 10.2322 | 17.3302 | 16.4335 | 15.2235 | 16.9449 | 16.2299 | 15.2385 | 10.815 | 12.0523 |  | 12.1441 | 10.3139 | 10.2228 | 8.7159 |  | 6.3761 | 6.361 | 5.8898 | 5.9811 | 5.984 | 6.2137 | 6.6255 | 4.995 | 6.3823 | 4.8533 | 6.6217 | 8.1751 | 42.4056 | 46.5817 | 42.8331 | 15.2825 |  |  | 0.12704 | 0.15714 | 0.097788 | 0.044686 | 0.18218 | 0.059336 | 0.57554 | -0.18416 | 0.039519 | -0.0096136 | -0.13383 | 8.8689 | 8.8699 | 2.0084 | 15.9309 | 16.7813 | 17.2927 | 17.6235 | 17.5864 | 16.5786 | 14.92 | 16.8767 | 17.2182 | 17.5113 | 17.553 | 17.2875 | 16.4995 | 14.7266 | 6.0792 | 8.3218 | 5.3051 | 5.4903 | 5.7041 | 6.5591 | 7.5776 | 16.0156 | 15.6027 | 15.4556 | 14.3751 | 14.2583 | 14.1956 |  |  |  | 10.7573 | 9.3438 | 9.0266 | 9.1734 | 0.05313 | 0.022985 | 12.7223 |  |  | 10.6416 |  |  | 16.8858 | 16.0833 | 15.0597 | 16.386 | 15.6701 | 14.7785 | 10.0272 | 10.5133 | 11.206 | 11.0008 | 9.396 |  | 10.6055 | 8.0391 | 9.848 | 9.2728 | 11.0478 | 12.0368 |  | 12.2553 |  |  | 11.7332 | 12.5647 | 12.5942 | [6 empty] | 12.534 |  |  | 11.2924 |  |  | 9.288 | 10.4093 | 11.8806 | 7.729 | 9.1793 | 12.4681 | 7.9347 | 9.5607 | 12.2801 | 9.1906 | 10.4855 | 7.7402 | 10.1674 | 8.1448 | 10.0765 | 7.7142 | 9.6712 | 13.1001 | 10.5324 | 10.1967 | 11.4227 | 8.1116 | 9.7266 | 12.6482 | 7.8786 | 10.2116 | 9.7328 | 9.7714 | 8.4675 | 10.0964 | -0.086875 | 20.9528 | 0.032839 | 0.049195 | -38.0095 | 3.1205 | 16.84 | 0.31 | 0.41815 | 0.46186 | 0.36434 | 0.24629 | 0.49717 | 0.28373 | 0.88367 | 0.40118 | 0.41392 | 0.41919 | 0.40039 | 0.60465 | 0.42698 | 0.41237
42810.4362 | -331 | 18.6406 | 18.6812 | 18.6488 | 18.6495 | 17.9942 | 16.6378 | 14.7082 | 16.7401 | 17.2291 | 17.3202 | 17.3367 | 16.8917 | 15.9343 | 14.5504 | 15.0768 | 15.0663 | 15.6005 | 13.4553 | 13.5644 | 14.1271 |  |  |  | 16.6485 | 15.9784 | 15.095 | 10.282 | 9.4727 | 10.237 | 17.3203 | 16.4338 | 15.2227 | 16.9452 | 16.2308 | 15.2303 | 10.812 | 12.0118 |  | 12.145 | 10.3067 | 10.2171 | 8.7119 |  | 6.3818 | 6.3628 | 5.8911 | 5.9863 | 6.0134 | 6.2386 | 6.6582 | 5.0493 | 6.3816 | 4.8884 | 6.624 | 8.18 | 42.4029 | 46.5677 | 42.8364 | 15.2908 |  |  | 0.099443 | -0.082709 | -0.074376 | 0.22868 | 0.28404 | 0.11388 | 0.45791 | -0.16576 | -0.56179 | -0.56663 | -0.30213 | 8.8678 | 8.8687 | 2.0087 | 15.9323 | 16.777 | 17.3034 | 17.6147 | 17.5816 | 16.5655 | 14.9176 | 16.8728 | 17.2125 | 17.5041 | 17.549 | 17.2907 | 16.5035 | 14.7228 | 6.0741 | 8.3452 | 5.3159 | 5.5289 | 5.7252 | 6.5715 | 7.5853 | 16.0055 | 15.6051 | 15.4472 | 14.3689 | 14.2566 | 14.1956 |  |  |  | 10.74 | 9.3466 | 9.032 | 9.1772 | 0.0083554 | 0.19462 | 12.7265 |  |  | 10.6487 |  |  | 16.8921 | 16.0879 | 15.0651 | 16.3881 | 15.6781 | 14.7846 | 10.0403 | 10.5157 | 11.2094 | 11.0031 | 9.3679 |  | 10.5931 | 8.0485 | 9.8412 | 9.2558 | 11.0436 | 11.9881 |  | 12.2546 |  |  | 11.7354 | 12.569 | 12.5922 | [6 empty] | 12.498 |  |  | 11.2835 |  |  | 9.2891 | 10.417 | 11.8829 | 7.7071 | 9.1521 | 12.4615 | 7.9371 | 9.563 | 12.2895 | 9.2029 | 10.4942 | 7.7435 | 10.151 | 8.1515 | 10.0755 | 7.6997 | 9.6862 | 13.0956 | 10.53 | 10.1995 | 11.4142 | 8.1161 | 9.7372 | 12.6413 | 7.8854 | 10.2162 | 9.7377 | 9.761 | 8.4621 | 10.0949 | -0.062222 | 20.9536 | 0.033613 | 0.050208 | -37.9731 | 3.1205 | 4.4 | 0.35 | 0.36995 | -0.33508 | -0.31775 | 0.55716 | 0.62081 | 0.39309 | 0.78825 | 0.40156 | 0.41344 | 0.41952 | 0.4024 | 0.60433 | 0.42699 | 0.4117
42810.4362 | -330 | 18.6316 | 18.674 | 18.6496 | 18.6475 | 17.9927 | 16.6372 | 14.7081 | 16.7355 | 17.2273 | 17.3157 | 17.3396 | 16.8921 | 15.9289 | 14.5461 | 15.0711 | 15.0476 | 15.5787 | 13.4339 | 13.5455 | 14.112 |  |  |  | 16.6287 | 15.9651 | 15.0695 | 10.2693 | 9.4622 | 10.189 | 17.3268 | 16.4368 | 15.2306 | 16.9507 | 16.2327 | 15.2319 | 10.8086 | 11.9829 |  | 12.1507 | 10.3105 | 10.2217 | 8.7273 |  | 6.3748 | 6.3564 | 5.8871 | 5.9778 | 6.0091 | 6.2206 | 6.6514 | 5.019 | 6.3802 | 4.8696 | 6.624 | 8.173 | 42.4012 | 46.5481 | 42.8402 | 15.29 |  |  | 0.079075 | -0.11557 | -0.001436 | 0.018398 | 0.26695 | 0.019912 | 0.63468 | -0.22424 | -0.30862 | 0.21634 | -0.20536 | 8.8701 | 8.8709 | 2.0085 | 15.9219 | 16.7706 | 17.2974 | 17.6085 | 17.5765 | 16.5628 | 14.913 | 16.8701 | 17.2085 | 17.4966 | 17.5447 | 17.2864 | 16.4917 | 14.7249 | 6.0557 | 8.3844 | 5.3125 | 5.5681 | 5.7403 | 6.5548 | 7.5862 | 16.0134 | 15.6111 | 15.456 | 14.3651 | 14.2543 | 14.1976 |  |  |  | 10.7568 | 9.3589 | 9.0504 | 9.1793 | 0.19475 | 0.028443 | 12.7306 |  |  | 10.6497 |  |  | 16.8922 | 16.0897 | 15.074 | 16.3907 | 15.68 | 14.7805 | 10.0546 | 10.5135 | 11.2177 | 10.9961 | 9.3612 |  | 10.5892 | 8.1364 | 9.8317 | 9.2612 | 11.0382 | 11.8708 |  | 12.2549 |  |  | 11.7464 | 12.5423 | 12.5776 | [6 empty] | 12.4964 |  |  | 11.2799 |  |  | 9.274 | 10.407 | 11.8731 | 7.6893 | 9.1141 | 12.4491 | 7.9162 | 9.5507 | 12.2782 | 9.197 | 10.4864 | 7.7181 | 10.1265 | 8.1564 | 10.0743 | 7.6869 | 9.6773 | 13.0942 | 10.5241 | 10.1951 | 11.4111 | 8.0966 | 9.7238 | 12.6246 | 7.8971 | 10.2066 | 9.7322 | 9.7563 | 8.4698 | 10.0827 | -0.18664 | 20.9499 | 0.03378 | 0.050643 | -37.9707 | 3.1205 | 3.71 | 0.35 | 0.32987 | -0.39607 | -0.044151 | 0.15803 | 0.60183 | 0.16437 | 0.92797 | 0.40161 | 0.41068 | 0.4192 | 0.40249 | 0.60482 | 0.42645 | 0.41219
42810.4362 | -329 | 18.6296 | 18.6819 | 18.6424 | 18.6507 | 17.9937 | 16.6326 | 14.7026 | 16.742 | 17.2287 | 17.3199 | 17.3378 | 16.8916 | 15.931 | 14.5419 | 15.0753 | 15.064 | 15.5913 | 13.4562 | 13.5558 | 14.1317 |  |  |  | 16.6503 | 15.9781 | 15.0832 | 10.2786 | 9.4783 | 10.1924 | 17.3304 | 16.4306 | 15.2325 | 16.9496 | 16.2313 | 15.2314 | 10.8045 | 11.9697 |  | 12.1494 | 10.3019 | 10.2213 | 8.7332 |  | 6.381 | 6.3676 | 5.8888 | 5.9852 | 6.0203 | 6.22 | 6.6759 | 5.0012 | 6.3873 | 4.8644 | 6.6256 | 8.1758 | 42.3939 | 46.544 | 42.8485 | 15.3052 |  |  | 0.083015 | -0.12017 | 0.18059 | -0.014458 | -0.043864 | -0.079972 | 0.63796 | -0.16838 | -0.29772 | -0.54251 | -0.28783 | 8.8685 | 8.8696 | 2.0084 | 15.9355 | 16.7786 | 17.3033 | 17.6147 | 17.5835 | 16.5689 | 14.9203 | 16.8834 | 17.2174 | 17.5032 | 17.5496 | 17.2961 | 16.504 | 14.7278 | 6.0919 | 8.4029 | 5.35 | 5.6032 | 5.7597 | 6.5664 | 7.5743 | 16.0043 | 15.5987 | 15.4484 | 14.3688 | 14.2518 | 14.1874 |  |  |  | 10.7406 | 9.3528 | 9.0443 | 9.153 | 0.099931 | 0.12593 | 12.7213 |  |  | 10.6415 |  |  | 16.8847 | 16.0821 | 15.0688 | 16.3825 | 15.6686 | 14.7768 | 10.0528 | 10.5037 | 11.2116 | 10.9576 | 9.3432 |  | 10.5849 | 8.2444 | 9.8309 | 9.2541 | 11.0366 | 11.7627 |  | 12.2478 |  |  | 11.7504 | 12.5514 | 12.5756 | [6 empty] | 12.46 |  |  | 11.2825 |  |  | 9.2782 | 10.4226 | 11.8778 | 7.6727 | 9.0911 | 12.4484 | 7.9229 | 9.5605 | 12.2924 | 9.2144 | 10.4846 | 7.7174 | 10.135 | 8.1484 | 10.0838 | 7.6789 | 9.687 | 13.0942 | 10.5281 | 10.1923 | 11.4208 | 8.1031 | 9.7514 | 12.6399 | 7.8983 | 10.2166 | 9.7346 | 9.7577 | 8.4781 | 10.0883 | 0.019826 | 20.9452 | 0.03312 | 0.050078 | -38.0068 | 3.1205 | 17.57 | 0.27 | 0.33799 | -0.40389 | 0.49513 | -0.1401 | -0.24396 | -0.3294 | 0.93037 | 0.40197 | 0.40766 | 0.41934 | 0.39983 | 0.59928 | 0.42616 | 0.41239
42810.4362 | -328 | 18.6287 | 18.6742 | 18.6415 | 18.6466 | 17.9848 | 16.6353 | 14.6948 | 16.7238 | 17.2201 | 17.3141 | 17.3251 | 16.8754 | 15.9263 | 14.5418 | 15.0711 | 15.0482 | 15.5821 | 13.4407 | 13.5463 | 14.1177 |  |  |  | 16.6378 | 15.9715 | 15.0807 | 10.2711 | 9.463 | 10.1426 | 17.3298 | 16.45 | 15.2462 | 16.9566 | 16.2371 | 15.2336 | 10.8219 | 11.9864 |  | 12.1529 | 10.2994 | 10.2209 | 8.7436 |  | 6.3696 | 6.3613 | 5.8786 | 5.971 | 6.0195 | 6.2408 | 6.7361 | 4.9521 | 6.3721 | 4.8416 | 6.6158 | 8.1805 | 42.396 | 46.5454 | 42.8562 | 15.3221 |  |  | 0.084987 | -0.20165 | 0.12079 | -0.033514 | 0.2249 | 0.17762 | 0.39088 | -0.067188 | -0.50614 | -0.64258 | -0.24053 | 8.8698 | 8.871 | 2.0085 | 15.9301 | 16.7736 | 17.2995 | 17.6066 | 17.5789 | 16.5627 | 14.915 | 16.8778 | 17.2111 | 17.5005 | 17.5474 | 17.296 | 16.5067 | 14.7231 | 6.1489 | 8.4034 | 5.3801 | 5.6181 | 5.7762 | 6.5652 | 7.5768 | 16.0078 | 15.6079 | 15.4464 | 14.372 | 14.2565 | 14.1906 |  |  |  | 10.7522 | 9.3626 | 9.0483 | 9.1415 | 0.12992 | 0.099206 | 12.7232 |  |  | 10.638 |  |  | 16.8858 | 16.0769 | 15.0604 | 16.3816 | 15.6642 | 14.7781 | 10.062 | 10.4984 | 11.1922 | 10.9176 | 9.3441 |  | 10.5873 | 8.3398 | 9.8425 | 9.2926 | 11.0375 | 11.7352 |  | 12.2484 |  |  | 11.7643 | 12.5478 | 12.5627 | [6 empty] | 12.4851 |  |  | 11.2911 |  |  | 9.2615 | 10.4092 | 11.8778 | 7.6606 | 9.0716 | 12.4482 | 7.9162 | 9.5514 | 12.2899 | 9.2032 | 10.48 | 7.7121 | 10.1284 | 8.1402 | 10.0735 | 7.6876 | 9.6857 | 13.0887 | 10.529 | 10.1855 | 11.421 | 8.0947 | 9.7386 | 12.6341 | 7.9054 | 10.226 | 9.7319 | 9.7573 | 8.4708 | 10.0832 | -0.051244 | 20.9486 | 0.03316 | 0.050773 | -37.9882 | 3.1206 | -1.51 | 0.33 | 0.34195 | -0.52319 | 0.40493 | -0.21329 | 0.55241 | 0.49093 | 0.72828 | 0.40203 | 0.40539 | 0.4183 | 0.39335 | 0.59622 | 0.42644 | 0.41309
42810.4362 | -327 | 18.6432 | 18.6808 | 18.6509 | 18.6539 | 17.995 | 16.6436 | 14.7096 | 16.7438 | 17.231 | 17.3175 | 17.3335 | 16.887 | 15.939 | 14.5476 | 15.0748 | 15.0495 | 15.5856 | 13.4401 | 13.5488 | 14.1239 |  |  |  | 16.6343 | 15.9673 | 15.077 | 10.2714 | 9.4758 | 10.1245 | 17.3248 | 16.4413 | 15.2308 | 16.9465 | 16.2346 | 15.2327 | 10.8118 | 11.9685 |  | 12.1475 | 10.2923 | 10.2217 | 8.7566 |  | 6.3768 | 6.3696 | 5.8872 | 5.982 | 6.0662 | 6.2957 | 6.8275 | 4.9118 | 6.376 | 4.8132 | 6.6259 | 8.1696 | 42.3917 | 46.5455 | 42.8551 | 15.3283 |  |  | 0.20064 | -0.14382 | 0.16482 | -0.040742 | 0.33201 | 0.042252 | 0.18849 | -0.17233 | -0.90468 | -0.039405 | -0.30074 | 8.8689 | 8.8704 | 2.0085 | 15.9152 | 16.7665 | 17.2916 | 17.5982 | 17.5716 | 16.556 | 14.9115 | 16.8774 | 17.2105 | 17.5025 | 17.5453 | 17.284 | 16.4979 | 14.7199 | 6.2308 | 8.4185 | 5.3808 | 5.6325 | 5.8097 | 6.5681 | 7.5767 | 16.006 | 15.5983 | 15.443 | 14.3633 | 14.2542 | 14.1902 |  |  |  | 10.7447 | 9.3738 | 9.0499 | 9.1193 | -0.080991 | 0.04651 | 12.7293 |  |  | 10.6382 |  |  | 16.8889 | 16.078 | 15.0613 | 16.3853 | 15.6676 | 14.772 | 10.0673 | 10.507 | 11.1796 | 10.8906 | 9.3161 |  | 10.5921 | 8.3666 | 9.8429 | 9.3334 | 11.0388 | 11.7484 |  | 12.2437 |  |  | 11.7856 | 12.5471 | 12.5572 | [6 empty] | 12.4865 |  |  | 11.286 |  |  | 9.2608 | 10.4028 | 11.8849 | 7.6708 | 9.0641 | 12.4545 | 7.9021 | 9.549 | 12.2871 | 9.2097 | 10.4775 | 7.7131 | 10.131 | 8.126 | 10.0788 | 7.6975 | 9.691 | 13.0925 | 10.5135 | 10.1871 | 11.4248 | 8.0927 | 9.7495 | 12.6345 | 7.9212 | 10.2159 | 9.7283 | 9.7793 | 8.4796 | 10.0931 | 0.21917 | 20.9537 | 0.032902 | 0.051026 | -37.9139 | 3.1205 | 14.2 | 0.32 | 0.52539 | -0.44186 | 0.47301 | -0.23518 | 0.67126 | 0.23946 | 0.50578 | 0.40296 | 0.40466 | 0.41721 | 0.38459 | 0.59612 | 0.42575 | 0.41346
42810.4363 | -326 | 18.6388 | 18.6761 | 18.6527 | 18.6539 | 17.9969 | 16.6454 | 14.7106 | 16.7477 | 17.2319 | 17.3151 | 17.3403 | 16.8849 | 15.9382 | 14.5498 | 15.0729 | 15.0481 | 15.588 | 13.4425 | 13.5457 | 14.1166 |  |  |  | 16.6385 | 15.9631 | 15.0755 | 10.2663 | 9.481 | 10.1083 | 17.3251 | 16.4417 | 15.2298 | 16.9589 | 16.2294 | 15.2341 | 10.8179 | 11.9593 |  | 12.1503 | 10.2925 | 10.2223 | 8.761 |  | 6.3919 | 6.384 | 5.9014 | 6.0191 | 6.0755 | 6.3263 | 6.882 | 4.8595 | 6.3839 | 4.7607 | 6.6247 | 8.1758 | 42.3763 | 46.5368 | 42.8577 | 15.33 |  |  | 0.014019 | -0.084681 | 0.02682 | -0.16099 | 0.018564 | -0.14962 | 0.1471 | -0.1605 | -0.4643 | 0.009688 | -0.26617 | 8.8692 | 8.8701 | 2.0085 | 15.9148 | 16.7697 | 17.2942 | 17.6079 | 17.5729 | 16.5543 | 14.9135 | 16.8747 | 17.2137 | 17.5053 | 17.5467 | 17.2844 | 16.4982 | 14.7262 | 6.3105 | 8.3898 | 5.3993 | 5.6536 | 5.8308 | 6.5727 | 7.5826 | 16.0067 | 15.595 | 15.4489 | 14.3743 | 14.2517 | 14.193 |  |  |  | 10.7475 | 9.3838 | 9.0576 | 9.1264 | 0.061842 | -0.037239 | 12.7329 |  |  | 10.6348 |  |  | 16.8847 | 16.0783 | 15.0612 | 16.3845 | 15.6678 | 14.7712 | 10.0751 | 10.5143 | 11.171 | 10.8631 | 9.2699 |  | 10.5881 | 8.347 | 9.8359 | 9.3516 | 11.0386 | 11.7707 |  | 12.2415 |  |  | 11.8034 | 12.5466 | 12.5734 | [6 empty] | 12.5017 |  |  | 11.2946 |  |  | 9.2607 | 10.4037 | 11.8881 | 7.6704 | 9.0629 | 12.4519 | 7.9045 | 9.5447 | 12.2853 | 9.2074 | 10.4856 | 7.7095 | 10.1343 | 8.1319 | 10.0866 | 7.6867 | 9.6967 | 13.0913 | 10.5104 | 10.181 | 11.4265 | 8.0964 | 9.7393 | 12.6403 | 7.9385 | 10.2276 | 9.7241 | 9.7723 | 8.4782 | 10.0923 | -0.064726 | 20.9546 | 0.032293 | 0.050404 | -37.9252 | 3.1206 | 11.79 | 0.26 | 0.13887 | -0.33906 | 0.19082 | -0.46751 | 0.15874 | -0.45065 | 0.44683 | 0.40412 | 0.40498 | 0.4167 | 0.37627 | 0.59476 | 0.42583 | 0.41335
42810.4363 | -325 | 18.6314 | 18.6766 | 18.6566 | 18.655 | 17.9957 | 16.6383 | 14.7071 | 16.7499 | 17.2369 | 17.3248 | 17.3416 | 16.8863 | 15.9395 | 14.5542 | 15.0783 | 15.0589 | 15.5952 | 13.4473 | 13.5603 | 14.1227 |  |  |  | 16.6471 | 15.9781 | 15.0825 | 10.2733 | 9.4942 | 10.0827 | 17.3242 | 16.4372 | 15.232 | 16.9463 | 16.2315 | 15.2344 | 10.8073 | 11.9299 |  | 12.1451 | 10.2931 | 10.2189 | 8.7786 |  | 6.3965 | 6.398 | 5.9298 | 6.0361 | 6.0564 | 6.3019 | 6.8576 | 4.8496 | 6.382 | 4.6772 | 6.6307 | 8.173 | 42.3666 | 46.5427 | 42.8812 | 15.328 |  |  | 0.13099 | -0.13265 | 0.1727 | -0.023658 | -0.074088 | -0.16211 | 0.26603 | -0.10464 | -0.55537 | -0.35452 | -0.29895 | 8.8701 | 8.8714 | 2.0086 | 15.9264 | 16.7643 | 17.2934 | 17.6062 | 17.5689 | 16.5576 | 14.9129 | 16.8757 | 17.2123 | 17.4934 | 17.5484 | 17.2892 | 16.5036 | 14.7215 | 6.3378 | 8.3735 | 5.4085 | 5.6623 | 5.8352 | 6.573 | 7.5788 | 16.0113 | 15.6069 | 15.4449 | 14.3657 | 14.2586 | 14.1888 |  |  |  | 10.7565 | 9.3845 | 9.057 | 9.1298 | 0.035099 | 0.027314 | 12.7328 |  |  | 10.6367 |  |  | 16.8841 | 16.0829 | 15.0623 | 16.3874 | 15.6687 | 14.7818 | 10.0911 | 10.5196 | 11.1731 | 10.8573 | 9.2462 |  | 10.5779 | 8.3047 | 9.8313 | 9.3526 | 11.0337 | 11.7919 |  | 12.2356 |  |  | 11.7995 | 12.5498 | 12.5733 | [6 empty] | 12.4986 |  |  | 11.2919 |  |  | 9.2588 | 10.4027 | 11.8947 | 7.6877 | 9.0743 | 12.4691 | 7.9052 | 9.5479 | 12.2889 | 9.2181 | 10.4878 | 7.7119 | 10.1511 | 8.1384 | 10.0847 | 7.6936 | 9.6976 | 13.089 | 10.5125 | 10.1812 | 11.4292 | 8.0899 | 9.7383 | 12.6305 | 7.9414 | 10.2338 | 9.7288 | 9.7757 | 8.4851 | 10.0905 | -0.0011678 | 20.9527 | 0.031283 | 0.050925 | -38.0194 | 3.1205 | 9.06 | 0.39 | 0.42448 | -0.42437 | 0.48422 | -0.17922 | -0.3171 | -0.46906 | 0.60088 | 0.40443 | 0.406 | 0.41651 | 0.37328 | 0.59331 | 0.42499 | 0.41356
42810.4363 | -324 | 18.6313 | 18.6762 | 18.6538 | 18.6561 | 17.9943 | 16.6338 | 14.7074 | 16.7494 | 17.236 | 17.3333 | 17.3372 | 16.8902 | 15.9374 | 14.5569 | 15.0761 | 15.0532 | 15.5955 | 13.4457 | 13.554 | 14.1237 |  |  |  | 16.6479 | 15.9804 | 15.0818 | 10.275 | 9.4882 | 10.0476 | 17.3299 | 16.44 | 15.2369 | 16.9511 | 16.2344 | 15.2391 | 10.8025 | 11.8896 |  | 12.1513 | 10.3068 | 10.2259 | 8.7944 |  | 6.4049 | 6.4043 | 5.9495 | 6.0571 | 6.0542 | 6.2943 | 6.8143 | 4.7893 | 6.3724 | 4.5491 | 6.6209 | 8.1779 | 42.3731 | 46.5576 | 42.8943 | 15.3284 |  |  | 0.15661 | 0.073027 | 0.051136 | 0.04797 | -0.043204 | -0.092456 | 0.56634 | -0.20584 | 0.19578 | -1.0788 | -0.15549 | 8.8704 | 8.8714 | 2.0086 | 15.919 | 16.7735 | 17.2935 | 17.6089 | 17.5726 | 16.5599 | 14.9052 | 16.8754 | 17.207 | 17.4906 | 17.5362 | 17.2823 | 16.4952 | 14.7251 | 6.3174 | 8.4013 | 5.4117 | 5.6872 | 5.8217 | 6.5714 | 7.5844 | 16.004 | 15.5954 | 15.4448 | 14.3536 | 14.2576 | 14.1811 |  |  |  | 10.7445 | 9.3866 | 9.0491 | 9.1224 | -0.084435 | -0.024818 | 12.7332 |  |  | 10.6461 |  |  | 16.8859 | 16.0916 | 15.0623 | 16.389 | 15.6696 | 14.7805 | 10.0983 | 10.5237 | 11.1733 | 10.8703 | 9.2457 |  | 10.5761 | 8.2675 | 9.8271 | 9.3527 | 11.029 | 11.8083 |  | 12.2404 |  |  | 11.788 | 12.5606 | 12.5613 | [6 empty] | 12.5132 |  |  | 11.2967 |  |  | 9.2548 | 10.4001 | 11.8974 | 7.6886 | 9.0642 | 12.4776 | 7.8981 | 9.553 | 12.2931 | 9.2157 | 10.4865 | 7.7084 | 10.1614 | 8.1386 | 10.0843 | 7.7092 | 9.7057 | 13.0862 | 10.5138 | 10.1888 | 11.4395 | 8.0944 | 9.7381 | 12.6325 | 7.9586 | 10.2499 | 9.7379 | 9.7877 | 8.4918 | 10.0954 | 0.033115 | 20.9518 | 0.031065 | 0.050237 | -38.0244 | 3.1205 | -4.87 | 0.39 | 0.46411 | 0.31488 | 0.26349 | 0.2552 | -0.24215 | -0.35423 | 0.8767 | 0.40439 | 0.40689 | 0.41635 | 0.37536 | 0.59359 | 0.42439 | 0.41337
42810.4363 | -323 | 18.6204 | 18.6696 | 18.6479 | 18.6452 | 17.9858 | 16.6314 | 14.7002 | 16.7341 | 17.2242 | 17.3225 | 17.3295 | 16.8817 | 15.9247 | 14.5422 | 15.0725 | 15.0548 | 15.5929 | 13.4438 | 13.5501 | 14.1203 |  |  |  | 16.6469 | 15.9779 | 15.0789 | 10.2691 | 9.4846 | 10.0286 | 17.3202 | 16.4342 | 15.2304 | 16.9486 | 16.2297 | 15.2252 | 10.7969 | 11.8381 |  | 12.1436 | 10.3134 | 10.2207 | 8.7942 |  | 6.4074 | 6.4027 | 5.9485 | 6.0574 | 6.0426 | 6.2835 | 6.7829 | 4.7359 | 6.3686 | 4.4749 | 6.6153 | 8.1753 | 42.3824 | 46.5505 | 42.8972 | 15.3298 |  |  | 0.11784 | -0.17602 | 0.03602 | -0.18399 | -0.056348 | 0.04948 | 0.51048 | -0.30572 | -0.34637 | -0.34823 | -0.2767 | 8.8695 | 8.8702 | 2.0087 | 15.9224 | 16.7708 | 17.3017 | 17.6135 | 17.5758 | 16.5613 | 14.9032 | 16.8768 | 17.2108 | 17.499 | 17.5433 | 17.292 | 16.4981 | 14.7235 | 6.2647 | 8.3918 | 5.3966 | 5.6945 | 5.8126 | 6.5654 | 7.5759 | 16.0066 | 15.5957 | 15.4465 | 14.3625 | 14.2571 | 14.1874 |  |  |  | 10.7425 | 9.3792 | 9.0473 | 9.1222 | 0.029223 | -0.055118 | 12.7399 |  |  | 10.6483 |  |  | 16.8881 | 16.0903 | 15.0637 | 16.3941 | 15.6723 | 14.7749 | 10.1016 | 10.5197 | 11.1762 | 10.8773 | 9.2536 |  | 10.5866 | 8.2379 | 9.8331 | 9.3489 | 11.0348 | 11.8377 |  | 12.2407 |  |  | 11.776 | 12.5697 | 12.5456 | [6 empty] | 12.5208 |  |  | 11.2745 |  |  | 9.2449 | 10.4042 | 11.9121 | 7.7034 | 9.0675 | 12.4904 | 7.9062 | 9.556 | 12.308 | 9.2156 | 10.488 | 7.7157 | 10.1836 | 8.1473 | 10.0938 | 7.7129 | 9.6956 | 13.0802 | 10.512 | 10.1799 | 11.4417 | 8.0911 | 9.7372 | 12.6323 | 7.9645 | 10.2575 | 9.7436 | 9.7874 | 8.4957 | 10.0926 | -0.083793 | 20.9533 | 0.031255 | 0.050672 | -38.0529 | 3.1205 | -1.18 | 0.36 | 0.40258 | -0.48886 | 0.22114 | -0.49981 | -0.27653 | 0.25913 | 0.83233 | 0.40452 | 0.40791 | 0.41665 | 0.38051 | 0.59428 | 0.42421 | 0.41331
42810.4363 | -322 | 18.6256 | 18.6622 | 18.6397 | 18.6407 | 17.9892 | 16.6225 | 14.697 | 16.7275 | 17.2199 | 17.3158 | 17.332 | 16.8794 | 15.9244 | 14.5363 | 15.0815 | 15.0568 | 15.592 | 13.4487 | 13.5531 | 14.123 |  |  |  | 16.6441 | 15.9796 | 15.0845 | 10.2679 | 9.4927 | 10.0305 | 17.3318 | 16.4414 | 15.2367 | 16.9568 | 16.2347 | 15.2303 | 10.81 | 11.8141 |  | 12.1484 | 10.3387 | 10.2297 | 8.8243 |  | 6.4244 | 6.4094 | 5.9488 | 6.0543 | 6.0423 | 6.2871 | 6.7619 | 4.7082 | 6.3659 | 4.4966 | 6.6158 | 8.175 | 42.3959 | 46.5515 | 42.8942 | 15.3207 |  |  | -0.036581 | 0.027687 | -0.11183 | -0.00657 | 0.18876 | -0.070772 | 0.26866 | -0.22424 | -0.24265 | -0.8507 | -0.31783 | 8.869 | 8.8703 | 2.0084 | 15.9284 | 16.7707 | 17.3076 | 17.6198 | 17.5818 | 16.5684 | 14.9066 | 16.8847 | 17.2158 | 17.5055 | 17.5491 | 17.2936 | 16.4969 | 14.7287 | 6.1967 | 8.3778 | 5.3546 | 5.6779 | 5.8184 | 6.5657 | 7.5776 | 16.0111 | 15.6064 | 15.4548 | 14.372 | 14.2566 | 14.1927 |  |  |  | 10.7458 | 9.3779 | 9.0432 | 9.138 | -0.11381 | 0.0081174 | 12.7388 |  |  | 10.6466 |  |  | 16.8859 | 16.0839 | 15.0677 | 16.3926 | 15.6748 | 14.7753 | 10.1063 | 10.513 | 11.1805 | 10.8858 | 9.2398 |  | 10.5782 | 8.2183 | 9.8395 | 9.3472 | 11.032 | 11.8362 |  | 12.233 |  |  | 11.7729 | 12.5574 | 12.5468 | [6 empty] | 12.522 |  |  | 11.2693 |  |  | 9.2348 | 10.4017 | 11.9221 | 7.7153 | 9.0746 | 12.5012 | 7.9177 | 9.5621 | 12.3128 | 9.2204 | 10.4881 | 7.7216 | 10.1936 | 8.1553 | 10.1017 | 7.7169 | 9.6836 | 13.0783 | 10.5033 | 10.1689 | 11.4353 | 8.0897 | 9.7316 | 12.63 | 7.9642 | 10.2559 | 9.7407 | 9.7894 | 8.4984 | 10.0971 | -0.027169 | 20.9532 | 0.031444 | 0.04976 | -37.9483 | 3.1205 | -19.12 | 0.34 | -0.2243 | 0.19388 | -0.38966 | -0.094447 | 0.50613 | -0.30991 | 0.60382 | 0.40462 | 0.40867 | 0.4166 | 0.38809 | 0.59915 | 0.4238 | 0.41298
42810.4363 | -321 | 18.6314 | 18.6739 | 18.6488 | 18.6503 | 17.9965 | 16.6385 | 14.7101 | 16.7407 | 17.2367 | 17.3214 | 17.341 | 16.8894 | 15.9336 | 14.545 | 15.0792 | 15.0529 | 15.598 | 13.4477 | 13.5551 | 14.1236 |  |  |  | 16.6431 | 15.9756 | 15.0807 | 10.2714 | 9.4955 | 10.054 | 17.3179 | 16.4293 | 15.2246 | 16.9383 | 16.214 | 15.2249 | 10.7917 | 11.7805 |  | 12.1302 | 10.3306 | 10.2251 | 8.8215 |  | 6.4368 | 6.4209 | 5.9537 | 6.0619 | 6.0513 | 6.2603 | 6.7481 | 4.7637 | 6.375 | 4.5117 | 6.6187 | 8.1728 | 42.4027 | 46.5562 | 42.8979 | 15.3142 |  |  | -0.050377 | -0.047881 | 0.049164 | 0.068342 | -0.096432 | -0.40327 | 0.47631 | -0.31032 | -0.3382 | 0.15907 | -0.33094 | 8.8682 | 8.8692 | 2.0084 | 15.9283 | 16.7795 | 17.3105 | 17.6196 | 17.5818 | 16.5606 | 14.9182 | 16.8855 | 17.2164 | 17.5055 | 17.552 | 17.292 | 16.4981 | 14.7344 | 6.1713 | 8.3812 | 5.3387 | 5.6777 | 5.8335 | 6.5591 | 7.5838 | 16.0143 | 15.6075 | 15.4541 | 14.3672 | 14.2636 | 14.1916 |  |  |  | 10.7514 | 9.3768 | 9.0422 | 9.149 | -0.034191 | 0.044628 | 12.7377 |  |  | 10.6461 |  |  | 16.8876 | 16.0832 | 15.0628 | 16.3938 | 15.6773 | 14.7784 | 10.112 | 10.5197 | 11.1823 | 10.8966 | 9.252 |  | 10.5785 | 8.2169 | 9.8413 | 9.3464 | 11.0338 | 11.8225 |  | 12.232 |  |  | 11.7839 | 12.5486 | 12.5582 | [6 empty] | 12.5337 |  |  | 11.2695 |  |  | 9.222 | 10.3929 | 11.9177 | 7.7208 | 9.0733 | 12.4941 | 7.9036 | 9.5575 | 12.2978 | 9.2134 | 10.4797 | 7.721 | 10.1923 | 8.1547 | 10.1015 | 7.7003 | 9.6655 | 13.0747 | 10.5062 | 10.1712 | 11.4391 | 8.093 | 9.7389 | 12.637 | 7.9384 | 10.2281 | 9.7481 | 9.8025 | 8.5052 | 10.1078 | 0.087043 | 20.953 | 0.031708 | 0.050527 | -37.9758 | 3.1205 | -9.39 | 0.3 | -0.26323 | -0.25497 | 0.25837 | 0.30462 | -0.36174 | -0.73975 | 0.80396 | 0.4043 | 0.40877 | 0.41668 | 0.39016 | 0.60164 | 0.42328 | 0.41286
42810.4363 | -320 | 18.6266 | 18.6715 | 18.645 | 18.6517 | 17.9905 | 16.6223 | 14.7008 | 16.7383 | 17.2206 | 17.3221 | 17.339 | 16.8843 | 15.9341 | 14.5475 | 15.0748 | 15.051 | 15.5997 | 13.4443 | 13.5572 | 14.1247 |  |  |  | 16.6503 | 15.9788 | 15.0811 | 10.2649 | 9.4925 | 10.0583 | 17.312 | 16.4361 | 15.2224 | 16.9389 | 16.2185 | 15.2224 | 10.7877 | 11.7588 |  | 12.1335 | 10.3469 | 10.2217 | 8.8191 |  | 6.4319 | 6.4161 | 5.9472 | 6.0528 | 6.0466 | 6.2543 | 6.736 | 4.7292 | 6.3692 | 4.5304 | 6.6173 | 8.1701 | 42.3988 | 46.5483 | 42.8883 | 15.3046 |  |  | 0.015331 | -0.11228 | 0.085304 | -0.051914 | 0.11253 | -0.083912 | 0.41914 | -0.2709 | -0.45418 | 0.30068 | -0.36949 | 8.8683 | 8.8699 | 2.0085 | 15.9224 | 16.778 | 17.3055 | 17.6134 | 17.5756 | 16.5546 | 14.9147 | 16.883 | 17.2143 | 17.4994 | 17.5477 | 17.2928 | 16.5001 | 14.7288 | 6.1478 | 8.3867 | 5.3956 | 5.6653 | 5.8342 | 6.5695 | 7.5848 | 16.0109 | 15.6062 | 15.4514 | 14.3742 | 14.2595 | 14.1896 |  |  |  | 10.7418 | 9.3695 | 9.0444 | 9.1452 | -0.088285 | -0.024253 | 12.7379 |  |  | 10.6458 |  |  | 16.8872 | 16.0823 | 15.057 | 16.3969 | 15.674 | 14.78 | 10.1139 | 10.5189 | 11.1904 | 10.9055 | 9.2532 |  | 10.579 | 8.2765 | 9.8407 | 9.3569 | 11.0438 | 11.8357 |  | 12.2401 |  |  | 11.7986 | 12.5508 | 12.572 | [6 empty] | 12.5376 |  |  | 11.2802 |  |  | 9.214 | 10.372 | 11.9264 | 7.7343 | 9.0737 | 12.5026 | 7.892 | 9.5663 | 12.293 | 9.2177 | 10.4814 | 7.727 | 10.1972 | 8.1604 | 10.1031 | 7.6462 | 9.5943 | 13.0711 | 10.4999 | 10.1713 | 11.4475 | 8.1031 | 9.7334 | 12.6377 | 7.8838 | 10.1687 | 9.7544 | 9.8051 | 8.5034 | 10.1213 | 0.078183 | 20.9531 | 0.031272 | 0.049629 | -38.0014 | 3.1205 | 13 | 0.41 | 0.14521 | -0.39044 | 0.34033 | -0.26549 | 0.39077 | -0.33744 | 0.75416 | 0.40428 | 0.40709 | 0.41672 | 0.39398 | 0.59542 | 0.42321 | 0.41264
42810.4363 | -319 | 18.625 | 18.6748 | 18.6431 | 18.6522 | 17.9957 | 16.6306 | 14.6969 | 16.7395 | 17.228 | 17.3182 | 17.3348 | 16.8891 | 15.937 | 14.5442 | 15.0753 | 15.0518 | 15.5961 | 13.4398 | 13.5551 | 14.1235 |  |  |  | 16.6416 | 15.9783 | 15.0887 | 10.2729 | 9.5004 | 10.0627 | 17.3297 | 16.4438 | 15.2337 | 16.9509 | 16.2354 | 15.2312 | 10.8049 | 11.7655 |  | 12.1456 | 10.3574 | 10.2312 | 8.816 |  | 6.4407 | 6.4264 | 5.9534 | 6.057 | 6.0544 | 6.3149 | 6.7813 | 4.6572 | 6.3736 | 4.5317 | 6.6248 | 8.1602 | 42.393 | 46.5371 | 42.8888 | 15.2908 |  |  | 0.035703 | 0.037543 | -0.10854 | -0.14128 | -0.001152 | -0.033316 | 0.40534 | -0.20781 | -0.54895 | -0.1036 | -0.3224 | 8.8687 | 8.8698 | 2.0087 | 15.9267 | 16.7785 | 17.301 | 17.6169 | 17.5758 | 16.5608 | 14.9105 | 16.8763 | 17.2141 | 17.4964 | 17.5428 | 17.2955 | 16.4994 | 14.7304 | 6.1316 | 8.3745 | 5.3886 | 5.6716 | 5.8007 | 6.5646 | 7.5889 | 16.0146 | 15.6049 | 15.4528 | 14.3777 | 14.2535 | 14.1928 |  |  |  | 10.7366 | 9.3728 | 9.036 | 9.1171 | -0.13367 | 0.012446 | 12.7337 |  |  | 10.638 |  |  | 16.8837 | 16.0764 | 15.0609 | 16.3937 | 15.6705 | 14.7717 | 10.1208 | 10.5075 | 11.1921 | 10.9132 | 9.2436 |  | 10.5795 | 8.313 | 9.8346 | 9.3598 | 11.0343 | 11.8465 |  | 12.2395 |  |  | 11.8105 | 12.5401 | 12.5751 | [6 empty] | 12.5416 |  |  | 11.2792 |  |  | 9.2051 | 10.3666 | 11.9338 | 7.7504 | 9.0713 | 12.506 | 7.8899 | 9.5693 | 12.286 | 9.2197 | 10.4937 | 7.7301 | 10.1976 | 8.1586 | 10.1193 | 7.6167 | 9.5349 | 13.0652 | 10.4966 | 10.1762 | 11.4496 | 8.1133 | 9.7382 | 12.6468 | 7.8577 | 10.1264 | 9.7607 | 9.8092 | 8.5076 | 10.128 | 0.026759 | 20.9532 | 0.031123 | 0.049615 | -38.0447 | 3.1205 | 11.18 | 0.23 | 0.2216 | 0.22578 | -0.3839 | -0.43798 | -0.039542 | -0.21265 | 0.74172 | 0.40456 | 0.40587 | 0.41633 | 0.3952 | 0.59668 | 0.42387 | 0.41325
42810.4364 | -318 | 18.6219 | 18.6692 | 18.6402 | 18.6431 | 17.9884 | 16.6282 | 14.6956 | 16.7349 | 17.2232 | 17.324 | 17.3353 | 16.8785 | 15.9279 | 14.5373 | 15.073 | 15.0523 | 15.5975 | 13.449 | 13.5578 | 14.119 |  |  |  | 16.6404 | 15.9767 | 15.0794 | 10.2737 | 9.4923 | 10.0756 | 17.3247 | 16.4468 | 15.2285 | 16.9509 | 16.2318 | 15.2323 | 10.8127 | 11.7538 |  | 12.1424 | 10.3596 | 10.2136 | 8.8163 |  | 6.432 | 6.4211 | 5.9578 | 6.0511 | 6.0811 | 6.4021 | 6.7873 | 4.602 | 6.3707 | 4.5871 | 6.6245 | 8.1669 | 42.4011 | 46.5393 | 42.8974 | 15.291 |  |  | -0.091777 | -0.022253 | -0.013264 | -0.18596 | 0.015936 | 0.02714 | 0.26603 | -0.29718 | -0.24382 | -0.16717 | -0.28703 | 8.87 | 8.8715 | 2.0085 | 15.9235 | 16.7673 | 17.2925 | 17.6147 | 17.5812 | 16.5484 | 14.9098 | 16.8764 | 17.2098 | 17.4958 | 17.5377 | 17.2841 | 16.4946 | 14.7228 | 6.0985 | 8.3853 | 5.3631 | 5.7349 | 5.728 | 6.5686 | 7.5811 | 16.0182 | 15.6092 | 15.4457 | 14.3646 | 14.258 | 14.1943 |  |  |  | 10.7327 | 9.3665 | 9.0304 | 9.0923 | 0.047862 | -0.038368 | 12.7268 |  |  | 10.6378 |  |  | 16.8782 | 16.0747 | 15.0615 | 16.3801 | 15.6661 | 14.7728 | 10.1252 | 10.5071 | 11.1954 | 10.9199 | 9.234 |  | 10.5815 | 8.3225 | 9.8372 | 9.3527 | 11.0394 | 11.852 |  | 12.2379 |  |  | 11.8326 | 12.5556 | 12.5877 | [6 empty] | 12.5591 |  |  | 11.2783 |  |  | 9.1959 | 10.3622 | 11.9267 | 7.7528 | 9.0712 | 12.503 | 7.8838 | 9.5567 | 12.2768 | 9.2169 | 10.479 | 7.7109 | 10.1742 | 8.1531 | 10.1074 | 7.6028 | 9.5208 | 13.0664 | 10.4964 | 10.1791 | 11.4612 | 8.1281 | 9.7473 | 12.6655 | 7.8626 | 10.1148 | 9.7755 | 9.8222 | 8.5275 | 10.139 | -0.04874 | 20.953 | 0.031427 | 0.049347 | -38.0785 | 3.1206 | 3.68 | 0.21 | -0.3553 | -0.17382 | -0.1342 | -0.50249 | 0.14709 | 0.19196 | 0.60099 | 0.40489 | 0.4057 | 0.41669 | 0.39934 | 0.5986 | 0.42412 | 0.41381
42810.4364 | -317 | 18.6171 | 18.6679 | 18.6381 | 18.6406 | 17.9887 | 16.6314 | 14.6907 | 16.7315 | 17.2208 | 17.3226 | 17.3344 | 16.8728 | 15.9213 | 14.5383 | 15.0646 | 15.0492 | 15.5879 | 13.4408 | 13.5562 | 14.1173 |  |  |  | 16.6349 | 15.9681 | 15.0712 | 10.2737 | 9.489 | 10.1034 | 17.317 | 16.4379 | 15.2237 | 16.9443 | 16.2268 | 15.2318 | 10.7986 | 11.7241 |  | 12.1312 | 10.35 | 10.2022 | 8.7884 |  | 6.4381 | 6.4262 | 5.9547 | 6.0621 | 6.1393 | 6.4469 | 6.8335 | 4.6203 | 6.3714 | 4.5924 | 6.6249 | 8.1648 | 42.3984 | 46.5461 | 42.9152 | 15.2815 |  |  | 0.086959 | 0.051343 | -0.090804 | -0.063742 | 0.11253 | -0.047116 | 0.41126 | -0.14473 | 0.047109 | -0.31634 | -0.38797 | 8.8685 | 8.8698 | 2.0085 | 15.9225 | 16.7751 | 17.2928 | 17.6187 | 17.5754 | 16.5535 | 14.9084 | 16.8787 | 17.2119 | 17.5004 | 17.5399 | 17.2826 | 16.4978 | 14.7199 | 6.1081 | 8.3907 | 5.3583 | 5.7398 | 5.7277 | 6.5626 | 7.5771 | 16.0202 | 15.6128 | 15.4502 | 14.3699 | 14.2605 | 14.2025 |  |  |  | 10.737 | 9.3716 | 9.032 | 9.1016 | 0.15787 | -0.10668 | 12.7338 |  |  | 10.6473 |  |  | 16.8879 | 16.0836 | 15.0636 | 16.3824 | 15.6691 | 14.7766 | 10.1312 | 10.5152 | 11.2009 | 10.9414 | 9.2174 |  | 10.587 | 8.2908 | 9.8471 | 9.3527 | 11.0387 | 11.8398 |  | 12.241 |  |  | 11.8307 | 12.5635 | 12.6046 | [6 empty] | 12.5735 |  |  | 11.2559 |  |  | 9.1827 | 10.3516 | 11.9355 | 7.7323 | 9.0598 | 12.5004 | 7.892 | 9.5453 | 12.256 | 9.2131 | 10.4684 | 7.6711 | 10.1668 | 8.1623 | 10.1147 | 7.5925 | 9.4894 | 13.0422 | 10.4808 | 10.1711 | 11.4529 | 8.1097 | 9.7441 | 12.658 | 7.8511 | 10.113 | 9.776 | 9.8168 | 8.5246 | 10.1373 | -0.043155 | 20.9532 | 0.031071 | 0.049687 | -38.0992 | 3.1205 | 6.17 | 0.33 | 0.34587 | 0.26403 | -0.35113 | -0.29419 | 0.3909 | -0.25294 | 0.74729 | 0.40554 | 0.4069 | 0.41667 | 0.39758 | 0.59868 | 0.42443 | 0.4137
42810.4364 | -316 | 18.6215 | 18.6656 | 18.6453 | 18.6533 | 17.9939 | 16.6359 | 14.6952 | 16.7379 | 17.2236 | 17.3193 | 17.3396 | 16.8778 | 15.9253 | 14.5341 | 15.0657 | 15.0465 | 15.5916 | 13.443 | 13.5473 | 14.1167 |  |  |  | 16.6399 | 15.9646 | 15.0791 | 10.2797 | 9.4975 | 10.1379 | 17.3173 | 16.4371 | 15.2259 | 16.939 | 16.2296 | 15.2298 | 10.7908 | 11.7317 |  | 12.1335 | 10.3342 | 10.2017 | 8.7574 |  | 6.429 | 6.4161 | 5.9627 | 6.065 | 6.1812 | 6.4696 | 6.8646 | 4.6756 | 6.3681 | 4.5895 | 6.6213 | 8.1726 | 42.406 | 46.5546 | 42.9325 | 15.2749 |  |  | 0.053447 | -0.053797 | 0.060992 | 0.060454 | -0.02612 | -0.02806 | 0.61562 | -0.27418 | -0.26503 | -0.15605 | -0.32697 | 8.8716 | 8.8726 | 2.0085 | 15.926 | 16.7742 | 17.2978 | 17.621 | 17.5787 | 16.5685 | 14.9082 | 16.8763 | 17.2165 | 17.5063 | 17.5437 | 17.2897 | 16.4973 | 14.724 | 6.1482 | 8.3928 | 5.3475 | 5.71 | 5.7411 | 6.5719 | 7.576 | 16.0212 | 15.6087 | 15.458 | 14.3783 | 14.2606 | 14.1892 |  |  |  | 10.7394 | 9.38 | 9.032 | 9.1028 | 0.017067 | -0.013714 | 12.7378 |  |  | 10.6526 |  |  | 16.885 | 16.0823 | 15.0631 | 16.3804 | 15.674 | 14.7699 | 10.1312 | 10.5202 | 11.2051 | 10.9453 | 9.2016 |  | 10.581 | 8.2836 | 9.8433 | 9.3594 | 11.04 | 11.8761 |  | 12.2394 |  |  | 11.8041 | 12.5633 | 12.5965 | [6 empty] | 12.5689 |  |  | 11.2578 |  |  | 9.1761 | 10.3466 | 11.9325 | 7.6946 | 9.0309 | 12.4954 | 7.8836 | 9.5396 | 12.2596 | 9.2147 | 10.4682 | 7.6374 | 10.1587 | 8.1436 | 10.111 | 7.5976 | 9.4666 | 13.0432 | 10.4785 | 10.1811 | 11.4635 | 8.1096 | 9.7508 | 12.6733 | 7.8439 | 10.1268 | 9.7766 | 9.8268 | 8.5279 | 10.1573 | -0.060296 | 20.9538 | 0.031255 | 0.050693 | -37.9671 | 3.1205 | 16.78 | 0.41 | 0.27117 | -0.27026 | 0.28777 | 0.2865 | -0.18834 | -0.19521 | 0.91434 | 0.40577 | 0.40698 | 0.41653 | 0.39421 | 0.59975 | 0.42503 | 0.41374
42810.4364 | -315 | 18.6419 | 18.6884 | 18.6615 | 18.6611 | 18.0069 | 16.6416 | 14.711 | 16.7466 | 17.2396 | 17.3341 | 17.3479 | 16.8992 | 15.9399 | 14.5506 | 15.0658 | 15.0523 | 15.5862 | 13.4347 | 13.5365 | 14.1097 |  |  |  | 16.6326 | 15.9607 | 15.0718 | 10.278 | 9.4862 | 10.1102 | 17.3052 | 16.4264 | 15.2255 | 16.9345 | 16.2169 | 15.2243 | 10.7823 | 11.7344 |  | 12.1352 | 10.3154 | 10.1932 | 8.7093 |  | 6.4288 | 6.4179 | 5.9649 | 6.061 | 6.2021 | 6.487 | 6.865 | 4.7519 | 6.3696 | 4.5685 | 6.6198 | 8.1687 | 42.3954 | 46.5401 | 42.9462 | 15.2642 |  |  | -0.036581 | 0.16962 | 0.10699 | -0.12814 | 0.052732 | -0.043828 | 0.68724 | -0.37078 | -0.25608 | -0.80161 | -0.22225 | 8.8704 | 8.8714 | 2.0088 | 15.9245 | 16.7745 | 17.2959 | 17.6164 | 17.5779 | 16.5608 | 14.9048 | 16.8747 | 17.2059 | 17.5008 | 17.5345 | 17.2892 | 16.4932 | 14.7197 | 6.2296 | 8.391 | 5.3404 | 5.6788 | 5.7385 | 6.5673 | 7.5753 | 16.0134 | 15.6041 | 15.4521 | 14.3752 | 14.2606 | 14.193 |  |  |  | 10.7341 | 9.3741 | 9.0256 | 9.0821 | 0.20265 | -0.10857 | 12.7349 |  |  | 10.6522 |  |  | 16.8774 | 16.0814 | 15.0613 | 16.3829 | 15.6717 | 14.7726 | 10.1333 | 10.5277 | 11.2163 | 10.9512 | 9.2104 |  | 10.5823 | 8.2688 | 9.8417 | 9.3687 | 11.0353 | 11.8985 |  | 12.2295 |  |  | 11.8162 | 12.5791 | 12.6189 | [6 empty] | 12.5878 |  |  | 11.2611 |  |  | 9.1759 | 10.3629 | 11.9356 | 7.68 | 9.0085 | 12.4932 | 7.8858 | 9.5583 | 12.2557 | 9.2337 | 10.4697 | 7.6385 | 10.1498 | 8.137 | 10.1274 | 7.592 | 9.4298 | 13.0154 | 10.4605 | 10.1669 | 11.4586 | 8.1111 | 9.7548 | 12.6721 | 7.8462 | 10.1227 | 9.7699 | 9.8154 | 8.5273 | 10.1386 | -0.027169 | 20.9537 | 0.030928 | 0.050042 | -37.9769 | 3.1205 | 11.85 | 0.36 | -0.22433 | 0.4799 | 0.38113 | -0.41711 | 0.26761 | -0.24397 | 0.96609 | 0.40558 | 0.40734 | 0.41612 | 0.38463 | 0.60046 | 0.42609 | 0.41414
42810.4364 | -314 | 18.6252 | 18.6754 | 18.645 | 18.6539 | 17.9971 | 16.6318 | 14.6968 | 16.7301 | 17.2243 | 17.3187 | 17.3305 | 16.8851 | 15.9302 | 14.5396 | 15.0737 | 15.0511 | 15.5954 | 13.4429 | 13.56 | 14.1188 |  |  |  | 16.6426 | 15.9682 | 15.0832 | 10.2952 | 9.4965 | 10.1222 | 17.3092 | 16.4322 | 15.235 | 16.9512 | 16.2278 | 15.2191 | 10.7962 | 11.7357 |  | 12.1315 | 10.3285 | 10.1892 | 8.6685 |  | 6.4295 | 6.4218 | 5.968 | 6.0571 | 6.2353 | 6.5175 | 6.8808 | 4.8158 | 6.3689 | 4.6004 | 6.6196 | 8.1737 | 42.3893 | 46.5407 | 42.9608 | 15.2596 |  |  | 0.064615 | 0.050687 | -0.021804 | -0.049282 | -0.00772 | 0.23084 | 0.56239 | -0.51008 | -0.065759 | -0.82028 | -0.16205 | 8.8683 | 8.8695 | 2.0084 | 15.9176 | 16.7773 | 17.3013 | 17.6122 | 17.5772 | 16.5664 | 14.9083 | 16.8795 | 17.2123 | 17.5045 | 17.5367 | 17.291 | 16.4923 | 14.7224 | 6.3138 | 8.4226 | 5.3497 | 5.6606 | 5.7813 | 6.5736 | 7.5674 | 16.0094 | 15.5997 | 15.4467 | 14.3721 | 14.2597 | 14.1901 |  |  |  | 10.7348 | 9.377 | 9.0265 | 9.0573 | 0.168 | 0.077563 | 12.73 |  |  | 10.6509 |  |  | 16.8835 | 16.0833 | 15.0654 | 16.3837 | 15.672 | 14.7757 | 10.1375 | 10.5275 | 11.2255 | 10.9554 | 9.2513 |  | 10.5852 | 8.2826 | 9.8466 | 9.3815 | 11.0348 | 11.9224 |  | 12.2414 |  |  | 11.8254 | 12.589 | 12.5979 | [6 empty] | 12.5692 |  |  | 11.2656 |  |  | 9.1763 | 10.343 | 11.9335 | 7.6589 | 8.9851 | 12.4913 | 7.8816 | 9.5458 | 12.2399 | 9.224 | 10.4717 | 7.6322 | 10.1465 | 8.1427 | 10.1289 | 7.5856 | 9.4093 | 13.0203 | 10.4608 | 10.1728 | 11.457 | 8.1097 | 9.7545 | 12.6724 | 7.8484 | 10.1435 | 9.7662 | 9.8188 | 8.5262 | 10.146 | 0.015396 | 20.9527 | 0.031312 | 0.049926 | -37.9699 | 3.1205 | 20.6 | 0.33 | 0.29815 | 0.26234 | -0.17206 | -0.25868 | -0.1024 | 0.55995 | 0.87399 | 0.40454 | 0.40712 | 0.41574 | 0.376 | 0.59851 | 0.42768 | 0.41486
42810.4364 | -313 | 18.6212 | 18.6659 | 18.643 | 18.651 | 17.9947 | 16.633 | 14.6955 | 16.7325 | 17.2326 | 17.3167 | 17.3293 | 16.8818 | 15.9281 | 14.5405 | 15.0703 | 15.0495 | 15.5941 | 13.4344 | 13.5519 | 14.1215 |  |  |  | 16.6344 | 15.9735 | 15.0821 | 10.2942 | 9.4888 | 10.1217 | 17.3229 | 16.4381 | 15.2392 | 16.9544 | 16.2246 | 15.2309 | 10.7976 | 11.7568 |  | 12.1424 | 10.3135 | 10.1877 | 8.6635 |  | 6.4316 | 6.4272 | 5.975 | 6.0745 | 6.2789 | 6.52 | 6.9078 | 4.9081 | 6.3741 | 4.6558 | 6.6167 | 8.1804 | 42.3808 | 46.5428 | 42.9699 | 15.2535 |  |  | 0.087615 | 0.030971 | 0.03142 | 0.08871 | 0.1191 | 0.38264 | 0.74507 | -0.46014 | 0.12728 | 0.074097 | -0.32776 | 8.8694 | 8.8711 | 2.0084 | 15.9283 | 16.7773 | 17.3061 | 17.6173 | 17.5818 | 16.5653 | 14.9114 | 16.8836 | 17.2162 | 17.5046 | 17.5454 | 17.2882 | 16.503 | 14.7286 | 6.3717 | 8.4454 | 5.405 | 5.6726 | 5.8119 | 6.571 | 7.5709 | 16.0176 | 15.6079 | 15.4531 | 14.3716 | 14.2635 | 14.1899 |  |  |  | 10.7434 | 9.3853 | 9.0355 | 9.0387 | 0.1052 | 0.20893 | 12.7391 |  |  | 10.6495 |  |  | 16.8885 | 16.0837 | 15.0666 | 16.3823 | 15.6714 | 14.7785 | 10.1468 | 10.5276 | 11.2315 | 10.965 | 9.2412 |  | 10.5823 | 8.3448 | 9.8432 | 9.3891 | 11.0422 | 11.9573 |  | 12.2422 |  |  | 11.798 | 12.5907 | 12.5933 | [6 empty] | 12.5661 |  |  | 11.2666 |  |  | 9.1731 | 10.3419 | 11.9333 | 7.6573 | 8.958 | 12.4981 | 7.8757 | 9.5432 | 12.2393 | 9.2228 | 10.4737 | 7.6423 | 10.1403 | 8.1321 | 10.1356 | 7.5827 | 9.4075 | 13.0191 | 10.4697 | 10.1792 | 11.4644 | 8.1201 | 9.7622 | 12.6875 | 7.8523 | 10.152 | 9.7728 | 9.8237 | 8.5447 | 10.151 | 0.27329 | 20.9536 | 0.031077 | 0.049123 | -38.0345 | 3.1205 | 12.04 | 0.28 | 0.34718 | 0.20507 | 0.20655 | 0.34706 | 0.40221 | 0.72092 | 1.006 | 0.40472 | 0.40528 | 0.41577 | 0.36926 | 0.59276 | 0.42786 | 0.41565
42810.4364 | -312 | 18.6255 | 18.6776 | 18.6396 | 18.6556 | 17.9919 | 16.6388 | 14.6962 | 16.7301 | 17.2286 | 17.3184 | 17.3331 | 16.8848 | 15.9271 | 14.5408 | 15.0681 | 15.0465 | 15.5982 | 13.4422 | 13.5407 | 14.1191 |  |  |  | 16.6353 | 15.9733 | 15.0731 | 10.2949 | 9.4855 | 10.1258 | 17.311 | 16.4304 | 15.2288 | 16.9409 | 16.217 | 15.2222 | 10.7981 | 11.7444 |  | 12.1336 | 10.3051 | 10.1721 | 8.6429 |  | 6.4361 | 6.4357 | 6.0009 | 6.1202 | 6.3115 | 6.5354 | 6.9677 | 4.9833 | 6.3807 | 4.6828 | 6.6229 | 8.1731 | 42.3651 | 46.5357 | 42.9693 | 15.2431 |  |  | 0.10207 | -0.043281 | 0.007108 | -0.001314 | 0.011992 | 0.39644 | 0.6649 | -0.49826 | -0.66688 | -0.64615 | -0.18311 | 8.8712 | 8.8721 | 2.0084 | 15.9245 | 16.7708 | 17.2978 | 17.6069 | 17.5817 | 16.5541 | 14.9031 | 16.87 | 17.2097 | 17.5017 | 17.5398 | 17.2819 | 16.4893 | 14.722 | 6.4213 | 8.4561 | 5.4594 | 5.6919 | 5.8074 | 6.5807 | 7.5771 | 16.0126 | 15.608 | 15.4499 | 14.3772 | 14.2613 | 14.1987 |  |  |  | 10.7254 | 9.3836 | 9.0252 | 9.0115 | 0.15463 | 0.1997 | 12.7457 |  |  | 10.6476 |  |  | 16.8893 | 16.0909 | 15.0671 | 16.3864 | 15.6745 | 14.7795 | 10.1533 | 10.525 | 11.2422 | 10.9771 | 9.2393 |  | 10.5765 | 8.3858 | 9.8384 | 9.4071 | 11.038 | 12.0017 |  | 12.2294 |  |  | 11.7867 | 12.5944 | 12.5913 | [6 empty] | 12.5601 |  |  | 11.2727 |  |  | 9.1578 | 10.3457 | 11.9253 | 7.6767 | 8.9235 | 12.4987 | 7.8739 | 9.537 | 12.2269 | 9.2237 | 10.4683 | 7.6357 | 10.1396 | 8.1327 | 10.144 | 7.5813 | 9.3988 | 13.0199 | 10.4695 | 10.1785 | 11.4622 | 8.1244 | 9.766 | 12.6897 | 7.8648 | 10.1646 | 9.7636 | 9.8348 | 8.5461 | 10.1593 | 0.12402 | 20.9539 | 0.032316 | 0.049883 | -38.0532 | 3.1205 | 12.04 | 0.27 | 0.37473 | -0.24242 | 0.098242 | -0.04224 | 0.12763 | 0.73382 | 0.95035 | 0.40458 | 0.40398 | 0.41514 | 0.36488 | 0.58744 | 0.42845 | 0.41582
42810.4364 | -311 | 18.6319 | 18.6767 | 18.6423 | 18.6627 | 17.9941 | 16.647 | 14.7022 | 16.7361 | 17.2287 | 17.321 | 17.3456 | 16.8893 | 15.9343 | 14.5439 | 15.0661 | 15.0488 | 15.5968 | 13.4362 | 13.5444 | 14.1221 |  |  |  | 16.635 | 15.9771 | 15.0816 | 10.3066 | 9.497 | 10.1194 | 17.3219 | 16.4411 | 15.2361 | 16.9502 | 16.229 | 15.2293 | 10.8052 | 11.7488 |  | 12.1389 | 10.3132 | 10.1864 | 8.6357 |  | 6.4488 | 6.4569 | 6.0204 | 6.1687 | 6.3243 | 6.5397 | 7.0477 | 5.0187 | 6.381 | 4.8022 | 6.6318 | 8.1751 | 42.3638 | 46.5501 | 42.981 | 15.2344 |  |  | 0.093531 | 0.069087 | 0.039964 | 0.013142 | -0.017576 | -0.1148 | 0.67476 | -0.61654 | -0.1401 | -1.0905 | -0.3073 | 8.8712 | 8.8721 | 2.0086 | 15.9326 | 16.7819 | 17.3091 | 17.6197 | 17.5862 | 16.5625 | 14.919 | 16.8833 | 17.2155 | 17.5124 | 17.554 | 17.2974 | 16.4983 | 14.7264 | 6.4558 | 8.4582 | 5.5127 | 5.7339 | 5.7955 | 6.5755 | 7.5776 | 16.0099 | 15.6114 | 15.4477 | 14.3644 | 14.2577 | 14.1886 |  |  |  | 10.7288 | 9.3756 | 9.0236 | 9.0069 | 0.080481 | 0.099206 | 12.7432 |  |  | 10.6445 |  |  | 16.8872 | 16.0925 | 15.0634 | 16.3863 | 15.6741 | 14.7746 | 10.1495 | 10.5217 | 11.2362 | 10.9784 | 9.2518 |  | 10.5716 | 8.3948 | 9.8322 | 9.404 | 11.0315 | 12.0578 |  | 12.2297 |  |  | 11.7944 | 12.5828 | 12.5923 | [6 empty] | 12.5593 |  |  | 11.2791 |  |  | 9.1439 | 10.3427 | 11.9223 | 7.6776 | 8.9088 | 12.4868 | 7.8649 | 9.5304 | 12.2174 | 9.2219 | 10.4598 | 7.6324 | 10.1333 | 8.1203 | 10.1376 | 7.5868 | 9.4009 | 13.0204 | 10.4665 | 10.1627 | 11.455 | 8.1254 | 9.762 | 12.6933 | 7.8636 | 10.169 | 9.7614 | 9.8361 | 8.5379 | 10.1601 | 0.04833 | 20.9523 | 0.031507 | 0.049289 | -38.0551 | 3.1205 | 14.02 | 0.31 | 0.35871 | 0.30629 | 0.23296 | 0.13359 | -0.15451 | -0.39488 | 0.95737 | 0.40407 | 0.40352 | 0.41501 | 0.36044 | 0.58157 | 0.42889 | 0.41606
42810.4364 | -310 | 18.6204 | 18.6764 | 18.6449 | 18.6578 | 17.9919 | 16.6354 | 14.6947 | 16.7345 | 17.225 | 17.3229 | 17.3402 | 16.8877 | 15.9281 | 14.537 | 15.0652 | 15.0416 | 15.5864 | 13.4286 | 13.5437 | 14.1176 |  |  |  | 16.6301 | 15.9655 | 15.0758 | 10.2943 | 9.4992 | 10.0998 | 17.327 | 16.4388 | 15.2359 | 16.9544 | 16.233 | 15.233 | 10.8029 | 11.7147 |  | 12.1388 | 10.3218 | 10.1845 | 8.6313 |  | 6.445 | 6.4588 | 6.0212 | 6.1937 | 6.3381 | 6.5553 | 7.0856 | 5.0151 | 6.3793 | 4.8528 | 6.6295 | 8.1709 | 42.3523 | 46.5575 | 42.9785 | 15.2256 |  |  | -0.026065 | -0.33899 | 0.078076 | -0.049282 | -0.09906 | -0.097056 | 0.58014 | -0.49629 | -0.2119 | -0.057868 | -0.35518 | 8.8687 | 8.87 | 2.0084 | 15.9287 | 16.777 | 17.3007 | 17.6198 | 17.5779 | 16.564 | 14.9112 | 16.8776 | 17.219 | 17.5047 | 17.5423 | 17.2908 | 16.4994 | 14.7317 | 6.4965 | 8.4637 | 5.55 | 5.7303 | 5.792 | 6.5754 | 7.5838 | 16.0124 | 15.6135 | 15.4508 | 14.3716 | 14.2594 | 14.1932 |  |  |  | 10.7318 | 9.373 | 9.0347 | 8.9862 | -0.065594 | 0.10485 | 12.7391 |  |  | 10.6411 |  |  | 16.8844 | 16.0867 | 15.0605 | 16.3837 | 15.6644 | 14.7694 | 10.1537 | 10.524 | 11.2252 | 10.9749 | 9.2631 |  | 10.5802 | 8.379 | 9.8417 | 9.3859 | 11.0395 | 12.118 |  | 12.2378 |  |  | 11.8046 | 12.5707 | 12.5997 | [6 empty] | 12.5708 |  |  | 11.2946 |  |  | 9.1468 | 10.334 | 11.9146 | 7.6686 | 8.9025 | 12.4902 | 7.8614 | 9.5194 | 12.2103 | 9.2209 | 10.4594 | 7.6352 | 10.1411 | 8.1243 | 10.1322 | 7.5829 | 9.4155 | 13.0229 | 10.4716 | 10.1698 | 11.4542 | 8.1279 | 9.7563 | 12.6911 | 7.8696 | 10.1839 | 9.7753 | 9.8324 | 8.543 | 10.1656 | -0.090727 | 20.9531 | 0.030945 | 0.048044 | -38.0229 | 3.1205 | 6.23 | 0.28 | -0.18936 | -0.67847 | 0.32561 | -0.25869 | -0.36683 | -0.3631 | 0.88773 | 0.40404 | 0.40428 | 0.41577 | 0.35591 | 0.57815 | 0.42894 | 0.41673
42810.4365 | -309 | 18.6294 | 18.686 | 18.6491 | 18.662 | 18.0017 | 16.6418 | 14.7051 | 16.737 | 17.2331 | 17.3311 | 17.3443 | 16.8922 | 15.9357 | 14.5508 | 15.0704 | 15.0511 | 15.5958 | 13.4367 | 13.5469 | 14.1245 |  |  |  | 16.6391 | 15.9715 | 15.0781 | 10.2977 | 9.5055 | 10.0965 | 17.3105 | 16.4294 | 15.2237 | 16.9374 | 16.2198 | 15.2249 | 10.7896 | 11.6527 |  | 12.1294 | 10.312 | 10.1709 | 8.6224 |  | 6.4602 | 6.4647 | 6.0296 | 6.2063 | 6.3501 | 6.591 | 7.1309 | 4.943 | 6.3876 | 4.8653 | 6.6322 | 8.1691 | 42.3401 | 46.5862 | 42.9852 | 15.2215 |  |  | -0.004381 | -0.084021 | 0.016964 | -0.042714 | 0.057332 | -0.10954 | 0.62482 | -0.36486 | -0.92978 | -0.34194 | -0.23994 | 8.8716 | 8.873 | 2.0085 | 15.9281 | 16.7705 | 17.3006 | 17.6128 | 17.5765 | 16.5543 | 14.9098 | 16.8744 | 17.2101 | 17.4954 | 17.5418 | 17.2838 | 16.4952 | 14.7206 | 6.6193 | 8.4885 | 5.5748 | 5.7763 | 5.8107 | 6.5862 | 7.5876 | 16.0108 | 15.6064 | 15.4563 | 14.3666 | 14.2562 | 14.191 |  |  |  | 10.7305 | 9.3672 | 9.0282 | 8.9696 | 0.092637 | 0.042182 | 12.7448 |  |  | 10.6429 |  |  | 16.8802 | 16.0829 | 15.0582 | 16.3804 | 15.6657 | 14.7708 | 10.1584 | 10.5294 | 11.2241 | 10.9775 | 9.2727 |  | 10.5789 | 8.3658 | 9.8424 | 9.3921 | 11.0348 | 12.1453 |  | 12.2279 |  |  | 11.8096 | 12.5546 | 12.6001 | [6 empty] | 12.5841 |  |  | 11.3082 |  |  | 9.1455 | 10.3311 | 11.9052 | 7.6741 | 8.9089 | 12.4934 | 7.8673 | 9.5211 | 12.1991 | 9.2285 | 10.4651 | 7.6329 | 10.1508 | 8.1294 | 10.1373 | 7.5848 | 9.4226 | 13.0254 | 10.4689 | 10.1711 | 11.456 | 8.128 | 9.7524 | 12.6869 | 7.8841 | 10.19 | 9.776 | 9.828 | 8.5414 | 10.1749 | -0.20956 | 20.9533 | 0.031369 | 0.048638 | -38.0629 | 3.1205 | 0.31 | 0.21 | -0.077631 | -0.33779 | 0.15178 | -0.24084 | 0.27909 | -0.38577 | 0.92135 | 0.40373 | 0.40467 | 0.41545 | 0.34352 | 0.57584 | 0.42874 | 0.41715
42810.4365 | -308 | 18.6255 | 18.6746 | 18.6373 | 18.6578 | 17.9937 | 16.6393 | 14.6931 | 16.7349 | 17.2266 | 17.326 | 17.3336 | 16.8823 | 15.9331 | 14.5397 | 15.0721 | 15.0486 | 15.6023 | 13.4398 | 13.5492 | 14.1193 |  |  |  | 16.6458 | 15.9736 | 15.0831 | 10.3035 | 9.5157 | 10.1014 | 17.3198 | 16.4361 | 15.2285 | 16.9422 | 16.2191 | 15.2253 | 10.7956 | 11.6001 |  | 12.1279 | 10.3238 | 10.1812 | 8.6271 |  | 6.4659 | 6.4619 | 6.027 | 6.2097 | 6.3645 | 6.607 | 7.1676 | 4.9259 | 6.3827 | 4.9218 | 6.6257 | 8.1722 | 42.3238 | 46.61 | 42.9928 | 15.2168 |  |  | -0.005037 | -0.091909 | 0.1221 | 0.07951 | -0.059632 | -0.12728 | 0.78778 | -0.49892 | -0.53436 | 0.086475 | -0.38201 | 8.8696 | 8.8707 | 2.0086 | 15.9211 | 16.7752 | 17.2955 | 17.6064 | 17.5771 | 16.5466 | 14.9059 | 16.8689 | 17.2023 | 17.4903 | 17.5318 | 17.2798 | 16.4871 | 14.7246 | 6.7919 | 8.5287 | 5.6597 | 5.8271 | 5.8113 | 6.5906 | 7.5876 | 16.0138 | 15.6088 | 15.4584 | 14.3645 | 14.2619 | 14.1908 |  |  |  | 10.7282 | 9.3719 | 9.0405 | 8.9735 | 0.086559 | 0.017339 | 12.7389 |  |  | 10.6496 |  |  | 16.882 | 16.0745 | 15.0564 | 16.378 | 15.6638 | 14.7709 | 10.155 | 10.5276 | 11.2132 | 10.9781 | 9.2469 |  | 10.5841 | 8.3507 | 9.8416 | 9.3761 | 11.0381 | 12.1623 |  | 12.2328 |  |  | 11.7931 | 12.554 | 12.6057 | [6 empty] | 12.5877 |  |  | 11.3116 |  |  | 9.1439 | 10.334 | 11.9008 | 7.6801 | 8.9222 | 12.507 | 7.8775 | 9.5251 | 12.1913 | 9.2307 | 10.4706 | 7.6369 | 10.1627 | 8.1245 | 10.1479 | 7.5819 | 9.43 | 13.0273 | 10.4635 | 10.1651 | 11.4583 | 8.1336 | 9.754 | 12.6893 | 7.8992 | 10.1938 | 9.7732 | 9.8283 | 8.5537 | 10.1747 | -0.13907 | 20.9515 | 0.031077 | 0.047502 | -38.0461 | 3.1205 | 8.79 | 0.31 | -0.083241 | -0.35328 | 0.4072 | 0.32859 | -0.28464 | -0.41586 | 1.0346 | 0.40462 | 0.40506 | 0.416 | 0.32486 | 0.56641 | 0.42881 | 0.41696
42810.4365 | -307 | 18.6264 | 18.6723 | 18.6439 | 18.6593 | 17.9879 | 16.6331 | 14.6951 | 16.7363 | 17.2257 | 17.3174 | 17.3266 | 16.881 | 15.9273 | 14.5421 | 15.0693 | 15.0453 | 15.5968 | 13.434 | 13.5477 | 14.12 |  |  |  | 16.6425 | 15.9741 | 15.0795 | 10.3043 | 9.5178 | 10.1219 | 17.3141 | 16.4348 | 15.2295 | 16.9454 | 16.2322 | 15.2227 | 10.807 | 11.5517 |  | 12.1266 | 10.3424 | 10.1786 | 8.6238 |  | 6.4705 | 6.4764 | 6.0416 | 6.213 | 6.3781 | 6.6175 | 7.1998 | 4.9103 | 6.3848 | 5.0076 | 6.6337 | 8.174 | 42.2969 | 46.6412 | 42.9837 | 15.2075 |  |  | 0.040303 | -0.11819 | 0.015648 | 0.11565 | -0.19828 | -0.085228 | 0.58539 | -0.23738 | -0.69899 | 0.17417 | -0.20596 | 8.8736 | 8.8746 | 2.0086 | 15.9206 | 16.7703 | 17.2914 | 17.6138 | 17.5783 | 16.5528 | 14.9034 | 16.8736 | 17.2001 | 17.4917 | 17.5376 | 17.2798 | 16.482 | 14.7209 | 6.9255 | 8.568 | 5.8421 | 5.8494 | 5.8514 | 6.5965 | 7.5902 | 16.0207 | 15.6047 | 15.4512 | 14.3722 | 14.2553 | 14.1938 |  |  |  | 10.7317 | 9.3748 | 9.044 | 8.9768 | 0.23203 | -0.012396 | 12.7416 |  |  | 10.6482 |  |  | 16.8868 | 16.0753 | 15.0638 | 16.3853 | 15.6683 | 14.767 | 10.1567 | 10.5311 | 11.2059 | 10.98 | 9.2266 |  | 10.587 | 8.313 | 9.8393 | 9.3495 | 11.0371 | 12.1936 |  | 12.2377 |  |  | 11.753 | 12.5563 | 12.6089 | [6 empty] | 12.5847 |  |  | 11.3031 |  |  | 9.147 | 10.3301 | 11.8971 | 7.6777 | 8.9345 | 12.5081 | 7.8804 | 9.5265 | 12.187 | 9.2275 | 10.4661 | 7.6341 | 10.1834 | 8.1155 | 10.1424 | 7.566 | 9.4349 | 13.023 | 10.46 | 10.1571 | 11.4502 | 8.1278 | 9.749 | 12.6741 | 7.9034 | 10.1943 | 9.7641 | 9.8196 | 8.553 | 10.1696 | 0.026181 | 20.9536 | 0.03153 | 0.048146 | -38.1543 | 3.1205 | 4.88 | 0.39 | 0.23547 | -0.40064 | 0.14578 | 0.39631 | -0.51905 | -0.3403 | 0.89184 | 0.40528 | 0.40603 | 0.4167 | 0.31069 | 0.54644 | 0.42928 | 0.41699
42810.4365 | -306 | 18.6294 | 18.6753 | 18.6421 | 18.6576 | 17.9897 | 16.6351 | 14.7028 | 16.7345 | 17.2243 | 17.3258 | 17.3265 | 16.8739 | 15.923 | 14.5445 | 15.0677 | 15.0441 | 15.5923 | 13.4346 | 13.55 | 14.1256 |  |  |  | 16.6421 | 15.9765 | 15.0805 | 10.3058 | 9.5208 | 10.1012 | 17.3185 | 16.4357 | 15.2261 | 16.9496 | 16.227 | 15.2336 | 10.7967 | 11.5118 |  | 12.1286 | 10.3553 | 10.1865 | 8.5987 |  | 6.4773 | 6.4732 | 6.0423 | 6.228 | 6.3883 | 6.6267 | 7.2274 | 4.8226 | 6.3817 | 5.0005 | 6.6331 | 8.1699 | 42.2861 | 46.6613 | 42.9651 | 15.2023 |  |  | 0.042931 | 0.052659 | 0.078732 | -0.29767 | 0.021848 | -0.27448 | 0.60116 | -0.15524 | -0.67855 | 0.20942 | -0.40883 | 8.8678 | 8.8687 | 2.0084 | 15.9289 | 16.7777 | 17.2923 | 17.6137 | 17.5822 | 16.5569 | 14.9088 | 16.8696 | 17.2055 | 17.4945 | 17.5397 | 17.2847 | 16.4844 | 14.7213 | 7.1013 | 8.5751 | 5.9964 | 5.9277 | 5.9191 | 6.5994 | 7.5929 | 16.0089 | 15.6057 | 15.4499 | 14.3742 | 14.2567 | 14.185 |  |  |  | 10.7268 | 9.3724 | 9.0268 | 8.9824 | -0.046347 | -0.012396 | 12.7467 |  |  | 10.6465 |  |  | 16.8888 | 16.0811 | 15.0679 | 16.3904 | 15.6745 | 14.7764 | 10.1569 | 10.5341 | 11.2242 | 10.9836 | 9.1967 |  | 10.5786 | 8.3432 | 9.8325 | 9.3324 | 11.0302 | 12.2037 |  | 12.236 |  |  | 11.7336 | 12.5451 | 12.6122 | [6 empty] | 12.5765 |  |  | 11.3118 |  |  | 9.1454 | 10.3251 | 11.8961 | 7.6792 | 8.9442 | 12.5134 | 7.8817 | 9.5223 | 12.182 | 9.2269 | 10.4664 | 7.6321 | 10.1915 | 8.1212 | 10.1455 | 7.56 | 9.4437 | 13.0251 | 10.4657 | 10.1595 | 11.4546 | 8.123 | 9.7529 | 12.6758 | 7.9161 | 10.2012 | 9.7653 | 9.8157 | 8.5582 | 10.1721 | 0.21358 | 20.952 | 0.032081 | 0.047306 | -38.0377 | 3.1205 | -4.34 | 0.38 | 0.24302 | 0.26742 | 0.32699 | -0.63581 | 0.1723 | -0.6107 | 0.90379 | 0.40583 | 0.40497 | 0.41695 | 0.2915 | 0.52961 | 0.42963 | 0.41667
42810.4365 | -305 | 18.6263 | 18.6715 | 18.6458 | 18.6571 | 17.9917 | 16.6318 | 14.6996 | 16.739 | 17.2258 | 17.3261 | 17.3309 | 16.879 | 15.9378 | 14.5418 | 15.0632 | 15.0449 | 15.5892 | 13.4325 | 13.5447 | 14.1136 |  |  |  | 16.6374 | 15.9668 | 15.0799 | 10.3051 | 9.5218 | 10.0607 | 17.3232 | 16.432 | 15.2342 | 16.9523 | 16.2256 | 15.2332 | 10.7924 | 11.4743 |  | 12.1238 | 10.3615 | 10.1905 | 8.5716 |  | 6.479 | 6.4794 | 6.0401 | 6.2304 | 6.4043 | 6.657 | 7.2556 | 4.7445 | 6.3863 | 4.9536 | 6.6289 | 8.1704 | 42.2834 | 46.6697 | 42.9661 | 15.2002 |  |  | 0.1093 | -0.13331 | 0.04982 | 0.03417 | 0.034336 | -0.13451 | 0.43426 | -0.14867 | -0.36564 | -0.50432 | 0.055926 | 8.8691 | 8.8703 | 2.0084 | 15.9256 | 16.7766 | 17.2947 | 17.6174 | 17.5774 | 16.5547 | 14.9089 | 16.8754 | 17.2073 | 17.5014 | 17.5417 | 17.2853 | 16.4875 | 14.7169 | 7.2354 | 8.6076 | 6.03 | 6.0607 | 5.9596 | 6.609 | 7.5988 | 16.01 | 15.6023 | 15.4497 | 14.3654 | 14.2551 | 14.1865 |  |  |  | 10.7243 | 9.3611 | 9.0178 | 8.9827 | 0.044418 | 0.12085 | 12.7506 |  |  | 10.646 |  |  | 16.8872 | 16.0819 | 15.0684 | 16.385 | 15.6712 | 14.7784 | 10.1612 | 10.5277 | 11.2177 | 10.986 | 9.2147 |  | 10.589 | 8.3503 | 9.8503 | 9.3415 | 11.0483 | 12.2174 |  | 12.2418 |  |  | 11.714 | 12.5509 | 12.6185 | [6 empty] | 12.5799 |  |  | 11.3044 |  |  | 9.143 | 10.3328 | 11.9 | 7.6845 | 8.961 | 12.5333 | 7.8859 | 9.5276 | 12.1801 | 9.2324 | 10.482 | 7.6474 | 10.2031 | 8.1257 | 10.1525 | 7.5586 | 9.4672 | 13.0349 | 10.4694 | 10.1607 | 11.4711 | 8.1307 | 9.7624 | 12.6817 | 7.933 | 10.2075 | 9.7731 | 9.811 | 8.567 | 10.1762 | 0.020403 | 20.9557 | 0.032466 | 0.047588 | -37.9076 | 3.1206 | -11.3 | 0.3 | 0.38773 | -0.42548 | 0.26011 | 0.21542 | 0.21601 | -0.42754 | 0.76819 | 0.40567 | 0.40536 | 0.4173 | 0.27771 | 0.52657 | 0.43024 | 0.41658
42810.4365 | -304 | 18.6205 | 18.6732 | 18.6446 | 18.6465 | 17.9955 | 16.635 | 14.6954 | 16.7385 | 17.2279 | 17.3252 | 17.3273 | 16.8765 | 15.9303 | 14.5388 | 15.0693 | 15.0508 | 15.6019 | 13.4372 | 13.5467 | 14.122 |  |  |  | 16.6267 | 15.9676 | 15.0846 | 10.3039 | 9.5317 | 10.0168 | 17.3176 | 16.432 | 15.2319 | 16.9477 | 16.2253 | 15.226 | 10.8006 | 11.4458 |  | 12.1253 | 10.3695 | 10.1967 | 8.5741 |  | 6.4824 | 6.4904 | 6.0459 | 6.2449 | 6.4335 | 6.6911 | 7.2835 | 4.691 | 6.3824 | 4.8023 | 6.6291 | 8.172 | 42.274 | 46.6684 | 42.9438 | 15.1928 |  |  | -0.19757 | -0.15105 | -0.026404 | -0.21553 | -0.13717 | 0.42535 | 0.35014 | -0.24855 | -0.2446 | -0.55279 | -0.25305 | 8.8709 | 8.8722 | 2.0084 | 15.9255 | 16.7813 | 17.2971 | 17.6139 | 17.5786 | 16.5636 | 14.9111 | 16.8832 | 17.1996 | 17.4996 | 17.5445 | 17.2878 | 16.4941 | 14.7167 | 7.3206 | 8.5949 | 6.1314 | 6.178 | 6.0334 | 6.6071 | 7.594 | 16.0096 | 15.6006 | 15.4536 | 14.367 | 14.2598 | 14.1939 |  |  |  | 10.7243 | 9.3645 | 9.025 | 8.9796 | 0.168 | -0.016725 | 12.7441 |  |  | 10.6485 |  |  | 16.8852 | 16.083 | 15.0573 | 16.3833 | 15.6699 | 14.7763 | 10.1613 | 10.5185 | 11.2214 | 10.9849 | 9.227 |  | 10.5818 | 8.3209 | 9.8465 | 9.3365 | 11.0395 | 12.2143 |  | 12.2411 |  |  | 11.7169 | 12.5547 | 12.6232 | [6 empty] | 12.5875 |  |  | 11.2859 |  |  | 9.1493 | 10.3244 | 11.8975 | 7.6821 | 8.9698 | 12.5433 | 7.8883 | 9.5288 | 12.1766 | 9.2301 | 10.4749 | 7.6454 | 10.2116 | 8.1145 | 10.1502 | 7.5582 | 9.4835 | 13.0406 | 10.477 | 10.1638 | 11.4829 | 8.1342 | 9.7631 | 12.6721 | 7.9438 | 10.2125 | 9.7682 | 9.8055 | 8.5693 | 10.1811 | 0.11824 | 20.9541 | 0.032402 | 0.047683 | -37.9531 | 3.1206 | 2.04 | 0.37 | -0.52126 | -0.45292 | -0.18937 | -0.54103 | -0.43177 | 0.76032 | 0.68984 | 0.4051 | 0.40605 | 0.41715 | 0.26803 | 0.51474 | 0.43045 | 0.41667
42810.4365 | -303 | 18.6237 | 18.6758 | 18.6484 | 18.6533 | 17.9894 | 16.6336 | 14.6973 | 16.7385 | 17.2254 | 17.3233 | 17.3346 | 16.8842 | 15.9252 | 14.5408 | 15.0706 | 15.0476 | 15.5893 | 13.4378 | 13.5505 | 14.1083 |  |  |  | 16.6248 | 15.974 | 15.0876 | 10.3057 | 9.5315 | 10.0069 | 17.3118 | 16.4366 | 15.2327 | 16.9484 | 16.222 | 15.2309 | 10.796 | 11.4248 |  | 12.1236 | 10.3755 | 10.2002 | 8.5982 |  | 6.4874 | 6.4964 | 6.0628 | 6.2456 | 6.4525 | 6.7042 | 7.3091 | 4.6362 | 6.3826 | 4.6676 | 6.625 | 8.1819 | 42.2701 | 46.6696 | 42.9302 | 15.1889 |  |  | 0.13295 | 0.18671 | 0.070192 | 0.045342 | -0.014292 | 0.079708 | 0.38891 | -0.2295 | -1.3696 | -0.30124 | -0.31584 | 8.8693 | 8.8705 | 2.0087 | 15.925 | 16.773 | 17.2964 | 17.6037 | 17.5723 | 16.5482 | 14.9029 | 16.8733 | 17.2057 | 17.4905 | 17.5392 | 17.2784 | 16.4817 | 14.7167 | 7.3412 | 8.6138 | 6.1182 | 6.2541 | 6.1222 | 6.6166 | 7.6002 | 16.006 | 15.6034 | 15.4504 | 14.3713 | 14.2578 | 14.1964 |  |  |  | 10.7181 | 9.3677 | 9.0288 | 8.9788 | -0.01231 | -0.11911 | 12.7392 |  |  | 10.6542 |  |  | 16.8867 | 16.0845 | 15.0669 | 16.3876 | 15.6674 | 14.7789 | 10.1677 | 10.5193 | 11.2172 | 10.9873 | 9.2155 |  | 10.5773 | 8.3475 | 9.8363 | 9.3049 | 11.0346 | 12.1914 |  | 12.2236 |  |  | 11.7263 | 12.5297 | 12.627 | [6 empty] | 12.579 |  |  | 11.2757 |  |  | 9.152 | 10.3185 | 11.885 | 7.686 | 8.9784 | 12.545 | 7.8764 | 9.5206 | 12.1665 | 9.2266 | 10.4698 | 7.6495 | 10.2195 | 8.1089 | 10.1383 | 7.571 | 9.4946 | 13.0531 | 10.4851 | 10.1684 | 11.4899 | 8.1269 | 9.7769 | 12.6554 | 7.9463 | 10.2228 | 9.7748 | 9.8057 | 8.5737 | 10.1724 | 0.078183 | 20.9535 | 0.032064 | 0.048298 | -38.0463 | 3.1205 | 6.49 | 0.28 | 0.4276 | 0.50356 | 0.30876 | 0.24815 | -0.13937 | 0.32914 | 0.72704 | 0.40527 | 0.40497 | 0.41786 | 0.26684 | 0.51692 | 0.42963 | 0.41649
42810.4365 | -302 | 18.6226 | 18.668 | 18.6469 | 18.6511 | 17.9853 | 16.6256 | 14.6997 | 16.7356 | 17.229 | 17.3217 | 17.3321 | 16.8818 | 15.928 | 14.5379 | 15.0704 | 15.0464 | 15.5911 | 13.4323 | 13.5436 | 14.1215 |  |  |  | 16.6364 | 15.9699 | 15.0729 | 10.3036 | 9.5314 | 10.0185 | 17.3105 | 16.4333 | 15.2329 | 16.948 | 16.22 | 15.2271 | 10.7944 | 11.4086 |  | 12.1204 | 10.3851 | 10.2072 | 8.6077 |  | 6.4897 | 6.4998 | 6.0699 | 6.2484 | 6.4458 | 6.6849 | 7.2868 | 4.6263 | 6.3857 | 4.5982 | 6.6257 | 8.1726 | 42.2601 | 46.65 | 42.9136 | 15.1749 |  |  | 0.004819 | 0.12166 | -0.12826 | -0.18136 | 0.06982 | -0.049088 | 0.39614 | -0.13684 | -0.36564 | -0.40278 | -0.17715 | 8.8724 | 8.8736 | 2.0083 | 15.9315 | 16.7752 | 17.3033 | 17.6175 | 17.5821 | 16.5511 | 14.9083 | 16.8766 | 17.2063 | 17.5025 | 17.5463 | 17.281 | 16.4868 | 14.7212 | 7.2972 | 8.6022 | 6.0618 | 6.2604 | 6.1754 | 6.6121 | 7.5993 | 16.0095 | 15.6044 | 15.455 | 14.3745 | 14.2473 | 14.189 |  |  |  | 10.7206 | 9.3673 | 9.0326 | 8.9931 | 0.083115 | 2.48e-05 | 12.7483 |  |  | 10.6552 |  |  | 16.8872 | 16.0798 | 15.064 | 16.3863 | 15.6758 | 14.7803 | 10.1878 | 10.5234 | 11.2126 | 10.9917 | 9.2175 |  | 10.5732 | 8.4593 | 9.8398 | 9.303 | 11.0356 | 12.1731 |  | 12.2298 |  |  | 11.7135 | 12.5481 | 12.6441 | [6 empty] | 12.5825 |  |  | 11.282 |  |  | 9.1646 | 10.3344 | 11.9065 | 7.7053 | 9.005 | 12.5689 | 7.8894 | 9.5317 | 12.1723 | 9.2405 | 10.4815 | 7.6754 | 10.2333 | 8.123 | 10.1539 | 7.5834 | 9.5092 | 13.0584 | 10.4836 | 10.169 | 11.4839 | 8.131 | 9.7727 | 12.6555 | 7.9632 | 10.2262 | 9.7709 | 9.8039 | 8.5696 | 10.1767 | 0.020403 | 20.9519 | 0.032225 | 0.047654 | -37.9862 | 3.1205 | -4.95 | 0.31 | 0.081408 | 0.40648 | -0.41737 | -0.4963 | 0.30804 | -0.25829 | 0.73374 | 0.40508 | 0.40198 | 0.41795 | 0.27121 | 0.52309 | 0.42931 | 0.41617
42810.4366 | -301 | 18.6217 | 18.6686 | 18.6477 | 18.6508 | 17.9864 | 16.6281 | 14.697 | 16.7363 | 17.2292 | 17.3261 | 17.3355 | 16.8769 | 15.9256 | 14.5394 | 15.0606 | 15.0497 | 15.5973 | 13.4366 | 13.5501 | 14.1151 |  |  |  | 16.6386 | 15.9684 | 15.0727 | 10.2923 | 9.5356 | 10.0403 | 17.318 | 16.4372 | 15.2319 | 16.9493 | 16.2244 | 15.2291 | 10.7959 | 11.4228 |  | 12.1179 | 10.3963 | 10.2127 | 8.6181 |  | 6.4933 | 6.4938 | 6.0653 | 6.2471 | 6.4426 | 6.6663 | 7.2442 | 4.64 | 6.3823 | 4.572 | 6.631 | 8.1713 | 42.2436 | 46.6251 | 42.8951 | 15.1645 |  |  | 0.10207 | -0.041969 | 0.029448 | -0.042714 | -0.011664 | 0.023196 | 0.3002 | -0.21044 | -0.26814 | -0.30543 | -0.1692 | 8.8717 | 8.8728 | 2.0084 | 15.9227 | 16.7683 | 17.3016 | 17.6056 | 17.5695 | 16.554 | 14.905 | 16.8706 | 17.2008 | 17.4949 | 17.5314 | 17.2724 | 16.4844 | 14.7099 | 7.2234 | 8.5895 | 6.0268 | 6.2102 | 6.2191 | 6.6284 | 7.6156 | 16.0129 | 15.6097 | 15.4632 | 14.3751 | 14.2554 | 14.1866 |  |  |  | 10.7242 | 9.373 | 9.0215 | 9.0132 | -0.005624 | 0.045946 | 12.7398 |  |  | 10.6519 |  |  | 16.8807 | 16.0768 | 15.0579 | 16.381 | 15.668 | 14.7693 | 10.1915 | 10.5147 | 11.202 | 10.9834 | 9.197 |  | 10.5783 | 8.5819 | 9.8399 | 9.2985 | 11.0347 | 12.1462 |  | 12.2346 |  |  | 11.7082 | 12.5638 | 12.649 | [6 empty] | 12.5815 |  |  | 11.2832 |  |  | 9.1636 | 10.3224 | 11.8942 | 7.7032 | 9.0032 | 12.5643 | 7.871 | 9.5276 | 12.1669 | 9.2248 | 10.4802 | 7.6705 | 10.2203 | 8.1043 | 10.1506 | 7.6058 | 9.5203 | 13.0729 | 10.4969 | 10.1687 | 11.4831 | 8.1314 | 9.7806 | 12.6573 | 7.9815 | 10.223 | 9.7732 | 9.7936 | 8.5728 | 10.1852 | 0.029263 | 20.9529 | 0.032483 | 0.047806 | -37.929 | 3.1206 | 15.54 | 0.38 | 0.37468 | -0.23874 | 0.19999 | -0.24085 | -0.1259 | 0.17755 | 0.63872 | 0.40581 | 0.39858 | 0.41804 | 0.2813 | 0.52887 | 0.42907 | 0.41573
42810.4366 | -300 | 18.6254 | 18.6742 | 18.6438 | 18.6483 | 17.9905 | 16.6354 | 14.6952 | 16.739 | 17.224 | 17.3185 | 17.3364 | 16.88 | 15.9271 | 14.5392 | 15.0639 | 15.0409 | 15.589 | 13.4317 | 13.5446 | 14.1133 |  |  |  | 16.6379 | 15.9656 | 15.074 | 10.294 | 9.5329 | 10.071 | 17.3142 | 16.4175 | 15.2154 | 16.9386 | 16.2103 | 15.2128 | 10.7843 | 11.4404 |  | 12.1035 | 10.397 | 10.2013 | 8.6083 |  | 6.5039 | 6.4993 | 6.0687 | 6.2462 | 6.4397 | 6.6557 | 7.2295 | 4.6657 | 6.3862 | 4.5867 | 6.626 | 8.17 | 42.213 | 46.6155 | 42.8878 | 15.1598 |  |  | -0.000437 | -0.12214 | -0.11512 | -0.12157 | 0.027104 | 0.1671 | 0.62416 | -0.18284 | -0.19575 | -0.26452 | -0.075614 | 8.8714 | 8.8726 | 2.0084 | 15.923 | 16.7646 | 17.298 | 17.6117 | 17.5746 | 16.5498 | 14.903 | 16.8722 | 17.1981 | 17.4935 | 17.536 | 17.2711 | 16.48 | 14.7114 | 7.1321 | 8.569 | 5.9422 | 6.1322 | 6.1584 | 6.6171 | 7.6052 | 16.0142 | 15.6124 | 15.4566 | 14.3785 | 14.2599 | 14.1969 |  |  |  | 10.7178 | 9.375 | 9.0279 | 9.0213 | 0.091827 | 0.019221 | 12.7345 |  |  | 10.6539 |  |  | 16.8817 | 16.0773 | 15.0608 | 16.3779 | 15.6656 | 14.7764 | 10.2114 | 10.5176 | 11.1932 | 10.9812 | 9.1882 |  | 10.5714 | 8.6825 | 9.8486 | 9.2827 | 11.0344 | 12.1055 |  | 12.232 |  |  | 11.7067 | 12.5518 | 12.6534 | [6 empty] | 12.5791 |  |  | 11.2752 |  |  | 9.1654 | 10.3187 | 11.8849 | 7.7136 | 9.02 | 12.5631 | 7.8729 | 9.5342 | 12.1619 | 9.2249 | 10.4791 | 7.6848 | 10.2189 | 8.1086 | 10.1408 | 7.607 | 9.5235 | 13.0535 | 10.4946 | 10.1712 | 11.4903 | 8.107 | 9.7855 | 12.6424 | 7.9753 | 10.2194 | 9.7673 | 9.789 | 8.5665 | 10.1727 | -0.17258 | 20.953 | 0.032448 | 0.048117 | -37.9246 | 3.1205 | 20.22 | 0.34 | -0.024517 | -0.40728 | -0.3954 | -0.40633 | 0.19192 | 0.47653 | 0.92097 | 0.40583 | 0.39607 | 0.41847 | 0.29012 | 0.53706 | 0.42896 | 0.4153
42810.4366 | -299 | 18.6226 | 18.6606 | 18.6426 | 18.6489 | 17.9863 | 16.6309 | 14.6983 | 16.7334 | 17.224 | 17.3175 | 17.3316 | 16.8705 | 15.9254 | 14.5274 | 15.0719 | 15.0447 | 15.5929 | 13.4291 | 13.5462 | 14.119 |  |  |  | 16.6322 | 15.9731 | 15.0812 | 10.3061 | 9.5416 | 10.074 | 17.3065 | 16.4243 | 15.2264 | 16.9272 | 16.2159 | 15.2187 | 10.7882 | 11.4432 |  | 12.1109 | 10.4082 | 10.209 | 8.6096 |  | 6.5042 | 6.5017 | 6.0661 | 6.2413 | 6.4283 | 6.6435 | 7.2496 | 4.6693 | 6.3878 | 4.5481 | 6.6281 | 8.162 | 42.1846 | 46.6094 | 42.8734 | 15.154 |  |  | 0.25452 | -0.000569 | 0.006452 | -0.10514 | 0.15656 | 0.11256 | 0.42703 | -0.16247 | 0.28121 | -0.16235 | -0.27392 | 8.8695 | 8.8707 | 2.0086 | 15.9248 | 16.765 | 17.2944 | 17.6087 | 17.574 | 16.5543 | 14.9005 | 16.8714 | 17.2052 | 17.494 | 17.5394 | 17.2736 | 16.4823 | 14.7084 | 7.0689 | 8.5673 | 5.8813 | 6.0504 | 6.0821 | 6.6198 | 7.6106 | 16.0064 | 15.6031 | 15.4482 | 14.3702 | 14.2548 | 14.19 |  |  |  | 10.7115 | 9.3692 | 9.0199 | 9.0217 | -0.035001 | 0.095442 | 12.7394 |  |  | 10.656 |  |  | 16.8834 | 16.0771 | 15.0606 | 16.3784 | 15.6635 | 14.7737 | 10.2184 | 10.5115 | 11.1865 | 10.9838 | 9.1769 |  | 10.5676 | 8.7818 | 9.8444 | 9.2623 | 11.0285 | 12.0905 |  | 12.2241 |  |  | 11.7093 | 12.5578 | 12.6428 | [6 empty] | 12.5539 |  |  | 11.2654 |  |  | 9.1737 | 10.324 | 11.8934 | 7.7357 | 9.0269 | 12.5758 | 7.8707 | 9.5405 | 12.1694 | 9.2242 | 10.4897 | 7.7037 | 10.2334 | 8.1134 | 10.1561 | 7.6301 | 9.5291 | 13.0653 | 10.4952 | 10.1773 | 11.4684 | 8.1076 | 9.7828 | 12.6376 | 7.9899 | 10.2242 | 9.7701 | 9.7811 | 8.5635 | 10.178 | -0.10787 | 20.9533 | 0.032425 | 0.047502 | -38.0372 | 3.1206 | 11.27 | 0.35 | 0.59169 | -0.027799 | 0.09361 | -0.37788 | 0.46123 | 0.3911 | 0.76175 | 0.40602 | 0.39318 | 0.41884 | 0.29747 | 0.54447 | 0.42905 | 0.41508
42810.4366 | -298 | 18.6224 | 18.6736 | 18.6439 | 18.6524 | 17.9895 | 16.6393 | 14.6938 | 16.7417 | 17.2309 | 17.3237 | 17.3419 | 16.8818 | 15.922 | 14.5385 | 15.0737 | 15.0537 | 15.6043 | 13.4442 | 13.5476 | 14.1236 |  |  |  | 16.6309 | 15.9726 | 15.0891 | 10.3107 | 9.5434 | 10.0675 | 17.3141 | 16.4303 | 15.2285 | 16.9373 | 16.2252 | 15.2283 | 10.796 | 11.456 |  | 12.1282 | 10.4205 | 10.2178 | 8.6164 |  | 6.5007 | 6.4939 | 6.0503 | 6.225 | 6.4056 | 6.6242 | 7.2493 | 4.6958 | 6.3823 | 4.534 | 6.6211 | 8.1723 | 42.1651 | 46.6186 | 42.8792 | 15.1519 |  |  | -0.053665 | 0.009287 | -0.031004 | -0.02497 | 0.083616 | -0.29025 | 0.35409 | -0.05536 | -0.41448 | -0.24039 | -0.2006 | 8.8675 | 8.8686 | 2.0084 | 15.9267 | 16.7697 | 17.2913 | 17.6149 | 17.5765 | 16.5571 | 14.897 | 16.8731 | 17.2074 | 17.4971 | 17.5468 | 17.2838 | 16.4834 | 14.7149 | 7.0093 | 8.5673 | 5.8188 | 5.9691 | 6.0112 | 6.621 | 7.6193 | 16.0042 | 15.6028 | 15.4463 | 14.3634 | 14.2572 | 14.1874 |  |  |  | 10.7111 | 9.3697 | 9.008 | 9.0474 | -0.035001 | 0.040864 | 12.7417 |  |  | 10.6549 |  |  | 16.8872 | 16.0827 | 15.0601 | 16.3862 | 15.6626 | 14.7693 | 10.2372 | 10.5141 | 11.1795 | 10.9774 | 9.1728 |  | 10.5679 | 8.8788 | 9.8421 | 9.2465 | 11.0283 | 12.0661 |  | 12.2247 |  |  | 11.7198 | 12.5724 | 12.6514 | [6 empty] | 12.5465 |  |  | 11.2739 |  |  | 9.1858 | 10.3367 | 11.8863 | 7.7477 | 9.0357 | 12.581 | 7.8806 | 9.5438 | 12.1689 | 9.2338 | 10.4983 | 7.7051 | 10.2485 | 8.1182 | 10.1497 | 7.6489 | 9.5407 | 13.0659 | 10.501 | 10.1832 | 11.4595 | 8.106 | 9.7962 | 12.649 | 7.9852 | 10.2157 | 9.7787 | 9.7775 | 8.5622 | 10.1764 | -0.14716 | 20.954 | 0.032357 | 0.047523 | -38.1248 | 3.1205 | 1.78 | 0.37 | -0.27169 | 0.11231 | -0.2052 | -0.18415 | 0.33707 | -0.62799 | 0.69363 | 0.40615 | 0.39041 | 0.41928 | 0.30422 | 0.55241 | 0.42912 | 0.41435
42810.4366 | -297 | 18.6126 | 18.6627 | 18.6321 | 18.6449 | 17.9934 | 16.6294 | 14.6966 | 16.7353 | 17.223 | 17.3154 | 17.3333 | 16.8818 | 15.9191 | 14.5298 | 15.0636 | 15.0396 | 15.5964 | 13.4328 | 13.5457 | 14.1237 |  |  |  | 16.6271 | 15.9667 | 15.0792 | 10.3073 | 9.5271 | 10.0715 | 17.3062 | 16.4245 | 15.2207 | 16.9384 | 16.2218 | 15.2162 | 10.7864 | 11.4565 |  | 12.1151 | 10.4201 | 10.2142 | 8.6379 |  | 6.4979 | 6.4993 | 6.0316 | 6.2088 | 6.3945 | 6.6162 | 7.2698 | 4.7514 | 6.3907 | 4.5184 | 6.6134 | 8.1662 | 42.1487 | 46.6361 | 42.8762 | 15.1429 |  |  | 0.089587 | 0.019803 | 0.053104 | 0.22736 | 0.14999 | -0.42956 | 0.30218 | -0.04222 | -0.6336 | -1.2598 | -0.11754 | 8.8684 | 8.8696 | 2.0085 | 15.9219 | 16.7769 | 17.2934 | 17.6138 | 17.5746 | 16.551 | 14.9032 | 16.8797 | 17.2077 | 17.504 | 17.5388 | 17.2849 | 16.4819 | 14.7111 | 6.9637 | 8.5839 | 5.8339 | 5.8952 | 5.9489 | 6.6254 | 7.6139 | 16.0193 | 15.6062 | 15.465 | 14.3696 | 14.2534 | 14.1832 |  |  |  | 10.7195 | 9.3644 | 9.0201 | 9.0491 | -0.10166 | 0.047828 | 12.7424 |  |  | 10.6546 |  |  | 16.8834 | 16.0828 | 15.0561 | 16.3827 | 15.6648 | 14.7695 | 10.2509 | 10.5165 | 11.171 | 10.971 | 9.1847 |  | 10.5749 | 9.0115 | 9.8417 | 9.2312 | 11.0248 | 12.0495 |  | 12.2245 |  |  | 11.7174 | 12.5625 | 12.6539 | [6 empty] | 12.5485 |  |  | 11.2777 |  |  | 9.1924 | 10.3313 | 11.8873 | 7.7568 | 9.0499 | 12.5801 | 7.8826 | 9.5377 | 12.1647 | 9.2326 | 10.4998 | 7.7162 | 10.2436 | 8.1261 | 10.1592 | 7.661 | 9.5536 | 13.0734 | 10.5061 | 10.1825 | 11.4552 | 8.1025 | 9.8068 | 12.6476 | 7.9969 | 10.2169 | 9.7801 | 9.7806 | 8.5614 | 10.1832 | 0.19837 | 20.9527 | 0.032127 | 0.047646 | -38.0899 | 3.1205 | 18.78 | 0.33 | 0.35104 | 0.164 | 0.26856 | 0.55569 | 0.45143 | -0.76397 | 0.64076 | 0.40604 | 0.38671 | 0.41958 | 0.3098 | 0.5501 | 0.42821 | 0.41458
42810.4366 | -296 | 18.6183 | 18.6638 | 18.6379 | 18.6463 | 17.9882 | 16.6325 | 14.6979 | 16.735 | 17.224 | 17.3224 | 17.3346 | 16.8761 | 15.9196 | 14.539 | 15.0682 | 15.0479 | 15.6029 | 13.4366 | 13.5494 | 14.1221 |  |  |  | 16.634 | 15.9682 | 15.0776 | 10.316 | 9.5332 | 10.0858 | 17.3176 | 16.4331 | 15.2302 | 16.9511 | 16.2323 | 15.228 | 10.7938 | 11.4644 |  | 12.1251 | 10.4347 | 10.2219 | 8.7077 |  | 6.4957 | 6.4842 | 6.0035 | 6.191 | 6.3725 | 6.5863 | 7.2794 | 4.7301 | 6.3853 | 4.5368 | 6.6206 | 8.1756 | 42.1459 | 46.6472 | 42.8778 | 15.1339 |  |  | -0.044465 | -0.038681 | 0.009736 | 0.12222 | 0.038276 | -0.069456 | 0.62416 | -0.088216 | -0.38685 | -1.358 | -0.37545 | 8.8698 | 8.8709 | 2.0084 | 15.9058 | 16.7587 | 17.2814 | 17.6003 | 17.5565 | 16.5384 | 14.8891 | 16.871 | 17.1957 | 17.4875 | 17.5307 | 17.2724 | 16.4723 | 14.6994 | 6.8297 | 8.5887 | 5.8456 | 5.8425 | 5.8822 | 6.6306 | 7.6199 | 16.0062 | 15.6051 | 15.4491 | 14.3596 | 14.2478 | 14.1829 |  |  |  | 10.7045 | 9.353 | 9.0053 | 9.0252 | -0.022237 | -0.10292 | 12.7384 |  |  | 10.6495 |  |  | 16.8771 | 16.0742 | 15.0593 | 16.3871 | 15.6665 | 14.7704 | 10.2616 | 10.5149 | 11.1632 | 10.9707 | 9.2216 |  | 10.5633 | 9.127 | 9.8478 | 9.2034 | 11.0219 | 12.0331 |  | 12.2285 |  |  | 11.7077 | 12.575 | 12.6636 | [6 empty] | 12.5392 |  |  | 11.2822 |  |  | 9.1878 | 10.3258 | 11.8827 | 7.7564 | 9.0425 | 12.5667 | 7.8767 | 9.5274 | 12.1657 | 9.2256 | 10.4962 | 7.7231 | 10.2313 | 8.119 | 10.1569 | 7.6689 | 9.5606 | 13.0738 | 10.5064 | 10.1751 | 11.4437 | 8.0977 | 9.8034 | 12.6361 | 8.0006 | 10.2076 | 9.7697 | 9.7713 | 8.5514 | 10.1736 | -0.018887 | 20.9537 | 0.031381 | 0.047154 | -37.9883 | 3.1205 | 0.89 | 0.33 | -0.24731 | -0.2292 | 0.11499 | 0.40741 | 0.22804 | -0.30718 | 0.92085 | 0.40464 | 0.3837 | 0.42026 | 0.3253 | 0.54951 | 0.42651 | 0.41475
42810.4366 | -295 | 18.6237 | 18.6665 | 18.6404 | 18.648 | 17.9913 | 16.6281 | 14.6955 | 16.7343 | 17.2239 | 17.3179 | 17.3329 | 16.8789 | 15.9222 | 14.5387 | 15.0589 | 15.0498 | 15.5954 | 13.4313 | 13.5478 | 14.115 |  |  |  | 16.6278 | 15.9626 | 15.0746 | 10.3153 | 9.5327 | 10.0929 | 17.3088 | 16.4319 | 15.2228 | 16.9469 | 16.2224 | 15.2318 | 10.7971 | 11.439 |  | 12.1132 | 10.4299 | 10.226 | 8.7574 |  | 6.4934 | 6.4871 | 5.9965 | 6.1828 | 6.3621 | 6.5807 | 7.2744 | 4.7235 | 6.3843 | 4.5949 | 6.6199 | 8.1736 | 42.1545 | 46.6554 | 42.882 | 15.1417 |  |  | 0.13099 | 0.022431 | 0.058364 | -0.049942 | 0.090188 | -0.10231 | 0.55911 | -0.20321 | -0.39716 | -0.3648 | -0.48672 | 8.8705 | 8.8716 | 2.0086 | 15.9132 | 16.7707 | 17.2953 | 17.6055 | 17.5727 | 16.5546 | 14.8932 | 16.8577 | 17.1944 | 17.4853 | 17.5345 | 17.2682 | 16.4764 | 14.7017 | 6.6998 | 8.5605 | 5.8262 | 5.8371 | 5.8338 | 6.6271 | 7.6214 | 16.0109 | 15.6081 | 15.456 | 14.3649 | 14.2511 | 14.1868 |  |  |  | 10.7093 | 9.3574 | 9.0033 | 9.0132 | -0.14441 | -0.17989 | 12.7513 |  |  | 10.6527 |  |  | 16.8824 | 16.0751 | 15.0634 | 16.388 | 15.673 | 14.7672 | 10.2789 | 10.515 | 11.1677 | 10.98 | 9.2202 |  | 10.57 | 9.2219 | 9.8533 | 9.2097 | 11.0343 | 12.0223 |  | 12.2334 |  |  | 11.6964 | 12.5819 | 12.6713 | [6 empty] | 12.5389 |  |  | 11.2857 |  |  | 9.1816 | 10.3212 | 11.8784 | 7.7532 | 9.0468 | 12.5565 | 7.8818 | 9.5221 | 12.1729 | 9.2265 | 10.4916 | 7.7328 | 10.2282 | 8.1158 | 10.1586 | 7.6821 | 9.5643 | 13.0769 | 10.5102 | 10.1731 | 11.4391 | 8.1015 | 9.8002 | 12.6302 | 8.0073 | 10.1937 | 9.7625 | 9.7682 | 8.555 | 10.1669 | -0.071082 | 20.953 | 0.031249 | 0.046749 | -37.9381 | 3.1205 | -15.03 | 0.37 | 0.42448 | 0.17454 | 0.28154 | -0.26043 | 0.35003 | -0.37282 | 0.87154 | 0.4049 | 0.38124 | 0.4205 | 0.33932 | 0.55183 | 0.42524 | 0.41524
42810.4366 | -294 | 18.6209 | 18.6705 | 18.6374 | 18.6487 | 17.9852 | 16.6255 | 14.6922 | 16.7341 | 17.2192 | 17.3179 | 17.3294 | 16.8793 | 15.9264 | 14.5343 | 15.0506 | 15.0439 | 15.5967 | 13.4325 | 13.5444 | 14.116 |  |  |  | 16.6257 | 15.9647 | 15.065 | 10.3128 | 9.5301 | 10.0771 | 17.3023 | 16.428 | 15.2202 | 16.9474 | 16.2251 | 15.2303 | 10.7939 | 11.3987 |  | 12.109 | 10.4248 | 10.2268 | 8.8026 |  | 6.4954 | 6.4807 | 5.9925 | 6.1827 | 6.3627 | 6.5827 | 7.293 | 4.7491 | 6.3823 | 4.6805 | 6.6184 | 8.1666 | 42.157 | 46.6537 | 42.8777 | 15.1306 |  |  | 0.003503 | -0.057081 | 0.11028 | 0.07031 | -0.087888 | -0.49658 | 0.45791 | -0.21176 | -0.82976 | -0.369 | -0.44679 | 8.8696 | 8.8708 | 2.0084 | 15.9277 | 16.7744 | 17.2977 | 17.6139 | 17.5755 | 16.5573 | 14.9024 | 16.8705 | 17.2068 | 17.4952 | 17.5395 | 17.2824 | 16.4812 | 14.7097 | 6.6068 | 8.545 | 5.8177 | 5.8597 | 5.8006 | 6.6309 | 7.6176 | 16.0096 | 15.6056 | 15.4585 | 14.3616 | 14.244 | 14.1906 |  |  |  | 10.7102 | 9.359 | 9.0021 | 8.9966 | -0.030341 | -0.14263 | 12.7505 |  |  | 10.6658 |  |  | 16.887 | 16.0743 | 15.0624 | 16.383 | 15.6717 | 14.7758 | 10.2837 | 10.5162 | 11.1702 | 10.9834 | 9.2348 |  | 10.5857 | 9.2861 | 9.8637 | 9.221 | 11.0399 | 12.0122 |  | 12.2331 |  |  | 11.6908 | 12.5937 | 12.6766 | [6 empty] | 12.5397 |  |  | 11.2854 |  |  | 9.1901 | 10.3219 | 11.8742 | 7.7413 | 9.0519 | 12.5548 | 7.8883 | 9.5172 | 12.1775 | 9.2324 | 10.4974 | 7.7393 | 10.2313 | 8.1129 | 10.1618 | 7.6933 | 9.5724 | 13.0884 | 10.5144 | 10.1773 | 11.432 | 8.1035 | 9.8045 | 12.6263 | 8.0147 | 10.1977 | 9.7621 | 9.7706 | 8.5572 | 10.1666 | 0.071828 | 20.9535 | 0.030905 | 0.046648 | -37.9365 | 3.1206 | -0.12 | 0.3 | 0.069415 | -0.27842 | 0.38699 | 0.30901 | -0.34554 | -0.82136 | 0.78873 | 0.40501 | 0.3798 | 0.42037 | 0.3501 | 0.55234 | 0.42388 | 0.41573
42810.4366 | -293 | 18.6155 | 18.6677 | 18.6382 | 18.6439 | 17.9758 | 16.6254 | 14.6895 | 16.7335 | 17.219 | 17.3192 | 17.3251 | 16.8754 | 15.9152 | 14.5251 | 15.0456 | 15.0351 | 15.5889 | 13.4291 | 13.5372 | 14.1145 |  |  |  | 16.6257 | 15.9661 | 15.0674 | 10.3076 | 9.5238 | 10.0488 | 17.2965 | 16.4211 | 15.2182 | 16.9416 | 16.2183 | 15.2225 | 10.7867 | 11.3695 |  | 12.1108 | 10.43 | 10.2224 | 8.8425 |  | 6.4927 | 6.4774 | 5.9918 | 6.1725 | 6.3514 | 6.6128 | 7.3023 | 4.7638 | 6.3879 | 4.7138 | 6.6179 | 8.1584 | 42.176 | 46.6528 | 42.8858 | 15.1194 |  |  | 0.031103 | -0.12214 | 0.19833 | 0.10579 | -0.070148 | -0.48016 | 0.39614 | -0.39509 | -1.4227 | 0.042207 | -0.24252 | 8.8701 | 8.8711 | 2.0084 | 15.9126 | 16.7694 | 17.2978 | 17.6098 | 17.5673 | 16.5492 | 14.899 | 16.8677 | 17.2027 | 17.487 | 17.5259 | 17.2739 | 16.484 | 14.7041 | 6.5381 | 8.5555 | 5.8345 | 5.8822 | 5.7785 | 6.6281 | 7.6238 | 15.9976 | 15.5906 | 15.4345 | 14.3591 | 14.2396 | 14.1758 |  |  |  | 10.6986 | 9.3462 | 8.9944 | 8.995 | -0.21592 | -0.191 | 12.7469 |  |  | 10.6604 |  |  | 16.8847 | 16.0771 | 15.0541 | 16.3873 | 15.6694 | 14.7652 | 10.2926 | 10.5196 | 11.1633 | 10.9803 | 9.2516 |  | 10.5667 | 9.3448 | 9.8516 | 9.1949 | 11.0194 | 11.9962 |  | 12.2255 |  |  | 11.7081 | 12.6176 | 12.6766 | [6 empty] | 12.5467 |  |  | 11.2917 |  |  | 9.1863 | 10.3185 | 11.8625 | 7.7295 | 9.0549 | 12.5507 | 7.8937 | 9.5139 | 12.1736 | 9.2313 | 10.5 | 7.7413 | 10.2311 | 8.1119 | 10.1631 | 7.71 | 9.5944 | 13.0967 | 10.5232 | 10.1879 | 11.4377 | 8.1059 | 9.8129 | 12.6393 | 8.0213 | 10.2033 | 9.7733 | 9.773 | 8.5555 | 10.1683 | -0.069733 | 20.9533 | 0.032116 | 0.047328 | -37.9402 | 3.1205 | -9.44 | 0.33 | 0.20683 | -0.40727 | 0.51898 | 0.37904 | -0.30872 | -0.80771 | 0.73365 | 0.40392 | 0.37777 | 0.42041 | 0.3574 | 0.55119 | 0.42253 | 0.41539
42810.4367 | -292 | 18.6173 | 18.6733 | 18.6436 | 18.6515 | 17.9867 | 16.6356 | 14.6963 | 16.7426 | 17.2274 | 17.3181 | 17.3326 | 16.8755 | 15.9138 | 14.5325 | 15.0522 | 15.0374 | 15.585 | 13.428 | 13.5401 | 14.1152 |  |  |  | 16.6269 | 15.9683 | 15.0687 | 10.3043 | 9.5328 | 10.0437 | 17.2874 | 16.4119 | 15.2087 | 16.9331 | 16.2101 | 15.2147 | 10.7839 | 11.331 |  | 12.1004 | 10.4353 | 10.2184 | 8.8458 |  | 6.4997 | 6.4796 | 5.9929 | 6.1792 | 6.353 | 6.6308 | 7.2963 | 4.7884 | 6.3922 | 4.774 | 6.6243 | 8.1607 | 42.1927 | 46.664 | 42.8923 | 15.1126 |  |  | 0.048847 | 8.7e-05 | 0.13524 | -0.00197 | -0.05832 | 0.084964 | 0.4428 | -0.42072 | -0.45165 | 0.077453 | -0.13264 | 8.8682 | 8.8696 | 2.0083 | 15.9143 | 16.7703 | 17.2902 | 17.6101 | 17.568 | 16.5453 | 14.9034 | 16.8665 | 17.2022 | 17.4867 | 17.5307 | 17.2762 | 16.4887 | 14.7097 | 6.5097 | 8.5577 | 5.8243 | 5.8859 | 5.772 | 6.6372 | 7.6305 | 15.9971 | 15.5929 | 15.453 | 14.3668 | 14.2402 | 14.1789 |  |  |  | 10.7099 | 9.3488 | 9.0056 | 9.0461 | -0.37598 | -0.096145 | 12.7573 |  |  | 10.6678 |  |  | 16.884 | 16.0819 | 15.0578 | 16.383 | 15.6716 | 14.7699 | 10.3015 | 10.526 | 11.1612 | 10.9784 | 9.2577 |  | 10.5796 | 9.4026 | 9.8589 | 9.1924 | 11.0319 | 12.0028 |  | 12.2298 |  |  | 11.7302 | 12.6245 | 12.6694 | [6 empty] | 12.5381 |  |  | 11.2929 |  |  | 9.1952 | 10.3237 | 11.8521 | 7.7291 | 9.063 | 12.5439 | 7.9015 | 9.5192 | 12.1834 | 9.2335 | 10.502 | 7.735 | 10.2319 | 8.1196 | 10.169 | 7.7198 | 9.6088 | 13.0913 | 10.5229 | 10.1873 | 11.4368 | 8.1094 | 9.8196 | 12.6311 | 8.0298 | 10.21 | 9.7693 | 9.7725 | 8.5469 | 10.1679 | -0.055096 | 20.9531 | 0.033051 | 0.048667 | -37.9051 | 3.1205 | -1.21 | 0.23 | 0.2592 | 0.01087 | 0.42857 | -0.051724 | -0.2815 | 0.33978 | 0.77567 | 0.40417 | 0.37641 | 0.4209 | 0.36162 | 0.5531 | 0.42235 | 0.41435
42810.4367 | -291 | 18.617 | 18.6751 | 18.6474 | 18.6486 | 17.991 | 16.6376 | 14.7011 | 16.7405 | 17.2305 | 17.3297 | 17.3246 | 16.883 | 15.9251 | 14.5275 | 15.0499 | 15.0377 | 15.5835 | 13.4276 | 13.5438 | 14.1191 |  |  |  | 16.6294 | 15.967 | 15.0676 | 10.3039 | 9.5339 | 10.0368 | 17.2991 | 16.4225 | 15.2206 | 16.94 | 16.2173 | 15.221 | 10.7945 | 11.3039 |  | 12.1118 | 10.4371 | 10.2302 | 8.8625 |  | 6.498 | 6.4784 | 5.9993 | 6.1787 | 6.3542 | 6.631 | 7.2868 | 4.838 | 6.3921 | 4.918 | 6.6248 | 8.1624 | 42.2116 | 46.6621 | 42.8972 | 15.1063 |  |  | -0.19429 | -0.020281 | 0.044564 | 0.11237 | -0.03992 | -0.21008 | 0.47434 | -0.30704 | -0.26698 | -0.17829 | -0.12092 | 8.8692 | 8.8704 | 2.0088 | 15.9136 | 16.7664 | 17.2876 | 17.6066 | 17.5738 | 16.5432 | 14.8994 | 16.869 | 17.2019 | 17.4912 | 17.538 | 17.2743 | 16.4852 | 14.7038 | 6.3969 | 8.5737 | 5.8048 | 5.841 | 5.7799 | 6.6374 | 7.6219 | 15.9977 | 15.5953 | 15.4483 | 14.3686 | 14.2437 | 14.1816 |  |  |  | 10.7103 | 9.3467 | 9.0012 | 9.0409 | -0.076331 | -0.11214 | 12.7571 |  |  | 10.6608 |  |  | 16.8753 | 16.0795 | 15.0508 | 16.3803 | 15.6663 | 14.7654 | 10.3041 | 10.5259 | 11.1582 | 10.9878 | 9.2401 |  | 10.5758 | 9.4164 | 9.8664 | 9.2138 | 11.0329 | 11.9981 |  | 12.232 |  |  | 11.7391 | 12.6237 | 12.6687 | [6 empty] | 12.5366 |  |  | 11.3012 |  |  | 9.2101 | 10.3408 | 11.8492 | 7.7364 | 9.0758 | 12.5491 | 7.9089 | 9.5207 | 12.1985 | 9.2394 | 10.502 | 7.7402 | 10.2444 | 8.122 | 10.1692 | 7.7286 | 9.6199 | 13.0905 | 10.5205 | 10.1906 | 11.4364 | 8.1118 | 9.8207 | 12.6199 | 8.0337 | 10.2143 | 9.757 | 9.7763 | 8.5539 | 10.1571 | -0.18414 | 20.9535 | 0.033418 | 0.049926 | -37.8586 | 3.1205 | 6.08 | 0.25 | -0.51693 | -0.16596 | 0.24601 | 0.39064 | -0.2329 | -0.53428 | 0.80283 | 0.40454 | 0.37627 | 0.42034 | 0.37417 | 0.55427 | 0.42223 | 0.4145
42810.4367 | -290 | 18.6125 | 18.6698 | 18.6445 | 18.6488 | 17.9953 | 16.6348 | 14.6994 | 16.7356 | 17.224 | 17.3213 | 17.33 | 16.8764 | 15.9142 | 14.5283 | 15.0502 | 15.0424 | 15.592 | 13.4275 | 13.5465 | 14.1258 |  |  |  | 16.6389 | 15.9725 | 15.0723 | 10.3126 | 9.5406 | 10.03 | 17.2953 | 16.419 | 15.2153 | 16.9385 | 16.2147 | 15.2176 | 10.7881 | 11.302 |  | 12.1028 | 10.4428 | 10.2259 | 8.8515 |  | 6.4847 | 6.4706 | 5.9934 | 6.1739 | 6.3453 | 6.6166 | 7.3206 | 4.8693 | 6.3903 | 5.0167 | 6.6256 | 8.1619 | 42.2206 | 46.6554 | 42.9128 | 15.1107 |  |  | 0.055415 | -0.036053 | -0.060576 | 0.055198 | -0.12206 | 0.22493 | 0.4888 | -0.31229 | -0.66824 | -0.34068 | -0.20139 | 8.8717 | 8.8726 | 2.0085 | 15.9148 | 16.7611 | 17.2819 | 17.605 | 17.5721 | 16.5366 | 14.8956 | 16.8637 | 17.1953 | 17.4875 | 17.5326 | 17.2692 | 16.4751 | 14.697 | 6.3361 | 8.5766 | 5.7943 | 5.8169 | 5.8003 | 6.6311 | 7.6197 | 15.9946 | 15.5922 | 15.4468 | 14.3661 | 14.2431 | 14.1881 |  |  |  | 10.7071 | 9.3453 | 8.9999 | 9.0548 | 0.11391 | -0.15505 | 12.7683 |  |  | 10.6666 |  |  | 16.883 | 16.0858 | 15.0613 | 16.3906 | 15.6706 | 14.7755 | 10.3182 | 10.5279 | 11.1668 | 10.9848 | 9.2254 |  | 10.5718 | 9.3362 | 9.8654 | 9.2218 | 11.0339 | 11.9889 |  | 12.2287 |  |  | 11.7346 | 12.619 | 12.6634 | [6 empty] | 12.5406 |  |  | 11.3067 |  |  | 9.215 | 10.3382 | 11.8418 | 7.7383 | 9.0785 | 12.5529 | 7.9119 | 9.5196 | 12.1965 | 9.2357 | 10.4992 | 7.7425 | 10.2555 | 8.1299 | 10.1773 | 7.7509 | 9.6246 | 13.1029 | 10.5262 | 10.1968 | 11.4352 | 8.114 | 9.8168 | 12.6201 | 8.0386 | 10.2268 | 9.7675 | 9.788 | 8.5654 | 10.1541 | 0.081458 | 20.9539 | 0.033946 | 0.051453 | -37.8907 | 3.1205 | 10.89 | 0.23 | 0.27607 | -0.22127 | -0.28681 | 0.27379 | -0.40724 | 0.55283 | 0.81495 | 0.40481 | 0.37847 | 0.42015 | 0.3802 | 0.55518 | 0.42233 | 0.41401
42810.4367 | -289 | 18.6067 | 18.6654 | 18.6374 | 18.6405 | 17.9841 | 16.6302 | 14.6906 | 16.7319 | 17.2248 | 17.3138 | 17.3258 | 16.8718 | 15.9118 | 14.522 | 15.0433 | 15.0404 | 15.586 | 13.4272 | 13.5442 | 14.1153 |  |  |  | 16.6308 | 15.9633 | 15.068 | 10.303 | 9.5399 | 10.0116 | 17.2971 | 16.418 | 15.2103 | 16.9354 | 16.2168 | 15.2168 | 10.7915 | 11.3049 |  | 12.1079 | 10.4547 | 10.2268 | 8.8389 |  | 6.4867 | 6.474 | 5.9969 | 6.1735 | 6.3458 | 6.6326 | 7.3608 | 4.8695 | 6.3896 | 5.0398 | 6.628 | 8.1566 | 42.2295 | 46.622 | 42.9088 | 15.1026 |  |  | 0.015991 | -0.070225 | 0.11028 | 0.045342 | 0.02382 | -0.24754 | 0.52625 | -0.26958 | 0.19403 | -0.39858 | -0.31326 | 8.8698 | 8.8711 | 2.0083 | 15.9228 | 16.768 | 17.285 | 17.5955 | 17.5695 | 16.546 | 14.9017 | 16.8566 | 17.195 | 17.4889 | 17.535 | 17.2699 | 16.4733 | 14.7024 | 6.336 | 8.5778 | 5.7831 | 5.8511 | 5.8817 | 6.6332 | 7.6104 | 15.9984 | 15.5896 | 15.4427 | 14.3639 | 14.2446 | 14.1769 |  |  |  | 10.7053 | 9.3432 | 8.9984 | 9.0702 | 0.068528 | -0.068292 | 12.7634 |  |  | 10.6572 |  |  | 16.8842 | 16.0839 | 15.0596 | 16.3909 | 15.67 | 14.7767 | 10.3221 | 10.5261 | 11.1668 | 10.9917 | 9.2416 |  | 10.5725 | 9.2693 | 9.873 | 9.2197 | 11.036 | 12.0042 |  | 12.2315 |  |  | 11.7358 | 12.6206 | 12.6746 | [6 empty] | 12.5539 |  |  | 11.3153 |  |  | 9.2157 | 10.3347 | 11.8482 | 7.7437 | 9.0834 | 12.5439 | 7.9155 | 9.5218 | 12.1946 | 9.2332 | 10.4927 | 7.7441 | 10.2633 | 8.1381 | 10.1752 | 7.7672 | 9.6443 | 13.1138 | 10.5352 | 10.2058 | 11.431 | 8.1327 | 9.8217 | 12.6207 | 8.0536 | 10.2453 | 9.7771 | 9.7982 | 8.565 | 10.1619 | 0.035041 | 20.9527 | 0.033682 | 0.050664 | -37.8376 | 3.1205 | 18.6 | 0.32 | 0.14829 | -0.30882 | 0.38699 | 0.24814 | 0.17991 | -0.57996 | 0.84562 | 0.40439 | 0.38058 | 0.42027 | 0.38046 | 0.55535 | 0.42279 | 0.41352
42810.4367 | -288 | 18.6056 | 18.6639 | 18.6317 | 18.6404 | 17.9792 | 16.6239 | 14.681 | 16.7275 | 17.2187 | 17.3124 | 17.3217 | 16.8698 | 15.9083 | 14.5193 | 15.0582 | 15.0361 | 15.5891 | 13.4285 | 13.5461 | 14.1105 |  |  |  | 16.6342 | 15.9624 | 15.0701 | 10.3041 | 9.5364 | 10.0048 | 17.293 | 16.4216 | 15.2085 | 16.9369 | 16.2207 | 15.2205 | 10.7889 | 11.3104 |  | 12.109 | 10.4616 | 10.2311 | 8.8281 |  | 6.4726 | 6.4692 | 5.9824 | 6.1685 | 6.3405 | 6.6661 | 7.3938 | 4.8569 | 6.3887 | 5.0026 | 6.6183 | 8.1564 | 42.2485 | 46.606 | 42.921 | 15.1124 |  |  | 0.16713 | -0.16222 | 0.04522 | 0.031542 | 0.020536 | -0.002432 | 0.59722 | -0.36552 | -0.35357 | -0.9107 | -0.37684 | 8.8695 | 8.8704 | 2.0085 | 15.9134 | 16.7765 | 17.2928 | 17.6072 | 17.5719 | 16.5544 | 14.9018 | 16.8667 | 17.1982 | 17.4929 | 17.537 | 17.271 | 16.478 | 14.7101 | 6.3646 | 8.5786 | 5.7494 | 5.8522 | 5.8381 | 6.6315 | 7.609 | 15.9896 | 15.5913 | 15.4397 | 14.3552 | 14.2316 | 14.1742 |  |  |  | 10.7078 | 9.3279 | 8.9982 | 9.0571 | 0.12931 | -0.16051 | 12.7597 |  |  | 10.6639 |  |  | 16.8854 | 16.0833 | 15.0533 | 16.3866 | 15.6728 | 14.7723 | 10.3298 | 10.5284 | 11.1622 | 10.9978 | 9.2675 |  | 10.5782 | 9.1875 | 9.8768 | 9.2145 | 11.0314 | 12.0205 |  | 12.2285 |  |  | 11.7288 | 12.6259 | 12.6515 | [6 empty] | 12.5612 |  |  | 11.3217 |  |  | 9.2194 | 10.3346 | 11.8537 | 7.7434 | 9.0828 | 12.5313 | 7.9108 | 9.5172 | 12.2023 | 9.2281 | 10.4811 | 7.7564 | 10.2716 | 8.1356 | 10.1718 | 7.7692 | 9.6505 | 13.1183 | 10.5303 | 10.2125 | 11.4268 | 8.1228 | 9.824 | 12.6183 | 8.0547 | 10.2462 | 9.7706 | 9.8027 | 8.5722 | 10.1576 | -0.023317 | 20.954 | 0.03374 | 0.050606 | -37.8467 | 3.1205 | -0.22 | 0.34 | 0.4794 | -0.46936 | 0.24781 | 0.20696 | 0.16706 | -0.057489 | 0.90089 | 0.40385 | 0.38297 | 0.42027 | 0.37708 | 0.55893 | 0.42301 | 0.41397
42810.4367 | -287 | 18.6004 | 18.6605 | 18.6382 | 18.6389 | 17.9785 | 16.6151 | 14.6813 | 16.7248 | 17.2182 | 17.3169 | 17.3273 | 16.8656 | 15.9077 | 14.5197 | 15.0492 | 15.0323 | 15.585 | 13.4253 | 13.5431 | 14.1064 |  |  |  | 16.6247 | 15.9608 | 15.0674 | 10.2932 | 9.529 | 9.9953 | 17.2846 | 16.4193 | 15.2058 | 16.9286 | 16.2122 | 15.2118 | 10.7818 | 11.3038 |  | 12.1016 | 10.4688 | 10.231 | 8.8003 |  | 6.4755 | 6.4651 | 5.9865 | 6.1691 | 6.3509 | 6.7248 | 7.4384 | 4.8419 | 6.3923 | 4.99 | 6.624 | 8.1559 | 42.2703 | 46.6007 | 42.9165 | 15.128 |  |  | 0.10996 | -0.026197 | 0.10173 | -0.34696 | 0.13816 | -0.1286 | 0.62876 | -0.35172 | -0.51062 | 0.90407 | -0.32836 | 8.8712 | 8.8725 | 2.0088 | 15.92 | 16.7778 | 17.2947 | 17.6093 | 17.585 | 16.5595 | 14.9103 | 16.8762 | 17.2049 | 17.4961 | 17.5443 | 17.2824 | 16.4853 | 14.7121 | 6.4257 | 8.5403 | 5.7281 | 5.8866 | 5.8138 | 6.6351 | 7.6132 | 15.9891 | 15.5964 | 15.4455 | 14.3663 | 14.2426 | 14.1788 |  |  |  | 10.7039 | 9.3375 | 9.0052 | 9.048 | -0.022845 | 0.014893 | 12.7675 |  |  | 10.6568 |  |  | 16.8847 | 16.0849 | 15.062 | 16.3888 | 15.6721 | 14.7683 | 10.3219 | 10.5221 | 11.1589 | 11.0106 | 9.2601 |  | 10.5703 | 9.0731 | 9.8788 | 9.2046 | 11.0293 | 12.0177 |  | 12.2293 |  |  | 11.7516 | 12.6222 | 12.6736 | [6 empty] | 12.5443 |  |  | 11.3151 |  |  | 9.2303 | 10.3364 | 11.8741 | 7.7575 | 9.0873 | 12.5339 | 7.9257 | 9.5181 | 12.2197 | 9.2395 | 10.4906 | 7.7765 | 10.2794 | 8.1476 | 10.1836 | 7.7852 | 9.6723 | 13.126 | 10.5461 | 10.2189 | 11.437 | 8.1316 | 9.8298 | 12.635 | 8.0748 | 10.2649 | 9.7851 | 9.8043 | 8.5863 | 10.1568 | -0.062222 | 20.9532 | 0.033751 | 0.050693 | -37.8057 | 3.1205 | -10.34 | 0.34 | 0.38885 | -0.18861 | 0.37169 | -0.68641 | 0.43335 | -0.41808 | 0.92447 | 0.4038 | 0.38621 | 0.42047 | 0.37071 | 0.56178 | 0.42354 | 0.41409
42810.4367 | -286 | 18.6046 | 18.6698 | 18.6356 | 18.639 | 17.9809 | 16.6196 | 14.6974 | 16.7292 | 17.2176 | 17.3204 | 17.3305 | 16.8739 | 15.906 | 14.5257 | 15.0538 | 15.0394 | 15.5849 | 13.4332 | 13.5527 | 14.1106 |  |  |  | 16.6334 | 15.9685 | 15.0734 | 10.3048 | 9.5495 | 9.9774 | 17.2834 | 16.4185 | 15.2077 | 16.9314 | 16.2191 | 15.2223 | 10.782 | 11.2921 |  | 12.1085 | 10.4787 | 10.2388 | 8.7707 |  | 6.4769 | 6.4649 | 5.9913 | 6.1822 | 6.3949 | 6.787 | 7.4598 | 4.8445 | 6.393 | 4.9742 | 6.6351 | 8.1631 | 42.3135 | 46.624 | 42.9141 | 15.1658 |  |  | 0.27358 | 0.003375 | 0.089904 | -0.42253 | 0.05536 | -0.16342 | 0.53085 | -0.39312 | -0.54331 | -0.043391 | -0.24133 | 8.8685 | 8.8698 | 2.0083 | 15.9119 | 16.775 | 17.2933 | 17.612 | 17.5708 | 16.5558 | 14.9011 | 16.8702 | 17.2047 | 17.4878 | 17.5366 | 17.2786 | 16.4823 | 14.709 | 6.4513 | 8.5501 | 5.7558 | 5.9238 | 5.8038 | 6.6401 | 7.6071 | 15.9924 | 15.5911 | 15.4475 | 14.3611 | 14.2475 | 14.1804 |  |  |  | 10.7076 | 9.3413 | 9.0038 | 9.0358 | -0.0001538 | -0.0048684 | 12.7726 |  |  | 10.6657 |  |  | 16.8974 | 16.0865 | 15.0672 | 16.3887 | 15.6719 | 14.7727 | 10.3191 | 10.531 | 11.1629 | 11.0184 | 9.2323 |  | 10.5698 | 8.9834 | 9.8728 | 9.2065 | 11.0238 | 12.0119 |  | 12.239 |  |  | 11.7658 | 12.6268 | 12.6728 | [6 empty] | 12.5511 |  |  | 11.3145 |  |  | 9.2369 | 10.3326 | 11.8705 | 7.7692 | 9.083 | 12.5447 | 7.9277 | 9.5219 | 12.224 | 9.2294 | 10.48 | 7.7717 | 10.2887 | 8.1434 | 10.1811 | 7.7732 | 9.6647 | 13.1179 | 10.5374 | 10.2126 | 11.4441 | 8.0984 | 9.821 | 12.6132 | 8.0639 | 10.2531 | 9.7706 | 9.8068 | 8.5759 | 10.1512 | -0.043732 | 20.9539 | 0.033573 | 0.050136 | -38.0066 | 3.1205 | 18.33 | 0.31 | 0.61334 | 0.067699 | 0.34941 | -0.75748 | 0.27434 | -0.47136 | 0.84954 | 0.40455 | 0.38851 | 0.42024 | 0.36845 | 0.55799 | 0.42437 | 0.41456
42810.4367 | -285 | 18.6059 | 18.6603 | 18.6309 | 18.6412 | 17.9802 | 16.624 | 14.6924 | 16.7297 | 17.2164 | 17.3172 | 17.323 | 16.8763 | 15.9158 | 14.5187 | 15.0509 | 15.034 | 15.5798 | 13.4329 | 13.5379 | 14.11 |  |  |  | 16.632 | 15.9633 | 15.0725 | 10.2929 | 9.5375 | 9.9478 | 17.2862 | 16.4116 | 15.2111 | 16.9393 | 16.2152 | 15.2269 | 10.7818 | 11.2963 |  | 12.1154 | 10.4869 | 10.241 | 8.7532 |  | 6.4729 | 6.4603 | 5.9899 | 6.1826 | 6.4106 | 6.7932 | 7.4435 | 4.8373 | 6.4036 | 4.9242 | 6.6332 | 8.1502 | 42.3397 | 46.6126 | 42.9158 | 15.1856 |  |  | 0.035047 | -0.15236 | 0.02288 | 0.097254 | 0.20518 | -0.38093 | 0.44937 | -0.30112 | -0.064981 | 0.022905 | -0.18112 | 8.871 | 8.8719 | 2.0083 | 15.9081 | 16.768 | 17.286 | 17.6085 | 17.5598 | 16.5539 | 14.8982 | 16.8684 | 17.1975 | 17.4858 | 17.5306 | 17.2746 | 16.4775 | 14.7066 | 6.4915 | 8.5641 | 5.8101 | 5.9109 | 5.8181 | 6.642 | 7.6098 | 15.9956 | 15.5961 | 15.4456 | 14.3695 | 14.2524 | 14.1856 |  |  |  | 10.708 | 9.348 | 9.0029 | 9.0348 | 0.0118 | 0.004918 | 12.7611 |  |  | 10.6581 |  |  | 16.8952 | 16.0868 | 15.0598 | 16.3842 | 15.6726 | 14.7635 | 10.3198 | 10.5227 | 11.1628 | 11.0178 | 9.2191 |  | 10.5751 | 8.9212 | 9.8793 | 9.2003 | 11.0356 | 12.0109 |  | 12.2418 |  |  | 11.777 | 12.6139 | 12.6787 | [6 empty] | 12.561 |  |  | 11.307 |  |  | 9.2415 | 10.3346 | 11.8762 | 7.7723 | 9.0909 | 12.5438 | 7.9246 | 9.5333 | 12.2382 | 9.2386 | 10.4848 | 7.7891 | 10.2926 | 8.1618 | 10.1777 | 7.7836 | 9.6812 | 13.1335 | 10.5433 | 10.2216 | 11.451 | 8.0991 | 9.8158 | 12.6235 | 8.081 | 10.2679 | 9.7713 | 9.7952 | 8.5702 | 10.1637 | -0.015805 | 20.9537 | 0.033453 | 0.04989 | -37.8665 | 3.1205 | 5.59 | 0.38 | 0.21951 | -0.45486 | 0.17627 | 0.36341 | 0.52817 | -0.71965 | 0.78163 | 0.4051 | 0.39045 | 0.4208 | 0.36419 | 0.55228 | 0.42485 | 0.4146
42810.4367 | -284 | 18.5932 | 18.6599 | 18.6275 | 18.6309 | 17.9824 | 16.6284 | 14.6891 | 16.7308 | 17.2185 | 17.3126 | 17.3258 | 16.8749 | 15.9124 | 14.5203 | 15.0448 | 15.0357 | 15.5796 | 13.433 | 13.5351 | 14.1087 |  |  |  | 16.637 | 15.9705 | 15.0775 | 10.2883 | 9.538 | 9.9353 | 17.2865 | 16.4203 | 15.2092 | 16.9418 | 16.2215 | 15.2274 | 10.7881 | 11.3191 |  | 12.1154 | 10.4978 | 10.2488 | 8.7438 |  | 6.4602 | 6.4514 | 5.9695 | 6.1647 | 6.3955 | 6.7693 | 7.407 | 4.8597 | 6.3951 | 4.9267 | 6.6321 | 8.1489 | 42.3632 | 46.6088 | 42.9015 | 15.2065 |  |  | -0.037893 | 0.13151 | 0.046536 | 0.15968 | 0.18021 | -0.1562 | 0.24303 | -0.38063 | 0.37345 | -0.47327 | -0.18232 | 8.8695 | 8.8705 | 2.0085 | 15.9054 | 16.7634 | 17.2851 | 17.6029 | 17.5567 | 16.5477 | 14.8941 | 16.8664 | 17.1989 | 17.4854 | 17.5238 | 17.2719 | 16.477 | 14.7037 | 6.4849 | 8.5806 | 5.8587 | 5.9188 | 5.832 | 6.6429 | 7.608 | 15.9951 | 15.6012 | 15.4446 | 14.3664 | 14.2524 | 14.1886 |  |  |  | 10.7114 | 9.338 | 8.9969 | 9.0304 | 0.087167 | -0.060199 | 12.7784 |  |  | 10.6595 |  |  | 16.8911 | 16.0864 | 15.0656 | 16.3807 | 15.6731 | 14.7829 | 10.3037 | 10.5362 | 11.1634 | 11.0321 | 9.2181 |  | 10.5756 | 8.8624 | 9.8856 | 9.177 | 11.0333 | 12.0048 |  | 12.2361 |  |  | 11.7709 | 12.6081 | 12.6713 | [6 empty] | 12.5651 |  |  | 11.313 |  |  | 9.2318 | 10.3302 | 11.8635 | 7.7457 | 9.0898 | 12.5321 | 7.9245 | 9.533 | 12.2427 | 9.2369 | 10.476 | 7.7659 | 10.2878 | 8.1598 | 10.1736 | 7.7734 | 9.6772 | 13.1314 | 10.5411 | 10.2152 | 11.4463 | 8.0889 | 9.8156 | 12.6292 | 8.092 | 10.2726 | 9.7696 | 9.7921 | 8.5599 | 10.1656 | -0.090727 | 20.953 | 0.033499 | 0.049933 | -37.844 | 3.1204 | 7.77 | 0.33 | -0.22825 | 0.42259 | 0.25138 | 0.46565 | 0.49497 | -0.46081 | 0.5748 | 0.40514 | 0.39229 | 0.42137 | 0.36504 | 0.54666 | 0.42532 | 0.41483
42810.4368 | -283 | 18.5931 | 18.6524 | 18.6289 | 18.6345 | 17.9687 | 16.6229 | 14.679 | 16.7226 | 17.214 | 17.3049 | 17.3158 | 16.87 | 15.9084 | 14.5127 | 15.0481 | 15.0429 | 15.592 | 13.432 | 13.5382 | 14.115 |  |  |  | 16.6347 | 15.971 | 15.0798 | 10.2945 | 9.5484 | 9.9333 | 17.2811 | 16.4091 | 15.2012 | 16.9238 | 16.212 | 15.2077 | 10.7789 | 11.3269 |  | 12.1103 | 10.4936 | 10.2482 | 8.7268 |  | 6.469 | 6.4574 | 5.9704 | 6.1647 | 6.3865 | 6.7523 | 7.3756 | 4.8794 | 6.3979 | 4.9319 | 6.6351 | 8.1514 | 42.3657 | 46.6118 | 42.8966 | 15.2297 |  |  | 0.019275 | -0.13068 | -0.019176 | -0.13405 | -0.04452 | -0.30405 | 0.4198 | -0.32215 | -0.33878 | -0.6495 | -0.35777 | 8.8679 | 8.8689 | 2.0086 | 15.9037 | 16.7561 | 17.2918 | 17.6098 | 17.5649 | 16.5439 | 14.8929 | 16.8667 | 17.2011 | 17.4861 | 17.5323 | 17.2653 | 16.4742 | 14.7021 | 6.4987 | 8.577 | 5.8818 | 5.9428 | 5.8659 | 6.6476 | 7.605 | 15.9945 | 15.6005 | 15.4454 | 14.3715 | 14.2478 | 14.182 |  |  |  | 10.715 | 9.3427 | 9.007 | 9.0262 | -0.074305 | 0.073799 | 12.7671 |  |  | 10.6498 |  |  | 16.8855 | 16.0794 | 15.0559 | 16.3877 | 15.6614 | 14.7673 | 10.282 | 10.5285 | 11.1721 | 11.0265 | 9.2133 |  | 10.5799 | 8.7706 | 9.8857 | 9.157 | 11.0356 | 11.9852 |  | 12.2382 |  |  | 11.7696 | 12.6014 | 12.6806 | [6 empty] | 12.5666 |  |  | 11.3243 |  |  | 9.2364 | 10.3216 | 11.8671 | 7.7382 | 9.09 | 12.5313 | 7.9256 | 9.5245 | 12.2547 | 9.2412 | 10.4787 | 7.7586 | 10.2913 | 8.1601 | 10.1819 | 7.7892 | 9.6816 | 13.1389 | 10.5453 | 10.2182 | 11.4564 | 8.0998 | 9.8161 | 12.6384 | 8.0981 | 10.2849 | 9.773 | 9.798 | 8.5585 | 10.1674 | 0.031959 | 20.9533 | 0.03378 | 0.050795 | -37.86 | 3.1205 | 6.29 | 0.38 | 0.16279 | -0.42125 | -0.16137 | -0.42665 | -0.24601 | -0.6429 | 0.75543 | 0.40541 | 0.39485 | 0.422 | 0.36405 | 0.54375 | 0.42549 | 0.41507
42810.4368 | -282 | 18.5876 | 18.6537 | 18.6333 | 18.6347 | 17.976 | 16.6143 | 14.6835 | 16.7248 | 17.2143 | 17.3079 | 17.3188 | 16.8698 | 15.9056 | 14.5154 | 15.0339 | 15.0249 | 15.5803 | 13.4232 | 13.5312 | 14.1108 |  |  |  | 16.6299 | 15.963 | 15.0685 | 10.2877 | 9.5433 | 9.9363 | 17.2766 | 16.4103 | 15.2075 | 16.9366 | 16.2169 | 15.2167 | 10.7882 | 11.3662 |  | 12.1116 | 10.5127 | 10.2646 | 8.7404 |  | 6.4674 | 6.4536 | 5.962 | 6.1633 | 6.3734 | 6.7439 | 7.3509 | 4.9133 | 6.4054 | 4.937 | 6.6361 | 8.1529 | 42.3676 | 46.609 | 42.8866 | 15.2547 |  |  | 0.13822 | -0.13593 | 0.12802 | -0.40938 | -0.21406 | -0.48607 | 0.49011 | -0.25972 | 0.12865 | 0.28893 | -0.29955 | 8.871 | 8.872 | 2.0084 | 15.9111 | 16.7699 | 17.2954 | 17.6103 | 17.5727 | 16.5496 | 14.8955 | 16.8696 | 17.2007 | 17.4924 | 17.5401 | 17.277 | 16.4813 | 14.7093 | 6.4828 | 8.5746 | 5.8887 | 5.9383 | 5.8792 | 6.6445 | 7.599 | 15.9883 | 15.5959 | 15.449 | 14.3628 | 14.243 | 14.1803 |  |  |  | 10.7092 | 9.3316 | 9.0004 | 9.025 | -0.040876 | -0.07996 | 12.7728 |  |  | 10.6506 |  |  | 16.8821 | 16.0727 | 15.0652 | 16.3762 | 15.6721 | 14.7683 | 10.2854 | 10.53 | 11.1731 | 11.0461 | 9.2027 |  | 10.5731 | 8.7008 | 9.881 | 9.143 | 11.029 | 11.959 |  | 12.2378 |  |  | 11.7622 | 12.5814 | 12.664 | [6 empty] | 12.5563 |  |  | 11.3156 |  |  | 9.2459 | 10.3345 | 11.8818 | 7.7289 | 9.1035 | 12.5329 | 7.9454 | 9.5442 | 12.2839 | 9.247 | 10.4842 | 7.7601 | 10.3088 | 8.1774 | 10.1919 | 7.7864 | 9.6763 | 13.1345 | 10.5484 | 10.2185 | 11.4413 | 8.0934 | 9.8069 | 12.6376 | 8.1015 | 10.2788 | 9.7712 | 9.7901 | 8.5574 | 10.158 | -0.0017456 | 20.9537 | 0.033062 | 0.051417 | -37.9123 | 3.1204 | 3.87 | 0.29 | 0.43592 | -0.42964 | 0.41694 | -0.74559 | -0.53942 | -0.81285 | 0.81622 | 0.40548 | 0.39663 | 0.42218 | 0.36546 | 0.54229 | 0.42542 | 0.41491
42810.4368 | -281 | 18.5923 | 18.6584 | 18.6367 | 18.637 | 17.9743 | 16.6171 | 14.6837 | 16.7302 | 17.2202 | 17.314 | 17.317 | 16.8687 | 15.9094 | 14.5171 | 15.0373 | 15.0315 | 15.5857 | 13.4219 | 13.5365 | 14.1072 |  |  |  | 16.6275 | 15.9639 | 15.0683 | 10.2825 | 9.54 | 9.9208 | 17.2718 | 16.4057 | 15.2061 | 16.9301 | 16.211 | 15.2075 | 10.7844 | 11.3691 |  | 12.1009 | 10.5093 | 10.2626 | 8.7286 |  | 6.4629 | 6.4508 | 5.9701 | 6.1549 | 6.3652 | 6.7287 | 7.3272 | 4.9788 | 6.3953 | 4.9356 | 6.63 | 8.1494 | 42.3614 | 46.6059 | 42.889 | 15.2803 |  |  | 0.083671 | -0.034081 | -0.016548 | 0.07031 | -0.058976 | -0.047772 | 0.35606 | -0.2157 | -0.331 | -1.1996 | -0.22881 | 8.8698 | 8.8712 | 2.0086 | 15.9046 | 16.7681 | 17.2916 | 17.5998 | 17.5642 | 16.5434 | 14.8951 | 16.8694 | 17.1948 | 17.4888 | 17.5315 | 17.2683 | 16.4823 | 14.7041 | 6.4812 | 8.5532 | 5.8751 | 5.943 | 5.9197 | 6.6498 | 7.599 | 15.9845 | 15.5948 | 15.4456 | 14.3656 | 14.2444 | 14.1814 |  |  |  | 10.7069 | 9.3276 | 8.9978 | 9.006 | 0.04847 | -0.13266 | 12.7718 |  |  | 10.6594 |  |  | 16.8831 | 16.085 | 15.067 | 16.3832 | 15.6743 | 14.7805 | 10.2693 | 10.5223 | 11.1798 | 11.0487 | 9.2125 |  | 10.5718 | 8.6238 | 9.8792 | 9.1484 | 11.0285 | 11.943 |  | 12.2376 |  |  | 11.7423 | 12.5619 | 12.6606 | [6 empty] | 12.5722 |  |  | 11.2965 |  |  | 9.2417 | 10.3423 | 11.8829 | 7.7153 | 9.1093 | 12.5388 | 7.9583 | 9.5465 | 12.2949 | 9.2575 | 10.4848 | 7.7573 | 10.309 | 8.1905 | 10.1952 | 7.7864 | 9.6817 | 13.1343 | 10.5514 | 10.2327 | 11.446 | 8.0945 | 9.8131 | 12.6422 | 8.1172 | 10.2736 | 9.7714 | 9.781 | 8.5631 | 10.1645 | -0.10402 | 20.9535 | 0.033085 | 0.050773 | -37.9674 | 3.1204 | 17.94 | 0.28 | 0.33916 | -0.21513 | -0.1499 | 0.30899 | -0.28313 | -0.25482 | 0.69568 | 0.40517 | 0.39871 | 0.42201 | 0.36625 | 0.54379 | 0.42562 | 0.41536
42810.4368 | -280 | 18.5934 | 18.6676 | 18.6365 | 18.6375 | 17.9767 | 16.6172 | 14.6856 | 16.7286 | 17.2231 | 17.3128 | 17.3167 | 16.8718 | 15.9098 | 14.5185 | 15.0412 | 15.0333 | 15.5849 | 13.4298 | 13.5384 | 14.1092 |  |  |  | 16.6303 | 15.9664 | 15.0694 | 10.2816 | 9.5456 | 9.8937 | 17.2726 | 16.4011 | 15.2051 | 16.9253 | 16.2071 | 15.2067 | 10.7825 | 11.3868 |  | 12.1005 | 10.5142 | 10.2658 | 8.7273 |  | 6.4647 | 6.453 | 5.9734 | 6.1556 | 6.3635 | 6.7145 | 7.3034 | 5.0483 | 6.4032 | 4.9304 | 6.6387 | 8.1505 | 42.3684 | 46.5972 | 42.8747 | 15.2966 |  |  | 0.16515 | -0.27393 | -0.098688 | -0.12879 | -0.018892 | -0.29945 | 0.16286 | -0.39838 | -0.54195 | -0.46215 | -0.11357 | 8.8716 | 8.8728 | 2.0084 | 15.9011 | 16.7609 | 17.2921 | 17.607 | 17.5665 | 16.5415 | 14.898 | 16.8658 | 17.1974 | 17.4835 | 17.5375 | 17.2644 | 16.4793 | 14.7035 | 6.4701 | 8.5317 | 5.8214 | 5.9313 | 5.9704 | 6.646 | 7.59 | 15.9814 | 15.6009 | 15.4453 | 14.3632 | 14.2448 | 14.1801 |  |  |  | 10.7102 | 9.3256 | 8.9988 | 8.9784 | 0.14997 | 0.0043534 | 12.7738 |  |  | 10.6563 |  |  | 16.8816 | 16.0918 | 15.0574 | 16.3809 | 15.6638 | 14.7746 | 10.2528 | 10.5228 | 11.1768 | 11.0454 | 9.2255 |  | 10.5833 | 8.5336 | 9.8912 | 9.1483 | 11.0336 | 11.9395 |  | 12.2346 |  |  | 11.7257 | 12.5654 | 12.6643 | [6 empty] | 12.5728 |  |  | 11.2917 |  |  | 9.2376 | 10.3404 | 11.8717 | 7.7085 | 9.1082 | 12.5314 | 7.9513 | 9.5298 | 12.2934 | 9.252 | 10.4779 | 7.7459 | 10.3007 | 8.1891 | 10.1815 | 7.7834 | 9.6896 | 13.1341 | 10.5597 | 10.2355 | 11.4447 | 8.093 | 9.8123 | 12.6446 | 8.1212 | 10.2835 | 9.7712 | 9.7817 | 8.5629 | 10.171 | 0.14039 | 20.9538 | 0.033631 | 0.050845 | -37.9319 | 3.1205 | 13.78 | 0.3 | 0.47647 | -0.6099 | -0.36607 | -0.4182 | -0.16024 | -0.63797 | 0.47049 | 0.40519 | 0.40161 | 0.42218 | 0.36705 | 0.54872 | 0.42559 | 0.41623
42810.4368 | -279 | 18.5919 | 18.6636 | 18.6317 | 18.6369 | 17.9747 | 16.6204 | 14.6818 | 16.7264 | 17.2194 | 17.3103 | 17.3209 | 16.8667 | 15.9064 | 14.5126 | 15.0366 | 15.0211 | 15.5781 | 13.42 | 13.5355 | 14.1037 |  |  |  | 16.6252 | 15.966 | 15.0628 | 10.2771 | 9.5496 | 9.8618 | 17.2685 | 16.3945 | 15.1968 | 16.9266 | 16.2056 | 15.2037 | 10.7722 | 11.4307 |  | 12.0981 | 10.5164 | 10.2609 | 8.7212 |  | 6.4645 | 6.4542 | 5.9602 | 6.1428 | 6.3478 | 6.7058 | 7.2939 | 5.0955 | 6.4129 | 4.9399 | 6.6446 | 8.1417 | 42.3771 | 46.5887 | 42.8743 | 15.3088 |  |  | -0.002409 | 0.017831 | 0.043904 | 0.37259 | 0.12042 | -0.3599 | 0.29495 | -0.33595 | -0.69062 | -0.476 | -0.22682 | 8.8702 | 8.8715 | 2.0084 | 15.8971 | 16.759 | 17.2888 | 17.5965 | 17.559 | 16.5392 | 14.8928 | 16.8654 | 17.1952 | 17.4859 | 17.5272 | 17.2687 | 16.4721 | 14.6964 | 6.4931 | 8.5346 | 5.8398 | 5.9426 | 6.0149 | 6.6437 | 7.5903 | 15.9845 | 15.5982 | 15.44 | 14.3593 | 14.2391 | 14.1819 |  |  |  | 10.7091 | 9.3223 | 8.9983 | 8.9676 | 0.036517 | 0.008682 | 12.7687 |  |  | 10.6504 |  |  | 16.884 | 16.0748 | 15.059 | 16.3773 | 15.6649 | 14.7639 | 10.2467 | 10.5234 | 11.197 | 11.0594 | 9.2388 |  | 10.5829 | 8.4266 | 9.8979 | 9.1613 | 11.0268 | 11.9539 |  | 12.2399 |  |  | 11.7409 | 12.5739 | 12.6555 | [6 empty] | 12.5639 |  |  | 11.2919 |  |  | 9.2392 | 10.3442 | 11.8704 | 7.7256 | 9.1166 | 12.527 | 7.9486 | 9.5224 | 12.3057 | 9.2596 | 10.4784 | 7.7557 | 10.3083 | 8.1975 | 10.1805 | 7.7729 | 9.6935 | 13.1304 | 10.5589 | 10.2332 | 11.4399 | 8.0828 | 9.811 | 12.6493 | 8.1126 | 10.2807 | 9.7777 | 9.767 | 8.5657 | 10.1717 | 0.085887 | 20.9534 | 0.03359 | 0.051156 | -37.8371 | 3.1205 | -4.99 | 0.36 | -0.057542 | 0.15561 | 0.24417 | 0.7113 | 0.40455 | -0.6994 | 0.63315 | 0.4048 | 0.40481 | 0.4216 | 0.36422 | 0.54672 | 0.42542 | 0.4165
42810.4368 | -278 | 18.583 | 18.6432 | 18.6269 | 18.6296 | 17.9638 | 16.6109 | 14.6763 | 16.7204 | 17.2059 | 17.3087 | 17.3106 | 16.8632 | 15.9039 | 14.5088 | 15.034 | 15.0189 | 15.5781 | 13.4201 | 13.5316 | 14.105 |  |  |  | 16.6255 | 15.9626 | 15.0649 | 10.271 | 9.5513 | 9.8362 | 17.2644 | 16.3976 | 15.1993 | 16.9265 | 16.206 | 15.2001 | 10.7775 | 11.4776 |  | 12.1058 | 10.5236 | 10.265 | 8.706 |  | 6.4534 | 6.4537 | 5.9543 | 6.1261 | 6.3312 | 6.6771 | 7.2489 | 5.0046 | 6.4003 | 4.9452 | 6.6385 | 8.1405 | 42.3923 | 46.5818 | 42.8725 | 15.3159 |  |  | 0.18684 | 0.15648 | 0.023536 | -0.082138 | -0.04452 | -0.079972 | 0.39023 | -0.14473 | -0.77391 | -0.4353 | -0.23537 | 8.8685 | 8.8699 | 2.0086 | 15.8979 | 16.761 | 17.2912 | 17.5986 | 17.5619 | 16.5419 | 14.8907 | 16.8582 | 17.1987 | 17.4885 | 17.5268 | 17.2649 | 16.4701 | 14.6993 | 6.4832 | 8.558 | 5.8596 | 5.9624 | 6.0782 | 6.6515 | 7.5954 | 15.9992 | 15.6005 | 15.4473 | 14.3704 | 14.2566 | 14.1808 |  |  |  | 10.7146 | 9.3215 | 9.0064 | 8.9632 | -0.099023 | -0.053989 | 12.7738 |  |  | 10.6534 |  |  | 16.889 | 16.0848 | 15.0679 | 16.3929 | 15.6722 | 14.7685 | 10.2429 | 10.5378 | 11.201 | 11.0798 | 9.2019 |  | 10.5754 | 8.3301 | 9.8929 | 9.1736 | 11.0249 | 11.956 |  | 12.2326 |  |  | 11.7382 | 12.5875 | 12.6376 | [6 empty] | 12.5665 |  |  | 11.2826 |  |  | 9.2396 | 10.3437 | 11.8713 | 7.7189 | 9.1218 | 12.5239 | 7.9434 | 9.5179 | 12.3059 | 9.2655 | 10.4777 | 7.7577 | 10.2923 | 8.1945 | 10.18 | 7.7834 | 9.7034 | 13.1428 | 10.561 | 10.2412 | 11.4508 | 8.0777 | 9.8165 | 12.6557 | 8.1113 | 10.2797 | 9.7869 | 9.7614 | 8.5724 | 10.1719 | -0.002516 | 20.9537 | 0.03281 | 0.052003 | -37.8888 | 3.1204 | 3.7 | 0.31 | 0.50674 | 0.46097 | 0.17877 | -0.33397 | -0.24597 | -0.32967 | 0.72823 | 0.40559 | 0.40732 | 0.42119 | 0.36622 | 0.54509 | 0.42602 | 0.4168
42810.4368 | -277 | 18.577 | 18.6541 | 18.6195 | 18.6278 | 17.9712 | 16.6122 | 14.6726 | 16.721 | 17.2112 | 17.3046 | 17.3129 | 16.8607 | 15.9007 | 14.5022 | 15.0217 | 15.0201 | 15.5701 | 13.4151 | 13.5225 | 14.0974 |  |  |  | 16.6203 | 15.9588 | 15.0644 | 10.2578 | 9.5444 | 9.8118 | 17.2559 | 16.3933 | 15.1938 | 16.9222 | 16.2092 | 15.1928 | 10.7774 | 11.5296 |  | 12.0927 | 10.5201 | 10.2631 | 8.6968 |  | 6.4507 | 6.4487 | 5.9569 | 6.1372 | 6.3285 | 6.6655 | 7.2145 | 4.9764 | 6.4048 | 4.9469 | 6.634 | 8.1432 | 42.4055 | 46.5679 | 42.8727 | 15.3267 |  |  | 0.033075 | -0.20493 | -0.095404 | -0.13734 | -0.1536 | -0.193 | 0.54334 | -0.14144 | -0.56432 | -0.21962 | -0.43963 | 8.8694 | 8.8704 | 2.0083 | 15.8953 | 16.7645 | 17.2928 | 17.6047 | 17.5671 | 16.5391 | 14.8998 | 16.8614 | 17.1967 | 17.4857 | 17.5254 | 17.2615 | 16.4715 | 14.6992 | 6.4243 | 8.5442 | 5.8627 | 6.007 | 6.2774 | 6.6449 | 7.5917 | 15.9874 | 15.5975 | 15.4441 | 14.3651 | 14.25 | 14.1768 |  |  |  | 10.7122 | 9.3235 | 9.0006 | 8.9545 | 0.091219 | -0.046461 | 12.7727 |  |  | 10.6399 |  |  | 16.8803 | 16.0789 | 15.0618 | 16.3824 | 15.6781 | 14.7762 | 10.2389 | 10.5376 | 11.2021 | 11.0778 | 9.2127 |  | 10.5684 | 8.2193 | 9.8944 | 9.1832 | 11.0258 | 11.977 |  | 12.2288 |  |  | 11.7285 | 12.595 | 12.6213 | [6 empty] | 12.5751 |  |  | 11.2722 |  |  | 9.2418 | 10.3513 | 11.8666 | 7.6878 | 9.1182 | 12.5143 | 7.9287 | 9.5122 | 12.3055 | 9.2614 | 10.4742 | 7.7465 | 10.2674 | 8.1934 | 10.1757 | 7.7957 | 9.7062 | 13.1451 | 10.5573 | 10.2474 | 11.4422 | 8.0693 | 9.8155 | 12.6579 | 8.121 | 10.2776 | 9.7885 | 9.7534 | 8.5685 | 10.1697 | 0.14502 | 20.9532 | 0.032971 | 0.05154 | -38.0616 | 3.1204 | -8.67 | 0.23 | 0.2132 | -0.52752 | -0.35993 | -0.43185 | -0.45688 | -0.51213 | 0.85928 | 0.40505 | 0.41045 | 0.42095 | 0.372 | 0.54433 | 0.42628 | 0.41697
42810.4368 | -276 | 18.5864 | 18.6507 | 18.617 | 18.6301 | 17.9735 | 16.6144 | 14.678 | 16.726 | 17.2117 | 17.3065 | 17.3183 | 16.8571 | 15.9046 | 14.5046 | 15.019 | 15.0251 | 15.5761 | 13.42 | 13.5277 | 14.1051 |  |  |  | 16.6301 | 15.9524 | 15.0688 | 10.2581 | 9.5434 | 9.8337 | 17.271 | 16.4022 | 15.2051 | 16.9306 | 16.2147 | 15.2091 | 10.7781 | 11.5969 |  | 12.1029 | 10.5421 | 10.2681 | 8.7036 |  | 6.4608 | 6.4527 | 5.9635 | 6.1441 | 6.3266 | 6.6534 | 7.1982 | 5.0083 | 6.4141 | 4.9352 | 6.6309 | 8.141 | 42.4134 | 46.5532 | 42.8658 | 15.3278 |  |  | -0.051693 | -0.23845 | 0.057704 | -0.080826 | -0.17134 | 0.14739 | 0.45528 | -0.23278 | -0.37984 | -0.77874 | -0.21828 | 8.8693 | 8.8707 | 2.0084 | 15.8957 | 16.7624 | 17.2855 | 17.6034 | 17.5696 | 16.5416 | 14.8992 | 16.8579 | 17.1966 | 17.4857 | 17.5295 | 17.2666 | 16.4716 | 14.701 | 6.3966 | 8.5212 | 5.8111 | 6.0416 | 6.468 | 6.6568 | 7.5885 | 15.9805 | 15.598 | 15.4404 | 14.3593 | 14.2458 | 14.1752 |  |  |  | 10.7089 | 9.3175 | 8.9967 | 8.9445 | 0.21865 | -0.013714 | 12.7738 |  |  | 10.6373 |  |  | 16.889 | 16.0804 | 15.0587 | 16.3805 | 15.6785 | 14.7741 | 10.216 | 10.5423 | 11.2007 | 11.0937 | 9.209 |  | 10.5809 | 8.1367 | 9.8902 | 9.1926 | 11.0323 | 11.9938 |  | 12.2386 |  |  | 11.7354 | 12.5826 | 12.624 | [6 empty] | 12.5835 |  |  | 11.2659 |  |  | 9.2526 | 10.356 | 11.8661 | 7.6684 | 9.1031 | 12.5104 | 7.9182 | 9.5095 | 12.3185 | 9.2601 | 10.4773 | 7.7221 | 10.2577 | 8.1989 | 10.182 | 7.7962 | 9.7119 | 13.1531 | 10.5604 | 10.2469 | 11.4228 | 8.0697 | 9.8203 | 12.6544 | 8.1256 | 10.2766 | 9.7951 | 9.7478 | 8.56 | 10.1732 | -0.010605 | 20.9532 | 0.03312 | 0.050505 | -38.0189 | 3.1205 | -3.24 | 0.28 | -0.26654 | -0.56903 | 0.27992 | -0.33129 | -0.48253 | 0.44754 | 0.78657 | 0.40557 | 0.4126 | 0.42091 | 0.37646 | 0.54969 | 0.42611 | 0.41713
42810.4369 | -275 | 18.5869 | 18.6516 | 18.6296 | 18.6318 | 17.9699 | 16.6148 | 14.6849 | 16.7241 | 17.2119 | 17.3065 | 17.3196 | 16.8678 | 15.9081 | 14.51 | 15.0151 | 15.0165 | 15.5691 | 13.4115 | 13.5316 | 14.1019 |  |  |  | 16.6206 | 15.9557 | 15.0629 | 10.2584 | 9.5359 | 9.8582 | 17.2629 | 16.399 | 15.1984 | 16.9263 | 16.2071 | 15.2081 | 10.7774 | 11.6355 |  | 12.1049 | 10.54 | 10.2651 | 8.7044 |  | 6.4678 | 6.4569 | 5.9586 | 6.1295 | 6.3183 | 6.6386 | 7.1672 | 5.0227 | 6.4107 | 4.9423 | 6.6371 | 8.1458 | 42.4189 | 46.539 | 42.8652 | 15.3261 |  |  | -0.041181 | -0.089937 | 0.03142 | 0.040086 | -0.08132 | -0.13057 | 0.40271 | -0.2157 | -0.25666 | -0.34403 | -0.35121 | 8.8679 | 8.869 | 2.0085 | 15.905 | 16.7654 | 17.2947 | 17.6044 | 17.5687 | 16.5473 | 14.9015 | 16.8622 | 17.2023 | 17.4954 | 17.5357 | 17.2712 | 16.4817 | 14.7066 | 6.3853 | 8.5224 | 5.8179 | 6.048 | 6.5143 | 6.6437 | 7.5892 | 15.9724 | 15.5875 | 15.4347 | 14.351 | 14.238 | 14.1679 |  |  |  | 10.7033 | 9.3006 | 8.9937 | 8.9505 | 0.15463 | -0.047213 | 12.7729 |  |  | 10.6332 |  |  | 16.8863 | 16.0819 | 15.0603 | 16.3812 | 15.6686 | 14.7705 | 10.1985 | 10.5412 | 11.2029 | 11.089 | 9.2339 |  | 10.5855 | 8.0607 | 9.887 | 9.2006 | 11.0309 | 12.0105 |  | 12.2351 |  |  | 11.7409 | 12.5762 | 12.6216 | [6 empty] | 12.5901 |  |  | 11.2757 |  |  | 9.2561 | 10.3504 | 11.8643 | 7.6508 | 9.0805 | 12.5074 | 7.9112 | 9.5108 | 12.321 | 9.2589 | 10.4728 | 7.688 | 10.2496 | 8.1988 | 10.1704 | 7.7864 | 9.7076 | 13.1497 | 10.5551 | 10.2447 | 11.43 | 8.0657 | 9.8112 | 12.6453 | 8.1317 | 10.2747 | 9.7869 | 9.7339 | 8.5638 | 10.1667 | -0.019657 | 20.9528 | 0.03308 | 0.050679 | -38.045 | 3.1204 | 9.79 | 0.29 | -0.23791 | -0.34947 | 0.20656 | 0.23331 | -0.33242 | -0.42121 | 0.73974 | 0.40503 | 0.41461 | 0.42064 | 0.3762 | 0.54902 | 0.42606 | 0.41678
42810.4369 | -274 | 18.5748 | 18.651 | 18.625 | 18.6288 | 17.9661 | 16.6153 | 14.6812 | 16.7261 | 17.2091 | 17.3059 | 17.3161 | 16.8649 | 15.8959 | 14.5115 | 15.0164 | 15.0106 | 15.5637 | 13.4138 | 13.529 | 14.0995 |  |  |  | 16.6167 | 15.9584 | 15.0637 | 10.2608 | 9.5427 | 9.8589 | 17.2604 | 16.3963 | 15.1961 | 16.9249 | 16.2018 | 15.2057 | 10.7846 | 11.6606 |  | 12.1015 | 10.5368 | 10.2659 | 8.7123 |  | 6.4712 | 6.4575 | 5.9696 | 6.143 | 6.3261 | 6.6363 | 7.1608 | 5.0401 | 6.4156 | 4.9768 | 6.6466 | 8.1341 | 42.4232 | 46.5203 | 42.8608 | 15.3251 |  |  | 0.13033 | -0.23582 | 0.061648 | 0.16822 | -0.13454 | -0.0688 | 0.55911 | -0.027104 | -0.29519 | -0.20179 | -0.39771 | 8.8671 | 8.8683 | 2.0083 | 15.894 | 16.7626 | 17.297 | 17.5968 | 17.5664 | 16.5412 | 14.8891 | 16.8608 | 17.1982 | 17.4881 | 17.5318 | 17.2588 | 16.4748 | 14.7022 | 6.3908 | 8.5373 | 5.9624 | 6.0435 | 6.5339 | 6.6468 | 7.594 | 15.9701 | 15.5946 | 15.4314 | 14.3571 | 14.2371 | 14.1735 |  |  |  | 10.7093 | 9.303 | 9.0081 | 8.9634 | 0.20873 | 0.004918 | 12.7806 |  |  | 10.6329 |  |  | 16.8956 | 16.0798 | 15.0594 | 16.3837 | 15.6689 | 14.7791 | 10.1907 | 10.5488 | 11.2128 | 11.0999 | 9.258 |  | 10.5845 | 7.9868 | 9.8964 | 9.2048 | 11.035 | 12.0239 |  | 12.2411 |  |  | 11.751 | 12.5689 | 12.6361 | [6 empty] | 12.5959 |  |  | 11.2873 |  |  | 9.2476 | 10.345 | 11.8633 | 7.6348 | 9.0694 | 12.4978 | 7.8963 | 9.5179 | 12.3295 | 9.2652 | 10.4667 | 7.6772 | 10.2518 | 8.1924 | 10.1783 | 7.7986 | 9.7173 | 13.1627 | 10.5613 | 10.2627 | 11.4282 | 8.076 | 9.816 | 12.6477 | 8.1379 | 10.2816 | 9.7933 | 9.7385 | 8.5801 | 10.175 | -0.13271 | 20.9541 | 0.032758 | 0.049868 | -38.0196 | 3.1205 | 17.94 | 0.34 | 0.42324 | -0.56589 | 0.28933 | 0.47795 | -0.42758 | -0.30576 | 0.87162 | 0.40433 | 0.41697 | 0.42066 | 0.37595 | 0.53353 | 0.42608 | 0.41662
42810.4369 | -273 | 18.5707 | 18.6472 | 18.621 | 18.6302 | 17.9677 | 16.6181 | 14.6764 | 16.7271 | 17.2096 | 17.3044 | 17.3144 | 16.8649 | 15.8952 | 14.5111 | 15.0089 | 15.0052 | 15.5532 | 13.416 | 13.5185 | 14.0865 |  |  |  | 16.608 | 15.9521 | 15.0594 | 10.2553 | 9.5262 | 9.8419 | 17.253 | 16.3949 | 15.1901 | 16.919 | 16.2059 | 15.2058 | 10.7809 | 11.661 |  | 12.0947 | 10.5335 | 10.2715 | 8.6984 |  | 6.4502 | 6.4503 | 5.9557 | 6.1262 | 6.3099 | 6.621 | 7.1556 | 5.0497 | 6.4118 | 4.9113 | 6.6292 | 8.1342 | 42.4337 | 46.5132 | 42.8665 | 15.3151 |  |  | 0.14413 | -0.084021 | 0.062304 | 0.090682 | 0.030392 | 0.15528 | 0.87715 | -0.098732 | -0.48357 | -0.2597 | -0.35836 | 8.8717 | 8.8725 | 2.0085 | 15.8862 | 16.7524 | 17.2788 | 17.5934 | 17.5604 | 16.5393 | 14.8973 | 16.8575 | 17.1855 | 17.477 | 17.5258 | 17.2705 | 16.4629 | 14.6989 | 6.4016 | 8.5266 | 5.9757 | 6.0302 | 6.4911 | 6.6556 | 7.5918 | 15.9722 | 15.587 | 15.4304 | 14.3569 | 14.241 | 14.1756 |  |  |  | 10.7025 | 9.3058 | 9.0052 | 8.9657 | 0.078455 | -0.081842 | 12.7821 |  |  | 10.6474 |  |  | 16.8895 | 16.089 | 15.063 | 16.3845 | 15.673 | 14.7773 | 10.1921 | 10.5605 | 11.2276 | 11.1096 | 9.2397 |  | 10.5703 | 7.8182 | 9.8853 | 9.2096 | 11.0346 | 12.0141 |  | 12.2295 |  |  | 11.7536 | 12.5529 | 12.6256 | [6 empty] | 12.5822 |  |  | 11.2744 |  |  | 9.2383 | 10.3428 | 11.8569 | 7.6215 | 9.0688 | 12.4742 | 7.8776 | 9.5076 | 12.3159 | 9.2509 | 10.4619 | 7.6713 | 10.2468 | 8.1913 | 10.1681 | 7.8048 | 9.7134 | 13.1624 | 10.5579 | 10.2519 | 11.4148 | 8.0723 | 9.8125 | 12.643 | 8.1283 | 10.2913 | 9.7903 | 9.7344 | 8.5798 | 10.1771 | -0.0628 | 20.953 | 0.0332 | 0.050787 | -38.0145 | 3.1204 | 15.04 | 0.3 | 0.44507 | -0.33778 | 0.29087 | 0.35091 | 0.20321 | 0.45933 | 1.0917 | 0.40437 | 0.42129 | 0.42051 | 0.37577 | 0.53178 | 0.42634 | 0.41633
42810.4369 | -272 | 18.5707 | 18.6526 | 18.6268 | 18.6289 | 17.9709 | 16.6191 | 14.6768 | 16.7232 | 17.2151 | 17.3062 | 17.3166 | 16.8619 | 15.8958 | 14.5089 | 15.0166 | 15.0171 | 15.567 | 13.4103 | 13.536 | 14.0991 |  |  |  | 16.6202 | 15.9583 | 15.0555 | 10.2582 | 9.5293 | 9.8461 | 17.2507 | 16.3893 | 15.1863 | 16.9197 | 16.2 | 15.2013 | 10.7797 | 11.6625 |  | 12.0903 | 10.5252 | 10.2708 | 8.6784 |  | 6.451 | 6.4536 | 5.9696 | 6.1449 | 6.3153 | 6.6317 | 7.1698 | 5.1054 | 6.4142 | 4.904 | 6.6333 | 8.1348 | 42.4501 | 46.5246 | 42.8732 | 15.3167 |  |  | 0.1553 | 0.044115 | 0.010392 | -0.33119 | 0.14999 | -0.2817 | 0.65439 | -0.31886 | -0.42538 | -1.4692 | -0.26021 | 8.8691 | 8.8702 | 2.0086 | 15.8875 | 16.7585 | 17.2817 | 17.5945 | 17.5596 | 16.5381 | 14.8899 | 16.8601 | 17.1954 | 17.488 | 17.5249 | 17.2732 | 16.4604 | 14.7017 | 6.4026 | 8.524 | 6.0445 | 6.0323 | 6.4702 | 6.6606 | 7.5851 | 15.9681 | 15.5915 | 15.4281 | 14.3522 | 14.2412 | 14.1768 |  |  |  | 10.7079 | 9.297 | 9.0087 | 8.985 | 0.084533 | -0.0031746 | 12.7733 |  |  | 10.6417 |  |  | 16.892 | 16.0935 | 15.0689 | 16.3889 | 15.6719 | 14.7891 | 10.1907 | 10.5663 | 11.2247 | 11.1121 | 9.2017 |  | 10.5662 | 7.6536 | 9.8874 | 9.2208 | 11.0267 | 12.0002 |  | 12.2255 |  |  | 11.7623 | 12.5647 | 12.6194 | [6 empty] | 12.58 |  |  | 11.2746 |  |  | 9.2493 | 10.3347 | 11.8601 | 7.608 | 9.0602 | 12.4765 | 7.8763 | 9.5166 | 12.3201 | 9.263 | 10.4693 | 7.6783 | 10.2384 | 8.2001 | 10.1737 | 7.8043 | 9.7203 | 13.1731 | 10.5647 | 10.2664 | 11.4172 | 8.0799 | 9.8164 | 12.6418 | 8.1403 | 10.296 | 9.7916 | 9.7407 | 8.5943 | 10.1825 | -0.0081014 | 20.9536 | 0.033918 | 0.051251 | -37.9296 | 3.1205 | 5.76 | 0.39 | 0.462 | 0.24475 | 0.11879 | -0.67062 | 0.45145 | -0.61869 | 0.94296 | 0.40528 | 0.42593 | 0.41994 | 0.37623 | 0.52336 | 0.42686 | 0.41597
42810.4369 | -271 | 18.5663 | 18.6466 | 18.6257 | 18.6244 | 17.9711 | 16.6138 | 14.677 | 16.7266 | 17.2113 | 17.3108 | 17.31 | 16.863 | 15.9039 | 14.5094 | 15.0186 | 15.0186 | 15.5728 | 13.4151 | 13.5303 | 14.0891 |  |  |  | 16.6231 | 15.9585 | 15.0625 | 10.2516 | 9.5368 | 9.8728 | 17.257 | 16.3889 | 15.1869 | 16.9168 | 16.207 | 15.2048 | 10.7807 | 11.6735 |  | 12.0982 | 10.525 | 10.2676 | 8.6632 |  | 6.4626 | 6.4469 | 5.9748 | 6.1481 | 6.3153 | 6.6221 | 7.1874 | 5.1598 | 6.4195 | 4.9069 | 6.6443 | 8.1337 | 42.4581 | 46.5256 | 42.8822 | 15.3225 |  |  | 0.097471 | -0.41849 | -0.006692 | 0.001314 | -0.23443 | 0.23676 | 0.31203 | -0.22293 | -0.24323 | -0.96882 | -0.27531 | 8.8686 | 8.8696 | 2.0081 | 15.8882 | 16.7606 | 17.2802 | 17.6031 | 17.5622 | 16.5394 | 14.8922 | 16.8537 | 17.1948 | 17.4875 | 17.5226 | 17.2724 | 16.4683 | 14.7029 | 6.3802 | 8.5465 | 6.1681 | 5.9824 | 6.4485 | 6.6477 | 7.5815 | 15.9652 | 15.5901 | 15.4298 | 14.3531 | 14.2338 | 14.1739 |  |  |  | 10.7053 | 9.3035 | 9.0061 | 9.0074 | -0.023655 | 0.10918 | 12.7791 |  |  | 10.6477 |  |  | 16.8924 | 16.0886 | 15.0583 | 16.3889 | 15.6691 | 14.7784 | 10.1818 | 10.5691 | 11.2268 | 11.1247 | 9.157 |  | 10.5778 | 7.5403 | 9.9007 | 9.2367 | 11.0336 | 11.9934 |  | 12.2233 |  |  | 11.7481 | 12.5599 | 12.6216 | [6 empty] | 12.5783 |  |  | 11.2758 |  |  | 9.2443 | 10.3377 | 11.8526 | 7.5734 | 9.0393 | 12.4587 | 7.8545 | 9.508 | 12.3107 | 9.261 | 10.47 | 7.6694 | 10.2374 | 8.192 | 10.1635 | 7.8028 | 9.7195 | 13.1618 | 10.5636 | 10.256 | 11.4015 | 8.0789 | 9.8094 | 12.6419 | 8.1311 | 10.29 | 9.7826 | 9.743 | 8.591 | 10.1785 | 0.094747 | 20.953 | 0.034469 | 0.050527 | -37.9023 | 3.1205 | -0.8 | 0.23 | 0.36603 | -0.75384 | -0.095326 | 0.042241 | -0.56438 | 0.56718 | 0.65113 | 0.40691 | 0.42951 | 0.41972 | 0.37722 | 0.50921 | 0.42731 | 0.41527
42810.4369 | -270 | 18.5683 | 18.648 | 18.6279 | 18.6292 | 17.9775 | 16.6204 | 14.6857 | 16.73 | 17.2208 | 17.3211 | 17.3185 | 16.8675 | 15.9031 | 14.5113 | 15.0085 | 15.015 | 15.5652 | 13.4181 | 13.5304 | 14.0988 |  |  |  | 16.6126 | 15.9548 | 15.0681 | 10.2574 | 9.5279 | 9.8777 | 17.2552 | 16.4003 | 15.1955 | 16.923 | 16.2086 | 15.1957 | 10.7819 | 11.6878 |  | 12.1127 | 10.5231 | 10.2855 | 8.6611 |  | 6.4544 | 6.4456 | 5.9651 | 6.1478 | 6.3106 | 6.6464 | 7.2251 | 5.2342 | 6.4213 | 4.9058 | 6.6459 | 8.1214 | 42.4606 | 46.5127 | 42.8805 | 15.3279 |  |  | 0.13295 | -0.18128 | 0.11028 | 0.037454 | 0.008048 | 0.087592 | -0.087496 | -0.33989 | -0.78948 | -0.032482 | -0.46308 | 8.8713 | 8.8725 | 2.0086 | 15.8811 | 16.7528 | 17.2776 | 17.5998 | 17.5613 | 16.538 | 14.8904 | 16.861 | 17.1915 | 17.4847 | 17.5239 | 17.268 | 16.4693 | 14.7 | 6.3801 | 8.538 | 6.2661 | 5.9558 | 6.4349 | 6.652 | 7.5881 | 15.9715 | 15.5808 | 15.4343 | 14.3526 | 14.2392 | 14.1761 |  |  |  | 10.7031 | 9.3002 | 9.011 | 9.0328 | 0.099931 | -0.12343 | 12.7721 |  |  | 10.6535 |  |  | 16.8848 | 16.0857 | 15.0661 | 16.3923 | 15.668 | 14.7741 | 10.1638 | 10.5814 | 11.2419 | 11.1421 | 9.1163 |  | 10.5707 | 7.5105 | 9.8887 | 9.2361 | 11.0281 | 12.001 |  | 12.2273 |  |  | 11.7488 | 12.5489 | 12.6264 | [6 empty] | 12.5733 |  |  | 11.2496 |  |  | 9.2389 | 10.3324 | 11.8429 | 7.5658 | 9.0362 | 12.4546 | 7.8504 | 9.4967 | 12.3064 | 9.2519 | 10.4566 | 7.6655 | 10.2313 | 8.1909 | 10.1626 | 7.8108 | 9.7149 | 13.1609 | 10.5503 | 10.2661 | 11.3924 | 8.0773 | 9.808 | 12.6383 | 8.1371 | 10.2899 | 9.7883 | 9.7452 | 8.5868 | 10.1815 | 0.0026842 | 20.9533 | 0.03421 | 0.050085 | -37.9094 | 3.1204 | -5.5 | 0.33 | 0.4275 | -0.49614 | 0.38697 | 0.22552 | 0.10458 | 0.345 | -0.34481 | 0.40781 | 0.42995 | 0.41956 | 0.37773 | 0.49909 | 0.42741 | 0.41449
42810.4369 | -269 | 18.5662 | 18.6453 | 18.625 | 18.6247 | 17.9666 | 16.6115 | 14.6766 | 16.7216 | 17.217 | 17.3039 | 17.3182 | 16.8677 | 15.8957 | 14.5162 | 15.0145 | 15.0222 | 15.5692 | 13.4236 | 13.5368 | 14.1037 |  |  |  | 16.6275 | 15.9571 | 15.0621 | 10.2603 | 9.5406 | 9.8566 | 17.2563 | 16.3825 | 15.1852 | 16.9164 | 16.2011 | 15.2028 | 10.7815 | 11.7176 |  | 12.0966 | 10.5111 | 10.277 | 8.6438 |  | 6.4508 | 6.4399 | 5.962 | 6.1383 | 6.3135 | 6.6574 | 7.2037 | 5.2669 | 6.4159 | 4.911 | 6.6412 | 8.1299 | 42.461 | 46.499 | 42.8698 | 15.3359 |  |  | 0.006135 | -0.17996 | 0.18978 | -0.093966 | 0.29784 | -0.39604 | 0.30086 | -0.35961 | -0.27009 | -0.1892 | -0.23398 | 8.8679 | 8.8694 | 2.0085 | 15.8791 | 16.7583 | 17.2808 | 17.5983 | 17.5607 | 16.5428 | 14.8916 | 16.8597 | 17.1962 | 17.4903 | 17.5262 | 17.2639 | 16.4696 | 14.6914 | 6.4032 | 8.5265 | 6.3017 | 5.9 | 6.3989 | 6.6498 | 7.5843 | 15.9601 | 15.5787 | 15.4304 | 14.3548 | 14.2402 | 14.1761 |  |  |  | 10.6989 | 9.299 | 9.0211 | 9.0746 | 0.25411 | 0.11351 | 12.7656 |  |  | 10.6388 |  |  | 16.8816 | 16.076 | 15.0598 | 16.3833 | 15.6596 | 14.7702 | 10.1542 | 10.5624 | 11.2466 | 11.1483 | 9.1089 |  | 10.5706 | 7.5716 | 9.8814 | 9.2458 | 11.0297 | 12.0211 |  | 12.2309 |  |  | 11.757 | 12.5435 | 12.616 | [6 empty] | 12.5569 |  |  | 11.2631 |  |  | 9.2401 | 10.3377 | 11.8596 | 7.5891 | 9.0618 | 12.4574 | 7.8521 | 9.5066 | 12.3065 | 9.2546 | 10.4633 | 7.6649 | 10.2474 | 8.198 | 10.1766 | 7.8106 | 9.719 | 13.1668 | 10.5478 | 10.2683 | 11.4063 | 8.09 | 9.8182 | 12.6343 | 8.1391 | 10.2975 | 9.789 | 9.7472 | 8.5845 | 10.1748 | -0.17528 | 20.9535 | 0.033682 | 0.049723 | -37.9194 | 3.1204 | 1.64 | 0.26 | 0.091827 | -0.49433 | 0.50764 | -0.3572 | 0.63619 | -0.73362 | 0.63941 | 0.40801 | 0.42801 | 0.41934 | 0.37492 | 0.49469 | 0.42788 | 0.41319
42810.4369 | -268 | 18.5515 | 18.6373 | 18.6156 | 18.6177 | 17.9593 | 16.607 | 14.6648 | 16.7117 | 17.2031 | 17.2959 | 17.3046 | 16.8508 | 15.8907 | 14.4951 | 15.0124 | 15.0157 | 15.5642 | 13.4139 | 13.5299 | 14.0996 |  |  |  | 16.6167 | 15.9533 | 15.0582 | 10.2489 | 9.5383 | 9.8343 | 17.2378 | 16.3789 | 15.1763 | 16.9159 | 16.1937 | 15.1863 | 10.7731 | 11.7147 |  | 12.0922 | 10.4958 | 10.2647 | 8.6316 |  | 6.4469 | 6.4445 | 5.9607 | 6.1401 | 6.294 | 6.6388 | 7.1766 | 5.2551 | 6.4168 | 4.908 | 6.6435 | 8.1294 | 42.4474 | 46.4951 | 42.8546 | 15.3399 |  |  | 0.056731 | -0.19573 | 0.00382 | -0.03877 | -0.015608 | -0.23505 | 0.63468 | -0.2755 | -0.34637 | -0.48292 | -0.31584 | 8.8713 | 8.8725 | 2.0085 | 15.8788 | 16.7566 | 17.2821 | 17.6007 | 17.56 | 16.5394 | 14.8959 | 16.8608 | 17.1909 | 17.4852 | 17.5232 | 17.2616 | 16.4675 | 14.684 | 6.4458 | 8.5493 | 6.3998 | 5.8781 | 6.3399 | 6.6548 | 7.5867 | 15.9579 | 15.5783 | 15.4279 | 14.3508 | 14.2367 | 14.1663 |  |  |  | 10.6895 | 9.2868 | 9.0024 | 9.0991 | -0.024263 | 0.13835 | 12.7729 |  |  | 10.6519 |  |  | 16.892 | 16.0843 | 15.0665 | 16.3882 | 15.6788 | 14.7748 | 10.1679 | 10.576 | 11.258 | 11.1722 | 9.0707 |  | 10.5751 | 7.6376 | 9.8934 | 9.2592 | 11.0274 | 12.0329 |  | 12.2304 |  |  | 11.7761 | 12.5413 | 12.5991 | [6 empty] | 12.5527 |  |  | 11.2629 |  |  | 9.2363 | 10.3402 | 11.8631 | 7.602 | 9.0712 | 12.4508 | 7.8443 | 9.512 | 12.3062 | 9.2463 | 10.4657 | 7.668 | 10.2495 | 8.1939 | 10.1762 | 7.8001 | 9.713 | 13.1516 | 10.5409 | 10.2661 | 11.3925 | 8.0861 | 9.8032 | 12.6253 | 8.1363 | 10.2958 | 9.7834 | 9.7467 | 8.5824 | 10.1677 | 0.005188 | 20.9542 | 0.034027 | 0.049108 | -37.8961 | 3.1204 | -0.75 | 0.32 | 0.27923 | -0.51554 | 0.072022 | -0.22945 | -0.14563 | -0.56515 | 0.92866 | 0.40922 | 0.42657 | 0.4189 | 0.37077 | 0.48408 | 0.42794 | 0.4122
42810.4369 | -267 | 18.5514 | 18.6394 | 18.6144 | 18.6174 | 17.9611 | 16.6034 | 14.6762 | 16.7145 | 17.2046 | 17.3028 | 17.3063 | 16.8543 | 15.8801 | 14.4999 | 15.0082 | 15.0112 | 15.5658 | 13.4075 | 13.5386 | 14.0971 |  |  |  | 16.6242 | 15.9554 | 15.0581 | 10.2448 | 9.5338 | 9.8208 | 17.244 | 16.3915 | 15.1916 | 16.9203 | 16.2059 | 15.1991 | 10.7742 | 11.7335 |  | 12.0995 | 10.5002 | 10.2706 | 8.6284 |  | 6.4432 | 6.4476 | 5.9648 | 6.1368 | 6.2876 | 6.6111 | 7.1418 | 5.2456 | 6.4184 | 4.8701 | 6.6483 | 8.1243 | 42.4197 | 46.5058 | 42.8429 | 15.3375 |  |  | 0.050159 | -0.11097 | -0.063204 | 0.062426 | -0.053064 | -0.147 | 0.52954 | -0.33726 | -0.25024 | -0.7372 | -0.3675 | 8.8682 | 8.8694 | 2.0084 | 15.8815 | 16.7679 | 17.2888 | 17.6022 | 17.5575 | 16.5486 | 14.8909 | 16.8716 | 17.1942 | 17.4851 | 17.5244 | 17.274 | 16.4734 | 14.6981 | 6.4647 | 8.5548 | 6.4982 | 5.928 | 6.2876 | 6.6666 | 7.6001 | 15.9715 | 15.5877 | 15.4293 | 14.3614 | 14.2459 | 14.1791 |  |  |  | 10.7019 | 9.2993 | 9.0127 | 9.1027 | 0.0036956 | 0.065707 | 12.7747 |  |  | 10.6416 |  |  | 16.888 | 16.0834 | 15.0727 | 16.391 | 15.682 | 14.7818 | 10.1701 | 10.5765 | 11.2679 | 11.1901 | 8.97 |  | 10.5659 | 7.6885 | 9.8713 | 9.258 | 11.022 | 12.0642 |  | 12.2188 |  |  | 11.7923 | 12.5046 | 12.5981 | [6 empty] | 12.5197 |  |  | 11.2414 |  |  | 9.2373 | 10.3355 | 11.8683 | 7.6091 | 9.0827 | 12.4519 | 7.8419 | 9.5135 | 12.2966 | 9.2525 | 10.4613 | 7.6816 | 10.257 | 8.196 | 10.1762 | 7.8023 | 9.7029 | 13.144 | 10.5414 | 10.2629 | 11.3851 | 8.0828 | 9.8033 | 12.6246 | 8.1317 | 10.2903 | 9.7816 | 9.7403 | 8.5789 | 10.1671 | 0.024255 | 20.9532 | 0.034032 | 0.049593 | -37.9081 | 3.1205 | 14.52 | 0.31 | 0.26255 | -0.38817 | -0.29296 | 0.29115 | -0.26851 | -0.4469 | 0.84822 | 0.41171 | 0.42443 | 0.41875 | 0.37004 | 0.47469 | 0.42807 | 0.41251
42810.437 | -266 | 18.5574 | 18.6468 | 18.6197 | 18.6224 | 17.9685 | 16.6072 | 14.6785 | 16.7205 | 17.2113 | 17.3064 | 17.3093 | 16.858 | 15.8857 | 14.5064 | 15.0029 | 15.0083 | 15.5588 | 13.4032 | 13.5291 | 14.0831 |  |  |  | 16.6202 | 15.9518 | 15.0584 | 10.2432 | 9.5343 | 9.8054 | 17.2406 | 16.3872 | 15.1849 | 16.9196 | 16.2025 | 15.2005 | 10.7774 | 11.7328 |  | 12.0957 | 10.4939 | 10.2681 | 8.6184 |  | 6.4466 | 6.4444 | 5.9649 | 6.1472 | 6.2854 | 6.5983 | 7.1226 | 5.2305 | 6.4207 | 4.8638 | 6.6495 | 8.1161 | 42.3892 | 46.5102 | 42.8255 | 15.3305 |  |  | -0.030665 | -0.17931 | 0.11028 | -0.2911 | 0.002792 | 0.11585 | 0.53742 | -0.28798 | -0.16695 | -0.043391 | -0.36174 | 8.8691 | 8.8702 | 2.0083 | 15.8724 | 16.7552 | 17.2857 | 17.5951 | 17.5533 | 16.531 | 14.8802 | 16.8569 | 17.19 | 17.4829 | 17.5204 | 17.2682 | 16.4632 | 14.6866 | 6.4628 | 8.5502 | 6.5449 | 5.938 | 6.2325 | 6.6584 | 7.6 | 15.9587 | 15.5754 | 15.4281 | 14.355 | 14.232 | 14.1732 |  |  |  | 10.7019 | 9.2905 | 9.0121 | 9.082 | 0.000454 | 0.052156 | 12.7587 |  |  | 10.6379 |  |  | 16.8863 | 16.0894 | 15.058 | 16.3857 | 15.6736 | 14.7761 | 10.1671 | 10.5722 | 11.2701 | 11.2049 | 8.9018 |  | 10.5677 | 7.7264 | 9.8774 | 9.2629 | 11.0339 | 12.1316 |  | 12.2297 |  |  | 11.8104 | 12.4953 | 12.5865 | [6 empty] | 12.511 |  |  | 11.2372 |  |  | 9.2331 | 10.3323 | 11.8652 | 7.6158 | 9.0851 | 12.4489 | 7.8349 | 9.5133 | 12.2901 | 9.2506 | 10.4514 | 7.6892 | 10.2625 | 8.1825 | 10.1722 | 7.7964 | 9.7057 | 13.1544 | 10.5471 | 10.2609 | 11.3895 | 8.082 | 9.8137 | 12.6326 | 8.1233 | 10.2907 | 9.7871 | 9.7502 | 8.5811 | 10.1659 | 0.059886 | 20.9528 | 0.033969 | 0.049304 | -37.8402 | 3.1204 | 0.55 | 0.24 | -0.20528 | -0.49343 | 0.38697 | -0.62871 | 0.06159 | 0.39673 | 0.85449 | 0.41367 | 0.42358 | 0.41901 | 0.36929 | 0.46948 | 0.42845 | 0.41309
42810.437 | -265 | 18.5558 | 18.6429 | 18.6194 | 18.6158 | 17.9616 | 16.6118 | 14.6786 | 16.7178 | 17.2168 | 17.3054 | 17.3127 | 16.8591 | 15.8934 | 14.5019 | 14.9971 | 15.0098 | 15.5593 | 13.4044 | 13.5181 | 14.0792 |  |  |  | 16.6191 | 15.9494 | 15.0541 | 10.2415 | 9.5374 | 9.8093 | 17.2416 | 16.382 | 15.1788 | 16.9177 | 16.2017 | 15.1973 | 10.7727 | 11.729 |  | 12.0967 | 10.4792 | 10.2621 | 8.6082 |  | 6.4476 | 6.4484 | 5.963 | 6.1457 | 6.2808 | 6.5832 | 7.1246 | 5.1611 | 6.4206 | 4.854 | 6.6434 | 8.1157 | 42.368 | 46.5165 | 42.8191 | 15.321 |  |  | -0.076665 | -0.047881 | 0.058364 | -0.00197 | -0.083948 | 0.29721 | 0.46185 | -0.30901 | 0.24132 | -0.22927 | -0.51871 | 8.8693 | 8.8704 | 2.0086 | 15.8854 | 16.76 | 17.2902 | 17.5976 | 17.5604 | 16.5411 | 14.883 | 16.8637 | 17.2015 | 17.4837 | 17.5308 | 17.2723 | 16.4718 | 14.693 | 6.4283 | 8.5435 | 6.6214 | 5.9751 | 6.19 | 6.6694 | 7.6097 | 15.9637 | 15.5748 | 15.4157 | 14.3574 | 14.2355 | 14.1699 |  |  |  | 10.6982 | 9.2793 | 9.013 | 9.0557 | -0.050399 | 0.014328 | 12.7652 |  |  | 10.6417 |  |  | 16.8966 | 16.0981 | 15.0575 | 16.3898 | 15.6788 | 14.783 | 10.1788 | 10.5792 | 11.2889 | 11.2125 | 8.8701 |  | 10.5636 | 7.76 | 9.8849 | 9.2539 | 11.0321 | 12.1511 |  | 12.2205 |  |  | 11.8291 | 12.513 | 12.5618 | [6 empty] | 12.5064 |  |  | 11.2439 |  |  | 9.2276 | 10.3324 | 11.8589 | 7.6072 | 9.0915 | 12.4431 | 7.8341 | 9.5049 | 12.2895 | 9.2405 | 10.4529 | 7.6794 | 10.2679 | 8.1733 | 10.1722 | 7.7942 | 9.7093 | 13.1642 | 10.558 | 10.2634 | 11.3979 | 8.0798 | 9.8184 | 12.643 | 8.1133 | 10.3001 | 9.7928 | 9.7622 | 8.5856 | 10.1749 | 0.019248 | 20.9545 | 0.033258 | 0.048746 | -37.9227 | 3.1204 | 16.95 | 0.37 | -0.32458 | -0.25499 | 0.28152 | -0.051721 | -0.33771 | 0.63544 | 0.79212 | 0.41441 | 0.42289 | 0.4192 | 0.3744 | 0.46212 | 0.42858 | 0.41369
42810.437 | -264 | 18.5577 | 18.6481 | 18.62 | 18.6199 | 17.9582 | 16.611 | 14.6717 | 16.7235 | 17.2133 | 17.3002 | 17.3155 | 16.8606 | 15.8952 | 14.507 | 14.9975 | 15.0006 | 15.5587 | 13.4036 | 13.5214 | 14.0827 |  |  |  | 16.614 | 15.9499 | 15.0501 | 10.2382 | 9.5369 | 9.8246 | 17.2334 | 16.3719 | 15.1784 | 16.9124 | 16.1978 | 15.1954 | 10.7716 | 11.7347 |  | 12.099 | 10.4689 | 10.2598 | 8.6196 |  | 6.4425 | 6.4487 | 5.971 | 6.1391 | 6.2802 | 6.567 | 7.1101 | 5.0664 | 6.4126 | 4.8134 | 6.6389 | 8.1151 | 42.3589 | 46.5238 | 42.8101 | 15.3226 |  |  | -0.068777 | -0.12082 | 0.085304 | -0.22211 | -0.097088 | -0.015572 | 0.26406 | -0.33069 | 0.54139 | -0.25151 | -0.41797 | 8.8717 | 8.8731 | 2.0088 | 15.8778 | 16.7504 | 17.2784 | 17.591 | 17.5568 | 16.5369 | 14.8901 | 16.8574 | 17.1962 | 17.4832 | 17.5256 | 17.2634 | 16.4704 | 14.6908 | 6.4032 | 8.5348 | 6.6936 | 5.9591 | 6.1781 | 6.6614 | 7.6099 | 15.9568 | 15.5725 | 15.4247 | 14.3557 | 14.2302 | 14.1681 |  |  |  | 10.6979 | 9.2745 | 9.0066 | 9.0482 | -0.029531 | -0.079396 | 12.7553 |  |  | 10.635 |  |  | 16.8888 | 16.0755 | 15.0546 | 16.3804 | 15.6652 | 14.7726 | 10.1759 | 10.5734 | 11.2877 | 11.2084 | 8.8153 |  | 10.5641 | 7.7855 | 9.8893 | 9.2442 | 11.0281 | 12.1378 |  | 12.2162 |  |  | 11.827 | 12.5131 | 12.5542 | [6 empty] | 12.4912 |  |  | 11.2414 |  |  | 9.2111 | 10.3216 | 11.8504 | 7.584 | 9.0924 | 12.4316 | 7.8273 | 9.4855 | 12.2817 | 9.2333 | 10.4521 | 7.657 | 10.2717 | 8.1608 | 10.1629 | 7.7729 | 9.7081 | 13.1642 | 10.5573 | 10.2674 | 11.3915 | 8.0686 | 9.8154 | 12.6476 | 8.1176 | 10.2903 | 9.7901 | 9.7631 | 8.5874 | 10.1758 | 0.051605 | 20.954 | 0.033481 | 0.048703 | -37.9323 | 3.1204 | 12.98 | 0.42 | -0.30744 | -0.40505 | 0.34034 | -0.54918 | -0.36317 | -0.14544 | 0.59893 | 0.41595 | 0.42233 | 0.41933 | 0.37625 | 0.45411 | 0.42823 | 0.41389
42810.437 | -263 | 18.561 | 18.6508 | 18.6239 | 18.6194 | 17.9617 | 16.6186 | 14.6753 | 16.7308 | 17.2132 | 17.3039 | 17.3217 | 16.8565 | 15.8992 | 14.5033 | 14.9914 | 14.9985 | 15.5558 | 13.409 | 13.5266 | 14.0826 |  |  |  | 16.6176 | 15.9469 | 15.0601 | 10.2366 | 9.5435 | 9.8557 | 17.2306 | 16.376 | 15.1785 | 16.9115 | 16.1991 | 15.1876 | 10.7758 | 11.7512 |  | 12.0967 | 10.4615 | 10.2688 | 8.6219 |  | 6.4389 | 6.4442 | 5.9664 | 6.1292 | 6.2665 | 6.5463 | 7.1369 | 4.9835 | 6.4187 | 4.7804 | 6.6444 | 8.1137 | 42.3468 | 46.5246 | 42.8105 | 15.3109 |  |  | -0.040521 | -0.11031 | 0.13262 | -0.071626 | -0.14966 | -0.15488 | 0.43426 | -0.13882 | 0.39583 | 0.6351 | -0.47103 | 8.8687 | 8.8697 | 2.0082 | 15.8712 | 16.7484 | 17.2708 | 17.591 | 17.5534 | 16.5396 | 14.8829 | 16.8552 | 17.19 | 17.4751 | 17.5222 | 17.256 | 16.4716 | 14.6915 | 6.4012 | 8.5464 | 6.7236 | 5.9082 | 6.2442 | 6.6648 | 7.6173 | 15.9547 | 15.5768 | 15.4239 | 14.3517 | 14.2368 | 14.1736 |  |  |  | 10.6991 | 9.2766 | 9.0064 | 9.0596 | -0.054248 | -0.0099498 | 12.7539 |  |  | 10.6277 |  |  | 16.8868 | 16.0748 | 15.0512 | 16.3809 | 15.6675 | 14.7668 | 10.1807 | 10.5695 | 11.291 | 11.2076 | 8.7748 |  | 10.573 | 7.8641 | 9.8913 | 9.2484 | 11.0409 | 12.149 |  | 12.2286 |  |  | 11.8289 | 12.5052 | 12.5532 | [6 empty] | 12.5028 |  |  | 11.2461 |  |  | 9.2066 | 10.3187 | 11.8507 | 7.561 | 9.0936 | 12.4304 | 7.8168 | 9.4721 | 12.2764 | 9.2272 | 10.4475 | 7.6518 | 10.262 | 8.1504 | 10.1611 | 7.7379 | 9.7005 | 13.1584 | 10.5507 | 10.264 | 11.3729 | 8.0592 | 9.8113 | 12.6447 | 8.1247 | 10.2824 | 9.7925 | 9.7639 | 8.5912 | 10.1665 | 0.14675 | 20.9529 | 0.032965 | 0.047697 | -37.8941 | 3.1205 | 5.19 | 0.36 | -0.236 | -0.38702 | 0.42435 | -0.31186 | -0.45088 | -0.45868 | 0.76804 | 0.41737 | 0.42021 | 0.41964 | 0.37688 | 0.45164 | 0.4283 | 0.41361
42810.437 | -262 | 18.5448 | 18.6484 | 18.6204 | 18.623 | 17.9545 | 16.617 | 14.6824 | 16.7192 | 17.2105 | 17.3032 | 17.3092 | 16.8592 | 15.8948 | 14.5012 | 14.9937 | 14.9989 | 15.5543 | 13.408 | 13.5235 | 14.0847 |  |  |  | 16.6155 | 15.9545 | 15.0624 | 10.2374 | 9.543 | 9.8706 | 17.2279 | 16.3803 | 15.1762 | 16.92 | 16.1971 | 15.2015 | 10.7849 | 11.7704 |  | 12.0953 | 10.4584 | 10.2706 | 8.6322 |  | 6.4349 | 6.4476 | 5.9663 | 6.1367 | 6.2677 | 6.5361 | 7.1176 | 4.9787 | 6.4165 | 4.7622 | 6.6352 | 8.116 | 42.3299 | 46.5237 | 42.7997 | 15.3326 |  |  | -0.086521 | -0.11162 | -0.031664 | -0.20305 | -0.29357 | -0.45847 | 0.36592 | -0.29324 | -0.44075 | 0.29858 | -0.27849 | 8.8659 | 8.867 | 2.0083 | 15.8636 | 16.7463 | 17.2727 | 17.5923 | 17.551 | 16.5362 | 14.885 | 16.8586 | 17.1853 | 17.4781 | 17.5178 | 17.2575 | 16.4686 | 14.6881 | 6.414 | 8.5557 | 6.6362 | 5.9022 | 6.2764 | 6.6578 | 7.6189 | 15.9552 | 15.5776 | 15.4245 | 14.3482 | 14.2426 | 14.174 |  |  |  | 10.7043 | 9.2843 | 9.0073 | 9.0794 | 0.05313 | -0.063775 | 12.7492 |  |  | 10.6387 |  |  | 16.8858 | 16.0841 | 15.0604 | 16.3819 | 15.6649 | 14.7685 | 10.1953 | 10.5728 | 11.2993 | 11.2206 | 8.8053 |  | 10.5665 | 7.9269 | 9.8895 | 9.2369 | 11.0393 | 12.1322 |  | 12.2194 |  |  | 11.8398 | 12.5056 | 12.5496 | [6 empty] | 12.5012 |  |  | 11.2518 |  |  | 9.2003 | 10.3215 | 11.8576 | 7.5621 | 9.0977 | 12.4359 | 7.8166 | 9.453 | 12.2746 | 9.2277 | 10.4501 | 7.6504 | 10.2648 | 8.1471 | 10.167 | 7.7395 | 9.7067 | 13.1537 | 10.5501 | 10.2545 | 11.3603 | 8.0641 | 9.8083 | 12.6482 | 8.1229 | 10.28 | 9.7934 | 9.7645 | 8.5896 | 10.1686 | 0.011544 | 20.9561 | 0.032603 | 0.046416 | -37.8478 | 3.1204 | 13.93 | 0.29 | -0.34486 | -0.38932 | -0.20736 | -0.52509 | -0.63148 | -0.78915 | 0.70501 | 0.41631 | 0.41841 | 0.41991 | 0.37465 | 0.46155 | 0.42832 | 0.41323
42810.437 | -261 | 18.5487 | 18.6382 | 18.6237 | 18.6189 | 17.9566 | 16.6106 | 14.6752 | 16.7208 | 17.2092 | 17.3 | 17.3088 | 16.846 | 15.8923 | 14.5015 | 14.996 | 14.9977 | 15.556 | 13.4148 | 13.5296 | 14.0897 |  |  |  | 16.6179 | 15.9521 | 15.0634 | 10.2437 | 9.5465 | 9.8763 | 17.2376 | 16.3767 | 15.1765 | 16.9061 | 16.1975 | 15.1982 | 10.7722 | 11.7905 |  | 12.0859 | 10.4518 | 10.2689 | 8.6421 |  | 6.4328 | 6.449 | 5.9717 | 6.1263 | 6.2624 | 6.5268 | 7.086 | 4.9339 | 6.4201 | 4.7491 | 6.6444 | 8.1065 | 42.3086 | 46.5059 | 42.7845 | 15.4264 |  |  | 0.12967 | -0.078109 | 0.048504 | -0.3095 | -0.24034 | -0.41904 | 0.33897 | -0.39246 | -0.31893 | -0.87693 | -0.20596 | 8.8701 | 8.8714 | 2.0085 | 15.8697 | 16.7565 | 17.2778 | 17.6023 | 17.5573 | 16.542 | 14.8931 | 16.8624 | 17.1889 | 17.4866 | 17.5264 | 17.2631 | 16.4676 | 14.6999 | 6.4618 | 8.5522 | 6.5585 | 5.9232 | 6.3012 | 6.6648 | 7.6123 | 15.9509 | 15.5722 | 15.4285 | 14.3466 | 14.2283 | 14.173 |  |  |  | 10.7001 | 9.2825 | 9.0071 | 9.0697 | 0.12262 | -0.0067504 | 12.7502 |  |  | 10.6426 |  |  | 16.892 | 16.0845 | 15.0598 | 16.3868 | 15.6719 | 14.7742 | 10.2155 | 10.5791 | 11.3037 | 11.2221 | 8.8358 |  | 10.5659 | 7.985 | 9.8917 | 9.2394 | 11.033 | 12.1254 |  | 12.2224 |  |  | 11.8407 | 12.4835 | 12.5611 | [6 empty] | 12.5127 |  |  | 11.2444 |  |  | 9.1936 | 10.3182 | 11.8529 | 7.5601 | 9.1098 | 12.4382 | 7.8071 | 9.4431 | 12.268 | 9.2215 | 10.4572 | 7.6625 | 10.2594 | 8.1449 | 10.1685 | 7.7571 | 9.7129 | 13.1598 | 10.5544 | 10.2571 | 11.3553 | 8.067 | 9.8112 | 12.6505 | 8.1194 | 10.2797 | 9.7932 | 9.7706 | 8.5926 | 10.1792 | 0.05796 | 20.9535 | 0.03219 | 0.046242 | -37.8064 | 3.1205 | 15.86 | 0.42 | 0.42218 | -0.32568 | 0.25664 | -0.64829 | -0.57136 | -0.75444 | 0.67854 | 0.41544 | 0.41687 | 0.41963 | 0.37014 | 0.46941 | 0.42762 | 0.41337
42810.437 | -260 | 18.5454 | 18.6386 | 18.613 | 18.6172 | 17.9512 | 16.6044 | 14.6819 | 16.7197 | 17.2084 | 17.3 | 17.3096 | 16.8512 | 15.8878 | 14.4943 | 14.9885 | 15.0085 | 15.5524 | 13.405 | 13.5227 | 14.0833 |  |  |  | 16.6223 | 15.9542 | 15.0587 | 10.2407 | 9.554 | 9.8746 | 17.2334 | 16.3776 | 15.1749 | 16.913 | 16.1927 | 15.195 | 10.7728 | 11.8089 |  | 12.0866 | 10.4496 | 10.2645 | 8.6358 |  | 6.4285 | 6.4496 | 5.9692 | 6.1228 | 6.2549 | 6.5169 | 7.0557 | 4.9066 | 6.4198 | 4.7568 | 6.642 | 8.1075 | 42.2803 | 46.4872 | 42.7726 | 15.402 |  |  | 0.086303 | -0.053797 | 0.092532 | -0.12157 | -0.126 | -0.26725 | 0.53676 | -0.50352 | -0.26892 | -0.25634 | -0.26418 | 8.8707 | 8.8719 | 2.0087 | 15.8763 | 16.7504 | 17.2788 | 17.6003 | 17.5625 | 16.5397 | 14.8847 | 16.854 | 17.1806 | 17.4812 | 17.5231 | 17.2642 | 16.4658 | 14.6963 | 6.466 | 8.5364 | 6.4577 | 5.9226 | 6.2636 | 6.6641 | 7.6223 | 15.9439 | 15.5721 | 15.4224 | 14.344 | 14.2232 | 14.1609 |  |  |  | 10.6921 | 9.2824 | 9.0116 | 9.0406 | -0.16385 | 0.054603 | 12.7539 |  |  | 10.6305 |  |  | 16.884 | 16.0793 | 15.0532 | 16.3769 | 15.6659 | 14.7685 | 10.2187 | 10.5751 | 11.3026 | 11.2177 | 8.8681 |  | 10.5648 | 8.0055 | 9.8918 | 9.2274 | 11.0292 | 12.1168 |  | 12.2218 |  |  | 11.8398 | 12.4577 | 12.5427 | [6 empty] | 12.5049 |  |  | 11.2469 |  |  | 9.19 | 10.3163 | 11.8424 | 7.5392 | 9.1037 | 12.432 | 7.7955 | 9.4327 | 12.2654 | 9.2177 | 10.451 | 7.6501 | 10.2587 | 8.1418 | 10.1663 | 7.7548 | 9.7121 | 13.1503 | 10.5409 | 10.2581 | 11.3546 | 8.0685 | 9.8127 | 12.6494 | 8.1236 | 10.2741 | 9.7944 | 9.7775 | 8.6055 | 10.1746 | -0.12 | 20.9538 | 0.032569 | 0.046553 | -37.8645 | 3.1204 | 2.39 | 0.26 | 0.34442 | -0.27028 | 0.35447 | -0.40629 | -0.41369 | -0.60248 | 0.85385 | 0.41451 | 0.4163 | 0.41984 | 0.3696 | 0.48177 | 0.42782 | 0.41391
42810.437 | -259 | 18.5393 | 18.6386 | 18.6172 | 18.6132 | 17.9576 | 16.6026 | 14.6796 | 16.7201 | 17.2089 | 17.2992 | 17.3098 | 16.8491 | 15.8883 | 14.4936 | 14.9828 | 15.0034 | 15.5567 | 13.3933 | 13.5191 | 14.0844 |  |  |  | 16.6145 | 15.9536 | 15.0539 | 10.232 | 9.5502 | 9.8712 | 17.2219 | 16.3725 | 15.1721 | 16.9067 | 16.1907 | 15.1883 | 10.7792 | 11.8142 |  | 12.0901 | 10.4441 | 10.2567 | 8.623 |  | 6.4325 | 6.4568 | 5.9716 | 6.1249 | 6.2497 | 6.512 | 7.0367 | 4.9251 | 6.418 | 4.7853 | 6.641 | 8.1048 | 42.2729 | 46.4695 | 42.7646 | 15.3895 |  |  | -0.076665 | -0.16288 | 0.047848 | 0.10185 | -0.12206 | -0.11283 | 0.49471 | -0.40758 | 1.6421 | -0.39732 | -0.27531 | 8.867 | 8.8683 | 2.0085 | 15.8704 | 16.7446 | 17.2806 | 17.5966 | 17.5612 | 16.5357 | 14.8885 | 16.8569 | 17.1917 | 17.489 | 17.5243 | 17.2679 | 16.4644 | 14.6974 | 6.4069 | 8.5061 | 6.3492 | 5.8989 | 6.1707 | 6.6631 | 7.6261 | 15.9441 | 15.5694 | 15.4251 | 14.3416 | 14.2341 | 14.1698 |  |  |  | 10.6884 | 9.2791 | 9.0089 | 9.0112 | -0.032367 | -0.057753 | 12.7473 |  |  | 10.6224 |  |  | 16.8867 | 16.0805 | 15.0603 | 16.3778 | 15.6747 | 14.7719 | 10.2305 | 10.5695 | 11.3069 | 11.2252 | 8.9017 |  | 10.5672 | 8.0091 | 9.8901 | 9.2326 | 11.0282 | 12.1092 |  | 12.2237 |  |  | 11.862 | 12.4606 | 12.5449 | [6 empty] | 12.5049 |  |  | 11.2366 |  |  | 9.1724 | 10.3173 | 11.8511 | 7.5187 | 9.1088 | 12.4437 | 7.7864 | 9.4326 | 12.2584 | 9.2112 | 10.439 | 7.6338 | 10.2614 | 8.1487 | 10.165 | 7.7495 | 9.7189 | 13.137 | 10.539 | 10.2477 | 11.3574 | 8.073 | 9.8149 | 12.6489 | 8.1248 | 10.2655 | 9.7973 | 9.7829 | 8.5983 | 10.1674 | -0.14851 | 20.9536 | 0.032058 | 0.046293 | -37.8957 | 3.1204 | 8.24 | 0.3 | -0.32462 | -0.4703 | 0.2549 | 0.3719 | -0.40716 | -0.39146 | 0.81971 | 0.41365 | 0.41614 | 0.41966 | 0.37605 | 0.49428 | 0.42838 | 0.41461
42810.437 | -258 | 18.5348 | 18.6394 | 18.6188 | 18.6084 | 17.9596 | 16.6028 | 14.6719 | 16.7254 | 17.212 | 17.3018 | 17.3097 | 16.8543 | 15.8927 | 14.4942 | 14.9809 | 14.9891 | 15.5494 | 13.4099 | 13.5164 | 14.0815 |  |  |  | 16.6167 | 15.9611 | 15.0635 | 10.2235 | 9.5575 | 9.8588 | 17.233 | 16.3768 | 15.1761 | 16.9108 | 16.196 | 15.1936 | 10.7804 | 11.7873 |  | 12.0921 | 10.4513 | 10.2434 | 8.6161 |  | 6.4125 | 6.4453 | 5.9678 | 6.1209 | 6.2401 | 6.4852 | 6.9984 | 4.8885 | 6.4209 | 4.8564 | 6.6425 | 8.099 | 42.2559 | 46.4604 | 42.7439 | 15.3738 |  |  | 0.001535 | 0.061855 | 0.18256 | -0.019058 | -0.10563 | -0.10757 | 0.53939 | -0.35632 | -0.48882 | -0.62475 | -0.32439 | 8.8694 | 8.8707 | 2.0083 | 15.8677 | 16.7551 | 17.273 | 17.5949 | 17.5605 | 16.5354 | 14.8866 | 16.8655 | 17.2014 | 17.4874 | 17.5237 | 17.268 | 16.4669 | 14.6978 | 6.37 | 8.4628 | 6.2226 | 5.8592 | 6.1114 | 6.6561 | 7.6272 | 15.944 | 15.5694 | 15.425 | 14.3485 | 14.2321 | 14.1672 |  |  |  | 10.6877 | 9.2814 | 9 | 8.9859 | -0.10044 | -0.01616 | 12.7457 |  |  | 10.621 |  |  | 16.8835 | 16.0781 | 15.059 | 16.3843 | 15.6704 | 14.7771 | 10.2366 | 10.5723 | 11.3084 | 11.2231 | 8.9298 |  | 10.5569 | 8.0161 | 9.8823 | 9.2309 | 11.0177 | 12.1056 |  | 12.2176 |  |  | 11.8715 | 12.4961 | 12.5515 | [6 empty] | 12.5137 |  |  | 11.2475 |  |  | 9.1748 | 10.3107 | 11.8503 | 7.4927 | 9.1087 | 12.4536 | 7.7812 | 9.4358 | 12.255 | 9.2126 | 10.4461 | 7.6236 | 10.2591 | 8.1551 | 10.1639 | 7.7395 | 9.7091 | 13.1339 | 10.5339 | 10.2453 | 11.3569 | 8.0641 | 9.8166 | 12.6474 | 8.1108 | 10.2644 | 9.7867 | 9.7749 | 8.596 | 10.1637 | -0.10459 | 20.9533 | 0.031874 | 0.046329 | -37.8456 | 3.1204 | 9.29 | 0.28 | 0.045933 | 0.28981 | 0.49789 | -0.16087 | -0.37876 | -0.38221 | 0.85588 | 0.41253 | 0.41569 | 0.41936 | 0.37933 | 0.50846 | 0.42861 | 0.41528
42810.4371 | -257 | 18.5396 | 18.631 | 18.616 | 18.6073 | 17.9535 | 16.6051 | 14.6664 | 16.7236 | 17.2098 | 17.3041 | 17.306 | 16.8502 | 15.8903 | 14.4965 | 14.9755 | 14.9954 | 15.5588 | 13.3992 | 13.5143 | 14.0821 |  |  |  | 16.6156 | 15.9451 | 15.0602 | 10.2245 | 9.5639 | 9.8561 | 17.2338 | 16.3762 | 15.1696 | 16.9073 | 16.195 | 15.1927 | 10.7815 | 11.7351 |  | 12.0929 | 10.4531 | 10.2475 | 8.5965 |  | 6.4092 | 6.4467 | 5.9692 | 6.1134 | 6.2358 | 6.4761 | 6.9815 | 4.8703 | 6.4215 | 4.9223 | 6.6391 | 8.1 | 42.239 | 46.4569 | 42.7324 | 15.3577 |  |  | 0.037675 | -0.13134 | -0.040204 | 0.042714 | -0.13389 | -0.27842 | 0.60773 | -0.30244 | -0.28235 | 0.23774 | -0.28842 | 8.8697 | 8.8708 | 2.0085 | 15.8657 | 16.7534 | 17.2761 | 17.6 | 17.5599 | 16.5442 | 14.8902 | 16.8609 | 17.2027 | 17.4867 | 17.5247 | 17.2699 | 16.4718 | 14.6931 | 6.3624 | 8.461 | 6.0656 | 5.8224 | 6.047 | 6.6553 | 7.6255 | 15.9414 | 15.5727 | 15.4194 | 14.3489 | 14.2295 | 14.1684 |  |  |  | 10.6897 | 9.2747 | 9.0015 | 8.9714 | 0.061234 | 0.10598 | 12.7534 |  |  | 10.6183 |  |  | 16.8888 | 16.0907 | 15.0571 | 16.3857 | 15.6716 | 14.7689 | 10.2519 | 10.5763 | 11.3111 | 11.232 | 8.9745 |  | 10.5554 | 8.0755 | 9.8829 | 9.2505 | 11.0191 | 12.1024 |  | 12.2291 |  |  | 11.8493 | 12.4908 | 12.5572 | [6 empty] | 12.5212 |  |  | 11.2335 |  |  | 9.18 | 10.3129 | 11.8522 | 7.4849 | 9.1089 | 12.4616 | 7.7709 | 9.4445 | 12.2439 | 9.2109 | 10.4451 | 7.6029 | 10.2569 | 8.1517 | 10.171 | 7.738 | 9.7142 | 13.1404 | 10.529 | 10.2385 | 11.367 | 8.0561 | 9.8143 | 12.6524 | 8.1223 | 10.2698 | 9.7892 | 9.7848 | 8.6 | 10.1728 | -0.33899 | 20.9545 | 0.031094 | 0.047132 | -37.8439 | 3.1204 | -3 | 0.34 | 0.22756 | -0.42231 | -0.23365 | 0.24083 | -0.42641 | -0.6149 | 0.90847 | 0.41124 | 0.41406 | 0.41886 | 0.38008 | 0.52572 | 0.42919 | 0.41575
42810.4371 | -256 | 18.5317 | 18.6342 | 18.6161 | 18.6103 | 17.9615 | 16.6028 | 14.6803 | 16.721 | 17.2116 | 17.3016 | 17.3083 | 16.8536 | 15.8856 | 14.501 | 14.9813 | 14.9987 | 15.547 | 13.4054 | 13.5168 | 14.0791 |  |  |  | 16.6189 | 15.9586 | 15.0569 | 10.2294 | 9.5573 | 9.8602 | 17.2196 | 16.3718 | 15.1794 | 16.9084 | 16.1964 | 15.1889 | 10.7756 | 11.6845 |  | 12.0922 | 10.4526 | 10.2427 | 8.5747 |  | 6.4174 | 6.4518 | 5.9636 | 6.1206 | 6.2291 | 6.4719 | 6.9768 | 4.8458 | 6.4189 | 5.0029 | 6.6395 | 8.1015 | 42.2429 | 46.4657 | 42.7308 | 15.3487 |  |  | 0.1139 | -0.079425 | 0.065592 | 0.17019 | -0.040576 | -0.33165 | 0.59328 | -0.21504 | -0.36622 | -0.22172 | -0.26279 | 8.8707 | 8.8718 | 2.0086 | 15.8637 | 16.7528 | 17.2729 | 17.5908 | 17.5525 | 16.5313 | 14.8839 | 16.8516 | 17.1908 | 17.4775 | 17.5191 | 17.2608 | 16.4736 | 14.6924 | 6.3387 | 8.4717 | 5.9502 | 5.7829 | 5.9967 | 6.6543 | 7.6293 | 15.9416 | 15.5736 | 15.4223 | 14.3451 | 14.2254 | 14.1619 |  |  |  | 10.6941 | 9.2758 | 9.0023 | 8.9556 | 0.088585 | -0.015596 | 12.7601 |  |  | 10.6266 |  |  | 16.8966 | 16.0902 | 15.0643 | 16.3913 | 15.6764 | 14.7753 | 10.263 | 10.5795 | 11.3114 | 11.2365 | 8.9803 |  | 10.5562 | 8.1721 | 9.8909 | 9.2622 | 11.0212 | 12.0942 |  | 12.2173 |  |  | 11.8143 | 12.4957 | 12.55 | [6 empty] | 12.5123 |  |  | 11.2206 |  |  | 9.1513 | 10.2934 | 11.8332 | 7.4595 | 9.0949 | 12.4574 | 7.7585 | 9.432 | 12.2393 | 9.1916 | 10.4319 | 7.5689 | 10.2408 | 8.1411 | 10.1442 | 7.7416 | 9.7176 | 13.1401 | 10.5233 | 10.2496 | 11.382 | 8.0683 | 9.8146 | 12.6432 | 8.1261 | 10.2703 | 9.8038 | 9.794 | 8.6 | 10.1783 | -0.15544 | 20.9529 | 0.031737 | 0.046539 | -37.9022 | 3.1204 | 6.28 | 0.31 | 0.39567 | -0.32841 | 0.29844 | 0.48074 | -0.23474 | -0.67111 | 0.8976 | 0.4111 | 0.41164 | 0.41861 | 0.3826 | 0.53897 | 0.4296 | 0.41634
42810.4371 | -255 | 18.5314 | 18.6271 | 18.6044 | 18.6117 | 17.9493 | 16.592 | 14.6695 | 16.7131 | 17.1993 | 17.2956 | 17.2987 | 16.844 | 15.8754 | 14.4834 | 14.9743 | 14.9982 | 15.5409 | 13.3992 | 13.5093 | 14.0864 |  |  |  | 16.6045 | 15.9434 | 15.051 | 10.2276 | 9.5597 | 9.8639 | 17.221 | 16.3683 | 15.1721 | 16.9035 | 16.1944 | 15.1832 | 10.7765 | 11.6272 |  | 12.0801 | 10.4481 | 10.2376 | 8.5374 |  | 6.435 | 6.4492 | 5.9666 | 6.1149 | 6.224 | 6.4741 | 7 | 4.8224 | 6.4202 | 5.0174 | 6.6505 | 8.098 | 42.2258 | 46.4674 | 42.7144 | 15.3392 |  |  | 0.053447 | -0.27985 | -0.006036 | 0.021026 | -0.089204 | -0.033972 | 0.6925 | -0.30046 | 0.042633 | -0.24879 | -0.33293 | 8.8706 | 8.872 | 2.0084 | 15.8668 | 16.7444 | 17.2759 | 17.5891 | 17.5594 | 16.5285 | 14.8843 | 16.8583 | 17.1913 | 17.4803 | 17.5232 | 17.2611 | 16.4757 | 14.7024 | 6.3677 | 8.4956 | 5.8931 | 5.7701 | 5.9464 | 6.653 | 7.6364 | 15.9377 | 15.5699 | 15.4184 | 14.3369 | 14.2226 | 14.1568 |  |  |  | 10.6884 | 9.2789 | 8.9967 | 8.9282 | 0.10256 | 0.051403 | 12.7603 |  |  | 10.6142 |  |  | 16.8927 | 16.0831 | 15.0601 | 16.3887 | 15.67 | 14.7757 | 10.2711 | 10.5796 | 11.3112 | 11.2355 | 9.0049 |  | 10.5593 | 8.2462 | 9.8853 | 9.2652 | 11.0217 | 12.1132 |  | 12.2152 |  |  | 11.8192 | 12.5085 | 12.5703 | [6 empty] | 12.4987 |  |  | 11.2212 |  |  | 9.1565 | 10.2961 | 11.8386 | 7.4572 | 9.1101 | 12.467 | 7.7608 | 9.4381 | 12.2404 | 9.1882 | 10.4393 | 7.5656 | 10.2365 | 8.1486 | 10.1508 | 7.7386 | 9.7067 | 13.1346 | 10.5176 | 10.2358 | 11.371 | 8.0622 | 9.8129 | 12.6365 | 8.1199 | 10.2607 | 9.7915 | 9.7947 | 8.5948 | 10.1652 | -0.075511 | 20.9514 | 0.032001 | 0.046228 | -37.8872 | 3.1204 | 12.02 | 0.31 | 0.27104 | -0.61644 | -0.090534 | 0.16897 | -0.34805 | -0.21479 | 0.96976 | 0.41053 | 0.4094 | 0.41854 | 0.37923 | 0.54614 | 0.43067 | 0.41691
42810.4371 | -254 | 18.5285 | 18.6321 | 18.614 | 18.612 | 17.9513 | 16.606 | 14.675 | 16.7214 | 17.2029 | 17.2953 | 17.3042 | 16.8496 | 15.8869 | 14.4882 | 14.9721 | 14.9913 | 15.5439 | 13.3949 | 13.5105 | 14.0812 |  |  |  | 16.6161 | 15.9501 | 15.0547 | 10.2236 | 9.5741 | 9.8585 | 17.219 | 16.3601 | 15.1613 | 16.896 | 16.1925 | 15.1823 | 10.7634 | 11.5766 |  | 12.0778 | 10.4576 | 10.2336 | 8.4831 |  | 6.4306 | 6.4504 | 5.957 | 6.093 | 6.216 | 6.4655 | 6.9921 | 4.8406 | 6.4183 | 4.9638 | 6.6465 | 8.0921 | 42.2236 | 46.467 | 42.709 | 15.324 |  |  | -0.012925 | -0.11359 | -0.036264 | -0.018398 | -0.080004 | -0.34019 | 0.47894 | -0.1697 | -1.6183 | -0.21899 | -0.31783 | 8.8679 | 8.8693 | 2.0086 | 15.8564 | 16.7364 | 17.2714 | 17.5928 | 17.5514 | 16.5262 | 14.8846 | 16.8565 | 17.1912 | 17.4848 | 17.5172 | 17.2603 | 16.4653 | 14.6929 | 6.4424 | 8.5255 | 5.8318 | 5.7754 | 5.9221 | 6.6665 | 7.6358 | 15.9404 | 15.5696 | 15.4208 | 14.3433 | 14.229 | 14.1636 |  |  |  | 10.6881 | 9.2779 | 9.0065 | 8.9255 | 0.22129 | 0.015457 | 12.7629 |  |  | 10.6228 |  |  | 16.8935 | 16.0837 | 15.0672 | 16.3896 | 15.6693 | 14.7798 | 10.2833 | 10.5788 | 11.3184 | 11.2488 | 9.0374 |  | 10.5626 | 8.3474 | 9.8809 | 9.2774 | 11.0298 | 12.1303 |  | 12.2249 |  |  | 11.8221 | 12.5048 | 12.5622 | [6 empty] | 12.492 |  |  | 11.2089 |  |  | 9.1559 | 10.2975 | 11.83 | 7.4671 | 9.1073 | 12.4566 | 7.7619 | 9.4426 | 12.2423 | 9.194 | 10.4347 | 7.5627 | 10.2403 | 8.1508 | 10.1531 | 7.74 | 9.6984 | 13.1292 | 10.5189 | 10.2459 | 11.3719 | 8.0681 | 9.8078 | 12.6317 | 8.1212 | 10.2666 | 9.7922 | 9.8089 | 8.5967 | 10.1628 | 0.024833 | 20.9519 | 0.032116 | 0.046126 | -37.8971 | 3.1204 | -8.56 | 0.4 | -0.13329 | -0.39275 | -0.22191 | -0.15806 | -0.32961 | -0.67968 | 0.80647 | 0.40973 | 0.40645 | 0.41847 | 0.3725 | 0.55289 | 0.43175 | 0.41698
42810.4371 | -253 | 18.5233 | 18.6295 | 18.6156 | 18.6091 | 17.9529 | 16.5996 | 14.6701 | 16.7208 | 17.2043 | 17.2965 | 17.3058 | 16.8503 | 15.8857 | 14.4881 | 14.9691 | 14.9819 | 15.5435 | 13.397 | 13.5075 | 14.0756 |  |  |  | 16.611 | 15.9423 | 15.0526 | 10.2153 | 9.5678 | 9.8343 | 17.2082 | 16.3626 | 15.1617 | 16.9038 | 16.1906 | 15.1858 | 10.7706 | 11.5245 |  | 12.0797 | 10.4659 | 10.2417 | 8.4682 |  | 6.4216 | 6.4487 | 5.9527 | 6.0844 | 6.2004 | 6.4593 | 6.9825 | 4.827 | 6.4063 | 4.922 | 6.6414 | 8.0921 | 42.228 | 46.4715 | 42.7001 | 15.3148 |  |  | 0.043587 | -0.16419 | -0.01392 | 0.13208 | -0.10366 | -0.015572 | 0.63796 | -0.30244 | -0.034818 | 0.11333 | -0.23338 | 8.8704 | 8.8714 | 2.0084 | 15.8543 | 16.7406 | 17.2691 | 17.5936 | 17.5476 | 16.525 | 14.8789 | 16.8543 | 17.1855 | 17.4873 | 17.5227 | 17.2625 | 16.4621 | 14.6885 | 6.5239 | 8.5384 | 5.7844 | 5.7419 | 5.9076 | 6.6646 | 7.6439 | 15.9401 | 15.573 | 15.4172 | 14.3446 | 14.2223 | 14.1615 |  |  |  | 10.6916 | 9.2723 | 9.0141 | 8.8964 | 0.10986 | -0.0037392 | 12.7578 |  |  | 10.6129 |  |  | 16.8933 | 16.0813 | 15.0628 | 16.3869 | 15.6675 | 14.7728 | 10.2858 | 10.5761 | 11.3137 | 11.2551 | 9.074 |  | 10.5622 | 8.3868 | 9.8844 | 9.2702 | 11.0266 | 12.1367 |  | 12.21 |  |  | 11.8397 | 12.5257 | 12.5614 | [6 empty] | 12.5079 |  |  | 11.2274 |  |  | 9.141 | 10.2898 | 11.8269 | 7.4545 | 9.1022 | 12.4562 | 7.7396 | 9.4348 | 12.2335 | 9.1856 | 10.4316 | 7.557 | 10.2402 | 8.1479 | 10.1419 | 7.7375 | 9.7004 | 13.12 | 10.5111 | 10.2446 | 11.365 | 8.0632 | 9.8013 | 12.6287 | 8.1201 | 10.2721 | 9.7897 | 9.8044 | 8.5998 | 10.1689 | -0.058948 | 20.9522 | 0.032643 | 0.046409 | -37.8659 | 3.1203 | 7.06 | 0.3 | 0.24475 | -0.47218 | -0.13748 | 0.4235 | -0.37519 | -0.14542 | 0.93076 | 0.4087 | 0.40546 | 0.41856 | 0.36321 | 0.55909 | 0.4324 | 0.4179
42810.4371 | -252 | 18.5273 | 18.6267 | 18.6095 | 18.6026 | 17.9499 | 16.5958 | 14.6654 | 16.7155 | 17.2 | 17.2979 | 17.3062 | 16.8476 | 15.88 | 14.4894 | 14.9553 | 14.9823 | 15.5268 | 13.3942 | 13.5032 | 14.0684 |  |  |  | 16.6029 | 15.9393 | 15.0511 | 10.2107 | 9.5607 | 9.8067 | 17.2108 | 16.3603 | 15.1664 | 16.9019 | 16.1899 | 15.1829 | 10.7692 | 11.4546 |  | 12.0755 | 10.4728 | 10.2373 | 8.4483 |  | 6.4276 | 6.4566 | 5.948 | 6.0801 | 6.1953 | 6.4516 | 6.9826 | 4.8309 | 6.4082 | 4.9195 | 6.6474 | 8.089 | 42.2361 | 46.4656 | 42.7039 | 15.3006 |  |  | -0.093093 | -0.21151 | 0.037992 | 0.044686 | -0.093804 | -0.071428 | 0.52231 | -0.27615 | -0.37654 | -0.34403 | -0.25246 | 8.8675 | 8.8689 | 2.0085 | 15.8655 | 16.7432 | 17.2684 | 17.5877 | 17.5596 | 16.532 | 14.8841 | 16.8567 | 17.1843 | 17.48 | 17.5293 | 17.2603 | 16.4695 | 14.6901 | 6.6501 | 8.5384 | 5.7524 | 5.7297 | 5.8794 | 6.6659 | 7.6341 | 15.9345 | 15.5643 | 15.4153 | 14.336 | 14.2239 | 14.1586 |  |  |  | 10.6826 | 9.2673 | 8.9996 | 8.8746 | -0.10632 | -0.10668 | 12.7521 |  |  | 10.6111 |  |  | 16.8871 | 16.0797 | 15.0642 | 16.3775 | 15.6665 | 14.7655 | 10.2876 | 10.576 | 11.3156 | 11.2473 | 9.0937 |  | 10.5642 | 8.4218 | 9.8879 | 9.2583 | 11.0233 | 12.1495 |  | 12.2264 |  |  | 11.8353 | 12.5237 | 12.5577 | [6 empty] | 12.4946 |  |  | 11.2234 |  |  | 9.1419 | 10.2979 | 11.8365 | 7.4524 | 9.1093 | 12.4653 | 7.7466 | 9.4435 | 12.23 | 9.1846 | 10.4321 | 7.5729 | 10.2648 | 8.147 | 10.144 | 7.7371 | 9.7011 | 13.1146 | 10.5075 | 10.2398 | 11.3624 | 8.0695 | 9.7954 | 12.6261 | 8.1192 | 10.273 | 9.7882 | 9.8022 | 8.6041 | 10.176 | 0.080687 | 20.9522 | 0.032936 | 0.047791 | -37.835 | 3.1205 | -5.03 | 0.35 | -0.35767 | -0.53592 | 0.22714 | 0.24634 | -0.3569 | -0.31144 | 0.84217 | 0.40822 | 0.40461 | 0.41879 | 0.34935 | 0.5615 | 0.43291 | 0.41821
42810.4371 | -251 | 18.521 | 18.6259 | 18.6119 | 18.6062 | 17.9488 | 16.5998 | 14.6664 | 16.7241 | 17.2028 | 17.2962 | 17.3041 | 16.8474 | 15.8795 | 14.4867 | 14.9576 | 14.987 | 15.5314 | 13.3929 | 13.5069 | 14.0712 |  |  |  | 16.6081 | 15.9456 | 15.0527 | 10.2118 | 9.5719 | 9.7898 | 17.2079 | 16.355 | 15.1652 | 16.9021 | 16.1818 | 15.18 | 10.7616 | 11.3879 |  | 12.0717 | 10.4756 | 10.2404 | 8.4512 |  | 6.4327 | 6.4569 | 5.9446 | 6.0727 | 6.1926 | 6.4396 | 7.0054 | 4.8428 | 6.4132 | 4.9356 | 6.6464 | 8.0872 | 42.242 | 46.4746 | 42.7095 | 15.2914 |  |  | 0.15464 | -0.080081 | 0.01828 | -0.17217 | -0.07212 | 0.10139 | 0.54202 | -0.17693 | -0.38938 | -0.20305 | -0.30352 | 8.8672 | 8.8685 | 2.0083 | 15.8548 | 16.736 | 17.27 | 17.5835 | 17.5563 | 16.5265 | 14.8788 | 16.8595 | 17.1822 | 17.4683 | 17.5186 | 17.2583 | 16.4645 | 14.6881 | 6.7349 | 8.5414 | 5.7977 | 5.7621 | 5.87 | 6.6747 | 7.6432 | 15.9301 | 15.5538 | 15.4174 | 14.3367 | 14.2267 | 14.1602 |  |  |  | 10.6822 | 9.2677 | 8.9878 | 8.8785 | 0.036517 | -0.11101 | 12.7593 |  |  | 10.606 |  |  | 16.8844 | 16.081 | 15.0594 | 16.3776 | 15.6649 | 14.7699 | 10.2945 | 10.5742 | 11.309 | 11.2418 | 9.0868 |  | 10.5559 | 8.511 | 9.8867 | 9.264 | 11.0225 | 12.1588 |  | 12.2247 |  |  | 11.823 | 12.5171 | 12.5658 | [6 empty] | 12.4866 |  |  | 11.2172 |  |  | 9.1339 | 10.2938 | 11.8279 | 7.4574 | 9.1039 | 12.4676 | 7.7556 | 9.4357 | 12.2253 | 9.1851 | 10.4317 | 7.5681 | 10.2779 | 8.1381 | 10.1442 | 7.7391 | 9.7023 | 13.1066 | 10.5028 | 10.2372 | 11.3609 | 8.0728 | 9.7919 | 12.619 | 8.1288 | 10.2726 | 9.7885 | 9.8051 | 8.5997 | 10.1739 | 0.026181 | 20.9523 | 0.032953 | 0.049456 | -37.8634 | 3.1204 | 0.23 | 0.36 | 0.46098 | -0.32977 | 0.15755 | -0.48352 | -0.31294 | 0.37105 | 0.8579 | 0.40814 | 0.40209 | 0.4186 | 0.34095 | 0.55753 | 0.43257 | 0.41809
42810.4371 | -250 | 18.5199 | 18.6251 | 18.6163 | 18.6073 | 17.9562 | 16.6016 | 14.6662 | 16.7218 | 17.202 | 17.2982 | 17.3074 | 16.8489 | 15.883 | 14.4925 | 14.9546 | 14.9815 | 15.5325 | 13.3919 | 13.5016 | 14.0724 |  |  |  | 16.6146 | 15.9427 | 15.0473 | 10.2093 | 9.5822 | 9.7824 | 17.2064 | 16.3556 | 15.1637 | 16.9045 | 16.1767 | 15.1872 | 10.7635 | 11.3379 |  | 12.0712 | 10.4809 | 10.2448 | 8.4419 |  | 6.425 | 6.4525 | 5.9396 | 6.0713 | 6.1807 | 6.4255 | 7.0383 | 4.8113 | 6.4055 | 4.9444 | 6.6478 | 8.0858 | 42.2545 | 46.489 | 42.7313 | 15.2832 |  |  | 0.21772 | -0.046569 | 0.12736 | 0.06177 | -0.093148 | -0.026088 | 0.40468 | -0.080988 | -0.2407 | -0.17473 | -0.48414 | 8.867 | 8.8683 | 2.0085 | 15.8562 | 16.7423 | 17.2774 | 17.5911 | 17.5554 | 16.5339 | 14.8853 | 16.8683 | 17.1868 | 17.484 | 17.5254 | 17.2659 | 16.4671 | 14.6866 | 6.7242 | 8.5445 | 5.8762 | 5.7908 | 5.8797 | 6.6753 | 7.6442 | 15.9349 | 15.5743 | 15.4281 | 14.3518 | 14.2384 | 14.1671 |  |  |  | 10.6871 | 9.2917 | 9.0003 | 8.922 | -0.049588 | -0.17613 | 12.7588 |  |  | 10.6065 |  |  | 16.8901 | 16.0801 | 15.056 | 16.3827 | 15.6633 | 14.7712 | 10.2985 | 10.5771 | 11.3054 | 11.2359 | 9.1158 |  | 10.5555 | 8.588 | 9.8797 | 9.2647 | 11.0193 | 12.163 |  | 12.2217 |  |  | 11.7975 | 12.5166 | 12.5747 | [6 empty] | 12.4974 |  |  | 11.2132 |  |  | 9.1268 | 10.288 | 11.8264 | 7.4709 | 9.107 | 12.4667 | 7.7517 | 9.4264 | 12.2171 | 9.1887 | 10.4277 | 7.5801 | 10.2826 | 8.1434 | 10.1456 | 7.751 | 9.702 | 13.1045 | 10.5022 | 10.2369 | 11.367 | 8.0811 | 9.7968 | 12.6222 | 8.1304 | 10.271 | 9.7974 | 9.8106 | 8.596 | 10.1723 | 0.076257 | 20.9515 | 0.032919 | 0.050187 | -37.8573 | 3.1204 | -1.4 | 0.33 | 0.54697 | -0.25147 | 0.41587 | 0.28962 | -0.35563 | -0.18821 | 0.74127 | 0.40732 | 0.39972 | 0.41848 | 0.34221 | 0.54893 | 0.43289 | 0.41704
42810.4372 | -249 | 18.5102 | 18.633 | 18.6107 | 18.6055 | 17.9588 | 16.5998 | 14.6722 | 16.717 | 17.2089 | 17.2969 | 17.3062 | 16.8477 | 15.884 | 14.4887 | 14.9566 | 14.9768 | 15.5408 | 13.396 | 13.5088 | 14.0707 |  |  |  | 16.6201 | 15.9435 | 15.0457 | 10.2084 | 9.5923 | 9.7662 | 17.205 | 16.3567 | 15.1543 | 16.8965 | 16.1919 | 15.1858 | 10.7668 | 11.3071 |  | 12.0734 | 10.4911 | 10.2472 | 8.4268 |  | 6.4237 | 6.4523 | 5.9378 | 6.0688 | 6.1764 | 6.4153 | 7.074 | 4.8076 | 6.4071 | 4.8813 | 6.6353 | 8.0875 | 42.2639 | 46.4923 | 42.751 | 15.2762 |  |  | 0.052787 | 0.022431 | -0.065176 | 0.030886 | 0.088876 | -0.21271 | 0.32714 | -0.16378 | 0.65621 | -0.58866 | -0.23994 | 8.8723 | 8.874 | 2.0087 | 15.857 | 16.748 | 17.2852 | 17.6008 | 17.5547 | 16.5366 | 14.8923 | 16.8643 | 17.1845 | 17.4858 | 17.5279 | 17.2665 | 16.4697 | 14.6889 | 6.6709 | 8.5249 | 5.839 | 5.8128 | 5.8769 | 6.6731 | 7.6364 | 15.9323 | 15.5688 | 15.4237 | 14.3444 | 14.2335 | 14.1671 |  |  |  | 10.6876 | 9.283 | 9.0084 | 8.9648 | 0.0083554 | -0.091817 | 12.7509 |  |  | 10.6035 |  |  | 16.8859 | 16.0772 | 15.0539 | 16.3791 | 15.6666 | 14.7725 | 10.2971 | 10.5744 | 11.299 | 11.2277 | 9.1101 |  | 10.5561 | 8.6437 | 9.8739 | 9.2613 | 11.0211 | 12.1645 |  | 12.2166 |  |  | 11.7874 | 12.5225 | 12.5575 | [6 empty] | 12.5062 |  |  | 11.2061 |  |  | 9.127 | 10.2856 | 11.8378 | 7.4842 | 9.1122 | 12.469 | 7.7498 | 9.4319 | 12.2068 | 9.1949 | 10.4294 | 7.5925 | 10.2974 | 8.1538 | 10.1517 | 7.7586 | 9.7053 | 13.1047 | 10.4924 | 10.2339 | 11.3663 | 8.0777 | 9.7904 | 12.623 | 8.1317 | 10.2818 | 9.8049 | 9.811 | 8.5961 | 10.1782 | 0.040049 | 20.9535 | 0.03246 | 0.049637 | -37.8523 | 3.1204 | 6.55 | 0.35 | 0.26931 | 0.17453 | -0.2975 | 0.20479 | 0.34738 | -0.5374 | 0.66647 | 0.4075 | 0.39798 | 0.41863 | 0.34787 | 0.55216 | 0.43342 | 0.41587
42810.4372 | -248 | 18.5206 | 18.6387 | 18.6174 | 18.6122 | 17.9568 | 16.6115 | 14.6669 | 16.7194 | 17.2117 | 17.3012 | 17.3097 | 16.849 | 15.8871 | 14.4926 | 14.9599 | 14.983 | 15.5383 | 13.3962 | 13.518 | 14.0746 |  |  |  | 16.6112 | 15.9449 | 15.0501 | 10.2055 | 9.6002 | 9.7416 | 17.2042 | 16.3525 | 15.1555 | 16.8869 | 16.174 | 15.1784 | 10.771 | 11.27 |  | 12.0745 | 10.5042 | 10.2532 | 8.4414 |  | 6.4345 | 6.4535 | 5.9484 | 6.0781 | 6.1809 | 6.4155 | 7.0759 | 4.7552 | 6.4095 | 4.8346 | 6.6458 | 8.0819 | 42.2517 | 46.495 | 42.7611 | 15.2615 |  |  | 0.14413 | -0.12674 | 0.05902 | 0.15245 | -0.073432 | -0.20614 | 0.43426 | -0.18613 | -0.73168 | -0.17892 | -0.38141 | 8.8688 | 8.8698 | 2.0081 | 15.8452 | 16.7358 | 17.2777 | 17.5911 | 17.5485 | 16.5328 | 14.8857 | 16.8524 | 17.1806 | 17.4754 | 17.5225 | 17.2622 | 16.4656 | 14.685 | 6.6804 | 8.4873 | 5.783 | 5.8222 | 5.8841 | 6.6668 | 7.6344 | 15.925 | 15.567 | 15.4194 | 14.3424 | 14.2233 | 14.1589 |  |  |  | 10.6789 | 9.2815 | 8.9857 | 8.9935 | 0.097297 | -0.026135 | 12.7491 |  |  | 10.6077 |  |  | 16.8834 | 16.0772 | 15.0481 | 16.3834 | 15.6646 | 14.7682 | 10.3071 | 10.568 | 11.2888 | 11.2174 | 9.1126 |  | 10.5553 | 8.6363 | 9.8726 | 9.2571 | 11.0131 | 12.1511 |  | 12.2202 |  |  | 11.7925 | 12.5216 | 12.5346 | [6 empty] | 12.5265 |  |  | 11.2117 |  |  | 9.1253 | 10.2827 | 11.8343 | 7.4872 | 9.1207 | 12.4756 | 7.744 | 9.432 | 12.2103 | 9.1922 | 10.4337 | 7.5986 | 10.3062 | 8.1615 | 10.1543 | 7.7651 | 9.7008 | 13.1006 | 10.4819 | 10.2351 | 11.3645 | 8.0734 | 9.7817 | 12.616 | 8.1357 | 10.2923 | 9.7986 | 9.8115 | 8.5939 | 10.1863 | -0.15486 | 20.9527 | 0.032477 | 0.048652 | -37.9679 | 3.1204 | 5.54 | 0.3 | 0.44499 | -0.41485 | 0.2831 | 0.45499 | -0.31576 | -0.52904 | 0.76786 | 0.4074 | 0.39815 | 0.41848 | 0.34608 | 0.55814 | 0.43316 | 0.41478
42810.4372 | -247 | 18.508 | 18.6275 | 18.5985 | 18.6015 | 17.9451 | 16.5909 | 14.6628 | 16.7064 | 17.1986 | 17.2886 | 17.2952 | 16.8369 | 15.8704 | 14.4755 | 14.9591 | 14.987 | 15.536 | 13.4004 | 13.5162 | 14.0813 |  |  |  | 16.6148 | 15.9482 | 15.0546 | 10.2023 | 9.6113 | 9.7206 | 17.1992 | 16.3521 | 15.1573 | 16.9013 | 16.1855 | 15.1827 | 10.7731 | 11.2451 |  | 12.075 | 10.5165 | 10.2624 | 8.5212 |  | 6.4395 | 6.4564 | 5.9456 | 6.0788 | 6.1819 | 6.408 | 7.0717 | 4.7081 | 6.4102 | 4.8517 | 6.6441 | 8.0778 | 42.2501 | 46.4972 | 42.7721 | 15.2455 |  |  | 0.071843 | -0.3127 | -0.046776 | -0.17413 | 0.080332 | 0.12965 | 0.5072 | 0.10366 | -0.49077 | -0.17745 | -0.45016 | 8.8686 | 8.8696 | 2.0087 | 15.8457 | 16.7352 | 17.2745 | 17.59 | 17.5522 | 16.5297 | 14.8839 | 16.8527 | 17.1819 | 17.4725 | 17.5202 | 17.2574 | 16.4675 | 14.6851 | 6.8389 | 8.4768 | 5.7076 | 5.7771 | 5.8962 | 6.6749 | 7.6398 | 15.9314 | 15.5728 | 15.4199 | 14.3415 | 14.2216 | 14.1627 |  |  |  | 10.6796 | 9.2788 | 8.9836 | 9.0224 | 0.10398 | 0.015457 | 12.7524 |  |  | 10.6035 |  |  | 16.879 | 16.0738 | 15.048 | 16.382 | 15.6646 | 14.7688 | 10.3122 | 10.5697 | 11.2752 | 11.2138 | 9.1046 |  | 10.5504 | 8.595 | 9.8819 | 9.2573 | 11.0159 | 12.1263 |  | 12.2182 |  |  | 11.8153 | 12.5227 | 12.5346 | [6 empty] | 12.5449 |  |  | 11.2212 |  |  | 9.1087 | 10.2739 | 11.8178 | 7.4935 | 9.117 | 12.48 | 7.7402 | 9.4351 | 12.2016 | 9.1877 | 10.4294 | 7.5993 | 10.3125 | 8.1574 | 10.1541 | 7.7642 | 9.6924 | 13.0962 | 10.4706 | 10.2213 | 11.3632 | 8.0722 | 9.7822 | 12.613 | 8.1334 | 10.2871 | 9.783 | 9.8095 | 8.6016 | 10.1896 | 0.0046102 | 20.9534 | 0.032862 | 0.048942 | -37.9463 | 3.1205 | 12.52 | 0.24 | 0.31416 | -0.65164 | -0.25203 | -0.48628 | 0.33025 | 0.41955 | 0.82983 | 0.40746 | 0.3996 | 0.41857 | 0.32942 | 0.56715 | 0.43101 | 0.414
42810.4372 | -246 | 18.5137 | 18.6279 | 18.6012 | 18.6095 | 17.953 | 16.599 | 14.6636 | 16.7123 | 17.21 | 17.2912 | 17.3058 | 16.8497 | 15.8821 | 14.4909 | 14.9529 | 14.9816 | 15.5376 | 13.3936 | 13.5075 | 14.0796 |  |  |  | 16.6154 | 15.9473 | 15.0543 | 10.1922 | 9.6105 | 9.6803 | 17.185 | 16.3481 | 15.1558 | 16.8952 | 16.1806 | 15.1696 | 10.7638 | 11.2446 |  | 12.0653 | 10.5217 | 10.2536 | 8.5526 |  | 6.4355 | 6.4515 | 5.9413 | 6.07 | 6.1824 | 6.4065 | 7.0423 | 4.6723 | 6.4014 | 4.7466 | 6.6409 | 8.0873 | 42.2474 | 46.5151 | 42.7973 | 15.2444 |  |  | 0.002191 | -0.13068 | 0.041936 | 0.071626 | 0.013964 | -0.047116 | 0.56568 | -0.023164 | -0.42343 | -0.19822 | -0.3218 | 8.8673 | 8.8684 | 2.0085 | 15.8516 | 16.7427 | 17.2766 | 17.5907 | 17.5516 | 16.5335 | 14.884 | 16.8563 | 17.1894 | 17.4763 | 17.5219 | 17.2611 | 16.469 | 14.69 | 6.9853 | 8.5005 | 5.6945 | 5.7407 | 5.8971 | 6.6827 | 7.6403 | 15.9249 | 15.5605 | 15.4133 | 14.3345 | 14.2294 | 14.157 |  |  |  | 10.6812 | 9.2734 | 8.9803 | 9.0427 | 0.07258 | -0.1861 | 12.7573 |  |  | 10.6129 |  |  | 16.8858 | 16.0793 | 15.0526 | 16.38 | 15.6719 | 14.7782 | 10.3123 | 10.5803 | 11.2755 | 11.2146 | 9.0812 |  | 10.5436 | 8.5549 | 9.863 | 9.2361 | 11.0123 | 12.0655 |  | 12.2136 |  |  | 11.8306 | 12.5276 | 12.5466 | [6 empty] | 12.5606 |  |  | 11.2247 |  |  | 9.1009 | 10.2716 | 11.8176 | 7.5038 | 9.125 | 12.4769 | 7.7354 | 9.4474 | 12.2088 | 9.1923 | 10.4323 | 7.6149 | 10.3174 | 8.1686 | 10.1677 | 7.7623 | 9.6779 | 13.0907 | 10.4629 | 10.2197 | 11.3552 | 8.0657 | 9.7735 | 12.6113 | 8.1254 | 10.2875 | 9.7771 | 9.8124 | 8.5981 | 10.1846 | 0.10611 | 20.9534 | 0.033298 | 0.049651 | -37.7938 | 3.1204 | 5.35 | 0.35 | 0.054859 | -0.42125 | 0.23863 | 0.31187 | 0.13769 | -0.25292 | 0.87637 | 0.40789 | 0.40009 | 0.41904 | 0.31406 | 0.56866 | 0.42983 | 0.41349
42810.4372 | -245 | 18.5142 | 18.6278 | 18.6128 | 18.6111 | 17.9562 | 16.6017 | 14.6734 | 16.7187 | 17.2038 | 17.3006 | 17.3051 | 16.8523 | 15.8854 | 14.4956 | 14.9399 | 14.9655 | 15.5256 | 13.3878 | 13.4964 | 14.0658 |  |  |  | 16.6029 | 15.9375 | 15.0384 | 10.1743 | 9.6026 | 9.6499 | 17.1948 | 16.3432 | 15.1544 | 16.8909 | 16.1777 | 15.1717 | 10.7685 | 11.2565 |  | 12.0696 | 10.5258 | 10.2456 | 8.5816 |  | 6.4262 | 6.4501 | 5.9348 | 6.0789 | 6.1867 | 6.412 | 7.0374 | 4.6399 | 6.3996 | 4.6631 | 6.6446 | 8.077 | 42.2349 | 46.5199 | 42.8133 | 15.2321 |  |  | 0.007447 | -0.17339 | -0.086204 | -0.011826 | 0.044848 | 0.10862 | 0.5118 | -0.088876 | -0.019445 | -0.32201 | -0.31664 | 8.8676 | 8.8687 | 2.0086 | 15.8472 | 16.7425 | 17.2649 | 17.59 | 17.5582 | 16.5418 | 14.8848 | 16.8636 | 17.1894 | 17.4794 | 17.5227 | 17.2682 | 16.4654 | 14.6912 | 6.9845 | 8.5129 | 5.7619 | 5.7178 | 5.8537 | 6.6846 | 7.6372 | 15.9229 | 15.5596 | 15.4029 | 14.3374 | 14.2231 | 14.1561 |  |  |  | 10.6698 | 9.2786 | 8.9839 | 9.0718 | 0.041177 | -0.07996 | 12.7526 |  |  | 10.6156 |  |  | 16.8841 | 16.0776 | 15.0497 | 16.3858 | 15.6672 | 14.7753 | 10.3143 | 10.5786 | 11.2635 | 11.2013 | 9.024 |  | 10.5468 | 8.5645 | 9.8706 | 9.2265 | 11.0175 | 12.0212 |  | 12.214 |  |  | 11.8241 | 12.5012 | 12.5332 | [6 empty] | 12.5716 |  |  | 11.227 |  |  | 9.0969 | 10.2675 | 11.8091 | 7.512 | 9.1331 | 12.4837 | 7.7422 | 9.4509 | 12.2139 | 9.1947 | 10.4279 | 7.6194 | 10.3171 | 8.1866 | 10.1684 | 7.7639 | 9.6751 | 13.0934 | 10.4571 | 10.2181 | 11.3533 | 8.0668 | 9.7715 | 12.5974 | 8.131 | 10.2965 | 9.7728 | 9.8034 | 8.5928 | 10.1816 | -0.002516 | 20.9534 | 0.033286 | 0.050563 | -37.8821 | 3.1204 | 13.76 | 0.26 | 0.10113 | -0.48523 | -0.34214 | -0.12672 | 0.24676 | 0.38403 | 0.83359 | 0.40958 | 0.40007 | 0.41948 | 0.31437 | 0.56082 | 0.42918 | 0.41231
42810.4372 | -244 | 18.5041 | 18.6235 | 18.6051 | 18.6052 | 17.9474 | 16.5984 | 14.6679 | 16.7157 | 17.1979 | 17.2967 | 17.3032 | 16.8415 | 15.8829 | 14.4865 | 14.9403 | 14.9641 | 15.5276 | 13.39 | 13.498 | 14.0736 |  |  |  | 16.6132 | 15.9384 | 15.0424 | 10.1808 | 9.6063 | 9.6982 | 17.1893 | 16.338 | 15.152 | 16.8878 | 16.1779 | 15.1678 | 10.7598 | 11.2775 |  | 12.0683 | 10.531 | 10.2484 | 8.6054 |  | 6.433 | 6.448 | 5.925 | 6.0755 | 6.2089 | 6.4649 | 7.0589 | 4.6738 | 6.4018 | 4.6568 | 6.649 | 8.0699 | 42.2335 | 46.5276 | 42.8307 | 15.2227 |  |  | 0.11127 | -0.16091 | 0.080704 | -0.012486 | 0.19533 | -0.003088 | 0.36197 | 0.005752 | -1.0119 | -0.25571 | -0.1849 | 8.8709 | 8.872 | 2.0083 | 15.8365 | 16.7293 | 17.2671 | 17.5906 | 17.5478 | 16.5324 | 14.8779 | 16.8487 | 17.1806 | 17.479 | 17.5269 | 17.2658 | 16.4645 | 14.6867 | 6.9001 | 8.4884 | 5.7855 | 5.7736 | 5.7958 | 6.6789 | 7.6328 | 15.9181 | 15.5556 | 15.4115 | 14.3436 | 14.2233 | 14.1585 |  |  |  | 10.6742 | 9.2756 | 8.9823 | 9.0868 | -0.014944 | -0.18291 | 12.7544 |  |  | 10.6146 |  |  | 16.8852 | 16.082 | 15.0539 | 16.3925 | 15.672 | 14.7769 | 10.3269 | 10.5839 | 11.2521 | 11.1828 | 8.9961 |  | 10.5563 | 8.5763 | 9.8792 | 9.229 | 11.0225 | 11.9761 |  | 12.2141 |  |  | 11.8263 | 12.5192 | 12.5309 | [6 empty] | 12.5457 |  |  | 11.2331 |  |  | 9.0862 | 10.2673 | 11.7916 | 7.5059 | 9.1309 | 12.4763 | 7.7405 | 9.4461 | 12.213 | 9.1825 | 10.4238 | 7.6345 | 10.3053 | 8.1863 | 10.173 | 7.7706 | 9.6691 | 13.0957 | 10.4476 | 10.214 | 11.3372 | 8.0657 | 9.7702 | 12.589 | 8.126 | 10.2999 | 9.7681 | 9.8003 | 8.5902 | 10.1701 | -0.1435 | 20.9521 | 0.033567 | 0.050881 | -37.9649 | 3.1204 | -6.98 | 0.43 | 0.39096 | -0.46743 | 0.33104 | -0.13021 | 0.51503 | -0.064757 | 0.70111 | 0.41067 | 0.40003 | 0.41957 | 0.32308 | 0.55768 | 0.42823 | 0.41204
42810.4372 | -243 | 18.501 | 18.6226 | 18.606 | 18.6031 | 17.952 | 16.601 | 14.6638 | 16.7139 | 17.2021 | 17.2898 | 17.3046 | 16.8474 | 15.8813 | 14.4857 | 14.9366 | 14.9579 | 15.5201 | 13.3911 | 13.4918 | 14.0705 |  |  |  | 16.6013 | 15.9422 | 15.0362 | 10.1727 | 9.6127 | 9.7256 | 17.1776 | 16.3334 | 15.1486 | 16.8864 | 16.1791 | 15.1706 | 10.7535 | 11.3069 |  | 12.0623 | 10.533 | 10.254 | 8.622 |  | 6.4297 | 6.4379 | 5.9299 | 6.0901 | 6.2379 | 6.5019 | 7.0908 | 4.7071 | 6.4104 | 4.6547 | 6.64 | 8.0723 | 42.2459 | 46.5307 | 42.8404 | 15.2233 |  |  | 0.007447 | -0.18325 | -0.092116 | -0.22671 | 0.13816 | -0.40393 | -0.28594 | 0.014948 | -0.079771 | -0.83413 | -0.27531 | 8.8707 | 8.8718 | 2.0082 | 15.8376 | 16.7369 | 17.2716 | 17.5938 | 17.5523 | 16.5349 | 14.8797 | 16.8511 | 17.1882 | 17.4809 | 17.5245 | 17.2605 | 16.4636 | 14.687 | 6.8343 | 8.4539 | 5.7642 | 5.8017 | 5.7894 | 6.6854 | 7.6364 | 15.9241 | 15.5517 | 15.4105 | 14.3454 | 14.2208 | 14.1576 |  |  |  | 10.6741 | 9.2745 | 8.9798 | 9.0763 | 0.041177 | -0.060764 | 12.7546 |  |  | 10.6163 |  |  | 16.8859 | 16.0812 | 15.0609 | 16.3867 | 15.6771 | 14.7786 | 10.3322 | 10.5862 | 11.2422 | 11.1783 | 8.9729 |  | 10.5448 | 8.5233 | 9.8727 | 9.2211 | 11.0174 | 11.9265 |  | 12.2142 |  |  | 11.8288 | 12.5132 | 12.5279 | [6 empty] | 12.5284 |  |  | 11.2344 |  |  | 9.0777 | 10.2615 | 11.798 | 7.5185 | 9.1459 | 12.4818 | 7.7446 | 9.4602 | 12.2206 | 9.1767 | 10.4308 | 7.6292 | 10.317 | 8.2068 | 10.1759 | 7.7737 | 9.6701 | 13.1104 | 10.4476 | 10.2128 | 11.3345 | 8.0642 | 9.7757 | 12.5991 | 8.1017 | 10.2977 | 9.7632 | 9.8004 | 8.6042 | 10.191 | -0.34804 | 20.9534 | 0.033849 | 0.050042 | -37.8927 | 3.1204 | -6.27 | 0.46 | 0.10115 | -0.49882 | -0.35367 | -0.55483 | 0.43318 | -0.74068 | -0.62318 | 0.41094 | 0.40129 | 0.41962 | 0.33116 | 0.56046 | 0.42756 | 0.41232
42810.4372 | -242 | 18.4999 | 18.6194 | 18.604 | 18.6029 | 17.95 | 16.5971 | 14.6615 | 16.7107 | 17.2012 | 17.2898 | 17.3032 | 16.8498 | 15.8797 | 14.4813 | 14.9348 | 14.9676 | 15.5182 | 13.3843 | 13.4971 | 14.0643 |  |  |  | 16.6045 | 15.941 | 15.0411 | 10.1756 | 9.6172 | 9.7646 | 17.1752 | 16.3288 | 15.1451 | 16.889 | 16.1714 | 15.1636 | 10.7525 | 11.3225 |  | 12.0566 | 10.5376 | 10.2532 | 8.6434 |  | 6.4269 | 6.4528 | 5.9295 | 6.0939 | 6.2393 | 6.5032 | 7.1032 | 4.6765 | 6.4142 | 4.6293 | 6.6502 | 8.0674 | 42.2458 | 46.5313 | 42.836 | 15.2014 |  |  | 0.13624 | 0.005343 | -0.14206 | -0.032198 | 0.1329 | -0.59712 | -0.006012 | -0.071788 | -0.31446 | -0.059336 | -0.28246 | 8.868 | 8.8688 | 2.0086 | 15.8271 | 16.7354 | 17.2733 | 17.5878 | 17.5508 | 16.5262 | 14.8806 | 16.854 | 17.1859 | 17.4801 | 17.5238 | 17.2579 | 16.4566 | 14.6877 | 6.78 | 8.3974 | 5.6807 | 5.7752 | 5.8424 | 6.6796 | 7.6298 | 15.9115 | 15.5466 | 15.4058 | 14.3375 | 14.2211 | 14.1481 |  |  |  | 10.6744 | 9.2641 | 8.97 | 9.0626 | -0.076939 | -0.077514 | 12.7482 |  |  | 10.6136 |  |  | 16.8872 | 16.079 | 15.06 | 16.3818 | 15.6726 | 14.7738 | 10.3354 | 10.5785 | 11.2302 | 11.1694 | 8.9992 |  | 10.5522 | 8.5112 | 9.8724 | 9.2341 | 11.0191 | 11.8799 |  | 12.2119 |  |  | 11.833 | 12.5161 | 12.5314 | [6 empty] | 12.54 |  |  | 11.2441 |  |  | 9.0672 | 10.2489 | 11.7896 | 7.5234 | 9.1485 | 12.4782 | 7.7343 | 9.4508 | 12.2377 | 9.1793 | 10.4245 | 7.6495 | 10.309 | 8.2057 | 10.18 | 7.7551 | 9.638 | 13.0931 | 10.4371 | 10.2027 | 11.3342 | 8.0563 | 9.7643 | 12.5952 | 8.0693 | 10.2879 | 9.7491 | 9.7915 | 8.5999 | 10.1926 | -0.17701 | 20.953 | 0.033183 | 0.049991 | -38.0306 | 3.1204 | 15.89 | 0.32 | 0.43266 | 0.085179 | -0.43921 | -0.2091 | 0.42485 | -0.90055 | -0.090362 | 0.41045 | 0.40161 | 0.41932 | 0.3365 | 0.56898 | 0.42693 | 0.41272
42810.4372 | -241 | 18.4962 | 18.6108 | 18.5987 | 18.5967 | 17.9455 | 16.5859 | 14.6549 | 16.7128 | 17.1992 | 17.2927 | 17.2926 | 16.8383 | 15.8731 | 14.4819 | 14.9405 | 14.9717 | 15.5245 | 13.3912 | 13.5087 | 14.0818 |  |  |  | 16.6124 | 15.9482 | 15.0487 | 10.1876 | 9.6285 | 9.7954 | 17.1756 | 16.3448 | 15.1468 | 16.8935 | 16.1772 | 15.1754 | 10.7588 | 11.3268 |  | 12.0642 | 10.556 | 10.2605 | 8.6733 |  | 6.4111 | 6.4275 | 5.9052 | 6.0538 | 6.2077 | 6.477 | 7.0504 | 4.6392 | 6.4146 | 4.6667 | 6.6494 | 8.064 | 42.2512 | 46.5369 | 42.8424 | 15.1957 |  |  | -0.003065 | -0.25816 | -0.053348 | -0.19582 | -0.052404 | -0.68189 | -0.1946 | -0.21833 | -0.88561 | -0.42774 | -0.31584 | 8.8696 | 8.8709 | 2.0085 | 15.8252 | 16.7354 | 17.2646 | 17.5944 | 17.5487 | 16.5242 | 14.8805 | 16.8546 | 17.1853 | 17.4819 | 17.5209 | 17.2511 | 16.4602 | 14.6942 | 6.7079 | 8.3835 | 5.602 | 5.7617 | 5.7993 | 6.6829 | 7.627 | 15.9158 | 15.5549 | 15.4126 | 14.3408 | 14.2201 | 14.1631 |  |  |  | 10.6764 | 9.269 | 8.9761 | 9.0763 | 0.0071398 | 0.044628 | 12.7458 |  |  | 10.6091 |  |  | 16.8905 | 16.0814 | 15.0569 | 16.38 | 15.6664 | 14.7655 | 10.3415 | 10.5741 | 11.2284 | 11.1575 | 9.0153 |  | 10.557 | 8.5804 | 9.8721 | 9.2422 | 11.021 | 11.8668 |  | 12.2175 |  |  | 11.8442 | 12.5155 | 12.5117 | [6 empty] | 12.5269 |  |  | 11.2564 |  |  | 9.0706 | 10.2585 | 11.7843 | 7.5341 | 9.1526 | 12.4856 | 7.7418 | 9.465 | 12.2435 | 9.1837 | 10.4243 | 7.6523 | 10.3167 | 8.2152 | 10.1702 | 7.7331 | 9.6182 | 13.0847 | 10.4303 | 10.1962 | 11.3353 | 8.0554 | 9.7632 | 12.5863 | 8.0405 | 10.2832 | 9.7304 | 9.7906 | 8.6024 | 10.1906 | -0.27736 | 20.953 | 0.032707 | 0.049217 | -37.9583 | 3.1204 | -1.07 | 0.29 | -0.064898 | -0.59205 | -0.26914 | -0.51564 | -0.26677 | -0.96231 | -0.51408 | 0.41016 | 0.39968 | 0.41916 | 0.3449 | 0.5774 | 0.42631 | 0.4124
42810.4373 | -240 | 18.5017 | 18.6163 | 18.6045 | 18.6018 | 17.9381 | 16.5972 | 14.6578 | 16.7128 | 17.1986 | 17.29 | 17.2975 | 16.8433 | 15.8807 | 14.4851 | 14.9361 | 14.9636 | 15.5233 | 13.3818 | 13.4986 | 14.0748 |  |  |  | 16.6081 | 15.9422 | 15.0474 | 10.1828 | 9.6203 | 9.8111 | 17.1796 | 16.3341 | 15.158 | 16.8917 | 16.1709 | 15.1772 | 10.7686 | 11.3183 |  | 12.0663 | 10.5689 | 10.2592 | 8.685 |  | 6.4133 | 6.4266 | 5.8951 | 6.037 | 6.2047 | 6.4717 | 7.0107 | 4.6686 | 6.4197 | 4.6719 | 6.6517 | 8.0694 | 42.262 | 46.5606 | 42.8414 | 15.1817 |  |  | 0.10142 | -0.21807 | -0.023776 | 0.034826 | -0.18711 | -0.11086 | 0.069556 | -0.23147 | -0.50225 | -0.31571 | -0.16861 | 8.8683 | 8.8692 | 2.0085 | 15.8318 | 16.7351 | 17.2751 | 17.5907 | 17.552 | 16.533 | 14.883 | 16.8564 | 17.1927 | 17.4801 | 17.5238 | 17.2605 | 16.462 | 14.6969 | 6.6358 | 8.3615 | 5.5291 | 5.7733 | 5.7526 | 6.6795 | 7.631 | 15.9028 | 15.5451 | 15.4078 | 14.3338 | 14.2179 | 14.1572 |  |  |  | 10.6769 | 9.2618 | 8.9651 | 9.067 | -0.092337 | -0.0235 | 12.7504 |  |  | 10.5979 |  |  | 16.8856 | 16.0807 | 15.0575 | 16.3815 | 15.6619 | 14.769 | 10.3461 | 10.5753 | 11.2273 | 11.1557 | 9.0168 |  | 10.57 | 8.6816 | 9.8844 | 9.2535 | 11.0246 | 11.8485 |  | 12.2174 |  |  | 11.8583 | 12.5334 | 12.5138 | [6 empty] | 12.5368 |  |  | 11.2671 |  |  | 9.0638 | 10.2389 | 11.7773 | 7.5335 | 9.1505 | 12.4782 | 7.7422 | 9.4602 | 12.2483 | 9.1704 | 10.4263 | 7.6559 | 10.3262 | 8.2208 | 10.1729 | 7.7315 | 9.6254 | 13.0918 | 10.4228 | 10.1982 | 11.336 | 8.0521 | 9.7647 | 12.5932 | 8.0167 | 10.303 | 9.7442 | 9.7999 | 8.6092 | 10.201 | -0.36769 | 20.9538 | 0.032282 | 0.048674 | -37.9826 | 3.1203 | 15.23 | 0.3 | 0.37332 | -0.54415 | -0.17967 | 0.21745 | -0.50408 | -0.388 | 0.30734 | 0.41055 | 0.39728 | 0.41896 | 0.35251 | 0.58596 | 0.42631 | 0.41268
42810.4373 | -239 | 18.4949 | 18.6227 | 18.6034 | 18.6103 | 17.9447 | 16.6001 | 14.6666 | 16.7186 | 17.2016 | 17.2979 | 17.3031 | 16.845 | 15.879 | 14.4944 | 14.9282 | 14.9599 | 15.5172 | 13.3843 | 13.4952 | 14.0701 |  |  |  | 16.6126 | 15.9428 | 15.0477 | 10.183 | 9.625 | 9.8179 | 17.1695 | 16.3334 | 15.1418 | 16.8777 | 16.1679 | 15.1685 | 10.755 | 11.286 |  | 12.0538 | 10.5641 | 10.2582 | 8.6767 |  | 6.4111 | 6.4315 | 5.9043 | 6.0453 | 6.2026 | 6.4569 | 6.9724 | 4.7215 | 6.4237 | 4.6682 | 6.6496 | 8.0578 | 42.266 | 46.5855 | 42.837 | 15.1721 |  |  | 0.1461 | -0.16616 | 0.15233 | -0.055854 | 0.076388 | -0.26265 | 0.21675 | -0.27878 | -0.49388 | -0.047587 | -0.2465 | 8.8682 | 8.8693 | 2.0082 | 15.8338 | 16.7314 | 17.2712 | 17.5859 | 17.5495 | 16.5315 | 14.8784 | 16.8516 | 17.1877 | 17.481 | 17.5163 | 17.2541 | 16.4587 | 14.6922 | 6.5673 | 8.3762 | 5.4659 | 5.7367 | 5.7443 | 6.6778 | 7.6328 | 15.9069 | 15.5453 | 15.4054 | 14.3352 | 14.2228 | 14.159 |  |  |  | 10.6763 | 9.2575 | 8.9597 | 9.0569 | -0.15048 | 0.092996 | 12.7579 |  |  | 10.5973 |  |  | 16.8875 | 16.0765 | 15.0554 | 16.3805 | 15.6625 | 14.7692 | 10.3588 | 10.5717 | 11.2204 | 11.1496 | 8.9876 |  | 10.5249 | 8.8018 | 9.8681 | 9.2333 | 11.022 | 11.8577 |  | 12.2175 |  |  | 11.8588 | 12.5524 | 12.5067 | [6 empty] | 12.5355 |  |  | 11.265 |  |  | 9.051 | 10.2378 | 11.7758 | 7.5377 | 9.1475 | 12.4756 | 7.7556 | 9.4589 | 12.2503 | 9.1698 | 10.427 | 7.6534 | 10.3288 | 8.2335 | 10.1834 | 7.7418 | 9.6316 | 13.0895 | 10.4147 | 10.1986 | 11.3333 | 8.05 | 9.7531 | 12.5972 | 8.0013 | 10.3037 | 9.7455 | 9.7999 | 8.6143 | 10.2021 | 0.11247 | 20.9549 | 0.031398 | 0.048602 | -38.0065 | 3.1203 | 0.39 | 0.27 | 0.44808 | -0.47499 | 0.4548 | -0.27539 | 0.32207 | -0.59721 | 0.54252 | 0.40987 | 0.3934 | 0.41944 | 0.35994 | 0.59319 | 0.42609 | 0.41294
42810.4373 | -238 | 18.4921 | 18.6176 | 18.6056 | 18.6089 | 17.9489 | 16.5971 | 14.6664 | 16.7152 | 17.2098 | 17.2936 | 17.3013 | 16.8401 | 15.8775 | 14.4892 | 14.9292 | 14.9597 | 15.5191 | 13.3822 | 13.5061 | 14.0671 |  |  |  | 16.6098 | 15.9436 | 15.052 | 10.1869 | 9.6359 | 9.8147 | 17.1801 | 16.3372 | 15.1476 | 16.8942 | 16.1806 | 15.1771 | 10.7621 | 11.3127 |  | 12.0637 | 10.5901 | 10.2562 | 8.6991 |  | 6.4079 | 6.4212 | 5.9006 | 6.0349 | 6.1938 | 6.4403 | 6.9367 | 4.7872 | 6.4205 | 4.7219 | 6.6472 | 8.0573 | 42.2776 | 46.5979 | 42.8376 | 15.1659 |  |  | 0.005475 | -0.078765 | 0.1037 | 0.16691 | 0.10333 | -0.18708 | 0.46908 | -0.20124 | -0.31173 | 1.4388 | -0.24391 | 8.8702 | 8.8711 | 2.0084 | 15.8298 | 16.7246 | 17.2656 | 17.5881 | 17.5396 | 16.5271 | 14.8791 | 16.8474 | 17.1839 | 17.477 | 17.5204 | 17.2542 | 16.4556 | 14.6885 | 6.5328 | 8.3916 | 5.4736 | 5.7338 | 5.732 | 6.6774 | 7.6313 | 15.9065 | 15.5472 | 15.415 | 14.3418 | 14.2199 | 14.1551 |  |  |  | 10.6739 | 9.258 | 8.9537 | 9.051 | -0.16041 | 0.06326 | 12.7596 |  |  | 10.6041 |  |  | 16.8852 | 16.0782 | 15.0527 | 16.3761 | 15.665 | 14.7664 | 10.3775 | 10.569 | 11.2153 | 11.149 | 8.9708 |  | 10.5205 | 8.8648 | 9.8661 | 9.2412 | 11.0213 | 11.837 |  | 12.2172 |  |  | 11.8432 | 12.5469 | 12.5343 | [6 empty] | 12.5228 |  |  | 11.2721 |  |  | 9.0461 | 10.2264 | 11.7585 | 7.5313 | 9.1394 | 12.4672 | 7.7502 | 9.4484 | 12.2532 | 9.1628 | 10.4265 | 7.6479 | 10.3386 | 8.2377 | 10.1871 | 7.7145 | 9.6398 | 13.091 | 10.4038 | 10.1942 | 11.3346 | 8.0569 | 9.7576 | 12.5937 | 7.9947 | 10.3084 | 9.7496 | 9.815 | 8.6157 | 10.1999 | 0.13346 | 20.9539 | 0.031645 | 0.049839 | -38.0144 | 3.1203 | -10.37 | 0.25 | 0.086741 | -0.32702 | 0.37524 | 0.47605 | 0.37458 | -0.50401 | 0.79809 | 0.41019 | 0.39158 | 0.4192 | 0.36371 | 0.59216 | 0.42571 | 0.41302
42810.4373 | -237 | 18.4878 | 18.6094 | 18.6057 | 18.6035 | 17.9446 | 16.588 | 14.6603 | 16.7111 | 17.1943 | 17.2883 | 17.2945 | 16.8415 | 15.8654 | 14.4793 | 14.9308 | 14.9629 | 15.5213 | 13.3794 | 13.5071 | 14.0672 |  |  |  | 16.6032 | 15.9385 | 15.05 | 10.1747 | 9.6324 | 9.7645 | 17.178 | 16.3345 | 15.1461 | 16.8919 | 16.1746 | 15.171 | 10.7557 | 11.3261 |  | 12.0627 | 10.5904 | 10.2474 | 8.6834 |  | 6.417 | 6.4231 | 5.9031 | 6.04 | 6.1943 | 6.4381 | 6.9129 | 4.787 | 6.4215 | 4.7836 | 6.6512 | 8.0598 | 42.2845 | 46.5946 | 42.846 | 15.1537 |  |  | 0.10404 | -0.23582 | 0.028792 | 0.16822 | -0.05372 | -0.44796 | 0.41586 | -0.1053 | -0.25102 | -1.3005 | -0.27531 | 8.8689 | 8.8701 | 2.0085 | 15.8269 | 16.7292 | 17.2658 | 17.5923 | 17.5524 | 16.5296 | 14.8709 | 16.8488 | 17.1841 | 17.4782 | 17.5226 | 17.2576 | 16.4599 | 14.6886 | 6.5221 | 8.4 | 5.5182 | 5.7275 | 5.7404 | 6.6777 | 7.6376 | 15.9036 | 15.5472 | 15.414 | 14.3412 | 14.223 | 14.1595 |  |  |  | 10.6712 | 9.2603 | 8.9416 | 9.0374 | -0.061744 | -0.052107 | 12.7616 |  |  | 10.6054 |  |  | 16.8777 | 16.0767 | 15.0523 | 16.3796 | 15.6694 | 14.7729 | 10.3842 | 10.5781 | 11.2135 | 11.1652 | 8.9392 |  | 10.5562 | 8.9307 | 9.877 | 9.2253 | 11.0144 | 11.8611 |  | 12.2102 |  |  | 11.8408 | 12.5346 | 12.5513 | [6 empty] | 12.5152 |  |  | 11.263 |  |  | 9.0387 | 10.2131 | 11.7387 | 7.5307 | 9.1397 | 12.4591 | 7.7477 | 9.4437 | 12.2521 | 9.1501 | 10.4269 | 7.6511 | 10.3505 | 8.2413 | 10.1989 | 7.7043 | 9.6487 | 13.0916 | 10.4026 | 10.1889 | 11.3467 | 8.0644 | 9.7606 | 12.5914 | 8.011 | 10.3102 | 9.7432 | 9.8207 | 8.616 | 10.2079 | 0.040819 | 20.9543 | 0.031892 | 0.049043 | -37.9892 | 3.1204 | 6.65 | 0.3 | 0.3781 | -0.56585 | 0.19772 | 0.47792 | -0.27008 | -0.77991 | 0.75145 | 0.41225 | 0.39011 | 0.41941 | 0.36495 | 0.58794 | 0.42593 | 0.41331
42810.4373 | -236 | 18.4873 | 18.6043 | 18.6001 | 18.5998 | 17.941 | 16.5855 | 14.66 | 16.7105 | 17.1923 | 17.2867 | 17.2992 | 16.8475 | 15.868 | 14.4819 | 14.9293 | 14.9623 | 15.5249 | 13.383 | 13.5042 | 14.066 |  |  |  | 16.6079 | 15.9405 | 15.0421 | 10.1699 | 9.6263 | 9.7349 | 17.1691 | 16.3316 | 15.1453 | 16.884 | 16.1662 | 15.1662 | 10.7502 | 11.3479 |  | 12.056 | 10.5948 | 10.2434 | 8.6374 |  | 6.4199 | 6.4295 | 5.9043 | 6.0357 | 6.1904 | 6.4266 | 6.873 | 4.7496 | 6.4295 | 4.8283 | 6.655 | 8.0572 | 42.2973 | 46.5912 | 42.8457 | 15.1451 |  |  | 0.028475 | -0.16485 | -0.1184 | 0.19779 | 0.089532 | -0.55046 | 0.47368 | -0.22556 | -0.069457 | -0.53768 | -0.19881 | 8.8686 | 8.8696 | 2.0086 | 15.8201 | 16.7203 | 17.2598 | 17.5925 | 17.5453 | 16.5314 | 14.8746 | 16.8486 | 17.1858 | 17.4733 | 17.5323 | 17.258 | 16.4613 | 14.6906 | 6.4848 | 8.4064 | 5.5393 | 5.7369 | 5.7649 | 6.6669 | 7.6361 | 15.9017 | 15.5401 | 15.3928 | 14.3367 | 14.2203 | 14.1469 |  |  |  | 10.6669 | 9.2518 | 8.9246 | 9.0357 | -0.052222 | -0.10292 | 12.7649 |  |  | 10.613 |  |  | 16.8836 | 16.0774 | 15.0524 | 16.3818 | 15.6704 | 14.7773 | 10.3844 | 10.5822 | 11.2203 | 11.1691 | 8.9244 |  | 10.5405 | 9.0283 | 9.8683 | 9.1768 | 10.9978 | 11.8496 |  | 12.203 |  |  | 11.8418 | 12.5199 | 12.5662 | [6 empty] | 12.523 |  |  | 11.2605 |  |  | 9.0402 | 10.2053 | 11.7323 | 7.5297 | 9.146 | 12.4586 | 7.7491 | 9.4528 | 12.2497 | 9.1484 | 10.4318 | 7.6581 | 10.3576 | 8.2527 | 10.2039 | 7.7048 | 9.6521 | 13.0875 | 10.394 | 10.1861 | 11.3563 | 8.0617 | 9.7632 | 12.5959 | 8.0148 | 10.3142 | 9.7424 | 9.8293 | 8.6185 | 10.2134 | 0.054686 | 20.9543 | 0.03289 | 0.048804 | -37.8758 | 3.1204 | 13.82 | 0.25 | 0.19779 | -0.47311 | -0.40095 | 0.51823 | 0.34866 | -0.86453 | 0.80197 | 0.41214 | 0.38711 | 0.42021 | 0.36784 | 0.58542 | 0.42703 | 0.41322
42810.4373 | -235 | 18.4891 | 18.6163 | 18.5994 | 18.6023 | 17.9485 | 16.5986 | 14.6614 | 16.7128 | 17.2003 | 17.2855 | 17.3028 | 16.8444 | 15.8739 | 14.4859 | 14.919 | 14.9528 | 15.5177 | 13.3792 | 13.4934 | 14.0616 |  |  |  | 16.6032 | 15.9381 | 15.0377 | 10.1647 | 9.6269 | 9.6979 | 17.1687 | 16.338 | 15.1411 | 16.881 | 16.1687 | 15.1625 | 10.7551 | 11.378 |  | 12.0598 | 10.606 | 10.2374 | 8.5739 |  | 6.4208 | 6.4214 | 5.8943 | 6.0319 | 6.1786 | 6.4131 | 6.8684 | 4.7414 | 6.4284 | 4.8602 | 6.6573 | 8.0558 | 42.3031 | 46.6069 | 42.8516 | 15.1329 |  |  | 0.098787 | -0.42113 | -0.19397 | 0.34499 | -0.002464 | -0.022144 | 0.40403 | -0.081648 | 0.61962 | -0.61153 | -0.32379 | 8.8694 | 8.8705 | 2.0085 | 15.8306 | 16.7301 | 17.2664 | 17.5915 | 17.5491 | 16.533 | 14.8658 | 16.8547 | 17.1924 | 17.4813 | 17.5228 | 17.2704 | 16.4663 | 14.6923 | 6.4832 | 8.4165 | 5.5498 | 5.7289 | 5.8338 | 6.6763 | 7.6428 | 15.9044 | 15.548 | 15.4029 | 14.3363 | 14.2163 | 14.1618 |  |  |  | 10.678 | 9.2491 | 8.9222 | 9.0596 | -0.080383 | -0.042132 | 12.7665 |  |  | 10.612 |  |  | 16.8912 | 16.0749 | 15.0542 | 16.3851 | 15.6714 | 14.7772 | 10.3924 | 10.5766 | 11.2163 | 11.1665 | 8.9061 |  | 10.5446 | 9.1026 | 9.8756 | 9.1852 | 11.0128 | 11.8472 |  | 12.2116 |  |  | 11.8147 | 12.5072 | 12.566 | [6 empty] | 12.5205 |  |  | 11.2525 |  |  | 9.0315 | 10.1961 | 11.7229 | 7.5355 | 9.1491 | 12.454 | 7.7534 | 9.4631 | 12.2542 | 9.1388 | 10.4315 | 7.657 | 10.3637 | 8.2593 | 10.2184 | 7.7056 | 9.6415 | 13.0892 | 10.393 | 10.1869 | 11.347 | 8.0666 | 9.7652 | 12.6077 | 8.0029 | 10.3188 | 9.7494 | 9.843 | 8.6177 | 10.2306 | -0.16314 | 20.9543 | 0.033252 | 0.04934 | -37.9049 | 3.1204 | -2.28 | 0.36 | 0.36838 | -0.75617 | -0.5132 | 0.68441 | -0.05784 | -0.17339 | 0.74065 | 0.41279 | 0.38529 | 0.42047 | 0.3691 | 0.58503 | 0.42895 | 0.41292
42810.4373 | -234 | 18.4942 | 18.6212 | 18.6033 | 18.6015 | 17.9521 | 16.6007 | 14.6626 | 16.7204 | 17.2042 | 17.2954 | 17.3048 | 16.849 | 15.8731 | 14.4919 | 14.9157 | 14.9512 | 15.5102 | 13.3761 | 13.486 | 14.0639 |  |  |  | 16.6034 | 15.9354 | 15.039 | 10.1566 | 9.6247 | 9.6672 | 17.1665 | 16.3304 | 15.1474 | 16.8825 | 16.1709 | 15.16 | 10.7556 | 11.3959 |  | 12.0601 | 10.6153 | 10.2388 | 8.5272 |  | 6.4113 | 6.4071 | 5.8876 | 6.0261 | 6.1646 | 6.398 | 6.8605 | 4.6969 | 6.432 | 4.7912 | 6.653 | 8.0597 | 42.2877 | 46.6313 | 42.8437 | 15.1313 |  |  | 0.092215 | -0.38761 | -0.007348 | 0.067682 | 0.029736 | -0.23834 | 0.498 | -0.34055 | -0.13815 | -0.38495 | -0.36492 | 8.8699 | 8.8709 | 2.0084 | 15.8192 | 16.7213 | 17.2626 | 17.5803 | 17.5466 | 16.5202 | 14.8646 | 16.8464 | 17.1838 | 17.4793 | 17.5206 | 17.257 | 16.4644 | 14.6872 | 6.4621 | 8.3907 | 5.5622 | 5.6798 | 5.8641 | 6.6657 | 7.6362 | 15.8944 | 15.5456 | 15.3913 | 14.3307 | 14.2084 | 14.1519 |  |  |  | 10.6576 | 9.2378 | 8.9184 | 9.0671 | -0.074305 | 0.071917 | 12.7614 |  |  | 10.6014 |  |  | 16.8852 | 16.0721 | 15.0467 | 16.3798 | 15.6625 | 14.7672 | 10.3943 | 10.5596 | 11.2058 | 11.1581 | 8.8676 |  | 10.5352 | 9.1446 | 9.8763 | 9.1524 | 11.0081 | 11.8392 |  | 12.2015 |  |  | 11.7631 | 12.5114 | 12.5695 | [6 empty] | 12.5129 |  |  | 11.2607 |  |  | 9.0267 | 10.1815 | 11.7161 | 7.5522 | 9.1522 | 12.4474 | 7.7569 | 9.4739 | 12.2702 | 9.1309 | 10.4391 | 7.661 | 10.3736 | 8.2705 | 10.2334 | 7.7009 | 9.6177 | 13.092 | 10.3857 | 10.1845 | 11.3427 | 8.0749 | 9.7567 | 12.6043 | 7.9927 | 10.3267 | 9.7544 | 9.8389 | 8.6032 | 10.2263 | 0.13924 | 20.9543 | 0.033315 | 0.051026 | -37.9447 | 3.1204 | -5.03 | 0.33 | 0.35589 | -0.72544 | -0.099882 | 0.30314 | 0.20093 | -0.56884 | 0.82226 | 0.41355 | 0.38415 | 0.42122 | 0.37022 | 0.58289 | 0.43027 | 0.41204
42810.4373 | -233 | 18.4886 | 18.6114 | 18.5969 | 18.597 | 17.9482 | 16.5886 | 14.6657 | 16.7159 | 17.204 | 17.2825 | 17.2972 | 16.8506 | 15.8767 | 14.4878 | 14.9146 | 14.9514 | 15.5125 | 13.3792 | 13.4881 | 14.0633 |  |  |  | 16.6051 | 15.935 | 15.047 | 10.1533 | 9.6191 | 9.6401 | 17.1714 | 16.3309 | 15.1358 | 16.8816 | 16.1747 | 15.1605 | 10.7598 | 11.429 |  | 12.0521 | 10.6308 | 10.2298 | 8.4854 |  | 6.4188 | 6.4182 | 5.8908 | 6.0212 | 6.1607 | 6.3879 | 6.8531 | 4.6889 | 6.44 | 4.7336 | 6.6644 | 8.0567 | 42.261 | 46.6568 | 42.8361 | 15.1136 |  |  | -0.002409 | -0.2345 | 0.11422 | 0.29833 | -0.1076 | -0.30405 | 0.55976 | -0.23804 | -0.39833 | 0.51971 | -0.1849 | 8.8695 | 8.8706 | 2.0083 | 15.8181 | 16.7142 | 17.2646 | 17.5839 | 17.5448 | 16.5215 | 14.8703 | 16.8462 | 17.1805 | 17.4792 | 17.5197 | 17.2541 | 16.4605 | 14.691 | 6.4616 | 8.4114 | 5.5556 | 5.6825 | 5.8504 | 6.677 | 7.642 | 15.8878 | 15.5419 | 15.3928 | 14.3282 | 14.212 | 14.1502 |  |  |  | 10.6572 | 9.2388 | 8.9098 | 9.0814 | -0.037635 | -0.12343 | 12.7594 |  |  | 10.6078 |  |  | 16.8815 | 16.0767 | 15.0465 | 16.3742 | 15.6667 | 14.7678 | 10.4046 | 10.5448 | 11.209 | 11.1587 | 8.8408 |  | 10.5444 | 9.2079 | 9.883 | 9.0878 | 11.0065 | 11.8494 |  | 12.2044 |  |  | 11.6853 | 12.4517 | 12.5339 | [6 empty] | 12.4787 |  |  | 11.2646 |  |  | 9.0006 | 10.1629 | 11.7025 | 7.5548 | 9.1386 | 12.4313 | 7.7503 | 9.4749 | 12.2634 | 9.1211 | 10.4362 | 7.6654 | 10.3778 | 8.2775 | 10.2277 | 7.7081 | 9.6162 | 13.0979 | 10.3801 | 10.1834 | 11.3452 | 8.0824 | 9.7556 | 12.6023 | 8.0026 | 10.3431 | 9.7569 | 9.846 | 8.6007 | 10.2286 | -0.15236 | 20.9556 | 0.034044 | 0.05146 | -37.9553 | 3.1204 | -9.47 | 0.35 | -0.05752 | -0.56427 | 0.3938 | 0.63644 | -0.38221 | -0.64248 | 0.87175 | 0.41459 | 0.38261 | 0.42297 | 0.37158 | 0.58429 | 0.43156 | 0.41163
42810.4373 | -232 | 18.4748 | 18.6035 | 18.6006 | 18.5921 | 17.9404 | 16.5856 | 14.6573 | 16.7122 | 17.2063 | 17.2843 | 17.2917 | 16.842 | 15.873 | 14.4839 | 14.9111 | 14.9494 | 15.5093 | 13.3747 | 13.4924 | 14.0587 |  |  |  | 16.595 | 15.9339 | 15.0423 | 10.1421 | 9.6168 | 9.6236 | 17.1652 | 16.3117 | 15.1323 | 16.8729 | 16.1674 | 15.1539 | 10.7467 | 11.4566 |  | 12.0497 | 10.6274 | 10.2127 | 8.4644 |  | 6.4143 | 6.4074 | 5.8764 | 6.0153 | 6.1536 | 6.3709 | 6.8298 | 4.6755 | 6.4272 | 4.6771 | 6.665 | 8.0554 | 42.2423 | 46.6931 | 42.8451 | 15.0951 |  |  | 0.015331 | -0.080081 | 0.28441 | 0.12354 | -0.1352 | 0.23479 | 0.57028 | -0.12962 | -0.13173 | -0.52656 | -0.42652 | 8.871 | 8.8723 | 2.0084 | 15.8132 | 16.7144 | 17.2672 | 17.5883 | 17.5438 | 16.5257 | 14.8728 | 16.8497 | 17.1831 | 17.4772 | 17.5183 | 17.2544 | 16.468 | 14.687 | 6.4568 | 8.3831 | 5.5606 | 5.7117 | 5.8216 | 6.6712 | 7.6428 | 15.8888 | 15.5373 | 15.3969 | 14.3215 | 14.2083 | 14.1525 |  |  |  | 10.6638 | 9.2401 | 8.9034 | 9.1133 | -0.12374 | -0.083724 | 12.7692 |  |  | 10.62 |  |  | 16.8872 | 16.0821 | 15.0535 | 16.3807 | 15.6735 | 14.7787 | 10.4171 | 10.5438 | 11.2208 | 11.1713 | 8.8343 |  | 10.5449 | 9.2096 | 9.8833 | 8.9974 | 11.008 | 11.8694 |  | 12.214 |  |  | 11.6444 | 12.3886 | 12.4964 | [6 empty] | 12.3952 |  |  | 11.2641 |  |  | 8.9978 | 10.1621 | 11.6921 | 7.5571 | 9.1429 | 12.4293 | 7.7545 | 9.4812 | 12.2674 | 9.1173 | 10.444 | 7.6718 | 10.381 | 8.2787 | 10.2447 | 7.7064 | 9.6179 | 13.1018 | 10.3851 | 10.178 | 11.3354 | 8.0757 | 9.7506 | 12.6022 | 8.0173 | 10.3389 | 9.7569 | 9.8485 | 8.5919 | 10.2347 | 0.027337 | 20.9563 | 0.033045 | 0.051164 | -38.0034 | 3.1203 | 3.22 | 0.35 | 0.1451 | -0.32974 | 0.62141 | 0.40955 | -0.42841 | 0.56456 | 0.87987 | 0.41479 | 0.38257 | 0.42553 | 0.37145 | 0.58384 | 0.43172 | 0.41096
42810.4374 | -231 | 18.4679 | 18.6079 | 18.5959 | 18.5942 | 17.9382 | 16.5852 | 14.6504 | 16.7012 | 17.1967 | 17.2816 | 17.2966 | 16.8396 | 15.8706 | 14.4836 | 14.913 | 14.947 | 15.5014 | 13.3719 | 13.4925 | 14.0556 |  |  |  | 16.6013 | 15.9314 | 15.0369 | 10.1402 | 9.6102 | 9.6344 | 17.1679 | 16.3305 | 15.1416 | 16.8873 | 16.1734 | 15.1691 | 10.7527 | 11.5052 |  | 12.0593 | 10.6502 | 10.2284 | 8.4495 |  | 6.4148 | 6.4016 | 5.881 | 6.0151 | 6.1526 | 6.3747 | 6.83 | 4.6938 | 6.4316 | 4.6506 | 6.6708 | 8.0586 | 42.2155 | 46.7297 | 42.8243 | 15.079 |  |  | 0.049503 | -0.19179 | 0.062304 | -0.046654 | -0.13257 | -0.27908 | 0.36394 | -0.23476 | -0.92336 | -0.30753 | -0.28643 | 8.8695 | 8.8708 | 2.0086 | 15.8114 | 16.722 | 17.2613 | 17.59 | 17.5448 | 16.5276 | 14.8837 | 16.852 | 17.1875 | 17.4817 | 17.5274 | 17.2645 | 16.469 | 14.6909 | 6.4243 | 8.3406 | 5.5021 | 5.6684 | 5.8118 | 6.658 | 7.6379 | 15.8831 | 15.5356 | 15.3938 | 14.3181 | 14.209 | 14.1485 |  |  |  | 10.6579 | 9.2311 | 8.9025 | 9.1017 | -0.079573 | -0.037803 | 12.775 |  |  | 10.62 |  |  | 16.8915 | 16.083 | 15.0582 | 16.3882 | 15.6709 | 14.7757 | 10.4193 | 10.5373 | 11.2236 | 11.1676 | 8.8398 |  | 10.5332 | 9.186 | 9.8774 | 8.9257 | 10.9989 | 11.8615 |  | 12.2016 |  |  | 11.6427 | 12.4039 | 12.4788 | [6 empty] | 12.3193 |  |  | 11.2709 |  |  | 9.0041 | 10.1615 | 11.6901 | 7.5675 | 9.1484 | 12.4312 | 7.7646 | 9.4969 | 12.2825 | 9.1119 | 10.4544 | 7.6812 | 10.392 | 8.2931 | 10.2673 | 7.7097 | 9.6095 | 13.0968 | 10.3789 | 10.1698 | 11.3291 | 8.0687 | 9.7376 | 12.5953 | 8.0402 | 10.3458 | 9.7644 | 9.836 | 8.5902 | 10.2407 | -0.18972 | 20.954 | 0.03374 | 0.050237 | -37.9689 | 3.1203 | 6.05 | 0.31 | 0.26074 | -0.51028 | 0.29084 | -0.25168 | -0.42423 | -0.61551 | 0.7029 | 0.41425 | 0.38303 | 0.42722 | 0.37352 | 0.58976 | 0.43233 | 0.41109
42810.4374 | -230 | 18.4727 | 18.6037 | 18.5939 | 18.595 | 17.9435 | 16.5824 | 14.6497 | 16.7089 | 17.2015 | 17.2876 | 17.2996 | 16.8376 | 15.8707 | 14.483 | 14.9094 | 14.9396 | 15.5052 | 13.3776 | 13.494 | 14.0661 |  |  |  | 16.5942 | 15.9497 | 15.0341 | 10.1447 | 9.6093 | 9.685 | 17.1664 | 16.3324 | 15.1429 | 16.8818 | 16.1684 | 15.1601 | 10.7446 | 11.5415 |  | 12.0526 | 10.6602 | 10.2137 | 8.4256 |  | 6.411 | 6.4006 | 5.8811 | 6.016 | 6.1448 | 6.3626 | 6.8188 | 4.7368 | 6.4307 | 4.6985 | 6.6661 | 8.0573 | 42.2012 | 46.7447 | 42.819 | 15.0667 |  |  | 0.21115 | -0.2345 | 0.09582 | 0.056514 | -0.10169 | -0.4795 | 0.5821 | -0.32938 | 0.4221 | -0.34131 | -0.33293 | 8.8692 | 8.8705 | 2.0084 | 15.82 | 16.7281 | 17.2555 | 17.5929 | 17.5496 | 16.5257 | 14.8782 | 16.8544 | 17.1851 | 17.4839 | 17.517 | 17.2578 | 16.4719 | 14.6865 | 6.3881 | 8.3144 | 5.4508 | 5.6194 | 5.8034 | 6.66 | 7.64 | 15.8763 | 15.5401 | 15.3944 | 14.3236 | 14.2109 | 14.1495 |  |  |  | 10.6506 | 9.2302 | 8.9035 | 9.0443 | -0.080991 | -0.1016 | 12.7755 |  |  | 10.6207 |  |  | 16.8912 | 16.074 | 15.0589 | 16.3836 | 15.6687 | 14.7723 | 10.4228 | 10.5205 | 11.2194 | 11.1623 | 8.8671 |  | 10.5345 | 9.1553 | 9.8883 | 8.8803 | 11.0048 | 11.8428 |  | 12.2111 |  |  | 11.6392 | 12.4081 | 12.4425 | [6 empty] | 12.3013 |  |  | 11.2536 |  |  | 9.0084 | 10.1581 | 11.6911 | 7.5641 | 9.1515 | 12.4229 | 7.7677 | 9.516 | 12.2968 | 9.1144 | 10.4523 | 7.6966 | 10.4006 | 8.3038 | 10.2827 | 7.7268 | 9.615 | 13.1024 | 10.3674 | 10.1599 | 11.3246 | 8.0652 | 9.7386 | 12.5866 | 8.0443 | 10.3597 | 9.7594 | 9.8345 | 8.5686 | 10.2409 | -0.077437 | 20.9571 | 0.033097 | 0.0507 | -37.9387 | 3.1203 | 8.58 | 0.29 | 0.53856 | -0.56425 | 0.36068 | 0.277 | -0.37154 | -0.80679 | 0.88893 | 0.41354 | 0.38425 | 0.42868 | 0.37777 | 0.5957 | 0.43272 | 0.41244
42810.4374 | -229 | 18.4764 | 18.6019 | 18.5972 | 18.5872 | 17.9447 | 16.584 | 14.6602 | 16.7086 | 17.1956 | 17.2898 | 17.2987 | 16.8405 | 15.8662 | 14.4831 | 14.913 | 14.9395 | 15.5074 | 13.3636 | 13.4899 | 14.0541 |  |  |  | 16.6049 | 15.9334 | 15.0339 | 10.1391 | 9.5977 | 9.7296 | 17.1647 | 16.3246 | 15.1383 | 16.8754 | 16.1562 | 15.1574 | 10.7464 | 11.5814 |  | 12.0482 | 10.6621 | 10.2138 | 8.4189 |  | 6.4214 | 6.4102 | 5.8836 | 6.0327 | 6.1398 | 6.362 | 6.8508 | 4.8211 | 6.4407 | 4.7305 | 6.6659 | 8.0532 | 42.193 | 46.7498 | 42.8091 | 15.0568 |  |  | 0.16384 | -0.24633 | -0.073716 | 0.18137 | 0.000164 | -0.02346 | 0.11424 | -0.21964 | 0.023367 | -0.61426 | -0.29617 | 8.8682 | 8.8691 | 2.0084 | 15.8106 | 16.7138 | 17.2634 | 17.5816 | 17.5412 | 16.5207 | 14.8693 | 16.8505 | 17.1837 | 17.478 | 17.5244 | 17.2591 | 16.4658 | 14.6889 | 6.3601 | 8.3049 | 5.4633 | 5.5961 | 5.7485 | 6.6634 | 7.6391 | 15.8739 | 15.5276 | 15.3858 | 14.3225 | 14.1978 | 14.148 |  |  |  | 10.6581 | 9.2273 | 8.901 | 8.9888 | 0.14187 | -0.084289 | 12.7723 |  |  | 10.6191 |  |  | 16.8862 | 16.0679 | 15.0505 | 16.3786 | 15.6608 | 14.7678 | 10.4271 | 10.4976 | 11.2201 | 11.1627 | 8.8775 |  | 10.5347 | 9.055 | 9.8906 | 8.8585 | 10.9893 | 11.8152 |  | 12.211 |  |  | 11.638 | 12.398 | 12.4235 | [6 empty] | 12.2081 |  |  | 11.2639 |  |  | 9.0052 | 10.1529 | 11.6817 | 7.5454 | 9.1473 | 12.4159 | 7.7765 | 9.5195 | 12.3065 | 9.1185 | 10.4533 | 7.6907 | 10.393 | 8.3068 | 10.2889 | 7.7352 | 9.6118 | 13.1152 | 10.3751 | 10.1669 | 11.3314 | 8.0731 | 9.7456 | 12.5729 | 8.0778 | 10.3606 | 9.7505 | 9.8358 | 8.5663 | 10.2429 | 0.036389 | 20.9546 | 0.03347 | 0.050483 | -37.8973 | 3.1204 | 11.81 | 0.3 | 0.47444 | -0.57831 | -0.31636 | 0.49623 | 0.014921 | -0.17846 | 0.3938 | 0.41325 | 0.38711 | 0.42877 | 0.38128 | 0.59422 | 0.43297 | 0.41423
42810.4374 | -228 | 18.4716 | 18.6046 | 18.5926 | 18.5851 | 17.9405 | 16.5867 | 14.6571 | 16.7071 | 17.1936 | 17.2894 | 17.2994 | 16.8369 | 15.8653 | 14.4743 | 14.9085 | 14.9376 | 15.5065 | 13.3732 | 13.4778 | 14.0525 |  |  |  | 16.5943 | 15.931 | 15.0365 | 10.1315 | 9.5975 | 9.7324 | 17.154 | 16.319 | 15.1339 | 16.8726 | 16.1502 | 15.1596 | 10.7411 | 11.6324 |  | 12.0438 | 10.6688 | 10.2101 | 8.4198 |  | 6.4244 | 6.4076 | 5.8757 | 6.0218 | 6.1376 | 6.3524 | 6.8746 | 4.8944 | 6.4353 | 4.7481 | 6.6743 | 8.0462 | 42.1764 | 46.7545 | 42.7929 | 15.0514 |  |  | -0.008325 | -0.042625 | 0.18913 | 0.027598 | -0.07606 | 0.059336 | -0.22812 | -0.28404 | -0.36311 | 0.0015058 | -0.32379 | 8.8702 | 8.8715 | 2.0081 | 15.8025 | 16.7111 | 17.2485 | 17.578 | 17.5356 | 16.516 | 14.8642 | 16.8479 | 17.1795 | 17.4714 | 17.5176 | 17.2593 | 16.4591 | 14.6823 | 6.3514 | 8.3199 | 5.4718 | 5.5732 | 5.7068 | 6.6651 | 7.6333 | 15.8819 | 15.528 | 15.3916 | 14.3187 | 14.2085 | 14.1523 |  |  |  | 10.6576 | 9.2185 | 8.8898 | 8.9554 | 0.091827 | -0.068292 | 12.7697 |  |  | 10.6148 |  |  | 16.8808 | 16.0682 | 15.047 | 16.3767 | 15.6593 | 14.7625 | 10.4201 | 10.4889 | 11.223 | 11.1688 | 8.8882 |  | 10.5298 | 8.9753 | 9.8881 | 8.8393 | 10.9863 | 11.7781 |  | 12.2009 |  |  | 11.5782 | 12.3826 | 12.3921 | [6 empty] | 12.1914 |  |  | 11.2565 |  |  | 8.9904 | 10.1421 | 11.6797 | 7.5401 | 9.1309 | 12.4119 | 7.7819 | 9.5343 | 12.3011 | 9.1056 | 10.4459 | 7.702 | 10.3958 | 8.2951 | 10.2714 | 7.7384 | 9.6195 | 13.1036 | 10.3739 | 10.1547 | 11.3409 | 8.0677 | 9.7304 | 12.5646 | 8.0723 | 10.3527 | 9.7428 | 9.8353 | 8.5494 | 10.2519 | 0.012892 | 20.9566 | 0.033074 | 0.049825 | -37.9294 | 3.1204 | 3.48 | 0.33 | -0.10695 | -0.24057 | 0.50673 | 0.19357 | -0.32132 | 0.2838 | -0.55647 | 0.41279 | 0.38924 | 0.4292 | 0.38244 | 0.5926 | 0.43277 | 0.41514
42810.4374 | -227 | 18.462 | 18.5986 | 18.5848 | 18.5893 | 17.9324 | 16.5804 | 14.6504 | 16.7011 | 17.1865 | 17.2844 | 17.2976 | 16.8321 | 15.8629 | 14.4684 | 14.9036 | 14.9405 | 15.5036 | 13.3751 | 13.4857 | 14.0588 |  |  |  | 16.6046 | 15.935 | 15.0382 | 10.1378 | 9.5879 | 9.7475 | 17.1579 | 16.319 | 15.1362 | 16.881 | 16.1604 | 15.1599 | 10.7403 | 11.7025 |  | 12.05 | 10.6759 | 10.2087 | 8.4306 |  | 6.4162 | 6.3998 | 5.8773 | 6.017 | 6.1266 | 6.3453 | 6.8464 | 4.852 | 6.4272 | 4.8123 | 6.6694 | 8.0441 | 42.1414 | 46.7504 | 42.7887 | 15.0411 |  |  | 0.035047 | -0.077453 | 0.092532 | 0.25956 | -0.052404 | -0.076028 | -0.1013 | -0.26301 | -0.29519 | -0.23284 | -0.28643 | 8.8685 | 8.8696 | 2.0087 | 15.805 | 16.7199 | 17.2629 | 17.5844 | 17.5501 | 16.5271 | 14.8745 | 16.8491 | 17.1803 | 17.4745 | 17.5283 | 17.2602 | 16.469 | 14.6925 | 6.3745 | 8.3507 | 5.5004 | 5.5743 | 5.6721 | 6.6613 | 7.6335 | 15.8879 | 15.5376 | 15.397 | 14.3233 | 14.2093 | 14.1474 |  |  |  | 10.66 | 9.205 | 8.8864 | 8.9224 | -0.066404 | -0.088617 | 12.7742 |  |  | 10.6159 |  |  | 16.88 | 16.0683 | 15.0444 | 16.3732 | 15.6615 | 14.7672 | 10.4092 | 10.4858 | 11.2218 | 11.1701 | 8.8861 |  | 10.5329 | 8.8954 | 9.879 | 8.8347 | 10.9852 | 11.7378 |  | 12.1924 |  |  | 11.6047 | 12.3996 | 12.3897 | [6 empty] | 12.2194 |  |  | 11.2621 |  |  | 8.9918 | 10.1357 | 11.6768 | 7.5419 | 9.1321 | 12.4052 | 7.7967 | 9.5269 | 12.3131 | 9.1089 | 10.4541 | 7.7057 | 10.3789 | 8.2977 | 10.2779 | 7.7531 | 9.6122 | 13.0935 | 10.3638 | 10.1454 | 11.3487 | 8.0776 | 9.7455 | 12.5719 | 8.0587 | 10.3632 | 9.7344 | 9.8262 | 8.5433 | 10.2498 | -0.015805 | 20.9557 | 0.032827 | 0.049152 | -37.9292 | 3.1204 | -1.59 | 0.25 | 0.21944 | -0.32428 | 0.35444 | 0.59363 | -0.26671 | -0.32125 | -0.37081 | 0.41296 | 0.39116 | 0.4293 | 0.37943 | 0.58944 | 0.43245 | 0.41613
42810.4374 | -226 | 18.4732 | 18.603 | 18.5895 | 18.6003 | 17.9339 | 16.5822 | 14.6596 | 16.7069 | 17.1914 | 17.2859 | 17.2947 | 16.8465 | 15.8707 | 14.487 | 14.9103 | 14.9508 | 15.5115 | 13.3862 | 13.495 | 14.0642 |  |  |  | 16.6106 | 15.9445 | 15.0355 | 10.1463 | 9.5784 | 9.7728 | 17.1592 | 16.3232 | 15.1379 | 16.8861 | 16.1679 | 15.1695 | 10.7488 | 11.7579 |  | 12.0426 | 10.6893 | 10.2275 | 8.4601 |  | 6.4175 | 6.4032 | 5.8804 | 6.0138 | 6.1115 | 6.3296 | 6.8138 | 4.7639 | 6.4276 | 4.906 | 6.6684 | 8.0519 | 42.1251 | 46.7582 | 42.7809 | 15.0319 |  |  | 0.093531 | -0.23187 | 0.15562 | 0.092654 | -0.15163 | -0.54521 | 0.20755 | -0.44174 | -0.075295 | -0.33103 | -0.41797 | 8.8697 | 8.8708 | 2.0085 | 15.7975 | 16.7131 | 17.26 | 17.5817 | 17.5441 | 16.5155 | 14.8764 | 16.8486 | 17.184 | 17.4741 | 17.5196 | 17.2612 | 16.4657 | 14.6898 | 6.3692 | 8.3606 | 5.5434 | 5.5597 | 5.6782 | 6.6643 | 7.6286 | 15.884 | 15.5402 | 15.3948 | 14.3241 | 14.2009 | 14.1468 |  |  |  | 10.6579 | 9.19 | 8.8762 | 8.8912 | -0.14299 | -0.13077 | 12.7747 |  |  | 10.6189 |  |  | 16.8811 | 16.0689 | 15.0465 | 16.3731 | 15.6598 | 14.7687 | 10.3956 | 10.4708 | 11.2161 | 11.1654 | 8.8915 |  | 10.5377 | 8.7969 | 9.8971 | 8.8899 | 10.9879 | 11.7058 |  | 12.2021 |  |  | 11.6237 | 12.4169 | 12.4052 | [6 empty] | 12.2505 |  |  | 11.2762 |  |  | 8.9916 | 10.1338 | 11.6881 | 7.5504 | 9.1455 | 12.3996 | 7.8034 | 9.5292 | 12.3205 | 9.1165 | 10.4388 | 7.7183 | 10.3725 | 8.2984 | 10.29 | 7.7462 | 9.6143 | 13.1012 | 10.3575 | 10.1446 | 11.3476 | 8.08 | 9.7505 | 12.5773 | 8.0634 | 10.3649 | 9.731 | 9.8265 | 8.5439 | 10.2535 | -0.058948 | 20.9562 | 0.03161 | 0.04892 | -37.8752 | 3.1203 | 0.41 | 0.35 | 0.35849 | -0.56108 | 0.45965 | 0.35468 | -0.45366 | -0.86025 | 0.53076 | 0.41297 | 0.39449 | 0.42785 | 0.38038 | 0.58409 | 0.4319 | 0.41693
42810.4374 | -225 | 18.4792 | 18.5903 | 18.5905 | 18.5955 | 17.9452 | 16.5925 | 14.6614 | 16.714 | 17.1967 | 17.2889 | 17.2981 | 16.8476 | 15.867 | 14.4904 | 14.9149 | 14.9451 | 15.5122 | 13.3781 | 13.4918 | 14.0637 |  |  |  | 16.6078 | 15.9389 | 15.04 | 10.1486 | 9.5786 | 9.7933 | 17.161 | 16.3265 | 15.1343 | 16.8787 | 16.1679 | 15.1585 | 10.7502 | 11.7669 |  | 12.0462 | 10.6827 | 10.2191 | 8.447 |  | 6.4123 | 6.3949 | 5.8735 | 6.0129 | 6.097 | 6.3154 | 6.7875 | 4.6965 | 6.4331 | 4.9787 | 6.677 | 8.0492 | 42.112 | 46.7666 | 42.7735 | 15.0295 |  |  | 0.002191 | 0.23468 | 0.16679 | -0.000658 | -0.022176 | -0.013604 | 0.54399 | -0.39509 | 0.11386 | -0.33648 | -0.43427 | 8.8686 | 8.8697 | 2.0084 | 15.7964 | 16.7125 | 17.2543 | 17.58 | 17.5386 | 16.5159 | 14.8756 | 16.8462 | 17.1837 | 17.4751 | 17.5187 | 17.2607 | 16.4649 | 14.6877 | 6.3059 | 8.3593 | 5.5941 | 5.5565 | 5.6969 | 6.6559 | 7.63 | 15.8754 | 15.532 | 15.3929 | 14.3291 | 14.21 | 14.1537 |  |  |  | 10.6601 | 9.1759 | 8.8757 | 8.8825 | 0.016459 | -0.052671 | 12.7693 |  |  | 10.6105 |  |  | 16.8784 | 16.0682 | 15.0528 | 16.3746 | 15.6564 | 14.7675 | 10.3836 | 10.4593 | 11.2159 | 11.1644 | 8.891 |  | 10.5401 | 8.7097 | 9.8934 | 8.9378 | 10.9893 | 11.6882 |  | 12.1978 |  |  | 11.6416 | 12.406 | 12.3955 | [6 empty] | 12.2625 |  |  | 11.2786 |  |  | 8.9837 | 10.1158 | 11.6899 | 7.5522 | 9.1409 | 12.3789 | 7.7965 | 9.5259 | 12.3189 | 9.1104 | 10.4266 | 7.7265 | 10.3641 | 8.3049 | 10.2899 | 7.7392 | 9.6149 | 13.1028 | 10.3528 | 10.1415 | 11.341 | 8.0734 | 9.7419 | 12.5864 | 8.0657 | 10.3632 | 9.7239 | 9.8231 | 8.5356 | 10.2499 | 0.080109 | 20.9572 | 0.032075 | 0.049499 | -37.7779 | 3.1203 | 6.54 | 0.28 | 0.05487 | 0.56446 | 0.47586 | -0.029889 | -0.17349 | -0.13588 | 0.85927 | 0.41306 | 0.39679 | 0.42657 | 0.38643 | 0.57862 | 0.43232 | 0.41725
42810.4374 | -224 | 18.4712 | 18.6065 | 18.6013 | 18.6019 | 17.9457 | 16.5924 | 14.6644 | 16.7123 | 17.205 | 17.2938 | 17.3007 | 16.8463 | 15.8703 | 14.4928 | 14.9077 | 14.9447 | 15.5132 | 13.3781 | 13.494 | 14.0604 |  |  |  | 16.6079 | 15.9423 | 15.0423 | 10.1526 | 9.5739 | 9.8088 | 17.1544 | 16.3164 | 15.1334 | 16.8733 | 16.1567 | 15.1609 | 10.7473 | 11.7362 |  | 12.0511 | 10.689 | 10.216 | 8.4642 |  | 6.4091 | 6.3976 | 5.8818 | 6.0066 | 6.0887 | 6.2996 | 6.7585 | 4.673 | 6.437 | 5.0598 | 6.6784 | 8.041 | 42.1007 | 46.7594 | 42.7691 | 15.0143 |  |  | 0.044903 | -0.087309 | 0.10896 | -0.035486 | 0.029736 | -0.44007 | 0.17864 | -0.2157 | -0.85408 | -0.02346 | -0.34346 | 8.8672 | 8.8683 | 2.0082 | 15.7959 | 16.717 | 17.2545 | 17.584 | 17.5455 | 16.5311 | 14.8847 | 16.8521 | 17.1873 | 17.4804 | 17.5318 | 17.265 | 16.4713 | 14.6924 | 6.2503 | 8.3588 | 5.587 | 5.5751 | 5.7145 | 6.6615 | 7.6338 | 15.8732 | 15.5287 | 15.3955 | 14.3268 | 14.2081 | 14.1465 |  |  |  | 10.6633 | 9.1774 | 8.8749 | 8.8932 | -0.094363 | -0.035357 | 12.7602 |  |  | 10.5991 |  |  | 16.8751 | 16.0624 | 15.0449 | 16.3675 | 15.6532 | 14.7676 | 10.3734 | 10.4427 | 11.2181 | 11.1628 | 8.9084 |  | 10.5346 | 8.6275 | 9.885 | 8.9548 | 10.9802 | 11.6605 |  | 12.1947 |  |  | 11.6415 | 12.4037 | 12.4081 | [6 empty] | 12.2633 |  |  | 11.285 |  |  | 8.9992 | 10.1214 | 11.6978 | 7.5586 | 9.1524 | 12.381 | 7.8121 | 9.5299 | 12.3253 | 9.1139 | 10.4363 | 7.7421 | 10.373 | 8.3279 | 10.296 | 7.7362 | 9.62 | 13.1012 | 10.3524 | 10.136 | 11.3355 | 8.078 | 9.7337 | 12.5855 | 8.0726 | 10.3752 | 9.7297 | 9.8212 | 8.5445 | 10.2539 | 0.12325 | 20.9572 | 0.03347 | 0.050165 | -37.7746 | 3.1203 | -3.55 | 0.23 | 0.24841 | -0.34429 | 0.38462 | -0.21949 | 0.20089 | -0.77282 | 0.49238 | 0.41239 | 0.3988 | 0.42579 | 0.39325 | 0.57985 | 0.43174 | 0.41706
42810.4375 | -223 | 18.4749 | 18.605 | 18.5986 | 18.6036 | 17.9461 | 16.5933 | 14.6625 | 16.7154 | 17.2049 | 17.2927 | 17.3078 | 16.8478 | 15.8745 | 14.4984 | 14.9035 | 14.9411 | 15.5084 | 13.3793 | 13.4974 | 14.0638 |  |  |  | 16.6075 | 15.9401 | 15.0415 | 10.1506 | 9.5699 | 9.7975 | 17.1587 | 16.3136 | 15.1385 | 16.8808 | 16.1632 | 15.1591 | 10.7536 | 11.6863 |  | 12.0458 | 10.7049 | 10.2222 | 8.4843 |  | 6.4043 | 6.4164 | 5.8843 | 6.0091 | 6.0956 | 6.2889 | 6.7403 | 4.5959 | 6.4369 | 5.1196 | 6.6842 | 8.046 | 42.0946 | 46.768 | 42.7678 | 15.0094 |  |  | 0.049503 | -0.012397 | 0.01828 | 0.05717 | -0.1076 | -0.43284 | 0.32517 | -0.29192 | -0.53805 | 0.97938 | -0.36035 | 8.8695 | 8.8704 | 2.0083 | 15.7998 | 16.7223 | 17.2596 | 17.5847 | 17.5492 | 16.532 | 14.8776 | 16.8532 | 17.1928 | 17.4842 | 17.5354 | 17.2677 | 16.4725 | 14.6922 | 6.1854 | 8.3638 | 5.5843 | 5.5985 | 5.7255 | 6.649 | 7.6214 | 15.8642 | 15.528 | 15.3922 | 14.315 | 14.2049 | 14.138 |  |  |  | 10.6556 | 9.1692 | 8.8683 | 8.8938 | -0.072279 | -0.14639 | 12.7698 |  |  | 10.6004 |  |  | 16.883 | 16.0715 | 15.0489 | 16.374 | 15.6666 | 14.7762 | 10.371 | 10.437 | 11.2243 | 11.1711 | 8.9468 |  | 10.5352 | 8.5003 | 9.8841 | 8.913 | 10.977 | 11.6781 |  | 12.1968 |  |  | 11.6252 | 12.4155 | 12.4192 | [6 empty] | 12.2875 |  |  | 11.2757 |  |  | 8.9883 | 10.1047 | 11.6899 | 7.5668 | 9.1535 | 12.37 | 7.8123 | 9.5082 | 12.3172 | 9.1098 | 10.4285 | 7.7339 | 10.3655 | 8.3203 | 10.2914 | 7.7493 | 9.6364 | 13.1085 | 10.3631 | 10.1452 | 11.3223 | 8.0888 | 9.7286 | 12.596 | 8.085 | 10.3855 | 9.7363 | 9.8268 | 8.5573 | 10.2656 | 0.043323 | 20.9573 | 0.033585 | 0.050852 | -37.7722 | 3.1203 | -4.23 | 0.29 | 0.26082 | -0.12974 | 0.15754 | 0.27861 | -0.38214 | -0.76643 | 0.6643 | 0.41135 | 0.4023 | 0.42685 | 0.39901 | 0.57871 | 0.43139 | 0.41679
42810.4375 | -222 | 18.4772 | 18.6005 | 18.5927 | 18.6004 | 17.9421 | 16.587 | 14.6579 | 16.7069 | 17.1938 | 17.2925 | 17.3004 | 16.8366 | 15.8735 | 14.4851 | 14.9049 | 14.9387 | 15.5083 | 13.376 | 13.501 | 14.0562 |  |  |  | 16.6073 | 15.9359 | 15.0433 | 10.1444 | 9.5607 | 9.7835 | 17.1616 | 16.3215 | 15.1377 | 16.8801 | 16.1599 | 15.1624 | 10.7531 | 11.6314 |  | 12.0477 | 10.7136 | 10.2384 | 8.4912 |  | 6.3913 | 6.4049 | 5.8796 | 5.9921 | 6.0673 | 6.2646 | 6.7079 | 4.5207 | 6.4313 | 5.0935 | 6.6773 | 8.0464 | 42.0763 | 46.7656 | 42.7767 | 15.0065 |  |  | 0.16647 | 0.29579 | -0.004064 | 0.014458 | -0.046492 | -0.4197 | -0.26886 | -0.067848 | -0.40864 | -0.40152 | -0.2767 | 8.8693 | 8.8706 | 2.0086 | 15.7913 | 16.7177 | 17.2528 | 17.5805 | 17.5393 | 16.5137 | 14.8762 | 16.8596 | 17.1841 | 17.4781 | 17.5255 | 17.2595 | 16.4659 | 14.6872 | 6.1259 | 8.3829 | 5.595 | 5.744 | 5.7145 | 6.6501 | 7.6322 | 15.8694 | 15.5298 | 15.3945 | 14.3237 | 14.2088 | 14.1512 |  |  |  | 10.6589 | 9.1716 | 8.8708 | 8.9197 | 0.077847 | -0.069421 | 12.7685 |  |  | 10.6028 |  |  | 16.8861 | 16.0727 | 15.0493 | 16.383 | 15.6712 | 14.7733 | 10.3605 | 10.432 | 11.2295 | 11.1788 | 8.9973 |  | 10.5347 | 8.3941 | 9.8868 | 8.8535 | 10.9868 | 11.6948 |  | 12.1923 |  |  | 11.6456 | 12.4335 | 12.4213 | [6 empty] | 12.3003 |  |  | 11.2698 |  |  | 8.9869 | 10.0999 | 11.6987 | 7.5812 | 9.155 | 12.363 | 7.8151 | 9.5048 | 12.3039 | 9.1124 | 10.4183 | 7.7366 | 10.3573 | 8.3143 | 10.3051 | 7.7505 | 9.6396 | 13.1034 | 10.3657 | 10.1422 | 11.3128 | 8.0912 | 9.7267 | 12.6029 | 8.0979 | 10.3877 | 9.7394 | 9.8252 | 8.5598 | 10.2678 | 0.16659 | 20.9581 | 0.034044 | 0.050027 | -37.7707 | 3.1203 | 0.21 | 0.26 | 0.47828 | 0.63371 | -0.074281 | 0.14011 | -0.25118 | -0.75468 | -0.60402 | 0.40993 | 0.40534 | 0.42882 | 0.40576 | 0.57878 | 0.43118 | 0.41617
42810.4375 | -221 | 18.4684 | 18.5952 | 18.5953 | 18.5991 | 17.9448 | 16.5866 | 14.6501 | 16.7112 | 17.1965 | 17.2879 | 17.2988 | 16.8385 | 15.8748 | 14.4866 | 14.9042 | 14.9336 | 15.5067 | 13.3699 | 13.4876 | 14.0521 |  |  |  | 16.6038 | 15.9329 | 15.042 | 10.1375 | 9.5506 | 9.7691 | 17.1559 | 16.3227 | 15.1321 | 16.8769 | 16.161 | 15.1612 | 10.7504 | 11.5788 |  | 12.0447 | 10.7137 | 10.2503 | 8.521 |  | 6.3993 | 6.4114 | 5.875 | 5.98 | 6.055 | 6.2592 | 6.6857 | 4.4504 | 6.4367 | 5.0202 | 6.6899 | 8.0453 | 42.0601 | 46.786 | 42.779 | 14.9974 |  |  | -0.092433 | -0.036053 | 0.16482 | 0.047314 | 0.05142 | -0.24096 | 0.13067 | -0.06916 | -0.9292 | 0.0015058 | -0.12747 | 8.8699 | 8.8709 | 2.0084 | 15.7869 | 16.7031 | 17.2535 | 17.5674 | 17.5379 | 16.5154 | 14.8652 | 16.8484 | 17.1791 | 17.4715 | 17.5256 | 17.2571 | 16.4568 | 14.6809 | 6.1401 | 8.3519 | 5.5526 | 5.8315 | 5.719 | 6.6511 | 7.6297 | 15.8605 | 15.5203 | 15.3902 | 14.3163 | 14.2016 | 14.1395 |  |  |  | 10.6564 | 9.166 | 8.8714 | 8.9208 | 0.14855 | -0.096145 | 12.7622 |  |  | 10.6059 |  |  | 16.8881 | 16.0756 | 15.052 | 16.3828 | 15.6686 | 14.7671 | 10.3514 | 10.4311 | 11.2362 | 11.1922 | 9.0518 |  | 10.5348 | 8.3152 | 9.8979 | 8.8223 | 10.9826 | 11.6966 |  | 12.2026 |  |  | 11.66 | 12.4376 | 12.4316 | [6 empty] | 12.2865 |  |  | 11.2598 |  |  | 8.9879 | 10.0955 | 11.7018 | 7.5978 | 9.1569 | 12.3666 | 7.8175 | 9.5032 | 12.2836 | 9.1154 | 10.4071 | 7.7389 | 10.3533 | 8.3152 | 10.3033 | 7.7363 | 9.6263 | 13.0863 | 10.3575 | 10.1323 | 11.3073 | 8.0862 | 9.7271 | 12.5983 | 8.0927 | 10.3805 | 9.7323 | 9.8121 | 8.5595 | 10.2625 | 0.093399 | 20.957 | 0.033481 | 0.049781 | -37.8314 | 3.1203 | -0.77 | 0.28 | -0.35638 | -0.22125 | 0.47305 | 0.25345 | 0.26415 | -0.57183 | 0.42109 | 0.40842 | 0.4079 | 0.42955 | 0.4043 | 0.5832 | 0.43027 | 0.41606
42810.4375 | -220 | 18.4723 | 18.6004 | 18.601 | 18.6005 | 17.9494 | 16.597 | 14.6628 | 16.7152 | 17.2033 | 17.2917 | 17.3017 | 16.8418 | 15.8757 | 14.5028 | 14.9105 | 14.935 | 15.5073 | 13.3766 | 13.4849 | 14.0573 |  |  |  | 16.6009 | 15.9369 | 15.0418 | 10.1385 | 9.5559 | 9.7535 | 17.1533 | 16.3218 | 15.1311 | 16.8766 | 16.1646 | 15.1579 | 10.7512 | 11.5404 |  | 12.0459 | 10.7119 | 10.2655 | 8.5681 |  | 6.3953 | 6.4027 | 5.8756 | 5.9682 | 6.0466 | 6.2437 | 6.6632 | 4.4285 | 6.4319 | 4.9499 | 6.6912 | 8.0464 | 42.0348 | 46.8265 | 42.7809 | 14.9906 |  |  | 0.13099 | 0.076315 | -0.098032 | -0.067682 | -0.046492 | -0.033316 | 0.22004 | -0.10924 | 1.3414 | -0.42837 | -0.384 | 8.8669 | 8.8683 | 2.0085 | 15.7823 | 16.7033 | 17.244 | 17.5704 | 17.5353 | 16.5115 | 14.8672 | 16.8448 | 17.1822 | 17.4694 | 17.5133 | 17.2534 | 16.4598 | 14.6895 | 6.2068 | 8.3563 | 5.5509 | 5.8073 | 5.8373 | 6.6536 | 7.626 | 15.8604 | 15.5207 | 15.3848 | 14.315 | 14.2051 | 14.1401 |  |  |  | 10.6563 | 9.167 | 8.8775 | 8.9215 | 0.061842 | -0.064528 | 12.759 |  |  | 10.6042 |  |  | 16.8795 | 16.0718 | 15.0457 | 16.3786 | 15.6635 | 14.7641 | 10.3389 | 10.4232 | 11.2324 | 11.1899 | 9.0741 |  | 10.5338 | 8.2162 | 9.8908 | 8.788 | 10.9726 | 11.7106 |  | 12.1952 |  |  | 11.6801 | 12.4439 | 12.4558 | [6 empty] | 12.2836 |  |  | 11.2687 |  |  | 8.9798 | 10.0805 | 11.6912 | 7.5971 | 9.1479 | 12.3628 | 7.8081 | 9.5013 | 12.263 | 9.1113 | 10.3961 | 7.7412 | 10.3435 | 8.3064 | 10.3107 | 7.7313 | 9.6306 | 13.072 | 10.353 | 10.1284 | 11.3111 | 8.0899 | 9.7325 | 12.6047 | 8.0974 | 10.3842 | 9.7326 | 9.8131 | 8.5673 | 10.2724 | -0.0036716 | 20.9575 | 0.033757 | 0.049817 | -37.7509 | 3.1203 | -1.04 | 0.23 | 0.42423 | 0.32189 | -0.36482 | -0.30313 | -0.25117 | -0.21262 | 0.54641 | 0.40776 | 0.41042 | 0.43017 | 0.39719 | 0.58296 | 0.42899 | 0.41604
42810.4375 | -219 | 18.4689 | 18.6035 | 18.602 | 18.6025 | 17.9436 | 16.5834 | 14.6577 | 16.7115 | 17.207 | 17.296 | 17.3012 | 16.8415 | 15.8722 | 14.4984 | 14.9039 | 14.9385 | 15.5063 | 13.3772 | 13.4844 | 14.0569 |  |  |  | 16.6004 | 15.936 | 15.0442 | 10.1326 | 9.5541 | 9.7461 | 17.1609 | 16.3278 | 15.1291 | 16.8808 | 16.1679 | 15.1593 | 10.7425 | 11.5036 |  | 12.0507 | 10.7141 | 10.2735 | 8.6423 |  | 6.3868 | 6.4051 | 5.8704 | 5.9634 | 6.0354 | 6.2308 | 6.6338 | 4.4314 | 6.4245 | 4.8587 | 6.6898 | 8.0434 | 42.0023 | 46.8631 | 42.782 | 14.9802 |  |  | 0.090903 | -0.13199 | -0.11249 | -0.13602 | -0.14243 | -0.14174 | 0.10307 | 0.077376 | 0.46764 | -0.62328 | -0.30412 | 8.8679 | 8.8692 | 2.0084 | 15.7832 | 16.7048 | 17.247 | 17.5789 | 17.5297 | 16.5071 | 14.8654 | 16.8444 | 17.1845 | 17.4741 | 17.5155 | 17.2601 | 16.4641 | 14.6927 | 6.2375 | 8.3689 | 5.5337 | 5.7853 | 5.9851 | 6.6548 | 7.6272 | 15.8539 | 15.517 | 15.3815 | 14.3127 | 14.2001 | 14.1392 |  |  |  | 10.6548 | 9.1557 | 8.8664 | 8.928 | 0.13923 | -0.0267 | 12.7582 |  |  | 10.6029 |  |  | 16.8735 | 16.0652 | 15.0462 | 16.3785 | 15.6596 | 14.7679 | 10.3196 | 10.4274 | 11.2304 | 11.1926 | 9.0984 |  | 10.5439 | 8.133 | 9.8995 | 8.7862 | 10.9906 | 11.7549 |  | 12.2074 |  |  | 11.688 | 12.4337 | 12.4739 | [6 empty] | 12.2663 |  |  | 11.2779 |  |  | 8.9823 | 10.07 | 11.6895 | 7.5881 | 9.152 | 12.3603 | 7.8096 | 9.5013 | 12.254 | 9.1085 | 10.398 | 7.7327 | 10.3388 | 8.3093 | 10.3043 | 7.734 | 9.6264 | 13.0691 | 10.3603 | 10.1184 | 11.3141 | 8.096 | 9.7251 | 12.6042 | 8.1063 | 10.3899 | 9.7273 | 9.8068 | 8.5732 | 10.2744 | -0.026591 | 20.957 | 0.033315 | 0.049014 | -37.8363 | 3.1202 | 2.66 | 0.27 | 0.3534 | -0.42333 | -0.3908 | -0.42974 | -0.43961 | -0.43854 | 0.37396 | 0.40742 | 0.41301 | 0.43082 | 0.3939 | 0.58502 | 0.42664 | 0.41581
42810.4375 | -218 | 18.4677 | 18.5954 | 18.5865 | 18.5954 | 17.9446 | 16.5798 | 14.6561 | 16.7132 | 17.1941 | 17.2864 | 17.306 | 16.8323 | 15.876 | 14.4819 | 14.9008 | 14.9324 | 15.5091 | 13.3629 | 13.4765 | 14.051 |  |  |  | 16.5961 | 15.9341 | 15.0463 | 10.1313 | 9.5463 | 9.7399 | 17.1554 | 16.3127 | 15.1346 | 16.8755 | 16.1621 | 15.1544 | 10.7423 | 11.4618 |  | 12.0445 | 10.7016 | 10.2801 | 8.6572 |  | 6.3812 | 6.3964 | 5.8476 | 5.9498 | 6.0328 | 6.2144 | 6.6187 | 4.4534 | 6.426 | 4.8321 | 6.6809 | 8.0498 | 41.9723 | 46.8934 | 42.7966 | 14.978 |  |  | 0.096815 | -0.15828 | -0.1 | 0.099882 | 0.080332 | -0.24885 | -0.35954 | -0.13947 | -0.3273 | 1.5102 | -0.49586 | 8.8703 | 8.8712 | 2.0084 | 15.7789 | 16.7043 | 17.2502 | 17.5723 | 17.53 | 16.5051 | 14.8654 | 16.842 | 17.1795 | 17.4755 | 17.519 | 17.2599 | 16.4682 | 14.6907 | 6.2521 | 8.3714 | 5.4911 | 5.8233 | 6.017 | 6.6577 | 7.6262 | 15.8569 | 15.5173 | 15.3763 | 14.3136 | 14.1954 | 14.1396 |  |  |  | 10.6628 | 9.1548 | 8.8653 | 8.9218 | 0.089193 | -0.060764 | 12.7538 |  |  | 10.6101 |  |  | 16.8794 | 16.0694 | 15.0483 | 16.3749 | 15.6621 | 14.7665 | 10.295 | 10.4249 | 11.233 | 11.2001 | 9.1115 |  | 10.5321 | 8.0525 | 9.8897 | 8.7732 | 10.9736 | 11.753 |  | 12.2014 |  |  | 11.7206 | 12.4442 | 12.4821 | [6 empty] | 12.221 |  |  | 11.288 |  |  | 8.9883 | 10.0734 | 11.6888 | 7.5743 | 9.1637 | 12.3603 | 7.8197 | 9.5095 | 12.2401 | 9.1165 | 10.3992 | 7.7014 | 10.3428 | 8.3277 | 10.3088 | 7.7407 | 9.6297 | 13.0629 | 10.3558 | 10.1153 | 11.3103 | 8.1082 | 9.7353 | 12.6058 | 8.1227 | 10.3892 | 9.7316 | 9.7996 | 8.5791 | 10.2839 | -0.069733 | 20.9582 | 0.032443 | 0.047241 | -37.798 | 3.1203 | 7.28 | 0.31 | 0.36471 | -0.46356 | -0.36847 | 0.36825 | 0.33014 | -0.58106 | -0.69844 | 0.40667 | 0.41493 | 0.43062 | 0.39261 | 0.58962 | 0.42622 | 0.41624
42810.4375 | -217 | 18.465 | 18.5967 | 18.5873 | 18.5978 | 17.941 | 16.5841 | 14.6515 | 16.7095 | 17.1949 | 17.2874 | 17.2996 | 16.8379 | 15.8729 | 14.4905 | 14.9085 | 14.9366 | 15.51 | 13.3763 | 13.4877 | 14.0578 |  |  |  | 16.6066 | 15.9321 | 15.0444 | 10.1294 | 9.5528 | 9.7315 | 17.1507 | 16.3062 | 15.1316 | 16.8689 | 16.1591 | 15.153 | 10.7357 | 11.4335 |  | 12.0358 | 10.6903 | 10.3015 | 8.6485 |  | 6.3869 | 6.3908 | 5.8421 | 5.9561 | 6.0303 | 6.2057 | 6.596 | 4.5335 | 6.4291 | 4.8173 | 6.6827 | 8.0479 | 41.9485 | 46.9079 | 42.807 | 14.9727 |  |  | 0.079075 | -0.14973 | 0.10896 | -0.059142 | 0.10662 | -0.56492 | -0.12429 | -0.010676 | -0.64508 | -1.029 | -0.4907 | 8.8703 | 8.8714 | 2.0084 | 15.7884 | 16.7067 | 17.2596 | 17.5822 | 17.5459 | 16.5203 | 14.879 | 16.8524 | 17.1869 | 17.4825 | 17.5315 | 17.2711 | 16.4707 | 14.6966 | 6.2406 | 8.3546 | 5.4234 | 5.8885 | 5.952 | 6.6449 | 7.622 | 15.8476 | 15.5045 | 15.3781 | 14.3123 | 14.1952 | 14.1362 |  |  |  | 10.6573 | 9.159 | 8.8725 | 8.917 | 0.047255 | -0.034039 | 12.7423 |  |  | 10.6009 |  |  | 16.872 | 16.0617 | 15.038 | 16.3663 | 15.6573 | 14.759 | 10.2707 | 10.4202 | 11.2225 | 11.2 | 9.1231 |  | 10.5408 | 8.0147 | 9.8847 | 8.7731 | 10.9767 | 11.7692 |  | 12.203 |  |  | 11.738 | 12.4407 | 12.4908 | [6 empty] | 12.2224 |  |  | 11.2855 |  |  | 8.9846 | 10.0704 | 11.6741 | 7.5463 | 9.1717 | 12.3657 | 7.8048 | 9.5053 | 12.2301 | 9.1211 | 10.3922 | 7.663 | 10.3413 | 8.324 | 10.3146 | 7.7385 | 9.6266 | 13.0518 | 10.3499 | 10.1168 | 11.3284 | 8.1149 | 9.7346 | 12.6068 | 8.1399 | 10.3861 | 9.7487 | 9.8007 | 8.5794 | 10.2866 | -0.086297 | 20.9572 | 0.031249 | 0.047017 | -37.8188 | 3.1203 | -1.51 | 0.23 | 0.3296 | -0.45087 | 0.38461 | -0.28336 | 0.38033 | -0.87547 | -0.41065 | 0.40663 | 0.41581 | 0.43072 | 0.39241 | 0.59666 | 0.42624 | 0.4162
42810.4375 | -216 | 18.4643 | 18.5929 | 18.5832 | 18.5923 | 17.9366 | 16.583 | 14.6474 | 16.7042 | 17.1934 | 17.2879 | 17.2935 | 16.8361 | 15.8718 | 14.4882 | 14.909 | 14.9462 | 15.5066 | 13.3725 | 13.4957 | 14.0625 |  |  |  | 16.6108 | 15.9421 | 15.0382 | 10.1289 | 9.5575 | 9.7212 | 17.1493 | 16.3123 | 15.1244 | 16.8646 | 16.1564 | 15.1488 | 10.7464 | 11.403 |  | 12.0388 | 10.6785 | 10.3075 | 8.6409 |  | 6.3786 | 6.3832 | 5.8422 | 5.9525 | 6.0202 | 6.1926 | 6.5633 | 4.588 | 6.4328 | 4.7665 | 6.6912 | 8.0412 | 41.9271 | 46.9381 | 42.8185 | 14.9668 |  |  | 0.076443 | -0.001225 | 0.064276 | -0.021686 | 0.11779 | -0.33428 | 0.28969 | -0.074416 | -0.12784 | -0.41872 | -0.51295 | 8.8695 | 8.8707 | 2.0085 | 15.7814 | 16.7163 | 17.2545 | 17.583 | 17.5469 | 16.5302 | 14.8752 | 16.8534 | 17.1915 | 17.4852 | 17.533 | 17.2699 | 16.4684 | 14.7046 | 6.2475 | 8.3465 | 5.3685 | 5.8601 | 5.9076 | 6.6519 | 7.6211 | 15.8506 | 15.5098 | 15.3774 | 14.3129 | 14.1914 | 14.1378 |  |  |  | 10.6566 | 9.1581 | 8.8776 | 8.9224 | -0.17723 | -0.12588 | 12.744 |  |  | 10.5955 |  |  | 16.8806 | 16.0646 | 15.0409 | 16.3788 | 15.6568 | 14.7592 | 10.2725 | 10.4341 | 11.2362 | 11.217 | 9.1499 |  | 10.5282 | 7.962 | 9.891 | 8.7646 | 10.9629 | 11.8093 |  | 12.1974 |  |  | 11.7551 | 12.4519 | 12.4934 | [6 empty] | 12.2414 |  |  | 11.2868 |  |  | 8.9888 | 10.06 | 11.6768 | 7.518 | 9.177 | 12.3644 | 7.805 | 9.504 | 12.2117 | 9.114 | 10.3933 | 7.6728 | 10.3446 | 8.3236 | 10.3145 | 7.7351 | 9.6275 | 13.0536 | 10.3538 | 10.1131 | 11.3313 | 8.1192 | 9.7185 | 12.609 | 8.1526 | 10.385 | 9.7494 | 9.8102 | 8.5898 | 10.2888 | 0.063546 | 20.959 | 0.031725 | 0.047531 | -37.749 | 3.1203 | -5.44 | 0.34 | 0.32406 | -0.04078 | 0.2954 | -0.17158 | 0.39975 | -0.67342 | 0.6269 | 0.40547 | 0.41748 | 0.43051 | 0.39245 | 0.60266 | 0.4268 | 0.41602
42810.4375 | -215 | 18.4669 | 18.596 | 18.5876 | 18.5996 | 17.9475 | 16.5892 | 14.6512 | 16.7059 | 17.1991 | 17.2939 | 17.2941 | 16.8402 | 15.8738 | 14.497 | 14.903 | 14.9402 | 15.5059 | 13.3685 | 13.478 | 14.0644 |  |  |  | 16.6014 | 15.9302 | 15.0423 | 10.1225 | 9.541 | 9.6798 | 17.1526 | 16.3178 | 15.1303 | 16.8732 | 16.1591 | 15.1574 | 10.7481 | 11.3844 |  | 12.0396 | 10.6793 | 10.3264 | 8.6397 |  | 6.3719 | 6.3693 | 5.8411 | 5.9359 | 6.0117 | 6.1828 | 6.5268 | 4.5846 | 6.4335 | 4.727 | 6.6868 | 8.0516 | 41.9253 | 46.9668 | 42.8308 | 14.981 |  |  | -0.056949 | -0.064309 | 0.071504 | -0.23591 | -0.088548 | -0.35924 | 0.55451 | -0.057332 | -1.0606 | -0.082204 | -0.4297 | 8.8702 | 8.8712 | 2.0085 | 15.7785 | 16.7058 | 17.2415 | 17.5696 | 17.5366 | 16.5193 | 14.8702 | 16.8399 | 17.1789 | 17.4792 | 17.5206 | 17.2685 | 16.4649 | 14.6939 | 6.2146 | 8.3077 | 5.326 | 5.8046 | 5.901 | 6.6422 | 7.6103 | 15.8465 | 15.5142 | 15.3776 | 14.3126 | 14.1959 | 14.1378 |  |  |  | 10.6574 | 9.1532 | 8.8889 | 8.9498 | -0.18249 | -0.12776 | 12.7398 |  |  | 10.5562 |  |  | 16.8752 | 16.065 | 15.0426 | 16.3787 | 15.6649 | 14.7638 | 10.2688 | 10.4471 | 11.2386 | 11.2275 | 9.1648 |  | 10.5293 | 7.9133 | 9.8806 | 8.7556 | 10.9774 | 11.8596 |  | 12.2077 |  |  | 11.7751 | 12.4756 | 12.4948 | [6 empty] | 12.2818 |  |  | 11.2707 |  |  | 8.9773 | 10.0429 | 11.6506 | 7.5059 | 9.1706 | 12.3517 | 7.7965 | 9.4902 | 12.2017 | 9.121 | 10.375 | 7.6659 | 10.3269 | 8.3142 | 10.2981 | 7.7377 | 9.6316 | 13.0626 | 10.3498 | 10.1035 | 11.3281 | 8.1259 | 9.7292 | 12.6091 | 8.1556 | 10.3885 | 9.7537 | 9.8097 | 8.6097 | 10.3137 | -0.010027 | 20.9584 | 0.032288 | 0.047791 | -37.7795 | 3.1203 | -6.81 | 0.32 | -0.27969 | -0.29547 | 0.31156 | -0.5659 | -0.34659 | -0.69811 | 0.86732 | 0.40509 | 0.41849 | 0.43124 | 0.39499 | 0.60612 | 0.42689 | 0.41529
42810.4376 | -214 | 18.4627 | 18.5986 | 18.5899 | 18.5983 | 17.9446 | 16.5909 | 14.6522 | 16.7106 | 17.1943 | 17.2956 | 17.3007 | 16.8462 | 15.8698 | 14.4967 | 14.9137 | 14.9476 | 15.5176 | 13.3754 | 13.4964 | 14.0667 |  |  |  | 16.6102 | 15.9487 | 15.0446 | 10.1278 | 9.5537 | 9.6738 | 17.1529 | 16.3196 | 15.1253 | 16.8731 | 16.1569 | 15.1558 | 10.7438 | 11.3794 |  | 12.0351 | 10.6734 | 10.3341 | 8.6522 |  | 6.3784 | 6.3788 | 5.8409 | 5.9263 | 6.0083 | 6.183 | 6.516 | 4.6074 | 6.4384 | 4.749 | 6.699 | 8.0485 | 41.9269 | 46.9894 | 42.8413 | 14.9932 |  |  | 0.029131 | -0.11754 | 0.12736 | -0.33776 | -0.13783 | -0.34348 | 0.37971 | -0.031048 | 0.0009884 | -1.2113 | -0.46129 | 8.871 | 8.8724 | 2.0084 | 15.7764 | 16.6997 | 17.2409 | 17.5771 | 17.529 | 16.513 | 14.8668 | 16.845 | 17.1811 | 17.481 | 17.5167 | 17.2681 | 16.4672 | 14.686 | 6.1623 | 8.2815 | 5.2919 | 5.7783 | 5.902 | 6.6397 | 7.6174 | 15.8442 | 15.5035 | 15.3738 | 14.3096 | 14.1997 | 14.1332 |  |  |  | 10.6535 | 9.1602 | 8.8973 | 8.9521 | 0.088585 | -0.054553 | 12.7391 |  |  | 10.4866 |  |  | 16.8743 | 16.0682 | 15.0427 | 16.3741 | 15.6636 | 14.7742 | 10.2743 | 10.4656 | 11.2425 | 11.2358 | 9.1611 |  | 10.524 | 7.8508 | 9.8753 | 8.7406 | 10.9699 | 11.9221 |  | 12.1999 |  |  | 11.7724 | 12.4846 | 12.4834 | [6 empty] | 12.292 |  |  | 11.2565 |  |  | 8.9768 | 10.0326 | 11.648 | 7.4817 | 9.1656 | 12.3565 | 7.8014 | 9.4811 | 12.2103 | 9.1251 | 10.3683 | 7.6824 | 10.3339 | 8.3123 | 10.2803 | 7.7501 | 9.6433 | 13.0797 | 10.3519 | 10.1122 | 11.3376 | 8.1346 | 9.7306 | 12.62 | 8.1624 | 10.3944 | 9.7536 | 9.7992 | 8.6096 | 10.3124 | 0.0026842 | 20.9584 | 0.032827 | 0.049014 | -37.7704 | 3.1202 | 2.28 | 0.28 | 0.20003 | -0.39945 | 0.41581 | -0.67715 | -0.43242 | -0.68262 | 0.71772 | 0.40502 | 0.42005 | 0.4314 | 0.40051 | 0.61074 | 0.4264 | 0.4151
42810.4376 | -213 | 18.4715 | 18.5995 | 18.5942 | 18.6034 | 17.9457 | 16.5862 | 14.6553 | 16.7085 | 17.2 | 17.2926 | 17.3034 | 16.8471 | 15.8717 | 14.4932 | 14.9124 | 14.9411 | 15.5137 | 13.3635 | 13.4843 | 14.0603 |  |  |  | 16.6062 | 15.9409 | 15.0422 | 10.1196 | 9.5437 | 9.6632 | 17.1569 | 16.3106 | 15.1276 | 16.8697 | 16.1563 | 15.1538 | 10.7431 | 11.3742 |  | 12.0334 | 10.6616 | 10.354 | 8.6604 |  | 6.3739 | 6.3742 | 5.8243 | 5.9152 | 5.9865 | 6.1659 | 6.5081 | 4.6537 | 6.4395 | 4.7434 | 6.6975 | 8.0427 | 41.9363 | 47.0056 | 42.837 | 15.0105 |  |  | 0.028475 | 0.044115 | 0.01302 | -0.25167 | -0.07672 | -0.089828 | 0.16221 | -0.011992 | -0.18622 | -1.1568 | -0.51673 | 8.8691 | 8.8707 | 2.0081 | 15.7681 | 16.6964 | 17.2452 | 17.5722 | 17.5297 | 16.5114 | 14.8628 | 16.8443 | 17.1793 | 17.4734 | 17.5164 | 17.2513 | 16.4658 | 14.6855 | 6.1137 | 8.2841 | 5.2385 | 5.7323 | 5.8892 | 6.6362 | 7.6085 | 15.8471 | 15.5099 | 15.384 | 14.3164 | 14.1984 | 14.1388 |  |  |  | 10.6595 | 9.1697 | 8.9049 | 8.9553 | -0.019603 | -0.034039 | 12.734 |  |  | 10.4225 |  |  | 16.8735 | 16.064 | 15.0413 | 16.3712 | 15.6568 | 14.7719 | 10.2756 | 10.4724 | 11.2501 | 11.2374 | 9.1613 |  | 10.5298 | 7.7084 | 9.8792 | 8.7526 | 10.9727 | 11.9897 |  | 12.1981 |  |  | 11.8033 | 12.5036 | 12.5117 | [6 empty] | 12.2932 |  |  | 11.2874 |  |  | 8.9903 | 10.0452 | 11.6369 | 7.4857 | 9.1735 | 12.3479 | 7.8132 | 9.4741 | 12.1961 | 9.1306 | 10.3763 | 7.6947 | 10.3215 | 8.3187 | 10.2791 | 7.7497 | 9.6455 | 13.0964 | 10.357 | 10.1156 | 11.3552 | 8.136 | 9.7159 | 12.6186 | 8.1592 | 10.3852 | 9.7551 | 9.8027 | 8.6017 | 10.3156 | -0.057022 | 20.9578 | 0.033108 | 0.049825 | -37.7029 | 3.1203 | 11.55 | 0.29 | 0.19776 | 0.24472 | 0.13295 | -0.58452 | -0.3226 | -0.34908 | 0.46908 | 0.40521 | 0.42414 | 0.43116 | 0.4055 | 0.61563 | 0.42615 | 0.41521
42810.4376 | -212 | 18.4666 | 18.5912 | 18.5891 | 18.599 | 17.9414 | 16.5785 | 14.6532 | 16.7065 | 17.201 | 17.2906 | 17.3017 | 16.8376 | 15.8639 | 14.4854 | 14.9055 | 14.9495 | 15.5183 | 13.3732 | 13.4877 | 14.0634 |  |  |  | 16.6072 | 15.9471 | 15.0465 | 10.1145 | 9.5559 | 9.6603 | 17.1543 | 16.3124 | 15.1304 | 16.871 | 16.1569 | 15.1442 | 10.7434 | 11.3628 |  | 12.0375 | 10.6589 | 10.3598 | 8.6585 |  | 6.359 | 6.361 | 5.8119 | 5.8975 | 5.9686 | 6.1573 | 6.4946 | 4.6619 | 6.4369 | 4.694 | 6.6956 | 8.0422 | 41.9443 | 47.0207 | 42.8364 | 15.0316 |  |  | -0.001753 | -0.044597 | -0.040204 | 0.03877 | -0.06226 | -0.50381 | 0.27589 | 0.078692 | -0.12336 | -0.31026 | -0.17834 | 8.8693 | 8.8704 | 2.0086 | 15.7648 | 16.6946 | 17.2394 | 17.5705 | 17.5254 | 16.5094 | 14.8597 | 16.8364 | 17.1776 | 17.467 | 17.5141 | 17.2512 | 16.4598 | 14.6899 | 6.0991 | 8.286 | 5.1768 | 5.6766 | 5.8823 | 6.6339 | 7.6042 | 15.8472 | 15.5158 | 15.3775 | 14.3037 | 14.1931 | 14.1412 |  |  |  | 10.658 | 9.1766 | 8.9137 | 8.9385 | 0.071769 | 0.12518 | 12.7276 |  |  | 10.4075 |  |  | 16.8735 | 16.0722 | 15.0461 | 16.3746 | 15.655 | 14.7572 | 10.2741 | 10.4818 | 11.2549 | 11.2396 | 9.1679 |  | 10.5317 | 7.6286 | 9.8785 | 8.7434 | 10.9654 | 12.0325 |  | 12.2008 |  |  | 11.8062 | 12.481 | 12.5071 | [6 empty] | 12.3163 |  |  | 11.2832 |  |  | 9.0015 | 10.0453 | 11.6281 | 7.4813 | 9.1824 | 12.3586 | 7.8237 | 9.4767 | 12.2012 | 9.1366 | 10.3816 | 7.7004 | 10.3263 | 8.3356 | 10.2798 | 7.7588 | 9.6318 | 13.0995 | 10.3688 | 10.11 | 11.3487 | 8.1533 | 9.7257 | 12.6332 | 8.1324 | 10.3745 | 9.7625 | 9.8088 | 8.614 | 10.3281 | -0.10286 | 20.9592 | 0.033367 | 0.050187 | -37.8396 | 3.1203 | 6.73 | 0.33 | -0.049069 | -0.24605 | -0.23362 | 0.22941 | -0.29061 | -0.82669 | 0.61175 | 0.40509 | 0.42633 | 0.43118 | 0.40686 | 0.62199 | 0.42622 | 0.41562
42810.4376 | -211 | 18.4808 | 18.595 | 18.5987 | 18.6028 | 17.9522 | 16.5931 | 14.6631 | 16.7226 | 17.201 | 17.2924 | 17.3023 | 16.8492 | 15.8739 | 14.4976 | 14.9043 | 14.9442 | 15.5117 | 13.3683 | 13.4824 | 14.0635 |  |  |  | 16.6043 | 15.9396 | 15.0366 | 10.1092 | 9.5472 | 9.6251 | 17.1627 | 16.322 | 15.1348 | 16.8739 | 16.1597 | 15.1602 | 10.7501 | 11.3713 |  | 12.0426 | 10.6632 | 10.3727 | 8.6361 |  | 6.3526 | 6.3579 | 5.8006 | 5.8953 | 5.9581 | 6.1463 | 6.4869 | 4.6753 | 6.4508 | 4.6543 | 6.7074 | 8.0476 | 41.955 | 47.0224 | 42.828 | 15.0528 |  |  | 0.056075 | -0.11622 | 0.096476 | -0.39755 | -0.024148 | -0.002432 | 0.33437 | -0.14144 | -0.80154 | -0.25151 | -0.51752 | 8.8681 | 8.8694 | 2.0085 | 15.7703 | 16.6963 | 17.2468 | 17.5735 | 17.5333 | 16.517 | 14.8647 | 16.8446 | 17.1853 | 17.4685 | 17.5227 | 17.2607 | 16.468 | 14.6952 | 6.0915 | 8.3038 | 5.1536 | 5.6361 | 5.8724 | 6.6367 | 7.611 | 15.8417 | 15.5092 | 15.3806 | 14.3067 | 14.1951 | 14.1366 |  |  |  | 10.6561 | 9.1793 | 8.9228 | 8.944 | 0.081899 | 0.0043534 | 12.7349 |  |  | 10.4223 |  |  | 16.8777 | 16.0818 | 15.0524 | 16.3729 | 15.6667 | 14.7692 | 10.2865 | 10.5014 | 11.2683 | 11.2485 | 9.1511 |  | 10.5332 | 7.5804 | 9.8787 | 8.7464 | 10.9711 | 12.0555 |  | 12.2046 |  |  | 11.8165 | 12.4888 | 12.5001 | [6 empty] | 12.3304 |  |  | 11.2856 |  |  | 9.002 | 10.0407 | 11.6138 | 7.4618 | 9.1827 | 12.3469 | 7.8288 | 9.469 | 12.1928 | 9.1361 | 10.3846 | 7.6975 | 10.3119 | 8.3191 | 10.2838 | 7.7234 | 9.6086 | 13.1 | 10.3675 | 10.105 | 11.3552 | 8.1594 | 9.7261 | 12.6368 | 8.0786 | 10.3621 | 9.7705 | 9.7942 | 8.617 | 10.3339 | -0.093808 | 20.9578 | 0.033711 | 0.050577 | -37.8169 | 3.1203 | 5.83 | 0.38 | 0.27751 | -0.3972 | 0.36189 | -0.73462 | -0.18098 | -0.057436 | 0.67346 | 0.4056 | 0.42768 | 0.43128 | 0.40802 | 0.62535 | 0.42706 | 0.41541
42810.4376 | -210 | 18.4763 | 18.6003 | 18.6021 | 18.6132 | 17.9535 | 16.6005 | 14.6549 | 16.72 | 17.2008 | 17.2947 | 17.3015 | 16.8457 | 15.8804 | 14.4985 | 14.9135 | 14.9349 | 15.5149 | 13.368 | 13.4873 | 14.0632 |  |  |  | 16.6124 | 15.9425 | 15.0411 | 10.1107 | 9.5533 | 9.5787 | 17.1664 | 16.3233 | 15.1379 | 16.8715 | 16.1573 | 15.1745 | 10.751 | 11.3773 |  | 12.0392 | 10.6537 | 10.3755 | 8.6167 |  | 6.3412 | 6.3419 | 5.7848 | 5.8767 | 5.9436 | 6.1313 | 6.4674 | 4.7008 | 6.4448 | 4.6058 | 6.7033 | 8.0492 | 41.9736 | 47.0235 | 42.8439 | 15.087 |  |  | -0.065493 | -0.13331 | -0.032976 | -0.32659 | 0.008708 | -0.31719 | 0.42506 | -0.085588 | 0.71245 | -0.74349 | -0.28047 | 8.8676 | 8.8688 | 2.0085 | 15.7727 | 16.6948 | 17.2464 | 17.5696 | 17.5353 | 16.5173 | 14.8623 | 16.8488 | 17.1887 | 17.4717 | 17.5224 | 17.263 | 16.4682 | 14.6965 | 6.0736 | 8.3138 | 5.18 | 5.6151 | 5.8604 | 6.6313 | 7.609 | 15.8379 | 15.5076 | 15.3757 | 14.3033 | 14.1948 | 14.1325 |  |  |  | 10.6483 | 9.1852 | 8.9258 | 8.9612 | -0.046954 | -0.053236 | 12.7317 |  |  | 10.4436 |  |  | 16.8835 | 16.0735 | 15.051 | 16.3772 | 15.662 | 14.7726 | 10.2904 | 10.5101 | 11.2811 | 11.2671 | 9.1242 |  | 10.5213 | 7.5636 | 9.8691 | 8.7435 | 10.9543 | 12.0738 |  | 12.1981 |  |  | 11.8296 | 12.4904 | 12.5015 | [6 empty] | 12.3547 |  |  | 11.2945 |  |  | 9.005 | 10.0332 | 11.602 | 7.4571 | 9.1809 | 12.352 | 7.8262 | 9.4685 | 12.1816 | 9.1365 | 10.3841 | 7.7009 | 10.3075 | 8.3142 | 10.284 | 7.7069 | 9.5623 | 13.0853 | 10.3574 | 10.1017 | 11.3586 | 8.1526 | 9.7139 | 12.636 | 8.0356 | 10.3468 | 9.7619 | 9.7779 | 8.6188 | 10.3253 | -0.0030938 | 20.9585 | 0.033441 | 0.050158 | -37.7831 | 3.1203 | -8.75 | 0.33 | -0.29988 | -0.42538 | -0.21157 | -0.66581 | 0.10868 | -0.65591 | 0.7593 | 0.40596 | 0.42783 | 0.43081 | 0.40939 | 0.6222 | 0.42763 | 0.41467
42810.4376 | -209 | 18.4706 | 18.5926 | 18.5892 | 18.6003 | 17.9393 | 16.5834 | 14.651 | 16.7089 | 17.1922 | 17.2931 | 17.2961 | 16.8352 | 15.8762 | 14.4909 | 14.9135 | 14.9355 | 15.5127 | 13.3707 | 13.4897 | 14.0623 |  |  |  | 16.612 | 15.9394 | 15.0469 | 10.1014 | 9.5553 | 9.5241 | 17.1552 | 16.3178 | 15.1304 | 16.8725 | 16.1588 | 15.1606 | 10.7564 | 11.3814 |  | 12.0377 | 10.6457 | 10.3758 | 8.6062 |  | 6.3333 | 6.3431 | 5.7809 | 5.8734 | 5.9341 | 6.1228 | 6.4534 | 4.7166 | 6.4484 | 4.6087 | 6.7018 | 8.048 | 41.9886 | 47.0141 | 42.8477 | 15.1139 |  |  | 0.053447 | -0.21545 | -0.04546 | 0.15442 | -0.023492 | -0.15291 | 0.60313 | -0.27352 | -0.2734 | -0.35725 | -0.34207 | 8.8696 | 8.8709 | 2.0082 | 15.7724 | 16.6974 | 17.2522 | 17.5682 | 17.5428 | 16.526 | 14.8742 | 16.8531 | 17.186 | 17.4844 | 17.5304 | 17.2651 | 16.4681 | 14.6992 | 6.0512 | 8.3024 | 5.194 | 5.67 | 5.8513 | 6.6333 | 7.6082 | 15.8399 | 15.5105 | 15.3704 | 14.3035 | 14.1961 | 14.1274 |  |  |  | 10.6389 | 9.1877 | 8.9157 | 8.9939 | 0.11999 | -0.043449 | 12.7278 |  |  | 10.455 |  |  | 16.8842 | 16.0666 | 15.05 | 16.379 | 15.6665 | 14.7704 | 10.2891 | 10.5114 | 11.2813 | 11.2821 | 9.1075 |  | 10.5212 | 7.5896 | 9.86 | 8.7544 | 10.9549 | 12.1035 |  | 12.205 |  |  | 11.8269 | 12.4887 | 12.496 | [6 empty] | 12.3805 |  |  | 11.3005 |  |  | 9.0181 | 10.0459 | 11.6022 | 7.4536 | 9.1832 | 12.3474 | 7.8443 | 9.4676 | 12.1762 | 9.1445 | 10.393 | 7.7147 | 10.2967 | 8.3166 | 10.276 | 7.7018 | 9.5413 | 13.078 | 10.3647 | 10.1044 | 11.3548 | 8.1607 | 9.7116 | 12.6368 | 8.019 | 10.3569 | 9.7641 | 9.7725 | 8.6137 | 10.3328 | -0.0030938 | 20.9574 | 0.033573 | 0.051178 | -37.7746 | 3.1203 | -9.57 | 0.34 | 0.27088 | -0.54078 | -0.24841 | 0.45783 | -0.1785 | -0.45541 | 0.90446 | 0.40642 | 0.42681 | 0.43053 | 0.41211 | 0.62054 | 0.4281 | 0.41346
42810.4376 | -208 | 18.4757 | 18.5979 | 18.598 | 18.607 | 17.9484 | 16.5838 | 14.6577 | 16.7116 | 17.1982 | 17.2887 | 17.2966 | 16.838 | 15.8752 | 14.493 | 14.903 | 14.9322 | 15.5029 | 13.3662 | 13.4912 | 14.0541 |  |  |  | 16.5938 | 15.9345 | 15.0385 | 10.0867 | 9.5523 | 9.4888 | 17.1502 | 16.3136 | 15.1269 | 16.8706 | 16.16 | 15.158 | 10.7462 | 11.3813 |  | 12.0285 | 10.623 | 10.365 | 8.5941 |  | 6.3259 | 6.3333 | 5.7787 | 5.8549 | 5.9114 | 6.1013 | 6.419 | 4.7642 | 6.4472 | 4.6162 | 6.6935 | 8.0437 | 42.0093 | 47.0087 | 42.8727 | 15.138 |  |  | 0.076443 | -0.16353 | 0.015648 | -0.07557 | -0.035976 | -0.46044 | 0.33174 | -0.29324 | -0.39522 | 0.06025 | -0.43506 | 8.8708 | 8.872 | 2.0086 | 15.7727 | 16.7012 | 17.2472 | 17.5704 | 17.5455 | 16.5203 | 14.872 | 16.854 | 17.1831 | 17.4845 | 17.5241 | 17.26 | 16.4627 | 14.701 | 6.0565 | 8.299 | 5.1572 | 5.6954 | 5.8707 | 6.626 | 7.6091 | 15.8301 | 15.506 | 15.3695 | 14.2952 | 14.1841 | 14.1223 |  |  |  | 10.6466 | 9.1999 | 8.9168 | 9.0096 | 0.14471 | -0.041567 | 12.7254 |  |  | 10.4659 |  |  | 16.8745 | 16.068 | 15.0492 | 16.3793 | 15.6633 | 14.7628 | 10.2836 | 10.5148 | 11.2858 | 11.2935 | 9.0894 |  | 10.5199 | 7.5973 | 9.8558 | 8.7534 | 10.9553 | 12.1081 |  | 12.2068 |  |  | 11.8177 | 12.4814 | 12.4981 | [6 empty] | 12.399 |  |  | 11.2956 |  |  | 9.0313 | 10.0572 | 11.6044 | 7.4517 | 9.1842 | 12.3484 | 7.8544 | 9.4841 | 12.1788 | 9.1509 | 10.4041 | 7.7306 | 10.275 | 8.328 | 10.2772 | 7.6982 | 9.5438 | 13.0704 | 10.3713 | 10.1064 | 11.3578 | 8.1723 | 9.7092 | 12.6474 | 8.0105 | 10.3547 | 9.7646 | 9.7745 | 8.6113 | 10.3364 | 0.054686 | 20.9583 | 0.033194 | 0.051062 | -37.7501 | 3.1203 | -4.06 | 0.28 | 0.32393 | -0.47114 | 0.14574 | -0.32027 | -0.22089 | -0.79023 | 0.67076 | 0.40688 | 0.42645 | 0.43057 | 0.41067 | 0.62474 | 0.4281 | 0.41327
42810.4376 | -207 | 18.4772 | 18.5947 | 18.5999 | 18.6087 | 17.9439 | 16.5836 | 14.6582 | 16.7171 | 17.1991 | 17.2922 | 17.3025 | 16.8428 | 15.8785 | 14.4966 | 14.8972 | 14.9296 | 15.498 | 13.3594 | 13.4852 | 14.0536 |  |  |  | 16.5911 | 15.9317 | 15.0301 | 10.0772 | 9.5553 | 9.4659 | 17.1582 | 16.3164 | 15.1285 | 16.8657 | 16.1586 | 15.1554 | 10.7468 | 11.3928 |  | 12.0367 | 10.61 | 10.351 | 8.5858 |  | 6.3312 | 6.3438 | 5.7807 | 5.8646 | 5.9173 | 6.1031 | 6.4044 | 4.812 | 6.4614 | 4.6604 | 6.7057 | 8.0442 | 42.049 | 47.0188 | 42.9074 | 15.1591 |  |  | 0.061331 | -0.16222 | 0.049164 | -0.17282 | -0.1536 | 0.089564 | 0.3646 | -0.30375 | -0.61959 | -0.42355 | -0.43109 | 8.8684 | 8.8696 | 2.0083 | 15.7619 | 16.688 | 17.2372 | 17.5751 | 17.5292 | 16.5124 | 14.8692 | 16.8383 | 17.1829 | 17.4766 | 17.5283 | 17.2566 | 16.4726 | 14.6817 | 6.0847 | 8.3384 | 5.1401 | 5.6697 | 5.9408 | 6.6326 | 7.6115 | 15.8315 | 15.5057 | 15.3734 | 14.307 | 14.1988 | 14.1304 |  |  |  | 10.6528 | 9.2098 | 8.9266 | 9.0199 | 0.047862 | 0.0081174 | 12.7235 |  |  | 10.4806 |  |  | 16.8816 | 16.0655 | 15.0505 | 16.3764 | 15.6646 | 14.7688 | 10.2722 | 10.5159 | 11.3026 | 11.303 | 9.0588 |  | 10.5169 | 7.6273 | 9.8579 | 8.7657 | 10.9578 | 12.125 |  | 12.2016 |  |  | 11.809 | 12.4839 | 12.4987 | [6 empty] | 12.409 |  |  | 11.29 |  |  | 9.0435 | 10.0599 | 11.6143 | 7.4501 | 9.1841 | 12.3534 | 7.8614 | 9.4951 | 12.1822 | 9.15 | 10.4156 | 7.7399 | 10.2615 | 8.3303 | 10.2812 | 7.6977 | 9.548 | 13.0701 | 10.3772 | 10.1161 | 11.3637 | 8.1773 | 9.7055 | 12.6591 | 8.0069 | 10.3547 | 9.7655 | 9.7802 | 8.609 | 10.329 | -0.087453 | 20.9562 | 0.033229 | 0.050592 | -37.8164 | 3.1203 | -2.7 | 0.34 | 0.29014 | -0.46925 | 0.25833 | -0.48434 | -0.45642 | 0.34852 | 0.70319 | 0.40763 | 0.42569 | 0.43031 | 0.40831 | 0.62692 | 0.42835 | 0.41319
42810.4377 | -206 | 18.4726 | 18.5876 | 18.5969 | 18.6058 | 17.9394 | 16.5893 | 14.6591 | 16.7154 | 17.1996 | 17.2877 | 17.3003 | 16.841 | 15.8795 | 14.4951 | 14.9022 | 14.9302 | 15.5021 | 13.3601 | 13.4844 | 14.0539 |  |  |  | 16.5976 | 15.937 | 15.0367 | 10.0735 | 9.5652 | 9.449 | 17.1615 | 16.3191 | 15.1309 | 16.8721 | 16.1568 | 15.1615 | 10.7548 | 11.4133 |  | 12.0459 | 10.5888 | 10.3358 | 8.5792 |  | 6.3356 | 6.3314 | 5.7785 | 5.8681 | 5.9148 | 6.1011 | 6.3948 | 4.8455 | 6.4587 | 4.7539 | 6.7025 | 8.0467 | 42.0821 | 47.0455 | 42.9304 | 15.1824 |  |  | 0.072503 | -0.18851 | 0.059676 | 0.19122 | -0.20026 | -0.14108 | 0.46842 | -0.28338 | -0.69899 | 0.072628 | -0.46964 | 8.8661 | 8.867 | 2.0084 | 15.7566 | 16.6911 | 17.2382 | 17.5675 | 17.529 | 16.5165 | 14.862 | 16.8434 | 17.1767 | 17.4707 | 17.519 | 17.2591 | 16.4604 | 14.6937 | 6.0637 | 8.3567 | 5.1355 | 5.6185 | 5.9332 | 6.6309 | 7.6151 | 15.8268 | 15.5023 | 15.3704 | 14.3005 | 14.1903 | 14.135 |  |  |  | 10.6443 | 9.2236 | 8.9621 | 9.0472 | -0.16507 | 0.014328 | 12.7234 |  |  | 10.4922 |  |  | 16.887 | 16.0702 | 15.0499 | 16.385 | 15.6694 | 14.7732 | 10.2537 | 10.5136 | 11.305 | 11.3122 | 9.0605 |  | 10.5103 | 7.6828 | 9.8565 | 8.781 | 10.955 | 12.1522 |  | 12.2059 |  |  | 11.7943 | 12.4684 | 12.4982 | [6 empty] | 12.4059 |  |  | 11.2908 |  |  | 9.0518 | 10.0686 | 11.6319 | 7.446 | 9.1807 | 12.3587 | 7.8673 | 9.4965 | 12.1882 | 9.1478 | 10.4247 | 7.7438 | 10.2582 | 8.3329 | 10.2842 | 7.7098 | 9.5644 | 13.0712 | 10.3868 | 10.1182 | 11.3615 | 8.1798 | 9.7057 | 12.6664 | 8.0125 | 10.3555 | 9.7703 | 9.7776 | 8.6131 | 10.3293 | 0.011544 | 20.9571 | 0.033918 | 0.049311 | -37.7637 | 3.1203 | 3.83 | 0.25 | 0.31545 | -0.50583 | 0.28461 | 0.50946 | -0.52114 | -0.43742 | 0.79705 | 0.40737 | 0.4241 | 0.42979 | 0.41045 | 0.62785 | 0.4288 | 0.41215
42810.4377 | -205 | 18.4645 | 18.5895 | 18.5949 | 18.598 | 17.9369 | 16.5767 | 14.6512 | 16.7058 | 17.1951 | 17.2837 | 17.2952 | 16.8308 | 15.868 | 14.4937 | 14.9056 | 14.9272 | 15.5051 | 13.3684 | 13.4864 | 14.0573 |  |  |  | 16.5943 | 15.9395 | 15.0338 | 10.0623 | 9.566 | 9.4243 | 17.1585 | 16.3176 | 15.1316 | 16.873 | 16.1593 | 15.1566 | 10.7494 | 11.4423 |  | 12.0439 | 10.566 | 10.3114 | 8.5704 |  | 6.3276 | 6.3314 | 5.7887 | 5.879 | 5.9188 | 6.1041 | 6.3855 | 4.9216 | 6.4678 | 4.8954 | 6.7082 | 8.0474 | 42.1069 | 47.0587 | 42.9569 | 15.1939 |  |  | 0.014675 | -0.10637 | 0.078076 | 0.11303 | -0.10563 | -0.26462 | 0.52822 | -0.36749 | 0.79593 | -0.42082 | -0.22682 | 8.8701 | 8.8714 | 2.0084 | 15.7583 | 16.6849 | 17.2349 | 17.5681 | 17.5329 | 16.5066 | 14.8534 | 16.8398 | 17.1721 | 17.4665 | 17.5166 | 17.2539 | 16.4563 | 14.6874 | 6.0579 | 8.3761 | 5.1399 | 5.588 | 5.8848 | 6.6243 | 7.6111 | 15.8293 | 15.4888 | 15.3629 | 14.2885 | 14.1791 | 14.1279 |  |  |  | 10.6409 | 9.2438 | 8.9967 | 9.0747 | 0.034491 | 0.072482 | 12.7146 |  |  | 10.4987 |  |  | 16.8783 | 16.0782 | 15.0471 | 16.3815 | 15.6612 | 14.7695 | 10.248 | 10.5149 | 11.301 | 11.3159 | 9.0414 |  | 10.5147 | 7.7339 | 9.8524 | 8.804 | 10.9534 | 12.1979 |  | 12.2025 |  |  | 11.7727 | 12.4513 | 12.5054 | [6 empty] | 12.416 |  |  | 11.2939 |  |  | 9.0568 | 10.0696 | 11.6448 | 7.4438 | 9.1705 | 12.355 | 7.8642 | 9.4929 | 12.1805 | 9.1445 | 10.427 | 7.7358 | 10.254 | 8.326 | 10.2805 | 7.7278 | 9.5808 | 13.0676 | 10.3905 | 10.1177 | 11.3549 | 8.1855 | 9.7148 | 12.67 | 8.0176 | 10.3563 | 9.7751 | 9.7772 | 8.6143 | 10.3381 | 0.10361 | 20.9574 | 0.033395 | 0.048211 | -37.7916 | 3.1203 | 9.7 | 0.38 | 0.14191 | -0.37996 | 0.32554 | 0.39168 | -0.3785 | -0.59907 | 0.8464 | 0.40804 | 0.42255 | 0.4291 | 0.41032 | 0.6269 | 0.42886 | 0.41128
42810.4377 | -204 | 18.4728 | 18.5839 | 18.5848 | 18.5951 | 17.9448 | 16.5809 | 14.6524 | 16.6961 | 17.1946 | 17.2771 | 17.2893 | 16.8346 | 15.8651 | 14.4799 | 14.9066 | 14.9343 | 15.5085 | 13.3733 | 13.4873 | 14.0646 |  |  |  | 16.5956 | 15.9474 | 15.0396 | 10.0564 | 9.5752 | 9.4046 | 17.1619 | 16.321 | 15.1273 | 16.8751 | 16.1537 | 15.1636 | 10.7485 | 11.4628 |  | 12.0444 | 10.5578 | 10.2866 | 8.5623 |  | 6.3311 | 6.3343 | 5.7902 | 5.8864 | 5.9228 | 6.1111 | 6.381 | 4.9643 | 6.4761 | 4.9281 | 6.7175 | 8.0454 | 42.1248 | 47.0712 | 42.9877 | 15.2104 |  |  | 0.19341 | -0.14908 | 0.024192 | -0.021686 | -0.023492 | 0.23282 | 0.55056 | -0.4378 | -0.38296 | 0.67601 | -0.22484 | 8.8696 | 8.8707 | 2.0087 | 15.7612 | 16.6798 | 17.2355 | 17.5695 | 17.5368 | 16.5137 | 14.8644 | 16.8416 | 17.1776 | 17.4705 | 17.5191 | 17.2649 | 16.461 | 14.6902 | 6.0409 | 8.3851 | 5.1929 | 5.5661 | 5.8468 | 6.6275 | 7.618 | 15.8363 | 15.4929 | 15.3576 | 14.2951 | 14.188 | 14.126 |  |  |  | 10.6385 | 9.272 | 9.0356 | 9.0779 | -0.096389 | 0.0043534 | 12.7073 |  |  | 10.5038 |  |  | 16.8803 | 16.0715 | 15.0492 | 16.3743 | 15.6566 | 14.7719 | 10.2351 | 10.515 | 11.2994 | 11.3197 | 9.0361 |  | 10.5196 | 7.7895 | 9.8476 | 8.8194 | 10.9565 | 12.2472 |  | 12.205 |  |  | 11.7418 | 12.4247 | 12.4923 | [6 empty] | 12.4309 |  |  | 11.2698 |  |  | 9.0553 | 10.0629 | 11.6703 | 7.4462 | 9.1607 | 12.3473 | 7.8552 | 9.5008 | 12.1627 | 9.1424 | 10.4285 | 7.7225 | 10.2548 | 8.3157 | 10.2765 | 7.7533 | 9.5971 | 13.0781 | 10.4022 | 10.1194 | 11.3588 | 8.1895 | 9.7236 | 12.6856 | 8.0356 | 10.373 | 9.7715 | 9.771 | 8.614 | 10.3435 | 0.047753 | 20.9564 | 0.032781 | 0.04664 | -37.7942 | 3.1203 | 11.96 | 0.35 | 0.51518 | -0.44983 | 0.18121 | -0.17157 | -0.1785 | 0.56193 | 0.86412 | 0.40835 | 0.42085 | 0.42877 | 0.41258 | 0.62181 | 0.42906 | 0.41111
42810.4377 | -203 | 18.466 | 18.588 | 18.583 | 18.5883 | 17.9422 | 16.5796 | 14.6507 | 16.6965 | 17.1891 | 17.2838 | 17.2845 | 16.8365 | 15.8681 | 14.4884 | 14.9027 | 14.9342 | 15.5073 | 13.3701 | 13.4821 | 14.0578 |  |  |  | 16.5949 | 15.9373 | 15.0485 | 10.0568 | 9.5704 | 9.3943 | 17.1594 | 16.3129 | 15.1298 | 16.8609 | 16.1558 | 15.1487 | 10.7489 | 11.4945 |  | 12.0315 | 10.5425 | 10.2668 | 8.5655 |  | 6.3211 | 6.3308 | 5.7833 | 5.8882 | 5.9271 | 6.1058 | 6.3819 | 4.9859 | 6.4741 | 4.9329 | 6.7097 | 8.042 | 42.1603 | 47.0911 | 43.0319 | 15.2329 |  |  | 0.073159 | -0.24567 | 0.034048 | -0.18925 | -0.18383 | -0.10494 | 0.53019 | -0.40495 | -0.15742 | 0.041578 | -0.36572 | 8.8704 | 8.8714 | 2.0082 | 15.7599 | 16.6913 | 17.2363 | 17.5743 | 17.5386 | 16.515 | 14.8691 | 16.8425 | 17.1832 | 17.4785 | 17.5261 | 17.266 | 16.4657 | 14.6925 | 6.0222 | 8.383 | 5.2554 | 5.5593 | 5.8341 | 6.6217 | 7.6157 | 15.8174 | 15.4887 | 15.364 | 14.2896 | 14.1854 | 14.1225 |  |  |  | 10.6342 | 9.3039 | 9.0493 | 9.0488 | -0.1677 | -0.10537 | 12.6989 |  |  | 10.5019 |  |  | 16.868 | 16.0697 | 15.0345 | 16.3704 | 15.6607 | 14.76 | 10.2206 | 10.5014 | 11.2874 | 11.3289 | 8.9648 |  | 10.5116 | 7.8755 | 9.8458 | 8.8249 | 10.9484 | 12.2677 |  | 12.2067 |  |  | 11.732 | 12.4336 | 12.4827 | [6 empty] | 12.4439 |  |  | 11.2711 |  |  | 9.0491 | 10.0611 | 11.6924 | 7.4493 | 9.1697 | 12.3479 | 7.8435 | 9.4966 | 12.1586 | 9.142 | 10.4281 | 7.7348 | 10.2513 | 8.3224 | 10.2709 | 7.7759 | 9.6129 | 13.0829 | 10.4046 | 10.1252 | 11.3801 | 8.1859 | 9.7241 | 12.6923 | 8.0568 | 10.3797 | 9.7686 | 9.7758 | 8.6263 | 10.3388 | 0.025604 | 20.9583 | 0.031398 | 0.046778 | -37.8745 | 3.1203 | 5.09 | 0.25 | 0.31684 | -0.57746 | 0.21498 | -0.50683 | -0.49931 | -0.37726 | 0.84798 | 0.41007 | 0.4184 | 0.42835 | 0.414 | 0.61459 | 0.42898 | 0.41177
42810.4377 | -202 | 18.4654 | 18.5962 | 18.5876 | 18.5934 | 17.9446 | 16.5854 | 14.6538 | 16.6981 | 17.187 | 17.2856 | 17.295 | 16.8428 | 15.8663 | 14.4769 | 14.9016 | 14.9258 | 15.5093 | 13.3581 | 13.4825 | 14.055 |  |  |  | 16.5959 | 15.9415 | 15.0435 | 10.0512 | 9.5771 | 9.4099 | 17.1569 | 16.3127 | 15.122 | 16.8691 | 16.156 | 15.1533 | 10.7442 | 11.5247 |  | 12.0373 | 10.5352 | 10.2474 | 8.5565 |  | 6.3246 | 6.3273 | 5.7834 | 5.8908 | 5.9186 | 6.1014 | 6.4015 | 5.0129 | 6.4779 | 4.9614 | 6.7087 | 8.0425 | 42.1825 | 47.1166 | 43.0668 | 15.2505 |  |  | -0.028693 | -0.051169 | -0.14403 | -0.19845 | -0.10958 | -0.13977 | 0.50851 | -0.65859 | -0.32652 | -0.64405 | -0.17973 | 8.8685 | 8.8697 | 2.0085 | 15.7521 | 16.6936 | 17.2319 | 17.5718 | 17.5308 | 16.51 | 14.8656 | 16.8379 | 17.18 | 17.474 | 17.5238 | 17.2615 | 16.4635 | 14.6973 | 6.008 | 8.3804 | 5.2904 | 5.5816 | 5.8459 | 6.6206 | 7.6105 | 15.8145 | 15.4931 | 15.3631 | 14.2947 | 14.1775 | 14.121 |  |  |  | 10.6402 | 9.3254 | 9.049 | 9.0382 | 0.045836 | 0.010564 | 12.6994 |  |  | 10.5107 |  |  | 16.8779 | 16.0753 | 15.0486 | 16.3774 | 15.6661 | 14.7666 | 10.2154 | 10.5052 | 11.3012 | 11.3391 | 8.8827 |  | 10.5084 | 7.9653 | 9.8479 | 8.8343 | 10.9526 | 12.2632 |  | 12.1992 |  |  | 11.7037 | 12.4242 | 12.4757 | [6 empty] | 12.4543 |  |  | 11.2541 |  |  | 9.056 | 10.0695 | 11.6992 | 7.4568 | 9.1781 | 12.3406 | 7.8395 | 9.5035 | 12.1609 | 9.1348 | 10.4515 | 7.7337 | 10.2541 | 8.3234 | 10.272 | 7.7936 | 9.6121 | 13.0767 | 10.4035 | 10.125 | 11.3809 | 8.1717 | 9.7233 | 12.6885 | 8.0661 | 10.3791 | 9.7645 | 9.7679 | 8.6246 | 10.3163 | 0.11439 | 20.9585 | 0.03091 | 0.046467 | -37.8927 | 3.1203 | -3.7 | 0.34 | -0.19843 | -0.26354 | -0.44214 | -0.519 | -0.3855 | -0.43538 | 0.83045 | 0.41224 | 0.41597 | 0.42823 | 0.41544 | 0.6101 | 0.42907 | 0.41226
42810.4377 | -201 | 18.4688 | 18.5948 | 18.5854 | 18.5985 | 17.9385 | 16.5779 | 14.6524 | 16.7041 | 17.1835 | 17.2828 | 17.2916 | 16.8357 | 15.8682 | 14.4819 | 14.8998 | 14.9291 | 15.495 | 13.3654 | 13.477 | 14.0523 |  |  |  | 16.5914 | 15.9315 | 15.0318 | 10.0442 | 9.5782 | 9.4563 | 17.1598 | 16.3108 | 15.1225 | 16.8728 | 16.1642 | 15.1616 | 10.7442 | 11.5522 |  | 12.0356 | 10.5324 | 10.2408 | 8.5736 |  | 6.3221 | 6.3179 | 5.7863 | 5.894 | 5.9162 | 6.0965 | 6.4333 | 5.0538 | 6.4883 | 5.0374 | 6.7091 | 8.0517 | 42.2057 | 47.1479 | 43.0981 | 15.2701 |  |  | 0.1139 | 0.096027 | -0.10723 | -0.20173 | 0.046164 | -0.16868 | 0.58605 | -0.37538 | -0.66182 | -0.10696 | -0.29756 | 8.8682 | 8.8696 | 2.0085 | 15.7533 | 16.6867 | 17.2344 | 17.5664 | 17.5283 | 16.5069 | 14.8668 | 16.839 | 17.1732 | 17.4706 | 17.5229 | 17.256 | 16.4594 | 14.6957 | 6.0088 | 8.3899 | 5.3983 | 5.6054 | 5.8506 | 6.6181 | 7.6175 | 15.8199 | 15.4911 | 15.3609 | 14.2941 | 14.1807 | 14.1307 |  |  |  | 10.6437 | 9.3293 | 9.0477 | 9.058 | 0.11654 | 0.048957 | 12.6909 |  |  | 10.5233 |  |  | 16.8767 | 16.0695 | 15.051 | 16.3762 | 15.6594 | 14.7657 | 10.2104 | 10.5121 | 11.2925 | 11.3316 | 8.7988 |  | 10.5115 | 8.1025 | 9.851 | 8.8487 | 10.9542 | 12.2511 |  | 12.2022 |  |  | 11.688 | 12.4209 | 12.4727 | [6 empty] | 12.4684 |  |  | 11.2541 |  |  | 9.0463 | 10.0736 | 11.7033 | 7.4741 | 9.1832 | 12.3637 | 7.8524 | 9.5104 | 12.163 | 9.1437 | 10.4646 | 7.7365 | 10.2722 | 8.3295 | 10.2667 | 7.8182 | 9.6198 | 13.083 | 10.4053 | 10.1378 | 11.3837 | 8.1696 | 9.7254 | 12.691 | 8.0762 | 10.3735 | 9.7655 | 9.7709 | 8.6378 | 10.3204 | -0.034873 | 20.9582 | 0.031151 | 0.04748 | -37.9407 | 3.1203 | 9.15 | 0.26 | 0.39538 | 0.36102 | -0.3815 | -0.52327 | 0.25021 | -0.47829 | 0.89151 | 0.41467 | 0.41226 | 0.42789 | 0.41505 | 0.59894 | 0.4286 | 0.41183
42810.4377 | -200 | 18.4747 | 18.5904 | 18.5883 | 18.5938 | 17.9406 | 16.5746 | 14.6541 | 16.701 | 17.1931 | 17.2825 | 17.2902 | 16.8365 | 15.866 | 14.4848 | 14.904 | 14.9265 | 15.5029 | 13.3608 | 13.4778 | 14.0495 |  |  |  | 16.5896 | 15.9328 | 15.0361 | 10.0541 | 9.5849 | 9.5512 | 17.1637 | 16.3185 | 15.1227 | 16.8775 | 16.161 | 15.1631 | 10.7469 | 11.583 |  | 12.04 | 10.5286 | 10.2356 | 8.5941 |  | 6.3289 | 6.33 | 5.7949 | 5.8982 | 5.9254 | 6.0959 | 6.4959 | 5.0772 | 6.495 | 5.1557 | 6.7071 | 8.0468 | 42.2145 | 47.1711 | 43.1132 | 15.2745 |  |  | -0.027381 | -0.21611 | -0.053348 | -0.21948 | -0.026776 | -0.080628 | 0.44477 | -0.49432 | 0.11892 | -0.9791 | -0.34724 | 8.8723 | 8.8734 | 2.0086 | 15.7472 | 16.675 | 17.2241 | 17.5552 | 17.5169 | 16.5032 | 14.8538 | 16.8285 | 17.1715 | 17.4668 | 17.5146 | 17.2488 | 16.461 | 14.6829 | 6.0052 | 8.3853 | 5.5442 | 5.6443 | 5.8636 | 6.6302 | 7.6187 | 15.8239 | 15.4935 | 15.3574 | 14.2979 | 14.1844 | 14.1322 |  |  |  | 10.643 | 9.3294 | 9.0518 | 9.0569 | 0.11715 | 0.13214 | 12.6798 |  |  | 10.5207 |  |  | 16.8857 | 16.0648 | 15.0539 | 16.3845 | 15.6597 | 14.7645 | 10.2131 | 10.5181 | 11.2932 | 11.3387 | 8.7365 |  | 10.5078 | 8.2123 | 9.8406 | 8.8614 | 10.9418 | 12.208 |  | 12.196 |  |  | 11.6813 | 12.4164 | 12.4836 | [6 empty] | 12.4742 |  |  | 11.2394 |  |  | 9.041 | 10.0665 | 11.6935 | 7.4652 | 9.165 | 12.3655 | 7.8438 | 9.4981 | 12.1502 | 9.1397 | 10.452 | 7.7174 | 10.2585 | 8.326 | 10.2448 | 7.8454 | 9.6262 | 13.0926 | 10.4091 | 10.1481 | 11.3731 | 8.1604 | 9.7409 | 12.6918 | 8.0868 | 10.3745 | 9.76 | 9.7766 | 8.6275 | 10.3247 | 0.01347 | 20.9562 | 0.031438 | 0.047371 | -37.907 | 3.1203 | 10.28 | 0.21 | -0.19389 | -0.5416 | -0.26909 | -0.54581 | -0.19056 | -0.33068 | 0.77665 | 0.41628 | 0.40887 | 0.42712 | 0.41687 | 0.58285 | 0.42812 | 0.41184
42810.4377 | -199 | 18.4705 | 18.5898 | 18.5871 | 18.5965 | 17.9378 | 16.5817 | 14.6532 | 16.6992 | 17.1934 | 17.2851 | 17.289 | 16.8364 | 15.8653 | 14.4885 | 14.9092 | 14.9308 | 15.5079 | 13.3555 | 13.4788 | 14.051 |  |  |  | 16.5984 | 15.9296 | 15.0366 | 10.0613 | 9.5813 | 9.6681 | 17.154 | 16.3079 | 15.1208 | 16.868 | 16.1571 | 15.154 | 10.747 | 11.6044 |  | 12.0383 | 10.5134 | 10.2305 | 8.623 |  | 6.3352 | 6.331 | 5.7942 | 5.9045 | 5.932 | 6.1502 | 6.5526 | 5.0865 | 6.4982 | 5.146 | 6.7122 | 8.0453 | 42.2338 | 47.1727 | 43.1407 | 15.2968 |  |  | -0.033293 | -0.10834 | -0.05532 | -0.10251 | 0.016592 | -0.18774 | 0.43163 | -0.4608 | -0.99575 | -1.6419 | -0.42592 | 8.8688 | 8.8699 | 2.0084 | 15.7521 | 16.6777 | 17.2363 | 17.5647 | 17.5313 | 16.5068 | 14.8665 | 16.8391 | 17.1841 | 17.4764 | 17.5313 | 17.2587 | 16.4688 | 14.6944 | 5.9885 | 8.4022 | 5.7135 | 5.6688 | 5.8893 | 6.6263 | 7.6194 | 15.8167 | 15.4865 | 15.3587 | 14.2947 | 14.1842 | 14.1271 |  |  |  | 10.6408 | 9.3249 | 9.06 | 9.0732 | 0.055764 | -0.030464 | 12.6901 |  |  | 10.5296 |  |  | 16.8859 | 16.0729 | 15.0552 | 16.3869 | 15.6655 | 14.7705 | 10.22 | 10.5257 | 11.2943 | 11.3471 | 8.7386 |  | 10.4996 | 8.3127 | 9.8348 | 8.8818 | 10.9423 | 12.1661 |  | 12.193 |  |  | 11.6938 | 12.415 | 12.4793 | [6 empty] | 12.4502 |  |  | 11.239 |  |  | 9.0602 | 10.0779 | 11.7038 | 7.4718 | 9.169 | 12.3849 | 7.8503 | 9.5005 | 12.1576 | 9.154 | 10.4762 | 7.7179 | 10.2562 | 8.3219 | 10.25 | 7.856 | 9.625 | 13.0823 | 10.4052 | 10.1463 | 11.3793 | 8.1605 | 9.7431 | 12.6866 | 8.0873 | 10.3689 | 9.7577 | 9.7647 | 8.6313 | 10.3245 | -0.050088 | 20.9576 | 0.031255 | 0.047994 | -37.8628 | 3.1203 | -8.21 | 0.28 | -0.21384 | -0.38347 | -0.27402 | -0.37301 | 0.15002 | -0.50463 | 0.76517 | 0.41596 | 0.40589 | 0.42657 | 0.41827 | 0.56412 | 0.42732 | 0.41132
42810.4377 | -198 | 18.4826 | 18.5986 | 18.5995 | 18.6033 | 17.9468 | 16.5989 | 14.66 | 16.7123 | 17.2002 | 17.2976 | 17.3037 | 16.8407 | 15.8771 | 14.4951 | 14.9041 | 14.9373 | 15.5113 | 13.3598 | 13.4798 | 14.0583 |  |  |  | 16.5983 | 15.9383 | 15.0382 | 10.0724 | 9.5812 | 9.8039 | 17.1495 | 16.3035 | 15.1164 | 16.8632 | 16.151 | 15.1501 | 10.7407 | 11.6218 |  | 12.0302 | 10.5075 | 10.2223 | 8.6513 |  | 6.3269 | 6.3366 | 5.7973 | 5.9056 | 5.9768 | 6.2028 | 6.6116 | 5.127 | 6.5 | 5.0882 | 6.7115 | 8.0515 | 42.2492 | 47.1887 | 43.1566 | 15.3039 |  |  | 0.15135 | -0.19179 | -0.13023 | 0.098566 | -0.10234 | 0.14148 | 0.36066 | -0.49563 | -0.35727 | 0.47083 | -0.54892 | 8.872 | 8.8733 | 2.0083 | 15.7502 | 16.6813 | 17.2417 | 17.5667 | 17.544 | 16.5122 | 14.8702 | 16.8418 | 17.1808 | 17.4801 | 17.5289 | 17.2684 | 16.4748 | 14.694 | 5.969 | 8.4316 | 5.8191 | 5.6923 | 5.8985 | 6.615 | 7.6128 | 15.8064 | 15.4902 | 15.3531 | 14.2974 | 14.1829 | 14.124 |  |  |  | 10.637 | 9.327 | 9.0582 | 9.0832 | -0.012918 | 0.027878 | 12.6897 |  |  | 10.5389 |  |  | 16.8898 | 16.074 | 15.0516 | 16.3747 | 15.667 | 14.772 | 10.2226 | 10.5339 | 11.2973 | 11.3447 | 8.7084 |  | 10.5066 | 8.3579 | 9.8437 | 8.9055 | 10.9484 | 12.1471 |  | 12.2016 |  |  | 11.698 | 12.415 | 12.4752 | [6 empty] | 12.4674 |  |  | 11.2382 |  |  | 9.0661 | 10.0774 | 11.7113 | 7.4729 | 9.1788 | 12.4024 | 7.8587 | 9.4972 | 12.1441 | 9.1604 | 10.492 | 7.7178 | 10.2685 | 8.3272 | 10.2498 | 7.8671 | 9.6257 | 13.1049 | 10.4071 | 10.1525 | 11.3816 | 8.1703 | 9.7534 | 12.6966 | 8.0965 | 10.3753 | 9.7532 | 9.7696 | 8.6309 | 10.3178 | 0.04833 | 20.9557 | 0.032052 | 0.048233 | -37.7978 | 3.1203 | 4.36 | 0.33 | 0.45606 | -0.51022 | -0.42044 | 0.36577 | -0.37263 | 0.43811 | 0.6995 | 0.41702 | 0.40493 | 0.42612 | 0.41912 | 0.55162 | 0.42633 | 0.41091
42810.4378 | -197 | 18.4853 | 18.599 | 18.5912 | 18.6019 | 17.9487 | 16.5893 | 14.6589 | 16.7089 | 17.2039 | 17.2953 | 17.3021 | 16.839 | 15.8752 | 14.4933 | 14.9005 | 14.9289 | 15.5028 | 13.3592 | 13.4783 | 14.0506 |  |  |  | 16.6025 | 15.9308 | 15.0355 | 10.0859 | 9.5812 | 9.9387 | 17.158 | 16.3069 | 15.115 | 16.864 | 16.1508 | 15.1486 | 10.7382 | 11.6253 |  | 12.035 | 10.4962 | 10.2105 | 8.7007 |  | 6.3298 | 6.3356 | 5.7999 | 5.9088 | 6.001 | 6.2184 | 6.659 | 5.1618 | 6.5036 | 5.1012 | 6.7164 | 8.0477 | 42.2532 | 47.2174 | 43.1812 | 15.3173 |  |  | 0.090903 | -0.21939 | -0.030348 | -0.16691 | 0.020536 | -0.46898 | 0.57488 | -0.37209 | -0.23623 | -0.4781 | -0.35459 | 8.87 | 8.8712 | 2.0085 | 15.7487 | 16.6808 | 17.2379 | 17.5672 | 17.535 | 16.5104 | 14.866 | 16.8418 | 17.1819 | 17.4768 | 17.5238 | 17.2569 | 16.4668 | 14.6897 | 5.9685 | 8.4481 | 5.9304 | 5.7151 | 5.8967 | 6.618 | 7.6115 | 15.8159 | 15.4836 | 15.3644 | 14.3054 | 14.1911 | 14.1337 |  |  |  | 10.6502 | 9.3354 | 9.0741 | 9.117 | 0.041784 | 0.061378 | 12.6854 |  |  | 10.5272 |  |  | 16.8721 | 16.0712 | 15.0428 | 16.3775 | 15.6639 | 14.7661 | 10.2254 | 10.5421 | 11.2962 | 11.3461 | 8.6786 |  | 10.5086 | 8.3491 | 9.8437 | 8.9502 | 10.9519 | 12.1162 |  | 12.1999 |  |  | 11.6752 | 12.4046 | 12.4744 | [6 empty] | 12.4807 |  |  | 11.237 |  |  | 9.0653 | 10.066 | 11.7419 | 7.4721 | 9.1678 | 12.4034 | 7.8402 | 9.4883 | 12.1402 | 9.1606 | 10.4914 | 7.7066 | 10.274 | 8.3178 | 10.2384 | 7.8637 | 9.6235 | 13.1147 | 10.4173 | 10.1546 | 11.3828 | 8.1707 | 9.7595 | 12.6952 | 8.1037 | 10.3711 | 9.7472 | 9.7757 | 8.6236 | 10.321 | -0.081867 | 20.9557 | 0.03277 | 0.048088 | -37.834 | 3.1203 | 1.81 | 0.31 | 0.35352 | -0.5457 | -0.20296 | -0.47597 | 0.16692 | -0.79769 | 0.88317 | 0.41792 | 0.40517 | 0.42499 | 0.41952 | 0.53911 | 0.42487 | 0.41041
42810.4378 | -196 | 18.4666 | 18.5882 | 18.5883 | 18.5968 | 17.9455 | 16.589 | 14.6541 | 16.7121 | 17.1954 | 17.2871 | 17.2945 | 16.8324 | 15.8661 | 14.4853 | 14.9013 | 14.9275 | 15.5009 | 13.3635 | 13.4833 | 14.0537 |  |  |  | 16.6021 | 15.9339 | 15.0337 | 10.1151 | 9.5813 | 10.0919 | 17.1654 | 16.3097 | 15.1267 | 16.8715 | 16.1572 | 15.1557 | 10.7498 | 11.6446 |  | 12.0441 | 10.505 | 10.22 | 8.796 |  | 6.3269 | 6.3405 | 5.7919 | 5.9143 | 6.0202 | 6.2706 | 6.7063 | 5.1817 | 6.4989 | 5.0677 | 6.7111 | 8.0399 | 42.2529 | 47.2188 | 43.1867 | 15.3199 |  |  | 0.027159 | -0.21545 | 0.023536 | -0.13799 | 0.032364 | -0.026088 | 0.52954 | -0.33529 | -0.99517 | -0.37383 | -0.33094 | 8.867 | 8.8682 | 2.0085 | 15.746 | 16.6843 | 17.241 | 17.5721 | 17.5338 | 16.5151 | 14.8623 | 16.8453 | 17.1898 | 17.4746 | 17.5261 | 17.2612 | 16.4674 | 14.7005 | 6.0012 | 8.4764 | 5.8912 | 5.7451 | 5.9036 | 6.6181 | 7.6208 | 15.8152 | 15.4883 | 15.3548 | 14.2974 | 14.1836 | 14.1312 |  |  |  | 10.6433 | 9.3363 | 9.0762 | 9.1431 | -0.021022 | 0.044064 | 12.6884 |  |  | 10.5251 |  |  | 16.873 | 16.0662 | 15.0516 | 16.3912 | 15.6621 | 14.7756 | 10.235 | 10.553 | 11.2853 | 11.3486 | 8.6286 |  | 10.4983 | 8.4168 | 9.8459 | 9.0106 | 10.9467 | 12.0874 |  | 12.1945 |  |  | 11.6645 | 12.3815 | 12.4919 | [6 empty] | 12.4794 |  |  | 11.2454 |  |  | 9.0742 | 10.0746 | 11.7525 | 7.4778 | 9.1614 | 12.4196 | 7.8446 | 9.4918 | 12.1263 | 9.161 | 10.5058 | 7.7171 | 10.276 | 8.3178 | 10.2451 | 7.8542 | 9.6295 | 13.1237 | 10.4261 | 10.1567 | 11.3767 | 8.1756 | 9.7538 | 12.6866 | 8.0958 | 10.3636 | 9.7537 | 9.7854 | 8.615 | 10.3069 | -0.20321 | 20.9558 | 0.033699 | 0.048015 | -37.8841 | 3.1202 | -1.3 | 0.39 | 0.19329 | -0.54078 | 0.17874 | -0.43279 | 0.20957 | -0.18816 | 0.8477 | 0.41897 | 0.40337 | 0.42314 | 0.4159 | 0.54455 | 0.42261 | 0.40945
42810.4378 | -195 | 18.4808 | 18.5919 | 18.5917 | 18.6006 | 17.9441 | 16.5856 | 14.6587 | 16.7122 | 17.1923 | 17.288 | 17.2955 | 16.8408 | 15.8646 | 14.4869 | 14.9014 | 14.9233 | 15.4991 | 13.3649 | 13.4772 | 14.0485 |  |  |  | 16.6019 | 15.9345 | 15.0371 | 10.1432 | 9.5807 | 10.2296 | 17.1512 | 16.3082 | 15.1193 | 16.8624 | 16.1584 | 15.1502 | 10.7352 | 11.6592 |  | 12.0399 | 10.486 | 10.2172 | 8.8357 |  | 6.3317 | 6.3437 | 5.7986 | 5.9329 | 6.0609 | 6.3263 | 6.7616 | 5.1631 | 6.5109 | 5.0093 | 6.7137 | 8.0499 | 42.2656 | 47.2482 | 43.2 | 15.3244 |  |  | 0.052787 | -0.20296 | -0.052692 | 0.038114 | 0.048132 | -0.29945 | 0.56568 | -0.51074 | 0.44273 | -0.026817 | -0.40486 | 8.8722 | 8.8735 | 2.0086 | 15.7399 | 16.6727 | 17.2388 | 17.5623 | 17.5309 | 16.5073 | 14.8572 | 16.8373 | 17.177 | 17.4714 | 17.5161 | 17.2584 | 16.4714 | 14.6901 | 6.0451 | 8.4736 | 5.83 | 5.7521 | 5.9033 | 6.6142 | 7.6118 | 15.8054 | 15.4865 | 15.3511 | 14.2902 | 14.1762 | 14.1219 |  |  |  | 10.6392 | 9.3351 | 9.0839 | 9.1714 | -0.060326 | 0.18408 | 12.6705 |  |  | 10.497 |  |  | 16.8709 | 16.0697 | 15.0449 | 16.3669 | 15.6569 | 14.7677 | 10.245 | 10.5639 | 11.2767 | 11.3382 | 8.6159 |  | 10.4821 | 8.4974 | 9.8322 | 9.0413 | 10.9357 | 12.0598 |  | 12.197 |  |  | 11.5912 | 12.341 | 12.4505 | [6 empty] | 12.4713 |  |  | 11.2188 |  |  | 9.081 | 10.0773 | 11.7407 | 7.474 | 9.143 | 12.4204 | 7.8359 | 9.4912 | 12.1179 | 9.1672 | 10.5097 | 7.7056 | 10.2827 | 8.3144 | 10.248 | 7.862 | 9.6368 | 13.1512 | 10.4419 | 10.176 | 11.3845 | 8.1917 | 9.7703 | 12.704 | 8.1014 | 10.3677 | 9.7623 | 9.8029 | 8.6205 | 10.3156 | 0.027337 | 20.9561 | 0.033809 | 0.048877 | -37.9894 | 3.1202 | 11.32 | 0.18 | 0.26953 | -0.52488 | -0.26744 | 0.22745 | 0.2556 | -0.63753 | 0.87624 | 0.41879 | 0.40067 | 0.42192 | 0.41057 | 0.55029 | 0.42102 | 0.40854
42810.4378 | -194 | 18.4842 | 18.588 | 18.5864 | 18.6002 | 17.9345 | 16.5812 | 14.654 | 16.7014 | 17.1912 | 17.2849 | 17.2946 | 16.8334 | 15.8635 | 14.4785 | 14.9008 | 14.9287 | 15.4954 | 13.3669 | 13.4777 | 14.056 |  |  |  | 16.6069 | 15.9351 | 15.0357 | 10.1655 | 9.5814 | 10.3389 | 17.1567 | 16.3051 | 15.1179 | 16.8627 | 16.1489 | 15.1475 | 10.7373 | 11.6685 |  | 12.0393 | 10.4861 | 10.2232 | 8.8389 |  | 6.3373 | 6.3476 | 5.8185 | 5.9589 | 6.0984 | 6.3518 | 6.8101 | 5.1185 | 6.5183 | 5.0153 | 6.7189 | 8.0473 | 42.2782 | 47.2728 | 43.2108 | 15.3267 |  |  | 0.13493 | -0.001225 | -0.07766 | 0.068998 | 0.12896 | -0.1608 | 0.47302 | -0.1375 | -0.2804 | -0.90735 | -0.45275 | 8.8699 | 8.8707 | 2.0083 | 15.7405 | 16.678 | 17.2271 | 17.5632 | 17.526 | 16.51 | 14.8597 | 16.8347 | 17.1728 | 17.4697 | 17.5199 | 17.2574 | 16.4645 | 14.6963 | 6.0811 | 8.4605 | 5.7796 | 5.7626 | 5.9095 | 6.6142 | 7.6092 | 15.8024 | 15.4812 | 15.3608 | 14.2957 | 14.1719 | 14.1244 |  |  |  | 10.6489 | 9.3441 | 9.0896 | 9.1874 | 0.033883 | -0.029146 | 12.6761 |  |  | 10.5046 |  |  | 16.8739 | 16.0649 | 15.0467 | 16.3769 | 15.6571 | 14.7657 | 10.257 | 10.582 | 11.2785 | 11.3402 | 8.6221 |  | 10.4879 | 8.5763 | 9.8401 | 9.0802 | 10.9389 | 12.0289 |  | 12.1961 |  |  | 11.5389 | 12.3184 | 12.4196 | [6 empty] | 12.4633 |  |  | 11.2088 |  |  | 9.0906 | 10.0792 | 11.7341 | 7.4746 | 9.1428 | 12.4184 | 7.8327 | 9.4972 | 12.1297 | 9.1775 | 10.5187 | 7.7077 | 10.2844 | 8.3196 | 10.2491 | 7.8618 | 9.6265 | 13.1639 | 10.4512 | 10.1808 | 11.3895 | 8.1917 | 9.7744 | 12.7098 | 8.0926 | 10.3679 | 9.7618 | 9.8108 | 8.6126 | 10.3095 | -0.058948 | 20.9563 | 0.033929 | 0.049296 | -37.9854 | 3.1202 | 23.85 | 0.32 | 0.43101 | -0.040778 | -0.32468 | 0.30604 | 0.4184 | -0.46719 | 0.80131 | 0.4188 | 0.39874 | 0.42095 | 0.40657 | 0.5556 | 0.421 | 0.40841
42810.4378 | -193 | 18.4777 | 18.581 | 18.5831 | 18.5923 | 17.9326 | 16.5752 | 14.6514 | 16.697 | 17.1855 | 17.2819 | 17.2939 | 16.8293 | 15.8648 | 14.4754 | 14.8966 | 14.9247 | 15.4936 | 13.3621 | 13.4734 | 14.0515 |  |  |  | 16.6039 | 15.93 | 15.0348 | 10.1898 | 9.5778 | 10.4124 | 17.1553 | 16.3011 | 15.121 | 16.8555 | 16.1482 | 15.1473 | 10.737 | 11.676 |  | 12.0402 | 10.4808 | 10.2222 | 8.8085 |  | 6.3279 | 6.3417 | 5.8135 | 5.9629 | 6.1174 | 6.3461 | 6.8526 | 5.0869 | 6.5152 | 5.0598 | 6.7105 | 8.0428 | 42.2779 | 47.2899 | 43.2241 | 15.3168 |  |  | 0.19867 | -0.18325 | 0.058364 | 0.008542 | -0.056348 | 0.052768 | 0.55911 | 0.070804 | -0.16053 | -0.20368 | -0.47103 | 8.8705 | 8.8714 | 2.0086 | 15.742 | 16.6861 | 17.2261 | 17.5625 | 17.5338 | 16.5168 | 14.8574 | 16.8419 | 17.1836 | 17.4716 | 17.5169 | 17.2592 | 16.4726 | 14.6963 | 6.1115 | 8.4758 | 5.74 | 5.8057 | 5.9165 | 6.6248 | 7.6057 | 15.7964 | 15.4804 | 15.3516 | 14.2852 | 14.1696 | 14.1205 |  |  |  | 10.6405 | 9.344 | 9.0818 | 9.2167 | 0.11249 | 0.0019068 | 12.6687 |  |  | 10.5056 |  |  | 16.8686 | 16.0628 | 15.0395 | 16.3758 | 15.6545 | 14.7663 | 10.2591 | 10.591 | 11.2706 | 11.3154 | 8.637 |  | 10.4954 | 8.6414 | 9.8306 | 9.1285 | 10.9516 | 12.0003 |  | 12.2083 |  |  | 11.4984 | 12.291 | 12.391 | [6 empty] | 12.4547 |  |  | 11.2093 |  |  | 9.0941 | 10.0799 | 11.7334 | 7.4649 | 9.1362 | 12.4273 | 7.8364 | 9.4963 | 12.1419 | 9.176 | 10.521 | 7.7011 | 10.2723 | 8.329 | 10.2517 | 7.8624 | 9.6263 | 13.161 | 10.4555 | 10.1853 | 11.3932 | 8.1957 | 9.7779 | 12.7113 | 8.0784 | 10.3646 | 9.7648 | 9.8192 | 8.6079 | 10.2991 | 0.17102 | 20.9562 | 0.034078 | 0.049347 | -37.9242 | 3.1202 | 8.19 | 0.34 | 0.52306 | -0.49874 | 0.28146 | 0.10768 | -0.27656 | 0.26763 | 0.87117 | 0.41864 | 0.39662 | 0.42003 | 0.40443 | 0.55959 | 0.42184 | 0.40732
42810.4378 | -192 | 18.4821 | 18.5848 | 18.5852 | 18.5946 | 17.9375 | 16.5815 | 14.6467 | 16.7071 | 17.1915 | 17.2895 | 17.2933 | 16.8336 | 15.8674 | 14.4838 | 14.895 | 14.931 | 15.4968 | 13.3656 | 13.4788 | 14.0495 |  |  |  | 16.6008 | 15.9322 | 15.0406 | 10.2131 | 9.5786 | 10.4648 | 17.1449 | 16.3029 | 15.1258 | 16.8577 | 16.1514 | 15.1443 | 10.7322 | 11.6704 |  | 12.0432 | 10.4799 | 10.2215 | 8.7914 |  | 6.3361 | 6.3506 | 5.8247 | 5.9739 | 6.1317 | 6.3626 | 6.9046 | 5.0522 | 6.514 | 5.0737 | 6.7206 | 8.0412 | 42.2987 | 47.3138 | 43.2408 | 15.3135 |  |  | 0.002191 | 0.000747 | 0.061648 | 0.018398 | -0.03532 | -0.046456 | 0.60773 | -0.080332 | -0.57016 | -0.09731 | -0.27272 | 8.8707 | 8.8718 | 2.0081 | 15.7338 | 16.6768 | 17.2297 | 17.5646 | 17.5234 | 16.5034 | 14.8584 | 16.8348 | 17.1744 | 17.4748 | 17.5218 | 17.2559 | 16.4649 | 14.693 | 6.2466 | 8.4814 | 5.7249 | 5.8861 | 5.9601 | 6.6286 | 7.6141 | 15.7947 | 15.4684 | 15.3414 | 14.282 | 14.1687 | 14.1096 |  |  |  | 10.6401 | 9.3374 | 9.0757 | 9.2243 | -0.12516 | -0.021054 | 12.6663 |  |  | 10.5138 |  |  | 16.8652 | 16.0606 | 15.0405 | 16.374 | 15.6635 | 14.7734 | 10.2568 | 10.6099 | 11.2674 | 11.3281 | 8.6442 |  | 10.4913 | 8.672 | 9.8306 | 9.1653 | 10.954 | 11.975 |  | 12.209 |  |  | 11.4772 | 12.2282 | 12.3157 | [6 empty] | 12.4486 |  |  | 11.2224 |  |  | 9.1057 | 10.089 | 11.7349 | 7.4473 | 9.1297 | 12.4315 | 7.8328 | 9.5017 | 12.1495 | 9.1782 | 10.5216 | 7.6907 | 10.2606 | 8.3306 | 10.2581 | 7.8664 | 9.6319 | 13.1644 | 10.4615 | 10.1878 | 11.3932 | 8.1918 | 9.778 | 12.7117 | 8.0633 | 10.3685 | 9.7687 | 9.831 | 8.605 | 10.2995 | -0.026591 | 20.9556 | 0.034285 | 0.04913 | -37.9669 | 3.1202 | -12.92 | 0.3 | 0.054935 | 0.031843 | 0.28928 | 0.15803 | -0.21897 | -0.25112 | 0.90829 | 0.4183 | 0.39577 | 0.41908 | 0.38985 | 0.56224 | 0.42216 | 0.40709
42810.4378 | -191 | 18.477 | 18.5901 | 18.5905 | 18.5982 | 17.9382 | 16.5879 | 14.6519 | 16.7078 | 17.1959 | 17.2895 | 17.297 | 16.8349 | 15.8692 | 14.4848 | 14.8967 | 14.9306 | 15.4957 | 13.36 | 13.4805 | 14.0515 |  |  |  | 16.597 | 15.9371 | 15.0411 | 10.2313 | 9.5845 | 10.5115 | 17.1539 | 16.3113 | 15.123 | 16.8626 | 16.1485 | 15.1491 | 10.7342 | 11.6727 |  | 12.0478 | 10.4874 | 10.2208 | 8.8058 |  | 6.3382 | 6.3513 | 5.8266 | 5.9801 | 6.1201 | 6.3587 | 6.9253 | 5.0099 | 6.5133 | 5.0199 | 6.7229 | 8.0401 | 42.3233 | 47.3362 | 43.2509 | 15.2994 |  |  | 0.2381 | -0.16288 | 0.21344 | -0.13471 | -0.096432 | -0.14634 | 0.66424 | -0.22884 | -0.59974 | -0.28739 | -0.4899 | 8.8698 | 8.8711 | 2.0086 | 15.7341 | 16.6732 | 17.2233 | 17.5582 | 17.5271 | 16.5029 | 14.8503 | 16.8401 | 17.1727 | 17.4723 | 17.5143 | 17.2568 | 16.4665 | 14.6937 | 6.3593 | 8.4796 | 5.7088 | 5.9457 | 5.9907 | 6.6116 | 7.6046 | 15.7923 | 15.4674 | 15.3405 | 14.2831 | 14.1702 | 14.1187 |  |  |  | 10.6344 | 9.3385 | 9.0873 | 9.2397 | 0.018485 | -0.047778 | 12.6693 |  |  | 10.5087 |  |  | 16.8649 | 16.065 | 15.0409 | 16.3677 | 15.6595 | 14.7663 | 10.2667 | 10.6302 | 11.2592 | 11.3007 | 8.6709 |  | 10.4911 | 8.732 | 9.8278 | 9.2148 | 10.951 | 11.9463 |  | 12.2016 |  |  | 11.4757 | 12.2406 | 12.3287 | [6 empty] | 12.4464 |  |  | 11.233 |  |  | 9.1204 | 10.1001 | 11.7272 | 7.4438 | 9.1395 | 12.4428 | 7.8503 | 9.517 | 12.1597 | 9.1875 | 10.5326 | 7.6975 | 10.2619 | 8.3346 | 10.2698 | 7.8767 | 9.6353 | 13.168 | 10.4688 | 10.189 | 11.3958 | 8.1941 | 9.7775 | 12.7115 | 8.0641 | 10.3657 | 9.7704 | 9.8405 | 8.6041 | 10.3084 | 0.18874 | 20.9542 | 0.033757 | 0.050194 | -37.8624 | 3.1202 | 16.79 | 0.32 | 0.57272 | -0.47021 | 0.53827 | -0.42762 | -0.36181 | -0.4457 | 0.94957 | 0.41756 | 0.39401 | 0.41761 | 0.37536 | 0.56292 | 0.42182 | 0.40648
42810.4378 | -190 | 18.4745 | 18.595 | 18.5913 | 18.596 | 17.9443 | 16.5826 | 14.6519 | 16.6998 | 17.1945 | 17.2829 | 17.2928 | 16.8362 | 15.8739 | 14.475 | 14.8986 | 14.9174 | 15.4891 | 13.3502 | 13.4706 | 14.0405 |  |  |  | 16.5895 | 15.9229 | 15.0308 | 10.2408 | 9.5725 | 10.5385 | 17.1509 | 16.3069 | 15.1161 | 16.861 | 16.1519 | 15.1455 | 10.7283 | 11.6726 |  | 12.048 | 10.4891 | 10.2178 | 8.8387 |  | 6.3392 | 6.3593 | 5.8417 | 5.9952 | 6.1209 | 6.3532 | 6.9112 | 5.0382 | 6.5207 | 4.9983 | 6.719 | 8.0375 | 42.3384 | 47.3715 | 43.2856 | 15.2989 |  |  | 0.19538 | -0.16353 | 0.12408 | 0.08477 | -0.055692 | -0.25674 | 0.51705 | -0.19073 | -0.70989 | -0.49551 | -0.2465 | 8.8694 | 8.8707 | 2.0083 | 15.7305 | 16.6689 | 17.2334 | 17.554 | 17.5314 | 16.5029 | 14.8604 | 16.8371 | 17.1739 | 17.4703 | 17.5206 | 17.2547 | 16.4641 | 14.6933 | 6.4585 | 8.4809 | 5.7286 | 6.0077 | 6.0714 | 6.6295 | 7.6092 | 15.7859 | 15.4673 | 15.3394 | 14.2804 | 14.1696 | 14.1131 |  |  |  | 10.6358 | 9.345 | 9.0954 | 9.2683 | 0.0010618 | -0.012396 | 12.6687 |  |  | 10.515 |  |  | 16.8623 | 16.055 | 15.0347 | 16.3647 | 15.6555 | 14.7644 | 10.2683 | 10.6304 | 11.2464 | 11.2963 | 8.718 |  | 10.4932 | 8.8369 | 9.8357 | 9.2705 | 10.9575 | 11.9112 |  | 12.2002 |  |  | 11.5088 | 12.2649 | 12.3681 | [6 empty] | 12.4608 |  |  | 11.2331 |  |  | 9.1257 | 10.1049 | 11.7233 | 7.4485 | 9.1291 | 12.4432 | 7.8584 | 9.526 | 12.1661 | 9.1908 | 10.5338 | 7.6887 | 10.2502 | 8.341 | 10.2741 | 7.8639 | 9.6285 | 13.1563 | 10.4644 | 10.1879 | 11.4055 | 8.1911 | 9.7707 | 12.7029 | 8.0586 | 10.3567 | 9.7674 | 9.8474 | 8.5897 | 10.3051 | 0.039471 | 20.9557 | 0.033809 | 0.05112 | -37.8635 | 3.1202 | 7.31 | 0.33 | 0.51884 | -0.47116 | 0.4104 | 0.33922 | -0.27495 | -0.59034 | 0.83778 | 0.41632 | 0.39136 | 0.41628 | 0.36641 | 0.56127 | 0.42071 | 0.40573
42810.4378 | -189 | 18.4762 | 18.5936 | 18.5896 | 18.5993 | 17.9352 | 16.5881 | 14.6544 | 16.7042 | 17.1946 | 17.2887 | 17.2955 | 16.8383 | 15.8756 | 14.489 | 14.9041 | 14.9227 | 15.4881 | 13.3489 | 13.4715 | 14.0454 |  |  |  | 16.59 | 15.9251 | 15.0342 | 10.2495 | 9.5855 | 10.5521 | 17.1428 | 16.3025 | 15.1191 | 16.8606 | 16.1493 | 15.1437 | 10.7254 | 11.6844 |  | 12.0467 | 10.5069 | 10.213 | 8.8863 |  | 6.3388 | 6.3617 | 5.8517 | 5.9995 | 6.1244 | 6.3744 | 6.8902 | 5.0934 | 6.5234 | 4.9998 | 6.731 | 8.039 | 42.339 | 47.3883 | 43.3061 | 15.2961 |  |  | 0.13559 | -0.18653 | 0.13919 | 0.10185 | 0.047476 | -0.21994 | 0.69579 | -0.2525 | -0.35805 | -1.5867 | -0.41936 | 8.868 | 8.8697 | 2.0088 | 15.7336 | 16.6733 | 17.2312 | 17.5692 | 17.5253 | 16.5063 | 14.8572 | 16.8412 | 17.1836 | 17.4733 | 17.5248 | 17.262 | 16.4731 | 14.6991 | 6.5273 | 8.4788 | 5.7555 | 6.0067 | 6.1396 | 6.6328 | 7.6092 | 15.8009 | 15.4774 | 15.3483 | 14.2922 | 14.181 | 14.1221 |  |  |  | 10.6386 | 9.3728 | 9.121 | 9.3159 | 0.089801 | 0.0056708 | 12.676 |  |  | 10.5249 |  |  | 16.8664 | 16.0709 | 15.046 | 16.3733 | 15.6673 | 14.7699 | 10.2844 | 10.6427 | 11.2406 | 11.2895 | 8.7634 |  | 10.4771 | 8.8608 | 9.8202 | 9.2949 | 10.9464 | 11.828 |  | 12.1931 |  |  | 11.5319 | 12.2446 | 12.3629 | [6 empty] | 12.4738 |  |  | 11.226 |  |  | 9.1262 | 10.1204 | 11.7147 | 7.459 | 9.1216 | 12.4327 | 7.8539 | 9.5204 | 12.1701 | 9.1892 | 10.5285 | 7.6838 | 10.2446 | 8.3465 | 10.2662 | 7.8519 | 9.6248 | 13.1436 | 10.469 | 10.1919 | 11.4045 | 8.1821 | 9.7631 | 12.6982 | 8.0463 | 10.3538 | 9.7708 | 9.8591 | 8.5833 | 10.2906 | -0.0042494 | 20.9559 | 0.033705 | 0.051554 | -37.7425 | 3.1202 | 5.7 | 0.21 | 0.43222 | -0.5032 | 0.43468 | 0.37184 | 0.25387 | -0.54642 | 0.97189 | 0.41453 | 0.39018 | 0.41523 | 0.35916 | 0.55827 | 0.4193 | 0.4045
42810.4379 | -188 | 18.4735 | 18.5809 | 18.588 | 18.5951 | 17.9341 | 16.5791 | 14.6366 | 16.6991 | 17.1911 | 17.2867 | 17.2854 | 16.8267 | 15.8656 | 14.4787 | 14.8967 | 14.9245 | 15.4947 | 13.3614 | 13.4669 | 14.0489 |  |  |  | 16.6012 | 15.9303 | 15.0236 | 10.2596 | 9.5781 | 10.5543 | 17.1472 | 16.3003 | 15.1102 | 16.8664 | 16.1508 | 15.1458 | 10.7264 | 11.7209 |  | 12.0392 | 10.5168 | 10.201 | 8.9077 |  | 6.3529 | 6.376 | 5.851 | 6.0026 | 6.1256 | 6.3843 | 6.8766 | 5.0954 | 6.5108 | 4.9917 | 6.7317 | 8.0452 | 42.3454 | 47.4005 | 43.3242 | 15.2898 |  |  | 0.017963 | -0.051825 | 0.16942 | 0.22671 | -0.20617 | -0.20942 | 0.49668 | -0.29981 | -0.27729 | -0.78084 | -0.39512 | 8.8681 | 8.8694 | 2.0082 | 15.7305 | 16.6717 | 17.2321 | 17.5689 | 17.5286 | 16.5074 | 14.856 | 16.8411 | 17.1835 | 17.4784 | 17.5255 | 17.2639 | 16.4722 | 14.71 | 6.5266 | 8.4786 | 5.7854 | 5.9656 | 6.1976 | 6.6333 | 7.6043 | 15.7929 | 15.4751 | 15.343 | 14.2832 | 14.1727 | 14.1156 |  |  |  | 10.6281 | 9.3725 | 9.1138 | 9.304 | 0.064476 | -0.051542 | 12.6861 |  |  | 10.546 |  |  | 16.8888 | 16.0764 | 15.0594 | 16.3859 | 15.6818 | 14.7794 | 10.2949 | 10.6588 | 11.2412 | 11.2846 | 8.7928 |  | 10.4761 | 8.7863 | 9.8219 | 9.3134 | 10.9507 | 11.7852 |  | 12.2043 |  |  | 11.5343 | 12.2559 | 12.3699 | [6 empty] | 12.4952 |  |  | 11.2287 |  |  | 9.1309 | 10.1275 | 11.7054 | 7.48 | 9.1201 | 12.4345 | 7.8528 | 9.5206 | 12.1841 | 9.202 | 10.5377 | 7.6908 | 10.2434 | 8.3454 | 10.2774 | 7.8492 | 9.6288 | 13.1489 | 10.4744 | 10.1976 | 11.4185 | 8.177 | 9.7668 | 12.6996 | 8.0512 | 10.3582 | 9.7806 | 9.8822 | 8.5804 | 10.2991 | -0.0055976 | 20.9566 | 0.034107 | 0.050375 | -37.7343 | 3.1202 | 3.01 | 0.33 | 0.15732 | -0.26525 | 0.47957 | 0.55477 | -0.52905 | -0.53321 | 0.82115 | 0.41367 | 0.39231 | 0.41486 | 0.35929 | 0.55437 | 0.41873 | 0.40449
42810.4379 | -187 | 18.4784 | 18.5853 | 18.5882 | 18.5964 | 17.9419 | 16.5753 | 14.6476 | 16.706 | 17.1924 | 17.2842 | 17.294 | 16.8334 | 15.865 | 14.4785 | 14.8955 | 14.9258 | 15.4891 | 13.3596 | 13.4765 | 14.042 |  |  |  | 16.5994 | 15.9353 | 15.0343 | 10.2761 | 9.5802 | 10.5476 | 17.1546 | 16.3112 | 15.1155 | 16.8702 | 16.1543 | 15.1451 | 10.7364 | 11.774 |  | 12.0455 | 10.5319 | 10.2027 | 8.9342 |  | 6.3624 | 6.3854 | 5.8646 | 6.0037 | 6.1349 | 6.3978 | 6.8837 | 5.1011 | 6.5179 | 5.0028 | 6.73 | 8.0416 | 42.3442 | 47.4273 | 43.3517 | 15.2847 |  |  | -0.042493 | -0.091909 | 0.079392 | 0.18531 | -0.001808 | -0.1516 | 0.61365 | -0.22621 | -0.16053 | -0.23976 | -0.25623 | 8.8696 | 8.8711 | 2.0085 | 15.7323 | 16.6646 | 17.225 | 17.5562 | 17.5216 | 16.5053 | 14.857 | 16.8355 | 17.1768 | 17.4744 | 17.5321 | 17.2615 | 16.4646 | 14.7023 | 6.4965 | 8.4799 | 5.8273 | 5.9553 | 6.2471 | 6.6309 | 7.6129 | 15.7899 | 15.4695 | 15.3425 | 14.273 | 14.167 | 14.1087 |  |  |  | 10.632 | 9.3771 | 9.1134 | 9.2999 | 0.087977 | -0.01616 | 12.6811 |  |  | 10.5438 |  |  | 16.8741 | 16.0731 | 15.0567 | 16.3866 | 15.6637 | 14.7711 | 10.2851 | 10.6693 | 11.2286 | 11.2578 | 8.8317 |  | 10.4874 | 8.726 | 9.8241 | 9.3258 | 10.9531 | 11.7731 |  | 12.2056 |  |  | 11.5554 | 12.2312 | 12.3808 | [6 empty] | 12.5014 |  |  | 11.2403 |  |  | 9.1511 | 10.1344 | 11.6948 | 7.4891 | 9.11 | 12.4402 | 7.8678 | 9.5397 | 12.1983 | 9.2099 | 10.5391 | 7.6853 | 10.2406 | 8.3591 | 10.2967 | 7.8527 | 9.6157 | 13.1364 | 10.471 | 10.1963 | 11.4239 | 8.1756 | 9.7647 | 12.7051 | 8.0467 | 10.3489 | 9.7804 | 9.8859 | 8.561 | 10.3013 | 0.046404 | 20.956 | 0.032334 | 0.048898 | -37.8332 | 3.1201 | 13.02 | 0.27 | -0.24197 | -0.35324 | 0.3283 | 0.50157 | -0.049544 | -0.45367 | 0.91276 | 0.41297 | 0.39406 | 0.4146 | 0.36236 | 0.55073 | 0.41833 | 0.40473
42810.4379 | -186 | 18.4714 | 18.5892 | 18.5859 | 18.5972 | 17.9388 | 16.5746 | 14.647 | 16.7046 | 17.1899 | 17.2844 | 17.2895 | 16.8347 | 15.862 | 14.4863 | 14.8948 | 14.9257 | 15.4928 | 13.3507 | 13.4716 | 14.0481 |  |  |  | 16.5985 | 15.9348 | 15.0254 | 10.27 | 9.5805 | 10.5499 | 17.1513 | 16.3003 | 15.1137 | 16.862 | 16.1474 | 15.1391 | 10.7307 | 11.8229 |  | 12.0355 | 10.5414 | 10.1898 | 8.9423 |  | 6.3751 | 6.3868 | 5.8748 | 6.0145 | 6.1481 | 6.4045 | 6.8949 | 5.1531 | 6.5239 | 5.005 | 6.7322 | 8.0426 | 42.339 | 47.4314 | 43.3703 | 15.268 |  |  | -0.070093 | -0.10768 | 0.17139 | 0.038114 | -0.027436 | -0.36384 | 0.54202 | -0.20256 | -0.20101 | -0.27774 | -0.37744 | 8.8702 | 8.8711 | 2.0084 | 15.7294 | 16.6748 | 17.2239 | 17.5539 | 17.5215 | 16.5057 | 14.8563 | 16.8413 | 17.1744 | 17.468 | 17.5174 | 17.2585 | 16.4541 | 14.6983 | 6.3859 | 8.4455 | 5.8497 | 5.9587 | 6.2685 | 6.6348 | 7.6167 | 15.7884 | 15.4647 | 15.3431 | 14.2822 | 14.1696 | 14.1157 |  |  |  | 10.64 | 9.3784 | 9.1231 | 9.3093 | 0.051914 | -0.22205 | 12.6841 |  |  | 10.5471 |  |  | 16.881 | 16.0717 | 15.0515 | 16.3856 | 15.6709 | 14.7746 | 10.2864 | 10.6813 | 11.2218 | 11.2599 | 8.8347 |  | 10.4788 | 8.6798 | 9.8239 | 9.3486 | 10.9488 | 11.7703 |  | 12.1983 |  |  | 11.5787 | 12.2531 | 12.3917 | [6 empty] | 12.5149 |  |  | 11.2591 |  |  | 9.1478 | 10.1267 | 11.6825 | 7.5013 | 9.0836 | 12.4276 | 7.873 | 9.5391 | 12.2124 | 9.1993 | 10.5445 | 7.6788 | 10.2438 | 8.3532 | 10.2973 | 7.8803 | 9.6261 | 13.1424 | 10.4785 | 10.2094 | 11.4499 | 8.1839 | 9.7639 | 12.7236 | 8.0645 | 10.3588 | 9.7878 | 9.9074 | 8.554 | 10.3159 | -0.013302 | 20.9549 | 0.031714 | 0.048037 | -37.7919 | 3.1201 | -4.01 | 0.35 | -0.31077 | -0.38234 | 0.48237 | 0.22747 | -0.193 | -0.70284 | 0.85784 | 0.4126 | 0.39533 | 0.41382 | 0.3751 | 0.54867 | 0.41792 | 0.40473
42810.4379 | -185 | 18.4728 | 18.587 | 18.5809 | 18.5937 | 17.9331 | 16.5805 | 14.6473 | 16.7036 | 17.191 | 17.2817 | 17.2912 | 16.8366 | 15.8619 | 14.4788 | 14.9053 | 14.9279 | 15.5065 | 13.3701 | 13.4839 | 14.0601 |  |  |  | 16.604 | 15.9326 | 15.0368 | 10.2894 | 9.587 | 10.5095 | 17.1491 | 16.2983 | 15.1065 | 16.8644 | 16.1457 | 15.1348 | 10.7268 | 11.8448 |  | 12.0303 | 10.5513 | 10.1838 | 8.9601 |  | 6.3801 | 6.3878 | 5.8839 | 6.0242 | 6.1613 | 6.4209 | 6.9325 | 5.1662 | 6.5308 | 4.9787 | 6.7479 | 8.0419 | 42.3346 | 47.4491 | 43.3847 | 15.2641 |  |  | 0.14938 | -0.20822 | 0.21541 | 0.29242 | -0.09446 | -0.15225 | 0.49405 | -0.1835 | -0.03365 | -0.60398 | -0.27928 | 8.8691 | 8.8702 | 2.0087 | 15.7246 | 16.663 | 17.2169 | 17.5585 | 17.5248 | 16.5 | 14.8502 | 16.8447 | 17.1709 | 17.4718 | 17.5168 | 17.2609 | 16.4694 | 14.6903 | 6.365 | 8.4491 | 5.8572 | 5.9905 | 6.2421 | 6.6321 | 7.6151 | 15.7811 | 15.454 | 15.3314 | 14.277 | 14.1692 | 14.1069 |  |  |  | 10.6294 | 9.3733 | 9.1271 | 9.312 | 0.013826 | -0.1351 | 12.6747 |  |  | 10.5422 |  |  | 16.8822 | 16.0651 | 15.0562 | 16.3734 | 15.6554 | 14.7625 | 10.2666 | 10.6845 | 11.2077 | 11.2283 | 8.8555 |  | 10.4824 | 8.6801 | 9.8286 | 9.3692 | 10.9496 | 11.7784 |  | 12.199 |  |  | 11.5673 | 12.2944 | 12.407 | [6 empty] | 12.5185 |  |  | 11.2691 |  |  | 9.1378 | 10.1271 | 11.6934 | 7.4966 | 9.075 | 12.4153 | 7.8714 | 9.5151 | 12.2181 | 9.1784 | 10.5378 | 7.68 | 10.2307 | 8.352 | 10.2965 | 7.8859 | 9.6346 | 13.1461 | 10.4738 | 10.199 | 11.4696 | 8.1794 | 9.752 | 12.7266 | 8.0656 | 10.3667 | 9.7911 | 9.9214 | 8.5438 | 10.3149 | 0.059116 | 20.957 | 0.03172 | 0.047465 | -37.7812 | 3.1201 | -7.35 | 0.24 | 0.45365 | -0.53167 | 0.54078 | 0.63007 | -0.35813 | -0.45467 | 0.81903 | 0.41214 | 0.39548 | 0.41327 | 0.37711 | 0.54766 | 0.41729 | 0.4043
42810.4379 | -184 | 18.4689 | 18.5839 | 18.5799 | 18.5954 | 17.9319 | 16.5848 | 14.648 | 16.7011 | 17.1914 | 17.2791 | 17.2946 | 16.8262 | 15.8636 | 14.4808 | 14.8926 | 14.9198 | 15.4873 | 13.3483 | 13.4704 | 14.0518 |  |  |  | 16.5989 | 15.9295 | 15.0283 | 10.2856 | 9.5764 | 10.5135 | 17.1498 | 16.3027 | 15.1071 | 16.8582 | 16.1434 | 15.1374 | 10.7336 | 11.8697 |  | 12.0421 | 10.5581 | 10.1802 | 8.9778 |  | 6.3873 | 6.4047 | 5.9025 | 6.0325 | 6.1808 | 6.4345 | 6.9492 | 5.1587 | 6.5253 | 4.9599 | 6.7532 | 8.0352 | 42.3368 | 47.4933 | 43.3978 | 15.2532 |  |  | 0.078415 | -0.2667 | 0.15496 | 0.15639 | -0.028092 | -0.1194 | 0.50128 | -0.18941 | -0.14457 | 0.067803 | -0.37148 | 8.8668 | 8.8679 | 2.0084 | 15.7218 | 16.6626 | 17.2185 | 17.5528 | 17.5199 | 16.5031 | 14.8534 | 16.836 | 17.1731 | 17.4717 | 17.52 | 17.2568 | 16.4663 | 14.6936 | 6.3852 | 8.4961 | 5.9797 | 5.9753 | 6.1956 | 6.632 | 7.608 | 15.7838 | 15.4572 | 15.3377 | 14.2755 | 14.1737 | 14.1056 |  |  |  | 10.6416 | 9.3898 | 9.1423 | 9.3215 | 0.054548 | 0.21457 | 12.6705 |  |  | 10.5375 |  |  | 16.8763 | 16.0642 | 15.0456 | 16.3737 | 15.6519 | 14.7637 | 10.2465 | 10.6987 | 11.1981 | 11.2271 | 8.8819 |  | 10.4822 | 8.635 | 9.8236 | 9.3825 | 10.9507 | 11.7789 |  | 12.1984 |  |  | 11.5526 | 12.3019 | 12.4018 | [6 empty] | 12.5378 |  |  | 11.2743 |  |  | 9.1501 | 10.122 | 11.7002 | 7.5115 | 9.0841 | 12.4085 | 7.8851 | 9.5159 | 12.2211 | 9.1815 | 10.542 | 7.674 | 10.2412 | 8.3564 | 10.2979 | 7.8996 | 9.6426 | 13.146 | 10.474 | 10.2003 | 11.4655 | 8.1818 | 9.7562 | 12.7237 | 8.0808 | 10.3788 | 9.7902 | 9.918 | 8.5405 | 10.3315 | -0.072237 | 20.9541 | 0.033286 | 0.047863 | -37.8081 | 3.1201 | 8.54 | 0.22 | 0.32868 | -0.60175 | 0.45868 | 0.4608 | -0.19531 | -0.40264 | 0.82502 | 0.4114 | 0.39657 | 0.41294 | 0.37484 | 0.53322 | 0.41702 | 0.40444
42810.4379 | -183 | 18.4638 | 18.5807 | 18.582 | 18.5931 | 17.9418 | 16.5812 | 14.6399 | 16.7004 | 17.1897 | 17.2797 | 17.2906 | 16.8343 | 15.8613 | 14.4824 | 14.8959 | 14.9265 | 15.4907 | 13.3529 | 13.476 | 14.0546 |  |  |  | 16.5985 | 15.9315 | 15.0276 | 10.301 | 9.5986 | 10.5325 | 17.1563 | 16.2999 | 15.1161 | 16.868 | 16.1509 | 15.1499 | 10.738 | 11.9295 |  | 12.0503 | 10.5773 | 10.188 | 8.9906 |  | 6.3994 | 6.433 | 5.9276 | 6.0532 | 6.2031 | 6.4446 | 6.9558 | 5.1499 | 6.5169 | 4.9488 | 6.7578 | 8.0393 | 42.3451 | 47.523 | 43.4131 | 15.2534 |  |  | 0.11653 | -0.059053 | -0.029692 | 0.13077 | -0.001152 | -0.077344 | 0.59262 | -0.14144 | -0.37537 | -0.03437 | -0.16006 | 8.8691 | 8.8699 | 2.0085 | 15.725 | 16.6661 | 17.2259 | 17.5585 | 17.522 | 16.5007 | 14.855 | 16.8334 | 17.1788 | 17.4725 | 17.5205 | 17.2589 | 16.4646 | 14.6926 | 6.4725 | 8.5171 | 6.147 | 5.9939 | 6.1528 | 6.6393 | 7.6176 | 15.7824 | 15.4524 | 15.3409 | 14.2711 | 14.1704 | 14.1138 |  |  |  | 10.6391 | 9.4151 | 9.1491 | 9.3173 | -0.080991 | -0.036674 | 12.6853 |  |  | 10.5483 |  |  | 16.8804 | 16.0677 | 15.0457 | 16.3894 | 15.6634 | 14.7786 | 10.2337 | 10.7095 | 11.1858 | 11.2184 | 8.9254 |  | 10.4818 | 8.6171 | 9.8197 | 9.3913 | 10.9554 | 11.7785 |  | 12.209 |  |  | 11.574 | 12.2756 | 12.4242 | [6 empty] | 12.5482 |  |  | 11.2931 |  |  | 9.1481 | 10.1191 | 11.7104 | 7.5167 | 9.0888 | 12.4082 | 7.8951 | 9.5344 | 12.2332 | 9.187 | 10.5525 | 7.6755 | 10.2564 | 8.3694 | 10.3127 | 7.9155 | 9.6559 | 13.1534 | 10.4669 | 10.2098 | 11.4621 | 8.1964 | 9.7557 | 12.7037 | 8.0846 | 10.3945 | 9.8055 | 9.9304 | 8.5369 | 10.3626 | 0.13596 | 20.955 | 0.033682 | 0.048153 | -37.7731 | 3.1201 | 3.28 | 0.26 | 0.40068 | -0.28317 | -0.20079 | 0.42138 | -0.039551 | -0.32407 | 0.89706 | 0.41018 | 0.39694 | 0.41285 | 0.366 | 0.51575 | 0.41681 | 0.40448
42810.4379 | -182 | 18.4681 | 18.5801 | 18.5804 | 18.5823 | 17.9308 | 16.5767 | 14.6406 | 16.6984 | 17.1879 | 17.2866 | 17.2882 | 16.8376 | 15.8635 | 14.4816 | 14.8908 | 14.9266 | 15.4902 | 13.3577 | 13.4739 | 14.0509 |  |  |  | 16.5954 | 15.9282 | 15.0308 | 10.3061 | 9.6155 | 10.4875 | 17.1416 | 16.2975 | 15.1083 | 16.8601 | 16.1464 | 15.1405 | 10.734 | 11.9576 |  | 12.0331 | 10.5779 | 10.175 | 8.9825 |  | 6.4213 | 6.4642 | 5.9573 | 6.0839 | 6.2263 | 6.453 | 6.9463 | 5.2124 | 6.528 | 4.996 | 6.7545 | 8.0483 | 42.3574 | 47.5269 | 43.4152 | 15.2424 |  |  | -0.11281 | -0.22859 | 0.13787 | -0.01577 | 0.004764 | -0.16474 | 0.43097 | -0.29324 | -0.18738 | -0.30543 | -0.38658 | 8.8682 | 8.8694 | 2.0086 | 15.7263 | 16.6654 | 17.2237 | 17.5581 | 17.5231 | 16.5045 | 14.8563 | 16.8352 | 17.1808 | 17.4732 | 17.5198 | 17.2571 | 16.4681 | 14.698 | 6.522 | 8.5217 | 6.2166 | 6.078 | 6.1417 | 6.6413 | 7.6258 | 15.7705 | 15.4498 | 15.3336 | 14.2716 | 14.1692 | 14.1058 |  |  |  | 10.6327 | 9.4326 | 9.1508 | 9.3153 | 0.13194 | -0.045896 | 12.6727 |  |  | 10.5438 |  |  | 16.8828 | 16.0707 | 15.0439 | 16.3748 | 15.6674 | 14.7662 | 10.2187 | 10.7183 | 11.188 | 11.213 | 8.9565 |  | 10.4819 | 8.616 | 9.8182 | 9.3842 | 10.9432 | 11.7746 |  | 12.186 |  |  | 11.5857 | 12.2613 | 12.4267 | [6 empty] | 12.5657 |  |  | 11.3141 |  |  | 9.1583 | 10.1245 | 11.7119 | 7.5208 | 9.0953 | 12.4008 | 7.911 | 9.5315 | 12.2441 | 9.1866 | 10.5509 | 7.6751 | 10.2624 | 8.37 | 10.3197 | 7.9202 | 9.6592 | 13.1525 | 10.4571 | 10.2074 | 11.4564 | 8.1935 | 9.7453 | 12.6981 | 8.0925 | 10.3901 | 9.8066 | 9.9304 | 8.5349 | 10.373 | -0.041806 | 20.956 | 0.033539 | 0.048102 | -37.8366 | 3.1201 | 0.81 | 0.26 | -0.3942 | -0.55715 | 0.4327 | -0.14634 | 0.080431 | -0.47297 | 0.765 | 0.40932 | 0.39692 | 0.41264 | 0.36072 | 0.50897 | 0.41691 | 0.40432
42810.4379 | -181 | 18.47 | 18.5807 | 18.5737 | 18.5882 | 17.9313 | 16.5743 | 14.641 | 16.7 | 17.1845 | 17.2791 | 17.2914 | 16.8278 | 15.8595 | 14.4779 | 14.8922 | 14.9119 | 15.4889 | 13.3552 | 13.4728 | 14.0415 |  |  |  | 16.5923 | 15.9274 | 15.0328 | 10.3033 | 9.6274 | 10.3975 | 17.1432 | 16.2966 | 15.1105 | 16.8534 | 16.1445 | 15.149 | 10.7393 | 11.9672 |  | 12.0349 | 10.5916 | 10.1893 | 8.9902 |  | 6.439 | 6.4831 | 5.9874 | 6.1068 | 6.2326 | 6.4446 | 6.9319 | 5.2803 | 6.5272 | 5.036 | 6.7641 | 8.0496 | 42.3696 | 47.5302 | 43.4247 | 15.2407 |  |  | 0.1369 | 0.056599 | 0.1267 | 0.15902 | 0.043532 | -0.13977 | 0.50654 | -0.20453 | -0.1689 | -0.46991 | -0.26815 | 8.8719 | 8.8728 | 2.0082 | 15.7316 | 16.6679 | 17.2309 | 17.5665 | 17.5264 | 16.5056 | 14.8579 | 16.8437 | 17.1857 | 17.48 | 17.5274 | 17.2629 | 16.4739 | 14.7037 | 6.5169 | 8.5068 | 6.2866 | 6.1584 | 6.1389 | 6.6453 | 7.6161 | 15.7798 | 15.4574 | 15.3357 | 14.2785 | 14.174 | 14.1183 |  |  |  | 10.6406 | 9.4561 | 9.1669 | 9.3301 | 0.1366 | 0.019786 | 12.6704 |  |  | 10.5374 |  |  | 16.874 | 16.0574 | 15.0383 | 16.3708 | 15.6664 | 14.76 | 10.2124 | 10.7211 | 11.1767 | 11.2102 | 9.0086 |  | 10.4806 | 8.6596 | 9.8292 | 9.3911 | 10.9559 | 11.7859 |  | 12.1987 |  |  | 11.5666 | 12.234 | 12.4088 | [6 empty] | 12.5732 |  |  | 11.3227 |  |  | 9.1633 | 10.1189 | 11.7076 | 7.5116 | 9.0874 | 12.3907 | 7.9065 | 9.5211 | 12.2389 | 9.1784 | 10.5418 | 7.668 | 10.2632 | 8.3434 | 10.3172 | 7.9247 | 9.6667 | 13.1478 | 10.4577 | 10.2137 | 11.4567 | 8.1944 | 9.7376 | 12.693 | 8.1021 | 10.3913 | 9.8104 | 9.9317 | 8.5229 | 10.3889 | 0.1531 | 20.954 | 0.033567 | 0.048906 | -37.8313 | 3.1201 | -21.05 | 0.26 | 0.43419 | 0.27725 | 0.41482 | 0.46472 | 0.24313 | -0.43565 | 0.82935 | 0.40783 | 0.39607 | 0.41287 | 0.36175 | 0.50006 | 0.41687 | 0.40417
42810.438 | -180 | 18.4604 | 18.5717 | 18.5711 | 18.5768 | 17.9187 | 16.5682 | 14.6378 | 16.6967 | 17.1823 | 17.2758 | 17.2754 | 16.8162 | 15.8563 | 14.4665 | 14.8926 | 14.9074 | 15.4834 | 13.3509 | 13.4674 | 14.0422 |  |  |  | 16.5868 | 15.9237 | 15.0273 | 10.2981 | 9.6448 | 10.3377 | 17.1507 | 16.3006 | 15.1102 | 16.8652 | 16.1499 | 15.1516 | 10.7384 | 11.9572 |  | 12.0411 | 10.6028 | 10.1908 | 8.9855 |  | 6.4425 | 6.4903 | 5.992 | 6.1202 | 6.2431 | 6.4275 | 6.9046 | 5.3101 | 6.5381 | 5.0482 | 6.7589 | 8.0423 | 42.3718 | 47.5271 | 43.4231 | 15.2293 |  |  | 0.062647 | -0.13265 | 0.14773 | -0.017086 | -0.032036 | -0.16802 | 0.5959 | -0.29784 | -0.58048 | -0.19822 | -0.36174 | 8.8646 | 8.866 | 2.0087 | 15.7264 | 16.6639 | 17.2255 | 17.5576 | 17.5218 | 16.5032 | 14.8564 | 16.8383 | 17.1865 | 17.478 | 17.5258 | 17.2617 | 16.4677 | 14.7013 | 6.5285 | 8.4734 | 6.39 | 6.1808 | 6.1677 | 6.6393 | 7.6217 | 15.7784 | 15.456 | 15.3407 | 14.274 | 14.1689 | 14.116 |  |  |  | 10.6395 | 9.4662 | 9.1712 | 9.3545 | -0.028923 | 0.1568 | 12.6657 |  |  | 10.5425 |  |  | 16.8646 | 16.0629 | 15.0402 | 16.3717 | 15.6577 | 14.7563 | 10.2116 | 10.737 | 11.1695 | 11.2017 | 9.1179 |  | 10.4757 | 8.718 | 9.8267 | 9.4017 | 10.9471 | 11.7818 |  | 12.1989 |  |  | 11.5381 | 12.2047 | 12.3916 | [6 empty] | 12.5723 |  |  | 11.337 |  |  | 9.1657 | 10.1198 | 11.7063 | 7.5132 | 9.0959 | 12.3808 | 7.9067 | 9.5183 | 12.2419 | 9.1704 | 10.5365 | 7.6716 | 10.2784 | 8.3465 | 10.3065 | 7.9415 | 9.67 | 13.1471 | 10.452 | 10.2159 | 11.4522 | 8.2055 | 9.723 | 12.6817 | 8.1168 | 10.4058 | 9.8094 | 9.9455 | 8.5171 | 10.4017 | 0.00904 | 20.9552 | 0.034905 | 0.051033 | -37.854 | 3.1201 | -9.08 | 0.31 | 0.29369 | -0.42444 | 0.44792 | -0.15233 | -0.20856 | -0.47764 | 0.89951 | 0.40463 | 0.39437 | 0.41229 | 0.35978 | 0.48923 | 0.41697 | 0.40346
42810.438 | -179 | 18.4638 | 18.5811 | 18.5704 | 18.5901 | 17.9275 | 16.5717 | 14.6462 | 16.7021 | 17.1931 | 17.2903 | 17.2897 | 16.8269 | 15.8549 | 14.4733 | 14.8955 | 14.9185 | 15.4891 | 13.3493 | 13.4711 | 14.0404 |  |  |  | 16.5951 | 15.9301 | 15.0315 | 10.3026 | 9.6762 | 10.3429 | 17.1466 | 16.2961 | 15.1072 | 16.8663 | 16.1511 | 15.1476 | 10.7312 | 11.9417 |  | 12.0428 | 10.6052 | 10.1911 | 8.9944 |  | 6.4486 | 6.499 | 5.9964 | 6.1264 | 6.2327 | 6.4094 | 6.9033 | 5.251 | 6.5348 | 5.0648 | 6.7556 | 8.0434 | 42.3834 | 47.5476 | 43.4151 | 15.2193 |  |  | 0.094843 | -0.044597 | 0.064276 | 0.06177 | 0.10728 | -0.20154 | 0.52428 | -0.14867 | -0.66318 | -1.3177 | -0.38598 | 8.8712 | 8.8723 | 2.0084 | 15.71 | 16.6531 | 17.2104 | 17.5451 | 17.5143 | 16.4973 | 14.8431 | 16.8298 | 17.1703 | 17.4698 | 17.5193 | 17.2583 | 16.4636 | 14.6966 | 6.5033 | 8.4495 | 6.4141 | 6.1725 | 6.1455 | 6.6439 | 7.6294 | 15.776 | 15.4467 | 15.3301 | 14.2716 | 14.165 | 14.1104 |  |  |  | 10.6366 | 9.4746 | 9.1702 | 9.4104 | 0.020511 | 0.07681 | 12.678 |  |  | 10.557 |  |  | 16.8737 | 16.0752 | 15.0443 | 16.3913 | 15.6655 | 14.7776 | 10.2361 | 10.7539 | 11.1776 | 11.2038 | 9.2695 |  | 10.4738 | 8.7854 | 9.826 | 9.4139 | 10.9441 | 11.7788 |  | 12.1901 |  |  | 11.5331 | 12.1909 | 12.3803 | [6 empty] | 12.57 |  |  | 11.3478 |  |  | 9.1697 | 10.1243 | 11.7154 | 7.5271 | 9.1049 | 12.3831 | 7.9129 | 9.5145 | 12.2495 | 9.1776 | 10.5376 | 7.6743 | 10.2941 | 8.3575 | 10.3111 | 7.9513 | 9.6712 | 13.1494 | 10.4574 | 10.2194 | 11.4448 | 8.2081 | 9.7019 | 12.6771 | 8.1238 | 10.4129 | 9.8134 | 9.9517 | 8.5189 | 10.41 | -0.17143 | 20.9544 | 0.032735 | 0.048211 | -37.7541 | 3.1201 | -6.45 | 0.33 | 0.36136 | -0.24611 | 0.29546 | 0.28964 | 0.38164 | -0.52309 | 0.8437 | 0.40036 | 0.39247 | 0.41185 | 0.36311 | 0.48744 | 0.41649 | 0.40181
42810.438 | -178 | 18.458 | 18.5776 | 18.5736 | 18.5835 | 17.9247 | 16.564 | 14.6423 | 16.6917 | 17.188 | 17.288 | 17.2888 | 16.828 | 15.8575 | 14.4636 | 14.8903 | 14.9175 | 15.4909 | 13.349 | 13.4731 | 14.0446 |  |  |  | 16.594 | 15.9268 | 15.032 | 10.3081 | 9.6994 | 10.3631 | 17.142 | 16.2941 | 15.1051 | 16.865 | 16.1499 | 15.1391 | 10.7354 | 11.9206 |  | 12.0365 | 10.6158 | 10.1881 | 9.0223 |  | 6.4681 | 6.5078 | 6.0157 | 6.1303 | 6.2485 | 6.4094 | 6.9427 | 5.1271 | 6.5367 | 5.0899 | 6.7575 | 8.0392 | 42.395 | 47.567 | 43.4185 | 15.2118 |  |  | 0.075131 | -0.020941 | -0.074376 | 0.065054 | 0.20716 | -0.16802 | 0.52362 | -0.18481 | -0.50984 | -0.28592 | -0.049584 | 8.8699 | 8.8712 | 2.0088 | 15.7242 | 16.657 | 17.2165 | 17.5541 | 17.5167 | 16.4957 | 14.8598 | 16.8341 | 17.1731 | 17.4733 | 17.5241 | 17.258 | 16.4652 | 14.6987 | 6.4715 | 8.4557 | 6.3409 | 6.1885 | 6.1011 | 6.6429 | 7.6243 | 15.7731 | 15.4561 | 15.331 | 14.2713 | 14.168 | 14.1091 |  |  |  | 10.6391 | 9.4837 | 9.1764 | 9.4515 | -0.1752 | 0.11351 | 12.6803 |  |  | 10.5418 |  |  | 16.8706 | 16.0725 | 15.0468 | 16.3864 | 15.6672 | 14.7704 | 10.2437 | 10.7749 | 11.1772 | 11.201 | 9.3602 |  | 10.475 | 8.8456 | 9.8323 | 9.4204 | 10.9481 | 11.7922 |  | 12.1927 |  |  | 11.5395 | 12.191 | 12.3843 | [6 empty] | 12.57 |  |  | 11.3505 |  |  | 9.1725 | 10.1199 | 11.721 | 7.5307 | 9.1024 | 12.3861 | 7.9104 | 9.5172 | 12.2523 | 9.1768 | 10.5268 | 7.6739 | 10.3057 | 8.3619 | 10.3206 | 7.9521 | 9.6731 | 13.1444 | 10.4512 | 10.2212 | 11.4454 | 8.2018 | 9.697 | 12.6681 | 8.1288 | 10.4174 | 9.8041 | 9.9479 | 8.5152 | 10.4189 | -0.0088718 | 20.9536 | 0.032138 | 0.047371 | -37.8239 | 3.1202 | 2.8 | 0.27 | 0.32163 | -0.16865 | -0.31783 | 0.29725 | 0.53034 | -0.47763 | 0.84317 | 0.39788 | 0.391 | 0.4118 | 0.36652 | 0.49497 | 0.41585 | 0.40075
42810.438 | -177 | 18.461 | 18.5781 | 18.58 | 18.5846 | 17.9318 | 16.5714 | 14.642 | 16.6957 | 17.1826 | 17.2823 | 17.2858 | 16.8299 | 15.861 | 14.4684 | 14.8844 | 14.9142 | 15.4856 | 13.3522 | 13.4669 | 14.0417 |  |  |  | 16.5833 | 15.9207 | 15.026 | 10.3022 | 9.721 | 10.3799 | 17.1396 | 16.2881 | 15.098 | 16.8543 | 16.139 | 15.1314 | 10.7339 | 11.8928 |  | 12.0315 | 10.6116 | 10.1886 | 9.0302 |  | 6.4768 | 6.5107 | 6.0187 | 6.1379 | 6.2529 | 6.4083 | 6.9768 | 5.0363 | 6.5423 | 5.0867 | 6.7598 | 8.0314 | 42.4127 | 47.5796 | 43.4116 | 15.2005 |  |  | 0.011391 | -0.23319 | 0.15036 | 0.23196 | 0.093476 | -0.16014 | 0.41454 | -0.29061 | -0.14963 | -0.46635 | -0.36631 | 8.8691 | 8.8701 | 2.0081 | 15.7164 | 16.6494 | 17.2141 | 17.5495 | 17.5087 | 16.4911 | 14.8407 | 16.8291 | 17.1724 | 17.4681 | 17.5172 | 17.2571 | 16.4554 | 14.69 | 6.4575 | 8.4593 | 6.2881 | 6.1951 | 6.0905 | 6.6394 | 7.6353 | 15.7758 | 15.4501 | 15.3283 | 14.2763 | 14.1681 | 14.1089 |  |  |  | 10.6434 | 9.4848 | 9.191 | 9.4563 | -0.13245 | 0.13402 | 12.6703 |  |  | 10.5439 |  |  | 16.8637 | 16.0699 | 15.0394 | 16.3818 | 15.6741 | 14.7606 | 10.2679 | 10.7983 | 11.1653 | 11.2 | 9.3975 |  | 10.4695 | 8.9049 | 9.8357 | 9.4232 | 10.9574 | 11.8013 |  | 12.1907 |  |  | 11.5381 | 12.1838 | 12.3909 | [6 empty] | 12.5531 |  |  | 11.3485 |  |  | 9.1799 | 10.1208 | 11.7231 | 7.5402 | 9.1062 | 12.3903 | 7.9271 | 9.5276 | 12.2406 | 9.1863 | 10.5207 | 7.6854 | 10.3225 | 8.3665 | 10.3287 | 7.9576 | 9.6764 | 13.1366 | 10.4553 | 10.2152 | 11.4452 | 8.2024 | 9.6966 | 12.6542 | 8.1406 | 10.4235 | 9.793 | 9.9489 | 8.4963 | 10.4314 | 0.13539 | 20.9563 | 0.031157 | 0.046344 | -37.8002 | 3.1201 | 11.28 | 0.32 | 0.12524 | -0.56278 | 0.45191 | 0.56129 | 0.35625 | -0.46629 | 0.75022 | 0.39666 | 0.38947 | 0.41203 | 0.36768 | 0.50213 | 0.41558 | 0.40076
42810.438 | -176 | 18.4673 | 18.5804 | 18.5804 | 18.5899 | 17.9305 | 16.5765 | 14.6366 | 16.6981 | 17.192 | 17.2797 | 17.2828 | 16.8285 | 15.8582 | 14.4767 | 14.8871 | 14.9168 | 15.4862 | 13.3544 | 13.4711 | 14.0447 |  |  |  | 16.5868 | 15.9294 | 15.0249 | 10.3119 | 9.7441 | 10.4009 | 17.1436 | 16.2939 | 15.1097 | 16.853 | 16.1466 | 15.1405 | 10.7371 | 11.8548 |  | 12.0302 | 10.6243 | 10.2011 | 9.0366 |  | 6.4788 | 6.5233 | 6.0233 | 6.148 | 6.2518 | 6.4097 | 7.0065 | 4.9512 | 6.546 | 4.9732 | 6.7582 | 8.035 | 42.4366 | 47.5802 | 43.4118 | 15.193 |  |  | 0.17435 | -0.057737 | 0.16547 | 0.19582 | -0.00312 | 0.14345 | 0.53216 | -0.20124 | -1.6381 | -0.70342 | -0.19543 | 8.8693 | 8.8704 | 2.0085 | 15.7113 | 16.6527 | 17.2127 | 17.5465 | 17.5104 | 16.4885 | 14.8457 | 16.8365 | 17.1715 | 17.4725 | 17.5179 | 17.2569 | 16.4599 | 14.7028 | 6.4404 | 8.4425 | 6.3127 | 6.1919 | 6.1217 | 6.6448 | 7.6477 | 15.7668 | 15.4438 | 15.3238 | 14.267 | 14.1574 | 14.0986 |  |  |  | 10.6427 | 9.4868 | 9.1891 | 9.4189 | -0.026897 | -0.019172 | 12.6712 |  |  | 10.5394 |  |  | 16.8611 | 16.0635 | 15.0429 | 16.3657 | 15.6584 | 14.7516 | 10.2781 | 10.8189 | 11.1618 | 11.2026 | 9.4126 |  | 10.4763 | 8.9803 | 9.8361 | 9.432 | 10.9475 | 11.7942 |  | 12.1875 |  |  | 11.5465 | 12.2113 | 12.413 | [6 empty] | 12.541 |  |  | 11.3544 |  |  | 9.1802 | 10.1203 | 11.7249 | 7.5422 | 9.1102 | 12.382 | 7.9377 | 9.5313 | 12.2263 | 9.1857 | 10.5102 | 7.6893 | 10.3379 | 8.362 | 10.3276 | 7.9693 | 9.6752 | 13.1264 | 10.4619 | 10.21 | 11.4526 | 8.2025 | 9.6895 | 12.6474 | 8.146 | 10.4292 | 9.7929 | 9.9494 | 8.4913 | 10.4429 | 0.11054 | 20.9523 | 0.032311 | 0.046047 | -37.8124 | 3.1201 | 3.35 | 0.3 | 0.49 | -0.28004 | 0.47408 | 0.51573 | -0.065085 | 0.44132 | 0.85002 | 0.39647 | 0.38739 | 0.41146 | 0.3702 | 0.50084 | 0.4155 | 0.40178
42810.438 | -175 | 18.4626 | 18.5824 | 18.5821 | 18.5872 | 17.929 | 16.5744 | 14.6382 | 16.7032 | 17.1993 | 17.2828 | 17.2931 | 16.8216 | 15.8669 | 14.4724 | 14.8905 | 14.9196 | 15.481 | 13.3515 | 13.4701 | 14.0389 |  |  |  | 16.5882 | 15.927 | 15.0305 | 10.3182 | 9.7677 | 10.415 | 17.1351 | 16.2902 | 15.099 | 16.8575 | 16.1453 | 15.1315 | 10.7328 | 11.8299 |  | 12.0289 | 10.6365 | 10.2143 | 9.0716 |  | 6.4792 | 6.5194 | 6.0256 | 6.1528 | 6.253 | 6.4492 | 7.0576 | 4.8866 | 6.5438 | 4.8685 | 6.7504 | 8.0455 | 42.4646 | 47.5927 | 43.4188 | 15.1841 |  |  | 0.35309 | 0.018487 | 0.046536 | 0.00657 | 0.096104 | -0.051716 | 0.81538 | -0.22161 | -1.1117 | -0.17473 | -0.20795 | 8.8682 | 8.8691 | 2.0083 | 15.7196 | 16.653 | 17.2159 | 17.5532 | 17.5178 | 16.496 | 14.8528 | 16.8497 | 17.1768 | 17.4709 | 17.5249 | 17.2678 | 16.473 | 14.704 | 6.4336 | 8.4559 | 6.3458 | 6.182 | 6.1414 | 6.6448 | 7.6477 | 15.7698 | 15.4399 | 15.3169 | 14.2669 | 14.1606 | 14.1108 |  |  |  | 10.64 | 9.4873 | 9.1942 | 9.4079 | -0.072279 | -0.13153 | 12.6919 |  |  | 10.554 |  |  | 16.8815 | 16.0744 | 15.0508 | 16.3812 | 15.6691 | 14.7797 | 10.3097 | 10.8374 | 11.1816 | 11.2171 | 9.4233 |  | 10.475 | 9.0347 | 9.8336 | 9.4436 | 10.9533 | 11.7937 |  | 12.1966 |  |  | 11.5743 | 12.2483 | 12.4137 | [6 empty] | 12.5409 |  |  | 11.3644 |  |  | 9.1736 | 10.1048 | 11.7334 | 7.5361 | 9.1088 | 12.3705 | 7.9377 | 9.5238 | 12.206 | 9.1751 | 10.4979 | 7.7031 | 10.3403 | 8.3638 | 10.3183 | 7.9875 | 9.6727 | 13.1212 | 10.4557 | 10.2068 | 11.4528 | 8.1994 | 9.6927 | 12.6341 | 8.1566 | 10.4277 | 9.8036 | 9.959 | 8.4983 | 10.4461 | -0.099009 | 20.9545 | 0.032919 | 0.046517 | -37.7798 | 3.12 | -2.77 | 0.36 | 0.69733 | 0.15846 | 0.25141 | 0.094465 | 0.36125 | -0.265 | 1.0522 | 0.39613 | 0.3858 | 0.41133 | 0.37096 | 0.49715 | 0.41439 | 0.40199
42810.438 | -174 | 18.4675 | 18.5728 | 18.5807 | 18.584 | 17.929 | 16.5674 | 14.6387 | 16.6957 | 17.1897 | 17.2693 | 17.283 | 16.8234 | 15.8499 | 14.4715 | 14.8897 | 14.9191 | 15.4824 | 13.3494 | 13.4722 | 14.0442 |  |  |  | 16.5957 | 15.9286 | 15.0314 | 10.3251 | 9.7932 | 10.4198 | 17.1361 | 16.291 | 15.0899 | 16.8517 | 16.1368 | 15.1332 | 10.7289 | 11.8318 |  | 12.0415 | 10.6435 | 10.2232 | 9.1248 |  | 6.4903 | 6.5322 | 6.0339 | 6.1533 | 6.262 | 6.4805 | 7.0975 | 4.8961 | 6.5439 | 4.7775 | 6.7518 | 8.0387 | 42.4862 | 47.6047 | 43.4142 | 15.1718 |  |  | 0.083015 | 0.066455 | 0.18518 | -0.047314 | -0.015608 | 0.29656 | 0.46317 | -0.086904 | -0.33353 | 0.2669 | -0.27849 | 8.8713 | 8.8722 | 2.0086 | 15.7179 | 16.6573 | 17.2148 | 17.5502 | 17.5115 | 16.4961 | 14.8517 | 16.8463 | 17.1802 | 17.4652 | 17.5276 | 17.2673 | 16.4759 | 14.7044 | 6.4388 | 8.4625 | 6.3778 | 6.154 | 6.1465 | 6.6412 | 7.6455 | 15.7621 | 15.4422 | 15.3221 | 14.2617 | 14.1597 | 14.1044 |  |  |  | 10.6366 | 9.5029 | 9.1961 | 9.4279 | -0.0029902 | 0.044064 | 12.6777 |  |  | 10.5432 |  |  | 16.875 | 16.0632 | 15.0417 | 16.3784 | 15.6608 | 14.7712 | 10.3198 | 10.841 | 11.18 | 11.216 | 9.4423 |  | 10.4774 | 9.0758 | 9.8355 | 9.4419 | 10.9548 | 11.7879 |  | 12.1969 |  |  | 11.6071 | 12.2672 | 12.4114 | [6 empty] | 12.555 |  |  | 11.3629 |  |  | 9.1832 | 10.1097 | 11.7429 | 7.5285 | 9.1103 | 12.3742 | 7.9487 | 9.5275 | 12.1997 | 9.1695 | 10.486 | 7.7014 | 10.3407 | 8.3643 | 10.3174 | 7.998 | 9.6746 | 13.1133 | 10.463 | 10.221 | 11.4623 | 8.2144 | 9.6879 | 12.6242 | 8.1681 | 10.4337 | 9.8086 | 9.9681 | 8.51 | 10.457 | 0.059116 | 20.9544 | 0.033665 | 0.04706 | -37.7694 | 3.1201 | 2.13 | 0.31 | 0.33812 | 0.30044 | 0.50153 | -0.25351 | -0.14559 | 0.63462 | 0.7931 | 0.39567 | 0.38472 | 0.41143 | 0.36996 | 0.49335 | 0.41279 | 0.40132
42810.438 | -173 | 18.4642 | 18.578 | 18.5812 | 18.5882 | 17.9222 | 16.5681 | 14.6371 | 16.6946 | 17.1861 | 17.2783 | 17.281 | 16.8222 | 15.8581 | 14.4682 | 14.8805 | 14.9162 | 15.4781 | 13.3447 | 13.4657 | 14.0402 |  |  |  | 16.5852 | 15.9193 | 15.0165 | 10.329 | 9.8001 | 10.4133 | 17.1386 | 16.2911 | 15.0992 | 16.8524 | 16.1504 | 15.1411 | 10.7383 | 11.8209 |  | 12.035 | 10.6682 | 10.2414 | 9.189 |  | 6.4945 | 6.5352 | 6.0312 | 6.1633 | 6.2673 | 6.5014 | 7.1504 | 4.9346 | 6.5492 | 4.6785 | 6.7622 | 8.0355 | 42.4969 | 47.6358 | 43.4061 | 15.1573 |  |  | 0.21444 | 0.10851 | 0.13327 | 0.25693 | 0.045504 | -0.14765 | 0.48814 | -0.1145 | -0.18875 | -0.36334 | -0.24709 | 8.8704 | 8.8712 | 2.0084 | 15.7175 | 16.6538 | 17.2205 | 17.548 | 17.5153 | 16.4919 | 14.8491 | 16.8389 | 17.1792 | 17.4752 | 17.5179 | 17.2633 | 16.4729 | 14.7087 | 6.4874 | 8.4846 | 6.4875 | 6.1258 | 6.1301 | 6.6417 | 7.6503 | 15.7701 | 15.4419 | 15.3185 | 14.2664 | 14.1582 | 14.1073 |  |  |  | 10.6449 | 9.4986 | 9.2045 | 9.4326 | -0.10571 | 0.044628 | 12.6782 |  |  | 10.5469 |  |  | 16.8798 | 16.0677 | 15.0464 | 16.3762 | 15.6618 | 14.7707 | 10.3347 | 10.8526 | 11.1848 | 11.2136 | 9.467 |  | 10.4851 | 9.1176 | 9.8496 | 9.4494 | 10.9508 | 11.7884 |  | 12.1971 |  |  | 11.6412 | 12.3041 | 12.4198 | [6 empty] | 12.5664 |  |  | 11.3749 |  |  | 9.1828 | 10.1265 | 11.7444 | 7.5365 | 9.1248 | 12.3793 | 7.9581 | 9.5362 | 12.1954 | 9.1717 | 10.482 | 7.7184 | 10.3427 | 8.3801 | 10.3217 | 7.9914 | 9.6769 | 13.1009 | 10.463 | 10.2055 | 11.4701 | 8.2069 | 9.685 | 12.5975 | 8.1722 | 10.448 | 9.8079 | 9.9698 | 8.5037 | 10.4582 | 0.080687 | 20.9534 | 0.033424 | 0.046756 | -37.7699 | 3.1201 | 2.42 | 0.33 | 0.54343 | 0.38392 | 0.42547 | 0.59076 | 0.2486 | -0.44781 | 0.81423 | 0.39524 | 0.38402 | 0.41109 | 0.36461 | 0.48171 | 0.41131 | 0.40147
42810.438 | -172 | 18.4571 | 18.5717 | 18.5746 | 18.5816 | 17.9151 | 16.5625 | 14.6325 | 16.6934 | 17.1846 | 17.272 | 17.2794 | 16.825 | 15.8535 | 14.4625 | 14.8893 | 14.9099 | 15.4865 | 13.3449 | 13.4605 | 14.033 |  |  |  | 16.584 | 15.9225 | 15.0318 | 10.3308 | 9.8218 | 10.4095 | 17.1388 | 16.291 | 15.0961 | 16.8498 | 16.1447 | 15.1371 | 10.741 | 11.7802 |  | 12.0329 | 10.6777 | 10.2675 | 9.2594 |  | 6.4929 | 6.5205 | 6.0231 | 6.1555 | 6.2616 | 6.5384 | 7.1822 | 4.911 | 6.53 | 4.6584 | 6.7548 | 8.039 | 42.5303 | 47.653 | 43.4075 | 15.1533 |  |  | 0.11193 | -0.015681 | 0.1911 | 0.11434 | -0.001808 | -0.054344 | 0.43097 | -0.022504 | -0.83618 | -0.52509 | -0.60853 | 8.8685 | 8.8695 | 2.0084 | 15.7124 | 16.6492 | 17.2111 | 17.5473 | 17.5176 | 16.4908 | 14.8499 | 16.8336 | 17.1732 | 17.4688 | 17.5192 | 17.2692 | 16.4735 | 14.6993 | 6.5192 | 8.4712 | 6.6274 | 6.0909 | 6.1008 | 6.6439 | 7.6539 | 15.7624 | 15.4409 | 15.3116 | 14.2613 | 14.153 | 14.0986 |  |  |  | 10.6394 | 9.4998 | 9.2026 | 9.4249 | -0.0062318 | -0.11722 | 12.6766 |  |  | 10.5422 |  |  | 16.8777 | 16.0668 | 15.0402 | 16.3726 | 15.6594 | 14.7606 | 10.3401 | 10.8515 | 11.1823 | 11.2078 | 9.464 |  | 10.4817 | 9.1449 | 9.849 | 9.4527 | 10.9483 | 11.7905 |  | 12.1945 |  |  | 11.6528 | 12.3243 | 12.4439 | [6 empty] | 12.5556 |  |  | 11.3731 |  |  | 9.1799 | 10.1314 | 11.745 | 7.5287 | 9.1353 | 12.3783 | 7.9695 | 9.5333 | 12.1789 | 9.1599 | 10.4839 | 7.7332 | 10.3451 | 8.3871 | 10.3213 | 7.9771 | 9.6858 | 13.0963 | 10.4705 | 10.2083 | 11.488 | 8.2181 | 9.6784 | 12.593 | 8.1742 | 10.4658 | 9.7957 | 9.9772 | 8.5167 | 10.4639 | -0.091305 | 20.9582 | 0.032953 | 0.047856 | -37.7757 | 3.1201 | 3.09 | 0.25 | 0.39261 | -0.14594 | 0.50947 | 0.39408 | -0.049557 | -0.27169 | 0.76511 | 0.39521 | 0.38324 | 0.41091 | 0.36134 | 0.46658 | 0.40944 | 0.4015
42810.4381 | -171 | 18.4694 | 18.587 | 18.5796 | 18.596 | 17.9331 | 16.5754 | 14.6432 | 16.7045 | 17.1941 | 17.2772 | 17.2887 | 16.8297 | 15.853 | 14.4693 | 14.8861 | 14.9121 | 15.4809 | 13.3476 | 13.4681 | 14.0319 |  |  |  | 16.5872 | 15.9249 | 15.0215 | 10.3399 | 9.8411 | 10.4167 | 17.1406 | 16.2913 | 15.1007 | 16.8554 | 16.1461 | 15.1384 | 10.7446 | 11.7521 |  | 12.034 | 10.696 | 10.2987 | 9.3426 |  | 6.4995 | 6.5304 | 6.0385 | 6.1696 | 6.2721 | 6.5848 | 7.2283 | 4.7978 | 6.5372 | 4.6528 | 6.7534 | 8.0401 | 42.5486 | 47.655 | 43.4075 | 15.1509 |  |  | 0.046219 | 0.088143 | -0.020492 | 0.068998 | -0.024808 | -0.051056 | 0.38891 | -0.017248 | 0.52154 | -0.31781 | -0.45851 | 8.8679 | 8.8691 | 2.0086 | 15.7104 | 16.6477 | 17.2041 | 17.5388 | 17.5147 | 16.4918 | 14.8487 | 16.8318 | 17.173 | 17.4804 | 17.5198 | 17.2596 | 16.4699 | 14.7075 | 6.4942 | 8.428 | 6.5509 | 6.1366 | 6.0772 | 6.6448 | 7.6518 | 15.7675 | 15.4451 | 15.3187 | 14.2669 | 14.1594 | 14.1081 |  |  |  | 10.6381 | 9.5086 | 9.209 | 9.4165 | -0.1284 | -0.17557 | 12.6905 |  |  | 10.5401 |  |  | 16.8753 | 16.0663 | 15.036 | 16.3736 | 15.6536 | 14.7656 | 10.3489 | 10.8583 | 11.1836 | 11.2233 | 9.4655 |  | 10.4732 | 9.1283 | 9.8477 | 9.4633 | 10.955 | 11.8107 |  | 12.1892 |  |  | 11.6791 | 12.3535 | 12.444 | [6 empty] | 12.5605 |  |  | 11.379 |  |  | 9.1806 | 10.1206 | 11.7319 | 7.5124 | 9.1354 | 12.3689 | 7.9796 | 9.4952 | 12.158 | 9.1558 | 10.4618 | 7.7228 | 10.3192 | 8.3808 | 10.3183 | 7.9544 | 9.6737 | 13.0882 | 10.4606 | 10.1881 | 11.4933 | 8.223 | 9.675 | 12.5911 | 8.1616 | 10.4585 | 9.781 | 9.9792 | 8.5076 | 10.473 | -0.046814 | 20.9495 | 0.032621 | 0.045815 | -37.7834 | 3.1201 | 6.47 | 0.39 | 0.25229 | 0.34601 | -0.16684 | 0.30614 | -0.18358 | -0.26337 | 0.72689 | 0.39489 | 0.38366 | 0.41084 | 0.36422 | 0.47484 | 0.40725 | 0.40169
42810.4381 | -170 | 18.4632 | 18.5826 | 18.5765 | 18.5883 | 17.923 | 16.5773 | 14.642 | 16.7018 | 17.1858 | 17.2756 | 17.2818 | 16.8227 | 15.8508 | 14.465 | 14.8854 | 14.909 | 15.4796 | 13.3489 | 13.4644 | 14.031 |  |  |  | 16.5886 | 15.9147 | 15.0244 | 10.3395 | 9.8635 | 10.3916 | 17.1442 | 16.2896 | 15.1032 | 16.854 | 16.1505 | 15.1325 | 10.7453 | 11.7285 |  | 12.0324 | 10.7042 | 10.3212 | 9.388 |  | 6.504 | 6.5353 | 6.0423 | 6.1779 | 6.2924 | 6.6055 | 7.2788 | 4.6501 | 6.5453 | 4.6779 | 6.7594 | 8.0415 | 42.5617 | 47.6642 | 43.4016 | 15.1387 |  |  | 0.10207 | 0.035571 | 0.21738 | -0.082798 | -0.037948 | 0.14016 | 0.41191 | -0.084932 | -0.91383 | -0.51691 | -0.60773 | 8.8687 | 8.87 | 2.0081 | 15.701 | 16.6515 | 17.2042 | 17.5441 | 17.511 | 16.4876 | 14.848 | 16.8387 | 17.1775 | 17.473 | 17.52 | 17.2654 | 16.4615 | 14.7029 | 6.4362 | 8.3875 | 6.3594 | 6.1704 | 6.0774 | 6.6512 | 7.6606 | 15.7592 | 15.4429 | 15.3249 | 14.265 | 14.159 | 14.1022 |  |  |  | 10.64 | 9.506 | 9.2012 | 9.4238 | -0.16912 | -0.13774 | 12.6863 |  |  | 10.5405 |  |  | 16.8685 | 16.0624 | 15.0378 | 16.3732 | 15.6545 | 14.7636 | 10.3668 | 10.8627 | 11.1865 | 11.2171 | 9.4706 |  | 10.4683 | 9.0987 | 9.8467 | 9.4687 | 10.9433 | 11.8329 |  | 12.1801 |  |  | 11.6867 | 12.3703 | 12.4498 | [6 empty] | 12.5687 |  |  | 11.4005 |  |  | 9.1673 | 10.1172 | 11.7295 | 7.5031 | 9.1301 | 12.3685 | 7.9736 | 9.4918 | 12.1526 | 9.15 | 10.453 | 7.6955 | 10.3138 | 8.3692 | 10.3078 | 7.9573 | 9.691 | 13.0834 | 10.4696 | 10.1959 | 11.5065 | 8.222 | 9.6779 | 12.5894 | 8.1632 | 10.4648 | 9.7759 | 9.9791 | 8.5183 | 10.4677 | 0.11767 | 20.9537 | 0.031588 | 0.04604 | -37.7187 | 3.1201 | 6.49 | 0.41 | 0.37491 | 0.21981 | 0.54339 | -0.33536 | -0.22707 | 0.43639 | 0.7481 | 0.39459 | 0.38445 | 0.4103 | 0.37141 | 0.49714 | 0.40601 | 0.40155
42810.4381 | -169 | 18.4568 | 18.5733 | 18.573 | 18.5831 | 17.9245 | 16.573 | 14.6336 | 16.6957 | 17.187 | 17.2818 | 17.2833 | 16.8244 | 15.8537 | 14.4673 | 14.88 | 14.9044 | 15.474 | 13.3367 | 13.4487 | 14.0306 |  |  |  | 16.5746 | 15.9072 | 15.0103 | 10.3452 | 9.8663 | 10.3899 | 17.14 | 16.2874 | 15.097 | 16.8569 | 16.1431 | 15.1349 | 10.7381 | 11.704 |  | 12.033 | 10.7086 | 10.3329 | 9.395 |  | 6.4948 | 6.5264 | 6.0464 | 6.1846 | 6.2775 | 6.6153 | 7.2828 | 4.5823 | 6.5314 | 4.641 | 6.7536 | 8.0371 | 42.5681 | 47.6861 | 43.4032 | 15.1298 |  |  | 0.19604 | 0.027687 | -0.011292 | -0.12485 | 0.23016 | -0.1746 | 0.34883 | -0.07376 | -0.73421 | 0.82119 | -0.44937 | 8.8698 | 8.8706 | 2.0085 | 15.7071 | 16.6523 | 17.2101 | 17.5419 | 17.5164 | 16.4931 | 14.8461 | 16.8417 | 17.1742 | 17.4662 | 17.5194 | 17.2634 | 16.4696 | 14.7037 | 6.3884 | 8.3692 | 6.2062 | 6.1282 | 6.0871 | 6.6396 | 7.6554 | 15.7573 | 15.4358 | 15.3236 | 14.265 | 14.1528 | 14.1005 |  |  |  | 10.6386 | 9.5025 | 9.21 | 9.4575 | -0.20519 | -0.13586 | 12.6887 |  |  | 10.5558 |  |  | 16.8711 | 16.0538 | 15.0389 | 16.3785 | 15.6518 | 14.764 | 10.3756 | 10.8651 | 11.1861 | 11.2219 | 9.4923 |  | 10.4702 | 9.0521 | 9.8482 | 9.492 | 10.9424 | 11.8194 |  | 12.183 |  |  | 11.671 | 12.3509 | 12.4589 | [6 empty] | 12.5669 |  |  | 11.4027 |  |  | 9.179 | 10.1231 | 11.7424 | 7.5052 | 9.1373 | 12.3807 | 7.9805 | 9.498 | 12.1565 | 9.1534 | 10.4427 | 7.6896 | 10.3132 | 8.362 | 10.322 | 7.9582 | 9.6946 | 13.0679 | 10.4612 | 10.1848 | 11.5177 | 8.2353 | 9.6704 | 12.5893 | 8.1711 | 10.4602 | 9.7788 | 9.9755 | 8.5083 | 10.472 | -0.03988 | 20.9569 | 0.033269 | 0.047335 | -37.7768 | 3.1201 | 12.27 | 0.26 | 0.51957 | 0.19392 | -0.12385 | -0.4118 | 0.55921 | -0.48706 | 0.68845 | 0.39405 | 0.38579 | 0.40963 | 0.37538 | 0.51356 | 0.40558 | 0.40057
42810.4381 | -168 | 18.4483 | 18.574 | 18.5648 | 18.579 | 17.9261 | 16.5648 | 14.6316 | 16.6904 | 17.1887 | 17.2765 | 17.2816 | 16.8147 | 15.8534 | 14.4671 | 14.8887 | 14.9075 | 15.4799 | 13.3391 | 13.4666 | 14.0333 |  |  |  | 16.5846 | 15.92 | 15.0199 | 10.3536 | 9.8905 | 10.3928 | 17.1366 | 16.2822 | 15.0958 | 16.8533 | 16.1393 | 15.1416 | 10.7432 | 11.6741 |  | 12.0277 | 10.7135 | 10.3437 | 9.3707 |  | 6.4941 | 6.5268 | 6.0496 | 6.2071 | 6.2849 | 6.6286 | 7.2497 | 4.6673 | 6.5285 | 4.6076 | 6.7495 | 8.0351 | 42.5768 | 47.7042 | 43.4076 | 15.1269 |  |  | 0.1139 | -0.14185 | 0.064276 | -0.008542 | 0.22161 | 0.000196 | 0.11227 | -0.088216 | -0.50089 | -0.30333 | -0.54633 | 8.869 | 8.8703 | 2.0084 | 15.7081 | 16.643 | 17.2172 | 17.5424 | 17.5156 | 16.4999 | 14.8551 | 16.8356 | 17.1743 | 17.4718 | 17.5203 | 17.2703 | 16.4644 | 14.7025 | 6.3524 | 8.3719 | 6.1179 | 6.0662 | 6.0659 | 6.6413 | 7.6746 | 15.7533 | 15.4363 | 15.3146 | 14.2596 | 14.1486 | 14.0976 |  |  |  | 10.6303 | 9.5062 | 9.2112 | 9.5084 | -0.057692 | -0.045896 | 12.6848 |  |  | 10.5515 |  |  | 16.8585 | 16.0573 | 15.0355 | 16.3688 | 15.659 | 14.7723 | 10.3977 | 10.8696 | 11.1849 | 11.2249 | 9.4972 |  | 10.4729 | 9.0441 | 9.8587 | 9.4964 | 10.9457 | 11.8306 |  | 12.184 |  |  | 11.6407 | 12.342 | 12.4749 | [6 empty] | 12.5672 |  |  | 11.4104 |  |  | 9.1875 | 10.1311 | 11.7534 | 7.5124 | 9.1362 | 12.3836 | 7.9781 | 9.506 | 12.1639 | 9.1654 | 10.4358 | 7.6782 | 10.3063 | 8.3656 | 10.3328 | 7.9773 | 9.7292 | 13.06 | 10.4565 | 10.1851 | 11.5322 | 8.24 | 9.683 | 12.6126 | 8.1803 | 10.4748 | 9.787 | 9.9939 | 8.5148 | 10.5013 | -0.10209 | 20.9469 | 0.03339 | 0.048276 | -37.75 | 3.1201 | 0.75 | 0.34 | 0.39604 | -0.43894 | 0.29547 | -0.10771 | 0.54875 | 0.016319 | 0.39057 | 0.394 | 0.38636 | 0.40961 | 0.37958 | 0.52561 | 0.40643 | 0.39888
42810.4381 | -167 | 18.4631 | 18.5865 | 18.5841 | 18.5872 | 17.9311 | 16.5798 | 14.6422 | 16.7076 | 17.1914 | 17.2876 | 17.2892 | 16.8313 | 15.8534 | 14.4776 | 14.8809 | 14.9062 | 15.4764 | 13.3364 | 13.4608 | 14.036 |  |  |  | 16.5834 | 15.9204 | 15.0262 | 10.357 | 9.905 | 10.4045 | 17.1312 | 16.2829 | 15.0942 | 16.862 | 16.1302 | 15.1362 | 10.749 | 11.689 |  | 12.025 | 10.7223 | 10.3545 | 9.3303 |  | 6.4929 | 6.5351 | 6.0551 | 6.2078 | 6.3172 | 6.6595 | 7.2154 | 4.7376 | 6.5293 | 4.5779 | 6.7477 | 8.0408 | 42.5876 | 47.7064 | 43.4138 | 15.1211 |  |  | 0.010735 | 0.10983 | 0.075448 | 0.12157 | -0.10958 | -0.23111 | -0.60662 | -0.17693 | 0.1773 | -0.45942 | -0.39632 | 8.87 | 8.8712 | 2.0088 | 15.7028 | 16.6466 | 17.2134 | 17.5503 | 17.5117 | 16.4975 | 14.8535 | 16.8397 | 17.1796 | 17.4735 | 17.5232 | 17.2671 | 16.4672 | 14.6999 | 6.2731 | 8.3215 | 5.9987 | 6.0468 | 6.0082 | 6.6357 | 7.6604 | 15.7548 | 15.4442 | 15.3118 | 14.2658 | 14.1528 | 14.0982 |  |  |  | 10.6334 | 9.5056 | 9.2141 | 9.5273 | -0.020211 | -0.17801 | 12.6884 |  |  | 10.5417 |  |  | 16.8609 | 16.0615 | 15.0375 | 16.3748 | 15.6644 | 14.765 | 10.4142 | 10.87 | 11.1902 | 11.2292 | 9.4779 |  | 10.468 | 9.0303 | 9.8522 | 9.4707 | 10.9462 | 11.8207 |  | 12.1828 |  |  | 11.6346 | 12.3519 | 12.4848 | [6 empty] | 12.572 |  |  | 11.4238 |  |  | 9.2005 | 10.1337 | 11.7662 | 7.538 | 9.1419 | 12.3964 | 7.994 | 9.526 | 12.174 | 9.1704 | 10.4515 | 7.6843 | 10.3167 | 8.3709 | 10.3407 | 7.9976 | 9.688 | 13.05 | 10.4541 | 10.1788 | 11.5282 | 8.2383 | 9.6816 | 12.6095 | 8.1749 | 10.47 | 9.7915 | 9.9888 | 8.5072 | 10.5074 | -0.03988 | 20.9663 | 0.033969 | 0.047567 | -37.6763 | 3.1201 | 8.85 | 0.39 | 0.12159 | 0.38624 | 0.32013 | 0.40636 | -0.38588 | -0.56041 | -0.90794 | 0.39438 | 0.38653 | 0.41034 | 0.38774 | 0.5372 | 0.40774 | 0.39846
42810.4381 | -166 | 18.4597 | 18.5747 | 18.5723 | 18.5803 | 17.9223 | 16.5646 | 14.6379 | 16.7003 | 17.1845 | 17.2773 | 17.2835 | 16.8265 | 15.8516 | 14.4668 | 14.8822 | 14.9095 | 15.4794 | 13.3414 | 13.4628 | 14.037 |  |  |  | 16.5866 | 15.9254 | 15.0201 | 10.3687 | 9.921 | 10.4297 | 17.1316 | 16.2886 | 15.0906 | 16.8486 | 16.1414 | 15.1333 | 10.7459 | 11.7184 |  | 12.0287 | 10.729 | 10.3685 | 9.2679 |  | 6.4895 | 6.5379 | 6.0524 | 6.2079 | 6.3122 | 6.6306 | 7.1504 | 4.7537 | 6.5261 | 4.6271 | 6.7461 | 8.0398 | 42.5996 | 47.6935 | 43.4222 | 15.1113 |  |  | 0.040303 | -0.16091 | 0.074792 | -0.02957 | 0.002792 | -0.48016 | -0.097352 | 0.015608 | -0.88113 | -0.0047882 | -0.44162 | 8.8682 | 8.8693 | 2.0082 | 15.7003 | 16.6487 | 17.2079 | 17.5438 | 17.5062 | 16.4932 | 14.8469 | 16.8372 | 17.171 | 17.4727 | 17.5207 | 17.2633 | 16.4637 | 14.6965 | 6.2205 | 8.3312 | 5.8751 | 5.9769 | 5.9999 | 6.6411 | 7.6683 | 15.762 | 15.4401 | 15.3273 | 14.272 | 14.153 | 14.0989 |  |  |  | 10.6468 | 9.5168 | 9.2173 | 9.4983 | -0.14906 | -0.17425 | 12.6857 |  |  | 10.5468 |  |  | 16.8654 | 16.0648 | 15.0363 | 16.3704 | 15.6626 | 14.7585 | 10.4248 | 10.8634 | 11.1949 | 11.2255 | 9.4853 |  | 10.4774 | 9.0438 | 9.8571 | 9.4305 | 10.9507 | 11.8378 |  | 12.1869 |  |  | 11.6218 | 12.3672 | 12.4923 | [6 empty] | 12.5734 |  |  | 11.4294 |  |  | 9.2076 | 10.1386 | 11.7655 | 7.5527 | 9.14 | 12.4029 | 7.9969 | 9.5403 | 12.1787 | 9.1733 | 10.4567 | 7.6845 | 10.3173 | 8.373 | 10.3566 | 8.0067 | 9.6514 | 13.0369 | 10.4576 | 10.1716 | 11.5298 | 8.2346 | 9.6849 | 12.6126 | 8.1655 | 10.4673 | 9.7854 | 9.9954 | 8.5053 | 10.5179 | 0.050834 | 20.9393 | 0.032959 | 0.04795 | -37.6839 | 3.1201 | -8.04 | 0.26 | 0.2356 | -0.46751 | 0.31874 | -0.20041 | 0.061593 | -0.80773 | -0.3637 | 0.39448 | 0.38632 | 0.41161 | 0.39421 | 0.55185 | 0.40937 | 0.3997
42810.4381 | -165 | 18.4464 | 18.5636 | 18.5659 | 18.5764 | 17.9244 | 16.5602 | 14.6281 | 16.6968 | 17.1805 | 17.2789 | 17.2816 | 16.8225 | 15.8546 | 14.4639 | 14.8829 | 14.9017 | 15.4674 | 13.3413 | 13.4624 | 14.0301 |  |  |  | 16.5787 | 15.9153 | 15.0133 | 10.3711 | 9.9263 | 10.4463 | 17.1342 | 16.2915 | 15.1002 | 16.8527 | 16.1486 | 15.1412 | 10.7521 | 11.7576 |  | 12.0277 | 10.7353 | 10.3756 | 9.2383 |  | 6.4864 | 6.5344 | 6.0429 | 6.2016 | 6.287 | 6.5996 | 7.0915 | 4.786 | 6.5257 | 4.6777 | 6.7451 | 8.0376 | 42.6261 | 47.6919 | 43.4338 | 15.1023 |  |  | 0.041619 | -0.12214 | -0.049404 | -0.15902 | 0.14933 | -0.5347 | -0.044784 | -0.090844 | -0.57717 | -1.3433 | -0.4448 | 8.8701 | 8.871 | 2.0085 | 15.6964 | 16.6436 | 17.2097 | 17.5393 | 17.5057 | 16.496 | 14.8449 | 16.8306 | 17.1687 | 17.4753 | 17.5206 | 17.2646 | 16.4723 | 14.6975 | 6.1383 | 8.2814 | 5.8432 | 5.8893 | 5.9359 | 6.6316 | 7.6696 | 15.7562 | 15.4387 | 15.3216 | 14.2648 | 14.1565 | 14.0891 |  |  |  | 10.633 | 9.529 | 9.2194 | 9.4435 | -0.20377 | -0.30561 | 12.6808 |  |  | 10.5394 |  |  | 16.8639 | 16.0569 | 15.0366 | 16.3635 | 15.654 | 14.751 | 10.4401 | 10.85 | 11.1944 | 11.228 | 9.48 |  | 10.475 | 9.051 | 9.8519 | 9.3939 | 10.9447 | 11.8386 |  | 12.179 |  |  | 11.6272 | 12.3832 | 12.489 | [6 empty] | 12.5794 |  |  | 11.4286 |  |  | 9.2101 | 10.1427 | 11.7644 | 7.5618 | 9.1349 | 12.3955 | 7.9992 | 9.5474 | 12.1896 | 9.1762 | 10.4567 | 7.6936 | 10.3148 | 8.3845 | 10.3678 | 8.0164 | 9.614 | 13.0242 | 10.461 | 10.1643 | 11.5319 | 8.2288 | 9.6822 | 12.613 | 8.1601 | 10.4687 | 9.7877 | 9.999 | 8.502 | 10.5272 | -0.10209 | 20.9575 | 0.033154 | 0.049231 | -37.7601 | 3.1201 | -3.44 | 0.29 | 0.23942 | -0.40731 | -0.25905 | -0.46476 | 0.45042 | -0.85232 | -0.24667 | 0.39455 | 0.38594 | 0.41243 | 0.40224 | 0.55554 | 0.4104 | 0.40077
42810.4381 | -164 | 18.4549 | 18.5754 | 18.5774 | 18.5822 | 17.9308 | 16.5682 | 14.6383 | 16.6952 | 17.1833 | 17.2772 | 17.287 | 16.8247 | 15.858 | 14.4702 | 14.8769 | 14.8966 | 15.4651 | 13.3406 | 13.454 | 14.0304 |  |  |  | 16.575 | 15.9101 | 15.0133 | 10.3803 | 9.9369 | 10.4726 | 17.13 | 16.2851 | 15.0971 | 16.8481 | 16.1427 | 15.1364 | 10.7457 | 11.7893 |  | 12.0264 | 10.743 | 10.3868 | 9.2051 |  | 6.4803 | 6.5281 | 6.0358 | 6.1806 | 6.2671 | 6.577 | 7.0376 | 4.7799 | 6.5262 | 4.7381 | 6.7416 | 8.0383 | 42.6559 | 47.6996 | 43.4525 | 15.0916 |  |  | 0.22561 | -0.090593 | -0.23734 | -0.27073 | 0.015276 | -1.0683 | 0.36788 | -0.024476 | -0.37907 | -1.781 | -0.46765 | 8.8687 | 8.8699 | 2.0083 | 15.698 | 16.6381 | 17.2087 | 17.5368 | 17.5125 | 16.4782 | 14.8388 | 16.8326 | 17.1722 | 17.462 | 17.5108 | 17.2648 | 16.4656 | 14.7082 | 6.089 | 8.2471 | 5.7178 | 5.7957 | 5.8602 | 6.6327 | 7.671 | 15.7543 | 15.4255 | 15.3143 | 14.2572 | 14.149 | 14.0977 |  |  |  | 10.6373 | 9.5304 | 9.2246 | 9.4036 | -0.40941 | -0.19966 | 12.6917 |  |  | 10.546 |  |  | 16.8737 | 16.0514 | 15.036 | 16.3669 | 15.6567 | 14.7641 | 10.4701 | 10.8576 | 11.1853 | 11.2196 | 9.4715 |  | 10.4886 | 9.0831 | 9.8676 | 9.3769 | 10.9418 | 11.8442 |  | 12.1786 |  |  | 11.6508 | 12.3768 | 12.4925 | [6 empty] | 12.5999 |  |  | 11.423 |  |  | 9.2209 | 10.1504 | 11.7682 | 7.572 | 9.1321 | 12.4046 | 8.0073 | 9.5654 | 12.2038 | 9.1788 | 10.4595 | 7.7049 | 10.3182 | 8.3987 | 10.3807 | 8.0222 | 9.6052 | 13.013 | 10.4544 | 10.1589 | 11.5361 | 8.2318 | 9.6813 | 12.6161 | 8.1631 | 10.4775 | 9.7876 | 10.0022 | 8.5082 | 10.5351 | -0.16257 | 20.9572 | 0.031852 | 0.048348 | -37.8765 | 3.1201 | -9.21 | 0.35 | 0.55746 | -0.35079 | -0.56778 | -0.60641 | 0.14406 | -1.2047 | 0.70695 | 0.39524 | 0.38557 | 0.4128 | 0.40784 | 0.56964 | 0.41111 | 0.40202
42810.4381 | -163 | 18.4516 | 18.5739 | 18.5719 | 18.5725 | 17.9208 | 16.5601 | 14.6288 | 16.6937 | 17.1806 | 17.2716 | 17.2806 | 16.82 | 15.8543 | 14.4677 | 14.8748 | 14.9014 | 15.4723 | 13.3418 | 13.4651 | 14.0313 |  |  |  | 16.5757 | 15.9179 | 15.0198 | 10.3868 | 9.9461 | 10.5024 | 17.1336 | 16.2892 | 15.0939 | 16.8532 | 16.1361 | 15.1345 | 10.7473 | 11.8357 |  | 12.0229 | 10.7464 | 10.3916 | 9.2336 |  | 6.485 | 6.5294 | 6.0182 | 6.1588 | 6.2426 | 6.5579 | 6.9821 | 4.7847 | 6.5349 | 4.7547 | 6.7464 | 8.0404 | 42.6787 | 47.7108 | 43.4732 | 15.0928 |  |  | 0.17698 | -0.22859 | -0.061888 | 0.095282 | 0.062592 | -0.90005 | -0.032956 | 0.20223 | -0.41623 | -0.14431 | -0.6274 | 8.8675 | 8.8687 | 2.0085 | 15.6911 | 16.6346 | 17.2139 | 17.5484 | 17.5055 | 16.4878 | 14.8436 | 16.8284 | 17.1682 | 17.4707 | 17.5175 | 17.2607 | 16.4654 | 14.6985 | 6.0397 | 8.2204 | 5.65 | 5.7347 | 5.7742 | 6.6297 | 7.665 | 15.7462 | 15.426 | 15.3108 | 14.2508 | 14.1438 | 14.0846 |  |  |  | 10.6328 | 9.5326 | 9.2159 | 9.375 | -0.36666 | -0.28585 | 12.6848 |  |  | 10.5636 |  |  | 16.8689 | 16.062 | 15.0375 | 16.3762 | 15.6639 | 14.7752 | 10.418 | 10.8545 | 11.2034 | 11.2475 | 9.4777 |  | 10.4737 | 9.0598 | 9.86 | 9.3344 | 10.9343 | 11.8342 |  | 12.1878 |  |  | 11.6662 | 12.3869 | 12.4912 | [6 empty] | 12.6128 |  |  | 11.4167 |  |  | 9.2246 | 10.1472 | 11.7679 | 7.5833 | 9.1295 | 12.4046 | 8.0042 | 9.5792 | 12.2088 | 9.1768 | 10.4539 | 7.7075 | 10.3211 | 8.3937 | 10.3917 | 8.0278 | 9.6079 | 13.0064 | 10.449 | 10.1609 | 11.5353 | 8.2388 | 9.6906 | 12.6218 | 8.1698 | 10.4747 | 9.7743 | 10.0068 | 8.5097 | 10.5452 | -0.010605 | 20.9615 | 0.031381 | 0.047053 | -37.8171 | 3.1201 | -2.19 | 0.24 | 0.49377 | -0.55722 | -0.28993 | 0.35975 | 0.29159 | -1.1057 | -0.21159 | 0.39457 | 0.38597 | 0.41374 | 0.41296 | 0.57648 | 0.41037 | 0.40267
42810.4382 | -162 | 18.4473 | 18.5698 | 18.5655 | 18.5687 | 17.9134 | 16.5552 | 14.6251 | 16.6853 | 17.1807 | 17.2658 | 17.2716 | 16.8183 | 15.8487 | 14.457 | 14.8674 | 14.9061 | 15.4766 | 13.3369 | 13.4656 | 14.0353 |  |  |  | 16.5827 | 15.9169 | 15.021 | 10.3953 | 9.9498 | 10.521 | 17.1288 | 16.2846 | 15.1022 | 16.8484 | 16.1365 | 15.1271 | 10.7484 | 11.8613 |  | 12.0225 | 10.7444 | 10.3894 | 9.2828 |  | 6.483 | 6.5247 | 6.0085 | 6.139 | 6.214 | 6.5332 | 6.93 | 4.8153 | 6.5227 | 4.6626 | 6.7392 | 8.0356 | 42.6866 | 47.7114 | 43.4914 | 15.0834 |  |  | -0.047749 | -0.16222 | -0.15914 | 0.18662 | -0.026776 | -0.37239 | 0.24238 | 0.10235 | -0.62154 | -0.1699 | -0.35181 | 8.8697 | 8.8708 | 2.0084 | 15.6984 | 16.6416 | 17.2063 | 17.5389 | 17.5139 | 16.4894 | 14.8507 | 16.8328 | 17.1765 | 17.4762 | 17.524 | 17.2577 | 16.467 | 14.7042 | 6.0295 | 8.2176 | 5.6662 | 5.6968 | 5.7113 | 6.6283 | 7.6662 | 15.746 | 15.4322 | 15.3164 | 14.2572 | 14.1488 | 14.1007 |  |  |  | 10.631 | 9.5441 | 9.2251 | 9.3545 | -0.29858 | -0.32236 | 12.6785 |  |  | 10.5567 |  |  | 16.869 | 16.057 | 15.0362 | 16.3744 | 15.6554 | 14.7643 | 10.4231 | 10.8396 | 11.2089 | 11.247 | 9.4797 |  | 10.4769 | 9.0485 | 9.8583 | 9.301 | 10.9509 | 11.8265 |  | 12.1905 |  |  | 11.6656 | 12.4016 | 12.4854 | [6 empty] | 12.6167 |  |  | 11.4216 |  |  | 9.2263 | 10.1506 | 11.7677 | 7.5959 | 9.1262 | 12.4013 | 8.0142 | 9.5859 | 12.2113 | 9.184 | 10.4441 | 7.7131 | 10.3176 | 8.3974 | 10.3968 | 8.0295 | 9.6064 | 13.0071 | 10.4512 | 10.1579 | 11.5412 | 8.2334 | 9.6878 | 12.61 | 8.1723 | 10.4635 | 9.768 | 10.012 | 8.5103 | 10.5538 | -0.055866 | 20.9532 | 0.032385 | 0.047436 | -37.853 | 3.1201 | 9.19 | 0.24 | -0.25648 | -0.4694 | -0.46493 | 0.50347 | -0.19071 | -0.71121 | 0.57378 | 0.39462 | 0.38622 | 0.41521 | 0.41394 | 0.57482 | 0.40904 | 0.40318
42810.4382 | -161 | 18.4543 | 18.58 | 18.572 | 18.5826 | 17.9211 | 16.5711 | 14.6369 | 16.6932 | 17.1865 | 17.2829 | 17.2876 | 16.8303 | 15.8592 | 14.4624 | 14.8693 | 14.8993 | 15.4723 | 13.3405 | 13.4509 | 14.025 |  |  |  | 16.5781 | 15.9124 | 15.0227 | 10.3979 | 9.9496 | 10.5342 | 17.1336 | 16.2868 | 15.1002 | 16.8526 | 16.1426 | 15.1326 | 10.7628 | 11.8852 |  | 12.0282 | 10.7489 | 10.4063 | 9.3436 |  | 6.4775 | 6.5289 | 6.0149 | 6.1416 | 6.2016 | 6.5031 | 6.8986 | 4.8591 | 6.5314 | 4.5522 | 6.7426 | 8.0348 | 42.7063 | 47.7114 | 43.515 | 15.0891 |  |  | 0.11127 | -0.17011 | -0.04612 | 0.19779 | -0.060292 | -0.21008 | 0.38234 | 0.059632 | -0.61764 | -0.74832 | -0.24133 | 8.8687 | 8.8698 | 2.0082 | 15.69 | 16.6401 | 17.1956 | 17.5377 | 17.5099 | 16.488 | 14.8383 | 16.8296 | 17.169 | 17.4655 | 17.5199 | 17.2582 | 16.4638 | 14.6927 | 5.9658 | 8.2383 | 5.7346 | 5.7035 | 5.6912 | 6.6304 | 7.6659 | 15.7502 | 15.4363 | 15.3108 | 14.2647 | 14.1454 | 14.1032 |  |  |  | 10.6367 | 9.5369 | 9.2293 | 9.3453 | -0.30588 | -0.2834 | 12.684 |  |  | 10.5688 |  |  | 16.8669 | 16.0629 | 15.0291 | 16.3657 | 15.6585 | 14.7648 | 10.4268 | 10.8438 | 11.2026 | 11.2542 | 9.4884 |  | 10.4843 | 9.0702 | 9.858 | 9.2774 | 10.9581 | 11.7963 |  | 12.1924 |  |  | 11.6762 | 12.4095 | 12.4815 | [6 empty] | 12.6139 |  |  | 11.4229 |  |  | 9.2276 | 10.158 | 11.7652 | 7.6004 | 9.1276 | 12.4046 | 8.0284 | 9.5991 | 12.2151 | 9.1872 | 10.4489 | 7.725 | 10.3081 | 8.4037 | 10.396 | 8.0408 | 9.614 | 13.0127 | 10.4564 | 10.1559 | 11.5567 | 8.2251 | 9.6925 | 12.6112 | 8.1877 | 10.47 | 9.7727 | 10.0232 | 8.5077 | 10.5773 | -0.21649 | 20.9582 | 0.033344 | 0.048609 | -37.8464 | 3.1201 | -13.07 | 0.29 | 0.39154 | -0.48068 | -0.25029 | 0.51833 | -0.28616 | -0.53416 | 0.72062 | 0.39462 | 0.38561 | 0.4161 | 0.42126 | 0.56718 | 0.40783 | 0.40362
42810.4382 | -160 | 18.4547 | 18.573 | 18.5696 | 18.5703 | 17.9101 | 16.5606 | 14.6296 | 16.6937 | 17.1763 | 17.266 | 17.2849 | 16.8195 | 15.8514 | 14.4611 | 14.8762 | 14.9093 | 15.4737 | 13.3369 | 13.4626 | 14.0279 |  |  |  | 16.5831 | 15.9155 | 15.0189 | 10.4051 | 9.9532 | 10.565 | 17.1319 | 16.2828 | 15.0992 | 16.8521 | 16.1416 | 15.1353 | 10.7569 | 11.9121 |  | 12.0317 | 10.7393 | 10.4094 | 9.3408 |  | 6.4849 | 6.5222 | 6.0132 | 6.1273 | 6.1839 | 6.4822 | 6.8578 | 4.8213 | 6.5222 | 4.4869 | 6.7348 | 8.0335 | 42.7309 | 47.695 | 43.5433 | 15.0991 |  |  | 0.004819 | -0.090593 | -0.038892 | 0.13668 | 0.094788 | -0.4335 | 0.35212 | 0.007064 | -0.84007 | -0.62055 | -0.37744 | 8.8701 | 8.8714 | 2.0085 | 15.694 | 16.638 | 17.1951 | 17.5455 | 17.5106 | 16.4856 | 14.8407 | 16.8298 | 17.1659 | 17.4671 | 17.5197 | 17.2585 | 16.4647 | 14.6978 | 5.9342 | 8.2061 | 5.7989 | 5.6775 | 5.687 | 6.6265 | 7.6641 | 15.7516 | 15.4296 | 15.3193 | 14.2644 | 14.1528 | 14.0993 |  |  |  | 10.639 | 9.5353 | 9.2346 | 9.3465 | -0.12637 | -0.39124 | 12.6883 |  |  | 10.5572 |  |  | 16.8654 | 16.0546 | 15.0275 | 16.3633 | 15.6524 | 14.7587 | 10.4517 | 10.8382 | 11.1965 | 11.2522 | 9.4951 |  | 10.4831 | 9.098 | 9.856 | 9.2639 | 10.9526 | 11.7638 |  | 12.1859 |  |  | 11.6827 | 12.4162 | 12.458 | [6 empty] | 12.6194 |  |  | 11.4058 |  |  | 9.2402 | 10.1651 | 11.7731 | 7.6183 | 9.1416 | 12.402 | 8.0347 | 9.6097 | 12.2223 | 9.2015 | 10.4536 | 7.7347 | 10.3283 | 8.4048 | 10.4057 | 8.0453 | 9.6156 | 12.9954 | 10.4647 | 10.156 | 11.5577 | 8.222 | 9.6911 | 12.6074 | 8.1958 | 10.4682 | 9.7704 | 10.0218 | 8.4981 | 10.5925 | -0.0036716 | 20.9551 | 0.033619 | 0.048913 | -37.8637 | 3.1201 | -9.23 | 0.34 | 0.081487 | -0.35078 | -0.22984 | 0.43087 | 0.35879 | -0.76728 | 0.69152 | 0.3944 | 0.38478 | 0.41629 | 0.42433 | 0.55982 | 0.40771 | 0.40366
42810.4382 | -159 | 18.4524 | 18.5682 | 18.5684 | 18.5783 | 17.9215 | 16.5602 | 14.6264 | 16.6917 | 17.1755 | 17.2717 | 17.2787 | 16.814 | 15.8521 | 14.4616 | 14.8773 | 14.9134 | 15.4752 | 13.3331 | 13.4615 | 14.0311 |  |  |  | 16.5814 | 15.9179 | 15.0252 | 10.4233 | 9.965 | 10.5821 | 17.1268 | 16.2776 | 15.0882 | 16.843 | 16.1356 | 15.1258 | 10.7492 | 11.9455 |  | 12.0129 | 10.7351 | 10.4002 | 9.3575 |  | 6.4963 | 6.536 | 6.0308 | 6.1376 | 6.1728 | 6.4706 | 6.8453 | 4.7724 | 6.5306 | 4.4834 | 6.7446 | 8.035 | 42.7668 | 47.6863 | 43.5561 | 15.1126 |  |  | 0.053447 | -0.003853 | 0.1175 | -0.17808 | -0.19566 | -0.56229 | 0.50062 | -0.23147 | -0.40475 | 0.04976 | -0.475 | 8.8666 | 8.8681 | 2.0079 | 15.692 | 16.635 | 17.2035 | 17.5439 | 17.508 | 16.493 | 14.848 | 16.8364 | 17.1742 | 17.4734 | 17.5241 | 17.2604 | 16.4683 | 14.7021 | 5.9474 | 8.2042 | 5.9508 | 5.6458 | 5.6922 | 6.6271 | 7.6574 | 15.7419 | 15.4222 | 15.306 | 14.2589 | 14.144 | 14.0898 |  |  |  | 10.6321 | 9.5302 | 9.2296 | 9.3433 | 0.0036956 | -0.15938 | 12.6871 |  |  | 10.5593 |  |  | 16.8653 | 16.0553 | 15.037 | 16.3646 | 15.6531 | 14.763 | 10.4522 | 10.8333 | 11.2016 | 11.2566 | 9.4998 |  | 10.4844 | 9.0807 | 9.8646 | 9.2446 | 10.9505 | 11.7337 |  | 12.1826 |  |  | 11.6915 | 12.4294 | 12.4635 | [6 empty] | 12.6319 |  |  | 11.3995 |  |  | 9.2389 | 10.1545 | 11.7562 | 7.6277 | 9.1485 | 12.3953 | 8.0352 | 9.6108 | 12.2215 | 9.2018 | 10.4444 | 7.7313 | 10.3104 | 8.4035 | 10.3903 | 8.0487 | 9.6218 | 12.9859 | 10.4632 | 10.1494 | 11.549 | 8.2199 | 9.6843 | 12.6067 | 8.1887 | 10.4608 | 9.7723 | 10.0192 | 8.4888 | 10.5935 | 0.017322 | 20.9536 | 0.033636 | 0.048356 | -37.8186 | 3.1201 | 7.84 | 0.26 | 0.27138 | -0.072344 | 0.39951 | -0.49182 | -0.51546 | -0.87384 | 0.82453 | 0.39431 | 0.38554 | 0.41676 | 0.42292 | 0.54218 | 0.40699 | 0.40353
42810.4382 | -158 | 18.4445 | 18.5685 | 18.5648 | 18.5723 | 17.9209 | 16.5584 | 14.6277 | 16.6843 | 17.1805 | 17.2762 | 17.2811 | 16.8123 | 15.8526 | 14.4576 | 14.8748 | 14.8926 | 15.4757 | 13.3354 | 13.4555 | 14.0237 |  |  |  | 16.5852 | 15.9093 | 15.0118 | 10.4326 | 9.9648 | 10.5892 | 17.1282 | 16.283 | 15.087 | 16.8475 | 16.1375 | 15.1274 | 10.7523 | 12.0042 |  | 12.0251 | 10.7464 | 10.4015 | 9.3893 |  | 6.4959 | 6.5432 | 6.0251 | 6.1346 | 6.1691 | 6.4431 | 6.8327 | 4.7688 | 6.5251 | 4.489 | 6.7372 | 8.0321 | 42.8198 | 47.6721 | 43.577 | 15.14 |  |  | 0.054103 | -0.089937 | 0.11553 | 0.036142 | -0.10366 | -0.27908 | 0.47631 | 0.002464 | -0.57464 | -0.13675 | -0.11158 | 8.8721 | 8.8733 | 2.0082 | 15.6833 | 16.6271 | 17.1936 | 17.5372 | 17.5037 | 16.4834 | 14.843 | 16.8304 | 17.1725 | 17.4708 | 17.5105 | 17.2569 | 16.4602 | 14.6961 | 6.0004 | 8.2354 | 6.1917 | 5.6681 | 5.6916 | 6.632 | 7.6601 | 15.7351 | 15.4198 | 15.3044 | 14.2491 | 14.1401 | 14.0885 |  |  |  | 10.6291 | 9.5253 | 9.2242 | 9.3441 | 0.088585 | 0.14757 | 12.6922 |  |  | 10.5598 |  |  | 16.8653 | 16.0648 | 15.0403 | 16.3762 | 15.6632 | 14.7643 | 10.4766 | 10.8453 | 11.2135 | 11.2602 | 9.5099 |  | 10.4804 | 9.0501 | 9.8648 | 9.2413 | 10.937 | 11.7114 |  | 12.1832 |  |  | 11.6991 | 12.4367 | 12.4587 | [6 empty] | 12.619 |  |  | 11.3987 |  |  | 9.2433 | 10.1548 | 11.7365 | 7.6292 | 9.1523 | 12.3778 | 8.0372 | 9.6106 | 12.218 | 9.1969 | 10.4486 | 7.7346 | 10.32 | 8.4017 | 10.3844 | 8.0593 | 9.6286 | 12.9908 | 10.4611 | 10.1501 | 11.5599 | 8.2212 | 9.6813 | 12.6136 | 8.1763 | 10.4761 | 9.7771 | 10.034 | 8.4941 | 10.6057 | -0.011953 | 20.9564 | 0.033946 | 0.048631 | -37.8893 | 3.12 | 26.54 | 0.34 | 0.27305 | -0.34952 | 0.39615 | 0.22157 | -0.37518 | -0.61559 | 0.80422 | 0.3939 | 0.38639 | 0.41641 | 0.4176 | 0.51572 | 0.40621 | 0.4034
42810.4382 | -157 | 18.4412 | 18.5706 | 18.5635 | 18.5708 | 17.919 | 16.5619 | 14.6277 | 16.6887 | 17.1763 | 17.2729 | 17.2811 | 16.8158 | 15.8499 | 14.4573 | 14.8697 | 14.8986 | 15.473 | 13.332 | 13.4658 | 14.04 |  |  |  | 16.5779 | 15.9233 | 15.0247 | 10.4448 | 9.982 | 10.6119 | 17.1238 | 16.2786 | 15.0909 | 16.8439 | 16.133 | 15.1313 | 10.7561 | 12.049 |  | 12.0215 | 10.7384 | 10.4011 | 9.4246 |  | 6.495 | 6.5463 | 6.0382 | 6.1438 | 6.1778 | 6.4349 | 6.8148 | 4.7582 | 6.5166 | 4.5309 | 6.7323 | 8.0393 | 42.8538 | 47.6743 | 43.5899 | 15.1614 |  |  | 0.015331 | -0.005825 | 0.01828 | 0.08017 | -0.10103 | -0.13451 | 0.48945 | -0.2341 | 0.14519 | -0.39103 | -0.2916 | 8.8698 | 8.8709 | 2.0082 | 15.6831 | 16.6301 | 17.1915 | 17.5316 | 17.4982 | 16.4845 | 14.8334 | 16.8299 | 17.1676 | 17.4624 | 17.5123 | 17.2615 | 16.4631 | 14.7015 | 6.047 | 8.2461 | 6.3339 | 5.6559 | 5.6893 | 6.6317 | 7.663 | 15.7299 | 15.4141 | 15.2958 | 14.2434 | 14.1412 | 14.0805 |  |  |  | 10.6314 | 9.5254 | 9.227 | 9.3485 | -0.05364 | 0.24243 | 12.6954 |  |  | 10.5544 |  |  | 16.8637 | 16.0622 | 15.039 | 16.3808 | 15.662 | 14.7695 | 10.4963 | 10.8476 | 11.2203 | 11.2525 | 9.5327 |  | 10.4832 | 9.0743 | 9.8646 | 9.2386 | 10.9453 | 11.7007 |  | 12.1922 |  |  | 11.7026 | 12.4156 | 12.439 | [6 empty] | 12.5862 |  |  | 11.3885 |  |  | 9.2447 | 10.1627 | 11.7409 | 7.6518 | 9.1414 | 12.3729 | 8.056 | 9.6283 | 12.2245 | 9.1974 | 10.4532 | 7.7518 | 10.3261 | 8.4098 | 10.3928 | 8.0345 | 9.6316 | 12.9827 | 10.4651 | 10.161 | 11.5618 | 8.2224 | 9.6848 | 12.6112 | 8.1541 | 10.479 | 9.7836 | 10.0424 | 8.4801 | 10.6155 | -0.026591 | 20.9525 | 0.032936 | 0.048428 | -37.9835 | 3.12 | 4.33 | 0.28 | 0.14535 | -0.088953 | 0.15758 | 0.33 | -0.37038 | -0.42737 | 0.81523 | 0.39336 | 0.38572 | 0.41676 | 0.4124 | 0.50025 | 0.40536 | 0.40336
42810.4382 | -156 | 18.4359 | 18.5698 | 18.5712 | 18.5746 | 17.9169 | 16.5555 | 14.6342 | 16.6916 | 17.1781 | 17.2732 | 17.2745 | 16.8173 | 15.8465 | 14.4597 | 14.878 | 14.8978 | 15.4659 | 13.3385 | 13.4599 | 14.0225 |  |  |  | 16.5885 | 15.9158 | 15.0205 | 10.4459 | 9.9874 | 10.6072 | 17.1205 | 16.2748 | 15.0911 | 16.8365 | 16.1381 | 15.1312 | 10.7567 | 12.0929 |  | 12.0164 | 10.7325 | 10.4034 | 9.4455 |  | 6.5053 | 6.5425 | 6.0407 | 6.155 | 6.1759 | 6.4278 | 6.7991 | 4.7914 | 6.5187 | 4.5776 | 6.7309 | 8.031 | 42.8786 | 47.6836 | 43.591 | 15.1747 |  |  | 0.18158 | 0.005343 | -0.094088 | 0.17413 | -0.14374 | -0.035944 | 0.46448 | -0.31426 | -0.70989 | -0.28949 | -0.26358 | 8.8696 | 8.8706 | 2.0081 | 15.6914 | 16.6347 | 17.2011 | 17.5404 | 17.5103 | 16.4913 | 14.8564 | 16.8307 | 17.1763 | 17.4799 | 17.53 | 17.2622 | 16.475 | 14.7083 | 6.0797 | 8.2442 | 6.3972 | 5.7238 | 5.688 | 6.6337 | 7.6592 | 15.7347 | 15.4148 | 15.2954 | 14.2486 | 14.1417 | 14.0871 |  |  |  | 10.6317 | 9.5285 | 9.2285 | 9.3436 | 0.0051138 | -0.090499 | 12.6931 |  |  | 10.559 |  |  | 16.8648 | 16.0523 | 15.0333 | 16.3692 | 15.6579 | 14.7586 | 10.4956 | 10.8432 | 11.2074 | 11.2323 | 9.5375 |  | 10.4823 | 9.0728 | 9.8698 | 9.2415 | 10.9467 | 11.6996 |  | 12.1938 |  |  | 11.7226 | 12.4063 | 12.447 | [6 empty] | 12.5781 |  |  | 11.4108 |  |  | 9.2465 | 10.1664 | 11.7393 | 7.6597 | 9.1139 | 12.3884 | 8.0597 | 9.6316 | 12.2353 | 9.2013 | 10.4601 | 7.747 | 10.3255 | 8.4232 | 10.3858 | 8.0215 | 9.6434 | 12.9734 | 10.4583 | 10.1639 | 11.5695 | 8.2148 | 9.6709 | 12.6144 | 8.1442 | 10.4735 | 9.7795 | 10.0402 | 8.4515 | 10.6003 | -0.083023 | 20.9544 | 0.031765 | 0.049123 | -37.9403 | 3.12 | -1.59 | 0.24 | 0.50024 | 0.085192 | -0.3575 | 0.48635 | -0.44179 | -0.22092 | 0.79415 | 0.39319 | 0.38593 | 0.41672 | 0.40899 | 0.49278 | 0.40479 | 0.40351
42810.4382 | -155 | 18.4464 | 18.568 | 18.5609 | 18.573 | 17.9188 | 16.5567 | 14.6315 | 16.6937 | 17.1788 | 17.2704 | 17.2743 | 16.8181 | 15.844 | 14.4593 | 14.8662 | 14.8954 | 15.4653 | 13.3294 | 13.4555 | 14.0286 |  |  |  | 16.5766 | 15.9207 | 15.0101 | 10.4495 | 10.0038 | 10.6186 | 17.1184 | 16.2793 | 15.089 | 16.8399 | 16.1373 | 15.1336 | 10.7614 | 12.1364 |  | 12.0216 | 10.7361 | 10.4087 | 9.448 |  | 6.5143 | 6.5557 | 6.0538 | 6.1685 | 6.1811 | 6.4241 | 6.7772 | 4.9011 | 6.5214 | 4.6248 | 6.7366 | 8.0267 | 42.9086 | 47.6941 | 43.5946 | 15.1927 |  |  | 0.004163 | -0.14053 | 0.078076 | 0.01643 | -0.083948 | 0.23413 | 0.5164 | -0.35172 | -0.57522 | -0.20242 | -0.35638 | 8.8689 | 8.8699 | 2.0082 | 15.6845 | 16.6344 | 17.1987 | 17.5387 | 17.5036 | 16.4886 | 14.842 | 16.826 | 17.1794 | 17.4752 | 17.5221 | 17.2579 | 16.4746 | 14.7067 | 6.1273 | 8.2619 | 6.3287 | 5.8559 | 5.6789 | 6.6362 | 7.6672 | 15.7311 | 15.4207 | 15.3017 | 14.2582 | 14.1423 | 14.0864 |  |  |  | 10.6356 | 9.5285 | 9.2391 | 9.3322 | -0.028315 | -0.14696 | 12.6954 |  |  | 10.5513 |  |  | 16.8651 | 16.0534 | 15.0293 | 16.3683 | 15.651 | 14.7639 | 10.5136 | 10.8427 | 11.2029 | 11.224 | 9.5702 |  | 10.4807 | 9.0853 | 9.8682 | 9.2517 | 10.9572 | 11.7101 |  | 12.1962 |  |  | 11.7241 | 12.3949 | 12.4432 | [6 empty] | 12.5703 |  |  | 11.4006 |  |  | 9.2553 | 10.1669 | 11.7408 | 7.6688 | 9.0972 | 12.3863 | 8.0822 | 9.643 | 12.2308 | 9.2102 | 10.4697 | 7.7394 | 10.3233 | 8.4204 | 10.3898 | 8.0323 | 9.6609 | 12.9964 | 10.481 | 10.1793 | 11.5837 | 8.2222 | 9.6844 | 12.6232 | 8.1484 | 10.4822 | 9.7952 | 10.0595 | 8.4554 | 10.6252 | -0.16815 | 20.9562 | 0.033258 | 0.049362 | -37.9431 | 3.12 | 5.6 | 0.34 | 0.075745 | -0.43692 | 0.32567 | 0.1494 | -0.33761 | 0.56383 | 0.83735 | 0.39223 | 0.38553 | 0.41679 | 0.404 | 0.50132 | 0.40488 | 0.40395
42810.4383 | -154 | 18.4384 | 18.5638 | 18.5589 | 18.5691 | 17.9183 | 16.5607 | 14.6413 | 16.6886 | 17.1778 | 17.2668 | 17.2826 | 16.8166 | 15.8426 | 14.4565 | 14.8673 | 14.891 | 15.4672 | 13.3298 | 13.4579 | 14.0286 |  |  |  | 16.5744 | 15.9197 | 15.0171 | 10.4671 | 10.0115 | 10.6475 | 17.1211 | 16.2774 | 15.0869 | 16.8428 | 16.1386 | 15.1311 | 10.7605 | 12.1636 |  | 12.0213 | 10.7274 | 10.422 | 9.4121 |  | 6.5188 | 6.5517 | 6.0569 | 6.1711 | 6.1731 | 6.4223 | 6.7535 | 4.908 | 6.5141 | 4.6748 | 6.7324 | 8.027 | 42.9405 | 47.7013 | 43.6019 | 15.2068 |  |  | 0.050159 | -0.18916 | 0.18716 | 0.22276 | -0.050432 | -0.058284 | 0.64322 | -0.18284 | -0.43686 | -0.6088 | -0.45473 | 8.8698 | 8.8708 | 2.0079 | 15.6815 | 16.6341 | 17.2037 | 17.5363 | 17.5048 | 16.488 | 14.8412 | 16.8363 | 17.176 | 17.4761 | 17.5292 | 17.2613 | 16.4801 | 14.7081 | 6.1364 | 8.2828 | 6.195 | 5.9375 | 5.6743 | 6.6314 | 7.6669 | 15.7265 | 15.4157 | 15.3048 | 14.2558 | 14.1388 | 14.0892 |  |  |  | 10.6347 | 9.5326 | 9.2449 | 9.3082 | -0.11239 | -0.16371 | 12.7037 |  |  | 10.5574 |  |  | 16.8683 | 16.0633 | 15.0358 | 16.37 | 15.6582 | 14.7642 | 10.5356 | 10.8646 | 11.218 | 11.2207 | 9.5944 |  | 10.4748 | 9.094 | 9.8654 | 9.2585 | 10.9436 | 11.711 |  | 12.1855 |  |  | 11.7269 | 12.4037 | 12.4448 | [6 empty] | 12.5735 |  |  | 11.3945 |  |  | 9.2665 | 10.1764 | 11.7388 | 7.6817 | 9.0898 | 12.3952 | 8.0846 | 9.6446 | 12.2424 | 9.2092 | 10.4711 | 7.7345 | 10.3286 | 8.4198 | 10.3885 | 8.0243 | 9.6607 | 12.9789 | 10.4727 | 10.1766 | 11.5912 | 8.2257 | 9.678 | 12.6081 | 8.1411 | 10.4819 | 9.7871 | 10.0622 | 8.4371 | 10.623 | 0.0026842 | 20.9538 | 0.03409 | 0.050382 | -37.8368 | 3.12 | 1 | 0.31 | 0.26293 | -0.50691 | 0.50422 | 0.55009 | -0.26168 | -0.28131 | 0.93453 | 0.39137 | 0.38519 | 0.41615 | 0.40243 | 0.51614 | 0.40584 | 0.40458
42810.4383 | -153 | 18.4393 | 18.5616 | 18.558 | 18.5648 | 17.9089 | 16.5559 | 14.6263 | 16.6837 | 17.1739 | 17.2713 | 17.2784 | 16.8086 | 15.8418 | 14.4519 | 14.863 | 14.8911 | 15.4644 | 13.3284 | 13.4553 | 14.0235 |  |  |  | 16.5708 | 15.9168 | 15.0153 | 10.4663 | 10.0067 | 10.6739 | 17.1149 | 16.2734 | 15.0876 | 16.8479 | 16.1249 | 15.118 | 10.7551 | 12.1663 |  | 12.0163 | 10.7162 | 10.4228 | 9.3598 |  | 6.5188 | 6.5642 | 6.0671 | 6.1881 | 6.184 | 6.4282 | 6.7945 | 4.834 | 6.5199 | 4.7899 | 6.734 | 8.0313 | 42.9595 | 47.7075 | 43.614 | 15.2329 |  |  | 0.11522 | -0.061681 | 0.19833 | 0.12025 | -0.05372 | -0.17985 | 0.52494 | -0.18744 | -0.49777 | -0.38411 | -0.41797 | 8.8682 | 8.8697 | 2.0083 | 15.6816 | 16.6377 | 17.1969 | 17.5385 | 17.5113 | 16.49 | 14.8468 | 16.8358 | 17.1726 | 17.4738 | 17.5243 | 17.2632 | 16.4768 | 14.7104 | 6.0772 | 8.279 | 6.1238 | 5.9114 | 5.7791 | 6.6304 | 7.6656 | 15.7337 | 15.4185 | 15.3074 | 14.253 | 14.1442 | 14.0833 |  |  |  | 10.6353 | 9.5316 | 9.245 | 9.3067 | -0.12779 | -0.12965 | 12.7004 |  |  | 10.5514 |  |  | 16.8609 | 16.0606 | 15.0283 | 16.3737 | 15.6601 | 14.7579 | 10.5387 | 10.8724 | 11.2156 | 11.2104 | 9.617 |  | 10.4787 | 9.0773 | 9.8598 | 9.2611 | 10.9506 | 11.7285 |  | 12.1844 |  |  | 11.7166 | 12.3994 | 12.4482 | [6 empty] | 12.5781 |  |  | 11.3969 |  |  | 9.2632 | 10.1736 | 11.7307 | 7.6803 | 9.0863 | 12.3941 | 8.0877 | 9.6462 | 12.2363 | 9.2105 | 10.4657 | 7.7216 | 10.3314 | 8.4158 | 10.3868 | 8.0225 | 9.6591 | 12.9768 | 10.481 | 10.1749 | 11.5982 | 8.2145 | 9.6746 | 12.6099 | 8.1417 | 10.4794 | 9.7737 | 10.072 | 8.4232 | 10.6331 | -0.19743 | 20.9545 | 0.034187 | 0.050476 | -37.8982 | 3.12 | 6.98 | 0.27 | 0.39852 | -0.28947 | 0.51906 | 0.40418 | -0.27008 | -0.49417 | 0.84425 | 0.39087 | 0.38547 | 0.41631 | 0.40888 | 0.5239 | 0.40712 | 0.40465
42810.4383 | -152 | 18.4303 | 18.5603 | 18.5545 | 18.5603 | 17.9125 | 16.5579 | 14.6285 | 16.6853 | 17.1738 | 17.2733 | 17.2681 | 16.8093 | 15.84 | 14.4451 | 14.862 | 14.9006 | 15.4637 | 13.3355 | 13.4535 | 14.0254 |  |  |  | 16.576 | 15.9177 | 15.0137 | 10.4779 | 9.995 | 10.6917 | 17.1121 | 16.2745 | 15.0866 | 16.8373 | 16.1203 | 15.1165 | 10.7523 | 12.1384 |  | 12.0096 | 10.7057 | 10.4301 | 9.298 |  | 6.5129 | 6.5589 | 6.0684 | 6.1801 | 6.1903 | 6.4374 | 6.8414 | 4.8077 | 6.5104 | 4.8047 | 6.7287 | 8.0287 | 42.9622 | 47.6975 | 43.5978 | 15.2405 |  |  | 0.089587 | 0.094055 | 0.10305 | -0.11302 | 0.031704 | -0.051716 | 0.43886 | -0.13619 | -0.48551 | -0.27081 | -0.40367 | 8.8702 | 8.8715 | 2.0081 | 15.6916 | 16.6409 | 17.2091 | 17.551 | 17.5169 | 16.4973 | 14.8562 | 16.8423 | 17.1847 | 17.4824 | 17.5286 | 17.2675 | 16.4862 | 14.7114 | 6.0209 | 8.2515 | 6.1762 | 5.8803 | 5.8241 | 6.6198 | 7.6598 | 15.7361 | 15.4189 | 15.302 | 14.2527 | 14.1425 | 14.0862 |  |  |  | 10.6374 | 9.535 | 9.2468 | 9.3007 | 0.035099 | -0.12343 | 12.7012 |  |  | 10.5492 |  |  | 16.8615 | 16.0603 | 15.0288 | 16.3719 | 15.6584 | 14.7603 | 10.5544 | 10.8816 | 11.2137 | 11.2044 | 9.6214 |  | 10.4709 | 9.0418 | 9.8632 | 9.2542 | 10.9412 | 11.7496 |  | 12.1786 |  |  | 11.7239 | 12.4021 | 12.4599 | [6 empty] | 12.5637 |  |  | 11.4056 |  |  | 9.2733 | 10.1676 | 11.7204 | 7.6862 | 9.0961 | 12.3872 | 8.083 | 9.6471 | 12.2344 | 9.2201 | 10.4644 | 7.7333 | 10.3389 | 8.4166 | 10.3907 | 8.0279 | 9.6505 | 12.9736 | 10.4832 | 10.1801 | 11.6035 | 8.2149 | 9.6676 | 12.6042 | 8.1447 | 10.4786 | 9.7716 | 10.0767 | 8.4244 | 10.6356 | 0.050834 | 20.9548 | 0.034423 | 0.051026 | -37.8064 | 3.12 | 4.55 | 0.28 | 0.35142 | 0.35745 | 0.37414 | -0.39183 | 0.20748 | -0.265 | 0.77195 | 0.39049 | 0.38657 | 0.41619 | 0.41392 | 0.5174 | 0.40875 | 0.40488
42810.4383 | -151 | 18.4425 | 18.5644 | 18.5629 | 18.5756 | 17.9196 | 16.5614 | 14.6331 | 16.6939 | 17.1768 | 17.2682 | 17.2771 | 16.8175 | 15.8479 | 14.4576 | 14.8541 | 14.8917 | 15.4545 | 13.3283 | 13.4539 | 14.0221 |  |  |  | 16.5729 | 15.9115 | 15.0125 | 10.4793 | 9.9856 | 10.6945 | 17.117 | 16.2768 | 15.0814 | 16.8313 | 16.1261 | 15.1202 | 10.7515 | 12.1161 |  | 12.0138 | 10.7025 | 10.4356 | 9.2488 |  | 6.5254 | 6.559 | 6.0726 | 6.2006 | 6.2057 | 6.4468 | 6.9029 | 4.8148 | 6.5168 | 4.7731 | 6.7261 | 8.0284 | 42.9767 | 47.7023 | 43.5872 | 15.2518 |  |  | 0.079731 | 0.022431 | 0.083332 | -0.09331 | -0.047148 | -0.33624 | 0.64453 | 0.17594 | 0.77024 | -0.52929 | -0.34147 | 8.8688 | 8.8699 | 2.0081 | 15.6855 | 16.6326 | 17.2032 | 17.543 | 17.5117 | 16.4906 | 14.8503 | 16.8361 | 17.1775 | 17.4729 | 17.5248 | 17.2672 | 16.4793 | 14.707 | 6.0493 | 8.2426 | 6.2064 | 5.8997 | 5.7732 | 6.6238 | 7.6615 | 15.7336 | 15.4262 | 15.3018 | 14.255 | 14.1423 | 14.0936 |  |  |  | 10.6396 | 9.5437 | 9.2579 | 9.2916 | 0.097297 | -0.092946 | 12.6975 |  |  | 10.549 |  |  | 16.8657 | 16.0564 | 15.0325 | 16.3662 | 15.6525 | 14.7632 | 10.5716 | 10.8932 | 11.2126 | 11.203 | 9.6366 |  | 10.4786 | 9.0246 | 9.8705 | 9.2641 | 10.9394 | 11.7984 |  | 12.1809 |  |  | 11.7277 | 12.4191 | 12.4738 | [6 empty] | 12.568 |  |  | 11.4165 |  |  | 9.2864 | 10.1784 | 11.7047 | 7.6919 | 9.1027 | 12.3963 | 8.086 | 9.6399 | 12.2301 | 9.2281 | 10.4622 | 7.7433 | 10.3511 | 8.4253 | 10.389 | 8.0484 | 9.6352 | 12.9692 | 10.4887 | 10.1873 | 11.6057 | 8.215 | 9.6656 | 12.6054 | 8.1564 | 10.4883 | 9.7596 | 10.088 | 8.4174 | 10.6385 | -0.075511 | 20.954 | 0.032764 | 0.04947 | -37.796 | 3.1199 | 14.61 | 0.34 | 0.33153 | 0.17456 | 0.33645 | -0.35603 | -0.25303 | -0.67571 | 0.93552 | 0.39032 | 0.38729 | 0.41586 | 0.41122 | 0.51424 | 0.41009 | 0.40521
42810.4383 | -150 | 18.432 | 18.5591 | 18.5619 | 18.5683 | 17.9055 | 16.5569 | 14.6295 | 16.6898 | 17.1741 | 17.2716 | 17.2739 | 16.8122 | 15.8424 | 14.4514 | 14.8598 | 14.8945 | 15.4635 | 13.3297 | 13.4574 | 14.0227 |  |  |  | 16.5789 | 15.913 | 15.0189 | 10.4925 | 10.0021 | 10.7139 | 17.1169 | 16.2732 | 15.0816 | 16.8413 | 16.13 | 15.1183 | 10.7603 | 12.0771 |  | 12.0246 | 10.7053 | 10.4562 | 9.2431 |  | 6.5291 | 6.5623 | 6.082 | 6.2126 | 6.2157 | 6.4515 | 6.9035 | 4.7893 | 6.5087 | 4.7303 | 6.7351 | 8.0276 | 42.9853 | 47.7127 | 43.5799 | 15.2652 |  |  | 0.035047 | 0.067115 | 0.16087 | -0.60915 | 0.002792 | -0.20876 | 0.70499 | 0.18054 | -0.74958 | -0.26452 | -0.37684 | 8.8697 | 8.871 | 2.008 | 15.6891 | 16.6326 | 17.1968 | 17.5419 | 17.5109 | 16.4965 | 14.8564 | 16.8411 | 17.1824 | 17.481 | 17.5277 | 17.2778 | 16.4758 | 14.7152 | 6.1146 | 8.244 | 6.211 | 5.9031 | 5.7834 | 6.6196 | 7.6608 | 15.7279 | 15.4196 | 15.3014 | 14.2545 | 14.1453 | 14.0951 |  |  |  | 10.6424 | 9.5414 | 9.2512 | 9.2885 | 0.031047 | -0.16371 | 12.6915 |  |  | 10.5466 |  |  | 16.8514 | 16.0477 | 15.0247 | 16.3614 | 15.6414 | 14.7585 | 10.5827 | 10.8863 | 11.2064 | 11.1932 | 9.6442 |  | 10.4753 | 8.995 | 9.8745 | 9.2725 | 10.952 | 11.8596 |  | 12.1794 |  |  | 11.7187 | 12.4268 | 12.4748 | [6 empty] | 12.5622 |  |  | 11.427 |  |  | 9.284 | 10.1842 | 11.6942 | 7.6896 | 9.1145 | 12.4009 | 8.0891 | 9.6364 | 12.2282 | 9.2329 | 10.4559 | 7.7485 | 10.3548 | 8.4309 | 10.3809 | 8.0532 | 9.6225 | 12.9735 | 10.4894 | 10.184 | 11.6095 | 8.212 | 9.6596 | 12.6095 | 8.1621 | 10.498 | 9.7529 | 10.0942 | 8.4159 | 10.6441 | -0.090727 | 20.9545 | 0.031473 | 0.04837 | -37.8493 | 3.1199 | 14.63 | 0.21 | 0.21981 | 0.30195 | 0.46748 | -0.90967 | 0.061574 | -0.53243 | 0.97843 | 0.39 | 0.38824 | 0.41604 | 0.40347 | 0.51365 | 0.41053 | 0.40539
42810.4383 | -149 | 18.4389 | 18.5616 | 18.5671 | 18.5671 | 17.9145 | 16.5612 | 14.6291 | 16.6899 | 17.1798 | 17.2745 | 17.2785 | 16.8154 | 15.8427 | 14.454 | 14.8575 | 14.8971 | 15.4673 | 13.3343 | 13.4501 | 14.0257 |  |  |  | 16.5773 | 15.9142 | 15.0227 | 10.5063 | 10.018 | 10.7364 | 17.1097 | 16.2666 | 15.079 | 16.8335 | 16.1216 | 15.1109 | 10.7588 | 12.0433 |  | 12.0167 | 10.7087 | 10.467 | 9.2261 |  | 6.5192 | 6.5513 | 6.0769 | 6.2121 | 6.2171 | 6.4462 | 6.9093 | 4.7289 | 6.5091 | 4.6884 | 6.7241 | 8.0274 | 42.9788 | 47.7113 | 43.562 | 15.2654 |  |  | 0.006791 | 0.023087 | -0.057288 | -0.26679 | 0.020536 | 0.012684 | 0.51508 | 0.4079 | -0.3382 | -0.98749 | -0.27531 | 8.869 | 8.8701 | 2.0081 | 15.6818 | 16.6364 | 17.2056 | 17.5391 | 17.5023 | 16.4943 | 14.8482 | 16.8415 | 17.1843 | 17.4879 | 17.5336 | 17.268 | 16.4831 | 14.7159 | 6.2267 | 8.2718 | 6.2286 | 5.8846 | 5.8329 | 6.6307 | 7.6635 | 15.7216 | 15.4121 | 15.2915 | 14.2425 | 14.1359 | 14.0845 |  |  |  | 10.6317 | 9.5425 | 9.244 | 9.2992 | 0.037125 | -0.1048 | 12.6916 |  |  | 10.548 |  |  | 16.8507 | 16.0568 | 15.0296 | 16.3656 | 15.6541 | 14.757 | 10.5939 | 10.8909 | 11.2108 | 11.1976 | 9.6361 |  | 10.4874 | 8.9535 | 9.8762 | 9.2881 | 10.9457 | 11.924 |  | 12.183 |  |  | 11.718 | 12.4249 | 12.4836 | [6 empty] | 12.565 |  |  | 11.4252 |  |  | 9.2821 | 10.1792 | 11.6785 | 7.6894 | 9.1211 | 12.403 | 8.0901 | 9.6378 | 12.2271 | 9.2312 | 10.4465 | 7.7381 | 10.3594 | 8.418 | 10.3731 | 8.0577 | 9.6092 | 12.9801 | 10.4816 | 10.1881 | 11.6094 | 8.2136 | 9.6602 | 12.6047 | 8.1634 | 10.4987 | 9.749 | 10.0925 | 8.4222 | 10.6536 | -0.19743 | 20.9546 | 0.033263 | 0.048298 | -37.8759 | 3.1199 | -5.05 | 0.28 | 0.096762 | 0.17709 | -0.27896 | -0.602 | 0.16699 | 0.13124 | 0.83632 | 0.39062 | 0.38945 | 0.4154 | 0.39231 | 0.51202 | 0.41096 | 0.40474
42810.4383 | -148 | 18.4301 | 18.5576 | 18.5533 | 18.5636 | 17.9072 | 16.5575 | 14.6253 | 16.6803 | 17.1728 | 17.2696 | 17.2711 | 16.8101 | 15.8394 | 14.4535 | 14.8581 | 14.8932 | 15.4657 | 13.33 | 13.4553 | 14.0237 |  |  |  | 16.574 | 15.9136 | 15.0188 | 10.516 | 10.0259 | 10.7515 | 17.1051 | 16.2599 | 15.078 | 16.8326 | 16.1271 | 15.1141 | 10.7607 | 12.0127 |  | 12.019 | 10.7185 | 10.4716 | 9.2109 |  | 6.5217 | 6.5532 | 6.0752 | 6.2108 | 6.2159 | 6.4502 | 6.942 | 4.7751 | 6.5106 | 4.6783 | 6.7268 | 8.0263 | 42.9903 | 47.7013 | 43.5586 | 15.2683 |  |  | 0.23087 | -0.20428 | 0.059676 | 0.20831 | 0.18021 | 0.16316 | 0.35606 | 0.11812 | -0.19828 | -0.96819 | -0.33035 | 8.8698 | 8.8707 | 2.008 | 15.6735 | 16.6262 | 17.198 | 17.5381 | 17.5019 | 16.4859 | 14.8393 | 16.8276 | 17.1651 | 17.4772 | 17.5293 | 17.261 | 16.4738 | 14.7037 | 6.3415 | 8.2862 | 6.3221 | 5.8509 | 5.7996 | 6.6247 | 7.6604 | 15.7263 | 15.4094 | 15.2856 | 14.2463 | 14.1325 | 14.0788 |  |  |  | 10.6315 | 9.5551 | 9.2472 | 9.3194 | 0.040569 | 0.13647 | 12.708 |  |  | 10.557 |  |  | 16.8663 | 16.0655 | 15.0356 | 16.3738 | 15.6636 | 14.7647 | 10.6094 | 10.8993 | 11.2223 | 11.2103 | 9.6255 |  | 10.482 | 8.9146 | 9.8719 | 9.3017 | 10.9391 | 11.9662 |  | 12.1724 |  |  | 11.7249 | 12.4273 | 12.4831 | [6 empty] | 12.5717 |  |  | 11.4236 |  |  | 9.2896 | 10.1857 | 11.6752 | 7.6988 | 9.123 | 12.4087 | 8.0905 | 9.6432 | 12.2264 | 9.2337 | 10.4462 | 7.7415 | 10.363 | 8.4106 | 10.3784 | 8.053 | 9.598 | 12.9871 | 10.4818 | 10.1957 | 11.611 | 8.218 | 9.6724 | 12.6026 | 8.1613 | 10.5034 | 9.7434 | 10.0964 | 8.4228 | 10.6589 | 0.13153 | 20.955 | 0.033636 | 0.048812 | -37.8761 | 3.12 | -9.71 | 0.26 | 0.5642 | -0.52678 | 0.28472 | 0.53194 | 0.49468 | 0.4707 | 0.69534 | 0.39074 | 0.39039 | 0.4148 | 0.37885 | 0.50126 | 0.41144 | 0.40417
42810.4383 | -147 | 18.4238 | 18.5547 | 18.5522 | 18.5525 | 17.9032 | 16.5546 | 14.6195 | 16.6851 | 17.1692 | 17.2596 | 17.2702 | 16.8135 | 15.8359 | 14.4546 | 14.8562 | 14.8876 | 15.4589 | 13.3243 | 13.4558 | 14.018 |  |  |  | 16.5782 | 15.9076 | 15.0122 | 10.5193 | 10.0309 | 10.7597 | 17.1071 | 16.2654 | 15.0842 | 16.8315 | 16.1275 | 15.1218 | 10.7591 | 11.9825 |  | 12.0168 | 10.7219 | 10.4771 | 9.2181 |  | 6.5122 | 6.5424 | 6.0741 | 6.2003 | 6.2201 | 6.4558 | 6.9791 | 4.8083 | 6.5057 | 4.6767 | 6.7208 | 8.0235 | 43.0126 | 47.6816 | 43.5625 | 15.2612 |  |  | -0.005037 | -0.11097 | 0.037992 | 0.032854 | 0.65465 | 0.30247 | 0.00056 | 0.2042 | -0.32263 | -0.98392 | -0.48017 | 8.8676 | 8.8688 | 2.0079 | 15.6757 | 16.6275 | 17.1863 | 17.5339 | 17.4997 | 16.4876 | 14.8386 | 16.8336 | 17.168 | 17.4744 | 17.5229 | 17.2697 | 16.4729 | 14.7071 | 6.4902 | 8.3088 | 6.4458 | 5.8595 | 5.7563 | 6.6175 | 7.6558 | 15.7228 | 15.4143 | 15.3036 | 14.2515 | 14.1374 | 14.0928 |  |  |  | 10.6352 | 9.5686 | 9.2635 | 9.3315 | -0.2919 | 0.099206 | 12.7014 |  |  | 10.5632 |  |  | 16.8595 | 16.0567 | 15.0277 | 16.3705 | 15.6545 | 14.762 | 10.6117 | 10.8932 | 11.2192 | 11.2108 | 9.6418 |  | 10.4737 | 8.915 | 9.8607 | 9.3208 | 10.9438 | 11.9941 |  | 12.1698 |  |  | 11.7307 | 12.4281 | 12.4835 | [6 empty] | 12.5565 |  |  | 11.4257 |  |  | 9.2981 | 10.1921 | 11.6682 | 7.7025 | 9.1242 | 12.4025 | 8.0991 | 9.6345 | 12.228 | 9.2352 | 10.457 | 7.7416 | 10.3714 | 8.4163 | 10.3825 | 8.0611 | 9.5888 | 13.0017 | 10.4848 | 10.1968 | 11.6129 | 8.2195 | 9.672 | 12.6017 | 8.1642 | 10.5091 | 9.7405 | 10.0989 | 8.427 | 10.6691 | -0.18221 | 20.9546 | 0.034015 | 0.04866 | -37.7926 | 3.12 | 6.04 | 0.24 | -0.083338 | -0.38824 | 0.22717 | 0.21125 | 0.94286 | 0.64089 | 0.027576 | 0.39001 | 0.39001 | 0.41443 | 0.36149 | 0.48698 | 0.41119 | 0.40395
42810.4383 | -146 | 18.4248 | 18.5577 | 18.5502 | 18.5585 | 17.9013 | 16.5507 | 14.6266 | 16.6788 | 17.1707 | 17.2604 | 17.2722 | 16.8099 | 15.8414 | 14.4529 | 14.8452 | 14.876 | 15.4508 | 13.3225 | 13.4456 | 14.0106 |  |  |  | 16.5681 | 15.9081 | 15.0124 | 10.5266 | 10.0354 | 10.7375 | 17.1112 | 16.2666 | 15.083 | 16.8344 | 16.1294 | 15.1131 | 10.7689 | 11.9417 |  | 12.0225 | 10.7294 | 10.4886 | 9.2581 |  | 6.5103 | 6.5411 | 6.0701 | 6.1994 | 6.2174 | 6.4464 | 6.9673 | 4.8426 | 6.5034 | 4.718 | 6.723 | 8.0202 | 43.0405 | 47.6589 | 43.5677 | 15.2518 |  |  | 0.069875 | -0.10242 | 0.10699 | 0.13471 | 0.34515 | -0.17131 | 0.17798 | 0.12009 | -1.2989 | -0.20871 | -0.31664 | 8.868 | 8.869 | 2.0084 | 15.6747 | 16.6191 | 17.186 | 17.5318 | 17.5028 | 16.486 | 14.8361 | 16.8301 | 17.1804 | 17.4735 | 17.522 | 17.2675 | 16.473 | 14.7054 | 6.4679 | 8.305 | 6.5182 | 5.9133 | 5.734 | 6.6231 | 7.6715 | 15.7144 | 15.3998 | 15.287 | 14.2423 | 14.1304 | 14.0793 |  |  |  | 10.646 | 9.5701 | 9.2541 | 9.3429 | -0.27792 | -0.20398 | 12.7051 |  |  | 10.5694 |  |  | 16.8606 | 16.0612 | 15.0306 | 16.3704 | 15.6567 | 14.7635 | 10.6278 | 10.9032 | 11.2233 | 11.2271 | 9.6457 |  | 10.4906 | 8.97 | 9.8776 | 9.3554 | 10.9432 | 12.0392 |  | 12.181 |  |  | 11.7295 | 12.4487 | 12.4966 | [6 empty] | 12.5654 |  |  | 11.4344 |  |  | 9.3046 | 10.1887 | 11.6644 | 7.6982 | 9.132 | 12.3951 | 8.1103 | 9.6289 | 12.2336 | 9.2412 | 10.4561 | 7.7415 | 10.3736 | 8.4158 | 10.3814 | 8.06 | 9.5887 | 13.0081 | 10.4882 | 10.1965 | 11.6111 | 8.229 | 9.6774 | 12.5978 | 8.1706 | 10.5085 | 9.7388 | 10.1054 | 8.427 | 10.6846 | -0.12886 | 20.9543 | 0.03382 | 0.048377 | -37.7869 | 3.12 | 3.52 | 0.37 | 0.31039 | -0.37299 | 0.38122 | 0.42777 | 0.6846 | -0.4823 | 0.49161 | 0.39046 | 0.38904 | 0.41345 | 0.36462 | 0.48075 | 0.4104 | 0.40399
42810.4384 | -145 | 18.4267 | 18.5541 | 18.5563 | 18.56 | 17.9112 | 16.5528 | 14.628 | 16.6843 | 17.1684 | 17.2709 | 17.2681 | 16.8116 | 15.8361 | 14.4512 | 14.847 | 14.8842 | 15.4593 | 13.3237 | 13.4456 | 14.0099 |  |  |  | 16.567 | 15.9075 | 15.012 | 10.533 | 10.0422 | 10.7187 | 17.1019 | 16.2579 | 15.0723 | 16.8316 | 16.1274 | 15.1151 | 10.7645 | 11.9181 |  | 12.0163 | 10.7417 | 10.5012 | 9.3073 |  | 6.503 | 6.5345 | 6.07 | 6.1889 | 6.2027 | 6.42 | 6.9254 | 4.8984 | 6.5029 | 4.8125 | 6.7171 | 8.0173 | 43.0524 | 47.6553 | 43.5795 | 15.2413 |  |  | -0.043809 | 0.023087 | 0.074792 | 0.15837 | 0.38326 | -0.51235 | 0.018956 | 0.1858 | 0.23937 | -1.7367 | -0.44738 | 8.8723 | 8.8732 | 2.0082 | 15.6812 | 16.6213 | 17.1901 | 17.5287 | 17.5086 | 16.4854 | 14.8404 | 16.8371 | 17.178 | 17.4774 | 17.532 | 17.2697 | 16.473 | 14.7104 | 6.3801 | 8.2679 | 6.4469 | 5.9787 | 5.7172 | 6.6238 | 7.6613 | 15.7173 | 15.4003 | 15.2917 | 14.2374 | 14.1416 | 14.0811 |  |  |  | 10.6401 | 9.581 | 9.261 | 9.3518 | -0.11705 | -0.16051 | 12.7038 |  |  | 10.5713 |  |  | 16.8583 | 16.0564 | 15.03 | 16.3689 | 15.6651 | 14.7647 | 10.636 | 10.9056 | 11.2261 | 11.2396 | 9.6476 |  | 10.4857 | 9.0227 | 9.872 | 9.3778 | 10.9415 | 12.0682 |  | 12.1723 |  |  | 11.7068 | 12.4462 | 12.491 | [6 empty] | 12.5529 |  |  | 11.4254 |  |  | 9.3027 | 10.1948 | 11.6586 | 7.6887 | 9.1303 | 12.4006 | 8.1132 | 9.6274 | 12.2313 | 9.2376 | 10.4597 | 7.7505 | 10.3853 | 8.4026 | 10.3749 | 8.0532 | 9.5915 | 13.0172 | 10.4837 | 10.1946 | 11.6155 | 8.2487 | 9.6876 | 12.6086 | 8.1833 | 10.5213 | 9.7403 | 10.1106 | 8.4325 | 10.6913 | -0.12308 | 20.9535 | 0.03215 | 0.046705 | -37.7812 | 3.12 | -11.33 | 0.32 | -0.24576 | 0.17709 | 0.31873 | 0.4638 | 0.72138 | -0.83406 | 0.16043 | 0.39025 | 0.38739 | 0.41277 | 0.37446 | 0.4875 | 0.40889 | 0.40355
42810.4384 | -144 | 18.4204 | 18.5544 | 18.5543 | 18.5594 | 17.9064 | 16.5519 | 14.6284 | 16.6836 | 17.1721 | 17.2695 | 17.276 | 16.8126 | 15.8324 | 14.4519 | 14.8404 | 14.8819 | 15.4506 | 13.3186 | 13.4589 | 14.021 |  |  |  | 16.575 | 15.9128 | 15.0114 | 10.5359 | 10.0435 | 10.6788 | 17.1091 | 16.2714 | 15.0811 | 16.8381 | 16.1271 | 15.1285 | 10.7744 | 11.9055 |  | 12.0127 | 10.7571 | 10.5118 | 9.3516 |  | 6.4859 | 6.5233 | 6.0628 | 6.1911 | 6.193 | 6.4084 | 6.8955 | 4.949 | 6.5032 | 4.8309 | 6.7188 | 8.0167 | 43.0702 | 47.6521 | 43.5797 | 15.239 |  |  | 0.14676 | 0.16699 | 0.09516 | 0.089366 | 0.61062 | -0.049744 | 0.51245 | 0.19368 | -0.41448 | -0.74895 | -0.34008 | 8.8692 | 8.87 | 2.0081 | 15.6766 | 16.6284 | 17.1986 | 17.5315 | 17.5128 | 16.4889 | 14.8491 | 16.8384 | 17.1764 | 17.477 | 17.5382 | 17.272 | 16.4795 | 14.7175 | 6.2982 | 8.2202 | 6.2642 | 5.9562 | 5.7228 | 6.6217 | 7.6595 | 15.7176 | 15.3984 | 15.2917 | 14.2442 | 14.1362 | 14.0839 |  |  |  | 10.6454 | 9.59 | 9.2664 | 9.3659 | -0.083017 | -0.26477 | 12.7101 |  |  | 10.5753 |  |  | 16.8565 | 16.0578 | 15.0339 | 16.3695 | 15.6645 | 14.7684 | 10.6422 | 10.9097 | 11.2414 | 11.2451 | 9.6445 |  | 10.4816 | 9.1139 | 9.8811 | 9.409 | 10.9471 | 12.1011 |  | 12.1739 |  |  | 11.7174 | 12.4682 | 12.5012 | [6 empty] | 12.56 |  |  | 11.4258 |  |  | 9.3128 | 10.1977 | 11.6514 | 7.6844 | 9.136 | 12.4178 | 8.116 | 9.6366 | 12.2409 | 9.2371 | 10.4643 | 7.7626 | 10.395 | 8.4128 | 10.3696 | 8.0499 | 9.5866 | 13.0247 | 10.4851 | 10.1908 | 11.6236 | 8.2375 | 9.6885 | 12.6106 | 8.1958 | 10.5258 | 9.7443 | 10.1111 | 8.4429 | 10.6976 | -0.27042 | 20.9525 | 0.032196 | 0.046807 | -37.748 | 3.12 | -15.55 | 0.28 | 0.44977 | 0.47626 | 0.35952 | 0.3484 | 0.91052 | -0.25988 | 0.83412 | 0.3902 | 0.38516 | 0.41208 | 0.38332 | 0.50759 | 0.40798 | 0.40334
42810.4384 | -143 | 18.4159 | 18.5552 | 18.5585 | 18.5634 | 17.9008 | 16.5496 | 14.6233 | 16.6841 | 17.1725 | 17.2633 | 17.2745 | 16.8127 | 15.8315 | 14.4464 | 14.8412 | 14.8845 | 15.4529 | 13.317 | 13.4381 | 14.0138 |  |  |  | 16.5741 | 15.9087 | 15.012 | 10.5401 | 10.0529 | 10.6529 | 17.101 | 16.2621 | 15.0796 | 16.8326 | 16.1226 | 15.121 | 10.777 | 11.9075 |  | 12.0168 | 10.7606 | 10.5231 | 9.3954 |  | 6.468 | 6.5165 | 6.0625 | 6.1893 | 6.1917 | 6.4023 | 6.8776 | 4.9663 | 6.5049 | 4.7946 | 6.7168 | 8.0208 | 43.0611 | 47.6292 | 43.5786 | 15.2272 |  |  | 0.091559 | -0.14711 | 0.06362 | 0.16297 | 0.2801 | -0.2771 | 0.54136 | 0.20288 | -0.65793 | -0.34613 | -0.33353 | 8.869 | 8.8703 | 2.0081 | 15.6724 | 16.6273 | 17.1981 | 17.5297 | 17.5044 | 16.4892 | 14.8456 | 16.8315 | 17.181 | 17.4805 | 17.5291 | 17.2743 | 16.4842 | 14.7173 | 6.2335 | 8.1949 | 6.1516 | 5.8843 | 5.7045 | 6.6138 | 7.662 | 15.7099 | 15.4043 | 15.289 | 14.2397 | 14.1316 | 14.0792 |  |  |  | 10.6447 | 9.5949 | 9.2744 | 9.376 | 0.0051138 | -0.2245 | 12.707 |  |  | 10.5754 |  |  | 16.8545 | 16.0574 | 15.0315 | 16.3698 | 15.6571 | 14.7694 | 10.639 | 10.9102 | 11.2514 | 11.248 | 9.6415 |  | 10.4774 | 9.1798 | 9.8763 | 9.4398 | 10.944 | 12.1168 |  | 12.1829 |  |  | 11.7397 | 12.4516 | 12.5013 | [6 empty] | 12.5814 |  |  | 11.4588 |  |  | 9.3147 | 10.1946 | 11.6376 | 7.6941 | 9.1326 | 12.4227 | 8.1147 | 9.6387 | 12.2441 | 9.239 | 10.4602 | 7.7624 | 10.4055 | 8.4079 | 10.3664 | 8.0588 | 9.5953 | 13.0331 | 10.4925 | 10.1919 | 11.6357 | 8.2543 | 9.689 | 12.6105 | 8.2013 | 10.5334 | 9.7595 | 10.1246 | 8.4452 | 10.7122 | -0.18337 | 20.9538 | 0.033338 | 0.049079 | -37.8233 | 3.12 | 1.81 | 0.34 | 0.35524 | -0.44699 | 0.29396 | 0.47047 | 0.61667 | -0.61337 | 0.85732 | 0.39014 | 0.38317 | 0.41113 | 0.3896 | 0.5204 | 0.40685 | 0.40303
42810.4384 | -142 | 18.4172 | 18.5497 | 18.5563 | 18.5612 | 17.8963 | 16.5464 | 14.6172 | 16.6832 | 17.1672 | 17.2666 | 17.2691 | 16.8101 | 15.8312 | 14.4435 | 14.8594 | 14.8908 | 15.4609 | 13.328 | 13.4565 | 14.0216 |  |  |  | 16.5862 | 15.9172 | 15.0145 | 10.551 | 10.0692 | 10.6629 | 17.0924 | 16.2561 | 15.0722 | 16.8286 | 16.1193 | 15.1126 | 10.7707 | 11.927 |  | 12.0157 | 10.7636 | 10.5271 | 9.4229 |  | 6.4737 | 6.5296 | 6.072 | 6.1975 | 6.195 | 6.3994 | 6.8648 | 4.9698 | 6.5054 | 4.8654 | 6.7193 | 8.0234 | 43.068 | 47.6215 | 43.6041 | 15.2315 |  |  | 0.084331 | 0.059887 | 0.1405 | -0.073598 | 0.35106 | -0.43547 | 0.49931 | 0.33299 | -0.64139 | -0.31508 | -0.23596 | 8.8704 | 8.8716 | 2.0082 | 15.668 | 16.6271 | 17.1924 | 17.5394 | 17.4978 | 16.4923 | 14.838 | 16.8321 | 17.1854 | 17.4823 | 17.5352 | 17.2797 | 16.4777 | 14.7117 | 6.1895 | 8.1786 | 6.0511 | 5.8698 | 5.6683 | 6.6154 | 7.6664 | 15.7121 | 15.3983 | 15.2796 | 14.2356 | 14.1296 | 14.0804 |  |  |  | 10.6417 | 9.6054 | 9.2742 | 9.3858 | -0.13833 | -0.14395 | 12.7068 |  |  | 10.5815 |  |  | 16.8571 | 16.0544 | 15.0263 | 16.3639 | 15.6561 | 14.7677 | 10.6409 | 10.9105 | 11.2488 | 11.257 | 9.6167 |  | 10.4861 | 9.1767 | 9.8776 | 9.4706 | 10.9452 | 12.1314 |  | 12.1832 |  |  | 11.7334 | 12.4586 | 12.4902 | [6 empty] | 12.5342 |  |  | 11.4564 |  |  | 9.3194 | 10.2005 | 11.6373 | 7.7001 | 9.1462 | 12.4375 | 8.1204 | 9.6398 | 12.2742 | 9.2452 | 10.4676 | 7.7848 | 10.4248 | 8.4104 | 10.3666 | 8.0362 | 9.5858 | 13.0214 | 10.4795 | 10.1926 | 11.6272 | 8.2435 | 9.6907 | 12.6071 | 8.1798 | 10.542 | 9.7517 | 10.1275 | 8.4493 | 10.7271 | -0.167 | 20.9531 | 0.033573 | 0.049275 | -37.8049 | 3.12 | -1.27 | 0.25 | 0.34094 | 0.28521 | 0.43685 | -0.31618 | 0.69038 | -0.76891 | 0.82334 | 0.39112 | 0.3833 | 0.41031 | 0.39467 | 0.53206 | 0.40588 | 0.40266
42810.4384 | -141 | 18.4123 | 18.5482 | 18.5596 | 18.5571 | 17.9013 | 16.5466 | 14.6222 | 16.6874 | 17.1745 | 17.2686 | 17.2744 | 16.8107 | 15.8348 | 14.4481 | 14.8377 | 14.888 | 15.4552 | 13.3252 | 13.4457 | 14.0139 |  |  |  | 16.5766 | 15.912 | 15.0062 | 10.5487 | 10.0833 | 10.6643 | 17.0914 | 16.254 | 15.0714 | 16.819 | 16.1155 | 15.1126 | 10.7649 | 11.9416 |  | 12.0111 | 10.7761 | 10.5349 | 9.4331 |  | 6.479 | 6.5381 | 6.0767 | 6.22 | 6.2032 | 6.3964 | 6.8437 | 4.8992 | 6.5028 | 4.9047 | 6.723 | 8.013 | 43.0599 | 47.6064 | 43.6179 | 15.2347 |  |  | 0.083671 | 0.088799 | -0.012608 | 0.026286 | 0.15064 | -0.066172 | 0.43097 | 0.19303 | 0.50364 | -0.8293 | -0.40824 | 8.8698 | 8.8712 | 2.0083 | 15.6714 | 16.6255 | 17.1908 | 17.5319 | 17.5104 | 16.4881 | 14.8382 | 16.8401 | 17.1816 | 17.4862 | 17.539 | 17.2768 | 16.4838 | 14.7145 | 6.1804 | 8.1545 | 5.9409 | 5.8709 | 5.6788 | 6.6202 | 7.6618 | 15.6996 | 15.401 | 15.284 | 14.2369 | 14.1261 | 14.0736 |  |  |  | 10.6301 | 9.6141 | 9.2765 | 9.3934 | -0.11381 | -0.17425 | 12.7096 |  |  | 10.5799 |  |  | 16.8549 | 16.0549 | 15.0306 | 16.3635 | 15.6568 | 14.7629 | 10.6373 | 10.9128 | 11.2457 | 11.2703 | 9.6008 |  | 10.4935 | 9.172 | 9.8898 | 9.5017 | 10.9522 | 12.1659 |  | 12.1863 |  |  | 11.7381 | 12.4662 | 12.4928 | [6 empty] | 12.5491 |  |  | 11.4576 |  |  | 9.332 | 10.2154 | 11.6327 | 7.7037 | 9.1662 | 12.4494 | 8.1383 | 9.6496 | 12.2877 | 9.2661 | 10.4812 | 7.7914 | 10.4575 | 8.409 | 10.3833 | 8.0304 | 9.5946 | 13.0336 | 10.4898 | 10.1991 | 11.6348 | 8.2686 | 9.7144 | 12.6078 | 8.1339 | 10.5437 | 9.7573 | 10.1315 | 8.4699 | 10.7497 | -0.14716 | 20.9533 | 0.034124 | 0.049521 | -37.8025 | 3.12 | -0.14 | 0.29 | 0.3396 | 0.3473 | -0.13087 | 0.18896 | 0.45224 | -0.29973 | 0.76492 | 0.3918 | 0.38383 | 0.40968 | 0.39623 | 0.54377 | 0.40541 | 0.40207
42810.4384 | -140 | 18.4128 | 18.5502 | 18.5601 | 18.5519 | 17.8975 | 16.5539 | 14.617 | 16.6888 | 17.1773 | 17.264 | 17.2688 | 16.8068 | 15.8393 | 14.4483 | 14.8488 | 14.8822 | 15.4595 | 13.3229 | 13.4469 | 14.0198 |  |  |  | 16.5814 | 15.9205 | 15.0253 | 10.5575 | 10.0964 | 10.6832 | 17.0931 | 16.2608 | 15.0737 | 16.8226 | 16.1231 | 15.1157 | 10.7719 | 11.9539 |  | 12.0145 | 10.7889 | 10.5471 | 9.4206 |  | 6.4694 | 6.5212 | 6.07 | 6.2181 | 6.1989 | 6.3862 | 6.8239 | 4.8694 | 6.491 | 4.9077 | 6.7108 | 8.012 | 43.0587 | 47.5849 | 43.6315 | 15.242 |  |  | 0.15004 | 0.13019 | 0.12276 | -0.00263 | 0.20781 | -0.13911 | 0.53216 | 0.23246 | -0.3561 | 2.1564 | -0.2157 | 8.8694 | 8.8705 | 2.008 | 15.6585 | 16.6216 | 17.1905 | 17.5258 | 17.5081 | 16.4875 | 14.8393 | 16.8334 | 17.1795 | 17.4783 | 17.5332 | 17.2679 | 16.4783 | 14.7153 | 6.1719 | 8.1363 | 5.8143 | 5.8287 | 5.712 | 6.615 | 7.6616 | 15.7065 | 15.3919 | 15.2839 | 14.2402 | 14.1298 | 14.0772 |  |  |  | 10.6443 | 9.6286 | 9.2856 | 9.4019 | -0.21511 | -0.31126 | 12.7145 |  |  | 10.5867 |  |  | 16.8551 | 16.0573 | 15.0272 | 16.3718 | 15.6566 | 14.7639 | 10.6399 | 10.9171 | 11.2605 | 11.2777 | 9.5944 |  | 10.4887 | 9.1811 | 9.8938 | 9.5269 | 10.952 | 12.1871 |  | 12.1824 |  |  | 11.7377 | 12.479 | 12.4932 | [6 empty] | 12.5459 |  |  | 11.4601 |  |  | 9.3343 | 10.2206 | 11.6306 | 7.698 | 9.1702 | 12.4632 | 8.143 | 9.6629 | 12.3049 | 9.2588 | 10.4884 | 7.8039 | 10.4789 | 8.4264 | 10.3787 | 7.9754 | 9.5951 | 13.0322 | 10.4947 | 10.196 | 11.6416 | 8.2801 | 9.718 | 12.6135 | 8.0891 | 10.5592 | 9.7686 | 10.1327 | 8.4827 | 10.7674 | 0.18238 | 20.9541 | 0.034939 | 0.049586 | -37.8263 | 3.12 | -8.81 | 0.31 | 0.45479 | 0.42052 | 0.40834 | -0.059768 | 0.53116 | -0.43458 | 0.84998 | 0.39182 | 0.38371 | 0.40897 | 0.39657 | 0.55782 | 0.40598 | 0.4023
42810.4384 | -139 | 18.4078 | 18.5393 | 18.5515 | 18.5537 | 17.9021 | 16.5489 | 14.6177 | 16.6792 | 17.1731 | 17.2613 | 17.2681 | 16.808 | 15.8343 | 14.4463 | 14.8486 | 14.8845 | 15.4488 | 13.3245 | 13.452 | 14.0215 |  |  |  | 16.58 | 15.9088 | 15.0189 | 10.567 | 10.0932 | 10.6801 | 17.0826 | 16.2432 | 15.0614 | 16.8179 | 16.1117 | 15.1068 | 10.7623 | 11.9363 |  | 12.0049 | 10.7876 | 10.5449 | 9.3515 |  | 6.4627 | 6.5214 | 6.0658 | 6.2173 | 6.2117 | 6.3822 | 6.8674 | 4.8413 | 6.486 | 4.9417 | 6.7076 | 8.0223 | 43.0649 | 47.5681 | 43.6509 | 15.2556 |  |  | 0.048187 | 0.15451 | 0.057704 | -0.23787 | 0.39772 | -0.10626 | 0.38957 | 0.19106 | -0.42713 | 0.0084292 | -0.19483 | 8.8703 | 8.8716 | 2.0084 | 15.6676 | 16.6176 | 17.1904 | 17.5291 | 17.5034 | 16.4892 | 14.8449 | 16.8373 | 17.1774 | 17.4759 | 17.5312 | 17.2719 | 16.4837 | 14.7243 | 6.1529 | 8.1225 | 5.7313 | 5.7641 | 5.677 | 6.6097 | 7.6601 | 15.7071 | 15.3961 | 15.2856 | 14.2348 | 14.1326 | 14.0805 |  |  |  | 10.6488 | 9.6327 | 9.2925 | 9.4047 | -0.089703 | -0.19909 | 12.7098 |  |  | 10.5873 |  |  | 16.8548 | 16.0513 | 15.0211 | 16.3694 | 15.6482 | 14.7561 | 10.6301 | 10.9163 | 11.2604 | 11.2793 | 9.5829 |  | 10.4863 | 9.213 | 9.8859 | 9.5657 | 10.9488 | 12.193 |  | 12.1865 |  |  | 11.7556 | 12.4921 | 12.5084 | [6 empty] | 12.5498 |  |  | 11.4647 |  |  | 9.3352 | 10.2225 | 11.6323 | 7.7028 | 9.1718 | 12.4697 | 8.1382 | 9.6569 | 12.3024 | 9.2688 | 10.493 | 7.8162 | 10.486 | 8.433 | 10.3813 | 7.9216 | 9.5952 | 13.0297 | 10.4919 | 10.1935 | 11.6403 | 8.274 | 9.723 | 12.6144 | 8.0625 | 10.5553 | 9.7732 | 10.1398 | 8.4953 | 10.7675 | 0.073754 | 20.9532 | 0.034778 | 0.05015 | -37.8107 | 3.12 | 13.1 | 0.25 | 0.25773 | 0.45811 | 0.27996 | -0.56841 | 0.7348 | -0.3798 | 0.72724 | 0.39206 | 0.38256 | 0.40779 | 0.39807 | 0.56687 | 0.40759 | 0.40237
42810.4384 | -138 | 18.4082 | 18.5465 | 18.5552 | 18.5564 | 17.9005 | 16.5522 | 14.6151 | 16.6827 | 17.1717 | 17.2604 | 17.2773 | 16.803 | 15.8439 | 14.4493 | 14.8388 | 14.8768 | 15.4487 | 13.3215 | 13.4479 | 14.0134 |  |  |  | 16.575 | 15.9162 | 15.0162 | 10.5711 | 10.0925 | 10.6655 | 17.0936 | 16.2545 | 15.0703 | 16.8322 | 16.1227 | 15.1188 | 10.7744 | 11.9744 |  | 12.007 | 10.8112 | 10.5714 | 9.2903 |  | 6.4597 | 6.5102 | 6.0651 | 6.2217 | 6.2091 | 6.3664 | 6.8796 | 4.7978 | 6.4908 | 4.8285 | 6.7114 | 8.0141 | 43.0845 | 47.5428 | 43.6707 | 15.2556 |  |  | 0.2473 | 0.17094 | -0.052692 | -0.17151 | 0.57974 | 0.059336 | -0.014556 | 0.3054 | -0.58048 | -0.29704 | -0.13204 | 8.8686 | 8.8696 | 2.0083 | 15.67 | 16.6191 | 17.1956 | 17.5422 | 17.5082 | 16.4908 | 14.8468 | 16.8346 | 17.185 | 17.4859 | 17.5349 | 17.2793 | 16.4818 | 14.7273 | 6.1669 | 8.1418 | 5.661 | 5.7068 | 5.6879 | 6.6076 | 7.6607 | 15.7098 | 15.3964 | 15.2806 | 14.2426 | 14.1287 | 14.0774 |  |  |  | 10.6428 | 9.6343 | 9.2964 | 9.4079 | -0.27853 | -0.17481 | 12.7133 |  |  | 10.5866 |  |  | 16.8576 | 16.0508 | 15.0269 | 16.3661 | 15.6549 | 14.7572 | 10.6259 | 10.9234 | 11.2662 | 11.2948 | 9.5537 |  | 10.4922 | 9.2436 | 9.8917 | 9.5615 | 10.9483 | 12.201 |  | 12.1797 |  |  | 11.7659 | 12.4969 | 12.5186 | [6 empty] | 12.5498 |  |  | 11.4729 |  |  | 9.342 | 10.2234 | 11.624 | 7.7094 | 9.1846 | 12.4854 | 8.1428 | 9.6586 | 12.3153 | 9.28 | 10.5043 | 7.83 | 10.4951 | 8.4438 | 10.3884 | 7.9016 | 9.5849 | 13.0346 | 10.4966 | 10.1968 | 11.6478 | 8.2797 | 9.7357 | 12.6232 | 8.0162 | 10.5604 | 9.7715 | 10.1515 | 8.5106 | 10.7722 | 0.093399 | 20.9526 | 0.034612 | 0.048276 | -37.7326 | 3.12 | 3.3 | 0.32 | 0.58384 | 0.48184 | -0.26752 | -0.48264 | 0.88713 | 0.28381 | -0.14057 | 0.39307 | 0.38191 | 0.40789 | 0.39627 | 0.57475 | 0.40969 | 0.40208
42810.4384 | -137 | 18.404 | 18.5511 | 18.5469 | 18.5545 | 17.9035 | 16.5482 | 14.6178 | 16.6854 | 17.1715 | 17.268 | 17.2765 | 16.8096 | 15.8356 | 14.4612 | 14.8347 | 14.8751 | 15.4467 | 13.3236 | 13.4461 | 14.012 |  |  |  | 16.5755 | 15.9117 | 15.0145 | 10.5742 | 10.1006 | 10.6704 | 17.0903 | 16.2549 | 15.0662 | 16.8237 | 16.1133 | 15.1201 | 10.7769 | 11.9897 |  | 12.0118 | 10.8229 | 10.587 | 9.212 |  | 6.45 | 6.5046 | 6.0624 | 6.2201 | 6.2035 | 6.3449 | 6.8658 | 4.8023 | 6.4875 | 4.7265 | 6.7047 | 8.0133 | 43.1161 | 47.5147 | 43.6836 | 15.2497 |  |  | 0.027819 | -0.041309 | -0.4187 | 0.25825 | 0.57711 | -0.1654 | -0.17621 | 0.34285 | -0.047078 | -0.45817 | -0.20139 | 8.8699 | 8.871 | 2.008 | 15.6654 | 16.62 | 17.1863 | 17.5353 | 17.5007 | 16.4851 | 14.8376 | 16.8289 | 17.1771 | 17.4816 | 17.5326 | 17.2779 | 16.4806 | 14.7195 | 6.1371 | 8.1137 | 5.6025 | 5.6749 | 5.666 | 6.6014 | 7.6487 | 15.7007 | 15.3994 | 15.2814 | 14.2372 | 14.1372 | 14.0738 |  |  |  | 10.6532 | 9.6499 | 9.3117 | 9.4087 | -0.20053 | -0.15938 | 12.7175 |  |  | 10.59 |  |  | 16.8614 | 16.0593 | 15.0303 | 16.3647 | 15.6612 | 14.7614 | 10.6219 | 10.9296 | 11.2767 | 11.3028 | 9.5398 |  | 10.4897 | 9.2593 | 9.883 | 9.5612 | 10.9447 | 12.2032 |  | 12.1786 |  |  | 11.7769 | 12.4996 | 12.5274 | [6 empty] | 12.5551 |  |  | 11.4766 |  |  | 9.3493 | 10.2254 | 11.6216 | 7.7128 | 9.193 | 12.4919 | 8.1517 | 9.6601 | 12.3288 | 9.2846 | 10.5052 | 7.8325 | 10.4928 | 8.4545 | 10.395 | 7.8851 | 9.5874 | 13.0411 | 10.5046 | 10.2078 | 11.6481 | 8.2906 | 9.754 | 12.6273 | 7.9992 | 10.5708 | 9.7791 | 10.1587 | 8.5182 | 10.7852 | -0.081867 | 20.9541 | 0.033292 | 0.047559 | -37.733 | 3.12 | 0.66 | 0.25 | 0.19582 | -0.23686 | -0.7541 | 0.59224 | 0.88508 | -0.47382 | -0.48907 | 0.39337 | 0.38118 | 0.40778 | 0.39886 | 0.57986 | 0.41194 | 0.4024
42810.4385 | -136 | 18.4012 | 18.5494 | 18.5488 | 18.5556 | 17.8988 | 16.5508 | 14.6193 | 16.6877 | 17.1717 | 17.2703 | 17.2683 | 16.8067 | 15.8413 | 14.4528 | 14.833 | 14.8666 | 15.4476 | 13.3213 | 13.4415 | 14.0103 |  |  |  | 16.5754 | 15.9145 | 15.0179 | 10.5796 | 10.1043 | 10.6786 | 17.0815 | 16.2447 | 15.0536 | 16.8217 | 16.1143 | 15.1076 | 10.7638 | 12.0099 |  | 12.0119 | 10.8338 | 10.5773 | 9.1464 |  | 6.4427 | 6.5015 | 6.0449 | 6.2015 | 6.1881 | 6.3344 | 6.8329 | 4.8278 | 6.4856 | 4.6546 | 6.7073 | 8.0079 | 43.1472 | 47.4843 | 43.6917 | 15.2425 |  |  | 0.094187 | 0.043459 | -0.56524 | 0.069654 | 0.08296 | -0.35267 | -0.63684 | 0.1904 | -1.1977 | -0.28403 | -0.37545 | 8.8686 | 8.8694 | 2.0083 | 15.6543 | 16.6063 | 17.1754 | 17.5263 | 17.4971 | 16.4785 | 14.8336 | 16.8276 | 17.1763 | 17.4773 | 17.5229 | 17.2742 | 16.481 | 14.7121 | 6.0599 | 8.0931 | 5.542 | 5.6124 | 5.6511 | 6.6028 | 7.6485 | 15.6972 | 15.3936 | 15.2837 | 14.2297 | 14.1225 | 14.0715 |  |  |  | 10.644 | 9.649 | 9.3075 | 9.3975 | -0.21916 | -0.15806 | 12.7125 |  |  | 10.5895 |  |  | 16.8593 | 16.0518 | 15.0266 | 16.3586 | 15.6495 | 14.7561 | 10.6114 | 10.9244 | 11.2779 | 11.3024 | 9.535 |  | 10.4932 | 9.2448 | 9.8914 | 9.566 | 10.9487 | 12.2055 |  | 12.1802 |  |  | 11.7874 | 12.5065 | 12.5334 | [6 empty] | 12.5521 |  |  | 11.4817 |  |  | 9.3479 | 10.2211 | 11.6195 | 7.6999 | 9.193 | 12.4847 | 8.1492 | 9.6569 | 12.328 | 9.2766 | 10.5077 | 7.7967 | 10.4873 | 8.4603 | 10.3999 | 7.8591 | 9.5926 | 13.0483 | 10.5036 | 10.2068 | 11.644 | 8.2785 | 9.7556 | 12.6217 | 7.9984 | 10.5869 | 9.7825 | 10.1597 | 8.5237 | 10.7855 | 0.046404 | 20.953 | 0.033849 | 0.047458 | -37.7919 | 3.12 | -3.59 | 0.34 | 0.36032 | 0.24295 | -0.87618 | 0.30757 | 0.33557 | -0.69188 | -0.92974 | 0.39362 | 0.38186 | 0.40778 | 0.40761 | 0.58656 | 0.41334 | 0.40241
42810.4385 | -135 | 18.4033 | 18.5589 | 18.5536 | 18.554 | 17.9014 | 16.5524 | 14.6233 | 16.6871 | 17.1752 | 17.2701 | 17.2683 | 16.8088 | 15.8401 | 14.457 | 14.8228 | 14.8659 | 15.4379 | 13.3082 | 13.4366 | 14.0038 |  |  |  | 16.5747 | 15.9133 | 15.0124 | 10.5791 | 10.1033 | 10.6814 | 17.0821 | 16.2529 | 15.0593 | 16.8239 | 16.125 | 15.1149 | 10.7707 | 12.0348 |  | 12.0139 | 10.8493 | 10.587 | 9.1048 |  | 6.4346 | 6.4902 | 6.0138 | 6.1629 | 6.1612 | 6.3085 | 6.7877 | 4.8186 | 6.4875 | 4.5776 | 6.7026 | 8.0058 | 43.1697 | 47.4677 | 43.7089 | 15.2417 |  |  | -0.11346 | -0.26342 | -0.16046 | -0.073598 | 0.007392 | -1.0236 | -0.27346 | 0.42499 | -0.60149 | -1.4872 | -0.37287 | 8.8708 | 8.8723 | 2.0081 | 15.6665 | 16.6256 | 17.1863 | 17.5323 | 17.4999 | 16.4879 | 14.8478 | 16.8396 | 17.1867 | 17.4809 | 17.5378 | 17.2841 | 16.4906 | 14.7261 | 6.0181 | 8.085 | 5.4353 | 5.5596 | 5.6529 | 6.5939 | 7.649 | 15.6945 | 15.3867 | 15.2775 | 14.2265 | 14.1186 | 14.0768 |  |  |  | 10.6443 | 9.6487 | 9.3141 | 9.3888 | -0.2372 | -0.43472 | 12.7117 |  |  | 10.5901 |  |  | 16.8563 | 16.0488 | 15.0269 | 16.3604 | 15.6511 | 14.761 | 10.6125 | 10.923 | 11.2898 | 11.3127 | 9.543 |  | 10.4859 | 9.1671 | 9.8892 | 9.586 | 10.9477 | 12.2121 |  | 12.1818 |  |  | 11.781 | 12.502 | 12.5364 | [6 empty] | 12.544 |  |  | 11.4794 |  |  | 9.3506 | 10.2271 | 11.619 | 7.6786 | 9.204 | 12.4939 | 8.1292 | 9.6557 | 12.338 | 9.2765 | 10.5074 | 7.7612 | 10.4851 | 8.4658 | 10.4016 | 7.8466 | 9.6013 | 13.0553 | 10.4997 | 10.2094 | 11.6505 | 8.2616 | 9.7693 | 12.6211 | 8.0041 | 10.6059 | 9.7807 | 10.1698 | 8.5316 | 10.7822 | 0.33935 | 20.9525 | 0.034859 | 0.048544 | -37.7823 | 3.12 | -4.22 | 0.38 | -0.39548 | -0.59812 | -0.46681 | -0.31615 | 0.10016 | -1.1787 | -0.60922 | 0.39316 | 0.38395 | 0.40719 | 0.41122 | 0.59847 | 0.41472 | 0.40266
42810.4385 | -134 | 18.3988 | 18.5459 | 18.548 | 18.5523 | 17.8974 | 16.5473 | 14.6188 | 16.6828 | 17.1705 | 17.2702 | 17.2667 | 16.8058 | 15.8436 | 14.452 | 14.8185 | 14.8622 | 15.4368 | 13.3071 | 13.4296 | 14.0018 |  |  |  | 16.5702 | 15.9053 | 15.0065 | 10.5834 | 10.1061 | 10.6752 | 17.0755 | 16.2446 | 15.0592 | 16.822 | 16.1125 | 15.111 | 10.7716 | 12.0488 |  | 12.0165 | 10.852 | 10.5927 | 9.0361 |  | 6.4354 | 6.488 | 6.0015 | 6.1562 | 6.1457 | 6.2893 | 6.7478 | 4.8217 | 6.491 | 4.5094 | 6.7075 | 7.9945 | 43.1707 | 47.4467 | 43.7139 | 15.2272 |  |  | 0.13559 | -0.050509 | 0.1037 | -0.021026 | -0.02152 | -0.51892 | 0.19638 | 0.22391 | -0.55226 | -0.46215 | -0.28504 | 8.8692 | 8.8703 | 2.0085 | 15.6578 | 16.6181 | 17.1903 | 17.5323 | 17.5023 | 16.485 | 14.8439 | 16.832 | 17.1762 | 17.4774 | 17.5368 | 17.2804 | 16.4762 | 14.7222 | 6.0089 | 8.0528 | 5.3731 | 5.4783 | 5.6845 | 6.5925 | 7.6413 | 15.6925 | 15.3925 | 15.2777 | 14.2222 | 14.1172 | 14.0786 |  |  |  | 10.6444 | 9.664 | 9.3227 | 9.3863 | -0.36342 | -0.27287 | 12.7069 |  |  | 10.5836 |  |  | 16.8499 | 16.0489 | 15.0235 | 16.3621 | 15.6504 | 14.7578 | 10.6116 | 10.9155 | 11.2935 | 11.3254 | 9.5471 |  | 10.4916 | 9.126 | 9.8918 | 9.5833 | 10.9476 | 12.2196 |  | 12.1814 |  |  | 11.7753 | 12.489 | 12.5465 | [6 empty] | 12.5391 |  |  | 11.4837 |  |  | 9.3462 | 10.2289 | 11.6293 | 7.6373 | 9.2033 | 12.4972 | 8.1223 | 9.6657 | 12.3488 | 9.2743 | 10.5016 | 7.74 | 10.4815 | 8.4672 | 10.4033 | 7.8373 | 9.6101 | 13.061 | 10.497 | 10.2123 | 11.6492 | 8.2489 | 9.7999 | 12.6315 | 8.0219 | 10.6239 | 9.7772 | 10.1842 | 8.5212 | 10.7902 | 0.0096178 | 20.9515 | 0.035083 | 0.049289 | -37.8347 | 3.12 | 9.09 | 0.27 | 0.43232 | -0.26191 | 0.37529 | -0.16898 | -0.1709 | -0.83919 | 0.51625 | 0.39323 | 0.38518 | 0.40726 | 0.41207 | 0.60449 | 0.41666 | 0.40274
42810.4385 | -133 | 18.3992 | 18.5379 | 18.5472 | 18.5488 | 17.8958 | 16.5442 | 14.6153 | 16.6841 | 17.1674 | 17.2648 | 17.2684 | 16.8057 | 15.8413 | 14.451 | 14.8288 | 14.8634 | 15.4453 | 13.3183 | 13.4392 | 14.0033 |  |  |  | 16.5702 | 15.9066 | 15.0146 | 10.5918 | 10.1129 | 10.6677 | 17.0765 | 16.2462 | 15.0584 | 16.8225 | 16.1163 | 15.1117 | 10.7755 | 12.0808 |  | 12.0165 | 10.8637 | 10.5984 | 8.9721 |  | 6.417 | 6.4641 | 5.9838 | 6.1256 | 6.0964 | 6.2528 | 6.6795 | 4.8344 | 6.4718 | 4.3808 | 6.6901 | 7.9991 | 43.1759 | 47.4435 | 43.7284 | 15.2177 |  |  | 0.051475 | -0.008453 | 0.18518 | 0.41464 | -0.10826 | -0.14897 | 0.066928 | 0.2686 | -0.5651 | -0.42355 | -0.43049 | 8.8675 | 8.8685 | 2.0081 | 15.6539 | 16.6107 | 17.1815 | 17.5193 | 17.4906 | 16.4692 | 14.836 | 16.8262 | 17.1769 | 17.4703 | 17.5212 | 17.2685 | 16.4816 | 14.7129 | 5.9075 | 8.0385 | 5.3814 | 5.4493 | 5.6787 | 6.5934 | 7.653 | 15.6948 | 15.3891 | 15.2773 | 14.2259 | 14.1174 | 14.0757 |  |  |  | 10.6396 | 9.6652 | 9.3198 | 9.4384 | -0.10044 | -0.30392 | 12.7133 |  |  | 10.5778 |  |  | 16.8537 | 16.0511 | 15.0229 | 16.3588 | 15.6412 | 14.7499 | 10.6087 | 10.9047 | 11.3022 | 11.3387 | 9.548 |  | 10.4948 | 9.1146 | 9.8868 | 9.5621 | 10.9472 | 12.2272 |  | 12.179 |  |  | 11.7784 | 12.4916 | 12.5552 | [6 empty] | 12.5461 |  |  | 11.491 |  |  | 9.3487 | 10.2306 | 11.6394 | 7.6011 | 9.2094 | 12.499 | 8.1289 | 9.6705 | 12.3527 | 9.2742 | 10.5089 | 7.732 | 10.4812 | 8.4817 | 10.4026 | 7.8278 | 9.6118 | 13.0574 | 10.4969 | 10.2115 | 11.6485 | 8.2383 | 9.8158 | 12.6207 | 8.0278 | 10.6337 | 9.7861 | 10.1854 | 8.503 | 10.7867 | 0.088391 | 20.9521 | 0.035077 | 0.050107 | -37.8046 | 3.12 | -10.44 | 0.21 | 0.26637 | -0.10714 | 0.50147 | 0.75038 | -0.38328 | -0.4496 | 0.30136 | 0.39331 | 0.38533 | 0.40784 | 0.42345 | 0.60493 | 0.41856 | 0.40113
42810.4385 | -132 | 18.4105 | 18.5491 | 18.5509 | 18.5565 | 17.9124 | 16.5565 | 14.622 | 16.6904 | 17.1806 | 17.2758 | 17.272 | 16.815 | 15.8393 | 14.4527 | 14.819 | 14.8661 | 15.4372 | 13.3135 | 13.4377 | 14.0064 |  |  |  | 16.5728 | 15.9007 | 15.0109 | 10.5941 | 10.1117 | 10.6496 | 17.0797 | 16.2502 | 15.0588 | 16.8211 | 16.1147 | 15.1108 | 10.775 | 12.1091 |  | 12.0207 | 10.8723 | 10.6022 | 8.9231 |  | 6.416 | 6.4581 | 5.9887 | 6.1122 | 6.0764 | 6.2374 | 6.6466 | 4.819 | 6.4729 | 4.3487 | 6.6892 | 8.0018 | 43.1848 | 47.445 | 43.7297 | 15.2157 |  |  | 0.23612 | 0.070399 | 0.068876 | 0.16034 | -0.045832 | -0.16277 | 0.22529 | 0.26202 | 0.97477 | -0.41453 | -0.42195 | 8.8688 | 8.8704 | 2.0084 | 15.6601 | 16.6168 | 17.1875 | 17.5272 | 17.4984 | 16.4822 | 14.8426 | 16.8359 | 17.1835 | 17.481 | 17.5309 | 17.2735 | 16.4838 | 14.7293 | 5.8387 | 8.0017 | 5.3198 | 5.416 | 5.6665 | 6.5862 | 7.6467 | 15.6903 | 15.3963 | 15.2828 | 14.2319 | 14.1243 | 14.0733 |  |  |  | 10.6475 | 9.6693 | 9.3375 | 9.5045 | -0.22909 | -0.11045 | 12.7159 |  |  | 10.5764 |  |  | 16.856 | 16.0509 | 15.0194 | 16.3578 | 15.641 | 14.75 | 10.6229 | 10.8978 | 11.3331 | 11.3457 | 9.5574 |  | 10.4938 | 9.0924 | 9.8895 | 9.535 | 10.9567 | 12.2407 |  | 12.1754 |  |  | 11.7496 | 12.442 | 12.5413 | [6 empty] | 12.5344 |  |  | 11.4838 |  |  | 9.3473 | 10.2294 | 11.6399 | 7.5971 | 9.2133 | 12.5045 | 8.127 | 9.6689 | 12.3578 | 9.2722 | 10.5122 | 7.7294 | 10.4842 | 8.4809 | 10.4081 | 7.8451 | 9.5568 | 13.0496 | 10.4954 | 10.2142 | 11.6595 | 8.2333 | 9.8153 | 12.6142 | 7.9934 | 10.6263 | 9.8032 | 10.1862 | 8.4977 | 10.7837 | 0.14367 | 20.9505 | 0.035496 | 0.048992 | -37.7562 | 3.1201 | 14.03 | 0.29 | 0.57048 | 0.30919 | 0.30583 | 0.46662 | -0.24938 | -0.46995 | 0.5529 | 0.39302 | 0.38603 | 0.4089 | 0.43026 | 0.61104 | 0.41991 | 0.39955
42810.4385 | -131 | 18.3934 | 18.535 | 18.535 | 18.5398 | 17.8874 | 16.5344 | 14.6098 | 16.674 | 17.1661 | 17.2552 | 17.2637 | 16.8051 | 15.8306 | 14.4461 | 14.8189 | 14.8609 | 15.4372 | 13.3154 | 13.4422 | 14.0088 |  |  |  | 16.568 | 15.9072 | 15.0132 | 10.5998 | 10.1222 | 10.6369 | 17.0689 | 16.2418 | 15.0558 | 16.8141 | 16.1149 | 15.1048 | 10.7676 | 12.143 |  | 12.0036 | 10.8751 | 10.605 | 8.8788 |  | 6.4035 | 6.4576 | 5.9852 | 6.0993 | 6.0583 | 6.2185 | 6.6201 | 4.7396 | 6.4649 | 4.335 | 6.6846 | 7.9913 | 43.1993 | 47.43 | 43.7274 | 15.2339 |  |  | -0.15814 | -0.077453 | 0.085304 | 0.019714 | -0.010348 | 0.000856 | 0.23778 | -0.070476 | -0.22592 | -0.99777 | -0.43904 | 8.8719 | 8.8729 | 2.0083 | 15.6617 | 16.621 | 17.1886 | 17.5316 | 17.4993 | 16.4861 | 14.8407 | 16.8307 | 17.1804 | 17.4851 | 17.5341 | 17.2697 | 16.4875 | 14.7295 | 5.8029 | 7.9986 | 5.245 | 5.4341 | 5.668 | 6.5786 | 7.6391 | 15.6848 | 15.3857 | 15.279 | 14.2271 | 14.1216 | 14.0766 |  |  |  | 10.6468 | 9.666 | 9.3354 | 9.5048 | -0.35065 | -0.16427 | 12.7131 |  |  | 10.5832 |  |  | 16.8523 | 16.0457 | 15.016 | 16.3603 | 15.6483 | 14.751 | 10.6258 | 10.8913 | 11.336 | 11.349 | 9.5756 |  | 10.4289 | 9.0332 | 9.8962 | 9.528 | 10.9797 | 12.2306 |  | 12.1858 |  |  | 11.7437 | 12.4058 | 12.5225 | [6 empty] | 12.5377 |  |  | 11.4527 |  |  | 9.3498 | 10.2167 | 11.6444 | 7.5972 | 9.2227 | 12.5088 | 8.127 | 9.6674 | 12.348 | 9.2662 | 10.5129 | 7.733 | 10.4875 | 8.4899 | 10.411 | 7.8221 | 9.5088 | 13.0504 | 10.492 | 10.2092 | 11.6494 | 8.2324 | 9.8087 | 12.6133 | 7.9679 | 10.64 | 9.8117 | 10.191 | 8.5017 | 10.7845 | -0.06723 | 20.9522 | 0.035611 | 0.048609 | -37.8251 | 3.1201 | 3.63 | 0.27 | -0.46686 | -0.32431 | 0.34035 | 0.16362 | -0.11849 | 0.034079 | 0.56799 | 0.39037 | 0.3879 | 0.40985 | 0.43335 | 0.61846 | 0.42089 | 0.39952
42810.4385 | -130 | 18.3983 | 18.5445 | 18.5449 | 18.5522 | 17.8929 | 16.5449 | 14.6057 | 16.6883 | 17.1775 | 17.2718 | 17.268 | 16.8075 | 15.834 | 14.4441 | 14.8187 | 14.864 | 15.443 | 13.3135 | 13.4358 | 14.012 |  |  |  | 16.579 | 15.91 | 15.0189 | 10.6043 | 10.1249 | 10.6379 | 17.0737 | 16.2402 | 15.0573 | 16.819 | 16.1165 | 15.1085 | 10.7704 | 12.1604 |  | 12.0083 | 10.8747 | 10.6093 | 8.8434 |  | 6.4033 | 6.4479 | 5.9793 | 6.0989 | 6.0539 | 6.2038 | 6.5861 | 4.7701 | 6.476 | 4.3772 | 6.6911 | 7.9951 | 43.2084 | 47.416 | 43.7295 | 15.2454 |  |  | -0.040521 | 0.18277 | 0.035364 | 0.19845 | -0.093148 | -0.10494 | 0.44608 | 0.18186 | -0.2086 | 0.62272 | -0.39055 | 8.8682 | 8.8692 | 2.008 | 15.6554 | 16.6161 | 17.1792 | 17.5275 | 17.4979 | 16.4864 | 14.8401 | 16.8263 | 17.1751 | 17.4804 | 17.5391 | 17.2727 | 16.4891 | 14.7216 | 5.7899 | 8.0086 | 5.3111 | 5.4199 | 5.6714 | 6.5719 | 7.6373 | 15.6895 | 15.3917 | 15.2735 | 14.2268 | 14.1226 | 14.0747 |  |  |  | 10.6413 | 9.6646 | 9.3389 | 9.5197 | -0.27123 | -0.18479 | 12.7172 |  |  | 10.5837 |  |  | 16.8527 | 16.0511 | 15.0203 | 16.3619 | 15.6542 | 14.7565 | 10.6173 | 10.8802 | 11.3306 | 11.3653 | 9.5556 |  | 10.444 | 8.9087 | 9.8992 | 9.5049 | 10.954 | 12.2825 |  | 12.1807 |  |  | 11.7295 | 12.4264 | 12.5388 | [6 empty] | 12.5431 |  |  | 11.4374 |  |  | 9.3384 | 10.2188 | 11.6448 | 7.6243 | 9.2193 | 12.5092 | 8.1136 | 9.659 | 12.3441 | 9.2652 | 10.5189 | 7.7375 | 10.5284 | 8.4727 | 10.4019 | 7.7779 | 9.5012 | 13.0371 | 10.4918 | 10.2122 | 11.6529 | 8.2315 | 9.8137 | 12.6123 | 7.9788 | 10.6436 | 9.8154 | 10.1924 | 8.4982 | 10.7833 | -0.20436 | 20.9522 | 0.035892 | 0.048327 | -37.769 | 3.12 | 8.8 | 0.31 | -0.23632 | 0.49818 | 0.21914 | 0.51911 | -0.35549 | -0.37732 | 0.77795 | 0.39143 | 0.39145 | 0.40965 | 0.43402 | 0.61092 | 0.42197 | 0.39893
42810.4385 | -129 | 18.3917 | 18.5402 | 18.5426 | 18.5439 | 17.8931 | 16.5408 | 14.6119 | 16.6803 | 17.173 | 17.2672 | 17.2735 | 16.8173 | 15.8347 | 14.4491 | 14.8241 | 14.8648 | 15.4283 | 13.3113 | 13.4411 | 14.0017 |  |  |  | 16.5674 | 15.9063 | 15.0063 | 10.6083 | 10.1294 | 10.6367 | 17.0761 | 16.2399 | 15.0566 | 16.8235 | 16.1083 | 15.1064 | 10.7739 | 12.1562 |  | 12.013 | 10.8849 | 10.6091 | 8.8368 |  | 6.4004 | 6.437 | 5.9729 | 6.0955 | 6.044 | 6.1961 | 6.5617 | 4.8256 | 6.4777 | 4.4635 | 6.6881 | 7.9919 | 43.1976 | 47.3732 | 43.7262 | 15.2261 |  |  | 0.086303 | 0.11508 | 0.21476 | 0.11959 | -0.10629 | 0.024512 | 0.52165 | -0.13422 | -0.47208 | -0.65433 | -0.38718 | 8.8696 | 8.8707 | 2.0085 | 15.6505 | 16.6084 | 17.1763 | 17.5249 | 17.4898 | 16.4766 | 14.8405 | 16.8294 | 17.1714 | 17.4748 | 17.5291 | 17.2766 | 16.4857 | 14.7182 | 5.7712 | 8.0386 | 5.2955 | 5.4246 | 5.6447 | 6.5737 | 7.633 | 15.6951 | 15.3933 | 15.2767 | 14.2319 | 14.1264 | 14.0768 |  |  |  | 10.6525 | 9.6818 | 9.3529 | 9.5363 | -0.42744 | -0.31182 | 12.7222 |  |  | 10.5646 |  |  | 16.8597 | 16.0562 | 15.0271 | 16.3629 | 15.6532 | 14.7612 | 10.606 | 10.875 | 11.3431 | 11.3823 | 9.5179 |  | 10.4764 | 8.6931 | 9.8944 | 9.4753 | 10.9504 | 12.268 |  | 12.1734 |  |  | 11.6815 | 12.3921 | 12.5483 | [6 empty] | 12.5353 |  |  | 11.4185 |  |  | 9.3489 | 10.2192 | 11.6421 | 7.6162 | 9.2334 | 12.5065 | 8.1083 | 9.656 | 12.3442 | 9.2838 | 10.5263 | 7.7616 | 10.5164 | 8.4884 | 10.4181 | 7.7897 | 9.5174 | 13.0241 | 10.5005 | 10.224 | 11.6642 | 8.2379 | 9.818 | 12.6262 | 8.0038 | 10.653 | 9.8421 | 10.2015 | 8.51 | 10.7778 | -0.28641 | 20.9523 | 0.035972 | 0.049557 | -37.8133 | 3.1201 | 7.06 | 0.36 | 0.34489 | 0.3953 | 0.54001 | 0.40298 | -0.37973 | 0.18236 | 0.84126 | 0.39354 | 0.39728 | 0.41035 | 0.4363 | 0.61215 | 0.42227 | 0.39884
42810.4386 | -128 | 18.3848 | 18.5413 | 18.5352 | 18.5503 | 17.9034 | 16.5401 | 14.6103 | 16.6803 | 17.1776 | 17.2723 | 17.2754 | 16.8175 | 15.8344 | 14.4501 | 14.8079 | 14.852 | 15.4291 | 13.2983 | 13.43 | 13.995 |  |  |  | 16.5677 | 15.8949 | 14.9984 | 10.6008 | 10.1303 | 10.6175 | 17.0689 | 16.2396 | 15.0567 | 16.8194 | 16.1083 | 15.1086 | 10.7796 | 12.1611 |  | 12.0142 | 10.8811 | 10.5996 | 8.8666 |  | 6.39 | 6.4243 | 5.9681 | 6.0827 | 6.0502 | 6.212 | 6.5419 | 4.7809 | 6.4756 | 4.4895 | 6.6858 | 8.0009 | 43.1711 | 47.3439 | 43.7265 | 15.2233 |  |  | 0.052787 | 0.074999 | 0.16744 | -0.17479 | 0.089532 | -0.28959 | 0.54399 | -0.23607 | -0.062451 | -0.35788 | -0.3532 | 8.8706 | 8.8715 | 2.0083 | 15.6433 | 16.6109 | 17.1733 | 17.5273 | 17.503 | 16.4806 | 14.8413 | 16.8329 | 17.175 | 17.473 | 17.5373 | 17.2784 | 16.4888 | 14.723 | 5.7063 | 7.9925 | 5.2096 | 5.473 | 5.6101 | 6.5657 | 7.6346 | 15.698 | 15.3924 | 15.2791 | 14.2271 | 14.1319 | 14.0882 |  |  |  | 10.6542 | 9.6812 | 9.35 | 9.5274 | -0.32391 | -0.40668 | 12.7236 |  |  | 10.5503 |  |  | 16.8611 | 16.0542 | 15.0263 | 16.3604 | 15.6579 | 14.7613 | 10.5886 | 10.8771 | 11.3507 | 11.3925 | 9.5042 |  | 10.4888 | 8.5209 | 9.8938 | 9.4527 | 10.9479 | 12.2787 |  | 12.1803 |  |  | 11.6715 | 12.3924 | 12.5527 | [6 empty] | 12.5396 |  |  | 11.3997 |  |  | 9.3373 | 10.2088 | 11.6446 | 7.6218 | 9.2446 | 12.5097 | 8.0938 | 9.6607 | 12.3357 | 9.2684 | 10.514 | 7.7821 | 10.5323 | 8.4725 | 10.4222 | 7.8254 | 9.5278 | 13.0352 | 10.501 | 10.2294 | 11.6731 | 8.2422 | 9.8361 | 12.6301 | 8.0387 | 10.6808 | 9.8543 | 10.2062 | 8.5186 | 10.7951 | -0.18915 | 20.9513 | 0.035978 | 0.049094 | -37.7487 | 3.12 | 6.27 | 0.29 | 0.26972 | 0.31911 | 0.47682 | -0.48717 | 0.34853 | -0.62682 | 0.85911 | 0.39433 | 0.40205 | 0.4109 | 0.44258 | 0.62188 | 0.42163 | 0.39914
42810.4386 | -127 | 18.3923 | 18.5463 | 18.5363 | 18.5529 | 17.9006 | 16.5478 | 14.6138 | 16.6849 | 17.1704 | 17.2691 | 17.2756 | 16.8163 | 15.8392 | 14.452 | 14.8132 | 14.8567 | 15.4334 | 13.3077 | 13.435 | 14.0022 |  |  |  | 16.5745 | 15.9136 | 15.0112 | 10.6041 | 10.1505 | 10.6117 | 17.0669 | 16.2335 | 15.0536 | 16.8148 | 16.1085 | 15.1033 | 10.7782 | 12.1596 |  | 12.0157 | 10.8763 | 10.5935 | 8.8693 |  | 6.3749 | 6.4169 | 5.9684 | 6.0746 | 6.0815 | 6.2548 | 6.5295 | 4.7388 | 6.4721 | 4.4894 | 6.6892 | 7.9898 | 43.1269 | 47.3299 | 43.7155 | 15.2296 |  |  | -0.10163 | 0.16765 | -0.18411 | -0.20173 | 0.020536 | 0.13885 | 0.4566 | -0.46409 | -0.5003 | -0.32264 | -0.32121 | 8.8683 | 8.8693 | 2.0086 | 15.6442 | 16.6083 | 17.1728 | 17.5219 | 17.4948 | 16.4894 | 14.8401 | 16.832 | 17.1754 | 17.4737 | 17.5355 | 17.2715 | 16.4867 | 14.7163 | 5.6876 | 7.9903 | 5.1889 | 5.4627 | 5.6324 | 6.5663 | 7.6297 | 15.6892 | 15.3842 | 15.2789 | 14.2248 | 14.1224 | 14.0719 |  |  |  | 10.6576 | 9.6736 | 9.3521 | 9.5532 | -0.18715 | -0.28284 | 12.7146 |  |  | 10.5325 |  |  | 16.8518 | 16.0442 | 15.0255 | 16.3587 | 15.6499 | 14.758 | 10.5624 | 10.8613 | 11.3504 | 11.3989 | 9.4874 |  | 10.4804 | 8.3944 | 9.8873 | 9.4346 | 10.9456 | 12.2963 |  | 12.1831 |  |  | 11.6177 | 12.3987 | 12.5574 | [6 empty] | 12.5325 |  |  | 11.3765 |  |  | 9.3447 | 10.2164 | 11.6533 | 7.6041 | 9.2478 | 12.5142 | 8.0789 | 9.652 | 12.3407 | 9.262 | 10.542 | 7.7962 | 10.5382 | 8.4817 | 10.427 | 7.8332 | 9.5377 | 13.026 | 10.495 | 10.2352 | 11.6833 | 8.2447 | 9.8302 | 12.6312 | 8.0503 | 10.6852 | 9.8653 | 10.2178 | 8.5195 | 10.7833 | -0.073585 | 20.9525 | 0.035743 | 0.048464 | -37.7491 | 3.1201 | 17.66 | 0.19 | -0.37425 | 0.4771 | -0.49998 | -0.52336 | 0.16693 | 0.43406 | 0.78714 | 0.39452 | 0.40535 | 0.41133 | 0.44474 | 0.62361 | 0.42151 | 0.39854
42810.4386 | -126 | 18.3846 | 18.5405 | 18.5355 | 18.5376 | 17.8933 | 16.5384 | 14.6092 | 16.6815 | 17.1645 | 17.2606 | 17.2702 | 16.8067 | 15.8341 | 14.4452 | 14.8167 | 14.8612 | 15.4356 | 13.3066 | 13.4359 | 13.9994 |  |  |  | 16.5696 | 15.9073 | 15.0075 | 10.6119 | 10.1482 | 10.5852 | 17.0602 | 16.2363 | 15.0555 | 16.816 | 16.1086 | 15.1073 | 10.7749 | 12.1793 |  | 12.0113 | 10.8758 | 10.6002 | 8.8864 |  | 6.3555 | 6.4021 | 5.9519 | 6.071 | 6.0916 | 6.2354 | 6.5247 | 4.6674 | 6.4618 | 4.4902 | 6.6808 | 7.985 | 43.0917 | 47.3157 | 43.7151 | 15.2333 |  |  | 0.22101 | -0.20887 | 0.018936 | -0.028914 | 0.11516 | -0.18117 | 0.56568 | -0.26038 | -0.92978 | -0.172 | -0.39175 | 8.8706 | 8.8719 | 2.0081 | 15.6434 | 16.6006 | 17.1734 | 17.5244 | 17.4962 | 16.4851 | 14.8415 | 16.8262 | 17.1736 | 17.4854 | 17.5306 | 17.2698 | 16.4814 | 14.722 | 5.641 | 7.9726 | 5.1837 | 5.3792 | 5.6553 | 6.5569 | 7.6152 | 15.6864 | 15.3802 | 15.2669 | 14.2224 | 14.1166 | 14.0632 |  |  |  | 10.6508 | 9.6748 | 9.3456 | 9.5487 | -0.12698 | -0.30448 | 12.7123 |  |  | 10.5227 |  |  | 16.8529 | 16.0467 | 15.0328 | 16.3685 | 15.6562 | 14.7574 | 10.5462 | 10.8563 | 11.3667 | 11.4153 | 9.4493 |  | 10.4835 | 8.2792 | 9.8883 | 9.4195 | 10.9457 | 12.3184 |  | 12.1838 |  |  | 11.565 | 12.3843 | 12.5497 | [6 empty] | 12.5326 |  |  | 11.3417 |  |  | 9.3453 | 10.2255 | 11.6543 | 7.5803 | 9.2545 | 12.5223 | 8.0651 | 9.6565 | 12.3317 | 9.2734 | 10.5493 | 7.7711 | 10.5522 | 8.4893 | 10.4266 | 7.8354 | 9.5652 | 13.0346 | 10.4915 | 10.2375 | 11.6807 | 8.232 | 9.8465 | 12.6245 | 8.0571 | 10.6959 | 9.8788 | 10.2204 | 8.5207 | 10.7629 | -0.10729 | 20.9504 | 0.036712 | 0.048833 | -37.7735 | 3.12 | 15.54 | 0.28 | 0.55186 | -0.53252 | 0.16034 | -0.19813 | 0.39529 | -0.4958 | 0.8761 | 0.39568 | 0.40858 | 0.41175 | 0.44882 | 0.6225 | 0.42092 | 0.39843
42810.4386 | -125 | 18.3866 | 18.5417 | 18.5443 | 18.5432 | 17.8979 | 16.5441 | 14.6144 | 16.6828 | 17.1712 | 17.2647 | 17.2653 | 16.8075 | 15.8364 | 14.4494 | 14.807 | 14.8554 | 15.4243 | 13.3076 | 13.4324 | 13.9958 |  |  |  | 16.5612 | 15.9021 | 15.0055 | 10.6165 | 10.1421 | 10.5624 | 17.055 | 16.2356 | 15.0587 | 16.8158 | 16.1129 | 15.1059 | 10.7783 | 12.2053 |  | 12.0181 | 10.8853 | 10.6134 | 8.9092 |  | 6.3404 | 6.3935 | 5.9502 | 6.0754 | 6.0923 | 6.2395 | 6.6111 | 4.6823 | 6.4588 | 4.4346 | 6.6805 | 7.9834 | 43.0578 | 47.2924 | 43.7107 | 15.2376 |  |  | 0.071843 | 0.000747 | -0.008008 | -0.090026 | 0.046164 | -0.070772 | 0.49471 | -0.19533 | -0.33431 | -0.5209 | -0.35181 | 8.8678 | 8.869 | 2.0081 | 15.6603 | 16.6076 | 17.1821 | 17.5253 | 17.5008 | 16.4841 | 14.8483 | 16.8395 | 17.1782 | 17.4877 | 17.5394 | 17.2771 | 16.4812 | 14.7338 | 5.6479 | 7.985 | 5.231 | 5.3211 | 5.6725 | 6.5604 | 7.6246 | 15.69 | 15.3846 | 15.2723 | 14.2241 | 14.1248 | 14.074 |  |  |  | 10.6574 | 9.6763 | 9.3542 | 9.5293 | -0.036217 | -0.29695 | 12.7115 |  |  | 10.5093 |  |  | 16.8586 | 16.0497 | 15.0289 | 16.3653 | 15.657 | 14.7635 | 10.5349 | 10.855 | 11.3771 | 11.4267 | 9.4311 |  | 10.4912 | 8.1777 | 9.8904 | 9.4294 | 10.9427 | 12.3542 |  | 12.1865 |  |  | 11.5448 | 12.3783 | 12.5355 | [6 empty] | 12.5356 |  |  | 11.348 |  |  | 9.3379 | 10.2277 | 11.6507 | 7.5464 | 9.2606 | 12.5151 | 8.0284 | 9.6327 | 12.332 | 9.2668 | 10.5443 | 7.7411 | 10.5444 | 8.4657 | 10.4173 | 7.8432 | 9.589 | 13.0428 | 10.4933 | 10.258 | 11.6953 | 8.2431 | 9.8514 | 12.6282 | 8.0728 | 10.7102 | 9.8947 | 10.2265 | 8.5214 | 10.7706 | 0.049101 | 20.9518 | 0.036007 | 0.048935 | -37.7398 | 3.12 | 1.94 | 0.3 | 0.31463 | 0.031846 | -0.10427 | -0.3496 | 0.25028 | -0.30989 | 0.81931 | 0.39644 | 0.41147 | 0.41137 | 0.44846 | 0.61834 | 0.4204 | 0.39919
42810.4386 | -124 | 18.3843 | 18.54 | 18.5433 | 18.5486 | 17.9057 | 16.5401 | 14.6117 | 16.6814 | 17.1698 | 17.2664 | 17.2708 | 16.807 | 15.8365 | 14.4526 | 14.8009 | 14.852 | 15.4244 | 13.303 | 13.4286 | 13.9961 |  |  |  | 16.5572 | 15.9015 | 14.9959 | 10.6086 | 10.1328 | 10.5456 | 17.0588 | 16.2306 | 15.0488 | 16.805 | 16.1026 | 15.1002 | 10.7688 | 12.215 |  | 12.0045 | 10.8945 | 10.6084 | 8.9056 |  | 6.3407 | 6.3988 | 5.9526 | 6.0768 | 6.1203 | 6.2524 | 6.6901 | 4.7321 | 6.4599 | 4.4464 | 6.6873 | 7.9898 | 43.0387 | 47.2605 | 43.7149 | 15.2429 |  |  | 0.12902 | -0.039997 | 0.06362 | 0.093966 | 0.050104 | 0.012684 | 0.48025 | -0.46343 | -0.059338 | 0.051858 | -0.56203 | 8.8691 | 8.8701 | 2.0084 | 15.6519 | 16.6097 | 17.1794 | 17.5266 | 17.5003 | 16.4831 | 14.8468 | 16.8343 | 17.1734 | 17.4816 | 17.5336 | 17.276 | 16.4861 | 14.7389 | 5.6942 | 8.0363 | 5.2424 | 5.2825 | 5.5662 | 6.5628 | 7.6196 | 15.6841 | 15.3806 | 15.2656 | 14.2197 | 14.1216 | 14.0725 |  |  |  | 10.6522 | 9.6788 | 9.3584 | 9.5122 | -0.073698 | -0.28529 | 12.7107 |  |  | 10.5022 |  |  | 16.8613 | 16.0531 | 15.0321 | 16.3694 | 15.6567 | 14.758 | 10.5151 | 10.8462 | 11.3839 | 11.4356 | 9.3991 |  | 10.4815 | 8.1178 | 9.8831 | 9.4334 | 10.9378 | 12.3713 |  | 12.1842 |  |  | 11.548 | 12.3825 | 12.5223 | [6 empty] | 12.5405 |  |  | 11.3518 |  |  | 9.3433 | 10.2402 | 11.6525 | 7.5576 | 9.2722 | 12.5259 | 8.0203 | 9.6402 | 12.3447 | 9.2706 | 10.5545 | 7.744 | 10.5492 | 8.4443 | 10.4252 | 7.8539 | 9.5914 | 13.0537 | 10.4974 | 10.2613 | 11.7005 | 8.2487 | 9.8692 | 12.6379 | 8.0945 | 10.715 | 9.8974 | 10.2325 | 8.5289 | 10.7664 | 0.078954 | 20.9529 | 0.036299 | 0.049347 | -37.8017 | 3.1201 | -0.28 | 0.21 | 0.42161 | -0.23303 | 0.2939 | 0.35718 | 0.26075 | 0.13119 | 0.80727 | 0.39701 | 0.41289 | 0.4111 | 0.44359 | 0.61649 | 0.42019 | 0.3995
42810.4386 | -123 | 18.3817 | 18.5348 | 18.539 | 18.5427 | 17.8979 | 16.5375 | 14.6153 | 16.6798 | 17.1671 | 17.2651 | 17.2744 | 16.8022 | 15.8341 | 14.4457 | 14.7983 | 14.8528 | 15.4209 | 13.2962 | 13.4291 | 14.0001 |  |  |  | 16.5613 | 15.8994 | 15.0037 | 10.6067 | 10.136 | 10.5086 | 17.0537 | 16.2172 | 15.0439 | 16.7974 | 16.0957 | 15.0942 | 10.7608 | 12.2257 |  | 12.0045 | 10.8825 | 10.6075 | 8.8904 |  | 6.3385 | 6.3922 | 5.953 | 6.1048 | 6.1707 | 6.3042 | 6.7958 | 4.7661 | 6.4583 | 4.4593 | 6.6834 | 7.9811 | 43.0189 | 47.2343 | 43.7185 | 15.236 |  |  | 0.086303 | -0.019625 | 0.11028 | 0.08017 | 0.081648 | 0.18485 | 0.51705 | -0.23738 | -1.1363 | -0.41516 | -0.44023 | 8.8711 | 8.8723 | 2.0083 | 15.6462 | 16.6081 | 17.175 | 17.5271 | 17.4959 | 16.481 | 14.8413 | 16.8375 | 17.1772 | 17.4781 | 17.5345 | 17.2788 | 16.4881 | 14.7257 | 5.7412 | 8.086 | 5.241 | 5.3168 | 5.4728 | 6.5642 | 7.6044 | 15.6787 | 15.3773 | 15.2651 | 14.217 | 14.1245 | 14.0729 |  |  |  | 10.6504 | 9.6828 | 9.3621 | 9.5229 | -0.040269 | -0.33177 | 12.7076 |  |  | 10.506 |  |  | 16.8569 | 16.0537 | 15.0315 | 16.3678 | 15.6553 | 14.7542 | 10.494 | 10.8416 | 11.3864 | 11.4402 | 9.3684 |  | 10.4769 | 8.1187 | 9.8843 | 9.4608 | 10.9372 | 12.3754 |  | 12.1783 |  |  | 11.563 | 12.3887 | 12.5095 | [6 empty] | 12.5588 |  |  | 11.3465 |  |  | 9.3341 | 10.2468 | 11.6519 | 7.5685 | 9.2804 | 12.5317 | 8.0099 | 9.6441 | 12.3301 | 9.2743 | 10.5531 | 7.735 | 10.5493 | 8.433 | 10.4164 | 7.8636 | 9.6001 | 13.0575 | 10.5017 | 10.2628 | 11.698 | 8.2469 | 9.8603 | 12.6317 | 8.1019 | 10.7214 | 9.895 | 10.2206 | 8.5412 | 10.7628 | -0.029673 | 20.9523 | 0.035467 | 0.049376 | -37.8126 | 3.12 | -0.13 | 0.25 | 0.34481 | -0.16323 | 0.38693 | 0.32991 | 0.33289 | 0.50088 | 0.8377 | 0.39772 | 0.41291 | 0.41032 | 0.43853 | 0.61489 | 0.42035 | 0.39914
42810.4386 | -122 | 18.3845 | 18.5318 | 18.543 | 18.5427 | 17.8983 | 16.5413 | 14.6141 | 16.6783 | 17.1681 | 17.2708 | 17.269 | 16.8109 | 15.8318 | 14.4571 | 14.7912 | 14.8436 | 15.4199 | 13.2975 | 13.4208 | 13.9959 |  |  |  | 16.5636 | 15.9015 | 15.0052 | 10.5973 | 10.1356 | 10.4564 | 17.0604 | 16.229 | 15.0432 | 16.8104 | 16.1066 | 15.1011 | 10.7613 | 12.2298 |  | 12.0116 | 10.8876 | 10.6165 | 8.9033 |  | 6.3201 | 6.3846 | 5.959 | 6.1358 | 6.1757 | 6.3198 | 6.8763 | 4.7666 | 6.4494 | 4.5063 | 6.676 | 7.9736 | 43.0158 | 47.2064 | 43.7206 | 15.2277 |  |  | 0.19341 | -0.096509 | 0.13656 | -0.067026 | 0.17102 | -0.16868 | 0.59656 | -0.2019 | -0.035596 | -0.48649 | -0.39632 | 8.868 | 8.8693 | 2.0082 | 15.6423 | 16.6059 | 17.1719 | 17.5194 | 17.4988 | 16.4731 | 14.8337 | 16.8348 | 17.1768 | 17.4827 | 17.5361 | 17.2792 | 16.4872 | 14.7211 | 5.768 | 8.144 | 5.2622 | 5.3646 | 5.4277 | 6.5602 | 7.6033 | 15.6734 | 15.3732 | 15.2722 | 14.222 | 14.117 | 14.0713 |  |  |  | 10.6539 | 9.6826 | 9.3591 | 9.5306 | 0.038543 | -0.23259 | 12.7088 |  |  | 10.5127 |  |  | 16.8588 | 16.0559 | 15.0273 | 16.3631 | 15.6586 | 14.7607 | 10.4774 | 10.8376 | 11.3957 | 11.4422 | 9.346 |  | 10.4871 | 8.1458 | 9.8848 | 9.5003 | 10.9432 | 12.4071 |  | 12.1933 |  |  | 11.5869 | 12.3752 | 12.4959 | [6 empty] | 12.5642 |  |  | 11.3409 |  |  | 9.3284 | 10.2452 | 11.652 | 7.566 | 9.2662 | 12.5308 | 7.9882 | 9.6367 | 12.3158 | 9.2722 | 10.5468 | 7.7096 | 10.5422 | 8.42 | 10.4123 | 7.8832 | 9.6222 | 13.0632 | 10.5139 | 10.2773 | 11.7112 | 8.2556 | 9.8662 | 12.6364 | 8.1175 | 10.7295 | 9.9068 | 10.2237 | 8.5486 | 10.7668 | 0.0007582 | 20.9532 | 0.035238 | 0.049796 | -37.7807 | 3.12 | 21.37 | 0.26 | 0.51614 | -0.36197 | 0.43057 | -0.30165 | 0.48178 | -0.47848 | 0.89984 | 0.39867 | 0.41217 | 0.40942 | 0.4351 | 0.61239 | 0.42001 | 0.39904
42810.4386 | -121 | 18.381 | 18.5363 | 18.5389 | 18.5374 | 17.8913 | 16.5411 | 14.6144 | 16.6794 | 17.1665 | 17.2651 | 17.2602 | 16.8066 | 15.8333 | 14.4559 | 14.7941 | 14.8395 | 15.4168 | 13.3012 | 13.4232 | 13.994 |  |  |  | 16.5683 | 15.9061 | 15.0038 | 10.5934 | 10.1342 | 10.4033 | 17.0574 | 16.2247 | 15.0505 | 16.8086 | 16.105 | 15.1024 | 10.7676 | 12.2327 |  | 12.009 | 10.8836 | 10.6291 | 8.8972 |  | 6.3255 | 6.3862 | 5.9902 | 6.1631 | 6.1758 | 6.3244 | 6.9327 | 4.7935 | 6.4617 | 4.4942 | 6.6827 | 7.9739 | 43.0385 | 47.1991 | 43.7198 | 15.22 |  |  | 0.092871 | 0.16962 | -0.098688 | 0.003286 | -0.15229 | 0.13885 | 0.63993 | -0.17956 | -0.25608 | -1.3628 | -0.33412 | 8.8702 | 8.8714 | 2.0085 | 15.64 | 16.6006 | 17.167 | 17.5168 | 17.4916 | 16.4746 | 14.8364 | 16.8305 | 17.1734 | 17.4822 | 17.5348 | 17.2727 | 16.4901 | 14.7265 | 5.8069 | 8.1789 | 5.3583 | 5.3788 | 5.4346 | 6.5528 | 7.5973 | 15.6708 | 15.3776 | 15.2743 | 14.2243 | 14.1207 | 14.0681 |  |  |  | 10.6565 | 9.6781 | 9.3643 | 9.4865 | 0.068528 | -0.14752 | 12.7062 |  |  | 10.518 |  |  | 16.8592 | 16.0564 | 15.0275 | 16.3641 | 15.6547 | 14.7576 | 10.4718 | 10.8257 | 11.4083 | 11.4263 | 9.2862 |  | 10.4829 | 8.1802 | 9.8817 | 9.5264 | 10.9495 | 12.4272 |  | 12.1937 |  |  | 11.6062 | 12.3708 | 12.4924 | [6 empty] | 12.5627 |  |  | 11.3375 |  |  | 9.3337 | 10.2488 | 11.6554 | 7.5642 | 9.233 | 12.5446 | 7.9869 | 9.6397 | 12.3177 | 9.2802 | 10.55 | 7.6961 | 10.538 | 8.4069 | 10.4232 | 7.894 | 9.6264 | 13.0528 | 10.5162 | 10.2803 | 11.7163 | 8.2598 | 9.875 | 12.6406 | 8.1259 | 10.7343 | 9.907 | 10.2195 | 8.5503 | 10.7589 | -0.050088 | 20.9538 | 0.035002 | 0.048623 | -37.7261 | 3.12 | 18.33 | 0.31 | 0.35762 | 0.47988 | -0.36603 | 0.066791 | -0.45464 | 0.43412 | 0.93198 | 0.40019 | 0.41112 | 0.4089 | 0.42991 | 0.60102 | 0.42038 | 0.40035
42810.4386 | -120 | 18.3811 | 18.5333 | 18.5441 | 18.5349 | 17.8881 | 16.5382 | 14.6092 | 16.6803 | 17.1688 | 17.2644 | 17.2635 | 16.8041 | 15.8279 | 14.4478 | 14.7919 | 14.8398 | 15.4163 | 13.3049 | 13.4313 | 14.001 |  |  |  | 16.5738 | 15.9162 | 15.0103 | 10.5902 | 10.1301 | 10.3252 | 17.0554 | 16.2233 | 15.0476 | 16.8039 | 16.1019 | 15.093 | 10.7623 | 12.2009 |  | 12.0095 | 10.8808 | 10.6266 | 8.8785 |  | 6.3136 | 6.38 | 5.992 | 6.1751 | 6.1708 | 6.3425 | 7.0281 | 4.8389 | 6.4516 | 4.4877 | 6.6748 | 7.974 | 43.0559 | 47.1812 | 43.7166 | 15.2086 |  |  | 0.091559 | 0.040171 | 0.089904 | 0.19976 | 0.13356 | -0.27908 | 0.6787 | -0.27681 | -0.37848 | 0.56608 | -0.28961 | 8.8694 | 8.8706 | 2.0084 | 15.6308 | 16.591 | 17.1707 | 17.5118 | 17.4873 | 16.4691 | 14.8263 | 16.8234 | 17.1591 | 17.475 | 17.5283 | 17.2649 | 16.4874 | 14.7097 | 5.8884 | 8.1908 | 5.4724 | 5.4526 | 5.4478 | 6.564 | 7.6026 | 15.6719 | 15.3758 | 15.2756 | 14.2199 | 14.1174 | 14.065 |  |  |  | 10.6542 | 9.6824 | 9.3672 | 9.4696 | -0.12435 | -0.11911 | 12.701 |  |  | 10.5151 |  |  | 16.8554 | 16.05 | 15.0224 | 16.3623 | 15.654 | 14.7521 | 10.4688 | 10.8131 | 11.4089 | 11.3906 | 9.2427 |  | 10.4864 | 8.1347 | 9.8848 | 9.5485 | 10.9539 | 12.4123 |  | 12.1917 |  |  | 11.6219 | 12.372 | 12.4807 | [6 empty] | 12.5773 |  |  | 11.3337 |  |  | 9.3334 | 10.2524 | 11.6527 | 7.5554 | 9.201 | 12.5474 | 7.9958 | 9.64 | 12.3209 | 9.284 | 10.556 | 7.6871 | 10.5305 | 8.3979 | 10.4228 | 7.9033 | 9.6302 | 13.0447 | 10.5263 | 10.2835 | 11.7253 | 8.2481 | 9.8786 | 12.6346 | 8.1402 | 10.7373 | 9.9082 | 10.2194 | 8.5563 | 10.7433 | -0.047584 | 20.9527 | 0.036334 | 0.049195 | -37.7364 | 3.12 | 2.86 | 0.19 | 0.35504 | 0.23353 | 0.34936 | 0.52076 | 0.42578 | -0.61548 | 0.95982 | 0.40152 | 0.41248 | 0.40843 | 0.42216 | 0.58897 | 0.42073 | 0.40075
42810.4387 | -119 | 18.3804 | 18.5288 | 18.5378 | 18.5348 | 17.8883 | 16.5376 | 14.6133 | 16.6764 | 17.173 | 17.2602 | 17.2637 | 16.8038 | 15.8303 | 14.4446 | 14.7944 | 14.8473 | 15.4222 | 13.299 | 13.4316 | 14.004 |  |  |  | 16.5771 | 15.9169 | 15.02 | 10.5792 | 10.1346 | 10.2526 | 17.0523 | 16.2226 | 15.0457 | 16.8064 | 16.1028 | 15.0903 | 10.7616 | 12.133 |  | 12.0109 | 10.8794 | 10.6328 | 8.8791 |  | 6.307 | 6.3656 | 5.9934 | 6.1714 | 6.1819 | 6.3858 | 7.1068 | 4.8683 | 6.4427 | 4.5059 | 6.6749 | 7.9728 | 43.0556 | 47.1648 | 43.72 | 15.2015 |  |  | 0.005475 | -0.18325 | 0.15759 | 0.11828 | 0.093476 | 0.21376 | 0.4934 | -0.23212 | -0.47598 | -0.30186 | -0.42652 | 8.8703 | 8.8716 | 2.0083 | 15.6346 | 16.593 | 17.164 | 17.5178 | 17.4878 | 16.4713 | 14.828 | 16.8286 | 17.1684 | 17.4695 | 17.5201 | 17.2748 | 16.4826 | 14.7231 | 6.2663 | 8.1838 | 5.5468 | 5.5656 | 5.4392 | 6.5639 | 7.5889 | 15.6818 | 15.3737 | 15.2666 | 14.2206 | 14.1147 | 14.0703 |  |  |  | 10.6629 | 9.6825 | 9.3659 | 9.4612 | -0.022845 | -0.018607 | 12.6924 |  |  | 10.5171 |  |  | 16.8526 | 16.0497 | 15.021 | 16.3623 | 15.648 | 14.7522 | 10.4897 | 10.8042 | 11.4119 | 11.3512 | 9.1667 |  | 10.4853 | 8.1134 | 9.867 | 9.5526 | 10.9446 | 12.3788 |  | 12.1891 |  |  | 11.6283 | 12.3955 | 12.4733 | [6 empty] | 12.5932 |  |  | 11.3334 |  |  | 9.3334 | 10.2617 | 11.6471 | 7.5475 | 9.1771 | 12.5506 | 7.986 | 9.6349 | 12.3164 | 9.2809 | 10.5564 | 7.6725 | 10.5225 | 8.3786 | 10.4232 | 7.9146 | 9.6368 | 13.0385 | 10.5391 | 10.2893 | 11.7304 | 8.2488 | 9.8757 | 12.6352 | 8.1545 | 10.7407 | 9.9127 | 10.2144 | 8.5608 | 10.7413 | 0.0076918 | 20.953 | 0.03584 | 0.049571 | -37.8017 | 3.12 | 9.93 | 0.29 | 0.086808 | -0.49876 | 0.46252 | 0.40071 | 0.35623 | 0.5387 | 0.81843 | 0.40359 | 0.41249 | 0.40801 | 0.38016 | 0.57911 | 0.42069 | 0.40127
42810.4387 | -118 | 18.3777 | 18.5311 | 18.5402 | 18.5383 | 17.8893 | 16.5359 | 14.613 | 16.6782 | 17.1794 | 17.2582 | 17.2646 | 16.8043 | 15.8347 | 14.4489 | 14.781 | 14.8402 | 15.411 | 13.2908 | 13.4222 | 13.9905 |  |  |  | 16.5687 | 15.9043 | 15.0128 | 10.5507 | 10.1193 | 10.1721 | 17.0542 | 16.2237 | 15.0466 | 16.8058 | 16.097 | 15.0946 | 10.7656 | 12.0519 |  | 12.0089 | 10.8727 | 10.6353 | 8.8948 |  | 6.2941 | 6.3637 | 5.9911 | 6.173 | 6.1969 | 6.4107 | 7.1073 | 4.9567 | 6.4374 | 4.5172 | 6.667 | 7.9754 | 43.0579 | 47.1492 | 43.7247 | 15.1954 |  |  | 0.010735 | 0.011915 | 0.020908 | 0.18399 | 0.2525 | 0.070508 | 0.57028 | -0.17167 | -0.17396 | -0.26326 | -0.55488 | 8.8686 | 8.8691 | 2.008 | 15.6358 | 16.5936 | 17.1683 | 17.5157 | 17.492 | 16.4731 | 14.8397 | 16.8296 | 17.1678 | 17.4777 | 17.5274 | 17.2842 | 16.4845 | 14.7206 | 6.596 | 8.2484 | 5.6468 | 5.6683 | 5.4349 | 6.5694 | 7.5997 | 15.6805 | 15.3818 | 15.2784 | 14.2223 | 14.1231 | 14.0723 |  |  |  | 10.6649 | 9.6865 | 9.3686 | 9.4447 | 0.1052 | 0.011129 | 12.6902 |  |  | 10.5275 |  |  | 16.8572 | 16.049 | 15.0249 | 16.3675 | 15.6508 | 14.7587 | 10.5283 | 10.8032 | 11.4222 | 11.3167 | 9.1403 |  | 10.4902 | 8.1632 | 9.8765 | 9.5639 | 10.9538 | 12.3827 |  | 12.2033 |  |  | 11.6125 | 12.3887 | 12.4468 | [6 empty] | 12.5848 |  |  | 11.3342 |  |  | 9.3414 | 10.2723 | 11.6525 | 7.5461 | 9.1699 | 12.5541 | 7.9883 | 9.6268 | 12.3089 | 9.2841 | 10.5663 | 7.6719 | 10.5252 | 8.381 | 10.431 | 7.9362 | 9.6539 | 13.0425 | 10.5496 | 10.3015 | 11.7385 | 8.2579 | 9.8835 | 12.6443 | 8.1708 | 10.7515 | 9.923 | 10.2137 | 8.5695 | 10.7455 | -0.046236 | 20.9534 | 0.034589 | 0.048956 | -37.8059 | 3.12 | 8.17 | 0.29 | 0.12154 | 0.12718 | 0.16847 | 0.49977 | 0.58551 | 0.3094 | 0.87993 | 0.40449 | 0.41142 | 0.408 | 0.34415 | 0.56924 | 0.42038 | 0.40179
42810.4387 | -117 | 18.3674 | 18.5315 | 18.5378 | 18.5392 | 17.8837 | 16.5334 | 14.6098 | 16.6815 | 17.1704 | 17.2629 | 17.2669 | 16.8085 | 15.83 | 14.4477 | 14.7853 | 14.8412 | 15.4119 | 13.2934 | 13.4219 | 14.0011 |  |  |  | 16.5746 | 15.9087 | 15.0178 | 10.5393 | 10.1088 | 10.1101 | 17.0627 | 16.2322 | 15.0485 | 16.8098 | 16.1068 | 15.1012 | 10.7665 | 11.965 |  | 12.0184 | 10.878 | 10.6382 | 8.9296 |  | 6.2968 | 6.3632 | 5.9808 | 6.1776 | 6.2208 | 6.4214 | 7.0696 | 5.0264 | 6.4402 | 4.5509 | 6.6687 | 7.9643 | 43.0418 | 47.1163 | 43.7139 | 15.1801 |  |  | -0.077321 | -0.056425 | 0.1589 | 0.025626 | 0.10728 | 0.25779 | 0.57816 | -0.19861 | -0.53358 | -0.42774 | -0.50759 | 8.8706 | 8.8719 | 2.0084 | 15.6355 | 16.602 | 17.1709 | 17.5201 | 17.4934 | 16.4731 | 14.8426 | 16.8321 | 17.1743 | 17.4813 | 17.5337 | 17.2809 | 16.4916 | 14.7338 | 6.6081 | 8.2662 | 5.7525 | 5.7274 | 5.4637 | 6.5754 | 7.5987 | 15.6748 | 15.3682 | 15.2714 | 14.217 | 14.1198 | 14.0622 |  |  |  | 10.66 | 9.6796 | 9.3617 | 9.4219 | 0.069135 | -0.13774 | 12.6875 |  |  | 10.5309 |  |  | 16.8488 | 16.0504 | 15.0244 | 16.3703 | 15.6527 | 14.7622 | 10.5514 | 10.8017 | 11.4185 | 11.287 | 9.1107 |  | 10.4884 | 8.2093 | 9.8713 | 9.5683 | 10.9545 | 12.383 |  | 12.1933 |  |  | 11.582 | 12.3655 | 12.4382 | [6 empty] | 12.5741 |  |  | 11.3268 |  |  | 9.3206 | 10.2747 | 11.6471 | 7.5404 | 9.1696 | 12.5503 | 7.9931 | 9.617 | 12.3048 | 9.2813 | 10.5667 | 7.6851 | 10.5244 | 8.3692 | 10.4276 | 7.9389 | 9.6568 | 13.0326 | 10.5449 | 10.2972 | 11.7384 | 8.2554 | 9.8827 | 12.6389 | 8.1811 | 10.7596 | 9.9236 | 10.2124 | 8.5692 | 10.7413 | 0.073754 | 20.9534 | 0.034159 | 0.048985 | -37.7907 | 3.12 | 7.31 | 0.3 | -0.32614 | -0.27676 | 0.46444 | 0.18651 | 0.38165 | 0.59162 | 0.88601 | 0.40525 | 0.40996 | 0.40791 | 0.3435 | 0.55739 | 0.41944 | 0.40226
42810.4387 | -116 | 18.3675 | 18.5288 | 18.5447 | 18.5407 | 17.8848 | 16.533 | 14.6079 | 16.6721 | 17.1606 | 17.2625 | 17.2601 | 16.8083 | 15.8294 | 14.4478 | 14.7866 | 14.8493 | 15.4202 | 13.2973 | 13.4228 | 13.993 |  |  |  | 16.5661 | 15.9087 | 15.0093 | 10.5237 | 10.1011 | 10.0433 | 17.0524 | 16.2234 | 15.0532 | 16.8011 | 16.1039 | 15.1042 | 10.7592 | 11.8813 |  | 12.0078 | 10.8739 | 10.6377 | 8.9615 |  | 6.2957 | 6.355 | 5.9758 | 6.1759 | 6.2283 | 6.4191 | 7.0275 | 4.9903 | 6.4461 | 4.5544 | 6.6761 | 7.9594 | 43.0024 | 47.0748 | 43.7039 | 15.162 |  |  | -0.008325 | -0.080081 | 0.22724 | -0.11762 | -0.057004 | -0.003744 | 0.51311 | -0.20453 | -0.25024 | 0.029199 | -0.5064 | 8.8703 | 8.8715 | 2.0085 | 15.6315 | 16.5941 | 17.1659 | 17.5113 | 17.4897 | 16.4691 | 14.8346 | 16.8297 | 17.1702 | 17.48 | 17.5326 | 17.277 | 16.4876 | 14.7283 | 6.4903 | 8.1942 | 5.8005 | 5.8001 | 5.5563 | 6.5737 | 7.5995 | 15.671 | 15.3727 | 15.2709 | 14.2214 | 14.1243 | 14.0657 |  |  |  | 10.6662 | 9.6751 | 9.356 | 9.4219 | -0.036217 | -0.28529 | 12.6859 |  |  | 10.5248 |  |  | 16.8456 | 16.0496 | 15.0246 | 16.3654 | 15.6522 | 14.7647 | 10.5743 | 10.7906 | 11.4265 | 11.2734 | 9.0649 |  | 10.4843 | 8.1919 | 9.8645 | 9.5877 | 10.9445 | 12.371 |  | 12.1937 |  |  | 11.5684 | 12.3556 | 12.4046 | [6 empty] | 12.5724 |  |  | 11.3193 |  |  | 9.3034 | 10.2651 | 11.6429 | 7.5194 | 9.1606 | 12.5466 | 7.9849 | 9.6179 | 12.307 | 9.2836 | 10.5591 | 7.7121 | 10.5186 | 8.3581 | 10.4219 | 7.9447 | 9.669 | 13.0302 | 10.5387 | 10.2925 | 11.7317 | 8.2568 | 9.8865 | 12.6355 | 8.1739 | 10.768 | 9.9242 | 10.2003 | 8.5605 | 10.7457 | -0.0036716 | 20.9535 | 0.034359 | 0.04866 | -37.8393 | 3.1199 | 19.12 | 0.39 | -0.107 | -0.32971 | 0.5554 | -0.39958 | -0.2782 | -0.071298 | 0.83467 | 0.40639 | 0.41022 | 0.40704 | 0.3564 | 0.55214 | 0.41832 | 0.40247
42810.4387 | -115 | 18.3738 | 18.5273 | 18.5409 | 18.5403 | 17.8906 | 16.534 | 14.6128 | 16.6763 | 17.1749 | 17.2599 | 17.2695 | 16.8163 | 15.8318 | 14.4478 | 14.7768 | 14.8446 | 15.4145 | 13.2909 | 13.4193 | 13.9969 |  |  |  | 16.5679 | 15.9025 | 15.0081 | 10.5118 | 10.0857 | 9.9896 | 17.0419 | 16.2189 | 15.0435 | 16.8032 | 16.0871 | 15.0805 | 10.7642 | 11.8014 |  | 12.0028 | 10.8596 | 10.6341 | 8.9645 |  | 6.271 | 6.3449 | 5.977 | 6.1666 | 6.242 | 6.4198 | 6.9918 | 4.8726 | 6.4465 | 4.6197 | 6.6662 | 7.9592 | 42.9737 | 47.0395 | 43.689 | 15.143 |  |  | 0.059359 | 0.080255 | 0.27652 | -0.044682 | -0.078032 | -0.27842 | 0.6373 | -0.05076 | -0.4355 | 0.42174 | -0.46308 | 8.8695 | 8.8707 | 2.0081 | 15.6345 | 16.5994 | 17.1714 | 17.5137 | 17.491 | 16.4737 | 14.8325 | 16.8328 | 17.1714 | 17.4822 | 17.5337 | 17.2788 | 16.4931 | 14.7267 | 6.3916 | 8.1847 | 5.7777 | 5.8582 | 5.6172 | 6.5792 | 7.5938 | 15.6678 | 15.3731 | 15.2667 | 14.2184 | 14.1199 | 14.067 |  |  |  | 10.6624 | 9.6693 | 9.3533 | 9.4181 | -0.23395 | -0.33666 | 12.6852 |  |  | 10.5178 |  |  | 16.851 | 16.0467 | 15.0248 | 16.3675 | 15.6517 | 14.7687 | 10.603 | 10.789 | 11.441 | 11.2767 | 9.0394 |  | 10.4931 | 8.1792 | 9.8701 | 9.6019 | 10.9582 | 12.3715 |  | 12.1969 |  |  | 11.5934 | 12.3738 | 12.3956 | [6 empty] | 12.59 |  |  | 11.2884 |  |  | 9.3025 | 10.2826 | 11.6493 | 7.5069 | 9.1547 | 12.5504 | 8.0032 | 9.6064 | 12.3104 | 9.2937 | 10.5623 | 7.7362 | 10.5125 | 8.3633 | 10.4313 | 7.9351 | 9.6677 | 13.0327 | 10.5449 | 10.2976 | 11.7438 | 8.2665 | 9.8824 | 12.632 | 8.1869 | 10.7779 | 9.93 | 10.1963 | 8.5596 | 10.7463 | 0.043323 | 20.9535 | 0.034032 | 0.047885 | -37.7982 | 3.1199 | 12.5 | 0.29 | 0.2857 | 0.33006 | 0.61266 | -0.24627 | -0.3255 | -0.61484 | 0.93022 | 0.40739 | 0.41076 | 0.40709 | 0.36801 | 0.55401 | 0.4184 | 0.40245
42810.4387 | -114 | 18.3717 | 18.5329 | 18.5424 | 18.5379 | 17.8928 | 16.539 | 14.6164 | 16.6844 | 17.1688 | 17.2619 | 17.2728 | 16.8036 | 15.8285 | 14.4489 | 14.7789 | 14.8425 | 15.4101 | 13.2976 | 13.4196 | 13.9817 |  |  |  | 16.5659 | 15.9103 | 15.011 | 10.499 | 10.0821 | 9.9631 | 17.0483 | 16.2217 | 15.0393 | 16.7969 | 16.0855 | 15.0839 | 10.7618 | 11.7356 |  | 11.9965 | 10.8557 | 10.6245 | 8.9775 |  | 6.2609 | 6.3358 | 5.9715 | 6.1718 | 6.2533 | 6.4073 | 6.977 | 4.7873 | 6.4486 | 4.6627 | 6.6609 | 7.9586 | 42.9511 | 47.0111 | 43.6762 | 15.137 |  |  | 0.079731 | 0.1256 | 0.061648 | 0.02957 | 0.11713 | -0.34676 | 0.55319 | -0.20058 | -0.39522 | -0.86161 | -0.37346 | 8.8667 | 8.8678 | 2.0085 | 15.6327 | 16.5969 | 17.1656 | 17.5076 | 17.4862 | 16.4665 | 14.8262 | 16.8293 | 17.1736 | 17.4783 | 17.5298 | 17.2726 | 16.49 | 14.7259 | 6.2952 | 8.2058 | 5.8406 | 5.9217 | 5.6678 | 6.5876 | 7.5921 | 15.6687 | 15.3656 | 15.2677 | 14.2191 | 14.1223 | 14.0684 |  |  |  | 10.6651 | 9.6707 | 9.3655 | 9.4131 | -0.36666 | -0.065092 | 12.6824 |  |  | 10.5142 |  |  | 16.8579 | 16.0493 | 15.0254 | 16.3646 | 15.6584 | 14.7646 | 10.6298 | 10.7823 | 11.4529 | 11.2828 | 9.0551 |  | 10.4933 | 8.1927 | 9.8708 | 9.5955 | 10.9528 | 12.378 |  | 12.1979 |  |  | 11.5926 | 12.3539 | 12.3848 | [6 empty] | 12.5877 |  |  | 11.2643 |  |  | 9.2896 | 10.2795 | 11.6401 | 7.5019 | 9.1488 | 12.554 | 7.9915 | 9.6094 | 12.305 | 9.2817 | 10.5587 | 7.7249 | 10.5113 | 8.3506 | 10.4242 | 7.9371 | 9.6781 | 13.0282 | 10.5416 | 10.2886 | 11.739 | 8.2588 | 9.8852 | 12.6278 | 8.1858 | 10.7823 | 9.9286 | 10.1996 | 8.5619 | 10.7328 | -0.015035 | 20.9534 | 0.03359 | 0.047357 | -37.7357 | 3.12 | 4.53 | 0.39 | 0.3311 | 0.4129 | 0.28927 | 0.20034 | 0.39879 | -0.68615 | 0.86664 | 0.40696 | 0.41041 | 0.40709 | 0.3797 | 0.54683 | 0.41796 | 0.40267
42810.4387 | -113 | 18.3588 | 18.5266 | 18.5397 | 18.5368 | 17.8907 | 16.5392 | 14.6155 | 16.6771 | 17.1629 | 17.2587 | 17.2686 | 16.8059 | 15.8303 | 14.4478 | 14.7818 | 14.8442 | 15.4158 | 13.2974 | 13.4258 | 14.0034 |  |  |  | 16.5723 | 15.9217 | 15.0124 | 10.4893 | 10.087 | 9.9407 | 17.0469 | 16.2178 | 15.0355 | 16.8068 | 16.0914 | 15.0848 | 10.7607 | 11.6971 |  | 12.0017 | 10.8579 | 10.6176 | 8.9905 |  | 6.2511 | 6.3121 | 5.9527 | 6.1633 | 6.2574 | 6.4153 | 6.9823 | 4.7397 | 6.4353 | 4.6574 | 6.6511 | 7.9548 | 42.9312 | 46.9804 | 43.6604 | 15.1223 |  |  | 0.060675 | 0.040831 | 0.18978 | -0.048626 | 0.058648 | -0.024116 | 0.52559 | -0.13947 | -0.013023 | -0.52929 | -0.46705 | 8.87 | 8.871 | 2.0083 | 15.629 | 16.5906 | 17.1656 | 17.5087 | 17.4878 | 16.4728 | 14.8263 | 16.8337 | 17.1765 | 17.4832 | 17.5369 | 17.2848 | 16.4902 | 14.738 | 6.204 | 8.2077 | 5.8296 | 5.9329 | 5.657 | 6.5845 | 7.5905 | 15.6611 | 15.3598 | 15.2547 | 14.2079 | 14.1155 | 14.0644 |  |  |  | 10.6534 | 9.6548 | 9.3471 | 9.3736 | -0.067012 | -0.1016 | 12.6709 |  |  | 10.514 |  |  | 16.8477 | 16.0507 | 15.0232 | 16.3645 | 15.6547 | 14.7575 | 10.6454 | 10.7763 | 11.4593 | 11.2932 | 9.0514 |  | 10.4908 | 8.2304 | 9.8676 | 9.5935 | 10.9551 | 12.4107 |  | 12.2004 |  |  | 11.5893 | 12.3402 | 12.3737 | [6 empty] | 12.5853 |  |  | 11.2707 |  |  | 9.2882 | 10.2822 | 11.6519 | 7.5254 | 9.1528 | 12.554 | 7.9999 | 9.6133 | 12.306 | 9.2974 | 10.5708 | 7.732 | 10.5097 | 8.3456 | 10.4194 | 7.9365 | 9.6831 | 13.0234 | 10.5438 | 10.2933 | 11.7243 | 8.257 | 9.8772 | 12.6128 | 8.2 | 10.7863 | 9.929 | 10.1992 | 8.5565 | 10.7304 | -0.073008 | 20.9546 | 0.03343 | 0.047625 | -37.7774 | 3.12 | 6.07 | 0.29 | 0.28882 | 0.23541 | 0.50753 | -0.2569 | 0.28219 | -0.18095 | 0.84476 | 0.40698 | 0.40926 | 0.40722 | 0.38946 | 0.54786 | 0.41757 | 0.40339
42810.4387 | -112 | 18.3616 | 18.5256 | 18.5358 | 18.5385 | 17.8922 | 16.5401 | 14.6115 | 16.6717 | 17.1638 | 17.2566 | 17.2652 | 16.8112 | 15.8333 | 14.4521 | 14.783 | 14.8333 | 15.4092 | 13.2957 | 13.4179 | 13.9882 |  |  |  | 16.5704 | 15.9125 | 15.0074 | 10.4747 | 10.0829 | 9.9288 | 17.0392 | 16.2126 | 15.0359 | 16.7958 | 16.0872 | 15.0863 | 10.7546 | 11.7003 |  | 12.0062 | 10.8488 | 10.6141 | 8.9972 |  | 6.2444 | 6.3139 | 5.9507 | 6.1757 | 6.2653 | 6.4275 | 6.9888 | 4.739 | 6.4428 | 4.6174 | 6.6619 | 7.9552 | 42.9247 | 46.9488 | 43.6397 | 15.1143 |  |  | 0.10536 | 0.065799 | 0.074132 | 0.078198 | -0.011664 | 0.1533 | 0.25355 | -0.05076 | -0.33878 | -0.72629 | -0.25246 | 8.8706 | 8.8721 | 2.0082 | 15.6294 | 16.5972 | 17.1725 | 17.5163 | 17.4857 | 16.4746 | 14.8381 | 16.8294 | 17.1772 | 17.4781 | 17.5401 | 17.2795 | 16.4934 | 14.725 | 6.1607 | 8.1588 | 5.8079 | 5.9576 | 5.6438 | 6.5919 | 7.5986 | 15.6606 | 15.3658 | 15.2602 | 14.2134 | 14.1187 | 14.0702 |  |  |  | 10.6671 | 9.6587 | 9.3555 | 9.3352 | -0.16649 | -0.28397 | 12.6658 |  |  | 10.5182 |  |  | 16.8513 | 16.0492 | 15.021 | 16.3663 | 15.6584 | 14.7749 | 10.6621 | 10.7749 | 11.4699 | 11.3039 | 9.0113 |  | 10.4811 | 8.2654 | 9.8638 | 9.5865 | 10.9499 | 12.4251 |  | 12.1907 |  |  | 11.6125 | 12.3185 | 12.3496 | [6 empty] | 12.5891 |  |  | 11.271 |  |  | 9.2874 | 10.2964 | 11.6679 | 7.4946 | 9.1324 | 12.5675 | 8.019 | 9.6226 | 12.3022 | 9.3048 | 10.5753 | 7.7151 | 10.5092 | 8.344 | 10.4318 | 7.9487 | 9.6876 | 13.0248 | 10.5475 | 10.305 | 11.7261 | 8.2659 | 9.8631 | 12.6044 | 8.2059 | 10.7949 | 9.9289 | 10.2103 | 8.5662 | 10.723 | -0.14985 | 20.9543 | 0.033367 | 0.048146 | -37.8252 | 3.12 | 8.39 | 0.28 | 0.38059 | 0.29884 | 0.3172 | 0.32578 | -0.12585 | 0.45624 | 0.58674 | 0.40777 | 0.40816 | 0.40725 | 0.39513 | 0.55122 | 0.41718 | 0.4049
42810.4388 | -111 | 18.3564 | 18.5277 | 18.5287 | 18.538 | 17.8926 | 16.5349 | 14.6113 | 16.6785 | 17.1681 | 17.2571 | 17.2625 | 16.8086 | 15.8329 | 14.4505 | 14.7771 | 14.8307 | 15.4047 | 13.2935 | 13.4088 | 13.9885 |  |  |  | 16.5612 | 15.9061 | 15.0092 | 10.4703 | 10.0696 | 9.9167 | 17.0331 | 16.2155 | 15.0363 | 16.7939 | 16.0903 | 15.0841 | 10.7584 | 11.7096 |  | 12.0056 | 10.8419 | 10.6131 | 8.9987 |  | 6.2429 | 6.3178 | 5.9605 | 6.1778 | 6.2726 | 6.4484 | 6.9816 | 4.8221 | 6.4454 | 4.6033 | 6.6627 | 7.9524 | 42.9254 | 46.9139 | 43.6187 | 15.1048 |  |  | -0.045777 | 0.11508 | 0.17204 | -0.14851 | 0.02842 | 0.19536 | 0.22004 | -0.25118 | -0.76885 | 0.46936 | -0.38201 | 8.8675 | 8.8688 | 2.0086 | 15.6297 | 16.6021 | 17.1717 | 17.5253 | 17.4973 | 16.4809 | 14.8422 | 16.8359 | 17.1941 | 17.4868 | 17.5415 | 17.288 | 16.4974 | 14.7383 | 6.0906 | 8.1456 | 5.7169 | 5.9779 | 5.6707 | 6.5876 | 7.5875 | 15.6558 | 15.3592 | 15.2546 | 14.2089 | 14.1082 | 14.0592 |  |  |  | 10.6568 | 9.6479 | 9.3444 | 9.282 | -0.21248 | -0.35831 | 12.6528 |  |  | 10.5133 |  |  | 16.8478 | 16.0442 | 15.0155 | 16.3573 | 15.6439 | 14.7617 | 10.6635 | 10.7632 | 11.47 | 11.308 | 8.9718 |  | 10.4912 | 8.2585 | 9.8609 | 9.5897 | 10.9517 | 12.4472 |  | 12.1917 |  |  | 11.6284 | 12.2834 | 12.3665 | [6 empty] | 12.597 |  |  | 11.2742 |  |  | 9.2901 | 10.3066 | 11.6762 | 7.4586 | 9.1021 | 12.5776 | 8.0162 | 9.6255 | 12.3107 | 9.3152 | 10.5826 | 7.6673 | 10.5083 | 8.3431 | 10.4362 | 7.9481 | 9.6904 | 13.0294 | 10.5498 | 10.3119 | 11.7196 | 8.261 | 9.8748 | 12.6097 | 8.2033 | 10.8103 | 9.9319 | 10.2223 | 8.5628 | 10.7165 | 0.2338 | 20.956 | 0.033458 | 0.047668 | -37.7391 | 3.1199 | 1.9 | 0.37 | -0.25086 | 0.39522 | 0.48323 | -0.44896 | 0.19645 | 0.51505 | 0.54661 | 0.4092 | 0.40825 | 0.40722 | 0.40243 | 0.56005 | 0.41726 | 0.40604
42810.4388 | -110 | 18.3501 | 18.5303 | 18.5252 | 18.533 | 17.8834 | 16.5277 | 14.6071 | 16.6761 | 17.1613 | 17.2536 | 17.2644 | 16.8064 | 15.8324 | 14.4508 | 14.7755 | 14.8324 | 15.4091 | 13.2933 | 13.414 | 13.9842 |  |  |  | 16.5672 | 15.9081 | 15.0091 | 10.4587 | 10.0645 | 9.9033 | 17.0298 | 16.2154 | 15.0341 | 16.8013 | 16.088 | 15.0876 | 10.7617 | 11.6848 |  | 12.008 | 10.8437 | 10.6181 | 8.9998 |  | 6.2206 | 6.3073 | 5.9459 | 6.152 | 6.2479 | 6.4232 | 6.9469 | 4.8139 | 6.4435 | 4.5698 | 6.6657 | 7.9506 | 42.9244 | 46.882 | 43.5975 | 15.0933 |  |  | -0.054977 | 0.017175 | 0.041276 | 0.20239 | 0.066532 | -0.1332 | -0.009956 | -0.054704 | -0.37537 | 0.32355 | -0.5515 | 8.8706 | 8.8717 | 2.0083 | 15.6271 | 16.5923 | 17.1673 | 17.5192 | 17.4881 | 16.4698 | 14.8324 | 16.831 | 17.1858 | 17.4797 | 17.5398 | 17.2818 | 16.4892 | 14.7334 | 6.1107 | 8.093 | 5.6463 | 5.9812 | 5.7167 | 6.5972 | 7.5875 | 15.6522 | 15.3568 | 15.2552 | 14.2013 | 14.1185 | 14.056 |  |  |  | 10.6533 | 9.6365 | 9.3387 | 9.2437 | -0.090919 | -0.2994 | 12.6523 |  |  | 10.5116 |  |  | 16.8449 | 16.0462 | 15.0167 | 16.3551 | 15.6383 | 14.7592 | 10.6715 | 10.7588 | 11.4768 | 11.3194 | 8.955 |  | 10.4847 | 8.3104 | 9.8659 | 9.5973 | 10.9508 | 12.4584 |  | 12.1968 |  |  | 11.6391 | 12.2795 | 12.3649 | [6 empty] | 12.5967 |  |  | 11.2624 |  |  | 9.2961 | 10.3039 | 11.6715 | 7.427 | 9.083 | 12.5721 | 8.0161 | 9.6235 | 12.3053 | 9.3011 | 10.5762 | 7.6262 | 10.5078 | 8.3289 | 10.4237 | 7.9551 | 9.6874 | 13.0461 | 10.5491 | 10.31 | 11.7156 | 8.2682 | 9.876 | 12.6128 | 8.1918 | 10.8061 | 9.9355 | 10.2231 | 8.5662 | 10.7043 | 0.005188 | 20.9539 | 0.033458 | 0.048146 | -37.7629 | 3.1199 | 16.22 | 0.33 | -0.27491 | 0.15268 | 0.23669 | 0.52411 | 0.30056 | -0.42527 | -0.11627 | 0.40945 | 0.40698 | 0.40697 | 0.40131 | 0.56789 | 0.41734 | 0.40699
42810.4388 | -109 | 18.3553 | 18.5233 | 18.5383 | 18.5457 | 17.8963 | 16.539 | 14.6097 | 16.6816 | 17.1755 | 17.262 | 17.2646 | 16.8082 | 15.8382 | 14.457 | 14.7728 | 14.8309 | 15.411 | 13.2907 | 13.4149 | 13.9888 |  |  |  | 16.5681 | 15.9119 | 15.0093 | 10.4544 | 10.059 | 9.8871 | 17.0397 | 16.208 | 15.0319 | 16.7904 | 16.0833 | 15.0828 | 10.7583 | 11.6343 |  | 12.0008 | 10.8402 | 10.6032 | 8.9985 |  | 6.2177 | 6.2983 | 5.9334 | 6.1389 | 6.2263 | 6.4126 | 6.9068 | 4.7257 | 6.434 | 4.5955 | 6.6574 | 7.9517 | 42.929 | 46.859 | 43.5782 | 15.1009 |  |  | 0.20064 | 0.13151 | 0.066248 | 0.02497 | -0.001808 | -0.089828 | 0.22858 | -0.058648 | -0.23817 | -0.76972 | -0.32776 | 8.8684 | 8.8697 | 2.0087 | 15.6278 | 16.5876 | 17.1662 | 17.5187 | 17.4829 | 16.4656 | 14.8375 | 16.8339 | 17.177 | 17.4782 | 17.5355 | 17.2764 | 16.4932 | 14.7354 | 6.1139 | 8.1203 | 5.6094 | 6.0908 | 5.7282 | 6.5978 | 7.5841 | 15.6487 | 15.3524 | 15.2548 | 14.2053 | 14.1091 | 14.0589 |  |  |  | 10.6598 | 9.642 | 9.328 | 9.2208 | -0.065594 | -0.29451 | 12.6544 |  |  | 10.5214 |  |  | 16.8544 | 16.0561 | 15.0179 | 16.3652 | 15.6436 | 14.7599 | 10.6788 | 10.7592 | 11.4817 | 11.3296 | 8.9704 |  | 10.4901 | 8.3879 | 9.8574 | 9.5953 | 10.953 | 12.4456 |  | 12.1953 |  |  | 11.652 | 12.2891 | 12.3818 | [6 empty] | 12.6062 |  |  | 11.2739 |  |  | 9.3014 | 10.3083 | 11.6665 | 7.407 | 9.0608 | 12.5686 | 8.0218 | 9.6274 | 12.3056 | 9.2976 | 10.5748 | 7.6073 | 10.5126 | 8.3328 | 10.4237 | 7.9598 | 9.6897 | 13.0475 | 10.5518 | 10.3111 | 11.7113 | 8.266 | 9.8684 | 12.6044 | 8.194 | 10.7997 | 9.9305 | 10.2181 | 8.5628 | 10.6966 | 0.016551 | 20.9554 | 0.033791 | 0.047632 | -37.7669 | 3.1199 | 22.94 | 0.32 | 0.52517 | 0.42247 | 0.29985 | 0.18409 | -0.049546 | -0.34923 | 0.55709 | 0.4092 | 0.40455 | 0.4071 | 0.40103 | 0.57159 | 0.41726 | 0.40784
42810.4388 | -108 | 18.3604 | 18.5191 | 18.5348 | 18.5362 | 17.8835 | 16.5284 | 14.605 | 16.6707 | 17.1671 | 17.2598 | 17.2584 | 16.8021 | 15.8269 | 14.451 | 14.7641 | 14.8315 | 15.4104 | 13.2911 | 13.4228 | 13.9941 |  |  |  | 16.5711 | 15.9116 | 15.0091 | 10.4466 | 10.0582 | 9.8584 | 17.042 | 16.2122 | 15.0348 | 16.7941 | 16.0932 | 15.0883 | 10.7607 | 11.5771 |  | 12.0011 | 10.8417 | 10.6169 | 8.9987 |  | 6.2072 | 6.2892 | 5.9155 | 6.1084 | 6.2048 | 6.3835 | 6.85 | 4.6518 | 6.4219 | 4.6842 | 6.6462 | 7.9502 | 42.9299 | 46.8372 | 43.553 | 15.1054 |  |  | 0.10339 | 0.22022 | 0.096476 | -0.022998 | -0.13717 | -0.1424 | 0.33306 | -0.047476 | -0.7778 | -0.71937 | -0.39771 | 8.8711 | 8.8721 | 2.0082 | 15.6267 | 16.5927 | 17.1728 | 17.5233 | 17.4911 | 16.4707 | 14.8373 | 16.8368 | 17.1726 | 17.4817 | 17.5414 | 17.2821 | 16.4986 | 14.74 | 6.073 | 8.1662 | 5.6047 | 6.0605 | 5.8351 | 6.5906 | 7.5757 | 15.6549 | 15.3534 | 15.2549 | 14.1973 | 14.1145 | 14.0575 |  |  |  | 10.6581 | 9.6429 | 9.3287 | 9.2024 | 0.039758 | -0.20097 | 12.6594 |  |  | 10.5206 |  |  | 16.8486 | 16.056 | 15.0219 | 16.363 | 15.6504 | 14.7679 | 10.6978 | 10.7654 | 11.4948 | 11.34 | 8.9724 |  | 10.4877 | 8.5174 | 9.8605 | 9.5792 | 10.9494 | 12.4285 |  | 12.1922 |  |  | 11.6766 | 12.3035 | 12.3877 | [6 empty] | 12.6128 |  |  | 11.2953 |  |  | 9.2982 | 10.3214 | 11.6645 | 7.3925 | 9.0505 | 12.5789 | 8.0193 | 9.6303 | 12.3021 | 9.296 | 10.569 | 7.6127 | 10.5268 | 8.3401 | 10.4235 | 7.9696 | 9.6984 | 13.0576 | 10.5536 | 10.3241 | 11.7201 | 8.2765 | 9.8757 | 12.6112 | 8.1932 | 10.7961 | 9.9326 | 10.2255 | 8.5633 | 10.697 | 0.049679 | 20.9546 | 0.033149 | 0.048261 | -37.7189 | 3.1199 | 12.08 | 0.33 | 0.37696 | 0.54669 | 0.36184 | -0.17667 | -0.43154 | -0.43968 | 0.67243 | 0.40907 | 0.40105 | 0.40743 | 0.40473 | 0.57114 | 0.41733 | 0.40829
42810.4388 | -107 | 18.3512 | 18.521 | 18.5324 | 18.5404 | 17.8895 | 16.5335 | 14.6092 | 16.6795 | 17.1688 | 17.264 | 17.2676 | 16.7947 | 15.8262 | 14.4495 | 14.7666 | 14.8277 | 15.4029 | 13.2845 | 13.4125 | 13.9881 |  |  |  | 16.5621 | 15.9071 | 15.0032 | 10.4332 | 10.0555 | 9.84 | 17.0329 | 16.2113 | 15.033 | 16.7942 | 16.0918 | 15.0935 | 10.7576 | 11.5445 |  | 11.9972 | 10.8376 | 10.61 | 8.987 |  | 6.2232 | 6.2995 | 5.9279 | 6.1157 | 6.1946 | 6.3806 | 6.8315 | 4.6786 | 6.433 | 4.7009 | 6.6568 | 7.9457 | 42.9185 | 46.7969 | 43.5265 | 15.1126 |  |  | 0.10273 | 0.084199 | 0.14379 | -0.23525 | -0.077376 | -0.43941 | 0.50325 | -0.1053 | -1.3349 | 0.14732 | -0.52607 | 8.8688 | 8.8703 | 2.0082 | 15.6209 | 16.5859 | 17.1665 | 17.5189 | 17.4823 | 16.4697 | 14.8283 | 16.8313 | 17.1727 | 17.4777 | 17.5367 | 17.2816 | 16.4977 | 14.7306 | 6.0415 | 8.1783 | 5.6337 | 5.9864 | 5.9099 | 6.5936 | 7.579 | 15.6592 | 15.353 | 15.2563 | 14.1988 | 14.1149 | 14.0654 |  |  |  | 10.6651 | 9.6455 | 9.3156 | 9.1879 | -0.03885 | -0.050225 | 12.6648 |  |  | 10.5224 |  |  | 16.852 | 16.0497 | 15.0187 | 16.3666 | 15.6563 | 14.7658 | 10.6987 | 10.7653 | 11.4794 | 11.3273 | 8.9825 |  | 10.4939 | 8.7449 | 9.8688 | 9.5804 | 10.956 | 12.4221 |  | 12.194 |  |  | 11.6909 | 12.309 | 12.3875 | [6 empty] | 12.6136 |  |  | 11.2982 |  |  | 9.3001 | 10.3279 | 11.6663 | 7.3999 | 9.0409 | 12.5925 | 8.0218 | 9.6389 | 12.289 | 9.2974 | 10.5589 | 7.6153 | 10.5383 | 8.3371 | 10.4237 | 7.9883 | 9.7107 | 13.0745 | 10.5639 | 10.3312 | 11.7246 | 8.2894 | 9.8847 | 12.6191 | 8.1938 | 10.7938 | 9.9286 | 10.2328 | 8.5671 | 10.6964 | -0.051244 | 20.9544 | 0.033717 | 0.047704 | -37.7285 | 3.1199 | 18.95 | 0.38 | 0.37575 | 0.33804 | 0.44175 | -0.56504 | -0.3241 | -0.77236 | 0.82656 | 0.40899 | 0.395 | 0.40762 | 0.40858 | 0.5683 | 0.41756 | 0.40893
42810.4388 | -106 | 18.3592 | 18.5309 | 18.5432 | 18.5503 | 17.8913 | 16.5386 | 14.6198 | 16.6849 | 17.178 | 17.2674 | 17.2744 | 16.8061 | 15.8386 | 14.4632 | 14.7687 | 14.8272 | 15.3979 | 13.2857 | 13.4063 | 13.9848 |  |  |  | 16.5551 | 15.9027 | 15.0047 | 10.4309 | 10.0551 | 9.8445 | 17.0302 | 16.2101 | 15.0309 | 16.7904 | 16.0863 | 15.0866 | 10.7536 | 11.5475 |  | 11.9957 | 10.8328 | 10.6055 | 8.9804 |  | 6.2179 | 6.2939 | 5.9377 | 6.0954 | 6.1799 | 6.3599 | 6.7947 | 4.7428 | 6.4301 | 4.633 | 6.6566 | 7.9398 | 42.9096 | 46.7694 | 43.5118 | 15.1276 |  |  | 0.054103 | -0.10045 | 0.19438 | -0.016426 | 0.070476 | -0.2909 | 0.41454 | -0.034332 | -0.13115 | -1.4734 | -0.42195 | 8.8691 | 8.87 | 2.0085 | 15.6208 | 16.5874 | 17.1609 | 17.5142 | 17.4867 | 16.4716 | 14.8305 | 16.8251 | 17.1705 | 17.4767 | 17.5312 | 17.274 | 16.4906 | 14.7288 | 6.042 | 8.1872 | 5.7044 | 5.9323 | 5.8914 | 6.5935 | 7.5755 | 15.6474 | 15.3495 | 15.2523 | 14.2016 | 14.1122 | 14.0626 |  |  |  | 10.6674 | 9.6429 | 9.3136 | 9.1719 | -0.087677 | -0.045896 | 12.6675 |  |  | 10.5309 |  |  | 16.8517 | 16.0413 | 15.0188 | 16.3633 | 15.6531 | 14.7604 | 10.7068 | 10.7638 | 11.4696 | 11.3202 | 8.9979 |  | 10.4863 | 8.9581 | 9.8633 | 9.5868 | 10.9537 | 12.4329 |  | 12.1948 |  |  | 11.6991 | 12.3279 | 12.4014 | [6 empty] | 12.6188 |  |  | 11.2952 |  |  | 9.3062 | 10.3402 | 11.6807 | 7.4123 | 9.0514 | 12.608 | 8.0394 | 9.6469 | 12.2827 | 9.3024 | 10.5534 | 7.6169 | 10.5554 | 8.3445 | 10.4372 | 7.9973 | 9.7126 | 13.0789 | 10.5775 | 10.3399 | 11.7324 | 8.2933 | 9.8822 | 12.619 | 8.1936 | 10.7912 | 9.9214 | 10.2406 | 8.5674 | 10.6914 | 0.031959 | 20.9546 | 0.033849 | 0.048247 | -37.7425 | 3.1199 | 15.29 | 0.27 | 0.27269 | -0.36922 | 0.51362 | -0.14931 | 0.3093 | -0.62841 | 0.75015 | 0.40832 | 0.3889 | 0.40736 | 0.4085 | 0.56004 | 0.41761 | 0.40945
42810.4388 | -105 | 18.3606 | 18.5238 | 18.5413 | 18.5394 | 17.8883 | 16.5337 | 14.6067 | 16.6822 | 17.1708 | 17.2657 | 17.268 | 16.803 | 15.8429 | 14.4591 | 14.7729 | 14.8295 | 15.4013 | 13.2929 | 13.4158 | 13.995 |  |  |  | 16.5627 | 15.9047 | 15.0064 | 10.434 | 10.0556 | 9.8647 | 17.0271 | 16.1983 | 15.0272 | 16.7873 | 16.0804 | 15.0741 | 10.7435 | 11.5681 |  | 11.9846 | 10.8375 | 10.5922 | 8.9606 |  | 6.2168 | 6.3041 | 5.9413 | 6.0902 | 6.1617 | 6.3493 | 6.7809 | 4.7953 | 6.4362 | 4.6231 | 6.6568 | 7.9395 | 42.8966 | 46.7465 | 43.493 | 15.1426 |  |  | -0.015553 | -0.053137 | -0.089488 | 0.086738 | -0.03072 | -0.22322 | 0.34817 | -0.062588 | -0.41818 | -1.1381 | -0.51037 | 8.8698 | 8.871 | 2.0083 | 15.6315 | 16.5878 | 17.1691 | 17.5097 | 17.4896 | 16.4689 | 14.8301 | 16.8281 | 17.1794 | 17.4771 | 17.5364 | 17.2838 | 16.4974 | 14.7313 | 6.017 | 8.1782 | 5.7946 | 5.8738 | 5.9427 | 6.5889 | 7.5671 | 15.65 | 15.3582 | 15.2483 | 14.2057 | 14.1117 | 14.0607 |  |  |  | 10.6764 | 9.638 | 9.2962 | 9.162 | -0.23861 | 0.099206 | 12.6679 |  |  | 10.5345 |  |  | 16.8507 | 16.0545 | 15.021 | 16.372 | 15.6527 | 14.7646 | 10.7174 | 10.757 | 11.4557 | 11.3142 | 9.0383 |  | 10.4904 | 9.1107 | 9.8708 | 9.5834 | 10.9535 | 12.4481 |  | 12.1942 |  |  | 11.7098 | 12.3408 | 12.4057 | [6 empty] | 12.6162 |  |  | 11.3076 |  |  | 9.315 | 10.3475 | 11.6793 | 7.4311 | 9.0652 | 12.6236 | 8.038 | 9.6513 | 12.2858 | 9.2962 | 10.5541 | 7.6148 | 10.5705 | 8.3465 | 10.4292 | 7.9916 | 9.7194 | 13.0793 | 10.5838 | 10.3359 | 11.7193 | 8.2923 | 9.8685 | 12.6172 | 8.1931 | 10.782 | 9.9147 | 10.2423 | 8.5606 | 10.6905 | 0.059886 | 20.9543 | 0.034285 | 0.047711 | -37.6652 | 3.1198 | 12.24 | 0.39 | -0.14621 | -0.26855 | -0.3485 | 0.3431 | -0.20421 | -0.55046 | 0.68747 | 0.40733 | 0.38491 | 0.40745 | 0.41076 | 0.54904 | 0.41783 | 0.41002
42810.4388 | -104 | 18.3574 | 18.5187 | 18.5356 | 18.5399 | 17.892 | 16.5392 | 14.6077 | 16.6768 | 17.1687 | 17.2661 | 17.2707 | 16.8092 | 15.8445 | 14.4664 | 14.7689 | 14.8214 | 15.4012 | 13.2863 | 13.4037 | 13.9837 |  |  |  | 16.5592 | 15.9025 | 15.0001 | 10.4257 | 10.0471 | 9.8696 | 17.0391 | 16.204 | 15.0332 | 16.7966 | 16.0869 | 15.0785 | 10.7575 | 11.6062 |  | 11.9921 | 10.8559 | 10.5926 | 8.9435 |  | 6.2085 | 6.2886 | 5.9143 | 6.0584 | 6.1402 | 6.3362 | 6.7621 | 4.7828 | 6.4256 | 4.6529 | 6.6477 | 7.9425 | 42.8666 | 46.7299 | 43.4755 | 15.1445 |  |  | 0.21772 | -0.045909 | 0.037992 | 0.05717 | -0.07146 | -0.38224 | 0.31597 | -0.16642 | -0.53436 | -0.65999 | -0.35638 | 8.8673 | 8.8685 | 2.0082 | 15.628 | 16.5936 | 17.1652 | 17.519 | 17.4913 | 16.4777 | 14.8416 | 16.8278 | 17.1709 | 17.4784 | 17.541 | 17.2821 | 16.4955 | 14.7367 | 6.0084 | 8.2082 | 5.7874 | 5.91 | 5.9567 | 6.5963 | 7.5698 | 15.6475 | 15.3604 | 15.2536 | 14.2078 | 14.1167 | 14.0688 |  |  |  | 10.6807 | 9.6343 | 9.3051 | 9.1628 | -0.080383 | -0.059446 | 12.6622 |  |  | 10.5181 |  |  | 16.8405 | 16.0405 | 15.0121 | 16.3587 | 15.6433 | 14.7499 | 10.7105 | 10.7449 | 11.43 | 11.2977 | 9.0578 |  | 10.4918 | 9.2388 | 9.8707 | 9.5805 | 10.9484 | 12.4482 |  | 12.1863 |  |  | 11.7147 | 12.3206 | 12.3977 | [6 empty] | 12.606 |  |  | 11.3112 |  |  | 9.3198 | 10.3467 | 11.6765 | 7.4577 | 9.0943 | 12.638 | 8.0425 | 9.6595 | 12.2911 | 9.3017 | 10.5537 | 7.6159 | 10.6053 | 8.3451 | 10.4304 | 7.9905 | 9.7217 | 13.0833 | 10.5841 | 10.3413 | 11.7129 | 8.3018 | 9.8684 | 12.6241 | 8.1949 | 10.7717 | 9.9043 | 10.2457 | 8.5595 | 10.6852 | -0.042384 | 20.9547 | 0.033734 | 0.04748 | -37.7047 | 3.1199 | 2.13 | 0.37 | 0.54705 | -0.24961 | 0.22707 | 0.27854 | -0.31144 | -0.72031 | 0.65489 | 0.40683 | 0.38135 | 0.40737 | 0.41257 | 0.55016 | 0.41876 | 0.41014
42810.4388 | -103 | 18.3609 | 18.5212 | 18.538 | 18.539 | 17.8935 | 16.5354 | 14.6124 | 16.6807 | 17.1737 | 17.264 | 17.2685 | 16.8064 | 15.8391 | 14.4676 | 14.7661 | 14.8171 | 15.4084 | 13.2902 | 13.4084 | 13.9856 |  |  |  | 16.5628 | 15.907 | 15.0011 | 10.4282 | 10.0504 | 9.8906 | 17.0405 | 16.2146 | 15.038 | 16.7977 | 16.089 | 15.0905 | 10.7593 | 11.6363 |  | 12.0006 | 10.8645 | 10.5943 | 8.9256 |  | 6.2104 | 6.2853 | 5.8998 | 6.0386 | 6.119 | 6.3209 | 6.7469 | 4.7227 | 6.4256 | 4.679 | 6.6559 | 7.9321 | 42.8291 | 46.731 | 43.4487 | 15.145 |  |  | 0.084331 | -0.17536 | -0.001436 | 0.10974 | -0.17463 | -0.743 | 0.2956 | 0.058976 | -1.0567 | -0.19822 | -0.36691 | 8.8711 | 8.8722 | 2.0084 | 15.6201 | 16.586 | 17.1594 | 17.5125 | 17.4803 | 16.4636 | 14.8371 | 16.8172 | 17.176 | 17.4675 | 17.5239 | 17.2762 | 16.4966 | 14.732 | 6.0536 | 8.1974 | 5.7428 | 5.9848 | 5.9103 | 6.5933 | 7.5689 | 15.6553 | 15.3524 | 15.2566 | 14.1984 | 14.1119 | 14.0574 |  |  |  | 10.6683 | 9.622 | 9.2861 | 9.162 | -0.1985 | -0.0005398 | 12.6782 |  |  | 10.5267 |  |  | 16.849 | 16.0444 | 15.0175 | 16.3641 | 15.6578 | 14.7583 | 10.7315 | 10.751 | 11.4286 | 11.3024 | 9.0786 |  | 10.4959 | 9.3516 | 9.875 | 9.5621 | 10.9464 | 12.4264 |  | 12.1943 |  |  | 11.7248 | 12.3356 | 12.3986 | [6 empty] | 12.6125 |  |  | 11.3218 |  |  | 9.3155 | 10.3455 | 11.6662 | 7.4681 | 9.1261 | 12.6478 | 8.0321 | 9.6737 | 12.2837 | 9.2926 | 10.546 | 7.6226 | 10.6216 | 8.3358 | 10.4376 | 7.9903 | 9.7357 | 13.0844 | 10.5951 | 10.3442 | 11.7201 | 8.3238 | 9.8795 | 12.6304 | 8.2069 | 10.7775 | 9.8961 | 10.2521 | 8.5667 | 10.6784 | -0.20879 | 20.9551 | 0.033728 | 0.047885 | -37.7001 | 3.1199 | -2.45 | 0.36 | 0.34047 | -0.48784 | -0.044145 | 0.38591 | -0.48685 | -1.0042 | 0.63342 | 0.40639 | 0.37836 | 0.40781 | 0.4072 | 0.555 | 0.41932 | 0.40976
42810.4389 | -102 | 18.3594 | 18.5258 | 18.5459 | 18.5427 | 17.8887 | 16.5397 | 14.6126 | 16.6848 | 17.1742 | 17.2662 | 17.2703 | 16.8158 | 15.8434 | 14.4612 | 14.7645 | 14.8272 | 15.4071 | 13.2844 | 13.408 | 13.9809 |  |  |  | 16.5649 | 15.9027 | 15.0041 | 10.4291 | 10.0554 | 9.9064 | 17.045 | 16.2147 | 15.0411 | 16.8018 | 16.0946 | 15.0823 | 10.7586 | 11.6647 |  | 12.01 | 10.879 | 10.5908 | 8.898 |  | 6.2088 | 6.2884 | 5.8922 | 6.0356 | 6.1073 | 6.3037 | 6.7314 | 4.6878 | 6.4185 | 4.7544 | 6.6547 | 7.9433 | 42.8066 | 46.7381 | 43.4154 | 15.1481 |  |  | 0.1415 | -0.19442 | -0.092116 | -0.045998 | -0.089204 | 0.09088 | 0.54071 | 0.034664 | 0.46122 | -0.83119 | -0.3675 | 8.8715 | 8.8726 | 2.0081 | 15.6254 | 16.589 | 17.1714 | 17.5126 | 17.486 | 16.4753 | 14.8415 | 16.832 | 17.1783 | 17.4797 | 17.5377 | 17.2813 | 16.498 | 14.7349 | 6.0239 | 8.2181 | 5.7251 | 6.0025 | 5.8939 | 6.5992 | 7.5803 | 15.6527 | 15.3456 | 15.2487 | 14.203 | 14.1051 | 14.0573 |  |  |  | 10.6704 | 9.6164 | 9.2693 | 9.1609 | -0.13772 | -0.075067 | 12.688 |  |  | 10.5361 |  |  | 16.8555 | 16.0519 | 15.0286 | 16.3679 | 15.6573 | 14.7603 | 10.7482 | 10.7532 | 11.4351 | 11.3041 | 9.113 |  | 10.497 | 9.4864 | 9.8777 | 9.5557 | 10.947 | 12.4088 |  | 12.1969 |  |  | 11.7305 | 12.3493 | 12.4123 | [6 empty] | 12.616 |  |  | 11.3103 |  |  | 9.3193 | 10.3545 | 11.6781 | 7.4893 | 9.1637 | 12.6581 | 8.0392 | 9.6863 | 12.2789 | 9.3018 | 10.5538 | 7.6461 | 10.6505 | 8.3484 | 10.4524 | 8.0029 | 9.7463 | 13.09 | 10.6038 | 10.3556 | 11.7256 | 8.3339 | 9.8842 | 12.645 | 8.2134 | 10.781 | 9.8941 | 10.2502 | 8.5689 | 10.6807 | 0.016551 | 20.9543 | 0.033969 | 0.047487 | -37.7021 | 3.1199 | 4.11 | 0.33 | 0.44104 | -0.51366 | -0.35357 | -0.24985 | -0.34795 | 0.3512 | 0.85665 | 0.40547 | 0.3747 | 0.40801 | 0.41118 | 0.5583 | 0.42007 | 0.40985
42810.4389 | -101 | 18.3526 | 18.5129 | 18.5345 | 18.54 | 17.8863 | 16.5256 | 14.6049 | 16.6733 | 17.1585 | 17.258 | 17.2685 | 16.8014 | 15.8303 | 14.4488 | 14.763 | 14.8282 | 15.4116 | 13.2843 | 13.4154 | 13.9831 |  |  |  | 16.5637 | 15.9004 | 15.0102 | 10.4232 | 10.0527 | 9.9225 | 17.0306 | 16.2021 | 15.0236 | 16.7846 | 16.0764 | 15.0772 | 10.7428 | 11.668 |  | 11.9903 | 10.8644 | 10.5707 | 8.8574 |  | 6.2026 | 6.2813 | 5.881 | 6.0078 | 6.0818 | 6.2749 | 6.7175 | 4.6773 | 6.4227 | 4.7731 | 6.6513 | 7.9382 | 42.7946 | 46.731 | 43.3802 | 15.1478 |  |  | 0.1093 | -0.2437 | 0.15824 | 0.18596 | 0.009364 | -0.14568 | 0.70039 | -0.07376 | -0.61881 | -1.0158 | -0.46844 | 8.8702 | 8.8712 | 2.0081 | 15.6276 | 16.5898 | 17.1661 | 17.5162 | 17.4895 | 16.4828 | 14.8426 | 16.8382 | 17.179 | 17.4838 | 17.5378 | 17.2835 | 16.4982 | 14.7396 | 5.9424 | 8.23 | 5.7283 | 5.9525 | 5.9388 | 6.596 | 7.5824 | 15.6521 | 15.3456 | 15.2476 | 14.1942 | 14.1048 | 14.0573 |  |  |  | 10.6742 | 9.6042 | 9.2662 | 9.1538 | -0.31054 | -0.11101 | 12.6762 |  |  | 10.5203 |  |  | 16.8453 | 16.0444 | 15.0187 | 16.3631 | 15.6533 | 14.7554 | 10.744 | 10.7443 | 11.4094 | 11.2984 | 9.1486 |  | 10.501 | 9.5797 | 9.8829 | 9.5596 | 10.9532 | 12.4127 |  | 12.2038 |  |  | 11.7494 | 12.3453 | 12.4001 | [6 empty] | 12.6227 |  |  | 11.309 |  |  | 9.3265 | 10.3547 | 11.6846 | 7.4877 | 9.184 | 12.6554 | 8.0265 | 9.6887 | 12.2681 | 9.2939 | 10.5364 | 7.6569 | 10.6796 | 8.3465 | 10.4551 | 7.9903 | 9.7501 | 13.0848 | 10.5986 | 10.3439 | 11.7124 | 8.3274 | 9.8669 | 12.6351 | 8.2167 | 10.7677 | 9.8723 | 10.236 | 8.5552 | 10.6667 | -0.086875 | 20.9546 | 0.034279 | 0.047154 | -37.6143 | 3.1198 | 17.51 | 0.29 | 0.38764 | -0.57509 | 0.46341 | 0.50236 | 0.11273 | -0.44464 | 0.97492 | 0.40461 | 0.37228 | 0.4081 | 0.41987 | 0.55818 | 0.42067 | 0.41018
42810.4389 | -100 | 18.3483 | 18.5131 | 18.5248 | 18.5329 | 17.8799 | 16.526 | 14.5959 | 16.6662 | 17.1675 | 17.2589 | 17.2637 | 16.7987 | 15.8253 | 14.4509 | 14.7725 | 14.8334 | 15.4041 | 13.2982 | 13.4244 | 13.9909 |  |  |  | 16.5695 | 15.9088 | 15.0242 | 10.4332 | 10.0453 | 9.9413 | 17.0427 | 16.213 | 15.0339 | 16.7933 | 16.0891 | 15.0863 | 10.7511 | 11.6765 |  | 12.0078 | 10.8757 | 10.5703 | 8.82 |  | 6.2183 | 6.294 | 5.8859 | 6.0154 | 6.0815 | 6.2809 | 6.7206 | 4.6864 | 6.4321 | 4.7665 | 6.654 | 7.9412 | 42.7825 | 46.7178 | 43.3434 | 15.1407 |  |  | -0.010293 | -0.076137 | 0.18913 | 0.22342 | -0.14046 | 0.000856 | 0.35212 | -0.044192 | -0.50341 | 0.74231 | -0.41599 | 8.8689 | 8.8701 | 2.0082 | 15.6273 | 16.5905 | 17.1713 | 17.5218 | 17.4918 | 16.4828 | 14.8389 | 16.8376 | 17.1859 | 17.4901 | 17.5375 | 17.2829 | 16.5045 | 14.7454 | 5.9007 | 8.1915 | 5.7417 | 5.8992 | 5.9511 | 6.5946 | 7.5779 | 15.6504 | 15.3472 | 15.2485 | 14.1972 | 14.1131 | 14.0607 |  |  |  | 10.679 | 9.5987 | 9.2743 | 9.1411 | -0.28866 | -0.068292 | 12.6848 |  |  | 10.524 |  |  | 16.8493 | 16.0383 | 15.0192 | 16.3609 | 15.6524 | 14.7554 | 10.7615 | 10.7404 | 11.4037 | 11.2992 | 9.1779 |  | 10.4916 | 9.6701 | 9.8794 | 9.5634 | 10.9581 | 12.4017 |  | 12.1969 |  |  | 11.7604 | 12.3544 | 12.3873 | [6 empty] | 12.602 |  |  | 11.3147 |  |  | 9.3421 | 10.3727 | 11.6906 | 7.505 | 9.2104 | 12.6702 | 8.0364 | 9.7055 | 12.2902 | 9.2981 | 10.5426 | 7.6783 | 10.7115 | 8.3629 | 10.4643 | 8.0012 | 9.7617 | 13.0793 | 10.6023 | 10.3377 | 11.7091 | 8.3276 | 9.8721 | 12.6475 | 8.2199 | 10.7613 | 9.8657 | 10.226 | 8.5501 | 10.6611 | 0.10168 | 20.955 | 0.033963 | 0.048312 | -37.6936 | 3.1199 | 12.77 | 0.29 | -0.11896 | -0.32145 | 0.50663 | 0.55065 | -0.4366 | 0.034083 | 0.69127 | 0.40349 | 0.36965 | 0.40816 | 0.42434 | 0.55617 | 0.42198 | 0.41069
42810.4389 | -99 | 18.3579 | 18.5172 | 18.5279 | 18.5346 | 17.8874 | 16.5384 | 14.6034 | 16.6727 | 17.1656 | 17.2635 | 17.2684 | 16.8118 | 15.8369 | 14.4563 | 14.7645 | 14.8179 | 15.3974 | 13.2894 | 13.4032 | 13.9804 |  |  |  | 16.5602 | 15.8923 | 15.0088 | 10.4181 | 10.0379 | 9.9565 | 17.0434 | 16.2147 | 15.0373 | 16.7947 | 16.0899 | 15.0895 | 10.7545 | 11.6781 |  | 12.0047 | 10.885 | 10.5647 | 8.799 |  | 6.2116 | 6.2852 | 5.8809 | 6.0052 | 6.072 | 6.263 | 6.7207 | 4.7176 | 6.4263 | 4.7374 | 6.6509 | 7.9399 | 42.7724 | 46.6859 | 43.2962 | 15.1308 |  |  | -0.025409 | -0.10242 | 0.1451 | 0.051254 | -0.060292 | -0.27054 | 0.34949 | -0.1145 | -0.33431 | -0.21753 | -0.35777 | 8.8724 | 8.8736 | 2.0081 | 15.6255 | 16.5963 | 17.1692 | 17.5201 | 17.4888 | 16.4737 | 14.8303 | 16.836 | 17.1852 | 17.4885 | 17.5415 | 17.2853 | 16.5016 | 14.7424 | 5.8761 | 8.1823 | 5.8022 | 5.8521 | 5.9353 | 6.5959 | 7.5814 | 15.6472 | 15.3558 | 15.2438 | 14.2051 | 14.1098 | 14.0627 |  |  |  | 10.6787 | 9.5963 | 9.2625 | 9.1325 | -0.25118 | -0.16239 | 12.6866 |  |  | 10.5255 |  |  | 16.8584 | 16.0485 | 15.0194 | 16.3721 | 15.6536 | 14.7696 | 10.7642 | 10.7425 | 11.4073 | 11.3062 | 9.2257 |  | 10.4991 | 9.7596 | 9.8802 | 9.5725 | 10.9564 | 12.3511 |  | 12.1996 |  |  | 11.7705 | 12.3549 | 12.4086 | [6 empty] | 12.6093 |  |  | 11.3255 |  |  | 9.3397 | 10.3651 | 11.6919 | 7.5215 | 9.2274 | 12.6856 | 8.0301 | 9.7114 | 12.3081 | 9.2941 | 10.5225 | 7.7 | 10.7264 | 8.3649 | 10.4672 | 8.011 | 9.7694 | 13.0914 | 10.6187 | 10.3513 | 11.7214 | 8.3329 | 9.8888 | 12.6568 | 8.2311 | 10.7583 | 9.8633 | 10.2406 | 8.5555 | 10.6742 | -0.11673 | 20.9544 | 0.034256 | 0.048182 | -37.7725 | 3.1199 | 2.53 | 0.25 | -0.18691 | -0.37282 | 0.44375 | 0.26374 | -0.28604 | -0.6059 | 0.68866 | 0.40241 | 0.36719 | 0.40785 | 0.42723 | 0.54986 | 0.42268 | 0.41092
42810.4389 | -98 | 18.3556 | 18.5201 | 18.5307 | 18.5399 | 17.8928 | 16.5396 | 14.6085 | 16.6819 | 17.1738 | 17.268 | 17.2755 | 16.8114 | 15.8386 | 14.4618 | 14.7709 | 14.8183 | 15.4086 | 13.2869 | 13.4159 | 13.9834 |  |  |  | 16.5616 | 15.9033 | 15.0058 | 10.4124 | 10.0435 | 9.9559 | 17.0408 | 16.2116 | 15.0418 | 16.7947 | 16.0855 | 15.0793 | 10.7584 | 11.6904 |  | 12.0001 | 10.8945 | 10.5451 | 8.7687 |  | 6.2089 | 6.2807 | 5.8776 | 5.9867 | 6.0601 | 6.2669 | 6.7537 | 4.7188 | 6.428 | 4.6878 | 6.6593 | 7.9364 | 42.7563 | 46.6569 | 43.272 | 15.1224 |  |  | 0.076443 | 0.015203 | 0.20753 | -0.13537 | -0.030064 | 0.065252 | 0.52625 | -0.11384 | -0.86829 | -0.22172 | -0.35836 | 8.8719 | 8.873 | 2.0085 | 15.6218 | 16.5891 | 17.1629 | 17.5078 | 17.4814 | 16.4764 | 14.8306 | 16.831 | 17.1727 | 17.4795 | 17.543 | 17.2828 | 16.4994 | 14.7372 | 5.9053 | 8.1899 | 5.8533 | 5.9235 | 5.9141 | 6.5922 | 7.5786 | 15.6497 | 15.349 | 15.2509 | 14.2011 | 14.11 | 14.0616 |  |  |  | 10.6765 | 9.587 | 9.262 | 9.1335 | 0.033073 | 0.071917 | 12.6887 |  |  | 10.5298 |  |  | 16.8599 | 16.0554 | 15.02 | 16.3678 | 15.6581 | 14.7625 | 10.7795 | 10.7549 | 11.4046 | 11.3245 | 9.2516 |  | 10.5069 | 9.8316 | 9.89 | 9.5752 | 10.9534 | 12.308 |  | 12.2046 |  |  | 11.768 | 12.3434 | 12.4202 | [6 empty] | 12.5994 |  |  | 11.3158 |  |  | 9.3468 | 10.3717 | 11.7013 | 7.5419 | 9.2457 | 12.6826 | 8.0276 | 9.7368 | 12.3286 | 9.297 | 10.5264 | 7.7237 | 10.7297 | 8.3556 | 10.4695 | 8.01 | 9.7743 | 13.0749 | 10.6136 | 10.3391 | 11.7013 | 8.3308 | 9.892 | 12.6585 | 8.215 | 10.7482 | 9.8529 | 10.2157 | 8.5663 | 10.6636 | 0.076257 | 20.9547 | 0.033831 | 0.048833 | -37.7836 | 3.1199 | 9.45 | 0.26 | 0.3242 | 0.14364 | 0.53069 | -0.42861 | -0.20198 | 0.29757 | 0.84507 | 0.40195 | 0.36551 | 0.40768 | 0.42355 | 0.54385 | 0.42365 | 0.41082
42810.4389 | -97 | 18.3646 | 18.5267 | 18.5338 | 18.5426 | 17.8955 | 16.5373 | 14.6046 | 16.6885 | 17.1797 | 17.2722 | 17.2719 | 16.8112 | 15.8454 | 14.4652 | 14.7703 | 14.823 | 15.4027 | 13.2804 | 13.4144 | 13.9856 |  |  |  | 16.5618 | 15.9091 | 15.0117 | 10.4215 | 10.0408 | 9.9445 | 17.0435 | 16.2195 | 15.0463 | 16.7974 | 16.0864 | 15.0845 | 10.7604 | 11.7236 |  | 12.0057 | 10.8976 | 10.5341 | 8.7461 |  | 6.2099 | 6.2841 | 5.8771 | 5.9858 | 6.0486 | 6.2639 | 6.7382 | 4.6894 | 6.4365 | 4.645 | 6.6574 | 7.9355 | 42.7135 | 46.6254 | 43.248 | 15.1086 |  |  | -0.072721 | 0.089455 | 0.1221 | 0.07951 | 0.084932 | -0.36779 | 0.34752 | -0.40429 | -0.40028 | 0.095496 | -0.43963 | 8.8652 | 8.866 | 2.0083 | 15.6228 | 16.5832 | 17.1592 | 17.5096 | 17.4731 | 16.4695 | 14.8189 | 16.8275 | 17.1756 | 17.477 | 17.5347 | 17.2812 | 16.494 | 14.7396 | 5.9269 | 8.185 | 6.0261 | 6.0482 | 5.8923 | 6.5911 | 7.5844 | 15.6536 | 15.3452 | 15.2482 | 14.2039 | 14.1084 | 14.0648 |  |  |  | 10.6818 | 9.581 | 9.2513 | 9.1456 | 0.030439 | 0.050839 | 12.6893 |  |  | 10.5319 |  |  | 16.8525 | 16.0519 | 15.0185 | 16.3674 | 15.6606 | 14.7704 | 10.7807 | 10.7441 | 11.4025 | 11.3134 | 9.2725 |  | 10.5031 | 9.8621 | 9.884 | 9.5651 | 10.9532 | 12.2882 |  | 12.2034 |  |  | 11.768 | 12.363 | 12.4248 | [6 empty] | 12.591 |  |  | 11.3125 |  |  | 9.346 | 10.3758 | 11.703 | 7.5631 | 9.2636 | 12.6908 | 8.0306 | 9.7352 | 12.3434 | 9.2941 | 10.5346 | 7.7501 | 10.7278 | 8.3661 | 10.4752 | 8.0095 | 9.7809 | 13.064 | 10.6135 | 10.3422 | 11.704 | 8.3316 | 9.8953 | 12.6642 | 8.2008 | 10.7591 | 9.8351 | 10.2133 | 8.556 | 10.6673 | -0.083793 | 20.954 | 0.033097 | 0.04947 | -37.7925 | 3.1199 | -21.59 | 0.28 | -0.3162 | 0.34842 | 0.40707 | 0.32849 | 0.33949 | -0.70646 | 0.68672 | 0.40124 | 0.36447 | 0.40795 | 0.42102 | 0.52534 | 0.42434 | 0.41066
42810.4389 | -96 | 18.3639 | 18.5144 | 18.5294 | 18.539 | 17.8975 | 16.537 | 14.6 | 16.6835 | 17.1682 | 17.2626 | 17.2668 | 16.8035 | 15.8376 | 14.4623 | 14.7617 | 14.8179 | 15.4031 | 13.2859 | 13.4105 | 13.9822 |  |  |  | 16.5662 | 15.909 | 15.0075 | 10.4216 | 10.037 | 9.9402 | 17.0391 | 16.2107 | 15.0305 | 16.7917 | 16.0844 | 15.0838 | 10.7525 | 11.7643 |  | 12.0042 | 10.8939 | 10.5138 | 8.7074 |  | 6.2139 | 6.2824 | 5.8758 | 5.9763 | 6.0399 | 6.2404 | 6.716 | 4.6909 | 6.4333 | 4.6166 | 6.6565 | 7.9404 | 42.6763 | 46.6123 | 43.232 | 15.102 |  |  | 0.035047 | -0.17931 | 0.041936 | 0.10448 | -0.093804 | -0.14634 | 0.40666 | -0.38523 | -0.1759 | -1.2424 | -0.39055 | 8.8681 | 8.8692 | 2.0082 | 15.6224 | 16.5931 | 17.1706 | 17.5149 | 17.4859 | 16.4805 | 14.8371 | 16.8339 | 17.1923 | 17.4885 | 17.5498 | 17.2912 | 16.5018 | 14.7424 | 5.9149 | 8.1703 | 6.0548 | 6.2153 | 5.9277 | 6.5834 | 7.5885 | 15.6495 | 15.3428 | 15.248 | 14.2067 | 14.1042 | 14.0576 |  |  |  | 10.6835 | 9.5723 | 9.2533 | 9.1549 | 0.021727 | 0.011129 | 12.702 |  |  | 10.5234 |  |  | 16.8514 | 16.0474 | 15.0145 | 16.3661 | 15.6584 | 14.7657 | 10.785 | 10.7443 | 11.3996 | 11.3107 | 9.2731 |  | 10.507 | 9.8606 | 9.8858 | 9.5548 | 10.9585 | 12.2891 |  | 12.2017 |  |  | 11.7686 | 12.3733 | 12.4379 | [6 empty] | 12.5971 |  |  | 11.3072 |  |  | 9.3511 | 10.3713 | 11.6997 | 7.5798 | 9.2788 | 12.7011 | 8.03 | 9.7353 | 12.3644 | 9.2834 | 10.5266 | 7.7508 | 10.7401 | 8.3722 | 10.476 | 7.9868 | 9.7795 | 13.0562 | 10.6023 | 10.3408 | 11.694 | 8.3252 | 9.8971 | 12.6612 | 8.1846 | 10.75 | 9.821 | 10.2061 | 8.5581 | 10.6717 | 0.034463 | 20.9547 | 0.032919 | 0.049514 | -37.8612 | 3.1199 | -4.17 | 0.27 | 0.21951 | -0.49329 | 0.23856 | 0.37655 | -0.35677 | -0.44561 | 0.74282 | 0.40135 | 0.36457 | 0.40841 | 0.42146 | 0.52261 | 0.42516 | 0.41045
42810.4389 | -95 | 18.3605 | 18.5173 | 18.5321 | 18.5396 | 17.8972 | 16.5371 | 14.6109 | 16.6813 | 17.1722 | 17.2664 | 17.2694 | 16.7981 | 15.8369 | 14.4687 | 14.7663 | 14.817 | 15.3987 | 13.2894 | 13.4137 | 13.9776 |  |  |  | 16.5659 | 15.9054 | 15.002 | 10.4155 | 10.0363 | 9.9444 | 17.033 | 16.1978 | 15.0328 | 16.7948 | 16.0824 | 15.0776 | 10.7511 | 11.8003 |  | 12.0019 | 10.8942 | 10.5008 | 8.6626 |  | 6.2139 | 6.2778 | 5.8734 | 5.9791 | 6.0295 | 6.237 | 6.723 | 4.6993 | 6.4381 | 4.6473 | 6.6584 | 7.9385 | 42.6357 | 46.5883 | 43.2082 | 15.0939 |  |  | -0.031321 | -0.076137 | 0.20161 | 0.12945 | -0.001808 | -0.047116 | 0.59525 | -0.38918 | -0.24323 | 0.49705 | -0.46189 | 8.8728 | 8.8739 | 2.0085 | 15.6257 | 16.5905 | 17.17 | 17.5119 | 17.4853 | 16.4758 | 14.8332 | 16.831 | 17.1758 | 17.4835 | 17.5416 | 17.2893 | 16.4948 | 14.7407 | 5.9127 | 8.1652 | 5.9753 | 6.3313 | 6.1246 | 6.5908 | 7.5814 | 15.6509 | 15.3449 | 15.2429 | 14.1962 | 14.1065 | 14.0518 |  |  |  | 10.679 | 9.5628 | 9.2477 | 9.1891 | 0.076632 | -0.087488 | 12.7023 |  |  | 10.5215 |  |  | 16.8541 | 16.0506 | 15.0174 | 16.3657 | 15.6584 | 14.7696 | 10.7992 | 10.7471 | 11.403 | 11.315 | 9.2632 |  | 10.5049 | 9.8579 | 9.8981 | 9.5378 | 10.9616 | 12.3077 |  | 12.1974 |  |  | 11.7575 | 12.3935 | 12.4455 | [6 empty] | 12.6036 |  |  | 11.3 |  |  | 9.3508 | 10.3757 | 11.709 | 7.5919 | 9.2981 | 12.6994 | 8.0282 | 9.7335 | 12.3726 | 9.2764 | 10.5345 | 7.7372 | 10.7551 | 8.3848 | 10.4806 | 7.9816 | 9.7945 | 13.0602 | 10.5993 | 10.3431 | 11.6917 | 8.3411 | 9.9099 | 12.6657 | 8.1922 | 10.7551 | 9.8268 | 10.2016 | 8.5617 | 10.674 | -0.083793 | 20.9533 | 0.033326 | 0.048385 | -37.8476 | 3.1199 | 4.07 | 0.18 | -0.20752 | -0.32144 | 0.52307 | 0.41913 | -0.04953 | -0.25284 | 0.89871 | 0.40156 | 0.36505 | 0.40899 | 0.42257 | 0.53061 | 0.42636 | 0.40935
42810.4389 | -94 | 18.3554 | 18.5247 | 18.5335 | 18.5455 | 17.8882 | 16.5317 | 14.6057 | 16.6778 | 17.1725 | 17.2612 | 17.2689 | 16.8152 | 15.8357 | 14.4642 | 14.7679 | 14.8237 | 15.4038 | 13.2916 | 13.4129 | 13.9872 |  |  |  | 16.5709 | 15.912 | 15.0152 | 10.4183 | 10.0368 | 9.9502 | 17.0367 | 16.2051 | 15.0339 | 16.7901 | 16.079 | 15.0872 | 10.749 | 11.8126 |  | 12.0118 | 10.9031 | 10.4931 | 8.6375 |  | 6.2148 | 6.2688 | 5.871 | 5.9777 | 6.0305 | 6.2523 | 6.7829 | 4.7187 | 6.4381 | 4.6895 | 6.6639 | 7.9419 | 42.5854 | 46.5898 | 43.1941 | 15.0874 |  |  | -0.074033 | 0.022431 | 0.041276 | -0.086082 | -0.007064 | -0.068144 | 0.48354 | -0.34975 | -0.28371 | -0.36816 | -0.51414 | 8.8701 | 8.8713 | 2.0081 | 15.6319 | 16.5866 | 17.1543 | 17.5104 | 17.484 | 16.477 | 14.8323 | 16.8299 | 17.177 | 17.4822 | 17.5358 | 17.2847 | 16.4929 | 14.7345 | 5.9361 | 8.1631 | 5.9134 | 6.41 | 6.3352 | 6.5929 | 7.5801 | 15.6531 | 15.3477 | 15.2485 | 14.2035 | 14.1103 | 14.0659 |  |  |  | 10.682 | 9.5687 | 9.2533 | 9.2227 | -0.00765 | -0.18535 | 12.7154 |  |  | 10.5368 |  |  | 16.8521 | 16.0613 | 15.0272 | 16.3809 | 15.6638 | 14.7703 | 10.8074 | 10.7527 | 11.4088 | 11.3294 | 9.2486 |  | 10.5045 | 9.8397 | 9.8931 | 9.5224 | 10.9511 | 12.3284 |  | 12.1976 |  |  | 11.7174 | 12.3978 | 12.4556 | [6 empty] | 12.5896 |  |  | 11.2724 |  |  | 9.3566 | 10.376 | 11.7167 | 7.6078 | 9.3156 | 12.6959 | 8.0238 | 9.7263 | 12.3812 | 9.2843 | 10.5375 | 7.7443 | 10.7696 | 8.399 | 10.5026 | 7.9802 | 9.8073 | 13.0573 | 10.5988 | 10.3397 | 11.6872 | 8.3415 | 9.9065 | 12.6558 | 8.1958 | 10.7608 | 9.8187 | 10.194 | 8.5576 | 10.6752 | -0.13637 | 20.9537 | 0.032707 | 0.047755 | -37.9793 | 3.1198 | -6.16 | 0.3 | -0.31904 | 0.17447 | 0.23667 | -0.34178 | -0.097906 | -0.30409 | 0.81002 | 0.40195 | 0.36539 | 0.40907 | 0.42021 | 0.53735 | 0.42698 | 0.40852
42810.439 | -93 | 18.3541 | 18.5206 | 18.5327 | 18.5398 | 17.8921 | 16.5329 | 14.6038 | 16.6822 | 17.1709 | 17.2586 | 17.2716 | 16.806 | 15.8375 | 14.458 | 14.7639 | 14.8227 | 15.4002 | 13.2903 | 13.4144 | 13.9883 |  |  |  | 16.5657 | 15.9107 | 15.0149 | 10.4102 | 10.0317 | 9.9614 | 17.032 | 16.198 | 15.0313 | 16.7868 | 16.078 | 15.0829 | 10.745 | 11.8198 |  | 12.0098 | 10.9094 | 10.4741 | 8.6009 |  | 6.2176 | 6.2691 | 5.8751 | 5.981 | 6.0193 | 6.2761 | 6.8592 | 4.7727 | 6.446 | 4.7365 | 6.6714 | 7.9353 | 42.5481 | 46.5874 | 43.1729 | 15.0923 |  |  | 0.11522 | -0.20953 | 0.003164 | -0.057826 | 0.032364 | 0.21902 | 0.60642 | -0.3031 | 0.098483 | -0.46845 | -0.42393 | 8.8708 | 8.872 | 2.0081 | 15.6298 | 16.589 | 17.157 | 17.5153 | 17.4842 | 16.469 | 14.8307 | 16.8313 | 17.1773 | 17.4882 | 17.5395 | 17.283 | 16.4978 | 14.7346 | 5.9559 | 8.1563 | 5.8484 | 6.4973 | 6.4864 | 6.593 | 7.5843 | 15.6479 | 15.3455 | 15.2431 | 14.2002 | 14.1021 | 14.0613 |  |  |  | 10.6818 | 9.5541 | 9.2528 | 9.1886 | 0.079265 | -0.14207 | 12.7072 |  |  | 10.5276 |  |  | 16.8484 | 16.0492 | 15.0184 | 16.3656 | 15.6491 | 14.7619 | 10.7962 | 10.7412 | 11.4004 | 11.3193 | 9.2142 |  | 10.5007 | 9.8088 | 9.8988 | 9.5038 | 10.9593 | 12.3387 |  | 12.2088 |  |  | 11.6431 | 12.4027 | 12.4575 | [6 empty] | 12.5729 |  |  | 11.2554 |  |  | 9.359 | 10.3697 | 11.7131 | 7.6196 | 9.3246 | 12.696 | 8.0206 | 9.7204 | 12.3948 | 9.2741 | 10.5299 | 7.7456 | 10.7699 | 8.3981 | 10.5107 | 7.9835 | 9.8197 | 13.0557 | 10.5928 | 10.339 | 11.6629 | 8.3349 | 9.8994 | 12.6461 | 8.2019 | 10.7578 | 9.8094 | 10.1792 | 8.5549 | 10.6753 | -0.076667 | 20.9524 | 0.033636 | 0.047748 | -37.8716 | 3.1199 | 7.35 | 0.3 | 0.39802 | -0.53324 | 0.065526 | -0.28013 | 0.20957 | 0.54518 | 0.90717 | 0.40278 | 0.36644 | 0.40985 | 0.41803 | 0.54505 | 0.42787 | 0.40946
42810.439 | -92 | 18.3544 | 18.5211 | 18.5335 | 18.5398 | 17.8931 | 16.5345 | 14.6074 | 16.6832 | 17.1729 | 17.266 | 17.2717 | 16.8198 | 15.8397 | 14.4612 | 14.7693 | 14.8196 | 15.4025 | 13.2984 | 13.4141 | 13.9909 |  |  |  | 16.5692 | 15.9106 | 15.0111 | 10.4107 | 10.0297 | 9.969 | 17.0365 | 16.2009 | 15.0273 | 16.7847 | 16.0765 | 15.0782 | 10.7457 | 11.8378 |  | 12.0028 | 10.9188 | 10.4779 | 8.6193 |  | 6.2174 | 6.2738 | 5.8773 | 5.9729 | 6.0161 | 6.3478 | 6.9382 | 4.8496 | 6.4532 | 4.7443 | 6.6705 | 7.9445 | 42.5092 | 46.5596 | 43.1487 | 15.1025 |  |  | 0.066587 | -0.013053 | 0.057704 | -0.011826 | -0.00772 | 0.086936 | 0.62613 | -0.50943 | -0.56822 | -0.1934 | -0.44738 | 8.8723 | 8.8738 | 2.0084 | 15.6214 | 16.5817 | 17.1539 | 17.5135 | 17.4836 | 16.4688 | 14.8351 | 16.8224 | 17.1747 | 17.4793 | 17.5373 | 17.2861 | 16.4921 | 14.7351 | 5.9672 | 8.1878 | 5.8395 | 6.5904 | 6.6278 | 6.5941 | 7.5838 | 15.6485 | 15.3455 | 15.2432 | 14.1972 | 14.1046 | 14.0581 |  |  |  | 10.6799 | 9.5498 | 9.2386 | 9.1302 | 0.017878 | -0.0048684 | 12.7103 |  |  | 10.544 |  |  | 16.8522 | 16.0495 | 15.0289 | 16.3704 | 15.6622 | 14.7673 | 10.8054 | 10.7347 | 11.4169 | 11.3281 | 9.2144 |  | 10.4942 | 9.7204 | 9.8933 | 9.4977 | 10.9504 | 12.3311 |  | 12.1995 |  |  | 11.5596 | 12.4219 | 12.4376 | [6 empty] | 12.5658 |  |  | 11.2543 |  |  | 9.3614 | 10.366 | 11.7197 | 7.6358 | 9.3492 | 12.6987 | 8.0327 | 9.7362 | 12.4126 | 9.2574 | 10.5255 | 7.7522 | 10.778 | 8.39 | 10.5264 | 7.9912 | 9.8269 | 13.0592 | 10.589 | 10.3371 | 11.6463 | 8.3411 | 9.9056 | 12.6546 | 8.2115 | 10.7516 | 9.8031 | 10.1629 | 8.5446 | 10.6718 | -0.048162 | 20.954 | 0.033929 | 0.049289 | -37.7524 | 3.1199 | 9.95 | 0.35 | 0.30258 | -0.13309 | 0.27983 | -0.12668 | -0.10237 | 0.34352 | 0.92191 | 0.40256 | 0.36872 | 0.40973 | 0.41689 | 0.54599 | 0.42738 | 0.41102
42810.439 | -91 | 18.3595 | 18.5206 | 18.5333 | 18.5432 | 17.8901 | 16.533 | 14.6077 | 16.6797 | 17.1728 | 17.2673 | 17.2659 | 16.814 | 15.8422 | 14.4647 | 14.7703 | 14.8198 | 15.4037 | 13.2918 | 13.4048 | 13.9906 |  |  |  | 16.571 | 15.9127 | 15.0094 | 10.4023 | 10.037 | 9.9698 | 17.0354 | 16.2104 | 15.0352 | 16.7909 | 16.0857 | 15.0851 | 10.7487 | 11.8986 |  | 12.0154 | 10.9367 | 10.4694 | 8.6012 |  | 6.2123 | 6.2793 | 5.8735 | 5.9716 | 6.0354 | 6.418 | 7.0043 | 4.9023 | 6.4555 | 4.7772 | 6.6689 | 7.9424 | 42.4676 | 46.5393 | 43.1177 | 15.1104 |  |  | -0.068777 | 0.11048 | 0.11224 | 0.12551 | 0.19336 | -0.01426 | 0.65964 | -0.39246 | -0.64255 | -0.75524 | -0.24193 | 8.8693 | 8.8702 | 2.0084 | 15.634 | 16.5871 | 17.1651 | 17.5074 | 17.4902 | 16.4697 | 14.8327 | 16.8325 | 17.1732 | 17.4839 | 17.5396 | 17.2992 | 16.5017 | 14.7415 | 5.9134 | 8.2122 | 5.8114 | 6.6315 | 6.7579 | 6.5925 | 7.5853 | 15.6582 | 15.35 | 15.2507 | 14.202 | 14.1082 | 14.0649 |  |  |  | 10.6852 | 9.5507 | 9.233 | 9.0822 | 0.035099 | 0.011693 | 12.7078 |  |  | 10.5328 |  |  | 16.8442 | 16.0501 | 15.0101 | 16.367 | 15.6499 | 14.7586 | 10.7828 | 10.7236 | 11.41 | 11.3306 | 9.2184 |  | 10.4946 | 9.5696 | 9.8962 | 9.5128 | 10.9537 | 12.3268 |  | 12.2045 |  |  | 11.5361 | 12.4423 | 12.4276 | [6 empty] | 12.5718 |  |  | 11.2677 |  |  | 9.3605 | 10.3535 | 11.7274 | 7.6572 | 9.3661 | 12.7021 | 8.0411 | 9.7505 | 12.4252 | 9.2493 | 10.5141 | 7.7574 | 10.782 | 8.3859 | 10.5346 | 7.9882 | 9.8359 | 13.0777 | 10.5967 | 10.3347 | 11.6371 | 8.3529 | 9.9123 | 12.6633 | 8.1872 | 10.7544 | 9.7988 | 10.1492 | 8.5454 | 10.6743 | 0.17853 | 20.9515 | 0.034279 | 0.050085 | -37.8264 | 3.1199 | 12.06 | 0.29 | -0.30752 | 0.38721 | 0.39029 | 0.41271 | 0.51238 | -0.13915 | 0.94638 | 0.40246 | 0.373 | 0.40942 | 0.42268 | 0.54929 | 0.42798 | 0.41253
42810.439 | -90 | 18.3529 | 18.5132 | 18.5265 | 18.5402 | 17.8892 | 16.5294 | 14.6053 | 16.6746 | 17.1726 | 17.2662 | 17.2692 | 16.808 | 15.8373 | 14.4631 | 14.7672 | 14.8181 | 15.3959 | 13.2794 | 13.401 | 13.9869 |  |  |  | 16.5701 | 15.9098 | 15.0065 | 10.4001 | 10.0315 | 9.9685 | 17.0265 | 16.2006 | 15.0228 | 16.7848 | 16.0738 | 15.0745 | 10.7375 | 11.9407 |  | 12.0021 | 10.9379 | 10.4485 | 8.5403 |  | 6.2085 | 6.2685 | 5.8714 | 5.9624 | 6.0801 | 6.5036 | 7.081 | 4.8599 | 6.46 | 4.8508 | 6.6658 | 7.9425 | 42.4186 | 46.5403 | 43.0881 | 15.1268 |  |  | -0.092433 | -0.030797 | 0.17204 | 0.03877 | 0.07376 | 0.09942 | 0.54859 | -0.40626 | -0.65092 | -0.02346 | -0.21709 | 8.8715 | 8.8728 | 2.0081 | 15.6209 | 16.5807 | 17.1612 | 17.5098 | 17.4735 | 16.4712 | 14.8285 | 16.8256 | 17.1732 | 17.4777 | 17.5411 | 17.2813 | 16.49 | 14.7348 | 5.9215 | 8.2631 | 5.7662 | 6.5758 | 6.8681 | 6.6002 | 7.5877 | 15.6638 | 15.3468 | 15.2534 | 14.2023 | 14.1058 | 14.0642 |  |  |  | 10.6915 | 9.5422 | 9.2333 | 9.072 | 0.020511 | 0.0099994 | 12.7174 |  |  | 10.5411 |  |  | 16.8475 | 16.0538 | 15.0186 | 16.369 | 15.6559 | 14.7598 | 10.7682 | 10.7212 | 11.4052 | 11.3353 | 9.222 |  | 10.5069 | 9.4127 | 9.9059 | 9.5358 | 10.9572 | 12.3383 |  | 12.2108 |  |  | 11.5364 | 12.4588 | 12.4138 | [6 empty] | 12.587 |  |  | 11.2867 |  |  | 9.3667 | 10.3417 | 11.7332 | 7.685 | 9.3849 | 12.7078 | 8.043 | 9.7713 | 12.438 | 9.2423 | 10.524 | 7.7793 | 10.7918 | 8.3873 | 10.5449 | 7.9719 | 9.8504 | 13.0931 | 10.6006 | 10.3187 | 11.6198 | 8.3521 | 9.9146 | 12.6605 | 8.1616 | 10.7609 | 9.7915 | 10.134 | 8.5389 | 10.6775 | 0.25037 | 20.952 | 0.0351 | 0.051019 | -37.8809 | 3.1199 | -1.9 | 0.33 | -0.3565 | -0.20443 | 0.48319 | 0.22937 | 0.31651 | 0.36746 | 0.86318 | 0.40277 | 0.37768 | 0.40889 | 0.42267 | 0.55459 | 0.42931 | 0.41302
42810.439 | -89 | 18.3608 | 18.5191 | 18.524 | 18.5415 | 17.8929 | 16.5358 | 14.6035 | 16.673 | 17.174 | 17.2646 | 17.2738 | 16.8096 | 15.8375 | 14.466 | 14.7676 | 14.8128 | 15.3937 | 13.2836 | 13.4021 | 13.9758 |  |  |  | 16.5646 | 15.9023 | 15.0101 | 10.3999 | 10.0229 | 9.9754 | 17.0378 | 16.2132 | 15.0306 | 16.7911 | 16.0854 | 15.081 | 10.7508 | 11.9975 |  | 12.0107 | 10.9629 | 10.451 | 8.4925 |  | 6.2077 | 6.2693 | 5.8686 | 5.9682 | 6.1241 | 6.5779 | 7.1541 | 4.8178 | 6.4637 | 4.8799 | 6.6733 | 7.9373 | 42.3929 | 46.5508 | 43.0676 | 15.1386 |  |  | -0.053665 | 0.043459 | -0.000776 | 0.012486 | -0.018236 | 0.028452 | 0.48091 | -0.37078 | -0.16754 | -0.58048 | -0.22106 | 8.8705 | 8.8715 | 2.0084 | 15.6264 | 16.5834 | 17.165 | 17.5093 | 17.481 | 16.4691 | 14.8223 | 16.8279 | 17.177 | 17.4794 | 17.5354 | 17.2902 | 16.4913 | 14.7405 | 5.9183 | 8.2571 | 5.7138 | 6.4914 | 6.83 | 6.6079 | 7.5892 | 15.6602 | 15.3389 | 15.2513 | 14.1939 | 14.1053 | 14.0595 |  |  |  | 10.6871 | 9.527 | 9.2221 | 9.0816 | 0.015041 | 0.037853 | 12.7218 |  |  | 10.5458 |  |  | 16.8507 | 16.0446 | 15.0122 | 16.3726 | 15.6633 | 14.7614 | 10.7516 | 10.7203 | 11.4168 | 11.3487 | 9.2063 |  | 10.5017 | 9.2088 | 9.9001 | 9.5037 | 10.962 | 12.3278 |  | 12.2156 |  |  | 11.513 | 12.4674 | 12.3765 | [6 empty] | 12.5841 |  |  | 11.2963 |  |  | 9.3608 | 10.337 | 11.7323 | 7.6931 | 9.3982 | 12.6985 | 8.0327 | 9.7734 | 12.4411 | 9.2251 | 10.5199 | 7.7995 | 10.7941 | 8.3805 | 10.5527 | 7.956 | 9.8577 | 13.0958 | 10.6005 | 10.3003 | 11.6051 | 8.3541 | 9.9152 | 12.6636 | 8.1553 | 10.768 | 9.7797 | 10.1142 | 8.5328 | 10.6725 | 0.22437 | 20.9513 | 0.035065 | 0.050961 | -37.8738 | 3.1199 | 34.55 | 0.44 | -0.27165 | 0.24285 | -0.032451 | 0.13017 | -0.1574 | 0.1966 | 0.80829 | 0.40303 | 0.38315 | 0.40995 | 0.42393 | 0.56059 | 0.43107 | 0.41261
42810.439 | -88 | 18.3583 | 18.5126 | 18.5275 | 18.5374 | 17.8878 | 16.5315 | 14.6045 | 16.6761 | 17.1665 | 17.2644 | 17.2718 | 16.8073 | 15.8382 | 14.4454 | 14.7693 | 14.8219 | 15.3928 | 13.2928 | 13.4072 | 13.9902 |  |  |  | 16.5647 | 15.9022 | 15.0073 | 10.4032 | 10.0257 | 9.9911 | 17.0414 | 16.2135 | 15.0247 | 16.7907 | 16.09 | 15.0817 | 10.7496 | 12.0511 |  | 12.0118 | 10.964 | 10.4454 | 8.4539 |  | 6.211 | 6.2663 | 5.8594 | 5.9615 | 6.1505 | 6.6529 | 7.2213 | 4.7945 | 6.4707 | 4.9041 | 6.6812 | 7.9396 | 42.3537 | 46.5705 | 43.0369 | 15.1381 |  |  | -0.019493 | -0.030141 | 0.13919 | 0.25036 | 0.14013 | 0.046196 | 0.44346 | -0.45554 | -0.91947 | -0.78839 | -0.36115 | 8.8694 | 8.8706 | 2.0081 | 15.628 | 16.5886 | 17.1658 | 17.5161 | 17.4825 | 16.4673 | 14.8335 | 16.8315 | 17.181 | 17.4924 | 17.5435 | 17.2915 | 16.4973 | 14.7389 | 5.9042 | 8.2593 | 5.6713 | 6.4387 | 6.7783 | 6.601 | 7.582 | 15.6585 | 15.3457 | 15.2524 | 14.1988 | 14.112 | 14.0659 |  |  |  | 10.6901 | 9.5301 | 9.2154 | 9.0071 | -0.086259 | -0.065657 | 12.7118 |  |  | 10.5417 |  |  | 16.8505 | 16.0595 | 15.0171 | 16.3755 | 15.6567 | 14.758 | 10.7267 | 10.7115 | 11.4269 | 11.3611 | 9.2019 |  | 10.5091 | 9.0186 | 9.9057 | 9.445 | 10.9589 | 12.3178 |  | 12.2176 |  |  | 11.5051 | 12.4513 | 12.3293 | [6 empty] | 12.5719 |  |  | 11.3048 |  |  | 9.3728 | 10.3409 | 11.7341 | 7.6846 | 9.4043 | 12.6931 | 8.0345 | 9.7705 | 12.4547 | 9.2197 | 10.518 | 7.8192 | 10.7854 | 8.3843 | 10.5607 | 7.9364 | 9.8606 | 13.1 | 10.5973 | 10.2886 | 11.5797 | 8.3459 | 9.9122 | 12.6593 | 8.1476 | 10.762 | 9.7619 | 10.0983 | 8.521 | 10.6567 | 0.014818 | 20.9522 | 0.035186 | 0.050809 | -37.9379 | 3.1199 | 0.6 | 0.38 | -0.16372 | -0.20224 | 0.4346 | 0.58288 | 0.43637 | 0.25055 | 0.77628 | 0.4034 | 0.38862 | 0.41147 | 0.42469 | 0.56447 | 0.4321 | 0.41477
42810.439 | -87 | 18.3534 | 18.518 | 18.5327 | 18.5335 | 17.8841 | 16.5298 | 14.6021 | 16.6781 | 17.1719 | 17.2628 | 17.2673 | 16.7952 | 15.8358 | 14.4507 | 14.7655 | 14.8169 | 15.3931 | 13.2849 | 13.4048 | 13.9842 |  |  |  | 16.5621 | 15.9077 | 15.0074 | 10.388 | 10.0094 | 9.9858 | 17.0362 | 16.2011 | 15.0218 | 16.7944 | 16.0812 | 15.0817 | 10.7406 | 12.1199 |  | 12.0096 | 10.9699 | 10.4313 | 8.4317 |  | 6.193 | 6.2658 | 5.8543 | 5.9583 | 6.1669 | 6.6875 | 7.2755 | 4.8236 | 6.4652 | 4.8954 | 6.679 | 7.9357 | 42.3157 | 46.5889 | 43.0141 | 15.1454 |  |  | -0.002409 | 0.11837 | 0.028792 | 0.20239 | 0.090188 | 0.12505 | 0.46317 | -0.2985 | 0.15044 | -0.39103 | -0.30611 | 8.8702 | 8.8713 | 2.0081 | 15.6232 | 16.579 | 17.1534 | 17.5015 | 17.4787 | 16.4668 | 14.8295 | 16.8275 | 17.1809 | 17.478 | 17.532 | 17.2792 | 16.4911 | 14.7306 | 5.8876 | 8.2734 | 5.6387 | 6.3669 | 6.8121 | 6.6021 | 7.5875 | 15.659 | 15.347 | 15.2518 | 14.2032 | 14.1097 | 14.0648 |  |  |  | 10.684 | 9.5155 | 9.2022 | 8.9463 | 0.10783 | -0.050225 | 12.7223 |  |  | 10.5616 |  |  | 16.8605 | 16.0563 | 15.0192 | 16.3808 | 15.6651 | 14.7708 | 10.7069 | 10.7027 | 11.4386 | 11.3742 | 9.1974 |  | 10.5053 | 8.8841 | 9.9072 | 9.4073 | 10.9596 | 12.3052 |  | 12.2171 |  |  | 11.4932 | 12.4398 | 12.3185 | [6 empty] | 12.5328 |  |  | 11.2996 |  |  | 9.3753 | 10.3376 | 11.7354 | 7.6881 | 9.4085 | 12.6914 | 8.0432 | 9.7697 | 12.4648 | 9.2067 | 10.5209 | 7.8466 | 10.7711 | 8.3921 | 10.5681 | 7.9643 | 9.8832 | 13.1108 | 10.6147 | 10.2897 | 11.5775 | 8.3643 | 9.9215 | 12.6705 | 8.1448 | 10.7761 | 9.769 | 10.1042 | 8.5274 | 10.6657 | -0.059526 | 20.9512 | 0.035335 | 0.049767 | -37.896 | 3.1199 | 0.87 | 0.26 | -0.057555 | 0.40078 | 0.19766 | 0.52407 | 0.3501 | 0.41225 | 0.79339 | 0.4034 | 0.3924 | 0.41254 | 0.42667 | 0.56873 | 0.43242 | 0.41626
42810.439 | -86 | 18.3545 | 18.5058 | 18.5273 | 18.5392 | 17.8882 | 16.524 | 14.6009 | 16.674 | 17.1713 | 17.2573 | 17.2703 | 16.8109 | 15.8326 | 14.4574 | 14.7654 | 14.8196 | 15.3947 | 13.2835 | 13.4199 | 13.9787 |  |  |  | 16.5739 | 15.9094 | 15.0093 | 10.4032 | 9.9974 | 9.9868 | 17.0409 | 16.2096 | 15.0394 | 16.7927 | 16.0944 | 15.0908 | 10.7504 | 12.1879 |  | 12.0084 | 10.9822 | 10.431 | 8.4178 |  | 6.1927 | 6.2682 | 5.8605 | 5.9682 | 6.189 | 6.7012 | 7.2975 | 4.8392 | 6.4794 | 4.8488 | 6.6853 | 7.9423 | 42.2927 | 46.602 | 42.9765 | 15.1375 |  |  | 0.11259 | 0.074999 | -0.038232 | 0.085426 | 0.15722 | -0.43941 | 0.31992 | -0.31229 | -0.23545 | -0.078638 | -0.17715 | 8.8678 | 8.8688 | 2.0084 | 15.6263 | 16.5755 | 17.1535 | 17.5002 | 17.4802 | 16.4647 | 14.8306 | 16.8261 | 17.1729 | 17.475 | 17.5314 | 17.2831 | 16.4943 | 14.7342 | 5.9091 | 8.2905 | 5.6326 | 6.2969 | 6.8246 | 6.6027 | 7.5937 | 15.6518 | 15.3457 | 15.2444 | 14.1941 | 14.1071 | 14.058 |  |  |  | 10.6763 | 9.4785 | 9.1768 | 8.897 | 0.027197 | 0.071917 | 12.726 |  |  | 10.5509 |  |  | 16.855 | 16.0484 | 15.0095 | 16.3717 | 15.6525 | 14.7638 | 10.6728 | 10.7048 | 11.4368 | 11.3652 | 9.2256 |  | 10.5084 | 8.756 | 9.9145 | 9.3962 | 10.9627 | 12.285 |  | 12.2299 |  |  | 11.4898 | 12.4554 | 12.2944 | [6 empty] | 12.4846 |  |  | 11.2763 |  |  | 9.3819 | 10.3255 | 11.7436 | 7.6874 | 9.4185 | 12.6901 | 8.0588 | 9.7661 | 12.4655 | 9.2004 | 10.5241 | 7.8381 | 10.7609 | 8.3902 | 10.5708 | 7.961 | 9.8771 | 13.1082 | 10.6161 | 10.2818 | 11.5461 | 8.3586 | 9.9171 | 12.6753 | 8.13 | 10.7696 | 9.7451 | 10.08 | 8.516 | 10.6509 | -0.0094496 | 20.9512 | 0.034939 | 0.048023 | -37.78 | 3.1199 | 2.9 | 0.32 | 0.39347 | 0.31902 | -0.22778 | 0.34048 | 0.46225 | -0.7728 | 0.6594 | 0.40272 | 0.3962 | 0.41296 | 0.42435 | 0.57013 | 0.43313 | 0.41738
42810.4391 | -85 | 18.3514 | 18.5155 | 18.5255 | 18.5407 | 17.8875 | 16.5288 | 14.6076 | 16.6772 | 17.1718 | 17.2661 | 17.2704 | 16.8066 | 15.8318 | 14.4463 | 14.7645 | 14.8147 | 15.3978 | 13.2881 | 13.4087 | 13.9813 |  |  |  | 16.5621 | 15.9002 | 15.0075 | 10.3852 | 9.9873 | 9.9663 | 17.0389 | 16.2084 | 15.0291 | 16.794 | 16.0822 | 15.0739 | 10.7497 | 12.2035 |  | 12.0115 | 10.9888 | 10.4215 | 8.4148 |  | 6.1897 | 6.2615 | 5.8596 | 5.9594 | 6.1827 | 6.687 | 7.2719 | 4.7311 | 6.4701 | 4.7973 | 6.6863 | 7.9425 | 42.2856 | 46.597 | 42.9546 | 15.1352 |  |  | 0.16975 | -0.13002 | -0.044148 | -0.08411 | 0.081648 | -0.15751 | 0.50128 | -0.34581 | -0.33431 | 0.10305 | -0.3218 | 8.8697 | 8.8706 | 2.0084 | 15.6312 | 16.5773 | 17.1575 | 17.5049 | 17.4836 | 16.4659 | 14.8309 | 16.8262 | 17.181 | 17.4849 | 17.5394 | 17.2774 | 16.4894 | 14.7381 | 5.9207 | 8.2964 | 5.7811 | 6.2201 | 6.7912 | 6.6047 | 7.5942 | 15.6619 | 15.3548 | 15.2493 | 14.2014 | 14.1036 | 14.0639 |  |  |  | 10.6746 | 9.4611 | 9.1638 | 8.8777 | -0.087677 | 0.062695 | 12.7065 |  |  | 10.5493 |  |  | 16.8473 | 16.0479 | 15.0151 | 16.3616 | 15.6468 | 14.7565 | 10.6438 | 10.6936 | 11.4323 | 11.3543 | 9.254 |  | 10.5014 | 8.6604 | 9.9118 | 9.3853 | 10.9565 | 12.2472 |  | 12.217 |  |  | 11.484 | 12.4479 | 12.3087 | [6 empty] | 12.4828 |  |  | 11.2902 |  |  | 9.3845 | 10.3291 | 11.7519 | 7.6595 | 9.4121 | 12.6861 | 8.0629 | 9.757 | 12.4632 | 9.2005 | 10.533 | 7.8284 | 10.754 | 8.4043 | 10.5806 | 7.9655 | 9.8951 | 13.1118 | 10.6197 | 10.283 | 11.5433 | 8.3552 | 9.9219 | 12.678 | 8.1423 | 10.775 | 9.7444 | 10.0722 | 8.5016 | 10.6551 | 0.017322 | 20.9504 | 0.033975 | 0.04596 | -37.7565 | 3.1199 | 4.06 | 0.24 | 0.48313 | -0.42005 | -0.24476 | -0.33784 | 0.33311 | -0.46268 | 0.82539 | 0.4017 | 0.39877 | 0.41305 | 0.42329 | 0.55369 | 0.43319 | 0.41786
42810.4391 | -84 | 18.3599 | 18.5198 | 18.532 | 18.5439 | 17.8874 | 16.5307 | 14.6051 | 16.6834 | 17.1651 | 17.2648 | 17.2693 | 16.81 | 15.8401 | 14.4586 | 14.7688 | 14.816 | 15.4115 | 13.2844 | 13.4167 | 13.9821 |  |  |  | 16.5653 | 15.903 | 15.0142 | 10.3913 | 9.9708 | 9.9364 | 17.0392 | 16.2109 | 15.0344 | 16.7934 | 16.085 | 15.0801 | 10.7534 | 12.2261 |  | 12.0172 | 10.9823 | 10.4182 | 8.4566 |  | 6.2012 | 6.2584 | 5.8656 | 5.9611 | 6.1919 | 6.674 | 7.2876 | 4.6511 | 6.4793 | 4.8143 | 6.6937 | 7.9508 | 42.2672 | 46.5893 | 42.9322 | 15.1322 |  |  | 0.10273 | 0.10851 | 0.067564 | 0.013142 | 0.09676 | 0.10994 | 0.43951 | -0.31426 | -0.28488 | -0.23137 | -0.505 | 8.8697 | 8.8704 | 2.0085 | 15.6317 | 16.581 | 17.1669 | 17.5083 | 17.4823 | 16.4721 | 14.8338 | 16.8343 | 17.1797 | 17.4871 | 17.5428 | 17.2853 | 16.4933 | 14.744 | 5.8977 | 8.2809 | 5.8272 | 6.1734 | 6.842 | 6.6098 | 7.5994 | 15.6561 | 15.3432 | 15.2544 | 14.2051 | 14.1064 | 14.0623 |  |  |  | 10.6751 | 9.4531 | 9.1578 | 8.8897 | 0.014433 | 0.088102 | 12.7157 |  |  | 10.5608 |  |  | 16.8585 | 16.0593 | 15.0278 | 16.3765 | 15.6641 | 14.7664 | 10.6335 | 10.7042 | 11.4568 | 11.3695 | 9.3021 |  | 10.5048 | 8.6007 | 9.908 | 9.3935 | 10.9546 | 12.2314 |  | 12.2172 |  |  | 11.4873 | 12.4254 | 12.3193 | [6 empty] | 12.4847 |  |  | 11.2803 |  |  | 9.3927 | 10.3121 | 11.7583 | 7.6573 | 9.4183 | 12.6749 | 8.071 | 9.7626 | 12.4564 | 9.2063 | 10.524 | 7.8188 | 10.7502 | 8.4035 | 10.58 | 7.964 | 9.9043 | 13.1129 | 10.6207 | 10.2879 | 11.521 | 8.3485 | 9.9157 | 12.6963 | 8.1535 | 10.7664 | 9.7345 | 10.0721 | 8.4913 | 10.6468 | 0.1011 | 20.9503 | 0.033183 | 0.045258 | -37.8601 | 3.1199 | 1.22 | 0.37 | 0.37582 | 0.38373 | 0.30279 | 0.13354 | 0.36262 | 0.38653 | 0.77285 | 0.40047 | 0.4003 | 0.41276 | 0.42644 | 0.54917 | 0.43215 | 0.41754
42810.4391 | -83 | 18.3622 | 18.518 | 18.5312 | 18.5433 | 17.8893 | 16.5303 | 14.6013 | 16.6786 | 17.1697 | 17.2627 | 17.2712 | 16.8117 | 15.8306 | 14.4553 | 14.7695 | 14.8133 | 15.3967 | 13.283 | 13.4071 | 13.9822 |  |  |  | 16.5633 | 15.9015 | 15.009 | 10.3758 | 9.9552 | 9.902 | 17.0387 | 16.208 | 15.0306 | 16.7917 | 16.0857 | 15.0766 | 10.7488 | 12.2423 |  | 12.015 | 10.9825 | 10.4247 | 8.496 |  | 6.1974 | 6.2636 | 5.8618 | 5.9567 | 6.1828 | 6.6638 | 7.3253 | 4.5793 | 6.4807 | 4.7705 | 6.6879 | 7.9451 | 42.2778 | 46.5752 | 42.9147 | 15.1243 |  |  | 0.026503 | 0.25768 | 0.16942 | 0.058482 | 0.24658 | 0.16579 | 0.44806 | -0.17233 | -0.52852 | -0.62601 | -0.23219 | 8.8682 | 8.8693 | 2.0084 | 15.6249 | 16.5823 | 17.1537 | 17.4998 | 17.4757 | 16.4783 | 14.8369 | 16.832 | 17.1798 | 17.4867 | 17.5424 | 17.2884 | 16.4898 | 14.7369 | 5.9094 | 8.2472 | 5.7847 | 6.1468 | 6.8705 | 6.6044 | 7.5969 | 15.6557 | 15.3503 | 15.2488 | 14.2059 | 14.1093 | 14.0659 |  |  |  | 10.672 | 9.4466 | 9.1587 | 8.9029 | -0.032975 | -0.061328 | 12.7199 |  |  | 10.5575 |  |  | 16.848 | 16.0383 | 15.017 | 16.3652 | 15.6586 | 14.766 | 10.6071 | 10.6952 | 11.4506 | 11.3648 | 9.3375 |  | 10.5028 | 8.6097 | 9.9064 | 9.4004 | 10.956 | 12.2001 |  | 12.2106 |  |  | 11.5125 | 12.4214 | 12.3292 | [6 empty] | 12.5034 |  |  | 11.3012 |  |  | 9.4017 | 10.3197 | 11.7613 | 7.6635 | 9.424 | 12.6722 | 8.0964 | 9.7676 | 12.4357 | 9.213 | 10.4959 | 7.8262 | 10.7473 | 8.4108 | 10.5735 | 7.963 | 9.9257 | 13.126 | 10.6321 | 10.2919 | 11.5218 | 8.3599 | 9.9291 | 12.7118 | 8.1702 | 10.7817 | 9.7415 | 10.084 | 8.4887 | 10.6549 | -0.078593 | 20.9507 | 0.032982 | 0.045714 | -37.8701 | 3.1199 | 5.08 | 0.29 | 0.19087 | 0.59133 | 0.47948 | 0.28171 | 0.57887 | 0.47466 | 0.78031 | 0.39943 | 0.4 | 0.41262 | 0.42451 | 0.5536 | 0.43091 | 0.41707
42810.4391 | -82 | 18.3638 | 18.5176 | 18.5271 | 18.5406 | 17.891 | 16.5273 | 14.5949 | 16.6746 | 17.1692 | 17.2589 | 17.2654 | 16.8064 | 15.8322 | 14.4571 | 14.7684 | 14.811 | 15.3909 | 13.2821 | 13.4071 | 13.9857 |  |  |  | 16.5649 | 15.9051 | 15.0057 | 10.3661 | 9.9396 | 9.8615 | 17.0371 | 16.2004 | 15.0187 | 16.7815 | 16.0804 | 15.0722 | 10.7486 | 12.1977 |  | 12.0106 | 10.9713 | 10.4218 | 8.5359 |  | 6.195 | 6.2558 | 5.861 | 5.9639 | 6.1758 | 6.692 | 7.3551 | 4.5761 | 6.4841 | 4.7142 | 6.6861 | 7.9481 | 42.265 | 46.5632 | 42.9031 | 15.1197 |  |  | -0.040521 | -0.23845 | -0.021804 | -0.019058 | 0.10333 | 0.21179 | 0.20098 | -0.26892 | -0.09203 | -1.0918 | -0.29438 | 8.8692 | 8.8703 | 2.0081 | 15.6447 | 16.592 | 17.1714 | 17.5219 | 17.4895 | 16.4717 | 14.8384 | 16.8364 | 17.1829 | 17.4922 | 17.546 | 17.2933 | 16.497 | 14.7483 | 5.9442 | 8.2279 | 5.7225 | 6.0881 | 6.9165 | 6.6022 | 7.59 | 15.6602 | 15.349 | 15.2467 | 14.2021 | 14.1023 | 14.0603 |  |  |  | 10.6708 | 9.4424 | 9.1507 | 8.9414 | -0.01697 | -0.067539 | 12.7191 |  |  | 10.56 |  |  | 16.8555 | 16.0497 | 15.0303 | 16.367 | 15.6564 | 14.7758 | 10.5939 | 10.7081 | 11.4679 | 11.3771 | 9.3613 |  | 10.5093 | 8.5765 | 9.9112 | 9.415 | 10.9554 | 12.1301 |  | 12.2222 |  |  | 11.5013 | 12.3921 | 12.3373 | [6 empty] | 12.4743 |  |  | 11.3011 |  |  | 9.4044 | 10.2944 | 11.7589 | 7.635 | 9.4127 | 12.6517 | 8.0838 | 9.7644 | 12.3939 | 9.1964 | 10.47 | 7.8153 | 10.7159 | 8.4085 | 10.5585 | 7.97 | 9.9329 | 13.1186 | 10.6276 | 10.2965 | 11.5114 | 8.3651 | 9.9223 | 12.7194 | 8.1839 | 10.7901 | 9.7302 | 10.0717 | 8.4777 | 10.6365 | 0.10746 | 20.9519 | 0.03421 | 0.047559 | -37.8248 | 3.1199 | 0.52 | 0.27 | -0.236 | -0.56883 | -0.17201 | -0.16081 | 0.37475 | 0.53651 | 0.52264 | 0.39898 | 0.40108 | 0.41219 | 0.42038 | 0.55971 | 0.42979 | 0.41596
42810.4391 | -81 | 18.3634 | 18.5173 | 18.528 | 18.5373 | 17.884 | 16.53 | 14.5978 | 16.6807 | 17.1704 | 17.2621 | 17.2636 | 16.8042 | 15.836 | 14.4544 | 14.763 | 14.8078 | 15.3836 | 13.2759 | 13.4019 | 13.9822 |  |  |  | 16.5661 | 15.9032 | 15.0057 | 10.3611 | 9.9224 | 9.8527 | 17.0324 | 16.1977 | 15.012 | 16.7758 | 16.0716 | 15.0696 | 10.7356 | 12.0699 |  | 12.0059 | 10.9665 | 10.4148 | 8.5849 |  | 6.2012 | 6.2574 | 5.8577 | 5.9647 | 6.1803 | 6.701 | 7.4045 | 4.6294 | 6.4846 | 4.6748 | 6.6973 | 7.9392 | 42.254 | 46.5271 | 42.8952 | 15.1081 |  |  | 0.096159 | -0.007141 | -0.05992 | -0.03417 | 0.045504 | -0.016232 | 0.37446 | -0.21504 | -0.42986 | 0.44523 | -0.34664 | 8.8693 | 8.8703 | 2.0084 | 15.6256 | 16.5859 | 17.1582 | 17.4998 | 17.4705 | 16.4632 | 14.8366 | 16.825 | 17.174 | 17.4822 | 17.5403 | 17.2846 | 16.4913 | 14.7322 | 5.9748 | 8.2349 | 5.686 | 6.1166 | 6.8424 | 6.6022 | 7.599 | 15.6554 | 15.3363 | 15.2443 | 14.1982 | 14.1053 | 14.058 |  |  |  | 10.6689 | 9.4339 | 9.1328 | 8.9613 | -0.1752 | -0.020489 | 12.7195 |  |  | 10.5744 |  |  | 16.8597 | 16.0628 | 15.0211 | 16.3743 | 15.6563 | 14.7635 | 10.5743 | 10.6979 | 11.4721 | 11.3871 | 9.3554 |  | 10.5078 | 8.5606 | 9.916 | 9.4276 | 10.9605 | 12.0886 |  | 12.2188 |  |  | 11.5101 | 12.3936 | 12.3368 | [6 empty] | 12.4804 |  |  | 11.2953 |  |  | 9.4123 | 10.2937 | 11.7642 | 7.6455 | 9.4203 | 12.6533 | 8.1004 | 9.7636 | 12.3712 | 9.2038 | 10.4563 | 7.8285 | 10.7033 | 8.4103 | 10.5602 | 7.9675 | 9.9347 | 13.1141 | 10.6244 | 10.2823 | 11.4975 | 8.3468 | 9.916 | 12.7136 | 8.1916 | 10.7937 | 9.7202 | 10.0555 | 8.4641 | 10.6346 | -0.060296 | 20.9504 | 0.034428 | 0.049173 | -37.754 | 3.1199 | 6.5 | 0.32 | 0.36354 | -0.098439 | -0.28515 | -0.21533 | 0.24869 | -0.14853 | 0.7134 | 0.39909 | 0.40168 | 0.41201 | 0.41699 | 0.56481 | 0.42801 | 0.41535
42810.4391 | -80 | 18.3685 | 18.5163 | 18.5355 | 18.5441 | 17.8958 | 16.5312 | 14.6025 | 16.6799 | 17.1727 | 17.2625 | 17.2713 | 16.8015 | 15.8381 | 14.4599 | 14.7651 | 14.8102 | 15.389 | 13.2774 | 13.4047 | 13.9801 |  |  |  | 16.5696 | 15.9037 | 15.009 | 10.3598 | 9.9085 | 9.8805 | 17.0396 | 16.1964 | 15.0243 | 16.7838 | 16.0859 | 15.0776 | 10.7495 | 11.9651 |  | 12.0046 | 10.9784 | 10.4278 | 8.6431 |  | 6.1955 | 6.2545 | 5.862 | 5.9675 | 6.1683 | 6.7036 | 7.4176 | 4.5625 | 6.4729 | 4.601 | 6.6893 | 7.9422 | 42.2399 | 46.5156 | 42.8899 | 15.0979 |  |  | 0.017303 | 0.072371 | 0.12736 | 0.095938 | 0.097416 | -0.24556 | 0.54005 | -0.036304 | -0.53689 | -0.28886 | -0.35518 | 8.8688 | 8.8701 | 2.0083 | 15.6347 | 16.5807 | 17.1612 | 17.5078 | 17.4852 | 16.4723 | 14.8345 | 16.8333 | 17.1783 | 17.4814 | 17.5389 | 17.2877 | 16.4953 | 14.7411 | 6.0156 | 8.23 | 5.6648 | 6.1296 | 6.6963 | 6.5951 | 7.6029 | 15.6536 | 15.336 | 15.2363 | 14.1923 | 14.1001 | 14.0533 |  |  |  | 10.6579 | 9.4201 | 9.1342 | 8.9322 | -0.20316 | -0.0067504 | 12.7248 |  |  | 10.5659 |  |  | 16.8502 | 16.0565 | 15.0242 | 16.3736 | 15.6611 | 14.7659 | 10.5474 | 10.6878 | 11.4818 | 11.3989 | 9.3341 |  | 10.5054 | 8.518 | 9.9091 | 9.4426 | 10.9505 | 12.0428 |  | 12.2193 |  |  | 11.5256 | 12.4172 | 12.3513 | [6 empty] | 12.4732 |  |  | 11.3107 |  |  | 9.418 | 10.287 | 11.7618 | 7.6402 | 9.4169 | 12.6535 | 8.1066 | 9.7637 | 12.3727 | 9.204 | 10.4411 | 7.8348 | 10.699 | 8.4135 | 10.556 | 7.9758 | 9.9418 | 13.1049 | 10.622 | 10.2825 | 11.4822 | 8.3501 | 9.9227 | 12.7262 | 8.2081 | 10.7948 | 9.7152 | 10.0457 | 8.4621 | 10.6363 | -0.041229 | 20.9511 | 0.035502 | 0.04884 | -37.7334 | 3.1199 | 10.83 | 0.33 | 0.15422 | 0.31338 | 0.41572 | 0.36081 | 0.36387 | -0.57772 | 0.85674 | 0.3996 | 0.40263 | 0.41126 | 0.41164 | 0.56761 | 0.42685 | 0.41579
42810.4391 | -79 | 18.3711 | 18.5192 | 18.5229 | 18.5434 | 17.8794 | 16.5253 | 14.6041 | 16.6766 | 17.1705 | 17.2542 | 17.2645 | 16.8021 | 15.8411 | 14.4581 | 14.7694 | 14.8122 | 15.392 | 13.2812 | 13.4057 | 13.987 |  |  |  | 16.5675 | 15.9076 | 15.0098 | 10.3632 | 9.8924 | 9.8948 | 17.0311 | 16.1986 | 15.0194 | 16.7863 | 16.0703 | 15.0737 | 10.7463 | 11.8625 |  | 11.9964 | 10.98 | 10.4359 | 8.7144 |  | 6.1957 | 6.2474 | 5.8467 | 5.9676 | 6.1862 | 6.6883 | 7.4097 | 4.5387 | 6.4738 | 4.5849 | 6.6922 | 7.9445 | 42.2217 | 46.4827 | 42.8792 | 15.0978 |  |  | 0.2197 | 0.075655 | 0.055076 | -0.12682 | 0.090848 | -0.17854 | 0.36197 | -0.084932 | -0.66629 | -0.55488 | -0.42652 | 8.8701 | 8.8712 | 2.0083 | 15.6337 | 16.5826 | 17.1604 | 17.5095 | 17.49 | 16.4727 | 14.8324 | 16.8359 | 17.1788 | 17.484 | 17.544 | 17.2888 | 16.4957 | 14.7473 | 5.9813 | 8.208 | 5.6716 | 6.0861 | 6.6378 | 6.5967 | 7.5967 | 15.6619 | 15.3489 | 15.2439 | 14.1995 | 14.1106 | 14.0597 |  |  |  | 10.6648 | 9.4207 | 9.1251 | 8.9334 | -0.25199 | -0.0080678 | 12.7118 |  |  | 10.5625 |  |  | 16.8513 | 16.0418 | 15.0018 | 16.3556 | 15.6494 | 14.7522 | 10.5238 | 10.6716 | 11.4762 | 11.3969 | 9.3573 |  | 10.5021 | 8.4937 | 9.9107 | 9.4567 | 10.9583 | 11.995 |  | 12.2186 |  |  | 11.5428 | 12.422 | 12.369 | [6 empty] | 12.4582 |  |  | 11.3188 |  |  | 9.4188 | 10.2743 | 11.7621 | 7.6367 | 9.4105 | 12.6461 | 8.1088 | 9.7558 | 12.3812 | 9.2019 | 10.4236 | 7.8427 | 10.6948 | 8.4119 | 10.5571 | 8.011 | 9.9608 | 13.1119 | 10.6223 | 10.2884 | 11.4662 | 8.3621 | 9.9373 | 12.7412 | 8.2313 | 10.8025 | 9.7292 | 10.0465 | 8.4776 | 10.6467 | 0.061042 | 20.9528 | 0.034394 | 0.048819 | -37.7689 | 3.1199 | 5.34 | 0.28 | 0.54955 | 0.3204 | 0.27338 | -0.41484 | 0.35138 | -0.49259 | 0.70139 | 0.39885 | 0.40336 | 0.41113 | 0.41563 | 0.56615 | 0.42476 | 0.41599
42810.4391 | -78 | 18.3729 | 18.5156 | 18.5348 | 18.5449 | 17.8885 | 16.5349 | 14.6044 | 16.6806 | 17.175 | 17.2634 | 17.2783 | 16.8077 | 15.8381 | 14.4594 | 14.7656 | 14.8139 | 15.3882 | 13.2829 | 13.4124 | 13.9886 |  |  |  | 16.5615 | 15.909 | 15.0095 | 10.3586 | 9.8731 | 9.8878 | 17.0389 | 16.1929 | 15.0169 | 16.7811 | 16.0728 | 15.0669 | 10.7373 | 11.7687 |  | 11.9971 | 10.9705 | 10.4442 | 8.785 |  | 6.192 | 6.2475 | 5.8552 | 5.9733 | 6.196 | 6.6775 | 7.3811 | 4.5243 | 6.479 | 4.5579 | 6.6959 | 7.9388 | 42.1821 | 46.4721 | 42.8766 | 15.0978 |  |  | -0.058921 | -0.048537 | 0.089904 | -0.2543 | -0.078688 | 0.10862 | 0.35606 | -0.01462 | -0.35163 | -0.51607 | -0.34863 | 8.8674 | 8.8688 | 2.0084 | 15.6305 | 16.5853 | 17.1643 | 17.5069 | 17.4821 | 16.4734 | 14.8324 | 16.8346 | 17.1791 | 17.4885 | 17.5492 | 17.2896 | 16.499 | 14.7483 | 5.9445 | 8.1876 | 5.6325 | 6.0089 | 6.5949 | 6.5962 | 7.6022 | 15.6615 | 15.3454 | 15.2436 | 14.1963 | 14.1036 | 14.0578 |  |  |  | 10.662 | 9.4186 | 9.1198 | 8.9354 | -0.18047 | -0.068856 | 12.7201 |  |  | 10.561 |  |  | 16.8516 | 16.0493 | 15.0133 | 16.3572 | 15.6579 | 14.7587 | 10.509 | 10.6694 | 11.4928 | 11.4215 | 9.3767 |  | 10.5102 | 8.452 | 9.9107 | 9.4421 | 10.9576 | 11.9543 |  | 12.2198 |  |  | 11.5593 | 12.4163 | 12.3802 | [6 empty] | 12.4404 |  |  | 11.3068 |  |  | 9.4122 | 10.2565 | 11.759 | 7.6433 | 9.4014 | 12.6298 | 8.1071 | 9.7408 | 12.3811 | 9.1864 | 10.4102 | 7.8444 | 10.6816 | 8.4101 | 10.5534 | 8.0392 | 9.9491 | 13.1017 | 10.6083 | 10.2837 | 11.452 | 8.3589 | 9.938 | 12.7396 | 8.2237 | 10.7851 | 9.7247 | 10.0435 | 8.4762 | 10.645 | 0.17602 | 20.9517 | 0.034365 | 0.049029 | -37.7426 | 3.1199 | -0.36 | 0.36 | -0.28459 | -0.25663 | 0.34928 | -0.58743 | -0.32701 | 0.38421 | 0.69562 | 0.39858 | 0.40452 | 0.41151 | 0.41965 | 0.57113 | 0.4225 | 0.41584
42810.4391 | -77 | 18.3616 | 18.5112 | 18.5272 | 18.5393 | 17.8867 | 16.5272 | 14.6015 | 16.6754 | 17.1686 | 17.2619 | 17.2603 | 16.8041 | 15.8346 | 14.4614 | 14.7677 | 14.8127 | 15.3888 | 13.2859 | 13.41 | 13.986 |  |  |  | 16.5608 | 15.9077 | 15.0081 | 10.3515 | 9.8523 | 9.8735 | 17.0375 | 16.1999 | 15.0217 | 16.7871 | 16.0828 | 15.0757 | 10.7458 | 11.6843 |  | 12.002 | 10.9667 | 10.4543 | 8.8299 |  | 6.1961 | 6.2512 | 5.8535 | 5.9705 | 6.1864 | 6.6656 | 7.3734 | 4.51 | 6.4765 | 4.5143 | 6.695 | 7.9422 | 42.1613 | 46.4809 | 42.8848 | 15.1149 |  |  | 0.11193 | -0.13331 | 0.032076 | -0.013798 | 0.20781 | -0.042516 | 0.10767 | -0.17561 | -0.61512 | -0.10843 | -0.47301 | 8.8701 | 8.8711 | 2.0087 | 15.6238 | 16.5839 | 17.159 | 17.5059 | 17.4809 | 16.4791 | 14.836 | 16.8297 | 17.1812 | 17.4921 | 17.5438 | 17.2887 | 16.4959 | 14.7395 | 5.9374 | 8.1802 | 5.5587 | 5.9428 | 6.5149 | 6.6015 | 7.6113 | 15.6629 | 15.3405 | 15.2442 | 14.1928 | 14.1033 | 14.06 |  |  |  | 10.6671 | 9.4161 | 9.1162 | 8.9641 | -0.10834 | -0.0099498 | 12.7254 |  |  | 10.5559 |  |  | 16.8573 | 16.0518 | 15.0153 | 16.3686 | 15.6662 | 14.7643 | 10.488 | 10.663 | 11.498 | 11.4241 | 9.3764 |  | 10.5099 | 8.3917 | 9.9072 | 9.4064 | 10.9562 | 11.9197 |  | 12.2122 |  |  | 11.5782 | 12.4253 | 12.4046 | [6 empty] | 12.4491 |  |  | 11.295 |  |  | 9.4101 | 10.2451 | 11.7643 | 7.6538 | 9.3887 | 12.6141 | 8.1144 | 9.735 | 12.3803 | 9.1705 | 10.3997 | 7.8508 | 10.6536 | 8.4172 | 10.5493 | 8.0559 | 9.918 | 13.0937 | 10.5961 | 10.2851 | 11.4207 | 8.3459 | 9.9321 | 12.7448 | 8.1988 | 10.7581 | 9.7192 | 10.0311 | 8.4724 | 10.6377 | 0.090895 | 20.9496 | 0.034997 | 0.049383 | -37.7926 | 3.1199 | 8.93 | 0.29 | 0.39223 | -0.42531 | 0.20863 | -0.13683 | 0.53142 | -0.24037 | 0.38251 | 0.39858 | 0.40608 | 0.41246 | 0.42107 | 0.58038 | 0.42153 | 0.41521
42810.4392 | -76 | 18.3607 | 18.5112 | 18.5314 | 18.5412 | 17.8828 | 16.5304 | 14.5998 | 16.6783 | 17.1718 | 17.2668 | 17.2648 | 16.8083 | 15.8317 | 14.4557 | 14.7656 | 14.8123 | 15.393 | 13.2818 | 13.3993 | 13.9782 |  |  |  | 16.5654 | 15.9033 | 15.0021 | 10.3438 | 9.8277 | 9.8596 | 17.043 | 16.1968 | 15.0249 | 16.7834 | 16.0743 | 15.0711 | 10.7454 | 11.6323 |  | 12.0053 | 10.9499 | 10.4734 | 8.8812 |  | 6.1998 | 6.2629 | 5.8513 | 5.9617 | 6.1746 | 6.6526 | 7.3656 | 4.5138 | 6.4792 | 4.4798 | 6.6961 | 7.9469 | 42.1185 | 46.4832 | 42.8826 | 15.1259 |  |  | 0.054759 | 0.10588 | -0.15848 | -0.11762 | 0.3964 | -0.2068 | -0.088808 | -0.19664 | -0.65481 | -0.28319 | -0.13781 | 8.8702 | 8.8713 | 2.0081 | 15.628 | 16.5848 | 17.156 | 17.5097 | 17.4814 | 16.4698 | 14.8314 | 16.8247 | 17.1689 | 17.482 | 17.539 | 17.2849 | 16.5006 | 14.74 | 5.9379 | 8.1774 | 5.4842 | 5.854 | 6.4217 | 6.5905 | 7.6111 | 15.6556 | 15.3408 | 15.2394 | 14.189 | 14.1047 | 14.0556 |  |  |  | 10.6576 | 9.4007 | 9.122 | 9.0089 | -0.021022 | 0.11727 | 12.7198 |  |  | 10.5614 |  |  | 16.855 | 16.0635 | 15.0261 | 16.3675 | 15.6625 | 14.7627 | 10.4812 | 10.6535 | 11.5055 | 11.4349 | 9.4059 |  | 10.5114 | 8.3193 | 9.9064 | 9.3885 | 10.9507 | 12.0033 |  | 12.2064 |  |  | 11.5898 | 12.4322 | 12.4292 | [6 empty] | 12.4546 |  |  | 11.306 |  |  | 9.4134 | 10.2472 | 11.7734 | 7.6373 | 9.3822 | 12.6086 | 8.1212 | 9.7248 | 12.379 | 9.1771 | 10.4099 | 7.8462 | 10.6277 | 8.4168 | 10.556 | 8.0702 | 9.8783 | 13.0817 | 10.5841 | 10.2779 | 11.3997 | 8.3345 | 9.9289 | 12.7373 | 8.1691 | 10.743 | 9.7142 | 10.0185 | 8.4703 | 10.6359 | 0.17159 | 20.9514 | 0.034704 | 0.049072 | -37.7703 | 3.1199 | -1.84 | 0.37 | 0.27434 | 0.37906 | -0.46375 | -0.39952 | 0.73394 | -0.53011 | -0.34739 | 0.39781 | 0.40806 | 0.41277 | 0.41973 | 0.58864 | 0.4201 | 0.41366
42810.4392 | -75 | 18.3654 | 18.5164 | 18.5316 | 18.544 | 17.8823 | 16.5324 | 14.6025 | 16.6803 | 17.1716 | 17.2618 | 17.269 | 16.8077 | 15.8273 | 14.4598 | 14.7723 | 14.8152 | 15.3999 | 13.282 | 13.4058 | 13.9873 |  |  |  | 16.5708 | 15.9004 | 14.9999 | 10.346 | 9.8121 | 9.8699 | 17.0389 | 16.2046 | 15.0203 | 16.7854 | 16.0727 | 15.0733 | 10.7445 | 11.599 |  | 12.0064 | 10.9274 | 10.4929 | 8.932 |  | 6.205 | 6.2464 | 5.8419 | 5.9412 | 6.1358 | 6.6209 | 7.3453 | 4.5188 | 6.4775 | 4.4503 | 6.7008 | 7.943 | 42.0992 | 46.4737 | 42.8739 | 15.1286 |  |  | 0.13427 | -0.11162 | -0.14337 | -0.45407 | 0.33792 | -0.058944 | 0.14775 | -0.27878 | -0.63944 | -1.3213 | -0.37744 | 8.8667 | 8.868 | 2.0082 | 15.6316 | 16.5843 | 17.1606 | 17.5107 | 17.486 | 16.4734 | 14.8385 | 16.8293 | 17.1841 | 17.4877 | 17.5493 | 17.2936 | 16.5044 | 14.7383 | 5.9427 | 8.2049 | 5.458 | 5.7742 | 6.3154 | 6.5982 | 7.6076 | 15.656 | 15.3421 | 15.2455 | 14.1962 | 14.1063 | 14.0491 |  |  |  | 10.6535 | 9.4061 | 9.1278 | 9.0747 | -0.16851 | 0.02355 | 12.7183 |  |  | 10.527 |  |  | 16.8525 | 16.0542 | 15.0168 | 16.3667 | 15.6531 | 14.7587 | 10.456 | 10.6484 | 11.5049 | 11.4373 | 9.3866 |  | 10.5086 | 8.2521 | 9.9038 | 9.3727 | 10.9486 | 11.9325 |  | 12.2127 |  |  | 11.5733 | 12.4266 | 12.4404 | [6 empty] | 12.464 |  |  | 11.2991 |  |  | 9.4255 | 10.2451 | 11.7836 | 7.6038 | 9.3677 | 12.6093 | 8.1272 | 9.7191 | 12.381 | 9.1888 | 10.4188 | 7.8107 | 10.6192 | 8.4169 | 10.5596 | 8.0928 | 9.8567 | 13.0722 | 10.5882 | 10.2796 | 11.4008 | 8.3393 | 9.9397 | 12.7328 | 8.1549 | 10.7346 | 9.7142 | 10.0199 | 8.4902 | 10.6418 | 0.079532 | 20.9509 | 0.034078 | 0.048739 | -37.7786 | 3.1199 | 13.12 | 0.33 | 0.4296 | -0.38918 | -0.44107 | -0.78494 | 0.6776 | -0.283 | 0.44806 | 0.39825 | 0.40985 | 0.41314 | 0.42009 | 0.59115 | 0.41866 | 0.41169
42810.4392 | -74 | 18.3638 | 18.5203 | 18.5309 | 18.5419 | 17.8849 | 16.53 | 14.605 | 16.6802 | 17.1769 | 17.2649 | 17.2706 | 16.8008 | 15.8361 | 14.4544 | 14.7744 | 14.813 | 15.394 | 13.2784 | 13.411 | 13.9903 |  |  |  | 16.5625 | 15.9037 | 15.0028 | 10.3423 | 9.8028 | 9.8661 | 17.0334 | 16.2006 | 15.0138 | 16.7743 | 16.0719 | 15.0676 | 10.7363 | 11.5889 |  | 11.993 | 10.9052 | 10.4928 | 8.9597 |  | 6.2055 | 6.2434 | 5.8283 | 5.9335 | 6.1238 | 6.6052 | 7.3084 | 4.5118 | 6.4799 | 4.3884 | 6.7 | 7.9471 | 42.0912 | 46.4619 | 42.8785 | 15.1305 |  |  | 0.086959 | 0.063171 | -0.043492 | -0.14654 | -0.097748 | -0.48081 | 0.41191 | -0.10202 | -0.85856 | -0.46635 | -0.67191 | 8.8696 | 8.8708 | 2.0086 | 15.6314 | 16.5714 | 17.156 | 17.4981 | 17.478 | 16.4605 | 14.8273 | 16.8231 | 17.177 | 17.4823 | 17.5388 | 17.2852 | 16.4889 | 14.7352 | 5.9396 | 8.1905 | 5.4007 | 5.7239 | 6.2292 | 6.5888 | 7.6175 | 15.6613 | 15.342 | 15.2458 | 14.1936 | 14.1011 | 14.0592 |  |  |  | 10.6655 | 9.4076 | 9.1362 | 9.1275 | -0.076331 | 0.065142 | 12.709 |  |  | 10.5283 |  |  | 16.8552 | 16.0615 | 15.0251 | 16.3707 | 15.6653 | 14.7613 | 10.4437 | 10.6499 | 11.512 | 11.451 | 9.3963 |  | 10.5238 | 8.1855 | 9.9086 | 9.3776 | 10.9496 | 11.9558 |  | 12.2167 |  |  | 11.5476 | 12.4313 | 12.4639 | [6 empty] | 12.4442 |  |  | 11.2816 |  |  | 9.4264 | 10.2531 | 11.7808 | 7.5822 | 9.3144 | 12.5893 | 8.1222 | 9.7056 | 12.3735 | 9.1835 | 10.4273 | 7.77 | 10.5967 | 8.4206 | 10.5495 | 8.0976 | 9.8342 | 13.056 | 10.5693 | 10.2651 | 11.3837 | 8.3375 | 9.938 | 12.7282 | 8.1453 | 10.7172 | 9.697 | 10.0134 | 8.5002 | 10.6381 | -0.034102 | 20.951 | 0.0339 | 0.047154 | -37.8458 | 3.1199 | 7.05 | 0.21 | 0.34572 | 0.29277 | -0.24293 | -0.44591 | -0.36443 | -0.80825 | 0.7481 | 0.39848 | 0.41185 | 0.41304 | 0.41934 | 0.59866 | 0.41762 | 0.41062
42810.4392 | -73 | 18.363 | 18.511 | 18.5246 | 18.5386 | 17.8851 | 16.5243 | 14.6068 | 16.6742 | 17.1739 | 17.2592 | 17.2665 | 16.797 | 15.8315 | 14.449 | 14.7783 | 14.8229 | 15.4052 | 13.2842 | 13.4025 | 13.9886 |  |  |  | 16.5635 | 15.8985 | 15.0081 | 10.3455 | 9.7901 | 9.845 | 17.0445 | 16.2042 | 15.0171 | 16.7767 | 16.0762 | 15.0809 | 10.7384 | 11.5925 |  | 11.9922 | 10.8824 | 10.521 | 8.9897 |  | 6.1925 | 6.2377 | 5.812 | 5.9169 | 6.1012 | 6.5849 | 7.2647 | 4.5189 | 6.4789 | 4.4094 | 6.6886 | 7.9451 | 42.0765 | 46.4549 | 42.8847 | 15.1348 |  |  | 0.18093 | -0.21085 | 0.025508 | -0.20502 | 0.042876 | -0.47556 | 0.43426 | -0.15787 | -0.49836 | -0.81336 | -0.28246 | 8.8713 | 8.8726 | 2.0084 | 15.6284 | 16.5723 | 17.1544 | 17.5013 | 17.4772 | 16.4587 | 14.8311 | 16.8238 | 17.1745 | 17.482 | 17.5364 | 17.2826 | 16.4933 | 14.7401 | 5.9148 | 8.1781 | 5.3802 | 5.7084 | 6.1581 | 6.5853 | 7.6172 | 15.6609 | 15.3423 | 15.242 | 14.1905 | 14.1079 | 14.06 |  |  |  | 10.666 | 9.4124 | 9.145 | 9.178 | -0.17986 | -0.094263 | 12.7214 |  |  | 10.5303 |  |  | 16.8515 | 16.0562 | 15.019 | 16.3626 | 15.6612 | 14.7589 | 10.4165 | 10.6385 | 11.5128 | 11.4469 | 9.3914 |  | 10.5107 | 8.1283 | 9.9056 | 9.405 | 10.9418 | 11.9626 |  | 12.2008 |  |  | 11.5081 | 12.4537 | 12.4821 | [6 empty] | 12.4484 |  |  | 11.2844 |  |  | 9.422 | 10.2658 | 11.7848 | 7.5694 | 9.2577 | 12.5693 | 8.1118 | 9.7084 | 12.3692 | 9.1837 | 10.4368 | 7.7216 | 10.5609 | 8.4083 | 10.5517 | 8.0891 | 9.8225 | 13.0494 | 10.5546 | 10.2675 | 11.3652 | 8.3339 | 9.9511 | 12.7287 | 8.1512 | 10.7199 | 9.6964 | 10.0254 | 8.5073 | 10.6405 | -0.0042494 | 20.9508 | 0.032517 | 0.047473 | -37.8125 | 3.1199 | 7.19 | 0.36 | 0.49866 | -0.53487 | 0.18604 | -0.52744 | 0.24135 | -0.80379 | 0.76809 | 0.39819 | 0.41334 | 0.41202 | 0.42169 | 0.6009 | 0.41685 | 0.40923
42810.4392 | -72 | 18.3554 | 18.5118 | 18.5288 | 18.5292 | 17.8734 | 16.512 | 14.599 | 16.6772 | 17.1587 | 17.2637 | 17.261 | 16.7935 | 15.8363 | 14.4556 | 14.7732 | 14.8122 | 15.3921 | 13.2821 | 13.4017 | 13.9724 |  |  |  | 16.5706 | 15.9026 | 15.0078 | 10.3349 | 9.7704 | 9.8492 | 17.0458 | 16.2046 | 15.0224 | 16.785 | 16.0815 | 15.0873 | 10.7518 | 11.5882 |  | 12.0074 | 10.8693 | 10.5458 | 9.0217 |  | 6.1844 | 6.229 | 5.8121 | 5.9175 | 6.0941 | 6.5669 | 7.2356 | 4.5496 | 6.4717 | 4.4523 | 6.6881 | 7.9382 | 42.0647 | 46.4584 | 42.8975 | 15.1293 |  |  | 0.12047 | 0.056599 | -0.021148 | 0.021026 | -0.13257 | -0.62406 | 0.23252 | -0.424 | -0.81828 | -0.26116 | -0.41281 | 8.8666 | 8.8678 | 2.0082 | 15.6306 | 16.5791 | 17.155 | 17.5083 | 17.4808 | 16.4613 | 14.8373 | 16.8311 | 17.1818 | 17.4848 | 17.5388 | 17.2845 | 16.5014 | 14.7397 | 5.8898 | 8.1764 | 5.363 | 5.6617 | 6.107 | 6.5811 | 7.6154 | 15.6577 | 15.3407 | 15.2364 | 14.192 | 14.105 | 14.0499 |  |  |  | 10.6594 | 9.4181 | 9.1458 | 9.2424 | 0.029223 | -0.048907 | 12.7205 |  |  | 10.5226 |  |  | 16.8543 | 16.0529 | 15.0214 | 16.3577 | 15.6551 | 14.7628 | 10.4103 | 10.6339 | 11.5087 | 11.4504 | 9.3565 |  | 10.5225 | 8.0245 | 9.9025 | 9.4377 | 10.9479 | 12.0173 |  | 12.2119 |  |  | 11.3985 | 12.3737 | 12.4759 | [6 empty] | 12.4705 |  |  | 11.2809 |  |  | 9.4259 | 10.2637 | 11.789 | 7.5538 | 9.2277 | 12.5505 | 8.0968 | 9.7076 | 12.3573 | 9.1892 | 10.4405 | 7.6871 | 10.5292 | 8.42 | 10.5506 | 8.0862 | 9.7973 | 13.0375 | 10.5377 | 10.2682 | 11.3538 | 8.3229 | 9.9443 | 12.7082 | 8.1372 | 10.721 | 9.685 | 10.0148 | 8.5181 | 10.6431 | 0.071828 | 20.9509 | 0.032311 | 0.047632 | -37.7595 | 3.1199 | 19.61 | 0.29 | 0.40691 | 0.27712 | -0.16939 | 0.1689 | -0.42438 | -0.92075 | 0.56203 | 0.39955 | 0.41613 | 0.41131 | 0.42399 | 0.6026 | 0.41641 | 0.40723
42810.4392 | -71 | 18.3636 | 18.5122 | 18.5293 | 18.5315 | 17.8805 | 16.5227 | 14.5972 | 16.6748 | 17.1644 | 17.2604 | 17.2684 | 16.8015 | 15.8314 | 14.4569 | 14.767 | 14.8117 | 15.3944 | 13.2792 | 13.4037 | 13.984 |  |  |  | 16.5629 | 15.9036 | 14.9997 | 10.3321 | 9.7802 | 9.8965 | 17.035 | 16.2057 | 15.0172 | 16.7832 | 16.0742 | 15.0727 | 10.741 | 11.5836 |  | 11.9963 | 10.8369 | 10.562 | 9.0413 |  | 6.1881 | 6.2259 | 5.8078 | 5.9127 | 6.0803 | 6.5397 | 7.1836 | 4.5823 | 6.4636 | 4.4458 | 6.6885 | 7.9428 | 42.0537 | 46.4618 | 42.9169 | 15.1295 |  |  | -0.039209 | 0.090771 | -0.022464 | -0.14522 | -0.17266 | -0.47687 | -0.44234 | -0.19401 | -0.29636 | -0.61636 | -0.61369 | 8.8706 | 8.8722 | 2.0085 | 15.6256 | 16.5805 | 17.1526 | 17.5024 | 17.4848 | 16.4662 | 14.8305 | 16.8279 | 17.1799 | 17.484 | 17.5414 | 17.2805 | 16.4948 | 14.736 | 5.906 | 8.1842 | 5.328 | 5.6554 | 6.059 | 6.5882 | 7.626 | 15.6618 | 15.3386 | 15.2455 | 14.1872 | 14.1016 | 14.0587 |  |  |  | 10.6631 | 9.4255 | 9.1434 | 9.2882 | -0.021629 | 0.057049 | 12.7111 |  |  | 10.5206 |  |  | 16.8455 | 16.044 | 15.016 | 16.3692 | 15.6451 | 14.7555 | 10.4019 | 10.6307 | 11.5081 | 11.4531 | 9.2523 |  | 10.5115 | 7.9589 | 9.9087 | 9.4647 | 10.949 | 12.0462 |  | 12.2137 |  |  | 11.3771 | 12.3208 | 12.4469 | [6 empty] | 12.495 |  |  | 11.2699 |  |  | 9.4333 | 10.2679 | 11.7956 | 7.5608 | 9.2004 | 12.5213 | 8.1011 | 9.7013 | 12.3548 | 9.1743 | 10.4599 | 7.661 | 10.5062 | 8.432 | 10.5448 | 8.0624 | 9.7834 | 13.0402 | 10.5357 | 10.268 | 11.3557 | 8.3088 | 9.9506 | 12.7196 | 8.1496 | 10.7144 | 9.6767 | 10.0227 | 8.5243 | 10.6356 | -0.0050198 | 20.9513 | 0.03289 | 0.047451 | -37.8267 | 3.12 | 4.65 | 0.3 | -0.23216 | 0.35094 | -0.17458 | -0.44389 | -0.48428 | -0.80483 | -0.77514 | 0.40208 | 0.41815 | 0.4106 | 0.423 | 0.60773 | 0.4155 | 0.40608
42810.4392 | -70 | 18.3701 | 18.5188 | 18.5277 | 18.5331 | 17.8903 | 16.537 | 14.6042 | 16.6763 | 17.1778 | 17.2692 | 17.2727 | 16.805 | 15.8417 | 14.4641 | 14.7754 | 14.8066 | 15.391 | 13.2754 | 13.3962 | 13.9765 |  |  |  | 16.5604 | 15.8973 | 14.9984 | 10.3378 | 9.7623 | 9.9427 | 17.039 | 16.201 | 15.0189 | 16.7845 | 16.0692 | 15.0715 | 10.7461 | 11.577 |  | 12.0035 | 10.8343 | 10.5848 | 9.0463 |  | 6.1843 | 6.2198 | 5.7967 | 5.9017 | 6.0613 | 6.5111 | 7.1168 | 4.643 | 6.4715 | 4.437 | 6.6854 | 7.9519 | 42.0544 | 46.471 | 42.9104 | 15.1198 |  |  | 0.060015 | -0.026853 | 0.064932 | -0.00723 | -0.01298 | -0.065516 | -0.011928 | -0.40823 | -0.56432 | -0.16298 | -0.291 | 8.87 | 8.8711 | 2.0085 | 15.6224 | 16.5755 | 17.1534 | 17.5034 | 17.4796 | 16.4748 | 14.8255 | 16.8251 | 17.1798 | 17.4793 | 17.5444 | 17.2861 | 16.4913 | 14.7366 | 5.8964 | 8.2216 | 5.3183 | 5.6419 | 6.0239 | 6.5802 | 7.6326 | 15.6537 | 15.338 | 15.2362 | 14.1854 | 14.1007 | 14.0547 |  |  |  | 10.6641 | 9.4361 | 9.1602 | 9.3309 | -0.23659 | 0.011129 | 12.7233 |  |  | 10.5309 |  |  | 16.8622 | 16.0534 | 15.0224 | 16.3686 | 15.6522 | 14.7625 | 10.3924 | 10.6669 | 11.5171 | 11.453 | 9.1572 |  | 10.5033 | 7.8982 | 9.9091 | 9.5055 | 10.9481 | 12.0933 |  | 12.214 |  |  | 11.3547 | 12.3051 | 12.4233 | [6 empty] | 12.4921 |  |  | 11.2337 |  |  | 9.4271 | 10.2731 | 11.791 | 7.5284 | 9.1855 | 12.5029 | 8.1017 | 9.7148 | 12.3425 | 9.1836 | 10.4822 | 7.6501 | 10.4991 | 8.4277 | 10.5435 | 8.051 | 9.7624 | 13.0249 | 10.5194 | 10.2677 | 11.3393 | 8.3044 | 9.9453 | 12.7079 | 8.1227 | 10.7088 | 9.6708 | 10.0112 | 8.5297 | 10.6292 | 0.060464 | 20.9499 | 0.033453 | 0.04845 | -37.8793 | 3.1199 | 19.6 | 0.33 | 0.28725 | -0.19088 | 0.29682 | -0.099043 | -0.13278 | -0.2983 | -0.12728 | 0.40445 | 0.41985 | 0.40944 | 0.42316 | 0.60957 | 0.41553 | 0.40492
42810.4392 | -69 | 18.3608 | 18.5042 | 18.5201 | 18.5286 | 17.8777 | 16.5255 | 14.5952 | 16.6716 | 17.1624 | 17.2522 | 17.2628 | 16.7984 | 15.8295 | 14.4481 | 14.7761 | 14.8109 | 15.3983 | 13.2785 | 13.4002 | 13.9821 |  |  |  | 16.5618 | 15.9014 | 15.0083 | 10.3354 | 9.7648 | 9.9853 | 17.0428 | 16.1956 | 15.0163 | 16.7782 | 16.0704 | 15.0725 | 10.7432 | 11.5839 |  | 12.0066 | 10.8215 | 10.5998 | 9.019 |  | 6.1752 | 6.2201 | 5.7913 | 5.8879 | 6.0395 | 6.4859 | 7.0637 | 4.6585 | 6.473 | 4.4677 | 6.6793 | 7.9467 | 42.0619 | 46.4741 | 42.9177 | 15.1082 |  |  | 0.13624 | -0.16353 | 0.028136 | 0.24116 | 0.044848 | -0.27973 | 0.17995 | -0.2755 | -0.66318 | -0.52866 | -0.5817 | 8.8709 | 8.872 | 2.0081 | 15.6329 | 16.5824 | 17.1534 | 17.4984 | 17.4835 | 16.464 | 14.8277 | 16.8275 | 17.1806 | 17.4813 | 17.5403 | 17.2929 | 16.4919 | 14.7413 | 5.9207 | 8.243 | 5.3482 | 5.7031 | 6.0065 | 6.5766 | 7.6382 | 15.66 | 15.3474 | 15.2425 | 14.2024 | 14.1074 | 14.0588 |  |  |  | 10.6754 | 9.4615 | 9.2199 | 9.3986 | -0.16568 | 0.12593 | 12.7244 |  |  | 10.5335 |  |  | 16.8544 | 16.0525 | 15.0189 | 16.3647 | 15.6561 | 14.7697 | 10.3676 | 10.7053 | 11.5176 | 11.4524 | 9.0807 |  | 10.5032 | 7.8315 | 9.9002 | 9.5459 | 10.9424 | 12.1725 |  | 12.2048 |  |  | 11.3704 | 12.2911 | 12.4103 | [6 empty] | 12.5031 |  |  | 11.2454 |  |  | 9.4324 | 10.2843 | 11.802 | 7.5014 | 9.1784 | 12.4927 | 8.1094 | 9.7149 | 12.3291 | 9.209 | 10.5052 | 7.6625 | 10.4863 | 8.4522 | 10.55 | 8.0497 | 9.74 | 13.0254 | 10.5246 | 10.2667 | 11.342 | 8.3142 | 9.9521 | 12.7024 | 8.1214 | 10.7056 | 9.666 | 10.0084 | 8.5234 | 10.6277 | 0.14559 | 20.9493 | 0.033699 | 0.050368 | -37.789 | 3.1199 | 14.32 | 0.35 | 0.43283 | -0.47104 | 0.19538 | 0.57202 | 0.24679 | -0.61636 | 0.49436 | 0.40657 | 0.42141 | 0.40813 | 0.42003 | 0.6069 | 0.4162 | 0.40342
42810.4392 | -68 | 18.3632 | 18.5083 | 18.5232 | 18.5374 | 17.8771 | 16.5282 | 14.6033 | 16.6804 | 17.1662 | 17.2558 | 17.2658 | 16.8017 | 15.8274 | 14.4569 | 14.7709 | 14.8112 | 15.3934 | 13.2654 | 13.3943 | 13.9767 |  |  |  | 16.5538 | 15.8913 | 14.9943 | 10.3382 | 9.7485 | 10.0435 | 17.0407 | 16.1986 | 15.0202 | 16.7808 | 16.0647 | 15.0746 | 10.7457 | 11.5782 |  | 11.9995 | 10.805 | 10.6002 | 8.9963 |  | 6.1743 | 6.225 | 5.7943 | 5.8838 | 6.0243 | 6.4676 | 7.0215 | 4.6669 | 6.4695 | 4.5833 | 6.6846 | 7.9399 | 42.0581 | 46.462 | 42.913 | 15.0933 |  |  | 0.057387 | -0.075481 | 0.061648 | -0.01577 | -0.10563 | 0.12374 | 0.4198 | -0.096104 | -0.87783 | -0.26599 | -0.35061 | 8.8699 | 8.8708 | 2.0083 | 15.6373 | 16.58 | 17.1551 | 17.503 | 17.4818 | 16.4554 | 14.8301 | 16.8238 | 17.1831 | 17.485 | 17.5343 | 17.287 | 16.4957 | 14.7447 | 5.9414 | 8.2375 | 5.4264 | 5.6965 | 6.0199 | 6.5848 | 7.6475 | 15.6652 | 15.3436 | 15.2376 | 14.1959 | 14.1028 | 14.0541 |  |  |  | 10.6748 | 9.4811 | 9.2689 | 9.4439 | 0.057182 | -0.011079 | 12.7194 |  |  | 10.5323 |  |  | 16.8478 | 16.0521 | 15.0191 | 16.3678 | 15.6537 | 14.7615 | 10.3363 | 10.7253 | 11.5282 | 11.4513 | 9.0402 |  | 10.5126 | 7.821 | 9.907 | 9.5892 | 10.9559 | 12.253 |  | 12.2109 |  |  | 11.3782 | 12.2538 | 12.3843 | [6 empty] | 12.5291 |  |  | 11.2633 |  |  | 9.4477 | 10.2802 | 11.7953 | 7.497 | 9.1414 | 12.4685 | 8.1104 | 9.712 | 12.3148 | 9.2062 | 10.506 | 7.6639 | 10.4732 | 8.4506 | 10.5433 | 8.0402 | 9.7361 | 13.0371 | 10.521 | 10.2653 | 11.3202 | 8.3243 | 9.9629 | 12.7105 | 8.1165 | 10.691 | 9.6707 | 10.0059 | 8.5233 | 10.6266 | -0.034873 | 20.9516 | 0.034394 | 0.049803 | -37.8534 | 3.1199 | 1.17 | 0.26 | 0.28094 | -0.32002 | 0.28921 | -0.14628 | -0.37875 | 0.40992 | 0.75504 | 0.408 | 0.42193 | 0.40737 | 0.41869 | 0.59928 | 0.41691 | 0.40214
42810.4393 | -67 | 18.3665 | 18.5166 | 18.533 | 18.5433 | 17.8884 | 16.5318 | 14.6019 | 16.685 | 17.1678 | 17.2631 | 17.2731 | 16.8097 | 15.8343 | 14.4613 | 14.7782 | 14.8203 | 15.4011 | 13.2729 | 13.4068 | 13.9864 |  |  |  | 16.5677 | 15.8991 | 15.0017 | 10.3539 | 9.7537 | 10.1159 | 17.0456 | 16.205 | 15.0232 | 16.7806 | 16.0734 | 15.0724 | 10.7501 | 11.5457 |  | 12.0058 | 10.7965 | 10.6055 | 8.9651 |  | 6.1791 | 6.2153 | 5.7928 | 5.8794 | 6.0224 | 6.4648 | 6.9967 | 4.6891 | 6.4694 | 4.6409 | 6.6796 | 7.9384 | 42.0476 | 46.4483 | 42.9152 | 15.0812 |  |  | 0.063959 | 0.047399 | 0.13064 | 0.15771 | -0.172 | -0.09114 | 0.40403 | -0.070476 | -0.49252 | -0.76426 | -0.33233 | 8.8633 | 8.8643 | 2.0084 | 15.6346 | 16.5785 | 17.151 | 17.4967 | 17.4765 | 16.4653 | 14.8271 | 16.8212 | 17.1829 | 17.4819 | 17.5392 | 17.2819 | 16.4995 | 14.7332 | 5.941 | 8.2472 | 5.4367 | 5.6862 | 6.0148 | 6.5738 | 7.6407 | 15.6587 | 15.338 | 15.2264 | 14.1833 | 14.0889 | 14.04 |  |  |  | 10.6586 | 9.4971 | 9.2963 | 9.4655 | 0.11594 | 0.001154 | 12.7234 |  |  | 10.5315 |  |  | 16.8568 | 16.0561 | 15.0229 | 16.372 | 15.6654 | 14.7687 | 10.3127 | 10.7494 | 11.5268 | 11.4509 | 9.0013 |  | 10.5041 | 7.8193 | 9.9055 | 9.6059 | 10.95 | 12.3045 |  | 12.2041 |  |  | 11.3916 | 12.2423 | 12.3705 | [6 empty] | 12.5432 |  |  | 11.2801 |  |  | 9.4564 | 10.2927 | 11.8168 | 7.4997 | 9.1331 | 12.4723 | 8.1184 | 9.7125 | 12.3029 | 9.2184 | 10.514 | 7.6705 | 10.4826 | 8.4589 | 10.5539 | 8.0275 | 9.7143 | 13.0434 | 10.5268 | 10.2553 | 11.2908 | 8.3216 | 9.9654 | 12.7158 | 8.1086 | 10.6804 | 9.6637 | 9.9927 | 8.5211 | 10.6163 | -0.13965 | 20.9514 | 0.034394 | 0.049673 | -37.8081 | 3.12 | -8.81 | 0.31 | 0.29663 | 0.25359 | 0.42102 | 0.46257 | -0.48329 | -0.3518 | 0.74072 | 0.40881 | 0.42192 | 0.40671 | 0.41745 | 0.59736 | 0.41792 | 0.401
42810.4393 | -66 | 18.3772 | 18.5164 | 18.5355 | 18.546 | 17.8859 | 16.5331 | 14.6007 | 16.6807 | 17.1714 | 17.2645 | 17.2721 | 16.8093 | 15.8411 | 14.4545 | 14.7768 | 14.823 | 15.4071 | 13.2858 | 13.415 | 13.9868 |  |  |  | 16.5715 | 15.9029 | 15.0072 | 10.3744 | 9.7555 | 10.2023 | 17.0557 | 16.2136 | 15.023 | 16.7854 | 16.0809 | 15.0855 | 10.7511 | 11.5211 |  | 12.0092 | 10.7921 | 10.6098 | 8.9348 |  | 6.1802 | 6.2181 | 5.7964 | 5.8768 | 6.0376 | 6.4752 | 7.0215 | 4.7113 | 6.473 | 4.6358 | 6.6775 | 7.9442 | 42.0519 | 46.4432 | 42.9191 | 15.0757 |  |  | -0.022121 | -0.039997 | 0.051792 | -0.000658 | -0.1122 | 0.25713 | 0.45265 | -0.21373 | -0.41565 | -1.2923 | -0.19543 | 8.8694 | 8.8702 | 2.0082 | 15.633 | 16.5843 | 17.1555 | 17.5025 | 17.4735 | 16.4697 | 14.825 | 16.827 | 17.1787 | 17.4868 | 17.5451 | 17.2866 | 16.4971 | 14.745 | 5.9309 | 8.2596 | 5.424 | 5.7229 | 6.0196 | 6.5796 | 7.652 | 15.6582 | 15.3293 | 15.2333 | 14.1708 | 14.0852 | 14.0405 |  |  |  | 10.6635 | 9.5205 | 9.3037 | 9.4879 | 0.10317 | -0.042132 | 12.7297 |  |  | 10.5292 |  |  | 16.8556 | 16.0494 | 15.0098 | 16.3681 | 15.6563 | 14.7696 | 10.2885 | 10.7657 | 11.5202 | 11.4357 | 8.9727 |  | 10.4952 | 7.8395 | 9.901 | 9.6115 | 10.9467 | 12.3059 |  | 12.2031 |  |  | 11.4324 | 12.2278 | 12.3591 | [6 empty] | 12.5456 |  |  | 11.286 |  |  | 9.4636 | 10.3015 | 11.8254 | 7.4984 | 9.1272 | 12.469 | 8.1279 | 9.7007 | 12.2922 | 9.229 | 10.5167 | 7.6812 | 10.4781 | 8.4635 | 10.5519 | 8.0231 | 9.7105 | 13.0508 | 10.5269 | 10.2586 | 11.2876 | 8.3248 | 9.9675 | 12.721 | 8.1069 | 10.6819 | 9.6658 | 9.9888 | 8.5202 | 10.6128 | -0.16122 | 20.9523 | 0.034095 | 0.049441 | -37.722 | 3.1199 | 10.66 | 0.3 | -0.17447 | -0.23295 | 0.26509 | -0.029879 | -0.39035 | 0.59092 | 0.78404 | 0.40931 | 0.42121 | 0.40645 | 0.41924 | 0.60007 | 0.4188 | 0.40054
42810.4393 | -65 | 18.3705 | 18.5161 | 18.5312 | 18.5309 | 17.8896 | 16.5239 | 14.5991 | 16.6838 | 17.1665 | 17.2669 | 17.2699 | 16.8037 | 15.8288 | 14.4569 | 14.7693 | 14.8129 | 15.3991 | 13.2787 | 13.4015 | 13.9819 |  |  |  | 16.5628 | 15.8975 | 15.0087 | 10.3828 | 9.7591 | 10.2995 | 17.0392 | 16.1999 | 15.012 | 16.7796 | 16.0735 | 15.0799 | 10.7348 | 11.5088 |  | 12.007 | 10.7784 | 10.5994 | 8.9067 |  | 6.2077 | 6.2293 | 5.8077 | 5.8886 | 6.1095 | 6.5358 | 7.0505 | 4.6977 | 6.4716 | 4.6534 | 6.6782 | 7.9396 | 42.0515 | 46.429 | 42.915 | 15.0622 |  |  | 0.1737 | -0.039337 | 0.018936 | 0.051254 | -0.040576 | -0.011632 | 0.57356 | -0.24724 | -0.40222 | -0.14305 | -0.32697 | 8.8683 | 8.8694 | 2.0082 | 15.6265 | 16.5784 | 17.155 | 17.5076 | 17.4746 | 16.4625 | 14.8238 | 16.8242 | 17.1728 | 17.4833 | 17.5405 | 17.2759 | 16.4915 | 14.7358 | 5.924 | 8.2699 | 5.3997 | 5.7283 | 6.0089 | 6.5807 | 7.6478 | 15.6575 | 15.3354 | 15.2366 | 14.1733 | 14.089 | 14.0504 |  |  |  | 10.6623 | 9.5483 | 9.3202 | 9.5008 | 0.069135 | 0.055732 | 12.7286 |  |  | 10.5312 |  |  | 16.8594 | 16.0588 | 15.0211 | 16.3696 | 15.6531 | 14.7677 | 10.2762 | 10.7828 | 11.5065 | 11.4126 | 8.9887 |  | 10.5088 | 7.8893 | 9.9057 | 9.6326 | 10.9495 | 12.304 |  | 12.2311 |  |  | 11.466 | 12.2097 | 12.3267 | [6 empty] | 12.544 |  |  | 11.297 |  |  | 9.4653 | 10.3025 | 11.8369 | 7.5097 | 9.1185 | 12.4818 | 8.131 | 9.7014 | 12.2763 | 9.2333 | 10.5218 | 7.6908 | 10.471 | 8.4674 | 10.5503 | 8.0102 | 9.6979 | 13.0548 | 10.5329 | 10.2539 | 11.3068 | 8.3264 | 9.9816 | 12.7323 | 8.1071 | 10.6835 | 9.6713 | 9.9848 | 8.5234 | 10.6089 | 0.045249 | 20.9525 | 0.033585 | 0.048703 | -37.7383 | 3.12 | 13.55 | 0.28 | 0.48899 | -0.23103 | 0.16029 | 0.26371 | -0.23477 | -0.1257 | 0.88266 | 0.40931 | 0.41999 | 0.40595 | 0.42014 | 0.60229 | 0.41904 | 0.40014
42810.4393 | -64 | 18.371 | 18.51 | 18.5291 | 18.5393 | 17.8888 | 16.527 | 14.6059 | 16.6821 | 17.1701 | 17.2652 | 17.2757 | 16.8062 | 15.8344 | 14.4624 | 14.7731 | 14.8124 | 15.3914 | 13.2775 | 13.4058 | 13.9811 |  |  |  | 16.5628 | 15.9003 | 15.0038 | 10.3964 | 9.7766 | 10.3874 | 17.0418 | 16.1971 | 15.013 | 16.7827 | 16.0702 | 15.0675 | 10.7446 | 11.5302 |  | 12.0027 | 10.7517 | 10.5841 | 8.9097 |  | 6.2183 | 6.2435 | 5.8121 | 5.885 | 6.1437 | 6.5625 | 7.0931 | 4.7067 | 6.4694 | 4.631 | 6.6816 | 7.9438 | 42.0635 | 46.4356 | 42.9083 | 15.0698 |  |  | 0.18356 | -0.10702 | 0.039308 | -0.036798 | -0.028092 | 0.16973 | 0.70696 | -0.11122 | -0.58943 | -0.3027 | -0.27213 | 8.8711 | 8.8724 | 2.0085 | 15.6316 | 16.5784 | 17.1531 | 17.5035 | 17.4804 | 16.4614 | 14.8259 | 16.8254 | 17.1717 | 17.4827 | 17.5415 | 17.2839 | 16.4935 | 14.7399 | 5.9209 | 8.2639 | 5.3729 | 5.6785 | 6.0218 | 6.5772 | 7.6526 | 15.6648 | 15.3394 | 15.2334 | 14.1872 | 14.0884 | 14.0513 |  |  |  | 10.6696 | 9.5663 | 9.3283 | 9.509 | 0.0097736 | -0.033475 | 12.7307 |  |  | 10.5254 |  |  | 16.8588 | 16.0524 | 15.0236 | 16.3684 | 15.6577 | 14.763 | 10.2511 | 10.7958 | 11.4885 | 11.3945 | 8.9931 |  | 10.5061 | 7.9172 | 9.9055 | 9.6546 | 10.9532 | 12.2826 |  | 12.2261 |  |  | 11.5034 | 12.1995 | 12.3057 | [6 empty] | 12.5607 |  |  | 11.3035 |  |  | 9.4686 | 10.3022 | 11.8489 | 7.5157 | 9.1148 | 12.4898 | 8.1275 | 9.7007 | 12.2598 | 9.225 | 10.5204 | 7.6986 | 10.4716 | 8.464 | 10.5416 | 8.0153 | 9.6989 | 13.0728 | 10.5422 | 10.2643 | 11.3279 | 8.3241 | 9.9939 | 12.747 | 8.1045 | 10.6841 | 9.6734 | 9.9906 | 8.5245 | 10.6084 | 0.15002 | 20.9514 | 0.033527 | 0.047748 | -37.7731 | 3.1199 | 6.08 | 0.28 | 0.50275 | -0.38107 | 0.23095 | -0.22345 | -0.19535 | 0.48018 | 0.97998 | 0.4091 | 0.4192 | 0.40546 | 0.42007 | 0.60582 | 0.41928 | 0.40016
42810.4393 | -63 | 18.3697 | 18.5186 | 18.5237 | 18.5334 | 17.8809 | 16.5255 | 14.5979 | 16.673 | 17.1626 | 17.2621 | 17.2709 | 16.8048 | 15.8353 | 14.4543 | 14.7769 | 14.8135 | 15.3944 | 13.2845 | 13.4097 | 13.9791 |  |  |  | 16.5682 | 15.9038 | 15.0038 | 10.4158 | 9.8034 | 10.473 | 17.0332 | 16.1892 | 15.0094 | 16.7761 | 16.0635 | 15.0656 | 10.7342 | 11.513 |  | 12.0004 | 10.7409 | 10.5743 | 8.9201 |  | 6.2209 | 6.259 | 5.8251 | 5.8935 | 6.174 | 6.5652 | 7.1257 | 4.7164 | 6.4753 | 4.6986 | 6.6805 | 7.9406 | 42.0678 | 46.4373 | 42.8996 | 15.0739 |  |  | 0.20852 | -0.15959 | 0.071504 | 0.10711 | 0.071132 | 0.039624 | 0.66293 | -0.42269 | 1.3081 | -0.5853 | -0.21053 | 8.8695 | 8.8708 | 2.0084 | 15.6291 | 16.5773 | 17.1524 | 17.4987 | 17.4764 | 16.4642 | 14.8255 | 16.8269 | 17.1749 | 17.4834 | 17.5364 | 17.2829 | 16.5 | 14.7392 | 5.9498 | 8.2514 | 5.362 | 5.652 | 6.0602 | 6.5848 | 7.6553 | 15.654 | 15.3326 | 15.2321 | 14.1858 | 14.0861 | 14.0526 |  |  |  | 10.6674 | 9.5704 | 9.3246 | 9.5238 | 0.014433 | -0.01616 | 12.7234 |  |  | 10.533 |  |  | 16.854 | 16.0524 | 15.0207 | 16.3587 | 15.6612 | 14.7609 | 10.2267 | 10.8094 | 11.4706 | 11.3718 | 8.984 |  | 10.5027 | 7.9676 | 9.9019 | 9.6599 | 10.9499 | 12.2539 |  | 12.2225 |  |  | 11.5261 | 12.2229 | 12.3214 | [6 empty] | 12.5648 |  |  | 11.3092 |  |  | 9.4791 | 10.3097 | 11.8545 | 7.5316 | 9.1159 | 12.5015 | 8.1258 | 9.7096 | 12.2483 | 9.2319 | 10.5186 | 7.7077 | 10.4773 | 8.469 | 10.5455 | 8.0304 | 9.7083 | 13.0815 | 10.5448 | 10.2689 | 11.3516 | 8.3232 | 9.9943 | 12.7596 | 8.0993 | 10.6868 | 9.6749 | 9.9934 | 8.5288 | 10.608 | 0.031189 | 20.9528 | 0.033648 | 0.048645 | -37.7343 | 3.12 | 14.32 | 0.28 | 0.53594 | -0.46537 | 0.3115 | 0.38124 | 0.31085 | 0.23201 | 0.94899 | 0.40924 | 0.41769 | 0.40521 | 0.41774 | 0.60735 | 0.41865 | 0.39967
42810.4393 | -62 | 18.3641 | 18.5062 | 18.5184 | 18.5311 | 17.8829 | 16.5257 | 14.5854 | 16.6716 | 17.1601 | 17.2562 | 17.2636 | 16.7984 | 15.8298 | 14.4557 | 14.7751 | 14.8106 | 15.394 | 13.2839 | 13.4062 | 13.9782 |  |  |  | 16.5623 | 15.8953 | 15.0048 | 10.4298 | 9.8187 | 10.5699 | 17.046 | 16.197 | 15.0104 | 16.7783 | 16.0748 | 15.0723 | 10.7403 | 11.4798 |  | 12.0122 | 10.7364 | 10.5704 | 8.9408 |  | 6.23 | 6.2745 | 5.8283 | 5.9109 | 6.1787 | 6.5649 | 7.1122 | 4.7223 | 6.4766 | 4.7726 | 6.6819 | 7.9404 | 42.0914 | 46.4227 | 42.8877 | 15.0813 |  |  | 0.067243 | -0.13791 | 0.078732 | 0.005914 | -0.21931 | -0.061572 | 0.64453 | -0.43452 | -0.52657 | -0.48229 | -0.45076 | 8.8705 | 8.8715 | 2.008 | 15.6226 | 16.571 | 17.147 | 17.494 | 17.4699 | 16.4572 | 14.8177 | 16.824 | 17.1759 | 17.4808 | 17.5396 | 17.2779 | 16.4882 | 14.723 | 5.9691 | 8.2596 | 5.357 | 5.6259 | 6.0623 | 6.584 | 7.6569 | 15.6499 | 15.3286 | 15.2286 | 14.186 | 14.0895 | 14.0475 |  |  |  | 10.6644 | 9.5705 | 9.3273 | 9.5323 | 0.21399 | -0.055118 | 12.7219 |  |  | 10.5287 |  |  | 16.8626 | 16.0591 | 15.0246 | 16.3667 | 15.6578 | 14.7701 | 10.2096 | 10.8245 | 11.4615 | 11.3611 | 8.9388 |  | 10.5021 | 8.0808 | 9.9032 | 9.6837 | 10.9479 | 12.2107 |  | 12.2258 |  |  | 11.5305 | 12.2513 | 12.3101 | [6 empty] | 12.5556 |  |  | 11.3071 |  |  | 9.495 | 10.3188 | 11.8677 | 7.551 | 9.1113 | 12.5103 | 8.1244 | 9.7155 | 12.2339 | 9.2382 | 10.5136 | 7.7134 | 10.482 | 8.4775 | 10.5452 | 8.0411 | 9.7104 | 13.0901 | 10.5412 | 10.2716 | 11.378 | 8.3235 | 9.9886 | 12.7623 | 8.1127 | 10.6937 | 9.686 | 10.0082 | 8.5306 | 10.6107 | -0.18279 | 20.9513 | 0.033895 | 0.048081 | -37.8984 | 3.1199 | 13.18 | 0.32 | 0.30439 | -0.4326 | 0.32687 | 0.089586 | -0.54583 | -0.28921 | 0.93572 | 0.41048 | 0.41458 | 0.40448 | 0.41551 | 0.60809 | 0.41827 | 0.39934
42810.4393 | -61 | 18.3653 | 18.5099 | 18.5217 | 18.5308 | 17.8836 | 16.5269 | 14.5906 | 16.6711 | 17.1652 | 17.2578 | 17.2661 | 16.8001 | 15.8307 | 14.4516 | 14.7707 | 14.8039 | 15.3889 | 13.2764 | 13.3978 | 13.9748 |  |  |  | 16.551 | 15.8938 | 15.0011 | 10.4452 | 9.8194 | 10.6417 | 17.0444 | 16.1972 | 15.0214 | 16.785 | 16.0718 | 15.0725 | 10.7377 | 11.4327 |  | 12.0133 | 10.7266 | 10.5652 | 8.9494 |  | 6.231 | 6.285 | 5.8341 | 5.919 | 6.1907 | 6.5581 | 7.0963 | 4.7365 | 6.484 | 4.893 | 6.6849 | 7.9395 | 42.1112 | 46.4163 | 42.8951 | 15.0903 |  |  | -0.007665 | -0.066937 | 0.07676 | -0.092654 | -0.088548 | -0.065516 | 0.57028 | -0.20387 | -0.26192 | -0.0054176 | -0.46844 | 8.8701 | 8.8712 | 2.0084 | 15.6312 | 16.5674 | 17.1456 | 17.4981 | 17.473 | 16.4584 | 14.8223 | 16.8332 | 17.1735 | 17.4732 | 17.5391 | 17.2783 | 16.4952 | 14.7332 | 6.0487 | 8.28 | 5.3581 | 5.6305 | 6.0266 | 6.5814 | 7.6435 | 15.6505 | 15.3284 | 15.2284 | 14.1817 | 14.0832 | 14.0469 |  |  |  | 10.6651 | 9.5927 | 9.3324 | 9.5473 | 0.12384 | -0.083724 | 12.7117 |  |  | 10.5309 |  |  | 16.8462 | 16.0486 | 15.0132 | 16.3493 | 15.6491 | 14.7601 | 10.1756 | 10.8251 | 11.4437 | 11.3369 | 8.8805 |  | 10.5042 | 8.1598 | 9.9008 | 9.7126 | 10.9574 | 12.1844 |  | 12.2174 |  |  | 11.5382 | 12.2566 | 12.2779 | [6 empty] | 12.5658 |  |  | 11.3144 |  |  | 9.502 | 10.3222 | 11.8884 | 7.5643 | 9.1142 | 12.5129 | 8.1308 | 9.7212 | 12.222 | 9.2456 | 10.5077 | 7.7242 | 10.4855 | 8.483 | 10.5409 | 8.0382 | 9.7086 | 13.0898 | 10.5435 | 10.2802 | 11.4113 | 8.319 | 9.9844 | 12.7602 | 8.1214 | 10.6983 | 9.6907 | 10.0252 | 8.5309 | 10.6127 | 0.049679 | 20.9521 | 0.033814 | 0.048146 | -37.9619 | 3.12 | 20.28 | 0.35 | -0.10278 | -0.3014 | 0.32276 | -0.3546 | -0.34682 | -0.29833 | 0.88016 | 0.41217 | 0.41231 | 0.40399 | 0.40637 | 0.60641 | 0.41795 | 0.39895
42810.4393 | -60 | 18.3668 | 18.5091 | 18.5184 | 18.5305 | 17.8805 | 16.53 | 14.5947 | 16.6759 | 17.1637 | 17.2573 | 17.2714 | 16.803 | 15.8312 | 14.4508 | 14.7751 | 14.8019 | 15.3827 | 13.2724 | 13.3921 | 13.9648 |  |  |  | 16.5574 | 15.8906 | 14.998 | 10.4644 | 9.8239 | 10.7033 | 17.0474 | 16.1995 | 15.0256 | 16.7832 | 16.0793 | 15.0796 | 10.7383 | 11.398 |  | 12.0116 | 10.7262 | 10.5586 | 8.9716 |  | 6.2324 | 6.2768 | 5.8312 | 5.9177 | 6.1829 | 6.5437 | 7.0767 | 4.7584 | 6.4754 | 4.9948 | 6.6762 | 7.9446 | 42.1403 | 46.4257 | 42.8948 | 15.1003 |  |  | -0.020153 | 0.13283 | 0.1405 | -0.031542 | -0.14309 | 0.24333 | 0.55451 | -0.23278 | -0.30084 | -0.63775 | -0.38857 | 8.8697 | 8.8707 | 2.0083 | 15.6335 | 16.5783 | 17.1408 | 17.4947 | 17.4671 | 16.4572 | 14.8079 | 16.8209 | 17.1687 | 17.4782 | 17.5308 | 17.2732 | 16.4909 | 14.7282 | 6.1272 | 8.2971 | 5.3912 | 5.6558 | 6.0599 | 6.5912 | 7.6462 | 15.6568 | 15.3267 | 15.2306 | 14.1847 | 14.0807 | 14.05 |  |  |  | 10.6654 | 9.6139 | 9.358 | 9.5499 | 0.24216 | 0.032772 | 12.7134 |  |  | 10.5358 |  |  | 16.8487 | 16.0507 | 15.0145 | 16.3566 | 15.657 | 14.757 | 10.183 | 10.8487 | 11.4437 | 11.3347 | 8.8595 |  | 10.5067 | 8.1542 | 9.9028 | 9.7262 | 10.9562 | 12.1564 |  | 12.2246 |  |  | 11.5674 | 12.2638 | 12.2676 | [6 empty] | 12.5816 |  |  | 11.3341 |  |  | 9.5097 | 10.327 | 11.904 | 7.5839 | 9.1139 | 12.5233 | 8.1362 | 9.7281 | 12.2221 | 9.2478 | 10.5092 | 7.7356 | 10.4837 | 8.4903 | 10.5385 | 8.0477 | 9.7201 | 13.0973 | 10.5504 | 10.2911 | 11.452 | 8.3307 | 10.0007 | 12.7674 | 8.1294 | 10.7073 | 9.696 | 10.0543 | 8.5299 | 10.6124 | 0.088969 | 20.952 | 0.034067 | 0.048565 | -37.846 | 3.12 | 5.17 | 0.36 | -0.16668 | 0.42456 | 0.43666 | -0.20689 | -0.44087 | 0.57492 | 0.86789 | 0.41283 | 0.41253 | 0.40358 | 0.39878 | 0.60304 | 0.41735 | 0.39888
42810.4394 | -59 | 18.371 | 18.5134 | 18.5248 | 18.536 | 17.8895 | 16.5322 | 14.5987 | 16.6801 | 17.1647 | 17.2616 | 17.2726 | 16.7987 | 15.8353 | 14.4496 | 14.7745 | 14.801 | 15.3784 | 13.2601 | 13.3948 | 13.9671 |  |  |  | 16.5608 | 15.8939 | 14.9915 | 10.4778 | 9.822 | 10.7428 | 17.0466 | 16.1965 | 15.0146 | 16.7843 | 16.0708 | 15.0793 | 10.7437 | 11.4146 |  | 12.0049 | 10.7076 | 10.5507 | 8.992 |  | 6.2441 | 6.2915 | 5.8456 | 5.9277 | 6.1913 | 6.5523 | 7.1025 | 4.8237 | 6.4818 | 4.9919 | 6.6863 | 7.9473 | 42.1431 | 46.4383 | 42.8916 | 15.0989 |  |  | 0.10404 | 0.009287 | 0.14313 | 0.009858 | -0.16937 | 0.10205 | 0.59853 | -0.34844 | -0.27534 | -0.57628 | -0.34664 | 8.8705 | 8.8715 | 2.0083 | 15.6237 | 16.5734 | 17.1325 | 17.4931 | 17.4629 | 16.4485 | 14.8125 | 16.8169 | 17.1635 | 17.477 | 17.5336 | 17.2761 | 16.4837 | 14.7216 | 6.1778 | 8.3178 | 5.4117 | 5.7002 | 6.1655 | 6.5916 | 7.6506 | 15.6597 | 15.3298 | 15.2298 | 14.183 | 14.085 | 14.0452 |  |  |  | 10.6638 | 9.6373 | 9.3707 | 9.5578 | 0.061234 | -0.095581 | 12.7148 |  |  | 10.5407 |  |  | 16.8539 | 16.0541 | 15.0186 | 16.3624 | 15.6547 | 14.7635 | 10.2078 | 10.8685 | 11.4454 | 11.329 | 8.836 |  | 10.4975 | 8.1499 | 9.8929 | 9.74 | 10.9499 | 12.0485 |  | 12.2083 |  |  | 11.5939 | 12.2968 | 12.2592 | [6 empty] | 12.5923 |  |  | 11.3502 |  |  | 9.5223 | 10.3394 | 11.9196 | 7.5959 | 9.1043 | 12.5186 | 8.132 | 9.7238 | 12.2403 | 9.2554 | 10.525 | 7.7488 | 10.49 | 8.5042 | 10.53 | 8.0562 | 9.7258 | 13.0979 | 10.5543 | 10.2857 | 11.4689 | 8.3196 | 9.9924 | 12.7642 | 8.1357 | 10.7046 | 9.7052 | 10.0692 | 8.525 | 10.6161 | 0.07125 | 20.9544 | 0.033975 | 0.048783 | -37.7303 | 3.1199 | 9.65 | 0.15 | 0.37875 | 0.11227 | 0.44074 | 0.11567 | -0.47966 | 0.37233 | 0.90169 | 0.41318 | 0.41232 | 0.40298 | 0.3932 | 0.60128 | 0.41696 | 0.39861
42810.4394 | -58 | 18.3708 | 18.5126 | 18.5381 | 18.5347 | 17.8905 | 16.5264 | 14.5985 | 16.6718 | 17.167 | 17.2618 | 17.2645 | 16.8065 | 15.8312 | 14.4529 | 14.7797 | 14.8095 | 15.3918 | 13.271 | 13.4 | 13.974 |  |  |  | 16.5533 | 15.9066 | 14.9993 | 10.4998 | 9.8216 | 10.7873 | 17.0399 | 16.1933 | 15.0124 | 16.7742 | 16.0665 | 15.0753 | 10.7344 | 11.4609 |  | 11.9998 | 10.6974 | 10.5364 | 8.997 |  | 6.2456 | 6.2988 | 5.8478 | 5.9311 | 6.1944 | 6.5409 | 7.1338 | 4.8415 | 6.4751 | 4.9529 | 6.6788 | 7.9505 | 42.1313 | 46.4471 | 42.8993 | 15.1056 |  |  | 0.051475 | -0.20296 | 0.17993 | 0.15377 | -0.066204 | 0.00874 | 0.69776 | -0.42269 | -1.5406 | 0.077453 | -0.39055 | 8.8684 | 8.8696 | 2.0081 | 15.6295 | 16.5772 | 17.1498 | 17.5016 | 17.4804 | 16.4584 | 14.8226 | 16.8265 | 17.179 | 17.4845 | 17.538 | 17.2844 | 16.5021 | 14.7384 | 6.218 | 8.322 | 5.4221 | 5.7679 | 6.172 | 6.5896 | 7.6444 | 15.6596 | 15.3398 | 15.2264 | 14.1825 | 14.0878 | 14.0427 |  |  |  | 10.6652 | 9.6735 | 9.3796 | 9.5859 | -0.014336 | -0.15882 | 12.7077 |  |  | 10.5293 |  |  | 16.8468 | 16.0437 | 15.0079 | 16.3544 | 15.6438 | 14.7644 | 10.2261 | 10.8712 | 11.4305 | 11.318 | 8.8562 |  | 10.5013 | 8.1886 | 9.9014 | 9.7741 | 10.9586 | 11.9949 |  | 12.2161 |  |  | 11.5933 | 12.3081 | 12.2453 | [6 empty] | 12.5967 |  |  | 11.3364 |  |  | 9.5213 | 10.3407 | 11.9233 | 7.6057 | 9.1286 | 12.5161 | 8.1289 | 9.7193 | 12.2284 | 9.2539 | 10.5167 | 7.7487 | 10.4922 | 8.5021 | 10.5261 | 8.0713 | 9.7405 | 13.1024 | 10.5668 | 10.3004 | 11.4953 | 8.3293 | 10 | 12.7565 | 8.155 | 10.7047 | 9.7206 | 10.0966 | 8.5189 | 10.6188 | 0.053531 | 20.9529 | 0.033705 | 0.047704 | -37.741 | 3.1199 | 9.93 | 0.25 | 0.26643 | -0.52484 | 0.49416 | 0.45682 | -0.29988 | 0.10896 | 0.97355 | 0.41274 | 0.41153 | 0.40232 | 0.3885 | 0.59941 | 0.41651 | 0.39788
42810.4394 | -57 | 18.378 | 18.5161 | 18.5272 | 18.534 | 17.885 | 16.5234 | 14.5919 | 16.6705 | 17.1694 | 17.2657 | 17.262 | 16.8041 | 15.8335 | 14.4454 | 14.7737 | 14.8148 | 15.3817 | 13.2713 | 13.3934 | 13.9712 |  |  |  | 16.5703 | 15.8962 | 15.0024 | 10.5132 | 9.8208 | 10.8251 | 17.0527 | 16.2052 | 15.0211 | 16.7892 | 16.0745 | 15.0745 | 10.7464 | 11.5585 |  | 12.0078 | 10.6931 | 10.5343 | 9.0154 |  | 6.2651 | 6.3101 | 5.8547 | 5.9518 | 6.2119 | 6.5777 | 7.1732 | 4.8826 | 6.4847 | 4.9325 | 6.686 | 7.9466 | 42.1111 | 46.4442 | 42.8942 | 15.0976 |  |  | 0.091559 | -0.086653 | 0.20556 | -0.14391 | -0.1122 | 0.042908 | 0.56634 | -0.27418 | -0.1868 | -0.98392 | -0.28504 | 8.871 | 8.8719 | 2.0085 | 15.6249 | 16.572 | 17.1446 | 17.5028 | 17.4757 | 16.4585 | 14.8167 | 16.8248 | 17.1706 | 17.4853 | 17.5344 | 17.286 | 16.4959 | 14.7385 | 6.2593 | 8.3335 | 5.4497 | 5.8288 | 6.1106 | 6.5916 | 7.6389 | 15.6546 | 15.326 | 15.2271 | 14.1693 | 14.0864 | 14.0429 |  |  |  | 10.6688 | 9.6881 | 9.3717 | 9.6172 | 0.11067 | -0.12212 | 12.7195 |  |  | 10.5439 |  |  | 16.8566 | 16.0584 | 15.0168 | 16.3621 | 15.6539 | 14.7656 | 10.2631 | 10.8891 | 11.4309 | 11.3169 | 8.9045 |  | 10.5101 | 8.221 | 9.9073 | 9.8081 | 10.9683 | 11.9353 |  | 12.2183 |  |  | 11.596 | 12.3216 | 12.2386 | [6 empty] | 12.6001 |  |  | 11.3512 |  |  | 9.5302 | 10.3492 | 11.9402 | 7.6145 | 9.1395 | 12.5221 | 8.1469 | 9.7217 | 12.2294 | 9.2493 | 10.5172 | 7.7573 | 10.4826 | 8.5028 | 10.5238 | 8.0658 | 9.7354 | 13.0911 | 10.5459 | 10.2848 | 11.4905 | 8.332 | 9.9889 | 12.7432 | 8.1499 | 10.6975 | 9.7062 | 10.0904 | 8.4919 | 10.6017 | 0.019826 | 20.9534 | 0.032994 | 0.04617 | -37.7601 | 3.12 | 16.31 | 0.25 | 0.35535 | -0.34294 | 0.52819 | -0.44195 | -0.39043 | 0.24144 | 0.87715 | 0.41169 | 0.41082 | 0.4017 | 0.38415 | 0.5957 | 0.4164 | 0.39712
42810.4394 | -56 | 18.3584 | 18.5075 | 18.5188 | 18.5373 | 17.8737 | 16.5263 | 14.5871 | 16.6687 | 17.1589 | 17.2525 | 17.2558 | 16.7969 | 15.824 | 14.4442 | 14.7772 | 14.8137 | 15.3929 | 13.2805 | 13.3993 | 13.976 |  |  |  | 16.564 | 15.9028 | 15.0005 | 10.5147 | 9.8233 | 10.853 | 17.0492 | 16.2011 | 15.0209 | 16.7922 | 16.0721 | 15.0718 | 10.7502 | 11.5983 |  | 12.0089 | 10.6906 | 10.5315 | 9.0172 |  | 6.27 | 6.3138 | 5.8721 | 5.9587 | 6.2361 | 6.6136 | 7.2102 | 4.9484 | 6.4817 | 4.9631 | 6.6813 | 7.9454 | 42.0951 | 46.4426 | 42.8987 | 15.0875 |  |  | 0.010075 | -0.11819 | 0.13524 | 0.04337 | 0.071788 | -0.085884 | 0.6971 | -0.32412 | -0.19011 | -1.0261 | -0.10184 | 8.8677 | 8.8685 | 2.0084 | 15.6305 | 16.575 | 17.153 | 17.5027 | 17.4737 | 16.4627 | 14.8195 | 16.8239 | 17.1706 | 17.4853 | 17.5412 | 17.2863 | 16.4959 | 14.7345 | 6.2777 | 8.3573 | 5.4727 | 5.8541 | 6.0766 | 6.595 | 7.6417 | 15.662 | 15.3386 | 15.2325 | 14.1794 | 14.0891 | 14.0442 |  |  |  | 10.6726 | 9.7061 | 9.3825 | 9.6658 | 0.022537 | -0.088053 | 12.7252 |  |  | 10.5448 |  |  | 16.861 | 16.0526 | 15.0216 | 16.3707 | 15.6564 | 14.7665 | 10.2813 | 10.8984 | 11.4257 | 11.3111 | 8.9385 |  | 10.4996 | 8.2942 | 9.8987 | 9.8008 | 10.959 | 11.8933 |  | 12.2108 |  |  | 11.6191 | 12.3593 | 12.2488 | [6 empty] | 12.616 |  |  | 11.3601 |  |  | 9.5323 | 10.3632 | 11.9835 | 7.6233 | 9.1409 | 12.5259 | 8.1566 | 9.7215 | 12.2205 | 9.2543 | 10.5082 | 7.7774 | 10.4664 | 8.506 | 10.5195 | 8.091 | 9.7442 | 13.1036 | 10.5669 | 10.306 | 11.5 | 8.3482 | 9.9941 | 12.7626 | 8.1673 | 10.6881 | 9.7202 | 10.111 | 8.4975 | 10.6066 | 0.080687 | 20.9532 | 0.032684 | 0.047096 | -37.8616 | 3.1199 | 13.91 | 0.18 | 0.11788 | -0.40052 | 0.42844 | 0.24262 | 0.31231 | -0.3416 | 0.97322 | 0.4104 | 0.40851 | 0.40159 | 0.3825 | 0.59346 | 0.41647 | 0.3959
42810.4394 | -55 | 18.3603 | 18.5012 | 18.5171 | 18.5314 | 17.8742 | 16.5135 | 14.5967 | 16.6619 | 17.1581 | 17.2497 | 17.2617 | 16.7897 | 15.825 | 14.443 | 14.768 | 14.8072 | 15.3842 | 13.2627 | 13.3913 | 13.9651 |  |  |  | 16.5467 | 15.8968 | 14.9945 | 10.5311 | 9.813 | 10.8519 | 17.0474 | 16.2005 | 15.0126 | 16.786 | 16.0679 | 15.0672 | 10.7402 | 11.6168 |  | 12.0103 | 10.6723 | 10.5223 | 9.0385 |  | 6.252 | 6.3086 | 5.8624 | 5.957 | 6.2498 | 6.6326 | 7.2221 | 5.0194 | 6.4737 | 4.9201 | 6.6777 | 7.9348 | 42.0771 | 46.4384 | 42.8962 | 15.0724 |  |  | 0.088931 | -0.031453 | 0.091876 | -0.007886 | -0.041892 | 0.23282 | 0.6833 | -0.21373 | -0.52346 | -0.54167 | -0.39373 | 8.8708 | 8.8715 | 2.008 | 15.626 | 16.5795 | 17.1504 | 17.5008 | 17.4711 | 16.4575 | 14.8224 | 16.821 | 17.1735 | 17.4809 | 17.5396 | 17.2846 | 16.4976 | 14.733 | 6.3189 | 8.4023 | 5.5019 | 5.8615 | 6.073 | 6.5948 | 7.6356 | 15.6596 | 15.339 | 15.2341 | 14.1845 | 14.0931 | 14.0548 |  |  |  | 10.6718 | 9.7125 | 9.3918 | 9.6983 | 0.09446 | 0.15378 | 12.7208 |  |  | 10.5395 |  |  | 16.8602 | 16.0577 | 15.0284 | 16.3687 | 15.6534 | 14.7695 | 10.2937 | 10.8998 | 11.4129 | 11.3001 | 9.0153 |  | 10.4975 | 8.3856 | 9.8967 | 9.7771 | 10.9665 | 11.87 |  | 12.2257 |  |  | 11.5885 | 12.3642 | 12.2607 | [6 empty] | 12.5997 |  |  | 11.366 |  |  | 9.5347 | 10.3725 | 11.9962 | 7.6319 | 9.1486 | 12.5331 | 8.1626 | 9.7325 | 12.2063 | 9.2597 | 10.5122 | 7.7801 | 10.4559 | 8.5096 | 10.5151 | 8.1284 | 9.7545 | 13.1119 | 10.5895 | 10.3237 | 11.5087 | 8.3618 | 9.9971 | 12.7727 | 8.1952 | 10.6819 | 9.7287 | 10.1328 | 8.5045 | 10.6243 | -0.034102 | 20.9532 | 0.032087 | 0.046908 | -37.8429 | 3.1199 | 6.59 | 0.33 | 0.35023 | -0.20661 | 0.35312 | -0.10346 | -0.23858 | 0.56245 | 0.96357 | 0.4082 | 0.4059 | 0.4025 | 0.37789 | 0.58952 | 0.41556 | 0.39497
42810.4394 | -54 | 18.362 | 18.5126 | 18.5246 | 18.5277 | 17.875 | 16.5176 | 14.5973 | 16.6646 | 17.1594 | 17.2508 | 17.2601 | 16.7907 | 15.8299 | 14.4469 | 14.7624 | 14.8012 | 15.3755 | 13.2512 | 13.3864 | 13.9609 |  |  |  | 16.5442 | 15.8874 | 14.9874 | 10.5236 | 9.8078 | 10.8593 | 17.0467 | 16.1968 | 15.0189 | 16.7748 | 16.0625 | 15.0629 | 10.7396 | 11.6312 |  | 12.0053 | 10.6594 | 10.5122 | 9.0495 |  | 6.2714 | 6.3252 | 5.8746 | 5.9739 | 6.262 | 6.6554 | 7.2538 | 5.0387 | 6.4857 | 4.9352 | 6.6911 | 7.94 | 42.0545 | 46.4379 | 42.9017 | 15.0656 |  |  | 0.078415 | -0.059709 | 0.1727 | -0.2819 | -0.1812 | 0.25976 | 0.74967 | -0.22161 | -0.72915 | -0.25277 | -0.31266 | 8.8701 | 8.8717 | 2.0083 | 15.6261 | 16.5703 | 17.1472 | 17.5008 | 17.4615 | 16.4565 | 14.8226 | 16.8241 | 17.1731 | 17.4792 | 17.5382 | 17.2876 | 16.4949 | 14.7334 | 6.3931 | 8.4257 | 5.551 | 5.855 | 6.0468 | 6.5962 | 7.6326 | 15.6553 | 15.3316 | 15.2245 | 14.1773 | 14.0846 | 14.0475 |  |  |  | 10.6622 | 9.7054 | 9.3904 | 9.7008 | 0.024563 | 0.08622 | 12.7144 |  |  | 10.5267 |  |  | 16.851 | 16.0517 | 15.0221 | 16.3632 | 15.6472 | 14.7569 | 10.3001 | 10.8959 | 11.4019 | 11.2737 | 9.0886 |  | 10.5065 | 8.4256 | 9.9026 | 9.7576 | 10.9678 | 11.885 |  | 12.2245 |  |  | 11.5973 | 12.3802 | 12.2801 | [6 empty] | 12.6174 |  |  | 11.3917 |  |  | 9.5312 | 10.382 | 12.0338 | 7.6326 | 9.1373 | 12.5311 | 8.1671 | 9.7444 | 12.1937 | 9.2609 | 10.5085 | 7.7891 | 10.4546 | 8.5075 | 10.5101 | 8.1421 | 9.766 | 13.1183 | 10.599 | 10.3195 | 11.5175 | 8.3685 | 10.0027 | 12.7946 | 8.193 | 10.663 | 9.741 | 10.1318 | 8.4996 | 10.6254 | -0.1383 | 20.9534 | 0.032328 | 0.046988 | -37.8036 | 3.12 | 5.8 | 0.17 | 0.32888 | -0.28468 | 0.48416 | -0.61857 | -0.49622 | 0.59413 | 1.0093 | 0.40646 | 0.40499 | 0.40308 | 0.36981 | 0.58372 | 0.41523 | 0.39459
42810.4394 | -53 | 18.3708 | 18.5087 | 18.5283 | 18.5239 | 17.8775 | 16.5215 | 14.5933 | 16.6747 | 17.1625 | 17.2488 | 17.262 | 16.7978 | 15.8272 | 14.4499 | 14.7759 | 14.8043 | 15.3807 | 13.2648 | 13.3909 | 13.963 |  |  |  | 16.5466 | 15.8898 | 14.995 | 10.5421 | 9.836 | 10.8771 | 17.052 | 16.2025 | 15.0133 | 16.7829 | 16.0643 | 15.0706 | 10.7412 | 11.6598 |  | 12.0075 | 10.661 | 10.5065 | 9.0579 |  | 6.274 | 6.3264 | 5.8851 | 5.9766 | 6.2651 | 6.6713 | 7.286 | 5.1234 | 6.4865 | 4.9827 | 6.6965 | 7.9494 | 42.0454 | 46.4457 | 42.8973 | 15.0545 |  |  | 0.067243 | -0.20493 | 0.21147 | -0.20765 | -0.15492 | -0.066828 | 0.33043 | -0.22227 | 0.27849 | -0.6986 | -0.42393 | 8.8671 | 8.8681 | 2.0085 | 15.6186 | 16.586 | 17.1453 | 17.4977 | 17.4706 | 16.4517 | 14.8153 | 16.8198 | 17.1784 | 17.4894 | 17.5382 | 17.2792 | 16.4973 | 14.7226 | 6.4303 | 8.4015 | 5.5975 | 5.8535 | 6.0329 | 6.5986 | 7.6339 | 15.651 | 15.3303 | 15.2204 | 14.1794 | 14.0803 | 14.0442 |  |  |  | 10.6595 | 9.7021 | 9.3878 | 9.7064 | -0.073698 | -0.01616 | 12.718 |  |  | 10.5296 |  |  | 16.8541 | 16.0494 | 15.0256 | 16.3674 | 15.6501 | 14.7612 | 10.3217 | 10.9047 | 11.4048 | 11.2691 | 9.1158 |  | 10.4989 | 8.4267 | 9.8982 | 9.7272 | 10.9641 | 11.9013 |  | 12.2119 |  |  | 11.6163 | 12.3669 | 12.2562 | [6 empty] | 12.6073 |  |  | 11.412 |  |  | 9.5397 | 10.3905 | 12.0652 | 7.6144 | 9.1386 | 12.5508 | 8.1748 | 9.754 | 12.1674 | 9.273 | 10.5131 | 7.7917 | 10.4531 | 8.5293 | 10.5053 | 8.1505 | 9.7648 | 13.1204 | 10.6074 | 10.3268 | 11.5344 | 8.3686 | 9.9927 | 12.8003 | 8.2022 | 10.6688 | 9.7415 | 10.1384 | 8.4908 | 10.6436 | -0.032947 | 20.9532 | 0.032529 | 0.04769 | -37.7887 | 3.1199 | -3.05 | 0.26 | 0.30456 | -0.52741 | 0.53575 | -0.53089 | -0.45883 | -0.30136 | 0.67011 | 0.40545 | 0.40481 | 0.40381 | 0.36596 | 0.5787 | 0.41505 | 0.39434
42810.4394 | -52 | 18.3706 | 18.5161 | 18.5316 | 18.5319 | 17.8774 | 16.5293 | 14.5999 | 16.6756 | 17.1606 | 17.2566 | 17.268 | 16.7973 | 15.8265 | 14.4587 | 14.7759 | 14.8092 | 15.3862 | 13.2748 | 13.3987 | 13.9739 |  |  |  | 16.565 | 15.8969 | 14.9957 | 10.5591 | 9.8641 | 10.9424 | 17.0453 | 16.1958 | 15.012 | 16.7844 | 16.0658 | 15.0696 | 10.7403 | 11.6635 |  | 11.9997 | 10.6635 | 10.4958 | 9.0624 |  | 6.2741 | 6.3311 | 5.8887 | 5.9782 | 6.2746 | 6.6751 | 7.277 | 5.0985 | 6.4854 | 4.9914 | 6.6941 | 7.9481 | 42.0327 | 46.4425 | 42.8898 | 15.0469 |  |  | 0.073159 | 0.011259 | 0.084648 | -0.12222 | 0.036964 | 0.061308 | 0.4336 | -0.13947 | -0.46897 | -0.67783 | -0.15748 | 8.8705 | 8.8712 | 2.0083 | 15.6238 | 16.5804 | 17.1456 | 17.4954 | 17.4723 | 16.4621 | 14.815 | 16.8268 | 17.1763 | 17.4792 | 17.5403 | 17.2795 | 16.4958 | 14.7303 | 6.4265 | 8.3767 | 5.6015 | 5.8481 | 6.0262 | 6.5981 | 7.6422 | 15.6592 | 15.3332 | 15.2284 | 14.1807 | 14.0896 | 14.0549 |  |  |  | 10.6687 | 9.7148 | 9.3947 | 9.7131 | -0.054248 | 0.067589 | 12.716 |  |  | 10.5243 |  |  | 16.8543 | 16.0475 | 15.0162 | 16.3632 | 15.6512 | 14.761 | 10.3314 | 10.9066 | 11.3962 | 11.2645 | 9.1496 |  | 10.505 | 8.3959 | 9.8988 | 9.7006 | 10.9664 | 11.9439 |  | 12.2146 |  |  | 11.6378 | 12.3591 | 12.2371 | [6 empty] | 12.5946 |  |  | 11.4139 |  |  | 9.5547 | 10.4059 | 12.0825 | 7.6073 | 9.1392 | 12.5573 | 8.1862 | 9.7568 | 12.1554 | 9.2876 | 10.5171 | 7.8093 | 10.4588 | 8.5326 | 10.5019 | 8.1696 | 9.7669 | 13.124 | 10.6121 | 10.34 | 11.5693 | 8.3567 | 9.9854 | 12.8064 | 8.2093 | 10.6662 | 9.7551 | 10.1424 | 8.4824 | 10.6587 | -0.069733 | 20.9531 | 0.03246 | 0.048023 | -37.8627 | 3.12 | 26.74 | 0.28 | 0.31771 | 0.12362 | 0.33896 | -0.4073 | 0.22413 | 0.28865 | 0.76763 | 0.40472 | 0.40569 | 0.40462 | 0.36633 | 0.57921 | 0.4149 | 0.39446
42810.4394 | -51 | 18.3773 | 18.5194 | 18.5271 | 18.5365 | 17.8825 | 16.5316 | 14.604 | 16.6784 | 17.1672 | 17.2675 | 17.2702 | 16.8086 | 15.8436 | 14.4626 | 14.7679 | 14.8078 | 15.3865 | 13.2698 | 13.3977 | 13.973 |  |  |  | 16.5613 | 15.8991 | 14.9953 | 10.5653 | 9.8891 | 10.9875 | 17.0428 | 16.1894 | 15.0205 | 16.7805 | 16.0762 | 15.0696 | 10.7444 | 11.6412 |  | 12.0076 | 10.6661 | 10.4937 | 9.0811 |  | 6.2638 | 6.3331 | 5.8887 | 5.9797 | 6.278 | 6.6672 | 7.2541 | 4.9386 | 6.486 | 5.0032 | 6.6919 | 7.9485 | 42.0264 | 46.433 | 42.8806 | 15.039 |  |  | 0.042931 | 0.041487 | 0.16087 | -0.047314 | 0.13093 | 0.14674 | -0.65262 | -0.084276 | -0.55615 | 0.20942 | -0.16145 | 8.8722 | 8.8732 | 2.0082 | 15.6244 | 16.572 | 17.1466 | 17.4936 | 17.4705 | 16.4592 | 14.8179 | 16.8179 | 17.1716 | 17.4759 | 17.5385 | 17.2808 | 16.494 | 14.729 | 6.4128 | 8.3458 | 5.5841 | 5.8395 | 6.0182 | 6.6017 | 7.6491 | 15.658 | 15.3346 | 15.2296 | 14.1838 | 14.0847 | 14.0403 |  |  |  | 10.6705 | 9.7116 | 9.398 | 9.6879 | -0.064378 | 0.019221 | 12.7175 |  |  | 10.5224 |  |  | 16.8501 | 16.0506 | 15.0135 | 16.3674 | 15.6515 | 14.7618 | 10.3457 | 10.91 | 11.394 | 11.259 | 9.173 |  | 10.5119 | 8.3696 | 9.9004 | 9.6774 | 10.9741 | 11.9855 |  | 12.2224 |  |  | 11.6457 | 12.3558 | 12.2391 | [6 empty] | 12.5945 |  |  | 11.4105 |  |  | 9.5576 | 10.4168 | 12.1044 | 7.592 | 9.1451 | 12.5533 | 8.1865 | 9.7521 | 12.1476 | 9.283 | 10.5232 | 7.8159 | 10.4541 | 8.526 | 10.5038 | 8.1761 | 9.767 | 13.1303 | 10.6204 | 10.3575 | 11.6001 | 8.3536 | 9.9811 | 12.8031 | 8.207 | 10.6504 | 9.7668 | 10.1564 | 8.4819 | 10.6704 | -0.25578 | 20.9531 | 0.032219 | 0.047509 | -37.9081 | 3.12 | 30 | 0.22 | 0.2434 | 0.2373 | 0.46729 | -0.25342 | 0.42182 | 0.44655 | -0.94174 | 0.40429 | 0.40647 | 0.40552 | 0.36827 | 0.58195 | 0.41451 | 0.39522
42810.4395 | -50 | 18.367 | 18.5056 | 18.5208 | 18.5308 | 17.8774 | 16.5201 | 14.5903 | 16.6712 | 17.1559 | 17.2531 | 17.2634 | 16.7999 | 15.8285 | 14.448 | 14.7669 | 14.8042 | 15.3895 | 13.2684 | 13.4009 | 13.9707 |  |  |  | 16.5535 | 15.8958 | 14.9947 | 10.5694 | 9.9273 | 11.0018 | 17.0387 | 16.1957 | 15.0098 | 16.7813 | 16.0736 | 15.0674 | 10.7385 | 11.5775 |  | 11.9938 | 10.6796 | 10.484 | 9.1139 |  | 6.2765 | 6.3325 | 5.9004 | 5.9822 | 6.2817 | 6.6499 | 7.2326 | 4.8264 | 6.4901 | 5.0068 | 6.6928 | 7.9466 | 42.0235 | 46.438 | 42.8703 | 15.0476 |  |  | -0.022781 | 0.013231 | 0.15956 | 0.072282 | -0.14834 | -0.35859 | -0.0231 | 0.11746 | -0.67213 | -0.76573 | -0.10383 | 8.8696 | 8.8706 | 2.0084 | 15.6285 | 16.5769 | 17.1517 | 17.4971 | 17.4756 | 16.462 | 14.8243 | 16.8229 | 17.1749 | 17.4779 | 17.5408 | 17.2875 | 16.4977 | 14.7339 | 6.3623 | 8.3156 | 5.5751 | 5.8311 | 6.0007 | 6.5891 | 7.6416 | 15.6562 | 15.3307 | 15.2268 | 14.1777 | 14.0822 | 14.0379 |  |  |  | 10.6687 | 9.7052 | 9.3962 | 9.6816 | -0.032367 | -0.10781 | 12.7213 |  |  | 10.5262 |  |  | 16.8457 | 16.0511 | 15.0174 | 16.3629 | 15.6484 | 14.7583 | 10.3559 | 10.9097 | 11.3839 | 11.2537 | 9.1875 |  | 10.5001 | 8.3686 | 9.8973 | 9.6383 | 10.9644 | 12.0127 |  | 12.2167 |  |  | 11.67 | 12.3663 | 12.2519 | [6 empty] | 12.5938 |  |  | 11.4104 |  |  | 9.5663 | 10.4263 | 12.1307 | 7.5934 | 9.1485 | 12.5638 | 8.1904 | 9.7554 | 12.1491 | 9.2955 | 10.5274 | 7.8257 | 10.4564 | 8.5344 | 10.5006 | 8.1821 | 9.7749 | 13.1342 | 10.629 | 10.3592 | 11.6257 | 8.351 | 9.9707 | 12.7953 | 8.2018 | 10.6447 | 9.7727 | 10.1617 | 8.4758 | 10.6815 | -0.002516 | 20.953 | 0.031691 | 0.047784 | -37.9223 | 3.12 | -5.97 | 0.24 | -0.17731 | 0.13401 | 0.46538 | 0.31323 | -0.44898 | -0.69805 | -0.17717 | 0.4035 | 0.40639 | 0.40629 | 0.37241 | 0.58208 | 0.4134 | 0.39533
42810.4395 | -49 | 18.372 | 18.5074 | 18.5253 | 18.5386 | 17.8798 | 16.5255 | 14.598 | 16.6748 | 17.1653 | 17.2643 | 17.2644 | 16.8075 | 15.8317 | 14.4485 | 14.7718 | 14.8059 | 15.3834 | 13.2703 | 13.398 | 13.9715 |  |  |  | 16.555 | 15.8886 | 14.9974 | 10.5841 | 9.9634 | 10.9945 | 17.041 | 16.2037 | 15.0228 | 16.7713 | 16.0678 | 15.0773 | 10.742 | 11.5495 |  | 12.0004 | 10.6794 | 10.4795 | 9.1663 |  | 6.2776 | 6.3308 | 5.9021 | 5.9827 | 6.2698 | 6.6282 | 7.1875 | 4.7403 | 6.4801 | 4.8832 | 6.6932 | 7.9511 | 42.0327 | 46.4555 | 42.8663 | 15.0373 |  |  | -0.044465 | 0.064487 | 0.16482 | 0.16559 | -0.026776 | -0.21862 | 0.080728 | 0.19894 | -0.52657 | -0.65517 | -0.49984 | 8.8697 | 8.8708 | 2.0086 | 15.6286 | 16.5734 | 17.1461 | 17.4947 | 17.4747 | 16.4574 | 14.8105 | 16.8242 | 17.1705 | 17.4821 | 17.5377 | 17.2825 | 16.4956 | 14.7289 | 6.3373 | 8.2873 | 5.5659 | 5.8126 | 6.013 | 6.5944 | 7.6527 | 15.6545 | 15.3225 | 15.2201 | 14.17 | 14.0796 | 14.0335 |  |  |  | 10.6633 | 9.7044 | 9.4012 | 9.6689 | -0.16385 | -0.15693 | 12.7262 |  |  | 10.5326 |  |  | 16.859 | 16.0546 | 15.0248 | 16.3709 | 15.656 | 14.7606 | 10.3762 | 10.9172 | 11.3722 | 11.2519 | 9.2036 |  | 10.5075 | 8.3944 | 9.9026 | 9.6005 | 10.9705 | 12.0387 |  | 12.2197 |  |  | 11.6777 | 12.3718 | 12.2582 | [6 empty] | 12.5907 |  |  | 11.4106 |  |  | 9.5636 | 10.4291 | 12.1489 | 7.5853 | 9.1458 | 12.5521 | 8.1784 | 9.7454 | 12.1503 | 9.2994 | 10.5224 | 7.8266 | 10.4447 | 8.5187 | 10.4931 | 8.1913 | 9.7795 | 13.1385 | 10.6373 | 10.3691 | 11.6597 | 8.351 | 9.9588 | 12.791 | 8.2129 | 10.6501 | 9.7854 | 10.1711 | 8.4777 | 10.6971 | -0.068578 | 20.9531 | 0.032242 | 0.048348 | -37.8957 | 3.12 | 14.46 | 0.22 | -0.24771 | 0.29586 | 0.47298 | 0.47409 | -0.19074 | -0.54503 | 0.3312 | 0.4033 | 0.40585 | 0.40754 | 0.3758 | 0.58439 | 0.41206 | 0.39551
42810.4395 | -48 | 18.3733 | 18.5088 | 18.5226 | 18.5347 | 17.874 | 16.5196 | 14.5952 | 16.6707 | 17.1588 | 17.2557 | 17.2566 | 16.7995 | 15.825 | 14.4514 | 14.77 | 14.8069 | 15.3818 | 13.2673 | 13.3937 | 13.9715 |  |  |  | 16.5575 | 15.8897 | 14.9953 | 10.6 | 9.9882 | 10.976 | 17.0445 | 16.2005 | 15.0136 | 16.7752 | 16.0664 | 15.0722 | 10.7387 | 11.5317 |  | 12.0025 | 10.6915 | 10.4715 | 9.1995 |  | 6.2842 | 6.3349 | 5.9068 | 5.98 | 6.2657 | 6.6075 | 7.1449 | 4.6785 | 6.4847 | 4.8336 | 6.6962 | 7.9524 | 42.0101 | 46.471 | 42.8591 | 15.0213 |  |  | 0.20721 | 0.088143 | 0.1819 | 0.13405 | 0.2801 | -0.19956 | 0.082696 | 0.040576 | -0.2374 | -1.199 | -0.2302 | 8.8698 | 8.8712 | 2.0081 | 15.6231 | 16.5728 | 17.1471 | 17.5007 | 17.4802 | 16.4564 | 14.8154 | 16.8262 | 17.1746 | 17.4812 | 17.5345 | 17.2843 | 16.4945 | 14.7333 | 6.301 | 8.2618 | 5.5462 | 5.7859 | 6.0047 | 6.5956 | 7.6463 | 15.6584 | 15.3242 | 15.2339 | 14.169 | 14.0822 | 14.0447 |  |  |  | 10.6624 | 9.7156 | 9.415 | 9.67 | -0.29332 | -0.039685 | 12.7291 |  |  | 10.5369 |  |  | 16.8587 | 16.0624 | 15.0251 | 16.3772 | 15.6607 | 14.7614 | 10.3933 | 10.9147 | 11.3515 | 11.2403 | 9.2109 |  | 10.5054 | 8.449 | 9.9109 | 9.573 | 10.9772 | 12.0555 |  | 12.2199 |  |  | 11.6916 | 12.3872 | 12.2751 | [6 empty] | 12.5977 |  |  | 11.4197 |  |  | 9.5675 | 10.4309 | 12.1585 | 7.5772 | 9.1521 | 12.5578 | 8.1757 | 9.7472 | 12.1631 | 9.309 | 10.5209 | 7.8342 | 10.4572 | 8.5034 | 10.4927 | 8.1883 | 9.7826 | 13.136 | 10.6391 | 10.376 | 11.6695 | 8.3491 | 9.9505 | 12.7871 | 8.2117 | 10.6392 | 9.7927 | 10.1731 | 8.4709 | 10.7034 | -0.085719 | 20.9538 | 0.032615 | 0.047806 | -37.8193 | 3.12 | 10.75 | 0.33 | 0.53472 | 0.34589 | 0.49689 | 0.42656 | 0.6169 | -0.52071 | 0.3352 | 0.40303 | 0.40461 | 0.40852 | 0.37998 | 0.58584 | 0.41103 | 0.39545
42810.4395 | -47 | 18.3792 | 18.5112 | 18.5253 | 18.5346 | 17.8734 | 16.5191 | 14.5893 | 16.6757 | 17.165 | 17.2561 | 17.2608 | 16.803 | 15.8242 | 14.4443 | 14.7855 | 14.8119 | 15.3921 | 13.2677 | 13.4011 | 13.9747 |  |  |  | 16.56 | 15.8968 | 14.9997 | 10.6107 | 10.0249 | 10.9529 | 17.0527 | 16.2092 | 15.0242 | 16.7866 | 16.0743 | 15.0788 | 10.7456 | 11.5601 |  | 12.0064 | 10.712 | 10.4687 | 9.2498 |  | 6.2847 | 6.3264 | 5.9038 | 5.9893 | 6.2581 | 6.5897 | 7.0996 | 4.6553 | 6.4772 | 4.7164 | 6.6948 | 7.9511 | 41.9908 | 46.4911 | 42.839 | 15.009 |  |  | -0.11609 | -0.026197 | 0.1405 | 0.19845 | -0.10234 | -0.40196 | 0.45725 | -0.20387 | -0.054083 | 0.047872 | -0.37346 | 8.8703 | 8.8713 | 2.0082 | 15.621 | 16.5649 | 17.1498 | 17.4901 | 17.47 | 16.4598 | 14.8153 | 16.8225 | 17.1617 | 17.4759 | 17.5391 | 17.281 | 16.4911 | 14.7237 | 6.2247 | 8.2068 | 5.5806 | 5.7786 | 5.9673 | 6.5905 | 7.6499 | 15.6546 | 15.3326 | 15.2151 | 14.1738 | 14.0814 | 14.0441 |  |  |  | 10.6723 | 9.7174 | 9.4002 | 9.7158 | -0.15919 | -0.095581 | 12.7313 |  |  | 10.5332 |  |  | 16.8568 | 16.0596 | 15.0181 | 16.3707 | 15.657 | 14.7652 | 10.4097 | 10.9041 | 11.3286 | 11.2259 | 9.2329 |  | 10.5164 | 8.5489 | 9.9088 | 9.5458 | 10.9793 | 12.0793 |  | 12.2158 |  |  | 11.71 | 12.4002 | 12.2897 | [6 empty] | 12.5834 |  |  | 11.4275 |  |  | 9.5748 | 10.4392 | 12.1602 | 7.5703 | 9.157 | 12.5657 | 8.1791 | 9.7475 | 12.1762 | 9.3137 | 10.5146 | 7.8453 | 10.4806 | 8.4995 | 10.4866 | 8.1779 | 9.7718 | 13.134 | 10.6337 | 10.38 | 11.6747 | 8.3414 | 9.9471 | 12.7761 | 8.2006 | 10.625 | 9.7921 | 10.1713 | 8.4593 | 10.7017 | -0.10093 | 20.9552 | 0.032701 | 0.047342 | -37.7912 | 3.12 | 24.07 | 0.25 | -0.40022 | -0.18857 | 0.43669 | 0.519 | -0.37289 | -0.73898 | 0.78817 | 0.40278 | 0.40176 | 0.40935 | 0.38787 | 0.58242 | 0.40986 | 0.3945
42810.4395 | -46 | 18.378 | 18.5165 | 18.5269 | 18.5339 | 17.8744 | 16.5194 | 14.5931 | 16.6782 | 17.1652 | 17.2634 | 17.2653 | 16.8032 | 15.8241 | 14.4515 | 14.7815 | 14.8152 | 15.3855 | 13.2704 | 13.3963 | 13.9713 |  |  |  | 16.5563 | 15.9023 | 14.999 | 10.6141 | 10.053 | 10.9409 | 17.052 | 16.2039 | 15.0173 | 16.7809 | 16.068 | 15.0785 | 10.7438 | 11.6025 |  | 12.0073 | 10.7151 | 10.4706 | 9.2758 |  | 6.2899 | 6.3291 | 5.9168 | 5.9937 | 6.2617 | 6.5788 | 7.0734 | 4.6845 | 6.4777 | 4.6601 | 6.6908 | 7.9522 | 41.9725 | 46.5133 | 42.8184 | 14.9983 |  |  | 0.063303 | -0.076793 | 0.052448 | 0.16494 | 0.046164 | -0.051716 | 0.06824 | 0.097748 | -0.34579 | -0.54439 | -0.35181 | 8.8707 | 8.8721 | 2.0085 | 15.6291 | 16.5682 | 17.1446 | 17.4935 | 17.4703 | 16.4559 | 14.8157 | 16.826 | 17.1719 | 17.4777 | 17.5384 | 17.2704 | 16.4861 | 14.7281 | 6.1517 | 8.1417 | 5.5938 | 5.7524 | 5.9292 | 6.5897 | 7.6465 | 15.6545 | 15.337 | 15.2233 | 14.1827 | 14.0773 | 14.0392 |  |  |  | 10.6764 | 9.721 | 9.4051 | 9.7897 | -0.031557 | -0.058882 | 12.7186 |  |  | 10.528 |  |  | 16.8588 | 16.0495 | 15.0115 | 16.3581 | 15.6546 | 14.7558 | 10.4207 | 10.9008 | 11.3055 | 11.207 | 9.2624 |  | 10.5147 | 8.6862 | 9.9066 | 9.5165 | 10.976 | 12.1009 |  | 12.2118 |  |  | 11.7176 | 12.4166 | 12.3018 | [6 empty] | 12.5775 |  |  | 11.438 |  |  | 9.582 | 10.4538 | 12.1857 | 7.5814 | 9.1723 | 12.5708 | 8.1808 | 9.7545 | 12.1837 | 9.3205 | 10.5156 | 7.8612 | 10.4989 | 8.4953 | 10.4944 | 8.1809 | 9.7656 | 13.1345 | 10.6366 | 10.3859 | 11.6823 | 8.3369 | 9.9435 | 12.7709 | 8.2089 | 10.6108 | 9.7852 | 10.171 | 8.4615 | 10.7177 | -0.042384 | 20.9537 | 0.031565 | 0.048804 | -37.7785 | 3.12 | 12.06 | 0.29 | 0.29553 | -0.32285 | 0.26681 | 0.47315 | 0.25043 | -0.26506 | 0.30448 | 0.4019 | 0.39788 | 0.41005 | 0.39588 | 0.58057 | 0.40908 | 0.39259
42810.4395 | -45 | 18.3747 | 18.5122 | 18.5273 | 18.5351 | 17.8776 | 16.5174 | 14.5885 | 16.6714 | 17.1647 | 17.2585 | 17.2635 | 16.8048 | 15.8202 | 14.453 | 14.7813 | 14.8202 | 15.3885 | 13.2666 | 13.3963 | 13.9686 |  |  |  | 16.5556 | 15.9007 | 15.0032 | 10.6337 | 10.0784 | 10.9519 | 17.0541 | 16.2057 | 15.0166 | 16.7798 | 16.0704 | 15.074 | 10.7378 | 11.6224 |  | 12.0027 | 10.7167 | 10.4724 | 9.3102 |  | 6.2815 | 6.3213 | 5.9127 | 5.9862 | 6.2476 | 6.5642 | 7.0498 | 4.7602 | 6.471 | 4.647 | 6.6866 | 7.9475 | 41.9574 | 46.5263 | 42.7979 | 15.0032 |  |  | -0.008981 | -0.15893 | 0.024848 | -0.018398 | 0.18744 | -0.23702 | 0.32452 | 0.12732 | -0.59254 | -0.56663 | -0.39115 | 8.8699 | 8.8712 | 2.0083 | 15.6343 | 16.5767 | 17.1522 | 17.4975 | 17.4765 | 16.4643 | 14.8246 | 16.8258 | 17.1772 | 17.4844 | 17.5407 | 17.2852 | 16.4955 | 14.7376 | 6.1025 | 8.117 | 5.5387 | 5.7916 | 5.8824 | 6.5953 | 7.652 | 15.6637 | 15.3365 | 15.2244 | 14.1787 | 14.0874 | 14.0457 |  |  |  | 10.6802 | 9.7222 | 9.4071 | 9.8246 | 0.027805 | -0.011832 | 12.715 |  |  | 10.5298 |  |  | 16.8544 | 16.0508 | 15.0189 | 16.3567 | 15.6538 | 14.7526 | 10.4325 | 10.8963 | 11.2866 | 11.1903 | 9.3075 |  | 10.5011 | 8.8519 | 9.9071 | 9.4806 | 10.9774 | 12.1298 |  | 12.2135 |  |  | 11.7218 | 12.4354 | 12.3123 | [6 empty] | 12.5906 |  |  | 11.4482 |  |  | 9.5674 | 10.4451 | 12.2124 | 7.5788 | 9.1767 | 12.5653 | 8.1755 | 9.7453 | 12.1923 | 9.3133 | 10.5038 | 7.8666 | 10.4916 | 8.4843 | 10.4778 | 8.1952 | 9.7806 | 13.1446 | 10.6428 | 10.3889 | 11.6896 | 8.3388 | 9.9409 | 12.7752 | 8.2074 | 10.6075 | 9.7942 | 10.1749 | 8.4605 | 10.7345 | -0.080519 | 20.9538 | 0.031536 | 0.048218 | -37.7289 | 3.1199 | -17.49 | 0.28 | -0.11132 | -0.46445 | 0.18365 | -0.15802 | 0.50461 | -0.56744 | 0.66396 | 0.4002 | 0.39329 | 0.4111 | 0.402 | 0.58733 | 0.40793 | 0.39174
42810.4395 | -44 | 18.376 | 18.5066 | 18.5286 | 18.5348 | 17.8751 | 16.5182 | 14.5867 | 16.6714 | 17.1648 | 17.2557 | 17.2595 | 16.7987 | 15.8269 | 14.4499 | 14.7735 | 14.8105 | 15.3859 | 13.2608 | 13.3861 | 13.9656 |  |  |  | 16.5518 | 15.8931 | 14.9842 | 10.622 | 10.1036 | 10.94 | 17.0508 | 16.1943 | 15.0125 | 16.7826 | 16.0735 | 15.0672 | 10.7424 | 11.6444 |  | 12.001 | 10.7217 | 10.4581 | 9.3313 |  | 6.2795 | 6.3356 | 5.927 | 5.9969 | 6.2497 | 6.5574 | 7.0251 | 4.8078 | 6.473 | 4.6521 | 6.6892 | 7.9505 | 41.954 | 46.5313 | 42.7828 | 15.0118 |  |  | 0.025847 | -0.36198 | 0.073476 | 0.15114 | 0.057992 | 0.038968 | 0.62219 | -0.010676 | 0.20026 | -0.51334 | -0.37943 | 8.8685 | 8.8695 | 2.0081 | 15.6345 | 16.57 | 17.1478 | 17.4941 | 17.4766 | 16.4573 | 14.8215 | 16.8251 | 17.1774 | 17.4803 | 17.5324 | 17.2787 | 16.4921 | 14.734 | 6.0599 | 8.0793 | 5.4721 | 5.7594 | 5.8276 | 6.584 | 7.651 | 15.6644 | 15.3322 | 15.2267 | 14.1765 | 14.0875 | 14.0417 |  |  |  | 10.6796 | 9.7191 | 9.4064 | 9.8144 | -0.055058 | 0.099771 | 12.7266 |  |  | 10.537 |  |  | 16.8547 | 16.0577 | 15.0221 | 16.3654 | 15.6596 | 14.7614 | 10.4622 | 10.8994 | 11.2838 | 11.1877 | 9.3586 |  | 10.5029 | 9.0151 | 9.9067 | 9.45 | 10.9748 | 12.1529 |  | 12.208 |  |  | 11.7082 | 12.4409 | 12.3276 | [6 empty] | 12.5964 |  |  | 11.4438 |  |  | 9.5641 | 10.4462 | 12.2321 | 7.5881 | 9.1779 | 12.5713 | 8.1769 | 9.7394 | 12.2121 | 9.3129 | 10.5089 | 7.8701 | 10.4821 | 8.4767 | 10.4798 | 8.1923 | 9.7605 | 13.1484 | 10.6391 | 10.3847 | 11.6874 | 8.3421 | 9.943 | 12.7704 | 8.1595 | 10.5959 | 9.7859 | 10.1705 | 8.4539 | 10.7409 | 0.066242 | 20.955 | 0.03219 | 0.04837 | -37.7395 | 3.1199 | 6.24 | 0.24 | 0.18884 | -0.70095 | 0.31581 | 0.45293 | 0.28067 | 0.23008 | 0.91935 | 0.39884 | 0.38875 | 0.41186 | 0.40542 | 0.59461 | 0.40749 | 0.392
42810.4395 | -43 | 18.3706 | 18.5086 | 18.5254 | 18.5278 | 17.8777 | 16.5212 | 14.5975 | 16.6769 | 17.1681 | 17.2599 | 17.2678 | 16.802 | 15.8264 | 14.4514 | 14.7782 | 14.8031 | 15.383 | 13.2635 | 13.3903 | 13.9673 |  |  |  | 16.5486 | 15.8885 | 14.9871 | 10.636 | 10.1438 | 10.9171 | 17.0455 | 16.1927 | 15.0069 | 16.7688 | 16.0641 | 15.0589 | 10.7402 | 11.6795 |  | 11.9886 | 10.7263 | 10.4613 | 9.3554 |  | 6.2836 | 6.3406 | 5.935 | 6.0016 | 6.2548 | 6.5334 | 7.0003 | 4.8962 | 6.4745 | 4.6588 | 6.6849 | 7.9572 | 41.9665 | 46.5353 | 42.7649 | 15.0077 |  |  | -0.003725 | -0.009113 | 0.26864 | -0.07557 | 0.10333 | 0.15068 | 0.42966 | 0.016264 | -1.0818 | -0.60733 | -0.39572 | 8.871 | 8.8722 | 2.0082 | 15.635 | 16.5739 | 17.1517 | 17.4951 | 17.4773 | 16.4527 | 14.8164 | 16.8246 | 17.1736 | 17.4745 | 17.5332 | 17.2779 | 16.4948 | 14.734 | 6.0415 | 8.1043 | 5.4349 | 5.6955 | 5.7664 | 6.5871 | 7.6489 | 15.6675 | 15.3434 | 15.2326 | 14.1742 | 14.076 | 14.0487 |  |  |  | 10.6765 | 9.7342 | 9.4128 | 9.8132 | -0.092337 | -0.08316 | 12.7314 |  |  | 10.5342 |  |  | 16.8531 | 16.0539 | 15.0199 | 16.3668 | 15.6548 | 14.7606 | 10.4801 | 10.8889 | 11.2646 | 11.1785 | 9.3968 |  | 10.5094 | 9.165 | 9.9131 | 9.4225 | 10.9762 | 12.1611 |  | 12.2147 |  |  | 11.7094 | 12.4431 | 12.3411 | [6 empty] | 12.5969 |  |  | 11.4507 |  |  | 9.5628 | 10.4554 | 12.2313 | 7.5868 | 9.1904 | 12.5674 | 8.16 | 9.7498 | 12.226 | 9.3137 | 10.4998 | 7.8463 | 10.4504 | 8.4697 | 10.4745 | 8.1857 | 9.7452 | 13.1399 | 10.6493 | 10.4083 | 11.7018 | 8.3463 | 9.9441 | 12.7755 | 8.146 | 10.5874 | 9.7953 | 10.1832 | 8.471 | 10.7507 | 0.091665 | 20.9547 | 0.032592 | 0.048037 | -37.8732 | 3.1199 | 4.97 | 0.21 | -0.071687 | -0.11122 | 0.60386 | -0.32028 | 0.37464 | 0.4524 | 0.76394 | 0.39799 | 0.38479 | 0.41267 | 0.40782 | 0.59851 | 0.40675 | 0.39194
42810.4395 | -42 | 18.3631 | 18.5145 | 18.5211 | 18.5235 | 17.8727 | 16.5172 | 14.5946 | 16.6698 | 17.1688 | 17.2491 | 17.2671 | 16.7967 | 15.8259 | 14.4459 | 14.7749 | 14.8099 | 15.387 | 13.2772 | 13.3996 | 13.9639 |  |  |  | 16.5505 | 15.8925 | 14.9931 | 10.6337 | 10.1801 | 10.8555 | 17.0473 | 16.1984 | 15.0146 | 16.7782 | 16.0707 | 15.0643 | 10.7444 | 11.7316 |  | 11.9855 | 10.7365 | 10.4832 | 9.3805 |  | 6.2885 | 6.3462 | 5.9281 | 6.004 | 6.2462 | 6.5232 | 6.975 | 4.9987 | 6.4671 | 4.6838 | 6.6833 | 7.9501 | 41.9634 | 46.5537 | 42.7557 | 14.9999 |  |  | -0.042493 | -0.29036 | 0.099104 | 0.059798 | 0.10202 | -0.21994 | 0.46448 | 0.028748 | -0.33489 | -0.55342 | -0.29756 | 8.8697 | 8.8705 | 2.0085 | 15.6304 | 16.5694 | 17.1483 | 17.496 | 17.4731 | 16.4542 | 14.8147 | 16.8229 | 17.1671 | 17.4757 | 17.5356 | 17.2748 | 16.4908 | 14.7283 | 6.0566 | 8.1159 | 5.3933 | 5.6285 | 5.7032 | 6.5762 | 7.6453 | 15.6742 | 15.355 | 15.2387 | 14.187 | 14.0964 | 14.0503 |  |  |  | 10.6816 | 9.7658 | 9.4063 | 9.7893 | -0.024871 | -0.063775 | 12.7361 |  |  | 10.5397 |  |  | 16.8539 | 16.0544 | 15.0234 | 16.3621 | 15.648 | 14.7577 | 10.4876 | 10.8914 | 11.2467 | 11.1673 | 9.4153 |  | 10.511 | 9.3086 | 9.9123 | 9.399 | 10.9723 | 12.1895 |  | 12.207 |  |  | 11.7176 | 12.4526 | 12.36 | [6 empty] | 12.6011 |  |  | 11.4547 |  |  | 9.5756 | 10.4635 | 12.2615 | 7.5911 | 9.2132 | 12.5876 | 8.1819 | 9.7477 | 12.2531 | 9.3135 | 10.5049 | 7.8259 | 10.4654 | 8.4677 | 10.4689 | 8.1736 | 9.7377 | 13.1474 | 10.6334 | 10.4039 | 11.712 | 8.3521 | 9.9469 | 12.7958 | 8.1388 | 10.5854 | 9.779 | 10.1929 | 8.4659 | 10.7398 | 0.11439 | 20.9544 | 0.032345 | 0.048052 | -37.9089 | 3.1198 | 9.84 | 0.29 | -0.2421 | -0.6278 | 0.36678 | 0.2849 | 0.37224 | -0.54656 | 0.79428 | 0.39753 | 0.38078 | 0.41319 | 0.40487 | 0.6027 | 0.4062 | 0.39277
42810.4396 | -41 | 18.3755 | 18.5099 | 18.5278 | 18.5306 | 17.8762 | 16.5171 | 14.5848 | 16.6643 | 17.1669 | 17.257 | 17.2657 | 16.7933 | 15.8268 | 14.4441 | 14.7809 | 14.8135 | 15.397 | 13.2751 | 13.3987 | 13.9632 |  |  |  | 16.5659 | 15.9004 | 15.001 | 10.6442 | 10.2239 | 10.8262 | 17.0492 | 16.2089 | 15.0216 | 16.7813 | 16.0712 | 15.0736 | 10.7452 | 11.8067 |  | 11.999 | 10.7553 | 10.4953 | 9.4244 |  | 6.3025 | 6.3593 | 5.9412 | 6.0139 | 6.2605 | 6.529 | 6.9633 | 5.0841 | 6.4734 | 4.7099 | 6.6949 | 7.9529 | 41.9614 | 46.5633 | 42.7549 | 14.994 |  |  | 0.019931 | -0.13725 | 0.07216 | 0.01643 | -0.01232 | -0.13911 | 0.49931 | -0.15656 | -0.4894 | -0.61489 | -0.29041 | 8.8708 | 8.8719 | 2.0081 | 15.6255 | 16.5702 | 17.1424 | 17.4896 | 17.4697 | 16.4517 | 14.8154 | 16.8205 | 17.1721 | 17.4749 | 17.5327 | 17.2841 | 16.4849 | 14.7283 | 6.1158 | 8.1289 | 5.3835 | 5.5852 | 5.6426 | 6.5849 | 7.6598 | 15.6616 | 15.3416 | 15.2267 | 14.1779 | 14.0835 | 14.042 |  |  |  | 10.6748 | 9.7612 | 9.4045 | 9.7431 | 0.21805 | -0.080525 | 12.7414 |  |  | 10.5416 |  |  | 16.8593 | 16.0584 | 15.0204 | 16.3574 | 15.6552 | 14.7591 | 10.4914 | 10.9055 | 11.2458 | 11.1603 | 9.443 |  | 10.5101 | 9.3743 | 9.9196 | 9.385 | 10.9742 | 12.2299 |  | 12.2141 |  |  | 11.7381 | 12.4609 | 12.3637 | [6 empty] | 12.5931 |  |  | 11.4586 |  |  | 9.5645 | 10.4561 | 12.2339 | 7.5689 | 9.206 | 12.5882 | 8.1633 | 9.747 | 12.2523 | 9.2963 | 10.5005 | 7.8119 | 10.4506 | 8.459 | 10.4521 | 8.1357 | 9.7444 | 13.1315 | 10.6302 | 10.3983 | 11.728 | 8.3472 | 9.9429 | 12.787 | 8.1117 | 10.5752 | 9.7695 | 10.1833 | 8.4727 | 10.7459 | 0.055457 | 20.9542 | 0.03289 | 0.048276 | -37.915 | 3.1199 | 4.84 | 0.29 | 0.1658 | -0.43164 | 0.31298 | 0.14934 | -0.12936 | -0.43469 | 0.82353 | 0.39673 | 0.37919 | 0.41365 | 0.39931 | 0.60548 | 0.405 | 0.39383
42810.4396 | -40 | 18.3751 | 18.5138 | 18.5218 | 18.5344 | 17.8855 | 16.5175 | 14.5892 | 16.6725 | 17.1644 | 17.2576 | 17.2624 | 16.7988 | 15.8315 | 14.4558 | 14.776 | 14.81 | 15.3913 | 13.263 | 13.3934 | 13.9652 |  |  |  | 16.5513 | 15.8962 | 14.9992 | 10.6355 | 10.2429 | 10.804 | 17.0494 | 16.2006 | 15.0093 | 16.7813 | 16.0583 | 15.07 | 10.7417 | 11.8559 |  | 11.9939 | 10.7637 | 10.5049 | 9.4765 |  | 6.3134 | 6.3738 | 5.9508 | 6.0272 | 6.2747 | 6.5292 | 6.9466 | 5.1442 | 6.4901 | 4.7505 | 6.6918 | 7.9552 | 41.9637 | 46.5735 | 42.7406 | 15.0049 |  |  | 0.12179 | 0.024403 | 0.10042 | 0.051914 | 0.1743 | -0.14634 | 0.52034 | -0.044192 | -0.61122 | -0.087659 | -0.42314 | 8.8685 | 8.8698 | 2.008 | 15.6255 | 16.5652 | 17.1449 | 17.4854 | 17.4764 | 16.4479 | 14.8198 | 16.8146 | 17.1687 | 17.4754 | 17.5329 | 17.2755 | 16.4851 | 14.7334 | 6.1397 | 8.1305 | 5.4046 | 5.6151 | 5.5874 | 6.5814 | 7.6616 | 15.6623 | 15.3328 | 15.226 | 14.1756 | 14.0886 | 14.0469 |  |  |  | 10.6717 | 9.7698 | 9.4081 | 9.7285 | 0.0097736 | -0.11101 | 12.7415 |  |  | 10.5374 |  |  | 16.8562 | 16.0531 | 15.0097 | 16.3522 | 15.6526 | 14.7541 | 10.485 | 10.904 | 11.2369 | 11.1549 | 9.4537 |  | 10.5097 | 9.3715 | 9.9221 | 9.3669 | 10.9802 | 12.2533 |  | 12.2262 |  |  | 11.7461 | 12.4455 | 12.3798 | [6 empty] | 12.5999 |  |  | 11.4632 |  |  | 9.563 | 10.4487 | 12.2285 | 7.537 | 9.2196 | 12.5743 | 8.1622 | 9.7428 | 12.249 | 9.2917 | 10.4995 | 7.7847 | 10.436 | 8.449 | 10.4335 | 8.1228 | 9.7351 | 13.1154 | 10.617 | 10.3906 | 11.7446 | 8.3412 | 9.9402 | 12.7914 | 8.1089 | 10.5901 | 9.761 | 10.1855 | 8.472 | 10.7503 | 0.030611 | 20.9542 | 0.032328 | 0.048406 | -37.784 | 3.1199 | 1.01 | 0.32 | 0.40982 | 0.18201 | 0.36921 | 0.26547 | 0.48657 | -0.44584 | 0.8407 | 0.39642 | 0.37935 | 0.41435 | 0.39626 | 0.60334 | 0.40344 | 0.39413
42810.4396 | -39 | 18.3788 | 18.513 | 18.5262 | 18.541 | 17.8846 | 16.5184 | 14.5914 | 16.6764 | 17.1635 | 17.2618 | 17.27 | 16.7973 | 15.8284 | 14.4545 | 14.7808 | 14.8119 | 15.3876 | 13.2624 | 13.3925 | 13.9671 |  |  |  | 16.5581 | 15.8979 | 14.9952 | 10.6461 | 10.2625 | 10.8088 | 17.0522 | 16.2002 | 15.0169 | 16.7792 | 16.0629 | 15.07 | 10.7487 | 11.888 |  | 11.9954 | 10.7752 | 10.5187 | 9.5333 |  | 6.3214 | 6.3781 | 5.9674 | 6.0458 | 6.2868 | 6.5313 | 6.9439 | 5.0452 | 6.4831 | 4.8012 | 6.696 | 7.9569 | 41.966 | 46.5732 | 42.7323 | 15.0205 |  |  | 0.029791 | -0.070881 | 0.14379 | 0.14654 | -0.028748 | -0.147 | 0.56896 | -0.10267 | -0.03618 | -0.66335 | -0.45791 | 8.8677 | 8.869 | 2.0083 | 15.6374 | 16.5789 | 17.1493 | 17.4955 | 17.4765 | 16.456 | 14.8202 | 16.8272 | 17.1709 | 17.4788 | 17.5345 | 17.2817 | 16.4899 | 14.7233 | 6.1962 | 8.1371 | 5.4633 | 5.6268 | 5.5868 | 6.5768 | 7.6575 | 15.666 | 15.3328 | 15.2279 | 14.1765 | 14.085 | 14.0498 |  |  |  | 10.6827 | 9.7691 | 9.4117 | 9.7135 | 0.1212 | -0.076949 | 12.7374 |  |  | 10.5314 |  |  | 16.8502 | 16.0478 | 15.0143 | 16.3568 | 15.6442 | 14.7508 | 10.4775 | 10.9067 | 11.2409 | 11.1637 | 9.4647 |  | 10.5074 | 9.3703 | 9.9245 | 9.3569 | 10.9805 | 12.2655 |  | 12.2162 |  |  | 11.7533 | 12.4475 | 12.3991 | [6 empty] | 12.5928 |  |  | 11.4655 |  |  | 9.5534 | 10.46 | 12.2284 | 7.547 | 9.2172 | 12.5852 | 8.1596 | 9.7484 | 12.26 | 9.2903 | 10.5031 | 7.7808 | 10.4388 | 8.4596 | 10.438 | 8.1283 | 9.7465 | 13.1082 | 10.6232 | 10.3907 | 11.7537 | 8.3479 | 9.9382 | 12.8013 | 8.1124 | 10.61 | 9.7494 | 10.1938 | 8.4684 | 10.7356 | 0.0038398 | 20.9538 | 0.032477 | 0.047516 | -37.7723 | 3.1199 | 11.28 | 0.25 | 0.20269 | -0.3102 | 0.44182 | 0.44602 | -0.19761 | -0.44684 | 0.87911 | 0.39604 | 0.37946 | 0.41463 | 0.38944 | 0.59635 | 0.40209 | 0.39491
42810.4396 | -38 | 18.3749 | 18.5064 | 18.5204 | 18.5338 | 17.8766 | 16.5146 | 14.585 | 16.6682 | 17.1556 | 17.2564 | 17.2623 | 16.7923 | 15.8194 | 14.448 | 14.7802 | 14.8094 | 15.3808 | 13.2639 | 13.394 | 13.9616 |  |  |  | 16.5503 | 15.8966 | 14.9861 | 10.6443 | 10.2845 | 10.7907 | 17.0524 | 16.1959 | 15.0211 | 16.7818 | 16.0705 | 15.0741 | 10.7527 | 11.88 |  | 12.0015 | 10.7859 | 10.5348 | 9.5783 |  | 6.3244 | 6.3836 | 5.9925 | 6.0599 | 6.2998 | 6.5409 | 6.9384 | 4.9263 | 6.4716 | 4.8164 | 6.6922 | 7.9547 | 41.9408 | 46.5785 | 42.7174 | 15.0336 |  |  | 0.075131 | -0.10965 | 0.13327 | 0.12814 | 0.32872 | -0.10428 | 0.58408 | 0.096432 | -0.25861 | -0.040035 | -0.35379 | 8.8708 | 8.872 | 2.0082 | 15.6384 | 16.5762 | 17.1489 | 17.4994 | 17.4728 | 16.4594 | 14.822 | 16.8265 | 17.1757 | 17.4771 | 17.544 | 17.2828 | 16.4921 | 14.7262 | 6.2498 | 8.152 | 5.4984 | 5.6746 | 5.6215 | 6.5824 | 7.6624 | 15.6537 | 15.3249 | 15.2183 | 14.1782 | 14.0727 | 14.0392 |  |  |  | 10.6802 | 9.7633 | 9.4102 | 9.6775 | 0.080481 | 0.0081174 | 12.745 |  |  | 10.5328 |  |  | 16.8492 | 16.0472 | 15.0256 | 16.367 | 15.6477 | 14.7545 | 10.482 | 10.9129 | 11.2509 | 11.1747 | 9.4418 |  | 10.5174 | 9.2723 | 9.9297 | 9.353 | 10.981 | 12.2573 |  | 12.2292 |  |  | 11.7538 | 12.4472 | 12.4105 | [6 empty] | 12.5841 |  |  | 11.4581 |  |  | 9.5609 | 10.4714 | 12.2245 | 7.5307 | 9.2124 | 12.5837 | 8.1517 | 9.7478 | 12.2652 | 9.2946 | 10.4998 | 7.773 | 10.447 | 8.4603 | 10.4319 | 8.1454 | 9.7641 | 13.1164 | 10.6336 | 10.3909 | 11.7853 | 8.3383 | 9.9319 | 12.7959 | 8.1263 | 10.6194 | 9.7542 | 10.1927 | 8.4792 | 10.745 | 0.10245 | 20.9633 | 0.032557 | 0.048377 | -37.7511 | 3.1199 | 5.59 | 0.25 | 0.32188 | -0.38582 | 0.42536 | 0.41708 | 0.66822 | -0.37637 | 0.89072 | 0.39701 | 0.38236 | 0.41476 | 0.38413 | 0.59302 | 0.40097 | 0.39583
42810.4396 | -37 | 18.3831 | 18.5093 | 18.5165 | 18.5275 | 17.88 | 16.5195 | 14.5833 | 16.6724 | 17.1661 | 17.2519 | 17.2633 | 16.7968 | 15.8265 | 14.4545 | 14.7815 | 14.809 | 15.3837 | 13.2743 | 13.3966 | 13.9701 |  |  |  | 16.5544 | 15.8964 | 14.9956 | 10.6531 | 10.3046 | 10.7876 | 17.0543 | 16.2034 | 15.0151 | 16.7851 | 16.0686 | 15.076 | 10.7535 | 11.8576 |  | 11.9995 | 10.7955 | 10.5506 | 9.612 |  | 6.3352 | 6.3925 | 6.0003 | 6.0715 | 6.3196 | 6.566 | 6.938 | 4.8018 | 6.4772 | 4.761 | 6.6958 | 7.9519 | 41.9307 | 46.5867 | 42.7051 | 15.0552 |  |  | -0.012265 | -0.023569 | 0.13327 | 0.31673 | -0.065548 | -0.58661 | 0.62745 | 0.17792 | -0.74705 | -0.10214 | -0.42393 | 8.8707 | 8.872 | 2.0082 | 15.6267 | 16.566 | 17.1371 | 17.4917 | 17.4655 | 16.4455 | 14.8059 | 16.8108 | 17.1641 | 17.4753 | 17.5265 | 17.2763 | 16.4831 | 14.7141 | 6.2847 | 8.182 | 5.5249 | 5.6793 | 5.6977 | 6.5868 | 7.6665 | 15.6539 | 15.3216 | 15.2183 | 14.162 | 14.0795 | 14.031 |  |  |  | 10.6713 | 9.7592 | 9.4065 | 9.6519 | 0.038543 | -0.060764 | 12.755 |  |  | 10.5394 |  |  | 16.8553 | 16.0508 | 15.018 | 16.3686 | 15.6486 | 14.7615 | 10.4889 | 10.9173 | 11.2594 | 11.1769 | 9.4376 |  | 10.5186 | 9.1228 | 9.9367 | 9.357 | 10.9842 | 12.2544 |  | 12.2173 |  |  | 11.7604 | 12.446 | 12.421 | [6 empty] | 12.5837 |  |  | 11.4548 |  |  | 9.5602 | 10.4595 | 12.215 | 7.5131 | 9.196 | 12.5849 | 8.1481 | 9.7404 | 12.2624 | 9.2942 | 10.4997 | 7.7514 | 10.4429 | 8.4513 | 10.4155 | 8.1601 | 9.7812 | 13.12 | 10.6343 | 10.3971 | 11.7989 | 8.329 | 9.9385 | 12.7987 | 8.1453 | 10.6221 | 9.7488 | 10.1943 | 8.48 | 10.744 | -0.010027 | 20.9604 | 0.032741 | 0.049615 | -37.7793 | 3.1199 | 15.3 | 0.29 | -0.13005 | -0.17888 | 0.42536 | 0.65575 | -0.2984 | -0.89269 | 0.92324 | 0.39716 | 0.38674 | 0.41475 | 0.38076 | 0.59054 | 0.40006 | 0.39624
42810.4396 | -36 | 18.3676 | 18.5058 | 18.5207 | 18.5271 | 17.8795 | 16.5151 | 14.5855 | 16.67 | 17.1549 | 17.2514 | 17.2571 | 16.7976 | 15.8235 | 14.4534 | 14.7783 | 14.8072 | 15.3902 | 13.2722 | 13.3998 | 13.9759 |  |  |  | 16.5577 | 15.8963 | 14.9949 | 10.6623 | 10.3197 | 10.8093 | 17.0551 | 16.2077 | 15.0188 | 16.7851 | 16.0776 | 15.0804 | 10.7552 | 11.8499 |  | 12 | 10.8157 | 10.5577 | 9.6152 |  | 6.3458 | 6.3971 | 6.0121 | 6.082 | 6.3342 | 6.6036 | 6.9477 | 4.7495 | 6.4699 | 4.7182 | 6.6966 | 7.9543 | 41.935 | 46.5832 | 42.6717 | 15.0684 |  |  | -0.053009 | -0.14053 | 0.047192 | 0.099882 | -0.14769 | -0.056316 | 0.47762 | 0.30342 | -0.52657 | 0.71189 | -0.40685 | 8.8708 | 8.8721 | 2.0081 | 15.6183 | 16.572 | 17.1355 | 17.4866 | 17.46 | 16.4456 | 14.8087 | 16.82 | 17.1615 | 17.4733 | 17.5251 | 17.2736 | 16.4834 | 14.7167 | 6.2711 | 8.1937 | 5.6034 | 5.7199 | 5.7069 | 6.5798 | 7.6592 | 15.6557 | 15.3229 | 15.2138 | 14.1655 | 14.0718 | 14.0338 |  |  |  | 10.6717 | 9.7623 | 9.4115 | 9.6321 | -0.05364 | 0.044064 | 12.7589 |  |  | 10.5422 |  |  | 16.8587 | 16.0532 | 15.0143 | 16.369 | 15.6487 | 14.7603 | 10.4943 | 10.9213 | 11.2659 | 11.1807 | 9.4281 |  | 10.5154 | 8.9809 | 9.9272 | 9.3676 | 10.9926 | 12.2508 |  | 12.2274 |  |  | 11.7667 | 12.441 | 12.4253 | [6 empty] | 12.5894 |  |  | 11.4513 |  |  | 9.5604 | 10.4584 | 12.2169 | 7.5091 | 9.1944 | 12.5916 | 8.1435 | 9.7348 | 12.2676 | 9.2961 | 10.4999 | 7.7468 | 10.4455 | 8.4491 | 10.4102 | 8.1871 | 9.8034 | 13.1299 | 10.6448 | 10.4019 | 11.8321 | 8.3377 | 9.9454 | 12.7983 | 8.1682 | 10.6439 | 9.7612 | 10.2044 | 8.4832 | 10.7516 | 0.14039 | 20.955 | 0.033057 | 0.049528 | -37.9072 | 3.1199 | 15.21 | 0.3 | -0.27038 | -0.4368 | 0.25312 | 0.36825 | -0.44795 | -0.27661 | 0.80556 | 0.39732 | 0.39037 | 0.41474 | 0.38146 | 0.58098 | 0.40003 | 0.39681
42810.4396 | -35 | 18.3719 | 18.5115 | 18.517 | 18.5376 | 17.8807 | 16.5195 | 14.5887 | 16.6711 | 17.1576 | 17.2504 | 17.2608 | 16.8021 | 15.8299 | 14.4522 | 14.7798 | 14.8085 | 15.3877 | 13.2644 | 13.3936 | 13.9713 |  |  |  | 16.5531 | 15.8899 | 14.9887 | 10.6641 | 10.3226 | 10.8283 | 17.0464 | 16.1964 | 15.0163 | 16.7828 | 16.0732 | 15.0726 | 10.749 | 11.8682 |  | 12.002 | 10.8249 | 10.5685 | 9.566 |  | 6.3541 | 6.3887 | 6.0104 | 6.0935 | 6.3267 | 6.6146 | 6.9624 | 4.7176 | 6.4688 | 4.6622 | 6.6946 | 7.9596 | 41.9216 | 46.5955 | 42.6607 | 15.0801 |  |  | -0.076665 | 0.031631 | 0.034048 | 0.04337 | 0.18481 | -0.049744 | 0.52165 | 0.16083 | -0.80349 | -0.47537 | -0.27729 | 8.87 | 8.8709 | 2.0083 | 15.6189 | 16.5726 | 17.1397 | 17.4905 | 17.4619 | 16.4542 | 14.8098 | 16.8225 | 17.1647 | 17.4746 | 17.5316 | 17.2735 | 16.4803 | 14.7227 | 6.2371 | 8.1845 | 5.6079 | 5.7956 | 5.6968 | 6.5785 | 7.6677 | 15.6521 | 15.323 | 15.2126 | 14.1671 | 14.0756 | 14.0316 |  |  |  | 10.6725 | 9.7638 | 9.4097 | 9.6132 | -0.081599 | -0.16427 | 12.7593 |  |  | 10.5439 |  |  | 16.8569 | 16.0522 | 15.0154 | 16.3712 | 15.6499 | 14.7553 | 10.4996 | 10.9258 | 11.2645 | 11.1793 | 9.4178 |  | 10.5129 | 8.8674 | 9.933 | 9.3754 | 10.988 | 12.2422 |  | 12.2322 |  |  | 11.7804 | 12.4408 | 12.4435 | [6 empty] | 12.5873 |  |  | 11.4551 |  |  | 9.5646 | 10.471 | 12.2317 | 7.5126 | 9.1937 | 12.5952 | 8.1419 | 9.7414 | 12.2901 | 9.2938 | 10.5084 | 7.7532 | 10.4528 | 8.4646 | 10.4095 | 8.2022 | 9.8174 | 13.1296 | 10.6453 | 10.393 | 11.8581 | 8.3354 | 9.9506 | 12.7986 | 8.1828 | 10.6505 | 9.771 | 10.203 | 8.4836 | 10.7488 | 0.07125 | 20.9527 | 0.033395 | 0.048623 | -37.7615 | 3.1199 | -5.05 | 0.22 | -0.32517 | 0.20723 | 0.215 | 0.24265 | 0.5011 | -0.25998 | 0.84189 | 0.39752 | 0.39371 | 0.41437 | 0.38509 | 0.58146 | 0.40119 | 0.39736
42810.4396 | -34 | 18.3765 | 18.5097 | 18.5268 | 18.5362 | 17.8836 | 16.5255 | 14.5891 | 16.6763 | 17.1572 | 17.2553 | 17.2635 | 16.8033 | 15.8301 | 14.4569 | 14.7786 | 14.8147 | 15.3876 | 13.2712 | 13.395 | 13.9725 |  |  |  | 16.5574 | 15.8893 | 14.9954 | 10.6788 | 10.3339 | 10.8501 | 17.052 | 16.2068 | 15.0188 | 16.792 | 16.0725 | 15.0793 | 10.762 | 11.9181 |  | 12.007 | 10.8402 | 10.5956 | 9.5523 |  | 6.3505 | 6.4096 | 6.0219 | 6.1152 | 6.3394 | 6.619 | 6.9929 | 4.7535 | 6.4661 | 4.6008 | 6.6949 | 7.9542 | 41.9046 | 46.602 | 42.6506 | 15.0843 |  |  | 0.003503 | 0.13348 | 0.18256 | 0.14654 | 0.052732 | 0.18419 | 0.57356 | 0.30342 | -1.7586 | -1.0372 | -0.27928 | 8.8673 | 8.8683 | 2.0082 | 15.6182 | 16.5632 | 17.1412 | 17.4823 | 17.4582 | 16.4503 | 14.7977 | 16.8145 | 17.1554 | 17.4701 | 17.5237 | 17.2703 | 16.4727 | 14.7208 | 6.1729 | 8.1892 | 5.5726 | 5.8073 | 5.7441 | 6.5864 | 7.6666 | 15.654 | 15.329 | 15.2208 | 14.1706 | 14.0849 | 14.0374 |  |  |  | 10.6769 | 9.7732 | 9.4231 | 9.6059 | -0.23112 | 0.047828 | 12.7608 |  |  | 10.546 |  |  | 16.8573 | 16.061 | 15.015 | 16.3681 | 15.6568 | 14.7558 | 10.5 | 10.9374 | 11.2618 | 11.1759 | 9.4086 |  | 10.5151 | 8.7857 | 9.9324 | 9.3742 | 10.9811 | 12.2289 |  | 12.2359 |  |  | 11.7886 | 12.4395 | 12.4549 | [6 empty] | 12.5843 |  |  | 11.4571 |  |  | 9.5669 | 10.474 | 12.2353 | 7.5116 | 9.2021 | 12.5933 | 8.1395 | 9.7468 | 12.2875 | 9.2897 | 10.5071 | 7.7559 | 10.4672 | 8.4682 | 10.4053 | 8.2139 | 9.8278 | 13.1375 | 10.6386 | 10.3844 | 11.8655 | 8.3285 | 9.9507 | 12.7937 | 8.1913 | 10.6642 | 9.7678 | 10.2071 | 8.4864 | 10.7536 | 0.11767 | 20.9562 | 0.033573 | 0.047545 | -37.891 | 3.1199 | 5.78 | 0.45 | 0.06951 | 0.42571 | 0.49785 | 0.44605 | 0.26767 | 0.50026 | 0.88279 | 0.39785 | 0.39596 | 0.41417 | 0.39314 | 0.58526 | 0.402 | 0.39771
42810.4397 | -33 | 18.3672 | 18.5111 | 18.5097 | 18.5282 | 17.8751 | 16.5188 | 14.591 | 16.6704 | 17.1602 | 17.2565 | 17.2614 | 16.8025 | 15.8293 | 14.448 | 14.781 | 14.8129 | 15.3856 | 13.2678 | 13.392 | 13.9694 |  |  |  | 16.5547 | 15.8949 | 14.9917 | 10.6888 | 10.3359 | 10.874 | 17.0581 | 16.2086 | 15.0209 | 16.785 | 16.0734 | 15.0754 | 10.7662 | 11.9534 |  | 12.015 | 10.8572 | 10.6117 | 9.521 |  | 6.3542 | 6.4151 | 6.0253 | 6.1302 | 6.3489 | 6.6367 | 7.0346 | 4.7316 | 6.4616 | 4.4905 | 6.6901 | 7.9607 | 41.9037 | 46.6083 | 42.646 | 15.0824 |  |  | 0.039647 | 0.086827 | 0.12013 | 0.14851 | 0.089532 | -0.15094 | 0.47368 | 0.29422 | -1.2137 | -0.87693 | -0.36691 | 8.8689 | 8.8699 | 2.0081 | 15.6268 | 16.5672 | 17.1404 | 17.4873 | 17.4737 | 16.4522 | 14.8109 | 16.8203 | 17.1599 | 17.4703 | 17.5261 | 17.2758 | 16.4811 | 14.7227 | 6.1019 | 8.185 | 5.5375 | 5.7691 | 5.7532 | 6.5889 | 7.6671 | 15.6534 | 15.3238 | 15.206 | 14.1709 | 14.0683 | 14.0278 |  |  |  | 10.6715 | 9.7663 | 9.4152 | 9.6027 | -0.22382 | -0.27343 | 12.7633 |  |  | 10.5487 |  |  | 16.8574 | 16.0653 | 15.0173 | 16.3677 | 15.6558 | 14.7608 | 10.5026 | 10.9541 | 11.2678 | 11.1793 | 9.4059 |  | 10.5152 | 8.7604 | 9.9404 | 9.3763 | 10.987 | 12.2321 |  | 12.2491 |  |  | 11.785 | 12.44 | 12.4507 | [6 empty] | 12.5856 |  |  | 11.4456 |  |  | 9.5767 | 10.4841 | 12.2445 | 7.5285 | 9.2149 | 12.6036 | 8.1438 | 9.7549 | 12.2866 | 9.2936 | 10.5175 | 7.7721 | 10.4863 | 8.4671 | 10.4128 | 8.2289 | 9.8415 | 13.1464 | 10.6447 | 10.3759 | 11.8759 | 8.3316 | 9.9512 | 12.794 | 8.2052 | 10.679 | 9.7692 | 10.2031 | 8.4878 | 10.7627 | -0.0094496 | 20.9558 | 0.033556 | 0.047277 | -37.8164 | 3.12 | -1.85 | 0.29 | 0.23386 | 0.34335 | 0.40387 | 0.44904 | 0.34879 | -0.45288 | 0.80227 | 0.39793 | 0.39693 | 0.41431 | 0.40133 | 0.58921 | 0.40301 | 0.39762
42810.4397 | -32 | 18.3782 | 18.512 | 18.5162 | 18.5313 | 17.8733 | 16.5207 | 14.5912 | 16.6669 | 17.1609 | 17.2527 | 17.259 | 16.7987 | 15.8287 | 14.4454 | 14.7794 | 14.8109 | 15.3845 | 13.2667 | 13.3889 | 13.9634 |  |  |  | 16.5502 | 15.8931 | 14.9905 | 10.6911 | 10.3316 | 10.9 | 17.048 | 16.1942 | 15.0107 | 16.7795 | 16.0622 | 15.0705 | 10.7529 | 11.9492 |  | 12.0068 | 10.8691 | 10.6152 | 9.4407 |  | 6.3535 | 6.4042 | 6.0281 | 6.1309 | 6.3502 | 6.6918 | 7.0773 | 4.716 | 6.452 | 4.4389 | 6.6775 | 7.9585 | 41.906 | 46.6164 | 42.641 | 15.0819 |  |  | 0.002847 | -0.085993 | 0.14773 | 0.076226 | 0.048132 | -0.24491 | 0.55319 | 0.30671 | -0.63808 | 0.1362 | -0.475 | 8.8666 | 8.8679 | 2.0082 | 15.6278 | 16.5708 | 17.1484 | 17.4956 | 17.4749 | 16.4548 | 14.8204 | 16.8254 | 17.17 | 17.4826 | 17.5367 | 17.2802 | 16.4868 | 14.7239 | 6.0818 | 8.1955 | 5.4901 | 5.7417 | 5.7337 | 6.5905 | 7.6589 | 15.6564 | 15.3347 | 15.22 | 14.1785 | 14.0809 | 14.0363 |  |  |  | 10.6819 | 9.7751 | 9.4226 | 9.6264 | -0.060326 | -0.14131 | 12.7622 |  |  | 10.5455 |  |  | 16.8581 | 16.0583 | 15.0158 | 16.3703 | 15.6507 | 14.7608 | 10.5074 | 10.9646 | 11.2707 | 11.1809 | 9.3815 |  | 10.511 | 8.7283 | 9.93 | 9.3703 | 10.9789 | 12.2235 |  | 12.2278 |  |  | 11.7795 | 12.4447 | 12.4535 | [6 empty] | 12.584 |  |  | 11.424 |  |  | 9.5797 | 10.4844 | 12.2514 | 7.5437 | 9.2175 | 12.6078 | 8.1357 | 9.7551 | 12.2769 | 9.2909 | 10.5122 | 7.783 | 10.4958 | 8.4694 | 10.4043 | 8.2299 | 9.8538 | 13.1477 | 10.6589 | 10.3657 | 11.8937 | 8.3341 | 9.9528 | 12.7936 | 8.2178 | 10.6884 | 9.7624 | 10.1918 | 8.4847 | 10.7616 | -0.10093 | 20.9565 | 0.033677 | 0.047936 | -37.8384 | 3.1199 | 1.26 | 0.3 | 0.06267 | -0.34169 | 0.44785 | 0.3217 | 0.25576 | -0.57693 | 0.86708 | 0.39847 | 0.39748 | 0.41421 | 0.40374 | 0.59354 | 0.4048 | 0.3973
42810.4397 | -31 | 18.3766 | 18.5081 | 18.5133 | 18.5289 | 17.876 | 16.5104 | 14.5784 | 16.669 | 17.1565 | 17.256 | 17.2599 | 16.7963 | 15.8205 | 14.4465 | 14.7764 | 14.8107 | 15.3879 | 13.2714 | 13.3928 | 13.9672 |  |  |  | 16.5544 | 15.896 | 14.9875 | 10.7064 | 10.3311 | 10.9233 | 17.0513 | 16.2065 | 15.0136 | 16.7818 | 16.0663 | 15.0663 | 10.7528 | 11.9389 |  | 12.0031 | 10.8848 | 10.6169 | 9.3854 |  | 6.3574 | 6.4121 | 6.0363 | 6.1444 | 6.378 | 6.7565 | 7.1323 | 4.7343 | 6.4591 | 4.4632 | 6.6834 | 7.9593 | 41.9217 | 46.5998 | 42.6244 | 15.0829 |  |  | 0.008103 | 0.14925 | 0.01762 | 0.01183 | 0.1605 | 0.17762 | 0.62219 | 0.16872 | -0.37342 | -0.25697 | -0.1849 | 8.8703 | 8.8712 | 2.008 | 15.6268 | 16.5594 | 17.1454 | 17.4859 | 17.4646 | 16.4385 | 14.8069 | 16.8214 | 17.1679 | 17.4745 | 17.5305 | 17.2822 | 16.4822 | 14.727 | 6.062 | 8.1914 | 5.3961 | 5.695 | 5.7126 | 6.5827 | 7.6563 | 15.6604 | 15.3313 | 15.2197 | 14.1778 | 14.0819 | 14.0372 |  |  |  | 10.683 | 9.7731 | 9.4289 | 9.6147 | 0.085141 | -0.066974 | 12.7589 |  |  | 10.5389 |  |  | 16.8582 | 16.0545 | 15.014 | 16.3692 | 15.6545 | 14.7576 | 10.5101 | 10.968 | 11.2707 | 11.1836 | 9.3894 |  | 10.5225 | 8.7079 | 9.9414 | 9.3883 | 10.9843 | 12.2258 |  | 12.2304 |  |  | 11.758 | 12.4546 | 12.448 | [6 empty] | 12.5746 |  |  | 11.4195 |  |  | 9.5678 | 10.4701 | 12.254 | 7.5551 | 9.2167 | 12.6044 | 8.1193 | 9.7548 | 12.2746 | 9.2845 | 10.5019 | 7.7842 | 10.5026 | 8.4603 | 10.3986 | 8.2307 | 9.8586 | 13.1553 | 10.6565 | 10.3663 | 11.9065 | 8.3309 | 9.9527 | 12.7883 | 8.2275 | 10.6835 | 9.7509 | 10.1985 | 8.4868 | 10.7559 | 0.1246 | 20.9551 | 0.033975 | 0.04955 | -37.8155 | 3.12 | 8.69 | 0.37 | 0.10573 | 0.45016 | 0.15467 | 0.12674 | 0.4671 | 0.49138 | 0.91967 | 0.39863 | 0.39842 | 0.41389 | 0.40504 | 0.60367 | 0.40633 | 0.39766
42810.4397 | -30 | 18.374 | 18.505 | 18.5182 | 18.535 | 17.8809 | 16.5131 | 14.5892 | 16.6764 | 17.1623 | 17.2579 | 17.2595 | 16.7997 | 15.8327 | 14.4452 | 14.7838 | 14.8222 | 15.3947 | 13.2735 | 13.4039 | 13.9752 |  |  |  | 16.561 | 15.8986 | 14.9971 | 10.7245 | 10.3411 | 10.9341 | 17.0574 | 16.2082 | 15.0193 | 16.7835 | 16.0734 | 15.0723 | 10.7588 | 11.9187 |  | 12.0057 | 10.8991 | 10.6315 | 9.3656 |  | 6.3524 | 6.4129 | 6.0392 | 6.1366 | 6.4098 | 6.8005 | 7.1987 | 4.6999 | 6.4572 | 4.4888 | 6.6762 | 7.964 | 41.9391 | 46.6114 | 42.6085 | 15.0792 |  |  | 0.077759 | 0.31419 | 0.053764 | 0.025626 | 0.11122 | 0.42141 | 0.54005 | 0.43945 | -0.45029 | -0.64258 | -0.24848 | 8.8697 | 8.8707 | 2.0083 | 15.6355 | 16.5777 | 17.1414 | 17.4886 | 17.4681 | 16.4567 | 14.8089 | 16.8215 | 17.173 | 17.477 | 17.5291 | 17.2824 | 16.49 | 14.7189 | 6.1644 | 8.2008 | 5.4198 | 5.6339 | 5.6794 | 6.5784 | 7.6558 | 15.6522 | 15.3242 | 15.2085 | 14.1736 | 14.0775 | 14.0354 |  |  |  | 10.6777 | 9.7624 | 9.4233 | 9.5576 | 0.13599 | -0.0061858 | 12.7573 |  |  | 10.5456 |  |  | 16.8551 | 16.0565 | 15.0167 | 16.3709 | 15.6563 | 14.7563 | 10.517 | 10.9775 | 11.2785 | 11.1889 | 9.3707 |  | 10.5268 | 8.6885 | 9.9435 | 9.391 | 10.9818 | 12.2184 |  | 12.2367 |  |  | 11.7169 | 12.4628 | 12.4439 | [6 empty] | 12.5709 |  |  | 11.4095 |  |  | 9.5637 | 10.4751 | 12.2587 | 7.5889 | 9.239 | 12.6217 | 8.1173 | 9.7687 | 12.2831 | 9.2914 | 10.5153 | 7.7983 | 10.5314 | 8.4687 | 10.4098 | 8.2237 | 9.8696 | 13.1583 | 10.6571 | 10.3528 | 11.9145 | 8.3268 | 9.9447 | 12.7848 | 8.2398 | 10.6834 | 9.7347 | 10.1961 | 8.4799 | 10.748 | -0.0042494 | 20.9557 | 0.034182 | 0.049506 | -37.8774 | 3.1199 | -7.4 | 0.39 | 0.32754 | 0.65314 | 0.27018 | 0.18653 | 0.38886 | 0.75694 | 0.85689 | 0.39929 | 0.39903 | 0.41373 | 0.39315 | 0.60098 | 0.40708 | 0.39908
42810.4397 | -29 | 18.3702 | 18.5076 | 18.5222 | 18.5349 | 17.8746 | 16.5181 | 14.5812 | 16.6676 | 17.1637 | 17.2526 | 17.2551 | 16.7987 | 15.8289 | 14.4427 | 14.7731 | 14.8038 | 15.3774 | 13.2619 | 13.3942 | 13.9666 |  |  |  | 16.5498 | 15.8879 | 14.9789 | 10.7178 | 10.3281 | 10.861 | 17.0538 | 16.1997 | 15.0088 | 16.7839 | 16.0712 | 15.0712 | 10.7673 | 11.8988 |  | 11.9975 | 10.913 | 10.6404 | 9.3556 |  | 6.3412 | 6.4024 | 6.0481 | 6.1499 | 6.4419 | 6.828 | 7.2197 | 4.6182 | 6.4617 | 4.5135 | 6.6818 | 7.9641 | 41.9769 | 46.6421 | 42.6064 | 15.0764 |  |  | -0.065493 | 0.23862 | 0.064276 | -0.14982 | 0.2019 | -0.15225 | 0.44542 | 0.41776 | 0.049638 | -0.23074 | -0.13383 | 8.8706 | 8.8719 | 2.0082 | 15.6225 | 16.5633 | 17.1435 | 17.4855 | 17.4615 | 16.4476 | 14.8062 | 16.8194 | 17.1614 | 17.4706 | 17.5289 | 17.2764 | 16.4856 | 14.714 | 6.1688 | 8.1856 | 5.3536 | 5.5722 | 5.6271 | 6.5858 | 7.6552 | 15.6533 | 15.3183 | 15.2164 | 14.1784 | 14.0708 | 14.0329 |  |  |  | 10.6835 | 9.7662 | 9.4227 | 9.5253 | 0.023753 | 0.097324 | 12.7596 |  |  | 10.5511 |  |  | 16.8535 | 16.0567 | 15.0185 | 16.3704 | 15.6532 | 14.762 | 10.5184 | 10.9872 | 11.2812 | 11.1933 | 9.3551 |  | 10.518 | 8.719 | 9.9316 | 9.3901 | 10.9794 | 12.2056 |  | 12.221 |  |  | 11.6846 | 12.4522 | 12.45 | [6 empty] | 12.5624 |  |  | 11.3985 |  |  | 9.5609 | 10.4751 | 12.249 | 7.6008 | 9.2412 | 12.6269 | 8.1165 | 9.7663 | 12.2806 | 9.2898 | 10.5173 | 7.8039 | 10.5388 | 8.4695 | 10.4066 | 8.2266 | 9.8832 | 13.1556 | 10.6649 | 10.3498 | 11.931 | 8.3484 | 9.9537 | 12.7907 | 8.2465 | 10.6894 | 9.7327 | 10.1927 | 8.4802 | 10.7549 | -0.061452 | 20.955 | 0.033837 | 0.049745 | -37.8276 | 3.1199 | -6.35 | 0.44 | -0.30056 | 0.56919 | 0.29541 | -0.45101 | 0.52396 | -0.455 | 0.77824 | 0.39944 | 0.39779 | 0.41367 | 0.39353 | 0.60827 | 0.40764 | 0.40016
42810.4397 | -28 | 18.3819 | 18.5113 | 18.5215 | 18.5428 | 17.876 | 16.5201 | 14.5871 | 16.6646 | 17.1683 | 17.2588 | 17.2615 | 16.7954 | 15.8297 | 14.4467 | 14.7856 | 14.8106 | 15.3857 | 13.2715 | 13.389 | 13.9763 |  |  |  | 16.5606 | 15.8894 | 14.9899 | 10.7293 | 10.3333 | 10.8266 | 17.0456 | 16.2029 | 15.0089 | 16.7782 | 16.0602 | 15.0663 | 10.7599 | 11.8612 |  | 11.9963 | 10.9191 | 10.6446 | 9.3657 |  | 6.3285 | 6.4004 | 6.0465 | 6.1524 | 6.4634 | 6.8227 | 7.2165 | 4.559 | 6.4619 | 4.4752 | 6.6835 | 7.9667 | 41.991 | 46.6603 | 42.6072 | 15.0859 |  |  | -0.043149 | 0.036887 | 0.22461 | 0.13077 | 0.027764 | 0.08628 | 0.43426 | 0.11286 | -0.67583 | -1.2957 | -0.17655 | 8.8703 | 8.8714 | 2.0082 | 15.623 | 16.563 | 17.1415 | 17.4849 | 17.4629 | 16.4471 | 14.8069 | 16.8148 | 17.1623 | 17.4678 | 17.5278 | 17.2762 | 16.4848 | 14.7169 | 6.1533 | 8.1671 | 5.3259 | 5.5124 | 5.5627 | 6.5836 | 7.6584 | 15.653 | 15.3172 | 15.2117 | 14.162 | 14.071 | 14.0363 |  |  |  | 10.6781 | 9.7555 | 9.4158 | 9.4983 | -0.37679 | -0.037803 | 12.7677 |  |  | 10.5517 |  |  | 16.8589 | 16.0534 | 15.0167 | 16.3708 | 15.6512 | 14.7631 | 10.5247 | 10.992 | 11.2806 | 11.1986 | 9.3713 |  | 10.5189 | 8.7193 | 9.9263 | 9.3953 | 10.9784 | 12.1947 |  | 12.2201 |  |  | 11.6763 | 12.4621 | 12.4295 | [6 empty] | 12.5727 |  |  | 11.37 |  |  | 9.5661 | 10.4679 | 12.244 | 7.6026 | 9.248 | 12.6227 | 8.1194 | 9.7776 | 12.2728 | 9.2879 | 10.5135 | 7.8153 | 10.5542 | 8.4687 | 10.4044 | 8.229 | 9.8995 | 13.1651 | 10.6638 | 10.3484 | 11.9297 | 8.3412 | 9.9496 | 12.8146 | 8.2679 | 10.6983 | 9.7158 | 10.1951 | 8.4769 | 10.7621 | -0.031021 | 20.9559 | 0.033642 | 0.050266 | -37.9135 | 3.1199 | 2.09 | 8.81 | -0.24395 | 0.22379 | 0.55222 | 0.42135 | 0.1943 | 0.34252 | 0.76842 | 0.39902 | 0.39761 | 0.4135 | 0.39499 | 0.61172 | 0.40712 | 0.40074
42810.4397 | -27 | 18.3793 | 18.5101 | 18.5205 | 18.5307 | 17.8726 | 16.5148 | 14.5816 | 16.6655 | 17.1597 | 17.2545 | 17.2614 | 16.8043 | 15.8278 | 14.4484 | 14.7787 | 14.8054 | 15.3831 | 13.2706 | 13.3895 | 13.9645 |  |  |  | 16.5579 | 15.9011 | 14.9968 | 10.7175 | 10.325 | 10.8558 | 17.0605 | 16.2046 | 15.0108 | 16.7846 | 16.0699 | 15.0619 | 10.7615 | 11.8246 |  | 12.005 | 10.9278 | 10.6629 | 9.383 |  | 6.3281 | 6.4038 | 6.0521 | 6.1627 | 6.4794 | 6.8226 | 7.2104 | 4.4914 | 6.4631 | 4.5219 | 6.6841 | 7.9628 | 42.0258 | 46.6591 | 42.6017 | 15.0956 |  |  | -0.20874 | -0.018313 | 0.12342 | 0.16691 | -0.083948 | 0.15593 | 0.39614 | 0.09446 | -0.45807 | -2.4817 | -0.1692 | 8.8699 | 8.8713 | 2.008 | 15.6211 | 16.5646 | 17.1385 | 17.4795 | 17.457 | 16.4451 | 14.8017 | 16.8168 | 17.1595 | 17.4649 | 17.5272 | 17.2726 | 16.4777 | 14.7168 | 6.1153 | 8.1436 | 5.2876 | 5.468 | 5.4728 | 6.5893 | 7.663 | 15.6521 | 15.3254 | 15.2111 | 14.1693 | 14.0794 | 14.0292 |  |  |  | 10.6827 | 9.7566 | 9.4234 | 9.4858 | -0.37213 | -0.039685 | 12.7655 |  |  | 10.557 |  |  | 16.8576 | 16.0545 | 15.0179 | 16.3704 | 15.6506 | 14.7584 | 10.5386 | 10.9994 | 11.2833 | 11.207 | 9.3847 |  | 10.5221 | 8.7625 | 9.9372 | 9.4058 | 10.9822 | 12.2058 |  | 12.2303 |  |  | 11.6315 | 12.4595 | 12.4388 | [6 empty] | 12.5824 |  |  | 11.3755 |  |  | 9.5779 | 10.475 | 12.2404 | 7.6292 | 9.2642 | 12.6233 | 8.1207 | 9.7751 | 12.2795 | 9.297 | 10.5083 | 7.831 | 10.5577 | 8.4829 | 10.4184 | 8.2471 | 9.9148 | 13.1744 | 10.6695 | 10.3464 | 11.9445 | 8.3537 | 9.9531 | 12.8029 | 8.279 | 10.7154 | 9.7212 | 10.1894 | 8.4655 | 10.7601 | -0.0017456 | 20.9558 | 0.033493 | 0.0507 | -37.8923 | 3.1199 | -4.99 | 15.45 | -0.53659 | -0.15768 | 0.40934 | 0.47603 | -0.33785 | 0.46046 | 0.73392 | 0.39875 | 0.39677 | 0.41333 | 0.39988 | 0.61652 | 0.40669 | 0.40123
42810.4397 | -26 | 18.3757 | 18.5055 | 18.5143 | 18.5286 | 17.8769 | 16.5129 | 14.5815 | 16.6646 | 17.1561 | 17.2541 | 17.2619 | 16.7948 | 15.8278 | 14.4358 | 14.7768 | 14.8117 | 15.3823 | 13.2687 | 13.4017 | 13.9662 |  |  |  | 16.5537 | 15.8951 | 14.9958 | 10.7186 | 10.3123 | 10.8757 | 17.0675 | 16.2093 | 15.0234 | 16.787 | 16.0775 | 15.0738 | 10.7725 | 11.8179 |  | 12.011 | 10.9471 | 10.6864 | 9.3645 |  | 6.3259 | 6.4016 | 6.06 | 6.1782 | 6.4758 | 6.8032 | 7.1889 | 4.4074 | 6.4569 | 4.5292 | 6.68 | 7.9612 | 42.0437 | 46.6682 | 42.6008 | 15.1023 |  |  | 0.096815 | 0.026371 | 0.10568 | 0.12945 | 0.077048 | -0.12466 | 0.20426 | 0.07606 | -0.70677 | -0.23074 | -0.109 | 8.8673 | 8.8686 | 2.0083 | 15.6253 | 16.5654 | 17.1447 | 17.4865 | 17.463 | 16.4432 | 14.8069 | 16.8109 | 17.1627 | 17.4734 | 17.5312 | 17.2716 | 16.4823 | 14.7193 | 6.0653 | 8.1286 | 5.2956 | 5.4849 | 5.4114 | 6.5771 | 7.6644 | 15.6547 | 15.3311 | 15.2159 | 14.173 | 14.076 | 14.0312 |  |  |  | 10.6852 | 9.7581 | 9.4258 | 9.4781 | -0.14299 | 0.031642 | 12.7612 |  |  | 10.5572 |  |  | 16.8575 | 16.0555 | 15.0153 | 16.3658 | 15.6547 | 14.7581 | 10.5523 | 10.9993 | 11.29 | 11.216 | 9.3909 |  | 10.5259 | 8.8255 | 9.9419 | 9.4193 | 10.9869 | 12.2113 |  | 12.233 |  |  | 11.5933 | 12.4541 | 12.4243 | [6 empty] | 12.5604 |  |  | 11.3786 |  |  | 9.5723 | 10.4903 | 12.2452 | 7.6514 | 9.2775 | 12.636 | 8.1256 | 9.7912 | 12.3005 | 9.3041 | 10.5194 | 7.845 | 10.5741 | 8.498 | 10.4122 | 8.2494 | 9.9158 | 13.173 | 10.6582 | 10.3464 | 11.9558 | 8.3512 | 9.9385 | 12.7937 | 8.2833 | 10.7128 | 9.7095 | 10.1845 | 8.4532 | 10.7513 | 0.14116 | 20.9562 | 0.033315 | 0.050621 | -37.8366 | 3.1199 | -0.45 | 15.3 | 0.36544 | 0.18922 | 0.37878 | 0.41923 | 0.32366 | -0.41169 | 0.52699 | 0.3987 | 0.39517 | 0.41311 | 0.40403 | 0.61578 | 0.40756 | 0.40153
42810.4397 | -25 | 18.3748 | 18.5057 | 18.5171 | 18.5262 | 17.8755 | 16.5108 | 14.5793 | 16.6652 | 17.152 | 17.2535 | 17.2581 | 16.7948 | 15.8242 | 14.4356 | 14.7885 | 14.8252 | 15.3885 | 13.2826 | 13.4 | 13.9786 |  |  |  | 16.56 | 15.9017 | 14.9946 | 10.736 | 10.329 | 10.8948 | 17.0549 | 16.2021 | 15.0229 | 16.7851 | 16.0735 | 15.0707 | 10.7643 | 11.8283 |  | 12.0103 | 10.9591 | 10.6875 | 9.3335 |  | 6.3322 | 6.4117 | 6.072 | 6.2051 | 6.4644 | 6.7763 | 7.1523 | 4.2764 | 6.4526 | 4.4965 | 6.6792 | 7.963 | 42.0848 | 46.6676 | 42.615 | 15.1048 |  |  | -0.076665 | -0.049197 | 0.14576 | -0.072282 | 0.073104 | -0.24294 | 0.4014 | 0.11483 | -0.71183 | -0.29221 | -0.16662 | 8.8705 | 8.8716 | 2.0082 | 15.6276 | 16.5687 | 17.1439 | 17.4999 | 17.4637 | 16.4567 | 14.8111 | 16.8101 | 17.1656 | 17.4808 | 17.5401 | 17.2758 | 16.487 | 14.7276 | 6.0342 | 8.0914 | 5.2721 | 5.481 | 5.362 | 6.5803 | 7.6521 | 15.6505 | 15.3272 | 15.2149 | 14.1751 | 14.0789 | 14.0332 |  |  |  | 10.6875 | 9.7577 | 9.426 | 9.475 | -0.13367 | -0.18102 | 12.7663 |  |  | 10.5559 |  |  | 16.8543 | 16.049 | 15.0147 | 16.361 | 15.6506 | 14.7563 | 10.5696 | 10.9997 | 11.2984 | 11.2183 | 9.4057 |  | 10.5346 | 8.9076 | 9.9444 | 9.4099 | 10.9923 | 12.2253 |  | 12.2369 |  |  | 11.5925 | 12.4654 | 12.4291 | [6 empty] | 12.5799 |  |  | 11.3866 |  |  | 9.571 | 10.4905 | 12.2468 | 7.6622 | 9.2906 | 12.634 | 8.1291 | 9.8036 | 12.3125 | 9.3027 | 10.5175 | 7.8564 | 10.5753 | 8.4981 | 10.4206 | 8.2646 | 9.9366 | 13.1994 | 10.6743 | 10.3685 | 11.9749 | 8.3684 | 9.9442 | 12.7978 | 8.3044 | 10.7327 | 9.7194 | 10.1824 | 8.4697 | 10.7516 | -0.20243 | 20.9554 | 0.033556 | 0.0501 | -37.8066 | 3.1199 | 3.52 | 15.59 | -0.32521 | -0.25845 | 0.44486 | -0.31327 | 0.31525 | -0.57469 | 0.73872 | 0.39858 | 0.39298 | 0.41355 | 0.40785 | 0.61696 | 0.40816 | 0.40169
42810.4398 | -24 | 18.3795 | 18.5163 | 18.5185 | 18.5297 | 17.8746 | 16.5171 | 14.5824 | 16.6685 | 17.1586 | 17.2543 | 17.2602 | 16.801 | 15.8281 | 14.4412 | 14.7841 | 14.8122 | 15.3902 | 13.2729 | 13.4017 | 13.9732 |  |  |  | 16.5519 | 15.894 | 14.9958 | 10.7467 | 10.3382 | 10.9048 | 17.0542 | 16.2055 | 15.0151 | 16.7837 | 16.073 | 15.0731 | 10.7603 | 11.8563 |  | 12.0114 | 10.9662 | 10.6981 | 9.3255 |  | 6.3311 | 6.4124 | 6.0585 | 6.1949 | 6.4516 | 6.765 | 7.1218 | 4.2756 | 6.4473 | 4.3823 | 6.6768 | 7.9608 | 42.1064 | 46.6525 | 42.6317 | 15.1081 |  |  | -0.087177 | -0.016341 | 0.080048 | 0.088054 | 0.01922 | -0.2022 | 0.46645 | 0.053064 | -0.93932 | -0.55342 | -0.37605 | 8.868 | 8.8692 | 2.0077 | 15.6324 | 16.5773 | 17.1464 | 17.4962 | 17.4728 | 16.451 | 14.815 | 16.8272 | 17.1719 | 17.4779 | 17.5308 | 17.2833 | 16.4895 | 14.7233 | 6.0018 | 8.1059 | 5.2586 | 5.4973 | 5.3599 | 6.5843 | 7.6553 | 15.6526 | 15.3195 | 15.2095 | 14.1745 | 14.0791 | 14.0246 |  |  |  | 10.6833 | 9.7585 | 9.4289 | 9.4391 | 0.073187 | 0.06326 | 12.7669 |  |  | 10.5628 |  |  | 16.8569 | 16.0484 | 15.0161 | 16.3693 | 15.6494 | 14.7569 | 10.5981 | 11.0115 | 11.3156 | 11.2349 | 9.4114 |  | 10.526 | 8.983 | 9.9423 | 9.4228 | 10.9934 | 12.2284 |  | 12.2283 |  |  | 11.6043 | 12.4583 | 12.4337 | [6 empty] | 12.575 |  |  | 11.3929 |  |  | 9.5729 | 10.4869 | 12.2524 | 7.6751 | 9.296 | 12.6322 | 8.1289 | 9.7938 | 12.3092 | 9.3015 | 10.5133 | 7.8734 | 10.5858 | 8.4944 | 10.4184 | 8.2722 | 9.9484 | 13.1971 | 10.6823 | 10.3612 | 11.9676 | 8.3835 | 9.9396 | 12.799 | 8.3176 | 10.7283 | 9.7239 | 10.1809 | 8.4625 | 10.7648 | -0.16623 | 20.9575 | 0.033677 | 0.050273 | -37.8742 | 3.1199 | 14 | 15.05 | -0.34679 | -0.14895 | 0.32967 | 0.34576 | 0.16164 | -0.52428 | 0.79631 | 0.39814 | 0.39081 | 0.41323 | 0.4119 | 0.61883 | 0.40825 | 0.40255
42810.4398 | -23 | 18.3766 | 18.5152 | 18.5269 | 18.5336 | 17.8753 | 16.5184 | 14.5832 | 16.6626 | 17.1632 | 17.2538 | 17.2643 | 16.7988 | 15.8266 | 14.4459 | 14.782 | 14.806 | 15.3877 | 13.2647 | 13.3971 | 13.9652 |  |  |  | 16.5547 | 15.8883 | 14.987 | 10.7468 | 10.3404 | 10.9123 | 17.0609 | 16.2085 | 15.0132 | 16.7753 | 16.068 | 15.0666 | 10.7563 | 11.8775 |  | 12.0103 | 10.9762 | 10.7082 | 9.3248 |  | 6.3341 | 6.4064 | 6.0477 | 6.1832 | 6.4405 | 6.7377 | 7.0909 | 4.3967 | 6.4366 | 4.3161 | 6.6768 | 7.9687 | 42.1136 | 46.643 | 42.6441 | 15.1058 |  |  | 0.031759 | -0.055109 | 0.2095 | -0.03417 | 0.017248 | 0.2867 | 0.47697 | 0.022836 | -0.33548 | 0.69385 | -0.14317 | 8.8695 | 8.8706 | 2.008 | 15.6282 | 16.5656 | 17.1319 | 17.4884 | 17.4595 | 16.4421 | 14.7992 | 16.8131 | 17.1604 | 17.4657 | 17.5283 | 17.2678 | 16.475 | 14.7109 | 5.9988 | 8.1172 | 5.2728 | 5.5334 | 5.3888 | 6.5855 | 7.6618 | 15.6507 | 15.3236 | 15.2029 | 14.1658 | 14.0724 | 14.0299 |  |  |  | 10.6799 | 9.7547 | 9.4209 | 9.4463 | -0.10632 | 0.18973 | 12.7722 |  |  | 10.5651 |  |  | 16.8639 | 16.0532 | 15.021 | 16.3696 | 15.6513 | 14.7526 | 10.6289 | 11.0214 | 11.3235 | 11.2517 | 9.4198 |  | 10.5272 | 9.0573 | 9.9479 | 9.4337 | 10.9948 | 12.2355 |  | 12.2232 |  |  | 11.612 | 12.446 | 12.4268 | [6 empty] | 12.5823 |  |  | 11.3919 |  |  | 9.5811 | 10.4914 | 12.2592 | 7.6959 | 9.3056 | 12.6492 | 8.142 | 9.8106 | 12.3151 | 9.3091 | 10.5157 | 7.8899 | 10.5947 | 8.5104 | 10.4284 | 8.2771 | 9.9546 | 13.207 | 10.6939 | 10.3589 | 11.9636 | 8.3905 | 9.9416 | 12.8059 | 8.3259 | 10.7265 | 9.7134 | 10.1727 | 8.4647 | 10.7828 | -0.042384 | 20.9557 | 0.033877 | 0.050454 | -37.9312 | 3.1199 | 24.12 | 13.64 | 0.20932 | -0.27354 | 0.53333 | -0.21539 | 0.15312 | 0.62427 | 0.8052 | 0.39794 | 0.38893 | 0.41297 | 0.41238 | 0.61801 | 0.40813 | 0.40224
42810.4398 | -22 | 18.382 | 18.5134 | 18.5163 | 18.5287 | 17.8794 | 16.5112 | 14.5801 | 16.6601 | 17.1654 | 17.2564 | 17.2566 | 16.797 | 15.8254 | 14.448 | 14.7813 | 14.8054 | 15.3911 | 13.2653 | 13.3952 | 13.9659 |  |  |  | 16.5544 | 15.8951 | 14.99 | 10.7573 | 10.3561 | 10.9464 | 17.0603 | 16.2098 | 15.019 | 16.7827 | 16.0757 | 15.0626 | 10.7598 | 11.9108 |  | 12.0121 | 10.9844 | 10.7162 | 9.3111 |  | 6.3208 | 6.4011 | 6.0385 | 6.176 | 6.4283 | 6.7207 | 7.1388 | 4.5529 | 6.4309 | 4.3446 | 6.681 | 7.9715 | 42.1298 | 46.6261 | 42.6472 | 15.101 |  |  | 0.1277 | 0.013887 | 0.09122 | 0.00197 | -0.060292 | 0.30313 | 0.29232 | 0.037948 | -0.4715 | -0.27144 | -0.14774 | 8.8709 | 8.8723 | 2.0082 | 15.6161 | 16.5575 | 17.1293 | 17.4842 | 17.4572 | 16.4333 | 14.7914 | 16.8119 | 17.1518 | 17.467 | 17.5242 | 17.264 | 16.4735 | 14.711 | 6.0126 | 8.1338 | 5.3156 | 5.5889 | 5.4688 | 6.5855 | 7.659 | 15.6557 | 15.3227 | 15.2083 | 14.1678 | 14.0758 | 14.0336 |  |  |  | 10.682 | 9.7617 | 9.4347 | 9.4466 | -0.076939 | -0.045896 | 12.7725 |  |  | 10.5653 |  |  | 16.8644 | 16.055 | 15.0214 | 16.3659 | 15.6585 | 14.7547 | 10.6567 | 11.0322 | 11.3289 | 11.2599 | 9.4012 |  | 10.5317 | 9.1763 | 9.9499 | 9.4501 | 10.9918 | 12.2289 |  | 12.2172 |  |  | 11.632 | 12.4413 | 12.4186 | [6 empty] | 12.5912 |  |  | 11.397 |  |  | 9.5869 | 10.4993 | 12.2751 | 7.7094 | 9.3129 | 12.6524 | 8.1401 | 9.8172 | 12.3106 | 9.3143 | 10.5155 | 7.9019 | 10.6056 | 8.5166 | 10.4264 | 8.2792 | 9.957 | 13.2107 | 10.6899 | 10.3615 | 11.9711 | 8.3903 | 9.9372 | 12.8002 | 8.3347 | 10.722 | 9.7094 | 10.1619 | 8.4601 | 10.7826 | 0.024833 | 20.9554 | 0.033946 | 0.050143 | -37.8941 | 3.1198 | 6.34 | 13.47 | 0.41975 | 0.13731 | 0.35192 | 0.051717 | -0.28627 | 0.64189 | 0.63034 | 0.39861 | 0.38569 | 0.41242 | 0.41085 | 0.61294 | 0.40863 | 0.4023
42810.4398 | -21 | 18.3843 | 18.516 | 18.523 | 18.521 | 17.879 | 16.5151 | 14.5776 | 16.6641 | 17.1574 | 17.2595 | 17.2559 | 16.7918 | 15.8243 | 14.449 | 14.7833 | 14.8131 | 15.3877 | 13.2675 | 13.3945 | 13.9659 |  |  |  | 16.5501 | 15.8894 | 14.9847 | 10.769 | 10.3608 | 10.9798 | 17.067 | 16.2111 | 15.0208 | 16.7854 | 16.0745 | 15.0739 | 10.7657 | 11.9396 |  | 12.0083 | 10.9936 | 10.7294 | 9.2824 |  | 6.3148 | 6.3908 | 6.042 | 6.169 | 6.4481 | 6.7848 | 7.1879 | 4.628 | 6.43 | 4.3784 | 6.6714 | 7.965 | 42.1347 | 46.6007 | 42.6563 | 15.0879 |  |  | 0.056731 | -0.042625 | 0.21081 | 0.24051 | 0.13422 | -0.26396 | 0.53151 | 0.051092 | -0.49077 | -0.60461 | -0.059916 | 8.8696 | 8.8704 | 2.0083 | 15.6196 | 16.5574 | 17.1375 | 17.4808 | 17.456 | 16.4425 | 14.8021 | 16.8119 | 17.1588 | 17.466 | 17.5287 | 17.2636 | 16.4761 | 14.7133 | 6.0232 | 8.1591 | 5.391 | 5.5789 | 5.5572 | 6.5823 | 7.6534 | 15.6528 | 15.3163 | 15.21 | 14.1649 | 14.0752 | 14.0326 |  |  |  | 10.6794 | 9.768 | 9.4421 | 9.4208 | 0.0030878 | -0.0099498 | 12.7772 |  |  | 10.5699 |  |  | 16.8629 | 16.0585 | 15.0089 | 16.3648 | 15.6587 | 14.7549 | 10.685 | 11.0479 | 11.3375 | 11.2576 | 9.3985 |  | 10.5324 | 9.3157 | 9.945 | 9.4694 | 10.9967 | 12.2188 |  | 12.221 |  |  | 11.6495 | 12.4383 | 12.4204 | [6 empty] | 12.5993 |  |  | 11.4026 |  |  | 9.5854 | 10.5061 | 12.2854 | 7.7229 | 9.3249 | 12.6572 | 8.149 | 9.8235 | 12.3119 | 9.324 | 10.5209 | 7.912 | 10.6158 | 8.5253 | 10.4305 | 8.2805 | 9.9576 | 13.2163 | 10.6879 | 10.3725 | 11.9894 | 8.3935 | 9.9362 | 12.7919 | 8.3457 | 10.7345 | 9.7114 | 10.1645 | 8.4596 | 10.7798 | -0.036028 | 20.9542 | 0.033929 | 0.050165 | -37.8914 | 3.1198 | 17.17 | 12.99 | 0.27979 | -0.24056 | 0.53498 | 0.57142 | 0.42717 | -0.59906 | 0.85006 | 0.39871 | 0.38166 | 0.41204 | 0.4093 | 0.6039 | 0.40962 | 0.40293
42810.4398 | -20 | 18.3905 | 18.5177 | 18.5234 | 18.5334 | 17.8825 | 16.5253 | 14.5879 | 16.662 | 17.1579 | 17.2616 | 17.2657 | 16.8008 | 15.8336 | 14.456 | 14.7831 | 14.814 | 15.3956 | 13.2776 | 13.3964 | 13.9665 |  |  |  | 16.5529 | 15.8887 | 14.989 | 10.7813 | 10.3546 | 11.009 | 17.0543 | 16.2065 | 15.0277 | 16.7862 | 16.073 | 15.0708 | 10.7632 | 11.9456 |  | 12.0083 | 10.999 | 10.7432 | 9.2538 |  | 6.3186 | 6.3976 | 6.0366 | 6.1689 | 6.5006 | 6.8758 | 7.1962 | 4.586 | 6.4314 | 4.4561 | 6.6706 | 7.9709 | 42.1581 | 46.6166 | 42.6615 | 15.0853 |  |  | 0.1185 | -0.092565 | 0.096476 | 0.11039 | -0.034664 | 0.27684 | 0.46908 | 0.089204 | 0.038741 | -0.55488 | -0.27133 | 8.8679 | 8.8689 | 2.0078 | 15.6264 | 16.5626 | 17.137 | 17.4912 | 17.4591 | 16.4433 | 14.8062 | 16.8145 | 17.1636 | 17.4706 | 17.5304 | 17.2712 | 16.4789 | 14.7195 | 6.0471 | 8.1772 | 5.4464 | 5.5719 | 5.5584 | 6.5768 | 7.6607 | 15.6539 | 15.3192 | 15.2091 | 14.1723 | 14.0759 | 14.0294 |  |  |  | 10.6914 | 9.7884 | 9.4435 | 9.4026 | -0.07775 | 0.08001 | 12.7852 |  |  | 10.5764 |  |  | 16.8583 | 16.053 | 15.0124 | 16.3637 | 15.658 | 14.7521 | 10.7131 | 11.0609 | 11.3432 | 11.2587 | 9.4115 |  | 10.5354 | 9.4277 | 9.9523 | 9.4896 | 10.996 | 12.2088 |  | 12.2293 |  |  | 11.6774 | 12.4412 | 12.4261 | [6 empty] | 12.6133 |  |  | 11.4104 |  |  | 9.5904 | 10.5088 | 12.2794 | 7.735 | 9.3317 | 12.6536 | 8.1566 | 9.8331 | 12.3077 | 9.3323 | 10.5296 | 7.9279 | 10.6248 | 8.5388 | 10.4367 | 8.2892 | 9.9638 | 13.2221 | 10.6872 | 10.3811 | 12.009 | 8.4001 | 9.9469 | 12.7965 | 8.3513 | 10.745 | 9.7196 | 10.1828 | 8.4757 | 10.779 | 0.077028 | 20.9548 | 0.033786 | 0.049557 | -37.8399 | 3.1198 | 15.46 | 13.64 | 0.40439 | -0.3545 | 0.36191 | 0.38714 | -0.21712 | 0.6136 | 0.79871 | 0.39844 | 0.37879 | 0.41146 | 0.40601 | 0.5986 | 0.41033 | 0.40383
42810.4398 | -19 | 18.393 | 18.5205 | 18.5329 | 18.5356 | 17.8799 | 16.5132 | 14.5906 | 16.6711 | 17.1645 | 17.2619 | 17.2677 | 16.8028 | 15.8324 | 14.4558 | 14.7772 | 14.8138 | 15.3928 | 13.2719 | 13.397 | 13.9699 |  |  |  | 16.5531 | 15.8933 | 14.9921 | 10.7902 | 10.3424 | 11.0258 | 17.0495 | 16.2088 | 15.0195 | 16.7803 | 16.0742 | 15.0704 | 10.7578 | 11.9363 |  | 12.0045 | 11.0014 | 10.7519 | 9.2457 |  | 6.3107 | 6.3943 | 6.0435 | 6.1793 | 6.5084 | 6.8736 | 7.2392 | 4.5122 | 6.4316 | 4.5304 | 6.6776 | 7.9709 | 42.1885 | 46.6195 | 42.6648 | 15.0774 |  |  | 0.19078 | -0.062997 | 0.12933 | 0.005914 | -0.00838 | 0.3235 | 0.54925 | -0.13159 | -0.63049 | -0.29221 | -0.21371 | 8.8699 | 8.8709 | 2.008 | 15.6256 | 16.565 | 17.1374 | 17.4933 | 17.469 | 16.4384 | 14.8061 | 16.8185 | 17.169 | 17.4744 | 17.5356 | 17.2786 | 16.476 | 14.7206 | 6.078 | 8.1946 | 5.5029 | 5.5661 | 5.5772 | 6.5859 | 7.6606 | 15.6515 | 15.3128 | 15.2037 | 14.16 | 14.0717 | 14.0225 |  |  |  | 10.6857 | 9.7908 | 9.438 | 9.3878 | -0.26252 | 0.01621 | 12.7946 |  |  | 10.5763 |  |  | 16.8586 | 16.0551 | 15.0173 | 16.3657 | 15.6569 | 14.7614 | 10.7343 | 11.0711 | 11.3493 | 11.2612 | 9.4014 |  | 10.5305 | 9.4872 | 9.946 | 9.5002 | 10.9901 | 12.1859 |  | 12.2232 |  |  | 11.6922 | 12.4414 | 12.4054 | [6 empty] | 12.5979 |  |  | 11.4025 |  |  | 9.5954 | 10.5016 | 12.2732 | 7.7401 | 9.3393 | 12.6501 | 8.1609 | 9.8326 | 12.2995 | 9.3257 | 10.5245 | 7.9323 | 10.6242 | 8.5461 | 10.4321 | 8.3063 | 9.9637 | 13.2312 | 10.6925 | 10.3835 | 12.0148 | 8.407 | 9.9509 | 12.7951 | 8.3568 | 10.7513 | 9.7217 | 10.1876 | 8.4802 | 10.778 | 0.14502 | 20.955 | 0.033458 | 0.04926 | -37.8097 | 3.1199 | 12.51 | 13.75 | 0.51313 | -0.29245 | 0.41903 | 0.089605 | -0.10675 | 0.66329 | 0.86427 | 0.39856 | 0.37693 | 0.41097 | 0.40362 | 0.5923 | 0.41038 | 0.40406
42810.4398 | -18 | 18.391 | 18.52 | 18.5304 | 18.5321 | 17.8697 | 16.5134 | 14.5819 | 16.6734 | 17.1604 | 17.2567 | 17.2595 | 16.8026 | 15.8295 | 14.452 | 14.7794 | 14.8173 | 15.3888 | 13.2656 | 13.399 | 13.969 |  |  |  | 16.5513 | 15.8889 | 14.9894 | 10.8024 | 10.33 | 11.0345 | 17.0548 | 16.2077 | 15.0193 | 16.7857 | 16.0763 | 15.0754 | 10.7665 | 11.9547 |  | 12.0112 | 11.015 | 10.7669 | 9.2451 |  | 6.3172 | 6.3854 | 6.0557 | 6.1884 | 6.5124 | 6.8673 | 7.264 | 4.3895 | 6.43 | 4.5665 | 6.6716 | 7.9707 | 42.2081 | 46.6324 | 42.6662 | 15.0568 |  |  | 0.049503 | -0.037369 | 0.08136 | 0.16231 | -0.06226 | -0.015572 | 0.51048 | -0.029736 | -0.61317 | -0.43257 | -0.29438 | 8.8663 | 8.8673 | 2.0082 | 15.6229 | 16.556 | 17.1314 | 17.4838 | 17.4577 | 16.4341 | 14.7966 | 16.8125 | 17.1569 | 17.4695 | 17.5241 | 17.2722 | 16.48 | 14.7116 | 6.0491 | 8.1768 | 5.5157 | 5.5483 | 5.5634 | 6.585 | 7.6597 | 15.6571 | 15.309 | 15.2017 | 14.1555 | 14.0757 | 14.022 |  |  |  | 10.6861 | 9.8013 | 9.4288 | 9.3701 | -0.093755 | -0.077514 | 12.7996 |  |  | 10.5765 |  |  | 16.858 | 16.0589 | 15.0147 | 16.3677 | 15.6533 | 14.7632 | 10.7571 | 11.0832 | 11.3501 | 11.2519 | 9.4448 |  | 10.5359 | 9.5647 | 9.9622 | 9.5239 | 10.9943 | 12.1641 |  | 12.2195 |  |  | 11.6975 | 12.4427 | 12.378 | [6 empty] | 12.5856 |  |  | 11.3899 |  |  | 9.598 | 10.4984 | 12.2819 | 7.7353 | 9.3385 | 12.6483 | 8.1662 | 9.8323 | 12.2955 | 9.3188 | 10.5162 | 7.9412 | 10.6249 | 8.555 | 10.4359 | 8.31 | 9.9557 | 13.2343 | 10.689 | 10.3842 | 12.0178 | 8.4035 | 9.9465 | 12.7945 | 8.3581 | 10.7476 | 9.7172 | 10.1868 | 8.488 | 10.7776 | -0.17258 | 20.9548 | 0.033194 | 0.049267 | -37.8477 | 3.1198 | -9.7 | 11.25 | 0.26139 | -0.22524 | 0.33235 | 0.46941 | -0.29098 | -0.14552 | 0.8332 | 0.39753 | 0.37531 | 0.41045 | 0.40673 | 0.59077 | 0.41068 | 0.40456
42810.4398 | -17 | 18.3835 | 18.5124 | 18.5227 | 18.5285 | 17.8771 | 16.5107 | 14.5755 | 16.6712 | 17.1625 | 17.2534 | 17.259 | 16.7915 | 15.8259 | 14.4506 | 14.7841 | 14.8177 | 15.3949 | 13.2705 | 13.3994 | 13.9697 |  |  |  | 16.5497 | 15.889 | 14.9926 | 10.8038 | 10.3232 | 11.0481 | 17.0575 | 16.2064 | 15.0208 | 16.7831 | 16.0774 | 15.0735 | 10.7665 | 11.9756 |  | 12.0089 | 11.0175 | 10.774 | 9.2337 |  | 6.3088 | 6.396 | 6.064 | 6.1988 | 6.5111 | 6.8463 | 7.3275 | 4.3955 | 6.4246 | 4.5182 | 6.6645 | 7.9766 | 42.242 | 46.6342 | 42.672 | 15.0524 |  |  | 0.056731 | 0.082883 | 0.09516 | 0.019058 | 0.096104 | -0.1562 | 0.56568 | 0.10235 | -0.52521 | -1.1845 | -0.25305 | 8.8704 | 8.8715 | 2.0079 | 15.6297 | 16.5672 | 17.1396 | 17.48 | 17.4635 | 16.4462 | 14.8078 | 16.8061 | 17.158 | 17.4753 | 17.5301 | 17.2749 | 16.4776 | 14.7093 | 6.0039 | 8.146 | 5.4672 | 5.5339 | 5.5405 | 6.5938 | 7.6645 | 15.6513 | 15.3182 | 15.2037 | 14.1642 | 14.0718 | 14.0217 |  |  |  | 10.6841 | 9.8107 | 9.4322 | 9.3718 | -0.063568 | -0.039121 | 12.799 |  |  | 10.5795 |  |  | 16.8574 | 16.0608 | 15.0152 | 16.3674 | 15.6526 | 14.7571 | 10.7726 | 11.0988 | 11.3499 | 11.2428 | 9.5179 |  | 10.5375 | 9.6411 | 9.9588 | 9.5579 | 10.9989 | 12.1677 |  | 12.2193 |  |  | 11.7252 | 12.4559 | 12.3958 | [6 empty] | 12.5976 |  |  | 11.3835 |  |  | 9.6082 | 10.5089 | 12.2869 | 7.7495 | 9.3521 | 12.6494 | 8.1669 | 9.8406 | 12.2938 | 9.3182 | 10.5225 | 7.9587 | 10.6284 | 8.5684 | 10.4451 | 8.3164 | 9.9508 | 13.2303 | 10.6918 | 10.3867 | 12.0295 | 8.4055 | 9.9503 | 12.7916 | 8.3591 | 10.749 | 9.7178 | 10.1977 | 8.4971 | 10.7763 | -0.047584 | 20.9556 | 0.032397 | 0.049817 | -37.887 | 3.1199 | 14.59 | 9.9 | 0.27983 | 0.33545 | 0.35944 | 0.16085 | 0.3615 | -0.46087 | 0.87706 | 0.39556 | 0.37307 | 0.40966 | 0.41278 | 0.59672 | 0.411 | 0.40445
42810.4398 | -16 | 18.3827 | 18.5176 | 18.527 | 18.5299 | 17.8782 | 16.5079 | 14.584 | 16.6702 | 17.1649 | 17.2565 | 17.2621 | 16.7929 | 15.8266 | 14.4513 | 14.7865 | 14.8163 | 15.3944 | 13.2765 | 13.4033 | 13.9748 |  |  |  | 16.5542 | 15.8936 | 14.9939 | 10.8161 | 10.3217 | 11.039 | 17.067 | 16.2102 | 15.0221 | 16.7869 | 16.082 | 15.0766 | 10.7719 | 11.9987 |  | 12.014 | 11.0237 | 10.7884 | 9.2419 |  | 6.3133 | 6.4086 | 6.0729 | 6.2177 | 6.5253 | 6.8599 | 7.3736 | 4.5141 | 6.4188 | 4.4627 | 6.6632 | 7.967 | 42.2633 | 46.6169 | 42.6644 | 15.0355 |  |  | -0.081921 | -0.11951 | 0.04522 | 0.13077 | -0.10432 | 0.14805 | 0.5164 | -0.074416 | -0.34637 | -0.13612 | -0.55289 | 8.8698 | 8.8714 | 2.0079 | 15.6215 | 16.557 | 17.1359 | 17.4819 | 17.4487 | 16.4279 | 14.7914 | 16.8021 | 17.1586 | 17.4569 | 17.5271 | 17.2632 | 16.4721 | 14.7061 | 6.0162 | 8.1157 | 5.4276 | 5.5163 | 5.4926 | 6.5963 | 7.6572 | 15.6575 | 15.3266 | 15.2114 | 14.1704 | 14.0746 | 14.0301 |  |  |  | 10.6925 | 9.8221 | 9.4399 | 9.3729 | -0.15048 | -0.088053 | 12.7864 |  |  | 10.5814 |  |  | 16.8572 | 16.0639 | 15.0147 | 16.3595 | 15.6546 | 14.7549 | 10.7949 | 11.1126 | 11.3542 | 11.2455 | 9.5615 |  | 10.5304 | 9.6721 | 9.9538 | 9.5822 | 10.9802 | 12.1756 |  | 12.2156 |  |  | 11.7323 | 12.4293 | 12.4145 | [6 empty] | 12.5815 |  |  | 11.3831 |  |  | 9.6082 | 10.5075 | 12.293 | 7.7649 | 9.3544 | 12.6518 | 8.1689 | 9.8507 | 12.3037 | 9.3114 | 10.5164 | 7.9754 | 10.619 | 8.5737 | 10.4369 | 8.3354 | 9.9653 | 13.2491 | 10.6927 | 10.3994 | 12.0477 | 8.4174 | 9.9627 | 12.7947 | 8.3689 | 10.755 | 9.7155 | 10.2103 | 8.4997 | 10.7753 | 0.007114 | 20.9532 | 0.032707 | 0.049528 | -37.9327 | 3.1199 | 17.99 | 9.81 | -0.33625 | -0.40281 | 0.24778 | 0.42136 | -0.37664 | 0.4487 | 0.838 | 0.39411 | 0.37205 | 0.40837 | 0.4117 | 0.60028 | 0.41095 | 0.40469
42810.4399 | -15 | 18.3896 | 18.5152 | 18.5204 | 18.5284 | 17.8756 | 16.5089 | 14.5829 | 16.664 | 17.1551 | 17.2536 | 17.2636 | 16.7945 | 15.8237 | 14.4433 | 14.7862 | 14.8085 | 15.3892 | 13.2656 | 13.3949 | 13.9584 |  |  |  | 16.5466 | 15.8844 | 14.9848 | 10.8176 | 10.3161 | 10.9978 | 17.0747 | 16.2128 | 15.017 | 16.7899 | 16.0774 | 15.0744 | 10.7674 | 11.9866 |  | 12.0204 | 11.0277 | 10.801 | 9.2681 |  | 6.3197 | 6.4235 | 6.1003 | 6.2352 | 6.5441 | 6.873 | 7.4436 | 4.5339 | 6.4164 | 4.5119 | 6.6736 | 7.9725 | 42.2868 | 46.616 | 42.6665 | 15.0343 |  |  | -0.15814 | 0.014543 | 0.087276 | 0.051914 | 0.00608 | 0.055396 | 0.44542 | 0.002464 | -0.63866 | -0.25697 | -0.23537 | 8.8682 | 8.8695 | 2.0081 | 15.6251 | 16.5646 | 17.1422 | 17.4863 | 17.4638 | 16.4286 | 14.8059 | 16.8132 | 17.1673 | 17.4655 | 17.5293 | 17.275 | 16.4773 | 14.7145 | 6.0707 | 8.1289 | 5.4347 | 5.5044 | 5.4621 | 6.5987 | 7.6627 | 15.6574 | 15.3209 | 15.2083 | 14.1677 | 14.0771 | 14.0202 |  |  |  | 10.6944 | 9.8297 | 9.4232 | 9.361 | -0.041687 | 0.022232 | 12.7929 |  |  | 10.5883 |  |  | 16.8625 | 16.0593 | 15.0112 | 16.3648 | 15.655 | 14.7573 | 10.8177 | 11.1351 | 11.3557 | 11.2538 | 9.6104 |  | 10.5298 | 9.606 | 9.9618 | 9.612 | 10.9964 | 12.1949 |  | 12.2195 |  |  | 11.7331 | 12.4331 | 12.4193 | [6 empty] | 12.5904 |  |  | 11.3671 |  |  | 9.6156 | 10.5091 | 12.2926 | 7.7799 | 9.3615 | 12.6538 | 8.1639 | 9.8494 | 12.2985 | 9.3066 | 10.5218 | 7.9806 | 10.617 | 8.5757 | 10.4385 | 8.3498 | 9.9907 | 13.266 | 10.7033 | 10.4159 | 12.0538 | 8.4242 | 9.969 | 12.7989 | 8.3802 | 10.7726 | 9.7288 | 10.2228 | 8.5128 | 10.7877 | -0.034873 | 20.9552 | 0.032844 | 0.049166 | -37.955 | 3.1198 | 13.71 | 8.82 | -0.46716 | 0.14052 | 0.34424 | 0.2655 | 0.090932 | 0.27448 | 0.77831 | 0.39273 | 0.37415 | 0.40807 | 0.40593 | 0.60013 | 0.41008 | 0.40509
42810.4399 | -14 | 18.3834 | 18.512 | 18.5208 | 18.5271 | 17.8735 | 16.5016 | 14.5805 | 16.6638 | 17.1584 | 17.249 | 17.2569 | 16.7879 | 15.8172 | 14.4423 | 14.7853 | 14.814 | 15.3968 | 13.2636 | 13.397 | 13.9692 |  |  |  | 16.5523 | 15.8883 | 14.9915 | 10.8213 | 10.3063 | 10.9638 | 17.0701 | 16.2161 | 15.0233 | 16.7901 | 16.0787 | 15.0768 | 10.7783 | 11.9846 |  | 12.0159 | 11.0382 | 10.8099 | 9.3065 |  | 6.3152 | 6.413 | 6.1058 | 6.2346 | 6.5395 | 6.8779 | 7.4909 | 4.5511 | 6.4046 | 4.5887 | 6.6616 | 7.9653 | 42.2925 | 46.6023 | 42.6615 | 15.0338 |  |  | 0.056075 | -0.048537 | 0.15299 | 0.10251 | 0.036304 | 0.17499 | 0.58539 | 0.00838 | 0.55618 | -0.46299 | -0.2157 | 8.8685 | 8.8698 | 2.0083 | 15.6225 | 16.5662 | 17.1445 | 17.4917 | 17.4573 | 16.4348 | 14.7963 | 16.8096 | 17.167 | 17.4679 | 17.5255 | 17.2669 | 16.4789 | 14.707 | 6.1008 | 8.1315 | 5.4589 | 5.4917 | 5.4389 | 6.6008 | 7.6474 | 15.6606 | 15.3282 | 15.2157 | 14.179 | 14.0855 | 14.0291 |  |  |  | 10.693 | 9.8523 | 9.4353 | 9.3742 | -0.11098 | -0.099909 | 12.7964 |  |  | 10.5882 |  |  | 16.8581 | 16.0511 | 15.0106 | 16.3684 | 15.6473 | 14.7544 | 10.8154 | 11.1391 | 11.3576 | 11.2547 | 9.634 |  | 10.5385 | 9.4866 | 9.9641 | 9.6325 | 10.9954 | 12.229 |  | 12.2179 |  |  | 11.7481 | 12.4608 | 12.4317 | [6 empty] | 12.6033 |  |  | 11.3909 |  |  | 9.6147 | 10.5031 | 12.2756 | 7.7852 | 9.3718 | 12.6478 | 8.1589 | 9.8439 | 12.2961 | 9.302 | 10.5012 | 7.983 | 10.6081 | 8.5671 | 10.4288 | 8.3362 | 9.9725 | 13.2485 | 10.6941 | 10.3955 | 12.0435 | 8.4048 | 9.9577 | 12.7834 | 8.3661 | 10.7723 | 9.7128 | 10.2056 | 8.5032 | 10.7711 | 0.033693 | 20.9549 | 0.033263 | 0.049065 | -37.872 | 3.1198 | 8.65 | 6.29 | 0.27816 | -0.25671 | 0.45576 | 0.37307 | 0.2222 | 0.48784 | 0.89226 | 0.39236 | 0.37754 | 0.40747 | 0.40284 | 0.59566 | 0.40937 | 0.40468
42810.4399 | -13 | 18.392 | 18.5147 | 18.5203 | 18.5404 | 17.8764 | 16.5056 | 14.5896 | 16.6651 | 17.1629 | 17.2565 | 17.2566 | 16.7929 | 15.8222 | 14.4516 | 14.7797 | 14.8131 | 15.3869 | 13.266 | 13.397 | 13.9717 |  |  |  | 16.5516 | 15.8861 | 14.9902 | 10.8222 | 10.3082 | 10.9485 | 17.0661 | 16.2168 | 15.0273 | 16.7881 | 16.0686 | 15.0749 | 10.7719 | 11.9604 |  | 12.0102 | 11.0275 | 10.8197 | 9.3262 |  | 6.3138 | 6.4221 | 6.1178 | 6.2451 | 6.536 | 6.9094 | 7.5626 | 4.5559 | 6.4047 | 4.6388 | 6.6507 | 7.9671 | 42.3089 | 46.5868 | 42.6649 | 15.037 |  |  | 0.13624 | -0.029481 | 0.043248 | 0.10448 | 0.095444 | -0.00046 | 0.59459 | -0.074416 | -0.5869 | 0.73203 | -0.384 | 8.8696 | 8.8709 | 2.0082 | 15.6172 | 16.5616 | 17.1323 | 17.4844 | 17.4515 | 16.4297 | 14.7918 | 16.8061 | 17.1524 | 17.4546 | 17.5198 | 17.2639 | 16.4675 | 14.702 | 6.1335 | 8.1831 | 5.5199 | 5.5103 | 5.4119 | 6.602 | 7.6514 | 15.6562 | 15.3183 | 15.2135 | 14.1727 | 14.0768 | 14.0244 |  |  |  | 10.6933 | 9.8645 | 9.4235 | 9.3671 | 0.0118 | -0.056435 | 12.8035 |  |  | 10.5942 |  |  | 16.8587 | 16.0498 | 15.0107 | 16.3682 | 15.6465 | 14.7537 | 10.8173 | 11.1408 | 11.3592 | 11.2647 | 9.6502 |  | 10.5374 | 9.3927 | 9.9664 | 9.6372 | 10.999 | 12.2609 |  | 12.2142 |  |  | 11.757 | 12.471 | 12.4543 | [6 empty] | 12.6118 |  |  | 11.401 |  |  | 9.6257 | 10.5103 | 12.2848 | 7.7954 | 9.3888 | 12.6564 | 8.1769 | 9.8509 | 12.2975 | 9.3154 | 10.5152 | 8.0117 | 10.6019 | 8.5734 | 10.4389 | 8.3424 | 9.9777 | 13.2478 | 10.6968 | 10.3952 | 12.0587 | 8.4004 | 9.9616 | 12.7847 | 8.3726 | 10.7769 | 9.7293 | 10.2125 | 8.5091 | 10.7749 | 0.054108 | 20.9541 | 0.032965 | 0.048956 | -37.8453 | 3.1198 | 1.94 | 6.26 | 0.43357 | -0.20007 | 0.24232 | 0.37665 | 0.3603 | -0.025013 | 0.89929 | 0.39188 | 0.38022 | 0.40746 | 0.39933 | 0.58934 | 0.40861 | 0.40488
42810.4399 | -12 | 18.3924 | 18.5144 | 18.5259 | 18.5314 | 17.8778 | 16.506 | 14.5878 | 16.6644 | 17.1614 | 17.2486 | 17.2584 | 16.7989 | 15.8249 | 14.4539 | 14.7851 | 14.8181 | 15.387 | 13.2709 | 13.3974 | 13.9678 |  |  |  | 16.5578 | 15.8998 | 14.9867 | 10.8327 | 10.3027 | 10.9609 | 17.0738 | 16.2126 | 15.0344 | 16.7912 | 16.0855 | 15.0821 | 10.7764 | 11.9695 |  | 12.0167 | 11.0445 | 10.8219 | 9.3611 |  | 6.3061 | 6.4254 | 6.1172 | 6.2347 | 6.5298 | 6.9351 | 7.6484 | 4.4839 | 6.4085 | 4.7077 | 6.6541 | 7.9665 | 42.3189 | 46.5756 | 42.6815 | 15.053 |  |  | 0.20787 | -0.1655 | 0.073476 | -0.19845 | 0.01922 | 0.27882 | 0.66753 | 0.16017 | -0.64508 | -0.45733 | -0.42652 | 8.8697 | 8.8707 | 2.0081 | 15.6241 | 16.5671 | 17.1368 | 17.4773 | 17.4538 | 16.4373 | 14.7956 | 16.806 | 17.1544 | 17.4643 | 17.5229 | 17.2623 | 16.4741 | 14.7091 | 6.1628 | 8.2676 | 5.6007 | 5.5772 | 5.433 | 6.6048 | 7.6474 | 15.6507 | 15.3128 | 15.2043 | 14.1615 | 14.0768 | 14.0181 |  |  |  | 10.693 | 9.874 | 9.4203 | 9.3702 | 0.1206 | 0.044064 | 12.8032 |  |  | 10.5869 |  |  | 16.8588 | 16.0517 | 15.0121 | 16.3679 | 15.6501 | 14.7575 | 10.8249 | 11.152 | 11.3682 | 11.2813 | 9.6451 |  | 10.5335 | 9.3447 | 9.9706 | 9.6672 | 10.9891 | 12.2863 |  | 12.2149 |  |  | 11.7633 | 12.4788 | 12.4641 | [6 empty] | 12.6113 |  |  | 11.3929 |  |  | 9.6305 | 10.5165 | 12.3039 | 7.8083 | 9.3974 | 12.6659 | 8.1858 | 9.8563 | 12.3044 | 9.3086 | 10.5135 | 8.0114 | 10.6078 | 8.5703 | 10.4367 | 8.3632 | 10.0053 | 13.2733 | 10.7111 | 10.4196 | 12.0716 | 8.4235 | 9.99 | 12.8042 | 8.3906 | 10.7969 | 9.7344 | 10.2207 | 8.5294 | 10.799 | -0.013302 | 20.954 | 0.032907 | 0.048783 | -37.8366 | 3.1199 | 1.4 | 6.16 | 0.53555 | -0.47405 | 0.31586 | -0.51909 | 0.16169 | 0.61584 | 0.9529 | 0.39189 | 0.3817 | 0.4063 | 0.39641 | 0.57991 | 0.40779 | 0.40479
42810.4399 | -11 | 18.3898 | 18.5008 | 18.5181 | 18.5212 | 17.8664 | 16.5008 | 14.5783 | 16.6583 | 17.1478 | 17.2461 | 17.2569 | 16.7908 | 15.8161 | 14.4411 | 14.7814 | 14.8153 | 15.3806 | 13.2549 | 13.3884 | 13.9557 |  |  |  | 16.5462 | 15.8815 | 14.9858 | 10.8252 | 10.3013 | 10.9454 | 17.0655 | 16.2135 | 15.0304 | 16.7915 | 16.08 | 15.0787 | 10.7779 | 11.9818 |  | 12.0168 | 11.0562 | 10.8374 | 9.4059 |  | 6.2979 | 6.4234 | 6.0988 | 6.2185 | 6.5341 | 6.9312 | 7.6924 | 4.4395 | 6.4084 | 4.7412 | 6.6466 | 7.9739 | 42.3328 | 46.5732 | 42.6993 | 15.0624 |  |  | 0.071843 | -0.34555 | -0.05532 | 0.024314 | 0.009364 | 0.061308 | 0.36854 | -0.017248 | -0.5797 | -0.3455 | -0.2 | 8.8692 | 8.8707 | 2.008 | 15.6325 | 16.5691 | 17.1424 | 17.4876 | 17.4534 | 16.437 | 14.8037 | 16.8176 | 17.1625 | 17.4685 | 17.5331 | 17.2674 | 16.4809 | 14.7117 | 6.2795 | 8.2973 | 5.783 | 5.6546 | 5.5085 | 6.61 | 7.6495 | 15.6474 | 15.3198 | 15.2041 | 14.1608 | 14.0815 | 14.0205 |  |  |  | 10.69 | 9.8885 | 9.4251 | 9.3755 | 0.16861 | 0.20516 | 12.8001 |  |  | 10.5793 |  |  | 16.8663 | 16.0585 | 15.0123 | 16.3691 | 15.6498 | 14.7591 | 10.8187 | 11.1589 | 11.3781 | 11.2881 | 9.6382 |  | 10.5461 | 9.3107 | 9.968 | 9.6838 | 10.9984 | 12.3165 |  | 12.2212 |  |  | 11.777 | 12.4804 | 12.4773 | [6 empty] | 12.6117 |  |  | 11.403 |  |  | 9.6353 | 10.5345 | 12.3122 | 7.8198 | 9.4067 | 12.6722 | 8.2039 | 9.8701 | 12.3225 | 9.3088 | 10.5142 | 8.0211 | 10.6112 | 8.5722 | 10.4529 | 8.3725 | 10.0092 | 13.2742 | 10.705 | 10.4162 | 12.0761 | 8.4276 | 9.9999 | 12.8049 | 8.4038 | 10.8147 | 9.7241 | 10.2143 | 8.5348 | 10.8019 | 0.11189 | 20.955 | 0.03277 | 0.048406 | -37.8513 | 3.1198 | 4.98 | 6.47 | 0.31484 | -0.68497 | -0.27407 | 0.1817 | 0.11286 | 0.28878 | 0.70803 | 0.3925 | 0.38255 | 0.40614 | 0.38404 | 0.5599 | 0.40659 | 0.40454
42810.4399 | -10 | 18.3914 | 18.5167 | 18.5217 | 18.5323 | 17.8752 | 16.5075 | 14.582 | 16.6666 | 17.1534 | 17.2526 | 17.2547 | 16.7947 | 15.8196 | 14.4424 | 14.7861 | 14.8233 | 15.3925 | 13.2713 | 13.3973 | 13.9637 |  |  |  | 16.5494 | 15.8933 | 14.9818 | 10.8309 | 10.3204 | 10.9611 | 17.0613 | 16.2097 | 15.0196 | 16.7794 | 16.066 | 15.0647 | 10.7696 | 11.9843 |  | 12.0082 | 11.0534 | 10.8329 | 9.4182 |  | 6.2898 | 6.4221 | 6.0876 | 6.2118 | 6.5155 | 6.9056 | 7.6891 | 4.4884 | 6.3997 | 4.6804 | 6.6492 | 7.9704 | 42.3319 | 46.5758 | 42.7069 | 15.0699 |  |  | 0.12902 | -0.005169 | 0.064932 | -0.076882 | -0.13914 | 0.24267 | 0.28378 | -0.053392 | -0.97201 | -0.27354 | -0.36889 | 8.8699 | 8.8708 | 2.0078 | 15.6281 | 16.5614 | 17.1271 | 17.481 | 17.4465 | 16.4374 | 14.8016 | 16.8055 | 17.1591 | 17.4658 | 17.5196 | 17.2714 | 16.4682 | 14.7037 | 6.454 | 8.3211 | 5.8934 | 5.7495 | 5.592 | 6.6119 | 7.6491 | 15.6535 | 15.3209 | 15.2139 | 14.1679 | 14.0805 | 14.0229 |  |  |  | 10.6994 | 9.8996 | 9.4259 | 9.3683 | 0.17672 | 0.13026 | 12.7968 |  |  | 10.5829 |  |  | 16.8628 | 16.0604 | 15.0176 | 16.365 | 15.647 | 14.7601 | 10.8166 | 11.179 | 11.3849 | 11.2952 | 9.6148 |  | 10.552 | 9.2651 | 9.9712 | 9.6956 | 11.0083 | 12.3372 |  | 12.2246 |  |  | 11.7816 | 12.4709 | 12.4938 | [6 empty] | 12.6114 |  |  | 11.4124 |  |  | 9.6397 | 10.5442 | 12.3197 | 7.8301 | 9.4165 | 12.6776 | 8.2079 | 9.8725 | 12.3314 | 9.3084 | 10.5159 | 8.0251 | 10.6119 | 8.5822 | 10.4639 | 8.3678 | 10.02 | 13.2783 | 10.7064 | 10.424 | 12.076 | 8.422 | 9.9955 | 12.7932 | 8.4045 | 10.821 | 9.7107 | 10.202 | 8.5319 | 10.7952 | 0.23708 | 20.9544 | 0.033005 | 0.047545 | -37.7875 | 3.1199 | 9.5 | 8.19 | 0.42192 | -0.083776 | 0.29692 | -0.32309 | -0.43503 | 0.57451 | 0.62127 | 0.39334 | 0.38392 | 0.40614 | 0.36487 | 0.54759 | 0.40598 | 0.40505
42810.4399 | -9 | 18.3916 | 18.5214 | 18.5295 | 18.5393 | 17.8853 | 16.5126 | 14.5876 | 16.6689 | 17.1609 | 17.2532 | 17.2634 | 16.7973 | 15.8234 | 14.4492 | 14.7872 | 14.8219 | 15.3917 | 13.2631 | 13.3896 | 13.961 |  |  |  | 16.5541 | 15.8884 | 14.9863 | 10.8442 | 10.3382 | 11.0015 | 17.0666 | 16.2133 | 15.0192 | 16.7849 | 16.0725 | 15.0687 | 10.773 | 12.0016 |  | 12.0134 | 11.0704 | 10.8431 | 9.438 |  | 6.2781 | 6.416 | 6.0828 | 6.1935 | 6.5016 | 6.894 | 7.6742 | 4.4889 | 6.4066 | 4.6485 | 6.6465 | 7.9756 | 42.3492 | 46.588 | 42.729 | 15.0799 |  |  | 0.068559 | -0.005169 | 0.039964 | 0.049942 | 0.13093 | 0.060652 | 0.16484 | 0.084604 | -0.4534 | 0.065705 | -0.46248 | 8.8689 | 8.8703 | 2.0081 | 15.6438 | 16.573 | 17.1452 | 17.4919 | 17.464 | 16.4438 | 14.8 | 16.8209 | 17.1651 | 17.4701 | 17.5336 | 17.28 | 16.4843 | 14.7151 | 6.5771 | 8.3374 | 5.9382 | 5.7671 | 5.6581 | 6.6224 | 7.6472 | 15.6582 | 15.3157 | 15.2156 | 14.1674 | 14.0741 | 14.0207 |  |  |  | 10.6976 | 9.9119 | 9.4226 | 9.3825 | 0.079265 | 0.18672 | 12.7971 |  |  | 10.5838 |  |  | 16.857 | 16.0567 | 15.011 | 16.371 | 15.6584 | 14.7534 | 10.8253 | 11.1983 | 11.3945 | 11.3103 | 9.6022 |  | 10.554 | 9.2309 | 9.9786 | 9.7001 | 11.0115 | 12.3414 |  | 12.2336 |  |  | 11.7815 | 12.4863 | 12.5038 | [6 empty] | 12.6195 |  |  | 11.4242 |  |  | 9.6413 | 10.5402 | 12.3193 | 7.817 | 9.4144 | 12.6712 | 8.2032 | 9.8628 | 12.3317 | 9.3151 | 10.5215 | 8.0154 | 10.6113 | 8.5898 | 10.462 | 8.377 | 10.0413 | 13.2932 | 10.7167 | 10.4409 | 12.0923 | 8.4227 | 9.9981 | 12.8019 | 8.4168 | 10.8377 | 9.714 | 10.204 | 8.5381 | 10.8016 | 0.050834 | 20.9546 | 0.03312 | 0.047834 | -37.7999 | 3.1199 | 1.5 | 8.47 | 0.30759 | -0.083775 | 0.23294 | 0.2604 | 0.42199 | 0.28721 | 0.47348 | 0.39376 | 0.38512 | 0.40612 | 0.35241 | 0.54238 | 0.40554 | 0.40459
42810.4399 | -8 | 18.3907 | 18.5167 | 18.5263 | 18.5355 | 17.8783 | 16.5197 | 14.5847 | 16.6657 | 17.156 | 17.2544 | 17.2618 | 16.7963 | 15.8241 | 14.4438 | 14.79 | 14.8189 | 15.3856 | 13.2639 | 13.3869 | 13.9614 |  |  |  | 16.5426 | 15.8866 | 14.989 | 10.8531 | 10.3507 | 11.0344 | 17.0649 | 16.2067 | 15.0136 | 16.7796 | 16.0719 | 15.0658 | 10.7755 | 12.0159 |  | 12.0132 | 11.0761 | 10.8514 | 9.4441 |  | 6.2729 | 6.4072 | 6.0748 | 6.1891 | 6.4904 | 6.872 | 7.6357 | 4.4853 | 6.398 | 4.646 | 6.6518 | 7.9775 | 42.356 | 46.6059 | 42.741 | 15.0725 |  |  | 0.17764 | 0.011259 | 0.070848 | 0.046654 | 0.094788 | -0.14962 | 0.093868 | -0.054048 | -0.19322 | -1.7476 | -0.45791 | 8.8682 | 8.8695 | 2.0081 | 15.6301 | 16.5619 | 17.1414 | 17.4927 | 17.4577 | 16.444 | 14.8023 | 16.814 | 17.1691 | 17.4705 | 17.5274 | 17.2642 | 16.4734 | 14.7133 | 6.5988 | 8.3143 | 5.9393 | 5.7819 | 5.6911 | 6.6286 | 7.6605 | 15.6593 | 15.3212 | 15.2096 | 14.1621 | 14.0735 | 14.0257 |  |  |  | 10.7005 | 9.9109 | 9.4265 | 9.3922 | -0.052222 | -0.06641 | 12.7989 |  |  | 10.5859 |  |  | 16.8562 | 16.0584 | 15.0137 | 16.3679 | 15.656 | 14.7583 | 10.825 | 11.2149 | 11.4014 | 11.3265 | 9.5729 |  | 10.5549 | 9.2329 | 9.9749 | 9.7128 | 11.0122 | 12.3368 |  | 12.2232 |  |  | 11.7909 | 12.487 | 12.508 | [6 empty] | 12.6073 |  |  | 11.4223 |  |  | 9.6504 | 10.5514 | 12.3155 | 7.8034 | 9.4167 | 12.6741 | 8.211 | 9.8759 | 12.3343 | 9.3108 | 10.5179 | 8.0061 | 10.6107 | 8.5982 | 10.4735 | 8.3803 | 10.0554 | 13.3071 | 10.7165 | 10.4463 | 12.0964 | 8.4411 | 10.0088 | 12.7967 | 8.4241 | 10.8479 | 9.7126 | 10.2039 | 8.5452 | 10.8097 | 0.098021 | 20.955 | 0.033252 | 0.048508 | -37.7959 | 3.1198 | 5.83 | 8.51 | 0.49515 | 0.12364 | 0.31015 | 0.25168 | 0.35904 | -0.45109 | 0.35729 | 0.3946 | 0.38494 | 0.40579 | 0.35071 | 0.54381 | 0.40545 | 0.40442
42810.44 | -7 | 18.3955 | 18.5205 | 18.533 | 18.5404 | 17.8804 | 16.5194 | 14.5887 | 16.6688 | 17.1565 | 17.2589 | 17.2697 | 16.8034 | 15.8214 | 14.4453 | 14.7937 | 14.823 | 15.3883 | 13.2663 | 13.3909 | 13.9637 |  |  |  | 16.5447 | 15.8884 | 14.9852 | 10.8679 | 10.3663 | 11.0693 | 17.0604 | 16.2066 | 15.0121 | 16.7811 | 16.0702 | 15.0676 | 10.7725 | 12.0169 |  | 12.012 | 11.0825 | 10.8573 | 9.4363 |  | 6.2721 | 6.4023 | 6.0642 | 6.1729 | 6.4742 | 6.8555 | 7.5893 | 4.5011 | 6.3915 | 4.656 | 6.6537 | 7.9708 | 42.3706 | 46.6138 | 42.7361 | 15.0664 |  |  | 0.060015 | 0.10917 | -0.025092 | -0.08411 | -0.019548 | -0.19825 | 0.2772 | 0.29488 | -0.25219 | -0.89203 | -0.20199 | 8.8708 | 8.872 | 2.0081 | 15.6389 | 16.5619 | 17.1366 | 17.4872 | 17.4602 | 16.4466 | 14.8069 | 16.8172 | 17.1599 | 17.473 | 17.5328 | 17.2727 | 16.4786 | 14.7065 | 6.5525 | 8.2324 | 5.8638 | 5.7834 | 5.654 | 6.6297 | 7.6536 | 15.6586 | 15.3174 | 15.2073 | 14.165 | 14.0687 | 14.0198 |  |  |  | 10.6963 | 9.9177 | 9.43 | 9.3883 | -0.13164 | -0.055118 | 12.7973 |  |  | 10.5865 |  |  | 16.8602 | 16.0559 | 15.0046 | 16.3625 | 15.6509 | 14.755 | 10.8205 | 11.2198 | 11.4093 | 11.3462 | 9.5651 |  | 10.5552 | 9.2792 | 9.9769 | 9.7241 | 11.0129 | 12.3517 |  | 12.2241 |  |  | 11.8095 | 12.4782 | 12.5157 | [6 empty] | 12.6062 |  |  | 11.4206 |  |  | 9.6654 | 10.561 | 12.3275 | 7.7957 | 9.4349 | 12.6783 | 8.223 | 9.8825 | 12.3356 | 9.3177 | 10.5249 | 7.9973 | 10.6051 | 8.5963 | 10.4835 | 8.3861 | 10.0698 | 13.3215 | 10.7276 | 10.4466 | 12.1132 | 8.4518 | 10.0107 | 12.7965 | 8.4316 | 10.8597 | 9.7155 | 10.2088 | 8.5464 | 10.8246 | 0.17352 | 20.9545 | 0.033217 | 0.049839 | -37.7442 | 3.1198 | 6.29 | 7.81 | 0.28782 | 0.38499 | -0.18457 | -0.33793 | -0.16304 | -0.51923 | 0.61397 | 0.39483 | 0.38372 | 0.4055 | 0.35599 | 0.55139 | 0.40557 | 0.40439
42810.44 | -6 | 18.4021 | 18.5199 | 18.5268 | 18.5368 | 17.8841 | 16.5118 | 14.5841 | 16.6708 | 17.1652 | 17.2559 | 17.2607 | 16.8011 | 15.8295 | 14.4463 | 14.7939 | 14.8224 | 15.391 | 13.2667 | 13.3924 | 13.9661 |  |  |  | 16.5511 | 15.889 | 14.9853 | 10.8815 | 10.3828 | 11.1037 | 17.068 | 16.2122 | 15.0245 | 16.7893 | 16.0806 | 15.0703 | 10.7795 | 12.0277 |  | 12.0118 | 11.085 | 10.8764 | 9.414 |  | 6.274 | 6.3885 | 6.062 | 6.1738 | 6.4639 | 6.8468 | 7.5413 | 4.5118 | 6.3897 | 4.6624 | 6.6571 | 7.969 | 42.3707 | 46.6188 | 42.7512 | 15.0595 |  |  | 0.064615 | -0.13068 | 0.17204 | -0.12091 | -0.13454 | 0.14214 | 0.41388 | 0.091832 | -0.85934 | -0.50034 | -0.33492 | 8.869 | 8.8704 | 2.0079 | 15.631 | 16.5611 | 17.1328 | 17.4852 | 17.4572 | 16.4397 | 14.8014 | 16.8136 | 17.1587 | 17.4664 | 17.5282 | 17.2693 | 16.4728 | 14.7022 | 6.4811 | 8.2087 | 5.7672 | 5.7646 | 5.6423 | 6.6318 | 7.6545 | 15.6611 | 15.3207 | 15.222 | 14.1731 | 14.075 | 14.0272 |  |  |  | 10.7012 | 9.9401 | 9.4497 | 9.4024 | -0.098415 | -0.16371 | 12.7885 |  |  | 10.5824 |  |  | 16.8499 | 16.0485 | 15.0047 | 16.3498 | 15.6378 | 14.7422 | 10.8124 | 11.2163 | 11.4138 | 11.3507 | 9.5625 |  | 10.5472 | 9.3294 | 9.977 | 9.7112 | 11.0138 | 12.3691 |  | 12.2101 |  |  | 11.8263 | 12.4689 | 12.5168 | [6 empty] | 12.618 |  |  | 11.4198 |  |  | 9.672 | 10.5663 | 12.3567 | 7.795 | 9.4448 | 12.6753 | 8.2288 | 9.8852 | 12.3441 | 9.3333 | 10.5285 | 7.9979 | 10.61 | 8.6076 | 10.494 | 8.3897 | 10.0774 | 13.3334 | 10.7363 | 10.4541 | 12.129 | 8.458 | 10.0182 | 12.7932 | 8.4407 | 10.8688 | 9.7247 | 10.2192 | 8.551 | 10.8321 | 0.083961 | 20.9549 | 0.033883 | 0.049897 | -37.7788 | 3.1198 | 1.94 | 6.12 | 0.29867 | -0.4212 | 0.48329 | -0.40515 | -0.42774 | 0.43964 | 0.75021 | 0.39464 | 0.38233 | 0.40589 | 0.36416 | 0.56223 | 0.40642 | 0.40416
42810.44 | -5 | 18.3909 | 18.5217 | 18.5274 | 18.5335 | 17.8793 | 16.5153 | 14.5795 | 16.6659 | 17.1588 | 17.2633 | 17.2609 | 16.8013 | 15.8226 | 14.4506 | 14.7908 | 14.8196 | 15.3868 | 13.2709 | 13.3903 | 13.9638 |  |  |  | 16.5526 | 15.8929 | 14.9855 | 10.8877 | 10.4006 | 11.1121 | 17.0787 | 16.2181 | 15.0229 | 16.7823 | 16.0755 | 15.0666 | 10.782 | 12.029 |  | 12.0158 | 11.1054 | 10.8885 | 9.4139 |  | 6.2746 | 6.3985 | 6.0596 | 6.1638 | 6.4558 | 6.8252 | 7.4997 | 4.4939 | 6.3901 | 4.6749 | 6.6558 | 7.9728 | 42.3834 | 46.6175 | 42.7717 | 15.0618 |  |  | 0.068559 | 0.078943 | 0.044564 | -0.090026 | -0.18383 | -0.095084 | 0.46054 | 0.2916 | -0.10351 | -0.60733 | -0.16543 | 8.8683 | 8.8696 | 2.0081 | 15.6294 | 16.5699 | 17.1284 | 17.4853 | 17.4603 | 16.4407 | 14.8002 | 16.8078 | 17.1584 | 17.4674 | 17.5262 | 17.2687 | 16.4723 | 14.7096 | 6.3879 | 8.2199 | 5.7022 | 5.7413 | 5.6653 | 6.6308 | 7.6586 | 15.6624 | 15.3213 | 15.2128 | 14.1671 | 14.0759 | 14.0286 |  |  |  | 10.6923 | 9.9532 | 9.467 | 9.4115 | -0.19384 | -0.052107 | 12.801 |  |  | 10.5852 |  |  | 16.8572 | 16.0492 | 15.0087 | 16.365 | 15.6424 | 14.7473 | 10.8128 | 11.2223 | 11.4288 | 11.3749 | 9.5495 |  | 10.5593 | 9.3971 | 9.9793 | 9.7153 | 11.017 | 12.3878 |  | 12.2277 |  |  | 11.8364 | 12.4843 | 12.522 | [6 empty] | 12.606 |  |  | 11.4193 |  |  | 9.6754 | 10.5722 | 12.3812 | 7.7936 | 9.444 | 12.6749 | 8.2259 | 9.8867 | 12.3466 | 9.332 | 10.5353 | 7.9971 | 10.6101 | 8.6092 | 10.5019 | 8.3782 | 10.0832 | 13.3385 | 10.7349 | 10.4617 | 12.1403 | 8.4589 | 10.0206 | 12.7923 | 8.4406 | 10.8754 | 9.7214 | 10.221 | 8.553 | 10.824 | 0.11824 | 20.9542 | 0.034285 | 0.050042 | -37.7758 | 3.1198 | 6.22 | 6.17 | 0.30765 | 0.32738 | 0.24597 | -0.34961 | -0.49996 | -0.35957 | 0.79134 | 0.3954 | 0.38053 | 0.40588 | 0.37441 | 0.56993 | 0.40651 | 0.40362
42810.44 | -4 | 18.3966 | 18.5219 | 18.5259 | 18.5369 | 17.8788 | 16.5132 | 14.5886 | 16.6656 | 17.1582 | 17.247 | 17.2615 | 16.7965 | 15.8316 | 14.4523 | 14.7828 | 14.8132 | 15.3837 | 13.2597 | 13.3883 | 13.9604 |  |  |  | 16.5497 | 15.8869 | 14.9802 | 10.8892 | 10.4023 | 11.0952 | 17.0679 | 16.2138 | 15.0152 | 16.7794 | 16.064 | 15.0657 | 10.78 | 12.0427 |  | 12.005 | 11.108 | 10.8976 | 9.4316 |  | 6.2725 | 6.3966 | 6.0531 | 6.1562 | 6.4489 | 6.8089 | 7.4736 | 4.5025 | 6.3767 | 4.6309 | 6.6479 | 7.9762 | 42.397 | 46.6024 | 42.7833 | 15.0615 |  |  | 0.30906 | 0.11837 | 0.12933 | -0.14719 | -0.14112 | 0.027796 | 0.43886 | 0.18252 | 0.37793 | -0.45124 | -0.28127 | 8.8684 | 8.8699 | 2.0083 | 15.637 | 16.569 | 17.1405 | 17.4887 | 17.4611 | 16.4441 | 14.8021 | 16.8147 | 17.1569 | 17.4656 | 17.534 | 17.2674 | 16.4756 | 14.7159 | 6.2512 | 8.2216 | 5.6471 | 5.7464 | 5.6934 | 6.6332 | 7.6476 | 15.666 | 15.3224 | 15.2105 | 14.1691 | 14.0687 | 14.0222 |  |  |  | 10.6905 | 9.9672 | 9.4935 | 9.4074 | -0.11908 | -0.068292 | 12.8034 |  |  | 10.5877 |  |  | 16.854 | 16.0515 | 15.0071 | 16.3613 | 15.6443 | 14.7453 | 10.8087 | 11.2281 | 11.4413 | 11.3921 | 9.5488 |  | 10.5557 | 9.4435 | 9.9846 | 9.709 | 11.0072 | 12.4133 |  | 12.2255 |  |  | 11.8388 | 12.4844 | 12.5277 | [6 empty] | 12.5971 |  |  | 11.4266 |  |  | 9.6774 | 10.5736 | 12.392 | 7.801 | 9.4344 | 12.6843 | 8.2261 | 9.8898 | 12.3457 | 9.3284 | 10.5363 | 7.9801 | 10.6085 | 8.5945 | 10.5109 | 8.3813 | 10.0887 | 13.3448 | 10.74 | 10.467 | 12.1386 | 8.4676 | 10.0266 | 12.7919 | 8.4432 | 10.8887 | 9.7206 | 10.2296 | 8.5554 | 10.835 | 0.00904 | 20.9537 | 0.034503 | 0.049673 | -37.7362 | 3.1198 | 13.74 | 6.17 | 0.65319 | 0.40088 | 0.41903 | -0.44703 | -0.43803 | 0.1944 | 0.77246 | 0.3953 | 0.37941 | 0.40574 | 0.38988 | 0.57479 | 0.40595 | 0.40367
42810.44 | -3 | 18.4013 | 18.5248 | 18.5265 | 18.5359 | 17.8827 | 16.5139 | 14.5932 | 16.6685 | 17.1573 | 17.2532 | 17.263 | 16.8019 | 15.831 | 14.4479 | 14.7909 | 14.8176 | 15.3869 | 13.2661 | 13.3929 | 13.9678 |  |  |  | 16.5495 | 15.8906 | 14.9805 | 10.9076 | 10.4289 | 11.1096 | 17.066 | 16.2117 | 15.0194 | 16.7843 | 16.0693 | 15.0653 | 10.7792 | 12.0629 |  | 12.0058 | 11.1179 | 10.9008 | 9.4548 |  | 6.2848 | 6.3976 | 6.0461 | 6.1447 | 6.4342 | 6.7958 | 7.4688 | 4.5254 | 6.381 | 4.5661 | 6.6597 | 7.9708 | 42.392 | 46.5909 | 42.7975 | 15.0484 |  |  | 0.090903 | 0.042143 | 0.065592 | -0.3187 | 0.004108 | 0.024512 | 0.44346 | 0.22391 | -0.39191 | 0.41691 | -0.36631 | 8.8711 | 8.8723 | 2.008 | 15.6351 | 16.562 | 17.1374 | 17.4808 | 17.4576 | 16.4423 | 14.7973 | 16.8187 | 17.1569 | 17.4686 | 17.5207 | 17.2704 | 16.4722 | 14.7031 | 6.1727 | 8.183 | 5.5535 | 5.7475 | 5.7626 | 6.634 | 7.654 | 15.6682 | 15.3293 | 15.2108 | 14.1712 | 14.074 | 14.0226 |  |  |  | 10.6986 | 9.985 | 9.4943 | 9.4019 | 0.076632 | -0.061328 | 12.8125 |  |  | 10.5827 |  |  | 16.8584 | 16.046 | 15.011 | 16.3575 | 15.6458 | 14.7478 | 10.8072 | 11.2178 | 11.4388 | 11.399 | 9.5423 |  | 10.5592 | 9.4923 | 9.9817 | 9.7013 | 11.0141 | 12.4286 |  | 12.2301 |  |  | 11.8498 | 12.469 | 12.5338 | [6 empty] | 12.5992 |  |  | 11.439 |  |  | 9.6858 | 10.5792 | 12.3943 | 7.812 | 9.4325 | 12.6955 | 8.2271 | 9.8921 | 12.3587 | 9.3357 | 10.5367 | 7.9713 | 10.6266 | 8.5958 | 10.5117 | 8.3769 | 10.096 | 13.3519 | 10.7442 | 10.4664 | 12.1422 | 8.4742 | 10.0361 | 12.7871 | 8.4496 | 10.9002 | 9.7272 | 10.2349 | 8.5522 | 10.8409 | 0.056612 | 20.955 | 0.03444 | 0.049094 | -37.751 | 3.1198 | 8.54 | 17.83 | 0.35425 | 0.2392 | 0.29841 | -0.65779 | 0.074734 | 0.18255 | 0.77648 | 0.39559 | 0.37796 | 0.40617 | 0.39869 | 0.58591 | 0.40528 | 0.40409
42810.44 | -2 | 18.3964 | 18.5199 | 18.5221 | 18.5311 | 17.8763 | 16.5085 | 14.5798 | 16.6617 | 17.1546 | 17.2548 | 17.2583 | 16.7962 | 15.8287 | 14.4403 | 14.7944 | 14.8204 | 15.3908 | 13.2789 | 13.3961 | 13.9694 |  |  |  | 16.552 | 15.8912 | 14.982 | 10.9158 | 10.4535 | 11.1321 | 17.0648 | 16.2051 | 15.0122 | 16.7868 | 16.0691 | 15.0668 | 10.7772 | 12.0889 |  | 12.0069 | 11.1252 | 10.8969 | 9.4629 |  | 6.2959 | 6.3976 | 6.0316 | 6.1367 | 6.4255 | 6.7819 | 7.4473 | 4.516 | 6.3836 | 4.5225 | 6.6696 | 7.9728 | 42.3968 | 46.582 | 42.8179 | 15.0453 |  |  | 0.10404 | 0.078943 | -0.016548 | -0.22145 | 0.098076 | 0.015968 | 0.51245 | 0.38491 | -0.65598 | -0.22864 | -0.35379 | 8.8683 | 8.8692 | 2.0079 | 15.6377 | 16.57 | 17.1378 | 17.4863 | 17.4597 | 16.4356 | 14.8063 | 16.8114 | 17.1506 | 17.4686 | 17.5236 | 17.2696 | 16.4708 | 14.7072 | 6.1533 | 8.1554 | 5.4424 | 5.7405 | 5.8211 | 6.6294 | 7.644 | 15.6665 | 15.3198 | 15.2123 | 14.1696 | 14.0751 | 14.0266 |  |  |  | 10.704 | 9.996 | 9.4992 | 9.3921 | -0.03885 | -0.065657 | 12.8094 |  |  | 10.5928 |  |  | 16.8603 | 16.0531 | 15.0115 | 16.3555 | 15.6459 | 14.7512 | 10.8073 | 11.2372 | 11.4471 | 11.4202 | 9.5602 |  | 10.5601 | 9.5401 | 9.9842 | 9.6717 | 11.0143 | 12.4333 |  | 12.2222 |  |  | 11.8547 | 12.4571 | 12.5244 | [6 empty] | 12.5969 |  |  | 11.4494 |  |  | 9.6934 | 10.583 | 12.4128 | 7.8275 | 9.4412 | 12.6952 | 8.2229 | 9.8977 | 12.3636 | 9.3483 | 10.5457 | 7.963 | 10.6401 | 8.5994 | 10.5154 | 8.3511 | 10.0959 | 13.3568 | 10.7449 | 10.4741 | 12.1282 | 8.4739 | 10.0272 | 12.7781 | 8.4536 | 10.904 | 9.7336 | 10.2375 | 8.5527 | 10.8406 | -0.19492 | 20.9542 | 0.03522 | 0.048551 | -37.8005 | 3.1198 | 4.63 | 16.62 | 0.37901 | 0.32738 | -0.14989 | -0.54831 | 0.36515 | 0.14734 | 0.83468 | 0.39513 | 0.37672 | 0.407 | 0.40031 | 0.5971 | 0.40499 | 0.40454
42810.44 | -1 | 18.4077 | 18.5218 | 18.5282 | 18.5448 | 17.8838 | 16.5168 | 14.5886 | 16.6688 | 17.1607 | 17.255 | 17.2659 | 16.7957 | 15.8272 | 14.4532 | 14.7929 | 14.8223 | 15.3931 | 13.2764 | 13.3892 | 13.9667 |  |  |  | 16.5563 | 15.8923 | 14.9818 | 10.9154 | 10.4752 | 11.1516 | 17.0707 | 16.2107 | 15.0147 | 16.7833 | 16.0671 | 15.0639 | 10.7769 | 12.1173 |  | 12.0105 | 11.1294 | 10.9101 | 9.453 |  | 6.285 | 6.3938 | 6.0287 | 6.1255 | 6.3998 | 6.7481 | 7.4084 | 4.4431 | 6.3818 | 4.4958 | 6.6551 | 7.9738 | 42.3951 | 46.5675 | 42.8279 | 15.0327 |  |  | 0.1507 | 0.040831 | 0.025508 | -0.13274 | 0.14276 | -0.21994 | 0.68659 | 0.17069 | -0.54525 | -0.42355 | -0.22166 | 8.8698 | 8.8708 | 2.008 | 15.6316 | 16.57 | 17.1366 | 17.4859 | 17.4491 | 16.4375 | 14.7926 | 16.8107 | 17.1626 | 17.4641 | 17.5272 | 17.2599 | 16.4707 | 14.7032 | 6.0987 | 8.1407 | 5.3556 | 5.7764 | 5.8814 | 6.6301 | 7.6366 | 15.6686 | 15.3316 | 15.2175 | 14.1718 | 14.0757 | 14.0293 |  |  |  | 10.6965 | 10.0079 | 9.4956 | 9.3793 | -0.01231 | -0.022936 | 12.8077 |  |  | 10.588 |  |  | 16.8584 | 16.055 | 15.0077 | 16.3651 | 15.6434 | 14.7487 | 10.8035 | 11.2431 | 11.4606 | 11.4384 | 9.5664 |  | 10.5566 | 9.5886 | 9.9845 | 9.6523 | 11.0153 | 12.4509 |  | 12.2346 |  |  | 11.8675 | 12.463 | 12.5276 | [6 empty] | 12.5916 |  |  | 11.4633 |  |  | 9.7075 | 10.5831 | 12.4487 | 7.8316 | 9.442 | 12.7148 | 8.2231 | 9.9104 | 12.3689 | 9.3577 | 10.5521 | 7.9497 | 10.6544 | 8.5793 | 10.5261 | 8.3559 | 10.1075 | 13.3713 | 10.751 | 10.483 | 12.1482 | 8.4862 | 10.0423 | 12.7824 | 8.4637 | 10.9065 | 9.7415 | 10.2408 | 8.5619 | 10.8606 | -0.19993 | 20.9556 | 0.035306 | 0.048631 | -37.822 | 3.1198 | 6.09 | 16.82 | 0.45615 | 0.23544 | 0.18609 | -0.42451 | 0.44052 | -0.54678 | 0.96608 | 0.39484 | 0.37538 | 0.40758 | 0.40646 | 0.60589 | 0.40525 | 0.40465
42810.44 | 0 | 18.4139 | 18.5262 | 18.5313 | 18.544 | 17.8889 | 16.5244 | 14.5866 | 16.6733 | 17.1653 | 17.2599 | 17.2695 | 16.8091 | 15.8369 | 14.4588 | 14.7961 | 14.8182 | 15.3853 | 13.2633 | 13.3952 | 13.968 |  |  |  | 16.5488 | 15.8907 | 14.984 | 10.9176 | 10.4916 | 11.1638 | 17.0751 | 16.2149 | 15.0253 | 16.7889 | 16.0735 | 15.0731 | 10.7829 | 12.1508 |  | 12.0145 | 11.1465 | 10.9163 | 9.4357 |  | 6.2931 | 6.3958 | 6.0145 | 6.1108 | 6.395 | 6.7377 | 7.4058 | 4.4196 | 6.3633 | 4.4393 | 6.648 | 7.9772 | 42.401 | 46.5644 | 42.8437 | 15.0255 |  |  | 0.091559 | -0.11031 | 0.11093 | -0.082798 | 0.11582 | -0.37107 | 0.52428 | 0.33365 | -1.4842 | -0.20997 | -0.34207 | 8.8678 | 8.8688 | 2.0079 | 15.6333 | 16.5678 | 17.1418 | 17.4781 | 17.4552 | 16.4345 | 14.8032 | 16.8136 | 17.1619 | 17.4652 | 17.5276 | 17.2626 | 16.4779 | 14.7045 | 6.1208 | 8.1341 | 5.3053 | 5.7506 | 5.9198 | 6.6322 | 7.6373 | 15.6681 | 15.3337 | 15.214 | 14.175 | 14.0769 | 14.0249 |  |  |  | 10.6951 | 10.0315 | 9.5021 | 9.3833 | 0.0051138 | -0.15317 | 12.8112 |  |  | 10.5916 |  |  | 16.8569 | 16.0546 | 15.0036 | 16.3612 | 15.6446 | 14.7432 | 10.8022 | 11.2444 | 11.4656 | 11.4447 | 9.5747 |  | 10.5604 | 9.629 | 9.9987 | 9.6426 | 11.0199 | 12.4656 |  | 12.2404 |  |  | 11.8708 | 12.4854 | 12.5339 | [6 empty] | 12.6064 |  |  | 11.4896 |  |  | 9.7019 | 10.5881 | 12.5029 | 7.792 | 9.4419 | 12.7174 | 8.2139 | 9.9146 | 12.3651 | 9.355 | 10.553 | 7.9444 | 10.6666 | 8.5661 | 10.5306 | 8.3566 | 10.1135 | 13.3843 | 10.7548 | 10.49 | 12.1742 | 8.4915 | 10.0538 | 12.7894 | 8.4734 | 10.9106 | 9.7583 | 10.2474 | 8.5706 | 10.8674 | 0.041975 | 20.9537 | 0.035054 | 0.048363 | -37.9297 | 3.1198 | -7.45 | 23.7 | 0.35556 | -0.38699 | 0.38808 | -0.33528 | 0.39677 | -0.71021 | 0.84419 | 0.39473 | 0.37472 | 0.408 | 0.40425 | 0.61155 | 0.40593 | 0.40449
42810.44 | 1 | 18.4028 | 18.5212 | 18.5296 | 18.5347 | 17.8868 | 16.5224 | 14.5919 | 16.6679 | 17.1633 | 17.2547 | 17.266 | 16.7997 | 15.8302 | 14.4594 | 14.8011 | 14.8189 | 15.3909 | 13.2783 | 13.4037 | 13.9768 |  |  |  | 16.5602 | 15.8854 | 14.9919 | 10.9323 | 10.5176 | 11.2396 | 17.0664 | 16.2021 | 15.0189 | 16.782 | 16.0632 | 15.0699 | 10.7771 | 12.1645 |  | 12.0087 | 11.151 | 10.9201 | 9.4031 |  | 6.296 | 6.3907 | 6.0033 | 6.1062 | 6.3808 | 6.7367 | 7.429 | 4.4299 | 6.3669 | 4.3686 | 6.657 | 7.9738 | 42.4088 | 46.5585 | 42.8513 | 15.0139 |  |  | 0.042275 | -0.19902 | 0.096476 | 0.08871 | -0.011008 | -0.19037 | 0.46711 | 0.37439 | -0.5939 | -0.008145 | -0.27272 | 8.8692 | 8.8704 | 2.008 | 15.6394 | 16.5704 | 17.1397 | 17.4848 | 17.4616 | 16.4417 | 14.8047 | 16.8151 | 17.1652 | 17.473 | 17.5235 | 17.2663 | 16.4769 | 14.7086 | 6.1007 | 8.129 | 5.2521 | 5.6826 | 5.9514 | 6.6277 | 7.6394 | 15.6621 | 15.3235 | 15.2067 | 14.1708 | 14.0724 | 14.0247 |  |  |  | 10.6959 | 10.0803 | 9.5759 | 9.385 | -0.10773 | -0.028582 | 12.8131 |  |  | 10.5834 |  |  | 16.8485 | 16.0441 | 15.0002 | 16.3573 | 15.6367 | 14.7413 | 10.8127 | 11.2671 | 11.4638 | 11.4511 | 9.5761 |  | 10.5483 | 9.6642 | 9.9918 | 9.6175 | 11.0288 | 12.4555 |  | 12.2378 |  |  | 11.8622 | 12.4844 | 12.5312 | [6 empty] | 12.6089 |  |  | 11.5078 |  |  | 9.6969 | 10.584 | 12.7283 | 7.7654 | 9.4417 | 12.7142 | 8.213 | 9.9175 | 12.3652 | 9.363 | 10.554 | 7.9388 | 10.6808 | 8.5579 | 10.525 | 8.3374 | 10.1211 | 13.3796 | 10.7531 | 10.4853 | 12.1915 | 8.4756 | 10.0522 | 12.7872 | 8.4809 | 10.8955 | 9.7617 | 10.2588 | 8.5629 | 10.8605 | 0.064316 | 20.955 | 0.034687 | 0.048862 | -37.8724 | 3.1198 | 14.47 | 35.42 | 0.24164 | -0.5198 | 0.36191 | 0.34704 | -0.12232 | -0.50869 | 0.79684 | 0.3943 | 0.37352 | 0.40899 | 0.40596 | 0.61771 | 0.40664 | 0.40447
42810.4401 | 2 | 18.4137 | 18.5261 | 18.5261 | 18.5364 | 17.8864 | 16.5186 | 14.5856 | 16.6773 | 17.1615 | 17.2599 | 17.263 | 16.8055 | 15.8287 | 14.4517 | 14.8 | 14.8243 | 15.3941 | 13.2678 | 13.3961 | 13.9697 |  |  |  | 16.544 | 15.8883 | 14.996 | 10.954 | 10.5471 | 11.3658 | 17.0677 | 16.2057 | 15.033 | 16.7789 | 16.0741 | 15.0654 | 10.7788 | 12.1895 |  | 12.0066 | 11.166 | 10.9264 | 9.3823 |  | 6.2924 | 6.3849 | 5.9905 | 6.0938 | 6.365 | 6.7624 | 7.4219 | 4.4843 | 6.3466 | 4.3358 | 6.6442 | 7.9793 | 42.4149 | 46.553 | 42.8587 | 15.0134 |  |  | 0.095499 | -0.085993 | 0.030764 | -0.14194 | -0.048464 | 0.036996 | 0.60905 | 0.12732 | 0.062482 | -2.3067 | -0.384 | 8.8708 | 8.8721 | 2.0081 | 15.637 | 16.5697 | 17.1388 | 17.4884 | 17.4603 | 16.4378 | 14.7992 | 16.8098 | 17.163 | 17.4734 | 17.5271 | 17.2661 | 16.4755 | 14.7015 | 6.043 | 8.1059 | 5.1822 | 5.631 | 5.9695 | 6.6268 | 7.6278 | 15.6649 | 15.3296 | 15.215 | 14.1783 | 14.0768 | 14.0363 |  |  |  | 10.7065 | 10.1818 | 9.6804 | 9.4017 | 0.13518 | -0.060199 | 12.8236 |  |  | 10.5864 |  |  | 16.8544 | 16.0546 | 15.0049 | 16.3634 | 15.6386 | 14.7531 | 10.8105 | 11.326 | 11.4736 | 11.458 | 9.5923 |  | 10.5618 | 9.7043 | 9.9953 | 9.6157 | 11.0259 | 12.46 |  | 12.2379 |  |  | 11.875 | 12.5103 | 12.5364 | [6 empty] | 12.6091 |  |  | 11.5329 |  |  | 9.7104 | 10.5998 | 13.2171 | 7.7705 | 9.4373 | 12.7252 | 8.2113 | 9.9384 | 12.3703 | 9.362 | 10.56 | 7.9249 | 10.6826 | 8.568 | 10.532 | 8.3372 | 10.1212 | 13.3859 | 10.755 | 10.5034 | 12.2622 | 8.4723 | 10.0534 | 12.793 | 8.4858 | 10.9075 | 9.7712 | 10.2777 | 8.5915 | 10.8787 | 0.029263 | 20.9545 | 0.034698 | 0.048898 | -37.8479 | 3.1198 | 2.39 | 34.83 | 0.36326 | -0.34168 | 0.20436 | -0.43897 | -0.25668 | 0.22426 | 0.90992 | 0.39429 | 0.37252 | 0.40894 | 0.41227 | 0.62414 | 0.40728 | 0.40436
42810.4401 | 3 | 18.4006 | 18.5155 | 18.5206 | 18.5282 | 17.8791 | 16.505 | 14.5872 | 16.6614 | 17.1549 | 17.2529 | 17.2546 | 16.7923 | 15.8115 | 14.443 | 14.8015 | 14.8159 | 15.3882 | 13.2745 | 13.4 | 13.9704 |  |  |  | 16.549 | 15.8837 | 14.9835 | 11.0013 | 10.5687 | 11.5829 | 17.0698 | 16.2084 | 15.0191 | 16.7846 | 16.0682 | 15.0668 | 10.7795 | 12.1972 |  | 12.0077 | 11.1793 | 10.9281 | 9.3794 |  | 6.2922 | 6.3883 | 5.9938 | 6.0997 | 6.384 | 6.7848 | 7.4284 | 4.5291 | 6.3562 | 4.3541 | 6.6467 | 7.9778 | 42.4251 | 46.5337 | 42.8664 | 15.0004 |  |  | 0.1001 | 0.015859 | 0.1037 | 0.12288 | 0.22424 | -0.11546 | 0.81932 | 0.25611 | -0.32458 | -0.95287 | -0.5058 | 8.8699 | 8.8706 | 2.0081 | 15.6372 | 16.5655 | 17.1324 | 17.4764 | 17.4497 | 16.4356 | 14.7904 | 16.8078 | 17.1531 | 17.4719 | 17.5243 | 17.2599 | 16.4667 | 14.6991 | 6.0316 | 8.1185 | 5.1444 | 5.5756 | 5.985 | 6.6327 | 7.6265 | 15.6666 | 15.337 | 15.2227 | 14.1695 | 14.0773 | 14.0399 |  |  |  | 10.7031 | 10.3999 | 9.7573 | 9.4141 | 0.22129 | 0.11652 | 12.8297 |  |  | 10.582 |  |  | 16.8633 | 16.0597 | 15.0107 | 16.3662 | 15.6451 | 14.7476 | 10.8197 | 11.366 | 11.4806 | 11.4799 | 9.6063 |  | 10.5645 | 9.6988 | 9.9971 | 9.6032 | 11.0209 | 12.4582 |  | 12.2348 |  |  | 11.8779 | 12.5159 | 12.523 | [6 empty] | 12.5967 |  |  | 11.5757 |  |  | 9.7064 | 10.6037 | 13.7819 | 7.7592 | 9.451 | 12.7306 | 8.2067 | 9.9346 | 12.3825 | 9.3714 | 10.5836 | 7.924 | 10.6918 | 8.5606 | 10.5401 | 8.3129 | 10.128 | 13.3816 | 10.7552 | 10.5025 | 12.4579 | 8.4697 | 10.0726 | 12.7957 | 8.4662 | 10.9039 | 9.7725 | 10.2788 | 8.5974 | 10.8753 | -0.085719 | 20.9546 | 0.034899 | 0.049239 | -37.8553 | 3.1198 | -0.99 | 40.99 | 0.37205 | 0.14673 | 0.37522 | 0.40844 | 0.55214 | -0.39619 | 1.0554 | 0.39399 | 0.37273 | 0.40912 | 0.41423 | 0.62819 | 0.40738 | 0.4039
42810.4401 | 4 | 18.4022 | 18.5202 | 18.5214 | 18.5249 | 17.8734 | 16.5109 | 14.5797 | 16.6631 | 17.1576 | 17.2483 | 17.257 | 16.793 | 15.8263 | 14.4469 | 14.7948 | 14.8133 | 15.3879 | 13.2698 | 13.3887 | 13.9629 |  |  |  | 16.5448 | 15.8815 | 14.9746 | 11.0304 | 10.5881 | 11.5858 | 17.0748 | 16.2122 | 15.0271 | 16.7974 | 16.0761 | 15.0706 | 10.7892 | 12.1953 |  | 12.0166 | 11.1951 | 10.947 | 9.3705 |  | 6.3016 | 6.3911 | 5.9969 | 6.1119 | 6.4119 | 6.8035 | 7.4761 | 4.5798 | 6.3635 | 4.4036 | 6.6457 | 7.98 | 42.4258 | 46.533 | 42.8782 | 14.9858 |  |  | 0.096159 | 0.053971 | 0.037336 | 0.10119 | 0.16247 | 0.23413 | 0.98295 | 0.040576 | -0.55615 | -0.43467 | -0.16801 | 8.8701 | 8.8714 | 2.0078 | 15.637 | 16.5631 | 17.1259 | 17.4734 | 17.4551 | 16.4338 | 14.7865 | 16.811 | 17.1528 | 17.4639 | 17.5173 | 17.2679 | 16.4664 | 14.7006 | 6.065 | 8.1586 | 5.1377 | 5.5329 | 5.9941 | 6.6313 | 7.6284 | 15.6654 | 15.3301 | 15.2182 | 14.1718 | 14.0771 | 14.0342 |  |  |  | 10.6964 | 10.6525 | 9.8245 | 9.4207 | 0.066502 | 0.17355 | 12.8296 |  |  | 10.5884 |  |  | 16.8627 | 16.0528 | 15.0104 | 16.3648 | 15.644 | 14.749 | 10.8357 | 11.4913 | 11.4978 | 11.5043 | 9.6162 |  | 10.572 | 9.6623 | 9.9962 | 9.6241 | 11.0318 | 12.4625 |  | 12.2437 |  |  | 11.8827 | 12.5116 | 12.5329 | [6 empty] | 12.6164 |  |  | 11.6175 |  |  | 9.7142 | 10.6162 | 14.4628 | 7.7334 | 9.457 | 12.7312 | 8.1971 | 9.9424 | 12.3873 | 9.3811 | 10.5926 | 7.9296 | 10.695 | 8.5562 | 10.5438 | 8.2676 | 10.1149 | 13.3837 | 10.7614 | 10.5151 | 12.752 | 8.4632 | 10.0635 | 12.7884 | 8.4273 | 10.9044 | 9.7825 | 10.2839 | 8.6054 | 10.8797 | 0.028107 | 20.9544 | 0.035576 | 0.04947 | -37.9503 | 3.1198 | 7.12 | 45.68 | 0.36466 | 0.27069 | 0.22514 | 0.37065 | 0.47 | 0.56421 | 1.156 | 0.39396 | 0.37372 | 0.4089 | 0.41034 | 0.62914 | 0.40795 | 0.40349
42810.4401 | 5 | 18.4028 | 18.5057 | 18.516 | 18.5209 | 17.8718 | 16.5052 | 14.5692 | 16.6573 | 17.1521 | 17.2493 | 17.257 | 16.7956 | 15.8229 | 14.4506 | 14.801 | 14.8189 | 15.3836 | 13.2683 | 13.3917 | 13.9615 |  |  |  | 16.5478 | 15.8778 | 14.9771 | 11.0725 | 10.6097 | 11.7061 | 17.079 | 16.2189 | 15.0237 | 16.7915 | 16.0754 | 15.0684 | 10.7892 | 12.2027 |  | 12.0147 | 11.2025 | 10.9507 | 9.3832 |  | 6.3043 | 6.3918 | 5.9963 | 6.1258 | 6.4352 | 6.89 | 7.5672 | 4.6468 | 6.3612 | 4.5053 | 6.6466 | 7.9775 | 42.4251 | 46.5356 | 42.882 | 14.9697 |  |  | 0.042275 | -0.22399 | 0.075448 | 0.17151 | 0.20453 | 0.56269 | 0.50522 | 0.2502 | -0.26814 | -0.40907 | -0.291 | 8.8676 | 8.8688 | 2.0081 | 15.6442 | 16.5683 | 17.1326 | 17.4869 | 17.4518 | 16.4331 | 14.7927 | 16.8114 | 17.1601 | 17.4664 | 17.5217 | 17.2638 | 16.467 | 14.689 | 6.1533 | 8.1604 | 5.1254 | 5.5028 | 5.9729 | 6.6307 | 7.6256 | 15.6689 | 15.3347 | 15.2222 | 14.182 | 14.0817 | 14.0275 |  |  |  | 10.7104 | 11.0796 | 9.8596 | 9.4515 | 0.12384 | 0.18352 | 12.8359 |  |  | 10.5892 |  |  | 16.8591 | 16.0506 | 15.0095 | 16.3675 | 15.6381 | 14.7462 | 10.846 | 11.5973 | 11.4978 | 11.5156 | 9.599 |  | 10.5707 | 9.6091 | 10.0027 | 9.642 | 11.0439 | 12.4652 |  | 12.2411 |  |  | 11.8767 | 12.5031 | 12.5286 | [6 empty] | 12.6272 |  |  | 11.6578 |  |  | 9.7051 | 10.6191 | 15.2927 | 7.7205 | 9.454 | 12.7335 | 8.196 | 9.9479 | 12.3928 | 9.3908 | 10.5944 | 7.9383 | 10.7059 | 8.5491 | 10.5509 | 8.2357 | 10.1207 | 13.3877 | 10.7724 | 10.5302 | 13.1766 | 8.471 | 10.0822 | 12.8017 | 8.4114 | 10.9136 | 9.7893 | 10.2927 | 8.6152 | 10.8901 | -0.024665 | 20.955 | 0.035984 | 0.049289 | -37.8452 | 3.1198 | 16.83 | 45.5 | 0.24184 | -0.55145 | 0.32005 | 0.48254 | 0.52742 | 0.8748 | 0.82893 | 0.3944 | 0.37541 | 0.40881 | 0.40047 | 0.63019 | 0.4076 | 0.4031
42810.4401 | 6 | 18.4127 | 18.5157 | 18.52 | 18.5296 | 17.8756 | 16.51 | 14.5747 | 16.6644 | 17.1531 | 17.2501 | 17.2625 | 16.7985 | 15.825 | 14.453 | 14.8114 | 14.8245 | 15.3957 | 13.2716 | 13.3977 | 13.9632 |  |  |  | 16.5518 | 15.8874 | 14.9823 | 11.1385 | 10.6411 | 12.0401 | 17.0813 | 16.2165 | 15.0313 | 16.7924 | 16.0781 | 15.0675 | 10.784 | 12.2544 |  | 12.0199 | 11.2046 | 10.955 | 9.4021 |  | 6.2962 | 6.3819 | 5.9936 | 6.1408 | 6.4671 | 6.9224 | 7.5553 | 4.6977 | 6.3522 | 4.5423 | 6.6358 | 7.9809 | 42.4281 | 46.5404 | 42.9018 | 14.9589 |  |  | 0.12704 | -0.20953 | 0.15233 | -0.15048 | 0.17824 | -0.071428 | 0.44608 | 0.1766 | 0.15667 | -0.20242 | -0.18629 | 8.8709 | 8.8719 | 2.0082 | 15.635 | 16.5678 | 17.1347 | 17.4797 | 17.4467 | 16.4292 | 14.7978 | 16.8104 | 17.1609 | 17.4676 | 17.5235 | 17.2603 | 16.4736 | 14.6982 | 6.2827 | 8.1756 | 5.1109 | 5.4778 | 5.94 | 6.6392 | 7.6259 | 15.6649 | 15.3233 | 15.2201 | 14.1707 | 14.0796 | 14.0302 |  |  |  | 10.709 | 11.4523 | 9.8594 | 9.4603 | -0.075724 | 0.11652 | 12.8446 |  |  | 10.5872 |  |  | 16.8629 | 16.0596 | 15.007 | 16.372 | 15.6514 | 14.7477 | 10.8701 | 11.6497 | 11.5079 | 11.5373 | 9.5786 |  | 10.5678 | 9.5415 | 10.0071 | 9.659 | 11.0433 | 12.4647 |  | 12.2405 |  |  | 11.8735 | 12.5087 | 12.5233 | [6 empty] | 12.6374 |  |  | 11.7023 |  |  | 9.714 | 10.6455 | 16.406 | 7.7217 | 9.4682 | 12.7415 | 8.2016 | 9.9566 | 12.4376 | 9.4083 | 10.6085 | 7.948 | 10.7228 | 8.5548 | 10.572 | 8.2092 | 10.1204 | 13.3953 | 10.7715 | 10.5439 | 13.6526 | 8.4727 | 10.0699 | 12.8179 | 8.4161 | 10.9186 | 9.8001 | 10.3012 | 8.618 | 10.8949 | 0.040819 | 20.9543 | 0.036661 | 0.050664 | -37.7667 | 3.1198 | 16.74 | 46.45 | 0.41948 | -0.53335 | 0.45476 | -0.45198 | 0.49239 | -0.3117 | 0.77895 | 0.39487 | 0.37743 | 0.40831 | 0.38707 | 0.63183 | 0.4069 | 0.40281
42810.4401 | 7 | 18.4097 | 18.5173 | 18.5202 | 18.5364 | 17.875 | 16.5143 | 14.5779 | 16.6604 | 17.1552 | 17.2489 | 17.2625 | 16.7963 | 15.8232 | 14.4541 | 14.8074 | 14.8274 | 15.3957 | 13.2751 | 13.399 | 13.9652 |  |  |  | 16.5514 | 15.8873 | 14.9867 | 11.1905 | 10.7214 | 12.0703 | 17.0875 | 16.2206 | 15.0325 | 16.7943 | 16.0838 | 15.072 | 10.798 | 12.8194 |  | 12.022 | 11.2206 | 10.9717 | 9.4172 |  | 6.2949 | 6.3785 | 6.016 | 6.1623 | 6.5014 | 6.9044 | 7.5072 | 4.7062 | 6.3577 | 4.5778 | 6.6407 | 7.985 | 42.4229 | 46.5435 | 42.923 | 14.9561 |  |  | -0.014893 | -0.19705 | -0.017204 | 0.3509 | 0.41678 | 0.03568 | 0.44674 | 0.064892 | -0.22202 | -2.57 | -0.25961 | 8.8698 | 8.8711 | 2.0079 | 15.652 | 16.575 | 17.1419 | 17.4869 | 17.4642 | 16.4356 | 14.8061 | 16.8115 | 17.1692 | 17.4719 | 17.5283 | 17.2676 | 16.4728 | 14.7043 | 6.3608 | 8.2272 | 5.1285 | 5.4517 | 5.9392 | 6.635 | 7.63 | 15.6759 | 15.3305 | 15.2209 | 14.175 | 14.0806 | 14.0344 |  |  |  | 10.7217 | 11.7187 | 9.8876 | 9.4821 | 0.04381 | -0.027829 | 12.8479 |  |  | 10.5927 |  |  | 16.8654 | 16.0562 | 15.0131 | 16.371 | 15.6498 | 14.7521 | 10.883 | 11.6825 | 11.526 | 11.5438 | 9.5736 |  | 10.575 | 9.4626 | 10.0131 | 9.6887 | 11.0479 | 12.4805 |  | 12.2421 |  |  | 11.8642 | 12.5215 | 12.529 | [6 empty] | 12.6562 |  |  | 11.7364 |  |  | 9.7172 | 10.6619 | 17.2362 | 7.7182 | 9.479 | 12.7454 | 8.1963 | 9.9475 | 12.6245 | 9.4182 | 10.6152 | 7.9457 | 10.7284 | 8.5521 | 10.5821 | 8.1992 | 10.1268 | 13.4033 | 10.7738 | 10.5646 | 14.2378 | 8.4707 | 10.0721 | 12.8753 | 8.4152 | 10.9268 | 9.8093 | 10.3012 | 8.6155 | 10.9052 | 0.07125 | 20.9541 | 0.035278 | 0.048652 | -37.8124 | 3.1199 | -1.02 | 45.22 | -0.14363 | -0.51721 | -0.15283 | 0.6902 | 0.7529 | 0.22029 | 0.7795 | 0.39525 | 0.37982 | 0.40764 | 0.37791 | 0.63035 | 0.40694 | 0.40262
42810.4401 | 8 | 18.4126 | 18.5234 | 18.5173 | 18.5384 | 17.8808 | 16.5149 | 14.5798 | 16.668 | 17.1622 | 17.2571 | 17.2613 | 16.7973 | 15.8212 | 14.4576 | 14.8057 | 14.8261 | 15.3932 | 13.276 | 13.3972 | 13.9669 |  |  |  | 16.5506 | 15.8849 | 14.9826 | 11.2131 | 10.9158 | 11.9962 | 17.0791 | 16.2172 | 15.0218 | 16.7836 | 16.071 | 15.066 | 10.797 | 13.8643 |  | 12.0291 | 11.2257 | 10.9723 | 9.4463 |  | 6.2934 | 6.3805 | 6.0196 | 6.1565 | 6.4793 | 6.8703 | 7.4577 | 4.698 | 6.3573 | 4.6208 | 6.6366 | 7.9839 | 42.4103 | 46.5213 | 42.932 | 14.9426 |  |  | 0.34324 | -0.039337 | 0.071504 | 0.097254 | 0.05602 | -0.076028 | 0.17206 | -0.031704 | -0.45476 | -1.5307 | -0.33353 | 8.8673 | 8.8684 | 2.0079 | 15.648 | 16.5729 | 17.1371 | 17.4801 | 17.4561 | 16.435 | 14.7986 | 16.8056 | 17.1636 | 17.472 | 17.5239 | 17.2601 | 16.4655 | 14.694 | 6.3838 | 8.2336 | 5.2698 | 5.4227 | 5.9297 | 6.6326 | 7.6298 | 15.6802 | 15.3413 | 15.2217 | 14.1762 | 14.0843 | 14.0287 |  |  |  | 10.7213 | 12.0978 | 10.067 | 9.5263 | -0.055666 | -0.014278 | 12.8438 |  |  | 10.5924 |  |  | 16.8609 | 16.0548 | 15.0071 | 16.3603 | 15.6475 | 14.7516 | 10.8907 | 11.7774 | 11.5313 | 11.5644 | 9.5804 |  | 10.5725 | 9.3739 | 10.0075 | 9.7092 | 11.0502 | 12.4821 |  | 12.2419 |  |  | 11.8767 | 12.534 | 12.5409 | [6 empty] | 12.6717 |  |  | 11.7864 |  |  | 9.714 | 10.6723 | 18.2849 | 7.7164 | 9.4868 | 12.7537 | 8.1917 | 9.9408 | 13.0152 | 9.4329 | 10.6135 | 7.9547 | 10.7323 | 8.5458 | 10.5934 | 8.2035 | 10.1339 | 13.4135 | 10.7858 | 10.578 | 14.9313 | 8.4716 | 10.0785 | 13.0923 | 8.4273 | 10.9335 | 9.8245 | 10.3084 | 8.6198 | 10.9318 | -0.024665 | 20.9538 | 0.03491 | 0.04698 | -37.8136 | 3.1198 | 4.72 | 45.12 | 0.68944 | -0.23109 | 0.31156 | 0.36336 | 0.27602 | -0.32155 | 0.48373 | 0.39498 | 0.3821 | 0.40715 | 0.37507 | 0.61462 | 0.4061 | 0.40138
42810.4401 | 9 | 18.4195 | 18.5265 | 18.5298 | 18.5441 | 17.8782 | 16.5128 | 14.5837 | 16.6693 | 17.1627 | 17.2578 | 17.2664 | 16.8058 | 15.8312 | 14.4527 | 14.8035 | 14.824 | 15.3923 | 13.2717 | 13.3958 | 13.9605 |  |  |  | 16.552 | 15.8828 | 14.9785 | 11.2312 | 11.2148 | 11.9068 | 17.0833 | 16.2264 | 15.0226 | 16.7888 | 16.0752 | 15.0616 | 10.7986 | 15.47 |  | 12.0338 | 11.2314 | 10.9767 | 9.562 |  | 6.2951 | 6.3805 | 6.0194 | 6.1474 | 6.4648 | 6.8357 | 7.4276 | 4.6985 | 6.3558 | 4.5945 | 6.6436 | 7.9917 | 42.411 | 46.502 | 42.9461 | 14.9382 |  |  | 0.11784 | 0.004687 | -0.035604 | 0.08477 | 0.048792 | -0.032 | 0.18192 | 0.1904 | 0.081747 | -0.34068 | -0.18629 | 8.8706 | 8.8717 | 2.0081 | 15.6544 | 16.5682 | 17.1419 | 17.4927 | 17.4587 | 16.4339 | 14.7974 | 16.8116 | 17.1657 | 17.4681 | 17.5267 | 17.267 | 16.4703 | 14.7003 | 6.3813 | 8.2239 | 5.4218 | 5.3804 | 5.9436 | 6.6352 | 7.6351 | 15.687 | 15.3268 | 15.2135 | 14.1758 | 14.0723 | 14.0309 |  |  |  | 10.7191 | 12.6466 | 10.2374 | 9.5669 | -0.0062318 | -0.093699 | 12.85 |  |  | 10.5978 |  |  | 16.8517 | 16.0598 | 15.0126 | 16.3688 | 15.6545 | 14.7493 | 10.9007 | 12.2404 | 11.543 | 11.5812 | 9.6136 |  | 10.5779 | 9.3116 | 10.0101 | 9.7126 | 11.0587 | 12.5022 |  | 12.233 |  |  | 11.8722 | 12.5425 | 12.5494 | [6 empty] | 12.6834 |  |  | 11.8454 |  |  | 9.7284 | 10.6919 | 19.2745 | 7.7309 | 9.512 | 12.7702 | 8.1939 | 9.9492 | 13.4583 | 9.4504 | 10.6319 | 7.9788 | 10.7487 | 8.5558 | 10.6091 | 8.1975 | 10.1395 | 13.4188 | 10.7989 | 10.5844 | 15.759 | 8.4672 | 10.0897 | 13.4252 | 8.4297 | 10.943 | 9.8369 | 10.3156 | 8.6253 | 10.9598 | -0.0094496 | 20.9555 | 0.034549 | 0.046249 | -37.8663 | 3.1198 | -6.94 | 44.68 | 0.40391 | 0.079768 | -0.21985 | 0.33924 | 0.25758 | -0.2086 | 0.49737 | 0.39423 | 0.38391 | 0.40733 | 0.37566 | 0.59836 | 0.40294 | 0.40018
42810.4402 | 10 | 18.4125 | 18.5239 | 18.5308 | 18.5405 | 17.8818 | 16.5071 | 14.5773 | 16.6635 | 17.1585 | 17.2616 | 17.2633 | 16.7997 | 15.8308 | 14.4505 | 14.8093 | 14.8203 | 15.3928 | 13.27 | 13.3915 | 13.9605 |  |  |  | 16.5512 | 15.8776 | 14.9794 | 11.2421 | 11.5689 | 11.944 | 17.0898 | 16.2214 | 15.032 | 16.7849 | 16.0707 | 15.0679 | 10.8078 | 17.1136 |  | 12.0607 | 11.244 | 10.9924 | 9.6487 |  | 6.2979 | 6.364 | 6.0263 | 6.1447 | 6.4497 | 6.8195 | 7.3892 | 4.7193 | 6.3606 | 4.6092 | 6.6452 | 7.9845 | 42.4072 | 46.4847 | 42.9551 | 14.925 |  |  | 0.12639 | 0.21168 | 0.085304 | -1.1283 | 0.24396 | -0.049088 | 0.19112 | -0.067848 | -1.1715 | -0.64342 | -0.31008 | 8.8698 | 8.8707 | 2.0082 | 15.6445 | 16.5669 | 17.1334 | 17.4847 | 17.4519 | 16.435 | 14.7945 | 16.8024 | 17.1549 | 17.4603 | 17.5177 | 17.2619 | 16.4676 | 14.6991 | 6.3491 | 8.2137 | 5.4959 | 5.3663 | 5.9639 | 6.6418 | 7.6426 | 15.6791 | 15.334 | 15.2174 | 14.167 | 14.0826 | 14.0406 |  |  |  | 10.7289 | 13.1156 | 10.2773 | 9.6066 | -0.10895 | -0.04025 | 12.849 |  |  | 10.5918 |  |  | 16.8538 | 16.0503 | 15.0049 | 16.3674 | 15.6499 | 14.7571 | 11.0183 | 12.6417 | 11.5564 | 11.5925 | 9.6556 |  | 10.5814 | 9.3051 | 10.004 | 9.7243 | 11.0656 | 12.4992 |  | 12.2247 |  |  | 11.8649 | 12.5411 | 12.5508 | [6 empty] | 12.6865 |  |  | 11.8933 |  |  | 9.7362 | 10.7102 | 19.9705 | 7.7392 | 9.5242 | 12.7766 | 8.1843 | 9.9587 | 13.832 | 9.4612 | 10.6395 | 7.9934 | 10.7564 | 8.5486 | 10.6125 | 8.1716 | 10.1458 | 13.429 | 10.8106 | 10.5959 | 16.4526 | 8.4652 | 10.1026 | 13.8644 | 8.4206 | 10.9434 | 9.8434 | 10.3283 | 8.6328 | 10.9935 | 0.053531 | 20.9534 | 0.034273 | 0.046076 | -37.8217 | 3.1198 | -10.58 | 42.33 | 0.41832 | 0.53605 | 0.34029 | -1.2376 | 0.57594 | -0.25835 | 0.50977 | 0.39318 | 0.3839 | 0.40724 | 0.38 | 0.591 | 0.40083 | 0.3994
42810.4402 | 11 | 18.4189 | 18.5274 | 18.5249 | 18.5436 | 17.8824 | 16.5071 | 14.5772 | 16.664 | 17.1597 | 17.2556 | 17.2627 | 16.8042 | 15.8262 | 14.4536 | 14.8071 | 14.8225 | 15.3945 | 13.2737 | 13.3895 | 13.9588 |  |  |  | 16.5458 | 15.8799 | 14.9773 | 11.3144 | 12.0753 | 13.3318 | 17.1029 | 16.2291 | 15.0334 | 16.7963 | 16.0772 | 15.0703 | 10.8059 | 18.2228 |  | 12.0936 | 11.2544 | 11.0095 | 9.8761 |  | 6.2916 | 6.3535 | 6.0144 | 6.1321 | 6.4419 | 6.7974 | 7.3489 | 4.7087 | 6.3638 | 4.5921 | 6.6404 | 7.9866 | 42.3878 | 46.4733 | 42.961 | 14.9144 |  |  | -0.017521 | -0.055765 | -0.23406 | -0.46458 | 0.14276 | -0.15817 | 0.04984 | 0.00838 | -0.31115 | -0.35788 | -0.51216 | 8.8701 | 8.871 | 2.0081 | 15.6456 | 16.5787 | 17.1379 | 17.4897 | 17.4563 | 16.4386 | 14.7965 | 16.8083 | 17.1519 | 17.4644 | 17.5178 | 17.2636 | 16.4706 | 14.6983 | 6.2734 | 8.193 | 5.4725 | 5.4138 | 5.9215 | 6.6414 | 7.6404 | 15.6802 | 15.3284 | 15.2173 | 14.1657 | 14.0806 | 14.0284 |  |  |  | 10.7303 | 13.6027 | 10.2718 | 9.651 | -0.046347 | 0.055167 | 12.8524 |  |  | 10.5879 |  |  | 16.8638 | 16.0546 | 15.0038 | 16.3641 | 15.6524 | 14.7553 | 11.2334 | 12.7788 | 11.5709 | 11.6187 | 9.6647 |  | 10.5785 | 9.3617 | 10.0075 | 9.7475 | 11.075 | 12.4968 |  | 12.236 |  |  | 11.8415 | 12.5389 | 12.5408 | [6 empty] | 12.7044 |  |  | 11.941 |  |  | 9.7389 | 10.7225 | 20.8434 | 7.7408 | 9.5421 | 12.789 | 8.1865 | 9.9526 | 14.2036 | 9.4798 | 10.6414 | 7.9967 | 10.7603 | 8.5402 | 10.6188 | 8.1616 | 10.1566 | 13.4391 | 10.8207 | 10.6155 | 16.9353 | 8.4721 | 10.1152 | 14.299 | 8.4272 | 10.95 | 9.8542 | 10.3485 | 8.6417 | 11.0291 | 0.075102 | 20.9543 | 0.034968 | 0.045967 | -37.7383 | 3.1198 | 6.19 | 42.11 | -0.15613 | -0.27513 | -0.56366 | -0.79413 | 0.44056 | -0.46373 | 0.26031 | 0.39283 | 0.38244 | 0.4069 | 0.38836 | 0.59334 | 0.39445 | 0.39821
42810.4402 | 12 | 18.4218 | 18.5273 | 18.5309 | 18.5437 | 17.8839 | 16.513 | 14.5828 | 16.6706 | 17.1621 | 17.2582 | 17.2673 | 16.8089 | 15.8344 | 14.4601 | 14.8158 | 14.8139 | 15.389 | 13.2745 | 13.3867 | 13.9593 |  |  |  | 16.5458 | 15.877 | 14.971 | 11.544 | 12.6407 | 14.5977 | 17.0989 | 16.2245 | 15.0306 | 16.7905 | 16.0764 | 15.0656 | 10.8111 | 19.6932 |  | 12.123 | 11.2687 | 11.0939 | 10.211 |  | 6.2875 | 6.3546 | 6.0009 | 6.1199 | 6.4273 | 6.7812 | 7.3155 | 4.657 | 6.3718 | 4.5775 | 6.6457 | 7.9931 | 42.3886 | 46.4735 | 42.9742 | 14.908 |  |  | 0.000875 | -0.13331 | 0.035364 | -0.12419 | 0.13684 | -0.16802 | 0.32846 | -0.22358 | -0.27281 | -0.6344 | -0.30928 | 8.8699 | 8.871 | 2.0082 | 15.6545 | 16.5721 | 17.1392 | 17.4898 | 17.4567 | 16.4369 | 14.7964 | 16.8088 | 17.1478 | 17.4631 | 17.5206 | 17.2653 | 16.4651 | 14.7002 | 6.1954 | 8.1607 | 5.4447 | 5.4072 | 5.8885 | 6.6422 | 7.6494 | 15.684 | 15.3286 | 15.2153 | 14.1716 | 14.0752 | 14.0346 |  |  |  | 10.737 | 14.0617 | 10.279 | 9.6825 | 0.041177 | 0.063825 | 12.8587 |  |  | 10.5883 |  |  | 16.8652 | 16.0647 | 15.0143 | 16.3691 | 15.6515 | 14.7536 | 11.3704 | 12.9438 | 11.5777 | 11.6273 | 9.6776 |  | 10.584 | 9.4264 | 10.0199 | 9.7897 | 11.0793 | 12.5214 |  | 12.2344 |  |  | 11.8292 | 12.5358 | 12.5412 | [6 empty] | 12.7518 |  |  | 11.9952 |  |  | 9.7478 | 10.7444 | 21.6231 | 7.7548 | 9.5672 | 12.9065 | 8.1794 | 9.9616 | 14.6625 | 9.4933 | 10.6577 | 8.0156 | 10.7749 | 8.5407 | 10.6162 | 8.1519 | 10.1687 | 13.4462 | 10.836 | 10.6329 | 17.3671 | 8.4627 | 10.1298 | 14.5749 | 8.4448 | 10.9672 | 9.871 | 10.3738 | 8.6487 | 11.0558 | -0.031599 | 20.9538 | 0.034681 | 0.047704 | -37.7284 | 3.1199 | -7.23 | 42.71 | 0.034968 | -0.42539 | 0.2191 | -0.41059 | 0.43133 | -0.47795 | 0.66824 | 0.39265 | 0.38105 | 0.40587 | 0.39712 | 0.59747 | 0.38532 | 0.39756
42810.4402 | 13 | 18.4211 | 18.5256 | 18.5279 | 18.5424 | 17.886 | 16.5176 | 14.5874 | 16.6666 | 17.1585 | 17.2638 | 17.2728 | 16.8073 | 15.8332 | 14.461 | 14.8192 | 14.8241 | 15.3989 | 13.2726 | 13.3912 | 13.9616 |  |  |  | 16.5494 | 15.8764 | 14.9756 | 11.7094 | 13.1437 | 14.5865 | 17.0974 | 16.2245 | 15.0332 | 16.7884 | 16.0726 | 15.0632 | 10.8188 | 21.4502 |  | 12.1699 | 11.3572 | 11.3565 | 10.3002 |  | 6.2812 | 6.3458 | 5.9973 | 6.1139 | 6.4061 | 6.7372 | 7.2728 | 4.6231 | 6.3636 | 4.5934 | 6.6453 | 7.989 | 42.3863 | 46.4635 | 42.98 | 14.8897 |  |  | -0.051037 | -0.18653 | 0.21344 | -0.051254 | 0.26564 | 0.13754 | 0.070868 | 0.037292 | -0.42713 | -0.52299 | -0.50381 | 8.8669 | 8.8681 | 2.0081 | 15.6549 | 16.5764 | 17.1434 | 17.4877 | 17.4605 | 16.4413 | 14.8009 | 16.8114 | 17.1572 | 17.4722 | 17.5236 | 17.2615 | 16.4678 | 14.6957 | 6.145 | 8.1503 | 5.3924 | 5.5166 | 5.8464 | 6.635 | 7.6446 | 15.6813 | 15.3275 | 15.2163 | 14.1699 | 14.0647 | 14.0319 |  |  |  | 10.7349 | 14.5773 | 10.3417 | 9.6787 | -0.033583 | 0.092431 | 12.8558 |  |  | 10.5772 |  |  | 16.854 | 16.0575 | 15.01 | 16.363 | 15.6428 | 14.75 | 11.5063 | 13.1838 | 11.5816 | 11.6283 | 9.6691 |  | 10.5931 | 9.4725 | 10.0211 | 9.8097 | 11.0909 | 12.5255 |  | 12.2351 |  |  | 11.8334 | 12.5347 | 12.5349 | [6 empty] | 12.7492 |  |  | 12.0355 |  |  | 9.7461 | 10.7604 | 22.4284 | 7.7367 | 9.5762 | 13.127 | 8.1447 | 9.9508 | 15.0685 | 9.5144 | 10.664 | 8.0119 | 10.771 | 8.53 | 10.6079 | 8.1293 | 10.1695 | 13.4518 | 10.8349 | 10.6353 | 17.7589 | 8.4378 | 10.1289 | 14.8776 | 8.4411 | 10.9649 | 9.8691 | 10.3865 | 8.64 | 11.0906 | -0.086297 | 20.9555 | 0.035427 | 0.048073 | -37.836 | 3.1198 | -8.74 | 42.52 | -0.26706 | -0.50319 | 0.53826 | -0.26377 | 0.6009 | 0.43238 | 0.31037 | 0.39319 | 0.37981 | 0.4057 | 0.40189 | 0.60272 | 0.3831 | 0.3976
42810.4402 | 14 | 18.4232 | 18.5264 | 18.5226 | 18.5494 | 17.8855 | 16.5164 | 14.5843 | 16.6621 | 17.1628 | 17.2622 | 17.2658 | 16.8063 | 15.8365 | 14.46 | 14.819 | 14.8276 | 15.3983 | 13.2686 | 13.3924 | 13.9692 |  |  |  | 16.5448 | 15.8877 | 14.9743 | 11.8644 | 13.6128 | 15.6849 | 17.1046 | 16.2324 | 15.0434 | 16.7925 | 16.0744 | 15.0711 | 10.8319 | 22.7206 |  | 12.2082 | 11.4962 | 11.7009 | 10.3001 |  | 6.2774 | 6.3365 | 5.9939 | 6.1064 | 6.3824 | 6.7081 | 7.2508 | 4.7313 | 6.3671 | 4.6802 | 6.6502 | 7.9938 | 42.3975 | 46.4785 | 43.0007 | 14.8894 |  |  | -0.076005 | -0.083365 | -0.04152 | 0.12945 | 0.012648 | 0.089564 | 0.52756 | 0.056348 | -0.92784 | -0.46719 | -0.40029 | 8.8693 | 8.8706 | 2.0077 | 15.6562 | 16.5782 | 17.1402 | 17.4851 | 17.4574 | 16.4467 | 14.7945 | 16.8087 | 17.1548 | 17.4597 | 17.5172 | 17.2615 | 16.465 | 14.6875 | 6.1046 | 8.1371 | 5.3463 | 5.5573 | 5.8275 | 6.6371 | 7.6468 | 15.6883 | 15.3391 | 15.2216 | 14.1663 | 14.0821 | 14.0298 |  |  |  | 10.7436 | 15.0787 | 10.5802 | 9.6968 | -0.14299 | 0.031078 | 12.8616 |  |  | 10.5687 |  |  | 16.8608 | 16.0473 | 14.9995 | 16.3676 | 15.6394 | 14.749 | 11.6095 | 13.4416 | 11.5856 | 11.6567 | 9.6461 |  | 10.5908 | 9.374 | 10.0223 | 9.8342 | 11.0889 | 12.6833 |  | 12.2422 |  |  | 11.8224 | 12.5228 | 12.5558 | [6 empty] | 12.7445 |  |  | 12.0891 |  |  | 9.7666 | 10.7817 | 23.4798 | 7.7378 | 9.6008 | 13.4555 | 8.1385 | 9.9702 | 15.4751 | 9.5383 | 10.6868 | 8.0094 | 10.7771 | 8.5398 | 10.6271 | 8.1175 | 10.1814 | 13.4463 | 10.8473 | 10.65 | 18.1947 | 8.4385 | 10.1421 | 15.29 | 8.4348 | 10.9655 | 9.8853 | 10.4101 | 8.6493 | 11.1605 | 0.055457 | 20.9538 | 0.035743 | 0.048392 | -37.916 | 3.1198 | -18.06 | 41.73 | -0.32652 | -0.33639 | -0.2374 | 0.41918 | 0.13111 | 0.3489 | 0.84679 | 0.39375 | 0.38258 | 0.40495 | 0.40662 | 0.6081 | 0.38353 | 0.39738
42810.4402 | 15 | 18.423 | 18.5275 | 18.5241 | 18.5425 | 17.8826 | 16.5092 | 14.5761 | 16.6615 | 17.1594 | 17.2551 | 17.2674 | 16.7989 | 15.829 | 14.4563 | 14.8178 | 14.8306 | 15.3964 | 13.2735 | 13.3911 | 13.9562 |  |  |  | 16.5532 | 15.8851 | 14.9786 | 12.1168 | 14.1053 | 17.9733 | 17.1115 | 16.2338 | 15.0379 | 16.7898 | 16.0819 | 15.0786 | 10.844 | 23.7541 |  | 12.2546 | 11.6036 | 11.9939 | 10.2724 |  | 6.2616 | 6.3317 | 5.9829 | 6.1015 | 6.3719 | 6.6759 | 7.2154 | 4.8303 | 6.3667 | 4.6839 | 6.6528 | 7.9934 | 42.4335 | 46.4718 | 42.9977 | 14.8725 |  |  | 0.13559 | 0.10917 | -0.05466 | 0.071626 | 0.094788 | 0.051452 | 0.47631 | 0.03992 | -0.22144 | -0.54041 | -0.30014 | 8.8667 | 8.868 | 2.0079 | 15.6591 | 16.5805 | 17.1452 | 17.4917 | 17.4572 | 16.4432 | 14.7919 | 16.8076 | 17.1554 | 17.466 | 17.5159 | 17.2625 | 16.4689 | 14.6915 | 6.0714 | 8.1643 | 5.2962 | 5.6215 | 5.7895 | 6.6314 | 7.6503 | 15.692 | 15.3336 | 15.2234 | 14.1731 | 14.0746 | 14.0324 |  |  |  | 10.7453 | 15.5392 | 10.862 | 9.7207 | -0.0068396 | -0.012961 | 12.8586 |  |  | 10.5638 |  |  | 16.8532 | 16.0564 | 15.0003 | 16.3685 | 15.6406 | 14.7419 | 11.7026 | 13.6395 | 11.6013 | 11.6756 | 9.6356 |  | 10.5847 | 8.9697 | 10.0187 | 9.8588 | 11.1031 | 13.325 |  | 12.2396 |  |  | 11.8062 | 12.5277 | 12.5528 | [6 empty] | 12.7565 |  |  | 12.1376 |  |  | 9.7608 | 10.7989 | 24.3957 | 7.72 | 9.5703 | 13.7768 | 8.1376 | 9.9789 | 15.8772 | 9.5647 | 10.6932 | 7.9867 | 10.7939 | 8.534 | 10.6199 | 8.1098 | 10.1964 | 13.5249 | 10.8505 | 10.6702 | 18.6023 | 8.444 | 10.1649 | 15.5993 | 8.4382 | 11.0082 | 9.9011 | 10.4236 | 8.6387 | 11.2822 | 0.0038398 | 20.9529 | 0.035662 | 0.04769 | -37.7761 | 3.1199 | 10.1 | 41.87 | 0.43784 | 0.38494 | -0.27238 | 0.3118 | 0.35891 | 0.26443 | 0.80456 | 0.39384 | 0.39369 | 0.40474 | 0.40964 | 0.61408 | 0.3847 | 0.39677
42810.4402 | 16 | 18.4297 | 18.5239 | 18.5241 | 18.5483 | 17.8847 | 16.51 | 14.5749 | 16.6691 | 17.1546 | 17.2585 | 17.2604 | 16.7991 | 15.8288 | 14.453 | 14.8228 | 14.8327 | 15.396 | 13.2793 | 13.3975 | 13.9769 |  |  |  | 16.5535 | 15.8963 | 14.9798 | 12.5212 | 14.5448 | 20.0621 | 17.1048 | 16.233 | 15.0391 | 16.7933 | 16.0917 | 15.0792 | 10.8416 | 24.551 |  | 12.301 | 11.6708 | 12.3118 | 10.221 |  | 6.2596 | 6.3322 | 5.9762 | 6.0973 | 6.3558 | 6.6582 | 7.2149 | 4.9324 | 6.3649 | 4.628 | 6.6421 | 8.0008 | 42.4619 | 46.4716 | 43.0132 | 14.8638 |  |  | 0.1461 | -0.036709 | -0.033632 | -0.16034 | 0.1053 | 0.18879 | 0.53085 | 0.12206 | -0.17921 | -1.2833 | -0.38718 | 8.8714 | 8.8724 | 2.0081 | 15.6557 | 16.5776 | 17.1393 | 17.4905 | 17.4579 | 16.4467 | 14.7993 | 16.8105 | 17.1551 | 17.4665 | 17.5238 | 17.263 | 16.4686 | 14.6933 | 6.038 | 8.1434 | 5.2797 | 5.6889 | 5.8095 | 6.6361 | 7.6619 | 15.6905 | 15.3361 | 15.2233 | 14.1752 | 14.0747 | 14.0289 |  |  |  | 10.7486 | 16.0019 | 11.1889 | 9.7394 | 0.015041 | 0.14757 | 12.8597 |  |  | 10.561 |  |  | 16.8631 | 16.0436 | 15.0031 | 16.3652 | 15.6393 | 14.7509 | 11.7404 | 14.0754 | 11.6188 | 11.7014 | 9.6217 |  | 10.5936 | 8.56 | 10.0182 | 9.8925 | 11.1119 | 13.8164 |  | 12.2558 |  |  | 11.7898 | 12.5236 | 12.5363 | [6 empty] | 12.752 |  |  | 12.1563 |  |  | 9.765 | 10.8175 | 25.0571 | 7.711 | 9.5202 | 14.2165 | 8.1123 | 9.9758 | 16.3168 | 9.5806 | 10.7051 | 7.9766 | 10.8116 | 8.5443 | 10.6286 | 8.1084 | 10.2185 | 13.6431 | 10.8604 | 10.6667 | 19.1885 | 8.4418 | 10.1607 | 15.933 | 8.4414 | 11.1107 | 9.9086 | 10.4692 | 8.6284 | 11.4393 | -0.20763 | 20.9545 | 0.03603 | 0.049123 | -37.7494 | 3.1199 | 12.85 | 43.18 | 0.45612 | -0.22322 | -0.21366 | -0.46651 | 0.37829 | 0.50651 | 0.84934 | 0.39452 | 0.40506 | 0.40409 | 0.4139 | 0.61726 | 0.38605 | 0.39636
42810.4402 | 17 | 18.4327 | 18.5236 | 18.5278 | 18.546 | 17.8829 | 16.5175 | 14.5793 | 16.6679 | 17.164 | 17.2507 | 17.2679 | 16.8024 | 15.8319 | 14.4629 | 14.8203 | 14.8271 | 15.3944 | 13.2769 | 13.3948 | 13.9679 |  |  |  | 16.5554 | 15.8937 | 14.9792 | 12.92 | 14.9258 | 20.7657 | 17.1063 | 16.2302 | 15.0383 | 16.7933 | 16.0696 | 15.0722 | 10.8432 | 25.6618 |  | 12.365 | 11.7426 | 12.5531 | 10.1609 |  | 6.2531 | 6.3288 | 5.9756 | 6.0923 | 6.3487 | 6.649 | 7.2781 | 5.0496 | 6.3744 | 4.6153 | 6.6434 | 8.0077 | 42.4705 | 46.4589 | 43.0123 | 14.8539 |  |  | -0.10886 | 0.016515 | -0.03232 | -0.45473 | -0.011664 | 0.53838 | 0.36657 | 0.11089 | -0.44192 | -0.54439 | -0.3073 | 8.8698 | 8.8708 | 2.008 | 15.6713 | 16.586 | 17.1557 | 17.4999 | 17.4685 | 16.4565 | 14.8103 | 16.821 | 17.1696 | 17.4791 | 17.5346 | 17.2722 | 16.4754 | 14.7099 | 5.9781 | 8.1413 | 5.2279 | 5.7228 | 5.7963 | 6.638 | 7.6599 | 15.6906 | 15.3325 | 15.2189 | 14.1778 | 14.0781 | 14.0369 |  |  |  | 10.762 | 16.6081 | 11.4732 | 9.7681 | -0.0029902 | 0.13139 | 12.8516 |  |  | 10.5657 |  |  | 16.8656 | 16.0602 | 15.005 | 16.3576 | 15.6436 | 14.7512 | 11.7677 | 14.2754 | 11.6799 | 11.748 | 9.6168 |  | 10.6002 | 8.3349 | 10.0258 | 9.9156 | 11.1232 | 14.4594 |  | 12.2786 |  |  | 11.7903 | 12.5229 | 12.5391 | [6 empty] | 12.7732 |  |  | 12.2051 |  |  | 9.7771 | 10.8424 | 25.9282 | 7.7426 | 9.5164 | 14.5258 | 8.1181 | 9.9822 | 16.7091 | 9.6035 | 10.7278 | 7.9804 | 10.8417 | 8.5451 | 10.639 | 8.1093 | 10.2495 | 13.9185 | 10.8627 | 10.6813 | 19.8118 | 8.44 | 10.1493 | 16.3196 | 8.4622 | 11.1977 | 9.9295 | 10.5281 | 8.6308 | 11.5405 | -0.078593 | 20.953 | 0.036299 | 0.048826 | -37.7584 | 3.1199 | 4.46 | 41.81 | -0.3942 | 0.14972 | -0.20945 | -0.78563 | -0.1259 | 0.85533 | 0.70578 | 0.39488 | 0.41156 | 0.40382 | 0.42077 | 0.62278 | 0.38777 | 0.39601
42810.4402 | 18 | 18.4438 | 18.5373 | 18.5446 | 18.5633 | 17.9006 | 16.5249 | 14.5863 | 16.675 | 17.1704 | 17.2657 | 17.2706 | 16.8199 | 15.8475 | 14.4735 | 14.8314 | 14.8263 | 15.3957 | 13.2812 | 13.4003 | 13.9725 |  |  |  | 16.5565 | 15.8925 | 14.9861 | 13.1925 | 15.3093 | 21.1064 | 17.1082 | 16.2257 | 15.041 | 16.7935 | 16.0773 | 15.0715 | 10.8516 | 26.5382 |  | 12.4389 | 11.8283 | 12.7195 | 10.178 |  | 6.2631 | 6.3232 | 5.9652 | 6.0937 | 6.3406 | 6.6914 | 7.4996 | 5.1998 | 6.3702 | 4.6693 | 6.6425 | 8.0056 | 42.485 | 46.4447 | 43.0232 | 14.844 |  |  | 0.000219 | -0.23385 | 0.20884 | -0.21159 | -0.060948 | 0.38855 | 0.50128 | 0.18514 | -0.50536 | 0.011157 | -0.56402 | 8.867 | 8.8679 | 2.0082 | 15.6729 | 16.5898 | 17.1555 | 17.4973 | 17.4622 | 16.4473 | 14.8084 | 16.8162 | 17.1647 | 17.4779 | 17.5292 | 17.2737 | 16.4752 | 14.7062 | 5.9267 | 8.1318 | 5.1864 | 5.7292 | 5.8261 | 6.632 | 7.6563 | 15.6927 | 15.3408 | 15.2289 | 14.1776 | 14.0863 | 14.0328 |  |  |  | 10.7622 | 17.2195 | 11.6516 | 9.8162 | -0.20984 | 0.057614 | 12.7944 |  |  | 10.5906 |  |  | 16.8516 | 16.052 | 14.9976 | 16.356 | 15.641 | 14.7502 | 11.7309 | 14.3705 | 11.797 | 11.8809 | 9.6287 |  | 10.5988 | 8.1454 | 10.027 | 9.9416 | 11.1306 | 15.2447 |  | 12.3027 |  |  | 11.8002 | 12.5162 | 12.5413 | [6 empty] | 12.7987 |  |  | 12.2363 |  |  | 9.7864 | 10.8546 | 26.7031 | 7.7658 | 9.5106 | 14.7893 | 8.1277 | 9.9861 | 17.0676 | 9.614 | 10.7595 | 7.9934 | 10.8621 | 8.55 | 10.6684 | 8.127 | 10.294 | 14.3123 | 10.8839 | 10.7036 | 20.5182 | 8.4507 | 10.1663 | 16.64 | 8.4858 | 11.2652 | 9.9418 | 10.5758 | 8.6365 | 11.5824 | -0.19165 | 20.953 | 0.035588 | 0.047885 | -37.7723 | 3.1199 | 5 | 41.75 | 0.017691 | -0.56338 | 0.53241 | -0.5359 | -0.28781 | 0.72669 | 0.8254 | 0.3945 | 0.41687 | 0.40334 | 0.42579 | 0.62697 | 0.38757 | 0.39468
42810.4403 | 19 | 18.4359 | 18.5318 | 18.5391 | 18.5572 | 17.8945 | 16.5163 | 14.5799 | 16.6631 | 17.1651 | 17.2592 | 17.2712 | 16.8128 | 15.8349 | 14.4604 | 14.83 | 14.8281 | 15.393 | 13.2766 | 13.3968 | 13.9647 |  |  |  | 16.5522 | 15.8884 | 14.9855 | 13.4035 | 15.6934 | 21.5181 | 17.1077 | 16.2274 | 15.0346 | 16.7993 | 16.0833 | 15.07 | 10.8527 | 27.2735 |  | 12.5172 | 11.9752 | 12.9983 | 10.1804 |  | 6.2637 | 6.3234 | 5.9665 | 6.0873 | 6.3442 | 6.7246 | 7.7713 | 5.3602 | 6.368 | 4.7308 | 6.6352 | 8.0063 | 42.5019 | 46.4174 | 43.0299 | 14.8413 |  |  | 0.055415 | -0.13857 | 0.16416 | 0.069654 | -0.18908 | 0.11585 | 0.56896 | 0.027436 | -0.11636 | -0.4588 | -0.1692 | 8.8698 | 8.8711 | 2.0082 | 15.6638 | 16.5825 | 17.1479 | 17.4962 | 17.4654 | 16.445 | 14.8026 | 16.8198 | 17.1581 | 17.4689 | 17.524 | 17.2605 | 16.4684 | 14.7044 | 5.8917 | 8.1117 | 5.1736 | 5.7015 | 5.8394 | 6.6322 | 7.6588 | 15.6967 | 15.3342 | 15.2203 | 14.1805 | 14.0809 | 14.0343 |  |  |  | 10.7671 | 18.0191 | 11.9455 | 9.8723 | -0.13043 | 0.15435 | 12.782 |  |  | 10.5474 |  |  | 16.8551 | 16.0581 | 15.0011 | 16.3625 | 15.6372 | 14.7414 | 11.7893 | 14.8774 | 11.9426 | 12.0997 | 9.4637 |  | 10.5963 | 7.9939 | 10.0092 | 9.9487 | 11.1428 | 15.9082 |  | 12.3361 |  |  | 11.7866 | 12.5141 | 12.5387 | [6 empty] | 12.8375 |  |  | 12.2597 |  |  | 9.788 | 10.8653 | 27.4154 | 7.7866 | 9.4876 | 15.135 | 8.124 | 9.9828 | 17.4017 | 9.6285 | 10.8079 | 8.0216 | 10.8798 | 8.5499 | 10.7658 | 8.1379 | 10.3161 | 14.6757 | 10.8942 | 10.7026 | 20.9397 | 8.4456 | 10.1563 | 17.0022 | 8.5025 | 11.3351 | 9.9497 | 10.5834 | 8.6287 | 11.5842 | -0.33263 | 20.9531 | 0.034893 | 0.046083 | -37.7829 | 3.1198 | 2.9 | 42.95 | 0.28161 | -0.43367 | 0.47203 | 0.30748 | -0.50696 | 0.39682 | 0.87941 | 0.399 | 0.42049 | 0.40355 | 0.4297 | 0.62868 | 0.38754 | 0.39328
42810.4403 | 20 | 18.4362 | 18.5359 | 18.5366 | 18.5545 | 17.8907 | 16.5164 | 14.5793 | 16.6683 | 17.1617 | 17.2591 | 17.2738 | 16.8115 | 15.836 | 14.4597 | 14.8298 | 14.8371 | 15.4085 | 13.2801 | 13.4 | 13.9788 |  |  |  | 16.5571 | 15.8923 | 14.9883 | 13.6811 | 16.0825 | 22.8995 | 17.1156 | 16.232 | 15.0377 | 16.8024 | 16.0793 | 15.0728 | 10.8588 | 27.9641 |  | 12.5975 | 12.17 | 13.3517 | 10.1411 |  | 6.2603 | 6.3211 | 5.964 | 6.0998 | 6.4315 | 6.7276 | 8.0042 | 5.4537 | 6.3789 | 4.8042 | 6.6421 | 8.0118 | 42.5211 | 46.4098 | 43.0269 | 14.8278 |  |  | 0.079075 | -0.053797 | 0.015648 | -0.18136 | -0.077376 | 0.13425 | 0.64782 | 0.16083 | -1.058 | 0.040948 | -0.40943 | 8.8688 | 8.8702 | 2.0082 | 15.6651 | 16.581 | 17.14 | 17.4896 | 17.4592 | 16.4409 | 14.8008 | 16.8137 | 17.1648 | 17.4696 | 17.5208 | 17.2661 | 16.4648 | 14.6964 | 5.8968 | 8.098 | 5.1778 | 5.6941 | 5.8227 | 6.6303 | 7.6567 | 15.6936 | 15.3418 | 15.2303 | 14.1804 | 14.078 | 14.0314 |  |  |  | 10.7745 | 18.6528 | 11.9692 | 9.8943 | -0.011499 | 0.01621 | 12.7749 |  |  | 10.5463 |  |  | 16.8613 | 16.0505 | 14.998 | 16.3604 | 15.6322 | 14.7413 | 12.0037 | 15.1712 | 12.1228 | 12.2854 | 9.2945 |  | 10.5971 | 7.9045 | 10.0114 | 9.9664 | 11.1514 | 16.3892 |  | 12.3605 |  |  | 11.762 | 12.4727 | 12.5288 | [6 empty] | 12.8572 |  |  | 12.2863 |  |  | 9.7987 | 10.8835 | 28.334 | 7.8124 | 9.5067 | 15.4945 | 8.121 | 9.9896 | 17.8779 | 9.6444 | 10.8658 | 8.0457 | 10.8906 | 8.5318 | 10.8928 | 8.1512 | 10.3525 | 14.9578 | 10.9063 | 10.7126 | 21.363 | 8.4515 | 10.174 | 17.3699 | 8.5177 | 11.4027 | 9.9649 | 10.5876 | 8.6317 | 11.6051 | 0.034463 | 20.9524 | 0.034004 | 0.047379 | -37.7924 | 3.1198 | 8.72 | 41.89 | 0.33719 | -0.27022 | 0.14574 | -0.49614 | -0.32431 | 0.42717 | 0.93838 | 0.40373 | 0.42304 | 0.40334 | 0.42892 | 0.62798 | 0.38884 | 0.39291
42810.4403 | 21 | 18.4427 | 18.5326 | 18.5341 | 18.552 | 17.8885 | 16.5186 | 14.5802 | 16.6739 | 17.1686 | 17.2581 | 17.2724 | 16.8072 | 15.8315 | 14.4624 | 14.8439 | 14.8465 | 15.4087 | 13.2895 | 13.4158 | 13.9834 |  |  |  | 16.5646 | 15.8993 | 14.9941 | 14.034 | 16.4827 | 24.0776 | 17.1116 | 16.2339 | 15.0371 | 16.7941 | 16.0802 | 15.0706 | 10.8591 | 28.6882 |  | 12.6681 | 12.3858 | 13.7366 | 10.0672 |  | 6.274 | 6.3288 | 5.9658 | 6.1271 | 6.4919 | 6.7389 | 8.1134 | 5.4383 | 6.3867 | 4.8442 | 6.6438 | 8.0138 | 42.5382 | 46.4064 | 43.0282 | 14.8208 |  |  | 0.010735 | -0.032109 | 0.11422 | -0.10054 | -0.16674 | 0.20193 | 0.59393 | 0.13914 | -1.1433 | -0.2148 | -0.25365 | 8.8684 | 8.8695 | 2.0078 | 15.6734 | 16.5816 | 17.1456 | 17.4878 | 17.4695 | 16.4472 | 14.802 | 16.8189 | 17.1628 | 17.473 | 17.5215 | 17.2675 | 16.4757 | 14.6997 | 5.9286 | 8.1276 | 5.2098 | 5.6884 | 5.785 | 6.6297 | 7.6542 | 15.7021 | 15.343 | 15.2397 | 14.1882 | 14.0869 | 14.0358 |  |  |  | 10.7844 | 18.9788 | 11.9487 | 9.9289 | -0.011499 | 0.019221 | 12.7939 |  |  | 10.5544 |  |  | 16.8645 | 16.0566 | 15.0064 | 16.3712 | 15.6478 | 14.7597 | 12.1958 | 15.4432 | 12.3109 | 12.4595 | 9.2068 |  | 10.6058 | 7.8737 | 10.011 | 9.9789 | 11.1663 | 16.9298 |  | 12.3785 |  |  | 11.7205 | 12.4207 | 12.5159 | [6 empty] | 12.8564 |  |  | 12.3026 |  |  | 9.8112 | 10.903 | 28.8775 | 7.8167 | 9.519 | 15.8296 | 8.1284 | 10.007 | 18.3278 | 9.6667 | 10.9018 | 8.0459 | 10.9298 | 8.5212 | 10.9953 | 8.1558 | 10.3656 | 15.1994 | 10.9127 | 10.7231 | 21.784 | 8.4483 | 10.179 | 17.6778 | 8.5252 | 11.4358 | 9.9774 | 10.5786 | 8.629 | 11.6443 | 0.028107 | 20.9513 | 0.035662 | 0.04659 | -37.7198 | 3.1198 | 24.84 | 43.38 | 0.12448 | -0.20876 | 0.39374 | -0.36941 | -0.47609 | 0.52392 | 0.89852 | 0.40645 | 0.42389 | 0.40349 | 0.42532 | 0.62413 | 0.3909 | 0.39228
42810.4403 | 22 | 18.4389 | 18.5331 | 18.539 | 18.5478 | 17.8911 | 16.5183 | 14.579 | 16.6668 | 17.1633 | 17.2506 | 17.2678 | 16.8085 | 15.8373 | 14.4597 | 14.8406 | 14.8432 | 15.4049 | 13.2855 | 13.4106 | 13.9739 |  |  |  | 16.5606 | 15.8914 | 14.9895 | 14.3496 | 16.8675 | 24.9318 | 17.1236 | 16.2416 | 15.0422 | 16.797 | 16.0809 | 15.0747 | 10.8683 | 29.2823 |  | 12.7321 | 12.6137 | 14.0967 | 10.0157 |  | 6.272 | 6.3497 | 5.9777 | 6.1619 | 6.5597 | 6.822 | 8.3625 | 5.3814 | 6.385 | 4.95 | 6.6408 | 8.0149 | 42.56 | 46.4081 | 43.0139 | 14.8134 |  |  | 0.005475 | -0.19705 | 0.18847 | 0.17677 | 0.01002 | 0.44901 | 0.69973 | 0.069492 | -0.28371 | -0.98539 | -0.29756 | 8.871 | 8.872 | 2.008 | 15.6669 | 16.5795 | 17.1414 | 17.4823 | 17.4616 | 16.4415 | 14.7966 | 16.814 | 17.1604 | 17.4639 | 17.5233 | 17.2609 | 16.4578 | 14.6948 | 6.0475 | 8.1491 | 5.269 | 5.6682 | 5.7691 | 6.6362 | 7.6652 | 15.7012 | 15.3469 | 15.2289 | 14.1825 | 14.0845 | 14.0278 |  |  |  | 10.7879 | 19.0992 | 11.9675 | 9.9397 | 0.033883 | 0.089984 | 12.7833 |  |  | 10.5292 |  |  | 16.8496 | 16.0509 | 14.9897 | 16.354 | 15.6327 | 14.7367 | 12.448 | 15.6459 | 12.467 | 12.6298 | 9.1405 |  | 10.606 | 7.8846 | 10.0151 | 9.9949 | 11.1755 | 17.5284 |  | 12.4198 |  |  | 11.674 | 12.3957 | 12.4844 | [6 empty] | 12.8289 |  |  | 12.328 |  |  | 9.8192 | 10.9157 | 29.3664 | 7.8056 | 9.5351 | 16.1693 | 8.1175 | 10.0099 | 18.7817 | 9.6905 | 10.9292 | 8.0322 | 11.0174 | 8.5125 | 11.0334 | 8.1692 | 10.3832 | 15.4343 | 10.9155 | 10.7273 | 22.174 | 8.4531 | 10.1885 | 17.9582 | 8.5321 | 11.4565 | 9.9924 | 10.5707 | 8.6289 | 11.6535 | -0.16314 | 20.9525 | 0.036162 | 0.048073 | -37.8286 | 3.1198 | 9.91 | 49.57 | 0.089028 | -0.51718 | 0.5058 | 0.48984 | 0.11672 | 0.78136 | 0.97541 | 0.4083 | 0.42372 | 0.40335 | 0.41286 | 0.61883 | 0.39263 | 0.39209
42810.4403 | 23 | 18.4491 | 18.5446 | 18.541 | 18.5578 | 17.8928 | 16.5228 | 14.5877 | 16.6736 | 17.1731 | 17.2621 | 17.2738 | 16.8168 | 15.8488 | 14.4746 | 14.8353 | 14.8404 | 15.4025 | 13.2804 | 13.4033 | 13.9685 |  |  |  | 16.5591 | 15.889 | 14.9816 | 14.6325 | 17.1831 | 25.1 | 17.1313 | 16.2435 | 15.0403 | 16.8001 | 16.089 | 15.0798 | 10.8693 | 30.2111 |  | 12.7932 | 12.8596 | 14.363 | 9.9845 |  | 6.2736 | 6.3744 | 5.9987 | 6.2089 | 6.6477 | 6.9914 | 8.6248 | 5.2747 | 6.3961 | 5.0669 | 6.6521 | 8.0212 | 42.5902 | 46.4155 | 43.0041 | 14.8144 |  |  | 0.000875 | 0.16371 | 0.020248 | -0.35813 | -0.14046 | 0.42732 | 0.60576 | 0.013636 | -0.12336 | 0.65105 | -0.23736 | 8.8688 | 8.8699 | 2.0081 | 15.67 | 16.5803 | 17.1485 | 17.4801 | 17.4637 | 16.4486 | 14.803 | 16.8153 | 17.1609 | 17.4659 | 17.5215 | 17.2574 | 16.4662 | 14.6935 | 6.1549 | 8.1574 | 5.4161 | 5.6729 | 5.7558 | 6.6374 | 7.6654 | 15.7075 | 15.3532 | 15.2341 | 14.1931 | 14.0889 | 14.037 |  |  |  | 10.7987 | 19.3159 | 12.152 | 9.9611 | 0.095271 | 0.11596 | 12.7885 |  |  | 10.5511 |  |  | 16.8701 | 16.0658 | 15.0124 | 16.3653 | 15.6501 | 14.76 | 12.8012 | 16.0555 | 12.6474 | 12.8703 | 9.1214 |  | 10.6108 | 7.976 | 10.0127 | 10.0358 | 11.1892 | 18.0686 |  | 12.4471 |  |  | 11.646 | 12.3778 | 12.4659 | [6 empty] | 12.8212 |  |  | 12.3565 |  |  | 9.8178 | 10.9299 | 29.9529 | 7.8065 | 9.5552 | 16.5165 | 8.1105 | 10.0047 | 19.195 | 9.6999 | 10.9485 | 8.0375 | 11.1406 | 8.5047 | 11.0517 | 8.1758 | 10.4063 | 15.6667 | 10.9259 | 10.7378 | 22.5475 | 8.4569 | 10.2014 | 18.2887 | 8.5336 | 11.4824 | 10.0088 | 10.5754 | 8.6259 | 11.6485 | -0.13714 | 20.9516 | 0.0365 | 0.048211 | -37.7871 | 3.1198 | 10.07 | 48.75 | 0.035601 | 0.47143 | 0.16579 | -0.69726 | -0.43715 | 0.76249 | 0.90783 | 0.40899 | 0.4211 | 0.40266 | 0.40107 | 0.60251 | 0.39353 | 0.39186
42810.4403 | 24 | 18.4505 | 18.5537 | 18.5409 | 18.5726 | 17.8999 | 16.5281 | 14.5905 | 16.6777 | 17.1752 | 17.2737 | 17.2838 | 16.817 | 15.8468 | 14.4745 | 14.8384 | 14.8404 | 15.4039 | 13.2793 | 13.4003 | 13.9723 |  |  |  | 16.5589 | 15.8886 | 14.9833 | 14.8767 | 17.5185 | 25.4672 | 17.1305 | 16.2458 | 15.0448 | 16.8032 | 16.0808 | 15.0816 | 10.8774 | 31.7096 |  | 12.8929 | 13.1444 | 14.7233 | 9.9176 |  | 6.2749 | 6.381 | 6.0048 | 6.2418 | 6.6958 | 7.0454 | 8.7559 | 5.0977 | 6.3989 | 5.1034 | 6.6468 | 8.0179 | 42.6063 | 46.4329 | 42.9901 | 14.8003 |  |  | 0.047531 | 0.037543 | 0.11093 | -0.040082 | 0.00542 | 0.24136 | 0.74376 | 0.22654 | -0.30414 | -0.35452 | -0.48811 | 8.8695 | 8.8709 | 2.0077 | 15.6678 | 16.5811 | 17.1456 | 17.4806 | 17.4617 | 16.4406 | 14.7982 | 16.8123 | 17.1581 | 17.4655 | 17.5228 | 17.2579 | 16.4613 | 14.6906 | 6.2898 | 8.1951 | 5.516 | 5.7248 | 5.7497 | 6.6412 | 7.6649 | 15.7084 | 15.3444 | 15.2296 | 14.1817 | 14.0873 | 14.0347 |  |  |  | 10.7879 | 19.6718 | 12.2657 | 9.9717 | 0.10256 | -0.13586 | 12.7811 |  |  | 10.5431 |  |  | 16.8524 | 16.0484 | 15.0009 | 16.3655 | 15.6414 | 14.744 | 13.1008 | 16.7326 | 12.82 | 13.0927 | 9.0973 |  | 10.6156 | 8.0273 | 10.0191 | 10.0652 | 11.1994 | 18.569 |  | 12.4778 |  |  | 11.6329 | 12.3539 | 12.4694 | [6 empty] | 12.834 |  |  | 12.4142 |  |  | 9.8145 | 10.944 | 30.6309 | 7.8106 | 9.5809 | 16.8368 | 8.1166 | 10.0093 | 19.6973 | 9.7149 | 10.9598 | 8.062 | 11.2531 | 8.509 | 11.0669 | 8.1831 | 10.4207 | 15.9433 | 10.9458 | 10.7363 | 22.8928 | 8.4467 | 10.2112 | 18.7201 | 8.543 | 11.4968 | 10.0079 | 10.579 | 8.6234 | 11.6543 | -0.20686 | 20.9527 | 0.036299 | 0.048703 | -37.8564 | 3.1198 | 11.96 | 49.76 | 0.26255 | 0.22576 | 0.38807 | -0.23327 | 0.085881 | 0.5731 | 1.006 | 0.40982 | 0.41989 | 0.40218 | 0.38651 | 0.59135 | 0.39566 | 0.39121
42810.4403 | 25 | 18.4451 | 18.5278 | 18.5375 | 18.5472 | 17.8844 | 16.5154 | 14.5689 | 16.6596 | 17.1551 | 17.2573 | 17.2624 | 16.8047 | 15.8383 | 14.4735 | 14.8422 | 14.8392 | 15.4046 | 13.2799 | 13.4024 | 13.9724 |  |  |  | 16.5519 | 15.8815 | 14.9841 | 15.2037 | 17.892 | 26.4242 | 17.1231 | 16.2426 | 15.0324 | 16.8061 | 16.0825 | 15.0768 | 10.8845 | 33.6059 |  | 12.9882 | 13.407 | 15.1396 | 9.8519 |  | 6.2835 | 6.3786 | 6.0268 | 6.332 | 6.7719 | 7.0622 | 8.9538 | 5.0182 | 6.3987 | 4.9588 | 6.6521 | 8.0145 | 42.6342 | 46.4448 | 42.9743 | 14.7862 |  |  | 0.038987 | -0.060365 | 0.1543 | -0.47838 | -0.053064 | 0.35438 | 0.43688 | 0.074092 | 0.078634 | -0.29096 | -0.20854 | 8.8706 | 8.8722 | 2.0077 | 15.6608 | 16.5807 | 17.1416 | 17.4833 | 17.4601 | 16.4327 | 14.7968 | 16.8063 | 17.1525 | 17.4571 | 17.5191 | 17.2539 | 16.4585 | 14.6925 | 6.6543 | 8.2749 | 5.5884 | 5.7142 | 5.8105 | 6.6523 | 7.6617 | 15.703 | 15.3399 | 15.2269 | 14.1725 | 14.0827 | 14.0359 |  |  |  | 10.8024 | 20.1758 | 12.364 | 9.9348 | -0.05364 | -0.11722 | 12.7993 |  |  | 10.566 |  |  | 16.8685 | 16.0676 | 15.0078 | 16.3763 | 15.6555 | 14.7541 | 13.4519 | 17.1742 | 13.0505 | 13.315 | 9.1157 |  | 10.5996 | 8.1765 | 10.0119 | 10.1017 | 11.207 | 19.3902 |  | 12.522 |  |  | 11.6483 | 12.3558 | 12.4652 | [6 empty] | 12.8408 |  |  | 12.4701 |  |  | 9.816 | 10.9555 | 31.1888 | 7.8145 | 9.6099 | 17.1569 | 8.1147 | 10.0242 | 20.1881 | 9.7286 | 10.9696 | 8.0847 | 11.3477 | 8.495 | 11.0848 | 8.2025 | 10.4373 | 16.2637 | 10.9651 | 10.7486 | 23.3971 | 8.4445 | 10.2239 | 19.1351 | 8.5614 | 11.5263 | 10.012 | 10.5839 | 8.6369 | 11.6751 | -0.15621 | 20.9524 | 0.036913 | 0.048486 | -37.6962 | 3.1198 | 6.07 | 48.93 | 0.23817 | -0.28627 | 0.45768 | -0.80587 | -0.26873 | 0.69446 | 0.77107 | 0.40878 | 0.41551 | 0.40142 | 0.3473 | 0.58294 | 0.39772 | 0.39271
42810.4403 | 26 | 18.4447 | 18.5312 | 18.5299 | 18.5453 | 17.8826 | 16.5156 | 14.5756 | 16.6608 | 17.1568 | 17.2551 | 17.2637 | 16.8003 | 15.8382 | 14.4605 | 14.8461 | 14.8334 | 15.4059 | 13.2827 | 13.4041 | 13.9665 |  |  |  | 16.5477 | 15.882 | 14.9807 | 15.63 | 18.2625 | 27.6827 | 17.1361 | 16.2464 | 15.0435 | 16.806 | 16.0816 | 15.0781 | 10.885 | 34.2356 |  | 13.0888 | 13.6892 | 15.5544 | 9.8078 |  | 6.2745 | 6.3859 | 6.0744 | 6.3864 | 6.7918 | 7.1615 | 9.1734 | 4.9994 | 6.3993 | 4.8196 | 6.6504 | 8.0215 | 42.6447 | 46.465 | 42.972 | 14.7831 |  |  | 0.013363 | -0.048537 | -0.06452 | -0.69063 | 0.048132 | 0.50683 | 0.62679 | 0.17463 | -0.62154 | -0.82448 | -0.25107 | 8.8688 | 8.8699 | 2.0078 | 15.6736 | 16.5812 | 17.1547 | 17.489 | 17.4639 | 16.4413 | 14.8051 | 16.8136 | 17.1658 | 17.4673 | 17.5262 | 17.2633 | 16.4607 | 14.6953 | 7.3434 | 8.5066 | 5.8123 | 5.7348 | 5.8584 | 6.6578 | 7.6669 | 15.7047 | 15.3402 | 15.2254 | 14.1796 | 14.079 | 14.038 |  |  |  | 10.8132 | 20.5364 | 12.4312 | 9.8832 | -0.073698 | -0.19344 | 12.7904 |  |  | 10.564 |  |  | 16.8616 | 16.0587 | 15.0099 | 16.3671 | 15.6466 | 14.7492 | 13.714 | 17.5937 | 13.2818 | 13.5303 | 9.1496 |  | 10.6031 | 8.4308 | 10.0141 | 10.1491 | 11.2144 | 19.8283 |  | 12.5533 |  |  | 11.6535 | 12.368 | 12.4529 | [6 empty] | 12.8502 |  |  | 12.4919 |  |  | 9.8202 | 10.9752 | 32.0101 | 7.8256 | 9.6393 | 17.4802 | 8.1089 | 10.0331 | 20.6117 | 9.7444 | 10.9936 | 8.1026 | 11.4173 | 8.4843 | 11.128 | 8.2173 | 10.4523 | 16.5901 | 10.9728 | 10.75 | 24.0111 | 8.4369 | 10.2254 | 19.5132 | 8.5612 | 11.5763 | 10.0135 | 10.579 | 8.6419 | 11.667 | 0.041975 | 20.9523 | 0.036615 | 0.048971 | -37.6533 | 3.1198 | 11.21 | 48.92 | 0.13973 | -0.2567 | -0.29596 | -0.9683 | 0.25598 | 0.83065 | 0.92374 | 0.40795 | 0.40851 | 0.40034 | 0.27138 | 0.55866 | 0.39896 | 0.3945
42810.4403 | 27 | 18.457 | 18.5416 | 18.5361 | 18.5476 | 17.8918 | 16.5243 | 14.5775 | 16.6659 | 17.1639 | 17.2603 | 17.2726 | 16.8062 | 15.8483 | 14.4659 | 14.849 | 14.8413 | 15.4123 | 13.2836 | 13.4003 | 13.9688 |  |  |  | 16.5532 | 15.8958 | 14.9877 | 16.0718 | 18.6547 | 28.7721 | 17.1383 | 16.2476 | 15.0471 | 16.8056 | 16.0809 | 15.0794 | 10.8912 | 34.6098 |  | 13.183 | 13.977 | 15.9348 | 9.7854 |  | 6.279 | 6.3788 | 6.091 | 6.4067 | 6.8443 | 7.2812 | 9.3289 | 5.004 | 6.4018 | 4.7357 | 6.6528 | 8.0336 | 42.6557 | 46.4805 | 42.9743 | 14.7802 |  |  | 0.13033 | -0.2299 | -0.35168 | -0.50664 | 0.031704 | 0.38395 | 0.37708 | -0.09216 | -0.20217 | -0.33711 | -0.17457 | 8.8719 | 8.873 | 2.008 | 15.6745 | 16.5789 | 17.1457 | 17.4839 | 17.4562 | 16.4395 | 14.7979 | 16.8036 | 17.1577 | 17.4592 | 17.5193 | 17.2535 | 16.4626 | 14.6863 | 7.5367 | 8.6217 | 6.0413 | 5.8592 | 5.8224 | 6.6654 | 7.6666 | 15.7196 | 15.3495 | 15.2304 | 14.186 | 14.0864 | 14.0426 |  |  |  | 10.8285 | 21.0258 | 12.7068 | 9.8575 | -0.07309 | -0.19664 | 12.8004 |  |  | 10.5663 |  |  | 16.8559 | 16.0552 | 15.0035 | 16.3679 | 15.6464 | 14.7449 | 13.9528 | 18.1145 | 13.5133 | 13.7666 | 9.1632 |  | 10.6039 | 8.95 | 10.0229 | 10.1977 | 11.2297 | 20.2169 |  | 12.5858 |  |  | 11.676 | 12.3793 | 12.4416 | [6 empty] | 12.878 |  |  | 12.5418 |  |  | 9.81 | 10.9877 | 32.6185 | 7.8204 | 9.6661 | 17.8053 | 8.1005 | 10.0327 | 20.9925 | 9.7578 | 11.0075 | 8.1118 | 11.4653 | 8.4822 | 11.185 | 8.241 | 10.471 | 16.9314 | 10.9893 | 10.7672 | 24.5856 | 8.4381 | 10.2344 | 19.8941 | 8.5593 | 11.6314 | 10.0293 | 10.5821 | 8.6542 | 11.655 | -0.0061754 | 20.9527 | 0.036311 | 0.050035 | -37.7027 | 3.1198 | 19.29 | 50.03 | 0.43715 | -0.55866 | -0.69096 | -0.82933 | 0.2078 | 0.72313 | 0.71664 | 0.4076 | 0.39438 | 0.3995 | 0.25078 | 0.53319 | 0.39979 | 0.39571
42810.4404 | 28 | 18.462 | 18.5401 | 18.542 | 18.5516 | 17.8869 | 16.5206 | 14.5763 | 16.6684 | 17.1653 | 17.2587 | 17.2687 | 16.8056 | 15.8468 | 14.4684 | 14.8536 | 14.8424 | 15.4005 | 13.2816 | 13.3992 | 13.9706 |  |  |  | 16.5522 | 15.8902 | 14.9821 | 16.423 | 19.1069 | 29.0075 | 17.1358 | 16.2472 | 15.0448 | 16.8023 | 16.0849 | 15.0776 | 10.8949 | 35.1197 |  | 13.2852 | 14.2386 | 16.2697 | 9.7743 |  | 6.2705 | 6.3754 | 6.0647 | 6.407 | 6.87 | 7.2807 | 9.4436 | 4.9048 | 6.3932 | 4.6483 | 6.6531 | 8.0278 | 42.6528 | 46.4839 | 42.9654 | 14.7709 |  |  | -0.059577 | -0.27459 | -0.15586 | -0.21816 | -0.032036 | -0.20482 | 0.25946 | 0.17792 | -0.40359 | -0.49257 | -0.40426 | 8.8673 | 8.8684 | 2.0078 | 15.6817 | 16.5912 | 17.1473 | 17.5036 | 17.4741 | 16.4513 | 14.7991 | 16.8154 | 17.1655 | 17.4762 | 17.5245 | 17.267 | 16.4647 | 14.706 | 7.506 | 8.568 | 6.1065 | 6.0057 | 5.8915 | 6.6709 | 7.6749 | 15.7204 | 15.3464 | 15.2361 | 14.1876 | 14.0846 | 14.0373 |  |  |  | 10.8225 | 21.4686 | 12.866 | 9.8793 | 0.019701 | -0.15185 | 12.823 |  |  | 10.5677 |  |  | 16.8612 | 16.0499 | 15.0096 | 16.3631 | 15.6503 | 14.7464 | 14.2462 | 18.3893 | 13.6992 | 13.963 | 9.232 |  | 10.6058 | 9.7485 | 10.0469 | 10.2395 | 11.2464 | 20.9465 |  | 12.6327 |  |  | 11.7167 | 12.386 | 12.4536 | [6 empty] | 12.895 |  |  | 12.5916 |  |  | 9.8256 | 11.0169 | 33.5822 | 7.8261 | 9.728 | 18.2566 | 8.1215 | 10.0462 | 21.4529 | 9.7949 | 11.0401 | 8.1309 | 11.5883 | 8.4805 | 11.2414 | 8.2149 | 10.4826 | 17.3047 | 10.9913 | 10.7685 | 24.9623 | 8.4343 | 10.24 | 20.2287 | 8.5408 | 11.703 | 10.0299 | 10.5903 | 8.6494 | 11.6476 | -0.071082 | 20.9521 | 0.035783 | 0.050389 | -37.7039 | 3.1198 | 4.28 | 48.88 | -0.29568 | -0.61054 | -0.45998 | -0.54421 | -0.20888 | -0.52817 | 0.59445 | 0.40575 | 0.37299 | 0.39889 | 0.25483 | 0.52691 | 0.40022 | 0.39491
42810.4404 | 29 | 18.4639 | 18.5393 | 18.5411 | 18.5589 | 17.8881 | 16.5172 | 14.5836 | 16.6692 | 17.1665 | 17.2593 | 17.2712 | 16.8061 | 15.8416 | 14.4712 | 14.8465 | 14.8393 | 15.414 | 13.2852 | 13.4029 | 13.9703 |  |  |  | 16.556 | 15.889 | 14.9828 | 16.7654 | 19.5567 | 29.6851 | 17.1403 | 16.25 | 15.0434 | 16.8048 | 16.0877 | 15.0791 | 10.8902 | 35.4761 |  | 13.357 | 14.4722 | 16.5833 | 9.7811 |  | 6.261 | 6.3706 | 6.0406 | 6.3732 | 6.8475 | 7.2752 | 9.4126 | 4.8416 | 6.4006 | 4.5503 | 6.6561 | 8.0291 | 42.6355 | 46.4921 | 42.9705 | 14.7602 |  |  | -0.088493 | -0.38893 | -0.026404 | -0.13997 | -0.10563 | -0.095084 | 0.61299 | 0.066204 | -0.26055 | -0.45187 | -0.17516 | 8.8705 | 8.8716 | 2.008 | 15.6827 | 16.586 | 17.1456 | 17.4979 | 17.4606 | 16.4447 | 14.8076 | 16.807 | 17.1619 | 17.4689 | 17.5178 | 17.263 | 16.4632 | 14.6921 | 7.3664 | 8.5227 | 6.1359 | 6.1058 | 5.982 | 6.6762 | 7.6679 | 15.7123 | 15.3502 | 15.2277 | 14.1815 | 14.0853 | 14.0329 |  |  |  | 10.8317 | 21.767 | 12.9415 | 9.8641 | -0.0048136 | 0.096195 | 12.849 |  |  | 10.562 |  |  | 16.8523 | 16.0507 | 15.0041 | 16.3625 | 15.6418 | 14.7453 | 14.497 | 18.7936 | 13.914 | 14.1994 | 9.3043 |  | 10.616 | 10.4573 | 10.0497 | 10.293 | 11.2642 | 21.5764 |  | 12.6723 |  |  | 11.7472 | 12.3915 | 12.4709 | [6 empty] | 12.9082 |  |  | 12.6444 |  |  | 9.8257 | 11.0439 | 34.4838 | 7.8404 | 9.7653 | 18.6721 | 8.1275 | 10.0497 | 21.8055 | 9.8109 | 11.0547 | 8.1499 | 11.6951 | 8.4759 | 11.2449 | 8.189 | 10.5024 | 17.7211 | 11.0051 | 10.7737 | 25.196 | 8.425 | 10.2541 | 20.6534 | 8.5311 | 11.8224 | 10.037 | 10.7054 | 8.6512 | 11.7402 | -0.11422 | 20.9519 | 0.03576 | 0.05002 | -37.6747 | 3.1199 | -4.38 | 48.57 | -0.36077 | -0.72662 | -0.18933 | -0.4359 | -0.37929 | -0.35986 | 0.9137 | 0.40408 | 0.35339 | 0.39799 | 0.27095 | 0.52283 | 0.39987 | 0.39564
42810.4404 | 30 | 18.4584 | 18.5358 | 18.5424 | 18.5644 | 17.8867 | 16.5183 | 14.5818 | 16.6653 | 17.1658 | 17.2531 | 17.2731 | 16.8108 | 15.8396 | 14.4707 | 14.8593 | 14.8459 | 15.4106 | 13.297 | 13.4028 | 13.9703 |  |  |  | 16.5526 | 15.8916 | 14.9872 | 17.1442 | 19.9855 | 30.2294 | 17.1482 | 16.2509 | 15.0493 | 16.8138 | 16.0965 | 15.0814 | 10.9037 | 36.0462 |  | 13.442 | 14.7224 | 16.9288 | 9.8079 |  | 6.262 | 6.3675 | 6.0269 | 6.3583 | 6.8193 | 7.2614 | 9.3676 | 4.8001 | 6.4037 | 4.5423 | 6.6564 | 8.038 | 42.633 | 46.5024 | 42.9814 | 14.7596 |  |  | -0.30271 | -0.43492 | 0.036676 | -0.18728 | -0.070804 | -0.10954 | 0.52691 | 0.2364 | -1.2503 | -0.061434 | -0.23994 | 8.8708 | 8.8716 | 2.0081 | 15.6862 | 16.5915 | 17.1479 | 17.4958 | 17.4612 | 16.4495 | 14.8076 | 16.82 | 17.1664 | 17.4643 | 17.5194 | 17.261 | 16.4653 | 14.692 | 7.1824 | 8.4725 | 6.0819 | 6.1881 | 6.0037 | 6.6738 | 7.6698 | 15.7182 | 15.3533 | 15.2352 | 14.1803 | 14.092 | 14.0325 |  |  |  | 10.8352 | 22.079 | 13.0095 | 9.8552 | 0.13923 | -0.067539 | 12.8782 |  |  | 10.57 |  |  | 16.8638 | 16.0525 | 15.0126 | 16.3615 | 15.648 | 14.7476 | 14.7542 | 19.2026 | 14.149 | 14.4652 | 9.3529 |  | 10.6213 | 10.9217 | 10.0645 | 10.3032 | 11.2641 | 22.0641 |  | 12.6953 |  |  | 11.7885 | 12.4173 | 12.4836 | [6 empty] | 12.924 |  |  | 12.697 |  |  | 9.823 | 11.0629 | 35.5583 | 7.8463 | 9.7878 | 19.0055 | 8.1191 | 10.0468 | 22.1065 | 9.8168 | 11.0688 | 8.1527 | 11.7993 | 8.4551 | 11.2444 | 8.1656 | 10.5121 | 18.0507 | 10.9978 | 10.7838 | 25.5712 | 8.419 | 10.2485 | 21.1463 | 8.5025 | 11.9905 | 10.0389 | 10.8059 | 8.6459 | 11.9837 | -0.12308 | 20.9521 | 0.036007 | 0.047834 | -37.6956 | 3.1198 | -5.22 | 50.36 | -0.66784 | -0.76838 | 0.22313 | -0.50421 | -0.31052 | -0.38623 | 0.8471 | 0.4029 | 0.34098 | 0.3977 | 0.29112 | 0.52903 | 0.39957 | 0.396
42810.4404 | 31 | 18.4656 | 18.5405 | 18.5399 | 18.561 | 17.9001 | 16.523 | 14.5769 | 16.6689 | 17.1674 | 17.2586 | 17.2805 | 16.8164 | 15.8436 | 14.4779 | 14.8655 | 14.8552 | 15.4164 | 13.2863 | 13.4176 | 13.9799 |  |  |  | 16.5576 | 15.8954 | 14.9796 | 17.59 | 20.3951 | 31.7459 | 17.1565 | 16.2585 | 15.0521 | 16.8198 | 16.0881 | 15.0877 | 10.9201 | 36.5265 |  | 13.5319 | 14.9962 | 17.2689 | 9.8405 |  | 6.2717 | 6.371 | 6.0234 | 6.3512 | 6.8162 | 7.3284 | 9.4912 | 4.7304 | 6.4102 | 4.527 | 6.6662 | 8.0287 | 42.6316 | 46.5048 | 42.9921 | 14.7501 |  |  | -0.049721 | -0.15762 | 0.046536 | -0.034826 | -0.070148 | 0.10468 | 0.48157 | 0.25414 | -0.73752 | -0.77119 | -0.16145 | 8.8685 | 8.8699 | 2.008 | 15.6859 | 16.5886 | 17.1521 | 17.49 | 17.4673 | 16.4527 | 14.8058 | 16.8181 | 17.1645 | 17.4694 | 17.5194 | 17.2608 | 16.4657 | 14.6925 | 7.1656 | 8.415 | 6.0192 | 6.1578 | 6.0866 | 6.6778 | 7.6778 | 15.7173 | 15.3507 | 15.2326 | 14.1788 | 14.0838 | 14.0335 |  |  |  | 10.8351 | 22.3581 | 13.1563 | 9.8482 | 0.10256 | -0.17368 | 12.8901 |  |  | 10.5732 |  |  | 16.8625 | 16.0558 | 15.0117 | 16.3686 | 15.6465 | 14.7508 | 15.0867 | 19.6531 | 14.3612 | 14.6751 | 9.4145 |  | 10.6181 | 11.292 | 10.087 | 10.3077 | 11.2869 | 22.764 |  | 12.7385 |  |  | 11.8221 | 12.4292 | 12.4868 | [6 empty] | 12.9406 |  |  | 12.739 |  |  | 9.8274 | 11.0805 | 36.2671 | 7.8679 | 9.823 | 19.2861 | 8.1177 | 10.0443 | 22.3933 | 9.8189 | 11.0835 | 8.1581 | 11.9939 | 8.4552 | 11.2739 | 8.1463 | 10.5288 | 18.3237 | 11.016 | 10.7778 | 25.8967 | 8.4216 | 10.2569 | 21.556 | 8.4795 | 12.1497 | 10.0368 | 10.7918 | 8.6502 | 12.0143 | -0.20629 | 20.9517 | 0.035731 | 0.046857 | -37.7404 | 3.1199 | 0.3 | 48.56 | -0.27134 | -0.46257 | 0.25134 | -0.21743 | -0.30912 | 0.37761 | 0.80993 | 0.40109 | 0.33144 | 0.39833 | 0.29345 | 0.53693 | 0.39921 | 0.39619
42810.4404 | 32 | 18.4624 | 18.5421 | 18.5508 | 18.5608 | 17.8973 | 16.5188 | 14.5808 | 16.67 | 17.1676 | 17.268 | 17.273 | 16.8109 | 15.8416 | 14.4826 | 14.8685 | 14.8588 | 15.4206 | 13.2887 | 13.4125 | 13.9817 |  |  |  | 16.564 | 15.891 | 14.9886 | 18.0788 | 20.7479 | 32.6698 | 17.1515 | 16.2626 | 15.0543 | 16.8123 | 16.0896 | 15.0941 | 10.924 | 36.6033 |  | 13.5805 | 15.2961 | 17.6369 | 9.8328 |  | 6.2806 | 6.366 | 6.0249 | 6.3458 | 6.7982 | 7.3571 | 9.6603 | 4.6041 | 6.4125 | 4.5462 | 6.661 | 8.0396 | 42.6325 | 46.4978 | 42.9952 | 14.7487 |  |  | -0.029353 | -0.10571 | 0.034048 | 0.11105 | 0.14473 | 0.012024 | 0.45331 | 0.21274 | -0.76379 | 0.058781 | -0.42711 | 8.869 | 8.8702 | 2.0081 | 15.6867 | 16.5876 | 17.1473 | 17.4952 | 17.4643 | 16.4457 | 14.8021 | 16.8088 | 17.1601 | 17.4749 | 17.5197 | 17.2625 | 16.4589 | 14.6929 | 7.4566 | 8.3943 | 6.0408 | 6.1589 | 6.1193 | 6.6817 | 7.6788 | 15.72 | 15.3529 | 15.232 | 14.1786 | 14.0803 | 14.033 |  |  |  | 10.8435 | 22.5887 | 13.4122 | 9.8463 | 0.070554 | -0.098027 | 12.9147 |  |  | 10.5785 |  |  | 16.8605 | 16.0568 | 15.0089 | 16.3682 | 15.6496 | 14.7568 | 15.5042 | 19.8534 | 14.594 | 14.8813 | 9.5537 |  | 10.6197 | 11.7276 | 10.0855 | 10.3282 | 11.2874 | 23.1583 |  | 12.7771 |  |  | 11.856 | 12.4132 | 12.4911 | [6 empty] | 12.9631 |  |  | 12.7749 |  |  | 9.8305 | 11.1227 | 37.0799 | 7.8668 | 9.8365 | 19.5347 | 8.128 | 10.0697 | 22.7982 | 9.8464 | 11.1016 | 8.1707 | 12.1908 | 8.4694 | 11.3334 | 8.1447 | 10.5775 | 18.6146 | 11.0207 | 10.7894 | 26.0898 | 8.425 | 10.2783 | 22.0094 | 8.4689 | 12.3105 | 10.0527 | 10.8182 | 8.6618 | 11.9957 | 0.039471 | 20.9511 | 0.035519 | 0.046915 | -37.734 | 3.1199 | 1.54 | 49.31 | -0.2088 | -0.37881 | 0.21499 | 0.38827 | 0.44403 | 0.12799 | 0.78585 | 0.39727 | 0.31929 | 0.39778 | 0.26157 | 0.53466 | 0.39955 | 0.39652
42810.4404 | 33 | 18.4732 | 18.5456 | 18.5464 | 18.5622 | 17.9017 | 16.5286 | 14.5835 | 16.6725 | 17.1718 | 17.2652 | 17.277 | 16.8115 | 15.848 | 14.4741 | 14.8696 | 14.8538 | 15.4178 | 13.2916 | 13.4079 | 13.9828 |  |  |  | 16.5589 | 15.8885 | 14.9851 | 18.5396 | 21.0704 | 33.129 | 17.1611 | 16.2545 | 15.0483 | 16.8209 | 16.0868 | 15.0959 | 10.9271 | 36.516 |  | 13.64 | 15.595 | 17.9724 | 9.8486 |  | 6.2689 | 6.3569 | 6.0112 | 6.3262 | 6.7936 | 7.3223 | 9.6205 | 4.4209 | 6.3934 | 4.5317 | 6.6546 | 8.048 | 42.6285 | 46.4889 | 43.002 | 14.7463 |  |  | -0.12266 | -0.053137 | 0.10568 | -0.051914 | 0.44043 | -0.0734 | 0.64322 | 0.26465 | -0.43239 | -0.54796 | -0.39453 | 8.8698 | 8.8713 | 2.0081 | 15.6883 | 16.592 | 17.1526 | 17.4992 | 17.4665 | 16.4447 | 14.7983 | 16.817 | 17.1641 | 17.4681 | 17.5241 | 17.26 | 16.4651 | 14.6935 | 7.5834 | 8.386 | 6.142 | 6.1924 | 6.1242 | 6.6876 | 7.6794 | 15.7372 | 15.3619 | 15.2456 | 14.193 | 14.0922 | 14.0427 |  |  |  | 10.8529 | 22.8131 | 13.7299 | 9.8439 | -0.098415 | -0.081278 | 12.9308 |  |  | 10.5842 |  |  | 16.8718 | 16.0621 | 15.0131 | 16.366 | 15.6513 | 14.748 | 15.8638 | 20.1934 | 14.8467 | 15.1303 | 9.7971 |  | 10.6287 | 11.942 | 10.0929 | 10.3712 | 11.2952 | 23.4227 |  | 12.8045 |  |  | 11.8773 | 12.4336 | 12.5243 | [6 empty] | 12.9867 |  |  | 12.8056 |  |  | 9.8309 | 11.143 | 37.5783 | 7.8561 | 9.8541 | 19.756 | 8.1278 | 10.0766 | 23.1431 | 9.8543 | 11.1179 | 8.1702 | 12.3525 | 8.4658 | 11.418 | 8.1361 | 10.6426 | 18.894 | 11.0382 | 10.7903 | 26.5112 | 8.4391 | 10.2847 | 22.3736 | 8.4571 | 12.4393 | 10.0693 | 10.9754 | 8.6712 | 12.0361 | 0.015396 | 20.9515 | 0.035553 | 0.048327 | -37.7778 | 3.1198 | 5.29 | 49.57 | -0.42715 | -0.26857 | 0.37875 | -0.26546 | 0.77455 | -0.3162 | 0.93603 | 0.39081 | 0.31357 | 0.39684 | 0.24816 | 0.52348 | 0.39921 | 0.3969
42810.4404 | 34 | 18.4729 | 18.5439 | 18.5435 | 18.5615 | 17.9053 | 16.5225 | 14.5832 | 16.6778 | 17.1713 | 17.2632 | 17.2769 | 16.8118 | 15.8526 | 14.4778 | 14.8716 | 14.8529 | 15.4182 | 13.2871 | 13.4116 | 13.9796 |  |  |  | 16.5561 | 15.8975 | 14.9895 | 18.9322 | 21.3964 | 34.3358 | 17.1599 | 16.2603 | 15.0534 | 16.8161 | 16.0826 | 15.0858 | 10.9278 | 36.7712 |  | 13.7079 | 15.9014 | 18.3252 | 9.883 |  | 6.2821 | 6.3601 | 6.0095 | 6.3221 | 6.7903 | 7.3083 | 9.537 | 4.354 | 6.3977 | 4.4843 | 6.6485 | 8.0431 | 42.611 | 46.478 | 43.0146 | 14.7343 |  |  | 0.16581 | -0.042625 | 0.17402 | -0.12748 | 0.21176 | -0.007032 | 0.66359 | 0.72595 | -1.3073 | -0.38348 | -0.10184 | 8.8691 | 8.8704 | 2.0078 | 15.6925 | 16.5906 | 17.156 | 17.4941 | 17.4725 | 16.4487 | 14.8029 | 16.8193 | 17.1671 | 17.4744 | 17.5242 | 17.2638 | 16.469 | 14.6933 | 7.5859 | 8.3741 | 6.0697 | 6.1539 | 6.131 | 6.6878 | 7.6819 | 15.7395 | 15.3718 | 15.2456 | 14.1936 | 14.0955 | 14.0452 |  |  |  | 10.8688 | 23.1298 | 14.1848 | 9.8644 | -0.23051 | -0.0080678 | 12.9462 |  |  | 10.5792 |  |  | 16.8635 | 16.052 | 15.0063 | 16.3588 | 15.6452 | 14.7395 | 16.1863 | 20.4893 | 15.1189 | 15.4138 | 10.0399 |  | 10.6313 | 12.0424 | 10.0962 | 10.4091 | 11.3035 | 23.8599 |  | 12.8302 |  |  | 11.8943 | 12.4312 | 12.5771 | [6 empty] | 12.9974 |  |  | 12.8449 |  |  | 9.8321 | 11.1634 | 38.1017 | 7.8486 | 9.8805 | 20.0081 | 8.1369 | 10.1015 | 23.4392 | 9.8546 | 11.1407 | 8.1669 | 12.5202 | 8.461 | 11.5335 | 8.1396 | 10.6984 | 19.1851 | 11.0366 | 10.8 | 27.0917 | 8.4472 | 10.2891 | 22.7078 | 8.4486 | 12.6056 | 10.0769 | 10.9744 | 8.6734 | 12.1519 | -0.073585 | 20.9521 | 0.036684 | 0.048775 | -37.6305 | 3.1199 | 21.84 | 48.97 | 0.49761 | -0.24055 | 0.48603 | -0.416 | 0.53706 | -0.097868 | 0.95072 | 0.38415 | 0.31089 | 0.39606 | 0.24792 | 0.5318 | 0.39828 | 0.39685
42810.4404 | 35 | 18.4734 | 18.5464 | 18.5445 | 18.5621 | 17.9037 | 16.5201 | 14.5758 | 16.6752 | 17.1677 | 17.2689 | 17.2756 | 16.8171 | 15.8463 | 14.4782 | 14.8666 | 14.8554 | 15.4168 | 13.2854 | 13.4081 | 13.9787 |  |  |  | 16.5496 | 15.8858 | 14.9829 | 19.3831 | 21.7162 | 35.5148 | 17.1586 | 16.2629 | 15.0569 | 16.8104 | 16.0823 | 15.0857 | 10.9224 | 37.1166 |  | 13.7774 | 16.1842 | 18.6654 | 9.9186 |  | 6.2726 | 6.3644 | 6.015 | 6.3133 | 6.7708 | 7.2593 | 9.445 | 4.3735 | 6.3945 | 4.3434 | 6.6474 | 8.0497 | 42.6038 | 46.4843 | 43.0289 | 14.7295 |  |  | 0.006135 | -0.19442 | -0.009976 | -0.06177 | 0.11253 | -0.26856 | 0.56962 | 0.37702 | 0.6023 | -0.80643 | -0.27789 | 8.8684 | 8.8693 | 2.008 | 15.7039 | 16.5952 | 17.1571 | 17.4961 | 17.4714 | 16.449 | 14.8123 | 16.8227 | 17.1662 | 17.4685 | 17.5286 | 17.2653 | 16.4749 | 14.6985 | 7.5285 | 8.3717 | 6.0486 | 6.1751 | 6.1506 | 6.6979 | 7.6802 | 15.7382 | 15.3644 | 15.2443 | 14.1879 | 14.0947 | 14.0408 |  |  |  | 10.8732 | 23.5655 | 14.3872 | 9.8974 | -0.4248 | -0.019924 | 12.9582 |  |  | 10.5833 |  |  | 16.8689 | 16.0553 | 15.0077 | 16.3576 | 15.6436 | 14.7437 | 16.4828 | 20.9435 | 15.3689 | 15.6543 | 10.3821 |  | 10.6556 | 12.0985 | 10.1167 | 10.4411 | 11.3347 | 24.1768 |  | 12.8855 |  |  | 11.8955 | 12.4394 | 12.6361 | [6 empty] | 13.0133 |  |  | 12.9055 |  |  | 9.8494 | 11.1942 | 38.8291 | 7.849 | 9.9309 | 20.2656 | 8.1483 | 10.1469 | 23.6618 | 9.8696 | 11.1836 | 8.1713 | 12.6858 | 8.4746 | 11.6269 | 8.1578 | 10.7438 | 19.4757 | 11.0413 | 10.7999 | 27.4867 | 8.4432 | 10.2981 | 23.0029 | 8.4467 | 12.7686 | 10.0803 | 10.9659 | 8.6789 | 12.3672 | -0.17258 | 20.9516 | 0.037057 | 0.049101 | -37.644 | 3.1199 | 22.29 | 49.58 | 0.0959 | -0.51373 | -0.11637 | -0.28957 | 0.39147 | -0.60477 | 0.88076 | 0.37545 | 0.31001 | 0.3962 | 0.25546 | 0.53395 | 0.39711 | 0.39608
42810.4405 | 36 | 18.4786 | 18.5491 | 18.5487 | 18.5677 | 17.8994 | 16.5242 | 14.5775 | 16.6753 | 17.1705 | 17.2654 | 17.2794 | 16.8172 | 15.8462 | 14.4744 | 14.8765 | 14.8514 | 15.4212 | 13.2853 | 13.408 | 13.9791 |  |  |  | 16.5512 | 15.8863 | 14.9826 | 19.8721 | 22.093 | 36.2419 | 17.1693 | 16.269 | 15.0678 | 16.8211 | 16.092 | 15.0966 | 10.9367 | 37.2646 |  | 13.8496 | 16.473 | 19.0534 | 9.9884 |  | 6.2815 | 6.3699 | 6.0231 | 6.3226 | 6.7497 | 7.2247 | 9.3582 | 4.4295 | 6.4034 | 4.2508 | 6.6506 | 8.0534 | 42.5934 | 46.4829 | 43.0413 | 14.7284 |  |  | -0.090461 | 0.11771 | 0.079392 | -0.067682 | 0.042876 | 0.011368 | 0.36723 | 0.5459 | -0.70599 | -0.18794 | -0.079588 | 8.8706 | 8.8717 | 2.0081 | 15.6955 | 16.5935 | 17.1509 | 17.4916 | 17.4732 | 16.4456 | 14.8086 | 16.8148 | 17.1615 | 17.4683 | 17.5154 | 17.254 | 16.4633 | 14.6949 | 7.3139 | 8.3469 | 6.0499 | 6.1732 | 6.2817 | 6.7003 | 7.6897 | 15.7407 | 15.3618 | 15.2454 | 14.1851 | 14.0943 | 14.042 |  |  |  | 10.8723 | 23.8965 | 14.423 | 9.8901 | -0.16446 | -0.21208 | 12.9701 |  |  | 10.588 |  |  | 16.8644 | 16.0661 | 15.0127 | 16.3615 | 15.6438 | 14.7466 | 16.7961 | 21.2873 | 15.5787 | 15.8684 | 10.723 |  | 10.6594 | 12.0012 | 10.1196 | 10.4719 | 11.3421 | 24.4026 |  | 12.9082 |  |  | 11.9004 | 12.4671 | 12.6954 | [6 empty] | 13.0639 |  |  | 12.9652 |  |  | 9.8444 | 11.2169 | 39.622 | 7.8446 | 9.9663 | 20.5042 | 8.1531 | 10.1742 | 23.8439 | 9.885 | 11.2069 | 8.1687 | 12.8199 | 8.4901 | 11.7826 | 8.166 | 10.7892 | 19.8023 | 11.0418 | 10.8068 | 28.1436 | 8.4553 | 10.3443 | 23.3452 | 8.449 | 12.9523 | 10.0759 | 10.9858 | 8.6906 | 12.6819 | 0.087043 | 20.9515 | 0.037803 | 0.049 | -37.7511 | 3.1199 | -12.68 | 49.44 | -0.36868 | 0.39974 | 0.32829 | -0.30312 | 0.24163 | 0.12442 | 0.70714 | 0.3661 | 0.31281 | 0.39559 | 0.27959 | 0.53491 | 0.39565 | 0.39626
42810.4405 | 37 | 18.4773 | 18.5453 | 18.5437 | 18.5613 | 17.8931 | 16.5149 | 14.5794 | 16.6708 | 17.1703 | 17.2616 | 17.2762 | 16.8102 | 15.8484 | 14.4717 | 14.8796 | 14.8553 | 15.4134 | 13.2825 | 13.4025 | 13.9769 |  |  |  | 16.5482 | 15.8879 | 14.9807 | 20.3314 | 22.4986 | 36.8914 | 17.1766 | 16.2777 | 15.0683 | 16.8242 | 16.0998 | 15.0916 | 10.9489 | 37.2575 |  | 13.9138 | 16.7604 | 19.4348 | 10.1289 |  | 6.2811 | 6.3738 | 6.0227 | 6.3306 | 6.7344 | 7.2082 | 9.2954 | 4.4791 | 6.3967 | 4.2012 | 6.647 | 8.0507 | 42.5839 | 46.471 | 43.0506 | 14.7168 |  |  | 0.024531 | -0.021597 | 0.098448 | -0.076226 | -0.036636 | -0.54127 | 0.37708 | 0.18514 | -0.37264 | -0.29494 | -0.45136 | 8.8699 | 8.871 | 2.0082 | 15.7052 | 16.6066 | 17.157 | 17.4935 | 17.4692 | 16.4511 | 14.814 | 16.8183 | 17.1651 | 17.4774 | 17.5239 | 17.2607 | 16.4601 | 14.6928 | 7.0916 | 8.29 | 6.0173 | 6.126 | 6.394 | 6.7048 | 7.6837 | 15.7462 | 15.3673 | 15.2447 | 14.1951 | 14.0992 | 14.0391 |  |  |  | 10.8869 | 24.3426 | 14.6172 | 9.8604 | -0.14299 | -0.30505 | 12.9802 |  |  | 10.5869 |  |  | 16.8566 | 16.0475 | 15.0041 | 16.3579 | 15.638 | 14.7461 | 17.1136 | 21.6975 | 15.7607 | 16.0879 | 10.8987 |  | 10.6697 | 11.8592 | 10.1192 | 10.4888 | 11.3606 | 24.7185 |  | 12.9375 |  |  | 11.9182 | 12.4866 | 12.7308 | [6 empty] | 13.0955 |  |  | 13.0082 |  |  | 9.839 | 11.241 | 40.38 | 7.8426 | 9.9971 | 20.7609 | 8.1602 | 10.2122 | 24.0595 | 9.8994 | 11.24 | 8.1649 | 12.9345 | 8.494 | 12.041 | 8.1616 | 10.8105 | 20.0911 | 11.0445 | 10.82 | 28.7688 | 8.4642 | 10.4299 | 23.6882 | 8.4548 | 13.1523 | 10.075 | 11.0093 | 8.708 | 12.9881 | 0.13596 | 20.9514 | 0.038337 | 0.048848 | -37.832 | 3.1199 | 6.63 | 48.73 | 0.19219 | -0.17123 | 0.36558 | -0.32168 | -0.22335 | -0.85848 | 0.71654 | 0.36156 | 0.31674 | 0.39573 | 0.30481 | 0.53783 | 0.39215 | 0.39756
42810.4405 | 38 | 18.4864 | 18.5502 | 18.5552 | 18.5639 | 17.9072 | 16.5252 | 14.5809 | 16.6686 | 17.1795 | 17.2687 | 17.2817 | 16.8171 | 15.8465 | 14.476 | 14.8866 | 14.8699 | 15.4282 | 13.2864 | 13.4139 | 13.9871 |  |  |  | 16.5567 | 15.8896 | 14.9879 | 20.7585 | 22.9361 | 37.3583 | 17.1766 | 16.2768 | 15.0736 | 16.8193 | 16.1031 | 15.1005 | 10.9468 | 37.4067 |  | 13.9632 | 17.0146 | 19.7576 | 10.3534 |  | 6.2789 | 6.36 | 6.0105 | 6.3172 | 6.7103 | 7.179 | 9.2525 | 4.5834 | 6.3967 | 4.1945 | 6.6405 | 8.0609 | 42.5994 | 46.4861 | 43.0641 | 14.7079 |  |  | -0.072065 | -0.12214 | 0.092532 | -0.13602 | -0.14046 | -0.98745 | 0.16944 | 0.55576 | -0.11694 | -0.52719 | -0.40287 | 8.8688 | 8.8703 | 2.0079 | 15.6987 | 16.6013 | 17.156 | 17.5033 | 17.4633 | 16.447 | 14.8108 | 16.8212 | 17.1636 | 17.4702 | 17.5294 | 17.2594 | 16.4612 | 14.6933 | 6.9384 | 8.2651 | 5.9262 | 6.1175 | 6.3578 | 6.7083 | 7.6848 | 15.7438 | 15.367 | 15.2451 | 14.1904 | 14.0932 | 14.0483 |  |  |  | 10.8952 | 24.9232 | 15.0929 | 9.8255 | -0.17176 | -0.19909 | 12.986 |  |  | 10.5878 |  |  | 16.8559 | 16.0422 | 15.0004 | 16.3587 | 15.633 | 14.746 | 17.485 | 22.177 | 15.9503 | 16.329 | 11.0312 |  | 10.6771 | 11.6353 | 10.1401 | 10.511 | 11.3634 | 25.0952 |  | 12.9636 |  |  | 11.9369 | 12.5089 | 12.753 | [6 empty] | 13.1174 |  |  | 13.053 |  |  | 9.8434 | 11.2674 | 40.918 | 7.8412 | 10.0168 | 21.0258 | 8.1677 | 10.2461 | 24.2816 | 9.9086 | 11.267 | 8.1592 | 13.0836 | 8.4975 | 12.3298 | 8.1546 | 10.8213 | 20.3337 | 11.051 | 10.8289 | 29.2859 | 8.4638 | 10.5078 | 24.0293 | 8.4663 | 13.3471 | 10.0737 | 10.9999 | 8.7143 | 13.157 | 0.10438 | 20.9529 | 0.038916 | 0.048486 | -37.7491 | 3.12 | 16.76 | 50.17 | -0.32966 | -0.40718 | 0.35441 | -0.4297 | -0.4373 | -1.1595 | 0.48029 | 0.35812 | 0.32365 | 0.39521 | 0.32224 | 0.54808 | 0.38584 | 0.39881
42810.4405 | 39 | 18.4844 | 18.5504 | 18.5487 | 18.5547 | 17.8987 | 16.5124 | 14.5752 | 16.6737 | 17.1612 | 17.2616 | 17.2719 | 16.8163 | 15.8519 | 14.4724 | 14.8953 | 14.8795 | 15.4388 | 13.2952 | 13.4262 | 13.9887 |  |  |  | 16.5687 | 15.9009 | 14.9985 | 21.1673 | 23.3853 | 38.2296 | 17.1718 | 16.2646 | 15.0612 | 16.8151 | 16.0869 | 15.083 | 10.9555 | 37.5733 |  | 14.0271 | 17.2444 | 20.07 | 10.7457 |  | 6.2812 | 6.3625 | 6.0084 | 6.3093 | 6.6919 | 7.1522 | 9.1678 | 4.6994 | 6.3995 | 4.247 | 6.6341 | 8.0584 | 42.6032 | 46.4982 | 43.0721 | 14.7038 |  |  | -0.083233 | -0.045253 | 0.04522 | 0.039426 | -0.037948 | -0.045144 | 0.1471 | 0.31328 | -0.59196 | -0.70699 | -0.38658 | 8.8702 | 8.8714 | 2.0079 | 15.7015 | 16.5952 | 17.1529 | 17.4935 | 17.4638 | 16.4458 | 14.8071 | 16.8206 | 17.1649 | 17.4687 | 17.5265 | 17.2616 | 16.4604 | 14.6949 | 6.8643 | 8.2509 | 5.8933 | 6.1223 | 6.2407 | 6.7108 | 7.6822 | 15.738 | 15.3651 | 15.2496 | 14.1896 | 14.0939 | 14.0432 |  |  |  | 10.8971 | 25.4683 | 15.5468 | 9.8311 | -0.083625 | -0.23692 | 12.9977 |  |  | 10.5972 |  |  | 16.8595 | 16.0536 | 15.0012 | 16.358 | 15.6339 | 14.7443 | 17.8807 | 22.7326 | 16.1893 | 16.5856 | 11.0769 |  | 10.6805 | 11.4377 | 10.1379 | 10.569 | 11.3776 | 25.0961 |  | 12.9984 |  |  | 11.9362 | 12.5237 | 12.765 | [6 empty] | 13.1454 |  |  | 13.0706 |  |  | 9.8462 | 11.2906 | 40.9977 | 7.8501 | 10.0311 | 21.2999 | 8.1769 | 10.2805 | 24.5632 | 9.9279 | 11.3402 | 8.1691 | 13.2783 | 8.5066 | 12.5488 | 8.1548 | 10.8382 | 20.5573 | 11.0682 | 10.8422 | 29.769 | 8.4698 | 10.5561 | 24.3339 | 8.4801 | 13.5659 | 10.0766 | 11.0197 | 8.7275 | 13.2766 | 0.06682 | 20.9555 | 0.039186 | 0.049752 | -37.75 | 3.12 | 16.55 | 48.63 | -0.35478 | -0.24785 | 0.24776 | 0.23134 | -0.22729 | -0.2479 | 0.44749 | 0.35696 | 0.32906 | 0.39407 | 0.33076 | 0.55143 | 0.37523 | 0.39871
42810.4405 | 40 | 18.4936 | 18.555 | 18.5504 | 18.5688 | 17.9124 | 16.5187 | 14.5888 | 16.6912 | 17.1709 | 17.2721 | 17.2859 | 16.8166 | 15.8563 | 14.4873 | 14.8978 | 14.8718 | 15.4372 | 13.3014 | 13.4268 | 13.9899 |  |  |  | 16.5694 | 15.8997 | 15.0012 | 21.5902 | 23.8412 | 39.0052 | 17.1798 | 16.2739 | 15.0667 | 16.8224 | 16.101 | 15.0911 | 10.9853 | 37.7552 |  | 14.0954 | 17.4719 | 20.3746 | 10.882 |  | 6.2793 | 6.3654 | 6.0054 | 6.3077 | 6.6779 | 7.1313 | 9.0902 | 4.7115 | 6.4048 | 4.3413 | 6.6351 | 8.0704 | 42.6197 | 46.5111 | 43.0896 | 14.7118 |  |  | -0.12266 | -0.11425 | 0.14773 | 0.11894 | -0.024808 | -0.17657 | 0.59853 | 0.6195 | -2.1606 | 0.073257 | -0.15947 | 8.8695 | 8.8705 | 2.0075 | 15.7134 | 16.5998 | 17.1606 | 17.4973 | 17.4634 | 16.4492 | 14.8064 | 16.8195 | 17.1698 | 17.4692 | 17.5225 | 17.2673 | 16.466 | 14.6892 | 6.8007 | 8.2141 | 5.8112 | 6.1694 | 6.1835 | 6.7083 | 7.6877 | 15.7493 | 15.373 | 15.2534 | 14.1921 | 14.0919 | 14.045 |  |  |  | 10.9125 | 26.0282 | 15.8707 | 9.9054 | -0.10976 | -0.092946 | 13.005 |  |  | 10.6058 |  |  | 16.863 | 16.0551 | 15.0066 | 16.3587 | 15.6298 | 14.7419 | 18.1738 | 23.2731 | 16.4208 | 16.8426 | 11.1005 |  | 10.6933 | 11.3179 | 10.1483 | 10.6391 | 11.393 | 25.289 |  | 13.045 |  |  | 11.9215 | 12.5414 | 12.7823 | [6 empty] | 13.1704 |  |  | 13.1034 |  |  | 9.8394 | 11.3152 | 41.3412 | 7.8465 | 10.0392 | 21.5559 | 8.1803 | 10.3022 | 24.8896 | 9.9458 | 11.4959 | 8.1687 | 13.4934 | 8.5134 | 12.7366 | 8.1582 | 10.8472 | 20.8639 | 11.0738 | 10.8511 | 30.3063 | 8.474 | 10.5848 | 24.6945 | 8.4898 | 13.8618 | 10.0711 | 11.1374 | 8.7292 | 13.4426 | -0.019657 | 20.952 | 0.039496 | 0.050013 | -37.7704 | 3.12 | 6.03 | 48.99 | -0.43123 | -0.39382 | 0.44782 | 0.40182 | -0.18376 | -0.49025 | 0.90263 | 0.35673 | 0.33274 | 0.39263 | 0.33754 | 0.5612 | 0.37243 | 0.39716
42810.4405 | 41 | 18.5027 | 18.5606 | 18.5525 | 18.571 | 17.9122 | 16.5239 | 14.583 | 16.6848 | 17.1747 | 17.278 | 17.289 | 16.8159 | 15.8533 | 14.4914 | 14.8926 | 14.8608 | 15.4242 | 13.2911 | 13.419 | 13.9806 |  |  |  | 16.5613 | 15.8913 | 14.9881 | 22.0203 | 24.2441 | 39.9165 | 17.1802 | 16.276 | 15.0694 | 16.8217 | 16.0961 | 15.0907 | 11.0019 | 38.4531 |  | 14.1721 | 17.6559 | 20.6896 | 10.849 |  | 6.2845 | 6.3585 | 5.9979 | 6.2976 | 6.6538 | 7.0974 | 9.0075 | 4.693 | 6.3995 | 4.4047 | 6.6264 | 8.0704 | 42.6194 | 46.5086 | 43.0909 | 14.7052 |  |  | -0.030009 | 0.13019 | 0.015648 | 0.12945 | -0.18646 | -0.23768 | -0.10458 | 0.59321 | -0.56432 | -1.427 | -0.34525 | 8.8703 | 8.8714 | 2.0057 | 15.7204 | 16.6031 | 17.174 | 17.5085 | 17.4767 | 16.4533 | 14.8154 | 16.8209 | 17.1769 | 17.4782 | 17.5305 | 17.2691 | 16.4751 | 14.7034 | 6.7306 | 8.1776 | 5.6511 | 6.1555 | 6.1785 | 6.7049 | 7.6861 | 15.7466 | 15.376 | 15.253 | 14.1939 | 14.0991 | 14.0413 |  |  |  | 10.9213 | 26.4117 | 16.1383 | 9.9241 | -0.16851 | -0.23316 | 13.022 |  |  | 10.6064 |  |  | 16.8628 | 16.053 | 15.0059 | 16.3585 | 15.6356 | 14.7445 | 18.4106 | 23.6298 | 16.6376 | 17.0763 | 11.0562 |  | 10.6872 | 11.4606 | 10.162 | 10.694 | 11.405 | 25.4331 |  | 13.0956 |  |  | 11.9134 | 12.5627 | 12.7997 | [6 empty] | 13.1839 |  |  | 13.1427 |  |  | 9.8538 | 11.345 | 42.3992 | 7.8483 | 10.0494 | 21.806 | 8.196 | 10.325 | 25.1926 | 9.9726 | 11.683 | 8.2126 | 13.7339 | 8.5346 | 12.8963 | 8.1652 | 10.8673 | 21.2272 | 11.0886 | 10.8581 | 31.2868 | 8.4795 | 10.6133 | 25.1085 | 8.4543 | 14.0787 | 10.0684 | 11.2869 | 8.7725 | 13.6312 | 0.051605 | 20.9556 | 0.039593 | 0.049673 | -37.7773 | 3.12 | 9.51 | 49.88 | -0.2136 | 0.4204 | 0.14575 | 0.41919 | -0.50376 | -0.56877 | -0.37728 | 0.35776 | 0.32922 | 0.3915 | 0.34493 | 0.57881 | 0.37389 | 0.39692
42810.4405 | 42 | 18.4966 | 18.5614 | 18.5498 | 18.5703 | 17.9077 | 16.5288 | 14.5846 | 16.6816 | 17.1732 | 17.2722 | 17.2882 | 16.8113 | 15.8541 | 14.4874 | 14.8954 | 14.8558 | 15.4272 | 13.302 | 13.4196 | 13.9825 |  |  |  | 16.5545 | 15.8952 | 14.989 | 22.4591 | 24.6206 | 40.1623 | 17.1758 | 16.2733 | 15.0566 | 16.8141 | 16.0974 | 15.0883 | 11.004 | 38.9301 |  | 14.251 | 17.8234 | 21.0329 | 10.8246 |  | 6.2846 | 6.3557 | 5.9992 | 6.2765 | 6.6176 | 7.0613 | 8.9524 | 4.6618 | 6.3998 | 4.4781 | 6.6306 | 8.0714 | 42.6243 | 46.4991 | 43.0904 | 14.6975 |  |  | 0.12573 | -0.070881 | -0.00932 | -0.016426 | -0.19894 | -0.65232 | 0.037356 | 0.54458 | -0.49836 | 0.32145 | -0.19344 | 8.8698 | 8.8709 | 2.0031 | 15.7134 | 16.5962 | 17.1617 | 17.4996 | 17.4648 | 16.4503 | 14.8063 | 16.8188 | 17.1634 | 17.4748 | 17.5209 | 17.2645 | 16.4672 | 14.694 | 6.7358 | 8.1675 | 5.5298 | 6.0622 | 6.1478 | 6.7107 | 7.6842 | 15.7596 | 15.3721 | 15.256 | 14.1961 | 14.0998 | 14.0453 |  |  |  | 10.9285 | 26.7443 | 16.5717 | 9.9432 | -0.022237 | -0.31069 | 13.0544 |  |  | 10.6103 |  |  | 16.8684 | 16.056 | 15.0056 | 16.3588 | 15.6417 | 14.7515 | 18.6848 | 23.902 | 16.8505 | 17.3117 | 11.004 |  | 10.7077 | 12.218 | 10.182 | 10.7678 | 11.43 | 25.7902 |  | 13.137 |  |  | 11.9282 | 12.5711 | 12.7954 | [6 empty] | 13.2111 |  |  | 13.1916 |  |  | 9.8613 | 11.3738 | 43.7589 | 7.8444 | 10.0811 | 22.0047 | 8.2226 | 10.3468 | 25.5121 | 10.0067 | 11.897 | 8.1833 | 13.9583 | 8.5368 | 13.0622 | 8.1433 | 10.8894 | 21.5724 | 11.1 | 10.8725 | 32.0991 | 8.4909 | 10.6436 | 25.424 | 8.4967 | 14.1928 | 10.084 | 11.3325 | 8.7667 | 13.8028 | 0.017322 | 20.9464 | 0.039651 | 0.050172 | -37.772 | 3.12 | 15.18 | 48.67 | 0.43739 | -0.31019 | -0.11248 | -0.14932 | -0.52032 | -0.94219 | 0.22547 | 0.35989 | 0.30884 | 0.39027 | 0.34503 | 0.59206 | 0.37464 | 0.39663
42810.4405 | 43 | 18.4936 | 18.5574 | 18.5523 | 18.5789 | 17.9022 | 16.5227 | 14.5788 | 16.6742 | 17.1772 | 17.2637 | 17.2824 | 16.8097 | 15.8568 | 14.4839 | 14.9021 | 14.8754 | 15.4369 | 13.2942 | 13.4225 | 13.9915 |  |  |  | 16.5673 | 15.897 | 14.9983 | 22.7347 | 25.1078 | 40.1929 | 17.1816 | 16.2731 | 15.057 | 16.8229 | 16.1044 | 15.0986 | 11.0165 | 39.3522 |  | 14.3421 | 18.0348 | 21.3653 | 10.8183 |  | 6.2806 | 6.3557 | 5.9839 | 6.2517 | 6.5698 | 7.0236 | 8.8876 | 4.673 | 6.3959 | 4.5654 | 6.6253 | 8.0754 | 42.6252 | 46.4937 | 43.0895 | 14.6937 |  |  | -0.092433 | -0.20624 | -0.01852 | 0.23788 | -0.020208 | -0.74169 | 0.20821 | 0.3284 | -0.57464 | -0.673 | -0.06707 | 8.87 | 8.8709 | 2.0009 | 15.7127 | 16.6025 | 17.1662 | 17.4978 | 17.4765 | 16.4457 | 14.811 | 16.8255 | 17.1761 | 17.4774 | 17.5325 | 17.261 | 16.4657 | 14.6877 | 6.6959 | 8.2021 | 5.4275 | 5.9381 | 6.1885 | 6.706 | 7.6798 | 15.7638 | 15.3829 | 15.2546 | 14.2001 | 14.0988 | 14.0577 |  |  |  | 10.9388 | 27.172 | 17.3734 | 9.9756 | 0.050496 | -0.10537 | 13.0894 |  |  | 10.6122 |  |  | 16.876 | 16.057 | 15.0037 | 16.3585 | 15.6427 | 14.7448 | 19.0163 | 24.2455 | 17.0624 | 17.5317 | 11.0195 |  | 10.7147 | 12.9323 | 10.201 | 10.8269 | 11.4379 | 26.4323 |  | 13.1636 |  |  | 11.9023 | 12.5724 | 12.7958 | [6 empty] | 13.2181 |  |  | 13.2301 |  |  | 9.8492 | 11.3985 | 44.5989 | 7.8327 | 10.0859 | 22.17 | 8.217 | 10.3395 | 25.8131 | 10.015 | 12.1525 | 8.198 | 14.1497 | 8.5423 | 13.2374 | 8.131 | 10.9173 | 21.8781 | 11.0959 | 10.8883 | 32.701 | 8.5059 | 10.6643 | 25.7131 | 8.5209 | 14.3366 | 10.1092 | 11.5419 | 8.7649 | 13.9459 | 0.10688 | 20.9544 | 0.040053 | 0.051214 | -37.7476 | 3.1201 | 13.72 | 48.96 | -0.37505 | -0.52912 | -0.15856 | 0.56825 | -0.16582 | -1.0046 | 0.53227 | 0.35969 | 0.28962 | 0.38889 | 0.34892 | 0.60291 | 0.37523 | 0.39608
42810.4405 | 44 | 18.4981 | 18.5593 | 18.5513 | 18.5705 | 17.9016 | 16.5253 | 14.5791 | 16.6757 | 17.1753 | 17.2743 | 17.2813 | 16.8193 | 15.8566 | 14.4765 | 14.9118 | 14.8804 | 15.439 | 13.3038 | 13.4211 | 13.9874 |  |  |  | 16.5684 | 15.8939 | 14.9963 | 23.1829 | 25.7733 | 41.8025 | 17.1815 | 16.2739 | 15.0604 | 16.8196 | 16.1058 | 15.0895 | 11.0231 | 39.8266 |  | 14.429 | 18.2589 | 21.6793 | 10.8009 |  | 6.2978 | 6.3576 | 5.9686 | 6.2444 | 6.5454 | 6.9971 | 8.8001 | 4.6593 | 6.3987 | 4.5662 | 6.6275 | 8.0841 | 42.6277 | 46.4955 | 43.0925 | 14.691 |  |  | 0.048847 | -0.016997 | 0.07742 | 0.16034 | -0.078032 | -0.15554 | 0.29626 | 0.20223 | -0.99517 | -0.063532 | -0.14436 | 8.8695 | 8.8706 | 1.9994 | 15.7196 | 16.6131 | 17.1594 | 17.4998 | 17.4748 | 16.4488 | 14.8094 | 16.8281 | 17.169 | 17.474 | 17.5321 | 17.2599 | 16.469 | 14.6804 | 6.6257 | 8.1756 | 5.4293 | 5.8067 | 6.2195 | 6.7079 | 7.6813 | 15.7676 | 15.38 | 15.2564 | 14.2031 | 14.1077 | 14.0542 |  |  |  | 10.9446 | 27.7433 | 18.3034 | 9.9632 | 0.070554 | -0.12833 | 13.1127 |  |  | 10.6144 |  |  | 16.8604 | 16.05 | 15.0024 | 16.3556 | 15.639 | 14.7396 | 19.3576 | 24.7882 | 17.2638 | 17.7066 | 11.2983 |  | 10.7218 | 13.6207 | 10.2164 | 10.9251 | 11.4467 | 26.892 |  | 13.2018 |  |  | 11.89 | 12.5835 | 12.8113 | [6 empty] | 13.2245 |  |  | 13.2858 |  |  | 9.8624 | 11.4312 | 44.9378 | 7.8387 | 10.0963 | 22.3524 | 8.2217 | 10.3572 | 26.145 | 10.047 | 12.3748 | 8.2215 | 14.3376 | 8.5514 | 13.4592 | 8.1548 | 10.934 | 22.1711 | 11.1024 | 10.9299 | 33.2778 | 8.5104 | 10.7006 | 26.1507 | 8.5441 | 14.5053 | 10.1247 | 11.7282 | 8.7961 | 14.0611 | 0.10168 | 20.9523 | 0.040862 | 0.051026 | -37.7692 | 3.12 | 17.78 | 49.99 | 0.27334 | -0.1519 | 0.32418 | 0.46653 | -0.32583 | -0.46002 | 0.63489 | 0.35217 | 0.27101 | 0.38645 | 0.35693 | 0.6029 | 0.37593 | 0.39661
42810.4406 | 45 | 18.5063 | 18.5651 | 18.5524 | 18.571 | 17.9006 | 16.53 | 14.583 | 16.6836 | 17.1808 | 17.2805 | 17.2867 | 16.8187 | 15.851 | 14.4833 | 14.8919 | 14.8692 | 15.4254 | 13.2836 | 13.4118 | 13.9788 |  |  |  | 16.556 | 15.8911 | 14.974 | 23.8883 | 26.3855 | 42.5589 | 17.1758 | 16.2738 | 15.0622 | 16.8223 | 16.0959 | 15.092 | 11.0262 | 40.3234 |  | 14.5125 | 18.495 | 21.9849 | 10.7712 |  | 6.3026 | 6.3599 | 5.9662 | 6.2304 | 6.5192 | 6.9763 | 8.7223 | 4.5838 | 6.4077 | 4.5691 | 6.6275 | 8.0767 | 42.6192 | 46.4907 | 43.0931 | 14.6777 |  |  | 0.097471 | 0.003375 | 0.094504 | -0.009858 | -0.17266 | -0.41378 | 0.42046 | 0.60898 | 0.96251 | -0.45397 | -0.18311 | 8.868 | 8.8692 | 1.9993 | 15.7129 | 16.6092 | 17.1679 | 17.4991 | 17.4704 | 16.4483 | 14.809 | 16.8244 | 17.1648 | 17.4719 | 17.5289 | 17.2599 | 16.4639 | 14.6849 | 6.5301 | 8.143 | 5.4104 | 5.7075 | 6.0872 | 6.6976 | 7.67 | 15.7689 | 15.3886 | 15.2596 | 14.2032 | 14.106 | 14.0563 |  |  |  | 10.9541 | 28.4345 | 19.416 | 9.9379 | -0.16183 | -0.14207 | 13.1415 |  |  | 10.614 |  |  | 16.8555 | 16.0507 | 14.9991 | 16.355 | 15.6337 | 14.7367 | 19.641 | 25.3721 | 17.4435 | 17.8553 | 12.2423 |  | 10.7459 | 14.4431 | 10.2465 | 11.0375 | 11.4643 | 27.094 |  | 13.2595 |  |  | 11.8476 | 12.5887 | 12.9036 | [6 empty] | 13.2498 |  |  | 13.3383 |  |  | 9.873 | 11.4601 | 45.4406 | 7.8217 | 10.0912 | 22.5121 | 8.2226 | 10.3732 | 26.5136 | 10.074 | 12.5445 | 8.229 | 14.4596 | 8.5675 | 13.7234 | 8.1684 | 10.9386 | 22.4275 | 11.1236 | 10.9572 | 33.8502 | 8.5145 | 10.7155 | 26.6302 | 8.5534 | 14.7014 | 10.1377 | 11.925 | 8.7908 | 14.2429 | 0.043901 | 20.9524 | 0.0412 | 0.050766 | -37.7941 | 3.1201 | 17.02 | 48.79 | 0.38659 | 0.067687 | 0.35817 | -0.11568 | -0.48466 | -0.75029 | 0.75632 | 0.32675 | 0.24916 | 0.38391 | 0.36636 | 0.60367 | 0.37685 | 0.39762
42810.4406 | 46 | 18.5145 | 18.5646 | 18.5619 | 18.5712 | 17.9139 | 16.5338 | 14.5963 | 16.6796 | 17.1796 | 17.2746 | 17.2845 | 16.8169 | 15.8604 | 14.4835 | 14.9068 | 14.8761 | 15.4285 | 13.3024 | 13.4182 | 13.9835 |  |  |  | 16.5629 | 15.8991 | 14.986 | 24.3386 | 26.8933 | 42.6588 | 17.1924 | 16.2909 | 15.0718 | 16.8273 | 16.1019 | 15.1017 | 11.0546 | 40.9048 |  | 14.6289 | 18.736 | 22.3666 | 10.7663 |  | 6.2981 | 6.3579 | 5.9542 | 6.2263 | 6.5038 | 6.9477 | 8.6689 | 4.5312 | 6.404 | 4.5311 | 6.6272 | 8.073 | 42.6118 | 46.4777 | 43.0902 | 14.6664 |  |  | -0.060893 | -0.007141 | 0.099104 | 0.007886 | -0.051092 | -0.25214 | 0.4244 | 0.33891 | -0.65287 | -1.2785 | -0.34207 | 8.8699 | 8.8711 | 1.9997 | 15.7256 | 16.6061 | 17.1685 | 17.5042 | 17.475 | 16.4516 | 14.8096 | 16.8306 | 17.1682 | 17.4721 | 17.5317 | 17.2637 | 16.4633 | 14.6876 | 6.4522 | 8.1437 | 5.364 | 5.676 | 5.9614 | 6.7035 | 7.6809 | 15.7753 | 15.3876 | 15.262 | 14.2001 | 14.0994 | 14.0537 |  |  |  | 10.9535 | 29.4155 | 20.3048 | 9.9063 | -0.061744 | -0.28886 | 13.1804 |  |  | 10.6177 |  |  | 16.8594 | 16.0562 | 15.0027 | 16.3602 | 15.6382 | 14.7422 | 19.9116 | 25.9104 | 17.6181 | 18.0052 | 13.2641 |  | 10.7694 | 15.0434 | 10.2737 | 11.1336 | 11.4808 | 27.3992 |  | 13.3045 |  |  | 11.8289 | 12.6013 | 13.0776 | [6 empty] | 13.2624 |  |  | 13.388 |  |  | 9.8897 | 11.5099 | 46.0305 | 7.8251 | 10.1028 | 22.7053 | 8.2188 | 10.4056 | 26.8044 | 10.1142 | 12.7486 | 8.2327 | 14.5995 | 8.5795 | 13.9772 | 8.1719 | 10.9391 | 22.7166 | 11.1298 | 10.9815 | 34.419 | 8.5124 | 10.7327 | 27.0156 | 8.5613 | 14.9044 | 10.1468 | 12.0317 | 8.8035 | 14.4466 | 0.13924 | 20.9523 | 0.04108 | 0.05057 | -37.7649 | 3.12 | 22.45 | 49.34 | -0.30561 | -0.098456 | 0.36678 | 0.10346 | -0.26363 | -0.58565 | 0.75981 | 0.29914 | 0.23338 | 0.38179 | 0.37571 | 0.6101 | 0.37793 | 0.39848
42810.4406 | 47 | 18.5014 | 18.5515 | 18.551 | 18.5655 | 17.8955 | 16.5203 | 14.5867 | 16.6715 | 17.1678 | 17.2649 | 17.2757 | 16.8121 | 15.8506 | 14.4736 | 14.9034 | 14.8741 | 15.4343 | 13.3002 | 13.4232 | 13.9822 |  |  |  | 16.5589 | 15.9014 | 14.9913 | 24.713 | 27.3839 | 42.9483 | 17.1933 | 16.2869 | 15.0749 | 16.8279 | 16.107 | 15.0989 | 11.0555 | 41.221 |  | 14.7005 | 18.9655 | 22.7207 | 10.7201 |  | 6.2969 | 6.3664 | 5.9546 | 6.2272 | 6.4915 | 6.9258 | 8.758 | 4.5065 | 6.412 | 4.4755 | 6.6214 | 8.0886 | 42.6198 | 46.4877 | 43.0979 | 14.6752 |  |  | -0.000437 | -0.21611 | 0.19438 | 0.050598 | -0.029408 | -0.51827 | 0.26209 | 0.35731 | -0.56432 | -1.0068 | -0.38598 | 8.8686 | 8.8701 | 2.0008 | 15.7302 | 16.6145 | 17.1711 | 17.5061 | 17.4774 | 16.4577 | 14.8077 | 16.8307 | 17.1683 | 17.4736 | 17.536 | 17.2622 | 16.4663 | 14.6886 | 6.4078 | 8.1488 | 5.3305 | 5.6364 | 5.8514 | 6.7014 | 7.6682 | 15.7775 | 15.389 | 15.2668 | 14.1965 | 14.1096 | 14.0566 |  |  |  | 10.9669 | 30.3474 | 20.9919 | 9.926 | 0.056574 | -0.24369 | 13.2119 |  |  | 10.6152 |  |  | 16.8597 | 16.0499 | 14.999 | 16.3571 | 15.6338 | 14.7411 | 20.1545 | 26.5992 | 17.7922 | 18.1792 | 14.0394 |  | 10.7927 | 15.2916 | 10.3008 | 11.1806 | 11.4887 | 27.5609 |  | 13.3155 |  |  | 11.818 | 12.6118 | 13.2421 | [6 empty] | 13.2808 |  |  | 13.4371 |  |  | 9.9063 | 11.5512 | 46.4379 | 7.8007 | 10.1169 | 22.9111 | 8.2173 | 10.4258 | 27.097 | 10.1399 | 12.9941 | 8.2347 | 14.7848 | 8.5827 | 14.1478 | 8.1899 | 10.9448 | 23.0286 | 11.1459 | 11.041 | 34.7994 | 8.5184 | 10.7389 | 27.4046 | 8.5551 | 15.1107 | 10.1611 | 12.1436 | 8.8176 | 14.6409 | 0.033693 | 20.9525 | 0.041355 | 0.050027 | -37.7019 | 3.1201 | 12.86 | 49.9 | -0.025901 | -0.54163 | 0.51369 | 0.26208 | -0.2 | -0.83962 | 0.59708 | 0.27837 | 0.22738 | 0.38074 | 0.38039 | 0.61234 | 0.37924 | 0.39838
42810.4406 | 48 | 18.511 | 18.5618 | 18.5582 | 18.5813 | 17.904 | 16.5264 | 14.5842 | 16.6781 | 17.1775 | 17.2699 | 17.2832 | 16.8195 | 15.8557 | 14.4855 | 14.9097 | 14.8783 | 15.4306 | 13.3034 | 13.4214 | 13.9876 |  |  |  | 16.5656 | 15.8993 | 14.9944 | 25.1399 | 27.8954 | 43.7262 | 17.1865 | 16.2775 | 15.0739 | 16.821 | 16.0971 | 15.0968 | 11.0615 | 41.3848 |  | 14.7614 | 19.2173 | 23.0932 | 10.7149 |  | 6.2894 | 6.3602 | 5.9362 | 6.2094 | 6.466 | 6.893 | 9.0113 | 4.4457 | 6.3953 | 4.4036 | 6.6139 | 8.0862 | 42.6163 | 46.5053 | 43.0869 | 14.6738 |  |  | 0.10799 | 0.013231 | 0.051792 | -0.053226 | -0.087232 | -0.10691 | 0.22595 | 0.37636 | -0.13231 | -0.26809 | -0.1392 | 8.8698 | 8.8712 | 2.0028 | 15.7279 | 16.616 | 17.1698 | 17.5074 | 17.4756 | 16.4523 | 14.8074 | 16.8203 | 17.1627 | 17.4698 | 17.5173 | 17.259 | 16.4636 | 14.686 | 6.3868 | 8.0848 | 5.4015 | 5.5972 | 5.7838 | 6.695 | 7.6625 | 15.7759 | 15.3858 | 15.2666 | 14.2035 | 14.1052 | 14.0572 |  |  |  | 10.979 | 31.0911 | 21.7331 | 9.9642 | 0.11999 | -0.14207 | 13.2503 |  |  | 10.6236 |  |  | 16.8611 | 16.0527 | 15.0008 | 16.3559 | 15.64 | 14.7459 | 20.4464 | 27.425 | 17.9513 | 18.3633 | 13.9987 |  | 10.8205 | 15.0708 | 10.323 | 11.2517 | 11.515 | 27.5243 |  | 13.354 |  |  | 11.804 | 12.6178 | 13.3432 | [6 empty] | 13.3118 |  |  | 13.471 |  |  | 9.9231 | 11.602 | 47.0961 | 7.8072 | 10.1273 | 23.1816 | 8.2233 | 10.4196 | 27.3788 | 10.1726 | 13.348 | 8.2446 | 14.9509 | 8.5943 | 14.313 | 8.2083 | 10.9483 | 23.3313 | 11.1477 | 11.1274 | 35.2473 | 8.5291 | 10.7476 | 27.7281 | 8.5706 | 15.2886 | 10.1718 | 12.3086 | 8.8255 | 14.8559 | -0.031021 | 20.9536 | 0.041361 | 0.048891 | -37.6864 | 3.12 | 21.56 | 48.8 | 0.40766 | 0.13402 | 0.26515 | -0.2688 | -0.34444 | -0.38132 | 0.55435 | 0.28042 | 0.23424 | 0.37964 | 0.38198 | 0.6038 | 0.37958 | 0.39772
42810.4406 | 49 | 18.5193 | 18.5595 | 18.5566 | 18.5753 | 17.9043 | 16.524 | 14.582 | 16.6777 | 17.1794 | 17.2725 | 17.2814 | 16.8196 | 15.8555 | 14.4871 | 14.9118 | 14.8739 | 15.4267 | 13.3091 | 13.4213 | 13.9893 |  |  |  | 16.5641 | 15.8966 | 14.9853 | 25.5266 | 28.4964 | 44.3529 | 17.1886 | 16.2849 | 15.0691 | 16.822 | 16.1044 | 15.0971 | 11.0737 | 41.8642 |  | 14.827 | 19.5078 | 23.4667 | 10.7426 |  | 6.2977 | 6.3616 | 5.9411 | 6.2139 | 6.4655 | 6.897 | 9.257 | 4.379 | 6.4039 | 4.4032 | 6.6164 | 8.0942 | 42.6088 | 46.5287 | 43.079 | 14.6719 |  |  | -0.019493 | 0.12494 | 0.17073 | -0.046654 | 0.009364 | -0.15291 | 0.61168 | 0.26531 | -1.6985 | -0.70972 | -0.40089 | 8.8692 | 8.8706 | 2.0042 | 15.7324 | 16.6154 | 17.1653 | 17.503 | 17.4729 | 16.4476 | 14.8062 | 16.8198 | 17.1744 | 17.4711 | 17.5178 | 17.2596 | 16.4556 | 14.679 | 6.5683 | 8.1075 | 5.4071 | 5.7092 | 5.7148 | 6.7064 | 7.6647 | 15.7794 | 15.3841 | 15.2612 | 14.1968 | 14.1062 | 14.0481 |  |  |  | 10.9783 | 31.8187 | 22.3961 | 9.9481 | -0.078357 | -0.075632 | 13.2901 |  |  | 10.6272 |  |  | 16.8631 | 16.0601 | 15.0054 | 16.3586 | 15.6422 | 14.7516 | 20.7953 | 28.1635 | 18.0998 | 18.5504 | 13.4404 |  | 10.8285 | 14.569 | 10.334 | 11.3489 | 11.5247 | 27.8186 |  | 13.3908 |  |  | 11.8149 | 12.6242 | 13.3415 | [6 empty] | 13.3312 |  |  | 13.491 |  |  | 9.924 | 11.6352 | 47.5458 | 7.8093 | 10.1074 | 23.4385 | 8.2175 | 10.416 | 27.7517 | 10.19 | 13.6808 | 8.247 | 15.1308 | 8.5963 | 14.4962 | 8.2152 | 10.9549 | 23.6294 | 11.1549 | 11.1865 | 35.9106 | 8.5302 | 10.7594 | 28.0001 | 8.5793 | 15.4671 | 10.1879 | 12.5284 | 8.8318 | 15.0433 | 0.1741 | 20.9533 | 0.04135 | 0.048059 | -37.6908 | 3.1201 | 21.84 | 49.34 | -0.17337 | 0.41183 | 0.48141 | -0.25166 | 0.11285 | -0.45604 | 0.9121 | 0.29619 | 0.24854 | 0.37726 | 0.36314 | 0.60343 | 0.37921 | 0.39814
42810.4406 | 50 | 18.5182 | 18.567 | 18.5604 | 18.5793 | 17.9067 | 16.5241 | 14.5836 | 16.6775 | 17.1731 | 17.2698 | 17.2799 | 16.8179 | 15.8531 | 14.4819 | 14.9089 | 14.8809 | 15.4312 | 13.3061 | 13.4223 | 13.989 |  |  |  | 16.5571 | 15.8946 | 14.9906 | 25.9543 | 29.0985 | 46.0561 | 17.1969 | 16.2897 | 15.0677 | 16.8276 | 16.1064 | 15.1002 | 11.0873 | 42.6453 |  | 14.9065 | 19.7838 | 23.8332 | 10.8085 |  | 6.3155 | 6.3594 | 5.9471 | 6.212 | 6.4574 | 6.8845 | 9.523 | 4.3174 | 6.4012 | 4.38 | 6.6206 | 8.0956 | 42.5959 | 46.5395 | 43.0656 | 14.6556 |  |  | -0.29745 | -0.003197 | 0.17796 | -0.2727 | -0.030064 | -0.37502 | -0.020468 | 0.39016 | 0.17399 | 0.21844 | -0.22424 | 8.8703 | 8.8714 | 2.0041 | 15.7296 | 16.6141 | 17.1688 | 17.5039 | 17.4694 | 16.4477 | 14.8069 | 16.8136 | 17.1684 | 17.4677 | 17.5241 | 17.2634 | 16.4514 | 14.6819 | 6.8282 | 8.2624 | 5.4721 | 5.8233 | 5.7074 | 6.7095 | 7.664 | 15.7862 | 15.3848 | 15.2572 | 14.2047 | 14.1021 | 14.0434 |  |  |  | 10.9911 | 32.5374 | 22.7008 | 9.9397 | -0.12698 | -0.14828 | 13.3125 |  |  | 10.636 |  |  | 16.8704 | 16.0631 | 15.0059 | 16.3729 | 15.6441 | 14.7498 | 21.1403 | 28.9569 | 18.2705 | 18.7556 | 12.9317 |  | 10.8364 | 14.2322 | 10.3489 | 11.4321 | 11.5418 | 27.7342 |  | 13.4237 |  |  | 11.8497 | 12.6257 | 13.3118 | [6 empty] | 13.3506 |  |  | 13.5184 |  |  | 9.939 | 11.6875 | 48.5532 | 7.8162 | 10.1092 | 23.6612 | 8.2217 | 10.4261 | 28.1749 | 10.2225 | 14.0786 | 8.2595 | 15.332 | 8.6041 | 14.7139 | 8.2154 | 10.9816 | 23.9727 | 11.1742 | 11.2393 | 36.4632 | 8.5326 | 10.7818 | 28.3001 | 8.5957 | 15.6523 | 10.2096 | 12.7291 | 8.8391 | 15.2098 | -0.010605 | 20.9527 | 0.040781 | 0.048218 | -37.6667 | 3.1201 | 15.64 | 49.15 | -0.67907 | -0.065877 | 0.4915 | -0.60843 | -0.20221 | -0.71416 | -0.16684 | 0.31058 | 0.25839 | 0.37551 | 0.33462 | 0.59613 | 0.37783 | 0.3988
42810.4406 | 51 | 18.5192 | 18.5686 | 18.5634 | 18.5762 | 17.9081 | 16.5309 | 14.5879 | 16.6731 | 17.173 | 17.2695 | 17.2821 | 16.8145 | 15.859 | 14.4824 | 14.9153 | 14.8826 | 15.4391 | 13.3078 | 13.4308 | 13.9941 |  |  |  | 16.5664 | 15.8989 | 14.9976 | 26.7139 | 29.635 | 48.9472 | 17.1952 | 16.2849 | 15.0757 | 16.8218 | 16.1036 | 15.0949 | 11.1035 | 43.4765 |  | 14.9994 | 20.0424 | 24.1554 | 11.0571 |  | 6.3315 | 6.3731 | 5.9553 | 6.2034 | 6.4368 | 6.8741 | 9.6541 | 4.2897 | 6.4061 | 4.3318 | 6.619 | 8.0858 | 42.5782 | 46.5498 | 43.0487 | 14.65 |  |  | 0.14347 | -0.061681 | 0.073476 | -0.036798 | -0.041236 | -0.67532 | -0.014556 | 0.37834 | -1.0284 | -2.0331 | -0.37287 | 8.8687 | 8.87 | 2.0036 | 15.7466 | 16.6249 | 17.1785 | 17.5115 | 17.476 | 16.46 | 14.8139 | 16.8265 | 17.1761 | 17.4826 | 17.5313 | 17.2673 | 16.4664 | 14.6887 | 6.883 | 8.2824 | 5.7477 | 5.9074 | 5.8802 | 6.718 | 7.6659 | 15.7858 | 15.3866 | 15.2575 | 14.1916 | 14.1052 | 14.0408 |  |  |  | 10.9992 | 33.1255 | 22.6482 | 9.9824 | -0.051614 | -0.14263 | 13.3359 |  |  | 10.6451 |  |  | 16.8666 | 16.0604 | 15.007 | 16.3716 | 15.6424 | 14.7497 | 21.4459 | 29.6731 | 18.4589 | 18.9688 | 12.5464 |  | 10.8517 | 14.3664 | 10.375 | 11.5318 | 11.5622 | 27.9311 |  | 13.4677 |  |  | 11.8658 | 12.6235 | 13.2825 | [6 empty] | 13.3637 |  |  | 13.5382 |  |  | 9.9511 | 11.7361 | 49.6337 | 7.8197 | 10.1116 | 23.8751 | 8.2211 | 10.4287 | 28.5846 | 10.2496 | 14.4009 | 8.2789 | 15.5094 | 8.6232 | 14.94 | 8.2184 | 11.0211 | 24.3367 | 11.1813 | 11.2975 | 36.882 | 8.5381 | 10.8027 | 28.6747 | 8.6022 | 15.8577 | 10.2184 | 12.9289 | 8.8444 | 15.4253 | -0.093231 | 20.9532 | 0.041298 | 0.049036 | -37.683 | 3.1201 | 27.23 | 48.54 | 0.47374 | -0.28937 | 0.31583 | -0.22351 | -0.23681 | -0.95834 | -0.1407 | 0.32179 | 0.25552 | 0.37341 | 0.32952 | 0.56573 | 0.37147 | 0.39787
42810.4406 | 52 | 18.5236 | 18.5708 | 18.5659 | 18.5787 | 17.9093 | 16.5305 | 14.5904 | 16.6802 | 17.1824 | 17.2699 | 17.2863 | 16.8206 | 15.8538 | 14.4863 | 14.9144 | 14.8769 | 15.4341 | 13.3072 | 13.4244 | 13.9906 |  |  |  | 16.565 | 15.8931 | 14.9931 | 27.523 | 30.1287 | 50.1383 | 17.1964 | 16.2944 | 15.0855 | 16.8338 | 16.1106 | 15.1037 | 11.1213 | 44.5737 |  | 15.1027 | 20.3326 | 24.4465 | 11.7175 |  | 6.3397 | 6.3815 | 5.957 | 6.201 | 6.4075 | 6.8498 | 9.6246 | 4.304 | 6.4091 | 4.2808 | 6.6157 | 8.0931 | 42.5628 | 46.562 | 43.0468 | 14.6559 |  |  | -0.11478 | -0.023569 | 0.18387 | -0.095282 | -0.13849 | -0.20482 | -0.13875 | 0.2318 | -0.42655 | -1.1996 | -0.31326 | 8.8668 | 8.8683 | 2.0037 | 15.7438 | 16.6194 | 17.1744 | 17.5068 | 17.4758 | 16.4545 | 14.816 | 16.8153 | 17.1674 | 17.473 | 17.5257 | 17.2652 | 16.4603 | 14.6818 | 6.907 | 8.2596 | 5.7303 | 5.988 | 5.9714 | 6.7151 | 7.6663 | 15.7899 | 15.3905 | 15.2642 | 14.2058 | 14.1045 | 14.0459 |  |  |  | 11.0103 | 33.6496 | 22.7132 | 10.2009 | -0.041687 | -0.092946 | 13.3582 |  |  | 10.6347 |  |  | 16.8549 | 16.0522 | 15.0032 | 16.3567 | 15.6308 | 14.7374 | 21.7204 | 30.3183 | 18.6374 | 19.1696 | 12.2611 |  | 10.8616 | 15.0108 | 10.4044 | 11.6199 | 11.5813 | 28.3562 |  | 13.5172 |  |  | 11.8837 | 12.6337 | 13.2745 | [6 empty] | 13.3901 |  |  | 13.5716 |  |  | 9.9575 | 11.7715 | 50.3043 | 7.8168 | 10.1235 | 24.1191 | 8.2238 | 10.4362 | 29.0208 | 10.2733 | 14.6586 | 8.2834 | 15.6875 | 8.6229 | 15.1669 | 8.228 | 11.0686 | 24.6996 | 11.1918 | 11.357 | 37.4647 | 8.5505 | 10.8473 | 29.1136 | 8.6145 | 16.0612 | 10.2386 | 13.1436 | 8.8622 | 15.6387 | -0.10286 | 20.9529 | 0.041579 | 0.048565 | -37.7043 | 3.1201 | 31.46 | 49.72 | -0.42451 | -0.17888 | 0.49962 | -0.35966 | -0.43396 | -0.52776 | -0.43438 | 0.33004 | 0.23859 | 0.3716 | 0.32652 | 0.56771 | 0.35371 | 0.39217
42810.4406 | 53 | 18.5262 | 18.5754 | 18.5638 | 18.5783 | 17.9156 | 16.5318 | 14.5946 | 16.6835 | 17.1767 | 17.2713 | 17.2841 | 16.8132 | 15.8555 | 14.4846 | 14.91 | 14.8755 | 15.43 | 13.3013 | 13.4227 | 13.9836 |  |  |  | 16.5615 | 15.8864 | 14.9877 | 28.1436 | 30.6211 | 50.6718 | 17.2015 | 16.2809 | 15.0699 | 16.8295 | 16.1051 | 15.1056 | 11.1395 | 45.3604 |  | 15.198 | 20.6359 | 24.8053 | 12.5628 |  | 6.3376 | 6.3966 | 5.9557 | 6.1864 | 6.3815 | 6.8233 | 9.5085 | 4.3417 | 6.404 | 4.1793 | 6.6086 | 8.0992 | 42.5519 | 46.5572 | 43.0406 | 14.6559 |  |  | 0.094187 | 0.092743 | 0.27587 | -0.11237 | -0.095776 | -0.33888 | 0.27129 | 0.28897 | -0.55421 | -0.44222 | -0.4442 | 8.8699 | 8.8708 | 2.0049 | 15.7472 | 16.6238 | 17.1744 | 17.5096 | 17.4816 | 16.4565 | 14.817 | 16.8237 | 17.1705 | 17.4787 | 17.5246 | 17.2651 | 16.4653 | 14.6911 | 6.8009 | 8.2088 | 5.6907 | 5.9692 | 5.8934 | 6.7072 | 7.6488 | 15.7877 | 15.3955 | 15.2652 | 14.2078 | 14.1046 | 14.0542 |  |  |  | 11.0232 | 34.0879 | 22.7643 | 10.7282 | -0.014944 | -0.044579 | 13.3987 |  |  | 10.6275 |  |  | 16.8628 | 16.0533 | 15.0046 | 16.3629 | 15.6373 | 14.7373 | 22.0205 | 30.8765 | 18.818 | 19.3752 | 12.0094 |  | 10.8592 | 15.8533 | 10.4202 | 11.6838 | 11.5922 | 28.4355 |  | 13.5544 |  |  | 11.8983 | 12.6439 | 13.2602 | [6 empty] | 13.4214 |  |  | 13.6089 |  |  | 9.9737 | 11.8088 | 51.0609 | 7.8135 | 10.1472 | 24.3987 | 8.2433 | 10.4455 | 29.4673 | 10.2981 | 15.0344 | 8.2894 | 15.8707 | 8.6379 | 15.4072 | 8.2386 | 11.0874 | 25.0443 | 11.2005 | 11.3969 | 38.1803 | 8.5557 | 10.8681 | 29.5609 | 8.6247 | 16.2512 | 10.2586 | 13.3358 | 8.8716 | 15.8426 | -0.059526 | 20.9532 | 0.042406 | 0.047494 | -37.7403 | 3.1201 | 10.01 | 48.86 | 0.38487 | 0.35484 | 0.61199 | -0.39058 | -0.36087 | -0.67881 | 0.60735 | 0.33695 | 0.21571 | 0.37018 | 0.33739 | 0.57007 | 0.33083 | 0.37795
42810.4407 | 54 | 18.5278 | 18.5725 | 18.5635 | 18.5788 | 17.9041 | 16.5341 | 14.587 | 16.6723 | 17.1829 | 17.2801 | 17.2823 | 16.8171 | 15.8521 | 14.4773 | 14.9082 | 14.8706 | 15.4281 | 13.2984 | 13.4158 | 13.9833 |  |  |  | 16.5609 | 15.8885 | 14.988 | 28.7 | 31.0883 | 51.709 | 17.2125 | 16.2891 | 15.071 | 16.8314 | 16.1097 | 15.1045 | 11.1603 | 45.8652 |  | 15.3044 | 20.9019 | 25.1966 | 13.2408 |  | 6.3462 | 6.4033 | 5.9603 | 6.1721 | 6.3703 | 6.7967 | 9.4391 | 4.4576 | 6.4119 | 4.1984 | 6.6092 | 8.0954 | 42.5231 | 46.5415 | 43.0392 | 14.6492 |  |  | -0.043809 | 0.029003 | 0.25418 | 0.041398 | -0.052404 | -0.14634 | 0.30546 | 0.35928 | -0.29636 | -0.50432 | -0.15092 | 8.8694 | 8.8703 | 2.0057 | 15.7423 | 16.6227 | 17.1632 | 17.5024 | 17.4713 | 16.4497 | 14.8142 | 16.8224 | 17.1646 | 17.4734 | 17.5178 | 17.259 | 16.4621 | 14.6824 | 6.6695 | 8.1693 | 5.6301 | 6.0313 | 5.8154 | 6.7086 | 7.6553 | 15.793 | 15.3997 | 15.2617 | 14.2042 | 14.1026 | 14.0488 |  |  |  | 11.0386 | 34.7492 | 23.0574 | 11.1004 | 0.054548 | -0.11967 | 13.4376 |  |  | 10.6278 |  |  | 16.8618 | 16.0611 | 15.0045 | 16.3572 | 15.6388 | 14.7389 | 22.3727 | 31.4501 | 18.9962 | 19.5615 | 11.9889 |  | 10.8757 | 16.558 | 10.4557 | 11.7288 | 11.602 | 28.6595 |  | 13.5974 |  |  | 11.9121 | 12.6504 | 13.3301 | [6 empty] | 13.4522 |  |  | 13.6464 |  |  | 9.99 | 11.8538 | 51.9783 | 7.8118 | 10.1832 | 24.7395 | 8.2551 | 10.4568 | 29.8787 | 10.332 | 15.5502 | 8.3084 | 16.05 | 8.6635 | 15.6504 | 8.243 | 11.1093 | 25.3667 | 11.2098 | 11.4169 | 38.8008 | 8.5602 | 10.8763 | 30.1026 | 8.6362 | 16.4508 | 10.272 | 13.5534 | 8.8757 | 16.0844 | -0.077437 | 20.9522 | 0.042228 | 0.047646 | -37.7581 | 3.1202 | 7.24 | 48.63 | -0.2629 | 0.19844 | 0.58745 | 0.23708 | -0.26692 | -0.44605 | 0.64444 | 0.33807 | 0.1973 | 0.36926 | 0.35215 | 0.57756 | 0.31268 | 0.36812
42810.4407 | 55 | 18.5325 | 18.5701 | 18.5587 | 18.5801 | 17.9027 | 16.525 | 14.5865 | 16.6778 | 17.1784 | 17.2709 | 17.2819 | 16.8178 | 15.8504 | 14.4717 | 14.9241 | 14.888 | 15.4432 | 13.3096 | 13.426 | 13.9935 |  |  |  | 16.5735 | 15.9076 | 15.0016 | 29.2505 | 31.5558 | 52.6791 | 17.204 | 16.2946 | 15.0734 | 16.8247 | 16.1117 | 15.099 | 11.1835 | 46.3006 |  | 15.4187 | 21.2209 | 25.6033 | 13.3175 |  | 6.3637 | 6.4105 | 5.9685 | 6.1773 | 6.3599 | 6.7792 | 9.3972 | 4.5887 | 6.4159 | 4.2315 | 6.6151 | 8.0982 | 42.4823 | 46.515 | 43.0343 | 14.6381 |  |  | 0.1139 | -0.26145 | 0.19176 | 0.038114 | -0.02612 | 0.13096 | 0.40863 | 0.32576 | -1.2162 | -0.72147 | -0.41479 | 8.8715 | 8.8729 | 2.0064 | 15.7391 | 16.618 | 17.1671 | 17.5043 | 17.4598 | 16.4535 | 14.8045 | 16.8146 | 17.1592 | 17.4688 | 17.5196 | 17.2572 | 16.4587 | 14.674 | 6.5635 | 8.1026 | 5.5421 | 6.0998 | 5.8427 | 6.7093 | 7.6561 | 15.803 | 15.3982 | 15.2649 | 14.2046 | 14.1041 | 14.0567 |  |  |  | 11.0543 | 35.4176 | 23.3128 | 11.4157 | -0.14177 | -0.086171 | 13.4793 |  |  | 10.6278 |  |  | 16.8657 | 16.06 | 15.0132 | 16.3525 | 15.6423 | 14.7402 | 22.7508 | 32.1203 | 19.185 | 19.7605 | 12.1115 |  | 10.9009 | 17.0237 | 10.4917 | 11.7438 | 11.6183 | 28.9821 |  | 13.6405 |  |  | 11.9427 | 12.669 | 13.4987 | [6 empty] | 13.4874 |  |  | 13.6483 |  |  | 9.9995 | 11.8909 | 52.8701 | 7.8059 | 10.2167 | 25.127 | 8.2495 | 10.4542 | 30.3486 | 10.3567 | 15.8811 | 8.3184 | 16.2084 | 8.6802 | 15.9052 | 8.2449 | 11.123 | 25.7755 | 11.2071 | 11.4272 | 39.5016 | 8.5673 | 10.882 | 30.618 | 8.6418 | 16.6356 | 10.2923 | 13.7886 | 8.8923 | 16.3264 | 0.040819 | 20.9533 | 0.042285 | 0.048247 | -37.8678 | 3.1201 | 25.61 | 50.31 | 0.42454 | -0.59579 | 0.51025 | 0.22748 | -0.18844 | 0.42196 | 0.74534 | 0.33549 | 0.18555 | 0.36938 | 0.36401 | 0.58743 | 0.31131 | 0.35988
42810.4407 | 56 | 18.5254 | 18.5638 | 18.5602 | 18.5751 | 17.9037 | 16.5185 | 14.5853 | 16.6808 | 17.1721 | 17.2731 | 17.2809 | 16.8127 | 15.8522 | 14.4755 | 14.9235 | 14.8884 | 15.4409 | 13.3089 | 13.4239 | 13.9999 |  |  |  | 16.5769 | 15.9062 | 14.9939 | 29.7062 | 32.0267 | 53.5366 | 17.219 | 16.3007 | 15.0801 | 16.8368 | 16.1117 | 15.1098 | 11.2082 | 46.7145 |  | 15.5389 | 21.5892 | 26.0363 | 13.2524 |  | 6.3675 | 6.4056 | 5.9718 | 6.1687 | 6.3588 | 6.7661 | 9.5466 | 4.6038 | 6.4057 | 4.2255 | 6.6121 | 8.0998 | 42.4303 | 46.486 | 43.0281 | 14.6449 |  |  | -0.10426 | -0.018969 | 0.19833 | 0.19188 | -0.077376 | 0.09942 | 0.31794 | 0.1628 | -0.3849 | -0.026817 | -0.23279 | 8.8688 | 8.87 | 2.0066 | 15.746 | 16.6203 | 17.1685 | 17.506 | 17.4725 | 16.4547 | 14.8041 | 16.8225 | 17.1612 | 17.4626 | 17.5204 | 17.2558 | 16.4541 | 14.677 | 6.4858 | 8.0907 | 5.4728 | 6.0023 | 5.9429 | 6.7093 | 7.6536 | 15.8048 | 15.3995 | 15.2657 | 14.2046 | 14.109 | 14.0579 |  |  |  | 11.0732 | 35.932 | 23.3771 | 11.6983 | -0.085043 | 0.010564 | 13.5245 |  |  | 10.6334 |  |  | 16.8696 | 16.056 | 15.02 | 16.357 | 15.6449 | 14.7462 | 23.3072 | 32.888 | 19.4049 | 19.9958 | 11.9807 |  | 10.9213 | 16.4573 | 10.5176 | 11.7685 | 11.6416 | 29.3547 |  | 13.7053 |  |  | 11.9707 | 12.685 | 13.5976 | [6 empty] | 13.5217 |  |  | 13.6778 |  |  | 10.0043 | 11.9193 | 53.4781 | 7.8075 | 10.2418 | 25.5217 | 8.2463 | 10.4656 | 30.8205 | 10.3834 | 16.0805 | 8.3272 | 16.3799 | 8.6845 | 16.1556 | 8.2548 | 11.1307 | 26.2587 | 11.2159 | 11.4383 | 40.0885 | 8.5787 | 10.9076 | 31.0616 | 8.6637 | 16.8161 | 10.313 | 14.0463 | 8.9041 | 16.584 | -0.063378 | 20.9535 | 0.042738 | 0.048319 | -37.7993 | 3.1201 | 35.77 | 48.62 | -0.40672 | -0.16048 | 0.51891 | 0.5104 | -0.32433 | 0.36764 | 0.65744 | 0.3398 | 0.20214 | 0.36946 | 0.37263 | 0.59483 | 0.31394 | 0.35265
42810.4407 | 57 | 18.5288 | 18.5776 | 18.5623 | 18.5767 | 17.9028 | 16.5257 | 14.584 | 16.6852 | 17.173 | 17.275 | 17.2897 | 16.8168 | 15.8596 | 14.4834 | 14.9177 | 14.895 | 15.4399 | 13.3102 | 13.427 | 13.9923 |  |  |  | 16.5637 | 15.8984 | 14.9914 | 30.1829 | 32.5706 | 54.0015 | 17.2145 | 16.2966 | 15.0799 | 16.8396 | 16.1155 | 15.1077 | 11.2199 | 47.1213 |  | 15.6348 | 21.9541 | 26.4411 | 13.1772 |  | 6.3916 | 6.4194 | 5.9804 | 6.1842 | 6.363 | 6.7551 | 10.0358 | 4.5741 | 6.414 | 4.2511 | 6.6195 | 8.1007 | 42.3969 | 46.475 | 43.0288 | 14.6389 |  |  | -0.075349 | -0.030797 | 0.25024 | 0.37259 | -0.103 | -0.003088 | 0.39417 | 0.35534 | -0.49777 | -0.51901 | -0.35518 | 8.8691 | 8.8703 | 2.0066 | 15.7567 | 16.6215 | 17.1639 | 17.5107 | 17.4718 | 16.4565 | 14.8125 | 16.8213 | 17.1643 | 17.4729 | 17.5189 | 17.2555 | 16.4569 | 14.6764 | 6.4538 | 8.1274 | 5.4466 | 5.8597 | 5.9566 | 6.7122 | 7.6506 | 15.8028 | 15.4009 | 15.2722 | 14.2083 | 14.1118 | 14.0585 |  |  |  | 11.0862 | 36.468 | 23.8237 | 11.8927 | -0.15048 | -0.098027 | 13.5518 |  |  | 10.6405 |  |  | 16.8697 | 16.0595 | 15.0164 | 16.3603 | 15.6414 | 14.7421 | 23.9543 | 33.5927 | 19.665 | 20.2435 | 11.8647 |  | 10.9406 | 15.8601 | 10.5411 | 11.8157 | 11.6628 | 30.062 |  | 13.7672 |  |  | 11.9733 | 12.6983 | 13.6242 | [6 empty] | 13.5498 |  |  | 13.7249 |  |  | 10.0102 | 11.9353 | 54.0972 | 7.8022 | 10.2596 | 26.0087 | 8.2528 | 10.4769 | 31.2216 | 10.4066 | 16.3939 | 8.3301 | 16.5555 | 8.6918 | 16.4014 | 8.2621 | 11.1312 | 26.6599 | 11.2323 | 11.4614 | 40.7025 | 8.5793 | 10.9184 | 31.5456 | 8.6723 | 16.9653 | 10.3326 | 14.348 | 8.9057 | 16.8421 | 0.24343 | 20.9516 | 0.042606 | 0.048421 | -37.7495 | 3.1201 | 24.95 | 49.03 | -0.346 | -0.20449 | 0.58289 | 0.71125 | -0.3742 | -0.06479 | 0.73201 | 0.34366 | 0.21951 | 0.36885 | 0.37654 | 0.59741 | 0.31641 | 0.34768
42810.4407 | 58 | 18.5355 | 18.5773 | 18.5612 | 18.5842 | 17.9021 | 16.5299 | 14.5852 | 16.6808 | 17.1743 | 17.2761 | 17.2853 | 16.8212 | 15.8631 | 14.4786 | 14.9379 | 14.8962 | 15.4505 | 13.3176 | 13.4358 | 13.9965 |  |  |  | 16.571 | 15.9017 | 15.0054 | 30.702 | 33.0244 | 54.4837 | 17.2092 | 16.2941 | 15.079 | 16.8323 | 16.1112 | 15.0995 | 11.2257 | 47.4003 |  | 15.7306 | 22.3234 | 26.8672 | 13.1263 |  | 6.3688 | 6.4216 | 5.9874 | 6.1857 | 6.3513 | 6.7426 | 10.6796 | 4.5256 | 6.4044 | 4.2934 | 6.6171 | 8.1002 | 42.3551 | 46.4426 | 43.029 | 14.6332 |  |  | 0.027819 | -0.15565 | 0.037992 | 0.08017 | -0.074088 | -0.22914 | 0.54399 | 0.39082 | -0.34715 | -0.57628 | -0.36889 | 8.8694 | 8.8707 | 2.0066 | 15.7631 | 16.6374 | 17.1828 | 17.5228 | 17.4819 | 16.4589 | 14.8187 | 16.8274 | 17.1752 | 17.4693 | 17.5246 | 17.2702 | 16.4707 | 14.6777 | 6.3992 | 8.0732 | 5.406 | 5.7417 | 5.8479 | 6.7047 | 7.6418 | 15.8168 | 15.4076 | 15.2739 | 14.2171 | 14.1175 | 14.0616 |  |  |  | 11.1037 | 36.998 | 24.2306 | 12.0836 | 0.061842 | -0.23504 | 13.5673 |  |  | 10.6428 |  |  | 16.8712 | 16.0557 | 15.0151 | 16.3583 | 15.6388 | 14.7401 | 24.452 | 34.1572 | 19.94 | 20.5039 | 11.8006 |  | 10.9541 | 15.3545 | 10.5603 | 11.8585 | 11.6839 | 31.3279 |  | 13.8243 |  |  | 11.9755 | 12.7138 | 13.6588 | [6 empty] | 13.584 |  |  | 13.7412 |  |  | 10.0292 | 11.9794 | 54.5658 | 7.7976 | 10.2642 | 26.5385 | 8.2548 | 10.4865 | 31.5956 | 10.4371 | 16.7661 | 8.3361 | 16.7278 | 8.6993 | 16.6381 | 8.2664 | 11.1464 | 27.0195 | 11.246 | 11.4825 | 41.2769 | 8.5969 | 10.9424 | 32.1292 | 8.6808 | 17.139 | 10.3479 | 14.6543 | 8.9189 | 17.0882 | 0.020403 | 20.9519 | 0.042905 | 0.049239 | -37.7032 | 3.1202 | 23.51 | 50.11 | 0.21039 | -0.45971 | 0.22712 | 0.32993 | -0.31735 | -0.5581 | 0.85992 | 0.34588 | 0.23418 | 0.36836 | 0.38173 | 0.60089 | 0.31802 | 0.34296
42810.4407 | 59 | 18.5257 | 18.5751 | 18.5614 | 18.5706 | 17.9013 | 16.5283 | 14.5739 | 16.6696 | 17.1749 | 17.2662 | 17.2775 | 16.8192 | 15.8498 | 14.4789 | 14.93 | 14.8896 | 15.4409 | 13.3113 | 13.4253 | 13.9982 |  |  |  | 16.5602 | 15.9058 | 14.9951 | 31.1651 | 33.5926 | 54.4124 | 17.2164 | 16.2987 | 15.0796 | 16.8305 | 16.1072 | 15.1058 | 11.2487 | 47.6186 |  | 15.8378 | 22.7347 | 27.3034 | 13.0238 |  | 6.3721 | 6.4285 | 5.9923 | 6.1937 | 6.3599 | 6.7518 | 11.2275 | 4.529 | 6.397 | 4.273 | 6.6177 | 8.1045 | 42.3248 | 46.4371 | 43.0285 | 14.6307 |  |  | -0.10163 | -0.11491 | 0.23644 | -0.049282 | 0.020536 | 0.23939 | 0.44871 | 0.39016 | 0.030568 | -0.65915 | -0.30869 | 8.8706 | 8.8717 | 2.0068 | 15.7533 | 16.6305 | 17.1675 | 17.5081 | 17.4773 | 16.4533 | 14.8133 | 16.819 | 17.1681 | 17.4646 | 17.5141 | 17.2574 | 16.453 | 14.6703 | 6.3828 | 8.1927 | 5.4907 | 5.6762 | 5.7699 | 6.7096 | 7.6382 | 15.8035 | 15.3998 | 15.2652 | 14.2042 | 14.1071 | 14.0545 |  |  |  | 11.1177 | 37.5865 | 24.6748 | 12.2424 | -0.17439 | -0.20022 | 13.5789 |  |  | 10.6402 |  |  | 16.8639 | 16.055 | 15.0139 | 16.3603 | 15.6408 | 14.7382 | 24.9763 | 34.8014 | 20.2291 | 20.7979 | 11.7275 |  | 10.971 | 14.9588 | 10.5573 | 11.928 | 11.6919 | 32.1439 |  | 13.892 |  |  | 11.9855 | 12.7281 | 13.7281 | [6 empty] | 13.6125 |  |  | 13.7713 |  |  | 10.0373 | 12.0114 | 55.1007 | 7.8106 | 10.2818 | 27.0612 | 8.2575 | 10.5072 | 31.9802 | 10.4715 | 17.1893 | 8.35 | 16.9442 | 8.7084 | 16.8804 | 8.2925 | 11.1574 | 27.4003 | 11.2598 | 11.5126 | 41.6881 | 8.597 | 10.981 | 32.6334 | 8.6834 | 17.338 | 10.3567 | 14.9512 | 8.9281 | 17.3103 | -0.10016 | 20.9509 | 0.042446 | 0.05023 | -37.8113 | 3.1202 | 20.35 | 48.75 | -0.4021 | -0.395 | 0.5666 | -0.25868 | 0.16708 | 0.57045 | 0.781 | 0.34847 | 0.24507 | 0.36669 | 0.38412 | 0.59105 | 0.32162 | 0.33901
42810.4407 | 60 | 18.5355 | 18.5886 | 18.5674 | 18.5743 | 17.9169 | 16.5375 | 14.5832 | 16.6831 | 17.1832 | 17.2843 | 17.2874 | 16.8228 | 15.8589 | 14.484 | 14.9377 | 14.8928 | 15.4499 | 13.3144 | 13.4337 | 13.9948 |  |  |  | 16.5694 | 15.9006 | 14.9955 | 31.5418 | 34.2081 | 54.6405 | 17.2196 | 16.3123 | 15.0916 | 16.8283 | 16.1076 | 15.1092 | 11.2669 | 48.0818 |  | 15.9408 | 23.1875 | 27.7205 | 12.8967 |  | 6.3753 | 6.4372 | 5.994 | 6.186 | 6.3486 | 6.7691 | 11.7239 | 4.5358 | 6.4055 | 4.283 | 6.6135 | 8.1003 | 42.3115 | 46.4448 | 43.0254 | 14.6291 |  |  | -0.076005 | 0.099971 | 0.55317 | 0.063742 | -0.000492 | 0.17499 | 0.38957 | 0.27582 | -0.3491 | -0.87147 | -0.32121 | 8.8688 | 8.87 | 2.0069 | 15.7604 | 16.621 | 17.1727 | 17.509 | 17.4719 | 16.4564 | 14.8129 | 16.8142 | 17.1684 | 17.4677 | 17.5163 | 17.2558 | 16.4528 | 14.6701 | 6.925 | 8.335 | 5.9499 | 5.6567 | 5.7034 | 6.7164 | 7.6404 | 15.8136 | 15.41 | 15.2751 | 14.2111 | 14.1158 | 14.0614 |  |  |  | 11.1392 | 38.1257 | 25.0496 | 12.414 | -0.11645 | -0.14207 | 13.5849 |  |  | 10.6386 |  |  | 16.8629 | 16.0576 | 15.0163 | 16.3647 | 15.6395 | 14.7457 | 25.6204 | 35.4573 | 20.5261 | 21.1307 | 11.5431 |  | 10.9912 | 14.5438 | 10.5762 | 12.0035 | 11.7104 | 33.0952 |  | 13.9468 |  |  | 11.9946 | 12.7363 | 13.6802 | [6 empty] | 13.6319 |  |  | 13.8105 |  |  | 10.0587 | 12.0548 | 55.6799 | 7.8238 | 10.2829 | 27.5798 | 8.2602 | 10.5285 | 32.2744 | 10.4859 | 17.552 | 8.3571 | 17.1587 | 8.7231 | 17.1014 | 8.3009 | 11.1732 | 27.7233 | 11.2779 | 11.5356 | 42.2365 | 8.6025 | 10.9867 | 32.9465 | 8.6953 | 17.5451 | 10.3803 | 15.2482 | 8.934 | 17.5333 | -0.19608 | 20.9499 | 0.042647 | 0.049832 | -37.7605 | 3.1202 | 20.66 | 49.43 | -0.34785 | 0.36844 | 0.86667 | 0.2942 | -0.025862 | 0.48774 | 0.72774 | 0.35426 | 0.25722 | 0.3652 | 0.32466 | 0.5403 | 0.32575 | 0.33495
42810.4407 | 61 | 18.5387 | 18.5784 | 18.5615 | 18.5721 | 17.903 | 16.5271 | 14.5761 | 16.676 | 17.1735 | 17.271 | 17.2809 | 16.8202 | 15.8575 | 14.4772 | 14.9326 | 14.8986 | 15.4499 | 13.3147 | 13.4359 | 13.9875 |  |  |  | 16.5719 | 15.8991 | 14.998 | 31.9836 | 34.7273 | 55.2499 | 17.2189 | 16.3069 | 15.091 | 16.8405 | 16.1181 | 15.1136 | 11.2728 | 49.5127 |  | 16.09 | 23.6581 | 28.2492 | 12.8605 |  | 6.3746 | 6.4318 | 5.9945 | 6.1832 | 6.3417 | 6.8732 | 12.0402 | 4.6351 | 6.4162 | 4.2663 | 6.6234 | 8.1107 | 42.2955 | 46.4639 | 43.0209 | 14.6308 |  |  | -0.11281 | -0.028169 | 0.33829 | 0.44027 | 0.45686 | 0.36752 | 0.51968 | 0.50779 | -0.61512 | -1.4388 | -0.291 | 8.871 | 8.8723 | 2.006 | 15.7606 | 16.628 | 17.1781 | 17.5145 | 17.4801 | 16.4579 | 14.8196 | 16.8196 | 17.1707 | 17.4769 | 17.5267 | 17.2587 | 16.457 | 14.672 | 7.9875 | 8.8697 | 6.6147 | 5.8269 | 5.6403 | 6.744 | 7.6552 | 15.8216 | 15.4166 | 15.2794 | 14.2188 | 14.122 | 14.0632 |  |  |  | 11.1567 | 38.8758 | 25.419 | 12.5803 | -0.038243 | -0.19589 | 13.5936 |  |  | 10.625 |  |  | 16.8603 | 16.0546 | 15.0184 | 16.3631 | 15.6315 | 14.745 | 26.1963 | 36.093 | 20.8172 | 21.4443 | 11.3262 |  | 10.9878 | 14.146 | 10.5948 | 12.0841 | 11.7274 | 33.619 |  | 14.0104 |  |  | 11.9784 | 12.7301 | 13.6217 | [6 empty] | 13.6499 |  |  | 13.8252 |  |  | 10.069 | 12.0757 | 56.2846 | 7.8313 | 10.2934 | 28.0225 | 8.2599 | 10.5271 | 32.6856 | 10.5043 | 17.867 | 8.3553 | 17.3562 | 8.7168 | 17.3082 | 8.326 | 11.1921 | 28.1141 | 11.311 | 11.5713 | 42.7073 | 8.6262 | 11.0079 | 33.2495 | 8.7226 | 17.7275 | 10.4056 | 15.5557 | 8.9593 | 17.7601 | -0.030443 | 20.9503 | 0.04318 | 0.049492 | -37.7443 | 3.1202 | 15.77 | 49.67 | -0.42416 | -0.19557 | 0.67775 | 0.77318 | 0.78823 | 0.70698 | 0.84068 | 0.36017 | 0.26889 | 0.36353 | 0.20981 | 0.46815 | 0.32695 | 0.33091
42810.4408 | 62 | 18.5347 | 18.5733 | 18.5524 | 18.5761 | 17.9026 | 16.5227 | 14.5788 | 16.6683 | 17.1697 | 17.2661 | 17.2825 | 16.8193 | 15.852 | 14.4796 | 14.9383 | 14.8901 | 15.4463 | 13.307 | 13.4298 | 13.9905 |  |  |  | 16.5687 | 15.8984 | 14.9967 | 32.4421 | 35.1688 | 54.979 | 17.2191 | 16.3034 | 15.0909 | 16.8373 | 16.1145 | 15.1066 | 11.2922 | 50.2865 |  | 16.2096 | 24.0279 | 28.7844 | 12.8656 |  | 6.3659 | 6.4246 | 5.9968 | 6.1781 | 6.3359 | 6.9087 | 12.151 | 4.6701 | 6.4111 | 4.2475 | 6.6149 | 8.1117 | 42.2819 | 46.4725 | 42.9922 | 14.6348 |  |  | -0.25934 | 0.11377 | 0.42043 | -0.30425 | 0.62574 | 0.66848 | 0.51442 | 0.5873 | -0.27904 | -0.035209 | -0.21172 | 8.8707 | 8.8716 | 2.0056 | 15.7701 | 16.6336 | 17.1811 | 17.5158 | 17.4805 | 16.4579 | 14.8183 | 16.8284 | 17.1731 | 17.4833 | 17.5322 | 17.2649 | 16.4645 | 14.6831 | 8.492 | 8.9473 | 7.9682 | 6.4447 | 5.8041 | 6.7476 | 7.6656 | 15.8161 | 15.4103 | 15.2798 | 14.2121 | 14.1081 | 14.0543 |  |  |  | 11.1602 | 39.4151 | 25.6417 | 12.7124 | -0.096389 | -0.086171 | 13.61 |  |  | 10.6174 |  |  | 16.8581 | 16.0515 | 15.0144 | 16.3601 | 15.6367 | 14.7437 | 26.6782 | 36.6685 | 21.1261 | 21.7477 | 11.0868 |  | 11.005 | 13.9363 | 10.6174 | 12.1854 | 11.7503 | 34.5544 |  | 14.0932 |  |  | 11.989 | 12.7494 | 13.5778 | [6 empty] | 13.6694 |  |  | 13.8704 |  |  | 10.087 | 12.1301 | 56.922 | 7.8602 | 10.3183 | 28.3668 | 8.2859 | 10.5494 | 33.1907 | 10.5336 | 18.2004 | 8.3816 | 17.5535 | 8.7301 | 17.4947 | 8.3259 | 11.1869 | 28.4596 | 11.3222 | 11.5893 | 43.3076 | 8.6264 | 11.0017 | 33.6264 | 8.7189 | 17.8822 | 10.4277 | 15.8392 | 8.9664 | 17.9689 | 0.061812 | 20.9528 | 0.043433 | 0.048413 | -37.768 | 3.1202 | 20.76 | 49.21 | -0.64287 | 0.39304 | 0.75555 | -0.64273 | 0.92255 | 0.95354 | 0.83647 | 0.36739 | 0.27545 | 0.36147 | 0.15417 | 0.31897 | 0.32745 | 0.32735
42810.4408 | 63 | 18.5368 | 18.5709 | 18.5537 | 18.572 | 17.8943 | 16.5224 | 14.5698 | 16.6709 | 17.165 | 17.2657 | 17.2763 | 16.8119 | 15.8527 | 14.4744 | 14.9429 | 14.9026 | 15.4497 | 13.3174 | 13.4294 | 13.9992 |  |  |  | 16.5717 | 15.9019 | 14.9957 | 32.9036 | 35.6377 | 55.6412 | 17.2201 | 16.3068 | 15.0868 | 16.8323 | 16.1143 | 15.1071 | 11.2994 | 50.7663 |  | 16.3281 | 24.3939 | 29.2846 | 12.877 |  | 6.3553 | 6.4201 | 5.9869 | 6.1779 | 6.3342 | 6.9695 | 12.4233 | 4.6538 | 6.4002 | 4.3405 | 6.6213 | 8.1113 | 42.2618 | 46.4926 | 42.9817 | 14.6559 |  |  | 0.019275 | 0.39501 | 0.42832 | 0.02037 | 0.23607 | 0.18156 | 0.46251 | 0.4033 | -0.6554 | -0.2597 | -0.13125 | 8.8689 | 8.87 | 2.006 | 15.7697 | 16.6344 | 17.1853 | 17.5201 | 17.4862 | 16.4634 | 14.8205 | 16.8303 | 17.1733 | 17.4757 | 17.5271 | 17.2655 | 16.457 | 14.6791 | 8.9217 | 8.8529 | 7.6729 | 7.1078 | 6.0175 | 6.7787 | 7.6712 | 15.8135 | 15.4185 | 15.2824 | 14.2153 | 14.1154 | 14.0596 |  |  |  | 11.1691 | 39.7849 | 25.6677 | 12.8223 | 0.054548 | 0.013011 | 13.6363 |  |  | 10.6249 |  |  | 16.8604 | 16.0552 | 15.0171 | 16.3597 | 15.6425 | 14.7393 | 27.1723 | 37.1628 | 21.4822 | 22.0767 | 10.9974 |  | 11.0136 | 13.8246 | 10.635 | 12.2794 | 11.7645 | 35.5734 |  | 14.1473 |  |  | 12.0025 | 12.7473 | 13.5344 | [6 empty] | 13.6914 |  |  | 13.9146 |  |  | 10.0953 | 12.1837 | 57.5172 | 7.8724 | 10.3189 | 28.709 | 8.2869 | 10.5531 | 33.5833 | 10.5519 | 18.4764 | 8.3845 | 17.7501 | 8.7298 | 17.6652 | 8.3356 | 11.2042 | 28.851 | 11.3405 | 11.628 | 43.91 | 8.6341 | 11.0107 | 33.9922 | 8.726 | 18.0707 | 10.4532 | 16.1277 | 8.9829 | 18.2072 | 0.016551 | 20.9501 | 0.043869 | 0.04719 | -37.756 | 3.1202 | 13.56 | 50.31 | 0.17544 | 0.73235 | 0.7626 | 0.16631 | 0.56671 | 0.49699 | 0.79323 | 0.37016 | 0.27914 | 0.35933 | 0.11005 | 0.35242 | 0.32737 | 0.32459
42810.4408 | 64 | 18.5395 | 18.5775 | 18.5618 | 18.5732 | 17.906 | 16.5249 | 14.5751 | 16.6715 | 17.1722 | 17.2647 | 17.2818 | 16.8186 | 15.8498 | 14.4734 | 14.9322 | 14.898 | 15.4417 | 13.3075 | 13.4266 | 13.9907 |  |  |  | 16.5689 | 15.8883 | 14.993 | 33.4102 | 36.0785 | 56.0373 | 17.227 | 16.3137 | 15.0878 | 16.8346 | 16.1134 | 15.1115 | 11.3135 | 51.2041 |  | 16.4444 | 24.7987 | 29.8258 | 12.953 |  | 6.3378 | 6.4242 | 5.9829 | 6.1672 | 6.3296 | 7.0228 | 12.5298 | 4.5594 | 6.401 | 4.3841 | 6.6228 | 8.1103 | 42.2293 | 46.5062 | 42.9732 | 14.6837 |  |  | -0.082577 | -0.032109 | 0.15036 | 0.16494 | 0.16313 | 0.02254 | 0.33963 | 0.64841 | -0.64508 | -0.59013 | -0.23934 | 8.8684 | 8.8695 | 2.0062 | 15.7669 | 16.6295 | 17.1713 | 17.5076 | 17.4767 | 16.4537 | 14.8116 | 16.8217 | 17.1684 | 17.4728 | 17.5179 | 17.2587 | 16.4491 | 14.6806 | 9.3974 | 9.0374 | 7.7674 | 7.1728 | 6.1335 | 6.7985 | 7.6898 | 15.819 | 15.4196 | 15.2832 | 14.2193 | 14.119 | 14.066 |  |  |  | 11.1927 | 40.1348 | 25.6561 | 12.9539 | -0.0029902 | -0.082407 | 13.648 |  |  | 10.6305 |  |  | 16.8646 | 16.0615 | 15.0258 | 16.3594 | 15.6357 | 14.7355 | 27.6804 | 37.7236 | 21.8578 | 22.4635 | 11.129 |  | 11.019 | 13.529 | 10.6432 | 12.3489 | 11.779 | 35.8578 |  | 14.2121 |  |  | 12.0046 | 12.759 | 13.5398 | [6 empty] | 13.726 |  |  | 13.9577 |  |  | 10.1108 | 12.2421 | 58.0101 | 7.8868 | 10.3329 | 29.0563 | 8.2962 | 10.5774 | 33.9329 | 10.5815 | 18.6887 | 8.3812 | 17.9676 | 8.747 | 17.9017 | 8.346 | 11.2115 | 29.2459 | 11.3528 | 11.6503 | 44.3604 | 8.6399 | 11.0189 | 34.3788 | 8.7295 | 18.2614 | 10.4718 | 16.4167 | 8.997 | 18.4364 | 0.11824 | 20.9504 | 0.045224 | 0.046952 | -37.7916 | 3.1202 | 21.97 | 49.04 | -0.36334 | -0.2088 | 0.45184 | 0.47323 | 0.47113 | 0.17513 | 0.6798 | 0.36668 | 0.28762 | 0.35788 | 0.059487 | 0.34409 | 0.32573 | 0.32172
42810.4408 | 65 | 18.547 | 18.5831 | 18.5689 | 18.5751 | 17.9127 | 16.5356 | 14.585 | 16.6833 | 17.1787 | 17.2719 | 17.2907 | 16.8178 | 15.8563 | 14.4813 | 14.9423 | 14.8888 | 15.4409 | 13.3062 | 13.4239 | 13.9865 |  |  |  | 16.5664 | 15.8894 | 14.9953 | 33.8352 | 36.6224 | 56.3416 | 17.2353 | 16.3155 | 15.0971 | 16.843 | 16.1186 | 15.1193 | 11.3312 | 51.396 |  | 16.5594 | 25.218 | 30.3508 | 13.1006 |  | 6.3382 | 6.4316 | 5.9885 | 6.1714 | 6.341 | 7.0366 | 12.6418 | 4.4863 | 6.3937 | 4.3314 | 6.6159 | 8.116 | 42.2258 | 46.5179 | 42.9636 | 14.7265 |  |  | -0.070093 | -0.032109 | 0.29098 | 0.32527 | 0.29981 | -0.047772 | 0.33437 | 0.3941 | -0.67019 | -0.29704 | -0.291 | 8.8714 | 8.8723 | 2.0067 | 15.7784 | 16.6417 | 17.1776 | 17.5208 | 17.4872 | 16.4587 | 14.8216 | 16.8286 | 17.1745 | 17.4682 | 17.5233 | 17.2702 | 16.4521 | 14.6879 | 9.9314 | 9.0368 | 7.9537 | 7.244 | 6.4572 | 6.8316 | 7.7061 | 15.8222 | 15.4184 | 15.2864 | 14.2207 | 14.1219 | 14.0672 |  |  |  | 11.2037 | 40.4008 | 25.763 | 13.0823 | 0.16922 | -0.03291 | 13.6486 |  |  | 10.6322 |  |  | 16.8656 | 16.0618 | 15.0288 | 16.3591 | 15.6349 | 14.7387 | 28.145 | 38.3011 | 22.2391 | 22.8683 | 11.4198 |  | 11.0375 | 13.0519 | 10.6665 | 12.402 | 11.8057 | 36.239 |  | 14.2787 |  |  | 11.9963 | 12.7702 | 13.6789 | [6 empty] | 13.754 |  |  | 14.004 |  |  | 10.1216 | 12.2824 | 58.4763 | 7.9069 | 10.3394 | 29.3954 | 8.3056 | 10.5919 | 34.2719 | 10.6001 | 18.8562 | 8.3715 | 18.2034 | 8.7585 | 18.1371 | 8.3613 | 11.2232 | 29.6452 | 11.3648 | 11.6818 | 44.7324 | 8.652 | 11.0254 | 34.7497 | 8.7425 | 18.5113 | 10.4884 | 16.6747 | 9.0054 | 18.6213 | 0.035041 | 20.9493 | 0.047117 | 0.04664 | -37.8045 | 3.1202 | 21.1 | 49.23 | -0.33491 | -0.2088 | 0.62857 | 0.66458 | 0.63872 | -0.25496 | 0.67454 | 0.35921 | 0.30164 | 0.35728 | 0.003987 | 0.32528 | 0.32221 | 0.31851
42810.4408 | 66 | 18.5525 | 18.5854 | 18.5729 | 18.5835 | 17.912 | 16.5341 | 14.5931 | 16.6842 | 17.1804 | 17.2746 | 17.2893 | 16.8232 | 15.8554 | 14.4805 | 14.9487 | 14.895 | 15.4473 | 13.3082 | 13.4294 | 13.9888 |  |  |  | 16.5659 | 15.8928 | 14.9966 | 34.3365 | 37.1161 | 57.3488 | 17.2357 | 16.3165 | 15.0963 | 16.8433 | 16.118 | 15.1136 | 11.3557 | 51.3842 |  | 16.6613 | 25.6201 | 30.8042 | 13.1669 |  | 6.3347 | 6.4375 | 5.9828 | 6.1728 | 6.3378 | 7.0166 | 12.7002 | 4.4958 | 6.3903 | 4.2895 | 6.6167 | 8.1128 | 42.2189 | 46.5078 | 42.954 | 14.7612 |  |  | 0.010075 | 0.079599 | 0.64385 | 0.19385 | 0.085588 | -0.33099 | 0.2312 | 0.32576 | -0.40475 | -2.2681 | -0.23398 | 8.8695 | 8.8707 | 2.0072 | 15.7711 | 16.6298 | 17.1799 | 17.514 | 17.4829 | 16.4566 | 14.8086 | 16.8222 | 17.1668 | 17.4667 | 17.5232 | 17.2583 | 16.4471 | 14.6766 | 10.3375 | 8.9736 | 7.8514 | 7.1643 | 6.5633 | 6.8483 | 7.7072 | 15.8227 | 15.4147 | 15.2741 | 14.2181 | 14.1202 | 14.0593 |  |  |  | 11.2279 | 40.9197 | 26.4632 | 13.2161 | 0.049078 | -0.13642 | 13.661 |  |  | 10.6257 |  |  | 16.8591 | 16.0536 | 15.0253 | 16.3508 | 15.6336 | 14.7351 | 28.626 | 38.8071 | 22.5956 | 23.2516 | 11.6877 |  | 11.0667 | 12.6989 | 10.6868 | 12.4392 | 11.8319 | 36.2744 |  | 14.3464 |  |  | 11.9866 | 12.7794 | 13.8759 | [6 empty] | 13.7843 |  |  | 14.0438 |  |  | 10.133 | 12.3339 | 58.9849 | 7.9239 | 10.3357 | 29.7832 | 8.3086 | 10.5992 | 34.6789 | 10.6197 | 19.0029 | 8.3611 | 18.456 | 8.7771 | 18.3414 | 8.374 | 11.2332 | 30.0342 | 11.3733 | 11.707 | 45.193 | 8.6504 | 11.0329 | 35.1624 | 8.7466 | 18.804 | 10.5057 | 16.9464 | 9.013 | 18.8203 | 0.047175 | 20.9491 | 0.049315 | 0.046459 | -37.7716 | 3.1201 | 29.14 | 49.95 | 0.12717 | 0.32876 | 0.93502 | 0.51305 | 0.34126 | -0.67109 | 0.56088 | 0.35273 | 0.31212 | 0.35711 | -0.039186 | 0.33678 | 0.32118 | 0.3156
42810.4408 | 67 | 18.5481 | 18.583 | 18.5642 | 18.5841 | 17.9112 | 16.5234 | 14.5881 | 16.681 | 17.1758 | 17.2814 | 17.2928 | 16.824 | 15.8564 | 14.4865 | 14.948 | 14.9031 | 15.4481 | 13.3118 | 13.4319 | 13.9983 |  |  |  | 16.5693 | 15.8949 | 15.0023 | 34.8834 | 37.5522 | 57.8399 | 17.24 | 16.3121 | 15.0905 | 16.8445 | 16.1193 | 15.1138 | 11.3702 | 51.8593 |  | 16.774 | 25.9778 | 31.2954 | 13.1646 |  | 6.3483 | 6.4455 | 5.9971 | 6.1804 | 6.3442 | 6.9971 | 12.6139 | 4.5218 | 6.4006 | 4.2616 | 6.6212 | 8.1174 | 42.1997 | 46.4968 | 42.9359 | 14.7978 |  |  | -0.35331 | -0.13002 | 0.11684 | 0.22999 | 0.025792 | -0.47227 | 0.45068 | 0.19368 | -0.3382 | -0.93777 | -0.23219 | 8.8696 | 8.8709 | 2.007 | 15.7732 | 16.6306 | 17.1773 | 17.5194 | 17.4831 | 16.4571 | 14.8104 | 16.8219 | 17.1664 | 17.4737 | 17.5245 | 17.2568 | 16.4579 | 14.6735 | 10.3808 | 9.1563 | 7.4613 | 7.1009 | 6.5584 | 6.8666 | 7.7085 | 15.8298 | 15.4155 | 15.2748 | 14.222 | 14.1239 | 14.063 |  |  |  | 11.244 | 41.1683 | 27.0846 | 13.3286 | -0.25928 | -0.1861 | 13.6918 |  |  | 10.616 |  |  | 16.8546 | 16.0488 | 15.0231 | 16.3449 | 15.6282 | 14.7339 | 29.1975 | 39.3394 | 22.8967 | 23.5963 | 11.9114 |  | 11.0791 | 12.6705 | 10.7142 | 12.4951 | 11.8543 | 36.1425 |  | 14.4193 |  |  | 12.0001 | 12.7832 | 13.9256 | [6 empty] | 13.8242 |  |  | 14.0848 |  |  | 10.1374 | 12.387 | 59.523 | 7.9379 | 10.3278 | 30.1722 | 8.3004 | 10.6319 | 35.1712 | 10.6439 | 19.1656 | 8.3587 | 18.7123 | 8.7895 | 18.5909 | 8.3835 | 11.23 | 30.4529 | 11.384 | 11.7297 | 45.5912 | 8.6541 | 11.0485 | 35.6317 | 8.7458 | 19.0873 | 10.5178 | 17.1876 | 9.0283 | 19.0405 | 0.016551 | 20.9505 | 0.052615 | 0.046228 | -37.7612 | 3.1202 | 27.61 | 48.49 | -0.75362 | -0.42018 | 0.39832 | 0.55884 | 0.18733 | -0.80159 | 0.78306 | 0.34693 | 0.31381 | 0.3563 | -0.041877 | 0.38027 | 0.32172 | 0.313
42810.4408 | 68 | 18.5552 | 18.5851 | 18.5649 | 18.5892 | 17.9075 | 16.5405 | 14.5873 | 16.6777 | 17.1819 | 17.2738 | 17.2884 | 16.8281 | 15.864 | 14.4859 | 14.9541 | 14.9089 | 15.4537 | 13.3122 | 13.4279 | 14.0006 |  |  |  | 16.5648 | 15.892 | 15.006 | 35.4621 | 37.9337 | 58.1133 | 17.229 | 16.3075 | 15.0982 | 16.841 | 16.1149 | 15.1046 | 11.3826 | 52.0723 |  | 16.8771 | 26.3279 | 31.8136 | 13.0616 |  | 6.3553 | 6.4467 | 5.9985 | 6.1675 | 6.3658 | 6.9842 | 12.4594 | 4.4722 | 6.3894 | 4.3075 | 6.6166 | 8.1038 | 42.1859 | 46.4827 | 42.9051 | 14.8144 |  |  | 0.040959 | -0.024881 | 0.11619 | 0.21488 | 0.12304 | -0.026744 | 0.13921 | 0.068176 | 0.28043 | -0.2169 | -0.13125 | 8.8691 | 8.8702 | 2.0071 | 15.7797 | 16.6366 | 17.1787 | 17.5152 | 17.4801 | 16.4625 | 14.8161 | 16.8229 | 17.1698 | 17.4754 | 17.5262 | 17.2642 | 16.4642 | 14.6736 | 9.7842 | 8.9518 | 7.2812 | 7.0548 | 6.5383 | 6.8729 | 7.7107 | 15.8331 | 15.4148 | 15.2832 | 14.221 | 14.1246 | 14.0634 |  |  |  | 11.2712 | 41.6513 | 27.7188 | 13.4343 | -0.31722 | -0.32933 | 13.747 |  |  | 10.613 |  |  | 16.8612 | 16.0497 | 15.0265 | 16.3529 | 15.6324 | 14.745 | 29.8307 | 39.9074 | 23.1945 | 23.8708 | 12.1068 |  | 11.0913 | 13.3461 | 10.7492 | 12.6327 | 11.8726 | 36.1239 |  | 14.4839 |  |  | 12.0042 | 12.7817 | 13.8871 | [6 empty] | 13.8783 |  |  | 14.1296 |  |  | 10.1444 | 12.4397 | 60.1883 | 7.9488 | 10.3257 | 30.5419 | 8.3004 | 10.6776 | 35.5803 | 10.6578 | 19.4219 | 8.3543 | 18.9383 | 8.7913 | 18.8683 | 8.3906 | 11.2192 | 30.8963 | 11.3987 | 11.7611 | 45.9115 | 8.6626 | 11.0636 | 35.9408 | 8.7526 | 19.3601 | 10.533 | 17.4015 | 9.0396 | 19.2688 | 0.11632 | 20.9502 | 0.055519 | 0.048225 | -37.744 | 3.1202 | 31.51 | 48.79 | 0.2567 | -0.18381 | 0.3972 | 0.54017 | 0.40915 | -0.19075 | 0.43519 | 0.3419 | 0.29619 | 0.35308 | 0.025138 | 0.40054 | 0.32499 | 0.31096
42810.4408 | 69 | 18.5447 | 18.5878 | 18.5615 | 18.5809 | 17.9049 | 16.5261 | 14.5888 | 16.6757 | 17.1763 | 17.2675 | 17.2876 | 16.8161 | 15.8518 | 14.4841 | 14.9472 | 14.9076 | 15.4574 | 13.3113 | 13.4272 | 13.997 |  |  |  | 16.5643 | 15.8845 | 14.9956 | 35.9664 | 38.2567 | 58.0852 | 17.2364 | 16.3109 | 15.1033 | 16.8428 | 16.1105 | 15.1088 | 11.3984 | 52.327 |  | 16.9844 | 26.7097 | 32.283 | 12.9312 |  | 6.3619 | 6.4479 | 6.01 | 6.1782 | 6.3808 | 6.9872 | 12.3116 | 4.4135 | 6.39 | 4.3245 | 6.6164 | 8.1174 | 42.1813 | 46.4812 | 42.9008 | 14.8569 |  |  | -0.19495 | -0.055765 | 0.30807 | 0.11368 | 0.29718 | -0.047772 | -0.16109 | 0.12469 | -0.69704 | -0.16088 | -0.29816 | 8.8707 | 8.8719 | 2.0071 | 15.7788 | 16.6418 | 17.1832 | 17.5192 | 17.476 | 16.4571 | 14.8129 | 16.824 | 17.1716 | 17.4789 | 17.5233 | 17.263 | 16.4634 | 14.6743 | 9.1791 | 8.73 | 7.0347 | 7.0486 | 6.6434 | 6.8889 | 7.7219 | 15.8379 | 15.42 | 15.2865 | 14.2203 | 14.1226 | 14.0688 |  |  |  | 11.2973 | 42.1257 | 28.0482 | 13.4577 | -0.32006 | -0.11101 | 13.8152 |  |  | 10.6098 |  |  | 16.8596 | 16.0493 | 15.0283 | 16.3561 | 15.6364 | 14.7435 | 30.4419 | 40.551 | 23.4981 | 24.1118 | 12.2896 |  | 11.1002 | 14.3415 | 10.7748 | 12.8067 | 11.8993 | 36.6292 |  | 14.5625 |  |  | 12.0032 | 12.785 | 13.8794 | [6 empty] | 13.9337 |  |  | 14.1584 |  |  | 10.1526 | 12.4933 | 60.7607 | 7.9556 | 10.332 | 30.9099 | 8.309 | 10.7083 | 35.9406 | 10.6853 | 19.7963 | 8.3697 | 19.1296 | 8.8006 | 19.098 | 8.3963 | 11.2083 | 31.3957 | 11.4015 | 11.7867 | 46.3304 | 8.6707 | 11.0721 | 36.3226 | 8.7503 | 19.6271 | 10.5477 | 17.6461 | 9.0472 | 19.5339 | 0.018477 | 20.9497 | 0.057683 | 0.048283 | -37.7241 | 3.1202 | 43.87 | 47.59 | -0.56 | -0.27518 | 0.64678 | 0.3929 | 0.63586 | -0.25494 | -0.46815 | 0.33712 | 0.26939 | 0.34913 | 0.094232 | 0.42922 | 0.32914 | 0.31117
42810.4408 | 70 | 18.5466 | 18.5807 | 18.563 | 18.5784 | 17.9051 | 16.5264 | 14.5828 | 16.6729 | 17.1766 | 17.2709 | 17.2904 | 16.8115 | 15.8522 | 14.4802 | 14.947 | 14.9034 | 15.4442 | 13.3071 | 13.4236 | 13.9907 |  |  |  | 16.5616 | 15.8838 | 14.9976 | 36.3956 | 38.5784 | 58.7628 | 17.2394 | 16.3139 | 15.0939 | 16.8396 | 16.1182 | 15.1115 | 11.4095 | 52.6484 |  | 17.0958 | 27.116 | 32.6973 | 12.7941 |  | 6.3871 | 6.4627 | 6.0248 | 6.1974 | 6.3845 | 6.996 | 12.1697 | 4.3971 | 6.396 | 4.3245 | 6.6211 | 8.1154 | 42.1873 | 46.4854 | 42.8838 | 14.8939 |  |  | -0.035921 | 0.069743 | 0.064276 | -0.097254 | -0.025464 | -0.094428 | -0.213 | 0.093148 | -0.12336 | -0.36543 | -0.40029 | 8.8673 | 8.8689 | 2.0072 | 15.7793 | 16.6409 | 17.1853 | 17.5167 | 17.4725 | 16.4512 | 14.8168 | 16.8248 | 17.1773 | 17.476 | 17.5288 | 17.2597 | 16.4584 | 14.6725 | 8.4851 | 8.609 | 6.7713 | 7.0044 | 6.7371 | 6.8718 | 7.7054 | 15.8364 | 15.4245 | 15.2847 | 14.2212 | 14.1213 | 14.0649 |  |  |  | 11.3165 | 42.5344 | 28.2265 | 13.4715 | -0.19789 | -0.0235 | 13.8931 |  |  | 10.6075 |  |  | 16.8559 | 16.0498 | 15.0296 | 16.3587 | 15.6327 | 14.7402 | 30.9762 | 41.1842 | 23.7873 | 24.3726 | 12.4718 |  | 11.1234 | 15.7121 | 10.8217 | 13.0245 | 11.9352 | 37.8629 |  | 14.6418 |  |  | 12.012 | 12.7766 | 14.0086 | [6 empty] | 13.9953 |  |  | 14.1891 |  |  | 10.1479 | 12.551 | 61.1877 | 7.9516 | 10.3872 | 31.2568 | 8.3248 | 10.7091 | 36.2267 | 10.7137 | 20.1069 | 8.3732 | 19.3006 | 8.8074 | 19.2916 | 8.4061 | 11.2033 | 31.8461 | 11.4113 | 11.8251 | 46.861 | 8.6778 | 11.0829 | 36.7242 | 8.7587 | 19.909 | 10.5696 | 18.0492 | 9.0647 | 19.8123 | 0.06239 | 20.9429 | 0.060059 | 0.047161 | -37.7568 | 3.1203 | 19.69 | 45.59 | -0.24063 | 0.30775 | 0.29544 | -0.36341 | -0.18613 | -0.35843 | -0.53834 | 0.33282 | 0.23286 | 0.34427 | 0.16936 | 0.45657 | 0.33331 | 0.31142
42810.4409 | 71 | 18.5497 | 18.582 | 18.5713 | 18.5824 | 17.9062 | 16.5296 | 14.589 | 16.6801 | 17.1802 | 17.2711 | 17.2859 | 16.8152 | 15.8564 | 14.4842 | 14.9569 | 14.9082 | 15.4525 | 13.318 | 13.4327 | 14.0022 |  |  |  | 16.575 | 15.8955 | 15.0063 | 36.8898 | 38.9079 | 59.4353 | 17.2393 | 16.3222 | 15.0994 | 16.8409 | 16.118 | 15.1209 | 11.4248 | 53.0277 |  | 17.2031 | 27.5587 | 33.1272 | 12.7346 |  | 6.3844 | 6.4677 | 6.0259 | 6.196 | 6.3789 | 6.9738 | 12.0481 | 4.3372 | 6.3836 | 4.366 | 6.618 | 8.1138 | 42.2127 | 46.5024 | 42.8734 | 14.9138 |  |  | -0.29745 | -0.094537 | -0.094088 | -0.14062 | -0.060948 | -0.4519 | -0.016528 | -0.075732 | -0.2374 | -1.6184 | -0.20656 | 8.8712 | 8.8721 | 2.0067 | 15.7702 | 16.636 | 17.1787 | 17.5091 | 17.4707 | 16.4437 | 14.811 | 16.8217 | 17.1644 | 17.4662 | 17.5185 | 17.2568 | 16.4522 | 14.6663 | 7.9471 | 8.5378 | 6.6256 | 7.0717 | 6.8713 | 6.881 | 7.7097 | 15.841 | 15.4271 | 15.2871 | 14.2243 | 14.1201 | 14.0622 |  |  |  | 11.3302 | 42.9106 | 28.4789 | 13.464 | -0.11705 | 0.0068 | 13.973 |  |  | 10.6079 |  |  | 16.8612 | 16.0507 | 15.0308 | 16.3548 | 15.6338 | 14.7389 | 31.4737 | 41.6719 | 24.0984 | 24.6818 | 12.6501 |  | 11.1317 | 17.1592 | 10.8543 | 13.4019 | 11.9539 | 38.5456 |  | 14.7012 |  |  | 12.0052 | 12.7677 | 14.3565 | [6 empty] | 14.0729 |  |  | 14.1984 |  |  | 10.1695 | 12.6228 | 61.5803 | 7.9671 | 10.4806 | 31.5809 | 8.3374 | 10.7215 | 36.5378 | 10.7506 | 20.2582 | 8.3796 | 19.5188 | 8.8281 | 19.5396 | 8.3983 | 11.1954 | 32.2366 | 11.4256 | 11.8767 | 47.3371 | 8.6859 | 11.0789 | 37.0725 | 8.7707 | 20.1305 | 10.5841 | 18.3451 | 9.0713 | 20.0994 | 0.099177 | 20.9429 | 0.063181 | 0.046952 | -37.7555 | 3.1203 | 29.52 | 45.69 | -0.69315 | -0.3583 | -0.35745 | -0.43699 | -0.28795 | -0.78409 | -0.14995 | 0.32815 | 0.19374 | 0.3344 | 0.2302 | 0.47326 | 0.33547 | 0.31208
42810.4409 | 72 | 18.5495 | 18.5848 | 18.5724 | 18.5885 | 17.9064 | 16.5261 | 14.5914 | 16.6763 | 17.1794 | 17.2677 | 17.2832 | 16.8204 | 15.852 | 14.4816 | 14.9543 | 14.9042 | 15.4592 | 13.3175 | 13.4304 | 13.9935 |  |  |  | 16.5744 | 15.8987 | 14.9996 | 37.4388 | 39.2688 | 60.9003 | 17.2473 | 16.3245 | 15.1062 | 16.8534 | 16.1218 | 15.1175 | 11.4421 | 53.1081 |  | 17.3117 | 28.0187 | 33.5924 | 12.6433 |  | 6.3765 | 6.4697 | 6.0245 | 6.1786 | 6.3614 | 6.9439 | 12.0224 | 4.3563 | 6.382 | 4.3252 | 6.6147 | 8.1305 | 42.2366 | 46.5281 | 42.8634 | 14.9416 |  |  | -0.062205 | -0.051169 | 0.15036 | 0.26482 | -0.099716 | -0.28893 | -0.14335 | 0.01692 | -0.18738 | 0.20942 | -0.21113 | 8.8696 | 8.8711 | 2.0064 | 15.7817 | 16.6476 | 17.1863 | 17.5136 | 17.484 | 16.4532 | 14.8139 | 16.832 | 17.1758 | 17.4742 | 17.5241 | 17.2653 | 16.4586 | 14.6745 | 7.479 | 8.4737 | 6.4705 | 7.071 | 6.9987 | 6.887 | 7.7151 | 15.8553 | 15.4388 | 15.3 | 14.2358 | 14.1246 | 14.078 |  |  |  | 11.3579 | 43.2668 | 28.6523 | 13.4944 | -0.19323 | -0.13021 | 14.0532 |  |  | 10.5903 |  |  | 16.8645 | 16.0524 | 15.0358 | 16.3557 | 15.6404 | 14.7449 | 31.9747 | 42.2706 | 24.4358 | 25.0046 | 12.9338 |  | 11.1585 | 16.89 | 10.9062 | 13.915 | 11.986 | 38.7946 |  | 14.7747 |  |  | 11.9999 | 12.7715 | 14.4444 | [6 empty] | 14.1953 |  |  | 14.2213 |  |  | 10.1873 | 12.7147 | 62.0916 | 7.9839 | 10.5893 | 32.0168 | 8.3507 | 10.7341 | 37.0394 | 10.7716 | 20.4512 | 8.3908 | 19.8622 | 8.8409 | 19.7758 | 8.3986 | 11.1966 | 32.5301 | 11.4451 | 11.9078 | 47.8558 | 8.6888 | 11.101 | 37.444 | 8.7419 | 20.3558 | 10.6028 | 18.6098 | 9.0835 | 20.3573 | -0.087453 | 20.9411 | 0.066492 | 0.046684 | -37.723 | 3.1203 | 16.17 | 50.13 | -0.31768 | -0.26361 | 0.45187 | 0.59969 | -0.3683 | -0.62693 | -0.44159 | 0.32115 | 0.20293 | 0.32121 | 0.28292 | 0.49112 | 0.33857 | 0.31215
42810.4409 | 73 | 18.5534 | 18.5837 | 18.5676 | 18.5862 | 17.9022 | 16.5255 | 14.5907 | 16.6703 | 17.1769 | 17.2747 | 17.2863 | 16.8189 | 15.8515 | 14.4816 | 14.9479 | 14.8989 | 15.4514 | 13.3076 | 13.4263 | 13.9826 |  |  |  | 16.562 | 15.8807 | 14.9926 | 38.164 | 39.6823 | 61.9045 | 17.2443 | 16.3225 | 15.1082 | 16.8487 | 16.1145 | 15.1153 | 11.437 | 53.2331 |  | 17.4126 | 28.4651 | 34.0311 | 12.4506 |  | 6.391 | 6.4682 | 6.0206 | 6.1725 | 6.3492 | 6.9672 | 12.4532 | 4.3428 | 6.3842 | 4.3106 | 6.6108 | 8.1224 | 42.262 | 46.5496 | 42.8367 | 14.9644 |  |  | -0.14041 | -0.22399 | 0.092532 | -0.37719 | 0.06062 | -0.54521 | 0.30809 | 0.12403 | -0.92725 | -0.39795 | -0.40824 | 8.8676 | 8.8687 | 2.0061 | 15.7883 | 16.6435 | 17.185 | 17.5116 | 17.4796 | 16.4444 | 14.8115 | 16.8246 | 17.1759 | 17.4759 | 17.5242 | 17.2582 | 16.4525 | 14.6684 | 7.1707 | 8.3618 | 6.3292 | 7.0296 | 6.9874 | 6.876 | 7.7107 | 15.8463 | 15.4294 | 15.2818 | 14.2305 | 14.1209 | 14.0618 |  |  |  | 11.3716 | 43.5861 | 29.0646 | 13.5146 | -0.17236 | -0.0075032 | 14.1044 |  |  | 10.56 |  |  | 16.8651 | 16.0489 | 15.0367 | 16.3605 | 15.6368 | 14.7435 | 32.41 | 42.8136 | 24.7514 | 25.2977 | 13.0131 |  | 11.1775 | 16.2981 | 10.9406 | 14.3379 | 12.0149 | 38.61 |  | 14.8531 |  |  | 12.0214 | 12.785 | 14.393 | [6 empty] | 14.2964 |  |  | 14.251 |  |  | 10.1861 | 12.7666 | 62.3233 | 7.9898 | 10.6004 | 32.4568 | 8.3553 | 10.7451 | 37.5522 | 10.8001 | 20.6756 | 8.3959 | 19.9299 | 8.8465 | 19.9946 | 8.3745 | 11.1982 | 32.9425 | 11.4488 | 11.9439 | 48.2033 | 8.7032 | 11.1036 | 37.8798 | 8.7009 | 20.5671 | 10.616 | 18.8626 | 9.0922 | 20.5502 | 0.040049 | 20.9385 | 0.069856 | 0.04761 | -37.7822 | 3.1204 | 36.33 | 49.45 | -0.47799 | -0.55152 | 0.35448 | -0.71569 | 0.28717 | -0.86123 | 0.6474 | 0.31957 | 0.22051 | 0.31042 | 0.31589 | 0.50631 | 0.34376 | 0.31204
42810.4409 | 74 | 18.5653 | 18.5929 | 18.5771 | 18.5918 | 17.9095 | 16.5295 | 14.5986 | 16.6859 | 17.1848 | 17.2787 | 17.2907 | 16.8242 | 15.8628 | 14.4827 | 14.9484 | 14.9065 | 15.4497 | 13.319 | 13.4288 | 13.9953 |  |  |  | 16.5728 | 15.9049 | 15.0128 | 38.681 | 40.0499 | 61.782 | 17.2462 | 16.3201 | 15.1089 | 16.8459 | 16.1175 | 15.1149 | 11.449 | 53.6456 |  | 17.51 | 28.8249 | 34.4693 | 12.2796 |  | 6.3866 | 6.4665 | 6.029 | 6.1635 | 6.3323 | 7.0179 | 12.7035 | 4.3394 | 6.3817 | 4.2967 | 6.6188 | 8.1295 | 42.2736 | 46.5592 | 42.8131 | 14.9812 |  |  | 0.003503 | -0.18456 | 0.08596 | -0.059142 | -0.13454 | -0.53798 | 0.49011 | -0.004108 | -0.19458 | -0.47957 | -0.24709 | 8.8704 | 8.8716 | 2.0056 | 15.7872 | 16.642 | 17.1826 | 17.5153 | 17.482 | 16.4464 | 14.8183 | 16.825 | 17.1738 | 17.4781 | 17.5205 | 17.2589 | 16.4571 | 14.6685 | 6.9343 | 8.351 | 6.16 | 7.1127 | 7.0448 | 6.8845 | 7.7168 | 15.8465 | 15.4289 | 15.2823 | 14.2304 | 14.1201 | 14.0617 |  |  |  | 11.3861 | 43.8489 | 29.6402 | 13.6121 | -0.060934 | -0.024253 | 14.133 |  |  | 10.5361 |  |  | 16.8697 | 16.0487 | 15.0438 | 16.3593 | 15.6325 | 14.7374 | 32.7959 | 43.3341 | 25.0472 | 25.5975 | 13.064 |  | 11.1994 | 15.7048 | 10.9714 | 14.5621 | 12.0468 | 39.0022 |  | 14.932 |  |  | 11.993 | 12.7823 | 14.3221 | [6 empty] | 14.3478 |  |  | 14.2765 |  |  | 10.205 | 12.8097 | 62.8711 | 8.0028 | 10.597 | 32.8336 | 8.3514 | 10.7384 | 37.9487 | 10.8181 | 20.935 | 8.3738 | 19.957 | 8.856 | 20.2285 | 8.3449 | 11.2124 | 33.3757 | 11.4733 | 11.9805 | 48.5265 | 8.7059 | 11.1154 | 38.3954 | 8.6852 | 20.8419 | 10.6536 | 19.1796 | 9.1153 | 20.6539 | 0.037545 | 20.9296 | 0.072851 | 0.047386 | -37.7867 | 3.1203 | 19.84 | 48.91 | 0.075486 | -0.50063 | 0.34166 | -0.2834 | -0.42787 | -0.85558 | 0.81662 | 0.31888 | 0.238 | 0.30524 | 0.34315 | 0.52582 | 0.3489 | 0.30982
42810.4409 | 75 | 18.5601 | 18.5915 | 18.5738 | 18.5867 | 17.9151 | 16.5323 | 14.5872 | 16.6802 | 17.1824 | 17.2761 | 17.2906 | 16.8224 | 15.8615 | 14.4851 | 14.9602 | 14.907 | 15.4522 | 13.318 | 13.4367 | 13.9886 |  |  |  | 16.5669 | 15.8914 | 15.0151 | 39.0555 | 40.4604 | 61.6734 | 17.2396 | 16.3271 | 15.1007 | 16.8368 | 16.1161 | 15.1181 | 11.46 | 53.9707 |  | 17.6222 | 29.1134 | 34.9015 | 12.1143 |  | 6.3892 | 6.4777 | 6.0145 | 6.1572 | 6.3102 | 6.9964 | 12.6047 | 4.3746 | 6.3783 | 4.2659 | 6.6283 | 8.1224 | 42.2767 | 46.5541 | 42.7852 | 14.9993 |  |  | -0.083893 | -0.13265 | 0.1359 | -0.059142 | -0.13652 | -0.32179 | 0.31532 | 0.20946 | -0.2228 | 0.080181 | -0.17119 | 8.8717 | 8.8727 | 2.0058 | 15.7883 | 16.6459 | 17.1839 | 17.5191 | 17.478 | 16.4522 | 14.8244 | 16.8343 | 17.1745 | 17.4763 | 17.5287 | 17.2603 | 16.457 | 14.6733 | 6.9231 | 8.3363 | 5.9954 | 7.0891 | 7.1104 | 6.8845 | 7.7096 | 15.8481 | 15.425 | 15.2962 | 14.2333 | 14.1247 | 14.0667 |  |  |  | 11.4075 | 44.4644 | 29.9732 | 13.7866 | 0.097905 | 0.022232 | 14.1493 |  |  | 10.5268 |  |  | 16.8647 | 16.0532 | 15.0441 | 16.3586 | 15.6372 | 14.7427 | 33.2325 | 43.8978 | 25.3391 | 25.9113 | 13.0962 |  | 11.2053 | 15.0929 | 10.9753 | 14.5299 | 12.0654 | 39.5124 |  | 15.0252 |  |  | 12.0097 | 12.7993 | 14.2746 | [6 empty] | 14.3867 |  |  | 14.3277 |  |  | 10.2099 | 12.8612 | 63.308 | 8.0094 | 10.5962 | 33.1494 | 8.3693 | 10.7658 | 38.3524 | 10.8516 | 21.2575 | 8.4004 | 20.2286 | 8.862 | 20.4732 | 8.3391 | 11.3832 | 33.7451 | 11.4788 | 12.0028 | 49.0486 | 8.7073 | 11.1237 | 38.8718 | 8.7348 | 21.1908 | 10.6683 | 19.4763 | 9.1213 | 20.8448 | 0.077028 | 20.9257 | 0.075549 | 0.046828 | -37.7117 | 3.1203 | 29.44 | 46.11 | -0.36935 | -0.42443 | 0.42961 | -0.2834 | -0.43097 | -0.66167 | 0.65499 | 0.31818 | 0.25513 | 0.30675 | 0.34439 | 0.54327 | 0.35386 | 0.30567
42810.4409 | 76 | 18.5641 | 18.5946 | 18.5686 | 18.5859 | 17.9115 | 16.5236 | 14.5808 | 16.6828 | 17.1722 | 17.2701 | 17.2841 | 16.8242 | 15.8593 | 14.4893 | 14.9658 | 14.9029 | 15.4591 | 13.3205 | 13.4324 | 14.0017 |  |  |  | 16.5682 | 15.8949 | 15.0082 | 39.4126 | 40.8763 | 61.7591 | 17.242 | 16.3235 | 15.1081 | 16.8435 | 16.1155 | 15.1136 | 11.4794 | 54.2706 |  | 17.7181 | 29.3806 | 35.3289 | 12.0915 |  | 6.3909 | 6.4811 | 6.0041 | 6.1391 | 6.2908 | 6.9688 | 12.6421 | 4.3882 | 6.3773 | 4.2405 | 6.6219 | 8.1267 | 42.2677 | 46.5644 | 42.7611 | 15.0208 |  |  | -0.23174 | -0.066281 | -0.05992 | 0.20239 | -0.036636 | 0.000856 | 0.39286 | 0.15097 | -0.44328 | -0.53202 | -0.26935 | 8.8703 | 8.8712 | 2.006 | 15.7911 | 16.6448 | 17.1859 | 17.5162 | 17.4799 | 16.449 | 14.8135 | 16.8264 | 17.1727 | 17.476 | 17.5232 | 17.2627 | 16.4541 | 14.6735 | 7.0516 | 8.3971 | 5.8651 | 6.9618 | 7.0234 | 6.8874 | 7.7226 | 15.8469 | 15.4303 | 15.2888 | 14.229 | 14.1201 | 14.0699 |  |  |  | 11.4284 | 44.8606 | 30.3322 | 14.1317 | 0.21602 | -0.018042 | 14.1492 |  |  | 10.5271 |  |  | 16.8598 | 16.0466 | 15.0378 | 16.3549 | 15.6363 | 14.7401 | 33.6477 | 44.3675 | 25.6566 | 26.2383 | 13.1125 |  | 11.2183 | 14.7479 | 11.001 | 14.4573 | 12.0925 | 40.1905 |  | 15.1132 |  |  | 12.0327 | 12.821 | 14.235 | [6 empty] | 14.4115 |  |  | 14.3449 |  |  | 10.2236 | 12.8988 | 63.8176 | 8.0173 | 10.6251 | 33.4116 | 8.387 | 10.7871 | 38.7139 | 10.8839 | 21.6426 | 8.3837 | 20.5128 | 8.8753 | 20.6828 | 8.3324 | 11.66 | 34.0214 | 11.4974 | 12.0231 | 49.5373 | 8.7191 | 11.1356 | 39.2376 | 8.7776 | 21.5517 | 10.6857 | 19.7719 | 9.1346 | 21.1068 | 0.040819 | 20.9204 | 0.078464 | 0.046988 | -37.699 | 3.1204 | 30.14 | 45.83 | -0.61395 | -0.30002 | -0.28526 | 0.52427 | -0.22325 | 0.034125 | 0.73106 | 0.31816 | 0.26556 | 0.30966 | 0.33046 | 0.55926 | 0.35513 | 0.29678
42810.4409 | 77 | 18.5575 | 18.5906 | 18.5743 | 18.589 | 17.9145 | 16.5301 | 14.5888 | 16.6748 | 17.1766 | 17.2778 | 17.287 | 16.825 | 15.8558 | 14.4845 | 14.9654 | 14.915 | 15.4678 | 13.322 | 13.4484 | 14.0059 |  |  |  | 16.5799 | 15.8952 | 15.0158 | 39.7969 | 41.3237 | 62.0366 | 17.2544 | 16.3267 | 15.1178 | 16.8495 | 16.1294 | 15.1259 | 11.5051 | 54.8021 |  | 17.813 | 29.6806 | 35.7101 | 12.9306 |  | 6.3982 | 6.4871 | 6.0093 | 6.1382 | 6.2963 | 6.9609 | 13.0172 | 4.4115 | 6.379 | 4.2362 | 6.6315 | 8.122 | 42.2428 | 46.5872 | 42.7459 | 15.0222 |  |  | -0.29614 | -0.28445 | 0.12867 | 2e-06 | 0.013308 | -0.13386 | -0.003384 | 0.19828 | -0.35163 | -1.0857 | -0.38857 | 8.8692 | 8.8707 | 2.0059 | 15.7922 | 16.6535 | 17.1922 | 17.5205 | 17.4896 | 16.4581 | 14.8084 | 16.8279 | 17.1679 | 17.4733 | 17.5234 | 17.2619 | 16.4548 | 14.6751 | 7.6723 | 8.4847 | 5.8384 | 6.7647 | 6.8784 | 6.9048 | 7.7139 | 15.8563 | 15.4365 | 15.2992 | 14.2337 | 14.1285 | 14.0738 |  |  |  | 11.4576 | 45.2578 | 30.8325 | 14.4249 | 0.039758 | 0.038982 | 14.1448 |  |  | 10.5231 |  |  | 16.8593 | 16.0451 | 15.0435 | 16.355 | 15.6337 | 14.7426 | 34.062 | 44.8003 | 25.9981 | 26.5619 | 13.0491 |  | 11.2301 | 14.6007 | 11.0084 | 14.3937 | 12.1178 | 40.3205 |  | 15.177 |  |  | 12.0385 | 12.8236 | 14.1922 | [6 empty] | 14.412 |  |  | 14.3699 |  |  | 10.232 | 12.9315 | 64.1869 | 7.9929 | 10.6266 | 33.6793 | 8.387 | 10.8004 | 39.0089 | 10.8999 | 21.9882 | 8.3613 | 20.8239 | 8.8764 | 20.8856 | 8.343 | 11.8265 | 34.2996 | 11.5162 | 12.0521 | 49.9343 | 8.7232 | 11.1571 | 39.6021 | 8.7991 | 21.8922 | 10.699 | 20.0266 | 9.1611 | 21.3869 | -0.031599 | 20.9158 | 0.081552 | 0.046648 | -37.6658 | 3.1205 | 38.35 | 47.75 | -0.69432 | -0.62153 | 0.41803 | 0.0016481 | 0.13455 | -0.42673 | -0.06785 | 0.32031 | 0.26989 | 0.31227 | 0.2635 | 0.56121 | 0.33268 | 0.2896
42810.4409 | 78 | 18.5553 | 18.5855 | 18.5732 | 18.5782 | 17.9014 | 16.5211 | 14.5799 | 16.6699 | 17.1721 | 17.2702 | 17.2804 | 16.8116 | 15.8478 | 14.4866 | 14.9621 | 14.9211 | 15.463 | 13.3184 | 13.4403 | 14.0037 |  |  |  | 16.5676 | 15.8933 | 15.0115 | 40.2764 | 41.7686 | 62.1802 | 17.2528 | 16.3271 | 15.1093 | 16.8483 | 16.1151 | 15.117 | 11.528 | 55.2749 |  | 17.9101 | 30.0328 | 36.0482 | 14.1966 |  | 6.3986 | 6.4767 | 6.0061 | 6.1187 | 6.2708 | 6.9356 | 13.4604 | 4.388 | 6.377 | 4.1809 | 6.6325 | 8.1245 | 42.2315 | 46.6027 | 42.7387 | 15.034 |  |  | -0.20086 | -0.16682 | 0.32778 | 0.14785 | -0.078032 | -0.7522 | 0.06364 | 0.16214 | 0.0087724 | -0.16172 | -0.25762 | 8.8683 | 8.8693 | 2.0059 | 15.7856 | 16.6385 | 17.1822 | 17.5173 | 17.4808 | 16.4515 | 14.8015 | 16.8216 | 17.1622 | 17.4726 | 17.5159 | 17.2487 | 16.4488 | 14.6619 | 8.5494 | 8.8136 | 6.0296 | 6.5754 | 6.8234 | 6.9274 | 7.7187 | 15.8625 | 15.4478 | 15.2957 | 14.2385 | 14.1305 | 14.0766 |  |  |  | 11.4842 | 45.6544 | 31.1031 | 14.6016 | 0.040569 | -0.047213 | 14.1397 |  |  | 10.5321 |  |  | 16.8586 | 16.049 | 15.0453 | 16.3532 | 15.6266 | 14.7426 | 34.5125 | 45.239 | 26.3426 | 26.9213 | 12.9099 |  | 11.2331 | 14.7053 | 11.0279 | 14.33 | 12.132 | 40.2707 |  | 15.2388 |  |  | 12.0201 | 12.8279 | 14.1536 | [6 empty] | 14.4205 |  |  | 14.4138 |  |  | 10.2323 | 12.9654 | 64.374 | 7.9494 | 10.6076 | 33.9576 | 8.3819 | 10.8073 | 39.2955 | 10.9172 | 22.1386 | 8.3705 | 21.2092 | 8.8714 | 21.0743 | 8.3586 | 11.9429 | 34.5331 | 11.5254 | 12.086 | 50.1991 | 8.7201 | 11.1754 | 40.0369 | 8.8113 | 22.2489 | 10.722 | 20.2687 | 9.1676 | 21.6474 | 0.090317 | 20.8894 | 0.085317 | 0.047668 | -37.6677 | 3.1204 | 35.6 | 49.52 | -0.57194 | -0.47597 | 0.66719 | 0.44809 | -0.3258 | -1.0115 | 0.29422 | 0.32427 | 0.26763 | 0.3145 | 0.16867 | 0.54053 | 0.29826 | 0.28557
42810.4409 | 79 | 18.5638 | 18.5948 | 18.5779 | 18.5832 | 17.9109 | 16.5298 | 14.5846 | 16.6804 | 17.1816 | 17.2758 | 17.2917 | 16.8211 | 15.8571 | 14.4856 | 14.9651 | 14.9197 | 15.4652 | 13.3234 | 13.4364 | 14.0052 |  |  |  | 16.5632 | 15.8907 | 15.0108 | 40.8168 | 42.1192 | 62.3374 | 17.2512 | 16.3247 | 15.1074 | 16.8456 | 16.1196 | 15.1188 | 11.5683 | 55.5199 |  | 18.0062 | 30.4152 | 36.3972 | 14.6138 |  | 6.4053 | 6.4648 | 6.001 | 6.1088 | 6.2491 | 6.9079 | 13.4111 | 4.4035 | 6.3764 | 4.1899 | 6.631 | 8.1297 | 42.2122 | 46.6178 | 42.7386 | 15.0459 |  |  | -0.096377 | -0.078765 | 0.32318 | 0.060454 | -0.2502 | -0.44598 | -0.17555 | 0.079348 | -2.283 | -0.2106 | -0.26557 | 8.8723 | 8.8737 | 2.0058 | 15.7968 | 16.6544 | 17.1847 | 17.5238 | 17.4787 | 16.4471 | 14.8146 | 16.828 | 17.1655 | 17.4712 | 17.5214 | 17.2581 | 16.453 | 14.6726 | 9.2862 | 9.2653 | 7.1112 | 6.5427 | 6.6889 | 6.9573 | 7.7324 | 15.8724 | 15.4437 | 15.2967 | 14.2372 | 14.1346 | 14.0819 |  |  |  | 11.5031 | 46.1204 | 31.1603 | 14.5165 | 0.1986 | -0.044014 | 14.1781 |  |  | 10.5379 |  |  | 16.8605 | 16.0509 | 15.0525 | 16.3556 | 15.6303 | 14.7449 | 34.9859 | 45.6247 | 26.6789 | 27.3307 | 12.7563 |  | 11.2463 | 16.461 | 11.062 | 14.294 | 12.1521 | 40.9439 |  | 15.3038 |  |  | 11.9945 | 12.8364 | 14.1108 | [6 empty] | 14.4131 |  |  | 14.4479 |  |  | 10.2472 | 13.0104 | 64.5276 | 7.9375 | 10.6087 | 34.305 | 8.383 | 10.838 | 39.6329 | 10.9491 | 22.3016 | 8.3854 | 21.5702 | 8.8913 | 21.2861 | 8.3687 | 12.0032 | 34.7017 | 11.5468 | 12.1076 | 50.6397 | 8.7151 | 11.1907 | 40.4522 | 8.82 | 22.5814 | 10.7425 | 20.5309 | 9.1777 | 21.887 | 0.064316 | 20.8761 | 0.089718 | 0.048674 | -37.7479 | 3.1204 | 23.19 | 49.21 | -0.39627 | -0.32705 | 0.66247 | 0.28652 | -0.58335 | -0.77884 | -0.48864 | 0.32898 | 0.21999 | 0.31617 | 0.09027 | 0.42195 | 0.288 | 0.28855
42810.441 | 80 | 18.5632 | 18.5979 | 18.5728 | 18.5866 | 17.9126 | 16.5303 | 14.5877 | 16.6844 | 17.1737 | 17.2727 | 17.2931 | 16.8247 | 15.8547 | 14.4773 | 14.9728 | 14.9191 | 15.4644 | 13.3297 | 13.442 | 13.998 |  |  |  | 16.5695 | 15.8986 | 15.0107 | 41.2751 | 42.3788 | 62.2042 | 17.2555 | 16.3292 | 15.116 | 16.8512 | 16.1284 | 15.129 | 11.6018 | 55.7615 |  | 18.1226 | 30.8094 | 36.7707 | 14.288 |  | 6.3985 | 6.4691 | 6.0007 | 6.0821 | 6.2128 | 6.8834 | 13.2799 | 4.4556 | 6.3748 | 4.2484 | 6.6383 | 8.1369 | 42.1846 | 46.6322 | 42.7474 | 15.0543 |  |  | -0.058921 | -0.14579 | 0.17533 | 0.12025 | -0.099716 | -0.54718 | -0.11706 | 0.26006 | -0.14126 | -0.84105 | -0.31326 | 8.8681 | 8.869 | 2.0057 | 15.8022 | 16.6554 | 17.1977 | 17.524 | 17.4822 | 16.4578 | 14.816 | 16.8266 | 17.1708 | 17.4731 | 17.5247 | 17.2618 | 16.4567 | 14.677 | 9.6133 | 9.1517 | 7.9269 | 6.7228 | 6.5545 | 6.9724 | 7.7385 | 15.8736 | 15.45 | 15.3046 | 14.2413 | 14.1325 | 14.0786 |  |  |  | 11.5228 | 46.5524 | 31.1667 | 14.4387 | -0.05364 | -0.095581 | 14.2683 |  |  | 10.5353 |  |  | 16.8665 | 16.049 | 15.0638 | 16.3571 | 15.6357 | 14.7414 | 35.4658 | 46.0742 | 26.9706 | 27.722 | 12.6993 |  | 11.2571 | 18.0739 | 11.0975 | 14.3258 | 12.1847 | 41.1267 |  | 15.3741 |  |  | 11.9731 | 12.8497 | 14.0808 | [6 empty] | 14.4169 |  |  | 14.4842 |  |  | 10.2583 | 13.0472 | 64.7348 | 7.9215 | 10.6212 | 34.6638 | 8.38 | 10.8638 | 40.0263 | 10.9803 | 22.5924 | 8.3849 | 21.908 | 8.9059 | 21.5746 | 8.3912 | 12.001 | 34.9377 | 11.5795 | 12.1324 | 51.045 | 8.7242 | 11.2109 | 40.7949 | 8.8286 | 22.874 | 10.7599 | 20.7337 | 9.1906 | 22.1203 | 0.16716 | 20.8661 | 0.093839 | 0.048971 | -37.678 | 3.1204 | 25.66 | 50.02 | -0.30978 | -0.44496 | 0.48795 | 0.40411 | -0.36826 | -0.86265 | -0.39901 | 0.33091 | 0.17636 | 0.31637 | 0.055686 | 0.33202 | 0.29816 | 0.29137
42810.441 | 81 | 18.5618 | 18.5899 | 18.5692 | 18.5842 | 17.9068 | 16.5263 | 14.5848 | 16.6792 | 17.1799 | 17.2685 | 17.2772 | 16.82 | 15.8515 | 14.4752 | 14.9697 | 14.9208 | 15.4635 | 13.3279 | 13.4456 | 13.9991 |  |  |  | 16.5757 | 15.9054 | 15.0151 | 41.6607 | 42.6497 | 62.3234 | 17.2507 | 16.3342 | 15.1142 | 16.8501 | 16.1221 | 15.1232 | 11.617 | 56.1204 |  | 18.2271 | 31.1803 | 37.1323 | 13.9762 |  | 6.3877 | 6.4592 | 5.9923 | 6.0678 | 6.1907 | 6.8542 | 13.0944 | 4.5175 | 6.3701 | 4.3196 | 6.6401 | 8.1255 | 42.149 | 46.628 | 42.7571 | 15.0586 |  |  | -0.10163 | -0.1655 | 0.091876 | 0.16559 | -0.095776 | -0.25936 | 0.21215 | -0.011336 | -0.25024 | -0.54943 | -0.2616 | 8.8702 | 8.8712 | 2.006 | 15.806 | 16.6566 | 17.2016 | 17.5247 | 17.4833 | 16.4585 | 14.8162 | 16.8402 | 17.1685 | 17.4772 | 17.5191 | 17.2641 | 16.4569 | 14.6774 | 9.4247 | 8.9772 | 7.7566 | 6.9281 | 6.5815 | 6.9908 | 7.7523 | 15.8781 | 15.4611 | 15.31 | 14.2453 | 14.1384 | 14.0855 |  |  |  | 11.5444 | 47.2606 | 31.3267 | 14.3794 | -0.019603 | -0.042132 | 14.369 |  |  | 10.5316 |  |  | 16.8648 | 16.046 | 15.0575 | 16.3569 | 15.64 | 14.7404 | 36.0079 | 46.6159 | 27.2182 | 28.0302 | 13.2749 |  | 11.2833 | 18.2226 | 11.1456 | 14.3742 | 12.216 | 40.9768 |  | 15.4502 |  |  | 11.9595 | 12.857 | 14.1759 | [6 empty] | 14.4373 |  |  | 14.5319 |  |  | 10.2725 | 13.1033 | 65.0375 | 7.9212 | 10.6395 | 35.0407 | 8.3852 | 10.8879 | 40.3848 | 11.0018 | 22.9224 | 8.3627 | 22.1911 | 8.9136 | 21.9134 | 8.4171 | 11.989 | 35.2645 | 11.6058 | 12.1716 | 51.281 | 8.7366 | 11.236 | 41.1406 | 8.8132 | 23.1459 | 10.779 | 20.8999 | 9.2059 | 22.3852 | 0.10168 | 20.8436 | 0.098069 | 0.049152 | -37.6242 | 3.1204 | 23.11 | 48.48 | -0.40692 | -0.47408 | 0.35322 | 0.4742 | -0.36089 | -0.59389 | 0.53712 | 0.31579 | 0.17381 | 0.31605 | 0.078784 | 0.35254 | 0.30732 | 0.29372
42810.441 | 82 | 18.5611 | 18.5883 | 18.5675 | 18.578 | 17.9158 | 16.5287 | 14.5843 | 16.6794 | 17.1745 | 17.2744 | 17.2811 | 16.8178 | 15.8522 | 14.4721 | 14.9698 | 14.924 | 15.4663 | 13.3193 | 13.441 | 14.0035 |  |  |  | 16.5744 | 15.8974 | 15.0191 | 42.0362 | 42.9431 | 62.6089 | 17.2498 | 16.3221 | 15.1075 | 16.844 | 16.1221 | 15.1252 | 11.6302 | 56.076 |  | 18.3292 | 31.5569 | 37.4676 | 13.6281 |  | 6.3822 | 6.4519 | 5.9865 | 6.0599 | 6.1845 | 6.8493 | 12.9408 | 4.4945 | 6.374 | 4.3961 | 6.6419 | 8.1274 | 42.1184 | 46.6211 | 42.7694 | 15.0679 |  |  | -0.16537 | -0.2345 | 0.28244 | 0.28585 | -0.060292 | -0.43876 | 0.30546 | 0.21537 | -0.48687 | -0.35369 | -0.37088 | 8.8701 | 8.8712 | 2.0063 | 15.8031 | 16.6597 | 17.2016 | 17.5227 | 17.4847 | 16.4596 | 14.8196 | 16.8381 | 17.1757 | 17.4739 | 17.5209 | 17.2615 | 16.4578 | 14.6759 | 8.9252 | 8.8216 | 7.5238 | 6.9683 | 6.6982 | 6.99 | 7.7532 | 15.8802 | 15.4644 | 15.3153 | 14.2468 | 14.1378 | 14.089 |  |  |  | 11.564 | 47.8136 | 31.5738 | 14.3706 | -0.071672 | -0.086171 | 14.4242 |  |  | 10.5296 |  |  | 16.8537 | 16.0502 | 15.055 | 16.3567 | 15.6411 | 14.7426 | 36.5658 | 47.0094 | 27.4597 | 28.2784 | 14.8367 |  | 11.3234 | 17.3349 | 11.1912 | 14.4872 | 12.252 | 41.7773 |  | 15.5449 |  |  | 11.9725 | 12.8713 | 14.43 | [6 empty] | 14.5062 |  |  | 14.5586 |  |  | 10.2866 | 13.1756 | 65.6846 | 7.9289 | 10.6494 | 35.3962 | 8.3966 | 10.9108 | 40.6412 | 11.0318 | 23.306 | 8.3227 | 22.4412 | 8.9191 | 22.2329 | 8.399 | 11.9762 | 35.5919 | 11.6209 | 12.2207 | 51.5652 | 8.7513 | 11.2492 | 41.4314 | 8.7838 | 23.4069 | 10.8042 | 21.0807 | 9.2198 | 22.642 | 0.21474 | 20.8363 | 0.10198 | 0.049325 | -37.6814 | 3.1204 | 22.74 | 49.03 | -0.51929 | -0.5643 | 0.6193 | 0.62302 | -0.28634 | -0.77243 | 0.6445 | 0.27373 | 0.19997 | 0.31411 | 0.13419 | 0.37852 | 0.31743 | 0.29462
42810.441 | 83 | 18.559 | 18.5977 | 18.5736 | 18.5839 | 17.9035 | 16.5343 | 14.5847 | 16.6757 | 17.1783 | 17.2772 | 17.2813 | 16.8333 | 15.8585 | 14.4755 | 14.9722 | 14.9208 | 15.4662 | 13.3139 | 13.4371 | 14.0059 |  |  |  | 16.5687 | 15.8888 | 15.0171 | 42.4692 | 43.2119 | 62.9254 | 17.2612 | 16.3363 | 15.1221 | 16.8492 | 16.1292 | 15.1301 | 11.6412 | 56.0116 |  | 18.436 | 31.9283 | 37.8439 | 13.301 |  | 6.3816 | 6.45 | 5.9801 | 6.0494 | 6.1729 | 6.8228 | 13.062 | 4.4957 | 6.3698 | 4.4978 | 6.6484 | 8.138 | 42.1076 | 46.6107 | 42.7817 | 15.0808 |  |  | 0.073815 | -0.17142 | 0.034708 | -0.13208 | -0.095116 | -0.39473 | 0.20689 | 0.24428 | -0.064397 | -0.26599 | -0.32637 | 8.8694 | 8.8709 | 2.006 | 15.8151 | 16.6615 | 17.2016 | 17.5286 | 17.49 | 16.4616 | 14.8199 | 16.835 | 17.1797 | 17.4795 | 17.5268 | 17.2616 | 16.4601 | 14.6775 | 8.4515 | 8.7009 | 7.4288 | 7.0557 | 6.8089 | 6.9937 | 7.7577 | 15.8825 | 15.4642 | 15.3166 | 14.2493 | 14.1396 | 14.0887 |  |  |  | 11.5813 | 48.0804 | 31.741 | 14.381 | -0.16851 | -0.083724 | 14.449 |  |  | 10.532 |  |  | 16.8546 | 16.0513 | 15.0663 | 16.357 | 15.6303 | 14.7412 | 37.0198 | 47.4995 | 27.7075 | 28.4898 | 15.6595 |  | 11.3619 | 16.5483 | 11.2115 | 14.5853 | 12.2809 | 42.8601 |  | 15.6401 |  |  | 11.9995 | 12.8654 | 14.709 | [6 empty] | 14.6 |  |  | 14.5853 |  |  | 10.3016 | 13.2313 | 66.302 | 7.9406 | 10.7292 | 35.6883 | 8.3932 | 10.9162 | 40.926 | 11.0595 | 23.6619 | 8.284 | 22.6885 | 8.9252 | 22.5179 | 8.3632 | 11.985 | 35.9305 | 11.6374 | 12.274 | 51.9746 | 8.7501 | 11.2654 | 41.6473 | 8.7861 | 23.6446 | 10.8283 | 21.315 | 9.2252 | 22.809 | 0.074524 | 20.8269 | 0.10608 | 0.049115 | -37.6369 | 3.1205 | 21.76 | 49.98 | 0.3471 | -0.48247 | 0.2171 | -0.4235 | -0.35963 | -0.73261 | 0.53039 | 0.25215 | 0.22249 | 0.31233 | 0.18724 | 0.38959 | 0.32688 | 0.2949
42810.441 | 84 | 18.5614 | 18.5917 | 18.5723 | 18.5774 | 17.9011 | 16.5179 | 14.5817 | 16.6751 | 17.1769 | 17.2672 | 17.2852 | 16.8149 | 15.8468 | 14.4753 | 14.9643 | 14.9109 | 15.4626 | 13.3169 | 13.4325 | 13.9967 |  |  |  | 16.5741 | 15.8932 | 15.0137 | 42.8069 | 43.4948 | 62.6434 | 17.2602 | 16.3344 | 15.1214 | 16.8543 | 16.1224 | 15.1303 | 11.6589 | 55.9913 |  | 18.5231 | 32.2386 | 38.1344 | 13.1465 |  | 6.3813 | 6.4477 | 5.985 | 6.0386 | 6.1531 | 6.8121 | 13.1021 | 4.538 | 6.3692 | 4.5485 | 6.6492 | 8.1393 | 42.1048 | 46.6068 | 42.7814 | 15.0834 |  |  | -0.091777 | -0.11228 | 0.11882 | -0.060454 | -0.078688 | -0.055 | 0.24106 | 0.40528 | -0.81049 | -0.85679 | -0.28445 | 8.865 | 8.866 | 2.005 | 15.8197 | 16.6663 | 17.2047 | 17.5315 | 17.4855 | 16.4691 | 14.8216 | 16.8336 | 17.1845 | 17.482 | 17.5295 | 17.2657 | 16.4541 | 14.6804 | 8.0204 | 8.6105 | 7.3096 | 7.0544 | 7.0089 | 6.9925 | 7.7618 | 15.8758 | 15.4561 | 15.3164 | 14.2479 | 14.1313 | 14.0861 |  |  |  | 11.5946 | 48.3382 | 32.0382 | 14.4119 | 0.043203 | -0.044014 | 14.4574 |  |  | 10.5314 |  |  | 16.8574 | 16.0487 | 15.0681 | 16.3524 | 15.6236 | 14.7446 | 37.398 | 48.0914 | 27.943 | 28.7319 | 15.7305 |  | 11.4002 | 15.923 | 11.2369 | 14.6383 | 12.3081 | 42.8426 |  | 15.7242 |  |  | 11.9999 | 12.8384 | 14.9723 | [6 empty] | 14.6561 |  |  | 14.6121 |  |  | 10.3143 | 13.2669 | 66.7807 | 7.9449 | 10.9994 | 35.9674 | 8.3952 | 10.9244 | 41.2403 | 11.0781 | 23.9871 | 8.2827 | 22.935 | 8.9285 | 22.7891 | 8.3439 | 12.0778 | 36.2016 | 11.6517 | 12.3315 | 52.5146 | 8.7493 | 11.2611 | 41.9318 | 8.8026 | 23.9284 | 10.8374 | 21.5464 | 9.225 | 23.0513 | 0.15888 | 20.8216 | 0.10974 | 0.049195 | -37.6783 | 3.1205 | 17.92 | 48.84 | -0.38687 | -0.39046 | 0.40167 | -0.28651 | -0.32709 | -0.27346 | 0.57251 | 0.25144 | 0.2407 | 0.31176 | 0.235 | 0.40331 | 0.33175 | 0.29448
42810.441 | 85 | 18.5663 | 18.5959 | 18.5694 | 18.5863 | 17.9023 | 16.5221 | 14.5875 | 16.6835 | 17.1738 | 17.2716 | 17.2876 | 16.8186 | 15.8491 | 14.4705 | 14.9692 | 14.9158 | 15.4673 | 13.3184 | 13.4317 | 13.9927 |  |  |  | 16.5653 | 15.8986 | 15.0168 | 43.07 | 43.8775 | 62.6185 | 17.2634 | 16.3382 | 15.1316 | 16.8611 | 16.1276 | 15.1377 | 11.6716 | 56.1323 |  | 18.6253 | 32.5769 | 38.45 | 13.1674 |  | 6.3763 | 6.446 | 5.9759 | 6.0414 | 6.1472 | 6.7915 | 13.0436 | 4.5552 | 6.3665 | 4.5664 | 6.6521 | 8.1394 | 42.1033 | 46.6194 | 42.7789 | 15.0821 |  |  | -0.1174 | -0.22333 | 0.01302 | -0.11368 | -0.11286 | -0.25082 | 0.39877 | 0.38425 | -0.22592 | -1.0731 | -0.36572 | 8.8716 | 8.8728 | 2.0048 | 15.8105 | 16.6527 | 17.1954 | 17.5227 | 17.4827 | 16.4576 | 14.8109 | 16.8329 | 17.1716 | 17.4682 | 17.5123 | 17.2596 | 16.4443 | 14.6726 | 7.8374 | 8.5256 | 6.9529 | 7.0822 | 7.1045 | 7.0009 | 7.7587 | 15.8782 | 15.4618 | 15.3112 | 14.2452 | 14.1426 | 14.0839 |  |  |  | 11.6223 | 48.7325 | 32.1844 | 14.4747 | -0.076939 | -0.19834 | 14.4545 |  |  | 10.5305 |  |  | 16.8541 | 16.0447 | 15.0663 | 16.3509 | 15.6251 | 14.7401 | 37.8342 | 48.6051 | 28.1848 | 29.0091 | 15.137 |  | 11.4216 | 15.1696 | 11.2658 | 14.7222 | 12.3285 | 42.7991 |  | 15.8194 |  |  | 12.0197 | 12.8489 | 14.9926 | [6 empty] | 14.703 |  |  | 14.6307 |  |  | 10.3295 | 13.3112 | 67.0386 | 7.9371 | 11.1615 | 36.2356 | 8.3957 | 10.9448 | 41.497 | 11.0979 | 24.3367 | 8.2858 | 23.2249 | 8.9236 | 23.0767 | 8.3395 | 12.2103 | 36.4842 | 11.6586 | 12.3555 | 53.0254 | 8.7548 | 11.2693 | 42.2736 | 8.8155 | 24.2502 | 10.8467 | 21.8733 | 9.2393 | 23.3301 | 0.094169 | 20.8121 | 0.11399 | 0.049362 | -37.7563 | 3.1205 | 35.37 | 49.83 | -0.43755 | -0.55069 | 0.13297 | -0.3929 | -0.39172 | -0.58396 | 0.73631 | 0.26863 | 0.26258 | 0.31011 | 0.25631 | 0.44259 | 0.33159 | 0.29365
42810.441 | 86 | 18.5745 | 18.6073 | 18.5754 | 18.5933 | 17.9136 | 16.5298 | 14.5878 | 16.6874 | 17.1837 | 17.2873 | 17.2941 | 16.8302 | 15.8618 | 14.4767 | 14.9748 | 14.9244 | 15.4638 | 13.3326 | 13.4433 | 14.0063 |  |  |  | 16.5739 | 15.8913 | 15.0293 | 43.3612 | 44.392 | 62.5399 | 17.2571 | 16.3374 | 15.1281 | 16.855 | 16.1339 | 15.1423 | 11.6948 | 56.1043 |  | 18.714 | 32.9132 | 38.744 | 13.3798 |  | 6.3736 | 6.4477 | 5.9747 | 6.0414 | 6.1516 | 6.7827 | 13.246 | 4.6128 | 6.3681 | 4.5214 | 6.6563 | 8.1389 | 42.0876 | 46.6344 | 42.7794 | 15.079 |  |  | -0.1818 | -0.12214 | 0.10633 | 0.018398 | -0.14243 | -0.1332 | 0.21281 | 0.32182 | -0.24966 | -0.052413 | -0.2 | 8.8679 | 8.869 | 2.0044 | 15.8189 | 16.6579 | 17.1955 | 17.5214 | 17.4814 | 16.4633 | 14.8189 | 16.8313 | 17.1694 | 17.4791 | 17.5314 | 17.2578 | 16.455 | 14.6614 | 7.782 | 8.4754 | 6.7192 | 6.8081 | 7.1405 | 7.0069 | 7.7592 | 15.8824 | 15.4614 | 15.3115 | 14.241 | 14.1379 | 14.0906 |  |  |  | 11.6441 | 49.2369 | 32.5727 | 14.4927 | -0.060326 | -0.12645 | 14.5634 |  |  | 10.5377 |  |  | 16.8554 | 16.0434 | 15.0773 | 16.3505 | 15.6336 | 14.7348 | 38.3124 | 49.1004 | 28.4269 | 29.2731 | 14.6342 |  | 11.4384 | 14.7792 | 11.3191 | 14.7924 | 12.3678 | 43.3557 |  | 15.9239 |  |  | 12.0405 | 12.8529 | 14.8645 | [6 empty] | 14.7512 |  |  | 14.6374 |  |  | 10.3425 | 13.3594 | 67.4894 | 7.9124 | 11.1551 | 36.5668 | 8.3917 | 10.9711 | 41.7419 | 11.1346 | 24.7792 | 8.2518 | 23.412 | 8.9206 | 23.3665 | 8.3459 | 12.382 | 36.7535 | 11.6679 | 12.3728 | 53.3657 | 8.7562 | 11.2915 | 42.7086 | 8.8229 | 24.5403 | 10.8677 | 22.3276 | 9.2463 | 23.5754 | -0.12636 | 20.8043 | 0.11725 | 0.04955 | -37.747 | 3.1205 | 10.2 | 48.94 | -0.54442 | -0.40725 | 0.37998 | 0.15806 | -0.44005 | -0.42554 | 0.53788 | 0.28315 | 0.27519 | 0.30945 | 0.26317 | 0.46861 | 0.32646 | 0.29387
42810.441 | 87 | 18.5716 | 18.6051 | 18.5744 | 18.5887 | 17.9116 | 16.5315 | 14.5845 | 16.6783 | 17.1857 | 17.2811 | 17.2866 | 16.8197 | 15.8592 | 14.4799 | 14.983 | 14.9295 | 15.4786 | 13.3373 | 13.4458 | 14.0058 |  |  |  | 16.5761 | 15.8969 | 15.0359 | 43.6461 | 44.8644 | 62.8744 | 17.2622 | 16.3406 | 15.1283 | 16.855 | 16.1344 | 15.1403 | 11.7234 | 56.1633 |  | 18.8076 | 33.2382 | 39.0036 | 13.6275 |  | 6.3718 | 6.4442 | 5.9693 | 6.0359 | 6.142 | 6.776 | 13.254 | 4.6723 | 6.3654 | 4.5015 | 6.6509 | 8.1373 | 42.0501 | 46.6341 | 42.7878 | 15.0734 |  |  | -0.072721 | -0.34096 | 0.005792 | 0.23065 | -0.089204 | -0.38947 | 0.18849 | 0.49727 | -0.45476 | 0.047032 | -0.23537 | 8.8694 | 8.8708 | 2.0035 | 15.8123 | 16.6586 | 17.1858 | 17.5253 | 17.4846 | 16.4567 | 14.8117 | 16.8237 | 17.1742 | 17.4751 | 17.5157 | 17.2644 | 16.4492 | 14.6644 | 7.8732 | 8.4903 | 6.5438 | 6.5686 | 7.149 | 7.0186 | 7.7614 | 15.8903 | 15.4628 | 15.3161 | 14.2425 | 14.1373 | 14.0904 |  |  |  | 11.6722 | 49.7878 | 32.9231 | 14.4745 | -0.13306 | -0.063775 | 14.6877 |  |  | 10.5403 |  |  | 16.852 | 16.044 | 15.0791 | 16.3469 | 15.6267 | 14.7383 | 38.6804 | 49.5457 | 28.7175 | 29.5653 | 14.4762 |  | 11.4553 | 14.3892 | 11.3753 | 14.7661 | 12.3883 | 44.141 |  | 16.0184 |  |  | 12.0644 | 12.864 | 14.7986 | [6 empty] | 14.781 |  |  | 14.6813 |  |  | 10.3404 | 13.3899 | 67.6242 | 7.8797 | 11.1318 | 36.9264 | 8.3783 | 10.9787 | 41.9791 | 11.1499 | 25.0373 | 8.2527 | 23.7525 | 8.9186 | 23.6279 | 8.3405 | 12.4609 | 36.9812 | 11.6891 | 12.4009 | 53.8251 | 8.7723 | 11.33 | 43.0477 | 8.8389 | 24.823 | 10.8973 | 22.6379 | 9.2608 | 23.8225 | -0.0036716 | 20.7959 | 0.12117 | 0.049253 | -37.7593 | 3.1205 | 29.89 | 48.9 | -0.34449 | -0.68043 | 0.088684 | 0.55963 | -0.34824 | -0.72766 | 0.50622 | 0.2881 | 0.28787 | 0.31086 | 0.2544 | 0.48837 | 0.32052 | 0.2953
42810.4411 | 88 | 18.5785 | 18.6067 | 18.5839 | 18.584 | 17.9074 | 16.5345 | 14.5917 | 16.6764 | 17.1809 | 17.2717 | 17.2898 | 16.8213 | 15.8577 | 14.4731 | 14.9744 | 14.9205 | 15.4703 | 13.324 | 13.4432 | 14.0004 |  |  |  | 16.5686 | 15.8978 | 15.0184 | 43.9925 | 45.1912 | 63.5268 | 17.2691 | 16.3373 | 15.131 | 16.8547 | 16.1302 | 15.1432 | 11.7498 | 56.1522 |  | 18.9176 | 33.5412 | 39.2457 | 14.3103 |  | 6.3715 | 6.4544 | 5.9552 | 6.018 | 6.1272 | 6.7587 | 13.2867 | 4.7331 | 6.3678 | 4.5078 | 6.6543 | 8.1356 | 42.0185 | 46.6331 | 42.7887 | 15.0643 |  |  | -0.33163 | -0.023569 | 0.3245 | -0.15508 | -0.005748 | -0.22256 | 0.23449 | 0.10629 | -0.38237 | -0.30396 | -0.38916 | 8.8696 | 8.8709 | 2.0035 | 15.8217 | 16.6577 | 17.1973 | 17.5258 | 17.4835 | 16.4581 | 14.8126 | 16.8314 | 17.1817 | 17.4735 | 17.5288 | 17.2637 | 16.4513 | 14.6657 | 8.0795 | 8.5821 | 6.4416 | 6.3902 | 7.0336 | 7.0222 | 7.7565 | 15.8937 | 15.4693 | 15.3242 | 14.2444 | 14.1471 | 14.0932 |  |  |  | 11.6993 | 50.2719 | 33.4548 | 14.3587 | -0.15514 | -0.15261 | 14.7693 |  |  | 10.5558 |  |  | 16.8552 | 16.0448 | 15.0769 | 16.3494 | 15.6307 | 14.7434 | 39.0166 | 49.9605 | 28.9824 | 29.8855 | 14.4062 |  | 11.4664 | 13.8398 | 11.4181 | 14.7021 | 12.4041 | 44.67 |  | 16.1197 |  |  | 12.0387 | 12.8743 | 14.7741 | [6 empty] | 14.7571 |  |  | 14.6932 |  |  | 10.3432 | 13.4285 | 67.9166 | 7.8744 | 11.1481 | 37.2053 | 8.3754 | 10.9904 | 42.2438 | 11.1769 | 25.0191 | 8.2647 | 24.118 | 8.9255 | 23.9199 | 8.3453 | 12.5498 | 37.2692 | 11.6924 | 12.4332 | 54.1505 | 8.7841 | 11.3669 | 43.3343 | 8.8555 | 25.1512 | 10.9156 | 22.8118 | 9.292 | 24.1655 | 0.13288 | 20.7933 | 0.12426 | 0.049535 | -37.7468 | 3.1205 | 29.78 | 50.05 | -0.73637 | -0.1789 | 0.66381 | -0.4589 | -0.088396 | -0.55005 | 0.5646 | 0.29041 | 0.30455 | 0.31316 | 0.23189 | 0.49914 | 0.30243 | 0.29942
42810.4411 | 89 | 18.5884 | 18.6121 | 18.5885 | 18.5927 | 17.9134 | 16.5333 | 14.5988 | 16.6895 | 17.1861 | 17.2788 | 17.2964 | 16.8294 | 15.8581 | 14.4781 | 14.9822 | 14.9327 | 15.4783 | 13.332 | 13.4424 | 14.0107 |  |  |  | 16.575 | 15.9018 | 15.0333 | 44.4996 | 45.5367 | 64.0082 | 17.2601 | 16.3352 | 15.1293 | 16.8541 | 16.1273 | 15.1389 | 11.7974 | 56.1343 |  | 19.0109 | 33.8218 | 39.4914 | 15.497 |  | 6.3851 | 6.4521 | 5.9476 | 6.0139 | 6.1278 | 6.7413 | 13.4907 | 4.7444 | 6.37 | 4.5352 | 6.6578 | 8.1392 | 42.0148 | 46.6315 | 42.7937 | 15.0556 |  |  | -0.004381 | -0.33504 | 0.12276 | -0.06571 | 0.032364 | -0.51958 | 0.18784 | 0.078692 | -1.9869 | -0.33438 | -0.25504 | 8.8672 | 8.8682 | 2.004 | 15.8245 | 16.661 | 17.203 | 17.5227 | 17.4825 | 16.4585 | 14.8129 | 16.8288 | 17.1748 | 17.4694 | 17.5274 | 17.2545 | 16.4541 | 14.6618 | 8.082 | 8.6401 | 6.5104 | 6.2856 | 6.8073 | 7.0325 | 7.7649 | 15.8987 | 15.4773 | 15.3183 | 14.2503 | 14.1513 | 14.0957 |  |  |  | 11.7185 | 50.8011 | 34.0283 | 14.2336 | -0.14035 | -0.13698 | 14.8464 |  |  | 10.5565 |  |  | 16.8635 | 16.0424 | 15.0856 | 16.3549 | 15.6298 | 14.7491 | 39.346 | 50.3273 | 29.2514 | 30.18 | 14.3351 |  | 11.4847 | 13.4833 | 11.4842 | 14.6301 | 12.4354 | 45.0892 |  | 16.2246 |  |  | 12.0587 | 12.8921 | 15.022 | [6 empty] | 14.7356 |  |  | 14.7171 |  |  | 10.3565 | 13.4684 | 68.2614 | 7.8857 | 11.1925 | 37.4862 | 8.3975 | 11.0106 | 42.5794 | 11.2093 | 25.1368 | 8.2855 | 24.4318 | 8.9312 | 24.273 | 8.3499 | 12.6194 | 37.5252 | 11.7136 | 12.4533 | 54.6845 | 8.7969 | 11.3988 | 43.6192 | 8.8713 | 25.4094 | 10.9405 | 23.0219 | 9.312 | 24.487 | 0.064316 | 20.7854 | 0.12732 | 0.048327 | -37.7238 | 3.1205 | 27.32 | 49.18 | -0.084697 | -0.67451 | 0.40829 | -0.29871 | 0.20975 | -0.8404 | 0.5053 | 0.29299 | 0.31663 | 0.3162 | 0.23281 | 0.49248 | 0.27104 | 0.30353
42810.4411 | 90 | 18.5743 | 18.6029 | 18.5859 | 18.5932 | 17.9104 | 16.5367 | 14.5861 | 16.6784 | 17.1851 | 17.2737 | 17.2896 | 16.8181 | 15.8574 | 14.4694 | 14.9782 | 14.931 | 15.4771 | 13.3318 | 13.4396 | 14.0104 |  |  |  | 16.5741 | 15.8994 | 15.0345 | 44.8828 | 45.8447 | 63.6763 | 17.2648 | 16.3461 | 15.146 | 16.8571 | 16.1343 | 15.1328 | 11.8491 | 55.9748 |  | 19.1307 | 34.1015 | 39.7478 | 17.0869 |  | 6.3779 | 6.4417 | 5.9393 | 6.0027 | 6.1038 | 6.7203 | 13.636 | 4.7558 | 6.3701 | 4.5539 | 6.6646 | 8.136 | 42.0183 | 46.636 | 42.7818 | 15.0458 |  |  | -0.005037 | -0.11622 | 0.028136 | -0.017742 | 0.06982 | -0.37567 | 0.37183 | -0.1283 | -0.15858 | -1.718 | -0.31723 | 8.8734 | 8.8748 | 2.0044 | 15.8226 | 16.6649 | 17.1957 | 17.5256 | 17.4848 | 16.4559 | 14.8082 | 16.8282 | 17.172 | 17.471 | 17.5277 | 17.25 | 16.4511 | 14.6613 | 8.2373 | 8.5676 | 6.5278 | 6.2343 | 6.6095 | 7.0404 | 7.7684 | 15.8963 | 15.4711 | 15.3205 | 14.2446 | 14.1473 | 14.0888 |  |  |  | 11.7388 | 51.4329 | 34.4646 | 14.1977 | -0.064378 | 0.088102 | 14.9123 |  |  | 10.5579 |  |  | 16.8484 | 16.0393 | 15.0876 | 16.3451 | 15.6196 | 14.743 | 39.6171 | 50.7183 | 29.5501 | 30.4758 | 14.298 |  | 11.5139 | 13.7343 | 11.5149 | 14.5862 | 12.4594 | 45.7657 |  | 16.2981 |  |  | 12.0746 | 12.8845 | 15.2259 | [6 empty] | 14.713 |  |  | 14.7492 |  |  | 10.3649 | 13.497 | 68.4693 | 7.8971 | 11.3572 | 37.7791 | 8.3962 | 11.0166 | 42.932 | 11.2233 | 25.5401 | 8.3002 | 24.8083 | 8.9331 | 24.591 | 8.3595 | 12.6481 | 37.7347 | 11.7105 | 12.477 | 55.2175 | 8.8043 | 11.4136 | 43.8155 | 8.8816 | 25.6276 | 10.9407 | 23.2097 | 9.3165 | 24.7678 | 0.15946 | 20.7801 | 0.13018 | 0.047516 | -37.7707 | 3.1205 | 22.19 | 48.76 | -0.090773 | -0.39726 | 0.19546 | -0.15521 | 0.30806 | -0.71458 | 0.71091 | 0.29498 | 0.31067 | 0.31821 | 0.21647 | 0.49095 | 0.22858 | 0.30519
42810.4411 | 91 | 18.5746 | 18.6058 | 18.576 | 18.5945 | 17.912 | 16.5305 | 14.5868 | 16.6798 | 17.1753 | 17.277 | 17.2775 | 16.8167 | 15.8499 | 14.4726 | 14.978 | 14.9321 | 15.4688 | 13.3293 | 13.4461 | 14.0026 |  |  |  | 16.5716 | 15.8974 | 15.0313 | 45.1745 | 46.1225 | 63.2704 | 17.2649 | 16.346 | 15.1416 | 16.8611 | 16.134 | 15.1458 | 11.8954 | 56.4731 |  | 19.2542 | 34.3376 | 40.0122 | 16.9124 |  | 6.371 | 6.4336 | 5.9282 | 5.9895 | 6.0887 | 6.7107 | 13.8941 | 4.7951 | 6.3665 | 4.5714 | 6.6641 | 8.1426 | 42.0193 | 46.6399 | 42.7715 | 15.0404 |  |  | -0.041181 | -0.22333 | 0.068876 | 0.095938 | -0.19828 | -0.35136 | 0.55845 | 0.037292 | -0.23545 | -0.77392 | -0.075614 | 8.8735 | 8.8746 | 2.0052 | 15.8164 | 16.6659 | 17.1996 | 17.5213 | 17.4865 | 16.4599 | 14.8043 | 16.8251 | 17.1766 | 17.4683 | 17.5218 | 17.2511 | 16.4439 | 14.6606 | 8.3012 | 8.5389 | 6.3771 | 6.196 | 6.5324 | 7.0371 | 7.7669 | 15.8958 | 15.4723 | 15.3168 | 14.2482 | 14.1525 | 14.0947 |  |  |  | 11.7503 | 51.8059 | 34.496 | 14.1726 | 0.085141 | -0.11591 | 14.9432 |  |  | 10.5566 |  |  | 16.8483 | 16.0396 | 15.0961 | 16.3498 | 15.6202 | 14.7406 | 39.931 | 51.2444 | 29.8501 | 30.7741 | 14.2752 |  | 11.538 | 14.2484 | 11.5503 | 14.5896 | 12.4778 | 46.1425 |  | 16.3854 |  |  | 12.0933 | 12.8756 | 15.2961 | [6 empty] | 14.7187 |  |  | 14.783 |  |  | 10.3749 | 13.5448 | 68.6829 | 7.9016 | 11.4958 | 38.054 | 8.3999 | 11.0456 | 43.262 | 11.2581 | 26.0362 | 8.3111 | 25.1484 | 8.9508 | 24.8794 | 8.3749 | 12.6713 | 38.0047 | 11.7358 | 12.5118 | 55.5716 | 8.8215 | 11.4397 | 44.0733 | 8.8984 | 25.8118 | 10.9684 | 23.4608 | 9.3316 | 25.0229 | 0.32413 | 20.7722 | 0.13293 | 0.047502 | -37.7719 | 3.1205 | 20.12 | 50.16 | -0.25939 | -0.55068 | 0.30581 | 0.36093 | -0.51914 | -0.69106 | 0.87122 | 0.29641 | 0.29756 | 0.31873 | 0.20899 | 0.50752 | 0.23495 | 0.30627
42810.4411 | 92 | 18.5784 | 18.6051 | 18.5759 | 18.5897 | 17.9118 | 16.5274 | 14.5886 | 16.6818 | 17.1808 | 17.2752 | 17.2901 | 16.8221 | 15.8507 | 14.4753 | 14.9835 | 14.9307 | 15.4769 | 13.3257 | 13.4423 | 13.9997 |  |  |  | 16.574 | 15.8915 | 15.0299 | 45.428 | 46.4217 | 63.3959 | 17.2701 | 16.3375 | 15.1319 | 16.8569 | 16.1362 | 15.1438 | 11.9208 | 56.8629 |  | 19.3608 | 34.5877 | 40.3035 | 16.6755 |  | 6.3731 | 6.4446 | 5.9085 | 5.9883 | 6.0802 | 6.6958 | 14.4502 | 4.8414 | 6.3717 | 4.5661 | 6.6719 | 8.1461 | 42.0493 | 46.6564 | 42.7581 | 15.0253 |  |  | -0.22846 | -0.3081 | 0.21147 | 0.07491 | -0.022836 | 0.18748 | 0.32057 | -0.3077 | -0.33489 | -0.80287 | -0.414 | 8.8667 | 8.8676 | 2.0057 | 15.8254 | 16.6695 | 17.2046 | 17.5276 | 17.4911 | 16.4654 | 14.8112 | 16.8327 | 17.1805 | 17.4735 | 17.5266 | 17.2576 | 16.443 | 14.6675 | 8.2287 | 8.5702 | 6.3546 | 6.1396 | 6.5121 | 7.0419 | 7.7664 | 15.9047 | 15.467 | 15.3172 | 14.2478 | 14.1448 | 14.0939 |  |  |  | 11.7669 | 52.1405 | 34.5499 | 14.1835 | 0.054548 | 0.019221 | 15.0074 |  |  | 10.5665 |  |  | 16.8579 | 16.0485 | 15.104 | 16.3512 | 15.6316 | 14.7454 | 40.2739 | 51.8718 | 30.1244 | 31.0626 | 14.4896 |  | 11.567 | 14.7817 | 11.5732 | 14.7239 | 12.5069 | 45.7302 |  | 16.4677 |  |  | 12.1053 | 12.8778 | 15.5161 | [6 empty] | 14.7633 |  |  | 14.8097 |  |  | 10.3907 | 13.5788 | 68.7863 | 7.8957 | 11.5493 | 38.2838 | 8.405 | 11.0691 | 43.4597 | 11.2788 | 26.4875 | 8.3148 | 25.4173 | 8.9358 | 25.1555 | 8.3856 | 12.6698 | 38.2501 | 11.7418 | 12.533 | 55.8316 | 8.8192 | 11.4526 | 44.3066 | 8.8953 | 25.9586 | 10.9872 | 23.7459 | 9.3343 | 25.2707 | 0.26501 | 20.7677 | 0.13558 | 0.047046 | -37.8233 | 3.1205 | 32.29 | 49.19 | -0.61107 | -0.64681 | 0.53587 | 0.31893 | -0.17617 | 0.50478 | 0.66007 | 0.29141 | 0.2835 | 0.31595 | 0.21761 | 0.50996 | 0.24238 | 0.30652
42810.4411 | 93 | 18.5807 | 18.6073 | 18.5804 | 18.5911 | 17.9118 | 16.5297 | 14.5881 | 16.6809 | 17.1758 | 17.2768 | 17.2935 | 16.8252 | 15.8578 | 14.4728 | 14.9886 | 14.9283 | 15.4786 | 13.327 | 13.4478 | 14.003 |  |  |  | 16.5707 | 15.9011 | 15.0384 | 45.6788 | 46.752 | 63.7161 | 17.2624 | 16.336 | 15.1377 | 16.8572 | 16.1358 | 15.1429 | 11.9449 | 57.1659 |  | 19.4599 | 34.863 | 40.586 | 16.4356 |  | 6.3807 | 6.4463 | 5.9148 | 5.9891 | 6.0812 | 6.6927 | 14.8214 | 4.8726 | 6.3783 | 4.5261 | 6.6745 | 8.1357 | 42.0743 | 46.6737 | 42.7414 | 15.007 |  |  | -0.096377 | 0.15714 | 0.019592 | 0.12025 | -0.10366 | -0.076028 | 0.48025 | -0.23081 | 0.17399 | -0.28256 | -0.12469 | 8.8718 | 8.8734 | 2.0055 | 15.8267 | 16.6714 | 17.2083 | 17.5361 | 17.4904 | 16.4672 | 14.8181 | 16.8354 | 17.1792 | 17.471 | 17.5259 | 17.2634 | 16.4497 | 14.6676 | 8.2022 | 8.5609 | 6.496 | 6.0793 | 6.4652 | 7.0571 | 7.7733 | 15.8959 | 15.4609 | 15.3096 | 14.2461 | 14.1427 | 14.0911 |  |  |  | 11.7864 | 52.4556 | 34.8963 | 14.1759 | -0.072279 | 0.027878 | 15.0758 |  |  | 10.576 |  |  | 16.8586 | 16.0537 | 15.1129 | 16.356 | 15.6329 | 14.7443 | 40.6399 | 52.3336 | 30.3674 | 31.3022 | 15.5944 |  | 11.6071 | 15.532 | 11.6045 | 15.0491 | 12.5358 | 45.4228 |  | 16.5307 |  |  | 12.1196 | 12.8961 | 15.9376 | [6 empty] | 14.934 |  |  | 14.8476 |  |  | 10.402 | 13.6205 | 68.9458 | 7.8956 | 11.5559 | 38.4923 | 8.4028 | 11.089 | 43.7196 | 11.3043 | 26.9661 | 8.3142 | 25.6352 | 8.9242 | 25.4586 | 8.3981 | 12.6711 | 38.4365 | 11.7463 | 12.5865 | 56.0293 | 8.8111 | 11.472 | 44.526 | 8.8947 | 26.1069 | 11.0163 | 24.0124 | 9.3411 | 25.4927 | 0.26058 | 20.7609 | 0.13884 | 0.047957 | -37.7522 | 3.1206 | 57 | 49.06 | -0.39708 | 0.46193 | 0.16311 | 0.40409 | -0.37534 | -0.32145 | 0.8079 | 0.26205 | 0.2637 | 0.30788 | 0.22231 | 0.49506 | 0.24983 | 0.30737
42810.4411 | 94 | 18.584 | 18.6076 | 18.5792 | 18.5868 | 17.9057 | 16.5237 | 14.5845 | 16.6811 | 17.1802 | 17.2751 | 17.2893 | 16.8163 | 15.8545 | 14.4758 | 14.9946 | 14.9366 | 15.4826 | 13.3308 | 13.4516 | 14.0055 |  |  |  | 16.5762 | 15.9041 | 15.0432 | 45.9907 | 47.0848 | 64.036 | 17.2641 | 16.3418 | 15.1417 | 16.8632 | 16.1394 | 15.1512 | 11.9691 | 57.3423 |  | 19.5599 | 35.1595 | 40.8662 | 16.1757 |  | 6.3923 | 6.44 | 5.9075 | 5.9859 | 6.0843 | 6.6976 | 14.7184 | 4.8955 | 6.3737 | 4.5349 | 6.671 | 8.1414 | 42.1068 | 46.6867 | 42.7331 | 15.004 |  |  | -0.31323 | 0.023743 | 0.032076 | 0.07951 | 0.14013 | 0.032396 | 0.47697 | -0.15722 | 0.1773 | -0.45124 | -0.34863 | 8.8704 | 8.8713 | 2.0054 | 15.8201 | 16.6667 | 17.1977 | 17.5243 | 17.4827 | 16.4613 | 14.8115 | 16.8259 | 17.1673 | 17.4723 | 17.5203 | 17.2556 | 16.445 | 14.6625 | 8.794 | 8.5861 | 6.4884 | 6.1326 | 6.3622 | 7.0667 | 7.7689 | 15.906 | 15.4716 | 15.323 | 14.2538 | 14.1481 | 14.0977 |  |  |  | 11.8166 | 52.9849 | 35.339 | 14.3701 | -0.063568 | -0.041003 | 15.1706 |  |  | 10.5754 |  |  | 16.8601 | 16.0452 | 15.1074 | 16.347 | 15.6274 | 14.745 | 41.0035 | 52.7489 | 30.5971 | 31.5416 | 16.8318 |  | 11.6621 | 17.3867 | 11.646 | 15.4876 | 12.5845 | 45.323 |  | 16.6004 |  |  | 12.1329 | 12.9043 | 16.2657 | [6 empty] | 15.1462 |  |  | 14.8849 |  |  | 10.4179 | 13.6696 | 69.0484 | 7.8979 | 11.5703 | 38.7103 | 8.405 | 11.1152 | 44.0496 | 11.3436 | 27.4112 | 8.3182 | 25.8364 | 8.9187 | 25.7979 | 8.4081 | 12.6859 | 38.6326 | 11.7642 | 12.6336 | 56.2253 | 8.8161 | 11.4929 | 44.7738 | 8.9102 | 26.2717 | 11.0514 | 24.2501 | 9.3612 | 25.7235 | 0.18296 | 20.7556 | 0.14088 | 0.048471 | -37.7495 | 3.1206 | 35.15 | 49.91 | -0.71619 | 0.17955 | 0.2087 | 0.32858 | 0.43641 | 0.20983 | 0.80514 | 0.22949 | 0.21354 | 0.29731 | 0.15768 | 0.49539 | 0.25785 | 0.30297
42810.4411 | 95 | 18.579 | 18.6075 | 18.5814 | 18.5837 | 17.9019 | 16.524 | 14.588 | 16.6812 | 17.18 | 17.2751 | 17.2834 | 16.8096 | 15.8493 | 14.4778 | 14.9893 | 14.9438 | 15.4785 | 13.3321 | 13.4466 | 14.0118 |  |  |  | 16.5804 | 15.9028 | 15.0421 | 46.3114 | 47.3761 | 64.283 | 17.2658 | 16.3415 | 15.1431 | 16.8574 | 16.1316 | 15.1579 | 11.9793 | 57.5996 |  | 19.6538 | 35.4283 | 41.1453 | 15.9565 |  | 6.3911 | 6.4382 | 5.9123 | 5.9932 | 6.0963 | 6.7102 | 14.6415 | 4.9038 | 6.39 | 4.6237 | 6.6754 | 8.1375 | 42.1138 | 46.7042 | 42.7186 | 14.9998 |  |  | -0.13383 | -0.1425 | 0.21804 | 0.049942 | 0.19401 | -0.053688 | 0.46514 | -0.12633 | 0.083693 | 1.434 | -0.28047 | 8.8732 | 8.8744 | 2.0054 | 15.8323 | 16.6782 | 17.2127 | 17.5289 | 17.4958 | 16.4652 | 14.8167 | 16.8408 | 17.1823 | 17.4791 | 17.5243 | 17.2628 | 16.4589 | 14.6686 | 9.8836 | 8.6357 | 6.5436 | 6.2034 | 6.3808 | 7.0973 | 7.7723 | 15.9011 | 15.4652 | 15.3236 | 14.2434 | 14.1469 | 14.0944 |  |  |  | 11.8438 | 53.5264 | 36.0202 | 14.7738 | 0.14653 | -0.071303 | 15.267 |  |  | 10.5733 |  |  | 16.8644 | 16.0431 | 15.1107 | 16.3439 | 15.6299 | 14.7509 | 41.3515 | 53.2058 | 30.8115 | 31.7633 | 16.6953 |  | 11.7123 | 19.3318 | 11.7181 | 15.5588 | 12.6281 | 45.6957 |  | 16.6835 |  |  | 12.1524 | 12.907 | 16.5111 | [6 empty] | 15.2602 |  |  | 14.9061 |  |  | 10.4388 | 13.7061 | 69.242 | 7.8926 | 11.599 | 38.9652 | 8.4043 | 11.1337 | 44.3226 | 11.3727 | 27.9409 | 8.3349 | 26.0527 | 8.9195 | 26.0696 | 8.424 | 12.7347 | 38.8882 | 11.7914 | 12.6676 | 56.5239 | 8.8221 | 11.5211 | 45.0397 | 8.9207 | 26.4457 | 11.0771 | 24.4936 | 9.3869 | 25.9624 | 0.2001 | 20.7496 | 0.14394 | 0.048175 | -37.6316 | 3.1205 | 28.11 | 48.97 | -0.46832 | -0.43989 | 0.54412 | 0.26041 | 0.51351 | -0.27013 | 0.79511 | 0.23494 | 0.1619 | 0.29677 | 0.040156 | 0.48964 | 0.26428 | 0.29266
42810.4411 | 96 | 18.5839 | 18.6135 | 18.5891 | 18.5939 | 17.9188 | 16.5354 | 14.5923 | 16.6842 | 17.188 | 17.2841 | 17.286 | 16.8224 | 15.8587 | 14.4803 | 14.9834 | 14.9364 | 15.4736 | 13.3333 | 13.4435 | 14.0073 |  |  |  | 16.576 | 15.9023 | 15.0426 | 46.5855 | 47.6538 | 64.2217 | 17.2639 | 16.3403 | 15.1325 | 16.8531 | 16.1323 | 15.1451 | 11.9968 | 57.83 |  | 19.7414 | 35.6443 | 41.4383 | 16.1838 |  | 6.3813 | 6.427 | 5.9154 | 5.9979 | 6.0991 | 6.7137 | 14.595 | 4.9058 | 6.3919 | 4.7207 | 6.6781 | 8.1511 | 42.1418 | 46.7343 | 42.7091 | 14.9917 |  |  | -0.27906 | -0.052481 | 0.039964 | -0.20305 | 0.24921 | 0.28144 | 0.41323 | -0.020536 | -0.16501 | -0.36543 | -0.29041 | 8.8689 | 8.87 | 2.0051 | 15.8383 | 16.672 | 17.2103 | 17.5287 | 17.4956 | 16.464 | 14.8209 | 16.827 | 17.1767 | 17.4793 | 17.5293 | 17.2598 | 16.4551 | 14.6675 | 10.9244 | 8.9731 | 6.7963 | 6.2652 | 6.3679 | 7.1342 | 7.7785 | 15.9051 | 15.4729 | 15.3252 | 14.2498 | 14.1515 | 14.1024 |  |  |  | 11.8761 | 54.0519 | 36.5849 | 15.0712 | 0.21197 | -0.018042 | 15.3273 |  |  | 10.5901 |  |  | 16.8561 | 16.0493 | 15.1239 | 16.353 | 15.6242 | 14.7584 | 41.6359 | 53.6439 | 30.9977 | 31.9768 | 16.1715 |  | 11.7529 | 20.3903 | 11.7748 | 15.3805 | 12.6589 | 46.3378 |  | 16.7611 |  |  | 12.1705 | 12.9179 | 16.5741 | [6 empty] | 15.2714 |  |  | 14.9162 |  |  | 10.4514 | 13.7363 | 69.579 | 7.882 | 11.6268 | 39.2675 | 8.4142 | 11.1447 | 44.526 | 11.3955 | 28.427 | 8.346 | 26.2984 | 8.9285 | 26.3633 | 8.4203 | 12.8004 | 39.1226 | 11.8056 | 12.6852 | 56.8613 | 8.8214 | 11.5442 | 45.3227 | 8.9287 | 26.6857 | 11.0953 | 24.7363 | 9.405 | 26.1943 | 0.12845 | 20.7447 | 0.14756 | 0.048413 | -37.695 | 3.1205 | 40.33 | 49.65 | -0.67619 | -0.26694 | 0.23294 | -0.52507 | 0.582 | 0.6185 | 0.74944 | 0.25083 | 0.13436 | 0.30274 | -0.07121 | 0.46229 | 0.25854 | 0.28546
42810.4412 | 97 | 18.5823 | 18.601 | 18.5762 | 18.5861 | 17.8916 | 16.5242 | 14.5786 | 16.672 | 17.1684 | 17.2674 | 17.2827 | 16.8152 | 15.8478 | 14.4728 | 14.9842 | 14.9324 | 15.4795 | 13.3306 | 13.4468 | 14.0052 |  |  |  | 16.5789 | 15.9023 | 15.0482 | 46.9716 | 47.8924 | 64.9616 | 17.2624 | 16.3327 | 15.1323 | 16.8618 | 16.1316 | 15.147 | 12.0244 | 57.9527 |  | 19.8354 | 35.8585 | 41.7506 | 16.8294 |  | 6.3767 | 6.4231 | 5.9181 | 6.0044 | 6.1003 | 6.7298 | 14.6289 | 4.8676 | 6.3905 | 4.7451 | 6.6736 | 8.1536 | 42.1606 | 46.7428 | 42.7116 | 14.9801 |  |  | 0.014675 | 0.002059 | 0.19898 | -0.27599 | -0.014292 | 0.061308 | 0.61299 | -0.13093 | -0.10098 | -0.2106 | -0.12151 | 8.8692 | 8.8701 | 2.0047 | 15.8328 | 16.667 | 17.2034 | 17.5256 | 17.4915 | 16.4646 | 14.8243 | 16.8281 | 17.1754 | 17.477 | 17.525 | 17.251 | 16.4437 | 14.659 | 11.5784 | 9.5501 | 8.5641 | 6.5549 | 6.3827 | 7.1697 | 7.7996 | 15.9056 | 15.474 | 15.328 | 14.254 | 14.1478 | 14.0965 |  |  |  | 11.9042 | 54.5173 | 36.9953 | 15.1985 | -0.01697 | -0.094828 | 15.3749 |  |  | 10.5836 |  |  | 16.8642 | 16.042 | 15.1265 | 16.3541 | 15.6205 | 14.7496 | 41.9433 | 54.0931 | 31.1982 | 32.1715 | 15.6326 |  | 11.7777 | 20.6352 | 11.826 | 15.2606 | 12.6908 | 46.4085 |  | 16.8413 |  |  | 12.1899 | 12.9328 | 16.3697 | [6 empty] | 15.2242 |  |  | 14.9393 |  |  | 10.4607 | 13.7664 | 70.1205 | 7.8856 | 11.6326 | 39.6159 | 8.4187 | 11.1605 | 44.7335 | 11.4225 | 28.8471 | 8.3531 | 26.5761 | 8.944 | 26.6095 | 8.4162 | 12.8459 | 39.3068 | 11.8253 | 12.7116 | 57.2967 | 8.8219 | 11.5672 | 45.6097 | 8.9371 | 26.977 | 11.1128 | 24.9496 | 9.4156 | 26.458 | 0.026759 | 20.7399 | 0.15036 | 0.048399 | -37.7214 | 3.1206 | 36.06 | 49.46 | 0.15523 | 0.052874 | 0.51979 | -0.61215 | -0.13938 | 0.28868 | 0.91281 | 0.26662 | 0.12925 | 0.30713 | -0.13975 | 0.26831 | 0.24152 | 0.28285
42810.4412 | 98 | 18.5799 | 18.6063 | 18.5827 | 18.5857 | 17.9089 | 16.5209 | 14.5763 | 16.6682 | 17.1664 | 17.2738 | 17.2894 | 16.819 | 15.8563 | 14.467 | 14.9829 | 14.9342 | 15.48 | 13.3296 | 13.4417 | 14.0063 |  |  |  | 16.5726 | 15.896 | 15.0523 | 47.4406 | 48.1334 | 65.3872 | 17.2753 | 16.3416 | 15.147 | 16.8662 | 16.1413 | 15.156 | 12.0895 | 58.035 |  | 19.9355 | 36.0853 | 42.0444 | 17.0699 |  | 6.3752 | 6.4266 | 5.9256 | 6.0152 | 6.111 | 6.7262 | 14.995 | 4.8919 | 6.3878 | 4.7813 | 6.6806 | 8.1435 | 42.1661 | 46.7484 | 42.6845 | 14.9656 |  |  | -0.031981 | -0.10965 | 0.13196 | -0.3095 | -0.028748 | 0.055396 | 0.47434 | -0.072448 | -0.85661 | -0.76909 | -0.23934 | 8.869 | 8.87 | 2.0043 | 15.8404 | 16.6837 | 17.2101 | 17.5381 | 17.4931 | 16.4711 | 14.8306 | 16.8379 | 17.181 | 17.4786 | 17.5265 | 17.2607 | 16.4513 | 14.6714 | 11.8963 | 9.5718 | 9.459 | 7.8015 | 6.7829 | 7.1963 | 7.8216 | 15.9085 | 15.4798 | 15.3221 | 14.2496 | 14.146 | 14.0961 |  |  |  | 11.9257 | 54.94 | 37.376 | 15.2474 | -0.032975 | -0.0267 | 15.4252 |  |  | 10.5824 |  |  | 16.8555 | 16.0439 | 15.132 | 16.3455 | 15.62 | 14.7444 | 42.3512 | 54.4154 | 31.4089 | 32.3522 | 15.2185 |  | 11.7993 | 20.4196 | 11.8739 | 15.1941 | 12.7128 | 46.3118 |  | 16.9225 |  |  | 12.1947 | 12.9437 | 16.238 | [6 empty] | 15.193 |  |  | 14.9382 |  |  | 10.4765 | 13.8025 | 70.59 | 7.8891 | 11.6271 | 39.9366 | 8.4189 | 11.1764 | 44.9407 | 11.4632 | 29.1541 | 8.3725 | 26.841 | 8.9537 | 26.8675 | 8.4238 | 12.8744 | 39.5081 | 11.8337 | 12.741 | 57.7331 | 8.8163 | 11.5826 | 45.9084 | 8.9341 | 27.2136 | 11.1302 | 25.1823 | 9.4203 | 26.8078 | 0.15946 | 20.736 | 0.15303 | 0.049115 | -37.675 | 3.1205 | 50.51 | 49.07 | -0.22931 | -0.38585 | 0.42329 | -0.64826 | -0.19768 | 0.2744 | 0.80296 | 0.27884 | 0.13682 | 0.3097 | -0.17198 | 0.17144 | 0.23699 | 0.28221
42810.4412 | 99 | 18.5861 | 18.6128 | 18.5892 | 18.5955 | 17.9171 | 16.5288 | 14.5883 | 16.6803 | 17.1753 | 17.2779 | 17.2906 | 16.8219 | 15.8576 | 14.4729 | 14.9866 | 14.9366 | 15.4742 | 13.3328 | 13.4465 | 14.0145 |  |  |  | 16.5657 | 15.8959 | 15.049 | 47.7733 | 48.4988 | 65.5114 | 17.2553 | 16.3365 | 15.1348 | 16.8585 | 16.135 | 15.1511 | 12.1176 | 58.0024 |  | 20.0126 | 36.2928 | 42.2603 | 16.8724 |  | 6.3874 | 6.4311 | 5.9255 | 6.016 | 6.1149 | 6.7285 | 14.992 | 4.8966 | 6.3844 | 4.7487 | 6.6823 | 8.1408 | 42.1677 | 46.7644 | 42.6598 | 14.9466 |  |  | -0.10755 | -0.007141 | 0.07742 | -0.21291 | -0.17923 | 0.052768 | 0.50391 | -0.1053 | -0.6951 | -0.29977 | -0.20914 | 8.8726 | 8.8735 | 2.0041 | 15.8439 | 16.6848 | 17.208 | 17.5329 | 17.4925 | 16.464 | 14.8272 | 16.8353 | 17.1758 | 17.4756 | 17.5248 | 17.2542 | 16.4505 | 14.6609 | 12.1698 | 9.573 | 9.5289 | 7.9763 | 7.4 | 7.2395 | 7.8418 | 15.8998 | 15.469 | 15.3259 | 14.2568 | 14.1452 | 14.0963 |  |  |  | 11.9605 | 55.2367 | 37.5332 | 15.2675 | -0.022845 | -0.036674 | 15.4426 |  |  | 10.5849 |  |  | 16.8568 | 16.04 | 15.1316 | 16.3409 | 15.6269 | 14.7499 | 42.7471 | 54.857 | 31.6152 | 32.5327 | 15.58 |  | 11.8349 | 19.7057 | 11.9075 | 15.1434 | 12.7449 | 46.1222 |  | 17.0187 |  |  | 12.1856 | 12.9627 | 16.2513 | [6 empty] | 15.2331 |  |  | 14.9313 |  |  | 10.487 | 13.8417 | 70.7708 | 7.893 | 11.6206 | 40.1773 | 8.4153 | 11.1904 | 45.2197 | 11.476 | 29.5196 | 8.3878 | 27.0936 | 8.9692 | 27.1405 | 8.424 | 12.8804 | 39.705 | 11.8527 | 12.7631 | 58.0189 | 8.816 | 11.6178 | 46.2357 | 8.9282 | 27.385 | 11.1488 | 25.4026 | 9.4304 | 27.2317 | 0.080109 | 20.7307 | 0.15564 | 0.049731 | -37.7488 | 3.1206 | 46.23 | 50.27 | -0.42058 | -0.098469 | 0.32423 | -0.53767 | -0.49358 | 0.26782 | 0.82761 | 0.26997 | 0.15776 | 0.31217 | -0.19736 | 0.16602 | 0.24341 | 0.2828
42810.4412 | 100 | 18.591 | 18.6125 | 18.5939 | 18.5923 | 17.9111 | 16.5329 | 14.5869 | 16.6853 | 17.1772 | 17.2763 | 17.2866 | 16.8249 | 15.8535 | 14.4734 | 14.9873 | 14.9409 | 15.4783 | 13.333 | 13.4521 | 14.0136 |  |  |  | 16.5799 | 15.8971 | 15.0471 | 48.0737 | 48.9039 | 65.8104 | 17.2562 | 16.3405 | 15.1453 | 16.8589 | 16.1401 | 15.1612 | 12.1403 | 58.2995 |  | 20.1111 | 36.5341 | 42.5091 | 16.6277 |  | 6.3885 | 6.4282 | 5.9272 | 6.0217 | 6.1199 | 6.7149 | 14.8577 | 4.8906 | 6.3924 | 4.749 | 6.6826 | 8.1452 | 42.1629 | 46.777 | 42.6449 | 14.9474 |  |  | -0.34148 | -0.20756 | 0.12933 | 0.013142 | 0.036304 | 0.18353 | 0.36526 | 0.15032 | -0.17532 | -1.8687 | -0.32578 | 8.8685 | 8.8698 | 2.0043 | 15.8416 | 16.6691 | 17.2079 | 17.5319 | 17.4903 | 16.4572 | 14.8141 | 16.829 | 17.1724 | 17.4732 | 17.517 | 17.2561 | 16.4444 | 14.6554 | 12.8681 | 9.6124 | 9.8383 | 8.321 | 7.6394 | 7.2778 | 7.8544 | 15.9115 | 15.4782 | 15.3297 | 14.2582 | 14.1503 | 14.1008 |  |  |  | 11.9967 | 55.5475 | 37.9239 | 15.514 | 0.12262 | -0.0061858 | 15.4576 |  |  | 10.5897 |  |  | 16.8596 | 16.0465 | 15.1404 | 16.3506 | 15.6272 | 14.7489 | 43.1403 | 55.2084 | 31.8415 | 32.7249 | 15.8229 |  | 11.8725 | 19.0144 | 11.9348 | 15.0442 | 12.7894 | 45.5295 |  | 17.0956 |  |  | 12.1776 | 12.9678 | 16.2377 | [6 empty] | 15.2912 |  |  | 14.9157 |  |  | 10.5032 | 13.885 | 71.0654 | 7.9058 | 11.6053 | 40.4342 | 8.4311 | 11.2058 | 45.6115 | 11.5112 | 30.0761 | 8.3882 | 27.3546 | 8.9875 | 27.3961 | 8.4086 | 12.8816 | 39.8429 | 11.873 | 12.8021 | 58.1839 | 8.814 | 11.6767 | 46.4966 | 8.9341 | 27.5791 | 11.1685 | 25.6266 | 9.439 | 27.6903 | 0.061042 | 20.727 | 0.15894 | 0.049579 | -37.7509 | 3.1206 | 54.52 | 48.94 | -0.74976 | -0.53087 | 0.41906 | 0.13358 | 0.22214 | 0.49946 | 0.7046 | 0.26446 | 0.17787 | 0.3164 | -0.2705 | 0.1331 | 0.25095 | 0.27715
42810.4412 | 101 | 18.5977 | 18.6121 | 18.593 | 18.5951 | 17.9139 | 16.5378 | 14.5958 | 16.6866 | 17.1843 | 17.2855 | 17.2932 | 16.8279 | 15.8577 | 14.4762 | 14.9893 | 14.9388 | 15.4807 | 13.3247 | 13.4566 | 14.0223 |  |  |  | 16.5752 | 15.8925 | 15.0581 | 48.3659 | 49.2282 | 66.4747 | 17.2576 | 16.3414 | 15.1521 | 16.8614 | 16.1429 | 15.1623 | 12.1545 | 58.8521 |  | 20.2296 | 36.81 | 42.7923 | 16.4078 |  | 6.3881 | 6.4349 | 5.9273 | 6.0197 | 6.1183 | 6.7036 | 14.7307 | 4.8659 | 6.3953 | 4.813 | 6.6854 | 8.1449 | 42.152 | 46.7902 | 42.6297 | 14.9467 |  |  | -0.19232 | -0.31927 | 0.15824 | -0.14457 | -0.048464 | -0.1838 | 0.36197 | 0.12009 | -0.24713 | -0.040035 | -0.36373 | 8.8712 | 8.8725 | 2.005 | 15.8422 | 16.6663 | 17.2004 | 17.5257 | 17.4906 | 16.4663 | 14.8196 | 16.8287 | 17.1677 | 17.4711 | 17.5252 | 17.2542 | 16.4376 | 14.6533 | 14.2763 | 9.9246 | 10.3859 | 8.68 | 7.9582 | 7.335 | 7.8624 | 15.9183 | 15.4835 | 15.3305 | 14.2579 | 14.1548 | 14.1068 |  |  |  | 12.0223 | 55.9434 | 38.5627 | 15.8184 | 0.11391 | -0.0043038 | 15.4738 |  |  | 10.5936 |  |  | 16.8579 | 16.0435 | 15.151 | 16.3534 | 15.631 | 14.7599 | 43.5068 | 55.6704 | 32.0237 | 32.9274 | 16.2265 |  | 11.8901 | 18.7172 | 11.9543 | 15.0004 | 12.8072 | 45.2036 |  | 17.1743 |  |  | 12.1568 | 12.9667 | 16.2828 | [6 empty] | 15.2635 |  |  | 14.9177 |  |  | 10.5075 | 13.9243 | 71.6287 | 7.9095 | 11.6192 | 40.6831 | 8.4416 | 11.2156 | 45.9256 | 11.5304 | 30.4413 | 8.3873 | 27.563 | 9.0004 | 27.6556 | 8.3936 | 12.8862 | 40.0647 | 11.8789 | 12.8311 | 58.3341 | 8.8259 | 11.7041 | 46.8723 | 8.9324 | 27.7429 | 11.1622 | 25.8449 | 9.4361 | 27.9287 | -0.018309 | 20.7213 | 0.16242 | 0.05091 | -37.6662 | 3.1206 | 48.72 | 49.18 | -0.56322 | -0.65842 | 0.46354 | -0.44305 | -0.25665 | -0.4998 | 0.70141 | 0.25384 | 0.18677 | 0.31821 | -0.42032 | 0.073188 | 0.25753 | 0.26954
42810.4412 | 102 | 18.5964 | 18.6183 | 18.5885 | 18.599 | 17.9182 | 16.5337 | 14.5955 | 16.6853 | 17.1817 | 17.2845 | 17.2911 | 16.8318 | 15.8615 | 14.4727 | 14.9931 | 14.9372 | 15.4714 | 13.3328 | 13.4421 | 14.0033 |  |  |  | 16.5658 | 15.8916 | 15.0588 | 48.8226 | 49.5239 | 67.2934 | 17.2604 | 16.3471 | 15.1511 | 16.8595 | 16.1352 | 15.1618 | 12.1854 | 59.4507 |  | 20.3531 | 37.1159 | 43.0998 | 16.4221 |  | 6.3901 | 6.4259 | 5.9285 | 6.0188 | 6.1189 | 6.6847 | 14.5995 | 4.7982 | 6.3938 | 4.8842 | 6.6942 | 8.1516 | 42.1269 | 46.7988 | 42.6265 | 14.9536 |  |  | -0.2784 | -0.092565 | 0.31004 | -0.042714 | 0.10136 | -0.31456 | 0.42571 | 0.19631 | -0.34968 | -0.17473 | -0.37148 | 8.8694 | 8.8708 | 2.0059 | 15.8426 | 16.6687 | 17.2029 | 17.5192 | 17.4902 | 16.4592 | 14.8164 | 16.8291 | 17.1636 | 17.4756 | 17.5158 | 17.2492 | 16.4492 | 14.6514 | 14.764 | 9.8779 | 10.9369 | 8.9508 | 8.0381 | 7.3816 | 7.897 | 15.9165 | 15.4793 | 15.3339 | 14.2565 | 14.1559 | 14.1022 |  |  |  | 12.06 | 56.3568 | 39.3356 | 15.9004 | 0.091219 | 0.18408 | 15.4917 |  |  | 10.5921 |  |  | 16.8605 | 16.0538 | 15.1616 | 16.3554 | 15.6299 | 14.7648 | 43.858 | 55.9858 | 32.2595 | 33.1713 | 17.2023 |  | 11.9304 | 18.7852 | 11.9916 | 14.9328 | 12.8415 | 45.456 |  | 17.2726 |  |  | 12.1388 | 12.9644 | 16.4259 | [6 empty] | 15.2729 |  |  | 14.9548 |  |  | 10.5281 | 13.9805 | 71.8937 | 7.9217 | 11.6714 | 40.9384 | 8.466 | 11.2376 | 46.1123 | 11.5625 | 30.7157 | 8.3943 | 27.7565 | 9.0161 | 27.9092 | 8.3892 | 12.8794 | 40.3685 | 11.8995 | 12.8812 | 58.5067 | 8.8363 | 11.7118 | 47.2307 | 8.9278 | 27.9602 | 11.1912 | 26.3042 | 9.452 | 28.1393 | 0.15253 | 20.7187 | 0.16546 | 0.05086 | -37.6608 | 3.1206 | 51.48 | 50.39 | -0.67846 | -0.35452 | 0.64882 | -0.24083 | 0.37115 | -0.65384 | 0.76063 | 0.22806 | 0.18611 | 0.32122 | -0.4691 | 0.01598 | 0.25816 | 0.2685
42810.4412 | 103 | 18.5838 | 18.6129 | 18.5858 | 18.593 | 17.9146 | 16.5294 | 14.5866 | 16.6783 | 17.1814 | 17.2751 | 17.2883 | 16.828 | 15.8551 | 14.4679 | 14.9936 | 14.946 | 15.4752 | 13.3341 | 13.4568 | 14.0125 |  |  |  | 16.5747 | 15.9005 | 15.0685 | 49.2348 | 49.7418 | 67.4585 | 17.2663 | 16.3501 | 15.1543 | 16.8595 | 16.1352 | 15.1721 | 12.2271 | 59.889 |  | 20.4778 | 37.4616 | 43.3884 | 16.5724 |  | 6.3892 | 6.4316 | 5.927 | 6.0194 | 6.1177 | 6.6811 | 14.5782 | 4.8223 | 6.396 | 4.9241 | 6.7033 | 8.1478 | 42.1033 | 46.8127 | 42.6144 | 14.9608 |  |  | -0.28891 | -0.086653 | 0.38298 | 0.00197 | -0.088548 | -0.0366 | 0.30218 | 0.15689 | -0.75484 | -0.21627 | -0.28047 | 8.8698 | 8.871 | 2.0064 | 15.8367 | 16.6773 | 17.2106 | 17.5206 | 17.4964 | 16.4632 | 14.8167 | 16.8306 | 17.1716 | 17.4714 | 17.5164 | 17.2558 | 16.4429 | 14.6475 | 14.7624 | 9.6779 | 10.6633 | 9.1812 | 8.1014 | 7.4235 | 7.9013 | 15.9221 | 15.4854 | 15.3259 | 14.2644 | 14.151 | 14.0991 |  |  |  | 12.0877 | 56.6669 | 40.0118 | 15.7188 | 0.077239 | 0.027878 | 15.5806 |  |  | 10.5933 |  |  | 16.8616 | 16.0459 | 15.1599 | 16.3481 | 15.6292 | 14.7491 | 44.1724 | 56.5532 | 32.5348 | 33.485 | 17.8342 |  | 11.9703 | 20.012 | 12.0392 | 14.9824 | 12.8639 | 46.2627 |  | 17.3545 |  |  | 12.1368 | 12.9772 | 16.6232 | [6 empty] | 15.3654 |  |  | 14.9824 |  |  | 10.5325 | 14.0237 | 72.2059 | 7.9404 | 11.6762 | 41.1616 | 8.468 | 11.2535 | 46.3602 | 11.5884 | 31.0892 | 8.3878 | 27.9425 | 9.0261 | 28.1766 | 8.3813 | 12.869 | 40.6745 | 11.9207 | 12.9065 | 58.7636 | 8.8299 | 11.7257 | 47.5367 | 8.9383 | 28.1875 | 11.2169 | 26.9969 | 9.4601 | 28.3446 | 0.007114 | 20.7118 | 0.16859 | 0.050983 | -37.6745 | 3.1207 | 44.91 | 49.42 | -0.69132 | -0.34301 | 0.72112 | 0.05172 | -0.3469 | -0.22303 | 0.64083 | 0.21182 | 0.15361 | 0.32058 | -0.46406 | 0.046886 | 0.25536 | 0.27447
42810.4412 | 104 | 18.5802 | 18.616 | 18.5843 | 18.5887 | 17.9201 | 16.5296 | 14.5867 | 16.6752 | 17.1767 | 17.2775 | 17.2869 | 16.8146 | 15.8512 | 14.4698 | 14.9892 | 14.9349 | 15.4735 | 13.3267 | 13.4486 | 14.0088 |  |  |  | 16.5696 | 15.8953 | 15.0661 | 49.5691 | 49.9341 | 67.4604 | 17.2759 | 16.3521 | 15.1571 | 16.8637 | 16.1329 | 15.1762 | 12.2608 | 59.9927 |  | 20.5797 | 37.7721 | 43.6493 | 16.5209 |  | 6.3872 | 6.4226 | 5.911 | 6.0087 | 6.1089 | 6.6873 | 14.8277 | 4.8151 | 6.3949 | 4.8589 | 6.6961 | 8.1515 | 42.1001 | 46.8341 | 42.6212 | 14.9822 |  |  | -0.15617 | 0.16108 | 0.34815 | 0.012486 | 0.12896 | -0.22979 | 0.27129 | 0.01758 | 0.18683 | -0.94868 | -0.26617 | 8.872 | 8.8733 | 2.007 | 15.834 | 16.6755 | 17.2079 | 17.5234 | 17.4932 | 16.458 | 14.8123 | 16.8253 | 17.1655 | 17.4681 | 17.5161 | 17.251 | 16.4355 | 14.6473 | 14.4163 | 9.4782 | 10.2954 | 9.1085 | 8.1637 | 7.4468 | 7.9177 | 15.9098 | 15.4779 | 15.3394 | 14.2601 | 14.1555 | 14.1009 |  |  |  | 12.118 | 56.9408 | 40.515 | 15.5364 | -0.041687 | -0.027264 | 15.7672 |  |  | 10.6074 |  |  | 16.8631 | 16.0482 | 15.1719 | 16.3558 | 15.6378 | 14.762 | 44.4394 | 56.996 | 32.846 | 33.8403 | 18.1616 |  | 12.004 | 21.9021 | 12.0947 | 15.1187 | 12.9015 | 46.4183 |  | 17.4397 |  |  | 12.1103 | 12.9804 | 16.7063 | [6 empty] | 15.5141 |  |  | 15 |  |  | 10.5482 | 14.0763 | 72.7525 | 7.9572 | 11.6748 | 41.4588 | 8.4739 | 11.263 | 46.5706 | 11.6013 | 31.5276 | 8.3899 | 28.1943 | 9.0437 | 28.4695 | 8.3699 | 12.8713 | 40.9174 | 11.9334 | 12.9367 | 59.2054 | 8.836 | 11.7515 | 47.8173 | 8.9346 | 28.3886 | 11.2364 | 27.2668 | 9.4706 | 28.5635 | 0.15388 | 20.7061 | 0.17153 | 0.051345 | -37.696 | 3.1207 | 44.58 | 49.09 | -0.50828 | 0.46767 | 0.68754 | 0.1302 | 0.41865 | -0.55884 | 0.6072 | 0.20384 | 0.10294 | 0.31804 | -0.4229 | 0.089666 | 0.2579 | 0.28053
42810.4413 | 105 | 18.5753 | 18.6147 | 18.587 | 18.5898 | 17.909 | 16.5254 | 14.582 | 16.6761 | 17.1843 | 17.2766 | 17.2814 | 16.8187 | 15.8599 | 14.4692 | 14.9874 | 14.9339 | 15.4796 | 13.3279 | 13.4455 | 14.0129 |  |  |  | 16.5649 | 15.8893 | 15.0695 | 49.8053 | 50.0841 | 67.4331 | 17.2662 | 16.3472 | 15.1626 | 16.8632 | 16.1397 | 15.1697 | 12.2763 | 60.6011 |  | 20.7096 | 38.0559 | 43.9014 | 16.3066 |  | 6.3933 | 6.4189 | 5.9319 | 6.0191 | 6.1181 | 6.6889 | 14.9088 | 4.8082 | 6.4002 | 4.903 | 6.7063 | 8.1405 | 42.0949 | 46.8487 | 42.6261 | 14.9914 |  |  | -0.34871 | 0.10786 | 0.40269 | -0.00723 | -0.24297 | -0.23045 | 0.39877 | 0.082632 | -0.40028 | 1.0788 | -0.18112 | 8.8683 | 8.8695 | 2.0071 | 15.8354 | 16.6735 | 17.207 | 17.5302 | 17.4942 | 16.4584 | 14.8115 | 16.8282 | 17.171 | 17.4657 | 17.5212 | 17.2499 | 16.4391 | 14.6551 | 13.7696 | 9.2885 | 9.7051 | 9.0488 | 8.1017 | 7.4725 | 7.9327 | 15.9081 | 15.4801 | 15.3285 | 14.2508 | 14.1537 | 14.1013 |  |  |  | 12.1392 | 57.2902 | 41.1356 | 15.3997 | 0.030439 | -0.047778 | 15.9214 |  |  | 10.6086 |  |  | 16.8699 | 16.058 | 15.187 | 16.3582 | 15.6399 | 14.7653 | 44.7517 | 57.4927 | 33.1271 | 34.1635 | 18.9241 |  | 12.0403 | 23.1417 | 12.1376 | 15.5351 | 12.9464 | 47.1237 |  | 17.541 |  |  | 12.1379 | 13.0083 | 16.9077 | [6 empty] | 15.6867 |  |  | 15.0283 |  |  | 10.5558 | 14.1112 | 73.3086 | 7.9766 | 11.6728 | 41.7641 | 8.478 | 11.2958 | 46.8783 | 11.6327 | 31.8493 | 8.396 | 28.451 | 9.0524 | 28.7301 | 8.3599 | 12.8895 | 41.1727 | 11.9456 | 12.9799 | 59.5898 | 8.8373 | 11.7566 | 48.1773 | 8.9207 | 28.5408 | 11.2457 | 27.4871 | 9.4703 | 28.744 | 0.14617 | 20.7031 | 0.1756 | 0.051323 | -37.7321 | 3.1207 | 48.34 | 49.98 | -0.75947 | 0.38268 | 0.73943 | -0.099079 | -0.57464 | -0.55964 | 0.73618 | 0.18386 | 0.069919 | 0.30796 | -0.34806 | 0.157 | 0.26437 | 0.28503
42810.4413 | 106 | 18.5812 | 18.6091 | 18.5755 | 18.5805 | 17.9009 | 16.5197 | 14.5788 | 16.6748 | 17.1684 | 17.2703 | 17.2798 | 16.8081 | 15.8497 | 14.4606 | 14.9895 | 14.9251 | 15.472 | 13.3253 | 13.4454 | 14.0033 |  |  |  | 16.5696 | 15.8885 | 15.0646 | 50.0546 | 50.3018 | 67.2007 | 17.2626 | 16.3463 | 15.1537 | 16.86 | 16.1342 | 15.1666 | 12.3008 | 60.9432 |  | 20.8208 | 38.364 | 44.1219 | 16.1286 |  | 6.3852 | 6.4151 | 5.9171 | 6.0235 | 6.1277 | 6.7031 | 15.3499 | 4.8357 | 6.4009 | 4.8148 | 6.7137 | 8.1426 | 42.1029 | 46.8532 | 42.6312 | 15.0013 |  |  | -0.074693 | -0.050509 | 0.46249 | -0.12222 | -0.033348 | -0.009004 | 0.5164 | 0.030064 | -0.38043 | -0.54251 | -0.31187 | 8.8694 | 8.8704 | 2.0062 | 15.843 | 16.6842 | 17.2091 | 17.5352 | 17.4978 | 16.4672 | 14.8185 | 16.8312 | 17.175 | 17.4793 | 17.5302 | 17.2532 | 16.4488 | 14.6558 | 13.0752 | 9.127 | 9.1813 | 8.773 | 8.1321 | 7.4779 | 7.933 | 15.9203 | 15.4908 | 15.3389 | 14.259 | 14.1589 | 14.109 |  |  |  | 12.1683 | 57.7527 | 41.434 | 15.4037 | -0.033583 | 0.02976 | 15.9886 |  |  | 10.5933 |  |  | 16.8598 | 16.0394 | 15.1821 | 16.3457 | 15.6233 | 14.7485 | 45.1131 | 57.824 | 33.3799 | 34.4139 | 19.7621 |  | 12.1018 | 23.0951 | 12.2015 | 15.7868 | 12.999 | 48.008 |  | 17.6437 |  |  | 12.168 | 13.0004 | 17.0851 | [6 empty] | 15.8175 |  |  | 15.0502 |  |  | 10.5661 | 14.1479 | 73.4296 | 7.9841 | 11.6774 | 42.0753 | 8.4825 | 11.3155 | 47.1735 | 11.6551 | 32.0709 | 8.4054 | 28.7031 | 9.0666 | 28.9913 | 8.3671 | 12.9233 | 41.4679 | 11.9784 | 13.0146 | 60.0162 | 8.8475 | 11.7783 | 48.4309 | 8.9234 | 28.6636 | 11.2746 | 27.8003 | 9.4802 | 28.9548 | 0.0065362 | 20.6982 | 0.17959 | 0.050737 | -37.7502 | 3.1207 | 58.12 | 49.32 | -0.35137 | -0.26187 | 0.79243 | -0.40736 | -0.2129 | -0.11062 | 0.83777 | 0.16261 | 0.073327 | 0.30271 | -0.27027 | 0.21523 | 0.27012 | 0.28588
42810.4413 | 107 | 18.5751 | 18.6167 | 18.5868 | 18.5871 | 17.9095 | 16.5211 | 14.5794 | 16.6777 | 17.1749 | 17.2773 | 17.2815 | 16.8148 | 15.8468 | 14.4653 | 14.9866 | 14.9355 | 15.4781 | 13.3333 | 13.4521 | 14.0133 |  |  |  | 16.5735 | 15.898 | 15.0767 | 50.2714 | 50.5967 | 67.3438 | 17.2633 | 16.3464 | 15.1549 | 16.8606 | 16.1343 | 15.1682 | 12.3276 | 61.0503 |  | 20.9252 | 38.7142 | 44.3373 | 16.0888 |  | 6.3783 | 6.4155 | 5.9107 | 6.037 | 6.1316 | 6.7006 | 15.5691 | 4.8852 | 6.4045 | 4.7699 | 6.7208 | 8.1388 | 42.1135 | 46.8603 | 42.641 | 15.0068 |  |  | -0.23831 | -0.051169 | 0.38166 | -0.19319 | 0.16773 | -0.069456 | 0.48485 | 0.14572 | 0.24463 | -0.61153 | -0.17377 | 8.8696 | 8.8708 | 2.0063 | 15.8324 | 16.6682 | 17.1967 | 17.5209 | 17.4897 | 16.4503 | 14.7981 | 16.8173 | 17.157 | 17.4608 | 17.5096 | 17.2455 | 16.4265 | 14.6429 | 13.1439 | 8.9824 | 8.6805 | 8.4371 | 8.0261 | 7.5024 | 7.9367 | 15.9189 | 15.4863 | 15.3357 | 14.2649 | 14.1639 | 14.1065 |  |  |  | 12.198 | 58.1238 | 41.7155 | 15.6347 | 0.12728 | -0.12889 | 15.998 |  |  | 10.5861 |  |  | 16.8536 | 16.0526 | 15.1934 | 16.3459 | 15.622 | 14.7628 | 45.5664 | 58.1621 | 33.6055 | 34.6296 | 19.7629 |  | 12.1351 | 22.8443 | 12.2313 | 15.5901 | 13.0244 | 48.153 |  | 17.728 |  |  | 12.1949 | 13.0206 | 17.0239 | [6 empty] | 15.8465 |  |  | 15.087 |  |  | 10.5871 | 14.186 | 73.6257 | 7.987 | 11.6887 | 42.4458 | 8.4805 | 11.3394 | 47.4114 | 11.6752 | 32.281 | 8.4225 | 28.9491 | 9.084 | 29.241 | 8.373 | 12.958 | 41.7981 | 11.9952 | 13.0438 | 60.3543 | 8.8579 | 11.7945 | 48.6756 | 8.9286 | 28.7792 | 11.3073 | 28.0434 | 9.4925 | 29.1381 | 0.16851 | 20.6957 | 0.18322 | 0.05107 | -37.7995 | 3.1207 | 62.1 | 49.13 | -0.62776 | -0.26358 | 0.71986 | -0.51215 | 0.47746 | -0.30725 | 0.81177 | 0.16369 | 0.081279 | 0.30901 | -0.27508 | 0.27131 | 0.27211 | 0.28045
42810.4413 | 108 | 18.5782 | 18.6224 | 18.5926 | 18.5961 | 17.9115 | 16.5286 | 14.5832 | 16.6809 | 17.1856 | 17.2736 | 17.2948 | 16.8179 | 15.8589 | 14.4758 | 14.9828 | 14.9387 | 15.4791 | 13.329 | 13.4467 | 14.0084 |  |  |  | 16.5706 | 15.8997 | 15.0792 | 50.5941 | 50.8796 | 67.9885 | 17.2694 | 16.3493 | 15.1709 | 16.8621 | 16.1334 | 15.1775 | 12.3563 | 60.8176 |  | 21.0244 | 39.0794 | 44.555 | 16.7712 |  | 6.3878 | 6.4279 | 5.9219 | 6.0271 | 6.1202 | 6.6771 | 15.6811 | 4.9805 | 6.411 | 4.818 | 6.7074 | 8.1407 | 42.1389 | 46.8868 | 42.6521 | 15.0103 |  |  | -0.17326 | -0.11228 | 0.2049 | -0.14719 | 0.11844 | 0.096792 | 0.45265 | 0.10498 | 0.33628 | -0.46026 | -0.19086 | 8.8688 | 8.8698 | 2.0068 | 15.8373 | 16.6738 | 17.2079 | 17.5309 | 17.484 | 16.4577 | 14.8137 | 16.8277 | 17.1732 | 17.4783 | 17.5166 | 17.2517 | 16.4376 | 14.6475 | 13.9999 | 8.9477 | 8.2338 | 8.1494 | 7.838 | 7.547 | 7.9373 | 15.9164 | 15.4807 | 15.3332 | 14.2563 | 14.153 | 14.0943 |  |  |  | 12.2316 | 58.6369 | 42.0744 | 15.9251 | 0.168 | -0.073185 | 16.0429 |  |  | 10.5863 |  |  | 16.8594 | 16.0472 | 15.2003 | 16.3536 | 15.6238 | 14.7653 | 46.0018 | 58.5319 | 33.8104 | 34.8378 | 19.4057 |  | 12.1652 | 22.865 | 12.266 | 15.4371 | 13.0504 | 48.2671 |  | 17.8208 |  |  | 12.1765 | 13.0443 | 16.9227 | [6 empty] | 15.761 |  |  | 15.111 |  |  | 10.6 | 14.2308 | 73.8093 | 7.9798 | 11.6813 | 42.7818 | 8.4832 | 11.3505 | 47.6338 | 11.7016 | 32.5277 | 8.4252 | 29.1773 | 9.0902 | 29.4626 | 8.376 | 12.9871 | 42.0652 | 12.0104 | 13.0652 | 60.5783 | 8.858 | 11.8053 | 48.8811 | 8.9415 | 28.8816 | 11.3215 | 28.2957 | 9.4952 | 29.3434 | 0.032537 | 20.689 | 0.18665 | 0.049079 | -37.769 | 3.1208 | 61.45 | 49.82 | -0.53578 | -0.39045 | 0.52746 | -0.44706 | 0.40121 | 0.36269 | 0.78432 | 0.17461 | 0.081849 | 0.31412 | -0.36499 | 0.32101 | 0.25411 | 0.27349
42810.4413 | 109 | 18.5794 | 18.6177 | 18.5829 | 18.5939 | 17.9074 | 16.5246 | 14.5783 | 16.68 | 17.1859 | 17.2706 | 17.2894 | 16.821 | 15.8551 | 14.4746 | 14.9836 | 14.9374 | 15.4856 | 13.33 | 13.4461 | 14.0085 |  |  |  | 16.5701 | 15.8965 | 15.0803 | 50.9115 | 51.2033 | 68.3359 | 17.2656 | 16.3486 | 15.1717 | 16.8623 | 16.1323 | 15.1742 | 12.3989 | 60.3372 |  | 21.1182 | 39.4275 | 44.7752 | 17.807 |  | 6.4021 | 6.4293 | 5.9344 | 6.0329 | 6.1241 | 6.6887 | 15.6972 | 5.0517 | 6.4135 | 4.8677 | 6.7101 | 8.1461 | 42.1664 | 46.9172 | 42.6522 | 15.0146 |  |  | -0.2278 | -0.058397 | 0.034048 | 0.036798 | 0.37735 | 0.34321 | 0.4244 | 0.10958 | -0.98096 | -0.37592 | -0.41281 | 8.8708 | 8.8722 | 2.0069 | 15.8295 | 16.6737 | 17.2051 | 17.5296 | 17.4802 | 16.4503 | 14.8048 | 16.8196 | 17.1628 | 17.4604 | 17.5058 | 17.2437 | 16.4296 | 14.6378 | 15.1023 | 9.4311 | 8.1652 | 7.8231 | 7.7143 | 7.6083 | 7.9427 | 15.9156 | 15.4794 | 15.3341 | 14.2549 | 14.1559 | 14.1001 |  |  |  | 12.2696 | 59.0751 | 42.2547 | 15.9414 | -0.20579 | -0.20097 | 16.1051 |  |  | 10.5821 |  |  | 16.8565 | 16.0551 | 15.2107 | 16.3527 | 15.6295 | 14.7705 | 46.3014 | 58.93 | 34.031 | 35.0164 | 19.0485 |  | 12.1941 | 22.4611 | 12.288 | 15.3462 | 13.0856 | 48.6435 |  | 17.9322 |  |  | 12.1495 | 13.0488 | 16.7858 | [6 empty] | 15.6888 |  |  | 15.1394 |  |  | 10.6172 | 14.2747 | 74.1435 | 7.9855 | 11.6771 | 43.0546 | 8.4866 | 11.3551 | 47.8106 | 11.7233 | 32.952 | 8.4211 | 29.3687 | 9.1004 | 29.6705 | 8.3951 | 13.0451 | 42.3449 | 12.0303 | 13.1077 | 60.8314 | 8.8645 | 11.8259 | 49.0991 | 8.9514 | 29.0078 | 11.3331 | 28.5732 | 9.5042 | 29.5942 | 0.047753 | 20.6835 | 0.19063 | 0.049832 | -37.6773 | 3.1207 | 60.12 | 48.86 | -0.61465 | -0.28159 | 0.21501 | 0.22353 | 0.71613 | 0.68297 | 0.75946 | 0.18549 | 0.093799 | 0.31781 | -0.48037 | 0.32926 | 0.22674 | 0.27429
42810.4413 | 110 | 18.5764 | 18.6052 | 18.5793 | 18.5874 | 17.903 | 16.5231 | 14.5794 | 16.6749 | 17.176 | 17.2739 | 17.2784 | 16.8146 | 15.8526 | 14.4631 | 14.989 | 14.935 | 15.4823 | 13.3297 | 13.4505 | 14.0047 |  |  |  | 16.5766 | 15.8931 | 15.0838 | 51.1535 | 51.552 | 68.2836 | 17.2737 | 16.3506 | 15.1734 | 16.8679 | 16.1358 | 15.1866 | 12.442 | 60.2904 |  | 21.222 | 39.7557 | 45.0155 | 18.3547 |  | 6.406 | 6.4323 | 5.9462 | 6.0487 | 6.1325 | 6.7932 | 16.1204 | 5.0962 | 6.4198 | 4.9143 | 6.7259 | 8.1489 | 42.1936 | 46.9507 | 42.6707 | 15.0247 |  |  | -0.23437 | -0.17471 | 0.30084 | -0.26087 | 0.27155 | -0.099028 | 0.42571 | -0.12896 | -0.33042 | 0.14312 | -0.34664 | 8.8693 | 8.8704 | 2.0067 | 15.832 | 16.6693 | 17.2003 | 17.5189 | 17.4822 | 16.4527 | 14.8046 | 16.8189 | 17.1632 | 17.4583 | 17.5035 | 17.2398 | 16.4296 | 14.6373 | 15.3513 | 9.9448 | 9.2465 | 7.7412 | 7.5628 | 7.6467 | 7.9508 | 15.9166 | 15.4856 | 15.333 | 14.2558 | 14.156 | 14.1035 |  |  |  | 12.2991 | 59.3226 | 42.43 | 15.9524 | 0.054548 | -0.1718 | 16.144 |  |  | 10.5748 |  |  | 16.8612 | 16.0535 | 15.2158 | 16.352 | 15.6226 | 14.7662 | 46.6888 | 59.348 | 34.2877 | 35.2153 | 18.7627 |  | 12.2215 | 21.2129 | 12.324 | 15.312 | 13.1131 | 48.6095 |  | 18.0265 |  |  | 12.1601 | 13.0441 | 16.7033 | [6 empty] | 15.6768 |  |  | 15.143 |  |  | 10.6236 | 14.3222 | 74.5441 | 7.9903 | 11.685 | 43.2959 | 8.486 | 11.3692 | 48.053 | 11.7402 | 33.4337 | 8.416 | 29.5046 | 9.1051 | 29.9089 | 8.4101 | 13.1255 | 42.6237 | 12.0449 | 13.1515 | 61.1679 | 8.86 | 11.8534 | 49.3555 | 8.9579 | 29.1469 | 11.3433 | 28.7961 | 9.5123 | 29.8361 | 0.094169 | 20.6773 | 0.1968 | 0.050447 | -37.5995 | 3.1207 | 62.41 | 49.47 | -0.62341 | -0.48705 | 0.63913 | -0.59516 | 0.60761 | -0.36693 | 0.76078 | 0.19433 | 0.12966 | 0.31967 | -0.50357 | 0.21006 | 0.21295 | 0.27496
42810.4413 | 111 | 18.5866 | 18.6086 | 18.5812 | 18.5821 | 17.9023 | 16.5276 | 14.5809 | 16.6781 | 17.1716 | 17.2725 | 17.2898 | 16.8155 | 15.8423 | 14.4682 | 14.9874 | 14.9341 | 15.4735 | 13.3312 | 13.4528 | 14.0127 |  |  |  | 16.5676 | 15.8945 | 15.0921 | 51.3484 | 51.8068 | 68.2453 | 17.271 | 16.3514 | 15.1697 | 16.8583 | 16.1358 | 15.1815 | 12.4793 | 60.6597 |  | 21.3391 | 40.0676 | 45.2665 | 18.3997 |  | 6.4074 | 6.4359 | 5.9485 | 6.0452 | 6.1454 | 6.8416 | 16.4466 | 5.049 | 6.4214 | 4.9259 | 6.7259 | 8.1472 | 42.1979 | 46.9512 | 42.6575 | 15.0128 |  |  | -0.18903 | -0.12148 | 0.28967 | 0.051254 | 0.3734 | -0.11546 | 0.62022 | 0.043864 | -0.35416 | -0.17536 | -0.3683 | 8.8665 | 8.868 | 2.0061 | 15.8366 | 16.676 | 17.2005 | 17.5262 | 17.4852 | 16.451 | 14.8068 | 16.8193 | 17.1633 | 17.4624 | 17.5065 | 17.2449 | 16.433 | 14.6416 | 15.633 | 10.1929 | 10.2388 | 8.3001 | 7.4761 | 7.6919 | 7.9763 | 15.9245 | 15.4924 | 15.3345 | 14.2648 | 14.1663 | 14.1137 |  |  |  | 12.3397 | 59.5515 | 42.4303 | 16.069 | 0.011192 | -0.092946 | 16.1182 |  |  | 10.573 |  |  | 16.8484 | 16.05 | 15.2256 | 16.3559 | 15.6251 | 14.7688 | 47.0959 | 59.8198 | 34.552 | 35.4833 | 18.6767 |  | 12.2495 | 20.2485 | 12.3511 | 15.4296 | 13.1428 | 48.6182 |  | 18.102 |  |  | 12.1833 | 13.0602 | 16.8722 | [6 empty] | 15.8272 |  |  | 15.1281 |  |  | 10.6342 | 14.3683 | 74.8139 | 7.9918 | 11.7244 | 43.5358 | 8.492 | 11.39 | 48.4165 | 11.7655 | 33.7788 | 8.4226 | 29.6362 | 9.1135 | 30.1892 | 8.4273 | 13.1807 | 42.8601 | 12.0619 | 13.192 | 61.4368 | 8.8755 | 11.904 | 49.6124 | 8.9631 | 29.3679 | 11.367 | 29.0041 | 9.5265 | 30.0945 | 0.26809 | 20.6712 | 0.20176 | 0.051649 | -37.7141 | 3.1207 | 40.04 | 49.75 | -0.55983 | -0.40614 | 0.62716 | 0.26381 | 0.71257 | -0.39623 | 0.91836 | 0.19765 | 0.15734 | 0.31739 | -0.52963 | 0.10277 | 0.21294 | 0.27306
42810.4413 | 112 | 18.59 | 18.6097 | 18.5839 | 18.599 | 17.9121 | 16.5266 | 14.5898 | 16.6742 | 17.1829 | 17.2754 | 17.2852 | 16.8237 | 15.8497 | 14.4698 | 14.9875 | 14.941 | 15.4751 | 13.343 | 13.4502 | 14.0152 |  |  |  | 16.5726 | 15.9012 | 15.0954 | 51.5949 | 52.0312 | 68.8059 | 17.2799 | 16.3637 | 15.1759 | 16.8656 | 16.1373 | 15.1858 | 12.5235 | 61.0374 |  | 21.4778 | 40.3846 | 45.5104 | 18.2532 |  | 6.4143 | 6.4324 | 5.9576 | 6.0588 | 6.1559 | 6.8428 | 16.6662 | 4.9844 | 6.4263 | 4.9443 | 6.7293 | 8.1498 | 42.2187 | 46.9456 | 42.6671 | 15.0013 |  |  | -0.21926 | 0.025059 | 0.17139 | -0.077538 | -0.12337 | 0.02714 | 0.35803 | 0.11286 | -0.95158 | -0.33501 | -0.16344 | 8.8697 | 8.8706 | 2.0057 | 15.8383 | 16.6759 | 17.208 | 17.5294 | 17.4812 | 16.4513 | 14.8071 | 16.8232 | 17.1599 | 17.4654 | 17.5074 | 17.2445 | 16.4319 | 14.6383 | 15.86 | 9.9718 | 10.539 | 8.5549 | 7.5916 | 7.7387 | 7.9906 | 15.929 | 15.4962 | 15.3397 | 14.27 | 14.1614 | 14.1105 |  |  |  | 12.3753 | 59.8642 | 42.4733 | 16.3225 | -0.083625 | 0.0037888 | 16.0903 |  |  | 10.5807 |  |  | 16.8592 | 16.0438 | 15.2385 | 16.3535 | 15.6271 | 14.7573 | 47.5472 | 60.1149 | 34.9295 | 35.8417 | 19.4927 |  | 12.2901 | 19.4971 | 12.3712 | 15.6002 | 13.184 | 48.3875 |  | 18.2033 |  |  | 12.2001 | 13.0686 | 17.1357 | [6 empty] | 16.0342 |  |  | 15.1481 |  |  | 10.6389 | 14.4108 | 75.1573 | 7.9948 | 11.769 | 43.7502 | 8.5031 | 11.4128 | 48.759 | 11.7774 | 33.9929 | 8.4259 | 29.8182 | 9.1241 | 30.4372 | 8.4505 | 13.1884 | 43.1359 | 12.0726 | 13.2207 | 61.5696 | 8.8867 | 11.9568 | 49.8083 | 8.9769 | 29.6513 | 11.395 | 29.3608 | 9.5349 | 30.3285 | 0.15253 | 20.6617 | 0.20669 | 0.051171 | -37.737 | 3.1207 | 50.66 | 49 | -0.60343 | 0.18446 | 0.48241 | -0.32447 | -0.40959 | 0.19211 | 0.69775 | 0.17632 | 0.17888 | 0.31402 | -0.54941 | 0.071068 | 0.21847 | 0.2672
42810.4413 | 113 | 18.593 | 18.6114 | 18.5893 | 18.597 | 17.9123 | 16.527 | 14.5799 | 16.677 | 17.1757 | 17.2739 | 17.2844 | 16.8278 | 15.8555 | 14.4672 | 14.9984 | 14.9422 | 15.4789 | 13.3367 | 13.4536 | 14.0178 |  |  |  | 16.5718 | 15.8973 | 15.1041 | 51.9413 | 52.3376 | 69.3229 | 17.27 | 16.3524 | 15.1831 | 16.8656 | 16.1377 | 15.1935 | 12.5476 | 61.6801 |  | 21.6166 | 40.6791 | 45.7568 | 18.3191 |  | 6.4117 | 6.4275 | 5.9518 | 6.0674 | 6.1659 | 6.8203 | 16.6086 | 4.7606 | 6.4217 | 4.9156 | 6.7352 | 8.1474 | 42.2337 | 46.9535 | 42.6843 | 14.9931 |  |  | -0.26394 | 0.10194 | 0.14247 | 0.07951 | 0.075076 | 0.1993 | 0.25946 | 0.14112 | -1.1195 | -0.58048 | -0.35459 | 8.8682 | 8.8695 | 2.0059 | 15.8398 | 16.6774 | 17.2087 | 17.5262 | 17.4847 | 16.4592 | 14.8035 | 16.8256 | 17.1641 | 17.4632 | 17.5087 | 17.245 | 16.4318 | 14.6346 | 15.2687 | 9.6553 | 9.9824 | 8.5886 | 7.5282 | 7.7663 | 8.0015 | 15.9309 | 15.492 | 15.3398 | 14.2663 | 14.1606 | 14.0969 |  |  |  | 12.401 | 60.2541 | 42.6814 | 16.561 | 0.085141 | 0.17787 | 16.1805 |  |  | 10.5672 |  |  | 16.848 | 16.0393 | 15.2334 | 16.3532 | 15.6155 | 14.7611 | 47.8768 | 60.4708 | 35.2297 | 36.213 | 19.8298 |  | 12.3426 | 21.1001 | 12.4237 | 15.5475 | 13.2303 | 48.5952 |  | 18.3246 |  |  | 12.2232 | 13.0796 | 17.3767 | [6 empty] | 16.0526 |  |  | 15.1723 |  |  | 10.6507 | 14.4503 | 75.3243 | 8.0022 | 11.812 | 43.8858 | 8.5092 | 11.4303 | 49.0366 | 11.7958 | 34.2317 | 8.4316 | 30.0322 | 9.1314 | 30.6611 | 8.4705 | 13.1723 | 43.4171 | 12.0804 | 13.2516 | 61.7618 | 8.8888 | 11.9906 | 50.0782 | 8.9847 | 29.9393 | 11.4205 | 29.6607 | 9.5389 | 30.5501 | 0.20203 | 20.6536 | 0.21185 | 0.051113 | -37.804 | 3.1208 | 39.26 | 50.08 | -0.66257 | 0.37204 | 0.43983 | 0.32857 | 0.3195 | 0.52057 | 0.59396 | 0.16869 | 0.13609 | 0.31701 | -0.4805 | 0.13418 | 0.21744 | 0.26142
42810.4414 | 114 | 18.5899 | 18.6201 | 18.5876 | 18.5971 | 17.9128 | 16.5295 | 14.5846 | 16.6817 | 17.1884 | 17.2791 | 17.2898 | 16.8294 | 15.8522 | 14.4778 | 14.9914 | 14.944 | 15.4815 | 13.333 | 13.4533 | 14.0142 |  |  |  | 16.5702 | 15.8912 | 15.103 | 52.3392 | 52.5848 | 69.5653 | 17.2666 | 16.3495 | 15.1813 | 16.8612 | 16.1285 | 15.1811 | 12.5708 | 61.9206 |  | 21.7193 | 40.9707 | 46.0161 | 18.3157 |  | 6.4147 | 6.4359 | 5.9519 | 6.0672 | 6.1672 | 6.8187 | 16.7013 | 4.6378 | 6.4194 | 4.7933 | 6.7352 | 8.1479 | 42.2514 | 46.9575 | 42.7075 | 14.9964 |  |  | -0.306 | -0.25356 | 0.097788 | -0.15574 | 0.066532 | -0.16211 | 0.06824 | 0.264 | -1.4797 | -0.84021 | -0.30611 | 8.8714 | 8.8728 | 2.0059 | 15.8487 | 16.6814 | 17.2067 | 17.5309 | 17.4918 | 16.463 | 14.8069 | 16.8278 | 17.1686 | 17.4726 | 17.5119 | 17.2465 | 16.436 | 14.6481 | 14.5318 | 9.4307 | 9.3616 | 8.3558 | 7.513 | 7.7807 | 8.0156 | 15.9204 | 15.4969 | 15.3401 | 14.2586 | 14.1626 | 14.1087 |  |  |  | 12.434 | 60.647 | 42.9095 | 16.4872 | -0.017577 | 0.17543 | 16.4227 |  |  | 10.5869 |  |  | 16.8596 | 16.0536 | 15.2474 | 16.3561 | 15.6313 | 14.7744 | 48.132 | 60.905 | 35.4919 | 36.5273 | 19.6502 |  | 12.3695 | 23.5796 | 12.4881 | 15.4487 | 13.266 | 48.8184 |  | 18.419 |  |  | 12.2375 | 13.0722 | 17.4494 | [6 empty] | 15.9809 |  |  | 15.2013 |  |  | 10.6622 | 14.4916 | 75.3941 | 8.006 | 11.8679 | 44.0787 | 8.517 | 11.4462 | 49.297 | 11.8282 | 34.5309 | 8.4402 | 30.2854 | 9.1563 | 30.8891 | 8.4831 | 13.1553 | 43.6561 | 12.0973 | 13.2647 | 61.9343 | 8.8878 | 12.0149 | 50.2835 | 8.9895 | 30.2145 | 11.4365 | 29.848 | 9.5507 | 30.7169 | 0.14752 | 20.6462 | 0.21656 | 0.049738 | -37.8136 | 3.1207 | 35.22 | 49.12 | -0.71366 | -0.58676 | 0.36439 | -0.45986 | 0.30077 | -0.46949 | 0.30461 | 0.17457 | 0.069344 | 0.32094 | -0.39695 | 0.20479 | 0.2183 | 0.26456
42810.4414 | 115 | 18.5894 | 18.6159 | 18.5863 | 18.5952 | 17.9149 | 16.525 | 14.5825 | 16.6777 | 17.1846 | 17.2749 | 17.2927 | 16.8257 | 15.8547 | 14.4754 | 14.9922 | 14.9382 | 15.4874 | 13.3329 | 13.4503 | 14.0225 |  |  |  | 16.5747 | 15.8861 | 15.1117 | 52.722 | 52.8068 | 69.7968 | 17.2702 | 16.3527 | 15.1807 | 16.8661 | 16.1312 | 15.193 | 12.5942 | 62.0956 |  | 21.8283 | 41.242 | 46.2712 | 18.103 |  | 6.4246 | 6.4542 | 5.9488 | 6.0777 | 6.1743 | 6.8142 | 16.8202 | 4.5311 | 6.4236 | 4.5911 | 6.7449 | 8.1523 | 42.2602 | 46.9779 | 42.7245 | 15.0068 |  |  | -0.25014 | 0.062515 | 0.23381 | -0.22868 | 0.002136 | -0.38684 | 0.22398 | 0.37768 | -0.61317 | 0.82455 | -0.43824 | 8.8708 | 8.8724 | 2.0053 | 15.8478 | 16.6816 | 17.2072 | 17.5366 | 17.5011 | 16.464 | 14.8139 | 16.8233 | 17.1707 | 17.4729 | 17.5192 | 17.2511 | 16.4338 | 14.6444 | 14.2935 | 9.292 | 8.8517 | 8.239 | 7.5141 | 7.7912 | 8.0067 | 15.9233 | 15.4902 | 15.3363 | 14.2566 | 14.1537 | 14.1062 |  |  |  | 12.4672 | 60.9296 | 43.217 | 16.425 | 0.057182 | 0.13271 | 16.6324 |  |  | 10.5837 |  |  | 16.8634 | 16.0552 | 15.2724 | 16.3632 | 15.6345 | 14.7813 | 48.4318 | 61.3899 | 35.7438 | 36.7539 | 19.4091 |  | 12.4007 | 25.0732 | 12.553 | 15.3135 | 13.289 | 49.1707 |  | 18.5403 |  |  | 12.2513 | 13.0794 | 17.3646 | [6 empty] | 15.925 |  |  | 15.2381 |  |  | 10.6787 | 14.5261 | 75.6955 | 8.018 | 11.9172 | 44.2863 | 8.5197 | 11.4657 | 49.5557 | 11.8514 | 34.8424 | 8.4525 | 30.4296 | 9.1598 | 31.101 | 8.4954 | 13.15 | 43.9018 | 12.1215 | 13.3081 | 62.0105 | 8.8931 | 12.0521 | 50.4762 | 9.0018 | 30.476 | 11.4555 | 30.0777 | 9.5679 | 30.9079 | 0.036389 | 20.6379 | 0.22235 | 0.0512 | -37.865 | 3.1208 | 51.37 | 48.98 | -0.64547 | 0.29136 | 0.56347 | -0.55725 | 0.053891 | -0.72525 | 0.55185 | 0.1823 | 0.029999 | 0.32545 | -0.36926 | 0.26041 | 0.22498 | 0.26739
42810.4414 | 116 | 18.5857 | 18.6103 | 18.5842 | 18.5936 | 17.9119 | 16.5203 | 14.5767 | 16.6773 | 17.1738 | 17.2707 | 17.2867 | 16.8218 | 15.8572 | 14.4723 | 14.9994 | 14.9422 | 15.4744 | 13.3421 | 13.4608 | 14.0143 |  |  |  | 16.5749 | 15.8954 | 15.1146 | 53.1252 | 53.1402 | 69.8752 | 17.2725 | 16.3456 | 15.1792 | 16.8638 | 16.1299 | 15.1995 | 12.6148 | 62.2931 |  | 21.9547 | 41.4946 | 46.5391 | 17.8777 |  | 6.4284 | 6.4563 | 5.9612 | 6.0804 | 6.1751 | 6.8103 | 17.164 | 4.3856 | 6.4225 | 4.3721 | 6.7412 | 8.163 | 42.2438 | 46.9872 | 42.7555 | 15.0221 |  |  | -0.14041 | -0.015025 | 0.18782 | -0.10317 | -0.070148 | -0.29813 | 0.49405 | -0.007392 | -0.5906 | -0.64132 | 0.038837 | 8.8704 | 8.8716 | 2.0043 | 15.8429 | 16.6877 | 17.2092 | 17.5305 | 17.4968 | 16.4582 | 14.8172 | 16.8245 | 17.1668 | 17.4645 | 17.5135 | 17.2473 | 16.4333 | 14.6498 | 13.9849 | 9.2119 | 8.5487 | 8.0802 | 7.5866 | 7.8208 | 8.0284 | 15.9206 | 15.498 | 15.3423 | 14.2606 | 14.164 | 14.1119 |  |  |  | 12.4966 | 61.1281 | 43.4091 | 16.3227 | -0.054248 | -0.0075032 | 16.7383 |  |  | 10.5872 |  |  | 16.863 | 16.056 | 15.2658 | 16.3532 | 15.6325 | 14.783 | 48.8143 | 61.7378 | 35.9853 | 36.9532 | 19.6306 |  | 12.4471 | 24.1192 | 12.6286 | 15.3066 | 13.3299 | 49.7502 |  | 18.6713 |  |  | 12.2856 | 13.1053 | 17.4091 | [6 empty] | 15.9657 |  |  | 15.2619 |  |  | 10.684 | 14.5556 | 75.9946 | 8.0295 | 11.9666 | 44.5077 | 8.5207 | 11.4703 | 49.9515 | 11.8713 | 35.1107 | 8.472 | 30.5596 | 9.1606 | 31.3682 | 8.5084 | 13.1677 | 44.1456 | 12.1196 | 13.3561 | 62.1995 | 8.8992 | 12.0549 | 50.5522 | 9.007 | 30.6609 | 11.4873 | 30.4435 | 9.588 | 31.1119 | 0.12595 | 20.6277 | 0.22765 | 0.05057 | -37.8053 | 3.1208 | 27.38 | 50.3 | -0.48364 | -0.14284 | 0.50502 | -0.37429 | -0.30883 | -0.63668 | 0.8196 | 0.17768 | 0.058999 | 0.327 | -0.33153 | 0.2966 | 0.23192 | 0.2712
42810.4414 | 117 | 18.5889 | 18.6126 | 18.5831 | 18.5926 | 17.9032 | 16.5228 | 14.5742 | 16.6751 | 17.1749 | 17.2667 | 17.2862 | 16.8174 | 15.854 | 14.4665 | 14.9886 | 14.9527 | 15.4961 | 13.3439 | 13.4571 | 14.0262 |  |  |  | 16.579 | 15.9037 | 15.1307 | 53.3674 | 53.4346 | 69.5837 | 17.277 | 16.3467 | 15.1875 | 16.8671 | 16.1337 | 15.2062 | 12.643 | 62.6338 |  | 22.0934 | 41.7825 | 46.8112 | 17.794 |  | 6.4248 | 6.4523 | 5.9575 | 6.0864 | 6.1688 | 6.8222 | 17.6933 | 4.3511 | 6.4246 | 4.2656 | 6.7475 | 8.1549 | 42.2191 | 47.0006 | 42.7661 | 15.0308 |  |  | -0.27577 | -0.089281 | 0.19176 | 0.059142 | -0.1536 | -0.37107 | 0.052472 | 0.088548 | -0.30278 | -0.54041 | -0.23596 | 8.8692 | 8.8704 | 2.004 | 15.8433 | 16.6878 | 17.212 | 17.5313 | 17.4921 | 16.4607 | 14.8165 | 16.827 | 17.1636 | 17.4674 | 17.5139 | 17.256 | 16.4308 | 14.6397 | 13.2137 | 9.0775 | 8.1421 | 7.9982 | 7.6246 | 7.8378 | 8.0292 | 15.9284 | 15.4994 | 15.3499 | 14.2664 | 14.1675 | 14.1224 |  |  |  | 12.5355 | 61.3229 | 43.6277 | 16.2671 | -0.16183 | -0.16936 | 16.8681 |  |  | 10.5902 |  |  | 16.8621 | 16.0385 | 15.2684 | 16.3471 | 15.6256 | 14.7757 | 49.1106 | 62.0292 | 36.2035 | 37.1306 | 20.2206 |  | 12.4923 | 23.0314 | 12.6826 | 15.6236 | 13.3658 | 50.2023 |  | 18.774 |  |  | 12.2922 | 13.1151 | 17.7112 | [6 empty] | 16.0591 |  |  | 15.295 |  |  | 10.6847 | 14.6009 | 76.3844 | 8.0382 | 11.9949 | 44.8201 | 8.5309 | 11.4963 | 50.4184 | 11.8857 | 35.5697 | 8.481 | 30.7899 | 9.1567 | 31.638 | 8.5186 | 13.2248 | 44.4123 | 12.1289 | 13.382 | 62.5675 | 8.9092 | 12.081 | 50.7974 | 9.0249 | 30.9113 | 11.4935 | 30.5964 | 9.6027 | 31.4987 | 0.34436 | 20.6213 | 0.23227 | 0.049897 | -37.7025 | 3.1207 | 33.91 | 49.17 | -0.67751 | -0.34819 | 0.51028 | 0.28339 | -0.457 | -0.71032 | 0.26711 | 0.16279 | 0.091003 | 0.31938 | -0.24388 | 0.34187 | 0.23517 | 0.27403
42810.4414 | 118 | 18.5956 | 18.6108 | 18.5972 | 18.5973 | 17.9086 | 16.5323 | 14.5777 | 16.6768 | 17.1843 | 17.2727 | 17.2881 | 16.8232 | 15.8586 | 14.4773 | 14.9985 | 14.939 | 15.4871 | 13.3347 | 13.4498 | 14.0106 |  |  |  | 16.5661 | 15.9007 | 15.1162 | 53.5791 | 53.6264 | 69.8308 | 17.2803 | 16.3528 | 15.1886 | 16.8685 | 16.1412 | 15.209 | 12.6764 | 63.0311 |  | 22.2353 | 42.0972 | 47.0491 | 18.2345 |  | 6.4278 | 6.4509 | 5.9707 | 6.0929 | 6.1786 | 6.9515 | 18.2684 | 4.348 | 6.4188 | 4.1814 | 6.7532 | 8.1598 | 42.2041 | 47.0243 | 42.7813 | 15.0373 |  |  | -0.10886 | 0.015859 | 0.020908 | -0.40281 | -0.20354 | -0.27645 | -0.014556 | 0.241 | -1.5253 | -0.37865 | -0.28326 | 8.8691 | 8.87 | 2.0049 | 15.846 | 16.6887 | 17.2166 | 17.5293 | 17.4949 | 16.4588 | 14.8117 | 16.8241 | 17.167 | 17.4613 | 17.5096 | 17.2526 | 16.4332 | 14.6447 | 12.269 | 8.9873 | 7.8847 | 7.8266 | 7.7352 | 7.8458 | 8.029 | 15.9225 | 15.5021 | 15.3416 | 14.2638 | 14.1574 | 14.11 |  |  |  | 12.5681 | 61.6106 | 44.0771 | 16.5412 | -0.019603 | -0.079396 | 16.8912 |  |  | 10.5901 |  |  | 16.8636 | 16.0561 | 15.2801 | 16.3555 | 15.6299 | 14.7964 | 49.4558 | 62.4563 | 36.5425 | 37.3832 | 20.518 |  | 12.5296 | 22.0875 | 12.7328 | 16.0171 | 13.4096 | 50.7796 |  | 18.8722 |  |  | 12.3054 | 13.1164 | 18.0303 | [6 empty] | 16.1869 |  |  | 15.3395 |  |  | 10.7037 | 14.6409 | 76.6754 | 8.0476 | 12.004 | 45.1207 | 8.536 | 11.5225 | 50.738 | 11.9091 | 35.7638 | 8.4871 | 31.1026 | 9.1631 | 31.869 | 8.5479 | 13.3028 | 44.6427 | 12.1664 | 13.4172 | 62.7827 | 8.9366 | 12.1004 | 51.0427 | 9.0426 | 31.1666 | 11.5145 | 30.7533 | 9.6203 | 31.7929 | 0.087813 | 20.6111 | 0.23697 | 0.049021 | -37.6137 | 3.1208 | 35.82 | 48.59 | -0.42583 | 0.14675 | 0.1685 | -0.73958 | -0.5262 | -0.61324 | -0.14072 | 0.15576 | 0.11888 | 0.30991 | -0.13798 | 0.37046 | 0.22404 | 0.2675
42810.4414 | 119 | 18.5868 | 18.6171 | 18.5938 | 18.5913 | 17.9105 | 16.5343 | 14.5826 | 16.6826 | 17.1773 | 17.2729 | 17.2852 | 16.8235 | 15.8569 | 14.4785 | 14.9951 | 14.9429 | 15.4825 | 13.3323 | 13.4545 | 14.0205 |  |  |  | 16.5679 | 15.8963 | 15.124 | 53.8864 | 53.8771 | 70.3936 | 17.2841 | 16.357 | 15.2028 | 16.8734 | 16.1338 | 15.2079 | 12.7163 | 63.2843 |  | 22.3513 | 42.3818 | 47.2395 | 19.8025 |  | 6.422 | 6.4496 | 5.9656 | 6.0956 | 6.1746 | 7.1542 | 18.6588 | 4.4178 | 6.4155 | 4.2161 | 6.7473 | 8.1507 | 42.1925 | 47.0416 | 42.7948 | 15.0383 |  |  | -0.10952 | -0.10768 | 0.080704 | -0.045998 | -0.16543 | -0.36122 | 0.3738 | 0.2272 | -0.56316 | -0.31089 | -0.28584 | 8.8691 | 8.8701 | 2.0057 | 15.8466 | 16.6867 | 17.2173 | 17.5332 | 17.5036 | 16.4669 | 14.8105 | 16.8222 | 17.1733 | 17.4627 | 17.5126 | 17.2536 | 16.4331 | 14.6459 | 11.4638 | 8.8729 | 7.7945 | 7.588 | 7.6912 | 7.8431 | 8.0283 | 15.9263 | 15.4924 | 15.337 | 14.2572 | 14.1515 | 14.108 |  |  |  | 12.6045 | 61.7769 | 44.1615 | 17.0447 | -0.025681 | -0.25367 | 16.8789 |  |  | 10.6 |  |  | 16.8625 | 16.0511 | 15.2967 | 16.3578 | 15.6269 | 14.7953 | 49.7596 | 62.9087 | 36.8327 | 37.6296 | 20.2694 |  | 12.5611 | 21.2615 | 12.763 | 16.2134 | 13.4496 | 50.9811 |  | 18.9801 |  |  | 12.3127 | 13.1216 | 18.0734 | [6 empty] | 16.2952 |  |  | 15.3706 |  |  | 10.7087 | 14.6834 | 76.9743 | 8.0306 | 11.9966 | 45.446 | 8.5396 | 11.5463 | 50.9648 | 11.9393 | 35.915 | 8.4903 | 31.3943 | 9.167 | 32.0932 | 8.5579 | 13.3616 | 44.8642 | 12.1831 | 13.4454 | 62.9679 | 8.9435 | 12.1226 | 51.29 | 9.0544 | 31.3434 | 11.5214 | 31.0171 | 9.6127 | 31.985 | 0.26308 | 20.6014 | 0.24369 | 0.050107 | -37.752 | 3.1208 | 50.35 | 49.93 | -0.42747 | -0.38238 | 0.33104 | -0.24992 | -0.47455 | -0.70124 | 0.71335 | 0.16371 | 0.14282 | 0.30578 | -0.048828 | 0.38038 | 0.18181 | 0.25472
42810.4414 | 120 | 18.5906 | 18.6184 | 18.5891 | 18.5931 | 17.9127 | 16.5244 | 14.5829 | 16.6803 | 17.1788 | 17.2714 | 17.2876 | 16.8162 | 15.8539 | 14.4777 | 14.9967 | 14.9512 | 15.4889 | 13.3367 | 13.4603 | 14.0221 |  |  |  | 16.5705 | 15.8999 | 15.1302 | 54.3294 | 54.1655 | 71.1581 | 17.2885 | 16.3665 | 15.2118 | 16.8755 | 16.1376 | 15.2135 | 12.7643 | 63.1932 |  | 22.464 | 42.6709 | 47.4565 | 20.3013 |  | 6.4309 | 6.4566 | 5.9754 | 6.1018 | 6.1582 | 7.1058 | 18.4811 | 4.5087 | 6.4212 | 4.2907 | 6.7441 | 8.1514 | 42.1807 | 47.0539 | 42.8073 | 15.0403 |  |  | -0.24291 | -0.073509 | 0.084648 | -0.11171 | -0.080004 | -0.22979 | 0.48485 | 0.30737 | -0.25997 | -1.4132 | -0.261 | 8.8719 | 8.8731 | 2.0064 | 15.843 | 16.6849 | 17.2102 | 17.531 | 17.4969 | 16.4656 | 14.8048 | 16.823 | 17.1632 | 17.464 | 17.5064 | 17.2439 | 16.4318 | 14.6427 | 10.8999 | 8.7934 | 7.7701 | 7.5823 | 7.5124 | 7.8554 | 8.0277 | 15.9299 | 15.4964 | 15.3408 | 14.254 | 14.1563 | 14.1072 |  |  |  | 12.6489 | 61.9949 | 44.4349 | 17.4551 | -0.12698 | -0.078831 | 16.8927 |  |  | 10.5917 |  |  | 16.8621 | 16.0494 | 15.2933 | 16.3586 | 15.6162 | 14.7873 | 50.1311 | 63.2307 | 37.0566 | 37.8614 | 20.0683 |  | 12.593 | 20.7486 | 12.7984 | 16.1327 | 13.4841 | 51.0243 |  | 19.0702 |  |  | 12.3144 | 13.1492 | 18.0753 | [6 empty] | 16.3399 |  |  | 15.3848 |  |  | 10.7225 | 14.7275 | 77.0798 | 8.0299 | 12 | 45.7267 | 8.5482 | 11.5604 | 51.2211 | 11.9601 | 36.2056 | 8.4856 | 31.6464 | 9.1748 | 32.3243 | 8.5765 | 13.3844 | 45.0829 | 12.1993 | 13.4639 | 63.3126 | 8.9497 | 12.1497 | 51.5425 | 9.0576 | 31.4336 | 11.5185 | 31.56 | 9.6079 | 32.2507 | 0.051605 | 20.5918 | 0.24807 | 0.050961 | -37.7595 | 3.1208 | 44.64 | 49.04 | -0.63733 | -0.31594 | 0.33904 | -0.38948 | -0.32999 | -0.55926 | 0.81236 | 0.17035 | 0.15824 | 0.30916 | 0.01527 | 0.38304 | 0.16954 | 0.24478
42810.4414 | 121 | 18.588 | 18.6149 | 18.5919 | 18.5875 | 17.9074 | 16.5278 | 14.5862 | 16.6754 | 17.1771 | 17.2744 | 17.2873 | 16.8147 | 15.8448 | 14.477 | 15.0031 | 14.9419 | 15.4881 | 13.3398 | 13.4655 | 14.0202 |  |  |  | 16.5682 | 15.8963 | 15.1333 | 54.6998 | 54.3908 | 71.2817 | 17.2796 | 16.3659 | 15.2109 | 16.8728 | 16.1415 | 15.223 | 12.8103 | 63.2959 |  | 22.5906 | 42.9069 | 47.6749 | 20.2402 |  | 6.4269 | 6.4561 | 5.9804 | 6.104 | 6.1364 | 7.06 | 18.1506 | 4.5701 | 6.4197 | 4.3323 | 6.748 | 8.1654 | 42.1827 | 47.0564 | 42.8296 | 15.0434 |  |  | -0.20546 | -0.14645 | 0.093848 | -0.081482 | -0.18448 | -0.055 | 0.37117 | 0.40462 | -0.25725 | -0.26809 | -0.34664 | 8.8685 | 8.8696 | 2.0066 | 15.8421 | 16.6837 | 17.2025 | 17.5323 | 17.5007 | 16.4572 | 14.8117 | 16.815 | 17.1625 | 17.465 | 17.506 | 17.2414 | 16.4323 | 14.6372 | 10.7967 | 8.8035 | 7.7564 | 7.5223 | 7.4643 | 7.8642 | 8.0344 | 15.9266 | 15.4966 | 15.3341 | 14.2563 | 14.1537 | 14.116 |  |  |  | 12.6921 | 62.1075 | 44.9305 | 17.5566 | 0.024563 | -0.0043038 | 16.9626 |  |  | 10.6091 |  |  | 16.867 | 16.0555 | 15.3058 | 16.3522 | 15.6313 | 14.7921 | 50.522 | 63.5932 | 37.2607 | 38.0848 | 20.0727 |  | 12.6239 | 20.8123 | 12.8386 | 16.0153 | 13.5121 | 50.98 |  | 19.1593 |  |  | 12.3188 | 13.1585 | 18.0455 | [6 empty] | 16.2878 |  |  | 15.3991 |  |  | 10.735 | 14.7519 | 77.3163 | 8.0292 | 12.0198 | 45.9781 | 8.5482 | 11.5779 | 51.4837 | 11.9647 | 36.4885 | 8.4771 | 31.8409 | 9.1832 | 32.5509 | 8.5837 | 13.3767 | 45.2573 | 12.2002 | 13.4839 | 63.6034 | 8.9515 | 12.1672 | 51.8041 | 9.0573 | 31.5868 | 11.5254 | 31.8845 | 9.607 | 32.5003 | 0.13924 | 20.5841 | 0.25285 | 0.050975 | -37.7268 | 3.1208 | 34.47 | 49.57 | -0.58624 | -0.44595 | 0.35699 | -0.33264 | -0.50106 | -0.27358 | 0.71072 | 0.17125 | 0.1578 | 0.31335 | 0.027747 | 0.38532 | 0.17276 | 0.24339
42810.4414 | 122 | 18.5893 | 18.6199 | 18.5947 | 18.596 | 17.909 | 16.5273 | 14.5818 | 16.6799 | 17.1814 | 17.2791 | 17.2922 | 16.8177 | 15.8498 | 14.4787 | 15.0035 | 14.9416 | 15.4866 | 13.3364 | 13.4614 | 14.0195 |  |  |  | 16.5701 | 15.889 | 15.1481 | 54.99 | 54.6108 | 71.5659 | 17.2857 | 16.3675 | 15.2183 | 16.8774 | 16.1441 | 15.2282 | 12.8558 | 64.059 |  | 22.7214 | 43.1565 | 47.8728 | 20.2379 |  | 6.4321 | 6.4628 | 5.9798 | 6.1039 | 6.1366 | 7.0343 | 18.0383 | 4.6724 | 6.4206 | 4.3628 | 6.7446 | 8.1537 | 42.189 | 47.0496 | 42.8256 | 15.0358 |  |  | -0.13318 | -0.12148 | 0.042592 | -0.32461 | -0.023492 | -0.097712 | 0.18849 | 0.4033 | -0.081133 | -0.40005 | -0.15609 | 8.8686 | 8.8697 | 2.0058 | 15.8454 | 16.694 | 17.2156 | 17.5358 | 17.4997 | 16.4551 | 14.8132 | 16.8263 | 17.1697 | 17.4737 | 17.5092 | 17.2425 | 16.4268 | 14.6377 | 10.3277 | 8.7913 | 7.7617 | 7.4082 | 7.4742 | 7.8724 | 8.0268 | 15.9261 | 15.4967 | 15.338 | 14.2606 | 14.1641 | 14.1123 |  |  |  | 12.7325 | 62.3697 | 45.49 | 17.3789 | -0.056882 | -0.1383 | 17.0929 |  |  | 10.5991 |  |  | 16.855 | 16.0488 | 15.3215 | 16.3539 | 15.6306 | 14.794 | 50.8673 | 63.9509 | 37.4563 | 38.3006 | 20.4048 |  | 12.6782 | 22.1064 | 12.9187 | 15.9792 | 13.553 | 51.417 |  | 19.2716 |  |  | 12.3219 | 13.1544 | 18.1322 | [6 empty] | 16.2612 |  |  | 15.4356 |  |  | 10.7371 | 14.784 | 77.5332 | 8.0343 | 12.1004 | 46.2174 | 8.5491 | 11.5918 | 51.6851 | 11.9886 | 36.7567 | 8.474 | 32.0402 | 9.1921 | 32.7723 | 8.5982 | 13.395 | 45.4524 | 12.2196 | 13.5179 | 63.8632 | 8.9637 | 12.2205 | 52.113 | 9.0742 | 31.8236 | 11.5536 | 32.0689 | 9.6181 | 32.7437 | 0.19317 | 20.5751 | 0.25848 | 0.052177 | -37.5958 | 3.1208 | 42.77 | 49.83 | -0.47219 | -0.40616 | 0.2405 | -0.66394 | -0.17879 | -0.36464 | 0.50645 | 0.16382 | 0.12451 | 0.31571 | 0.080816 | 0.38386 | 0.17433 | 0.24967
42810.4415 | 123 | 18.5896 | 18.6264 | 18.5939 | 18.6004 | 17.911 | 16.5261 | 14.5757 | 16.6796 | 17.1802 | 17.2772 | 17.2891 | 16.8184 | 15.8622 | 14.4741 | 14.9964 | 14.9452 | 15.4864 | 13.3343 | 13.4554 | 14.0203 |  |  |  | 16.56 | 15.8892 | 15.1506 | 55.206 | 54.9073 | 71.6524 | 17.287 | 16.3679 | 15.2215 | 16.8798 | 16.1437 | 15.233 | 12.896 | 64.4002 |  | 22.8301 | 43.4222 | 48.0893 | 20.1926 |  | 6.4243 | 6.4578 | 5.9786 | 6.1003 | 6.1401 | 7.0114 | 18.2808 | 4.8126 | 6.4249 | 4.5266 | 6.7463 | 8.1575 | 42.2102 | 47.0546 | 42.8214 | 15.0271 |  |  | -0.17457 | -0.29758 | 0.097132 | 0.078854 | -0.018236 | 0.052768 | 0.031444 | 0.40133 | -1.5842 | -0.26935 | -0.23279 | 8.8683 | 8.8694 | 2.0057 | 15.853 | 16.6926 | 17.2192 | 17.5392 | 17.4944 | 16.4617 | 14.8165 | 16.8265 | 17.1675 | 17.4709 | 17.5174 | 17.2462 | 16.4385 | 14.649 | 10.0856 | 8.7378 | 7.5244 | 7.3657 | 7.4916 | 7.874 | 8.0288 | 15.9203 | 15.5021 | 15.3369 | 14.2505 | 14.1592 | 14.1106 |  |  |  | 12.7553 | 62.6462 | 45.9075 | 17.0277 | 0.0051138 | -0.15693 | 17.2113 |  |  | 10.6051 |  |  | 16.8606 | 16.0461 | 15.3288 | 16.3566 | 15.6271 | 14.7891 | 51.1063 | 64.4469 | 37.6707 | 38.4746 | 20.9984 |  | 12.7134 | 24.7126 | 12.9968 | 16.0117 | 13.5947 | 51.4673 |  | 19.3903 |  |  | 12.3091 | 13.1477 | 18.2701 | [6 empty] | 16.3322 |  |  | 15.4566 |  |  | 10.7465 | 14.8295 | 77.6307 | 8.0484 | 12.1683 | 46.4428 | 8.54 | 11.5998 | 51.796 | 12.0057 | 37.0473 | 8.4692 | 32.2302 | 9.1834 | 33.0074 | 8.6142 | 13.4258 | 45.6469 | 12.2389 | 13.5544 | 64.1549 | 8.9747 | 12.2808 | 52.4128 | 9.0902 | 32.1087 | 11.5782 | 32.3315 | 9.6262 | 32.9747 | 0.24844 | 20.5671 | 0.26196 | 0.051077 | -37.6329 | 3.1209 | 44.59 | 49.31 | -0.54068 | -0.63569 | 0.36318 | 0.32723 | -0.15752 | 0.26795 | 0.20684 | 0.1485 | 0.054696 | 0.31618 | 0.1079 | 0.41046 | 0.17691 | 0.26017
42810.4415 | 124 | 18.5839 | 18.6106 | 18.5857 | 18.5927 | 17.9001 | 16.517 | 14.5695 | 16.6768 | 17.1696 | 17.2713 | 17.2754 | 16.8105 | 15.8458 | 14.4586 | 14.9964 | 14.9461 | 15.4892 | 13.3398 | 13.4587 | 14.0198 |  |  |  | 16.562 | 15.8941 | 15.1482 | 55.3833 | 55.2042 | 71.465 | 17.2913 | 16.3566 | 15.2196 | 16.871 | 16.1413 | 15.2362 | 12.9247 | 64.5234 |  | 22.9418 | 43.6695 | 48.3046 | 19.9743 |  | 6.4278 | 6.4723 | 5.9789 | 6.0979 | 6.1365 | 7.0115 | 18.2147 | 4.851 | 6.4305 | 4.6574 | 6.7553 | 8.1588 | 42.2201 | 47.0186 | 42.8122 | 15.0123 |  |  | -0.095061 | -0.040653 | 0.40532 | -0.20831 | 0.43649 | 0.024512 | -0.13612 | 0.62081 | -0.87277 | -1.0047 | -0.15032 | 8.8691 | 8.8705 | 2.0051 | 15.8537 | 16.6912 | 17.2133 | 17.5331 | 17.4977 | 16.4635 | 14.8224 | 16.8262 | 17.1796 | 17.4717 | 17.5167 | 17.2449 | 16.4293 | 14.6476 | 11.0725 | 9.0829 | 7.5116 | 7.2459 | 7.4113 | 7.9085 | 8.032 | 15.9353 | 15.5045 | 15.337 | 14.2619 | 14.1568 | 14.1151 |  |  |  | 12.7907 | 62.939 | 46.1069 | 16.8572 | 0.025171 | -0.17989 | 17.3648 |  |  | 10.5993 |  |  | 16.8641 | 16.0496 | 15.3475 | 16.3576 | 15.628 | 14.797 | 51.3401 | 64.7689 | 37.8845 | 38.6304 | 21.8242 |  | 12.7633 | 26.8242 | 13.0686 | 16.2326 | 13.6294 | 52.048 |  | 19.507 |  |  | 12.2853 | 13.1286 | 18.4451 | [6 empty] | 16.4666 |  |  | 15.4781 |  |  | 10.7623 | 14.8912 | 77.7528 | 8.0684 | 12.2005 | 46.6435 | 8.5414 | 11.6184 | 51.9365 | 12.0235 | 37.4719 | 8.4784 | 32.4425 | 9.1943 | 33.2459 | 8.6204 | 13.447 | 45.8402 | 12.2513 | 13.5834 | 64.3882 | 8.9801 | 12.2915 | 52.6487 | 9.105 | 32.35 | 11.6076 | 32.5683 | 9.6363 | 33.1513 | 0.28792 | 20.5583 | 0.2677 | 0.051562 | -37.6467 | 3.1209 | 57.5 | 49.88 | -0.39887 | -0.23496 | 0.74191 | -0.53187 | 0.77065 | 0.18263 | -0.43036 | 0.1272 | -0.0015825 | 0.3112 | 0.0022564 | 0.41225 | 0.18393 | 0.26608
42810.4415 | 125 | 18.5934 | 18.6176 | 18.5906 | 18.5943 | 17.9093 | 16.5252 | 14.576 | 16.6877 | 17.1862 | 17.2784 | 17.2875 | 16.8154 | 15.8571 | 14.4729 | 15.0029 | 14.95 | 15.491 | 13.3442 | 13.4648 | 14.0172 |  |  |  | 16.5682 | 15.8928 | 15.158 | 55.6795 | 55.4183 | 71.7221 | 17.2949 | 16.3597 | 15.2206 | 16.8689 | 16.1458 | 15.2361 | 12.9561 | 64.0302 |  | 23.0477 | 43.9047 | 48.513 | 19.4379 |  | 6.4159 | 6.4655 | 5.9659 | 6.0928 | 6.1278 | 6.9718 | 18.0217 | 4.7739 | 6.4224 | 4.7693 | 6.7563 | 8.1597 | 42.2377 | 47.001 | 42.8179 | 15.0054 |  |  | -0.21663 | -0.079425 | -0.03692 | -0.48429 | 0.36158 | -0.56886 | 0.22201 | 0.6333 | -0.25277 | -1.3918 | -0.12151 | 8.8674 | 8.8684 | 2.0047 | 15.8536 | 16.6958 | 17.2211 | 17.5389 | 17.5035 | 16.4674 | 14.8216 | 16.8287 | 17.171 | 17.4699 | 17.5173 | 17.2439 | 16.4344 | 14.6449 | 11.6301 | 9.6569 | 8.6917 | 7.2468 | 7.3115 | 7.94 | 8.0539 | 15.9405 | 15.4999 | 15.3401 | 14.2622 | 14.1603 | 14.1207 |  |  |  | 12.8309 | 63.1779 | 46.154 | 17.1905 | -0.11705 | -0.20831 | 17.5059 |  |  | 10.5971 |  |  | 16.8652 | 16.0516 | 15.3451 | 16.3496 | 15.622 | 14.8014 | 51.6234 | 64.9565 | 38.1224 | 38.8583 | 22.407 |  | 12.8045 | 28.0871 | 13.1435 | 16.5027 | 13.6692 | 52.6274 |  | 19.6154 |  |  | 12.2804 | 13.136 | 18.5591 | [6 empty] | 16.6272 |  |  | 15.4958 |  |  | 10.7795 | 14.9443 | 77.9468 | 8.0868 | 12.221 | 46.8202 | 8.5457 | 11.6399 | 52.0668 | 12.047 | 37.8686 | 8.4885 | 32.6225 | 9.2074 | 33.4972 | 8.6301 | 13.447 | 46.0807 | 12.2697 | 13.6198 | 64.51 | 8.9795 | 12.2929 | 52.8601 | 9.1144 | 32.5479 | 11.6121 | 32.7487 | 9.6383 | 33.3969 | 0.19317 | 20.5561 | 0.27278 | 0.051663 | -37.6779 | 3.1208 | 35.34 | 49.14 | -0.60236 | -0.32842 | -0.22391 | -0.81097 | 0.70136 | -0.87972 | 0.54957 | 0.11238 | -0.034183 | 0.30501 | -0.05605 | 0.28368 | 0.19987 | 0.25816
42810.4415 | 126 | 18.5999 | 18.625 | 18.5893 | 18.6049 | 17.9123 | 16.5265 | 14.5825 | 16.692 | 17.1831 | 17.2867 | 17.2914 | 16.8341 | 15.8605 | 14.4784 | 15.001 | 14.9501 | 15.4923 | 13.3341 | 13.4615 | 14.0266 |  |  |  | 16.566 | 15.8921 | 15.1664 | 56.0236 | 55.5946 | 72.1484 | 17.2853 | 16.3636 | 15.2231 | 16.8795 | 16.1434 | 15.239 | 12.9781 | 64.0203 |  | 23.1346 | 44.1427 | 48.6807 | 18.859 |  | 6.425 | 6.4659 | 5.9631 | 6.096 | 6.1335 | 6.9485 | 17.876 | 4.6661 | 6.4249 | 4.777 | 6.7548 | 8.1692 | 42.2556 | 46.9967 | 42.8252 | 15.0064 |  |  | -0.20874 | -0.15039 | -0.22354 | -0.64529 | 0.29652 | -0.3277 | 0.25355 | 0.76735 | -0.50166 | -0.56936 | -0.1994 | 8.8726 | 8.8738 | 2.0055 | 15.8566 | 16.7016 | 17.2196 | 17.5407 | 17.5029 | 16.4705 | 14.8163 | 16.8285 | 17.1747 | 17.4692 | 17.5186 | 17.24 | 16.4327 | 14.6406 | 11.299 | 9.459 | 9.6532 | 8.0685 | 7.2712 | 7.9458 | 8.0666 | 15.934 | 15.5046 | 15.3405 | 14.2654 | 14.1678 | 14.124 |  |  |  | 12.8765 | 63.3355 | 46.282 | 17.8902 | -0.075724 | -0.21208 | 17.6144 |  |  | 10.59 |  |  | 16.8714 | 16.0453 | 15.3631 | 16.3535 | 15.631 | 14.8025 | 51.9643 | 65.3062 | 38.3835 | 39.0903 | 22.6323 |  | 12.8627 | 27.699 | 13.216 | 16.5287 | 13.7109 | 53.1527 |  | 19.7086 |  |  | 12.2936 | 13.1589 | 18.6573 | [6 empty] | 16.7264 |  |  | 15.5025 |  |  | 10.799 | 14.9915 | 77.9523 | 8.114 | 12.3499 | 47.0346 | 8.5676 | 11.6775 | 52.1713 | 12.0725 | 38.0711 | 8.4996 | 32.7721 | 9.2237 | 33.7355 | 8.6445 | 13.4419 | 46.339 | 12.2763 | 13.6608 | 64.6012 | 8.9901 | 12.3183 | 53.0632 | 9.1273 | 32.6901 | 11.6218 | 33.0043 | 9.6472 | 33.7593 | 0.2078 | 20.5474 | 0.27523 | 0.049014 | -37.6585 | 3.1208 | 32.21 | 49.09 | -0.59166 | -0.45192 | -0.55097 | -0.9361 | 0.63511 | -0.66767 | 0.58729 | 0.10804 | -0.021005 | 0.30567 | -0.018582 | 0.17831 | 0.21668 | 0.24023
42810.4415 | 127 | 18.6041 | 18.6231 | 18.5863 | 18.5938 | 17.9099 | 16.5242 | 14.5737 | 16.679 | 17.1785 | 17.2748 | 17.2823 | 16.8205 | 15.8585 | 14.4769 | 15.0096 | 14.9585 | 15.4934 | 13.3399 | 13.461 | 14.0249 |  |  |  | 16.5692 | 15.8903 | 15.1717 | 56.2448 | 55.7999 | 72.0458 | 17.2795 | 16.3731 | 15.2287 | 16.87 | 16.1444 | 15.2396 | 13.0116 | 64.4185 |  | 23.2312 | 44.3696 | 48.9038 | 18.4319 |  | 6.4311 | 6.4628 | 5.945 | 6.0724 | 6.1215 | 6.9239 | 17.8363 | 4.6911 | 6.4104 | 4.6809 | 6.7482 | 8.1653 | 42.2546 | 46.9891 | 42.8244 | 14.985 |  |  | -0.19626 | -0.37578 | -0.22288 | -0.58155 | -0.16017 | -0.30076 | 0.33897 | 0.71215 | -0.83171 | -0.76363 | -0.41797 | 8.872 | 8.8728 | 2.0065 | 15.8524 | 16.6909 | 17.2086 | 17.5393 | 17.4967 | 16.4647 | 14.8062 | 16.831 | 17.172 | 17.4618 | 17.5134 | 17.2428 | 16.4255 | 14.6418 | 10.8424 | 9.2031 | 9.2352 | 8.5621 | 8.0216 | 7.9626 | 8.075 | 15.9332 | 15.4973 | 15.3391 | 14.2654 | 14.1656 | 14.1263 |  |  |  | 12.9124 | 63.5608 | 46.4374 | 18.5336 | -0.12374 | -0.16126 | 17.6574 |  |  | 10.5896 |  |  | 16.8627 | 16.0496 | 15.3706 | 16.357 | 15.627 | 14.7996 | 52.2616 | 65.6648 | 38.6837 | 39.4159 | 22.7397 |  | 12.913 | 28.0188 | 13.2677 | 16.5114 | 13.7519 | 53.1898 |  | 19.8105 |  |  | 12.2841 | 13.1667 | 18.8156 | [6 empty] | 16.6934 |  |  | 15.5272 |  |  | 10.8 | 15.0326 | 78.0139 | 8.1213 | 12.4864 | 47.2879 | 8.5677 | 11.6935 | 52.3421 | 12.0971 | 38.2901 | 8.5016 | 32.9753 | 9.2323 | 33.9134 | 8.6544 | 13.4518 | 46.5842 | 12.2875 | 13.6799 | 64.8319 | 8.9988 | 12.3457 | 53.346 | 9.1432 | 32.8169 | 11.6456 | 33.2453 | 9.6522 | 33.9711 | 0.35707 | 20.5354 | 0.28025 | 0.050896 | -37.6546 | 3.1209 | 35.52 | 50.22 | -0.5736 | -0.71435 | -0.55015 | -0.88866 | -0.46676 | -0.63961 | 0.67902 | 0.10673 | -0.028177 | 0.30751 | 0.034106 | 0.22573 | 0.22965 | 0.22354
42810.4415 | 128 | 18.593 | 18.6177 | 18.5874 | 18.5982 | 17.9008 | 16.5139 | 14.5753 | 16.6801 | 17.1792 | 17.2672 | 17.2829 | 16.82 | 15.8511 | 14.4731 | 15.0109 | 14.9537 | 15.4835 | 13.3401 | 13.4611 | 14.0155 |  |  |  | 16.5755 | 15.8882 | 15.1679 | 56.4296 | 55.9997 | 72.0554 | 17.2796 | 16.3629 | 15.2333 | 16.8735 | 16.1353 | 15.2387 | 13.0408 | 65.0126 |  | 23.3334 | 44.5119 | 49.1037 | 18.6696 |  | 6.4372 | 6.4635 | 5.9327 | 6.0578 | 6.1106 | 6.9006 | 17.6506 | 4.77 | 6.4227 | 4.5892 | 6.7473 | 8.1675 | 42.2733 | 46.9915 | 42.8435 | 14.9753 |  |  | -0.29942 | -0.14579 | -0.021148 | -0.13011 | -0.14703 | -0.21336 | 0.32583 | 0.4263 | -0.19964 | -0.11661 | -0.22822 | 8.8693 | 8.8702 | 2.0055 | 15.8478 | 16.6974 | 17.2173 | 17.5392 | 17.4933 | 16.4688 | 14.8084 | 16.8367 | 17.179 | 17.4698 | 17.5206 | 17.2405 | 16.4294 | 14.6426 | 10.4485 | 9.0542 | 8.6957 | 8.4887 | 8.2678 | 7.9683 | 8.0889 | 15.9342 | 15.506 | 15.3386 | 14.2722 | 14.1675 | 14.1234 |  |  |  | 12.9643 | 63.8903 | 46.7769 | 18.646 | -0.11908 | -0.14884 | 17.7114 |  |  | 10.6046 |  |  | 16.8561 | 16.0467 | 15.3747 | 16.3419 | 15.6261 | 14.8049 | 52.5822 | 65.9213 | 38.919 | 39.6831 | 22.8114 |  | 12.9466 | 28.2969 | 13.3238 | 16.5205 | 13.7786 | 52.7704 |  | 19.92 |  |  | 12.2851 | 13.1809 | 19.0427 | [6 empty] | 16.5981 |  |  | 15.5411 |  |  | 10.8067 | 15.071 | 78.2825 | 8.1386 | 12.5579 | 47.5628 | 8.5664 | 11.7075 | 52.6065 | 12.1173 | 38.5613 | 8.5143 | 33.1751 | 9.2254 | 34.0942 | 8.6457 | 13.4563 | 46.859 | 12.3041 | 13.7029 | 65.0197 | 9.0062 | 12.3814 | 53.642 | 9.1423 | 32.9707 | 11.6733 | 33.3643 | 9.6521 | 34.173 | 0.10495 | 20.5246 | 0.28447 | 0.052343 | -37.7724 | 3.1208 | 40.34 | 49.31 | -0.70852 | -0.44495 | -0.16947 | -0.42034 | -0.44718 | -0.5387 | 0.66571 | 0.10585 | -0.034044 | 0.30814 | 0.078532 | 0.2873 | 0.22401 | 0.22214
42810.4415 | 129 | 18.6009 | 18.62 | 18.5923 | 18.5984 | 17.9115 | 16.523 | 14.5828 | 16.6866 | 17.1837 | 17.2808 | 17.2916 | 16.8211 | 15.8534 | 14.4744 | 15.0022 | 14.9671 | 15.4977 | 13.3555 | 13.4616 | 14.0305 |  |  |  | 16.5737 | 15.9048 | 15.1749 | 56.7319 | 56.15 | 72.0448 | 17.2909 | 16.3689 | 15.2361 | 16.8757 | 16.1424 | 15.253 | 13.0964 | 65.2669 |  | 23.4474 | 44.6541 | 49.3424 | 19.9799 |  | 6.4468 | 6.4682 | 5.9227 | 6.0538 | 6.1041 | 6.8975 | 17.8394 | 4.8366 | 6.4316 | 4.6113 | 6.7557 | 8.1697 | 42.3046 | 46.9973 | 42.8653 | 14.9725 |  |  | -0.3428 | 0.011915 | -0.014576 | -0.2635 | -0.18186 | -0.13057 | 0.43886 | 0.27582 | 0.59977 | -0.18018 | -0.16721 | 8.8695 | 8.8706 | 2.0046 | 15.8399 | 16.6852 | 17.2072 | 17.5288 | 17.4849 | 16.4535 | 14.8035 | 16.8195 | 17.158 | 17.4546 | 17.5063 | 17.2351 | 16.42 | 14.626 | 10.3323 | 8.9875 | 8.3373 | 8.1754 | 8.3337 | 7.9788 | 8.0838 | 15.93 | 15.5093 | 15.3477 | 14.265 | 14.1768 | 14.1278 |  |  |  | 13.0023 | 64.2206 | 46.8872 | 18.4011 | -0.084435 | -0.28962 | 17.7149 |  |  | 10.6041 |  |  | 16.8612 | 16.0477 | 15.379 | 16.3421 | 15.6186 | 14.8015 | 52.8394 | 66.1162 | 39.1424 | 39.9349 | 22.8994 |  | 12.9875 | 27.5095 | 13.3608 | 16.7467 | 13.8225 | 52.474 |  | 20.0472 |  |  | 12.3031 | 13.1991 | 19.1681 | [6 empty] | 16.643 |  |  | 15.5647 |  |  | 10.804 | 15.1034 | 78.4243 | 8.1569 | 12.5626 | 47.7621 | 8.5665 | 11.735 | 52.855 | 12.1269 | 38.8197 | 8.5231 | 33.4156 | 9.2238 | 34.2617 | 8.6252 | 13.4493 | 47.1175 | 12.2984 | 13.7151 | 65.1761 | 8.9989 | 12.3936 | 53.8545 | 9.118 | 33.1405 | 11.6719 | 33.5769 | 9.6633 | 34.34 | 0.23823 | 20.5182 | 0.28708 | 0.050418 | -37.6559 | 3.1209 | 39.21 | 48.89 | -0.75808 | 0.1272 | -0.14069 | -0.59819 | -0.49733 | -0.42141 | 0.77258 | 0.10476 | -0.010944 | 0.30331 | 0.092664 | 0.32652 | 0.18946 | 0.2302
42810.4415 | 130 | 18.6049 | 18.6276 | 18.5992 | 18.602 | 17.9151 | 16.5276 | 14.5878 | 16.6872 | 17.1843 | 17.2795 | 17.2955 | 16.826 | 15.8554 | 14.4736 | 15.005 | 14.9512 | 15.4936 | 13.3425 | 13.4655 | 14.03 |  |  |  | 16.5725 | 15.8956 | 15.1864 | 56.9906 | 56.3602 | 72.4522 | 17.29 | 16.3647 | 15.2382 | 16.8715 | 16.1365 | 15.2519 | 13.1479 | 65.2719 |  | 23.5667 | 44.8417 | 49.5768 | 20.8689 |  | 6.4298 | 6.448 | 5.9104 | 6.0337 | 6.0804 | 6.8668 | 17.9652 | 4.8366 | 6.422 | 4.6459 | 6.7466 | 8.1674 | 42.3137 | 47.0118 | 42.872 | 14.9571 |  |  | -0.3106 | -0.053137 | -0.20908 | -0.18333 | 0.19401 | 0.088908 | 0.4198 | 0.24626 | -0.22845 | -0.56873 | -0.10045 | 8.8714 | 8.8728 | 2.0053 | 15.8374 | 16.6806 | 17.2062 | 17.521 | 17.4754 | 16.4535 | 14.8012 | 16.8067 | 17.1582 | 17.451 | 17.4923 | 17.2304 | 16.4194 | 14.6223 | 10.6315 | 8.9788 | 8.1096 | 7.8626 | 8.4171 | 7.9994 | 8.0889 | 15.9313 | 15.5055 | 15.3448 | 14.2698 | 14.1725 | 14.1241 |  |  |  | 13.0432 | 64.5214 | 46.9928 | 18.3074 | 0.041784 | -0.27832 | 17.6752 |  |  | 10.6082 |  |  | 16.8684 | 16.0542 | 15.3961 | 16.347 | 15.6224 | 14.8136 | 53.3071 | 66.3709 | 39.4057 | 40.2064 | 22.6478 |  | 13.036 | 26.2569 | 13.3914 | 17.3932 | 13.8682 | 52.8509 |  | 20.1497 |  |  | 12.3118 | 13.192 | 19.0289 | [6 empty] | 16.7673 |  |  | 15.5769 |  |  | 10.8234 | 15.1355 | 78.7841 | 8.1823 | 12.5719 | 48.019 | 8.5895 | 11.7671 | 53.0722 | 12.1608 | 39.1441 | 8.5385 | 33.6699 | 9.2356 | 34.4585 | 8.5988 | 13.4504 | 47.3552 | 12.3217 | 13.7459 | 65.5229 | 9.0073 | 12.4152 | 54.0201 | 9.1081 | 33.3969 | 11.6783 | 33.9278 | 9.6603 | 34.5049 | 0.27714 | 20.5086 | 0.29211 | 0.051287 | -37.6228 | 3.1209 | 33.4 | 50.07 | -0.72203 | -0.26862 | -0.53284 | -0.49895 | 0.51366 | 0.34772 | 0.75558 | 0.11335 | 0.024864 | 0.28687 | 0.061818 | 0.35242 | 0.16647 | 0.23415
42810.4416 | 131 | 18.6013 | 18.6223 | 18.5924 | 18.5958 | 17.9133 | 16.5252 | 14.5788 | 16.6855 | 17.1775 | 17.2715 | 17.2887 | 16.8218 | 15.8525 | 14.4697 | 15.0053 | 14.9502 | 15.5091 | 13.3539 | 13.4644 | 14.031 |  |  |  | 16.5708 | 15.9 | 15.1947 | 57.3406 | 56.5615 | 73.1603 | 17.2884 | 16.3644 | 15.2361 | 16.8701 | 16.1308 | 15.2547 | 13.1867 | 65.213 |  | 23.6767 | 45.0414 | 49.7593 | 20.8652 |  | 6.4269 | 6.4464 | 5.9047 | 6.0201 | 6.0682 | 6.854 | 18.2147 | 4.8377 | 6.4101 | 4.6934 | 6.7435 | 8.1688 | 42.3227 | 47.03 | 42.8817 | 14.9464 |  |  | -0.12595 | 0.092743 | -0.049404 | -0.049282 | 0.22753 | 0.3649 | 0.48025 | 0.43419 | -0.20918 | -0.047587 | -0.21908 | 8.8718 | 8.8728 | 2.006 | 15.8421 | 16.6902 | 17.2123 | 17.5282 | 17.4906 | 16.4541 | 14.8015 | 16.8187 | 17.1684 | 17.4561 | 17.5014 | 17.2349 | 16.4165 | 14.6287 | 11.5749 | 9.077 | 7.7575 | 7.7252 | 8.2255 | 8.0322 | 8.0856 | 15.9403 | 15.5064 | 15.3436 | 14.2676 | 14.1707 | 14.1306 |  |  |  | 13.0786 | 64.8818 | 47.1192 | 18.4036 | 0.075213 | -0.14018 | 17.6171 |  |  | 10.6086 |  |  | 16.866 | 16.0522 | 15.4067 | 16.3425 | 15.6176 | 14.8107 | 53.5013 | 66.6542 | 39.6229 | 40.456 | 22.4435 |  | 13.0687 | 25.4619 | 13.4315 | 17.9378 | 13.9147 | 52.838 |  | 20.2503 |  |  | 12.3202 | 13.2134 | 18.9099 | [6 empty] | 16.8438 |  |  | 15.5942 |  |  | 10.828 | 15.1757 | 78.9434 | 8.1574 | 12.5413 | 48.28 | 8.597 | 11.7997 | 53.2396 | 12.1762 | 39.347 | 8.5252 | 33.9162 | 9.2371 | 34.6581 | 8.5945 | 13.4786 | 47.6249 | 12.3377 | 13.7706 | 65.7652 | 9.0281 | 12.452 | 54.1286 | 9.1198 | 33.6984 | 11.6692 | 34.2619 | 9.666 | 34.7419 | 0.087813 | 20.5013 | 0.2965 | 0.052162 | -37.6564 | 3.1209 | 35.67 | 48.88 | -0.46025 | 0.35487 | -0.25901 | -0.25869 | 0.55625 | 0.70442 | 0.80813 | 0.12011 | 0.048271 | 0.27328 | -0.039203 | 0.39115 | 0.16785 | 0.23266
42810.4416 | 132 | 18.5983 | 18.6194 | 18.5927 | 18.5902 | 17.9046 | 16.5126 | 14.5745 | 16.6798 | 17.1801 | 17.2715 | 17.2769 | 16.8202 | 15.8512 | 14.4611 | 15.0086 | 14.9422 | 15.4925 | 13.3393 | 13.4649 | 14.0299 |  |  |  | 16.5778 | 15.8931 | 15.1948 | 57.5882 | 56.8532 | 73.0921 | 17.2938 | 16.3678 | 15.2394 | 16.8723 | 16.1361 | 15.2547 | 13.2246 | 64.7331 |  | 23.7876 | 45.21 | 49.9574 | 20.6395 |  | 6.4293 | 6.4516 | 5.9009 | 6.0178 | 6.0693 | 6.8525 | 18.7104 | 4.8755 | 6.4116 | 4.6609 | 6.7603 | 8.1657 | 42.3455 | 47.0439 | 42.9048 | 14.936 |  |  | -0.2968 | -0.37775 | 0.079392 | 0.026286 | 0.15393 | -0.21402 | 0.27458 | 0.68389 | -0.9329 | -0.37928 | -0.36035 | 8.8689 | 8.8701 | 2.0067 | 15.842 | 16.6905 | 17.2153 | 17.5344 | 17.4907 | 16.4593 | 14.8079 | 16.8163 | 17.1652 | 17.4577 | 17.5021 | 17.2395 | 16.4256 | 14.6292 | 12.5165 | 9.0685 | 7.5267 | 7.5732 | 8.0142 | 8.0605 | 8.086 | 15.932 | 15.5102 | 15.3503 | 14.2732 | 14.1746 | 14.1258 |  |  |  | 13.1242 | 65.2351 | 47.354 | 18.558 | 0.17266 | -0.11911 | 17.7137 |  |  | 10.6133 |  |  | 16.8685 | 16.0571 | 15.4168 | 16.3478 | 15.6177 | 14.8152 | 53.6043 | 66.9026 | 39.8375 | 40.6912 | 22.29 |  | 13.1289 | 25.0354 | 13.4767 | 18.2941 | 13.956 | 53.4419 |  | 20.3769 |  |  | 12.3477 | 13.2193 | 18.8977 | [6 empty] | 16.9122 |  |  | 15.614 |  |  | 10.8367 | 15.2197 | 79.1753 | 8.124 | 12.5702 | 48.5006 | 8.5948 | 11.8202 | 53.3883 | 12.1936 | 39.5955 | 8.4896 | 34.2118 | 9.2421 | 34.8047 | 8.6003 | 13.536 | 47.8279 | 12.3539 | 13.8182 | 66.0627 | 9.0255 | 12.5174 | 54.3275 | 9.161 | 33.9895 | 11.693 | 34.4407 | 9.6841 | 34.9872 | 0.18238 | 20.4923 | 0.29907 | 0.050766 | -37.6002 | 3.1209 | 55.29 | 48.69 | -0.70646 | -0.71621 | 0.32834 | 0.18893 | 0.45752 | -0.53948 | 0.61105 | 0.12636 | 0.061616 | 0.26475 | -0.14053 | 0.41686 | 0.17538 | 0.22988
42810.4416 | 133 | 18.6032 | 18.6267 | 18.5921 | 18.594 | 17.9089 | 16.5203 | 14.5787 | 16.6821 | 17.1758 | 17.2723 | 17.2857 | 16.8164 | 15.8497 | 14.4715 | 15.0102 | 14.957 | 15.4991 | 13.3482 | 13.4657 | 14.0369 |  |  |  | 16.5786 | 15.8909 | 15.2047 | 57.7595 | 57.229 | 72.8321 | 17.3002 | 16.3717 | 15.2429 | 16.8761 | 16.1365 | 15.2671 | 13.2641 | 64.5655 |  | 23.9135 | 45.4233 | 50.1885 | 20.3556 |  | 6.4238 | 6.4451 | 5.8987 | 6.0137 | 6.0646 | 6.8241 | 18.8649 | 4.8653 | 6.4118 | 4.5458 | 6.7613 | 8.1719 | 42.3801 | 47.0748 | 42.928 | 14.9264 |  |  | -0.29154 | -0.27393 | 0.060992 | -0.04337 | 0.01462 | -0.54258 | 0.14118 | 0.48413 | 0.55229 | -0.1485 | -0.27531 | 8.8704 | 8.8714 | 2.006 | 15.852 | 16.6962 | 17.2217 | 17.5341 | 17.4972 | 16.4587 | 14.8055 | 16.8203 | 17.1692 | 17.4653 | 17.507 | 17.2431 | 16.4217 | 14.6345 | 13.4482 | 9.3206 | 7.6302 | 7.3113 | 7.8668 | 8.1053 | 8.0898 | 15.9308 | 15.5024 | 15.3394 | 14.2605 | 14.1688 | 14.1231 |  |  |  | 13.1614 | 65.5072 | 47.6905 | 18.8068 | 0.056574 | -0.32933 | 17.7691 |  |  | 10.6158 |  |  | 16.8636 | 16.0459 | 15.4331 | 16.3414 | 15.6178 | 14.8159 | 53.8107 | 67.1443 | 40.0708 | 40.951 | 21.9767 |  | 13.1668 | 24.1461 | 13.5069 | 18.2079 | 13.9914 | 53.6179 |  | 20.485 |  |  | 12.3765 | 13.2273 | 18.9373 | [6 empty] | 16.9479 |  |  | 15.638 |  |  | 10.8428 | 15.2569 | 79.0323 | 8.1173 | 12.6713 | 48.6758 | 8.6029 | 11.8337 | 53.5552 | 12.223 | 39.8486 | 8.4725 | 34.489 | 9.2502 | 34.9749 | 8.6039 | 13.5896 | 48.0568 | 12.3746 | 13.8389 | 66.2156 | 9.0379 | 12.5683 | 54.5831 | 9.211 | 34.2652 | 11.7031 | 34.5835 | 9.7002 | 35.2196 | 0.26944 | 20.4853 | 0.30301 | 0.05188 | -37.688 | 3.1209 | 41.65 | 50.04 | -0.69991 | -0.60989 | 0.28779 | -0.24268 | 0.14099 | -0.85893 | 0.43814 | 0.13632 | 0.087322 | 0.26832 | -0.23885 | 0.4058 | 0.18457 | 0.22419
42810.4416 | 134 | 18.6105 | 18.6269 | 18.5877 | 18.6021 | 17.9147 | 16.5235 | 14.5738 | 16.6776 | 17.179 | 17.2742 | 17.2883 | 16.8181 | 15.8534 | 14.4746 | 15.0081 | 14.9551 | 15.4977 | 13.3462 | 13.4702 | 14.0308 |  |  |  | 16.5751 | 15.8979 | 15.2103 | 58.0088 | 57.5026 | 73.0819 | 17.2937 | 16.3697 | 15.2571 | 16.881 | 16.1418 | 15.278 | 13.3064 | 64.8575 |  | 24.0428 | 45.662 | 50.425 | 20.4977 |  | 6.4192 | 6.4454 | 5.8973 | 6.0044 | 6.0598 | 6.8052 | 18.8688 | 4.8472 | 6.4126 | 4.4843 | 6.767 | 8.1701 | 42.3818 | 47.0924 | 42.9384 | 14.9241 |  |  | -0.083233 | -0.30547 | 0.11816 | 0.14588 | 0.076388 | -0.21534 | 0.22332 | 0.51567 | -0.69198 | -1.3364 | -0.14973 | 8.8677 | 8.8687 | 2.0047 | 15.8592 | 16.702 | 17.2207 | 17.5337 | 17.5007 | 16.461 | 14.8147 | 16.8299 | 17.1678 | 17.4687 | 17.5092 | 17.2428 | 16.4292 | 14.6374 | 13.8298 | 9.5363 | 8.4095 | 7.1535 | 7.6962 | 8.1351 | 8.1021 | 15.9373 | 15.511 | 15.355 | 14.2783 | 14.1762 | 14.1383 |  |  |  | 13.2107 | 65.8555 | 48.1835 | 19.3085 | -0.054248 | -0.29451 | 17.7753 |  |  | 10.614 |  |  | 16.8636 | 16.0488 | 15.4401 | 16.3432 | 15.6208 | 14.821 | 54.0593 | 67.2769 | 40.3268 | 41.1519 | 21.7707 |  | 13.2096 | 23.5534 | 13.5481 | 17.8421 | 14.027 | 53.6011 |  | 20.6007 |  |  | 12.3861 | 13.2116 | 19.0588 | [6 empty] | 16.8931 |  |  | 15.6248 |  |  | 10.8614 | 15.2977 | 78.9988 | 8.1311 | 12.7653 | 48.8897 | 8.6219 | 11.8585 | 53.8823 | 12.2481 | 40.3921 | 8.4715 | 34.6547 | 9.2501 | 35.1754 | 8.5933 | 13.612 | 48.3752 | 12.3823 | 13.8604 | 66.3643 | 9.0362 | 12.5941 | 54.8241 | 9.2164 | 34.5326 | 11.7162 | 34.7348 | 9.7066 | 35.4447 | 0.10804 | 20.4779 | 0.30703 | 0.05306 | -37.7487 | 3.121 | 50.8 | 49.33 | -0.37411 | -0.64404 | 0.40056 | 0.44507 | 0.32227 | -0.54109 | 0.55103 | 0.14346 | 0.10515 | 0.27966 | -0.2778 | 0.32063 | 0.18203 | 0.21189
42810.4416 | 135 | 18.6104 | 18.635 | 18.6027 | 18.6048 | 17.9206 | 16.5311 | 14.5903 | 16.6751 | 17.1883 | 17.2835 | 17.2944 | 16.8252 | 15.8573 | 14.4689 | 15.0064 | 14.9515 | 15.4941 | 13.3428 | 13.4696 | 14.0334 |  |  |  | 16.5752 | 15.8981 | 15.2185 | 58.2699 | 57.7139 | 73.1394 | 17.2913 | 16.3735 | 15.2519 | 16.8754 | 16.1388 | 15.2677 | 13.3448 | 64.7453 |  | 24.1662 | 45.9315 | 50.6329 | 21.0121 |  | 6.4331 | 6.452 | 5.906 | 6.01 | 6.0633 | 6.8038 | 19.3349 | 4.7937 | 6.4251 | 4.4783 | 6.768 | 8.1716 | 42.3822 | 47.0994 | 42.9437 | 14.9307 |  |  | -0.082577 | -0.20887 | -0.012608 | 0.050598 | -0.13454 | -0.15291 | 0.66884 | 0.38031 | -0.49446 | -0.93504 | -0.19742 | 8.8683 | 8.8695 | 2.0051 | 15.8532 | 16.6924 | 17.2144 | 17.5338 | 17.4935 | 16.4526 | 14.8021 | 16.8225 | 17.1622 | 17.4648 | 17.5021 | 17.2304 | 16.4243 | 14.6287 | 13.4969 | 9.4329 | 8.8907 | 7.1959 | 7.4469 | 8.156 | 8.1136 | 15.9345 | 15.5049 | 15.3452 | 14.2703 | 14.1723 | 14.1322 |  |  |  | 13.2425 | 66.0964 | 48.5849 | 19.5912 | -0.098415 | -0.22694 | 17.862 |  |  | 10.619 |  |  | 16.8535 | 16.052 | 15.4538 | 16.3505 | 15.6298 | 14.8245 | 54.3018 | 67.3505 | 40.5703 | 41.4085 | 21.7996 |  | 13.2578 | 24.7047 | 13.6333 | 17.6501 | 14.0728 | 53.2049 |  | 20.7163 |  |  | 12.3755 | 13.2113 | 19.1502 | [6 empty] | 16.8973 |  |  | 15.6548 |  |  | 10.8702 | 15.3287 | 79.0245 | 8.1448 | 12.7816 | 49.1725 | 8.6291 | 11.878 | 54.1148 | 12.2612 | 40.6896 | 8.475 | 34.7043 | 9.2651 | 35.3863 | 8.6002 | 13.6304 | 48.6374 | 12.3899 | 13.8915 | 66.459 | 9.0295 | 12.6272 | 55.0428 | 9.1981 | 34.7831 | 11.7208 | 34.8364 | 9.7096 | 35.5804 | 0.24536 | 20.4722 | 0.30985 | 0.052459 | -37.7557 | 3.1209 | 50.68 | 49.73 | -0.37266 | -0.53257 | -0.13085 | 0.26212 | -0.4277 | -0.45596 | 0.95361 | 0.14425 | 0.075989 | 0.28652 | -0.23838 | 0.2685 | 0.16901 | 0.20509
42810.4416 | 136 | 18.6054 | 18.6262 | 18.5984 | 18.5985 | 17.9159 | 16.5282 | 14.5816 | 16.6781 | 17.1871 | 17.2795 | 17.2892 | 16.8229 | 15.8521 | 14.4773 | 15.0114 | 14.954 | 15.4934 | 13.3458 | 13.4621 | 14.0347 |  |  |  | 16.5706 | 15.896 | 15.2199 | 58.4297 | 57.9287 | 72.5468 | 17.2971 | 16.3688 | 15.2612 | 16.8785 | 16.1396 | 15.2736 | 13.3897 | 64.4914 |  | 24.251 | 46.1839 | 50.8485 | 20.8354 |  | 6.4321 | 6.4565 | 5.905 | 6.007 | 6.075 | 6.8309 | 20.0581 | 4.7058 | 6.4214 | 4.4503 | 6.7659 | 8.1772 | 42.3866 | 47.1078 | 42.953 | 14.951 |  |  | -0.11412 | -0.079425 | 0.14839 | 0.24511 | -0.11943 | 0.13162 | 0.24172 | 0.27911 | -0.331 | -0.35788 | -0.36691 | 8.8705 | 8.8713 | 2.0062 | 15.8522 | 16.6915 | 17.2214 | 17.5379 | 17.4915 | 16.4599 | 14.8063 | 16.8175 | 17.1578 | 17.4566 | 17.5032 | 17.2354 | 16.419 | 14.626 | 13.0885 | 9.4204 | 8.6382 | 7.2122 | 7.1828 | 8.1741 | 8.1167 | 15.9391 | 15.5123 | 15.3485 | 14.2726 | 14.1795 | 14.1447 |  |  |  | 13.2947 | 66.2134 | 48.9731 | 19.4341 | -0.05364 | -0.042132 | 18.0165 |  |  | 10.6262 |  |  | 16.8619 | 16.0458 | 15.4665 | 16.3438 | 15.6266 | 14.8236 | 54.5854 | 67.3871 | 40.7932 | 41.6336 | 21.6112 |  | 13.2947 | 26.166 | 13.7222 | 18.0164 | 14.1119 | 52.9257 |  | 20.8056 |  |  | 12.36 | 13.206 | 19.1351 | [6 empty] | 16.9972 |  |  | 15.6763 |  |  | 10.8897 | 15.3709 | 79.2673 | 8.1549 | 12.8008 | 49.4347 | 8.6354 | 11.9174 | 54.318 | 12.2861 | 40.8671 | 8.493 | 34.7874 | 9.2671 | 35.6177 | 8.6003 | 13.6301 | 48.8373 | 12.3951 | 13.9263 | 66.5724 | 9.0302 | 12.6722 | 55.3011 | 9.149 | 35.0188 | 11.7168 | 35.0132 | 9.7157 | 35.6973 | 0.19451 | 20.467 | 0.31238 | 0.051562 | -37.8008 | 3.121 | 56.17 | 49.78 | -0.43772 | -0.32841 | 0.44889 | 0.57692 | -0.40299 | 0.42305 | 0.57331 | 0.15071 | 0.038347 | 0.27764 | -0.19089 | 0.29691 | 0.1754 | 0.21118
42810.4416 | 137 | 18.6016 | 18.6257 | 18.5982 | 18.5971 | 17.9129 | 16.5269 | 14.576 | 16.678 | 17.1822 | 17.2739 | 17.2949 | 16.8216 | 15.8564 | 14.4722 | 15.0122 | 14.9545 | 15.4947 | 13.3427 | 13.4686 | 14.0353 |  |  |  | 16.5745 | 15.9012 | 15.2254 | 58.5299 | 58.1501 | 72.4751 | 17.2925 | 16.3696 | 15.2587 | 16.8766 | 16.139 | 15.2795 | 13.4155 | 64.4939 |  | 24.3446 | 46.403 | 51.0631 | 20.0598 |  | 6.4461 | 6.4627 | 5.9053 | 6.0112 | 6.0964 | 7.0923 | 20.7437 | 4.6304 | 6.4248 | 4.4645 | 6.77 | 8.1776 | 42.3951 | 47.1119 | 42.9527 | 14.9637 |  |  | -0.099661 | -0.032769 | 0.15562 | -0.010514 | 0.089532 | -0.15357 | 0.51114 | 0.42959 | -0.49388 | -0.18648 | -0.29816 | 8.8721 | 8.8731 | 2.0062 | 15.8493 | 16.6977 | 17.2183 | 17.5422 | 17.4922 | 16.4627 | 14.8063 | 16.8253 | 17.1634 | 17.457 | 17.5089 | 17.2368 | 16.4228 | 14.6294 | 12.4419 | 9.2017 | 8.3006 | 7.2164 | 7.0976 | 8.1827 | 8.1238 | 15.9396 | 15.5225 | 15.3531 | 14.2761 | 14.1828 | 14.1424 |  |  |  | 13.3355 | 66.3773 | 49.5285 | 19.1293 | -0.064986 | -0.23259 | 18.1291 |  |  | 10.6222 |  |  | 16.8694 | 16.0594 | 15.476 | 16.3515 | 15.6215 | 14.8302 | 54.9094 | 67.5095 | 41.0126 | 41.8274 | 21.3792 |  | 13.3332 | 26.4156 | 13.7909 | 18.4465 | 14.1466 | 52.5936 |  | 20.8888 |  |  | 12.3541 | 13.2301 | 19.1332 | [6 empty] | 17.0859 |  |  | 15.6835 |  |  | 10.8984 | 15.4055 | 79.4977 | 8.1295 | 12.8464 | 49.6276 | 8.6314 | 11.9348 | 54.4797 | 12.3023 | 40.9013 | 8.4969 | 34.9204 | 9.2713 | 35.7999 | 8.5525 | 13.6067 | 49.0828 | 12.4008 | 13.9501 | 66.7807 | 9.0273 | 12.7007 | 55.4793 | 9.1003 | 35.2398 | 11.7138 | 35.2866 | 9.7235 | 35.8161 | 0.091665 | 20.4615 | 0.31643 | 0.052973 | -37.7734 | 3.121 | 44.95 | 48.91 | -0.40901 | -0.21095 | 0.4597 | -0.11949 | 0.34908 | -0.45718 | 0.83407 | 0.15843 | 0.033687 | 0.26684 | -0.11805 | 0.33525 | 0.1978 | 0.221
42810.4416 | 138 | 18.5996 | 18.626 | 18.5901 | 18.5973 | 17.9078 | 16.521 | 14.5703 | 16.6788 | 17.1713 | 17.2732 | 17.2888 | 16.8201 | 15.8541 | 14.4661 | 15.0081 | 14.9571 | 15.4952 | 13.3387 | 13.4663 | 14.0344 |  |  |  | 16.5739 | 15.8925 | 15.2286 | 58.7203 | 58.3636 | 72.9054 | 17.2878 | 16.371 | 15.2522 | 16.8759 | 16.1364 | 15.2837 | 13.4358 | 64.3883 |  | 24.4554 | 46.6175 | 51.2862 | 19.7218 |  | 6.4374 | 6.4531 | 5.9018 | 6.0096 | 6.147 | 7.2619 | 21.234 | 4.5423 | 6.413 | 4.474 | 6.7598 | 8.1748 | 42.3974 | 47.1036 | 42.9507 | 14.9668 |  |  | -0.077321 | 0.042799 | 0.088588 | -0.17085 | 0.1789 | 0.20062 | 0.34817 | 0.19106 | -0.33548 | -0.28193 | -0.21451 | 8.8697 | 8.8707 | 2.0058 | 15.859 | 16.7009 | 17.2213 | 17.5438 | 17.5051 | 16.4607 | 14.8114 | 16.824 | 17.164 | 17.4718 | 17.5091 | 17.2335 | 16.426 | 14.6253 | 11.746 | 8.9724 | 7.7769 | 7.185 | 7.0959 | 8.1853 | 8.1284 | 15.9367 | 15.5128 | 15.3511 | 14.2726 | 14.1809 | 14.1463 |  |  |  | 13.3608 | 66.5909 | 49.6903 | 18.6878 | 0.05779 | -0.053989 | 18.2424 |  |  | 10.6174 |  |  | 16.8569 | 16.051 | 15.4828 | 16.3492 | 15.6201 | 14.8273 | 55.1527 | 67.7816 | 41.2237 | 42.0127 | 21.2928 |  | 13.3727 | 25.3311 | 13.8486 | 18.4229 | 14.1837 | 52.6356 |  | 20.997 |  |  | 12.35 | 13.2499 | 19.1412 | [6 empty] | 17.0937 |  |  | 15.709 |  |  | 10.9051 | 15.4343 | 79.7051 | 8.0893 | 12.8862 | 49.8033 | 8.6386 | 11.9357 | 54.6821 | 12.3127 | 40.9179 | 8.5151 | 35.0819 | 9.2721 | 35.9371 | 8.5235 | 13.606 | 49.2888 | 12.4162 | 13.9762 | 67.0313 | 9.035 | 12.7315 | 55.6222 | 9.108 | 35.4434 | 11.719 | 35.4917 | 9.7374 | 35.9995 | 0.1766 | 20.4581 | 0.3195 | 0.052763 | -37.7079 | 3.121 | 55.22 | 49.86 | -0.36049 | 0.24108 | 0.34684 | -0.48167 | 0.49359 | 0.52269 | 0.68859 | 0.16213 | 0.065725 | 0.26873 | -0.040427 | 0.39397 | 0.20786 | 0.2341
42810.4416 | 139 | 18.5973 | 18.6301 | 18.5881 | 18.597 | 17.9106 | 16.5231 | 14.5695 | 16.6796 | 17.1706 | 17.2672 | 17.2885 | 16.8238 | 15.8525 | 14.4704 | 15.013 | 14.9649 | 15.5011 | 13.3486 | 13.48 | 14.04 |  |  |  | 16.5725 | 15.8941 | 15.2457 | 58.9264 | 58.5678 | 73.0519 | 17.2922 | 16.3675 | 15.2644 | 16.8751 | 16.142 | 15.2906 | 13.4738 | 64.7681 |  | 24.5796 | 46.8319 | 51.4855 | 20.3151 |  | 6.4365 | 6.4437 | 5.8913 | 6.0077 | 6.1611 | 7.4566 | 21.4547 | 4.4787 | 6.4099 | 4.4771 | 6.764 | 8.1786 | 42.3843 | 47.1019 | 42.9375 | 14.9829 |  |  | 0.099443 | -0.24567 | 0.15233 | -0.06111 | 0.20913 | 0.092192 | 0.41717 | 0.23574 | -0.016331 | -0.52719 | -0.27789 | 8.8693 | 8.8708 | 2.0061 | 15.8539 | 16.7013 | 17.2221 | 17.5388 | 17.5077 | 16.4562 | 14.8043 | 16.8242 | 17.1624 | 17.4614 | 17.5058 | 17.2361 | 16.418 | 14.6268 | 11.8284 | 8.8776 | 7.3431 | 6.9776 | 7.067 | 8.1933 | 8.1259 | 15.9364 | 15.51 | 15.3595 | 14.2756 | 14.1836 | 14.1413 |  |  |  | 13.3844 | 66.8413 | 49.9743 | 18.2235 | -0.19992 | -0.047213 | 18.1826 |  |  | 10.6184 |  |  | 16.8608 | 16.0444 | 15.5018 | 16.3515 | 15.6269 | 14.837 | 55.3403 | 67.9607 | 41.4288 | 42.2436 | 20.9375 |  | 13.4186 | 23.7025 | 13.899 | 17.9606 | 14.2331 | 52.5966 |  | 21.1104 |  |  | 12.3466 | 13.254 | 19.1997 | [6 empty] | 16.9983 |  |  | 15.7394 |  |  | 10.9183 | 15.4627 | 79.7857 | 8.0384 | 12.8868 | 50.0047 | 8.6491 | 11.9462 | 54.892 | 12.3251 | 41.082 | 8.5281 | 35.1877 | 9.28 | 36.0545 | 8.522 | 13.6466 | 49.4344 | 12.4292 | 14.0299 | 67.2255 | 9.0462 | 12.7508 | 55.7959 | 9.1009 | 35.6081 | 11.7273 | 35.5516 | 9.7539 | 36.2735 | 0.066242 | 20.4512 | 0.32083 | 0.050498 | -37.7347 | 3.121 | 24.5 | 49.63 | 0.4089 | -0.57758 | 0.45481 | -0.28806 | 0.53385 | 0.35446 | 0.754 | 0.17352 | 0.11263 | 0.28321 | -0.048659 | 0.44188 | 0.19264 | 0.24778
42810.4417 | 140 | 18.6034 | 18.6342 | 18.5927 | 18.5957 | 17.9121 | 16.5266 | 14.5731 | 16.6733 | 17.1791 | 17.2672 | 17.2846 | 16.8192 | 15.8534 | 14.4765 | 15.0236 | 14.9659 | 15.5016 | 13.3512 | 13.485 | 14.0473 |  |  |  | 16.5766 | 15.9003 | 15.2543 | 59.0758 | 58.7968 | 73.0946 | 17.2945 | 16.3688 | 15.2737 | 16.8784 | 16.1405 | 15.3018 | 13.532 | 65.3898 |  | 24.7078 | 47.0346 | 51.6899 | 21.6571 |  | 6.4395 | 6.4534 | 5.9002 | 6.0041 | 6.1569 | 7.5015 | 21.4211 | 4.4953 | 6.4095 | 4.4943 | 6.7627 | 8.1788 | 42.363 | 47.0997 | 42.9354 | 14.9839 |  |  | -0.214 | -0.13265 | 0.009736 | -0.11697 | 0.14999 | 0.16973 | 0.38103 | 0.15294 | -0.50419 | -0.70972 | -0.27332 | 8.8716 | 8.8727 | 2.0067 | 15.8525 | 16.6936 | 17.2099 | 17.5317 | 17.4934 | 16.4598 | 14.8063 | 16.8228 | 17.1593 | 17.4603 | 17.508 | 17.2337 | 16.4114 | 14.6273 | 12.2551 | 8.8044 | 7.1023 | 6.7801 | 6.9869 | 8.2189 | 8.1253 | 15.9311 | 15.5078 | 15.3463 | 14.2732 | 14.1707 | 14.1295 |  |  |  | 13.4037 | 67.1032 | 50.3681 | 17.8881 | -0.14441 | -0.124 | 18.0805 |  |  | 10.6195 |  |  | 16.8739 | 16.0525 | 15.5166 | 16.3561 | 15.6282 | 14.8424 | 55.5438 | 68.1672 | 41.6185 | 42.4475 | 20.2244 |  | 13.4484 | 22.947 | 13.9297 | 17.6815 | 14.255 | 52.9676 |  | 21.1953 |  |  | 12.3336 | 13.2629 | 19.065 | [6 empty] | 16.881 |  |  | 15.7776 |  |  | 10.9225 | 15.4893 | 79.7853 | 7.9811 | 12.8639 | 50.2398 | 8.6624 | 11.9482 | 55.1646 | 12.3359 | 41.299 | 8.526 | 35.3954 | 9.2817 | 36.1668 | 8.5421 | 13.7295 | 49.5997 | 12.4419 | 14.0756 | 67.4067 | 9.057 | 12.7769 | 56.0073 | 9.0897 | 35.8106 | 11.7485 | 35.6927 | 9.7697 | 36.5241 | 0.10303 | 20.4486 | 0.32481 | 0.053342 | -37.8508 | 3.1211 | 46.13 | 49.01 | -0.59988 | -0.42441 | 0.11498 | -0.39854 | 0.45215 | 0.48099 | 0.72066 | 0.19432 | 0.13463 | 0.29169 | -0.093088 | 0.46857 | 0.15729 | 0.25773
42810.4417 | 141 | 18.6055 | 18.6377 | 18.6012 | 18.599 | 17.9095 | 16.5237 | 14.5758 | 16.6703 | 17.183 | 17.2683 | 17.2901 | 16.8221 | 15.8578 | 14.4761 | 15.0163 | 14.9622 | 15.4973 | 13.3444 | 13.4719 | 14.0397 |  |  |  | 16.5748 | 15.8914 | 15.2538 | 59.2808 | 58.9828 | 73.2267 | 17.2981 | 16.3822 | 15.2707 | 16.8797 | 16.1378 | 15.2981 | 13.5793 | 65.6693 |  | 24.8435 | 47.2454 | 51.9144 | 22.2221 |  | 6.4229 | 6.4466 | 5.8988 | 6.0065 | 6.145 | 7.5286 | 21.5025 | 4.5679 | 6.4086 | 4.4554 | 6.7561 | 8.1773 | 42.3448 | 47.1127 | 42.9329 | 14.9836 |  |  | -0.10623 | -0.070225 | 0.038648 | -0.047314 | -0.013636 | 0.05474 | 0.6143 | 0.21406 | -0.7669 | -0.4076 | -0.37545 | 8.869 | 8.87 | 2.0069 | 15.8577 | 16.6947 | 17.2184 | 17.538 | 17.4945 | 16.4605 | 14.8042 | 16.8234 | 17.1667 | 17.4587 | 17.5063 | 17.2339 | 16.4182 | 14.6263 | 12.8106 | 8.7652 | 6.9193 | 6.6598 | 6.9161 | 8.2448 | 8.127 | 15.9418 | 15.5202 | 15.35 | 14.2786 | 14.1862 | 14.1466 |  |  |  | 13.4301 | 67.5396 | 50.5591 | 17.6932 | -0.089703 | -0.11911 | 18.028 |  |  | 10.6151 |  |  | 16.871 | 16.0534 | 15.5208 | 16.3564 | 15.6279 | 14.8497 | 55.7545 | 68.3681 | 41.8054 | 42.653 | 19.5469 |  | 13.4785 | 23.3084 | 13.9725 | 17.5521 | 14.2848 | 52.8249 |  | 21.3023 |  |  | 12.3182 | 13.2734 | 18.7714 | [6 empty] | 16.7902 |  |  | 15.8184 |  |  | 10.9328 | 15.5149 | 79.8246 | 7.9523 | 12.8626 | 50.476 | 8.6712 | 11.9662 | 55.4371 | 12.3381 | 41.4828 | 8.5496 | 35.715 | 9.282 | 36.3004 | 8.534 | 13.8082 | 49.7758 | 12.46 | 14.092 | 67.4806 | 9.0652 | 12.8306 | 56.1406 | 9.1208 | 36.078 | 11.7607 | 35.953 | 9.7754 | 36.7637 | 0.32587 | 20.4447 | 0.32749 | 0.0545 | -37.76 | 3.1211 | 34.06 | 50.42 | -0.42274 | -0.3088 | 0.22908 | -0.25347 | -0.13634 | 0.27316 | 0.91509 | 0.21414 | 0.12602 | 0.29627 | -0.15181 | 0.48909 | 0.14316 | 0.26402
42810.4417 | 142 | 18.6163 | 18.6325 | 18.5964 | 18.6078 | 17.9211 | 16.5223 | 14.5778 | 16.6799 | 17.1765 | 17.2802 | 17.2918 | 16.8232 | 15.8549 | 14.4719 | 15.0146 | 14.9665 | 15.5047 | 13.3526 | 13.4734 | 14.034 |  |  |  | 16.5758 | 15.8909 | 15.2611 | 59.5409 | 59.1355 | 73.1068 | 17.2943 | 16.3717 | 15.2821 | 16.8858 | 16.1457 | 15.3075 | 13.6367 | 65.4513 |  | 24.9988 | 47.4505 | 52.1401 | 22.4819 |  | 6.4343 | 6.4433 | 5.8983 | 6.0201 | 6.1548 | 7.5559 | 21.8661 | 4.6077 | 6.4032 | 4.3953 | 6.7586 | 8.1872 | 42.3292 | 47.1281 | 42.9477 | 14.9927 |  |  | -0.14566 | 0.14531 | 0.18124 | -0.11039 | 0.034992 | 0.24136 | 0.41651 | 0.33759 | -0.19128 | -0.11388 | -0.36234 | 8.8697 | 8.871 | 2.0069 | 15.8544 | 16.7007 | 17.2235 | 17.5431 | 17.4986 | 16.4597 | 14.8111 | 16.8212 | 17.1714 | 17.4592 | 17.5083 | 17.2347 | 16.418 | 14.6253 | 12.4065 | 8.7858 | 7.7127 | 6.5843 | 6.8878 | 8.2375 | 8.1271 | 15.9432 | 15.5202 | 15.3586 | 14.2809 | 14.1935 | 14.1496 |  |  |  | 13.4738 | 67.7917 | 50.824 | 17.527 | 0.049078 | -0.090499 | 18.0915 |  |  | 10.6182 |  |  | 16.8628 | 16.0512 | 15.5331 | 16.3592 | 15.6228 | 14.8543 | 55.9213 | 68.5662 | 41.9863 | 42.8897 | 18.9651 |  | 13.4975 | 25.1726 | 14.0362 | 17.3109 | 14.3038 | 53.2369 |  | 21.4066 |  |  | 12.2477 | 13.2929 | 18.486 | [6 empty] | 16.7183 |  |  | 15.8539 |  |  | 10.9416 | 15.5328 | 79.8947 | 7.9719 | 12.8904 | 50.5828 | 8.6748 | 11.9786 | 55.5796 | 12.3384 | 41.5406 | 8.5849 | 36.0043 | 9.2768 | 36.4921 | 8.5256 | 13.8648 | 49.9058 | 12.477 | 14.1237 | 67.5064 | 9.0684 | 12.8943 | 56.2454 | 9.1566 | 36.3093 | 11.7834 | 36.2602 | 9.7862 | 37.0016 | 0.27964 | 20.4376 | 0.32882 | 0.053132 | -37.7014 | 3.121 | 50.86 | 49.07 | -0.49492 | 0.4442 | 0.49609 | -0.38717 | 0.21841 | 0.57362 | 0.75354 | 0.23092 | 0.076346 | 0.3036 | -0.10776 | 0.40096 | 0.13785 | 0.27009
42810.4417 | 143 | 18.6152 | 18.6292 | 18.5936 | 18.5993 | 17.9088 | 16.5204 | 14.5738 | 16.6803 | 17.1807 | 17.272 | 17.286 | 16.816 | 15.8532 | 14.4697 | 15.0118 | 14.9671 | 15.5 | 13.35 | 13.4759 | 14.0424 |  |  |  | 16.5793 | 15.8902 | 15.2665 | 59.7137 | 59.2977 | 72.8395 | 17.2946 | 16.3778 | 15.2787 | 16.8835 | 16.1442 | 15.3093 | 13.6825 | 65.3866 |  | 25.1213 | 47.6626 | 52.3031 | 22.2198 |  | 6.4416 | 6.4566 | 5.9132 | 6.0279 | 6.1581 | 7.5224 | 22.0202 | 4.6678 | 6.4124 | 4.3505 | 6.7651 | 8.1792 | 42.3085 | 47.1115 | 42.964 | 14.9851 |  |  | -0.23306 | -0.13659 | 0.032736 | 0.22473 | 0.03302 | -0.080628 | 0.51574 | 0.033348 | 0.88428 | -0.73175 | -0.3532 | 8.8716 | 8.8727 | 2.0069 | 15.8456 | 16.6913 | 17.2165 | 17.5359 | 17.4956 | 16.4578 | 14.8044 | 16.8231 | 17.1618 | 17.4573 | 17.5049 | 17.2372 | 16.4148 | 14.626 | 11.8496 | 8.706 | 7.8691 | 7.0944 | 7.0171 | 8.2394 | 8.1326 | 15.9354 | 15.5146 | 15.3526 | 14.2814 | 14.1898 | 14.1514 |  |  |  | 13.5103 | 68.0238 | 51.3877 | 17.466 | 0.036517 | 0.09356 | 18.1983 |  |  | 10.6303 |  |  | 16.8644 | 16.0502 | 15.547 | 16.3622 | 15.6267 | 14.8566 | 56.1175 | 68.7269 | 42.151 | 43.1117 | 19.3412 |  | 13.5506 | 27.3641 | 14.136 | 17.0069 | 14.3465 | 52.9616 |  | 21.4968 |  |  | 12.2187 | 13.3096 | 18.4436 | [6 empty] | 16.6407 |  |  | 15.8938 |  |  | 10.9559 | 15.5573 | 79.7759 | 7.9873 | 12.8866 | 50.7029 | 8.6874 | 12.0048 | 55.7133 | 12.369 | 41.7261 | 8.6243 | 36.3149 | 9.2784 | 36.7053 | 8.53 | 13.913 | 50.0955 | 12.5042 | 14.1775 | 67.5906 | 9.0673 | 12.9409 | 56.3402 | 9.1877 | 36.5166 | 11.813 | 36.5443 | 9.8017 | 37.2005 | 0.286 | 20.4357 | 0.33288 | 0.053972 | -37.7854 | 3.121 | 36.51 | 48.97 | -0.62579 | -0.43068 | 0.21084 | 0.55243 | 0.21216 | -0.33152 | 0.83846 | 0.22224 | 0.018777 | 0.31346 | -0.045656 | 0.38422 | 0.14664 | 0.27299
42810.4417 | 144 | 18.6133 | 18.6321 | 18.5935 | 18.5988 | 17.9059 | 16.5174 | 14.5732 | 16.6785 | 17.1796 | 17.277 | 17.2813 | 16.8198 | 15.8502 | 14.4683 | 15.0234 | 14.9695 | 15.4965 | 13.3526 | 13.4761 | 14.0487 |  |  |  | 16.5774 | 15.8915 | 15.2765 | 59.8067 | 59.4735 | 72.4335 | 17.3034 | 16.3785 | 15.2899 | 16.8774 | 16.1477 | 15.3206 | 13.7258 | 65.4549 |  | 25.2357 | 47.8808 | 52.4534 | 21.8674 |  | 6.4341 | 6.4525 | 5.9056 | 6.0378 | 6.151 | 7.4677 | 21.8254 | 4.6985 | 6.409 | 4.3449 | 6.7575 | 8.1756 | 42.2763 | 47.0773 | 42.9874 | 14.9707 |  |  | -0.32571 | -0.11557 | 0.032076 | 0.12748 | 0.023164 | -0.3231 | 0.50654 | 0.020208 | -0.69451 | -0.20242 | -0.23596 | 8.8697 | 8.871 | 2.0068 | 15.8505 | 16.6923 | 17.2201 | 17.5379 | 17.4847 | 16.4511 | 14.7949 | 16.807 | 17.1516 | 17.4528 | 17.4947 | 17.2384 | 16.4163 | 14.6195 | 11.3642 | 8.6434 | 7.499 | 7.2442 | 7.2351 | 8.2412 | 8.1425 | 15.9339 | 15.5122 | 15.3504 | 14.2784 | 14.1868 | 14.1449 |  |  |  | 13.5379 | 68.2399 | 52.0224 | 17.342 | -0.094363 | -0.063775 | 18.2731 |  |  | 10.6328 |  |  | 16.8638 | 16.051 | 15.5605 | 16.3582 | 15.6305 | 14.8587 | 56.3203 | 68.8422 | 42.3485 | 43.3481 | 20.2911 |  | 13.5958 | 28.7234 | 14.2223 | 16.7805 | 14.3678 | 52.7756 |  | 21.5674 |  |  | 12.1727 | 13.3088 | 18.6679 | [6 empty] | 16.5244 |  |  | 15.903 |  |  | 10.9539 | 15.5829 | 79.8486 | 7.986 | 12.8889 | 50.9062 | 8.6852 | 12.0051 | 55.8811 | 12.3662 | 42.1361 | 8.6192 | 36.6599 | 9.2785 | 36.9035 | 8.5454 | 13.9303 | 50.3045 | 12.5156 | 14.2017 | 67.7183 | 9.0722 | 12.963 | 56.5083 | 9.2127 | 36.6977 | 11.8279 | 36.6713 | 9.8179 | 37.3234 | 0.35707 | 20.4324 | 0.33564 | 0.055101 | -37.7671 | 3.1211 | 40.42 | 50.48 | -0.73936 | -0.39614 | 0.2087 | 0.41607 | 0.17768 | -0.66358 | 0.83086 | 0.19735 | -0.016118 | 0.32045 | 0.0084926 | 0.42648 | 0.15787 | 0.27735
42810.4417 | 145 | 18.6105 | 18.6293 | 18.5951 | 18.6041 | 17.9041 | 16.5217 | 14.573 | 16.6771 | 17.1753 | 17.2782 | 17.2812 | 16.8137 | 15.8493 | 14.4736 | 15.0225 | 14.9786 | 15.5077 | 13.3556 | 13.4845 | 14.0522 |  |  |  | 16.5774 | 15.8951 | 15.2885 | 59.9448 | 59.5816 | 72.7809 | 17.3066 | 16.383 | 15.2986 | 16.8819 | 16.1485 | 15.3312 | 13.7603 | 65.6909 |  | 25.3516 | 48.1494 | 52.6091 | 21.5008 |  | 6.443 | 6.463 | 5.9218 | 6.0516 | 6.1605 | 7.438 | 21.6726 | 4.7181 | 6.4208 | 4.3665 | 6.7658 | 8.1729 | 42.2534 | 47.0612 | 43.0089 | 14.965 |  |  | -0.15683 | -0.026853 | 0.067564 | -0.069654 | -0.11877 | 0.2223 | 0.45528 | 0.095776 | -0.65987 | 0.3374 | -0.20795 | 8.8693 | 8.8707 | 2.0062 | 15.8584 | 16.6998 | 17.2124 | 17.5359 | 17.4994 | 16.4603 | 14.8002 | 16.8199 | 17.1566 | 17.4527 | 17.5001 | 17.2294 | 16.4153 | 14.6185 | 11.087 | 8.6357 | 7.3409 | 7.0575 | 7.2903 | 8.2544 | 8.1503 | 15.9398 | 15.516 | 15.349 | 14.2715 | 14.1914 | 14.1556 |  |  |  | 13.5745 | 68.5113 | 52.5521 | 17.1365 | -0.00765 | -0.039121 | 18.3229 |  |  | 10.6332 |  |  | 16.8604 | 16.0494 | 15.5746 | 16.3488 | 15.6197 | 14.8527 | 56.5116 | 68.9701 | 42.5411 | 43.5486 | 21.4295 |  | 13.6453 | 28.4236 | 14.3011 | 16.6104 | 14.3877 | 52.5081 |  | 21.6543 |  |  | 12.1821 | 13.3084 | 18.9817 | [6 empty] | 16.4572 |  |  | 15.9179 |  |  | 10.9808 | 15.5973 | 80.0592 | 7.9817 | 12.8786 | 51.061 | 8.6891 | 12.0404 | 56.0675 | 12.3715 | 42.5299 | 8.6653 | 36.9704 | 9.3045 | 37.1527 | 8.5554 | 13.9403 | 50.5681 | 12.5464 | 14.2411 | 67.7783 | 9.0913 | 12.9865 | 56.6528 | 9.2486 | 36.929 | 11.8635 | 36.8726 | 9.842 | 37.4711 | 0.16331 | 20.4283 | 0.33836 | 0.053726 | -37.7479 | 3.1211 | 51.3 | 49.37 | -0.51331 | -0.19096 | 0.3029 | -0.30755 | -0.40231 | 0.5504 | 0.78767 | 0.16737 | -0.0051774 | 0.32584 | 0.040828 | 0.44496 | 0.1692 | 0.28427
42810.4417 | 146 | 18.6102 | 18.6405 | 18.6042 | 18.6091 | 17.9128 | 16.5276 | 14.577 | 16.6893 | 17.1853 | 17.2731 | 17.2952 | 16.8127 | 15.8553 | 14.4777 | 15.0198 | 14.9635 | 15.4979 | 13.3449 | 13.4719 | 14.039 |  |  |  | 16.5651 | 15.8921 | 15.2838 | 60.1255 | 59.74 | 73.3566 | 17.304 | 16.3876 | 15.302 | 16.8883 | 16.1418 | 15.3327 | 13.7903 | 65.7907 |  | 25.4505 | 48.3964 | 52.743 | 21.2306 |  | 6.4489 | 6.468 | 5.9276 | 6.0575 | 6.1607 | 7.4386 | 21.6927 | 4.6926 | 6.4208 | 4.4182 | 6.7754 | 8.182 | 42.2323 | 47.0541 | 43.0385 | 14.9551 |  |  | -0.306 | -0.26473 | -0.057948 | -0.091338 | -0.087888 | -0.055 | 0.53545 | 0.20946 | -0.30025 | -0.43467 | -0.29498 | 8.8695 | 8.8705 | 2.006 | 15.849 | 16.6988 | 17.2157 | 17.5354 | 17.4842 | 16.4556 | 14.8031 | 16.8168 | 17.1567 | 17.4508 | 17.4994 | 17.2266 | 16.4161 | 14.6124 | 11.6353 | 8.6895 | 7.2539 | 7.1463 | 7.1961 | 8.2697 | 8.1445 | 15.9454 | 15.5192 | 15.3532 | 14.2762 | 14.1959 | 14.1506 |  |  |  | 13.6053 | 68.8196 | 52.7893 | 16.8171 | 0.055764 | -0.0086324 | 18.416 |  |  | 10.6404 |  |  | 16.8629 | 16.0557 | 15.5885 | 16.353 | 15.6255 | 14.8627 | 56.7317 | 69.1785 | 42.727 | 43.7186 | 22.1708 |  | 13.7009 | 27.5456 | 14.3625 | 16.5338 | 14.4176 | 52.1832 |  | 21.7502 |  |  | 12.1887 | 13.3173 | 19.1315 | [6 empty] | 16.412 |  |  | 15.9336 |  |  | 10.9907 | 15.6132 | 80.2201 | 7.9726 | 12.8783 | 51.1757 | 8.6978 | 12.0688 | 56.1779 | 12.3804 | 42.6138 | 8.697 | 37.2366 | 9.3136 | 37.3828 | 8.5516 | 13.9372 | 50.745 | 12.5436 | 14.2427 | 67.856 | 9.087 | 12.9867 | 56.7815 | 9.2779 | 37.0717 | 11.863 | 37.1034 | 9.832 | 37.6858 | 0.14116 | 20.4267 | 0.34019 | 0.052807 | -37.6987 | 3.1211 | 54.03 | 49.53 | -0.7176 | -0.59958 | -0.28052 | -0.35219 | -0.34607 | -0.27377 | 0.85421 | 0.14862 | 0.021247 | 0.32896 | -0.018323 | 0.45396 | 0.1777 | 0.29416
42810.4417 | 147 | 18.6164 | 18.6404 | 18.6052 | 18.6066 | 17.9164 | 16.5285 | 14.5863 | 16.687 | 17.1851 | 17.2786 | 17.2944 | 16.8183 | 15.8577 | 14.4763 | 15.019 | 14.9667 | 15.5038 | 13.342 | 13.4789 | 14.0481 |  |  |  | 16.5726 | 15.8954 | 15.2955 | 60.2796 | 59.9346 | 73.2958 | 17.3057 | 16.3835 | 15.3051 | 16.881 | 16.1495 | 15.329 | 13.8141 | 65.7822 |  | 25.533 | 48.6218 | 52.8595 | 21.0642 |  | 6.4467 | 6.4603 | 5.9274 | 6.0494 | 6.1575 | 7.4386 | 21.8889 | 4.6599 | 6.4018 | 4.453 | 6.7594 | 8.1843 | 42.221 | 47.0634 | 43.0523 | 14.9452 |  |  | -0.082577 | -0.022253 | -0.13549 | 0.21816 | 0.091504 | -0.0918 | 0.39154 | 0.47493 | -0.12083 | -0.7372 | -0.2308 | 8.8723 | 8.8732 | 2.0069 | 15.8519 | 16.7024 | 17.2192 | 17.5373 | 17.4942 | 16.4607 | 14.805 | 16.8123 | 17.1612 | 17.4573 | 17.5041 | 17.2333 | 16.4156 | 14.6246 | 12.7014 | 8.9446 | 7.3659 | 7.3949 | 7.3152 | 8.3027 | 8.1482 | 15.9341 | 15.5154 | 15.355 | 14.2795 | 14.194 | 14.1519 |  |  |  | 13.6251 | 69.0086 | 53.0904 | 16.5129 | -0.070253 | -0.15505 | 18.5983 |  |  | 10.6446 |  |  | 16.8658 | 16.0575 | 15.6004 | 16.3599 | 15.625 | 14.8677 | 56.9539 | 69.3723 | 42.8881 | 43.8814 | 22.6542 |  | 13.7361 | 27.0401 | 14.4053 | 16.5332 | 14.4442 | 52.0625 |  | 21.8296 |  |  | 12.1637 | 13.3075 | 19.2743 | [6 empty] | 16.5458 |  |  | 15.9295 |  |  | 11.0046 | 15.6466 | 80.2444 | 7.9784 | 12.871 | 51.2769 | 8.713 | 12.0853 | 56.3116 | 12.389 | 42.7445 | 8.7084 | 37.4583 | 9.3322 | 37.566 | 8.5566 | 13.9388 | 50.8638 | 12.5589 | 14.2619 | 68.0517 | 9.1044 | 13.026 | 56.998 | 9.3042 | 37.273 | 11.8724 | 37.1868 | 9.8522 | 37.9219 | 0.16524 | 20.4216 | 0.34454 | 0.054732 | -37.6413 | 3.1211 | 51.72 | 50.55 | -0.37275 | -0.17384 | -0.42894 | 0.54429 | 0.35312 | -0.35369 | 0.73045 | 0.13635 | 0.036708 | 0.32986 | -0.13295 | 0.44194 | 0.18311 | 0.30327
42810.4417 | 148 | 18.6168 | 18.6289 | 18.5882 | 18.6064 | 17.9085 | 16.5211 | 14.5772 | 16.6718 | 17.1704 | 17.2707 | 17.2901 | 16.8121 | 15.8475 | 14.4755 | 15.0204 | 14.9724 | 15.5027 | 13.3527 | 13.4761 | 14.0522 |  |  |  | 16.5747 | 15.9049 | 15.3036 | 60.2967 | 60.0529 | 73.1273 | 17.3054 | 16.3841 | 15.308 | 16.8823 | 16.1521 | 15.3438 | 13.8415 | 65.3937 |  | 25.6279 | 48.8251 | 52.9723 | 20.9927 |  | 6.4474 | 6.4762 | 5.9322 | 6.0717 | 6.1752 | 7.4446 | 21.7208 | 4.638 | 6.4054 | 4.4428 | 6.7705 | 8.1793 | 42.2164 | 47.0662 | 43.0677 | 14.9394 |  |  | -0.27906 | -0.11819 | -0.078976 | -0.071626 | 0.072448 | -0.23176 | 0.14972 | 0.55116 | -0.12336 | -0.68748 | -0.25822 | 8.8698 | 8.8711 | 2.0074 | 15.8583 | 16.702 | 17.2303 | 17.5442 | 17.4936 | 16.461 | 14.8096 | 16.8205 | 17.1608 | 17.4627 | 17.506 | 17.2386 | 16.42 | 14.6248 | 13.8675 | 9.125 | 7.3546 | 7.4208 | 7.43 | 8.3464 | 8.149 | 15.931 | 15.5112 | 15.3576 | 14.2792 | 14.1886 | 14.1453 |  |  |  | 13.6376 | 69.1353 | 53.0509 | 16.4227 | 0.032465 | -0.22996 | 18.6648 |  |  | 10.6524 |  |  | 16.8689 | 16.0573 | 15.6116 | 16.3539 | 15.6294 | 14.8659 | 57.0875 | 69.561 | 43.0567 | 44.0484 | 22.9425 |  | 13.7948 | 26.9233 | 14.4575 | 16.4268 | 14.49 | 51.9336 |  | 21.9093 |  |  | 12.165 | 13.2926 | 19.4199 | [6 empty] | 16.7094 |  |  | 15.9693 |  |  | 11.0094 | 15.6626 | 80.3096 | 7.9812 | 12.8568 | 51.4181 | 8.7183 | 12.0858 | 56.396 | 12.3921 | 43.0691 | 8.7194 | 37.5823 | 9.3443 | 37.733 | 8.5695 | 13.9498 | 51.0001 | 12.5627 | 14.2696 | 68.1953 | 9.1169 | 13.0645 | 57.1638 | 9.2977 | 37.4669 | 11.8908 | 37.2646 | 9.8663 | 38.1848 | 0.17159 | 20.419 | 0.3471 | 0.055904 | -37.7196 | 3.1211 | 50.32 | 49.35 | -0.68506 | -0.40064 | -0.32749 | -0.31188 | 0.31421 | -0.56199 | 0.4517 | 0.13029 | 0.041684 | 0.33433 | -0.25744 | 0.44329 | 0.186 | 0.30619
42810.4418 | 149 | 18.6098 | 18.6307 | 18.6023 | 18.6014 | 17.9075 | 16.5155 | 14.5737 | 16.6789 | 17.1788 | 17.2737 | 17.2854 | 16.8204 | 15.8515 | 14.4732 | 15.0117 | 14.9662 | 15.5012 | 13.3526 | 13.4793 | 14.0492 |  |  |  | 16.5666 | 15.9048 | 15.3131 | 60.4495 | 60.0949 | 73.9271 | 17.3009 | 16.3794 | 15.3179 | 16.8835 | 16.152 | 15.3342 | 13.8959 | 64.5991 |  | 25.7237 | 49.0189 | 53.098 | 21.1174 |  | 6.4428 | 6.4766 | 5.9254 | 6.0687 | 6.1731 | 7.4246 | 21.4641 | 4.6198 | 6.4052 | 4.4591 | 6.7681 | 8.181 | 42.234 | 47.0456 | 43.0693 | 14.9498 |  |  | -0.053009 | -0.22596 | -0.015892 | -0.077538 | 0.053392 | -0.0688 | 0.3048 | 0.44339 | -0.23934 | -0.1548 | -0.23934 | 8.8685 | 8.8695 | 2.0064 | 15.86 | 16.7012 | 17.2315 | 17.542 | 17.4915 | 16.4642 | 14.8126 | 16.8271 | 17.1596 | 17.4628 | 17.5061 | 17.2329 | 16.4215 | 14.623 | 14.746 | 9.3193 | 7.6149 | 7.3484 | 7.3918 | 8.4002 | 8.1566 | 15.9398 | 15.5128 | 15.3577 | 14.2819 | 14.1914 | 14.1521 |  |  |  | 13.6664 | 69.2491 | 53.0173 | 16.2855 | -0.068227 | -0.20022 | 18.7091 |  |  | 10.6557 |  |  | 16.8667 | 16.0571 | 15.6167 | 16.3525 | 15.6217 | 14.866 | 57.2131 | 69.8174 | 43.2298 | 44.205 | 21.7063 |  | 13.8544 | 26.8858 | 14.5233 | 16.2392 | 14.5356 | 52.3381 |  | 22.0049 |  |  | 12.1511 | 13.2784 | 19.4924 | [6 empty] | 16.7694 |  |  | 15.9978 |  |  | 11.017 | 15.6944 | 80.5242 | 7.9909 | 12.8465 | 51.5629 | 8.7262 | 12.1046 | 56.4607 | 12.4107 | 43.4107 | 8.7196 | 37.7635 | 9.3492 | 37.932 | 8.5771 | 13.9831 | 51.1214 | 12.5747 | 14.2873 | 68.2803 | 9.1197 | 13.0831 | 57.2532 | 9.3107 | 37.6763 | 11.9033 | 37.5131 | 9.8731 | 38.4955 | 0.21474 | 20.4142 | 0.34863 | 0.054283 | -37.7372 | 3.1212 | 66.61 | 49.49 | -0.29892 | -0.55395 | -0.14691 | -0.3245 | 0.26973 | -0.30619 | 0.64447 | 0.16661 | 0.044911 | 0.34106 | -0.3488 | 0.41525 | 0.18434 | 0.31095
42810.4418 | 150 | 18.6082 | 18.6332 | 18.5999 | 18.6056 | 17.9138 | 16.5187 | 14.5706 | 16.6732 | 17.1729 | 17.2764 | 17.2858 | 16.813 | 15.8482 | 14.4709 | 15.0182 | 14.9659 | 15.5012 | 13.3483 | 13.479 | 14.0535 |  |  |  | 16.5731 | 15.8952 | 15.3209 | 60.7461 | 60.1089 | 74.178 | 17.2961 | 16.3807 | 15.3265 | 16.879 | 16.1444 | 15.3399 | 13.9306 | 64.184 |  | 25.8267 | 49.1759 | 53.2319 | 21.4126 |  | 6.4381 | 6.4835 | 5.9179 | 6.0628 | 6.1623 | 7.3998 | 21.3294 | 4.6281 | 6.4051 | 4.5542 | 6.7685 | 8.1871 | 42.2637 | 47.0359 | 43.0641 | 14.966 |  |  | -0.32768 | 0.042799 | 0.03602 | 0.16888 | -0.041892 | -0.66218 | 0.023556 | 0.3284 | -0.18038 | -0.48649 | -0.2759 | 8.869 | 8.87 | 2.0055 | 15.8577 | 16.7056 | 17.2316 | 17.5436 | 17.4977 | 16.4655 | 14.8027 | 16.8286 | 17.1587 | 17.4658 | 17.5096 | 17.2329 | 16.4171 | 14.6211 | 14.846 | 9.3913 | 7.7351 | 7.3839 | 7.3007 | 8.4295 | 8.1659 | 15.9457 | 15.5148 | 15.355 | 14.2811 | 14.194 | 14.1554 |  |  |  | 13.6923 | 69.3225 | 53.2701 | 16.5125 | 0.017878 | -0.24746 | 18.7537 |  |  | 10.6622 |  |  | 16.8681 | 16.0567 | 15.6373 | 16.3556 | 15.6231 | 14.8729 | 57.3695 | 70.0377 | 43.3997 | 44.3424 | 20.4315 |  | 13.8883 | 26.179 | 14.5594 | 16.1599 | 14.58 | 52.1917 |  | 22.0789 |  |  | 12.1662 | 13.2835 | 19.3708 | [6 empty] | 16.7213 |  |  | 16.033 |  |  | 11.0402 | 15.7213 | 80.6253 | 8.0073 | 12.8525 | 51.7332 | 8.7337 | 12.1485 | 56.5374 | 12.43 | 43.6827 | 8.6991 | 38.0056 | 9.3513 | 38.1162 | 8.604 | 14.0377 | 51.2062 | 12.5872 | 14.3076 | 68.4335 | 9.1359 | 13.1033 | 57.326 | 9.3406 | 37.8836 | 11.9318 | 37.8113 | 9.8833 | 38.7608 | -0.043155 | 20.4123 | 0.35187 | 0.05416 | -37.7228 | 3.1211 | 50.44 | 49.85 | -0.74347 | 0.24109 | 0.22117 | 0.4789 | -0.23891 | -0.94986 | 0.17915 | 0.20314 | 0.06574 | 0.34473 | -0.35651 | 0.40298 | 0.17729 | 0.30551
42810.4418 | 151 | 18.6134 | 18.6344 | 18.6006 | 18.6053 | 17.917 | 16.5208 | 14.5708 | 16.6728 | 17.173 | 17.2739 | 17.284 | 16.8146 | 15.847 | 14.4707 | 15.0248 | 14.963 | 15.5011 | 13.3482 | 13.4815 | 14.0564 |  |  |  | 16.5673 | 15.8936 | 15.3205 | 60.9479 | 60.1698 | 73.9473 | 17.3017 | 16.3718 | 15.3168 | 16.8796 | 16.1427 | 15.3413 | 13.9974 | 63.5895 |  | 25.9134 | 49.3081 | 53.319 | 21.5654 |  | 6.435 | 6.4611 | 5.9072 | 6.0565 | 6.152 | 7.3752 | 21.6428 | 4.5375 | 6.4055 | 4.619 | 6.7679 | 8.1821 | 42.2779 | 47.0319 | 43.0451 | 14.9713 |  |  | -0.38945 | 0.13677 | 0.02748 | -0.12288 | 0.05996 | -0.19037 | 0.34423 | 0.29948 | -0.78228 | -0.33103 | -0.33293 | 8.8688 | 8.8699 | 2.0062 | 15.8527 | 16.6986 | 17.2179 | 17.5425 | 17.484 | 16.4633 | 14.8 | 16.8182 | 17.156 | 17.4622 | 17.5072 | 17.2318 | 16.4116 | 14.6172 | 14.1455 | 9.2316 | 7.6924 | 7.4171 | 7.2657 | 8.4469 | 8.167 | 15.9479 | 15.518 | 15.3579 | 14.2805 | 14.189 | 14.1557 |  |  |  | 13.7315 | 69.3967 | 53.3165 | 17.4154 | -0.12637 | -0.12456 | 18.6894 |  |  | 10.67 |  |  | 16.8757 | 16.0597 | 15.6556 | 16.3575 | 15.6339 | 14.8797 | 57.5621 | 70.1658 | 43.5471 | 44.4654 | 19.842 |  | 13.9227 | 25.3616 | 14.5826 | 16.077 | 14.5988 | 52.0698 |  | 22.1438 |  |  | 12.1829 | 13.2885 | 19.3103 | [6 empty] | 16.7156 |  |  | 16.0432 |  |  | 11.0483 | 15.7369 | 80.61 | 8.0099 | 12.8512 | 51.8737 | 8.7468 | 12.1576 | 56.621 | 12.4497 | 43.9137 | 8.6808 | 38.1907 | 9.352 | 38.3204 | 8.5996 | 14.0405 | 51.2471 | 12.5934 | 14.3133 | 68.6916 | 9.1396 | 13.1104 | 57.3748 | 9.3627 | 38.0493 | 11.9457 | 38.0219 | 9.8848 | 38.9236 | 0.13789 | 20.4064 | 0.35546 | 0.055195 | -37.649 | 3.1211 | 59.06 | 48.87 | -0.81025 | 0.43096 | 0.19318 | -0.4085 | 0.28581 | -0.50927 | 0.68482 | 0.22066 | 0.089217 | 0.34766 | -0.27665 | 0.40785 | 0.17526 | 0.28172
42810.4418 | 152 | 18.6147 | 18.63 | 18.5966 | 18.606 | 17.9172 | 16.5227 | 14.574 | 16.6736 | 17.1794 | 17.2761 | 17.2853 | 16.8181 | 15.8584 | 14.4667 | 15.0214 | 14.9602 | 15.5024 | 13.3466 | 13.4754 | 14.0493 |  |  |  | 16.5696 | 15.886 | 15.3202 | 61.1192 | 60.295 | 74.1579 | 17.3023 | 16.376 | 15.3244 | 16.8833 | 16.1464 | 15.3522 | 14.0651 | 63.1554 |  | 25.9924 | 49.4246 | 53.4215 | 21.4742 |  | 6.4265 | 6.4616 | 5.9063 | 6.0597 | 6.1554 | 7.3631 | 22.2514 | 4.4683 | 6.3976 | 4.5882 | 6.7721 | 8.1808 | 42.2902 | 47.0225 | 43.035 | 14.9774 |  |  | -0.12989 | -0.22333 | -0.056632 | -0.31673 | 0.057332 | 0.011368 | 0.021584 | 0.096432 | -0.28877 | -0.40278 | -0.32896 | 8.8717 | 8.8728 | 2.0064 | 15.8568 | 16.697 | 17.2184 | 17.529 | 17.4907 | 16.448 | 14.7964 | 16.8223 | 17.1573 | 17.4574 | 17.4973 | 17.2283 | 16.407 | 14.609 | 13.1608 | 9.0436 | 7.4918 | 7.3306 | 7.3014 | 8.4402 | 8.1664 | 15.9404 | 15.5193 | 15.3571 | 14.2897 | 14.1968 | 14.1608 |  |  |  | 13.7713 | 69.5208 | 53.3123 | 17.8078 | -0.023655 | -0.065092 | 18.604 |  |  | 10.6665 |  |  | 16.8724 | 16.0587 | 15.663 | 16.3569 | 15.6316 | 14.8839 | 57.7681 | 70.3037 | 43.6724 | 44.5918 | 20.6358 |  | 13.9665 | 24.7271 | 14.6046 | 16.0445 | 14.6304 | 51.6824 |  | 22.2372 |  |  | 12.1898 | 13.3066 | 19.3861 | [6 empty] | 16.7756 |  |  | 16.0279 |  |  | 11.0562 | 15.752 | 80.5774 | 8.0053 | 12.8509 | 51.9765 | 8.756 | 12.1673 | 56.7595 | 12.4642 | 44.2026 | 8.677 | 38.3001 | 9.3407 | 38.5124 | 8.6034 | 14.0227 | 51.2483 | 12.6001 | 14.3243 | 68.8133 | 9.1473 | 13.1215 | 57.3987 | 9.372 | 38.2097 | 11.9602 | 38.3079 | 9.9022 | 39.1153 | 0.061042 | 20.4021 | 0.35693 | 0.053726 | -37.6868 | 3.1211 | 64.36 | 49.55 | -0.46807 | -0.55071 | -0.27732 | -0.65583 | 0.27947 | 0.12445 | 0.17148 | 0.20005 | 0.10757 | 0.34961 | -0.16802 | 0.43007 | 0.18003 | 0.27214
42810.4418 | 153 | 18.6192 | 18.6291 | 18.5969 | 18.6081 | 17.9221 | 16.5217 | 14.5798 | 16.6782 | 17.1839 | 17.2781 | 17.2871 | 16.8286 | 15.8587 | 14.4671 | 15.028 | 14.9701 | 15.5053 | 13.3501 | 13.4811 | 14.0508 |  |  |  | 16.5715 | 15.8913 | 15.3405 | 61.4013 | 60.4317 | 74.5791 | 17.2966 | 16.3742 | 15.3316 | 16.8756 | 16.1482 | 15.3493 | 14.0985 | 63.0142 |  | 26.0855 | 49.5685 | 53.5307 | 21.1301 |  | 6.4341 | 6.4613 | 5.9095 | 6.0613 | 6.1594 | 7.3655 | 23.1123 | 4.3914 | 6.4045 | 4.4962 | 6.7857 | 8.1832 | 42.3235 | 47.0397 | 43.0254 | 14.986 |  |  | -0.14435 | -0.15236 | -0.067804 | 0.10843 | -0.08986 | -0.029372 | 0.20886 | 0.32051 | -0.33295 | -0.86371 | -0.37943 | 8.8692 | 8.8705 | 2.0067 | 15.8562 | 16.7024 | 17.2185 | 17.5426 | 17.4849 | 16.4503 | 14.8106 | 16.8233 | 17.1593 | 17.4604 | 17.5094 | 17.2329 | 16.4128 | 14.622 | 12.2703 | 8.9225 | 7.1525 | 7.2163 | 7.1941 | 8.4487 | 8.1642 | 15.9417 | 15.5187 | 15.3573 | 14.2821 | 14.194 | 14.1609 |  |  |  | 13.8012 | 69.6724 | 53.2828 | 17.8622 | 0.013218 | -0.09671 | 18.6098 |  |  | 10.6564 |  |  | 16.8635 | 16.049 | 15.6663 | 16.3427 | 15.6165 | 14.8803 | 57.9011 | 70.541 | 43.8031 | 44.729 | 21.3388 |  | 14.0227 | 24.3664 | 14.6486 | 16.084 | 14.6773 | 51.5993 |  | 22.3334 |  |  | 12.188 | 13.3138 | 19.4637 | [6 empty] | 16.8508 |  |  | 16.0102 |  |  | 11.0638 | 15.77 | 80.7556 | 8.0016 | 12.8384 | 52.1181 | 8.7528 | 12.1756 | 56.9001 | 12.4724 | 44.5024 | 8.6792 | 38.4265 | 9.3411 | 38.7065 | 8.6152 | 14.0185 | 51.2662 | 12.6075 | 14.3353 | 68.8454 | 9.1499 | 13.127 | 57.5116 | 9.3645 | 38.3536 | 11.9765 | 38.7555 | 9.9279 | 39.3623 | 0.026181 | 20.3988 | 0.35929 | 0.052358 | -37.6351 | 3.1211 | 83.01 | 49.44 | -0.49373 | -0.45486 | -0.30344 | 0.38372 | -0.34989 | -0.20004 | 0.53343 | 0.18239 | 0.11905 | 0.35007 | -0.068083 | 0.46751 | 0.1907 | 0.27163
42810.4418 | 154 | 18.6186 | 18.6339 | 18.6007 | 18.6039 | 17.9149 | 16.5169 | 14.5773 | 16.6784 | 17.1821 | 17.2809 | 17.2866 | 16.8187 | 15.8486 | 14.4752 | 15.0336 | 14.9681 | 15.511 | 13.3515 | 13.4756 | 14.0526 |  |  |  | 16.5689 | 15.8912 | 15.3481 | 61.71 | 60.5748 | 74.6327 | 17.3006 | 16.3814 | 15.3381 | 16.8828 | 16.148 | 15.3633 | 14.1369 | 63.276 |  | 26.174 | 49.7218 | 53.6636 | 20.7557 |  | 6.4284 | 6.4532 | 5.8995 | 6.0554 | 6.1606 | 7.4108 | 23.7441 | 4.3681 | 6.3984 | 4.4389 | 6.7848 | 8.1867 | 42.3506 | 47.0548 | 43.0082 | 14.9896 |  |  | -0.2554 | -0.11359 | 0.22856 | -0.27336 | 0.079676 | -0.46307 | -0.46205 | 0.2732 | -0.46761 | -1.2032 | -0.31723 | 8.8716 | 8.8724 | 2.0056 | 15.8638 | 16.7063 | 17.2279 | 17.5439 | 17.494 | 16.4605 | 14.8055 | 16.8218 | 17.164 | 17.4649 | 17.5088 | 17.2309 | 16.4182 | 14.626 | 11.5696 | 8.8249 | 6.8937 | 7.1419 | 7.0443 | 8.4477 | 8.1661 | 15.9559 | 15.5315 | 15.3683 | 14.2866 | 14.2059 | 14.1701 |  |  |  | 13.8422 | 69.7544 | 53.2223 | 17.868 | -0.06296 | -0.080525 | 18.71 |  |  | 10.6616 |  |  | 16.8593 | 16.0505 | 15.6828 | 16.344 | 15.6159 | 14.8856 | 58.0229 | 70.7485 | 43.9339 | 44.8717 | 21.3524 |  | 14.0626 | 23.6666 | 14.6756 | 16.0891 | 14.7146 | 51.8084 |  | 22.4177 |  |  | 12.1925 | 13.297 | 19.4591 | [6 empty] | 16.9107 |  |  | 15.9929 |  |  | 11.089 | 15.7965 | 80.9992 | 8.0083 | 12.849 | 52.2133 | 8.7671 | 12.1858 | 57.046 | 12.498 | 44.7312 | 8.6838 | 38.6096 | 9.359 | 38.8405 | 8.6375 | 14.0381 | 51.3178 | 12.6222 | 14.3461 | 69.0354 | 9.1597 | 13.1425 | 57.7079 | 9.3787 | 38.4916 | 12.0011 | 39.1191 | 9.9513 | 39.5808 | 0.13789 | 20.3949 | 0.36295 | 0.053863 | -37.5596 | 3.1212 | 66 | 48.81 | -0.65679 | -0.39275 | 0.5571 | -0.60927 | 0.32949 | -0.79433 | -0.79346 | 0.18334 | 0.13939 | 0.35117 | 0.0096482 | 0.49649 | 0.20238 | 0.27282
42810.4418 | 155 | 18.6156 | 18.6356 | 18.5973 | 18.6065 | 17.9174 | 16.5212 | 14.5707 | 16.6825 | 17.1808 | 17.2796 | 17.289 | 16.8222 | 15.8474 | 14.4719 | 15.0334 | 14.9677 | 15.5123 | 13.3504 | 13.4806 | 14.0636 |  |  |  | 16.5685 | 15.8949 | 15.3558 | 61.882 | 60.7528 | 74.1757 | 17.3057 | 16.3873 | 15.3436 | 16.8834 | 16.1492 | 15.3715 | 14.1725 | 63.5315 |  | 26.2679 | 49.8683 | 53.7941 | 20.4495 |  | 6.438 | 6.4628 | 5.8987 | 6.0623 | 6.1534 | 7.4739 | 23.9102 | 4.3837 | 6.4001 | 4.397 | 6.7807 | 8.1842 | 42.3709 | 47.064 | 43.0056 | 14.9854 |  |  | -0.047749 | -0.007141 | -0.026404 | -0.083454 | 0.03302 | -0.58398 | -0.17621 | -0.008048 | -0.19906 | -0.39858 | -0.25901 | 8.87 | 8.8711 | 2.0035 | 15.8568 | 16.7034 | 17.223 | 17.5383 | 17.4867 | 16.4527 | 14.7961 | 16.8167 | 17.1558 | 17.4529 | 17.4978 | 17.2257 | 16.4078 | 14.6126 | 10.8885 | 8.7622 | 6.7211 | 7.0285 | 7.026 | 8.4474 | 8.1627 | 15.9436 | 15.5184 | 15.3595 | 14.2806 | 14.1977 | 14.1647 |  |  |  | 13.8794 | 69.7663 | 53.2035 | 17.8969 | -0.1517 | -0.091064 | 18.6993 |  |  | 10.6757 |  |  | 16.8661 | 16.0521 | 15.6953 | 16.35 | 15.6198 | 14.8896 | 58.171 | 70.9428 | 44.0683 | 45.019 | 21.2968 |  | 14.1041 | 22.6644 | 14.6947 | 16.0415 | 14.75 | 51.6736 |  | 22.4963 |  |  | 12.2029 | 13.3047 | 19.4516 | [6 empty] | 16.8893 |  |  | 16.007 |  |  | 11.0915 | 15.8114 | 81.2249 | 8.0032 | 12.8491 | 52.3085 | 8.7827 | 12.1935 | 57.1919 | 12.5091 | 44.8805 | 8.6609 | 38.796 | 9.3633 | 38.9164 | 8.6371 | 14.0586 | 51.4033 | 12.6403 | 14.3705 | 69.2483 | 9.1762 | 13.1559 | 57.86 | 9.3948 | 38.6405 | 12.024 | 39.3385 | 9.9655 | 39.8298 | 0.22822 | 20.3902 | 0.36575 | 0.053487 | -37.6422 | 3.1212 | 71.08 | 50 | -0.2838 | -0.098475 | -0.18936 | -0.33664 | 0.21214 | -0.89213 | -0.49005 | 0.18626 | 0.16786 | 0.35366 | 0.085297 | 0.51527 | 0.21206 | 0.27325
42810.4418 | 156 | 18.6242 | 18.63 | 18.6061 | 18.6076 | 17.9216 | 16.5214 | 14.5764 | 16.6823 | 17.1857 | 17.2908 | 17.2913 | 16.8225 | 15.8478 | 14.4719 | 15.0252 | 14.9653 | 15.5133 | 13.3461 | 13.4847 | 14.0576 |  |  |  | 16.5734 | 15.8986 | 15.3659 | 61.9585 | 60.9477 | 73.7249 | 17.3074 | 16.3821 | 15.3473 | 16.882 | 16.1496 | 15.3725 | 14.2084 | 64.3315 |  | 26.3832 | 50.0129 | 53.969 | 20.0831 |  | 6.4323 | 6.4579 | 5.8921 | 6.0488 | 6.1355 | 7.4398 | 23.6685 | 4.4512 | 6.4006 | 4.3619 | 6.783 | 8.1862 | 42.3648 | 47.0709 | 42.9989 | 14.9789 |  |  | 0.060675 | -0.11885 | -0.19463 | 0.14588 | 0.019876 | -0.55835 | -0.32077 | 0.13717 | -0.6266 | -0.18794 | -0.36035 | 8.8699 | 8.8709 | 2.0042 | 15.8527 | 16.7026 | 17.2266 | 17.5387 | 17.49 | 16.4519 | 14.796 | 16.8122 | 17.1545 | 17.4526 | 17.495 | 17.2195 | 16.4053 | 14.609 | 10.1567 | 8.7106 | 6.6048 | 6.9479 | 7.0362 | 8.4444 | 8.1636 | 15.9525 | 15.5273 | 15.3728 | 14.2915 | 14.2106 | 14.1773 |  |  |  | 13.9181 | 69.9629 | 53.3306 | 18.022 | -0.013525 | -0.18968 | 18.6084 |  |  | 10.6833 |  |  | 16.8743 | 16.0565 | 15.7149 | 16.352 | 15.6243 | 14.8984 | 58.3409 | 71.1798 | 44.2201 | 45.1971 | 21.3691 |  | 14.1506 | 21.824 | 14.7139 | 16.2581 | 14.7928 | 52.0259 |  | 22.5979 |  |  | 12.2225 | 13.3095 | 19.3667 | [6 empty] | 16.9373 |  |  | 16.0009 |  |  | 11.0974 | 15.8237 | 81.3161 | 8.0022 | 12.8549 | 52.4687 | 8.798 | 12.212 | 57.4434 | 12.5251 | 45.0466 | 8.645 | 38.9459 | 9.3844 | 39.0412 | 8.6188 | 14.0561 | 51.4844 | 12.6559 | 14.3834 | 69.3963 | 9.1754 | 13.1574 | 57.9362 | 9.3852 | 38.7548 | 12.0307 | 39.4599 | 9.9648 | 40.0843 | 0.080687 | 20.3862 | 0.36734 | 0.051287 | -37.6444 | 3.1212 | 57.17 | 49.39 | 0.31971 | -0.40173 | -0.5141 | 0.44508 | 0.16458 | -0.87228 | -0.66115 | 0.18579 | 0.19184 | 0.34907 | 0.16626 | 0.52829 | 0.22343 | 0.27106
42810.4419 | 157 | 18.6225 | 18.6396 | 18.6034 | 18.6096 | 17.91 | 16.5184 | 14.5806 | 16.6823 | 17.187 | 17.2779 | 17.2901 | 16.8232 | 15.8499 | 14.4719 | 15.0309 | 14.9758 | 15.526 | 13.3489 | 13.4912 | 14.0666 |  |  |  | 16.5752 | 15.8952 | 15.3798 | 61.9991 | 61.1584 | 73.4667 | 17.3189 | 16.3916 | 15.3607 | 16.8976 | 16.152 | 15.3866 | 14.2421 | 65.1083 |  | 26.5087 | 50.1806 | 54.1455 | 19.7579 |  | 6.4357 | 6.4568 | 5.8839 | 6.035 | 6.1203 | 7.3983 | 23.7966 | 4.5536 | 6.4009 | 4.36 | 6.7837 | 8.1874 | 42.3547 | 47.0769 | 43.0021 | 14.9683 |  |  | -0.2462 | -0.14317 | -0.032976 | -0.10579 | 0.12764 | -0.74629 | -0.12495 | -0.02382 | -1.1304 | -0.26116 | -0.22941 | 8.8709 | 8.872 | 2.0061 | 15.8564 | 16.7019 | 17.2268 | 17.5403 | 17.4896 | 16.4478 | 14.7997 | 16.8132 | 17.1562 | 17.4536 | 17.5026 | 17.223 | 16.4107 | 14.6146 | 9.5303 | 8.6288 | 6.5304 | 7.0277 | 6.9255 | 8.4364 | 8.1591 | 15.9545 | 15.5294 | 15.3692 | 14.2906 | 14.2095 | 14.1804 |  |  |  | 13.9586 | 70.1687 | 53.2974 | 18.1214 | -0.046347 | -0.15449 | 18.5212 |  |  | 10.6831 |  |  | 16.8783 | 16.061 | 15.7337 | 16.3514 | 15.6243 | 14.9048 | 58.4918 | 71.4208 | 44.361 | 45.3956 | 21.1206 |  | 14.187 | 21.2739 | 14.7342 | 16.8714 | 14.834 | 52.3517 |  | 22.6896 |  |  | 12.2521 | 13.33 | 19.2961 | [6 empty] | 17.1018 |  |  | 15.984 |  |  | 11.1071 | 15.8659 | 81.5695 | 8.0148 | 12.8695 | 52.6853 | 8.8038 | 12.2251 | 57.6691 | 12.5321 | 45.2662 | 8.6412 | 39.086 | 9.3954 | 39.112 | 8.5736 | 14.0433 | 51.5612 | 12.6712 | 14.4087 | 69.531 | 9.1809 | 13.1451 | 58.0981 | 9.3715 | 38.8407 | 12.039 | 39.6916 | 9.9637 | 40.2809 | 0.14868 | 20.3809 | 0.37102 | 0.052112 | -37.6571 | 3.1212 | 59.82 | 49 | -0.64378 | -0.44092 | -0.21161 | -0.37903 | 0.41703 | -1.0084 | -0.41261 | 0.1939 | 0.20779 | 0.3334 | 0.23493 | 0.53604 | 0.23358 | 0.26964
42810.4419 | 158 | 18.6257 | 18.6455 | 18.6102 | 18.6132 | 17.9228 | 16.5264 | 14.5827 | 16.6919 | 17.1853 | 17.2837 | 17.291 | 16.8228 | 15.8535 | 14.4775 | 15.0308 | 14.9733 | 15.5245 | 13.3599 | 13.4942 | 14.0612 |  |  |  | 16.5766 | 15.8962 | 15.3855 | 62.0929 | 61.2899 | 73.8575 | 17.3106 | 16.3838 | 15.3616 | 16.8892 | 16.1512 | 15.3858 | 14.2651 | 65.6858 |  | 26.6101 | 50.36 | 54.2459 | 19.3847 |  | 6.4246 | 6.4407 | 5.8716 | 6.0197 | 6.0975 | 7.345 | 24.3056 | 4.6724 | 6.3978 | 4.3687 | 6.7835 | 8.1903 | 42.3491 | 47.0642 | 42.9969 | 14.9677 |  |  | -0.12595 | -0.38301 | -0.009976 | 0.07031 | -0.01692 | -0.93225 | 0.001216 | -0.048132 | -0.68945 | 0.76581 | -0.24451 | 8.8701 | 8.8715 | 2.0067 | 15.8659 | 16.7009 | 17.2319 | 17.548 | 17.4939 | 16.4667 | 14.8092 | 16.8167 | 17.1665 | 17.4602 | 17.4999 | 17.2283 | 16.4206 | 14.6179 | 9.0767 | 8.6054 | 6.5879 | 6.9536 | 6.9878 | 8.4282 | 8.1575 | 15.9482 | 15.5231 | 15.3549 | 14.2834 | 14.2022 | 14.1773 |  |  |  | 13.9897 | 70.3235 | 53.3007 | 18.1804 | -0.13306 | -0.065657 | 18.4719 |  |  | 10.6766 |  |  | 16.8743 | 16.0582 | 15.7473 | 16.3487 | 15.622 | 14.9071 | 58.6933 | 71.7313 | 44.4746 | 45.556 | 20.6807 |  | 14.2114 | 20.6925 | 14.756 | 17.3231 | 14.8618 | 52.5836 |  | 22.7806 |  |  | 12.286 | 13.3378 | 19.1763 | [6 empty] | 17.2534 |  |  | 15.995 |  |  | 11.12 | 15.903 | 81.9191 | 8.0263 | 12.8599 | 52.8933 | 8.7911 | 12.2327 | 57.8264 | 12.5408 | 45.4497 | 8.6783 | 39.2832 | 9.4095 | 39.2315 | 8.5875 | 14.0523 | 51.7095 | 12.6889 | 14.4415 | 69.6971 | 9.1885 | 13.156 | 58.2346 | 9.3805 | 39.0159 | 12.0543 | 39.9641 | 9.9911 | 40.4376 | 0.067398 | 20.3771 | 0.37399 | 0.052691 | -37.6676 | 3.1212 | 59.92 | 50.47 | -0.46072 | -0.72116 | -0.11639 | 0.30898 | -0.15182 | -1.1269 | 0.0407 | 0.20693 | 0.22467 | 0.32178 | 0.28438 | 0.52946 | 0.24471 | 0.26903
42810.4419 | 159 | 18.6286 | 18.6529 | 18.6123 | 18.6166 | 17.9233 | 16.5369 | 14.5887 | 16.6866 | 17.1871 | 17.2889 | 17.2923 | 16.8244 | 15.8537 | 14.4797 | 15.0321 | 14.9724 | 15.5103 | 13.3592 | 13.4887 | 14.0657 |  |  |  | 16.5779 | 15.894 | 15.3879 | 62.2648 | 61.4283 | 74.1535 | 17.2968 | 16.3782 | 15.353 | 16.8763 | 16.1376 | 15.3832 | 14.2889 | 66.0452 |  | 26.7161 | 50.5335 | 54.3356 | 19.1503 |  | 6.4193 | 6.4405 | 5.8692 | 6.0105 | 6.087 | 7.3119 | 24.6491 | 4.7599 | 6.3984 | 4.4159 | 6.7807 | 8.1909 | 42.3481 | 47.0639 | 42.9996 | 14.9562 |  |  | -0.13909 | 0.030971 | 0.012364 | -0.011826 | 0.026448 | -0.25608 | 0.078756 | 0.00772 | -0.42071 | 0.11333 | -0.109 | 8.8698 | 8.8708 | 2.0069 | 15.8688 | 16.7104 | 17.2357 | 17.5552 | 17.5056 | 16.4559 | 14.8061 | 16.832 | 17.1666 | 17.4677 | 17.5038 | 17.2289 | 16.4164 | 14.6223 | 8.699 | 8.548 | 6.6166 | 6.9537 | 6.9088 | 8.4297 | 8.1578 | 15.9486 | 15.5223 | 15.3561 | 14.2792 | 14.2066 | 14.1801 |  |  |  | 14.0234 | 70.4817 | 53.4094 | 18.1188 | 0.046444 | -0.019924 | 18.497 |  |  | 10.6647 |  |  | 16.8774 | 16.0521 | 15.7548 | 16.3565 | 15.6262 | 14.9097 | 58.9195 | 71.9519 | 44.6065 | 45.6857 | 20.2527 |  | 14.2469 | 19.9941 | 14.7806 | 17.3425 | 14.9176 | 52.7068 |  | 22.9093 |  |  | 12.306 | 13.3513 | 18.9921 | [6 empty] | 17.3073 |  |  | 16.0162 |  |  | 11.1262 | 15.9227 | 82.2501 | 7.9986 | 12.8814 | 53.1085 | 8.7736 | 12.2467 | 57.9187 | 12.5521 | 45.5871 | 8.6823 | 39.4972 | 9.4126 | 39.4172 | 8.5963 | 14.095 | 51.8327 | 12.6936 | 14.4394 | 70.032 | 9.1905 | 13.1616 | 58.3487 | 9.3853 | 39.1992 | 12.0491 | 40.1219 | 10.0036 | 40.5884 | 0.21108 | 20.374 | 0.37516 | 0.050266 | -37.6962 | 3.1212 | 48.23 | 49.06 | -0.48436 | 0.20507 | 0.12957 | -0.12672 | 0.1898 | -0.59059 | 0.32753 | 0.22 | 0.24488 | 0.32309 | 0.32652 | 0.5263 | 0.25201 | 0.27186
42810.4419 | 160 | 18.6297 | 18.6436 | 18.6086 | 18.6084 | 17.9193 | 16.5313 | 14.5813 | 16.682 | 17.1826 | 17.2813 | 17.2874 | 16.8155 | 15.8522 | 14.4711 | 15.0289 | 14.9711 | 15.5092 | 13.3492 | 13.4841 | 14.064 |  |  |  | 16.5661 | 15.8954 | 15.4032 | 62.3692 | 61.5664 | 74.5123 | 17.3085 | 16.3866 | 15.3661 | 16.8825 | 16.145 | 15.4001 | 14.3317 | 65.9694 |  | 26.8197 | 50.7183 | 54.4412 | 19.1305 |  | 6.4077 | 6.4398 | 5.87 | 6.006 | 6.0794 | 7.2975 | 24.9439 | 4.7205 | 6.4068 | 4.4634 | 6.7864 | 8.1851 | 42.3376 | 47.0496 | 42.989 | 14.9436 |  |  | 0.040303 | -0.22727 | 0.19636 | -0.054542 | -0.089204 | -0.30076 | 0.084012 | 0.01692 | -0.38549 | 0.16116 | -0.3526 | 8.8681 | 8.8691 | 2.0074 | 15.8595 | 16.7035 | 17.2318 | 17.5465 | 17.4976 | 16.4544 | 14.8066 | 16.8284 | 17.157 | 17.4699 | 17.5076 | 17.2317 | 16.4157 | 14.6163 | 8.4306 | 8.5415 | 6.5268 | 7.0008 | 6.8372 | 8.423 | 8.1565 | 15.9594 | 15.5212 | 15.3617 | 14.2907 | 14.2088 | 14.1891 |  |  |  | 14.0626 | 70.7667 | 53.4969 | 17.953 | 0.071769 | -0.020489 | 18.5584 |  |  | 10.652 |  |  | 16.8721 | 16.0546 | 15.7564 | 16.3518 | 15.6224 | 14.9098 | 59.1311 | 72.0763 | 44.7474 | 45.8016 | 20.1224 |  | 14.2712 | 19.4198 | 14.8101 | 17.3018 | 14.9386 | 53.0509 |  | 23.0057 |  |  | 12.3064 | 13.355 | 18.8946 | [6 empty] | 17.28 |  |  | 16.0284 |  |  | 11.1327 | 15.931 | 82.2272 | 7.9767 | 12.8879 | 53.2486 | 8.7611 | 12.2514 | 57.9655 | 12.5575 | 45.8079 | 8.6786 | 39.7027 | 9.4166 | 39.6117 | 8.5563 | 14.1272 | 51.9165 | 12.6915 | 14.4355 | 70.2744 | 9.1966 | 13.1751 | 58.5509 | 9.3486 | 39.3058 | 12.0486 | 40.2688 | 10.0036 | 40.8087 | 0.2028 | 20.3689 | 0.37945 | 0.053306 | -37.6195 | 3.1212 | 48.81 | 49.18 | 0.26086 | -0.55552 | 0.51636 | -0.27214 | -0.34857 | -0.64003 | 0.33827 | 0.22442 | 0.26182 | 0.32492 | 0.35556 | 0.53614 | 0.25398 | 0.27776
42810.4419 | 161 | 18.6291 | 18.6401 | 18.6093 | 18.612 | 17.9192 | 16.5234 | 14.5796 | 16.6856 | 17.1817 | 17.2751 | 17.2911 | 16.8187 | 15.8568 | 14.4716 | 15.0319 | 14.9842 | 15.5159 | 13.3584 | 13.4919 | 14.0709 |  |  |  | 16.5763 | 15.8998 | 15.4097 | 62.5233 | 61.7965 | 74.4267 | 17.3114 | 16.3895 | 15.3785 | 16.8877 | 16.1571 | 15.4125 | 14.3767 | 66.1452 |  | 26.9307 | 50.9237 | 54.5296 | 19.0053 |  | 6.4232 | 6.4486 | 5.8717 | 6.013 | 6.0774 | 7.2869 | 25.1653 | 4.7064 | 6.4187 | 4.5471 | 6.7966 | 8.1865 | 42.3488 | 47.0523 | 42.9847 | 14.9364 |  |  | -0.11346 | -0.12345 | 0.09056 | 0.17019 | -0.18252 | -0.37633 | 0.34883 | -0.080332 | -0.87393 | 0.0027646 | -0.18689 | 8.8729 | 8.8738 | 2.0072 | 15.868 | 16.711 | 17.235 | 17.5498 | 17.5025 | 16.463 | 14.8109 | 16.824 | 17.1681 | 17.4682 | 17.5048 | 17.2266 | 16.4207 | 14.6158 | 8.8512 | 8.5498 | 6.3329 | 6.9717 | 6.8528 | 8.4321 | 8.1491 | 15.9549 | 15.5277 | 15.3644 | 14.2896 | 14.2168 | 14.1909 |  |  |  | 14.0865 | 70.9132 | 53.6658 | 17.8025 | 0.098512 | -0.0012926 | 18.5921 |  |  | 10.65 |  |  | 16.8723 | 16.0589 | 15.7748 | 16.3545 | 15.622 | 14.9159 | 59.3419 | 72.2427 | 44.9279 | 45.9628 | 19.9864 |  | 14.3178 | 18.8005 | 14.8533 | 17.3024 | 14.9823 | 52.9829 |  | 23.1211 |  |  | 12.3266 | 13.3544 | 19.0076 | [6 empty] | 17.1647 |  |  | 16.0131 |  |  | 11.1267 | 15.9352 | 82.1873 | 7.9656 | 12.8928 | 53.4511 | 8.7523 | 12.2666 | 58.165 | 12.5504 | 45.9608 | 8.6499 | 39.8135 | 9.4185 | 39.8156 | 8.5447 | 14.1313 | 52.0199 | 12.7061 | 14.4591 | 70.4954 | 9.2196 | 13.2043 | 58.6723 | 9.3261 | 39.3571 | 12.038 | 40.391 | 10.0139 | 40.9913 | 0.17853 | 20.3654 | 0.38205 | 0.05374 | -37.6685 | 3.1212 | 42.32 | 50.11 | -0.43764 | -0.40943 | 0.35067 | 0.48074 | -0.49858 | -0.71593 | 0.68927 | 0.22974 | 0.28046 | 0.32635 | 0.30989 | 0.55681 | 0.25895 | 0.28274
42810.4419 | 162 | 18.6174 | 18.6465 | 18.597 | 18.6077 | 17.9122 | 16.5262 | 14.5786 | 16.6785 | 17.177 | 17.2694 | 17.2923 | 16.8168 | 15.8459 | 14.4682 | 15.0311 | 14.9745 | 15.515 | 13.3521 | 13.4868 | 14.0692 |  |  |  | 16.5694 | 15.8952 | 15.4102 | 62.6024 | 62.0441 | 74.3445 | 17.3064 | 16.3925 | 15.3833 | 16.8838 | 16.1555 | 15.4207 | 14.4072 | 66.436 |  | 27.0343 | 51.1192 | 54.621 | 18.8725 |  | 6.4181 | 6.4563 | 5.8729 | 6.0032 | 6.0605 | 7.2633 | 25.476 | 4.6861 | 6.4087 | 4.5306 | 6.7997 | 8.1867 | 42.3496 | 47.0453 | 42.9726 | 14.9245 |  |  | -0.20546 | -0.027509 | 0.22658 | 0.25759 | -0.037292 | -0.15685 | 0.31072 | 0.066204 | 0.95356 | -0.429 | -0.26219 | 8.8679 | 8.8694 | 2.0068 | 15.8655 | 16.7084 | 17.2293 | 17.5393 | 17.4953 | 16.4536 | 14.8031 | 16.8194 | 17.1613 | 17.4579 | 17.5017 | 17.2276 | 16.4077 | 14.6183 | 9.7267 | 8.9189 | 6.2022 | 6.8806 | 6.8976 | 8.4504 | 8.1438 | 15.942 | 15.5237 | 15.3558 | 14.2845 | 14.1959 | 14.1779 |  |  |  | 14.1112 | 70.9213 | 53.8257 | 17.6401 | 0.07258 | -0.15317 | 18.5856 |  |  | 10.6509 |  |  | 16.8735 | 16.061 | 15.7994 | 16.3639 | 15.6277 | 14.9277 | 59.6135 | 72.4388 | 45.1188 | 46.1404 | 19.5974 |  | 14.3484 | 19.1031 | 14.8947 | 17.134 | 15.0091 | 53.5975 |  | 23.2282 |  |  | 12.3544 | 13.3576 | 18.8866 | [6 empty] | 17.0686 |  |  | 16.014 |  |  | 11.1231 | 15.9532 | 82.2343 | 7.943 | 12.8945 | 53.645 | 8.7512 | 12.2846 | 58.4015 | 12.5582 | 46.1715 | 8.6603 | 39.9056 | 9.4312 | 39.9804 | 8.5468 | 14.1177 | 52.1662 | 12.7232 | 14.5008 | 70.7039 | 9.2313 | 13.2085 | 58.8053 | 9.324 | 39.4563 | 12.0445 | 40.605 | 10.021 | 41.1966 | 0.07568 | 20.3626 | 0.38331 | 0.051815 | -37.7093 | 3.1212 | 47.21 | 49.18 | -0.58885 | -0.19328 | 0.5547 | 0.59143 | -0.22536 | -0.46218 | 0.6505 | 0.24156 | 0.27342 | 0.33192 | 0.21474 | 0.57073 | 0.26365 | 0.28807
42810.4419 | 163 | 18.6119 | 18.6349 | 18.5998 | 18.6039 | 17.9113 | 16.5195 | 14.57 | 16.6727 | 17.1773 | 17.272 | 17.2836 | 16.8076 | 15.834 | 14.4652 | 15.0271 | 14.9786 | 15.5182 | 13.3533 | 13.4932 | 14.0687 |  |  |  | 16.5745 | 15.895 | 15.4237 | 62.7004 | 62.2239 | 74.0012 | 17.3008 | 16.3741 | 15.38 | 16.878 | 16.1446 | 15.4091 | 14.4322 | 66.6473 |  | 27.1304 | 51.3236 | 54.7097 | 20.2004 |  | 6.4209 | 6.4624 | 5.8711 | 6.0034 | 6.0515 | 7.242 | 25.6547 | 4.6866 | 6.4019 | 4.4572 | 6.7985 | 8.1852 | 42.3522 | 47.0399 | 42.9792 | 14.9292 |  |  | -0.23766 | -0.26078 | 0.052448 | -0.000658 | -0.095776 | -0.12662 | 0.63862 | 0.03072 | -0.39191 | -0.47054 | -0.23994 | 8.8722 | 8.8731 | 2.0071 | 15.8663 | 16.7044 | 17.229 | 17.5351 | 17.4911 | 16.4511 | 14.8015 | 16.816 | 17.1628 | 17.4583 | 17.4992 | 17.2273 | 16.4084 | 14.6145 | 10.5405 | 9.3615 | 6.5477 | 6.7982 | 6.8113 | 8.4742 | 8.1476 | 15.9497 | 15.5224 | 15.3653 | 14.2875 | 14.2005 | 14.1877 |  |  |  | 14.1477 | 70.971 | 53.897 | 17.4671 | -0.060326 | -0.24614 | 18.6414 |  |  | 10.6514 |  |  | 16.8731 | 16.0598 | 15.8085 | 16.3554 | 15.6248 | 14.9287 | 59.8716 | 72.5829 | 45.315 | 46.3031 | 19.2615 |  | 14.3674 | 20.4081 | 14.9492 | 17.0395 | 15.038 | 53.343 |  | 23.3394 |  |  | 12.3655 | 13.3809 | 18.7709 | [6 empty] | 16.996 |  |  | 16.0147 |  |  | 11.12 | 15.99 | 82.2288 | 7.9158 | 12.9141 | 53.772 | 8.7505 | 12.2954 | 58.6114 | 12.5669 | 46.3793 | 8.6721 | 40.0296 | 9.4452 | 40.1838 | 8.5414 | 14.1196 | 52.3255 | 12.7425 | 14.5331 | 70.8353 | 9.2344 | 13.2038 | 58.922 | 9.2915 | 39.6147 | 12.0426 | 40.7782 | 10.0274 | 41.3425 | 0.19317 | 20.3576 | 0.38756 | 0.053139 | -37.7015 | 3.1213 | 50.85 | 49.62 | -0.633 | -0.5951 | 0.26688 | -0.029892 | -0.36114 | -0.41525 | 0.93254 | 0.25152 | 0.23898 | 0.3355 | 0.12708 | 0.53278 | 0.22759 | 0.29408
42810.4419 | 164 | 18.6204 | 18.6469 | 18.6072 | 18.6094 | 17.915 | 16.5216 | 14.5762 | 16.6786 | 17.1756 | 17.2808 | 17.2899 | 16.8234 | 15.849 | 14.4668 | 15.0273 | 14.9768 | 15.5053 | 13.3519 | 13.4914 | 14.0673 |  |  |  | 16.5685 | 15.8898 | 15.4321 | 62.7865 | 62.3382 | 73.6017 | 17.3013 | 16.382 | 15.3867 | 16.8875 | 16.1519 | 15.4239 | 14.4596 | 66.9714 |  | 27.2375 | 51.5124 | 54.7775 | 20.1727 |  | 6.4305 | 6.4594 | 5.8726 | 6.0079 | 6.0617 | 7.2321 | 25.7971 | 4.6887 | 6.4028 | 4.4575 | 6.8045 | 8.1859 | 42.3488 | 47.0262 | 42.9783 | 14.9328 |  |  | -0.26197 | -0.080081 | 0.14379 | 0.017742 | -0.21866 | -0.26134 | 0.46448 | 0.19763 | -0.24635 | 1.0679 | -0.34207 | 8.8697 | 8.8708 | 2.0071 | 15.8651 | 16.7035 | 17.2258 | 17.5402 | 17.4932 | 16.4547 | 14.8025 | 16.8197 | 17.1635 | 17.4584 | 17.4965 | 17.2277 | 16.4112 | 14.6177 | 11.5387 | 9.4146 | 7.3207 | 7.1106 | 6.7104 | 8.5042 | 8.1527 | 15.96 | 15.5328 | 15.3721 | 14.2937 | 14.2158 | 14.2045 |  |  |  | 14.1786 | 71.1226 | 54.0386 | 17.3557 | -0.091729 | -0.055871 | 18.7201 |  |  | 10.6527 |  |  | 16.8647 | 16.0553 | 15.8146 | 16.3473 | 15.6186 | 14.9192 | 60.0429 | 72.6119 | 45.5169 | 46.4464 | 19.0456 |  | 14.4051 | 21.8425 | 15.006 | 17.0426 | 15.0671 | 53.2172 |  | 23.4165 |  |  | 12.3672 | 13.395 | 18.8224 | [6 empty] | 16.9631 |  |  | 16.0449 |  |  | 11.1283 | 16.0243 | 82.1688 | 7.9203 | 12.9335 | 53.9118 | 8.7486 | 12.3084 | 58.8245 | 12.587 | 46.5604 | 8.6463 | 40.2092 | 9.4533 | 40.3606 | 8.5385 | 14.2296 | 52.4492 | 12.7586 | 14.5659 | 70.976 | 9.2438 | 13.1908 | 59.0364 | 9.2729 | 39.7844 | 12.0444 | 40.9676 | 10.0379 | 41.479 | 0.37614 | 20.3542 | 0.39014 | 0.052864 | -37.7231 | 3.1213 | 49.73 | 49.53 | -0.6642 | -0.32977 | 0.44188 | 0.15522 | -0.54566 | -0.59654 | 0.79529 | 0.25877 | 0.20102 | 0.33638 | 0.019654 | 0.44748 | 0.22927 | 0.2982
42810.4419 | 165 | 18.6134 | 18.6361 | 18.5998 | 18.6037 | 17.9107 | 16.5162 | 14.5723 | 16.6814 | 17.177 | 17.2694 | 17.2797 | 16.812 | 15.8464 | 14.4608 | 15.0231 | 14.9705 | 15.5036 | 13.3597 | 13.494 | 14.0758 |  |  |  | 16.5711 | 15.8952 | 15.4433 | 62.8169 | 62.4198 | 73.2894 | 17.3045 | 16.3787 | 15.3976 | 16.8879 | 16.1554 | 15.433 | 14.4874 | 67.3118 |  | 27.3217 | 51.6697 | 54.8316 | 19.8362 |  | 6.4339 | 6.4645 | 5.8709 | 6.0194 | 6.0729 | 7.2341 | 25.6771 | 4.7006 | 6.4067 | 4.4774 | 6.8057 | 8.1874 | 42.3511 | 47.0123 | 42.9872 | 14.9418 |  |  | -0.013581 | -0.028825 | 0.060332 | -0.085426 | -0.14046 | -0.39867 | 0.34489 | 0.32971 | -0.25802 | -1.0565 | -0.10979 | 8.8699 | 8.871 | 2.0069 | 15.8634 | 16.7061 | 17.23 | 17.5449 | 17.5052 | 16.4521 | 14.8039 | 16.8105 | 17.1609 | 17.4621 | 17.5012 | 17.2263 | 16.4143 | 14.6143 | 12.756 | 9.5044 | 7.7663 | 7.3677 | 6.8364 | 8.544 | 8.163 | 15.9546 | 15.5301 | 15.3668 | 14.2899 | 14.216 | 14.194 |  |  |  | 14.2028 | 71.2131 | 54.2034 | 17.2531 | 0.0077476 | -0.15072 | 18.8153 |  |  | 10.6511 |  |  | 16.864 | 16.0527 | 15.8349 | 16.3497 | 15.6187 | 14.9251 | 60.2415 | 72.6244 | 45.6632 | 46.5572 | 18.9431 |  | 14.443 | 22.6936 | 15.0612 | 16.9939 | 15.0942 | 53.2611 |  | 23.4946 |  |  | 12.3367 | 13.387 | 18.7753 | [6 empty] | 16.9319 |  |  | 16.0799 |  |  | 11.134 | 16.0402 | 82.2777 | 7.9188 | 12.9349 | 54.0648 | 8.7469 | 12.3196 | 59.035 | 12.6126 | 46.6949 | 8.635 | 40.3728 | 9.4518 | 40.5145 | 8.5465 | 14.3838 | 52.5665 | 12.7742 | 14.5718 | 71.122 | 9.2502 | 13.1869 | 59.0903 | 9.2719 | 39.9495 | 12.0434 | 41.0848 | 10.0498 | 41.6186 | 0.239 | 20.3487 | 0.39124 | 0.051764 | -37.7279 | 3.1213 | 45.68 | 49.14 | -0.15116 | -0.19785 | 0.28623 | -0.3406 | -0.43734 | -0.7368 | 0.6853 | 0.26287 | 0.17922 | 0.33863 | -0.11098 | 0.39917 | 0.23954 | 0.30185
42810.442 | 166 | 18.613 | 18.6402 | 18.5981 | 18.6031 | 17.9108 | 16.5124 | 14.575 | 16.6769 | 17.1729 | 17.2722 | 17.2805 | 16.8073 | 15.8472 | 14.4572 | 15.0243 | 14.9693 | 15.5048 | 13.3562 | 13.4879 | 14.0747 |  |  |  | 16.5705 | 15.8924 | 15.4462 | 62.8472 | 62.5627 | 72.9341 | 17.3052 | 16.3864 | 15.3961 | 16.8866 | 16.1566 | 15.4431 | 14.5177 | 67.4996 |  | 27.4015 | 51.8167 | 54.9129 | 19.5324 |  | 6.4264 | 6.4472 | 5.8693 | 6.0139 | 6.0508 | 7.2258 | 25.5698 | 4.778 | 6.4018 | 4.4938 | 6.7944 | 8.1906 | 42.3466 | 46.9999 | 42.987 | 14.9527 |  |  | -0.26328 | -0.22596 | 0.11553 | 0.036798 | -0.08986 | -0.41576 | 0.3508 | 0.12206 | 0.42599 | -0.19487 | -0.41082 | 8.8692 | 8.8702 | 2.0072 | 15.8582 | 16.6893 | 17.222 | 17.5376 | 17.4944 | 16.4397 | 14.8041 | 16.8246 | 17.1559 | 17.4553 | 17.4929 | 17.2195 | 16.4024 | 14.6097 | 13.8182 | 9.8176 | 7.839 | 7.5015 | 6.9924 | 8.5831 | 8.1713 | 15.9451 | 15.526 | 15.3639 | 14.2795 | 14.216 | 14.1875 |  |  |  | 14.2156 | 71.3322 | 54.5556 | 17.1772 | -0.025681 | -0.13209 | 18.965 |  |  | 10.6602 |  |  | 16.8715 | 16.0543 | 15.8611 | 16.3558 | 15.6237 | 14.9399 | 60.4606 | 72.6701 | 45.7884 | 46.6739 | 18.6886 |  | 14.493 | 22.2585 | 15.1208 | 16.9246 | 15.1294 | 53.0922 |  | 23.5895 |  |  | 12.3267 | 13.3855 | 18.7126 | [6 empty] | 16.9298 |  |  | 16.1179 |  |  | 11.1338 | 16.0584 | 82.354 | 7.9095 | 12.934 | 54.2139 | 8.7422 | 12.3401 | 59.1842 | 12.6284 | 46.7436 | 8.6288 | 40.4781 | 9.4539 | 40.678 | 8.557 | 14.5231 | 52.7133 | 12.772 | 14.5708 | 71.2159 | 9.2481 | 13.1858 | 59.1419 | 9.2621 | 40.0999 | 12.0323 | 41.0937 | 10.0631 | 41.835 | 0.22629 | 20.3456 | 0.39566 | 0.053074 | -37.7236 | 3.1213 | 39.75 | 50.35 | -0.66523 | -0.55392 | 0.39608 | 0.22353 | -0.3498 | -0.75241 | 0.69114 | 0.2716 | 0.19328 | 0.34173 | -0.22446 | 0.39205 | 0.24898 | 0.30439
42810.442 | 167 | 18.6101 | 18.6327 | 18.5993 | 18.5962 | 17.9005 | 16.5099 | 14.5653 | 16.6739 | 17.1689 | 17.2704 | 17.2765 | 16.8025 | 15.8425 | 14.4571 | 15.0247 | 14.9714 | 15.5097 | 13.3528 | 13.4915 | 14.077 |  |  |  | 16.5712 | 15.8906 | 15.4544 | 62.9281 | 62.7086 | 72.7432 | 17.3007 | 16.3831 | 15.3982 | 16.8868 | 16.1525 | 15.4387 | 14.5467 | 67.4876 |  | 27.5007 | 51.9429 | 55.0056 | 20.0665 |  | 6.4284 | 6.4413 | 5.874 | 6.0193 | 6.0548 | 7.2154 | 25.3738 | 4.7986 | 6.404 | 4.5346 | 6.8011 | 8.1898 | 42.3386 | 46.9749 | 42.9948 | 14.9673 |  |  | -0.25409 | -0.21807 | 0.07676 | -0.059798 | -0.10234 | -0.13714 | 0.49011 | 0.043864 | 0.01967 | -0.07654 | -0.22166 | 8.87 | 8.8712 | 2.0066 | 15.868 | 16.7138 | 17.229 | 17.543 | 17.4898 | 16.4577 | 14.8053 | 16.8112 | 17.1525 | 17.4617 | 17.5076 | 17.2322 | 16.4119 | 14.6196 | 14.3988 | 10.0477 | 8.9765 | 7.7269 | 7.1583 | 8.6228 | 8.1766 | 15.9547 | 15.5278 | 15.375 | 14.2914 | 14.2201 | 14.1894 |  |  |  | 14.2451 | 71.4892 | 55.0126 | 17.0739 | -0.044321 | -0.25292 | 19.1054 |  |  | 10.6711 |  |  | 16.8751 | 16.0561 | 15.8778 | 16.3554 | 15.6231 | 14.9442 | 60.5777 | 72.7367 | 45.9169 | 46.7829 | 18.5134 |  | 14.5431 | 21.4703 | 15.1917 | 16.8216 | 15.1536 | 53.0183 |  | 23.6805 |  |  | 12.3382 | 13.3852 | 18.9335 | [6 empty] | 16.8959 |  |  | 16.1565 |  |  | 11.1385 | 16.0866 | 82.5576 | 7.9093 | 12.9389 | 54.3394 | 8.7391 | 12.3561 | 59.2759 | 12.6446 | 46.8824 | 8.629 | 40.5948 | 9.4632 | 40.7909 | 8.5784 | 14.693 | 52.8799 | 12.7815 | 14.5964 | 71.2632 | 9.2672 | 13.2025 | 59.2882 | 9.2796 | 40.2896 | 12.0354 | 41.3442 | 10.083 | 42.0981 | 0.23323 | 20.3427 | 0.39857 | 0.053849 | -37.7223 | 3.1214 | 42.8 | 49.18 | -0.65332 | -0.54416 | 0.32285 | -0.28495 | -0.3733 | -0.43213 | 0.81691 | 0.27813 | 0.21753 | 0.34539 | -0.28435 | 0.26629 | 0.23511 | 0.30823
42810.442 | 168 | 18.6077 | 18.6281 | 18.6003 | 18.5985 | 17.9028 | 16.5089 | 14.5712 | 16.6751 | 17.1683 | 17.2747 | 17.2747 | 16.803 | 15.839 | 14.4541 | 15.0236 | 14.9749 | 15.5131 | 13.3558 | 13.4978 | 14.078 |  |  |  | 16.5714 | 15.8892 | 15.467 | 63.0564 | 62.89 | 73.3698 | 17.3049 | 16.3825 | 15.4131 | 16.89 | 16.151 | 15.4391 | 14.5876 | 67.5044 |  | 27.5909 | 52.0369 | 55.0766 | 22.3058 |  | 6.435 | 6.4424 | 5.8894 | 6.0314 | 6.0599 | 7.2002 | 25.0102 | 4.8174 | 6.416 | 4.583 | 6.8153 | 8.1888 | 42.3356 | 46.9534 | 43.0155 | 14.9715 |  |  | -0.068121 | 0.12494 | 0.080048 | 0.18399 | -0.16872 | -0.19825 | 0.40863 | -0.059304 | 0.16951 | -0.20179 | -0.15688 | 8.8685 | 8.8701 | 2.006 | 15.8624 | 16.6967 | 17.2189 | 17.5304 | 17.4878 | 16.4441 | 14.7915 | 16.812 | 17.1581 | 17.4558 | 17.4925 | 17.2272 | 16.4017 | 14.6087 | 14.1873 | 9.9341 | 9.4508 | 8.2437 | 7.3828 | 8.6457 | 8.1947 | 15.9572 | 15.5263 | 15.3748 | 14.2949 | 14.2144 | 14.2007 |  |  |  | 14.2658 | 71.6154 | 55.1403 | 16.9903 | 0.098512 | -0.13077 | 19.2252 |  |  | 10.6756 |  |  | 16.8781 | 16.0643 | 15.8833 | 16.353 | 15.6225 | 14.9478 | 60.6368 | 72.7876 | 46.0658 | 46.8845 | 18.2919 |  | 14.593 | 21.0861 | 15.25 | 16.7399 | 15.1774 | 53.7488 |  | 23.7786 |  |  | 12.3296 | 13.3974 | 19.1432 | [6 empty] | 16.8433 |  |  | 16.1873 |  |  | 11.1488 | 16.1222 | 82.8899 | 7.9131 | 12.9495 | 54.4088 | 8.7389 | 12.3843 | 59.3922 | 12.6679 | 47.0126 | 8.6394 | 40.7468 | 9.4689 | 40.908 | 8.5804 | 14.7981 | 53.0392 | 12.7896 | 14.6204 | 71.32 | 9.2763 | 13.2183 | 59.3748 | 9.2863 | 40.4683 | 12.04 | 41.7038 | 10.0959 | 42.2995 | 0.33935 | 20.3376 | 0.39978 | 0.051337 | -37.7505 | 3.1213 | 59.98 | 49.1 | -0.33859 | 0.41189 | 0.32969 | 0.49984 | -0.47929 | -0.51955 | 0.7459 | 0.28594 | 0.23014 | 0.34845 | -0.25819 | 0.21568 | 0.17426 | 0.31124
42810.442 | 169 | 18.6159 | 18.6323 | 18.6048 | 18.6007 | 17.9056 | 16.5096 | 14.5727 | 16.6714 | 17.1709 | 17.2716 | 17.2771 | 16.8075 | 15.8406 | 14.4592 | 15.0201 | 14.9649 | 15.5033 | 13.3488 | 13.4883 | 14.0654 |  |  |  | 16.5671 | 15.8857 | 15.4692 | 63.2227 | 63.0423 | 73.9837 | 17.2992 | 16.3784 | 15.4124 | 16.8862 | 16.1431 | 15.445 | 14.6473 | 67.4858 |  | 27.6715 | 52.1205 | 55.1521 | 23.906 |  | 6.4426 | 6.4554 | 5.8867 | 6.0274 | 6.0566 | 7.1666 | 24.6386 | 4.8187 | 6.4252 | 4.6788 | 6.8185 | 8.1839 | 42.3343 | 46.9358 | 43.0239 | 14.9629 |  |  | -0.26 | -0.14053 | 0.005136 | -0.2543 | -0.19631 | -0.43744 | 0.6787 | -0.47329 | -0.14204 | 0.24823 | -0.19086 | 8.8695 | 8.8704 | 2.0065 | 15.868 | 16.7026 | 17.2336 | 17.5405 | 17.4863 | 16.4472 | 14.7991 | 16.8201 | 17.1618 | 17.4635 | 17.4942 | 17.2256 | 16.41 | 14.6155 | 13.7634 | 9.7786 | 9.3506 | 8.481 | 7.7837 | 8.6589 | 8.1974 | 15.9592 | 15.5385 | 15.3769 | 14.3017 | 14.2203 | 14.2106 |  |  |  | 14.2841 | 71.7278 | 55.3194 | 16.9413 | 0.029831 | -0.17914 | 19.2918 |  |  | 10.667 |  |  | 16.8632 | 16.0514 | 15.8867 | 16.3433 | 15.6131 | 14.9472 | 60.6774 | 72.8172 | 46.2405 | 46.9988 | 17.506 |  | 14.6431 | 21.7368 | 15.3231 | 16.6828 | 15.217 | 54.3861 |  | 23.8877 |  |  | 12.3348 | 13.4191 | 19.1036 | [6 empty] | 16.7882 |  |  | 16.2232 |  |  | 11.1647 | 16.1614 | 82.9931 | 7.9416 | 13.0127 | 54.5231 | 8.7399 | 12.4177 | 59.5287 | 12.6875 | 46.9581 | 8.6541 | 40.9068 | 9.4627 | 41.1125 | 8.5808 | 14.8752 | 53.1752 | 12.7965 | 14.6262 | 71.3629 | 9.2825 | 13.2373 | 59.4409 | 9.2779 | 40.6144 | 12.0393 | 42.0323 | 10.1088 | 42.4632 | 0.18874 | 20.3332 | 0.40242 | 0.051714 | -37.7347 | 3.1214 | 32.24 | 50.19 | -0.66206 | -0.43685 | 0.083513 | -0.58764 | -0.51697 | -0.7717 | 0.96124 | 0.30944 | 0.21449 | 0.35135 | -0.20956 | 0.22713 | 0.1318 | 0.31321
42810.442 | 170 | 18.6291 | 18.6358 | 18.6041 | 18.6018 | 17.9078 | 16.5224 | 14.5751 | 16.6744 | 17.1736 | 17.2714 | 17.2824 | 16.816 | 15.8424 | 14.4581 | 15.0272 | 14.9755 | 15.5041 | 13.3509 | 13.4965 | 14.0755 |  |  |  | 16.5721 | 15.8926 | 15.4814 | 63.3789 | 63.1258 | 73.9212 | 17.3007 | 16.3862 | 15.4248 | 16.8901 | 16.1499 | 15.4563 | 14.7006 | 67.0363 |  | 27.7599 | 52.2078 | 55.2555 | 23.6026 |  | 6.454 | 6.4613 | 5.8851 | 6.0254 | 6.0624 | 7.147 | 24.3985 | 4.8383 | 6.4293 | 4.7652 | 6.8087 | 8.1818 | 42.3395 | 46.9089 | 43.0303 | 14.9722 |  |  | -0.20809 | -0.082053 | 0.00908 | -0.009858 | 0.040248 | -0.047116 | 0.38826 | -0.52651 | -0.22533 | -0.27984 | -0.035079 | 8.8679 | 8.869 | 2.0072 | 15.8683 | 16.7124 | 17.241 | 17.5423 | 17.4941 | 16.4596 | 14.8078 | 16.8284 | 17.162 | 17.4698 | 17.5078 | 17.2343 | 16.4156 | 14.6207 | 13.2959 | 9.6416 | 8.9296 | 8.5196 | 8.0479 | 8.679 | 8.199 | 15.9575 | 15.5267 | 15.3629 | 14.296 | 14.2144 | 14.2056 |  |  |  | 14.3081 | 71.8321 | 55.3809 | 16.9042 | -0.16507 | -0.23071 | 19.3113 |  |  | 10.6697 |  |  | 16.8601 | 16.043 | 15.899 | 16.341 | 15.6139 | 14.9548 | 60.728 | 73.0109 | 46.403 | 47.1225 | 17.5303 |  | 14.6882 | 22.4681 | 15.3746 | 16.6907 | 15.2378 | 54.5026 |  | 23.993 |  |  | 12.35 | 13.4089 | 19.212 | [6 empty] | 16.7289 |  |  | 16.2501 |  |  | 11.1812 | 16.1956 | 83.0231 | 7.9536 | 13.0515 | 54.6663 | 8.7372 | 12.4337 | 59.5637 | 12.697 | 47.0869 | 8.6556 | 41.0212 | 9.4557 | 41.3323 | 8.5974 | 14.9465 | 53.3016 | 12.8065 | 14.6298 | 71.5934 | 9.3019 | 13.2943 | 59.5398 | 9.2936 | 40.7511 | 12.052 | 42.2588 | 10.1237 | 42.6542 | 0.17294 | 20.3306 | 0.40523 | 0.052271 | -37.7658 | 3.1213 | 35.62 | 49.17 | -0.59224 | -0.3338 | 0.11104 | -0.1157 | 0.23407 | -0.25326 | 0.727 | 0.31026 | 0.19589 | 0.35182 | -0.15529 | 0.27409 | 0.14199 | 0.31504
42810.442 | 171 | 18.6213 | 18.6488 | 18.6169 | 18.607 | 17.9142 | 16.5233 | 14.5761 | 16.6863 | 17.1809 | 17.2798 | 17.285 | 16.8133 | 15.843 | 14.4742 | 15.0252 | 14.96 | 15.5004 | 13.3539 | 13.4998 | 14.0765 |  |  |  | 16.5742 | 15.8923 | 15.485 | 63.519 | 63.1976 | 73.7509 | 17.3016 | 16.3837 | 15.435 | 16.8861 | 16.1508 | 15.4636 | 14.7349 | 66.6533 |  | 27.8543 | 52.2891 | 55.3668 | 22.9115 |  | 6.4724 | 6.4654 | 5.9003 | 6.0329 | 6.0596 | 7.1339 | 24.244 | 4.868 | 6.4339 | 4.8192 | 6.8208 | 8.1854 | 42.3267 | 46.8931 | 43.039 | 14.9688 |  |  | -0.12595 | -0.12082 | 0.10765 | 0.009858 | -0.011664 | -0.38422 | 0.5867 | -0.44109 | -0.63749 | -0.43194 | -0.25822 | 8.8693 | 8.8703 | 2.0073 | 15.8693 | 16.7054 | 17.2378 | 17.5371 | 17.4916 | 16.4521 | 14.8048 | 16.826 | 17.1596 | 17.4645 | 17.507 | 17.2267 | 16.4121 | 14.6161 | 12.8243 | 9.8432 | 8.6576 | 8.4788 | 8.0219 | 8.6875 | 8.2039 | 15.964 | 15.5356 | 15.3731 | 14.3036 | 14.228 | 14.2185 |  |  |  | 14.3403 | 71.9652 | 55.6803 | 16.9509 | -0.15312 | -0.20831 | 19.3745 |  |  | 10.6819 |  |  | 16.8741 | 16.0592 | 15.9253 | 16.3523 | 15.6243 | 14.9726 | 60.8755 | 73.284 | 46.5428 | 47.2266 | 18.5562 |  | 14.7482 | 23.5177 | 15.4322 | 16.7122 | 15.2593 | 55.3685 |  | 24.0837 |  |  | 12.3607 | 13.4146 | 19.4474 | [6 empty] | 16.6999 |  |  | 16.2771 |  |  | 11.194 | 16.2177 | 83.1249 | 7.9691 | 13.0553 | 54.8004 | 8.7387 | 12.437 | 59.5997 | 12.7095 | 47.4252 | 8.654 | 41.118 | 9.4547 | 41.4965 | 8.5998 | 14.9914 | 53.4398 | 12.8114 | 14.6316 | 71.9293 | 9.3146 | 13.3552 | 59.6506 | 9.3208 | 40.8892 | 12.07 | 42.3962 | 10.1295 | 42.857 | 0.3902 | 20.3263 | 0.40727 | 0.052416 | -37.7672 | 3.1214 | 37.52 | 49.25 | -0.46065 | -0.40506 | 0.38234 | 0.1157 | -0.12601 | -0.72319 | 0.89367 | 0.28375 | 0.16865 | 0.35194 | -0.1019 | 0.30489 | 0.16233 | 0.31481
42810.442 | 172 | 18.614 | 18.6391 | 18.6048 | 18.6085 | 17.9136 | 16.5168 | 14.5721 | 16.668 | 17.1704 | 17.268 | 17.2856 | 16.8084 | 15.8333 | 14.4617 | 15.0271 | 14.9712 | 15.5096 | 13.3563 | 13.5012 | 14.0818 |  |  |  | 16.5743 | 15.9024 | 15.501 | 63.6325 | 63.2989 | 73.4943 | 17.3016 | 16.3734 | 15.429 | 16.8865 | 16.1483 | 15.468 | 14.7657 | 66.4409 |  | 27.9401 | 52.3649 | 55.4595 | 22.4436 |  | 6.4795 | 6.4832 | 5.9003 | 6.0429 | 6.0665 | 7.1277 | 24.0717 | 4.9148 | 6.4277 | 4.8367 | 6.8215 | 8.1826 | 42.313 | 46.8906 | 43.0629 | 14.9588 |  |  | -0.28629 | -0.078765 | 0.034708 | -0.17677 | -0.038604 | -0.0596 | 0.55582 | -0.45883 | -1.4976 | -0.3669 | -0.20596 | 8.8685 | 8.8692 | 2.0078 | 15.864 | 16.7073 | 17.2244 | 17.5395 | 17.4971 | 16.4524 | 14.7943 | 16.826 | 17.1568 | 17.4491 | 17.5045 | 17.2218 | 16.4065 | 14.6124 | 12.8709 | 10.1511 | 8.8746 | 8.3017 | 7.9689 | 8.7145 | 8.2257 | 15.9632 | 15.5427 | 15.3716 | 14.3015 | 14.2273 | 14.2147 |  |  |  | 14.3795 | 72.1284 | 55.9213 | 17.0011 | -0.14704 | -0.30317 | 19.4197 |  |  | 10.6882 |  |  | 16.8749 | 16.0586 | 15.9413 | 16.3531 | 15.6257 | 14.9739 | 61.0201 | 73.5257 | 46.6793 | 47.3201 | 19.854 |  | 14.8075 | 24.6845 | 15.4946 | 16.7379 | 15.294 | 55.6703 |  | 24.209 |  |  | 12.3527 | 13.3918 | 19.7353 | [6 empty] | 16.7795 |  |  | 16.2889 |  |  | 11.216 | 16.253 | 83.3256 | 7.9736 | 13.1343 | 54.9194 | 8.7265 | 12.4414 | 59.7095 | 12.7368 | 47.7839 | 8.675 | 41.1855 | 9.4793 | 41.6765 | 8.618 | 15.0444 | 53.5575 | 12.8186 | 14.6524 | 72.1392 | 9.3264 | 13.3695 | 59.8236 | 9.3368 | 41.0392 | 12.0788 | 42.5921 | 10.136 | 42.9946 | 0.19837 | 20.3231 | 0.40829 | 0.051851 | -37.7304 | 3.1214 | 48.76 | 49.9 | -0.69424 | -0.32706 | 0.21711 | -0.48996 | -0.22923 | -0.28483 | 0.86982 | 0.24967 | 0.13831 | 0.35238 | -0.10394 | 0.28331 | 0.17635 | 0.31471
42810.442 | 173 | 18.615 | 18.6436 | 18.6006 | 18.5979 | 17.9066 | 16.514 | 14.5777 | 16.6713 | 17.172 | 17.265 | 17.2869 | 16.8135 | 15.8384 | 14.4624 | 15.0279 | 14.971 | 15.5159 | 13.363 | 13.5041 | 14.0922 |  |  |  | 16.5828 | 15.9021 | 15.5091 | 63.8043 | 63.4131 | 73.664 | 17.2927 | 16.3774 | 15.4311 | 16.8876 | 16.144 | 15.4757 | 14.8047 | 66.266 |  | 28.018 | 52.4173 | 55.5533 | 22.5493 |  | 6.488 | 6.4875 | 5.9027 | 6.0473 | 6.077 | 7.1198 | 23.8778 | 4.928 | 6.4422 | 4.8298 | 6.8255 | 8.1809 | 42.3067 | 46.8913 | 43.0827 | 14.9553 |  |  | -0.13712 | -0.093221 | -0.00472 | -0.19319 | -0.21931 | -0.17854 | 0.48945 | -0.49629 | -0.84766 | -1.1161 | -0.28584 | 8.8701 | 8.8715 | 2.0068 | 15.8677 | 16.7116 | 17.2321 | 17.5485 | 17.494 | 16.4596 | 14.8029 | 16.823 | 17.1602 | 17.4591 | 17.5034 | 17.2277 | 16.4039 | 14.6128 | 13.554 | 10.2426 | 8.9844 | 8.1127 | 7.8928 | 8.7492 | 8.2284 | 15.9726 | 15.5425 | 15.3777 | 14.3123 | 14.2219 | 14.2237 |  |  |  | 14.4263 | 72.2429 | 55.9192 | 17.0186 | 0.13721 | -0.18479 | 19.4503 |  |  | 10.6956 |  |  | 16.8775 | 16.0548 | 15.9503 | 16.3563 | 15.6272 | 14.9735 | 61.163 | 73.721 | 46.8534 | 47.449 | 20.7861 |  | 14.8721 | 25.6986 | 15.5555 | 16.8392 | 15.3344 | 55.504 |  | 24.3179 |  |  | 12.3614 | 13.3985 | 20.1246 | [6 empty] | 16.9256 |  |  | 16.3224 |  |  | 11.2193 | 16.2633 | 83.3804 | 7.9936 | 13.2759 | 54.986 | 8.7226 | 12.4761 | 59.7886 | 12.7512 | 48.0528 | 8.6921 | 41.229 | 9.4879 | 41.8887 | 8.6265 | 15.0885 | 53.6052 | 12.8336 | 14.6682 | 72.1759 | 9.3383 | 13.3605 | 59.9107 | 9.3471 | 41.1508 | 12.0873 | 42.864 | 10.1581 | 43.1651 | 0.10688 | 20.3203 | 0.41209 | 0.054761 | -37.7454 | 3.1214 | 41.66 | 48.69 | -0.48057 | -0.35581 | -0.080064 | -0.51222 | -0.54637 | -0.49297 | 0.81623 | 0.22592 | 0.11216 | 0.35091 | -0.1758 | 0.27142 | 0.1747 | 0.31578
42810.442 | 174 | 18.6182 | 18.6386 | 18.5934 | 18.5922 | 17.909 | 16.5149 | 14.5699 | 16.6756 | 17.1758 | 17.2642 | 17.2789 | 16.8086 | 15.8343 | 14.4625 | 15.0186 | 14.9654 | 15.4963 | 13.3543 | 13.4897 | 14.0797 |  |  |  | 16.5687 | 15.8929 | 15.5244 | 63.9066 | 63.6339 | 73.4162 | 17.2937 | 16.3754 | 15.4323 | 16.8824 | 16.1475 | 15.478 | 14.8536 | 66.2923 |  | 28.0996 | 52.4819 | 55.668 | 23.1563 |  | 6.4869 | 6.5065 | 5.9085 | 6.0484 | 6.0817 | 7.11 | 23.7125 | 4.9252 | 6.4403 | 4.8391 | 6.827 | 8.1859 | 42.3096 | 46.8951 | 43.0985 | 14.95 |  |  | -0.15223 | -0.065625 | 0.12539 | -0.060454 | -0.043204 | -0.30996 | 0.4612 | -0.38918 | -0.19186 | 0.45006 | -0.24252 | 8.8737 | 6.8751 | 2.0054 | 15.8696 | 16.7109 | 17.2353 | 17.5494 | 17.4976 | 16.4593 | 14.8065 | 16.8252 | 17.1639 | 17.4665 | 17.5075 | 17.2296 | 16.4072 | 14.6056 | 14.6914 | 10.4382 | 8.8572 | 8.0807 | 7.8264 | 8.7876 | 8.2312 | 15.9728 | 15.5404 | 15.3804 | 14.3073 | 14.2299 | 14.2295 |  |  |  | 14.4511 | 72.2591 | 56.1308 | 17.3149 | -0.17054 | -0.19777 | 19.5096 |  |  | 10.6961 |  |  | 16.8766 | 16.0592 | 15.9623 | 16.3495 | 15.6253 | 14.9776 | 61.2986 | 73.9412 | 47.0274 | 47.6241 | 21.6618 |  | 14.926 | 27.062 | 15.6086 | 16.9366 | 15.3722 | 55.0784 |  | 24.4183 |  |  | 12.3558 | 13.4092 | 20.2211 | [6 empty] | 17.1633 |  |  | 16.3591 |  |  | 11.2352 | 16.291 | 83.5555 | 8.0147 | 13.3794 | 55.1171 | 8.7438 | 12.5022 | 59.7356 | 12.7576 | 48.3897 | 8.7129 | 41.2887 | 9.4902 | 42.0843 | 8.6404 | 15.1314 | 53.6404 | 12.8577 | 14.715 | 72.3304 | 9.3536 | 13.3719 | 60.1298 | 9.3731 | 41.2542 | 12.1163 | 43.1908 | 10.1667 | 43.3445 | 0.15773 | 20.3161 | 0.41476 | 0.055434 | -37.7619 | 3.1214 | 49.43 | 49.7 | -0.50619 | -0.29855 | 0.41267 | -0.28654 | -0.2425 | -0.64953 | 0.7923 | 0.20338 | 0.076056 | 0.34946 | -0.29772 | 0.28588 | 0.15947 | 0.30837
42810.4421 | 175 | 18.621 | 18.6416 | 18.5986 | 18.6014 | 17.9146 | 16.5189 | 14.5707 | 16.678 | 17.1753 | 17.2683 | 17.2775 | 16.8131 | 15.8445 | 14.464 | 15.0176 | 14.9728 | 15.502 | 13.3526 | 13.4958 | 14.0836 |  |  |  | 16.5635 | 15.8888 | 15.5252 | 63.9591 | 63.7774 | 73.5217 | 17.2946 | 16.3753 | 15.4396 | 16.8818 | 16.1519 | 15.4857 | 14.903 | 66.0007 |  | 28.1778 | 52.5825 | 55.7893 | 23.4781 |  | 6.4909 | 6.5117 | 5.9128 | 6.0666 | 6.0989 | 7.1135 | 23.497 | 4.9575 | 6.4422 | 4.9434 | 6.829 | 8.1766 | 42.3171 | 46.885 | 43.1005 | 14.9396 |  |  | -0.34345 | -0.009113 | 0.10699 | -0.026942 | -0.037948 | -0.11348 | 0.48157 | -0.27812 | -0.17143 | 0.16662 | -0.30074 | 8.9007 | -0.00040248 | 2.0053 | 15.8705 | 16.7062 | 17.2275 | 17.5439 | 17.4935 | 16.4556 | 14.8044 | 16.8185 | 17.1492 | 17.4543 | 17.4915 | 17.2191 | 16.3959 | 14.6043 | 15.7079 | 10.8323 | 9.2843 | 8.0665 | 7.7994 | 8.8347 | 8.245 | 15.9766 | 15.5449 | 15.3791 | 14.3042 | 14.2384 | 14.2239 |  |  |  | 14.5062 | 72.3622 | 56.8647 | 18.3575 | 0.12465 | -0.22393 | 19.6166 |  |  | 10.7016 |  |  | 16.8737 | 16.0633 | 15.9843 | 16.3462 | 15.6276 | 14.9835 | 61.4784 | 74.18 | 47.1849 | 47.7985 | 22.415 |  | 14.9847 | 27.907 | 15.6717 | 16.9086 | 15.4175 | 54.6605 |  | 24.5256 |  |  | 12.3832 | 13.408 | 20.3158 | [6 empty] | 17.2572 |  |  | 16.3764 |  |  | 11.2405 | 16.3125 | 83.7176 | 8.0267 | 13.381 | 55.2075 | 8.7487 | 12.5056 | 59.7617 | 12.7581 | 48.7073 | 8.7146 | 41.3731 | 9.4896 | 42.2178 | 8.6639 | 15.1518 | 53.7142 | 12.8613 | 14.7573 | 72.4104 | 9.3761 | 13.3914 | 60.3014 | 9.397 | 41.3199 | 12.14 | 43.2991 | 10.2071 | 43.5397 | 0.18373 | 20.3133 | 0.41624 | 0.054399 | -37.7522 | 3.1214 | 49.85 | 49.75 | -0.76043 | -0.11125 | 0.3812 | -0.19129 | -0.22727 | -0.39302 | 0.80962 | 0.18441 | 0.054682 | 0.35174 | -0.4052 | 0.24003 | 0.15217 | 0.28124
42810.4421 | 176 | 18.6239 | 18.6429 | 18.6073 | 18.6077 | 17.9169 | 16.5207 | 14.5761 | 16.6744 | 17.174 | 17.2729 | 17.285 | 16.8162 | 15.8517 | 14.4707 | 15.0211 | 14.9728 | 15.51 | 13.3606 | 13.4988 | 14.0983 |  |  |  | 16.5801 | 15.8949 | 15.5448 | 64.1443 | 63.8862 | 74.7215 | 17.2944 | 16.3741 | 15.4525 | 16.8863 | 16.1446 | 15.4949 | 14.9462 | 65.6902 |  | 28.2586 | 52.6913 | 55.9052 | 23.2798 |  | 6.4982 | 6.5134 | 5.9315 | 6.0799 | 6.0999 | 7.1197 | 23.2813 | 4.9757 | 6.4465 | 5.0759 | 6.8317 | 8.1849 | 42.323 | 46.894 | 43.1184 | 14.9441 |  |  | -0.27577 | -0.33832 | 0.009736 | -0.16757 | -0.045832 | -0.38422 | 0.52559 | -0.18284 | -0.83365 | -0.59978 | -0.20139 | 8.9013 | -0.00040905 | 2.0053 | 15.8734 | 16.7106 | 17.2404 | 17.5475 | 17.4983 | 16.4622 | 14.8069 | 16.8201 | 17.1629 | 17.4584 | 17.5044 | 17.2305 | 16.4052 | 14.6124 | 16.669 | 11.1952 | 10.3084 | 8.2437 | 7.808 | 8.8846 | 8.2545 | 15.9715 | 15.5377 | 15.3781 | 14.2977 | 14.2216 | 14.225 |  |  |  | 14.5391 | 72.4249 | 57.0797 | 19.0305 | -0.013525 | -0.22751 | 19.6366 |  |  | 10.7086 |  |  | 16.8715 | 16.0644 | 15.9994 | 16.3481 | 15.6304 | 14.9873 | 61.633 | 74.4418 | 47.3213 | 47.9553 | 22.3716 |  | 15.0438 | 27.9985 | 15.725 | 16.9424 | 15.4637 | 54.3324 |  | 24.6175 |  |  | 12.4139 | 13.4116 | 20.3598 | [6 empty] | 17.3196 |  |  | 16.4159 |  |  | 11.2476 | 16.3511 | 84.0065 | 8.0574 | 13.3658 | 55.2341 | 8.7734 | 12.5168 | 59.8337 | 12.7719 | 48.9339 | 8.73 | 41.4992 | 9.494 | 42.3478 | 8.6681 | 15.1437 | 53.807 | 12.8645 | 14.7643 | 72.5054 | 9.3888 | 13.3931 | 60.453 | 9.3933 | 41.381 | 12.1377 | 43.2978 | 10.2066 | 43.7365 | 0.26501 | 20.3091 | 0.41818 | 0.053147 | -37.7085 | 3.1214 | 60.96 | 48.95 | -0.68257 | -0.67788 | 0.11499 | -0.47707 | -0.24977 | -0.72317 | 0.84582 | 0.18758 | 0.053911 | 0.35234 | -0.50619 | 0.12735 | 0.15911 | 0.26363
42810.4421 | 177 | 18.6148 | 18.6454 | 18.6021 | 18.5996 | 17.9092 | 16.5251 | 14.5693 | 16.6743 | 17.1768 | 17.2674 | 17.2844 | 16.8161 | 15.8437 | 14.4616 | 15.0165 | 14.9674 | 15.5059 | 13.3608 | 13.4964 | 14.0949 |  |  |  | 16.5651 | 15.8924 | 15.5445 | 64.3976 | 63.9632 | 75.2642 | 17.2988 | 16.378 | 15.4577 | 16.8903 | 16.1474 | 15.4966 | 14.9881 | 65.451 |  | 28.3554 | 52.7633 | 56.0239 | 22.9152 |  | 6.5014 | 6.5182 | 5.9327 | 6.0907 | 6.1229 | 7.1318 | 23.0836 | 4.9777 | 6.4496 | 5.1461 | 6.8436 | 8.1908 | 42.3161 | 46.9032 | 43.1244 | 14.931 |  |  | -0.3382 | -0.1517 | 0.02288 | -0.058482 | 0.12896 | -0.11348 | 0.49077 | -0.32149 | 0.36197 | 0.61244 | -0.28783 | 8.9021 | -0.00044684 | 2.0058 | 15.8707 | 16.7091 | 17.2356 | 17.542 | 17.5036 | 16.4628 | 14.8068 | 16.8246 | 17.166 | 17.4636 | 17.5006 | 17.2273 | 16.4073 | 14.6088 | 16.948 | 11.4763 | 11.1311 | 8.6387 | 8.082 | 8.9307 | 8.2774 | 15.9733 | 15.5378 | 15.3856 | 14.296 | 14.2237 | 14.2274 |  |  |  | 14.5772 | 72.5438 | 57.4186 | 19.2639 | -0.12901 | -0.26044 | 19.5944 |  |  | 10.7187 |  |  | 16.8783 | 16.066 | 16.0122 | 16.35 | 15.6273 | 14.993 | 61.7182 | 74.6572 | 47.4496 | 48.1106 | 22.5896 |  | 15.0918 | 27.6955 | 15.7681 | 17.2612 | 15.5052 | 54.1554 |  | 24.7065 |  |  | 12.4379 | 13.4302 | 20.4381 | [6 empty] | 17.4766 |  |  | 16.4468 |  |  | 11.2597 | 16.3978 | 84.1097 | 8.0545 | 13.3373 | 55.2107 | 8.7893 | 12.5167 | 59.9679 | 12.7881 | 49.1333 | 8.7501 | 41.6272 | 9.5033 | 42.5068 | 8.6807 | 15.1409 | 53.865 | 12.8627 | 14.7976 | 72.5535 | 9.3695 | 13.3938 | 60.4912 | 9.4024 | 41.455 | 12.1417 | 43.4531 | 10.2127 | 43.8662 | 0.30757 | 20.3075 | 0.42136 | 0.054884 | -37.7067 | 3.1215 | 64.43 | 50.22 | -0.75648 | -0.45393 | 0.17629 | -0.28184 | 0.41898 | -0.39304 | 0.81734 | 0.18312 | 0.063761 | 0.34486 | -0.53182 | 0.038592 | 0.17063 | 0.25842
42810.4421 | 178 | 18.6153 | 18.6447 | 18.605 | 18.5958 | 17.8952 | 16.5174 | 14.574 | 16.6751 | 17.1743 | 17.2687 | 17.2735 | 16.8125 | 15.8501 | 14.4643 | 15.0235 | 14.9749 | 15.5069 | 13.3602 | 13.4973 | 14.0979 |  |  |  | 16.5662 | 15.8916 | 15.5573 | 64.644 | 64.1119 | 75.3517 | 17.2999 | 16.3829 | 15.47 | 16.8901 | 16.1586 | 15.5089 | 15.0199 | 65.2031 |  | 28.4589 | 52.807 | 56.1137 | 23.192 |  | 6.4903 | 6.5214 | 5.9367 | 6.1172 | 6.1318 | 7.16 | 22.8383 | 4.9806 | 6.4606 | 5.1152 | 6.8436 | 8.1788 | 42.276 | 46.9115 | 43.1191 | 14.9285 |  |  | -0.27906 | -0.11688 | 0.059676 | -0.13931 | 0.072448 | -0.095084 | 0.47565 | -0.34646 | -0.95547 | -1.3746 | -0.25504 | 8.9019 | -0.00047148 | 2.005 | 15.8782 | 16.7062 | 17.2337 | 17.5427 | 17.5047 | 16.458 | 14.8039 | 16.8232 | 17.1645 | 17.458 | 17.5058 | 17.2291 | 16.4084 | 14.6132 | 16.8056 | 11.2944 | 12.1077 | 9.0841 | 8.9231 | 8.9707 | 8.3098 | 15.9723 | 15.5348 | 15.3803 | 14.2967 | 14.2225 | 14.2261 |  |  |  | 14.6233 | 72.768 | 57.9997 | 19.4256 | 0.046444 | -0.081842 | 19.5485 |  |  | 10.7198 |  |  | 16.8707 | 16.0608 | 16.0291 | 16.3464 | 15.6296 | 14.9929 | 61.8014 | 74.7672 | 47.563 | 48.2545 | 23.2193 |  | 15.1491 | 27.1427 | 15.8031 | 17.6324 | 15.5491 | 54.1944 |  | 24.804 |  |  | 12.4414 | 13.4167 | 20.5094 | [6 empty] | 17.6257 |  |  | 16.4758 |  |  | 11.2664 | 16.433 | 84.2582 | 8.044 | 13.321 | 55.3685 | 8.7989 | 12.5213 | 60.1752 | 12.7895 | 49.3003 | 8.7564 | 41.7891 | 9.5039 | 42.6805 | 8.6808 | 15.1258 | 53.8962 | 12.8753 | 14.8819 | 72.5871 | 9.369 | 13.391 | 60.6026 | 9.4059 | 41.5314 | 12.1391 | 43.9235 | 10.2151 | 44.055 | 0.14617 | 20.3036 | 0.42426 | 0.055781 | -37.7362 | 3.1215 | 74.53 | 48.91 | -0.68725 | -0.39843 | 0.2847 | -0.43499 | 0.31405 | -0.35978 | 0.80469 | 0.16753 | 0.080281 | 0.33601 | -0.51136 | -0.066158 | 0.164 | 0.25546
42810.4421 | 179 | 18.606 | 18.6341 | 18.5953 | 18.6021 | 17.9023 | 16.5169 | 14.5656 | 16.6659 | 17.164 | 17.2677 | 17.2778 | 16.8122 | 15.8422 | 14.4596 | 15.0188 | 14.9681 | 15.5043 | 13.356 | 13.4983 | 14.0955 |  |  |  | 16.5694 | 15.8916 | 15.5698 | 64.8328 | 64.2814 | 75.4178 | 17.3005 | 16.3832 | 15.4762 | 16.8845 | 16.1467 | 15.5181 | 15.0572 | 65.269 |  | 28.5477 | 52.8447 | 56.1758 | 22.8647 |  | 6.4892 | 6.5223 | 5.9406 | 6.1201 | 6.1621 | 7.1708 | 22.6066 | 4.9539 | 6.461 | 5.0421 | 6.8423 | 8.1818 | 42.2607 | 46.9228 | 43.1182 | 14.9436 |  |  | -0.34148 | -0.29101 | 0.01828 | -0.097254 | 0.093476 | 0.18025 | 0.57094 | -0.22161 | -0.47208 | 0.024374 | -0.23676 | 8.9018 | -0.00039755 | 2.0035 | 15.8717 | 16.7099 | 17.2278 | 17.5402 | 17.4909 | 16.4545 | 14.8008 | 16.8149 | 17.1595 | 17.4512 | 17.5042 | 17.2281 | 16.4006 | 14.6061 | 18.0609 | 11.1435 | 12.598 | 9.3215 | 9.2334 | 9.0277 | 8.3326 | 15.9836 | 15.545 | 15.3783 | 14.3024 | 14.2294 | 14.2334 |  |  |  | 14.671 | 72.8965 | 58.2688 | 19.2282 | 0.1366 | -0.18422 | 19.5259 |  |  | 10.7184 |  |  | 16.8708 | 16.0518 | 16.0455 | 16.3481 | 15.6271 | 15.0002 | 61.9052 | 74.8437 | 47.6603 | 48.366 | 23.6429 |  | 15.2197 | 26.3383 | 15.8548 | 17.8467 | 15.591 | 54.4354 |  | 24.9071 |  |  | 12.421 | 13.3865 | 20.5908 | [6 empty] | 17.7698 |  |  | 16.4994 |  |  | 11.2593 | 16.4482 | 84.4187 | 8.0295 | 13.3029 | 55.5605 | 8.8007 | 12.5227 | 60.3408 | 12.7991 | 49.4107 | 8.7544 | 41.976 | 9.5092 | 42.8076 | 8.6847 | 15.1326 | 53.9473 | 12.8809 | 14.9646 | 72.7694 | 9.3665 | 13.3962 | 60.7263 | 9.4151 | 41.6098 | 12.1541 | 44.4883 | 10.2303 | 44.2427 | 0.19124 | 20.2981 | 0.42599 | 0.054667 | -37.7043 | 3.1215 | 61.12 | 48.95 | -0.76032 | -0.62871 | 0.15757 | -0.36345 | 0.35673 | 0.49537 | 0.88163 | 0.15811 | 0.10434 | 0.33145 | -0.64421 | -0.11799 | 0.17433 | 0.26252
42810.4421 | 180 | 18.6118 | 18.6329 | 18.5959 | 18.5927 | 17.9072 | 16.5134 | 14.5609 | 16.6659 | 17.1675 | 17.2648 | 17.2751 | 16.8014 | 15.8308 | 14.4555 | 15.0206 | 14.9668 | 15.507 | 13.3555 | 13.4987 | 14.1015 |  |  |  | 16.5752 | 15.8901 | 15.5826 | 65.009 | 64.4006 | 75.5391 | 17.2908 | 16.3707 | 15.4765 | 16.8826 | 16.1461 | 15.5133 | 15.0905 | 65.3346 |  | 28.6473 | 52.8797 | 56.2712 | 22.4627 |  | 6.4813 | 6.5226 | 5.944 | 6.1329 | 6.1865 | 7.1676 | 22.3733 | 4.9254 | 6.4582 | 5.0131 | 6.8409 | 8.1809 | 42.2464 | 46.9291 | 43.1116 | 14.9562 |  |  | -0.23897 | -0.17602 | -0.027064 | -0.16822 | -0.00312 | 0.36096 | 0.63073 | -0.31426 | -0.50283 | -0.086191 | -0.087536 | 8.9021 | -0.00042548 | 2.0041 | 15.8804 | 16.7162 | 17.2272 | 17.5353 | 17.4936 | 16.4591 | 14.8065 | 16.8208 | 17.1638 | 17.4619 | 17.5047 | 17.2271 | 16.404 | 14.6096 | 20.0676 | 11.7968 | 13.0284 | 9.6505 | 9.2414 | 9.1118 | 8.362 | 15.9762 | 15.5426 | 15.3836 | 14.311 | 14.2298 | 14.2452 |  |  |  | 14.7039 | 72.967 | 58.7073 | 18.9456 | 0.052522 | -0.042132 | 19.5622 |  |  | 10.722 |  |  | 16.8751 | 16.0554 | 16.0673 | 16.349 | 15.6299 | 15.0179 | 61.9846 | 74.9419 | 47.7694 | 48.4621 | 23.822 |  | 15.2577 | 25.7685 | 15.8859 | 17.8297 | 15.6246 | 55.5268 |  | 24.9944 |  |  | 12.4132 | 13.3849 | 20.6768 | [6 empty] | 17.8237 |  |  | 16.5157 |  |  | 11.2587 | 16.4615 | 84.5682 | 8.0323 | 13.2922 | 55.6968 | 8.807 | 12.5493 | 60.4624 | 12.8196 | 49.5378 | 8.752 | 42.156 | 9.5148 | 42.8987 | 8.6917 | 15.1349 | 54.088 | 12.8877 | 14.99 | 72.9492 | 9.3708 | 13.4398 | 60.9127 | 9.425 | 41.6781 | 12.1667 | 44.7743 | 10.2418 | 44.4631 | 0.26308 | 20.2946 | 0.42814 | 0.05484 | -37.7595 | 3.1215 | 69.26 | 50.16 | -0.63615 | -0.48896 | -0.19173 | -0.47801 | -0.065173 | 0.701 | 0.92665 | 0.1544 | 0.12121 | 0.33304 | -0.8574 | -0.16238 | 0.1866 | 0.27146
42810.4421 | 181 | 18.6162 | 18.6395 | 18.6046 | 18.5942 | 17.9101 | 16.5202 | 14.5692 | 16.6685 | 17.1696 | 17.2637 | 17.2812 | 16.8067 | 15.8387 | 14.4594 | 15.019 | 14.957 | 15.4995 | 13.3483 | 13.4948 | 14.0933 |  |  |  | 16.5667 | 15.8864 | 15.582 | 65.1796 | 64.5345 | 75.6002 | 17.2833 | 16.3678 | 15.4742 | 16.8802 | 16.1499 | 15.5137 | 15.119 | 65.4411 |  | 28.7497 | 52.9403 | 56.366 | 22.1973 |  | 6.499 | 6.538 | 5.9778 | 6.1749 | 6.2152 | 7.2148 | 22.1513 | 4.8825 | 6.463 | 5.0223 | 6.856 | 8.1835 | 42.2405 | 46.9318 | 43.1021 | 14.9622 |  |  | -0.22583 | -0.098481 | 0.11816 | -0.25365 | -0.12403 | -0.083912 | 0.71616 | -0.28535 | -0.96695 | -0.48565 | -0.33035 | 8.9016 | -0.00042548 | 2.0038 | 15.8766 | 16.7112 | 17.2346 | 17.5423 | 17.4899 | 16.4545 | 14.8074 | 16.8204 | 17.1579 | 17.4517 | 17.4943 | 17.2227 | 16.4014 | 14.6094 | 20.2439 | 12.0801 | 14.2105 | 10.0826 | 9.4468 | 9.1727 | 8.4074 | 15.9758 | 15.5442 | 15.3857 | 14.3119 | 14.2312 | 14.2525 |  |  |  | 14.7375 | 73.116 | 59.0937 | 18.9519 | -0.061744 | -0.15185 | 19.6369 |  |  | 10.7279 |  |  | 16.8699 | 16.0591 | 16.0771 | 16.3481 | 15.6193 | 15.0167 | 62.0981 | 75.1437 | 47.8768 | 48.5712 | 24.0738 |  | 15.3183 | 25.2142 | 15.9246 | 17.8446 | 15.668 | 55.8124 |  | 25.0919 |  |  | 12.4342 | 13.3947 | 20.7127 | [6 empty] | 17.8736 |  |  | 16.5418 |  |  | 11.2585 | 16.4863 | 84.4246 | 8.0352 | 13.2926 | 55.7597 | 8.8145 | 12.5803 | 60.5863 | 12.844 | 49.702 | 8.752 | 42.3167 | 9.531 | 42.995 | 8.6999 | 15.1455 | 54.2 | 12.8977 | 14.9967 | 73.024 | 9.381 | 13.4625 | 61.1084 | 9.4337 | 41.7358 | 12.1716 | 45.0296 | 10.2567 | 44.6283 | 0.39828 | 20.292 | 0.43124 | 0.056556 | -37.7661 | 3.1215 | 62.46 | 48.91 | -0.61846 | -0.36575 | 0.40063 | -0.58697 | -0.41096 | -0.33802 | 0.98749 | 0.14941 | 0.13789 | 0.33407 | -0.86992 | -0.28846 | 0.19492 | 0.27241
42810.4421 | 182 | 18.6169 | 18.6417 | 18.6115 | 18.6045 | 17.9168 | 16.5231 | 14.5741 | 16.6715 | 17.1784 | 17.2665 | 17.2862 | 16.8143 | 15.8457 | 14.4617 | 15.0203 | 14.9689 | 15.5038 | 13.3549 | 13.4991 | 14.0978 |  |  |  | 16.5676 | 15.8938 | 15.597 | 65.2801 | 64.6945 | 75.6321 | 17.2906 | 16.3816 | 15.4891 | 16.8854 | 16.1505 | 15.5291 | 15.1696 | 65.713 |  | 28.862 | 53.042 | 56.4814 | 23.0968 |  | 6.4884 | 6.5404 | 6.0052 | 6.1881 | 6.2207 | 7.2319 | 21.9708 | 4.8398 | 6.46 | 4.9805 | 6.8528 | 8.189 | 42.2549 | 46.9343 | 43.0948 | 14.9779 |  |  | -0.32965 | -0.18193 | -0.021804 | 0.087398 | 0.092816 | -0.015572 | 0.77004 | -0.20518 | -0.88756 | -0.71664 | -0.41996 | 8.9025 | -0.00043534 | 2.0033 | 15.8778 | 16.7135 | 17.2328 | 17.5439 | 17.4889 | 16.4565 | 14.7991 | 16.8145 | 17.1557 | 17.4539 | 17.4929 | 17.2246 | 16.4035 | 14.6016 | 20.0944 | 11.8902 | 14.8257 | 10.8487 | 10.0761 | 9.2252 | 8.4463 | 15.9759 | 15.5438 | 15.3845 | 14.3053 | 14.2339 | 14.2478 |  |  |  | 14.7679 | 73.2529 | 59.1696 | 19.5865 | 0.077239 | -0.16672 | 19.8022 |  |  | 10.7267 |  |  | 16.8705 | 16.0607 | 16.0877 | 16.348 | 15.6221 | 15.0148 | 62.1826 | 75.362 | 48.0186 | 48.7113 | 24.1145 |  | 15.3811 | 25.3547 | 15.9693 | 17.9998 | 15.7182 | 55.7932 |  | 25.1874 |  |  | 12.4448 | 13.3989 | 20.7443 | [6 empty] | 17.9578 |  |  | 16.5793 |  |  | 11.261 | 16.5191 | 84.3394 | 8.0366 | 13.3476 | 55.8086 | 8.8208 | 12.5955 | 60.7144 | 12.8655 | 49.8394 | 8.7469 | 42.4597 | 9.5335 | 43.1016 | 8.6956 | 15.211 | 54.2367 | 12.9053 | 15.0006 | 73.1387 | 9.3935 | 13.4766 | 61.3426 | 9.4381 | 41.8136 | 12.1757 | 45.4041 | 10.2612 | 44.7584 | 0.30564 | 20.2894 | 0.43434 | 0.056013 | -37.729 | 3.1215 | 55.88 | 49.19 | -0.74726 | -0.49712 | -0.1721 | 0.34455 | 0.35551 | -0.14562 | 1.024 | 0.15037 | 0.13547 | 0.33143 | -0.8472 | -0.35229 | 0.17161 | 0.25579
42810.4422 | 183 | 18.6111 | 18.6364 | 18.6114 | 18.6051 | 17.9116 | 16.5122 | 14.5709 | 16.6772 | 17.1738 | 17.2679 | 17.2857 | 16.8117 | 15.8395 | 14.4677 | 15.0212 | 14.9734 | 15.5031 | 13.347 | 13.4976 | 14.108 |  |  |  | 16.5677 | 15.8886 | 15.6064 | 65.3767 | 64.7665 | 75.665 | 17.2906 | 16.3836 | 15.4951 | 16.8816 | 16.1489 | 15.5419 | 15.2272 | 66.1222 |  | 28.9533 | 53.1449 | 56.6076 | 25.5788 |  | 6.5023 | 6.5485 | 6.0151 | 6.2015 | 6.2431 | 7.2443 | 21.7528 | 4.8437 | 6.4684 | 4.9168 | 6.8617 | 8.1877 | 42.2635 | 46.9284 | 43.0831 | 14.9824 |  |  | -0.30271 | -0.2207 | -0.01392 | -0.17939 | 0.080988 | -0.097712 | 0.61956 | 0.054376 | -0.35727 | -0.15668 | -0.41201 | 8.9025 | -0.00045998 | 2.004 | 15.8785 | 16.7109 | 17.2314 | 17.5413 | 17.4889 | 16.4489 | 14.8049 | 16.8185 | 17.165 | 17.4626 | 17.4925 | 17.2182 | 16.3959 | 14.6063 | 20.711 | 12.2662 | 15.591 | 11.3254 | 10.6899 | 9.3034 | 8.4899 | 15.9745 | 15.5403 | 15.3923 | 14.3008 | 14.2314 | 14.2416 |  |  |  | 14.8169 | 73.4364 | 59.4677 | 20.6737 | 0.21339 | -0.12645 | 19.9322 |  |  | 10.7259 |  |  | 16.8716 | 16.0533 | 16.1045 | 16.3466 | 15.6231 | 15.0197 | 62.2239 | 75.5087 | 48.2066 | 48.8728 | 24.5681 |  | 15.4395 | 27.5646 | 16.0503 | 18.1001 | 15.7566 | 56.208 |  | 25.2976 |  |  | 12.4417 | 13.4093 | 20.8184 | [6 empty] | 18.0922 |  |  | 16.6267 |  |  | 11.2663 | 16.545 | 84.3536 | 8.0406 | 13.4163 | 55.8852 | 8.8162 | 12.6089 | 60.8543 | 12.8811 | 49.9735 | 8.7453 | 42.5889 | 9.5472 | 43.1979 | 8.6946 | 15.3161 | 54.2974 | 12.9283 | 15.0193 | 73.3509 | 9.4101 | 13.5095 | 61.5013 | 9.4521 | 41.93 | 12.1925 | 45.7526 | 10.2702 | 44.9013 | 0.2028 | 20.2846 | 0.43461 | 0.053762 | -37.7433 | 3.1215 | 62.95 | 50.54 | -0.71611 | -0.54754 | -0.13751 | -0.49365 | 0.33209 | -0.36478 | 0.91853 | 0.13971 | 0.076782 | 0.32992 | -0.90662 | -0.43226 | 0.10458 | 0.22721
42810.4422 | 184 | 18.6155 | 18.6463 | 18.6154 | 18.612 | 17.9176 | 16.5217 | 14.5743 | 16.6802 | 17.1801 | 17.2772 | 17.2869 | 16.8155 | 15.8442 | 14.4674 | 15.0169 | 14.9759 | 15.5091 | 13.3483 | 13.4933 | 14.1046 |  |  |  | 16.5766 | 15.8933 | 15.6157 | 65.5051 | 64.8359 | 75.522 | 17.2831 | 16.3795 | 15.4926 | 16.8809 | 16.1378 | 15.5459 | 15.2777 | 66.2184 |  | 29.0385 | 53.2573 | 56.746 | 27.0147 |  | 6.5065 | 6.5633 | 6.0257 | 6.217 | 6.2681 | 7.2629 | 21.5727 | 4.9038 | 6.4792 | 4.8831 | 6.8718 | 8.1858 | 42.2618 | 46.9125 | 43.0875 | 14.9842 |  |  | -0.30534 | -0.14842 | 0.028792 | -0.16953 | 0.10464 | 0.22033 | 0.475 | 0.22851 | -0.33042 | -0.46782 | -0.17119 | 8.9017 | -0.00049284 | 2.0045 | 15.8794 | 16.7105 | 17.2294 | 17.539 | 17.4923 | 16.4486 | 14.8001 | 16.8228 | 17.1558 | 17.4553 | 17.4882 | 17.2167 | 16.4012 | 14.6088 | 21.6703 | 12.8423 | 16.5548 | 12.094 | 11.2862 | 9.3807 | 8.5325 | 15.978 | 15.5491 | 15.384 | 14.3005 | 14.2361 | 14.2552 |  |  |  | 14.8667 | 73.672 | 59.5146 | 20.6989 | 0.028413 | -0.10612 | 20.1285 |  |  | 10.7281 |  |  | 16.8823 | 16.0581 | 16.1246 | 16.3537 | 15.6294 | 15.0365 | 62.3229 | 75.5672 | 48.3995 | 49.0551 | 25.0538 |  | 15.4921 | 29.3996 | 16.1315 | 18.1634 | 15.7945 | 56.7129 |  | 25.4079 |  |  | 12.4506 | 13.4423 | 20.9997 | [6 empty] | 18.196 |  |  | 16.65 |  |  | 11.2723 | 16.5721 | 84.4424 | 8.0343 | 13.4393 | 56.0378 | 8.82 | 12.6313 | 60.9892 | 12.8956 | 50.1351 | 8.7465 | 42.7071 | 9.5624 | 43.254 | 8.7023 | 15.3619 | 54.4086 | 12.9307 | 15.0405 | 73.4551 | 9.413 | 13.5376 | 61.6033 | 9.4563 | 42.0502 | 12.1887 | 46.0112 | 10.2713 | 45.0172 | 0.34628 | 20.2792 | 0.43785 | 0.054297 | -37.755 | 3.1215 | 81.99 | 48.99 | -0.71906 | -0.44903 | 0.19777 | -0.4799 | 0.37751 | 0.54778 | 0.80429 | 0.12797 | 0.028511 | 0.32942 | -1.0042 | -0.53441 | 0.066374 | 0.22816
42810.4422 | 185 | 18.6033 | 18.6397 | 18.6015 | 18.607 | 17.9087 | 16.522 | 14.5675 | 16.6809 | 17.1738 | 17.2686 | 17.283 | 16.8072 | 15.8364 | 14.4622 | 15.0101 | 14.968 | 15.5042 | 13.3495 | 13.4885 | 14.0993 |  |  |  | 16.5681 | 15.8878 | 15.6247 | 65.5875 | 64.9997 | 75.6325 | 17.2899 | 16.3847 | 15.5019 | 16.8842 | 16.1381 | 15.5528 | 15.3385 | 66.3644 |  | 29.1376 | 53.3968 | 56.878 | 26.4439 |  | 6.5 | 6.5655 | 6.0214 | 6.2292 | 6.2876 | 7.2733 | 21.4532 | 4.8981 | 6.4818 | 4.8942 | 6.8674 | 8.1729 | 42.2386 | 46.901 | 43.082 | 14.9774 |  |  | -0.52547 | -0.11359 | 0.15627 | -0.26087 | 0.05996 | -0.28828 | 0.81407 | 0.014948 | -0.331 | -0.37991 | -0.24709 | 8.9013 | -0.00045998 | 2.005 | 15.8812 | 16.7132 | 17.2377 | 17.5517 | 17.4947 | 16.4596 | 14.8068 | 16.8214 | 17.1591 | 17.4542 | 17.4931 | 17.2248 | 16.3997 | 14.6061 | 22.0986 | 13.0404 | 17.3472 | 12.9751 | 11.8066 | 9.4589 | 8.5715 | 15.9798 | 15.5468 | 15.3846 | 14.3051 | 14.2329 | 14.2517 |  |  |  | 14.9019 | 73.8727 | 59.4158 | 20.369 | 0.053738 | -0.099157 | 20.2765 |  |  | 10.7244 |  |  | 16.8761 | 16.0583 | 16.1386 | 16.3575 | 15.63 | 15.0378 | 62.5445 | 75.5656 | 48.5682 | 49.1773 | 24.5606 |  | 15.5535 | 28.7624 | 16.2203 | 18.2684 | 15.8412 | 57.3908 |  | 25.5264 |  |  | 12.4542 | 13.4418 | 21.0745 | [6 empty] | 18.3054 |  |  | 16.6723 |  |  | 11.2912 | 16.6039 | 84.5295 | 8.031 | 13.4319 | 56.1617 | 8.824 | 12.6611 | 61.0662 | 12.9111 | 50.3696 | 8.743 | 42.7992 | 9.572 | 43.3261 | 8.7149 | 15.3575 | 54.5458 | 12.9323 | 15.0933 | 73.5502 | 9.4242 | 13.5711 | 61.6747 | 9.4628 | 42.1931 | 12.1941 | 46.3617 | 10.2836 | 45.1856 | 0.32144 | 20.2763 | 0.44054 | 0.056498 | -37.7292 | 3.1215 | 56.95 | 49.48 | -0.94345 | -0.39283 | 0.46075 | -0.59531 | 0.28576 | -0.62658 | 1.0529 | 0.14371 | 0.049164 | 0.32806 | -1.0427 | -0.61791 | 0.084249 | 0.2385
42810.4422 | 186 | 18.6021 | 18.6315 | 18.5897 | 18.6063 | 17.905 | 16.5134 | 14.5738 | 16.6735 | 17.1638 | 17.2652 | 17.2791 | 16.8019 | 15.8278 | 14.4502 | 15.0151 | 14.9662 | 15.499 | 13.3529 | 13.4961 | 14.0993 |  |  |  | 16.5693 | 15.8852 | 15.633 | 65.7714 | 65.1551 | 75.9786 | 17.2875 | 16.3707 | 15.5111 | 16.8823 | 16.136 | 15.5613 | 15.3674 | 66.5662 |  | 29.2413 | 53.548 | 56.9876 | 25.6238 |  | 6.515 | 6.5643 | 6.0251 | 6.2344 | 6.3145 | 7.2878 | 21.34 | 4.8582 | 6.4764 | 4.9686 | 6.8754 | 8.1783 | 42.2174 | 46.9112 | 43.0919 | 14.9764 |  |  | -0.36448 | -0.11885 | 0.030108 | -0.088054 | 0.05996 | 0.39184 | 0.42046 | -0.12042 | -0.040072 | -0.39523 | -0.48156 | 8.901 | -0.00044191 | 2.0045 | 15.8866 | 16.7143 | 17.2374 | 17.5491 | 17.495 | 16.4608 | 14.809 | 16.8249 | 17.166 | 17.4578 | 17.4989 | 17.2288 | 16.4044 | 14.6036 | 22.8708 | 13.0142 | 17.8265 | 13.6747 | 12.4704 | 9.5369 | 8.6223 | 15.9856 | 15.5463 | 15.3951 | 14.3037 | 14.2358 | 14.2583 |  |  |  | 14.945 | 74.1082 | 59.4267 | 20.1155 | 0.035909 | -0.1272 | 20.2922 |  |  | 10.7257 |  |  | 16.8748 | 16.0602 | 16.1544 | 16.3562 | 15.6281 | 15.0374 | 62.7098 | 75.6872 | 48.7377 | 49.3135 | 23.8616 |  | 15.6218 | 26.8917 | 16.3173 | 18.3195 | 15.8918 | 57.5487 |  | 25.6417 |  |  | 12.4815 | 13.4382 | 21.2815 | [6 empty] | 18.3765 |  |  | 16.7327 |  |  | 11.3017 | 16.6363 | 84.5706 | 8.0211 | 13.4224 | 56.3561 | 8.8273 | 12.6825 | 61.1109 | 12.9212 | 50.5897 | 8.7245 | 42.8856 | 9.5685 | 43.3699 | 8.728 | 15.338 | 54.667 | 12.9474 | 15.13 | 73.5763 | 9.428 | 13.5903 | 61.7861 | 9.4589 | 42.299 | 12.2009 | 46.6745 | 10.2863 | 45.4538 | 0.24209 | 20.2722 | 0.44206 | 0.056382 | -37.7463 | 3.1215 | 54.84 | 49.38 | -0.78614 | -0.40181 | 0.20224 | -0.34586 | 0.28577 | 0.73053 | 0.75674 | 0.16539 | 0.10436 | 0.32832 | -1.1195 | -0.66526 | 0.10799 | 0.24697
42810.4422 | 187 | 18.6106 | 18.636 | 18.6033 | 18.5996 | 17.9036 | 16.5163 | 14.5665 | 16.6736 | 17.1665 | 17.2667 | 17.2789 | 16.8078 | 15.834 | 14.4565 | 15.0169 | 14.9725 | 15.5119 | 13.3605 | 13.5097 | 14.121 |  |  |  | 16.5766 | 15.8977 | 15.6481 | 65.9532 | 65.2398 | 75.9212 | 17.2854 | 16.3709 | 15.5179 | 16.8769 | 16.1476 | 15.5618 | 15.4058 | 67.017 |  | 29.3534 | 53.6738 | 57.0582 | 25.3741 |  | 6.5201 | 6.5772 | 6.0382 | 6.2458 | 6.3494 | 7.3218 | 21.2549 | 4.8648 | 6.484 | 5.0431 | 6.8821 | 8.1769 | 42.2176 | 46.9162 | 43.1031 | 14.9777 |  |  | -0.14106 | -0.095849 | 0.01762 | -0.23591 | 0.03762 | 0.41746 | 0.34094 | 0.009036 | 0.17846 | -0.31089 | -0.36572 | 8.9006 | -0.00044519 | 2.0037 | 15.8895 | 16.718 | 17.2425 | 17.5498 | 17.5011 | 16.4611 | 14.8074 | 16.8234 | 17.1686 | 17.4667 | 17.5008 | 17.2281 | 16.4105 | 14.6065 | 23.3732 | 13.6269 | 18.2831 | 14.3713 | 12.5531 | 9.6102 | 8.6753 | 15.9827 | 15.5512 | 15.3943 | 14.3028 | 14.2367 | 14.2617 |  |  |  | 14.9699 | 74.4239 | 59.3881 | 20.0581 | 0.14997 | -0.25235 | 20.3085 |  |  | 10.7315 |  |  | 16.8736 | 16.0602 | 16.1684 | 16.3517 | 15.6306 | 15.047 | 62.7612 | 75.8293 | 48.8621 | 49.4449 | 23.4569 |  | 15.6784 | 25.8326 | 16.3967 | 18.2544 | 15.9402 | 57.5891 |  | 25.7431 |  |  | 12.5059 | 13.4641 | 21.3723 | [6 empty] | 18.4031 |  |  | 16.7563 |  |  | 11.3043 | 16.6607 | 84.6384 | 8.0073 | 13.4487 | 56.5941 | 8.8291 | 12.6828 | 61.3005 | 12.9337 | 50.7612 | 8.6919 | 42.9868 | 9.57 | 43.4069 | 8.753 | 15.4036 | 54.8117 | 12.9564 | 15.1636 | 73.6191 | 9.4334 | 13.5949 | 61.9396 | 9.4622 | 42.3645 | 12.2117 | 46.8279 | 10.2835 | 45.5418 | 0.3952 | 20.2687 | 0.44338 | 0.055796 | -37.7745 | 3.1215 | 61.28 | 49.22 | -0.48902 | -0.36085 | 0.15472 | -0.56611 | 0.22637 | 0.75409 | 0.68148 | 0.17852 | 0.13642 | 0.33173 | -1.1668 | -0.70984 | 0.1162 | 0.24939
42810.4422 | 188 | 18.6083 | 18.6333 | 18.5957 | 18.5974 | 17.9017 | 16.5169 | 14.5682 | 16.6671 | 17.1666 | 17.2605 | 17.2776 | 16.804 | 15.835 | 14.4504 | 15.0186 | 14.9754 | 15.5102 | 13.3685 | 13.4979 | 14.116 |  |  |  | 16.5756 | 15.8901 | 15.6557 | 66.1171 | 65.3477 | 75.9371 | 17.2793 | 16.3728 | 15.5177 | 16.873 | 16.1454 | 15.5632 | 15.4509 | 67.626 |  | 29.4712 | 53.7726 | 57.1361 | 25.6696 |  | 6.5091 | 6.5724 | 6.0381 | 6.2575 | 6.3822 | 7.3266 | 21.2174 | 4.9113 | 6.4794 | 5.0194 | 6.8863 | 8.1788 | 42.2277 | 46.9183 | 43.114 | 14.971 |  |  | -0.092433 | -0.30547 | 0.029448 | -0.41793 | 0.056676 | -0.19234 | 0.38826 | -0.015936 | 0.12281 | 0.10032 | -0.31843 | 8.9019 | -0.00043205 | 2.0024 | 15.8873 | 16.711 | 17.2439 | 17.5537 | 17.5145 | 16.4547 | 14.8076 | 16.8319 | 17.168 | 17.4611 | 17.4986 | 17.2272 | 16.4086 | 14.6136 | 22.8102 | 13.3166 | 17.0833 | 14.077 | 12.7447 | 9.6596 | 8.6986 | 15.9812 | 15.5494 | 15.3843 | 14.2994 | 14.2354 | 14.2601 |  |  |  | 15.0076 | 74.7261 | 59.28 | 20.2354 | -0.070253 | -0.15129 | 20.3539 |  |  | 10.7302 |  |  | 16.8681 | 16.0566 | 16.1842 | 16.3529 | 15.6224 | 15.0471 | 62.8737 | 75.9927 | 48.9583 | 49.544 | 23.0017 |  | 15.7215 | 25.3717 | 16.4658 | 18.1625 | 15.9772 | 57.5029 |  | 25.8454 |  |  | 12.5204 | 13.5028 | 21.4303 | [6 empty] | 18.4445 |  |  | 16.7841 |  |  | 11.3151 | 16.7029 | 84.7337 | 8.0244 | 13.5136 | 56.7549 | 8.8337 | 12.694 | 61.4639 | 12.9486 | 50.9534 | 8.686 | 43.1225 | 9.5854 | 43.5629 | 8.7727 | 15.5266 | 54.9134 | 12.9645 | 15.1871 | 73.7242 | 9.4546 | 13.6084 | 62.04 | 9.4885 | 42.4555 | 12.2355 | 47.0601 | 10.2969 | 45.6056 | 0.2053 | 20.2634 | 0.44644 | 0.055716 | -37.7314 | 3.1215 | 61.35 | 49.73 | -0.39587 | -0.64419 | 0.20001 | -0.75349 | 0.27785 | -0.51185 | 0.72723 | 0.1926 | 0.15152 | 0.33552 | -1.0985 | -0.57383 | 0.10949 | 0.24572
42810.4422 | 189 | 18.6002 | 18.6309 | 18.5906 | 18.5954 | 17.8961 | 16.5105 | 14.5591 | 16.666 | 17.1593 | 17.2571 | 17.2718 | 16.7957 | 15.8312 | 14.4454 | 15.0133 | 14.967 | 15.5099 | 13.362 | 13.498 | 14.1186 |  |  |  | 16.5647 | 15.8901 | 15.6665 | 66.2076 | 65.484 | 75.6217 | 17.2779 | 16.367 | 15.527 | 16.8805 | 16.1397 | 15.5739 | 15.5003 | 67.9076 |  | 29.5781 | 53.8696 | 57.2182 | 25.7742 |  | 6.5136 | 6.5893 | 6.0473 | 6.2762 | 6.4185 | 7.3299 | 21.3073 | 4.9501 | 6.4839 | 4.994 | 6.888 | 8.1776 | 42.2399 | 46.923 | 43.1229 | 14.9662 |  |  | -0.25671 | -0.21151 | 0.047848 | 0.16362 | 0.23804 | 0.41484 | 0.291 | -0.034332 | -0.31699 | -0.28739 | -0.29697 | 8.9025 | -0.00043041 | 1.9988 | 15.8949 | 16.7148 | 17.2384 | 17.5394 | 17.4967 | 16.4558 | 14.7908 | 16.8189 | 17.1557 | 17.4545 | 17.4931 | 17.2176 | 16.4033 | 14.5966 | 21.9831 | 12.6389 | 15.857 | 13.1432 | 12.558 | 9.7083 | 8.7184 | 15.9801 | 15.5548 | 15.3869 | 14.3003 | 14.2411 | 14.2709 |  |  |  | 15.0656 | 74.8823 | 59.346 | 20.6959 | -0.083625 | -0.26176 | 20.4058 |  |  | 10.7246 |  |  | 16.8745 | 16.0606 | 16.1983 | 16.3536 | 15.6242 | 15.0526 | 62.9852 | 76.1241 | 49.0423 | 49.6145 | 23.4367 |  | 15.7899 | 25.8916 | 16.5468 | 18.1614 | 16.0092 | 57.523 |  | 25.9568 |  |  | 12.5538 | 13.528 | 21.6072 | [6 empty] | 18.4982 |  |  | 16.8117 |  |  | 11.3275 | 16.733 | 84.5782 | 8.0358 | 13.5818 | 56.9385 | 8.8406 | 12.7253 | 61.6828 | 12.9712 | 51.1232 | 8.6932 | 43.2044 | 9.5869 | 43.7155 | 8.7909 | 15.5755 | 55.0676 | 12.9655 | 15.2122 | 73.8886 | 9.4525 | 13.6303 | 62.2073 | 9.4906 | 42.5238 | 12.2567 | 47.3931 | 10.3086 | 45.7066 | 0.26616 | 20.2627 | 0.44739 | 0.054609 | -37.7455 | 3.1215 | 81.74 | 49.47 | -0.65942 | -0.53605 | 0.25496 | 0.47148 | 0.56943 | 0.75172 | 0.6296 | 0.18279 | 0.13978 | 0.33661 | -1.0009 | -0.43527 | 0.10823 | 0.23485
42810.4422 | 190 | 18.6017 | 18.6354 | 18.5926 | 18.5972 | 17.9012 | 16.512 | 14.5617 | 16.672 | 17.168 | 17.2625 | 17.2755 | 16.8053 | 15.8288 | 14.4429 | 15.0128 | 14.9738 | 15.5083 | 13.3542 | 13.5064 | 14.1218 |  |  |  | 16.5605 | 15.8927 | 15.6731 | 66.277 | 65.5909 | 75.6173 | 17.2803 | 16.3702 | 15.5282 | 16.8759 | 16.1382 | 15.5904 | 15.542 | 67.9787 |  | 29.665 | 53.991 | 57.3072 | 25.2765 |  | 6.5286 | 6.6124 | 6.0838 | 6.3165 | 6.4395 | 7.3311 | 21.4221 | 4.9938 | 6.4978 | 5.078 | 6.8933 | 8.1709 | 42.2564 | 46.9235 | 43.1171 | 14.9588 |  |  | -0.35725 | 0.034915 | 0.07742 | -0.23525 | 0.16378 | 0.27947 | 0.065612 | -0.12567 | -0.45535 | -0.48019 | -0.42195 | 8.9016 | -0.00046491 | 1.9876 | 15.887 | 16.7177 | 17.2353 | 17.547 | 17.4972 | 16.4608 | 14.8052 | 16.8232 | 17.1633 | 17.4594 | 17.5017 | 17.2301 | 16.4044 | 14.6075 | 21.5486 | 12.2717 | 15.1307 | 12.429 | 12.2075 | 9.7695 | 8.7522 | 15.9796 | 15.5496 | 15.383 | 14.2985 | 14.2386 | 14.271 |  |  |  | 15.1056 | 75.0481 | 59.5418 | 21.0981 | -0.04898 | -0.28209 | 20.4277 |  |  | 10.7275 |  |  | 16.8807 | 16.0613 | 16.2213 | 16.3535 | 15.6216 | 15.0636 | 63.0908 | 76.3667 | 49.1095 | 49.6544 | 25.0834 |  | 15.8412 | 27.0923 | 16.6147 | 18.2575 | 16.0569 | 57.4605 |  | 26.0617 |  |  | 12.5539 | 13.5333 | 21.6287 | [6 empty] | 18.5578 |  |  | 16.8189 |  |  | 11.3274 | 16.7465 | 84.6973 | 8.0386 | 13.5916 | 57.077 | 8.8233 | 12.7622 | 61.9284 | 12.9723 | 51.6362 | 8.6913 | 43.2376 | 9.5897 | 43.802 | 8.8187 | 15.5669 | 55.1572 | 12.9847 | 15.2335 | 73.999 | 9.4637 | 13.6553 | 62.2952 | 9.4939 | 42.5689 | 12.29 | 47.5587 | 10.3155 | 45.8752 | 0.38191 | 20.2607 | 0.44943 | 0.054059 | -37.7338 | 3.1214 | 69.94 | 49.07 | -0.7779 | 0.2178 | 0.32433 | -0.56536 | 0.47234 | 0.617 | 0.29896 | 0.13875 | 0.10868 | 0.33553 | -0.94552 | -0.35064 | 0.12344 | 0.22501
42810.4422 | 191 | 18.6072 | 18.6353 | 18.5965 | 18.6032 | 17.9071 | 16.5194 | 14.5674 | 16.6752 | 17.1667 | 17.2625 | 17.2803 | 16.8062 | 15.8312 | 14.4513 | 15.0132 | 14.9707 | 15.5091 | 13.3539 | 13.4987 | 14.1173 |  |  |  | 16.5641 | 15.8957 | 15.679 | 66.3543 | 65.6545 | 75.425 | 17.2862 | 16.3803 | 15.5434 | 16.8792 | 16.1492 | 15.5998 | 15.5922 | 68.2634 |  | 29.7911 | 54.1318 | 57.4368 | 25.1988 |  | 6.5373 | 6.6221 | 6.1054 | 6.3269 | 6.4389 | 7.3158 | 21.2898 | 5.0976 | 6.5011 | 5.1276 | 6.898 | 8.1774 | 42.2621 | 46.9277 | 43.1133 | 14.9505 |  |  | -0.21729 | -0.15631 | 0.097788 | -0.059142 | 0.12764 | -0.23242 | 0.39154 | 0.03072 | -0.27398 | -0.14095 | -0.28584 | 8.9016 | -0.00046655 | 1.978 | 15.897 | 16.7271 | 17.2382 | 17.5534 | 17.4967 | 16.4613 | 14.8094 | 16.8279 | 17.1685 | 17.4643 | 17.5049 | 17.2313 | 16.4079 | 14.6127 | 21.1424 | 11.9305 | 14.5016 | 12.0453 | 12.0151 | 9.8111 | 8.7671 | 15.9865 | 15.552 | 15.3823 | 14.3083 | 14.2447 | 14.2791 |  |  |  | 15.1508 | 75.2125 | 59.6716 | 21.3487 | -0.28602 | -0.30072 | 20.4657 |  |  | 10.7316 |  |  | 16.8773 | 16.0667 | 16.2353 | 16.3551 | 15.6282 | 15.068 | 63.1335 | 76.7132 | 49.2065 | 49.7383 | 25.9221 |  | 15.9003 | 28.5319 | 16.6776 | 18.2089 | 16.104 | 57.6554 |  | 26.1633 |  |  | 12.5722 | 13.5422 | 21.7005 | [6 empty] | 18.5899 |  |  | 16.8565 |  |  | 11.323 | 16.7838 | 84.7041 | 8.0687 | 13.6169 | 57.1866 | 8.8282 | 12.7833 | 62.0707 | 12.9984 | 51.8911 | 8.7131 | 43.239 | 9.6086 | 43.8949 | 8.8292 | 15.5324 | 55.2416 | 12.9885 | 15.2719 | 73.9575 | 9.4596 | 13.653 | 62.4017 | 9.4948 | 42.6824 | 12.312 | 47.6355 | 10.3176 | 46.0828 | 0.42448 | 20.2553 | 0.45113 | 0.054283 | -37.7174 | 3.1215 | 66.11 | 50.33 | -0.6065 | -0.46085 | 0.36451 | -0.28348 | 0.41697 | -0.56266 | 0.73029 | 0.11742 | 0.070792 | 0.33845 | -0.89554 | -0.27902 | 0.12727 | 0.21955
42810.4423 | 192 | 18.6016 | 18.6376 | 18.602 | 18.6077 | 17.8999 | 16.5144 | 14.5622 | 16.6728 | 17.1727 | 17.2718 | 17.2796 | 16.7957 | 15.8248 | 14.4463 | 15.0131 | 14.9707 | 15.5084 | 13.3538 | 13.5041 | 14.1181 |  |  |  | 16.5711 | 15.8876 | 15.699 | 66.3757 | 65.7776 | 75.0848 | 17.2844 | 16.3705 | 15.5505 | 16.8809 | 16.1429 | 15.6068 | 15.6454 | 68.4607 |  | 29.902 | 54.242 | 57.5742 | 26.2007 |  | 6.5365 | 6.6195 | 6.1099 | 6.3344 | 6.4306 | 7.3195 | 21.0879 | 5.1491 | 6.4971 | 5.118 | 6.9016 | 8.1751 | 42.2665 | 46.9515 | 43.1078 | 14.9375 |  |  | -0.30271 | -0.19113 | 0.010392 | -0.25759 | 0.040904 | 0.3879 | 0.3968 | -0.25184 | -0.60091 | -0.53684 | -0.26021 | 8.902 | -0.00045998 | 1.9683 | 15.8897 | 16.725 | 17.2413 | 17.553 | 17.4982 | 16.4599 | 14.8034 | 16.8281 | 17.1637 | 17.4596 | 17.5028 | 17.2229 | 16.4098 | 14.6078 | 20.0929 | 11.6962 | 14.1058 | 11.6598 | 11.6722 | 9.8375 | 8.7792 | 15.9858 | 15.5536 | 15.3902 | 14.3034 | 14.2451 | 14.2809 |  |  |  | 15.1987 | 75.4317 | 60.234 | 21.3712 | -0.099023 | -0.21151 | 20.4739 |  |  | 10.7338 |  |  | 16.8757 | 16.0632 | 16.26 | 16.3561 | 15.6279 | 15.073 | 63.1738 | 76.8886 | 49.3489 | 49.8355 | 26.2259 |  | 15.9612 | 29.9891 | 16.734 | 17.9949 | 16.1516 | 57.9054 |  | 26.2962 |  |  | 12.5864 | 13.553 | 21.73 | [6 empty] | 18.5063 |  |  | 16.8851 |  |  | 11.3158 | 16.8058 | 84.6355 | 8.0911 | 13.6441 | 57.2841 | 8.8332 | 12.7872 | 62.0873 | 13.0193 | 52.214 | 8.7272 | 43.2521 | 9.6097 | 43.9874 | 8.8469 | 15.5304 | 55.3501 | 12.9941 | 15.2996 | 73.9796 | 9.4769 | 13.6796 | 62.5653 | 9.507 | 42.8164 | 12.3506 | 47.868 | 10.3285 | 46.2622 | 0.27772 | 20.2478 | 0.45322 | 0.056034 | -37.7668 | 3.1215 | 54.7 | 48.76 | -0.71551 | -0.50961 | 0.11883 | -0.5916 | 0.23604 | 0.72689 | 0.73518 | 0.111 | 0.032188 | 0.34598 | -0.77587 | -0.23362 | 0.1012 | 0.22051
42810.4423 | 193 | 18.6059 | 18.6282 | 18.6004 | 18.6026 | 17.9008 | 16.5117 | 14.5609 | 16.6698 | 17.1666 | 17.2531 | 17.2698 | 16.7941 | 15.8237 | 14.4405 | 15.0123 | 14.9661 | 15.5059 | 13.3527 | 13.5017 | 14.1243 |  |  |  | 16.5668 | 15.8874 | 15.7042 | 66.3665 | 65.9312 | 74.9684 | 17.2819 | 16.3656 | 15.558 | 16.8869 | 16.1421 | 15.6057 | 15.6932 | 68.4135 |  | 30.0169 | 54.3691 | 57.6487 | 26.1113 |  | 6.527 | 6.609 | 6.0983 | 6.3374 | 6.4403 | 7.3308 | 21.0562 | 5.1478 | 6.4975 | 5.045 | 6.8937 | 8.1739 | 42.2573 | 46.9692 | 43.1034 | 14.9457 |  |  | -0.145 | -0.005825 | -0.044804 | -0.38901 | 0.31821 | 0.015312 | 0.32517 | -0.010676 | -0.37264 | -0.53768 | -0.13661 | 8.9008 | -0.00045834 | 1.9564 | 15.891 | 16.7182 | 17.2426 | 17.549 | 17.502 | 16.4635 | 14.8024 | 16.8283 | 17.1644 | 17.4588 | 17.5037 | 17.2214 | 16.4035 | 14.6011 | 19.6006 | 11.9381 | 13.8757 | 11.4346 | 11.5396 | 9.8693 | 8.7968 | 15.9896 | 15.5528 | 15.3962 | 14.3121 | 14.2491 | 14.2911 |  |  |  | 15.2452 | 75.783 | 60.7107 | 21.3867 | -0.020211 | -0.24426 | 20.4698 |  |  | 10.7289 |  |  | 16.8729 | 16.0618 | 16.2661 | 16.3465 | 15.6209 | 15.0715 | 63.2189 | 76.9942 | 49.5087 | 49.9585 | 26.0357 |  | 16.0146 | 30.9235 | 16.7949 | 17.6389 | 16.1847 | 57.7947 |  | 26.4326 |  |  | 12.6026 | 13.5575 | 21.7492 | [6 empty] | 18.4303 |  |  | 16.8897 |  |  | 11.3212 | 16.8441 | 84.6958 | 8.1236 | 13.7218 | 57.3867 | 8.8313 | 12.8136 | 62.1487 | 13.045 | 52.6584 | 8.7345 | 43.3124 | 9.622 | 44.0791 | 8.8607 | 15.5566 | 55.3988 | 12.9944 | 15.3284 | 74.1166 | 9.4806 | 13.7161 | 62.6743 | 9.5239 | 42.9546 | 12.3682 | 48.0142 | 10.3226 | 46.4632 | 0.26173 | 20.246 | 0.45522 | 0.057077 | -37.7415 | 3.1215 | 45.67 | 49.03 | -0.49513 | -0.088963 | -0.24673 | -0.72701 | 0.65838 | 0.14442 | 0.66554 | 0.11806 | 0.008264 | 0.35697 | -0.71748 | -0.20601 | 0.10528 | 0.22163
42810.4423 | 194 | 18.607 | 18.6324 | 18.5917 | 18.5938 | 17.8979 | 16.5108 | 14.5612 | 16.6694 | 17.1649 | 17.2643 | 17.2667 | 16.7971 | 15.8196 | 14.4346 | 15.0084 | 14.9629 | 15.5047 | 13.3432 | 13.4954 | 14.1212 |  |  |  | 16.5595 | 15.8818 | 15.7083 | 66.3982 | 66.0533 | 74.8195 | 17.2751 | 16.3649 | 15.5532 | 16.8715 | 16.1349 | 15.6038 | 15.7465 | 68.209 |  | 30.1162 | 54.4975 | 57.7629 | 25.3355 |  | 6.536 | 6.6263 | 6.1056 | 6.345 | 6.4588 | 7.3455 | 21.0184 | 5.1744 | 6.5012 | 4.9877 | 6.9006 | 8.1668 | 42.244 | 46.9686 | 43.0866 | 14.9625 |  |  | -0.35659 | -0.22333 | -0.016548 | -0.23065 | 0.33595 | -0.005716 | -0.038212 | -0.19533 | -0.30998 | -0.99085 | -0.23795 | 8.901 | -0.00048462 | 1.9648 | 15.8908 | 16.7177 | 17.2337 | 17.5488 | 17.5029 | 16.4619 | 14.8034 | 16.8277 | 17.164 | 17.4628 | 17.5042 | 17.223 | 16.4055 | 14.601 | 19.984 | 12.0558 | 13.9648 | 11.334 | 11.4964 | 9.9159 | 8.8192 | 15.9944 | 15.5565 | 15.3871 | 14.3079 | 14.2488 | 14.2888 |  |  |  | 15.2843 | 76.0752 | 60.9289 | 21.2974 | -0.091729 | -0.20643 | 20.5268 |  |  | 10.7331 |  |  | 16.8791 | 16.0669 | 16.2868 | 16.3526 | 15.6327 | 15.0904 | 63.3708 | 77.1065 | 49.669 | 50.124 | 25.4909 |  | 16.0735 | 30.5336 | 16.8458 | 17.502 | 16.226 | 57.9043 |  | 26.5439 |  |  | 12.6207 | 13.5698 | 21.7806 | [6 empty] | 18.5068 |  |  | 16.9247 |  |  | 11.33 | 16.8524 | 84.5906 | 8.1414 | 13.7708 | 57.4591 | 8.8431 | 12.8374 | 62.225 | 13.0631 | 52.7957 | 8.7393 | 43.4216 | 9.6256 | 44.1848 | 8.8695 | 15.5937 | 55.452 | 13.0002 | 15.3377 | 74.2566 | 9.4845 | 13.7692 | 62.7409 | 9.5314 | 43.078 | 12.3882 | 48.0385 | 10.3296 | 46.6292 | 0.43006 | 20.2435 | 0.45712 | 0.05628 | -37.7802 | 3.1215 | 48.18 | 50.57 | -0.77629 | -0.55087 | -0.14995 | -0.55982 | 0.6765 | -0.088242 | -0.22815 | 0.13516 | 0.020788 | 0.36215 | -0.75465 | -0.21332 | 0.1286 | 0.22541
42810.4423 | 195 | 18.6019 | 18.6331 | 18.5963 | 18.5881 | 17.9019 | 16.5137 | 14.5658 | 16.6643 | 17.1674 | 17.2669 | 17.2686 | 16.8034 | 15.8246 | 14.443 | 15.0122 | 14.9621 | 15.5073 | 13.3431 | 13.5037 | 14.1252 |  |  |  | 16.5626 | 15.8819 | 15.7252 | 66.4293 | 66.169 | 74.6641 | 17.2857 | 16.3668 | 15.5607 | 16.883 | 16.1423 | 15.6226 | 15.7838 | 68.3914 |  | 30.2266 | 54.6288 | 57.878 | 24.5993 |  | 6.5349 | 6.6309 | 6.1084 | 6.3431 | 6.4503 | 7.3281 | 21.093 | 5.3331 | 6.5037 | 4.934 | 6.9076 | 8.1736 | 42.2273 | 46.9817 | 43.0792 | 14.9803 |  |  | -0.34148 | -0.25947 | 0.15299 | -0.051914 | 0.15984 | -0.67663 | -0.032296 | -0.18153 | 0.0048804 | -0.56181 | -0.04561 | 8.9011 | -0.00046491 | 1.9729 | 15.8917 | 16.7224 | 17.2353 | 17.5517 | 17.498 | 16.4528 | 14.8052 | 16.8273 | 17.161 | 17.4643 | 17.4988 | 17.2169 | 16.4078 | 14.605 | 20.0312 | 11.6581 | 14.3044 | 11.4279 | 11.4316 | 9.9558 | 8.8498 | 15.9998 | 15.5579 | 15.4005 | 14.3156 | 14.2525 | 14.2936 |  |  |  | 15.3243 | 76.2842 | 60.9495 | 21.09 | -0.21714 | -0.19288 | 20.5276 |  |  | 10.7264 |  |  | 16.8717 | 16.0642 | 16.2997 | 16.3577 | 15.6216 | 15.0893 | 63.5184 | 77.138 | 49.808 | 50.273 | 25.0507 |  | 16.1241 | 29.6529 | 16.8916 | 17.9554 | 16.2657 | 57.9282 |  | 26.6303 |  |  | 12.6339 | 13.5828 | 21.9401 | [6 empty] | 18.701 |  |  | 16.959 |  |  | 11.3242 | 16.8614 | 84.5733 | 8.1328 | 13.7611 | 57.5267 | 8.847 | 12.8473 | 62.289 | 13.0725 | 52.8342 | 8.7431 | 43.5189 | 9.6252 | 44.2836 | 8.8704 | 15.6158 | 55.5606 | 13.0068 | 15.3501 | 74.3846 | 9.488 | 13.7776 | 62.8376 | 9.5397 | 43.1839 | 12.4005 | 48.0673 | 10.339 | 46.8043 | 0.22552 | 20.2404 | 0.45834 | 0.055173 | -37.7393 | 3.1215 | 53.4 | 48.56 | -0.75949 | -0.59378 | 0.45594 | -0.26559 | 0.46662 | -0.96005 | -0.20974 | 0.14907 | 0.046777 | 0.35087 | -0.75525 | -0.2475 | 0.15029 | 0.2325
42810.4423 | 196 | 18.6064 | 18.6372 | 18.6009 | 18.5993 | 17.9108 | 16.5144 | 14.5706 | 16.6681 | 17.1721 | 17.2708 | 17.2726 | 16.8019 | 15.8349 | 14.4542 | 15.0092 | 14.967 | 15.5061 | 13.3505 | 13.505 | 14.1339 |  |  |  | 16.5691 | 15.8864 | 15.7395 | 66.4822 | 66.3054 | 74.7106 | 17.2805 | 16.3635 | 15.5648 | 16.8833 | 16.1409 | 15.6284 | 15.8329 | 68.4907 |  | 30.3228 | 54.7667 | 57.9846 | 25.316 |  | 6.5407 | 6.6368 | 6.1016 | 6.3362 | 6.4499 | 7.3142 | 21.1173 | 5.4435 | 6.5113 | 4.9125 | 6.92 | 8.1751 | 42.2273 | 47.008 | 43.0725 | 14.9954 |  |  | -0.28629 | -0.11097 | -0.065176 | 0.18202 | -0.11877 | -0.21796 | 0.094524 | -0.42532 | -0.31173 | -0.16235 | -0.28902 | 8.9011 | -0.00045341 | 1.9463 | 15.8909 | 16.7247 | 17.2446 | 17.5598 | 17.5019 | 16.4687 | 14.8091 | 16.8352 | 17.1608 | 17.4594 | 17.5006 | 17.2295 | 16.4108 | 14.6072 | 18.9097 | 11.2163 | 14.0454 | 11.4064 | 11.3399 | 9.9694 | 8.8691 | 15.9961 | 15.5609 | 15.3976 | 14.3154 | 14.2548 | 14.3002 |  |  |  | 15.3593 | 76.5137 | 61.0938 | 20.9682 | -0.19708 | -0.059446 | 20.5685 |  |  | 10.7303 |  |  | 16.8795 | 16.0601 | 16.3153 | 16.3572 | 15.6293 | 15.1005 | 63.6373 | 77.2596 | 49.9233 | 50.4487 | 25.4158 |  | 16.186 | 29.8287 | 16.9415 | 19.0724 | 16.3269 | 57.682 |  | 26.7284 |  |  | 12.6375 | 13.5778 | 22.0804 | [6 empty] | 18.8984 |  |  | 16.978 |  |  | 11.3222 | 16.8846 | 84.6426 | 8.1214 | 13.729 | 57.6189 | 8.8465 | 12.8476 | 62.357 | 13.0759 | 52.9063 | 8.7238 | 43.6015 | 9.6246 | 44.3616 | 8.8792 | 15.62 | 55.6584 | 13.0178 | 15.3565 | 74.5679 | 9.4999 | 13.772 | 62.9412 | 9.5482 | 43.332 | 12.4179 | 48.2648 | 10.35 | 46.9234 | 0.23766 | 20.2384 | 0.46083 | 0.055513 | -37.7457 | 3.1215 | 55.36 | 49.03 | -0.69545 | -0.38831 | -0.29759 | 0.49733 | -0.40222 | -0.54488 | 0.35882 | 0.14099 | 0.043557 | 0.32188 | -0.62906 | -0.21648 | 0.13201 | 0.23704
42810.4423 | 197 | 18.6007 | 18.6421 | 18.6032 | 18.5973 | 17.9078 | 16.5215 | 14.565 | 16.6647 | 17.1705 | 17.2657 | 17.2765 | 16.8042 | 15.8283 | 14.4455 | 15.006 | 14.9731 | 15.5048 | 13.3532 | 13.5076 | 14.1316 |  |  |  | 16.5647 | 15.8853 | 15.7445 | 66.5344 | 66.4157 | 74.6612 | 17.2711 | 16.3676 | 15.5731 | 16.8819 | 16.14 | 15.6322 | 15.8928 | 68.7221 |  | 30.4036 | 54.8986 | 58.0883 | 26.3583 |  | 6.5411 | 6.6399 | 6.0943 | 6.3316 | 6.4356 | 7.2891 | 21.224 | 5.3013 | 6.5138 | 4.905 | 6.9231 | 8.1724 | 42.2114 | 47.0183 | 43.0502 | 14.9957 |  |  | -0.2738 | -0.16748 | 0.16679 | 0.12354 | -0.172 | -0.46438 | 0.23252 | -0.12239 | -0.68108 | 0.14102 | -0.076409 | 8.9017 | -0.00045505 | 1.936 | 15.8934 | 16.7272 | 17.2399 | 17.5537 | 17.5055 | 16.4612 | 14.8057 | 16.8292 | 17.1664 | 17.4568 | 17.5023 | 17.2277 | 16.404 | 14.6114 | 17.8219 | 10.8395 | 13.3179 | 11.2317 | 11.1721 | 9.9756 | 8.8748 | 15.9927 | 15.5574 | 15.387 | 14.3142 | 14.2501 | 14.3007 |  |  |  | 15.39 | 76.7037 | 61.3892 | 21.3325 | -0.30993 | -0.089935 | 20.6596 |  |  | 10.7225 |  |  | 16.8795 | 16.066 | 16.3385 | 16.3522 | 15.619 | 15.103 | 63.7692 | 77.3742 | 50.0029 | 50.6068 | 25.9186 |  | 16.2414 | 31.0351 | 16.9927 | 19.5886 | 16.3904 | 57.0855 |  | 26.7985 |  |  | 12.636 | 13.5919 | 22.1567 | [6 empty] | 19.0266 |  |  | 16.9941 |  |  | 11.3326 | 16.9149 | 84.7409 | 8.1229 | 13.7319 | 57.644 | 8.8494 | 12.8574 | 62.3389 | 13.0999 | 52.9678 | 8.7265 | 43.7081 | 9.632 | 44.4536 | 8.8847 | 15.6322 | 55.7642 | 13.0297 | 15.3706 | 74.7848 | 9.5185 | 13.7853 | 63.1111 | 9.5533 | 43.493 | 12.4486 | 48.4478 | 10.3681 | 47.0414 | 0.42005 | 20.236 | 0.46356 | 0.05505 | -37.7368 | 3.1215 | 55.55 | 50.36 | -0.68007 | -0.47705 | 0.47606 | 0.40972 | -0.48401 | -0.79529 | 0.56275 | 0.12886 | 0.011752 | 0.30965 | -0.50748 | -0.13498 | 0.10505 | 0.22794
42810.4423 | 198 | 18.5979 | 18.6395 | 18.603 | 18.5978 | 17.902 | 16.514 | 14.5638 | 16.6735 | 17.1669 | 17.2618 | 17.2744 | 16.802 | 15.8289 | 14.4474 | 15.0041 | 14.9717 | 15.5051 | 13.3518 | 13.5061 | 14.1397 |  |  |  | 16.5612 | 15.882 | 15.7546 | 66.5717 | 66.5216 | 74.5791 | 17.2714 | 16.3661 | 15.5821 | 16.8721 | 16.1381 | 15.6436 | 15.9412 | 69.1364 |  | 30.4937 | 55.007 | 58.1733 | 25.9362 |  | 6.5489 | 6.637 | 6.0859 | 6.3106 | 6.4129 | 7.2734 | 21.3178 | 5.1519 | 6.5152 | 4.8963 | 6.9201 | 8.1798 | 42.2042 | 47.0291 | 43.0283 | 15.005 |  |  | -0.14632 | -0.15368 | 0.080048 | 0.21356 | -0.13717 | -0.21008 | 0.16155 | -0.067188 | -0.44523 | -1.0221 | -0.20656 | 8.9017 | -0.00047148 | 1.9557 | 15.8943 | 16.7286 | 17.2411 | 17.5523 | 17.5026 | 16.4618 | 14.8108 | 16.8247 | 17.1605 | 17.4648 | 17.5049 | 17.2253 | 16.3983 | 14.6014 | 17.0243 | 10.5617 | 12.4862 | 11.1005 | 11.077 | 10.0002 | 8.8963 | 15.9871 | 15.5595 | 15.402 | 14.3114 | 14.2618 | 14.303 |  |  |  | 15.4462 | 76.8856 | 61.5271 | 22.0067 | -0.042902 | -0.090499 | 20.8313 |  |  | 10.7319 |  |  | 16.8788 | 16.063 | 16.3542 | 16.3542 | 15.6226 | 15.1186 | 63.821 | 77.5135 | 50.1064 | 50.6987 | 26.229 |  | 16.2884 | 31.7004 | 17.033 | 19.4011 | 16.4272 | 56.884 |  | 26.872 |  |  | 12.6092 | 13.5989 | 22.2772 | [6 empty] | 19.0054 |  |  | 17.0207 |  |  | 11.3359 | 16.9467 | 84.9387 | 8.1348 | 13.7716 | 57.696 | 8.8487 | 12.8781 | 62.3551 | 13.1136 | 53.0198 | 8.7312 | 43.7585 | 9.6484 | 44.5906 | 8.8929 | 15.629 | 55.877 | 13.041 | 15.3838 | 74.9392 | 9.529 | 13.8073 | 63.3216 | 9.5562 | 43.6567 | 12.4596 | 48.5575 | 10.3717 | 47.1385 | 0.312 | 20.2328 | 0.46591 | 0.056541 | -37.7587 | 3.1216 | 56.34 | 49.17 | -0.49709 | -0.45697 | 0.3298 | 0.53869 | -0.43222 | -0.53489 | 0.46906 | 0.1218 | -0.0053848 | 0.31609 | -0.416 | -0.040076 | 0.11839 | 0.21108
42810.4423 | 199 | 18.5903 | 18.634 | 18.5925 | 18.5858 | 17.893 | 16.4992 | 14.5515 | 16.6577 | 17.1535 | 17.2513 | 17.256 | 16.7968 | 15.8139 | 14.4303 | 15.0018 | 14.9646 | 15.5019 | 13.3555 | 13.5042 | 14.1362 |  |  |  | 16.5632 | 15.8875 | 15.7646 | 66.706 | 66.6373 | 75.3663 | 17.2711 | 16.3663 | 15.5897 | 16.8784 | 16.1358 | 15.6459 | 15.9624 | 69.4311 |  | 30.5896 | 55.0937 | 58.2644 | 25.3402 |  | 6.5574 | 6.651 | 6.0915 | 6.3098 | 6.4126 | 7.2674 | 21.653 | 5.1145 | 6.5221 | 4.8885 | 6.9249 | 8.1704 | 42.1936 | 47.0407 | 43.0151 | 15.001 |  |  | -0.24029 | -0.080081 | 0.20884 | 0.06571 | -0.12666 | 0.16645 | 0.39877 | 0.10432 | -0.15411 | -0.90798 | -0.43248 | 8.9016 | -0.00047641 | 1.9636 | 15.8968 | 16.7302 | 17.2391 | 17.5464 | 17.5016 | 16.4626 | 14.8085 | 16.8234 | 17.1618 | 17.4559 | 17.498 | 17.2183 | 16.395 | 14.604 | 16.7768 | 10.2356 | 11.761 | 10.8739 | 10.9716 | 10.0077 | 8.8916 | 15.9892 | 15.5516 | 15.3912 | 14.3036 | 14.2484 | 14.2933 |  |  |  | 15.4841 | 77.0348 | 61.6789 | 22.2808 | -0.019603 | -0.14018 | 20.953 |  |  | 10.7209 |  |  | 16.8823 | 16.065 | 16.3671 | 16.3513 | 15.6239 | 15.1209 | 63.8909 | 77.6742 | 50.1604 | 50.7621 | 27.3836 |  | 16.3573 | 30.4992 | 17.1005 | 19.2454 | 16.4794 | 57.2861 |  | 27.0034 |  |  | 12.5898 | 13.5953 | 22.4678 | [6 empty] | 18.8926 |  |  | 17.048 |  |  | 11.3363 | 16.9661 | 85.3185 | 8.1494 | 13.8256 | 57.7911 | 8.8453 | 12.9037 | 62.4514 | 13.1141 | 53.0226 | 8.7441 | 43.7835 | 9.6598 | 44.7659 | 8.8887 | 15.6177 | 55.9701 | 13.0514 | 15.3901 | 75.0683 | 9.5291 | 13.8222 | 63.4721 | 9.5673 | 43.7769 | 12.4707 | 48.6546 | 10.3761 | 47.279 | 0.44355 | 20.2317 | 0.46554 | 0.053183 | -37.7413 | 3.1216 | 58.92 | 49.35 | -0.63774 | -0.32988 | 0.53272 | 0.29882 | -0.41533 | 0.47611 | 0.73694 | 0.092025 | 0.030231 | 0.32215 | -0.38762 | 0.039962 | 0.13564 | 0.20473
42810.4423 | 200 | 18.5851 | 18.6306 | 18.5914 | 18.5926 | 17.8892 | 16.5017 | 14.546 | 16.6587 | 17.1558 | 17.2535 | 17.2609 | 16.7923 | 15.8161 | 14.4384 | 14.9954 | 14.9601 | 15.4848 | 13.341 | 13.4953 | 14.1285 |  |  |  | 16.5557 | 15.8717 | 15.7567 | 66.9114 | 66.7242 | 75.9885 | 17.2672 | 16.3631 | 15.5902 | 16.8806 | 16.134 | 15.6544 | 16.0114 | 68.8184 |  | 30.6941 | 55.1424 | 58.3661 | 24.5882 |  | 6.569 | 6.6614 | 6.0975 | 6.3168 | 6.4058 | 7.2672 | 21.785 | 5.1922 | 6.5273 | 4.9041 | 6.9427 | 8.1707 | 42.1755 | 47.0607 | 43.0016 | 14.9975 |  |  | -0.42756 | 0.099311 | 0.17664 | -0.051914 | -0.083948 | -0.12531 | 0.44477 | -0.057992 | -0.76379 | -0.44432 | -0.24332 | 8.9014 | -0.00043041 | 1.9614 | 15.8996 | 16.7298 | 17.2429 | 17.5533 | 17.5017 | 16.4588 | 14.8084 | 16.8246 | 17.1645 | 17.4509 | 17.4972 | 17.2179 | 16.399 | 14.5979 | 16.9732 | 10.2206 | 11.0323 | 10.5534 | 10.941 | 10.0412 | 8.8913 | 15.987 | 15.553 | 15.394 | 14.3028 | 14.2511 | 14.299 |  |  |  | 15.5304 | 77.1815 | 61.9317 | 22.0694 | -0.01697 | -0.11591 | 20.915 |  |  | 10.7167 |  |  | 16.8804 | 16.0717 | 16.3893 | 16.3528 | 15.628 | 15.1263 | 63.9106 | 77.8437 | 50.2005 | 50.8274 | 28.3795 |  | 16.4113 | 28.9151 | 17.1401 | 19.2183 | 16.5143 | 57.7061 |  | 27.1086 |  |  | 12.5691 | 13.5891 | 22.8899 | [6 empty] | 18.8166 |  |  | 17.0756 |  |  | 11.3467 | 17.004 | 85.673 | 8.1805 | 13.8707 | 57.7948 | 8.8514 | 12.9266 | 62.5641 | 13.1268 | 52.9994 | 8.7729 | 43.9152 | 9.6717 | 44.9029 | 8.9106 | 15.6366 | 56.0492 | 13.0696 | 15.409 | 75.2377 | 9.5504 | 13.835 | 63.4984 | 9.5857 | 43.857 | 12.4979 | 48.7547 | 10.4019 | 47.4431 | 0.364 | 20.2296 | 0.46728 | 0.053914 | -37.7456 | 3.1216 | 50.56 | 49.59 | -0.85147 | 0.36737 | 0.48995 | -0.26561 | -0.33812 | -0.41311 | 0.77828 | 0.066157 | 0.075551 | 0.32406 | -0.40556 | 0.1209 | 0.15817 | 0.21214
42810.4424 | 201 | 18.5896 | 18.6323 | 18.6006 | 18.5849 | 17.8877 | 16.504 | 14.5528 | 16.6585 | 17.1598 | 17.2601 | 17.2641 | 16.7971 | 15.8177 | 14.433 | 15.0037 | 14.9637 | 15.5061 | 13.3497 | 13.5075 | 14.1389 |  |  |  | 16.5656 | 15.8825 | 15.7852 | 67.0501 | 66.8482 | 75.4873 | 17.2615 | 16.3627 | 15.5901 | 16.878 | 16.1335 | 15.6526 | 16.0466 | 68.7709 |  | 30.7773 | 55.202 | 58.4762 | 23.9281 |  | 6.5659 | 6.6644 | 6.1041 | 6.3147 | 6.4037 | 7.2449 | 21.6564 | 5.2868 | 6.5289 | 4.9093 | 6.9307 | 8.1656 | 42.1623 | 47.0759 | 42.9961 | 14.993 |  |  | -0.39142 | -0.097821 | 0.057048 | -0.20502 | -0.13192 | -0.27448 | 0.44346 | 0.00312 | 0.80605 | -0.32201 | -0.31584 | 8.9008 | -0.00046491 | 1.9585 | 15.899 | 16.7213 | 17.2431 | 17.5463 | 17.4943 | 16.4606 | 14.8061 | 16.8196 | 17.1612 | 17.4536 | 17.4949 | 17.2178 | 16.3951 | 14.5974 | 17.6515 | 10.3689 | 10.7849 | 10.1232 | 10.6505 | 10.0941 | 8.9058 | 15.9902 | 15.5626 | 15.3868 | 14.3074 | 14.257 | 14.3159 |  |  |  | 15.5655 | 77.3212 | 62.3144 | 21.675 | -0.099023 | -0.21208 | 20.8977 |  |  | 10.7214 |  |  | 16.8685 | 16.0692 | 16.4082 | 16.3537 | 15.6311 | 15.1318 | 64.0025 | 77.9968 | 50.2955 | 50.9108 | 28.7274 |  | 16.475 | 28.7184 | 17.1939 | 19.5809 | 16.5712 | 57.7094 |  | 27.1984 |  |  | 12.5723 | 13.5562 | 22.9387 | [6 empty] | 18.8796 |  |  | 17.0784 |  |  | 11.3579 | 17.0443 | 85.5191 | 8.171 | 13.9459 | 57.7917 | 8.8534 | 12.9364 | 62.5312 | 13.1444 | 53.0534 | 8.7996 | 44.1409 | 9.6738 | 44.9845 | 8.9035 | 15.6542 | 56.144 | 13.0825 | 15.4107 | 75.4558 | 9.5412 | 13.8322 | 63.5935 | 9.5979 | 43.9314 | 12.5196 | 49.0475 | 10.401 | 47.5875 | 0.26693 | 20.2275 | 0.47033 | 0.054674 | -37.7498 | 3.1216 | 55.03 | 48.75 | -0.8141 | -0.3646 | 0.27843 | -0.52784 | -0.42384 | -0.61137 | 0.7771 | 0.058615 | 0.082811 | 0.31589 | -0.47476 | 0.15007 | 0.17767 | 0.22426
42810.4424 | 202 | 18.5947 | 18.6416 | 18.6016 | 18.5966 | 17.9018 | 16.5149 | 14.572 | 16.6677 | 17.1634 | 17.26 | 17.2666 | 16.7992 | 15.8196 | 14.4439 | 15.0037 | 14.9556 | 15.4975 | 13.3474 | 13.5018 | 14.1391 |  |  |  | 16.5634 | 15.8847 | 15.7907 | 67.0887 | 66.9874 | 75.454 | 17.2598 | 16.3648 | 15.5962 | 16.8717 | 16.1477 | 15.6647 | 16.0801 | 68.6661 |  | 30.8772 | 55.2728 | 58.5849 | 23.5164 |  | 6.5735 | 6.6782 | 6.1112 | 6.3181 | 6.4023 | 7.2401 | 21.5695 | 5.3058 | 6.5319 | 4.8868 | 6.9301 | 8.1661 | 42.1456 | 47.0829 | 42.9812 | 14.9848 |  |  | -0.29745 | -0.25619 | 0.070192 | -0.14128 | -0.082632 | 0.10534 | 0.38694 | -0.18218 | 0.16504 | -0.4076 | -0.31723 | 8.9017 | -0.00047641 | 1.9667 | 15.8883 | 16.7215 | 17.2364 | 17.5492 | 17.5006 | 16.4568 | 14.8068 | 16.8068 | 17.1679 | 17.452 | 17.4944 | 17.2147 | 16.3893 | 14.597 | 18.5042 | 10.688 | 10.8384 | 9.6975 | 10.3044 | 10.1449 | 8.9012 | 15.9887 | 15.5595 | 15.3918 | 14.3065 | 14.2597 | 14.3157 |  |  |  | 15.6225 | 77.5395 | 62.584 | 21.3291 | -0.027505 | -0.23127 | 21.0108 |  |  | 10.7284 |  |  | 16.8789 | 16.061 | 16.429 | 16.3565 | 15.6195 | 15.1367 | 64.149 | 78.0469 | 50.4037 | 51.021 | 27.869 |  | 16.5204 | 29.5388 | 17.2629 | 20.2092 | 16.6173 | 57.7575 |  | 27.2776 |  |  | 12.548 | 13.5692 | 22.6444 | [6 empty] | 19.0263 |  |  | 17.0777 |  |  | 11.3786 | 17.0815 | 85.5026 | 8.1756 | 13.9931 | 57.8984 | 8.865 | 12.9416 | 62.566 | 13.1623 | 53.1897 | 8.8198 | 44.3024 | 9.6817 | 45.0548 | 8.8936 | 15.6514 | 56.2164 | 13.096 | 15.413 | 75.5694 | 9.5477 | 13.8426 | 63.7602 | 9.5987 | 44.0157 | 12.5331 | 49.2275 | 10.4008 | 47.7132 | 0.07125 | 20.2284 | 0.4723 | 0.054674 | -37.7411 | 3.1216 | 58.8 | 50.22 | -0.70965 | -0.59006 | 0.30886 | -0.43818 | -0.33545 | 0.37874 | 0.72589 | 0.08397 | 0.062321 | 0.29997 | -0.5636 | 0.14359 | 0.19022 | 0.23577
42810.4424 | 203 | 18.595 | 18.6409 | 18.601 | 18.5969 | 17.8989 | 16.5123 | 14.5698 | 16.666 | 17.1646 | 17.2656 | 17.2649 | 16.7939 | 15.8179 | 14.4418 | 14.9943 | 14.9541 | 15.5049 | 13.3554 | 13.5131 | 14.1527 |  |  |  | 16.555 | 15.8922 | 15.8034 | 67.105 | 67.1421 | 75.4599 | 17.2667 | 16.3672 | 15.6079 | 16.876 | 16.1418 | 15.6777 | 16.1303 | 68.9222 |  | 30.9817 | 55.3383 | 58.6603 | 23.9416 |  | 6.5754 | 6.6821 | 6.1157 | 6.3306 | 6.4161 | 7.3058 | 21.4677 | 5.2162 | 6.5443 | 4.9073 | 6.932 | 8.1687 | 42.129 | 47.1065 | 42.9937 | 14.9803 |  |  | -0.33688 | -0.087309 | 0.016964 | 0.04797 | 0.076388 | 0.24924 | 0.49142 | 0.23903 | -0.70677 | 1.2288 | -0.37148 | 8.9014 | -0.0004337 | 1.9826 | 15.9012 | 16.7246 | 17.2339 | 17.5503 | 17.5048 | 16.4612 | 14.7995 | 16.8193 | 17.1609 | 17.4536 | 17.4958 | 17.2138 | 16.3972 | 14.5976 | 19.0034 | 10.8822 | 11.7013 | 9.7537 | 9.8876 | 10.1938 | 8.9187 | 15.992 | 15.5651 | 15.3977 | 14.3137 | 14.2637 | 14.3216 |  |  |  | 15.6601 | 77.745 | 62.8114 | 21.0206 | 0.010381 | -0.31615 | 21.0918 |  |  | 10.719 |  |  | 16.8688 | 16.0615 | 16.4357 | 16.3481 | 15.6204 | 15.1315 | 64.3491 | 78.048 | 50.5237 | 51.1552 | 27.0653 |  | 16.5611 | 30.8246 | 17.3301 | 20.473 | 16.6644 | 58.0205 |  | 27.3621 |  |  | 12.5391 | 13.5892 | 22.5001 | [6 empty] | 19.1378 |  |  | 17.1051 |  |  | 11.388 | 17.1231 | 85.6465 | 8.1441 | 14.0088 | 58.04 | 8.8547 | 12.9497 | 62.6428 | 13.1783 | 53.3159 | 8.82 | 44.4279 | 9.6924 | 45.18 | 8.8997 | 15.6397 | 56.2488 | 13.1111 | 15.4401 | 75.6387 | 9.5498 | 13.846 | 63.9469 | 9.6172 | 44.1444 | 12.5557 | 49.3651 | 10.4086 | 47.8178 | 0.19451 | 20.226 | 0.47374 | 0.053892 | -37.7315 | 3.1216 | 51.21 | 49.43 | -0.75522 | -0.34447 | 0.15184 | 0.25533 | 0.32256 | 0.58266 | 0.81814 | 0.10765 | 0.028844 | 0.29421 | -0.61338 | 0.049752 | 0.18008 | 0.24558
42810.4424 | 204 | 18.5834 | 18.6318 | 18.5981 | 18.5943 | 17.8962 | 16.5034 | 14.5643 | 16.6664 | 17.1616 | 17.2607 | 17.2652 | 16.7868 | 15.8175 | 14.4346 | 14.9961 | 14.9606 | 15.5039 | 13.3524 | 13.5153 | 14.1453 |  |  |  | 16.5673 | 15.886 | 15.8223 | 67.1725 | 67.3626 | 75.5456 | 17.2646 | 16.3685 | 15.6188 | 16.885 | 16.1419 | 15.6919 | 16.1986 | 69.1045 |  | 31.0951 | 55.392 | 58.7015 | 26.0805 |  | 6.5688 | 6.6782 | 6.1029 | 6.3246 | 6.457 | 7.369 | 21.5657 | 5.0358 | 6.5321 | 4.9068 | 6.9408 | 8.1688 | 42.0861 | 47.1255 | 42.9967 | 14.9693 |  |  | -0.39471 | -0.17931 | 0.016964 | -0.13865 | 0.4102 | 0.51012 | 0.47302 | 0.16543 | -0.5906 | -0.64824 | -0.2006 | 8.9006 | -0.00044027 | 1.9866 | 15.884 | 16.7225 | 17.2316 | 17.5461 | 17.5009 | 16.4525 | 14.7963 | 16.8148 | 17.1585 | 17.4558 | 17.4963 | 17.2111 | 16.3885 | 14.5957 | 19.1825 | 10.8736 | 11.7608 | 10.0239 | 9.7656 | 10.2562 | 8.9339 | 15.9914 | 15.5648 | 15.3946 | 14.3075 | 14.2589 | 14.3202 |  |  |  | 15.6976 | 77.8945 | 62.9939 | 20.9216 | -0.028315 | -0.24501 | 21.2677 |  |  | 10.7262 |  |  | 16.8819 | 16.0666 | 16.4501 | 16.3496 | 15.6252 | 15.1462 | 64.5934 | 78.0795 | 50.6175 | 51.2591 | 27.1108 |  | 16.6175 | 31.2881 | 17.391 | 20.3901 | 16.7095 | 58.0779 |  | 27.4559 |  |  | 12.5368 | 13.6047 | 22.591 | [6 empty] | 19.1031 |  |  | 17.1306 |  |  | 11.3899 | 17.1364 | 85.6756 | 8.132 | 13.9711 | 58.1965 | 8.8395 | 12.9513 | 62.7602 | 13.1912 | 53.3181 | 8.784 | 44.5372 | 9.6945 | 45.3033 | 8.9089 | 15.6437 | 56.306 | 13.1201 | 15.6123 | 75.7598 | 9.5622 | 13.8816 | 64.0596 | 9.6318 | 44.2659 | 12.5701 | 49.5208 | 10.4271 | 47.9394 | 0.24652 | 20.2242 | 0.47566 | 0.055477 | -37.7474 | 3.1216 | 60.9 | 49.08 | -0.81758 | -0.49364 | 0.15184 | -0.43408 | 0.74756 | 0.83365 | 0.80277 | 0.10827 | 0.018 | 0.29801 | -0.62602 | 0.044902 | 0.12294 | 0.24958
42810.4424 | 205 | 18.5815 | 18.6292 | 18.5927 | 18.5907 | 17.8963 | 16.5052 | 14.5557 | 16.6626 | 17.1594 | 17.2553 | 17.2612 | 16.7861 | 15.8131 | 14.4289 | 14.9914 | 14.9596 | 15.5019 | 13.3436 | 13.5117 | 14.144 |  |  |  | 16.5635 | 15.8826 | 15.8271 | 67.2033 | 67.5486 | 75.5111 | 17.2588 | 16.3559 | 15.6165 | 16.8715 | 16.1338 | 15.6912 | 16.2441 | 69.4604 |  | 31.2016 | 55.4393 | 58.7581 | 26.8548 |  | 6.5745 | 6.6855 | 6.1166 | 6.3405 | 6.4744 | 7.4746 | 21.7781 | 4.9072 | 6.5376 | 4.835 | 6.9444 | 8.1577 | 42.0448 | 47.12 | 42.9915 | 14.9638 |  |  | -0.39274 | -0.29167 | -0.017204 | -0.13668 | 0.52651 | 0.000856 | 0.47237 | -0.025792 | 0.054114 | -0.38201 | -0.44281 | 8.9019 | -0.00051583 | 1.9538 | 15.8951 | 16.721 | 17.2339 | 17.5408 | 17.4967 | 16.4546 | 14.7926 | 16.8136 | 17.1563 | 17.4562 | 17.4939 | 17.2153 | 16.389 | 14.5927 | 19.6804 | 11.2475 | 12.4855 | 9.9793 | 9.7643 | 10.3198 | 8.9607 | 15.9993 | 15.564 | 15.4015 | 14.3122 | 14.2584 | 14.3269 |  |  |  | 15.7379 | 77.9559 | 63.0138 | 20.8676 | 0.11452 | -0.2053 | 21.2772 |  |  | 10.7181 |  |  | 16.876 | 16.0691 | 16.4763 | 16.3431 | 15.6189 | 15.143 | 64.698 | 78.0893 | 50.7142 | 51.3377 | 27.4349 |  | 16.6757 | 31.749 | 17.4495 | 20.2716 | 16.7439 | 57.8736 |  | 27.5295 |  |  | 12.552 | 13.6182 | 22.6103 | [6 empty] | 18.9416 |  |  | 17.129 |  |  | 11.4026 | 17.1729 | 85.8771 | 8.1361 | 13.9835 | 58.3416 | 8.86 | 12.9758 | 62.8612 | 13.2092 | 53.398 | 8.7845 | 44.6561 | 9.6956 | 45.4422 | 8.8883 | 15.6705 | 56.4666 | 13.1248 | 15.6113 | 75.8878 | 9.5625 | 13.9288 | 64.2456 | 9.6307 | 44.4033 | 12.5664 | 49.5965 | 10.4372 | 48.077 | 0.31142 | 20.2228 | 0.47684 | 0.055448 | -37.7621 | 3.1216 | 56.34 | 49.72 | -0.81549 | -0.6296 | -0.15291 | -0.43099 | 0.8471 | 0.034156 | 0.80236 | 0.1012 | 0.007147 | 0.30245 | -0.67396 | -0.032516 | 0.10295 | 0.25242
42810.4424 | 206 | 18.5836 | 18.6218 | 18.5894 | 18.5869 | 17.8963 | 16.5003 | 14.5541 | 16.6621 | 17.1606 | 17.2471 | 17.2586 | 16.7892 | 15.817 | 14.428 | 14.9955 | 14.9524 | 15.4966 | 13.3405 | 13.5049 | 14.1475 |  |  |  | 16.5651 | 15.8788 | 15.8321 | 67.2799 | 67.6409 | 76.1005 | 17.2603 | 16.3659 | 15.6305 | 16.8773 | 16.1398 | 15.6965 | 16.2984 | 69.5752 |  | 31.3219 | 55.5147 | 58.8536 | 26.1803 |  | 6.5702 | 6.69 | 6.1142 | 6.3364 | 6.4997 | 7.6106 | 22.2517 | 4.8823 | 6.534 | 4.6643 | 6.9467 | 8.1583 | 42.0344 | 47.1036 | 42.988 | 14.9559 |  |  | -0.32308 | -0.024881 | 0.17467 | -0.16691 | 0.37735 | -0.22716 | 0.15367 | 0.43616 | -1.6113 | -0.08703 | -0.12012 | 8.9018 | -0.00048134 | 1.936 | 15.8961 | 16.7259 | 17.2349 | 17.548 | 17.4998 | 16.4579 | 14.7954 | 16.8187 | 17.159 | 17.4564 | 17.4973 | 17.2132 | 16.3927 | 14.5864 | 20.1192 | 11.7951 | 14.163 | 10.9489 | 9.9062 | 10.373 | 8.9929 | 15.9955 | 15.5647 | 15.3909 | 14.3129 | 14.2619 | 14.3305 |  |  |  | 15.773 | 77.9587 | 62.9688 | 20.8338 | -0.11766 | -0.25423 | 21.3288 |  |  | 10.7176 |  |  | 16.8774 | 16.0603 | 16.4851 | 16.3473 | 15.622 | 15.1568 | 64.7958 | 78.1341 | 50.7863 | 51.3988 | 27.0718 |  | 16.7236 | 31.9281 | 17.5231 | 19.813 | 16.7813 | 57.4039 |  | 27.6183 |  |  | 12.5693 | 13.6229 | 22.6516 | [6 empty] | 18.787 |  |  | 17.1649 |  |  | 11.4135 | 17.2128 | 86.0859 | 8.1458 | 14.0799 | 58.4627 | 8.8774 | 12.9835 | 62.9798 | 13.2218 | 53.5447 | 8.796 | 44.8124 | 9.7144 | 45.5564 | 8.8844 | 15.6802 | 56.5907 | 13.1447 | 15.6037 | 75.9978 | 9.5503 | 13.9704 | 64.4714 | 9.6246 | 44.4919 | 12.5855 | 49.6511 | 10.4404 | 48.2729 | 0.39828 | 20.2201 | 0.47805 | 0.05505 | -37.7452 | 3.1216 | 45.45 | 49.19 | -0.74027 | -0.18389 | 0.48723 | -0.47628 | 0.71731 | -0.55655 | 0.45775 | 0.11288 | 0.0046266 | 0.31643 | -0.71652 | -0.21515 | 0.12349 | 0.25453
42810.4424 | 207 | 18.5923 | 18.6381 | 18.5986 | 18.5946 | 17.8989 | 16.515 | 14.5561 | 16.6683 | 17.1601 | 17.2559 | 17.2716 | 16.8031 | 15.8189 | 14.4298 | 14.9943 | 14.952 | 15.4998 | 13.3425 | 13.511 | 14.152 |  |  |  | 16.5682 | 15.8854 | 15.8533 | 67.4715 | 67.7462 | 76.6696 | 17.2491 | 16.3524 | 15.6201 | 16.8603 | 16.1354 | 15.7003 | 16.3335 | 69.5271 |  | 31.4386 | 55.5972 | 58.9386 | 25.5351 |  | 6.5702 | 6.6952 | 6.1092 | 6.3431 | 6.4944 | 7.7321 | 22.5728 | 4.9242 | 6.5293 | 4.6274 | 6.942 | 8.1604 | 42.0386 | 47.1135 | 42.9965 | 14.9451 |  |  | -0.39668 | -0.047881 | 0.14904 | -0.068338 | 0.1467 | -0.25082 | -0.007984 | 0.051748 | -0.61181 | 0.17564 | -0.14635 | 8.9017 | -0.00045998 | 1.9538 | 15.8986 | 16.7301 | 17.2442 | 17.5546 | 17.5013 | 16.4578 | 14.7989 | 16.828 | 17.1633 | 17.4579 | 17.5033 | 17.2242 | 16.398 | 14.596 | 19.0408 | 11.4309 | 14.5455 | 11.6183 | 10.7748 | 10.4029 | 9.0312 | 15.9981 | 15.5531 | 15.402 | 14.3215 | 14.272 | 14.3391 |  |  |  | 15.8136 | 78.1438 | 63.0617 | 20.9883 | -0.10976 | -0.27531 | 21.3238 |  |  | 10.7203 |  |  | 16.872 | 16.0633 | 16.502 | 16.3447 | 15.6185 | 15.16 | 64.8973 | 78.1718 | 50.8727 | 51.4476 | 27.5231 |  | 16.8048 | 31.5351 | 17.581 | 19.6215 | 16.8165 | 57.4666 |  | 27.72 |  |  | 12.5799 | 13.6306 | 22.687 | [6 empty] | 18.6923 |  |  | 17.19 |  |  | 11.4287 | 17.2389 | 86.2105 | 8.1583 | 14.1826 | 58.5964 | 8.8892 | 12.9865 | 63.051 | 13.2377 | 53.64 | 8.8055 | 44.9521 | 9.7321 | 45.6725 | 8.8903 | 15.6549 | 56.6923 | 13.1513 | 15.6132 | 75.9904 | 9.5391 | 13.9613 | 64.5891 | 9.6162 | 44.6186 | 12.6148 | 49.8443 | 10.4513 | 48.5548 | 0.27714 | 20.2182 | 0.48034 | 0.056157 | -37.7526 | 3.1216 | 63.1 | 49.03 | -0.82093 | -0.2551 | 0.45007 | -0.30476 | 0.44735 | -0.58494 | -0.10436 | 0.10305 | 0.017472 | 0.32293 | -0.59323 | -0.25321 | 0.14258 | 0.25158
42810.4424 | 208 | 18.5867 | 18.6337 | 18.5946 | 18.5969 | 17.903 | 16.5078 | 14.5629 | 16.6748 | 17.1592 | 17.259 | 17.2632 | 16.799 | 15.8124 | 14.4275 | 14.9879 | 14.9512 | 15.4954 | 13.3476 | 13.5069 | 14.152 |  |  |  | 16.5676 | 15.8817 | 15.8574 | 67.607 | 67.9175 | 76.8331 | 17.2588 | 16.3593 | 15.6488 | 16.8714 | 16.1384 | 15.7211 | 16.3734 | 69.4092 |  | 31.5703 | 55.69 | 59.0338 | 25.257 |  | 6.556 | 6.6843 | 6.1067 | 6.3319 | 6.4883 | 7.7303 | 23.2975 | 4.9927 | 6.5296 | 4.685 | 6.9426 | 8.1578 | 42.0403 | 47.1218 | 42.9954 | 14.9389 |  |  | -0.38617 | -0.22004 | 0.00908 | -0.064398 | 0.047476 | 0.33861 | -0.19592 | -0.002136 | -0.38996 | 0.0069606 | -0.12151 | 8.9018 | -0.00048462 | 1.9762 | 15.8918 | 16.7248 | 17.2448 | 17.5515 | 17.4987 | 16.4571 | 14.7958 | 16.821 | 17.16 | 17.46 | 17.4993 | 17.2171 | 16.3972 | 14.5987 | 17.3818 | 10.7798 | 13.4224 | 11.5188 | 10.9174 | 10.4052 | 9.0439 | 15.9928 | 15.5579 | 15.3943 | 14.3173 | 14.2606 | 14.3336 |  |  |  | 15.8557 | 78.4901 | 63.0545 | 20.9858 | -0.13164 | -0.21697 | 21.2941 |  |  | 10.7254 |  |  | 16.8731 | 16.0618 | 16.5187 | 16.3493 | 15.6082 | 15.1709 | 64.9873 | 78.1646 | 50.975 | 51.5102 | 28.4076 |  | 16.8769 | 30.9276 | 17.6458 | 19.6374 | 16.8654 | 57.4207 |  | 27.8089 |  |  | 12.5723 | 13.6202 | 22.7583 | [6 empty] | 18.7571 |  |  | 17.213 |  |  | 11.4306 | 17.263 | 86.3266 | 8.1645 | 14.1514 | 58.6988 | 8.8878 | 13.0191 | 63.1158 | 13.2591 | 53.6724 | 8.7894 | 45.0775 | 9.7293 | 45.8233 | 8.8827 | 15.6221 | 56.8699 | 13.1641 | 15.6495 | 76.0317 | 9.5394 | 13.9648 | 64.7159 | 9.613 | 44.7712 | 12.6346 | 50.0563 | 10.4591 | 48.7449 | 0.33299 | 20.2168 | 0.48038 | 0.053718 | -37.743 | 3.1216 | 47.66 | 50.17 | -0.81017 | -0.54686 | 0.11109 | -0.29584 | 0.25449 | 0.67964 | -0.51697 | 0.080878 | 0.036508 | 0.32412 | -0.40863 | -0.12694 | 0.15163 | 0.25305
42810.4425 | 209 | 18.5858 | 18.6341 | 18.6029 | 18.5919 | 17.8919 | 16.5058 | 14.566 | 16.6675 | 17.1616 | 17.2554 | 17.2681 | 16.7921 | 15.8126 | 14.4294 | 14.9817 | 14.9507 | 15.4933 | 13.3503 | 13.5048 | 14.1581 |  |  |  | 16.5601 | 15.8781 | 15.8657 | 67.7158 | 68.0315 | 76.5983 | 17.2585 | 16.3525 | 15.6501 | 16.8749 | 16.1379 | 15.7226 | 16.4211 | 69.4246 |  | 31.6713 | 55.7454 | 59.129 | 25.8587 |  | 6.5671 | 6.6912 | 6.1161 | 6.3389 | 6.4942 | 7.7854 | 24.0234 | 5.1149 | 6.5433 | 4.718 | 6.9585 | 8.1603 | 42.0364 | 47.1371 | 43.0015 | 14.9323 |  |  | -0.214 | -0.18719 | -0.037576 | 0.003942 | 0.11122 | 0.052768 | -0.26492 | -0.080988 | -0.12589 | -0.61992 | -0.10582 | 8.9021 | -0.00043698 | 1.9912 | 15.8849 | 16.7245 | 17.2413 | 17.5473 | 17.4978 | 16.4515 | 14.7896 | 16.8173 | 17.1554 | 17.4494 | 17.4895 | 17.2164 | 16.3936 | 14.5871 | 16.0134 | 10.3216 | 12.1568 | 10.9258 | 10.905 | 10.4069 | 9.0561 | 15.9865 | 15.5498 | 15.3878 | 14.3072 | 14.2609 | 14.3333 |  |  |  | 15.8757 | 78.6879 | 62.9663 | 20.748 | -0.096997 | -0.051542 | 21.4267 |  |  | 10.7271 |  |  | 16.8839 | 16.0772 | 16.5564 | 16.3643 | 15.6224 | 15.1842 | 65.1178 | 78.2251 | 51.0942 | 51.6313 | 28.4422 |  | 16.9395 | 31.1244 | 17.7127 | 19.6795 | 16.9144 | 58.1259 |  | 27.9116 |  |  | 12.5544 | 13.6175 | 22.7973 | [6 empty] | 18.9298 |  |  | 17.2167 |  |  | 11.43 | 17.273 | 86.4253 | 8.1607 | 14.1003 | 58.7741 | 8.8886 | 13.0628 | 63.194 | 13.2722 | 53.7295 | 8.7723 | 45.2012 | 9.7302 | 45.9674 | 8.8781 | 15.6267 | 56.9964 | 13.1759 | 15.6675 | 76.2078 | 9.5436 | 13.994 | 64.8549 | 9.6321 | 44.8984 | 12.6467 | 50.2087 | 10.471 | 48.8627 | 0.40849 | 20.212 | 0.48268 | 0.053928 | -37.7313 | 3.1217 | 47.14 | 49 | -0.60291 | -0.50439 | -0.22598 | 0.073195 | 0.38954 | 0.26832 | -0.60121 | 0.082004 | 0.033272 | 0.32458 | -0.25638 | 0.015099 | 0.13651 | 0.26032
42810.4425 | 210 | 18.5783 | 18.6325 | 18.5974 | 18.5923 | 17.8927 | 16.5054 | 14.5594 | 16.6705 | 17.1622 | 17.2561 | 17.2654 | 16.7956 | 15.818 | 14.4308 | 14.986 | 14.9543 | 15.4927 | 13.3498 | 13.5127 | 14.1613 |  |  |  | 16.558 | 15.8822 | 15.8828 | 67.8083 | 68.1271 | 76.4044 | 17.2408 | 16.3436 | 15.6408 | 16.8697 | 16.1314 | 15.7186 | 16.4711 | 69.3803 |  | 31.7583 | 55.8282 | 59.2145 | 26.2882 |  | 6.5681 | 6.6933 | 6.1127 | 6.3472 | 6.4938 | 7.759 | 24.3141 | 5.1997 | 6.5363 | 4.7538 | 6.9561 | 8.1531 | 42.0298 | 47.1431 | 43.0027 | 14.9188 |  |  | -0.39734 | -0.039337 | 0.06362 | 0.019058 | -0.041236 | -0.08654 | 0.17206 | -0.052076 | -0.64197 | -0.56726 | -0.056737 | 8.9029 | -0.00046327 | 1.9942 | 15.8784 | 16.7189 | 17.2396 | 17.544 | 17.4891 | 16.4491 | 14.7962 | 16.8217 | 17.1626 | 17.4561 | 17.4906 | 17.2144 | 16.3807 | 14.5864 | 14.8427 | 10.0178 | 11.1192 | 10.344 | 10.447 | 10.4058 | 9.0642 | 15.9842 | 15.5564 | 15.4004 | 14.3131 | 14.2734 | 14.3482 |  |  |  | 15.9099 | 78.8173 | 63.2846 | 20.5636 | -0.16446 | -0.12532 | 21.4531 |  |  | 10.7213 |  |  | 16.8787 | 16.0671 | 16.5632 | 16.3472 | 15.6201 | 15.1905 | 65.2152 | 78.2904 | 51.2017 | 51.7095 | 27.5652 |  | 16.9994 | 31.7514 | 17.7675 | 19.5168 | 16.9531 | 58.5931 |  | 28.0034 |  |  | 12.5433 | 13.633 | 22.6906 | [6 empty] | 19.0272 |  |  | 17.2365 |  |  | 11.4379 | 17.2873 | 86.5226 | 8.1558 | 14.1108 | 58.8345 | 8.8863 | 13.073 | 63.2267 | 13.2925 | 53.8172 | 8.7691 | 45.3086 | 9.7356 | 46.1038 | 8.8813 | 15.6282 | 57.0734 | 13.1853 | 15.6691 | 76.3579 | 9.543 | 14.0696 | 65.0197 | 9.6444 | 45.0077 | 12.6606 | 50.3609 | 10.4796 | 49.0028 | 0.22302 | 20.2095 | 0.48398 | 0.053986 | -37.7498 | 3.1217 | 49.91 | 48.98 | -0.8213 | -0.23122 | 0.29405 | 0.16094 | -0.23719 | -0.3436 | 0.4845 | 0.10836 | 0.017686 | 0.33039 | -0.12643 | 0.13133 | 0.12624 | 0.26659
42810.4425 | 211 | 18.5724 | 18.631 | 18.5942 | 18.5868 | 17.8913 | 16.5018 | 14.5527 | 16.66 | 17.1618 | 17.2566 | 17.261 | 16.7881 | 15.8125 | 14.4236 | 14.9838 | 14.9526 | 15.4991 | 13.349 | 13.5148 | 14.1603 |  |  |  | 16.5626 | 15.8828 | 15.8954 | 67.9108 | 68.1905 | 76.4392 | 17.2456 | 16.3438 | 15.6513 | 16.8662 | 16.1371 | 15.734 | 16.5131 | 69.5422 |  | 31.8606 | 55.962 | 59.3614 | 25.8778 |  | 6.5694 | 6.6917 | 6.1169 | 6.3385 | 6.4715 | 7.7099 | 24.3394 | 5.1917 | 6.5362 | 4.8552 | 6.9542 | 8.1532 | 41.9988 | 47.1505 | 43.0129 | 14.9189 |  |  | -0.44333 | -0.061681 | 0.021564 | -0.07031 | -0.03072 | -0.49658 | 0.13527 | 0.14703 | -1.7401 | -0.64824 | -0.20596 | 8.9016 | -0.00050433 | 1.9903 | 15.89 | 16.7239 | 17.2432 | 17.5472 | 17.4954 | 16.4537 | 14.8024 | 16.8265 | 17.1626 | 17.4522 | 17.4947 | 17.2128 | 16.3954 | 14.593 | 13.7774 | 9.7966 | 10.411 | 9.7526 | 10.0191 | 10.3951 | 9.0682 | 15.9875 | 15.5586 | 15.3972 | 14.3167 | 14.269 | 14.3545 |  |  |  | 15.953 | 78.8658 | 63.3878 | 20.4987 | -0.086259 | -0.16371 | 21.4725 |  |  | 10.7091 |  |  | 16.8779 | 16.0565 | 16.5675 | 16.3446 | 15.6183 | 15.1801 | 65.2937 | 78.2758 | 51.3299 | 51.7658 | 26.9784 |  | 17.0541 | 31.7431 | 17.8143 | 19.3482 | 16.988 | 59.1936 |  | 28.0985 |  |  | 12.525 | 13.6525 | 22.6181 | [6 empty] | 19.0703 |  |  | 17.2748 |  |  | 11.4626 | 17.3113 | 86.6693 | 8.1584 | 14.1473 | 58.9468 | 8.8847 | 13.0767 | 63.2631 | 13.313 | 53.9479 | 8.7733 | 45.4448 | 9.7365 | 46.2136 | 8.8816 | 15.6297 | 57.1608 | 13.1909 | 15.6779 | 76.442 | 9.5524 | 14.1107 | 65.1831 | 9.6589 | 45.1195 | 12.682 | 50.5882 | 10.4919 | 49.1352 | 0.26366 | 20.207 | 0.48618 | 0.055383 | -37.7503 | 3.1216 | 50.33 | 50.16 | -0.86758 | -0.28953 | 0.17119 | -0.30912 | -0.2047 | -0.82302 | 0.42955 | 0.12648 | 0.019479 | 0.33623 | -0.0093097 | 0.21048 | 0.13904 | 0.26982
42810.4425 | 212 | 18.5684 | 18.6267 | 18.5868 | 18.5858 | 17.8889 | 16.501 | 14.5609 | 16.6517 | 17.1565 | 17.2525 | 17.2523 | 16.7778 | 15.8087 | 14.4197 | 14.9743 | 14.9429 | 15.4957 | 13.3417 | 13.51 | 14.1602 |  |  |  | 16.5566 | 15.877 | 15.9023 | 67.9965 | 68.2552 | 76.4076 | 17.2483 | 16.3454 | 15.6647 | 16.8666 | 16.1348 | 15.7422 | 16.553 | 69.7787 |  | 31.957 | 56.0914 | 59.5127 | 25.5821 |  | 6.5729 | 6.6944 | 6.1112 | 6.3416 | 6.4591 | 7.6819 | 24.4377 | 5.1882 | 6.5355 | 4.9146 | 6.9613 | 8.1531 | 41.9927 | 47.1345 | 43.0269 | 14.9095 |  |  | -0.37762 | -0.095193 | 0.04522 | -0.30819 | 0.00082 | -0.48016 | 0.11687 | -0.11976 | -0.32789 | 0.63804 | -0.11357 | 8.9018 | -0.00042055 | 1.9811 | 15.8925 | 16.7221 | 17.2381 | 17.55 | 17.487 | 16.4525 | 14.7922 | 16.8172 | 17.1573 | 17.4451 | 17.4906 | 17.2097 | 16.3927 | 14.5905 | 12.9061 | 9.6174 | 9.7199 | 9.2873 | 9.6457 | 10.3841 | 9.0687 | 15.9913 | 15.5502 | 15.3944 | 14.3121 | 14.2723 | 14.3501 |  |  |  | 15.9933 | 78.8373 | 63.4299 | 20.5324 | -0.17054 | -0.16747 | 21.4574 |  |  | 10.7002 |  |  | 16.8765 | 16.0671 | 16.5976 | 16.3577 | 15.6219 | 15.205 | 65.3461 | 78.4424 | 51.4994 | 51.8963 | 27.034 |  | 17.1243 | 31.1907 | 17.8746 | 19.2827 | 17.0425 | 59.0202 |  | 28.1967 |  |  | 12.5009 | 13.6559 | 22.7292 | [6 empty] | 19.2192 |  |  | 17.3001 |  |  | 11.4719 | 17.3239 | 86.885 | 8.1739 | 14.131 | 59.1006 | 8.877 | 13.0686 | 63.2969 | 13.3196 | 54.1155 | 8.7712 | 45.5548 | 9.7332 | 46.3651 | 8.8877 | 15.6361 | 57.2693 | 13.2045 | 15.7138 | 76.5032 | 9.5755 | 14.1131 | 65.2885 | 9.7047 | 45.2574 | 12.7131 | 50.8465 | 10.5131 | 49.2962 | 0.27887 | 20.2056 | 0.48778 | 0.05636 | -37.7692 | 3.1217 | 57.88 | 49.06 | -0.80067 | -0.35969 | 0.24791 | -0.64719 | 0.033442 | -0.80925 | 0.39924 | 0.12728 | 0.036833 | 0.33987 | 0.086224 | 0.28733 | 0.14858 | 0.27022
42810.4425 | 213 | 18.5798 | 18.6283 | 18.5924 | 18.5873 | 17.8909 | 16.5 | 14.5601 | 16.6577 | 17.1547 | 17.2523 | 17.2583 | 16.7833 | 15.8103 | 14.4205 | 14.9694 | 14.9484 | 15.4943 | 13.345 | 13.5151 | 14.1712 |  |  |  | 16.5598 | 15.8825 | 15.9143 | 68.0732 | 68.3399 | 76.4577 | 17.2416 | 16.3449 | 15.6721 | 16.8621 | 16.1377 | 15.7498 | 16.6003 | 69.6713 |  | 32.0456 | 56.228 | 59.6491 | 25.3384 |  | 6.5732 | 6.7036 | 6.1062 | 6.348 | 6.4527 | 7.6636 | 24.8993 | 5.3043 | 6.5305 | 4.9191 | 6.9596 | 8.1521 | 41.9948 | 47.1233 | 43.052 | 14.907 |  |  | -0.12069 | -0.069565 | 0.10633 | -0.29899 | 0.008708 | -0.26396 | 0.32977 | -0.095444 | -0.11636 | -0.10843 | -0.19344 | 8.9023 | -0.00045834 | 1.9719 | 15.8882 | 16.7234 | 17.2352 | 17.5484 | 17.4969 | 16.4515 | 14.7953 | 16.8203 | 17.1622 | 17.4459 | 17.4942 | 17.2106 | 16.3841 | 14.5825 | 12.2844 | 9.4669 | 9.0972 | 8.8118 | 9.3066 | 10.3816 | 9.0694 | 15.9872 | 15.5554 | 15.4003 | 14.3127 | 14.2717 | 14.3458 |  |  |  | 16.0362 | 78.7545 | 63.4267 | 20.5595 | -0.048373 | -0.04966 | 21.4736 |  |  | 10.695 |  |  | 16.8802 | 16.0694 | 16.6247 | 16.3486 | 15.6185 | 15.2044 | 65.4365 | 78.5242 | 51.6055 | 52.0393 | 26.6171 |  | 17.1973 | 31.2462 | 17.927 | 19.2238 | 17.0781 | 59.0477 |  | 28.2886 |  |  | 12.4922 | 13.6614 | 22.841 | [6 empty] | 19.3357 |  |  | 17.3144 |  |  | 11.4849 | 17.3487 | 87.1792 | 8.2022 | 14.1373 | 59.2554 | 8.8804 | 13.0832 | 63.3927 | 13.3396 | 54.2357 | 8.7914 | 45.6297 | 9.7372 | 46.4802 | 8.91 | 15.7037 | 57.4171 | 13.2095 | 15.7434 | 76.5185 | 9.5778 | 14.1103 | 65.2843 | 9.7435 | 45.3601 | 12.7268 | 50.9814 | 10.5169 | 49.4244 | 0.16216 | 20.2032 | 0.48923 | 0.056049 | -37.7441 | 3.1217 | 56.66 | 49.18 | -0.45268 | -0.30749 | 0.38016 | -0.63747 | 0.10898 | -0.6 | 0.67063 | 0.14129 | 0.037042 | 0.34269 | 0.15501 | 0.3566 | 0.15692 | 0.2709
42810.4425 | 214 | 18.5657 | 18.6274 | 18.5927 | 18.5811 | 17.8895 | 16.4981 | 14.5526 | 16.6624 | 17.1501 | 17.2512 | 17.2557 | 16.7871 | 15.8042 | 14.4202 | 14.9712 | 14.9417 | 15.4892 | 13.3394 | 13.5054 | 14.1619 |  |  |  | 16.5539 | 15.8812 | 15.9138 | 68.1505 | 68.4043 | 76.6714 | 17.2402 | 16.3461 | 15.6706 | 16.8654 | 16.1381 | 15.7621 | 16.6399 | 69.3058 |  | 32.132 | 56.3504 | 59.759 | 24.9998 |  | 6.5706 | 6.6987 | 6.107 | 6.3381 | 6.43 | 7.6403 | 25.4836 | 5.5026 | 6.5264 | 4.9455 | 6.9574 | 8.1545 | 42.0144 | 47.1156 | 43.0753 | 14.8992 |  |  | -0.090461 | -0.22136 | 0.097788 | -0.24116 | -0.03072 | -0.16474 | 0.073496 | -0.20387 | -0.14516 | -0.90042 | -0.14695 | 8.9026 | -0.00043862 | 1.9726 | 15.8888 | 16.7251 | 17.24 | 17.552 | 17.5002 | 16.4558 | 14.8 | 16.8195 | 17.1571 | 17.4484 | 17.4962 | 17.2146 | 16.3884 | 14.5863 | 12.8579 | 9.4367 | 8.675 | 8.451 | 8.9037 | 10.4044 | 9.0681 | 15.9844 | 15.5569 | 15.3976 | 14.3113 | 14.2646 | 14.3473 |  |  |  | 16.0726 | 78.7431 | 63.3823 | 20.4743 | 0.061234 | -0.032157 | 21.5051 |  |  | 10.6926 |  |  | 16.8661 | 16.062 | 16.635 | 16.3418 | 15.6184 | 15.2053 | 65.5338 | 78.5315 | 51.6873 | 52.1917 | 25.7807 |  | 17.2495 | 32.3385 | 17.985 | 19.1774 | 17.1245 | 59.3162 |  | 28.3589 |  |  | 12.4541 | 13.6825 | 22.6326 | [6 empty] | 19.344 |  |  | 17.3252 |  |  | 11.5066 | 17.369 | 87.3802 | 8.2219 | 14.2438 | 59.3152 | 8.8743 | 13.1038 | 63.6075 | 13.3502 | 54.3056 | 8.8027 | 45.7219 | 9.7486 | 46.5842 | 8.9707 | 15.7281 | 57.5959 | 13.2192 | 15.7423 | 76.5205 | 9.5788 | 14.1145 | 65.2508 | 9.7534 | 45.4593 | 12.732 | 51.0357 | 10.5271 | 49.5636 | 0.2885 | 20.2035 | 0.49037 | 0.056411 | -37.7384 | 3.1217 | 55.17 | 49.59 | -0.39203 | -0.5485 | 0.36456 | -0.57251 | -0.20468 | -0.47398 | 0.31658 | 0.16626 | 0.0086338 | 0.34552 | 0.093937 | 0.40335 | 0.16765 | 0.27448
42810.4425 | 215 | 18.566 | 18.6221 | 18.5809 | 18.5785 | 17.8862 | 16.4922 | 14.5394 | 16.6591 | 17.1472 | 17.2409 | 17.2489 | 16.7823 | 15.8049 | 14.413 | 14.9778 | 14.9445 | 15.4883 | 13.3474 | 13.5125 | 14.172 |  |  |  | 16.5645 | 15.8785 | 15.9428 | 68.2724 | 68.4974 | 77.0302 | 17.2341 | 16.3422 | 15.6796 | 16.8608 | 16.1319 | 15.7538 | 16.6822 | 69.0776 |  | 32.2332 | 56.4847 | 59.8552 | 24.599 |  | 6.5692 | 6.6941 | 6.1033 | 6.338 | 6.4203 | 7.6305 | 25.6709 | 5.6324 | 6.5366 | 5.041 | 6.9578 | 8.1435 | 42.0317 | 47.1097 | 43.0831 | 14.8834 |  |  | -0.34871 | -0.091909 | 0.025508 | -0.17085 | -0.051748 | -0.17 | 0.30414 | -0.11319 | -1.0214 | -0.35369 | -0.261 | 8.9023 | -0.00047476 | 1.9757 | 15.8885 | 16.7268 | 17.2372 | 17.5466 | 17.4965 | 16.4546 | 14.7989 | 16.8122 | 17.1492 | 17.4503 | 17.4938 | 17.2127 | 16.3871 | 14.5805 | 14.107 | 9.3648 | 8.3451 | 8.1796 | 8.4995 | 10.4325 | 9.0683 | 15.9878 | 15.5637 | 15.3992 | 14.3092 | 14.2703 | 14.3538 |  |  |  | 16.1179 | 78.8893 | 63.4452 | 20.3105 | -0.026289 | -0.15618 | 21.6923 |  |  | 10.6962 |  |  | 16.8768 | 16.0696 | 16.6453 | 16.3509 | 15.6188 | 15.2129 | 65.5577 | 78.6581 | 51.8177 | 52.2961 | 25.1751 |  | 17.31 | 33.4509 | 18.0637 | 18.9675 | 17.1691 | 59.4375 |  | 28.4574 |  |  | 12.4463 | 13.7137 | 22.4653 | [6 empty] | 19.2171 |  |  | 17.36 |  |  | 11.5034 | 17.3834 | 87.3749 | 8.2398 | 14.3398 | 59.2667 | 8.8832 | 13.1125 | 63.7988 | 13.3588 | 54.4097 | 8.7986 | 45.8015 | 9.7557 | 46.6568 | 8.9978 | 15.7616 | 57.689 | 13.2353 | 15.7422 | 76.5502 | 9.5769 | 14.1447 | 65.3304 | 9.751 | 45.5694 | 12.741 | 51.2614 | 10.5453 | 49.7145 | 0.26501 | 20.1921 | 0.49121 | 0.056266 | -37.746 | 3.1217 | 69.85 | 48.82 | -0.7701 | -0.35343 | 0.18619 | -0.48187 | -0.26564 | -0.48147 | 0.64401 | 0.1851 | -0.019637 | 0.35284 | -0.041582 | 0.44005 | 0.18019 | 0.28053
42810.4425 | 216 | 18.5556 | 18.6088 | 18.5742 | 18.5695 | 17.8811 | 16.4895 | 14.5408 | 16.6491 | 17.1448 | 17.2396 | 17.2394 | 16.7751 | 15.7984 | 14.3979 | 14.9691 | 14.9379 | 15.4871 | 13.3396 | 13.51 | 14.1731 |  |  |  | 16.5648 | 15.8797 | 15.9524 | 68.3845 | 68.5709 | 77.0419 | 17.2323 | 16.3456 | 15.6825 | 16.8638 | 16.1244 | 15.7619 | 16.7127 | 69.0523 |  | 32.3709 | 56.616 | 59.9283 | 24.5417 |  | 6.5717 | 6.6986 | 6.1134 | 6.3467 | 6.4283 | 7.6133 | 25.8685 | 5.7276 | 6.5423 | 5.2191 | 6.9666 | 8.139 | 42.0589 | 47.1065 | 43.1002 | 14.8704 |  |  | -0.31323 | -0.15433 | 0.088588 | -0.3095 | 0.057332 | -0.40787 | 0.31597 | -0.50023 | -0.23428 | -0.3883 | -0.2916 | 8.9022 | -0.00044684 | 1.9789 | 15.8917 | 16.724 | 17.2309 | 17.5469 | 17.5013 | 16.4497 | 14.8016 | 16.8124 | 17.1496 | 17.4543 | 17.4946 | 17.214 | 16.3821 | 14.5792 | 15.2534 | 9.8738 | 8.1245 | 8.1081 | 8.255 | 10.4618 | 9.0735 | 15.9899 | 15.5563 | 15.389 | 14.3093 | 14.2645 | 14.3605 |  |  |  | 16.1386 | 79.0289 | 63.6185 | 20.0392 | -0.049588 | -0.21396 | 21.845 |  |  | 10.6974 |  |  | 16.8666 | 16.0657 | 16.6711 | 16.3378 | 15.6168 | 15.2159 | 65.6242 | 78.7784 | 51.9258 | 52.422 | 25.5792 |  | 17.3572 | 34.7324 | 18.1324 | 18.7493 | 17.1912 | 58.9124 |  | 28.5465 |  |  | 12.4507 | 13.6904 | 22.6432 | [6 empty] | 19.029 |  |  | 17.3918 |  |  | 11.5153 | 17.4199 | 87.3193 | 8.2388 | 14.3434 | 59.2546 | 8.8921 | 13.1158 | 63.9657 | 13.3721 | 54.6847 | 8.8001 | 45.8135 | 9.7576 | 46.6857 | 8.9851 | 15.8103 | 57.7954 | 13.2504 | 15.7665 | 76.5828 | 9.584 | 14.1694 | 65.3554 | 9.7801 | 45.6562 | 12.7587 | 51.4908 | 10.5708 | 49.8855 | 0.38249 | 20.1973 | 0.49286 | 0.055492 | -37.7401 | 3.1217 | 61.62 | 49.66 | -0.72987 | -0.45799 | 0.34699 | -0.64858 | 0.2796 | -0.74576 | 0.65639 | 0.17545 | -0.052942 | 0.35964 | -0.16556 | 0.46516 | 0.1828 | 0.28876
42810.4425 | 217 | 18.5542 | 18.6145 | 18.5844 | 18.5691 | 17.8844 | 16.4852 | 14.5494 | 16.6612 | 17.1487 | 17.2424 | 17.2486 | 16.7791 | 15.8058 | 14.41 | 14.9643 | 14.9476 | 15.4815 | 13.3397 | 13.5179 | 14.1811 |  |  |  | 16.5532 | 15.883 | 15.9596 | 68.4901 | 68.6859 | 77.1408 | 17.2251 | 16.3329 | 15.6866 | 16.8591 | 16.1259 | 15.7698 | 16.7561 | 70.028 |  | 32.4943 | 56.7407 | 60.0151 | 25.1172 |  | 6.5594 | 6.6821 | 6.106 | 6.3287 | 6.4076 | 7.5879 | 26.0102 | 5.7557 | 6.5428 | 5.3204 | 6.9654 | 8.1379 | 42.0871 | 47.0996 | 43.1141 | 14.8663 |  |  | -0.17589 | -0.053137 | -0.011948 | -0.13405 | -0.07606 | -0.14108 | 0.2726 | -0.38655 | -0.29325 | -0.39166 | -0.29438 | 8.9025 | -0.00044848 | 1.9869 | 15.8904 | 16.7236 | 17.2405 | 17.5533 | 17.5052 | 16.4534 | 14.7982 | 16.8142 | 17.1566 | 17.45 | 17.4913 | 17.208 | 16.3804 | 14.5884 | 15.734 | 10.2013 | 8.651 | 8.0084 | 8.1568 | 10.476 | 9.0717 | 15.9936 | 15.5687 | 15.391 | 14.305 | 14.2752 | 14.3692 |  |  |  | 16.1768 | 79.1352 | 63.7994 | 19.7715 | -0.19911 | -0.30448 | 21.9103 |  |  | 10.6986 |  |  | 16.8802 | 16.0717 | 16.6874 | 16.3437 | 15.6134 | 15.2249 | 65.7456 | 78.9335 | 52.0611 | 52.5437 | 26.1122 |  | 17.4154 | 34.9793 | 18.1813 | 18.5855 | 17.2152 | 58.8987 |  | 28.629 |  |  | 12.4678 | 13.6846 | 22.5753 | [6 empty] | 18.921 |  |  | 17.4018 |  |  | 11.5211 | 17.4335 | 87.3666 | 8.1952 | 14.3067 | 59.3185 | 8.8945 | 13.1135 | 64.0774 | 13.3694 | 55.1268 | 8.8233 | 45.8015 | 9.7675 | 46.7634 | 8.9509 | 15.8324 | 57.8913 | 13.2504 | 15.8006 | 76.5666 | 9.5874 | 14.1529 | 65.3882 | 9.8015 | 45.7614 | 12.7471 | 51.6383 | 10.5663 | 49.9519 | 0.24979 | 20.1968 | 0.49441 | 0.055108 | -37.7524 | 3.1217 | 64.72 | 49.37 | -0.54702 | -0.26873 | -0.12743 | -0.42682 | -0.32203 | -0.43859 | 0.60965 | 0.16259 | -0.058168 | 0.36499 | -0.21731 | 0.40645 | 0.16826 | 0.29746
42810.4426 | 218 | 18.5532 | 18.6199 | 18.5902 | 18.5775 | 17.8779 | 16.4955 | 14.5429 | 16.6577 | 17.1421 | 17.245 | 17.2496 | 16.7777 | 15.8025 | 14.4125 | 14.9595 | 14.9324 | 15.4811 | 13.3317 | 13.5102 | 14.173 |  |  |  | 16.552 | 15.8815 | 15.9659 | 68.6964 | 68.8118 | 77.3181 | 17.2184 | 16.3362 | 15.6907 | 16.8583 | 16.1242 | 15.7824 | 16.8072 | 70.7739 |  | 32.6056 | 56.8844 | 60.1092 | 25.2862 |  | 6.5537 | 6.6822 | 6.0981 | 6.3217 | 6.3988 | 7.5761 | 25.9764 | 5.8454 | 6.5466 | 5.3921 | 6.9708 | 8.1302 | 42.1115 | 47.0999 | 43.119 | 14.858 |  |  | -0.27248 | 0.006659 | -0.13417 | -0.37324 | -0.10629 | -0.77586 | -0.30566 | -0.34121 | -0.23039 | -0.34466 | -0.073627 | 8.9031 | -0.00043534 | 1.9961 | 15.8777 | 16.7121 | 17.2335 | 17.5357 | 17.4865 | 16.4414 | 14.7843 | 16.7999 | 17.1445 | 17.4446 | 17.4783 | 17.2041 | 16.3762 | 14.5864 | 15.2619 | 10.035 | 9.2561 | 8.2672 | 8.0924 | 10.4884 | 9.0833 | 15.9887 | 15.5723 | 15.4001 | 14.309 | 14.2768 | 14.3656 |  |  |  | 16.1957 | 79.1934 | 64.0253 | 19.5648 | -0.14501 | -0.10424 | 21.9354 |  |  | 10.7152 |  |  | 16.8872 | 16.0836 | 16.7055 | 16.3598 | 15.6266 | 15.2498 | 65.9737 | 79.0052 | 52.1629 | 52.7077 | 25.411 |  | 17.4777 | 34.7506 | 18.2356 | 18.5342 | 17.2497 | 59.2279 |  | 28.7104 |  |  | 12.4535 | 13.6931 | 22.3946 | [6 empty] | 18.8882 |  |  | 17.3965 |  |  | 11.5156 | 17.4383 | 87.3325 | 8.1843 | 14.2807 | 59.4291 | 8.8963 | 13.1232 | 64.2031 | 13.387 | 55.4463 | 8.8218 | 45.8738 | 9.7549 | 46.8789 | 8.9195 | 15.88 | 58.0387 | 13.2631 | 15.8269 | 76.5986 | 9.5889 | 14.1784 | 65.4865 | 9.8237 | 45.8712 | 12.763 | 51.801 | 10.5851 | 50.0125 | 0.28349 | 20.1898 | 0.49509 | 0.053147 | -37.7484 | 3.1217 | 77.73 | 48.99 | -0.68102 | 0.095131 | -0.42702 | -0.71221 | -0.38067 | -1.0285 | -0.64554 | 0.18414 | -0.050004 | 0.36756 | -0.16341 | 0.34057 | 0.16526 | 0.30383
42810.4426 | 219 | 18.5461 | 18.616 | 18.5828 | 18.5751 | 17.882 | 16.4933 | 14.5405 | 16.6581 | 17.1461 | 17.2485 | 17.2529 | 16.7775 | 15.7999 | 14.4136 | 14.9594 | 14.9431 | 15.4738 | 13.3367 | 13.5157 | 14.1765 |  |  |  | 16.5544 | 15.8775 | 15.983 | 68.8526 | 68.9078 | 77.4415 | 17.2215 | 16.3334 | 15.7004 | 16.8569 | 16.13 | 15.7885 | 16.8497 | 70.9895 |  | 32.7065 | 57.0104 | 60.2534 | 24.5751 |  | 6.5518 | 6.6806 | 6.0919 | 6.3241 | 6.3766 | 7.5508 | 25.6982 | 5.7408 | 6.5485 | 5.3261 | 6.9776 | 8.1397 | 42.1465 | 47.1077 | 43.1284 | 14.8485 |  |  | -0.1956 | -0.002541 | 0.041276 | -0.19056 | -0.07606 | -0.22585 | -0.007984 | -0.26301 | -0.5112 | -0.48166 | -0.40685 | 8.9026 | -0.00044191 | 2.0012 | 15.8824 | 16.7171 | 17.2334 | 17.5383 | 17.4852 | 16.4415 | 14.7954 | 16.8101 | 17.1493 | 17.4456 | 17.4839 | 17.1994 | 16.3838 | 14.5738 | 14.6311 | 9.822 | 8.9383 | 8.5537 | 8.2319 | 10.4921 | 9.0858 | 15.9848 | 15.5587 | 15.3901 | 14.3133 | 14.2673 | 14.369 |  |  |  | 16.2293 | 79.3084 | 64.3092 | 19.4053 | -0.044928 | 0.12028 | 21.9309 |  |  | 10.7037 |  |  | 16.8752 | 16.0733 | 16.7205 | 16.3426 | 15.623 | 15.2523 | 66.1933 | 79.1538 | 52.2452 | 52.8079 | 24.6064 |  | 17.5441 | 34.1873 | 18.2852 | 18.732 | 17.3002 | 59.2248 |  | 28.7992 |  |  | 12.3903 | 13.6956 | 22.374 | [6 empty] | 18.926 |  |  | 17.4028 |  |  | 11.5157 | 17.443 | 87.4265 | 8.179 | 14.2542 | 59.5616 | 8.8979 | 13.1312 | 64.3231 | 13.3925 | 55.5345 | 8.8264 | 45.9918 | 9.754 | 47.0036 | 8.8909 | 15.927 | 58.1326 | 13.2727 | 15.8414 | 76.6568 | 9.5919 | 14.2036 | 65.5842 | 9.8359 | 45.927 | 12.7807 | 52.0583 | 10.5982 | 50.1259 | 0.16408 | 20.1904 | 0.49613 | 0.053595 | -37.75 | 3.1217 | 52.41 | 50.18 | -0.5771 | -0.058765 | 0.23684 | -0.5089 | -0.32201 | -0.55488 | -0.10433 | 0.20871 | -0.032699 | 0.36375 | -0.092881 | 0.37616 | 0.18643 | 0.30938
42810.4426 | 220 | 18.5486 | 18.6206 | 18.5832 | 18.571 | 17.8787 | 16.4967 | 14.54 | 16.6552 | 17.1461 | 17.2537 | 17.2491 | 16.7776 | 15.8059 | 14.4166 | 14.955 | 14.9406 | 15.4781 | 13.3373 | 13.52 | 14.1881 |  |  |  | 16.5549 | 15.8855 | 16.0013 | 68.9264 | 68.9066 | 77.0725 | 17.2246 | 16.3415 | 15.712 | 16.8629 | 16.1402 | 15.8018 | 16.8892 | 70.9622 |  | 32.8143 | 57.1384 | 60.4035 | 24.018 |  | 6.5502 | 6.681 | 6.0959 | 6.321 | 6.3817 | 7.5344 | 25.4722 | 5.5161 | 6.5505 | 5.2372 | 6.9809 | 8.1287 | 42.1658 | 47.1121 | 43.125 | 14.8349 |  |  | -0.1726 | -0.20953 | 0.041936 | -0.14982 | 0.007392 | -0.012944 | 0.28378 | -0.14473 | -0.45671 | 0.0069606 | -0.27272 | 8.9018 | -0.00045669 | 2.0024 | 15.8843 | 16.7241 | 17.2348 | 17.5439 | 17.4932 | 16.4477 | 14.792 | 16.8154 | 17.1513 | 17.4471 | 17.4894 | 17.2097 | 16.3823 | 14.5792 | 13.9598 | 9.7613 | 8.6869 | 8.5987 | 8.4569 | 10.5023 | 9.098 | 15.9886 | 15.5576 | 15.3907 | 14.318 | 14.2805 | 14.3794 |  |  |  | 16.2681 | 79.4916 | 64.5097 | 19.2549 | -0.12111 | -0.18479 | 21.901 |  |  | 10.6896 |  |  | 16.8713 | 16.0677 | 16.7396 | 16.3375 | 15.6163 | 15.2411 | 66.3373 | 79.257 | 52.2874 | 52.8616 | 24.0964 |  | 17.6109 | 32.9381 | 18.3394 | 18.9356 | 17.3528 | 59.0551 |  | 28.8995 |  |  | 12.4102 | 13.6938 | 22.4553 | [6 empty] | 18.9658 |  |  | 17.4326 |  |  | 11.5097 | 17.4559 | 87.5446 | 8.1416 | 14.2262 | 59.684 | 8.8933 | 13.1207 | 64.3861 | 13.3916 | 55.6558 | 8.8247 | 46.1043 | 9.7582 | 47.0756 | 8.8674 | 15.9609 | 58.2129 | 13.2818 | 15.8448 | 76.6948 | 9.5871 | 14.1913 | 65.6838 | 9.8557 | 45.9812 | 12.8085 | 52.2627 | 10.596 | 50.2765 | 0.25807 | 20.1889 | 0.4988 | 0.055709 | -37.759 | 3.1217 | 53.1 | 49.15 | -0.54183 | -0.53363 | 0.23873 | -0.45123 | 0.10038 | -0.13283 | 0.62196 | 0.2251 | 0.0038109 | 0.35985 | -0.017112 | 0.40552 | 0.20322 | 0.31485
42810.4426 | 221 | 18.5431 | 18.6127 | 18.5835 | 18.5753 | 17.88 | 16.4883 | 14.537 | 16.6573 | 17.1422 | 17.239 | 17.2388 | 16.7687 | 15.7977 | 14.4036 | 14.9564 | 14.9389 | 15.4775 | 13.3397 | 13.5125 | 14.1898 |  |  |  | 16.5609 | 15.8866 | 16.0087 | 68.9504 | 68.8944 | 76.7901 | 17.2118 | 16.3409 | 15.7115 | 16.8507 | 16.1259 | 15.8087 | 16.9174 | 70.8346 |  | 32.8964 | 57.2531 | 60.5151 | 23.8079 |  | 6.5625 | 6.6938 | 6.1031 | 6.3179 | 6.3873 | 7.5223 | 25.387 | 5.2961 | 6.5511 | 5.1499 | 6.9792 | 8.134 | 42.2024 | 47.1366 | 43.1432 | 14.8343 |  |  | -0.35199 | -0.17076 | -0.049404 | -0.18136 | -0.013636 | 0.091536 | 0.31269 | -0.29915 | -0.0003738 | -1.0974 | -0.26875 | 8.9027 | -0.00048298 | 2.0003 | 15.8773 | 16.7218 | 17.2347 | 17.5417 | 17.4857 | 16.4507 | 14.7919 | 16.8122 | 17.1481 | 17.4428 | 17.4867 | 17.2067 | 16.3786 | 14.5758 | 13.5385 | 9.7599 | 8.625 | 8.3309 | 8.4559 | 10.5069 | 9.0938 | 15.99 | 15.5553 | 15.3936 | 14.3155 | 14.2857 | 14.3843 |  |  |  | 16.2982 | 79.6307 | 64.6558 | 19.1596 | -0.24327 | -0.18291 | 21.8545 |  |  | 10.6887 |  |  | 16.8748 | 16.0754 | 16.7608 | 16.3465 | 15.6194 | 15.2566 | 66.4396 | 79.3202 | 52.3336 | 52.9002 | 23.5291 |  | 17.666 | 32.4938 | 18.3778 | 18.9215 | 17.3824 | 58.525 |  | 28.9975 |  |  | 12.4389 | 13.7193 | 22.5263 | [6 empty] | 18.9297 |  |  | 17.4532 |  |  | 11.531 | 17.4722 | 87.6512 | 8.154 | 14.2375 | 59.796 | 8.887 | 13.1281 | 64.4319 | 13.412 | 55.6934 | 8.8312 | 46.2147 | 9.7691 | 47.159 | 8.8874 | 16.0261 | 58.3115 | 13.3009 | 15.8582 | 76.7093 | 9.5957 | 14.2009 | 65.7694 | 9.8718 | 46.036 | 12.8284 | 52.4478 | 10.599 | 50.3965 | 0.37999 | 20.1854 | 0.50008 | 0.056773 | -37.7476 | 3.1217 | 59.21 | 49.17 | -0.77345 | -0.48175 | -0.25912 | -0.49648 | -0.13634 | 0.35323 | 0.65286 | 0.2427 | 0.017434 | 0.36123 | 0.030234 | 0.41192 | 0.21 | 0.3185
42810.4426 | 222 | 18.5339 | 18.6069 | 18.5753 | 18.5669 | 17.8748 | 16.4887 | 14.5429 | 16.6437 | 17.1396 | 17.2355 | 17.2551 | 16.7699 | 15.8004 | 14.4097 | 14.9549 | 14.9371 | 15.4752 | 13.3431 | 13.5087 | 14.1809 |  |  |  | 16.561 | 15.8874 | 16.015 | 69.0175 | 68.8664 | 77.0244 | 17.2093 | 16.3335 | 15.7127 | 16.8498 | 16.1327 | 15.8097 | 16.9695 | 70.4518 |  | 32.9868 | 57.3855 | 60.626 | 25.7141 |  | 6.5595 | 6.6917 | 6.1095 | 6.3202 | 6.3817 | 7.514 | 25.2892 | 5.1744 | 6.5472 | 5.1084 | 6.9792 | 8.1322 | 42.23 | 47.1525 | 43.149 | 14.8228 |  |  | -0.22451 | -0.097165 | -0.031664 | -0.23459 | 0.07376 | -0.089172 | 0.41388 | -0.33595 | -0.36895 | 0.8791 | -0.25047 | 8.9024 | -0.00045177 | 1.9989 | 15.8834 | 16.722 | 17.2362 | 17.5479 | 17.4926 | 16.4517 | 14.7923 | 16.8124 | 17.1509 | 17.451 | 17.4881 | 17.2071 | 16.3819 | 14.5777 | 13.8123 | 9.7164 | 8.9941 | 8.0218 | 8.2544 | 10.5194 | 9.0924 | 15.9877 | 15.5624 | 15.4021 | 14.3195 | 14.286 | 14.3846 |  |  |  | 16.3481 | 79.8327 | 65.2342 | 19.0649 | -0.010284 | -0.16427 | 21.8642 |  |  | 10.6987 |  |  | 16.8877 | 16.0701 | 16.7738 | 16.3508 | 15.6285 | 15.2639 | 66.5051 | 79.5369 | 52.3885 | 52.9679 | 22.8471 |  | 17.7234 | 32.4387 | 18.4329 | 18.743 | 17.4067 | 58.4557 |  | 29.094 |  |  | 12.4609 | 13.741 | 22.5747 | [6 empty] | 18.8515 |  |  | 17.4585 |  |  | 11.5547 | 17.4872 | 87.4789 | 8.1779 | 14.2355 | 59.9094 | 8.8898 | 13.1366 | 64.4683 | 13.4272 | 55.7277 | 8.8403 | 46.3151 | 9.7665 | 47.2448 | 8.9211 | 16.0878 | 58.3518 | 13.3247 | 15.8775 | 76.7101 | 9.603 | 14.2115 | 65.8173 | 9.8882 | 46.0871 | 12.8329 | 52.7013 | 10.5987 | 50.5569 | 0.26308 | 20.1836 | 0.50109 | 0.05623 | -37.7401 | 3.1217 | 79.58 | 50.4 | -0.61792 | -0.36339 | -0.20745 | -0.56465 | 0.31708 | -0.34864 | 0.7511 | 0.26355 | 0.020807 | 0.367 | 0.0012669 | 0.37073 | 0.15878 | 0.32279
42810.4426 | 223 | 18.5444 | 18.6121 | 18.577 | 18.5754 | 17.8751 | 16.4894 | 14.537 | 16.6495 | 17.145 | 17.2381 | 17.2421 | 16.776 | 15.7925 | 14.4119 | 14.9462 | 14.9274 | 15.4725 | 13.3343 | 13.5143 | 14.1797 |  |  |  | 16.5545 | 15.8798 | 16.0251 | 69.0929 | 68.8749 | 77.1085 | 17.2137 | 16.3274 | 15.7296 | 16.8479 | 16.1319 | 15.8192 | 17.0313 | 70.0781 |  | 33.0808 | 57.4835 | 60.7284 | 26.8904 |  | 6.5585 | 6.6948 | 6.1045 | 6.3143 | 6.3807 | 7.5194 | 24.9593 | 5.0694 | 6.5477 | 5.0564 | 6.9869 | 8.1243 | 42.2556 | 47.1674 | 43.1486 | 14.8109 |  |  | -0.28562 | -0.15433 | 0.10042 | -0.22079 | -0.12666 | 0.069196 | 0.56042 | -0.10333 | -0.44523 | -0.41725 | -0.23596 | 8.9027 | -0.00045177 | 1.9991 | 15.8782 | 16.7181 | 17.2332 | 17.5443 | 17.492 | 16.4429 | 14.7891 | 16.814 | 17.1481 | 17.4494 | 17.4883 | 17.2096 | 16.388 | 14.5756 | 14.5891 | 9.902 | 8.7894 | 7.9431 | 7.9687 | 10.5494 | 9.0987 | 15.9836 | 15.5592 | 15.3946 | 14.3125 | 14.2787 | 14.3884 |  |  |  | 16.3766 | 80.0316 | 65.5525 | 18.8486 | 0.10925 | -0.21697 | 22.0429 |  |  | 10.7003 |  |  | 16.8765 | 16.0675 | 16.7863 | 16.3464 | 15.6209 | 15.2759 | 66.5933 | 79.6561 | 52.4428 | 53.0286 | 22.6282 |  | 17.7759 | 31.6515 | 18.4887 | 18.5127 | 17.4444 | 58.213 |  | 29.1853 |  |  | 12.4725 | 13.7589 | 22.6738 | [6 empty] | 18.7753 |  |  | 17.4555 |  |  | 11.5663 | 17.5006 | 87.3199 | 8.1931 | 14.2496 | 60.0113 | 8.892 | 13.165 | 64.5217 | 13.4425 | 55.8697 | 8.8633 | 46.4599 | 9.7655 | 47.3694 | 8.9457 | 16.142 | 58.3924 | 13.3423 | 15.903 | 76.7421 | 9.5859 | 14.2197 | 65.9118 | 9.8925 | 46.1433 | 12.8351 | 52.7882 | 10.6081 | 50.6978 | 0.34436 | 20.1813 | 0.5017 | 0.055202 | -37.7364 | 3.1217 | 59.7 | 48.86 | -0.69704 | -0.45799 | 0.36943 | -0.54779 | -0.41551 | 0.30712 | 0.87402 | 0.27139 | 0.044535 | 0.37465 | -0.081561 | 0.39421 | 0.12817 | 0.32975
42810.4426 | 224 | 18.539 | 18.6032 | 18.5786 | 18.5766 | 17.8752 | 16.4869 | 14.5346 | 16.6493 | 17.1435 | 17.2407 | 17.2415 | 16.7713 | 15.7911 | 14.4032 | 14.9403 | 14.9325 | 15.4744 | 13.3355 | 13.516 | 14.1906 |  |  |  | 16.5572 | 15.8793 | 16.0422 | 69.1832 | 68.8719 | 77.1907 | 17.2052 | 16.3225 | 15.7398 | 16.8489 | 16.1278 | 15.8293 | 17.0873 | 69.8773 |  | 33.1571 | 57.5756 | 60.8139 | 26.3954 |  | 6.5719 | 6.7013 | 6.1046 | 6.3131 | 6.3743 | 7.5188 | 24.576 | 4.9632 | 6.5479 | 4.9621 | 6.9931 | 8.1209 | 42.2708 | 47.1933 | 43.1653 | 14.8074 |  |  | -0.021465 | -0.2897 | 0.023536 | -0.077538 | -0.034004 | -0.3507 | 0.58342 | -0.28338 | -0.45282 | -0.36334 | -0.05018 | 8.9024 | -0.00047476 | 2.0019 | 15.8728 | 16.7186 | 17.2315 | 17.5385 | 17.4887 | 16.4406 | 14.7928 | 16.8069 | 17.1464 | 17.4393 | 17.4758 | 17.2031 | 16.3766 | 14.5778 | 15.54 | 10.3859 | 9.2622 | 7.7933 | 7.7952 | 10.6009 | 9.1098 | 15.9846 | 15.5605 | 15.3958 | 14.3108 | 14.2834 | 14.3919 |  |  |  | 16.4032 | 80.1196 | 65.587 | 18.7164 | -0.0583 | -0.24934 | 22.1548 |  |  | 10.7007 |  |  | 16.8834 | 16.0703 | 16.8232 | 16.3532 | 15.6206 | 15.2849 | 66.743 | 79.7336 | 52.4786 | 53.1126 | 22.9361 |  | 17.8411 | 31.7112 | 18.5434 | 18.4913 | 17.4865 | 58.4392 |  | 29.2639 |  |  | 12.4974 | 13.7695 | 22.7635 | [6 empty] | 18.7668 |  |  | 17.4418 |  |  | 11.5781 | 17.514 | 87.3859 | 8.1826 | 14.2268 | 60.1525 | 8.887 | 13.1757 | 64.675 | 13.4496 | 55.9347 | 8.8735 | 46.6266 | 9.7705 | 47.5249 | 8.9675 | 16.1711 | 58.4438 | 13.3654 | 15.8975 | 76.7725 | 9.5689 | 14.2323 | 65.9198 | 9.8941 | 46.2282 | 12.8377 | 52.7865 | 10.6158 | 50.84 | 0.37556 | 20.181 | 0.50182 | 0.053451 | -37.7435 | 3.1217 | 58.09 | 48.82 | -0.19111 | -0.62749 | 0.17885 | -0.32463 | -0.21529 | -0.69141 | 0.89177 | 0.26501 | 0.044705 | 0.37665 | -0.18123 | 0.34296 | 0.14378 | 0.33431
42810.4426 | 225 | 18.5328 | 18.6073 | 18.5702 | 18.5632 | 17.8729 | 16.4857 | 14.5311 | 16.6454 | 17.142 | 17.2322 | 17.2459 | 16.7679 | 15.7894 | 14.3898 | 14.938 | 14.9281 | 15.4733 | 13.333 | 13.5158 | 14.1885 |  |  |  | 16.5543 | 15.8837 | 16.0523 | 69.2913 | 68.8547 | 77.2807 | 17.2089 | 16.3264 | 15.7424 | 16.8547 | 16.1238 | 15.8518 | 17.1434 | 69.5943 |  | 33.2508 | 57.6929 | 60.8824 | 26.0212 |  | 6.5799 | 6.7056 | 6.1033 | 6.3112 | 6.3856 | 7.532 | 24.3094 | 4.8842 | 6.5477 | 4.9423 | 6.9976 | 8.1112 | 42.3028 | 47.2006 | 43.1757 | 14.8017 |  |  | -0.22583 | -0.021597 | -0.025092 | -0.24116 | -0.06686 | 0.25647 | 0.54071 | -0.35238 | -0.32399 | -0.48502 | -0.37804 | 8.9025 | -0.00045998 | 2.0007 | 15.8881 | 16.7356 | 17.2401 | 17.5509 | 17.5035 | 16.4448 | 14.7939 | 16.8226 | 17.1555 | 17.4496 | 17.49 | 17.2085 | 16.385 | 14.5859 | 15.3819 | 10.5252 | 10.2533 | 8.2829 | 7.7122 | 10.6204 | 9.1141 | 15.9762 | 15.5567 | 15.3891 | 14.3054 | 14.2848 | 14.3888 |  |  |  | 16.4264 | 80.1395 | 65.5702 | 18.5935 | -0.13448 | -0.095581 | 22.242 |  |  | 10.7124 |  |  | 16.8821 | 16.0763 | 16.8349 | 16.3505 | 15.6218 | 15.2906 | 66.8222 | 79.8179 | 52.497 | 53.1553 | 23.1392 |  | 17.8983 | 31.7932 | 18.5972 | 18.4891 | 17.5182 | 59.1305 |  | 29.3421 |  |  | 12.5305 | 13.7833 | 22.8278 | [6 empty] | 18.7635 |  |  | 17.462 |  |  | 11.5935 | 17.5234 | 87.6936 | 8.1843 | 14.1978 | 60.28 | 8.8816 | 13.1765 | 64.8085 | 13.4483 | 55.8762 | 8.8857 | 46.7985 | 9.7722 | 47.6599 | 8.9955 | 16.171 | 58.4754 | 13.3951 | 15.9136 | 76.8062 | 9.5831 | 14.2757 | 65.8414 | 9.8994 | 46.298 | 12.8435 | 52.8992 | 10.6219 | 50.9846 | 0.37036 | 20.1787 | 0.50485 | 0.056389 | -37.7319 | 3.1218 | 55.31 | 49.74 | -0.61995 | -0.17133 | -0.18467 | -0.57252 | -0.3019 | 0.59128 | 0.85853 | 0.26128 | 0.044225 | 0.37777 | -0.16139 | 0.23334 | 0.15605 | 0.33849
42810.4427 | 226 | 18.5274 | 18.6087 | 18.5745 | 18.5631 | 17.8767 | 16.4856 | 14.5349 | 16.6483 | 17.1463 | 17.2341 | 17.2408 | 16.7619 | 15.7926 | 14.398 | 14.9347 | 14.9273 | 15.4695 | 13.3244 | 13.5108 | 14.1939 |  |  |  | 16.5457 | 15.8756 | 16.0633 | 69.3559 | 68.8329 | 77.1639 | 17.2045 | 16.3261 | 15.7373 | 16.8528 | 16.1255 | 15.8558 | 17.1986 | 69.5803 |  | 33.3461 | 57.8204 | 60.9685 | 25.9694 |  | 6.5931 | 6.7136 | 6.1058 | 6.3185 | 6.399 | 7.5452 | 24.0399 | 4.8553 | 6.5565 | 4.883 | 6.9988 | 8.1121 | 42.3302 | 47.2008 | 43.1866 | 14.7936 |  |  | -0.13318 | 0.080915 | 0.1543 | 0.099882 | -0.046492 | -0.20745 | 0.35672 | -0.25052 | 0.5554 | -0.56453 | -0.21311 | 8.9015 | -0.00046984 | 1.9943 | 15.8813 | 16.7222 | 17.2341 | 17.5363 | 17.4855 | 16.4466 | 14.7897 | 16.8169 | 17.151 | 17.4495 | 17.4871 | 17.2055 | 16.3884 | 14.5861 | 15.0086 | 10.2622 | 10.2176 | 8.864 | 8.1218 | 10.6329 | 9.1266 | 15.9906 | 15.5587 | 15.3985 | 14.3134 | 14.2892 | 14.4011 |  |  |  | 16.472 | 80.0453 | 65.6061 | 18.4222 | -0.20843 | -0.093699 | 22.3156 |  |  | 10.7136 |  |  | 16.8752 | 16.0759 | 16.8453 | 16.349 | 15.6236 | 15.2981 | 66.8944 | 79.8605 | 52.5243 | 53.2002 | 23.4893 |  | 17.9651 | 32.04 | 18.6563 | 18.3802 | 17.5611 | 60.0144 |  | 29.4338 |  |  | 12.5561 | 13.8009 | 22.9713 | [6 empty] | 18.6545 |  |  | 17.4834 |  |  | 11.6007 | 17.5367 | 87.9163 | 8.1943 | 14.1999 | 60.377 | 8.8698 | 13.1772 | 64.8884 | 13.4472 | 55.8236 | 8.9022 | 46.9499 | 9.7713 | 47.7615 | 9.0234 | 16.1543 | 58.5396 | 13.413 | 15.9215 | 76.8737 | 9.5933 | 14.3029 | 65.9053 | 9.907 | 46.3694 | 12.8508 | 53.015 | 10.618 | 51.0897 | 0.2808 | 20.1769 | 0.50602 | 0.056744 | -37.7391 | 3.1218 | 68.09 | 49.09 | -0.476 | 0.33163 | 0.45796 | 0.36845 | -0.25175 | -0.53179 | 0.69734 | 0.25378 | 0.039345 | 0.38222 | -0.11846 | 0.23877 | 0.15933 | 0.34477
42810.4427 | 227 | 18.5328 | 18.6165 | 18.5856 | 18.5682 | 17.8817 | 16.4916 | 14.5425 | 16.6465 | 17.1481 | 17.2454 | 17.2451 | 16.7734 | 15.7982 | 14.407 | 14.9335 | 14.9296 | 15.4747 | 13.329 | 13.518 | 14.2027 |  |  |  | 16.5535 | 15.878 | 16.0782 | 69.3723 | 68.8368 | 76.6527 | 17.1986 | 16.3171 | 15.7396 | 16.8445 | 16.1162 | 15.8612 | 17.2586 | 70.022 |  | 33.4326 | 57.94 | 61.0502 | 26.4216 |  | 6.5886 | 6.7128 | 6.0933 | 6.3032 | 6.3823 | 7.522 | 23.6629 | 4.851 | 6.5497 | 4.8342 | 6.9895 | 8.1175 | 42.3426 | 47.1974 | 43.199 | 14.8023 |  |  | -0.32111 | 0.076315 | -0.090144 | -0.01577 | -0.20683 | -0.095084 | 0.48814 | -0.2525 | -0.49524 | -2.3103 | -0.25365 | 8.9019 | -0.00045012 | 1.9921 | 15.8811 | 16.7249 | 17.2417 | 17.5448 | 17.4942 | 16.4514 | 14.7928 | 16.8115 | 17.1503 | 17.4482 | 17.4949 | 17.2059 | 16.3868 | 14.5804 | 15.3512 | 10.1494 | 9.8224 | 8.7896 | 8.3195 | 10.667 | 9.1318 | 15.9842 | 15.5663 | 15.4022 | 14.3178 | 14.2845 | 14.4025 |  |  |  | 16.5055 | 79.8371 | 65.4268 | 18.2911 | -0.046954 | -0.19288 | 22.3732 |  |  | 10.7083 |  |  | 16.8719 | 16.0769 | 16.8694 | 16.3496 | 15.6192 | 15.293 | 67.0359 | 79.9079 | 52.5594 | 53.2519 | 24.0692 |  | 18.0261 | 32.6012 | 18.7201 | 18.4214 | 17.6006 | 59.6669 |  | 29.5201 |  |  | 12.553 | 13.7986 | 23.1538 | [6 empty] | 18.5793 |  |  | 17.4938 |  |  | 11.6122 | 17.5604 | 88.0658 | 8.2117 | 14.2389 | 60.4807 | 8.8829 | 13.2191 | 64.9616 | 13.4553 | 55.8335 | 8.9155 | 47.0944 | 9.7804 | 47.8671 | 9.0376 | 16.1391 | 58.5907 | 13.4225 | 15.9248 | 76.9718 | 9.5911 | 14.3025 | 66.0368 | 9.9129 | 46.4438 | 12.867 | 53.0449 | 10.6053 | 51.2055 | 0.27829 | 20.1759 | 0.50696 | 0.056512 | -37.7378 | 3.1217 | 57.96 | 49.35 | -0.73859 | 0.32207 | -0.35003 | -0.1464 | -0.53097 | -0.36001 | 0.81572 | 0.23971 | 0.025888 | 0.3824 | -0.15257 | 0.28328 | 0.14876 | 0.34953
42810.4427 | 228 | 18.5223 | 18.6023 | 18.5741 | 18.5552 | 17.8741 | 16.4857 | 14.5327 | 16.6452 | 17.1337 | 17.2325 | 17.237 | 16.7693 | 15.786 | 14.3948 | 14.9368 | 14.9314 | 15.4686 | 13.3334 | 13.5159 | 14.2029 |  |  |  | 16.5539 | 15.8887 | 16.09 | 69.3513 | 68.8424 | 76.2385 | 17.1994 | 16.3253 | 15.7542 | 16.8489 | 16.1263 | 15.87 | 17.3179 | 70.4342 |  | 33.5264 | 58.0278 | 61.1224 | 26.929 |  | 6.5867 | 6.7188 | 6.0883 | 6.2993 | 6.3765 | 7.4924 | 23.3117 | 4.7634 | 6.554 | 4.7489 | 6.9975 | 8.1063 | 42.3619 | 47.2117 | 43.1983 | 14.8153 |  |  | -0.53402 | 0.007315 | 0.021564 | 0.082798 | -0.1352 | 0.14674 | 0.27392 | -0.31755 | -0.31173 | 0.74231 | -0.33293 | 8.9028 | -0.00044519 | 1.9976 | 15.8772 | 16.7207 | 17.235 | 17.5467 | 17.4918 | 16.4509 | 14.7945 | 16.8055 | 17.1529 | 17.4474 | 17.4893 | 17.2063 | 16.377 | 14.5742 | 16.579 | 10.3061 | 9.7848 | 8.6116 | 8.4044 | 10.7178 | 9.1425 | 15.985 | 15.567 | 15.3995 | 14.3161 | 14.2838 | 14.4047 |  |  |  | 16.5307 | 79.6784 | 65.4286 | 18.1492 | 0.025171 | -0.24859 | 22.5541 |  |  | 10.7146 |  |  | 16.8782 | 16.0824 | 16.8888 | 16.3517 | 15.6194 | 15.3 | 67.1364 | 79.9082 | 52.6182 | 53.3069 | 25.3081 |  | 18.0889 | 32.9321 | 18.7674 | 18.5481 | 17.635 | 59.7754 |  | 29.6046 |  |  | 12.529 | 13.8121 | 23.3399 | [6 empty] | 18.7109 |  |  | 17.5097 |  |  | 11.6204 | 17.583 | 88.0479 | 8.2363 | 14.2571 | 60.5515 | 8.899 | 13.3282 | 65.1201 | 13.4644 | 55.8928 | 8.9318 | 47.1972 | 9.8009 | 47.9722 | 9.0495 | 16.1618 | 58.563 | 13.4319 | 15.9368 | 77.0923 | 9.589 | 14.3015 | 66.0823 | 9.9188 | 46.483 | 12.8788 | 53.1826 | 10.6064 | 51.3348 | 0.15195 | 20.1756 | 0.50746 | 0.054971 | -37.752 | 3.1218 | 77.14 | 49.63 | -0.95192 | 0.099713 | 0.1712 | 0.33547 | -0.42927 | 0.44721 | 0.61102 | 0.20739 | 0.018276 | 0.38003 | -0.28307 | 0.2887 | 0.13665 | 0.35431
42810.4427 | 229 | 18.5221 | 18.5997 | 18.5751 | 18.5606 | 17.8722 | 16.4768 | 14.5408 | 16.6428 | 17.1428 | 17.2366 | 17.2414 | 16.7636 | 15.7899 | 14.3937 | 14.9152 | 14.9251 | 15.4599 | 13.3211 | 13.5095 | 14.1953 |  |  |  | 16.5425 | 15.8773 | 16.085 | 69.3162 | 68.7941 | 76.0922 | 17.1975 | 16.3278 | 15.7648 | 16.8494 | 16.1239 | 15.8905 | 17.3896 | 70.3719 |  | 33.6389 | 58.1137 | 61.1948 | 27.5039 |  | 6.5907 | 6.7229 | 6.0913 | 6.3098 | 6.3873 | 7.4636 | 23.0484 | 4.6311 | 6.5629 | 4.6879 | 6.9982 | 8.1131 | 42.4002 | 47.23 | 43.1974 | 14.8334 |  |  | -0.3106 | 0.015859 | 0.12802 | 0.11171 | 0.1145 | 0.2591 | 0.4014 | -0.36158 | -0.61122 | -0.67867 | -0.47301 | 8.9024 | -0.00047805 | 2.0021 | 15.881 | 16.7246 | 17.236 | 17.5477 | 17.4969 | 16.4544 | 14.8009 | 16.8096 | 17.1544 | 17.4511 | 17.4897 | 17.209 | 16.3837 | 14.5777 | 17.6418 | 10.5875 | 10.0201 | 8.6475 | 8.3792 | 10.7679 | 9.1449 | 15.9748 | 15.5632 | 15.3916 | 14.3125 | 14.2806 | 14.4024 |  |  |  | 16.5542 | 79.6033 | 65.327 | 18.0461 | 0.00248 | -0.23447 | 22.6251 |  |  | 10.7169 |  |  | 16.8832 | 16.0796 | 16.8974 | 16.3502 | 15.6222 | 15.3114 | 67.2139 | 79.895 | 52.7013 | 53.3833 | 26.846 |  | 18.1569 | 32.2208 | 18.8303 | 18.5483 | 17.6836 | 60.6241 |  | 29.6968 |  |  | 12.5144 | 13.8042 | 23.5591 | [6 empty] | 18.8672 |  |  | 17.5246 |  |  | 11.6267 | 17.6444 | 88.1979 | 8.248 | 14.2333 | 60.556 | 8.9053 | 13.3665 | 65.239 | 13.4842 | 55.9757 | 8.9539 | 47.3189 | 9.8113 | 48.0758 | 9.0722 | 16.2171 | 58.5385 | 13.4456 | 15.968 | 77.1855 | 9.5993 | 14.3084 | 66.1499 | 9.9236 | 46.5906 | 12.9012 | 53.4809 | 10.6167 | 51.4515 | 0.28022 | 20.1746 | 0.50804 | 0.054905 | -37.7528 | 3.1218 | 80.68 | 48.83 | -0.72582 | 0.14682 | 0.41714 | 0.38967 | 0.39503 | 0.59423 | 0.73962 | 0.16694 | 0.040134 | 0.38164 | -0.39534 | 0.26283 | 0.12307 | 0.35795
42810.4427 | 230 | 18.527 | 18.6018 | 18.577 | 18.5746 | 17.8762 | 16.4834 | 14.5338 | 16.6509 | 17.1495 | 17.2313 | 17.2441 | 16.7664 | 15.8013 | 14.4012 | 14.9204 | 14.9241 | 15.4627 | 13.3199 | 13.5168 | 14.1945 |  |  |  | 16.5421 | 15.8748 | 16.1045 | 69.3134 | 68.752 | 76.2453 | 17.1951 | 16.3218 | 15.7689 | 16.8434 | 16.1158 | 15.8822 | 17.4376 | 70.7373 |  | 33.7314 | 58.1908 | 61.2455 | 26.8206 |  | 6.5942 | 6.7124 | 6.0845 | 6.3086 | 6.3806 | 7.4593 | 22.835 | 4.5413 | 6.5568 | 4.6351 | 6.9907 | 8.1057 | 42.4402 | 47.2252 | 43.2039 | 14.8581 |  |  | -0.47356 | 0.054627 | 0.041936 | -0.12945 | -0.26137 | -0.27973 | 0.34226 | -0.19007 | -0.54 | -0.17137 | -0.20397 | 8.9019 | -0.00043041 | 2.0025 | 15.8781 | 16.7233 | 17.2366 | 17.5497 | 17.4913 | 16.4444 | 14.7906 | 16.8103 | 17.1514 | 17.4435 | 17.4839 | 17.2073 | 16.3826 | 14.572 | 18.4852 | 10.9834 | 10.1714 | 8.8159 | 8.3955 | 10.8177 | 9.1455 | 15.9857 | 15.5668 | 15.3936 | 14.3144 | 14.2912 | 14.4125 |  |  |  | 16.5905 | 79.5545 | 65.3499 | 18.3771 | 0.050496 | -0.27908 | 22.5595 |  |  | 10.7245 |  |  | 16.8885 | 16.0828 | 16.9305 | 16.3542 | 15.6305 | 15.3241 | 67.3168 | 80.0277 | 52.7818 | 53.4645 | 27.2899 |  | 18.2108 | 31.4264 | 18.8651 | 18.502 | 17.7271 | 61.2283 |  | 29.7903 |  |  | 12.5218 | 13.8192 | 23.552 | [6 empty] | 18.8756 |  |  | 17.5473 |  |  | 11.6356 | 17.6742 | 88.2934 | 8.2487 | 14.2151 | 60.5625 | 8.9179 | 13.3558 | 65.3089 | 13.4956 | 56.0423 | 8.9683 | 47.4295 | 9.8126 | 48.1583 | 9.081 | 16.2348 | 58.5615 | 13.4456 | 15.9887 | 77.1958 | 9.6031 | 14.3156 | 66.2346 | 9.9241 | 46.6569 | 12.9103 | 53.8207 | 10.6166 | 51.5803 | 0.19124 | 20.1717 | 0.5114 | 0.05644 | -37.7417 | 3.1218 | 82.77 | 49.9 | -0.89642 | 0.27249 | 0.23874 | -0.41946 | -0.59682 | -0.61743 | 0.68296 | 0.15641 | 0.063368 | 0.38438 | -0.48326 | 0.24609 | 0.14365 | 0.34997
42810.4427 | 231 | 18.5212 | 18.5958 | 18.5719 | 18.5532 | 17.8663 | 16.4776 | 14.5309 | 16.6482 | 17.135 | 17.2349 | 17.2378 | 16.7632 | 15.7844 | 14.3922 | 14.9267 | 14.9176 | 15.467 | 13.3191 | 13.5172 | 14.2054 |  |  |  | 16.5586 | 15.8791 | 16.1177 | 69.3907 | 68.8009 | 75.9874 | 17.1939 | 16.3236 | 15.7756 | 16.8592 | 16.129 | 15.8905 | 17.4752 | 71.0088 |  | 33.8243 | 58.2455 | 61.2918 | 26.221 |  | 6.5857 | 6.698 | 6.0911 | 6.3208 | 6.3867 | 7.5344 | 22.5573 | 4.5834 | 6.554 | 4.5715 | 6.992 | 8.1056 | 42.4815 | 47.2263 | 43.1994 | 14.8784 |  |  | -0.23897 | -0.083365 | 0.17467 | 0.12025 | -0.10498 | 0.2775 | 0.39483 | -0.017248 | -1.3855 | -0.8721 | -0.24848 | 8.9021 | -0.00048462 | 1.9976 | 15.879 | 16.7251 | 17.238 | 17.5517 | 17.4993 | 16.4516 | 14.7861 | 16.8031 | 17.156 | 17.4432 | 17.4862 | 17.2011 | 16.3852 | 14.5787 | 19.4743 | 11.2806 | 11.3156 | 8.9969 | 8.586 | 10.891 | 9.1724 | 15.9824 | 15.5645 | 15.4044 | 14.3123 | 14.292 | 14.4161 |  |  |  | 16.6371 | 79.638 | 65.7258 | 19.4965 | 0.093853 | -0.20022 | 22.532 |  |  | 10.719 |  |  | 16.8689 | 16.0741 | 16.9405 | 16.3404 | 15.6111 | 15.3201 | 67.3306 | 79.9609 | 52.8368 | 53.5255 | 27.481 |  | 18.2631 | 31.4338 | 18.9156 | 18.4885 | 17.7591 | 61.0543 |  | 29.8859 |  |  | 12.5111 | 13.8403 | 23.5107 | [6 empty] | 18.8612 |  |  | 17.5829 |  |  | 11.6392 | 17.6685 | 88.33 | 8.2336 | 14.2626 | 60.5959 | 8.9155 | 13.3512 | 65.4383 | 13.505 | 56.1389 | 8.9771 | 47.5527 | 9.8245 | 48.2125 | 9.0874 | 16.2696 | 58.6605 | 13.4448 | 15.9892 | 77.1336 | 9.614 | 14.3178 | 66.38 | 9.9407 | 46.7032 | 12.9282 | 54.2286 | 10.6374 | 51.6703 | 0.21166 | 20.171 | 0.51309 | 0.056794 | -37.7478 | 3.1218 | 73.52 | 49.01 | -0.63656 | -0.3366 | 0.48724 | 0.40428 | -0.37829 | 0.61505 | 0.73364 | 0.15285 | 0.064847 | 0.38582 | -0.58464 | 0.12208 | 0.16156 | 0.32043
42810.4427 | 232 | 18.5295 | 18.6022 | 18.5748 | 18.5651 | 17.8747 | 16.4889 | 14.5367 | 16.6466 | 17.1411 | 17.2409 | 17.2436 | 16.7669 | 15.7892 | 14.4029 | 14.9182 | 14.9136 | 15.4715 | 13.3192 | 13.5145 | 14.2081 |  |  |  | 16.5499 | 15.8626 | 16.1324 | 69.4699 | 68.87 | 75.8364 | 17.1941 | 16.3138 | 15.7878 | 16.8448 | 16.1153 | 15.8967 | 17.5231 | 71.1068 |  | 33.9086 | 58.2815 | 61.3182 | 25.9271 |  | 6.5802 | 6.7108 | 6.1015 | 6.3286 | 6.3891 | 7.547 | 22.3132 | 4.5778 | 6.5539 | 4.5501 | 6.9928 | 8.1071 | 42.5098 | 47.224 | 43.1964 | 14.9026 |  |  | -0.34148 | -0.010425 | -0.019836 | -0.03877 | 0.13356 | -0.077344 | 0.53808 | 0.01758 | 0.047109 | 0.74504 | -0.16861 | 8.9024 | -0.00045177 | 1.9942 | 15.8754 | 16.7181 | 17.2434 | 17.549 | 17.4872 | 16.4401 | 14.7935 | 16.8072 | 17.1459 | 17.4389 | 17.4775 | 17.1964 | 16.3777 | 14.5701 | 20.5364 | 11.9259 | 12.588 | 9.6908 | 8.8829 | 10.9604 | 9.2013 | 15.9788 | 15.5564 | 15.3968 | 14.3154 | 14.2859 | 14.4249 |  |  |  | 16.6779 | 79.7169 | 65.7261 | 20.2033 | 0.2221 | -0.25612 | 22.5498 |  |  | 10.7289 |  |  | 16.8718 | 16.0734 | 16.9609 | 16.3427 | 15.6158 | 15.3272 | 67.2875 | 80.0089 | 52.9389 | 53.574 | 27.9127 |  | 18.3153 | 31.641 | 18.9588 | 18.4448 | 17.7834 | 60.5202 |  | 29.9849 |  |  | 12.4935 | 13.8385 | 23.3687 | [6 empty] | 18.7549 |  |  | 17.6047 |  |  | 11.6375 | 17.667 | 88.4326 | 8.218 | 14.2827 | 60.5892 | 8.9022 | 13.3349 | 65.4947 | 13.508 | 56.3921 | 8.9742 | 47.7199 | 9.8161 | 48.2282 | 9.1069 | 16.3195 | 58.7362 | 13.4735 | 15.9816 | 77.1098 | 9.6304 | 14.3365 | 66.4783 | 9.9442 | 46.7669 | 12.9444 | 54.6699 | 10.659 | 51.7722 | 0.27772 | 20.171 | 0.51454 | 0.056635 | -37.7561 | 3.1218 | 59.94 | 48.78 | -0.76077 | -0.11904 | -0.1642 | -0.22955 | 0.4267 | -0.32471 | 0.85646 | 0.1426 | 0.060538 | 0.38784 | -0.69457 | -0.015933 | 0.17132 | 0.30215
42810.4427 | 233 | 18.5321 | 18.6126 | 18.5793 | 18.5686 | 17.8754 | 16.4916 | 14.5428 | 16.6497 | 17.1455 | 17.2452 | 17.2534 | 16.7759 | 15.7937 | 14.4111 | 14.9224 | 14.9164 | 15.4669 | 13.3261 | 13.5159 | 14.2133 |  |  |  | 16.5472 | 15.8735 | 16.1411 | 69.5717 | 68.9549 | 76.434 | 17.195 | 16.3091 | 15.7991 | 16.8395 | 16.1131 | 15.9063 | 17.5721 | 71.1075 |  | 33.9947 | 58.317 | 61.3611 | 27.0273 |  | 6.5724 | 6.708 | 6.1036 | 6.3374 | 6.393 | 7.5079 | 22.5573 | 4.6723 | 6.5493 | 4.5651 | 6.9937 | 8.1002 | 42.536 | 47.2358 | 43.1956 | 14.9192 |  |  | -0.38682 | -0.15762 | 0.1313 | 0.008542 | 0.13027 | 0.13754 | 0.52165 | -0.24855 | -0.29578 | -0.42984 | 0.080763 | 8.9022 | -0.0004337 | 1.9993 | 15.8718 | 16.7272 | 17.249 | 17.5545 | 17.4993 | 16.455 | 14.7941 | 16.8216 | 17.1613 | 17.4452 | 17.4918 | 17.2127 | 16.3828 | 14.576 | 21.3328 | 12.5267 | 13.9015 | 9.9077 | 9.4063 | 11.031 | 9.2336 | 15.9809 | 15.5561 | 15.3989 | 14.3107 | 14.2937 | 14.431 |  |  |  | 16.7205 | 79.793 | 65.9373 | 20.2915 | 0.092637 | -0.18855 | 22.5622 |  |  | 10.7252 |  |  | 16.8703 | 16.078 | 16.9813 | 16.3488 | 15.6173 | 15.3349 | 67.3153 | 80.0436 | 53.0221 | 53.5975 | 27.3395 |  | 18.3801 | 30.3979 | 19.0277 | 18.5592 | 17.8371 | 60.674 |  | 30.0759 |  |  | 12.5285 | 13.8368 | 23.2372 | [6 empty] | 18.7715 |  |  | 17.5762 |  |  | 11.6593 | 17.7236 | 88.6861 | 8.2277 | 14.2655 | 60.5631 | 8.9196 | 13.3976 | 65.4939 | 13.5291 | 56.6174 | 9.0004 | 47.913 | 9.8412 | 48.3386 | 9.096 | 16.311 | 58.7989 | 13.4702 | 15.9616 | 77.2186 | 9.6235 | 14.3634 | 66.5211 | 9.9396 | 46.8419 | 12.9475 | 54.9122 | 10.6651 | 51.8453 | 0.35322 | 20.1702 | 0.5147 | 0.054971 | -37.7243 | 3.1218 | 83.28 | 50.15 | -0.8104 | -0.46285 | 0.42245 | 0.10775 | 0.42139 | 0.43298 | 0.84323 | 0.16069 | 0.097372 | 0.38646 | -0.77485 | -0.15812 | 0.14239 | 0.30112
42810.4427 | 234 | 18.5209 | 18.6034 | 18.5746 | 18.5667 | 17.8703 | 16.486 | 14.5405 | 16.6474 | 17.1418 | 17.2401 | 17.2459 | 16.7693 | 15.7862 | 14.4045 | 14.9214 | 14.9221 | 15.4694 | 13.3303 | 13.5224 | 14.2214 |  |  |  | 16.5443 | 15.8766 | 16.1602 | 69.6863 | 69.0427 | 77.4827 | 17.1881 | 16.309 | 15.7936 | 16.8408 | 16.108 | 15.912 | 17.6313 | 71.0131 |  | 34.0821 | 58.3419 | 61.399 | 28.9318 |  | 6.5764 | 6.7232 | 6.1122 | 6.3412 | 6.3985 | 7.4904 | 22.6277 | 4.7509 | 6.5582 | 4.5312 | 6.9981 | 8.1056 | 42.5642 | 47.2354 | 43.1964 | 14.9408 |  |  | -0.5465 | 0.001403 | -0.040864 | 0.10317 | -0.08132 | -0.053688 | 0.64519 | -0.093476 | -0.087555 | -0.077379 | 0.105 | 8.9016 | -0.00048134 | 2.0029 | 15.8856 | 16.726 | 17.2485 | 17.5562 | 17.4981 | 16.4566 | 14.8021 | 16.8162 | 17.1515 | 17.4459 | 17.4887 | 17.2136 | 16.3799 | 14.579 | 21.9948 | 12.9539 | 14.94 | 10.2437 | 9.2825 | 11.1026 | 9.2692 | 15.9863 | 15.5615 | 15.4094 | 14.3148 | 14.3017 | 14.4339 |  |  |  | 16.7571 | 79.8962 | 66.1135 | 20.229 | 0.28815 | -0.21452 | 22.4428 |  |  | 10.7314 |  |  | 16.8796 | 16.0779 | 16.9913 | 16.3448 | 15.6245 | 15.3538 | 67.3602 | 80.1234 | 53.0655 | 53.6052 | 27.5923 |  | 18.4395 | 29.4914 | 19.0439 | 19.1243 | 17.8804 | 60.4009 |  | 30.1472 |  |  | 12.5339 | 13.8229 | 23.2692 | [6 empty] | 19.0949 |  |  | 17.555 |  |  | 11.6557 | 17.78 | 88.9301 | 8.2196 | 14.2358 | 60.6186 | 8.908 | 13.4028 | 65.4728 | 13.5223 | 56.6524 | 8.9997 | 48.0409 | 9.8271 | 48.43 | 9.098 | 16.3195 | 58.8534 | 13.4871 | 15.9936 | 77.2289 | 9.6504 | 14.4301 | 66.6291 | 9.961 | 46.9573 | 12.9843 | 55.1762 | 10.6785 | 51.9738 | 0.28715 | 20.1688 | 0.51554 | 0.054153 | -37.7426 | 3.1219 | 62.23 | 48.92 | -0.96469 | 0.043669 | -0.23568 | 0.37447 | -0.33292 | -0.27051 | 0.93775 | 0.15565 | 0.12309 | 0.37221 | -0.84006 | -0.26938 | 0.091463 | 0.30407
42810.4428 | 235 | 18.5185 | 18.603 | 18.5749 | 18.57 | 17.8778 | 16.4827 | 14.5385 | 16.6516 | 17.1366 | 17.2402 | 17.2524 | 16.7749 | 15.7881 | 14.4051 | 14.917 | 14.9176 | 15.4703 | 13.3252 | 13.5184 | 14.2139 |  |  |  | 16.5427 | 15.8782 | 16.1665 | 69.9026 | 69.0549 | 78.1428 | 17.1846 | 16.3027 | 15.8025 | 16.8376 | 16.1094 | 15.9219 | 17.7013 | 70.8827 |  | 34.1817 | 58.3586 | 61.4134 | 29.6542 |  | 6.5736 | 6.7234 | 6.1211 | 6.3448 | 6.4134 | 7.5257 | 22.3541 | 4.8582 | 6.5573 | 4.4944 | 6.9977 | 8.1016 | 42.5805 | 47.2234 | 43.1934 | 14.9605 |  |  | -0.52745 | 0.032287 | 0.039308 | 0.055854 | 0.2341 | 0.25187 | 0.57882 | 0.000492 | -0.59702 | -0.49194 | -0.21172 | 8.9018 | -0.00048298 | 2.002 | 15.8782 | 16.7253 | 17.2398 | 17.5502 | 17.4952 | 16.4513 | 14.7855 | 16.8149 | 17.1506 | 17.4464 | 17.4871 | 17.2026 | 16.3766 | 14.5717 | 22.3916 | 13.1094 | 15.0626 | 10.2195 | 9.7473 | 11.1685 | 9.3033 | 15.9728 | 15.5551 | 15.3947 | 14.3089 | 14.2831 | 14.4297 |  |  |  | 16.7869 | 79.9672 | 65.9863 | 19.9522 | -0.012918 | -0.0235 | 22.462 |  |  | 10.7315 |  |  | 16.8784 | 16.073 | 17.0136 | 16.346 | 15.6198 | 15.355 | 67.4634 | 80.2314 | 53.1067 | 53.6218 | 28.1185 |  | 18.4976 | 31.0822 | 19.0951 | 19.4378 | 17.9309 | 59.9681 |  | 30.2203 |  |  | 12.5437 | 13.8412 | 23.6049 | [6 empty] | 19.325 |  |  | 17.5752 |  |  | 11.6603 | 17.7984 | 89.0358 | 8.212 | 14.2357 | 60.7541 | 8.9237 | 13.4001 | 65.4716 | 13.5185 | 56.7096 | 8.9966 | 48.1342 | 9.8277 | 48.5181 | 9.0894 | 16.2923 | 58.9575 | 13.4953 | 16.0232 | 77.1936 | 9.6463 | 14.484 | 66.6997 | 9.9534 | 47.0572 | 12.998 | 55.3854 | 10.6796 | 52.0309 | 0.20973 | 20.1676 | 0.51752 | 0.055709 | -37.7359 | 3.1219 | 78.6 | 49.2 | -0.94862 | 0.20949 | 0.23115 | 0.27553 | 0.56489 | 0.58595 | 0.88826 | 0.14297 | 0.080618 | 0.36518 | -0.8765 | -0.27904 | 0.073733 | 0.31275
42810.4428 | 236 | 18.513 | 18.598 | 18.5693 | 18.5591 | 17.8749 | 16.4812 | 14.5338 | 16.6476 | 17.1387 | 17.2371 | 17.2437 | 16.7569 | 15.7892 | 14.3914 | 14.9217 | 14.9233 | 15.4725 | 13.3255 | 13.5242 | 14.2266 |  |  |  | 16.5479 | 15.8857 | 16.1816 | 70.1961 | 69.1004 | 79.1222 | 17.1811 | 16.3059 | 15.8089 | 16.8459 | 16.1161 | 15.9281 | 17.7588 | 70.7509 |  | 34.2793 | 58.3953 | 61.4123 | 29.2845 |  | 6.5831 | 6.7215 | 6.1217 | 6.3569 | 6.4199 | 7.5892 | 22.0426 | 4.8805 | 6.5572 | 4.5885 | 6.9994 | 8.0939 | 42.5796 | 47.226 | 43.2053 | 14.9799 |  |  | -0.33031 | 0.19394 | 0.22198 | -0.026942 | 0.13684 | 0.30313 | 0.54531 | 0.13717 | -1.5875 | 1.1397 | -0.2 | 8.903 | -0.00044191 | 1.9939 | 15.8699 | 16.7275 | 17.2403 | 17.5491 | 17.497 | 16.4511 | 14.7871 | 16.8128 | 17.1517 | 17.4408 | 17.4813 | 17.2103 | 16.375 | 14.5774 | 21.3079 | 12.6068 | 15.6123 | 10.2544 | 9.5618 | 11.205 | 9.338 | 15.9841 | 15.564 | 15.411 | 14.3137 | 14.3003 | 14.4486 |  |  |  | 16.8295 | 80.0333 | 65.7545 | 19.8751 | -0.099023 | -0.2356 | 22.6887 |  |  | 10.7223 |  |  | 16.8814 | 16.0861 | 17.0303 | 16.3476 | 15.624 | 15.3628 | 67.5674 | 80.358 | 53.1736 | 53.6521 | 28.0714 |  | 18.5571 | 32.4044 | 19.1809 | 19.498 | 17.9701 | 60.0135 |  | 30.2984 |  |  | 12.5763 | 13.8585 | 23.7159 | [6 empty] | 19.4361 |  |  | 17.5867 |  |  | 11.6671 | 17.8234 | 89.1812 | 8.2425 | 14.3626 | 60.8345 | 8.9414 | 13.417 | 65.4786 | 13.5341 | 56.8421 | 9.0151 | 48.1911 | 9.853 | 48.6118 | 9.0893 | 16.2647 | 59.1061 | 13.5184 | 16.0493 | 77.1677 | 9.6531 | 14.5245 | 66.7105 | 9.9646 | 47.1112 | 13.0032 | 55.5439 | 10.6868 | 52.1238 | 0.31258 | 20.1691 | 0.51882 | 0.055629 | -37.7342 | 3.1219 | 70.65 | 50.05 | -0.75174 | 0.51343 | 0.5493 | -0.19136 | 0.43195 | 0.64288 | 0.86226 | 0.14627 | 0.046759 | 0.36482 | -0.75184 | -0.33607 | 0.08592 | 0.31631
42810.4428 | 237 | 18.51 | 18.5933 | 18.5635 | 18.5587 | 17.8654 | 16.4798 | 14.5319 | 16.6418 | 17.1367 | 17.2348 | 17.2341 | 16.7594 | 15.7814 | 14.3977 | 14.9172 | 14.9204 | 15.4648 | 13.3231 | 13.5153 | 14.2317 |  |  |  | 16.5461 | 15.8793 | 16.196 | 70.3986 | 69.129 | 78.7774 | 17.1759 | 16.3068 | 15.8162 | 16.8315 | 16.115 | 15.9372 | 17.8033 | 70.8491 |  | 34.3891 | 58.448 | 61.4293 | 28.5794 |  | 6.5786 | 6.7217 | 6.1251 | 6.3655 | 6.4253 | 7.6174 | 22.2285 | 4.7435 | 6.5598 | 4.766 | 7.0048 | 8.0941 | 42.5463 | 47.2288 | 43.2132 | 14.9872 |  |  | -0.32637 | -0.010425 | 0.1037 | 0.10514 | 0.11976 | 0.17696 | 0.54925 | 0.25808 | -0.84708 | -0.88658 | -0.12469 | 8.9024 | -0.00044848 | 1.992 | 15.8741 | 16.7288 | 17.2431 | 17.545 | 17.4997 | 16.45 | 14.7969 | 16.8143 | 17.1559 | 17.4407 | 17.4836 | 17.2107 | 16.3816 | 14.5818 | 21.0858 | 11.9719 | 14.3212 | 10.249 | 9.4508 | 11.2532 | 9.3519 | 15.9857 | 15.5705 | 15.4104 | 14.3172 | 14.3025 | 14.4507 |  |  |  | 16.8801 | 80.076 | 65.5028 | 20.2956 | 0.086559 | -0.28886 | 22.8896 |  |  | 10.7186 |  |  | 16.8686 | 16.0796 | 17.0479 | 16.3383 | 15.6206 | 15.3639 | 67.6706 | 80.4845 | 53.2439 | 53.7211 | 27.4204 |  | 18.6122 | 30.3113 | 19.2392 | 19.6655 | 18.015 | 59.7693 |  | 30.3858 |  |  | 12.5929 | 13.8654 | 23.63 | [6 empty] | 19.5004 |  |  | 17.5833 |  |  | 11.6717 | 17.835 | 89.1755 | 8.2543 | 14.4466 | 60.9348 | 8.9506 | 13.4483 | 65.4952 | 13.5389 | 56.9512 | 9.019 | 48.2495 | 9.8636 | 48.69 | 9.101 | 16.2673 | 59.1626 | 13.5372 | 16.0673 | 77.204 | 9.6686 | 14.5139 | 66.7588 | 9.9874 | 47.1718 | 13.0188 | 55.6175 | 10.6951 | 52.2115 | 0.18488 | 20.1663 | 0.51988 | 0.055521 | -37.7391 | 3.1219 | 54.75 | 48.82 | -0.74688 | -0.11904 | 0.37544 | 0.37803 | 0.40411 | 0.49122 | 0.86542 | 0.16619 | 0.10685 | 0.36167 | -0.72155 | -0.191 | 0.10699 | 0.30632
42810.4428 | 238 | 18.5162 | 18.5935 | 18.577 | 18.5688 | 17.8725 | 16.4803 | 14.5389 | 16.6413 | 17.1395 | 17.2335 | 17.2339 | 16.7615 | 15.7859 | 14.3997 | 14.9153 | 14.921 | 15.464 | 13.3224 | 13.5119 | 14.2325 |  |  |  | 16.5415 | 15.872 | 16.2038 | 70.4698 | 69.1762 | 78.4878 | 17.1781 | 16.3088 | 15.8277 | 16.8381 | 16.1246 | 15.9571 | 17.8458 | 71.1163 |  | 34.4814 | 58.5428 | 61.4523 | 28.0522 |  | 6.5702 | 6.7178 | 6.1284 | 6.3631 | 6.4589 | 7.6332 | 22.5992 | 4.5606 | 6.5518 | 4.8582 | 7.0015 | 8.0975 | 42.5363 | 47.2296 | 43.2219 | 15.0001 |  |  | -0.46502 | -0.045909 | 0.15364 | -0.18005 | 0.36684 | 0.12768 | 0.48485 | 0.1766 | -0.5869 | -0.53684 | -0.39632 | 8.9021 | -0.00043862 | 1.9983 | 15.8833 | 16.7292 | 17.2455 | 17.5512 | 17.4986 | 16.4473 | 14.8 | 16.8157 | 17.1564 | 17.4506 | 17.4922 | 17.2104 | 16.3792 | 14.5773 | 21.9425 | 12.2837 | 13.2185 | 9.8471 | 9.4695 | 11.3254 | 9.3565 | 15.9782 | 15.5656 | 15.4073 | 14.3175 | 14.303 | 14.4543 |  |  |  | 16.9224 | 80.0662 | 65.2369 | 20.5699 | -0.009676 | -0.24501 | 22.88 |  |  | 10.7322 |  |  | 16.8808 | 16.0872 | 17.0801 | 16.3501 | 15.6242 | 15.3785 | 67.855 | 80.5971 | 53.3221 | 53.8031 | 27.3235 |  | 18.6676 | 28.3652 | 19.2658 | 20.146 | 18.0644 | 59.1548 |  | 30.4629 |  |  | 12.6187 | 13.8848 | 23.6021 | [6 empty] | 19.6883 |  |  | 17.5825 |  |  | 11.666 | 17.8487 | 89.1285 | 8.2451 | 14.4516 | 61.0149 | 8.9583 | 13.4736 | 65.6507 | 13.5469 | 57.0118 | 9.0073 | 48.3305 | 9.8758 | 48.8173 | 9.1102 | 16.2891 | 59.1995 | 13.5478 | 16.0836 | 77.2327 | 9.6775 | 14.5158 | 66.9538 | 10.0023 | 47.2674 | 13.0291 | 55.7509 | 10.6999 | 52.2647 | 0.30757 | 20.1627 | 0.52009 | 0.054145 | -37.7232 | 3.1219 | 61.8 | 48.75 | -0.89115 | -0.2498 | 0.45698 | -0.4947 | 0.70728 | 0.41726 | 0.81312 | 0.17073 | 0.1618 | 0.34997 | -0.80835 | -0.067953 | 0.12305 | 0.30011
42810.4428 | 239 | 18.5094 | 18.5905 | 18.5735 | 18.5614 | 17.8673 | 16.4838 | 14.5354 | 16.6394 | 17.1319 | 17.2359 | 17.2358 | 16.7638 | 15.7826 | 14.3955 | 14.9146 | 14.918 | 15.4633 | 13.3249 | 13.5189 | 14.2343 |  |  |  | 16.5419 | 15.8791 | 16.2198 | 70.5701 | 69.1619 | 78.6319 | 17.1779 | 16.3042 | 15.8362 | 16.8443 | 16.1192 | 15.9653 | 17.8946 | 71.3652 |  | 34.5803 | 58.6125 | 61.4869 | 28.0643 |  | 6.5586 | 6.7135 | 6.1417 | 6.3734 | 6.4971 | 7.6619 | 22.5841 | 4.4397 | 6.5427 | 4.7479 | 6.985 | 8.0986 | 42.517 | 47.2406 | 43.2473 | 15.012 |  |  | -0.19888 | 0.008631 | 0.1221 | -0.15639 | 0.13422 | 0.03174 | 0.28838 | -0.048792 | -0.51626 | -0.48439 | -0.18947 | 8.9029 | -0.00046162 | 1.998 | 15.88 | 16.7306 | 17.2514 | 17.555 | 17.5013 | 16.454 | 14.7973 | 16.8084 | 17.1508 | 17.4507 | 17.4896 | 17.205 | 16.3787 | 14.5813 | 22.607 | 12.5427 | 12.5552 | 9.6038 | 9.0234 | 11.3862 | 9.3612 | 15.9828 | 15.5649 | 15.4028 | 14.3114 | 14.3047 | 14.4567 |  |  |  | 16.9652 | 80.0097 | 65.078 | 20.5314 | 0.021119 | -0.27776 | 22.8318 |  |  | 10.7317 |  |  | 16.8801 | 16.0857 | 17.0972 | 16.3574 | 15.6247 | 15.3918 | 68.0171 | 80.6681 | 53.3813 | 53.886 | 27.5091 |  | 18.7167 | 26.7158 | 19.3121 | 21.2346 | 18.1274 | 58.8276 |  | 30.5557 |  |  | 12.6347 | 13.8971 | 23.5612 | [6 empty] | 19.942 |  |  | 17.5743 |  |  | 11.6605 | 17.8653 | 89.1113 | 8.2384 | 14.4326 | 61.0951 | 8.9702 | 13.49 | 65.7874 | 13.5488 | 57.0438 | 8.9901 | 48.4402 | 9.8844 | 48.9246 | 9.1092 | 16.3013 | 59.3143 | 13.5474 | 16.1077 | 77.2862 | 9.679 | 14.5154 | 67.1409 | 10.0054 | 47.3431 | 13.0409 | 55.9251 | 10.694 | 52.3368 | 0.25037 | 20.1608 | 0.52076 | 0.053632 | -37.7547 | 3.122 | 74.69 | 50.1 | -0.58291 | 0.10831 | 0.40739 | -0.46105 | 0.42784 | 0.20806 | 0.62713 | 0.16722 | 0.20916 | 0.32183 | -0.87511 | 0.0063024 | 0.12435 | 0.3026
42810.4428 | 240 | 18.5094 | 18.5927 | 18.5746 | 18.5603 | 17.8609 | 16.4817 | 14.531 | 16.6374 | 17.1311 | 17.2347 | 17.2376 | 16.7609 | 15.778 | 14.392 | 14.9092 | 14.9131 | 15.4652 | 13.3259 | 13.5214 | 14.2397 |  |  |  | 16.5434 | 15.8765 | 16.2296 | 70.7276 | 69.1467 | 78.9304 | 17.1779 | 16.3033 | 15.8396 | 16.844 | 16.1204 | 15.9689 | 17.9493 | 71.2366 |  | 34.6754 | 58.6801 | 61.5288 | 28.5866 |  | 6.5544 | 6.7222 | 6.1581 | 6.3842 | 6.5257 | 7.6875 | 22.393 | 4.4263 | 6.5497 | 4.6169 | 6.9886 | 8.0977 | 42.5168 | 47.2707 | 43.2524 | 15.0158 |  |  | -0.28957 | -0.14579 | 0.09516 | 0.032198 | 0.32412 | 0.12505 | 0.23515 | 0.10629 | -0.77138 | -0.52656 | -0.16543 | 8.9016 | -0.00046655 | 1.9875 | 15.8775 | 16.7257 | 17.239 | 17.5468 | 17.4976 | 16.4452 | 14.7943 | 16.8104 | 17.146 | 17.4408 | 17.4821 | 17.1993 | 16.3783 | 14.5667 | 21.8623 | 12.2174 | 12.9318 | 9.8086 | 8.657 | 11.4173 | 9.3794 | 15.9801 | 15.5576 | 15.3976 | 14.3171 | 14.31 | 14.4515 |  |  |  | 17.014 | 79.9878 | 65.095 | 20.4886 | -0.095781 | -0.10047 | 22.9108 |  |  | 10.7348 |  |  | 16.8798 | 16.0849 | 17.1243 | 16.3457 | 15.6268 | 15.4017 | 68.0677 | 80.7433 | 53.4565 | 53.9525 | 27.5915 |  | 18.7807 | 27.6747 | 19.3877 | 21.3977 | 18.1818 | 58.8695 |  | 30.6421 |  |  | 12.6439 | 13.9037 | 23.5833 | [6 empty] | 20.0614 |  |  | 17.5631 |  |  | 11.6751 | 17.8944 | 89.1021 | 8.2365 | 14.4687 | 61.1813 | 8.9745 | 13.487 | 65.8365 | 13.5606 | 57.0515 | 8.9901 | 48.5209 | 9.9027 | 49.0104 | 9.1167 | 16.2996 | 59.4278 | 13.5557 | 16.1419 | 77.2752 | 9.6833 | 14.4999 | 67.2609 | 10.0061 | 47.3989 | 13.0403 | 56.0875 | 10.7022 | 52.41 | 0.43449 | 20.1574 | 0.52324 | 0.055238 | -37.7213 | 3.122 | 56.92 | 49.09 | -0.70366 | -0.44516 | 0.35965 | 0.2092 | 0.66489 | 0.41298 | 0.56632 | 0.16707 | 0.18506 | 0.31911 | -0.78875 | -0.033438 | 0.11166 | 0.30542
42810.4428 | 241 | 18.5079 | 18.5975 | 18.5764 | 18.5607 | 17.8648 | 16.4816 | 14.53 | 16.6437 | 17.1433 | 17.2444 | 17.2433 | 16.7618 | 15.7829 | 14.3938 | 14.9148 | 14.9132 | 15.4616 | 13.3232 | 13.5263 | 14.2419 |  |  |  | 16.5498 | 15.8869 | 16.2507 | 70.8612 | 69.1783 | 78.8579 | 17.1748 | 16.31 | 15.8442 | 16.8412 | 16.1192 | 15.9774 | 18.0058 | 71.0133 |  | 34.7693 | 58.75 | 61.5788 | 28.0653 |  | 6.5513 | 6.7316 | 6.1891 | 6.4115 | 6.5403 | 7.6755 | 22.2675 | 4.4106 | 6.5456 | 4.5326 | 6.9929 | 8.0915 | 42.5056 | 47.2749 | 43.2423 | 15.0099 |  |  | -0.25409 | 0.042143 | 0.026164 | 0.068998 | 0.26761 | -0.11348 | 0.34883 | 0.066204 | -0.38996 | 0.52265 | -0.19086 | 8.9025 | -0.00044848 | 1.9869 | 15.8702 | 16.7171 | 17.2398 | 17.5538 | 17.4999 | 16.451 | 14.7926 | 16.8144 | 17.1508 | 17.4367 | 17.4811 | 17.197 | 16.3779 | 14.5729 | 20.4046 | 11.5343 | 13.0219 | 9.875 | 8.6717 | 11.4407 | 9.3923 | 15.9741 | 15.5548 | 15.3898 | 14.3122 | 14.304 | 14.4614 |  |  |  | 17.066 | 80.0287 | 65.1353 | 20.9176 | -0.38408 | -0.25423 | 23.0272 |  |  | 10.7398 |  |  | 16.8775 | 16.0871 | 17.1384 | 16.3452 | 15.6267 | 15.408 | 68.0676 | 80.8418 | 53.5215 | 54.0067 | 27.6096 |  | 18.8309 | 30.0905 | 19.4641 | 21.0225 | 18.2126 | 59.0772 |  | 30.7331 |  |  | 12.6707 | 13.9065 | 23.6267 | [6 empty] | 19.9364 |  |  | 17.5983 |  |  | 11.686 | 17.9321 | 89.0734 | 8.222 | 14.5921 | 61.2351 | 8.9887 | 13.4941 | 65.9096 | 13.5705 | 57.1145 | 8.9966 | 48.595 | 9.9225 | 49.0938 | 9.124 | 16.2565 | 59.434 | 13.5525 | 16.1711 | 77.252 | 9.6827 | 14.4954 | 67.3654 | 10.0021 | 47.488 | 13.0283 | 56.4171 | 10.7082 | 52.4604 | 0.30179 | 20.1543 | 0.52419 | 0.055557 | -37.7634 | 3.122 | 61.41 | 49.8 | -0.65907 | 0.23934 | 0.18858 | 0.30625 | 0.60414 | -0.39342 | 0.68975 | 0.16825 | 0.12051 | 0.33056 | -0.62406 | -0.041952 | 0.12803 | 0.29523
42810.4428 | 242 | 18.5109 | 18.5964 | 18.5762 | 18.5652 | 17.8696 | 16.4845 | 14.5302 | 16.642 | 17.1452 | 17.2437 | 17.2401 | 16.7685 | 15.7863 | 14.3915 | 14.9089 | 14.9045 | 15.4599 | 13.3226 | 13.5248 | 14.2331 |  |  |  | 16.5482 | 15.8881 | 16.2597 | 70.9119 | 69.2047 | 78.584 | 17.1739 | 16.3043 | 15.8539 | 16.8436 | 16.1235 | 15.9901 | 18.0533 | 71.1075 |  | 34.8636 | 58.8135 | 61.6155 | 27.2755 |  | 6.5545 | 6.7433 | 6.2018 | 6.4474 | 6.5576 | 7.6845 | 22.1116 | 4.4774 | 6.5429 | 4.4756 | 6.9876 | 8.0909 | 42.5111 | 47.3024 | 43.2418 | 15.0097 |  |  | -0.3014 | -0.12805 | -0.019836 | -0.24379 | 0.10728 | -0.22388 | 0.23318 | 0.09446 | -0.34073 | 0.97938 | -0.15947 | 8.903 | -0.00044519 | 1.9942 | 15.868 | 16.7232 | 17.2441 | 17.5544 | 17.5019 | 16.454 | 14.7941 | 16.8137 | 17.1554 | 17.445 | 17.4934 | 17.2041 | 16.3796 | 14.5787 | 18.736 | 11.1444 | 12.1082 | 9.6843 | 8.7186 | 11.4482 | 9.4031 | 15.9735 | 15.5527 | 15.3917 | 14.3055 | 14.2998 | 14.4618 |  |  |  | 17.1062 | 80.1796 | 65.131 | 21.3641 | -0.14967 | -0.27098 | 23.011 |  |  | 10.7414 |  |  | 16.883 | 16.0879 | 17.1565 | 16.346 | 15.6248 | 15.4178 | 68.0626 | 81.0367 | 53.5856 | 54.0485 | 27.6924 |  | 18.8928 | 32.1391 | 19.548 | 20.7338 | 18.2366 | 59.9424 |  | 30.8395 |  |  | 12.6803 | 13.9028 | 23.6736 | [6 empty] | 19.7332 |  |  | 17.6329 |  |  | 11.6899 | 17.9619 | 89.1541 | 8.196 | 14.6343 | 61.2529 | 8.9914 | 13.5 | 66.0041 | 13.5741 | 57.3038 | 9.0081 | 48.6419 | 9.9296 | 49.1649 | 9.1311 | 16.2208 | 59.491 | 13.5516 | 16.1823 | 77.2615 | 9.6753 | 14.4871 | 67.4199 | 10.0064 | 47.5903 | 13.019 | 56.6388 | 10.7088 | 52.5043 | 0.22244 | 20.1501 | 0.52488 | 0.056346 | -37.7764 | 3.122 | 35.65 | 49.64 | -0.71754 | -0.41721 | -0.16421 | -0.57567 | 0.38251 | -0.55259 | 0.56394 | 0.16801 | 0.066409 | 0.33939 | -0.43779 | 0.060832 | 0.15155 | 0.28417
42810.4428 | 243 | 18.5014 | 18.595 | 18.5683 | 18.5561 | 17.8626 | 16.4805 | 14.5299 | 16.6404 | 17.1264 | 17.2364 | 17.237 | 16.7651 | 15.7784 | 14.3906 | 14.9022 | 14.906 | 15.4519 | 13.3232 | 13.5184 | 14.244 |  |  |  | 16.5491 | 15.8832 | 16.2571 | 70.9786 | 69.2466 | 78.7322 | 17.1672 | 16.3059 | 15.8583 | 16.835 | 16.1099 | 15.9987 | 18.0937 | 71.3311 |  | 34.9396 | 58.8632 | 61.6592 | 27.3534 |  | 6.5536 | 6.7507 | 6.2188 | 6.4775 | 6.5693 | 7.6879 | 22.4299 | 4.5513 | 6.5424 | 4.4381 | 6.99 | 8.086 | 42.507 | 47.3266 | 43.2442 | 15.0008 |  |  | -0.34871 | -0.25093 | 0.020908 | -0.14588 | -0.074748 | 0.001512 | 0.21018 | 0.16083 | -0.39269 | -0.88595 | -0.29359 | 8.9034 | -0.00047805 | 1.9989 | 15.87 | 16.721 | 17.2371 | 17.5462 | 17.4926 | 16.449 | 14.7883 | 16.8179 | 17.1503 | 17.4394 | 17.4845 | 17.2027 | 16.3769 | 14.5696 | 17.3817 | 10.7748 | 11.257 | 9.3617 | 8.5202 | 11.4494 | 9.4034 | 15.9742 | 15.5573 | 15.4016 | 14.3176 | 14.3112 | 14.472 |  |  |  | 17.1533 | 80.2941 | 65.3416 | 21.4155 | -0.12901 | -0.31314 | 22.9064 |  |  | 10.742 |  |  | 16.8791 | 16.0836 | 17.168 | 16.3463 | 15.6244 | 15.423 | 68.1098 | 81.1479 | 53.7209 | 54.1057 | 27.9777 |  | 18.9603 | 33.0188 | 19.6322 | 20.5901 | 18.2839 | 61.0011 |  | 30.9417 |  |  | 12.7047 | 13.9004 | 23.8869 | [6 empty] | 19.6532 |  |  | 17.6628 |  |  | 11.6974 | 17.9733 | 89.2921 | 8.1814 | 14.5996 | 61.3032 | 8.9992 | 13.4927 | 66.1103 | 13.5772 | 57.4852 | 9.0012 | 48.6745 | 9.9186 | 49.2251 | 9.125 | 16.2029 | 59.5569 | 13.5411 | 16.1994 | 77.3391 | 9.6639 | 14.4825 | 67.4996 | 10.0095 | 47.6612 | 13.0127 | 56.7133 | 10.7146 | 52.5507 | 0.29794 | 20.1488 | 0.52457 | 0.05602 | -37.7342 | 3.122 | 45.1 | 48.83 | -0.77196 | -0.58404 | 0.16859 | -0.44531 | -0.3193 | 0.045412 | 0.53541 | 0.16235 | 0.04479 | 0.34496 | -0.28717 | 0.15544 | 0.15074 | 0.28431
42810.4429 | 244 | 18.5113 | 18.5967 | 18.5738 | 18.564 | 17.8719 | 16.4808 | 14.5355 | 16.6463 | 17.1435 | 17.2263 | 17.2475 | 16.7643 | 15.7861 | 14.4016 | 14.9004 | 14.9068 | 15.4532 | 13.3149 | 13.5223 | 14.2474 |  |  |  | 16.5365 | 15.8754 | 16.2742 | 71.0546 | 69.2692 | 79.0291 | 17.1634 | 16.3002 | 15.8679 | 16.8371 | 16.1166 | 16.0124 | 18.1528 | 71.5235 |  | 35.0496 | 58.942 | 61.7534 | 26.6461 |  | 6.5541 | 6.7546 | 6.2394 | 6.5088 | 6.5759 | 7.6846 | 22.609 | 4.6083 | 6.5464 | 4.4346 | 6.9897 | 8.0871 | 42.5168 | 47.3446 | 43.2377 | 14.9954 |  |  | -0.44268 | 0.11837 | 0.092532 | -0.33644 | -0.09906 | 0.19996 | 0.21544 | 0.10498 | -0.075879 | -0.34341 | -0.15609 | 8.9027 | -0.00044519 | 1.9973 | 15.8742 | 16.7186 | 17.239 | 17.5479 | 17.4919 | 16.4486 | 14.795 | 16.8134 | 17.1478 | 17.4448 | 17.4822 | 17.1991 | 16.3756 | 14.573 | 16.1589 | 10.421 | 10.4836 | 9.0238 | 8.3791 | 11.4412 | 9.4007 | 15.9693 | 15.5536 | 15.3945 | 14.3073 | 14.3043 | 14.466 |  |  |  | 17.1936 | 80.3227 | 65.5011 | 21.145 | -0.13448 | -0.27531 | 22.8199 |  |  | 10.7447 |  |  | 16.8796 | 16.0849 | 17.1912 | 16.3514 | 15.6195 | 15.4283 | 68.1555 | 81.3131 | 53.9169 | 54.2163 | 28.5362 |  | 19.0188 | 32.8186 | 19.678 | 20.8715 | 18.3285 | 61.3297 |  | 31.0315 |  |  | 12.725 | 13.9156 | 23.9793 | [6 empty] | 19.7149 |  |  | 17.7107 |  |  | 11.7152 | 18.0257 | 89.1971 | 8.2009 | 14.5696 | 61.4518 | 9.0222 | 13.5278 | 66.1581 | 13.6054 | 57.7095 | 9.0164 | 48.7918 | 9.952 | 49.3007 | 9.1316 | 16.1769 | 59.558 | 13.5426 | 16.2549 | 77.4222 | 9.6611 | 14.487 | 67.5719 | 10.0023 | 47.7102 | 13.024 | 56.8688 | 10.7282 | 52.5767 | 0.4162 | 20.1437 | 0.52593 | 0.055846 | -37.7372 | 3.122 | 59.61 | 49.83 | -0.87015 | 0.40113 | 0.35466 | -0.67628 | -0.36757 | 0.52223 | 0.54207 | 0.14879 | 0.051882 | 0.33863 | -0.15225 | 0.24106 | 0.17236 | 0.29317
42810.4429 | 245 | 18.5013 | 18.5912 | 18.5687 | 18.5576 | 17.8651 | 16.4733 | 14.538 | 16.6391 | 17.1375 | 17.2238 | 17.2367 | 16.7633 | 15.7739 | 14.3846 | 14.8958 | 14.9045 | 15.454 | 13.3048 | 13.5248 | 14.2525 |  |  |  | 16.5432 | 15.8761 | 16.292 | 71.0859 | 69.2711 | 78.8824 | 17.1623 | 16.2999 | 15.8727 | 16.8353 | 16.1166 | 16.013 | 18.1868 | 71.6327 |  | 35.1276 | 59.0379 | 61.8477 | 26.0137 |  | 6.5598 | 6.764 | 6.2427 | 6.5224 | 6.5854 | 7.6894 | 22.991 | 4.6619 | 6.5544 | 4.5056 | 6.9915 | 8.0915 | 42.5108 | 47.3492 | 43.2284 | 14.9876 |  |  | -0.2002 | 0.10391 | 0.062964 | -0.37653 | 0.038276 | -0.25279 | 0.026184 | 0.10038 | -0.11694 | -0.10297 | -0.070447 | 8.9033 | -0.00045012 | 1.9953 | 15.8725 | 16.7231 | 17.2405 | 17.5522 | 17.4946 | 16.448 | 14.7942 | 16.8133 | 17.1442 | 17.4489 | 17.4845 | 17.197 | 16.3768 | 14.5744 | 15.0173 | 10.1678 | 9.8647 | 8.6839 | 8.1513 | 11.4194 | 9.3952 | 15.9566 | 15.5548 | 15.3869 | 14.3122 | 14.306 | 14.4673 |  |  |  | 17.2404 | 80.2938 | 65.4499 | 20.9562 | 0.075213 | -0.11214 | 22.7805 |  |  | 10.7551 |  |  | 16.8793 | 16.0844 | 17.2127 | 16.3456 | 15.6222 | 15.4365 | 68.1805 | 81.4792 | 54.1193 | 54.3874 | 29.3331 |  | 19.0771 | 31.9034 | 19.7137 | 21.2591 | 18.3698 | 61.1687 |  | 31.1122 |  |  | 12.7649 | 13.9362 | 24.1484 | [6 empty] | 19.8811 |  |  | 17.7502 |  |  | 11.7169 | 18.058 | 89.1748 | 8.2184 | 14.5437 | 61.598 | 9.0415 | 13.5472 | 66.139 | 13.6051 | 58.1044 | 9.0254 | 48.8532 | 9.9565 | 49.3516 | 9.1413 | 16.1352 | 59.4945 | 13.5595 | 16.2954 | 77.3967 | 9.6547 | 14.5045 | 67.6384 | 9.978 | 47.8067 | 13.0212 | 57.0921 | 10.7508 | 52.6057 | 0.32336 | 20.142 | 0.52823 | 0.057663 | -37.7487 | 3.122 | 69.66 | 49.14 | -0.58505 | 0.37585 | 0.29257 | -0.71545 | 0.22849 | -0.58719 | 0.18898 | 0.1286 | 0.078503 | 0.32924 | -0.027944 | 0.30919 | 0.19106 | 0.29998
42810.4429 | 246 | 18.507 | 18.5987 | 18.5671 | 18.5682 | 17.8699 | 16.4854 | 14.5406 | 16.6558 | 17.1422 | 17.2335 | 17.2496 | 16.7615 | 15.7809 | 14.3999 | 14.8955 | 14.9 | 15.46 | 13.3252 | 13.5252 | 14.2555 |  |  |  | 16.5403 | 15.8801 | 16.3207 | 71.0651 | 69.2942 | 78.9497 | 17.1549 | 16.2911 | 15.8741 | 16.8245 | 16.1115 | 16.0148 | 18.2199 | 71.4111 |  | 35.2092 | 59.1262 | 61.9138 | 26.1772 |  | 6.5605 | 6.7618 | 6.2258 | 6.4977 | 6.5617 | 7.6503 | 23.2306 | 4.7104 | 6.5468 | 4.5911 | 6.991 | 8.0875 | 42.5087 | 47.3526 | 43.2152 | 14.9831 |  |  | -0.25803 | -0.22924 | 0.12013 | -0.22211 | -0.14966 | -0.3737 | 0.19638 | 0.24888 | -0.65151 | -0.24102 | -0.35518 | 8.9024 | -0.00047641 | 1.9945 | 15.8754 | 16.7273 | 17.2438 | 17.5535 | 17.4944 | 16.4515 | 14.7942 | 16.8206 | 17.1536 | 17.4498 | 17.4819 | 17.2003 | 16.381 | 14.5754 | 14.3796 | 9.9527 | 9.2479 | 8.4556 | 7.9166 | 11.4177 | 9.3914 | 15.9709 | 15.556 | 15.3927 | 14.3145 | 14.3114 | 14.4829 |  |  |  | 17.2975 | 80.3094 | 65.4301 | 21.1442 | -0.0001538 | -0.067539 | 22.785 |  |  | 10.7521 |  |  | 16.8871 | 16.0823 | 17.2303 | 16.3485 | 15.6221 | 15.4469 | 68.1743 | 81.6521 | 54.2617 | 54.538 | 29.4855 |  | 19.1469 | 30.5708 | 19.7786 | 21.3546 | 18.4223 | 60.9413 |  | 31.1991 |  |  | 12.779 | 13.9451 | 24.1124 | [6 empty] | 20.0289 |  |  | 17.7748 |  |  | 11.7248 | 18.0636 | 89.3217 | 8.2309 | 14.5039 | 61.7169 | 9.0471 | 13.5469 | 66.1121 | 13.6078 | 58.2439 | 9.0208 | 48.921 | 9.9513 | 49.3889 | 9.162 | 16.0471 | 59.4535 | 13.5613 | 16.3132 | 77.3716 | 9.6711 | 14.527 | 67.624 | 9.9654 | 47.9051 | 13.0127 | 57.252 | 10.7656 | 52.7002 | -0.002516 | 20.1374 | 0.52952 | 0.05699 | -37.7866 | 3.1221 | 56.38 | 48.82 | -0.66425 | -0.55825 | 0.40412 | -0.54949 | -0.45177 | -0.71388 | 0.5175 | 0.1267 | 0.11769 | 0.32834 | 0.042724 | 0.37728 | 0.18762 | 0.29666
42810.4429 | 247 | 18.5063 | 18.5911 | 18.5669 | 18.5557 | 17.8668 | 16.4842 | 14.5327 | 16.6463 | 17.1403 | 17.233 | 17.2438 | 16.7566 | 15.7828 | 14.3874 | 14.8949 | 14.8983 | 15.4539 | 13.3288 | 13.5291 | 14.2581 |  |  |  | 16.5445 | 15.8812 | 16.3269 | 71.2155 | 69.343 | 79.7283 | 17.1591 | 16.2913 | 15.8855 | 16.8277 | 16.1101 | 16.0258 | 18.2597 | 71.1549 |  | 35.2918 | 59.2312 | 61.9787 | 27.106 |  | 6.5576 | 6.7573 | 6.2082 | 6.4722 | 6.5301 | 7.6215 | 22.9882 | 4.7624 | 6.5422 | 4.6455 | 6.9806 | 8.082 | 42.5077 | 47.3515 | 43.1991 | 14.9892 |  |  | -0.10098 | -0.094537 | 0.043904 | -0.15968 | -0.092488 | -0.32442 | 0.44148 | -0.036304 | -0.33353 | -0.86518 | -0.15688 | 8.9029 | -0.00048626 | 1.9977 | 15.88 | 16.7335 | 17.2501 | 17.5585 | 17.5016 | 16.4557 | 14.8005 | 16.8247 | 17.161 | 17.4453 | 17.493 | 17.2051 | 16.3939 | 14.5764 | 14.7905 | 10.1018 | 8.8669 | 8.1747 | 7.8521 | 11.4314 | 9.3957 | 15.9762 | 15.5606 | 15.402 | 14.3155 | 14.3128 | 14.4896 |  |  |  | 17.3393 | 80.3463 | 65.7619 | 21.7045 | -0.1985 | -0.045331 | 22.7737 |  |  | 10.7529 |  |  | 16.8842 | 16.0853 | 17.2424 | 16.3425 | 15.6174 | 15.4479 | 68.1627 | 81.7643 | 54.3645 | 54.6481 | 28.438 |  | 19.1889 | 29.9855 | 19.8315 | 21.1169 | 18.4576 | 60.2295 |  | 31.2763 |  |  | 12.7808 | 13.9358 | 23.8608 | [6 empty] | 19.9349 |  |  | 17.8284 |  |  | 11.7096 | 18.057 | 89.3642 | 8.2333 | 14.4476 | 61.8235 | 9.0326 | 13.5352 | 66.2037 | 13.6102 | 58.2072 | 8.9943 | 48.9595 | 9.9383 | 49.4159 | 9.1735 | 15.9856 | 59.5161 | 13.568 | 16.319 | 77.3477 | 9.6699 | 14.578 | 67.7019 | 9.9631 | 47.9435 | 13.0129 | 57.2889 | 10.771 | 52.7789 | 0.14425 | 20.1379 | 0.53083 | 0.056621 | -37.7454 | 3.1221 | 50.8 | 50.17 | -0.416 | -0.35849 | 0.2443 | -0.4659 | -0.35513 | -0.66511 | 0.77589 | 0.1572 | 0.13572 | 0.33613 | -0.0013529 | 0.42012 | 0.16315 | 0.28249
42810.4429 | 248 | 18.5028 | 18.589 | 18.5672 | 18.5493 | 17.8644 | 16.4841 | 14.5354 | 16.6397 | 17.1403 | 17.2327 | 17.2382 | 16.7539 | 15.7787 | 14.3854 | 14.9003 | 14.8943 | 15.46 | 13.3201 | 13.5312 | 14.2674 |  |  |  | 16.5455 | 15.8778 | 16.3329 | 71.3863 | 69.3647 | 79.9293 | 17.1571 | 16.2992 | 15.8956 | 16.8326 | 16.1086 | 16.0378 | 18.3066 | 70.8095 |  | 35.3836 | 59.3434 | 62.0591 | 27.8255 |  | 6.5598 | 6.7624 | 6.1895 | 6.4581 | 6.5209 | 7.607 | 22.7776 | 4.8206 | 6.5481 | 4.6412 | 6.9915 | 8.0881 | 42.4976 | 47.3355 | 43.1741 | 14.996 |  |  | -0.41836 | -0.10176 | 0.13196 | -0.25496 | -0.16346 | -0.31456 | 0.40797 | 0.10235 | -0.38996 | 0.40999 | -0.15609 | 8.9028 | -0.00046327 | 1.9977 | 15.8607 | 16.7173 | 17.235 | 17.5486 | 17.493 | 16.4352 | 14.7907 | 16.8059 | 17.145 | 17.4311 | 17.4768 | 17.1935 | 16.3694 | 14.5626 | 14.4823 | 10.2877 | 9.0851 | 7.9102 | 7.7737 | 11.4313 | 9.3962 | 15.9787 | 15.5615 | 15.3988 | 14.3185 | 14.3152 | 14.4984 |  |  |  | 17.386 | 80.3559 | 66.0305 | 21.9677 | 0.022537 | -0.24313 | 22.7396 |  |  | 10.7577 |  |  | 16.8809 | 16.0876 | 17.273 | 16.3448 | 15.6246 | 15.4598 | 68.1321 | 81.8997 | 54.4513 | 54.757 | 27.259 |  | 19.2301 | 30.1318 | 19.8797 | 20.9154 | 18.4914 | 59.6806 |  | 31.3671 |  |  | 12.7869 | 13.9487 | 23.6948 | [6 empty] | 19.7789 |  |  | 17.8806 |  |  | 11.7303 | 18.073 | 89.4537 | 8.2421 | 14.4057 | 61.8899 | 9.0535 | 13.5535 | 66.3855 | 13.6195 | 58.1674 | 8.9844 | 49.0476 | 9.9465 | 49.4836 | 9.1649 | 15.9368 | 59.5414 | 13.5723 | 16.3288 | 77.4164 | 9.6714 | 14.6338 | 67.7193 | 9.9721 | 47.9929 | 13.0127 | 57.3895 | 10.7697 | 52.8411 | 0.32587 | 20.1354 | 0.53111 | 0.055796 | -37.7648 | 3.122 | 59.7 | 49.02 | -0.84699 | -0.37194 | 0.42354 | -0.58873 | -0.4721 | -0.65491 | 0.74584 | 0.19133 | 0.13327 | 0.34285 | 0.032885 | 0.39592 | 0.14473 | 0.27673
42810.4429 | 249 | 18.4955 | 18.5871 | 18.5647 | 18.5577 | 17.8666 | 16.4777 | 14.5329 | 16.6484 | 17.1307 | 17.227 | 17.2322 | 16.7616 | 15.7789 | 14.3818 | 14.899 | 14.8996 | 15.458 | 13.3169 | 13.5305 | 14.2747 |  |  |  | 16.5459 | 15.8773 | 16.3471 | 71.5332 | 69.3878 | 80.3422 | 17.1604 | 16.3017 | 15.9048 | 16.8297 | 16.1137 | 16.0474 | 18.3659 | 70.6472 |  | 35.4778 | 59.45 | 62.1514 | 29.3545 |  | 6.5567 | 6.7645 | 6.1827 | 6.4464 | 6.5073 | 7.597 | 23.088 | 4.9037 | 6.5463 | 4.6009 | 6.9922 | 8.082 | 42.4804 | 47.3073 | 43.1645 | 15.0034 |  |  | -0.3198 | -0.082053 | 0.17993 | -0.25102 | -0.019548 | 0.19208 | 0.10307 | 0.069492 | -0.31446 | -0.24249 | -0.20914 | 8.9024 | -0.00043041 | 1.9839 | 15.8663 | 16.721 | 17.2383 | 17.547 | 17.49 | 16.4512 | 14.7908 | 16.8097 | 17.1503 | 17.4473 | 17.4846 | 17.2009 | 16.3749 | 14.5688 | 14.4503 | 10.127 | 8.9788 | 7.8814 | 7.6297 | 11.4431 | 9.3965 | 15.9691 | 15.5578 | 15.3937 | 14.3135 | 14.3091 | 14.4911 |  |  |  | 17.419 | 80.3897 | 66.0512 | 21.7417 | -0.0062318 | -0.3218 | 22.702 |  |  | 10.7592 |  |  | 16.8797 | 16.0837 | 17.2923 | 16.348 | 15.6207 | 15.4691 | 68.1169 | 82.0063 | 54.5041 | 54.8351 | 26.4017 |  | 19.2706 | 30.1808 | 19.9269 | 20.7401 | 18.5242 | 59.3532 |  | 31.4675 |  |  | 12.8037 | 13.9679 | 23.659 | [6 empty] | 19.7146 |  |  | 17.9085 |  |  | 11.7303 | 18.1022 | 89.6852 | 8.2466 | 14.3737 | 61.9004 | 9.0592 | 13.5546 | 66.4972 | 13.6341 | 58.0851 | 8.9618 | 49.1466 | 9.9615 | 49.526 | 9.1667 | 16.008 | 59.5723 | 13.5771 | 16.3602 | 77.556 | 9.6749 | 14.6745 | 67.7717 | 9.993 | 48.061 | 13.0219 | 57.4802 | 10.7724 | 52.8914 | 0.27136 | 20.1321 | 0.53366 | 0.056288 | -37.7618 | 3.1221 | 63.47 | 49.08 | -0.74096 | -0.33398 | 0.49457 | -0.58416 | -0.16326 | 0.51175 | 0.37487 | 0.2165 | 0.13349 | 0.34882 | 0.037809 | 0.40777 | 0.10424 | 0.28411
42810.4429 | 250 | 18.4913 | 18.5832 | 18.5563 | 18.5514 | 17.8541 | 16.4709 | 14.5207 | 16.6385 | 17.129 | 17.222 | 17.2264 | 16.7511 | 15.7673 | 14.3776 | 14.8942 | 14.9026 | 15.4577 | 13.3255 | 13.5357 | 14.2808 |  |  |  | 16.5539 | 15.8848 | 16.3627 | 71.7219 | 69.425 | 80.8395 | 17.1512 | 16.2941 | 15.913 | 16.8346 | 16.1134 | 16.0562 | 18.4284 | 71.0496 |  | 35.575 | 59.5496 | 62.2367 | 30.1755 |  | 6.5435 | 6.7515 | 6.1749 | 6.4432 | 6.4951 | 7.626 | 23.2147 | 4.9977 | 6.5414 | 4.6539 | 6.9849 | 8.076 | 42.4726 | 47.2892 | 43.1558 | 15.0117 |  |  | -0.29548 | -0.070881 | -0.11446 | -0.26416 | -0.12863 | -0.35859 | 0.4658 | 0.12666 | 0.37092 | -0.3946 | -0.36631 | 8.9026 | -0.00051255 | 1.9739 | 15.8661 | 16.7242 | 17.2423 | 17.5533 | 17.4986 | 16.4518 | 14.7897 | 16.8133 | 17.149 | 17.4468 | 17.491 | 17.1986 | 16.3788 | 14.5749 | 15.0248 | 10.3694 | 8.9004 | 7.7222 | 7.5119 | 11.483 | 9.401 | 15.9675 | 15.5563 | 15.3842 | 14.3137 | 14.3105 | 14.4959 |  |  |  | 17.4549 | 80.5874 | 66.135 | 21.3662 | 0.11857 | -0.24501 | 22.6848 |  |  | 10.7587 |  |  | 16.8859 | 16.088 | 17.3127 | 16.3514 | 15.6243 | 15.4796 | 68.1424 | 82.0873 | 54.5378 | 54.8955 | 27.0714 |  | 19.3339 | 30.9574 | 19.9783 | 20.6888 | 18.5805 | 59.2083 |  | 31.5558 |  |  | 12.795 | 13.9679 | 23.7006 | [6 empty] | 19.8284 |  |  | 17.9347 |  |  | 11.7369 | 18.1053 | 89.6727 | 8.2536 | 14.4953 | 61.9063 | 9.0686 | 13.5534 | 66.5758 | 13.6491 | 57.9205 | 8.9706 | 49.2123 | 9.9767 | 49.5911 | 9.1617 | 16.0547 | 59.6665 | 13.5834 | 16.3881 | 77.766 | 9.6765 | 14.7029 | 67.7943 | 10.0126 | 48.138 | 13.028 | 57.4883 | 10.7765 | 52.9431 | 0.41234 | 20.1303 | 0.53617 | 0.058206 | -37.7418 | 3.1221 | 67.32 | 50.03 | -0.71273 | -0.31041 | -0.39445 | -0.59925 | -0.41881 | -0.69927 | 0.79698 | 0.20001 | 0.11364 | 0.35212 | -0.021371 | 0.41702 | 0.083524 | 0.29574
42810.4429 | 251 | 18.4895 | 18.5847 | 18.5673 | 18.555 | 17.8622 | 16.4692 | 14.5313 | 16.6469 | 17.1365 | 17.2286 | 17.2319 | 16.7642 | 15.7755 | 14.3849 | 14.8897 | 14.8988 | 15.4552 | 13.3183 | 13.53 | 14.271 |  |  |  | 16.5522 | 15.8859 | 16.374 | 71.8616 | 69.4338 | 80.6612 | 17.1478 | 16.293 | 15.9181 | 16.8314 | 16.1118 | 16.0604 | 18.4744 | 71.2666 |  | 35.6486 | 59.642 | 62.2971 | 29.3179 |  | 6.5355 | 6.7346 | 6.1696 | 6.443 | 6.4888 | 7.7089 | 23.5526 | 5.1248 | 6.5434 | 4.6776 | 6.9866 | 8.0831 | 42.4838 | 47.2798 | 43.157 | 15.0156 |  |  | -0.22714 | -0.082709 | 0.043904 | -0.39033 | 0.061276 | 0.12242 | 0.33569 | -0.016592 | -0.1401 | 0.97582 | -0.3369 | 8.9029 | -0.00046655 | 1.9781 | 15.8632 | 16.7238 | 17.2417 | 17.5501 | 17.4973 | 16.4486 | 14.7899 | 16.8115 | 17.1484 | 17.4471 | 17.4799 | 17.1975 | 16.3712 | 14.5722 | 16.4264 | 11.0872 | 10.1063 | 7.7221 | 7.2605 | 11.531 | 9.4124 | 15.9597 | 15.549 | 15.3935 | 14.3097 | 14.3156 | 14.4976 |  |  |  | 17.4923 | 80.7307 | 66.2453 | 21.3369 | 0.054548 | -0.16126 | 22.7692 |  |  | 10.7597 |  |  | 16.8866 | 16.0948 | 17.3244 | 16.3493 | 15.6298 | 15.4913 | 68.16 | 82.1734 | 54.6144 | 54.9854 | 28.2192 |  | 19.3916 | 33.0304 | 20.0593 | 20.4863 | 18.6213 | 59.3332 |  | 31.6268 |  |  | 12.7695 | 13.9621 | 23.7273 | [6 empty] | 19.9555 |  |  | 17.9507 |  |  | 11.7411 | 18.1002 | 89.5479 | 8.2263 | 14.8406 | 61.8492 | 9.0762 | 13.5493 | 66.6363 | 13.6532 | 57.9476 | 8.9697 | 49.2497 | 9.9775 | 49.6713 | 9.1501 | 16.0191 | 59.7497 | 13.5937 | 16.3863 | 78.1055 | 9.6745 | 14.7261 | 67.8165 | 10.026 | 48.26 | 13.0235 | 57.4326 | 10.7687 | 52.9982 | 0.3457 | 20.1271 | 0.53699 | 0.058155 | -37.8796 | 3.1221 | 59.5 | 49 | -0.62474 | -0.3353 | 0.24429 | -0.7284 | 0.28911 | 0.40864 | 0.67667 | 0.17006 | 0.058769 | 0.35911 | -0.17152 | 0.28434 | 0.10888 | 0.2978
42810.443 | 252 | 18.4951 | 18.5952 | 18.5687 | 18.5555 | 17.8666 | 16.4782 | 14.5335 | 16.6453 | 17.1394 | 17.2352 | 17.232 | 16.76 | 15.7825 | 14.3952 | 14.889 | 14.8987 | 15.4548 | 13.3108 | 13.5255 | 14.2745 |  |  |  | 16.544 | 15.8762 | 16.3848 | 71.9421 | 69.4242 | 80.2291 | 17.1607 | 16.2947 | 15.9373 | 16.8335 | 16.1114 | 16.0852 | 18.5176 | 71.3248 |  | 35.7352 | 59.7237 | 62.3392 | 28.2143 |  | 6.5255 | 6.725 | 6.1558 | 6.4322 | 6.4883 | 7.8214 | 23.6942 | 5.1547 | 6.5406 | 4.7002 | 6.9882 | 8.0808 | 42.4811 | 47.2638 | 43.1424 | 15.0096 |  |  | -0.30534 | -0.011741 | -0.1046 | -0.29373 | 0.039592 | -0.041856 | 0.42374 | -0.14736 | -0.34131 | 0.6179 | -0.32637 | 8.9029 | -0.00048298 | 1.9909 | 15.8592 | 16.7272 | 17.2408 | 17.5515 | 17.4944 | 16.4517 | 14.7906 | 16.815 | 17.1531 | 17.4452 | 17.4745 | 17.1981 | 16.3702 | 14.5727 | 16.9285 | 11.5334 | 11.2917 | 7.9789 | 7.2654 | 11.5776 | 9.4278 | 15.9629 | 15.5447 | 15.3913 | 14.3073 | 14.3122 | 14.5015 |  |  |  | 17.5316 | 80.7006 | 66.1308 | 21.1467 | -0.12779 | -0.13077 | 22.9452 |  |  | 10.7588 |  |  | 16.8854 | 16.0915 | 17.3463 | 16.3438 | 15.6243 | 15.4938 | 68.1972 | 82.242 | 54.7079 | 55.0709 | 28.5334 |  | 19.4599 | 35.3829 | 20.1536 | 20.2625 | 18.665 | 59.7301 |  | 31.7181 |  |  | 12.7689 | 13.9619 | 23.789 | [6 empty] | 19.9215 |  |  | 17.9742 |  |  | 11.749 | 18.1123 | 89.4601 | 8.1862 | 15.1834 | 61.8132 | 9.0853 | 13.556 | 66.6782 | 13.6551 | 58.1366 | 8.9815 | 49.2959 | 9.9876 | 49.7747 | 9.1664 | 16.0091 | 59.7907 | 13.606 | 16.4056 | 78.3195 | 9.6773 | 14.7423 | 67.8646 | 10.0389 | 48.376 | 13.0165 | 57.4577 | 10.777 | 53.0667 | 0.34436 | 20.1248 | 0.53817 | 0.057808 | -37.8577 | 3.1221 | 53.96 | 49.46 | -0.7239 | -0.12633 | -0.37707 | -0.63186 | 0.23244 | -0.23899 | 0.76041 | 0.16362 | -0.0034194 | 0.36679 | -0.2219 | 0.15443 | 0.14098 | 0.30439
42810.443 | 253 | 18.4866 | 18.5807 | 18.5621 | 18.5583 | 17.8615 | 16.4686 | 14.5263 | 16.6439 | 17.1334 | 17.2298 | 17.2324 | 16.753 | 15.774 | 14.3907 | 14.8857 | 14.8976 | 15.4531 | 13.3156 | 13.5295 | 14.2844 |  |  |  | 16.55 | 15.8802 | 16.3963 | 72.088 | 69.5389 | 80.7318 | 17.16 | 16.3057 | 15.9318 | 16.8287 | 16.1172 | 16.0858 | 18.5412 | 71.6759 |  | 35.8341 | 59.7656 | 62.3836 | 27.4276 |  | 6.526 | 6.7197 | 6.1412 | 6.4235 | 6.4847 | 7.8794 | 23.7873 | 5.0817 | 6.548 | 4.7718 | 6.9844 | 8.0822 | 42.4883 | 47.2404 | 43.1348 | 15.0023 |  |  | -0.32702 | -0.12674 | -0.002748 | -0.12879 | -0.087888 | -0.069456 | 0.44411 | -0.077704 | -0.36817 | -0.77056 | -0.29557 | 8.9025 | -0.00047969 | 1.9931 | 15.8655 | 16.7287 | 17.2493 | 17.545 | 17.5009 | 16.4564 | 14.788 | 16.8081 | 17.1509 | 17.4426 | 17.4811 | 17.203 | 16.3733 | 14.5683 | 16.2741 | 11.2405 | 11.7197 | 8.2584 | 7.5285 | 11.5864 | 9.4286 | 15.9596 | 15.5442 | 15.3884 | 14.3022 | 14.3094 | 14.5018 |  |  |  | 17.5746 | 80.6123 | 65.827 | 21.0265 | -0.046347 | -0.13341 | 23.0908 |  |  | 10.7573 |  |  | 16.8853 | 16.0936 | 17.373 | 16.3406 | 15.6247 | 15.5004 | 68.2769 | 82.2981 | 54.7884 | 55.1442 | 29.04 |  | 19.5292 | 35.6236 | 20.2326 | 20.2157 | 18.7053 | 59.3055 |  | 31.8221 |  |  | 12.7951 | 13.977 | 23.9797 | [6 empty] | 19.9407 |  |  | 18.0032 |  |  | 11.7541 | 18.1294 | 89.4724 | 8.1502 | 15.3304 | 61.8795 | 9.0953 | 13.5824 | 66.7733 | 13.6522 | 58.2865 | 8.9815 | 49.3599 | 9.9903 | 49.8782 | 9.1532 | 16.0347 | 59.812 | 13.6064 | 16.4393 | 78.398 | 9.6794 | 14.7544 | 67.9637 | 10.0437 | 48.4373 | 13.0073 | 57.6478 | 10.788 | 53.1665 | 0.27772 | 20.1234 | 0.53893 | 0.057301 | -37.9165 | 3.1221 | 69.37 | 49.92 | -0.7497 | -0.41505 | -0.061116 | -0.4184 | -0.34634 | -0.30789 | 0.77855 | 0.15187 | -0.0074592 | 0.36944 | -0.14815 | 0.10696 | 0.16362 | 0.30917
42810.443 | 254 | 18.4894 | 18.5879 | 18.57 | 18.5553 | 17.8623 | 16.475 | 14.5303 | 16.6423 | 17.139 | 17.2274 | 17.2342 | 16.7518 | 15.7687 | 14.3881 | 14.8872 | 14.8922 | 15.4532 | 13.3191 | 13.5331 | 14.2905 |  |  |  | 16.5507 | 15.8897 | 16.416 | 72.3024 | 69.7296 | 81.4021 | 17.1545 | 16.2966 | 15.9461 | 16.8324 | 16.1141 | 16.0959 | 18.5921 | 72.2545 |  | 35.9334 | 59.8079 | 62.4444 | 27.5697 |  | 6.5118 | 6.7147 | 6.1412 | 6.4267 | 6.4794 | 7.8536 | 24.1031 | 5.0314 | 6.5493 | 4.8532 | 6.9887 | 8.075 | 42.5 | 47.2099 | 43.1252 | 15 |  |  | -0.43216 | -0.14119 | -0.044804 | 0.001314 | -0.1214 | 0.16382 | 0.11687 | 0.21077 | 0.021421 | -0.51271 | -0.37287 | 8.9026 | -0.00045012 | 1.9874 | 15.8625 | 16.7184 | 17.245 | 17.546 | 17.4966 | 16.4513 | 14.7861 | 16.8108 | 17.1487 | 17.4408 | 17.4821 | 17.1955 | 16.3736 | 14.5671 | 16.5263 | 11.0712 | 11.6847 | 8.5455 | 7.8117 | 11.6138 | 9.4495 | 15.9578 | 15.5467 | 15.3922 | 14.3072 | 14.3152 | 14.5111 |  |  |  | 17.6217 | 80.5664 | 65.5804 | 21.0957 | -0.18452 | -0.17237 | 23.092 |  |  | 10.7549 |  |  | 16.8839 | 16.0939 | 17.3859 | 16.3405 | 15.6259 | 15.5102 | 68.3177 | 82.3386 | 54.8492 | 55.2089 | 29.6828 |  | 19.6027 | 33.4521 | 20.2671 | 20.3279 | 18.7414 | 59.227 |  | 31.9053 |  |  | 12.8142 | 13.9963 | 24.2529 | [6 empty] | 20.0766 |  |  | 18.0443 |  |  | 11.7565 | 18.1364 | 89.4565 | 8.1299 | 15.2968 | 61.9909 | 9.0961 | 13.5903 | 66.8619 | 13.6497 | 58.3081 | 8.9936 | 49.4071 | 9.9952 | 49.9957 | 9.1134 | 16.1009 | 59.8785 | 13.6147 | 16.4621 | 78.4198 | 9.6814 | 14.7506 | 68.0594 | 10.0589 | 48.478 | 12.9945 | 57.8805 | 10.7785 | 53.2711 | 0.286 | 20.1211 | 0.53919 | 0.056975 | -37.9444 | 3.1221 | 87.79 | 49.26 | -0.86264 | -0.43807 | -0.24677 | 0.042261 | -0.40704 | 0.47283 | 0.39937 | 0.13647 | 0.054018 | 0.36752 | -0.17299 | 0.11328 | 0.16138 | 0.30881
42810.443 | 255 | 18.4861 | 18.5863 | 18.5621 | 18.5584 | 17.862 | 16.4783 | 14.5291 | 16.6353 | 17.1311 | 17.2244 | 17.2282 | 16.7507 | 15.767 | 14.3831 | 14.888 | 14.897 | 15.4602 | 13.3217 | 13.5376 | 14.2917 |  |  |  | 16.5498 | 15.8899 | 16.4322 | 72.461 | 69.8939 | 81.1946 | 17.1487 | 16.284 | 15.9451 | 16.8276 | 16.1043 | 16.097 | 18.6493 | 72.678 |  | 36.0211 | 59.8465 | 62.5216 | 27.8467 |  | 6.5021 | 6.7133 | 6.1263 | 6.4185 | 6.4773 | 7.838 | 24.4519 | 5.0395 | 6.5506 | 4.8571 | 6.9951 | 8.0853 | 42.5243 | 47.209 | 43.1186 | 14.9886 |  |  | -0.35396 | -0.053137 | 0.11553 | -0.22342 | -0.1628 | -0.34413 | 0.0643 | 0.36979 | -1.492 | 0.18047 | -0.40685 | 8.9033 | -0.00045012 | 1.9869 | 15.8613 | 16.7219 | 17.2389 | 17.5524 | 17.4947 | 16.4515 | 14.794 | 16.8037 | 17.1467 | 17.4418 | 17.4785 | 17.1972 | 16.3685 | 14.5606 | 15.9646 | 10.9415 | 11.7486 | 8.5964 | 8.0248 | 11.6303 | 9.4586 | 15.9607 | 15.5529 | 15.3906 | 14.3095 | 14.3157 | 14.517 |  |  |  | 17.6708 | 80.5908 | 65.9073 | 21.4198 | -0.14704 | -0.16314 | 22.9869 |  |  | 10.7622 |  |  | 16.8884 | 16.0989 | 17.4063 | 16.3505 | 15.6314 | 15.5234 | 68.3587 | 82.376 | 54.9141 | 55.289 | 28.7918 |  | 19.6658 | 31.5015 | 20.3012 | 20.3 | 18.7856 | 58.9272 |  | 31.9903 |  |  | 12.8358 | 13.9989 | 24.1553 | [6 empty] | 20.1488 |  |  | 18.0649 |  |  | 11.7675 | 18.1515 | 89.38 | 8.1335 | 15.2374 | 62.054 | 9.0958 | 13.5893 | 66.8887 | 13.6606 | 58.2939 | 9.0001 | 49.4125 | 10.0147 | 50.1045 | 9.103 | 16.1383 | 59.9283 | 13.6218 | 16.4825 | 78.5532 | 9.6816 | 14.7533 | 68.1832 | 10.0787 | 48.5054 | 12.9848 | 58.0902 | 10.7719 | 53.3443 | 0.067398 | 20.1195 | 0.54227 | 0.057808 | -38.0488 | 3.1221 | 77.58 | 49.22 | -0.78048 | -0.26874 | 0.39627 | -0.55106 | -0.47134 | -0.68529 | 0.29622 | 0.16333 | 0.10934 | 0.36977 | -0.10865 | 0.10723 | 0.15559 | 0.30145
42810.443 | 256 | 18.4842 | 18.5864 | 18.5648 | 18.5548 | 17.8681 | 16.4779 | 14.5309 | 16.6417 | 17.1303 | 17.2279 | 17.2324 | 16.7543 | 15.7677 | 14.3863 | 14.8808 | 14.8985 | 15.4549 | 13.3148 | 13.5345 | 14.2976 |  |  |  | 16.5495 | 15.8929 | 16.4398 | 72.5127 | 69.9668 | 80.6741 | 17.1547 | 16.2987 | 15.9534 | 16.8291 | 16.1108 | 16.1057 | 18.7111 | 72.9986 |  | 36.1258 | 59.891 | 62.605 | 28.4304 |  | 6.4997 | 6.7093 | 6.1251 | 6.419 | 6.468 | 7.8054 | 24.9801 | 5.1956 | 6.5615 | 4.825 | 6.9933 | 8.073 | 42.5539 | 47.2102 | 43.115 | 14.9703 |  |  | -0.4453 | -0.20624 | -0.006692 | 0.026942 | 0.068504 | -0.34216 | 0.17075 | 0.24297 | -0.83307 | -1.8382 | -0.25504 | 8.9028 | -0.00044848 | 1.9913 | 15.8584 | 16.7141 | 17.2291 | 17.5433 | 17.4881 | 16.4463 | 14.7899 | 16.801 | 17.1531 | 17.4418 | 17.4705 | 17.1935 | 16.3642 | 14.5597 | 15.7956 | 10.9935 | 11.8047 | 8.699 | 8.2717 | 11.6507 | 9.4682 | 15.9528 | 15.5483 | 15.3883 | 14.3052 | 14.3131 | 14.5145 |  |  |  | 17.7097 | 80.6214 | 65.9183 | 21.522 | 0.037125 | -0.16503 | 22.9393 |  |  | 10.7651 |  |  | 16.8897 | 16.0978 | 17.4231 | 16.3514 | 15.6284 | 15.526 | 68.4461 | 82.3518 | 54.962 | 55.3751 | 27.1333 |  | 19.7019 | 30.6135 | 20.3525 | 20.2505 | 18.8151 | 58.7708 |  | 32.0652 |  |  | 12.8599 | 14.0141 | 23.8664 | [6 empty] | 20.0944 |  |  | 18.0995 |  |  | 11.7743 | 18.1696 | 89.4138 | 8.111 | 15.1836 | 62.0973 | 9.0871 | 13.5764 | 66.907 | 13.6633 | 58.323 | 8.9746 | 49.4058 | 10.0232 | 50.2013 | 9.0954 | 16.1487 | 59.9925 | 13.6254 | 16.5065 | 78.7018 | 9.689 | 14.7594 | 68.2104 | 10.0948 | 48.5133 | 12.9874 | 58.1481 | 10.7734 | 53.3744 | 0.37171 | 20.1179 | 0.54438 | 0.058517 | -38.0174 | 3.1221 | 53.06 | 49.28 | -0.87476 | -0.52945 | -0.095371 | 0.19136 | 0.30573 | -0.68328 | 0.48269 | 0.21061 | 0.13573 | 0.37214 | -0.087515 | 0.10213 | 0.14144 | 0.29991
42810.443 | 257 | 18.4866 | 18.5869 | 18.5661 | 18.5515 | 17.8654 | 16.474 | 14.5316 | 16.6371 | 17.1334 | 17.2261 | 17.2286 | 16.7535 | 15.7692 | 14.3895 | 14.8768 | 14.8813 | 15.4403 | 13.3071 | 13.5226 | 14.2941 |  |  |  | 16.5435 | 15.8822 | 16.4446 | 72.5678 | 70.0566 | 80.5156 | 17.1511 | 16.2946 | 15.9662 | 16.8258 | 16.1085 | 16.1198 | 18.7638 | 72.843 |  | 36.2325 | 59.9146 | 62.6464 | 30.5435 |  | 6.494 | 6.7109 | 6.1227 | 6.406 | 6.4681 | 7.7807 | 25.2509 | 5.3743 | 6.5674 | 4.7909 | 6.9889 | 8.078 | 42.5951 | 47.2219 | 43.127 | 14.9724 |  |  | -0.41705 | -0.27787 | 0.13919 | -0.033514 | -0.10694 | -0.41378 | 0.37708 | -0.3077 | -0.27534 | 0.68294 | -0.24908 | 8.9019 | -0.00042877 | 1.9882 | 15.8547 | 16.7186 | 17.2276 | 17.5465 | 17.4911 | 16.4454 | 14.7848 | 16.8016 | 17.1489 | 17.4357 | 17.4863 | 17.1926 | 16.3639 | 14.5559 | 15.7151 | 11.0217 | 12.0032 | 8.8025 | 8.2369 | 11.6711 | 9.4834 | 15.9423 | 15.5403 | 15.3776 | 14.3019 | 14.3032 | 14.5124 |  |  |  | 17.7435 | 80.6476 | 65.925 | 21.1485 | -0.013525 | -0.13077 | 22.9711 |  |  | 10.7651 |  |  | 16.8863 | 16.0941 | 17.4406 | 16.3494 | 15.6225 | 15.5352 | 68.5872 | 82.3711 | 55.0108 | 55.4567 | 26.0927 |  | 19.7443 | 30.7135 | 20.4149 | 20.2149 | 18.8508 | 58.888 |  | 32.1605 |  |  | 12.8698 | 14.0079 | 23.5703 | [6 empty] | 19.9579 |  |  | 18.1001 |  |  | 11.7797 | 18.1745 | 89.5559 | 8.0727 | 15.1752 | 62.2157 | 9.0813 | 13.5782 | 66.9017 | 13.6566 | 58.3351 | 8.9501 | 49.4428 | 10.0186 | 50.3273 | 9.0886 | 16.2004 | 60.0004 | 13.6242 | 16.5161 | 78.7036 | 9.6817 | 14.7461 | 68.2429 | 10.09 | 48.5893 | 12.9764 | 58.3618 | 10.7692 | 53.4219 | 0.31065 | 20.1165 | 0.54569 | 0.058061 | -38.0994 | 3.1221 | 58.26 | 48.93 | -0.84636 | -0.61456 | 0.43495 | -0.21343 | -0.38198 | -0.75137 | 0.71727 | 0.24093 | 0.13504 | 0.37432 | -0.076192 | 0.081826 | 0.084506 | 0.31141
42810.443 | 258 | 18.4849 | 18.5926 | 18.5659 | 18.5562 | 17.8629 | 16.4751 | 14.538 | 16.6416 | 17.1394 | 17.2328 | 17.2283 | 16.7575 | 15.7692 | 14.3884 | 14.8813 | 14.8884 | 15.452 | 13.3168 | 13.5351 | 14.3035 |  |  |  | 16.5498 | 15.8936 | 16.472 | 72.637 | 70.203 | 80.4343 | 17.1457 | 16.2881 | 15.9682 | 16.8225 | 16.107 | 16.1261 | 18.811 | 72.7517 |  | 36.3158 | 59.9537 | 62.6766 | 30.4811 |  | 6.4912 | 6.6978 | 6.1186 | 6.401 | 6.4646 | 7.7636 | 25.3857 | 5.3794 | 6.558 | 4.7849 | 6.9844 | 8.0614 | 42.5991 | 47.222 | 43.1264 | 14.9541 |  |  | -0.17655 | -0.10242 | -0.015892 | 0.067682 | -0.060948 | -0.37436 | 0.2588 | -0.008048 | -0.19711 | -0.1057 | -0.2616 | 8.903 | -0.00048791 | 1.9667 | 15.8576 | 16.7196 | 17.2348 | 17.5412 | 17.4888 | 16.441 | 14.7834 | 16.807 | 17.145 | 17.4367 | 17.4809 | 17.1925 | 16.3632 | 14.5599 | 15.8657 | 10.9378 | 11.9935 | 9.0315 | 8.1921 | 11.691 | 9.4944 | 15.9527 | 15.549 | 15.3862 | 14.3048 | 14.323 | 14.5262 |  |  |  | 17.7814 | 80.6135 | 66.06 | 20.9331 | 0.032465 | -0.15995 | 22.965 |  |  | 10.7698 |  |  | 16.8782 | 16.0965 | 17.4591 | 16.3452 | 15.6312 | 15.5452 | 68.6972 | 82.4713 | 55.0513 | 55.5355 | 25.9252 |  | 19.7807 | 30.1889 | 20.4587 | 20.0957 | 18.8798 | 59.0238 |  | 32.2297 |  |  | 12.874 | 13.9797 | 23.5036 | [6 empty] | 19.834 |  |  | 18.1144 |  |  | 11.8034 | 18.1867 | 89.5418 | 8.0633 | 15.1718 | 62.3061 | 9.0811 | 13.5962 | 66.9753 | 13.6609 | 58.3166 | 8.9612 | 49.5183 | 10.0221 | 50.4496 | 9.1024 | 16.2638 | 60.097 | 13.6526 | 16.5527 | 78.7322 | 9.7062 | 14.7791 | 68.3095 | 10.1012 | 48.7027 | 13.0028 | 58.6809 | 10.7886 | 53.5168 | 0.43449 | 20.115 | 0.54682 | 0.059074 | -38.0977 | 3.1221 | 38.01 | 50.13 | -0.55061 | -0.3731 | -0.14697 | 0.30329 | -0.28836 | -0.71466 | 0.59421 | 0.24681 | 0.15108 | 0.3786 | -0.090621 | 0.084191 | 0.087817 | 0.31866
42810.443 | 259 | 18.4815 | 18.583 | 18.565 | 18.5489 | 17.8548 | 16.4654 | 14.5145 | 16.6447 | 17.126 | 17.2249 | 17.2262 | 16.7489 | 15.7718 | 14.384 | 14.8772 | 14.8875 | 15.4474 | 13.3069 | 13.5308 | 14.3062 |  |  |  | 16.5488 | 15.8773 | 16.4803 | 72.6433 | 70.2828 | 80.289 | 17.1427 | 16.2909 | 15.9827 | 16.8222 | 16.1087 | 16.133 | 18.8568 | 72.5015 |  | 36.4134 | 60.0672 | 62.7384 | 29.4341 |  | 6.4874 | 6.7009 | 6.1186 | 6.3993 | 6.4487 | 7.7472 | 25.3004 | 5.3838 | 6.5668 | 4.9173 | 6.9865 | 8.0676 | 42.6065 | 47.2292 | 43.1274 | 14.9496 |  |  | -0.46765 | -0.061681 | 0.074792 | -0.13339 | -0.045176 | -0.58661 | 0.25552 | 0.35271 | -0.42596 | 0.058152 | -0.20914 | 8.9027 | -0.00047312 | 1.9708 | 15.8625 | 16.718 | 17.233 | 17.5467 | 17.5 | 16.4496 | 14.7863 | 16.8139 | 17.1468 | 17.4413 | 17.4793 | 17.1982 | 16.3646 | 14.5648 | 16.447 | 11.3379 | 11.7994 | 9.1636 | 8.5508 | 11.7195 | 9.5019 | 15.953 | 15.5438 | 15.3791 | 14.2989 | 14.3143 | 14.5326 |  |  |  | 17.8172 | 80.5492 | 66.1518 | 20.8276 | 0.14389 | -0.25235 | 22.9304 |  |  | 10.7732 |  |  | 16.8723 | 16.0935 | 17.4825 | 16.3418 | 15.6331 | 15.5466 | 68.726 | 82.5464 | 55.0874 | 55.6119 | 26.7993 |  | 19.841 | 28.5816 | 20.5112 | 19.9662 | 18.912 | 59.3382 |  | 32.3394 |  |  | 12.9038 | 13.9689 | 23.5787 | [6 empty] | 19.7658 |  |  | 18.1425 |  |  | 11.8063 | 18.1865 | 89.6551 | 8.0246 | 15.1265 | 62.2316 | 9.0732 | 13.572 | 66.9633 | 13.6512 | 58.1792 | 8.9539 | 49.5937 | 10.0148 | 50.539 | 9.0983 | 16.2415 | 60.1788 | 13.6513 | 16.5691 | 78.8315 | 9.7011 | 14.8039 | 68.3853 | 10.0899 | 48.824 | 12.9998 | 58.7345 | 10.7836 | 53.5531 | 0.32529 | 20.1144 | 0.54773 | 0.057988 | -38.074 | 3.1221 | 50.7 | 49.37 | -0.89595 | -0.28954 | 0.31883 | -0.42579 | -0.24825 | -0.89457 | 0.59041 | 0.22455 | 0.19749 | 0.38327 | -0.15189 | 0.10662 | 0.11843 | 0.32278
42810.443 | 260 | 18.4865 | 18.5811 | 18.5701 | 18.5524 | 17.8625 | 16.4736 | 14.521 | 16.6341 | 17.1268 | 17.223 | 17.2336 | 16.7494 | 15.7684 | 14.3904 | 14.8747 | 14.8802 | 15.446 | 13.3048 | 13.5337 | 14.3037 |  |  |  | 16.5422 | 15.8669 | 16.4971 | 72.6508 | 70.3332 | 80.1475 | 17.1302 | 16.2893 | 15.9861 | 16.8259 | 16.1064 | 16.1493 | 18.8857 | 72.2972 |  | 36.5214 | 60.1494 | 62.7957 | 28.6174 |  | 6.4785 | 6.7033 | 6.1215 | 6.4016 | 6.4477 | 7.7233 | 24.9005 | 5.3853 | 6.5649 | 5.0424 | 6.9965 | 8.07 | 42.6208 | 47.2453 | 43.1334 | 14.9434 |  |  | -0.32243 | 0.000747 | -0.079632 | 0.086738 | -0.055032 | -0.49855 | 0.291 | 0.21143 | 0.97924 | -0.61426 | -0.31008 | 8.902 | -0.00045998 | 1.9857 | 15.8564 | 16.7222 | 17.2362 | 17.5458 | 17.489 | 16.4469 | 14.7886 | 16.811 | 17.1465 | 17.4406 | 17.4756 | 17.1983 | 16.3633 | 14.5626 | 16.9133 | 11.3892 | 11.3175 | 9.0776 | 8.5736 | 11.7613 | 9.5128 | 15.9602 | 15.5572 | 15.3878 | 14.307 | 14.3237 | 14.541 |  |  |  | 17.8583 | 80.5841 | 66.192 | 20.869 | 0.16071 | -0.20285 | 22.9475 |  |  | 10.7698 |  |  | 16.8759 | 16.0922 | 17.5017 | 16.342 | 15.6261 | 15.5516 | 68.7535 | 82.5762 | 55.1366 | 55.6903 | 27.3001 |  | 19.8994 | 28.1753 | 20.562 | 19.9106 | 18.9394 | 59.7674 |  | 32.4168 |  |  | 12.9144 | 13.9797 | 23.6503 | [6 empty] | 19.7306 |  |  | 18.1546 |  |  | 11.8083 | 18.1859 | 89.7369 | 8.0116 | 15.1212 | 62.3147 | 9.0696 | 13.5771 | 66.9783 | 13.6685 | 58.0705 | 8.9753 | 49.6797 | 10.0282 | 50.6601 | 9.0978 | 16.2308 | 60.2506 | 13.6674 | 16.5961 | 78.8583 | 9.6847 | 14.8702 | 68.4517 | 10.107 | 48.8987 | 13.0175 | 58.7204 | 10.7872 | 53.576 | 0.18565 | 20.1113 | 0.5479 | 0.056787 | -38.0531 | 3.1222 | 58.25 | 49.03 | -0.74379 | 0.031863 | -0.32898 | 0.34335 | -0.27399 | -0.82466 | 0.63005 | 0.21259 | 0.21048 | 0.38573 | -0.19884 | 0.16143 | 0.14208 | 0.323
42810.4431 | 261 | 18.4836 | 18.5805 | 18.5647 | 18.5574 | 17.8591 | 16.4682 | 14.5282 | 16.6427 | 17.1304 | 17.2227 | 17.2287 | 16.7523 | 15.7696 | 14.3913 | 14.8773 | 14.883 | 15.4479 | 13.3046 | 13.5312 | 14.317 |  |  |  | 16.5387 | 15.8912 | 16.513 | 72.6628 | 70.3683 | 80.0687 | 17.1353 | 16.2826 | 15.9902 | 16.8265 | 16.1041 | 16.1605 | 18.9262 | 72.3206 |  | 36.6278 | 60.2403 | 62.8336 | 28.361 |  | 6.4886 | 6.7046 | 6.112 | 6.4032 | 6.4456 | 7.7018 | 24.7454 | 5.3277 | 6.5635 | 5.0924 | 6.9911 | 8.0649 | 42.6256 | 47.2641 | 43.1337 | 14.9287 |  |  | -0.36382 | -0.14317 | -0.001436 | 0.051914 | -0.083948 | 0.07708 | 0.45594 | 0.11878 | -0.062451 | -0.25151 | -0.31127 | 8.9024 | -0.00045505 | 1.9925 | 15.8486 | 16.7158 | 17.2307 | 17.5461 | 17.4893 | 16.4433 | 14.7849 | 16.8047 | 17.1385 | 17.4352 | 17.4795 | 17.1984 | 16.3635 | 14.5623 | 16.2134 | 11.5507 | 10.8349 | 8.7831 | 8.3347 | 11.7762 | 9.512 | 15.9556 | 15.562 | 15.3884 | 14.3081 | 14.3197 | 14.5502 |  |  |  | 17.8961 | 80.5572 | 66.1977 | 21.2589 | -0.10166 | -0.16371 | 23.0621 |  |  | 10.7639 |  |  | 16.8833 | 16.0947 | 17.5161 | 16.3433 | 15.6248 | 15.5656 | 68.7975 | 82.5769 | 55.1943 | 55.764 | 27.094 |  | 19.9575 | 28.5876 | 20.6159 | 19.914 | 18.9707 | 60.7982 |  | 32.504 |  |  | 12.9141 | 13.9926 | 23.6746 | [6 empty] | 19.6378 |  |  | 18.1903 |  |  | 11.8242 | 18.1904 | 89.7909 | 7.9999 | 15.1164 | 62.4345 | 9.0579 | 13.6922 | 67.0851 | 13.6667 | 57.9897 | 8.9839 | 49.7871 | 10.0268 | 50.7051 | 9.1133 | 16.2783 | 60.2829 | 13.6752 | 16.6233 | 78.9034 | 9.6748 | 14.8985 | 68.4005 | 10.0979 | 48.912 | 13.0126 | 58.7392 | 10.7906 | 53.6374 | 0.36477 | 20.1106 | 0.54994 | 0.057511 | -38.0797 | 3.1222 | 57.95 | 50.2 | -0.79001 | -0.44111 | -0.044178 | 0.26563 | -0.33838 | 0.32425 | 0.7886 | 0.22026 | 0.20083 | 0.38668 | -0.11933 | 0.21496 | 0.15056 | 0.31343
42810.4431 | 262 | 18.4871 | 18.5914 | 18.5635 | 18.5549 | 17.8686 | 16.4794 | 14.5363 | 16.6482 | 17.1366 | 17.2336 | 17.2338 | 16.7549 | 15.7748 | 14.3892 | 14.8754 | 14.888 | 15.4497 | 13.3137 | 13.5352 | 14.3169 |  |  |  | 16.5382 | 15.8836 | 16.5246 | 72.6535 | 70.4588 | 79.655 | 17.1419 | 16.2837 | 16.0003 | 16.824 | 16.1038 | 16.1736 | 18.9719 | 71.7984 |  | 36.7334 | 60.3327 | 62.894 | 28.2228 |  | 6.4833 | 6.7084 | 6.1202 | 6.4075 | 6.4422 | 7.6941 | 24.8449 | 5.2955 | 6.5696 | 5.0316 | 6.9993 | 8.0594 | 42.6305 | 47.2735 | 43.1241 | 14.9107 |  |  | -0.18246 | -0.21282 | 0.012364 | -0.24379 | -0.23771 | -0.71409 | 0.39088 | 0.17988 | -0.62212 | -0.059966 | -0.37804 | 8.9024 | -0.00048626 | 1.9598 | 15.8545 | 16.7266 | 17.2472 | 17.5537 | 17.5028 | 16.4576 | 14.7918 | 16.8181 | 17.1535 | 17.4446 | 17.4859 | 17.2018 | 16.3739 | 14.5717 | 15.3784 | 11.1558 | 10.9838 | 8.4832 | 8.1124 | 11.786 | 9.5247 | 15.9535 | 15.5622 | 15.3905 | 14.3102 | 14.3173 | 14.5519 |  |  |  | 17.9444 | 80.4796 | 66.1836 | 21.7411 | 0.066502 | -0.17368 | 23.1804 |  |  | 10.7671 |  |  | 16.8835 | 16.0974 | 17.5371 | 16.3476 | 15.6276 | 15.5744 | 68.8415 | 82.5857 | 55.2866 | 55.858 | 27.1708 |  | 20.0187 | 29.8222 | 20.6721 | 19.9307 | 19.0023 | 61.3823 |  | 32.5929 |  |  | 12.9055 | 13.9815 | 23.7369 | [6 empty] | 19.5835 |  |  | 18.214 |  |  | 11.8129 | 18.2085 | 89.5957 | 7.9771 | 15.1132 | 62.514 | 9.061 | 13.8038 | 67.2116 | 13.6579 | 57.9806 | 8.9978 | 49.8597 | 10.0282 | 50.7733 | 9.132 | 16.3259 | 60.4173 | 13.6865 | 16.6566 | 78.943 | 9.6777 | 14.9041 | 68.5385 | 10.1167 | 48.9724 | 13.0452 | 58.6923 | 10.8215 | 53.762 | 0.34378 | 20.1096 | 0.55219 | 0.059139 | -38.0358 | 3.1221 | 81.56 | 48.73 | -0.55914 | -0.53782 | 0.12963 | -0.57563 | -0.56941 | -0.98691 | 0.73017 | 0.22017 | 0.16842 | 0.38728 | -0.025408 | 0.19989 | 0.15593 | 0.30165
42810.4431 | 263 | 18.479 | 18.5854 | 18.5654 | 18.5532 | 17.8685 | 16.4755 | 14.5281 | 16.6451 | 17.1359 | 17.2302 | 17.2344 | 16.7542 | 15.7724 | 14.3931 | 14.8647 | 14.8762 | 15.44 | 13.3073 | 13.53 | 14.3184 |  |  |  | 16.5416 | 15.8809 | 16.5274 | 72.6359 | 70.5016 | 79.1702 | 17.1357 | 16.2799 | 16.0085 | 16.8172 | 16.1066 | 16.1768 | 19.0176 | 71.1106 |  | 36.8223 | 60.4235 | 62.9887 | 28.7366 |  | 6.4899 | 6.709 | 6.1272 | 6.4095 | 6.4391 | 7.6702 | 24.4642 | 5.2687 | 6.5738 | 4.9472 | 6.9942 | 8.0525 | 42.6393 | 47.2697 | 43.1282 | 14.8985 |  |  | -0.1956 | 0.014543 | -0.13154 | 0.15442 | -0.83634 | -0.64378 | 0.24303 | -0.061932 | -0.30278 | -0.2576 | -0.0068635 | 8.9019 | -0.00046655 | 1.9009 | 15.8466 | 16.7159 | 17.2412 | 17.5456 | 17.4937 | 16.4447 | 14.7844 | 16.8069 | 17.143 | 17.439 | 17.4859 | 17.197 | 16.3661 | 14.5595 | 14.6649 | 10.767 | 10.6428 | 8.397 | 8.0199 | 11.78 | 9.5291 | 15.9564 | 15.5565 | 15.3992 | 14.3113 | 14.3283 | 14.5546 |  |  |  | 17.9921 | 80.4932 | 66.5016 | 21.7977 | -0.081599 | -0.2213 | 23.2601 |  |  | 10.7746 |  |  | 16.887 | 16.106 | 17.5623 | 16.35 | 15.6326 | 15.5819 | 68.8709 | 82.5931 | 55.3933 | 55.9392 | 27.9573 |  | 20.0868 | 31.5321 | 20.7484 | 20.0152 | 19.0405 | 61.2795 |  | 32.6907 |  |  | 12.8548 | 14.0033 | 23.8407 | [6 empty] | 19.6172 |  |  | 18.2162 |  |  | 11.8285 | 18.2274 | 89.4025 | 7.9725 | 15.0894 | 62.5707 | 9.0715 | 13.8131 | 67.2551 | 13.671 | 58.0326 | 9.0299 | 49.9055 | 10.0287 | 50.8744 | 9.1387 | 16.402 | 60.5217 | 13.6994 | 16.6563 | 78.9288 | 9.6925 | 14.9173 | 68.6278 | 10.1155 | 49.0672 | 13.0577 | 58.7126 | 10.8159 | 53.8243 | 0.338 | 20.106 | 0.55307 | 0.058343 | -38.0592 | 3.1222 | 73.44 | 48.7 | -0.57852 | 0.14059 | -0.42284 | 0.45813 | -1.068 | -0.93702 | 0.57572 | 0.20061 | 0.12348 | 0.38621 | 0.053169 | 0.2383 | 0.14318 | 0.30167
42810.4431 | 264 | 18.4835 | 18.5817 | 18.5713 | 18.5586 | 17.8709 | 16.4747 | 14.5342 | 16.6469 | 17.1387 | 17.2366 | 17.2378 | 16.7616 | 15.7735 | 14.3971 | 14.8679 | 14.8778 | 15.4409 | 13.3108 | 13.5337 | 14.3177 |  |  |  | 16.5422 | 15.8838 | 16.5458 | 72.6402 | 70.5424 | 78.6999 | 17.1391 | 16.2822 | 16.0178 | 16.8222 | 16.103 | 16.1916 | 19.0677 | 70.5814 |  | 36.906 | 60.4991 | 63.0675 | 28.3189 |  | 6.4901 | 6.7161 | 6.1344 | 6.4199 | 6.4208 | 7.6162 | 23.8911 | 5.2777 | 6.5809 | 4.9345 | 7.0032 | 8.0619 | 42.6196 | 47.2654 | 43.1277 | 14.8983 |  |  | -0.091121 | 0.013887 | 0.11816 | 0.15639 | -0.27911 | -0.3185 | 0.3554 | 0.046492 | -1.2053 | -0.25067 | -0.14893 | 8.9019 | -0.00050433 | 1.9233 | 15.8399 | 16.7113 | 17.2372 | 17.5431 | 17.4877 | 16.4375 | 14.7824 | 16.8081 | 17.1429 | 17.4385 | 17.4769 | 17.1955 | 16.3647 | 14.5627 | 14.3403 | 10.5133 | 10.1876 | 8.2673 | 8.0862 | 11.7803 | 9.5188 | 15.9478 | 15.5418 | 15.3852 | 14.3025 | 14.334 | 14.5586 |  |  |  | 18.0314 | 80.5476 | 66.605 | 21.0652 | -0.25057 | -0.3218 | 23.3293 |  |  | 10.7739 |  |  | 16.8861 | 16.1007 | 17.5804 | 16.345 | 15.6333 | 15.5917 | 68.8715 | 82.5546 | 55.4726 | 55.9868 | 28.9602 |  | 20.146 | 32.5061 | 20.8083 | 20.2665 | 19.0828 | 60.7712 |  | 32.7592 |  |  | 12.8157 | 14.0045 | 24.0029 | [6 empty] | 19.8289 |  |  | 18.23 |  |  | 11.8327 | 18.247 | 89.3927 | 7.9628 | 15.1388 | 62.5437 | 9.068 | 13.8173 | 67.2221 | 13.6777 | 58.1458 | 9.035 | 49.9538 | 10.0296 | 50.9406 | 9.1441 | 16.496 | 60.6185 | 13.7113 | 16.6507 | 78.9633 | 9.7053 | 14.9214 | 68.641 | 10.0995 | 49.1565 | 13.0654 | 58.6601 | 10.814 | 53.8786 | 0.35322 | 20.1053 | 0.55403 | 0.057692 | -38.1298 | 3.1222 | 79.62 | 50.09 | -0.3946 | 0.13739 | 0.40075 | 0.46105 | -0.61692 | -0.65902 | 0.69614 | 0.17473 | 0.098437 | 0.38064 | 0.089268 | 0.28767 | 0.15646 | 0.32333
42810.4431 | 265 | 18.4815 | 18.5822 | 18.5743 | 18.5651 | 17.8566 | 16.4654 | 14.5345 | 16.6375 | 17.1368 | 17.2327 | 17.2248 | 16.7515 | 15.772 | 14.3976 | 14.8713 | 14.887 | 15.4523 | 13.3152 | 13.5383 | 14.3348 |  |  |  | 16.5547 | 15.889 | 16.5708 | 72.686 | 70.5968 | 78.5563 | 17.1441 | 16.2776 | 16.0282 | 16.8166 | 16.1101 | 16.1914 | 19.112 | 70.1285 |  | 36.9774 | 60.548 | 63.1262 | 27.2775 |  | 6.4922 | 6.7256 | 6.1301 | 6.4032 | 6.4128 | 7.5865 | 23.4187 | 5.292 | 6.583 | 4.8659 | 7.0034 | 8.074 | 42.6052 | 47.2616 | 43.1508 | 14.8919 |  |  | -0.25409 | -0.089937 | 0.096476 | 0.10054 | -0.17923 | -0.43876 | 0.41126 | -0.06982 | 0.36197 | -0.0068862 | -0.17 | 8.9025 | -0.00045177 | 1.9686 | 15.8429 | 16.7099 | 17.2366 | 17.5445 | 17.4909 | 16.4367 | 14.7889 | 16.8031 | 17.1457 | 17.4411 | 17.477 | 17.1981 | 16.373 | 14.5566 | 13.4281 | 10.2373 | 9.8173 | 8.2961 | 8.2575 | 11.7729 | 9.5154 | 15.9528 | 15.548 | 15.39 | 14.3038 | 14.3318 | 14.563 |  |  |  | 18.0605 | 80.584 | 66.6529 | 20.6642 | -0.22322 | -0.11666 | 23.3566 |  |  | 10.7772 |  |  | 16.8866 | 16.0976 | 17.6009 | 16.3505 | 15.6346 | 15.6025 | 68.8936 | 82.5049 | 55.5259 | 55.9979 | 29.2568 |  | 20.2092 | 33.1105 | 20.8563 | 20.3713 | 19.1257 | 60.6176 |  | 32.8212 |  |  | 12.8352 | 14.0068 | 24.1139 | [6 empty] | 20.0441 |  |  | 18.2772 |  |  | 11.8419 | 18.2572 | 89.5041 | 7.9922 | 15.258 | 62.4836 | 9.0725 | 13.8224 | 67.2118 | 13.6891 | 58.2905 | 9.0606 | 49.9908 | 10.0346 | 51.0133 | 9.1624 | 16.5611 | 60.6832 | 13.717 | 16.665 | 78.9069 | 9.7201 | 14.9081 | 68.5717 | 10.0969 | 49.2776 | 13.0904 | 58.7878 | 10.8061 | 53.9206 | 0.40984 | 20.1034 | 0.55479 | 0.056838 | -38.1025 | 3.1221 | 71.44 | 48.86 | -0.65879 | -0.34964 | 0.36213 | 0.36967 | -0.49433 | -0.77344 | 0.74881 | 0.16861 | 0.083258 | 0.37916 | 0.18976 | 0.32843 | 0.18687 | 0.33544
42810.4431 | 266 | 18.4763 | 18.5826 | 18.5677 | 18.5593 | 17.8577 | 16.4668 | 14.5273 | 16.6318 | 17.1315 | 17.2279 | 17.2298 | 16.7512 | 15.7667 | 14.3867 | 14.879 | 14.8899 | 15.4536 | 13.3168 | 13.5428 | 14.3414 |  |  |  | 16.5516 | 15.8953 | 16.5827 | 72.7029 | 70.6686 | 78.245 | 17.1333 | 16.2767 | 16.0323 | 16.8207 | 16.1083 | 16.2044 | 19.1575 | 69.4639 |  | 37.0479 | 60.6368 | 63.2068 | 27.0245 |  | 6.4972 | 6.7399 | 6.1274 | 6.383 | 6.3994 | 7.5699 | 23.0891 | 5.1563 | 6.5789 | 4.8899 | 6.9906 | 8.0642 | 42.5855 | 47.2468 | 43.152 | 14.8791 |  |  | -0.31585 | -0.017653 | 0.043904 | 0.06571 | -0.079348 | -0.124 | 0.39614 | 0.13454 | -0.68108 | -1.8569 | -0.14973 | 8.9023 | -0.00045998 | 1.9882 | 15.8467 | 16.711 | 17.235 | 17.5433 | 17.4905 | 16.4406 | 14.7857 | 16.8078 | 17.1381 | 17.4417 | 17.4792 | 17.194 | 16.3718 | 14.5623 | 12.5674 | 10.007 | 9.5325 | 8.6007 | 8.5224 | 11.7657 | 9.5261 | 15.9369 | 15.5389 | 15.3805 | 14.3035 | 14.3161 | 14.5627 |  |  |  | 18.0847 | 80.5725 | 66.6326 | 20.5093 | 0.0077476 | 0.047828 | 23.3296 |  |  | 10.7791 |  |  | 16.8853 | 16.1029 | 17.6173 | 16.3523 | 15.6322 | 15.6131 | 68.9641 | 82.5104 | 55.5715 | 55.9929 | 28.9484 |  | 20.265 | 34.0227 | 20.9178 | 20.1939 | 19.1771 | 60.9873 |  | 32.9006 |  |  | 12.8387 | 14.0161 | 24.0574 | [6 empty] | 20.0117 |  |  | 18.3044 |  |  | 11.8441 | 18.2664 | 89.5869 | 8.0053 | 15.3264 | 62.4577 | 9.0848 | 13.8432 | 67.2069 | 13.7055 | 58.4114 | 9.08 | 50.0625 | 10.0405 | 51.0584 | 9.1762 | 16.6037 | 60.6816 | 13.7165 | 16.6948 | 78.8205 | 9.7286 | 14.9003 | 68.5919 | 10.0932 | 49.3761 | 13.1043 | 58.9788 | 10.8079 | 53.9872 | 0.33935 | 20.1041 | 0.55529 | 0.055984 | -38.0458 | 3.1221 | 59.66 | 49.68 | -0.73419 | -0.15491 | 0.24429 | 0.29887 | -0.32891 | -0.41116 | 0.7349 | 0.17905 | 0.059982 | 0.38581 | 0.28455 | 0.36132 | 0.19542 | 0.34055
42810.4431 | 267 | 18.4777 | 18.5809 | 18.5632 | 18.5571 | 17.8657 | 16.4719 | 14.5329 | 16.6375 | 17.138 | 17.2205 | 17.2285 | 16.7501 | 15.7724 | 14.3885 | 14.8673 | 14.8829 | 15.4386 | 13.3085 | 13.5381 | 14.3382 |  |  |  | 16.544 | 15.8819 | 16.5832 | 72.6504 | 70.682 | 77.6175 | 17.1352 | 16.277 | 16.0462 | 16.8176 | 16.1098 | 16.218 | 19.2226 | 68.8175 |  | 37.1442 | 60.6872 | 63.2979 | 28.5246 |  | 6.5084 | 6.7592 | 6.1414 | 6.3952 | 6.4112 | 7.5564 | 23.5874 | 5.0269 | 6.5883 | 4.8722 | 6.9984 | 8.0585 | 42.5465 | 47.2192 | 43.1509 | 14.8748 |  |  | -0.24949 | -0.024881 | -0.061232 | 0.21882 | -0.082632 | -0.3783 | 0.39088 | -0.14407 | -0.24635 | -0.064162 | -0.1392 | 8.9021 | -0.00051419 | 1.9721 | 15.8481 | 16.7124 | 17.2332 | 17.5426 | 17.4933 | 16.4486 | 14.7802 | 16.8109 | 17.142 | 17.444 | 17.4756 | 17.192 | 16.3706 | 14.5629 | 12.0905 | 9.8394 | 9.2554 | 8.4948 | 8.5171 | 11.7619 | 9.5226 | 15.9438 | 15.5413 | 15.3804 | 14.3039 | 14.3277 | 14.5729 |  |  |  | 18.1187 | 80.6465 | 66.9213 | 20.7453 | 0.043203 | -0.071303 | 23.3248 |  |  | 10.7765 |  |  | 16.8816 | 16.0984 | 17.6331 | 16.3429 | 15.6271 | 15.6148 | 69.0262 | 82.5104 | 55.6284 | 55.9935 | 28.5232 |  | 20.316 | 34.5913 | 20.9745 | 20.0683 | 19.2019 | 61.1391 |  | 32.9642 |  |  | 12.8107 | 14.0257 | 24.1438 | [6 empty] | 19.8233 |  |  | 18.2983 |  |  | 11.8529 | 18.2753 | 89.5279 | 8.0151 | 15.3448 | 62.5561 | 9.0902 | 13.8703 | 67.1992 | 13.7148 | 58.5163 | 9.1044 | 50.1372 | 10.0318 | 51.0956 | 9.1933 | 16.6607 | 60.6817 | 13.7257 | 16.7047 | 78.7789 | 9.7428 | 14.8976 | 68.6458 | 10.1014 | 49.4645 | 13.1128 | 59.1156 | 10.8101 | 54.099 | 0.3615 | 20.1023 | 0.55805 | 0.057446 | -38.0861 | 3.1222 | 50.22 | 50 | -0.65193 | -0.18391 | -0.28851 | 0.5454 | -0.33564 | -0.71814 | 0.72999 | 0.19257 | 0.046088 | 0.39013 | 0.3371 | 0.3917 | 0.15592 | 0.33513
42810.4431 | 268 | 18.4837 | 18.582 | 18.5622 | 18.5553 | 17.8592 | 16.4802 | 14.5346 | 16.6372 | 17.135 | 17.2218 | 17.229 | 16.7523 | 15.7761 | 14.3927 | 14.8639 | 14.8779 | 15.4404 | 13.3057 | 13.5348 | 14.3356 |  |  |  | 16.5434 | 15.8709 | 16.5955 | 72.5964 | 70.6956 | 77.3346 | 17.1439 | 16.2775 | 16.0574 | 16.825 | 16.1132 | 16.2316 | 19.3057 | 68.7551 |  | 37.2226 | 60.746 | 63.389 | 29.9713 |  | 6.5284 | 6.7738 | 6.1553 | 6.4043 | 6.4217 | 7.5649 | 23.8476 | 4.9135 | 6.5919 | 4.8093 | 7.0071 | 8.0595 | 42.5526 | 47.2005 | 43.1457 | 14.8553 |  |  | -0.34805 | -0.11951 | 0.012364 | 0.004598 | -0.20814 | -0.062884 | 0.44411 | -0.14013 | -0.6554 | -0.44914 | -0.28445 | 8.9027 | -0.00047476 | 1.9094 | 15.8372 | 16.7034 | 17.2301 | 17.5414 | 17.4944 | 16.4422 | 14.7765 | 16.8015 | 17.1395 | 17.4301 | 17.4771 | 17.183 | 16.3635 | 14.5598 | 12.0787 | 9.785 | 9.0022 | 8.2539 | 8.4124 | 11.7536 | 9.5224 | 15.9454 | 15.5416 | 15.3885 | 14.3046 | 14.3266 | 14.5734 |  |  |  | 18.1616 | 80.7797 | 67.0929 | 21.6499 | 0.039151 | -0.041567 | 23.3061 |  |  | 10.7736 |  |  | 16.8767 | 16.0963 | 17.654 | 16.3392 | 15.6256 | 15.6189 | 69.1036 | 82.5354 | 55.686 | 56.0195 | 28.5993 |  | 20.3794 | 33.6982 | 21.0294 | 19.8784 | 19.2291 | 61.0254 |  | 33.0397 |  |  | 12.8127 | 14.0454 | 24.3227 | [6 empty] | 19.6826 |  |  | 18.2833 |  |  | 11.8585 | 18.2913 | 89.3262 | 8.0404 | 15.3284 | 62.7171 | 9.095 | 13.8738 | 67.1786 | 13.7231 | 58.6344 | 9.1274 | 50.2051 | 10.0301 | 51.1672 | 9.2114 | 16.6913 | 60.6424 | 13.7352 | 16.6942 | 78.8647 | 9.7481 | 14.8941 | 68.6857 | 10.1015 | 49.5652 | 13.1249 | 59.2218 | 10.8181 | 54.1836 | 0.32972 | 20.1003 | 0.55994 | 0.057453 | -38.1012 | 3.1222 | 58.15 | 48.69 | -0.7697 | -0.40308 | 0.12965 | 0.079063 | -0.53269 | -0.2928 | 0.77812 | 0.19258 | 0.072742 | 0.39631 | 0.33745 | 0.41981 | 0.11852 | 0.31144
42810.4431 | 269 | 18.4791 | 18.5784 | 18.5633 | 18.5568 | 17.86 | 16.4745 | 14.5378 | 16.6389 | 17.1343 | 17.2257 | 17.2323 | 16.7549 | 15.7735 | 14.3928 | 14.8652 | 14.8765 | 15.4411 | 13.3076 | 13.5371 | 14.3411 |  |  |  | 16.5326 | 15.8766 | 16.6071 | 72.6334 | 70.7023 | 77.8649 | 17.134 | 16.273 | 16.0577 | 16.8186 | 16.103 | 16.2349 | 19.3629 | 68.5526 |  | 37.279 | 60.7892 | 63.4198 | 29.0882 |  | 6.5123 | 6.7664 | 6.1558 | 6.4056 | 6.4373 | 7.6152 | 23.6647 | 4.8016 | 6.5773 | 4.7636 | 6.999 | 8.0627 | 42.5403 | 47.1794 | 43.1483 | 14.8503 |  |  | -0.34148 | 0.12691 | 0.044564 | -0.16428 | -0.10563 | 0.35767 | 0.40534 | -0.052076 | -0.19011 | -0.39313 | -0.33551 | 8.902 | -0.00046655 | 1.9036 | 15.8437 | 16.7099 | 17.2364 | 17.5454 | 17.4883 | 16.4396 | 14.7854 | 16.8027 | 17.1474 | 17.4373 | 17.4802 | 17.1899 | 16.3685 | 14.5583 | 13.6748 | 10.17 | 9.0116 | 7.9894 | 8.335 | 11.794 | 9.5236 | 15.9436 | 15.5405 | 15.3765 | 14.3038 | 14.3297 | 14.5754 |  |  |  | 18.2161 | 80.9698 | 67.5974 | 22.1399 | 0.0083554 | -0.13397 | 23.2719 |  |  | 10.7738 |  |  | 16.8716 | 16.0937 | 17.6674 | 16.3343 | 15.6221 | 15.6266 | 69.2312 | 82.6271 | 55.7233 | 56.0439 | 29.1957 |  | 20.4473 | 32.6201 | 21.071 | 19.8602 | 19.2675 | 60.5869 |  | 33.125 |  |  | 12.8245 | 14.0559 | 24.4715 | [6 empty] | 19.7125 |  |  | 18.2872 |  |  | 11.8641 | 18.3194 | 89.2953 | 8.0779 | 15.3077 | 62.795 | 9.1085 | 13.879 | 67.1631 | 13.7343 | 58.7267 | 9.148 | 50.3053 | 10.0309 | 51.2658 | 9.2329 | 16.6911 | 60.6015 | 13.7421 | 16.6865 | 78.9322 | 9.7574 | 14.9104 | 68.747 | 10.0989 | 49.6752 | 13.1526 | 59.3019 | 10.8191 | 54.2716 | 0.16023 | 20.0975 | 0.56073 | 0.057554 | -38.1494 | 3.1222 | 62.78 | 49.88 | -0.76298 | 0.41537 | 0.24613 | -0.47258 | -0.37952 | 0.69836 | 0.74344 | 0.17829 | 0.10408 | 0.3981 | 0.16481 | 0.4189 | 0.14496 | 0.29964
42810.4432 | 270 | 18.4838 | 18.5844 | 18.5697 | 18.564 | 17.8682 | 16.4731 | 14.5434 | 16.6487 | 17.1367 | 17.2276 | 17.2388 | 16.7543 | 15.7857 | 14.3962 | 14.8635 | 14.8798 | 15.4436 | 13.3033 | 13.5448 | 14.3433 |  |  |  | 16.5334 | 15.8794 | 16.6229 | 72.7283 | 70.7111 | 78.4218 | 17.1324 | 16.2737 | 16.0689 | 16.8142 | 16.1065 | 16.2428 | 19.4006 | 68.5215 |  | 37.3444 | 60.8318 | 63.4487 | 28.3655 |  | 6.5356 | 6.7863 | 6.1762 | 6.431 | 6.4711 | 7.645 | 23.6218 | 4.7883 | 6.5938 | 4.7691 | 7.0122 | 8.0615 | 42.5382 | 47.1724 | 43.1567 | 14.8426 |  |  | -0.50576 | -0.099137 | -0.044148 | -0.12354 | 0.094788 | -0.076684 | 0.58802 | 0.08986 | -0.10468 | -0.23494 | -0.16801 | 8.9027 | -0.00044355 | 1.9555 | 15.847 | 16.7105 | 17.2361 | 17.5412 | 17.4919 | 16.4445 | 14.7797 | 16.8073 | 17.1412 | 17.4358 | 17.4745 | 17.196 | 16.3611 | 14.5607 | 14.7305 | 10.3186 | 9.548 | 7.7832 | 8.1059 | 11.8167 | 9.5312 | 15.9373 | 15.5417 | 15.3791 | 14.3052 | 14.3252 | 14.5792 |  |  |  | 18.2595 | 81.2258 | 68.232 | 22.1969 | 0.20994 | -0.053236 | 23.3178 |  |  | 10.7783 |  |  | 16.8753 | 16.1011 | 17.684 | 16.3419 | 15.62 | 15.6345 | 69.358 | 82.707 | 55.7696 | 56.0516 | 30.0261 |  | 20.5067 | 32.6744 | 21.1311 | 20.4448 | 19.3161 | 60.4768 |  | 33.222 |  |  | 12.8151 | 14.0345 | 24.6017 | [6 empty] | 19.8655 |  |  | 18.2976 |  |  | 11.8648 | 18.3323 | 89.3177 | 8.1102 | 15.3308 | 62.8556 | 9.1104 | 13.8916 | 67.1993 | 13.7461 | 58.7534 | 9.1657 | 50.4188 | 10.0389 | 51.3532 | 9.2444 | 16.6996 | 60.5859 | 13.7545 | 16.7459 | 78.943 | 9.761 | 14.9553 | 68.8313 | 10.1132 | 49.7371 | 13.1877 | 59.4281 | 10.8225 | 54.3371 | 0.26308 | 20.0977 | 0.56197 | 0.057612 | -38.1008 | 3.1221 | 58.44 | 49.52 | -0.92928 | -0.36713 | -0.24499 | -0.40982 | 0.35953 | -0.32338 | 0.89548 | 0.15721 | 0.10459 | 0.38349 | 0.050143 | 0.36018 | 0.1663 | 0.29951
42810.4432 | 271 | 18.4783 | 18.5828 | 18.5649 | 18.5635 | 17.8736 | 16.4729 | 14.5369 | 16.6398 | 17.134 | 17.2275 | 17.2335 | 16.7568 | 15.7776 | 14.3917 | 14.8658 | 14.8818 | 15.4548 | 13.3127 | 13.5473 | 14.3537 |  |  |  | 16.5521 | 15.8862 | 16.6465 | 72.7913 | 70.7132 | 78.5998 | 17.1391 | 16.2783 | 16.079 | 16.8208 | 16.1124 | 16.2581 | 19.447 | 68.3185 |  | 37.4295 | 60.867 | 63.4909 | 28.9239 |  | 6.5481 | 6.798 | 6.1827 | 6.4442 | 6.4835 | 7.6799 | 23.4225 | 4.8589 | 6.5967 | 4.7705 | 7.0236 | 8.064 | 42.5384 | 47.166 | 43.1568 | 14.836 |  |  | -0.54978 | 0.12823 | -0.1 | -0.060454 | 0.053392 | 0.19076 | 0.41257 | 0.14834 | -0.20607 | -0.053042 | -0.23537 | 8.9029 | -0.00049941 | 1.9883 | 15.8363 | 16.7141 | 17.2268 | 17.5426 | 17.4969 | 16.4482 | 14.7825 | 16.8006 | 17.1379 | 17.4369 | 17.4822 | 17.1944 | 16.3642 | 14.559 | 16.3471 | 11.1751 | 10.2839 | 8.0061 | 7.9185 | 11.8713 | 9.5394 | 15.9434 | 15.5503 | 15.3879 | 14.3119 | 14.3314 | 14.5969 |  |  |  | 18.3029 | 81.3098 | 68.2905 | 22.0251 | 0.16456 | -0.016725 | 23.3617 |  |  | 10.7842 |  |  | 16.8762 | 16.1088 | 17.7127 | 16.3485 | 15.6219 | 15.6453 | 69.4285 | 82.8283 | 55.8032 | 56.0714 | 30.8432 |  | 20.5615 | 34.0064 | 21.1992 | 20.8435 | 19.3613 | 60.067 |  | 33.3038 |  |  | 12.8259 | 14.0362 | 24.6918 | [6 empty] | 20.0074 |  |  | 18.3212 |  |  | 11.8667 | 18.3389 | 89.3277 | 8.1217 | 15.3607 | 62.8834 | 9.122 | 13.9077 | 67.2541 | 13.7584 | 58.8244 | 9.1729 | 50.5318 | 10.0516 | 51.4082 | 9.2629 | 16.7369 | 60.6027 | 13.7626 | 16.7836 | 78.9854 | 9.7691 | 14.9905 | 68.8689 | 10.1215 | 49.728 | 13.2183 | 59.5185 | 10.8363 | 54.3982 | 0.12595 | 20.0964 | 0.56248 | 0.056736 | -38.1375 | 3.1221 | 60.58 | 49.08 | -0.96913 | 0.41754 | -0.36874 | -0.28669 | 0.26985 | 0.51007 | 0.75013 | 0.13635 | 0.069876 | 0.37393 | -0.12312 | 0.27937 | 0.15234 | 0.30573
42810.4432 | 272 | 18.4827 | 18.582 | 18.5638 | 18.5584 | 17.8678 | 16.4771 | 14.5386 | 16.6461 | 17.1383 | 17.2292 | 17.2332 | 16.76 | 15.7793 | 14.3953 | 14.8606 | 14.8847 | 15.4538 | 13.3095 | 13.5515 | 14.362 |  |  |  | 16.5395 | 15.8825 | 16.6577 | 72.8295 | 70.7206 | 78.6734 | 17.1422 | 16.2822 | 16.0919 | 16.8231 | 16.1126 | 16.2689 | 19.5002 | 68.5114 |  | 37.5062 | 60.8926 | 63.5274 | 29.9002 |  | 6.5453 | 6.7853 | 6.1868 | 6.4466 | 6.4844 | 7.7207 | 23.1989 | 4.8665 | 6.5904 | 4.7359 | 7.0108 | 8.0686 | 42.5339 | 47.1658 | 43.1663 | 14.8337 |  |  | -0.40194 | -0.17865 | 0.1681 | 0.18531 | -0.027436 | 0.20719 | 0.39746 | 0.21668 | -0.54253 | -0.54586 | -0.22166 | 8.9033 | -0.00045998 | 1.983 | 15.8374 | 16.719 | 17.2289 | 17.5468 | 17.4926 | 16.4453 | 14.7871 | 16.8067 | 17.142 | 17.4374 | 17.4769 | 17.1963 | 16.3654 | 14.5589 | 17.2649 | 11.0914 | 11.2442 | 8.6098 | 8.2398 | 11.9005 | 9.5598 | 15.9328 | 15.5419 | 15.3851 | 14.3023 | 14.3331 | 14.5986 |  |  |  | 18.3444 | 81.3914 | 68.4686 | 22.264 | -0.11766 | -0.24746 | 23.3462 |  |  | 10.777 |  |  | 16.8723 | 16.1034 | 17.736 | 16.3437 | 15.6214 | 15.6533 | 69.4395 | 82.9981 | 55.8269 | 56.1168 | 31.4543 |  | 20.6253 | 35.0675 | 21.2692 | 20.9413 | 19.4078 | 60.0473 |  | 33.3741 |  |  | 12.8456 | 14.0483 | 24.7418 | [6 empty] | 20.1845 |  |  | 18.3349 |  |  | 11.8797 | 18.3661 | 89.348 | 8.1424 | 15.3572 | 62.8929 | 9.1248 | 13.9162 | 67.3032 | 13.7793 | 58.9536 | 9.1707 | 50.6183 | 10.0641 | 51.4568 | 9.2844 | 16.7692 | 60.634 | 13.7583 | 16.7945 | 79.0045 | 9.7681 | 15.005 | 68.8555 | 10.1215 | 49.7179 | 13.2266 | 59.5045 | 10.8403 | 54.4359 | 0.35206 | 20.0945 | 0.56211 | 0.05623 | -38.1284 | 3.1221 | 59.6 | 50.33 | -0.82872 | -0.49283 | 0.47806 | 0.50193 | -0.19346 | 0.53162 | 0.73632 | 0.12152 | 0.042749 | 0.37277 | -0.2217 | 0.17504 | 0.127 | 0.30048
42810.4432 | 273 | 18.4771 | 18.581 | 18.556 | 18.5589 | 17.8649 | 16.4727 | 14.5286 | 16.6384 | 17.1408 | 17.2254 | 17.2317 | 16.7565 | 15.7766 | 14.396 | 14.8689 | 14.8874 | 15.4499 | 13.319 | 13.5574 | 14.3719 |  |  |  | 16.5505 | 15.8865 | 16.6724 | 72.8535 | 70.7566 | 78.3836 | 17.1367 | 16.2843 | 16.0929 | 16.8192 | 16.1131 | 16.285 | 19.5553 | 68.6223 |  | 37.5836 | 60.9326 | 63.5644 | 29.7276 |  | 6.5513 | 6.7974 | 6.1825 | 6.451 | 6.4869 | 7.7702 | 23.0216 | 4.8422 | 6.591 | 4.6921 | 7.0079 | 8.0596 | 42.5263 | 47.1653 | 43.1562 | 14.8216 |  |  | -0.41245 | -0.13988 | -0.02312 | 0.017742 | 0.11056 | 0.24333 | 0.47565 | 0.37176 | -0.29519 | -0.33648 | -0.13979 | 8.9035 | -0.00050105 | 1.9084 | 15.8366 | 16.7147 | 17.2333 | 17.546 | 17.4907 | 16.4411 | 14.785 | 16.8087 | 17.1448 | 17.4396 | 17.4782 | 17.1933 | 16.3637 | 14.5552 | 16.9092 | 10.6132 | 10.7557 | 8.7994 | 8.6227 | 11.9115 | 9.5723 | 15.9387 | 15.5427 | 15.3822 | 14.2992 | 14.3348 | 14.5929 |  |  |  | 18.388 | 81.4271 | 68.5227 | 22.8334 | 0.015041 | 0.050274 | 23.3739 |  |  | 10.7748 |  |  | 16.8697 | 16.1046 | 17.7527 | 16.3424 | 15.6224 | 15.6612 | 69.4351 | 83.2175 | 55.8543 | 56.1853 | 31.859 |  | 20.6756 | 34.6251 | 21.3207 | 21.0847 | 19.4624 | 59.8044 |  | 33.4567 |  |  | 12.8437 | 14.0607 | 24.7444 | [6 empty] | 20.4196 |  |  | 18.3506 |  |  | 11.8905 | 18.3769 | 89.3552 | 8.1789 | 15.3145 | 62.9376 | 9.1339 | 13.9236 | 67.3363 | 13.8063 | 59.0378 | 9.1853 | 50.6689 | 10.0886 | 51.5257 | 9.3024 | 16.792 | 60.702 | 13.7513 | 16.7856 | 79.0461 | 9.7677 | 15.009 | 68.8826 | 10.1233 | 49.7069 | 13.2383 | 59.5381 | 10.8435 | 54.4805 | 0.23515 | 20.0954 | 0.56402 | 0.056888 | -38.1903 | 3.1221 | 73.85 | 49.26 | -0.83914 | -0.43609 | -0.1773 | 0.15531 | 0.38838 | 0.57618 | 0.80557 | 0.11196 | 0.056771 | 0.37061 | -0.18091 | 0.23077 | 0.13364 | 0.28612
42810.4432 | 274 | 18.4898 | 18.5875 | 18.5712 | 18.5618 | 17.8738 | 16.4818 | 14.5317 | 16.6541 | 17.144 | 17.2377 | 17.2403 | 16.7616 | 15.7837 | 14.4025 | 14.8645 | 14.8778 | 15.441 | 13.307 | 13.5496 | 14.3692 |  |  |  | 16.548 | 15.8812 | 16.6843 | 72.8113 | 70.782 | 78.1344 | 17.1338 | 16.2814 | 16.1062 | 16.818 | 16.1105 | 16.2877 | 19.5941 | 68.5052 |  | 37.6485 | 60.9545 | 63.5808 | 29.7124 |  | 6.5644 | 6.8135 | 6.1932 | 6.4568 | 6.5085 | 7.8251 | 23.2046 | 4.8106 | 6.5929 | 4.6392 | 7.0015 | 8.0697 | 42.5184 | 47.1842 | 43.1705 | 14.8245 |  |  | -0.30928 | 0.015859 | 0.020248 | -0.015114 | -0.11877 | 0.11059 | 0.50325 | 0.43616 | 0.50364 | -0.70762 | -0.078992 | 8.9036 | -0.00045669 | 1.8826 | 15.8336 | 16.7163 | 17.237 | 17.5444 | 17.492 | 16.4406 | 14.7867 | 16.8064 | 17.1484 | 17.4411 | 17.4799 | 17.1921 | 16.3676 | 14.5567 | 15.7349 | 10.2852 | 9.9478 | 8.7304 | 8.6991 | 11.9101 | 9.5773 | 15.9405 | 15.545 | 15.3902 | 14.3057 | 14.3329 | 14.6055 |  |  |  | 18.4427 | 81.3938 | 68.771 | 23.2618 | -0.078965 | -0.17425 | 23.3917 |  |  | 10.7909 |  |  | 16.8857 | 16.111 | 17.7785 | 16.3446 | 15.6244 | 15.6717 | 69.4951 | 83.4691 | 55.8904 | 56.2449 | 31.9271 |  | 20.729 | 33.2887 | 21.352 | 20.9543 | 19.498 | 59.5335 |  | 33.5219 |  |  | 12.8225 | 14.0683 | 24.853 | [6 empty] | 20.4447 |  |  | 18.371 |  |  | 11.8887 | 18.3859 | 89.3136 | 8.2024 | 15.2639 | 63.0036 | 9.141 | 13.9568 | 67.3298 | 13.82 | 59.0915 | 9.1987 | 50.7342 | 10.0968 | 51.5901 | 9.3328 | 16.79 | 60.7325 | 13.7693 | 16.7899 | 79.0643 | 9.7929 | 15.0344 | 68.8709 | 10.1557 | 49.6814 | 13.2711 | 59.6609 | 10.8523 | 54.5915 | 0.26558 | 20.0908 | 0.56564 | 0.058886 | -38.1543 | 3.1221 | 54.24 | 49.08 | -0.7264 | 0.14684 | 0.16592 | -0.14335 | -0.40259 | 0.38847 | 0.82869 | 0.11186 | 0.094942 | 0.37543 | -0.050588 | 0.32111 | 0.13536 | 0.27605
42810.4432 | 275 | 18.4871 | 18.579 | 18.5617 | 18.5631 | 17.8665 | 16.4749 | 14.5275 | 16.6484 | 17.1434 | 17.2327 | 17.237 | 16.7562 | 15.7746 | 14.3971 | 14.8673 | 14.8838 | 15.451 | 13.3133 | 13.5591 | 14.377 |  |  |  | 16.5561 | 15.8899 | 16.7043 | 72.8605 | 70.7654 | 78.5872 | 17.1351 | 16.2723 | 16.1125 | 16.8154 | 16.1016 | 16.3001 | 19.6451 | 68.8805 |  | 37.7228 | 60.9927 | 63.5895 | 30.0206 |  | 6.5845 | 6.8353 | 6.2022 | 6.4708 | 6.5485 | 7.8368 | 23.3202 | 4.8174 | 6.5969 | 4.6204 | 7.0171 | 8.0688 | 42.4878 | 47.1862 | 43.1826 | 14.8134 |  |  | -0.34805 | -0.013713 | 0.053104 | -0.14391 | 0.048132 | -0.1792 | 0.4612 | 0.17332 | 0.15161 | -0.73531 | -0.26875 | 8.9039 | -0.00047476 | 1.9348 | 15.8448 | 16.7127 | 17.238 | 17.55 | 17.4982 | 16.4436 | 14.7909 | 16.8118 | 17.1549 | 17.4417 | 17.4759 | 17.1952 | 16.3727 | 14.5597 | 14.6386 | 10.0552 | 9.3607 | 8.4979 | 8.5996 | 11.8935 | 9.5676 | 15.9371 | 15.539 | 15.3837 | 14.2957 | 14.3316 | 14.6063 |  |  |  | 18.4866 | 81.3734 | 68.8038 | 23.5851 | 0.061234 | -0.191 | 23.2726 |  |  | 10.7911 |  |  | 16.8857 | 16.1106 | 17.7988 | 16.3462 | 15.6288 | 15.6786 | 69.5759 | 83.6374 | 55.9091 | 56.265 | 31.6722 |  | 20.7948 | 32.1611 | 21.3918 | 20.9048 | 19.5489 | 59.6932 |  | 33.6197 |  |  | 12.8039 | 14.0612 | 24.8371 | [6 empty] | 20.4398 |  |  | 18.3783 |  |  | 11.8851 | 18.4116 | 89.309 | 8.2434 | 15.3063 | 63.0693 | 9.1357 | 14.0342 | 67.3271 | 13.8225 | 59.1357 | 9.2171 | 50.8404 | 10.103 | 51.6588 | 9.3361 | 16.7959 | 60.8109 | 13.7865 | 16.7985 | 79.0854 | 9.7958 | 15.0551 | 68.9569 | 10.1625 | 49.6615 | 13.2749 | 59.9389 | 10.8529 | 54.6254 | 0.41812 | 20.0895 | 0.56808 | 0.059197 | -38.154 | 3.1221 | 61.16 | 50.37 | -0.77108 | -0.13655 | 0.26872 | -0.44236 | 0.25629 | -0.49451 | 0.79333 | 0.12115 | 0.1276 | 0.3785 | 0.069288 | 0.38523 | 0.12851 | 0.26853
42810.4432 | 276 | 18.4797 | 18.5766 | 18.5683 | 18.5647 | 17.868 | 16.4709 | 14.5303 | 16.6485 | 17.1469 | 17.2377 | 17.2348 | 16.761 | 15.7789 | 14.4054 | 14.8724 | 14.8887 | 15.4473 | 13.3137 | 13.5548 | 14.3736 |  |  |  | 16.5511 | 15.891 | 16.7124 | 72.9158 | 70.7516 | 78.6861 | 17.14 | 16.2732 | 16.1229 | 16.8164 | 16.1077 | 16.3097 | 19.7009 | 69.4855 |  | 37.8144 | 61.0254 | 63.6102 | 30.0424 |  | 6.5991 | 6.8335 | 6.2133 | 6.4782 | 6.5792 | 7.863 | 23.113 | 4.8493 | 6.5873 | 4.6426 | 7.0239 | 8.0696 | 42.4649 | 47.1837 | 43.1966 | 14.8022 |  |  | -0.39405 | -0.11951 | 0.13722 | 0.009198 | 0.03762 | 0.16448 | 0.36263 | -0.004764 | -0.39891 | -0.4139 | -0.14377 | 8.9033 | -0.00047476 | 1.9756 | 15.8424 | 16.7086 | 17.2332 | 17.5447 | 17.4888 | 16.4362 | 14.7789 | 16.8025 | 17.1434 | 17.4368 | 17.477 | 17.1852 | 16.3559 | 14.5568 | 15.1164 | 10.0424 | 9.1014 | 8.292 | 8.5509 | 11.9245 | 9.5687 | 15.9364 | 15.5348 | 15.3869 | 14.2956 | 14.3404 | 14.6137 |  |  |  | 18.5269 | 81.403 | 68.6704 | 23.6613 | 0.22129 | -0.082407 | 23.2177 |  |  | 10.7829 |  |  | 16.8771 | 16.1038 | 17.8065 | 16.3432 | 15.6312 | 15.6858 | 69.5772 | 83.7375 | 55.9162 | 56.2766 | 31.3978 |  | 20.8569 | 32.3657 | 21.4458 | 21.0562 | 19.6106 | 60.275 |  | 33.7205 |  |  | 12.8268 | 14.0746 | 24.8422 | [6 empty] | 20.6157 |  |  | 18.346 |  |  | 11.906 | 18.4382 | 89.3003 | 8.2627 | 15.2795 | 63.1569 | 9.1375 | 14.0379 | 67.4111 | 13.8134 | 59.3637 | 9.2231 | 50.9395 | 10.1127 | 51.6899 | 9.3408 | 16.8159 | 60.841 | 13.7956 | 16.8123 | 79.1772 | 9.8079 | 15.0749 | 69.0749 | 10.1711 | 49.7017 | 13.2829 | 60.1119 | 10.8682 | 54.6587 | 0.29428 | 20.0905 | 0.56937 | 0.059812 | -38.1544 | 3.1222 | 63.59 | 48.75 | -0.82056 | -0.40312 | 0.43195 | 0.11184 | 0.22659 | 0.47379 | 0.70349 | 0.13085 | 0.12373 | 0.37636 | 0.019815 | 0.41417 | 0.12977 | 0.26776
42810.4432 | 277 | 18.4852 | 18.5812 | 18.5692 | 18.5632 | 17.875 | 16.476 | 14.5307 | 16.6524 | 17.1468 | 17.2314 | 17.2389 | 16.7574 | 15.781 | 14.4114 | 14.8642 | 14.8806 | 15.4425 | 13.3115 | 13.5568 | 14.3806 |  |  |  | 16.5478 | 15.8904 | 16.7277 | 72.9537 | 70.7762 | 78.2543 | 17.1397 | 16.2761 | 16.138 | 16.8235 | 16.1113 | 16.3199 | 19.7535 | 69.7443 |  | 37.9149 | 61.0542 | 63.6334 | 30.466 |  | 6.6033 | 6.8415 | 6.2197 | 6.488 | 6.6031 | 7.9124 | 23.4501 | 4.8637 | 6.596 | 4.6608 | 7.0256 | 8.0714 | 42.4388 | 47.2018 | 43.2028 | 14.8064 |  |  | -0.41836 | -0.038681 | 0.093848 | -0.02037 | -0.13389 | 0.50683 | 0.74836 | 0.17988 | -0.24323 | -0.95162 | -0.39711 | 8.9026 | -0.00043041 | 1.9615 | 15.8495 | 16.715 | 17.2392 | 17.5521 | 17.4967 | 16.4459 | 14.7864 | 16.8104 | 17.1583 | 17.4465 | 17.4821 | 17.1912 | 16.3648 | 14.5572 | 16.9236 | 11.0259 | 9.9802 | 8.2807 | 8.5055 | 11.9757 | 9.5739 | 15.9423 | 15.5445 | 15.3858 | 14.3007 | 14.3408 | 14.6134 |  |  |  | 18.5795 | 81.4971 | 68.403 | 23.8475 | 0.20204 | -0.12532 | 23.3288 |  |  | 10.7848 |  |  | 16.8699 | 16.1019 | 17.8261 | 16.3409 | 15.6261 | 15.6904 | 69.5404 | 83.8188 | 55.9473 | 56.3106 | 30.9879 |  | 20.9079 | 32.7066 | 21.507 | 21.1385 | 19.6459 | 60.7763 |  | 33.8015 |  |  | 12.8552 | 14.0862 | 24.8979 | [6 empty] | 20.7298 |  |  | 18.339 |  |  | 11.9201 | 18.5269 | 89.3875 | 8.2771 | 15.2467 | 63.2239 | 9.1434 | 14.0335 | 67.6124 | 13.8172 | 59.4739 | 9.2487 | 51.0458 | 10.1036 | 51.7347 | 9.3609 | 16.8585 | 60.8761 | 13.804 | 16.8392 | 79.3121 | 9.8146 | 15.107 | 69.1322 | 10.1672 | 49.7246 | 13.2782 | 60.293 | 10.8743 | 54.6825 | 0.27329 | 20.0879 | 0.57049 | 0.059704 | -38.1189 | 3.1222 | 60.28 | 49.42 | -0.84498 | -0.22934 | 0.35723 | -0.16643 | -0.4275 | 0.83176 | 1.0107 | 0.14395 | 0.11632 | 0.37526 | -0.17503 | 0.31713 | 0.11976 | 0.26435
42810.4433 | 278 | 18.4893 | 18.5879 | 18.5733 | 18.5668 | 17.8732 | 16.4712 | 14.5376 | 16.6505 | 17.1393 | 17.2272 | 17.2445 | 16.7592 | 15.7784 | 14.4098 | 14.8623 | 14.8799 | 15.441 | 13.3126 | 13.5601 | 14.3912 |  |  |  | 16.5426 | 15.8879 | 16.7469 | 72.9867 | 70.9427 | 78.787 | 17.1339 | 16.2815 | 16.1358 | 16.8262 | 16.1128 | 16.324 | 19.7868 | 69.6796 |  | 37.9987 | 61.1098 | 63.6486 | 30.66 |  | 6.5874 | 6.8278 | 6.2178 | 6.4886 | 6.6499 | 7.9664 | 23.7077 | 4.8085 | 6.5809 | 4.6843 | 7.0141 | 8.0604 | 42.4051 | 47.2174 | 43.1919 | 14.8017 |  |  | -0.20612 | -0.054453 | 0.049164 | -0.049942 | 0.06982 | 0.1395 | 0.6373 | 0.15754 | -0.30667 | -0.44558 | -0.16404 | 8.9036 | -0.00048134 | 1.9297 | 15.8459 | 16.7101 | 17.239 | 17.5485 | 17.4904 | 16.4437 | 14.7921 | 16.8151 | 17.1423 | 17.4402 | 17.4824 | 17.1856 | 16.3634 | 14.5551 | 18.6999 | 11.7855 | 11.5633 | 8.4774 | 8.4345 | 12.0294 | 9.5947 | 15.9361 | 15.5383 | 15.3824 | 14.3018 | 14.3449 | 14.6173 |  |  |  | 18.6244 | 81.54 | 68.2362 | 24.3244 | 0.20001 | -0.22262 | 23.3972 |  |  | 10.7856 |  |  | 16.866 | 16.1047 | 17.8522 | 16.3398 | 15.6231 | 15.7013 | 69.5325 | 83.8908 | 56.029 | 56.3573 | 30.5271 |  | 20.9616 | 31.3891 | 21.5668 | 21.0579 | 19.6844 | 60.9479 |  | 33.8932 |  |  | 12.8788 | 14.0975 | 24.7657 | [6 empty] | 20.8035 |  |  | 18.3119 |  |  | 11.9316 | 18.5821 | 89.3842 | 8.252 | 15.2424 | 63.2875 | 9.1505 | 14.04 | 67.7606 | 13.818 | 59.3762 | 9.2751 | 51.1041 | 10.1019 | 51.7819 | 9.3747 | 16.8885 | 60.8949 | 13.8131 | 16.9326 | 79.4413 | 9.8281 | 15.1155 | 69.1083 | 10.1636 | 49.7317 | 13.2828 | 60.3316 | 10.8739 | 54.7556 | 0.39193 | 20.0854 | 0.57161 | 0.058719 | -38.17 | 3.1221 | 63.63 | 49.97 | -0.59355 | -0.27211 | 0.25855 | -0.26059 | 0.30875 | 0.43642 | 0.93279 | 0.15855 | 0.15492 | 0.37878 | -0.36614 | 0.14364 | 0.11549 | 0.2526
42810.4433 | 279 | 18.4925 | 18.5867 | 18.5751 | 18.5692 | 17.8735 | 16.4791 | 14.532 | 16.6495 | 17.1444 | 17.2412 | 17.2433 | 16.7705 | 15.7747 | 14.4093 | 14.8677 | 14.8791 | 15.4497 | 13.3126 | 13.5607 | 14.3984 |  |  |  | 16.5478 | 15.8923 | 16.7527 | 73.0112 | 71.1193 | 78.9727 | 17.1352 | 16.2752 | 16.1372 | 16.8215 | 16.1071 | 16.3391 | 19.8203 | 69.6102 |  | 38.1037 | 61.1748 | 63.6747 | 31.5157 |  | 6.5835 | 6.8272 | 6.2364 | 6.5383 | 6.7405 | 8.0244 | 23.8943 | 4.8323 | 6.5785 | 4.6862 | 7.012 | 8.0661 | 42.402 | 47.2333 | 43.197 | 14.8104 |  |  | -0.25146 | 0.1256 | 0.1221 | 0.02037 | -0.029408 | 0.088908 | 0.59459 | 0.045176 | -0.51879 | -0.62391 | -0.093298 | 8.9034 | -0.00046491 | 1.945 | 15.8392 | 16.7109 | 17.2288 | 17.5414 | 17.4871 | 16.4419 | 14.7876 | 16.807 | 17.141 | 17.4338 | 17.4767 | 17.1935 | 16.3628 | 14.5584 | 20.4 | 12.471 | 12.6969 | 9.187 | 8.5824 | 12.0971 | 9.6306 | 15.9271 | 15.5358 | 15.3785 | 14.2972 | 14.3378 | 14.6225 |  |  |  | 18.6758 | 81.6531 | 68.4675 | 24.7961 | 0.14005 | -0.14564 | 23.3782 |  |  | 10.79 |  |  | 16.8756 | 16.1109 | 17.8756 | 16.3458 | 15.6286 | 15.7138 | 69.5058 | 83.9026 | 56.1315 | 56.445 | 29.9771 |  | 21.0158 | 29.5947 | 21.6218 | 20.9648 | 19.7187 | 60.9791 |  | 33.975 |  |  | 12.8931 | 14.1024 | 24.6917 | [6 empty] | 20.7396 |  |  | 18.3182 |  |  | 11.9406 | 18.5934 | 89.4608 | 8.2279 | 15.3392 | 63.3764 | 9.1608 | 14.042 | 67.8179 | 13.8316 | 59.376 | 9.2859 | 51.1496 | 10.1129 | 51.8172 | 9.3929 | 16.896 | 60.9949 | 13.8284 | 17.0937 | 79.5314 | 9.8303 | 15.1434 | 69.1806 | 10.168 | 49.7729 | 13.2899 | 60.1633 | 10.8774 | 54.8691 | 0.33222 | 20.0832 | 0.57193 | 0.056708 | -38.1127 | 3.1222 | 73.36 | 49.03 | -0.65576 | 0.41326 | 0.40747 | 0.16643 | -0.2004 | 0.34844 | 0.90108 | 0.17565 | 0.20661 | 0.38252 | -0.54716 | 0.021863 | 0.09284 | 0.24122
42810.4433 | 280 | 18.4803 | 18.5769 | 18.5621 | 18.5609 | 17.8641 | 16.4698 | 14.5247 | 16.6418 | 17.1296 | 17.2291 | 17.2339 | 16.7542 | 15.7747 | 14.3976 | 14.8701 | 14.88 | 15.4463 | 13.3097 | 13.5595 | 14.4028 |  |  |  | 16.5518 | 15.8964 | 16.7681 | 73.0889 | 71.2501 | 79.2227 | 17.1472 | 16.2791 | 16.1652 | 16.8307 | 16.1196 | 16.3585 | 19.8816 | 69.6857 |  | 38.2039 | 61.256 | 63.7578 | 34.0039 |  | 6.5763 | 6.8218 | 6.2436 | 6.5743 | 6.7748 | 8.0696 | 24.0271 | 4.8376 | 6.5828 | 4.7084 | 7.0171 | 8.066 | 42.4183 | 47.2352 | 43.186 | 14.8278 |  |  | -0.1818 | -0.051169 | -0.14074 | -0.13799 | 0.050764 | 0.2729 | 0.56502 | 0.60767 | -0.6696 | -1.1837 | -0.082966 | 8.9022 | -0.00045834 | 1.9636 | 15.8432 | 16.712 | 17.2393 | 17.5427 | 17.488 | 16.4396 | 14.7821 | 16.8074 | 17.1441 | 17.4349 | 17.4757 | 17.1929 | 16.3646 | 14.5575 | 20.5807 | 12.3738 | 13.7238 | 9.8619 | 9.1094 | 12.1287 | 9.658 | 15.9297 | 15.5377 | 15.3771 | 14.3017 | 14.338 | 14.6284 |  |  |  | 18.7221 | 81.7284 | 68.7259 | 25.141 | 0.004506 | -0.24181 | 23.3718 |  |  | 10.7936 |  |  | 16.8837 | 16.1131 | 17.8949 | 16.34 | 15.6323 | 15.7278 | 69.5225 | 83.9113 | 56.2358 | 56.5459 | 29.9346 |  | 21.0739 | 30.8165 | 21.6985 | 20.838 | 19.7529 | 60.9248 |  | 34.0676 |  |  | 12.8978 | 14.1071 | 24.7064 | [6 empty] | 20.6 |  |  | 18.3271 |  |  | 11.9532 | 18.6141 | 89.6416 | 8.2066 | 15.4896 | 63.4645 | 9.1709 | 14.09 | 67.8102 | 13.8489 | 59.4624 | 9.294 | 51.2011 | 10.1209 | 51.8925 | 9.3998 | 16.8737 | 61.0739 | 13.8318 | 17.2041 | 79.6087 | 9.842 | 15.1711 | 69.2257 | 10.1681 | 49.8394 | 13.2897 | 60.1586 | 10.8732 | 54.9894 | 0.15696 | 20.0825 | 0.57182 | 0.055861 | -38.0635 | 3.1221 | 58.31 | 49.58 | -0.55778 | -0.26377 | -0.43746 | -0.43317 | 0.26331 | 0.61051 | 0.87846 | 0.17878 | 0.17525 | 0.38719 | -0.56357 | -0.089056 | 0.025777 | 0.23318
42810.4433 | 281 | 18.4902 | 18.581 | 18.569 | 18.5628 | 17.8731 | 16.4732 | 14.53 | 16.6484 | 17.1456 | 17.2343 | 17.2368 | 16.7629 | 15.7801 | 14.4137 | 14.8734 | 14.8779 | 15.4397 | 13.3114 | 13.5632 | 14.3976 |  |  |  | 16.5458 | 15.8869 | 16.7808 | 73.2023 | 71.3606 | 79.6079 | 17.1427 | 16.2811 | 16.1739 | 16.8251 | 16.1159 | 16.364 | 19.9321 | 70.064 |  | 38.29 | 61.3306 | 63.8186 | 35.0431 |  | 6.587 | 6.8303 | 6.248 | 6.5992 | 6.8154 | 8.1151 | 23.8405 | 4.6961 | 6.5862 | 4.6931 | 7.0134 | 8.0716 | 42.434 | 47.2157 | 43.1793 | 14.854 |  |  | -0.19823 | -0.066281 | 0.021564 | -0.13931 | 0.2111 | -0.23242 | 0.7109 | 0.51962 | -0.61181 | 0.10787 | -0.16145 | 8.9029 | -0.00052898 | 1.9466 | 15.8318 | 16.7093 | 17.2301 | 17.5473 | 17.489 | 16.4362 | 14.7836 | 16.802 | 17.1372 | 17.4302 | 17.4686 | 17.1847 | 16.3595 | 14.5516 | 19.2819 | 11.6566 | 13.2432 | 10.298 | 9.1796 | 12.1587 | 9.6743 | 15.9274 | 15.5377 | 15.3761 | 14.299 | 14.337 | 14.6368 |  |  |  | 18.768 | 81.7524 | 68.9472 | 25.5009 | -0.044321 | -0.18422 | 23.3752 |  |  | 10.7801 |  |  | 16.8792 | 16.1069 | 17.9098 | 16.3414 | 15.6245 | 15.7286 | 69.5716 | 83.9675 | 56.3327 | 56.647 | 29.9224 |  | 21.1246 | 32.9782 | 21.7657 | 20.8214 | 19.7909 | 60.6404 |  | 34.1525 |  |  | 12.9136 | 14.1269 | 24.7587 | [6 empty] | 20.5313 |  |  | 18.3906 |  |  | 11.9586 | 18.6273 | 89.9758 | 8.2016 | 15.5501 | 63.6004 | 9.1818 | 14.2809 | 67.8081 | 13.858 | 59.4424 | 9.3017 | 51.2489 | 10.121 | 51.9478 | 9.4123 | 16.8471 | 61.1258 | 13.8247 | 17.1994 | 79.7296 | 9.8497 | 15.2088 | 69.2398 | 10.1529 | 49.881 | 13.288 | 60.3748 | 10.8722 | 55.0271 | 0.30064 | 20.0826 | 0.57398 | 0.057779 | -38.0495 | 3.1222 | 49.7 | 49.36 | -0.58276 | -0.30021 | 0.17124 | -0.43523 | 0.53699 | -0.56346 | 0.98544 | 0.18082 | 0.11746 | 0.38892 | -0.41577 | -0.033754 | -0.0014 | 0.22472
42810.4433 | 282 | 18.484 | 18.5747 | 18.5592 | 18.5626 | 17.8735 | 16.4751 | 14.5205 | 16.6448 | 17.1372 | 17.2336 | 17.2467 | 16.752 | 15.7754 | 14.3994 | 14.8713 | 14.8725 | 15.4386 | 13.3116 | 13.5542 | 14.4052 |  |  |  | 16.5421 | 15.8872 | 16.792 | 73.2754 | 71.4584 | 79.7989 | 17.1373 | 16.279 | 16.1774 | 16.8271 | 16.1118 | 16.3683 | 19.9831 | 70.8356 |  | 38.3875 | 61.3929 | 63.855 | 34.7297 |  | 6.5807 | 6.8251 | 6.2399 | 6.601 | 6.8293 | 8.1101 | 23.8479 | 4.6462 | 6.5779 | 4.7189 | 7.0211 | 8.07 | 42.452 | 47.1837 | 43.1767 | 14.8735 |  |  | -0.26263 | 0.051343 | 0.00448 | -0.28782 | 0.02842 | 0.23676 | 0.20229 | 0.40725 | -0.5869 | -0.48712 | -0.19026 | 8.9029 | -0.00047312 | 1.9155 | 15.832 | 16.7102 | 17.2305 | 17.5519 | 17.4878 | 16.4413 | 14.7854 | 16.81 | 17.1451 | 17.4337 | 17.4735 | 17.186 | 16.3584 | 14.5586 | 18.3486 | 11.3557 | 12.6153 | 10.1124 | 9.3168 | 12.1765 | 9.6809 | 15.9221 | 15.526 | 15.3725 | 14.2965 | 14.3411 | 14.6327 |  |  |  | 18.8142 | 81.782 | 69.2205 | 25.5424 | -0.20579 | -0.20718 | 23.3925 |  |  | 10.7619 |  |  | 16.8768 | 16.1122 | 17.9318 | 16.3447 | 15.6264 | 15.7384 | 69.5928 | 84.0396 | 56.4047 | 56.7743 | 29.9733 |  | 21.1767 | 34.8134 | 21.8265 | 21.1526 | 19.8255 | 60.4273 |  | 34.2233 |  |  | 12.924 | 14.1346 | 24.8486 | [6 empty] | 20.5683 |  |  | 18.4448 |  |  | 11.9636 | 18.6344 | 90.1168 | 8.2067 | 15.5013 | 63.7171 | 9.1945 | 14.4839 | 67.8617 | 13.8719 | 59.3913 | 9.31 | 51.2779 | 10.1218 | 51.9117 | 9.4324 | 16.8557 | 61.2186 | 13.8322 | 17.192 | 79.8465 | 9.8689 | 15.2389 | 69.2913 | 10.1523 | 49.95 | 13.2983 | 60.4332 | 10.8863 | 55.0731 | 0.36034 | 20.0821 | 0.57592 | 0.058423 | -38.085 | 3.1222 | 62.08 | 49.05 | -0.67096 | 0.26422 | 0.078049 | -0.62558 | 0.19703 | 0.56869 | 0.52567 | 0.18115 | 0.068526 | 0.38088 | -0.31 | 0.036782 | 0.0090156 | 0.22511
42810.4433 | 283 | 18.4875 | 18.5769 | 18.5564 | 18.5661 | 17.8698 | 16.4708 | 14.518 | 16.6417 | 17.1381 | 17.2318 | 17.241 | 16.7589 | 15.7742 | 14.3967 | 14.8694 | 14.8853 | 15.4428 | 13.3163 | 13.5542 | 14.4148 |  |  |  | 16.5449 | 15.893 | 16.8081 | 73.3599 | 71.4804 | 80.2292 | 17.1411 | 16.2842 | 16.1977 | 16.826 | 16.117 | 16.3814 | 20.0299 | 71.321 |  | 38.4763 | 61.4801 | 63.9222 | 33.6396 |  | 6.5678 | 6.8204 | 6.2218 | 6.5777 | 6.8 | 8.0732 | 23.7362 | 4.6404 | 6.5825 | 4.5932 | 7.0209 | 8.0744 | 42.4571 | 47.1636 | 43.1726 | 14.8966 |  |  | -0.39996 | 0.024403 | -0.38585 | -0.034826 | -0.083288 | -0.15488 | -0.26229 | 0.76735 | -0.047078 | -0.22655 | -0.17318 | 8.9025 | -0.00051583 | 1.9198 | 15.8315 | 16.7118 | 17.2343 | 17.5469 | 17.484 | 16.4357 | 14.7841 | 16.8134 | 17.1413 | 17.434 | 17.4777 | 17.1826 | 16.3587 | 14.5628 | 17.0125 | 10.9724 | 12.6903 | 9.931 | 9.2225 | 12.1785 | 9.7012 | 15.9266 | 15.5385 | 15.3806 | 14.2908 | 14.3525 | 14.6432 |  |  |  | 18.855 | 81.7399 | 68.9467 | 24.9049 | -0.21775 | -0.23071 | 23.4002 |  |  | 10.7527 |  |  | 16.8762 | 16.1101 | 17.9436 | 16.3372 | 15.6247 | 15.7376 | 69.5927 | 84.1984 | 56.4504 | 56.85 | 30.564 |  | 21.2574 | 36.112 | 21.8912 | 21.681 | 19.8945 | 60.035 |  | 34.3158 |  |  | 12.9512 | 14.1563 | 25.0449 | [6 empty] | 20.641 |  |  | 18.4869 |  |  | 11.9753 | 18.6495 | 90.1361 | 8.217 | 15.4692 | 63.8353 | 9.206 | 14.5755 | 67.9015 | 13.8843 | 59.4302 | 9.3214 | 51.322 | 10.1466 | 51.8559 | 9.4432 | 16.8448 | 61.3583 | 13.8376 | 17.1692 | 79.8808 | 9.8732 | 15.2352 | 69.3208 | 10.1333 | 50.0459 | 13.2958 | 60.4671 | 10.8808 | 55.128 | 0.43584 | 20.0808 | 0.57681 | 0.057735 | -38.0939 | 3.1222 | 56.79 | 50.05 | -0.82851 | 0.18216 | -0.72432 | -0.21761 | -0.33727 | -0.45993 | -0.59852 | 0.16745 | 0.034626 | 0.36851 | -0.1613 | 0.030799 | 0.040862 | 0.24418
42810.4433 | 284 | 18.493 | 18.5889 | 18.5675 | 18.5691 | 17.8813 | 16.4805 | 14.5265 | 16.65 | 17.1407 | 17.2385 | 17.2445 | 16.7647 | 15.7843 | 14.4022 | 14.8765 | 14.8806 | 15.4404 | 13.3054 | 13.5617 | 14.4186 |  |  |  | 16.5459 | 15.8913 | 16.8212 | 73.4764 | 71.4829 | 80.5836 | 17.1395 | 16.2845 | 16.1973 | 16.8207 | 16.107 | 16.3906 | 20.0716 | 71.742 |  | 38.5539 | 61.558 | 63.9655 | 32.8929 |  | 6.5687 | 6.8135 | 6.2076 | 6.5573 | 6.7754 | 8.0457 | 23.686 | 4.7538 | 6.5863 | 4.5117 | 7.0212 | 8.0761 | 42.444 | 47.1651 | 43.1659 | 14.9106 |  |  | -0.26526 | 0.13348 | 0.024192 | -0.16362 | -0.15623 | -0.65232 | -0.38911 | 0.53144 | -2.0073 | -0.33984 | -0.35002 | 8.9033 | -0.00048134 | 1.9571 | 15.824 | 16.698 | 17.2249 | 17.5427 | 17.4848 | 16.4306 | 14.7785 | 16.7996 | 17.1423 | 17.4377 | 17.4704 | 17.1854 | 16.3595 | 14.5489 | 16.0782 | 10.73 | 12.0748 | 9.7329 | 9.0315 | 12.1689 | 9.7075 | 15.927 | 15.5369 | 15.3768 | 14.2974 | 14.3454 | 14.6452 |  |  |  | 18.9079 | 81.6868 | 68.5644 | 24.561 | -0.14643 | -0.23316 | 23.4574 |  |  | 10.7618 |  |  | 16.8781 | 16.1109 | 17.9705 | 16.3323 | 15.629 | 15.7585 | 69.6134 | 84.3848 | 56.4742 | 56.8895 | 31.4415 |  | 21.3044 | 36.8593 | 21.9385 | 21.9557 | 19.9285 | 59.9732 |  | 34.389 |  |  | 12.9673 | 14.1792 | 25.2117 | [6 empty] | 20.7275 |  |  | 18.4781 |  |  | 11.9844 | 18.7734 | 90.2332 | 8.2328 | 15.5517 | 63.8879 | 9.2183 | 14.6014 | 67.9248 | 13.8953 | 59.5128 | 9.3368 | 51.3718 | 10.1441 | 51.8678 | 9.4463 | 16.8164 | 61.4751 | 13.8395 | 17.1728 | 79.8982 | 9.881 | 15.2395 | 69.4233 | 10.133 | 50.085 | 13.308 | 60.6402 | 10.8929 | 55.2018 | 0.42063 | 20.0815 | 0.57792 | 0.057142 | -37.9839 | 3.1223 | 67.7 | 48.95 | -0.67505 | 0.42602 | 0.18137 | -0.47167 | -0.4619 | -0.94385 | -0.72897 | 0.14466 | 0.015459 | 0.36202 | -0.05862 | 0.099929 | 0.062999 | 0.2555
42810.4433 | 285 | 18.4875 | 18.5796 | 18.5609 | 18.5685 | 17.8762 | 16.4749 | 14.5221 | 16.6458 | 17.1357 | 17.235 | 17.24 | 16.7616 | 15.7835 | 14.401 | 14.8762 | 14.8799 | 15.4477 | 13.3175 | 13.5676 | 14.4276 |  |  |  | 16.5461 | 15.898 | 16.8405 | 73.5974 | 71.5011 | 80.7016 | 17.1405 | 16.2825 | 16.2049 | 16.8186 | 16.1096 | 16.3996 | 20.1165 | 72.0172 |  | 38.6225 | 61.6388 | 63.9949 | 32.1813 |  | 6.5657 | 6.8109 | 6.1936 | 6.5517 | 6.7559 | 8.0067 | 23.3693 | 4.7235 | 6.5765 | 4.4809 | 7.0159 | 8.0744 | 42.4129 | 47.1616 | 43.1519 | 14.9254 |  |  | -0.27906 | 0.090111 | 0.21081 | -0.08871 | -0.103 | -0.58858 | -0.42657 | 0.2226 | -0.092614 | 0.23585 | -0.17914 | 8.9032 | -0.00049284 | 1.9759 | 15.8259 | 16.7061 | 17.2276 | 17.548 | 17.4878 | 16.4444 | 14.7833 | 16.798 | 17.1462 | 17.435 | 17.4693 | 17.1897 | 16.3584 | 14.5524 | 15.0556 | 10.3844 | 11.2524 | 9.4523 | 8.8793 | 12.1637 | 9.7173 | 15.9273 | 15.5375 | 15.3821 | 14.299 | 14.3445 | 14.6467 |  |  |  | 18.9561 | 81.6357 | 68.5295 | 24.8496 | -0.074305 | -0.11158 | 23.5 |  |  | 10.7682 |  |  | 16.8774 | 16.1171 | 17.9993 | 16.34 | 15.6347 | 15.765 | 69.6129 | 84.5412 | 56.5048 | 56.9129 | 32.5728 |  | 21.3854 | 37.9087 | 22.0029 | 22.2882 | 19.9869 | 60.3692 |  | 34.4727 |  |  | 12.9708 | 14.1925 | 25.5009 | [6 empty] | 20.846 |  |  | 18.4947 |  |  | 11.9895 | 18.9353 | 90.4282 | 8.2503 | 15.7672 | 63.9168 | 9.2234 | 14.5952 | 67.8975 | 13.9101 | 59.5981 | 9.3498 | 51.4211 | 10.1509 | 51.9001 | 9.4494 | 16.7703 | 61.5344 | 13.8373 | 17.187 | 79.9529 | 9.8946 | 15.2408 | 69.5815 | 10.1268 | 50.0909 | 13.2977 | 60.7767 | 10.902 | 55.3103 | 0.25287 | 20.0784 | 0.57796 | 0.05725 | -38.0198 | 3.1222 | 75.83 | 48.97 | -0.69251 | 0.35003 | 0.53538 | -0.3473 | -0.37503 | -0.89649 | -0.76319 | 0.11595 | -0.011528 | 0.35474 | 0.054412 | 0.19244 | 0.084271 | 0.2491
42810.4433 | 286 | 18.4819 | 18.5652 | 18.5572 | 18.5602 | 17.8672 | 16.4663 | 14.5224 | 16.6391 | 17.1331 | 17.2351 | 17.2321 | 16.7532 | 15.78 | 14.3934 | 14.8743 | 14.8821 | 15.4496 | 13.3204 | 13.5712 | 14.4332 |  |  |  | 16.5519 | 15.903 | 16.8532 | 73.6683 | 71.4774 | 80.6642 | 17.147 | 16.2878 | 16.2148 | 16.8254 | 16.1197 | 16.4137 | 20.162 | 71.7812 |  | 38.6942 | 61.7552 | 64.0352 | 31.2195 |  | 6.5798 | 6.8238 | 6.192 | 6.5399 | 6.7395 | 7.9662 | 23.0162 | 4.5621 | 6.5773 | 4.4578 | 7.0074 | 8.0707 | 42.3785 | 47.1604 | 43.1376 | 14.9446 |  |  | -0.31125 | 0.065143 | -0.033632 | 0.18137 | -0.064892 | -1.1905 | -0.57705 | 0.41119 | -0.46177 | -1.2474 | -0.26617 | 8.9032 | -0.00043862 | 1.9597 | 15.8358 | 16.7108 | 17.2358 | 17.5497 | 17.496 | 16.4479 | 14.79 | 16.811 | 17.1471 | 17.4425 | 17.4866 | 17.1954 | 16.3592 | 14.5561 | 13.6612 | 9.9832 | 10.3151 | 9.0079 | 8.674 | 12.1418 | 9.7124 | 15.9246 | 15.5314 | 15.3786 | 14.3047 | 14.3508 | 14.6599 |  |  |  | 19.0085 | 81.6685 | 68.7735 | 25.367 | -0.17642 | -0.30561 | 23.6784 |  |  | 10.7706 |  |  | 16.876 | 16.1188 | 18.0153 | 16.3376 | 15.6309 | 15.7688 | 69.5403 | 84.5485 | 56.5492 | 56.9331 | 32.8842 |  | 21.454 | 39.1598 | 22.0621 | 22.4977 | 20.0393 | 60.267 |  | 34.541 |  |  | 12.9894 | 14.2039 | 25.6345 | [6 empty] | 20.9551 |  |  | 18.5399 |  |  | 11.997 | 18.9882 | 90.6044 | 8.2552 | 15.9361 | 63.954 | 9.2256 | 14.577 | 67.9342 | 13.9272 | 59.5414 | 9.365 | 51.4306 | 10.1567 | 51.9617 | 9.4599 | 16.7545 | 61.6086 | 13.855 | 17.2032 | 80.0773 | 9.9067 | 15.2595 | 69.7127 | 10.1252 | 50.1217 | 13.2908 | 60.7615 | 10.9208 | 55.4242 | 0.25865 | 20.0784 | 0.57858 | 0.055173 | -37.9371 | 3.1222 | 55.46 | 50.11 | -0.73133 | 0.29762 | -0.21385 | 0.4966 | -0.29765 | -1.2749 | -0.8876 | 0.1096 | -0.044293 | 0.35067 | 0.20679 | 0.29601 | 0.11251 | 0.23648
42810.4434 | 287 | 18.4817 | 18.5757 | 18.5545 | 18.5617 | 17.8646 | 16.4692 | 14.5195 | 16.6325 | 17.1404 | 17.2273 | 17.2301 | 16.7547 | 15.78 | 14.397 | 14.8762 | 14.8912 | 15.4538 | 13.3196 | 13.5704 | 14.4441 |  |  |  | 16.5552 | 15.9007 | 16.8722 | 73.709 | 71.4464 | 80.7434 | 17.1508 | 16.2834 | 16.2222 | 16.8188 | 16.1187 | 16.4255 | 20.2044 | 71.2095 |  | 38.7644 | 61.8586 | 64.0638 | 30.2686 |  | 6.5905 | 6.8211 | 6.1807 | 6.5125 | 6.7099 | 7.9139 | 22.5963 | 4.4595 | 6.5688 | 4.4188 | 7.007 | 8.0656 | 42.3444 | 47.152 | 43.1213 | 14.9532 |  |  | -0.29548 | 0.044771 | 0.24827 | 0.088054 | -0.1214 | -0.20154 | -0.34377 | 0.36716 | -0.57269 | -0.34613 | -0.092702 | 8.9035 | -0.00045998 | 1.9267 | 15.8322 | 16.7084 | 17.2343 | 17.5451 | 17.4939 | 16.4444 | 14.7841 | 16.8088 | 17.1476 | 17.4367 | 17.485 | 17.1929 | 16.3673 | 14.5573 | 12.5055 | 9.7355 | 9.54 | 8.5504 | 8.3636 | 12.121 | 9.7147 | 15.9249 | 15.5275 | 15.375 | 14.2935 | 14.3491 | 14.6638 |  |  |  | 19.047 | 81.6871 | 68.6515 | 24.9451 | -0.0029902 | -0.21772 | 23.8752 |  |  | 10.7769 |  |  | 16.8794 | 16.1239 | 18.0404 | 16.3383 | 15.6249 | 15.7799 | 69.5021 | 84.6549 | 56.6024 | 56.9856 | 31.8342 |  | 21.52 | 38.5552 | 22.1173 | 22.5555 | 20.1044 | 59.9017 |  | 34.6278 |  |  | 13.0019 | 14.2156 | 25.3647 | [6 empty] | 21.0334 |  |  | 18.5427 |  |  | 12.0012 | 18.9847 | 90.7142 | 8.2759 | 15.9563 | 63.9963 | 9.2363 | 14.5731 | 68.0711 | 13.9461 | 59.5568 | 9.3735 | 51.4187 | 10.161 | 52.116 | 9.4335 | 16.7521 | 61.6591 | 13.8699 | 17.2346 | 80.1489 | 9.9159 | 15.3121 | 69.7278 | 10.1479 | 50.1552 | 13.2892 | 60.7773 | 10.9304 | 55.5129 | 0.35765 | 20.0772 | 0.57852 | 0.054942 | -37.9036 | 3.1223 | 56.23 | 49.22 | -0.71264 | 0.24673 | 0.58101 | 0.34602 | -0.40709 | -0.5245 | -0.68502 | 0.14099 | -0.02564 | 0.35125 | 0.33277 | 0.38241 | 0.14034 | 0.24948
42810.4434 | 288 | 18.4853 | 18.5708 | 18.5601 | 18.5504 | 17.8645 | 16.4646 | 14.5136 | 16.6307 | 17.1363 | 17.2259 | 17.2261 | 16.7543 | 15.7716 | 14.3936 | 14.868 | 14.8719 | 15.4404 | 13.3088 | 13.5691 | 14.4363 |  |  |  | 16.5402 | 15.892 | 16.8662 | 73.8209 | 71.506 | 81.0277 | 17.1568 | 16.2932 | 16.2417 | 16.8305 | 16.1242 | 16.4403 | 20.2569 | 71.1413 |  | 38.86 | 61.9687 | 64.1507 | 30.8287 |  | 6.598 | 6.8142 | 6.1701 | 6.5027 | 6.6762 | 7.8589 | 22.1728 | 4.4496 | 6.5677 | 4.3304 | 6.9992 | 8.0716 | 42.3053 | 47.1598 | 43.1173 | 14.9628 |  |  | -0.31585 | -0.039997 | 0.050476 | 0.06111 | -0.17528 | -0.28762 | -0.084868 | 0.49596 | -0.80991 | -0.41117 | -0.19801 | 8.9032 | -0.00049119 | 1.8795 | 15.8231 | 16.6974 | 17.2299 | 17.5393 | 17.4884 | 16.4379 | 14.7809 | 16.8045 | 17.1473 | 17.4402 | 17.4748 | 17.1864 | 16.3573 | 14.5533 | 11.6996 | 9.5072 | 8.8887 | 8.1145 | 7.9494 | 12.0898 | 9.7029 | 15.9265 | 15.5271 | 15.3842 | 14.2931 | 14.3577 | 14.674 |  |  |  | 19.0812 | 81.6601 | 68.7664 | 24.3604 | 0.026387 | -0.40235 | 23.8248 |  |  | 10.7775 |  |  | 16.8776 | 16.1239 | 18.0534 | 16.3368 | 15.6243 | 15.7941 | 69.5623 | 84.6218 | 56.6469 | 57.0646 | 30.9193 |  | 21.5649 | 37.8904 | 22.1623 | 22.5311 | 20.1457 | 59.774 |  | 34.7004 |  |  | 13.0041 | 14.2112 | 25.0159 | [6 empty] | 21.0906 |  |  | 18.5841 |  |  | 12.0191 | 18.9918 | 90.6502 | 8.2992 | 15.9569 | 64.0461 | 9.2423 | 14.5839 | 68.099 | 13.954 | 59.6619 | 9.3852 | 51.4708 | 10.1713 | 52.2112 | 9.4358 | 16.9107 | 61.6964 | 13.8902 | 17.2562 | 80.2713 | 9.9329 | 15.4825 | 69.82 | 10.1726 | 50.1973 | 13.3061 | 60.856 | 10.9507 | 55.5623 | 0.22437 | 20.0766 | 0.58159 | 0.057381 | -37.9663 | 3.1223 | 63.41 | 48.6 | -0.73709 | -0.2332 | 0.26198 | 0.28825 | -0.4891 | -0.62652 | -0.34033 | 0.16791 | -0.0056599 | 0.35331 | 0.41869 | 0.45339 | 0.12655 | 0.26687
42810.4434 | 289 | 18.4918 | 18.5812 | 18.5643 | 18.562 | 17.8711 | 16.4827 | 14.5219 | 16.644 | 17.1344 | 17.2293 | 17.2346 | 16.7664 | 15.7775 | 14.4053 | 14.8733 | 14.8803 | 15.4434 | 13.3179 | 13.5781 | 14.4462 |  |  |  | 16.5354 | 15.8964 | 16.8966 | 73.9519 | 71.5595 | 81.0574 | 17.1476 | 16.2852 | 16.2441 | 16.8318 | 16.1218 | 16.4508 | 20.3087 | 71.1971 |  | 38.9412 | 62.039 | 64.2369 | 30.9415 |  | 6.6143 | 6.8125 | 6.1764 | 6.4916 | 6.6616 | 7.8257 | 21.8176 | 4.4774 | 6.5657 | 4.2645 | 6.9991 | 8.0781 | 42.2822 | 47.1554 | 43.1159 | 14.9836 |  |  | -0.25606 | 0.1072 | 0.039964 | 0.18333 | -0.17726 | -0.14502 | 0.42966 | -0.15853 | -0.080354 | -0.62118 | -0.13065 | 8.9027 | -0.00048298 | 1.828 | 15.8223 | 16.6946 | 17.2266 | 17.5373 | 17.4811 | 16.432 | 14.7795 | 16.7987 | 17.1392 | 17.4338 | 17.4675 | 17.1821 | 16.3642 | 14.5541 | 11.0908 | 9.3625 | 8.332 | 7.7386 | 7.5677 | 12.064 | 9.6907 | 15.9227 | 15.5282 | 15.3815 | 14.3004 | 14.3597 | 14.6702 |  |  |  | 19.1305 | 81.7375 | 69.0198 | 24.5618 | -0.19506 | -0.16051 | 23.7169 |  |  | 10.7761 |  |  | 16.8783 | 16.1208 | 18.0798 | 16.3351 | 15.6297 | 15.8025 | 69.6765 | 84.5478 | 56.7118 | 57.1587 | 30.9247 |  | 21.6164 | 37.4979 | 22.2115 | 22.2666 | 20.2027 | 59.778 |  | 34.7738 |  |  | 13.014 | 14.213 | 25.0954 | [6 empty] | 21.1378 |  |  | 18.6202 |  |  | 12.0188 | 19.0134 | 90.7613 | 8.3278 | 15.9933 | 64.0461 | 9.2266 | 14.5594 | 68.1283 | 13.9575 | 59.7602 | 9.4127 | 51.6083 | 10.1656 | 52.298 | 9.5075 | 17.6025 | 61.7671 | 13.8916 | 17.2553 | 80.3955 | 9.9269 | 15.532 | 69.912 | 10.1761 | 50.2681 | 13.3039 | 61.0251 | 10.9437 | 55.6106 | 0.35842 | 20.0762 | 0.58167 | 0.059052 | -37.9718 | 3.1223 | 53.41 | 50.1 | -0.66369 | 0.38178 | 0.2331 | 0.49927 | -0.49182 | -0.44486 | 0.76571 | 0.16949 | 0.0068963 | 0.36257 | 0.48334 | 0.51384 | 0.12515 | 0.26292
42810.4434 | 290 | 18.49 | 18.5797 | 18.562 | 18.5614 | 17.8695 | 16.482 | 14.5257 | 16.6428 | 17.1318 | 17.2252 | 17.2326 | 16.7567 | 15.7701 | 14.3936 | 14.868 | 14.8757 | 15.4403 | 13.3102 | 13.5729 | 14.4386 |  |  |  | 16.5289 | 15.8996 | 16.9085 | 73.9901 | 71.6193 | 80.8447 | 17.1447 | 16.2842 | 16.2546 | 16.8275 | 16.1148 | 16.4617 | 20.3602 | 71.2055 |  | 39.0035 | 62.0986 | 64.2943 | 30.9244 |  | 6.618 | 6.8136 | 6.1778 | 6.4941 | 6.6535 | 7.8122 | 21.9789 | 4.522 | 6.5719 | 4.2641 | 7.0018 | 8.0777 | 42.2673 | 47.1302 | 43.1139 | 14.9871 |  |  | -0.53467 | 0.006003 | 0.023536 | -0.023658 | -0.25348 | -0.17 | 0.23646 | -0.13487 | -1.0164 | 0.65797 | -0.054154 | 8.9027 | -0.00040741 | 1.8231 | 15.8258 | 16.6917 | 17.2322 | 17.5478 | 17.4859 | 16.4399 | 14.7799 | 16.803 | 17.1351 | 17.4312 | 17.4728 | 17.1781 | 16.3657 | 14.5524 | 10.4859 | 9.2699 | 7.8925 | 7.4232 | 7.3086 | 12.0426 | 9.6885 | 15.9184 | 15.5313 | 15.3758 | 14.3008 | 14.3506 | 14.6726 |  |  |  | 19.1728 | 81.8927 | 68.9813 | 24.9805 | -0.16446 | -0.3329 | 23.6704 |  |  | 10.7785 |  |  | 16.8793 | 16.1202 | 18.0942 | 16.3317 | 15.6287 | 15.8103 | 69.7004 | 84.6019 | 56.7472 | 57.2241 | 30.8073 |  | 21.6716 | 37.2772 | 22.2546 | 22.0132 | 20.2392 | 59.7718 |  | 34.8499 |  |  | 12.9961 | 14.2042 | 25.059 | [6 empty] | 21.0192 |  |  | 18.6572 |  |  | 12.0281 | 19.0552 | 90.695 | 8.3614 | 15.9821 | 64.0391 | 9.2417 | 14.5521 | 68.1424 | 13.9822 | 59.7838 | 9.438 | 51.7233 | 10.1621 | 52.3675 | 9.5158 | 17.8769 | 61.7664 | 13.8973 | 17.2913 | 80.3926 | 9.9293 | 15.528 | 69.9917 | 10.1918 | 50.39 | 13.3141 | 61.2182 | 10.9527 | 55.7158 | 0.24209 | 20.0737 | 0.58208 | 0.058336 | -38.0756 | 3.1223 | 66.27 | 48.72 | -0.95876 | 0.090345 | 0.17889 | -0.17935 | -0.58812 | -0.48163 | 0.56803 | 0.1746 | 0.014475 | 0.37083 | 0.54805 | 0.56242 | 0.12735 | 0.25271
42810.4434 | 291 | 18.4939 | 18.5744 | 18.5626 | 18.5588 | 17.8674 | 16.473 | 14.5224 | 16.6368 | 17.1288 | 17.2224 | 17.2285 | 16.7489 | 15.7701 | 14.3926 | 14.8751 | 14.8739 | 15.4463 | 13.3141 | 13.5694 | 14.4533 |  |  |  | 16.5423 | 15.8988 | 16.9238 | 74.0253 | 71.7338 | 80.5535 | 17.1427 | 16.2811 | 16.2545 | 16.8216 | 16.1105 | 16.4637 | 20.4098 | 71.3474 |  | 39.0864 | 62.1472 | 64.3608 | 31.2612 |  | 6.6197 | 6.8139 | 6.1829 | 6.4965 | 6.6345 | 7.8872 | 22.9269 | 4.5984 | 6.5682 | 4.3167 | 6.9954 | 8.0792 | 42.2718 | 47.1114 | 43.1055 | 14.9848 |  |  | -0.37302 | -0.050509 | -0.005376 | -0.02037 | -0.19106 | -0.12991 | 0.24238 | -0.21701 | -0.30862 | 0.87511 | -0.20795 | 8.9036 | -0.00048955 | 1.8402 | 15.8198 | 16.6974 | 17.2243 | 17.5347 | 17.4878 | 16.4398 | 14.777 | 16.8032 | 17.1444 | 17.4289 | 17.4703 | 17.1854 | 16.359 | 14.5484 | 9.895 | 9.1487 | 7.5511 | 7.1572 | 7.116 | 12.0272 | 9.6848 | 15.9145 | 15.5212 | 15.3695 | 14.2868 | 14.355 | 14.6688 |  |  |  | 19.2153 | 82.0392 | 69.2145 | 25.1322 | 0.080481 | -0.18291 | 23.6376 |  |  | 10.7862 |  |  | 16.8811 | 16.1264 | 18.1183 | 16.3362 | 15.624 | 15.8223 | 69.8264 | 84.7269 | 56.7776 | 57.2754 | 29.83 |  | 21.7139 | 37.5083 | 22.2933 | 21.7792 | 20.2704 | 59.5369 |  | 34.9147 |  |  | 12.9841 | 14.2049 | 24.8071 | [6 empty] | 20.8895 |  |  | 18.7001 |  |  | 12.0416 | 19.0709 | 90.6723 | 8.3901 | 15.9539 | 63.9559 | 9.2639 | 14.5855 | 68.2093 | 13.9954 | 59.8022 | 9.4471 | 51.829 | 10.1727 | 52.4201 | 9.5055 | 17.8406 | 61.8151 | 13.9091 | 17.3247 | 80.4315 | 9.946 | 15.5516 | 70.0483 | 10.2072 | 50.5146 | 13.2933 | 61.3057 | 10.9679 | 55.8304 | 0.26443 | 20.0741 | 0.58292 | 0.058321 | -38.0739 | 3.1223 | 54.03 | 49 | -0.80049 | -0.26206 | -0.085496 | -0.16642 | -0.51066 | -0.42109 | 0.57517 | 0.20317 | 0.0093581 | 0.37837 | 0.61191 | 0.59992 | 0.11966 | 0.24991
42810.4434 | 292 | 18.4888 | 18.5723 | 18.5594 | 18.5619 | 17.8651 | 16.4674 | 14.5164 | 16.6318 | 17.1302 | 17.2209 | 17.2289 | 16.7476 | 15.772 | 14.3929 | 14.8794 | 14.8845 | 15.4459 | 13.3155 | 13.5741 | 14.4497 |  |  |  | 16.5491 | 15.9085 | 16.9391 | 74.0151 | 71.8046 | 80.0173 | 17.1443 | 16.277 | 16.2658 | 16.8183 | 16.1144 | 16.4763 | 20.4703 | 71.5912 |  | 39.1678 | 62.1861 | 64.4353 | 31.6906 |  | 6.6248 | 6.8098 | 6.1897 | 6.4968 | 6.6307 | 7.8744 | 23.2881 | 4.6615 | 6.5742 | 4.3749 | 6.9923 | 8.0804 | 42.2773 | 47.1117 | 43.1009 | 14.9892 |  |  | -0.19429 | -0.077453 | -0.006692 | 0.17282 | 0.15393 | -0.0596 | 0.20164 | -0.39969 | -0.11752 | -0.46152 | -0.065877 | 8.9035 | -0.00049119 | 1.8793 | 15.8178 | 16.705 | 17.2296 | 17.5408 | 17.4847 | 16.4401 | 14.7826 | 16.7964 | 17.1402 | 17.4301 | 17.4729 | 17.1919 | 16.3546 | 14.5442 | 9.8414 | 9.0825 | 7.2649 | 6.9372 | 6.9481 | 12.0108 | 9.668 | 15.9159 | 15.5293 | 15.3754 | 14.2943 | 14.3504 | 14.6866 |  |  |  | 19.2747 | 82.133 | 69.3567 | 25.0214 | 0.20265 | -0.086171 | 23.6465 |  |  | 10.784 |  |  | 16.8806 | 16.1207 | 18.1405 | 16.3395 | 15.6276 | 15.8296 | 69.9521 | 84.7359 | 56.8094 | 57.3203 | 29.4256 |  | 21.7465 | 37.4778 | 22.3294 | 21.7448 | 20.304 | 59.2046 |  | 34.9784 |  |  | 12.9763 | 14.2055 | 24.7279 | [6 empty] | 20.8442 |  |  | 18.7393 |  |  | 12.0559 | 19.094 | 90.6733 | 8.4122 | 15.9386 | 63.9212 | 9.2671 | 14.7065 | 68.2186 | 14.0238 | 59.8613 | 9.4727 | 51.9355 | 10.2013 | 52.5096 | 9.5457 | 17.7978 | 61.849 | 13.9126 | 17.3389 | 80.522 | 9.9548 | 15.5617 | 70.1671 | 10.2181 | 50.571 | 13.294 | 61.2725 | 10.9757 | 55.8771 | 0.36978 | 20.072 | 0.58363 | 0.057786 | -38.039 | 3.1224 | 69.69 | 49.97 | -0.57727 | -0.32451 | -0.095388 | 0.48475 | 0.45835 | -0.28521 | 0.52459 | 0.2155 | 0.011419 | 0.38045 | 0.61596 | 0.62977 | 0.10976 | 0.25498
42810.4434 | 293 | 18.4911 | 18.5751 | 18.5668 | 18.5623 | 17.8712 | 16.4709 | 14.524 | 16.6368 | 17.1385 | 17.2289 | 17.2361 | 16.7529 | 15.7723 | 14.3919 | 14.8706 | 14.8754 | 15.4409 | 13.3154 | 13.5727 | 14.4645 |  |  |  | 16.5492 | 15.9036 | 16.9527 | 74.0415 | 71.7942 | 80.1208 | 17.147 | 16.2835 | 16.2769 | 16.8215 | 16.1171 | 16.4834 | 20.521 | 71.7477 |  | 39.2466 | 62.2358 | 64.4894 | 31.7708 |  | 6.6235 | 6.8264 | 6.196 | 6.4992 | 6.637 | 7.8547 | 23.3721 | 4.7199 | 6.57 | 4.4219 | 6.9912 | 8.0776 | 42.2777 | 47.114 | 43.0766 | 14.9804 |  |  | -0.59579 | -0.13462 | 0.041936 | -0.36536 | -0.006408 | 0.13359 | 0.22726 | -0.11056 | -0.04124 | -0.28047 | -0.20338 | 8.9033 | -0.00045505 | 1.9314 | 15.8263 | 16.7054 | 17.2342 | 17.545 | 17.4869 | 16.4419 | 14.7766 | 16.8056 | 17.1372 | 17.4384 | 17.4729 | 17.1888 | 16.3607 | 14.5528 | 11.3186 | 9.2752 | 7.2501 | 6.8092 | 6.79 | 12.0416 | 9.6597 | 15.9152 | 15.5393 | 15.3848 | 14.3005 | 14.3564 | 14.6959 |  |  |  | 19.3139 | 82.3088 | 69.547 | 24.6649 | 0.21075 | -0.06641 | 23.6933 |  |  | 10.7836 |  |  | 16.8732 | 16.1223 | 18.1578 | 16.3353 | 15.6237 | 15.8347 | 70.0515 | 84.777 | 56.8127 | 57.3559 | 31.0731 |  | 21.8103 | 36.6684 | 22.3743 | 21.9565 | 20.3482 | 59.4725 |  | 35.0698 |  |  | 12.9657 | 14.2183 | 24.8325 | [6 empty] | 20.9227 |  |  | 18.8112 |  |  | 12.0738 | 19.1212 | 90.4577 | 8.4342 | 16.0103 | 63.928 | 9.2865 | 14.8043 | 68.2543 | 14.0466 | 60.0342 | 9.5176 | 52.0285 | 10.2261 | 52.6025 | 9.5659 | 17.7762 | 61.897 | 13.9358 | 17.3624 | 80.6031 | 9.9631 | 15.5559 | 70.2368 | 10.2436 | 50.5789 | 13.2965 | 61.2214 | 10.9788 | 55.9606 | 0.40984 | 20.0727 | 0.58323 | 0.056729 | -37.9767 | 3.1223 | 54.78 | 48.46 | -1.011 | -0.42784 | 0.23879 | -0.70483 | -0.093516 | 0.42699 | 0.55692 | 0.17188 | 0.035411 | 0.37606 | 0.45543 | 0.63044 | 0.10923 | 0.26619
42810.4434 | 294 | 18.4949 | 18.5763 | 18.5708 | 18.5568 | 17.8693 | 16.4738 | 14.5235 | 16.6431 | 17.1326 | 17.2265 | 17.2275 | 16.7542 | 15.7708 | 14.3883 | 14.8733 | 14.8815 | 15.4476 | 13.3178 | 13.583 | 14.469 |  |  |  | 16.5466 | 15.9038 | 16.9669 | 74.1023 | 71.7781 | 80.2905 | 17.1608 | 16.2918 | 16.283 | 16.8243 | 16.1249 | 16.5048 | 20.5761 | 71.945 |  | 39.3185 | 62.302 | 64.5455 | 31.1745 |  | 6.6509 | 6.8503 | 6.202 | 6.515 | 6.6558 | 7.867 | 23.3665 | 4.792 | 6.5732 | 4.4923 | 6.9983 | 8.0751 | 42.288 | 47.1179 | 43.055 | 14.9694 |  |  | -0.35462 | -0.16091 | -0.002748 | -0.28585 | 0.030392 | 0.090224 | 0.42703 | -0.089532 | -0.27009 | 0.12382 | -0.2308 | 8.9031 | -0.00044355 | 1.959 | 15.8174 | 16.7051 | 17.2353 | 17.5453 | 17.4952 | 16.4443 | 14.7796 | 16.8114 | 17.146 | 17.4356 | 17.477 | 17.1884 | 16.3603 | 14.5518 | 12.7719 | 10.0458 | 8.3746 | 7.1849 | 6.6659 | 12.0696 | 9.6623 | 15.9101 | 15.5371 | 15.3824 | 14.3035 | 14.3583 | 14.7016 |  |  |  | 19.3495 | 82.5681 | 69.9979 | 24.5314 | 0.05779 | -0.20285 | 23.7993 |  |  | 10.7864 |  |  | 16.874 | 16.128 | 18.1683 | 16.3325 | 15.6243 | 15.8452 | 70.1154 | 84.7904 | 56.7982 | 57.3646 | 32.3314 |  | 21.8668 | 36.1666 | 22.4224 | 22.1249 | 20.3851 | 59.6414 |  | 35.1293 |  |  | 12.9501 | 14.2092 | 24.9464 | [6 empty] | 21.0608 |  |  | 18.8507 |  |  | 12.0865 | 19.1574 | 90.4518 | 8.4411 | 16.2094 | 63.9755 | 9.2987 | 14.8073 | 68.1699 | 14.0682 | 60.3452 | 9.5498 | 52.0939 | 10.2394 | 52.6647 | 9.5715 | 17.7829 | 61.9897 | 13.9451 | 17.3862 | 80.5577 | 9.9751 | 15.5846 | 70.2361 | 10.2851 | 50.6425 | 13.2964 | 61.277 | 10.9836 | 55.9869 | 0.17988 | 20.0709 | 0.58379 | 0.056107 | -37.9056 | 3.1223 | 37.53 | 49.77 | -0.78021 | -0.46777 | -0.06113 | -0.62347 | 0.20366 | 0.35091 | 0.76342 | 0.13882 | 0.050969 | 0.37262 | 0.2972 | 0.5058 | 0.12764 | 0.27109
42810.4434 | 295 | 18.4847 | 18.5749 | 18.5606 | 18.5616 | 17.8681 | 16.4714 | 14.5275 | 16.6359 | 17.1289 | 17.23 | 17.229 | 16.7492 | 15.7735 | 14.3895 | 14.8719 | 14.8837 | 15.4454 | 13.3133 | 13.5857 | 14.4697 |  |  |  | 16.5425 | 15.9005 | 16.9811 | 74.1819 | 71.8165 | 80.2389 | 17.1478 | 16.2832 | 16.2854 | 16.815 | 16.1128 | 16.5159 | 20.6171 | 71.9388 |  | 39.3928 | 62.3853 | 64.599 | 30.5905 |  | 6.6579 | 6.8521 | 6.1986 | 6.5227 | 6.6527 | 7.9114 | 23.2731 | 4.882 | 6.571 | 4.6047 | 7 | 8.078 | 42.2952 | 47.1169 | 43.0537 | 14.9743 |  |  | -0.37959 | -0.041309 | 0.036676 | -0.081482 | 0.07376 | 0.079052 | 0.45988 | -0.11253 | 0.10101 | -1.5735 | -0.17775 | 8.9038 | -0.00050269 | 1.975 | 15.8189 | 16.7062 | 17.2368 | 17.5544 | 17.4935 | 16.4385 | 14.7904 | 16.8117 | 17.1507 | 17.4384 | 17.4809 | 17.1851 | 16.3618 | 14.5519 | 14.2648 | 11.0207 | 9.9342 | 7.7475 | 7.1487 | 12.0958 | 9.6774 | 15.9169 | 15.5335 | 15.3758 | 14.3005 | 14.3569 | 14.7044 |  |  |  | 19.3966 | 82.7393 | 70.2755 | 24.6177 | 0.06792 | -0.011832 | 23.8298 |  |  | 10.7932 |  |  | 16.8705 | 16.1309 | 18.194 | 16.337 | 15.636 | 15.857 | 70.1953 | 84.897 | 56.8033 | 57.3611 | 32.2216 |  | 21.9187 | 37.1937 | 22.4833 | 22.2395 | 20.433 | 60.153 |  | 35.2087 |  |  | 12.9303 | 14.2044 | 24.9497 | [6 empty] | 21.1908 |  |  | 18.8689 |  |  | 12.1018 | 19.1869 | 90.5167 | 8.4315 | 16.2946 | 64.0172 | 9.3024 | 14.8092 | 68.089 | 14.0946 | 60.4381 | 9.5736 | 52.1133 | 10.251 | 52.6709 | 9.5872 | 17.7987 | 62.0699 | 13.9553 | 17.4133 | 80.4503 | 9.9826 | 15.6901 | 70.2156 | 10.2987 | 50.6596 | 13.3118 | 61.4537 | 10.9952 | 56.0156 | 0.085887 | 20.0697 | 0.5855 | 0.05628 | -37.8621 | 3.1224 | 41.2 | 49.35 | -0.80715 | -0.23701 | 0.22333 | -0.33287 | 0.31731 | 0.32849 | 0.7923 | 0.14362 | 0.024487 | 0.37104 | 0.13437 | 0.33427 | 0.14523 | 0.27027
42810.4435 | 296 | 18.487 | 18.5752 | 18.5683 | 18.567 | 17.8653 | 16.4743 | 14.5212 | 16.639 | 17.1285 | 17.2177 | 17.2347 | 16.7489 | 15.7731 | 14.3936 | 14.8723 | 14.8866 | 15.4436 | 13.3132 | 13.5823 | 14.4763 |  |  |  | 16.5434 | 15.906 | 16.9938 | 74.2719 | 71.8042 | 80.2672 | 17.157 | 16.294 | 16.3097 | 16.8286 | 16.1159 | 16.5347 | 20.6571 | 71.8453 |  | 39.464 | 62.4582 | 64.6199 | 30.1626 |  | 6.6658 | 6.8622 | 6.1956 | 6.5311 | 6.6627 | 7.9205 | 23.2397 | 5.0456 | 6.5827 | 4.683 | 7.0026 | 8.0688 | 42.3014 | 47.1098 | 43.0442 | 14.9686 |  |  | -0.36382 | -0.16222 | -0.026404 | -0.13142 | 0.6586 | 0.12176 | 0.4612 | 0.00378 | -0.2374 | -0.15333 | -0.39969 | 8.9036 | -0.00047641 | 1.9895 | 15.8242 | 16.7057 | 17.229 | 17.5563 | 17.4853 | 16.4376 | 14.794 | 16.8113 | 17.1477 | 17.4364 | 17.4785 | 17.1886 | 16.3575 | 14.5502 | 15.3751 | 11.5295 | 11.4263 | 8.7555 | 7.8211 | 12.1156 | 9.6916 | 15.919 | 15.5234 | 15.3857 | 14.3001 | 14.3592 | 14.7202 |  |  |  | 19.4458 | 82.798 | 70.3746 | 24.9915 | 0.15058 | -0.1383 | 23.8709 |  |  | 10.7943 |  |  | 16.879 | 16.1309 | 18.2126 | 16.3385 | 15.6331 | 15.8663 | 70.261 | 85.1323 | 56.8061 | 57.3929 | 30.8782 |  | 21.9688 | 38.31 | 22.5539 | 22.3403 | 20.481 | 60.7621 |  | 35.31 |  |  | 12.925 | 14.2283 | 24.8667 | [6 empty] | 21.1801 |  |  | 18.8861 |  |  | 12.1267 | 19.2252 | 90.5202 | 8.427 | 16.2417 | 64.0136 | 9.313 | 14.8513 | 68.0499 | 14.1181 | 60.3946 | 9.5864 | 52.1333 | 10.2686 | 52.6719 | 9.6024 | 17.7684 | 62.1815 | 13.9651 | 17.4519 | 80.3468 | 9.9905 | 15.772 | 70.1884 | 10.2727 | 50.6275 | 13.3194 | 61.5974 | 11.0125 | 56.0499 | 0.27444 | 20.0692 | 0.58779 | 0.056657 | -37.8609 | 3.1224 | 61.69 | 48.65 | -0.79024 | -0.46969 | -0.18949 | -0.42276 | 0.94817 | 0.40769 | 0.79345 | 0.18262 | -0.0041474 | 0.36985 | 0.013303 | 0.17012 | 0.15846 | 0.26153
42810.4435 | 297 | 18.4894 | 18.5731 | 18.5704 | 18.568 | 17.8617 | 16.4724 | 14.5316 | 16.6398 | 17.1325 | 17.2237 | 17.2316 | 16.7542 | 15.7725 | 14.4017 | 14.8761 | 14.8753 | 15.44 | 13.3114 | 13.5844 | 14.4799 |  |  |  | 16.5458 | 15.901 | 17.0019 | 74.3545 | 71.7896 | 80.512 | 17.1478 | 16.2932 | 16.319 | 16.824 | 16.1203 | 16.5396 | 20.6994 | 71.8744 |  | 39.5356 | 62.5162 | 64.6527 | 30.1656 |  | 6.6665 | 6.8555 | 6.2056 | 6.5303 | 6.6596 | 7.8979 | 23.0249 | 5.1755 | 6.574 | 4.7014 | 6.9912 | 8.0696 | 42.3114 | 47.0827 | 43.0363 | 14.9814 |  |  | -0.5097 | -0.13331 | -0.012608 | -0.14654 | 0.69868 | 0.1441 | 0.63205 | -0.23278 | -0.31115 | 0.047032 | -0.17318 | 8.9032 | -0.00049284 | 1.9644 | 15.8251 | 16.6987 | 17.2289 | 17.5474 | 17.4895 | 16.436 | 14.7862 | 16.8129 | 17.1413 | 17.4345 | 17.4675 | 17.1885 | 16.3527 | 14.5536 | 16.9252 | 11.8689 | 12.6662 | 9.4992 | 8.182 | 12.1702 | 9.7263 | 15.9087 | 15.5219 | 15.3804 | 14.2991 | 14.3566 | 14.7084 |  |  |  | 19.4911 | 82.8417 | 70.4778 | 25.4571 | 0.26404 | -0.085606 | 23.9165 |  |  | 10.7975 |  |  | 16.8775 | 16.1258 | 18.2358 | 16.3406 | 15.6331 | 15.8717 | 70.3709 | 85.2158 | 56.8076 | 57.4301 | 30.4035 |  | 22.0081 | 37.0298 | 22.6102 | 22.5269 | 20.515 | 61.1076 |  | 35.3939 |  |  | 12.9334 | 14.2415 | 24.8772 | [6 empty] | 21.2582 |  |  | 18.9136 |  |  | 12.1476 | 19.2481 | 90.4917 | 8.4156 | 16.1901 | 64.0316 | 9.3244 | 14.9532 | 68.0194 | 14.1362 | 60.464 | 9.6052 | 52.1395 | 10.2847 | 52.6928 | 9.6186 | 17.708 | 62.27 | 13.967 | 17.4825 | 80.3343 | 9.9936 | 15.8618 | 70.199 | 10.2499 | 50.6147 | 13.3208 | 61.6983 | 11.0192 | 56.1436 | 0.49112 | 20.068 | 0.58728 | 0.057402 | -37.8916 | 3.1223 | 51.22 | 50.34 | -0.93566 | -0.42577 | -0.13094 | -0.4464 | 0.97655 | 0.4435 | 0.92882 | 0.19713 | 0.033307 | 0.3658 | -0.15256 | 0.036398 | 0.1598 | 0.25012
42810.4435 | 298 | 18.4968 | 18.5774 | 18.5695 | 18.5667 | 17.8653 | 16.4712 | 14.529 | 16.6405 | 17.1404 | 17.2267 | 17.2349 | 16.7565 | 15.779 | 14.4025 | 14.8771 | 14.8717 | 15.4433 | 13.3129 | 13.5856 | 14.4856 |  |  |  | 16.5456 | 15.9092 | 17.0196 | 74.5016 | 71.8096 | 81.2215 | 17.1518 | 16.2924 | 16.3293 | 16.8236 | 16.1239 | 16.5484 | 20.7528 | 71.7475 |  | 39.6017 | 62.5734 | 64.7016 | 31.3568 |  | 6.6686 | 6.8743 | 6.2202 | 6.5392 | 6.677 | 7.9176 | 22.6479 | 5.3174 | 6.5821 | 4.7408 | 6.9913 | 8.0685 | 42.3219 | 47.0485 | 43.0281 | 14.9849 |  |  | -0.52679 | -0.093221 | 0.15299 | -0.3739 | -0.072776 | 0.3189 | 0.65767 | -0.29915 | -0.18622 | -0.21354 | -0.17059 | 8.9032 | -0.00046327 | 1.8531 | 15.8232 | 16.6918 | 17.2257 | 17.5349 | 17.4886 | 16.4329 | 14.7791 | 16.8005 | 17.1336 | 17.4255 | 17.4751 | 17.1917 | 16.3553 | 14.5567 | 18.7582 | 12.3869 | 14.1821 | 10.0928 | 8.6977 | 12.2177 | 9.7644 | 15.9112 | 15.5267 | 15.3807 | 14.2922 | 14.3664 | 14.7214 |  |  |  | 19.5381 | 82.8537 | 70.4626 | 25.6562 | -0.089703 | -0.124 | 23.9261 |  |  | 10.799 |  |  | 16.8734 | 16.1333 | 18.2489 | 16.3284 | 15.6269 | 15.8813 | 70.432 | 85.3866 | 56.8575 | 57.4812 | 31.3752 |  | 22.0629 | 35.2546 | 22.643 | 22.6039 | 20.568 | 61.413 |  | 35.4673 |  |  | 12.9542 | 14.256 | 25.006 | [6 empty] | 21.376 |  |  | 18.9435 |  |  | 12.1632 | 19.2777 | 90.4196 | 8.4216 | 16.1963 | 64.1365 | 9.3413 | 15.0272 | 68.0466 | 14.1575 | 60.5506 | 9.6239 | 52.1663 | 10.2957 | 52.7259 | 9.6281 | 17.7276 | 62.3354 | 13.9734 | 17.5195 | 80.4182 | 9.9991 | 15.9266 | 70.2558 | 10.2545 | 50.654 | 13.3171 | 61.801 | 11.0244 | 56.2655 | 0.239 | 20.064 | 0.58764 | 0.057236 | -37.8648 | 3.1224 | 54.23 | 49.03 | -0.95217 | -0.35606 | 0.45614 | -0.71309 | -0.31519 | 0.65978 | 0.9475 | 0.17197 | 0.08372 | 0.36544 | -0.3507 | -0.12761 | 0.1285 | 0.24616
42810.4435 | 299 | 18.4974 | 18.5813 | 18.5717 | 18.5676 | 17.8704 | 16.4754 | 14.5271 | 16.6407 | 17.1418 | 17.2357 | 17.2344 | 16.7578 | 15.7834 | 14.4017 | 14.8771 | 14.8795 | 15.4405 | 13.315 | 13.5811 | 14.4919 |  |  |  | 16.5464 | 15.913 | 17.037 | 74.6892 | 71.8403 | 81.9606 | 17.1498 | 16.2875 | 16.3417 | 16.8233 | 16.1257 | 16.5576 | 20.8253 | 71.8282 |  | 39.6636 | 62.6294 | 64.7473 | 32.8823 |  | 6.6716 | 6.8701 | 6.2248 | 6.5428 | 6.7327 | 7.9733 | 22.4539 | 5.3971 | 6.5761 | 4.8488 | 6.9959 | 8.0686 | 42.3357 | 47.0281 | 43.0178 | 14.9928 |  |  | -0.55833 | -0.075481 | 0.020908 | 0.074254 | 0.042876 | 0.22033 | 0.4934 | -0.33989 | -0.67914 | -0.20662 | -0.043027 | 8.9037 | -0.00045177 | 1.8008 | 15.8197 | 16.7028 | 17.2239 | 17.5442 | 17.4905 | 16.4472 | 14.7741 | 16.8121 | 17.1479 | 17.425 | 17.4794 | 17.1931 | 16.36 | 14.5526 | 17.6125 | 11.6974 | 14.2157 | 10.6471 | 9.4107 | 12.2337 | 9.7913 | 15.9124 | 15.525 | 15.3811 | 14.2884 | 14.3644 | 14.7255 |  |  |  | 19.5889 | 82.9146 | 70.8081 | 25.6196 | -0.2846 | -0.096145 | 23.864 |  |  | 10.796 |  |  | 16.8691 | 16.1276 | 18.2741 | 16.3348 | 15.6347 | 15.8844 | 70.5488 | 85.5167 | 56.9305 | 57.5691 | 31.8721 |  | 22.1208 | 33.8277 | 22.6681 | 22.4797 | 20.5992 | 61.589 |  | 35.537 |  |  | 12.9701 | 14.2733 | 25.0871 | [6 empty] | 21.4207 |  |  | 19.0003 |  |  | 12.1806 | 19.2969 | 90.5215 | 8.4389 | 16.2961 | 64.2327 | 9.3471 | 15.0273 | 68.1373 | 14.1655 | 60.531 | 9.6409 | 52.2293 | 10.3094 | 52.7857 | 9.6285 | 17.7943 | 62.4039 | 13.987 | 17.5595 | 80.5459 | 10.0136 | 15.9397 | 70.3224 | 10.2691 | 50.7222 | 13.3203 | 61.9548 | 11.0407 | 56.3898 | 0.22745 | 20.0666 | 0.58808 | 0.057373 | -37.8433 | 3.1224 | 38.57 | 48.99 | -0.98128 | -0.32039 | 0.16862 | 0.31778 | 0.24195 | 0.54847 | 0.82075 | 0.16012 | 0.1242 | 0.36994 | -0.22156 | -0.12821 | 0.088556 | 0.24888
42810.4435 | 300 | 18.4976 | 18.5841 | 18.5765 | 18.5681 | 17.8753 | 16.4824 | 14.5315 | 16.6478 | 17.141 | 17.2358 | 17.2353 | 16.7618 | 15.7875 | 14.4078 | 14.8839 | 14.8847 | 15.4513 | 13.3179 | 13.5892 | 14.5033 |  |  |  | 16.5523 | 15.9128 | 17.0537 | 74.862 | 71.8931 | 82.1983 | 17.1547 | 16.2862 | 16.3464 | 16.8187 | 16.1212 | 16.5651 | 20.8963 | 72.2062 |  | 39.7416 | 62.6688 | 64.8262 | 34.0057 |  | 6.6723 | 6.878 | 6.2337 | 6.558 | 6.7511 | 7.9599 | 23.0865 | 5.4457 | 6.572 | 4.9504 | 6.9906 | 8.0838 | 42.3576 | 47.0272 | 43.0231 | 14.9939 |  |  | -0.47948 | 0.050027 | 0.16679 | -0.20042 | -0.064232 | 0.50355 | 0.58868 | -0.015936 | -0.39522 | -0.042762 | -0.17516 | 8.9035 | -0.00045669 | 1.7886 | 15.8172 | 16.7012 | 17.2196 | 17.5437 | 17.4856 | 16.4405 | 14.7798 | 16.8036 | 17.1368 | 17.4342 | 17.4666 | 17.1838 | 16.3595 | 14.5528 | 16.2311 | 11.1214 | 13.1494 | 10.1733 | 9.396 | 12.2374 | 9.7971 | 15.9066 | 15.5181 | 15.3718 | 14.28 | 14.3568 | 14.7268 |  |  |  | 19.6319 | 83.1165 | 71.1568 | 25.5275 | -0.025681 | -0.29338 | 23.8124 |  |  | 10.8137 |  |  | 16.8761 | 16.1403 | 18.2981 | 16.3455 | 15.6384 | 15.9033 | 70.5835 | 85.8167 | 57.0219 | 57.6392 | 30.4835 |  | 22.16 | 33.4569 | 22.7238 | 22.4142 | 20.6451 | 61.3515 |  | 35.6191 |  |  | 12.9627 | 14.2823 | 24.977 | [6 empty] | 21.4552 |  |  | 19.0441 |  |  | 12.2013 | 19.3324 | 90.6817 | 8.4467 | 16.3222 | 64.3294 | 9.3665 | 15.0178 | 68.1847 | 14.1833 | 60.3705 | 9.6667 | 52.323 | 10.3201 | 52.9208 | 9.6314 | 17.779 | 62.4833 | 13.9975 | 17.6451 | 80.7516 | 10.0284 | 15.9476 | 70.3857 | 10.2756 | 50.7949 | 13.3273 | 62.0517 | 11.0564 | 56.4835 | 0.16524 | 20.0644 | 0.58751 | 0.056903 | -37.9091 | 3.1224 | 56.07 | 50.37 | -0.90966 | 0.26084 | 0.47627 | -0.52208 | -0.29613 | 0.82914 | 0.89649 | 0.20001 | 0.13638 | 0.3733 | -0.067634 | -0.0090554 | 0.059732 | 0.25287
42810.4435 | 301 | 18.5003 | 18.5764 | 18.5605 | 18.5663 | 17.871 | 16.4768 | 14.5333 | 16.648 | 17.1334 | 17.2274 | 17.2378 | 16.7593 | 15.776 | 14.4055 | 14.8772 | 14.8814 | 15.4419 | 13.3139 | 13.5818 | 14.5022 |  |  |  | 16.5534 | 15.9044 | 17.0637 | 74.8994 | 71.9587 | 81.7981 | 17.1453 | 16.2834 | 16.3493 | 16.8178 | 16.1196 | 16.5727 | 20.9468 | 72.4008 |  | 39.8165 | 62.7047 | 64.8976 | 33.99 |  | 6.6752 | 6.8863 | 6.2437 | 6.5758 | 6.7617 | 8.0601 | 23.8859 | 5.4334 | 6.5804 | 5.1155 | 6.9999 | 8.0777 | 42.368 | 47.0094 | 43.0221 | 14.9874 |  |  | -0.49722 | -0.2713 | 0.10042 | -0.12354 | -0.057004 | -0.092456 | 0.55254 | 0.01232 | -0.39891 | -0.30879 | -0.24451 | 8.903 | -0.00048134 | 1.8114 | 15.8155 | 16.6968 | 17.2166 | 17.5411 | 17.4858 | 16.4348 | 14.7741 | 16.7998 | 17.1352 | 17.4333 | 17.4688 | 17.1785 | 16.3505 | 14.5487 | 16.7199 | 10.7745 | 12.125 | 9.5985 | 8.9573 | 12.2648 | 9.7902 | 15.9128 | 15.5218 | 15.3822 | 14.2925 | 14.3728 | 14.7285 |  |  |  | 19.6829 | 83.3233 | 71.1113 | 25.4868 | -0.19911 | -0.098592 | 23.9432 |  |  | 10.8144 |  |  | 16.8784 | 16.1405 | 18.314 | 16.3491 | 15.6356 | 15.9136 | 70.5285 | 85.898 | 57.1035 | 57.7303 | 29.6393 |  | 22.188 | 33.82 | 22.7717 | 22.6099 | 20.6928 | 60.9521 |  | 35.6915 |  |  | 12.9674 | 14.2785 | 24.7882 | [6 empty] | 21.4664 |  |  | 19.0832 |  |  | 12.2103 | 19.3497 | 90.8544 | 8.4214 | 16.2659 | 64.3715 | 9.385 | 15.039 | 68.2061 | 14.1927 | 60.314 | 9.6607 | 52.365 | 10.326 | 53.0745 | 9.6493 | 17.7486 | 62.6145 | 14.0358 | 17.7583 | 80.8864 | 10.0569 | 15.9948 | 70.4036 | 10.3065 | 50.8405 | 13.347 | 62.1323 | 11.066 | 56.5849 | 0.16582 | 20.0641 | 0.5878 | 0.056223 | -37.9176 | 3.1223 | 55.02 | 48.76 | -0.92581 | -0.60744 | 0.36955 | -0.4099 | -0.27902 | -0.35534 | 0.86869 | 0.2244 | 0.1279 | 0.36946 | -0.11875 | 0.10396 | 0.061863 | 0.25571
42810.4435 | 302 | 18.4904 | 18.5781 | 18.5568 | 18.5676 | 17.8631 | 16.4684 | 14.5311 | 16.642 | 17.1359 | 17.2317 | 17.2296 | 16.7592 | 15.7729 | 14.3978 | 14.8886 | 14.8856 | 15.4519 | 13.3172 | 13.5932 | 14.5218 |  |  |  | 16.5559 | 15.9123 | 17.086 | 74.9731 | 71.9751 | 82.1343 | 17.1552 | 16.2933 | 16.36 | 16.8217 | 16.1194 | 16.5902 | 20.9939 | 72.5067 |  | 39.8942 | 62.7571 | 64.9603 | 33.4557 |  | 6.693 | 6.8852 | 6.2468 | 6.5793 | 6.7577 | 8.0548 | 23.9682 | 5.3931 | 6.5823 | 5.1552 | 6.9975 | 8.0837 | 42.3779 | 47.0066 | 43.0205 | 14.9843 |  |  | -0.43873 | -0.069565 | -0.034948 | 0.29833 | -0.084604 | -0.017544 | 0.73061 | -0.32806 | -0.29519 | -0.29914 | 0.137 | 8.9035 | -0.00047148 | 1.8551 | 15.812 | 16.6974 | 17.2225 | 17.5409 | 17.4902 | 16.4374 | 14.7796 | 16.8024 | 17.1386 | 17.4327 | 17.4744 | 17.1808 | 16.3569 | 14.5506 | 16.9032 | 10.5321 | 11.5852 | 9.1468 | 8.6016 | 12.2763 | 9.7934 | 15.9141 | 15.5318 | 15.3889 | 14.293 | 14.3747 | 14.739 |  |  |  | 19.7342 | 83.4544 | 70.9954 | 25.8869 | -0.16102 | -0.17914 | 24.1355 |  |  | 10.8137 |  |  | 16.878 | 16.1387 | 18.3385 | 16.3476 | 15.6386 | 15.9217 | 70.5446 | 85.9379 | 57.1661 | 57.795 | 30.6425 |  | 22.2313 | 33.7483 | 22.8138 | 23.0567 | 20.7459 | 60.6674 |  | 35.7803 |  |  | 12.9994 | 14.2818 | 25.2748 | [6 empty] | 21.6223 |  |  | 19.1373 |  |  | 12.2142 | 19.5563 | 91.1057 | 8.4192 | 16.2144 | 64.3305 | 9.3745 | 15.2139 | 68.3434 | 14.1914 | 60.2998 | 9.6638 | 52.3699 | 10.3365 | 53.1817 | 9.6694 | 17.7107 | 62.7226 | 14.0578 | 17.8542 | 80.9964 | 10.0612 | 16.0837 | 70.4539 | 10.3167 | 50.8863 | 13.3504 | 62.1971 | 11.0681 | 56.6054 | 0.40021 | 20.0624 | 0.58997 | 0.058264 | -37.9022 | 3.1224 | 47.71 | 49.28 | -0.87007 | -0.30759 | -0.21801 | 0.63697 | -0.33992 | -0.15479 | 0.9989 | 0.19799 | 0.13131 | 0.35883 | -0.13779 | 0.16431 | 0.078283 | 0.24631
42810.4435 | 303 | 18.5077 | 18.5863 | 18.5659 | 18.5729 | 17.8736 | 16.4826 | 14.5325 | 16.6376 | 17.137 | 17.2311 | 17.2413 | 16.7599 | 15.784 | 14.4084 | 14.8765 | 14.8836 | 15.44 | 13.3085 | 13.5851 | 14.5107 |  |  |  | 16.5426 | 15.9063 | 17.0839 | 75.056 | 72.0462 | 82.5522 | 17.1573 | 16.2955 | 16.3736 | 16.8245 | 16.1212 | 16.6021 | 21.0491 | 72.3007 |  | 39.9864 | 62.7983 | 65.0195 | 32.9979 |  | 6.7063 | 6.8922 | 6.2539 | 6.5806 | 6.8456 | 8.2339 | 24.5527 | 5.4171 | 6.5773 | 5.1873 | 6.9992 | 8.0832 | 42.4013 | 46.9928 | 43.016 | 14.9788 |  |  | -0.5787 | -0.17602 | 0.005136 | -0.23985 | -0.034004 | 0.10205 | 0.51048 | 0.063576 | -0.15216 | -0.59496 | -0.38261 | 8.9035 | -0.00043862 | 1.806 | 15.8093 | 16.6944 | 17.2169 | 17.5365 | 17.4854 | 16.4367 | 14.771 | 16.7979 | 17.1308 | 17.4257 | 17.4633 | 17.177 | 16.3469 | 14.5414 | 17.1407 | 10.2908 | 10.9539 | 8.7563 | 8.5066 | 12.289 | 9.7931 | 15.9074 | 15.5303 | 15.381 | 14.2939 | 14.3698 | 14.7408 |  |  |  | 19.7789 | 83.4871 | 71.1271 | 26.4375 | -0.18857 | -0.087488 | 24.0873 |  |  | 10.8121 |  |  | 16.8864 | 16.1447 | 18.3596 | 16.3421 | 15.6345 | 15.9376 | 70.5741 | 86.0152 | 57.2419 | 57.8282 | 32.089 |  | 22.3014 | 33.2419 | 22.8661 | 23.393 | 20.7957 | 60.8827 |  | 35.8714 |  |  | 12.9778 | 14.2754 | 25.5119 | [6 empty] | 21.6174 |  |  | 19.1537 |  |  | 12.2389 | 19.8138 | 91.3925 | 8.427 | 16.2496 | 64.3318 | 9.3967 | 15.2782 | 68.626 | 14.2093 | 60.2991 | 9.6814 | 52.4587 | 10.3481 | 53.271 | 9.6544 | 17.65 | 62.772 | 14.0787 | 17.9362 | 81.095 | 10.0726 | 16.0902 | 70.3807 | 10.3414 | 50.9826 | 13.358 | 62.2954 | 11.0618 | 56.6362 | 0.33049 | 20.0618 | 0.59026 | 0.060261 | -37.8912 | 3.1223 | 55.66 | 50.04 | -0.99986 | -0.48928 | 0.083578 | -0.57114 | -0.21557 | 0.37345 | 0.83523 | 0.16017 | 0.14714 | 0.35116 | -0.16269 | 0.23442 | 0.092856 | 0.23252
42810.4436 | 304 | 18.5001 | 18.579 | 18.5623 | 18.565 | 17.8654 | 16.4706 | 14.5238 | 16.6439 | 17.1369 | 17.2267 | 17.2332 | 16.7529 | 15.7778 | 14.4 | 14.879 | 14.883 | 15.446 | 13.3136 | 13.5958 | 14.5293 |  |  |  | 16.541 | 15.9112 | 17.1041 | 75.2253 | 72.1444 | 82.9827 | 17.1594 | 16.3025 | 16.3859 | 16.8219 | 16.1317 | 16.6139 | 21.109 | 73.085 |  | 40.0886 | 62.8628 | 65.0978 | 32.7815 |  | 6.7204 | 6.8982 | 6.2596 | 6.5885 | 7.0302 | 8.5211 | 25.4009 | 5.4086 | 6.5793 | 5.2267 | 6.9991 | 8.0794 | 42.4025 | 46.9687 | 43.0144 | 14.9675 |  |  | -0.36251 | -0.25422 | -0.03232 | -0.085426 | -0.019548 | -0.21665 | 0.56174 | -0.26038 | -0.68361 | 0.51573 | -0.3375 | 8.9026 | -0.00046819 | 1.7679 | 15.8155 | 16.6903 | 17.2226 | 17.5392 | 17.4815 | 16.436 | 14.7725 | 16.8031 | 17.1354 | 17.421 | 17.4654 | 17.1846 | 16.3553 | 14.5489 | 15.9762 | 10.2327 | 10.5276 | 8.4677 | 8.3312 | 12.2932 | 9.7878 | 15.9004 | 15.512 | 15.3707 | 14.2847 | 14.3631 | 14.7384 |  |  |  | 19.8133 | 83.561 | 71.4405 | 26.7246 | -0.13711 | -0.10781 | 24.0658 |  |  | 10.8074 |  |  | 16.8706 | 16.1353 | 18.3738 | 16.3266 | 15.6352 | 15.9398 | 70.5441 | 86.0618 | 57.2913 | 57.8669 | 32.4399 |  | 22.3544 | 33.9498 | 22.9037 | 23.488 | 20.8383 | 61.2509 |  | 35.9367 |  |  | 12.9936 | 14.2761 | 25.7442 | [6 empty] | 21.539 |  |  | 19.1981 |  |  | 12.2493 | 19.905 | 91.5603 | 8.4252 | 16.3183 | 64.4282 | 9.4206 | 15.2668 | 68.7966 | 14.2323 | 60.2883 | 9.6493 | 52.5769 | 10.3636 | 53.2872 | 9.6431 | 17.6064 | 62.8372 | 14.0891 | 18.004 | 81.2239 | 10.0919 | 16.0972 | 70.4541 | 10.3603 | 51.0865 | 13.3946 | 62.4607 | 11.0715 | 56.693 | 0.29678 | 20.0609 | 0.59094 | 0.058314 | -37.9121 | 3.1223 | 72.64 | 48.88 | -0.79183 | -0.58801 | -0.20966 | -0.34086 | -0.16353 | -0.5444 | 0.87661 | 0.1522 | 0.12874 | 0.34994 | -0.03281 | 0.28117 | 0.10088 | 0.22569
42810.4436 | 305 | 18.503 | 18.5856 | 18.5705 | 18.5724 | 17.8746 | 16.4786 | 14.5273 | 16.6465 | 17.136 | 17.2297 | 17.2398 | 16.7573 | 15.7837 | 14.4085 | 14.8804 | 14.8827 | 15.4398 | 13.3136 | 13.5919 | 14.5297 |  |  |  | 16.5399 | 15.9086 | 17.1196 | 75.3757 | 72.2256 | 82.9907 | 17.1592 | 16.3002 | 16.3937 | 16.8258 | 16.1322 | 16.627 | 21.154 | 74.0659 |  | 40.197 | 63.0005 | 65.1486 | 32.2083 |  | 6.7357 | 6.9132 | 6.2668 | 6.5914 | 7.032 | 8.6472 | 25.7493 | 5.2133 | 6.5859 | 5.3149 | 7.0029 | 8.0845 | 42.4266 | 46.9478 | 43.0114 | 14.9672 |  |  | -0.3198 | 0.005343 | -0.013264 | 0.033514 | -0.063576 | -0.26265 | 0.60116 | -0.013964 | -0.22981 | -1.8445 | -0.38062 | 8.9022 | -0.00050762 | 1.7675 | 15.817 | 16.6878 | 17.2194 | 17.5347 | 17.4855 | 16.4282 | 14.7743 | 16.8005 | 17.1413 | 17.4302 | 17.4716 | 17.1816 | 16.3504 | 14.5435 | 15.4752 | 10.0735 | 10.4241 | 8.2695 | 8.1543 | 12.2967 | 9.7882 | 15.9013 | 15.5183 | 15.373 | 14.2895 | 14.3706 | 14.7541 |  |  |  | 19.8657 | 83.5859 | 71.4722 | 26.7668 | -0.14238 | -0.13586 | 24.2106 |  |  | 10.8158 |  |  | 16.8819 | 16.1436 | 18.4007 | 16.3415 | 15.6459 | 15.96 | 70.675 | 86.1387 | 57.3554 | 57.923 | 31.9112 |  | 22.4086 | 35.6951 | 22.9806 | 23.6576 | 20.8887 | 61.4905 |  | 36.0272 |  |  | 13.0077 | 14.291 | 25.6943 | [6 empty] | 21.502 |  |  | 19.2593 |  |  | 12.2798 | 19.8997 | 91.8373 | 8.4507 | 16.3094 | 64.5676 | 9.4335 | 15.267 | 68.8945 | 14.2566 | 60.249 | 9.6746 | 52.6691 | 10.3599 | 53.331 | 9.6281 | 17.5668 | 62.9052 | 14.1233 | 18.0375 | 81.2951 | 10.1044 | 16.1138 | 70.6651 | 10.3839 | 51.17 | 13.4236 | 62.7396 | 11.0827 | 56.7914 | 0.24979 | 20.0594 | 0.59161 | 0.05822 | -37.8736 | 3.1224 | 75.8 | 49.73 | -0.74373 | 0.085249 | -0.13432 | 0.21351 | -0.29497 | -0.59955 | 0.90705 | 0.16871 | 0.08285 | 0.34693 | 0.023259 | 0.29271 | 0.11831 | 0.22628
42810.4436 | 306 | 18.5006 | 18.5774 | 18.5667 | 18.5648 | 17.8747 | 16.4776 | 14.5229 | 16.6435 | 17.134 | 17.2216 | 17.2379 | 16.7549 | 15.7827 | 14.4028 | 14.8802 | 14.8636 | 15.4372 | 13.3158 | 13.5914 | 14.5306 |  |  |  | 16.5401 | 15.9094 | 17.1215 | 75.4375 | 72.2653 | 82.6291 | 17.1602 | 16.2996 | 16.4023 | 16.8321 | 16.132 | 16.6346 | 21.1935 | 74.597 |  | 40.3096 | 63.1438 | 65.1704 | 31.8266 |  | 6.7453 | 6.9209 | 6.2699 | 6.5746 | 7.0017 | 8.6211 | 25.6648 | 4.9545 | 6.5863 | 5.3374 | 7.0007 | 8.0815 | 42.4348 | 46.9201 | 43.0054 | 14.9582 |  |  | -0.46371 | -0.24107 | -0.008008 | -0.08411 | -0.12732 | -0.47752 | 0.53085 | -0.32346 | -0.43492 | -0.17682 | -0.3683 | 8.9025 | -0.00044191 | 1.8414 | 15.8228 | 16.6905 | 17.2265 | 17.5395 | 17.4896 | 16.4484 | 14.7846 | 16.803 | 17.1414 | 17.4367 | 17.4773 | 17.1853 | 16.3636 | 14.5454 | 14.9918 | 10.306 | 10.0733 | 8.2028 | 7.9734 | 12.2924 | 9.7837 | 15.8953 | 15.5173 | 15.3734 | 14.2897 | 14.3698 | 14.7667 |  |  |  | 19.9043 | 83.5752 | 71.8212 | 26.6662 | -0.076939 | -0.1686 | 24.2733 |  |  | 10.814 |  |  | 16.8808 | 16.1466 | 18.4186 | 16.3381 | 15.6507 | 15.9624 | 70.7464 | 86.2725 | 57.4469 | 57.986 | 31.5701 |  | 22.4753 | 36.1561 | 23.0467 | 23.8574 | 20.9409 | 61.9321 |  | 36.129 |  |  | 13.0081 | 14.3172 | 25.9309 | [6 empty] | 21.5285 |  |  | 19.3077 |  |  | 12.295 | 19.901 | 92.3659 | 8.4581 | 16.286 | 64.7422 | 9.4568 | 15.236 | 69.0922 | 14.2717 | 60.3208 | 9.6354 | 52.72 | 10.3691 | 53.3832 | 9.6038 | 17.5267 | 62.8942 | 14.1346 | 18.0625 | 81.3646 | 10.1127 | 16.1285 | 70.7316 | 10.385 | 51.1694 | 13.4493 | 62.9205 | 11.0847 | 56.9399 | 0.31893 | 20.0572 | 0.59191 | 0.056874 | -37.9059 | 3.1224 | 80.58 | 49.75 | -0.89511 | -0.57263 | -0.10437 | -0.33824 | -0.4174 | -0.80837 | 0.85232 | 0.18043 | 0.072269 | 0.34313 | 0.076476 | 0.33117 | 0.13024 | 0.23036
42810.4436 | 307 | 18.4982 | 18.5777 | 18.5677 | 18.557 | 17.8669 | 16.4704 | 14.5183 | 16.6475 | 17.1406 | 17.2304 | 17.2359 | 16.7549 | 15.7707 | 14.3984 | 14.8926 | 14.8807 | 15.45 | 13.3228 | 13.5983 | 14.5423 |  |  |  | 16.547 | 15.9187 | 17.1511 | 75.4743 | 72.3172 | 82.5426 | 17.1533 | 16.2902 | 16.4114 | 16.8234 | 16.1233 | 16.6449 | 21.2232 | 75.2377 |  | 40.4156 | 63.2607 | 65.1995 | 31.1587 |  | 6.7587 | 6.9309 | 6.2713 | 6.581 | 6.9822 | 8.562 | 25.2184 | 4.8314 | 6.5871 | 5.1526 | 7.0064 | 8.0833 | 42.4561 | 46.9024 | 43.0019 | 14.9494 |  |  | -0.39865 | -0.17273 | -0.044804 | 0.040086 | -0.03992 | -0.62144 | 0.65044 | -0.038932 | -0.80213 | -0.29914 | -0.3381 | 8.9024 | -0.00045505 | 1.9027 | 15.8137 | 16.6858 | 17.2173 | 17.541 | 17.4863 | 16.4293 | 14.7768 | 16.7969 | 17.1355 | 17.4215 | 17.4641 | 17.1771 | 16.3535 | 14.5427 | 14.4506 | 10.3025 | 9.9718 | 8.1111 | 7.7702 | 12.2865 | 9.7797 | 15.896 | 15.5182 | 15.3677 | 14.2862 | 14.3734 | 14.7645 |  |  |  | 19.9502 | 83.6743 | 71.7859 | 26.6909 | 0.12262 | -0.14696 | 24.2632 |  |  | 10.8188 |  |  | 16.8787 | 16.1441 | 18.4425 | 16.3349 | 15.6392 | 15.967 | 70.9653 | 86.4549 | 57.5677 | 58.0534 | 31.9554 |  | 22.5158 | 35.1525 | 23.0878 | 23.9073 | 20.9806 | 62.1399 |  | 36.2268 |  |  | 13.0101 | 14.3091 | 25.987 | [6 empty] | 21.5061 |  |  | 19.345 |  |  | 12.3163 | 19.9141 | 92.7629 | 8.4411 | 16.3223 | 64.8829 | 9.4742 | 15.2323 | 69.3117 | 14.2867 | 60.3308 | 9.5707 | 52.7478 | 10.3818 | 53.4085 | 9.6017 | 17.519 | 62.9103 | 14.1609 | 18.0993 | 81.5025 | 10.1378 | 16.149 | 70.8679 | 10.4088 | 51.2242 | 13.4792 | 62.9728 | 11.1025 | 57.0125 | 0.27078 | 20.0561 | 0.59088 | 0.056816 | -37.8288 | 3.1224 | 91.81 | 49.22 | -0.82985 | -0.48473 | -0.24687 | 0.23351 | -0.2337 | -0.92208 | 0.94335 | 0.17109 | 0.10153 | 0.34307 | 0.13591 | 0.34198 | 0.14978 | 0.23121
42810.4436 | 308 | 18.5011 | 18.5758 | 18.5639 | 18.5616 | 17.8651 | 16.4668 | 14.5219 | 16.6414 | 17.14 | 17.2323 | 17.235 | 16.7532 | 15.7717 | 14.3909 | 14.888 | 14.876 | 15.448 | 13.3125 | 13.6041 | 14.538 |  |  |  | 16.5493 | 15.9187 | 17.1606 | 75.5056 | 72.3782 | 82.5076 | 17.1523 | 16.2942 | 16.4148 | 16.8175 | 16.1284 | 16.6496 | 21.249 | 76.0832 |  | 40.5239 | 63.3368 | 65.2215 | 30.239 |  | 6.771 | 6.9387 | 6.2715 | 6.5782 | 6.9682 | 8.5163 | 24.7984 | 4.7348 | 6.5886 | 4.9396 | 7.0101 | 8.0839 | 42.4712 | 46.9031 | 42.9863 | 14.9445 |  |  | -0.41771 | -0.19179 | 0.12999 | 0.12879 | -0.088548 | -0.48541 | 0.59853 | 0.32182 | 0.25942 | -0.3732 | -0.19424 | 8.9022 | -0.00047476 | 1.8663 | 15.8109 | 16.6919 | 17.2218 | 17.5388 | 17.4902 | 16.4295 | 14.7727 | 16.7944 | 17.1386 | 17.43 | 17.47 | 17.1799 | 16.3492 | 14.5452 | 13.9927 | 10.136 | 9.6933 | 8.109 | 7.6821 | 12.2903 | 9.7882 | 15.9005 | 15.5186 | 15.3753 | 14.2915 | 14.3724 | 14.7667 |  |  |  | 20.0034 | 83.7626 | 71.6977 | 26.731 | 0.19941 | -0.058882 | 24.3328 |  |  | 10.8199 |  |  | 16.8738 | 16.144 | 18.4603 | 16.3328 | 15.6487 | 15.9796 | 71.0762 | 86.618 | 57.6746 | 58.1136 | 32.3003 |  | 22.5756 | 35.6617 | 23.155 | 23.767 | 21.0226 | 62.376 |  | 36.3185 |  |  | 13.014 | 14.3109 | 25.8581 | [6 empty] | 21.428 |  |  | 19.4022 |  |  | 12.3172 | 19.9323 | 92.9096 | 8.4122 | 16.4165 | 65.0216 | 9.4658 | 15.2266 | 69.3971 | 14.2828 | 60.3087 | 9.5208 | 52.7655 | 10.3951 | 53.3992 | 9.5966 | 17.5066 | 62.9805 | 14.1846 | 18.1624 | 81.6465 | 10.1577 | 16.1663 | 70.9384 | 10.4341 | 51.2722 | 13.4934 | 62.8674 | 11.1185 | 57.0955 | 0.32587 | 20.0548 | 0.59046 | 0.057518 | -37.8684 | 3.1224 | 100.07 | 50.35 | -0.84941 | -0.51077 | 0.4205 | 0.41856 | -0.34804 | -0.81487 | 0.90485 | 0.16352 | 0.089651 | 0.34838 | 0.18724 | 0.37392 | 0.1762 | 0.23188
42810.4436 | 309 | 18.505 | 18.5811 | 18.5689 | 18.5724 | 17.8707 | 16.4744 | 14.5322 | 16.6415 | 17.1387 | 17.2347 | 17.245 | 16.7582 | 15.7708 | 14.4075 | 14.8819 | 14.8729 | 15.4406 | 13.3106 | 13.6007 | 14.5406 |  |  |  | 16.5486 | 15.9112 | 17.1695 | 75.5745 | 72.4782 | 82.6675 | 17.1554 | 16.2938 | 16.4346 | 16.8179 | 16.1288 | 16.6659 | 21.2818 | 76.5839 |  | 40.6229 | 63.387 | 65.262 | 29.8156 |  | 6.7816 | 6.9458 | 6.2883 | 6.5886 | 6.9547 | 8.4966 | 24.5272 | 4.6585 | 6.5856 | 4.7456 | 7.005 | 8.084 | 42.4868 | 46.9021 | 42.9876 | 14.9341 |  |  | -0.27446 | -0.20822 | 0.097132 | -0.059142 | -0.10432 | 0.20456 | 0.59328 | 0.1214 | 0.27927 | -0.64824 | -0.40883 | 8.9024 | -0.00048791 | 1.8042 | 15.8096 | 16.6868 | 17.2199 | 17.531 | 17.4784 | 16.4241 | 14.7691 | 16.7987 | 17.136 | 17.4279 | 17.4614 | 17.1732 | 16.3392 | 14.5428 | 13.4546 | 9.8956 | 9.3207 | 8.0363 | 7.8499 | 12.2782 | 9.7739 | 15.9023 | 15.517 | 15.375 | 14.2903 | 14.3717 | 14.7703 |  |  |  | 20.0553 | 83.9332 | 71.7851 | 26.5523 | 0.028413 | -0.094263 | 24.4892 |  |  | 10.8267 |  |  | 16.8754 | 16.1528 | 18.4708 | 16.3276 | 15.6437 | 15.9831 | 71.0773 | 86.8373 | 57.7756 | 58.227 | 32.64 |  | 22.644 | 37.4056 | 23.2403 | 23.5053 | 21.067 | 62.8647 |  | 36.4116 |  |  | 13.0355 | 14.3277 | 25.8395 | [6 empty] | 21.3226 |  |  | 19.4675 |  |  | 12.327 | 19.9579 | 92.9272 | 8.3744 | 16.4873 | 65.1954 | 9.4696 | 15.3131 | 69.4369 | 14.2968 | 60.2996 | 9.5175 | 52.7844 | 10.4142 | 53.4366 | 9.5914 | 17.4861 | 63.051 | 14.1992 | 18.1943 | 81.8425 | 10.1617 | 16.1572 | 70.9744 | 10.4397 | 51.3072 | 13.4984 | 62.7371 | 11.1287 | 57.1309 | 0.34936 | 20.0532 | 0.59152 | 0.056874 | -37.8784 | 3.1224 | 101.12 | 49.01 | -0.68868 | -0.5322 | 0.3635 | -0.28364 | -0.37774 | 0.52897 | 0.90084 | 0.15638 | 0.044083 | 0.35714 | 0.24562 | 0.41365 | 0.18906 | 0.23858
42810.4436 | 310 | 18.5104 | 18.5826 | 18.5814 | 18.5718 | 17.8728 | 16.4843 | 14.5312 | 16.6487 | 17.1427 | 17.2346 | 17.2407 | 16.755 | 15.7839 | 14.3982 | 14.8788 | 14.8721 | 15.4436 | 13.3075 | 13.6041 | 14.5559 |  |  |  | 16.5454 | 15.9046 | 17.1867 | 75.6389 | 72.6128 | 82.4886 | 17.1616 | 16.2993 | 16.4397 | 16.8268 | 16.1321 | 16.6807 | 21.3362 | 76.7788 |  | 40.7297 | 63.4598 | 65.3133 | 31.4177 |  | 6.7888 | 6.9527 | 6.3032 | 6.6082 | 6.9614 | 8.521 | 24.3155 | 4.6449 | 6.5857 | 4.7008 | 7.0048 | 8.093 | 42.4872 | 46.9007 | 42.9735 | 14.9172 |  |  | -0.2462 | -0.22004 | 0.29164 | 0.041398 | 0.007392 | -0.09574 | 0.71156 | 0.007064 | -0.43803 | -0.73447 | -0.52984 | 8.9025 | -0.00047805 | 1.7785 | 15.812 | 16.6893 | 17.2287 | 17.5296 | 17.4853 | 16.4299 | 14.7719 | 16.8025 | 17.1383 | 17.4339 | 17.4675 | 17.1768 | 16.3509 | 14.5452 | 12.9843 | 9.7275 | 8.8537 | 7.9465 | 7.8731 | 12.2728 | 9.7729 | 15.8971 | 15.5148 | 15.3717 | 14.2887 | 14.3727 | 14.7814 |  |  |  | 20.0884 | 84.0057 | 71.7097 | 26.1724 | 0.038543 | -0.079396 | 24.5808 |  |  | 10.8181 |  |  | 16.8707 | 16.1427 | 18.4944 | 16.3344 | 15.6407 | 15.9891 | 71.1459 | 86.8723 | 57.8574 | 58.3368 | 31.8414 |  | 22.6908 | 37.9939 | 23.3009 | 23.4384 | 21.1085 | 63.0182 |  | 36.4901 |  |  | 13.0568 | 14.3364 | 25.6752 | [6 empty] | 21.2508 |  |  | 19.5281 |  |  | 12.345 | 19.992 | 92.9154 | 8.3599 | 16.5208 | 65.4185 | 9.4868 | 15.464 | 69.5096 | 14.3179 | 60.3449 | 9.5135 | 52.8279 | 10.426 | 53.5908 | 9.5952 | 17.4519 | 63.1014 | 14.2185 | 18.2122 | 82.0564 | 10.1652 | 16.1614 | 71.0217 | 10.4442 | 51.3627 | 13.5012 | 62.726 | 11.1322 | 57.1957 | 0.23958 | 20.0533 | 0.59298 | 0.057048 | -37.9416 | 3.1224 | 97.59 | 49.13 | -0.6521 | -0.54712 | 0.62987 | 0.23731 | 0.10056 | -0.3619 | 0.9866 | 0.18014 | 0.029781 | 0.36039 | 0.29725 | 0.46543 | 0.14638 | 0.25024
42810.4436 | 311 | 18.4959 | 18.5819 | 18.5674 | 18.5723 | 17.8765 | 16.4778 | 14.5268 | 16.6436 | 17.141 | 17.2321 | 17.2405 | 16.75 | 15.7803 | 14.3992 | 14.8845 | 14.8736 | 15.4478 | 13.3057 | 13.606 | 14.5626 |  |  |  | 16.5522 | 15.9077 | 17.201 | 75.672 | 72.7417 | 82.2796 | 17.1622 | 16.3027 | 16.4546 | 16.8308 | 16.1322 | 16.6973 | 21.3941 | 76.9824 |  | 40.846 | 63.4952 | 65.391 | 32.0267 |  | 6.8012 | 6.9687 | 6.3122 | 6.637 | 6.9831 | 8.5262 | 24.4296 | 4.607 | 6.596 | 4.6975 | 7.004 | 8.0903 | 42.4984 | 46.9086 | 42.973 | 14.9107 |  |  | -0.31125 | -0.14645 | 0.051136 | -0.13668 | 0.1329 | 0.19208 | 0.33043 | 0.21603 | -0.39386 | -0.57901 | -0.59343 | 8.9024 | -0.00050926 | 1.8289 | 15.8128 | 16.6899 | 17.22 | 17.5326 | 17.4811 | 16.426 | 14.77 | 16.796 | 17.1318 | 17.4275 | 17.4659 | 17.1768 | 16.3467 | 14.5407 | 13.1764 | 9.71 | 8.517 | 7.8103 | 7.7882 | 12.2732 | 9.7701 | 15.8982 | 15.5154 | 15.3722 | 14.2831 | 14.3727 | 14.7868 |  |  |  | 20.1291 | 83.8589 | 71.4839 | 25.8472 | 0.015852 | -0.011079 | 24.629 |  |  | 10.8346 |  |  | 16.8763 | 16.1459 | 18.5281 | 16.3388 | 15.6332 | 16.001 | 71.32 | 86.9743 | 57.9305 | 58.4046 | 31.0143 |  | 22.7469 | 37.9771 | 23.3813 | 23.6532 | 21.1675 | 63.4424 |  | 36.5771 |  |  | 13.0716 | 14.3295 | 25.4513 | [6 empty] | 21.4293 |  |  | 19.5738 |  |  | 12.3767 | 20.0417 | 92.9378 | 8.3687 | 16.5856 | 65.6681 | 9.5167 | 15.5687 | 69.7483 | 14.3487 | 60.375 | 9.5197 | 52.8853 | 10.4499 | 53.7532 | 9.6139 | 17.4389 | 63.2222 | 14.2555 | 18.2377 | 82.164 | 10.1802 | 16.2258 | 71.1471 | 10.4498 | 51.435 | 13.5109 | 62.8433 | 11.1485 | 57.3487 | 0.24401 | 20.0526 | 0.59473 | 0.0583 | -37.9068 | 3.1224 | 88.11 | 50.21 | -0.73299 | -0.44636 | 0.26376 | -0.43121 | 0.42639 | 0.5126 | 0.67233 | 0.205 | 0.032956 | 0.3564 | 0.27594 | 0.50251 | 0.13141 | 0.26064
42810.4436 | 312 | 18.504 | 18.5807 | 18.5647 | 18.5623 | 17.8772 | 16.4752 | 14.527 | 16.6449 | 17.1418 | 17.2335 | 17.2386 | 16.7548 | 15.7827 | 14.3984 | 14.8822 | 14.8698 | 15.44 | 13.3104 | 13.5945 | 14.5625 |  |  |  | 16.5481 | 15.9131 | 17.2166 | 75.686 | 72.843 | 82.1583 | 17.157 | 16.3005 | 16.4603 | 16.8215 | 16.1308 | 16.7021 | 21.4431 | 77.8571 |  | 40.9631 | 63.5203 | 65.4497 | 31.4764 |  | 6.7988 | 6.9665 | 6.3161 | 6.6461 | 6.998 | 8.5389 | 24.6033 | 4.5636 | 6.5825 | 4.6048 | 7.0012 | 8.0955 | 42.5313 | 46.9165 | 42.9636 | 14.9126 |  |  | -0.30994 | -0.10834 | 0.11028 | 0.22539 | 0.23147 | 0.2821 | 0.43031 | 0.17332 | -0.45476 | -0.23976 | -0.38857 | 8.9023 | -0.00047805 | 1.9326 | 15.8182 | 16.7015 | 17.225 | 17.5347 | 17.4764 | 16.434 | 14.7734 | 16.8013 | 17.1326 | 17.4234 | 17.4654 | 17.1832 | 16.3475 | 14.5389 | 14.577 | 9.7195 | 8.5212 | 7.6729 | 7.6995 | 12.3131 | 9.7611 | 15.9009 | 15.5207 | 15.383 | 14.2944 | 14.3868 | 14.7905 |  |  |  | 20.1742 | 83.8024 | 71.606 | 25.9501 | 0.17591 | -0.17726 | 24.6727 |  |  | 10.824 |  |  | 16.8705 | 16.1433 | 18.5447 | 16.3392 | 15.6449 | 16.0124 | 71.4646 | 87.0658 | 58.0117 | 58.4852 | 31.4967 |  | 22.7933 | 39.6648 | 23.4585 | 23.8482 | 21.2289 | 63.1541 |  | 36.6701 |  |  | 13.1066 | 14.3481 | 25.465 | [6 empty] | 21.9391 |  |  | 19.6475 |  |  | 12.3883 | 20.0985 | 93.0647 | 8.3658 | 16.6902 | 65.9022 | 9.5403 | 15.573 | 70.0023 | 14.3683 | 60.3179 | 9.5298 | 52.9586 | 10.4698 | 53.809 | 9.6286 | 17.425 | 63.3598 | 14.2744 | 18.2635 | 82.2299 | 10.1886 | 16.361 | 71.2723 | 10.4558 | 51.4986 | 13.528 | 63.0086 | 11.1636 | 57.51 | 0.52733 | 20.0521 | 0.59517 | 0.058951 | -37.9768 | 3.1224 | 104.18 | 49.23 | -0.73132 | -0.38391 | 0.38733 | 0.55374 | 0.56273 | 0.62123 | 0.76726 | 0.19316 | -0.011322 | 0.35305 | 0.12497 | 0.501 | 0.14834 | 0.25929
42810.4437 | 313 | 18.5053 | 18.5837 | 18.5624 | 18.5635 | 17.8674 | 16.4711 | 14.5279 | 16.6465 | 17.145 | 17.2327 | 17.2392 | 16.7646 | 15.7785 | 14.3892 | 14.8838 | 14.8788 | 15.4426 | 13.3146 | 13.6037 | 14.5703 |  |  |  | 16.5449 | 15.9166 | 17.234 | 75.732 | 72.9052 | 82.2831 | 17.1527 | 16.2958 | 16.471 | 16.816 | 16.1311 | 16.7102 | 21.4966 | 78.5124 |  | 41.0762 | 63.5722 | 65.479 | 31.7062 |  | 6.804 | 6.9689 | 6.3237 | 6.6485 | 7.0005 | 8.5352 | 24.742 | 4.5303 | 6.5861 | 4.5279 | 7.0062 | 8.0882 | 42.5633 | 46.9288 | 42.9625 | 14.8958 |  |  | -0.32308 | -0.047881 | -0.01852 | -0.01117 | 0.25644 | -0.001772 | 0.50654 | 0.47493 | 0.043995 | -0.19759 | -0.52865 | 8.9028 | -0.00048298 | 1.9663 | 15.7881 | 16.6928 | 17.2226 | 17.5352 | 17.4851 | 16.4288 | 14.7741 | 16.8069 | 17.1379 | 17.4271 | 17.467 | 17.1812 | 16.3504 | 14.5433 | 17.5603 | 10.9616 | 8.7679 | 7.6457 | 7.6693 | 12.3602 | 9.7541 | 15.8931 | 15.5185 | 15.3737 | 14.289 | 14.3811 | 14.7995 |  |  |  | 20.2158 | 83.7138 | 71.4757 | 26.1594 | 0.065083 | -0.061328 | 24.6154 |  |  | 10.8269 |  |  | 16.8696 | 16.1471 | 18.5516 | 16.3374 | 15.6453 | 16.0197 | 71.6778 | 87.3353 | 58.0723 | 58.5718 | 32.8662 |  | 22.8493 | 42.0362 | 23.5568 | 23.6204 | 21.2875 | 62.6786 |  | 36.7675 |  |  | 13.1245 | 14.3683 | 25.4938 | [6 empty] | 22.0782 |  |  | 19.7245 |  |  | 12.4017 | 20.1471 | 93.221 | 8.3822 | 16.7806 | 66.0586 | 9.5612 | 15.5607 | 70.1553 | 14.3835 | 60.2405 | 9.5545 | 53.0414 | 10.4835 | 53.9064 | 9.6308 | 17.4151 | 63.5161 | 14.2888 | 18.2871 | 82.3558 | 10.187 | 16.5004 | 71.3785 | 10.4603 | 51.5643 | 13.539 | 63.0771 | 11.1699 | 57.6074 | 0.45876 | 20.0524 | 0.59603 | 0.059052 | -37.9627 | 3.1224 | 89.06 | 48.76 | -0.7468 | -0.25522 | -0.15873 | -0.12327 | 0.5923 | -0.049236 | 0.83244 | 0.15701 | -0.073883 | 0.36134 | -0.20103 | 0.47278 | 0.14375 | 0.25487
42810.4437 | 314 | 18.5081 | 18.5819 | 18.5665 | 18.5697 | 17.8664 | 16.4754 | 14.5286 | 16.6488 | 17.1436 | 17.2325 | 17.2362 | 16.7559 | 15.7754 | 14.3933 | 14.8886 | 14.879 | 15.4435 | 13.3085 | 13.6045 | 14.5717 |  |  |  | 16.5473 | 15.9153 | 17.2427 | 75.8014 | 72.9498 | 82.551 | 17.1585 | 16.2992 | 16.4806 | 16.8222 | 16.1379 | 16.726 | 21.5624 | 78.4904 |  | 41.173 | 63.6464 | 65.5106 | 30.9957 |  | 6.8054 | 6.9705 | 6.3242 | 6.663 | 7.005 | 8.5157 | 24.8124 | 4.5501 | 6.5951 | 4.4892 | 7.0139 | 8.0827 | 42.5873 | 46.9482 | 42.942 | 14.8841 |  |  | -0.54519 | -0.20756 | 0.070848 | -0.02037 | 0.065876 | -0.16474 | 0.52099 | 0.06752 | -1.2816 | -0.053042 | -0.33094 | 8.9035 | -0.00046819 | 1.9103 | 15.8015 | 16.69 | 17.2204 | 17.5374 | 17.4833 | 16.4206 | 14.7717 | 16.7946 | 17.1302 | 17.4287 | 17.4654 | 17.1788 | 16.3509 | 14.5481 | 17.6665 | 11.393 | 10.652 | 8.1235 | 7.6772 | 12.3694 | 9.7895 | 15.8943 | 15.5135 | 15.3697 | 14.2877 | 14.3815 | 14.8008 |  |  |  | 20.2555 | 83.7411 | 71.2822 | 25.9429 | 0.023753 | -0.1686 | 24.8389 |  |  | 10.8421 |  |  | 16.8747 | 16.1563 | 18.5908 | 16.3432 | 15.6476 | 16.041 | 71.8171 | 87.6039 | 58.1413 | 58.704 | 33.3408 |  | 22.8997 | 42.8377 | 23.6381 | 23.4702 | 21.3292 | 63.2829 |  | 36.8694 |  |  | 13.1279 | 14.3887 | 25.5812 | [6 empty] | 21.9284 |  |  | 19.7887 |  |  | 12.4271 | 20.1962 | 93.6604 | 8.4075 | 16.8599 | 66.1355 | 9.5745 | 15.6051 | 70.3532 | 14.3999 | 60.2114 | 9.5865 | 53.1076 | 10.4851 | 54.0136 | 9.6397 | 17.4231 | 63.6208 | 14.3087 | 18.2848 | 82.4794 | 10.2028 | 16.565 | 71.5234 | 10.4666 | 51.6315 | 13.5738 | 63.12 | 11.1918 | 57.6649 | 0.37228 | 20.0514 | 0.59622 | 0.058003 | -37.9358 | 3.1224 | 111.55 | 50.44 | -0.97047 | -0.53139 | 0.31046 | -0.16647 | 0.30019 | -0.47472 | 0.84421 | 0.14552 | -0.09341 | 0.36691 | -0.21176 | 0.26754 | 0.1657 | 0.26222
42810.4437 | 315 | 18.5163 | 18.5859 | 18.5783 | 18.5747 | 17.8733 | 16.4837 | 14.5375 | 16.6571 | 17.1509 | 17.2381 | 17.2412 | 16.767 | 15.7859 | 14.4071 | 14.885 | 14.8815 | 15.4443 | 13.3119 | 13.6118 | 14.5823 |  |  |  | 16.5541 | 15.9207 | 17.2584 | 75.8754 | 73.0027 | 82.6072 | 17.1617 | 16.3014 | 16.4874 | 16.8259 | 16.1374 | 16.7393 | 21.6144 | 78.2782 |  | 41.2656 | 63.736 | 65.5867 | 30.7845 |  | 6.8079 | 6.9797 | 6.3283 | 6.6714 | 6.9997 | 8.5832 | 24.6264 | 4.527 | 6.6017 | 4.4958 | 7.0221 | 8.0895 | 42.6182 | 46.9589 | 42.938 | 14.8761 |  |  | -0.40194 | -0.023569 | 0.00448 | -0.088054 | 0.13619 | 0.16053 | 0.59919 | 0.005092 | -0.49836 | -0.82783 | -0.25365 | 8.9035 | -0.00044684 | 1.8068 | 15.8095 | 16.6943 | 17.2205 | 17.5427 | 17.4861 | 16.4258 | 14.7728 | 16.7968 | 17.1369 | 17.4328 | 17.4749 | 17.1814 | 16.3485 | 14.5431 | 17.2196 | 10.7914 | 11.1123 | 8.89 | 8.3619 | 12.3969 | 9.8027 | 15.8929 | 15.5094 | 15.3647 | 14.2733 | 14.3753 | 14.8021 |  |  |  | 20.2834 | 83.8878 | 71.0371 | 25.7217 | 0.10925 | -0.11158 | 24.9112 |  |  | 10.8305 |  |  | 16.8758 | 16.1518 | 18.6012 | 16.3329 | 15.6383 | 16.0346 | 71.9205 | 87.7599 | 58.1933 | 58.7767 | 33.3552 |  | 22.9419 | 42.9112 | 23.7111 | 23.4019 | 21.3614 | 63.9663 |  | 36.9623 |  |  | 13.1552 | 14.4145 | 25.7408 | [6 empty] | 21.8167 |  |  | 19.8479 |  |  | 12.4388 | 20.2586 | 94.1464 | 8.3986 | 16.8553 | 66.2092 | 9.5831 | 15.8592 | 70.5466 | 14.4302 | 60.2382 | 9.6264 | 53.1927 | 10.4984 | 54.1138 | 9.65 | 17.4761 | 63.7138 | 14.341 | 18.2887 | 82.4659 | 10.21 | 16.5785 | 71.6369 | 10.4781 | 51.6781 | 13.6075 | 63.252 | 11.2204 | 57.74 | 0.20973 | 20.0506 | 0.59496 | 0.058126 | -37.9556 | 3.1225 | 93.95 | 49.1 | -0.83334 | -0.17907 | 0.07807 | -0.34612 | 0.43167 | 0.46867 | 0.90546 | 0.14654 | -0.092988 | 0.36989 | -0.1589 | 0.21792 | 0.17331 | 0.26929
42810.4437 | 316 | 18.5102 | 18.5915 | 18.5704 | 18.5755 | 17.8734 | 16.4756 | 14.5383 | 16.651 | 17.1493 | 17.2423 | 17.2483 | 16.7681 | 15.7871 | 14.4091 | 14.8941 | 14.8927 | 15.4493 | 13.3204 | 13.6176 | 14.5943 |  |  |  | 16.5644 | 15.9273 | 17.2804 | 75.8961 | 73.1327 | 82.6087 | 17.1633 | 16.2923 | 16.4993 | 16.8236 | 16.128 | 16.7469 | 21.6597 | 78.2116 |  | 41.3561 | 63.849 | 65.6573 | 30.4616 |  | 6.7921 | 6.9652 | 6.3384 | 6.6606 | 7.0009 | 8.6128 | 24.4691 | 4.4452 | 6.5956 | 4.4701 | 7.0075 | 8.0863 | 42.6239 | 46.9581 | 42.9232 | 14.8632 |  |  | -0.22517 | 0.008631 | 0.068876 | -0.11368 | 0.1283 | 0.10139 | 0.6511 | 0.20288 | -0.22144 | -0.40907 | -0.19285 | 8.9036 | -0.00046327 | 1.7497 | 15.8012 | 16.6893 | 17.2154 | 17.5362 | 17.485 | 16.4324 | 14.7721 | 16.8029 | 17.1355 | 17.4267 | 17.4727 | 17.1849 | 16.348 | 14.5463 | 17.7864 | 10.6959 | 10.6952 | 8.8276 | 9.042 | 12.4267 | 9.8 | 15.8976 | 15.5113 | 15.3756 | 14.2822 | 14.3866 | 14.813 |  |  |  | 20.3347 | 83.8986 | 70.6651 | 25.6073 | -0.031557 | -0.27663 | 25.0183 |  |  | 10.8336 |  |  | 16.8831 | 16.1619 | 18.6212 | 16.3405 | 15.6538 | 16.0596 | 72.0941 | 87.7427 | 58.3789 | 58.8717 | 33.4855 |  | 23.0091 | 41.9163 | 23.7765 | 23.7073 | 21.4268 | 64.4966 |  | 37.0748 |  |  | 13.1665 | 14.4198 | 25.841 | [6 empty] | 21.7708 |  |  | 19.8798 |  |  | 12.4697 | 20.3196 | 94.5693 | 8.4013 | 16.8842 | 66.3875 | 9.5797 | 16.0051 | 70.7095 | 14.4804 | 60.2729 | 9.6692 | 53.2684 | 10.526 | 54.1621 | 9.6467 | 17.57 | 63.8295 | 14.3571 | 18.3463 | 82.5186 | 10.2092 | 16.5874 | 71.7098 | 10.4696 | 51.7173 | 13.6493 | 63.4192 | 11.2324 | 57.8277 | 0.39655 | 20.0509 | 0.59552 | 0.056085 | -37.9178 | 3.1224 | 90.79 | 49.39 | -0.62374 | 0.10836 | 0.3061 | -0.39326 | 0.41901 | 0.37249 | 0.94392 | 0.14519 | -0.063149 | 0.3636 | -0.2184 | 0.26396 | 0.1838 | 0.27419
42810.4437 | 317 | 18.5088 | 18.5835 | 18.5704 | 18.5708 | 17.8735 | 16.4739 | 14.5329 | 16.6461 | 17.143 | 17.2419 | 17.2366 | 16.7615 | 15.7792 | 14.405 | 14.8793 | 14.8694 | 15.4389 | 13.3084 | 13.5981 | 14.5894 |  |  |  | 16.5353 | 15.9155 | 17.2825 | 75.9206 | 73.2201 | 82.7932 | 17.1589 | 16.3022 | 16.5055 | 16.8213 | 16.1328 | 16.751 | 21.7127 | 78.2748 |  | 41.4708 | 64.0083 | 65.7066 | 29.7369 |  | 6.7889 | 6.9735 | 6.3378 | 6.6572 | 7.0042 | 8.5818 | 24.3446 | 4.4429 | 6.5987 | 4.4157 | 7.0173 | 8.0898 | 42.6351 | 46.958 | 42.9201 | 14.8592 |  |  | -0.24423 | -0.056425 | 0.009736 | 0.086738 | 0.34515 | 0.092852 | 0.44477 | 0.078032 | -0.6805 | -0.37991 | -0.13463 | 8.903 | -0.00045012 | 1.7738 | 15.8013 | 16.681 | 17.2109 | 17.5381 | 17.482 | 16.4294 | 14.7691 | 16.7994 | 17.1343 | 17.4282 | 17.4682 | 17.1808 | 16.3536 | 14.5414 | 18.1975 | 10.5946 | 10.2225 | 8.7473 | 9.1099 | 12.4634 | 9.8029 | 15.8855 | 15.5116 | 15.3718 | 14.2767 | 14.3859 | 14.8124 |  |  |  | 20.376 | 83.9803 | 70.7316 | 25.7954 | -0.0001538 | -0.1718 | 24.9765 |  |  | 10.8254 |  |  | 16.8902 | 16.1576 | 18.6546 | 16.3436 | 15.6586 | 16.0749 | 72.3051 | 87.9816 | 58.554 | 59.0485 | 34.4209 |  | 23.0712 | 40.8443 | 23.841 | 24.0819 | 21.4898 | 64.7844 |  | 37.1828 |  |  | 13.172 | 14.431 | 25.9638 | [6 empty] | 21.7668 |  |  | 19.9433 |  |  | 12.4983 | 20.3556 | 94.8525 | 8.4135 | 16.89 | 66.6327 | 9.5813 | 16.0214 | 70.9462 | 14.5202 | 60.3102 | 9.6912 | 53.3394 | 10.5457 | 54.2331 | 9.6569 | 17.6908 | 63.8952 | 14.3811 | 18.4572 | 82.5379 | 10.2226 | 16.595 | 71.7369 | 10.4815 | 51.8205 | 13.6904 | 63.4692 | 11.2708 | 57.9228 | 0.35899 | 20.051 | 0.599 | 0.056375 | -37.9015 | 3.1224 | 111.95 | 49.97 | -0.64976 | -0.27706 | 0.11509 | 0.34352 | 0.68721 | 0.35644 | 0.7801 | 0.1213 | -0.031192 | 0.35531 | -0.25982 | 0.31682 | 0.20572 | 0.27035
42810.4437 | 318 | 18.5144 | 18.5753 | 18.5691 | 18.5602 | 17.8677 | 16.4714 | 14.5299 | 16.6435 | 17.1382 | 17.2288 | 17.2308 | 16.7553 | 15.7744 | 14.3961 | 14.8814 | 14.8759 | 15.4429 | 13.3075 | 13.6062 | 14.5906 |  |  |  | 16.546 | 15.9201 | 17.3059 | 76.0514 | 73.2595 | 83.0132 | 17.1618 | 16.3075 | 16.5144 | 16.8236 | 16.1329 | 16.7648 | 21.7606 | 78.7664 |  | 41.5956 | 64.15 | 65.7419 | 30.5703 |  | 6.7921 | 6.9627 | 6.3444 | 6.6688 | 7.0108 | 8.5854 | 24.1147 | 4.527 | 6.6075 | 4.3859 | 7.0231 | 8.0917 | 42.6445 | 46.9649 | 42.9191 | 14.8491 |  |  | -0.35659 | -0.23319 | 0.025508 | 0.23262 | 0.31689 | -0.0274 | 0.62416 | -0.06522 | 0.029789 | -0.3476 | -0.25762 | 8.9026 | -0.00048791 | 1.8205 | 15.7991 | 16.6755 | 17.2095 | 17.5333 | 17.48 | 16.4162 | 14.766 | 16.7933 | 17.128 | 17.4307 | 17.4628 | 17.1719 | 16.3425 | 14.5359 | 18.0821 | 10.6038 | 9.9291 | 8.5809 | 9.1957 | 12.496 | 9.7972 | 15.8858 | 15.5143 | 15.3691 | 14.2824 | 14.3815 | 14.8256 |  |  |  | 20.4283 | 84.1005 | 70.7539 | 26.5137 | -0.011499 | -0.31314 | 24.8792 |  |  | 10.8119 |  |  | 16.8825 | 16.1499 | 18.667 | 16.3325 | 15.6383 | 16.0679 | 72.4411 | 88.2381 | 58.6779 | 59.1817 | 34.6706 |  | 23.1273 | 40.6115 | 23.8972 | 24.3 | 21.5467 | 65.052 |  | 37.2786 |  |  | 13.1867 | 14.432 | 25.9342 | [6 empty] | 21.9362 |  |  | 20.0154 |  |  | 12.5277 | 20.4294 | 95.2597 | 8.4195 | 16.8471 | 66.9789 | 9.5808 | 15.9801 | 71.0581 | 14.555 | 60.3486 | 9.7165 | 53.4199 | 10.5782 | 54.3628 | 9.6463 | 17.7749 | 63.9509 | 14.3912 | 18.6341 | 82.4924 | 10.2305 | 16.6166 | 71.6946 | 10.4566 | 51.9785 | 13.7315 | 63.5066 | 11.2893 | 58.0584 | 0.2573 | 20.0504 | 0.60064 | 0.058806 | -37.7447 | 3.1225 | 83.92 | 48.63 | -0.78538 | -0.56323 | 0.18628 | 0.56254 | 0.65848 | -0.19363 | 0.92414 | 0.11625 | -0.022833 | 0.35117 | -0.2432 | 0.34877 | 0.18418 | 0.25215
42810.4437 | 319 | 18.5054 | 18.5817 | 18.5683 | 18.5614 | 17.8711 | 16.4679 | 14.5277 | 16.648 | 17.1404 | 17.2249 | 17.2333 | 16.7599 | 15.7733 | 14.3935 | 14.8807 | 14.8803 | 15.4422 | 13.3135 | 13.6125 | 14.6016 |  |  |  | 16.5545 | 15.9234 | 17.3139 | 76.1867 | 73.262 | 83.1594 | 17.1647 | 16.3027 | 16.5199 | 16.8213 | 16.1331 | 16.7712 | 21.8114 | 79.2474 |  | 41.7 | 64.2655 | 65.7971 | 32.5445 |  | 6.7841 | 6.9591 | 6.3381 | 6.6684 | 7.0006 | 8.6006 | 23.8038 | 4.5794 | 6.6061 | 4.3468 | 7.0237 | 8.0873 | 42.6304 | 46.9636 | 42.911 | 14.8414 |  |  | -0.42822 | 0.12166 | 0.060332 | 0.013798 | 0.27484 | 0.2223 | 0.53151 | 0.087232 | -1.3772 | -0.75944 | -0.32776 | 8.9036 | -0.00047805 | 1.8467 | 15.803 | 16.6844 | 17.2181 | 17.5339 | 17.4849 | 16.4206 | 14.7737 | 16.7914 | 17.1274 | 17.4336 | 17.4651 | 17.1779 | 16.3504 | 14.5397 | 19.1141 | 11.2025 | 10.7883 | 8.6445 | 8.9687 | 12.5516 | 9.804 | 15.8836 | 15.5093 | 15.3691 | 14.284 | 14.3824 | 14.8322 |  |  |  | 20.4777 | 84.3218 | 70.5824 | 27.2909 | 0.054548 | -0.17989 | 24.9082 |  |  | 10.8062 |  |  | 16.8769 | 16.1503 | 18.6773 | 16.3252 | 15.6396 | 16.0768 | 72.5732 | 88.5291 | 58.8035 | 59.3273 | 34.1783 |  | 23.1857 | 40.6148 | 23.9456 | 24.4786 | 21.6077 | 65.1304 |  | 37.3867 |  |  | 13.2069 | 14.4552 | 25.8675 | [6 empty] | 22.0733 |  |  | 20.0537 |  |  | 12.555 | 20.4638 | 95.5532 | 8.4448 | 16.8298 | 67.1955 | 9.5906 | 15.955 | 71.2934 | 14.5816 | 60.4041 | 9.7361 | 53.4805 | 10.5933 | 54.6159 | 9.6415 | 17.7611 | 64.0726 | 14.4247 | 18.7631 | 82.5147 | 10.248 | 16.6988 | 71.7538 | 10.4523 | 52.0675 | 13.7723 | 63.7537 | 11.3262 | 58.2032 | 0.38827 | 20.0497 | 0.59967 | 0.057619 | -37.866 | 3.1225 | 92.5 | 49.83 | -0.86082 | 0.40681 | 0.28649 | 0.13701 | 0.61325 | 0.55153 | 0.85281 | 0.13189 | -0.021292 | 0.34825 | -0.35139 | 0.25408 | 0.13104 | 0.23222
42810.4437 | 320 | 18.5061 | 18.5827 | 18.562 | 18.5594 | 17.8686 | 16.4726 | 14.5257 | 16.6476 | 17.1408 | 17.234 | 17.2345 | 16.7537 | 15.7756 | 14.3946 | 14.8857 | 14.8841 | 15.4454 | 13.316 | 13.615 | 14.6104 |  |  |  | 16.5449 | 15.9238 | 17.3287 | 76.289 | 73.2972 | 83.4904 | 17.1593 | 16.3003 | 16.5289 | 16.8229 | 16.1323 | 16.7886 | 21.8788 | 79.8552 |  | 41.8066 | 64.3691 | 65.8764 | 34.0542 |  | 6.7717 | 6.9551 | 6.3231 | 6.666 | 7.0132 | 8.6269 | 23.7894 | 4.754 | 6.5959 | 4.3072 | 7.0175 | 8.0884 | 42.6058 | 46.947 | 42.9042 | 14.835 |  |  | -0.39734 | -0.001885 | 0.21607 | 0.10974 | 0.28075 | -0.12268 | 0.61102 | 0.25808 | -0.51062 | 1.3457 | -0.3224 | 8.9031 | -0.00049119 | 1.8761 | 15.8008 | 16.6938 | 17.2209 | 17.5391 | 17.4846 | 16.4335 | 14.7749 | 16.793 | 17.1299 | 17.4287 | 17.4688 | 17.1872 | 16.3545 | 14.5359 | 19.3827 | 11.3195 | 11.8645 | 9.1517 | 9.1809 | 12.5855 | 9.8143 | 15.8919 | 15.5114 | 15.3741 | 14.2779 | 14.3856 | 14.8343 |  |  |  | 20.5285 | 84.6134 | 70.5793 | 28.0184 | -0.021022 | -0.16672 | 24.9698 |  |  | 10.8147 |  |  | 16.8812 | 16.1556 | 18.7041 | 16.3353 | 15.6554 | 16.0934 | 72.807 | 88.9171 | 58.9203 | 59.4581 | 33.5372 |  | 23.2309 | 40.4082 | 23.9982 | 24.7819 | 21.6758 | 65.8822 |  | 37.5029 |  |  | 13.2047 | 14.4782 | 25.7204 | [6 empty] | 22.1105 |  |  | 20.1595 |  |  | 12.5796 | 20.527 | 96.02 | 8.451 | 16.8065 | 67.3543 | 9.5885 | 15.9594 | 71.5119 | 14.6191 | 60.5039 | 9.7476 | 53.5397 | 10.6103 | 54.8268 | 9.6305 | 17.7552 | 64.1193 | 14.4444 | 18.8118 | 82.7823 | 10.2401 | 16.7217 | 71.8906 | 10.4352 | 52.1919 | 13.8046 | 63.8051 | 11.3388 | 58.3002 | 0.28022 | 20.049 | 0.59933 | 0.058531 | -37.8387 | 3.1225 | 87.26 | 49.78 | -0.82959 | -0.050639 | 0.54216 | 0.38637 | 0.61984 | -0.40975 | 0.91442 | 0.15122 | -0.013778 | 0.34211 | -0.3773 | 0.13571 | 0.091369 | 0.21371
42810.4437 | 321 | 18.5008 | 18.5756 | 18.5666 | 18.5637 | 17.8726 | 16.4781 | 14.526 | 16.6454 | 17.1426 | 17.2358 | 17.2395 | 16.7545 | 15.7784 | 14.3983 | 14.8894 | 14.8769 | 15.4399 | 13.3123 | 13.6216 | 14.6122 |  |  |  | 16.5459 | 15.9263 | 17.3445 | 76.348 | 73.2928 | 82.8454 | 17.1566 | 16.2999 | 16.5429 | 16.8246 | 16.1335 | 16.7995 | 21.9624 | 79.717 |  | 41.9125 | 64.4584 | 65.9479 | 36.6341 |  | 6.7712 | 6.9517 | 6.3216 | 6.6705 | 7.0221 | 8.6606 | 23.8527 | 4.917 | 6.5962 | 4.3158 | 7.0255 | 8.0883 | 42.5825 | 46.9353 | 42.8998 | 14.8301 |  |  | -0.35923 | 0.087483 | 0.10502 | 0.23722 | 0.59486 | 0.61132 | 0.86598 | 0.03992 | -0.11246 | -0.66964 | -0.32896 | 8.9039 | -0.00047969 | 1.8516 | 15.8012 | 16.6838 | 17.2144 | 17.5366 | 17.4849 | 16.4387 | 14.7702 | 16.7969 | 17.1387 | 17.4322 | 17.4706 | 17.179 | 16.3488 | 14.5436 | 19.4208 | 11.2384 | 11.6947 | 9.492 | 9.24 | 12.6303 | 9.8256 | 15.8885 | 15.4969 | 15.3681 | 14.2736 | 14.3911 | 14.8303 |  |  |  | 20.5881 | 84.8648 | 70.6384 | 28.4724 | 0.004506 | -0.11967 | 25.0266 |  |  | 10.8124 |  |  | 16.882 | 16.1545 | 18.7196 | 16.3332 | 15.6485 | 16.0986 | 72.982 | 89.3794 | 58.9671 | 59.5963 | 33.6909 |  | 23.2871 | 40.0701 | 24.0606 | 25.3344 | 21.7563 | 66.4754 |  | 37.62 |  |  | 13.212 | 14.4975 | 25.721 | [6 empty] | 22.3538 |  |  | 20.2264 |  |  | 12.607 | 20.6345 | 96.4082 | 8.4455 | 16.779 | 67.4549 | 9.6081 | 15.9597 | 71.7111 | 14.6526 | 60.5973 | 9.7331 | 53.5909 | 10.6402 | 54.9133 | 9.63 | 17.7655 | 64.1531 | 14.4708 | 18.8464 | 83.1369 | 10.2612 | 16.7557 | 72.0833 | 10.4412 | 52.2934 | 13.8509 | 63.9068 | 11.3732 | 58.3575 | 0.46242 | 20.0496 | 0.59954 | 0.058068 | -37.8487 | 3.1225 | 99.61 | 48.87 | -0.78808 | 0.34497 | 0.37797 | 0.56807 | 0.9023 | 0.9147 | 1.0887 | 0.14884 | -0.00228 | 0.32947 | -0.37631 | 0.15588 | 0.022517 | 0.2031
42810.4438 | 322 | 18.5041 | 18.5755 | 18.5569 | 18.5592 | 17.8736 | 16.4695 | 14.5242 | 16.6396 | 17.1401 | 17.2331 | 17.2349 | 16.7468 | 15.774 | 14.3937 | 14.8877 | 14.8773 | 15.4451 | 13.3113 | 13.6186 | 14.6175 |  |  |  | 16.5452 | 15.9294 | 17.3566 | 76.3739 | 73.274 | 82.9411 | 17.1568 | 16.295 | 16.5468 | 16.8176 | 16.1281 | 16.8011 | 22.0363 | 79.611 |  | 42.0121 | 64.5561 | 65.9991 | 39.0587 |  | 6.7631 | 6.946 | 6.3047 | 6.6759 | 7.0392 | 8.6701 | 23.8951 | 4.8608 | 6.5967 | 4.4584 | 7.0235 | 8.0855 | 42.5526 | 46.926 | 42.887 | 14.8159 |  |  | -0.53336 | -0.20428 | -0.043492 | 0.001314 | 0.10004 | 0.15002 | 0.55648 | -0.28272 | -0.33295 | -0.14493 | -0.28504 | 8.9032 | -0.0004337 | 1.7416 | 15.8065 | 16.6906 | 17.213 | 17.5326 | 17.4788 | 16.439 | 14.775 | 16.7976 | 17.1331 | 17.432 | 17.4712 | 17.1771 | 16.3416 | 14.5469 | 20.6362 | 11.7004 | 12.3403 | 9.5797 | 9.3982 | 12.6709 | 9.8408 | 15.881 | 15.5103 | 15.372 | 14.2818 | 14.3937 | 14.8453 |  |  |  | 20.6345 | 85.035 | 70.6488 | 28.5527 | 0.0097736 | -0.11967 | 25.082 |  |  | 10.8149 |  |  | 16.874 | 16.161 | 18.7473 | 16.3461 | 15.6525 | 16.1117 | 73.2762 | 89.8906 | 59.1543 | 59.7493 | 34.5997 |  | 23.3447 | 39.5135 | 24.1177 | 26.1394 | 21.8438 | 66.6595 |  | 37.7494 |  |  | 13.2281 | 14.5108 | 25.7587 | [6 empty] | 23.1991 |  |  | 20.3056 |  |  | 12.6247 | 20.8295 | 96.7855 | 8.4546 | 16.7998 | 67.5464 | 9.6247 | 15.9617 | 71.8876 | 14.6853 | 60.7128 | 9.7291 | 53.6659 | 10.6646 | 54.9887 | 9.6386 | 17.8153 | 64.1866 | 14.4958 | 19.0168 | 83.5105 | 10.2695 | 16.8641 | 72.2441 | 10.4328 | 52.3724 | 13.8689 | 63.9251 | 11.3904 | 58.4742 | 0.21551 | 20.0473 | 0.59833 | 0.057598 | -37.8502 | 3.1225 | 79.45 | 49.92 | -0.96041 | -0.52715 | -0.24323 | 0.042278 | 0.37004 | 0.45313 | 0.87273 | 0.12554 | 0.015106 | 0.31005 | -0.50662 | 0.085919 | -0.042349 | 0.20243
42810.4438 | 323 | 18.4997 | 18.579 | 18.5568 | 18.565 | 17.8677 | 16.4672 | 14.5252 | 16.6445 | 17.1352 | 17.2293 | 17.2268 | 16.7474 | 15.7748 | 14.3922 | 14.8833 | 14.872 | 15.4423 | 13.3084 | 13.608 | 14.6191 |  |  |  | 16.5332 | 15.9227 | 17.363 | 76.4992 | 73.3142 | 83.7841 | 17.1509 | 16.29 | 16.55 | 16.8192 | 16.1263 | 16.816 | 22.1171 | 80.0257 |  | 42.1214 | 64.6786 | 66.0289 | 39.4446 |  | 6.7762 | 6.9489 | 6.3148 | 6.7097 | 7.0669 | 8.6809 | 24.0103 | 4.7977 | 6.6031 | 4.6543 | 7.0272 | 8.093 | 42.5163 | 46.9374 | 42.89 | 14.8145 |  |  | -0.29614 | 0.13479 | 0.25024 | 0.015114 | -0.035976 | 0.21902 | 0.45594 | -0.006076 | -0.030342 | -0.11472 | -0.20854 | 8.9034 | -0.00048462 | 1.6789 | 15.7976 | 16.6865 | 17.214 | 17.5293 | 17.4815 | 16.4288 | 14.7726 | 16.7911 | 17.1345 | 17.4285 | 17.4666 | 17.1802 | 16.3454 | 14.548 | 21.5388 | 11.5984 | 13.1886 | 10.4587 | 9.7503 | 12.7036 | 9.8654 | 15.8759 | 15.512 | 15.3708 | 14.2805 | 14.39 | 14.8512 |  |  |  | 20.6834 | 85.3028 | 70.3794 | 28.4558 | 0.19536 | -0.04025 | 25.0774 |  |  | 10.8072 |  |  | 16.8781 | 16.1642 | 18.7669 | 16.3414 | 15.6532 | 16.1194 | 73.5804 | 90.1411 | 59.3904 | 59.9196 | 34.9147 |  | 23.4025 | 39.0371 | 24.1729 | 27.1357 | 21.9356 | 67.1352 |  | 37.8573 |  |  | 13.2219 | 14.5248 | 25.8361 | [6 empty] | 23.8894 |  |  | 20.4212 |  |  | 12.6542 | 20.938 | 97.382 | 8.4551 | 16.8691 | 67.7018 | 9.6407 | 16.0399 | 72.1682 | 14.7195 | 60.7913 | 9.7269 | 53.7325 | 10.6891 | 55.1189 | 9.6448 | 17.9436 | 64.209 | 14.5301 | 19.3408 | 83.5911 | 10.2832 | 17.0153 | 72.3316 | 10.4391 | 52.4901 | 13.9115 | 63.9292 | 11.415 | 58.605 | 0.21108 | 20.0485 | 0.59977 | 0.05699 | -37.9583 | 3.1225 | 71.28 | 48.89 | -0.71649 | 0.42821 | 0.58345 | 0.14339 | -0.22191 | 0.54752 | 0.78998 | 0.11874 | 0.0302 | 0.28546 | -0.60312 | -0.0054823 | -0.050351 | 0.20676
42810.4438 | 324 | 18.5046 | 18.58 | 18.5646 | 18.5639 | 17.8754 | 16.4746 | 14.5305 | 16.6376 | 17.1439 | 17.2315 | 17.2362 | 16.7574 | 15.7804 | 14.3884 | 14.8866 | 14.8768 | 15.4418 | 13.3135 | 13.6157 | 14.6277 |  |  |  | 16.5397 | 15.9278 | 17.3837 | 76.6578 | 73.4013 | 84.2268 | 17.1588 | 16.3072 | 16.5706 | 16.8211 | 16.1339 | 16.8323 | 22.1913 | 80.8401 |  | 42.234 | 64.823 | 66.0666 | 38.7238 |  | 6.7669 | 6.9383 | 6.3363 | 6.7426 | 7.104 | 8.7519 | 24.1392 | 4.7814 | 6.6077 | 4.7298 | 7.0316 | 8.0998 | 42.4689 | 46.9373 | 42.8915 | 14.8003 |  |  | -0.50773 | -0.063653 | 0.11159 | 0.17217 | 0.041564 | 0.31298 | 0.56896 | -0.029736 | -0.045716 | -0.53831 | -0.22285 | 8.9023 | -0.00048955 | 1.6721 | 15.8024 | 16.6905 | 17.2216 | 17.5336 | 17.4777 | 16.4296 | 14.7773 | 16.7988 | 17.1355 | 17.4276 | 17.47 | 17.1847 | 16.3532 | 14.5485 | 22.6046 | 11.3839 | 12.3543 | 10.7066 | 10.5014 | 12.7666 | 9.8732 | 15.8848 | 15.5136 | 15.3711 | 14.2844 | 14.3932 | 14.8571 |  |  |  | 20.7434 | 85.6279 | 70.3126 | 28.6221 | 0.10317 | -0.15995 | 25.2097 |  |  | 10.79 |  |  | 16.8804 | 16.1591 | 18.7717 | 16.3275 | 15.6419 | 16.123 | 73.7791 | 90.5118 | 59.599 | 60.1463 | 35.1643 |  | 23.4692 | 38.945 | 24.2419 | 27.1777 | 22.0255 | 67.4569 |  | 37.9694 |  |  | 13.2017 | 14.5417 | 26.0409 | [6 empty] | 23.958 |  |  | 20.5554 |  |  | 12.6868 | 21.0008 | 98.0969 | 8.4704 | 16.8844 | 67.8577 | 9.6541 | 16.2239 | 72.5011 | 14.7655 | 60.8681 | 9.7266 | 53.8321 | 10.7167 | 55.2937 | 9.6479 | 18.1036 | 64.2847 | 14.5577 | 19.5574 | 83.7631 | 10.3019 | 17.0916 | 72.6086 | 10.4502 | 52.6317 | 13.9707 | 64.0273 | 11.4388 | 58.7291 | 0.15253 | 20.0475 | 0.60077 | 0.059479 | -37.9199 | 3.1225 | 62.29 | 48.67 | -0.93875 | -0.29426 | 0.3896 | 0.48394 | 0.23855 | 0.6546 | 0.88259 | 0.11405 | 0.035086 | 0.28731 | -0.7142 | 0.088124 | -0.027837 | 0.20415
42810.4438 | 325 | 18.5098 | 18.5848 | 18.5635 | 18.5639 | 17.8633 | 16.4711 | 14.5293 | 16.6444 | 17.1438 | 17.2336 | 17.2359 | 16.7634 | 15.777 | 14.3841 | 14.8788 | 14.8695 | 15.4376 | 13.3041 | 13.616 | 14.6317 |  |  |  | 16.5356 | 15.9224 | 17.3991 | 76.8413 | 73.5019 | 85.1322 | 17.1534 | 16.3033 | 16.5796 | 16.8214 | 16.1248 | 16.8418 | 22.2658 | 81.466 |  | 42.3623 | 64.9722 | 66.0988 | 40.2239 |  | 6.7664 | 6.9401 | 6.3474 | 6.7712 | 7.1201 | 8.7767 | 24.5962 | 4.769 | 6.593 | 4.7007 | 7.0328 | 8.0995 | 42.4296 | 46.9159 | 42.8788 | 14.7971 |  |  | -0.43413 | -0.10899 | 0.005792 | 0.27927 | 0.025792 | 0.16185 | 0.429 | -0.10267 | -0.28624 | -2.5327 | -0.21649 | 8.903 | -0.00046327 | 1.7555 | 15.7928 | 16.6833 | 17.2219 | 17.5362 | 17.4787 | 16.4294 | 14.7664 | 16.8026 | 17.1373 | 17.4259 | 17.4625 | 17.1755 | 16.3472 | 14.547 | 23.5007 | 11.3474 | 11.7496 | 10.3564 | 10.4046 | 12.8165 | 9.8764 | 15.8796 | 15.5006 | 15.3653 | 14.2854 | 14.3973 | 14.8544 |  |  |  | 20.8065 | 85.9191 | 70.2434 | 29.2466 | 0.26687 | 0.010564 | 25.3711 |  |  | 10.7993 |  |  | 16.8825 | 16.1669 | 18.8087 | 16.3436 | 15.6508 | 16.1477 | 74.0781 | 90.953 | 59.7764 | 60.3335 | 35.352 |  | 23.5259 | 39.0201 | 24.3041 | 26.8679 | 22.0951 | 67.7229 |  | 38.0906 |  |  | 13.1819 | 14.5453 | 26.2832 | [6 empty] | 23.9296 |  |  | 20.6878 |  |  | 12.7162 | 21.0989 | 98.5281 | 8.4829 | 16.8505 | 67.9626 | 9.6738 | 16.3527 | 72.7862 | 14.8288 | 60.941 | 9.7347 | 53.9391 | 10.7453 | 55.3771 | 9.6439 | 18.2328 | 64.413 | 14.582 | 19.5971 | 84.0899 | 10.3102 | 17.0825 | 73.0107 | 10.4606 | 52.7664 | 14.034 | 63.9777 | 11.4415 | 58.8623 | 0.31701 | 20.0456 | 0.60262 | 0.059487 | -37.9488 | 3.1225 | 78.76 | 50.01 | -0.86914 | -0.38505 | 0.088763 | 0.61636 | 0.18792 | 0.47075 | 0.76641 | 0.11075 | 0.0351 | 0.29826 | -0.80795 | 0.15569 | -0.067001 | 0.18892
42810.4438 | 326 | 18.5027 | 18.5852 | 18.562 | 18.564 | 17.8643 | 16.4695 | 14.5215 | 16.6413 | 17.139 | 17.2388 | 17.229 | 16.762 | 15.7785 | 14.391 | 14.8823 | 14.8701 | 15.4375 | 13.3097 | 13.6136 | 14.6357 |  |  |  | 16.5399 | 15.9225 | 17.4226 | 77.1549 | 73.6151 | 86.5756 | 17.1604 | 16.3077 | 16.583 | 16.8232 | 16.1359 | 16.8517 | 22.3538 | 81.5728 |  | 42.4822 | 65.1089 | 66.1428 | 40.9951 |  | 6.7725 | 6.939 | 6.3912 | 6.8132 | 7.187 | 8.8373 | 25.0705 | 4.8141 | 6.6077 | 4.7165 | 7.0376 | 8.0962 | 42.3916 | 46.8936 | 42.8621 | 14.7912 |  |  | -0.26328 | -0.11359 | 0.071504 | 0.091998 | -0.053064 | 0.008084 | 0.45988 | -0.006736 | -0.21366 | -0.037937 | -0.16344 | 8.9033 | -0.00048626 | 1.7791 | 15.786 | 16.6787 | 17.2107 | 17.5292 | 17.4746 | 16.4266 | 14.7617 | 16.7943 | 17.1262 | 17.4218 | 17.4623 | 17.1693 | 16.3364 | 14.5328 | 24.3411 | 11.8607 | 11.9361 | 9.9933 | 10.0903 | 12.872 | 9.883 | 15.8763 | 15.5073 | 15.3637 | 14.285 | 14.394 | 14.8644 |  |  |  | 20.8622 | 86.1052 | 70.0604 | 29.8839 | -0.014944 | 0.062695 | 25.2964 |  |  | 10.8051 |  |  | 16.8764 | 16.1723 | 18.8286 | 16.3389 | 15.6519 | 16.1451 | 74.347 | 91.1777 | 59.8967 | 60.4541 | 35.3532 |  | 23.5765 | 39.4623 | 24.3657 | 27.384 | 22.1785 | 68.7762 |  | 38.2233 |  |  | 13.1849 | 14.5393 | 26.4306 | [6 empty] | 24.7694 |  |  | 20.8447 |  |  | 12.7445 | 21.1969 | 99.1996 | 8.4738 | 16.8268 | 68.1458 | 9.6934 | 16.369 | 72.9891 | 14.8861 | 61.026 | 9.74 | 54.019 | 10.7672 | 55.4274 | 9.6435 | 18.3233 | 64.5848 | 14.6219 | 19.6561 | 84.3882 | 10.3198 | 17.059 | 73.3071 | 10.4785 | 52.8875 | 14.0875 | 64.0195 | 11.4608 | 59.0608 | 0.29601 | 20.0456 | 0.6014 | 0.059704 | -37.8982 | 3.1225 | 63.93 | 49.34 | -0.67821 | -0.39309 | 0.31187 | 0.35376 | -0.26958 | 0.10522 | 0.79361 | 0.11242 | 0.024896 | 0.28673 | -0.89488 | 0.13574 | -0.085464 | 0.17308
42810.4438 | 327 | 18.5053 | 18.5842 | 18.5596 | 18.5659 | 17.8676 | 16.4763 | 14.5273 | 16.6435 | 17.1366 | 17.2334 | 17.2331 | 16.7539 | 15.7752 | 14.3909 | 14.8792 | 14.8704 | 15.44 | 13.3142 | 13.62 | 14.6415 |  |  |  | 16.5426 | 15.9273 | 17.4345 | 77.4837 | 73.8732 | 88.3286 | 17.1551 | 16.3017 | 16.5959 | 16.8189 | 16.137 | 16.8627 | 22.4248 | 81.5444 |  | 42.6108 | 65.2825 | 66.2138 | 41.189 |  | 6.7683 | 6.9318 | 6.4005 | 6.8596 | 7.2329 | 8.9026 | 25.1071 | 4.863 | 6.5982 | 4.7126 | 7.0334 | 8.0921 | 42.3695 | 46.8854 | 42.8637 | 14.8025 |  |  | -0.44202 | -0.066281 | 0.014992 | 0.080826 | -0.080004 | 0.02254 | 0.45397 | -0.15853 | -0.79123 | -0.54733 | -0.17119 | 8.903 | -0.00047312 | 1.7708 | 15.7922 | 16.6805 | 17.2084 | 17.5302 | 17.4806 | 16.418 | 14.7722 | 16.7936 | 17.1283 | 17.4228 | 17.4587 | 17.1756 | 16.3404 | 14.5373 | 23.9414 | 12.1257 | 13.6462 | 10.1879 | 9.7109 | 12.9165 | 9.9247 | 15.8822 | 15.5098 | 15.3717 | 14.2862 | 14.4009 | 14.8716 |  |  |  | 20.9208 | 86.4123 | 70.0759 | 30.1931 | 0.047255 | -0.18855 | 25.3298 |  |  | 10.8029 |  |  | 16.8749 | 16.1708 | 18.84 | 16.3352 | 15.647 | 16.1553 | 74.55 | 91.3002 | 60.1167 | 60.7235 | 35.9414 |  | 23.6432 | 40.5929 | 24.4374 | 27.8374 | 22.2825 | 69.4248 |  | 38.3741 |  |  | 13.2049 | 14.5469 | 26.5342 | [6 empty] | 25.3265 |  |  | 21.0166 |  |  | 12.7721 | 21.3005 | 100.2776 | 8.4392 | 16.9631 | 68.3963 | 9.7009 | 16.3682 | 73.2802 | 14.938 | 61.1184 | 9.7408 | 54.1234 | 10.7824 | 55.5497 | 9.6617 | 18.3715 | 64.7145 | 14.6701 | 19.7951 | 85.1017 | 10.3291 | 17.0965 | 73.5781 | 10.4923 | 53.0239 | 14.1245 | 64.3392 | 11.4714 | 59.3258 | 0.43642 | 20.0455 | 0.60178 | 0.060254 | -37.9955 | 3.1226 | 61.09 | 49 | -0.88091 | -0.30026 | 0.1428 | 0.33158 | -0.33105 | 0.17572 | 0.78858 | 0.098328 | -0.0040916 | 0.27763 | -0.84528 | -0.049426 | -0.088464 | 0.16646
42810.4438 | 328 | 18.4976 | 18.5733 | 18.5576 | 18.5547 | 17.8607 | 16.4669 | 14.5223 | 16.6411 | 17.1376 | 17.2276 | 17.2294 | 16.7476 | 15.7687 | 14.3816 | 14.8764 | 14.8796 | 15.4437 | 13.3177 | 13.6311 | 14.6496 |  |  |  | 16.5437 | 15.935 | 17.4463 | 77.8366 | 74.1455 | 90.2338 | 17.1513 | 16.3031 | 16.6054 | 16.8214 | 16.1344 | 16.8696 | 22.4844 | 82.6795 |  | 42.7474 | 65.4672 | 66.3266 | 41.1239 |  | 6.774 | 6.9289 | 6.3861 | 6.8897 | 7.2525 | 8.9179 | 24.911 | 4.9223 | 6.5886 | 4.7211 | 7.029 | 8.097 | 42.3402 | 46.8741 | 42.8709 | 14.8188 |  |  | -0.56424 | 0.13151 | 0.005792 | -0.13734 | 0.099388 | -0.09114 | 0.35014 | -0.2525 | -0.52793 | -0.35369 | -0.14436 | 7.9242 | -0.00049776 | 1.7611 | 15.8001 | 16.6838 | 17.2243 | 17.5435 | 17.4829 | 16.4385 | 14.7688 | 16.8023 | 17.1324 | 17.4341 | 17.4708 | 17.177 | 16.3502 | 14.5414 | 23.1993 | 11.7923 | 13.9124 | 10.2612 | 9.3634 | 12.9568 | 9.9465 | 15.8697 | 15.5027 | 15.3626 | 14.2735 | 14.3971 | 14.8749 |  |  |  | 20.9741 | 86.6636 | 70.1769 | 30.6578 | -0.086259 | 0.0092466 | 25.4781 |  |  | 10.819 |  |  | 16.8861 | 16.1802 | 18.8599 | 16.3492 | 15.6552 | 16.1693 | 74.8057 | 91.975 | 60.3559 | 60.9997 | 37.083 |  | 23.6997 | 41.5498 | 24.5203 | 27.8578 | 22.373 | 70.0036 |  | 38.4996 |  |  | 13.2116 | 14.5479 | 26.6703 | [6 empty] | 25.2037 |  |  | 21.1926 |  |  | 12.8031 | 21.3903 | 100.8723 | 8.4142 | 17.3355 | 68.6726 | 9.7153 | 16.4784 | 73.7274 | 14.9907 | 61.1951 | 9.7455 | 54.2572 | 10.8022 | 55.7371 | 9.6798 | 18.4104 | 64.9012 | 14.73 | 19.962 | 85.6918 | 10.349 | 17.2947 | 73.8034 | 10.5063 | 53.1595 | 14.1618 | 64.3702 | 11.4735 | 59.5172 | 0.45356 | 20.0455 | 0.6018 | 0.06016 | -37.8673 | 3.1225 | 63.23 | 50.7 | -0.99789 | 0.42295 | 0.088761 | -0.43222 | 0.36899 | -0.35334 | 0.69258 | 0.068524 | -0.027874 | 0.28011 | -0.75813 | -0.076465 | -0.084651 | 0.15534
42810.4438 | 329 | 18.4972 | 18.5792 | 18.5608 | 18.5551 | 17.8619 | 16.464 | 14.5221 | 16.6334 | 17.1414 | 17.2251 | 17.2251 | 16.7485 | 15.7649 | 14.3748 | 14.8694 | 14.8755 | 15.4424 | 13.3099 | 13.6233 | 14.6579 |  |  |  | 16.549 | 15.9291 | 17.4664 | 78.3489 | 74.3508 | 92.2732 | 17.1539 | 16.3026 | 16.6139 | 16.8216 | 16.1392 | 16.8882 | 22.541 | 84.4336 |  | 42.9031 | 65.6557 | 66.5416 | 40.3274 |  | 6.7931 | 6.9396 | 6.4092 | 6.9053 | 7.2842 | 8.945 | 24.6905 | 5.0285 | 6.6045 | 4.7711 | 7.0466 | 8.0983 | 42.3255 | 46.8595 | 42.8752 | 14.8384 |  |  | -0.35988 | -0.18851 | -0.027064 | -0.29176 | 0.00608 | -0.009004 | 0.52494 | -0.18613 | -0.367 | 0.77693 | -0.24908 | -0.00061604 | -0.00062097 | 1.7344 | 15.7864 | 16.6735 | 17.2164 | 17.5291 | 17.4733 | 16.4234 | 14.7666 | 16.7902 | 17.1264 | 17.4261 | 17.4527 | 17.1643 | 16.342 | 14.5347 | 22.065 | 11.8314 | 14.4315 | 10.3882 | 9.6349 | 12.9891 | 9.9693 | 15.8705 | 15.514 | 15.3677 | 14.2772 | 14.4022 | 14.8859 |  |  |  | 21.0511 | 86.9003 | 70.1694 | 31.3243 | -0.013525 | -0.21829 | 25.5713 |  |  | 10.8211 |  |  | 16.8827 | 16.1767 | 18.8875 | 16.3445 | 15.6585 | 16.1782 | 75.1215 | 92.8454 | 60.605 | 61.2647 | 37.9044 |  | 23.7618 | 42.1315 | 24.5943 | 27.5861 | 22.4514 | 69.9162 |  | 38.6239 |  |  | 13.2284 | 14.5431 | 26.6574 | [6 empty] | 24.9715 |  |  | 21.3788 |  |  | 12.8397 | 21.4756 | 102.0383 | 8.4092 | 17.6749 | 68.9439 | 9.7305 | 16.6565 | 74.333 | 15.0562 | 61.2635 | 9.7486 | 54.365 | 10.8215 | 55.8494 | 9.6934 | 18.4451 | 65.1032 | 14.7844 | 20.0139 | 85.9313 | 10.3448 | 17.5807 | 74.0951 | 10.512 | 53.2998 | 14.1949 | 64.1763 | 11.4821 | 59.6606 | 0.29428 | 20.0456 | 0.60185 | 0.060399 | -37.8553 | 3.1226 | 65.5 | 48.9 | -0.79918 | -0.50638 | -0.19187 | -0.62998 | 0.091268 | -0.11107 | 0.84804 | 0.047798 | -0.041533 | 0.29029 | -0.62834 | -0.13151 | -0.060621 | 0.13941
42810.4439 | 330 | 18.5034 | 18.5829 | 18.5666 | 18.5588 | 17.8603 | 16.466 | 14.524 | 16.6372 | 17.1395 | 17.2211 | 17.2293 | 16.7517 | 15.7652 | 14.3842 | 14.8687 | 14.8679 | 15.4339 | 13.3009 | 13.6186 | 14.6525 |  |  |  | 16.5262 | 15.9137 | 17.4699 | 78.8463 | 74.6121 | 93.5354 | 17.1607 | 16.3016 | 16.6258 | 16.8257 | 16.1397 | 16.8992 | 22.5967 | 86.0963 |  | 43.0675 | 65.8451 | 66.7979 | 40.0758 |  | 6.7983 | 6.9384 | 6.4208 | 6.919 | 7.2867 | 8.9127 | 24.7019 | 5.1083 | 6.5976 | 4.7442 | 7.0438 | 8.0999 | 42.3086 | 46.8269 | 42.898 | 14.8612 |  |  | -0.45779 | -0.096509 | 0.12802 | 0.15837 | 0.047476 | -0.17197 | 0.46711 | -0.19533 | -0.14321 | -0.70489 | -0.20338 | -0.00058483 | -0.00062919 | 1.7057 | 15.7925 | 16.6788 | 17.2097 | 17.5359 | 17.4769 | 16.426 | 14.7591 | 16.7889 | 17.1317 | 17.4288 | 17.4559 | 17.1708 | 16.3394 | 14.5316 | 21.5582 | 11.7459 | 14.8574 | 11.0885 | 10.1657 | 13.0247 | 9.9897 | 15.8792 | 15.5036 | 15.3641 | 14.2812 | 14.397 | 14.8899 |  |  |  | 21.1209 | 87.0866 | 70.0999 | 32.0461 | 0.2375 | -0.25555 | 25.6159 |  |  | 10.824 |  |  | 16.886 | 16.1797 | 18.9132 | 16.3361 | 15.6608 | 16.1868 | 75.4004 | 94.2629 | 60.8934 | 61.5822 | 38.714 |  | 23.85 | 42.7614 | 24.6713 | 26.8977 | 22.5485 | 69.9967 |  | 38.7766 |  |  | 13.2435 | 14.5733 | 26.7434 | [6 empty] | 24.5887 |  |  | 21.5276 |  |  | 12.8673 | 21.5745 | 103.1319 | 8.4034 | 17.7261 | 69.2719 | 9.7395 | 16.8015 | 74.8701 | 15.1096 | 61.3502 | 9.7563 | 54.4502 | 10.8372 | 55.933 | 9.712 | 18.4726 | 65.2604 | 14.8538 | 20.0723 | 85.9314 | 10.3485 | 17.8035 | 74.472 | 10.5299 | 53.4779 | 14.2413 | 64.1978 | 11.4889 | 59.9669 | 0.44798 | 20.0457 | 0.60189 | 0.059682 | -37.9127 | 3.1226 | 71.74 | 49.35 | -0.90291 | -0.36233 | 0.4173 | 0.46414 | 0.25502 | -0.48536 | 0.79993 | 0.028285 | -0.056429 | 0.31268 | -0.56789 | -0.17645 | -0.051758 | 0.1217
42810.4439 | 331 | 18.4979 | 18.5745 | 18.5613 | 18.5618 | 17.8667 | 16.4716 | 14.5193 | 16.6456 | 17.1365 | 17.2276 | 17.2299 | 16.7572 | 15.7639 | 14.384 | 14.8716 | 14.8699 | 15.4357 | 13.3087 | 13.6289 | 14.6598 |  |  |  | 16.5354 | 15.9245 | 17.4804 | 79.1976 | 74.7692 | 93.036 | 17.1567 | 16.3036 | 16.6349 | 16.8208 | 16.1352 | 16.9043 | 22.672 | 87.644 |  | 43.2221 | 66.1169 | 67.0323 | 41.7518 |  | 6.7854 | 6.9436 | 6.4238 | 6.9191 | 7.2706 | 8.8735 | 25.094 | 5.1127 | 6.5976 | 4.7831 | 7.0469 | 8.0985 | 42.2996 | 46.7985 | 42.9083 | 14.8778 |  |  | -0.41902 | -0.058397 | 0.092532 | 0.039426 | 0.088876 | -0.032 | 0.31729 | -0.18678 | -0.43102 | -0.75881 | -0.48931 | -0.00058647 | -0.00058155 | 1.6917 | 15.7982 | 16.6862 | 17.2125 | 17.5311 | 17.4847 | 16.4241 | 14.7647 | 16.7958 | 17.1279 | 17.4211 | 17.4678 | 17.1734 | 16.3456 | 14.5349 | 22.1736 | 12.0263 | 14.6291 | 11.3694 | 10.6366 | 13.0898 | 10.0219 | 15.8684 | 15.5011 | 15.3546 | 14.2787 | 14.3991 | 14.8927 |  |  |  | 21.1799 | 87.2586 | 70.2871 | 32.3022 | 0.21075 | -0.1432 | 25.6153 |  |  | 10.8192 |  |  | 16.878 | 16.1742 | 18.929 | 16.337 | 15.6523 | 16.1891 | 75.4811 | 95.4441 | 61.1427 | 61.7776 | 39.197 |  | 23.9383 | 43.4574 | 24.7564 | 26.8997 | 22.6318 | 70.2951 |  | 38.8818 |  |  | 13.2149 | 14.5902 | 26.8878 | [6 empty] | 24.3899 |  |  | 21.7135 |  |  | 12.8901 | 21.7294 | 103.8668 | 8.3962 | 17.7664 | 69.5933 | 9.7632 | 16.9664 | 75.4634 | 15.1675 | 61.4453 | 9.7855 | 54.4956 | 10.8507 | 56.1945 | 9.7307 | 18.5359 | 65.4624 | 14.923 | 20.2536 | 86.062 | 10.3363 | 17.8065 | 74.9677 | 10.5491 | 53.6376 | 14.2612 | 64.4438 | 11.4787 | 60.231 | 0.32279 | 20.0461 | 0.60267 | 0.059682 | -38.0084 | 3.1225 | 54.88 | 49.64 | -0.86325 | -0.28185 | 0.35478 | 0.23158 | 0.3489 | -0.20936 | 0.65923 | 0.017844 | -0.072889 | 0.31543 | -0.62868 | -0.14733 | -0.095779 | 0.11657
42810.4439 | 332 | 18.5015 | 18.5841 | 18.5635 | 18.553 | 17.8676 | 16.4755 | 14.5201 | 16.6435 | 17.1354 | 17.2359 | 17.23 | 16.75 | 15.7763 | 14.3865 | 14.8699 | 14.8801 | 15.4428 | 13.3091 | 13.6345 | 14.6795 |  |  |  | 16.5402 | 15.931 | 17.5003 | 79.7066 | 74.9561 | 94.5572 | 17.1474 | 16.2991 | 16.6436 | 16.8158 | 16.132 | 16.9083 | 22.7714 | 89.6233 |  | 43.4371 | 66.4504 | 67.2691 | 41.136 |  | 6.7751 | 6.9387 | 6.4126 | 6.9029 | 7.2666 | 8.8431 | 25.9836 | 5.1072 | 6.6039 | 4.8049 | 7.048 | 8.1023 | 42.2913 | 46.7739 | 42.9222 | 14.8998 |  |  | -0.47488 | 0.027031 | 0.18782 | 0.022998 | 0.05602 | -0.03726 | 0.31992 | 0.045176 | -0.35805 | -0.30459 | -0.33094 | -0.00062097 | -0.00061769 | 1.6926 | 15.7934 | 16.6758 | 17.209 | 17.5278 | 17.4799 | 16.4173 | 14.7641 | 16.7894 | 17.1287 | 17.4208 | 17.4705 | 17.1775 | 16.3422 | 14.538 | 22.3458 | 11.6054 | 14.1097 | 11.1931 | 10.5286 | 13.1337 | 10.0395 | 15.8657 | 15.4946 | 15.3546 | 14.2712 | 14.3951 | 14.8985 |  |  |  | 21.2417 | 87.3784 | 70.787 | 32.1252 | 0.21339 | -0.010514 | 25.5701 |  |  | 10.8225 |  |  | 16.8852 | 16.1841 | 18.9517 | 16.3397 | 15.6689 | 16.2172 | 75.7159 | 96.2811 | 61.3837 | 62.0018 | 40.2342 |  | 24.0061 | 43.9371 | 24.8348 | 27.3513 | 22.7364 | 70.6916 |  | 39.0059 |  |  | 13.178 | 14.6026 | 26.9573 | [6 empty] | 24.817 |  |  | 21.8474 |  |  | 12.9114 | 21.8642 | 105.3605 | 8.4137 | 17.9309 | 69.937 | 9.7838 | 17.1891 | 76.4038 | 15.2261 | 61.5519 | 9.7849 | 54.5353 | 10.8577 | 56.4625 | 9.7527 | 18.6206 | 65.7378 | 15.0048 | 20.4568 | 86.3783 | 10.3541 | 17.8741 | 75.5716 | 10.5556 | 53.7933 | 14.3223 | 64.5693 | 11.4823 | 60.6677 | 0.34763 | 20.0483 | 0.60456 | 0.063815 | -37.9973 | 3.1226 | 48.9 | 49.42 | -0.92089 | 0.19175 | 0.50545 | 0.17687 | 0.27699 | -0.2259 | 0.66192 | -0.0086803 | -0.083566 | 0.3064 | -0.6427 | -0.087576 | -0.075327 | 0.12356
42810.4439 | 333 | 18.4824 | 18.5715 | 18.561 | 18.547 | 17.8544 | 16.4655 | 14.5129 | 16.636 | 17.128 | 17.2139 | 17.2281 | 16.7531 | 15.7643 | 14.3718 | 14.8631 | 14.8703 | 15.4346 | 13.2983 | 13.6299 | 14.6777 |  |  |  | 16.5348 | 15.9213 | 17.5175 | 80.0642 | 75.2379 | 93.8393 | 17.1461 | 16.292 | 16.6471 | 16.8156 | 16.1269 | 16.9137 | 22.8415 | 91.2387 |  | 43.6514 | 66.6985 | 67.5067 | 39.5038 |  | 6.7747 | 6.9371 | 6.4139 | 6.9129 | 7.2751 | 8.841 | 26.5321 | 5.0635 | 6.6091 | 4.8421 | 7.0644 | 8.1029 | 42.2735 | 46.7542 | 42.9274 | 14.9172 |  |  | -0.29154 | -0.093221 | 0.024848 | -0.087398 | -0.04912 | 0.015312 | 0.39351 | 0.01692 | -1.2355 | 0.022276 | -0.24391 | -0.00057005 | -0.00058483 | 1.7061 | 15.7886 | 16.6704 | 17.2101 | 17.5337 | 17.4764 | 16.4205 | 14.7602 | 16.7897 | 17.1322 | 17.4207 | 17.4656 | 17.1764 | 16.3427 | 14.5374 | 22.2152 | 11.5367 | 13.0509 | 10.6296 | 10.3087 | 13.1824 | 10.048 | 15.8758 | 15.4975 | 15.3703 | 14.2814 | 14.4074 | 14.9177 |  |  |  | 21.3124 | 87.4558 | 71.0297 | 32.0187 | 0.030439 | -0.027264 | 25.5623 |  |  | 10.8241 |  |  | 16.8898 | 16.1862 | 18.9746 | 16.3492 | 15.6638 | 16.223 | 76.0321 | 97.3675 | 61.7436 | 62.3066 | 40.8748 |  | 24.0815 | 44.2953 | 24.9122 | 27.9037 | 22.8389 | 71.398 |  | 39.1671 |  |  | 13.2003 | 14.6449 | 26.9758 | [6 empty] | 24.8663 |  |  | 22.003 |  |  | 12.9476 | 21.9944 | 106.6189 | 8.4566 | 18.1508 | 70.2996 | 9.7902 | 17.2701 | 77.1311 | 15.2863 | 61.6618 | 9.797 | 54.644 | 10.8897 | 56.5874 | 9.7434 | 18.7067 | 66.0664 | 15.0613 | 20.5019 | 87.0041 | 10.3567 | 18.0835 | 76.0336 | 10.5804 | 53.8614 | 14.3635 | 64.6463 | 11.4934 | 60.9967 | 0.38634 | 20.0466 | 0.60501 | 0.063663 | -37.9509 | 3.1226 | 70.8 | 49.99 | -0.72085 | -0.3561 | 0.18385 | -0.3448 | -0.25937 | 0.14481 | 0.73411 | -0.023932 | -0.090901 | 0.2945 | -0.62252 | 0.031052 | -0.02763 | 0.12889
42810.4439 | 334 | 18.4904 | 18.5732 | 18.5588 | 18.5499 | 17.8519 | 16.4592 | 14.5229 | 16.6316 | 17.1319 | 17.2219 | 17.2263 | 16.7485 | 15.7612 | 14.3739 | 14.8731 | 14.8729 | 15.4339 | 13.3061 | 13.6244 | 14.6895 |  |  |  | 16.5374 | 15.9281 | 17.5316 | 80.2712 | 75.6159 | 94.3412 | 17.1423 | 16.2905 | 16.6514 | 16.8114 | 16.1223 | 16.9293 | 22.8996 | 92.8725 |  | 43.8132 | 66.8788 | 67.7613 | 39.4494 |  | 6.7667 | 6.9314 | 6.41 | 6.9113 | 7.2636 | 8.8166 | 26.8959 | 5.0894 | 6.6005 | 4.8184 | 7.0657 | 8.1042 | 42.2724 | 46.7537 | 42.9212 | 14.9279 |  |  | -0.48079 | -0.097165 | 0.18716 | -0.019058 | 0.22818 | 0.18879 | 0.3646 | 0.15623 | -0.10799 | -1.6696 | -0.17198 | -0.0006144 | -0.00062754 | 1.7117 | 15.7932 | 16.6768 | 17.2126 | 17.5291 | 17.4668 | 16.4161 | 14.7605 | 16.7941 | 17.125 | 17.4219 | 17.46 | 17.1769 | 16.3375 | 14.5342 | 21.6153 | 11.6136 | 13.6118 | 10.4577 | 9.7619 | 13.2125 | 10.0717 | 15.8698 | 15.4933 | 15.3641 | 14.2762 | 14.3984 | 14.9131 |  |  |  | 21.3738 | 87.549 | 71.026 | 32.0932 | 0.082507 | -0.21942 | 25.5046 |  |  | 10.8197 |  |  | 16.8898 | 16.1935 | 18.9927 | 16.3497 | 15.6684 | 16.2286 | 76.2979 | 97.7733 | 62.0842 | 62.6438 | 41.0815 |  | 24.1689 | 44.3956 | 24.9929 | 29.0656 | 22.9875 | 72.3213 |  | 39.3485 |  |  | 13.2056 | 14.6522 | 27.1978 | [6 empty] | 25.5154 |  |  | 22.1489 |  |  | 12.9758 | 22.0946 | 107.5828 | 8.4821 | 18.2573 | 70.8011 | 9.7955 | 17.2398 | 77.6126 | 15.3513 | 61.8232 | 9.7981 | 54.8208 | 10.9075 | 56.73 | 9.7199 | 18.7891 | 66.4535 | 15.1173 | 20.5361 | 87.5217 | 10.3732 | 18.2959 | 76.4394 | 10.588 | 53.9749 | 14.3928 | 64.7393 | 11.4953 | 61.1715 | 0.39193 | 20.0477 | 0.60499 | 0.060312 | -37.9083 | 3.1226 | 102.87 | 49.38 | -0.92633 | -0.36355 | 0.50456 | -0.16101 | 0.559 | 0.50846 | 0.7066 | -0.026724 | -0.090962 | 0.26723 | -0.55235 | -0.028512 | -0.024163 | 0.12888
42810.4439 | 335 | 18.4881 | 18.5775 | 18.5594 | 18.5489 | 17.8576 | 16.463 | 14.5233 | 16.6322 | 17.1323 | 17.2259 | 17.2321 | 16.7483 | 15.7646 | 14.3745 | 14.8808 | 14.8767 | 15.4444 | 13.314 | 13.6408 | 14.7001 |  |  |  | 16.5477 | 15.9413 | 17.5551 | 80.6259 | 75.8608 | 95.5563 | 17.1397 | 16.2923 | 16.6582 | 16.814 | 16.1284 | 16.9406 | 22.979 | 94.5078 |  | 43.9988 | 67.1212 | 68.0512 | 40.9102 |  | 6.7591 | 6.9269 | 6.4083 | 6.9092 | 7.2513 | 8.7857 | 27.458 | 5.214 | 6.6043 | 4.7803 | 7.0694 | 8.106 | 42.2812 | 46.7629 | 42.9321 | 14.9409 |  |  | -0.33163 | -0.18259 | -0.048748 | -0.18136 | 0.090848 | 0.03634 | 0.05444 | 0.16872 | -0.14905 | 0.32774 | -0.22424 | -0.00061276 | -0.00060126 | 1.6853 | 15.7847 | 16.6778 | 17.2177 | 17.5278 | 17.4725 | 16.4202 | 14.767 | 16.7974 | 17.1323 | 17.4183 | 17.4644 | 17.1743 | 16.3416 | 14.5392 | 22.0511 | 12.335 | 14.3631 | 10.8886 | 9.5803 | 13.2635 | 10.098 | 15.8632 | 15.4916 | 15.3633 | 14.2687 | 14.3961 | 14.9146 |  |  |  | 21.4476 | 87.6663 | 70.9502 | 32.4538 | 0.11654 | -0.058317 | 25.4858 |  |  | 10.8092 |  |  | 16.8776 | 16.1827 | 19.0016 | 16.3358 | 15.6574 | 16.2306 | 76.8033 | 98.3467 | 62.3589 | 62.9903 | 40.9274 |  | 24.2315 | 44.247 | 25.056 | 30.3094 | 23.1397 | 73.7907 |  | 39.5144 |  |  | 13.2286 | 14.6647 | 27.4253 | [6 empty] | 26.6729 |  |  | 22.2667 |  |  | 13.0309 | 22.2225 | 108.7583 | 8.5089 | 18.3281 | 71.5442 | 9.8134 | 17.2721 | 78.245 | 15.4274 | 62.0561 | 9.7902 | 55.0046 | 10.9245 | 56.8947 | 9.7187 | 19.0638 | 66.8094 | 15.1907 | 20.6067 | 87.8418 | 10.3824 | 18.4606 | 76.9337 | 10.6155 | 54.0646 | 14.4426 | 65.0338 | 11.5145 | 61.4509 | 0.35129 | 20.0472 | 0.60589 | 0.059646 | -37.9346 | 3.1226 | 96.66 | 48.89 | -0.7706 | -0.49836 | -0.2575 | -0.49668 | 0.3527 | 0.22307 | 0.27302 | -0.020332 | -0.084698 | 0.23781 | -0.59484 | -0.10893 | -0.062068 | 0.12134
42810.4439 | 336 | 18.4856 | 18.5801 | 18.5588 | 18.551 | 17.8579 | 16.4635 | 14.5198 | 16.6371 | 17.1332 | 17.2268 | 17.2291 | 16.7474 | 15.7632 | 14.3757 | 14.8762 | 14.878 | 15.4445 | 13.3093 | 13.6402 | 14.7022 |  |  |  | 16.5462 | 15.9357 | 17.5636 | 81.0507 | 76.0778 | 96.9842 | 17.1461 | 16.3002 | 16.6746 | 16.8219 | 16.1454 | 16.9537 | 23.0642 | 95.5258 |  | 44.1758 | 67.351 | 68.4146 | 40.7924 |  | 6.7483 | 6.9282 | 6.3996 | 6.8982 | 7.248 | 8.743 | 27.3422 | 5.3392 | 6.6051 | 4.7564 | 7.0552 | 8.1077 | 42.2744 | 46.7546 | 42.9374 | 14.9524 |  |  | -0.306 | -0.3633 | -0.05072 | -0.10317 | 0.085588 | 0.033052 | 0.18192 | 0.06292 | -0.41176 | -0.028286 | -0.34068 | -0.00059797 | -0.00062754 | 1.6605 | 15.7993 | 16.688 | 17.211 | 17.5353 | 17.4763 | 16.429 | 14.7644 | 16.8015 | 17.136 | 17.4332 | 17.4636 | 17.1741 | 16.3453 | 14.5389 | 22.2533 | 12.5408 | 16.4744 | 11.8789 | 10.1389 | 13.3222 | 10.1441 | 15.8663 | 15.4996 | 15.3645 | 14.2728 | 14.4129 | 14.929 |  |  |  | 21.5247 | 87.8132 | 71.1173 | 32.8987 | 0.13255 | -0.025382 | 25.4657 |  |  | 10.8261 |  |  | 16.8824 | 16.1871 | 19.0217 | 16.3372 | 15.6591 | 16.2449 | 77.2881 | 99.208 | 62.591 | 63.2821 | 40.4829 |  | 24.3169 | 43.6468 | 25.1216 | 30.7063 | 23.2798 | 74.9441 |  | 39.722 |  |  | 13.2526 | 14.685 | 27.499 | [6 empty] | 26.6299 |  |  | 22.4125 |  |  | 13.0711 | 22.3346 | 110.0403 | 8.5174 | 18.3742 | 72.0817 | 9.8243 | 17.383 | 78.9387 | 15.4657 | 62.1752 | 9.7678 | 55.098 | 10.9321 | 57.0172 | 9.7215 | 19.358 | 67.2934 | 15.2635 | 20.7309 | 88.1663 | 10.4027 | 18.5546 | 77.4921 | 10.6293 | 54.2363 | 14.5023 | 65.2418 | 11.5309 | 61.7702 | 0.40271 | 20.0473 | 0.6066 | 0.059371 | -37.8692 | 3.1227 | 109.71 | 50.12 | -0.74166 | -0.70297 | -0.26266 | -0.37461 | 0.34231 | 0.21272 | 0.49906 | -0.005103 | -0.065813 | 0.23151 | -0.61049 | -0.33816 | -0.055928 | 0.11157
42810.4439 | 337 | 18.485 | 18.5761 | 18.5554 | 18.549 | 17.8573 | 16.4639 | 14.519 | 16.6414 | 17.1314 | 17.2204 | 17.2303 | 16.7488 | 15.7602 | 14.3774 | 14.8709 | 14.8754 | 15.4381 | 13.3082 | 13.6367 | 14.7024 |  |  |  | 16.5395 | 15.9293 | 17.5772 | 81.596 | 76.2637 | 98.8748 | 17.1473 | 16.2981 | 16.6881 | 16.8213 | 16.1412 | 16.9743 | 23.1436 | 96.3948 |  | 44.3185 | 67.5633 | 68.7646 | 39.7905 |  | 6.7582 | 6.9365 | 6.4119 | 6.9043 | 7.249 | 8.7041 | 26.9653 | 5.43 | 6.6142 | 4.8404 | 7.0686 | 8.1049 | 42.2545 | 46.7263 | 42.9324 | 14.9644 |  |  | -0.31782 | -0.15499 | 0.033392 | -0.089366 | 0.048792 | 0.37015 | 0.44082 | 0.02218 | -0.040072 | 0.063607 | -0.18947 | -0.00063412 | -0.00060947 | 1.6933 | 15.7937 | 16.6801 | 17.207 | 17.5306 | 17.4791 | 16.4273 | 14.7634 | 16.7952 | 17.1256 | 17.4255 | 17.4622 | 17.1728 | 16.3439 | 14.5398 | 21.9798 | 12.143 | 17.0654 | 12.7537 | 10.9817 | 13.3609 | 10.1824 | 15.8602 | 15.4999 | 15.3655 | 14.2705 | 14.4114 | 14.9325 |  |  |  | 21.5968 | 87.9581 | 71.2423 | 33.065 | -0.029531 | -0.19533 | 25.4332 |  |  | 10.8331 |  |  | 16.8878 | 16.1843 | 19.0406 | 16.3435 | 15.6667 | 16.2564 | 77.8694 | 100.0304 | 62.9006 | 63.6335 | 40.7724 |  | 24.4073 | 44.0789 | 25.201 | 31.6912 | 23.4372 | 76.0799 |  | 39.9055 |  |  | 13.2844 | 14.7003 | 27.7469 | [6 empty] | 26.8398 |  |  | 22.5246 |  |  | 13.1038 | 22.4344 | 111.4722 | 8.5275 | 18.7208 | 72.576 | 9.8277 | 17.435 | 79.3227 | 15.5078 | 62.2898 | 9.7722 | 55.1584 | 10.9542 | 57.1536 | 9.7188 | 19.7077 | 67.8196 | 15.3391 | 20.9043 | 88.6854 | 10.4178 | 18.6303 | 78.238 | 10.6412 | 54.4848 | 14.5606 | 65.5268 | 11.54 | 62.1297 | 0.40464 | 20.0468 | 0.60556 | 0.058748 | -37.8903 | 3.1226 | 90.89 | 49.17 | -0.75779 | -0.45917 | 0.21312 | -0.34866 | 0.25844 | 0.71182 | 0.7768 | -0.010092 | -0.075131 | 0.20945 | -0.57559 | -0.39938 | -0.025425 | 0.10938
42810.4439 | 338 | 18.4937 | 18.5786 | 18.5492 | 18.5483 | 17.8606 | 16.4633 | 14.5123 | 16.649 | 17.1246 | 17.2199 | 17.2298 | 16.748 | 15.7559 | 14.3772 | 14.8634 | 14.8691 | 15.4393 | 13.3069 | 13.6319 | 14.7114 |  |  |  | 16.5383 | 15.9321 | 17.5871 | 82.0539 | 76.5623 | 98.8299 | 17.1493 | 16.3064 | 16.6978 | 16.8226 | 16.1392 | 16.9828 | 23.1895 | 96.8252 |  | 44.4473 | 67.7825 | 69.0629 | 38.6657 |  | 6.7598 | 6.947 | 6.4204 | 6.9078 | 7.249 | 8.7001 | 26.6246 | 5.5187 | 6.6124 | 5.0127 | 7.0777 | 8.1084 | 42.2336 | 46.6963 | 42.9403 | 14.9704 |  |  | -0.38814 | 0.017831 | 0.030764 | -0.13208 | -0.058976 | -0.055 | 0.52099 | 0.009692 | 0.12028 | -0.61363 | -0.044815 | -0.00059633 | -0.00059962 | 1.7274 | 15.7892 | 16.6805 | 17.2127 | 17.5369 | 17.4805 | 16.4236 | 14.7659 | 16.7983 | 17.1221 | 17.4225 | 17.4556 | 17.1715 | 16.3433 | 14.5358 | 20.8206 | 11.7259 | 16.0543 | 12.943 | 11.4216 | 13.3825 | 10.1951 | 15.8531 | 15.489 | 15.3588 | 14.2655 | 14.4062 | 14.9346 |  |  |  | 21.665 | 88.0582 | 71.3277 | 33.3888 | -0.018185 | -0.034792 | 25.4672 |  |  | 10.8264 |  |  | 16.883 | 16.192 | 19.0678 | 16.3488 | 15.6633 | 16.2679 | 78.712 | 100.7987 | 63.334 | 64.0467 | 41.2429 |  | 24.488 | 44.9702 | 25.2736 | 33.5205 | 23.6623 | 77.5446 |  | 40.0647 |  |  | 13.3074 | 14.7095 | 28.4638 | [6 empty] | 27.8474 |  |  | 22.6334 |  |  | 13.1342 | 22.5337 | 113.0092 | 8.5224 | 19.2988 | 73.0884 | 9.8337 | 17.594 | 79.8032 | 15.5684 | 62.4255 | 9.7884 | 55.3005 | 10.9771 | 57.2763 | 9.7196 | 20.1057 | 68.1939 | 15.4182 | 21.1964 | 89.0589 | 10.4427 | 18.6956 | 78.7886 | 10.6582 | 54.7089 | 14.6121 | 65.8118 | 11.5594 | 62.4323 | 0.46184 | 20.0454 | 0.60487 | 0.057619 | -37.7835 | 3.1227 | 105.5 | 49.07 | -0.83737 | 0.15574 | 0.20457 | -0.42388 | -0.28413 | -0.27438 | 0.84448 | -0.020438 | -0.097434 | 0.16622 | -0.44426 | -0.28555 | 0.0073677 | 0.10267
42810.444 | 339 | 18.4889 | 18.5773 | 18.5574 | 18.5523 | 17.8532 | 16.4619 | 14.5142 | 16.6366 | 17.1366 | 17.2258 | 17.2268 | 16.7488 | 15.7624 | 14.3727 | 14.8617 | 14.8624 | 15.4333 | 13.302 | 13.6365 | 14.7159 |  |  |  | 16.5344 | 15.9337 | 17.5979 | 82.2905 | 77.008 | 97.825 | 17.136 | 16.3046 | 16.7034 | 16.8109 | 16.1435 | 16.99 | 23.2583 | 97.7782 |  | 44.6179 | 67.9504 | 69.3885 | 39.1137 |  | 6.7616 | 6.9534 | 6.4298 | 6.9227 | 7.2384 | 8.6952 | 26.4462 | 5.6246 | 6.6253 | 5.1507 | 7.0906 | 8.1083 | 42.2001 | 46.6779 | 42.9384 | 14.9666 |  |  | -0.25409 | 0.021771 | -0.02772 | -0.14062 | -0.11549 | -0.14108 | 0.57816 | 0.23706 | -0.043964 | 0.38502 | -0.065877 | -0.00058483 | -0.00060947 | 1.7735 | 15.7874 | 16.6687 | 17.2069 | 17.5289 | 17.4713 | 16.4206 | 14.7595 | 16.7911 | 17.12 | 17.4154 | 17.4539 | 17.1665 | 16.3359 | 14.5309 | 20.7808 | 11.408 | 14.7638 | 12.3505 | 11.2038 | 13.424 | 10.2068 | 15.8625 | 15.4976 | 15.3665 | 14.2738 | 14.4086 | 14.9431 |  |  |  | 21.7557 | 88.106 | 71.3819 | 34.3004 | 0.17996 | -0.25913 | 25.4345 |  |  | 10.8247 |  |  | 16.88 | 16.1996 | 19.0876 | 16.3472 | 15.652 | 16.2823 | 79.2197 | 101.3115 | 63.7806 | 64.4697 | 41.6815 |  | 24.5884 | 45.8649 | 25.3552 | 33.9065 | 23.8288 | 78.6131 |  | 40.2769 |  |  | 13.3115 | 14.7299 | 29.0395 | [6 empty] | 28.3142 |  |  | 22.7654 |  |  | 13.1684 | 22.6685 | 114.6825 | 8.5187 | 19.7527 | 73.5822 | 9.8316 | 17.8322 | 80.4313 | 15.6339 | 62.6591 | 9.8076 | 55.5048 | 10.9937 | 57.3992 | 9.7307 | 20.3649 | 68.4761 | 15.4924 | 21.4568 | 89.3797 | 10.4589 | 18.7965 | 79.2967 | 10.657 | 54.9286 | 14.6652 | 65.9691 | 11.5886 | 62.7375 | 0.27252 | 20.0469 | 0.60718 | 0.05788 | -37.8344 | 3.1227 | 110.96 | 50.29 | -0.6766 | 0.17209 | -0.19419 | -0.43737 | -0.39759 | -0.43945 | 0.88961 | -0.029231 | -0.11953 | 0.16111 | -0.43501 | -0.14081 | -0.0027587 | 0.080395
42810.444 | 340 | 18.4831 | 18.5684 | 18.5582 | 18.5535 | 17.8513 | 16.4647 | 14.5129 | 16.6369 | 17.1338 | 17.218 | 17.2239 | 16.7418 | 15.7619 | 14.3781 | 14.8602 | 14.8661 | 15.432 | 13.3047 | 13.6369 | 14.7142 |  |  |  | 16.5419 | 15.9336 | 17.6168 | 82.4178 | 77.4425 | 96.7603 | 17.1467 | 16.2977 | 16.7106 | 16.815 | 16.1347 | 16.9996 | 23.3548 | 98.5623 |  | 44.7926 | 68.1598 | 69.8322 | 42.1822 |  | 6.7634 | 6.9572 | 6.4337 | 6.9213 | 7.2298 | 8.6519 | 26.2304 | 5.6752 | 6.6249 | 5.1911 | 7.0901 | 8.1111 | 42.1949 | 46.6568 | 42.9414 | 14.9618 |  |  | -0.41508 | -0.11819 | 0.076104 | 0.16297 | -0.15229 | 0.25253 | 0.61562 | 0.037292 | -0.2265 | -0.50726 | -0.21768 | -0.00058483 | -0.00061276 | 1.8329 | 15.788 | 16.669 | 17.2067 | 17.5227 | 17.4719 | 16.4182 | 14.7603 | 16.7903 | 17.1262 | 17.4159 | 17.4548 | 17.1711 | 16.3309 | 14.529 | 21.6279 | 12.4565 | 14.5706 | 11.7718 | 10.6858 | 13.4863 | 10.2261 | 15.8561 | 15.4994 | 15.3584 | 14.2718 | 14.4146 | 14.9428 |  |  |  | 21.8595 | 88.2742 | 71.8042 | 35.4651 | -0.014336 | -0.031593 | 25.4098 |  |  | 10.8283 |  |  | 16.8839 | 16.2025 | 19.1111 | 16.3471 | 15.6573 | 16.2867 | 79.5792 | 102.2995 | 64.2151 | 64.879 | 42.6904 |  | 24.6979 | 46.208 | 25.431 | 34.0497 | 23.9648 | 80.09 |  | 40.4811 |  |  | 13.3115 | 14.7496 | 29.0759 | [6 empty] | 27.9746 |  |  | 22.917 |  |  | 13.2062 | 22.8742 | 116.1327 | 8.5279 | 20.0862 | 73.9835 | 9.8367 | 18.0313 | 81.0866 | 15.7191 | 62.9171 | 9.8232 | 55.7046 | 11.0156 | 57.5503 | 9.743 | 20.5326 | 68.8032 | 15.5626 | 21.5771 | 89.6327 | 10.4696 | 18.9749 | 79.7925 | 10.6515 | 55.1217 | 14.7152 | 66.0712 | 11.6113 | 63.0019 | 0.37748 | 20.0467 | 0.60596 | 0.057562 | -37.8737 | 3.1227 | 93.18 | 49.11 | -0.86353 | -0.40098 | 0.32176 | 0.47084 | -0.45653 | 0.58789 | 0.9179 | -0.053559 | -0.1265 | 0.16172 | -0.52187 | -0.11709 | -0.084747 | 0.051529
42810.444 | 341 | 18.4796 | 18.5744 | 18.5589 | 18.548 | 17.8493 | 16.4593 | 14.5194 | 16.639 | 17.1322 | 17.2266 | 17.2234 | 16.7467 | 15.7655 | 14.3763 | 14.8571 | 14.8618 | 15.4294 | 13.3002 | 13.6326 | 14.7161 |  |  |  | 16.5378 | 15.9306 | 17.6287 | 82.7515 | 77.8943 | 98.4105 | 17.1338 | 16.2922 | 16.7175 | 16.8082 | 16.1359 | 17.008 | 23.4359 | 99.1307 |  | 44.9696 | 68.4385 | 70.4008 | 41.99 |  | 6.7793 | 6.9755 | 6.4482 | 6.9173 | 7.2287 | 8.6441 | 26.3408 | 5.6895 | 6.639 | 5.2261 | 7.096 | 8.1056 | 42.1945 | 46.6301 | 42.9423 | 14.9611 |  |  | -0.47619 | -0.29101 | 0.060332 | -0.05257 | -0.04912 | -0.09574 | 0.45397 | 0.2594 | -0.37984 | -0.035839 | -0.17198 | -0.00060783 | -0.00061933 | 1.8274 | 15.7924 | 16.6676 | 17.2073 | 17.5217 | 17.4696 | 16.422 | 14.7589 | 16.7936 | 17.1264 | 17.4214 | 17.4585 | 17.1725 | 16.3355 | 14.5328 | 21.1848 | 12.8611 | 15.3653 | 11.4483 | 10.2198 | 13.522 | 10.2572 | 15.8692 | 15.5012 | 15.3676 | 14.2767 | 14.4189 | 14.9507 |  |  |  | 21.9473 | 88.5231 | 72.1501 | 35.6213 | 0.080481 | -0.22996 | 25.4073 |  |  | 10.8342 |  |  | 16.8816 | 16.1976 | 19.1277 | 16.3427 | 15.6655 | 16.298 | 80.0413 | 103.1861 | 64.6923 | 65.3052 | 43.8499 |  | 24.8168 | 46.1773 | 25.5042 | 34.415 | 24.097 | 80.8764 |  | 40.6459 |  |  | 13.316 | 14.7697 | 29.0983 | [6 empty] | 27.962 |  |  | 23.0509 |  |  | 13.2473 | 23.1586 | 117.3845 | 8.5329 | 20.4174 | 74.3207 | 9.8444 | 18.2515 | 81.716 | 15.7993 | 63.0934 | 9.8323 | 55.9215 | 11.0378 | 57.7142 | 9.7526 | 20.7685 | 69.2049 | 15.6218 | 21.6504 | 89.9757 | 10.4879 | 19.1582 | 80.536 | 10.6511 | 55.3146 | 14.7663 | 66.1506 | 11.6296 | 63.2402 | 0.42178 | 20.0454 | 0.60946 | 0.057583 | -37.8216 | 3.1228 | 101.46 | 49.15 | -0.92698 | -0.62922 | 0.2865 | -0.26743 | -0.25928 | -0.36198 | 0.78822 | -0.081754 | -0.12317 | 0.15603 | -0.46849 | -0.20178 | -0.076675 | 0.050144
42810.444 | 342 | 18.4814 | 18.5688 | 18.5617 | 18.5544 | 17.8527 | 16.455 | 14.5157 | 16.6435 | 17.1367 | 17.2254 | 17.2195 | 16.7453 | 15.7688 | 14.3777 | 14.8604 | 14.8521 | 15.4233 | 13.2927 | 13.6336 | 14.7212 |  |  |  | 16.5311 | 15.9232 | 17.6374 | 83.3096 | 78.359 | 100.3006 | 17.1347 | 16.2988 | 16.7242 | 16.8085 | 16.1393 | 17.0193 | 23.5003 | 100.6952 |  | 45.2003 | 68.8402 | 70.971 | 41.3847 |  | 6.7896 | 6.9794 | 6.4532 | 6.9235 | 7.2306 | 8.6671 | 26.6155 | 5.6482 | 6.6326 | 5.2633 | 7.1013 | 8.1048 | 42.1994 | 46.6153 | 42.9554 | 14.9597 |  |  | -0.32177 | -0.13528 | -0.081604 | 0.028914 | -0.092488 | 0.13162 | 0.52822 | 0.49924 | -0.90604 | -0.16445 | -0.2767 | -0.00059797 | -0.00063083 | 1.772 | 15.7971 | 16.6751 | 17.2114 | 17.5267 | 17.478 | 16.4274 | 14.7672 | 16.7938 | 17.1276 | 17.4323 | 17.461 | 17.1743 | 16.3397 | 14.5376 | 21.8505 | 12.4808 | 14.8453 | 11.3749 | 10.2065 | 13.5716 | 10.2787 | 15.8623 | 15.4899 | 15.3628 | 14.2747 | 14.4181 | 14.957 |  |  |  | 22.0262 | 88.8984 | 72.753 | 35.7149 | 0.063868 | -0.12776 | 25.4488 |  |  | 10.8397 |  |  | 16.8792 | 16.2036 | 19.1463 | 16.3392 | 15.6692 | 16.3109 | 80.4935 | 104.1687 | 65.1427 | 65.6894 | 44.5702 |  | 24.9464 | 46.6357 | 25.5816 | 34.4862 | 24.2395 | 81.5658 |  | 40.8254 |  |  | 13.3221 | 14.7741 | 29.265 | [6 empty] | 27.8653 |  |  | 23.1872 |  |  | 13.2946 | 23.4462 | 118.401 | 8.5625 | 20.6762 | 74.7032 | 9.8619 | 18.5378 | 82.5053 | 15.8724 | 63.3039 | 9.8512 | 56.1868 | 11.0611 | 57.8777 | 9.7554 | 21.0747 | 69.5671 | 15.7001 | 21.8206 | 90.5762 | 10.5122 | 19.305 | 81.27 | 10.6601 | 55.5527 | 14.8159 | 66.1717 | 11.6561 | 63.4804 | 0.42756 | 20.0467 | 0.60775 | 0.061397 | -37.8385 | 3.1227 | 102.64 | 50.12 | -0.76393 | -0.429 | -0.3332 | 0.19834 | -0.35579 | 0.42444 | 0.85028 | -0.097381 | -0.13328 | 0.15886 | -0.53667 | -0.14151 | -0.057689 | 0.050196
42810.444 | 343 | 18.4851 | 18.5705 | 18.5617 | 18.5504 | 17.859 | 16.4586 | 14.5132 | 16.6397 | 17.1351 | 17.2255 | 17.2206 | 16.7438 | 15.7607 | 14.3793 | 14.8609 | 14.8631 | 15.4322 | 13.2966 | 13.6415 | 14.7244 |  |  |  | 16.5369 | 15.9287 | 17.6598 | 83.8868 | 78.8044 | 101.5225 | 17.1349 | 16.2998 | 16.7415 | 16.8168 | 16.1441 | 17.0296 | 23.5705 | 102.1688 |  | 45.4327 | 69.3471 | 71.505 | 40.4518 |  | 6.783 | 6.9912 | 6.454 | 6.929 | 7.2439 | 8.6953 | 26.8076 | 5.6299 | 6.638 | 5.3155 | 7.1113 | 8.1137 | 42.2055 | 46.6124 | 42.9581 | 14.959 |  |  | -0.52153 | -0.17076 | 0.034048 | -0.16691 | -0.047148 | -0.10034 | 0.48682 | 0.19697 | -0.53552 | 0.20186 | -0.26358 | -0.00063083 | -0.00059633 | 1.7663 | 15.8077 | 16.6822 | 17.2263 | 17.5434 | 17.4932 | 16.4427 | 14.7754 | 16.8012 | 17.1398 | 17.4314 | 17.475 | 17.1855 | 16.3525 | 14.5456 | 23.3397 | 12.6194 | 14.4018 | 10.8981 | 10.2599 | 13.6504 | 10.3003 | 15.8678 | 15.4874 | 15.3646 | 14.2741 | 14.4216 | 14.9626 |  |  |  | 22.1068 | 89.3818 | 73.4175 | 36.033 | 0.39836 | 0.0005894 | 25.5564 |  |  | 10.8415 |  |  | 16.8782 | 16.2022 | 19.1673 | 16.3382 | 15.666 | 16.3173 | 80.9314 | 104.9655 | 65.5554 | 66.0196 | 45.1367 |  | 25.068 | 47.6472 | 25.6665 | 34.599 | 24.3878 | 81.6788 |  | 41.0135 |  |  | 13.3341 | 14.8017 | 29.5487 | [6 empty] | 27.6199 |  |  | 23.3652 |  |  | 13.3315 | 23.6219 | 119.7409 | 8.5752 | 20.8483 | 75.2114 | 9.8714 | 18.9296 | 83.1831 | 15.9578 | 63.5154 | 9.8718 | 56.462 | 11.0821 | 58.0054 | 9.7817 | 21.285 | 69.8144 | 15.794 | 22.0547 | 91.2666 | 10.5294 | 19.4389 | 81.9774 | 10.6767 | 55.871 | 14.8756 | 66.2449 | 11.6802 | 63.8226 | 0.4969 | 20.0467 | 0.6081 | 0.058669 | -37.9034 | 3.1227 | 115.37 | 49.27 | -0.97416 | -0.482 | 0.21523 | -0.47653 | -0.25404 | -0.3706 | 0.81632 | -0.10901 | -0.15851 | 0.16073 | -0.69297 | -0.089716 | -0.029412 | 0.044067
42810.444 | 344 | 18.475 | 18.5705 | 18.5495 | 18.5498 | 17.8538 | 16.4546 | 14.513 | 16.631 | 17.1314 | 17.2171 | 17.2218 | 16.7407 | 15.7524 | 14.3696 | 14.8566 | 14.8614 | 15.4215 | 13.3003 | 13.637 | 14.732 |  |  |  | 16.5245 | 15.9302 | 17.668 | 84.3599 | 79.2909 | 101.2534 | 17.1277 | 16.2952 | 16.7467 | 16.8093 | 16.145 | 17.0394 | 23.6408 | 103.742 |  | 45.6592 | 69.8603 | 72.086 | 40.5738 |  | 6.7845 | 6.9882 | 6.4565 | 6.9523 | 7.2512 | 8.6907 | 27.1676 | 5.4602 | 6.6399 | 5.3695 | 7.1143 | 8.1093 | 42.1967 | 46.5936 | 42.9566 | 14.9452 |  |  | -0.49656 | -0.15368 | -0.048092 | 0.16165 | 0.065876 | 0.19273 | 0.5072 | 0.056348 | -0.4137 | -1.8596 | -0.25047 | -0.00061276 | -0.00057169 | 1.7969 | 15.7814 | 16.6744 | 17.2049 | 17.5343 | 17.4776 | 16.431 | 14.7653 | 16.7959 | 17.1293 | 17.4231 | 17.4642 | 17.1765 | 16.3362 | 14.5397 | 25.5605 | 13.7922 | 15.3011 | 10.682 | 10.3277 | 13.7456 | 10.3245 | 15.8439 | 15.4909 | 15.3543 | 14.2657 | 14.4207 | 14.9686 |  |  |  | 22.1819 | 89.9477 | 73.7715 | 36.6288 | 0.35683 | 0.013575 | 25.7419 |  |  | 10.8473 |  |  | 16.8844 | 16.198 | 19.186 | 16.3452 | 15.6693 | 16.326 | 81.4648 | 105.9014 | 65.9289 | 66.342 | 46.0193 |  | 25.1848 | 48.5163 | 25.7352 | 35.1074 | 24.5305 | 82.4016 |  | 41.1905 |  |  | 13.3233 | 14.843 | 29.6871 | [6 empty] | 27.4949 |  |  | 23.492 |  |  | 13.387 | 23.8795 | 120.7449 | 8.5863 | 21.0043 | 75.6145 | 9.8647 | 19.3241 | 83.9626 | 16.0521 | 63.6653 | 9.9131 | 56.5927 | 11.1029 | 58.1573 | 9.8006 | 21.37 | 70.1744 | 15.8614 | 22.3196 | 91.7383 | 10.5424 | 19.5521 | 82.6706 | 10.6947 | 56.2086 | 14.9352 | 66.2906 | 11.7079 | 64.2756 | 0.39655 | 20.0472 | 0.60904 | 0.059783 | -37.9186 | 3.1227 | 126.25 | 49.49 | -0.95022 | -0.45725 | -0.25579 | 0.46897 | 0.30028 | 0.51362 | 0.83321 | -0.12958 | -0.18033 | 0.15143 | -0.92864 | -0.18683 | -0.03043 | 0.030041
42810.444 | 345 | 18.4809 | 18.5734 | 18.5537 | 18.5456 | 17.8544 | 16.4563 | 14.5121 | 16.6305 | 17.1288 | 17.2176 | 17.2201 | 16.7413 | 15.7549 | 14.3744 | 14.8513 | 14.8547 | 15.4215 | 13.2926 | 13.6469 | 14.7397 |  |  |  | 16.5231 | 15.9364 | 17.6858 | 84.7616 | 79.7043 | 101.2054 | 17.1311 | 16.2925 | 16.7521 | 16.8163 | 16.1399 | 17.0494 | 23.7183 | 105.8712 |  | 45.9228 | 70.3828 | 72.659 | 41.8326 |  | 6.8023 | 7.0055 | 6.4617 | 6.9673 | 7.2875 | 8.7141 | 27.373 | 5.3089 | 6.6472 | 5.396 | 7.1277 | 8.1092 | 42.1987 | 46.5988 | 42.9571 | 14.9424 |  |  | -0.46633 | 0.037543 | 0.053104 | 0.27467 | 0.21504 | 0.20916 | 0.38366 | 0.11878 | -0.19711 | 0.36572 | -0.092106 | -0.00059469 | -0.00063083 | 1.7448 | 15.796 | 16.6844 | 17.2137 | 17.5391 | 17.4833 | 16.4268 | 14.7669 | 16.7992 | 17.1367 | 17.4234 | 17.4688 | 17.1799 | 16.3447 | 14.5437 | 28.4117 | 14.9884 | 17.0132 | 11.1968 | 10.3007 | 13.8775 | 10.3717 | 15.8493 | 15.491 | 15.351 | 14.2717 | 14.4184 | 14.9796 |  |  |  | 22.2748 | 90.3904 | 73.8459 | 37.5694 | 0.51769 | -0.086171 | 25.8868 |  |  | 10.8575 |  |  | 16.8782 | 16.2035 | 19.2063 | 16.3379 | 15.6662 | 16.3376 | 82.0052 | 106.9026 | 66.3298 | 66.7048 | 47.3245 |  | 25.3083 | 49.0012 | 25.8197 | 35.5818 | 24.6893 | 83.4486 |  | 41.3895 |  |  | 13.3399 | 14.8626 | 30.0459 | [6 empty] | 27.4827 |  |  | 23.6497 |  |  | 13.4384 | 24.2471 | 121.6939 | 8.5893 | 21.1199 | 75.9348 | 9.8718 | 19.5605 | 84.6389 | 16.1366 | 63.8436 | 9.9398 | 56.7391 | 11.1327 | 58.3152 | 9.8238 | 21.3629 | 70.6223 | 15.944 | 22.6532 | 92.3979 | 10.5585 | 19.7572 | 83.5297 | 10.7271 | 56.5278 | 15.0208 | 66.3038 | 11.7364 | 64.6911 | 0.36728 | 20.0465 | 0.60855 | 0.059697 | -37.9514 | 3.1228 | 110.34 | 49.62 | -0.92078 | 0.22601 | 0.2688 | 0.61133 | 0.54256 | 0.53509 | 0.7247 | -0.16166 | -0.19094 | 0.14361 | -1.2301 | -0.37156 | -0.062785 | 0.0070398
42810.444 | 346 | 18.4859 | 18.5722 | 18.5623 | 18.5482 | 17.8538 | 16.4592 | 14.5169 | 16.636 | 17.1315 | 17.2279 | 17.2238 | 16.7474 | 15.7583 | 14.382 | 14.8516 | 14.8756 | 15.4425 | 13.3055 | 13.6556 | 14.7494 |  |  |  | 16.5392 | 15.9416 | 17.7057 | 85.1411 | 80.1475 | 101.5178 | 17.1228 | 16.29 | 16.7633 | 16.8029 | 16.1372 | 17.0594 | 23.7977 | 106.8938 |  | 46.1462 | 70.8543 | 73.1553 | 41.4393 |  | 6.8048 | 7.0154 | 6.4661 | 6.9686 | 7.2964 | 8.7354 | 27.3792 | 5.2216 | 6.6506 | 5.3888 | 7.1368 | 8.1073 | 42.2023 | 46.6028 | 42.9468 | 14.9345 |  |  | -0.39865 | -0.18456 | -0.057948 | 0.11631 | -0.05372 | 0.28342 | 0.50391 | -0.08756 | -0.1183 | -0.49341 | -0.10323 | -0.00058976 | -0.00059962 | 1.7377 | 15.7945 | 16.6828 | 17.2209 | 17.5369 | 17.4885 | 16.424 | 14.7721 | 16.7995 | 17.1349 | 17.4216 | 17.4676 | 17.1763 | 16.3443 | 14.5369 | 31.5536 | 16.0889 | 19.1895 | 12.241 | 10.1007 | 14.0441 | 10.4575 | 15.8563 | 15.496 | 15.3626 | 14.2775 | 14.4247 | 14.986 |  |  |  | 22.3702 | 90.6987 | 73.773 | 38.5044 | 0.48771 | 0.25861 | 26.1413 |  |  | 10.8655 |  |  | 16.8831 | 16.2106 | 19.2308 | 16.3394 | 15.6712 | 16.3503 | 82.4507 | 107.7051 | 66.83 | 67.1603 | 47.9306 |  | 25.4223 | 49.2269 | 25.9137 | 36.2086 | 24.854 | 84.8415 |  | 41.5711 |  |  | 13.3699 | 14.8741 | 30.2865 | [6 empty] | 27.61 |  |  | 23.8481 |  |  | 13.4952 | 24.6345 | 122.542 | 8.6033 | 21.3191 | 76.5071 | 9.8976 | 19.6929 | 85.1825 | 16.2166 | 64.0473 | 9.9656 | 57.1339 | 11.148 | 58.5599 | 9.851 | 21.3403 | 70.9616 | 16.0315 | 22.9243 | 92.9519 | 10.5817 | 19.9493 | 84.1818 | 10.7559 | 56.859 | 15.0954 | 66.4189 | 11.7681 | 64.8598 | 0.46069 | 20.0469 | 0.6089 | 0.057156 | -37.9346 | 3.1228 | 115.87 | 49.04 | -0.8517 | -0.50112 | -0.2808 | 0.39782 | -0.27119 | 0.6229 | 0.83058 | -0.17464 | -0.19403 | 0.13176 | -1.5598 | -0.60341 | -0.049181 | -0.015729
42810.4441 | 347 | 18.466 | 18.5633 | 18.5434 | 18.5431 | 17.8401 | 16.4519 | 14.5042 | 16.6278 | 17.13 | 17.2101 | 17.2162 | 16.7396 | 15.7563 | 14.3702 | 14.8583 | 14.8676 | 15.4427 | 13.3015 | 13.6537 | 14.7621 |  |  |  | 16.5357 | 15.941 | 17.7232 | 85.5829 | 80.5771 | 102.1959 | 17.1339 | 16.2991 | 16.7749 | 16.8131 | 16.14 | 17.0776 | 23.8748 | 107.223 |  | 46.3571 | 71.3683 | 73.6599 | 40.4834 |  | 6.7979 | 7.0271 | 6.4598 | 6.9664 | 7.2998 | 8.7278 | 27.2304 | 5.1861 | 6.6525 | 5.2877 | 7.1483 | 8.1154 | 42.1912 | 46.6067 | 42.9254 | 14.9326 |  |  | -0.44268 | -0.18325 | 0.043248 | -0.14785 | 0.17298 | -0.0274 | 0.38037 | 0.18186 | -0.1002 | -0.20452 | -0.13125 | -0.00057826 | -0.00060126 | 1.7144 | 15.7897 | 16.6743 | 17.2121 | 17.5252 | 17.4841 | 16.4198 | 14.7712 | 16.7876 | 17.1337 | 17.4197 | 17.4595 | 17.1738 | 16.3378 | 14.53 | 33.5422 | 16.8385 | 22.3181 | 13.8313 | 10.9521 | 14.2007 | 10.5457 | 15.856 | 15.4858 | 15.3601 | 14.267 | 14.4235 | 14.9845 |  |  |  | 22.4732 | 91.0373 | 73.6829 | 39.2879 | 0.43908 | 0.19029 | 26.415 |  |  | 10.8646 |  |  | 16.8898 | 16.2146 | 19.2515 | 16.3442 | 15.6676 | 16.3644 | 82.8204 | 108.5514 | 67.3144 | 67.6672 | 47.9359 |  | 25.531 | 49.9628 | 26.0117 | 36.4751 | 25.0132 | 85.6136 |  | 41.7466 |  |  | 13.4201 | 14.8914 | 30.4693 | [6 empty] | 27.689 |  |  | 24.0148 |  |  | 13.5169 | 25.0291 | 123.4965 | 8.5752 | 21.5527 | 77.0673 | 9.8989 | 19.9252 | 85.7317 | 16.2601 | 64.2299 | 9.9707 | 57.6735 | 11.1685 | 59.0881 | 9.8471 | 21.4733 | 71.2847 | 16.1183 | 23.1863 | 93.4299 | 10.5866 | 20.1602 | 84.6863 | 10.7564 | 57.0783 | 15.184 | 66.4254 | 11.7917 | 65.1802 | 0.43392 | 20.0475 | 0.60855 | 0.057967 | -37.9421 | 3.1228 | 126.26 | 49.93 | -0.89831 | -0.49935 | 0.24259 | -0.44853 | 0.48663 | -0.19367 | 0.72161 | -0.17111 | -0.21115 | 0.12974 | -1.7625 | -0.94077 | -0.020031 | -0.034024
42810.4441 | 348 | 18.4808 | 18.5727 | 18.5527 | 18.5444 | 17.8511 | 16.4576 | 14.5092 | 16.629 | 17.1403 | 17.2193 | 17.2224 | 16.7478 | 15.7602 | 14.3727 | 14.8522 | 14.8589 | 15.4309 | 13.2919 | 13.6385 | 14.7547 |  |  |  | 16.5264 | 15.9343 | 17.7237 | 86.2167 | 80.8974 | 104.8204 | 17.1273 | 16.2958 | 16.7817 | 16.8069 | 16.1455 | 17.0932 | 23.9384 | 107.9495 |  | 46.5829 | 71.8746 | 74.1686 | 40.3154 |  | 6.7896 | 7.0225 | 6.465 | 6.9734 | 7.3107 | 8.7049 | 27.0684 | 5.2155 | 6.6468 | 5.2602 | 7.1419 | 8.1315 | 42.1986 | 46.5876 | 42.9072 | 14.935 |  |  | -0.57673 | 0.008631 | 0.042592 | 0.065054 | 0.09676 | 0.26304 | 0.37577 | 0.32774 | -0.45165 | -0.45607 | -0.20656 | -0.00055198 | -0.00062754 | 1.7249 | 15.7856 | 16.6717 | 17.2046 | 17.5244 | 17.4723 | 16.4203 | 14.7599 | 16.7868 | 17.1262 | 17.4109 | 17.4523 | 17.1666 | 16.332 | 14.5281 | 34.3426 | 16.3836 | 23.9182 | 15.5689 | 12.853 | 14.3322 | 10.6271 | 15.8544 | 15.4883 | 15.3576 | 14.2674 | 14.4162 | 14.9927 |  |  |  | 22.5746 | 91.3907 | 73.5455 | 39.9952 | 0.16861 | 0.017339 | 26.6214 |  |  | 10.8614 |  |  | 16.8897 | 16.2202 | 19.27 | 16.3477 | 15.6683 | 16.3739 | 83.2517 | 109.1595 | 67.7989 | 68.1241 | 49.0938 |  | 25.6352 | 50.369 | 26.0968 | 37.0108 | 25.1891 | 85.8758 |  | 41.9514 |  |  | 13.4269 | 14.9178 | 30.5424 | [6 empty] | 28.2533 |  |  | 24.189 |  |  | 13.5622 | 25.4775 | 124.1989 | 8.5612 | 21.5209 | 77.6882 | 9.9175 | 20.2097 | 86.2401 | 16.321 | 64.4266 | 9.9991 | 57.9061 | 11.1932 | 59.4552 | 9.8364 | 21.643 | 71.741 | 16.1779 | 23.4289 | 93.6624 | 10.5994 | 20.3864 | 85.5871 | 10.7614 | 57.368 | 15.2438 | 66.5532 | 11.811 | 65.5536 | 0.44855 | 20.0462 | 0.60849 | 0.055745 | -38.0266 | 3.1229 | 122.56 | 49.22 | -1.0289 | 0.10837 | 0.24074 | 0.29752 | 0.36394 | 0.60006 | 0.7172 | -0.19975 | -0.21955 | 0.1208 | -1.8361 | -1.1091 | -0.013217 | -0.050263
42810.4441 | 349 | 18.4739 | 18.5699 | 18.557 | 18.5417 | 17.8468 | 16.4594 | 14.5131 | 16.6352 | 17.1304 | 17.2238 | 17.2189 | 16.7406 | 15.757 | 14.3676 | 14.8571 | 14.8635 | 15.4365 | 13.3045 | 13.6531 | 14.7654 |  |  |  | 16.5329 | 15.9403 | 17.7471 | 86.998 | 81.223 | 107.1566 | 17.12 | 16.285 | 16.7875 | 16.8045 | 16.1395 | 17.0927 | 24.0217 | 108.0975 |  | 46.8217 | 72.367 | 74.6869 | 42.3316 |  | 6.7994 | 7.0439 | 6.4754 | 6.9735 | 7.3224 | 8.7115 | 27.8255 | 5.2772 | 6.6659 | 5.2404 | 7.1617 | 8.1325 | 42.1914 | 46.5771 | 42.8816 | 14.9324 |  |  | -0.71801 | 0.083543 | 0.02682 | -0.11039 | 0.11844 | 0.068536 | 0.34489 | 0.40593 | -0.42071 | 1.0941 | -0.25822 | -0.0006029 | -0.00061933 | 1.7668 | 15.7886 | 16.6751 | 17.2092 | 17.5296 | 17.4719 | 16.4182 | 14.7587 | 16.7908 | 17.1256 | 17.4161 | 17.4495 | 17.1718 | 16.3395 | 14.5341 | 33.1615 | 15.8247 | 23.21 | 15.6351 | 13.8244 | 14.4325 | 10.6936 | 15.8496 | 15.4876 | 15.3644 | 14.2717 | 14.4342 | 15.0058 |  |  |  | 22.7002 | 91.7324 | 73.5928 | 41.0263 | 0.23669 | -0.04025 | 26.8521 |  |  | 10.8631 |  |  | 16.8808 | 16.2173 | 19.2876 | 16.343 | 15.6706 | 16.3804 | 83.8589 | 109.8464 | 68.3118 | 68.6043 | 49.7124 |  | 25.7517 | 50.9072 | 26.1824 | 37.6074 | 25.3639 | 86.1237 |  | 42.1665 |  |  | 13.3915 | 14.944 | 30.6377 | [6 empty] | 28.6801 |  |  | 24.3355 |  |  | 13.5955 | 25.8481 | 125.1593 | 8.5275 | 21.5159 | 78.4418 | 9.9337 | 20.281 | 87.0576 | 16.3718 | 64.6373 | 10.021 | 58.1036 | 11.2205 | 59.7008 | 9.8435 | 21.694 | 72.4379 | 16.2391 | 23.6844 | 94.1047 | 10.6062 | 20.5545 | 86.3198 | 10.7869 | 57.6757 | 15.2975 | 66.7668 | 11.8334 | 65.8383 | 0.37421 | 20.0473 | 0.61126 | 0.057055 | -37.864 | 3.1228 | 141.48 | 48.46 | -1.1516 | 0.33717 | 0.19104 | -0.38759 | 0.40266 | 0.3063 | 0.68711 | -0.21299 | -0.2316 | 0.11014 | -1.6932 | -1.0227 | -0.066417 | -0.074679
42810.4441 | 350 | 18.4788 | 18.572 | 18.5616 | 18.5398 | 17.8524 | 16.4598 | 14.5199 | 16.6476 | 17.1255 | 17.2261 | 17.2211 | 16.7438 | 15.7548 | 14.3739 | 14.8563 | 14.8632 | 15.4348 | 13.303 | 13.6531 | 14.7717 |  |  |  | 16.529 | 15.9383 | 17.7671 | 87.7381 | 81.6003 | 107.9553 | 17.1273 | 16.2965 | 16.8039 | 16.8155 | 16.1444 | 17.1093 | 24.1267 | 108.6801 |  | 47.0645 | 72.8488 | 75.1757 | 45.0576 |  | 6.8032 | 7.0492 | 6.4688 | 6.9712 | 7.3288 | 8.709 | 27.9842 | 5.29 | 6.669 | 5.2021 | 7.1772 | 8.1296 | 42.1875 | 46.5703 | 42.8558 | 14.9349 |  |  | -0.35791 | 0.20577 | 0.094504 | -0.20765 | 0.027764 | 0.023196 | 0.47105 | 0.37176 | -0.48804 | -1.0303 | -0.14436 | -0.00061276 | -0.00060126 | 1.761 | 15.7949 | 16.6788 | 17.2086 | 17.5374 | 17.4867 | 16.4274 | 14.7647 | 16.8007 | 17.1317 | 17.4212 | 17.4634 | 17.1722 | 16.3371 | 14.5295 | 31.7999 | 15.6854 | 22.4485 | 15.25 | 13.6234 | 14.5113 | 10.7479 | 15.8544 | 15.4816 | 15.3562 | 14.2577 | 14.4253 | 15.0042 |  |  |  | 22.7909 | 91.9817 | 73.6443 | 41.6748 | 0.13721 | -0.033475 | 27.0615 |  |  | 10.8639 |  |  | 16.8813 | 16.219 | 19.3075 | 16.3385 | 15.6701 | 16.3882 | 84.462 | 110.7196 | 68.7915 | 69.1573 | 49.2015 |  | 25.8722 | 51.7527 | 26.281 | 38.2027 | 25.5475 | 87.2364 |  | 42.3769 |  |  | 13.4098 | 14.9811 | 30.7074 | [6 empty] | 28.6964 |  |  | 24.4586 |  |  | 13.6349 | 26.2144 | 125.9363 | 8.5207 | 21.6978 | 79.1574 | 9.9592 | 20.2768 | 87.7719 | 16.4426 | 64.9131 | 10.0179 | 58.3413 | 11.2282 | 59.8691 | 9.8519 | 21.6529 | 72.9785 | 16.3171 | 23.8991 | 94.567 | 10.626 | 20.6975 | 86.8447 | 10.8202 | 57.9359 | 15.3432 | 67.1751 | 11.8601 | 66.0931 | 0.4447 | 20.0464 | 0.61247 | 0.057996 | -37.875 | 3.1229 | 131.75 | 49.7 | -0.81391 | 0.52916 | 0.35861 | -0.53158 | 0.19495 | 0.17819 | 0.803 | -0.19472 | -0.25175 | 0.099813 | -1.5327 | -0.93173 | -0.13859 | -0.089639
42810.4441 | 351 | 18.4747 | 18.5786 | 18.5579 | 18.5461 | 17.8548 | 16.4665 | 14.5186 | 16.6411 | 17.1293 | 17.2251 | 17.2251 | 16.7454 | 15.7558 | 14.3736 | 14.8557 | 14.8699 | 15.4395 | 13.3025 | 13.6568 | 14.7821 |  |  |  | 16.5282 | 15.9418 | 17.7805 | 88.3492 | 81.9471 | 108.6375 | 17.1105 | 16.2883 | 16.8042 | 16.8098 | 16.1432 | 17.116 | 24.224 | 109.6969 |  | 47.3233 | 73.3695 | 75.5984 | 48.6082 |  | 6.8032 | 7.05 | 6.4691 | 6.9717 | 7.3383 | 8.7247 | 29.0376 | 5.1956 | 6.6707 | 5.2202 | 7.1808 | 8.1346 | 42.1661 | 46.5546 | 42.8193 | 14.946 |  |  | -0.55767 | 0.039515 | 0.075448 | -0.15179 | 0.04682 | 0.16448 | 0.46645 | 0.31985 | -0.38043 | -0.23347 | -0.044815 | -0.0006259 | -0.00064726 | 1.7592 | 15.785 | 16.6687 | 17.1986 | 17.5297 | 17.4756 | 16.4187 | 14.7603 | 16.7925 | 17.1243 | 17.4221 | 17.4647 | 17.171 | 16.3494 | 14.5276 | 31.2772 | 15.6642 | 22.4456 | 14.899 | 13.16 | 14.6168 | 10.8024 | 15.8516 | 15.487 | 15.359 | 14.2669 | 14.4245 | 15.0039 |  |  |  | 22.8811 | 92.3741 | 73.7005 | 41.7288 | 0.28956 | -0.13266 | 27.2544 |  |  | 10.8562 |  |  | 16.8762 | 16.2151 | 19.3298 | 16.3372 | 15.6674 | 16.3945 | 85.1321 | 111.2787 | 69.2119 | 69.7386 | 49.167 |  | 25.9729 | 52.2282 | 26.3708 | 38.8596 | 25.7194 | 87.3124 |  | 42.5915 |  |  | 13.4311 | 15.0125 | 30.8316 | [6 empty] | 28.9347 |  |  | 24.5741 |  |  | 13.664 | 26.5543 | 126.9001 | 8.4987 | 21.8236 | 79.606 | 9.9844 | 20.4875 | 88.3582 | 16.5133 | 65.1793 | 10.0177 | 58.5688 | 11.2494 | 60.0981 | 9.8547 | 21.6772 | 73.3443 | 16.3893 | 24.178 | 94.789 | 10.6404 | 20.8404 | 87.4379 | 10.8399 | 58.1902 | 15.388 | 67.4039 | 11.8869 | 66.3925 | 0.44027 | 20.0475 | 0.6133 | 0.058886 | -37.8921 | 3.1228 | 130.64 | 49.1 | -1.0169 | 0.23189 | 0.32042 | -0.45449 | 0.25317 | 0.47451 | 0.7991 | -0.19036 | -0.26192 | 0.087382 | -1.4623 | -0.92508 | -0.23394 | -0.088104
42810.4441 | 352 | 18.4772 | 18.576 | 18.5508 | 18.5406 | 17.8508 | 16.4595 | 14.5146 | 16.6334 | 17.1301 | 17.2232 | 17.2201 | 16.7401 | 15.7556 | 14.3719 | 14.855 | 14.8763 | 15.4419 | 13.3114 | 13.6585 | 14.7961 |  |  |  | 16.5374 | 15.9533 | 17.798 | 89.0645 | 82.2968 | 109.8492 | 17.1109 | 16.2843 | 16.815 | 16.796 | 16.1409 | 17.1242 | 24.3679 | 110.9794 |  | 47.5935 | 73.9665 | 76.0386 | 52.5408 |  | 6.8016 | 7.0527 | 6.4701 | 6.9828 | 7.348 | 8.7227 | 30.0987 | 5.0838 | 6.6705 | 5.2257 | 7.1839 | 8.1473 | 42.1495 | 46.5346 | 42.7854 | 14.9545 |  |  | -0.48276 | -0.083365 | -0.020492 | -0.10317 | 0.15196 | 0.17105 | 0.1701 | 0.38096 | 0.40615 | -0.24186 | -0.12151 | -0.0006029 | -0.0006374 | 1.7339 | 15.7833 | 16.6682 | 17.2065 | 17.533 | 17.4754 | 16.4204 | 14.7657 | 16.7921 | 17.1294 | 17.4226 | 17.4657 | 17.1724 | 16.3404 | 14.5287 | 32.0231 | 16.1783 | 22.6515 | 14.9547 | 12.5052 | 14.7322 | 10.8626 | 15.8579 | 15.4912 | 15.3671 | 14.2708 | 14.4339 | 15.0221 |  |  |  | 22.9758 | 92.8239 | 74.0571 | 41.6902 | 0.10317 | -0.07996 | 27.3335 |  |  | 10.8641 |  |  | 16.8837 | 16.2221 | 19.3591 | 16.3487 | 15.6737 | 16.4137 | 85.7835 | 112.0332 | 69.6181 | 70.2954 | 49.4556 |  | 26.0752 | 52.4622 | 26.4527 | 39.1814 | 25.8646 | 87.5147 |  | 42.7816 |  |  | 13.4753 | 15.0431 | 30.9399 | [6 empty] | 28.9898 |  |  | 24.7023 |  |  | 13.6996 | 26.888 | 127.4408 | 8.4822 | 21.9442 | 80.061 | 10.0087 | 20.9278 | 89.1443 | 16.5783 | 65.4119 | 10.0168 | 58.8076 | 11.2705 | 60.3044 | 9.8563 | 21.9416 | 73.6258 | 16.4405 | 24.5048 | 94.9953 | 10.6526 | 20.9835 | 87.9384 | 10.8535 | 58.4387 | 15.4389 | 67.4886 | 11.9089 | 66.7572 | 0.52983 | 20.0469 | 0.61493 | 0.057084 | -37.946 | 3.1228 | 123.47 | 49.02 | -0.94762 | -0.33682 | -0.16699 | -0.37469 | 0.45609 | 0.4839 | 0.48255 | -0.19491 | -0.26564 | 0.083356 | -1.5318 | -0.94096 | -0.33832 | -0.083843
42810.4441 | 353 | 18.4725 | 18.5667 | 18.556 | 18.5447 | 17.8569 | 16.4573 | 14.5077 | 16.6303 | 17.1247 | 17.2186 | 17.225 | 16.7416 | 15.7481 | 14.3661 | 14.8538 | 14.8688 | 15.4318 | 13.3062 | 13.6525 | 14.7954 |  |  |  | 16.5266 | 15.9512 | 17.8045 | 89.5851 | 82.6223 | 109.7684 | 17.112 | 16.2936 | 16.8227 | 16.801 | 16.1323 | 17.1367 | 24.499 | 112.3597 |  | 47.8522 | 74.555 | 76.4705 | 56.492 |  | 6.8109 | 7.0598 | 6.4798 | 6.9941 | 7.3479 | 8.7224 | 30.0495 | 4.9539 | 6.6819 | 5.0852 | 7.1945 | 8.1532 | 42.1272 | 46.517 | 42.7586 | 14.9582 |  |  | -0.58659 | 0.056599 | 0.055732 | -0.18268 | 0.17627 | 0.11388 | -0.017184 | 0.195 | -0.75854 | -0.34068 | 0.0034689 | -0.00059305 | -0.00064069 | 1.7185 | 15.7981 | 16.6719 | 17.2115 | 17.5358 | 17.48 | 16.4313 | 14.7646 | 16.7906 | 17.1324 | 17.4241 | 17.4634 | 17.1756 | 16.3412 | 14.5316 | 32.2273 | 15.406 | 22.619 | 15.2707 | 12.2736 | 14.8178 | 10.9118 | 15.8549 | 15.4831 | 15.3611 | 14.268 | 14.4419 | 15.0239 |  |  |  | 23.0757 | 93.5152 | 74.8492 | 42.0714 | 0.051914 | -0.028582 | 27.4867 |  |  | 10.8667 |  |  | 16.8893 | 16.2288 | 19.3818 | 16.343 | 15.6757 | 16.4231 | 86.2747 | 112.8829 | 70.0617 | 70.8088 | 49.5039 |  | 26.1841 | 53.2637 | 26.5474 | 39.1534 | 26.0402 | 87.0353 |  | 42.9844 |  |  | 13.5119 | 15.0707 | 31.0294 | [6 empty] | 28.8007 |  |  | 24.8297 |  |  | 13.7346 | 27.0693 | 127.4629 | 8.4818 | 22.1351 | 80.639 | 10.0333 | 21.2526 | 89.9095 | 16.6393 | 65.6328 | 10.0283 | 59.1583 | 11.2794 | 60.5344 | 9.8518 | 22.283 | 73.9336 | 16.508 | 24.8081 | 95.2051 | 10.6664 | 21.1164 | 88.4635 | 10.8592 | 58.6925 | 15.486 | 67.6522 | 11.9227 | 67.0581 | 0.51404 | 20.0465 | 0.61548 | 0.057496 | -37.8504 | 3.1229 | 124.03 | 50.37 | -1.0444 | 0.27753 | 0.2754 | -0.4986 | 0.49123 | 0.39484 | -0.15338 | -0.19257 | -0.2847 | 0.090076 | -1.5445 | -0.93163 | -0.44365 | -0.091067
42810.4441 | 354 | 18.4666 | 18.5608 | 18.5422 | 18.5396 | 17.8444 | 16.4528 | 14.4973 | 16.6245 | 17.1225 | 17.2069 | 17.213 | 16.7354 | 15.7493 | 14.3597 | 14.8514 | 14.8608 | 15.4257 | 13.2976 | 13.652 | 14.7909 |  |  |  | 16.5239 | 15.9409 | 17.8108 | 90.0324 | 82.868 | 109.5818 | 17.1175 | 16.2915 | 16.837 | 16.8026 | 16.1514 | 17.1596 | 24.6642 | 112.4426 |  | 48.1476 | 75.2171 | 76.9146 | 59.5535 |  | 6.8088 | 7.0679 | 6.4842 | 6.9969 | 7.3507 | 8.7082 | 30.5112 | 4.8841 | 6.6858 | 4.9538 | 7.2052 | 8.1586 | 42.099 | 46.5151 | 42.7296 | 14.9598 |  |  | -0.36382 | 0.030971 | 0.051136 | 0.04337 | 0.07442 | 0.075108 | -0.14992 | 0.12534 | -0.32458 | -1.6282 | -0.15291 | -0.0005799 | -0.00060619 | 1.7241 | 15.7937 | 16.6753 | 17.2153 | 17.5323 | 17.4844 | 16.4325 | 14.7626 | 16.7932 | 17.1308 | 17.4246 | 17.4585 | 17.1771 | 16.337 | 14.5345 | 30.5713 | 14.3595 | 21.69 | 14.876 | 12.581 | 14.8789 | 10.9637 | 15.8567 | 15.4931 | 15.372 | 14.2721 | 14.4418 | 15.0327 |  |  |  | 23.1687 | 94.3439 | 75.123 | 42.5651 | -0.032975 | -0.13266 | 27.6863 |  |  | 10.8705 |  |  | 16.8909 | 16.2325 | 19.404 | 16.3443 | 15.6759 | 16.4379 | 86.8356 | 113.3812 | 70.5159 | 71.3564 | 49.3514 |  | 26.2902 | 53.9936 | 26.6511 | 39.8259 | 26.2022 | 87.5833 |  | 43.2283 |  |  | 13.5306 | 15.0938 | 31.1442 | [6 empty] | 28.7134 |  |  | 24.9603 |  |  | 13.7703 | 27.1251 | 127.4705 | 8.4926 | 22.3043 | 81.2226 | 10.0425 | 21.4133 | 90.7259 | 16.7016 | 65.902 | 10.0521 | 59.5901 | 11.2998 | 60.7639 | 9.8448 | 22.5599 | 74.2492 | 16.5817 | 25.0492 | 95.4696 | 10.6767 | 21.2333 | 89.0139 | 10.8654 | 59.0503 | 15.5556 | 67.8264 | 11.9323 | 67.4149 | 0.56296 | 20.0436 | 0.61705 | 0.057446 | -37.9264 | 3.1229 | 140.16 | 48.92 | -0.82236 | 0.2053 | 0.2638 | 0.24295 | 0.31917 | 0.32065 | -0.45301 | -0.18474 | -0.30146 | 0.07688 | -1.3534 | -0.82237 | -0.52312 | -0.10165
42810.4441 | 355 | 18.46 | 18.5567 | 18.5418 | 18.5334 | 17.8384 | 16.4442 | 14.4976 | 16.6302 | 17.1202 | 17.2111 | 17.2125 | 16.7392 | 15.7446 | 14.3558 | 14.8471 | 14.8635 | 15.4287 | 13.2973 | 13.6564 | 14.7975 |  |  |  | 16.5308 | 15.94 | 17.8334 | 90.4204 | 83.061 | 109.022 | 17.1107 | 16.2868 | 16.8463 | 16.7989 | 16.1415 | 17.162 | 24.7956 | 112.2929 |  | 48.425 | 75.8217 | 77.2707 | 59.9952 |  | 6.8124 | 7.0675 | 6.4733 | 6.9834 | 7.3559 | 8.7457 | 31.2288 | 4.8726 | 6.6846 | 4.8466 | 7.2171 | 8.1546 | 42.0582 | 46.5078 | 42.6948 | 14.9543 |  |  | -0.33163 | -0.22136 | -0.00472 | -0.20765 | -0.06226 | -0.13517 | 0.32517 | 0.25677 | -0.085609 | -0.9577 | -0.17775 | -0.00058647 | -0.00059797 | 1.7422 | 15.7955 | 16.6773 | 17.2142 | 17.537 | 17.4819 | 16.4305 | 14.7684 | 16.7914 | 17.1331 | 17.4328 | 17.4637 | 17.1729 | 16.3342 | 14.5389 | 28.8595 | 14.1089 | 20.1708 | 14.2994 | 12.3983 | 14.938 | 10.9971 | 15.8564 | 15.4943 | 15.3616 | 14.2723 | 14.4444 | 15.0412 |  |  |  | 23.2526 | 95.0887 | 75.4772 | 42.9165 | 0.20994 | -0.13153 | 27.8547 |  |  | 10.8839 |  |  | 16.8893 | 16.2309 | 19.4233 | 16.347 | 15.6787 | 16.4538 | 87.2769 | 113.9246 | 71.0588 | 71.9298 | 49.8589 |  | 26.3874 | 54.5961 | 26.7368 | 40.5112 | 26.3636 | 88.593 |  | 43.4881 |  |  | 13.5592 | 15.1156 | 31.2264 | [6 empty] | 28.9123 |  |  | 25.0452 |  |  | 13.8032 | 27.3035 | 127.9058 | 8.4983 | 22.4879 | 81.8075 | 10.0406 | 21.583 | 91.5558 | 16.7696 | 66.1864 | 10.0713 | 59.9396 | 11.321 | 60.9926 | 9.8455 | 22.7224 | 74.5629 | 16.653 | 25.224 | 95.6535 | 10.6931 | 21.3873 | 89.4575 | 10.8854 | 59.4199 | 15.6189 | 68.0072 | 11.9453 | 67.7114 | 0.64982 | 20.0452 | 0.6186 | 0.056932 | -37.9443 | 3.1229 | 121.4 | 49.66 | -0.78455 | -0.54886 | -0.080147 | -0.53159 | -0.29195 | -0.43018 | 0.66722 | -0.19554 | -0.31529 | 0.063309 | -1.1563 | -0.64968 | -0.53095 | -0.10859
42810.4442 | 356 | 18.4655 | 18.5636 | 18.5473 | 18.5354 | 17.848 | 16.4532 | 14.5049 | 16.6284 | 17.124 | 17.2088 | 17.215 | 16.7353 | 15.7468 | 14.358 | 14.8418 | 14.8542 | 15.4269 | 13.2936 | 13.6523 | 14.8107 |  |  |  | 16.5256 | 15.9425 | 17.8408 | 90.6813 | 83.256 | 108.1839 | 17.1108 | 16.2903 | 16.8537 | 16.8024 | 16.1451 | 17.172 | 24.9135 | 112.4505 |  | 48.7022 | 76.3554 | 77.6353 | 57.5375 |  | 6.8106 | 7.0687 | 6.4669 | 6.9803 | 7.3456 | 8.8578 | 32.327 | 4.8668 | 6.6881 | 4.696 | 7.2178 | 8.1662 | 42.0307 | 46.5013 | 42.686 | 14.9543 |  |  | -0.56885 | -0.020281 | -0.10329 | -0.28125 | -0.051092 | 0.083652 | 0.19769 | 0.42893 | -0.42207 | -0.38075 | -0.17318 | -0.00060455 | -0.00058812 | 1.7478 | 15.8022 | 16.687 | 17.2218 | 17.5395 | 17.4896 | 16.4422 | 14.77 | 16.8012 | 17.1431 | 17.434 | 17.4641 | 17.1782 | 16.3455 | 14.5425 | 29.4704 | 13.9116 | 19.4249 | 13.5696 | 12.2496 | 15.0304 | 11.0216 | 15.853 | 15.486 | 15.3637 | 14.2707 | 14.4447 | 15.0446 |  |  |  | 23.3301 | 95.645 | 75.5471 | 43.0664 | 0.36149 | -0.14018 | 27.9938 |  |  | 10.8818 |  |  | 16.8858 | 16.2348 | 19.4381 | 16.3496 | 15.6793 | 16.4577 | 87.7165 | 114.7637 | 71.6962 | 72.4528 | 50.3868 |  | 26.4992 | 52.4717 | 26.8317 | 41.7395 | 26.593 | 89.1845 |  | 43.7715 |  |  | 13.5875 | 15.1311 | 31.3492 | [6 empty] | 30.2642 |  |  | 25.1028 |  |  | 13.8389 | 27.6843 | 128.6676 | 8.5092 | 22.5632 | 82.4146 | 10.0515 | 21.8234 | 92.206 | 16.8376 | 66.4403 | 10.0659 | 60.2183 | 11.344 | 61.2403 | 9.8429 | 22.771 | 74.9422 | 16.7286 | 25.394 | 95.9901 | 10.7079 | 21.5754 | 89.8792 | 10.9073 | 59.8473 | 15.6503 | 68.3699 | 11.9511 | 68.0815 | 0.53561 | 20.0433 | 0.61948 | 0.055658 | -37.9416 | 3.1229 | 133.93 | 49.8 | -1.0264 | -0.16613 | -0.37492 | -0.61867 | -0.26453 | 0.33848 | 0.52035 | -0.20642 | -0.25306 | 0.036962 | -1.2134 | -0.56395 | -0.4587 | -0.11014
42810.4442 | 357 | 18.4598 | 18.5594 | 18.5432 | 18.5354 | 17.8409 | 16.4521 | 14.502 | 16.6257 | 17.1245 | 17.2167 | 17.2142 | 16.7347 | 15.7422 | 14.3599 | 14.8399 | 14.8584 | 15.4298 | 13.2894 | 13.6485 | 14.8202 |  |  |  | 16.522 | 15.9426 | 17.8529 | 91.1064 | 83.5887 | 110.7643 | 17.1109 | 16.2953 | 16.8661 | 16.8038 | 16.1435 | 17.182 | 25.0124 | 112.4214 |  | 48.9565 | 76.7506 | 78.0456 | 56.1105 |  | 6.8213 | 7.0835 | 6.4717 | 6.9875 | 7.3628 | 8.8479 | 32.6667 | 4.948 | 6.7002 | 4.6487 | 7.2249 | 8.1594 | 42.0008 | 46.4932 | 42.6663 | 14.9526 |  |  | -0.50116 | -0.082709 | 0.16284 | -0.22802 | -0.17332 | 0.11125 | 0.36066 | 0.17529 | -0.38743 | -0.12836 | -0.046206 | -0.00055198 | -0.00061769 | 1.7357 | 15.7919 | 16.6733 | 17.2105 | 17.5269 | 17.4712 | 16.4294 | 14.7546 | 16.794 | 17.1316 | 17.4217 | 17.4644 | 17.1617 | 16.3403 | 14.5218 | 30.8764 | 14.0965 | 18.2579 | 12.8749 | 11.9439 | 15.1493 | 11.0531 | 15.8554 | 15.489 | 15.3612 | 14.2659 | 14.4364 | 15.0419 |  |  |  | 23.4239 | 95.9055 | 75.4366 | 43.0591 | 0.26019 | -0.061328 | 28.1042 |  |  | 10.8829 |  |  | 16.8913 | 16.2393 | 19.4645 | 16.3527 | 15.682 | 16.466 | 88.1836 | 115.4995 | 72.235 | 72.9848 | 50.7216 |  | 26.6052 | 50.3619 | 26.9353 | 42.2416 | 26.8149 | 89.5979 |  | 44.0422 |  |  | 13.6208 | 15.1673 | 31.6071 | [6 empty] | 31.4423 |  |  | 25.1473 |  |  | 13.8655 | 28.1201 | 130.067 | 8.5085 | 22.5546 | 82.9788 | 10.0629 | 22.0392 | 92.6921 | 16.9011 | 66.7109 | 10.0639 | 60.4719 | 11.3598 | 61.5121 | 9.8465 | 23.0127 | 75.5212 | 16.8078 | 25.5902 | 96.341 | 10.7209 | 21.7221 | 90.3992 | 10.925 | 60.4091 | 15.6686 | 68.6482 | 11.9563 | 68.501 | 0.52347 | 20.0435 | 0.62017 | 0.05665 | -37.96 | 3.1229 | 127.4 | 49.08 | -0.96666 | -0.33551 | 0.47077 | -0.55707 | -0.4872 | 0.39034 | 0.70281 | -0.21213 | -0.19095 | 0.030535 | -1.3558 | -0.43062 | -0.41572 | -0.10678
42810.4442 | 358 | 18.4638 | 18.5565 | 18.5491 | 18.5394 | 17.8442 | 16.4544 | 14.5047 | 16.6281 | 17.1304 | 17.2187 | 17.2146 | 16.7387 | 15.7449 | 14.3609 | 14.8467 | 14.8544 | 15.4274 | 13.2984 | 13.6584 | 14.8213 |  |  |  | 16.5291 | 15.9513 | 17.8769 | 91.8405 | 83.8556 | 112.8542 | 17.1161 | 16.2938 | 16.8781 | 16.8041 | 16.1502 | 17.201 | 25.1143 | 111.7775 |  | 49.1912 | 77.1363 | 78.4615 | 57.0878 |  | 6.8213 | 7.0834 | 6.4787 | 6.9894 | 7.3475 | 8.8353 | 32.5257 | 5.0376 | 6.6952 | 4.6662 | 7.2286 | 8.1569 | 41.9702 | 46.4827 | 42.6517 | 14.9361 |  |  | -0.24686 | -0.15433 | 0.06822 | -0.16428 | -0.057664 | 0.44572 | 0.46382 | -0.12304 | -0.5906 | -0.42292 | -0.11754 | -0.00062919 | -0.00062426 | 1.726 | 15.7916 | 16.6702 | 17.2082 | 17.5217 | 17.4789 | 16.4306 | 14.7654 | 16.7908 | 17.1372 | 17.4223 | 17.4608 | 17.1701 | 16.3429 | 14.5318 | 31.4988 | 14.3082 | 19.0113 | 12.4499 | 11.4968 | 15.2417 | 11.0865 | 15.8446 | 15.4845 | 15.3598 | 14.2624 | 14.4407 | 15.0564 |  |  |  | 23.5143 | 96.3631 | 75.6414 | 43.2685 | 0.1052 | -0.11346 | 28.2836 |  |  | 10.8882 |  |  | 16.8943 | 16.238 | 19.4874 | 16.3478 | 15.6805 | 16.4779 | 88.6285 | 116.2379 | 72.7545 | 73.5561 | 50.823 |  | 26.6953 | 51.8134 | 27.0403 | 42.5329 | 26.9948 | 89.3351 |  | 44.27 |  |  | 13.6328 | 15.1919 | 31.779 | [6 empty] | 31.3154 |  |  | 25.249 |  |  | 13.8905 | 28.468 | 131.2914 | 8.5189 | 22.7316 | 83.5984 | 10.0741 | 22.2382 | 93.2302 | 16.9581 | 67.0461 | 10.0671 | 60.7878 | 11.3725 | 61.7741 | 9.8355 | 23.5696 | 76.1538 | 16.873 | 25.8449 | 96.7551 | 10.7353 | 21.8741 | 90.8474 | 10.9517 | 60.927 | 15.691 | 68.8125 | 11.9779 | 68.8123 | 0.59011 | 20.0427 | 0.6221 | 0.058285 | -37.9608 | 3.1229 | 127.84 | 50.06 | -0.68028 | -0.45831 | 0.30471 | -0.47284 | -0.28102 | 0.78129 | 0.797 | -0.21189 | -0.2277 | 0.028543 | -1.4141 | -0.51045 | -0.43942 | -0.10955
42810.4442 | 359 | 18.4579 | 18.5649 | 18.5424 | 18.536 | 17.8437 | 16.4506 | 14.5056 | 16.6235 | 17.123 | 17.218 | 17.2173 | 16.7328 | 15.7434 | 14.3604 | 14.8392 | 14.8548 | 15.4267 | 13.2882 | 13.655 | 14.8218 |  |  |  | 16.5315 | 15.9501 | 17.8883 | 92.3231 | 84.0508 | 112.3047 | 17.1106 | 16.2905 | 16.8838 | 16.7978 | 16.1433 | 17.2104 | 25.2278 | 111.4054 |  | 49.4263 | 77.5949 | 78.8076 | 58.3247 |  | 6.8337 | 7.1085 | 6.4777 | 6.995 | 7.3469 | 8.8367 | 32.5545 | 5.1699 | 6.6973 | 4.7132 | 7.2339 | 8.1536 | 41.9428 | 46.4821 | 42.6518 | 14.9256 |  |  | -0.41639 | -0.19376 | 0.030764 | -0.13602 | 0.049448 | 0.20785 | 0.42506 | 0.099716 | 0.13234 | -0.35096 | -0.18311 | -0.00057169 | -0.0006029 | 1.7056 | 15.7903 | 16.6743 | 17.2093 | 17.5324 | 17.4782 | 16.4272 | 14.7692 | 16.7904 | 17.1294 | 17.426 | 17.4666 | 17.1712 | 16.3423 | 14.5303 | 30.6087 | 14.4008 | 20.0338 | 12.7511 | 11.4144 | 15.3236 | 11.1301 | 15.8435 | 15.4859 | 15.361 | 14.263 | 14.4463 | 15.0637 |  |  |  | 23.6113 | 96.8033 | 75.7507 | 43.6143 | -0.01231 | -0.30749 | 28.5218 |  |  | 10.8829 |  |  | 16.8825 | 16.2365 | 19.5001 | 16.3348 | 15.6719 | 16.4805 | 89.1558 | 117.039 | 73.2354 | 74.052 | 50.8315 |  | 26.7968 | 53.7338 | 27.1446 | 41.8812 | 27.1523 | 89.6446 |  | 44.4783 |  |  | 13.6173 | 15.2189 | 32.1653 | [6 empty] | 31.0885 |  |  | 25.3635 |  |  | 13.9228 | 28.7319 | 131.7471 | 8.5388 | 23.2513 | 83.9488 | 10.0946 | 22.4666 | 93.7901 | 17.025 | 68.1307 | 10.0776 | 61.1986 | 11.4048 | 62.082 | 9.8559 | 24.1329 | 76.6633 | 16.9175 | 26.0351 | 96.9717 | 10.7415 | 22.0712 | 91.2172 | 10.9717 | 61.4006 | 15.7192 | 68.9395 | 11.9919 | 69.2013 | 0.78079 | 20.0368 | 0.62593 | 0.060703 | -37.9381 | 3.1229 | 137.37 | 49.69 | -0.88289 | -0.51355 | 0.20463 | -0.43028 | 0.26023 | 0.53352 | 0.76296 | -0.20869 | -0.27751 | 0.051987 | -1.3057 | -0.61899 | -0.46994 | -0.11588
42810.4442 | 360 | 18.4605 | 18.5629 | 18.5432 | 18.5374 | 17.8396 | 16.4485 | 14.5094 | 16.6357 | 17.1292 | 17.2125 | 17.2149 | 16.734 | 15.7436 | 14.3615 | 14.8305 | 14.8567 | 15.4277 | 13.2976 | 13.6657 | 14.8377 |  |  |  | 16.5291 | 15.9535 | 17.9016 | 92.8115 | 84.3692 | 113.0498 | 17.1121 | 16.2896 | 16.8861 | 16.7967 | 16.1508 | 17.2145 | 25.3647 | 111.474 |  | 49.6559 | 78.0114 | 79.2061 | 60.5474 |  | 6.8421 | 7.1167 | 6.4702 | 7.0043 | 7.3518 | 8.8349 | 32.8632 | 5.3191 | 6.7005 | 4.7664 | 7.2418 | 8.1704 | 41.9188 | 46.4789 | 42.6512 | 14.9218 |  |  | -0.44005 | -0.13397 | 0.05442 | -0.18925 | 0.15327 | -0.10626 | 0.39548 | -0.031048 | -0.25277 | -0.14431 | -0.078197 | -0.00060126 | -0.00060455 | 1.6575 | 15.7935 | 16.6776 | 17.2098 | 17.535 | 17.4835 | 16.4304 | 14.768 | 16.7893 | 17.1328 | 17.4264 | 17.4686 | 17.17 | 16.3416 | 14.5279 | 29.553 | 14.3336 | 20.2965 | 12.8862 | 11.8621 | 15.3979 | 11.172 | 15.8498 | 15.4882 | 15.3687 | 14.2739 | 14.4528 | 15.0728 |  |  |  | 23.6944 | 97.038 | 76.1563 | 44.0674 | 0.22737 | -0.044014 | 28.8121 |  |  | 10.8818 |  |  | 16.8785 | 16.2386 | 19.5208 | 16.339 | 15.6739 | 16.4873 | 89.7377 | 117.6197 | 73.7195 | 74.4881 | 50.7458 |  | 26.9182 | 55.497 | 27.2604 | 43.4639 | 27.4503 | 90.337 |  | 44.7221 |  |  | 13.6058 | 15.2177 | 32.1992 | [6 empty] | 31.718 |  |  | 25.4184 |  |  | 13.9571 | 28.9619 | 131.7716 | 8.5707 | 23.6237 | 84.3386 | 10.0935 | 22.6384 | 94.3136 | 17.0857 | 68.5177 | 10.0753 | 61.7077 | 11.4185 | 62.3904 | 9.8638 | 24.2932 | 77.1556 | 16.98 | 26.231 | 97.3933 | 10.7487 | 22.299 | 91.5593 | 10.9863 | 61.8538 | 15.7408 | 69.1506 | 11.9972 | 69.4543 | 0.6556 | 20.0374 | 0.62922 | 0.057858 | -37.9752 | 3.1229 | 147.39 | 48.87 | -0.9085 | -0.42702 | 0.27216 | -0.50754 | 0.45815 | -0.38147 | 0.73594 | -0.20219 | -0.32256 | 0.018135 | -1.1797 | -0.64331 | -0.52705 | -0.12567
42810.4442 | 361 | 18.4586 | 18.575 | 18.556 | 18.5464 | 17.8447 | 16.4568 | 14.5142 | 16.6383 | 17.1284 | 17.2192 | 17.2216 | 16.7371 | 15.7423 | 14.3632 | 14.8354 | 14.8555 | 15.4233 | 13.2946 | 13.6738 | 14.8367 |  |  |  | 16.5325 | 15.9564 | 17.9125 | 93.3677 | 84.7057 | 113.7802 | 17.1111 | 16.2869 | 16.9028 | 16.8077 | 16.1465 | 17.2275 | 25.5312 | 111.9428 |  | 49.9125 | 78.4094 | 79.6134 | 64.0066 |  | 6.8503 | 7.1218 | 6.4852 | 7.0238 | 7.3688 | 8.8686 | 33.1401 | 5.473 | 6.7144 | 4.8702 | 7.2637 | 8.1674 | 41.8875 | 46.4489 | 42.6515 | 14.9111 |  |  | -0.31454 | 0.008631 | -0.006692 | -0.12485 | 0.1007 | -0.02346 | 0.42768 | -0.20584 | 0.061898 | -0.14431 | 0.0002897 | -0.00064069 | -0.0006259 | 1.632 | 15.7936 | 16.6711 | 17.2086 | 17.5272 | 17.4787 | 16.4253 | 14.7653 | 16.7938 | 17.131 | 17.4282 | 17.4627 | 17.1692 | 16.339 | 14.5299 | 30.3292 | 15.2056 | 21.038 | 12.8498 | 12.2066 | 15.5019 | 11.2163 | 15.8501 | 15.4867 | 15.3571 | 14.2679 | 14.4518 | 15.073 |  |  |  | 23.7777 | 97.3807 | 76.6268 | 44.3377 | 0.30942 | 0.048957 | 29.0559 |  |  | 10.8917 |  |  | 16.8805 | 16.2408 | 19.5446 | 16.3448 | 15.6765 | 16.494 | 90.2044 | 118.3926 | 74.1654 | 74.9604 | 50.4163 |  | 27.0059 | 57.0891 | 27.3739 | 44.636 | 27.6948 | 90.5581 |  | 44.9502 |  |  | 13.6014 | 15.2393 | 32.3405 | [6 empty] | 31.7808 |  |  | 25.4471 |  |  | 13.9895 | 29.0999 | 132.4516 | 8.613 | 23.8354 | 85.0732 | 10.1211 | 22.7877 | 94.7117 | 17.1272 | 68.7306 | 10.0953 | 62.1251 | 11.4366 | 62.76 | 9.8954 | 24.561 | 77.6202 | 17.0531 | 26.4347 | 98.0977 | 10.7503 | 22.5396 | 92.08 | 11.0214 | 62.3083 | 15.7922 | 69.3364 | 12.0189 | 69.6646 | 0.61496 | 20.0307 | 0.63156 | 0.061006 | -37.9707 | 3.123 | 136.65 | 50.08 | -0.76882 | 0.10839 | -0.095441 | -0.41224 | 0.37139 | -0.17925 | 0.76536 | -0.19006 | -0.36293 | -0.0061266 | -1.2539 | -0.72054 | -0.61751 | -0.13037
42810.4442 | 362 | 18.4618 | 18.5731 | 18.5543 | 18.5446 | 17.8362 | 16.4496 | 14.5099 | 16.6344 | 17.1253 | 17.2141 | 17.2119 | 16.737 | 15.7538 | 14.3512 | 14.8323 | 14.8496 | 15.4191 | 13.2919 | 13.6656 | 14.8396 |  |  |  | 16.5322 | 15.9573 | 17.9251 | 93.725 | 85.1233 | 112.906 | 17.1012 | 16.2887 | 16.9173 | 16.8096 | 16.1449 | 17.2439 | 25.7491 | 112.2182 |  | 50.1522 | 78.9096 | 80.0098 | 65.0243 |  | 6.8399 | 7.1185 | 6.486 | 7.0307 | 7.3744 | 8.8732 | 33.3692 | 5.5372 | 6.7202 | 4.937 | 7.2671 | 8.1846 | 41.8619 | 46.4338 | 42.6595 | 14.9059 |  |  | -0.50839 | -0.055765 | -0.023776 | -0.24773 | -0.000492 | 0.3373 | 0.3462 | -0.00542 | -0.18816 | -0.3648 | -0.20536 | -0.0006029 | -0.00063904 | 1.5902 | 15.7926 | 16.6706 | 17.2065 | 17.5249 | 17.4719 | 16.4218 | 14.76 | 16.7961 | 17.1289 | 17.4254 | 17.4577 | 17.1711 | 16.333 | 14.5328 | 31.9557 | 16.3666 | 22.6913 | 13.8148 | 11.9453 | 15.6281 | 11.3036 | 15.8555 | 15.4915 | 15.3675 | 14.2772 | 14.4572 | 15.0875 |  |  |  | 23.8708 | 97.7526 | 77.3552 | 44.7014 | 0.20407 | 0.16188 | 29.2873 |  |  | 10.9032 |  |  | 16.8859 | 16.2482 | 19.5679 | 16.3415 | 15.684 | 16.5131 | 90.6349 | 119.3941 | 74.6147 | 75.4216 | 50.6655 |  | 27.0986 | 58.6781 | 27.4834 | 44.737 | 27.8947 | 90.6011 |  | 45.1918 |  |  | 13.6149 | 15.2398 | 33.0844 | [6 empty] | 31.5372 |  |  | 25.4871 |  |  | 14.0312 | 29.3044 | 132.9673 | 8.6474 | 24.0723 | 85.4907 | 10.1354 | 23.1024 | 95.29 | 17.1662 | 68.9839 | 10.1158 | 62.3931 | 11.4585 | 63.0775 | 9.9228 | 24.978 | 77.9331 | 17.1455 | 26.6236 | 98.5887 | 10.7584 | 22.723 | 92.4559 | 11.041 | 62.7622 | 15.823 | 69.4667 | 12.0442 | 69.8321 | 0.51847 | 20.0155 | 0.63379 | 0.059928 | -37.9921 | 3.1229 | 119.65 | 48.99 | -0.97632 | -0.27551 | -0.1799 | -0.58069 | -0.025959 | 0.6797 | 0.68861 | -0.19384 | -0.40336 | -0.0021424 | -1.4199 | -0.89407 | -0.63841 | -0.13733
42810.4442 | 363 | 18.4509 | 18.5584 | 18.5444 | 18.5387 | 17.8363 | 16.4439 | 14.499 | 16.6347 | 17.1183 | 17.2092 | 17.2048 | 16.7306 | 15.7389 | 14.3528 | 14.8311 | 14.856 | 15.4272 | 13.2997 | 13.6643 | 14.8463 |  |  |  | 16.5331 | 15.9538 | 17.9518 | 93.9121 | 85.5478 | 112.2866 | 17.1029 | 16.2846 | 16.9207 | 16.7984 | 16.1514 | 17.2508 | 25.9035 | 113.6979 |  | 50.397 | 79.3823 | 80.4067 | 61.7387 |  | 6.8392 | 7.1282 | 6.4854 | 7.0479 | 7.3752 | 8.8826 | 33.2443 | 5.5619 | 6.7304 | 5.0064 | 7.2826 | 8.1805 | 41.8277 | 46.3967 | 42.6481 | 14.8949 |  |  | -0.30928 | -0.17142 | 0.05442 | -0.053226 | 0.19796 | 0.060652 | 0.37512 | 0.01692 | -0.77975 | 0.068432 | -0.093298 | -0.00058647 | -0.0006374 | 1.6004 | 15.7905 | 16.6739 | 17.2105 | 17.5326 | 17.4757 | 16.4252 | 14.7618 | 16.7908 | 17.137 | 17.4251 | 17.4609 | 17.1733 | 16.3359 | 14.5313 | 32.7137 | 16.4451 | 23.9906 | 15.0908 | 12.7648 | 15.7454 | 11.388 | 15.8539 | 15.494 | 15.3675 | 14.2725 | 14.4573 | 15.1009 |  |  |  | 23.9941 | 98.1084 | 77.9823 | 45.062 | 0.069946 | -0.068292 | 29.5004 |  |  | 10.9073 |  |  | 16.8922 | 16.257 | 19.592 | 16.3437 | 15.692 | 16.5332 | 91.1482 | 120.0329 | 75.0739 | 75.8169 | 51.7693 |  | 27.2219 | 58.9272 | 27.6074 | 44.9651 | 28.0746 | 91.7843 |  | 45.4448 |  |  | 13.6066 | 15.2406 | 33.6541 | [6 empty] | 31.3988 |  |  | 25.5167 |  |  | 14.05 | 29.4972 | 133.9185 | 8.6778 | 24.3611 | 85.6642 | 10.1196 | 23.4342 | 95.844 | 17.2262 | 69.3312 | 10.1235 | 62.639 | 11.4673 | 63.3666 | 9.8597 | 25.4554 | 78.3953 | 17.1913 | 26.7388 | 99.0719 | 10.7379 | 22.9389 | 92.7949 | 11.0456 | 63.1576 | 15.8395 | 69.6149 | 12.0517 | 70.1305 | 0.5229 | 20.0318 | 0.637 | 0.059935 | -37.9803 | 3.1229 | 122.71 | 49.05 | -0.76089 | -0.48305 | 0.27217 | -0.26917 | 0.52072 | 0.28823 | 0.7168 | -0.22032 | -0.40607 | -0.0023665 | -1.4904 | -1.0286 | -0.54192 | -0.14319
42810.4442 | 364 | 18.4468 | 18.5613 | 18.5432 | 18.5333 | 17.8371 | 16.4461 | 14.5002 | 16.6267 | 17.1193 | 17.2128 | 17.2119 | 16.733 | 15.7399 | 14.3514 | 14.8299 | 14.8542 | 15.4211 | 13.2927 | 13.6698 | 14.8567 |  |  |  | 16.5277 | 15.9525 | 17.9657 | 94.218 | 85.8599 | 112.8594 | 17.1038 | 16.2841 | 16.9264 | 16.7947 | 16.1516 | 17.2576 | 26.0152 | 114.3867 |  | 50.6781 | 79.843 | 80.7952 | 59.5229 |  | 6.8237 | 7.1274 | 6.486 | 7.0471 | 7.3734 | 8.9273 | 32.8928 | 5.5273 | 6.7295 | 5.0343 | 7.2843 | 8.1756 | 41.8177 | 46.3684 | 42.6485 | 14.8819 |  |  | -0.55636 | 0.10194 | 0.13787 | -0.13142 | 0.1007 | -0.038572 | 0.45922 | -0.01002 | -0.28741 | -0.99441 | -0.077005 | -0.00062754 | -0.00067847 | 1.5855 | 15.8024 | 16.6685 | 17.2106 | 17.5313 | 17.473 | 16.4181 | 14.761 | 16.791 | 17.1297 | 17.4263 | 17.4603 | 17.1611 | 16.3351 | 14.5273 | 32.4959 | 15.8977 | 24.1248 | 15.0875 | 13.7026 | 15.8324 | 11.4417 | 15.8431 | 15.4897 | 15.3587 | 14.2648 | 14.4564 | 15.0967 |  |  |  | 24.0892 | 98.3302 | 78.2897 | 45.3213 | 0.21197 | -0.23316 | 29.6595 |  |  | 10.9079 |  |  | 16.8929 | 16.2541 | 19.6172 | 16.3481 | 15.6922 | 16.544 | 91.6982 | 120.5376 | 75.487 | 76.1543 | 52.1927 |  | 27.3407 | 58.3722 | 27.7184 | 45.4774 | 28.239 | 92.1267 |  | 45.6532 |  |  | 13.6363 | 15.2662 | 33.7625 | [6 empty] | 31.4024 |  |  | 25.5781 |  |  | 14.0635 | 29.7158 | 134.3723 | 8.6928 | 24.4641 | 85.9511 | 10.117 | 23.6123 | 96.3222 | 17.2842 | 69.6194 | 10.1294 | 62.8666 | 11.4691 | 63.6939 | 9.8598 | 25.7838 | 78.747 | 17.2528 | 26.934 | 99.2913 | 10.7381 | 23.2104 | 93.1772 | 11.0816 | 63.5172 | 15.872 | 70.0667 | 12.0511 | 70.4454 | 0.57239 | 20.0286 | 0.64101 | 0.060218 | -37.9731 | 3.123 | 126.92 | 50.11 | -1.0213 | 0.3725 | 0.43321 | -0.42296 | 0.37143 | -0.22987 | 0.79316 | -0.22805 | -0.38688 | -0.01101 | -1.4561 | -1.0373 | -0.47659 | -0.14719
42810.4443 | 365 | 18.4557 | 18.5689 | 18.551 | 18.5383 | 17.8421 | 16.449 | 14.5103 | 16.6294 | 17.13 | 17.2192 | 17.2127 | 16.7358 | 15.7424 | 14.3611 | 14.8245 | 14.8457 | 15.4197 | 13.2897 | 13.6652 | 14.8538 |  |  |  | 16.5209 | 15.9518 | 17.9752 | 94.6373 | 86.1253 | 113.9324 | 17.1052 | 16.2885 | 16.9352 | 16.8011 | 16.1525 | 17.2765 | 26.1329 | 114.0602 |  | 50.9192 | 80.2447 | 81.1446 | 60.4146 |  | 6.8258 | 7.1303 | 6.4838 | 7.0381 | 7.3734 | 8.9674 | 32.7804 | 5.3846 | 6.7375 | 5.0535 | 7.2935 | 8.1814 | 41.8185 | 46.3493 | 42.651 | 14.8797 |  |  | -0.283 | 0.060543 | 0.070848 | -0.085426 | 0.15393 | 0.13754 | 0.64059 | 0.05372 | -0.18232 | -0.82364 | -0.33611 | -0.0006144 | -0.00067519 | 1.5676 | 15.8031 | 16.6705 | 17.2075 | 17.5363 | 17.4799 | 16.429 | 14.7656 | 16.7956 | 17.1304 | 17.44 | 17.4695 | 17.1785 | 16.3412 | 14.5465 | 32.5032 | 15.1181 | 22.816 | 15.34 | 14.0654 | 15.9456 | 11.4888 | 15.8408 | 15.4928 | 15.3647 | 14.2694 | 14.4616 | 15.1109 |  |  |  | 24.1991 | 98.63 | 78.6327 | 45.7885 | 0.18401 | -0.10537 | 29.7849 |  |  | 10.9126 |  |  | 16.8922 | 16.2555 | 19.6368 | 16.3485 | 15.6921 | 16.5503 | 92.2089 | 121.0771 | 75.9209 | 76.5945 | 52.0923 |  | 27.4379 | 59.2208 | 27.8216 | 45.8359 | 28.4175 | 92.6018 |  | 45.8761 |  |  | 13.6656 | 15.2654 | 33.791 | [6 empty] | 31.6226 |  |  | 25.6409 |  |  | 14.0975 | 29.957 | 135.1878 | 8.7007 | 24.4748 | 86.4084 | 10.1195 | 23.735 | 96.7241 | 17.3392 | 69.9247 | 10.1459 | 63.0845 | 11.4872 | 64.0395 | 9.8916 | 26.0368 | 79.0561 | 17.314 | 27.2418 | 99.4585 | 10.7337 | 23.3827 | 93.6336 | 11.0971 | 63.8642 | 15.9092 | 70.5713 | 12.0637 | 70.8028 | 0.65887 | 20.0255 | 0.64393 | 0.059906 | -38.0347 | 3.123 | 123.72 | 49.07 | -0.72939 | 0.28707 | 0.31055 | -0.341 | 0.45924 | 0.4341 | 0.93685 | -0.22196 | -0.40695 | -0.014901 | -1.4437 | -0.88639 | -0.49737 | -0.15645
42810.4443 | 366 | 18.4553 | 18.5595 | 18.5452 | 18.5401 | 17.8419 | 16.4478 | 14.5027 | 16.6251 | 17.1229 | 17.2098 | 17.2132 | 16.723 | 15.7401 | 14.36 | 14.8246 | 14.8442 | 15.4208 | 13.2947 | 13.6667 | 14.8577 |  |  |  | 16.523 | 15.9635 | 17.998 | 95.0013 | 86.4134 | 113.6579 | 17.0982 | 16.2891 | 16.9526 | 16.7987 | 16.15 | 17.2894 | 26.2637 | 114.2692 |  | 51.1395 | 80.529 | 81.4482 | 62.2329 |  | 6.813 | 7.1234 | 6.4777 | 7.0279 | 7.3617 | 8.9637 | 33.3052 | 5.21 | 6.734 | 5.1495 | 7.291 | 8.1776 | 41.8466 | 46.3479 | 42.6448 | 14.8673 |  |  | -0.38419 | -0.13265 | 0.048504 | -0.12288 | 0.030392 | 0.12308 | 0.37512 | -0.084276 | -0.82217 | 0.10934 | -0.16086 | -0.00060126 | -0.0005914 | 1.5917 | 15.7889 | 16.6671 | 17.2138 | 17.5323 | 17.4761 | 16.4295 | 14.7664 | 16.7924 | 17.1326 | 17.4276 | 17.4646 | 17.1774 | 16.3403 | 14.5332 | 32.8703 | 15.045 | 22.8535 | 14.9586 | 13.9694 | 16.0369 | 11.5362 | 15.8482 | 15.4915 | 15.3643 | 14.2675 | 14.4617 | 15.1106 |  |  |  | 24.29 | 98.9424 | 78.8828 | 45.95 | 0.29544 | -0.12343 | 29.8939 |  |  | 10.9197 |  |  | 16.8919 | 16.2589 | 19.6593 | 16.3517 | 15.6942 | 16.5593 | 92.6497 | 121.5563 | 76.4001 | 77.1069 | 52.7457 |  | 27.5522 | 59.805 | 27.9359 | 46.264 | 28.6138 | 93.7671 |  | 46.0782 |  |  | 13.692 | 15.271 | 33.9457 | [6 empty] | 32.1886 |  |  | 25.6762 |  |  | 14.1251 | 30.0649 | 135.4042 | 8.7127 | 24.5864 | 86.9093 | 10.1118 | 23.9496 | 97.1716 | 17.3716 | 70.2336 | 10.1616 | 63.2111 | 11.4933 | 64.3782 | 9.9273 | 26.3526 | 79.3808 | 17.3844 | 27.5433 | 99.6668 | 10.7228 | 23.354 | 94.1849 | 11.1181 | 64.2385 | 15.9697 | 70.8439 | 12.0799 | 71.2328 | 0.64674 | 20.0255 | 0.64703 | 0.059805 | -38.0401 | 3.1231 | 133.26 | 48.9 | -0.84955 | -0.42492 | 0.25695 | -0.40898 | 0.20406 | 0.41065 | 0.71691 | -0.23624 | -0.4193 | -0.020117 | -1.4738 | -0.88504 | -0.54345 | -0.15787
42810.4443 | 367 | 18.4607 | 18.5659 | 18.5473 | 18.5444 | 17.844 | 16.4535 | 14.5107 | 16.6366 | 17.1232 | 17.225 | 17.2199 | 16.7375 | 15.7491 | 14.3694 | 14.8279 | 14.8445 | 15.4179 | 13.2923 | 13.6585 | 14.8736 |  |  |  | 16.5213 | 15.9607 | 18.0135 | 95.2529 | 86.6412 | 113.0953 | 17.0903 | 16.2823 | 16.9592 | 16.7887 | 16.1479 | 17.2908 | 26.4077 | 115.1492 |  | 51.3687 | 80.7846 | 81.7842 | 62.8179 |  | 6.8112 | 7.1327 | 6.4753 | 7.0363 | 7.3719 | 8.9694 | 33.6868 | 5.0997 | 6.7461 | 5.2177 | 7.317 | 8.191 | 41.8672 | 46.3525 | 42.6347 | 14.8585 |  |  | -0.27577 | -0.13528 | -0.00472 | -0.25036 | -0.01232 | 0.20193 | 0.4658 | 0.043864 | 0.47212 | -0.11535 | -0.054154 | -0.00060126 | -0.00059962 | 1.588 | 15.7889 | 16.6717 | 17.2097 | 17.526 | 17.4769 | 16.4273 | 14.7625 | 16.7946 | 17.1247 | 17.4246 | 17.4536 | 17.1723 | 16.3346 | 14.5311 | 33.6061 | 15.6784 | 22.2651 | 15.8059 | 14.1959 | 16.1719 | 11.5756 | 15.8469 | 15.4929 | 15.3611 | 14.2768 | 14.4529 | 15.125 |  |  |  | 24.3829 | 99.3154 | 79.085 | 46.355 | 0.5497 | 0.2046 | 30.0091 |  |  | 10.9186 |  |  | 16.8892 | 16.259 | 19.6779 | 16.3469 | 15.6943 | 16.5684 | 93.1904 | 121.9691 | 76.8115 | 77.4976 | 53.7029 |  | 27.6585 | 59.7748 | 28.0554 | 45.9943 | 28.7764 | 95.0609 |  | 46.2845 |  |  | 13.7215 | 15.2905 | 34.2896 | [6 empty] | 32.5617 |  |  | 25.7337 |  |  | 14.139 | 30.1883 | 135.5739 | 8.7262 | 24.8025 | 87.4192 | 10.1116 | 24.2786 | 97.6348 | 17.3915 | 70.524 | 10.1699 | 63.5141 | 11.4962 | 64.7406 | 9.9611 | 26.4895 | 79.7638 | 17.4364 | 27.7085 | 99.8216 | 10.72 | 23.4924 | 94.8093 | 11.1409 | 64.6518 | 16.0033 | 71.1498 | 12.0951 | 71.6252 | 0.49613 | 20.0192 | 0.65081 | 0.058213 | -38.0465 | 3.123 | 135.29 | 50.08 | -0.71924 | -0.42912 | -0.080156 | -0.58378 | -0.12992 | 0.526 | 0.79888 | -0.25922 | -0.4144 | -0.007094 | -1.5398 | -0.81508 | -0.55483 | -0.16599
42810.4443 | 368 | 18.4413 | 18.5561 | 18.5376 | 18.5358 | 17.8334 | 16.4401 | 14.4987 | 16.6298 | 17.1201 | 17.2078 | 17.2024 | 16.7232 | 15.7371 | 14.354 | 14.8232 | 14.8457 | 15.4181 | 13.2904 | 13.6668 | 14.8823 |  |  |  | 16.5229 | 15.958 | 18.0247 | 95.5338 | 86.789 | 113.2864 | 17.0885 | 16.2857 | 16.9675 | 16.7831 | 16.1475 | 17.3048 | 26.5396 | 114.636 |  | 51.6271 | 81.059 | 82.2303 | 61.4034 |  | 6.8086 | 7.1302 | 6.4652 | 7.0397 | 7.3759 | 8.958 | 34.0844 | 5.069 | 6.7426 | 5.2266 | 7.3182 | 8.1982 | 41.874 | 46.3345 | 42.6299 | 14.8567 |  |  | -0.51167 | -0.028825 | 0.045876 | 0.064398 | -0.087888 | 0.15462 | 0.51048 | 0.001808 | -0.34637 | -0.41453 | -0.10323 | -0.00055526 | -0.00055855 | 1.5805 | 15.7922 | 16.6737 | 17.2029 | 17.525 | 17.4764 | 16.4201 | 14.7599 | 16.7941 | 17.1321 | 17.4218 | 17.453 | 17.1705 | 16.3353 | 14.5323 | 36.0673 | 17.8131 | 25.2532 | 16.7235 | 14.6666 | 16.3536 | 11.6685 | 15.8446 | 15.4812 | 15.3578 | 14.2675 | 14.4608 | 15.1211 |  |  |  | 24.4827 | 99.5536 | 79.1061 | 47.095 | 0.54038 | 0.34914 | 30.1432 |  |  | 10.9205 |  |  | 16.8912 | 16.2627 | 19.7015 | 16.3428 | 15.6946 | 16.5792 | 93.8228 | 122.3075 | 77.0909 | 77.82 | 54.2137 |  | 27.7457 | 60.595 | 28.1748 | 45.8639 | 28.9282 | 95.9186 |  | 46.4418 |  |  | 13.7232 | 15.3054 | 34.27 | [6 empty] | 32.7484 |  |  | 25.8135 |  |  | 14.1478 | 30.333 | 136.1383 | 8.7377 | 24.8078 | 87.8243 | 10.1239 | 24.4717 | 98.0997 | 17.4203 | 70.7962 | 10.1905 | 63.8927 | 11.4993 | 65.1005 | 9.9842 | 26.6774 | 80.2362 | 17.4867 | 27.7807 | 99.998 | 10.7238 | 23.8086 | 95.2359 | 11.1574 | 65.0401 | 16.015 | 71.4228 | 12.1 | 71.8373 | 0.50133 | 20.0113 | 0.65301 | 0.059516 | -38.0745 | 3.123 | 116.11 | 49.18 | -0.97995 | -0.19808 | 0.24989 | 0.29607 | -0.34701 | 0.46026 | 0.8363 | -0.27044 | -0.43312 | 0.0016941 | -1.7921 | -1.1363 | -0.51107 | -0.18318
42810.4443 | 369 | 18.4436 | 18.5595 | 18.5435 | 18.539 | 17.8355 | 16.4436 | 14.5149 | 16.6319 | 17.1221 | 17.2098 | 17.213 | 16.7295 | 15.7421 | 14.3571 | 14.8232 | 14.8428 | 15.4133 | 13.2863 | 13.668 | 14.8775 |  |  |  | 16.5267 | 15.9532 | 18.0347 | 95.8915 | 86.9696 | 114.3914 | 17.0838 | 16.2964 | 16.9775 | 16.7986 | 16.1508 | 17.3206 | 26.6598 | 113.6188 |  | 51.8721 | 81.4232 | 82.7433 | 59.3779 |  | 6.806 | 7.1274 | 6.4811 | 7.0403 | 7.3835 | 8.9519 | 33.5924 | 5.1635 | 6.7521 | 5.1893 | 7.3252 | 8.2019 | 41.8797 | 46.3241 | 42.6163 | 14.8421 |  |  | -0.20677 | -0.061681 | 0.066904 | -0.16691 | -0.036636 | 0.21244 | 0.39943 | 0.036636 | -0.29578 | -1.3538 | -0.035675 | -0.00057333 | -0.00059305 | 1.6138 | 15.7967 | 16.6756 | 17.206 | 17.5318 | 17.4804 | 16.4227 | 14.7569 | 16.792 | 17.1318 | 17.4214 | 17.4623 | 17.1726 | 16.3423 | 14.5325 | 37.9548 | 18.7126 | 28.0162 | 18.5866 | 15.5047 | 16.5063 | 11.7798 | 15.8507 | 15.4951 | 15.3721 | 14.2715 | 14.4628 | 15.1281 |  |  |  | 24.5813 | 99.743 | 79.1305 | 47.5275 | 0.35217 | 0.19029 | 30.4432 |  |  | 10.9243 |  |  | 16.8854 | 16.2634 | 19.7202 | 16.3362 | 15.6938 | 16.5813 | 94.2725 | 122.46 | 77.3682 | 78.0799 | 54.7932 |  | 27.8426 | 62.2906 | 28.3193 | 46.8858 | 29.1219 | 95.7972 |  | 46.6012 |  |  | 13.7241 | 15.3279 | 34.3145 | [6 empty] | 33.4095 |  |  | 25.893 |  |  | 14.1701 | 30.5348 | 136.9022 | 8.7517 | 24.7921 | 88.2533 | 10.1311 | 24.6029 | 98.6681 | 17.4613 | 71.0766 | 10.2276 | 64.2848 | 11.5066 | 65.455 | 10.0174 | 26.8876 | 80.6436 | 17.5404 | 27.9726 | 100.1723 | 10.7273 | 24.0768 | 95.5518 | 11.1854 | 65.336 | 16.0481 | 71.7525 | 12.124 | 72.2016 | 0.5801 | 20.0082 | 0.6572 | 0.058227 | -38.04 | 3.1231 | 134.02 | 49.31 | -0.62384 | -0.28976 | 0.30178 | -0.47665 | -0.22404 | 0.5395 | 0.73976 | -0.28325 | -0.47531 | -0.020101 | -1.984 | -1.4303 | -0.45073 | -0.19186
42810.4443 | 370 | 18.4513 | 18.5666 | 18.5515 | 18.5406 | 17.8423 | 16.4531 | 14.5042 | 16.6295 | 17.1271 | 17.2126 | 17.2098 | 16.7333 | 15.7419 | 14.3557 | 14.8196 | 14.8378 | 15.4155 | 13.2812 | 13.6569 | 14.8857 |  |  |  | 16.5212 | 15.9475 | 18.0483 | 96.362 | 87.2014 | 115.4849 | 17.0862 | 16.2859 | 16.9943 | 16.7998 | 16.1579 | 17.3386 | 26.7602 | 113.4235 |  | 52.1024 | 81.9248 | 83.096 | 58.251 |  | 6.8233 | 7.143 | 6.4927 | 7.0593 | 7.3937 | 8.9559 | 33.3553 | 5.2648 | 6.7587 | 5.1062 | 7.3377 | 8.211 | 41.9005 | 46.3295 | 42.6123 | 14.846 |  |  | -0.38156 | -0.25685 | -0.034292 | -0.15508 | -0.10432 | 0.14148 | 0.38891 | 0.11089 | -0.33489 | -0.64048 | -0.34863 | -0.00054048 | -0.00063412 | 1.653 | 15.806 | 16.6751 | 17.2173 | 17.5414 | 17.4895 | 16.4329 | 14.7707 | 16.7963 | 17.1405 | 17.4322 | 17.4702 | 17.1752 | 16.3473 | 14.5416 | 38.6874 | 18.8523 | 30.1127 | 19.5472 | 16.5301 | 16.6492 | 11.8752 | 15.8569 | 15.4954 | 15.3715 | 14.2676 | 14.4697 | 15.1382 |  |  |  | 24.6918 | 99.8303 | 79.1477 | 47.6819 | 0.31752 | 0.1854 | 30.7626 |  |  | 10.9346 |  |  | 16.8881 | 16.2628 | 19.7431 | 16.3442 | 15.6986 | 16.594 | 94.5665 | 122.4067 | 77.7448 | 78.3077 | 55.5856 |  | 27.9776 | 61.8786 | 28.4828 | 49.1903 | 29.4562 | 97.1919 |  | 46.8146 |  |  | 13.7419 | 15.3416 | 34.4482 | [6 empty] | 34.8326 |  |  | 25.9799 |  |  | 14.1874 | 30.899 | 137.4636 | 8.7502 | 24.9194 | 88.7327 | 10.1402 | 24.8858 | 99.2307 | 17.4907 | 71.454 | 10.2528 | 64.639 | 11.5126 | 65.7744 | 10.0497 | 26.9368 | 81.0523 | 17.6023 | 28.2948 | 100.5405 | 10.7356 | 24.2305 | 95.7875 | 11.2106 | 65.63 | 16.0904 | 71.997 | 12.1493 | 72.6317 | 0.44663 | 20.0067 | 0.6613 | 0.063844 | -38.0161 | 3.1231 | 137.2 | 50.2 | -0.84864 | -0.5913 | -0.21606 | -0.45946 | -0.37805 | 0.44027 | 0.72996 | -0.30068 | -0.45831 | -0.072731 | -2.0488 | -1.6522 | -0.41602 | -0.19242
42810.4443 | 371 | 18.4509 | 18.5623 | 18.5405 | 18.5385 | 17.8426 | 16.4514 | 14.5032 | 16.6263 | 17.1219 | 17.2087 | 17.2097 | 16.7291 | 15.7415 | 14.3568 | 14.8187 | 14.8438 | 15.4208 | 13.2925 | 13.6694 | 14.8948 |  |  |  | 16.5272 | 15.9587 | 18.0633 | 96.7653 | 87.4219 | 115.0661 | 17.0865 | 16.2831 | 17.0008 | 16.7947 | 16.1542 | 17.3481 | 26.8562 | 113.5813 |  | 52.3149 | 82.3822 | 83.4219 | 57.9698 |  | 6.8132 | 7.1472 | 6.4918 | 7.0633 | 7.4078 | 8.9524 | 33.4749 | 5.3498 | 6.7624 | 5.0161 | 7.3364 | 8.2288 | 41.907 | 46.3366 | 42.6045 | 14.8346 |  |  | -0.38156 | -0.17996 | 0.01368 | 0.16231 | -0.16477 | 0.082336 | 0.32189 | 0.23048 | -0.1041 | -0.50306 | 0.034267 | -0.00056183 | -0.00058976 | 1.6405 | 15.7893 | 16.6683 | 17.2015 | 17.523 | 17.468 | 16.417 | 14.762 | 16.7924 | 17.1263 | 17.418 | 17.4636 | 17.166 | 16.3377 | 14.5345 | 39.1061 | 18.8578 | 30.636 | 20.2458 | 16.4999 | 16.7992 | 11.9844 | 15.846 | 15.4806 | 15.3593 | 14.2662 | 14.4607 | 15.142 |  |  |  | 24.7931 | 99.8316 | 79.1678 | 47.9383 | 0.33414 | -0.045896 | 31.0264 |  |  | 10.9399 |  |  | 16.8867 | 16.2606 | 19.7622 | 16.346 | 15.6963 | 16.606 | 94.8252 | 122.7497 | 78.1518 | 78.6271 | 55.9622 |  | 28.0818 | 60.6584 | 28.6165 | 50.3555 | 29.7307 | 97.7912 |  | 46.981 |  |  | 13.7503 | 15.3551 | 34.7129 | [6 empty] | 35.5609 |  |  | 26.0326 |  |  | 14.2056 | 31.2448 | 137.799 | 8.7546 | 25.1652 | 89.1548 | 10.1591 | 25.0938 | 99.5767 | 17.5134 | 71.9576 | 10.2747 | 64.984 | 11.528 | 66.0226 | 10.045 | 27.0063 | 81.597 | 17.6504 | 28.6662 | 100.8996 | 10.7271 | 24.3854 | 96.2311 | 11.2405 | 66.0005 | 16.1246 | 72.0322 | 12.1736 | 72.9595 | 0.4994 | 20.0034 | 0.66725 | 0.062331 | -37.9803 | 3.1231 | 142.49 | 49 | -0.84818 | -0.49495 | 0.13646 | 0.47005 | -0.47513 | 0.33587 | 0.66408 | -0.3076 | -0.41987 | -0.095746 | -2.0778 | -1.6976 | -0.40496 | -0.19612
42810.4443 | 372 | 18.4547 | 18.5609 | 18.5442 | 18.5392 | 17.8412 | 16.449 | 14.5112 | 16.6257 | 17.1242 | 17.2118 | 17.2152 | 16.7324 | 15.7406 | 14.363 | 14.8094 | 14.8376 | 15.4154 | 13.2873 | 13.6803 | 14.9026 |  |  |  | 16.5203 | 15.9536 | 18.0839 | 97.1147 | 87.6808 | 115.1794 | 17.0862 | 16.2801 | 17.0107 | 16.7968 | 16.1554 | 17.361 | 26.9599 | 113.6908 |  | 52.523 | 82.775 | 83.7602 | 60.2286 |  | 6.8257 | 7.1528 | 6.5015 | 7.0904 | 7.4307 | 8.9576 | 33.9588 | 5.3571 | 6.7742 | 4.9734 | 7.3447 | 8.2319 | 41.9041 | 46.3326 | 42.5889 | 14.826 |  |  | -0.4545 | -0.10834 | 0.11816 | 0.039426 | -0.009692 | 0.04094 | 0.33569 | 0.09446 | -0.0054334 | -0.038566 | -0.27849 | -0.00060619 | -0.00060126 | 1.6649 | 15.7971 | 16.6671 | 17.2078 | 17.5297 | 17.4805 | 16.4332 | 14.7596 | 16.7958 | 17.1302 | 17.4319 | 17.4652 | 17.1725 | 16.3401 | 14.5327 | 38.6068 | 18.2085 | 29.476 | 19.9813 | 16.5679 | 16.9111 | 12.0654 | 15.846 | 15.4768 | 15.3597 | 14.263 | 14.4632 | 15.1456 |  |  |  | 24.8879 | 99.9837 | 79.3355 | 48.8567 | 0.29807 | -0.17293 | 31.2212 |  |  | 10.9472 |  |  | 16.8872 | 16.272 | 19.785 | 16.347 | 15.697 | 16.6159 | 95.1606 | 123.3747 | 78.5281 | 79.0031 | 55.774 |  | 28.1842 | 60.0358 | 28.7332 | 49.5244 | 29.9336 | 97.5576 |  | 47.1571 |  |  | 13.7553 | 15.3842 | 34.8218 | [6 empty] | 36.1346 |  |  | 26.0303 |  |  | 14.2221 | 31.3934 | 138.0427 | 8.7601 | 25.1856 | 89.5262 | 10.1696 | 25.1426 | 99.6839 | 17.5375 | 72.3294 | 10.2956 | 65.262 | 11.5389 | 66.3476 | 10.0116 | 27.0889 | 82.142 | 17.6969 | 29.0129 | 101.1875 | 10.7253 | 24.4364 | 96.6939 | 11.2527 | 66.4268 | 16.1661 | 72.302 | 12.1878 | 73.1824 | 0.62189 | 20.0007 | 0.67121 | 0.063858 | -37.985 | 3.1231 | 142.11 | 49.66 | -0.92584 | -0.38403 | 0.40107 | 0.23167 | -0.11523 | 0.23684 | 0.67818 | -0.29889 | -0.3986 | -0.065744 | -2.0093 | -1.5593 | -0.46419 | -0.21843
42810.4444 | 373 | 18.4476 | 18.557 | 18.5373 | 18.5373 | 17.8413 | 16.4499 | 14.5021 | 16.6297 | 17.1262 | 17.2075 | 17.2124 | 16.7303 | 15.732 | 14.3597 | 14.8219 | 14.8486 | 15.4259 | 13.2931 | 13.6835 | 14.9147 |  |  |  | 16.5274 | 15.9744 | 18.1019 | 97.7314 | 88.0009 | 118.5935 | 17.0868 | 16.2775 | 17.0163 | 16.7935 | 16.1537 | 17.3688 | 27.0716 | 113.8552 |  | 52.7401 | 83.1309 | 84.0906 | 62.3415 |  | 6.8202 | 7.1695 | 6.4994 | 7.1006 | 7.4268 | 8.9758 | 34.2824 | 5.3886 | 6.7755 | 4.9859 | 7.3509 | 8.2348 | 41.8973 | 46.3483 | 42.5726 | 14.8115 |  |  | -0.69304 | -0.26867 | -0.06912 | -0.00657 | 0.01002 | -0.10166 | 0.29363 | 0.12074 | 0.61826 | -1.0158 | -0.0036843 | -0.00063576 | -0.00062097 | 1.6873 | 15.8012 | 16.664 | 17.2157 | 17.529 | 17.4765 | 16.4251 | 14.7719 | 16.8033 | 17.1332 | 17.4208 | 17.4665 | 17.1653 | 16.3433 | 14.5342 | 38.4108 | 17.9611 | 27.9189 | 19.356 | 16.362 | 17.0522 | 12.1308 | 15.8407 | 15.4895 | 15.3635 | 14.2696 | 14.4619 | 15.1577 |  |  |  | 25.0137 | 100.1428 | 79.5554 | 49.9514 | 0.25269 | -0.051542 | 31.3649 |  |  | 10.9438 |  |  | 16.8943 | 16.2837 | 19.8151 | 16.3496 | 15.7053 | 16.6342 | 95.5103 | 123.8777 | 78.9205 | 79.358 | 55.831 |  | 28.3211 | 60.6598 | 28.8854 | 49.4342 | 30.1811 | 97.2275 |  | 47.3906 |  |  | 13.7759 | 15.3782 | 34.9187 | [6 empty] | 36.9901 |  |  | 26.037 |  |  | 14.2517 | 31.55 | 138.5595 | 8.7602 | 25.101 | 89.9211 | 10.1789 | 25.5297 | 99.7937 | 17.561 | 72.5314 | 10.3243 | 65.6232 | 11.5511 | 66.5569 | 9.9863 | 27.0033 | 82.5847 | 17.7345 | 29.1482 | 101.512 | 10.7345 | 24.525 | 97.0912 | 11.2571 | 66.7891 | 16.1739 | 72.8377 | 12.1862 | 73.5025 | 0.57105 | 19.9983 | 0.67768 | 0.062027 | -37.998 | 3.1231 | 178.27 | 49.25 | -1.1483 | -0.60479 | -0.30676 | -0.094575 | 0.11717 | -0.37321 | 0.63429 | -0.29582 | -0.41076 | -0.054799 | -1.971 | -1.3787 | -0.51909 | -0.24459
42810.4444 | 374 | 18.4554 | 18.5617 | 18.5404 | 18.536 | 17.8461 | 16.4435 | 14.5069 | 16.6364 | 17.1231 | 17.2162 | 17.2166 | 16.7375 | 15.7467 | 14.3647 | 14.8147 | 14.8404 | 15.4146 | 13.2827 | 13.6793 | 14.9106 |  |  |  | 16.5273 | 15.961 | 18.1026 | 98.5963 | 88.3083 | 119.993 | 17.0874 | 16.2865 | 17.0182 | 16.785 | 16.1522 | 17.3833 | 27.184 | 113.5389 |  | 52.948 | 83.4959 | 84.4488 | 61.5904 |  | 6.8097 | 7.1725 | 6.5123 | 7.0995 | 7.4148 | 8.98 | 34.5168 | 5.3223 | 6.776 | 4.992 | 7.3604 | 8.2278 | 41.8798 | 46.3531 | 42.5644 | 14.8011 |  |  | -0.30008 | -0.021597 | 0.050476 | -0.086738 | -0.10366 | 0.18156 | 0.53019 | 0.053064 | -0.29831 | 0.5281 | -0.0319 | -0.00058976 | -0.00060455 | 1.6636 | 15.7957 | 16.6671 | 17.2186 | 17.5331 | 17.4892 | 16.4238 | 14.7647 | 16.7976 | 17.1335 | 17.4229 | 17.4667 | 17.1665 | 16.341 | 14.5364 | 37.5839 | 17.8114 | 27.5647 | 18.9053 | 16.3119 | 17.1551 | 12.2124 | 15.8416 | 15.4839 | 15.3638 | 14.2669 | 14.4677 | 15.1611 |  |  |  | 25.1273 | 100.4995 | 79.6718 | 50.2216 | 0.074606 | -0.24313 | 31.4698 |  |  | 10.9242 |  |  | 16.8947 | 16.2788 | 19.8273 | 16.3407 | 15.7061 | 16.6414 | 95.8861 | 124.3575 | 79.3218 | 79.6901 | 56.9247 |  | 28.4452 | 61.4726 | 29.0086 | 49.908 | 30.3642 | 96.7577 |  | 47.5881 |  |  | 13.7977 | 15.4046 | 35.6637 | [6 empty] | 37.3988 |  |  | 26.0458 |  |  | 14.2483 | 31.8257 | 138.6359 | 8.7381 | 25.5834 | 90.3066 | 10.1703 | 25.9995 | 100.0304 | 17.5775 | 72.6551 | 10.3383 | 65.964 | 11.5511 | 66.7514 | 9.9886 | 26.92 | 82.942 | 17.7689 | 29.2943 | 101.6676 | 10.7363 | 24.866 | 97.5083 | 11.2522 | 67.1077 | 16.1892 | 73.0896 | 12.2052 | 73.7195 | 0.56103 | 19.9947 | 0.68192 | 0.064618 | -38.0201 | 3.1231 | 181.62 | 48.93 | -0.75694 | -0.17147 | 0.26214 | -0.34364 | -0.37687 | 0.49877 | 0.85233 | -0.32198 | -0.42915 | -0.061712 | -1.8671 | -1.3298 | -0.49441 | -0.24825
42810.4444 | 375 | 18.4419 | 18.5548 | 18.5389 | 18.5288 | 17.8397 | 16.4414 | 14.5017 | 16.6314 | 17.1135 | 17.207 | 17.2079 | 16.7335 | 15.7427 | 14.3606 | 14.8096 | 14.8338 | 15.418 | 13.2866 | 13.6745 | 14.9135 |  |  |  | 16.5214 | 15.9612 | 18.1196 | 99.1718 | 88.5912 | 119.7944 | 17.0787 | 16.2853 | 17.0367 | 16.7908 | 16.1413 | 17.3792 | 27.2915 | 112.5372 |  | 53.139 | 83.9391 | 84.8464 | 62.1868 |  | 6.812 | 7.1879 | 6.5147 | 7.1022 | 7.4037 | 8.9666 | 35.1172 | 5.2485 | 6.777 | 4.9862 | 7.3617 | 8.2273 | 41.8794 | 46.3603 | 42.5601 | 14.7929 |  |  | -0.32177 | -0.069565 | 0.16087 | -0.18991 | -0.064892 | 0.12899 | 0.47894 | 0.21011 | -0.071403 | 0.0069606 | 0.13779 | -0.00061276 | -0.00060619 | 1.6196 | 15.7884 | 16.6659 | 17.2162 | 17.5307 | 17.4792 | 16.4176 | 14.7612 | 16.786 | 17.133 | 17.425 | 17.4592 | 17.1726 | 16.3339 | 14.5332 | 36.1304 | 16.9566 | 25.7058 | 18.4954 | 16.2693 | 17.2386 | 12.2524 | 15.8499 | 15.4898 | 15.3606 | 14.2761 | 14.4802 | 15.1746 |  |  |  | 25.2524 | 100.6923 | 79.968 | 50.079 | -0.14582 | -0.20154 | 31.6743 |  |  | 10.9162 |  |  | 16.885 | 16.2776 | 19.8464 | 16.343 | 15.7014 | 16.6473 | 96.3079 | 124.888 | 79.6839 | 80.0335 | 57.7023 |  | 28.5645 | 62.3691 | 29.1282 | 49.9667 | 30.5389 | 96.1425 |  | 47.7594 |  |  | 13.7821 | 15.4179 | 36.4117 | [6 empty] | 37 |  |  | 26.1156 |  |  | 14.2535 | 31.9469 | 138.9061 | 8.6975 | 26.0939 | 90.6496 | 10.1869 | 26.2153 | 100.5069 | 17.5885 | 72.8849 | 10.3632 | 66.2073 | 11.5657 | 67.0791 | 9.996 | 27.1002 | 83.2838 | 17.8181 | 29.6919 | 101.7144 | 10.7703 | 25.2358 | 97.7858 | 11.2633 | 67.3397 | 16.247 | 73.6325 | 12.2362 | 73.9897 | 0.55025 | 19.9911 | 0.68651 | 0.064227 | -37.9422 | 3.1232 | 178.48 | 50.62 | -0.78362 | -0.30775 | 0.468 | -0.50848 | -0.29818 | 0.4204 | 0.81007 | -0.33952 | -0.44998 | -0.057382 | -1.6959 | -1.1186 | -0.50733 | -0.24006
42810.4444 | 376 | 18.4348 | 18.5601 | 18.5381 | 18.5324 | 17.8373 | 16.4427 | 14.4941 | 16.6258 | 17.1164 | 17.2159 | 17.2121 | 16.722 | 15.7451 | 14.3511 | 14.8116 | 14.8488 | 15.4219 | 13.2843 | 13.6883 | 14.9341 |  |  |  | 16.5249 | 15.9692 | 18.1562 | 99.4128 | 88.972 | 118.1596 | 17.0826 | 16.2903 | 17.0425 | 16.7947 | 16.1626 | 17.4035 | 27.4725 | 112.8031 |  | 53.3644 | 84.4446 | 85.2709 | 65.835 |  | 6.8171 | 7.1855 | 6.5204 | 7.111 | 7.385 | 8.9455 | 36.1243 | 5.1607 | 6.7886 | 4.9524 | 7.3768 | 8.2355 | 41.8703 | 46.3603 | 42.5641 | 14.7967 |  |  | -0.38354 | -0.18653 | 0.091876 | -0.31345 | -0.01298 | 0.38724 | 0.43491 | 0.2916 | -0.085609 | -0.48565 | -0.13065 | -0.00057497 | -0.00062262 | 1.53 | 15.7871 | 16.6688 | 17.2092 | 17.5344 | 17.4808 | 16.4221 | 14.7688 | 16.7901 | 17.1318 | 17.43 | 17.4626 | 17.1772 | 16.3357 | 14.5308 | 34.4153 | 16.2142 | 24.2334 | 17.5398 | 15.6739 | 17.2999 | 12.3021 | 15.847 | 15.4879 | 15.3637 | 14.274 | 14.4783 | 15.1807 |  |  |  | 25.3959 | 100.7879 | 80.408 | 51.1795 | 0.26606 | -0.19232 | 31.9835 |  |  | 10.9098 |  |  | 16.8829 | 16.2817 | 19.873 | 16.3519 | 15.7017 | 16.6593 | 96.6938 | 125.1553 | 79.9973 | 80.3912 | 58.2429 |  | 28.6979 | 64.4752 | 29.2587 | 50.0298 | 30.7696 | 95.0679 |  | 47.9249 |  |  | 13.8012 | 15.4411 | 36.6064 | [6 empty] | 37.62 |  |  | 26.2103 |  |  | 14.2652 | 32.0632 | 138.7683 | 8.6855 | 26.4401 | 90.9046 | 10.2119 | 26.3827 | 101.3022 | 17.6205 | 73.022 | 10.3863 | 66.4391 | 11.5998 | 67.5053 | 9.9932 | 27.571 | 83.6114 | 17.8533 | 29.9725 | 101.886 | 10.7669 | 25.4165 | 98.2658 | 11.2497 | 67.5804 | 16.2844 | 74.0039 | 12.2374 | 74.426 | 0.70837 | 19.9751 | 0.69051 | 0.064444 | -38.0796 | 3.1232 | 165.82 | 49.23 | -0.85375 | -0.50395 | 0.35368 | -0.65326 | -0.13335 | 0.72838 | 0.77191 | -0.35001 | -0.50404 | -0.051257 | -1.4982 | -0.94924 | -0.60253 | -0.26578
42810.4444 | 377 | 18.4273 | 18.5512 | 18.5297 | 18.5235 | 17.8165 | 16.4343 | 14.4907 | 16.6149 | 17.1134 | 17.2011 | 17.1992 | 16.7146 | 15.7306 | 14.3473 | 14.8131 | 14.8468 | 15.424 | 13.2978 | 13.6889 | 14.9376 |  |  |  | 16.5279 | 15.9744 | 18.1686 | 99.6172 | 89.3514 | 117.9923 | 17.0755 | 16.2833 | 17.0513 | 16.7891 | 16.1566 | 17.4182 | 27.665 | 113.9455 |  | 53.5712 | 84.8581 | 85.5577 | 67.3613 |  | 6.8099 | 7.2012 | 6.528 | 7.1136 | 7.3929 | 8.9373 | 36.0156 | 5.1002 | 6.7946 | 4.9074 | 7.3954 | 8.2304 | 41.8411 | 46.3282 | 42.5618 | 14.7762 |  |  | -0.32505 | -0.084681 | 0.05902 | -0.12157 | -0.041236 | 0.12045 | 0.58802 | -0.00148 | -0.6048 | -0.63566 | -0.0011012 | -0.00058483 | -0.00058976 | 1.5415 | 15.8037 | 16.6738 | 17.2136 | 17.5383 | 17.4815 | 16.4236 | 14.7673 | 16.7974 | 17.135 | 17.4319 | 17.4607 | 17.174 | 16.3382 | 14.5301 | 34.3548 | 16.4684 | 22.8884 | 16.3917 | 14.8342 | 17.4103 | 12.3496 | 15.8427 | 15.491 | 15.3694 | 14.2651 | 14.4838 | 15.1894 |  |  |  | 25.5397 | 100.9521 | 80.8649 | 52.7899 | 0.40971 | -0.078078 | 32.2402 |  |  | 10.8992 |  |  | 16.8857 | 16.2847 | 19.8954 | 16.3504 | 15.7007 | 16.6679 | 96.9923 | 125.4349 | 80.2469 | 80.6736 | 59.1526 |  | 28.835 | 66.0422 | 29.4064 | 50.2823 | 30.9788 | 95.1898 |  | 48.098 |  |  | 13.8201 | 15.4502 | 36.5227 | [6 empty] | 37.4581 |  |  | 26.2775 |  |  | 14.2802 | 32.4772 | 138.9147 | 8.6556 | 26.5783 | 91.012 | 10.2258 | 26.6217 | 101.7672 | 17.6187 | 73.1237 | 10.3897 | 66.9558 | 11.6088 | 67.8585 | 9.9976 | 27.7611 | 83.9195 | 17.9209 | 29.971 | 101.8774 | 10.7791 | 25.4923 | 98.5943 | 11.2572 | 67.8953 | 16.3363 | 74.3862 | 12.2525 | 74.778 | 0.63403 | 19.9707 | 0.69658 | 0.063677 | -38.0399 | 3.1232 | 172.95 | 49.31 | -0.7858 | -0.33956 | 0.28348 | -0.40684 | -0.23768 | 0.40622 | 0.89754 | -0.37061 | -0.54253 | -0.051131 | -1.4786 | -0.79427 | -0.63839 | -0.30565
42810.4444 | 378 | 18.4346 | 18.5558 | 18.5361 | 18.5329 | 17.834 | 16.4408 | 14.4963 | 16.6232 | 17.125 | 17.2067 | 17.2078 | 16.7304 | 15.7433 | 14.3548 | 14.8058 | 14.8356 | 15.42 | 13.2907 | 13.6809 | 14.9358 |  |  |  | 16.5234 | 15.9657 | 18.1728 | 99.7115 | 89.5908 | 117.0467 | 17.0776 | 16.276 | 17.06 | 16.7867 | 16.1566 | 17.4312 | 27.8439 | 114.6021 |  | 53.794 | 85.2233 | 85.8448 | 68.556 |  | 6.8167 | 7.2113 | 6.531 | 7.1295 | 7.4056 | 8.9454 | 35.5867 | 5.1128 | 6.7944 | 4.8627 | 7.3939 | 8.2335 | 41.8345 | 46.3083 | 42.5522 | 14.7749 |  |  | -0.40785 | 0.056599 | 0.13787 | -0.019714 | 0.063248 | 0.5042 | 0.54268 | -0.039592 | 0.46764 | 0.67811 | -0.043623 | -0.00064561 | -0.0005454 | 1.6319 | 15.8002 | 16.6677 | 17.2117 | 17.5313 | 17.4757 | 16.4186 | 14.7607 | 16.7942 | 17.1257 | 17.427 | 17.462 | 17.1678 | 16.3311 | 14.5279 | 35.0354 | 17.691 | 24.4916 | 16.524 | 14.3801 | 17.52 | 12.4172 | 15.8511 | 15.4976 | 15.3659 | 14.2785 | 14.4846 | 15.1978 |  |  |  | 25.6706 | 100.9885 | 81.0429 | 53.229 | 0.54585 | 0.45265 | 32.3505 |  |  | 10.8924 |  |  | 16.8908 | 16.2782 | 19.9239 | 16.3424 | 15.7032 | 16.6761 | 97.371 | 125.5225 | 80.4273 | 80.9466 | 59.3256 |  | 28.9756 | 65.4572 | 29.5355 | 51.2478 | 31.1699 | 96.0159 |  | 48.2567 |  |  | 13.8268 | 15.4536 | 36.2134 | [6 empty] | 37.5219 |  |  | 26.2872 |  |  | 14.2951 | 32.9008 | 138.7178 | 8.6491 | 26.6984 | 91.2374 | 10.2414 | 26.7844 | 102.1926 | 17.629 | 73.2308 | 10.4092 | 67.3075 | 11.6257 | 68.1657 | 10.0126 | 27.7725 | 84.2506 | 17.9816 | 30.0443 | 101.9052 | 10.7918 | 25.6294 | 99.0324 | 11.2576 | 68.2 | 16.3956 | 74.6219 | 12.2736 | 75.1467 | 0.54254 | 19.9653 | 0.7012 | 0.063286 | -38.071 | 3.1232 | 159.94 | 50.35 | -0.87914 | 0.27761 | 0.43328 | -0.16384 | 0.29437 | 0.83113 | 0.86226 | -0.37063 | -0.52189 | -0.07142 | -1.5414 | -0.96453 | -0.66551 | -0.31342
42810.4444 | 379 | 18.4311 | 18.5526 | 18.536 | 18.5328 | 17.8352 | 16.441 | 14.5002 | 16.6223 | 17.1246 | 17.2084 | 17.2147 | 16.728 | 15.7436 | 14.358 | 14.8066 | 14.8388 | 15.4273 | 13.2912 | 13.6833 | 14.9549 |  |  |  | 16.5224 | 15.9725 | 18.1968 | 100.0172 | 89.7826 | 118.1206 | 17.0738 | 16.2782 | 17.0671 | 16.7809 | 16.1487 | 17.4402 | 27.9836 | 115.1713 |  | 54.028 | 85.5438 | 86.1888 | 68.6968 |  | 6.805 | 7.2059 | 6.5155 | 7.1305 | 7.4178 | 8.921 | 35.6006 | 5.127 | 6.803 | 4.7898 | 7.4054 | 8.2316 | 41.819 | 46.283 | 42.5514 | 14.7713 |  |  | -0.38419 | -0.007141 | 0.030764 | 0.27927 | -0.05832 | 0.1809 | 0.44082 | 0.26925 | -0.40864 | -0.74077 | -0.17516 | -0.00060947 | -0.00065383 | 1.6566 | 15.7854 | 16.6607 | 17.2028 | 17.5255 | 17.4656 | 16.4159 | 14.7584 | 16.7926 | 17.1261 | 17.4247 | 17.4583 | 17.1696 | 16.3333 | 14.5254 | 36.1433 | 18.3121 | 26.6973 | 17.2928 | 14.784 | 17.6596 | 12.5128 | 15.8471 | 15.4813 | 15.3657 | 14.2748 | 14.4842 | 15.1944 |  |  |  | 25.7732 | 101.0458 | 81.3305 | 53.1453 | 0.51911 | 0.29456 | 32.4011 |  |  | 10.8948 |  |  | 16.8969 | 16.2833 | 19.953 | 16.3495 | 15.7071 | 16.6925 | 97.8308 | 125.8376 | 80.6855 | 81.2197 | 58.5308 |  | 29.0909 | 65.1606 | 29.6613 | 54.8237 | 31.493 | 96.1206 |  | 48.4145 |  |  | 13.8364 | 15.4755 | 36.4156 | [6 empty] | 39.6121 |  |  | 26.3089 |  |  | 14.324 | 33.0776 | 138.8649 | 8.6404 | 26.794 | 91.6664 | 10.2576 | 26.7302 | 102.819 | 17.6353 | 73.3304 | 10.4359 | 67.5603 | 11.6337 | 68.4233 | 10.0148 | 27.9855 | 84.5681 | 18.0411 | 30.3306 | 101.9263 | 10.7939 | 25.8271 | 99.3349 | 11.2519 | 68.4572 | 16.4266 | 74.9106 | 12.288 | 75.5549 | 0.42178 | 19.9598 | 0.7068 | 0.06291 | -37.9958 | 3.1232 | 162.61 | 48.98 | -0.85444 | -0.098606 | 0.20466 | 0.61665 | -0.28265 | 0.49782 | 0.7771 | -0.34463 | -0.50936 | -0.1597 | -1.6482 | -1.1985 | -0.66467 | -0.30762
42810.4444 | 380 | 18.4344 | 18.5584 | 18.5463 | 18.5374 | 17.841 | 16.4454 | 14.5003 | 16.6301 | 17.1244 | 17.2099 | 17.2159 | 16.7269 | 15.7429 | 14.3632 | 14.7994 | 14.8331 | 15.412 | 13.2823 | 13.6887 | 14.9566 |  |  |  | 16.5187 | 15.9694 | 18.2067 | 100.2796 | 89.9242 | 118.3582 | 17.0675 | 16.2727 | 17.0725 | 16.7744 | 16.1397 | 17.4388 | 28.1455 | 115.1414 |  | 54.2397 | 85.8389 | 86.5615 | 69.5838 |  | 6.7998 | 7.2008 | 6.511 | 7.1359 | 7.4275 | 8.9172 | 35.7736 | 5.1077 | 6.8028 | 4.7497 | 7.4083 | 8.2345 | 41.7906 | 46.2711 | 42.5496 | 14.7622 |  |  | -0.091777 | 0.18474 | 0.10108 | -0.005914 | 0.1421 | 0.48515 | 0.42308 | 0.13126 | -0.2446 | -0.69923 | -0.15688 | -0.00060783 | -0.00059469 | 1.6631 | 15.7948 | 16.6558 | 17.2007 | 17.5245 | 17.4625 | 16.4124 | 14.7613 | 16.7903 | 17.1146 | 17.4109 | 17.4509 | 17.1639 | 16.3335 | 14.5188 | 38.0451 | 18.9181 | 28.8112 | 17.8382 | 14.5383 | 17.8246 | 12.6137 | 15.8506 | 15.4889 | 15.3718 | 14.2777 | 14.4867 | 15.2063 |  |  |  | 25.8884 | 101.1047 | 81.6464 | 53.0913 | 0.41497 | 0.16564 | 32.4311 |  |  | 10.9045 |  |  | 16.8873 | 16.2829 | 19.9704 | 16.3518 | 15.7076 | 16.7013 | 98.2604 | 126.1432 | 80.9461 | 81.4648 | 58.4425 |  | 29.2428 | 65.054 | 29.7996 | 55.9986 | 31.8199 | 97.1377 |  | 48.6133 |  |  | 13.8617 | 15.5165 | 36.7553 | [6 empty] | 41.1406 |  |  | 26.2909 |  |  | 14.3417 | 33.1798 | 139.0664 | 8.6364 | 26.8654 | 92.0076 | 10.2774 | 26.7366 | 102.9568 | 17.6573 | 73.4661 | 10.4612 | 67.7878 | 11.6494 | 68.6876 | 10.0301 | 28.3856 | 84.9036 | 18.0845 | 30.7187 | 102.1067 | 10.8079 | 26.0261 | 99.5181 | 11.261 | 68.7165 | 16.4584 | 75.1204 | 12.2971 | 75.9399 | 0.69046 | 19.9458 | 0.71327 | 0.06283 | -37.9543 | 3.1231 | 160.82 | 48.98 | -0.41774 | 0.50153 | 0.37097 | -0.089734 | 0.4412 | 0.81523 | 0.7613 | -0.337 | -0.50169 | -0.18116 | -1.8403 | -1.4216 | -0.68381 | -0.30223
42810.4444 | 381 | 18.4359 | 18.5603 | 18.546 | 18.5341 | 17.8375 | 16.4418 | 14.502 | 16.6334 | 17.121 | 17.2073 | 17.2101 | 16.7267 | 15.7384 | 14.3564 | 14.7998 | 14.8357 | 15.4122 | 13.2846 | 13.6863 | 14.9621 |  |  |  | 16.5196 | 15.9679 | 18.222 | 100.5459 | 90.0436 | 118.6997 | 17.069 | 16.2776 | 17.089 | 16.7876 | 16.1472 | 17.451 | 28.328 | 114.4479 |  | 54.4497 | 86.2008 | 86.9486 | 69.2048 |  | 6.799 | 7.1904 | 6.5066 | 7.1348 | 7.4326 | 8.9281 | 35.8306 | 4.9864 | 6.8074 | 4.7386 | 7.4191 | 8.2548 | 41.7783 | 46.2897 | 42.5556 | 14.7622 |  |  | -0.38945 | 0.096683 | 0.055076 | -0.19253 | 0.06982 | -0.076028 | 0.19506 | -0.044848 | 0.094591 | -0.62181 | -0.16721 | -0.0005914 | -0.00060947 | 1.6717 | 15.7919 | 16.6675 | 17.2073 | 17.5318 | 17.4811 | 16.4203 | 14.7627 | 16.7955 | 17.1303 | 17.4224 | 17.4624 | 17.1671 | 16.3362 | 14.5258 | 39.0168 | 18.2836 | 28.768 | 19.2352 | 15.4601 | 17.9673 | 12.7043 | 15.8536 | 15.4812 | 15.373 | 14.2678 | 14.4842 | 15.2138 |  |  |  | 25.9982 | 101.2482 | 82.0471 | 52.6864 | 0.41234 | 0.037853 | 32.6162 |  |  | 10.9041 |  |  | 16.886 | 16.2788 | 19.9781 | 16.3427 | 15.6968 | 16.7109 | 98.5812 | 126.5583 | 81.1424 | 81.6636 | 58.7359 |  | 29.3433 | 65.2417 | 29.9089 | 56.5213 | 32.0203 | 97.0367 |  | 48.7521 |  |  | 13.8668 | 15.5525 | 36.8653 | [6 empty] | 40.832 |  |  | 26.3197 |  |  | 14.3563 | 33.4534 | 139.4991 | 8.6317 | 27.1204 | 92.269 | 10.275 | 27.0082 | 102.9464 | 17.6708 | 73.5771 | 10.4763 | 68.0288 | 11.657 | 68.971 | 10.0365 | 28.4469 | 85.2556 | 18.1009 | 30.8335 | 102.2292 | 10.8176 | 26.1871 | 99.6418 | 11.2671 | 69.001 | 16.4701 | 75.2883 | 12.309 | 76.3323 | 0.92042 | 19.939 | 0.72159 | 0.063373 | -38.091 | 3.1232 | 131.26 | 50.12 | -0.8609 | 0.36281 | 0.27384 | -0.51199 | 0.30927 | -0.32273 | 0.51694 | -0.34173 | -0.50318 | -0.18882 | -1.9316 | -1.4063 | -0.66708 | -0.28726
42810.4445 | 382 | 18.4364 | 18.5528 | 18.5487 | 18.5294 | 17.8375 | 16.4429 | 14.4977 | 16.6321 | 17.118 | 17.2113 | 17.2085 | 16.7319 | 15.736 | 14.3625 | 14.8082 | 14.8337 | 15.4115 | 13.2851 | 13.6882 | 14.9678 |  |  |  | 16.5206 | 15.9698 | 18.2331 | 100.7994 | 90.2205 | 118.9864 | 17.0625 | 16.2717 | 17.0876 | 16.7805 | 16.1435 | 17.4681 | 28.4659 | 114.1325 |  | 54.665 | 86.6109 | 87.2627 | 69.1213 |  | 6.7924 | 7.186 | 6.5201 | 7.1407 | 7.4441 | 8.9297 | 35.3444 | 4.8331 | 6.8201 | 4.7112 | 7.431 | 8.2747 | 41.7431 | 46.3059 | 42.5542 | 14.7556 |  |  | -0.30665 | -0.12739 | 0.19242 | -0.24379 | 0.071788 | -0.012944 | 0.56174 | 0.15952 | -1.781 | -0.6986 | -0.43904 | -0.00057826 | -0.0006374 | 1.6827 | 15.7915 | 16.6664 | 17.2087 | 17.5253 | 17.4766 | 16.4246 | 14.7587 | 16.7896 | 17.1251 | 17.4148 | 17.4559 | 17.1691 | 16.3296 | 14.5221 | 39.2741 | 18.7138 | 29.6642 | 19.4217 | 16.5144 | 18.0921 | 12.784 | 15.852 | 15.4837 | 15.3668 | 14.2766 | 14.4921 | 15.2295 |  |  |  | 26.1222 | 101.461 | 82.5694 | 52.7539 | 0.36615 | 0.20215 | 32.8561 |  |  | 10.9051 |  |  | 16.8868 | 16.2844 | 20.0073 | 16.3443 | 15.7045 | 16.7239 | 98.9673 | 126.6421 | 81.3508 | 81.8258 | 58.712 |  | 29.4488 | 65.5795 | 30.0282 | 57.1686 | 32.2732 | 96.5866 |  | 48.8951 |  |  | 13.8736 | 15.5693 | 36.6503 | [6 empty] | 41.2401 |  |  | 26.4054 |  |  | 14.3717 | 33.6254 | 139.9682 | 8.6344 | 27.4308 | 92.592 | 10.2693 | 27.3242 | 103.0362 | 17.6873 | 73.727 | 10.4696 | 68.2963 | 11.6663 | 69.368 | 10.0395 | 28.3764 | 85.597 | 18.1271 | 30.885 | 102.3018 | 10.8256 | 26.4334 | 99.8061 | 11.283 | 69.2651 | 16.5049 | 75.4935 | 12.3262 | 76.7686 | 0.77 | 19.933 | 0.72881 | 0.063793 | -38.0642 | 3.1231 | 140.04 | 49.35 | -0.7642 | -0.41647 | 0.51183 | -0.57612 | 0.3136 | -0.13316 | 0.87724 | -0.33747 | -0.50849 | -0.19815 | -1.9456 | -1.4966 | -0.66007 | -0.28494
42810.4445 | 383 | 18.4298 | 18.5558 | 18.5421 | 18.5316 | 17.8236 | 16.444 | 14.4953 | 16.6263 | 17.1094 | 17.2089 | 17.208 | 16.7278 | 15.744 | 14.3545 | 14.8023 | 14.8296 | 15.4122 | 13.278 | 13.681 | 14.9692 |  |  |  | 16.5181 | 15.9668 | 18.2428 | 101.0921 | 90.372 | 119.243 | 17.0683 | 16.2799 | 17.1051 | 16.7738 | 16.1457 | 17.4859 | 28.6443 | 114.3481 |  | 54.8805 | 86.9066 | 87.5629 | 70.3305 |  | 6.7857 | 7.179 | 6.518 | 7.141 | 7.4496 | 8.9218 | 35.6167 | 4.7337 | 6.8184 | 4.6479 | 7.4331 | 8.2822 | 41.7241 | 46.3414 | 42.5379 | 14.7477 |  |  | -0.40128 | -0.062997 | 0.17139 | -0.16099 | 0.18087 | 0.10139 | 0.39746 | 0.28962 | 0.26311 | 0.81553 | -0.19881 | -0.00063247 | -0.0005684 | 1.6935 | 15.7928 | 16.6693 | 17.2144 | 17.5347 | 17.4743 | 16.4279 | 14.7628 | 16.7924 | 17.1253 | 17.4233 | 17.4572 | 17.1719 | 16.3303 | 14.5273 | 39.1964 | 18.1963 | 29.383 | 19.0216 | 16.7134 | 18.2085 | 12.8604 | 15.8542 | 15.4989 | 15.375 | 14.2809 | 14.4945 | 15.2302 |  |  |  | 26.234 | 101.5765 | 82.8717 | 52.8931 | 0.10783 | -0.042697 | 32.9623 |  |  | 10.9135 |  |  | 16.8845 | 16.2947 | 20.0371 | 16.3524 | 15.7131 | 16.7397 | 99.1664 | 126.7069 | 81.5308 | 81.9751 | 58.8621 |  | 29.5795 | 66.1635 | 30.1536 | 55.2131 | 32.4738 | 95.857 |  | 49.0948 |  |  | 13.8854 | 15.5906 | 36.5918 | [6 empty] | 41.0789 |  |  | 26.4365 |  |  | 14.383 | 33.6642 | 140.1028 | 8.633 | 27.4655 | 92.9115 | 10.2735 | 27.5413 | 103.1255 | 17.7138 | 73.873 | 10.4858 | 68.5217 | 11.6714 | 69.8878 | 10.0509 | 28.4816 | 85.9664 | 18.1865 | 31.0588 | 102.4959 | 10.8304 | 26.6519 | 100.0819 | 11.2961 | 69.5649 | 16.5267 | 75.7015 | 12.34 | 77.133 | 0.66061 | 19.9254 | 0.73843 | 0.066406 | -38.0911 | 3.1232 | 151.25 | 49.3 | -0.87448 | -0.29286 | 0.48305 | -0.46817 | 0.49777 | 0.37269 | 0.73789 | -0.33719 | -0.52044 | -0.13696 | -1.9234 | -1.4564 | -0.68759 | -0.28502
42810.4445 | 384 | 18.4291 | 18.5439 | 18.54 | 18.532 | 17.8358 | 16.4435 | 14.4883 | 16.6209 | 17.1278 | 17.2095 | 17.206 | 16.7266 | 15.7343 | 14.3517 | 14.7979 | 14.8288 | 15.4119 | 13.2831 | 13.6852 | 14.9757 |  |  |  | 16.5197 | 15.9675 | 18.2634 | 101.3603 | 90.5189 | 118.9701 | 17.0769 | 16.2819 | 17.1266 | 16.7912 | 16.1638 | 17.5075 | 28.8246 | 114.1837 |  | 55.0848 | 87.1198 | 87.7909 | 70.2748 |  | 6.8 | 7.1999 | 6.5039 | 7.1502 | 7.4679 | 8.9374 | 36.0914 | 4.6667 | 6.8232 | 4.6499 | 7.4399 | 8.2924 | 41.7171 | 46.3784 | 42.5255 | 14.7447 |  |  | -0.49524 | -0.009769 | 0.047848 | -0.19648 | 0.15459 | 0.12571 | 0.452 | 0.011008 | -0.0003738 | 0.031088 | -0.12926 | -0.0005569 | -0.00058319 | 1.6182 | 15.794 | 16.6692 | 17.2092 | 17.5239 | 17.473 | 16.4247 | 14.7657 | 16.7866 | 17.1242 | 17.4142 | 17.4572 | 17.1719 | 16.3265 | 14.5251 | 38.3903 | 17.4681 | 27.3868 | 18.3281 | 16.4644 | 18.2928 | 12.9209 | 15.8624 | 15.4949 | 15.3795 | 14.2744 | 14.4968 | 15.2441 |  |  |  | 26.344 | 101.7632 | 83.0608 | 52.8373 | 0.24337 | -0.037239 | 33.0966 |  |  | 10.9194 |  |  | 16.892 | 16.2974 | 20.0642 | 16.3613 | 15.7174 | 16.7498 | 99.2835 | 127.0172 | 81.6749 | 82.0904 | 59.8233 |  | 29.7034 | 66.6903 | 30.2857 | 54.5202 | 32.6661 | 96.3315 |  | 49.3058 |  |  | 13.8956 | 15.5852 | 36.5989 | [6 empty] | 40.9004 |  |  | 26.4792 |  |  | 14.389 | 33.7991 | 139.9568 | 8.6144 | 27.5395 | 93.1188 | 10.2646 | 27.4811 | 103.2354 | 17.7265 | 74.0011 | 10.5048 | 68.6671 | 11.6681 | 70.4243 | 10.052 | 28.6362 | 86.2766 | 18.272 | 31.2688 | 102.7128 | 10.8284 | 26.746 | 100.3436 | 11.3104 | 69.9112 | 16.5453 | 75.9493 | 12.3579 | 77.4508 | 0.69508 | 19.9183 | 0.74772 | 0.064763 | -37.9939 | 3.1232 | 155.85 | 49.55 | -0.97115 | -0.11533 | 0.25524 | -0.51722 | 0.4602 | 0.41499 | 0.78691 | -0.35967 | -0.53057 | -0.11112 | -1.824 | -1.2276 | -0.67991 | -0.27974
42810.4445 | 385 | 18.4344 | 18.5457 | 18.538 | 18.5328 | 17.8358 | 16.448 | 14.4963 | 16.6222 | 17.1172 | 17.2072 | 17.2073 | 16.7285 | 15.7338 | 14.3525 | 14.7997 | 14.8335 | 15.4124 | 13.2889 | 13.6999 | 14.9893 |  |  |  | 16.5322 | 15.9825 | 18.2889 | 101.6303 | 90.6489 | 118.4377 | 17.0665 | 16.2762 | 17.1296 | 16.7804 | 16.1545 | 17.5107 | 28.9385 | 114.644 |  | 55.2671 | 87.3319 | 87.9717 | 69.9272 |  | 6.8062 | 7.2029 | 6.5191 | 7.1689 | 7.4859 | 8.9622 | 36.2591 | 4.6626 | 6.825 | 4.6705 | 7.4413 | 8.291 | 41.7057 | 46.3895 | 42.5075 | 14.7424 |  |  | -0.49787 | 0.099971 | 0.23447 | -0.14062 | 0.16378 | 0.048824 | 0.42966 | -0.000164 | -0.34773 | -0.89623 | -0.19603 | -0.00060126 | -0.00059797 | 1.5432 | 15.7926 | 16.6697 | 17.2068 | 17.5291 | 17.4612 | 16.4111 | 14.7664 | 16.7876 | 17.1291 | 17.4185 | 17.4545 | 17.1653 | 16.3358 | 14.5291 | 37.6559 | 17.0103 | 26.592 | 18.2562 | 16.2136 | 18.4019 | 12.9727 | 15.8672 | 15.4938 | 15.3795 | 14.2726 | 14.5038 | 15.2543 |  |  |  | 26.4512 | 102.0908 | 83.308 | 52.7769 | 0.20994 | -0.082407 | 33.1336 |  |  | 10.9246 |  |  | 16.8886 | 16.2987 | 20.0874 | 16.3531 | 15.7103 | 16.7536 | 99.5096 | 127.1417 | 81.9043 | 82.2587 | 60.2071 |  | 29.8027 | 66.9484 | 30.4048 | 54.9319 | 32.8468 | 96.8866 |  | 49.4873 |  |  | 13.89 | 15.5808 | 36.3822 | [6 empty] | 40.6071 |  |  | 26.5568 |  |  | 14.3914 | 34.0404 | 140.1031 | 8.5899 | 27.7696 | 93.2358 | 10.2679 | 27.5739 | 103.4527 | 17.7282 | 74.141 | 10.5179 | 68.8955 | 11.6691 | 70.8708 | 10.0397 | 28.859 | 86.4066 | 18.338 | 31.4385 | 102.8573 | 10.8134 | 26.9469 | 100.5233 | 11.3122 | 70.1721 | 16.5524 | 76.1666 | 12.3734 | 77.8253 | 0.74516 | 19.9136 | 0.75546 | 0.066818 | -37.9905 | 3.1232 | 131.46 | 48.92 | -0.97306 | 0.36894 | 0.56502 | -0.43757 | 0.47371 | 0.25864 | 0.76725 | -0.36694 | -0.53367 | -0.11637 | -1.7297 | -1.1332 | -0.66638 | -0.27444
42810.4445 | 386 | 18.4405 | 18.5489 | 18.5385 | 18.5338 | 17.8358 | 16.445 | 14.4934 | 16.6231 | 17.1166 | 17.2148 | 17.215 | 16.7248 | 15.7422 | 14.3538 | 14.8002 | 14.8337 | 15.4131 | 13.2916 | 13.6927 | 14.995 |  |  |  | 16.5245 | 15.979 | 18.3028 | 101.9658 | 90.8312 | 118.6586 | 17.0643 | 16.2717 | 17.1439 | 16.7786 | 16.1527 | 17.5261 | 29.0726 | 115.1142 |  | 55.4723 | 87.6159 | 88.1716 | 69.9891 |  | 6.8173 | 7.2113 | 6.5243 | 7.1843 | 7.5048 | 9.0141 | 36.5631 | 4.7178 | 6.8267 | 4.6245 | 7.4488 | 8.293 | 41.7025 | 46.4083 | 42.4988 | 14.7444 |  |  | -0.58724 | 0.12691 | 0.21147 | -0.18136 | 0.084276 | -0.22388 | 0.41388 | -0.020536 | -0.70035 | -0.16927 | -0.091311 | -0.00057169 | -0.00061112 | 1.5723 | 15.805 | 16.6709 | 17.2112 | 17.5326 | 17.4735 | 16.4257 | 14.762 | 16.7937 | 17.1255 | 17.4198 | 17.4575 | 17.1726 | 16.3282 | 14.5334 | 35.6882 | 16.3686 | 25.041 | 18.1605 | 16.4909 | 18.4805 | 13.0148 | 15.8497 | 15.4838 | 15.3631 | 14.2744 | 14.4946 | 15.25 |  |  |  | 26.5581 | 102.4427 | 83.4457 | 52.6221 | -0.030949 | -0.10424 | 33.0755 |  |  | 10.9194 |  |  | 16.8803 | 16.2978 | 20.1035 | 16.3462 | 15.7096 | 16.7625 | 99.6925 | 127.0621 | 82.2163 | 82.5702 | 60.1058 |  | 29.9156 | 68.041 | 30.5492 | 56.6625 | 33.0541 | 97.6986 |  | 49.6498 |  |  | 13.8783 | 15.567 | 36.5516 | [6 empty] | 40.2656 |  |  | 26.6388 |  |  | 14.4059 | 34.1308 | 140.6343 | 8.5621 | 27.963 | 93.4432 | 10.2787 | 27.8193 | 103.6419 | 17.7275 | 74.3133 | 10.5134 | 69.2003 | 11.6751 | 71.206 | 10.0356 | 29.3902 | 86.5231 | 18.3812 | 31.5226 | 102.9936 | 10.8096 | 27.3393 | 100.6077 | 11.3095 | 70.3937 | 16.568 | 76.311 | 12.3927 | 78.1625 | 0.7908 | 19.9062 | 0.7617 | 0.06705 | -38.1184 | 3.1232 | 138 | 49.95 | -1.0571 | 0.4157 | 0.5366 | -0.49693 | 0.33984 | -0.55389 | 0.75311 | -0.36028 | -0.55909 | -0.15733 | -1.5018 | -0.956 | -0.66354 | -0.26652
42810.4445 | 387 | 18.4278 | 18.5447 | 18.5359 | 18.5273 | 17.8404 | 16.435 | 14.4974 | 16.62 | 17.1102 | 17.2054 | 17.2068 | 16.7204 | 15.7325 | 14.3474 | 14.7984 | 14.8392 | 15.4237 | 13.288 | 13.6994 | 15.0113 |  |  |  | 16.5261 | 15.9851 | 18.3257 | 102.3198 | 91.0362 | 119.0812 | 17.0611 | 16.2768 | 17.1456 | 16.7745 | 16.1514 | 17.533 | 29.2303 | 115.8027 |  | 55.7091 | 87.9414 | 88.3597 | 73.1992 |  | 6.8297 | 7.2249 | 6.5343 | 7.2096 | 7.5171 | 9.0944 | 37.2497 | 4.7644 | 6.8326 | 4.5942 | 7.4596 | 8.2985 | 41.6931 | 46.4162 | 42.4721 | 14.74 |  |  | -0.15552 | -0.077453 | 0.078076 | -0.035486 | 0.036304 | -0.24162 | 0.5913 | 0.17529 | 0.68695 | -0.94595 | -0.24848 | -0.00056019 | -0.00056183 | 1.6296 | 15.813 | 16.6759 | 17.214 | 17.5406 | 17.4855 | 16.427 | 14.7691 | 16.7968 | 17.1424 | 17.4277 | 17.4651 | 17.1793 | 16.3338 | 14.5316 | 32.5927 | 15.4364 | 23.0914 | 17.2755 | 15.8807 | 18.5217 | 13.0551 | 15.855 | 15.4907 | 15.3768 | 14.2802 | 14.5023 | 15.2624 |  |  |  | 26.6697 | 102.883 | 83.8517 | 52.2329 | 0.12526 | -0.22393 | 33.1467 |  |  | 10.9195 |  |  | 16.883 | 16.2995 | 20.1279 | 16.3467 | 15.7071 | 16.7847 | 99.949 | 127.0011 | 82.478 | 82.8546 | 60.8461 |  | 30.0695 | 69.2902 | 30.6943 | 58.3177 | 33.2836 | 98.5224 |  | 49.8202 |  |  | 13.8578 | 15.5511 | 36.6582 | [6 empty] | 39.9104 |  |  | 26.6754 |  |  | 14.4166 | 34.3134 | 141.2259 | 8.5465 | 28.0736 | 93.6271 | 10.2896 | 28.0195 | 103.9774 | 17.7419 | 74.4542 | 10.5001 | 69.4991 | 11.6918 | 71.4406 | 10.0298 | 29.671 | 86.698 | 18.4279 | 31.5251 | 103.2071 | 10.8067 | 27.6821 | 100.901 | 11.3181 | 70.6446 | 16.5887 | 76.4372 | 12.4045 | 78.4119 | 0.75016 | 19.8953 | 0.77331 | 0.066485 | -38.1265 | 3.1232 | 146.34 | 49.38 | -0.54429 | -0.32475 | 0.32606 | -0.21982 | 0.22308 | -0.5755 | 0.9003 | -0.3756 | -0.58884 | -0.19544 | -1.1531 | -0.73469 | -0.74734 | -0.25192
42810.4445 | 388 | 18.4333 | 18.5472 | 18.5372 | 18.5219 | 17.8395 | 16.4477 | 14.4965 | 16.6197 | 17.1124 | 17.2058 | 17.2075 | 16.7276 | 15.7378 | 14.3486 | 14.7895 | 14.8351 | 15.4052 | 13.2816 | 13.6953 | 15.0105 |  |  |  | 16.5129 | 15.9718 | 18.3311 | 102.5907 | 91.3023 | 118.305 | 17.0676 | 16.2868 | 17.1593 | 16.7814 | 16.1552 | 17.5498 | 29.4174 | 116.08 |  | 55.9448 | 88.2726 | 88.5091 | 75.733 |  | 6.8295 | 7.2238 | 6.5463 | 7.2155 | 7.529 | 9.1452 | 37.9131 | 4.784 | 6.8377 | 4.5798 | 7.4598 | 8.3023 | 41.6529 | 46.4334 | 42.4508 | 14.726 |  |  | -0.42888 | 0.1762 | -0.002092 | 0.065054 | -0.009036 | -0.0642 | 0.60313 | 0.22391 | -0.29714 | 0.47628 | -0.3073 | -0.00058976 | -0.00061112 | 1.6013 | 15.7969 | 16.6653 | 17.207 | 17.5267 | 17.4726 | 16.4212 | 14.7602 | 16.7863 | 17.1235 | 17.4146 | 17.4562 | 17.163 | 16.3259 | 14.5275 | 31.2978 | 15.0448 | 21.6297 | 16.7366 | 15.492 | 18.5917 | 13.0783 | 15.8637 | 15.4952 | 15.377 | 14.2769 | 14.5036 | 15.2748 |  |  |  | 26.7711 | 103.1881 | 83.9392 | 51.8109 | 0.28085 | -0.21885 | 33.0791 |  |  | 10.9222 |  |  | 16.8859 | 16.2987 | 20.1495 | 16.3444 | 15.706 | 16.7874 | 100.3059 | 127.1965 | 82.5901 | 83.0435 | 61.4568 |  | 30.2093 | 70.1234 | 30.8096 | 57.9594 | 33.4524 | 97.858 |  | 49.9697 |  |  | 13.8535 | 15.5524 | 37.0574 | [6 empty] | 39.4613 |  |  | 26.7246 |  |  | 14.4418 | 34.5478 | 141.5664 | 8.54 | 28.2435 | 93.8742 | 10.3042 | 28.1865 | 104.2062 | 17.755 | 74.943 | 10.5051 | 69.7111 | 11.7224 | 71.6553 | 10.042 | 29.6756 | 86.915 | 18.4863 | 31.6647 | 103.5549 | 10.8045 | 27.7303 | 101.1783 | 11.3484 | 70.9404 | 16.6115 | 76.6896 | 12.4118 | 78.8012 | 0.70259 | 19.8866 | 0.77913 | 0.070618 | -38.0502 | 3.1232 | 163.57 | 48.4 | -0.90297 | 0.48982 | -0.053372 | 0.29763 | -0.1113 | -0.29668 | 0.90934 | -0.3878 | -0.60805 | -0.17969 | -1.001 | -0.5696 | -0.81135 | -0.23676
42810.4445 | 389 | 18.4288 | 18.5396 | 18.5268 | 18.5255 | 17.8287 | 16.4405 | 14.4969 | 16.6207 | 17.1141 | 17.2005 | 17.2054 | 16.7199 | 15.7299 | 14.3424 | 14.7948 | 14.8237 | 15.406 | 13.2689 | 13.6911 | 15.0095 |  |  |  | 16.5121 | 15.9756 | 18.3474 | 102.5967 | 91.5592 | 116.0491 | 17.0703 | 16.2854 | 17.1735 | 16.7826 | 16.1641 | 17.5685 | 29.5995 | 116.4992 |  | 56.165 | 88.6042 | 88.6198 | 77.3724 |  | 6.8355 | 7.2189 | 6.5585 | 7.2404 | 7.5416 | 9.2205 | 38.4791 | 4.8903 | 6.839 | 4.612 | 7.4737 | 8.3159 | 41.6149 | 46.4422 | 42.433 | 14.726 |  |  | -0.51233 | 0.088799 | 0.058364 | -0.14194 | 0.2111 | -0.17262 | 0.52099 | 0.16609 | -0.27145 | -0.49194 | -0.17059 | -0.00058647 | -0.00060783 | 1.6155 | 15.8054 | 16.673 | 17.2075 | 17.5256 | 17.4746 | 16.4219 | 14.7597 | 16.7926 | 17.1297 | 17.422 | 17.4618 | 17.1681 | 16.336 | 14.5367 | 31.4772 | 15.077 | 20.9892 | 16.3063 | 15.2008 | 18.6785 | 13.1101 | 15.8593 | 15.496 | 15.3778 | 14.2796 | 14.5108 | 15.2852 |  |  |  | 26.8665 | 103.3262 | 83.947 | 51.8102 | 0.41031 | -0.04025 | 32.9776 |  |  | 10.9296 |  |  | 16.8874 | 16.3101 | 20.18 | 16.3434 | 15.7104 | 16.8029 | 100.6722 | 127.4501 | 82.7745 | 83.2332 | 61.2342 |  | 30.33 | 70.817 | 30.9189 | 57.3322 | 33.6154 | 96.9732 |  | 50.1041 |  |  | 13.8537 | 15.5397 | 37.1466 | [6 empty] | 38.8741 |  |  | 26.6722 |  |  | 14.4597 | 34.7779 | 142.076 | 8.5448 | 28.8054 | 94.0753 | 10.3288 | 28.445 | 104.4139 | 17.7798 | 75.4352 | 10.521 | 69.9396 | 11.7358 | 72.192 | 10.0537 | 29.6808 | 87.1032 | 18.5252 | 31.867 | 103.8489 | 10.8142 | 27.7796 | 101.5537 | 11.3571 | 71.1816 | 16.6214 | 76.9217 | 12.4272 | 79.1306 | 0.66138 | 19.8777 | 0.78767 | 0.068114 | -38.0654 | 3.1232 | 142.07 | 50.34 | -0.98408 | 0.34772 | 0.28191 | -0.43962 | 0.53805 | -0.48655 | 0.84526 | -0.3775 | -0.62358 | -0.15668 | -1.0108 | -0.49472 | -0.85068 | -0.23351
42810.4445 | 390 | 18.4261 | 18.5409 | 18.5355 | 18.5381 | 17.8308 | 16.4405 | 14.4925 | 16.6252 | 17.1198 | 17.2131 | 17.2061 | 16.7277 | 15.736 | 14.348 | 14.7939 | 14.835 | 15.4122 | 13.2842 | 13.6996 | 15.0188 |  |  |  | 16.5133 | 15.9826 | 18.3665 | 102.9006 | 91.8708 | 118.3088 | 17.0618 | 16.2758 | 17.1878 | 16.7729 | 16.1511 | 17.5778 | 29.7653 | 116.6158 |  | 56.3742 | 88.9011 | 88.7262 | 78.3586 |  | 6.8321 | 7.2219 | 6.5557 | 7.2479 | 7.5515 | 9.2532 | 38.5916 | 5.0471 | 6.8449 | 4.6242 | 7.476 | 8.3254 | 41.5942 | 46.448 | 42.4049 | 14.72 |  |  | -0.3244 | 0.11968 | 0.1681 | -0.024314 | -0.19828 | -0.12597 | 0.56174 | 0.010352 | 0.036211 | -0.18438 | -0.261 | -0.00057169 | -0.00061112 | 1.6771 | 15.799 | 16.6604 | 17.2054 | 17.524 | 17.4805 | 16.4165 | 14.7588 | 16.7881 | 17.1323 | 17.4157 | 17.4591 | 17.1692 | 16.3319 | 14.5224 | 32.6016 | 15.0969 | 20.7932 | 16.6765 | 15.2029 | 18.7824 | 13.1388 | 15.8517 | 15.4901 | 15.3797 | 14.2796 | 14.5041 | 15.2827 |  |  |  | 26.9663 | 103.4417 | 83.9787 | 52.2164 | 0.53978 | -0.065092 | 32.966 |  |  | 10.9308 |  |  | 16.8874 | 16.3054 | 20.2021 | 16.343 | 15.7109 | 16.8166 | 100.9904 | 127.4596 | 82.9014 | 83.3674 | 60.942 |  | 30.4884 | 70.9963 | 31.0652 | 56.7781 | 33.856 | 95.5924 |  | 50.3014 |  |  | 13.8693 | 15.5577 | 36.9314 | [6 empty] | 38.7669 |  |  | 26.7657 |  |  | 14.468 | 34.9332 | 142.494 | 8.5499 | 29.3723 | 94.3371 | 10.3213 | 28.9521 | 104.7485 | 17.7925 | 75.5909 | 10.5232 | 70.1569 | 11.7566 | 72.6958 | 10.0538 | 29.6426 | 87.4203 | 18.5344 | 32.099 | 104.0977 | 10.8145 | 28.0738 | 101.7248 | 11.3518 | 71.4483 | 16.6303 | 77.1473 | 12.4273 | 79.3733 | 0.62324 | 19.8687 | 0.79822 | 0.070299 | -38.105 | 3.1233 | 157.66 | 49 | -0.78532 | 0.40369 | 0.47843 | -0.18195 | -0.52149 | -0.41565 | 0.87774 | -0.36397 | -0.62356 | -0.13303 | -1.1236 | -0.46961 | -0.87243 | -0.24141
42810.4446 | 391 | 18.422 | 18.5373 | 18.5277 | 18.5262 | 17.8254 | 16.4344 | 14.4874 | 16.6206 | 17.1099 | 17.2092 | 17.2059 | 16.7228 | 15.7297 | 14.3507 | 14.7919 | 14.8452 | 15.4063 | 13.2943 | 13.7125 | 15.0304 |  |  |  | 16.5244 | 15.9873 | 18.3845 | 103.1997 | 92.1417 | 117.7917 | 17.0596 | 16.2801 | 17.1882 | 16.7773 | 16.1508 | 17.5836 | 29.9338 | 116.4562 |  | 56.5872 | 89.1199 | 88.8559 | 79.4713 |  | 6.8339 | 7.2347 | 6.556 | 7.2472 | 7.5562 | 9.33 | 39.5817 | 5.1576 | 6.8519 | 4.6358 | 7.4832 | 8.3241 | 41.5704 | 46.4362 | 42.3786 | 14.7108 |  |  | -0.23109 | 0.074343 | 0.19044 | 0.12617 | -0.14177 | 0.082336 | 0.44148 | 0.11352 | -1.6856 | 0.064446 | -0.1994 | -0.00057333 | -0.00060455 | 1.6131 | 15.7906 | 16.6578 | 17.1992 | 17.5193 | 17.4647 | 16.415 | 14.752 | 16.7809 | 17.1223 | 17.4155 | 17.4517 | 17.1645 | 16.3304 | 14.5131 | 34.7241 | 16.5663 | 21.3969 | 16.7571 | 15.3927 | 18.9228 | 13.1679 | 15.8551 | 15.4855 | 15.3735 | 14.2711 | 14.5151 | 15.2944 |  |  |  | 27.0804 | 103.5116 | 83.9704 | 52.6408 | 0.46036 | 0.013011 | 32.8828 |  |  | 10.9287 |  |  | 16.8903 | 16.3102 | 20.2333 | 16.3426 | 15.7197 | 16.8242 | 101.4194 | 127.6771 | 83.0235 | 83.5132 | 60.3826 |  | 30.6209 | 71.3743 | 31.1723 | 56.2225 | 34.0355 | 94.9798 |  | 50.4852 |  |  | 13.8906 | 15.5869 | 37.1591 | [6 empty] | 38.7543 |  |  | 26.8815 |  |  | 14.4801 | 34.8652 | 142.5004 | 8.5579 | 29.2191 | 94.5691 | 10.3337 | 28.9815 | 104.9907 | 17.8168 | 75.7424 | 10.5255 | 70.3615 | 11.7588 | 72.9527 | 10.0482 | 29.6882 | 87.6043 | 18.5663 | 32.2531 | 104.4707 | 10.8178 | 28.3112 | 101.9857 | 11.3498 | 71.712 | 16.6495 | 77.3401 | 12.4305 | 79.5228 | 0.75286 | 19.8576 | 0.80645 | 0.070227 | -38.0927 | 3.1232 | 160.96 | 49.06 | -0.66238 | 0.31817 | 0.50925 | 0.41449 | -0.44102 | 0.33609 | 0.77825 | -0.34391 | -0.63041 | -0.11143 | -1.3431 | -0.53329 | -0.8976 | -0.24933
42810.4446 | 392 | 18.4213 | 18.5411 | 18.5353 | 18.5257 | 17.8262 | 16.4328 | 14.4935 | 16.6181 | 17.118 | 17.2088 | 17.2105 | 16.7242 | 15.7296 | 14.3507 | 14.7901 | 14.8303 | 15.4086 | 13.2807 | 13.7073 | 15.0426 |  |  |  | 16.5266 | 15.9851 | 18.3974 | 103.3742 | 92.4182 | 117.3768 | 17.0594 | 16.2791 | 17.2034 | 16.776 | 16.1595 | 17.6059 | 30.109 | 117.0179 |  | 56.8013 | 89.3156 | 89.0264 | 79.7375 |  | 6.8249 | 7.2298 | 6.5628 | 7.2467 | 7.5912 | 9.4118 | 40.1527 | 5.1546 | 6.8527 | 4.6439 | 7.4855 | 8.3263 | 41.5456 | 46.4258 | 42.3472 | 14.7035 |  |  | -0.58724 | 0.036887 | -0.019176 | -0.017742 | 0.12567 | -0.08654 | 0.53019 | 0.083948 | 0.11444 | 0.038011 | -0.1549 | -0.00057169 | -0.00055855 | 1.5584 | 15.7979 | 16.658 | 17.204 | 17.5259 | 17.4686 | 16.4184 | 14.7533 | 16.7901 | 17.1241 | 17.4225 | 17.4547 | 17.1688 | 16.3354 | 14.519 | 35.6702 | 17.6691 | 22.3717 | 16.7714 | 15.3759 | 19.0375 | 13.2144 | 15.848 | 15.48 | 15.3675 | 14.2691 | 14.4982 | 15.2952 |  |  |  | 27.1891 | 103.612 | 84.0338 | 52.9419 | 0.36351 | 0.072482 | 32.9543 |  |  | 10.9456 |  |  | 16.8935 | 16.3191 | 20.2592 | 16.3534 | 15.719 | 16.8442 | 101.7119 | 127.6865 | 83.196 | 83.6915 | 60.3775 |  | 30.7571 | 71.6976 | 31.2983 | 56.3224 | 34.224 | 95.0482 |  | 50.6637 |  |  | 13.8787 | 15.6209 | 37.0327 | [6 empty] | 38.8046 |  |  | 27.0336 |  |  | 14.4985 | 34.8823 | 142.8391 | 8.5457 | 29.4232 | 94.6172 | 10.3386 | 29.1452 | 105.2457 | 17.8495 | 75.9704 | 10.5329 | 70.5197 | 11.7694 | 73.1521 | 10.0478 | 29.6373 | 87.9696 | 18.5945 | 32.393 | 104.8119 | 10.816 | 28.4436 | 102.3481 | 11.3488 | 71.9475 | 16.6623 | 77.4151 | 12.4369 | 79.6709 | 0.57374 | 19.8477 | 0.81628 | 0.071407 | -38.0897 | 3.1233 | 156.69 | 50.35 | -1.0554 | 0.22412 | -0.16159 | -0.15543 | 0.41528 | -0.34461 | 0.85298 | -0.33912 | -0.63508 | -0.10773 | -1.4348 | -0.63618 | -0.89901 | -0.254
42810.4446 | 393 | 18.4151 | 18.5382 | 18.5305 | 18.5272 | 17.8275 | 16.4309 | 14.489 | 16.6193 | 17.1165 | 17.2057 | 17.2041 | 16.7207 | 15.7306 | 14.3452 | 14.7825 | 14.8293 | 15.4087 | 13.2828 | 13.708 | 15.0425 |  |  |  | 16.5255 | 15.9859 | 18.4169 | 103.554 | 92.7177 | 117.1977 | 17.0516 | 16.2718 | 17.2049 | 16.7744 | 16.1557 | 17.6141 | 30.301 | 117.1734 |  | 57.0139 | 89.4715 | 89.1926 | 80.0189 |  | 6.8234 | 7.2362 | 6.562 | 7.254 | 7.6338 | 9.4704 | 40.1154 | 5.1161 | 6.8572 | 4.6475 | 7.4952 | 8.3458 | 41.5277 | 46.4317 | 42.3228 | 14.7057 |  |  | -0.24554 | -0.17931 | 0.15167 | 0.12551 | -0.06752 | -0.003088 | 0.41126 | 0.26071 | -0.087555 | -0.049056 | -0.17914 | -0.0005799 | -0.0005914 | 1.6271 | 15.8026 | 16.6687 | 17.2055 | 17.5292 | 17.4708 | 16.4159 | 14.7603 | 16.7845 | 17.1285 | 17.4239 | 17.4638 | 17.1697 | 16.3413 | 14.5233 | 35.3121 | 17.7691 | 23.2211 | 17.0636 | 15.3645 | 19.1159 | 13.2749 | 15.8541 | 15.4828 | 15.3674 | 14.2725 | 14.5124 | 15.3035 |  |  |  | 27.2946 | 103.7284 | 84.0929 | 53.1358 | 0.41031 | -0.014278 | 33.2729 |  |  | 10.9449 |  |  | 16.8869 | 16.3147 | 20.2781 | 16.3432 | 15.713 | 16.8481 | 101.9381 | 127.5482 | 83.4577 | 83.9585 | 61.1067 |  | 30.9028 | 72.2382 | 31.4432 | 56.9912 | 34.4185 | 95.2856 |  | 50.833 |  |  | 13.8842 | 15.6397 | 36.8448 | [6 empty] | 39.0523 |  |  | 27.1833 |  |  | 14.5138 | 35.0976 | 143.1555 | 8.5362 | 29.9009 | 94.7518 | 10.3496 | 29.5189 | 105.6173 | 17.888 | 76.3002 | 10.5382 | 70.7417 | 11.7732 | 73.3552 | 10.0234 | 29.6576 | 88.2355 | 18.6436 | 32.5102 | 105.0641 | 10.8107 | 28.5443 | 102.689 | 11.3524 | 72.2164 | 16.6593 | 77.5123 | 12.438 | 79.8372 | 0.74651 | 19.8387 | 0.82573 | 0.070791 | -38.0991 | 3.1232 | 163.58 | 49.02 | -0.68227 | -0.49413 | 0.45446 | 0.41341 | -0.30443 | -0.065104 | 0.75132 | -0.3544 | -0.64515 | -0.11962 | -1.3859 | -0.72352 | -0.90028 | -0.25581
42810.4446 | 394 | 18.4148 | 18.5434 | 18.5278 | 18.5211 | 17.829 | 16.4323 | 14.4872 | 16.6175 | 17.111 | 17.2005 | 17.1984 | 16.7214 | 15.7351 | 14.3483 | 14.7863 | 14.8301 | 15.4165 | 13.2831 | 13.7084 | 15.0528 |  |  |  | 16.5281 | 15.9878 | 18.4365 | 103.5719 | 92.995 | 115.9998 | 17.0566 | 16.2736 | 17.2206 | 16.7767 | 16.1573 | 17.628 | 30.492 | 117.2967 |  | 57.2288 | 89.7155 | 89.4218 | 79.9451 |  | 6.8128 | 7.2366 | 6.5599 | 7.2549 | 7.6402 | 9.5189 | 40.1364 | 5.0544 | 6.8612 | 4.7697 | 7.4989 | 8.3533 | 41.5088 | 46.4228 | 42.2945 | 14.6933 |  |  | -0.30994 | 0.15911 | 0.02748 | -0.028914 | -0.04452 | -0.18511 | 0.55582 | -0.12764 | -0.41818 | 0.33383 | -0.15231 | -0.00058483 | -0.0006029 | 1.6747 | 15.7963 | 16.6633 | 17.2012 | 17.5246 | 17.4739 | 16.4206 | 14.7635 | 16.7888 | 17.1294 | 17.4211 | 17.4606 | 17.1652 | 16.3245 | 14.5216 | 35.3862 | 17.4069 | 23.6204 | 17.9955 | 15.4314 | 19.2136 | 13.3289 | 15.8626 | 15.4872 | 15.3752 | 14.2726 | 14.5226 | 15.3218 |  |  |  | 27.4023 | 103.9271 | 84.1753 | 53.2705 | 0.46704 | -0.081842 | 33.5522 |  |  | 10.9555 |  |  | 16.8949 | 16.3186 | 20.3084 | 16.3456 | 15.7143 | 16.8618 | 102.2143 | 127.9598 | 83.705 | 84.2516 | 60.3496 |  | 31.045 | 72.6602 | 31.579 | 57.1681 | 34.5989 | 95.2103 |  | 50.9722 |  |  | 13.8788 | 15.6582 | 36.7902 | [6 empty] | 38.868 |  |  | 27.3277 |  |  | 14.5492 | 35.5098 | 143.4909 | 8.5663 | 30.0763 | 95.1163 | 10.3766 | 29.8011 | 105.8999 | 17.9274 | 76.9429 | 10.5436 | 71.0788 | 11.7959 | 73.5694 | 9.9983 | 29.9307 | 88.4752 | 18.6798 | 32.6411 | 105.1344 | 10.818 | 28.7349 | 102.9865 | 11.3688 | 72.5378 | 16.6757 | 77.6242 | 12.4597 | 80.0889 | 0.73187 | 19.8287 | 0.83426 | 0.071168 | -38.0802 | 3.1232 | 163.65 | 49.57 | -0.76536 | 0.46547 | 0.19344 | -0.19843 | -0.24722 | -0.5041 | 0.87352 | -0.32851 | -0.65223 | -0.11833 | -1.3827 | -0.7616 | -0.89171 | -0.2559
42810.4446 | 395 | 18.4096 | 18.5429 | 18.5288 | 18.5212 | 17.8206 | 16.4317 | 14.4837 | 16.6211 | 17.113 | 17.1995 | 17.2035 | 16.7181 | 15.7314 | 14.3461 | 14.7904 | 14.8334 | 15.4093 | 13.2773 | 13.7102 | 15.0673 |  |  |  | 16.5216 | 15.9877 | 18.4505 | 103.6251 | 93.2271 | 115.5112 | 17.0538 | 16.2796 | 17.2333 | 16.7721 | 16.1591 | 17.6358 | 30.6994 | 117.171 |  | 57.3902 | 90.0518 | 89.6893 | 80.1336 |  | 6.813 | 7.2354 | 6.5575 | 7.2655 | 7.6685 | 9.5662 | 40.6525 | 5.0571 | 6.8655 | 4.876 | 7.513 | 8.3418 | 41.479 | 46.4035 | 42.2677 | 14.6882 |  |  | -0.37499 | -0.21545 | -0.012608 | 0.030886 | 0.070476 | -0.15882 | 0.61496 | 0.11812 | -0.30667 | -0.56726 | 0.067053 | -0.00056348 | -0.00064561 | 1.627 | 15.8009 | 16.6672 | 17.1949 | 17.5276 | 17.4752 | 16.4093 | 14.7613 | 16.7878 | 17.1285 | 17.416 | 17.4572 | 17.1689 | 16.3316 | 14.5203 | 36.6992 | 17.0295 | 24.1729 | 18.3738 | 15.9021 | 19.3511 | 13.3832 | 15.849 | 15.4896 | 15.3727 | 14.2573 | 14.5127 | 15.3149 |  |  |  | 27.5016 | 104.1133 | 84.426 | 53.6327 | 0.4249 | 0.018657 | 33.7221 |  |  | 10.9553 |  |  | 16.8845 | 16.3142 | 20.3279 | 16.3406 | 15.7189 | 16.8681 | 102.5688 | 128.5826 | 83.8962 | 84.5354 | 59.3047 |  | 31.1662 | 72.6511 | 31.7114 | 57.5349 | 34.8132 | 95.7877 |  | 51.1182 |  |  | 13.8541 | 15.672 | 36.732 | [6 empty] | 39.7664 |  |  | 27.3848 |  |  | 14.5722 | 35.6816 | 144.0713 | 8.601 | 29.9987 | 95.5093 | 10.3842 | 29.938 | 106.1064 | 17.9666 | 77.1933 | 10.5418 | 71.2839 | 11.8083 | 73.7937 | 9.9859 | 30.283 | 88.7429 | 18.7175 | 32.7734 | 105.2291 | 10.8222 | 28.8722 | 103.3482 | 11.3799 | 72.8448 | 16.7048 | 77.9125 | 12.4731 | 80.382 | 0.6346 | 19.8198 | 0.84347 | 0.070864 | -38.0346 | 3.1233 | 159.23 | 49.5 | -0.84133 | -0.54164 | -0.13103 | 0.20508 | 0.31107 | -0.46698 | 0.91889 | -0.29535 | -0.64744 | -0.12115 | -1.5125 | -0.81666 | -0.88987 | -0.26259
42810.4446 | 396 | 18.4154 | 18.5456 | 18.5373 | 18.5268 | 17.8337 | 16.4377 | 14.4932 | 16.629 | 17.1196 | 17.2057 | 17.2058 | 16.7259 | 15.729 | 14.3476 | 14.7835 | 14.8261 | 15.4099 | 13.2741 | 13.714 | 15.0745 |  |  |  | 16.5212 | 15.9874 | 18.4682 | 103.676 | 93.4135 | 114.8223 | 17.0511 | 16.2793 | 17.2418 | 16.7691 | 16.1574 | 17.6527 | 30.9073 | 116.9685 |  | 57.5672 | 90.3893 | 89.8871 | 79.7713 |  | 6.8161 | 7.2395 | 6.5731 | 7.2875 | 7.6642 | 9.6242 | 41.5055 | 5.1239 | 6.8771 | 4.886 | 7.5291 | 8.3436 | 41.4504 | 46.3857 | 42.2388 | 14.6828 |  |  | -0.29482 | 0.084199 | 0.091876 | -0.060454 | 0.1007 | -0.40853 | 0.68922 | 0.2088 | 0.26506 | -0.10696 | -0.1386 | -0.00057662 | -0.00059962 | 1.5833 | 15.7982 | 16.6649 | 17.1978 | 17.5249 | 17.4769 | 16.4128 | 14.7625 | 16.7933 | 17.13 | 17.4257 | 17.4599 | 17.1698 | 16.3278 | 14.5252 | 37.8432 | 16.3101 | 23.3758 | 17.9569 | 15.8095 | 19.4683 | 13.4217 | 15.849 | 15.4878 | 15.3761 | 14.2691 | 14.5199 | 15.3316 |  |  |  | 27.6174 | 104.2389 | 84.7142 | 54.1645 | 0.23142 | -0.16503 | 33.8278 |  |  | 10.9627 |  |  | 16.8877 | 16.325 | 20.358 | 16.3466 | 15.7229 | 16.8856 | 103.0642 | 128.9602 | 84.0855 | 84.7419 | 59.5269 |  | 31.2921 | 71.9259 | 31.827 | 57.681 | 35.062 | 96.2592 |  | 51.264 |  |  | 13.8663 | 15.6827 | 36.8355 | [6 empty] | 41.0086 |  |  | 27.4191 |  |  | 14.5888 | 35.7167 | 144.7246 | 8.6115 | 30.2622 | 95.93 | 10.3709 | 30.1028 | 106.2909 | 18.0005 | 77.387 | 10.5476 | 71.433 | 11.8163 | 73.9944 | 9.9565 | 30.46 | 88.958 | 18.7577 | 32.9805 | 105.5562 | 10.8334 | 29.0287 | 103.7526 | 11.3767 | 73.0724 | 16.7354 | 78.0737 | 12.4746 | 80.7345 | 0.67139 | 19.8086 | 0.85224 | 0.070285 | -38.0674 | 3.1232 | 154.57 | 49.2 | -0.74533 | 0.33861 | 0.35371 | -0.28692 | 0.37189 | -0.74903 | 0.97289 | -0.29722 | -0.62335 | -0.11665 | -1.6259 | -0.72361 | -0.87271 | -0.27343
42810.4446 | 397 | 18.4175 | 18.5346 | 18.5351 | 18.529 | 17.8317 | 16.4347 | 14.4956 | 16.6254 | 17.1101 | 17.2137 | 17.2015 | 16.7213 | 15.7278 | 14.3413 | 14.7877 | 14.8257 | 15.4129 | 13.278 | 13.7176 | 15.0713 |  |  |  | 16.5221 | 15.9935 | 18.4886 | 103.6819 | 93.5794 | 113.7752 | 17.0562 | 16.2872 | 17.2621 | 16.786 | 16.1597 | 17.6807 | 31.1013 | 116.8082 |  | 57.7732 | 90.6642 | 90.0335 | 80.6312 |  | 6.8143 | 7.2465 | 6.5701 | 7.3181 | 7.6951 | 9.6667 | 42.3443 | 5.1099 | 6.884 | 4.9048 | 7.531 | 8.3604 | 41.4206 | 46.3899 | 42.2225 | 14.6842 |  |  | -0.40457 | -0.16156 | 0.025508 | -0.009198 | -0.087232 | 0.38658 | 0.58474 | -0.11056 | -0.57658 | -0.64615 | -0.076409 | -0.00057169 | -0.00057662 | 1.5549 | 15.8009 | 16.6634 | 17.2069 | 17.5261 | 17.4716 | 16.4189 | 14.7625 | 16.7933 | 17.1282 | 17.4177 | 17.459 | 17.1684 | 16.3284 | 14.5298 | 37.1606 | 16.1493 | 21.9878 | 16.9124 | 15.18 | 19.5627 | 13.4614 | 15.8437 | 15.4872 | 15.376 | 14.2616 | 14.5205 | 15.3402 |  |  |  | 27.7344 | 104.3854 | 84.7996 | 54.5093 | 0.37952 | -0.022936 | 33.9187 |  |  | 10.9745 |  |  | 16.8864 | 16.3253 | 20.3956 | 16.3401 | 15.7247 | 16.8996 | 103.3877 | 129.1189 | 84.2267 | 84.887 | 61.1484 |  | 31.426 | 70.9719 | 31.9812 | 56.8889 | 35.3181 | 96.5728 |  | 51.4122 |  |  | 13.8507 | 15.7005 | 36.9652 | [6 empty] | 41.4031 |  |  | 27.4925 |  |  | 14.6124 | 35.7107 | 144.7503 | 8.633 | 30.5166 | 96.3251 | 10.3811 | 30.274 | 106.473 | 18.0372 | 77.6025 | 10.554 | 71.5868 | 11.8299 | 74.2302 | 9.9268 | 30.6018 | 89.1332 | 18.811 | 33.125 | 105.875 | 10.8283 | 29.0745 | 104.0922 | 11.3643 | 73.2208 | 16.7743 | 78.0777 | 12.4862 | 80.9525 | 0.59281 | 19.8003 | 0.86188 | 0.069293 | -38.0751 | 3.1232 | 141.86 | 49.95 | -0.87192 | -0.46905 | 0.18638 | -0.11192 | -0.34614 | 0.72868 | 0.89619 | -0.33768 | -0.59157 | -0.085828 | -1.5391 | -0.56477 | -0.88997 | -0.27904
42810.4446 | 398 | 18.407 | 18.539 | 18.5213 | 18.5147 | 17.8154 | 16.422 | 14.492 | 16.6164 | 17.1047 | 17.2057 | 17.204 | 16.7184 | 15.7251 | 14.3335 | 14.7864 | 14.8238 | 15.4069 | 13.2814 | 13.7167 | 15.0774 |  |  |  | 16.5179 | 15.9936 | 18.5053 | 103.7585 | 93.7481 | 114.3654 | 17.0547 | 16.2673 | 17.2574 | 16.7712 | 16.1531 | 17.6803 | 31.2954 | 116.9007 |  | 57.9844 | 90.8988 | 90.2141 | 81.7999 |  | 6.8111 | 7.245 | 6.5678 | 7.3597 | 7.7432 | 9.7119 | 42.5483 | 5.1014 | 6.8882 | 4.8831 | 7.5362 | 8.3599 | 41.3701 | 46.389 | 42.2037 | 14.6728 |  |  | -0.56227 | 0.063171 | 0.037992 | 0.14719 | 0.008708 | 0.13819 | 0.51245 | -0.058648 | -0.46177 | -1.3828 | -0.095881 | -0.00060783 | -0.0005914 | 1.6314 | 15.8028 | 16.6612 | 17.204 | 17.5229 | 17.4744 | 16.4214 | 14.7527 | 16.7927 | 17.1238 | 17.4181 | 17.453 | 17.1683 | 16.3306 | 14.523 | 37.5979 | 16.0212 | 21.6741 | 16.5 | 14.1426 | 19.6931 | 13.4948 | 15.8453 | 15.4893 | 15.3766 | 14.268 | 14.52 | 15.346 |  |  |  | 27.8582 | 104.486 | 84.8878 | 54.7457 | 0.55112 | -0.12099 | 34.0576 |  |  | 10.9736 |  |  | 16.8952 | 16.3386 | 20.4232 | 16.3497 | 15.7306 | 16.9188 | 103.5469 | 129.3301 | 84.3843 | 85.0456 | 61.9525 |  | 31.553 | 70.7964 | 32.1087 | 57.7823 | 35.5067 | 97.2043 |  | 51.5532 |  |  | 13.8097 | 15.7252 | 37.4225 | [6 empty] | 41.0393 |  |  | 27.5734 |  |  | 14.637 | 35.8963 | 144.9276 | 8.654 | 30.7974 | 96.5293 | 10.3791 | 30.5305 | 106.6951 | 18.0618 | 77.7885 | 10.5477 | 71.7641 | 11.8471 | 74.6199 | 9.9237 | 30.9785 | 89.3618 | 18.8609 | 33.273 | 105.9862 | 10.8144 | 29.1194 | 104.3744 | 11.3651 | 73.4038 | 16.7873 | 78.145 | 12.5062 | 81.2686 | 0.77944 | 19.7884 | 0.87131 | 0.069004 | -38.0178 | 3.1232 | 133.86 | 49.26 | -1.0287 | 0.2933 | 0.22746 | 0.44771 | 0.10937 | 0.43571 | 0.83904 | -0.35568 | -0.58233 | -0.10415 | -1.5724 | -0.52603 | -0.9158 | -0.2814
42810.4447 | 399 | 18.4062 | 18.5266 | 18.5256 | 18.5189 | 17.8184 | 16.4297 | 14.4818 | 16.6195 | 17.1156 | 17.2045 | 17.1969 | 16.7201 | 15.7273 | 14.3319 | 14.7801 | 14.829 | 15.4105 | 13.2795 | 13.7216 | 15.0903 |  |  |  | 16.5176 | 15.9916 | 18.5221 | 104.0089 | 93.9679 | 115.7653 | 17.0469 | 16.2765 | 17.2722 | 16.7695 | 16.1589 | 17.7003 | 31.4853 | 116.7192 |  | 58.1525 | 91.0556 | 90.5142 | 80.1042 |  | 6.8133 | 7.2426 | 6.576 | 7.3822 | 7.7607 | 9.779 | 42.5851 | 5.0813 | 6.9019 | 4.8697 | 7.5458 | 8.3682 | 41.3149 | 46.3959 | 42.1957 | 14.6773 |  |  | -0.62404 | -0.11031 | -0.05992 | -0.11434 | -0.043204 | 0.40958 | 0.49997 | 0.23968 | -0.20276 | -0.70195 | -0.084158 | -0.00057497 | -0.00057169 | 1.6185 | 15.8037 | 16.6612 | 17.2064 | 17.5185 | 17.4663 | 16.4177 | 14.7491 | 16.7882 | 17.1311 | 17.4192 | 17.4542 | 17.1641 | 16.3315 | 14.5129 | 38.4073 | 16.422 | 21.4419 | 16.0919 | 13.775 | 19.8217 | 13.536 | 15.8471 | 15.4836 | 15.3755 | 14.2663 | 14.5187 | 15.3495 |  |  |  | 27.9672 | 104.7512 | 85.0627 | 54.6966 | 0.1834 | -0.068292 | 34.2023 |  |  | 10.9712 |  |  | 16.894 | 16.3248 | 20.4383 | 16.3436 | 15.7219 | 16.9148 | 103.7295 | 129.6304 | 84.6541 | 85.2969 | 62.4023 |  | 31.6719 | 71.7524 | 32.2163 | 57.9494 | 35.6584 | 97.22 |  | 51.6915 |  |  | 13.8068 | 15.7497 | 37.7241 | [6 empty] | 40.8409 |  |  | 27.6335 |  |  | 14.66 | 36.1949 | 145.1962 | 8.6634 | 31.2014 | 96.6253 | 10.3662 | 30.7239 | 107.1265 | 18.0777 | 77.9412 | 10.5474 | 72.0093 | 11.8653 | 75.0361 | 9.9434 | 31.2534 | 89.5311 | 18.8869 | 33.5427 | 106.0732 | 10.7842 | 29.5321 | 104.6006 | 11.36 | 73.5726 | 16.7969 | 78.2296 | 12.5177 | 81.7737 | 0.73938 | 19.7792 | 0.87954 | 0.070712 | -38.0097 | 3.1233 | 147.63 | 49.17 | -1.0857 | -0.38757 | -0.28565 | -0.39459 | -0.24365 | 0.7502 | 0.82885 | -0.3641 | -0.6052 | -0.10356 | -1.6473 | -0.49541 | -0.86221 | -0.27633
42810.4447 | 400 | 18.4114 | 18.5372 | 18.5319 | 18.5221 | 17.8296 | 16.4416 | 14.4879 | 16.625 | 17.1179 | 17.21 | 17.2103 | 16.7212 | 15.7311 | 14.347 | 14.7713 | 14.8241 | 15.4044 | 13.2729 | 13.7131 | 15.0839 |  |  |  | 16.5154 | 15.9878 | 18.5349 | 104.2903 | 94.0382 | 116.0856 | 17.0506 | 16.2728 | 17.2836 | 16.7653 | 16.1598 | 17.714 | 31.6698 | 116.8529 |  | 58.3292 | 91.2465 | 90.8565 | 80.8432 |  | 6.8077 | 7.2572 | 6.5829 | 7.3892 | 7.7754 | 9.8348 | 42.6538 | 5.0564 | 6.902 | 4.8812 | 7.5612 | 8.366 | 41.2559 | 46.4011 | 42.1832 | 14.6668 |  |  | -0.43873 | -0.047881 | -0.2058 | -0.055198 | -0.08986 | -0.29945 | 0.47894 | -0.14407 | 0.043995 | -0.60251 | -0.14893 | -0.00057333 | -0.00061933 | 1.5152 | 15.8019 | 16.6705 | 17.2067 | 17.521 | 17.4716 | 16.4248 | 14.7558 | 16.7933 | 17.1337 | 17.4203 | 17.4602 | 17.1676 | 16.331 | 14.5264 | 37.2114 | 16.4655 | 21.3388 | 15.7185 | 13.8832 | 19.8982 | 13.5753 | 15.8548 | 15.4844 | 15.3714 | 14.2673 | 14.5244 | 15.3626 |  |  |  | 28.0743 | 105.0274 | 85.1107 | 54.598 | 0.071769 | -0.088053 | 34.2797 |  |  | 10.9759 |  |  | 16.8732 | 16.3165 | 20.4623 | 16.3443 | 15.7179 | 16.9216 | 103.9357 | 130.2029 | 84.9961 | 85.6006 | 62.6039 |  | 31.8001 | 72.5012 | 32.3779 | 58.3947 | 35.8861 | 96.9766 |  | 51.9216 |  |  | 13.8309 | 15.7721 | 37.812 | [6 empty] | 40.9322 |  |  | 27.711 |  |  | 14.6821 | 36.2355 | 144.9519 | 8.6733 | 31.2681 | 96.798 | 10.346 | 30.6773 | 107.477 | 18.0967 | 78.2986 | 10.535 | 72.2964 | 11.8752 | 75.5323 | 9.9443 | 31.561 | 89.7008 | 18.9349 | 33.6113 | 106.1945 | 10.762 | 29.8577 | 104.7417 | 11.3622 | 73.6834 | 16.8099 | 78.3766 | 12.5193 | 82.0379 | 0.60918 | 19.7709 | 0.89033 | 0.073911 | -38.0906 | 3.1233 | 148.58 | 50.46 | -0.9107 | -0.25535 | -0.5294 | -0.27417 | -0.35142 | -0.64152 | 0.81131 | -0.36532 | -0.62047 | -0.10808 | -1.5055 | -0.4794 | -0.87642 | -0.26996
42810.4447 | 401 | 18.4133 | 18.5363 | 18.5325 | 18.5223 | 17.8278 | 16.4328 | 14.4858 | 16.6206 | 17.1169 | 17.2041 | 17.2107 | 16.7194 | 15.7274 | 14.3374 | 14.7683 | 14.8199 | 15.3989 | 13.2712 | 13.7142 | 15.0827 |  |  |  | 16.5138 | 15.9942 | 18.551 | 104.5279 | 94.0164 | 117.506 | 17.0396 | 16.2722 | 17.2872 | 16.7606 | 16.1506 | 17.7204 | 31.8615 | 117.603 |  | 58.522 | 91.4394 | 91.161 | 81.1097 |  | 6.8157 | 7.2634 | 6.5783 | 7.3978 | 7.8028 | 9.8904 | 42.4531 | 5.0309 | 6.917 | 4.9081 | 7.5698 | 8.3704 | 41.2228 | 46.4109 | 42.1818 | 14.6736 |  |  | -0.38814 | -0.16353 | -0.016548 | -0.05651 | -0.00772 | 0.1901 | 0.61759 | 0.20354 | -1.1452 | -0.10214 | -0.24709 | -0.00059305 | -0.00062262 | 1.4839 | 15.807 | 16.6613 | 17.2034 | 17.5326 | 17.4757 | 16.4286 | 14.7595 | 16.7926 | 17.1319 | 17.4244 | 17.4581 | 17.1723 | 16.3347 | 14.5299 | 35.3393 | 16.331 | 21.3501 | 15.8283 | 13.6751 | 19.9604 | 13.6109 | 15.8511 | 15.4849 | 15.3757 | 14.2659 | 14.5215 | 15.377 |  |  |  | 28.2021 | 105.2814 | 85.2136 | 54.8649 | 0.23 | -0.12889 | 34.4984 |  |  | 10.981 |  |  | 16.8838 | 16.3373 | 20.4873 | 16.3373 | 15.7205 | 16.9449 | 104.0546 | 130.7022 | 85.3019 | 85.9108 | 62.8776 |  | 31.9123 | 73.4845 | 32.5222 | 57.4648 | 36.0763 | 97.4063 |  | 52.12 |  |  | 13.8635 | 15.7742 | 38.1068 | [6 empty] | 40.6022 |  |  | 27.7819 |  |  | 14.7254 | 36.2 | 144.693 | 8.6952 | 31.4838 | 97.1601 | 10.3383 | 30.788 | 107.7187 | 18.1305 | 78.5047 | 10.5224 | 72.5109 | 11.9002 | 76.0567 | 9.9266 | 31.8288 | 89.8309 | 18.9739 | 33.7334 | 106.4628 | 10.7443 | 29.8908 | 104.8417 | 11.3559 | 73.7604 | 16.8494 | 78.92 | 12.5393 | 82.2977 | 0.70124 | 19.7635 | 0.89831 | 0.073375 | -38.0394 | 3.1232 | 147.77 | 48.57 | -0.85814 | -0.47192 | -0.15012 | -0.27741 | -0.10301 | 0.5112 | 0.92138 | -0.36908 | -0.64284 | -0.075695 | -1.2903 | -0.4765 | -0.87727 | -0.27303
42810.4447 | 402 | 18.4081 | 18.5337 | 18.5266 | 18.5232 | 17.8213 | 16.4282 | 14.4846 | 16.6162 | 17.1099 | 17.2013 | 17.2037 | 16.7178 | 15.7332 | 14.338 | 14.7819 | 14.8139 | 15.3968 | 13.2753 | 13.7163 | 15.1089 |  |  |  | 16.514 | 15.9906 | 18.5664 | 104.9999 | 94.0572 | 118.3174 | 17.0385 | 16.2705 | 17.2972 | 16.7668 | 16.1559 | 17.7423 | 32.0189 | 118.307 |  | 58.7312 | 91.6901 | 91.4081 | 80.3798 |  | 6.8131 | 7.2632 | 6.5583 | 7.3812 | 7.8138 | 9.8972 | 42.4892 | 4.9986 | 6.9162 | 4.8736 | 7.5674 | 8.3779 | 41.1924 | 46.4116 | 42.1936 | 14.6962 |  |  | -0.40325 | 0.065799 | -0.029032 | 0.033514 | -0.19763 | -0.098368 | 0.70039 | -0.000164 | -0.46702 | -0.32956 | -0.1084 | -0.00058976 | -0.00061604 | 1.5098 | 15.8047 | 16.6555 | 17.2019 | 17.5262 | 17.4741 | 16.4149 | 14.7516 | 16.7913 | 17.1186 | 17.4211 | 17.4549 | 17.1679 | 16.3242 | 14.5217 | 34.6581 | 16.758 | 22.2788 | 16.7325 | 13.7988 | 20.0532 | 13.6548 | 15.8477 | 15.4849 | 15.3781 | 14.2647 | 14.5243 | 15.3763 |  |  |  | 28.3228 | 105.4787 | 85.2519 | 55.2239 | 0.54322 | 0.36965 | 34.6757 |  |  | 10.9812 |  |  | 16.8884 | 16.3413 | 20.5267 | 16.3313 | 15.7259 | 16.9557 | 104.1664 | 130.8539 | 85.5984 | 86.1742 | 63.9291 |  | 32.0381 | 74.588 | 32.6479 | 56.8052 | 36.2536 | 97.7554 |  | 52.2934 |  |  | 13.8762 | 15.7887 | 38.44 | [6 empty] | 40.8046 |  |  | 27.8669 |  |  | 14.7692 | 36.2195 | 144.7781 | 8.7127 | 31.9348 | 97.3128 | 10.3353 | 31.0724 | 107.9 | 18.1894 | 78.5652 | 10.522 | 72.652 | 11.9158 | 76.4486 | 9.9077 | 32.2218 | 90.0193 | 19.0203 | 33.8804 | 106.6956 | 10.7198 | 30.2287 | 104.8535 | 11.3506 | 73.864 | 16.8893 | 79.5981 | 12.5624 | 82.7147 | 0.796 | 19.7552 | 0.9089 | 0.072984 | -38.0501 | 3.1232 | 171.03 | 48.99 | -0.87559 | 0.29935 | -0.19884 | 0.21364 | -0.52122 | -0.36773 | 0.98122 | -0.39399 | -0.66919 | -0.051258 | -1.2037 | -0.57457 | -0.85161 | -0.2789
42810.4447 | 403 | 18.4044 | 18.5337 | 18.5237 | 18.5152 | 17.8231 | 16.4281 | 14.4855 | 16.6178 | 17.1072 | 17.202 | 17.1978 | 16.7187 | 15.7292 | 14.3425 | 14.7739 | 14.8147 | 15.3975 | 13.2731 | 13.7208 | 15.1149 |  |  |  | 16.5109 | 15.998 | 18.5845 | 105.2786 | 94.2309 | 117.9918 | 17.0376 | 16.2728 | 17.3111 | 16.7587 | 16.1533 | 17.7511 | 32.1567 | 118.2432 |  | 58.9472 | 91.9064 | 91.5749 | 80.3887 |  | 6.8172 | 7.2693 | 6.5436 | 7.3678 | 7.7977 | 9.887 | 42.2038 | 4.9939 | 6.9131 | 4.8527 | 7.5754 | 8.3844 | 41.1644 | 46.4274 | 42.197 | 14.7188 |  |  | -0.39668 | 0.074343 | 0.052448 | 0.030886 | 0.002136 | -0.27645 | 0.76938 | 0.1858 | 0.061314 | 0.60069 | -0.16205 | -0.00060947 | -0.00058976 | 1.5755 | 15.8067 | 16.6681 | 17.2102 | 17.5235 | 17.4782 | 16.4179 | 14.7649 | 16.7964 | 17.1313 | 17.4263 | 17.458 | 17.1706 | 16.3339 | 14.5312 | 35.7126 | 18.3821 | 24.8314 | 18.111 | 14.7506 | 20.1731 | 13.7213 | 15.8531 | 15.4887 | 15.3785 | 14.2665 | 14.5352 | 15.3823 |  |  |  | 28.4465 | 105.6647 | 85.336 | 55.9117 | 0.6198 | 0.22511 | 34.7381 |  |  | 10.9882 |  |  | 16.8892 | 16.3478 | 20.5542 | 16.3407 | 15.7232 | 16.9695 | 104.5841 | 130.9226 | 85.8695 | 86.4128 | 65.4733 |  | 32.1852 | 75.1956 | 32.7937 | 56.9183 | 36.5377 | 98.587 |  | 52.4738 |  |  | 13.8933 | 15.7966 | 38.3874 | [6 empty] | 41.1644 |  |  | 27.8278 |  |  | 14.8021 | 36.458 | 144.8605 | 8.7421 | 31.9439 | 97.4219 | 10.3146 | 31.2354 | 108.0376 | 18.2148 | 78.622 | 10.5225 | 72.9068 | 11.9336 | 76.6592 | 9.8965 | 32.6425 | 90.1169 | 19.0493 | 33.8567 | 106.8278 | 10.7187 | 30.4576 | 105.1536 | 11.3346 | 74.0629 | 16.9 | 79.7624 | 12.5796 | 83.016 | 0.64616 | 19.7479 | 0.91502 | 0.071732 | -38.1158 | 3.1232 | 157.14 | 50.45 | -0.86807 | 0.31819 | 0.26726 | 0.20509 | 0.054186 | -0.61645 | 1.0284 | -0.43185 | -0.68107 | -0.044596 | -1.3069 | -0.85045 | -0.84714 | -0.2938
42810.4447 | 404 | 18.4033 | 18.5338 | 18.5196 | 18.5161 | 17.8271 | 16.4276 | 14.4887 | 16.6179 | 17.1076 | 17.2019 | 17.1957 | 16.7184 | 15.7279 | 14.3396 | 14.7745 | 14.816 | 15.4029 | 13.2742 | 13.7133 | 15.1309 |  |  |  | 16.514 | 15.9921 | 18.5999 | 105.5274 | 94.2797 | 119.2735 | 17.0317 | 16.272 | 17.3213 | 16.7587 | 16.1576 | 17.7511 | 32.298 | 118.6008 |  | 59.1476 | 92.0537 | 91.7299 | 80.5062 |  | 6.8282 | 7.2805 | 6.5497 | 7.36 | 7.7859 | 9.8805 | 43.1366 | 4.9911 | 6.9255 | 4.8541 | 7.5935 | 8.3879 | 41.1468 | 46.4434 | 42.2011 | 14.742 |  |  | -0.29548 | 0.18868 | -0.001436 | -0.030886 | -0.042548 | 0.17433 | 0.59853 | -0.050104 | -0.30667 | -0.61363 | -0.13125 | -0.00057333 | -0.00060455 | 1.6353 | 15.7954 | 16.6561 | 17.1949 | 17.5237 | 17.4635 | 16.4146 | 14.7548 | 16.7836 | 17.1248 | 17.413 | 17.4476 | 17.1641 | 16.3261 | 14.5184 | 36.8769 | 19.2131 | 26.2129 | 18.8441 | 15.9167 | 20.2909 | 13.7878 | 15.852 | 15.4936 | 15.3819 | 14.2636 | 14.5388 | 15.3964 |  |  |  | 28.556 | 105.8601 | 85.3045 | 56.2507 | 0.45428 | 0.08622 | 34.6601 |  |  | 10.9921 |  |  | 16.8922 | 16.342 | 20.5825 | 16.3406 | 15.7247 | 16.981 | 104.9673 | 131.0432 | 86.0768 | 86.6657 | 66.1699 |  | 32.3222 | 75.0878 | 32.9275 | 56.8382 | 36.7533 | 99.6454 |  | 52.6005 |  |  | 13.915 | 15.8377 | 38.6698 | [6 empty] | 41.8777 |  |  | 27.9187 |  |  | 14.8292 | 36.7531 | 144.7232 | 8.7609 | 31.9661 | 97.5228 | 10.2974 | 31.074 | 108.3899 | 18.2464 | 78.7083 | 10.5233 | 73.196 | 11.9507 | 77.0515 | 9.9095 | 32.7498 | 90.322 | 19.1014 | 33.9559 | 107.008 | 10.7045 | 30.6264 | 105.5948 | 11.3243 | 74.2817 | 16.9152 | 79.7432 | 12.6119 | 83.2995 | 0.63903 | 19.7433 | 0.92402 | 0.069699 | -38.065 | 3.1232 | 164.33 | 48.69 | -0.75043 | 0.50692 | -0.044224 | -0.2051 | -0.24184 | 0.48952 | 0.90704 | -0.44651 | -0.67349 | -0.034932 | -1.4225 | -0.99621 | -0.84556 | -0.29949
42810.4447 | 405 | 18.4046 | 18.5355 | 18.5228 | 18.5231 | 17.8147 | 16.4336 | 14.4797 | 16.6104 | 17.1174 | 17.2015 | 17.2038 | 16.7182 | 15.7217 | 14.3423 | 14.7696 | 14.8096 | 15.4004 | 13.2802 | 13.7223 | 15.13 |  |  |  | 16.5152 | 15.9934 | 18.6291 | 105.7148 | 94.3522 | 118.5804 | 17.0374 | 16.27 | 17.3413 | 16.7664 | 16.1607 | 17.7777 | 32.4646 | 118.5724 |  | 59.3712 | 92.3021 | 91.8899 | 78.3585 |  | 6.8233 | 7.2918 | 6.5599 | 7.3649 | 7.7843 | 9.8777 | 43.1124 | 5.0068 | 6.9348 | 4.8788 | 7.5982 | 8.3845 | 41.1246 | 46.4401 | 42.2138 | 14.7739 |  |  | -0.41968 | 0.11311 | 0.024192 | -0.23985 | -0.096432 | 0.29261 | 0.59393 | 0.057664 | -0.8426 | -0.45942 | -0.17715 | -0.00060126 | -0.0006029 | 1.5406 | 15.7999 | 16.6619 | 17.1982 | 17.5301 | 17.469 | 16.4176 | 14.7617 | 16.7919 | 17.1318 | 17.4165 | 17.4521 | 17.1655 | 16.3332 | 14.5281 | 36.9875 | 19.0409 | 26.3703 | 19.1113 | 16.5645 | 20.3941 | 13.8404 | 15.8549 | 15.4891 | 15.3807 | 14.2667 | 14.5377 | 15.4144 |  |  |  | 28.6815 | 106.166 | 85.4874 | 56.7904 | 0.54646 | 0.01621 | 34.7933 |  |  | 10.9998 |  |  | 16.8916 | 16.3495 | 20.6031 | 16.3326 | 15.7288 | 16.9953 | 105.1788 | 131.1706 | 86.3062 | 86.9623 | 66.0442 |  | 32.4517 | 75.2191 | 33.0603 | 56.9296 | 36.933 | 99.8733 |  | 52.7539 |  |  | 13.9388 | 15.8599 | 38.6662 | [6 empty] | 41.4375 |  |  | 27.9956 |  |  | 14.8435 | 37.1143 | 144.8773 | 8.7792 | 32.4836 | 97.7878 | 10.2886 | 31.2357 | 108.738 | 18.2787 | 78.8313 | 10.5209 | 73.4848 | 11.9693 | 77.3684 | 9.9314 | 32.8131 | 90.4868 | 19.1537 | 34.2432 | 107.3047 | 10.7084 | 30.6865 | 105.8719 | 11.3252 | 74.4955 | 16.956 | 79.8301 | 12.626 | 83.5063 | 0.7648 | 19.7324 | 0.93299 | 0.071493 | -38.0332 | 3.1232 | 170.69 | 49.19 | -0.89355 | 0.3925 | 0.18152 | -0.57155 | -0.36408 | 0.6342 | 0.90355 | -0.43858 | -0.67258 | -0.031261 | -1.4227 | -1.0076 | -0.7802 | -0.31021
42810.4447 | 406 | 18.3954 | 18.5324 | 18.5203 | 18.5123 | 17.8234 | 16.4256 | 14.4874 | 16.6146 | 17.1051 | 17.1981 | 17.1974 | 16.7184 | 15.7209 | 14.3409 | 14.7604 | 14.8098 | 15.3922 | 13.2657 | 13.7138 | 15.1265 |  |  |  | 16.5064 | 15.9878 | 18.6378 | 105.7533 | 94.5483 | 118.7847 | 17.034 | 16.2719 | 17.346 | 16.761 | 16.1566 | 17.7932 | 32.6121 | 118.7135 |  | 59.6037 | 92.5226 | 92.0482 | 76.4333 |  | 6.8245 | 7.2934 | 6.5582 | 7.3751 | 7.7825 | 9.8558 | 43.0513 | 5.1059 | 6.9355 | 4.9198 | 7.6042 | 8.387 | 41.1207 | 46.4545 | 42.2207 | 14.7932 |  |  | -0.35528 | -0.15236 | -0.031664 | -0.15639 | 0.077704 | -0.094428 | 0.61365 | 0.13454 | 0.35672 | -0.43803 | -0.16861 | -0.00055526 | -0.00059797 | 1.4994 | 15.8038 | 16.658 | 17.1968 | 17.5245 | 17.469 | 16.4198 | 14.7631 | 16.7948 | 17.1311 | 17.4175 | 17.4571 | 17.1628 | 16.3294 | 14.5319 | 38.8758 | 19.1715 | 26.1335 | 19.2642 | 17.1614 | 20.5128 | 13.9001 | 15.8531 | 15.4943 | 15.382 | 14.2599 | 14.5471 | 15.4229 |  |  |  | 28.8209 | 106.4663 | 85.6707 | 57.6419 | 0.46502 | 0.17863 | 35.1238 |  |  | 11.0057 |  |  | 16.8906 | 16.3441 | 20.6251 | 16.3485 | 15.7334 | 17.0063 | 105.2527 | 131.3763 | 86.5834 | 87.3376 | 66.0898 |  | 32.5941 | 75.4295 | 33.2131 | 57.6049 | 37.1433 | 99.9702 |  | 52.9749 |  |  | 13.99 | 15.8658 | 39.2013 | [6 empty] | 41.2249 |  |  | 28.0186 |  |  | 14.8684 | 37.2358 | 145.1253 | 8.7861 | 32.7449 | 98.0169 | 10.2949 | 31.5816 | 108.8146 | 18.3073 | 78.9284 | 10.5083 | 73.7291 | 11.9709 | 77.611 | 9.9577 | 32.9453 | 90.6595 | 19.1852 | 34.4254 | 107.4938 | 10.7101 | 30.7936 | 106.0711 | 11.3405 | 74.6697 | 17.053 | 80.0091 | 12.6417 | 83.6261 | 0.64038 | 19.7218 | 0.94192 | 0.070922 | -38.1143 | 3.1232 | 171.6 | 50.06 | -0.82236 | -0.45554 | -0.20767 | -0.46153 | 0.3268 | -0.36026 | 0.91838 | -0.43497 | -0.67319 | -0.042759 | -1.6187 | -0.97431 | -0.72167 | -0.32912
42810.4447 | 407 | 18.4019 | 18.5331 | 18.5219 | 18.5111 | 17.8221 | 16.4289 | 14.4896 | 16.6106 | 17.1069 | 17.2045 | 17.1995 | 16.7098 | 15.7248 | 14.3429 | 14.7651 | 14.806 | 15.3898 | 13.2641 | 13.7191 | 15.1319 |  |  |  | 16.5055 | 15.9969 | 18.6571 | 106.0394 | 94.7329 | 119.7183 | 17.0315 | 16.2659 | 17.3532 | 16.762 | 16.16 | 17.8034 | 32.7331 | 119.4589 |  | 59.8253 | 92.7174 | 92.2382 | 75.0904 |  | 6.8216 | 7.2973 | 6.5567 | 7.3852 | 7.8035 | 9.8455 | 43.5729 | 5.173 | 6.9359 | 4.9638 | 7.6088 | 8.3905 | 41.125 | 46.4612 | 42.2406 | 14.8197 |  |  | -0.53073 | -0.082053 | 0.002508 | 0.27993 | 0.04222 | 0.17039 | 0.55188 | 0.1444 | 0.32655 | -1.0282 | -0.20397 | -0.00061276 | -0.0006259 | 1.611 | 15.7985 | 16.6574 | 17.1995 | 17.5287 | 17.4744 | 16.4228 | 14.7618 | 16.7926 | 17.131 | 17.4254 | 17.4622 | 17.1608 | 16.3341 | 14.5298 | 39.1568 | 19.1833 | 27.6448 | 20.0208 | 16.9847 | 20.6289 | 13.9622 | 15.8512 | 15.4897 | 15.376 | 14.2703 | 14.5507 | 15.4263 |  |  |  | 28.9487 | 106.7618 | 85.8314 | 58.5392 | 0.40971 | 0.26238 | 35.0313 |  |  | 11.0052 |  |  | 16.8793 | 16.3576 | 20.6471 | 16.3391 | 15.7277 | 17.0126 | 105.5461 | 131.6889 | 86.8555 | 87.594 | 66.9103 |  | 32.7277 | 75.3669 | 33.3497 | 58.4564 | 37.3494 | 100.446 |  | 53.1538 |  |  | 14.0223 | 15.8943 | 39.9394 | [6 empty] | 41.3462 |  |  | 28.0314 |  |  | 14.9122 | 37.3044 | 145.0817 | 8.8026 | 32.5615 | 98.3217 | 10.3102 | 31.6891 | 108.7918 | 18.3419 | 79.0362 | 10.5137 | 73.9334 | 11.9863 | 77.7289 | 9.9743 | 33.1769 | 90.8712 | 19.1977 | 34.5801 | 107.5554 | 10.7022 | 31.0106 | 106.2032 | 11.3394 | 74.9006 | 17.1107 | 80.1313 | 12.6497 | 83.7678 | 0.74131 | 19.7136 | 0.95058 | 0.073983 | -38.1251 | 3.1233 | 158.71 | 49.12 | -1.0063 | -0.3343 | 0.058446 | 0.61747 | 0.24089 | 0.48393 | 0.87092 | -0.45318 | -0.66676 | -0.059284 | -1.6363 | -1.135 | -0.68022 | -0.3497
42810.4448 | 408 | 18.4028 | 18.5407 | 18.5317 | 18.5167 | 17.8264 | 16.4353 | 14.4903 | 16.6197 | 17.114 | 17.2056 | 17.2046 | 16.7174 | 15.7226 | 14.3413 | 14.7569 | 14.7953 | 15.391 | 13.2632 | 13.7182 | 15.1448 |  |  |  | 16.5091 | 15.995 | 18.6742 | 106.2805 | 94.8297 | 119.3836 | 17.0349 | 16.276 | 17.3725 | 16.7548 | 16.1629 | 17.8166 | 32.8638 | 119.1892 |  | 60.0737 | 92.8927 | 92.4853 | 76.3393 |  | 6.8169 | 7.2999 | 6.5722 | 7.388 | 7.8414 | 9.8409 | 44.8069 | 5.2178 | 6.9397 | 5.0018 | 7.6184 | 8.4018 | 41.1289 | 46.4539 | 42.2604 | 14.8443 |  |  | -0.40982 | -0.14973 | -0.057288 | -0.00723 | -0.1766 | 0.44506 | 0.60708 | 0.049776 | -0.0048496 | 0.53985 | -0.1241 | -0.00059797 | -0.00056348 | 1.4518 | 15.8002 | 16.6571 | 17.204 | 17.5211 | 17.4601 | 16.4181 | 14.7565 | 16.788 | 17.1192 | 17.4144 | 17.4467 | 17.1649 | 16.3339 | 14.5156 | 40.4783 | 20.1666 | 29.8467 | 21.0677 | 17.8968 | 20.7778 | 14.0624 | 15.8409 | 15.4834 | 15.3704 | 14.2636 | 14.5427 | 15.4276 |  |  |  | 29.0604 | 107.0271 | 86.0615 | 59.3458 | 0.44962 | 0.4278 | 34.9172 |  |  | 11.0259 |  |  | 16.8824 | 16.3571 | 20.6921 | 16.3347 | 15.7331 | 17.0247 | 105.5498 | 131.8664 | 87.1408 | 87.9129 | 67.6188 |  | 32.8626 | 75.2376 | 33.4612 | 58.7828 | 37.5387 | 100.4883 |  | 53.3254 |  |  | 14.0251 | 15.8838 | 39.9562 | [6 empty] | 40.8703 |  |  | 28.0626 |  |  | 14.9405 | 37.6789 | 145.6689 | 8.8074 | 32.6206 | 98.4488 | 10.3176 | 31.6536 | 108.901 | 18.3883 | 79.2071 | 10.5202 | 74.0784 | 11.9959 | 77.8867 | 9.9986 | 33.4369 | 91.0954 | 19.2195 | 34.7102 | 107.7558 | 10.7097 | 31.3711 | 106.5151 | 11.3512 | 75.1081 | 17.1574 | 80.2766 | 12.6711 | 83.8128 | 0.68102 | 19.7042 | 0.95787 | 0.073882 | -38.0317 | 3.1232 | 174.86 | 49.9 | -0.8839 | -0.4516 | -0.27934 | -0.099235 | -0.49266 | 0.7821 | 0.91343 | -0.46824 | -0.65935 | -0.061809 | -1.7657 | -1.368 | -0.71044 | -0.36831
42810.4448 | 409 | 18.3993 | 18.5314 | 18.5295 | 18.5201 | 17.8296 | 16.4279 | 14.4913 | 16.6214 | 17.1113 | 17.2007 | 17.1982 | 16.7236 | 15.7244 | 14.337 | 14.7566 | 14.8042 | 15.3916 | 13.2657 | 13.726 | 15.1522 |  |  |  | 16.5103 | 16.0037 | 18.6944 | 106.4166 | 94.9388 | 119.3681 | 17.0362 | 16.2741 | 17.392 | 16.7643 | 16.1662 | 17.8348 | 33.0429 | 119.5131 |  | 60.3067 | 93.0736 | 92.7219 | 79.2351 |  | 6.7981 | 7.2949 | 6.5662 | 7.3825 | 7.8777 | 9.8115 | 44.8268 | 5.2565 | 6.9313 | 4.9821 | 7.6176 | 8.4035 | 41.1395 | 46.4435 | 42.2589 | 14.8585 |  |  | -0.51299 | 0.092083 | 0.034048 | 0.048626 | -0.13257 | 0.20456 | 0.44542 | 0.24494 | -0.47014 | -0.16717 | -0.19424 | -0.00057826 | -0.00064397 | 1.2816 | 15.7964 | 16.6566 | 17.1911 | 17.52 | 17.4616 | 16.4171 | 14.7448 | 16.7891 | 17.1181 | 17.4124 | 17.4527 | 17.1607 | 16.3255 | 14.519 | 41.662 | 20.5998 | 30.4408 | 20.9274 | 17.8785 | 20.8835 | 14.1364 | 15.847 | 15.4841 | 15.378 | 14.2721 | 14.5493 | 15.4444 |  |  |  | 29.2014 | 107.3228 | 86.3208 | 59.2101 | 0.25411 | 0.074364 | 34.8232 |  |  | 11.0252 |  |  | 16.8905 | 16.3599 | 20.7133 | 16.3288 | 15.7343 | 17.0417 | 105.4843 | 131.8774 | 87.3753 | 88.183 | 68.2586 |  | 32.9775 | 74.9738 | 33.56 | 58.6538 | 37.7003 | 101.2565 |  | 53.5035 |  |  | 14.0447 | 15.899 | 39.9233 | [6 empty] | 40.8799 |  |  | 28.1427 |  |  | 14.9554 | 37.9623 | 145.966 | 8.8157 | 32.9949 | 98.5861 | 10.3134 | 31.9451 | 109.2377 | 18.4276 | 79.4312 | 10.5152 | 74.2271 | 11.9891 | 78.0176 | 10.0188 | 33.5022 | 91.291 | 19.2436 | 34.719 | 107.9807 | 10.7144 | 31.694 | 106.6699 | 11.3599 | 75.3028 | 17.2202 | 80.3926 | 12.6808 | 83.9353 | 0.74901 | 19.696 | 0.96445 | 0.075105 | -38.0993 | 3.1232 | 173.09 | 49.52 | -0.9889 | 0.35414 | 0.21535 | 0.25735 | -0.42683 | 0.5302 | 0.78238 | -0.48207 | -0.64863 | -0.052637 | -1.8849 | -1.4254 | -0.78473 | -0.35974
42810.4448 | 410 | 18.3872 | 18.5255 | 18.5214 | 18.5165 | 17.8213 | 16.4208 | 14.488 | 16.6177 | 17.1099 | 17.2026 | 17.193 | 16.7152 | 15.7271 | 14.3353 | 14.747 | 14.8086 | 15.396 | 13.2642 | 13.7254 | 15.1625 |  |  |  | 16.5098 | 16.0073 | 18.7167 | 106.5458 | 95.1367 | 119.2283 | 17.037 | 16.2655 | 17.3974 | 16.7557 | 16.1664 | 17.8517 | 33.2393 | 120.2311 |  | 60.5372 | 93.215 | 92.9042 | 80.4104 |  | 6.799 | 7.3009 | 6.5657 | 7.4054 | 7.9074 | 9.8113 | 44.2968 | 5.3115 | 6.943 | 4.9478 | 7.6266 | 8.4215 | 41.1505 | 46.4287 | 42.2783 | 14.8822 |  |  | -0.49196 | -0.046569 | 0.078076 | 0.11631 | 0.06456 | 0.010056 | 0.45791 | -0.18087 | 0.23821 | -0.1741 | -0.076409 | -0.00057826 | -0.00058812 | 1.3005 | 15.8032 | 16.6521 | 17.1968 | 17.5244 | 17.4652 | 16.4094 | 14.7502 | 16.785 | 17.118 | 17.4126 | 17.451 | 17.1642 | 16.3287 | 14.5256 | 41.746 | 19.9718 | 29.2509 | 19.8439 | 17.2214 | 20.9903 | 14.1975 | 15.8431 | 15.4891 | 15.3737 | 14.269 | 14.5487 | 15.4465 |  |  |  | 29.344 | 107.6897 | 86.4565 | 59.138 | 0.21602 | 0.0037888 | 34.6676 |  |  | 11.0136 |  |  | 16.8836 | 16.3576 | 20.746 | 16.3294 | 15.7347 | 17.0532 | 105.6677 | 132.1747 | 87.5945 | 88.4611 | 68.2286 |  | 33.121 | 74.9587 | 33.6883 | 60.5282 | 37.9359 | 101.3309 |  | 53.6976 |  |  | 14.079 | 15.9446 | 39.9288 | [6 empty] | 41.9049 |  |  | 28.2071 |  |  | 14.9859 | 38.1377 | 145.9775 | 8.8221 | 33.4704 | 98.7936 | 10.3145 | 32.2656 | 109.5294 | 18.442 | 79.9368 | 10.5049 | 74.5086 | 12.0014 | 78.2074 | 10.0418 | 33.6916 | 91.5976 | 19.2775 | 34.8038 | 108.1802 | 10.7213 | 31.9038 | 106.7489 | 11.3778 | 75.4469 | 17.2864 | 80.384 | 12.6838 | 84.2493 | 0.87343 | 19.6899 | 0.97061 | 0.074808 | -38.095 | 3.1232 | 175.41 | 49.22 | -0.96824 | -0.25185 | 0.3261 | 0.39802 | 0.29786 | 0.11756 | 0.79327 | -0.47632 | -0.6438 | -0.096553 | -1.8818 | -1.286 | -0.81064 | -0.35288
42810.4448 | 411 | 18.3897 | 18.5221 | 18.5116 | 18.5045 | 17.819 | 16.4183 | 14.4799 | 16.6085 | 17.0981 | 17.2013 | 17.1923 | 16.7078 | 15.7156 | 14.3346 | 14.7473 | 14.8051 | 15.3967 | 13.2638 | 13.73 | 15.1703 |  |  |  | 16.5076 | 16.0006 | 18.731 | 106.6263 | 95.3818 | 118.7803 | 17.0284 | 16.2651 | 17.4056 | 16.7576 | 16.1631 | 17.8615 | 33.4172 | 120.5681 |  | 60.753 | 93.3971 | 93.0318 | 81.8376 |  | 6.7999 | 7.3014 | 6.5763 | 7.4131 | 7.9383 | 9.8021 | 44.3809 | 5.3832 | 6.9416 | 4.9096 | 7.6273 | 8.4222 | 41.1682 | 46.4062 | 42.2734 | 14.8927 |  |  | -0.35068 | -0.13462 | -0.081604 | -0.062426 | 0.046164 | 0.33598 | 0.60445 | 0.036636 | -1.4272 | 0.22117 | -0.20715 | -0.00058976 | -0.0005914 | 1.3428 | 15.8007 | 16.6565 | 17.1932 | 17.5265 | 17.4697 | 16.4161 | 14.7517 | 16.7786 | 17.1187 | 17.4189 | 17.4526 | 17.1697 | 16.3279 | 14.5221 | 40.7337 | 19.3296 | 28.868 | 18.7793 | 16.4902 | 21.0692 | 14.2684 | 15.8421 | 15.4811 | 15.3758 | 14.2627 | 14.5526 | 15.4532 |  |  |  | 29.4648 | 108.2572 | 86.6093 | 59.8253 | 0.16071 | -0.19909 | 34.7256 |  |  | 11.0059 |  |  | 16.8911 | 16.3574 | 20.7713 | 16.324 | 15.7384 | 17.0698 | 105.9542 | 132.0707 | 87.8295 | 88.6937 | 68.356 |  | 33.2488 | 75.076 | 33.7916 | 62.0035 | 38.1749 | 100.3648 |  | 53.8572 |  |  | 14.1135 | 15.9766 | 39.7502 | [6 empty] | 42.3681 |  |  | 28.2845 |  |  | 15.0116 | 38.4874 | 145.8934 | 8.8247 | 33.6227 | 98.9097 | 10.3195 | 32.2805 | 109.7803 | 18.468 | 80.6726 | 10.4917 | 74.7632 | 12.0183 | 78.4456 | 10.0605 | 34.1924 | 91.8964 | 19.3246 | 35.0851 | 108.4187 | 10.7331 | 32.0291 | 106.9252 | 11.3925 | 75.6267 | 17.3416 | 80.506 | 12.6853 | 84.6026 | 0.64674 | 19.6825 | 0.97725 | 0.076328 | -38.1135 | 3.1232 | 166.9 | 50.22 | -0.81701 | -0.42821 | -0.33339 | -0.29159 | 0.25187 | 0.67949 | 0.91139 | -0.47547 | -0.64351 | -0.12926 | -1.7601 | -1.2352 | -0.84419 | -0.36786
42810.4448 | 412 | 18.3815 | 18.5132 | 18.5108 | 18.5078 | 17.8102 | 16.4231 | 14.4788 | 16.6028 | 17.0975 | 17.1932 | 17.1953 | 16.7067 | 15.7127 | 14.3338 | 14.7505 | 14.8088 | 15.4047 | 13.2704 | 13.7338 | 15.1821 |  |  |  | 16.5063 | 15.9963 | 18.7513 | 106.81 | 95.6089 | 118.8762 | 17.0184 | 16.2673 | 17.4156 | 16.7564 | 16.154 | 17.8743 | 33.6038 | 120.8553 |  | 60.9495 | 93.5778 | 93.1362 | 80.7972 |  | 6.8089 | 7.3027 | 6.5846 | 7.4507 | 7.9546 | 9.8192 | 44.6638 | 5.5211 | 6.9506 | 4.9052 | 7.6346 | 8.4287 | 41.1956 | 46.3866 | 42.2845 | 14.9073 |  |  | -0.53336 | 0.14531 | -0.071748 | 0.071626 | -0.01232 | 0.12636 | 0.55451 | -0.10136 | 0.2709 | -0.24039 | -0.19424 | -0.00062262 | -0.0006144 | 1.4456 | 15.8072 | 16.658 | 17.1952 | 17.5235 | 17.4678 | 16.414 | 14.7514 | 16.7803 | 17.1225 | 17.4187 | 17.4547 | 17.1655 | 16.3294 | 14.5172 | 40.7104 | 19.1546 | 27.5046 | 18.2052 | 16.1675 | 21.1814 | 14.3225 | 15.8319 | 15.484 | 15.3792 | 14.2613 | 14.5523 | 15.4612 |  |  |  | 29.5987 | 108.747 | 86.8066 | 60.457 | 0.58779 | 0.1216 | 34.7475 |  |  | 11.0004 |  |  | 16.8838 | 16.3727 | 20.8024 | 16.3354 | 15.7381 | 17.0784 | 106.3624 | 132.2756 | 88.0446 | 88.9134 | 69.2311 |  | 33.3835 | 75.6829 | 33.8999 | 61.1543 | 38.3526 | 99.6651 |  | 54.0213 |  |  | 14.1446 | 15.9796 | 39.7667 | [6 empty] | 42.2736 |  |  | 28.4159 |  |  | 15.0316 | 38.6821 | 145.8922 | 8.8236 | 33.8715 | 99.0923 | 10.316 | 32.279 | 109.9185 | 18.501 | 80.9123 | 10.48 | 74.9953 | 12.027 | 78.752 | 10.087 | 34.5665 | 92.1266 | 19.3698 | 35.3824 | 108.8041 | 10.7496 | 32.0967 | 107.1449 | 11.4087 | 75.8156 | 17.3771 | 80.8205 | 12.6885 | 84.7821 | 0.70201 | 19.6748 | 0.98453 | 0.075206 | -38.1501 | 3.1233 | 177.76 | 49.2 | -1.0077 | 0.44488 | -0.31261 | 0.31234 | -0.13012 | 0.41672 | 0.87295 | -0.49516 | -0.65665 | -0.099517 | -1.7444 | -1.0774 | -0.80888 | -0.38084
42810.4448 | 413 | 18.3873 | 18.5287 | 18.5242 | 18.5109 | 17.8101 | 16.4227 | 14.4887 | 16.6185 | 17.1056 | 17.1996 | 17.1907 | 16.7079 | 15.724 | 14.3391 | 14.7412 | 14.8114 | 15.3984 | 13.2705 | 13.7384 | 15.188 |  |  |  | 16.5093 | 16.0049 | 18.7659 | 106.9534 | 95.8641 | 118.0567 | 17.0201 | 16.2766 | 17.4284 | 16.7564 | 16.161 | 17.9029 | 33.782 | 122.1087 |  | 61.2014 | 93.7555 | 93.2796 | 78.565 |  | 6.8107 | 7.312 | 6.608 | 7.4802 | 7.9697 | 9.8315 | 44.7328 | 5.6259 | 6.9495 | 4.8958 | 7.6333 | 8.438 | 41.2305 | 46.369 | 42.2938 | 14.9126 |  |  | -0.55504 | 0.048715 | 0.13722 | -0.13471 | 0.068504 | 0.2821 | 0.50916 | -0.14144 | -0.22397 | 0.99386 | -0.071044 | -0.00060126 | -0.0006029 | 1.5324 | 15.8082 | 16.6579 | 17.2035 | 17.521 | 17.4732 | 16.418 | 14.7544 | 16.7929 | 17.1285 | 17.4223 | 17.4568 | 17.1662 | 16.3304 | 14.5227 | 42.6303 | 19.7429 | 27.9375 | 18.3314 | 15.5837 | 21.3267 | 14.3889 | 15.8379 | 15.4887 | 15.3829 | 14.2612 | 14.5584 | 15.4759 |  |  |  | 29.7498 | 109.2388 | 86.762 | 60.9126 | 0.42956 | 0.22455 | 34.8795 |  |  | 10.9957 |  |  | 16.8818 | 16.3641 | 20.8321 | 16.3385 | 15.7425 | 17.0978 | 106.6329 | 132.3651 | 88.2449 | 89.1824 | 69.9115 |  | 33.5296 | 76.032 | 34.0105 | 63.0948 | 38.6254 | 99.6231 |  | 54.2197 |  |  | 14.1636 | 15.9916 | 39.8588 | [6 empty] | 42.5816 |  |  | 28.4863 |  |  | 15.0458 | 38.6816 | 146.3401 | 8.8241 | 34.2229 | 99.4494 | 10.318 | 32.6828 | 110.1046 | 18.5278 | 80.9947 | 10.4728 | 75.2228 | 12.0382 | 78.9932 | 10.101 | 34.5597 | 92.3311 | 19.4104 | 35.4536 | 109.3205 | 10.7568 | 32.1711 | 107.3724 | 11.4244 | 76.0389 | 17.3844 | 80.9759 | 12.6782 | 84.922 | 0.93756 | 19.6671 | 0.99193 | 0.076487 | -38.1359 | 3.1233 | 172.66 | 48.86 | -1.0269 | 0.25759 | 0.43232 | -0.42836 | 0.30683 | 0.62266 | 0.83652 | -0.50905 | -0.66255 | -0.14397 | -1.9407 | -1.1178 | -0.74076 | -0.38835
42810.4448 | 414 | 18.3828 | 18.5261 | 18.5214 | 18.5145 | 17.8145 | 16.43 | 14.4866 | 16.6123 | 17.1043 | 17.1949 | 17.2019 | 16.7084 | 15.7245 | 14.3301 | 14.7422 | 14.8025 | 15.3888 | 13.2634 | 13.7386 | 15.1956 |  |  |  | 16.5071 | 16.0097 | 18.7904 | 107.043 | 96.1101 | 118.7161 | 17.0065 | 16.2616 | 17.4346 | 16.7462 | 16.1568 | 17.8978 | 33.902 | 122.5128 |  | 61.4258 | 93.8135 | 93.4255 | 79.3657 |  | 6.8179 | 7.3164 | 6.6231 | 7.5011 | 8.0009 | 9.8322 | 45.1973 | 5.7694 | 6.9554 | 4.9245 | 7.6477 | 8.4417 | 41.2616 | 46.3581 | 42.3001 | 14.9141 |  |  | -0.37894 | 0.14137 | -0.11972 | 0.02497 | 0.2755 | -0.063544 | 0.56042 | 0.1122 | -0.21502 | -0.83119 | 0.06904 | -0.00058812 | -0.00060455 | 1.5279 | 15.8053 | 16.6537 | 17.1926 | 17.5185 | 17.4645 | 16.4129 | 14.7517 | 16.7961 | 17.1236 | 17.4169 | 17.454 | 17.1628 | 16.329 | 14.5166 | 42.185 | 19.1131 | 28.6576 | 19.7348 | 16.4914 | 21.443 | 14.4616 | 15.8408 | 15.4822 | 15.3761 | 14.2622 | 14.5657 | 15.4838 |  |  |  | 29.9005 | 109.5839 | 86.8134 | 61.4004 | 0.44638 | 0.14005 | 35.0837 |  |  | 10.9983 |  |  | 16.8859 | 16.371 | 20.858 | 16.3317 | 15.7411 | 17.1117 | 106.9085 | 132.4486 | 88.4177 | 89.3801 | 70.0691 |  | 33.6787 | 75.775 | 34.1164 | 62.6323 | 38.9409 | 100.0511 |  | 54.4208 |  |  | 14.1707 | 16.0146 | 39.6536 | [6 empty] | 43.0347 |  |  | 28.5721 |  |  | 15.0662 | 38.8379 | 146.6968 | 8.8207 | 34.2197 | 99.6703 | 10.3185 | 33.2482 | 110.3542 | 18.5644 | 81.0535 | 10.4774 | 75.4047 | 12.0448 | 79.1868 | 10.1178 | 34.3712 | 92.6047 | 19.4419 | 35.5545 | 109.7136 | 10.7735 | 32.336 | 107.592 | 11.4545 | 76.3256 | 17.3955 | 81.0472 | 12.6867 | 85.0929 | 0.82701 | 19.6591 | 0.9982 | 0.077262 | -37.969 | 3.1233 | 164.83 | 50.36 | -0.84922 | 0.43881 | -0.40382 | 0.18442 | 0.61532 | -0.29552 | 0.87761 | -0.50831 | -0.65177 | -0.12019 | -1.8776 | -1.1894 | -0.75888 | -0.39676
42810.4448 | 415 | 18.3771 | 18.5196 | 18.5173 | 18.5044 | 17.8115 | 16.4225 | 14.4749 | 16.6104 | 17.1048 | 17.1899 | 17.1931 | 16.7076 | 15.7215 | 14.3418 | 14.7478 | 14.8003 | 15.3974 | 13.2648 | 13.7367 | 15.2057 |  |  |  | 16.5109 | 16.0145 | 18.8185 | 107.2649 | 96.2579 | 119.9549 | 17.0089 | 16.2639 | 17.4554 | 16.7524 | 16.1643 | 17.9213 | 34.0357 | 122.1681 |  | 61.6514 | 93.8675 | 93.6187 | 80.1476 |  | 6.8197 | 7.3217 | 6.6313 | 7.5292 | 8.0151 | 9.8305 | 45.0777 | 5.7714 | 6.9738 | 4.9465 | 7.653 | 8.4474 | 41.2903 | 46.3639 | 42.2999 | 14.9095 |  |  | -0.25803 | 0.063827 | 0.066248 | -0.09791 | 0.2341 | 0.21376 | 0.40731 | 0.24691 | -0.37984 | 0.076824 | -0.016202 | -0.00061604 | -0.00063412 | 1.4544 | 15.7992 | 16.6623 | 17.1923 | 17.5136 | 17.4678 | 16.407 | 14.752 | 16.7871 | 17.1271 | 17.4125 | 17.4554 | 17.162 | 16.3211 | 14.5228 | 42.3991 | 19.3652 | 29.0425 | 19.3082 | 17.0355 | 21.551 | 14.5266 | 15.833 | 15.4832 | 15.3829 | 14.2697 | 14.5674 | 15.4949 |  |  |  | 30.0358 | 109.8708 | 86.89 | 61.4857 | 0.32948 | 0.095442 | 35.1199 |  |  | 10.9961 |  |  | 16.8872 | 16.3759 | 20.8935 | 16.3358 | 15.7435 | 17.1095 | 107.2062 | 132.892 | 88.4972 | 89.4854 | 70.7832 |  | 33.8046 | 74.5276 | 34.2257 | 61.7234 | 39.2141 | 100.4702 |  | 54.5961 |  |  | 14.1783 | 16.048 | 39.602 | [6 empty] | 43.2608 |  |  | 28.6641 |  |  | 15.0709 | 39.1022 | 147.0426 | 8.8193 | 34.2451 | 99.7945 | 10.317 | 33.5092 | 110.6727 | 18.6029 | 81.1512 | 10.4902 | 75.5829 | 12.0551 | 79.2686 | 10.1181 | 34.2988 | 92.8329 | 19.4677 | 35.8664 | 110.0017 | 10.7757 | 32.4951 | 107.9247 | 11.4758 | 76.5671 | 17.4065 | 81.1838 | 12.6904 | 85.3248 | 0.72551 | 19.6532 | 1.0038 | 0.077472 | -37.9336 | 3.1233 | 144.88 | 48.89 | -0.70187 | 0.29486 | 0.3004 | -0.3652 | 0.56721 | 0.54201 | 0.74818 | -0.52382 | -0.61337 | -0.085464 | -1.8888 | -1.2246 | -0.77601 | -0.39452
42810.4448 | 416 | 18.3754 | 18.5213 | 18.518 | 18.512 | 17.8136 | 16.4264 | 14.4852 | 16.6101 | 17.1051 | 17.1975 | 17.2001 | 16.7123 | 15.7164 | 14.3363 | 14.7406 | 14.7909 | 15.3907 | 13.2651 | 13.7381 | 15.2177 |  |  |  | 16.5015 | 16.012 | 18.8269 | 107.4948 | 96.4249 | 120.2325 | 17.0098 | 16.2674 | 17.4679 | 16.7515 | 16.1653 | 17.9416 | 34.1742 | 121.6697 |  | 61.8424 | 93.9539 | 93.8178 | 80.9975 |  | 6.8285 | 7.3365 | 6.6415 | 7.5515 | 8.0316 | 9.845 | 44.4295 | 5.7774 | 6.9832 | 4.9582 | 7.6605 | 8.456 | 41.304 | 46.3753 | 42.2981 | 14.9133 |  |  | -0.48276 | 0.20905 | -0.029032 | 0.16165 | 0.21438 | 0.50158 | 0.46645 | 0.02152 | 0.84769 | -0.56453 | -0.050776 | -0.0006259 | -0.0005799 | 1.4219 | 15.795 | 16.6519 | 17.195 | 17.5182 | 17.4642 | 16.4087 | 14.7489 | 16.7857 | 17.1184 | 17.4175 | 17.4559 | 17.1597 | 16.3311 | 14.5097 | 42.0912 | 19.2634 | 29.4484 | 19.3363 | 17.0962 | 21.6687 | 14.6056 | 15.8355 | 15.4876 | 15.3836 | 14.2647 | 14.5674 | 15.5021 |  |  |  | 30.1521 | 110.4599 | 87.5079 | 61.2742 | 0.28146 | -0.11101 | 35.2706 |  |  | 11.002 |  |  | 16.8952 | 16.3828 | 20.9246 | 16.3395 | 15.7511 | 17.131 | 107.4063 | 133.2204 | 88.7372 | 89.7071 | 71.0057 |  | 33.9279 | 74.3775 | 34.3399 | 62.0831 | 39.4625 | 99.9714 |  | 54.7685 |  |  | 14.1854 | 16.0842 | 39.5919 | [6 empty] | 43.2604 |  |  | 28.7341 |  |  | 15.0848 | 39.374 | 147.606 | 8.8059 | 34.5528 | 99.9134 | 10.3112 | 33.4281 | 111.2132 | 18.6271 | 81.3026 | 10.488 | 75.7855 | 12.0733 | 79.306 | 10.128 | 34.3738 | 93.0399 | 19.5123 | 36.1553 | 110.624 | 10.7901 | 32.5453 | 108.2663 | 11.5119 | 76.8497 | 17.4326 | 81.3088 | 12.6952 | 85.5901 | 0.61361 | 19.6461 | 1.0086 | 0.076538 | -37.9892 | 3.1233 | 131.43 | 49.19 | -0.96037 | 0.53364 | -0.19887 | 0.46926 | 0.54282 | 0.83028 | 0.80068 | -0.52577 | -0.60527 | -0.086836 | -1.8408 | -1.2604 | -0.79486 | -0.38468
42810.4449 | 417 | 18.3732 | 18.5212 | 18.5145 | 18.5092 | 17.8143 | 16.4223 | 14.4798 | 16.6107 | 17.1045 | 17.1921 | 17.2037 | 16.7111 | 15.7184 | 14.335 | 14.7358 | 14.8066 | 15.3912 | 13.2543 | 13.7344 | 15.2234 |  |  |  | 16.5098 | 16.0139 | 18.8499 | 107.7332 | 96.5596 | 121.3656 | 17.0189 | 16.2718 | 17.487 | 16.758 | 16.1659 | 17.9611 | 34.3475 | 121.638 |  | 62.0214 | 94.1168 | 94.0308 | 81.8918 |  | 6.8291 | 7.3383 | 6.6562 | 7.562 | 8.0436 | 9.8296 | 44.3163 | 5.6668 | 6.9888 | 4.9952 | 7.6608 | 8.4752 | 41.3317 | 46.3793 | 42.2982 | 14.9209 |  |  | -0.41902 | 0.050027 | 0.091876 | -0.11434 | 0.02842 | 0.076424 | 0.73521 | 0.26597 | -0.99711 | 0.76098 | -0.20795 | -0.0006144 | -0.00060947 | 1.3989 | 15.7909 | 16.65 | 17.1942 | 17.5128 | 17.4587 | 16.4074 | 14.7394 | 16.7885 | 17.1232 | 17.4176 | 17.4524 | 17.1581 | 16.3258 | 14.5057 | 40.4229 | 18.0128 | 27.4108 | 18.7849 | 16.5257 | 21.7456 | 14.6534 | 15.8401 | 15.4872 | 15.3932 | 14.2694 | 14.5736 | 15.5139 |  |  |  | 30.2654 | 110.7282 | 87.9329 | 61.0175 | 0.41963 | -0.2691 | 35.4791 |  |  | 11.0023 |  |  | 16.8828 | 16.3686 | 20.9456 | 16.3361 | 15.7441 | 17.1408 | 107.533 | 133.1055 | 89.0317 | 89.974 | 70.9916 |  | 34.0616 | 74.4038 | 34.4712 | 62.2969 | 39.7073 | 100.1269 |  | 55.0106 |  |  | 14.1851 | 16.0762 | 39.9906 | [6 empty] | 43.738 |  |  | 28.7794 |  |  | 15.1324 | 39.809 | 147.807 | 8.7889 | 35.0553 | 100.0617 | 10.3095 | 33.43 | 111.57 | 18.6627 | 81.4052 | 10.468 | 76.044 | 12.0648 | 79.5037 | 10.1408 | 34.5958 | 93.3683 | 19.563 | 36.1815 | 110.8779 | 10.8018 | 32.6986 | 108.501 | 11.5215 | 77.145 | 17.4542 | 81.5457 | 12.7063 | 85.8222 | 0.70124 | 19.6424 | 1.0136 | 0.078673 | -37.9751 | 3.1233 | 147.85 | 50.07 | -0.89602 | 0.26105 | 0.35377 | -0.39466 | 0.19763 | 0.32409 | 1.0052 | -0.52078 | -0.60149 | -0.08428 | -1.6465 | -1.0285 | -0.81374 | -0.37368
42810.4449 | 418 | 18.3688 | 18.5154 | 18.5079 | 18.4956 | 17.8048 | 16.4223 | 14.4772 | 16.6045 | 17.0963 | 17.1877 | 17.1932 | 16.7053 | 15.7143 | 14.331 | 14.737 | 14.8042 | 15.3955 | 13.2649 | 13.7499 | 15.2273 |  |  |  | 16.5115 | 16.0162 | 18.8652 | 107.98 | 96.7382 | 121.5859 | 17.0179 | 16.2692 | 17.4909 | 16.7533 | 16.1682 | 17.9776 | 34.5351 | 122.2261 |  | 62.2116 | 94.3535 | 94.1845 | 81.1344 |  | 6.8327 | 7.3488 | 6.6634 | 7.5682 | 8.0471 | 9.805 | 45.2501 | 5.6236 | 6.9964 | 5.0609 | 7.6815 | 8.4831 | 41.3495 | 46.3818 | 42.3006 | 14.9372 |  |  | -0.76795 | 0.070399 | 0.18782 | 0.32133 | -0.080004 | 0.025824 | 0.4566 | 0.19894 | -0.23876 | -1.49 | -0.21649 | -0.0005799 | -0.00065219 | 1.4298 | 15.7984 | 16.6616 | 17.1982 | 17.5244 | 17.4729 | 16.4149 | 14.7482 | 16.7893 | 17.1285 | 17.4203 | 17.4549 | 17.1644 | 16.3306 | 14.5231 | 39.5267 | 17.5062 | 25.0669 | 18.2304 | 15.9218 | 21.8497 | 14.6842 | 15.8298 | 15.4741 | 15.3829 | 14.2541 | 14.5705 | 15.5169 |  |  |  | 30.3757 | 111.0651 | 88.2171 | 60.7346 | 0.57726 | -0.024818 | 35.4377 |  |  | 11.0035 |  |  | 16.8843 | 16.3755 | 20.9877 | 16.345 | 15.7485 | 17.1676 | 107.786 | 133.4389 | 89.3478 | 90.1974 | 70.7881 |  | 34.1834 | 74.2556 | 34.5704 | 62.0654 | 39.8749 | 100.3139 |  | 55.1957 |  |  | 14.2182 | 16.0931 | 40.1943 | [6 empty] | 43.499 |  |  | 28.83 |  |  | 15.1541 | 39.8191 | 148.2502 | 8.7667 | 35.4541 | 100.2864 | 10.31 | 33.6081 | 112.0493 | 18.6787 | 81.5172 | 10.48 | 76.2405 | 12.0624 | 79.7727 | 10.1542 | 34.8663 | 93.7124 | 19.5929 | 36.3003 | 110.9956 | 10.802 | 32.9882 | 108.7814 | 11.5372 | 77.4655 | 17.4639 | 81.8181 | 12.7344 | 86.1205 | 0.96819 | 19.6359 | 1.0173 | 0.077204 | -37.9675 | 3.1233 | 175.47 | 48.87 | -1.2134 | 0.30968 | 0.50582 | 0.66162 | -0.33157 | 0.18838 | 0.79212 | -0.51095 | -0.59396 | -0.072028 | -1.5347 | -0.76445 | -0.78626 | -0.36206
42810.4449 | 419 | 18.369 | 18.5126 | 18.5038 | 18.5012 | 17.8065 | 16.4185 | 14.468 | 16.6024 | 17.0948 | 17.1893 | 17.1888 | 16.7116 | 15.7124 | 14.3236 | 14.7343 | 14.7965 | 15.3836 | 13.2699 | 13.7473 | 15.2418 |  |  |  | 16.5017 | 16.0149 | 18.8864 | 108.3045 | 96.9143 | 121.7301 | 17.0111 | 16.26 | 17.4953 | 16.7524 | 16.1654 | 17.9859 | 34.7143 | 122.959 |  | 62.4193 | 94.5914 | 94.3339 | 81.6693 |  | 6.8302 | 7.3385 | 6.6553 | 7.5576 | 8.0356 | 9.7856 | 45.3196 | 5.5912 | 6.9983 | 5.0021 | 7.6835 | 8.4876 | 41.357 | 46.3764 | 42.29 | 14.9307 |  |  | -0.46371 | -0.015025 | -0.049404 | 0.29636 | -0.028748 | 0.25056 | 0.60576 | 0.10366 | -0.18291 | -0.51817 | -0.31525 | -0.00057826 | -0.00064561 | 1.5482 | 15.7926 | 16.654 | 17.19 | 17.5183 | 17.472 | 16.4175 | 14.7452 | 16.7867 | 17.1262 | 17.4157 | 17.4509 | 17.1612 | 16.3261 | 14.5232 | 41.2604 | 18.3291 | 25.0388 | 18.0478 | 15.4626 | 22.0093 | 14.7373 | 15.8221 | 15.4756 | 15.3833 | 14.2531 | 14.5696 | 15.5242 |  |  |  | 30.4822 | 111.4749 | 88.5359 | 60.4586 | 0.67937 | 0.17919 | 35.4067 |  |  | 11.014 |  |  | 16.8979 | 16.3887 | 21.0107 | 16.3471 | 15.7494 | 17.187 | 108.12 | 133.643 | 89.6463 | 90.5102 | 68.9481 |  | 34.3024 | 74.0454 | 34.6609 | 62.4913 | 40.0797 | 100.2415 |  | 55.3605 |  |  | 14.2282 | 16.0993 | 40.1007 | [6 empty] | 43.8718 |  |  | 28.9728 |  |  | 15.1887 | 39.7245 | 148.7786 | 8.7618 | 35.7548 | 100.7266 | 10.3161 | 33.7942 | 112.388 | 18.7146 | 81.6685 | 10.4845 | 76.3314 | 12.0804 | 79.9865 | 10.1665 | 35.1656 | 93.9588 | 19.6273 | 36.4427 | 111.3484 | 10.8108 | 33.0874 | 108.9102 | 11.5377 | 77.7218 | 17.4639 | 81.9201 | 12.7358 | 86.3316 | 0.74516 | 19.6308 | 1.0224 | 0.078318 | -38.1024 | 3.1233 | 155.79 | 49.51 | -0.94302 | -0.14306 | -0.25942 | 0.63538 | -0.19875 | 0.58677 | 0.91235 | -0.45575 | -0.58501 | -0.076743 | -1.7087 | -0.75514 | -0.79495 | -0.35076
42810.4449 | 420 | 18.3762 | 18.5226 | 18.5222 | 18.508 | 17.8143 | 16.4196 | 14.4849 | 16.6186 | 17.113 | 17.197 | 17.1915 | 16.7173 | 15.7285 | 14.3447 | 14.7303 | 14.7822 | 15.3794 | 13.2577 | 13.7441 | 15.2449 |  |  |  | 16.5079 | 16.0204 | 18.9033 | 108.6652 | 97.1356 | 124.2126 | 17.0041 | 16.2663 | 17.5061 | 16.7389 | 16.1668 | 17.9882 | 34.9395 | 123.6747 |  | 62.6679 | 94.8964 | 94.503 | 83.2712 |  | 6.8414 | 7.3443 | 6.6616 | 7.5649 | 8.0575 | 9.8344 | 45.0408 | 5.6255 | 7.0008 | 4.8872 | 7.7024 | 8.4918 | 41.3733 | 46.3861 | 42.2983 | 14.9431 |  |  | -0.58921 | 0.12231 | 0.085304 | 0.10908 | -0.037948 | -0.18248 | 0.49602 | 0.2686 | -0.62601 | -0.27627 | -0.14118 | -0.00060455 | -0.0005914 | 1.4936 | 15.7974 | 16.6506 | 17.1935 | 17.5158 | 17.4615 | 16.4183 | 14.7523 | 16.7865 | 17.1219 | 17.4139 | 17.4575 | 17.1594 | 16.3232 | 14.5227 | 43.8619 | 19.7364 | 26.9048 | 18.0329 | 15.7913 | 22.183 | 14.7911 | 15.8228 | 15.4819 | 15.3752 | 14.2608 | 14.5708 | 15.5311 |  |  |  | 30.5952 | 111.8717 | 88.9191 | 60.2836 | 0.4871 | 0.29211 | 35.4874 |  |  | 11.0038 |  |  | 16.8818 | 16.3759 | 21.0293 | 16.3282 | 15.7382 | 17.1812 | 108.3249 | 133.7125 | 89.8375 | 90.7763 | 68.2059 |  | 34.4396 | 73.7403 | 34.7994 | 65.4441 | 40.3363 | 100.6704 |  | 55.5528 |  |  | 14.2574 | 16.1244 | 39.904 | [6 empty] | 46.8 |  |  | 29.0729 |  |  | 15.2004 | 39.9319 | 149.645 | 8.7529 | 36.0022 | 100.9771 | 10.3389 | 33.9402 | 112.6893 | 18.7416 | 81.8972 | 10.4765 | 76.5172 | 12.1029 | 80.1255 | 10.1957 | 35.2496 | 94.0999 | 19.6542 | 36.5603 | 111.6756 | 10.834 | 33.005 | 109.1313 | 11.5383 | 77.9416 | 17.4845 | 82.1317 | 12.7599 | 86.5206 | 0.73495 | 19.6259 | 1.0264 | 0.079592 | -38.1237 | 3.1232 | 163.43 | 49.5 | -1.0663 | 0.40819 | 0.34089 | 0.38548 | -0.22837 | -0.50079 | 0.82566 | -0.43041 | -0.57177 | -0.14985 | -1.9774 | -0.95621 | -0.8317 | -0.34204
42810.4449 | 421 | 18.3632 | 18.5125 | 18.5163 | 18.4969 | 17.8104 | 16.4148 | 14.4698 | 16.6068 | 17.1026 | 17.1865 | 17.1856 | 16.7048 | 15.7088 | 14.3237 | 14.7287 | 14.7855 | 15.3803 | 13.2566 | 13.7456 | 15.2578 |  |  |  | 16.5128 | 16.0217 | 18.9287 | 109.1928 | 97.43 | 126.0077 | 17.0016 | 16.2694 | 17.5261 | 16.7465 | 16.1716 | 18.0215 | 35.151 | 124.2589 |  | 62.9248 | 95.1895 | 94.7114 | 82.5506 |  | 6.841 | 7.3408 | 6.6544 | 7.5625 | 8.0648 | 9.8727 | 45.1708 | 5.6831 | 7.0051 | 4.8244 | 7.7074 | 8.4979 | 41.3929 | 46.3903 | 42.306 | 14.9427 |  |  | -0.45911 | -0.044597 | 0.1359 | 0.091338 | -0.08066 | 0.13425 | 0.38366 | 0.40922 | 0.4509 | -0.14997 | -0.22563 | -0.00053883 | -0.00060783 | 1.411 | 15.7957 | 16.6506 | 17.1928 | 17.5148 | 17.4577 | 16.4084 | 14.7455 | 16.7801 | 17.1233 | 17.4112 | 17.4545 | 17.1578 | 16.319 | 14.5144 | 43.8538 | 19.5026 | 28.7253 | 19.0199 | 16.6228 | 22.33 | 14.8724 | 15.8305 | 15.4829 | 15.3808 | 14.264 | 14.5773 | 15.5478 |  |  |  | 30.7005 | 112.5494 | 89.1795 | 59.6575 | 0.22129 | 0.17787 | 35.514 |  |  | 11.0208 |  |  | 16.8954 | 16.3963 | 21.0753 | 16.3395 | 15.7447 | 17.1998 | 108.5474 | 133.9389 | 90.0025 | 91.0223 | 68.5939 |  | 34.5571 | 73.4343 | 34.9077 | 63.7759 | 40.5014 | 100.9832 |  | 55.7109 |  |  | 14.2554 | 16.1432 | 39.9211 | [6 empty] | 46.4084 |  |  | 29.09 |  |  | 15.2076 | 40.2329 | 149.9385 | 8.7344 | 36.2024 | 101.3555 | 10.3533 | 34.1439 | 112.8603 | 18.7632 | 82.0554 | 10.5037 | 76.6974 | 12.1121 | 80.2757 | 10.2003 | 35.4259 | 94.2516 | 19.6769 | 36.7178 | 112.3416 | 10.8532 | 33.2764 | 109.4292 | 11.5331 | 78.007 | 17.5016 | 82.3051 | 12.7696 | 86.848 | 0.81507 | 19.6233 | 1.0301 | 0.080171 | -38.1027 | 3.1233 | 157.9 | 49.26 | -0.9434 | -0.24648 | 0.43027 | 0.35274 | -0.33297 | 0.42957 | 0.72619 | -0.43715 | -0.55955 | -0.097768 | -1.9593 | -1.149 | -0.8044 | -0.32105
42810.4449 | 422 | 18.3625 | 18.505 | 18.5092 | 18.497 | 17.8061 | 16.4165 | 14.4739 | 16.6067 | 17.1 | 17.1892 | 17.1863 | 16.7028 | 15.7099 | 14.3279 | 14.731 | 14.79 | 15.3869 | 13.2614 | 13.758 | 15.2655 |  |  |  | 16.5166 | 16.0264 | 18.9477 | 109.5727 | 97.6788 | 126.1918 | 16.9962 | 16.2618 | 17.5356 | 16.7495 | 16.1692 | 18.037 | 35.3464 | 124.1855 |  | 63.1158 | 95.4981 | 94.8875 | 83.1053 |  | 6.836 | 7.3414 | 6.6502 | 7.5527 | 8.0721 | 9.9213 | 44.7133 | 5.7577 | 7.0088 | 4.8361 | 7.706 | 8.5094 | 41.3991 | 46.4015 | 42.3227 | 14.943 |  |  | -0.43545 | 0.001403 | 0.033392 | 0.22473 | -0.12074 | -0.12794 | 0.32846 | 0.25414 | 0.56066 | -0.16088 | -0.29697 | -0.00058976 | -0.00057169 | 1.3787 | 15.7952 | 16.6463 | 17.1936 | 17.5198 | 17.4662 | 16.4115 | 14.7461 | 16.7837 | 17.1238 | 17.4178 | 17.4483 | 17.1598 | 16.3342 | 14.5126 | 41.9874 | 18.481 | 28.8218 | 19.0815 | 17.112 | 22.4312 | 14.9463 | 15.823 | 15.4825 | 15.3788 | 14.2536 | 14.5804 | 15.5558 |  |  |  | 30.8033 | 112.9851 | 89.4718 | 58.9194 | 0.22615 | -0.085042 | 35.5647 |  |  | 11.0248 |  |  | 16.8921 | 16.3992 | 21.113 | 16.3356 | 15.7545 | 17.2164 | 108.7403 | 134.4558 | 90.238 | 91.2147 | 68.0085 |  | 34.6815 | 73.4445 | 35.0109 | 63.0139 | 40.7007 | 100.9053 |  | 55.8976 |  |  | 14.2617 | 16.1495 | 39.7164 | [6 empty] | 46.2697 |  |  | 29.1765 |  |  | 15.2215 | 40.2164 | 149.8282 | 8.7381 | 36.2851 | 101.5708 | 10.3674 | 34.4107 | 112.9528 | 18.7973 | 82.2236 | 10.5467 | 76.8854 | 12.1326 | 80.4965 | 10.2132 | 35.8166 | 94.4209 | 19.7236 | 36.8894 | 113.0433 | 10.8708 | 33.4892 | 109.8783 | 11.5366 | 78.1015 | 17.5241 | 82.3714 | 12.7918 | 87.1191 | 0.79851 | 19.6182 | 1.0339 | 0.080403 | -38.1734 | 3.1233 | 158.82 | 48.33 | -0.91898 | 0.043718 | 0.21328 | 0.5533 | -0.40742 | -0.41939 | 0.67198 | -0.41661 | -0.55628 | -0.069667 | -1.7401 | -1.1511 | -0.81308 | -0.29704
42810.4449 | 423 | 18.3653 | 18.5081 | 18.5154 | 18.498 | 17.8105 | 16.4172 | 14.4721 | 16.6142 | 17.1019 | 17.1918 | 17.1876 | 16.704 | 15.7058 | 14.3312 | 14.725 | 14.7886 | 15.3885 | 13.257 | 13.7543 | 15.2685 |  |  |  | 16.5128 | 16.0268 | 18.9611 | 110.0031 | 98.0122 | 126.9074 | 17.0021 | 16.2678 | 17.5532 | 16.749 | 16.1772 | 18.0473 | 35.5604 | 123.7288 |  | 63.3145 | 95.7714 | 95.1049 | 85.118 |  | 6.8384 | 7.3384 | 6.6526 | 7.5512 | 8.0891 | 9.9691 | 44.1909 | 5.7936 | 7.02 | 4.915 | 7.7192 | 8.5199 | 41.4061 | 46.409 | 42.3404 | 14.9376 |  |  | -0.6707 | -0.10702 | 0.12079 | 0.25036 | -0.1582 | 0.10336 | 0.52559 | 0.64052 | -0.2228 | -1.7325 | -0.25365 | -0.00060126 | -0.00064397 | 1.4684 | 15.7901 | 16.6489 | 17.1891 | 17.5125 | 17.4602 | 16.408 | 14.7398 | 16.7849 | 17.1205 | 17.4059 | 17.4455 | 17.1483 | 16.3255 | 14.5149 | 38.9086 | 17.3668 | 26.7898 | 18.9032 | 17.3427 | 22.494 | 14.985 | 15.8256 | 15.484 | 15.3807 | 14.2641 | 14.5886 | 15.569 |  |  |  | 30.9168 | 113.3596 | 89.6051 | 58.3932 | 0.23081 | -0.1718 | 35.7376 |  |  | 11.0146 |  |  | 16.8953 | 16.3938 | 21.1415 | 16.3333 | 15.753 | 17.2314 | 109.0138 | 134.8448 | 90.4712 | 91.4525 | 68.1368 |  | 34.8244 | 73.7367 | 35.1278 | 62.8351 | 40.9787 | 101.6407 |  | 56.0872 |  |  | 14.2717 | 16.1624 | 39.4925 | [6 empty] | 46.2322 |  |  | 29.3543 |  |  | 15.2471 | 40.2166 | 150.3613 | 8.7561 | 36.2342 | 101.7964 | 10.372 | 34.7065 | 113.2011 | 18.8482 | 82.3462 | 10.5618 | 77.1705 | 12.1575 | 80.6936 | 10.213 | 36.1537 | 94.582 | 19.7922 | 36.9775 | 113.3331 | 10.8911 | 33.6142 | 110.2237 | 11.5378 | 78.3101 | 17.5337 | 82.4555 | 12.8115 | 87.3631 | 0.84107 | 19.6149 | 1.0362 | 0.080207 | -38.1727 | 3.1233 | 152.34 | 45.99 | -1.1415 | -0.38182 | 0.40564 | 0.58399 | -0.4664 | 0.377 | 0.85011 | -0.41526 | -0.56038 | -0.055027 | -1.3907 | -0.92083 | -0.86162 | -0.27855
42810.4449 | 424 | 18.3543 | 18.5065 | 18.5134 | 18.4961 | 17.8083 | 16.4123 | 14.4638 | 16.6093 | 17.0971 | 17.1894 | 17.1816 | 16.7021 | 15.7032 | 14.3223 | 14.7135 | 14.7812 | 15.3754 | 13.251 | 13.7493 | 15.2791 |  |  |  | 16.5048 | 16.021 | 18.9771 | 110.4151 | 98.3446 | 128.0682 | 16.994 | 16.2673 | 17.5599 | 16.7422 | 16.1715 | 18.0559 | 35.761 | 122.7317 |  | 63.5018 | 96.0192 | 95.4232 | 84.8581 |  | 6.8482 | 7.3469 | 6.6416 | 7.543 | 8.0729 | 9.9886 | 43.816 | 5.7057 | 7.013 | 5.084 | 7.723 | 8.514 | 41.4127 | 46.4158 | 42.3469 | 14.939 |  |  | -0.39208 | 0.25965 | 0.060332 | 0.07557 | -0.10892 | -0.00966 | 0.52428 | 0.49662 | -0.27651 | -0.59768 | -0.10522 | -0.00061769 | -0.00061276 | 1.3835 | 15.7934 | 16.6432 | 17.1972 | 17.5115 | 17.4604 | 16.4097 | 14.7532 | 16.7782 | 17.1083 | 17.4132 | 17.4476 | 17.1562 | 16.3214 | 14.5148 | 37.5092 | 16.4938 | 24.3405 | 18.3495 | 16.8744 | 22.5713 | 15.0162 | 15.8204 | 15.4785 | 15.3787 | 14.2575 | 14.586 | 15.5713 |  |  |  | 31.0242 | 113.6592 | 89.6521 | 58.3513 | 0.36615 | -0.0061858 | 36.0132 |  |  | 11.0248 |  |  | 16.8857 | 16.4006 | 21.171 | 16.3331 | 15.752 | 17.2462 | 109.2932 | 135.1757 | 90.6321 | 91.6451 | 67.9557 |  | 34.9611 | 74.0955 | 35.2462 | 61.6717 | 41.2022 | 101.8762 |  | 56.2449 |  |  | 14.2969 | 16.1807 | 39.4368 | [6 empty] | 45.5124 |  |  | 29.5434 |  |  | 15.2513 | 40.4329 | 151.1135 | 8.7567 | 36.3393 | 101.9731 | 10.3756 | 34.895 | 113.3253 | 18.8798 | 82.4571 | 10.5312 | 77.3637 | 12.17 | 80.8855 | 10.2146 | 36.4 | 94.7528 | 19.8297 | 37.0516 | 113.6009 | 10.917 | 33.926 | 110.5243 | 11.5336 | 78.6284 | 17.5365 | 82.6709 | 12.8283 | 87.5746 | 0.6893 | 19.6138 | 1.039 | 0.080808 | -38.0564 | 3.1233 | 163.98 | 45.41 | -0.87407 | 0.59473 | 0.28668 | 0.32085 | -0.387 | -0.11525 | 0.84908 | -0.40553 | -0.56626 | -0.014929 | -1.2261 | -0.64506 | -0.84749 | -0.27372
42810.445 | 425 | 18.3649 | 18.5139 | 18.5172 | 18.502 | 17.808 | 16.4153 | 14.4799 | 16.6143 | 17.1013 | 17.1957 | 17.1904 | 16.711 | 15.7092 | 14.3334 | 14.7201 | 14.7819 | 15.3718 | 13.249 | 13.7464 | 15.28 |  |  |  | 16.5052 | 16.0205 | 19.0014 | 110.8745 | 98.5556 | 128.7994 | 17.0024 | 16.2616 | 17.573 | 16.7423 | 16.1723 | 18.0824 | 35.9358 | 122.4115 |  | 63.6579 | 96.2393 | 95.7807 | 83.6407 |  | 6.8396 | 7.347 | 6.6472 | 7.5453 | 8.0778 | 10.0427 | 44.2585 | 5.6526 | 7.0269 | 5.2082 | 7.7246 | 8.5282 | 41.41 | 46.4226 | 42.3509 | 14.9285 |  |  | -0.5005 | 0.052659 | 0.020248 | 0.26087 | -0.040576 | 0.18879 | 0.31203 | 0.42039 | -0.58807 | 0.04913 | -0.2157 | -0.00054869 | -0.00058483 | 1.2666 | 15.8007 | 16.6476 | 17.1945 | 17.5184 | 17.4659 | 16.4087 | 14.7434 | 16.79 | 17.1196 | 17.4146 | 17.4585 | 17.1571 | 16.3259 | 14.5159 | 37.7018 | 17.2022 | 25.4147 | 18.2309 | 16.2011 | 22.6783 | 15.0657 | 15.8222 | 15.4671 | 15.3743 | 14.253 | 14.5834 | 15.5863 |  |  |  | 31.1295 | 113.8729 | 89.5519 | 58.705 | 0.33555 | 0.032772 | 36.222 |  |  | 11.0193 |  |  | 16.884 | 16.3985 | 21.2008 | 16.34 | 15.7477 | 17.2502 | 109.4887 | 135.7619 | 90.7629 | 91.7994 | 67.8268 |  | 35.0764 | 74.7666 | 35.3677 | 62.5406 | 41.447 | 101.4844 |  | 56.3789 |  |  | 14.314 | 16.2016 | 39.6194 | [6 empty] | 45.477 |  |  | 29.6713 |  |  | 15.2713 | 40.8258 | 151.5069 | 8.7678 | 36.7787 | 102.157 | 10.3872 | 35.1802 | 113.4501 | 18.8973 | 82.6047 | 10.5295 | 77.5285 | 12.1737 | 81.406 | 10.2171 | 36.6532 | 95.0192 | 19.8594 | 37.175 | 113.9506 | 10.94 | 34.3284 | 111.0784 | 11.5499 | 78.9477 | 17.539 | 82.9247 | 12.8262 | 87.8453 | 0.93198 | 19.6109 | 1.0436 | 0.081539 | -38.0497 | 3.1233 | 176.74 | 46.65 | -0.98845 | 0.26784 | 0.16608 | 0.59614 | -0.23623 | 0.50956 | 0.6551 | -0.39798 | -0.58072 | -0.030538 | -1.235 | -0.75864 | -0.80765 | -0.27994
42810.445 | 426 | 18.366 | 18.5053 | 18.502 | 18.493 | 17.8072 | 16.4143 | 14.4782 | 16.6018 | 17.1019 | 17.1935 | 17.1821 | 16.708 | 15.7142 | 14.3225 | 14.7181 | 14.7838 | 15.3766 | 13.2545 | 13.754 | 15.2933 |  |  |  | 16.5135 | 16.0317 | 19.0286 | 111.3188 | 98.6804 | 129.5526 | 17.0031 | 16.2676 | 17.587 | 16.737 | 16.1745 | 18.0969 | 36.0728 | 122.4238 |  | 63.8558 | 96.3684 | 96.1085 | 83.9987 |  | 6.8295 | 7.3494 | 6.6576 | 7.5367 | 8.0973 | 10.229 | 45.8006 | 5.6348 | 7.0282 | 5.2468 | 7.7307 | 8.5258 | 41.3986 | 46.4248 | 42.3555 | 14.9163 |  |  | -0.41114 | -0.005169 | 0.1773 | 0.040086 | 0.02382 | 0.014652 | 0.55976 | 0.4999 | -0.75153 | 0.17564 | -0.2308 | -0.00061769 | -0.00062097 | 1.3443 | 15.7949 | 16.6492 | 17.1858 | 17.5169 | 17.4596 | 16.4076 | 14.7476 | 16.7829 | 17.1162 | 17.4149 | 17.4565 | 17.1557 | 16.325 | 14.5201 | 37.8196 | 16.7565 | 25.8715 | 18.9456 | 16.6705 | 22.7744 | 15.1218 | 15.8132 | 15.4686 | 15.3768 | 14.2545 | 14.5863 | 15.5953 |  |  |  | 31.2313 | 113.9689 | 89.4177 | 58.8929 | 0.49844 | -0.15618 | 36.2856 |  |  | 11.0227 |  |  | 16.8845 | 16.401 | 21.226 | 16.3295 | 15.7528 | 17.2664 | 109.7616 | 136.0921 | 90.9107 | 91.9667 | 68.3474 |  | 35.1709 | 75.3459 | 35.47 | 62.2509 | 41.6891 | 101.4643 |  | 56.5574 |  |  | 14.328 | 16.2123 | 39.6222 | [6 empty] | 46.193 |  |  | 29.7566 |  |  | 15.297 | 41.044 | 152.1486 | 8.7781 | 37.2497 | 102.4536 | 10.3947 | 35.4674 | 113.7562 | 18.9055 | 82.7815 | 10.548 | 77.8093 | 12.1797 | 82.1866 | 10.2188 | 37.052 | 95.1724 | 19.8971 | 37.2279 | 114.2244 | 10.9476 | 34.5178 | 111.5914 | 11.5627 | 79.2554 | 17.5454 | 83.0971 | 12.8195 | 88.0217 | 0.77058 | 19.607 | 1.047 | 0.082147 | -38.0753 | 3.1233 | 184.85 | 45.52 | -0.89671 | -0.083914 | 0.49146 | 0.23368 | 0.18106 | 0.142 | 0.87771 | -0.40918 | -0.59329 | -0.014055 | -1.2369 | -0.80285 | -0.81287 | -0.28169
42810.445 | 427 | 18.3522 | 18.5079 | 18.5058 | 18.4981 | 17.8021 | 16.4108 | 14.4687 | 16.6026 | 17.089 | 17.1913 | 17.1816 | 16.7001 | 15.7131 | 14.3225 | 14.7131 | 14.781 | 15.3773 | 13.2584 | 13.7597 | 15.3061 |  |  |  | 16.5139 | 16.0381 | 19.0445 | 111.7707 | 98.8753 | 130.1839 | 16.9993 | 16.2611 | 17.6079 | 16.7407 | 16.1698 | 18.1141 | 36.2707 | 123.0299 |  | 64.106 | 96.4745 | 96.4136 | 85.9669 |  | 6.8307 | 7.3564 | 6.6651 | 7.5541 | 8.1461 | 10.4069 | 47.3094 | 5.3467 | 7.0302 | 5.0734 | 7.7424 | 8.5372 | 41.3917 | 46.4218 | 42.3563 | 14.9146 |  |  | -0.45122 | 0.026371 | 0.09056 | 0.24707 | -0.086576 | -0.081284 | 0.47762 | 0.24626 | -0.47598 | -2.1492 | -0.14436 | -0.00061769 | -0.00063904 | 1.3769 | 15.7892 | 16.6442 | 17.1817 | 17.5103 | 17.4595 | 16.4016 | 14.7453 | 16.7754 | 17.1151 | 17.415 | 17.451 | 17.1556 | 16.3203 | 14.517 | 37.9371 | 16.7023 | 25.1867 | 18.3216 | 16.2863 | 22.8725 | 15.1625 | 15.8113 | 15.4628 | 15.3787 | 14.2469 | 14.5923 | 15.5947 |  |  |  | 31.332 | 113.9394 | 89.3261 | 59.0145 | 0.25735 | 0.036536 | 36.3977 |  |  | 11.0332 |  |  | 16.8839 | 16.4071 | 21.266 | 16.3452 | 15.7527 | 17.2864 | 109.93 | 136.7827 | 91.138 | 92.181 | 68.9755 |  | 35.3031 | 76.0129 | 35.6034 | 59.8897 | 41.9216 | 102.129 |  | 56.7969 |  |  | 14.3361 | 16.2161 | 39.7876 | [6 empty] | 45.7412 |  |  | 29.7753 |  |  | 15.3214 | 41.1684 | 152.36 | 8.7949 | 37.3767 | 102.6789 | 10.406 | 35.3922 | 113.9996 | 18.9133 | 83.124 | 10.5574 | 78.093 | 12.1915 | 82.564 | 10.2207 | 37.4455 | 95.3953 | 19.9269 | 37.2523 | 114.5982 | 10.9585 | 34.507 | 111.7815 | 11.5809 | 79.4786 | 17.5399 | 83.1833 | 12.8146 | 88.429 | 0.81449 | 19.6045 | 1.0507 | 0.081756 | -38.07 | 3.1233 | 174.05 | 45.44 | -0.94014 | 0.18954 | 0.35124 | 0.58017 | -0.34529 | -0.33457 | 0.81102 | -0.42208 | -0.60722 | 0.059641 | -1.2384 | -0.72202 | -0.86072 | -0.28162
42810.445 | 428 | 18.3508 | 18.5084 | 18.5087 | 18.4931 | 17.8004 | 16.4204 | 14.475 | 16.6069 | 17.1043 | 17.1925 | 17.1933 | 16.7054 | 15.7127 | 14.3283 | 14.7117 | 14.772 | 15.3734 | 13.2493 | 13.7565 | 15.305 |  |  |  | 16.4988 | 16.0349 | 19.0636 | 112.1233 | 99.1403 | 129.9181 | 16.9875 | 16.2561 | 17.6103 | 16.7276 | 16.1663 | 18.128 | 36.4292 | 122.7377 |  | 64.3166 | 96.6384 | 96.8488 | 83.7374 |  | 6.8257 | 7.3603 | 6.6637 | 7.5547 | 8.1873 | 10.3925 | 47.4015 | 5.2059 | 7.0352 | 4.953 | 7.7533 | 8.5349 | 41.3883 | 46.4222 | 42.3574 | 14.9057 |  |  | -0.40194 | -0.19245 | 0.16284 | -0.032198 | -0.009036 | -0.081284 | 0.33832 | 0.45653 | -0.50225 | -0.95162 | -0.20258 | -0.00065054 | -0.00064233 | 1.2756 | 15.7925 | 16.6353 | 17.1862 | 17.5119 | 17.4623 | 16.405 | 14.7474 | 16.778 | 17.1149 | 17.4159 | 17.4493 | 17.1621 | 16.3263 | 14.5197 | 38.8278 | 17.4084 | 27.0389 | 18.7571 | 16.3955 | 22.9792 | 15.228 | 15.8175 | 15.4732 | 15.3775 | 14.259 | 14.5949 | 15.6195 |  |  |  | 31.4467 | 114.1686 | 89.3039 | 59.4985 | 0.16132 | 0.058367 | 36.5197 |  |  | 11.0345 |  |  | 16.877 | 16.4048 | 21.2985 | 16.3355 | 15.754 | 17.2995 | 110.1829 | 137.5188 | 91.3626 | 92.4371 | 70.1658 |  | 35.4257 | 76.3137 | 35.7223 | 59.2467 | 42.1017 | 102.6165 |  | 56.9667 |  |  | 14.3564 | 16.2457 | 40.2531 | [6 empty] | 46.3224 |  |  | 29.8211 |  |  | 15.3495 | 41.4419 | 153.12 | 8.8268 | 37.3007 | 102.8336 | 10.4177 | 35.3461 | 114.0872 | 18.9425 | 83.3953 | 10.5692 | 78.3999 | 12.2088 | 82.6984 | 10.2315 | 37.4417 | 95.6366 | 19.9601 | 37.4604 | 115.1289 | 10.9614 | 34.6598 | 112.1095 | 11.6047 | 79.622 | 17.5359 | 83.2908 | 12.8234 | 88.8558 | 0.86072 | 19.6025 | 1.0526 | 0.08067 | -38.0637 | 3.1233 | 199.75 | 46.63 | -0.88702 | -0.51203 | 0.47101 | -0.20944 | -0.11155 | -0.33456 | 0.68255 | -0.45092 | -0.61148 | 0.083785 | -1.3249 | -0.92018 | -0.79332 | -0.29115
42810.445 | 429 | 18.3491 | 18.509 | 18.5041 | 18.497 | 17.8022 | 16.419 | 14.4668 | 16.5984 | 17.0965 | 17.1892 | 17.1898 | 16.7075 | 15.7095 | 14.3251 | 14.7077 | 14.7752 | 15.3742 | 13.2448 | 13.7543 | 15.3195 |  |  |  | 16.5068 | 16.0363 | 19.0848 | 112.4163 | 99.36 | 129.5574 | 16.9854 | 16.2594 | 17.6252 | 16.7359 | 16.1699 | 18.1444 | 36.5528 | 122.547 |  | 64.5069 | 96.8942 | 97.2518 | 81.9536 |  | 6.826 | 7.3566 | 6.6701 | 7.5601 | 8.2194 | 10.4086 | 47.1362 | 5.1594 | 7.0307 | 4.7788 | 7.7535 | 8.5439 | 41.3928 | 46.4317 | 42.367 | 14.8943 |  |  | -0.49656 | -0.17076 | 0.10502 | 0.16691 | 0.031048 | 0.18616 | 0.20098 | 0.69835 | -0.55343 | -0.65706 | -0.30869 | -0.00060947 | -0.00062754 | 1.2368 | 15.7923 | 16.6506 | 17.1873 | 17.5168 | 17.4606 | 16.4102 | 14.7515 | 16.7833 | 17.1281 | 17.4162 | 17.4553 | 17.1664 | 16.3312 | 14.5187 | 38.3761 | 17.6144 | 28.0775 | 19.4376 | 17.1939 | 23.0545 | 15.2977 | 15.8144 | 15.4724 | 15.3699 | 14.2543 | 14.604 | 15.6285 |  |  |  | 31.5623 | 114.3308 | 89.2993 | 59.9015 | 0.46968 | -0.012961 | 36.5383 |  |  | 11.0233 |  |  | 16.8759 | 16.4074 | 21.3273 | 16.3355 | 15.7568 | 17.3119 | 110.529 | 138.2542 | 91.5116 | 92.6892 | 71.4496 |  | 35.5464 | 76.9958 | 35.8435 | 60.2203 | 42.2964 | 102.7284 |  | 57.1201 |  |  | 14.3852 | 16.2725 | 40.968 | [6 empty] | 46.9049 |  |  | 29.9305 |  |  | 15.3758 | 41.5312 | 154.0415 | 8.8645 | 37.5902 | 102.9768 | 10.4238 | 35.6901 | 114.2335 | 18.9786 | 83.5043 | 10.5749 | 78.6779 | 12.2291 | 82.8978 | 10.2607 | 37.5039 | 95.7483 | 19.9991 | 37.7433 | 115.5858 | 10.9734 | 34.9179 | 112.543 | 11.637 | 79.6983 | 17.5463 | 83.3865 | 12.8388 | 89.2391 | 0.80621 | 19.6009 | 1.0554 | 0.081018 | -38.1096 | 3.1233 | 214.72 | 45.62 | -0.98548 | -0.48232 | 0.37824 | 0.47684 | 0.20678 | 0.50633 | 0.5261 | -0.48243 | -0.62625 | 0.06353 | -1.2659 | -1.0275 | -0.7395 | -0.29838
42810.445 | 430 | 18.3497 | 18.5025 | 18.5062 | 18.4969 | 17.8004 | 16.4161 | 14.4746 | 16.6017 | 17.0941 | 17.1894 | 17.1843 | 16.704 | 15.7083 | 14.324 | 14.6947 | 14.7764 | 15.3688 | 13.2444 | 13.7532 | 15.3215 |  |  |  | 16.5059 | 16.0275 | 19.1058 | 112.5401 | 99.477 | 128.6445 | 16.9856 | 16.2608 | 17.6422 | 16.7332 | 16.1684 | 18.1634 | 36.6928 | 122.1065 |  | 64.7002 | 97.2136 | 97.5541 | 82.5025 |  | 6.8228 | 7.363 | 6.6769 | 7.5646 | 8.2423 | 10.4935 | 47.1775 | 5.1623 | 7.0401 | 4.6641 | 7.7557 | 8.5453 | 41.3781 | 46.4278 | 42.3625 | 14.8859 |  |  | -0.22254 | -0.040653 | 0.070848 | -0.050598 | 0.1467 | -0.039228 | 0.46908 | 0.72792 | -0.26756 | -0.85888 | -0.261 | -0.00055526 | -0.00059633 | 1.3102 | 15.7892 | 16.6501 | 17.1947 | 17.5154 | 17.4613 | 16.4091 | 14.7511 | 16.7848 | 17.1218 | 17.4109 | 17.4529 | 17.1643 | 16.3259 | 14.5159 | 38.1309 | 17.7312 | 27.5544 | 19.7002 | 17.2648 | 23.1375 | 15.3491 | 15.8126 | 15.4759 | 15.3887 | 14.2603 | 14.6092 | 15.6442 |  |  |  | 31.6794 | 114.7637 | 89.7831 | 59.6136 | 0.36291 | 0.13214 | 36.5831 |  |  | 11.0252 |  |  | 16.8771 | 16.4168 | 21.3544 | 16.3313 | 15.7507 | 17.3232 | 110.7816 | 138.8102 | 91.6531 | 92.8009 | 72.8436 |  | 35.7214 | 77.6327 | 35.9872 | 60.438 | 42.5759 | 102.3474 |  | 57.3064 |  |  | 14.3818 | 16.3075 | 41.3552 | [6 empty] | 46.5139 |  |  | 30.0195 |  |  | 15.3943 | 41.8682 | 154.1613 | 8.8737 | 37.9497 | 103.1872 | 10.4361 | 36.0263 | 114.4481 | 19.0097 | 83.6318 | 10.5683 | 78.9086 | 12.2228 | 83.088 | 10.2802 | 37.7739 | 95.9252 | 20.0227 | 37.978 | 115.8683 | 10.9808 | 34.9399 | 112.9191 | 11.6621 | 79.8979 | 17.5643 | 83.6967 | 12.8504 | 89.5197 | 0.67139 | 19.5979 | 1.0591 | 0.083254 | -38.095 | 3.1233 | 193.43 | 45.79 | -0.65899 | -0.23534 | 0.31068 | -0.26255 | 0.44954 | -0.23246 | 0.80385 | -0.51512 | -0.63899 | 0.067239 | -1.229 | -0.96335 | -0.74992 | -0.28639
42810.445 | 431 | 18.3458 | 18.5031 | 18.4997 | 18.4932 | 17.7975 | 16.4078 | 14.4656 | 16.6005 | 17.093 | 17.1861 | 17.1859 | 16.7 | 15.7016 | 14.3243 | 14.7042 | 14.7693 | 15.3699 | 13.2446 | 13.7563 | 15.3301 |  |  |  | 16.5068 | 16.0379 | 19.1258 | 112.6093 | 99.61 | 128.3319 | 16.9924 | 16.2679 | 17.6618 | 16.7398 | 16.1798 | 18.1844 | 36.8638 | 122.2639 |  | 64.9212 | 97.5332 | 97.8059 | 83.7703 |  | 6.8296 | 7.3525 | 6.6785 | 7.5744 | 8.245 | 10.5659 | 47.5599 | 5.0667 | 7.035 | 4.6432 | 7.7615 | 8.5472 | 41.3872 | 46.4421 | 42.3538 | 14.8724 |  |  | -0.46173 | 0.023743 | 0.22067 | 0.30293 | 0.36946 | 0.098764 | 0.39943 | 0.73975 | -0.51431 | -0.10969 | -0.17914 | -0.0006144 | -0.00063576 | 1.3176 | 15.7818 | 16.6419 | 17.1776 | 17.5063 | 17.4554 | 16.3938 | 14.7441 | 16.7717 | 17.1142 | 17.4053 | 17.4484 | 17.1619 | 16.3237 | 14.5078 | 38.4874 | 17.8628 | 27.9251 | 20.0416 | 17.5902 | 23.2221 | 15.4006 | 15.8106 | 15.4679 | 15.3837 | 14.2555 | 14.607 | 15.6519 |  |  |  | 31.7827 | 115.3497 | 90.4705 | 59.4118 | 0.28207 | -0.15806 | 36.5902 |  |  | 11.0331 |  |  | 16.8836 | 16.4128 | 21.3923 | 16.3373 | 15.7598 | 17.3386 | 111.2723 | 138.9549 | 91.8447 | 92.9594 | 73.1518 |  | 35.8439 | 77.1039 | 36.0943 | 59.3885 | 42.8086 | 103.7114 |  | 57.4954 |  |  | 14.3974 | 16.3352 | 41.6459 | [6 empty] | 45.992 |  |  | 30.0938 |  |  | 15.4141 | 42.2833 | 154.1845 | 8.9043 | 37.8644 | 103.3853 | 10.4673 | 35.9935 | 114.6556 | 19.0433 | 83.8989 | 10.5956 | 79.1321 | 12.2423 | 83.269 | 10.3176 | 37.7799 | 96.164 | 20.0646 | 38.1964 | 116.2998 | 11.0028 | 34.9575 | 113.0986 | 11.6953 | 80.1405 | 17.5809 | 84.2891 | 12.8688 | 90.0922 | 0.63403 | 19.5947 | 1.063 | 0.083138 | -38.0102 | 3.1233 | 190.72 | 46.57 | -0.94885 | 0.17985 | 0.54829 | 0.6424 | 0.7135 | 0.3689 | 0.74187 | -0.51946 | -0.62061 | 0.10452 | -1.2587 | -0.99854 | -0.77923 | -0.27725
42810.445 | 432 | 18.3462 | 18.5076 | 18.5039 | 18.4982 | 17.7994 | 16.4103 | 14.4744 | 16.6036 | 17.0978 | 17.1939 | 17.1863 | 16.7038 | 15.7112 | 14.3287 | 14.6932 | 14.7596 | 15.3704 | 13.2324 | 13.7591 | 15.3464 |  |  |  | 16.5026 | 16.0321 | 19.1406 | 112.6089 | 99.7403 | 127.0025 | 16.9792 | 16.2593 | 17.6614 | 16.7316 | 16.1776 | 18.1945 | 37.0278 | 122.8871 |  | 65.1263 | 97.8029 | 98.0541 | 84.0599 |  | 6.8305 | 7.349 | 6.6779 | 7.5826 | 8.2748 | 10.5819 | 48.7308 | 5.002 | 7.0271 | 4.7335 | 7.7713 | 8.5607 | 41.3838 | 46.4515 | 42.3585 | 14.8663 |  |  | -0.47684 | 0.052659 | 0.085304 | -0.10514 | 0.25512 | 0.06788 | 0.36854 | 0.2962 | -0.331 | -1.915 | -0.18689 | -0.00058976 | -0.00062426 | 1.2614 | 15.7899 | 16.6343 | 17.1726 | 17.512 | 17.4512 | 16.3943 | 14.7376 | 16.7772 | 17.1147 | 17.4012 | 17.4413 | 17.1563 | 16.3221 | 14.5045 | 37.9486 | 17.8747 | 27.6973 | 19.9516 | 17.9088 | 23.304 | 15.4506 | 15.8134 | 15.4709 | 15.3841 | 14.262 | 14.6149 | 15.671 |  |  |  | 31.8926 | 116.1154 | 91.4116 | 59.5431 | -0.032975 | 0.02976 | 36.5647 |  |  | 11.0229 |  |  | 16.8762 | 16.4054 | 21.4153 | 16.3272 | 15.7556 | 17.3383 | 111.6205 | 139.4957 | 92.1642 | 93.275 | 73.1525 |  | 35.9608 | 76.7374 | 36.2012 | 58.8669 | 43.0292 | 105.4539 |  | 57.6712 |  |  | 14.3941 | 16.3669 | 41.8036 | [6 empty] | 45.7865 |  |  | 30.1821 |  |  | 15.4249 | 42.3032 | 154.1973 | 8.9333 | 37.6531 | 103.5479 | 10.4797 | 36.0118 | 114.7728 | 19.0689 | 84.0021 | 10.6093 | 79.3691 | 12.2422 | 83.4573 | 10.3548 | 37.5867 | 96.387 | 20.1059 | 38.3308 | 116.6612 | 11.0225 | 35.1714 | 113.4209 | 11.6925 | 80.319 | 17.5763 | 84.4468 | 12.8857 | 90.3408 | 0.75286 | 19.5915 | 1.0669 | 0.083479 | -38.1065 | 3.1233 | 189 | 44.97 | -0.96265 | 0.26784 | 0.34089 | -0.37845 | 0.59292 | 0.30584 | 0.71263 | -0.51545 | -0.60674 | 0.12671 | -1.1892 | -0.9674 | -0.78161 | -0.27713
42810.445 | 433 | 18.342 | 18.5049 | 18.5077 | 18.4947 | 17.8056 | 16.4154 | 14.4699 | 16.6054 | 17.0988 | 17.1889 | 17.1948 | 16.7023 | 15.7145 | 14.3305 | 14.6962 | 14.7602 | 15.358 | 13.2318 | 13.7547 | 15.3485 |  |  |  | 16.4972 | 16.0398 | 19.1615 | 112.8977 | 100.0781 | 128.8404 | 16.9788 | 16.2616 | 17.6813 | 16.7367 | 16.176 | 18.2117 | 37.2056 | 123.2831 |  | 65.3276 | 98.0122 | 98.3082 | 84.4502 |  | 6.8263 | 7.3543 | 6.6825 | 7.5854 | 8.2738 | 10.5876 | 48.6297 | 4.9918 | 7.029 | 4.8069 | 7.7734 | 8.5667 | 41.3803 | 46.4665 | 42.3681 | 14.8589 |  |  | -0.4545 | -0.23122 | -0.11709 | -0.23591 | 0.19927 | 0.19996 | 0.48485 | 0.46113 | -0.39969 | -0.82301 | -0.13721 | -0.00057662 | -0.00057826 | 1.3916 | 15.7876 | 16.6415 | 17.1816 | 17.5115 | 17.4549 | 16.4048 | 14.7412 | 16.7806 | 17.1115 | 17.4084 | 17.4494 | 17.1657 | 16.3152 | 14.5153 | 34.6547 | 17.2112 | 27.3354 | 19.6788 | 17.4928 | 23.323 | 15.4952 | 15.8055 | 15.4718 | 15.3862 | 14.2515 | 14.6158 | 15.6768 |  |  |  | 31.9962 | 116.6786 | 91.8728 | 59.7832 | 0.11391 | -0.069421 | 36.6959 |  |  | 11.0279 |  |  | 16.8784 | 16.4094 | 21.4499 | 16.3327 | 15.7509 | 17.3566 | 111.9722 | 140.405 | 92.5588 | 93.6349 | 73.4498 |  | 36.0931 | 76.6991 | 36.3357 | 58.8508 | 43.2068 | 106.2501 |  | 57.8617 |  |  | 14.3915 | 16.384 | 41.8399 | [6 empty] | 44.9856 |  |  | 30.1989 |  |  | 15.4394 | 42.1928 | 154.6233 | 8.9655 | 38.0744 | 103.8563 | 10.5004 | 36.3427 | 114.8866 | 19.0881 | 84.0659 | 10.619 | 79.6157 | 12.2409 | 83.9139 | 10.3734 | 37.7602 | 96.5197 | 20.1921 | 38.3701 | 116.8528 | 11.0464 | 35.4447 | 113.525 | 11.6955 | 80.5207 | 17.5748 | 84.7583 | 12.902 | 90.4492 | 0.6633 | 19.5889 | 1.0691 | 0.082292 | -38.1801 | 3.1233 | 193.25 | 45.78 | -0.94199 | -0.56124 | -0.39939 | -0.5669 | 0.52402 | 0.52492 | 0.81739 | -0.51914 | -0.60103 | 0.13337 | -0.82103 | -0.92199 | -0.78631 | -0.28026
42810.4451 | 434 | 18.3308 | 18.4918 | 18.4912 | 18.484 | 17.7955 | 16.3984 | 14.4664 | 16.5978 | 17.0849 | 17.1831 | 17.1793 | 16.6937 | 15.6993 | 14.3196 | 14.6971 | 14.768 | 15.37 | 13.2469 | 13.7746 | 15.3649 |  |  |  | 16.5047 | 16.0441 | 19.1967 | 113.2184 | 100.3911 | 128.5764 | 16.9793 | 16.2576 | 17.6905 | 16.7242 | 16.1723 | 18.2274 | 37.401 | 124.2918 |  | 65.5379 | 98.209 | 98.6104 | 85.569 |  | 6.8378 | 7.3573 | 6.6801 | 7.6096 | 8.2918 | 10.5723 | 48.4079 | 4.8929 | 7.0294 | 4.8604 | 7.7724 | 8.5693 | 41.3909 | 46.477 | 42.3723 | 14.8469 |  |  | -0.51956 | 0.11574 | 0.016964 | -0.03417 | 0.14539 | 0.21048 | 0.72207 | 0.4815 | -0.39191 | -0.25487 | -0.34147 | -0.00058319 | -0.00061604 | 1.4104 | 15.7854 | 16.6432 | 17.1808 | 17.5123 | 17.4593 | 16.4058 | 14.7473 | 16.7873 | 17.1154 | 17.4117 | 17.4477 | 17.1626 | 16.3218 | 14.5178 | 32.2175 | 16.4733 | 25.9606 | 19.1872 | 17.3457 | 23.3539 | 15.5317 | 15.8081 | 15.4746 | 15.3867 | 14.2569 | 14.6216 | 15.6904 |  |  |  | 32.1137 | 116.9428 | 92.4215 | 59.7544 | 0.27883 | -0.26778 | 36.6801 |  |  | 11.0339 |  |  | 16.8741 | 16.4138 | 21.4789 | 16.3281 | 15.755 | 17.3721 | 112.2826 | 140.8338 | 92.8539 | 93.9955 | 74.1112 |  | 36.2264 | 77.0807 | 36.4618 | 58.7763 | 43.3482 | 106.8978 |  | 58.0515 |  |  | 14.4059 | 16.3752 | 42.0508 | [6 empty] | 44.6121 |  |  | 30.2591 |  |  | 15.4631 | 42.3574 | 155.5028 | 9.0042 | 38.1519 | 104.0919 | 10.4983 | 36.5054 | 115.0843 | 19.1215 | 84.2241 | 10.6372 | 79.8171 | 12.2534 | 84.1766 | 10.3347 | 37.8034 | 96.5782 | 20.2184 | 38.5402 | 116.9301 | 11.0597 | 35.5037 | 113.844 | 11.7218 | 80.708 | 17.5659 | 85.1458 | 12.9187 | 90.6949 | 0.64674 | 19.5867 | 1.0715 | 0.082567 | -38.174 | 3.1233 | 187.52 | 46.11 | -1.0068 | 0.39708 | 0.15202 | -0.21576 | 0.44759 | 0.53854 | 0.99748 | -0.53292 | -0.60729 | 0.14038 | -0.54661 | -0.76498 | -0.81063 | -0.27544
42810.4451 | 435 | 18.3311 | 18.4932 | 18.4883 | 18.4843 | 17.8017 | 16.4047 | 14.4671 | 16.5997 | 17.0965 | 17.1921 | 17.1778 | 16.7026 | 15.7012 | 14.3164 | 14.6855 | 14.7612 | 15.3633 | 13.2444 | 13.7714 | 15.3775 |  |  |  | 16.4997 | 16.0421 | 19.2011 | 113.3231 | 100.5408 | 127.6765 | 16.9648 | 16.2478 | 17.6987 | 16.7239 | 16.1644 | 18.2404 | 37.5934 | 124.7539 |  | 65.7461 | 98.4393 | 98.8341 | 87.6054 |  | 6.8297 | 7.3659 | 6.6818 | 7.6202 | 8.3343 | 10.583 | 49.3706 | 4.8781 | 7.0331 | 4.9137 | 7.7819 | 8.5725 | 41.4027 | 46.4748 | 42.3742 | 14.8404 |  |  | -0.60038 | -0.033425 | -0.021804 | 0.055198 | -0.036636 | 0.21902 | 0.39417 | 0.53933 | -0.55985 | -0.57901 | -0.12211 | -0.00059305 | -0.00062426 | 1.3338 | 15.7857 | 16.6455 | 17.1791 | 17.5106 | 17.4579 | 16.4042 | 14.7452 | 16.787 | 17.1153 | 17.4112 | 17.4523 | 17.1597 | 16.3245 | 14.515 | 32.1867 | 15.7862 | 24.437 | 18.2763 | 16.7233 | 23.417 | 15.5525 | 15.8013 | 15.4704 | 15.3834 | 14.2608 | 14.6212 | 15.69 |  |  |  | 32.2127 | 117.3467 | 92.5163 | 59.8685 | 0.61251 | 0.073799 | 36.8703 |  |  | 11.04 |  |  | 16.877 | 16.4207 | 21.5166 | 16.3315 | 15.7603 | 17.3913 | 112.7607 | 141.1043 | 93.0821 | 94.2836 | 73.9649 |  | 36.3541 | 77.4446 | 36.5793 | 60.2021 | 43.5297 | 106.9415 |  | 58.2481 |  |  | 14.421 | 16.4097 | 42.6828 | [6 empty] | 44.2507 |  |  | 30.3111 |  |  | 15.4632 | 42.3994 | 155.7576 | 9.044 | 38.2022 | 104.253 | 10.4988 | 36.7392 | 115.2779 | 19.1409 | 84.3514 | 10.6598 | 80.0886 | 12.249 | 84.3674 | 10.3299 | 37.8914 | 96.6709 | 20.2071 | 38.8169 | 117.3403 | 11.0747 | 35.5515 | 114.1238 | 11.7662 | 80.8953 | 17.5746 | 85.2986 | 12.936 | 90.8943 | 0.79215 | 19.5826 | 1.0751 | 0.085628 | -38.1029 | 3.1233 | 186.17 | 45.47 | -1.0811 | -0.21339 | -0.17235 | 0.27423 | -0.22469 | 0.54936 | 0.737 | -0.52445 | -0.61334 | 0.10713 | -0.53581 | -0.59327 | -0.86054 | -0.27522
42810.4451 | 436 | 18.3231 | 18.4934 | 18.4943 | 18.4817 | 17.7943 | 16.4024 | 14.4644 | 16.6043 | 17.0894 | 17.1842 | 17.1887 | 16.7038 | 15.6974 | 14.3203 | 14.6903 | 14.7745 | 15.3728 | 13.245 | 13.7682 | 15.3934 |  |  |  | 16.5112 | 16.0535 | 19.2393 | 113.4121 | 100.5787 | 128.0484 | 16.9653 | 16.2469 | 17.72 | 16.7254 | 16.1693 | 18.2652 | 37.7926 | 125.5784 |  | 65.9604 | 98.636 | 99.0166 | 89.3205 |  | 6.8246 | 7.3703 | 6.6833 | 7.6222 | 8.3552 | 10.6038 | 49.4652 | 4.8401 | 7.0352 | 4.887 | 7.7843 | 8.5705 | 41.4133 | 46.4626 | 42.3757 | 14.8308 |  |  | -0.45779 | -0.001225 | 0.16153 | 0.12419 | 0.25972 | 0.24202 | 0.4244 | 0.16674 | -0.53436 | -0.20787 | -0.15231 | -0.00061604 | -0.0006029 | 1.3983 | 15.7775 | 16.6385 | 17.172 | 17.5057 | 17.4554 | 16.399 | 14.7379 | 16.7758 | 17.1082 | 17.4032 | 17.4479 | 17.1616 | 16.3233 | 14.5122 | 35.8899 | 17.4517 | 25.9392 | 17.8519 | 16.0346 | 23.5462 | 15.616 | 15.8032 | 15.4588 | 15.3754 | 14.2529 | 14.6224 | 15.702 |  |  |  | 32.3138 | 117.4889 | 92.5008 | 59.6161 | 0.42835 | 0.066271 | 37.0647 |  |  | 11.0486 |  |  | 16.8805 | 16.4328 | 21.549 | 16.3311 | 15.7654 | 17.4162 | 113.1528 | 141.1745 | 93.3165 | 94.6066 | 72.3099 |  | 36.4787 | 77.7439 | 36.7105 | 61.3224 | 43.7292 | 106.8325 |  | 58.4552 |  |  | 14.4482 | 16.4177 | 42.373 | [6 empty] | 44.8418 |  |  | 30.302 |  |  | 15.4703 | 42.3971 | 155.7819 | 9.0795 | 38.4523 | 104.9251 | 10.498 | 37.1063 | 115.4562 | 19.1638 | 84.5283 | 10.6671 | 80.4889 | 12.2384 | 85.0345 | 10.3094 | 38.0788 | 96.961 | 20.2249 | 38.8691 | 117.7513 | 11.0896 | 35.7931 | 114.5336 | 11.8044 | 81.1119 | 17.5915 | 85.3825 | 12.9534 | 91.1521 | 0.85128 | 19.5796 | 1.0773 | 0.086323 | -37.9829 | 3.1233 | 188.87 | 46.07 | -0.94445 | -0.040852 | 0.46911 | 0.41134 | 0.59827 | 0.57751 | 0.76476 | -0.47418 | -0.61712 | 0.082989 | -0.93215 | -0.75277 | -0.9013 | -0.26474
42810.4451 | 437 | 18.3333 | 18.5019 | 18.5026 | 18.494 | 17.7979 | 16.4085 | 14.4671 | 16.6001 | 17.0925 | 17.1922 | 17.1925 | 16.7102 | 15.7082 | 14.3264 | 14.6896 | 14.771 | 15.3684 | 13.2368 | 13.7728 | 15.3961 |  |  |  | 16.5159 | 16.0558 | 19.262 | 113.642 | 100.65 | 128.5253 | 16.9606 | 16.2488 | 17.7257 | 16.7236 | 16.1674 | 18.2778 | 37.9611 | 125.5687 |  | 66.1592 | 98.8181 | 99.1831 | 89.2562 |  | 6.8127 | 7.3686 | 6.6837 | 7.6446 | 8.3614 | 10.6462 | 49.9845 | 4.825 | 7.031 | 4.7635 | 7.7895 | 8.578 | 41.429 | 46.4415 | 42.3918 | 14.8248 |  |  | -0.79029 | 0.047399 | -0.044148 | -0.02497 | 0.39838 | -0.18905 | 0.30546 | 0.29028 | -0.078408 | -1.2797 | -0.033688 | -0.00060947 | -0.00067683 | 1.3816 | 15.7914 | 16.6332 | 17.184 | 17.5088 | 17.454 | 16.4062 | 14.7418 | 16.782 | 17.1148 | 17.4103 | 17.4453 | 17.1627 | 16.3254 | 14.518 | 37.6302 | 17.9485 | 27.4456 | 18.8482 | 16.4002 | 23.6552 | 15.6853 | 15.8055 | 15.4663 | 15.3802 | 14.2509 | 14.6241 | 15.7094 |  |  |  | 32.4174 | 117.6813 | 92.663 | 59.4181 | 0.4324 | 0.055167 | 37.2607 |  |  | 11.049 |  |  | 16.8791 | 16.4345 | 21.5841 | 16.334 | 15.7663 | 17.4249 | 113.3579 | 141.2891 | 93.5854 | 94.8828 | 71.6618 |  | 36.6184 | 78.4244 | 36.8775 | 62.4978 | 43.933 | 108.3579 |  | 58.705 |  |  | 14.4683 | 16.417 | 42.1251 | [6 empty] | 44.5816 |  |  | 30.364 |  |  | 15.4912 | 42.7486 | 155.5676 | 9.097 | 38.704 | 105.2979 | 10.5215 | 37.1533 | 115.6618 | 19.2016 | 84.6881 | 10.6715 | 80.7813 | 12.2593 | 85.3559 | 10.3006 | 38.5018 | 97.2017 | 20.2481 | 38.8836 | 118.2501 | 11.1068 | 36.0065 | 114.8087 | 11.8389 | 81.2808 | 17.5937 | 85.5844 | 12.9643 | 91.3529 | 0.62132 | 19.5777 | 1.0803 | 0.085954 | -38.188 | 3.1233 | 173.85 | 45.76 | -1.2416 | 0.25412 | -0.24525 | -0.18444 | 0.741 | -0.51046 | 0.64885 | -0.45135 | -0.63026 | 0.05747 | -1.1128 | -0.91208 | -0.89368 | -0.2557
42810.4451 | 438 | 18.3363 | 18.497 | 18.5009 | 18.4918 | 17.8023 | 16.4085 | 14.471 | 16.5974 | 17.0936 | 17.1949 | 17.1917 | 16.7049 | 15.7146 | 14.3292 | 14.6862 | 14.7652 | 15.3643 | 13.2386 | 13.7685 | 15.403 |  |  |  | 16.5146 | 16.0533 | 19.2776 | 113.8956 | 100.8157 | 128.324 | 16.9544 | 16.2444 | 17.7331 | 16.7217 | 16.165 | 18.2965 | 38.1132 | 125.2371 |  | 66.3649 | 99.023 | 99.3841 | 89.4269 |  | 6.8147 | 7.3649 | 6.702 | 7.6454 | 8.3471 | 10.7693 | 50.92 | 4.8666 | 7.0297 | 4.7127 | 7.7893 | 8.5764 | 41.4385 | 46.4271 | 42.3977 | 14.8038 |  |  | -0.39471 | 0.13085 | 0.28704 | -0.17217 | 0.41283 | 0.24662 | 0.30546 | 0.54458 | -0.34073 | -0.33711 | -0.061307 | -0.00060947 | -0.00060619 | 1.2581 | 15.7803 | 16.6289 | 17.1779 | 17.5045 | 17.4471 | 16.3937 | 14.7334 | 16.7729 | 17.1141 | 17.4047 | 17.4424 | 17.1545 | 16.3173 | 14.5094 | 37.6992 | 18.5144 | 27.9035 | 18.8176 | 16.8551 | 23.7631 | 15.7472 | 15.7936 | 15.4655 | 15.3811 | 14.253 | 14.6255 | 15.718 |  |  |  | 32.5233 | 118.017 | 92.8445 | 59.2088 | 0.40221 | -0.11045 | 37.3073 |  |  | 11.0466 |  |  | 16.8756 | 16.4393 | 21.6207 | 16.3374 | 15.7665 | 17.4333 | 113.7307 | 141.432 | 93.9149 | 95.1161 | 72.0228 |  | 36.7469 | 78.4832 | 37.011 | 62.1078 | 44.0952 | 109.0937 |  | 58.9138 |  |  | 14.4778 | 16.438 | 41.8178 | [6 empty] | 44.8749 |  |  | 30.4307 |  |  | 15.5048 | 43.1231 | 155.512 | 9.0907 | 38.8718 | 105.4086 | 10.5459 | 36.9813 | 115.8764 | 19.2159 | 84.7926 | 10.6619 | 80.9563 | 12.2765 | 85.4278 | 10.3112 | 38.7736 | 97.311 | 20.2738 | 39.0108 | 118.9948 | 11.131 | 36.1747 | 115.0578 | 11.8717 | 81.3692 | 17.618 | 85.8444 | 12.9844 | 91.6089 | 0.79793 | 19.5754 | 1.0821 | 0.084376 | -38.179 | 3.1233 | 190.43 | 45.34 | -0.87727 | 0.42222 | 0.62534 | -0.4843 | 0.75449 | 0.58314 | 0.649 | -0.45695 | -0.62728 | 0.073981 | -1.1078 | -0.95574 | -0.89316 | -0.24625
42810.4451 | 439 | 18.3303 | 18.4931 | 18.4946 | 18.4861 | 17.7973 | 16.4025 | 14.4612 | 16.5931 | 17.0942 | 17.188 | 17.1868 | 16.7035 | 15.7089 | 14.3206 | 14.685 | 14.7576 | 15.3648 | 13.2309 | 13.7679 | 15.4084 |  |  |  | 16.5154 | 16.0441 | 19.2946 | 114.119 | 101.027 | 128.8154 | 16.9648 | 16.2514 | 17.7502 | 16.7282 | 16.1687 | 18.3119 | 38.2903 | 125.2464 |  | 66.5618 | 99.2696 | 99.5896 | 89.6182 |  | 6.8182 | 7.3572 | 6.6933 | 7.6288 | 8.3519 | 10.9551 | 52.4873 | 4.8682 | 7.0464 | 4.5934 | 7.7977 | 8.5842 | 41.4522 | 46.4201 | 42.4069 | 14.7968 |  |  | -0.50379 | 0.012575 | 0.15562 | -0.12945 | 0.44634 | -0.066172 | 0.19112 | 0.26202 | -0.56121 | -0.35998 | -0.037066 | -0.00061604 | -0.00063412 | 1.2844 | 15.7819 | 16.6331 | 17.1788 | 17.5059 | 17.4489 | 16.3976 | 14.7368 | 16.7771 | 17.1103 | 17.4114 | 17.447 | 17.1613 | 16.3153 | 14.5129 | 38.1575 | 19.4667 | 28.6504 | 18.9586 | 16.8184 | 23.8672 | 15.8024 | 15.7943 | 15.4617 | 15.3746 | 14.2488 | 14.6166 | 15.7326 |  |  |  | 32.6404 | 118.2315 | 92.9685 | 59.0958 | 0.28551 | 0.16809 | 37.3205 |  |  | 11.0583 |  |  | 16.8805 | 16.4416 | 21.6487 | 16.3345 | 15.7677 | 17.453 | 114.0234 | 141.4977 | 94.2924 | 95.4063 | 71.4654 |  | 36.8606 | 75.5808 | 37.1065 | 61.9742 | 44.3782 | 108.9996 |  | 59.1164 |  |  | 14.4774 | 16.4342 | 41.7939 | [6 empty] | 46.1896 |  |  | 30.4668 |  |  | 15.5157 | 43.4168 | 155.7143 | 9.0937 | 39.1167 | 105.6094 | 10.5688 | 37.2584 | 116.0249 | 19.2234 | 84.9662 | 10.6444 | 81.1119 | 12.2758 | 85.77 | 10.3122 | 38.8531 | 97.3077 | 20.3011 | 39.1251 | 119.5932 | 11.1464 | 36.3181 | 115.2634 | 11.8841 | 81.4119 | 17.673 | 86.0121 | 13.0004 | 91.9713 | 0.67852 | 19.5727 | 1.0857 | 0.084969 | -38.0582 | 3.1233 | 179.78 | 46.36 | -0.99171 | 0.13089 | 0.46043 | -0.41994 | 0.78477 | -0.30216 | 0.51352 | -0.43754 | -0.54336 | 0.087604 | -1.1465 | -1.0323 | -0.89234 | -0.2391
42810.4451 | 440 | 18.3329 | 18.498 | 18.5017 | 18.4888 | 17.7985 | 16.4042 | 14.4653 | 16.5964 | 17.0945 | 17.1985 | 17.1899 | 16.705 | 15.7083 | 14.3236 | 14.6838 | 14.7529 | 15.3629 | 13.2377 | 13.7668 | 15.4193 |  |  |  | 16.5074 | 16.0489 | 19.3148 | 114.4545 | 101.3852 | 130.2983 | 16.9665 | 16.2523 | 17.765 | 16.7297 | 16.1752 | 18.3338 | 38.4596 | 125.1819 |  | 66.7614 | 99.5393 | 99.7913 | 87.6366 |  | 6.8037 | 7.3514 | 6.6926 | 7.6067 | 8.3472 | 10.9468 | 53.3718 | 4.8625 | 7.0469 | 4.4875 | 7.8028 | 8.5822 | 41.4673 | 46.4129 | 42.4223 | 14.788 |  |  | -0.53205 | -0.018969 | 0.033392 | 0.02497 | 0.22753 | -0.20745 | -0.236 | 0.35731 | -0.53689 | -0.35515 | -0.091311 | -0.00060783 | -0.0005799 | 1.2425 | 15.7833 | 16.635 | 17.1832 | 17.5051 | 17.457 | 16.3997 | 14.7391 | 16.7822 | 17.1193 | 17.413 | 17.4467 | 17.1517 | 16.327 | 14.5205 | 37.0295 | 18.9337 | 28.3627 | 19.59 | 17.1629 | 23.924 | 15.8588 | 15.7967 | 15.4645 | 15.3861 | 14.2544 | 14.6308 | 15.7452 |  |  |  | 32.7442 | 118.5911 | 93.0656 | 59.3853 | -0.13103 | -0.36282 | 37.3386 |  |  | 11.0608 |  |  | 16.882 | 16.4442 | 21.6816 | 16.3295 | 15.7667 | 17.4661 | 114.2556 | 141.592 | 94.5719 | 95.6992 | 71.1717 |  | 37.0158 | 72.8469 | 37.2326 | 60.9903 | 44.6069 | 109.0997 |  | 59.3477 |  |  | 14.483 | 16.4391 | 42.2678 | [6 empty] | 46.6218 |  |  | 30.4834 |  |  | 15.5323 | 43.6098 | 156.0742 | 9.117 | 39.3242 | 105.9404 | 10.5925 | 37.679 | 116.4302 | 19.2503 | 85.2602 | 10.6393 | 81.3327 | 12.2779 | 86.4368 | 10.3186 | 38.9622 | 97.4425 | 20.3199 | 39.2601 | 119.8485 | 11.1694 | 36.3059 | 115.478 | 11.9013 | 81.5016 | 17.7255 | 86.0501 | 13.0107 | 92.3367 | 0.72108 | 19.5727 | 1.0885 | 0.085889 | -38.0937 | 3.1233 | 162.29 | 45.35 | -1.021 | -0.16075 | 0.21328 | 0.18444 | 0.5603 | -0.53501 | -0.57064 | -0.42402 | -0.46306 | 0.12295 | -1.0145 | -0.99376 | -0.83143 | -0.24359
42810.4451 | 441 | 18.3323 | 18.4905 | 18.4974 | 18.4889 | 17.8014 | 16.407 | 14.4639 | 16.6063 | 17.0932 | 17.193 | 17.1859 | 16.7052 | 15.7117 | 14.3364 | 14.6761 | 14.7556 | 15.3632 | 13.2409 | 13.7695 | 15.4293 |  |  |  | 16.5052 | 16.0541 | 19.3378 | 114.8762 | 101.7368 | 131.7394 | 16.9605 | 16.2489 | 17.7671 | 16.7181 | 16.1666 | 18.339 | 38.5728 | 125.5083 |  | 66.9436 | 99.8077 | 99.9882 | 87.3478 |  | 6.7951 | 7.3377 | 6.6974 | 7.6028 | 8.3289 | 10.9015 | 54.1149 | 4.9028 | 7.0399 | 4.5103 | 7.8075 | 8.5818 | 41.4593 | 46.4106 | 42.4284 | 14.7787 |  |  | -0.54716 | 0.15122 | 0.17927 | -0.11959 | 0.11582 | -0.0918 | 0.43688 | 0.74238 | -0.35357 | -0.429 | -0.12926 | -0.00058319 | -0.00066204 | 1.1834 | 15.7804 | 16.6364 | 17.1809 | 17.5072 | 17.4573 | 16.4027 | 14.7437 | 16.7755 | 17.1248 | 17.4106 | 17.4506 | 17.1553 | 16.3257 | 14.525 | 33.932 | 17.3748 | 25.5102 | 18.9929 | 17.1434 | 23.9289 | 15.881 | 15.8093 | 15.474 | 15.3944 | 14.2636 | 14.6434 | 15.7678 |  |  |  | 32.8568 | 119.0005 | 93.0355 | 59.5385 | 0.0071398 | -0.18234 | 37.3701 |  |  | 11.0658 |  |  | 16.8775 | 16.4429 | 21.7147 | 16.3339 | 15.7678 | 17.475 | 114.5136 | 141.9025 | 94.8791 | 95.995 | 71.7249 |  | 37.1351 | 74.0806 | 37.3647 | 60.5126 | 44.7912 | 108.4737 |  | 59.5673 |  |  | 14.4557 | 16.4358 | 42.5279 | [6 empty] | 46.3806 |  |  | 30.5243 |  |  | 15.5505 | 43.5681 | 156.3719 | 9.1358 | 39.349 | 106.1676 | 10.6132 | 37.6601 | 116.8498 | 19.2775 | 85.4324 | 10.6414 | 81.5605 | 12.2823 | 86.7527 | 10.3355 | 39.2188 | 97.7735 | 20.3356 | 39.518 | 120.0413 | 11.1881 | 36.1296 | 115.716 | 11.9197 | 81.6331 | 17.7733 | 86.2866 | 13.0226 | 92.5813 | 0.67775 | 19.5703 | 1.0912 | 0.086497 | -38.1096 | 3.1233 | 176.44 | 45.59 | -1.0373 | 0.45387 | 0.49417 | -0.40363 | 0.39971 | -0.35587 | 0.77633 | -0.43526 | -0.49276 | 0.14269 | -0.66982 | -0.67422 | -0.81949 | -0.24398
42810.4452 | 442 | 18.3219 | 18.4949 | 18.4937 | 18.4914 | 17.8 | 16.4118 | 14.465 | 16.5991 | 17.1001 | 17.1922 | 17.1862 | 16.7069 | 15.7202 | 14.3283 | 14.6716 | 14.7579 | 15.3596 | 13.2368 | 13.7747 | 15.4335 |  |  |  | 16.5001 | 16.0447 | 19.3576 | 115.3998 | 101.9397 | 133.6617 | 16.9595 | 16.257 | 17.7985 | 16.7296 | 16.1724 | 18.364 | 38.7429 | 125.7549 |  | 67.124 | 100.0214 | 100.2211 | 88.6098 |  | 6.7918 | 7.3305 | 6.6787 | 7.5954 | 8.3006 | 10.8328 | 54.0888 | 4.8505 | 7.0384 | 4.4799 | 7.8071 | 8.5943 | 41.4811 | 46.4053 | 42.447 | 14.7698 |  |  | -0.45976 | 0.12231 | 0.12933 | 0.00197 | 0.12764 | -0.2068 | 0.51442 | 1.1209 | -0.62465 | -1.4948 | -0.17457 | -0.00060126 | -0.00061933 | 1.0851 | 15.785 | 16.6358 | 17.1789 | 17.5143 | 17.458 | 16.4021 | 14.7433 | 16.7796 | 17.1232 | 17.4115 | 17.4529 | 17.1559 | 16.3264 | 14.5215 | 30.9691 | 16.6366 | 24.297 | 18.134 | 16.4622 | 23.9167 | 15.8933 | 15.8086 | 15.4709 | 15.3757 | 14.2536 | 14.6335 | 15.7703 |  |  |  | 32.956 | 119.5211 | 93.2798 | 59.6328 | -0.020211 | -0.24614 | 37.5012 |  |  | 11.0712 |  |  | 16.876 | 16.4375 | 21.7419 | 16.3256 | 15.7706 | 17.487 | 114.8399 | 142.206 | 95.1572 | 96.3443 | 71.075 |  | 37.244 | 75.1037 | 37.4733 | 59.7624 | 44.956 | 108.3326 |  | 59.7573 |  |  | 14.4156 | 16.448 | 42.5301 | [6 empty] | 47.1849 |  |  | 30.628 |  |  | 15.5699 | 43.4655 | 156.8527 | 9.1277 | 39.4874 | 106.2086 | 10.6167 | 37.5534 | 117.0722 | 19.2947 | 85.5242 | 10.6519 | 81.8157 | 12.2956 | 86.7789 | 10.3534 | 39.4648 | 98.1047 | 20.3658 | 39.6648 | 120.5267 | 11.1969 | 36.1942 | 115.9275 | 11.9541 | 81.7981 | 17.8267 | 86.6034 | 13.0291 | 92.8691 | 0.68795 | 19.5662 | 1.0923 | 0.084542 | -38.1412 | 3.1233 | 169.63 | 49.06 | -0.95308 | 0.40818 | 0.41973 | 0.051803 | 0.41958 | -0.53405 | 0.84231 | -0.41345 | -0.51743 | 0.1693 | -0.34204 | -0.53798 | -0.84865 | -0.24321
42810.4452 | 443 | 18.317 | 18.4844 | 18.4897 | 18.4859 | 17.7889 | 16.4103 | 14.4582 | 16.5931 | 17.094 | 17.1877 | 17.1818 | 16.7021 | 15.7078 | 14.3177 | 14.6772 | 14.7513 | 15.3587 | 13.2297 | 13.773 | 15.4459 |  |  |  | 16.5029 | 16.0461 | 19.3751 | 115.8828 | 102.0966 | 134.6261 | 16.9519 | 16.257 | 17.8073 | 16.7196 | 16.1691 | 18.372 | 38.946 | 125.4366 |  | 67.2898 | 100.2112 | 100.419 | 90.15 |  | 6.7949 | 7.3187 | 6.6718 | 7.5988 | 8.2677 | 10.7698 | 54.003 | 4.6364 | 7.0402 | 4.4672 | 7.8131 | 8.5989 | 41.5148 | 46.3992 | 42.4552 | 14.7623 |  |  | -0.58921 | -0.3587 | 0.00382 | 0.026942 | -0.51173 | -0.31456 | 0.30809 | 0.77523 | -0.55226 | -0.37509 | -0.11098 | -0.00058319 | -0.00059797 | 0.98543 | 15.7876 | 16.6314 | 17.1824 | 17.5104 | 17.4543 | 16.4005 | 14.7398 | 16.7868 | 17.1146 | 17.4119 | 17.4479 | 17.1587 | 16.3237 | 14.5196 | 27.7957 | 15.4034 | 22.5311 | 17.5771 | 15.8095 | 23.8868 | 15.9116 | 15.8154 | 15.4721 | 15.3902 | 14.2604 | 14.6502 | 15.7891 |  |  |  | 33.0754 | 120.1827 | 93.445 | 59.834 | -0.20782 | -0.43961 | 37.5797 |  |  | 11.0793 |  |  | 16.876 | 16.4516 | 21.7856 | 16.3179 | 15.7712 | 17.5058 | 115.0756 | 142.5004 | 95.3626 | 96.6381 | 70.271 |  | 37.3525 | 74.536 | 37.5814 | 59.3012 | 45.1526 | 107.9065 |  | 59.9349 |  |  | 14.3695 | 16.4437 | 42.5131 | [6 empty] | 47.0482 |  |  | 30.7114 |  |  | 15.5944 | 43.6852 | 157.5751 | 9.1044 | 39.9047 | 106.2242 | 10.6242 | 37.752 | 117.3263 | 19.2965 | 85.6431 | 10.682 | 82.0781 | 12.2994 | 86.7822 | 10.3705 | 39.83 | 98.4565 | 20.3915 | 39.6914 | 121.0222 | 11.2012 | 36.3387 | 116.1499 | 11.9841 | 82.0684 | 17.8555 | 86.8708 | 13.0423 | 93.0604 | 0.78714 | 19.5664 | 1.0961 | 0.08544 | -38.1055 | 3.1233 | 167.19 | 48.82 | -1.0802 | -0.69899 | 0.072134 | 0.19157 | -0.84001 | -0.65859 | 0.65178 | -0.38736 | -0.49792 | 0.18901 | 0.0070719 | -0.33964 | -0.88439 | -0.2447
42810.4452 | 444 | 18.3228 | 18.4874 | 18.4973 | 18.4862 | 17.8009 | 16.4066 | 14.4654 | 16.5994 | 17.0943 | 17.1901 | 17.1909 | 16.7016 | 15.7149 | 14.3288 | 14.6799 | 14.7602 | 15.3659 | 13.2389 | 13.7799 | 15.4596 |  |  |  | 16.5103 | 16.0571 | 19.4087 | 116.2872 | 102.4386 | 134.8745 | 16.9499 | 16.2491 | 17.8203 | 16.7232 | 16.1705 | 18.392 | 39.156 | 125.8084 |  | 67.4733 | 100.398 | 100.6122 | 89.3527 |  | 6.7859 | 7.3176 | 6.6655 | 7.5911 | 8.239 | 10.7404 | 54.5913 | 4.3252 | 7.0259 | 4.432 | 7.8037 | 8.602 | 41.5398 | 46.3956 | 42.4601 | 14.7437 |  |  | -0.47684 | 0.046087 | -0.036264 | 0.083454 | -0.04912 | -0.72066 | -0.017184 | 1.1215 | -0.87471 | -0.60524 | -0.21967 | -0.00057662 | -0.00062262 | 1.1528 | 15.7898 | 16.6297 | 17.1826 | 17.5021 | 17.4532 | 16.3961 | 14.7381 | 16.7751 | 17.1181 | 17.4108 | 17.4503 | 17.1544 | 16.3169 | 14.5194 | 25.2727 | 14.3573 | 19.9433 | 16.8447 | 15.1667 | 23.8574 | 15.9095 | 15.81 | 15.4702 | 15.3901 | 14.2604 | 14.6584 | 15.8059 |  |  |  | 33.1891 | 120.8035 | 93.5376 | 59.8405 | -0.0068396 | -0.28717 | 37.753 |  |  | 11.0785 |  |  | 16.8758 | 16.4503 | 21.8185 | 16.3169 | 15.7622 | 17.5173 | 115.2465 | 142.6569 | 95.5475 | 96.8146 | 70.4724 |  | 37.4701 | 73.9665 | 37.7214 | 59.0048 | 45.3346 | 107.9991 |  | 60.1431 |  |  | 14.3558 | 16.4317 | 42.5474 | [6 empty] | 46.2414 |  |  | 30.7979 |  |  | 15.6053 | 44.0246 | 157.9626 | 9.0944 | 40.12 | 106.3215 | 10.6448 | 37.9584 | 117.5508 | 19.3057 | 85.9272 | 10.7527 | 82.2838 | 12.3105 | 86.8719 | 10.3898 | 40.2493 | 98.7281 | 20.4183 | 39.8437 | 121.2633 | 11.223 | 36.4774 | 116.2505 | 12.0215 | 82.3746 | 17.8457 | 87.258 | 13.0541 | 93.2712 | 0.76865 | 19.5633 | 1.0987 | 0.086055 | -38.0794 | 3.1234 | 150.56 | 48.9 | -0.97207 | 0.25055 | -0.22225 | 0.33716 | -0.26024 | -0.9968 | -0.15392 | -0.38889 | -0.47726 | 0.20363 | 0.28396 | -0.052353 | -0.85496 | -0.24098
42810.4452 | 445 | 18.3166 | 18.4815 | 18.4887 | 18.4793 | 17.7925 | 16.3957 | 14.4609 | 16.6002 | 17.0901 | 17.188 | 17.1875 | 16.7025 | 15.704 | 14.3303 | 14.668 | 14.7552 | 15.3633 | 13.2356 | 13.78 | 15.4704 |  |  |  | 16.4973 | 16.0608 | 19.4236 | 116.6284 | 102.711 | 135.6355 | 16.95 | 16.257 | 17.8423 | 16.7213 | 16.1804 | 18.415 | 39.3514 | 125.614 |  | 67.6537 | 100.6114 | 100.8661 | 89.1486 |  | 6.7844 | 7.3237 | 6.6652 | 7.5771 | 8.2151 | 10.7537 | 54.6277 | 4.2295 | 7.03 | 4.302 | 7.8055 | 8.6041 | 41.5808 | 46.4064 | 42.4774 | 14.7385 |  |  | -0.74298 | 0.073027 | 0.25287 | 0.031542 | -0.20354 | -1.4816 | -0.28857 | 0.84554 | -0.45866 | -0.613 | -0.19285 | -0.00058976 | -0.00064726 | 1.3248 | 15.7912 | 16.639 | 17.1795 | 17.5112 | 17.4632 | 16.3912 | 14.7362 | 16.7803 | 17.111 | 17.4116 | 17.448 | 17.1529 | 16.3275 | 14.5092 | 23.8027 | 13.8376 | 18.0432 | 15.6501 | 14.3871 | 23.822 | 15.8952 | 15.8046 | 15.4703 | 15.3823 | 14.2593 | 14.6524 | 15.8119 |  |  |  | 33.29 | 121.2071 | 93.8368 | 59.8154 | -0.12901 | -0.29827 | 38.0178 |  |  | 11.0819 |  |  | 16.874 | 16.4531 | 21.8546 | 16.3244 | 15.7678 | 17.5343 | 115.3281 | 142.8124 | 95.7598 | 97.0248 | 70.8988 |  | 37.6052 | 74.2704 | 37.8703 | 59.0111 | 45.5291 | 107.2551 |  | 60.3213 |  |  | 14.3736 | 16.452 | 42.5835 | [6 empty] | 46.4089 |  |  | 30.8218 |  |  | 15.6266 | 44.0207 | 157.9017 | 9.0875 | 40.1404 | 106.4209 | 10.656 | 38.0846 | 117.6647 | 19.3076 | 86.0711 | 10.8184 | 82.4218 | 12.3247 | 87.1017 | 10.4056 | 40.4123 | 98.9983 | 20.4465 | 39.949 | 121.5429 | 11.2435 | 36.7446 | 116.61 | 12.0603 | 82.5866 | 17.8482 | 87.7673 | 13.0779 | 93.5175 | 0.85321 | 19.5608 | 1.1009 | 0.084962 | -38.1492 | 3.1233 | 183.94 | 50.44 | -1.2145 | 0.31539 | 0.58689 | 0.20728 | -0.52976 | -1.4293 | -0.63078 | -0.39607 | -0.48055 | 0.21029 | 0.44315 | 0.1571 | -0.84251 | -0.23682
42810.4452 | 446 | 18.3072 | 18.4782 | 18.4838 | 18.4782 | 17.7891 | 16.3976 | 14.458 | 16.5902 | 17.0886 | 17.1792 | 17.1779 | 16.7015 | 15.701 | 14.3259 | 14.6668 | 14.7431 | 15.3534 | 13.2264 | 13.7769 | 15.4726 |  |  |  | 16.5018 | 16.0627 | 19.4469 | 117.0536 | 102.9248 | 136.75 | 16.9427 | 16.2478 | 17.8545 | 16.7144 | 16.1696 | 18.4329 | 39.5284 | 125.2479 |  | 67.8323 | 100.7932 | 101.1155 | 89.1869 |  | 6.7791 | 7.3146 | 6.64 | 7.5356 | 8.139 | 10.644 | 53.3908 | 4.3497 | 7.0179 | 4.1889 | 7.7982 | 8.6077 | 41.6205 | 46.4308 | 42.4768 | 14.7284 |  |  | -0.46962 | -0.013713 | 0.1037 | 0.041398 | -0.50713 | -0.14502 | -0.14532 | 1.067 | -0.32458 | -0.57838 | -0.037066 | -0.00058319 | -0.00062426 | 1.278 | 15.7889 | 16.6363 | 17.1827 | 17.5095 | 17.453 | 16.3985 | 14.7427 | 16.7822 | 17.1144 | 17.4138 | 17.4487 | 17.1593 | 16.3289 | 14.5184 | 21.964 | 13.3579 | 16.6938 | 14.4137 | 13.4424 | 23.7563 | 15.8704 | 15.8041 | 15.4662 | 15.3869 | 14.2592 | 14.6543 | 15.8147 |  |  |  | 33.3923 | 121.6146 | 94.2081 | 59.5701 | -0.19445 | -0.30072 | 38.1937 |  |  | 11.0855 |  |  | 16.87 | 16.449 | 21.8873 | 16.3198 | 15.7725 | 17.5488 | 115.5058 | 143.0419 | 95.9995 | 97.2822 | 71.9348 |  | 37.7189 | 75.0933 | 38.0008 | 58.0478 | 45.7086 | 106.4212 |  | 60.5035 |  |  | 14.4051 | 16.4674 | 42.6696 | [6 empty] | 46.1139 |  |  | 30.8272 |  |  | 15.6548 | 43.8816 | 157.6553 | 9.095 | 40.4887 | 106.5327 | 10.6619 | 38.3932 | 117.6811 | 19.2976 | 86.1604 | 10.8712 | 82.5887 | 12.3342 | 87.2924 | 10.4207 | 40.5545 | 99.1194 | 20.4847 | 40.0064 | 121.9605 | 11.2681 | 37.0423 | 117.0103 | 12.0994 | 82.7688 | 17.8604 | 88.0594 | 13.1016 | 93.6492 | 0.77751 | 19.5593 | 1.1022 | 0.083565 | -38.1642 | 3.1233 | 170.01 | 48.69 | -0.96689 | -0.13667 | 0.37584 | 0.23746 | -0.83604 | -0.44708 | -0.44754 | -0.42091 | -0.49889 | 0.24335 | 0.63975 | 0.30414 | -0.83743 | -0.2265
42810.4452 | 447 | 18.3054 | 18.4829 | 18.4814 | 18.474 | 17.7884 | 16.401 | 14.4537 | 16.5895 | 17.0832 | 17.175 | 17.1689 | 16.6999 | 15.6969 | 14.3182 | 14.6575 | 14.7473 | 15.3501 | 13.2437 | 13.7867 | 15.4946 |  |  |  | 16.5103 | 16.0742 | 19.4781 | 117.4212 | 103.3196 | 136.4299 | 16.9482 | 16.2545 | 17.866 | 16.7193 | 16.1736 | 18.4551 | 39.702 | 124.5669 |  | 68.0275 | 100.9377 | 101.3588 | 87.5313 |  | 6.7803 | 7.3143 | 6.6186 | 7.5149 | 8.1007 | 10.5948 | 52.8043 | 4.596 | 7.0263 | 4.2207 | 7.8022 | 8.6045 | 41.6667 | 46.4585 | 42.479 | 14.7173 |  |  | -0.59118 | 0.015203 | 0.015648 | -0.16165 | -0.149 | -0.60041 | -0.11904 | 0.74238 | -0.34443 | 1.8542 | -0.18311 | -0.00055362 | -0.0005799 | 1.1814 | 15.8001 | 16.6372 | 17.1853 | 17.5091 | 17.4506 | 16.4036 | 14.7407 | 16.7782 | 17.1261 | 17.4197 | 17.4535 | 17.162 | 16.3235 | 14.513 | 20.1255 | 12.704 | 15.2597 | 13.3229 | 12.7343 | 23.6914 | 15.8605 | 15.8048 | 15.4705 | 15.3936 | 14.2574 | 14.6595 | 15.8355 |  |  |  | 33.5001 | 121.9077 | 94.6058 | 59.3629 | -0.14704 | -0.39745 | 38.3981 |  |  | 11.0931 |  |  | 16.8758 | 16.4536 | 21.9194 | 16.3221 | 15.7724 | 17.5674 | 115.6532 | 143.5793 | 96.2004 | 97.5193 | 72.234 |  | 37.867 | 75.7986 | 38.1614 | 58.4948 | 45.8757 | 106.5084 |  | 60.7138 |  |  | 14.4225 | 16.5057 | 42.9517 | [6 empty] | 47.895 |  |  | 30.9274 |  |  | 15.6647 | 44.0711 | 158.415 | 9.0875 | 40.4737 | 106.5065 | 10.6659 | 38.8328 | 117.5311 | 19.3134 | 86.3876 | 10.9132 | 82.8044 | 12.3347 | 87.6315 | 10.4488 | 40.726 | 99.1466 | 20.5291 | 40.0385 | 122.719 | 11.2899 | 37.2547 | 117.1678 | 12.1378 | 82.9732 | 17.8667 | 88.2027 | 13.1276 | 93.7212 | 0.84993 | 19.5567 | 1.1061 | 0.086178 | -38.0917 | 3.1232 | 174.1 | 49.36 | -1.0844 | 0.1439 | 0.14599 | -0.46924 | -0.45313 | -0.90961 | -0.40501 | -0.4241 | -0.51293 | 0.2368 | 0.83644 | 0.46233 | -0.78542 | -0.21705
42810.4452 | 448 | 18.3154 | 18.4821 | 18.486 | 18.4785 | 17.7888 | 16.3996 | 14.4627 | 16.5971 | 17.0862 | 17.1836 | 17.1871 | 16.706 | 15.7102 | 14.324 | 14.6652 | 14.7491 | 15.3475 | 13.2407 | 13.7808 | 15.5033 |  |  |  | 16.5067 | 16.0757 | 19.5024 | 117.6625 | 103.9175 | 137.2137 | 16.9434 | 16.2517 | 17.877 | 16.7095 | 16.1696 | 18.4682 | 39.8193 | 125.7696 |  | 68.2408 | 101.0875 | 101.5925 | 87.3599 |  | 6.7685 | 7.312 | 6.6077 | 7.5122 | 8.0687 | 10.535 | 53.5253 | 4.8342 | 7.0195 | 4.3541 | 7.7999 | 8.6032 | 41.7045 | 46.4497 | 42.4835 | 14.7089 |  |  | -0.51496 | 0.005343 | -0.004064 | 0.042714 | 0.46277 | -0.81331 | -0.22878 | 0.70229 | -0.35474 | -0.99714 | 0.0074429 | -0.00060126 | -0.00059962 | 1.2136 | 15.7967 | 16.64 | 17.1924 | 17.5113 | 17.4639 | 16.4039 | 14.7414 | 16.7793 | 17.123 | 17.4155 | 17.4532 | 17.1585 | 16.3235 | 14.5145 | 18.4268 | 12.2162 | 13.7235 | 12.4843 | 12.2621 | 23.6166 | 15.8353 | 15.808 | 15.4665 | 15.3879 | 14.2506 | 14.6643 | 15.8385 |  |  |  | 33.6132 | 122.1548 | 94.8946 | 59.1072 | -0.073698 | -0.41289 | 38.5903 |  |  | 11.0955 |  |  | 16.8786 | 16.4624 | 21.9593 | 16.3211 | 15.7762 | 17.5834 | 115.6922 | 144.0207 | 96.3603 | 97.6746 | 71.9574 |  | 37.989 | 75.698 | 38.275 | 58.9765 | 46.0301 | 107.6209 |  | 60.9001 |  |  | 14.4328 | 16.4939 | 43.1439 | [6 empty] | 47.7941 |  |  | 30.945 |  |  | 15.7095 | 44.4989 | 159.1102 | 9.086 | 40.6263 | 106.697 | 10.6797 | 39.2122 | 117.7778 | 19.3369 | 86.5428 | 10.9269 | 83.0571 | 12.3497 | 87.9399 | 10.459 | 40.7385 | 99.1671 | 20.546 | 39.9673 | 123.2678 | 11.2999 | 37.5717 | 117.4066 | 12.1622 | 83.2304 | 17.9296 | 88.2501 | 13.1412 | 93.8676 | 0.87535 | 19.5543 | 1.1083 | 0.086945 | -38.1172 | 3.1232 | 170.18 | 49.99 | -1.0131 | 0.085309 | -0.074401 | 0.24121 | 0.79849 | -1.0586 | -0.56142 | -0.41219 | -0.5062 | 0.22885 | 1.0164 | 0.63009 | -0.77658 | -0.20606
42810.4452 | 449 | 18.312 | 18.487 | 18.4884 | 18.4887 | 17.8022 | 16.4044 | 14.4648 | 16.6037 | 17.0943 | 17.1807 | 17.1877 | 16.7051 | 15.7092 | 14.3306 | 14.6708 | 14.7523 | 15.3653 | 13.2366 | 13.7892 | 15.5192 |  |  |  | 16.51 | 16.0795 | 19.5135 | 117.9769 | 104.2585 | 136.9629 | 16.9455 | 16.2539 | 17.8998 | 16.7165 | 16.174 | 18.4895 | 40.001 | 128.0947 |  | 68.5109 | 101.309 | 101.8514 | 88.7907 |  | 6.764 | 7.3059 | 6.5981 | 7.5057 | 8.0409 | 10.5111 | 54.778 | 4.9903 | 7.0197 | 4.5632 | 7.8061 | 8.6053 | 41.7362 | 46.445 | 42.4954 | 14.6975 |  |  | -0.45582 | 0.004687 | 0.096476 | 0.14719 | 0.1513 | -0.32573 | -0.55536 | 0.48216 | -0.2086 | -0.12983 | -0.11754 | -0.00057662 | -0.00062262 | 1.1506 | 15.8001 | 16.6413 | 17.1889 | 17.5079 | 17.4681 | 16.4051 | 14.7412 | 16.7861 | 17.1279 | 17.4177 | 17.4536 | 17.1557 | 16.3256 | 14.5211 | 18.7084 | 12.2958 | 12.804 | 11.676 | 11.6764 | 23.5772 | 15.808 | 15.8113 | 15.4752 | 15.401 | 14.2565 | 14.6731 | 15.8549 |  |  |  | 33.717 | 122.31 | 95.0133 | 59.0415 | 0.11188 | -0.29018 | 38.5855 |  |  | 11.0979 |  |  | 16.8765 | 16.4646 | 21.993 | 16.3249 | 15.7771 | 17.5997 | 115.8134 | 144.3157 | 96.4822 | 97.7573 | 72.5528 |  | 38.1153 | 75.5015 | 38.384 | 59.1987 | 46.2736 | 107.4633 |  | 61.0713 |  |  | 14.4379 | 16.5283 | 43.4925 | [6 empty] | 47.7586 |  |  | 30.9041 |  |  | 15.7454 | 44.8447 | 160.4382 | 9.1132 | 40.932 | 106.7388 | 10.6884 | 39.2006 | 118.1217 | 19.3771 | 86.705 | 10.9506 | 83.3915 | 12.3646 | 88.0905 | 10.4841 | 40.5926 | 99.3888 | 20.591 | 40.0707 | 123.4944 | 11.324 | 37.8536 | 117.5136 | 12.1797 | 83.4403 | 17.9692 | 88.7591 | 13.1597 | 94.0478 | 0.79909 | 19.554 | 1.1088 | 0.08591 | -38.1005 | 3.1232 | 152.85 | 48.73 | -0.95283 | 0.0799 | 0.3625 | 0.44776 | 0.45655 | -0.66988 | -0.87469 | -0.42436 | -0.49696 | 0.23124 | 0.98053 | 0.72908 | -0.81002 | -0.20067
42810.4452 | 450 | 18.3076 | 18.4843 | 18.4934 | 18.4908 | 17.7984 | 16.3996 | 14.4548 | 16.5935 | 17.0865 | 17.1772 | 17.1852 | 16.7027 | 15.7121 | 14.3358 | 14.6591 | 14.7433 | 15.3551 | 13.2366 | 13.7807 | 15.5251 |  |  |  | 16.501 | 16.0674 | 19.5346 | 118.1622 | 104.5596 | 136.4143 | 16.9406 | 16.2536 | 17.9091 | 16.7109 | 16.1748 | 18.5029 | 40.1877 | 128.6759 |  | 68.7317 | 101.5387 | 102.0772 | 88.3465 |  | 6.7519 | 7.2932 | 6.58 | 7.4727 | 7.9958 | 10.5855 | 55.8221 | 4.9228 | 7.019 | 4.6744 | 7.8082 | 8.6088 | 41.7635 | 46.4342 | 42.5013 | 14.687 |  |  | -0.58396 | -0.13134 | -0.07306 | -0.70771 | 0.08296 | -0.58661 | -0.19395 | 0.68061 | 0.00994 | -0.073812 | -0.24848 | -0.00057169 | -0.00059469 | 1.0083 | 15.7996 | 16.6351 | 17.179 | 17.5081 | 17.4587 | 16.4047 | 14.7426 | 16.7855 | 17.116 | 17.4182 | 17.4484 | 17.1546 | 16.3226 | 14.5181 | 20.0443 | 13.0885 | 13.7269 | 11.2536 | 11.0677 | 23.5673 | 15.7976 | 15.8156 | 15.4753 | 15.4004 | 14.2585 | 14.6767 | 15.8681 |  |  |  | 33.8259 | 122.822 | 95.0331 | 59.4085 | 0.2067 | -0.23316 | 38.538 |  |  | 11.0946 |  |  | 16.8751 | 16.4703 | 22.0293 | 16.328 | 15.7745 | 17.6117 | 115.9597 | 144.6466 | 96.5776 | 97.8033 | 72.8722 |  | 38.2505 | 75.2383 | 38.5089 | 58.9588 | 46.512 | 106.8935 |  | 61.222 |  |  | 14.4441 | 16.5668 | 43.4927 | [6 empty] | 47.4521 |  |  | 30.9573 |  |  | 15.7664 | 44.9339 | 160.569 | 9.1138 | 40.991 | 106.8715 | 10.6912 | 39.2531 | 118.5113 | 19.3736 | 87.1575 | 10.9892 | 83.7543 | 12.349 | 88.3033 | 10.4947 | 40.7475 | 99.5138 | 20.637 | 40.3873 | 123.7455 | 11.3438 | 37.7816 | 117.7837 | 12.1334 | 83.607 | 17.9826 | 89.4099 | 13.1698 | 94.2891 | 0.93448 | 19.5524 | 1.113 | 0.087177 | -38.2002 | 3.1232 | 137.75 | 49.84 | -1.0778 | -0.42294 | -0.31545 | -0.98179 | 0.33811 | -0.89908 | -0.51697 | -0.42855 | -0.48533 | 0.24629 | 0.83094 | 0.62531 | -0.79119 | -0.20713
42810.4453 | 451 | 18.3121 | 18.4804 | 18.4937 | 18.4849 | 17.7933 | 16.4015 | 14.4641 | 16.5936 | 17.0945 | 17.1859 | 17.1895 | 16.7013 | 15.7066 | 14.336 | 14.6516 | 14.741 | 15.3497 | 13.2301 | 13.7851 | 15.5363 |  |  |  | 16.5017 | 16.0704 | 19.5529 | 118.3686 | 104.9207 | 137.9749 | 16.9456 | 16.2448 | 17.9293 | 16.7118 | 16.1758 | 18.5254 | 40.3115 | 128.4898 |  | 68.9066 | 101.7874 | 102.2552 | 86.4213 |  | 6.7556 | 7.295 | 6.5794 | 7.456 | 7.9574 | 10.6057 | 56.7593 | 4.8706 | 7.0207 | 4.7931 | 7.8144 | 8.6062 | 41.7752 | 46.4138 | 42.494 | 14.6759 |  |  | -0.6753 | -0.14973 | 0.11684 | -0.36207 | -0.043864 | 0.20325 | 0.17535 | 0.45653 | -0.59643 | -0.19969 | -0.3218 | -0.00062262 | -0.00062262 | 0.97966 | 15.7934 | 16.633 | 17.1755 | 17.5039 | 17.4563 | 16.3988 | 14.7357 | 16.7772 | 17.1112 | 17.4154 | 17.4417 | 17.1554 | 16.328 | 14.5056 | 22.7104 | 13.8206 | 14.3142 | 11.2338 | 10.7299 | 23.5885 | 15.7868 | 15.8132 | 15.4742 | 15.3942 | 14.2538 | 14.679 | 15.8736 |  |  |  | 33.9307 | 123.2302 | 95.0629 | 59.7168 | 0.37688 | -0.1575 | 38.5213 |  |  | 11.0989 |  |  | 16.8788 | 16.4706 | 22.0655 | 16.3204 | 15.7752 | 17.6269 | 116.0988 | 145.0094 | 96.623 | 97.8191 | 72.975 |  | 38.3716 | 74.6796 | 38.6363 | 58.4843 | 46.6519 | 105.974 |  | 61.3782 |  |  | 14.4551 | 16.5783 | 43.3935 | [6 empty] | 46.9404 |  |  | 30.9688 |  |  | 15.786 | 44.7872 | 160.8362 | 9.1083 | 40.8328 | 107.138 | 10.7024 | 39.6493 | 118.6146 | 19.386 | 87.719 | 11.0024 | 84.0142 | 12.3426 | 88.4188 | 10.4856 | 40.8692 | 99.7476 | 20.6716 | 40.514 | 124.0366 | 11.3803 | 37.6485 | 118.0877 | 12.1315 | 83.7637 | 18.0029 | 89.7229 | 13.1862 | 94.5841 | 0.67332 | 19.5492 | 1.1168 | 0.089203 | -38.2485 | 3.1232 | 142.69 | 49.48 | -1.1612 | -0.4516 | 0.39893 | -0.70224 | -0.24586 | 0.52924 | 0.49158 | -0.42721 | -0.46539 | 0.26439 | 0.53719 | 0.55881 | -0.73341 | -0.21209
42810.4453 | 452 | 18.306 | 18.4771 | 18.4864 | 18.4873 | 17.7929 | 16.4021 | 14.4521 | 16.5935 | 17.0907 | 17.182 | 17.1849 | 16.6969 | 15.7046 | 14.3351 | 14.6567 | 14.7404 | 15.3481 | 13.2333 | 13.7834 | 15.5474 |  |  |  | 16.4983 | 16.0767 | 19.5823 | 118.9412 | 105.4268 | 139.367 | 16.9447 | 16.2519 | 17.9465 | 16.7149 | 16.1783 | 18.5465 | 40.4353 | 128.1394 |  | 69.0433 | 102.0207 | 102.4018 | 86.4422 |  | 6.7352 | 7.2874 | 6.5599 | 7.4305 | 7.915 | 10.7005 | 56.7745 | 4.7599 | 7.0214 | 4.7723 | 7.8159 | 8.6174 | 41.7811 | 46.4017 | 42.4991 | 14.6636 |  |  | -0.62733 | -0.16682 | -0.065176 | -0.17808 | 0.38064 | 0.044224 | 0.16484 | 0.28831 | -0.47656 | -2.72 | -0.050776 | -0.00059962 | -0.00057826 | 0.98858 | 15.7967 | 16.6373 | 17.1789 | 17.5072 | 17.4451 | 16.3989 | 14.7468 | 16.7801 | 17.1177 | 17.4096 | 17.4494 | 17.1623 | 16.3247 | 14.5234 | 25.7641 | 15.2318 | 15.342 | 11.4399 | 10.4882 | 23.6301 | 15.7925 | 15.8051 | 15.4603 | 15.3899 | 14.2514 | 14.6736 | 15.8918 |  |  |  | 34.039 | 123.4813 | 95.3128 | 59.6864 | 0.55456 | 0.074364 | 38.4587 |  |  | 11.1107 |  |  | 16.8866 | 16.4802 | 22.1089 | 16.3222 | 15.7867 | 17.6489 | 116.3385 | 144.9731 | 96.7107 | 97.8982 | 72.6249 |  | 38.4982 | 75.6296 | 38.7619 | 60.7298 | 46.8917 | 106.0408 |  | 61.5217 |  |  | 14.4845 | 16.5942 | 43.2362 | [6 empty] | 47.9971 |  |  | 31.0166 |  |  | 15.8062 | 44.8746 | 160.9769 | 9.082 | 40.6555 | 107.4238 | 10.7113 | 39.9605 | 118.659 | 19.4091 | 87.9213 | 10.9975 | 84.3552 | 12.3455 | 88.617 | 10.4874 | 40.9151 | 100.1256 | 20.6899 | 40.6351 | 124.4637 | 11.4072 | 37.7596 | 118.5385 | 12.1497 | 83.9716 | 18.0397 | 90.0106 | 13.1949 | 94.832 | 0.83972 | 19.5485 | 1.1197 | 0.089073 | -38.1906 | 3.1232 | 136.27 | 49.54 | -1.1211 | -0.47666 | -0.29794 | -0.49248 | 0.72438 | 0.24691 | 0.47669 | -0.4131 | -0.48743 | 0.21046 | 0.20275 | 0.44527 | -0.72969 | -0.20753
42810.4453 | 453 | 18.3096 | 18.4824 | 18.4848 | 18.4851 | 17.7924 | 16.4065 | 14.4571 | 16.5935 | 17.0883 | 17.1882 | 17.1839 | 16.6964 | 15.7083 | 14.3316 | 14.6545 | 14.7404 | 15.3602 | 13.2356 | 13.7901 | 15.5614 |  |  |  | 16.5065 | 16.0812 | 19.6029 | 119.559 | 105.8721 | 140.0099 | 16.9438 | 16.2592 | 17.962 | 16.7218 | 16.1788 | 18.5646 | 40.5713 | 128.4866 |  | 69.2208 | 102.1886 | 102.5986 | 84.7457 |  | 6.7261 | 7.2797 | 6.5438 | 7.4141 | 7.8928 | 10.7188 | 56.5959 | 4.7296 | 7.0225 | 4.6857 | 7.8232 | 8.6156 | 41.7969 | 46.4069 | 42.5015 | 14.6579 |  |  | -0.5419 | -0.13002 | -0.12629 | -0.10579 | 0.31098 | -0.40787 | 0.245 | 0.41382 | -0.09203 | -0.38285 | -0.13065 | -0.00058812 | -0.00059469 | 0.99675 | 15.7966 | 16.6375 | 17.1793 | 17.5015 | 17.4565 | 16.4045 | 14.7387 | 16.783 | 17.1159 | 17.4134 | 17.4612 | 17.1607 | 16.32 | 14.5184 | 28.9351 | 16.3667 | 17.5388 | 12.4973 | 10.8715 | 23.6881 | 15.823 | 15.8076 | 15.4709 | 15.394 | 14.2613 | 14.6881 | 15.9139 |  |  |  | 34.159 | 124.0611 | 95.9998 | 59.4422 | 0.18928 | -0.21942 | 38.5884 |  |  | 11.1087 |  |  | 16.8844 | 16.4789 | 22.1396 | 16.3261 | 15.7896 | 17.6616 | 116.5074 | 145.1174 | 96.8201 | 98.0437 | 72.0148 |  | 38.6367 | 76.9862 | 38.9035 | 59.6152 | 47.1783 | 106.3606 |  | 61.6938 |  |  | 14.5049 | 16.6037 | 43.3726 | [6 empty] | 49.7956 |  |  | 31.0942 |  |  | 15.8291 | 45.1013 | 161.2443 | 9.0666 | 40.5308 | 107.5339 | 10.7173 | 39.9976 | 118.8161 | 19.4329 | 88.1631 | 11.0382 | 84.6334 | 12.3521 | 88.9296 | 10.5201 | 41.1325 | 100.4279 | 20.7207 | 40.8441 | 124.8306 | 11.4191 | 37.9087 | 118.7717 | 12.1791 | 84.1906 | 18.0607 | 90.2607 | 13.208 | 94.9714 | 0.65752 | 19.5456 | 1.1218 | 0.08827 | -38.1642 | 3.1232 | 136.27 | 50.41 | -1.0428 | -0.42081 | -0.41472 | -0.37959 | 0.65477 | -0.74987 | 0.58118 | -0.39135 | -0.5202 | 0.25152 | -0.14278 | 0.20474 | -0.67783 | -0.19662
42810.4453 | 454 | 18.307 | 18.4849 | 18.4873 | 18.4849 | 17.7963 | 16.4028 | 14.4631 | 16.5918 | 17.087 | 17.1871 | 17.1885 | 16.6997 | 15.7063 | 14.3286 | 14.6625 | 14.7509 | 15.3634 | 13.2297 | 13.7909 | 15.5767 |  |  |  | 16.5129 | 16.0876 | 19.6279 | 119.9992 | 106.2604 | 139.9426 | 16.9393 | 16.2594 | 17.9727 | 16.7159 | 16.1832 | 18.5876 | 40.6876 | 128.8961 |  | 69.4204 | 102.4115 | 102.8159 | 81.5492 |  | 6.7262 | 7.2732 | 6.5309 | 7.3907 | 7.879 | 10.674 | 57.026 | 4.7566 | 7.0115 | 4.6015 | 7.8148 | 8.6251 | 41.8158 | 46.4092 | 42.505 | 14.6499 |  |  | -0.63915 | -0.45201 | -0.075032 | -0.09331 | 0.058648 | -0.078656 | 0.096496 | 0.48742 | -0.75678 | -0.22109 | 0.051952 | -0.0005914 | -0.00057826 | 1.0254 | 15.8048 | 16.6375 | 17.1749 | 17.5049 | 17.4561 | 16.4022 | 14.7326 | 16.7774 | 17.1129 | 17.4082 | 17.4553 | 17.158 | 16.3239 | 14.5164 | 29.3691 | 16.4281 | 18.1191 | 13.0842 | 11.7669 | 23.7135 | 15.8431 | 15.8058 | 15.4706 | 15.401 | 14.2635 | 14.7012 | 15.9191 |  |  |  | 34.2664 | 124.7012 | 96.3459 | 59.5124 | 0.095879 | -0.21942 | 38.7228 |  |  | 11.1106 |  |  | 16.8752 | 16.4776 | 22.1656 | 16.3195 | 15.785 | 17.666 | 116.6106 | 145.4339 | 96.961 | 98.2491 | 72.0625 |  | 38.7694 | 76.8824 | 39.0553 | 58.1904 | 47.4141 | 107.456 |  | 61.9016 |  |  | 14.5098 | 16.625 | 43.4153 | [6 empty] | 49.7005 |  |  | 31.1966 |  |  | 15.8324 | 45.097 | 161.4045 | 9.0382 | 40.7287 | 107.559 | 10.72 | 39.7447 | 118.9248 | 19.4388 | 88.2991 | 11.0788 | 84.8183 | 12.348 | 89.1421 | 10.5615 | 41.2317 | 100.5702 | 20.7552 | 40.9413 | 125.2012 | 11.4386 | 38.0761 | 119.1071 | 12.2143 | 84.3847 | 18.0521 | 90.4563 | 13.2269 | 95.3013 | 0.75402 | 19.5442 | 1.1273 | 0.089211 | -38.1587 | 3.1232 | 111.47 | 48.91 | -1.1324 | -0.7846 | -0.31967 | -0.35648 | 0.28433 | -0.32927 | 0.36471 | -0.38808 | -0.51206 | 0.2994 | -0.18803 | 0.1426 | -0.58499 | -0.19488
42810.4453 | 455 | 18.3082 | 18.4755 | 18.4854 | 18.4848 | 17.7884 | 16.3977 | 14.4538 | 16.5878 | 17.0886 | 17.1792 | 17.1796 | 16.6941 | 15.7004 | 14.3366 | 14.6517 | 14.7459 | 15.359 | 13.224 | 13.7822 | 15.5776 |  |  |  | 16.5023 | 16.0807 | 19.6469 | 120.3136 | 106.6351 | 139.6888 | 16.9383 | 16.2556 | 17.989 | 16.711 | 16.1799 | 18.5994 | 40.7672 | 128.621 |  | 69.6038 | 102.6717 | 103.0147 | 78.7878 |  | 6.7138 | 7.2704 | 6.522 | 7.3681 | 7.8611 | 10.6519 | 57.8745 | 4.7885 | 7.0222 | 4.5633 | 7.8249 | 8.621 | 41.8204 | 46.3957 | 42.4993 | 14.6347 |  |  | -0.72524 | -0.15236 | 0.10108 | -0.50532 | 0.016592 | -0.27579 | 0.024872 | 0.54787 | 0.17477 | -0.27354 | -0.11635 | -0.00062754 | -0.0006259 | 1.0672 | 15.806 | 16.631 | 17.1794 | 17.5056 | 17.4542 | 16.3961 | 14.7351 | 16.7768 | 17.1088 | 17.4108 | 17.4536 | 17.1576 | 16.3269 | 14.5151 | 28.83 | 16.4925 | 18.2165 | 12.7787 | 11.62 | 23.7224 | 15.849 | 15.8101 | 15.4732 | 15.4106 | 14.2603 | 14.7029 | 15.9299 |  |  |  | 34.3734 | 125.1538 | 96.405 | 59.4962 | 0.19191 | -0.20718 | 38.675 |  |  | 11.1074 |  |  | 16.8731 | 16.4753 | 22.1987 | 16.3178 | 15.7852 | 17.6842 | 116.563 | 145.7348 | 97.1256 | 98.4793 | 72.3578 |  | 38.8894 | 76.7777 | 39.1946 | 58.9264 | 47.6736 | 108.8 |  | 62.1056 |  |  | 14.494 | 16.6282 | 43.6706 | [6 empty] | 50.3201 |  |  | 31.272 |  |  | 15.8338 | 45.3068 | 161.6039 | 9.0146 | 41.1393 | 107.8097 | 10.6937 | 39.6676 | 118.8312 | 19.4395 | 88.3774 | 11.0925 | 84.959 | 12.3373 | 89.2935 | 10.5546 | 41.3487 | 100.7128 | 20.8093 | 41.0007 | 125.646 | 11.4581 | 38.2283 | 119.5299 | 12.2534 | 84.6216 | 18.0505 | 90.5569 | 13.2528 | 95.8354 | 0.85879 | 19.54 | 1.1318 | 0.089254 | -38.187 | 3.1232 | 120.08 | 48.77 | -1.2059 | -0.45552 | 0.37102 | -0.82958 | 0.15123 | -0.61655 | 0.18515 | -0.39213 | -0.50432 | 0.28811 | -0.1271 | 0.13247 | -0.50552 | -0.19075
42810.4453 | 456 | 18.297 | 18.468 | 18.4815 | 18.4876 | 17.7903 | 16.3832 | 14.455 | 16.5888 | 17.0853 | 17.1734 | 17.1808 | 16.6896 | 15.7054 | 14.3314 | 14.6472 | 14.7373 | 15.3529 | 13.2155 | 13.7772 | 15.5764 |  |  |  | 16.497 | 16.0721 | 19.6663 | 120.6142 | 106.981 | 139.1581 | 16.9398 | 16.2533 | 18.0063 | 16.7075 | 16.1771 | 18.6212 | 40.8804 | 127.9397 |  | 69.7953 | 102.9515 | 103.2931 | 79.1543 |  | 6.7115 | 7.2712 | 6.5057 | 7.3644 | 7.8383 | 10.6159 | 58.8862 | 4.7669 | 7.0246 | 4.5382 | 7.8308 | 8.6131 | 41.8291 | 46.4026 | 42.5033 | 14.6195 |  |  | -0.47225 | 0.096683 | -0.14797 | -0.35944 | -0.078032 | 0.032396 | 0.16418 | 0.27057 | -0.77527 | 0.57237 | 0.083942 | -0.00060619 | -0.00062754 | 1.1449 | 15.801 | 16.6314 | 17.1801 | 17.5091 | 17.4527 | 16.3955 | 14.7363 | 16.7799 | 17.1197 | 17.4147 | 17.4528 | 17.1582 | 16.3252 | 14.5172 | 29.2271 | 16.6329 | 18.9504 | 12.7803 | 11.1252 | 23.7603 | 15.8855 | 15.8129 | 15.479 | 15.4055 | 14.2598 | 14.707 | 15.9438 |  |  |  | 34.4794 | 125.4785 | 96.4525 | 59.2692 | 0.21865 | -0.2834 | 38.7156 |  |  | 11.1161 |  |  | 16.8826 | 16.4837 | 22.2406 | 16.3208 | 15.7942 | 17.7106 | 116.6499 | 146.0912 | 97.3452 | 98.7075 | 72.691 |  | 39.0202 | 77.8331 | 39.3387 | 57.6222 | 47.8173 | 108.7271 |  | 62.3195 |  |  | 14.4094 | 16.6449 | 44.137 | [6 empty] | 49.5045 |  |  | 31.3356 |  |  | 15.8372 | 45.4887 | 161.9772 | 9.0157 | 41.4801 | 108.1154 | 10.6849 | 40.0379 | 118.8666 | 19.4545 | 88.493 | 11.1228 | 85.154 | 12.3411 | 89.5342 | 10.5262 | 41.678 | 100.8419 | 20.8698 | 40.9123 | 126.2018 | 11.4796 | 38.3453 | 119.6192 | 12.2946 | 84.9177 | 18.0465 | 90.7805 | 13.2647 | 96.4721 | 0.80429 | 19.5384 | 1.1353 | 0.088769 | -38.2159 | 3.1232 | 117.16 | 50.55 | -0.97244 | 0.36287 | -0.44891 | -0.69966 | -0.32793 | 0.2113 | 0.47567 | -0.39684 | -0.52864 | 0.32941 | -0.16678 | 0.055181 | -0.51176 | -0.1808
42810.4453 | 457 | 18.2954 | 18.4772 | 18.4835 | 18.4837 | 17.7986 | 16.399 | 14.4571 | 16.5811 | 17.0924 | 17.1782 | 17.1901 | 16.6986 | 15.7102 | 14.3308 | 14.6474 | 14.7375 | 15.3501 | 13.2154 | 13.7818 | 15.5834 |  |  |  | 16.5046 | 16.0728 | 19.6834 | 120.8706 | 107.2702 | 138.7838 | 16.9448 | 16.2535 | 18.0178 | 16.708 | 16.1723 | 18.6355 | 41.0432 | 127.4642 |  | 69.9651 | 103.2599 | 103.6347 | 80.789 |  | 6.7011 | 7.2719 | 6.4971 | 7.3657 | 7.811 | 10.5925 | 59.7181 | 4.711 | 7.0294 | 4.5688 | 7.8408 | 8.631 | 41.828 | 46.4054 | 42.5076 | 14.6147 |  |  | -0.57081 | -0.025541 | -0.054004 | -0.3003 | 0.031704 | 0.011368 | 0.31663 | 0.32182 | -0.18038 | -0.34131 | -0.077005 | -0.00056183 | -0.00061769 | 1.2711 | 15.8067 | 16.6244 | 17.1798 | 17.5086 | 17.4551 | 16.4004 | 14.734 | 16.7778 | 17.1233 | 17.4106 | 17.4518 | 17.1613 | 16.3205 | 14.5126 | 31.1559 | 16.2011 | 18.91 | 13.2099 | 10.9927 | 23.8133 | 15.8945 | 15.8133 | 15.4807 | 15.4081 | 14.2649 | 14.7038 | 15.9625 |  |  |  | 34.5938 | 125.7828 | 96.4514 | 59.0434 | 0.35095 | -0.23748 | 38.9943 |  |  | 11.1296 |  |  | 16.88 | 16.4946 | 22.2835 | 16.3223 | 15.7972 | 17.7344 | 116.8601 | 146.4992 | 97.5933 | 98.9559 | 73.4359 |  | 39.1658 | 79.5271 | 39.487 | 55.5423 | 48.0091 | 108.4568 |  | 62.5361 |  |  | 14.3619 | 16.6855 | 44.3172 | [6 empty] | 49.4245 |  |  | 31.4264 |  |  | 15.8199 | 45.2754 | 161.9244 | 9.0169 | 41.3835 | 108.3352 | 10.6753 | 40.4412 | 118.9053 | 19.4711 | 88.6997 | 11.1533 | 85.3576 | 12.3321 | 89.7871 | 10.5227 | 41.7482 | 100.9168 | 20.9083 | 40.6798 | 126.6529 | 11.5052 | 38.4989 | 119.836 | 12.3331 | 85.137 | 18.0385 | 90.9847 | 13.2678 | 96.979 | 1.092 | 19.5341 | 1.139 | 0.087445 | -38.1999 | 3.1232 | 127.81 | 48.86 | -1.0686 | -0.18651 | -0.2712 | -0.63952 | 0.20902 | 0.12516 | 0.66055 | -0.41249 | -0.57054 | 0.39395 | -0.37489 | 0.06071 | -0.5515 | -0.1706
42810.4453 | 458 | 18.3004 | 18.4675 | 18.4815 | 18.4778 | 17.7839 | 16.386 | 14.4547 | 16.5823 | 17.081 | 17.1797 | 17.1791 | 16.6898 | 15.7082 | 14.3243 | 14.6509 | 14.7381 | 15.3563 | 13.2223 | 13.7905 | 15.6101 |  |  |  | 16.5061 | 16.0836 | 19.7137 | 121.2015 | 107.7073 | 139.6857 | 16.9369 | 16.2561 | 18.0272 | 16.7052 | 16.1765 | 18.6502 | 41.1666 | 127.8086 |  | 70.1453 | 103.5388 | 103.859 | 79.1762 |  | 6.6951 | 7.2736 | 6.4903 | 7.3568 | 7.7941 | 10.6169 | 59.7936 | 4.6796 | 7.0301 | 4.5789 | 7.8398 | 8.6225 | 41.8341 | 46.3867 | 42.5105 | 14.607 |  |  | -0.6477 | -0.12477 | 0.11356 | -0.14917 | -0.070148 | 0.079052 | 0.43294 | 0.37636 | -0.39386 | -0.5895 | -0.084754 | -0.00061112 | -0.00061112 | 1.1808 | 15.8072 | 16.6277 | 17.1772 | 17.5077 | 17.4492 | 16.4018 | 14.7326 | 16.7774 | 17.1217 | 17.4093 | 17.4544 | 17.1536 | 16.32 | 14.5174 | 32.7059 | 16.2121 | 19.0634 | 13.747 | 11.4613 | 23.8742 | 15.9036 | 15.8141 | 15.4768 | 15.4056 | 14.2678 | 14.7085 | 15.9703 |  |  |  | 34.7072 | 126.2368 | 96.485 | 58.7084 | 0.30354 | -0.14263 | 39.1616 |  |  | 11.1335 |  |  | 16.8705 | 16.4931 | 22.3165 | 16.3222 | 15.7921 | 17.7418 | 117.0056 | 146.8108 | 97.805 | 99.1714 | 73.7855 |  | 39.3049 | 80.1618 | 39.6159 | 56.0935 | 48.2147 | 108.8217 |  | 62.7296 |  |  | 14.3699 | 16.7118 | 44.3914 | [6 empty] | 49.5027 |  |  | 31.518 |  |  | 15.8092 | 45.1373 | 162.0464 | 9.0247 | 41.4748 | 108.6566 | 10.6656 | 40.2627 | 119.1681 | 19.513 | 89.1833 | 11.1822 | 85.5404 | 12.321 | 89.9226 | 10.5507 | 41.6557 | 101.0544 | 20.9191 | 40.6579 | 127.1571 | 11.5369 | 38.6038 | 120.0465 | 12.3726 | 85.2863 | 18.0506 | 91.2436 | 13.2971 | 97.2503 | 0.95028 | 19.5298 | 1.1446 | 0.089406 | -38.1852 | 3.1233 | 144.05 | 49.26 | -1.1396 | -0.41221 | 0.39327 | -0.45072 | -0.31092 | 0.33007 | 0.77243 | -0.41737 | -0.5837 | 0.38589 | -0.53998 | 0.044732 | -0.5024 | -0.15739
42810.4453 | 459 | 18.3025 | 18.4672 | 18.4819 | 18.4846 | 17.7902 | 16.3955 | 14.4554 | 16.5898 | 17.0838 | 17.1788 | 17.1815 | 16.6992 | 15.7094 | 14.3306 | 14.6512 | 14.7366 | 15.3512 | 13.2208 | 13.7939 | 15.6141 |  |  |  | 16.4992 | 16.0908 | 19.751 | 121.5506 | 108.2599 | 139.8486 | 16.9453 | 16.2522 | 18.0491 | 16.703 | 16.1768 | 18.673 | 41.2849 | 129.1002 |  | 70.3424 | 103.8059 | 104.1202 | 78.8141 |  | 6.6983 | 7.2565 | 6.4647 | 7.33 | 7.7666 | 10.7084 | 59.2478 | 4.6308 | 7.0327 | 4.5453 | 7.8487 | 8.6302 | 41.8372 | 46.3688 | 42.54 | 14.5992 |  |  | -0.76927 | -0.1517 | 0.074132 | -0.15902 | -0.093148 | -0.37304 | 0.46514 | 0.52947 | -0.4176 | -0.36061 | -0.41539 | -0.00054869 | -0.00062426 | 1.129 | 15.8227 | 16.6391 | 17.1851 | 17.5067 | 17.457 | 16.3999 | 14.7325 | 16.7912 | 17.1203 | 17.4127 | 17.4618 | 17.1613 | 16.3286 | 14.5199 | 34.0408 | 16.371 | 19.2324 | 14.167 | 11.9956 | 23.938 | 15.9314 | 15.812 | 15.4759 | 15.4033 | 14.2655 | 14.7104 | 15.9799 |  |  |  | 34.8059 | 126.6962 | 96.7333 | 58.6039 | 0.23081 | 0.013575 | 39.2639 |  |  | 11.1354 |  |  | 16.8803 | 16.5032 | 22.3538 | 16.3281 | 15.7922 | 17.7593 | 117.2266 | 147.1908 | 98.0168 | 99.3921 | 73.9598 |  | 39.4131 | 80.3088 | 39.7365 | 56.1171 | 48.385 | 109.3506 |  | 62.8896 |  |  | 14.3868 | 16.7209 | 44.629 | [6 empty] | 49.1207 |  |  | 31.567 |  |  | 15.8224 | 45.0867 | 161.8586 | 9.0486 | 42.0124 | 108.9202 | 10.671 | 39.9681 | 119.3629 | 19.5662 | 89.7218 | 11.2001 | 85.6211 | 12.3383 | 90.0203 | 10.5726 | 41.7795 | 101.3225 | 20.9348 | 40.9184 | 127.6174 | 11.5616 | 38.7725 | 120.2325 | 12.3966 | 85.2937 | 18.0695 | 91.6418 | 13.3131 | 97.2415 | 0.79466 | 19.5288 | 1.1494 | 0.090709 | -38.1367 | 3.1232 | 155.67 | 50.06 | -1.2422 | -0.45453 | 0.31773 | -0.46536 | -0.35835 | -0.71713 | 0.80077 | -0.41846 | -0.5836 | 0.39125 | -0.68084 | 0.029198 | -0.48823 | -0.15109
42810.4454 | 460 | 18.3075 | 18.476 | 18.4865 | 18.4829 | 17.7913 | 16.4035 | 14.4568 | 16.5952 | 17.0885 | 17.1808 | 17.1815 | 16.7041 | 15.7145 | 14.3341 | 14.6536 | 14.742 | 15.3537 | 13.2249 | 13.797 | 15.6243 |  |  |  | 16.4985 | 16.1004 | 19.7699 | 121.8038 | 108.7407 | 139.6999 | 16.9485 | 16.2541 | 18.0665 | 16.7029 | 16.1811 | 18.7007 | 41.4403 | 129.2639 |  | 70.523 | 104.0427 | 104.4142 | 79.2168 |  | 6.6906 | 7.259 | 6.4702 | 7.3009 | 7.7462 | 10.7268 | 59.0829 | 4.592 | 7.0338 | 4.5428 | 7.8538 | 8.6383 | 41.8416 | 46.3553 | 42.5541 | 14.5878 |  |  | -0.70224 | -0.11097 | 0.10305 | -0.11697 | -0.001152 | -0.088512 | 0.4474 | 0.33299 | -0.38938 | -0.14011 | -0.071044 | -0.00059469 | -0.00059469 | 1.2863 | 15.8102 | 16.6331 | 17.1825 | 17.5171 | 17.4558 | 16.3935 | 14.7395 | 16.7781 | 17.1224 | 17.4184 | 17.4597 | 17.1585 | 16.3174 | 14.5176 | 34.8909 | 17.1436 | 20.9176 | 14.7511 | 11.8005 | 23.9878 | 15.9601 | 15.8208 | 15.48 | 15.4083 | 14.2684 | 14.7199 | 16.0005 |  |  |  | 34.9086 | 127.2357 | 97.0926 | 58.4466 | 0.1285 | -0.11045 | 39.3972 |  |  | 11.1458 |  |  | 16.888 | 16.5093 | 22.3933 | 16.3285 | 15.7944 | 17.7844 | 117.4539 | 147.4078 | 98.2791 | 99.5768 | 73.9204 |  | 39.5385 | 81.0697 | 39.8805 | 55.8374 | 48.5992 | 110.524 |  | 63.0981 |  |  | 14.4019 | 16.718 | 44.9125 | [6 empty] | 48.0318 |  |  | 31.5789 |  |  | 15.8437 | 44.9306 | 162.3283 | 9.0677 | 42.4549 | 109.135 | 10.6677 | 40.3282 | 119.4484 | 19.6054 | 90.2736 | 11.1848 | 85.7364 | 12.3102 | 90.294 | 10.5806 | 42.0572 | 101.5633 | 20.9671 | 41.0347 | 127.9444 | 11.5793 | 38.835 | 120.3072 | 12.4208 | 85.2811 | 18.0904 | 91.7479 | 13.336 | 97.4231 | 0.82701 | 19.526 | 1.1532 | 0.08853 | -38.0462 | 3.1232 | 179.97 | 49.32 | -1.1866 | -0.38874 | 0.37461 | -0.39911 | -0.039853 | -0.34933 | 0.78538 | -0.41302 | -0.59973 | 0.40659 | -0.76946 | -0.15471 | -0.494 | -0.14319
42810.4454 | 461 | 18.3077 | 18.4735 | 18.4866 | 18.4828 | 17.7972 | 16.403 | 14.4534 | 16.5921 | 17.0854 | 17.1795 | 17.1826 | 16.6988 | 15.7143 | 14.3383 | 14.656 | 14.7315 | 15.3582 | 13.2353 | 13.8031 | 15.6496 |  |  |  | 16.5128 | 16.0917 | 19.7983 | 122.0973 | 109.0353 | 140.6002 | 16.9418 | 16.2496 | 18.0816 | 16.6983 | 16.1883 | 18.7194 | 41.6109 | 129.0347 |  | 70.6978 | 104.2683 | 104.6863 | 79.546 |  | 6.6987 | 7.2743 | 6.4742 | 7.3048 | 7.7518 | 10.7512 | 59.747 | 4.5748 | 7.0465 | 4.5655 | 7.8697 | 8.6244 | 41.8476 | 46.3432 | 42.5793 | 14.59 |  |  | -0.52613 | -0.15696 | 0.1037 | -0.18925 | 0.013964 | -0.35004 | 0.48551 | 0.1122 | -0.43161 | -1.0697 | 0.041421 | -0.00054212 | -0.0005684 | 1.52 | 15.8145 | 16.6345 | 17.1898 | 17.5098 | 17.466 | 16.3995 | 14.7443 | 16.7869 | 17.1278 | 17.413 | 17.4529 | 17.159 | 16.331 | 14.5211 | 34.8426 | 17.6109 | 22.5783 | 15.4769 | 12.162 | 24.0401 | 15.9994 | 15.8221 | 15.4733 | 15.4086 | 14.2633 | 14.7275 | 16.0189 |  |  |  | 35.0113 | 127.8547 | 97.3318 | 58.1436 | 0.51769 | 0.051403 | 39.4446 |  |  | 11.1549 |  |  | 16.8802 | 16.5081 | 22.4312 | 16.3279 | 15.7988 | 17.7995 | 117.7149 | 147.7147 | 98.5501 | 99.7167 | 73.0412 |  | 39.6364 | 82.4536 | 39.9881 | 58.3937 | 48.8254 | 111.989 |  | 63.2641 |  |  | 14.3701 | 16.7013 | 45.176 | [6 empty] | 49.0758 |  |  | 31.5779 |  |  | 15.8759 | 44.9817 | 162.9266 | 9.1267 | 42.5155 | 109.378 | 10.6892 | 40.7315 | 119.7046 | 19.6494 | 91.0981 | 11.1881 | 85.964 | 12.3141 | 90.5567 | 10.5981 | 41.9778 | 101.9933 | 20.9851 | 40.8822 | 128.2618 | 11.6105 | 38.9238 | 120.5205 | 12.456 | 85.3473 | 18.1729 | 92.0281 | 13.3583 | 97.5814 | 0.94585 | 19.5204 | 1.1579 | 0.088993 | -38.1391 | 3.1232 | 167.85 | 50.02 | -1.0282 | -0.46235 | 0.37581 | -0.50768 | 0.13876 | -0.69472 | 0.81818 | -0.38519 | -0.63443 | 0.34358 | -0.75797 | -0.33465 | -0.4972 | -0.13124
42810.4454 | 462 | 18.3082 | 18.466 | 18.4847 | 18.4826 | 17.8003 | 16.4019 | 14.4552 | 16.5891 | 17.0914 | 17.1808 | 17.1866 | 16.6953 | 15.7086 | 14.3426 | 14.659 | 14.7367 | 15.3524 | 13.2317 | 13.7937 | 15.655 |  |  |  | 16.4991 | 16.0915 | 19.814 | 122.6507 | 109.1897 | 142.2846 | 16.9437 | 16.2503 | 18.0961 | 16.7053 | 16.1904 | 18.7387 | 41.7564 | 129.1444 |  | 70.8542 | 104.5267 | 104.9625 | 79.5587 |  | 6.6934 | 7.2723 | 6.466 | 7.2771 | 7.7466 | 10.7556 | 59.8564 | 4.578 | 7.0356 | 4.5805 | 7.8664 | 8.6315 | 41.8496 | 46.3286 | 42.5919 | 14.5768 |  |  | -0.56096 | -0.065625 | -0.021148 | -0.053226 | -0.084604 | 0.05408 | 0.39548 | 0.10563 | -0.39074 | 0.37054 | -0.012228 | -0.00056676 | -0.00055033 | 1.2934 | 15.8265 | 16.6408 | 17.1819 | 17.504 | 17.4569 | 16.4016 | 14.7406 | 16.7809 | 17.1223 | 17.4093 | 17.455 | 17.1614 | 16.3277 | 14.5205 | 37.5515 | 18.6213 | 23.8877 | 15.7219 | 12.0683 | 24.1572 | 16.0557 | 15.8276 | 15.477 | 15.4162 | 14.2629 | 14.7249 | 16.0268 |  |  |  | 35.1163 | 128.2835 | 97.6417 | 58.7534 | 0.18057 | 0.16677 | 39.5145 |  |  | 11.1552 |  |  | 16.8809 | 16.5132 | 22.4765 | 16.327 | 15.8044 | 17.8084 | 118.0488 | 148.2047 | 98.7822 | 99.8699 | 72.4263 |  | 39.7803 | 82.6304 | 40.1131 | 57.628 | 49.0477 | 112.2768 |  | 63.4299 |  |  | 14.2927 | 16.7171 | 45.0599 | [6 empty] | 48.0186 |  |  | 31.4257 |  |  | 15.8807 | 45.1222 | 163.0831 | 9.1461 | 42.1047 | 109.6823 | 10.6887 | 40.4737 | 119.9367 | 19.6723 | 91.4524 | 11.2043 | 86.23 | 12.3023 | 90.7654 | 10.6232 | 42.282 | 102.2876 | 21.0213 | 40.9061 | 128.99 | 11.6392 | 39.0655 | 120.628 | 12.4539 | 85.4688 | 18.2641 | 92.5426 | 13.3937 | 97.7457 | 0.84165 | 19.514 | 1.1641 | 0.090173 | -38.144 | 3.1232 | 167.49 | 49.59 | -1.0639 | -0.29896 | -0.16971 | -0.26924 | -0.34155 | 0.27307 | 0.73845 | -0.36311 | -0.635 | 0.3727 | -1.0452 | -0.47357 | -0.49248 | -0.14457
42810.4454 | 463 | 18.3041 | 18.4656 | 18.4743 | 18.4793 | 17.7924 | 16.4056 | 14.4588 | 16.598 | 17.0839 | 17.1771 | 17.1781 | 16.7018 | 15.711 | 14.3411 | 14.6524 | 14.7442 | 15.3645 | 13.2214 | 13.7937 | 15.6705 |  |  |  | 16.5016 | 16.0954 | 19.8403 | 123.1507 | 109.4423 | 142.5273 | 16.9364 | 16.2613 | 18.1191 | 16.7138 | 16.1849 | 18.7563 | 41.8738 | 128.9909 |  | 70.9958 | 104.7969 | 105.1812 | 80.8014 |  | 6.6987 | 7.274 | 6.4712 | 7.285 | 7.7357 | 10.7385 | 59.0195 | 4.5959 | 7.038 | 4.5619 | 7.8742 | 8.6346 | 41.8485 | 46.3402 | 42.6046 | 14.5725 |  |  | -0.4821 | 0.007315 | 0.093848 | 0.14917 | 0.20387 | 0.11322 | 0.4152 | -0.019876 | -0.74258 | 0.019339 | -0.075614 | -0.00055033 | -0.00060619 | 1.0981 | 15.8205 | 16.6446 | 17.1769 | 17.5126 | 17.46 | 16.4073 | 14.7432 | 16.78 | 17.1233 | 17.4187 | 17.4605 | 17.1651 | 16.3302 | 14.527 | 37.6949 | 19.5496 | 24.9995 | 17.0665 | 12.5403 | 24.2209 | 16.1116 | 15.8201 | 15.4728 | 15.4056 | 14.2588 | 14.7261 | 16.0391 |  |  |  | 35.245 | 128.6476 | 97.8392 | 59.1568 | 0.42774 | 0.13703 | 39.5831 |  |  | 11.1534 |  |  | 16.8799 | 16.5167 | 22.5124 | 16.3275 | 15.8056 | 17.8216 | 118.2891 | 148.3417 | 98.9872 | 100.0025 | 73.4403 |  | 39.9129 | 83.2085 | 40.2587 | 57.3273 | 49.2696 | 110.928 |  | 63.6113 |  |  | 14.3143 | 16.7172 | 45.3074 | [6 empty] | 49.0508 |  |  | 31.5698 |  |  | 15.8846 | 45.0706 | 164.046 | 9.1672 | 42.1341 | 110.0819 | 10.6797 | 40.4245 | 120.1065 | 19.7173 | 91.4649 | 11.1862 | 86.3981 | 12.3044 | 91.1699 | 10.6377 | 42.5944 | 102.3935 | 21.0462 | 41.1076 | 129.2612 | 11.6515 | 38.9787 | 120.9628 | 12.4724 | 85.6461 | 18.3542 | 92.8532 | 13.411 | 97.8698 | 0.93756 | 19.506 | 1.1694 | 0.089826 | -38.1176 | 3.1232 | 176.78 | 48.97 | -0.98654 | 0.099812 | 0.35751 | 0.45072 | 0.53018 | 0.3951 | 0.75661 | -0.38668 | -0.646 | 0.38891 | -1.0537 | -0.59059 | -0.52291 | -0.15134
42810.4454 | 464 | 18.2973 | 18.4619 | 18.4711 | 18.4813 | 17.7886 | 16.3899 | 14.4513 | 16.5853 | 17.0863 | 17.1756 | 17.1835 | 16.7 | 15.7041 | 14.3307 | 14.6527 | 14.7405 | 15.3605 | 13.2266 | 13.7844 | 15.6802 |  |  |  | 16.4995 | 16.1043 | 19.8605 | 123.5428 | 109.7753 | 142.0368 | 16.9475 | 16.2598 | 18.1355 | 16.7157 | 16.2004 | 18.7818 | 42.0108 | 128.9786 |  | 71.1577 | 105.0964 | 105.3662 | 83.3715 |  | 6.6866 | 7.2645 | 6.4664 | 7.3133 | 7.7162 | 10.7789 | 58.7431 | 4.5758 | 7.0336 | 4.5403 | 7.8796 | 8.6415 | 41.8464 | 46.3403 | 42.6224 | 14.5602 |  |  | -0.49459 | 0.12231 | 0.11816 | -0.14062 | 0.046164 | 0.32876 | 0.45002 | 0.10103 | -0.9329 | -0.28949 | -0.28186 | -0.00052898 | -0.00058976 | 1.0475 | 15.8226 | 16.6403 | 17.1797 | 17.5145 | 17.4587 | 16.4041 | 14.7352 | 16.7806 | 17.1221 | 17.4162 | 17.4534 | 17.1653 | 16.3271 | 14.5256 | 37.9313 | 19.188 | 26.351 | 17.9515 | 13.9704 | 24.3056 | 16.175 | 15.8274 | 15.4762 | 15.4103 | 14.2637 | 14.732 | 16.0471 |  |  |  | 35.3459 | 129.1671 | 98.127 | 59.2695 | 0.40687 | 0.16131 | 39.8368 |  |  | 11.1558 |  |  | 16.8733 | 16.5138 | 22.542 | 16.3295 | 15.7976 | 17.8403 | 118.5155 | 148.4193 | 99.1519 | 100.1849 | 74.4933 |  | 40.0302 | 84.0633 | 40.4064 | 57.1982 | 49.4549 | 110.6762 |  | 63.8148 |  |  | 14.3337 | 16.7288 | 45.0351 | [6 empty] | 48.4379 |  |  | 31.6448 |  |  | 15.8956 | 45.1374 | 164.5997 | 9.1906 | 42.3459 | 110.3047 | 10.6836 | 40.9816 | 120.3546 | 19.7687 | 91.7292 | 11.2005 | 86.5624 | 12.31 | 91.4722 | 10.6346 | 42.6447 | 102.537 | 21.0836 | 40.9649 | 129.2591 | 11.6627 | 38.9155 | 121.2164 | 12.4967 | 85.8541 | 18.4073 | 93.1359 | 13.4321 | 97.9177 | 0.82066 | 19.5011 | 1.1746 | 0.089066 | -38.1399 | 3.1232 | 184.26 | 50.04 | -0.99864 | 0.40813 | 0.40115 | -0.43762 | 0.2523 | 0.6733 | 0.78775 | -0.41185 | -0.66461 | 0.39905 | -1.0701 | -0.73336 | -0.58952 | -0.151
42810.4454 | 465 | 18.3101 | 18.4736 | 18.495 | 18.4872 | 17.8012 | 16.4055 | 14.4598 | 16.6026 | 17.1039 | 17.1846 | 17.1913 | 16.7023 | 15.7151 | 14.3482 | 14.6599 | 14.7473 | 15.3674 | 13.2315 | 13.7923 | 15.6839 |  |  |  | 16.5054 | 16.1017 | 19.8801 | 123.7038 | 110.208 | 142.2457 | 16.9555 | 16.2606 | 18.1595 | 16.7165 | 16.2072 | 18.8043 | 42.1537 | 129.3782 |  | 71.3024 | 105.3501 | 105.6197 | 83.4253 |  | 6.6921 | 7.2732 | 6.4977 | 7.335 | 7.7811 | 10.8457 | 58.2974 | 4.5985 | 7.0388 | 4.5227 | 7.8921 | 8.64 | 41.8367 | 46.3274 | 42.615 | 14.5459 |  |  | -0.47356 | -0.16813 | 0.028136 | -0.14917 | -0.11286 | 0.000856 | 0.24303 | 0.33956 | 0.6998 | -0.49824 | -0.22822 | -0.00059305 | -0.00056019 | 1.2604 | 15.8197 | 16.6386 | 17.1861 | 17.5081 | 17.4528 | 16.4013 | 14.7316 | 16.7803 | 17.1203 | 17.4157 | 17.4491 | 17.1584 | 16.3251 | 14.525 | 39.1702 | 19.7664 | 26.6264 | 18.5776 | 14.3377 | 24.4097 | 16.2299 | 15.8358 | 15.4838 | 15.4165 | 14.2654 | 14.7482 | 16.0657 |  |  |  | 35.4392 | 129.8249 | 98.3405 | 58.9989 | 0.3469 | 0.059496 | 40.0623 |  |  | 11.1626 |  |  | 16.8717 | 16.5172 | 22.5788 | 16.3227 | 15.7933 | 17.8585 | 118.8029 | 148.7506 | 99.3894 | 100.4111 | 73.651 |  | 40.1577 | 83.9969 | 40.55 | 56.5144 | 49.6426 | 111.6107 |  | 64.0565 |  |  | 14.3348 | 16.773 | 44.9336 | [6 empty] | 47.3247 |  |  | 31.7692 |  |  | 15.908 | 45.3158 | 165.1416 | 9.2146 | 42.4877 | 110.4124 | 10.702 | 41.2236 | 120.7331 | 19.8205 | 92.0427 | 11.1946 | 86.7268 | 12.3279 | 91.6375 | 10.6431 | 42.7407 | 102.6909 | 21.1262 | 40.8092 | 129.7384 | 11.6955 | 39.2424 | 121.4664 | 12.5296 | 86.0579 | 18.4654 | 93.3211 | 13.4617 | 98.0408 | 0.6791 | 19.4945 | 1.1786 | 0.087915 | -38.0937 | 3.1233 | 174.59 | 48.93 | -0.97743 | -0.47852 | 0.19575 | -0.45072 | -0.39454 | 0.034361 | 0.57897 | -0.38402 | -0.65777 | 0.42469 | -1.1955 | -0.75756 | -0.58603 | -0.14027
42810.4454 | 466 | 18.3158 | 18.4705 | 18.4835 | 18.4799 | 17.7996 | 16.3965 | 14.4504 | 16.596 | 17.0956 | 17.1854 | 17.1868 | 16.701 | 15.7125 | 14.3434 | 14.6648 | 14.7392 | 15.364 | 13.23 | 13.7971 | 15.7 |  |  |  | 16.5021 | 16.0984 | 19.9074 | 124.1555 | 110.5668 | 143.9937 | 16.9532 | 16.2712 | 18.1693 | 16.7135 | 16.2059 | 18.8263 | 42.259 | 129.8503 |  | 71.4754 | 105.5109 | 105.8413 | 82.2212 |  | 6.6977 | 7.2815 | 6.5033 | 7.3291 | 7.8274 | 10.9608 | 58.134 | 4.6104 | 7.0549 | 4.48 | 7.8936 | 8.6444 | 41.8457 | 46.345 | 42.6142 | 14.5448 |  |  | -0.85206 | -0.062337 | -0.11117 | -0.31345 | 0.034992 | 0.09548 | 0.3094 | 0.24297 | -0.53436 | -1.7421 | -0.109 | -0.00060947 | -0.00062262 | 1.3071 | 15.8239 | 16.6327 | 17.1766 | 17.5057 | 17.4495 | 16.3994 | 14.7442 | 16.7827 | 17.1135 | 17.4149 | 17.4572 | 17.1643 | 16.3255 | 14.5234 | 39.2713 | 19.4426 | 27.0428 | 19.0849 | 14.8723 | 24.4993 | 16.2821 | 15.8316 | 15.4801 | 15.4228 | 14.2675 | 14.752 | 16.0829 |  |  |  | 35.5565 | 130.3054 | 98.4639 | 58.8988 | 0.32623 | 0.083774 | 39.9481 |  |  | 11.1731 |  |  | 16.8815 | 16.5269 | 22.6193 | 16.3302 | 15.8068 | 17.8726 | 119.2135 | 149.0955 | 99.7277 | 100.6911 | 74.5829 |  | 40.2778 | 82.8492 | 40.6664 | 56.4759 | 49.873 | 112.6096 |  | 64.2924 |  |  | 14.3544 | 16.7829 | 44.8667 | [6 empty] | 46.9617 |  |  | 31.9491 |  |  | 15.9143 | 45.6287 | 165.5938 | 9.232 | 42.5905 | 110.4601 | 10.7289 | 41.0925 | 121.0029 | 19.876 | 92.3869 | 11.1825 | 86.8364 | 12.3488 | 91.7303 | 10.6442 | 42.905 | 102.7871 | 21.1627 | 40.9496 | 130.4345 | 11.7186 | 39.2899 | 121.7505 | 12.5605 | 86.1989 | 18.5108 | 93.4286 | 13.4855 | 98.1601 | 0.94719 | 19.4894 | 1.1853 | 0.088747 | -38.1649 | 3.1232 | 182.98 | 49.1 | -1.3138 | -0.29138 | -0.38912 | -0.65337 | 0.21973 | 0.36297 | 0.65339 | -0.40573 | -0.62184 | 0.43392 | -1.1963 | -0.79774 | -0.54891 | -0.13344
42810.4454 | 467 | 18.3136 | 18.4668 | 18.4823 | 18.4812 | 17.796 | 16.3931 | 14.4499 | 16.5859 | 17.0899 | 17.1812 | 17.1835 | 16.7025 | 15.714 | 14.3413 | 14.6703 | 14.7428 | 15.3648 | 13.2323 | 13.793 | 15.7164 |  |  |  | 16.5092 | 16.1068 | 19.9341 | 124.6012 | 111.0039 | 144.4111 | 16.9555 | 16.2716 | 18.1854 | 16.7177 | 16.2077 | 18.8484 | 42.3728 | 130.4123 |  | 71.6726 | 105.6706 | 106.0136 | 82.1073 |  | 6.7004 | 7.2973 | 6.5205 | 7.3435 | 7.8468 | 11.1509 | 58.47 | 4.641 | 7.0557 | 4.4734 | 7.9022 | 8.6475 | 41.8483 | 46.3547 | 42.6216 | 14.5421 |  |  | -0.54256 | 0.069087 | 0.028792 | -0.39033 | 0.048792 | 0.15922 | 0.29692 | 0.005092 | -0.24382 | -0.50852 | -0.37287 | -0.00060947 | -0.00058155 | 1.1203 | 15.8233 | 16.6302 | 17.1753 | 17.5122 | 17.4477 | 16.3932 | 14.7456 | 16.7868 | 17.12 | 17.4143 | 17.4547 | 17.1636 | 16.3324 | 14.5183 | 39.1176 | 19.0955 | 27.1166 | 19.2519 | 15.8599 | 24.5724 | 16.3214 | 15.8363 | 15.4875 | 15.4243 | 14.2633 | 14.7509 | 16.0994 |  |  |  | 35.6811 | 130.518 | 98.3655 | 59.3349 | 0.20467 | -0.011079 | 39.8224 |  |  | 11.1821 |  |  | 16.8854 | 16.5298 | 22.6613 | 16.3281 | 15.8124 | 17.8885 | 119.6479 | 149.3652 | 100.0094 | 100.9671 | 74.5359 |  | 40.4265 | 82.0178 | 40.8302 | 56.5648 | 50.0809 | 112.4793 |  | 64.5385 |  |  | 14.3985 | 16.7793 | 44.6985 | [6 empty] | 47.2047 |  |  | 32.151 |  |  | 15.932 | 45.8478 | 166.1291 | 9.2503 | 42.7063 | 110.7066 | 10.7653 | 41.0113 | 121.1578 | 19.9256 | 92.7744 | 11.1805 | 86.9583 | 12.3769 | 92.0694 | 10.6527 | 43.2552 | 102.9494 | 21.2021 | 41.23 | 130.8255 | 11.7413 | 39.0621 | 122.0431 | 12.5822 | 86.3558 | 18.5592 | 93.5876 | 13.5111 | 98.2916 | 0.87035 | 19.4852 | 1.1906 | 0.08882 | -38.1155 | 3.1232 | 177.83 | 50.19 | -1.0489 | 0.30675 | 0.19803 | -0.72913 | 0.25956 | 0.46887 | 0.64028 | -0.39926 | -0.59305 | 0.43881 | -1.1706 | -0.80136 | -0.54177 | -0.14127
42810.4455 | 468 | 18.3112 | 18.4664 | 18.4792 | 18.4831 | 17.7959 | 16.3925 | 14.449 | 16.587 | 17.0882 | 17.1789 | 17.1793 | 16.6978 | 15.7143 | 14.3432 | 14.6544 | 14.7376 | 15.3627 | 13.2247 | 13.7898 | 15.7335 |  |  |  | 16.5013 | 16.1043 | 19.9527 | 124.9909 | 111.5407 | 144.8835 | 16.941 | 16.2653 | 18.1993 | 16.7064 | 16.2013 | 18.8587 | 42.4852 | 131.4737 |  | 71.8815 | 105.861 | 106.1603 | 80.0791 |  | 6.7167 | 7.3166 | 6.5324 | 7.3629 | 7.8771 | 11.2544 | 57.5558 | 4.7745 | 7.0617 | 4.4869 | 7.9158 | 8.6456 | 41.841 | 46.3604 | 42.6176 | 14.5299 |  |  | -0.53599 | -0.17076 | 0.092532 | -0.29899 | 0.032364 | 0.58306 | 0.35146 | 0.14112 | -0.31115 | -0.71937 | -0.34008 | -0.00057662 | -0.00058647 | 1.1187 | 15.8357 | 16.6328 | 17.1858 | 17.5081 | 17.4553 | 16.3985 | 14.7465 | 16.7866 | 17.1243 | 17.4145 | 17.4546 | 17.162 | 16.329 | 14.514 | 37.462 | 19.0999 | 27.142 | 19.1462 | 15.9254 | 24.6405 | 16.377 | 15.8397 | 15.492 | 15.4261 | 14.2692 | 14.7614 | 16.1126 |  |  |  | 35.8005 | 131.197 | 98.3068 | 59.8054 | 0.41558 | -0.0099498 | 39.8658 |  |  | 11.1816 |  |  | 16.8803 | 16.5333 | 22.6964 | 16.3227 | 15.8096 | 17.9073 | 120.003 | 149.4543 | 100.2516 | 101.2065 | 73.8851 |  | 40.5409 | 82.3191 | 40.9829 | 59.3832 | 50.2926 | 113.1861 |  | 64.7157 |  |  | 14.4192 | 16.7678 | 44.5999 | [6 empty] | 48.0343 |  |  | 32.2772 |  |  | 15.9395 | 45.8164 | 166.6865 | 9.2629 | 42.8905 | 111.0638 | 10.7944 | 41.2277 | 121.3537 | 19.959 | 93.1046 | 11.2064 | 87.1791 | 12.4071 | 92.4079 | 10.6615 | 43.567 | 103.0576 | 21.2398 | 41.4619 | 130.8865 | 11.7509 | 39.0611 | 122.5019 | 12.6006 | 86.5635 | 18.5937 | 93.9332 | 13.5285 | 98.4418 | 0.86399 | 19.4809 | 1.1962 | 0.089645 | -38.2379 | 3.1232 | 189.16 | 48.74 | -1.0432 | -0.48228 | 0.35502 | -0.63816 | 0.21143 | 0.89741 | 0.69674 | -0.3772 | -0.5961 | 0.36803 | -0.97872 | -0.79769 | -0.48151 | -0.15022
42810.4455 | 469 | 18.3191 | 18.4761 | 18.4891 | 18.4878 | 17.799 | 16.4009 | 14.4596 | 16.5991 | 17.0976 | 17.1813 | 17.1803 | 16.7051 | 15.7185 | 14.3538 | 14.6529 | 14.7374 | 15.3621 | 13.2254 | 13.7932 | 15.7441 |  |  |  | 16.5028 | 16.1081 | 19.976 | 125.375 | 111.9415 | 145.5984 | 16.9486 | 16.2699 | 18.2311 | 16.7116 | 16.2079 | 18.8889 | 42.5866 | 132.2727 |  | 72.1143 | 106.0529 | 106.3321 | 79.3209 |  | 6.7248 | 7.326 | 6.5499 | 7.3812 | 7.9336 | 11.2743 | 57.2847 | 4.8714 | 7.0662 | 4.5084 | 7.9178 | 8.646 | 41.8142 | 46.3604 | 42.6184 | 14.5167 |  |  | -0.40522 | -0.16025 | -0.023776 | 0.003286 | 0.084276 | 0.18879 | 0.36788 | 0.28765 | 0.1376 | -0.52719 | -0.069057 | -0.00060126 | -0.00058812 | 1.399 | 15.8233 | 16.6308 | 17.1754 | 17.4965 | 17.45 | 16.3927 | 14.7355 | 16.7779 | 17.1099 | 17.4118 | 17.4496 | 17.1591 | 16.3214 | 14.5113 | 38.0157 | 19.1563 | 27.0377 | 19.5081 | 16.6401 | 24.696 | 16.4267 | 15.8355 | 15.4898 | 15.4257 | 14.2673 | 14.7653 | 16.1267 |  |  |  | 35.9083 | 131.765 | 98.7645 | 60.2791 | 0.0010618 | 0.11219 | 39.9879 |  |  | 11.1798 |  |  | 16.8827 | 16.5295 | 22.7305 | 16.3251 | 15.8093 | 17.9255 | 120.2594 | 149.7558 | 100.541 | 101.5459 | 73.6065 |  | 40.643 | 81.564 | 41.1145 | 59.6172 | 50.4993 | 112.9368 |  | 64.91 |  |  | 14.4185 | 16.7893 | 44.3745 | [6 empty] | 48.2902 |  |  | 32.4166 |  |  | 15.9467 | 45.8467 | 167.3671 | 9.2826 | 42.7978 | 111.3137 | 10.8214 | 41.1721 | 121.6368 | 19.9934 | 93.3405 | 11.2115 | 87.4017 | 12.4462 | 92.5895 | 10.6699 | 43.7458 | 103.1231 | 21.2723 | 41.4637 | 131.2372 | 11.7459 | 39.1773 | 122.9953 | 12.6245 | 86.7841 | 18.6394 | 94.2329 | 13.5525 | 98.6342 | 1.0215 | 19.4758 | 1.1999 | 0.088328 | -38.2118 | 3.1232 | 198 | 49.04 | -0.9078 | -0.46721 | -0.17996 | 0.066903 | 0.34119 | 0.51067 | 0.71286 | -0.36592 | -0.57055 | 0.36886 | -1.0337 | -0.7803 | -0.45691 | -0.15967
42810.4455 | 470 | 18.3237 | 18.4712 | 18.4875 | 18.4915 | 17.8086 | 16.4004 | 14.4554 | 16.5933 | 17.1002 | 17.186 | 17.1845 | 16.7031 | 15.7198 | 14.3562 | 14.6672 | 14.7423 | 15.371 | 13.2328 | 13.8 | 15.7613 |  |  |  | 16.5195 | 16.1217 | 20.0066 | 125.7264 | 112.1195 | 145.9429 | 16.9575 | 16.2632 | 18.2367 | 16.7099 | 16.2126 | 18.9084 | 42.7015 | 132.8826 |  | 72.2962 | 106.1799 | 106.4803 | 81.5564 |  | 6.7202 | 7.3274 | 6.5536 | 7.3913 | 7.9705 | 11.2701 | 57.9 | 4.8512 | 7.07 | 4.5295 | 7.9178 | 8.6433 | 41.7804 | 46.357 | 42.6044 | 14.5123 |  |  | -0.47948 | 0.059887 | 0.070848 | -0.030226 | -0.050432 | -0.033316 | 0.4934 | -0.1375 | -0.64956 | 0.3374 | -0.086741 | -0.0005799 | -0.00059305 | 1.3038 | 15.8239 | 16.6335 | 17.1743 | 17.5002 | 17.4491 | 16.3951 | 14.7419 | 16.7737 | 17.1132 | 17.4145 | 17.452 | 17.1616 | 16.3171 | 14.5122 | 36.0198 | 18.3902 | 28.0782 | 19.9776 | 17.3261 | 24.7209 | 16.4801 | 15.8322 | 15.5002 | 15.4289 | 14.2758 | 14.7629 | 16.1374 |  |  |  | 36.0228 | 132.2261 | 99.0725 | 60.7469 | 0.22331 | -0.033475 | 40.1409 |  |  | 11.1865 |  |  | 16.8838 | 16.5336 | 22.7729 | 16.3286 | 15.8202 | 17.9388 | 120.4811 | 150.1858 | 100.8253 | 101.9416 | 72.8999 |  | 40.7611 | 81.0295 | 41.2667 | 57.5102 | 50.6844 | 112.1938 |  | 65.1267 |  |  | 14.437 | 16.8063 | 44.3545 | [6 empty] | 47.7276 |  |  | 32.5688 |  |  | 15.9628 | 46.009 | 167.7566 | 9.3053 | 42.6163 | 111.3486 | 10.8353 | 41.2159 | 121.7291 | 20.0207 | 93.5169 | 11.224 | 87.7045 | 12.4698 | 92.7139 | 10.668 | 43.7116 | 103.1013 | 21.3035 | 41.264 | 131.812 | 11.7366 | 39.1446 | 123.4665 | 12.656 | 87.0274 | 18.6861 | 94.3506 | 13.5908 | 98.8902 | 0.89635 | 19.4675 | 1.2051 | 0.088067 | -38.2251 | 3.1233 | 200.22 | 50.28 | -0.98788 | 0.28562 | 0.31066 | -0.20291 | -0.26394 | -0.21452 | 0.82555 | -0.34218 | -0.5504 | 0.43395 | -0.80906 | -0.88969 | -0.515 | -0.16871
42810.4455 | 471 | 18.3183 | 18.4764 | 18.4886 | 18.4929 | 17.7969 | 16.4029 | 14.4639 | 16.6007 | 17.0902 | 17.1878 | 17.1862 | 16.7106 | 15.7194 | 14.3409 | 14.6613 | 14.7375 | 15.3692 | 13.2276 | 13.7947 | 15.768 |  |  |  | 16.5145 | 16.1215 | 20.0251 | 126.0918 | 112.3257 | 146.7721 | 16.9535 | 16.2747 | 18.2464 | 16.7079 | 16.2052 | 18.9295 | 42.875 | 133.6725 |  | 72.4939 | 106.327 | 106.6832 | 83.6469 |  | 6.729 | 7.3283 | 6.5572 | 7.3957 | 8.0197 | 11.2732 | 58.0265 | 4.7927 | 7.0837 | 4.5674 | 7.9213 | 8.6395 | 41.7472 | 46.3564 | 42.5917 | 14.504 |  |  | -0.56753 | -0.010425 | 0.17007 | -0.12682 | 0.040904 | 0.28013 | 0.27852 | -0.038932 | -0.2047 | -0.71454 | -0.073031 | -0.0005454 | -0.0005454 | 1.0868 | 15.8339 | 16.6354 | 17.1764 | 17.5088 | 17.4549 | 16.3963 | 14.743 | 16.7821 | 17.1187 | 17.4146 | 17.4557 | 17.16 | 16.3253 | 14.5179 | 35.1917 | 17.7837 | 27.4628 | 19.864 | 17.6954 | 24.764 | 16.5322 | 15.8362 | 15.4837 | 15.4197 | 14.2686 | 14.7702 | 16.1559 |  |  |  | 36.1349 | 132.6577 | 99.3265 | 61.3287 | 0.39431 | 0.23001 | 40.3377 |  |  | 11.1902 |  |  | 16.8797 | 16.535 | 22.8046 | 16.326 | 15.8141 | 17.9516 | 120.8474 | 150.3757 | 101.0822 | 102.2661 | 73.0365 |  | 40.8868 | 81.0231 | 41.4162 | 57.3341 | 50.8965 | 111.7481 |  | 65.3314 |  |  | 14.447 | 16.81 | 44.43 | [6 empty] | 46.915 |  |  | 32.6859 |  |  | 15.9855 | 46.2035 | 168.8734 | 9.3145 | 43.1404 | 111.4512 | 10.8491 | 41.7329 | 121.8959 | 20.0366 | 93.712 | 11.2343 | 88.0576 | 12.4995 | 92.9048 | 10.6746 | 43.5647 | 103.0887 | 21.3422 | 41.3359 | 132.4745 | 11.7385 | 39.0301 | 123.7603 | 12.6751 | 87.2034 | 18.7217 | 94.6135 | 13.624 | 99.179 | 1.0158 | 19.4664 | 1.2106 | 0.089847 | -38.137 | 3.1233 | 223.63 | 48.75 | -1.0758 | -0.11917 | 0.48132 | -0.41564 | 0.2377 | 0.62205 | 0.62027 | -0.3416 | -0.54501 | 0.44637 | -0.712 | -0.81524 | -0.567 | -0.181
42810.4455 | 472 | 18.3169 | 18.4701 | 18.4856 | 18.48 | 17.7968 | 16.4041 | 14.4598 | 16.5859 | 17.0873 | 17.187 | 17.184 | 16.7089 | 15.7089 | 14.3423 | 14.6676 | 14.7371 | 15.3714 | 13.2309 | 13.7988 | 15.7824 |  |  |  | 16.5115 | 16.1252 | 20.0535 | 126.3551 | 112.639 | 145.8399 | 16.9547 | 16.2677 | 18.2683 | 16.7096 | 16.2126 | 18.9467 | 43.027 | 134.093 |  | 72.7066 | 106.5533 | 106.9491 | 80.8222 |  | 6.7304 | 7.3313 | 6.5466 | 7.3945 | 8.0552 | 11.3104 | 58.0513 | 4.7846 | 7.0845 | 4.6598 | 7.9252 | 8.6482 | 41.7275 | 46.3571 | 42.5837 | 14.5036 |  |  | -0.49919 | -0.082053 | 0.12342 | -0.00723 | -0.006408 | -0.069456 | 0.35803 | -0.11516 | -0.018861 | -1.4637 | -0.15152 | -0.0005799 | -0.00057333 | 1.0631 | 15.839 | 16.6324 | 17.1816 | 17.509 | 17.4539 | 16.4003 | 14.7377 | 16.7842 | 17.1145 | 17.4113 | 17.4519 | 17.1647 | 16.3255 | 14.519 | 36.7122 | 19.0707 | 28.4664 | 19.6423 | 17.9743 | 24.8339 | 16.5902 | 15.827 | 15.4735 | 15.4093 | 14.2537 | 14.7582 | 16.1608 |  |  |  | 36.2451 | 133.4219 | 99.3821 | 61.7155 | 0.29544 | 0.38753 | 40.5278 |  |  | 11.1897 |  |  | 16.8753 | 16.5416 | 22.8369 | 16.3237 | 15.8085 | 17.9663 | 121.4424 | 150.5582 | 101.336 | 102.5448 | 71.7466 |  | 41.0159 | 81.5339 | 41.5439 | 58.0679 | 51.1077 | 111.6735 |  | 65.5034 |  |  | 14.464 | 16.8179 | 44.205 | [6 empty] | 46.9523 |  |  | 32.7397 |  |  | 16.0173 | 46.4044 | 169.4316 | 9.3116 | 43.62 | 111.6151 | 10.8481 | 42.0644 | 122.1388 | 20.061 | 94.0208 | 11.2452 | 88.2775 | 12.5296 | 93.1018 | 10.6793 | 43.5971 | 103.3156 | 21.3669 | 41.6724 | 132.911 | 11.7338 | 39.0411 | 124.0337 | 12.6805 | 87.3028 | 18.7519 | 94.7496 | 13.6556 | 99.4738 | 1.0901 | 19.4596 | 1.216 | 0.090919 | -38.2649 | 3.1232 | 221.02 | 49.38 | -1.0079 | -0.33432 | 0.41002 | -0.09924 | -0.094089 | -0.30977 | 0.70329 | -0.30127 | -0.55475 | 0.43348 | -0.87275 | -0.91998 | -0.48323 | -0.18795
42810.4455 | 473 | 18.3237 | 18.4729 | 18.4815 | 18.4887 | 17.8003 | 16.4077 | 14.4613 | 16.591 | 17.0939 | 17.186 | 17.1897 | 16.708 | 15.7127 | 14.3458 | 14.6647 | 14.7366 | 15.3675 | 13.2309 | 13.7932 | 15.7869 |  |  |  | 16.5048 | 16.126 | 20.0757 | 126.5257 | 113.0831 | 145.4988 | 16.9542 | 16.2681 | 18.2891 | 16.7115 | 16.2072 | 18.9642 | 43.1379 | 134.9676 |  | 72.9295 | 106.7637 | 107.2595 | 80.2204 |  | 6.7428 | 7.3408 | 6.5526 | 7.4024 | 8.0652 | 11.3427 | 58.5311 | 4.8652 | 7.0889 | 4.7103 | 7.9412 | 8.659 | 41.7124 | 46.3756 | 42.5798 | 14.5225 |  |  | -0.52745 | -0.15499 | 0.10896 | -0.080826 | 0.11976 | 0.066568 | 0.50391 | 0.079348 | -0.4425 | -0.19487 | -0.072434 | -0.0005569 | -0.00057826 | 1.2837 | 15.8375 | 16.6366 | 17.1773 | 17.5064 | 17.453 | 16.3999 | 14.7409 | 16.7833 | 17.1158 | 17.4185 | 17.455 | 17.1695 | 16.3229 | 14.5185 | 37.1553 | 19.6891 | 30.0223 | 20.7055 | 19.3785 | 24.8942 | 16.6597 | 15.8361 | 15.4839 | 15.4247 | 14.2728 | 14.7748 | 16.1806 |  |  |  | 36.3795 | 134.0151 | 99.6758 | 61.9762 | 0.3783 | 0.054603 | 40.7353 |  |  | 11.197 |  |  | 16.882 | 16.5508 | 22.8829 | 16.3275 | 15.8192 | 17.9845 | 121.9741 | 150.7668 | 101.553 | 102.7865 | 71.0231 |  | 41.1513 | 81.1297 | 41.6911 | 57.8463 | 51.3748 | 111.9388 |  | 65.7107 |  |  | 14.5149 | 16.8473 | 44.371 | [6 empty] | 47.196 |  |  | 32.7795 |  |  | 16.0495 | 46.4097 | 169.9398 | 9.3321 | 43.571 | 111.7181 | 10.8472 | 41.8299 | 122.1514 | 20.0903 | 94.4648 | 11.2622 | 88.3879 | 12.5344 | 93.3617 | 10.6842 | 43.8372 | 103.6874 | 21.389 | 41.8833 | 133.2665 | 11.7357 | 39.1558 | 124.1668 | 12.6869 | 87.4271 | 18.7866 | 95.0595 | 13.6897 | 99.8433 | 0.75286 | 19.4546 | 1.2209 | 0.090528 | -38.1754 | 3.1232 | 239.49 | 49.87 | -1.0356 | -0.4595 | 0.38527 | -0.33182 | 0.40678 | 0.30327 | 0.83441 | -0.27646 | -0.53839 | 0.44913 | -0.91494 | -1.0847 | -0.46264 | -0.19056
42810.4455 | 474 | 18.3278 | 18.4682 | 18.4826 | 18.487 | 17.8039 | 16.4064 | 14.4619 | 16.5951 | 17.0999 | 17.1865 | 17.1927 | 16.7118 | 15.7177 | 14.3488 | 14.6698 | 14.7382 | 15.3662 | 13.224 | 13.7973 | 15.7911 |  |  |  | 16.5067 | 16.1182 | 20.0972 | 126.7408 | 113.5682 | 145.6502 | 16.958 | 16.2771 | 18.3101 | 16.7111 | 16.207 | 18.9818 | 43.273 | 135.7866 |  | 73.1602 | 106.9579 | 107.5858 | 82.3439 |  | 6.7463 | 7.3516 | 6.5618 | 7.409 | 8.0733 | 11.4177 | 59.6737 | 5.0235 | 7.091 | 4.766 | 7.9425 | 8.6522 | 41.6962 | 46.3811 | 42.5632 | 14.5468 |  |  | -0.25934 | -0.057081 | -0.00932 | -0.19122 | -0.091176 | 0.31167 | 0.41323 | -0.16313 | 0.1446 | -0.21753 | -0.11237 | -0.00053062 | -0.00058647 | 1.3191 | 15.8341 | 16.6351 | 17.1688 | 17.4992 | 17.4498 | 16.4017 | 14.7344 | 16.781 | 17.1215 | 17.4158 | 17.4486 | 17.1579 | 16.3155 | 14.5112 | 36.5873 | 19.3247 | 29.4039 | 20.7883 | 19.9675 | 24.9531 | 16.7169 | 15.8404 | 15.4886 | 15.4342 | 14.2715 | 14.7796 | 16.1943 |  |  |  | 36.4905 | 134.7615 | 100.4429 | 62.3351 | 0.3548 | -0.0067504 | 40.706 |  |  | 11.1986 |  |  | 16.8794 | 16.5495 | 22.9219 | 16.3269 | 15.8195 | 18.0044 | 122.2748 | 151.0364 | 101.75 | 103.0103 | 71.8104 |  | 41.3113 | 79.8609 | 41.826 | 57.4655 | 51.6308 | 113.5201 |  | 65.9729 |  |  | 14.566 | 16.9095 | 44.4746 | [6 empty] | 48.0641 |  |  | 32.7714 |  |  | 16.0745 | 46.4478 | 170.1683 | 9.3405 | 43.5874 | 111.9419 | 10.8494 | 41.7969 | 122.2895 | 20.1198 | 95.2232 | 11.2846 | 88.6423 | 12.5279 | 93.555 | 10.7011 | 44.1395 | 104.0384 | 21.4128 | 41.9167 | 134.1037 | 11.7464 | 39.2528 | 124.3089 | 12.6991 | 87.5442 | 18.8303 | 95.4524 | 13.7247 | 100.1894 | 0.91407 | 19.449 | 1.225 | 0.090788 | -38.1181 | 3.1233 | 228.16 | 49.3 | -0.72628 | -0.27886 | -0.11268 | -0.51039 | -0.35498 | 0.65631 | 0.75571 | -0.29276 | -0.49845 | 0.4688 | -0.84492 | -1.0094 | -0.5169 | -0.19669
42810.4455 | 475 | 18.3235 | 18.4638 | 18.4897 | 18.4827 | 17.8003 | 16.3991 | 14.4478 | 16.5921 | 17.0928 | 17.1836 | 17.1871 | 16.7034 | 15.7182 | 14.3467 | 14.6769 | 14.7461 | 15.3712 | 13.2337 | 13.8013 | 15.8131 |  |  |  | 16.5177 | 16.128 | 20.13 | 126.9862 | 113.6933 | 146.0082 | 16.9575 | 16.2777 | 18.3249 | 16.7104 | 16.2075 | 19.0053 | 43.4246 | 135.4951 |  | 73.384 | 107.0712 | 107.8407 | 83.1183 |  | 6.7468 | 7.3605 | 6.565 | 7.427 | 8.0752 | 11.4452 | 60.7057 | 5.0623 | 7.0972 | 4.7678 | 7.9541 | 8.6515 | 41.666 | 46.3851 | 42.5423 | 14.5689 |  |  | -0.39799 | -0.14777 | 0.04062 | -0.03417 | -0.016264 | 0.3189 | 0.31006 | 0.06752 | -1.7041 | -0.71035 | -0.17059 | -0.00053226 | -0.00057826 | 1.1955 | 15.8515 | 16.6454 | 17.1967 | 17.5172 | 17.4625 | 16.3966 | 14.7444 | 16.7881 | 17.1235 | 17.4206 | 17.4557 | 17.1713 | 16.3321 | 14.5165 | 36.8466 | 19.6595 | 28.9763 | 20.8564 | 19.7273 | 25.0037 | 16.7615 | 15.845 | 15.4865 | 15.4309 | 14.2794 | 14.7886 | 16.2066 |  |  |  | 36.6 | 135.4627 | 101.0346 | 62.6742 | 0.53451 | 0.11219 | 40.734 |  |  | 11.2007 |  |  | 16.872 | 16.5505 | 22.9509 | 16.323 | 15.8258 | 18.0156 | 122.5348 | 151.5443 | 102.0184 | 103.3134 | 72.1293 |  | 41.4471 | 78.3464 | 41.931 | 57.4409 | 51.8961 | 114.6868 |  | 66.1743 |  |  | 14.6001 | 16.9417 | 44.2944 | [6 empty] | 48.3538 |  |  | 32.8472 |  |  | 16.0949 | 46.6925 | 170.0873 | 9.3632 | 43.6327 | 112.2725 | 10.8508 | 42.0574 | 122.6059 | 20.1517 | 95.5478 | 11.3085 | 88.9011 | 12.523 | 93.7865 | 10.7058 | 43.9819 | 104.2906 | 21.4602 | 41.9161 | 135.0013 | 11.7527 | 39.2834 | 124.7874 | 12.7084 | 87.7011 | 18.8765 | 95.4283 | 13.7621 | 100.4018 | 0.73688 | 19.4441 | 1.2288 | 0.08937 | -38.1979 | 3.1232 | 242.01 | 50.13 | -0.90011 | -0.44867 | 0.23524 | -0.21576 | -0.14993 | 0.66391 | 0.65464 | -0.29689 | -0.45272 | 0.47892 | -0.86781 | -0.95666 | -0.53311 | -0.20233
42810.4455 | 476 | 18.3248 | 18.4689 | 18.4905 | 18.4852 | 17.7976 | 16.3947 | 14.4471 | 16.5975 | 17.094 | 17.1867 | 17.187 | 16.7053 | 15.7206 | 14.3471 | 14.6676 | 14.7307 | 15.3638 | 13.2229 | 13.7917 | 15.8138 |  |  |  | 16.5099 | 16.133 | 20.1464 | 127.328 | 114.2447 | 147.2576 | 16.9545 | 16.2718 | 18.3372 | 16.7093 | 16.2143 | 19.0235 | 43.5502 | 135.8721 |  | 73.5828 | 107.1303 | 108.0638 | 82.1208 |  | 6.7577 | 7.3768 | 6.5629 | 7.4484 | 8.09 | 11.4597 | 60.7976 | 5.0428 | 7.1056 | 4.7797 | 7.9649 | 8.6512 | 41.6261 | 46.4048 | 42.5257 | 14.5973 |  |  | -0.50444 | -0.074825 | 0.069532 | 0.02037 | 0.01002 | -0.00046 | 0.3968 | -0.094132 | -0.61317 | -1.1381 | -0.037662 | -0.00057169 | -0.00060619 | 1.2414 | 15.8414 | 16.635 | 17.1828 | 17.4992 | 17.4474 | 16.3969 | 14.7358 | 16.7856 | 17.1184 | 17.4087 | 17.4455 | 17.1609 | 16.3259 | 14.5095 | 38.1726 | 19.2555 | 28.9023 | 21.5547 | 19.9174 | 25.0935 | 16.8143 | 15.8478 | 15.491 | 15.4432 | 14.2833 | 14.7931 | 16.229 |  |  |  | 36.7291 | 136.1936 | 101.5496 | 62.8744 | 0.74075 | 0.12593 | 40.934 |  |  | 11.2067 |  |  | 16.8729 | 16.5537 | 22.99 | 16.3254 | 15.8277 | 18.0347 | 122.7967 | 152.3777 | 102.3464 | 103.6462 | 71.7384 |  | 41.5676 | 78.6454 | 42.0311 | 57.2193 | 52.102 | 115.5587 |  | 66.3533 |  |  | 14.6594 | 16.9827 | 44.254 | [6 empty] | 48.0507 |  |  | 33.0302 |  |  | 16.105 | 46.7689 | 170.1212 | 9.378 | 43.5917 | 112.6047 | 10.8551 | 42.1981 | 122.9641 | 20.1758 | 96.1247 | 11.3082 | 89.0217 | 12.5448 | 94.0443 | 10.6639 | 44.0346 | 104.4914 | 21.521 | 41.9027 | 135.5013 | 11.7766 | 39.2498 | 124.8688 | 12.7273 | 87.8346 | 18.9118 | 95.7717 | 13.8091 | 100.5688 | 0.91657 | 19.4378 | 1.235 | 0.090238 | -38.2559 | 3.1233 | 236.55 | 49.54 | -1.0149 | -0.31928 | 0.30778 | 0.16659 | 0.11769 | -0.025216 | 0.74059 | -0.28183 | -0.45753 | 0.4924 | -1.0046 | -0.94227 | -0.50101 | -0.20344
42810.4456 | 477 | 18.3288 | 18.4727 | 18.4944 | 18.4857 | 17.8042 | 16.3963 | 14.4549 | 16.6013 | 17.1011 | 17.1897 | 17.1862 | 16.7149 | 15.7191 | 14.3438 | 14.6632 | 14.741 | 15.3707 | 13.2283 | 13.7935 | 15.8473 |  |  |  | 16.5162 | 16.1377 | 20.1801 | 127.8141 | 114.8246 | 149.0051 | 16.9586 | 16.271 | 18.3579 | 16.7092 | 16.2207 | 19.042 | 43.6675 | 136.4039 |  | 73.7916 | 107.1915 | 108.3237 | 83.1195 |  | 6.7635 | 7.3931 | 6.5704 | 7.4767 | 8.1261 | 11.4871 | 60.6863 | 5.0295 | 7.103 | 4.7851 | 7.9761 | 8.6566 | 41.5927 | 46.4266 | 42.5211 | 14.6345 |  |  | -0.40719 | -0.11688 | 0.016308 | -0.010514 | 0.13027 | 0.048168 | 0.48617 | -0.043532 | -0.57328 | -0.65643 | -0.034483 | -0.00059962 | -0.0005684 | 1.2717 | 15.8429 | 16.6395 | 17.1808 | 17.5008 | 17.4477 | 16.3961 | 14.7395 | 16.785 | 17.1264 | 17.4176 | 17.4548 | 17.1642 | 16.3286 | 14.5118 | 40.3994 | 19.7651 | 29.5408 | 21.9014 | 19.7241 | 25.2272 | 16.8674 | 15.8482 | 15.4877 | 15.4319 | 14.2761 | 14.798 | 16.2422 |  |  |  | 36.8366 | 137.1071 | 101.5425 | 63.0797 | 0.50918 | 0.11596 | 41.0741 |  |  | 11.2096 |  |  | 16.8793 | 16.5586 | 23.0277 | 16.3245 | 15.823 | 18.0491 | 123.122 | 152.8525 | 102.6375 | 103.9752 | 71.8788 |  | 41.7255 | 79.5183 | 42.18 | 57.0532 | 52.2854 | 114.5855 |  | 66.5558 |  |  | 14.7244 | 17.0139 | 44.0846 | [6 empty] | 47.7721 |  |  | 33.2005 |  |  | 16.1267 | 46.7083 | 170.548 | 9.3903 | 43.5927 | 112.8334 | 10.861 | 42.1248 | 123.2772 | 20.2457 | 96.3752 | 11.308 | 89.2032 | 12.5778 | 94.2427 | 10.6455 | 44.5653 | 104.5796 | 21.576 | 41.8977 | 135.8903 | 11.7502 | 39.4389 | 124.7846 | 12.7384 | 88.1046 | 18.9524 | 96.2655 | 13.8434 | 100.7314 | 0.86958 | 19.433 | 1.2398 | 0.091157 | -38.177 | 3.1232 | 243.43 | 48.84 | -0.9137 | -0.39905 | 0.14906 | -0.11969 | 0.42436 | 0.25804 | 0.8198 | -0.28023 | -0.47659 | 0.50354 | -1.2364 | -1.007 | -0.52465 | -0.20543
42810.4456 | 478 | 18.3337 | 18.4753 | 18.4872 | 18.4961 | 17.8026 | 16.3977 | 14.4538 | 16.5978 | 17.0987 | 17.1959 | 17.1906 | 16.7134 | 15.7141 | 14.3447 | 14.6679 | 14.74 | 15.3723 | 13.2255 | 13.7955 | 15.8522 |  |  |  | 16.5165 | 16.1354 | 20.205 | 128.2199 | 115.5515 | 150.8048 | 16.962 | 16.2799 | 18.362 | 16.7067 | 16.2285 | 19.0685 | 43.8089 | 136.6699 |  | 73.9848 | 107.4437 | 108.5661 | 84.9372 |  | 6.7787 | 7.3968 | 6.5769 | 7.4916 | 8.1735 | 11.4895 | 60.9924 | 4.9952 | 7.1085 | 4.7928 | 7.9791 | 8.6504 | 41.5442 | 46.4612 | 42.5182 | 14.6562 |  |  | -0.4545 | 0.10983 | -0.03232 | -0.051914 | -0.036636 | 0.11125 | 0.53151 | 0.034664 | -0.064397 | -0.17347 | -0.17914 | -0.00056348 | -0.00056676 | 1.1264 | 15.8451 | 16.6418 | 17.1854 | 17.5123 | 17.4563 | 16.395 | 14.7428 | 16.7865 | 17.1216 | 17.4122 | 17.4618 | 17.1692 | 16.3239 | 14.5204 | 40.8361 | 20.5198 | 30.4187 | 21.9783 | 20.0691 | 25.344 | 16.9302 | 15.8442 | 15.4901 | 15.4338 | 14.2697 | 14.8029 | 16.2502 |  |  |  | 36.947 | 137.6711 | 102.0272 | 63.0098 | 0.33495 | 0.19594 | 41.1328 |  |  | 11.2021 |  |  | 16.8746 | 16.5585 | 23.073 | 16.3205 | 15.8207 | 18.0616 | 123.5921 | 153.2462 | 102.8532 | 104.2384 | 71.6927 |  | 41.8351 | 79.4502 | 42.3032 | 58.8051 | 52.5195 | 114.9717 |  | 66.7545 |  |  | 14.7618 | 17.0136 | 44.0285 | [6 empty] | 50.5109 |  |  | 33.3484 |  |  | 16.1498 | 46.7206 | 171.1043 | 9.3914 | 44.1412 | 113.0731 | 10.8581 | 41.9858 | 123.6291 | 20.3136 | 96.6434 | 11.3007 | 89.49 | 12.6127 | 94.4749 | 10.6517 | 44.7303 | 104.8156 | 21.6251 | 42.0094 | 136.3743 | 11.7362 | 39.6263 | 124.9379 | 12.7456 | 88.2355 | 18.9949 | 97.0881 | 13.8763 | 101.1132 | 1.0196 | 19.4284 | 1.2446 | 0.091454 | -38.1421 | 3.1232 | 229.07 | 49.9 | -0.96738 | 0.38683 | -0.20985 | -0.26596 | -0.22504 | 0.39216 | 0.85717 | -0.27124 | -0.4704 | 0.46321 | -1.2712 | -1.0972 | -0.57019 | -0.19967
42810.4456 | 479 | 18.3312 | 18.4775 | 18.4879 | 18.4872 | 17.7998 | 16.397 | 14.4524 | 16.6119 | 17.099 | 17.1839 | 17.1924 | 16.7006 | 15.7137 | 14.3492 | 14.6658 | 14.7373 | 15.3598 | 13.2303 | 13.7891 | 15.861 |  |  |  | 16.5117 | 16.1326 | 20.216 | 128.6859 | 116.107 | 152.2223 | 16.965 | 16.2867 | 18.3961 | 16.7128 | 16.2174 | 19.0935 | 43.9643 | 136.4554 |  | 74.1815 | 107.8883 | 108.8818 | 86.2469 |  | 6.7817 | 7.4062 | 6.5886 | 7.5135 | 8.1913 | 11.4944 | 62.0341 | 4.9816 | 7.1129 | 4.81 | 7.9828 | 8.6616 | 41.5002 | 46.4791 | 42.521 | 14.692 |  |  | -0.39405 | 0.008631 | 0.057048 | 0.010514 | 0.16378 | 0.066568 | 0.47565 | 0.078692 | 0.44643 | -0.28676 | -0.048193 | -0.00061769 | -0.00060947 | 1.1059 | 15.8552 | 16.6435 | 17.1861 | 17.5138 | 17.453 | 16.3937 | 14.7372 | 16.7853 | 17.1167 | 17.4149 | 17.4589 | 17.1644 | 16.3269 | 14.5209 | 42.3594 | 19.6497 | 31.0516 | 21.6505 | 20.1135 | 25.4789 | 16.9843 | 15.8409 | 15.4929 | 15.444 | 14.2762 | 14.8065 | 16.2657 |  |  |  | 37.0618 | 138.4306 | 103.0086 | 62.7527 | 0.77479 | 0.11727 | 41.3367 |  |  | 11.2185 |  |  | 16.8818 | 16.5673 | 23.1186 | 16.3283 | 15.8286 | 18.0842 | 124.1005 | 153.7206 | 103.0602 | 104.5028 | 71.6696 |  | 41.9382 | 79.9269 | 42.4348 | 59.6633 | 52.7483 | 115.8903 |  | 66.9576 |  |  | 14.7855 | 17.0328 | 44.1576 | [6 empty] | 51.5192 |  |  | 33.4602 |  |  | 16.1663 | 46.9462 | 171.8356 | 9.4031 | 44.3942 | 113.361 | 10.8658 | 42.2721 | 123.8326 | 20.3491 | 96.9069 | 11.2941 | 89.7331 | 12.6412 | 94.7569 | 10.6279 | 44.6213 | 104.9555 | 21.6386 | 41.9302 | 137.0267 | 11.7377 | 39.5707 | 125.1588 | 12.7515 | 88.4008 | 19.0412 | 97.367 | 13.914 | 101.5734 | 0.89442 | 19.4232 | 1.2488 | 0.091317 | -38.1043 | 3.1233 | 206.52 | 48.92 | -0.90225 | 0.10844 | 0.2788 | 0.11969 | 0.47583 | 0.30335 | 0.81089 | -0.267 | -0.47904 | 0.44752 | -1.4247 | -1.1613 | -0.60113 | -0.18857
42810.4456 | 480 | 18.3317 | 18.482 | 18.486 | 18.4864 | 17.7969 | 16.3987 | 14.4499 | 16.6029 | 17.0995 | 17.1848 | 17.1908 | 16.7004 | 15.7164 | 14.3428 | 14.6684 | 14.7339 | 15.3583 | 13.2288 | 13.7942 | 15.8833 |  |  |  | 16.5104 | 16.1385 | 20.249 | 129.1212 | 116.6113 | 152.4318 | 16.9616 | 16.2838 | 18.4056 | 16.7062 | 16.223 | 19.1086 | 44.1048 | 136.1505 |  | 74.3533 | 108.2258 | 109.1615 | 86.2951 |  | 6.7838 | 7.4196 | 6.6025 | 7.5371 | 8.2023 | 11.4936 | 62.636 | 4.9456 | 7.1191 | 4.899 | 7.99 | 8.6637 | 41.4568 | 46.4954 | 42.5303 | 14.7104 |  |  | -0.61353 | 0.072371 | 0.074132 | 0.090026 | -0.18843 | 0.40761 | 0.39351 | 0.17594 | 0.63305 | -0.69923 | -0.12092 | -0.00059797 | -0.00058483 | 1.2575 | 15.8522 | 16.6372 | 17.176 | 17.5064 | 17.4478 | 16.392 | 14.73 | 16.7828 | 17.1222 | 17.4158 | 17.455 | 17.1581 | 16.3258 | 14.5166 | 45.7381 | 21.5543 | 31.7734 | 21.4054 | 19.8859 | 25.6665 | 17.0647 | 15.8531 | 15.497 | 15.4438 | 14.2768 | 14.8114 | 16.2891 |  |  |  | 37.179 | 139.2053 | 103.6349 | 62.028 | 0.71725 | 0.65101 | 41.5281 |  |  | 11.2272 |  |  | 16.8869 | 16.5803 | 23.1633 | 16.3314 | 15.8377 | 18.1108 | 124.5657 | 154.0445 | 103.342 | 104.8221 | 71.8672 |  | 42.0781 | 80.0892 | 42.5588 | 58.9467 | 53.0036 | 117.4673 |  | 67.1516 |  |  | 14.7731 | 17.0808 | 44.5422 | [6 empty] | 52.2083 |  |  | 33.5781 |  |  | 16.1979 | 46.9193 | 172.537 | 9.4159 | 43.9606 | 113.7643 | 10.8645 | 42.5166 | 124.0544 | 20.3847 | 97.2368 | 11.3029 | 89.9909 | 12.6847 | 94.9423 | 10.6396 | 44.677 | 105.1212 | 21.6638 | 41.9209 | 137.7767 | 11.7532 | 39.5493 | 125.5587 | 12.7691 | 88.6015 | 19.0699 | 97.8172 | 13.9533 | 101.8452 | 0.89307 | 19.4175 | 1.2523 | 0.089601 | -38.0748 | 3.1232 | 188.61 | 49.21 | -1.1261 | 0.31403 | 0.31783 | 0.35024 | -0.51038 | 0.75065 | 0.73756 | -0.26761 | -0.47922 | 0.47653 | -1.7781 | -1.2321 | -0.59755 | -0.16439
42810.4456 | 481 | 18.327 | 18.4713 | 18.4832 | 18.4847 | 17.7967 | 16.3944 | 14.456 | 16.5982 | 17.0902 | 17.1814 | 17.1818 | 16.6984 | 15.7151 | 14.3459 | 14.6711 | 14.739 | 15.3663 | 13.2265 | 13.8026 | 15.8933 |  |  |  | 16.5117 | 16.1451 | 20.2798 | 129.5348 | 117.2234 | 153.1125 | 16.9554 | 16.2803 | 18.4213 | 16.7027 | 16.219 | 19.1293 | 44.2321 | 136.4494 |  | 74.5328 | 108.4908 | 109.4078 | 85.3413 |  | 6.7722 | 7.432 | 6.592 | 7.535 | 8.2135 | 11.4915 | 62.1959 | 4.8607 | 7.1184 | 4.926 | 7.9953 | 8.6635 | 41.4261 | 46.5089 | 42.5347 | 14.7324 |  |  | -0.51299 | 0.022431 | 0.000536 | 0.12222 | 0.12239 | -0.35399 | 0.31334 | 0.10103 | -0.50283 | -1.6205 | 0.098447 | -0.00056183 | -0.00058976 | 1.3035 | 15.8596 | 16.6376 | 17.1779 | 17.4991 | 17.4494 | 16.3935 | 14.7371 | 16.7785 | 17.1127 | 17.4169 | 17.4501 | 17.158 | 16.3247 | 14.5117 | 47.6865 | 23.2668 | 33.2638 | 22.0822 | 19.8639 | 25.8083 | 17.1491 | 15.8398 | 15.4925 | 15.438 | 14.2767 | 14.8075 | 16.3005 |  |  |  | 37.3044 | 139.9057 | 104.1435 | 61.9681 | 0.68322 | 0.45585 | 41.635 |  |  | 11.225 |  |  | 16.884 | 16.5851 | 23.1944 | 16.3347 | 15.8348 | 18.129 | 125.033 | 154.3748 | 103.6476 | 105.1124 | 71.9392 |  | 42.1949 | 80.4264 | 42.6775 | 60.2155 | 53.2237 | 118.7481 |  | 67.329 |  |  | 14.7856 | 17.1199 | 44.6752 | [6 empty] | 51.8346 |  |  | 33.6386 |  |  | 16.2348 | 46.9636 | 173.0473 | 9.426 | 43.6869 | 114.16 | 10.8649 | 42.4674 | 124.3129 | 20.4192 | 97.4612 | 11.3243 | 90.3769 | 12.7376 | 95.1976 | 10.6535 | 44.8241 | 105.3658 | 21.7151 | 42.0601 | 138.3814 | 11.7637 | 39.6633 | 126.0154 | 12.8063 | 88.811 | 19.1022 | 98.4437 | 13.9974 | 102.068 | 0.90386 | 19.4106 | 1.2572 | 0.089268 | -38.1279 | 3.1233 | 201.95 | 50.11 | -1.0305 | 0.17483 | 0.027026 | 0.4081 | 0.41133 | -0.69954 | 0.65815 | -0.26553 | -0.48445 | 0.44913 | -1.978 | -1.3878 | -0.5666 | -0.15839
42810.4456 | 482 | 18.3336 | 18.4712 | 18.4869 | 18.4882 | 17.8028 | 16.3963 | 14.4574 | 16.5974 | 17.0923 | 17.1885 | 17.1864 | 16.7039 | 15.7185 | 14.3455 | 14.6726 | 14.7385 | 15.3658 | 13.2274 | 13.793 | 15.9037 |  |  |  | 16.5136 | 16.1443 | 20.2997 | 129.9844 | 117.9369 | 153.4623 | 16.9614 | 16.2892 | 18.4442 | 16.7141 | 16.2229 | 19.1585 | 44.4053 | 136.9585 |  | 74.6894 | 108.7713 | 109.6144 | 87.5422 |  | 6.7907 | 7.4474 | 6.6072 | 7.5483 | 8.243 | 11.5273 | 62.4472 | 4.7649 | 7.1321 | 4.9451 | 8.0199 | 8.6609 | 41.4256 | 46.5209 | 42.5275 | 14.7512 |  |  | -0.47093 | 0.012575 | 0.12144 | -0.046654 | 0.071788 | -0.035944 | 0.39811 | 0.018892 | -0.045132 | -0.25214 | 0.051952 | -0.00060126 | -0.00060619 | 1.2551 | 15.8583 | 16.6432 | 17.188 | 17.5124 | 17.456 | 16.394 | 14.7418 | 16.7835 | 17.1213 | 17.4173 | 17.46 | 17.1628 | 16.3295 | 14.512 | 48.5916 | 24.0877 | 33.711 | 23.0496 | 20.6295 | 25.942 | 17.2209 | 15.8491 | 15.5007 | 15.445 | 14.2827 | 14.8231 | 16.3168 |  |  |  | 37.4264 | 140.8241 | 104.7171 | 62.6982 | 0.64391 | 0.31375 | 41.9235 |  |  | 11.2185 |  |  | 16.8816 | 16.5737 | 23.2263 | 16.3223 | 15.835 | 18.1389 | 125.5061 | 154.8437 | 103.9388 | 105.3682 | 72.5056 |  | 42.2978 | 81.4069 | 42.8073 | 61.7691 | 53.4374 | 119.3973 |  | 67.5308 |  |  | 14.8074 | 17.1298 | 44.528 | [6 empty] | 52.0023 |  |  | 33.6397 |  |  | 16.2566 | 47.1543 | 173.4761 | 9.4349 | 43.7431 | 114.473 | 10.8619 | 42.6129 | 124.5233 | 20.4775 | 97.7502 | 11.3602 | 90.6713 | 12.776 | 95.5447 | 10.6611 | 44.7928 | 105.5303 | 21.7572 | 42.3531 | 139.1884 | 11.7553 | 39.7655 | 126.5071 | 12.8178 | 89.0017 | 19.1485 | 98.8232 | 14.0349 | 102.3919 | 0.78965 | 19.4042 | 1.2631 | 0.090781 | -38.1367 | 3.1233 | 214.28 | 48.85 | -0.98779 | 0.13091 | 0.40681 | -0.25215 | 0.31504 | -0.22292 | 0.7419 | -0.27768 | -0.50715 | 0.41359 | -2.0629 | -1.4292 | -0.62167 | -0.17445
42810.4456 | 483 | 18.3408 | 18.4778 | 18.4954 | 18.4896 | 17.8075 | 16.4016 | 14.4582 | 16.6046 | 17.1003 | 17.191 | 17.1945 | 16.7086 | 15.7265 | 14.3481 | 14.6724 | 14.7409 | 15.3693 | 13.2307 | 13.7926 | 15.9221 |  |  |  | 16.5154 | 16.1551 | 20.3286 | 130.5438 | 118.7264 | 154.4497 | 16.9616 | 16.2911 | 18.4642 | 16.7166 | 16.2279 | 19.1771 | 44.5872 | 136.8994 |  | 74.8539 | 109.0406 | 109.8426 | 89.2058 |  | 6.806 | 7.4635 | 6.6047 | 7.5452 | 8.2584 | 11.5661 | 62.7441 | 4.7469 | 7.1359 | 4.8207 | 8.0317 | 8.6648 | 41.4156 | 46.5302 | 42.5348 | 14.7756 |  |  | -0.55242 | -0.16419 | -0.012608 | -0.018398 | 0.008048 | -0.080628 | 0.33174 | -0.075732 | -0.40864 | -0.36543 | -0.055942 | -0.00061769 | -0.00058483 | 1.2605 | 15.863 | 16.6422 | 17.1874 | 17.5098 | 17.4564 | 16.3991 | 14.7414 | 16.7838 | 17.1221 | 17.4154 | 17.4576 | 17.165 | 16.3305 | 14.5141 | 48.751 | 23.1836 | 32.4919 | 23.4291 | 21.4341 | 26.0698 | 17.2779 | 15.8459 | 15.499 | 15.4406 | 14.2793 | 14.8175 | 16.32 |  |  |  | 37.5437 | 141.7098 | 104.7966 | 62.7009 | 0.59529 | 0.025996 | 42.1207 |  |  | 11.2269 |  |  | 16.8792 | 16.5707 | 23.2711 | 16.3181 | 15.8309 | 18.155 | 125.7772 | 155.4872 | 104.2663 | 105.7341 | 72.2831 |  | 42.4222 | 83.0869 | 42.9564 | 60.4971 | 53.6007 | 120.545 |  | 67.7172 |  |  | 14.8396 | 17.1465 | 44.481 | [6 empty] | 50.9751 |  |  | 33.7522 |  |  | 16.275 | 47.3182 | 173.9401 | 9.4658 | 44.0006 | 114.6861 | 10.8634 | 42.8936 | 124.8881 | 20.5406 | 98.0893 | 11.4054 | 90.7651 | 12.816 | 95.9079 | 10.6564 | 44.8719 | 105.6666 | 21.7973 | 42.4995 | 139.6743 | 11.7484 | 39.8332 | 127.0217 | 12.8152 | 89.1992 | 19.2017 | 99.1997 | 14.0757 | 102.5341 | 0.97454 | 19.3998 | 1.2689 | 0.092048 | -38.1188 | 3.1232 | 228.44 | 48.99 | -1.0711 | -0.47304 | -0.13108 | -0.15835 | 0.10549 | -0.3339 | 0.67729 | -0.26716 | -0.54861 | 0.45476 | -2.0656 | -1.287 | -0.6615 | -0.17047
42810.4456 | 484 | 18.3416 | 18.4802 | 18.4962 | 18.4907 | 17.8074 | 16.4031 | 14.4608 | 16.6074 | 17.0982 | 17.202 | 17.1945 | 16.71 | 15.725 | 14.3509 | 14.68 | 14.7415 | 15.3771 | 13.2307 | 13.8025 | 15.9302 |  |  |  | 16.5182 | 16.159 | 20.3549 | 131.0714 | 119.2774 | 154.8236 | 16.9678 | 16.2872 | 18.4752 | 16.7111 | 16.2283 | 19.2007 | 44.7549 | 137.3327 |  | 75.0499 | 109.2898 | 110.1648 | 89.1816 |  | 6.8087 | 7.4733 | 6.6092 | 7.5435 | 8.245 | 11.6197 | 62.3164 | 4.8057 | 7.1316 | 4.686 | 8.0309 | 8.6596 | 41.4034 | 46.536 | 42.5313 | 14.7902 |  |  | -0.38551 | -0.011081 | 0.16022 | 0.3417 | -0.049776 | 0.015968 | 0.33174 | -0.10596 | -0.049608 | -0.32683 | -0.014215 | -0.00057662 | -0.00063412 | 1.2021 | 15.8555 | 16.6355 | 17.1785 | 17.5007 | 17.45 | 16.3932 | 14.7335 | 16.7811 | 17.1189 | 17.4112 | 17.4447 | 17.1551 | 16.3138 | 14.5129 | 49.291 | 23.1986 | 31.2598 | 23.0101 | 21.5042 | 26.2072 | 17.3256 | 15.8482 | 15.4985 | 15.4382 | 14.2763 | 14.8248 | 16.3359 |  |  |  | 37.6603 | 142.8675 | 105.4691 | 62.4476 | 0.48771 | 0.17674 | 42.2806 |  |  | 11.2213 |  |  | 16.8759 | 16.5793 | 23.3086 | 16.3184 | 15.8391 | 18.1771 | 126.2167 | 156.1209 | 104.5908 | 106.0625 | 73.3459 |  | 42.5752 | 84.0963 | 43.1366 | 59.6106 | 53.7579 | 120.4201 |  | 67.9272 |  |  | 14.8696 | 17.1667 | 44.498 | [6 empty] | 50.4242 |  |  | 33.9146 |  |  | 16.3048 | 47.2705 | 174.4817 | 9.497 | 44.1317 | 114.8197 | 10.8693 | 42.8992 | 125.308 | 20.5943 | 98.5173 | 11.4429 | 90.8688 | 12.8406 | 96.2386 | 10.6513 | 45.2622 | 105.8975 | 21.8634 | 42.5783 | 140.2176 | 11.7385 | 39.9887 | 127.2248 | 12.8068 | 89.4023 | 19.249 | 99.7907 | 14.1098 | 102.6981 | 0.88036 | 19.3939 | 1.2731 | 0.091693 | -38.1072 | 3.1233 | 216.13 | 50.26 | -0.89514 | -0.12289 | 0.46728 | 0.68242 | -0.26238 | 0.14861 | 0.67735 | -0.29134 | -0.57035 | 0.48499 | -2.1095 | -1.1446 | -0.65495 | -0.1594
42810.4456 | 485 | 18.334 | 18.4781 | 18.4898 | 18.4885 | 17.8011 | 16.4004 | 14.4559 | 16.5937 | 17.0971 | 17.1918 | 17.1925 | 16.707 | 15.727 | 14.3469 | 14.6796 | 14.7404 | 15.3812 | 13.2349 | 13.8044 | 15.9475 |  |  |  | 16.5257 | 16.1587 | 20.3824 | 131.4761 | 119.5707 | 154.7586 | 16.9625 | 16.2858 | 18.4893 | 16.7112 | 16.2278 | 19.2238 | 44.8864 | 139.0326 |  | 75.2595 | 109.5283 | 110.5236 | 89.4354 |  | 6.8191 | 7.4895 | 6.6179 | 7.5491 | 8.2314 | 11.6288 | 61.9862 | 4.9906 | 7.1358 | 4.6255 | 8.0363 | 8.6674 | 41.3961 | 46.5476 | 42.5254 | 14.8056 |  |  | -0.72129 | -0.020281 | 0.014992 | -0.096594 | 0.1145 | -0.10757 | 0.32386 | -0.018564 | 0.031735 | -0.46572 | 0.01857 | -0.0005684 | -0.00058647 | 1.1887 | 15.8689 | 16.6413 | 17.1841 | 17.5105 | 17.4513 | 16.3979 | 14.7332 | 16.781 | 17.124 | 17.4142 | 17.4562 | 17.1646 | 16.3213 | 14.5179 | 48.7172 | 22.9774 | 31.9446 | 22.6465 | 20.9886 | 26.3429 | 17.387 | 15.8416 | 15.4919 | 15.4392 | 14.2678 | 14.8299 | 16.344 |  |  |  | 37.7697 | 143.8104 | 106.1048 | 62.6383 | 0.6587 | 0.15058 | 42.4935 |  |  | 11.219 |  |  | 16.8783 | 16.595 | 23.3526 | 16.3273 | 15.8438 | 18.1907 | 126.6517 | 156.733 | 104.9225 | 106.3839 | 73.4191 |  | 42.6961 | 84.4427 | 43.2858 | 59.2337 | 53.8995 | 119.2374 |  | 68.0965 |  |  | 14.8575 | 17.199 | 44.7373 | [6 empty] | 49.79 |  |  | 34.0604 |  |  | 16.3213 | 47.3368 | 175.3298 | 9.5381 | 44.2228 | 115.039 | 10.8814 | 42.8238 | 125.662 | 20.6358 | 98.9317 | 11.4515 | 91.0394 | 12.8717 | 96.5446 | 10.6767 | 45.6047 | 106.1461 | 21.9152 | 42.5899 | 140.9227 | 11.7341 | 40.1907 | 127.3353 | 12.8089 | 89.623 | 19.3019 | 100.2508 | 14.1454 | 103.0199 | 0.9002 | 19.3889 | 1.2783 | 0.093148 | -38.159 | 3.1232 | 211.43 | 49.24 | -1.2243 | -0.16626 | 0.14295 | -0.36284 | 0.39795 | -0.38571 | 0.66927 | -0.28915 | -0.57475 | 0.50052 | -2.0299 | -1.2135 | -0.65739 | -0.16092
42810.4457 | 486 | 18.338 | 18.4772 | 18.4772 | 18.4867 | 17.7931 | 16.3997 | 14.45 | 16.6 | 17.0912 | 17.1893 | 17.1896 | 16.7093 | 15.718 | 14.3421 | 14.6729 | 14.7354 | 15.3708 | 13.2251 | 13.7939 | 15.9581 |  |  |  | 16.5136 | 16.1588 | 20.4045 | 131.907 | 119.7904 | 155.309 | 16.9603 | 16.292 | 18.5235 | 16.7093 | 16.2375 | 19.2444 | 45.0181 | 140.8069 |  | 75.5256 | 109.802 | 110.8538 | 88.2207 |  | 6.8229 | 7.503 | 6.6332 | 7.5646 | 8.2096 | 11.5878 | 62.3013 | 5.1698 | 7.1464 | 4.6038 | 8.0542 | 8.6676 | 41.3789 | 46.5718 | 42.5214 | 14.8168 |  |  | -0.59118 | -0.21151 | 0.10502 | 0.089366 | 0.057332 | -0.25674 | 0.47697 | 0.028748 | -0.19575 | -1.0918 | 0.070232 | -0.00055855 | -0.00061112 | 1.1871 | 15.8727 | 16.6489 | 17.1856 | 17.5083 | 17.4545 | 16.4038 | 14.7419 | 16.7821 | 17.1221 | 17.4184 | 17.4545 | 17.1641 | 16.3281 | 14.5184 | 49.8073 | 23.3432 | 32.057 | 22.8811 | 20.843 | 26.5248 | 17.4396 | 15.854 | 15.4929 | 15.4507 | 14.2748 | 14.8305 | 16.3749 |  |  |  | 37.902 | 144.3679 | 106.5102 | 63.0356 | 0.72475 | 0.031642 | 42.5383 |  |  | 11.2133 |  |  | 16.8761 | 16.5929 | 23.3916 | 16.3284 | 15.8392 | 18.2048 | 127.2358 | 157.286 | 105.2215 | 106.6396 | 73.0603 |  | 42.7972 | 83.8366 | 43.4299 | 59.4114 | 54.0493 | 119.4597 |  | 68.2667 |  |  | 14.854 | 17.2323 | 45.4057 | [6 empty] | 49.2524 |  |  | 34.1735 |  |  | 16.3486 | 47.4828 | 176.2281 | 9.5741 | 44.5096 | 115.302 | 10.8986 | 43.0149 | 126.0077 | 20.6887 | 99.2794 | 11.4645 | 91.4141 | 12.8991 | 96.8763 | 10.7081 | 45.7452 | 106.4974 | 21.9678 | 42.6473 | 141.5797 | 11.727 | 40.2988 | 127.5979 | 12.8293 | 89.7835 | 19.3575 | 100.5045 | 14.1761 | 103.2758 | 0.90848 | 19.3818 | 1.2814 | 0.092721 | -38.2124 | 3.1233 | 213.98 | 49.81 | -1.1091 | -0.53692 | 0.37834 | 0.34901 | 0.28157 | -0.59584 | 0.81215 | -0.27565 | -0.55288 | 0.50093 | -2.1297 | -1.2199 | -0.61903 | -0.16737
42810.4457 | 487 | 18.3264 | 18.462 | 18.4791 | 18.4818 | 17.7905 | 16.3911 | 14.4468 | 16.5864 | 17.0853 | 17.1798 | 17.184 | 16.701 | 15.7111 | 14.3501 | 14.6706 | 14.7392 | 15.371 | 13.2232 | 13.8041 | 15.9683 |  |  |  | 16.5071 | 16.164 | 20.4295 | 132.4502 | 120.0896 | 156.7949 | 16.9663 | 16.285 | 18.5328 | 16.7081 | 16.2306 | 19.2573 | 45.1252 | 141.6331 |  | 75.7126 | 110.0753 | 111.1421 | 84.842 |  | 6.8289 | 7.5092 | 6.6341 | 7.5669 | 8.1819 | 11.5435 | 62.3203 | 5.2214 | 7.1482 | 4.6412 | 8.0515 | 8.6678 | 41.3545 | 46.6017 | 42.5247 | 14.8311 |  |  | -0.44793 | -0.075481 | 0.020248 | 0.24707 | 0.039592 | 0.18156 | 0.37774 | 0.096432 | -0.2086 | -0.58048 | 0.17296 | -0.00056183 | -0.0005454 | 1.1203 | 15.8695 | 16.6378 | 17.1807 | 17.5093 | 17.461 | 16.4063 | 14.7377 | 16.784 | 17.1243 | 17.4101 | 17.4525 | 17.1597 | 16.327 | 14.5155 | 51.2581 | 24.4683 | 31.7999 | 22.1237 | 20.6779 | 26.6842 | 17.5069 | 15.8482 | 15.5026 | 15.4451 | 14.2713 | 14.8412 | 16.3847 |  |  |  | 37.9994 | 144.797 | 106.9937 | 62.9396 | 0.41153 | 0.38941 | 42.5815 |  |  | 11.2031 |  |  | 16.8747 | 16.5994 | 23.4283 | 16.3265 | 15.8399 | 18.2228 | 127.7787 | 157.6065 | 105.6475 | 107.0291 | 73.822 |  | 42.9382 | 82.8175 | 43.6067 | 62.3423 | 54.3351 | 120.5276 |  | 68.454 |  |  | 14.8396 | 17.2577 | 45.5798 | [6 empty] | 49.3846 |  |  | 34.3105 |  |  | 16.3853 | 47.5386 | 176.9521 | 9.5834 | 44.7389 | 115.6042 | 10.9136 | 43.3111 | 126.4185 | 20.7379 | 99.6123 | 11.4691 | 91.754 | 12.9276 | 97.0509 | 10.6763 | 45.7959 | 106.753 | 22.0338 | 42.8222 | 141.9698 | 11.7232 | 40.2181 | 128.0716 | 12.8398 | 89.9494 | 19.399 | 100.731 | 14.1869 | 103.4692 | 0.92428 | 19.3767 | 1.2846 | 0.091577 | -38.262 | 3.1233 | 226.7 | 49.77 | -0.96712 | -0.32076 | 0.16613 | 0.58032 | 0.23397 | 0.50103 | 0.72269 | -0.29188 | -0.51839 | 0.42973 | -2.2722 | -1.1834 | -0.52142 | -0.16134
42810.4457 | 488 | 18.3374 | 18.4694 | 18.4823 | 18.4901 | 17.7942 | 16.3938 | 14.4505 | 16.5902 | 17.093 | 17.1872 | 17.1888 | 16.6995 | 15.7199 | 14.3424 | 14.6763 | 14.7458 | 15.3713 | 13.2314 | 13.801 | 15.9822 |  |  |  | 16.5161 | 16.1709 | 20.4591 | 132.9069 | 120.3237 | 157.4594 | 16.9654 | 16.2942 | 18.5508 | 16.7119 | 16.2261 | 19.2834 | 45.2408 | 141.8145 |  | 75.9093 | 110.4718 | 111.4415 | 82.6288 |  | 6.8613 | 7.5201 | 6.6525 | 7.5838 | 8.1736 | 11.5347 | 62.0612 | 5.2195 | 7.1667 | 4.7711 | 8.0692 | 8.6685 | 41.3205 | 46.6169 | 42.5352 | 14.8369 |  |  | -0.306 | -0.26342 | 0.07742 | 0.15442 | 0.002136 | -0.079972 | 0.48551 | -0.28272 | 0.054114 | -0.24669 | 0.045395 | -0.00059469 | -0.00055198 | 1.1134 | 15.876 | 16.6425 | 17.1816 | 17.5164 | 17.4517 | 16.3996 | 14.7406 | 16.7899 | 17.1206 | 17.4158 | 17.4563 | 17.1624 | 16.3265 | 14.5108 | 51.6111 | 24.209 | 33.5895 | 21.7784 | 19.7016 | 26.864 | 17.5921 | 15.8552 | 15.5055 | 15.4543 | 14.2779 | 14.8448 | 16.3998 |  |  |  | 38.1178 | 145.64 | 107.524 | 62.5047 | 0.54646 | 0.42159 | 42.6592 |  |  | 11.2024 |  |  | 16.8784 | 16.6004 | 23.4662 | 16.3257 | 15.8441 | 18.2411 | 128.1807 | 157.9937 | 106.1274 | 107.5183 | 74.4644 |  | 43.0453 | 82.4223 | 43.738 | 62.3888 | 54.5267 | 120.6145 |  | 68.6471 |  |  | 14.8188 | 17.2844 | 45.6336 | [6 empty] | 48.9516 |  |  | 34.3515 |  |  | 16.4143 | 47.5974 | 177.2663 | 9.5917 | 44.7914 | 116.0122 | 10.9121 | 43.2818 | 126.9057 | 20.7848 | 99.9513 | 11.4738 | 92.0587 | 12.9499 | 97.1629 | 10.6267 | 46.2165 | 107.0615 | 22.1095 | 42.9303 | 142.5746 | 11.7313 | 40.17 | 128.2856 | 12.8477 | 90.1428 | 19.4726 | 101.2943 | 14.2076 | 103.7363 | 0.77886 | 19.3723 | 1.2873 | 0.091592 | -38.2874 | 3.1233 | 210.34 | 48.7 | -0.79996 | -0.59922 | 0.32486 | 0.4588 | 0.054344 | -0.33252 | 0.81931 | -0.30598 | -0.50281 | 0.43529 | -2.2903 | -1.3723 | -0.45588 | -0.14516
42810.4457 | 489 | 18.3367 | 18.4728 | 18.4873 | 18.4944 | 17.7995 | 16.397 | 14.4575 | 16.6023 | 17.0981 | 17.1932 | 17.1934 | 16.7039 | 15.7267 | 14.3477 | 14.669 | 14.7412 | 15.374 | 13.224 | 13.8056 | 15.9974 |  |  |  | 16.5143 | 16.1673 | 20.4803 | 133.4157 | 120.4969 | 158.4685 | 16.9649 | 16.2924 | 18.5718 | 16.7082 | 16.2303 | 19.3047 | 45.3435 | 142.1244 |  | 76.1217 | 111.0048 | 111.7235 | 81.0128 |  | 6.8666 | 7.5398 | 6.6655 | 7.6129 | 8.1714 | 11.4943 | 62.6429 | 5.3478 | 7.1844 | 4.9656 | 8.0836 | 8.6824 | 41.2858 | 46.6336 | 42.5486 | 14.8479 |  |  | -0.52416 | -0.070881 | 0.082676 | -0.06111 | 0.1099 | -0.37699 | 0.2772 | 0.14703 | -0.25549 | 0.084377 | -0.074422 | -0.00065219 | -0.00057333 | 1.1865 | 15.867 | 16.6362 | 17.1826 | 17.5111 | 17.445 | 16.3957 | 14.7365 | 16.7824 | 17.1195 | 17.4161 | 17.4445 | 17.1546 | 16.3156 | 14.5106 | 52.2969 | 23.7233 | 34.6441 | 22.488 | 19.2301 | 27.0266 | 17.675 | 15.8526 | 15.4978 | 15.4592 | 14.2882 | 14.8444 | 16.4212 |  |  |  | 38.2403 | 146.6597 | 108.0375 | 62.7688 | 0.49905 | 0.52266 | 42.6396 |  |  | 11.2056 |  |  | 16.8846 | 16.6119 | 23.5116 | 16.3248 | 15.8519 | 18.2698 | 128.5992 | 158.0293 | 106.6248 | 108.0181 | 74.7294 |  | 43.156 | 82.1562 | 43.8513 | 66.4104 | 54.8416 | 121.0213 |  | 68.8764 |  |  | 14.8222 | 17.2881 | 45.8372 | [6 empty] | 53.3892 |  |  | 34.5164 |  |  | 16.4659 | 47.6273 | 177.4771 | 9.5974 | 44.7824 | 116.5557 | 10.9483 | 43.2267 | 127.2608 | 20.8547 | 100.2741 | 11.5021 | 92.2076 | 12.9868 | 97.4668 | 10.5976 | 46.7408 | 107.5583 | 22.1741 | 43.0027 | 143.4633 | 11.7437 | 40.2952 | 128.4371 | 12.858 | 90.362 | 19.5332 | 101.5189 | 14.2415 | 104.0145 | 1.0335 | 19.3681 | 1.2928 | 0.091852 | -38.2352 | 3.1233 | 223.33 | 50.17 | -1.0482 | -0.31085 | 0.33571 | -0.28863 | 0.38978 | -0.72191 | 0.61904 | -0.30948 | -0.49146 | 0.33484 | -2.3475 | -1.4798 | -0.40739 | -0.14825
42810.4457 | 490 | 18.3383 | 18.4747 | 18.4833 | 18.4864 | 17.8009 | 16.398 | 14.4554 | 16.5995 | 17.0943 | 17.19 | 17.1918 | 16.7083 | 15.7255 | 14.3492 | 14.6698 | 14.7366 | 15.3705 | 13.2261 | 13.8015 | 16.0046 |  |  |  | 16.5065 | 16.17 | 20.5106 | 133.797 | 120.7223 | 158.6163 | 16.9691 | 16.287 | 18.5879 | 16.7055 | 16.2326 | 19.3222 | 45.4692 | 142.858 |  | 76.3415 | 111.5167 | 112.0155 | 81.9826 |  | 6.8586 | 7.54 | 6.6777 | 7.6215 | 8.1765 | 11.4549 | 62.7064 | 5.4457 | 7.185 | 5.0855 | 8.0837 | 8.6875 | 41.2684 | 46.6551 | 42.5595 | 14.8588 |  |  | -0.34148 | 0.097999 | 0.030108 | 0.08017 | -0.018236 | -0.038572 | 0.35212 | 0.12534 | 0.30165 | -0.6965 | -0.019978 | -0.00058647 | -0.00060619 | 1.299 | 15.8692 | 16.6485 | 17.1863 | 17.5089 | 17.4519 | 16.3991 | 14.7374 | 16.7812 | 17.1239 | 17.412 | 17.4524 | 17.1605 | 16.3248 | 14.5091 | 52.3702 | 23.9965 | 35.3791 | 23.4045 | 19.3267 | 27.184 | 17.7722 | 15.8506 | 15.4998 | 15.4561 | 14.2782 | 14.8534 | 16.4302 |  |  |  | 38.3715 | 147.4946 | 109.6415 | 63.8934 | 0.71543 | 0.18728 | 42.605 |  |  | 11.1983 |  |  | 16.8735 | 16.61 | 23.5478 | 16.319 | 15.8493 | 18.28 | 128.9923 | 158.3347 | 107.1343 | 108.5247 | 74.6932 |  | 43.2769 | 81.7632 | 43.9799 | 68.0435 | 55.1822 | 120.9757 |  | 69.1124 |  |  | 14.9001 | 17.3366 | 46.071 | [6 empty] | 53.7784 |  |  | 34.7289 |  |  | 16.494 | 47.7702 | 177.8212 | 9.5985 | 44.8115 | 116.8598 | 10.9746 | 43.4918 | 127.6312 | 20.9047 | 100.9975 | 11.5069 | 92.5059 | 13.0181 | 97.6045 | 10.6183 | 46.9789 | 108.0536 | 22.2325 | 43.115 | 144.2452 | 11.7555 | 40.4105 | 129.0494 | 12.8725 | 90.6638 | 19.606 | 101.5794 | 14.2606 | 104.4003 | 1.0876 | 19.3629 | 1.2965 | 0.093068 | -38.1673 | 3.1234 | 199.48 | 49.38 | -0.8462 | 0.3655 | 0.20259 | 0.33059 | -0.15876 | -0.2309 | 0.69764 | -0.30425 | -0.47604 | 0.30167 | -2.3371 | -1.5502 | -0.42991 | -0.17495
42810.4457 | 491 | 18.3356 | 18.471 | 18.4773 | 18.4859 | 17.7986 | 16.3958 | 14.4559 | 16.5929 | 17.097 | 17.1901 | 17.1879 | 16.7036 | 15.7235 | 14.347 | 14.6839 | 14.7436 | 15.3739 | 13.2234 | 13.8185 | 16.0237 |  |  |  | 16.5105 | 16.1711 | 20.535 | 134.3961 | 120.9466 | 159.3591 | 16.9703 | 16.2864 | 18.6061 | 16.7037 | 16.237 | 19.3463 | 45.6061 | 142.9788 |  | 76.5556 | 111.8777 | 112.3548 | 82.1762 |  | 6.8653 | 7.5521 | 6.6825 | 7.6341 | 8.1927 | 11.4316 | 62.7413 | 5.5154 | 7.1892 | 5.1855 | 8.1008 | 8.6873 | 41.2768 | 46.6783 | 42.5616 | 14.8572 |  |  | -0.31323 | -0.22859 | 0.043248 | -0.088054 | 0.000164 | -0.083912 | 0.4888 | 0.001152 | -0.158 | -0.48082 | 0.039434 | -0.00057333 | -0.00055033 | 1.2404 | 15.873 | 16.6493 | 17.184 | 17.5075 | 17.4487 | 16.4006 | 14.738 | 16.7859 | 17.1198 | 17.4146 | 17.4542 | 17.163 | 16.3276 | 14.5136 | 52.4545 | 24.6104 | 34.4234 | 23.7467 | 19.7155 | 27.3277 | 17.8327 | 15.8627 | 15.5041 | 15.4627 | 14.2788 | 14.8636 | 16.4455 |  |  |  | 38.4996 | 147.9952 | 110.1356 | 64.5907 | 0.47575 | 0.048392 | 42.6096 |  |  | 11.1856 |  |  | 16.8728 | 16.6167 | 23.5859 | 16.3224 | 15.8506 | 18.3009 | 129.4652 | 159.1361 | 107.554 | 108.9618 | 75.5389 |  | 43.4372 | 82.2473 | 44.1132 | 64.9864 | 55.4009 | 120.4945 |  | 69.3008 |  |  | 14.9319 | 17.4012 | 45.7126 | [6 empty] | 52.799 |  |  | 34.9519 |  |  | 16.5233 | 48.1492 | 178.2826 | 9.6188 | 44.8641 | 117.4271 | 11.0044 | 43.8661 | 127.8714 | 20.9892 | 101.4932 | 11.5162 | 92.7889 | 13.0285 | 97.8504 | 10.6377 | 47.0843 | 108.4272 | 22.3198 | 43.444 | 144.8678 | 11.759 | 40.3506 | 129.3497 | 12.8894 | 90.9878 | 19.6639 | 101.901 | 14.2798 | 104.8434 | 1.0965 | 19.3597 | 1.3001 | 0.092981 | -38.2225 | 3.1233 | 194.87 | 49.19 | -0.81113 | -0.55824 | 0.24281 | -0.34647 | 0.015055 | -0.34055 | 0.82193 | -0.32213 | -0.48482 | 0.39442 | -2.3297 | -1.4369 | -0.43048 | -0.18988
42810.4457 | 492 | 18.336 | 18.4698 | 18.468 | 18.488 | 17.7912 | 16.3929 | 14.4518 | 16.5886 | 17.0959 | 17.1801 | 17.1844 | 16.7039 | 15.7137 | 14.3447 | 14.6748 | 14.7421 | 15.378 | 13.2241 | 13.8194 | 16.0422 |  |  |  | 16.5111 | 16.1748 | 20.558 | 134.763 | 121.4695 | 157.9922 | 16.9699 | 16.293 | 18.615 | 16.7083 | 16.243 | 19.3658 | 45.7368 | 142.8915 |  | 76.7311 | 112.1795 | 112.6772 | 80.7217 |  | 6.852 | 7.5577 | 6.6807 | 7.6502 | 8.2104 | 11.3979 | 63.3135 | 5.428 | 7.1909 | 5.2505 | 8.1052 | 8.6904 | 41.3205 | 46.7157 | 42.5619 | 14.8563 |  |  | -0.50839 | -0.12739 | 0.12802 | -0.06571 | 0.17562 | -0.16014 | 0.3738 | 0.14966 | -0.32399 | -0.19969 | -0.10443 | -0.00056183 | -0.00059633 | 1.1878 | 15.8638 | 16.6444 | 17.1801 | 17.5016 | 17.4495 | 16.3955 | 14.7307 | 16.7815 | 17.1215 | 17.4134 | 17.4487 | 17.156 | 16.3136 | 14.5126 | 51.8288 | 24.0632 | 33.4431 | 23.4043 | 19.8572 | 27.4512 | 17.8903 | 15.8612 | 15.5094 | 15.4596 | 14.2754 | 14.8654 | 16.4587 |  |  |  | 38.6157 | 148.259 | 110.0748 | 65.4061 | 0.37688 | 0.0005894 | 42.72 |  |  | 11.1759 |  |  | 16.8828 | 16.6211 | 23.6333 | 16.3221 | 15.8586 | 18.3192 | 129.9301 | 159.6573 | 107.8694 | 109.357 | 75.3367 |  | 43.5538 | 84.3427 | 44.2825 | 63.9414 | 55.6236 | 120.8528 |  | 69.4909 |  |  | 14.9653 | 17.4133 | 45.3191 | [6 empty] | 54.0939 |  |  | 35.1136 |  |  | 16.5453 | 48.4578 | 178.9395 | 9.6229 | 45.078 | 117.7731 | 11.0436 | 44.1423 | 128.0889 | 21.0829 | 101.8127 | 11.5223 | 92.8748 | 13.0691 | 98.2838 | 10.6606 | 46.9826 | 108.7374 | 22.3875 | 43.6863 | 145.5445 | 11.7802 | 40.3224 | 129.7568 | 12.9062 | 91.2723 | 19.7212 | 102.2883 | 14.3029 | 105.2014 | 1.0387 | 19.3558 | 1.3029 | 0.091787 | -38.2739 | 3.1233 | 212.03 | 49.69 | -1.0318 | -0.41674 | 0.41776 | -0.2993 | 0.49264 | -0.47043 | 0.71873 | -0.31244 | -0.53709 | 0.43143 | -2.2457 | -1.3213 | -0.38549 | -0.20851
42810.4457 | 493 | 18.3308 | 18.4716 | 18.4843 | 18.4792 | 17.7897 | 16.3912 | 14.4444 | 16.5858 | 17.0926 | 17.1728 | 17.1846 | 16.6976 | 15.7068 | 14.3445 | 14.678 | 14.7407 | 15.3775 | 13.2221 | 13.8104 | 16.0516 |  |  |  | 16.511 | 16.1727 | 20.5801 | 134.989 | 122.0466 | 157.089 | 16.9727 | 16.3012 | 18.641 | 16.7082 | 16.2421 | 19.3876 | 45.8604 | 142.2851 |  | 76.929 | 112.5384 | 113.0514 | 79.3927 |  | 6.8645 | 7.5767 | 6.6914 | 7.6628 | 8.2372 | 11.3987 | 63.0811 | 5.2169 | 7.2025 | 5.2952 | 8.1277 | 8.692 | 41.334 | 46.7174 | 42.556 | 14.8514 |  |  | -0.42953 | -0.10374 | 0.13787 | -0.10514 | 0.061932 | 0.11454 | 0.38234 | 0.13389 | -0.47072 | -0.23494 | -0.11098 | -0.00061769 | -0.00059797 | 1.1493 | 15.8703 | 16.6407 | 17.1792 | 17.5043 | 17.456 | 16.3967 | 14.733 | 16.7867 | 17.121 | 17.4113 | 17.4529 | 17.1548 | 16.3253 | 14.5143 | 49.3931 | 22.848 | 31.6834 | 22.7118 | 19.5477 | 27.5571 | 17.9342 | 15.8546 | 15.5099 | 15.4585 | 14.277 | 14.8723 | 16.4775 |  |  |  | 38.7411 | 148.9688 | 110.0554 | 65.8279 | 0.62446 | -0.087488 | 43.0885 |  |  | 11.1594 |  |  | 16.8823 | 16.6257 | 23.6657 | 16.3283 | 15.8573 | 18.3413 | 130.3836 | 159.9984 | 108.0501 | 109.5971 | 75.2584 |  | 43.6889 | 85.9534 | 44.4491 | 62.7175 | 55.8229 | 121.3235 |  | 69.6715 |  |  | 15.0025 | 17.4593 | 45.1572 | [6 empty] | 53.4386 |  |  | 35.2103 |  |  | 16.5674 | 48.8146 | 179.121 | 9.6453 | 45.5068 | 117.8062 | 11.0699 | 44.224 | 128.5001 | 21.1441 | 102.0186 | 11.5128 | 93.1759 | 13.0949 | 98.3712 | 10.6782 | 47.199 | 109.2522 | 22.449 | 43.7601 | 146.206 | 11.7833 | 40.6316 | 130.0376 | 12.9293 | 91.445 | 19.815 | 102.7989 | 14.3274 | 105.5736 | 0.93834 | 19.3532 | 1.3079 | 0.095493 | -38.2313 | 3.1234 | 239.21 | 48.76 | -0.94737 | -0.37608 | 0.43356 | -0.37861 | 0.29255 | 0.39785 | 0.7269 | -0.30553 | -0.576 | 0.47257 | -1.9626 | -1.1206 | -0.34423 | -0.21588
42810.4458 | 494 | 18.3372 | 18.4714 | 18.479 | 18.4818 | 17.7997 | 16.4019 | 14.4488 | 16.5963 | 17.0912 | 17.1856 | 17.1823 | 16.7093 | 15.7246 | 14.3471 | 14.6803 | 14.7467 | 15.3763 | 13.2273 | 13.8084 | 16.0598 |  |  |  | 16.5085 | 16.1738 | 20.6093 | 135.3689 | 122.4481 | 158.2724 | 16.9785 | 16.306 | 18.6587 | 16.7138 | 16.2476 | 19.4183 | 46.0017 | 142.703 |  | 77.1389 | 112.9908 | 113.4845 | 80.3106 |  | 6.8678 | 7.5787 | 6.691 | 7.6795 | 8.2559 | 11.3909 | 62.2664 | 5.1165 | 7.1972 | 5.3271 | 8.1279 | 8.6917 | 41.3447 | 46.7112 | 42.5419 | 14.8504 |  |  | -0.74035 | -0.081393 | 0.11093 | -0.032198 | 0.18021 | -0.24819 | 0.18258 | 0.034008 | 1.1657 | -0.22529 | -0.096676 | -0.00057169 | -0.0006144 | 1.2405 | 15.8775 | 16.6403 | 17.186 | 17.515 | 17.4536 | 16.3941 | 14.73 | 16.7915 | 17.1207 | 17.4101 | 17.4515 | 17.1606 | 16.3286 | 14.5131 | 49.1514 | 22.6347 | 30.2544 | 21.2417 | 18.5658 | 27.6776 | 17.9702 | 15.8485 | 15.5056 | 15.4564 | 14.2733 | 14.8689 | 16.4852 |  |  |  | 38.8547 | 149.5619 | 110.0757 | 65.8298 | 0.41822 | -0.024818 | 43.316 |  |  | 11.1528 |  |  | 16.8866 | 16.63 | 23.708 | 16.3252 | 15.8615 | 18.3558 | 130.6956 | 160.1936 | 108.1376 | 109.758 | 74.7274 |  | 43.8222 | 87.0744 | 44.6157 | 62.8509 | 56.0629 | 121.6189 |  | 69.8482 |  |  | 15.017 | 17.4747 | 45.0324 | [6 empty] | 53.2361 |  |  | 35.1304 |  |  | 16.5917 | 49.2674 | 179.7505 | 9.6513 | 45.8472 | 118.0224 | 11.0927 | 44.2274 | 128.8187 | 21.2151 | 102.2814 | 11.5099 | 93.6925 | 13.1301 | 98.5395 | 10.6942 | 47.1957 | 109.5949 | 22.5016 | 43.8998 | 147.1849 | 11.7792 | 40.8359 | 130.1882 | 12.9306 | 91.5855 | 19.913 | 103.0833 | 14.3244 | 105.8154 | 0.79793 | 19.3491 | 1.3094 | 0.092786 | -38.2555 | 3.1234 | 245.01 | 49.06 | -1.2455 | -0.33312 | 0.3889 | -0.20952 | 0.49904 | -0.58564 | 0.5023 | -0.28612 | -0.6013 | 0.47747 | -1.9216 | -0.95765 | -0.36476 | -0.21199
42810.4458 | 495 | 18.347 | 18.4769 | 18.4798 | 18.4932 | 17.7932 | 16.3963 | 14.4566 | 16.597 | 17.0941 | 17.1881 | 17.1903 | 16.7038 | 15.7184 | 14.3552 | 14.6879 | 14.7497 | 15.3764 | 13.2314 | 13.8149 | 16.0771 |  |  |  | 16.5088 | 16.1797 | 20.6396 | 135.8187 | 122.7206 | 158.6883 | 16.9787 | 16.3094 | 18.6905 | 16.7091 | 16.2521 | 19.4461 | 46.1491 | 142.7229 |  | 77.3609 | 113.3032 | 113.891 | 82.485 |  | 6.8722 | 7.5965 | 6.6918 | 7.6817 | 8.2736 | 11.3797 | 62.4722 | 5.1815 | 7.2043 | 5.3365 | 8.146 | 8.6956 | 41.3665 | 46.6993 | 42.5566 | 14.8458 |  |  | -0.26526 | 0.008631 | 0.092532 | -0.004598 | 0.18744 | 0.10074 | 0.14907 | 0.2318 | -0.0009576 | -0.6281 | 0.047382 | -0.00063412 | -0.00061604 | 1.3045 | 15.8712 | 16.6396 | 17.1736 | 17.5028 | 17.4481 | 16.3918 | 14.7299 | 16.7796 | 17.1154 | 17.4063 | 17.4494 | 17.1475 | 16.3152 | 14.5032 | 48.4737 | 22.7161 | 30.3352 | 21.4791 | 18.2204 | 27.7955 | 18.024 | 15.8531 | 15.5147 | 15.4639 | 14.2836 | 14.8822 | 16.5059 |  |  |  | 38.9914 | 150.4743 | 110.6718 | 65.51 | 0.5031 | 0.20516 | 43.4647 |  |  | 11.1663 |  |  | 16.8807 | 16.6279 | 23.7528 | 16.3217 | 15.857 | 18.3658 | 131.1475 | 160.4351 | 108.245 | 109.9939 | 74.9395 |  | 43.9516 | 86.6773 | 44.7531 | 62.9463 | 56.2945 | 122.2274 |  | 70.0538 |  |  | 15.0193 | 17.4825 | 45.1702 | [6 empty] | 52.4507 |  |  | 35.1756 |  |  | 16.6262 | 49.6253 | 180.0527 | 9.6483 | 46.0356 | 118.389 | 11.106 | 44.3817 | 129.1321 | 21.2717 | 102.6287 | 11.5314 | 94.0603 | 13.1648 | 98.9233 | 10.7096 | 47.0232 | 109.8465 | 22.5606 | 43.9798 | 147.9186 | 11.7776 | 40.7216 | 130.393 | 12.9287 | 91.7988 | 19.9779 | 103.3441 | 14.3277 | 106.1197 | 1.191 | 19.3445 | 1.3122 | 0.092323 | -38.224 | 3.1233 | 253.51 | 50.55 | -0.74587 | 0.10848 | 0.3552 | -0.079179 | 0.50894 | 0.3731 | 0.45386 | -0.28748 | -0.58545 | 0.48313 | -1.8325 | -0.96034 | -0.41998 | -0.19837
42810.4458 | 496 | 18.3417 | 18.4715 | 18.4752 | 18.4831 | 17.7901 | 16.3894 | 14.4518 | 16.5944 | 17.092 | 17.1858 | 17.1829 | 16.7023 | 15.7158 | 14.343 | 14.6794 | 14.741 | 15.3663 | 13.2276 | 13.8119 | 16.0895 |  |  |  | 16.5079 | 16.182 | 20.6676 | 136.1723 | 123.0898 | 158.4672 | 16.9753 | 16.3053 | 18.7012 | 16.7086 | 16.2492 | 19.4604 | 46.2937 | 142.8769 |  | 77.5688 | 113.4765 | 114.185 | 81.3455 |  | 6.8747 | 7.6035 | 6.7035 | 7.6866 | 8.2684 | 11.357 | 62.6195 | 5.2663 | 7.2136 | 5.2351 | 8.1542 | 8.6894 | 41.3726 | 46.6902 | 42.5628 | 14.8408 |  |  | -0.38879 | -0.16419 | -0.016548 | 0.049282 | 0.11713 | -0.32113 | 0.087296 | 0.1858 | -0.21696 | 0.07053 | 0.019961 | -0.00054212 | -0.00058319 | 1.2581 | 15.8791 | 16.6364 | 17.1737 | 17.5023 | 17.4408 | 16.3938 | 14.7238 | 16.7732 | 17.1156 | 17.4015 | 17.4438 | 17.1492 | 16.3124 | 14.5002 | 46.8955 | 22.4688 | 32.1149 | 22.9344 | 19.1897 | 27.8795 | 18.099 | 15.8527 | 15.5075 | 15.4612 | 14.2781 | 14.8858 | 16.5228 |  |  |  | 39.1212 | 151.1818 | 110.9236 | 65.572 | 0.09446 | 0.35836 | 43.5313 |  |  | 11.1663 |  |  | 16.8818 | 16.6395 | 23.7943 | 16.3204 | 15.8593 | 18.3869 | 131.7857 | 160.4535 | 108.5131 | 110.3543 | 75.5669 |  | 44.0911 | 85.4027 | 44.8936 | 62.9646 | 56.533 | 123.0392 |  | 70.2532 |  |  | 15.0246 | 17.4972 | 45.4731 | [6 empty] | 52.5874 |  |  | 35.2826 |  |  | 16.6717 | 49.8241 | 180.4295 | 9.6379 | 45.9259 | 118.7719 | 11.1183 | 44.655 | 129.5764 | 21.3344 | 102.9406 | 11.5524 | 94.3022 | 13.1794 | 99.2509 | 10.7345 | 47.0314 | 110.0753 | 22.6245 | 44.1457 | 148.1409 | 11.7938 | 40.6152 | 130.4893 | 12.9392 | 92.0028 | 20.0209 | 103.6962 | 14.3501 | 106.5321 | 1.0398 | 19.3414 | 1.3151 | 0.091751 | -38.1513 | 3.1233 | 269.07 | 49.09 | -0.90277 | -0.47315 | -0.15021 | 0.25922 | 0.4023 | -0.66612 | 0.3473 | -0.30003 | -0.54511 | 0.49118 | -1.6473 | -1.1493 | -0.38324 | -0.1956
42810.4458 | 497 | 18.3414 | 18.4715 | 18.4785 | 18.4839 | 17.7949 | 16.3951 | 14.4549 | 16.5965 | 17.0952 | 17.1888 | 17.1809 | 16.7082 | 15.7235 | 14.3471 | 14.672 | 14.7374 | 15.3719 | 13.2225 | 13.8127 | 16.1001 |  |  |  | 16.5073 | 16.1761 | 20.6793 | 136.426 | 123.4924 | 158.5681 | 16.9715 | 16.3045 | 18.7208 | 16.7084 | 16.2525 | 19.4782 | 46.4329 | 143.7191 |  | 77.778 | 113.5872 | 114.4382 | 79.3561 |  | 6.8976 | 7.6211 | 6.6895 | 7.6754 | 8.2632 | 11.3112 | 63.3704 | 5.2002 | 7.214 | 5.1452 | 8.1641 | 8.6891 | 41.3686 | 46.7107 | 42.569 | 14.8343 |  |  | -0.54059 | 0.086827 | 0.14444 | -0.11499 | -0.068176 | -0.21074 | -0.13481 | 0.062264 | -0.65092 | -0.7158 | -0.17914 | -0.00056183 | -0.00059633 | 1.2232 | 15.8811 | 16.6438 | 17.1886 | 17.5007 | 17.4487 | 16.4017 | 14.74 | 16.7772 | 17.126 | 17.4111 | 17.4612 | 17.1645 | 16.3292 | 14.5165 | 43.1545 | 20.9059 | 32.391 | 23.5591 | 20.474 | 27.918 | 18.1783 | 15.8563 | 15.5047 | 15.4599 | 14.279 | 14.8849 | 16.5335 |  |  |  | 39.2369 | 151.8132 | 111.3652 | 65.2141 | 0.064476 | -0.043449 | 43.8084 |  |  | 11.1761 |  |  | 16.8745 | 16.6329 | 23.833 | 16.3265 | 15.8588 | 18.4005 | 132.2732 | 160.7533 | 108.8325 | 110.7637 | 76.0495 |  | 44.2292 | 85.4936 | 45.061 | 65.9549 | 56.9112 | 122.7013 |  | 70.4891 |  |  | 15.0301 | 17.5104 | 46.0794 | [6 empty] | 53.555 |  |  | 35.346 |  |  | 16.6995 | 49.9111 | 180.6309 | 9.6535 | 45.9819 | 119.1436 | 11.1462 | 44.7304 | 130.0182 | 21.413 | 103.2307 | 11.5713 | 94.4376 | 13.2076 | 99.4521 | 10.7379 | 47.0936 | 110.2608 | 22.6884 | 44.4567 | 148.2979 | 11.7973 | 40.8415 | 130.717 | 12.9581 | 92.1285 | 20.0498 | 104.026 | 14.3689 | 106.8065 | 1.0285 | 19.3396 | 1.3201 | 0.091165 | -38.1885 | 3.1233 | 258.64 | 49.29 | -1.0646 | 0.34409 | 0.44381 | -0.39599 | -0.3069 | -0.53957 | -0.43156 | -0.30859 | -0.54177 | 0.4217 | -1.2271 | -1.1708 | -0.32309 | -0.18164
42810.4458 | 498 | 18.3462 | 18.4729 | 18.4866 | 18.4896 | 17.7958 | 16.3948 | 14.4595 | 16.5954 | 17.0978 | 17.1928 | 17.1873 | 16.7085 | 15.7299 | 14.3506 | 14.6831 | 14.7505 | 15.3861 | 13.2279 | 13.8271 | 16.1188 |  |  |  | 16.5126 | 16.1874 | 20.7133 | 136.6943 | 123.8628 | 158.5154 | 16.9827 | 16.316 | 18.7388 | 16.7153 | 16.2645 | 19.5075 | 46.5692 | 144.0262 |  | 78.0086 | 113.7138 | 114.7075 | 78.6965 |  | 6.9096 | 7.6225 | 6.7023 | 7.674 | 8.2578 | 11.2912 | 64.1345 | 5.1165 | 7.2164 | 5.1016 | 8.1782 | 8.6999 | 41.3652 | 46.7621 | 42.5802 | 14.8336 |  |  | -0.50116 | 0.067115 | 0.023536 | -0.36273 | 0.020536 | -0.51235 | 0.10241 | 0.12666 | -0.35221 | 0.12109 | -0.037066 | -0.00058155 | -0.00058483 | 1.0995 | 15.8766 | 16.6396 | 17.1795 | 17.5003 | 17.4424 | 16.3953 | 14.7355 | 16.778 | 17.1161 | 17.4112 | 17.4418 | 17.1502 | 16.3171 | 14.5026 | 40.5332 | 19.3785 | 29.7616 | 23.4509 | 20.6031 | 27.931 | 18.2071 | 15.8584 | 15.5159 | 15.4624 | 14.2803 | 14.8911 | 16.5531 |  |  |  | 39.3681 | 151.9645 | 112.0671 | 65.0034 | -0.011499 | -0.15505 | 44.1551 |  |  | 11.17 |  |  | 16.8794 | 16.6279 | 23.8704 | 16.319 | 15.8537 | 18.4239 | 132.7328 | 161.2356 | 109.0716 | 111.0844 | 76.4169 |  | 44.3657 | 85.333 | 45.212 | 63.2339 | 57.1123 | 122.9088 |  | 70.7079 |  |  | 15.0503 | 17.5278 | 46.2201 | [6 empty] | 53.9156 |  |  | 35.4139 |  |  | 16.7404 | 50.1543 | 181.3941 | 9.6811 | 46.4494 | 119.4931 | 11.1649 | 44.8139 | 130.427 | 21.4869 | 103.5435 | 11.5839 | 94.5463 | 13.2352 | 99.6964 | 10.7454 | 47.1293 | 110.4366 | 22.7754 | 44.6143 | 148.4138 | 11.7989 | 41.0574 | 131.0513 | 12.9883 | 92.3153 | 20.0825 | 104.4758 | 14.3918 | 107.1085 | 1.0995 | 19.3359 | 1.3246 | 0.09267 | -38.1418 | 3.1233 | 246.98 | 49.92 | -1.025 | 0.30252 | 0.17915 | -0.70329 | 0.16843 | -0.84129 | 0.37613 | -0.31402 | -0.53201 | 0.50451 | -0.93431 | -0.87525 | -0.29997 | -0.17123
42810.4458 | 499 | 18.3412 | 18.4728 | 18.4785 | 18.481 | 17.7838 | 16.3883 | 14.4483 | 16.5879 | 17.0845 | 17.1864 | 17.1823 | 16.7076 | 15.7168 | 14.3405 | 14.6829 | 14.7517 | 15.3883 | 13.2238 | 13.8285 | 16.1329 |  |  |  | 16.5135 | 16.1948 | 20.7439 | 136.8621 | 124.2873 | 157.3229 | 16.9744 | 16.3125 | 18.7524 | 16.7139 | 16.2553 | 19.5271 | 46.6793 | 144.3657 |  | 78.221 | 113.9546 | 114.9836 | 80.1547 |  | 6.9143 | 7.6201 | 6.7108 | 7.6649 | 8.2405 | 11.259 | 65.2505 | 4.9966 | 7.2273 | 5.1394 | 8.1822 | 8.7006 | 41.3416 | 46.7934 | 42.5737 | 14.8156 |  |  | -0.60499 | -0.27985 | 0.10436 | -0.27665 | -0.007064 | -0.18905 | 0.093212 | 0.4125 | 0.65737 | -0.057868 | 0.17375 | -0.00053226 | -0.00057169 | 1.066 | 15.8817 | 16.6443 | 17.1813 | 17.5059 | 17.4541 | 16.3969 | 14.7387 | 16.7801 | 17.1234 | 17.4184 | 17.4516 | 17.1526 | 16.323 | 14.5163 | 38.6316 | 18.4399 | 27.5782 | 22.4692 | 20.1625 | 27.9274 | 18.2217 | 15.8442 | 15.5048 | 15.4525 | 14.2691 | 14.8864 | 16.5618 |  |  |  | 39.4776 | 152.2465 | 112.8181 | 65.236 | 0.11128 | -0.1878 | 44.1491 |  |  | 11.1734 |  |  | 16.8831 | 16.6501 | 23.9231 | 16.3206 | 15.8601 | 18.4448 | 132.9964 | 161.4634 | 109.4209 | 111.5022 | 77.3438 |  | 44.5379 | 86.1891 | 45.3681 | 62.0134 | 57.3228 | 122.9655 |  | 70.9178 |  |  | 15.0654 | 17.5657 | 46.7885 | [6 empty] | 54.3423 |  |  | 35.5628 |  |  | 16.7894 | 50.3957 | 182.1477 | 9.6796 | 46.9493 | 119.7004 | 11.175 | 45.0753 | 130.883 | 21.55 | 103.8703 | 11.598 | 94.6869 | 13.2717 | 100.055 | 10.7383 | 47.2745 | 110.6828 | 22.8753 | 44.8552 | 148.5763 | 11.8097 | 41.1131 | 131.38 | 13.0139 | 92.4642 | 20.1159 | 105.0529 | 14.417 | 107.455 | 0.89577 | 19.3301 | 1.3289 | 0.093386 | -38.1698 | 3.1233 | 228.68 | 49.31 | -1.1246 | -0.61773 | 0.37723 | -0.61419 | -0.098779 | -0.51101 | 0.35882 | -0.33373 | -0.55031 | 0.54598 | -0.72345 | -0.63095 | -0.3366 | -0.1739
42810.4458 | 500 | 18.3448 | 18.4737 | 18.4926 | 18.4848 | 17.7874 | 16.3908 | 14.4591 | 16.5993 | 17.0886 | 17.1854 | 17.1814 | 16.7044 | 15.7151 | 14.3449 | 14.6845 | 14.7523 | 15.3818 | 13.2306 | 13.8301 | 16.1457 |  |  |  | 16.5177 | 16.1981 | 20.7748 | 136.9877 | 124.729 | 156.4485 | 16.9786 | 16.3131 | 18.7722 | 16.7102 | 16.2492 | 19.5494 | 46.8077 | 145.1773 |  | 78.4319 | 114.2592 | 115.3017 | 80.6157 |  | 6.9139 | 7.6294 | 6.7172 | 7.6622 | 8.2206 | 11.2154 | 65.5558 | 4.8741 | 7.232 | 5.1321 | 8.1953 | 8.7165 | 41.3268 | 46.8164 | 42.5843 | 14.8134 |  |  | -0.70027 | -0.088621 | 0.080048 | -0.33644 | -0.040576 | -0.003744 | 0.42768 | 0.27451 | -0.082884 | -1.1541 | 0.048773 | -0.00055198 | -0.00058812 | 1.1789 | 15.8838 | 16.6394 | 17.1824 | 17.4992 | 17.4497 | 16.3977 | 14.7331 | 16.7775 | 17.1193 | 17.416 | 17.4524 | 17.1541 | 16.3177 | 14.5097 | 36.2714 | 17.7711 | 25.3896 | 21.1649 | 19.0632 | 27.9252 | 18.2211 | 15.8514 | 15.509 | 15.4612 | 14.2731 | 14.9012 | 16.5784 |  |  |  | 39.6138 | 152.3304 | 112.9669 | 65.6418 | 0.33292 | -0.24313 | 44.3337 |  |  | 11.1897 |  |  | 16.8947 | 16.6563 | 23.9763 | 16.3305 | 15.8691 | 18.4783 | 133.5622 | 161.9236 | 109.8468 | 111.9821 | 78.5331 |  | 44.6981 | 86.5268 | 45.5476 | 63.6226 | 57.6271 | 122.9229 |  | 71.1304 |  |  | 15.0809 | 17.5924 | 47.7086 | [6 empty] | 55.3355 |  |  | 35.5977 |  |  | 16.8282 | 50.3971 | 182.286 | 9.6739 | 46.8403 | 119.9106 | 11.184 | 45.3066 | 131.1967 | 21.6103 | 104.1133 | 11.5913 | 94.8154 | 13.289 | 100.4164 | 10.7203 | 47.6401 | 110.927 | 22.9737 | 45.0372 | 148.819 | 11.8228 | 41.2781 | 131.7516 | 13.028 | 92.6118 | 20.1455 | 105.5364 | 14.4456 | 107.8365 | 0.95355 | 19.3264 | 1.333 | 0.092721 | -38.1388 | 3.1233 | 200.09 | 49.83 | -1.2087 | -0.34763 | 0.33039 | -0.67734 | -0.23672 | -0.071907 | 0.76854 | -0.36115 | -0.55339 | 0.51223 | -0.46147 | -0.38783 | -0.34488 | -0.18044
42810.4458 | 501 | 18.3436 | 18.4756 | 18.4836 | 18.4843 | 17.7916 | 16.3866 | 14.4519 | 16.5864 | 17.091 | 17.1885 | 17.1838 | 16.7069 | 15.7171 | 14.3384 | 14.6892 | 14.7464 | 15.3782 | 13.2372 | 13.8287 | 16.1595 |  |  |  | 16.5148 | 16.2017 | 20.8026 | 137.3361 | 125.0879 | 157.5978 | 16.9743 | 16.3047 | 18.7972 | 16.7039 | 16.2586 | 19.5734 | 46.9544 | 145.9743 |  | 78.6972 | 114.5728 | 115.6386 | 81.8208 |  | 6.9106 | 7.642 | 6.7191 | 7.6619 | 8.2188 | 11.1903 | 65.9125 | 4.7988 | 7.2283 | 5.0633 | 8.2047 | 8.7143 | 41.3148 | 46.8166 | 42.597 | 14.803 |  |  | -0.6753 | -0.001885 | -0.029032 | -0.44749 | 0.08296 | -0.17722 | 0.49274 | 0.1122 | -0.16501 | -1.5376 | -0.037066 | -0.00054705 | -0.0005569 | 1.3081 | 15.8776 | 16.6333 | 17.1835 | 17.496 | 17.4452 | 16.3901 | 14.7272 | 16.7796 | 17.1126 | 17.4082 | 17.4467 | 17.1537 | 16.3166 | 14.5063 | 36.8303 | 18.2846 | 24.0601 | 19.8515 | 18.1891 | 27.9716 | 18.2283 | 15.8565 | 15.5108 | 15.4638 | 14.2729 | 14.9034 | 16.597 |  |  |  | 39.7331 | 152.5512 | 113.0034 | 65.9024 | 0.61251 | -0.046461 | 44.3713 |  |  | 11.1971 |  |  | 16.8859 | 16.6565 | 23.9974 | 16.3258 | 15.8653 | 18.4782 | 133.953 | 162.3887 | 110.2127 | 112.4014 | 78.5883 |  | 44.8596 | 85.2621 | 45.6925 | 62.9237 | 57.9338 | 123.7317 |  | 71.3367 |  |  | 15.0627 | 17.6227 | 48.3304 | [6 empty] | 55.0713 |  |  | 35.7228 |  |  | 16.8568 | 50.4818 | 182.277 | 9.691 | 46.762 | 120.259 | 11.1896 | 45.4084 | 131.5765 | 21.6718 | 104.3244 | 11.5929 | 95.0134 | 13.3142 | 100.6015 | 10.7223 | 48.0669 | 111.2205 | 23.0519 | 45.0841 | 149.315 | 11.8447 | 41.5011 | 132.1664 | 13.0264 | 92.8794 | 20.166 | 106.1045 | 14.4624 | 108.0786 | 0.89307 | 19.3225 | 1.3378 | 0.093842 | -38.2092 | 3.1233 | 213.47 | 49.38 | -1.1886 | -0.050701 | -0.19897 | -0.78118 | 0.33847 | -0.49471 | 0.82488 | -0.35702 | -0.51317 | 0.54269 | -0.51813 | -0.23928 | -0.37319 | -0.18354
42810.4458 | 502 | 18.3432 | 18.4735 | 18.4848 | 18.4802 | 17.791 | 16.3855 | 14.4428 | 16.5901 | 17.09 | 17.1875 | 17.1855 | 16.7113 | 15.7252 | 14.3444 | 14.6858 | 14.7517 | 15.3861 | 13.233 | 13.8418 | 16.1783 |  |  |  | 16.5154 | 16.2034 | 20.8194 | 137.74 | 125.4572 | 158.8075 | 16.9715 | 16.3117 | 18.8095 | 16.7105 | 16.2674 | 19.6007 | 47.0994 | 146.6231 |  | 78.9188 | 114.943 | 115.9974 | 80.7243 |  | 6.9272 | 7.6538 | 6.7354 | 7.6868 | 8.2267 | 11.1906 | 65.6163 | 4.8283 | 7.2441 | 4.9941 | 8.2223 | 8.7104 | 41.3044 | 46.8021 | 42.6028 | 14.8044 |  |  | -0.56818 | -0.098481 | 0.07216 | -0.13865 | 0.027104 | -0.24162 | 0.27655 | 0.081976 | -0.30356 | 0.033186 | -0.0088505 | -0.00058483 | -0.00057169 | 1.2686 | 15.8811 | 16.6362 | 17.1813 | 17.502 | 17.4433 | 16.3821 | 14.7295 | 16.771 | 17.1081 | 17.4047 | 17.4461 | 17.1517 | 16.3205 | 14.5059 | 39.5454 | 19.0736 | 24.4315 | 19.1575 | 17.5516 | 28.0359 | 18.2426 | 15.8574 | 15.5086 | 15.4627 | 14.2784 | 14.9071 | 16.6111 |  |  |  | 39.8505 | 152.8654 | 113.7125 | 65.8033 | 0.85482 | 0.065142 | 44.5965 |  |  | 11.1872 |  |  | 16.8813 | 16.6602 | 24.0345 | 16.3259 | 15.8696 | 18.5053 | 134.5538 | 162.8936 | 110.6112 | 112.8316 | 78.6727 |  | 44.991 | 84.038 | 45.804 | 61.0379 | 58.1079 | 125.0925 |  | 71.55 |  |  | 15.0561 | 17.6419 | 48.2916 | [6 empty] | 55.134 |  |  | 35.8891 |  |  | 16.8897 | 50.9496 | 182.6823 | 9.7066 | 47.0342 | 120.629 | 11.2008 | 45.5517 | 131.9046 | 21.7263 | 104.6899 | 11.6015 | 95.3067 | 13.3425 | 100.7427 | 10.7306 | 48.2809 | 111.6563 | 23.1138 | 45.3191 | 149.8065 | 11.8558 | 41.6115 | 132.4393 | 13.0191 | 93.1445 | 20.1883 | 106.5316 | 14.4658 | 108.18 | 0.96549 | 19.3175 | 1.3413 | 0.092641 | -38.1066 | 3.1233 | 206.7 | 48.91 | -1.0918 | -0.36648 | 0.3137 | -0.43484 | 0.19347 | -0.57763 | 0.61798 | -0.35476 | -0.47525 | 0.60134 | -0.81226 | -0.27887 | -0.33763 | -0.17671
42810.4459 | 503 | 18.3476 | 18.476 | 18.4857 | 18.4826 | 17.7893 | 16.3907 | 14.4455 | 16.5902 | 17.0909 | 17.1872 | 17.195 | 16.7126 | 15.7257 | 14.3414 | 14.6882 | 14.7539 | 15.3873 | 13.2338 | 13.84 | 16.1858 |  |  |  | 16.5103 | 16.2076 | 20.8512 | 138.2514 | 125.8984 | 160.5353 | 16.9802 | 16.3188 | 18.8286 | 16.7107 | 16.2717 | 19.6249 | 47.2082 | 147.4175 |  | 79.1656 | 115.3105 | 116.2796 | 79.1443 |  | 6.9441 | 7.6636 | 6.7307 | 7.6924 | 8.2218 | 11.164 | 65.9342 | 4.8079 | 7.251 | 4.8768 | 8.2265 | 8.7118 | 41.3051 | 46.7945 | 42.609 | 14.8065 |  |  | -0.5925 | -0.12082 | -0.004064 | -0.25167 | 0.08756 | 0.068536 | 0.30743 | 0.19368 | -0.29325 | -0.080106 | -0.097272 | -0.00056676 | -0.00059797 | 1.2458 | 15.8808 | 16.6476 | 17.1785 | 17.5068 | 17.4481 | 16.3921 | 14.7304 | 16.7813 | 17.1192 | 17.4069 | 17.4409 | 17.1563 | 16.3188 | 14.5085 | 43.0782 | 21.115 | 25.9668 | 19.1963 | 17.7867 | 28.1594 | 18.2863 | 15.8526 | 15.5155 | 15.4728 | 14.2721 | 14.9135 | 16.6251 |  |  |  | 39.9683 | 153.0606 | 114.3935 | 65.6164 | 0.7675 | 0.37831 | 44.5881 |  |  | 11.2011 |  |  | 16.8828 | 16.6673 | 24.0802 | 16.3244 | 15.8742 | 18.5062 | 134.997 | 163.0565 | 110.8928 | 113.1928 | 77.8601 |  | 45.1502 | 83.398 | 45.9543 | 60.9231 | 58.2971 | 125.5197 |  | 71.7766 |  |  | 15.0656 | 17.6735 | 48.1223 | [6 empty] | 54.0027 |  |  | 36.0059 |  |  | 16.9375 | 51.3913 | 183.4976 | 9.7185 | 47.1098 | 120.9938 | 11.2216 | 45.8284 | 132.366 | 21.7857 | 105.0031 | 11.6389 | 95.6362 | 13.3482 | 100.9333 | 10.749 | 48.1946 | 112.0799 | 23.1706 | 45.4607 | 150.2703 | 11.8594 | 41.6719 | 132.6717 | 13.0575 | 93.4477 | 20.2144 | 106.9309 | 14.4828 | 108.4689 | 0.91022 | 19.3125 | 1.3463 | 0.091845 | -38.1459 | 3.1233 | 199.36 | 50.21 | -1.1171 | -0.40593 | -0.074448 | -0.58586 | 0.34771 | 0.30763 | 0.65154 | -0.3266 | -0.45219 | 0.61134 | -1.1903 | -0.44436 | -0.28991 | -0.16742
42810.4459 | 504 | 18.3556 | 18.4743 | 18.4815 | 18.4835 | 17.7928 | 16.3959 | 14.4471 | 16.5965 | 17.0943 | 17.1873 | 17.1887 | 16.714 | 15.7266 | 14.344 | 14.6837 | 14.7493 | 15.381 | 13.2378 | 13.8396 | 16.1984 |  |  |  | 16.514 | 16.2083 | 20.8769 | 138.6969 | 126.1826 | 160.028 | 16.9886 | 16.3153 | 18.8523 | 16.7123 | 16.2638 | 19.6471 | 47.3151 | 148.5121 |  | 79.4519 | 115.7018 | 116.5284 | 79.3117 |  | 6.9572 | 7.68 | 6.7422 | 7.699 | 8.2186 | 11.125 | 65.6268 | 4.7684 | 7.2586 | 4.7686 | 8.2343 | 8.7169 | 41.2976 | 46.7992 | 42.6408 | 14.8142 |  |  | -0.64441 | 0.054627 | 0.17139 | -0.10054 | 0.1651 | 0.004796 | 0.42046 | -0.15853 | 0.34271 | -0.56118 | -0.032496 | -0.00060126 | -0.00056348 | 1.1196 | 15.8934 | 16.6517 | 17.1826 | 17.5082 | 17.454 | 16.4038 | 14.737 | 16.7801 | 17.121 | 17.4139 | 17.4516 | 17.1614 | 16.3226 | 14.5137 | 45.9907 | 22.3285 | 28.7635 | 19.7731 | 17.544 | 28.3284 | 18.3474 | 15.8529 | 15.5145 | 15.4761 | 14.28 | 14.9111 | 16.6371 |  |  |  | 40.0915 | 153.2027 | 114.5817 | 65.5112 | 0.65728 | 0.34161 | 44.6283 |  |  | 11.2029 |  |  | 16.8761 | 16.669 | 24.1249 | 16.3219 | 15.8807 | 18.5411 | 135.651 | 163.1076 | 111.2648 | 113.4118 | 78.8026 |  | 45.3148 | 84.4795 | 46.1362 | 64.8396 | 58.6345 | 124.4328 |  | 71.997 |  |  | 15.0665 | 17.6968 | 47.9484 | [6 empty] | 55.6772 |  |  | 36.0681 |  |  | 16.9866 | 51.3243 | 184.4741 | 9.7017 | 47.1532 | 121.4081 | 11.2408 | 46.0235 | 133.0803 | 21.8996 | 105.127 | 11.6541 | 95.8793 | 13.3761 | 101.1843 | 10.7846 | 48.1989 | 112.39 | 23.2046 | 45.5708 | 151.1162 | 11.8613 | 41.9223 | 132.8511 | 13.0843 | 93.7969 | 20.2553 | 107.126 | 14.5082 | 108.9238 | 1.0025 | 19.3068 | 1.3521 | 0.093386 | -38.1265 | 3.1233 | 212.44 | 49.08 | -1.1643 | 0.27296 | 0.48348 | -0.3703 | 0.47743 | 0.081372 | 0.7619 | -0.347 | -0.47584 | 0.51472 | -1.4941 | -0.74797 | -0.29079 | -0.16022
42810.4459 | 505 | 18.3424 | 18.4729 | 18.4736 | 18.479 | 17.7874 | 16.3927 | 14.4389 | 16.5878 | 17.0907 | 17.18 | 17.1882 | 16.7082 | 15.7197 | 14.3431 | 14.6857 | 14.747 | 15.3807 | 13.2334 | 13.8389 | 16.2133 |  |  |  | 16.508 | 16.2038 | 20.8994 | 138.9972 | 126.4816 | 160.8812 | 16.9889 | 16.3183 | 18.8682 | 16.7068 | 16.2644 | 19.6652 | 47.4423 | 148.8983 |  | 79.7009 | 116.1085 | 116.8101 | 80.0398 |  | 6.9662 | 7.691 | 6.7626 | 7.7126 | 8.2335 | 11.1247 | 64.911 | 4.7603 | 7.2641 | 4.6945 | 8.2538 | 8.725 | 41.2981 | 46.7934 | 42.6585 | 14.8176 |  |  | -0.82906 | -0.12542 | 0.11093 | -0.13734 | 0.049448 | -0.14765 | 0.45002 | 0.038604 | 0.050417 | 1.7921 | -0.073627 | -0.00054869 | -0.00058647 | 1.0915 | 15.8787 | 16.6384 | 17.1689 | 17.4965 | 17.4438 | 16.3902 | 14.7217 | 16.7716 | 17.1056 | 17.4042 | 17.4409 | 17.1493 | 16.3123 | 14.4977 | 47.8442 | 21.793 | 29.3726 | 20.2663 | 18.4213 | 28.4833 | 18.4048 | 15.8535 | 15.5183 | 15.4716 | 14.2802 | 14.918 | 16.6599 |  |  |  | 40.227 | 153.5742 | 115.0376 | 65.8337 | 0.40565 | -0.029146 | 44.6709 |  |  | 11.2065 |  |  | 16.8725 | 16.6693 | 24.1627 | 16.3167 | 15.8698 | 18.5596 | 136.326 | 163.7767 | 111.577 | 113.7187 | 79.0884 |  | 45.437 | 85.381 | 46.2931 | 65.7875 | 58.9319 | 124.7693 |  | 72.2099 |  |  | 15.0792 | 17.7064 | 48.1437 | [6 empty] | 56.3302 |  |  | 36.2221 |  |  | 17.021 | 51.2597 | 185.7107 | 9.6903 | 47.3853 | 122.0232 | 11.2717 | 46.1646 | 133.4722 | 21.9591 | 105.3896 | 11.6403 | 96.0664 | 13.3914 | 101.3649 | 10.8225 | 48.4352 | 112.7193 | 23.2722 | 45.7471 | 151.7247 | 11.8742 | 42.1762 | 133.0989 | 13.0994 | 94.0422 | 20.3247 | 107.2139 | 14.5347 | 109.227 | 1.0614 | 19.3002 | 1.3578 | 0.094262 | -38.1009 | 3.1234 | 210.94 | 48.84 | -1.322 | -0.4136 | 0.38898 | -0.43281 | 0.26128 | -0.4515 | 0.78823 | -0.35065 | -0.49536 | 0.49911 | -1.6819 | -0.80894 | -0.30653 | -0.16447
42810.4459 | 506 | 18.3506 | 18.4736 | 18.4822 | 18.4852 | 17.7911 | 16.3948 | 14.4418 | 16.5881 | 17.0873 | 17.1795 | 17.1963 | 16.7104 | 15.7222 | 14.346 | 14.6961 | 14.758 | 15.396 | 13.2325 | 13.8491 | 16.2309 |  |  |  | 16.5226 | 16.2119 | 20.9397 | 139.5906 | 126.8337 | 162.9905 | 16.9787 | 16.3251 | 18.8899 | 16.7108 | 16.2696 | 19.6877 | 47.596 | 149.4983 |  | 79.9341 | 116.5256 | 117.1198 | 82.2873 |  | 6.9698 | 7.6882 | 6.7634 | 7.714 | 8.2589 | 11.19 | 65.6948 | 4.8012 | 7.2646 | 4.679 | 8.2623 | 8.7255 | 41.3009 | 46.7889 | 42.6794 | 14.8296 |  |  | -0.77518 | -0.005825 | 0.08596 | 0.044686 | 0.097416 | 0.11454 | 0.44674 | -0.061276 | -0.26951 | -0.14493 | -0.11158 | -0.00058976 | -0.00057826 | 1.0954 | 15.8801 | 16.644 | 17.1788 | 17.4974 | 17.4454 | 16.3948 | 14.7286 | 16.7701 | 17.111 | 17.4035 | 17.4434 | 17.1551 | 16.3162 | 14.5002 | 46.4731 | 20.4692 | 28.6109 | 19.4631 | 18.9348 | 28.5535 | 18.4463 | 15.8455 | 15.5134 | 15.4727 | 14.2779 | 14.9177 | 16.6753 |  |  |  | 40.3449 | 154.228 | 115.26 | 66.1542 | 0.33211 | -0.25555 | 44.9992 |  |  | 11.209 |  |  | 16.8833 | 16.6752 | 24.2055 | 16.3252 | 15.8734 | 18.5787 | 136.7414 | 164.2618 | 111.9554 | 114.0449 | 79.1324 |  | 45.5598 | 86.196 | 46.441 | 64.8812 | 59.1374 | 127.0838 |  | 72.465 |  |  | 15.0916 | 17.7625 | 47.7813 | [6 empty] | 56.0594 |  |  | 36.3704 |  |  | 17.0716 | 51.728 | 185.7631 | 9.7093 | 47.5038 | 122.4934 | 11.3024 | 46.4681 | 133.8228 | 22.0176 | 105.7722 | 11.6064 | 96.5102 | 13.4096 | 101.7527 | 10.8157 | 48.5675 | 112.8967 | 23.3444 | 45.9565 | 152.0034 | 11.8921 | 42.0294 | 133.3856 | 13.1244 | 94.3987 | 20.3313 | 107.3124 | 14.5518 | 109.5301 | 1.2731 | 19.2941 | 1.363 | 0.094783 | -38.1791 | 3.1233 | 184.03 | 50.31 | -1.2814 | -0.089134 | 0.34241 | 0.24688 | 0.36678 | 0.3977 | 0.78544 | -0.34756 | -0.5128 | 0.53171 | -1.5213 | -0.71947 | -0.36354 | -0.16927
42810.4459 | 507 | 18.3512 | 18.4748 | 18.4937 | 18.4962 | 17.7944 | 16.4043 | 14.4519 | 16.5966 | 17.0962 | 17.1904 | 17.1976 | 16.7133 | 15.7201 | 14.3511 | 14.6919 | 14.7492 | 15.3922 | 13.2258 | 13.8498 | 16.251 |  |  |  | 16.5138 | 16.2104 | 20.968 | 140.2226 | 127.4238 | 163.4419 | 16.9834 | 16.3183 | 18.9048 | 16.71 | 16.2764 | 19.7093 | 47.7622 | 149.2573 |  | 80.1641 | 116.9316 | 117.3959 | 81.959 |  | 6.9809 | 7.6877 | 6.7603 | 7.7199 | 8.2678 | 11.2504 | 65.5442 | 4.9571 | 7.2655 | 4.6288 | 8.2618 | 8.7335 | 41.3222 | 46.808 | 42.7054 | 14.8321 |  |  | -0.59447 | 0.001403 | 0.20096 | -0.16165 | -0.029408 | -0.23308 | 0.54005 | 0.11352 | -0.18933 | 0.0084292 | 0.11077 | -0.00054048 | -0.0005569 | 1.035 | 15.8861 | 16.6423 | 17.1784 | 17.4968 | 17.4454 | 16.3875 | 14.7319 | 16.7735 | 17.1103 | 17.4101 | 17.4419 | 17.1505 | 16.3131 | 14.5004 | 45.384 | 19.7692 | 27.4149 | 18.9785 | 18.6785 | 28.6234 | 18.4611 | 15.8441 | 15.5097 | 15.4698 | 14.2759 | 14.9171 | 16.6846 |  |  |  | 40.454 | 154.4732 | 115.4567 | 65.9782 | 0.61393 | 0.18484 | 45.0424 |  |  | 11.2136 |  |  | 16.8713 | 16.6765 | 24.2423 | 16.3146 | 15.8785 | 18.5913 | 137.2312 | 164.9135 | 112.3581 | 114.4107 | 80.4725 |  | 45.7364 | 87.5079 | 46.6058 | 68.1906 | 59.4235 | 129.5901 |  | 72.7416 |  |  | 15.0726 | 17.7801 | 47.5629 | [6 empty] | 58.2974 |  |  | 36.4774 |  |  | 17.1238 | 52.1859 | 185.6235 | 9.7452 | 47.6252 | 122.6556 | 11.3352 | 46.7564 | 134.2616 | 22.0825 | 106.4089 | 11.6156 | 96.7998 | 13.4406 | 102.3055 | 10.8055 | 49.1125 | 113.1859 | 23.4171 | 46.1675 | 152.2179 | 11.922 | 41.958 | 134.0842 | 13.1462 | 94.7053 | 20.3632 | 107.9073 | 14.584 | 109.8238 | 1.1567 | 19.2871 | 1.3668 | 0.092294 | -38.1427 | 3.1234 | 183.78 | 49.1 | -1.1227 | 0.043745 | 0.52353 | -0.46955 | -0.20154 | -0.56739 | 0.86367 | -0.37858 | -0.54344 | 0.45011 | -1.3921 | -0.58485 | -0.34856 | -0.16059
42810.4459 | 508 | 18.3557 | 18.4847 | 18.4856 | 18.494 | 17.795 | 16.3977 | 14.4504 | 16.6058 | 17.0994 | 17.1952 | 17.1914 | 16.7137 | 15.7287 | 14.3608 | 14.6981 | 14.7574 | 15.3989 | 13.2284 | 13.862 | 16.2689 |  |  |  | 16.516 | 16.2205 | 20.989 | 140.7847 | 127.7217 | 164.2017 | 16.9824 | 16.3327 | 18.9378 | 16.7132 | 16.2781 | 19.7433 | 47.9071 | 150.5387 |  | 80.4396 | 117.2865 | 117.6187 | 79.2808 |  | 6.9823 | 7.6933 | 6.774 | 7.7377 | 8.2912 | 11.2907 | 64.7109 | 4.9908 | 7.2765 | 4.6333 | 8.2765 | 8.7266 | 41.3302 | 46.8225 | 42.7245 | 14.8305 |  |  | -0.68055 | -0.055765 | 0.061648 | -0.00723 | 0.04682 | 0.019912 | 0.72864 | 0.1168 | -0.075879 | -0.26809 | 0.047382 | -0.00057826 | -0.00056183 | 1.0737 | 15.8883 | 16.6459 | 17.1811 | 17.5029 | 17.4501 | 16.4012 | 14.7387 | 16.7764 | 17.1195 | 17.4162 | 17.452 | 17.161 | 16.3188 | 14.5049 | 46.7054 | 21.6697 | 29.1422 | 20.4997 | 18.4614 | 28.7678 | 18.524 | 15.8516 | 15.5135 | 15.4733 | 14.2728 | 14.9281 | 16.702 |  |  |  | 40.5763 | 154.7904 | 115.6988 | 66.3418 | 0.7286 | 0.31677 | 45.2067 |  |  | 11.2276 |  |  | 16.8757 | 16.6836 | 24.289 | 16.3322 | 15.8758 | 18.6206 | 137.8664 | 165.4259 | 112.8443 | 114.7683 | 80.6721 |  | 45.8695 | 88.0898 | 46.7403 | 70.2459 | 59.7277 | 129.2057 |  | 72.9285 |  |  | 15.0374 | 17.7989 | 48.0093 | [6 empty] | 58.7705 |  |  | 36.5671 |  |  | 17.1639 | 52.3826 | 186.0388 | 9.7551 | 47.7525 | 122.8551 | 11.3328 | 46.7711 | 134.5154 | 22.1308 | 107.4938 | 11.6207 | 97.1324 | 13.4671 | 102.5967 | 10.7978 | 49.6578 | 113.7518 | 23.5047 | 46.1121 | 153.2251 | 11.9441 | 42.1991 | 134.4798 | 13.1607 | 94.9506 | 20.3953 | 108.4188 | 14.6315 | 109.9945 | 1.1307 | 19.2826 | 1.3722 | 0.091729 | -38.1705 | 3.1234 | 192.6 | 49.1 | -1.2023 | -0.27579 | 0.28997 | -0.099304 | 0.25432 | 0.16585 | 1.0033 | -0.37945 | -0.55487 | 0.40401 | -1.5219 | -0.76943 | -0.26905 | -0.16644
42810.4459 | 509 | 18.3458 | 18.4694 | 18.4777 | 18.4762 | 17.7856 | 16.3875 | 14.4525 | 16.5912 | 17.092 | 17.1881 | 17.1887 | 16.7012 | 15.7262 | 14.3471 | 14.6938 | 14.7588 | 15.3958 | 13.235 | 13.8601 | 16.2778 |  |  |  | 16.513 | 16.2218 | 21.0212 | 141.3807 | 128.0031 | 165.6491 | 16.9894 | 16.3398 | 18.9571 | 16.7151 | 16.2852 | 19.7644 | 48.0405 | 151.0282 |  | 80.6668 | 117.6038 | 117.7991 | 81.2602 |  | 6.9774 | 7.6855 | 6.7757 | 7.7512 | 8.3009 | 11.3051 | 64.2718 | 4.9557 | 7.2781 | 4.7108 | 8.2776 | 8.737 | 41.3451 | 46.8476 | 42.757 | 14.8269 |  |  | -0.27511 | -0.007141 | 0.034048 | 0.12945 | 0.013964 | -0.0964 | 0.67476 | -0.1191 | -0.31057 | 0.098224 | 0.02771 | -0.00055362 | -0.00057169 | 1.1656 | 15.8912 | 16.6452 | 17.1833 | 17.5063 | 17.4505 | 16.3968 | 14.7385 | 16.7737 | 17.1159 | 17.4118 | 17.4493 | 17.1589 | 16.3166 | 14.5035 | 48.69 | 22.7816 | 31.0658 | 21.5027 | 19.6139 | 28.9502 | 18.5939 | 15.8569 | 15.5051 | 15.4729 | 14.2823 | 14.9335 | 16.7171 |  |  |  | 40.7125 | 155.5562 | 116.0575 | 66.735 | 0.95105 | 0.043311 | 45.2575 |  |  | 11.2317 |  |  | 16.8768 | 16.6802 | 24.3307 | 16.3219 | 15.8773 | 18.6307 | 138.4021 | 165.8183 | 113.1378 | 115.197 | 80.316 |  | 46.0092 | 88.2851 | 46.8877 | 73.6691 | 60.1128 | 128.852 |  | 73.1101 |  |  | 15.0671 | 17.8169 | 48.3911 | [6 empty] | 60.9943 |  |  | 36.7238 |  |  | 17.1999 | 52.267 | 186.9375 | 9.7631 | 48.0794 | 123.0472 | 11.337 | 46.8587 | 134.5873 | 22.1791 | 107.8606 | 11.6261 | 97.4655 | 13.4817 | 102.728 | 10.8191 | 50.0237 | 114.1237 | 23.5484 | 46.1458 | 154.1944 | 11.9461 | 42.3993 | 134.7504 | 13.1667 | 95.1262 | 20.4343 | 108.571 | 14.6537 | 110.2752 | 1.3093 | 19.276 | 1.3798 | 0.09296 | -38.0904 | 3.1234 | 197.65 | 50.24 | -0.76569 | -0.09869 | 0.2155 | 0.42019 | 0.13889 | -0.36493 | 0.96549 | -0.36465 | -0.5551 | 0.32285 | -1.7211 | -0.97501 | -0.31933 | -0.17262
42810.4459 | 510 | 18.3511 | 18.4764 | 18.4789 | 18.4902 | 17.7977 | 16.3911 | 14.4533 | 16.5889 | 17.0968 | 17.1945 | 17.197 | 16.7089 | 15.7224 | 14.3451 | 14.6935 | 14.7509 | 15.3881 | 13.2306 | 13.8723 | 16.2833 |  |  |  | 16.5056 | 16.2207 | 21.0532 | 141.8324 | 128.4008 | 166.4881 | 16.9911 | 16.3344 | 18.9799 | 16.719 | 16.2893 | 19.7887 | 48.2219 | 150.171 |  | 80.8385 | 117.8572 | 118.0429 | 82.9404 |  | 6.9677 | 7.6789 | 6.7765 | 7.7533 | 8.3085 | 11.3281 | 64.7998 | 4.9017 | 7.2863 | 4.7676 | 8.2884 | 8.7436 | 41.3647 | 46.8749 | 42.7846 | 14.8242 |  |  | -0.35923 | -0.14317 | -0.014576 | -0.03417 | 0.04682 | -0.16868 | 0.48091 | 0.30211 | -0.008547 | 0.10095 | 0.0022767 | -0.00053062 | -0.0005914 | 1.0831 | 15.8915 | 16.6469 | 17.1794 | 17.5074 | 17.4479 | 16.3921 | 14.7302 | 16.7764 | 17.1169 | 17.404 | 17.4436 | 17.1497 | 16.3072 | 14.4958 | 51.2302 | 23.6826 | 30.6818 | 21.6054 | 18.9131 | 29.1467 | 18.6486 | 15.8476 | 15.5093 | 15.4748 | 14.2792 | 14.9428 | 16.7339 |  |  |  | 40.8354 | 156.095 | 116.2567 | 66.9873 | 0.84489 | 0.14626 | 45.3262 |  |  | 11.2329 |  |  | 16.8762 | 16.6965 | 24.3612 | 16.323 | 15.8849 | 18.6561 | 138.7625 | 166.2297 | 113.5147 | 115.6648 | 80.6036 |  | 46.1886 | 87.9864 | 47.048 | 76.4913 | 60.5532 | 128.5797 |  | 73.3809 |  |  | 15.1099 | 17.8527 | 48.5277 | [6 empty] | 61.4367 |  |  | 36.7901 |  |  | 17.2442 | 52.3768 | 187.6805 | 9.7984 | 48.3626 | 123.4945 | 11.333 | 47.1424 | 134.6973 | 22.2407 | 108.1783 | 11.649 | 97.8416 | 13.5028 | 102.9026 | 10.8528 | 50.3057 | 114.3654 | 23.594 | 46.4424 | 154.6715 | 11.9579 | 42.4239 | 134.9996 | 13.189 | 95.28 | 20.4734 | 108.8858 | 14.6782 | 110.6899 | 1.1263 | 19.2697 | 1.3858 | 0.09301 | -38.1943 | 3.1234 | 216.87 | 48.89 | -0.87579 | -0.44188 | -0.141 | -0.21588 | 0.25434 | -0.48275 | 0.81512 | -0.36633 | -0.54116 | 0.26039 | -1.9802 | -0.92595 | -0.3596 | -0.17536
42810.4459 | 511 | 18.3548 | 18.4753 | 18.4785 | 18.4892 | 17.7898 | 16.3912 | 14.4516 | 16.5904 | 17.0957 | 17.1906 | 17.188 | 16.7107 | 15.7181 | 14.3405 | 14.6931 | 14.747 | 15.3933 | 13.2308 | 13.8798 | 16.2998 |  |  |  | 16.5107 | 16.2258 | 21.0802 | 142.1484 | 128.8655 | 166.9617 | 16.989 | 16.3337 | 18.9944 | 16.7153 | 16.293 | 19.8124 | 48.3759 | 149.6048 |  | 81.0245 | 118.0431 | 118.2487 | 81.66 |  | 6.9658 | 7.6696 | 6.7721 | 7.7469 | 8.3136 | 11.3024 | 65.8186 | 4.728 | 7.2851 | 4.8044 | 8.2863 | 8.7382 | 41.3718 | 46.8538 | 42.7999 | 14.8124 |  |  | -0.5189 | -0.059053 | -0.087516 | -0.65251 | 0.17824 | 0.061308 | 0.74113 | 0.23706 | -0.15022 | 1.318 | 0.092486 | -0.00056183 | -0.00061933 | 1.0552 | 15.8857 | 16.6354 | 17.1681 | 17.5005 | 17.4472 | 16.3957 | 14.7242 | 16.7708 | 17.1157 | 17.4092 | 17.4389 | 17.1459 | 16.3122 | 14.4921 | 52.9647 | 24.2172 | 30.8242 | 21.4401 | 18.3804 | 29.3406 | 18.699 | 15.8553 | 15.5175 | 15.4801 | 14.2801 | 14.9475 | 16.7519 |  |  |  | 40.9718 | 156.5704 | 116.2867 | 67.8822 | 0.7134 | 0.42856 | 45.3849 |  |  | 11.2353 |  |  | 16.8803 | 16.6948 | 24.41 | 16.3146 | 15.8902 | 18.6735 | 139.024 | 166.7099 | 113.9379 | 116.3299 | 81.4097 |  | 46.3473 | 88.5427 | 47.2219 | 74.1927 | 60.969 | 128.7741 |  | 73.6485 |  |  | 15.1646 | 17.886 | 48.679 | [6 empty] | 61.6304 |  |  | 36.8565 |  |  | 17.2736 | 52.8258 | 188.1112 | 9.8388 | 48.1835 | 123.9879 | 11.3446 | 47.382 | 134.8951 | 22.2852 | 108.667 | 11.6746 | 98.1361 | 13.534 | 103.1659 | 10.8518 | 50.6666 | 114.6628 | 23.6438 | 46.7526 | 155.0841 | 11.9561 | 42.4751 | 135.3551 | 13.2028 | 95.4368 | 20.5126 | 109.3114 | 14.7098 | 111.1658 | 1.0075 | 19.2628 | 1.3926 | 0.093864 | -38.221 | 3.1235 | 218.99 | 49.77 | -1.0532 | -0.28379 | -0.34548 | -0.94336 | 0.49623 | 0.29103 | 1.0119 | -0.38314 | -0.55049 | 0.3393 | -2.1502 | -0.93589 | -0.31859 | -0.19547
42810.446 | 512 | 18.35 | 18.47 | 18.4707 | 18.4777 | 17.7826 | 16.3855 | 14.4436 | 16.5859 | 17.0922 | 17.1846 | 17.1796 | 16.6997 | 15.7149 | 14.339 | 14.6995 | 14.7513 | 15.3951 | 13.2303 | 13.8797 | 16.3185 |  |  |  | 16.5137 | 16.2329 | 21.1044 | 142.5767 | 129.3691 | 167.9865 | 16.9911 | 16.3352 | 19.0044 | 16.7076 | 16.2907 | 19.8286 | 48.497 | 149.7444 |  | 81.2208 | 118.2456 | 118.4285 | 81.6692 |  | 6.9763 | 7.7054 | 6.7803 | 7.7567 | 8.3113 | 11.2615 | 65.5329 | 4.6427 | 7.3021 | 4.8279 | 8.3136 | 8.756 | 41.3991 | 46.8483 | 42.815 | 14.8154 |  |  | -0.3244 | -0.15565 | 0.08596 | -0.34301 | 0.02382 | -0.51892 | 0.42111 | 0.066204 | -0.54448 | -0.082204 | -0.018786 | -0.00060455 | -0.00062262 | 1.2865 | 15.8911 | 16.6466 | 17.1804 | 17.4985 | 17.4485 | 16.3909 | 14.7302 | 16.7759 | 17.1162 | 17.4071 | 17.4448 | 17.1514 | 16.3096 | 14.4955 | 52.9 | 24.6892 | 31.6613 | 22.7628 | 19.4871 | 29.4884 | 18.7716 | 15.8558 | 15.5133 | 15.4748 | 14.2708 | 14.9487 | 16.762 |  |  |  | 41.1052 | 157.1091 | 116.5929 | 69.2597 | 0.73731 | 0.091114 | 45.5093 |  |  | 11.2382 |  |  | 16.8818 | 16.7046 | 24.4588 | 16.328 | 15.9001 | 18.6921 | 139.2057 | 166.7967 | 114.2817 | 116.6768 | 81.6933 |  | 46.4711 | 90.0219 | 47.4007 | 73.1585 | 61.3482 | 128.5158 |  | 73.8486 |  |  | 15.2084 | 17.9325 | 48.8213 | [6 empty] | 61.4029 |  |  | 36.9941 |  |  | 17.2975 | 53.0722 | 188.6818 | 9.8801 | 48.1445 | 124.3499 | 11.3489 | 47.5408 | 135.124 | 22.3395 | 109.1344 | 11.699 | 98.3443 | 13.5719 | 103.6276 | 10.8479 | 50.9123 | 115.046 | 23.7144 | 46.898 | 155.392 | 11.9445 | 42.6769 | 135.7493 | 13.2193 | 95.559 | 20.5781 | 109.8765 | 14.7428 | 111.6382 | 0.9497 | 19.2551 | 1.3977 | 0.090622 | -38.2178 | 3.1235 | 213.14 | 50.34 | -0.83367 | -0.46077 | 0.34242 | -0.68401 | 0.18139 | -0.84663 | 0.76267 | -0.38666 | -0.58528 | 0.38177 | -2.1257 | -1.0204 | -0.31457 | -0.22909
42810.446 | 513 | 18.3516 | 18.4764 | 18.4722 | 18.4811 | 17.7869 | 16.385 | 14.4418 | 16.5875 | 17.0944 | 17.1866 | 17.1899 | 16.6989 | 15.7207 | 14.3311 | 14.7004 | 14.7557 | 15.3986 | 13.2284 | 13.8816 | 16.3372 |  |  |  | 16.5117 | 16.2329 | 21.1264 | 143.0489 | 129.7889 | 168.324 | 16.9843 | 16.3354 | 19.0211 | 16.7108 | 16.2792 | 19.8446 | 48.6402 | 149.3675 |  | 81.4043 | 118.5466 | 118.6486 | 83.0893 |  | 6.9931 | 7.7207 | 6.7863 | 7.7625 | 8.3438 | 11.2735 | 64.7778 | 4.6353 | 7.3039 | 4.8179 | 8.3195 | 8.7443 | 41.4383 | 46.8416 | 42.8193 | 14.8049 |  |  | -0.42756 | 0.027031 | 0.23644 | -0.23065 | 0.004108 | 0.17433 | 0.3416 | 0.16412 | -0.60227 | 0.20606 | 0.1815 | -0.00054869 | -0.00057497 | 1.3121 | 15.8901 | 16.6334 | 17.1762 | 17.4909 | 17.4483 | 16.3876 | 14.7243 | 16.7684 | 17.1167 | 17.4069 | 17.4465 | 17.1473 | 16.3109 | 14.4999 | 54.4165 | 23.861 | 31.1396 | 23.4619 | 20.2784 | 29.6662 | 18.8188 | 15.8547 | 15.518 | 15.4789 | 14.2732 | 14.9503 | 16.7826 |  |  |  | 41.2489 | 157.7606 | 117.5325 | 70.0098 | 0.66458 | -0.050225 | 45.6628 |  |  | 11.2314 |  |  | 16.8728 | 16.7068 | 24.4905 | 16.3182 | 15.8904 | 18.7065 | 139.3003 | 167.106 | 114.5527 | 116.9355 | 81.3693 |  | 46.6103 | 90.0538 | 47.5618 | 73.473 | 61.7543 | 128.6016 |  | 74.0799 |  |  | 15.2259 | 17.953 | 48.9458 | [6 empty] | 62.2255 |  |  | 37.0395 |  |  | 17.3314 | 52.9789 | 188.985 | 9.9125 | 48.7153 | 124.7121 | 11.3472 | 47.9355 | 135.3146 | 22.4165 | 109.5117 | 11.7317 | 98.6 | 13.6104 | 104.223 | 10.8653 | 50.9483 | 115.4216 | 23.7907 | 47.2272 | 155.8429 | 11.944 | 42.8734 | 136.1535 | 13.2385 | 95.5518 | 20.6457 | 110.2972 | 14.7897 | 111.9102 | 1.1269 | 19.2481 | 1.4046 | 0.090911 | -38.1658 | 3.1235 | 218.94 | 49.2 | -0.95746 | 0.19202 | 0.56791 | -0.56091 | 0.075329 | 0.49073 | 0.68692 | -0.37277 | -0.58048 | 0.38777 | -2.2733 | -0.95695 | -0.34896 | -0.24492
42810.446 | 514 | 18.365 | 18.4745 | 18.4813 | 18.4818 | 17.7884 | 16.3954 | 14.4494 | 16.5982 | 17.0968 | 17.1942 | 17.1943 | 16.707 | 15.7224 | 14.3398 | 14.6973 | 14.7535 | 15.3986 | 13.23 | 13.8888 | 16.3479 |  |  |  | 16.5127 | 16.2281 | 21.1527 | 143.409 | 130.1235 | 168.2578 | 16.9991 | 16.341 | 19.0442 | 16.7135 | 16.2855 | 19.8808 | 48.7887 | 149.081 |  | 81.5813 | 118.9301 | 118.8963 | 84.6687 |  | 6.9912 | 7.7271 | 6.795 | 7.7677 | 8.379 | 11.3042 | 64.8715 | 4.6401 | 7.3002 | 4.8106 | 8.3186 | 8.747 | 41.4724 | 46.8155 | 42.8152 | 14.7955 |  |  | -0.46436 | -0.17865 | 0.10042 | -0.29965 | 0.13422 | 0.12308 | 0.33503 | 0.052404 | -0.54973 | -0.73531 | -0.0062674 | -0.00055198 | -0.00060619 | 1.1335 | 15.8913 | 16.6386 | 17.1824 | 17.4973 | 17.4437 | 16.3905 | 14.7299 | 16.772 | 17.1159 | 17.4041 | 17.4386 | 17.1464 | 16.3138 | 14.5045 | 55.5012 | 23.8432 | 30.2576 | 23.4708 | 21.4106 | 29.866 | 18.86 | 15.8431 | 15.5092 | 15.4707 | 14.2672 | 14.9571 | 16.7902 |  |  |  | 41.4026 | 158.7744 | 117.8918 | 70.145 | 0.85016 | 0.4167 | 45.6586 |  |  | 11.2395 |  |  | 16.8816 | 16.7028 | 24.541 | 16.3183 | 15.8908 | 18.7235 | 139.2481 | 167.6844 | 114.9336 | 117.4346 | 81.7791 |  | 46.7799 | 88.4773 | 47.7092 | 71.8615 | 62.1337 | 127.9542 |  | 74.3135 |  |  | 15.2574 | 17.963 | 49.6885 | [6 empty] | 62.3672 |  |  | 37.0472 |  |  | 17.3489 | 53.3087 | 188.9554 | 9.9138 | 49.1248 | 124.9971 | 11.3502 | 48.3537 | 135.6395 | 22.4836 | 109.9063 | 11.758 | 98.8469 | 13.6255 | 104.6877 | 10.8847 | 50.8874 | 115.6552 | 23.8627 | 47.5872 | 156.5756 | 11.9583 | 43.106 | 136.5629 | 13.2622 | 95.6272 | 20.7068 | 110.7309 | 14.8292 | 112.058 | 1.0907 | 19.2437 | 1.4125 | 0.091194 | -38.201 | 3.1235 | 220.87 | 50.44 | -0.99773 | -0.49366 | 0.37011 | -0.63934 | 0.4306 | 0.41235 | 0.68032 | -0.37818 | -0.53149 | 0.44631 | -2.3703 | -0.85413 | -0.38758 | -0.24332
42810.446 | 515 | 18.3642 | 18.4743 | 18.4822 | 18.4865 | 17.8001 | 16.3976 | 14.45 | 16.6034 | 17.1018 | 17.1899 | 17.1987 | 16.7071 | 15.7213 | 14.3466 | 14.6943 | 14.7493 | 15.3918 | 13.2244 | 13.8876 | 16.3563 |  |  |  | 16.5118 | 16.2314 | 21.18 | 143.9215 | 130.4934 | 168.4302 | 16.9909 | 16.3424 | 19.0672 | 16.7184 | 16.2903 | 19.9047 | 48.9423 | 148.9503 |  | 81.7807 | 119.352 | 119.1414 | 84.041 |  | 6.9969 | 7.7391 | 6.8032 | 7.7771 | 8.4105 | 11.3704 | 65.6142 | 4.6004 | 7.3031 | 4.7141 | 8.3325 | 8.7511 | 41.5133 | 46.7988 | 42.8177 | 14.7864 |  |  | -0.55702 | 0.023087 | 0.02682 | 0.16231 | 0.003448 | -0.16868 | 0.49274 | 0.62607 | -0.63419 | 0.20732 | -0.069057 | -0.00058647 | -0.00061769 | 1.0739 | 15.8864 | 16.6447 | 17.182 | 17.4999 | 17.4433 | 16.3886 | 14.7306 | 16.7779 | 17.1145 | 17.4055 | 17.4419 | 17.1534 | 16.3154 | 14.5065 | 57.0007 | 25.9401 | 32.8754 | 23.7028 | 21.818 | 30.0638 | 18.9498 | 15.8406 | 15.5207 | 15.4759 | 14.2774 | 14.9642 | 16.8151 |  |  |  | 41.5386 | 159.645 | 118.1019 | 70.4299 | 0.58779 | 0.48295 | 45.6124 |  |  | 11.2471 |  |  | 16.8787 | 16.7126 | 24.5855 | 16.321 | 15.8951 | 18.7377 | 139.3547 | 168.1214 | 115.2698 | 117.7578 | 83.7145 |  | 46.9041 | 88.6774 | 47.8763 | 73.9137 | 62.5488 | 126.855 |  | 74.5246 |  |  | 15.2863 | 17.98 | 50.2291 | [6 empty] | 64.0021 |  |  | 37.1505 |  |  | 17.3819 | 53.8893 | 189.05 | 9.905 | 49.2346 | 125.1924 | 11.3619 | 48.5377 | 135.9386 | 22.5671 | 110.297 | 11.7754 | 99.0498 | 13.6603 | 104.9409 | 10.9204 | 50.9989 | 115.82 | 23.9349 | 47.8349 | 157.461 | 11.9734 | 43.2527 | 136.9008 | 13.2985 | 95.8404 | 20.8138 | 111.3322 | 14.8639 | 112.1893 | 1.0113 | 19.2369 | 1.4199 | 0.091671 | -38.2277 | 3.1235 | 218.79 | 49.85 | -1.093 | 0.17747 | 0.19128 | 0.47055 | 0.069025 | -0.48279 | 0.82515 | -0.42757 | -0.53116 | 0.40439 | -2.5137 | -1.1345 | -0.36472 | -0.24649
42810.446 | 516 | 18.3629 | 18.4853 | 18.4875 | 18.4854 | 17.7922 | 16.4016 | 14.4541 | 16.5995 | 17.0995 | 17.1911 | 17.1873 | 16.7071 | 15.724 | 14.3451 | 14.7042 | 14.7628 | 15.4061 | 13.2268 | 13.8929 | 16.3675 |  |  |  | 16.5218 | 16.2384 | 21.2144 | 144.3227 | 130.9506 | 168.1331 | 16.9875 | 16.3442 | 19.0812 | 16.7118 | 16.2979 | 19.9216 | 49.0836 | 148.1255 |  | 81.974 | 119.7435 | 119.4168 | 81.4083 |  | 7.01 | 7.7449 | 6.8048 | 7.7906 | 8.4212 | 11.4079 | 65.7056 | 4.5259 | 7.3084 | 4.6866 | 8.3389 | 8.7523 | 41.5627 | 46.7917 | 42.8245 | 14.7853 |  |  | -0.42625 | -0.13725 | 0.091876 | -0.082138 | 0.19007 | 0.15134 | 0.28838 | 0.2962 | -0.38296 | 0.91791 | 0.0068468 | -0.00057826 | -0.00056676 | 1.1112 | 15.8932 | 16.6489 | 17.1808 | 17.5003 | 17.4472 | 16.3898 | 14.7272 | 16.7852 | 17.1139 | 17.4097 | 17.4486 | 17.154 | 16.3111 | 14.5027 | 54.8943 | 25.9195 | 34.2578 | 25.2423 | 22.1398 | 30.1766 | 19.0164 | 15.844 | 15.5168 | 15.4782 | 14.2815 | 14.9681 | 16.8319 |  |  |  | 41.6854 | 160.5202 | 118.4819 | 71.0276 | 0.19475 | 0.058931 | 45.7287 |  |  | 11.2477 |  |  | 16.8703 | 16.7177 | 24.6275 | 16.315 | 15.8901 | 18.7562 | 139.7597 | 168.8884 | 115.5402 | 118.0367 | 84.1851 |  | 47.037 | 90.4396 | 48.0534 | 73.8756 | 62.8389 | 126.6629 |  | 74.7089 |  |  | 15.3129 | 18.0169 | 50.2565 | [6 empty] | 63.3778 |  |  | 37.2921 |  |  | 17.423 | 54.2078 | 188.9302 | 9.9101 | 49.4174 | 125.2048 | 11.3702 | 48.6009 | 136.0453 | 22.6315 | 110.5866 | 11.7874 | 99.4079 | 13.6942 | 105.1314 | 10.9645 | 51.2684 | 116.0425 | 24.0384 | 47.9005 | 158.1909 | 11.9806 | 43.368 | 137.225 | 13.3251 | 96.1279 | 20.9182 | 111.6163 | 14.8995 | 112.5174 | 0.88614 | 19.2323 | 1.4276 | 0.091838 | -38.1943 | 3.1236 | 229.74 | 49.49 | -0.95578 | -0.43271 | 0.35403 | -0.33474 | 0.51252 | 0.45732 | 0.63129 | -0.43596 | -0.57386 | 0.416 | -2.2664 | -1.2803 | -0.28659 | -0.25798
42810.446 | 517 | 18.3556 | 18.4804 | 18.4817 | 18.4756 | 17.7921 | 16.3909 | 14.4472 | 16.59 | 17.0943 | 17.1832 | 17.1839 | 16.7011 | 15.718 | 14.3398 | 14.6993 | 14.7585 | 15.3906 | 13.2364 | 13.8921 | 16.3854 |  |  |  | 16.5195 | 16.2394 | 21.2436 | 144.8443 | 131.651 | 168.7925 | 16.9859 | 16.3462 | 19.0973 | 16.7078 | 16.2948 | 19.9451 | 49.2169 | 148.1083 |  | 82.1536 | 120.0929 | 119.6772 | 81.5158 |  | 7.0177 | 7.7575 | 6.8035 | 7.7978 | 8.4211 | 11.4569 | 67.0442 | 4.4928 | 7.3034 | 4.6542 | 8.341 | 8.7555 | 41.6039 | 46.7904 | 42.8199 | 14.7767 |  |  | -0.52285 | -0.047881 | 0.14773 | 0.16625 | 0.062592 | 0.16185 | 0.20295 | 0.75289 | -0.014969 | -0.2362 | 0.0074429 | -0.00057333 | -0.00059305 | 1.0986 | 15.9002 | 16.6458 | 17.1778 | 17.4956 | 17.4481 | 16.3915 | 14.7231 | 16.7789 | 17.1154 | 17.406 | 17.4491 | 17.1568 | 16.3157 | 14.4994 | 51.4391 | 24.1185 | 34.0826 | 24.7211 | 21.437 | 30.2359 | 19.0886 | 15.8464 | 15.5113 | 15.4737 | 14.2772 | 14.9738 | 16.8473 |  |  |  | 41.8277 | 161.7893 | 118.8954 | 71.6951 | 0.064476 | -0.086171 | 45.7725 |  |  | 11.254 |  |  | 16.8669 | 16.718 | 24.667 | 16.3159 | 15.8955 | 18.776 | 140.2499 | 170.0162 | 115.7814 | 118.3022 | 84.3384 |  | 47.2046 | 91.3367 | 48.2171 | 74.3364 | 63.2209 | 128.1621 |  | 74.9373 |  |  | 15.3648 | 18.0624 | 51.1915 | [6 empty] | 63.5253 |  |  | 37.5151 |  |  | 17.4693 | 54.2977 | 189.2498 | 9.926 | 50.3082 | 125.3625 | 11.3966 | 48.8982 | 136.1792 | 22.6869 | 110.7951 | 11.793 | 99.7641 | 13.7269 | 105.4204 | 10.997 | 51.352 | 116.1917 | 24.1292 | 48.2174 | 158.8723 | 11.9958 | 43.4869 | 137.5078 | 13.3622 | 96.4047 | 20.9861 | 112.2886 | 14.9465 | 112.9124 | 1.0005 | 19.2232 | 1.4342 | 0.090528 | -38.2567 | 3.1235 | 242.12 | 50.13 | -1.0593 | -0.25558 | 0.44894 | 0.47624 | 0.29414 | 0.47298 | 0.52964 | -0.43431 | -0.593 | 0.4171 | -1.8756 | -1.2524 | -0.28486 | -0.27156
42810.446 | 518 | 18.3515 | 18.4781 | 18.478 | 18.4712 | 17.7823 | 16.3863 | 14.4409 | 16.5897 | 17.0882 | 17.1872 | 17.181 | 16.6977 | 15.7126 | 14.3299 | 14.6938 | 14.7609 | 15.4028 | 13.2296 | 13.8878 | 16.4043 |  |  |  | 16.5186 | 16.2446 | 21.2695 | 145.3359 | 132.5741 | 169.6647 | 16.9894 | 16.3477 | 19.117 | 16.7105 | 16.3005 | 19.9687 | 49.3705 | 148.7883 |  | 82.3367 | 120.4769 | 119.9162 | 83.7206 |  | 7.0256 | 7.7589 | 6.808 | 7.8105 | 8.4242 | 11.6097 | 68.5997 | 4.5288 | 7.3099 | 4.5823 | 8.3515 | 8.7502 | 41.6445 | 46.8059 | 42.8233 | 14.7608 |  |  | -0.72589 | 0.12363 | 0.23513 | 0.076882 | 0.16313 | 0.17893 | 0.40534 | 0.54064 | -0.53436 | -0.58803 | 0.0008858 | -0.00059633 | -0.00052405 | 1.0607 | 15.8907 | 16.645 | 17.1818 | 17.5006 | 17.4441 | 16.3971 | 14.7253 | 16.7814 | 17.1141 | 17.4148 | 17.4447 | 17.1595 | 16.3212 | 14.5011 | 46.7974 | 21.5474 | 32.0042 | 23.8257 | 21.6169 | 30.269 | 19.1216 | 15.8468 | 15.5067 | 15.4827 | 14.2779 | 14.9804 | 16.8635 |  |  |  | 41.9659 | 163.2851 | 120.1097 | 71.7225 | 0.42571 | -0.13586 | 46.0248 |  |  | 11.2664 |  |  | 16.8773 | 16.7281 | 24.7197 | 16.317 | 15.9053 | 18.8139 | 140.8712 | 170.7284 | 115.9067 | 118.5158 | 85.8289 |  | 47.4066 | 90.3437 | 48.35 | 74.7432 | 63.5668 | 129.3925 |  | 75.1469 |  |  | 15.4004 | 18.0737 | 52.1547 | [6 empty] | 63.0855 |  |  | 37.6062 |  |  | 17.5061 | 54.5569 | 189.4747 | 9.9437 | 50.5311 | 125.8018 | 11.4093 | 49.1476 | 136.5935 | 22.7575 | 111.0814 | 11.775 | 100.0291 | 13.766 | 105.5742 | 11.049 | 51.2307 | 116.2384 | 24.201 | 48.6579 | 159.6564 | 12.034 | 43.5974 | 137.896 | 13.3925 | 96.6457 | 21.0694 | 112.828 | 14.9871 | 113.1986 | 1.0221 | 19.2134 | 1.4426 | 0.090701 | -38.2236 | 3.1236 | 238.83 | 49.08 | -1.2494 | 0.41068 | 0.56637 | 0.32386 | 0.47497 | 0.49745 | 0.74871 | -0.46859 | -0.56072 | 0.4184 | -1.3559 | -1.0177 | -0.34067 | -0.2675
42810.446 | 519 | 18.3509 | 18.4762 | 18.4749 | 18.4695 | 17.7814 | 16.3848 | 14.4426 | 16.5854 | 17.0896 | 17.182 | 17.1797 | 16.7005 | 15.713 | 14.3288 | 14.699 | 14.7554 | 15.4018 | 13.2295 | 13.8863 | 16.4121 |  |  |  | 16.5138 | 16.2482 | 21.2958 | 145.7416 | 133.2633 | 168.8949 | 16.9847 | 16.3517 | 19.1459 | 16.7186 | 16.3058 | 19.9975 | 49.5379 | 149.4017 |  | 82.5046 | 120.7488 | 120.1635 | 86.1844 |  | 7.0449 | 7.7721 | 6.8183 | 7.8298 | 8.4359 | 11.7568 | 68.683 | 4.5025 | 7.3113 | 4.6498 | 8.359 | 8.757 | 41.6699 | 46.8189 | 42.8293 | 14.7617 |  |  | -0.65427 | -0.10702 | 0.36721 | -0.059142 | 0.23672 | 0.068536 | 0.48288 | 0.38819 | -0.79707 | -0.23976 | 0.089307 | -0.00058812 | -0.00055855 | 1.0369 | 15.8878 | 16.6363 | 17.1669 | 17.4932 | 17.4357 | 16.384 | 14.7106 | 16.7604 | 17.1005 | 17.3994 | 17.4374 | 17.1459 | 16.2988 | 14.4815 | 46.3369 | 21.4182 | 33.0372 | 23.0575 | 21.2149 | 30.3893 | 19.1782 | 15.8413 | 15.5132 | 15.4854 | 14.2794 | 14.987 | 16.8837 |  |  |  | 42.1273 | 164.9893 | 122.7877 | 71.5308 | 0.72941 | 0.18107 | 46.0836 |  |  | 11.2619 |  |  | 16.8835 | 16.7401 | 24.7651 | 16.3284 | 15.9095 | 18.8305 | 141.7364 | 171.687 | 116.3551 | 118.8949 | 86.8365 |  | 47.56 | 89.856 | 48.4829 | 76.9926 | 63.9939 | 130.3193 |  | 75.4036 |  |  | 15.4667 | 18.116 | 51.9711 | [6 empty] | 64.2053 |  |  | 37.6896 |  |  | 17.5615 | 55.0461 | 190.466 | 9.9455 | 50.3002 | 126.1734 | 11.4432 | 48.8078 | 137.0735 | 22.8237 | 111.2488 | 11.7903 | 100.1724 | 13.8207 | 105.8031 | 11.0676 | 51.7343 | 116.4129 | 24.2784 | 48.692 | 160.1389 | 12.0367 | 43.7649 | 138.0648 | 13.3848 | 96.9531 | 21.1394 | 113.1934 | 14.9979 | 113.498 | 1.0373 | 19.2026 | 1.4517 | 0.09275 | -38.2514 | 3.1235 | 216.34 | 49.11 | -1.1852 | -0.38212 | 0.70781 | -0.28406 | 0.57232 | 0.30795 | 0.81741 | -0.49118 | -0.54248 | 0.37149 | -1.2906 | -1.1258 | -0.40319 | -0.25655
42810.4461 | 520 | 18.3622 | 18.4833 | 18.4745 | 18.4685 | 17.7883 | 16.389 | 14.4508 | 16.586 | 17.1005 | 17.1936 | 17.2 | 16.7084 | 15.7169 | 14.3367 | 14.6986 | 14.7563 | 15.4063 | 13.2399 | 13.8927 | 16.4393 |  |  |  | 16.5109 | 16.2569 | 21.337 | 146.0666 | 133.8211 | 169.6096 | 16.9795 | 16.3469 | 19.1572 | 16.7139 | 16.2976 | 20.0206 | 49.7003 | 149.7158 |  | 82.6788 | 121.0195 | 120.3918 | 86.8601 |  | 7.0563 | 7.7835 | 6.8273 | 7.8362 | 8.4279 | 11.7532 | 67.7733 | 4.4421 | 7.3086 | 4.6825 | 8.3692 | 8.7614 | 41.679 | 46.8 | 42.8396 | 14.7431 |  |  | -0.53796 | 0.037543 | 0.1773 | -0.12879 | 0.34252 | -0.066172 | 0.48025 | 0.41973 | -0.27009 | -0.62328 | 0.047382 | -0.0006029 | -0.00056348 | 1.0042 | 15.8916 | 16.6373 | 17.1766 | 17.4915 | 17.4383 | 16.3819 | 14.7203 | 16.7735 | 17.1043 | 17.4075 | 17.4448 | 17.1532 | 16.3085 | 14.4938 | 48.1018 | 22.3941 | 33.5714 | 23.6124 | 21.8518 | 30.5343 | 19.2406 | 15.8385 | 15.5051 | 15.4854 | 14.284 | 14.9929 | 16.8988 |  |  |  | 42.2829 | 166.4175 | 123.8221 | 71.2272 | 0.53046 | 0.40616 | 46.0799 |  |  | 11.2582 |  |  | 16.8736 | 16.7271 | 24.7982 | 16.3169 | 15.8954 | 18.8342 | 142.0569 | 172.4265 | 116.8607 | 119.3782 | 86.5905 |  | 47.7051 | 91.2859 | 48.6209 | 75.631 | 64.4543 | 131.1964 |  | 75.7047 |  |  | 15.5076 | 18.1291 | 51.9522 | [6 empty] | 64.2192 |  |  | 37.8457 |  |  | 17.5958 | 55.6228 | 191.478 | 9.9526 | 50.5406 | 126.7231 | 11.4354 | 48.9453 | 137.5126 | 22.8951 | 111.7157 | 11.8157 | 100.6314 | 13.8664 | 106.2519 | 11.0809 | 52.3306 | 116.7457 | 24.4049 | 48.7527 | 160.6789 | 12.0551 | 43.9195 | 138.3321 | 13.3892 | 97.183 | 21.2456 | 113.7917 | 15.0234 | 113.9359 | 1.0965 | 19.193 | 1.4618 | 0.094472 | -38.2675 | 3.1235 | 223.9 | 50.28 | -1.0755 | 0.22633 | 0.49184 | -0.4192 | 0.68843 | -0.30259 | 0.81517 | -0.47923 | -0.57733 | 0.42611 | -1.4697 | -1.1779 | -0.41621 | -0.24269
42810.4461 | 521 | 18.3619 | 18.48 | 18.4759 | 18.4793 | 17.7881 | 16.3875 | 14.4485 | 16.5911 | 17.0946 | 17.1871 | 17.1862 | 16.7052 | 15.7162 | 14.3397 | 14.7011 | 14.7587 | 15.3979 | 13.2314 | 13.8848 | 16.4497 |  |  |  | 16.5226 | 16.2495 | 21.3653 | 146.5977 | 134.2356 | 170.9389 | 16.985 | 16.3477 | 19.1688 | 16.7118 | 16.2957 | 20.0398 | 49.8485 | 149.9481 |  | 82.9071 | 121.3924 | 120.6267 | 87.1993 |  | 7.0498 | 7.7719 | 6.8327 | 7.8374 | 8.4107 | 11.7733 | 68.3692 | 4.4156 | 7.304 | 4.5767 | 8.3731 | 8.759 | 41.6872 | 46.7795 | 42.8418 | 14.7408 |  |  | -0.39208 | 0.10325 | 0.066248 | -0.07491 | 0.075732 | 0.19339 | 0.4014 | 0.28962 | -0.26114 | -0.60251 | 0.10957 | -0.00054705 | -0.0005684 | 1.0166 | 15.8872 | 16.6345 | 17.1732 | 17.4977 | 17.4385 | 16.3832 | 14.7238 | 16.7703 | 17.1088 | 17.4135 | 17.4494 | 17.1521 | 16.3101 | 14.5016 | 49.6443 | 23.1013 | 34.4103 | 23.2714 | 21.0403 | 30.6733 | 19.3154 | 15.8393 | 15.5076 | 15.4788 | 14.286 | 15.0009 | 16.919 |  |  |  | 42.4427 | 167.4553 | 125.3483 | 71.5865 | 1.0951 | 0.18164 | 46.0959 |  |  | 11.2645 |  |  | 16.8825 | 16.7531 | 24.8528 | 16.3251 | 15.9113 | 18.8724 | 142.455 | 172.9373 | 117.2904 | 119.9019 | 86.3124 |  | 47.8584 | 92.5191 | 48.7715 | 76.6448 | 64.844 | 132.4109 |  | 76.041 |  |  | 15.5448 | 18.1204 | 53.076 | [6 empty] | 64.6839 |  |  | 38.0301 |  |  | 17.6336 | 56.1844 | 192.063 | 9.9447 | 51.0199 | 127.3369 | 11.4425 | 49.4149 | 138.1241 | 23.0099 | 112.0723 | 11.8382 | 100.9995 | 13.8858 | 106.5378 | 11.0536 | 52.7931 | 117.1129 | 24.5238 | 49.0065 | 161.5441 | 12.0902 | 44.0022 | 138.4889 | 13.38 | 97.4415 | 21.3687 | 114.2701 | 15.0719 | 114.3256 | 1.2234 | 19.1868 | 1.4689 | 0.090694 | -38.3059 | 3.1235 | 213.94 | 49.12 | -0.91958 | 0.37533 | 0.30064 | -0.31969 | 0.32372 | 0.5173 | 0.74528 | -0.46609 | -0.60626 | 0.41218 | -1.6247 | -1.2624 | -0.42038 | -0.24709
42810.4461 | 522 | 18.3552 | 18.4781 | 18.48 | 18.4761 | 17.7829 | 16.3804 | 14.4521 | 16.5888 | 17.0871 | 17.1867 | 17.1834 | 16.7069 | 15.7088 | 14.3441 | 14.7078 | 14.7677 | 15.4116 | 13.2429 | 13.8951 | 16.4833 |  |  |  | 16.5302 | 16.2647 | 21.4057 | 147.0245 | 134.8903 | 171.3229 | 16.9866 | 16.3559 | 19.1984 | 16.7177 | 16.3003 | 20.0683 | 50.0073 | 151.2041 |  | 83.1404 | 121.7471 | 120.8777 | 87.1871 |  | 7.0348 | 7.7666 | 6.8356 | 7.8465 | 8.4353 | 11.8203 | 69.6877 | 4.4111 | 7.3112 | 4.4784 | 8.3785 | 8.7684 | 41.7083 | 46.7912 | 42.8458 | 14.7316 |  |  | -0.49722 | -0.059053 | 0.12802 | 0.10908 | 0.20058 | 0.35044 | 0.406 | 0.53276 | -0.50341 | -0.19277 | 0.034863 | -0.00054869 | -0.00056183 | 1.0962 | 15.8872 | 16.6443 | 17.1777 | 17.498 | 17.4483 | 16.386 | 14.7256 | 16.7713 | 17.1098 | 17.4164 | 17.4488 | 17.1603 | 16.3152 | 14.5063 | 54.4179 | 24.3761 | 34.9995 | 22.8651 | 21.1129 | 30.8913 | 19.3865 | 15.8493 | 15.5208 | 15.4828 | 14.2827 | 15.0062 | 16.9354 |  |  |  | 42.6148 | 169.0204 | 127.1348 | 72.6108 | 0.88885 | 0.63313 | 46.3049 |  |  | 11.2746 |  |  | 16.886 | 16.7453 | 24.8902 | 16.3178 | 15.9123 | 18.8842 | 142.8288 | 174.0213 | 117.7785 | 120.4951 | 86.566 |  | 48.02 | 93.9481 | 48.9171 | 77.7665 | 65.2712 | 133.5266 |  | 76.3123 |  |  | 15.5959 | 18.1723 | 53.1142 | [6 empty] | 65.6921 |  |  | 38.2138 |  |  | 17.6709 | 56.6771 | 192.8852 | 9.9419 | 50.9705 | 127.8181 | 11.4571 | 49.6714 | 138.7298 | 23.1336 | 112.6692 | 11.8232 | 101.1484 | 13.927 | 106.7935 | 11.0296 | 53.2353 | 117.2672 | 24.6441 | 49.2831 | 162.2056 | 12.1232 | 44.1825 | 138.6857 | 13.3681 | 97.6955 | 21.52 | 114.2761 | 15.1117 | 114.5384 | 1.1255 | 19.1749 | 1.4775 | 0.090036 | -38.2211 | 3.1236 | 225.51 | 49.52 | -1.036 | -0.28384 | 0.41791 | 0.38577 | 0.52688 | 0.69642 | 0.7496 | -0.46744 | -0.64081 | 0.39664 | -2.1295 | -1.3195 | -0.41441 | -0.26954
42810.4461 | 523 | 18.3491 | 18.4695 | 18.4751 | 18.481 | 17.7819 | 16.3791 | 14.4454 | 16.5847 | 17.0829 | 17.1724 | 17.1909 | 16.7025 | 15.707 | 14.3308 | 14.6933 | 14.7588 | 15.4047 | 13.2323 | 13.8854 | 16.4822 |  |  |  | 16.5192 | 16.2638 | 21.4291 | 147.6284 | 135.7147 | 173.3628 | 16.9832 | 16.3469 | 19.2182 | 16.7124 | 16.3042 | 20.0868 | 50.1757 | 153.1323 |  | 83.4087 | 121.9884 | 121.1592 | 89.3128 |  | 7.0239 | 7.7654 | 6.834 | 7.8629 | 8.443 | 11.7729 | 69.77 | 4.4167 | 7.3142 | 4.4507 | 8.3925 | 8.7695 | 41.732 | 46.7958 | 42.8563 | 14.7263 |  |  | -0.47159 | -0.018969 | 0.13656 | -0.028914 | 0.10399 | 0.07708 | 0.44542 | 0.40659 | -1.0407 | -0.02346 | 0.093877 | -0.00055855 | -0.00056512 | 1.0564 | 15.8969 | 16.6427 | 17.1802 | 17.4983 | 17.453 | 16.3898 | 14.7283 | 16.7774 | 17.1126 | 17.4141 | 17.4512 | 17.1612 | 16.3155 | 14.5035 | 57.001 | 25.2492 | 37.045 | 24.1352 | 21.0484 | 31.0972 | 19.4904 | 15.845 | 15.5139 | 15.4994 | 14.277 | 15.0099 | 16.9394 |  |  |  | 42.8019 | 170.3669 | 128.6941 | 73.7665 | 0.93829 | 0.40484 | 46.5369 |  |  | 11.2722 |  |  | 16.8821 | 16.7527 | 24.9209 | 16.3099 | 15.9162 | 18.8971 | 143.2799 | 175.8162 | 118.2307 | 121.0114 | 88.4951 |  | 48.188 | 95.8202 | 49.0794 | 76.7571 | 65.6893 | 133.3777 |  | 76.5453 |  |  | 15.6496 | 18.2551 | 53.3208 | [6 empty] | 66.4371 |  |  | 38.3654 |  |  | 17.7085 | 56.9366 | 194.1391 | 9.9757 | 50.929 | 128.2953 | 11.4836 | 49.7586 | 139.4111 | 23.2612 | 113.1077 | 11.8288 | 101.5378 | 13.9577 | 107.1752 | 11.039 | 53.6521 | 117.4874 | 24.7832 | 49.3506 | 162.5401 | 12.1461 | 44.3256 | 139.0373 | 13.384 | 97.8563 | 21.6453 | 114.8862 | 15.1381 | 114.8446 | 1.245 | 19.1677 | 1.4872 | 0.090354 | -38.1797 | 3.1235 | 241.48 | 50.04 | -1.0113 | -0.16087 | 0.43163 | -0.19861 | 0.37933 | 0.32659 | 0.78509 | -0.51509 | -0.68707 | 0.43997 | -2.3924 | -1.5347 | -0.46749 | -0.29511
42810.4461 | 524 | 18.3518 | 18.4771 | 18.4755 | 18.4793 | 17.7869 | 16.3894 | 14.4431 | 16.5867 | 17.0887 | 17.1855 | 17.1914 | 16.7051 | 15.7111 | 14.3368 | 14.6961 | 14.7605 | 15.4061 | 13.2353 | 13.8847 | 16.4999 |  |  |  | 16.5243 | 16.2722 | 21.4518 | 148.2984 | 136.5245 | 174.2827 | 16.9927 | 16.3594 | 19.2432 | 16.7146 | 16.3138 | 20.1189 | 50.3764 | 154.6847 |  | 83.7168 | 122.4144 | 121.46 | 92.712 |  | 7.0114 | 7.7604 | 6.8309 | 7.8596 | 8.4544 | 11.6986 | 69.4652 | 4.422 | 7.3213 | 4.4491 | 8.3984 | 8.7678 | 41.7553 | 46.796 | 42.862 | 14.7157 |  |  | -0.44859 | 0.10588 | 0.087932 | -0.10514 | 0.070476 | -0.053028 | 0.55911 | 0.55707 | 0.19403 | -0.64468 | 0.12011 | -0.00053719 | -0.00052241 | 0.98233 | 15.8988 | 16.6409 | 17.1788 | 17.4891 | 17.4452 | 16.3856 | 14.7234 | 16.7744 | 17.1074 | 17.4055 | 17.448 | 17.1519 | 16.3113 | 14.496 | 59.4808 | 27.7188 | 38.0931 | 25.1765 | 21.4683 | 31.2955 | 19.6013 | 15.8339 | 15.5078 | 15.4924 | 14.2761 | 15.0106 | 16.9622 |  |  |  | 42.982 | 171.033 | 129.5629 | 75.1643 | 0.81207 | 0.065142 | 46.5286 |  |  | 11.2873 |  |  | 16.8817 | 16.7587 | 24.9769 | 16.3259 | 15.9168 | 18.9272 | 144.2885 | 177.3721 | 118.637 | 121.4241 | 89.8964 |  | 48.3352 | 97.0293 | 49.2478 | 78.2294 | 66.2317 | 133.5655 |  | 76.8084 |  |  | 15.7024 | 18.3204 | 52.9787 | [6 empty] | 66.3927 |  |  | 38.5273 |  |  | 17.7577 | 57.1833 | 195.4139 | 9.9753 | 51.3179 | 128.9139 | 11.5142 | 50.2566 | 140.154 | 23.3791 | 113.5821 | 11.8236 | 102.0665 | 13.9871 | 108.0033 | 11.0642 | 54.2174 | 117.6679 | 24.9276 | 49.6626 | 163.3503 | 12.1668 | 44.4731 | 139.587 | 13.4007 | 98.0252 | 21.7712 | 115.3828 | 15.1773 | 115.1646 | 1.0304 | 19.1595 | 1.4964 | 0.091888 | -38.26 | 3.1236 | 250.28 | 49.24 | -0.98731 | 0.38007 | 0.34636 | -0.37873 | 0.31224 | -0.27085 | 0.87947 | -0.54882 | -0.7147 | 0.41894 | -2.6446 | -1.6382 | -0.5548 | -0.32764
42810.4461 | 525 | 18.3498 | 18.4756 | 18.4706 | 18.4752 | 17.7817 | 16.3877 | 14.4398 | 16.5858 | 17.0862 | 17.1822 | 17.1881 | 16.7027 | 15.7094 | 14.3371 | 14.7012 | 14.7629 | 15.4103 | 13.2369 | 13.8884 | 16.5185 |  |  |  | 16.5251 | 16.2721 | 21.4812 | 148.8719 | 137.341 | 174.5095 | 16.9828 | 16.3513 | 19.2567 | 16.7062 | 16.3076 | 20.1339 | 50.5522 | 155.7897 |  | 84.0003 | 122.9101 | 121.7302 | 94.435 |  | 6.9919 | 7.7573 | 6.8182 | 7.876 | 8.494 | 11.6897 | 70.283 | 4.4576 | 7.3293 | 4.4345 | 8.4063 | 8.7675 | 41.8041 | 46.7683 | 42.8603 | 14.7078 |  |  | -0.6799 | 0.13283 | 0.12802 | -0.042054 | 0.29258 | 0.035024 | 0.10701 | 0.49924 | -0.23934 | 0.17019 | 0.12786 | -0.00051255 | -0.0005684 | 1.0631 | 15.8888 | 16.6444 | 17.173 | 17.488 | 17.4424 | 16.3784 | 14.719 | 16.7654 | 17.1044 | 17.4039 | 17.4438 | 17.1515 | 16.3079 | 14.4936 | 58.577 | 26.3544 | 36.0674 | 24.6085 | 21.751 | 31.4535 | 19.6519 | 15.8358 | 15.5097 | 15.4933 | 14.2809 | 15.0146 | 16.9793 |  |  |  | 43.1589 | 171.5073 | 130.3464 | 76.7057 | 1.0043 | 0.26972 | 46.9142 |  |  | 11.2769 |  |  | 16.8768 | 16.7677 | 25.0166 | 16.3096 | 15.9159 | 18.9395 | 145.2995 | 178.8741 | 119.1593 | 122.0422 | 88.6422 |  | 48.4796 | 96.7307 | 49.395 | 78.5122 | 66.6424 | 135.6943 |  | 77.1357 |  |  | 15.7406 | 18.3673 | 52.7404 | [6 empty] | 66.4663 |  |  | 38.7727 |  |  | 17.8029 | 57.7687 | 196.9228 | 9.9563 | 52.1184 | 129.5234 | 11.5433 | 50.4548 | 140.9731 | 23.5071 | 114.162 | 11.8153 | 102.3979 | 14.0268 | 108.7272 | 11.0997 | 54.9495 | 117.9432 | 25.0758 | 50.1152 | 164.1615 | 12.1967 | 44.8323 | 140.338 | 13.4174 | 98.2545 | 21.9275 | 115.6182 | 15.2146 | 115.3794 | 1.1733 | 19.1534 | 1.5031 | 0.087857 | -38.2217 | 3.1236 | 256.9 | 49.56 | -1.2158 | 0.42569 | 0.41791 | -0.23953 | 0.63619 | 0.22012 | 0.38475 | -0.50888 | -0.7012 | 0.42614 | -2.5256 | -1.4072 | -0.59643 | -0.36427
42810.4461 | 526 | 18.3492 | 18.4813 | 18.4773 | 18.476 | 17.7819 | 16.3869 | 14.4445 | 16.5891 | 17.0935 | 17.1896 | 17.1865 | 16.7056 | 15.7146 | 14.3395 | 14.6946 | 14.76 | 15.4062 | 13.2368 | 13.8902 | 16.5327 |  |  |  | 16.5221 | 16.2712 | 21.5118 | 149.3472 | 138.0997 | 174.8107 | 16.9826 | 16.35 | 19.2822 | 16.6979 | 16.3068 | 20.1533 | 50.7638 | 157.5252 |  | 84.2563 | 123.4001 | 122.0645 | 96.9695 |  | 6.9815 | 7.7611 | 6.821 | 7.8917 | 8.5551 | 11.8227 | 70.9325 | 4.5144 | 7.3288 | 4.435 | 8.4209 | 8.7609 | 41.848 | 46.75 | 42.8594 | 14.7047 |  |  | -0.43939 | 0.083543 | 0.15693 | -0.033514 | 0.49366 | 0.25187 | -0.15518 | 0.48216 | -0.37148 | 0.76853 | 0.006052 | -0.00056512 | -0.00056676 | 1.2036 | 15.8877 | 16.6365 | 17.1651 | 17.4898 | 17.4398 | 16.3821 | 14.7179 | 16.7643 | 17.1033 | 17.4026 | 17.4381 | 17.1422 | 16.3019 | 14.492 | 59.8735 | 26.6393 | 35.6107 | 24.2863 | 21.5298 | 31.6767 | 19.7179 | 15.8356 | 15.5058 | 15.4858 | 14.2767 | 15.014 | 16.9847 |  |  |  | 43.3496 | 171.6408 | 131.0542 | 78.4697 | 1.1265 | 0.79498 | 47.0321 |  |  | 11.2904 |  |  | 16.8793 | 16.772 | 25.0651 | 16.3171 | 15.9265 | 18.9615 | 145.7869 | 180.4374 | 119.9905 | 122.7601 | 87.5347 |  | 48.6135 | 96.914 | 49.5257 | 79.4606 | 67.0279 | 138.2565 |  | 77.4665 |  |  | 15.7949 | 18.4306 | 52.6734 | [6 empty] | 66.2753 |  |  | 39.1056 |  |  | 17.8619 | 58.1213 | 198.6888 | 9.9101 | 52.6969 | 130.6189 | 11.5755 | 50.4828 | 141.8142 | 23.621 | 114.5469 | 11.8178 | 102.665 | 14.0592 | 109.1527 | 11.1343 | 55.5621 | 118.4225 | 25.213 | 50.5183 | 164.9241 | 12.2176 | 45.2223 | 140.9593 | 13.4262 | 98.6424 | 22.0507 | 115.8419 | 15.2457 | 115.6621 | 1.3289 | 19.1435 | 1.513 | 0.088306 | -38.1841 | 3.1236 | 251.7 | 49.52 | -0.97772 | 0.3376 | 0.4627 | -0.21383 | 0.82658 | 0.59042 | -0.46343 | -0.47339 | -0.70166 | 0.41394 | -2.6434 | -1.3487 | -0.65933 | -0.4066
42810.4461 | 527 | 18.3468 | 18.4785 | 18.4816 | 18.4687 | 17.7811 | 16.3825 | 14.4391 | 16.5912 | 17.0911 | 17.1817 | 17.1869 | 16.7027 | 15.7136 | 14.3338 | 14.6907 | 14.7606 | 15.4057 | 13.2268 | 13.8888 | 16.5413 |  |  |  | 16.5202 | 16.2745 | 21.5388 | 149.7455 | 138.6735 | 174.5171 | 16.9757 | 16.3527 | 19.3015 | 16.7019 | 16.3067 | 20.1755 | 50.9829 | 159.8809 |  | 84.5329 | 123.9526 | 122.4895 | 99.8829 |  | 6.981 | 7.7698 | 6.8293 | 7.9273 | 8.6385 | 12.0002 | 71.7405 | 4.6425 | 7.3218 | 4.4559 | 8.4307 | 8.7641 | 41.9033 | 46.7332 | 42.8457 | 14.69 |  |  | -0.76466 | -0.070881 | 0.00448 | -0.14588 | 0.063904 | -0.44796 | 0.18192 | 0.56561 | 0.023367 | -0.22927 | 0.14753 | -0.00058647 | -0.00056019 | 1.0954 | 15.8875 | 16.6327 | 17.1648 | 17.4909 | 17.4392 | 16.3829 | 14.711 | 16.7627 | 17.1077 | 17.4039 | 17.437 | 17.1365 | 16.3031 | 14.496 | 62.503 | 27.6525 | 38.6024 | 24.0544 | 21.3382 | 31.8681 | 19.8329 | 15.8303 | 15.5053 | 15.4858 | 14.2678 | 15.0192 | 17.0037 |  |  |  | 43.526 | 171.4545 | 130.88 | 79.7108 | 0.38965 | 0.4613 | 47.3035 |  |  | 11.2755 |  |  | 16.8831 | 16.7752 | 25.1023 | 16.321 | 15.9265 | 18.9843 | 146.8351 | 182.1322 | 120.8751 | 123.6955 | 87.7939 |  | 48.8051 | 97.0471 | 49.6867 | 80.7622 | 67.4845 | 139.3751 |  | 77.8088 |  |  | 15.827 | 18.4917 | 52.7974 | [6 empty] | 66.5364 |  |  | 39.4047 |  |  | 17.9222 | 58.5059 | 200.7187 | 9.8622 | 52.8964 | 131.8577 | 11.5978 | 50.747 | 142.7386 | 23.7044 | 114.8824 | 11.8334 | 102.9711 | 14.0952 | 109.5969 | 11.1649 | 56.0834 | 119.1063 | 25.3761 | 50.8049 | 165.4594 | 12.2448 | 45.4791 | 141.6409 | 13.4402 | 99.1024 | 22.1754 | 116.0053 | 15.2897 | 116.0495 | 1.2203 | 19.1323 | 1.5216 | 0.088957 | -38.2083 | 3.1236 | 259.26 | 49.04 | -1.2894 | -0.31097 | 0.07818 | -0.44612 | 0.29749 | -0.78763 | 0.50194 | -0.47382 | -0.69966 | 0.39455 | -2.9131 | -1.6677 | -0.73248 | -0.43491
42810.4461 | 528 | 18.347 | 18.475 | 18.4784 | 18.4724 | 17.7769 | 16.3846 | 14.4398 | 16.5864 | 17.0824 | 17.1754 | 17.1853 | 16.7048 | 15.7125 | 14.3361 | 14.6878 | 14.7555 | 15.4035 | 13.2319 | 13.8871 | 16.5496 |  |  |  | 16.5158 | 16.2725 | 21.5688 | 149.9986 | 139.1816 | 173.2532 | 16.9916 | 16.3641 | 19.326 | 16.7156 | 16.3148 | 20.2082 | 51.2126 | 162.4297 |  | 84.8438 | 124.5717 | 123.026 | 99.1675 |  | 6.9784 | 7.7653 | 6.8239 | 7.9468 | 8.6415 | 12.0179 | 71.8829 | 4.6971 | 7.3263 | 4.5065 | 8.4369 | 8.7724 | 41.9657 | 46.7208 | 42.8485 | 14.6869 |  |  | -0.51693 | 0.074999 | 0.20358 | -0.005914 | 0.079676 | -0.34676 | -0.092096 | 0.47624 | -1.0664 | -0.47747 | 0.11077 | -0.00052569 | -0.00054212 | 1.0445 | 15.8867 | 16.6323 | 17.1625 | 17.4873 | 17.4337 | 16.3831 | 14.7181 | 16.7628 | 17.1025 | 17.4013 | 17.4423 | 17.141 | 16.3085 | 14.4966 | 58.7368 | 26.1581 | 39.1411 | 25.1362 | 21.9413 | 31.9782 | 19.9319 | 15.8403 | 15.5184 | 15.4947 | 14.2882 | 15.0284 | 17.0321 |  |  |  | 43.7239 | 171.6263 | 130.5688 | 81.5507 | 0.26343 | -0.090499 | 47.4162 |  |  | 11.283 |  |  | 16.8876 | 16.7757 | 25.1515 | 16.3169 | 15.9193 | 19.0007 | 147.8709 | 184.1362 | 121.6348 | 124.4447 | 88.5287 |  | 48.9583 | 97.0981 | 49.8423 | 85.1251 | 67.9351 | 140.6168 |  | 78.1104 |  |  | 15.8659 | 18.5501 | 53.0073 | [6 empty] | 67.2306 |  |  | 39.5969 |  |  | 17.9898 | 59.0672 | 202.011 | 9.8502 | 53.0698 | 132.7682 | 11.6184 | 51.1271 | 143.9611 | 23.7852 | 115.2534 | 11.8628 | 103.1782 | 14.1315 | 109.9292 | 11.1954 | 56.6968 | 119.7665 | 25.5482 | 51.0654 | 166.2367 | 12.2837 | 45.711 | 142.4653 | 13.4675 | 99.5194 | 22.2872 | 116.0818 | 15.3477 | 116.7627 | 1.0075 | 19.1211 | 1.5285 | 0.087712 | -38.2338 | 3.1235 | 247.1 | 50.4 | -1.0586 | 0.31988 | 0.52702 | -0.089825 | 0.33219 | -0.693 | -0.35714 | -0.48881 | -0.69557 | 0.28992 | -2.4817 | -1.716 | -0.70445 | -0.4791
42810.4462 | 529 | 18.3441 | 18.4707 | 18.4691 | 18.47 | 17.7691 | 16.3808 | 14.4385 | 16.5745 | 17.0848 | 17.1869 | 17.1864 | 16.6967 | 15.7076 | 14.3294 | 14.6949 | 14.7624 | 15.4058 | 13.2275 | 13.8967 | 16.5667 |  |  |  | 16.5146 | 16.2756 | 21.6028 | 150.3648 | 139.7629 | 175.0101 | 16.9804 | 16.345 | 19.3308 | 16.6998 | 16.3095 | 20.2195 | 51.3931 | 163.6 |  | 85.1637 | 125.2241 | 123.5966 | 97.3686 |  | 6.9622 | 7.7686 | 6.819 | 7.9556 | 8.635 | 11.9687 | 72.7936 | 4.7091 | 7.331 | 4.5556 | 8.4481 | 8.7689 | 41.998 | 46.7114 | 42.8451 | 14.6754 |  |  | -0.62798 | -0.051169 | 0.19373 | 0.01577 | 0.023164 | -0.44993 | 0.32123 | 0.21537 | 0.45421 | -0.39858 | 0.11673 | -0.00058483 | -0.00054705 | 1.1215 | 15.8958 | 16.6377 | 17.1696 | 17.5005 | 17.437 | 16.3887 | 14.7263 | 16.7758 | 17.1121 | 17.4088 | 17.4458 | 17.1534 | 16.3136 | 14.5016 | 55.3599 | 24.9068 | 36.9558 | 24.4395 | 21.8667 | 32.0959 | 19.9941 | 15.8363 | 15.5163 | 15.4946 | 14.2839 | 15.0415 | 17.0482 |  |  |  | 43.9134 | 171.2027 | 130.5025 | 82.8648 | 0.67856 | -0.019172 | 47.5311 |  |  | 11.2928 |  |  | 16.8839 | 16.7858 | 25.1857 | 16.3183 | 15.9269 | 19.022 | 148.793 | 186.0183 | 122.4302 | 125.3593 | 89.5834 |  | 49.0873 | 97.2111 | 49.9769 | 88.2221 | 68.3695 | 142.9456 |  | 78.4596 |  |  | 15.9113 | 18.601 | 53.3262 | [6 empty] | 68.1421 |  |  | 39.8131 |  |  | 18.0391 | 59.2752 | 202.9621 | 9.8561 | 53.37 | 134.0799 | 11.6463 | 51.2783 | 145.1127 | 23.89 | 115.674 | 11.9164 | 103.4313 | 14.1602 | 110.271 | 11.2073 | 57.1557 | 120.384 | 25.7161 | 51.4048 | 166.8542 | 12.3117 | 45.862 | 143.2966 | 13.5081 | 99.8795 | 22.3697 | 116.1846 | 15.4076 | 117.4287 | 1.2654 | 19.1131 | 1.5372 | 0.090839 | -38.198 | 3.1236 | 252.87 | 48.99 | -1.1691 | -0.26422 | 0.51411 | 0.14668 | 0.1791 | -0.78932 | 0.66694 | -0.51355 | -0.69394 | 0.21988 | -2.0926 | -1.4659 | -0.64807 | -0.50897
42810.4462 | 530 | 18.3443 | 18.4719 | 18.4768 | 18.4694 | 17.7725 | 16.3846 | 14.4357 | 16.5897 | 17.0795 | 17.1797 | 17.1848 | 16.6953 | 15.7119 | 14.332 | 14.7031 | 14.7665 | 15.4002 | 13.2385 | 13.9055 | 16.592 |  |  |  | 16.5191 | 16.2866 | 21.6335 | 150.9949 | 140.2509 | 175.7939 | 16.9741 | 16.3547 | 19.3481 | 16.6977 | 16.3097 | 20.2504 | 51.5696 | 165.1568 |  | 85.4965 | 125.8036 | 124.1988 | 96.1697 |  | 6.9516 | 7.7805 | 6.8162 | 7.9452 | 8.6358 | 11.9463 | 73.2217 | 4.6505 | 7.3351 | 4.588 | 8.4518 | 8.7764 | 42.0217 | 46.7009 | 42.8474 | 14.6729 |  |  | -0.55833 | 0.13808 | 0.17204 | 0.028914 | -0.04912 | -0.11808 | 0.31334 | 0.40988 | -0.36895 | 0.046403 | 0.03228 | -0.0005684 | -0.0005799 | 1.0917 | 15.9 | 16.644 | 17.1701 | 17.4946 | 17.4404 | 16.3831 | 14.7212 | 16.7704 | 17.1141 | 17.4024 | 17.4455 | 17.1558 | 16.31 | 14.4995 | 54.9509 | 25.0546 | 36.0852 | 23.6005 | 21.5267 | 32.2259 | 20.0436 | 15.8372 | 15.5064 | 15.4906 | 14.2771 | 15.0469 | 17.0619 |  |  |  | 44.1039 | 170.831 | 130.659 | 83.6614 | 0.51911 | 0.13026 | 47.7138 |  |  | 11.2948 |  |  | 16.8862 | 16.7849 | 25.2383 | 16.3187 | 15.9323 | 19.0455 | 149.4707 | 187.3739 | 123.2444 | 126.2536 | 89.9165 |  | 49.256 | 97.5238 | 50.1307 | 91.3028 | 68.953 | 144.633 |  | 78.8544 |  |  | 15.9608 | 18.6682 | 53.8625 | [6 empty] | 71.1927 |  |  | 40.0252 |  |  | 18.1024 | 59.7417 | 203.6304 | 9.8538 | 53.722 | 135.2365 | 11.6802 | 51.5877 | 146.2658 | 24.0193 | 116.3222 | 11.9788 | 103.7651 | 14.1868 | 110.6133 | 11.2208 | 57.3992 | 120.9348 | 25.8704 | 51.7798 | 167.7519 | 12.3373 | 46.0255 | 143.8845 | 13.5454 | 100.2779 | 22.4618 | 116.3175 | 15.4528 | 117.7931 | 1.1117 | 19.1048 | 1.5451 | 0.091512 | -38.1963 | 3.1235 | 260.4 | 49.06 | -1.1033 | 0.43405 | 0.48449 | 0.19862 | -0.26079 | -0.40435 | 0.65868 | -0.51683 | -0.69717 | 0.1558 | -2.0319 | -1.3634 | -0.60849 | -0.52442
42810.4462 | 531 | 18.3443 | 18.4699 | 18.4665 | 18.4748 | 17.7803 | 16.3858 | 14.4382 | 16.5876 | 17.08 | 17.1798 | 17.1825 | 16.6948 | 15.7047 | 14.3285 | 14.6942 | 14.7571 | 15.4014 | 13.2289 | 13.8964 | 16.5982 |  |  |  | 16.5229 | 16.2794 | 21.6581 | 151.6047 | 140.7007 | 177.5482 | 16.9787 | 16.3521 | 19.374 | 16.7059 | 16.313 | 20.2859 | 51.7311 | 168.2689 |  | 85.8554 | 126.195 | 124.8321 | 94.1695 |  | 6.952 | 7.7938 | 6.8335 | 7.9522 | 8.6341 | 11.9389 | 73.8476 | 4.5577 | 7.3407 | 4.6133 | 8.4636 | 8.7815 | 42.0308 | 46.6917 | 42.8634 | 14.6657 |  |  | -0.61944 | -0.10571 | 0.17862 | 0.089366 | 0.16444 | -0.11611 | 0.43031 | 0.77326 | -0.14769 | -0.020733 | 0.036851 | -0.00054869 | -0.00054705 | 0.99023 | 15.8938 | 16.6361 | 17.1669 | 17.4866 | 17.4392 | 16.3776 | 14.7119 | 16.7663 | 17.1071 | 17.3987 | 17.4386 | 17.1492 | 16.3055 | 14.4982 | 54.051 | 24.7688 | 35.3211 | 23.0627 | 21.1303 | 32.3436 | 20.1042 | 15.8283 | 15.5078 | 15.4967 | 14.2813 | 15.0486 | 17.0785 |  |  |  | 44.3215 | 171.2034 | 131.0803 | 85.9752 | 1.0457 | -0.14131 | 48.0374 |  |  | 11.2899 |  |  | 16.8803 | 16.7894 | 25.2799 | 16.32 | 15.9212 | 19.0617 | 149.8538 | 188.6514 | 123.9526 | 127.0787 | 90.4865 |  | 49.4465 | 97.9166 | 50.291 | 89.5364 | 69.57 | 145.9547 |  | 79.2257 |  |  | 16.001 | 18.6916 | 54.6834 | [6 empty] | 71.407 |  |  | 40.2492 |  |  | 18.1823 | 60.4234 | 205.488 | 9.857 | 54.0157 | 136.0131 | 11.7143 | 52.15 | 147.4089 | 24.1367 | 116.8553 | 12.0434 | 104.0551 | 14.2176 | 110.8971 | 11.2457 | 58.1385 | 121.7445 | 25.9961 | 52.2242 | 168.2858 | 12.3675 | 46.4341 | 144.7336 | 13.5828 | 100.554 | 22.5564 | 116.3241 | 15.4887 | 118.1573 | 1.2787 | 19.0943 | 1.5516 | 0.089507 | -38.1876 | 3.1236 | 268.44 | 50.16 | -1.1644 | -0.37978 | 0.49367 | 0.34919 | 0.47716 | -0.40096 | 0.77188 | -0.52592 | -0.7024 | 0.22762 | -1.9181 | -1.2714 | -0.54719 | -0.58107
42810.4462 | 532 | 18.3443 | 18.47 | 18.4733 | 18.4716 | 17.7739 | 16.3811 | 14.4399 | 16.5868 | 17.0813 | 17.1759 | 17.1781 | 16.6979 | 15.7086 | 14.331 | 14.6871 | 14.7539 | 15.4134 | 13.2235 | 13.8964 | 16.6121 |  |  |  | 16.5126 | 16.2854 | 21.6865 | 152.1698 | 141.0135 | 177.1714 | 16.9742 | 16.3616 | 19.3994 | 16.7068 | 16.3209 | 20.3122 | 51.9048 | 169.9221 |  | 86.2246 | 126.7005 | 125.443 | 95.3509 |  | 6.947 | 7.8093 | 6.8597 | 7.994 | 8.6481 | 11.9978 | 73.3273 | 4.5063 | 7.3655 | 4.6164 | 8.4902 | 8.7888 | 42.0308 | 46.6905 | 42.8651 | 14.659 |  |  | -0.55242 | -0.020941 | 0.26667 | 0.30687 | -0.015608 | -0.10297 | 0.51311 | 0.45588 | -0.23623 | -0.35851 | 0.15925 | -0.00057662 | -0.00057333 | 0.8775 | 15.8924 | 16.6389 | 17.1723 | 17.4909 | 17.4424 | 16.3894 | 14.7144 | 16.7724 | 17.1081 | 17.4074 | 17.4377 | 17.1476 | 16.3068 | 14.4978 | 54.7074 | 25.239 | 33.4583 | 22.2754 | 20.6113 | 32.4961 | 20.1392 | 15.8238 | 15.5112 | 15.5048 | 14.2807 | 15.0565 | 17.0875 |  |  |  | 44.5633 | 171.2028 | 131.2097 | 88.4263 | 0.68403 | 0.059496 | 48.1246 |  |  | 11.2881 |  |  | 16.8785 | 16.791 | 25.3152 | 16.3151 | 15.9268 | 19.0886 | 150.6849 | 189.9512 | 124.7368 | 127.835 | 91.3735 |  | 49.5903 | 98.0675 | 50.4228 | 87.6707 | 70.0994 | 145.8534 |  | 79.5316 |  |  | 16.0022 | 18.7265 | 54.9573 | [6 empty] | 70.1361 |  |  | 40.5169 |  |  | 18.2449 | 60.558 | 207.3613 | 9.8947 | 54.3025 | 136.8198 | 11.7199 | 52.5424 | 148.3269 | 24.2712 | 117.2773 | 12.1189 | 104.4417 | 14.2599 | 111.3205 | 11.2785 | 59.1457 | 122.6562 | 26.1006 | 52.6805 | 168.7496 | 12.3908 | 46.8514 | 145.5721 | 13.6493 | 100.9911 | 22.6718 | 116.4669 | 15.5354 | 119.0972 | 1.2037 | 19.0881 | 1.5603 | 0.089963 | -38.2116 | 3.1235 | 277.28 | 49 | -1.0992 | -0.16904 | 0.60322 | 0.6471 | -0.14702 | -0.37762 | 0.84296 | -0.54547 | -0.70192 | 0.29899 | -1.9731 | -1.0604 | -0.57383 | -0.64069
42810.4462 | 533 | 18.3471 | 18.4726 | 18.4779 | 18.4706 | 17.7801 | 16.3774 | 14.442 | 16.5901 | 17.0857 | 17.18 | 17.1782 | 16.693 | 15.7075 | 14.3345 | 14.6926 | 14.7653 | 15.419 | 13.2317 | 13.9035 | 16.6298 |  |  |  | 16.5218 | 16.2923 | 21.7249 | 152.7238 | 141.4485 | 177.9904 | 16.9757 | 16.3658 | 19.4128 | 16.7008 | 16.3196 | 20.3232 | 52.12 | 171.3775 |  | 86.5931 | 127.3728 | 126.1114 | 98.8981 |  | 6.9377 | 7.8009 | 6.8517 | 8.0107 | 8.6657 | 12.0742 | 72.9436 | 4.5024 | 7.3652 | 4.5853 | 8.4943 | 8.7787 | 42.0293 | 46.6998 | 42.8683 | 14.6417 |  |  | -1.2444 | -0.12017 | 0.2555 | -0.090682 | 0.43386 | 0.19339 | 0.39351 | 0.47559 | -0.20607 | -0.40341 | 0.031684 | -0.00057005 | -0.00058319 | 0.89547 | 15.8942 | 16.6365 | 17.1718 | 17.4875 | 17.4398 | 16.3846 | 14.7188 | 16.7648 | 17.1059 | 17.3978 | 17.4292 | 17.151 | 16.3036 | 14.4919 | 54.931 | 24.9864 | 32.8259 | 21.4039 | 19.9892 | 32.6194 | 20.179 | 15.8363 | 15.5162 | 15.5116 | 14.2917 | 15.0685 | 17.1211 |  |  |  | 44.8207 | 171.2496 | 131.2739 | 91.3291 | 0.71543 | 0.29889 | 48.1896 |  |  | 11.2862 |  |  | 16.8748 | 16.7924 | 25.3658 | 16.3162 | 15.9328 | 19.1004 | 151.3583 | 191.0782 | 125.3013 | 128.4872 | 91.1266 |  | 49.7489 | 97.7973 | 50.5612 | 85.3312 | 70.5252 | 145.5272 |  | 79.8085 |  |  | 16.0453 | 18.7735 | 55.6559 | [6 empty] | 69.3334 |  |  | 40.7254 |  |  | 18.278 | 60.9508 | 208.8031 | 9.8889 | 54.7982 | 137.5375 | 11.7218 | 52.9027 | 149.2543 | 24.3826 | 117.6278 | 12.1512 | 104.7865 | 14.3101 | 111.6806 | 11.3043 | 59.5835 | 123.4748 | 26.2497 | 52.926 | 169.7492 | 12.4198 | 47.065 | 146.5683 | 13.6929 | 101.3375 | 22.8278 | 116.7103 | 15.5719 | 119.8422 | 1.28 | 19.08 | 1.5682 | 0.090137 | -38.2559 | 3.1235 | 256.56 | 49.16 | -1.6512 | -0.40492 | 0.59044 | -0.35176 | 0.77524 | 0.51758 | 0.73831 | -0.533 | -0.68951 | 0.37972 | -1.9834 | -0.98545 | -0.6647 | -0.71229
42810.4462 | 534 | 18.3444 | 18.4705 | 18.4755 | 18.4647 | 17.7743 | 16.377 | 14.4343 | 16.5836 | 17.0865 | 17.1809 | 17.1713 | 16.6936 | 15.699 | 14.3241 | 14.6898 | 14.7572 | 15.4132 | 13.2335 | 13.913 | 16.6462 |  |  |  | 16.5253 | 16.294 | 21.7629 | 153.1847 | 141.8709 | 176.9717 | 16.979 | 16.3698 | 19.4323 | 16.7046 | 16.3258 | 20.3507 | 52.3375 | 173.8799 |  | 86.9402 | 128.1916 | 126.8259 | 98.6666 |  | 6.9312 | 7.8084 | 6.8638 | 8.0436 | 8.697 | 12.2564 | 72.7722 | 4.5324 | 7.3692 | 4.5448 | 8.5118 | 8.7791 | 42.035 | 46.7053 | 42.875 | 14.6436 |  |  | -0.66675 | -0.13922 | 0.11356 | -0.11499 | 0.34909 | 0.15199 | 0.46777 | 0.1812 | -0.0823 | -1.3081 | 0.21628 | -0.00054048 | -0.00054212 | 0.92099 | 15.8921 | 16.6345 | 17.1697 | 17.4934 | 17.4344 | 16.3846 | 14.7146 | 16.7604 | 17.105 | 17.3971 | 17.4301 | 17.1498 | 16.3046 | 14.499 | 54.3342 | 25.2849 | 34.3297 | 21.5362 | 19.5799 | 32.7437 | 20.2508 | 15.8266 | 15.5102 | 15.5011 | 14.2829 | 15.0683 | 17.1395 |  |  |  | 45.0466 | 171.2982 | 131.0195 | 92.4597 | 0.79546 | 0.43025 | 48.2751 |  |  | 11.2967 |  |  | 16.8823 | 16.803 | 25.4167 | 16.3247 | 15.9421 | 19.1271 | 152.0942 | 192.1051 | 125.7556 | 129.0704 | 90.5696 |  | 49.9321 | 97.7003 | 50.7192 | 91.3467 | 71.0796 | 145.8358 |  | 80.2095 |  |  | 16.1041 | 18.8493 | 56.0377 | [6 empty] | 71.5654 |  |  | 40.7747 |  |  | 18.317 | 61.5373 | 209.1608 | 9.9051 | 55.2615 | 138.207 | 11.7455 | 53.3224 | 150.3545 | 24.5101 | 117.9618 | 12.1723 | 105.124 | 14.3435 | 112.0958 | 11.3009 | 59.8823 | 124.0741 | 26.3877 | 53.1239 | 170.4423 | 12.4362 | 47.5159 | 147.3927 | 13.6752 | 101.7778 | 22.9482 | 116.9505 | 15.613 | 120.5431 | 1.0965 | 19.0748 | 1.5739 | 0.087575 | -38.2845 | 3.1235 | 268.81 | 49.87 | -1.2073 | -0.43585 | 0.39364 | -0.39612 | 0.69561 | 0.459 | 0.80522 | -0.51104 | -0.68121 | 0.23314 | -1.9025 | -1.1441 | -0.65053 | -0.73578
42810.4462 | 535 | 18.3483 | 18.4648 | 18.4731 | 18.4604 | 17.7684 | 16.3829 | 14.4355 | 16.5816 | 17.0809 | 17.1773 | 17.176 | 16.6988 | 15.7044 | 14.3225 | 14.6841 | 14.7582 | 15.4157 | 13.2272 | 13.8982 | 16.6514 |  |  |  | 16.5186 | 16.2991 | 21.7866 | 153.5437 | 142.2568 | 176.0491 | 16.9832 | 16.3738 | 19.459 | 16.7072 | 16.3288 | 20.3801 | 52.5859 | 176.4439 |  | 87.3006 | 129.0308 | 127.5258 | 100.1425 |  | 6.924 | 7.8263 | 6.8696 | 8.0534 | 8.7239 | 12.5386 | 74.0237 | 4.6234 | 7.3759 | 4.5143 | 8.5224 | 8.7793 | 42.0347 | 46.7198 | 42.9021 | 14.636 |  |  | -0.44793 | 0.034259 | 0.09582 | -0.077538 | 0.25512 | 0.3327 | 0.20426 | 0.50647 | 0.022784 | -0.30879 | 0.11017 | -0.00057333 | -0.00056348 | 0.9456 | 15.8804 | 16.6244 | 17.1578 | 17.4837 | 17.4242 | 16.3716 | 14.7119 | 16.7602 | 17.0929 | 17.3928 | 17.4262 | 17.1404 | 16.3001 | 14.4835 | 53.6532 | 25.3283 | 34.6528 | 22.7966 | 19.6584 | 32.8512 | 20.3121 | 15.8206 | 15.5092 | 15.4983 | 14.2723 | 15.0659 | 17.1429 |  |  |  | 45.2618 | 171.2964 | 130.8774 | 93.1564 | 0.81673 | 0.35779 | 48.2438 |  |  | 11.2918 |  |  | 16.8787 | 16.8051 | 25.4511 | 16.3196 | 15.9422 | 19.1434 | 152.7071 | 193.1123 | 126.2534 | 129.6313 | 89.9873 |  | 50.0932 | 98.7428 | 50.8617 | 95.0989 | 71.509 | 146.776 |  | 80.5199 |  |  | 16.0928 | 18.8796 | 56.0865 | [6 empty] | 73.3296 |  |  | 40.9391 |  |  | 18.3848 | 62.1693 | 210.6537 | 9.9138 | 55.4593 | 138.9376 | 11.7872 | 53.3613 | 151.1873 | 24.5999 | 118.3355 | 12.2034 | 105.4855 | 14.378 | 112.475 | 11.2735 | 60.0812 | 124.7378 | 26.5597 | 53.7172 | 170.6968 | 12.4552 | 48.0965 | 147.9647 | 13.6876 | 102.2883 | 23.0343 | 117.3337 | 15.6475 | 121.1654 | 1.1872 | 19.0658 | 1.5822 | 0.088096 | -38.2392 | 3.1235 | 273.22 | 48.91 | -0.98854 | 0.21622 | 0.3616 | -0.32528 | 0.59496 | 0.67942 | 0.53236 | -0.48916 | -0.70511 | 0.14482 | -1.8142 | -1.1729 | -0.68269 | -0.74758
42810.4462 | 536 | 18.3499 | 18.4755 | 18.4727 | 18.4665 | 17.7737 | 16.3811 | 14.4408 | 16.5843 | 17.0891 | 17.1807 | 17.1747 | 16.7002 | 15.7056 | 14.3284 | 14.6852 | 14.7539 | 15.41 | 13.2271 | 13.8993 | 16.6638 |  |  |  | 16.5222 | 16.3018 | 21.8157 | 153.7316 | 142.5415 | 175.3092 | 16.972 | 16.3686 | 19.4706 | 16.7023 | 16.3251 | 20.3936 | 52.8458 | 176.8175 |  | 87.6316 | 129.8552 | 128.0965 | 103.0235 |  | 6.9328 | 7.8495 | 6.8731 | 8.0628 | 8.7379 | 12.7207 | 76.0484 | 4.7194 | 7.3817 | 4.5343 | 8.5334 | 8.7861 | 42.0529 | 46.7199 | 42.9271 | 14.6258 |  |  | -0.64178 | -0.096509 | -0.044148 | -0.10842 | 0.44306 | -0.13122 | 0.21872 | 0.42368 | -0.35863 | 0.28348 | -0.03647 | -0.00053883 | -0.00053719 | 0.98147 | 15.8869 | 16.6318 | 17.1618 | 17.4928 | 17.4367 | 16.3736 | 14.7156 | 16.7678 | 17.0984 | 17.4014 | 17.4406 | 17.146 | 16.3072 | 14.4907 | 52.7307 | 25.8552 | 35.7774 | 22.8477 | 19.9338 | 32.9445 | 20.3881 | 15.824 | 15.5091 | 15.5007 | 14.2679 | 15.0743 | 17.1635 |  |  |  | 45.4716 | 171.6944 | 131.0304 | 93.4631 | 0.495 | 0.37266 | 48.4251 |  |  | 11.3067 |  |  | 16.8765 | 16.8146 | 25.4885 | 16.317 | 15.9453 | 19.1635 | 153.322 | 194.0959 | 126.7742 | 130.1707 | 89.8914 |  | 50.259 | 99.6175 | 51.016 | 96.5437 | 71.9187 | 148.2199 |  | 80.8392 |  |  | 16.0844 | 18.9333 | 56.1681 | [6 empty] | 73.3915 |  |  | 41.0619 |  |  | 18.4192 | 62.8618 | 212.3998 | 9.9701 | 55.6701 | 139.8337 | 11.8326 | 53.7802 | 151.8483 | 24.6905 | 118.7398 | 12.2442 | 105.8791 | 14.42 | 112.8804 | 11.2568 | 60.3562 | 125.4283 | 26.7454 | 54.2053 | 170.6913 | 12.4637 | 48.1422 | 148.6765 | 13.6711 | 102.8378 | 23.1425 | 117.8614 | 15.6891 | 121.591 | 1.2527 | 19.0554 | 1.5899 | 0.087828 | -38.2041 | 3.1235 | 284.79 | 49.7 | -1.1823 | -0.36291 | -0.24546 | -0.38466 | 0.7843 | -0.42683 | 0.55106 | -0.48062 | -0.72393 | 0.11988 | -1.7007 | -1.289 | -0.75346 | -0.74873
42810.4463 | 537 | 18.351 | 18.4797 | 18.47 | 18.4681 | 17.7821 | 16.3831 | 14.4387 | 16.5816 | 17.0743 | 17.181 | 17.1816 | 16.7017 | 15.7132 | 14.331 | 14.6711 | 14.7495 | 15.4059 | 13.2258 | 13.9021 | 16.6814 |  |  |  | 16.5132 | 16.3 | 21.8436 | 154.1158 | 142.7766 | 177.9323 | 16.9649 | 16.3623 | 19.5004 | 16.6991 | 16.3262 | 20.424 | 53.1307 | 176.3791 |  | 87.9711 | 130.4902 | 128.7046 | 104.365 |  | 6.9323 | 7.8594 | 6.8762 | 8.0745 | 8.742 | 12.838 | 78.6045 | 4.8298 | 7.3831 | 4.5685 | 8.549 | 8.7819 | 42.0697 | 46.7083 | 42.9503 | 14.6085 |  |  | -0.65164 | 0.017175 | 0.16547 | -0.18531 | 0.19336 | 0.039624 | 0.43163 | 0.19106 | -0.27904 | -0.26452 | 0.040824 | -0.00056348 | -0.00056019 | 0.97679 | 15.884 | 16.6269 | 17.1666 | 17.4905 | 17.4361 | 16.374 | 14.7127 | 16.7636 | 17.1004 | 17.4034 | 17.4373 | 17.142 | 16.3031 | 14.4869 | 50.9407 | 25.0195 | 35.6319 | 22.5482 | 19.6391 | 33.0249 | 20.4626 | 15.8205 | 15.5231 | 15.5157 | 14.2811 | 15.0842 | 17.1774 |  |  |  | 45.6872 | 172.2039 | 131.0173 | 93.2216 | 0.84084 | -0.042697 | 48.617 |  |  | 11.3014 |  |  | 16.8721 | 16.807 | 25.53 | 16.312 | 15.9336 | 19.1804 | 153.7202 | 194.6766 | 127.4159 | 130.8115 | 90.2011 |  | 50.4379 | 100.7226 | 51.1918 | 97.571 | 72.2996 | 148.3642 |  | 81.242 |  |  | 16.1155 | 18.9986 | 56.6621 | [6 empty] | 73.0474 |  |  | 41.1535 |  |  | 18.4886 | 63.567 | 213.7604 | 10.0246 | 55.9379 | 140.6357 | 11.8918 | 54.3669 | 152.6159 | 24.7894 | 119.3033 | 12.2876 | 106.3363 | 14.472 | 113.3893 | 11.2068 | 60.7409 | 126.0584 | 26.9029 | 54.4925 | 170.8844 | 12.4688 | 48.2102 | 149.2396 | 13.6424 | 103.4055 | 23.261 | 118.1023 | 15.7264 | 122.1915 | 1.2349 | 19.0443 | 1.5961 | 0.086475 | -38.2321 | 3.1235 | 303.4 | 49.74 | -1.1948 | 0.1531 | 0.47521 | -0.50289 | 0.51823 | 0.2346 | 0.77428 | -0.48288 | -0.74838 | 0.10548 | -1.4924 | -1.2641 | -0.78056 | -0.73445
42810.4463 | 538 | 18.3383 | 18.4708 | 18.4614 | 18.4679 | 17.7709 | 16.366 | 14.4298 | 16.5791 | 17.0796 | 17.1742 | 17.1771 | 16.6897 | 15.705 | 14.3209 | 14.6744 | 14.7556 | 15.4063 | 13.2323 | 13.9132 | 16.7 |  |  |  | 16.5198 | 16.3007 | 21.8787 | 154.6035 | 143.0734 | 180.0689 | 16.9691 | 16.3763 | 19.5179 | 16.7064 | 16.3372 | 20.4483 | 53.4112 | 178.4222 |  | 88.3618 | 131.0472 | 129.2778 | 107.7651 |  | 6.9381 | 7.8674 | 6.8796 | 8.0964 | 8.7527 | 13.0246 | 80.0367 | 4.8854 | 7.3962 | 4.5868 | 8.5613 | 8.7865 | 42.0828 | 46.6988 | 42.9862 | 14.604 |  |  | -0.45713 | 0.13874 | 0.10436 | -0.38507 | 0.06456 | -0.22059 | 0.37052 | 0.44076 | -0.63049 | -0.26389 | -0.049584 | -0.00055198 | -0.00057169 | 0.94236 | 15.8813 | 16.6298 | 17.1746 | 17.4856 | 17.4318 | 16.3804 | 14.7112 | 16.7603 | 17.0957 | 17.4011 | 17.4372 | 17.1381 | 16.3031 | 14.4847 | 51.6499 | 25.044 | 35.0251 | 22.8223 | 20.5458 | 33.1052 | 20.5277 | 15.8288 | 15.5179 | 15.5159 | 14.2754 | 15.0914 | 17.1917 |  |  |  | 45.9026 | 171.8804 | 130.756 | 93.0452 | 0.13599 | 1.0107 | 48.7212 |  |  | 11.3048 |  |  | 16.8757 | 16.8156 | 25.5848 | 16.3142 | 15.9384 | 19.2 | 154.4412 | 195.3631 | 128.056 | 131.4726 | 91.0355 |  | 50.633 | 102.232 | 51.3537 | 97.4323 | 72.6555 | 148.5012 |  | 81.6203 |  |  | 16.1181 | 19.0564 | 56.796 | [6 empty] | 73.7888 |  |  | 41.4119 |  |  | 18.5431 | 64.0055 | 215.576 | 10.0359 | 56.2039 | 141.2939 | 11.9322 | 54.5926 | 153.518 | 24.9214 | 119.6026 | 12.3085 | 106.7894 | 14.5145 | 113.6494 | 11.1866 | 61.1979 | 126.8495 | 27.0579 | 54.8852 | 171.4064 | 12.4815 | 48.6671 | 150.1587 | 13.6182 | 103.9551 | 23.3723 | 118.2573 | 15.7669 | 123.0064 | 1.2825 | 19.0342 | 1.6046 | 0.08756 | -38.1944 | 3.1235 | 287.35 | 48.8 | -1.0031 | 0.43514 | 0.3774 | -0.72494 | 0.29955 | -0.5537 | 0.71761 | -0.49913 | -0.78456 | 0.12255 | -1.5617 | -1.1891 | -0.86501 | -0.72198
42810.4463 | 539 | 18.3427 | 18.4739 | 18.4669 | 18.4634 | 17.7787 | 16.3743 | 14.4382 | 16.5816 | 17.0777 | 17.1779 | 17.1805 | 16.6978 | 15.7036 | 14.3309 | 14.6762 | 14.7511 | 15.4057 | 13.2324 | 13.9112 | 16.7195 |  |  |  | 16.5237 | 16.3091 | 21.9062 | 155.1373 | 143.3438 | 180.36 | 16.9728 | 16.3737 | 19.5394 | 16.7019 | 16.3319 | 20.4775 | 53.7358 | 179.1144 |  | 88.6933 | 131.6127 | 129.7567 | 113.4469 |  | 6.9575 | 7.8694 | 6.8887 | 8.1129 | 8.7716 | 12.993 | 81.0536 | 4.7606 | 7.4026 | 4.595 | 8.5796 | 8.7844 | 42.0829 | 46.6813 | 43.0024 | 14.5992 |  |  | -0.5649 | 0.14005 | -0.029692 | -0.10974 | 0.26104 | -0.15817 | 0.18521 | 0.67666 | -0.36311 | 0.27173 | 0.20455 | -0.00056512 | -0.00056348 | 0.94529 | 15.8914 | 16.6321 | 17.1697 | 17.4914 | 17.4293 | 16.3738 | 14.7121 | 16.7642 | 17.092 | 17.3937 | 17.4366 | 17.1354 | 16.3014 | 14.4865 | 48.9376 | 24.3066 | 36.8144 | 23.822 | 21.9968 | 33.1591 | 20.6231 | 15.821 | 15.5132 | 15.513 | 14.2766 | 15.0914 | 17.2079 |  |  |  | 46.1101 | 171.535 | 130.7448 | 93.6028 | 0.54646 | -0.325 | 48.7225 |  |  | 11.3128 |  |  | 16.8726 | 16.8161 | 25.6212 | 16.3179 | 15.9432 | 19.2193 | 155.0799 | 196.1379 | 128.7265 | 132.1744 | 91.3243 |  | 50.7948 | 103.3957 | 51.5087 | 98.7553 | 73.1165 | 149.292 |  | 81.9395 |  |  | 16.1121 | 19.0982 | 56.7715 | [6 empty] | 74.7849 |  |  | 41.5679 |  |  | 18.6049 | 64.2117 | 217.0461 | 10.0556 | 56.5064 | 141.9391 | 11.9672 | 54.8014 | 154.2015 | 25.0524 | 119.8388 | 12.3096 | 107.5508 | 14.552 | 113.9002 | 11.1822 | 61.7697 | 127.8275 | 27.1966 | 55.2883 | 172.4742 | 12.5255 | 48.9143 | 151.0034 | 13.632 | 104.4792 | 23.4525 | 118.4718 | 15.812 | 123.342 | 1.3093 | 19.0271 | 1.6124 | 0.087821 | -38.2293 | 3.1235 | 274.69 | 50.11 | -1.1154 | 0.4372 | -0.20131 | -0.387 | 0.6023 | -0.46883 | 0.50733 | -0.50141 | -0.81138 | 0.10294 | -1.254 | -1.3767 | -1.0113 | -0.73018
42810.4463 | 540 | 18.3382 | 18.4686 | 18.4648 | 18.4662 | 17.7744 | 16.3775 | 14.4365 | 16.5838 | 17.0751 | 17.1803 | 17.1767 | 16.6896 | 15.701 | 14.326 | 14.6715 | 14.7484 | 15.3982 | 13.2257 | 13.9113 | 16.7292 |  |  |  | 16.5218 | 16.3063 | 21.9378 | 155.6247 | 143.8061 | 180.7752 | 16.9751 | 16.3704 | 19.5594 | 16.7013 | 16.3322 | 20.5054 | 54.0834 | 179.2467 |  | 89.0138 | 132.3119 | 130.2067 | 117.4157 |  | 6.9655 | 7.8854 | 6.8855 | 8.1165 | 8.7871 | 12.9222 | 81.7516 | 4.544 | 7.3978 | 4.6213 | 8.5948 | 8.7893 | 42.0796 | 46.658 | 43.0045 | 14.5923 |  |  | -0.68384 | 0.16765 | -0.013264 | -0.14325 | 0.27155 | -0.084572 | 0.26998 | 0.55576 | -0.3958 | 0.062348 | 0.27052 | -0.00053226 | -0.00056348 | 0.9458 | 15.8861 | 16.6266 | 17.1649 | 17.4867 | 17.4273 | 16.3747 | 14.7037 | 16.7647 | 17.093 | 17.3938 | 17.4268 | 17.1329 | 16.3063 | 14.4872 | 47.8867 | 22.6487 | 34.2978 | 23.5622 | 22.6526 | 33.217 | 20.6635 | 15.8188 | 15.5117 | 15.5109 | 14.2818 | 15.0925 | 17.2302 |  |  |  | 46.3114 | 171.2816 | 131.0604 | 93.8572 | 0.24742 | -0.054553 | 48.8153 |  |  | 11.3222 |  |  | 16.871 | 16.8228 | 25.6724 | 16.3223 | 15.95 | 19.2511 | 155.4896 | 196.9052 | 129.2535 | 132.7202 | 91.3462 |  | 50.9701 | 104.5956 | 51.6842 | 99.1859 | 73.7207 | 150.2469 |  | 82.255 |  |  | 16.0706 | 19.1038 | 57.0342 | [6 empty] | 75.7625 |  |  | 41.5825 |  |  | 18.6479 | 64.7048 | 218.61 | 10.0801 | 57.0619 | 142.6406 | 12.0103 | 55.2466 | 154.7936 | 25.1726 | 120.1048 | 12.3457 | 108.2738 | 14.5912 | 114.0691 | 11.2003 | 62.29 | 128.565 | 27.336 | 55.6126 | 173.7103 | 12.5696 | 49.1526 | 151.7379 | 13.6748 | 104.7617 | 23.5378 | 118.7812 | 15.8483 | 123.8064 | 1.3771 | 19.0166 | 1.6186 | 0.08612 | -38.2339 | 3.1235 | 282.96 | 49.54 | -1.2278 | 0.47836 | -0.13455 | -0.44218 | 0.61423 | -0.34278 | 0.61245 | -0.4958 | -0.83847 | 0.11347 | -1.1305 | -1.0924 | -1.1091 | -0.73017
42810.4463 | 541 | 18.3347 | 18.4654 | 18.4666 | 18.4658 | 17.7659 | 16.3773 | 14.4314 | 16.579 | 17.074 | 17.1792 | 17.1769 | 16.6961 | 15.7018 | 14.3289 | 14.6735 | 14.7552 | 15.4127 | 13.2292 | 13.9181 | 16.7501 |  |  |  | 16.5202 | 16.3173 | 21.9815 | 156.2006 | 144.3314 | 182.1148 | 16.9731 | 16.3776 | 19.5798 | 16.7044 | 16.3389 | 20.5279 | 54.3874 | 178.7332 |  | 89.3353 | 133.1432 | 130.7099 | 118.4807 |  | 6.9777 | 7.9063 | 6.8969 | 8.1403 | 8.8046 | 12.8807 | 82.4245 | 4.4339 | 7.4062 | 4.6902 | 8.6245 | 8.7902 | 42.0767 | 46.6223 | 43.0052 | 14.5814 |  |  | -0.76138 | 0.051343 | 0.10896 | -0.45998 | 0.20913 | -0.029372 | 0.13592 | 0.80678 | -0.37907 | -0.61573 | 0.16064 | -0.00052733 | -0.00062262 | 0.89305 | 15.8965 | 16.6274 | 17.1696 | 17.4889 | 17.4339 | 16.376 | 14.7139 | 16.7651 | 17.0929 | 17.4079 | 17.4329 | 17.1456 | 16.3031 | 14.5036 | 46.478 | 20.9423 | 31.4771 | 22.8028 | 21.3311 | 33.2665 | 20.6933 | 15.8152 | 15.5063 | 15.5067 | 14.2749 | 15.0931 | 17.2409 |  |  |  | 46.4971 | 170.9723 | 131.5053 | 93.777 | 1.027 | -0.26534 | 48.983 |  |  | 11.3273 |  |  | 16.8735 | 16.8353 | 25.7208 | 16.3134 | 15.9544 | 19.2743 | 156.1626 | 197.3711 | 129.7579 | 133.1999 | 92.7914 |  | 51.1636 | 105.5129 | 51.8617 | 99.5137 | 74.2605 | 149.3937 |  | 82.5656 |  |  | 16.0602 | 19.1016 | 57.5558 | [6 empty] | 77.1886 |  |  | 41.6272 |  |  | 18.716 | 65.3226 | 219.2844 | 10.1385 | 57.4928 | 143.124 | 12.0553 | 55.813 | 155.4087 | 25.2855 | 120.4525 | 12.3981 | 108.7527 | 14.6261 | 114.3418 | 11.2685 | 62.6529 | 129.3285 | 27.4885 | 55.9898 | 174.4595 | 12.6131 | 49.5807 | 152.3945 | 13.7132 | 105.1658 | 23.6379 | 119.0696 | 15.8862 | 124.351 | 1.3771 | 19.0057 | 1.6282 | 0.087032 | -38.2071 | 3.1235 | 265.79 | 49.43 | -1.2975 | 0.26473 | 0.38565 | -0.79238 | 0.53899 | -0.20199 | 0.43453 | -0.52908 | -0.85764 | 0.12447 | -0.9681 | -0.77548 | -1.1278 | -0.7214
42810.4463 | 542 | 18.3361 | 18.4694 | 18.4672 | 18.4649 | 17.7707 | 16.3758 | 14.4327 | 16.5867 | 17.0806 | 17.1846 | 17.1813 | 16.7004 | 15.7084 | 14.326 | 14.6699 | 14.7426 | 15.41 | 13.2241 | 13.9226 | 16.7679 |  |  |  | 16.5163 | 16.3237 | 22.0039 | 156.87 | 144.8066 | 182.7915 | 16.9664 | 16.3772 | 19.5997 | 16.6969 | 16.34 | 20.5475 | 54.6676 | 177.7398 |  | 89.6393 | 133.7741 | 131.2608 | 119.1752 |  | 6.9723 | 7.9003 | 6.9075 | 8.154 | 8.829 | 12.8399 | 83.6445 | 4.4066 | 7.4089 | 4.6403 | 8.632 | 8.7948 | 42.0692 | 46.6029 | 43.0053 | 14.5791 |  |  | -0.72064 | 0.11114 | 0.091876 | -0.3555 | 0.50023 | -0.040544 | 0.10767 | 0.4631 | -0.39191 | -0.41809 | -0.029118 | -0.00052898 | -0.00056183 | 0.88424 | 15.8904 | 16.6279 | 17.1618 | 17.4844 | 17.4286 | 16.3787 | 14.706 | 16.7659 | 17.0969 | 17.3994 | 17.4378 | 17.1444 | 16.3046 | 14.495 | 48.7743 | 21.7628 | 29.1349 | 21.3799 | 20.5901 | 33.3862 | 20.7031 | 15.8208 | 15.5126 | 15.513 | 14.2679 | 15.102 | 17.2629 |  |  |  | 46.7038 | 170.6384 | 131.7393 | 93.4543 | 1.0611 | 0.31865 | 49.1153 |  |  | 11.3312 |  |  | 16.8749 | 16.8359 | 25.7617 | 16.3141 | 15.9566 | 19.2901 | 156.79 | 198.1446 | 130.1982 | 133.694 | 95.194 |  | 51.3398 | 106.2047 | 52.0359 | 103.9766 | 74.7497 | 149.1812 |  | 82.8643 |  |  | 16.0554 | 19.1393 | 57.8418 | [6 empty] | 79.2239 |  |  | 41.8171 |  |  | 18.8134 | 65.6862 | 219.9379 | 10.1882 | 57.6046 | 143.4323 | 12.0913 | 56.3853 | 156.0031 | 25.3954 | 120.8521 | 12.4013 | 109.1604 | 14.6577 | 114.8202 | 11.2976 | 62.8933 | 130.1066 | 27.6412 | 56.3773 | 175.056 | 12.6473 | 50.0343 | 153.0425 | 13.7704 | 105.6851 | 23.7563 | 119.4135 | 15.9327 | 124.8821 | 1.4533 | 18.997 | 1.6358 | 0.086352 | -38.2212 | 3.1235 | 272.17 | 50.28 | -1.2632 | 0.38949 | 0.35413 | -0.69659 | 0.83354 | -0.2373 | 0.38671 | -0.58955 | -0.87066 | 0.018757 | -1.2092 | -0.51409 | -1.1371 | -0.70517
42810.4463 | 543 | 18.34 | 18.464 | 18.4567 | 18.4669 | 17.7649 | 16.3717 | 14.4246 | 16.5827 | 17.0791 | 17.181 | 17.1788 | 16.6983 | 15.7099 | 14.3262 | 14.6704 | 14.7446 | 15.4082 | 13.2236 | 13.9284 | 16.7792 |  |  |  | 16.517 | 16.3285 | 22.0294 | 157.416 | 145.0995 | 182.4786 | 16.9745 | 16.3922 | 19.627 | 16.7126 | 16.3444 | 20.5799 | 54.9877 | 177.0588 |  | 89.9767 | 134.265 | 131.8623 | 118.6799 |  | 6.9724 | 7.9059 | 6.9122 | 8.164 | 8.8304 | 12.8002 | 84.1961 | 4.3997 | 7.413 | 4.5213 | 8.6316 | 8.7844 | 42.0453 | 46.5847 | 42.9937 | 14.5681 |  |  | -0.62995 | 0.13019 | 0.07282 | 0.01577 | 0.31361 | -0.47884 | 0.39088 | 0.67929 | 0.036795 | -0.64048 | 0.0008858 | -0.00056019 | -0.00057662 | 0.94357 | 15.8959 | 16.635 | 17.1668 | 17.4906 | 17.434 | 16.38 | 14.7176 | 16.7682 | 17.1024 | 17.3972 | 17.4346 | 17.1509 | 16.3022 | 14.497 | 50.7014 | 22.1881 | 30.0669 | 21.2369 | 19.7116 | 33.5347 | 20.758 | 15.8088 | 15.5086 | 15.5111 | 14.2754 | 15.1116 | 17.2859 |  |  |  | 46.8945 | 170.5908 | 131.5928 | 93.3102 | 0.85482 | 0.27348 | 49.3898 |  |  | 11.3332 |  |  | 16.8743 | 16.8391 | 25.8099 | 16.3147 | 15.958 | 19.3143 | 157.3272 | 199.2057 | 130.5122 | 134.0597 | 96.5791 |  | 51.5249 | 106.4205 | 52.2072 | 103.9177 | 75.2028 | 148.7921 |  | 83.1274 |  |  | 16.0375 | 19.1941 | 58.0911 | [6 empty] | 79.2502 |  |  | 42.1148 |  |  | 18.9027 | 66.0335 | 220.593 | 10.222 | 58.8401 | 143.7524 | 12.1033 | 56.578 | 156.3255 | 25.5138 | 121.202 | 12.4045 | 109.7474 | 14.6872 | 115.5462 | 11.3256 | 63.3636 | 130.5784 | 27.8141 | 56.8461 | 175.7396 | 12.6581 | 50.3962 | 153.722 | 13.8865 | 106.1597 | 23.9035 | 119.9045 | 15.9909 | 125.5171 | 1.3842 | 18.9866 | 1.6447 | 0.085889 | -38.2625 | 3.1235 | 270.84 | 48.76 | -1.1807 | 0.42156 | 0.31527 | 0.14672 | 0.65994 | -0.81547 | 0.73678 | -0.62145 | -0.87056 | 0.037314 | -1.4058 | -0.61124 | -1.1119 | -0.69445
42810.4463 | 544 | 18.3354 | 18.4639 | 18.4602 | 18.4621 | 17.7721 | 16.369 | 14.4222 | 16.5765 | 17.0773 | 17.1726 | 17.1707 | 16.6959 | 15.7021 | 14.3276 | 14.668 | 14.7509 | 15.4109 | 13.2281 | 13.9344 | 16.7896 |  |  |  | 16.5161 | 16.3209 | 22.0638 | 157.845 | 145.5192 | 182.0731 | 16.9669 | 16.3764 | 19.6421 | 16.7007 | 16.3407 | 20.5982 | 55.3091 | 176.9868 |  | 90.3105 | 134.6894 | 132.4616 | 121.1409 |  | 6.9599 | 7.9133 | 6.9085 | 8.1691 | 8.8142 | 12.7575 | 85.1826 | 4.3719 | 7.4153 | 4.4306 | 8.6434 | 8.7896 | 42.0233 | 46.5832 | 42.9757 | 14.5629 |  |  | -0.73772 | 0.23994 | 0.04062 | -0.10119 | 0.42992 | 0.006768 | 0.28246 | 0.72069 | 0.43047 | -0.51125 | 0.12329 | -0.00057333 | -0.00057497 | 1.0145 | 15.8889 | 16.6272 | 17.1605 | 17.4872 | 17.4275 | 16.365 | 14.7097 | 16.7617 | 17.0954 | 17.3958 | 17.4306 | 17.1446 | 16.3015 | 14.4936 | 52.3038 | 22.5508 | 31.8661 | 21.9878 | 19.6369 | 33.6737 | 20.8295 | 15.8056 | 15.5092 | 15.5106 | 14.2741 | 15.1135 | 17.294 |  |  |  | 47.0777 | 170.4935 | 131.7017 | 93.1998 | 0.86556 | 0.30322 | 49.7407 |  |  | 11.3372 |  |  | 16.8759 | 16.8481 | 25.8594 | 16.3103 | 15.9579 | 19.336 | 157.8053 | 199.8826 | 130.8547 | 134.3902 | 98.1136 |  | 51.7414 | 107.2827 | 52.4203 | 108.732 | 75.7701 | 148.4373 |  | 83.3836 |  |  | 16.0281 | 19.2584 | 58.4207 | [6 empty] | 79.9592 |  |  | 42.3416 |  |  | 18.9671 | 66.664 | 222.2581 | 10.2225 | 60.3297 | 144.1966 | 12.0939 | 56.8566 | 156.6068 | 25.6329 | 121.5479 | 12.4743 | 110.4028 | 14.7118 | 116.2707 | 11.3509 | 64.3709 | 131.0149 | 27.9402 | 57.1887 | 176.4299 | 12.6747 | 50.7784 | 154.3289 | 13.9779 | 106.7126 | 24.0723 | 120.1559 | 16.0456 | 126.1958 | 1.1777 | 18.9763 | 1.6535 | 0.087401 | -38.2253 | 3.1235 | 293.19 | 49.24 | -1.2771 | 0.57229 | 0.23547 | -0.37166 | 0.77263 | 0.096942 | 0.62627 | -0.65638 | -0.88692 | -0.075206 | -1.5675 | -0.8028 | -1.1687 | -0.68493
42810.4463 | 545 | 18.3299 | 18.4607 | 18.4641 | 18.4643 | 17.7697 | 16.3707 | 14.4269 | 16.5772 | 17.0801 | 17.1725 | 17.1731 | 16.6915 | 15.7029 | 14.3201 | 14.6683 | 14.7471 | 15.4049 | 13.2163 | 13.9367 | 16.8082 |  |  |  | 16.5175 | 16.3212 | 22.1007 | 158.3899 | 146.2657 | 183.382 | 16.9691 | 16.3854 | 19.6653 | 16.7046 | 16.3438 | 20.6321 | 55.6448 | 176.8933 |  | 90.642 | 135.0528 | 133.1396 | 123.4428 |  | 6.9655 | 7.927 | 6.9117 | 8.1504 | 8.8001 | 12.6806 | 86.8156 | 4.3603 | 7.4207 | 4.3755 | 8.6579 | 8.7918 | 42.003 | 46.5846 | 42.9515 | 14.5548 |  |  | -0.37039 | 0.14662 | 0.1037 | -0.003942 | 0.23936 | 0.10534 | 0.429 | 0.70755 | -0.20023 | -0.66545 | 0.13839 | -0.00058319 | -0.00058812 | 1.0349 | 15.8868 | 16.6276 | 17.1661 | 17.4796 | 17.4311 | 16.3698 | 14.7089 | 16.7652 | 17.1026 | 17.4017 | 17.4308 | 17.142 | 16.3017 | 14.4897 | 54.1158 | 23.0401 | 33.465 | 22.851 | 20.7154 | 33.8027 | 20.9007 | 15.8126 | 15.5104 | 15.5151 | 14.2799 | 15.1262 | 17.3207 |  |  |  | 47.2724 | 170.7523 | 131.9719 | 93.2643 | 0.42227 | 0.1711 | 50.0586 |  |  | 11.3437 |  |  | 16.8824 | 16.8571 | 25.9157 | 16.3161 | 15.9613 | 19.362 | 158.3285 | 200.5188 | 131.3256 | 134.7578 | 99.1162 |  | 51.9521 | 107.5516 | 52.5945 | 105.819 | 76.2337 | 149.22 |  | 83.6384 |  |  | 16.0713 | 19.3532 | 58.87 | [6 empty] | 78.541 |  |  | 42.5806 |  |  | 19.0288 | 67.2842 | 223.8223 | 10.2351 | 60.5575 | 144.6162 | 12.0826 | 57.489 | 156.9582 | 25.7611 | 121.8889 | 12.5183 | 110.9777 | 14.7437 | 116.8166 | 11.3754 | 65.0157 | 131.5547 | 28.0518 | 57.2568 | 176.7877 | 12.7082 | 51.0434 | 154.9916 | 14.0705 | 107.3045 | 24.21 | 120.5816 | 16.0899 | 126.5284 | 1.3295 | 18.968 | 1.6605 | 0.085367 | -38.1736 | 3.1235 | 271.12 | 50.25 | -0.90622 | 0.44738 | 0.37625 | -0.073356 | 0.57643 | 0.38239 | 0.7717 | -0.67674 | -0.88819 | 0.023066 | -1.7537 | -0.97212 | -1.2206 | -0.67986
42810.4464 | 546 | 18.3279 | 18.4649 | 18.4652 | 18.4589 | 17.7654 | 16.369 | 14.4347 | 16.5732 | 17.0716 | 17.1754 | 17.1727 | 16.6971 | 15.7041 | 14.3257 | 14.6642 | 14.7507 | 15.4049 | 13.2182 | 13.9514 | 16.8309 |  |  |  | 16.5184 | 16.3319 | 22.1363 | 158.8049 | 146.8517 | 182.4886 | 16.9749 | 16.3829 | 19.6799 | 16.7035 | 16.3531 | 20.6568 | 55.9349 | 176.9506 |  | 90.9651 | 135.4635 | 133.6713 | 122.9683 |  | 6.9632 | 7.928 | 6.9016 | 8.141 | 8.7715 | 12.6033 | 88.4555 | 4.4118 | 7.4171 | 4.4069 | 8.6591 | 8.7855 | 41.9689 | 46.5671 | 42.9256 | 14.5421 |  |  | -0.54782 | 0.15385 | 0.13064 | 0.02497 | 0.57317 | 0.063936 | 0.28969 | 0.8692 | -0.47792 | 0.51363 | 0.0068468 | -0.00054048 | -0.00055198 | 1.167 | 15.8906 | 16.6278 | 17.1622 | 17.4771 | 17.427 | 16.3768 | 14.7105 | 16.7599 | 17.1026 | 17.3985 | 17.4298 | 17.1375 | 16.3034 | 14.4908 | 53.3478 | 21.7441 | 33.4751 | 22.7104 | 21.5706 | 33.907 | 20.9559 | 15.816 | 15.5079 | 15.5189 | 14.2803 | 15.1265 | 17.3409 |  |  |  | 47.4808 | 171.0901 | 132.1404 | 93.3377 | 0.83091 | -0.0075032 | 50.2819 |  |  | 11.3476 |  |  | 16.8795 | 16.8622 | 25.9619 | 16.3163 | 15.9625 | 19.3815 | 158.9854 | 201.5354 | 131.896 | 135.181 | 101.0013 |  | 52.1625 | 107.5391 | 52.7754 | 104.5794 | 76.725 | 149.3788 |  | 83.8965 |  |  | 16.1171 | 19.3973 | 58.5212 | [6 empty] | 77.7533 |  |  | 42.7424 |  |  | 19.0469 | 67.7163 | 224.1936 | 10.2536 | 60.7637 | 144.9067 | 12.0916 | 57.8278 | 157.4372 | 25.8951 | 122.4165 | 12.4871 | 111.585 | 14.7482 | 117.1179 | 11.4227 | 64.9935 | 132.0436 | 28.1966 | 57.6206 | 178.4889 | 12.746 | 51.3244 | 155.7997 | 14.1717 | 107.7595 | 24.3326 | 120.8621 | 16.1311 | 127.007 | 1.3162 | 18.9594 | 1.6693 | 0.086569 | -38.1947 | 3.1235 | 276.78 | 48.73 | -1.101 | 0.45829 | 0.4223 | 0.18462 | 0.89187 | 0.29788 | 0.63406 | -0.72161 | -0.8814 | 0.075906 | -1.6561 | -0.9668 | -1.1971 | -0.67456
42810.4464 | 547 | 18.3366 | 18.4691 | 18.465 | 18.4598 | 17.7723 | 16.3715 | 14.4313 | 16.5823 | 17.0775 | 17.1776 | 17.177 | 16.6991 | 15.7038 | 14.3319 | 14.6709 | 14.7584 | 15.413 | 13.2235 | 13.9628 | 16.8473 |  |  |  | 16.5205 | 16.3357 | 22.1676 | 159.3409 | 147.6624 | 186.3169 | 16.971 | 16.3851 | 19.713 | 16.7061 | 16.349 | 20.6775 | 56.2092 | 177.4178 |  | 91.2881 | 135.9204 | 134.1942 | 122.5632 |  | 6.9773 | 7.9412 | 6.907 | 8.1478 | 8.787 | 12.5273 | 88.8126 | 4.4539 | 7.4283 | 4.4654 | 8.6714 | 8.7963 | 41.9472 | 46.5625 | 42.9132 | 14.5412 |  |  | -0.54584 | 0.057259 | 0.14707 | -0.12814 | 0.60997 | 0.35372 | 0.30809 | 0.9198 | -0.21113 | -0.25697 | 0.19859 | -0.00056676 | -0.00057005 | 1.1137 | 15.8944 | 16.6262 | 17.1658 | 17.483 | 17.4273 | 16.3717 | 14.7109 | 16.7643 | 17.1048 | 17.4001 | 17.4382 | 17.1509 | 16.3147 | 14.4941 | 54.7827 | 22.3684 | 33.3119 | 23.5363 | 21.8635 | 34.0703 | 21.0045 | 15.8136 | 15.5111 | 15.5186 | 14.2812 | 15.134 | 17.3586 |  |  |  | 47.7089 | 171.0924 | 132.4278 | 93.4195 | 0.9624 | 0.23001 | 50.5678 |  |  | 11.3551 |  |  | 16.8831 | 16.8708 | 26.0072 | 16.3129 | 15.9725 | 19.3979 | 159.4337 | 202.483 | 132.403 | 135.7027 | 101.9436 |  | 52.4054 | 108.1167 | 52.9987 | 101.9536 | 77.2398 | 150.2078 |  | 84.2324 |  |  | 16.1617 | 19.4397 | 58.1986 | [6 empty] | 76.6001 |  |  | 42.8528 |  |  | 19.068 | 68.2881 | 223.8135 | 10.261 | 60.8069 | 145.1373 | 12.1152 | 58.2637 | 158.094 | 26.0278 | 123.1109 | 12.4855 | 112.096 | 14.762 | 117.6776 | 11.475 | 64.9726 | 132.3793 | 28.3054 | 58.0871 | 178.8718 | 12.7803 | 51.6137 | 156.6113 | 14.2715 | 108.211 | 24.4527 | 121.3105 | 16.1795 | 127.5121 | 1.2394 | 18.9515 | 1.6768 | 0.085129 | -38.2522 | 3.1235 | 266.83 | 49.17 | -1.1036 | 0.27958 | 0.44808 | -0.41824 | 0.91994 | 0.70055 | 0.6538 | -0.73914 | -0.88949 | 0.16816 | -1.7963 | -0.94299 | -1.176 | -0.66879
42810.4464 | 548 | 18.3282 | 18.4684 | 18.4583 | 18.4601 | 17.766 | 16.3662 | 14.4243 | 16.5801 | 17.0724 | 17.1716 | 17.1725 | 16.696 | 15.6976 | 14.3313 | 14.659 | 14.7475 | 15.4217 | 13.2203 | 13.9461 | 16.8614 |  |  |  | 16.5237 | 16.3365 | 22.201 | 159.7412 | 148.2805 | 184.1632 | 16.9668 | 16.3887 | 19.7385 | 16.7077 | 16.352 | 20.7087 | 56.4464 | 178.2752 |  | 91.6292 | 136.3569 | 134.7436 | 119.0334 |  | 6.9732 | 7.9399 | 6.9123 | 8.156 | 8.7872 | 12.4506 | 88.6014 | 4.5014 | 7.4379 | 4.4687 | 8.6838 | 8.7948 | 41.9164 | 46.5482 | 42.8976 | 14.5282 |  |  | -0.59841 | 0.26951 | 0.1957 | -0.19319 | 0.26892 | 0.12702 | 0.51574 | 0.91388 | -0.23623 | -0.0012216 | 0.16064 | -0.00057005 | -0.00059305 | 1.0489 | 15.8959 | 16.6263 | 17.161 | 17.489 | 17.4364 | 16.3663 | 14.7117 | 16.7544 | 17.1061 | 17.3963 | 17.4402 | 17.1441 | 16.3027 | 14.5001 | 56.6906 | 24.0017 | 34.9438 | 23.5808 | 22.0729 | 34.2352 | 21.0697 | 15.8117 | 15.5072 | 15.5145 | 14.274 | 15.1356 | 17.3694 |  |  |  | 47.9058 | 171.3758 | 132.8281 | 93.8799 | 0.69395 | 0.33352 | 51.1771 |  |  | 11.3581 |  |  | 16.881 | 16.8724 | 26.05 | 16.3151 | 15.9777 | 19.4203 | 159.8189 | 203.2744 | 132.7767 | 136.1648 | 102.2853 |  | 52.6368 | 109.7387 | 53.2116 | 101.7236 | 77.7285 | 151.3116 |  | 84.5322 |  |  | 16.2153 | 19.4929 | 58.4966 | [6 empty] | 78.1757 |  |  | 42.9352 |  |  | 19.1223 | 68.8697 | 224.1578 | 10.2234 | 61.2526 | 145.307 | 12.1117 | 58.8523 | 158.9787 | 26.1134 | 123.4519 | 12.495 | 112.5549 | 14.7505 | 118.122 | 11.517 | 65.3223 | 132.6663 | 28.4773 | 58.5179 | 179.1338 | 12.833 | 52.0283 | 156.7397 | 14.3813 | 108.6571 | 24.6189 | 121.9602 | 16.2258 | 128.1527 | 1.5791 | 18.9414 | 1.6834 | 0.083247 | -38.2483 | 3.1235 | 300.89 | 50.34 | -1.1529 | 0.60656 | 0.51687 | -0.51355 | 0.61075 | 0.41974 | 0.84579 | -0.74039 | -0.92695 | 0.1929 | -1.9889 | -1.1167 | -1.0694 | -0.67463
42810.4464 | 549 | 18.3227 | 18.4622 | 18.4646 | 18.4608 | 17.7668 | 16.3696 | 14.4269 | 16.5771 | 17.0796 | 17.17 | 17.175 | 16.6946 | 15.7022 | 14.3304 | 14.6693 | 14.7484 | 15.4172 | 13.2215 | 13.9417 | 16.8804 |  |  |  | 16.5239 | 16.335 | 22.232 | 159.8543 | 148.7591 | 182.6081 | 16.9648 | 16.3889 | 19.753 | 16.7065 | 16.3566 | 20.7378 | 56.6874 | 179.1446 |  | 91.9462 | 136.7794 | 135.4034 | 119.4854 |  | 6.9718 | 7.9503 | 6.9092 | 8.1633 | 8.7777 | 12.3748 | 89.1297 | 4.5113 | 7.4293 | 4.421 | 8.69 | 8.7933 | 41.8979 | 46.5522 | 42.8877 | 14.5235 |  |  | -0.71866 | 0.014543 | 0.092532 | -0.11631 | 0.058648 | 0.35372 | 0.44608 | 0.64052 | -0.85214 | 0.37117 | 0.12666 | -0.00055033 | -0.00056019 | 0.98855 | 15.8953 | 16.6174 | 17.1555 | 17.4779 | 17.4293 | 16.3694 | 14.7154 | 16.7566 | 17.0995 | 17.3961 | 17.4361 | 17.1436 | 16.2983 | 14.4852 | 57.5087 | 24.4294 | 35.9391 | 24.84 | 22.7584 | 34.4068 | 21.1419 | 15.8054 | 15.5149 | 15.5146 | 14.2657 | 15.1372 | 17.3896 |  |  |  | 48.0907 | 171.4826 | 133.3814 | 95.2245 | 1.2507 | 0.34104 | 51.6617 |  |  | 11.362 |  |  | 16.8884 | 16.8781 | 26.1036 | 16.3251 | 15.9832 | 19.4462 | 160.1995 | 204.1995 | 133.152 | 136.5768 | 102.9657 |  | 52.8435 | 110.9093 | 53.4128 | 101.5705 | 78.1893 | 151.7911 |  | 84.7806 |  |  | 16.2761 | 19.5343 | 59.2238 | [6 empty] | 79.8249 |  |  | 43.1251 |  |  | 19.1738 | 68.9052 | 223.8749 | 10.243 | 61.3096 | 145.4858 | 12.1393 | 59.2741 | 159.5441 | 26.227 | 123.7126 | 12.5703 | 113.0487 | 14.7676 | 118.332 | 11.5363 | 65.7919 | 132.7762 | 28.5999 | 58.7859 | 179.2023 | 12.8555 | 52.3811 | 156.8594 | 14.4335 | 109.2273 | 24.7582 | 122.2561 | 16.2604 | 128.7531 | 1.5435 | 18.9323 | 1.6917 | 0.085302 | -38.2745 | 3.1235 | 288.6 | 49.13 | -1.2612 | 0.1409 | 0.35542 | -0.39848 | 0.28518 | 0.70036 | 0.7865 | -0.75193 | -0.95229 | 0.21448 | -2.0595 | -1.2188 | -1.0733 | -0.70545
42810.4464 | 550 | 18.322 | 18.4632 | 18.4673 | 18.461 | 17.7647 | 16.3734 | 14.4277 | 16.5711 | 17.0774 | 17.1755 | 17.1722 | 16.6933 | 15.7016 | 14.3229 | 14.6601 | 14.7461 | 15.4049 | 13.2154 | 13.9128 | 16.8838 |  |  |  | 16.5094 | 16.3319 | 22.2642 | 159.9378 | 149.1981 | 181.934 | 16.9648 | 16.3867 | 19.7687 | 16.7018 | 16.3534 | 20.7526 | 56.9435 | 178.9853 |  | 92.2393 | 137.2711 | 135.9479 | 122.045 |  | 6.9872 | 7.9604 | 6.9226 | 8.1876 | 8.8002 | 12.3505 | 89.1877 | 4.498 | 7.4439 | 4.4207 | 8.7014 | 8.7996 | 41.8819 | 46.5603 | 42.8729 | 14.52 |  |  | -0.6891 | 0.27411 | 0.032076 | -0.17939 | 0.10202 | 0.10402 | 0.34883 | 0.79232 | -0.24635 | -0.36963 | 0.16124 | -0.00059797 | -0.00056183 | 0.97208 | 15.8999 | 16.6215 | 17.1626 | 17.4847 | 17.4255 | 16.3666 | 14.7129 | 16.7646 | 17.101 | 17.3956 | 17.4399 | 17.1446 | 16.304 | 14.4893 | 59.9078 | 26.3882 | 36.5791 | 24.8587 | 22.8886 | 34.6305 | 21.2311 | 15.8127 | 15.5065 | 15.5177 | 14.2673 | 15.1439 | 17.4077 |  |  |  | 48.3174 | 172.5792 | 134.554 | 96.8832 | 0.99036 | 0.54317 | 51.7293 |  |  | 11.3582 |  |  | 16.8935 | 16.8839 | 26.1519 | 16.3196 | 15.9811 | 19.4709 | 160.4844 | 205.2693 | 133.4488 | 136.8354 | 103.2122 |  | 53.0592 | 111.1333 | 53.6083 | 104.6193 | 78.8356 | 151.7658 |  | 85.0488 |  |  | 16.3167 | 19.5645 | 59.3572 | [6 empty] | 80.8926 |  |  | 43.1698 |  |  | 19.2543 | 69.4774 | 224.1469 | 10.2443 | 61.4911 | 145.7571 | 12.1592 | 59.8615 | 160.0834 | 26.3193 | 124.2168 | 12.6283 | 113.4281 | 14.8221 | 118.8705 | 11.5241 | 65.7054 | 132.9393 | 28.7132 | 59.0956 | 179.449 | 12.9053 | 52.6866 | 157.2155 | 14.4847 | 109.7802 | 24.9293 | 122.9546 | 16.2864 | 129.4213 | 1.2482 | 18.9246 | 1.6983 | 0.08544 | -38.2513 | 3.1234 | 296.07 | 49.86 | -1.2341 | 0.61174 | 0.20926 | -0.49489 | 0.3761 | 0.37978 | 0.69547 | -0.75109 | -0.95153 | 0.15412 | -2.2998 | -1.2795 | -1.1352 | -0.74353
42810.4464 | 551 | 18.3328 | 18.4626 | 18.4739 | 18.4624 | 17.7705 | 16.3706 | 14.4317 | 16.579 | 17.0829 | 17.1763 | 17.1826 | 16.6935 | 15.7166 | 14.3351 | 14.6744 | 14.7533 | 15.4068 | 13.2208 | 13.9008 | 16.9072 |  |  |  | 16.5172 | 16.3441 | 22.2962 | 160.2814 | 149.2905 | 184.0893 | 16.972 | 16.3931 | 19.7882 | 16.6921 | 16.3577 | 20.7751 | 57.2099 | 179.8932 |  | 92.5838 | 137.848 | 136.3927 | 124.9647 |  | 6.9952 | 7.9719 | 6.926 | 8.1933 | 8.8206 | 12.3345 | 88.7032 | 4.5334 | 7.4405 | 4.3473 | 8.7172 | 8.7963 | 41.8737 | 46.5642 | 42.8701 | 14.5014 |  |  | -0.51036 | 0.12428 | 0.16284 | 0.021686 | 0.28601 | -0.03726 | 0.30612 | 0.49333 | -0.24713 | 0.033186 | 0.10242 | -0.00054212 | -0.00057005 | 0.99424 | 15.901 | 16.6301 | 17.1635 | 17.4957 | 17.4307 | 16.3771 | 14.7154 | 16.7645 | 17.1059 | 17.4034 | 17.4462 | 17.1485 | 16.3062 | 14.493 | 60.2209 | 27.3263 | 37.5291 | 24.7726 | 22.2897 | 34.8107 | 21.3269 | 15.8129 | 15.5064 | 15.5242 | 14.2711 | 15.1506 | 17.4233 |  |  |  | 48.5472 | 173.5726 | 135.3374 | 97.8538 | 0.64391 | 0.3943 | 51.5684 |  |  | 11.3712 |  |  | 16.8962 | 16.8981 | 26.1951 | 16.3178 | 15.9837 | 19.4961 | 160.9962 | 206.2332 | 133.7712 | 137.1032 | 103.5686 |  | 53.2859 | 110.375 | 53.8307 | 105.2124 | 79.4576 | 151.3875 |  | 85.3619 |  |  | 16.3611 | 19.5883 | 59.7305 | [6 empty] | 83.0426 |  |  | 43.1256 |  |  | 19.2824 | 70.2462 | 224.8957 | 10.2609 | 62.429 | 146.1378 | 12.1875 | 60.22 | 160.7859 | 26.3799 | 124.4901 | 12.6779 | 113.7871 | 14.8422 | 119.5022 | 11.5494 | 65.9232 | 133.4792 | 28.8603 | 59.5195 | 179.8557 | 12.9561 | 53.0346 | 157.5931 | 14.5418 | 110.3033 | 25.0893 | 123.3709 | 16.3151 | 129.935 | 1.3212 | 18.915 | 1.7056 | 0.085158 | -38.1992 | 3.1235 | 279.04 | 50.14 | -1.0646 | 0.41193 | 0.47152 | 0.17207 | 0.62972 | -0.22729 | 0.65148 | -0.75291 | -0.92253 | 0.16109 | -2.3134 | -1.3739 | -1.2067 | -0.76237
42810.4464 | 552 | 18.3286 | 18.4517 | 18.4671 | 18.4616 | 17.7687 | 16.3688 | 14.4205 | 16.585 | 17.0745 | 17.1665 | 17.1675 | 16.6958 | 15.7075 | 14.3286 | 14.6712 | 14.7548 | 15.4209 | 13.2279 | 13.8981 | 16.9322 |  |  |  | 16.53 | 16.3581 | 22.3456 | 160.8761 | 149.6856 | 184.5786 | 16.9681 | 16.3741 | 19.8109 | 16.6859 | 16.3521 | 20.8038 | 57.5121 | 181.67 |  | 92.9551 | 138.4247 | 136.8533 | 124.7869 |  | 6.9877 | 7.9965 | 6.9399 | 8.2149 | 8.8914 | 12.4938 | 89.8528 | 4.5221 | 7.4488 | 4.2424 | 8.7249 | 8.8036 | 41.8597 | 46.5587 | 42.8733 | 14.4984 |  |  | -0.25014 | -0.042625 | 0.15102 | -0.076882 | 0.30047 | -0.060916 | 0.5164 | 0.68915 | -0.81302 | -0.17892 | 0.21568 | -0.0006029 | -0.00062262 | 1.0315 | 15.9001 | 16.626 | 17.1606 | 17.4907 | 17.4289 | 16.3792 | 14.7067 | 16.767 | 17.1009 | 17.3992 | 17.444 | 17.1453 | 16.3005 | 14.4944 | 58.048 | 26.2386 | 37.5626 | 24.7928 | 22.6542 | 34.9267 | 21.406 | 15.8018 | 15.509 | 15.5246 | 14.2738 | 15.1574 | 17.4399 |  |  |  | 48.802 | 175.031 | 136.8854 | 97.8573 | 0.37688 | -0.0086324 | 51.5264 |  |  | 11.3836 |  |  | 16.8891 | 16.8966 | 26.2391 | 16.316 | 15.984 | 19.5101 | 161.6938 | 207.0431 | 134.1263 | 137.428 | 103.6408 |  | 53.4797 | 109.7718 | 54.0366 | 102.4087 | 80.0309 | 151.379 |  | 85.668 |  |  | 16.4104 | 19.641 | 60.3087 | [6 empty] | 84.4268 |  |  | 43.1327 |  |  | 19.3078 | 70.6313 | 225.3474 | 10.293 | 62.7006 | 146.7716 | 12.2263 | 60.7108 | 161.2761 | 26.458 | 124.7145 | 12.7302 | 114.0825 | 14.8582 | 120.0665 | 11.5725 | 66.2538 | 134.1806 | 28.9678 | 59.999 | 180.9366 | 13.0013 | 53.332 | 157.9682 | 14.6114 | 110.7056 | 25.2565 | 123.7338 | 16.356 | 130.2194 | 1.3524 | 18.9075 | 1.713 | 0.086142 | -38.2027 | 3.1235 | 285.05 | 48.36 | -0.7457 | -0.24125 | 0.45409 | -0.324 | 0.64562 | -0.2907 | 0.84639 | -0.748 | -0.89842 | 0.2606 | -2.0583 | -1.3683 | -1.1909 | -0.75347
42810.4464 | 553 | 18.3248 | 18.4617 | 18.4712 | 18.4653 | 17.771 | 16.3776 | 14.4262 | 16.576 | 17.0801 | 17.1757 | 17.1701 | 16.6899 | 15.7131 | 14.3323 | 14.6656 | 14.7514 | 15.4173 | 13.2249 | 13.895 | 16.944 |  |  |  | 16.5217 | 16.3582 | 22.3721 | 161.4441 | 150.2373 | 185.6212 | 16.9693 | 16.3922 | 19.8404 | 16.7012 | 16.3667 | 20.8444 | 57.8206 | 180.6254 |  | 93.253 | 138.9843 | 137.3339 | 125.4786 |  | 6.9892 | 8.021 | 6.9587 | 8.2421 | 9.0047 | 12.6361 | 90.803 | 4.5673 | 7.4446 | 4.1963 | 8.7402 | 8.8022 | 41.85 | 46.551 | 42.8722 | 14.4972 |  |  | -0.47159 | -0.18193 | 0.000536 | -0.20436 | 0.032364 | -0.4381 | 0.22266 | 0.36454 | -0.062451 | -0.11325 | 0.16839 | -0.00056183 | -0.00057169 | 1.0345 | 15.9047 | 16.6273 | 17.1592 | 17.4902 | 17.428 | 16.3786 | 14.7082 | 16.7678 | 17.1038 | 17.3947 | 17.4456 | 17.1451 | 16.3006 | 14.4956 | 55.2411 | 23.9827 | 35.0792 | 23.8554 | 22.6116 | 34.9862 | 21.4378 | 15.8117 | 15.5106 | 15.5217 | 14.2692 | 15.16 | 17.459 |  |  |  | 49.0025 | 175.7723 | 137.1745 | 97.7596 | 0.18604 | 0.030325 | 51.6851 |  |  | 11.39 |  |  | 16.8853 | 16.8979 | 26.2872 | 16.3195 | 15.9837 | 19.5275 | 162.1834 | 207.666 | 134.5454 | 137.8745 | 103.7667 |  | 53.6766 | 110.3406 | 54.204 | 104.4396 | 80.5661 | 152.962 |  | 85.9637 |  |  | 16.4682 | 19.6727 | 59.8959 | [6 empty] | 86.022 |  |  | 43.2197 |  |  | 19.3498 | 70.8617 | 226.231 | 10.3007 | 62.9821 | 147.2322 | 12.2663 | 61.05 | 161.3943 | 26.5527 | 124.9777 | 12.8141 | 114.4523 | 14.8959 | 120.6792 | 11.6007 | 66.7698 | 134.7099 | 29.0677 | 60.4662 | 181.5117 | 13.0482 | 53.5942 | 158.22 | 14.686 | 111.0307 | 25.4196 | 123.916 | 16.3713 | 130.5951 | 1.1808 | 18.9026 | 1.7183 | 0.08481 | -38.2578 | 3.1235 | 312.62 | 50.05 | -1.0251 | -0.49843 | 0.027054 | -0.52827 | 0.21194 | -0.77978 | 0.55592 | -0.74447 | -0.90824 | 0.22442 | -1.7394 | -1.0887 | -1.199 | -0.74366
42810.4464 | 554 | 18.3191 | 18.4591 | 18.4615 | 18.4647 | 17.7646 | 16.3702 | 14.4262 | 16.569 | 17.0756 | 17.1718 | 17.1667 | 16.6922 | 15.7036 | 14.3313 | 14.664 | 14.7463 | 15.4179 | 13.2199 | 13.888 | 16.9554 |  |  |  | 16.5177 | 16.3544 | 22.3999 | 162.0202 | 150.5919 | 186.6592 | 16.9617 | 16.3962 | 19.8667 | 16.6942 | 16.3614 | 20.8607 | 58.1312 | 180.343 |  | 93.5391 | 139.5646 | 137.6544 | 126.1639 |  | 6.991 | 8.0281 | 6.9705 | 8.2622 | 9.0275 | 12.6438 | 90.7778 | 4.649 | 7.4588 | 4.1636 | 8.7544 | 8.8055 | 41.8323 | 46.5386 | 42.8729 | 14.4867 |  |  | -0.75941 | 0.053971 | 0.011708 | -0.45735 | 0.058648 | -0.674 | 0.32846 | 0.28305 | -0.47656 | 0.44922 | 0.20912 | -0.00055033 | -0.00055033 | 1.0286 | 15.8995 | 16.6312 | 17.1558 | 17.4818 | 17.4257 | 16.3676 | 14.7019 | 16.7659 | 17.1053 | 17.4032 | 17.441 | 17.1412 | 16.3003 | 14.494 | 50.7402 | 23.1608 | 33.4268 | 22.8464 | 20.8603 | 34.9913 | 21.4754 | 15.8067 | 15.5111 | 15.5243 | 14.2742 | 15.1638 | 17.4781 |  |  |  | 49.2105 | 176.0663 | 137.6625 | 98.1216 | 0.11918 | -0.27042 | 51.8347 |  |  | 11.3946 |  |  | 16.8896 | 16.9066 | 26.3305 | 16.3185 | 15.9905 | 19.5506 | 162.5969 | 208.1165 | 135.0497 | 138.4754 | 104.4268 |  | 53.902 | 109.7223 | 54.4228 | 104.3625 | 81.142 | 152.7299 |  | 86.2825 |  |  | 16.5011 | 19.6787 | 59.4103 | [6 empty] | 87.5785 |  |  | 43.3724 |  |  | 19.3991 | 71.4947 | 226.9054 | 10.3234 | 63.5683 | 147.5736 | 12.2929 | 61.515 | 161.7075 | 26.6502 | 125.3239 | 12.9009 | 114.8183 | 14.9167 | 121.356 | 11.6137 | 66.9417 | 135.0758 | 29.1599 | 61.0042 | 181.5166 | 13.0927 | 53.9001 | 158.4547 | 14.7317 | 111.4491 | 25.5855 | 124.5287 | 16.3843 | 130.9856 | 1.3093 | 18.8968 | 1.7256 | 0.085628 | -38.3144 | 3.1235 | 324.32 | 49.09 | -1.3022 | 0.27148 | 0.12644 | -0.79029 | 0.28531 | -0.96722 | 0.6752 | -0.75476 | -0.88325 | 0.24835 | -1.2387 | -0.90069 | -1.2069 | -0.74636
42810.4465 | 555 | 18.3266 | 18.466 | 18.4639 | 18.4635 | 17.7747 | 16.3757 | 14.4272 | 16.5759 | 17.0797 | 17.1695 | 17.1738 | 16.688 | 15.7013 | 14.335 | 14.6692 | 14.7554 | 15.4234 | 13.2236 | 13.8878 | 16.9779 |  |  |  | 16.5261 | 16.3615 | 22.4347 | 162.4916 | 150.8367 | 186.6886 | 16.9673 | 16.3948 | 19.8874 | 16.7025 | 16.369 | 20.8878 | 58.417 | 180.5075 |  | 93.8938 | 140.1468 | 137.9365 | 123.8631 |  | 7.0016 | 8.0354 | 6.9841 | 8.2882 | 8.9958 | 12.6064 | 90.9711 | 4.745 | 7.4692 | 4.2657 | 8.7643 | 8.8058 | 41.817 | 46.5446 | 42.8764 | 14.4885 |  |  | -0.73181 | 0.041487 | 0.00448 | -0.18465 | 0.1099 | 0.050796 | -0.007984 | 0.24888 | -0.15547 | 0.40705 | 0.23456 | -0.00052733 | -0.00057005 | 1.0649 | 15.9104 | 16.6301 | 17.1712 | 17.489 | 17.4305 | 16.3673 | 14.7066 | 16.7662 | 17.1063 | 17.4027 | 17.4359 | 17.1457 | 16.3005 | 14.501 | 45.9479 | 21.2651 | 30.3386 | 21.7864 | 20.0336 | 34.9877 | 21.4974 | 15.8124 | 15.5077 | 15.5319 | 14.2774 | 15.1831 | 17.5014 |  |  |  | 49.4265 | 176.6243 | 138.3137 | 98.6715 | 0.24742 | -0.27719 | 51.851 |  |  | 11.4005 |  |  | 16.8891 | 16.9133 | 26.3832 | 16.3231 | 15.9968 | 19.5741 | 162.9779 | 208.3828 | 135.4717 | 138.8914 | 104.249 |  | 54.0714 | 109.6198 | 54.6102 | 106.1179 | 81.7575 | 151.9076 |  | 86.5445 |  |  | 16.5327 | 19.7138 | 59.513 | [6 empty] | 89.4968 |  |  | 43.5572 |  |  | 19.463 | 72.1946 | 227.1627 | 10.3423 | 64.0324 | 147.8325 | 12.3264 | 61.9985 | 162.1531 | 26.7544 | 125.6534 | 12.9455 | 115.2365 | 14.944 | 121.8446 | 11.6406 | 67.1889 | 135.3153 | 29.2897 | 61.5338 | 181.8671 | 13.1459 | 54.2273 | 158.5565 | 14.778 | 111.9479 | 25.7739 | 125.0031 | 16.398 | 131.5798 | 1.2419 | 18.8919 | 1.7321 | 0.086236 | -38.2405 | 3.1235 | 318.51 | 48.9 | -1.2784 | 0.23802 | 0.078217 | -0.50216 | 0.39055 | 0.26551 | -0.10526 | -0.74377 | -0.8737 | 0.22291 | -0.70663 | -0.55499 | -1.1327 | -0.754
42810.4465 | 556 | 18.3309 | 18.4607 | 18.4728 | 18.4644 | 17.7798 | 16.3778 | 14.4231 | 16.585 | 17.0781 | 17.1721 | 17.1718 | 16.694 | 15.7069 | 14.3399 | 14.6734 | 14.7567 | 15.4275 | 13.2231 | 13.8853 | 16.995 |  |  |  | 16.5193 | 16.3636 | 22.4728 | 163.003 | 151.115 | 188.0442 | 16.9638 | 16.3978 | 19.9064 | 16.701 | 16.3642 | 20.9169 | 58.6455 | 180.6653 |  | 94.2279 | 140.6929 | 138.1679 | 121.4787 |  | 6.9951 | 8.0429 | 6.9938 | 8.2989 | 8.9768 | 12.5734 | 90.9334 | 4.7724 | 7.4767 | 4.3958 | 8.7707 | 8.814 | 41.8076 | 46.5425 | 42.8684 | 14.4848 |  |  | -0.57016 | -0.015025 | 0.10108 | 0.14785 | -0.037948 | -0.26528 | 0.22004 | 0.41579 | -0.2374 | -0.20934 | 0.15071 | -0.00053391 | -0.00055526 | 1.0656 | 15.9164 | 16.629 | 17.1606 | 17.482 | 17.4296 | 16.3749 | 14.7117 | 16.7617 | 17.1153 | 17.4058 | 17.4394 | 17.145 | 16.3086 | 14.5047 | 43.1777 | 19.7027 | 27.916 | 20.53 | 19.2507 | 34.9775 | 21.4846 | 15.8121 | 15.5193 | 15.5282 | 14.2844 | 15.186 | 17.5249 |  |  |  | 49.6776 | 177.2756 | 139.7819 | 99.2124 | 0.2067 | -0.23316 | 51.9676 |  |  | 11.3924 |  |  | 16.8813 | 16.9175 | 26.4373 | 16.3248 | 15.9943 | 19.5978 | 163.3836 | 208.7463 | 135.7508 | 139.1003 | 104.5525 |  | 54.2341 | 109.8546 | 54.7497 | 104.8625 | 82.3151 | 151.1458 |  | 86.841 |  |  | 16.5322 | 19.7662 | 59.977 | [6 empty] | 89.9606 |  |  | 43.7206 |  |  | 19.5391 | 72.8008 | 228.2143 | 10.3594 | 64.4188 | 148.0288 | 12.3528 | 62.1908 | 162.5114 | 26.8361 | 125.937 | 12.9759 | 115.6616 | 14.9707 | 122.2253 | 11.6416 | 67.5621 | 135.6855 | 29.4417 | 61.9517 | 182.255 | 13.19 | 54.4925 | 158.7201 | 14.8227 | 112.3922 | 25.901 | 125.2325 | 16.4188 | 132.1092 | 1.3917 | 18.8874 | 1.7364 | 0.084738 | -38.2673 | 3.1235 | 321.07 | 50.25 | -1.1301 | -0.14324 | 0.37153 | 0.44934 | -0.22947 | -0.60672 | 0.55257 | -0.74639 | -0.87523 | 0.27894 | -0.40003 | -0.28731 | -1.0582 | -0.76013
42810.4465 | 557 | 18.3297 | 18.4569 | 18.4701 | 18.4704 | 17.7788 | 16.3816 | 14.4281 | 16.5823 | 17.0837 | 17.1778 | 17.1761 | 16.6978 | 15.7111 | 14.3393 | 14.6744 | 14.7585 | 15.4234 | 13.2268 | 13.8982 | 17.0164 |  |  |  | 16.5297 | 16.3755 | 22.5148 | 163.5865 | 151.4453 | 188.9543 | 16.9707 | 16.4067 | 19.94 | 16.7018 | 16.3654 | 20.9459 | 58.8934 | 179.2383 |  | 94.5091 | 141.2411 | 138.3625 | 121.5877 |  | 6.9982 | 8.0551 | 7.006 | 8.3156 | 8.9639 | 12.532 | 92.099 | 4.7982 | 7.4777 | 4.529 | 8.7846 | 8.8262 | 41.7882 | 46.5504 | 42.8678 | 14.4713 |  |  | -0.61024 | -0.11754 | 0.1267 | -0.003286 | 0.18218 | -0.27185 | 0.28706 | 0.46639 | -0.091252 | -0.14011 | 0.089307 | -0.00056348 | -0.00054376 | 1.0589 | 15.91 | 16.6231 | 17.1607 | 17.4799 | 17.4238 | 16.3775 | 14.7061 | 16.7648 | 17.1108 | 17.41 | 17.4457 | 17.1554 | 16.3033 | 14.501 | 41.3259 | 18.9433 | 25.501 | 19.8346 | 18.1744 | 34.9805 | 21.4578 | 15.8133 | 15.5105 | 15.5342 | 14.2875 | 15.1888 | 17.5392 |  |  |  | 49.9042 | 178.1422 | 140.9187 | 99.2909 | 0.83091 | -0.087488 | 52.1573 |  |  | 11.3779 |  |  | 16.8827 | 16.9208 | 26.4832 | 16.3225 | 15.9941 | 19.6158 | 163.6999 | 209.3384 | 135.9467 | 139.3377 | 105.1849 |  | 54.454 | 110.2174 | 54.9336 | 106.232 | 82.9276 | 151.7536 |  | 87.2219 |  |  | 16.5025 | 19.8179 | 60.5585 | [6 empty] | 90.9665 |  |  | 43.8485 |  |  | 19.6063 | 73.2144 | 229.3359 | 10.3626 | 64.9134 | 148.3568 | 12.3586 | 62.6601 | 162.8115 | 26.8884 | 126.1646 | 13.0061 | 116.0413 | 15.0022 | 122.8612 | 11.6422 | 67.6705 | 136.1645 | 29.5622 | 62.4975 | 182.7428 | 13.2162 | 54.6967 | 159.084 | 14.8571 | 112.7823 | 25.9617 | 125.5114 | 16.4282 | 132.4696 | 1.5144 | 18.8802 | 1.7437 | 0.087191 | -38.3136 | 3.1235 | 283.53 | 48.89 | -1.1703 | -0.40065 | 0.41598 | -0.06699 | 0.50276 | -0.61415 | 0.6311 | -0.75609 | -0.87873 | 0.26417 | -0.19393 | -0.022119 | -1.0523 | -0.75429
42810.4465 | 558 | 18.3221 | 18.4485 | 18.4511 | 18.4596 | 17.7658 | 16.3727 | 14.4219 | 16.57 | 17.0739 | 17.1652 | 17.1721 | 16.69 | 15.7004 | 14.3292 | 14.6738 | 14.7586 | 15.4236 | 13.2166 | 13.9111 | 17.0253 |  |  |  | 16.526 | 16.3713 | 22.5444 | 164.2969 | 151.9493 | 190.9606 | 16.9822 | 16.4102 | 19.9675 | 16.7075 | 16.3775 | 20.9737 | 59.1442 | 179.8494 |  | 94.799 | 141.7781 | 138.504 | 123.3174 |  | 6.9964 | 8.0691 | 7.0176 | 8.3275 | 8.9662 | 12.5082 | 92.1552 | 4.7971 | 7.4739 | 4.5822 | 8.7982 | 8.8246 | 41.773 | 46.5541 | 42.8625 | 14.47 |  |  | -0.61156 | -0.068909 | -0.048092 | -0.09331 | 0.22358 | 0.17959 | -0.04084 | 1.0052 | -0.38938 | 0.12655 | 0.046786 | -0.00056676 | -0.00059962 | 1.0864 | 15.9105 | 16.6323 | 17.1691 | 17.4875 | 17.4272 | 16.3799 | 14.7125 | 16.7688 | 17.1148 | 17.4116 | 17.447 | 17.1535 | 16.305 | 14.5073 | 43.323 | 20.6298 | 24.699 | 18.4711 | 17.3522 | 35.0742 | 21.4605 | 15.8113 | 15.5089 | 15.54 | 14.2814 | 15.1972 | 17.5553 |  |  |  | 50.0933 | 178.7422 | 141.3288 | 99.2412 | 1.0098 | 0.54637 | 52.5157 |  |  | 11.3708 |  |  | 16.8829 | 16.9256 | 26.5269 | 16.3259 | 16.0002 | 19.6341 | 164.0124 | 210.3495 | 136.1371 | 139.49 | 105.6588 |  | 54.644 | 110.7613 | 55.1288 | 104.3346 | 83.4183 | 151.8102 |  | 87.5161 |  |  | 16.5078 | 19.837 | 61.002 | [6 empty] | 91.3774 |  |  | 44.0125 |  |  | 19.6647 | 73.8412 | 229.9107 | 10.4013 | 65.3448 | 148.6459 | 12.3867 | 63.0686 | 163.0884 | 26.9241 | 126.4311 | 13.0395 | 116.2525 | 15.0359 | 123.2354 | 11.6706 | 68.0317 | 136.4126 | 29.639 | 63.1975 | 183.2577 | 13.2364 | 54.8811 | 159.56 | 14.879 | 113.0775 | 26.0473 | 125.9851 | 16.4568 | 132.8524 | 1.5271 | 18.874 | 1.7499 | 0.087879 | -38.2883 | 3.1235 | 279.52 | 48.72 | -1.1741 | -0.30678 | -0.25629 | -0.35699 | 0.55694 | 0.49915 | -0.23803 | -0.76246 | -0.88685 | 0.33553 | -0.4048 | 0.067311 | -1.0913 | -0.7462
42810.4465 | 559 | 18.3287 | 18.4598 | 18.4661 | 18.4632 | 17.772 | 16.3704 | 14.4242 | 16.5666 | 17.0756 | 17.1758 | 17.1713 | 16.6915 | 15.7093 | 14.3425 | 14.6662 | 14.7521 | 15.426 | 13.2088 | 13.9114 | 17.0363 |  |  |  | 16.5091 | 16.3719 | 22.5663 | 164.8105 | 152.2908 | 189.9616 | 16.9715 | 16.4042 | 19.9825 | 16.702 | 16.3872 | 21.0022 | 59.4178 | 179.8691 |  | 95.1088 | 142.2759 | 138.6759 | 121.2496 |  | 7.0079 | 8.0813 | 7.0264 | 8.3409 | 8.9746 | 12.496 | 91.3576 | 4.808 | 7.4808 | 4.6021 | 8.8145 | 8.8212 | 41.7577 | 46.547 | 42.8464 | 14.4685 |  |  | -0.73509 | -0.10834 | -0.028376 | 0.095282 | 0.23541 | -0.44861 | 0.049184 | 0.4585 | 0.23568 | 0.087943 | 0.12845 | -0.0005684 | -0.00058812 | 1.051 | 15.9147 | 16.6287 | 17.167 | 17.492 | 17.4319 | 16.3794 | 14.7148 | 16.7654 | 17.1123 | 17.406 | 17.4452 | 17.1495 | 16.306 | 14.5021 | 46.4408 | 22.7107 | 27.4483 | 18.6349 | 16.336 | 35.1833 | 21.51 | 15.8088 | 15.5162 | 15.5448 | 14.2763 | 15.1985 | 17.5698 |  |  |  | 50.3088 | 179.1035 | 142.0019 | 99.8613 | 0.57057 | 0.29512 | 52.8224 |  |  | 11.3737 |  |  | 16.8882 | 16.9377 | 26.5794 | 16.3261 | 16.0097 | 19.665 | 164.4956 | 211.1721 | 136.3205 | 139.5776 | 106.0913 |  | 54.855 | 111.9189 | 55.2938 | 104.1429 | 83.7978 | 150.967 |  | 87.7181 |  |  | 16.5227 | 19.8843 | 61.3354 | [6 empty] | 90.3699 |  |  | 44.2056 |  |  | 19.7325 | 74.5945 | 230.6169 | 10.4631 | 65.7357 | 149.0361 | 12.4459 | 63.1832 | 163.4092 | 26.9864 | 126.8305 | 13.078 | 116.6852 | 15.072 | 123.6584 | 11.697 | 68.6183 | 136.6686 | 29.6966 | 63.8237 | 183.6129 | 13.2333 | 55.1455 | 160.0811 | 14.8807 | 113.5187 | 26.133 | 126.4217 | 16.4958 | 133.1586 | 1.534 | 18.8668 | 1.7548 | 0.085281 | -38.2961 | 3.1235 | 288.51 | 50.51 | -1.2858 | -0.38467 | -0.19687 | 0.36075 | 0.57147 | -0.78889 | 0.26121 | -0.76693 | -0.91309 | 0.35531 | -0.73837 | -0.23238 | -1.024 | -0.75579
42810.4465 | 560 | 18.3267 | 18.4558 | 18.4617 | 18.463 | 17.7787 | 16.3725 | 14.4266 | 16.5724 | 17.0786 | 17.1699 | 17.1775 | 16.6961 | 15.712 | 14.3429 | 14.669 | 14.7508 | 15.4304 | 13.2204 | 13.9185 | 17.0634 |  |  |  | 16.5219 | 16.3733 | 22.603 | 165.0632 | 152.4404 | 190.7917 | 16.9814 | 16.4174 | 20.0129 | 16.7046 | 16.3893 | 21.037 | 59.7513 | 180.8945 |  | 95.4837 | 142.695 | 138.9049 | 124.0165 |  | 7.0031 | 8.0873 | 7.0454 | 8.3236 | 8.9446 | 12.4561 | 91.486 | 4.8267 | 7.4771 | 4.5587 | 8.818 | 8.8337 | 41.775 | 46.555 | 42.8545 | 14.4703 |  |  | -0.57344 | -0.044597 | 0.018936 | 0.11303 | -0.074748 | -0.17985 | 0.0275 | 0.81466 | 0.0048804 | -0.1485 | 0.12984 | -0.00056183 | -0.00056512 | 1.0211 | 15.9101 | 16.6199 | 17.1554 | 17.4793 | 17.4232 | 16.3693 | 14.7058 | 16.7645 | 17.1039 | 17.3945 | 17.4378 | 17.1396 | 16.2959 | 14.4896 | 46.9489 | 22.3854 | 29.2308 | 19.9669 | 17.7624 | 35.2402 | 21.5633 | 15.8243 | 15.51 | 15.5515 | 14.2779 | 15.2081 | 17.5915 |  |  |  | 50.5302 | 179.523 | 142.2998 | 101.3163 | 0.57584 | -0.0024218 | 52.9254 |  |  | 11.3769 |  |  | 16.8951 | 16.9419 | 26.6379 | 16.326 | 16.0121 | 19.6917 | 165.083 | 211.6961 | 136.5167 | 139.8583 | 106.3031 |  | 55.0754 | 112.763 | 55.4728 | 105.7296 | 84.2323 | 150.7555 |  | 87.9828 |  |  | 16.496 | 19.9072 | 62.1335 | [6 empty] | 90.4543 |  |  | 44.3566 |  |  | 19.7666 | 74.8325 | 231.7493 | 10.5036 | 66.4276 | 149.4748 | 12.4821 | 63.8301 | 164.3045 | 27.0352 | 127.1924 | 13.095 | 117.4108 | 15.0997 | 124.1709 | 11.7074 | 69.5198 | 136.9986 | 29.7431 | 64.2056 | 183.9287 | 13.248 | 55.3827 | 160.3575 | 14.8865 | 113.9308 | 26.1972 | 126.5145 | 16.5574 | 133.4017 | 1.348 | 18.8605 | 1.762 | 0.086649 | -38.323 | 3.1234 | 283.02 | 48.97 | -1.1367 | -0.24681 | 0.16082 | 0.39291 | -0.322 | -0.49947 | 0.19531 | -0.76492 | -0.93013 | 0.3278 | -0.78812 | -0.4242 | -1.0888 | -0.78836
42810.4465 | 561 | 18.3362 | 18.4645 | 18.4671 | 18.4701 | 17.7799 | 16.3765 | 14.4289 | 16.5766 | 17.0779 | 17.1723 | 17.1758 | 16.6896 | 15.7038 | 14.3382 | 14.67 | 14.7564 | 15.4364 | 13.2205 | 13.907 | 17.0826 |  |  |  | 16.523 | 16.3876 | 22.6365 | 165.4728 | 152.8235 | 191.2147 | 16.9819 | 16.4099 | 20.0266 | 16.6966 | 16.3902 | 21.0537 | 60.0919 | 181.5363 |  | 95.804 | 143.0536 | 139.1467 | 125.5086 |  | 7.0233 | 8.1094 | 7.0682 | 8.3444 | 8.9324 | 12.4475 | 91.9201 | 4.8954 | 7.4932 | 4.498 | 8.8348 | 8.8381 | 41.7635 | 46.5377 | 42.8396 | 14.4666 |  |  | -0.60433 | 0.075655 | 0.021564 | 0.18005 | 0.11844 | -0.61224 | -0.090124 | 0.6195 | -0.27281 | -0.22529 | -0.026535 | -0.0005799 | -0.00056512 | 1.0096 | 15.9205 | 16.6237 | 17.1627 | 17.4844 | 17.4351 | 16.3735 | 14.7079 | 16.7626 | 17.1114 | 17.4027 | 17.4384 | 17.1433 | 16.3082 | 14.4994 | 45.5203 | 21.4614 | 27.2396 | 19.1765 | 17.9408 | 35.2592 | 21.5679 | 15.8227 | 15.5131 | 15.5414 | 14.2768 | 15.2115 | 17.6171 |  |  |  | 50.7687 | 179.6833 | 142.4894 | 102.4513 | 0.46096 | -0.087488 | 53.0483 |  |  | 11.382 |  |  | 16.894 | 16.9433 | 26.6858 | 16.3287 | 16.0117 | 19.711 | 165.745 | 212.4257 | 136.7063 | 140.2013 | 106.5333 |  | 55.2804 | 112.1395 | 55.6731 | 106.2603 | 84.7656 | 152.4665 |  | 88.3004 |  |  | 16.5031 | 19.9256 | 62.9769 | [6 empty] | 90.4117 |  |  | 44.4995 |  |  | 19.8326 | 74.8361 | 232.5896 | 10.5182 | 67.2393 | 149.7399 | 12.4811 | 64.3633 | 165.1662 | 27.1078 | 127.5829 | 13.1073 | 118.1221 | 15.1376 | 124.4901 | 11.7202 | 70.0156 | 137.3677 | 29.8438 | 64.6815 | 184.0746 | 13.2647 | 55.6091 | 160.6413 | 14.9301 | 114.2661 | 26.2794 | 126.8605 | 16.6179 | 133.6808 | 1.4553 | 18.8549 | 1.7682 | 0.087227 | -38.3529 | 3.1235 | 279.49 | 49.28 | -1.1674 | 0.32147 | 0.17163 | 0.49593 | 0.40532 | -0.92152 | -0.35356 | -0.76397 | -0.90563 | 0.3334 | -0.62715 | -0.20242 | -1.1179 | -0.81142
42810.4465 | 562 | 18.3354 | 18.4634 | 18.464 | 18.4711 | 17.7807 | 16.3787 | 14.4228 | 16.578 | 17.075 | 17.1701 | 17.175 | 16.6931 | 15.7085 | 14.3432 | 14.6758 | 14.762 | 15.4348 | 13.2197 | 13.8896 | 17.1015 |  |  |  | 16.5181 | 16.3933 | 22.6734 | 165.8654 | 153.1758 | 191.0963 | 16.9865 | 16.4251 | 20.052 | 16.7046 | 16.3978 | 21.0939 | 60.3987 | 180.7346 |  | 96.068 | 143.4849 | 139.4839 | 124.2766 |  | 7.0362 | 8.1344 | 7.075 | 8.3489 | 8.9197 | 12.448 | 93.556 | 4.9908 | 7.5036 | 4.4471 | 8.8503 | 8.837 | 41.7732 | 46.5165 | 42.839 | 14.4491 |  |  | -0.69764 | -0.032769 | 0.053764 | -0.055198 | 0.22753 | -0.73577 | 0.005816 | 0.5873 | -0.23623 | -0.30669 | -0.037662 | -0.00055526 | -0.00061933 | 0.97904 | 15.9266 | 16.6286 | 17.1654 | 17.4895 | 17.4261 | 16.372 | 14.7171 | 16.7652 | 17.1052 | 17.3983 | 17.4377 | 17.1475 | 16.3078 | 14.4969 | 45.7566 | 20.781 | 25.6483 | 18.1716 | 16.9605 | 35.3108 | 21.5704 | 15.8212 | 15.5245 | 15.5468 | 14.28 | 15.2296 | 17.6436 |  |  |  | 50.9933 | 180.0807 | 143.3733 | 103.0319 | 0.53187 | -0.032157 | 53.0998 |  |  | 11.3883 |  |  | 16.8902 | 16.9506 | 26.7328 | 16.3206 | 16.0095 | 19.7323 | 166.4277 | 213.1753 | 136.9796 | 140.4997 | 107.5866 |  | 55.4795 | 112.0878 | 55.8576 | 106.1783 | 85.2326 | 154.8455 |  | 88.5963 |  |  | 16.5382 | 19.9961 | 63.5861 | [6 empty] | 89.4662 |  |  | 44.6553 |  |  | 19.8794 | 75.1383 | 232.3695 | 10.5371 | 67.6754 | 150.1547 | 12.5008 | 64.7491 | 165.4118 | 27.189 | 127.9208 | 13.1282 | 118.8609 | 15.1737 | 125.0988 | 11.7263 | 70.168 | 137.6639 | 29.966 | 65.2451 | 184.731 | 13.3069 | 55.9438 | 161.1094 | 14.9844 | 114.5749 | 26.3597 | 127.3494 | 16.6772 | 134.056 | 1.4133 | 18.8487 | 1.7725 | 0.085635 | -38.1675 | 3.1234 | 281.25 | 50 | -1.2542 | -0.21158 | 0.27101 | -0.2746 | 0.56177 | -1.0102 | 0.089817 | -0.7861 | -0.89758 | 0.35352 | -0.64734 | -0.025314 | -1.0726 | -0.81958
42810.4466 | 563 | 18.3367 | 18.4667 | 18.4689 | 18.4673 | 17.7797 | 16.3764 | 14.4271 | 16.5749 | 17.0784 | 17.1743 | 17.1782 | 16.6972 | 15.7133 | 14.345 | 14.6682 | 14.7584 | 15.4362 | 13.2197 | 13.8937 | 17.1143 |  |  |  | 16.5205 | 16.382 | 22.7193 | 166.1522 | 153.4044 | 189.7198 | 16.9829 | 16.4171 | 20.0715 | 16.6988 | 16.3924 | 21.1133 | 60.6393 | 180.2666 |  | 96.3013 | 143.9996 | 139.8246 | 122.8697 |  | 7.0441 | 8.1517 | 7.0525 | 8.3362 | 8.9074 | 12.4613 | 95.0822 | 5.0275 | 7.5083 | 4.4841 | 8.8619 | 8.8407 | 41.7965 | 46.4991 | 42.8273 | 14.4501 |  |  | -0.75218 | -0.21151 | 0.10633 | 0.11762 | 0.083616 | -0.40787 | -0.15846 | 0.24822 | 0.53361 | -1.1505 | 0.16918 | -0.00057662 | -0.00055855 | 0.96383 | 15.9301 | 16.6186 | 17.1634 | 17.4927 | 17.4301 | 16.3752 | 14.7036 | 16.7603 | 17.1014 | 17.3988 | 17.4333 | 17.1404 | 16.2985 | 14.4894 | 47.7459 | 21.5463 | 25.8497 | 17.2783 | 16.1618 | 35.3715 | 21.5677 | 15.8227 | 15.5227 | 15.5571 | 14.2852 | 15.2385 | 17.6631 |  |  |  | 51.222 | 180.2124 | 143.6392 | 103.656 | 0.26809 | 0.11972 | 53.1876 |  |  | 11.3959 |  |  | 16.887 | 16.9493 | 26.7744 | 16.3124 | 16.0087 | 19.7507 | 167.0965 | 213.5747 | 137.3958 | 140.8281 | 109.3048 |  | 55.6575 | 112.8978 | 56.0299 | 105.7006 | 85.6602 | 156.0598 |  | 88.8696 |  |  | 16.6013 | 20.0544 | 62.8623 | [6 empty] | 87.4824 |  |  | 44.7019 |  |  | 19.9138 | 75.8999 | 232.6421 | 10.5661 | 67.9126 | 150.5656 | 12.5228 | 65.262 | 165.6908 | 27.2669 | 128.1012 | 13.1595 | 119.699 | 15.2129 | 125.6538 | 11.759 | 70.4612 | 138.0273 | 30.0778 | 65.6775 | 185.5627 | 13.3406 | 56.3709 | 161.6733 | 15.0254 | 114.7262 | 26.3854 | 127.4747 | 16.7452 | 134.4402 | 1.3942 | 18.8419 | 1.7789 | 0.086156 | -38.2883 | 3.1234 | 294.19 | 49.41 | -1.3003 | -0.53754 | 0.38114 | 0.40086 | 0.34056 | -0.75217 | -0.46883 | -0.82745 | -0.9139 | 0.38314 | -0.86122 | -0.048015 | -1.0248 | -0.82879
42810.4466 | 564 | 18.339 | 18.4614 | 18.4739 | 18.4723 | 17.7827 | 16.3772 | 14.4296 | 16.5771 | 17.0833 | 17.176 | 17.1816 | 16.7022 | 15.7084 | 14.3444 | 14.6622 | 14.7556 | 15.4209 | 13.227 | 13.8792 | 17.1302 |  |  |  | 16.5199 | 16.3855 | 22.7458 | 166.3426 | 153.4742 | 189.3951 | 16.9813 | 16.4203 | 20.0889 | 16.6983 | 16.3895 | 21.1327 | 60.9154 | 182.3926 |  | 96.59 | 144.5001 | 140.1885 | 123.3304 |  | 7.0482 | 8.1671 | 7.0462 | 8.3401 | 8.8992 | 12.4408 | 96.1298 | 5.1022 | 7.5201 | 4.5276 | 8.8718 | 8.8341 | 41.7964 | 46.4655 | 42.8243 | 14.4408 |  |  | -0.41771 | -0.13002 | -0.087516 | -0.34827 | 0.091504 | -0.077344 | -0.15189 | 0.59584 | -0.36895 | -1.4478 | 0.11474 | -0.00055362 | -0.00053226 | 0.97476 | 15.9334 | 16.6331 | 17.1682 | 17.4945 | 17.4392 | 16.3757 | 14.715 | 16.7688 | 17.1043 | 17.4074 | 17.4456 | 17.1496 | 16.3082 | 14.5026 | 45.5596 | 20.3722 | 25.5314 | 17.2696 | 16.0992 | 35.3857 | 21.5773 | 15.8216 | 15.5233 | 15.5538 | 14.2857 | 15.2454 | 17.6785 |  |  |  | 51.4315 | 180.3946 | 143.8923 | 104.4132 | 0.62649 | -0.1432 | 53.4442 |  |  | 11.4121 |  |  | 16.8906 | 16.9577 | 26.8237 | 16.3221 | 16.0156 | 19.7716 | 167.6647 | 213.5323 | 137.8451 | 141.1891 | 108.5944 |  | 55.8659 | 113.9043 | 56.2357 | 110.1909 | 86.1643 | 156.8653 |  | 89.2029 |  |  | 16.6531 | 20.1203 | 62.5489 | [6 empty] | 89.166 |  |  | 44.8823 |  |  | 19.973 | 76.1205 | 233.3702 | 10.6051 | 68.521 | 151.0141 | 12.536 | 65.5035 | 166.3922 | 27.3438 | 128.3135 | 13.184 | 120.1415 | 15.233 | 126.082 | 11.7859 | 70.6208 | 138.6709 | 30.1785 | 66.0043 | 186.1203 | 13.372 | 56.7774 | 162.0035 | 15.0299 | 114.9904 | 26.4283 | 127.592 | 16.8095 | 135.0605 | 1.4133 | 18.8366 | 1.7841 | 0.086352 | -38.2749 | 3.1234 | 298.97 | 49.82 | -0.96868 | -0.42148 | -0.34579 | -0.6898 | 0.35625 | -0.32753 | -0.45899 | -0.80025 | -0.93448 | 0.2777 | -0.61662 | -0.011523 | -1.0276 | -0.84239
42810.4466 | 565 | 18.3487 | 18.4622 | 18.4753 | 18.4787 | 17.7841 | 16.3885 | 14.4397 | 16.5836 | 17.0853 | 17.1784 | 17.1832 | 16.7111 | 15.7167 | 14.3535 | 14.6656 | 14.7529 | 15.4278 | 13.2165 | 13.8823 | 17.1432 |  |  |  | 16.5265 | 16.3935 | 22.7789 | 166.6849 | 153.7034 | 190.3907 | 16.982 | 16.4236 | 20.1138 | 16.6986 | 16.3904 | 21.1607 | 61.2122 | 183.8191 |  | 96.8713 | 144.859 | 140.5496 | 125.8664 |  | 7.0668 | 8.174 | 7.0372 | 8.3366 | 8.8963 | 12.4231 | 97.451 | 5.0459 | 7.5233 | 4.4928 | 8.8891 | 8.8454 | 41.8117 | 46.4642 | 42.8195 | 14.434 |  |  | -0.50182 | 0.059887 | -0.008008 | -0.22539 | 0.35895 | -0.16014 | -0.33917 | 0.77523 | -0.32263 | -0.81881 | 0.078776 | -0.00052405 | -0.00058647 | 0.96997 | 15.9264 | 16.6247 | 17.166 | 17.478 | 17.4293 | 16.3729 | 14.7087 | 16.7625 | 17.1086 | 17.4028 | 17.4356 | 17.1397 | 16.2983 | 14.4959 | 46.3282 | 19.5995 | 23.6925 | 16.7721 | 15.813 | 35.4658 | 21.5682 | 15.8319 | 15.5223 | 15.5587 | 14.2859 | 15.2479 | 17.7006 |  |  |  | 51.6492 | 180.5417 | 143.9645 | 104.8651 | 1.0078 | -0.076196 | 53.83 |  |  | 11.4263 |  |  | 16.8944 | 16.9727 | 26.878 | 16.3292 | 16.0266 | 19.8018 | 167.9437 | 213.4374 | 138.3186 | 141.6724 | 107.6493 |  | 56.0687 | 113.8412 | 56.428 | 112.1049 | 86.566 | 156.5979 |  | 89.5432 |  |  | 16.6637 | 20.1423 | 62.0714 | [6 empty] | 89.4596 |  |  | 45.0853 |  |  | 20.0185 | 76.4799 | 234.5825 | 10.6197 | 68.8122 | 151.441 | 12.5581 | 65.5744 | 166.7857 | 27.4289 | 128.6633 | 13.2003 | 120.2903 | 15.2739 | 126.2915 | 11.76 | 70.798 | 139.1395 | 30.2568 | 66.2919 | 186.6202 | 13.3879 | 57.2853 | 162.3893 | 15.0008 | 115.3557 | 26.4617 | 127.8046 | 16.8549 | 135.5153 | 1.5868 | 18.8299 | 1.788 | 0.085512 | -38.3612 | 3.1234 | 282 | 49.36 | -1.0629 | 0.28605 | -0.1046 | -0.55493 | 0.70557 | -0.47128 | -0.68586 | -0.76672 | -0.92583 | 0.23993 | -0.69258 | 0.19174 | -1.0873 | -0.8472
42810.4466 | 566 | 18.3618 | 18.4712 | 18.4767 | 18.4846 | 17.7873 | 16.3843 | 14.44 | 16.5885 | 17.0948 | 17.1867 | 17.1924 | 16.6982 | 15.724 | 14.3628 | 14.6825 | 14.7659 | 15.4424 | 13.2296 | 13.8768 | 17.1731 |  |  |  | 16.532 | 16.4039 | 22.8209 | 166.9508 | 154.0291 | 189.8481 | 16.9843 | 16.4245 | 20.1453 | 16.7049 | 16.3958 | 21.1881 | 61.4992 | 183.6325 |  | 97.1174 | 145.1529 | 140.9625 | 126.8245 |  | 7.0782 | 8.1778 | 7.0422 | 8.3335 | 8.8783 | 12.4069 | 98.5405 | 4.8515 | 7.5302 | 4.4631 | 8.9036 | 8.8496 | 41.816 | 46.4729 | 42.7987 | 14.4346 |  |  | -0.71275 | 0.078943 | 0.020908 | -0.21488 | 0.10268 | -0.54061 | -0.27214 | 0.80809 | 0.022784 | -0.061434 | 0.37206 | -0.00053391 | -0.00060619 | 0.95959 | 15.9276 | 16.6276 | 17.1689 | 17.4814 | 17.4236 | 16.374 | 14.709 | 16.7619 | 17.1009 | 17.3991 | 17.4383 | 17.1423 | 16.3088 | 14.4961 | 49.4193 | 20.3956 | 24.7731 | 17.2715 | 15.4555 | 35.5905 | 21.5759 | 15.8354 | 15.5303 | 15.5619 | 14.289 | 15.2606 | 17.7235 |  |  |  | 51.8827 | 181.525 | 145.0994 | 105.0744 | 0.58658 | -0.037803 | 54.1315 |  |  | 11.4372 |  |  | 16.8947 | 16.9798 | 26.9287 | 16.326 | 16.0241 | 19.8274 | 168.1546 | 213.5805 | 138.8242 | 142.2699 | 108.1668 |  | 56.2676 | 113.7671 | 56.6284 | 111.5703 | 87.0536 | 155.5347 |  | 89.839 |  |  | 16.6425 | 20.2011 | 61.7119 | [6 empty] | 89.4741 |  |  | 45.1203 |  |  | 20.0625 | 77.0078 | 235.0095 | 10.6377 | 69.0313 | 151.9467 | 12.581 | 65.8463 | 167.0868 | 27.513 | 129.0086 | 13.205 | 120.657 | 15.3105 | 126.7699 | 11.7488 | 71.1388 | 139.5201 | 30.374 | 66.6233 | 186.5532 | 13.4132 | 57.3331 | 162.9047 | 15.0216 | 115.8736 | 26.5135 | 128.1512 | 16.915 | 135.855 | 1.473 | 18.8253 | 1.7919 | 0.085273 | -38.138 | 3.1234 | 288.29 | 48.9 | -1.266 | 0.32842 | 0.16902 | -0.54184 | 0.37735 | -0.86587 | -0.61435 | -0.77396 | -0.91657 | 0.27348 | -1.0214 | 0.072581 | -1.1035 | -0.84471
42810.4466 | 567 | 18.3389 | 18.4656 | 18.4768 | 18.4739 | 17.7787 | 16.3761 | 14.4275 | 16.5828 | 17.0828 | 17.1732 | 17.1866 | 16.6933 | 15.7049 | 14.3364 | 14.6843 | 14.7611 | 15.444 | 13.2273 | 13.8675 | 17.1905 |  |  |  | 16.5323 | 16.4072 | 22.8548 | 167.2018 | 154.1979 | 189.1671 | 16.9796 | 16.4346 | 20.1684 | 16.7001 | 16.4027 | 21.221 | 61.8297 | 184.2845 |  | 97.4734 | 145.5188 | 141.4609 | 128.7967 |  | 7.0775 | 8.185 | 7.0137 | 8.2981 | 8.8479 | 12.3573 | 99.4152 | 4.8442 | 7.5349 | 4.5231 | 8.9173 | 8.8502 | 41.8241 | 46.4956 | 42.7917 | 14.4201 |  |  | -0.73772 | -0.020281 | 0.22264 | -0.17282 | -0.02612 | -0.26856 | -0.029012 | 0.89483 | -0.80991 | -0.32054 | 0.067053 | -0.00055855 | -0.00055362 | 0.94273 | 15.9362 | 16.6328 | 17.1676 | 17.4881 | 17.4278 | 16.3776 | 14.7103 | 16.7684 | 17.1004 | 17.403 | 17.4402 | 17.1429 | 16.3113 | 14.4895 | 49.6631 | 20.8538 | 25.5402 | 18.0073 | 16.1863 | 35.671 | 21.5838 | 15.837 | 15.5393 | 15.5746 | 14.2956 | 15.2631 | 17.7485 |  |  |  | 52.0807 | 182.7677 | 145.5815 | 105.1827 | 0.51445 | -0.18102 | 54.0678 |  |  | 11.4482 |  |  | 16.8909 | 16.9824 | 26.9865 | 16.3262 | 16.0242 | 19.8484 | 168.5935 | 213.8295 | 139.216 | 142.8079 | 108.5117 |  | 56.469 | 113.9232 | 56.846 | 107.5817 | 87.464 | 153.4568 |  | 90.1557 |  |  | 16.6543 | 20.251 | 62.2135 | [6 empty] | 87.6839 |  |  | 45.2719 |  |  | 20.1021 | 77.3787 | 235.0327 | 10.6173 | 69.2687 | 152.4998 | 12.6024 | 66.4018 | 167.3517 | 27.6121 | 129.3509 | 13.2257 | 121.0115 | 15.3448 | 127.1471 | 11.7854 | 71.5927 | 140.043 | 30.4743 | 66.9812 | 186.6359 | 13.4374 | 57.2497 | 163.3181 | 15.0437 | 116.3941 | 26.5808 | 128.5194 | 16.9648 | 136.2388 | 1.6095 | 18.8194 | 1.7957 | 0.087698 | -38.2358 | 3.1233 | 283.83 | 50.17 | -1.287 | -0.16647 | 0.55154 | -0.48594 | -0.19031 | -0.61024 | -0.20057 | -0.77631 | -0.91309 | 0.40003 | -1.039 | -0.011736 | -1.1463 | -0.84068
42810.4466 | 568 | 18.3487 | 18.4647 | 18.4693 | 18.4726 | 17.7772 | 16.3802 | 14.4282 | 16.5862 | 17.0801 | 17.1827 | 17.1846 | 16.6994 | 15.7097 | 14.3388 | 14.6835 | 14.7586 | 15.441 | 13.2323 | 13.8719 | 17.2082 |  |  |  | 16.5321 | 16.4048 | 22.8964 | 167.386 | 154.2048 | 188.5342 | 16.9795 | 16.4286 | 20.1841 | 16.7026 | 16.4029 | 21.2464 | 62.177 | 184.8657 |  | 97.8032 | 145.9102 | 141.9329 | 131.6222 |  | 7.0804 | 8.1794 | 6.9994 | 8.241 | 8.8048 | 12.3122 | 100.1842 | 4.8149 | 7.5339 | 4.5799 | 8.9322 | 8.861 | 41.8252 | 46.5162 | 42.7816 | 14.4199 |  |  | -0.65624 | 0.16239 | 0.12539 | -0.3003 | -0.042548 | -0.4013 | -0.15584 | 0.64907 | -0.7599 | -0.099408 | 0.34265 | -0.00056019 | -0.0005569 | 0.9476 | 15.936 | 16.6354 | 17.1722 | 17.4869 | 17.4322 | 16.3758 | 14.7093 | 16.7695 | 17.1045 | 17.4043 | 17.4409 | 17.1466 | 16.304 | 14.493 | 48.0137 | 21.0664 | 25.0003 | 17.8356 | 16.4892 | 35.7223 | 21.5869 | 15.8345 | 15.5376 | 15.5697 | 14.2926 | 15.2659 | 17.765 |  |  |  | 52.2759 | 183.4079 | 145.7994 | 104.9384 | 0.61798 | 0.13082 | 53.9736 |  |  | 11.4551 |  |  | 16.8856 | 16.9861 | 27.0306 | 16.3251 | 16.0291 | 19.8748 | 169.0514 | 213.712 | 139.4461 | 143.1714 | 108.6483 |  | 56.6796 | 114.7456 | 57.0599 | 109.7246 | 87.8989 | 152.2786 |  | 90.4457 |  |  | 16.6815 | 20.2876 | 63.1413 | [6 empty] | 89.9238 |  |  | 45.3617 |  |  | 20.1513 | 77.5379 | 236.0428 | 10.6 | 69.8633 | 152.8618 | 12.6123 | 66.6141 | 167.5722 | 27.7333 | 129.6813 | 13.2727 | 121.2454 | 15.3813 | 127.5254 | 11.8316 | 71.9655 | 140.7038 | 30.5931 | 67.3277 | 186.7723 | 13.4673 | 57.7719 | 163.496 | 15.0833 | 116.7261 | 26.6556 | 128.6299 | 17.0346 | 136.5298 | 1.4356 | 18.8151 | 1.7982 | 0.088921 | -38.2772 | 3.1234 | 273.43 | 49.07 | -1.213 | 0.47104 | 0.41391 | -0.64055 | -0.24287 | -0.74589 | -0.46481 | -0.77255 | -0.92825 | 0.35722 | -0.84965 | 0.048609 | -1.2121 | -0.82694
42810.4466 | 569 | 18.3546 | 18.4725 | 18.4764 | 18.4766 | 17.788 | 16.3852 | 14.4353 | 16.591 | 17.0855 | 17.1844 | 17.1899 | 16.7049 | 15.7177 | 14.3441 | 14.6893 | 14.7606 | 15.4383 | 13.2299 | 13.8834 | 17.2266 |  |  |  | 16.5343 | 16.4061 | 22.9373 | 167.5268 | 154.1629 | 188.6025 | 16.9915 | 16.4342 | 20.2158 | 16.7125 | 16.4157 | 21.2784 | 62.5428 | 185.2718 |  | 98.1108 | 146.3976 | 142.4691 | 132.9969 |  | 7.0735 | 8.1587 | 7.0017 | 8.2331 | 8.7965 | 12.2998 | 100.7133 | 4.7905 | 7.5313 | 4.6004 | 8.9357 | 8.8646 | 41.8275 | 46.5099 | 42.763 | 14.4106 |  |  | -0.76927 | 0.061855 | 0.036676 | -0.037454 | 0.16707 | -0.33428 | 0.1287 | 0.47427 | -0.52716 | -2.0296 | 0.046786 | -0.00056183 | -0.00057826 | 0.98265 | 15.9537 | 16.639 | 17.1703 | 17.4894 | 17.4344 | 16.3845 | 14.7118 | 16.775 | 17.1099 | 17.411 | 17.4462 | 17.1507 | 16.3097 | 14.5027 | 47.4732 | 21.6257 | 25.7459 | 17.6976 | 16.3827 | 35.7903 | 21.6023 | 15.8293 | 15.5426 | 15.5721 | 14.2898 | 15.2841 | 17.7858 |  |  |  | 52.4724 | 184.3106 | 146.1088 | 104.8603 | 0.74663 | -0.035921 | 54.273 |  |  | 11.4654 |  |  | 16.8828 | 16.9857 | 27.0765 | 16.3187 | 16.0334 | 19.8927 | 169.3697 | 213.7794 | 139.5312 | 143.2679 | 108.6428 |  | 56.8832 | 115.4772 | 57.2521 | 112.0569 | 88.4327 | 151.4593 |  | 90.6756 |  |  | 16.7244 | 20.3126 | 63.3584 | [6 empty] | 91.0799 |  |  | 45.3091 |  |  | 20.2081 | 77.7398 | 236.7354 | 10.557 | 70.8627 | 153.1904 | 12.63 | 66.855 | 167.783 | 27.8415 | 129.9061 | 13.3154 | 121.4708 | 15.3907 | 128.0482 | 11.8488 | 72.5434 | 141.2589 | 30.6855 | 67.5693 | 186.8477 | 13.5109 | 58.275 | 163.9132 | 15.121 | 116.9288 | 26.7253 | 128.7854 | 17.0949 | 136.8297 | 1.4331 | 18.8119 | 1.7983 | 0.086656 | -38.2561 | 3.1234 | 261.44 | 48.9 | -1.3134 | 0.2907 | 0.22385 | -0.22621 | 0.48126 | -0.68074 | 0.42239 | -0.76508 | -0.94166 | 0.31297 | -0.78159 | -0.032433 | -1.237 | -0.81778
42810.4466 | 570 | 18.3541 | 18.4739 | 18.4758 | 18.4813 | 17.7882 | 16.388 | 14.4368 | 16.595 | 17.0933 | 17.1933 | 17.1915 | 16.706 | 15.7281 | 14.3499 | 14.6855 | 14.7608 | 15.4387 | 13.226 | 13.8727 | 17.2399 |  |  |  | 16.5279 | 16.4118 | 22.9726 | 167.7786 | 154.306 | 188.9583 | 16.9901 | 16.4376 | 20.2347 | 16.7089 | 16.4154 | 21.3098 | 62.8568 | 184.5824 |  | 98.3702 | 146.8364 | 142.932 | 131.1332 |  | 7.0779 | 8.1618 | 7.0092 | 8.2664 | 8.7899 | 12.4565 | 101.2908 | 4.6794 | 7.5345 | 4.5913 | 8.9463 | 8.8678 | 41.8382 | 46.488 | 42.7517 | 14.4098 |  |  | -0.62207 | 0.053315 | 0.08202 | -0.34104 | 0.15787 | -0.2817 | -0.07764 | 0.71478 | -0.27982 | 0.075355 | 0.1056 | -0.00058483 | -0.0005569 | 1.0156 | 15.9409 | 16.6356 | 17.1609 | 17.4854 | 17.4352 | 16.375 | 14.7087 | 16.7683 | 17.1013 | 17.3969 | 17.4415 | 17.1456 | 16.3054 | 14.4875 | 47.8211 | 21.7608 | 25.6 | 17.8033 | 16.2928 | 35.8767 | 21.6234 | 15.8293 | 15.5383 | 15.5656 | 14.2879 | 15.2849 | 17.8003 |  |  |  | 52.6746 | 184.7788 | 146.323 | 105.0486 | 0.78269 | -0.15995 | 54.6288 |  |  | 11.4784 |  |  | 16.8891 | 16.9863 | 27.1281 | 16.3221 | 16.0374 | 19.9112 | 169.7798 | 214.2169 | 139.7225 | 143.3845 | 109.1787 |  | 57.0743 | 116.3448 | 57.4518 | 108.9887 | 88.8093 | 150.784 |  | 90.9758 |  |  | 16.7833 | 20.3471 | 63.2254 | [6 empty] | 89.1591 |  |  | 45.3871 |  |  | 20.2686 | 78.3214 | 236.2741 | 10.5285 | 71.5158 | 153.369 | 12.642 | 67.3794 | 168.0933 | 27.9397 | 130.0569 | 13.3375 | 121.6421 | 15.394 | 128.5387 | 11.8729 | 73.0923 | 141.7657 | 30.7668 | 67.7013 | 187.0811 | 13.5327 | 58.5308 | 164.3862 | 15.1629 | 117.3391 | 26.7678 | 128.9646 | 17.1454 | 137.2074 | 1.5868 | 18.8106 | 1.8008 | 0.087712 | -38.3333 | 3.1234 | 278.19 | 50.02 | -1.1816 | 0.26989 | 0.33475 | -0.6826 | 0.46795 | -0.6251 | -0.32817 | -0.7731 | -0.95858 | 0.41271 | -0.81007 | -0.013755 | -1.1738 | -0.81581
42810.4466 | 571 | 18.3569 | 18.4743 | 18.479 | 18.4838 | 17.7915 | 16.385 | 14.4391 | 16.5905 | 17.0891 | 17.1911 | 17.1894 | 16.7087 | 15.7307 | 14.3555 | 14.6788 | 14.7645 | 15.4362 | 13.2246 | 13.8608 | 17.2534 |  |  |  | 16.5261 | 16.413 | 23.0065 | 168.0871 | 154.6348 | 188.7728 | 16.9898 | 16.4409 | 20.2632 | 16.7093 | 16.4154 | 21.3453 | 63.1264 | 183.3414 |  | 98.639 | 147.3335 | 143.2773 | 128.4689 |  | 7.076 | 8.1573 | 7.0188 | 8.2789 | 8.7963 | 12.6212 | 102.3115 | 4.5404 | 7.5369 | 4.5437 | 8.9523 | 8.8604 | 41.8446 | 46.4517 | 42.7204 | 14.3972 |  |  | -0.81855 | 0.14794 | 0.11224 | -0.51452 | 0.72956 | -0.53667 | -0.0093 | 0.34416 | -0.44387 | -0.12563 | 0.25741 | -0.00056348 | -0.00059305 | 1.0368 | 15.9416 | 16.6309 | 17.1622 | 17.49 | 17.4253 | 16.3681 | 14.7125 | 16.7714 | 17.1063 | 17.4054 | 17.4388 | 17.1485 | 16.3085 | 14.4867 | 48.3 | 22.0712 | 25.3356 | 17.7601 | 15.9629 | 35.9486 | 21.6245 | 15.8381 | 15.5407 | 15.5791 | 14.2986 | 15.2974 | 17.8363 |  |  |  | 52.8962 | 185.0687 | 146.6693 | 105.3897 | 0.60056 | 0.23622 | 54.6485 |  |  | 11.4851 |  |  | 16.8923 | 16.9985 | 27.1812 | 16.3168 | 16.0348 | 19.9378 | 170.097 | 214.4136 | 139.9898 | 143.6158 | 108.8956 |  | 57.2974 | 116.809 | 57.6896 | 110.7805 | 89.2612 | 152.2733 |  | 91.3173 |  |  | 16.8422 | 20.395 | 63.0001 | [6 empty] | 89.4096 |  |  | 45.5231 |  |  | 20.3353 | 78.7386 | 236.6102 | 10.531 | 71.852 | 153.5074 | 12.6642 | 67.6391 | 168.2807 | 28.0623 | 130.2249 | 13.3773 | 121.7454 | 15.4207 | 128.8044 | 11.9146 | 73.5948 | 142.3377 | 30.8545 | 68.0285 | 187.5529 | 13.554 | 58.7188 | 164.7751 | 15.2179 | 117.7138 | 26.8207 | 129.1699 | 17.211 | 137.7419 | 1.635 | 18.808 | 1.802 | 0.087662 | -38.1734 | 3.1234 | 286.07 | 49.08 | -1.3551 | 0.44957 | 0.3916 | -0.83842 | 1.0063 | -0.86304 | -0.11361 | -0.75721 | -0.96292 | 0.38035 | -0.8548 | 0.015758 | -1.09 | -0.81739
42810.4467 | 572 | 18.3607 | 18.4714 | 18.4802 | 18.4837 | 17.794 | 16.3851 | 14.437 | 16.5859 | 17.0881 | 17.1875 | 17.1851 | 16.7091 | 15.7192 | 14.3595 | 14.6707 | 14.7615 | 15.4334 | 13.2199 | 13.8615 | 17.2636 |  |  |  | 16.5214 | 16.4025 | 23.0328 | 168.2991 | 154.9974 | 188.4427 | 16.9891 | 16.4442 | 20.2933 | 16.7072 | 16.423 | 21.3642 | 63.372 | 182.509 |  | 98.9326 | 147.7261 | 143.5024 | 126.5886 |  | 7.0781 | 8.1821 | 7.0231 | 8.2943 | 8.8132 | 12.7177 | 103.6916 | 4.4578 | 7.5459 | 4.5415 | 8.9749 | 8.8639 | 41.8597 | 46.4461 | 42.7041 | 14.3973 |  |  | -0.60827 | -0.039997 | -0.058604 | -0.31016 | 0.30704 | -0.11151 | 0.26735 | 0.87708 | -1.1335 | 0.18256 | -0.046802 | -0.00052405 | -0.00057826 | 1.1486 | 15.9566 | 16.6371 | 17.1711 | 17.497 | 17.4339 | 16.3804 | 14.7155 | 16.7765 | 17.1111 | 17.4028 | 17.4392 | 17.1548 | 16.311 | 14.4976 | 48.2814 | 22.9477 | 26.9972 | 18.1783 | 15.9611 | 36.0219 | 21.6412 | 15.8266 | 15.5242 | 15.5688 | 14.2863 | 15.2892 | 17.8387 |  |  |  | 53.0696 | 185.7148 | 147.3994 | 105.243 | 0.8301 | 0.20403 | 54.5744 |  |  | 11.4892 |  |  | 16.892 | 17.0029 | 27.2282 | 16.3154 | 16.0317 | 19.9605 | 170.1749 | 214.2797 | 140.2007 | 143.8435 | 109.173 |  | 57.4969 | 116.9845 | 57.8883 | 116.7408 | 89.6952 | 153.7778 |  | 91.5828 |  |  | 16.8902 | 20.4038 | 62.921 | [6 empty] | 91.9772 |  |  | 45.6202 |  |  | 20.3733 | 78.742 | 236.9392 | 10.5231 | 72.7125 | 153.6691 | 12.6761 | 67.8731 | 168.6118 | 28.1759 | 130.4516 | 13.4004 | 121.9904 | 15.4389 | 129.0876 | 11.9494 | 73.5738 | 142.675 | 30.9147 | 68.3705 | 188.0663 | 13.5816 | 59.0617 | 165.172 | 15.2542 | 118.0337 | 26.8842 | 129.4536 | 17.2661 | 138.1441 | 1.7812 | 18.8097 | 1.8027 | 0.087503 | -38.2053 | 3.1234 | 283.14 | 48.87 | -1.1677 | -0.23377 | -0.28297 | -0.65098 | 0.6529 | -0.39347 | 0.60924 | -0.75774 | -0.96064 | 0.23154 | -0.8441 | -0.16691 | -1.0288 | -0.80713
42810.4467 | 573 | 18.3648 | 18.4758 | 18.4853 | 18.4877 | 17.7888 | 16.3919 | 14.447 | 16.5986 | 17.0971 | 17.1927 | 17.1956 | 16.7198 | 15.7246 | 14.3489 | 14.6806 | 14.7531 | 15.4347 | 13.2249 | 13.858 | 17.2796 |  |  |  | 16.5161 | 16.4143 | 23.0722 | 168.456 | 155.3317 | 186.9588 | 16.9936 | 16.4442 | 20.316 | 16.7159 | 16.4229 | 21.3965 | 63.6408 | 180.9368 |  | 99.2013 | 148.1337 | 143.6726 | 126.976 |  | 7.0776 | 8.1771 | 7.0118 | 8.2902 | 8.8068 | 12.7589 | 104.6023 | 4.5157 | 7.5424 | 4.5168 | 8.9805 | 8.8613 | 41.883 | 46.4428 | 42.6742 | 14.3818 |  |  | -0.43413 | -0.13397 | 0.064276 | -0.56446 | -0.041892 | 0.3051 | 0.25486 | 0.54196 | -0.58554 | -0.3476 | 0.053939 | -0.00052405 | -0.00058155 | 1.0616 | 15.9588 | 16.6421 | 17.1711 | 17.4997 | 17.4458 | 16.3844 | 14.7173 | 16.7747 | 17.1149 | 17.4055 | 17.4419 | 17.1496 | 16.3157 | 14.5033 | 50.3468 | 24.1701 | 28.3372 | 18.6833 | 16.8474 | 36.138 | 21.673 | 15.8298 | 15.5365 | 15.5768 | 14.2937 | 15.2975 | 17.8584 |  |  |  | 53.2679 | 185.9632 | 148.3625 | 104.6378 | 0.95227 | 0.18728 | 54.5249 |  |  | 11.4938 |  |  | 16.8818 | 17.0059 | 27.2798 | 16.3133 | 16.0391 | 19.9777 | 170.3965 | 214.1344 | 140.3394 | 144.014 | 109.9123 |  | 57.7202 | 117.1333 | 58.0796 | 115.6356 | 90.2118 | 155.2633 |  | 91.857 |  |  | 16.9533 | 20.4489 | 63.2267 | [6 empty] | 94.1477 |  |  | 45.7354 |  |  | 20.4325 | 78.8488 | 237.0236 | 10.5123 | 73.4896 | 154.0075 | 12.6663 | 68.533 | 168.9944 | 28.2478 | 130.7341 | 13.4882 | 122.254 | 15.4616 | 129.5058 | 11.9949 | 73.5395 | 142.9081 | 30.9807 | 68.5512 | 188.6556 | 13.6181 | 59.5063 | 165.6176 | 15.2533 | 118.3895 | 26.9434 | 129.6807 | 17.3127 | 138.3332 | 1.6675 | 18.8093 | 1.8025 | 0.086967 | -38.2835 | 3.1234 | 282.61 | 50 | -0.98494 | -0.42783 | 0.29634 | -0.87819 | -0.24118 | 0.65088 | 0.59488 | -0.77024 | -0.95789 | 0.2822 | -1.0599 | -0.31209 | -1.0298 | -0.78325
42810.4467 | 574 | 18.358 | 18.4764 | 18.4776 | 18.4725 | 17.7814 | 16.3797 | 14.4331 | 16.5899 | 17.0834 | 17.1813 | 17.1849 | 16.7023 | 15.7203 | 14.3436 | 14.6873 | 14.7552 | 15.4488 | 13.234 | 13.8539 | 17.318 |  |  |  | 16.5303 | 16.4326 | 23.1176 | 168.5279 | 155.6572 | 186.6378 | 16.9986 | 16.4525 | 20.3396 | 16.7118 | 16.4284 | 21.4283 | 63.9067 | 180.453 |  | 99.4815 | 148.5984 | 143.8833 | 126.4042 |  | 7.0653 | 8.1716 | 7.0038 | 8.2954 | 8.8123 | 12.7983 | 105.6331 | 4.6515 | 7.5431 | 4.4527 | 8.9861 | 8.8723 | 41.9077 | 46.447 | 42.657 | 14.3772 |  |  | -0.41836 | 0.24848 | -0.11512 | -0.69654 | -0.011664 | -0.049744 | -0.075012 | 0.52224 | -0.09456 | -0.96819 | 0.20455 | -0.00055526 | -0.00058812 | 0.99996 | 15.9524 | 16.6355 | 17.1628 | 17.484 | 17.4379 | 16.3712 | 14.715 | 16.768 | 17.1065 | 17.4007 | 17.4386 | 17.1372 | 16.3036 | 14.4953 | 53.1481 | 25.0146 | 29.4083 | 19.6977 | 16.8903 | 36.2869 | 21.7056 | 15.8264 | 15.536 | 15.5762 | 14.2963 | 15.3038 | 17.8825 |  |  |  | 53.4748 | 186.0645 | 148.7894 | 104.6763 | 0.89493 | 0.16997 | 54.7115 |  |  | 11.4986 |  |  | 16.8846 | 17.0072 | 27.3328 | 16.3048 | 16.0383 | 20.0003 | 170.7584 | 214.1247 | 140.6501 | 144.2998 | 110.6341 |  | 57.967 | 117.4582 | 58.2734 | 109.5833 | 90.6585 | 156.1051 |  | 92.1653 |  |  | 16.9974 | 20.4917 | 63.4421 | [6 empty] | 94.3727 |  |  | 45.7384 |  |  | 20.4993 | 79.5377 | 236.8107 | 10.5061 | 73.8101 | 154.4132 | 12.6773 | 68.8559 | 169.2198 | 28.2897 | 131.0483 | 13.5756 | 122.5366 | 15.4911 | 129.7514 | 12.0364 | 74.1722 | 143.1898 | 31.0698 | 68.7974 | 188.9225 | 13.6228 | 59.793 | 165.9181 | 15.2539 | 118.7184 | 27.0374 | 129.9899 | 17.3556 | 138.6622 | 1.6319 | 18.809 | 1.8039 | 0.087785 | -38.295 | 3.1234 | 284.05 | 48.8 | -0.96655 | 0.58266 | -0.39659 | -0.97553 | -0.12727 | -0.26283 | -0.32276 | -0.78141 | -0.95993 | 0.4676 | -1.3536 | -0.42729 | -1.0042 | -0.77693
42810.4467 | 575 | 18.3554 | 18.472 | 18.4639 | 18.4725 | 17.7843 | 16.3725 | 14.4264 | 16.5789 | 17.0783 | 17.1769 | 17.1851 | 16.7033 | 15.7112 | 14.343 | 14.679 | 14.7549 | 15.454 | 13.2334 | 13.8541 | 17.3294 |  |  |  | 16.5302 | 16.4337 | 23.1611 | 168.6232 | 156.1269 | 186.869 | 16.9979 | 16.4475 | 20.3663 | 16.7049 | 16.4297 | 21.4566 | 64.1494 | 180.1333 |  | 99.7748 | 148.9386 | 144.1412 | 124.9212 |  | 7.0791 | 8.183 | 7.0067 | 8.3185 | 8.8426 | 12.9084 | 107.0713 | 4.7481 | 7.5501 | 4.4047 | 8.9959 | 8.8711 | 41.9137 | 46.4516 | 42.6315 | 14.366 |  |  | -0.46436 | -0.20428 | -0.15783 | -0.026286 | 0.080988 | -0.17525 | -0.17226 | 0.54656 | -0.29636 | -0.21899 | 0.10043 | -0.00052076 | -0.00056676 | 0.97723 | 15.9565 | 16.6258 | 17.1648 | 17.4829 | 17.4347 | 16.3668 | 14.7135 | 16.7606 | 17.1056 | 17.4005 | 17.4375 | 17.1385 | 16.298 | 14.4879 | 56.7778 | 26.3614 | 31.0793 | 20.129 | 17.3949 | 36.4677 | 21.752 | 15.8334 | 15.5345 | 15.581 | 14.2931 | 15.3106 | 17.9066 |  |  |  | 53.6961 | 186.6142 | 149.1692 | 105.0107 | 0.36291 | 0.42856 | 54.9214 |  |  | 11.5079 |  |  | 16.8926 | 17.0204 | 27.3937 | 16.3159 | 16.0492 | 20.0333 | 171.2182 | 214.2268 | 140.9613 | 144.6856 | 111.9218 |  | 58.1844 | 118.0785 | 58.4695 | 107.8416 | 91.005 | 156.5922 |  | 92.4178 |  |  | 16.9834 | 20.5441 | 63.3746 | [6 empty] | 93.9063 |  |  | 45.8657 |  |  | 20.5297 | 79.8547 | 236.7492 | 10.5751 | 73.9124 | 154.7834 | 12.6796 | 68.8515 | 169.0633 | 28.3432 | 131.3144 | 13.638 | 122.9592 | 15.4793 | 130.3367 | 12.0711 | 74.2237 | 143.5139 | 31.1838 | 69.2193 | 189.2042 | 13.6351 | 60.0401 | 166.3553 | 15.2624 | 119.0166 | 27.1155 | 130.6113 | 17.3947 | 139.1308 | 1.654 | 18.8103 | 1.8038 | 0.088176 | -38.3043 | 3.1234 | 280.26 | 49.58 | -1.0186 | -0.52831 | -0.46438 | -0.18951 | 0.33543 | -0.49343 | -0.48921 | -0.80935 | -0.97009 | 0.52939 | -1.7356 | -0.60753 | -0.95419 | -0.77833
42810.4467 | 576 | 18.3647 | 18.4746 | 18.473 | 18.4764 | 17.7898 | 16.3796 | 14.4339 | 16.5831 | 17.0832 | 17.1814 | 17.1839 | 16.7021 | 15.7187 | 14.3476 | 14.6913 | 14.7702 | 15.4532 | 13.2377 | 13.862 | 17.3517 |  |  |  | 16.5421 | 16.4405 | 23.2011 | 169.0667 | 156.5253 | 189.0735 | 17.006 | 16.4684 | 20.3947 | 16.7157 | 16.4451 | 21.4899 | 64.4145 | 178.8529 |  | 100.0578 | 149.2196 | 144.5776 | 126.5141 |  | 7.0931 | 8.1906 | 7.0043 | 8.3322 | 8.8511 | 13.0069 | 108.125 | 4.8014 | 7.5569 | 4.4017 | 9.0177 | 8.8726 | 41.9294 | 46.453 | 42.6233 | 14.3634 |  |  | -0.60958 | 0.034259 | 0.084648 | -0.68931 | 0.002792 | -0.095084 | 0.015672 | 0.40002 | 0.28686 | 0.0063312 | 0.093877 | -0.00057005 | -0.00056183 | 0.98237 | 15.9549 | 16.6292 | 17.1702 | 17.4836 | 17.4318 | 16.3717 | 14.7108 | 16.765 | 17.1062 | 17.4029 | 17.4367 | 17.1343 | 16.3033 | 14.4886 | 57.3997 | 25.4303 | 31.3472 | 21.2568 | 18.8687 | 36.6107 | 21.8025 | 15.8385 | 15.5388 | 15.5867 | 14.2975 | 15.3326 | 17.9324 |  |  |  | 53.9055 | 186.8439 | 149.3234 | 105.2452 | 1.2213 | -0.29884 | 55.0874 |  |  | 11.5081 |  |  | 16.8853 | 17.0278 | 27.4424 | 16.314 | 16.049 | 20.0529 | 171.5091 | 214.0529 | 141.2201 | 144.9587 | 112.0566 |  | 58.3736 | 118.87 | 58.6675 | 113.2304 | 91.4816 | 156.3633 |  | 92.6304 |  |  | 16.9525 | 20.6006 | 63.0017 | [6 empty] | 95.9701 |  |  | 45.8942 |  |  | 20.5679 | 79.8968 | 237.7089 | 10.6264 | 74.4602 | 155.0001 | 12.7233 | 69.4498 | 168.9185 | 28.4314 | 131.5277 | 13.6582 | 123.4234 | 15.478 | 130.799 | 12.0413 | 74.1822 | 143.6538 | 31.2884 | 69.6825 | 189.178 | 13.665 | 60.2421 | 166.6185 | 15.2793 | 119.4063 | 27.2134 | 131.0368 | 17.4702 | 139.5043 | 1.4127 | 18.8112 | 1.8031 | 0.087054 | -38.301 | 3.1234 | 286.03 | 49.86 | -1.1698 | 0.21636 | 0.34009 | -0.97049 | 0.062291 | -0.36352 | 0.14758 | -0.80627 | -0.98494 | 0.39817 | -1.7879 | -0.63139 | -0.98877 | -0.77736
42810.4467 | 577 | 18.36 | 18.4729 | 18.4732 | 18.48 | 17.7839 | 16.3805 | 14.4319 | 16.5864 | 17.087 | 17.1857 | 17.1849 | 16.7019 | 15.7187 | 14.3472 | 14.6914 | 14.7622 | 15.4523 | 13.2287 | 13.8787 | 17.3693 |  |  |  | 16.5366 | 16.4475 | 23.2407 | 169.5524 | 156.7354 | 192.0143 | 17.0088 | 16.4682 | 20.4185 | 16.719 | 16.4519 | 21.5242 | 64.6923 | 178.1027 |  | 100.3288 | 149.4998 | 145.1193 | 128.4984 |  | 7.1064 | 8.2064 | 7.0063 | 8.3283 | 8.8478 | 12.9452 | 108.7896 | 4.7886 | 7.564 | 4.4235 | 9.0338 | 8.8792 | 41.9364 | 46.4552 | 42.6176 | 14.3547 |  |  | -0.53467 | -0.013713 | -0.27611 | -0.58023 | -0.025464 | -0.031344 | 0.24566 | 0.27714 | -0.17785 | 0.045774 | 0.26277 | -0.00057826 | -0.00058647 | 1.0159 | 15.9641 | 16.6243 | 17.1654 | 17.4854 | 17.4377 | 16.3754 | 14.7106 | 16.7691 | 17.1049 | 17.393 | 17.4406 | 17.1372 | 16.3034 | 14.4905 | 58.2646 | 24.7429 | 28.7794 | 20.3078 | 18.907 | 36.7581 | 21.8093 | 15.835 | 15.5407 | 15.5905 | 14.2994 | 15.3368 | 17.9516 |  |  |  | 54.0931 | 187.1252 | 149.3678 | 105.0526 | 1.2 | -0.079396 | 55.1563 |  |  | 11.5099 |  |  | 16.8806 | 17.026 | 27.4912 | 16.3143 | 16.0458 | 20.0779 | 171.5887 | 213.9486 | 141.4699 | 145.1387 | 111.7508 |  | 58.6074 | 119.1058 | 58.8803 | 114.845 | 92.1375 | 156.9917 |  | 92.9068 |  |  | 16.9747 | 20.6228 | 63.0037 | [6 empty] | 96.0072 |  |  | 45.9442 |  |  | 20.6079 | 79.8511 | 238.2613 | 10.5988 | 75.0209 | 155.2916 | 12.7411 | 69.3776 | 168.8736 | 28.4605 | 132.1256 | 13.6094 | 123.8317 | 15.4669 | 130.8502 | 11.9481 | 75.0024 | 144.0175 | 31.378 | 70.0026 | 189.4195 | 13.7229 | 60.5541 | 166.5246 | 15.3198 | 119.7519 | 27.2901 | 131.2683 | 17.5053 | 139.7798 | 1.4127 | 18.8096 | 1.8037 | 0.086569 | -38.2673 | 3.1234 | 273.04 | 49.14 | -1.099 | -0.13689 | -0.61424 | -0.89042 | -0.1881 | -0.20869 | 0.58424 | -0.78935 | -0.98381 | 0.37877 | -1.8666 | -0.34528 | -1.0337 | -0.76531
42810.4467 | 578 | 18.3622 | 18.4733 | 18.4783 | 18.4791 | 17.781 | 16.3825 | 14.4351 | 16.5884 | 17.0885 | 17.1878 | 17.1865 | 16.705 | 15.7192 | 14.3528 | 14.6989 | 14.7779 | 15.4702 | 13.2334 | 13.8838 | 17.3987 |  |  |  | 16.5348 | 16.45 | 23.2794 | 170.0304 | 156.9458 | 192.2896 | 17.0078 | 16.4663 | 20.4314 | 16.7094 | 16.4465 | 21.5498 | 64.987 | 176.7602 |  | 100.5776 | 149.7839 | 145.5902 | 128.9369 |  | 7.1111 | 8.219 | 7.005 | 8.3092 | 8.8431 | 12.9154 | 108.4705 | 4.6893 | 7.5681 | 4.4769 | 9.0396 | 8.8793 | 41.9525 | 46.4591 | 42.6118 | 14.3487 |  |  | -0.51825 | 0.060543 | -0.1184 | -0.02037 | 0.19467 | -0.20548 | 0.33372 | 0.60044 | -0.52346 | -0.29914 | 0.25085 | -0.0005454 | -0.00058155 | 1.0303 | 15.9575 | 16.6272 | 17.1681 | 17.4868 | 17.4368 | 16.3737 | 14.7111 | 16.7707 | 17.1056 | 17.3982 | 17.4378 | 17.1404 | 16.3045 | 14.4836 | 58.3433 | 24.5276 | 28.4457 | 19.0761 | 17.8568 | 36.8847 | 21.822 | 15.8338 | 15.5373 | 15.5856 | 14.3012 | 15.3457 | 17.965 |  |  |  | 54.2907 | 187.5549 | 149.5212 | 104.7919 | 0.97699 | 0.14005 | 55.1534 |  |  | 11.5228 |  |  | 16.8925 | 17.034 | 27.55 | 16.3136 | 16.0503 | 20.1052 | 171.5481 | 214.0599 | 141.7757 | 145.3748 | 112.4483 |  | 58.8332 | 119.5963 | 59.071 | 114.3211 | 92.6359 | 157.2107 |  | 93.171 |  |  | 17.0375 | 20.6425 | 63.7942 | [6 empty] | 95.3584 |  |  | 45.9063 |  |  | 20.6352 | 80.5313 | 238.2983 | 10.5983 | 75.3202 | 155.4249 | 12.7448 | 69.5332 | 168.8651 | 28.5131 | 132.6503 | 13.655 | 123.9245 | 15.4706 | 131.0091 | 11.9304 | 75.297 | 144.361 | 31.4635 | 70.0557 | 189.2506 | 13.7687 | 60.8127 | 167.0055 | 15.4979 | 120.1102 | 27.3537 | 131.4714 | 17.5411 | 139.995 | 1.4096 | 18.8141 | 1.8049 | 0.088067 | -38.2471 | 3.1233 | 294.72 | 49.61 | -1.0823 | 0.28763 | -0.40224 | -0.16684 | 0.52006 | -0.5343 | 0.68091 | -0.80058 | -0.99056 | 0.41269 | -1.8604 | -0.30672 | -1.0352 | -0.75101
42810.4467 | 579 | 18.365 | 18.4715 | 18.4779 | 18.483 | 17.7847 | 16.3753 | 14.4336 | 16.5829 | 17.0831 | 17.1834 | 17.1834 | 16.6972 | 15.7259 | 14.351 | 14.7021 | 14.7699 | 15.4611 | 13.2334 | 13.8592 | 17.4066 |  |  |  | 16.5355 | 16.4458 | 23.3109 | 170.282 | 156.8113 | 191.4337 | 17.0105 | 16.4669 | 20.4608 | 16.7103 | 16.4496 | 21.569 | 65.2363 | 176.3693 |  | 100.8107 | 150.0744 | 145.9967 | 127.7473 |  | 7.1234 | 8.2414 | 7.0092 | 8.31 | 8.8337 | 12.9082 | 107.2423 | 4.51 | 7.5697 | 4.4502 | 9.0515 | 8.8853 | 41.9635 | 46.4652 | 42.6003 | 14.3328 |  |  | -0.62272 | -0.22267 | 0.01368 | -0.12551 | 0.17298 | 0.12111 | 0.29232 | 0.64118 | -0.015747 | -0.55488 | 0.2582 | -0.00053391 | -0.00059962 | 1.0061 | 15.9651 | 16.6385 | 17.1737 | 17.4955 | 17.4335 | 16.3773 | 14.7195 | 16.7712 | 17.1105 | 17.4054 | 17.4386 | 17.1506 | 16.3042 | 14.4908 | 58.4598 | 25.2685 | 29.4402 | 19.5969 | 17.9778 | 37.0109 | 21.845 | 15.8382 | 15.5406 | 15.5885 | 14.2978 | 15.3496 | 17.9872 |  |  |  | 54.494 | 188.4058 | 150.1366 | 104.7707 | 0.80336 | 0.23377 | 55.0869 |  |  | 11.5303 |  |  | 16.8945 | 17.0406 | 27.596 | 16.3161 | 16.0589 | 20.1296 | 171.641 | 213.8778 | 142.0243 | 145.4934 | 114.2549 |  | 59.0482 | 120.0831 | 59.2501 | 111.316 | 93.0194 | 155.6113 |  | 93.4078 |  |  | 17.0614 | 20.6789 | 63.9629 | [6 empty] | 93.485 |  |  | 45.7864 |  |  | 20.7053 | 80.9885 | 238.1323 | 10.612 | 75.5973 | 155.4341 | 12.779 | 70.1195 | 168.9718 | 28.583 | 132.8835 | 13.6998 | 124.1168 | 15.4756 | 131.2052 | 11.9184 | 75.3677 | 144.745 | 31.5906 | 70.3325 | 189.514 | 13.8035 | 61.0151 | 167.3355 | 15.6094 | 120.502 | 27.4214 | 131.5407 | 17.5544 | 140.1326 | 1.5321 | 18.8205 | 1.8054 | 0.088914 | -38.3204 | 3.1234 | 315.96 | 49.24 | -1.1854 | -0.55164 | 0.13673 | -0.41415 | 0.49023 | 0.41019 | 0.63727 | -0.843 | -0.99761 | 0.51108 | -1.8585 | -0.41453 | -0.993 | -0.74315
42810.4467 | 580 | 18.3719 | 18.4807 | 18.4795 | 18.4775 | 17.7873 | 16.384 | 14.4348 | 16.583 | 17.0911 | 17.1791 | 17.1859 | 16.7041 | 15.7224 | 14.3525 | 14.7125 | 14.7805 | 15.4656 | 13.2379 | 13.8449 | 17.4246 |  |  |  | 16.5414 | 16.4544 | 23.3587 | 170.5066 | 156.9425 | 190.658 | 17.012 | 16.4743 | 20.4852 | 16.7138 | 16.4506 | 21.598 | 65.4227 | 177.1943 |  | 101.0793 | 150.4072 | 146.3342 | 126.4421 |  | 7.122 | 8.2484 | 7.0097 | 8.3141 | 8.8465 | 12.9125 | 106.2627 | 4.4544 | 7.5729 | 4.4368 | 9.0574 | 8.8816 | 41.9668 | 46.4801 | 42.6013 | 14.333 |  |  | -0.69238 | 0.24979 | 0.12342 | -0.13142 | -0.039264 | -0.0366 | 0.50654 | 1.0768 | 0.061898 | -0.61426 | 0.091294 | -0.00057169 | -0.00057826 | 1.0467 | 15.9647 | 16.6391 | 17.1644 | 17.4955 | 17.4337 | 16.376 | 14.7195 | 16.7704 | 17.1059 | 17.4022 | 17.4385 | 17.1501 | 16.3019 | 14.4922 | 57.775 | 25.6231 | 29.2561 | 20.3709 | 18.4641 | 37.1186 | 21.8675 | 15.8414 | 15.5437 | 15.5921 | 14.3087 | 15.3614 | 18.0122 |  |  |  | 54.717 | 188.6359 | 150.3654 | 104.5316 | 0.57523 | 0.033524 | 55.2814 |  |  | 11.5387 |  |  | 16.8972 | 17.0501 | 27.6504 | 16.3174 | 16.067 | 20.1558 | 171.9735 | 213.5317 | 142.2276 | 145.622 | 114.8004 |  | 59.3005 | 121.0189 | 59.4291 | 111.7389 | 93.4859 | 154.9267 |  | 93.6686 |  |  | 17.066 | 20.7239 | 64.6147 | [6 empty] | 95.1916 |  |  | 45.756 |  |  | 20.7665 | 80.8066 | 238.4332 | 10.5905 | 75.7729 | 155.7549 | 12.8276 | 70.3469 | 169.358 | 28.6256 | 132.9164 | 13.7257 | 124.3344 | 15.4745 | 131.3818 | 11.8811 | 75.2626 | 144.986 | 31.6963 | 70.4424 | 189.4696 | 13.8303 | 61.2652 | 167.7441 | 15.6009 | 120.848 | 27.4975 | 131.7499 | 17.5441 | 140.3878 | 1.6991 | 18.8196 | 1.8053 | 0.086663 | -38.255 | 3.1234 | 295.31 | 48.75 | -1.2488 | 0.58427 | 0.41069 | -0.4238 | -0.23356 | -0.2255 | 0.83889 | -0.84905 | -1.0171 | 0.5175 | -1.7697 | -0.39144 | -0.94992 | -0.72854
42810.4468 | 581 | 18.3646 | 18.4776 | 18.473 | 18.4766 | 17.7826 | 16.3759 | 14.4246 | 16.579 | 17.0836 | 17.181 | 17.1791 | 16.6972 | 15.718 | 14.3464 | 14.7014 | 14.7818 | 15.468 | 13.2327 | 13.8437 | 17.4389 |  |  |  | 16.5374 | 16.4617 | 23.3943 | 170.7014 | 157.0998 | 190.2978 | 17.0153 | 16.4721 | 20.5197 | 16.7148 | 16.454 | 21.6339 | 65.6418 | 177.6667 |  | 101.3597 | 150.6856 | 146.5692 | 127.4427 |  | 7.1286 | 8.2608 | 7.0164 | 8.3198 | 8.8614 | 12.9084 | 106.9403 | 4.5247 | 7.5767 | 4.3479 | 9.0639 | 8.8835 | 41.9544 | 46.4964 | 42.6063 | 14.3304 |  |  | -0.54782 | -0.000569 | 0.030764 | -0.086082 | 0.13159 | 0.026484 | 0.31203 | 0.33102 | -0.52521 | -0.54733 | 0.15071 | -0.00058647 | -0.00060126 | 1.0606 | 15.9669 | 16.6313 | 17.1664 | 17.4887 | 17.4316 | 16.3794 | 14.7114 | 16.7692 | 17.109 | 17.399 | 17.4376 | 17.1466 | 16.3041 | 14.4908 | 56.5526 | 25.5332 | 29.5115 | 21.0635 | 18.8234 | 37.2013 | 21.8808 | 15.8398 | 15.5459 | 15.5971 | 14.3029 | 15.366 | 18.043 |  |  |  | 54.9172 | 188.7772 | 150.4282 | 103.7479 | 0.50635 | 0.53696 | 55.2311 |  |  | 11.5549 |  |  | 16.8997 | 17.0673 | 27.7221 | 16.3212 | 16.0741 | 20.1894 | 172.3718 | 213.1372 | 142.4525 | 145.9127 | 114.9548 |  | 59.6048 | 121.0049 | 59.6332 | 108.3654 | 94.024 | 154.878 |  | 93.9626 |  |  | 17.0373 | 20.7407 | 65.3635 | [6 empty] | 95.1654 |  |  | 45.9242 |  |  | 20.8223 | 80.7423 | 238.6372 | 10.6044 | 76.0067 | 156.3262 | 12.8859 | 70.5637 | 169.6397 | 28.6628 | 133.0972 | 13.7745 | 124.6522 | 15.4847 | 131.571 | 11.8459 | 75.4407 | 144.9643 | 31.7702 | 70.5758 | 189.7395 | 13.8493 | 61.4386 | 168.2342 | 15.638 | 121.09 | 27.545 | 131.9913 | 17.57 | 140.5874 | 1.9196 | 18.8218 | 1.8072 | 0.08819 | -38.237 | 3.1234 | 312.51 | 50.11 | -1.1104 | -0.027886 | 0.20505 | -0.343 | 0.42757 | 0.19182 | 0.65841 | -0.84235 | -1.0094 | 0.63218 | -1.6241 | -0.41826 | -0.9697 | -0.69961
42810.4468 | 582 | 18.3643 | 18.4668 | 18.4686 | 18.4791 | 17.7782 | 16.3783 | 14.4285 | 16.5859 | 17.093 | 17.1821 | 17.1811 | 16.6971 | 15.7189 | 14.3555 | 14.6991 | 14.7678 | 15.4662 | 13.2288 | 13.8368 | 17.4539 |  |  |  | 16.5377 | 16.4666 | 23.4312 | 170.7812 | 157.324 | 189.539 | 17.0079 | 16.4742 | 20.5442 | 16.7184 | 16.45 | 21.6651 | 65.8847 | 178.2202 |  | 101.6334 | 150.8941 | 146.8969 | 128.3053 |  | 7.1404 | 8.2851 | 7.0375 | 8.3382 | 8.8988 | 12.9076 | 107.8438 | 4.5844 | 7.5962 | 4.2965 | 9.0843 | 8.8857 | 41.945 | 46.5105 | 42.6033 | 14.3187 |  |  | -0.48013 | 0.15779 | 0.065592 | -0.21488 | 0.042876 | 0.18156 | 0.051812 | 0.42565 | 0.2203 | -0.26242 | 0.2588 | -0.00055198 | -0.00056019 | 1.0106 | 15.9761 | 16.6328 | 17.1774 | 17.4996 | 17.4317 | 16.3823 | 14.7073 | 16.7652 | 17.1073 | 17.403 | 17.4392 | 17.1409 | 16.3001 | 14.4936 | 55.4788 | 25.4738 | 32.05 | 22.0166 | 19.4693 | 37.2941 | 21.9314 | 15.8414 | 15.5491 | 15.6061 | 14.3088 | 15.3822 | 18.0617 |  |  |  | 55.1246 | 189.0133 | 150.7825 | 103.8172 | 0.95895 | 0.30811 | 55.2681 |  |  | 11.5551 |  |  | 16.8931 | 17.066 | 27.7688 | 16.3173 | 16.072 | 20.2035 | 172.6103 | 212.6221 | 142.6877 | 146.1244 | 114.6177 |  | 59.8944 | 120.4633 | 59.8131 | 104.7605 | 94.5156 | 156.6556 |  | 94.2187 |  |  | 17.0128 | 20.7513 | 65.7599 | [6 empty] | 95.477 |  |  | 46.1024 |  |  | 20.8512 | 81.0696 | 237.9294 | 10.6173 | 76.339 | 156.6895 | 12.9175 | 70.7485 | 169.9884 | 28.709 | 133.3523 | 13.8306 | 124.8379 | 15.5013 | 131.9741 | 11.8802 | 75.8059 | 144.8557 | 31.821 | 70.7996 | 190.6454 | 13.8695 | 61.4983 | 168.5184 | 15.6768 | 121.2514 | 27.6467 | 132.4071 | 17.6034 | 140.9039 | 1.9069 | 18.8228 | 1.8086 | 0.089232 | -38.3398 | 3.1233 | 321.83 | 48.99 | -1.0387 | 0.46441 | 0.29942 | -0.54194 | 0.24406 | 0.50223 | 0.26829 | -0.82251 | -0.98783 | 0.7515 | -1.4939 | -0.69441 | -0.98477 | -0.69411
42810.4468 | 583 | 18.3583 | 18.4723 | 18.4601 | 18.4688 | 17.7783 | 16.3697 | 14.4205 | 16.5794 | 17.0813 | 17.1755 | 17.1737 | 16.6904 | 15.7105 | 14.3483 | 14.7015 | 14.7738 | 15.4745 | 13.2343 | 13.8459 | 17.4787 |  |  |  | 16.5412 | 16.4651 | 23.4699 | 170.9259 | 157.7596 | 189.3665 | 17.0169 | 16.4821 | 20.5757 | 16.7176 | 16.4662 | 21.6972 | 66.1276 | 178.3759 |  | 101.8975 | 151.0669 | 147.2705 | 127.2592 |  | 7.1364 | 8.2955 | 7.036 | 8.3522 | 8.9031 | 12.9192 | 108.9932 | 4.5504 | 7.5997 | 4.2542 | 9.0921 | 8.9003 | 41.944 | 46.521 | 42.6188 | 14.3176 |  |  | -0.64638 | 0.29579 | 0.043904 | -0.3923 | 0.096104 | 0.034368 | 0.13264 | 0.4355 | 0.53108 | -0.6088 | 0.17892 | -0.00053226 | -0.00056676 | 1.0122 | 15.9717 | 16.6329 | 17.168 | 17.4917 | 17.4338 | 16.3781 | 14.704 | 16.7639 | 17.1147 | 17.399 | 17.4344 | 17.1395 | 16.3015 | 14.4909 | 56.4267 | 26.5425 | 33.5458 | 22.4823 | 20.3937 | 37.4382 | 21.9945 | 15.842 | 15.5412 | 15.6027 | 14.3003 | 15.3809 | 18.0801 |  |  |  | 55.3261 | 189.3934 | 151.5223 | 104.4609 | 0.83273 | 0.43721 | 55.5372 |  |  | 11.5647 |  |  | 16.8959 | 17.0702 | 27.8232 | 16.3205 | 16.0768 | 20.2312 | 172.8528 | 212.5577 | 142.9395 | 146.3337 | 114.3487 |  | 60.1259 | 120.0448 | 59.983 | 104.5249 | 94.9628 | 158.8188 |  | 94.4861 |  |  | 17.0611 | 20.7607 | 64.9967 | [6 empty] | 96.8783 |  |  | 46.2685 |  |  | 20.9011 | 81.1819 | 237.8691 | 10.6608 | 76.0828 | 156.8904 | 12.9352 | 70.9566 | 170.0355 | 28.7524 | 133.6173 | 13.8889 | 124.8528 | 15.5455 | 132.6816 | 11.9075 | 76.0751 | 144.8788 | 31.8755 | 71.0985 | 191.3107 | 13.899 | 61.6325 | 168.9698 | 15.6886 | 121.3614 | 27.7664 | 132.7171 | 17.6417 | 141.195 | 1.5824 | 18.8251 | 1.8095 | 0.088233 | -38.3435 | 3.1234 | 311.12 | 49.19 | -1.205 | 0.63585 | 0.24497 | -0.73227 | 0.3654 | 0.21851 | 0.42928 | -0.80667 | -0.97006 | 0.77552 | -1.5822 | -0.85323 | -0.94682 | -0.70477
42810.4468 | 584 | 18.369 | 18.479 | 18.4658 | 18.4802 | 17.7858 | 16.3769 | 14.4266 | 16.5895 | 17.0853 | 17.1797 | 17.1837 | 16.6991 | 15.7205 | 14.3503 | 14.705 | 14.7787 | 15.4773 | 13.2359 | 13.8578 | 17.4987 |  |  |  | 16.5418 | 16.4683 | 23.5122 | 171.0963 | 158.4069 | 189.821 | 17.0142 | 16.477 | 20.5826 | 16.7071 | 16.4524 | 21.715 | 66.3703 | 177.8795 |  | 102.1382 | 151.2142 | 147.5416 | 127.9631 |  | 7.1277 | 8.2906 | 7.0214 | 8.3596 | 8.9102 | 13.2069 | 110.2503 | 4.5999 | 7.6045 | 4.2778 | 9.0996 | 8.9001 | 41.9417 | 46.4968 | 42.6249 | 14.305 |  |  | -0.38419 | 0.29645 | 0.087932 | -0.34827 | 0.12962 | 0.18945 | 0.056412 | 0.58664 | -0.4606 | 0.20942 | 0.089903 | -0.00053555 | -0.00056183 | 1.0267 | 15.9719 | 16.6336 | 17.171 | 17.4814 | 17.4287 | 16.3754 | 14.7129 | 16.7675 | 17.1019 | 17.4021 | 17.4341 | 17.1396 | 16.2963 | 14.496 | 56.492 | 26.6305 | 34.6155 | 22.697 | 20.0801 | 37.5482 | 22.0564 | 15.8356 | 15.5471 | 15.6018 | 14.2958 | 15.3857 | 18.0935 |  |  |  | 55.5292 | 189.6149 | 151.7452 | 105.2209 | 0.87346 | -0.04966 | 55.7176 |  |  | 11.5751 |  |  | 16.8928 | 17.0763 | 27.8733 | 16.3148 | 16.0752 | 20.2578 | 173.1863 | 212.8854 | 143.281 | 146.6099 | 112.9227 |  | 60.3629 | 119.6056 | 60.1954 | 108.862 | 95.5482 | 159.9293 |  | 94.7805 |  |  | 17.1074 | 20.7854 | 64.5347 | [6 empty] | 96.3228 |  |  | 46.4398 |  |  | 20.9162 | 81.4342 | 238.1573 | 10.7032 | 75.916 | 156.7777 | 12.9639 | 71.342 | 170.1004 | 28.8016 | 133.9375 | 13.9417 | 125.0096 | 15.5711 | 133.0042 | 11.8911 | 76.4728 | 144.9877 | 31.9827 | 71.4637 | 191.8293 | 13.9345 | 61.7334 | 169.5534 | 15.6751 | 121.4316 | 27.8545 | 132.9415 | 17.6857 | 141.3728 | 1.7035 | 18.8246 | 1.8102 | 0.08662 | -38.2922 | 3.1234 | 313.71 | 49.85 | -0.92943 | 0.63655 | 0.34668 | -0.68995 | 0.42457 | 0.51329 | 0.2801 | -0.75848 | -0.95018 | 0.67795 | -1.5765 | -0.96484 | -0.95748 | -0.71861
42810.4468 | 585 | 18.3675 | 18.4729 | 18.4719 | 18.4818 | 17.7875 | 16.3775 | 14.4225 | 16.5815 | 17.0836 | 17.1862 | 17.1908 | 16.6999 | 15.7207 | 14.3472 | 14.7089 | 14.7752 | 15.4821 | 13.2341 | 13.8641 | 17.5177 |  |  |  | 16.5364 | 16.4779 | 23.5494 | 171.347 | 158.8346 | 190.5989 | 17.0179 | 16.4808 | 20.6093 | 16.7126 | 16.4558 | 21.7519 | 66.6348 | 177.2915 |  | 102.3774 | 151.3626 | 147.7768 | 130.5036 |  | 7.1269 | 8.3004 | 7.0271 | 8.3771 | 8.9248 | 13.3523 | 111.0407 | 4.6847 | 7.6089 | 4.3345 | 9.1154 | 8.9064 | 41.9448 | 46.4759 | 42.6417 | 14.3048 |  |  | -0.58527 | -0.013053 | -0.021804 | -0.34039 | 0.39838 | 0.06788 | 0.18718 | 0.23508 | -0.51178 | 0.11753 | 0.11077 | -0.00056348 | -0.00053391 | 1.0694 | 15.9729 | 16.6337 | 17.1653 | 17.4867 | 17.4333 | 16.3723 | 14.7122 | 16.7694 | 17.107 | 17.4001 | 17.4379 | 17.1411 | 16.3049 | 14.4936 | 55.7091 | 27.2923 | 33.7706 | 22.7741 | 20.6047 | 37.6606 | 22.0949 | 15.8339 | 15.5401 | 15.5941 | 14.2888 | 15.384 | 18.1041 |  |  |  | 55.7488 | 190.4816 | 153.0177 | 105.8898 | 1.0037 | 0.13271 | 55.7854 |  |  | 11.5904 |  |  | 16.8971 | 17.0836 | 27.925 | 16.3129 | 16.0796 | 20.2838 | 173.5322 | 213.5156 | 143.541 | 146.8154 | 111.6892 |  | 60.572 | 119.3819 | 60.3721 | 108.6004 | 96.1046 | 158.8733 |  | 95.0056 |  |  | 17.1468 | 20.8484 | 64.373 | [6 empty] | 94.3445 |  |  | 46.5504 |  |  | 20.9333 | 81.9526 | 238.2619 | 10.7064 | 76.244 | 156.7797 | 12.995 | 71.5287 | 170.207 | 28.8556 | 134.3346 | 13.9783 | 125.2722 | 15.5918 | 133.1063 | 11.8669 | 77.134 | 145.105 | 32.1426 | 71.9104 | 192.2188 | 13.9808 | 62.0525 | 169.8703 | 15.686 | 121.4664 | 27.9592 | 133.096 | 17.7233 | 141.5853 | 1.4235 | 18.8257 | 1.8136 | 0.089087 | -38.2859 | 3.1234 | 338.25 | 48.9 | -1.1481 | -0.13357 | -0.17264 | -0.68211 | 0.74452 | 0.30733 | 0.51034 | -0.71665 | -0.93757 | 0.70701 | -1.4763 | -0.86646 | -1.0183 | -0.72932
42810.4468 | 586 | 18.3704 | 18.4742 | 18.4724 | 18.4797 | 17.7883 | 16.3757 | 14.426 | 16.5841 | 17.0841 | 17.185 | 17.1925 | 16.7025 | 15.7172 | 14.3473 | 14.7012 | 14.7753 | 15.4837 | 13.2323 | 13.871 | 17.5337 |  |  |  | 16.5402 | 16.4749 | 23.5881 | 171.7365 | 159.2556 | 192.6694 | 17.0163 | 16.4947 | 20.6495 | 16.7171 | 16.4664 | 21.7831 | 66.8936 | 176.7236 |  | 102.5997 | 151.4804 | 148.0267 | 132.0897 |  | 7.1238 | 8.3026 | 7.0319 | 8.3884 | 8.9453 | 13.3035 | 110.2689 | 4.7512 | 7.6287 | 4.3799 | 9.1356 | 8.9055 | 41.9318 | 46.4656 | 42.6605 | 14.3046 |  |  | -0.65033 | -0.012397 | -0.011948 | -0.55001 | 0.39246 | 0.44506 | 0.015672 | 0.71544 | 0.41062 | -0.008145 | 0.51472 | -0.0005914 | -0.00054705 | 1.0534 | 15.9842 | 16.6397 | 17.1728 | 17.4943 | 17.4405 | 16.373 | 14.7125 | 16.7706 | 17.1096 | 17.4059 | 17.4393 | 17.1359 | 16.3002 | 14.4912 | 56.2535 | 27.5027 | 34.0331 | 22.3 | 20.3073 | 37.8004 | 22.1436 | 15.8399 | 15.5413 | 15.6037 | 14.2961 | 15.4009 | 18.1441 |  |  |  | 55.9689 | 190.8492 | 153.2114 | 105.562 | 1.525 | 0.34594 | 56.1511 |  |  | 11.5965 |  |  | 16.8945 | 17.0881 | 27.985 | 16.3178 | 16.081 | 20.311 | 174.1312 | 214.0511 | 143.7097 | 147.0119 | 110.6244 |  | 60.7637 | 119.4709 | 60.5544 | 104.0827 | 96.5647 | 158.7732 |  | 95.2442 |  |  | 17.1428 | 20.905 | 64.3925 | [6 empty] | 94.1921 |  |  | 46.7315 |  |  | 20.9783 | 82.2925 | 238.6386 | 10.705 | 76.2956 | 156.79 | 13.0309 | 71.5871 | 170.5349 | 28.9465 | 134.7967 | 13.9698 | 125.4002 | 15.6453 | 133.2222 | 11.8542 | 77.8898 | 145.0666 | 32.3026 | 72.339 | 192.3257 | 14.0424 | 62.4406 | 169.8797 | 15.7019 | 121.6245 | 28.1062 | 133.2997 | 17.7694 | 141.7944 | 1.5036 | 18.824 | 1.8163 | 0.089297 | -38.3079 | 3.1235 | 350.52 | 48.94 | -1.2129 | -0.13018 | -0.1278 | -0.86707 | 0.73891 | 0.78687 | 0.14766 | -0.68013 | -0.93345 | 0.85054 | -1.5203 | -0.88994 | -1.0529 | -0.71232
42810.4468 | 587 | 18.3749 | 18.4803 | 18.476 | 18.4864 | 17.7926 | 16.3762 | 14.4236 | 16.5886 | 17.0859 | 17.1871 | 17.1888 | 16.7093 | 15.7206 | 14.3566 | 14.7141 | 14.7796 | 15.4771 | 13.2431 | 13.8695 | 17.5557 |  |  |  | 16.535 | 16.4777 | 23.6331 | 172.2626 | 159.608 | 193.8017 | 17.0242 | 16.5001 | 20.6732 | 16.7162 | 16.4772 | 21.8192 | 67.1962 | 177.0083 |  | 102.8658 | 151.581 | 148.2676 | 132.2994 |  | 7.107 | 8.2978 | 7.0184 | 8.3991 | 8.9475 | 13.3106 | 110.3014 | 4.6257 | 7.6321 | 4.4351 | 9.1543 | 8.9127 | 41.9243 | 46.4646 | 42.6804 | 14.3272 |  |  | -0.70158 | 0.081571 | 0.088588 | 0.074254 | 0.043532 | 0.15528 | 0.21675 | 0.47756 | -0.40806 | 0.16389 | 0.020557 | -0.0005684 | -0.00052733 | 0.97959 | 15.9811 | 16.6358 | 17.1686 | 17.4956 | 17.4374 | 16.3809 | 14.7129 | 16.7674 | 17.108 | 17.4043 | 17.4361 | 17.1465 | 16.3063 | 14.4917 | 58.7653 | 28.9133 | 35.6973 | 22.1672 | 20.1344 | 37.9876 | 22.2179 | 15.8386 | 15.5515 | 15.6122 | 14.3036 | 15.4135 | 18.1747 |  |  |  | 56.196 | 190.7647 | 153.2294 | 105.1703 | 0.56044 | 0.581 | 56.2264 |  |  | 11.6015 |  |  | 16.8883 | 17.0932 | 28.0276 | 16.3109 | 16.0772 | 20.3303 | 174.4552 | 214.9976 | 144.04 | 147.177 | 109.8131 |  | 60.9906 | 119.8316 | 60.7541 | 100.7117 | 97.1756 | 159.5019 |  | 95.5483 |  |  | 17.0913 | 20.9402 | 64.388 | [6 empty] | 93.9307 |  |  | 46.9392 |  |  | 21.0256 | 82.4586 | 239.3774 | 10.7261 | 76.723 | 156.7143 | 13.0638 | 71.6622 | 171.2396 | 29.0318 | 135.2336 | 13.9729 | 125.475 | 15.6885 | 133.4967 | 11.8784 | 78.2492 | 145.1864 | 32.4763 | 72.8612 | 192.529 | 14.0815 | 62.5844 | 170.1077 | 15.7422 | 121.8644 | 28.2637 | 133.6036 | 17.8543 | 142.2275 | 1.5346 | 18.823 | 1.8172 | 0.087879 | -38.37 | 3.1235 | 360.16 | 50 | -1.2614 | 0.33391 | 0.34798 | 0.31859 | 0.2461 | 0.46478 | 0.54913 | -0.64938 | -0.93624 | 0.96817 | -1.7773 | -1.0662 | -1.0476 | -0.6933
42810.4468 | 588 | 18.3767 | 18.4691 | 18.4789 | 18.4831 | 17.784 | 16.3769 | 14.4224 | 16.5865 | 17.0896 | 17.1844 | 17.1911 | 16.6997 | 15.7174 | 14.3543 | 14.7095 | 14.785 | 15.4767 | 13.2369 | 13.861 | 17.5763 |  |  |  | 16.5305 | 16.4902 | 23.6708 | 172.7944 | 159.789 | 194.676 | 17.0234 | 16.4903 | 20.694 | 16.7203 | 16.4729 | 21.8491 | 67.4577 | 179.1011 |  | 103.1614 | 151.7428 | 148.5398 | 131.6067 |  | 7.1056 | 8.3009 | 7.0217 | 8.4118 | 8.9664 | 13.7235 | 111.5725 | 4.5215 | 7.6409 | 4.4725 | 9.1602 | 8.917 | 41.8905 | 46.4565 | 42.7007 | 14.3518 |  |  | -0.46699 | -0.007141 | 0.04522 | -0.31081 | 0.09216 | 0.14608 | 0.34489 | 0.59518 | -0.19069 | -1.0878 | 0.28503 | -0.0005569 | -0.00057005 | 1.0167 | 15.9762 | 16.6322 | 17.1669 | 17.4846 | 17.4325 | 16.3794 | 14.7138 | 16.7635 | 17.1046 | 17.4021 | 17.4375 | 17.1433 | 16.3005 | 14.4855 | 57.4743 | 27.2521 | 36.0323 | 22.3728 | 20.2882 | 38.0935 | 22.3012 | 15.838 | 15.5495 | 15.6089 | 14.3022 | 15.4148 | 18.1898 |  |  |  | 56.4293 | 190.6159 | 153.2422 | 105.7804 | 1.3488 | 0.10297 | 56.1931 |  |  | 11.6087 |  |  | 16.8851 | 17.0941 | 28.0827 | 16.313 | 16.0824 | 20.3555 | 174.9594 | 215.6156 | 144.3502 | 147.3819 | 110.5531 |  | 61.2007 | 120.1491 | 60.9269 | 101.5866 | 97.954 | 159.7929 |  | 95.8202 |  |  | 17.1287 | 21.0151 | 64.7584 | [6 empty] | 97.3331 |  |  | 47.1252 |  |  | 21.0719 | 82.5574 | 240.9365 | 10.7903 | 77.3483 | 156.9023 | 13.1089 | 71.9796 | 172.0056 | 29.1293 | 135.5727 | 14.0387 | 125.6981 | 15.7362 | 133.9579 | 11.9318 | 78.1263 | 145.3875 | 32.6585 | 73.4075 | 192.5156 | 14.1257 | 63.2067 | 170.699 | 15.7759 | 122.11 | 28.4315 | 133.9064 | 17.9443 | 142.9423 | 1.567 | 18.8224 | 1.8197 | 0.087242 | -38.3479 | 3.1235 | 358.1 | 48.73 | -1.0301 | -0.098798 | 0.24862 | -0.65181 | 0.35833 | 0.45113 | 0.69319 | -0.66231 | -0.93879 | 0.97449 | -1.6213 | -1.0936 | -1.0188 | -0.70187
42810.4469 | 589 | 18.3777 | 18.4731 | 18.4766 | 18.4872 | 17.7843 | 16.3744 | 14.4278 | 16.5901 | 17.0856 | 17.1831 | 17.1874 | 16.7143 | 15.7207 | 14.3585 | 14.7086 | 14.7809 | 15.4797 | 13.2398 | 13.8721 | 17.5887 |  |  |  | 16.531 | 16.4898 | 23.7173 | 173.3102 | 159.9909 | 196.3391 | 17.0279 | 16.5005 | 20.7346 | 16.7246 | 16.486 | 21.8881 | 67.6925 | 182.9933 |  | 103.574 | 151.8595 | 148.8087 | 131.6763 |  | 7.1092 | 8.3103 | 7.0353 | 8.4386 | 9.0044 | 14.263 | 112.6886 | 4.4542 | 7.6483 | 4.4863 | 9.1862 | 8.9174 | 41.8566 | 46.4425 | 42.7203 | 14.3782 |  |  | -0.42888 | 0.16174 | 0.010392 | -0.54409 | 0.1007 | 0.13556 | 0.078756 | 0.75223 | -0.32205 | -1.9142 | 0.13441 | -0.00053719 | -0.00054869 | 1.0599 | 15.9854 | 16.6374 | 17.1615 | 17.4932 | 17.4383 | 16.3835 | 14.7144 | 16.7693 | 17.107 | 17.4033 | 17.4404 | 17.147 | 16.3005 | 14.4911 | 60.1393 | 26.25 | 35.0638 | 22.2455 | 21.0444 | 38.2464 | 22.369 | 15.84 | 15.5486 | 15.6122 | 14.3092 | 15.4191 | 18.2094 |  |  |  | 56.6735 | 190.9222 | 153.632 | 106.6275 | 1.0317 | 0.030325 | 56.4379 |  |  | 11.6142 |  |  | 16.893 | 17.1058 | 28.1341 | 16.32 | 16.0925 | 20.3879 | 175.5224 | 216.5181 | 144.6718 | 147.7799 | 111.5354 |  | 61.3727 | 121.1628 | 61.1267 | 109.0135 | 98.7407 | 160.2608 |  | 96.0474 |  |  | 17.1731 | 21.0695 | 64.7701 | [6 empty] | 102.6469 |  |  | 47.2888 |  |  | 21.1338 | 82.961 | 242.7243 | 10.7876 | 76.9727 | 157.2691 | 13.159 | 72.3388 | 172.8604 | 29.2018 | 135.8274 | 14.0444 | 125.89 | 15.7939 | 134.2399 | 11.9999 | 78.2944 | 145.592 | 32.8666 | 73.6779 | 192.7811 | 14.1573 | 63.8814 | 171.2962 | 15.8153 | 122.3192 | 28.585 | 134.3101 | 17.9785 | 143.1852 | 1.6007 | 18.8213 | 1.8223 | 0.088624 | -38.3568 | 3.1235 | 342.98 | 49.55 | -0.98889 | 0.4702 | 0.11919 | -0.8624 | 0.37492 | 0.435 | 0.33156 | -0.68336 | -0.95971 | 0.79918 | -1.8994 | -0.97809 | -1.0121 | -0.71663
42810.4469 | 590 | 18.3728 | 18.4722 | 18.4803 | 18.4842 | 17.7877 | 16.3742 | 14.4275 | 16.5804 | 17.0834 | 17.1776 | 17.1816 | 16.7024 | 15.7198 | 14.3524 | 14.7177 | 14.7763 | 15.4801 | 13.2407 | 13.8769 | 17.6215 |  |  |  | 16.5415 | 16.4925 | 23.7546 | 173.9305 | 160.602 | 196.6931 | 17.0312 | 16.5011 | 20.7586 | 16.7251 | 16.481 | 21.9121 | 67.9653 | 185.3046 |  | 103.9141 | 152.1133 | 148.9754 | 133.3354 |  | 7.1064 | 8.3189 | 7.033 | 8.4458 | 9.0692 | 14.7863 | 113.8197 | 4.4462 | 7.6501 | 4.4767 | 9.1941 | 8.9259 | 41.8442 | 46.442 | 42.7577 | 14.4163 |  |  | -0.75218 | -0.041969 | 0.011052 | -0.33053 | 0.2249 | 0.016624 | 0.30218 | 0.8278 | -0.2804 | 0.45908 | 0.23515 | -0.0005454 | -0.0005684 | 1.0625 | 15.9928 | 16.6374 | 17.1653 | 17.4886 | 17.4362 | 16.3772 | 14.7082 | 16.7746 | 17.1105 | 17.4088 | 17.4438 | 17.1456 | 16.3053 | 14.4936 | 60.0659 | 25.1081 | 34.2018 | 23.0697 | 22.1974 | 38.3644 | 22.4102 | 15.8326 | 15.5477 | 15.6091 | 14.3028 | 15.4312 | 18.2335 |  |  |  | 56.9238 | 190.5051 | 153.4971 | 107.4175 | 0.8455 | 0.059496 | 56.5663 |  |  | 11.6288 |  |  | 16.8974 | 17.1198 | 28.1966 | 16.3251 | 16.0966 | 20.4144 | 175.8672 | 217.5624 | 144.9722 | 148.051 | 111.4806 |  | 61.5567 | 122.2144 | 61.3369 | 117.009 | 99.4841 | 161.7508 |  | 96.3645 |  |  | 17.2171 | 21.0942 | 64.845 | [6 empty] | 105.424 |  |  | 47.5679 |  |  | 21.1924 | 83.5372 | 243.9461 | 10.7283 | 76.5626 | 157.8814 | 13.2065 | 72.4581 | 173.2475 | 29.285 | 136.1108 | 14.0698 | 126.0883 | 15.8473 | 134.513 | 12.0601 | 78.5852 | 145.8657 | 33.1228 | 74.1031 | 192.8442 | 14.2064 | 63.8668 | 172.0323 | 15.8656 | 122.5879 | 28.7608 | 134.6249 | 18.0407 | 143.2665 | 1.5487 | 18.8208 | 1.8243 | 0.087879 | -38.2889 | 3.1235 | 317.28 | 49.77 | -1.3101 | -0.23952 | 0.12291 | -0.67218 | 0.5608 | 0.15247 | 0.65005 | -0.67517 | -0.9813 | 0.60643 | -1.8773 | -0.87749 | -1.0481 | -0.72959
42810.4469 | 591 | 18.3822 | 18.4715 | 18.4803 | 18.4803 | 17.7804 | 16.3731 | 14.4283 | 16.5771 | 17.0813 | 17.1715 | 17.1859 | 16.7 | 15.7196 | 14.3498 | 14.7157 | 14.7824 | 15.4766 | 13.2316 | 13.8615 | 17.6362 |  |  |  | 16.5389 | 16.4893 | 23.797 | 174.3678 | 161.1021 | 196.7658 | 17.0334 | 16.511 | 20.7822 | 16.7324 | 16.4919 | 21.9444 | 68.3033 | 188.2694 |  | 104.2593 | 152.6382 | 149.2721 | 136.0773 |  | 7.127 | 8.3352 | 7.0529 | 8.4577 | 9.1906 | 15.1228 | 113.8574 | 4.5408 | 7.6512 | 4.4699 | 9.2106 | 8.9226 | 41.83 | 46.4506 | 42.7856 | 14.4485 |  |  | -0.68712 | 0.039515 | -0.073716 | -0.040742 | 0.1835 | 0.15462 | 0.4244 | 0.52224 | -0.045716 | 0.20606 | 0.040824 | -0.00054048 | -0.00061112 | 1.0131 | 15.9921 | 16.6324 | 17.1686 | 17.4797 | 17.4369 | 16.3683 | 14.7117 | 16.7711 | 17.1031 | 17.4059 | 17.4448 | 17.1501 | 16.307 | 14.4873 | 58.7191 | 25.1385 | 34.4714 | 23.3328 | 22.5116 | 38.479 | 22.4711 | 15.8298 | 15.5535 | 15.6112 | 14.3026 | 15.4331 | 18.2588 |  |  |  | 57.1593 | 189.5616 | 153.3443 | 107.8163 | 0.56713 | 0.45942 | 56.4251 |  |  | 11.637 |  |  | 16.8966 | 17.1176 | 28.2441 | 16.32 | 16.0994 | 20.4381 | 176.1065 | 218.1892 | 145.4775 | 148.6011 | 112.3186 |  | 61.769 | 123.3116 | 61.5558 | 127.6075 | 100.2665 | 163.7631 |  | 96.7671 |  |  | 17.2857 | 21.1318 | 65.0537 | [6 empty] | 109.6804 |  |  | 47.7439 |  |  | 21.251 | 83.748 | 246.0978 | 10.7093 | 76.9507 | 158.7523 | 13.2156 | 72.5668 | 174.3394 | 29.36 | 136.5995 | 14.0503 | 126.1267 | 15.8973 | 134.9015 | 12.1084 | 78.6145 | 146.086 | 33.3174 | 74.5152 | 193.0808 | 14.2505 | 64.2028 | 173.0824 | 15.9154 | 123.0005 | 28.8946 | 134.6506 | 18.0831 | 143.7166 | 1.7005 | 18.8199 | 1.8251 | 0.085758 | -38.3568 | 3.1234 | 308.11 | 49.22 | -1.2523 | 0.23242 | -0.31745 | -0.236 | 0.50686 | 0.46527 | 0.77082 | -0.69074 | -1.0038 | 0.34297 | -1.7142 | -0.90033 | -1.1119 | -0.7322
42810.4469 | 592 | 18.3847 | 18.4743 | 18.4801 | 18.4853 | 17.7878 | 16.3756 | 14.4332 | 16.5778 | 17.0855 | 17.1764 | 17.1883 | 16.6987 | 15.7219 | 14.354 | 14.7228 | 14.7935 | 15.4885 | 13.248 | 13.8881 | 17.6714 |  |  |  | 16.55 | 16.5114 | 23.8529 | 174.7455 | 161.4714 | 195.2959 | 17.0313 | 16.5124 | 20.8057 | 16.7309 | 16.4981 | 21.9765 | 68.657 | 192.6555 |  | 104.7211 | 153.1243 | 150.0309 | 137.6054 |  | 7.1463 | 8.3635 | 7.0709 | 8.4658 | 9.2426 | 15.1105 | 113.1831 | 4.6963 | 7.6538 | 4.4506 | 9.2143 | 8.9285 | 41.8176 | 46.4611 | 42.8105 | 14.4813 |  |  | -0.63784 | 0.11771 | 0.046536 | -0.11828 | 0.2709 | -0.28499 | 0.37906 | 0.64447 | -0.76768 | -0.31781 | 0.27509 | -0.00055362 | -0.00057005 | 0.99403 | 15.9905 | 16.6331 | 17.1625 | 17.491 | 17.4299 | 16.3694 | 14.6985 | 16.7753 | 17.1102 | 17.3994 | 17.4348 | 17.1451 | 16.2914 | 14.4912 | 56.8334 | 24.9278 | 35.6991 | 24.6561 | 22.5755 | 38.5704 | 22.5286 | 15.8363 | 15.545 | 15.6196 | 14.3035 | 15.4392 | 18.2874 |  |  |  | 57.3874 | 189.571 | 153.5348 | 107.9576 | 0.73062 | 0.49913 | 56.554 |  |  | 11.6444 |  |  | 16.9015 | 17.1326 | 28.3068 | 16.3297 | 16.1086 | 20.4756 | 176.2133 | 219.0799 | 145.9722 | 149.2366 | 113.7115 |  | 61.9858 | 124.6309 | 61.7726 | 128.1843 | 100.7974 | 164.0467 |  | 97.0575 |  |  | 17.3342 | 21.2273 | 65.5143 | [6 empty] | 108.6449 |  |  | 47.8436 |  |  | 21.3112 | 84.0861 | 246.9506 | 10.7438 | 77.4151 | 159.3163 | 13.2457 | 73.1038 | 175.1529 | 29.4299 | 137.0615 | 14.0584 | 126.573 | 15.9353 | 135.0308 | 12.1385 | 78.9234 | 146.8171 | 33.5 | 75.0218 | 193.0319 | 14.3096 | 64.6363 | 173.7675 | 15.9779 | 123.5835 | 29.0189 | 134.9743 | 18.1455 | 144.3464 | 1.5144 | 18.8158 | 1.8288 | 0.087206 | -38.2903 | 3.1234 | 313.21 | 50.14 | -1.2046 | 0.40117 | 0.25224 | -0.40214 | 0.61583 | -0.63165 | 0.72847 | -0.72156 | -1.0326 | 0.34798 | -1.4939 | -1.03 | -1.1413 | -0.72792
42810.4469 | 593 | 18.3804 | 18.4766 | 18.4748 | 18.4822 | 17.788 | 16.378 | 14.4301 | 16.5774 | 17.0875 | 17.1757 | 17.1859 | 16.7016 | 15.7224 | 14.3582 | 14.728 | 14.8021 | 15.4983 | 13.252 | 13.8911 | 17.6936 |  |  |  | 16.5547 | 16.5161 | 23.8966 | 175.027 | 161.4543 | 195.4803 | 17.0293 | 16.5124 | 20.8262 | 16.7238 | 16.4977 | 22.0026 | 69.0174 | 196.5386 |  | 105.1811 | 153.561 | 150.7578 | 139.977 |  | 7.1725 | 8.394 | 7.0788 | 8.4577 | 9.2887 | 15.0595 | 113.0172 | 4.6779 | 7.6699 | 4.503 | 9.2388 | 8.9351 | 41.8199 | 46.4724 | 42.8287 | 14.5094 |  |  | -0.65427 | 0.14728 | 0.10962 | 0.10514 | 0.22621 | -0.49461 | 0.16221 | 0.74632 | -0.85292 | -0.53265 | 0.26277 | -0.00055855 | -0.00058483 | 1.0372 | 15.9876 | 16.6306 | 17.1613 | 17.4873 | 17.4264 | 16.3722 | 14.7065 | 16.7606 | 17.1095 | 17.3983 | 17.4323 | 17.1384 | 16.302 | 14.4927 | 55.0219 | 24.7444 | 37.4673 | 26.0833 | 23.6748 | 38.6296 | 22.606 | 15.8363 | 15.5396 | 15.6105 | 14.2995 | 15.452 | 18.3015 |  |  |  | 57.6076 | 189.581 | 153.6333 | 108.1316 | -0.15919 | -0.042132 | 56.9575 |  |  | 11.643 |  |  | 16.8926 | 17.1356 | 28.3609 | 16.3211 | 16.1075 | 20.4923 | 176.2515 | 220.1767 | 146.3977 | 149.6143 | 114.8454 |  | 62.1912 | 126.1018 | 61.9626 | 122.2273 | 101.1387 | 163.8806 |  | 97.3687 |  |  | 17.379 | 21.3275 | 66.4155 | [6 empty] | 106.6113 |  |  | 47.9834 |  |  | 21.367 | 84.7605 | 248.8946 | 10.7769 | 77.9414 | 160.086 | 13.2521 | 73.6854 | 175.6769 | 29.5616 | 137.6194 | 14.0569 | 126.9899 | 15.9863 | 135.3337 | 12.1966 | 79.3407 | 147.4655 | 33.6892 | 75.4396 | 192.7308 | 14.3477 | 64.7854 | 174.8038 | 16.0665 | 124.1672 | 29.1482 | 135.4765 | 18.2269 | 144.9514 | 1.5733 | 18.8132 | 1.8311 | 0.087133 | -38.2789 | 3.1234 | 301.42 | 49.03 | -1.2203 | 0.44876 | 0.38715 | 0.37916 | 0.5627 | -0.83206 | 0.47649 | -0.7456 | -1.0666 | 0.52699 | -1.2856 | -1.2174 | -1.1939 | -0.72483
42810.4469 | 594 | 18.3929 | 18.4799 | 18.4792 | 18.4841 | 17.7947 | 16.387 | 14.4333 | 16.5861 | 17.0871 | 17.1778 | 17.1883 | 16.7079 | 15.7253 | 14.3562 | 14.7264 | 14.7936 | 15.4983 | 13.2513 | 13.8921 | 17.7061 |  |  |  | 16.5525 | 16.5204 | 23.9373 | 175.3991 | 161.2852 | 195.8023 | 17.0258 | 16.5045 | 20.8475 | 16.718 | 16.4974 | 22.0345 | 69.3718 | 198.6135 |  | 105.5849 | 154.06 | 151.2632 | 140.97 |  | 7.2042 | 8.4027 | 7.066 | 8.4395 | 9.2771 | 14.9946 | 112.2537 | 4.5885 | 7.6708 | 4.614 | 9.2502 | 8.9293 | 41.8367 | 46.4805 | 42.843 | 14.542 |  |  | -0.6339 | 0.18211 | 0.08136 | 0.11499 | -0.064892 | -0.031344 | 0.22989 | 0.72266 | -0.27904 | -0.28529 | 0.21687 | -0.0006029 | -0.00056183 | 1.1193 | 15.991 | 16.6231 | 17.1625 | 17.4766 | 17.4257 | 16.364 | 14.7053 | 16.7665 | 17.1084 | 17.3929 | 17.4354 | 17.1392 | 16.2989 | 14.4938 | 49.8138 | 22.6628 | 34.95 | 27.2897 | 23.6444 | 38.6144 | 22.6384 | 15.8461 | 15.5594 | 15.626 | 14.3104 | 15.4735 | 18.3304 |  |  |  | 57.8652 | 188.8375 | 153.4518 | 108.072 | 0.27477 | -0.20398 | 57.0979 |  |  | 11.6516 |  |  | 16.9034 | 17.1413 | 28.4158 | 16.3168 | 16.1069 | 20.5204 | 176.5068 | 220.9724 | 146.7589 | 149.9685 | 116.7774 |  | 62.4244 | 126.8915 | 62.1787 | 127.2021 | 101.6867 | 163.7766 |  | 97.7131 |  |  | 17.4687 | 21.3429 | 66.5841 | [6 empty] | 108.8128 |  |  | 48.0687 |  |  | 21.4121 | 85.1198 | 250.4452 | 10.7972 | 78.4918 | 160.6449 | 13.2655 | 74.2642 | 176.7076 | 29.6918 | 138.1979 | 14.0998 | 127.3827 | 16.0203 | 135.8742 | 12.2495 | 79.4407 | 148.1369 | 33.8417 | 75.4837 | 192.6153 | 14.3681 | 65.0903 | 175.6242 | 16.1525 | 124.5407 | 29.2558 | 135.6622 | 18.2986 | 145.2159 | 1.8332 | 18.8114 | 1.8338 | 0.086279 | -38.1644 | 3.1235 | 300.36 | 48.77 | -1.2015 | 0.49902 | 0.33354 | 0.39654 | -0.30135 | -0.20944 | 0.5672 | -0.79079 | -1.0807 | 0.41055 | -0.70871 | -0.93393 | -1.2084 | -0.7139
42810.4469 | 595 | 18.3952 | 18.4784 | 18.4832 | 18.4925 | 17.783 | 16.3794 | 14.4333 | 16.5829 | 17.0904 | 17.1865 | 17.1896 | 16.7073 | 15.7208 | 14.358 | 14.7217 | 14.7907 | 15.4972 | 13.2374 | 13.8794 | 17.7184 |  |  |  | 16.5475 | 16.5285 | 23.9643 | 175.7157 | 161.1978 | 195.8919 | 17.0357 | 16.5116 | 20.8846 | 16.7264 | 16.5033 | 22.0716 | 69.7134 | 198.3001 |  | 105.9807 | 154.5567 | 151.6674 | 142.8795 |  | 7.2264 | 8.4144 | 7.0602 | 8.4472 | 9.2535 | 14.9646 | 113.357 | 4.6589 | 7.6762 | 4.7363 | 9.27 | 8.9309 | 41.877 | 46.4922 | 42.8531 | 14.5716 |  |  | -0.84221 | 0.19591 | 0.15956 | -0.003286 | 0.020536 | -0.14634 | 0.13724 | 0.81138 | -0.2625 | -0.22802 | 0.36212 | -0.00052241 | -0.00058319 | 1.0177 | 15.9898 | 16.6206 | 17.1615 | 17.478 | 17.4271 | 16.366 | 14.7039 | 16.7599 | 17.1023 | 17.3955 | 17.4333 | 17.1409 | 16.2994 | 14.4859 | 46.7239 | 21.4128 | 31.3822 | 26.3615 | 22.9576 | 38.5929 | 22.6312 | 15.8343 | 15.5542 | 15.6368 | 14.3051 | 15.4713 | 18.3509 |  |  |  | 58.0856 | 187.9637 | 153.3348 | 108.214 | 0.76871 | -0.36527 | 57.3004 |  |  | 11.6545 |  |  | 16.8916 | 17.1401 | 28.4722 | 16.3224 | 16.1152 | 20.5498 | 176.5736 | 221.4994 | 147.1975 | 150.31 | 117.9064 |  | 62.67 | 127.1881 | 62.3634 | 129.3061 | 102.3719 | 163.0551 |  | 97.99 |  |  | 17.5471 | 21.373 | 67.1637 | [6 empty] | 108.158 |  |  | 48.2473 |  |  | 21.4645 | 84.939 | 251.3577 | 10.8049 | 78.8075 | 161.0138 | 13.2937 | 74.8186 | 177.4429 | 29.7896 | 138.9197 | 14.1404 | 127.9667 | 16.0524 | 136.1096 | 12.3105 | 79.3782 | 148.9718 | 33.9897 | 75.5727 | 192.7043 | 14.3847 | 65.5344 | 176.4902 | 16.2196 | 124.8189 | 29.3982 | 135.8609 | 18.3652 | 145.9158 | 1.6617 | 18.8083 | 1.8357 | 0.084289 | -38.1378 | 3.1235 | 322.31 | 50.13 | -1.3851 | 0.51758 | 0.46711 | -0.067033 | 0.16951 | -0.45251 | 0.43822 | -0.81322 | -1.0822 | 0.37935 | -0.36793 | -0.53835 | -1.2488 | -0.70991
42810.4469 | 596 | 18.3829 | 18.4784 | 18.4749 | 18.487 | 17.7825 | 16.3737 | 14.4216 | 16.5748 | 17.083 | 17.1811 | 17.1898 | 16.7061 | 15.7161 | 14.358 | 14.73 | 14.7927 | 15.4967 | 13.2415 | 13.8704 | 17.7395 |  |  |  | 16.5468 | 16.5253 | 24.0072 | 176.1446 | 161.1374 | 197.1299 | 17.0379 | 16.5171 | 20.9095 | 16.724 | 16.5015 | 22.1064 | 70.078 | 198.6238 |  | 106.376 | 155.1472 | 152.2466 | 145.5517 |  | 7.2243 | 8.4213 | 7.0682 | 8.4367 | 9.2596 | 14.9655 | 114.0781 | 4.7671 | 7.6774 | 4.7648 | 9.2794 | 8.934 | 41.9231 | 46.5122 | 42.8631 | 14.5977 |  |  | -0.71604 | 0.053971 | -0.016548 | -0.09791 | 0.29455 | -0.23308 | 0.28115 | 0.43682 | 0.084277 | -0.42984 | 0.25224 | -0.00052076 | -0.00058812 | 0.98233 | 15.994 | 16.6263 | 17.1601 | 17.4837 | 17.429 | 16.3705 | 14.708 | 16.761 | 17.1059 | 17.3999 | 17.4367 | 17.1425 | 16.3017 | 14.4827 | 47.3366 | 21.2022 | 29.9867 | 24.7989 | 21.7755 | 38.6352 | 22.6408 | 15.8447 | 15.5564 | 15.6311 | 14.3086 | 15.4892 | 18.372 |  |  |  | 58.316 | 187.4236 | 153.3 | 108.4202 | 0.78877 | 0.12348 | 57.3403 |  |  | 11.6619 |  |  | 16.8995 | 17.1512 | 28.5246 | 16.3176 | 16.111 | 20.5674 | 176.8559 | 222.4298 | 147.4918 | 150.5348 | 118.8014 |  | 62.8896 | 127.5054 | 62.5438 | 131.5002 | 103.1196 | 162.622 |  | 98.2813 |  |  | 17.6217 | 21.4602 | 67.9229 | [6 empty] | 107.6954 |  |  | 48.5573 |  |  | 21.5411 | 85.6968 | 252.3784 | 10.8441 | 78.9179 | 161.4638 | 13.3271 | 75.3725 | 178.1613 | 29.9142 | 139.6345 | 14.1544 | 128.3095 | 16.095 | 136.7714 | 12.3799 | 79.485 | 149.6553 | 34.1658 | 76.11 | 192.8339 | 14.3916 | 65.9078 | 177.4691 | 16.2638 | 125.2451 | 29.5938 | 136.2709 | 18.4234 | 146.7724 | 1.7881 | 18.8073 | 1.8397 | 0.08578 | -38.2137 | 3.1235 | 333.87 | 48.94 | -1.2788 | 0.27167 | -0.15043 | -0.36591 | 0.64199 | -0.57109 | 0.62722 | -0.8301 | -1.0845 | 0.34817 | -0.43102 | -0.38218 | -1.3096 | -0.70734
42810.4469 | 597 | 18.3957 | 18.4814 | 18.4836 | 18.4861 | 17.7851 | 16.3776 | 14.4327 | 16.5886 | 17.0877 | 17.1794 | 17.187 | 16.7061 | 15.7247 | 14.3587 | 14.7345 | 14.8 | 15.5017 | 13.2522 | 13.866 | 17.7668 |  |  |  | 16.5516 | 16.5261 | 24.0525 | 176.6311 | 161.289 | 197.9968 | 17.0563 | 16.5341 | 20.9449 | 16.7342 | 16.5168 | 22.1498 | 70.4171 | 199.6648 |  | 106.7613 | 155.6254 | 152.9791 | 146.626 |  | 7.2352 | 8.4367 | 7.0857 | 8.4687 | 9.2942 | 15.1189 | 114.5324 | 4.8786 | 7.688 | 4.8055 | 9.296 | 8.9351 | 41.9599 | 46.5218 | 42.8737 | 14.6175 |  |  | -0.60433 | 0.1164 | 0.14313 | -0.028254 | 0.26301 | 0.088252 | 0.047212 | 0.68258 | -0.367 | 0.0913 | 0.13183 | -0.00054705 | -0.00056348 | 1.043 | 15.9958 | 16.6298 | 17.1633 | 17.483 | 17.4311 | 16.3677 | 14.7103 | 16.7602 | 17.1087 | 17.4003 | 17.4406 | 17.1401 | 16.3012 | 14.4801 | 49.2343 | 22.0971 | 31.3871 | 23.7874 | 20.8586 | 38.674 | 22.6653 | 15.8472 | 15.5627 | 15.6306 | 14.313 | 15.4946 | 18.4054 |  |  |  | 58.5406 | 187.392 | 153.3896 | 108.7146 | 0.3702 | 0.052721 | 57.3881 |  |  | 11.6636 |  |  | 16.9034 | 17.1554 | 28.584 | 16.3311 | 16.1176 | 20.6015 | 177.2569 | 223.7818 | 147.8731 | 150.7867 | 119.3947 |  | 63.1022 | 128.0607 | 62.7243 | 127.0749 | 103.6715 | 162.5875 |  | 98.5687 |  |  | 17.6579 | 21.5015 | 68.6721 | [6 empty] | 106.0861 |  |  | 48.7538 |  |  | 21.616 | 86.2274 | 253.6548 | 10.892 | 79.3851 | 161.8411 | 13.3551 | 75.9442 | 178.772 | 30.0256 | 140.1162 | 14.1609 | 128.6219 | 16.1765 | 137.3623 | 12.4321 | 79.837 | 150.088 | 34.3746 | 76.5731 | 192.5952 | 14.414 | 66.2272 | 178.0697 | 16.3256 | 125.5871 | 29.7655 | 136.6876 | 18.4865 | 147.2668 | 1.8166 | 18.806 | 1.843 | 0.086829 | -38.1608 | 3.1235 | 361.59 | 49.06 | -1.1759 | 0.39898 | 0.44243 | -0.19657 | 0.60681 | 0.3515 | 0.25709 | -0.83884 | -1.0933 | 0.49312 | -0.6373 | -0.53491 | -1.3269 | -0.70742
42810.447 | 598 | 18.4039 | 18.4812 | 18.4864 | 18.4904 | 17.7891 | 16.3771 | 14.4275 | 16.5864 | 17.0943 | 17.1887 | 17.1944 | 16.7108 | 15.7258 | 14.3561 | 14.7374 | 14.8053 | 15.5062 | 13.2579 | 13.8642 | 17.7841 |  |  |  | 16.5564 | 16.5287 | 24.0948 | 177.122 | 161.6483 | 198.0385 | 17.0581 | 16.5308 | 20.9732 | 16.7361 | 16.522 | 22.1848 | 70.7546 | 200.0198 |  | 107.1754 | 155.9097 | 153.5985 | 148.2621 |  | 7.2601 | 8.4707 | 7.1249 | 8.5063 | 9.3373 | 15.2027 | 115.3613 | 4.9462 | 7.6954 | 4.895 | 9.3051 | 8.9387 | 41.9925 | 46.5292 | 42.8879 | 14.6441 |  |  | -0.72721 | 0.15188 | 0.041936 | -0.022342 | 0.01002 | -0.50512 | 0.25486 | 0.93294 | -0.6914 | -0.22592 | 0.21946 | -0.00051091 | 0.58021 | 1.0199 | 16.0059 | 16.6404 | 17.166 | 17.4914 | 17.4361 | 16.3782 | 14.715 | 16.7706 | 17.1098 | 17.4094 | 17.4436 | 17.1437 | 16.298 | 14.4878 | 47.6791 | 21.3857 | 30.7179 | 23.549 | 20.5903 | 38.6742 | 22.6814 | 15.8394 | 15.5557 | 15.6329 | 14.3103 | 15.4999 | 18.4212 |  |  |  | 58.7634 | 186.9637 | 153.4549 | 109.1055 | 0.15605 | -0.061328 | 57.5258 |  |  | 11.6786 |  |  | 16.8962 | 17.1688 | 28.641 | 16.3199 | 16.1228 | 20.6284 | 177.7149 | 224.7861 | 148.0486 | 151.0365 | 119.4781 |  | 63.3223 | 128.24 | 62.9188 | 123.8512 | 104.2535 | 164.1294 |  | 98.8371 |  |  | 17.6943 | 21.5568 | 69.0196 | [6 empty] | 104.9456 |  |  | 49.0099 |  |  | 21.7091 | 86.1326 | 254.4085 | 10.9499 | 80.07 | 162.1568 | 13.3861 | 76.4245 | 179.5998 | 30.1559 | 140.376 | 14.1737 | 129.0659 | 16.2343 | 137.4897 | 12.4427 | 80.1142 | 150.2884 | 34.592 | 77.0716 | 192.4427 | 14.4614 | 66.6522 | 178.6194 | 16.4067 | 125.9939 | 29.9421 | 137.1059 | 18.5417 | 147.6791 | 1.6051 | 18.7988 | 1.8454 | 0.087249 | -38.2009 | 3.1234 | 382.12 | 50.3 | -1.29 | 0.45578 | 0.23949 | -0.17481 | 0.11846 | -0.84106 | 0.59742 | -0.83314 | -1.0912 | 0.60591 | -0.46447 | -0.45867 | -1.3599 | -0.71024
42810.447 | 599 | 18.3996 | 18.4867 | 18.4821 | 18.4921 | 17.7936 | 16.3865 | 14.4337 | 16.5882 | 17.0945 | 17.1932 | 17.1909 | 16.7143 | 15.7308 | 14.3624 | 14.7361 | 14.8037 | 15.5066 | 13.251 | 13.8567 | 17.8049 |  |  |  | 16.5496 | 16.5288 | 24.1366 | 177.4416 | 162.0509 | 196.9467 | 17.0523 | 16.5324 | 20.9996 | 16.7266 | 16.5194 | 22.205 | 71.1232 | 202.3418 |  | 107.6098 | 156.164 | 154.1781 | 149.9138 |  | 7.2701 | 8.5002 | 7.1514 | 8.5234 | 9.3145 | 15.1517 | 115.7452 | 4.8765 | 7.7023 | 4.996 | 9.3235 | 8.9459 | 42.0063 | 46.5242 | 42.8918 | 14.6686 |  |  | -0.78635 | -0.071537 | 0.15759 | 0.017086 | -0.10103 | -0.6188 | 0.0597 | 0.72332 | -0.11383 | -0.16843 | 0.26655 | -0.00061769 | 8.9048 | 0.98622 | 16.0048 | 16.6369 | 17.1685 | 17.4805 | 17.4382 | 16.3758 | 14.7092 | 16.7669 | 17.1048 | 17.3974 | 17.4336 | 17.141 | 16.2931 | 14.484 | 43.8713 | 20.6898 | 28.8482 | 22.5595 | 20.0305 | 38.6387 | 22.6819 | 15.8383 | 15.5466 | 15.6286 | 14.304 | 15.5075 | 18.446 |  |  |  | 59.0121 | 186.2533 | 153.5457 | 109.5069 | 0.030439 | -0.11835 | 57.6205 |  |  | 11.6743 |  |  | 16.902 | 17.1766 | 28.6893 | 16.3252 | 16.1282 | 20.6612 | 177.8597 | 225.8224 | 148.1361 | 151.0021 | 119.2045 |  | 63.5284 | 128.0488 | 63.0829 | 128.0673 | 104.9247 | 164.8375 |  | 99.1121 |  |  | 17.7005 | 21.6008 | 70.0588 | [6 empty] | 107.0516 |  |  | 49.2229 |  |  | 21.7992 | 86.5284 | 255.2117 | 10.988 | 80.3206 | 162.512 | 13.4175 | 76.9087 | 180.5923 | 30.2816 | 140.5564 | 14.191 | 129.5987 | 16.2909 | 137.8821 | 12.4254 | 80.241 | 150.625 | 34.8128 | 77.625 | 192.7816 | 14.4902 | 66.8881 | 179.1709 | 16.4658 | 126.5039 | 30.0869 | 137.3169 | 18.5866 | 147.7726 | 1.9266 | 18.7964 | 1.8485 | 0.085295 | -38.2355 | 3.1235 | 406.52 | 48.45 | -1.3399 | -0.31281 | 0.46428 | 0.15288 | -0.37611 | -0.93082 | 0.28912 | -0.81803 | -1.0799 | 0.51564 | -0.045575 | -0.25087 | -1.3921 | -0.71242
42810.447 | 600 | 18.3941 | 18.4843 | 18.48 | 18.4927 | 17.7899 | 16.3837 | 14.4254 | 16.5857 | 17.0893 | 17.1881 | 17.1864 | 16.7084 | 15.7313 | 14.362 | 14.7371 | 14.81 | 15.51 | 13.2533 | 13.8524 | 17.8305 |  |  |  | 16.5544 | 16.5377 | 24.1851 | 177.7328 | 162.3308 | 197.0208 | 17.0511 | 16.5438 | 21.0221 | 16.7281 | 16.524 | 22.2393 | 71.4911 | 203.8958 |  | 108.0329 | 156.5182 | 154.6844 | 151.0155 |  | 7.3003 | 8.5437 | 7.1654 | 8.5376 | 9.277 | 15.057 | 115.9993 | 4.7549 | 7.7165 | 5.0055 | 9.3527 | 8.9482 | 42.0113 | 46.5385 | 42.8845 | 14.6823 |  |  | -0.64638 | 0.16568 | -0.052032 | -0.34301 | 0.12502 | -0.57938 | -0.47848 | 0.73909 | -0.24829 | -0.21753 | 0.442 | -0.00063412 | 8.9055 | 0.96701 | 16.0043 | 16.639 | 17.1662 | 17.4865 | 17.4345 | 16.3783 | 14.7016 | 16.765 | 17.1063 | 17.3987 | 17.439 | 17.1441 | 16.3074 | 14.483 | 40.012 | 20.3951 | 27.7866 | 21.5214 | 20.0585 | 38.5688 | 22.6798 | 15.8353 | 15.5564 | 15.6433 | 14.3115 | 15.5206 | 18.4787 |  |  |  | 59.2391 | 185.6276 | 153.4914 | 109.5407 | 0.14126 | -0.26967 | 57.6702 |  |  | 11.687 |  |  | 16.9005 | 17.1796 | 28.7494 | 16.3158 | 16.1216 | 20.6717 | 178.4555 | 226.2584 | 148.3965 | 151.3744 | 119.739 |  | 63.7193 | 127.4401 | 63.2325 | 132.1079 | 105.5865 | 164.9789 |  | 99.4114 |  |  | 17.714 | 21.6512 | 70.6412 | [6 empty] | 107.9063 |  |  | 49.3755 |  |  | 21.8706 | 87.2696 | 256.605 | 10.9906 | 81.0251 | 162.8637 | 13.4556 | 77.465 | 181.2083 | 30.394 | 140.7459 | 14.2129 | 130.2948 | 16.3638 | 138.2961 | 12.4371 | 80.4446 | 151.2585 | 35.0006 | 78.2055 | 193.1468 | 14.5159 | 67.0924 | 179.4315 | 16.5103 | 126.8297 | 30.1952 | 137.4463 | 18.645 | 148.2014 | 1.4959 | 18.7949 | 1.8541 | 0.087184 | -38.2398 | 3.1235 | 397.91 | 48.99 | -1.2149 | 0.4761 | -0.2668 | -0.68503 | 0.41831 | -0.90054 | -0.81837 | -0.82593 | -1.0576 | 0.42992 | 0.37499 | -0.13317 | -1.4091 | -0.70516
42810.447 | 601 | 18.4046 | 18.4893 | 18.4847 | 18.4999 | 17.7915 | 16.3897 | 14.4337 | 16.5971 | 17.0879 | 17.1838 | 17.1873 | 16.709 | 15.7339 | 14.361 | 14.7384 | 14.808 | 15.5101 | 13.2541 | 13.8432 | 17.8501 |  |  |  | 16.5528 | 16.5513 | 24.2291 | 178.0501 | 162.5274 | 196.5992 | 17.048 | 16.5466 | 21.0573 | 16.7314 | 16.5221 | 22.2712 | 71.867 | 204.5777 |  | 108.424 | 156.9627 | 155.0761 | 152.0079 |  | 7.3021 | 8.5668 | 7.1722 | 8.5413 | 9.2621 | 15.114 | 117.041 | 4.6799 | 7.7125 | 4.9538 | 9.353 | 8.9537 | 42.0084 | 46.5549 | 42.8781 | 14.7028 |  |  | -0.80738 | 0.25571 | 0.09122 | 0.026286 | 0.25972 | -0.15554 | -0.29974 | 0.55641 | -0.33625 | -0.17829 | 0.30589 | -0.0006144 | 8.905 | 0.94592 | 16.0033 | 16.6367 | 17.1654 | 17.487 | 17.4312 | 16.373 | 14.7007 | 16.7593 | 17.1003 | 17.3912 | 17.4333 | 17.1401 | 16.3 | 14.4826 | 38.3774 | 19.7957 | 26.1613 | 20.7002 | 19.7028 | 38.5253 | 22.658 | 15.8361 | 15.5517 | 15.6396 | 14.3078 | 15.5201 | 18.492 |  |  |  | 59.4681 | 185.5127 | 153.3826 | 109.773 | 1.5238 | -0.38936 | 57.8038 |  |  | 11.6993 |  |  | 16.9055 | 17.187 | 28.8063 | 16.3268 | 16.1237 | 20.7135 | 178.8955 | 227.6064 | 148.602 | 151.6914 | 119.6532 |  | 64.0124 | 127.1886 | 63.4878 | 133.8258 | 106.4512 | 164.5424 |  | 99.7286 |  |  | 17.7044 | 21.7253 | 70.6284 | [6 empty] | 109.4089 |  |  | 49.4683 |  |  | 21.9438 | 87.9511 | 258.4794 | 11.0211 | 81.6363 | 163.4938 | 13.5112 | 77.9551 | 181.9533 | 30.5328 | 140.941 | 14.2525 | 130.8954 | 16.4492 | 138.6196 | 12.474 | 80.7474 | 151.8172 | 35.1669 | 78.7965 | 193.3091 | 14.562 | 67.355 | 180.0328 | 16.5504 | 127.0557 | 30.314 | 137.5712 | 18.7004 | 148.9958 | 1.6648 | 18.7917 | 1.8588 | 0.0884 | -38.2784 | 3.1235 | 376.3 | 49.97 | -1.3572 | 0.59149 | 0.35328 | 0.18964 | 0.603 | -0.46664 | -0.64779 | -0.81286 | -1.0413 | 0.41691 | 0.55148 | 0.04487 | -1.4227 | -0.70334
42810.447 | 602 | 18.4066 | 18.4945 | 18.4886 | 18.5002 | 17.7896 | 16.386 | 14.43 | 16.5923 | 17.0943 | 17.1906 | 17.1934 | 16.714 | 15.7275 | 14.3737 | 14.7447 | 14.8092 | 15.5094 | 13.2567 | 13.8444 | 17.8771 |  |  |  | 16.5502 | 16.5515 | 24.2759 | 178.3056 | 162.6957 | 197.0951 | 17.0512 | 16.5486 | 21.0881 | 16.7379 | 16.5315 | 22.3043 | 72.2587 | 205.03 |  | 108.7803 | 157.4878 | 155.3416 | 153.8937 |  | 7.3349 | 8.5982 | 7.1902 | 8.5601 | 9.2504 | 15.1389 | 118.2514 | 4.6009 | 7.7408 | 4.8176 | 9.3856 | 8.9627 | 42.0031 | 46.5504 | 42.872 | 14.7093 |  |  | -0.76729 | -0.12608 | -0.015892 | -0.22473 | 0.023164 | -0.61026 | -0.006672 | 0.2548 | -0.65793 | -0.79678 | 0.31761 | -0.00060947 | 8.9047 | 0.96347 | 16.0061 | 16.6352 | 17.1659 | 17.4837 | 17.4291 | 16.3695 | 14.7087 | 16.7622 | 17.1008 | 17.3971 | 17.4392 | 17.1431 | 16.2968 | 14.4817 | 43.9328 | 20.3271 | 25.4644 | 19.4436 | 18.2855 | 38.6086 | 22.6376 | 15.8355 | 15.5551 | 15.6435 | 14.3148 | 15.5355 | 18.5215 |  |  |  | 59.6995 | 185.2725 | 153.3302 | 110.4281 | 0.45306 | -0.090499 | 58.0022 |  |  | 11.6952 |  |  | 16.8968 | 17.1907 | 28.8576 | 16.3133 | 16.1304 | 20.7382 | 179.2386 | 228.939 | 148.7482 | 151.9675 | 121.3553 |  | 64.2534 | 127.4753 | 63.6963 | 134.5812 | 107.037 | 164.5491 |  | 99.9877 |  |  | 17.7195 | 21.7798 | 70.7382 | [6 empty] | 107.5191 |  |  | 49.6777 |  |  | 22.0168 | 88.3884 | 259.377 | 11.0375 | 81.8734 | 164.0662 | 13.5604 | 78.412 | 182.5734 | 30.6993 | 141.0644 | 14.3163 | 131.0807 | 16.5176 | 138.8672 | 12.5002 | 81.1019 | 152.353 | 35.3791 | 79.3898 | 193.3894 | 14.6061 | 67.5393 | 180.9122 | 16.5627 | 127.3905 | 30.4171 | 137.7122 | 18.7571 | 149.6501 | 1.8459 | 18.7877 | 1.8634 | 0.088516 | -38.2444 | 3.1235 | 379.19 | 49.47 | -1.3238 | -0.41535 | -0.14746 | -0.55454 | 0.18009 | -0.92436 | -0.096652 | -0.85134 | -1.0417 | 0.41948 | -0.055953 | 0.11992 | -1.4606 | -0.71318
42810.447 | 603 | 18.3986 | 18.4783 | 18.4813 | 18.4887 | 17.7926 | 16.3806 | 14.4195 | 16.588 | 17.0857 | 17.1858 | 17.1936 | 16.7099 | 15.7311 | 14.3616 | 14.7424 | 14.8032 | 15.5151 | 13.254 | 13.8497 | 17.8877 |  |  |  | 16.5564 | 16.5533 | 24.3138 | 178.6083 | 162.808 | 196.9496 | 17.0577 | 16.5529 | 21.1236 | 16.74 | 16.5427 | 22.3347 | 72.7369 | 205.8207 |  | 109.203 | 158.011 | 155.7554 | 156.8679 |  | 7.3267 | 8.5857 | 7.1844 | 8.5405 | 9.2283 | 15.1512 | 119.5432 | 4.5299 | 7.736 | 4.6315 | 9.3901 | 8.9708 | 41.9929 | 46.5338 | 42.8577 | 14.718 |  |  | -0.67792 | 0.024403 | -0.031004 | -0.54672 | 0.15064 | -0.53075 | 0.016328 | 0.57547 | -0.50984 | 0.63384 | 0.15726 | -0.00062426 | 8.9042 | 0.95585 | 16.0085 | 16.6327 | 17.1674 | 17.4839 | 17.4263 | 16.365 | 14.7045 | 16.762 | 17.1044 | 17.4028 | 17.4364 | 17.1379 | 16.2978 | 14.4836 | 46.4516 | 20.3171 | 24.7733 | 19.3462 | 17.4474 | 38.6694 | 22.6226 | 15.8335 | 15.5545 | 15.6364 | 14.3142 | 15.5384 | 18.5465 |  |  |  | 59.9547 | 185.3162 | 153.3462 | 110.9152 | 0.93829 | -0.16747 | 58.2909 |  |  | 11.6772 |  |  | 16.8901 | 17.1855 | 28.9216 | 16.3167 | 16.1245 | 20.7615 | 179.4557 | 229.5749 | 148.9677 | 152.1795 | 121.6838 |  | 64.4808 | 127.6384 | 63.8811 | 133.7536 | 107.54 | 165.5631 |  | 100.3014 |  |  | 17.8092 | 21.8334 | 70.4642 | [6 empty] | 106.8737 |  |  | 49.8231 |  |  | 22.075 | 88.6811 | 259.8569 | 11.0688 | 82.6037 | 164.3913 | 13.6042 | 78.7274 | 183.7066 | 30.8438 | 141.2065 | 14.3695 | 131.2311 | 16.5931 | 139.027 | 12.5233 | 81.7024 | 152.6336 | 35.5669 | 79.8481 | 193.735 | 14.6649 | 67.6852 | 181.8346 | 16.5648 | 127.9849 | 30.5091 | 138.0498 | 18.8306 | 150.0043 | 1.9393 | 18.7876 | 1.8663 | 0.086605 | -38.2496 | 3.1235 | 366.67 | 50.11 | -1.2441 | 0.18273 | -0.20597 | -0.86491 | 0.45927 | -0.86206 | 0.1512 | -0.85217 | -1.0395 | 0.46273 | -0.32865 | 0.19497 | -1.5254 | -0.71749
42810.447 | 604 | 18.3918 | 18.477 | 18.4647 | 18.4827 | 17.7863 | 16.3718 | 14.4197 | 16.5789 | 17.0836 | 17.1823 | 17.1941 | 16.7081 | 15.7187 | 14.3577 | 14.7408 | 14.8164 | 15.5128 | 13.2488 | 13.8445 | 17.9062 |  |  |  | 16.548 | 16.5573 | 24.3682 | 178.9848 | 163.0955 | 197.9643 | 17.0607 | 16.5549 | 21.138 | 16.7395 | 16.5428 | 22.369 | 73.1689 | 206.0943 |  | 109.5898 | 158.4495 | 156.3219 | 158.4065 |  | 7.3251 | 8.5841 | 7.191 | 8.5172 | 9.2104 | 15.1588 | 120.7376 | 4.5369 | 7.7546 | 4.4817 | 9.3966 | 8.9687 | 41.9811 | 46.524 | 42.8381 | 14.7193 |  |  | -0.69961 | -0.24962 | -0.192 | -0.27402 | -0.03992 | -0.29025 | -0.078952 | 0.5919 | -0.41117 | -0.71307 | 0.24966 | -0.00065383 | 8.9049 | 0.94823 | 16.0066 | 16.6273 | 17.1656 | 17.4771 | 17.4235 | 16.3611 | 14.6974 | 16.7616 | 17.1009 | 17.3997 | 17.431 | 17.1356 | 16.2876 | 14.4778 | 48.5695 | 22.4165 | 25.03 | 19.3572 | 16.986 | 38.7501 | 22.6185 | 15.8333 | 15.5602 | 15.6482 | 14.3178 | 15.5516 | 18.5654 |  |  |  | 60.235 | 184.9428 | 153.4548 | 111.1128 | 0.26809 | 0.092431 | 58.3663 |  |  | 11.6701 |  |  | 16.8953 | 17.2088 | 28.9762 | 16.3201 | 16.1337 | 20.7978 | 180.0683 | 230.0693 | 149.4614 | 152.7045 | 121.4442 |  | 64.7508 | 126.9887 | 64.1154 | 132.0535 | 108.0242 | 167.4564 |  | 100.6937 |  |  | 17.8074 | 21.8997 | 69.8159 | [6 empty] | 106.2064 |  |  | 50.0108 |  |  | 22.1386 | 89.2965 | 260.8257 | 11.1284 | 83.1135 | 164.6337 | 13.6383 | 78.9914 | 184.425 | 30.9511 | 141.3038 | 14.4007 | 131.5428 | 16.6442 | 139.1973 | 12.5663 | 82.497 | 153.076 | 35.8716 | 80.3062 | 194.2684 | 14.7136 | 67.9152 | 182.3735 | 16.5784 | 128.416 | 30.6637 | 138.3867 | 18.9183 | 150.2865 | 1.635 | 18.7815 | 1.871 | 0.087119 | -38.2551 | 3.1236 | 381.18 | 49.96 | -1.2652 | -0.58442 | -0.51255 | -0.61232 | -0.23642 | -0.6375 | -0.33249 | -0.83565 | -1.0129 | 0.52947 | -0.55445 | 0.16596 | -1.5521 | -0.71284
42810.447 | 605 | 18.4138 | 18.4962 | 18.4812 | 18.4965 | 17.7989 | 16.3867 | 14.4318 | 16.6003 | 17.1005 | 17.1944 | 17.2004 | 16.7196 | 15.7347 | 14.3675 | 14.7445 | 14.81 | 15.5193 | 13.2596 | 13.8531 | 17.9254 |  |  |  | 16.5604 | 16.5605 | 24.4039 | 179.3731 | 163.4598 | 199.925 | 17.0614 | 16.558 | 21.1742 | 16.7405 | 16.5472 | 22.4055 | 73.5588 | 206.0389 |  | 109.9128 | 158.9452 | 156.8959 | 158.9991 |  | 7.3184 | 8.5858 | 7.1731 | 8.4932 | 9.1994 | 15.1022 | 122.1668 | 4.5593 | 7.7505 | 4.3834 | 9.4089 | 8.9806 | 41.9824 | 46.5123 | 42.8242 | 14.7318 |  |  | -0.856 | -0.17405 | 0.062964 | -0.21028 | -0.006408 | -0.38027 | 0.20624 | 0.76866 | -0.13426 | -0.33921 | 0.013404 | -0.00065876 | 8.9051 | 0.9866 | 16.0067 | 16.6297 | 17.1596 | 17.4761 | 17.4255 | 16.3647 | 14.6919 | 16.7599 | 17.0934 | 17.3997 | 17.4266 | 17.143 | 16.2886 | 14.4793 | 46.2557 | 21.5311 | 25.0999 | 19.7244 | 17.1136 | 38.7474 | 22.619 | 15.8285 | 15.5546 | 15.646 | 14.3103 | 15.5537 | 18.5912 |  |  |  | 60.4683 | 184.94 | 153.6623 | 111.5355 | 0.85948 | 0.12518 | 58.5899 |  |  | 11.6761 |  |  | 16.8965 | 17.2096 | 29.0346 | 16.3151 | 16.1416 | 20.8216 | 180.3548 | 230.4711 | 149.914 | 153.2584 | 120.9581 |  | 64.9543 | 127.6127 | 64.3212 | 129.9695 | 108.5011 | 168.4214 |  | 100.994 |  |  | 17.8087 | 21.922 | 70.0223 | [6 empty] | 105.4061 |  |  | 50.2873 |  |  | 22.2016 | 89.7699 | 261.0332 | 11.1751 | 83.2115 | 165.0531 | 13.6617 | 79.2797 | 185.5487 | 31.0385 | 141.9272 | 14.4246 | 131.9532 | 16.719 | 139.4345 | 12.5793 | 83.052 | 153.4343 | 36.0723 | 80.7861 | 194.9973 | 14.7279 | 68.1322 | 183.0009 | 16.6024 | 128.6674 | 30.7953 | 138.4868 | 18.9731 | 150.4937 | 1.8097 | 18.7748 | 1.8759 | 0.088523 | -38.2572 | 3.1235 | 368.27 | 48.94 | -1.4024 | -0.488 | 0.29352 | -0.5364 | -0.094714 | -0.72963 | 0.53732 | -0.81472 | -1.0227 | 0.60661 | -0.29768 | 0.15825 | -1.554 | -0.71614
42810.447 | 606 | 18.4119 | 18.4867 | 18.4872 | 18.4976 | 17.7898 | 16.3821 | 14.4323 | 16.5918 | 17.089 | 17.198 | 17.1924 | 16.7231 | 15.7281 | 14.369 | 14.7463 | 14.8119 | 15.5237 | 13.2533 | 13.8562 | 17.9495 |  |  |  | 16.5443 | 16.5606 | 24.4417 | 179.9301 | 163.9124 | 198.3938 | 17.0668 | 16.565 | 21.2013 | 16.7413 | 16.5445 | 22.4404 | 73.9456 | 206.553 |  | 110.3225 | 159.3955 | 157.3317 | 159.6538 |  | 7.3252 | 8.6066 | 7.1675 | 8.4786 | 9.1941 | 15.0804 | 122.6414 | 4.5105 | 7.7626 | 4.3849 | 9.4321 | 8.9748 | 41.9657 | 46.5005 | 42.7947 | 14.7223 |  |  | -0.68515 | 0.17685 | 0.01302 | -0.33316 | 0.05602 | -0.092456 | -0.13481 | 0.9428 | -0.55985 | -0.3925 | 0.3039 | -0.00064397 | 8.9053 | 0.96532 | 16.0164 | 16.6348 | 17.1719 | 17.4914 | 17.4335 | 16.3745 | 14.7012 | 16.7658 | 17.1019 | 17.4028 | 17.4414 | 17.1471 | 16.2981 | 14.4872 | 47.3985 | 22.3958 | 26.1336 | 20.3749 | 17.5573 | 38.8217 | 22.6338 | 15.8288 | 15.5572 | 15.6481 | 14.3065 | 15.562 | 18.6149 |  |  |  | 60.6984 | 184.9043 | 153.8936 | 111.9019 | 1.1774 | 0.41105 | 58.9403 |  |  | 11.6794 |  |  | 16.8924 | 17.2159 | 29.0916 | 16.3295 | 16.1405 | 20.8464 | 180.6731 | 231.1509 | 150.2789 | 153.7198 | 120.4767 |  | 65.1456 | 128.1537 | 64.5254 | 128.8367 | 108.9746 | 168.4461 |  | 101.2732 |  |  | 17.8382 | 21.9561 | 70.8091 | [6 empty] | 105.1193 |  |  | 50.3035 |  |  | 22.2638 | 90.7146 | 261.8081 | 11.1853 | 83.7417 | 165.4764 | 13.6793 | 79.3705 | 186.5077 | 31.1309 | 142.8566 | 14.4714 | 132.6023 | 16.7796 | 139.9461 | 12.6434 | 83.6713 | 153.7648 | 36.2181 | 81.2039 | 195.4594 | 14.7821 | 68.2886 | 183.7862 | 16.6266 | 129.1873 | 30.9396 | 138.5521 | 19.036 | 151.2976 | 1.7659 | 18.7719 | 1.8797 | 0.089196 | -38.2741 | 3.1235 | 359.49 | 50.26 | -1.2526 | 0.49194 | 0.13348 | -0.67519 | 0.28003 | -0.35975 | -0.4344 | -0.79435 | -1.0303 | 0.65721 | -0.4159 | 0.045126 | -1.5578 | -0.71798
42810.4471 | 607 | 18.4112 | 18.4791 | 18.486 | 18.4944 | 17.7883 | 16.382 | 14.426 | 16.5857 | 17.0829 | 17.1908 | 17.1917 | 16.7145 | 15.7281 | 14.366 | 14.7562 | 14.8201 | 15.5418 | 13.261 | 13.875 | 17.987 |  |  |  | 16.5596 | 16.5854 | 24.4979 | 180.2043 | 164.3377 | 198.8142 | 17.0658 | 16.5685 | 21.232 | 16.7405 | 16.5507 | 22.4823 | 74.3293 | 206.5178 |  | 110.7097 | 159.7432 | 157.8278 | 159.7504 |  | 7.3281 | 8.6048 | 7.1599 | 8.4696 | 9.1826 | 15.1693 | 122.228 | 4.4651 | 7.7683 | 4.3954 | 9.445 | 8.9759 | 41.9622 | 46.498 | 42.7799 | 14.7311 |  |  | -0.9112 | -0.19442 | -0.20514 | -0.24576 | -0.052404 | -0.50841 | -0.078952 | 1.2352 | 0.032319 | -0.035839 | 0.21628 | -0.0006374 | 8.9048 | 0.94045 | 16.0084 | 16.6362 | 17.1566 | 17.4831 | 17.4232 | 16.3634 | 14.7083 | 16.7657 | 17.1024 | 17.399 | 17.4347 | 17.1386 | 16.2909 | 14.4875 | 51.5822 | 23.6235 | 27.9818 | 21.339 | 18.4878 | 38.9691 | 22.6756 | 15.8332 | 15.5579 | 15.6462 | 14.3068 | 15.5709 | 18.6406 |  |  |  | 60.9245 | 184.5865 | 154.172 | 111.665 | 0.48507 | 0.3832 | 59.1157 |  |  | 11.7091 |  |  | 16.8992 | 17.2337 | 29.1566 | 16.3253 | 16.1631 | 20.8841 | 180.5479 | 231.7183 | 150.4854 | 154.034 | 119.6012 |  | 65.3584 | 128.4967 | 64.7379 | 129.9009 | 109.4965 | 167.0772 |  | 101.6027 |  |  | 17.8713 | 22.0152 | 71.377 | [6 empty] | 107.744 |  |  | 50.5762 |  |  | 22.355 | 91.0388 | 263.4695 | 11.2047 | 84.7198 | 165.9955 | 13.7076 | 79.4027 | 187.2522 | 31.2566 | 143.4505 | 14.4917 | 133.1209 | 16.8442 | 140.5084 | 12.6618 | 84.3786 | 154.1581 | 36.3804 | 81.6931 | 195.5779 | 14.7873 | 68.3551 | 185.1558 | 16.6561 | 129.5922 | 31.0868 | 138.6164 | 19.0714 | 151.9153 | 2.0283 | 18.7651 | 1.8837 | 0.088878 | -38.2477 | 3.1235 | 353.49 | 49.36 | -1.4452 | -0.51579 | -0.52982 | -0.57991 | -0.27089 | -0.84375 | -0.3325 | -0.76225 | -1.032 | 0.64876 | -0.86336 | -0.15534 | -1.5462 | -0.70321
42810.4471 | 608 | 18.4155 | 18.4836 | 18.4889 | 18.4987 | 17.7901 | 16.3867 | 14.4273 | 16.591 | 17.0944 | 17.191 | 17.1969 | 16.7165 | 15.7416 | 14.3701 | 14.7445 | 14.8164 | 15.5318 | 13.2533 | 13.8926 | 17.9908 |  |  |  | 16.5546 | 16.5772 | 24.548 | 180.6963 | 164.5177 | 203.3918 | 17.0687 | 16.5747 | 21.2665 | 16.7413 | 16.5564 | 22.515 | 74.701 | 206.9572 |  | 111.1378 | 160.0897 | 158.497 | 160.8197 |  | 7.3324 | 8.6216 | 7.1694 | 8.463 | 9.1699 | 15.1412 | 122.8297 | 4.4421 | 7.7737 | 4.4157 | 9.4623 | 8.9934 | 41.9781 | 46.507 | 42.7657 | 14.7396 |  |  | -0.78306 | -0.24107 | -0.19266 | -0.19911 | 0.12304 | -0.48672 | 0.16286 | 0.7404 | -0.16442 | 0.13892 | 0.30986 | -0.00061933 | 8.9053 | 0.92205 | 16.0176 | 16.6292 | 17.157 | 17.4808 | 17.4235 | 16.3676 | 14.7062 | 16.7631 | 17.1012 | 17.3975 | 17.4321 | 17.1362 | 16.3004 | 14.4882 | 51.662 | 23.0574 | 29.059 | 21.4445 | 18.5508 | 39.0319 | 22.7086 | 15.8255 | 15.5613 | 15.6499 | 14.3164 | 15.5805 | 18.6625 |  |  |  | 61.1606 | 183.7847 | 154.2889 | 110.9615 | 0.43159 | -0.16616 | 59.2894 |  |  | 11.7159 |  |  | 16.9018 | 17.235 | 29.2109 | 16.3246 | 16.1571 | 20.9053 | 180.8639 | 233.3014 | 150.5352 | 154.2058 | 119.3766 |  | 65.5615 | 128.6416 | 64.9462 | 131.5501 | 110.1638 | 166.1152 |  | 101.9056 |  |  | 17.8675 | 22.0976 | 71.6665 | [6 empty] | 108.992 |  |  | 50.8633 |  |  | 22.4387 | 91.3358 | 265.1133 | 11.2098 | 84.763 | 166.3895 | 13.7224 | 79.6973 | 187.8381 | 31.2979 | 144.0786 | 14.5416 | 133.4479 | 16.8932 | 141.0688 | 12.624 | 84.5605 | 154.416 | 36.5476 | 82.0119 | 196.0632 | 14.7979 | 68.5829 | 185.8851 | 16.653 | 130.0921 | 31.1752 | 138.703 | 19.121 | 152.3815 | 2.2505 | 18.7532 | 1.8866 | 0.087097 | -38.2769 | 3.1235 | 346.77 | 49.39 | -1.3462 | -0.57437 | -0.51346 | -0.52198 | 0.41506 | -0.82551 | 0.47752 | -0.74858 | -1.0284 | 0.62999 | -0.8648 | -0.27116 | -1.562 | -0.67511
42810.4471 | 609 | 18.4122 | 18.4901 | 18.4852 | 18.4901 | 17.7927 | 16.3846 | 14.4284 | 16.5881 | 17.0849 | 17.1857 | 17.1954 | 16.7132 | 15.7389 | 14.3639 | 14.753 | 14.8222 | 15.5276 | 13.2634 | 13.9143 | 18.0157 |  |  |  | 16.5498 | 16.5812 | 24.5845 | 181.4126 | 164.5428 | 204.4777 | 17.072 | 16.5786 | 21.2921 | 16.7464 | 16.5652 | 22.5516 | 75.0537 | 208.8855 |  | 111.6247 | 160.4346 | 159.1247 | 161.9927 |  | 7.3383 | 8.6528 | 7.1654 | 8.4585 | 9.1479 | 15.0491 | 123.4297 | 4.4203 | 7.7807 | 4.4465 | 9.4809 | 8.9895 | 41.9694 | 46.498 | 42.7522 | 14.7408 |  |  | -0.47882 | -0.082709 | 0.015648 | -0.27599 | -0.029408 | -0.15028 | 0.25158 | 0.69244 | -0.055446 | 1.2295 | 0.30788 | -0.00064233 | 8.9054 | 0.92135 | 16.0072 | 16.6246 | 17.1555 | 17.4784 | 17.4172 | 16.364 | 14.6956 | 16.752 | 17.1023 | 17.3882 | 17.4236 | 17.1315 | 16.2966 | 14.4817 | 51.2304 | 22.3451 | 27.7779 | 20.8405 | 18.3133 | 39.0856 | 22.7084 | 15.8396 | 15.5626 | 15.6486 | 14.3105 | 15.5903 | 18.6904 |  |  |  | 61.4089 | 183.0132 | 154.2395 | 110.3139 | 0.62446 | 0.34914 | 59.5153 |  |  | 11.7152 |  |  | 16.9086 | 17.2384 | 29.2704 | 16.338 | 16.1613 | 20.9355 | 181.3197 | 234.3049 | 150.6258 | 154.2916 | 119.7842 |  | 65.7621 | 129.7664 | 65.1521 | 126.8625 | 110.6373 | 166.6024 |  | 102.1425 |  |  | 17.8325 | 22.155 | 71.4903 | [6 empty] | 106.7887 |  |  | 51.1519 |  |  | 22.5005 | 91.6233 | 266.0568 | 11.2236 | 84.8286 | 166.9326 | 13.7511 | 80.1236 | 188.5682 | 31.3295 | 144.5719 | 14.5753 | 133.7806 | 16.9382 | 141.4711 | 12.6012 | 84.8035 | 154.7458 | 36.7055 | 81.9463 | 196.4637 | 14.8426 | 69.0935 | 186.1895 | 16.6789 | 130.3957 | 31.2786 | 138.7548 | 19.2038 | 152.7902 | 1.9705 | 18.7514 | 1.8919 | 0.088248 | -38.2367 | 3.1235 | 346.24 | 50.01 | -1.0539 | -0.33645 | 0.14634 | -0.61459 | -0.20288 | -0.45864 | 0.5934 | -0.75256 | -1.0522 | 0.77942 | -0.81052 | -0.12885 | -1.5815 | -0.64812
42810.4471 | 610 | 18.428 | 18.4862 | 18.4917 | 18.496 | 17.7913 | 16.386 | 14.4312 | 16.5966 | 17.1023 | 17.1934 | 17.1923 | 16.7187 | 15.7348 | 14.3734 | 14.7533 | 14.8203 | 15.5278 | 13.2558 | 13.9223 | 18.0312 |  |  |  | 16.5462 | 16.582 | 24.6237 | 181.9403 | 164.8007 | 202.5007 | 17.066 | 16.5708 | 21.3142 | 16.7369 | 16.5675 | 22.5727 | 75.4205 | 210.9912 |  | 112.0453 | 160.7287 | 159.551 | 162.9464 |  | 7.3426 | 8.6519 | 7.1581 | 8.4555 | 9.12 | 14.9908 | 122.9876 | 4.4808 | 7.7782 | 4.4177 | 9.4895 | 8.9936 | 41.9631 | 46.5072 | 42.7327 | 14.7299 |  |  | -0.48342 | 0.121 | -0.012608 | -0.21422 | 0.050764 | 0.13294 | 0.39417 | 1.0111 | 0.11386 | -0.019264 | 0.30589 | -0.00064561 | 8.9053 | 0.91505 | 16.0115 | 16.6214 | 17.1595 | 17.4783 | 17.4183 | 16.3649 | 14.6969 | 16.7553 | 17.101 | 17.3878 | 17.4238 | 17.1299 | 16.2948 | 14.4788 | 51.1653 | 23.1536 | 27.9608 | 20.3049 | 17.3172 | 39.1217 | 22.7287 | 15.8318 | 15.5588 | 15.6532 | 14.3095 | 15.5985 | 18.7151 |  |  |  | 61.6269 | 182.4819 | 154.1485 | 109.6498 | 0.433 | 0.35836 | 60.017 |  |  | 11.7101 |  |  | 16.9027 | 17.2479 | 29.3219 | 16.3236 | 16.1593 | 20.9627 | 181.8805 | 235.5453 | 150.8679 | 154.4825 | 120.0242 |  | 65.9867 | 131.5523 | 65.3838 | 127.5943 | 111.1094 | 168.8951 |  | 102.4235 |  |  | 17.8797 | 22.2105 | 71.4383 | [6 empty] | 105.4041 |  |  | 51.3513 |  |  | 22.5628 | 91.6885 | 267.0819 | 11.1984 | 85.2669 | 167.374 | 13.7746 | 80.5059 | 189.2376 | 31.4813 | 144.995 | 14.5942 | 134.4933 | 16.9679 | 141.8566 | 12.6015 | 84.8869 | 155.1829 | 36.9205 | 82.2794 | 196.375 | 14.8869 | 69.5194 | 186.5272 | 16.6915 | 130.7328 | 31.3784 | 138.8687 | 19.2729 | 153.3348 | 1.9196 | 18.7485 | 1.8954 | 0.089131 | -38.1923 | 3.1235 | 357.81 | 48.7 | -1.0567 | 0.40694 | -0.13136 | -0.54146 | 0.26653 | 0.43131 | 0.7427 | -0.75101 | -1.0933 | 0.77826 | -0.79903 | -0.1468 | -1.5942 | -0.62177
42810.4471 | 611 | 18.4052 | 18.4806 | 18.4735 | 18.4884 | 17.7887 | 16.3613 | 14.4171 | 16.5792 | 17.087 | 17.1759 | 17.1887 | 16.7043 | 15.729 | 14.3543 | 14.7615 | 14.8206 | 15.5338 | 13.2591 | 13.9326 | 18.0535 |  |  |  | 16.5544 | 16.5879 | 24.6719 | 182.1376 | 165.3498 | 200.6343 | 17.0752 | 16.5778 | 21.3508 | 16.7495 | 16.5733 | 22.6209 | 75.8449 | 210.0882 |  | 112.4853 | 161.0381 | 159.947 | 163.9663 |  | 7.3391 | 8.6697 | 7.165 | 8.47 | 9.1439 | 15.2302 | 123.519 | 4.5876 | 7.7809 | 4.3713 | 9.5053 | 8.9934 | 41.9765 | 46.5224 | 42.7349 | 14.7292 |  |  | -0.76335 | -0.15565 | -0.056632 | -0.37127 | -0.069492 | 0.081024 | 0.38563 | 0.79298 | 0.38824 | 0.19012 | 0.076789 | -0.00066369 | 8.9051 | 0.92741 | 16.0135 | 16.6268 | 17.1529 | 17.4723 | 17.4182 | 16.3636 | 14.6961 | 16.7555 | 17.0998 | 17.3877 | 17.4244 | 17.1312 | 16.2899 | 14.4691 | 49.4624 | 21.6235 | 27.6483 | 20.2461 | 17.2462 | 39.1508 | 22.755 | 15.834 | 15.5608 | 15.657 | 14.3184 | 15.6085 | 18.7458 |  |  |  | 61.8443 | 181.7719 | 154.1127 | 109.5805 | 0.41356 | -0.034792 | 60.6044 |  |  | 11.7129 |  |  | 16.9068 | 17.2571 | 29.3818 | 16.3308 | 16.1638 | 20.9959 | 182.0853 | 236.6142 | 151.3895 | 154.7911 | 120.5985 |  | 66.2267 | 132.7373 | 65.6395 | 124.8005 | 111.608 | 171.838 |  | 102.7638 |  |  | 17.9442 | 22.2585 | 71.4737 | [6 empty] | 103.4639 |  |  | 51.5748 |  |  | 22.6474 | 91.9362 | 267.8433 | 11.1676 | 85.4566 | 167.7598 | 13.7913 | 80.7741 | 189.5818 | 31.6654 | 145.1861 | 14.6616 | 135.2022 | 17.0123 | 142.2022 | 12.6545 | 85.0019 | 155.4828 | 37.092 | 82.6894 | 196.8718 | 14.9236 | 69.8446 | 187.085 | 16.7431 | 131.1691 | 31.519 | 139.1611 | 19.3305 | 153.6876 | 1.8478 | 18.7474 | 1.8989 | 0.090093 | -38.2466 | 3.1234 | 369.08 | 48.66 | -1.3253 | -0.46156 | -0.27841 | -0.71285 | -0.31197 | 0.33687 | 0.73491 | -0.75817 | -1.1169 | 0.87615 | -0.60638 | -0.109 | -1.6067 | -0.61195
42810.4471 | 612 | 18.4174 | 18.4898 | 18.4787 | 18.4933 | 17.7899 | 16.3809 | 14.4261 | 16.588 | 17.0885 | 17.1909 | 17.196 | 16.7084 | 15.733 | 14.3626 | 14.7676 | 14.8262 | 15.544 | 13.2667 | 13.9353 | 18.0815 |  |  |  | 16.5577 | 16.5967 | 24.7207 | 182.3543 | 166.1913 | 200.0455 | 17.0799 | 16.583 | 21.382 | 16.7447 | 16.5751 | 22.6496 | 76.2534 | 208.8762 |  | 112.8168 | 161.3164 | 160.4341 | 165.2078 |  | 7.3496 | 8.6794 | 7.1732 | 8.4829 | 9.1709 | 15.5258 | 124.5689 | 4.6169 | 7.7985 | 4.3492 | 9.5254 | 9.0015 | 41.9931 | 46.5433 | 42.7338 | 14.7247 |  |  | -0.50839 | 0.077627 | 0.1911 | -0.26876 | 0.02382 | 0.10205 | 0.32057 | 0.73712 | -0.21949 | -0.3476 | 0.29019 | -0.00063576 | 8.9051 | 0.94696 | 16.0123 | 16.6287 | 17.1585 | 17.4796 | 17.4233 | 16.3686 | 14.6979 | 16.7527 | 17.1088 | 17.3926 | 17.4295 | 17.1347 | 16.2884 | 14.4714 | 48.2993 | 21.8241 | 28.8726 | 20.5335 | 17.1877 | 39.1542 | 22.7688 | 15.8315 | 15.5564 | 15.6614 | 14.3123 | 15.6186 | 18.7689 |  |  |  | 62.0702 | 181.1583 | 154.1539 | 109.4032 | 0.89291 | 0.42856 | 60.849 |  |  | 11.7195 |  |  | 16.9109 | 17.2649 | 29.4482 | 16.3355 | 16.176 | 21.0303 | 182.1842 | 236.8393 | 151.8886 | 155.1638 | 121.4707 |  | 66.4454 | 133.1294 | 65.845 | 125.5185 | 112.083 | 172.5793 |  | 103.0486 |  |  | 18.0119 | 22.3013 | 71.5722 | [6 empty] | 102.5034 |  |  | 51.6199 |  |  | 22.722 | 92.3716 | 268.4667 | 11.1442 | 85.3615 | 168.3434 | 13.7994 | 81.2447 | 190.1216 | 31.8382 | 145.4726 | 14.7256 | 135.6855 | 17.0525 | 142.603 | 12.7358 | 85.5496 | 155.982 | 37.2334 | 83.0883 | 197.8975 | 14.9739 | 70.297 | 187.5569 | 16.803 | 131.7232 | 31.6839 | 139.5259 | 19.39 | 153.9059 | 1.952 | 18.7465 | 1.9021 | 0.090832 | -38.228 | 3.1234 | 369.88 | 50.33 | -1.0809 | 0.32596 | 0.51144 | -0.60652 | 0.18274 | 0.37825 | 0.6704 | -0.77438 | -1.1202 | 0.87555 | -0.47674 | -0.24341 | -1.6259 | -0.59882
42810.4471 | 613 | 18.4264 | 18.4974 | 18.4921 | 18.4996 | 17.7885 | 16.3784 | 14.4377 | 16.5915 | 17.0922 | 17.1874 | 17.1934 | 16.7107 | 15.7308 | 14.3614 | 14.7647 | 14.8256 | 15.5466 | 13.2585 | 13.9422 | 18.099 |  |  |  | 16.5585 | 16.5982 | 24.7585 | 182.5021 | 166.8973 | 199.0651 | 17.0897 | 16.5973 | 21.4189 | 16.7492 | 16.5813 | 22.6918 | 76.6422 | 208.0438 |  | 113.2289 | 161.6881 | 161.0263 | 165.4179 |  | 7.3513 | 8.6737 | 7.1878 | 8.501 | 9.1892 | 15.5034 | 123.6459 | 4.5469 | 7.8003 | 4.4027 | 9.5466 | 9.0071 | 41.9987 | 46.5598 | 42.7319 | 14.7121 |  |  | -0.60499 | 0.097999 | 0.1175 | -0.25562 | -0.057004 | 0.14345 | -0.16372 | 0.55773 | -0.61764 | 1.7997 | 0.038241 | -0.00065219 | 8.9051 | 0.99857 | 16.0077 | 16.626 | 17.1589 | 17.4833 | 17.4309 | 16.3731 | 14.7025 | 16.753 | 17.0914 | 17.3917 | 17.4304 | 17.1341 | 16.2856 | 14.4835 | 51.5313 | 22.9659 | 31.1762 | 22.591 | 19.1844 | 39.2682 | 22.8185 | 15.8382 | 15.564 | 15.6723 | 14.3243 | 15.6285 | 18.7998 |  |  |  | 62.3358 | 180.7293 | 154.261 | 109.4929 | 1.3488 | 0.46262 | 61.3173 |  |  | 11.7292 |  |  | 16.9058 | 17.2758 | 29.5121 | 16.3232 | 16.1685 | 21.0489 | 182.6482 | 237.7861 | 152.3702 | 155.6726 | 122.9668 |  | 66.6581 | 133.0843 | 66.0537 | 126.9209 | 112.6137 | 171.7129 |  | 103.3323 |  |  | 18.1086 | 22.3692 | 71.9213 | [6 empty] | 102.1767 |  |  | 51.4534 |  |  | 22.7924 | 92.8579 | 269.1093 | 11.1458 | 85.3564 | 168.6724 | 13.8143 | 81.6587 | 190.6308 | 31.9903 | 145.7829 | 14.7465 | 136.2473 | 17.0821 | 143.0407 | 12.7923 | 85.784 | 156.5988 | 37.4363 | 83.3254 | 198.7073 | 15.0064 | 70.8381 | 187.8826 | 16.8407 | 132.1809 | 31.8175 | 139.8314 | 19.4363 | 154.0263 | 1.9628 | 18.7435 | 1.9041 | 0.089341 | -38.2014 | 3.1235 | 361.83 | 48.53 | -1.1779 | 0.36624 | 0.40103 | -0.5915 | -0.28269 | 0.44844 | -0.47908 | -0.80814 | -1.1113 | 0.85823 | -0.8224 | -0.49356 | -1.6172 | -0.59167
42810.4471 | 614 | 18.4321 | 18.5006 | 18.4928 | 18.4979 | 17.7977 | 16.3846 | 14.4342 | 16.595 | 17.0893 | 17.1892 | 17.1945 | 16.7125 | 15.7326 | 14.3621 | 14.7669 | 14.8296 | 15.5473 | 13.2567 | 13.9467 | 18.1226 |  |  |  | 16.5615 | 16.6074 | 24.8038 | 182.5612 | 167.342 | 198.7741 | 17.087 | 16.5992 | 21.4464 | 16.7479 | 16.5854 | 22.7197 | 77.0068 | 207.5446 |  | 113.6322 | 162.1778 | 161.5533 | 165.033 |  | 7.3673 | 8.6829 | 7.1915 | 8.5244 | 9.2187 | 15.4217 | 122.3854 | 4.545 | 7.8047 | 4.388 | 9.5623 | 9.0127 | 42.0085 | 46.5574 | 42.734 | 14.7015 |  |  | -0.48802 | -0.064965 | 0.043248 | 0.032854 | 0.07836 | -0.40262 | -0.064496 | 0.37045 | -0.36817 | -0.58174 | 0.048773 | -0.00065876 | 8.9055 | 0.98811 | 16.023 | 16.6239 | 17.1619 | 17.4844 | 17.4224 | 16.3707 | 14.7003 | 16.7514 | 17.0988 | 17.3869 | 17.4262 | 17.1327 | 16.2876 | 14.4795 | 57.0392 | 25.0716 | 33.8465 | 24.0875 | 20.1573 | 39.411 | 22.8707 | 15.8296 | 15.5694 | 15.6691 | 14.3196 | 15.6409 | 18.8261 |  |  |  | 62.5778 | 180.7659 | 154.618 | 110.3448 | 0.59326 | 0.58344 | 61.3549 |  |  | 11.7223 |  |  | 16.8962 | 17.2722 | 29.5563 | 16.3193 | 16.1662 | 21.0707 | 183.1386 | 238.2884 | 152.5155 | 155.9536 | 124.3104 |  | 66.9381 | 132.4801 | 66.3096 | 125.5966 | 113.1598 | 172.3733 |  | 103.6879 |  |  | 18.1587 | 22.4441 | 72.2882 | [6 empty] | 103.0687 |  |  | 51.2161 |  |  | 22.843 | 93.1824 | 269.651 | 11.1471 | 85.3743 | 169.0691 | 13.8378 | 81.927 | 191.0305 | 32.1205 | 145.9638 | 14.7608 | 136.8926 | 17.1003 | 143.4165 | 12.8067 | 85.7169 | 157.0896 | 37.6199 | 83.6027 | 199.0774 | 15.0355 | 71.2313 | 188.2827 | 16.876 | 132.4869 | 31.9545 | 140.119 | 19.4444 | 154.2238 | 1.7977 | 18.7373 | 1.9075 | 0.089753 | -38.2137 | 3.1235 | 348.12 | 49.79 | -1.0576 | -0.2982 | 0.2433 | 0.21206 | 0.33139 | -0.75117 | -0.30065 | -0.83519 | -1.0852 | 0.91731 | -1.4175 | -0.78415 | -1.5928 | -0.60653
42810.4472 | 615 | 18.4177 | 18.4991 | 18.487 | 18.4963 | 17.8002 | 16.3837 | 14.4303 | 16.5891 | 17.094 | 17.1892 | 17.1955 | 16.7084 | 15.7324 | 14.3648 | 14.7685 | 14.8255 | 15.5479 | 13.2607 | 13.9422 | 18.1438 |  |  |  | 16.5579 | 16.6095 | 24.8507 | 182.6247 | 167.6264 | 199.5394 | 17.0935 | 16.6077 | 21.4788 | 16.7523 | 16.5963 | 22.7621 | 77.3867 | 207.8219 |  | 114.0329 | 162.7333 | 161.8808 | 165.2718 |  | 7.3783 | 8.6922 | 7.1982 | 8.5457 | 9.2431 | 15.4923 | 122.7019 | 4.6191 | 7.8041 | 4.3891 | 9.5677 | 9.0133 | 42.0069 | 46.5448 | 42.7158 | 14.6898 |  |  | -0.96574 | 0.038199 | -0.072404 | -0.52898 | 0.072448 | -0.21336 | -0.15649 | 0.37965 | -0.13231 | 0.072628 | 0.39292 | -0.00065054 | 8.9057 | 0.96144 | 16.0243 | 16.626 | 17.1627 | 17.4757 | 17.4246 | 16.3697 | 14.6984 | 16.7618 | 17.0976 | 17.3962 | 17.4376 | 17.1401 | 16.2945 | 14.4778 | 56.3914 | 24.1943 | 34.5779 | 24.617 | 21.3367 | 39.4908 | 22.9258 | 15.8323 | 15.5749 | 15.675 | 14.3221 | 15.6531 | 18.8541 |  |  |  | 62.8484 | 181.1052 | 155.2154 | 110.8403 | 0.68727 | -0.060764 | 61.7502 |  |  | 11.7148 |  |  | 16.9041 | 17.2803 | 29.6162 | 16.32 | 16.1734 | 21.1101 | 183.8491 | 239.1962 | 152.6555 | 156.0255 | 125.588 |  | 67.219 | 132.7827 | 66.5154 | 130.1655 | 113.7208 | 173.4 |  | 103.971 |  |  | 18.2173 | 22.5265 | 73.0163 | [6 empty] | 104.3113 |  |  | 51.219 |  |  | 22.9302 | 93.6334 | 270.084 | 11.15 | 85.4792 | 169.6191 | 13.8812 | 82.3731 | 191.793 | 32.2533 | 146.1214 | 14.8112 | 137.3622 | 17.1367 | 143.8238 | 12.8131 | 85.656 | 157.6901 | 37.7862 | 84.1536 | 199.5053 | 15.0718 | 71.4581 | 188.6013 | 16.9368 | 132.6837 | 32.1276 | 140.4241 | 19.4504 | 154.6495 | 1.7093 | 18.7341 | 1.9103 | 0.090723 | -38.2577 | 3.1235 | 382.08 | 50.35 | -1.489 | 0.22866 | -0.31481 | -0.85092 | 0.31868 | -0.5469 | -0.46837 | -0.86036 | -1.086 | 0.81333 | -1.3361 | -0.85896 | -1.5852 | -0.61045
42810.4472 | 616 | 18.4236 | 18.4993 | 18.4903 | 18.5012 | 17.8017 | 16.381 | 14.4352 | 16.587 | 17.0987 | 17.192 | 17.1968 | 16.7141 | 15.7333 | 14.366 | 14.7666 | 14.8278 | 15.5516 | 13.2599 | 13.9455 | 18.1647 |  |  |  | 16.5621 | 16.6141 | 24.8975 | 182.964 | 167.874 | 200.3921 | 17.0897 | 16.6088 | 21.509 | 16.7582 | 16.5955 | 22.7905 | 77.7896 | 210.3867 |  | 114.435 | 163.1929 | 162.097 | 166.6045 |  | 7.3796 | 8.707 | 7.2002 | 8.5472 | 9.2197 | 15.5394 | 123.8996 | 4.5973 | 7.8124 | 4.4648 | 9.5796 | 9.0177 | 42.0135 | 46.5387 | 42.7231 | 14.6903 |  |  | -0.57279 | 0.13085 | 0.032736 | -0.10974 | 0.083616 | -0.10363 | 0.17995 | 0.61358 | -0.83482 | -0.40844 | 0.37464 | -0.00064726 | 8.9052 | 0.92653 | 16.0235 | 16.6328 | 17.1597 | 17.4841 | 17.4245 | 16.3719 | 14.6984 | 16.7651 | 17.102 | 17.3976 | 17.4365 | 17.1365 | 16.2965 | 14.4791 | 55.4605 | 24.042 | 33.0899 | 23.4737 | 21.0152 | 39.5667 | 22.9437 | 15.8313 | 15.5681 | 15.6705 | 14.3205 | 15.6649 | 18.8758 |  |  |  | 63.0865 | 181.2122 | 155.2384 | 111.4483 | 1.3702 | 0.28458 | 62.2535 |  |  | 11.7325 |  |  | 16.9069 | 17.2948 | 29.676 | 16.3215 | 16.1886 | 21.1434 | 184.2592 | 239.9786 | 153.0636 | 156.4226 | 126.53 |  | 67.4331 | 133.4296 | 66.7175 | 129.6397 | 114.182 | 173.3858 |  | 104.2601 |  |  | 18.2979 | 22.5792 | 73.0756 | [6 empty] | 106.0347 |  |  | 51.3953 |  |  | 23.0333 | 94.1189 | 270.4815 | 11.1793 | 85.719 | 170.0424 | 13.9188 | 82.5781 | 192.7028 | 32.3515 | 146.4858 | 14.8521 | 137.6317 | 17.1617 | 144.3964 | 12.8468 | 85.8834 | 158.2189 | 37.9667 | 84.736 | 200.1482 | 15.1125 | 71.7216 | 188.9846 | 16.9893 | 132.9647 | 32.2764 | 141.0274 | 19.4886 | 154.9761 | 2.1679 | 18.7304 | 1.9126 | 0.091288 | -38.2919 | 3.1235 | 370.9 | 49.63 | -1.1477 | 0.42323 | 0.21169 | -0.38758 | 0.34239 | -0.38117 | 0.5023 | -0.87867 | -1.0966 | 0.84681 | -1.2237 | -0.69155 | -1.6071 | -0.61868
42810.4472 | 617 | 18.4337 | 18.4971 | 18.4884 | 18.4962 | 17.7965 | 16.3818 | 14.4386 | 16.5844 | 17.0896 | 17.1896 | 17.194 | 16.708 | 15.7336 | 14.3598 | 14.776 | 14.8314 | 15.5572 | 13.2651 | 13.9402 | 18.1983 |  |  |  | 16.5652 | 16.6238 | 24.9485 | 183.2318 | 168.4655 | 199.8377 | 17.0923 | 16.5959 | 21.5329 | 16.7365 | 16.5936 | 22.8227 | 78.1493 | 212.1233 |  | 114.8417 | 163.6347 | 162.3158 | 166.787 |  | 7.3887 | 8.7221 | 7.2027 | 8.5503 | 9.2277 | 15.5721 | 124.0105 | 4.5338 | 7.8152 | 4.5408 | 9.5869 | 9.0147 | 42.0212 | 46.5292 | 42.7127 | 14.6715 |  |  | -0.76269 | -0.009113 | -0.072404 | -0.65449 | -0.009036 | 0.22756 | -0.19986 | 0.59124 | -0.62971 | 0.38502 | 0.30072 | -0.00059962 | 8.9053 | 0.93391 | 16.031 | 16.629 | 17.1534 | 17.4812 | 17.4268 | 16.3622 | 14.6955 | 16.754 | 17.0902 | 17.393 | 17.4291 | 17.1318 | 16.2924 | 14.4798 | 57.7916 | 24.8377 | 33.7045 | 24.07 | 20.1777 | 39.721 | 22.9766 | 15.8302 | 15.5722 | 15.6777 | 14.3228 | 15.6693 | 18.9032 |  |  |  | 63.3337 | 181.0622 | 155.1669 | 112.599 | 0.54849 | 0.35723 | 62.2282 |  |  | 11.7353 |  |  | 16.905 | 17.3015 | 29.7378 | 16.3262 | 16.1848 | 21.1703 | 184.8213 | 240.9631 | 153.4472 | 156.9188 | 125.654 |  | 67.6533 | 134.3001 | 66.9602 | 134.7435 | 114.855 | 173.5696 |  | 104.5629 |  |  | 18.3028 | 22.6229 | 72.8941 | [6 empty] | 108.6993 |  |  | 51.6016 |  |  | 23.1314 | 94.5953 | 271.2183 | 11.2393 | 85.9993 | 170.4241 | 13.9696 | 82.5731 | 193.1187 | 32.4535 | 147.0119 | 14.8698 | 137.9123 | 17.2165 | 145.1845 | 12.8884 | 86.0723 | 158.6444 | 38.1291 | 85.157 | 200.86 | 15.1608 | 72.0053 | 189.4515 | 17.0491 | 133.417 | 32.4903 | 141.4095 | 19.53 | 155.4866 | 1.6795 | 18.7293 | 1.9152 | 0.090832 | -38.161 | 3.1235 | 374.34 | 50.64 | -1.3236 | -0.11169 | -0.31483 | -0.94655 | -0.11256 | 0.56488 | -0.52939 | -0.84624 | -1.1119 | 0.73263 | -1.4645 | -0.75598 | -1.5986 | -0.64164
42810.4472 | 618 | 18.4328 | 18.5011 | 18.4972 | 18.5101 | 17.7967 | 16.389 | 14.433 | 16.5943 | 17.096 | 17.1912 | 17.202 | 16.7221 | 15.7395 | 14.3665 | 14.7766 | 14.844 | 15.5602 | 13.2741 | 13.9352 | 18.2267 |  |  |  | 16.5752 | 16.63 | 24.9967 | 183.4911 | 169.267 | 201.5075 | 17.0843 | 16.5989 | 21.5622 | 16.746 | 16.5906 | 22.8592 | 78.5512 | 212.046 |  | 115.245 | 164.1123 | 162.6266 | 165.7783 |  | 7.383 | 8.7382 | 7.2022 | 8.5702 | 9.2334 | 16.0085 | 124.238 | 4.4018 | 7.8246 | 4.5663 | 9.6133 | 9.0204 | 42.0265 | 46.52 | 42.7044 | 14.6521 |  |  | -0.71078 | -0.042625 | -0.23208 | -0.062426 | -0.084604 | 0.073796 | -0.39502 | 0.63067 | -0.31563 | -1.5626 | 0.40405 | -0.00065054 | 8.9051 | 1.0184 | 16.0282 | 16.6242 | 17.1521 | 17.4759 | 17.4259 | 16.3619 | 14.6991 | 16.7557 | 17.0861 | 17.3922 | 17.425 | 17.13 | 16.2909 | 14.4804 | 56.1497 | 24.3962 | 34.2056 | 25.3317 | 21.4748 | 39.7686 | 23.0139 | 15.8412 | 15.5742 | 15.6829 | 14.3237 | 15.6852 | 18.936 |  |  |  | 63.5814 | 181.2744 | 155.6496 | 113.7251 | 0.40829 | -0.095581 | 62.0322 |  |  | 11.7478 |  |  | 16.9075 | 17.308 | 29.8019 | 16.3239 | 16.1887 | 21.1886 | 185.0779 | 241.4463 | 153.6628 | 157.2312 | 124.3321 |  | 67.9053 | 134.7736 | 67.2132 | 134.1303 | 115.6541 | 173.7927 |  | 104.8983 |  |  | 18.321 | 22.6609 | 72.5658 | [6 empty] | 111.1529 |  |  | 51.8096 |  |  | 23.1923 | 94.9235 | 272.2509 | 11.2875 | 86.4345 | 170.8547 | 13.9982 | 82.7288 | 193.1094 | 32.5703 | 147.6099 | 14.9039 | 138.1691 | 17.248 | 146.0065 | 12.9285 | 86.2839 | 158.8333 | 38.2563 | 85.3611 | 201.2132 | 15.2076 | 72.237 | 189.8176 | 17.1094 | 134.0171 | 32.6445 | 141.69 | 19.5949 | 156.0313 | 1.6991 | 18.7281 | 1.916 | 0.089927 | -38.216 | 3.1235 | 360.66 | 50.02 | -1.28 | -0.24157 | -0.56367 | -0.29234 | -0.34469 | 0.32192 | -0.74481 | -0.80026 | -1.1157 | 0.78248 | -1.2765 | -0.80729 | -1.5555 | -0.6639
42810.4472 | 619 | 18.446 | 18.5062 | 18.5025 | 18.5114 | 17.8073 | 16.3989 | 14.4431 | 16.6005 | 17.0965 | 17.1987 | 17.205 | 16.7231 | 15.7455 | 14.3738 | 14.7832 | 14.8425 | 15.563 | 13.2717 | 13.952 | 18.243 |  |  |  | 16.5715 | 16.6411 | 25.0429 | 183.7165 | 169.5961 | 199.6807 | 17.092 | 16.6159 | 21.5972 | 16.7561 | 16.5972 | 22.9029 | 78.9318 | 210.9023 |  | 115.6542 | 164.4278 | 163.0734 | 165.3513 |  | 7.3737 | 8.7403 | 7.1974 | 8.5766 | 9.2428 | 16.4132 | 125.4298 | 4.3182 | 7.8092 | 4.4762 | 9.6163 | 9.0311 | 42.0267 | 46.5146 | 42.7092 | 14.6548 |  |  | -0.39142 | -0.038681 | -0.038232 | -0.35353 | 0.05142 | 0.088908 | -0.01784 | 0.87512 | -0.5182 | 0.029199 | 0.47737 | -0.00066204 | 8.9052 | 0.95809 | 16.0243 | 16.6273 | 17.1524 | 17.474 | 17.4176 | 16.3621 | 14.6906 | 16.7514 | 17.0915 | 17.3882 | 17.4246 | 17.132 | 16.2859 | 14.4774 | 52.1209 | 23.3905 | 32.4452 | 24.4847 | 21.4888 | 39.7706 | 23.0233 | 15.8321 | 15.5633 | 15.6797 | 14.3275 | 15.6858 | 18.9538 |  |  |  | 63.8095 | 182.5698 | 156.4485 | 114.3464 | 0.49966 | -0.081842 | 62.3429 |  |  | 11.7614 |  |  | 16.9052 | 17.3101 | 29.858 | 16.3195 | 16.1955 | 21.2311 | 185.5016 | 241.8349 | 153.8084 | 157.4993 | 124.5338 |  | 68.1245 | 134.9983 | 67.423 | 130.8706 | 116.2382 | 174.8108 |  | 105.1913 |  |  | 18.3653 | 22.7097 | 72.4529 | [6 empty] | 111.3635 |  |  | 52.1025 |  |  | 23.2241 | 95.1662 | 272.5106 | 11.324 | 86.7573 | 171.3832 | 13.999 | 83.0183 | 192.9413 | 32.6937 | 148.2102 | 14.8681 | 138.3483 | 17.2961 | 146.5968 | 12.969 | 86.6823 | 159.3188 | 38.3774 | 85.7817 | 201.5392 | 15.2581 | 72.4322 | 190.7387 | 17.1855 | 134.5316 | 32.7612 | 142.2818 | 19.6783 | 156.2377 | 1.5652 | 18.7246 | 1.9154 | 0.088711 | -38.2114 | 3.1235 | 367.5 | 50 | -0.94807 | -0.23012 | -0.22878 | -0.6957 | 0.26891 | 0.3536 | -0.15839 | -0.7978 | -1.1143 | 0.89706 | -0.82861 | -0.61061 | -1.5293 | -0.67284
42810.4472 | 620 | 18.4422 | 18.4992 | 18.4948 | 18.5068 | 17.8016 | 16.3894 | 14.4365 | 16.5888 | 17.095 | 17.1928 | 17.2 | 16.7156 | 15.7332 | 14.3627 | 14.7727 | 14.8332 | 15.5551 | 13.2607 | 13.9308 | 18.2587 |  |  |  | 16.5514 | 16.623 | 25.0847 | 183.8342 | 169.8361 | 201.0141 | 17.0807 | 16.6144 | 21.6244 | 16.7511 | 16.6038 | 22.9275 | 79.3113 | 212.4329 |  | 116.0771 | 164.6269 | 163.6353 | 165.6244 |  | 7.3884 | 8.7636 | 7.2075 | 8.5911 | 9.2641 | 16.7826 | 125.6377 | 4.3781 | 7.8282 | 4.4173 | 9.6361 | 9.0377 | 42.025 | 46.5097 | 42.7014 | 14.6407 |  |  | -0.42559 | -0.087965 | 0.058364 | -0.40084 | 0.12962 | -0.10626 | -0.2038 | 1.201 | -0.44581 | -0.34676 | 0.37404 | -0.00063576 | 8.9058 | 0.92868 | 16.0353 | 16.6312 | 17.154 | 17.4753 | 17.4154 | 16.3607 | 14.6998 | 16.7616 | 17.0985 | 17.3902 | 17.4311 | 17.1348 | 16.2903 | 14.4754 | 50.4645 | 23.373 | 31.9606 | 23.677 | 20.8614 | 39.8139 | 23.043 | 15.8314 | 15.5676 | 15.683 | 14.3241 | 15.7027 | 18.977 |  |  |  | 64.0492 | 183.8154 | 156.758 | 114.9702 | 0.52377 | 0.056485 | 62.6393 |  |  | 11.7878 |  |  | 16.9173 | 17.326 | 29.9429 | 16.34 | 16.2044 | 21.2645 | 185.8751 | 242.1079 | 154.3041 | 157.955 | 125.2335 |  | 68.3228 | 135.5512 | 67.6123 | 127.2944 | 116.8452 | 176.2838 |  | 105.4886 |  |  | 18.4397 | 22.7149 | 72.876 | [6 empty] | 114.4177 |  |  | 52.2641 |  |  | 23.2632 | 95.8636 | 273.8396 | 11.3152 | 87.1463 | 171.4729 | 13.9757 | 83.143 | 193.2701 | 32.7809 | 148.7872 | 14.9008 | 138.5415 | 17.3384 | 146.9935 | 12.9767 | 86.7383 | 159.6682 | 38.5272 | 86.4387 | 201.4207 | 15.2891 | 72.8249 | 191.5028 | 17.229 | 134.8661 | 32.8613 | 142.5923 | 19.727 | 156.6849 | 1.6338 | 18.7239 | 1.917 | 0.088494 | -38.2698 | 3.1235 | 365.78 | 49.78 | -0.98998 | -0.34704 | 0.28268 | -0.74082 | 0.42721 | -0.38681 | -0.5357 | -0.80994 | -1.1227 | 1.0214 | -0.63945 | -0.55444 | -1.5225 | -0.68143
42810.4472 | 621 | 18.4335 | 18.5063 | 18.487 | 18.4952 | 17.7976 | 16.3766 | 14.43 | 16.5849 | 17.0924 | 17.1915 | 17.1933 | 16.7092 | 15.7313 | 14.3674 | 14.7639 | 14.8418 | 15.5586 | 13.2644 | 13.9285 | 18.2809 |  |  |  | 16.5639 | 16.6412 | 25.1252 | 184.0199 | 169.8469 | 202.1888 | 17.0863 | 16.6136 | 21.6534 | 16.753 | 16.607 | 22.9663 | 79.6922 | 213.0871 |  | 116.4853 | 164.8295 | 164.0754 | 165.8009 |  | 7.3891 | 8.7672 | 7.2163 | 8.6028 | 9.3028 | 16.9191 | 124.6763 | 4.3852 | 7.8263 | 4.3875 | 9.6388 | 9.0443 | 42.0202 | 46.5168 | 42.7007 | 14.6352 |  |  | -0.48276 | -0.20756 | 0.12604 | -0.24905 | 0.35435 | -0.18905 | 0.046556 | 1.3016 | -0.44776 | -0.42355 | 0.11414 | 7.9972 | 8.8887 | 0.91687 | 16.0292 | 16.634 | 17.1581 | 17.4747 | 17.4226 | 16.3593 | 14.7085 | 16.755 | 17.0989 | 17.3969 | 17.4383 | 17.1399 | 16.2937 | 14.4779 | 48.8398 | 22.4627 | 31.3834 | 23.9215 | 20.4894 | 39.8287 | 23.0511 | 15.8306 | 15.5651 | 15.6823 | 14.3248 | 15.7137 | 19.004 |  |  |  | 64.2878 | 184.1454 | 156.8867 | 116.6206 | 0.5965 | -0.2021 | 62.805 |  |  | 11.7886 |  |  | 16.9208 | 17.3382 | 29.9922 | 16.3368 | 16.202 | 21.2941 | 186.0412 | 242.3742 | 154.6614 | 158.3833 | 124.4332 |  | 68.5495 | 133.9906 | 67.8554 | 127.6262 | 117.598 | 176.1827 |  | 105.8869 |  |  | 18.499 | 22.739 | 72.8303 | [6 empty] | 115.4533 |  |  | 52.5517 |  |  | 23.3259 | 96.0482 | 273.6047 | 11.3019 | 87.8952 | 171.6005 | 13.9613 | 83.3665 | 194.0896 | 32.8657 | 148.9294 | 14.9425 | 138.7597 | 17.3623 | 146.9393 | 12.9613 | 86.8819 | 160.0526 | 38.664 | 86.889 | 202.3244 | 15.3178 | 73.1524 | 191.9975 | 17.2653 | 135.0615 | 32.9481 | 142.8234 | 19.7899 | 157.0133 | 1.633 | 18.7204 | 1.9197 | 0.088451 | -38.0969 | 3.1235 | 378.22 | 48.35 | -1.0557 | -0.53309 | 0.41542 | -0.58394 | 0.70653 | -0.51607 | 0.2561 | -0.77936 | -1.0704 | 1.0433 | -0.45717 | -0.48936 | -1.5131 | -0.71857
42810.4472 | 622 | 18.4373 | 18.5074 | 18.4834 | 18.4879 | 17.7905 | 16.3764 | 14.4286 | 16.5834 | 17.0952 | 17.1917 | 17.1926 | 16.7118 | 15.7329 | 14.3679 | 14.7751 | 14.8395 | 15.5624 | 13.2752 | 13.9524 | 18.3056 |  |  |  | 16.5666 | 16.6442 | 25.1796 | 184.568 | 170.0758 | 204.1478 | 17.0989 | 16.6273 | 21.6862 | 16.7584 | 16.6161 | 23.0062 | 80.0829 | 212.9195 |  | 116.8784 | 165.1647 | 164.5877 | 164.4653 |  | 7.3876 | 8.7825 | 7.2294 | 8.7208 | 9.3178 | 16.9237 | 125.1362 | 4.4448 | 7.825 | 4.3788 | 9.6557 | 9.0477 | 42.0166 | 46.5474 | 42.6979 | 14.6204 |  |  | -0.55636 | -0.001225 | 0.007108 | -0.45932 | -0.051092 | 0.13162 | 0.047872 | 1.1642 | 0.026676 | 0.25725 | 0.1672 | 8.8766 | 8.8778 | 0.88887 | 16.0218 | 16.6221 | 17.1535 | 17.4787 | 17.4191 | 16.3611 | 14.6952 | 16.7595 | 17.0909 | 17.3877 | 17.4299 | 17.1281 | 16.2876 | 14.4703 | 48.2961 | 21.7428 | 29.3486 | 23.3559 | 20.5718 | 39.8671 | 23.0487 | 15.8258 | 15.5664 | 15.686 | 14.3261 | 15.713 | 19.0358 |  |  |  | 64.5557 | 184.4433 | 157.2342 | 117.3463 | 0.26079 | -0.081842 | 62.9094 |  |  | 11.7981 |  |  | 16.9019 | 17.3433 | 30.0489 | 16.3412 | 16.2046 | 21.317 | 186.2513 | 242.742 | 154.9031 | 158.652 | 125.0159 |  | 68.7608 | 133.595 | 68.0652 | 133.7675 | 118.1896 | 176.1166 |  | 106.1988 |  |  | 18.4828 | 22.7931 | 73.0427 | [6 empty] | 117.2064 |  |  | 52.6004 |  |  | 23.3876 | 96.4814 | 274.9129 | 11.3138 | 88.2763 | 171.8987 | 13.9833 | 83.6279 | 194.5586 | 32.9794 | 149.2139 | 14.9731 | 139.0989 | 17.3925 | 146.8982 | 13.0048 | 87.5316 | 160.2906 | 38.8449 | 87.2458 | 202.1241 | 15.3335 | 73.153 | 192.4746 | 17.3154 | 135.231 | 33.0614 | 143.593 | 19.8565 | 157.157 | 1.8567 | 18.719 | 1.921 | 0.089891 | -38.1303 | 3.1235 | 388.32 | 50.36 | -1.1356 | -0.040955 | 0.098654 | -0.79305 | -0.26829 | 0.43061 | 0.25969 | -0.78776 | -1.0517 | 0.89712 | -0.39224 | -0.26355 | -1.4612 | -0.72895
42810.4472 | 623 | 18.4426 | 18.5075 | 18.4921 | 18.497 | 17.7957 | 16.381 | 14.4345 | 16.5874 | 17.0933 | 17.1889 | 17.202 | 16.7159 | 15.7397 | 14.3646 | 14.7844 | 14.8446 | 15.5826 | 13.2719 | 13.964 | 18.3355 |  |  |  | 16.5685 | 16.6587 | 25.2313 | 184.7118 | 170.3673 | 201.6572 | 17.1041 | 16.6326 | 21.7251 | 16.7696 | 16.6271 | 23.0489 | 80.4676 | 213.2509 |  | 117.2705 | 165.6194 | 165.1558 | 161.8198 |  | 7.4018 | 8.8024 | 7.2385 | 8.7521 | 9.3146 | 16.908 | 125.8983 | 4.4585 | 7.8361 | 4.3908 | 9.6626 | 9.0404 | 42.0212 | 46.5444 | 42.6954 | 14.6076 |  |  | -0.49722 | 0.055943 | 0.005792 | -0.095282 | -0.078032 | -0.37107 | -0.31092 | 0.61818 | -0.65734 | -1.4629 | 0.19144 | 8.8748 | 8.8759 | 0.89461 | 16.0336 | 16.6246 | 17.1585 | 17.4792 | 17.418 | 16.3566 | 14.6962 | 16.7563 | 17.0977 | 17.3915 | 17.4284 | 17.1284 | 16.2884 | 14.471 | 47.401 | 21.922 | 28.6368 | 22.6753 | 20.5115 | 39.8713 | 23.0445 | 15.8266 | 15.5668 | 15.6932 | 14.3234 | 15.7278 | 19.0627 |  |  |  | 64.8194 | 184.4743 | 157.3977 | 117.5122 | 0.64918 | -0.078831 | 63.2519 |  |  | 11.8063 |  |  | 16.9118 | 17.3493 | 30.1044 | 16.3363 | 16.2135 | 21.3498 | 186.4936 | 243.3135 | 155.1425 | 158.8196 | 126.2711 |  | 68.9885 | 132.7889 | 68.2585 | 133.6419 | 118.7499 | 174.547 |  | 106.4728 |  |  | 18.5211 | 22.828 | 74.0716 | [6 empty] | 116.2421 |  |  | 52.5195 |  |  | 23.4332 | 96.8923 | 275.5172 | 11.3589 | 88.6233 | 172.375 | 14.0195 | 83.8176 | 194.9616 | 33.0769 | 149.5998 | 14.9902 | 139.4497 | 17.4445 | 147.1142 | 13.0297 | 87.6641 | 160.7242 | 38.9624 | 87.6412 | 201.9503 | 15.3764 | 73.7552 | 192.9338 | 17.3637 | 135.5868 | 33.167 | 144.1694 | 19.9186 | 157.4369 | 2.0092 | 18.717 | 1.9225 | 0.089558 | -38.1582 | 3.1235 | 382.53 | 49.75 | -1.0708 | 0.27678 | 0.089057 | -0.36121 | -0.33155 | -0.723 | -0.66181 | -0.81424 | -1.0222 | 0.9238 | -0.29228 | -0.18496 | -1.3732 | -0.72393
42810.4473 | 624 | 18.4476 | 18.5116 | 18.5015 | 18.4983 | 17.7956 | 16.3902 | 14.4356 | 16.5951 | 17.1032 | 17.1924 | 17.2073 | 16.7179 | 15.7311 | 14.3677 | 14.7773 | 14.8455 | 15.5758 | 13.2694 | 13.9525 | 18.3598 |  |  |  | 16.5647 | 16.6599 | 25.2784 | 184.8977 | 170.7245 | 202.8135 | 17.0993 | 16.6333 | 21.7515 | 16.7648 | 16.6346 | 23.0794 | 80.8512 | 214.5292 |  | 117.6896 | 166.1029 | 165.5237 | 162.0076 |  | 7.4057 | 8.794 | 7.2162 | 8.728 | 9.2804 | 16.8519 | 126.5926 | 4.3695 | 7.8398 | 4.3805 | 9.6734 | 9.044 | 42.0188 | 46.5591 | 42.6922 | 14.6012 |  |  | -0.62995 | -0.085993 | 0.12013 | -0.024314 | -0.10563 | -0.36516 | 0.15301 | 0.74172 | -0.3452 | 0.12382 | 0.15071 | 8.8752 | 8.8764 | 0.91353 | 16.0377 | 16.6259 | 17.1531 | 17.4841 | 17.4216 | 16.3647 | 14.701 | 16.7564 | 17.0948 | 17.3948 | 17.4295 | 17.1327 | 16.2907 | 14.4743 | 47.9213 | 21.6805 | 28.2807 | 22.1394 | 19.6533 | 39.898 | 23.052 | 15.8295 | 15.5764 | 15.6958 | 14.3306 | 15.7422 | 19.0927 |  |  |  | 65.0816 | 184.912 | 157.922 | 117.4179 | 0.49297 | -0.18535 | 63.1584 |  |  | 11.8148 |  |  | 16.92 | 17.3541 | 30.1765 | 16.3357 | 16.2285 | 21.3828 | 186.7798 | 243.4213 | 155.3291 | 159.0078 | 125.7512 |  | 69.2455 | 130.7877 | 68.5053 | 135.5028 | 119.4348 | 174.2676 |  | 106.8821 |  |  | 18.5762 | 22.9062 | 73.9086 | [6 empty] | 118.3446 |  |  | 52.4658 |  |  | 23.5065 | 97.2074 | 274.705 | 11.3741 | 88.932 | 172.9332 | 14.0758 | 84.1 | 195.3054 | 33.2157 | 150.0074 | 15.0356 | 139.7365 | 17.5106 | 147.4099 | 13.0419 | 87.771 | 161.1756 | 39.016 | 88.1543 | 201.7669 | 15.4135 | 74.0874 | 193.3946 | 17.3917 | 135.8937 | 33.239 | 144.3921 | 19.977 | 157.7798 | 1.7569 | 18.7168 | 1.924 | 0.08942 | -38.2033 | 3.1236 | 390.64 | 48.37 | -1.2067 | -0.34315 | 0.40558 | -0.18246 | -0.38571 | -0.71715 | 0.46422 | -0.79032 | -0.9575 | 0.90051 | -0.34694 | -0.14452 | -1.3639 | -0.71172
42810.4473 | 625 | 18.4385 | 18.5006 | 18.4864 | 18.5016 | 17.7907 | 16.385 | 14.4341 | 16.5881 | 17.0895 | 17.1914 | 17.198 | 16.7058 | 15.7328 | 14.3568 | 14.7819 | 14.8412 | 15.5703 | 13.2641 | 13.9517 | 18.3779 |  |  |  | 16.5679 | 16.6608 | 25.3236 | 185.0772 | 170.9683 | 202.7121 | 17.0987 | 16.6366 | 21.7705 | 16.7576 | 16.6255 | 23.1177 | 81.2347 | 214.4894 |  | 118.1376 | 166.5688 | 165.8406 | 163.0987 |  | 7.3971 | 8.7755 | 7.2297 | 8.7386 | 9.284 | 16.9096 | 127.4168 | 4.4216 | 7.8301 | 4.3418 | 9.6822 | 9.0492 | 42.0194 | 46.5664 | 42.6825 | 14.603 |  |  | -0.44596 | 0.22088 | 0.2371 | -0.18991 | 0.052076 | -0.15882 | -0.075012 | 0.84292 | 0.20804 | -0.24312 | 0.26138 | 8.8761 | 8.877 | 0.91031 | 16.0305 | 16.625 | 17.1466 | 17.4808 | 17.4121 | 16.3594 | 14.696 | 16.7494 | 17.0936 | 17.3926 | 17.4231 | 17.1303 | 16.2858 | 14.4697 | 46.8949 | 21.3096 | 27.6178 | 21.4277 | 18.7052 | 39.9001 | 23.0438 | 15.8245 | 15.5658 | 15.6883 | 14.3314 | 15.751 | 19.1153 |  |  |  | 65.3285 | 185.3352 | 158.6529 | 117.3189 | 0.52114 | 0.3019 | 63.0563 |  |  | 11.8277 |  |  | 16.9139 | 17.3584 | 30.2323 | 16.3294 | 16.2239 | 21.4108 | 186.8847 | 243.6423 | 155.644 | 159.3665 | 125.9433 |  | 69.5104 | 130.5516 | 68.7025 | 140.4438 | 120.1321 | 175.0414 |  | 107.2664 |  |  | 18.611 | 22.9678 | 74.1008 | [6 empty] | 120.0013 |  |  | 52.5092 |  |  | 23.5707 | 97.6588 | 274.9394 | 11.3906 | 89.2139 | 173.3584 | 14.142 | 84.6182 | 195.4944 | 33.3298 | 150.2848 | 15.0989 | 140.0856 | 17.5737 | 147.6192 | 13.045 | 88.3695 | 161.4105 | 39.0843 | 88.6605 | 202.0612 | 15.4737 | 74.3601 | 193.585 | 17.4386 | 136.2066 | 33.356 | 144.4947 | 20.0448 | 158.0968 | 1.9691 | 18.7163 | 1.9252 | 0.08874 | -38.1549 | 3.1236 | 392.26 | 48.16 | -1.0152 | 0.54994 | 0.56977 | -0.50992 | 0.27085 | -0.47301 | -0.32507 | -0.78588 | -0.94368 | 0.79222 | -0.23265 | -0.071818 | -1.3797 | -0.69995
42810.4473 | 626 | 18.4424 | 18.5026 | 18.4936 | 18.5008 | 17.7946 | 16.3785 | 14.4289 | 16.5897 | 17.0972 | 17.1961 | 17.1986 | 16.7127 | 15.7323 | 14.3698 | 14.778 | 14.8439 | 15.5713 | 13.2663 | 13.9632 | 18.4002 |  |  |  | 16.569 | 16.664 | 25.3628 | 185.2731 | 171.0638 | 203.639 | 17.0964 | 16.6333 | 21.8138 | 16.7552 | 16.6279 | 23.1473 | 81.6279 | 213.9083 |  | 118.5962 | 166.9928 | 166.2262 | 163.2767 |  | 7.3915 | 8.7666 | 7.2491 | 8.7667 | 9.283 | 17.0377 | 128.2836 | 4.5172 | 7.839 | 4.342 | 9.7007 | 9.0513 | 42.0013 | 46.5498 | 42.6811 | 14.6124 |  |  | -0.48473 | 0.013231 | -0.012608 | -0.56775 | 0.05996 | -0.58398 | -0.39437 | 0.94937 | -1.0855 | -0.27081 | 0.31583 | 8.8756 | 8.8766 | 0.91914 | 16.0367 | 16.6249 | 17.159 | 17.4799 | 17.4238 | 16.3699 | 14.6922 | 16.7531 | 17.0988 | 17.388 | 17.4325 | 17.1329 | 16.2922 | 14.4685 | 47.2475 | 22.4846 | 29.8039 | 22.6217 | 19.066 | 39.943 | 23.0835 | 15.838 | 15.5794 | 15.7 | 14.3285 | 15.7633 | 19.1429 |  |  |  | 65.5774 | 185.6685 | 159.0993 | 117.5028 | 1.1913 | 0.24563 | 62.9179 |  |  | 11.8354 |  |  | 16.92 | 17.3667 | 30.2966 | 16.3324 | 16.2237 | 21.4452 | 187.0278 | 243.9139 | 156.0791 | 159.8983 | 128.4485 |  | 69.764 | 130.4154 | 68.9072 | 139.5522 | 120.8331 | 175.2742 |  | 107.5658 |  |  | 18.6367 | 23.0019 | 75.3376 | [6 empty] | 118.7965 |  |  | 52.5707 |  |  | 23.6238 | 98.0536 | 275.8128 | 11.425 | 89.5454 | 173.7998 | 14.1915 | 85.2818 | 195.8377 | 33.351 | 150.5639 | 15.1559 | 140.4826 | 17.6338 | 148.0056 | 13.0392 | 88.5892 | 161.5781 | 39.1585 | 89.1303 | 202.1886 | 15.5273 | 74.9326 | 193.995 | 17.4897 | 136.5245 | 33.5057 | 144.782 | 20.1064 | 158.6002 | 2.0053 | 18.7174 | 1.9255 | 0.086663 | -38.1457 | 3.1236 | 404 | 49.5 | -1.0595 | 0.13459 | -0.13139 | -0.88167 | 0.29069 | -0.90721 | -0.74552 | -0.84611 | -0.93235 | 0.84616 | -0.26677 | -0.31008 | -1.3697 | -0.69595
42810.4473 | 627 | 18.4433 | 18.507 | 18.4887 | 18.4934 | 17.7919 | 16.3833 | 14.4278 | 16.5895 | 17.0982 | 17.1968 | 17.1936 | 16.7104 | 15.7355 | 14.3669 | 14.7731 | 14.8409 | 15.5661 | 13.2677 | 13.9627 | 18.4205 |  |  |  | 16.5647 | 16.6627 | 25.4095 | 185.5667 | 171.4271 | 204.6559 | 17.1052 | 16.64 | 21.8474 | 16.7611 | 16.6417 | 23.19 | 82.0175 | 213.7079 |  | 119.0408 | 167.4782 | 166.6685 | 162.9764 |  | 7.3967 | 8.7848 | 7.2582 | 8.77 | 9.2814 | 17.1845 | 128.8843 | 4.5292 | 7.8431 | 4.4236 | 9.7148 | 9.0527 | 41.9959 | 46.5099 | 42.6828 | 14.6173 |  |  | -0.74758 | 0.010603 | 0.042592 | -0.09331 | 0.096104 | -0.39473 | -0.44825 | 0.7864 | -0.57795 | 0.17291 | 0.21429 | 8.8727 | 8.8743 | 0.94972 | 16.0428 | 16.6271 | 17.1524 | 17.4733 | 17.4156 | 16.3611 | 14.6957 | 16.7491 | 17.0925 | 17.3899 | 17.4264 | 17.1348 | 16.2855 | 14.4755 | 50.4341 | 22.6242 | 31.17 | 23.8225 | 20.5277 | 40.0287 | 23.1077 | 15.8209 | 15.565 | 15.7025 | 14.3204 | 15.7652 | 19.1674 |  |  |  | 65.8312 | 185.6484 | 159.1374 | 117.9704 | 0.20265 | 0.084903 | 62.9172 |  |  | 11.8498 |  |  | 16.9195 | 17.3812 | 30.3572 | 16.3406 | 16.2241 | 21.4754 | 187.6197 | 244.1989 | 156.3663 | 160.3329 | 129.9074 |  | 70.0205 | 130.8236 | 69.1491 | 139.8513 | 121.5128 | 174.5097 |  | 107.8494 |  |  | 18.662 | 23.0743 | 75.0954 | [6 empty] | 117.5724 |  |  | 52.6125 |  |  | 23.6967 | 98.4132 | 275.8056 | 11.4482 | 89.7548 | 174.2169 | 14.2244 | 85.6509 | 196.3578 | 33.3621 | 150.8295 | 15.1765 | 140.919 | 17.673 | 148.0834 | 13.053 | 88.742 | 161.9692 | 39.2788 | 89.531 | 202.5946 | 15.5884 | 75.2664 | 194.5543 | 17.551 | 136.9263 | 33.648 | 145.1848 | 20.1615 | 158.8763 | 2.0098 | 18.7159 | 1.9254 | 0.08654 | -38.1809 | 3.1236 | 389.52 | 49.54 | -1.3171 | 0.12049 | 0.24149 | -0.35744 | 0.36812 | -0.74605 | -0.79502 | -0.87716 | -0.93477 | 0.86618 | -0.61071 | -0.45903 | -1.3466 | -0.69965
42810.4473 | 628 | 18.4395 | 18.5055 | 18.4944 | 18.4963 | 17.7886 | 16.3804 | 14.4296 | 16.5866 | 17.0922 | 17.1864 | 17.1911 | 16.7154 | 15.7325 | 14.3623 | 14.7789 | 14.8328 | 15.5705 | 13.2639 | 13.963 | 18.4386 |  |  |  | 16.5674 | 16.6621 | 25.4529 | 185.7588 | 172.3208 | 204.2836 | 17.1001 | 16.6406 | 21.8812 | 16.7591 | 16.6433 | 23.2231 | 82.3998 | 212.6976 |  | 119.4465 | 167.989 | 167.1304 | 163.9679 |  | 7.3851 | 8.7832 | 7.2497 | 8.7529 | 9.2568 | 17.1099 | 129.5302 | 4.5351 | 7.8407 | 4.4853 | 9.7091 | 9.0474 | 41.9887 | 46.4926 | 42.6804 | 14.6322 |  |  | -0.74824 | -0.032109 | -0.073716 | -0.31541 | 0.35369 | -0.44073 | -0.44562 | 0.44076 | 0.05353 | 0.056054 | 0.21489 | 8.8741 | 8.8751 | 0.94562 | 16.0342 | 16.6244 | 17.1486 | 17.4731 | 17.4205 | 16.3579 | 14.6896 | 16.7506 | 17.1004 | 17.3877 | 17.4239 | 17.128 | 16.2781 | 14.4701 | 46.9591 | 21.4695 | 30.2293 | 24.246 | 21.3627 | 40.0068 | 23.1243 | 15.8268 | 15.5707 | 15.7071 | 14.3298 | 15.7845 | 19.1979 |  |  |  | 66.0797 | 185.6856 | 159.9383 | 118.5365 | -0.060934 | -0.25913 | 62.991 |  |  | 11.8707 |  |  | 16.9236 | 17.3933 | 30.4277 | 16.3469 | 16.2363 | 21.5088 | 188.5445 | 244.795 | 156.5348 | 160.6192 | 130.7243 |  | 70.3275 | 131.3227 | 69.3809 | 138.8837 | 122.1272 | 173.3729 |  | 108.144 |  |  | 18.6772 | 23.1402 | 74.3869 | [6 empty] | 117.6986 |  |  | 52.731 |  |  | 23.7693 | 98.8634 | 275.6955 | 11.4718 | 89.9626 | 174.561 | 14.2594 | 85.9483 | 196.5754 | 33.4081 | 151.0119 | 15.188 | 141.084 | 17.7102 | 148.0685 | 13.1075 | 88.699 | 162.4188 | 39.3707 | 90.0224 | 203.1654 | 15.6326 | 75.7706 | 194.733 | 17.6233 | 137.3402 | 33.7658 | 145.3617 | 20.2267 | 159.0212 | 1.5658 | 18.7161 | 1.9272 | 0.086098 | -38.1788 | 3.1236 | 387.5 | 50.87 | -1.3172 | -0.20968 | -0.3177 | -0.65717 | 0.70611 | -0.78822 | -0.79258 | -0.88851 | -0.94009 | 0.91872 | -0.22718 | -0.35256 | -1.3597 | -0.70627
42810.4473 | 629 | 18.4456 | 18.5133 | 18.5033 | 18.5073 | 17.7973 | 16.3887 | 14.4384 | 16.5909 | 17.1014 | 17.1979 | 17.2039 | 16.7229 | 15.7373 | 14.3735 | 14.7887 | 14.8466 | 15.5912 | 13.2749 | 13.9723 | 18.4716 |  |  |  | 16.5722 | 16.6795 | 25.5019 | 185.8047 | 172.7627 | 202.6371 | 17.1017 | 16.6478 | 21.9068 | 16.7529 | 16.6336 | 23.2555 | 82.7519 | 212.9699 |  | 119.8645 | 168.4716 | 167.5814 | 164.4069 |  | 7.3806 | 8.7839 | 7.2476 | 8.7524 | 9.2731 | 17.2 | 130.434 | 4.5464 | 7.8517 | 4.5719 | 9.7285 | 9.061 | 41.9932 | 46.5072 | 42.6828 | 14.6535 |  |  | -0.78898 | 0.30433 | 0.088588 | -0.12945 | 0.06456 | 0.042908 | -0.16241 | 0.58401 | -0.20159 | -0.13738 | 0.32497 | 8.8741 | 8.8751 | 0.91346 | 16.0398 | 16.6289 | 17.1578 | 17.4734 | 17.4189 | 16.3599 | 14.6952 | 16.764 | 17.093 | 17.3866 | 17.4215 | 17.1326 | 16.2829 | 14.4719 | 42.6347 | 20.0665 | 27.8569 | 23.3886 | 20.7632 | 39.9523 | 23.1097 | 15.8261 | 15.576 | 15.7117 | 14.3367 | 15.7934 | 19.2345 |  |  |  | 66.3148 | 185.5729 | 160.3083 | 119.0728 | 0.40424 | -0.15693 | 62.9949 |  |  | 11.8736 |  |  | 16.9159 | 17.3934 | 30.4857 | 16.3436 | 16.2386 | 21.5366 | 188.7976 | 245.196 | 156.7014 | 160.8154 | 130.0429 |  | 70.5939 | 131.0988 | 69.5885 | 141.7165 | 122.7463 | 173.9271 |  | 108.3634 |  |  | 18.7193 | 23.2054 | 73.9755 | [6 empty] | 118.0792 |  |  | 52.8619 |  |  | 23.8345 | 99.4656 | 275.9951 | 11.4835 | 90.5043 | 174.7367 | 14.2973 | 86.462 | 197.0702 | 33.4537 | 151.1587 | 15.221 | 141.2926 | 17.7426 | 148.4258 | 13.1585 | 88.3573 | 162.7566 | 39.449 | 90.5907 | 203.7698 | 15.6823 | 76.3388 | 194.7889 | 17.6744 | 137.7899 | 33.8627 | 145.5319 | 20.2978 | 159.0838 | 1.3815 | 18.7124 | 1.9289 | 0.08743 | -38.142 | 3.1235 | 379.75 | 50.06 | -1.3502 | 0.64553 | 0.34828 | -0.42101 | 0.30172 | 0.24598 | -0.47855 | -0.85973 | -0.92621 | 0.86592 | 0.24687 | -0.090678 | -1.3585 | -0.71256
42810.4473 | 630 | 18.4513 | 18.5123 | 18.5021 | 18.5105 | 17.7969 | 16.3889 | 14.4378 | 16.5922 | 17.103 | 17.197 | 17.2069 | 16.725 | 15.7415 | 14.3677 | 14.7952 | 14.8598 | 15.5996 | 13.2824 | 13.9738 | 18.502 |  |  |  | 16.5753 | 16.6858 | 25.5586 | 185.7795 | 172.912 | 201.5062 | 17.0972 | 16.6546 | 21.9373 | 16.7518 | 16.6421 | 23.2869 | 83.124 | 213.7353 |  | 120.2742 | 168.917 | 167.9145 | 163.9081 |  | 7.3757 | 8.7942 | 7.2348 | 8.7441 | 9.3406 | 17.3222 | 131.5627 | 4.4871 | 7.8531 | 4.6664 | 9.7372 | 9.0602 | 42.01 | 46.5054 | 42.6855 | 14.6596 |  |  | -0.49853 | 0.005343 | 0.067564 | 0.008542 | 0.16313 | 0.06328 | 0.57816 | 0.68258 | -0.49894 | 0.032556 | 0.15726 | 8.8754 | 8.8765 | 0.89184 | 16.0319 | 16.6138 | 17.1505 | 17.4699 | 17.4135 | 16.3526 | 14.6908 | 16.7538 | 17.0866 | 17.3865 | 17.4208 | 17.1259 | 16.2766 | 14.4676 | 42.1326 | 19.7435 | 26.3177 | 21.8314 | 19.4134 | 39.959 | 23.1002 | 15.8237 | 15.5802 | 15.7133 | 14.3369 | 15.8045 | 19.2556 |  |  |  | 66.5492 | 185.6927 | 160.5456 | 119.7723 | 1.0351 | -0.025382 | 62.8587 |  |  | 11.8866 |  |  | 16.9171 | 17.4059 | 30.5474 | 16.3473 | 16.2419 | 21.5689 | 188.9494 | 245.4004 | 156.8949 | 161.036 | 130.3793 |  | 70.8619 | 130.3964 | 69.8104 | 144.9254 | 123.3897 | 174.4003 |  | 108.6505 |  |  | 18.765 | 23.2818 | 73.8023 | [6 empty] | 119.8439 |  |  | 53.0715 |  |  | 23.9003 | 99.9994 | 276.5967 | 11.5213 | 90.9422 | 175.0582 | 14.3496 | 86.5854 | 197.8213 | 33.5061 | 151.3604 | 15.2913 | 141.5904 | 17.784 | 148.8039 | 13.1278 | 88.5491 | 163.1483 | 39.5554 | 90.9843 | 204.2825 | 15.7201 | 76.5532 | 195.0299 | 17.6579 | 138.2606 | 33.9818 | 145.7256 | 20.377 | 159.3545 | 1.6858 | 18.7118 | 1.9299 | 0.089218 | -38.212 | 3.1236 | 381.11 | 48.96 | -1.072 | 0.085534 | 0.30416 | 0.10815 | 0.47972 | 0.29878 | 0.90312 | -0.85916 | -0.89851 | 0.80373 | 0.30345 | 0.079235 | -1.3305 | -0.7234
42810.4473 | 631 | 18.4505 | 18.5122 | 18.4944 | 18.5028 | 17.7909 | 16.3872 | 14.4284 | 16.5907 | 17.0881 | 17.1926 | 17.1984 | 16.7174 | 15.7238 | 14.3603 | 14.7905 | 14.8527 | 15.5904 | 13.2749 | 13.9628 | 18.5152 |  |  |  | 16.575 | 16.6914 | 25.5978 | 185.9318 | 173.1401 | 202.7286 | 17.0967 | 16.6534 | 21.9662 | 16.7528 | 16.6446 | 23.3288 | 83.5054 | 212.8458 |  | 120.6338 | 169.4831 | 168.147 | 164.7416 |  | 7.3779 | 8.8152 | 7.2441 | 8.7643 | 9.5388 | 17.6527 | 132.5422 | 4.5146 | 7.8563 | 4.7695 | 9.7465 | 9.0675 | 42.0383 | 46.508 | 42.6883 | 14.6592 |  |  | -0.59053 | -0.012397 | 0.083988 | -0.17611 | 0.032364 | 0.081024 | 0.61628 | 0.33168 | -0.35221 | -0.11179 | 0.15607 | 8.8736 | 8.8749 | 0.8997 | 16.0453 | 16.6219 | 17.1555 | 17.48 | 17.4204 | 16.3668 | 14.694 | 16.7494 | 17.0952 | 17.3962 | 17.4248 | 17.1378 | 16.2853 | 14.4738 | 44.3175 | 19.9728 | 26.1456 | 21.3637 | 18.7882 | 40.0033 | 23.0932 | 15.8192 | 15.5719 | 15.7126 | 14.3334 | 15.8083 | 19.2787 |  |  |  | 66.7796 | 185.6153 | 160.5996 | 120.7592 | 1.1646 | -0.052671 | 62.9295 |  |  | 11.8877 |  |  | 16.9232 | 17.4106 | 30.6154 | 16.3424 | 16.2441 | 21.599 | 189.1536 | 245.7729 | 157.2275 | 161.4064 | 130.2153 |  | 71.131 | 131.0808 | 70.0335 | 143.6224 | 123.9898 | 174.7757 |  | 109.0054 |  |  | 18.789 | 23.3501 | 73.8054 | [6 empty] | 119.1848 |  |  | 53.3794 |  |  | 23.9406 | 100.4812 | 277.9857 | 11.5732 | 90.6759 | 175.2939 | 14.3601 | 86.9148 | 198.0866 | 33.5798 | 151.6092 | 15.3402 | 142.0198 | 17.8038 | 149.1093 | 13.0941 | 88.9064 | 163.573 | 39.7087 | 91.3467 | 204.7618 | 15.7443 | 76.6452 | 195.4265 | 17.6599 | 138.6187 | 34.1021 | 145.8694 | 20.4276 | 159.76 | 1.8917 | 18.7099 | 1.9308 | 0.089934 | -38.2634 | 3.1236 | 372.47 | 49.83 | -1.1682 | -0.13029 | 0.33914 | -0.49108 | 0.21379 | 0.33828 | 0.93294 | -0.84464 | -0.90928 | 0.8651 | 0.065912 | 0.097536 | -1.3391 | -0.74236
42810.4473 | 632 | 18.4408 | 18.5064 | 18.4933 | 18.4901 | 17.7892 | 16.3742 | 14.4226 | 16.5901 | 17.0884 | 17.193 | 17.189 | 16.7148 | 15.7319 | 14.3542 | 14.7943 | 14.8539 | 15.5883 | 13.2721 | 13.9526 | 18.5403 |  |  |  | 16.5747 | 16.6836 | 25.6411 | 186.1155 | 173.4073 | 201.5364 | 17.1049 | 16.664 | 21.9979 | 16.7649 | 16.6591 | 23.371 | 83.888 | 213.3558 |  | 121.0112 | 169.9097 | 168.3213 | 164.792 |  | 7.3753 | 8.8347 | 7.2618 | 8.7957 | 9.5865 | 17.8369 | 133.4665 | 4.4732 | 7.8628 | 4.7751 | 9.7645 | 9.0745 | 42.031 | 46.5132 | 42.6931 | 14.6592 |  |  | -0.53007 | 0.056599 | 0.10108 | -0.3371 | 0.19533 | -0.043172 | 0.57159 | 0.30408 | -1.131 | -0.22445 | 0.28701 | 3.0624 | 8.8923 | 0.89289 | 16.0545 | 16.6241 | 17.1536 | 17.4765 | 17.4277 | 16.3685 | 14.6969 | 16.7536 | 17.0971 | 17.3987 | 17.434 | 17.1378 | 16.2891 | 14.4737 | 48.3368 | 21.532 | 26.7128 | 21.2521 | 19.3448 | 40.106 | 23.0955 | 15.8138 | 15.5627 | 15.7154 | 14.3303 | 15.8178 | 19.3209 |  |  |  | 67.0339 | 185.6741 | 161.2314 | 121.2984 | 0.74278 | 0.56312 | 63.0903 |  |  | 11.892 |  |  | 16.9191 | 17.4184 | 30.6744 | 16.3325 | 16.2449 | 21.6289 | 189.3263 | 246.0575 | 157.4063 | 161.6838 | 129.434 |  | 71.3841 | 133.1779 | 70.2199 | 141.7908 | 124.5103 | 174.1459 |  | 109.288 |  |  | 18.76 | 23.3826 | 73.729 | [6 empty] | 118.8772 |  |  | 53.538 |  |  | 23.9605 | 100.9174 | 278.5464 | 11.6551 | 90.8602 | 175.3624 | 14.4026 | 87.4168 | 198.6409 | 33.7021 | 151.7981 | 15.3716 | 142.4495 | 17.8405 | 149.4633 | 13.1214 | 89.3509 | 163.9521 | 39.8595 | 91.7816 | 204.7552 | 15.751 | 76.9696 | 195.7265 | 17.6836 | 138.9459 | 34.1761 | 145.9481 | 20.4657 | 160.3006 | 1.6452 | 18.7089 | 1.9322 | 0.089601 | -38.2163 | 3.1236 | 376.49 | 49.36 | -1.1054 | 0.27841 | 0.37205 | -0.67945 | 0.5254 | -0.247 | 0.89877 | -0.81356 | -0.96064 | 0.93784 | -0.36855 | 0.034777 | -1.326 | -0.748
42810.4474 | 633 | 18.4481 | 18.5083 | 18.4916 | 18.5009 | 17.7934 | 16.3825 | 14.4287 | 16.5903 | 17.0875 | 17.1879 | 17.1902 | 16.7194 | 15.7274 | 14.3607 | 14.7916 | 14.8583 | 15.5896 | 13.2699 | 13.9601 | 18.5643 |  |  |  | 16.5694 | 16.6933 | 25.6936 | 186.3521 | 173.5868 | 201.4327 | 17.1043 | 16.6589 | 22.041 | 16.764 | 16.6653 | 23.4094 | 84.2437 | 213.2689 |  | 121.4175 | 170.2286 | 168.4945 | 164.5992 |  | 7.3935 | 8.851 | 7.2747 | 8.8076 | 9.6392 | 17.8723 | 134.0535 | 4.3866 | 7.8725 | 4.7543 | 9.7766 | 9.082 | 42.0247 | 46.5107 | 42.6961 | 14.6603 |  |  | -0.26591 | -0.061681 | 0.08596 | -0.063082 | 0.2249 | -0.11414 | 0.34817 | 0.55576 | -0.43044 | -2.0193 | 0.41319 | 4.6234 | 8.8988 | 0.88115 | 16.0508 | 16.628 | 17.1529 | 17.473 | 17.4211 | 16.3679 | 14.6961 | 16.7554 | 17.0927 | 17.3962 | 17.4306 | 17.1325 | 16.2866 | 14.4697 | 50.2515 | 22.9828 | 30.4513 | 21.7479 | 20.2974 | 40.1771 | 23.1354 | 15.8228 | 15.5719 | 15.7126 | 14.3369 | 15.831 | 19.3425 |  |  |  | 67.2558 | 185.6606 | 161.4568 | 121.3996 | 1.3755 | 0.11972 | 63.3077 |  |  | 11.9096 |  |  | 16.9265 | 17.4281 | 30.7462 | 16.3439 | 16.2564 | 21.6645 | 189.664 | 246.1423 | 157.4648 | 161.6955 | 128.6785 |  | 71.6284 | 134.2974 | 70.4069 | 143.8953 | 125.122 | 174.0533 |  | 109.5273 |  |  | 18.7933 | 23.3814 | 73.5749 | [6 empty] | 118.6215 |  |  | 53.6111 |  |  | 24.0027 | 101.2465 | 278.1659 | 11.7241 | 91.2754 | 175.468 | 14.4228 | 87.781 | 199.2089 | 33.8229 | 151.9286 | 15.4273 | 142.7767 | 17.9085 | 150.1261 | 13.1297 | 89.6153 | 164.2648 | 39.9673 | 92.0659 | 205.3045 | 15.7637 | 77.2997 | 196.5539 | 17.7035 | 139.2005 | 34.233 | 146.0581 | 20.527 | 160.9672 | 2.0048 | 18.7071 | 1.9327 | 0.089876 | -38.2564 | 3.1235 | 380.22 | 49.11 | -0.78288 | -0.29065 | 0.34312 | -0.29393 | 0.56379 | -0.40165 | 0.7015 | -0.78352 | -0.98483 | 0.90512 | -0.57289 | -0.37594 | -1.307 | -0.74267
42810.4474 | 634 | 18.4422 | 18.5066 | 18.502 | 18.4937 | 17.7891 | 16.3828 | 14.4235 | 16.585 | 17.0975 | 17.1907 | 17.1928 | 16.7134 | 15.7291 | 14.3642 | 14.7881 | 14.849 | 15.5881 | 13.2743 | 13.958 | 18.5796 |  |  |  | 16.5742 | 16.6958 | 25.7274 | 186.2309 | 173.6479 | 198.963 | 17.1144 | 16.673 | 22.0737 | 16.7681 | 16.6675 | 23.4492 | 84.585 | 213.8969 |  | 121.7726 | 170.5981 | 168.8579 | 164.8431 |  | 7.4123 | 8.8542 | 7.2913 | 8.827 | 9.6918 | 17.9459 | 134.7826 | 4.3781 | 7.8688 | 4.739 | 9.7815 | 9.0812 | 42.0246 | 46.5027 | 42.6881 | 14.6476 |  |  | -0.73181 | 0.081571 | 0.078732 | -0.07097 | 0.12436 | 0.26107 | 0.41783 | 0.91191 | -0.40475 | -0.75105 | 0.20714 | 8.8765 | 8.8776 | 0.87102 | 16.0513 | 16.6273 | 17.1504 | 17.4712 | 17.421 | 16.3647 | 14.6878 | 16.7505 | 17.0945 | 17.3841 | 17.4231 | 17.1328 | 16.2872 | 14.4718 | 53.8358 | 26.8692 | 33.5952 | 23.1962 | 21.6391 | 40.3342 | 23.1985 | 15.8194 | 15.5749 | 15.7193 | 14.3335 | 15.838 | 19.3719 |  |  |  | 67.4871 | 185.6889 | 161.78 | 120.9921 | 1.6298 | 1.7232 | 63.6407 |  |  | 11.9183 |  |  | 16.9234 | 17.4316 | 30.8004 | 16.3346 | 16.2586 | 21.6939 | 189.8712 | 246.0628 | 157.5785 | 161.731 | 129.2675 |  | 71.8753 | 134.9454 | 70.6277 | 147.288 | 125.8615 | 175.1814 |  | 109.8054 |  |  | 18.779 | 23.4513 | 74.3257 | [6 empty] | 119.6129 |  |  | 53.6041 |  |  | 24.0476 | 101.6623 | 278.0284 | 11.7964 | 91.3344 | 175.6498 | 14.4573 | 88.1367 | 199.72 | 33.9327 | 152.1438 | 15.486 | 143.0682 | 17.981 | 150.5651 | 13.1388 | 89.793 | 164.8114 | 40.0215 | 92.2862 | 205.5952 | 15.808 | 77.6747 | 197.081 | 17.7176 | 139.5022 | 34.3114 | 146.295 | 20.5999 | 161.2748 | 1.9235 | 18.7085 | 1.9337 | 0.088653 | -38.1918 | 3.1236 | 367.02 | 50.77 | -1.2954 | 0.33424 | 0.32838 | -0.31177 | 0.4193 | 0.60753 | 0.76857 | -0.79073 | -0.99466 | 0.84204 | -0.9526 | -0.71788 | -1.3008 | -0.72285
42810.4474 | 635 | 18.446 | 18.5154 | 18.4913 | 18.4957 | 17.7882 | 16.38 | 14.4255 | 16.5853 | 17.0905 | 17.1862 | 17.1987 | 16.7097 | 15.7315 | 14.3602 | 14.7914 | 14.8539 | 15.59 | 13.28 | 13.9594 | 18.6134 |  |  |  | 16.5805 | 16.6971 | 25.7843 | 186.2724 | 173.5256 | 200.6056 | 17.1124 | 16.6694 | 22.0949 | 16.7689 | 16.6735 | 23.4873 | 84.9169 | 212.8385 |  | 122.1264 | 170.9781 | 169.2095 | 164.2046 |  | 7.4356 | 8.8855 | 7.3023 | 8.8524 | 9.7398 | 17.971 | 135.9957 | 4.415 | 7.8726 | 4.6325 | 9.8046 | 9.0809 | 42.0565 | 46.5078 | 42.6874 | 14.6477 |  |  | -0.71932 | 0.12954 | 0.12736 | -0.50269 | 0.27352 | 0.015312 | 0.26866 | 1.2181 | 0.31702 | -0.14913 | 0.32616 | 8.8723 | 8.8732 | 0.88922 | 16.0494 | 16.6231 | 17.1561 | 17.4638 | 17.4138 | 16.3569 | 14.6863 | 16.7466 | 17.0915 | 17.3905 | 17.4268 | 17.1355 | 16.2842 | 14.4725 | 60.3535 | 30.9712 | 41.4881 | 27.1639 | 23.6575 | 40.5523 | 23.3284 | 15.8132 | 15.5761 | 15.7247 | 14.3411 | 15.8545 | 19.4016 |  |  |  | 67.7301 | 185.9305 | 162.2327 | 121.0537 | 1.3563 | 0.99955 | 64.0157 |  |  | 11.9269 |  |  | 16.9275 | 17.4418 | 30.8701 | 16.3384 | 16.2683 | 21.7352 | 190.0526 | 246.1066 | 157.642 | 161.7881 | 129.3769 |  | 72.1111 | 135.5263 | 70.8796 | 145.276 | 126.4664 | 175.9383 |  | 110.0562 |  |  | 18.7565 | 23.4904 | 73.9743 | [6 empty] | 120.3638 |  |  | 53.6808 |  |  | 24.0749 | 102.0281 | 277.6663 | 11.8535 | 92.164 | 175.7906 | 14.5081 | 88.2873 | 200.1835 | 34.0966 | 152.431 | 15.5528 | 143.3687 | 18.0554 | 151.0013 | 13.1093 | 90.2739 | 165.178 | 40.1419 | 92.7804 | 205.2427 | 15.8493 | 78.2205 | 197.1018 | 17.7329 | 139.8902 | 34.4003 | 146.5103 | 20.6487 | 161.9087 | 1.7189 | 18.7071 | 1.9345 | 0.087655 | -38.2182 | 3.1236 | 360.51 | 49.12 | -1.2865 | 0.42123 | 0.41767 | -0.82979 | 0.62187 | 0.14714 | 0.61632 | -0.78502 | -1.0015 | 0.92347 | -1.651 | -1.5797 | -1.2704 | -0.71563
42810.4474 | 636 | 18.4454 | 18.5113 | 18.4885 | 18.4969 | 17.7915 | 16.3771 | 14.4287 | 16.5837 | 17.0924 | 17.1866 | 17.1997 | 16.7082 | 15.7358 | 14.36 | 14.7977 | 14.8642 | 15.603 | 13.2717 | 13.969 | 18.6358 |  |  |  | 16.579 | 16.7149 | 25.8343 | 186.6751 | 173.6305 | 202.2552 | 17.1129 | 16.6799 | 22.1325 | 16.7709 | 16.6838 | 23.5199 | 85.2464 | 211.171 |  | 122.4755 | 171.2031 | 169.5066 | 164.1161 |  | 7.4754 | 8.9169 | 7.3203 | 8.8884 | 9.7696 | 17.9437 | 136.7797 | 4.4273 | 7.8762 | 4.5579 | 9.8235 | 9.0871 | 42.0893 | 46.5204 | 42.6842 | 14.6446 |  |  | -0.53402 | 0.048715 | 0.20358 | -0.62163 | 0.23278 | -1.0453 | -0.64933 | 0.91914 | -0.65929 | 0.3374 | 0.23793 | 8.8764 | 8.8774 | 0.89216 | 16.0434 | 16.6138 | 17.1423 | 17.4668 | 17.4083 | 16.3527 | 14.6833 | 16.749 | 17.0922 | 17.3729 | 17.4096 | 17.1222 | 16.2811 | 14.4652 | 64.7146 | 30.223 | 43.6392 | 28.9503 | 24.2025 | 40.7733 | 23.4371 | 15.8193 | 15.5815 | 15.7229 | 14.3445 | 15.8608 | 19.4261 |  |  |  | 67.9736 | 185.6579 | 162.4304 | 121.5918 | 1.246 | 0.55747 | 64.3173 |  |  | 11.9278 |  |  | 16.9236 | 17.4456 | 30.9313 | 16.3377 | 16.2662 | 21.757 | 189.9545 | 246.1293 | 157.6813 | 161.8837 | 129.466 |  | 72.3575 | 136.4809 | 71.0958 | 142.6295 | 127.0882 | 175.8823 |  | 110.2904 |  |  | 18.8449 | 23.5327 | 74.1205 | [6 empty] | 119.2818 |  |  | 53.8005 |  |  | 24.1119 | 102.0972 | 279.0088 | 11.8492 | 92.5407 | 176.2413 | 14.5302 | 88.5693 | 199.8174 | 34.2539 | 152.7431 | 15.575 | 143.995 | 18.133 | 151.2199 | 13.0924 | 90.4822 | 165.5195 | 40.2524 | 93.2471 | 205.227 | 15.8679 | 78.5293 | 197.2818 | 17.7573 | 140.3135 | 34.5661 | 146.7028 | 20.7134 | 162.0545 | 2.1596 | 18.7063 | 1.9351 | 0.086287 | -38.2202 | 3.1236 | 382.07 | 48.52 | -1.1104 | 0.25833 | 0.5281 | -0.9228 | 0.57367 | -1.2156 | -0.95811 | -0.77835 | -1.02 | 1.0233 | -2.1095 | -1.8059 | -1.2553 | -0.72163
42810.4474 | 637 | 18.4431 | 18.5007 | 18.4851 | 18.4918 | 17.7853 | 16.3672 | 14.4223 | 16.5762 | 17.0915 | 17.1799 | 17.19 | 16.7016 | 15.7265 | 14.3544 | 14.7901 | 14.8571 | 15.6027 | 13.2775 | 13.9626 | 18.666 |  |  |  | 16.5692 | 16.716 | 25.8838 | 187.0536 | 173.7893 | 202.0752 | 17.1187 | 16.6812 | 22.1691 | 16.7697 | 16.6815 | 23.5622 | 85.5941 | 210.9353 |  | 122.8208 | 171.3776 | 169.675 | 164.3029 |  | 7.4973 | 8.9392 | 7.3325 | 8.909 | 9.7629 | 17.8538 | 137.0071 | 4.5361 | 7.8835 | 4.5832 | 9.8397 | 9.0872 | 42.1014 | 46.543 | 42.6851 | 14.6433 |  |  | -0.66872 | 0.089455 | 0.058364 | 0.17873 | -0.54064 | -0.74957 | -0.1992 | 0.96448 | 0.027843 | -0.17347 | 0.32616 | 8.8756 | 8.8768 | 0.8765 | 16.0464 | 16.6204 | 17.1526 | 17.4733 | 17.4116 | 16.3575 | 14.6848 | 16.7457 | 17.0887 | 17.3873 | 17.4226 | 17.1243 | 16.2818 | 14.4678 | 66.1017 | 29.1747 | 42.3427 | 29.9891 | 25.6321 | 40.9453 | 23.5173 | 15.8191 | 15.5741 | 15.7318 | 14.3367 | 15.8749 | 19.4598 |  |  |  | 68.2137 | 185.6868 | 162.4115 | 121.9741 | 0.1366 | -0.11402 | 64.6263 |  |  | 11.9412 |  |  | 16.9276 | 17.4571 | 31.0011 | 16.3396 | 16.2671 | 21.7903 | 190.0097 | 246.2795 | 157.8046 | 162.0401 | 129.7189 |  | 72.6351 | 137.1167 | 71.2737 | 138.3828 | 127.633 | 175.0679 |  | 110.5561 |  |  | 18.8857 | 23.5736 | 74.0582 | [6 empty] | 117.4536 |  |  | 53.7044 |  |  | 24.16 | 102.4832 | 279.1977 | 11.8771 | 92.4275 | 176.5867 | 14.551 | 89.1267 | 199.5037 | 34.3603 | 153.1934 | 15.6072 | 144.4464 | 18.2107 | 151.4839 | 13.0982 | 90.5729 | 165.6303 | 40.3043 | 93.595 | 205.0989 | 15.892 | 78.8055 | 197.5408 | 17.7742 | 140.6784 | 34.7069 | 147.0363 | 20.7593 | 162.5236 | 2.0333 | 18.7062 | 1.9375 | 0.086453 | -38.1419 | 3.1236 | 405.59 | 50.33 | -1.2423 | 0.35008 | 0.28277 | 0.49484 | -0.87412 | -1.0293 | -0.5306 | -0.77506 | -1.0311 | 1.1643 | -2.2433 | -1.6525 | -1.2472 | -0.72341
42810.4474 | 638 | 18.437 | 18.5088 | 18.4879 | 18.4903 | 17.791 | 16.3776 | 14.4194 | 16.5885 | 17.0907 | 17.1837 | 17.192 | 16.7131 | 15.725 | 14.3606 | 14.7958 | 14.8664 | 15.6097 | 13.2813 | 13.9525 | 18.6792 |  |  |  | 16.5781 | 16.7177 | 25.931 | 187.4418 | 173.9141 | 204.4424 | 17.1199 | 16.678 | 22.1988 | 16.7609 | 16.676 | 23.5905 | 85.9287 | 211.2361 |  | 123.2243 | 171.5678 | 169.8476 | 165.3368 |  | 7.5196 | 8.9562 | 7.3296 | 8.8913 | 9.7093 | 17.7446 | 136.8844 | 4.6688 | 7.8896 | 4.5427 | 9.8523 | 9.0966 | 42.1209 | 46.5849 | 42.6932 | 14.6575 |  |  | -0.62667 | 0.19854 | 0.23316 | 0.036142 | -0.26334 | -0.42496 | -0.56259 | 1.1307 | -0.33295 | -1.8563 | 0.28622 | 8.8741 | 8.8753 | 0.9175 | 16.0547 | 16.6219 | 17.1521 | 17.4748 | 17.4191 | 16.3577 | 14.6882 | 16.7527 | 17.0898 | 17.3899 | 17.4302 | 17.1216 | 16.2834 | 14.4684 | 60.0252 | 26.1119 | 38.273 | 28.1093 | 25.0644 | 40.9771 | 23.5454 | 15.8162 | 15.5698 | 15.7315 | 14.3324 | 15.8803 | 19.4771 |  |  |  | 68.439 | 185.6884 | 162.0828 | 122.2997 | 0.35095 | -0.36019 | 64.5518 |  |  | 11.951 |  |  | 16.9213 | 17.4627 | 31.0711 | 16.3336 | 16.273 | 21.8209 | 190.2095 | 246.6338 | 157.9807 | 162.2391 | 130.3831 |  | 72.8882 | 136.8055 | 71.5138 | 136.1865 | 128.0426 | 174.3648 |  | 110.8432 |  |  | 18.9097 | 23.639 | 74.2443 | [6 empty] | 116.3717 |  |  | 53.9413 |  |  | 24.2097 | 102.8784 | 279.7482 | 11.8859 | 92.6359 | 176.6782 | 14.5983 | 89.4894 | 199.2816 | 34.4758 | 153.8759 | 15.6501 | 144.6838 | 18.2848 | 151.8129 | 13.1475 | 90.7624 | 165.7504 | 40.3853 | 93.9623 | 205.5774 | 15.9375 | 79.0251 | 197.7991 | 17.7872 | 140.8976 | 34.7937 | 147.3766 | 20.8002 | 162.9538 | 1.8669 | 18.7064 | 1.9404 | 0.086214 | -38.1686 | 3.1236 | 409.01 | 49.49 | -1.2056 | 0.52155 | 0.56519 | 0.22253 | -0.60995 | -0.77483 | -0.89152 | -0.7841 | -1.0135 | 1.2427 | -1.5644 | -1.197 | -1.2631 | -0.72416
42810.4474 | 639 | 18.4513 | 18.5169 | 18.4917 | 18.499 | 17.791 | 16.3795 | 14.4326 | 16.5877 | 17.0929 | 17.1887 | 17.1944 | 16.7165 | 15.7246 | 14.3592 | 14.7951 | 14.8732 | 15.6182 | 13.2853 | 13.9469 | 18.7116 |  |  |  | 16.5809 | 16.7247 | 25.9837 | 187.7633 | 174.2007 | 203.874 | 17.12 | 16.6812 | 22.2281 | 16.757 | 16.6809 | 23.6253 | 86.2921 | 210.111 |  | 123.6193 | 171.8255 | 170.1386 | 166.9068 |  | 7.5272 | 8.9723 | 7.3254 | 8.8861 | 9.6782 | 17.6947 | 137.548 | 4.7379 | 7.8969 | 4.4514 | 9.8657 | 9.099 | 42.1187 | 46.6215 | 42.6939 | 14.673 |  |  | -1.019 | 0.24453 | 0.11553 | -0.083454 | -0.00312 | -0.94802 | -0.6191 | 1.086 | -0.35026 | 0.30005 | 0.24171 | 8.8746 | 8.8755 | 0.9111 | 16.0546 | 16.6253 | 17.1508 | 17.4787 | 17.4183 | 16.3603 | 14.6907 | 16.7562 | 17.0905 | 17.3889 | 17.4297 | 17.1257 | 16.2834 | 14.4723 | 56.0984 | 23.761 | 33.7207 | 25.6537 | 23.0901 | 40.9958 | 23.5456 | 15.8175 | 15.5713 | 15.7365 | 14.3396 | 15.8943 | 19.5179 |  |  |  | 68.6676 | 185.1776 | 161.8679 | 122.5873 | 0.26404 | -0.18422 | 64.6452 |  |  | 11.961 |  |  | 16.9234 | 17.4731 | 31.1376 | 16.3398 | 16.2803 | 21.8552 | 190.527 | 246.8785 | 158.1158 | 162.3564 | 130.3902 |  | 73.0723 | 135.33 | 71.7184 | 138.5881 | 128.5337 | 173.6452 |  | 111.0651 |  |  | 18.9616 | 23.7077 | 74.5026 | [6 empty] | 117.0832 |  |  | 54.1297 |  |  | 24.2948 | 103.2985 | 280.5459 | 11.9182 | 93.2073 | 176.7895 | 14.6755 | 89.7006 | 199.3931 | 34.6189 | 154.4602 | 15.6817 | 144.9529 | 18.3429 | 152.1155 | 13.1608 | 90.8267 | 165.9026 | 40.4972 | 94.3052 | 205.7819 | 15.9595 | 79.3011 | 197.99 | 17.8116 | 141.0946 | 34.8509 | 147.822 | 20.8418 | 163.3271 | 1.6565 | 18.7044 | 1.944 | 0.086591 | -38.2354 | 3.1236 | 416.64 | 49.1 | -1.5364 | 0.57884 | 0.39787 | -0.33815 | -0.066386 | -1.1572 | -0.93515 | -0.77745 | -0.96495 | 1.1968 | -1.1258 | -0.69119 | -1.2928 | -0.72373
42810.4474 | 640 | 18.4521 | 18.5137 | 18.4887 | 18.5008 | 17.7942 | 16.3735 | 14.4207 | 16.5813 | 17.0951 | 17.1891 | 17.1956 | 16.7163 | 15.7375 | 14.3589 | 14.8006 | 14.8811 | 15.6212 | 13.2959 | 13.9607 | 18.746 |  |  |  | 16.5835 | 16.7424 | 26.0425 | 187.9946 | 174.2752 | 203.8931 | 17.113 | 16.6944 | 22.2631 | 16.7659 | 16.6992 | 23.6867 | 86.7004 | 207.3276 |  | 123.9705 | 172.149 | 170.4573 | 168.7363 |  | 7.5288 | 8.965 | 7.3272 | 8.8666 | 9.6757 | 17.8854 | 138.1919 | 4.7102 | 7.8915 | 4.4182 | 9.8776 | 9.1022 | 42.1178 | 46.6449 | 42.6918 | 14.6785 |  |  | -0.52745 | 0.13085 | -0.054004 | -0.15179 | -0.009036 | -1.4356 | -0.67496 | 1.1445 | -0.2625 | -0.24585 | 0.42233 | 8.8754 | 8.8764 | 0.88571 | 16.0465 | 16.6246 | 17.1528 | 17.4737 | 17.4122 | 16.3569 | 14.69 | 16.755 | 17.0932 | 17.3929 | 17.4244 | 17.1208 | 16.2804 | 14.4677 | 51.543 | 22.3868 | 30.5031 | 23.9524 | 21.3478 | 40.9696 | 23.5309 | 15.8126 | 15.5799 | 15.7422 | 14.3357 | 15.9055 | 19.5409 |  |  |  | 68.8954 | 184.7709 | 161.8294 | 122.4904 | 0.27741 | -0.40856 | 64.6434 |  |  | 11.9752 |  |  | 16.928 | 17.4831 | 31.2023 | 16.3449 | 16.2863 | 21.89 | 190.5788 | 247.265 | 158.2908 | 162.4829 | 129.5588 |  | 73.2657 | 134.7242 | 71.8911 | 140.456 | 129.0365 | 176.5011 |  | 111.322 |  |  | 19.0091 | 23.7855 | 74.926 | [6 empty] | 117.5109 |  |  | 54.229 |  |  | 24.3973 | 103.6364 | 280.39 | 11.95 | 93.285 | 177.028 | 14.7196 | 89.9267 | 199.5127 | 34.6993 | 154.9095 | 15.695 | 145.2279 | 18.3889 | 152.3502 | 13.1872 | 91.0797 | 166.2077 | 40.6274 | 94.6711 | 205.7034 | 15.9656 | 79.6439 | 198.6931 | 17.864 | 141.2928 | 34.9334 | 148.1421 | 20.8886 | 163.6201 | 1.5055 | 18.7048 | 1.9481 | 0.085708 | -38.1576 | 3.1236 | 404.18 | 50.63 | -1.1054 | 0.42342 | -0.27202 | -0.45604 | -0.11301 | -1.4245 | -0.97674 | -0.74717 | -0.94171 | 1.1663 | -0.62279 | -0.33541 | -1.328 | -0.71265
42810.4475 | 641 | 18.4519 | 18.5165 | 18.4917 | 18.5 | 17.7954 | 16.3744 | 14.4247 | 16.5969 | 17.0935 | 17.1924 | 17.1996 | 16.7156 | 15.7314 | 14.3584 | 14.7933 | 14.8688 | 15.6111 | 13.281 | 13.9524 | 18.7632 |  |  |  | 16.5776 | 16.742 | 26.0827 | 188.2477 | 174.2514 | 203.5914 | 17.1234 | 16.697 | 22.2893 | 16.7701 | 16.6983 | 23.717 | 87.1143 | 206.8042 |  | 124.3183 | 172.3472 | 170.7321 | 170.2939 |  | 7.5318 | 8.9638 | 7.3217 | 8.8445 | 9.618 | 17.7722 | 138.0588 | 4.6641 | 7.8917 | 4.406 | 9.89 | 9.0993 | 42.1106 | 46.6757 | 42.6966 | 14.6773 |  |  | -0.71801 | 0.067771 | 0.045876 | -0.45932 | -0.21603 | -0.93225 | -0.53959 | 0.64381 | 1.4683 | -0.19487 | 0.23793 | 8.8752 | 8.8762 | 0.86342 | 16.0556 | 16.6193 | 17.1505 | 17.4704 | 17.4128 | 16.3515 | 14.6881 | 16.7536 | 17.0922 | 17.389 | 17.4237 | 17.1215 | 16.2781 | 14.4729 | 48.0054 | 21.6526 | 27.948 | 22.1107 | 19.8113 | 40.9516 | 23.5137 | 15.8203 | 15.5925 | 15.7399 | 14.3425 | 15.9238 | 19.5752 |  |  |  | 69.163 | 184.7438 | 162.5521 | 122.3412 | 0.53512 | -0.11478 | 64.5488 |  |  | 11.982 |  |  | 16.929 | 17.4931 | 31.2667 | 16.3426 | 16.2869 | 21.9239 | 190.737 | 247.8371 | 158.4905 | 162.6823 | 130.3431 |  | 73.5619 | 133.8044 | 72.1065 | 140.3622 | 129.5663 | 177.8407 |  | 111.6089 |  |  | 19.0511 | 23.8799 | 75.7903 | [6 empty] | 116.4957 |  |  | 54.3332 |  |  | 24.4791 | 104.0398 | 280.7828 | 11.9642 | 93.1528 | 177.2611 | 14.7145 | 90.3517 | 199.5246 | 34.7531 | 155.355 | 15.738 | 145.4426 | 18.4587 | 152.756 | 13.2255 | 91.6374 | 166.2854 | 40.7842 | 95.0934 | 205.8688 | 15.9692 | 79.8391 | 198.9454 | 17.9174 | 141.4624 | 34.9906 | 148.4484 | 20.9514 | 163.9777 | 1.9907 | 18.7048 | 1.9522 | 0.087655 | -38.2308 | 3.1237 | 409.04 | 48.66 | -1.2894 | 0.30472 | 0.25071 | -0.7933 | -0.55247 | -1.1477 | -0.87315 | -0.75793 | -0.90817 | 1.1915 | -0.23185 | -0.053512 | -1.3554 | -0.69864
42810.4475 | 642 | 18.4602 | 18.5092 | 18.4894 | 18.5 | 17.7866 | 16.3749 | 14.4297 | 16.5901 | 17.0867 | 17.1882 | 17.199 | 16.7088 | 15.7288 | 14.3612 | 14.7955 | 14.8636 | 15.6139 | 13.2743 | 13.9395 | 18.7811 |  |  |  | 16.5735 | 16.7333 | 26.1252 | 188.3168 | 174.3598 | 201.7873 | 17.1239 | 16.7058 | 22.3328 | 16.7758 | 16.7044 | 23.7572 | 87.4586 | 207.388 |  | 124.664 | 172.5167 | 171.09 | 170.5156 |  | 7.521 | 8.9583 | 7.3004 | 8.8063 | 9.5623 | 17.6333 | 138.3003 | 4.6708 | 7.8916 | 4.4579 | 9.8853 | 9.097 | 42.0978 | 46.6678 | 42.7071 | 14.6757 |  |  | -0.59184 | 0.015203 | 0.12079 | -0.6466 | 0.10596 | -0.4473 | -0.59479 | 0.59256 | -0.16384 | -0.70762 | 0.2588 | 8.8734 | 8.8749 | 0.83971 | 16.0594 | 16.6235 | 17.1555 | 17.4679 | 17.4138 | 16.3489 | 14.6815 | 16.7517 | 17.0886 | 17.3923 | 17.4249 | 17.1225 | 16.2828 | 14.4653 | 46.2547 | 21.6032 | 27.9752 | 21.5006 | 18.8178 | 40.9368 | 23.5068 | 15.8095 | 15.5721 | 15.7445 | 14.3357 | 15.9259 | 19.6049 |  |  |  | 69.4052 | 184.8249 | 162.5946 | 122.1841 | 0.67005 | -0.29394 | 64.746 |  |  | 11.9836 |  |  | 16.9272 | 17.5028 | 31.3321 | 16.3436 | 16.2924 | 21.9491 | 190.83 | 248.3489 | 158.7335 | 162.905 | 131.3699 |  | 73.8094 | 133.5573 | 72.3211 | 142.3268 | 130.082 | 177.6691 |  | 111.8401 |  |  | 19.0949 | 23.9482 | 76.0987 | [6 empty] | 117.1854 |  |  | 54.606 |  |  | 24.5783 | 104.1803 | 280.6118 | 11.9645 | 93.2807 | 177.3061 | 14.7338 | 90.6086 | 199.544 | 34.8235 | 155.6697 | 15.7985 | 145.8713 | 18.5038 | 153.1486 | 13.244 | 91.7394 | 166.4123 | 40.8994 | 95.2544 | 206.0778 | 15.9642 | 80.3006 | 198.969 | 17.9375 | 141.7011 | 35.0438 | 148.6722 | 21.0205 | 164.4082 | 1.926 | 18.7033 | 1.9567 | 0.087495 | -38.2665 | 3.1237 | 407.66 | 49.76 | -1.1684 | 0.14432 | 0.40681 | -0.94122 | 0.38683 | -0.79479 | -0.9165 | -0.77723 | -0.89334 | 1.1589 | -0.03908 | -0.057359 | -1.3483 | -0.68534
42810.4475 | 643 | 18.4653 | 18.5204 | 18.4949 | 18.5015 | 17.7908 | 16.3829 | 14.4319 | 16.5928 | 17.091 | 17.1905 | 17.196 | 16.7123 | 15.7328 | 14.3661 | 14.8051 | 14.8672 | 15.628 | 13.283 | 13.9541 | 18.8173 |  |  |  | 16.5817 | 16.7431 | 26.1793 | 188.2891 | 174.638 | 200.2018 | 17.1211 | 16.6979 | 22.3604 | 16.7718 | 16.7038 | 23.793 | 87.8327 | 208.5885 |  | 125.0223 | 172.7882 | 171.3067 | 170.3243 |  | 7.5308 | 8.9831 | 7.3048 | 8.802 | 9.5517 | 17.5439 | 138.4163 | 4.6679 | 7.9017 | 4.5606 | 9.9102 | 9.1116 | 42.0916 | 46.6415 | 42.715 | 14.6784 |  |  | -0.76795 | 0.036887 | 0.028792 | -0.074254 | 0.12962 | -0.15094 | 0.22924 | 0.52882 | -0.15469 | -0.13822 | 0.22403 | 8.874 | 8.875 | 0.83261 | 16.0635 | 16.6219 | 17.1427 | 17.4686 | 17.414 | 16.3485 | 14.688 | 16.7462 | 17.0951 | 17.3836 | 17.4191 | 17.1278 | 16.2797 | 14.4673 | 45.9193 | 20.9046 | 26.0484 | 20.9633 | 18.9585 | 40.9471 | 23.4899 | 15.8112 | 15.5756 | 15.7427 | 14.3445 | 15.9493 | 19.6377 |  |  |  | 69.6508 | 184.723 | 162.7581 | 122.1304 | 1.1079 | -0.1718 | 65.1143 |  |  | 11.9833 |  |  | 16.9301 | 17.5035 | 31.399 | 16.3367 | 16.2907 | 21.9815 | 191.1013 | 248.5075 | 158.9575 | 163.0938 | 131.4096 |  | 74.0186 | 134.3007 | 72.5205 | 141.6314 | 130.5903 | 177.2449 |  | 112.0638 |  |  | 19.1638 | 23.9938 | 76.2433 | [6 empty] | 119.681 |  |  | 54.8009 |  |  | 24.6756 | 104.3166 | 279.9419 | 11.9909 | 93.2456 | 177.5224 | 14.7798 | 90.6077 | 199.7223 | 34.9201 | 155.8401 | 15.8656 | 146.3772 | 18.5432 | 153.2713 | 13.2739 | 91.4803 | 166.554 | 41.0619 | 95.3698 | 205.5812 | 15.9247 | 80.7387 | 199.2219 | 17.9722 | 142.036 | 35.1091 | 148.8427 | 21.0708 | 164.6321 | 2.0263 | 18.7021 | 1.9612 | 0.087669 | -38.286 | 3.1237 | 394.3 | 50.18 | -1.3287 | 0.22482 | 0.19862 | -0.31897 | 0.42777 | -0.46162 | 0.56889 | -0.77054 | -0.90659 | 1.1999 | -0.00059397 | 0.15475 | -1.3287 | -0.67479
42810.4475 | 644 | 18.4591 | 18.5176 | 18.4945 | 18.4997 | 17.7931 | 16.379 | 14.4312 | 16.5964 | 17.0938 | 17.1956 | 17.1941 | 16.7152 | 15.7411 | 14.3631 | 14.8046 | 14.8707 | 15.63 | 13.2819 | 13.9499 | 18.8334 |  |  |  | 16.5785 | 16.7522 | 26.2271 | 188.3606 | 174.8628 | 200.8582 | 17.1218 | 16.6964 | 22.3905 | 16.7711 | 16.7049 | 23.8286 | 88.1939 | 208.7867 |  | 125.3657 | 173.1568 | 171.4908 | 169.4366 |  | 7.5325 | 8.9919 | 7.3036 | 8.7905 | 9.5422 | 17.5446 | 138.9568 | 4.6149 | 7.901 | 4.6095 | 9.9224 | 9.1248 | 42.056 | 46.6102 | 42.7249 | 14.6785 |  |  | -0.78438 | -0.14645 | 0.02748 | -0.76751 | 0.035648 | -0.36122 | 0.025528 | 0.56956 | -0.38685 | -0.83958 | 0.075597 | 8.8763 | 8.8776 | 0.83522 | 16.0619 | 16.615 | 17.1478 | 17.47 | 17.4053 | 16.3496 | 14.6822 | 16.7511 | 17.0896 | 17.3801 | 17.4221 | 17.1283 | 16.285 | 14.467 | 49.1988 | 22.6228 | 25.4688 | 19.5924 | 17.9746 | 41.0401 | 23.4776 | 15.8181 | 15.579 | 15.7452 | 14.3446 | 15.9619 | 19.663 |  |  |  | 69.8943 | 184.9906 | 163.1443 | 122.5248 | 1.0732 | 0.43401 | 65.5408 |  |  | 11.9807 |  |  | 16.9304 | 17.5141 | 31.4645 | 16.3341 | 16.2905 | 22.0134 | 191.5772 | 248.7891 | 159.1212 | 163.3111 | 130.7387 |  | 74.238 | 135.0104 | 72.7333 | 142.2762 | 131.2057 | 177.7675 |  | 112.3281 |  |  | 19.2184 | 24.0573 | 76.1377 | [6 empty] | 122.2309 |  |  | 54.9759 |  |  | 24.7412 | 104.6949 | 279.948 | 12.0569 | 93.3953 | 177.9735 | 14.8307 | 90.7785 | 199.7641 | 35.0356 | 155.9964 | 15.9524 | 146.6877 | 18.574 | 153.4141 | 13.3116 | 91.6274 | 166.569 | 41.24 | 95.8148 | 205.0089 | 15.93 | 80.7931 | 199.6569 | 18.0583 | 142.4532 | 35.1562 | 149.0407 | 21.1307 | 164.7666 | 1.9957 | 18.6996 | 1.9663 | 0.087408 | -38.2689 | 3.1237 | 387.27 | 48.99 | -1.3438 | -0.44796 | 0.19405 | -1.0255 | 0.22434 | -0.71412 | 0.18984 | -0.74372 | -0.9184 | 1.2083 | -0.354 | 0.21772 | -1.2901 | -0.67675
42810.4475 | 645 | 18.4604 | 18.515 | 18.4974 | 18.5046 | 17.7967 | 16.3809 | 14.4256 | 16.5916 | 17.0947 | 17.1899 | 17.1985 | 16.7191 | 15.7377 | 14.361 | 14.806 | 14.8721 | 15.6274 | 13.287 | 13.9445 | 18.8618 |  |  |  | 16.5706 | 16.751 | 26.2746 | 188.533 | 175.109 | 201.9417 | 17.1215 | 16.7101 | 22.4314 | 16.7729 | 16.7143 | 23.873 | 88.4968 | 209.545 |  | 125.7347 | 173.5704 | 171.7181 | 166.4154 |  | 7.5214 | 9.0111 | 7.294 | 8.7996 | 9.5542 | 17.7201 | 140.0014 | 4.5753 | 7.916 | 4.6394 | 9.9344 | 9.1136 | 42.0047 | 46.5803 | 42.712 | 14.6598 |  |  | -0.65033 | 0.28265 | -0.09146 | -0.39164 | 0.1421 | -0.3783 | 0.27523 | 0.36191 | -0.41701 | -0.15815 | 0.24708 | 8.8742 | 8.8751 | 0.81606 | 16.0632 | 16.6159 | 17.1538 | 17.4823 | 17.4183 | 16.3616 | 14.6932 | 16.7556 | 17.0989 | 17.3911 | 17.4251 | 17.1329 | 16.2909 | 14.4786 | 52.9445 | 23.6699 | 28.0632 | 20.4168 | 17.4351 | 41.1551 | 23.504 | 15.8193 | 15.5884 | 15.7514 | 14.3441 | 15.9716 | 19.6951 |  |  |  | 70.1314 | 184.7903 | 163.1685 | 123.0712 | 0.93221 | 0.0037888 | 65.5307 |  |  | 11.9952 |  |  | 16.934 | 17.5287 | 31.5345 | 16.3427 | 16.2988 | 22.056 | 191.838 | 249.1044 | 159.2441 | 163.4316 | 128.8565 |  | 74.4615 | 135.4898 | 72.934 | 144.0039 | 131.8851 | 178.5318 |  | 112.5655 |  |  | 19.1828 | 24.1104 | 75.3748 | [6 empty] | 124.2927 |  |  | 55.1741 |  |  | 24.7983 | 104.9935 | 280.0174 | 12.1167 | 93.3197 | 178.548 | 14.8437 | 90.8657 | 199.919 | 35.1422 | 156.1225 | 16.0423 | 146.7596 | 18.6115 | 153.6301 | 13.3393 | 91.796 | 166.778 | 41.3779 | 95.8049 | 204.8683 | 15.9701 | 80.7179 | 199.7464 | 18.1219 | 142.8196 | 35.2322 | 149.1364 | 21.1651 | 164.9306 | 1.8682 | 18.6963 | 1.9708 | 0.087553 | -38.3046 | 3.1237 | 392.85 | 49.85 | -1.225 | 0.62235 | -0.35402 | -0.73259 | 0.44804 | -0.73103 | 0.62354 | -0.68311 | -0.92425 | 1.1894 | -0.7566 | -0.06746 | -1.1945 | -0.68317
42810.4475 | 646 | 18.4518 | 18.5116 | 18.4908 | 18.4999 | 17.7833 | 16.3678 | 14.4182 | 16.5794 | 17.0915 | 17.1799 | 17.1884 | 16.7071 | 15.7223 | 14.3561 | 14.805 | 14.8735 | 15.6348 | 13.284 | 13.9664 | 18.8884 |  |  |  | 16.5828 | 16.764 | 26.3257 | 188.6916 | 175.3542 | 201.7033 | 17.1242 | 16.7157 | 22.4618 | 16.7781 | 16.7187 | 23.9132 | 88.8111 | 210.4773 |  | 126.0672 | 173.9474 | 171.9394 | 166.0206 |  | 7.5141 | 9.0005 | 7.2897 | 8.7966 | 9.57 | 18.1339 | 140.6308 | 4.6192 | 7.9234 | 4.6498 | 9.9494 | 9.1297 | 41.9695 | 46.5764 | 42.7174 | 14.6597 |  |  | -0.87309 | -0.11819 | 0.068876 | -0.30753 | 0.4654 | 0.029112 | -0.34968 | 0.4539 | -1.2137 | -0.17829 | 0.23595 | 8.8721 | 8.8734 | 0.82054 | 16.0605 | 16.6126 | 17.1411 | 17.4738 | 17.4136 | 16.3497 | 14.6901 | 16.75 | 17.0866 | 17.3851 | 17.4189 | 17.1243 | 16.2816 | 14.4626 | 52.9979 | 23.3503 | 27.6193 | 21.2885 | 18.1236 | 41.2217 | 23.5099 | 15.8077 | 15.5821 | 15.7496 | 14.336 | 15.9727 | 19.7157 |  |  |  | 70.4106 | 184.6059 | 163.2458 | 123.1847 | 0.91499 | 0.14889 | 65.5646 |  |  | 12.005 |  |  | 16.9369 | 17.5301 | 31.5984 | 16.3414 | 16.3014 | 22.0902 | 191.9282 | 249.5216 | 159.3619 | 163.4783 | 129.7126 |  | 74.6862 | 135.6982 | 73.1327 | 142.4646 | 132.5375 | 179.9891 |  | 112.81 |  |  | 19.1466 | 24.1662 | 75.3236 | [6 empty] | 125.0012 |  |  | 55.4642 |  |  | 24.8709 | 105.1693 | 280.7328 | 12.1792 | 92.7255 | 178.849 | 14.8557 | 91.0465 | 200.0678 | 35.2403 | 156.3715 | 16.0576 | 146.8875 | 18.6509 | 153.7206 | 13.3792 | 92.0153 | 167.2067 | 41.5454 | 95.8166 | 204.7527 | 15.9956 | 81.0147 | 199.9965 | 18.164 | 143.1461 | 35.362 | 149.5019 | 21.1899 | 165.607 | 1.9108 | 18.6943 | 1.9764 | 0.087293 | -38.2477 | 3.1237 | 387.37 | 49.21 | -1.419 | -0.40244 | 0.30721 | -0.64916 | 0.81141 | 0.20294 | -0.70334 | -0.6985 | -0.92265 | 1.2601 | -0.75466 | -0.017449 | -1.1714 | -0.67601
42810.4475 | 647 | 18.4599 | 18.5119 | 18.4971 | 18.5003 | 17.7929 | 16.3807 | 14.4214 | 16.5897 | 17.0931 | 17.1902 | 17.1992 | 16.7036 | 15.7373 | 14.3678 | 14.8059 | 14.8758 | 15.6297 | 13.2892 | 13.9678 | 18.9157 |  |  |  | 16.5893 | 16.766 | 26.3735 | 188.9519 | 175.5464 | 202.6923 | 17.1249 | 16.7156 | 22.5073 | 16.7805 | 16.7227 | 23.9517 | 89.1791 | 211.8901 |  | 126.4561 | 174.4315 | 172.2156 | 166.5697 |  | 7.5003 | 8.999 | 7.2839 | 8.8105 | 9.5903 | 18.8841 | 141.4418 | 4.6454 | 7.9278 | 4.684 | 9.954 | 9.1203 | 41.9377 | 46.5714 | 42.7115 | 14.6483 |  |  | -0.61812 | -0.11031 | -0.055976 | -0.13997 | 0.55411 | -0.49658 | -0.15386 | 0.4999 | -0.37907 | 1.0885 | 0.049369 | 8.8756 | 8.8768 | 0.85727 | 16.0571 | 16.6136 | 17.1439 | 17.4637 | 17.4091 | 16.3418 | 14.6835 | 16.74 | 17.0789 | 17.3792 | 17.4156 | 17.1172 | 16.2772 | 14.4579 | 52.8452 | 24.3796 | 28.6975 | 20.8622 | 17.9341 | 41.3006 | 23.5193 | 15.8138 | 15.5881 | 15.758 | 14.3424 | 15.9858 | 19.7564 |  |  |  | 70.67 | 184.4206 | 163.4082 | 123.3842 | 0.75473 | 0.52209 | 65.5504 |  |  | 12.01 |  |  | 16.928 | 17.5343 | 31.6573 | 16.3441 | 16.3019 | 22.1173 | 192.1021 | 250.0692 | 159.6394 | 163.795 | 131.5734 |  | 74.9231 | 136.2274 | 73.3692 | 140.1851 | 133.3372 | 180.2706 |  | 113.0422 |  |  | 19.1891 | 24.2084 | 75.968 | [6 empty] | 126.6626 |  |  | 55.7328 |  |  | 24.9557 | 105.4977 | 280.2915 | 12.2257 | 93.2116 | 179.0299 | 14.8517 | 91.6086 | 200.4721 | 35.3318 | 156.7263 | 16.0951 | 147.2739 | 18.6734 | 154.3343 | 13.4562 | 92.2192 | 167.6007 | 41.777 | 96.208 | 204.8462 | 16.0528 | 81.2766 | 200.1841 | 18.2224 | 143.474 | 35.4806 | 149.7959 | 21.2263 | 165.9624 | 1.9462 | 18.6908 | 1.9817 | 0.086431 | -38.2568 | 3.1237 | 366.66 | 49.18 | -1.1952 | -0.38879 | -0.27695 | -0.43794 | 0.88651 | -0.83923 | -0.46715 | -0.74135 | -0.92855 | 1.3578 | -0.72837 | -0.13614 | -1.1725 | -0.67195
42810.4475 | 648 | 18.4615 | 18.5222 | 18.5051 | 18.5022 | 17.8022 | 16.3891 | 14.4323 | 16.5973 | 17.1052 | 17.1964 | 17.2022 | 16.7178 | 15.7441 | 14.37 | 14.8117 | 14.8812 | 15.6308 | 13.2893 | 13.9597 | 18.9337 |  |  |  | 16.5858 | 16.7781 | 26.4125 | 189.4312 | 175.5691 | 203.5623 | 17.1385 | 16.7311 | 22.5353 | 16.7746 | 16.7277 | 23.9866 | 89.5656 | 213.7036 |  | 126.8789 | 174.7872 | 172.6298 | 166.0685 |  | 7.4999 | 8.9896 | 7.2737 | 8.8119 | 9.6117 | 18.8188 | 141.7138 | 4.5671 | 7.9331 | 4.7272 | 9.9752 | 9.1244 | 41.9257 | 46.5642 | 42.7126 | 14.6359 |  |  | -0.62207 | -0.017653 | 0.01762 | -0.46129 | 0.15459 | 0.039624 | 0.2864 | 0.18712 | -0.34715 | 0.74378 | 0.093281 | 8.8746 | 8.8759 | 0.88012 | 16.0645 | 16.6199 | 17.1499 | 17.4714 | 17.4167 | 16.3508 | 14.6887 | 16.7503 | 17.0898 | 17.3919 | 17.4264 | 17.1278 | 16.2857 | 14.4648 | 52.658 | 24.7744 | 30.3615 | 21.7408 | 18.6437 | 41.3221 | 23.5417 | 15.8165 | 15.5877 | 15.764 | 14.3479 | 15.9968 | 19.7857 |  |  |  | 70.9564 | 184.0391 | 163.516 | 123.261 | 0.24884 | -0.1048 | 65.8057 |  |  | 12.0239 |  |  | 16.9323 | 17.5466 | 31.7299 | 16.353 | 16.3069 | 22.1544 | 192.2924 | 250.4861 | 159.9197 | 164.2232 | 131.1902 |  | 75.1806 | 139.0805 | 73.6628 | 140.3742 | 134.2311 | 179.6953 |  | 113.2915 |  |  | 19.3016 | 24.2091 | 76.6776 | [6 empty] | 127.3653 |  |  | 56.0328 |  |  | 25.0306 | 105.8205 | 280.8788 | 12.2031 | 94.2204 | 179.1159 | 14.8907 | 91.5123 | 200.9055 | 35.4051 | 157.2483 | 16.0718 | 147.6195 | 18.692 | 154.6106 | 13.5587 | 92.2751 | 167.8968 | 42.0375 | 96.6798 | 205.4822 | 16.1122 | 81.5469 | 200.3899 | 18.2942 | 143.6317 | 35.6724 | 150.0489 | 21.2477 | 166.2176 | 2.1253 | 18.6847 | 1.9875 | 0.086576 | -38.1698 | 3.1237 | 375.92 | 49.77 | -1.2001 | -0.15553 | 0.15538 | -0.79504 | 0.46819 | 0.23704 | 0.63727 | -0.72108 | -0.99688 | 1.391 | -0.70503 | -0.31841 | -1.1437 | -0.65793
42810.4475 | 649 | 18.4649 | 18.5201 | 18.5059 | 18.5096 | 17.7969 | 16.3836 | 14.4306 | 16.5952 | 17.1029 | 17.2014 | 17.2023 | 16.7132 | 15.7348 | 14.3637 | 14.8054 | 14.8882 | 15.6371 | 13.2964 | 13.9566 | 18.9592 |  |  |  | 16.5886 | 16.7826 | 26.4681 | 189.7164 | 175.6846 | 204.822 | 17.1324 | 16.7249 | 22.5593 | 16.7747 | 16.7294 | 24.0216 | 89.9191 | 215.2164 |  | 127.2153 | 175.0851 | 172.9114 | 165.023 |  | 7.4875 | 8.9979 | 7.2711 | 8.8179 | 9.6149 | 18.6858 | 140.9006 | 4.5745 | 7.9346 | 4.7369 | 9.984 | 9.1232 | 41.9094 | 46.5582 | 42.7198 | 14.6255 |  |  | -0.91186 | -0.14053 | -0.002748 | -0.16231 | 0.12042 | -0.23176 | 0.10635 | 0.24954 | -0.29908 | -0.10004 | 0.14812 | 8.8736 | 8.8746 | 0.86206 | 16.0674 | 16.6216 | 17.1534 | 17.4768 | 17.4142 | 16.3515 | 14.689 | 16.7515 | 17.0874 | 17.3878 | 17.4251 | 17.1244 | 16.2852 | 14.4644 | 49.6671 | 23.2638 | 29.624 | 21.8961 | 19.3483 | 41.3194 | 23.551 | 15.8098 | 15.5837 | 15.763 | 14.3437 | 16.0018 | 19.8056 |  |  |  | 71.2606 | 183.8362 | 163.6792 | 123.3708 | 0.5732 | -0.052671 | 66.0159 |  |  | 12.0329 |  |  | 16.9317 | 17.545 | 31.7909 | 16.3444 | 16.3119 | 22.1816 | 192.5316 | 250.6118 | 160.1273 | 164.4812 | 132.4675 |  | 75.4523 | 140.6889 | 73.8776 | 144.4011 | 134.9384 | 180.1678 |  | 113.5298 |  |  | 19.377 | 24.2095 | 78.1452 | [6 empty] | 130.2335 |  |  | 56.4804 |  |  | 25.1047 | 106.1536 | 282.0108 | 12.2426 | 95.2032 | 179.166 | 14.9507 | 91.268 | 201.4967 | 35.5001 | 157.8534 | 16.0464 | 147.769 | 18.7674 | 155.143 | 13.6349 | 92.8719 | 167.93 | 42.3581 | 97.1908 | 206.3555 | 16.1443 | 81.8569 | 200.5537 | 18.3985 | 143.7913 | 36.0536 | 150.2229 | 21.2697 | 166.6698 | 2.4398 | 18.6721 | 1.9925 | 0.086938 | -38.212 | 3.1236 | 359.05 | 49.15 | -1.4549 | -0.43883 | -0.061364 | -0.4716 | 0.41312 | -0.57314 | 0.38825 | -0.74641 | -1.0336 | 1.3097 | -0.37303 | -0.23538 | -1.101 | -0.64971
42810.4476 | 650 | 18.4676 | 18.519 | 18.5016 | 18.5078 | 17.7937 | 16.3782 | 14.4306 | 16.5917 | 17.0964 | 17.2028 | 17.2035 | 16.7174 | 15.7398 | 14.3644 | 14.8077 | 14.8847 | 15.6444 | 13.2904 | 13.9526 | 18.9923 |  |  |  | 16.5822 | 16.7787 | 26.5169 | 190.1487 | 175.7816 | 204.7385 | 17.1359 | 16.7311 | 22.6018 | 16.7794 | 16.7357 | 24.0649 | 90.2959 | 215.8094 |  | 127.5654 | 175.3767 | 173.0827 | 165.9944 |  | 7.5048 | 9.0289 | 7.2919 | 8.83 | 9.6314 | 18.679 | 141.069 | 4.7424 | 7.9609 | 4.7428 | 10.0291 | 9.1281 | 41.912 | 46.5529 | 42.7237 | 14.6104 |  |  | -0.61944 | -0.078765 | 0.1175 | -0.15968 | 0.088876 | 0.048824 | 0.24763 | 0.30211 | 0.17846 | -0.019264 | 0.15925 | 8.8726 | 8.8741 | 0.8766 | 16.0682 | 16.6168 | 17.1502 | 17.4749 | 17.4108 | 16.3512 | 14.6888 | 16.7531 | 17.0857 | 17.3917 | 17.4267 | 17.1216 | 16.2871 | 14.4673 | 49.6605 | 23.4688 | 29.2709 | 22.2512 | 19.3329 | 41.3575 | 23.5666 | 15.8095 | 15.5839 | 15.7545 | 14.3441 | 16.0253 | 19.8394 |  |  |  | 71.5772 | 183.6971 | 163.9769 | 123.6399 | 1.2466 | 0.24864 | 66.0443 |  |  | 12.0421 |  |  | 16.9296 | 17.5572 | 31.8593 | 16.3433 | 16.3169 | 22.2128 | 192.888 | 250.7547 | 160.3971 | 164.7112 | 133.8944 |  | 75.7287 | 140.6063 | 74.0747 | 141.1131 | 135.5124 | 180.3761 |  | 113.7963 |  |  | 19.4142 | 24.2537 | 78.4355 | [6 empty] | 129.3114 |  |  | 56.9109 |  |  | 25.1996 | 106.6041 | 283.1775 | 12.2591 | 95.4818 | 179.4106 | 15.0204 | 91.9268 | 202.5103 | 35.6212 | 158.1159 | 16.0745 | 147.9638 | 18.7794 | 155.6596 | 13.6752 | 92.8818 | 168.2297 | 42.7489 | 97.6278 | 206.655 | 16.181 | 82.0927 | 201.3087 | 18.4514 | 143.9745 | 36.4103 | 150.8359 | 21.3245 | 167.1901 | 2.0327 | 18.6599 | 1.9975 | 0.086345 | -38.2374 | 3.1237 | 366.83 | 48.93 | -1.199 | -0.32855 | 0.40129 | -0.46779 | 0.35491 | 0.26306 | 0.59243 | -0.77571 | -1.0239 | 1.4258 | -0.36779 | -0.19432 | -1.1134 | -0.64546
42810.4476 | 651 | 18.4673 | 18.5193 | 18.5057 | 18.5021 | 17.7978 | 16.3861 | 14.4348 | 16.5984 | 17.1001 | 17.1997 | 17.2049 | 16.7222 | 15.7414 | 14.364 | 14.8086 | 14.885 | 15.6449 | 13.2897 | 13.96 | 19.0092 |  |  |  | 16.5812 | 16.7885 | 26.5675 | 190.39 | 175.8071 | 207.2135 | 17.1344 | 16.7323 | 22.6338 | 16.7759 | 16.7435 | 24.1071 | 90.6847 | 218.9187 |  | 127.9716 | 175.6378 | 173.2718 | 168.3854 |  | 7.5248 | 9.0462 | 7.296 | 8.8655 | 9.6562 | 18.8972 | 141.5401 | 4.8214 | 7.9823 | 4.7215 | 10.0464 | 9.1389 | 41.9315 | 46.5644 | 42.7446 | 14.6079 |  |  | -1.0709 | -0.099137 | 0.15759 | 0.14917 | 0.088876 | 0.15922 | 0.30152 | 0.32576 | -0.42266 | -0.42628 | 0.33669 | 8.8762 | 8.8776 | 0.92237 | 16.0646 | 16.616 | 17.1463 | 17.474 | 17.4094 | 16.3512 | 14.6822 | 16.7454 | 17.0906 | 17.3834 | 17.4209 | 17.1242 | 16.2795 | 14.4609 | 53.4289 | 25.4823 | 32.0542 | 22.9429 | 19.2635 | 41.5194 | 23.6064 | 15.8109 | 15.5795 | 15.7693 | 14.354 | 16.0367 | 19.8746 |  |  |  | 71.8876 | 183.5846 | 164.319 | 123.3753 | 1.6792 | 0.69881 | 66.0026 |  |  | 12.056 |  |  | 16.9359 | 17.5754 | 31.9297 | 16.3494 | 16.3289 | 22.2577 | 193.1219 | 251.3081 | 160.6543 | 165.0218 | 134.0016 |  | 76.0555 | 139.9839 | 74.34 | 147.1743 | 136.2228 | 179.9006 |  | 114.0661 |  |  | 19.4258 | 24.3186 | 79.1787 | [6 empty] | 131.2216 |  |  | 57.6346 |  |  | 25.3158 | 107.0782 | 283.8855 | 12.2924 | 95.5036 | 180.2403 | 15.1035 | 92.1941 | 203.4374 | 35.8248 | 158.857 | 16.1706 | 148.2413 | 18.7769 | 156.1585 | 13.7019 | 93.005 | 168.8541 | 43.0273 | 98.1099 | 207.162 | 16.2246 | 82.4911 | 202.1326 | 18.4868 | 144.2265 | 36.6542 | 151.1485 | 21.3892 | 167.4942 | 2.1197 | 18.652 | 2.0012 | 0.08641 | -38.2465 | 3.1237 | 347.39 | 50.3 | -1.5806 | -0.3686 | 0.46473 | 0.45214 | 0.35505 | 0.47522 | 0.65396 | -0.76646 | -0.99673 | 1.2882 | -0.76737 | -0.49891 | -1.1648 | -0.6266
42810.4476 | 652 | 18.4652 | 18.5208 | 18.5046 | 18.4982 | 17.7951 | 16.3817 | 14.4355 | 16.5945 | 17.0977 | 17.1952 | 17.2015 | 16.7184 | 15.7489 | 14.3666 | 14.8121 | 14.887 | 15.6488 | 13.2893 | 13.9531 | 19.037 |  |  |  | 16.5855 | 16.7902 | 26.614 | 191.1482 | 176.0596 | 212.2056 | 17.1373 | 16.735 | 22.6616 | 16.7777 | 16.7502 | 24.1439 | 91.0699 | 222.7348 |  | 128.4174 | 175.9017 | 173.63 | 170.0504 |  | 7.5277 | 9.055 | 7.2903 | 8.8875 | 9.6827 | 19.2828 | 141.928 | 4.8825 | 7.9809 | 4.6584 | 10.0644 | 9.1373 | 41.941 | 46.5733 | 42.7479 | 14.5969 |  |  | -0.63127 | 0.054627 | -0.013264 | -0.060454 | 0.10662 | 0.36621 | 0.3416 | 0.38688 | -0.44134 | 1.4313 | 0.38636 | 8.8736 | 8.8749 | 0.92627 | 16.0755 | 16.6111 | 17.1439 | 17.472 | 17.4156 | 16.3501 | 14.6876 | 16.7501 | 17.0897 | 17.3815 | 17.4222 | 17.1261 | 16.2803 | 14.4619 | 60.1028 | 27.5618 | 35.0481 | 25.4037 | 21.4122 | 41.7371 | 23.6697 | 15.8036 | 15.5848 | 15.7746 | 14.3641 | 16.0522 | 19.9145 |  |  |  | 72.188 | 183.4361 | 164.693 | 123.2753 | 1.0852 | 0.69825 | 66.1285 |  |  | 12.0616 |  |  | 16.9412 | 17.585 | 31.9951 | 16.345 | 16.3373 | 22.2933 | 193.4966 | 252.3778 | 160.7057 | 165.167 | 135.1443 |  | 76.3071 | 139.5425 | 74.5679 | 152.2042 | 137.0187 | 178.3772 |  | 114.2976 |  |  | 19.511 | 24.37 | 79.2907 | [6 empty] | 130.2898 |  |  | 58.1484 |  |  | 25.44 | 107.6573 | 284.9309 | 12.299 | 95.7938 | 180.7219 | 15.1637 | 92.6043 | 204.2855 | 36.0972 | 160.0638 | 16.2774 | 148.4404 | 18.7851 | 156.9904 | 13.7267 | 93.2892 | 169.0274 | 43.3027 | 98.5852 | 208.2225 | 16.2543 | 82.809 | 202.5282 | 18.5298 | 144.5097 | 36.8628 | 151.4113 | 21.4399 | 167.8393 | 2.0529 | 18.6453 | 2.0042 | 0.086106 | -38.1351 | 3.1238 | 371.35 | 48.83 | -1.2198 | 0.27362 | -0.13483 | -0.28785 | 0.38913 | 0.72118 | 0.69653 | -0.78878 | -0.97597 | 1.183 | -1.4832 | -0.82416 | -1.1961 | -0.61267
42810.4476 | 653 | 18.4733 | 18.5232 | 18.5061 | 18.5099 | 17.7955 | 16.386 | 14.4291 | 16.5982 | 17.0982 | 17.1962 | 17.2058 | 16.718 | 15.7436 | 14.367 | 14.8242 | 14.8923 | 15.6558 | 13.2872 | 13.9614 | 19.0717 |  |  |  | 16.5878 | 16.7928 | 26.6663 | 192.5723 | 176.8062 | 220.4888 | 17.1354 | 16.7439 | 22.6963 | 16.7785 | 16.7584 | 24.1821 | 91.4641 | 225.1635 |  | 128.9027 | 176.2217 | 174.1268 | 170.6897 |  | 7.531 | 9.0664 | 7.3054 | 8.9193 | 9.7104 | 19.4926 | 140.3904 | 4.8925 | 8.0022 | 4.6534 | 10.0812 | 9.1391 | 41.9562 | 46.5989 | 42.7597 | 14.5842 |  |  | -0.79949 | 0.050687 | 0.22001 | 0.047314 | 0.16182 | 0.21376 | 0.17732 | 0.56758 | -0.10098 | 0.89987 | 0.17832 | 8.8731 | 8.8747 | 0.89338 | 16.0772 | 16.6175 | 17.1469 | 17.4644 | 17.4127 | 16.3537 | 14.6866 | 16.749 | 17.0929 | 17.3779 | 17.4188 | 17.122 | 16.2799 | 14.4645 | 61.5765 | 27.6858 | 36.0629 | 26.5977 | 22.6806 | 41.8465 | 23.7397 | 15.8 | 15.5854 | 15.7741 | 14.3528 | 16.059 | 19.9381 |  |  |  | 72.4803 | 183.331 | 165.1124 | 123.1932 | 1.1259 | 0.8266 | 66.3956 |  |  | 12.0679 |  |  | 16.9381 | 17.59 | 32.0596 | 16.3466 | 16.3396 | 22.3211 | 193.8658 | 254.0647 | 160.5964 | 165.0423 | 135.1065 |  | 76.5608 | 139.3658 | 74.7723 | 150.8337 | 137.7377 | 177.9251 |  | 114.5984 |  |  | 19.5479 | 24.4408 | 79.6057 | [6 empty] | 130.4689 |  |  | 58.5786 |  |  | 25.5274 | 108.5802 | 286.7467 | 12.3034 | 96.5239 | 181.0148 | 15.1979 | 93.2856 | 205.7878 | 36.3414 | 161.6237 | 16.3174 | 148.5791 | 18.7774 | 157.2945 | 13.7809 | 93.4095 | 169.4108 | 43.6185 | 99.1916 | 208.6428 | 16.3059 | 83.1342 | 203.1928 | 18.5757 | 144.83 | 37.1074 | 151.9281 | 21.4988 | 168.1455 | 1.8738 | 18.6404 | 2.007 | 0.084383 | -38.1244 | 3.1237 | 390.38 | 48.96 | -1.3845 | 0.26358 | 0.54914 | 0.25466 | 0.47956 | 0.55119 | 0.50202 | -0.77822 | -0.96343 | 1.2524 | -1.634 | -0.92872 | -1.1986 | -0.59954
42810.4476 | 654 | 18.4702 | 18.5272 | 18.5022 | 18.5078 | 17.7997 | 16.3862 | 14.4396 | 16.5945 | 17.1041 | 17.2005 | 17.2065 | 16.7266 | 15.7398 | 14.3775 | 14.8181 | 14.8926 | 15.6545 | 13.2947 | 13.9679 | 19.0985 |  |  |  | 16.5849 | 16.8005 | 26.7261 | 194.1751 | 177.2756 | 224.7422 | 17.1444 | 16.7409 | 22.728 | 16.7851 | 16.7589 | 24.2197 | 91.8955 | 228.8894 |  | 129.3617 | 176.5975 | 174.6307 | 173.2658 |  | 7.5529 | 9.0934 | 7.3362 | 8.9659 | 9.7693 | 19.61 | 140.2813 | 4.8634 | 8.0145 | 4.7074 | 10.1052 | 9.1465 | 41.9925 | 46.612 | 42.7711 | 14.5798 |  |  | -0.94931 | -0.059053 | 0.099104 | -0.048626 | 0.052732 | 0.14016 | 0.20229 | 0.76078 | -0.11305 | 0.31872 | 0.37206 | 8.8767 | 8.8778 | 0.88348 | 16.0836 | 16.6213 | 17.1507 | 17.4666 | 17.4159 | 16.3569 | 14.6832 | 16.7522 | 17.0952 | 17.3879 | 17.4195 | 17.1297 | 16.2761 | 14.4709 | 61.3741 | 27.5216 | 38.9485 | 28.6161 | 24.328 | 41.9678 | 23.835 | 15.8135 | 15.5862 | 15.7766 | 14.3518 | 16.0759 | 19.9703 |  |  |  | 72.7865 | 183.5536 | 165.617 | 123.7656 | 1.1593 | 0.60208 | 66.5964 |  |  | 12.0814 |  |  | 16.9392 | 17.6032 | 32.1257 | 16.3521 | 16.346 | 22.3637 | 194.4892 | 255.9345 | 160.5315 | 164.8759 | 134.7133 |  | 76.8408 | 139.7011 | 75.0029 | 146.0522 | 138.4545 | 179.1846 |  | 114.9178 |  |  | 19.5724 | 24.5067 | 79.59 | [6 empty] | 129.8951 |  |  | 58.8613 |  |  | 25.6381 | 109.1322 | 289.2188 | 12.3121 | 96.9108 | 181.7175 | 15.2159 | 93.8659 | 207.003 | 36.5956 | 162.4972 | 16.336 | 149.1307 | 18.7636 | 157.4347 | 13.8297 | 93.7339 | 170.0174 | 43.9263 | 99.8845 | 209.273 | 16.3856 | 83.5186 | 204.1452 | 18.617 | 145.274 | 37.4207 | 152.4902 | 21.5563 | 168.9964 | 2.0835 | 18.6362 | 2.0087 | 0.082436 | -38.2226 | 3.1237 | 397.43 | 50.16 | -1.5151 | -0.28451 | 0.36857 | -0.25817 | 0.27382 | 0.44642 | 0.53631 | -0.7568 | -0.96414 | 1.4164 | -1.5972 | -1.2382 | -1.2534 | -0.60406
42810.4476 | 655 | 18.4823 | 18.5227 | 18.5084 | 18.5121 | 17.799 | 16.3925 | 14.434 | 16.6051 | 17.1014 | 17.2028 | 17.2066 | 16.7178 | 15.7424 | 14.3747 | 14.815 | 14.8875 | 15.6593 | 13.3045 | 13.9693 | 19.1274 |  |  |  | 16.5923 | 16.8155 | 26.7804 | 195.5887 | 177.6326 | 226.4967 | 17.141 | 16.761 | 22.7716 | 16.7824 | 16.7683 | 24.2743 | 92.4123 | 235.6206 |  | 130.0587 | 176.9616 | 175.3547 | 176.3063 |  | 7.5597 | 9.1411 | 7.3569 | 9.0196 | 9.8775 | 19.7535 | 141.6912 | 4.8581 | 8.0253 | 4.684 | 10.1256 | 9.1492 | 42.0296 | 46.6136 | 42.7761 | 14.5711 |  |  | -0.68252 | -0.045253 | 0.033392 | -0.10054 | 0.27024 | -0.030688 | 0.48617 | 0.71675 | -0.037542 | -0.3455 | 0.29158 | 8.8747 | 8.8755 | 0.88021 | 16.0775 | 16.6146 | 17.1443 | 17.463 | 17.4166 | 16.3534 | 14.6826 | 16.7506 | 17.086 | 17.3813 | 17.4223 | 17.13 | 16.274 | 14.4694 | 62.4839 | 28.1603 | 41.4684 | 29.6792 | 25.2192 | 42.1308 | 23.9284 | 15.8076 | 15.5876 | 15.7766 | 14.3616 | 16.0858 | 20.0051 |  |  |  | 73.108 | 183.7922 | 166.1376 | 124.8547 | 1.2795 | 0.94253 | 66.8402 |  |  | 12.0864 |  |  | 16.9449 | 17.6157 | 32.1934 | 16.3546 | 16.3571 | 22.3999 | 195.3237 | 257.6142 | 160.7306 | 164.8777 | 134.1903 |  | 77.0998 | 139.922 | 75.2216 | 143.2257 | 139.2725 | 181.262 |  | 115.3092 |  |  | 19.6407 | 24.5809 | 79.8206 | [6 empty] | 127.1683 |  |  | 59.1467 |  |  | 25.7792 | 109.363 | 292.1097 | 12.3451 | 97.4866 | 182.587 | 15.2457 | 94.5201 | 208.5402 | 36.8906 | 163.1155 | 16.3657 | 150.0127 | 18.777 | 157.6823 | 13.8666 | 93.9941 | 170.848 | 44.2054 | 100.3247 | 209.6778 | 16.4821 | 83.8888 | 205.03 | 18.6824 | 145.7338 | 37.7672 | 152.7809 | 21.6268 | 169.7923 | 2.2149 | 18.6325 | 2.0099 | 0.082798 | -38.2455 | 3.1237 | 432.09 | 49.46 | -1.2869 | -0.24908 | 0.21396 | -0.37126 | 0.62002 | -0.20894 | 0.83162 | -0.73256 | -0.9621 | 1.5306 | -1.7012 | -1.5072 | -1.3178 | -0.62236
42810.4476 | 656 | 18.4724 | 18.5211 | 18.5042 | 18.5013 | 17.7918 | 16.3803 | 14.4335 | 16.5899 | 17.1018 | 17.1929 | 17.2015 | 16.7235 | 15.7391 | 14.3689 | 14.822 | 14.8941 | 15.6596 | 13.2975 | 13.9509 | 19.1453 |  |  |  | 16.5978 | 16.8245 | 26.8229 | 196.8496 | 178.1386 | 229.8711 | 17.1438 | 16.7522 | 22.8036 | 16.7848 | 16.7622 | 24.3013 | 92.8141 | 241.2396 |  | 130.7237 | 177.5854 | 176.0994 | 178.5366 |  | 7.5783 | 9.1672 | 7.3725 | 9.0568 | 9.9388 | 19.7753 | 142.583 | 4.8739 | 8.0368 | 4.6288 | 10.1466 | 9.1492 | 42.041 | 46.6115 | 42.7712 | 14.5578 |  |  | -1.5723 | 0.011259 | 0.065592 | -0.3325 | 0.4562 | 0.45098 | 0.07744 | 0.20748 | -0.50984 | -0.51607 | 0.32218 | 8.8742 | 8.8753 | 0.88554 | 16.0798 | 16.6144 | 17.1403 | 17.4684 | 17.4129 | 16.3505 | 14.683 | 16.7458 | 17.0826 | 17.3827 | 17.4159 | 17.1224 | 16.2753 | 14.4629 | 63.96 | 29.3869 | 43.7205 | 30.8197 | 26.5654 | 42.2853 | 24.0399 | 15.8188 | 15.6008 | 15.7887 | 14.3621 | 16.1022 | 20.044 |  |  |  | 73.407 | 184.5232 | 167.693 | 125.6335 | 1.0337 | 0.36344 | 66.8354 |  |  | 12.0968 |  |  | 16.9475 | 17.619 | 32.2547 | 16.3531 | 16.3553 | 22.4285 | 195.9535 | 259.3049 | 161.1274 | 165.1131 | 134.0575 |  | 77.346 | 138.7107 | 75.4065 | 144.4056 | 140.0004 | 184.9591 |  | 115.6418 |  |  | 19.784 | 24.6582 | 80.0042 | [6 empty] | 126.6448 |  |  | 59.5346 |  |  | 25.9112 | 110.0317 | 294.3968 | 12.4124 | 98.2832 | 183.6647 | 15.2967 | 94.9718 | 210.2439 | 37.1515 | 163.7329 | 16.4197 | 150.5041 | 18.8213 | 158.1667 | 13.892 | 94.0337 | 171.6631 | 44.5182 | 100.7143 | 209.8282 | 16.5542 | 84.2276 | 206.1436 | 18.7561 | 146.2365 | 38.0392 | 153.1736 | 21.7255 | 170.3612 | 2.0791 | 18.6274 | 2.0111 | 0.083081 | -38.1604 | 3.1237 | 446.55 | 49.51 | -1.9598 | 0.12425 | 0.29989 | -0.6752 | 0.80561 | 0.80098 | 0.33192 | -0.71963 | -0.92154 | 1.5297 | -1.847 | -1.7444 | -1.3641 | -0.63287
42810.4476 | 657 | 18.475 | 18.5186 | 18.5029 | 18.5027 | 17.7968 | 16.3771 | 14.4301 | 16.5928 | 17.0969 | 17.1922 | 17.2063 | 16.722 | 15.742 | 14.3726 | 14.8255 | 14.8977 | 15.6669 | 13.2978 | 13.9477 | 19.169 |  |  |  | 16.5959 | 16.8281 | 26.8753 | 198.153 | 178.6201 | 231.8375 | 17.1565 | 16.771 | 22.8505 | 16.7969 | 16.7761 | 24.3519 | 93.2529 | 244.435 |  | 131.4338 | 178.3029 | 177.0095 | 179.4185 |  | 7.6036 | 9.1839 | 7.397 | 9.1006 | 10.002 | 19.7585 | 143.7092 | 4.9112 | 8.0503 | 4.5363 | 10.174 | 9.1545 | 42.0756 | 46.6167 | 42.7627 | 14.5555 |  |  | -1.0032 | -0.079425 | 0.019592 | -0.58023 | 0.33398 | 0.15659 | -0.24192 | 0.20683 | 0.60795 | -0.80014 | 0.51274 | 8.8761 | 8.8776 | 0.86227 | 16.0847 | 16.6182 | 17.1499 | 17.4602 | 17.4064 | 16.349 | 14.6766 | 16.7357 | 17.0861 | 17.3858 | 17.4108 | 17.1278 | 16.2744 | 14.4635 | 63.9529 | 29.3382 | 42.6127 | 30.6108 | 27.4834 | 42.3904 | 24.0984 | 15.8106 | 15.5949 | 15.787 | 14.3571 | 16.1071 | 20.0687 |  |  |  | 73.694 | 185.3041 | 168.499 | 126.1228 | 0.5185 | 0.56425 | 66.7506 |  |  | 12.1045 |  |  | 16.9431 | 17.6204 | 32.3133 | 16.3466 | 16.3478 | 22.4585 | 196.798 | 260.7617 | 161.4697 | 165.4077 | 134.6615 |  | 77.5892 | 136.3483 | 75.6066 | 149.1267 | 140.8315 | 185.4823 |  | 115.9978 |  |  | 19.9171 | 24.7485 | 80.0483 | [6 empty] | 126.2148 |  |  | 59.9562 |  |  | 26.0209 | 110.5985 | 296.1507 | 12.4828 | 98.6488 | 184.9293 | 15.3501 | 95.3523 | 212.1178 | 37.3899 | 164.3541 | 16.4811 | 150.8172 | 18.8731 | 158.5485 | 13.9334 | 94.6352 | 172.515 | 44.8293 | 101.2859 | 210.24 | 16.6189 | 84.6432 | 207.19 | 18.8094 | 146.7293 | 38.304 | 153.8038 | 21.8435 | 171.0583 | 2.2289 | 18.6247 | 2.0126 | 0.082255 | -38.2556 | 3.1238 | 447.1 | 49.77 | -1.5686 | -0.33001 | 0.1639 | -0.89197 | 0.68928 | 0.47197 | -0.58663 | -0.72728 | -0.84844 | 1.4349 | -1.8337 | -1.6145 | -1.3716 | -0.63578
42810.4477 | 658 | 18.4811 | 18.5247 | 18.5077 | 18.507 | 17.8013 | 16.3802 | 14.4342 | 16.5984 | 17.0975 | 17.1918 | 17.201 | 16.7252 | 15.7414 | 14.37 | 14.8243 | 14.8911 | 15.6695 | 13.296 | 13.9444 | 19.1915 |  |  |  | 16.588 | 16.8236 | 26.9158 | 199.4042 | 178.8366 | 233.8733 | 17.1556 | 16.7779 | 22.8781 | 16.7976 | 16.7868 | 24.3987 | 93.7181 | 245.7604 |  | 132.0641 | 179.1857 | 177.8223 | 181.6511 |  | 7.616 | 9.2124 | 7.4272 | 9.1382 | 10.0838 | 19.7886 | 144.9571 | 4.9754 | 8.0708 | 4.5076 | 10.2061 | 9.1616 | 42.1155 | 46.6279 | 42.7361 | 14.5387 |  |  | -1.2003 | 0.070399 | -0.025092 | -0.2681 | 0.23147 | -0.0504 | -0.305 | 0.64381 | -0.13115 | -0.29851 | 0.5795 | 8.8747 | 8.8761 | 0.84614 | 16.0892 | 16.6186 | 17.1492 | 17.4655 | 17.4129 | 16.3451 | 14.6773 | 16.7448 | 17.0847 | 17.3813 | 17.4204 | 17.1191 | 16.2741 | 14.4663 | 61.2717 | 27.5256 | 41.6197 | 31.0153 | 27.2516 | 42.4792 | 24.1773 | 15.8068 | 15.5845 | 15.7847 | 14.3583 | 16.1193 | 20.0951 |  |  |  | 74.0015 | 186.2897 | 168.9258 | 126.0464 | 1.5704 | 0.35459 | 66.7969 |  |  | 12.1058 |  |  | 16.9463 | 17.6332 | 32.3802 | 16.3485 | 16.36 | 22.4952 | 197.7891 | 261.9451 | 161.837 | 165.7538 | 135.8177 |  | 77.8566 | 134.8735 | 75.8155 | 151.7389 | 141.6566 | 184.3812 |  | 116.3393 |  |  | 20.038 | 24.881 | 80.1781 | [6 empty] | 124.3059 |  |  | 60.2677 |  |  | 26.1466 | 111.0965 | 298.4231 | 12.5396 | 98.9795 | 186.2388 | 15.4049 | 95.8291 | 214.1456 | 37.6625 | 164.8699 | 16.5438 | 151.2178 | 18.9295 | 158.9961 | 13.9639 | 95.3698 | 173.7545 | 45.1249 | 101.8563 | 210.6844 | 16.6825 | 85.0009 | 208.0159 | 18.8511 | 147.1928 | 38.6845 | 154.1969 | 21.9366 | 171.6075 | 2.1488 | 18.6231 | 2.0141 | 0.081821 | -38.2328 | 3.1238 | 468.5 | 49.03 | -1.7192 | 0.31071 | -0.1855 | -0.60635 | 0.57385 | -0.26778 | -0.65873 | -0.74935 | -0.79966 | 1.3986 | -1.5253 | -1.4949 | -1.4155 | -0.6222
42810.4477 | 659 | 18.4817 | 18.5259 | 18.5103 | 18.5104 | 17.8004 | 16.382 | 14.4338 | 16.5989 | 17.1007 | 17.1965 | 17.201 | 16.7209 | 15.7462 | 14.3675 | 14.8311 | 14.8994 | 15.6783 | 13.2995 | 13.9418 | 19.2219 |  |  |  | 16.588 | 16.8355 | 26.9719 | 200.3973 | 179.2419 | 231.6881 | 17.1554 | 16.7783 | 22.9145 | 16.7954 | 16.7946 | 24.4401 | 94.1593 | 249.51 |  | 132.7362 | 180.0695 | 178.5385 | 183.2796 |  | 7.6271 | 9.231 | 7.4216 | 9.1282 | 10.0891 | 19.7648 | 145.768 | 4.9642 | 8.0832 | 4.5317 | 10.2318 | 9.1554 | 42.1209 | 46.631 | 42.714 | 14.526 |  |  | -0.53139 | -0.14185 | -0.169 | 0.010514 | 0.090848 | -0.26659 | 0.051812 | 0.26597 | -0.16306 | 0.098224 | 0.43624 | 8.8753 | 8.8762 | 0.8576 | 16.0947 | 16.6248 | 17.1514 | 17.4682 | 17.4125 | 16.3525 | 14.6817 | 16.7571 | 17.0955 | 17.3878 | 17.4241 | 17.1237 | 16.2805 | 14.4698 | 62.4385 | 27.0832 | 40.413 | 30.5032 | 26.7605 | 42.6546 | 24.2515 | 15.8109 | 15.5918 | 15.7952 | 14.3662 | 16.1379 | 20.1239 |  |  |  | 74.2931 | 187.0526 | 169.5494 | 126.5664 | 1.0511 | 0.12028 | 66.8486 |  |  | 12.1094 |  |  | 16.9539 | 17.6411 | 32.4484 | 16.3542 | 16.3717 | 22.5328 | 198.9417 | 263.3466 | 162.1449 | 166.0735 | 136.9883 |  | 78.1689 | 135.4793 | 75.9921 | 150.5532 | 142.3839 | 185.0669 |  | 116.7174 |  |  | 20.1432 | 25.024 | 80.2686 | [6 empty] | 126.5841 |  |  | 60.6539 |  |  | 26.2494 | 111.5715 | 301.026 | 12.606 | 99.3287 | 187.7231 | 15.4383 | 96.3827 | 215.922 | 37.928 | 165.5804 | 16.6125 | 151.7542 | 18.9972 | 159.6915 | 13.9404 | 95.569 | 175.0188 | 45.4027 | 102.392 | 211.0634 | 16.7363 | 85.2063 | 209.131 | 18.8908 | 147.6286 | 38.9848 | 154.6017 | 22.0147 | 172.0459 | 2.2187 | 18.6212 | 2.0166 | 0.08345 | -38.255 | 3.1238 | 454.55 | 49.73 | -1.1414 | -0.44106 | -0.48142 | 0.12008 | 0.3595 | -0.61583 | 0.27149 | -0.77012 | -0.80988 | 1.4636 | -1.6342 | -1.3522 | -1.4435 | -0.62577
42810.4477 | 660 | 18.4808 | 18.5213 | 18.5137 | 18.513 | 17.7986 | 16.3842 | 14.4414 | 16.6004 | 17.1041 | 17.1958 | 17.2053 | 16.7195 | 15.7391 | 14.3696 | 14.8227 | 14.9103 | 15.6855 | 13.3022 | 13.9399 | 19.2592 |  |  |  | 16.5918 | 16.844 | 27.0266 | 200.9152 | 179.8708 | 228.6259 | 17.1495 | 16.777 | 22.949 | 16.7917 | 16.7952 | 24.4726 | 94.5854 | 253.4756 |  | 133.3948 | 180.9358 | 179.2728 | 185.2379 |  | 7.6565 | 9.2533 | 7.4006 | 9.1175 | 10.0876 | 19.7452 | 146.859 | 4.9885 | 8.1027 | 4.5717 | 10.2529 | 9.1614 | 42.133 | 46.6455 | 42.6811 | 14.5307 |  |  | -1.2647 | -0.10308 | -0.006036 | -0.17085 | 0.09216 | -0.11414 | 0.35606 | 0.28765 | 0.55482 | -0.021992 | 0.33013 | 8.8733 | 8.8745 | 0.85758 | 16.0997 | 16.62 | 17.1463 | 17.4697 | 17.4155 | 16.3616 | 14.6889 | 16.7537 | 17.0949 | 17.3923 | 17.4309 | 17.1326 | 16.2874 | 14.4663 | 61.5591 | 25.7885 | 38.041 | 29.1135 | 26.3944 | 42.7295 | 24.2857 | 15.8094 | 15.5946 | 15.805 | 14.3699 | 16.1583 | 20.1677 |  |  |  | 74.6141 | 187.4137 | 170.1702 | 127.1472 | 0.45164 | -0.16126 | 66.9999 |  |  | 12.1095 |  |  | 16.9481 | 17.6458 | 32.5107 | 16.3504 | 16.3688 | 22.5638 | 200.0558 | 264.815 | 162.3858 | 166.4275 | 136.9486 |  | 78.4511 | 134.496 | 76.1892 | 152.1888 | 143.0173 | 187.1456 |  | 117.0614 |  |  | 20.2347 | 25.1323 | 80.6426 | [6 empty] | 126.9399 |  |  | 61.165 |  |  | 26.3706 | 111.9567 | 304.014 | 12.6634 | 99.6416 | 189.1841 | 15.4746 | 96.7317 | 217.3208 | 38.1694 | 166.5391 | 16.6662 | 152.5123 | 19.0904 | 159.9173 | 13.9163 | 95.8654 | 176.1854 | 45.6804 | 102.9197 | 211.9741 | 16.8103 | 85.8002 | 210.8253 | 18.9651 | 148.2539 | 39.1694 | 154.9117 | 22.1019 | 172.645 | 2.2536 | 18.6212 | 2.0178 | 0.084593 | -38.1883 | 3.1238 | 474.99 | 48.67 | -1.7556 | -0.376 | -0.090986 | -0.48407 | 0.36207 | -0.40294 | 0.71168 | -0.7584 | -0.77519 | 1.446 | -1.5277 | -1.0846 | -1.4813 | -0.62993
42810.4477 | 661 | 18.4859 | 18.5245 | 18.5078 | 18.5064 | 17.801 | 16.3888 | 14.4396 | 16.5949 | 17.0984 | 17.2022 | 17.2071 | 16.727 | 15.7412 | 14.3691 | 14.8255 | 14.9095 | 15.6785 | 13.2972 | 13.9346 | 19.2777 |  |  |  | 16.5935 | 16.8424 | 27.076 | 201.6152 | 180.8388 | 231.2198 | 17.1668 | 16.7863 | 22.9913 | 16.8003 | 16.797 | 24.5231 | 95.0636 | 255.2508 |  | 134.0423 | 181.7667 | 180.0529 | 187.7748 |  | 7.6805 | 9.2827 | 7.4072 | 9.1356 | 10.1053 | 19.7034 | 148.0543 | 5.0923 | 8.1255 | 4.6475 | 10.2927 | 9.1706 | 42.1501 | 46.6442 | 42.6637 | 14.52 |  |  | -0.77452 | -0.25685 | 0.070848 | -0.34236 | 0.07376 | 0.12439 | 0.40994 | 0.29488 | -1.5118 | 0.018709 | 0.40345 | 8.8748 | 8.876 | 0.81697 | 16.1033 | 16.6169 | 17.1457 | 17.4676 | 17.4113 | 16.3547 | 14.6843 | 16.7562 | 17.09 | 17.3857 | 17.4195 | 17.1323 | 16.2832 | 14.461 | 58.9119 | 24.9274 | 35.4513 | 26.9163 | 24.4776 | 42.8131 | 24.3038 | 15.8123 | 15.5955 | 15.7978 | 14.3698 | 16.17 | 20.2005 |  |  |  | 74.9128 | 187.9526 | 170.5119 | 127.4358 | 1.6239 | 0.47429 | 67.3045 |  |  | 12.116 |  |  | 16.9477 | 17.6609 | 32.5786 | 16.35 | 16.3719 | 22.6018 | 201.0831 | 265.8833 | 162.6315 | 166.8555 | 137.0659 |  | 78.7747 | 134.3775 | 76.4289 | 158.5645 | 143.8625 | 188.2324 |  | 117.4273 |  |  | 20.266 | 25.2343 | 80.7335 | [6 empty] | 127.7539 |  |  | 61.7783 |  |  | 26.4846 | 112.4183 | 305.9098 | 12.7126 | 100.7031 | 190.2574 | 15.5352 | 97.3288 | 218.3613 | 38.3676 | 167.7979 | 16.7026 | 153.3119 | 19.1922 | 160.5911 | 13.9388 | 96.439 | 177.1845 | 46.0346 | 103.4387 | 213.5687 | 16.8429 | 86.0627 | 212.4329 | 19.0232 | 148.9397 | 39.3277 | 155.1247 | 22.2074 | 173.369 | 2.3597 | 18.6203 | 2.0201 | 0.085939 | -38.1122 | 3.1238 | 472.3 | 49.04 | -1.3774 | -0.59355 | 0.31174 | -0.68527 | 0.32389 | 0.42062 | 0.76358 | -0.74948 | -0.76292 | 1.3063 | -1.2236 | -0.79474 | -1.533 | -0.6268
42810.4477 | 662 | 18.4732 | 18.5282 | 18.4992 | 18.503 | 17.7929 | 16.3709 | 14.4336 | 16.5904 | 17.101 | 17.1968 | 17.2009 | 16.7211 | 15.7339 | 14.3694 | 14.8237 | 14.8986 | 15.6749 | 13.2985 | 13.9054 | 19.3002 |  |  |  | 16.59 | 16.8511 | 27.1214 | 202.423 | 181.7194 | 232.3569 | 17.1526 | 16.789 | 23.0188 | 16.7863 | 16.8008 | 24.5618 | 95.6498 | 259.0008 |  | 134.786 | 182.7862 | 181.1889 | 190.5443 |  | 7.6838 | 9.3141 | 7.4118 | 9.1524 | 10.1215 | 19.6365 | 149.2911 | 5.0898 | 8.1392 | 4.725 | 10.3255 | 9.168 | 42.1552 | 46.6438 | 42.6417 | 14.5167 |  |  | -0.6753 | -0.035397 | 0.15233 | -0.23656 | -0.082632 | -0.11874 | 0.3462 | 0.51699 | -0.43628 | 1.0297 | 0.29278 | 8.8737 | 8.8746 | 0.76358 | 16.1043 | 16.6211 | 17.1542 | 17.4713 | 17.4155 | 16.3549 | 14.6851 | 16.756 | 17.0941 | 17.3881 | 17.4236 | 17.1322 | 16.2855 | 14.4665 | 63.6616 | 28.6251 | 37.1257 | 26.7495 | 23.4712 | 43.0662 | 24.3607 | 15.8131 | 15.5977 | 15.8064 | 14.3676 | 16.1839 | 20.2304 |  |  |  | 75.1943 | 187.9924 | 170.6984 | 128.1223 | 1.8749 | 1.1292 | 67.5865 |  |  | 12.127 |  |  | 16.9504 | 17.6738 | 32.6435 | 16.3565 | 16.3778 | 22.6427 | 202.5375 | 267.4002 | 162.903 | 167.1867 | 137.8208 |  | 79.024 | 135.7416 | 76.6766 | 155.861 | 144.6425 | 188.1947 |  | 117.7927 |  |  | 20.3478 | 25.3251 | 81.1773 | [6 empty] | 127.8949 |  |  | 62.2869 |  |  | 26.5591 | 112.8184 | 307.5324 | 12.7487 | 101.4282 | 190.9121 | 15.6071 | 97.9519 | 219.4652 | 38.5678 | 168.2147 | 16.7138 | 153.9726 | 19.2725 | 160.9512 | 13.9889 | 97.072 | 178.2038 | 46.3244 | 103.9423 | 214.9545 | 16.8904 | 86.0445 | 214.0125 | 19.0374 | 149.7564 | 39.4597 | 155.5 | 22.3364 | 173.84 | 2.4067 | 18.618 | 2.0219 | 0.085809 | -38.2725 | 3.1239 | 461.63 | 50.09 | -1.2876 | -0.22036 | 0.45713 | -0.56967 | -0.34278 | -0.4109 | 0.70163 | -0.76105 | -0.79152 | 1.4159 | -1.7215 | -0.97411 | -1.587 | -0.63536
42810.4477 | 663 | 18.4733 | 18.5306 | 18.502 | 18.5083 | 17.7927 | 16.3813 | 14.4226 | 16.5937 | 17.0988 | 17.1919 | 17.1972 | 16.7171 | 15.7346 | 14.3712 | 14.8206 | 14.9134 | 15.6839 | 13.3056 | 13.9332 | 19.3457 |  |  |  | 16.6043 | 16.8569 | 27.1791 | 203.109 | 182.2247 | 233.5949 | 17.167 | 16.7981 | 23.0657 | 16.7974 | 16.8135 | 24.617 | 96.1493 | 259.8867 |  | 135.5221 | 183.6605 | 182.3976 | 191.4086 |  | 7.7134 | 9.3376 | 7.4345 | 9.1881 | 10.1595 | 19.5952 | 150.6146 | 5.1587 | 8.1516 | 4.7974 | 10.3546 | 9.1788 | 42.1537 | 46.6512 | 42.6164 | 14.5104 |  |  | -0.75809 | -0.21807 | 0.018936 | -0.028914 | 0.030392 | 0.24662 | 0.4612 | 0.14703 | -0.23097 | -0.10843 | 0.27191 | 8.8745 | 8.8753 | 0.79256 | 16.1076 | 16.6252 | 17.1524 | 17.4682 | 17.4131 | 16.3543 | 14.6894 | 16.7577 | 17.093 | 17.3856 | 17.4248 | 17.1293 | 16.2862 | 14.472 | 67.7539 | 31.7986 | 40.7904 | 27.8928 | 23.9738 | 43.3098 | 24.4762 | 15.8178 | 15.5989 | 15.8096 | 14.3693 | 16.19 | 20.2653 |  |  |  | 75.477 | 187.6817 | 170.835 | 128.482 | 1.6579 | 0.62316 | 67.9505 |  |  | 12.1351 |  |  | 16.9459 | 17.6794 | 32.7093 | 16.3574 | 16.3853 | 22.6763 | 203.5063 | 269.4912 | 163.1931 | 167.4214 | 138.3625 |  | 79.3016 | 138.5238 | 76.9157 | 157.5042 | 145.5089 | 189.6233 |  | 118.1553 |  |  | 20.4353 | 25.4089 | 80.9679 | [6 empty] | 130.2592 |  |  | 62.6395 |  |  | 26.6905 | 113.3399 | 309.2825 | 12.7488 | 102.1795 | 191.4152 | 15.6865 | 98.1426 | 220.8057 | 38.7915 | 169.1235 | 16.7346 | 154.5467 | 19.3608 | 161.6458 | 14.0505 | 97.42 | 179.2874 | 46.653 | 104.4596 | 214.6223 | 16.9431 | 86.6295 | 215.0366 | 19.0685 | 150.7218 | 39.7064 | 155.7319 | 22.4996 | 174.3157 | 2.2809 | 18.6173 | 2.0236 | 0.085237 | -38.342 | 3.1239 | 470.12 | 49.58 | -1.3659 | -0.54698 | 0.16118 | -0.19917 | 0.20787 | 0.59214 | 0.80976 | -0.76563 | -0.85984 | 1.4087 | -2.1474 | -1.3678 | -1.5915 | -0.63478
42810.4477 | 664 | 18.4775 | 18.5288 | 18.5049 | 18.508 | 17.7986 | 16.3873 | 14.4292 | 16.5963 | 17.1028 | 17.1941 | 17.202 | 16.7224 | 15.7387 | 14.3708 | 14.8379 | 14.9064 | 15.6933 | 13.3037 | 13.9507 | 19.3704 |  |  |  | 16.6023 | 16.8708 | 27.233 | 203.6689 | 182.9596 | 233.5629 | 17.1658 | 16.7929 | 23.0912 | 16.8011 | 16.8105 | 24.6553 | 96.6526 | 258.3857 |  | 136.0913 | 184.7224 | 183.3329 | 191.3134 |  | 7.7396 | 9.3623 | 7.4656 | 9.2185 | 10.1884 | 19.6372 | 151.8066 | 5.1274 | 8.1635 | 4.8417 | 10.3845 | 9.1862 | 42.1538 | 46.6727 | 42.6094 | 14.4986 |  |  | -1.3561 | -0.070881 | 0.1589 | -0.15114 | 0.19138 | -0.03266 | 0.38037 | 0.25282 | -0.31504 | 0.029199 | 0.33609 | 8.8756 | 8.8766 | 0.8103 | 16.1082 | 16.6183 | 17.1438 | 17.4644 | 17.4069 | 16.352 | 14.6823 | 16.7426 | 17.0926 | 17.3841 | 17.4266 | 17.1267 | 16.2841 | 14.469 | 71.5667 | 34.126 | 42.9242 | 29.1617 | 23.8146 | 43.5865 | 24.5612 | 15.8111 | 15.6001 | 15.8191 | 14.3794 | 16.2023 | 20.2912 |  |  |  | 75.7901 | 187.5133 | 171.2102 | 129.0095 | 1.4383 | 1.1317 | 68.2988 |  |  | 12.1419 |  |  | 16.9434 | 17.6874 | 32.7787 | 16.3538 | 16.3956 | 22.7059 | 204.3348 | 271.5373 | 163.5868 | 167.7375 | 139.6446 |  | 79.6473 | 140.7899 | 77.1579 | 156.1235 | 146.2322 | 191.8798 |  | 118.5774 |  |  | 20.4681 | 25.5332 | 81.2122 | [6 empty] | 129.8361 |  |  | 62.802 |  |  | 26.8289 | 114.1368 | 312.4296 | 12.7997 | 102.9211 | 192.1009 | 15.7617 | 98.5027 | 222.1272 | 39.0228 | 169.2735 | 16.7551 | 155.0457 | 19.4604 | 162.8659 | 14.0703 | 97.3182 | 180.2559 | 46.8751 | 104.8896 | 214.7287 | 16.972 | 87.2704 | 216.1809 | 19.1324 | 151.424 | 40.0519 | 155.9522 | 22.636 | 175.3215 | 2.0689 | 18.6174 | 2.0257 | 0.085353 | -38.2212 | 3.1238 | 468.88 | 49.07 | -1.8268 | -0.31185 | 0.46693 | -0.45538 | 0.52167 | -0.2155 | 0.73544 | -0.78821 | -0.9137 | 1.4792 | -2.5383 | -1.5949 | -1.5691 | -0.63772
42810.4477 | 665 | 18.486 | 18.537 | 18.5041 | 18.5096 | 17.8054 | 16.3842 | 14.4307 | 16.5904 | 17.1056 | 17.1943 | 17.2071 | 16.7243 | 15.7445 | 14.3714 | 14.8347 | 14.9185 | 15.6926 | 13.3026 | 13.9677 | 19.4 |  |  |  | 16.5978 | 16.8719 | 27.283 | 204.5485 | 183.8608 | 238.0318 | 17.1692 | 16.8042 | 23.1348 | 16.7972 | 16.8182 | 24.6954 | 97.1623 | 258.8914 |  | 136.6542 | 185.5376 | 184.1557 | 190.981 |  | 7.7518 | 9.3979 | 7.4885 | 9.2501 | 10.237 | 19.6651 | 153.157 | 4.975 | 8.1792 | 4.9554 | 10.4199 | 9.183 | 42.1585 | 46.6634 | 42.5894 | 14.4849 |  |  | -1.7438 | -0.12608 | -0.14009 | -0.32067 | 0.37998 | -0.0734 | 0.44608 | 0.43025 | 0.18819 | -0.049056 | 0.37603 | 8.8904 | 8.8915 | 0.81948 | 16.1089 | 16.6129 | 17.1504 | 17.4731 | 17.4088 | 16.3497 | 14.6846 | 16.7439 | 17.0878 | 17.3887 | 17.4213 | 17.1289 | 16.2726 | 14.4672 | 72.9915 | 33.9792 | 45.8353 | 30.7046 | 25.4595 | 43.8349 | 24.6817 | 15.8079 | 15.6019 | 15.8155 | 14.3726 | 16.2229 | 20.3308 |  |  |  | 76.1198 | 187.8691 | 171.6658 | 129.8677 | 1.5364 | 0.85445 | 68.4784 |  |  | 12.153 |  |  | 16.9485 | 17.6956 | 32.8418 | 16.3588 | 16.401 | 22.7452 | 205.7252 | 273.5748 | 164.1003 | 168.2118 | 141.7384 |  | 79.9609 | 140.6704 | 77.4478 | 155.5096 | 146.9511 | 193.8566 |  | 119.0303 |  |  | 20.4397 | 25.6568 | 81.5453 | [6 empty] | 127.5428 |  |  | 63.1045 |  |  | 26.9624 | 114.5873 | 315.8091 | 12.8256 | 103.4093 | 192.9066 | 15.8461 | 98.9976 | 223.9715 | 39.3001 | 169.5137 | 16.7989 | 155.8915 | 19.5504 | 163.1667 | 14.0857 | 97.9272 | 181.2961 | 47.1108 | 105.3233 | 215.2568 | 17.0206 | 87.5134 | 217.7598 | 19.2156 | 152.0774 | 40.342 | 156.7602 | 22.7448 | 176.2776 | 2.3312 | 18.6169 | 2.0287 | 0.085259 | -38.2476 | 3.1239 | 470.09 | 50.51 | -2.0806 | -0.41594 | -0.43844 | -0.66335 | 0.73509 | -0.32308 | 0.79647 | -0.83453 | -0.8995 | 1.5283 | -2.6672 | -1.9043 | -1.5398 | -0.64922
42810.4477 | 666 | 18.4855 | 18.5292 | 18.5063 | 18.508 | 17.7996 | 16.3815 | 14.4246 | 16.5903 | 17.0922 | 17.1981 | 17.2057 | 16.7225 | 15.7432 | 14.3652 | 14.8363 | 14.9138 | 15.6923 | 13.3057 | 13.947 | 19.4226 |  |  |  | 16.5933 | 16.8756 | 27.33 | 206.4246 | 184.7111 | 246.3605 | 17.1772 | 16.8079 | 23.1665 | 16.7972 | 16.822 | 24.7321 | 97.6384 | 260.3585 |  | 137.2871 | 186.4088 | 185.0429 | 189.7546 |  | 7.7844 | 9.4384 | 7.5241 | 9.3023 | 10.2932 | 19.6416 | 154.1476 | 4.9337 | 8.1938 | 5.0267 | 10.4538 | 9.1808 | 42.1619 | 46.6649 | 42.5819 | 14.4823 |  |  | -1.2798 | -0.086653 | -0.000776 | -0.000658 | 0.1237 | 0.31758 | 0.49011 | 0.55707 | -1.0401 | -0.27354 | 0.41061 | 8.8699 | 8.8709 | 0.81165 | 16.1166 | 16.6202 | 17.1482 | 17.474 | 17.4067 | 16.3426 | 14.6793 | 16.7554 | 17.0961 | 17.3893 | 17.4279 | 17.1276 | 16.2828 | 14.4595 | 73.3432 | 33.7222 | 47.7119 | 32.8293 | 26.3225 | 44.0499 | 24.8185 | 15.8205 | 15.6043 | 15.8214 | 14.3789 | 16.2435 | 20.3678 |  |  |  | 76.4316 | 188.3553 | 172.2225 | 130.4558 | 2.003 | 0.94742 | 68.8983 |  |  | 12.1622 |  |  | 16.9544 | 17.7035 | 32.9029 | 16.3567 | 16.3994 | 22.7854 | 206.6507 | 275.8152 | 164.7232 | 168.7995 | 142.4074 |  | 80.2342 | 141.5101 | 77.7012 | 155.4896 | 147.6478 | 195.1323 |  | 119.4426 |  |  | 20.5192 | 25.8213 | 81.6571 | [6 empty] | 127.4888 |  |  | 63.692 |  |  | 27.0876 | 115.0869 | 319.4086 | 12.8361 | 103.5897 | 194.0909 | 15.934 | 99.1464 | 225.5159 | 39.6982 | 170.1362 | 16.8676 | 156.9819 | 19.6243 | 163.6306 | 14.1538 | 98.1726 | 182.2936 | 47.385 | 105.7879 | 216.3966 | 17.0469 | 87.9609 | 219.3972 | 19.2911 | 152.5076 | 40.6536 | 157.1974 | 22.9087 | 177.5695 | 2.572 | 18.616 | 2.0311 | 0.084622 | -38.2681 | 3.1239 | 467.93 | 49.37 | -1.797 | -0.34485 | -0.032634 | -0.030051 | 0.4194 | 0.67201 | 0.83482 | -0.84279 | -0.91331 | 1.56 | -2.6808 | -2.0968 | -1.487 | -0.65388
42810.4478 | 667 | 18.4828 | 18.5278 | 18.4969 | 18.5057 | 17.7936 | 16.376 | 14.4259 | 16.5878 | 17.0925 | 17.1913 | 17.2011 | 16.7235 | 15.7311 | 14.3592 | 14.8395 | 14.9125 | 15.6924 | 13.3107 | 13.9734 | 19.4582 |  |  |  | 16.5994 | 16.8795 | 27.3854 | 208.0546 | 185.6125 | 246.7705 | 17.1791 | 16.8054 | 23.2035 | 16.8036 | 16.8272 | 24.7614 | 98.1937 | 265.0675 |  | 138.0347 | 187.4167 | 185.9649 | 191.7359 |  | 7.8222 | 9.4847 | 7.5629 | 9.3783 | 10.3594 | 19.6235 | 155.4693 | 4.9305 | 8.2143 | 5.0856 | 10.4855 | 9.1884 | 42.189 | 46.6695 | 42.5855 | 14.4784 |  |  | -1.1228 | -0.072853 | -0.05466 | -0.31081 | 0.066532 | 0.069196 | 0.38826 | 0.2364 | 0.17029 | 0.81007 | 0.61805 | 7.1085 | 7.1093 | 0.78962 | 16.1111 | 16.6045 | 17.1384 | 17.4668 | 17.4047 | 16.3364 | 14.6726 | 16.7442 | 17.0879 | 17.3885 | 17.4119 | 17.122 | 16.2735 | 14.4528 | 76.361 | 34.3661 | 50.0485 | 33.8705 | 28.4961 | 44.3454 | 24.979 | 15.8156 | 15.6094 | 15.8235 | 14.3747 | 16.2515 | 20.4012 |  |  |  | 76.7523 | 189.2137 | 173.3647 | 130.8745 | 1.449 | 1.5389 | 69.4715 |  |  | 12.1735 |  |  | 16.9581 | 17.7194 | 32.9671 | 16.3544 | 16.4028 | 22.8175 | 207.5732 | 278.5178 | 165.4621 | 169.5423 | 143.8595 |  | 80.5344 | 142.1659 | 77.9383 | 151.6772 | 148.1896 | 196.4947 |  | 119.855 |  |  | 20.6228 | 25.9862 | 82.9085 | [6 empty] | 125.2246 |  |  | 64.5254 |  |  | 27.2755 | 115.7972 | 323.1431 | 12.8547 | 104.1853 | 195.2264 | 15.9958 | 99.4512 | 227.6443 | 40.1579 | 170.7857 | 16.9652 | 157.8148 | 19.7192 | 164.8071 | 14.2311 | 98.6557 | 183.2945 | 47.7409 | 106.3576 | 217.6032 | 17.1191 | 88.8532 | 221.0113 | 19.3693 | 152.8966 | 41.0281 | 157.6454 | 23.0922 | 178.5364 | 2.8037 | 18.6176 | 2.0347 | 0.084485 | -38.1639 | 3.124 | 486.21 | 49.48 | -1.6838 | -0.31623 | -0.27391 | -0.65318 | 0.30757 | 0.31367 | 0.74301 | -0.87178 | -0.92261 | 1.6901 | -2.9811 | -2.3376 | -1.5202 | -0.65349
42810.4478 | 668 | 18.494 | 18.5348 | 18.5152 | 18.5179 | 17.7975 | 16.3879 | 14.4297 | 16.6008 | 17.1078 | 17.2086 | 17.2154 | 16.7337 | 15.7511 | 14.3722 | 14.8445 | 14.925 | 15.7048 | 13.3169 | 14.0073 | 19.4919 |  |  |  | 16.6162 | 16.8995 | 27.4463 | 209.5475 | 186.9623 | 247.6537 | 17.1732 | 16.824 | 23.2379 | 16.8073 | 16.8386 | 24.8146 | 98.7752 | 270.2749 |  | 138.8697 | 188.5505 | 187.0053 | 197.9333 |  | 7.8417 | 9.5167 | 7.6019 | 9.4496 | 10.4347 | 19.7109 | 156.7421 | 4.9419 | 8.2287 | 5.1015 | 10.5161 | 9.2011 | 42.1976 | 46.6864 | 42.5926 | 14.4767 |  |  | -1.0472 | 0.043459 | -0.030348 | -0.10777 | 0.011992 | 0.03108 | 0.53808 | 0.27057 | -0.24129 | 0.78784 | 0.91729 | 5.0255 | 5.026 | 0.78297 | 16.1195 | 16.6119 | 17.1394 | 17.4591 | 17.4082 | 16.3411 | 14.6807 | 16.7494 | 17.09 | 17.3877 | 17.4219 | 17.1273 | 16.2757 | 14.4593 | 78.4466 | 34.0818 | 54.2883 | 35.5078 | 30.9206 | 44.6304 | 25.1568 | 15.8206 | 15.6155 | 15.8323 | 14.3808 | 16.2668 | 20.4337 |  |  |  | 77.0948 | 190.3329 | 174.5735 | 130.91 | 1.696 | 1.6103 | 69.9144 |  |  | 12.1873 |  |  | 16.9539 | 17.7328 | 33.0278 | 16.3589 | 16.4075 | 22.8559 | 209.2431 | 282.4633 | 166.2278 | 170.4841 | 143.997 |  | 80.896 | 144.2632 | 78.2349 | 148.638 | 148.7309 | 195.8059 |  | 120.3973 |  |  | 20.6307 | 26.1187 | 83.8291 | [6 empty] | 123.6512 |  |  | 65.5096 |  |  | 27.4484 | 116.602 | 327.3864 | 12.8754 | 104.442 | 196.743 | 16.028 | 100.0575 | 230.4228 | 40.7168 | 171.8496 | 17.0631 | 158.6266 | 19.8394 | 165.6992 | 14.3223 | 99.3002 | 184.1412 | 48.1514 | 106.9748 | 218.9533 | 17.2259 | 89.8404 | 223.1053 | 19.465 | 153.4949 | 41.4444 | 158.3239 | 23.2945 | 180.0117 | 2.3921 | 18.6151 | 2.0379 | 0.08476 | -38.1567 | 3.1239 | 492.83 | 50.31 | -1.6275 | 0.24426 | -0.20411 | -0.38463 | 0.1306 | 0.21025 | 0.87482 | -0.86192 | -0.96972 | 1.7987 | -3.1791 | -2.7878 | -1.6695 | -0.64163
42810.4478 | 669 | 18.493 | 18.5366 | 18.5203 | 18.5194 | 17.8063 | 16.3865 | 14.4298 | 16.5929 | 17.1028 | 17.2031 | 17.2154 | 16.7272 | 15.7486 | 14.3677 | 14.8434 | 14.9201 | 15.7068 | 13.3121 | 14.0084 | 19.5135 |  |  |  | 16.6113 | 16.9032 | 27.4979 | 211.1292 | 188.1806 | 252.0284 | 17.1829 | 16.8252 | 23.2805 | 16.8133 | 16.8418 | 24.8488 | 99.3848 | 277.4904 |  | 139.7885 | 189.879 | 188.3026 | 201.6834 |  | 7.8379 | 9.5416 | 7.6306 | 9.5214 | 10.507 | 19.777 | 157.6324 | 4.8656 | 8.2429 | 5.1243 | 10.5545 | 9.2058 | 42.1935 | 46.6904 | 42.5893 | 14.4671 |  |  | -0.90791 | -0.2345 | 0.083988 | -0.30359 | 0.30375 | 0.069196 | 0.35474 | 0.51633 | -0.12025 | -0.12291 | 0.79807 | 3.5753 | 3.5757 | 0.79535 | 16.1218 | 16.6174 | 17.1421 | 17.4677 | 17.4097 | 16.3503 | 14.685 | 16.753 | 17.0895 | 17.3842 | 17.4254 | 17.1323 | 16.2815 | 14.4655 | 81.108 | 34.3715 | 55.3558 | 36.8762 | 31.5357 | 44.9357 | 25.3114 | 15.8199 | 15.6076 | 15.836 | 14.3843 | 16.2809 | 20.4689 |  |  |  | 77.4715 | 191.2211 | 175.3939 | 130.9583 | 1.9308 | 0.56989 | 70.3571 |  |  | 12.1995 |  |  | 16.9573 | 17.7348 | 33.0852 | 16.3594 | 16.4058 | 22.891 | 210.7803 | 288.0101 | 166.8309 | 171.2559 | 145.2033 |  | 81.3026 | 147.5648 | 78.4917 | 148.8497 | 149.2812 | 195.5287 |  | 120.8278 |  |  | 20.6887 | 26.2928 | 84.3142 | [6 empty] | 123.1988 |  |  | 66.4274 |  |  | 27.6322 | 117.5651 | 335.1016 | 12.9194 | 105.1468 | 198.9079 | 16.0737 | 100.7204 | 233.3353 | 41.3323 | 173.2554 | 17.1538 | 159.2937 | 19.9728 | 167.1221 | 14.3989 | 100.0659 | 185.3257 | 48.5878 | 107.6936 | 220.0835 | 17.3142 | 90.5134 | 225.7561 | 19.5573 | 154.4678 | 41.8763 | 158.9596 | 23.5269 | 181.3955 | 2.5839 | 18.6136 | 2.0419 | 0.084101 | -38.1892 | 3.1239 | 484.02 | 49.22 | -1.5217 | -0.56741 | 0.33957 | -0.6456 | 0.65736 | 0.31375 | 0.7104 | -0.88004 | -1.0518 | 1.8175 | -3.4387 | -2.8883 | -1.7496 | -0.62883
42810.4478 | 670 | 18.4935 | 18.5309 | 18.5094 | 18.5032 | 17.7934 | 16.3854 | 14.4266 | 16.5977 | 17.094 | 17.2047 | 17.2096 | 16.7235 | 15.7507 | 14.3636 | 14.853 | 14.9209 | 15.7125 | 13.3125 | 14.0201 | 19.5372 |  |  |  | 16.61 | 16.9054 | 27.5443 | 213.1217 | 189.5198 | 258.2738 | 17.1959 | 16.838 | 23.3114 | 16.8172 | 16.8536 | 24.8956 | 100.1002 | 284.518 |  | 140.8384 | 191.9202 | 190.1842 | 207.1043 |  | 7.8446 | 9.5765 | 7.664 | 9.5992 | 10.62 | 19.8035 | 159.1943 | 4.7857 | 8.264 | 5.0761 | 10.6005 | 9.2118 | 42.1852 | 46.6993 | 42.5913 | 14.4574 |  |  | -0.70093 | -0.060365 | 0.047192 | -0.07097 | 0.13882 | 0.20785 | 0.2358 | 0.58007 | -0.92784 | -0.4353 | 0.43346 | 2.5565 | 2.5568 | 0.80164 | 16.1268 | 16.6166 | 17.146 | 17.4703 | 17.4163 | 16.3508 | 14.6868 | 16.7605 | 17.0943 | 17.3878 | 17.4261 | 17.1368 | 16.2888 | 14.4671 | 83.4862 | 31.7418 | 53.9476 | 35.9978 | 31.3829 | 45.2618 | 25.4509 | 15.8234 | 15.6082 | 15.8324 | 14.3714 | 16.2845 | 20.5002 |  |  |  | 77.8914 | 192.4861 | 176.1612 | 131.593 | 2.0937 | 0.74586 | 70.5194 |  |  | 12.2078 |  |  | 16.9516 | 17.7359 | 33.1305 | 16.3586 | 16.407 | 22.9142 | 212.4859 | 294.4413 | 167.4294 | 171.8742 | 148.2628 |  | 81.6891 | 149.8039 | 78.7519 | 149.979 | 149.8548 | 196.7052 |  | 121.2945 |  |  | 20.8285 | 26.4799 | 84.5438 | [6 empty] | 123.3718 |  |  | 67.4721 |  |  | 27.861 | 118.6742 | 343.6389 | 12.9851 | 106.0273 | 201.3762 | 16.1579 | 101.5966 | 236.705 | 42.0339 | 175.0281 | 17.2504 | 160.218 | 20.1205 | 168.9077 | 14.492 | 100.9405 | 187.075 | 49.0818 | 108.5042 | 221.3243 | 17.4084 | 90.908 | 228.2012 | 19.6725 | 155.75 | 42.3144 | 159.7066 | 23.762 | 183.1476 | 2.6234 | 18.6103 | 2.0456 | 0.083428 | -38.1699 | 3.124 | 511.96 | 49.81 | -1.345 | -0.2879 | 0.25456 | -0.31217 | 0.44441 | 0.5438 | 0.57922 | -0.95038 | -1.1042 | 1.8119 | -3.6643 | -2.7155 | -1.8719 | -0.63068
42810.4478 | 671 | 18.4957 | 18.5346 | 18.5116 | 18.5121 | 17.8017 | 16.3841 | 14.4328 | 16.5952 | 17.1078 | 17.1988 | 17.2124 | 16.7234 | 15.7439 | 14.3725 | 14.8485 | 14.9182 | 15.7125 | 13.3133 | 14.0386 | 19.5582 |  |  |  | 16.604 | 16.908 | 27.586 | 215.1028 | 190.8741 | 261.0169 | 17.1871 | 16.8374 | 23.3435 | 16.8138 | 16.8515 | 24.9291 | 100.8212 | 286.1437 |  | 141.6965 | 194.3504 | 192.4134 | 212.2969 |  | 7.8515 | 9.6194 | 7.7067 | 9.6842 | 10.7396 | 19.8087 | 160.307 | 4.7006 | 8.2862 | 5.0182 | 10.6424 | 9.2161 | 42.1831 | 46.7213 | 42.6057 | 14.4588 |  |  | -1.0137 | 0.11837 | 0.052448 | 0.037454 | 0.1329 | -0.12137 | 0.16615 | 0.77918 | -0.16442 | -0.72902 | 0.91789 | 1.8371 | 1.8373 | 0.77951 | 16.1189 | 16.6062 | 17.1361 | 17.4596 | 17.4078 | 16.3402 | 14.6723 | 16.7442 | 17.088 | 17.3766 | 17.4216 | 17.1176 | 16.2734 | 14.4551 | 87.2682 | 34.8902 | 53.4961 | 36.3594 | 31.2513 | 45.6709 | 25.612 | 15.8194 | 15.6123 | 15.8433 | 14.3802 | 16.2975 | 20.5355 |  |  |  | 78.3043 | 194.4665 | 176.9233 | 132.7299 | 1.7446 | 1.3238 | 70.5192 |  |  | 12.2249 |  |  | 16.9501 | 17.7461 | 33.1977 | 16.3643 | 16.4247 | 22.9543 | 214.3419 | 302.4795 | 168.312 | 172.898 | 152.4564 |  | 82.1724 | 148.8418 | 79.0499 | 150.9876 | 150.5996 | 201.898 |  | 121.8997 |  |  | 21.0245 | 26.7062 | 85.2298 | [6 empty] | 124.3506 |  |  | 68.4407 |  |  | 28.109 | 120.0376 | 349.4411 | 13.0143 | 106.5368 | 203.7618 | 16.2412 | 102.7276 | 240.2271 | 42.8488 | 176.9115 | 17.3624 | 161.3642 | 20.2889 | 170.3358 | 14.603 | 102.2848 | 189.217 | 49.6415 | 109.2623 | 223.1391 | 17.5057 | 91.5979 | 230.7498 | 19.8157 | 157.165 | 42.8343 | 160.3783 | 24.0023 | 184.636 | 2.7409 | 18.6056 | 2.0494 | 0.082733 | -38.1797 | 3.124 | 551.19 | 49.73 | -1.6217 | 0.40318 | 0.26838 | 0.22679 | 0.43484 | -0.41555 | 0.48621 | -1.0485 | -1.0662 | 1.8174 | -4.0361 | -2.6465 | -1.9875 | -0.64674
42810.4478 | 672 | 18.5024 | 18.5439 | 18.5164 | 18.5232 | 17.8105 | 16.3931 | 14.4359 | 16.6014 | 17.1114 | 17.2073 | 17.2159 | 16.7275 | 15.7501 | 14.3821 | 14.8419 | 14.9228 | 15.711 | 13.313 | 14.0017 | 19.5908 |  |  |  | 16.6096 | 16.9162 | 27.6462 | 217.0608 | 192.041 | 266.5329 | 17.1848 | 16.835 | 23.387 | 16.8085 | 16.8572 | 24.9771 | 101.6164 | 294.828 |  | 142.6242 | 196.7435 | 194.4842 | 218.9017 |  | 7.8525 | 9.676 | 7.7636 | 9.7823 | 10.8558 | 19.8869 | 161.4846 | 4.6233 | 8.3023 | 4.9554 | 10.6872 | 9.2276 | 42.1927 | 46.7409 | 42.6198 | 14.4572 |  |  | -0.87769 | -0.021597 | 0.11093 | -0.35813 | 0.12896 | -0.16474 | 0.33043 | 0.93754 | -0.73032 | -0.71664 | 1.0822 | 1.3268 | 1.327 | 0.76475 | 16.1269 | 16.6096 | 17.1416 | 17.4646 | 17.4013 | 16.3388 | 14.6735 | 16.7435 | 17.0836 | 17.3809 | 17.419 | 17.1148 | 16.2721 | 14.4591 | 89.9439 | 36.4187 | 54.9366 | 36.854 | 31.7585 | 46.0546 | 25.7836 | 15.8183 | 15.6123 | 15.8435 | 14.3877 | 16.3163 | 20.5606 |  |  |  | 78.7544 | 196.6513 | 177.7731 | 134.6109 | 1.9515 | 0.51212 | 70.7682 |  |  | 12.2438 |  |  | 16.9583 | 17.7644 | 33.261 | 16.3669 | 16.4321 | 22.9927 | 217.1601 | 311.1643 | 169.5745 | 174.3492 | 155.714 |  | 82.6679 | 146.4827 | 79.3479 | 152.3851 | 151.3881 | 207.0481 |  | 122.5229 |  |  | 21.2803 | 26.9569 | 86.2264 | [6 empty] | 126.4117 |  |  | 69.7481 |  |  | 28.3996 | 121.6494 | 354.9906 | 13.0603 | 107.4425 | 206.8036 | 16.331 | 103.5284 | 246.0663 | 43.838 | 179.0862 | 17.4992 | 162.8739 | 20.487 | 171.9637 | 14.7133 | 103.3464 | 191.4498 | 50.2336 | 110.1433 | 226.0866 | 17.619 | 92.354 | 233.4989 | 19.9659 | 158.4825 | 43.4178 | 160.9951 | 24.2725 | 186.2797 | 3.1817 | 18.6001 | 2.0519 | 0.082639 | -38.1653 | 3.1239 | 558.58 | 49.01 | -1.5167 | -0.17224 | 0.39035 | -0.70137 | 0.42841 | -0.4842 | 0.68576 | -1.1202 | -0.98945 | 1.8141 | -4.2879 | -2.7865 | -2.1395 | -0.68204
42810.4478 | 673 | 18.4956 | 18.5358 | 18.5112 | 18.5201 | 17.8023 | 16.3849 | 14.4311 | 16.5921 | 17.1031 | 17.1973 | 17.2071 | 16.7192 | 15.7448 | 14.3645 | 14.8477 | 14.9246 | 15.7151 | 13.3204 | 14.0013 | 19.6271 |  |  |  | 16.6095 | 16.9162 | 27.6945 | 219.32 | 193.4085 | 273.6418 | 17.1866 | 16.8503 | 23.4177 | 16.8113 | 16.8642 | 25.0206 | 102.4156 | 313.8738 |  | 143.7325 | 199.0058 | 196.443 | 224.1953 |  | 7.8683 | 9.7317 | 7.8245 | 9.8891 | 10.981 | 19.9687 | 161.7358 | 4.5922 | 8.3286 | 4.8828 | 10.7323 | 9.2257 | 42.2021 | 46.7689 | 42.6248 | 14.448 |  |  | -0.90528 | -0.038681 | 0.033392 | -0.077538 | 0.18678 | 0.06788 | 0.4382 | 0.88694 | -0.19964 | -0.86161 | 1.0751 | 0.96358 | 0.96367 | 0.77994 | 16.1263 | 16.6167 | 17.1346 | 17.4633 | 17.4052 | 16.3369 | 14.6795 | 16.7479 | 17.0806 | 17.3802 | 17.4168 | 17.1169 | 16.273 | 14.4528 | 91.0186 | 36.3687 | 53.2946 | 35.6524 | 30.6389 | 46.446 | 25.909 | 15.8183 | 15.6161 | 15.845 | 14.3903 | 16.3335 | 20.5993 |  |  |  | 79.23 | 198.6528 | 178.7378 | 136.6487 | 2.3936 | 0.86876 | 71.3783 |  |  | 12.255 |  |  | 16.9589 | 17.7741 | 33.3171 | 16.364 | 16.4349 | 23.0284 | 220.4248 | 324.5599 | 171.1292 | 176.2259 | 157.9258 |  | 83.183 | 145.8422 | 79.6182 | 157.4943 | 152.2796 | 214.0626 |  | 123.1263 |  |  | 21.5332 | 27.2967 | 86.9256 | [6 empty] | 129.8071 |  |  | 71.3528 |  |  | 28.7215 | 123.4221 | 360.4187 | 13.1055 | 108.6657 | 209.995 | 16.4914 | 104.0433 | 253.4038 | 44.9683 | 182.0851 | 17.6569 | 164.3235 | 20.7432 | 173.561 | 14.7675 | 104.0526 | 193.7533 | 50.8234 | 111.1765 | 229.2738 | 17.7829 | 92.9127 | 236.1951 | 20.1364 | 159.7075 | 44.042 | 161.8129 | 24.6045 | 188.9824 | 3.1284 | 18.596 | 2.054 | 0.08274 | -38.1591 | 3.1239 | 562.7 | 49.98 | -1.5505 | -0.23053 | 0.21419 | -0.32638 | 0.51565 | 0.31086 | 0.78981 | -1.1621 | -0.96146 | 1.7125 | -4.361 | -2.5893 | -2.2547 | -0.72073
42810.4478 | 674 | 18.4931 | 18.5265 | 18.5097 | 18.5109 | 17.7968 | 16.3725 | 14.4277 | 16.5949 | 17.0999 | 17.1945 | 17.2013 | 16.7181 | 15.7374 | 14.3628 | 14.8526 | 14.9288 | 15.7155 | 13.3147 | 14.011 | 19.652 |  |  |  | 16.6093 | 16.9162 | 27.7465 | 221.8619 | 195.1469 | 277.4015 | 17.1885 | 16.8581 | 23.4574 | 16.8136 | 16.8688 | 25.0546 | 103.2532 | 338.3523 |  | 145.1584 | 200.8886 | 198.6911 | 230.4449 |  | 7.8956 | 9.7911 | 7.897 | 9.9873 | 11.0954 | 20.0694 | 163.5589 | 4.6029 | 8.3472 | 4.8553 | 10.7771 | 9.2379 | 42.206 | 46.804 | 42.6352 | 14.442 |  |  | -0.76729 | 0.099971 | -0.058604 | -0.036142 | 0.31952 | -0.45453 | 0.4244 | 1.2004 | -0.32458 | 0.35733 | 1.6189 | 0.7041 | 0.70419 | 0.77301 | 16.1332 | 16.6126 | 17.1466 | 17.4678 | 17.4134 | 16.349 | 14.6831 | 16.754 | 17.0843 | 17.3829 | 17.4248 | 17.1193 | 16.2732 | 14.4593 | 95.2528 | 37.2136 | 52.5247 | 34.3775 | 30.9485 | 46.9633 | 26.034 | 15.8191 | 15.6113 | 15.8415 | 14.3798 | 16.3492 | 20.6361 |  |  |  | 79.841 | 200.6579 | 180.095 | 139.2178 | 2.4462 | 1.9383 | 71.9553 |  |  | 12.2764 |  |  | 16.9645 | 17.786 | 33.3846 | 16.3689 | 16.4448 | 23.0682 | 223.695 | 342.2037 | 172.7601 | 178.0839 | 160.7852 |  | 83.7673 | 145.7653 | 79.9635 | 163.2115 | 153.4265 | 222.3474 |  | 123.809 |  |  | 21.8268 | 27.6544 | 87.5957 | [6 empty] | 134.3075 |  |  | 73.2369 |  |  | 29.0948 | 125.4857 | 365.4459 | 13.1418 | 109.6764 | 214.8108 | 16.6987 | 104.9314 | 261.9162 | 46.2234 | 185.6414 | 17.826 | 165.4058 | 21.0776 | 175.0881 | 14.817 | 105.0178 | 196.3376 | 51.491 | 112.2748 | 233.6391 | 17.9995 | 94.1069 | 240.0799 | 20.3347 | 160.7752 | 44.8325 | 162.6769 | 24.938 | 191.8967 | 3.4618 | 18.5927 | 2.056 | 0.082929 | -38.1214 | 3.1239 | 583.09 | 49.14 | -1.4323 | 0.37064 | -0.28378 | -0.22285 | 0.67455 | -0.80453 | 0.77741 | -1.2192 | -0.94629 | 1.6057 | -4.7701 | -2.4891 | -2.395 | -0.76904
42810.4478 | 675 | 18.5062 | 18.5385 | 18.5162 | 18.5168 | 17.8027 | 16.3863 | 14.4327 | 16.6058 | 17.1066 | 17.2063 | 17.2116 | 16.727 | 15.7445 | 14.3752 | 14.8519 | 14.9307 | 15.7155 | 13.3157 | 13.9945 | 19.6727 |  |  |  | 16.603 | 16.9245 | 27.8014 | 224.2763 | 197.7796 | 279.1541 | 17.1918 | 16.8631 | 23.4939 | 16.8216 | 16.8779 | 25.097 | 104.1422 | 357.1129 |  | 146.7847 | 202.6795 | 201.3845 | 235.9856 |  | 7.9398 | 9.882 | 7.9636 | 10.1472 | 11.2512 | 20.1782 | 166.1784 | 4.6874 | 8.3693 | 4.858 | 10.8407 | 9.2415 | 42.2062 | 46.8339 | 42.6453 | 14.4371 |  |  | -0.53796 | -0.065625 | -0.03232 | -0.12354 | 0.38655 | -0.060256 | 0.47631 | 0.95528 | -0.18369 | 0.040948 | 1.6418 | 0.51809 | 0.51821 | 0.76197 | 16.1413 | 16.6151 | 17.149 | 17.4644 | 17.4105 | 16.3521 | 14.6801 | 16.7457 | 17.0887 | 17.3815 | 17.4223 | 17.1201 | 16.274 | 14.4588 | 98.3287 | 38.3299 | 56.4248 | 36.6781 | 31.2175 | 47.4673 | 26.246 | 15.8247 | 15.6168 | 15.8563 | 14.3813 | 16.3723 | 20.6742 |  |  |  | 80.4252 | 202.882 | 182.6503 | 141.7517 | 2.7279 | 1.2557 | 72.6481 |  |  | 12.2995 |  |  | 16.9607 | 17.7958 | 33.4495 | 16.3733 | 16.4521 | 23.1062 | 228.5097 | 362.6151 | 174.603 | 180.0672 | 164.3757 |  | 84.3547 | 145.5609 | 80.3845 | 169.6926 | 154.696 | 239.9761 |  | 124.6374 |  |  | 22.1324 | 28.1815 | 89.0217 | [6 empty] | 139.1662 |  |  | 75.0657 |  |  | 29.5351 | 127.9183 | 369.8554 | 13.2006 | 110.5431 | 219.4853 | 16.9233 | 106.1093 | 272.4307 | 47.5982 | 188.8033 | 18.0192 | 166.7173 | 21.4565 | 176.0758 | 14.8985 | 106.173 | 199.2376 | 52.2545 | 113.3803 | 238.6242 | 18.2477 | 95.6898 | 244.9281 | 20.538 | 162.2436 | 45.6698 | 163.4321 | 25.3036 | 194.6184 | 3.7788 | 18.5881 | 2.0586 | 0.08185 | -38.2869 | 3.1239 | 592.65 | 49.3 | -1.2012 | -0.30034 | -0.21078 | -0.41208 | 0.74207 | -0.29298 | 0.82374 | -1.2966 | -0.92471 | 1.4833 | -5.0521 | -2.8976 | -2.5134 | -0.81736
42810.4479 | 676 | 18.5021 | 18.5488 | 18.5186 | 18.5177 | 17.8026 | 16.3861 | 14.4387 | 16.5983 | 17.1072 | 17.1955 | 17.2204 | 16.7286 | 15.7509 | 14.3735 | 14.8538 | 14.9346 | 15.7343 | 13.3209 | 13.9897 | 19.7154 |  |  |  | 16.6117 | 16.9353 | 27.8681 | 226.5414 | 201.0173 | 283.3778 | 17.2001 | 16.871 | 23.5344 | 16.8262 | 16.8874 | 25.1648 | 105.105 | 371.8132 |  | 148.4553 | 205.0911 | 204.1491 | 239.4002 |  | 7.97 | 9.9619 | 8.0242 | 10.2776 | 11.4127 | 20.3114 | 168.1117 | 4.7485 | 8.3938 | 4.9078 | 10.8976 | 9.2424 | 42.2164 | 46.8656 | 42.6688 | 14.4401 |  |  | -1.3311 | 0.017175 | 0.062964 | -0.02037 | 0.20847 | -0.15554 | 0.38497 | 1.1537 | 0.01247 | 0.25243 | 1.9245 | 0.38399 | 0.38405 | 0.73519 | 16.1496 | 16.6227 | 17.1459 | 17.4704 | 17.4118 | 16.3579 | 14.6772 | 16.7511 | 17.0893 | 17.3845 | 17.4244 | 17.1294 | 16.2804 | 14.463 | 100.2864 | 37.3737 | 57.0589 | 39.813 | 33.9668 | 47.9661 | 26.4363 | 15.8197 | 15.6149 | 15.8597 | 14.3886 | 16.3836 | 20.7057 |  |  |  | 81.0081 | 205.9285 | 186.5639 | 143.8257 | 2.1432 | 0.82528 | 73.0288 |  |  | 12.3291 |  |  | 16.9631 | 17.7985 | 33.5295 | 16.3685 | 16.4531 | 23.1388 | 231.7123 | 386.5548 | 176.7678 | 182.3503 | 168.9762 |  | 84.9785 | 145.65 | 80.7356 | 177.2564 | 155.9827 | 247.2628 |  | 125.4215 |  |  | 22.5708 | 28.7804 | 90.5693 | [6 empty] | 144.8805 |  |  | 76.8101 |  |  | 30.0432 | 130.5543 | 375.5706 | 13.2944 | 111.5055 | 224.6573 | 17.1933 | 107.3498 | 282.6683 | 49.0357 | 192.9909 | 18.2478 | 168.677 | 21.8806 | 179.3845 | 15.0223 | 107.6823 | 203.2698 | 53.0635 | 114.7163 | 243.972 | 18.5421 | 96.9217 | 249.299 | 20.8162 | 163.9195 | 46.5245 | 164.7322 | 25.7088 | 196.8059 | 5.0116 | 18.5867 | 2.0615 | 0.082465 | -38.2452 | 3.1239 | 603.11 | 49.86 | -1.8968 | 0.15367 | 0.29423 | -0.16736 | 0.54508 | -0.47083 | 0.74073 | -1.4006 | -0.91391 | 1.3319 | -5.2105 | -2.9458 | -2.5697 | -0.85292
42810.4479 | 677 | 18.5032 | 18.5341 | 18.5213 | 18.5181 | 17.8031 | 16.3797 | 14.435 | 16.6023 | 17.1041 | 17.2058 | 17.2094 | 16.7202 | 15.7456 | 14.3807 | 14.8586 | 14.9263 | 15.7364 | 13.3237 | 14.0321 | 19.7392 |  |  |  | 16.6157 | 16.9457 | 27.9205 | 229.7479 | 203.6881 | 294.945 | 17.185 | 16.8582 | 23.5563 | 16.8159 | 16.8873 | 25.1966 | 106.2447 | 392.901 |  | 150.5033 | 208.0216 | 207.8451 | 246.7265 |  | 7.9981 | 10.0665 | 8.0964 | 10.4148 | 11.5894 | 20.4595 | 170.3904 | 4.7815 | 8.4241 | 4.9655 | 10.9475 | 9.2435 | 42.2305 | 46.8928 | 42.6825 | 14.4311 |  |  | -0.57213 | 0.058571 | -0.052692 | -0.17217 | 0.35172 | 0.028452 | 0.54531 | 1.3266 | -0.1759 | -0.60943 | 1.9764 | 0.28717 | 0.28715 | 0.70759 | 16.1405 | 16.6139 | 17.1454 | 17.472 | 17.4056 | 16.3514 | 14.6736 | 16.7496 | 17.086 | 17.3887 | 17.4232 | 17.1239 | 16.277 | 14.463 | 99.5911 | 36.9382 | 55.4592 | 40.1802 | 35.7152 | 48.3537 | 26.5892 | 15.82 | 15.6183 | 15.861 | 14.395 | 16.3931 | 20.7456 |  |  |  | 81.6473 | 208.8449 | 188.9222 | 146.0512 | 2.2526 | 1.9315 | 73.3912 |  |  | 12.3481 |  |  | 16.9639 | 17.8077 | 33.6172 | 16.3669 | 16.4551 | 23.1651 | 234.5767 | 410.5155 | 179.1791 | 184.6815 | 174.6582 |  | 85.6334 | 148.4459 | 81.1438 | 183.3731 | 157.3571 | 253.4371 |  | 126.3299 |  |  | 23.0124 | 29.5243 | 92.4696 | [6 empty] | 149.9669 |  |  | 78.7014 |  |  | 30.5633 | 133.6468 | 385.3694 | 13.4635 | 112.3916 | 230.9539 | 17.504 | 108.7207 | 293.1308 | 50.5795 | 196.9538 | 18.5018 | 170.5913 | 22.4074 | 182.1955 | 15.1625 | 108.9955 | 207.5195 | 53.8807 | 116.2884 | 249.2459 | 18.894 | 98.3835 | 254.2251 | 21.0683 | 165.3595 | 47.5189 | 165.9145 | 26.1588 | 199.3996 | 4.8235 | 18.5833 | 2.0637 | 0.082834 | -38.2178 | 3.124 | 626.48 | 49.08 | -1.2564 | 0.28384 | -0.26921 | -0.48663 | 0.70819 | 0.20142 | 0.88181 | -1.5334 | -0.97612 | 1.225 | -5.0872 | -2.7501 | -2.7275 | -0.89053
42810.4479 | 678 | 18.5143 | 18.5455 | 18.5218 | 18.5245 | 17.8071 | 16.399 | 14.437 | 16.601 | 17.1094 | 17.2063 | 17.2266 | 16.7346 | 15.7546 | 14.3724 | 14.8513 | 14.9256 | 15.7302 | 13.3096 | 14.0718 | 19.7598 |  |  |  | 16.6077 | 16.9382 | 27.965 | 233.1152 | 206.0949 | 296.6322 | 17.1976 | 16.8714 | 23.5845 | 16.82 | 16.8969 | 25.2411 | 107.2596 | 418.249 |  | 152.8222 | 211.5715 | 211.4804 | 250.5135 |  | 8.0265 | 10.1839 | 8.1806 | 10.573 | 11.7871 | 20.5657 | 173.2185 | 4.8424 | 8.4497 | 4.9963 | 11.0162 | 9.2448 | 42.246 | 46.9016 | 42.689 | 14.4216 |  |  | -0.2692 | 0.14991 | 0.034708 | -0.12682 | 0.34778 | 0.43455 | 0.51771 | 1.4383 | 0.017724 | 0.62 | 2.2498 | 0.21679 | 0.21691 | 0.71595 | 16.1415 | 16.6149 | 17.1488 | 17.4744 | 17.4075 | 16.3481 | 14.6767 | 16.7438 | 17.0879 | 17.3893 | 17.421 | 17.1242 | 16.2711 | 14.4633 | 99.1825 | 36.8561 | 58.8173 | 40.185 | 34.8185 | 48.8422 | 26.8073 | 15.8175 | 15.6259 | 15.8542 | 14.3886 | 16.4113 | 20.782 |  |  |  | 82.3206 | 213.2807 | 191.1078 | 149.1482 | 2.7139 | 2.2868 | 73.8659 |  |  | 12.3753 |  |  | 16.9669 | 17.8228 | 33.7052 | 16.3611 | 16.4644 | 23.1975 | 238.6536 | 436.5813 | 182.1103 | 187.5928 | 179.8819 |  | 86.461 | 151.5639 | 81.5715 | 190.5843 | 159.0321 | 259.8657 |  | 127.3217 |  |  | 23.6759 | 30.4291 | 95.1272 | [6 empty] | 155.7859 |  |  | 80.7205 |  |  | 31.1831 | 137.0355 | 394.5437 | 13.6093 | 113.94 | 237.228 | 17.8381 | 110.224 | 306.0641 | 52.3168 | 200.8625 | 18.7533 | 172.8728 | 22.9966 | 184.0369 | 15.3357 | 110.207 | 212.1001 | 54.7882 | 118.0156 | 255.2284 | 19.2767 | 100.157 | 261.1643 | 21.3166 | 167.2388 | 48.6309 | 167.2962 | 26.675 | 203.6278 | 5.0191 | 18.5832 | 2.0652 | 0.084687 | -38.2858 | 3.1239 | 627.95 | 48.81 | -0.86309 | 0.45419 | 0.21854 | -0.41775 | 0.70434 | 0.78732 | 0.85936 | -1.6468 | -1.0465 | 1.1017 | -4.9839 | -3.0977 | -2.7919 | -0.95101
42810.4479 | 679 | 18.5144 | 18.5384 | 18.5161 | 18.5202 | 17.805 | 16.3918 | 14.4295 | 16.5928 | 17.1061 | 17.207 | 17.2149 | 16.7283 | 15.7525 | 14.3746 | 14.8578 | 14.9321 | 15.7328 | 13.3198 | 14.0383 | 19.795 |  |  |  | 16.61 | 16.9479 | 28.02 | 235.5207 | 209.4627 | 300.413 | 17.1964 | 16.8772 | 23.6441 | 16.8173 | 16.8931 | 25.2863 | 108.3893 | 443.7164 |  | 155.3977 | 215.5607 | 215.4486 | 256.5576 |  | 8.0628 | 10.298 | 8.2685 | 10.7357 | 11.9823 | 20.6131 | 175.7997 | 4.9025 | 8.4735 | 5.0078 | 11.0776 | 9.2577 | 42.2615 | 46.9078 | 42.6978 | 14.4215 |  |  | -0.9434 | -0.17142 | -0.05926 | -0.018398 | 0.20847 | 0.3971 | 0.75098 | 1.3811 | -0.75095 | 0.22956 | 2.1772 | 0.16563 | 0.16564 | 0.70865 | 16.1501 | 16.617 | 17.1485 | 17.4638 | 17.4133 | 16.3458 | 14.6761 | 16.7463 | 17.0847 | 17.3887 | 17.4214 | 17.1241 | 16.2792 | 14.4557 | 104.3187 | 40.3903 | 63.2124 | 41.1366 | 35.5857 | 49.4271 | 27.0718 | 15.8193 | 15.6221 | 15.8676 | 14.3946 | 16.4222 | 20.8155 |  |  |  | 83.1741 | 218.5595 | 193.5888 | 153.5492 | 2.752 | 2.4895 | 74.2543 |  |  | 12.4152 |  |  | 16.9651 | 17.8262 | 33.7979 | 16.3624 | 16.4686 | 23.2269 | 245.0932 | 466.0713 | 185.3448 | 190.8378 | 183.3915 |  | 87.3187 | 152.7118 | 81.949 | 196.4366 | 160.551 | 267.5942 |  | 128.2469 |  |  | 24.3524 | 31.4173 | 97.1105 | [6 empty] | 161.184 |  |  | 82.8488 |  |  | 31.8063 | 140.2569 | 403.5735 | 13.7792 | 115.4171 | 243.0305 | 18.24 | 112.0611 | 317.3653 | 54.0409 | 204.6316 | 19.0399 | 175.1177 | 23.6815 | 186.0619 | 15.5176 | 111.7199 | 217.074 | 55.6859 | 119.7986 | 260.7119 | 19.6936 | 101.8284 | 266.5239 | 21.597 | 169.09 | 49.5262 | 168.6591 | 27.2379 | 206.5643 | 5.4092 | 18.5811 | 2.0675 | 0.08392 | -38.1969 | 3.124 | 624.66 | 50.63 | -1.6211 | -0.48578 | -0.28562 | -0.15914 | 0.54536 | 0.75269 | 1.0351 | -1.7114 | -1.0641 | 1.0092 | -5.4851 | -3.555 | -2.9142 | -1.0408
42810.4479 | 680 | 18.5121 | 18.5415 | 18.5223 | 18.5208 | 17.806 | 16.3859 | 14.4312 | 16.6002 | 17.1069 | 17.2032 | 17.2155 | 16.7281 | 15.7527 | 14.3745 | 14.8657 | 14.937 | 15.7493 | 13.3245 | 14.0384 | 19.8299 |  |  |  | 16.6141 | 16.9659 | 28.0855 | 238.6024 | 213.0358 | 313.673 | 17.2034 | 16.882 | 23.6709 | 16.8168 | 16.8977 | 25.3376 | 109.5604 | 462.5445 |  | 158.0232 | 219.6172 | 219.2632 | 263.4572 |  | 8.1334 | 10.4774 | 8.4058 | 10.9622 | 12.2673 | 20.7648 | 179.5676 | 4.8756 | 8.5201 | 5.0938 | 11.167 | 9.2644 | 42.2564 | 46.9118 | 42.7031 | 14.421 |  |  | -0.85337 | -0.064965 | 0.046536 | -0.25167 | 0.3826 | 0.6928 | 0.34226 | 1.5533 | -0.081717 | 0.46097 | 2.6883 | 0.12801 | 0.12804 | 0.68783 | 16.1501 | 16.6066 | 17.1415 | 17.4543 | 17.4005 | 16.3334 | 14.6738 | 16.7466 | 17.0777 | 17.3799 | 17.4136 | 17.1136 | 16.2737 | 14.4607 | 106.8576 | 41.8968 | 68.5347 | 44.6942 | 39.4186 | 50.0257 | 27.3831 | 15.8273 | 15.6266 | 15.873 | 14.3962 | 16.436 | 20.8419 |  |  |  | 83.9584 | 221.7729 | 195.7538 | 157.9704 | 2.8113 | 2.9905 | 74.8881 |  |  | 12.4578 |  |  | 16.9612 | 17.8319 | 33.8821 | 16.3668 | 16.4705 | 23.2616 | 253.1884 | 495.332 | 188.5223 | 194.2669 | 188.3104 |  | 88.2905 | 154.4769 | 82.4414 | 202.3292 | 162.1042 | 275.7495 |  | 129.1945 |  |  | 25.0889 | 32.681 | 99.91 | [6 empty] | 166.4626 |  |  | 84.7969 |  |  | 32.4766 | 143.6353 | 415.2214 | 13.9221 | 117.0588 | 250.739 | 18.7297 | 114.2762 | 330.8345 | 55.9081 | 209.2825 | 19.3538 | 177.8583 | 24.442 | 188.1383 | 15.7441 | 113.4567 | 223.1511 | 56.6802 | 121.7488 | 268.8073 | 20.1648 | 103.3313 | 271.1791 | 21.9223 | 170.9838 | 50.5512 | 170.14 | 27.8992 | 210.2885 | 6.4496 | 18.5794 | 2.0686 | 0.084152 | -38.2553 | 3.124 | 653.93 | 49.33 | -1.5595 | -0.29914 | 0.25318 | -0.58879 | 0.73901 | 0.99444 | 0.69897 | -1.8107 | -1.0944 | 0.91759 | -5.6962 | -4.1099 | -3.0585 | -1.1338
42810.4479 | 681 | 18.5104 | 18.5396 | 18.5194 | 18.5159 | 17.8061 | 16.3827 | 14.4314 | 16.6011 | 17.1079 | 17.2037 | 17.213 | 16.7274 | 15.7496 | 14.3757 | 14.8665 | 14.9468 | 15.755 | 13.3336 | 13.9839 | 19.8611 |  |  |  | 16.6212 | 16.9816 | 28.1518 | 242.8937 | 216.6652 | 321.3736 | 17.2131 | 16.8909 | 23.7315 | 16.8287 | 16.9141 | 25.3896 | 110.873 | 473.6228 |  | 160.6275 | 224.2073 | 223.1776 | 270.691 |  | 8.1907 | 10.635 | 8.5208 | 11.1823 | 12.5637 | 20.9432 | 182.7531 | 4.7776 | 8.5441 | 5.2331 | 11.2442 | 9.2697 | 42.2516 | 46.9004 | 42.7032 | 14.418 |  |  | -0.764 | 0.14005 | 0.020908 | -0.18136 | 0.11976 | 0.13754 | 0.44608 | 1.4764 | -0.24966 | -0.25151 | 2.7773 | 0.10028 | 0.10021 | 0.68788 | 16.1536 | 16.6224 | 17.1458 | 17.4689 | 17.4103 | 16.3439 | 14.6744 | 16.7505 | 17.0947 | 17.3845 | 17.4154 | 17.1181 | 16.271 | 14.4582 | 108.7155 | 45.5574 | 75.3768 | 48.4678 | 43.2915 | 50.6199 | 27.7526 | 15.8235 | 15.6226 | 15.8797 | 14.3995 | 16.4522 | 20.8822 |  |  |  | 84.7756 | 225.1493 | 198.3474 | 162.1152 | 3.565 | 3.0327 | 76.0098 |  |  | 12.5017 |  |  | 16.9635 | 17.8362 | 33.968 | 16.3646 | 16.4608 | 23.2863 | 259.8788 | 521.4611 | 191.7319 | 197.3643 | 194.3439 |  | 89.5206 | 158.6673 | 83.133 | 209.0375 | 163.9601 | 290.243 |  | 130.5406 |  |  | 25.8849 | 33.9752 | 103.105 | [6 empty] | 171.3855 |  |  | 86.8252 |  |  | 33.1807 | 147.3905 | 428.3551 | 14.1337 | 119.2562 | 259.5456 | 19.2453 | 116.4571 | 343.075 | 57.7436 | 214.4779 | 19.6825 | 181.0787 | 25.3188 | 190.6866 | 15.999 | 115.0836 | 228.3648 | 57.6197 | 123.7392 | 274.1356 | 20.6381 | 105.0313 | 277.6566 | 22.2858 | 173.3478 | 51.6328 | 171.6383 | 28.553 | 214.1458 | 7.2677 | 18.5773 | 2.0704 | 0.084021 | -38.2967 | 3.124 | 656.26 | 49.24 | -1.4853 | 0.43935 | 0.16975 | -0.49996 | 0.41359 | 0.44322 | 0.79821 | -1.9308 | -1.1846 | 0.81774 | -5.832 | -4.8268 | -3.2063 | -1.2177
42810.4479 | 682 | 18.5178 | 18.5347 | 18.5226 | 18.5209 | 17.8037 | 16.3877 | 14.4349 | 16.6026 | 17.1023 | 17.2002 | 17.2137 | 16.7309 | 15.7515 | 14.3753 | 14.8654 | 14.948 | 15.7533 | 13.3273 | 13.9654 | 19.8866 |  |  |  | 16.6099 | 16.9717 | 28.1992 | 247.2878 | 221.1827 | 333.3518 | 17.2036 | 16.8865 | 23.7721 | 16.834 | 16.9193 | 25.4256 | 112.219 | 477.5935 |  | 163.3372 | 229.1732 | 227.4821 | 277.857 |  | 8.2534 | 10.8308 | 8.6526 | 11.4245 | 12.93 | 21.2632 | 185.6372 | 4.8149 | 8.5792 | 5.2617 | 11.3267 | 9.28 | 42.2523 | 46.8886 | 42.7123 | 14.4168 |  |  | -0.83694 | 0.026371 | 0.067564 | -0.31016 | 0.13619 | -0.24622 | 0.47894 | 1.5559 | -0.41507 | 1.7196 | 2.8318 | 0.079675 | 0.079715 | 0.67856 | 16.1572 | 16.6222 | 17.1449 | 17.4659 | 17.4077 | 16.3474 | 14.672 | 16.7467 | 17.0832 | 17.3817 | 17.4161 | 17.1175 | 16.2691 | 14.4563 | 113.4859 | 50.4119 | 81.9996 | 50.5185 | 44.0755 | 51.3049 | 28.1378 | 15.8206 | 15.6272 | 15.8823 | 14.4047 | 16.4645 | 20.9173 |  |  |  | 85.6287 | 231.5164 | 201.8772 | 165.9759 | 3.6471 | 3.2399 | 77.7126 |  |  | 12.5648 |  |  | 16.9707 | 17.8554 | 34.0666 | 16.3759 | 16.4774 | 23.3297 | 267.9611 | 546.8623 | 194.9449 | 200.5209 | 201.1443 |  | 90.7189 | 160.7858 | 83.8005 | 215.7151 | 165.7638 | 298.2656 |  | 131.8113 |  |  | 26.8395 | 35.4878 | 106.8699 | [6 empty] | 176.434 |  |  | 88.7545 |  |  | 33.7991 | 151.1026 | 438.1213 | 14.3257 | 120.9158 | 265.5541 | 19.8152 | 118.8735 | 355.0975 | 59.5719 | 219.2966 | 20.0605 | 184.3308 | 26.2156 | 193.5722 | 16.3096 | 116.7096 | 233.7028 | 58.461 | 125.708 | 281.5723 | 21.1543 | 106.5662 | 283.8132 | 22.6491 | 176.0522 | 52.7772 | 173.2259 | 29.293 | 218.4448 | 6.7741 | 18.5758 | 2.0721 | 0.084854 | -38.2543 | 3.124 | 674.41 | 50.09 | -1.5701 | 0.19071 | 0.30526 | -0.65404 | 0.44128 | -0.59334 | 0.82753 | -2.0734 | -1.218 | 0.71672 | -6.2807 | -5.5174 | -3.3505 | -1.2924
42810.4479 | 683 | 18.5132 | 18.5469 | 18.5249 | 18.5309 | 17.8051 | 16.3874 | 14.4379 | 16.607 | 17.1123 | 17.2118 | 17.2204 | 16.7378 | 15.7555 | 14.3727 | 14.8711 | 14.9411 | 15.7487 | 13.3234 | 13.9847 | 19.9098 |  |  |  | 16.6112 | 16.9761 | 28.2599 | 251.634 | 225.3943 | 341.0151 | 17.2019 | 16.8957 | 23.8072 | 16.815 | 16.9169 | 25.4588 | 113.642 | 483.2928 |  | 166.0144 | 234.595 | 232.0047 | 287.8069 |  | 8.321 | 11.0394 | 8.7822 | 11.6811 | 13.2662 | 21.6056 | 188.3841 | 4.9835 | 8.6077 | 5.3814 | 11.4206 | 9.2875 | 42.2647 | 46.8914 | 42.7114 | 14.4152 |  |  | -0.50379 | 0.015203 | 0.021564 | -0.10777 | -0.043864 | 0.39972 | 0.42111 | 1.8292 | -0.16053 | 0.37327 | 2.9567 | 0.064401 | 0.064471 | 0.59738 | 16.1725 | 16.6239 | 17.1474 | 17.4777 | 17.4114 | 16.3547 | 14.6841 | 16.7557 | 17.0907 | 17.3933 | 17.4228 | 17.1277 | 16.2852 | 14.4664 | 119.478 | 52.4737 | 90.3453 | 51.8657 | 46.0967 | 52.0824 | 28.5623 | 15.8316 | 15.6411 | 15.8927 | 14.4112 | 16.4911 | 20.957 |  |  |  | 86.5524 | 239.5308 | 205.8583 | 169.5788 | 3.1391 | 2.3804 | 79.0949 |  |  | 12.6249 |  |  | 16.97 | 17.8618 | 34.152 | 16.3711 | 16.4839 | 23.36 | 277.646 | 572.6009 | 198.0604 | 203.6855 | 204.7126 |  | 91.939 | 163.3698 | 84.4602 | 221.7778 | 167.5806 | 304.5165 |  | 133.0211 |  |  | 27.7721 | 36.921 | 110.0701 | [6 empty] | 181.3371 |  |  | 90.5917 |  |  | 34.4547 | 154.5449 | 447.0018 | 14.5067 | 123.1832 | 269.8101 | 20.3726 | 121.35 | 366.9292 | 61.3963 | 224.0726 | 20.4487 | 187.817 | 27.0702 | 196.7256 | 16.6835 | 118.1802 | 240.2642 | 59.3013 | 127.7898 | 288.0517 | 21.6798 | 108.4109 | 289.7762 | 23.0718 | 179.1446 | 53.8574 | 174.7364 | 30.0577 | 222.396 | 7.2156 | 18.5767 | 2.0747 | 0.085389 | -38.3309 | 3.124 | 702.13 | 48.59 | -1.2258 | 0.14486 | 0.17252 | -0.38567 | -0.25058 | 0.75645 | 0.77642 | -2.1253 | -1.2646 | 0.63384 | -6.854 | -6.3949 | -3.5688 | -1.3571
42810.448 | 684 | 18.5197 | 18.5471 | 18.5237 | 18.5237 | 17.8038 | 16.3839 | 14.4415 | 16.6088 | 17.1123 | 17.2121 | 17.2203 | 16.7315 | 15.7526 | 14.3886 | 14.8762 | 14.9494 | 15.7555 | 13.3258 | 14.0336 | 19.9431 |  |  |  | 16.6178 | 16.9849 | 28.325 | 256.1071 | 229.9197 | 352.8102 | 17.2026 | 16.8997 | 23.8414 | 16.8291 | 16.929 | 25.5123 | 115.355 | 493.1489 |  | 169.0622 | 240.1782 | 237.0317 | 297.6483 |  | 8.4009 | 11.2266 | 8.9088 | 11.9354 | 13.5627 | 21.9572 | 191.5708 | 5.1491 | 8.6413 | 5.4565 | 11.5161 | 9.2839 | 42.2531 | 46.9072 | 42.707 | 14.4066 |  |  | -0.46436 | 0.12691 | 0.028136 | -0.20108 | 0.20584 | 0.04094 | 0.15564 | 1.9778 | -0.093782 | 0.016611 | 3.1773 | 0.052842 | 0.052898 | 0.62556 | 16.1758 | 16.619 | 17.1406 | 17.4729 | 17.4137 | 16.3465 | 14.6783 | 16.7485 | 17.0921 | 17.3846 | 17.4207 | 17.1262 | 16.2808 | 14.4579 | 120.9002 | 51.7081 | 94.7618 | 52.3126 | 46.0065 | 52.7784 | 28.9889 | 15.8359 | 15.6403 | 15.8922 | 14.4101 | 16.5122 | 20.9994 |  |  |  | 87.5575 | 248.7457 | 210.9142 | 173.7679 | 3.519 | 2.5757 | 80.3244 |  |  | 12.6815 |  |  | 16.965 | 17.8766 | 34.246 | 16.3697 | 16.488 | 23.3817 | 285.7445 | 595.214 | 200.8813 | 206.8036 | 210.6873 |  | 93.3096 | 168.1875 | 85.2073 | 229.0102 | 169.5679 | 311.8026 |  | 134.3427 |  |  | 28.6437 | 38.3615 | 113.5656 | [6 empty] | 186.4326 |  |  | 92.5393 |  |  | 35.2056 | 158.1827 | 455.4751 | 14.7008 | 125.8966 | 275.0466 | 20.9573 | 123.7698 | 378.45 | 63.3594 | 229.0204 | 20.872 | 191.3389 | 28.0163 | 201.3404 | 17.0237 | 119.848 | 247.033 | 60.1662 | 129.895 | 294.5476 | 22.23 | 110.4761 | 295.8203 | 23.5412 | 182.4397 | 55.0437 | 176.6788 | 30.8059 | 226.3927 | 8.2546 | 18.5735 | 2.0771 | 0.08434 | -38.2653 | 3.1241 | 732.69 | 49.38 | -1.1881 | 0.41866 | 0.19713 | -0.52698 | 0.54315 | 0.24223 | 0.47229 | -2.2379 | -1.3699 | 0.52699 | -6.9292 | -6.8356 | -3.772 | -1.4349
42810.448 | 685 | 18.5186 | 18.5497 | 18.5229 | 18.53 | 17.8115 | 16.3896 | 14.4345 | 16.5991 | 17.1099 | 17.211 | 17.2204 | 16.7284 | 15.7576 | 14.3811 | 14.871 | 14.9524 | 15.7602 | 13.327 | 14.0607 | 19.9737 |  |  |  | 16.6132 | 16.9918 | 28.3803 | 261.0311 | 234.978 | 363.5124 | 17.2142 | 16.9027 | 23.8958 | 16.8254 | 16.9321 | 25.5687 | 116.9378 | 497.2522 |  | 171.8984 | 245.7211 | 241.4419 | 304.8693 |  | 8.4875 | 11.4219 | 9.0579 | 12.2247 | 13.9306 | 22.4339 | 195.1148 | 5.199 | 8.686 | 5.5211 | 11.6136 | 9.2907 | 42.2488 | 46.9169 | 42.7117 | 14.4086 |  |  | -0.26197 | -0.087309 | 0.014336 | -0.18071 | 0.65991 | 0.33598 | 0.12344 | 2.2754 | -0.83676 | 0.44167 | 3.2147 | 0.044012 | 0.043915 | 0.66322 | 16.1718 | 16.6188 | 17.1427 | 17.4646 | 17.4088 | 16.344 | 14.6772 | 16.7446 | 17.0919 | 17.3813 | 17.4192 | 17.1243 | 16.2768 | 14.4607 | 123.2411 | 53.3449 | 95.2943 | 51.3775 | 45.8513 | 53.5477 | 29.393 | 15.8284 | 15.6422 | 15.8912 | 14.4111 | 16.5282 | 21.032 |  |  |  | 88.5113 | 255.2285 | 215.0876 | 177.426 | 3.7753 | 3.5066 | 81.4122 |  |  | 12.7438 |  |  | 16.9643 | 17.885 | 34.3356 | 16.3672 | 16.4862 | 23.4155 | 295.6514 | 614.1384 | 203.7952 | 210.1067 | 217.7415 |  | 94.8355 | 173.6102 | 86.0812 | 236.8593 | 171.7771 | 320.861 |  | 135.7928 |  |  | 29.4743 | 39.9232 | 117.6229 | [6 empty] | 191.936 |  |  | 94.1862 |  |  | 36.0217 | 161.8055 | 461.9757 | 14.9718 | 128.3417 | 280.9849 | 21.5698 | 126.1678 | 388.21 | 65.3951 | 235.2993 | 21.2816 | 195.1401 | 29.0216 | 205.8885 | 17.3644 | 121.9777 | 253.0583 | 61.0501 | 131.9195 | 301.5832 | 22.7917 | 112.405 | 301.8055 | 24.0204 | 185.8384 | 56.3034 | 178.9405 | 31.5993 | 230.3414 | 7.2327 | 18.5709 | 2.0794 | 0.082791 | -38.1618 | 3.124 | 763.16 | 49.92 | -0.90001 | -0.34737 | 0.14076 | -0.49975 | 0.97331 | 0.69449 | 0.42095 | -2.3744 | -1.4871 | 0.41413 | -7.0978 | -6.8473 | -3.9074 | -1.4998
42810.448 | 686 | 18.5203 | 18.5524 | 18.5293 | 18.5323 | 17.8116 | 16.3862 | 14.4295 | 16.6042 | 17.1096 | 17.2101 | 17.2208 | 16.7328 | 15.7591 | 14.3861 | 14.8722 | 14.9553 | 15.7625 | 13.3287 | 14.0267 | 20.0027 |  |  |  | 16.6192 | 17.0006 | 28.4313 | 265.4366 | 240.1105 | 366.9415 | 17.2166 | 16.9127 | 23.9408 | 16.8294 | 16.9393 | 25.6156 | 118.5705 | 499.6952 |  | 174.6569 | 250.9934 | 245.6548 | 308.7483 |  | 8.5501 | 11.599 | 9.1936 | 12.4552 | 14.2146 | 22.9704 | 198.2484 | 5.1438 | 8.7085 | 5.5923 | 11.6967 | 9.2976 | 42.263 | 46.9275 | 42.7252 | 14.4026 |  |  | -0.87966 | 0.004687 | -0.029032 | -0.2773 | 0.24264 | 0.35241 | 0.48617 | 1.6242 | 1.0376 | 1.0581 | 3.4589 | 0.037185 | 0.037221 | 0.73279 | 16.1818 | 16.6254 | 17.1539 | 17.4666 | 17.4125 | 16.3484 | 14.684 | 16.7463 | 17.0934 | 17.3908 | 17.425 | 17.1256 | 16.2803 | 14.4599 | 126.7053 | 54.0258 | 95.4966 | 52.7093 | 46.4957 | 54.3217 | 29.8244 | 15.8237 | 15.633 | 15.8909 | 14.409 | 16.5345 | 21.066 |  |  |  | 89.505 | 260.9602 | 219.0861 | 180.5995 | 3.4295 | 2.0717 | 82.5448 |  |  | 12.807 |  |  | 16.9692 | 17.8885 | 34.428 | 16.3712 | 16.4952 | 23.4462 | 303.315 | 630.1044 | 207.0351 | 213.6346 | 222.2624 |  | 96.2639 | 177.8117 | 86.9082 | 243.1357 | 173.8284 | 324.0376 |  | 137.1201 |  |  | 30.3788 | 41.5012 | 121.8094 | [6 empty] | 196.9887 |  |  | 95.8413 |  |  | 36.81 | 165.3151 | 465.9401 | 15.3221 | 130.513 | 286.6098 | 22.186 | 128.7158 | 398.2154 | 67.3865 | 242.3276 | 21.7108 | 198.8865 | 30.0397 | 209.1128 | 17.6722 | 124.5834 | 259.2322 | 61.9251 | 133.9593 | 309.6139 | 23.3372 | 114.3606 | 308.1885 | 24.5142 | 189.0427 | 57.4659 | 181.2602 | 32.3848 | 235.1349 | 7.9657 | 18.5679 | 2.0823 | 0.081018 | -38.2579 | 3.124 | 780.34 | 48.85 | -1.6537 | 0.080509 | -0.20037 | -0.61926 | 0.59072 | 0.71191 | 0.83617 | -2.444 | -1.5721 | 0.33803 | -7.3906 | -6.8191 | -3.9477 | -1.5497
42810.448 | 687 | 18.5184 | 18.5531 | 18.5185 | 18.5251 | 17.8111 | 16.3876 | 14.4321 | 16.5996 | 17.1134 | 17.2123 | 17.2184 | 16.7333 | 15.7513 | 14.3825 | 14.8707 | 14.9464 | 15.7637 | 13.3272 | 13.9786 | 20.0358 |  |  |  | 16.6151 | 17.0012 | 28.488 | 269.5233 | 244.6814 | 373.5527 | 17.2083 | 16.9107 | 23.9817 | 16.8292 | 16.9363 | 25.6481 | 120.239 | 500.8169 |  | 177.2039 | 256.2867 | 250.6619 | 312.8346 |  | 8.6405 | 11.8334 | 9.3515 | 12.7269 | 14.5444 | 24.0813 | 201.0196 | 5.0678 | 8.7531 | 5.5072 | 11.8032 | 9.315 | 42.2879 | 46.9393 | 42.7525 | 14.4129 |  |  | -0.59316 | 0.031631 | 0.003164 | -0.33776 | 0.15262 | -0.24096 | 0.55122 | 1.797 | 0.037573 | 1.5515 | 3.93 | 0.032025 | 0.032062 | 0.76633 | 16.1663 | 16.6119 | 17.1351 | 17.4618 | 17.3994 | 16.3489 | 14.674 | 16.7466 | 17.0843 | 17.3816 | 17.422 | 17.1188 | 16.265 | 14.4455 | 125.7148 | 50.1799 | 89.8065 | 52.394 | 46.4338 | 54.9744 | 30.154 | 15.818 | 15.6329 | 15.8925 | 14.4115 | 16.5463 | 21.0965 |  |  |  | 90.5462 | 267.5796 | 223.1543 | 182.8382 | 3.2919 | 2.0604 | 84.393 |  |  | 12.8774 |  |  | 16.9729 | 17.907 | 34.5184 | 16.377 | 16.5063 | 23.4833 | 310.7749 | 645.3025 | 210.2417 | 217.2194 | 227.7673 |  | 97.7148 | 181.8854 | 87.7177 | 248.6696 | 175.9443 | 325.848 |  | 138.435 |  |  | 31.357 | 43.0619 | 125.8297 | [6 empty] | 201.6331 |  |  | 97.553 |  |  | 37.5685 | 168.8885 | 471.0588 | 15.6563 | 132.7777 | 291.632 | 22.8094 | 131.757 | 408.3964 | 69.3573 | 246.5697 | 22.1239 | 202.3747 | 31.0943 | 212.8316 | 17.9744 | 126.949 | 265.063 | 62.8515 | 136.1253 | 315.5277 | 23.87 | 116.3763 | 314.4567 | 25.0598 | 192.2967 | 58.5762 | 183.5178 | 33.2334 | 240.3392 | 8.2115 | 18.5656 | 2.0878 | 0.084181 | -38.1866 | 3.124 | 787.29 | 50.25 | -1.3649 | 0.20923 | 0.066175 | -0.68372 | 0.46937 | -0.58978 | 0.89202 | -2.5399 | -1.6542 | 0.28624 | -7.2028 | -6.1482 | -3.992 | -1.5716
42810.448 | 688 | 18.5134 | 18.545 | 18.5145 | 18.5131 | 17.806 | 16.3874 | 14.4304 | 16.5979 | 17.1114 | 17.2034 | 17.2157 | 16.7297 | 15.7438 | 14.376 | 14.8725 | 14.9546 | 15.766 | 13.3292 | 13.9937 | 20.0637 |  |  |  | 16.6225 | 17.0166 | 28.5437 | 273.8122 | 248.2697 | 379.5691 | 17.2123 | 16.9147 | 24.0194 | 16.8272 | 16.9404 | 25.696 | 121.9384 | 509.1147 |  | 179.9465 | 261.5005 | 256.1708 | 317.3943 |  | 8.7343 | 12.0826 | 9.5153 | 13.0296 | 14.8485 | 24.8324 | 203.971 | 4.9901 | 8.8008 | 5.4246 | 11.9213 | 9.3196 | 42.297 | 46.9383 | 42.7633 | 14.4126 |  |  | -0.58593 | 0.11443 | 0.019592 | -0.27205 | 0.25775 | 0.22953 | 0.30283 | 1.8128 | 0.12728 | 0.38082 | 3.7998 | 0.028014 | 0.028046 | 0.6581 | 16.185 | 16.6194 | 17.1443 | 17.4671 | 17.4089 | 16.3516 | 14.6784 | 16.7443 | 17.082 | 17.3816 | 17.412 | 17.1265 | 16.2712 | 14.4524 | 125.8663 | 48.5994 | 85.014 | 50.4172 | 44.586 | 55.7007 | 30.4468 | 15.8256 | 15.6416 | 15.9099 | 14.4107 | 16.5686 | 21.1366 |  |  |  | 91.7279 | 275.9345 | 228.4449 | 186.0175 | 3.4775 | 1.8261 | 86.0032 |  |  | 12.9535 |  |  | 16.975 | 17.9069 | 34.5995 | 16.3691 | 16.4962 | 23.505 | 318.4399 | 660.5197 | 213.0804 | 220.2733 | 235.8664 |  | 99.4532 | 185.6506 | 88.7616 | 257.3855 | 178.4606 | 333.0667 |  | 140.0934 |  |  | 32.3202 | 44.6698 | 129.3329 | [6 empty] | 206.0238 |  |  | 99.1938 |  |  | 38.3811 | 172.306 | 477.2936 | 15.9924 | 135.7174 | 296.2855 | 23.4668 | 134.7742 | 418.7005 | 71.3626 | 251.0338 | 22.5563 | 206.0535 | 32.1899 | 217.2952 | 18.3032 | 129.1383 | 269.9914 | 63.8541 | 138.621 | 320.6767 | 24.4518 | 118.7123 | 319.6337 | 25.6133 | 195.684 | 59.7544 | 186.431 | 34.0955 | 245.0259 | 9.1306 | 18.5641 | 2.0928 | 0.084347 | -38.324 | 3.1239 | 814.14 | 49.37 | -1.3629 | 0.39814 | 0.16474 | -0.61389 | 0.61075 | 0.57635 | 0.66201 | -2.6964 | -1.7186 | 0.16616 | -7.1331 | -5.5813 | -4.0478 | -1.6141
42810.448 | 689 | 18.5267 | 18.5549 | 18.5268 | 18.5222 | 17.8126 | 16.3866 | 14.4416 | 16.6052 | 17.116 | 17.2068 | 17.2257 | 16.7337 | 15.7521 | 14.3784 | 14.874 | 14.9601 | 15.777 | 13.3376 | 13.9434 | 20.0983 |  |  |  | 16.6265 | 17.0156 | 28.596 | 278.457 | 251.619 | 388.5123 | 17.2168 | 16.9317 | 24.0765 | 16.8283 | 16.9533 | 25.744 | 123.6118 | 515.3056 |  | 182.8126 | 267.3292 | 261.3776 | 323.6501 |  | 8.821 | 12.3068 | 9.6725 | 13.3296 | 15.1685 | 25.3148 | 207.1064 | 4.9653 | 8.8368 | 5.3722 | 12.0269 | 9.3247 | 42.3118 | 46.9406 | 42.7856 | 14.4235 |  |  | -0.41179 | 0.29513 | -0.046776 | -0.015114 | 0.28864 | 0.33336 | 0.53085 | 2.3359 | -0.13173 | 0.45404 | 3.9864 | 0.024778 | 0.024816 | 0.44461 | 16.1902 | 16.6289 | 17.1522 | 17.4745 | 17.4173 | 16.3559 | 14.6907 | 16.7551 | 17.095 | 17.3866 | 17.4273 | 17.1379 | 16.2848 | 14.4701 | 127.0444 | 49.2468 | 84.7064 | 49.0865 | 42.0387 | 56.4581 | 30.7762 | 15.8269 | 15.6415 | 15.9038 | 14.4188 | 16.5837 | 21.1753 |  |  |  | 92.942 | 285.3025 | 235.8034 | 189.6361 | 4.4173 | 3.4512 | 87.7966 |  |  | 13.0343 |  |  | 16.9716 | 17.9165 | 34.6861 | 16.3721 | 16.5052 | 23.5371 | 324.0621 | 674.6663 | 215.7603 | 223.3343 | 239.3326 |  | 100.9963 | 190.9492 | 89.6111 | 265.3889 | 180.604 | 339.1563 |  | 141.5652 |  |  | 33.2895 | 46.2349 | 133.2725 | [6 empty] | 210.518 |  |  | 100.7081 |  |  | 39.22 | 175.6632 | 481.6718 | 16.3213 | 138.5817 | 301.6311 | 24.1624 | 137.4524 | 428.5787 | 73.5096 | 257.3209 | 23.0181 | 210.0483 | 33.283 | 220.9529 | 18.689 | 131.3403 | 275.3208 | 64.8331 | 140.8546 | 326.5346 | 25.039 | 121.2122 | 324.0701 | 26.2086 | 199.0969 | 61.0478 | 188.982 | 35.0031 | 249.9629 | 9.713 | 18.5604 | 2.097 | 0.084593 | -38.3128 | 3.124 | 836.27 | 48.72 | -1.1503 | 0.63966 | -0.25465 | -0.14475 | 0.64683 | 0.69513 | 0.8772 | -2.7316 | -1.8331 | 0.04848 | -7.1737 | -5.5085 | -4.1515 | -1.6675
42810.448 | 690 | 18.5262 | 18.545 | 18.5229 | 18.523 | 17.8104 | 16.3894 | 14.4432 | 16.6009 | 17.1133 | 17.2083 | 17.2212 | 16.7287 | 15.753 | 14.3778 | 14.8691 | 14.9506 | 15.7683 | 13.3237 | 13.9243 | 20.1266 |  |  |  | 16.6161 | 17.0096 | 28.6422 | 283.3916 | 255.1512 | 390.4353 | 17.2171 | 16.9314 | 24.107 | 16.8271 | 16.9575 | 25.7919 | 125.2998 | 516.1067 |  | 185.7356 | 273.5876 | 265.9525 | 328.5981 |  | 8.906 | 12.5505 | 9.84 | 13.7017 | 15.602 | 26.0761 | 210.9173 | 5.0673 | 8.8786 | 5.272 | 12.1418 | 9.3383 | 42.3275 | 46.9544 | 42.8123 | 14.4503 |  |  | -0.67004 | 0.056599 | 0.01368 | -0.14128 | 0.3918 | 0.10731 | 0.47105 | 2.0645 | 0.10354 | 0.19221 | 3.9457 | 0.022194 | 0.022229 | 0.45806 | 16.1845 | 16.6246 | 17.1534 | 17.4717 | 17.4144 | 16.3505 | 14.6826 | 16.7549 | 17.0961 | 17.3832 | 17.4226 | 17.1226 | 16.2801 | 14.4619 | 132.0916 | 54.4751 | 93.6954 | 50.8149 | 42.9043 | 57.3345 | 31.2233 | 15.8353 | 15.6472 | 15.9083 | 14.4209 | 16.6037 | 21.2131 |  |  |  | 94.1193 | 293.5331 | 241.6007 | 192.9353 | 3.1104 | 4.4161 | 89.5425 |  |  | 13.1405 |  |  | 16.9839 | 17.9355 | 34.7857 | 16.3761 | 16.5248 | 23.5783 | 330.5764 | 683.4996 | 218.6086 | 226.4732 | 240.0246 |  | 102.56 | 200.0642 | 90.5569 | 271.0319 | 182.8085 | 339.8944 |  | 142.969 |  |  | 34.1145 | 47.8215 | 136.8095 | [6 empty] | 214.4139 |  |  | 102.5539 |  |  | 40.0814 | 179.1626 | 487.1413 | 16.6308 | 140.707 | 308.1444 | 24.8911 | 140.4242 | 436.567 | 75.7172 | 262.7547 | 23.5517 | 213.4756 | 34.4459 | 226.743 | 19.0824 | 134.4228 | 280.9732 | 65.756 | 143.141 | 332.4407 | 25.653 | 123.7126 | 327.773 | 26.7973 | 202.7601 | 62.2411 | 192.2842 | 35.9373 | 254.8391 | 9.9684 | 18.5554 | 2.1027 | 0.08434 | -38.261 | 3.124 | 861.8 | 50.17 | -1.4695 | 0.28024 | 0.13777 | -0.44275 | 0.75457 | 0.3949 | 0.82737 | -2.6887 | -2.0497 | 1.747e-05 | -7.63 | -6.4547 | -4.218 | -1.7133
42810.448 | 691 | 18.529 | 18.5551 | 18.5289 | 18.5285 | 17.8207 | 16.3916 | 14.4372 | 16.6072 | 17.1168 | 17.207 | 17.2247 | 16.7413 | 15.7592 | 14.3797 | 14.8803 | 14.9647 | 15.7807 | 13.3419 | 13.9431 | 20.162 |  |  |  | 16.6249 | 17.0304 | 28.7029 | 287.6842 | 259.3658 | 397.5419 | 17.2111 | 16.929 | 24.1805 | 16.8305 | 16.9581 | 25.8357 | 127.173 | 520.9735 |  | 189.014 | 279.5926 | 270.5026 | 330.9741 |  | 9.0009 | 12.7653 | 10.0158 | 14.0145 | 15.981 | 26.4413 | 214.5 | 5.1225 | 8.9224 | 5.2312 | 12.2527 | 9.343 | 42.3393 | 46.9659 | 42.8455 | 14.4772 |  |  | -0.54322 | 0.070399 | 0.030108 | 0.01117 | 0.53571 | 0.24924 | 0.41717 | 2.188 | -0.71047 | -0.59013 | 4.2082 | 0.020149 | 0.020119 | 0.51842 | 16.1845 | 16.624 | 17.1461 | 17.4634 | 17.4091 | 16.3458 | 14.6751 | 16.7494 | 17.0933 | 17.3777 | 17.4174 | 17.1217 | 16.277 | 14.452 | 130.3866 | 56.0402 | 100.1525 | 51.6014 | 44.8833 | 58.0117 | 31.682 | 15.8359 | 15.6492 | 15.9146 | 14.4228 | 16.6218 | 21.2476 |  |  |  | 95.3381 | 300.0718 | 246.4014 | 196.3452 | 2.8387 | 2.4828 | 91.9366 |  |  | 13.2352 |  |  | 16.9753 | 17.9333 | 34.8806 | 16.3698 | 16.5183 | 23.604 | 337.7184 | 692.883 | 221.309 | 229.4382 | 246.1717 |  | 104.5424 | 206.3256 | 91.6597 | 276.0144 | 185.4053 | 336.157 |  | 144.3812 |  |  | 35.0568 | 49.6587 | 141.3222 | [6 empty] | 219.4675 |  |  | 104.4308 |  |  | 40.9849 | 182.8996 | 492.8433 | 16.9977 | 142.8185 | 314.6452 | 25.6822 | 143.4339 | 446.7642 | 77.9567 | 266.895 | 24.0246 | 216.7334 | 35.6328 | 232.9448 | 19.5067 | 136.9109 | 285.9182 | 66.7885 | 145.6458 | 338.7107 | 26.3133 | 126.2678 | 332.0524 | 27.4425 | 206.284 | 63.6284 | 195.1944 | 36.9275 | 259.6622 | 9.9697 | 18.5517 | 2.1075 | 0.083167 | -38.2665 | 3.124 | 897.51 | 48.88 | -1.3302 | 0.31266 | 0.20447 | 0.12454 | 0.88287 | 0.6022 | 0.77909 | -2.7803 | -2.1809 | -0.0099423 | -7.3597 | -7.1183 | -4.2049 | -1.7604
42810.448 | 692 | 18.5227 | 18.5468 | 18.5269 | 18.5274 | 17.8088 | 16.385 | 14.4398 | 16.6034 | 17.1081 | 17.2029 | 17.2226 | 16.7342 | 15.7523 | 14.3778 | 14.8842 | 14.9641 | 15.7819 | 13.3417 | 13.9266 | 20.1886 |  |  |  | 16.6311 | 17.037 | 28.7568 | 292.5238 | 263.312 | 404.8127 | 17.2267 | 16.95 | 24.2165 | 16.8287 | 16.9753 | 25.8853 | 129.0331 | 523.9574 |  | 192.4338 | 285.0811 | 275.2247 | 333.4757 |  | 9.1009 | 12.9826 | 10.2036 | 14.3606 | 16.3724 | 26.8486 | 218.7987 | 5.1455 | 8.9673 | 5.2531 | 12.3696 | 9.3519 | 42.3604 | 46.972 | 42.8688 | 14.5042 |  |  | -0.46699 | 0.005343 | 0.053104 | -0.18596 | 0.12633 | -0.00506 | 0.68199 | 2.0198 | 0.16504 | 1.991 | 4.9052 | 0.018404 | 0.018478 | 0.58518 | 16.1992 | 16.6247 | 17.1479 | 17.4644 | 17.4135 | 16.3594 | 14.6838 | 16.7498 | 17.0921 | 17.3866 | 17.4266 | 17.1273 | 16.2805 | 14.461 | 127.1512 | 54.4754 | 97.7367 | 51.9832 | 45.1537 | 58.6667 | 32.0783 | 15.8411 | 15.6486 | 15.9262 | 14.4338 | 16.6366 | 21.2868 |  |  |  | 96.5594 | 306.6131 | 250.4456 | 200.0369 | 4.0703 | 3.5393 | 93.7833 |  |  | 13.3301 |  |  | 16.9737 | 17.9426 | 34.9814 | 16.3673 | 16.5209 | 23.641 | 346.6555 | 700.8258 | 223.7063 | 231.9839 | 248.9652 |  | 106.3719 | 212.7693 | 92.6158 | 280.9259 | 187.9321 | 333.6356 |  | 145.7375 |  |  | 36.0779 | 51.3556 | 144.914 | [6 empty] | 224.7773 |  |  | 106.6266 |  |  | 41.9077 | 187.1335 | 497.1605 | 17.3538 | 145.5498 | 320.7967 | 26.5131 | 146.6078 | 456.2868 | 80.4129 | 274.2754 | 24.5353 | 220.1631 | 36.9974 | 238.8134 | 19.9871 | 139.1588 | 290.3469 | 67.8968 | 148.6779 | 343.1007 | 27.0958 | 128.944 | 338.4431 | 28.1493 | 209.8523 | 65.3068 | 199.3492 | 37.9152 | 266.9056 | 10.9325 | 18.5476 | 2.1141 | 0.082639 | -38.1788 | 3.124 | 950.89 | 49 | -1.24 | 0.086167 | 0.27165 | -0.50835 | 0.42903 | -0.085862 | 0.99682 | -2.7846 | -2.3228 | -0.020468 | -6.922 | -6.8032 | -4.1955 | -1.8151
42810.4481 | 693 | 18.527 | 18.547 | 18.524 | 18.5284 | 17.806 | 16.3911 | 14.438 | 16.5995 | 17.1085 | 17.1999 | 17.2239 | 16.735 | 15.756 | 14.3783 | 14.8884 | 14.9746 | 15.7925 | 13.3529 | 13.9185 | 20.2192 |  |  |  | 16.6332 | 17.0434 | 28.8181 | 297.3061 | 266.5993 | 409.8042 | 17.2187 | 16.9481 | 24.2728 | 16.8349 | 16.9721 | 25.9246 | 130.8542 | 536.1983 |  | 195.7101 | 289.5612 | 280.5933 | 336.8689 |  | 9.2138 | 13.2301 | 10.4009 | 14.684 | 16.7321 | 27.5202 | 222.1393 | 5.0526 | 9.0294 | 5.3135 | 12.5048 | 9.3639 | 42.3811 | 46.9802 | 42.9046 | 14.54 |  |  | -0.51233 | 0.025715 | 0.08662 | -0.16691 | 0.43912 | -0.11348 | 0.57422 | 2.2196 | -0.099036 | 0.12109 | 5.2136 | 0.017003 | 0.017077 | 0.64034 | 16.1908 | 16.6166 | 17.1456 | 17.4648 | 17.4078 | 16.3506 | 14.6743 | 16.74 | 17.0892 | 17.3843 | 17.4176 | 17.118 | 16.2675 | 14.4586 | 127.2822 | 55.166 | 100.289 | 53.415 | 45.3057 | 59.4035 | 32.5488 | 15.8379 | 15.6509 | 15.9314 | 14.4344 | 16.6608 | 21.3274 |  |  |  | 98.0018 | 314.098 | 255.8099 | 202.9262 | 3.1598 | 3.7595 | 94.9541 |  |  | 13.4504 |  |  | 16.9814 | 17.9609 | 35.0934 | 16.3819 | 16.5325 | 23.6876 | 357.3978 | 709.3266 | 226.1072 | 234.5774 | 249.5828 |  | 108.1012 | 219.0654 | 93.4975 | 285.7176 | 190.3553 | 337.6915 |  | 147.0485 |  |  | 36.9001 | 53.2293 | 149.3297 | [6 empty] | 229.5462 |  |  | 108.2889 |  |  | 42.8454 | 191.174 | 501.9651 | 17.658 | 147.5253 | 324.6583 | 27.3808 | 149.4165 | 466.1084 | 82.8596 | 279.4642 | 25.0599 | 222.8154 | 38.433 | 243.7903 | 20.4049 | 141.5056 | 295.3499 | 69.0278 | 151.4236 | 347.2243 | 27.8118 | 131.5178 | 344.4875 | 28.7918 | 213.6713 | 66.8281 | 204.0778 | 38.9853 | 271.4405 | 11.393 | 18.5413 | 2.122 | 0.083109 | -38.1472 | 3.124 | 972.35 | 50.55 | -1.3036 | 0.18912 | 0.34709 | -0.48181 | 0.80076 | -0.40708 | 0.9157 | -2.7321 | -2.4633 | -0.031964 | -6.8486 | -7.0315 | -4.2121 | -1.8386
42810.4481 | 694 | 18.5223 | 18.5494 | 18.5247 | 18.522 | 17.7979 | 16.3754 | 14.4255 | 16.5938 | 17.1074 | 17.2004 | 17.2144 | 16.7281 | 15.7503 | 14.3717 | 14.8902 | 14.9693 | 15.787 | 13.3482 | 13.9187 | 20.2525 |  |  |  | 16.6241 | 17.0473 | 28.8654 | 301.8122 | 270.4313 | 412.8069 | 17.2175 | 16.9493 | 24.3191 | 16.836 | 16.9741 | 25.9672 | 132.6923 | 550.2104 |  | 199.1097 | 293.8494 | 285.8753 | 339.0164 |  | 9.3285 | 13.4727 | 10.5895 | 14.9789 | 17.0643 | 28.455 | 225.3732 | 4.9773 | 9.0781 | 5.3435 | 12.6314 | 9.3748 | 42.3817 | 46.9917 | 42.9343 | 14.5669 |  |  | -0.81395 | 0.072371 | -0.001436 | 0.18991 | 0.35566 | -0.063544 | 0.43754 | 2.3793 | 0.45674 | 0.34831 | 5.5867 | 0.015774 | 0.015807 | 0.66869 | 16.2016 | 16.6124 | 17.1467 | 17.4694 | 17.4131 | 16.3505 | 14.6742 | 16.7518 | 17.0858 | 17.3809 | 17.4139 | 17.1191 | 16.2769 | 14.4615 | 125.0852 | 51.5959 | 98.4419 | 55.0754 | 46.1422 | 60.0734 | 32.9811 | 15.8243 | 15.6462 | 15.9327 | 14.4185 | 16.6609 | 21.3571 |  |  |  | 99.3533 | 320.3294 | 261.1707 | 206.2889 | 4.6524 | 2.2136 | 96.2255 |  |  | 13.5691 |  |  | 16.9896 | 17.9785 | 35.2081 | 16.3766 | 16.548 | 23.7322 | 367.9401 | 715.9803 | 229.0795 | 237.57 | 249.7453 |  | 110.0782 | 221.9775 | 94.609 | 290.6693 | 192.9213 | 341.4727 |  | 148.551 |  |  | 38.0126 | 55.3304 | 153.709 | [6 empty] | 233.514 |  |  | 110.0616 |  |  | 43.7731 | 195.2464 | 505.7585 | 18.0118 | 150.1121 | 330.3483 | 28.2464 | 152.1209 | 474.7596 | 85.3191 | 283.3395 | 25.6108 | 226.3936 | 39.8893 | 248.0343 | 20.8854 | 144.0309 | 300.6998 | 70.1444 | 153.9039 | 350.8901 | 28.5319 | 134.4543 | 349.4768 | 29.4408 | 217.1061 | 68.0734 | 206.8145 | 40.0238 | 276.9695 | 12.1438 | 18.5346 | 2.1302 | 0.082791 | -38.2614 | 3.124 | 1010.29 | 48.85 | -1.6467 | 0.3174 | -0.044709 | 0.51415 | 0.72178 | -0.30509 | 0.80056 | -2.6567 | -2.5009 | -0.039798 | -6.5244 | -6.7754 | -4.193 | -1.8787
42810.4481 | 695 | 18.52 | 18.548 | 18.5176 | 18.5196 | 17.7966 | 16.3808 | 14.4272 | 16.5878 | 17.1045 | 17.1953 | 17.2157 | 16.7265 | 15.7401 | 14.3705 | 14.8919 | 14.969 | 15.7971 | 13.3446 | 13.8972 | 20.2914 |  |  |  | 16.6356 | 17.0612 | 28.9279 | 306.068 | 274.6627 | 414.4234 | 17.2232 | 16.9576 | 24.3857 | 16.8391 | 16.9879 | 26.0204 | 134.6255 | 558.2853 |  | 202.5009 | 298.6625 | 291.1213 | 344.5263 |  | 9.475 | 13.7637 | 10.8252 | 15.3986 | 17.4908 | 29.2225 | 230.0649 | 5.0172 | 9.1327 | 5.3865 | 12.7695 | 9.3765 | 42.3895 | 46.9833 | 42.9752 | 14.5938 |  |  | -0.79818 | 0.1854 | -0.049404 | 0.21488 | 0.39443 | 0.43258 | 0.41191 | 1.7077 | 0.054893 | 0.3718 | 5.5166 | 0.014788 | 0.014714 | 0.65302 | 16.206 | 16.6187 | 17.1445 | 17.4732 | 17.4153 | 16.3546 | 14.6834 | 16.7512 | 17.0935 | 17.391 | 17.4216 | 17.121 | 16.2739 | 14.4629 | 131.1386 | 51.6165 | 95.346 | 53.2673 | 45.7887 | 60.9059 | 33.3425 | 15.837 | 15.6581 | 15.9361 | 14.4307 | 16.6868 | 21.4111 |  |  |  | 100.7007 | 325.4871 | 266.3867 | 210.9985 | 4.4534 | 2.1039 | 98.6866 |  |  | 13.7001 |  |  | 16.9931 | 17.9919 | 35.3352 | 16.3832 | 16.543 | 23.7606 | 377.7301 | 719.5083 | 232.2377 | 240.4439 | 253.026 |  | 112.2928 | 226.6816 | 95.8193 | 295.1367 | 195.6003 | 354.3487 |  | 150.2208 |  |  | 39.2605 | 57.3908 | 157.4007 | [6 empty] | 238.0418 |  |  | 111.6807 |  |  | 44.7567 | 199.2054 | 509.8979 | 18.45 | 152.5333 | 334.2991 | 29.1515 | 155.3322 | 483.831 | 87.5851 | 288.3969 | 26.1772 | 229.8054 | 41.439 | 254.5913 | 21.3096 | 146.1777 | 305.5142 | 71.1788 | 156.6342 | 355.1657 | 29.2733 | 137.164 | 354.167 | 30.1261 | 220.61 | 69.2315 | 209.527 | 41.096 | 282.5061 | 12.5161 | 18.526 | 2.1391 | 0.082154 | -38.2523 | 3.124 | 1049.35 | 49.17 | -1.6326 | 0.50827 | -0.26238 | 0.54719 | 0.76107 | 0.79702 | 0.77775 | -2.6578 | -2.5842 | -0.027431 | -7.0975 | -6.3889 | -4.2629 | -1.9562
42810.4481 | 696 | 18.526 | 18.5481 | 18.5233 | 18.5241 | 17.8 | 16.3873 | 14.4303 | 16.6002 | 17.1055 | 17.1983 | 17.2125 | 16.7285 | 15.7447 | 14.378 | 14.8852 | 14.9669 | 15.7956 | 13.3394 | 13.8834 | 20.3166 |  |  |  | 16.6298 | 17.0693 | 28.9828 | 309.9556 | 278.3976 | 419.5345 | 17.2333 | 16.9587 | 24.4257 | 16.8387 | 16.9853 | 26.0645 | 136.6366 | 563.4743 |  | 205.884 | 304.1118 | 295.772 | 346.1316 |  | 9.591 | 14.0257 | 11.0233 | 15.7621 | 17.9069 | 29.9316 | 234.5616 | 5.1501 | 9.1854 | 5.4832 | 12.9051 | 9.3839 | 42.3957 | 46.9834 | 43.0209 | 14.6138 |  |  | -0.61419 | 0.27213 | 0.14904 | 0.035486 | 0.41086 | 0.078396 | 0.47434 | 2.326 | 0.36761 | 1.1051 | 5.2484 | 0.013849 | 0.013944 | 0.66359 | 16.2087 | 16.6271 | 17.1484 | 17.4691 | 17.4111 | 16.3516 | 14.6779 | 16.7475 | 17.0868 | 17.3977 | 17.4205 | 17.1228 | 16.2748 | 14.461 | 137.9059 | 51.2025 | 95.4873 | 52.2805 | 45.0033 | 61.8835 | 33.7584 | 15.8361 | 15.6554 | 15.9401 | 14.432 | 16.7081 | 21.44 |  |  |  | 102.0606 | 329.8914 | 270.7893 | 214.4716 | 4.7332 | 2.9534 | 100.8234 |  |  | 13.8136 |  |  | 16.9861 | 17.9912 | 35.471 | 16.3677 | 16.5495 | 23.7933 | 391.1911 | 723.1879 | 235.2686 | 243.4145 | 260.2419 |  | 114.3882 | 237.1214 | 96.8933 | 298.6748 | 198.0626 | 359.3841 |  | 151.7624 |  |  | 40.5438 | 59.5287 | 162.1955 | [6 empty] | 242.5126 |  |  | 113.5287 |  |  | 45.6932 | 203.3388 | 513.6387 | 18.9164 | 155.0823 | 339.6231 | 30.0632 | 158.8611 | 491.6304 | 89.9056 | 292.9982 | 26.8349 | 233.2458 | 43.0476 | 261.1069 | 21.7974 | 148.5895 | 310.5872 | 72.2321 | 159.4451 | 360.1476 | 30.044 | 140.0184 | 358.5684 | 30.8552 | 224.1729 | 70.5194 | 211.8088 | 42.2189 | 287.5614 | 11.1536 | 18.5192 | 2.1483 | 0.081409 | -38.2012 | 3.124 | 1085.28 | 49.93 | -1.4374 | 0.61607 | 0.45593 | 0.22247 | 0.77767 | 0.3397 | 0.83559 | -2.7726 | -2.8321 | 0.0006577 | -7.7325 | -6.3557 | -4.2204 | -1.9987
42810.4481 | 697 | 18.5343 | 18.5623 | 18.5286 | 18.5385 | 17.8113 | 16.3969 | 14.4396 | 16.6044 | 17.1133 | 17.215 | 17.2229 | 16.744 | 15.753 | 14.3841 | 14.8807 | 14.965 | 15.7985 | 13.3404 | 13.8717 | 20.3482 |  |  |  | 16.633 | 17.0695 | 29.0349 | 314.3384 | 281.4984 | 424.5834 | 17.2335 | 16.9617 | 24.4664 | 16.8409 | 16.9927 | 26.1021 | 138.6459 | 569.8353 |  | 209.4365 | 309.864 | 299.7605 | 347.9512 |  | 9.7541 | 14.3169 | 11.2342 | 16.1497 | 18.3611 | 31.742 | 238.8333 | 5.279 | 9.2453 | 5.5727 | 13.0409 | 9.4012 | 42.4065 | 46.9948 | 43.0766 | 14.6496 |  |  | -0.47356 | 0.006003 | 0.011052 | 0.12814 | 0.35566 | 0.7572 | 0.22464 | 1.9186 | 0.10101 | 0.98694 | 5.4892 | 0.013103 | 0.013111 | 0.72757 | 16.2155 | 16.6234 | 17.1492 | 17.4662 | 17.4142 | 16.3514 | 14.6877 | 16.7434 | 17.0907 | 17.3898 | 17.4211 | 17.1198 | 16.2748 | 14.4641 | 144.1949 | 51.6129 | 98.4965 | 52.9929 | 45.3321 | 62.9077 | 34.1968 | 15.8403 | 15.6586 | 15.9448 | 14.4393 | 16.7248 | 21.4744 |  |  |  | 103.4823 | 334.1781 | 274.9203 | 217.3171 | 4.8333 | 1.9669 | 103.0311 |  |  | 13.9188 |  |  | 16.985 | 17.9993 | 35.5996 | 16.371 | 16.5562 | 23.8174 | 400.2606 | 727.3281 | 238.077 | 246.5181 | 265.0043 |  | 116.4797 | 245.9787 | 98.0318 | 303.0409 | 200.5568 | 363.4123 |  | 153.3417 |  |  | 41.8295 | 61.4811 | 167.1316 | [6 empty] | 245.91 |  |  | 115.3665 |  |  | 46.6659 | 207.6394 | 517.173 | 19.3533 | 157.5256 | 346.5028 | 30.9681 | 162.2332 | 497.3223 | 92.1737 | 297.8889 | 27.502 | 236.7046 | 44.5958 | 265.6154 | 22.3266 | 151.129 | 315.5664 | 73.1851 | 162.0981 | 364.6523 | 30.8655 | 142.7258 | 364.4484 | 31.627 | 227.9056 | 71.807 | 214.995 | 43.3716 | 293.3568 | 11.233 | 18.5097 | 2.16 | 0.08329 | -38.188 | 3.124 | 1113.6 | 49.03 | -1.2668 | 0.091547 | 0.12422 | 0.42296 | 0.7257 | 1.0589 | 0.57674 | -2.8189 | -3.0333 | 0.0083183 | -8.3087 | -6.6385 | -4.1836 | -2.0212
42810.4481 | 698 | 18.5366 | 18.5601 | 18.5282 | 18.5314 | 17.8203 | 16.3916 | 14.4327 | 16.6013 | 17.1168 | 17.2082 | 17.2308 | 16.7335 | 15.7527 | 14.3757 | 14.8852 | 14.9646 | 15.799 | 13.3478 | 13.8766 | 20.3833 |  |  |  | 16.6332 | 17.0777 | 29.0967 | 318.9587 | 284.8715 | 427.8661 | 17.2293 | 16.9675 | 24.508 | 16.832 | 16.9992 | 26.1495 | 140.6102 | 572.2228 |  | 212.9791 | 314.7251 | 304.3404 | 350.4817 |  | 9.8976 | 14.6276 | 11.4564 | 16.5299 | 18.7688 | 33.6889 | 242.622 | 5.3461 | 9.3155 | 5.6472 | 13.1853 | 9.4086 | 42.4343 | 46.9969 | 43.1096 | 14.6761 |  |  | -0.57936 | 0.1072 | -0.034948 | -0.33579 | 0.539 | 0.50026 | 0.70236 | 2.1177 | 0.10685 | 0.47356 | 5.785 | 0.012398 | 0.012429 | 0.75177 | 16.2179 | 16.6228 | 17.148 | 17.467 | 17.4089 | 16.3501 | 14.6753 | 16.7446 | 17.0887 | 17.3893 | 17.4244 | 17.1176 | 16.2721 | 14.4606 | 147.4417 | 48.1165 | 96.3019 | 54.2668 | 46.5062 | 63.8933 | 34.5534 | 15.8407 | 15.663 | 15.9468 | 14.438 | 16.7433 | 21.5235 |  |  |  | 105.1147 | 338.3854 | 278.3638 | 219.9923 | 3.7253 | 1.4392 | 106.4576 |  |  | 14.077 |  |  | 16.9891 | 18.0223 | 35.7624 | 16.3777 | 16.5552 | 23.879 | 412.6482 | 731.43 | 240.9832 | 249.7276 | 268.5358 |  | 118.9303 | 250.2074 | 99.5974 | 309.229 | 203.5923 | 373.8897 |  | 155.5077 |  |  | 43.014 | 63.2419 | 171.3326 | [6 empty] | 249.8919 |  |  | 117.02 |  |  | 47.6062 | 211.8013 | 521.4832 | 19.8108 | 160.294 | 352.3796 | 31.8664 | 165.8098 | 504.0195 | 94.5417 | 303.1168 | 28.2199 | 239.8081 | 46.1417 | 270.249 | 22.8547 | 153.7194 | 320.5859 | 74.2913 | 164.8352 | 368.2462 | 31.7382 | 145.3503 | 369.2477 | 32.3823 | 231.5935 | 73.1747 | 218.6271 | 44.5714 | 298.7274 | 11.4198 | 18.4977 | 2.1709 | 0.082451 | -38.2217 | 3.1241 | 1141.45 | 49.81 | -1.4044 | 0.38707 | -0.22101 | -0.68506 | 0.89622 | 0.86342 | 1.0231 | -2.8158 | -3.089 | -0.0053621 | -8.5515 | -6.3527 | -4.168 | -2.0302
42810.4481 | 699 | 18.5334 | 18.5591 | 18.5204 | 18.5245 | 17.7986 | 16.3857 | 14.431 | 16.601 | 17.109 | 17.2033 | 17.2192 | 16.7297 | 15.7497 | 14.3755 | 14.8845 | 14.9753 | 15.8035 | 13.3475 | 13.8699 | 20.4089 |  |  |  | 16.6359 | 17.0771 | 29.1474 | 323.3729 | 287.7342 | 432.5573 | 17.2251 | 16.9809 | 24.5616 | 16.838 | 17.0033 | 26.202 | 142.6868 | 584.8785 |  | 216.784 | 320.3033 | 309.5591 | 350.3501 |  | 10.0144 | 14.8841 | 11.6282 | 16.8698 | 19.1343 | 35.2811 | 246.0468 | 5.3466 | 9.3606 | 5.6924 | 13.3165 | 9.4181 | 42.445 | 46.9863 | 43.1419 | 14.6839 |  |  | -1.157 | 0.18868 | -0.079632 | -0.086738 | 0.6356 | 0.2131 | 0.9882 | 2.4404 | 0.21952 | 0.96554 | 5.8838 | 0.011795 | 0.011792 | 0.77142 | 16.2198 | 16.6241 | 17.1483 | 17.4719 | 17.4106 | 16.346 | 14.6754 | 16.748 | 17.0841 | 17.3849 | 17.4171 | 17.1204 | 16.2733 | 14.4581 | 145.3511 | 46.7016 | 91.2192 | 53.1191 | 46.9492 | 64.6945 | 34.891 | 15.8416 | 15.6678 | 15.9597 | 14.4446 | 16.7665 | 21.5589 |  |  |  | 106.5926 | 341.5412 | 281.1284 | 224.1637 | 4.3888 | 3.3645 | 109.478 |  |  | 14.3536 |  |  | 16.9848 | 18.0254 | 35.9325 | 16.3774 | 16.5592 | 23.9107 | 420.737 | 734.3013 | 245.0059 | 253.613 | 271.2564 |  | 121.0324 | 251.85 | 100.8824 | 313.6883 | 206.2269 | 378.7263 |  | 157.3493 |  |  | 44.186 | 64.9738 | 175.6222 | [6 empty] | 254.3761 |  |  | 118.635 |  |  | 48.6677 | 216.0417 | 526.1617 | 20.2767 | 163.7102 | 359.0228 | 32.8306 | 169.4137 | 512.3513 | 97.0935 | 308.2076 | 28.9528 | 243.1658 | 47.7423 | 274.5219 | 23.4085 | 156.3206 | 324.9741 | 75.5002 | 167.731 | 371.79 | 32.6275 | 148.1085 | 374.9079 | 33.1491 | 235.4175 | 74.6523 | 221.3311 | 45.7404 | 303.4243 | 12.7721 | 18.4867 | 2.1816 | 0.081105 | -38.2074 | 3.1241 | 1148.22 | 49.43 | -1.9913 | 0.51375 | -0.33376 | -0.34833 | 0.97575 | 0.56499 | 1.2167 | -2.804 | -3.0838 | 0.0092319 | -8.2232 | -5.7482 | -4.073 | -2.0868
42810.4481 | 700 | 18.5388 | 18.5539 | 18.5329 | 18.5189 | 17.7994 | 16.3841 | 14.4334 | 16.6043 | 17.1088 | 17.2093 | 17.2106 | 16.7293 | 15.7516 | 14.3797 | 14.8944 | 14.9798 | 15.8145 | 13.356 | 13.8671 | 20.4474 |  |  |  | 16.6428 | 17.0879 | 29.2164 | 327.9132 | 290.2265 | 435.2028 | 17.2334 | 16.9806 | 24.6019 | 16.8407 | 17.0094 | 26.251 | 144.6495 | 588.7397 |  | 220.4193 | 325.6531 | 314.38 | 354.6704 |  | 10.1865 | 15.2238 | 11.8609 | 17.2728 | 19.6973 | 35.9413 | 250.3631 | 5.3402 | 9.427 | 5.954 | 13.4768 | 9.4296 | 42.4809 | 46.9791 | 43.1793 | 14.7033 |  |  | -0.88952 | 0.041487 | 0.071504 | -0.62886 | 0.40889 | 0.51406 | 0.31532 | 1.7905 | 0.9016 | 0.52873 | 5.7346 | 0.011209 | 0.011324 | 0.78295 | 16.2114 | 16.6153 | 17.1425 | 17.4589 | 17.4044 | 16.3404 | 14.6756 | 16.7379 | 17.0783 | 17.3785 | 17.4094 | 17.1161 | 16.2717 | 14.4484 | 146.0171 | 47.6047 | 94.2009 | 54.8246 | 48.9314 | 65.5686 | 35.3154 | 15.8467 | 15.6655 | 15.9653 | 14.4474 | 16.7879 | 21.5923 |  |  |  | 108.084 | 345.459 | 284.4941 | 227.9834 | 5.1797 | 3.6615 | 111.7425 |  |  | 14.5267 |  |  | 16.9785 | 18.0224 | 36.1126 | 16.3652 | 16.5528 | 23.9414 | 432.0491 | 735.5082 | 248.1264 | 257.0013 | 275.1304 |  | 123.2014 | 253.6729 | 102.1663 | 319.4829 | 208.898 | 376.2085 |  | 159.0307 |  |  | 45.2754 | 66.6756 | 179.8835 | [6 empty] | 259.1545 |  |  | 120.5478 |  |  | 49.7763 | 220.4283 | 531.4254 | 20.7646 | 167.4317 | 365.7465 | 33.8125 | 173.0794 | 520.3414 | 99.6829 | 313.9623 | 29.6876 | 246.6414 | 49.4101 | 278.5923 | 23.9624 | 158.6926 | 328.099 | 76.6796 | 170.7806 | 375.6847 | 33.4763 | 151.1998 | 380.9111 | 33.9665 | 239.0317 | 76.0764 | 224.3553 | 46.9055 | 307.5504 | 12.3083 | 18.4735 | 2.1922 | 0.079976 | -38.2064 | 3.1241 | 1184.06 | 49.03 | -1.7493 | 0.24105 | 0.31645 | -0.93847 | 0.78346 | 0.87845 | 0.68799 | -2.821 | -3.0835 | -0.010235 | -8.1924 | -6.0295 | -4.1063 | -2.1328
42810.4481 | 701 | 18.5351 | 18.5622 | 18.5296 | 18.5279 | 17.8087 | 16.3865 | 14.4398 | 16.6062 | 17.115 | 17.2115 | 17.2204 | 16.7402 | 15.7498 | 14.3828 | 14.895 | 14.9742 | 15.8135 | 13.3544 | 13.8657 | 20.4792 |  |  |  | 16.6408 | 17.1002 | 29.2733 | 332.3903 | 293.2257 | 439.9036 | 17.239 | 16.995 | 24.6604 | 16.8422 | 17.0168 | 26.2964 | 146.8429 | 591.4973 |  | 224.0459 | 331.0061 | 319.0399 | 358.5216 |  | 10.3326 | 15.5087 | 12.0407 | 17.6227 | 20.1047 | 36.7258 | 253.9609 | 5.2507 | 9.4704 | 6.0479 | 13.616 | 9.4457 | 42.5084 | 46.9578 | 43.195 | 14.72 |  |  | -0.81395 | -0.059053 | 0.01368 | -0.53489 | 0.22227 | 0.57254 | 0.38628 | 2.1197 | -0.122 | 0.71818 | 6.0467 | 0.010703 | 0.010708 | 0.76495 | 16.2344 | 16.631 | 17.1525 | 17.4689 | 17.4149 | 16.3519 | 14.683 | 16.7605 | 17.0981 | 17.3958 | 17.4289 | 17.1262 | 16.278 | 14.4591 | 150.7015 | 45.7845 | 95.2297 | 55.7657 | 49.5223 | 66.566 | 35.716 | 15.8393 | 15.6695 | 15.9632 | 14.4504 | 16.8055 | 21.6306 |  |  |  | 109.5885 | 349.3213 | 287.9898 | 230.99 | 5.6163 | 2.9516 | 114.7548 |  |  | 14.6792 |  |  | 16.992 | 18.05 | 36.3217 | 16.3795 | 16.5814 | 23.9962 | 441.4482 | 734.6237 | 250.6476 | 259.5774 | 279.5937 |  | 125.6789 | 251.9266 | 103.5831 | 326.9397 | 211.9226 | 380.6391 |  | 161.0995 |  |  | 46.2932 | 68.4009 | 183.9985 | [6 empty] | 263.5323 |  |  | 122.412 |  |  | 50.8571 | 224.809 | 537.334 | 21.272 | 170.793 | 372.3284 | 34.8575 | 176.6876 | 527.1529 | 102.0934 | 318.9425 | 30.3692 | 250.1232 | 50.9982 | 282.6797 | 24.4958 | 160.6738 | 331.8 | 77.8629 | 173.6575 | 378.5686 | 34.342 | 154.5235 | 387.5278 | 34.7886 | 242.4361 | 77.3556 | 227.4988 | 48.0742 | 313.3572 | 12.1209 | 18.4626 | 2.2065 | 0.081756 | -38.232 | 3.1241 | 1216.85 | 50.21 | -1.6789 | -0.28773 | 0.13848 | -0.86595 | 0.57836 | 0.92825 | 0.76245 | -2.8408 | -2.9785 | -0.055781 | -8.5932 | -6.0966 | -4.1158 | -2.1555
42810.4482 | 702 | 18.5342 | 18.5596 | 18.525 | 18.5321 | 17.8108 | 16.3874 | 14.4364 | 16.6086 | 17.1172 | 17.2146 | 17.2227 | 16.7356 | 15.7509 | 14.3809 | 14.8947 | 14.983 | 15.8187 | 13.3538 | 13.87 | 20.5151 |  |  |  | 16.6423 | 17.1074 | 29.3319 | 337.1802 | 296.3198 | 444.5191 | 17.2377 | 16.994 | 24.7121 | 16.8452 | 17.0187 | 26.3466 | 149.0165 | 592.7214 |  | 227.507 | 336.6991 | 323.7665 | 360.4429 |  | 10.5007 | 15.8459 | 12.2453 | 17.9956 | 20.5321 | 37.735 | 257.6896 | 5.1765 | 9.5485 | 6.1191 | 13.7746 | 9.4565 | 42.5349 | 46.9276 | 43.2109 | 14.7367 |  |  | -0.90332 | 0.11574 | -0.15914 | -0.3877 | 0.61917 | -0.25476 | 0.12475 | 1.9272 | 0.27401 | 1.7728 | 6.4153 | 0.010302 | 0.010281 | 0.7783 | 16.2248 | 16.6224 | 17.143 | 17.4663 | 17.403 | 16.3467 | 14.6775 | 16.7472 | 17.087 | 17.3851 | 17.4155 | 17.1188 | 16.2674 | 14.4578 | 154.6343 | 46.7474 | 97.6706 | 56.8625 | 49.9356 | 67.549 | 36.135 | 15.8454 | 15.6735 | 15.9766 | 14.4525 | 16.8202 | 21.6716 |  |  |  | 111.2088 | 352.4148 | 291.1657 | 233.1774 | 4.4822 | 2.2688 | 117.2322 |  |  | 14.8116 |  |  | 16.9813 | 18.0451 | 36.5232 | 16.3707 | 16.5765 | 24.0387 | 454.6644 | 735.7976 | 253.4948 | 262.4267 | 282.0662 |  | 128.0111 | 254.0417 | 105.0964 | 334.4791 | 214.7738 | 385.6866 |  | 162.9534 |  |  | 47.2457 | 69.9112 | 187.4815 | [6 empty] | 267.3222 |  |  | 124.7966 |  |  | 51.9002 | 229.3844 | 542.4579 | 21.811 | 173.4465 | 378.8045 | 35.9497 | 180.0785 | 534.9951 | 104.4222 | 325.5035 | 31.074 | 253.0681 | 52.6063 | 286.7696 | 24.9662 | 162.6826 | 336.5943 | 79.0188 | 176.2219 | 380.995 | 35.2089 | 157.7795 | 394.0421 | 35.5623 | 245.8194 | 78.5679 | 230.022 | 49.2641 | 319.3439 | 14.1459 | 18.4553 | 2.219 | 0.08214 | -38.3578 | 3.1241 | 1252 | 49.38 | -1.7744 | 0.40304 | -0.47262 | -0.73767 | 0.96688 | -0.62021 | 0.434 | -2.8109 | -2.9768 | -0.11155 | -8.9122 | -6.3185 | -4.0719 | -2.1506
42810.4482 | 703 | 18.5336 | 18.556 | 18.5261 | 18.5259 | 17.8095 | 16.3857 | 14.435 | 16.6009 | 17.1111 | 17.2123 | 17.2155 | 16.7378 | 15.746 | 14.3732 | 14.8944 | 14.9805 | 15.8207 | 13.3606 | 13.8552 | 20.5423 |  |  |  | 16.6335 | 17.1106 | 29.3947 | 341.3517 | 298.7076 | 444.1292 | 17.2433 | 16.9955 | 24.7676 | 16.8436 | 17.0314 | 26.3974 | 151.1846 | 594.335 |  | 230.9965 | 342.2579 | 328.1478 | 366.3187 |  | 10.6611 | 16.1902 | 12.4398 | 18.315 | 20.9561 | 38.8757 | 260.7284 | 5.1739 | 9.6194 | 6.0513 | 13.9362 | 9.4757 | 42.5657 | 46.9184 | 43.216 | 14.7497 |  |  | -1.1254 | 0.060543 | -0.046776 | -0.22539 | -0.049776 | 0.23676 | 0.39351 | 2.3313 | 0.010524 | 0.44376 | 6.2687 | 0.0098584 | 0.0098962 | 0.79484 | 16.236 | 16.6258 | 17.144 | 17.4701 | 17.4104 | 16.3492 | 14.672 | 16.7425 | 17.0895 | 17.3836 | 17.4126 | 17.1198 | 16.2798 | 14.4603 | 153.1575 | 42.2438 | 94.0505 | 55.3931 | 50.7879 | 68.4564 | 36.4369 | 15.8491 | 15.6692 | 15.9732 | 14.4572 | 16.8391 | 21.7181 |  |  |  | 112.8924 | 356.8911 | 295.7639 | 235.961 | 5.448 | 0.75339 | 118.4913 |  |  | 14.9684 |  |  | 16.9995 | 18.075 | 36.7539 | 16.3795 | 16.5912 | 24.0816 | 461.684 | 736.3036 | 256.5028 | 265.4847 | 284.6762 |  | 130.2553 | 255.2007 | 106.4865 | 339.5232 | 217.4236 | 391.8548 |  | 164.9253 |  |  | 48.3695 | 71.5234 | 191.2022 | [6 empty] | 270.9597 |  |  | 126.8584 |  |  | 52.9303 | 233.4914 | 546.7331 | 22.3383 | 176.8639 | 385.0891 | 36.9844 | 183.4558 | 542.9713 | 106.8815 | 331.0569 | 31.7699 | 256.792 | 54.2751 | 290.3715 | 25.4893 | 164.96 | 341.482 | 80.1169 | 179.0112 | 383.7501 | 36.1824 | 161.0041 | 399.5244 | 36.3857 | 249.0112 | 80.0296 | 232.0499 | 50.4062 | 324.4853 | 12.8901 | 18.4379 | 2.2326 | 0.080793 | -38.3181 | 3.1241 | 1306.61 | 49.12 | -1.98 | 0.29168 | -0.25638 | -0.56278 | -0.27465 | 0.59899 | 0.77222 | -2.7879 | -2.9532 | -0.10768 | -8.6391 | -5.8807 | -4.1376 | -2.1593
42810.4482 | 704 | 18.5343 | 18.5603 | 18.5276 | 18.5213 | 17.8011 | 16.3822 | 14.4235 | 16.5959 | 17.1051 | 17.2059 | 17.2109 | 16.7316 | 15.7441 | 14.3687 | 14.902 | 14.9829 | 15.8288 | 13.3595 | 13.8286 | 20.5673 |  |  |  | 16.6338 | 17.1149 | 29.4532 | 345.5005 | 301.2919 | 451.8197 | 17.2505 | 17.011 | 24.8117 | 16.8512 | 17.04 | 26.4494 | 153.4401 | 601.771 |  | 234.5714 | 347.4476 | 333.0636 | 371.2693 |  | 10.8185 | 16.503 | 12.6355 | 18.5879 | 21.2488 | 40.0995 | 263.9791 | 5.2316 | 9.6714 | 5.8719 | 14.0818 | 9.4772 | 42.5964 | 46.9243 | 43.2193 | 14.7602 |  |  | -1.0111 | -0.036709 | -0.10657 | -0.46064 | 0.51009 | -0.42036 | 0.5164 | 2.4857 | 0.19014 | 0.53985 | 6.346 | 0.0094674 | 0.0095101 | 0.79557 | 16.2481 | 16.6334 | 17.1469 | 17.4724 | 17.4141 | 16.351 | 14.6793 | 16.7532 | 17.0956 | 17.3815 | 17.4251 | 17.1261 | 16.2746 | 14.4605 | 157.5566 | 40.4414 | 86.6966 | 52.3216 | 48.6075 | 69.4075 | 36.6578 | 15.8487 | 15.6784 | 15.9812 | 14.4552 | 16.8586 | 21.7632 |  |  |  | 114.4683 | 362.7481 | 301.3854 | 238.6777 | 4.9994 | 1.8677 | 119.4099 |  |  | 15.119 |  |  | 16.9976 | 18.0743 | 36.9833 | 16.3783 | 16.5906 | 24.1291 | 470.2077 | 736.1293 | 259.7729 | 268.4498 | 287.9302 |  | 132.5857 | 257.6729 | 107.9009 | 345.7938 | 220.3064 | 390.4455 |  | 166.9064 |  |  | 49.4367 | 73.104 | 194.871 | [6 empty] | 275.1572 |  |  | 128.6147 |  |  | 53.9854 | 237.8976 | 552.7905 | 22.9526 | 180.4725 | 392.1997 | 37.9482 | 186.6636 | 549.8459 | 109.3378 | 335.4973 | 32.4518 | 260.6557 | 55.7718 | 293.5788 | 26.1518 | 167.1978 | 345.6944 | 81.179 | 182.5545 | 386.6785 | 37.0965 | 164.361 | 404.5273 | 37.2079 | 252.5687 | 81.5869 | 234.5583 | 51.6745 | 329.7822 | 13.4084 | 18.4203 | 2.2456 | 0.079853 | -38.2471 | 3.1241 | 1328.68 | 50.26 | -1.8868 | -0.22724 | -0.38719 | -0.80498 | 0.88092 | -0.79969 | 0.88635 | -2.7785 | -2.9649 | -0.12391 | -9.0136 | -5.0375 | -4.1731 | -2.1703
42810.4482 | 705 | 18.542 | 18.5589 | 18.5268 | 18.5253 | 17.8053 | 16.3832 | 14.4293 | 16.6008 | 17.1089 | 17.2106 | 17.224 | 16.7288 | 15.7552 | 14.3728 | 14.8971 | 14.9938 | 15.8421 | 13.3505 | 13.8247 | 20.6112 |  |  |  | 16.6349 | 17.1186 | 29.5183 | 350.2494 | 304.2869 | 456.3767 | 17.2435 | 17.0099 | 24.8482 | 16.8521 | 17.0424 | 26.4946 | 155.8487 | 603.976 |  | 238.0917 | 352.376 | 337.9863 | 376.4327 |  | 11.0377 | 16.8717 | 12.8997 | 18.9553 | 21.6184 | 41.4318 | 267.3701 | 5.2902 | 9.7358 | 5.7901 | 14.2619 | 9.4995 | 42.6318 | 46.9466 | 43.224 | 14.7834 |  |  | -0.51627 | -0.045253 | -0.05532 | -0.32199 | 0.44503 | 0.17959 | 0.54071 | 2.4239 | -0.66882 | 1.13 | 6.7714 | 0.0092013 | 0.0091503 | 0.71644 | 16.2412 | 16.6244 | 17.1466 | 17.4674 | 17.4094 | 16.3479 | 14.675 | 16.752 | 17.0888 | 17.3787 | 17.4195 | 17.1142 | 16.2688 | 14.4555 | 159.0314 | 44.4414 | 87.5118 | 52.6128 | 49.1306 | 70.3144 | 36.9993 | 15.8477 | 15.6711 | 15.99 | 14.4591 | 16.8761 | 21.7985 |  |  |  | 116.0885 | 370.0085 | 307.5463 | 241.473 | 3.4943 | 3.6255 | 120.7879 |  |  | 15.2573 |  |  | 16.9899 | 18.0851 | 37.2327 | 16.38 | 16.5921 | 24.1659 | 479.2377 | 738.2839 | 262.4188 | 271.3029 | 290.3577 |  | 135.0376 | 258.0836 | 109.4314 | 352.5474 | 223.5181 | 390.3717 |  | 168.9036 |  |  | 50.3215 | 74.5905 | 197.8642 | [6 empty] | 280.1259 |  |  | 130.5309 |  |  | 55.1771 | 242.2871 | 561.4061 | 23.5004 | 183.674 | 397.3553 | 38.8696 | 190.1028 | 555.459 | 111.8922 | 340.331 | 33.2447 | 264.0429 | 57.261 | 297.0723 | 26.8502 | 169.7752 | 349.3449 | 82.3115 | 186.4976 | 389.4257 | 37.9403 | 167.8966 | 409.8586 | 38.0641 | 256.2737 | 83.2401 | 236.7457 | 52.9059 | 336.0228 | 14.2316 | 18.4041 | 2.2619 | 0.082748 | -38.2954 | 3.1242 | 1371.51 | 48.96 | -1.3525 | -0.25247 | -0.27914 | -0.67344 | 0.82457 | 0.52381 | 0.9089 | -2.7404 | -2.9145 | -0.13392 | -9.0684 | -5.0879 | -4.2069 | -2.1814
42810.4482 | 706 | 18.5444 | 18.564 | 18.5343 | 18.5346 | 17.8063 | 16.3929 | 14.436 | 16.6118 | 17.1183 | 17.2149 | 17.2271 | 16.738 | 15.7605 | 14.3768 | 14.9132 | 14.9933 | 15.8426 | 13.3601 | 13.8353 | 20.6466 |  |  |  | 16.6499 | 17.1389 | 29.5977 | 355.1677 | 307.2638 | 464.2044 | 17.25 | 17.0098 | 24.9026 | 16.854 | 17.0401 | 26.5554 | 158.4802 | 605.3391 |  | 241.8586 | 357.615 | 343.488 | 385.3707 |  | 11.2073 | 17.2069 | 13.0975 | 19.2303 | 21.9552 | 42.146 | 270.5446 | 5.3859 | 9.7975 | 5.8403 | 14.4092 | 9.5109 | 42.645 | 46.9602 | 43.2117 | 14.7952 |  |  | -1.3942 | 0.40487 | -0.022464 | -0.24773 | 0.7795 | 0.075108 | 0.7983 | 2.0224 | 0.10296 | -0.63167 | 7.0849 | 0.0088218 | 0.0089056 | 0.6496 | 16.2492 | 16.6234 | 17.1521 | 17.468 | 17.4119 | 16.3455 | 14.6765 | 16.7518 | 17.0927 | 17.386 | 17.4278 | 17.1199 | 16.2734 | 14.4626 | 153.0667 | 45.9187 | 92.513 | 55.1944 | 50.507 | 71.0289 | 37.3895 | 15.8426 | 15.6655 | 15.9885 | 14.4563 | 16.8872 | 21.8324 |  |  |  | 117.7753 | 376.3081 | 315.1353 | 246.2974 | 3.9568 | 2.6943 | 122.7423 |  |  | 15.4365 |  |  | 17.0041 | 18.1007 | 37.5156 | 16.3763 | 16.6103 | 24.2251 | 486.7789 | 739.7073 | 264.2453 | 273.4732 | 295.2393 |  | 137.353 | 259.9718 | 110.8388 | 358.5207 | 226.4848 | 393.8575 |  | 170.6034 |  |  | 51.4048 | 76.5738 | 202.468 | [6 empty] | 285.3709 |  |  | 131.674 |  |  | 56.3379 | 246.7553 | 572.0201 | 24.0293 | 186.4946 | 401.725 | 39.8413 | 193.6878 | 559.4009 | 114.6746 | 346.0429 | 34.1066 | 266.915 | 59.0078 | 301.9357 | 27.5045 | 172.3798 | 353.0701 | 83.7187 | 189.9696 | 396.8609 | 38.9848 | 171.6348 | 417.1899 | 38.9358 | 259.5503 | 84.8265 | 240.3156 | 54.2503 | 343.3482 | 14.6122 | 18.386 | 2.2767 | 0.082907 | -38.2417 | 3.1242 | 1406.59 | 48.79 | -2.2344 | 0.7556 | -0.17798 | -0.59105 | 1.0925 | 0.33913 | 1.1056 | -2.7756 | -2.9099 | -0.13426 | -8.3197 | -5.5975 | -4.3345 | -2.2458
42810.4482 | 707 | 18.5405 | 18.5641 | 18.5333 | 18.5267 | 17.8099 | 16.3901 | 14.4321 | 16.6048 | 17.1149 | 17.2149 | 17.2284 | 16.7343 | 15.7567 | 14.3834 | 14.8983 | 14.9963 | 15.8409 | 13.3576 | 13.8302 | 20.6796 |  |  |  | 16.641 | 17.1367 | 29.6611 | 359.7122 | 311.1495 | 463.2225 | 17.2458 | 17.0235 | 24.9567 | 16.8536 | 17.0543 | 26.605 | 160.7802 | 605.0534 |  | 245.5148 | 362.96 | 349.305 | 390.0154 |  | 11.3823 | 17.5635 | 13.2515 | 19.4981 | 22.3147 | 42.98 | 274.4966 | 5.3949 | 9.8671 | 5.9813 | 14.5701 | 9.5154 | 42.6573 | 46.9691 | 43.2169 | 14.7932 |  |  | -0.42165 | 0.38121 | 0.064276 | 0.06111 | 0.56594 | 0.35636 | 0.91264 | 2.4896 | -0.09203 | 0.85497 | 7.3369 | 0.0085491 | 0.0084883 | 0.67211 | 16.2593 | 16.6238 | 17.1489 | 17.4678 | 17.4117 | 16.345 | 14.679 | 16.7623 | 17.0922 | 17.3889 | 17.4256 | 17.1318 | 16.2836 | 14.4569 | 149.3924 | 46.1661 | 92.423 | 57.8867 | 52.2687 | 71.8472 | 37.7366 | 15.8436 | 15.6792 | 15.9972 | 14.4624 | 16.9179 | 21.8821 |  |  |  | 119.6666 | 383.3975 | 322.3791 | 250.6986 | 5.5189 | 2.7681 | 124.5663 |  |  | 15.5852 |  |  | 16.9807 | 18.1026 | 37.7859 | 16.3667 | 16.5947 | 24.2595 | 498.8665 | 744.3785 | 266.904 | 276.1873 | 301.4503 |  | 139.7672 | 262.2132 | 112.1893 | 361.7516 | 229.577 | 398.4405 |  | 172.4588 |  |  | 52.7675 | 78.2954 | 206.7781 | [6 empty] | 290.786 |  |  | 133.7331 |  |  | 57.6939 | 251.5985 | 579.9452 | 24.5322 | 188.82 | 407.8911 | 40.9647 | 197.0223 | 564.0789 | 117.6145 | 352.2625 | 35.0676 | 270.6917 | 60.7666 | 306.2765 | 28.1755 | 174.8408 | 355.4435 | 85.0688 | 193.977 | 400.8926 | 39.9892 | 175.8515 | 423.9268 | 39.8549 | 262.6442 | 86.5005 | 244.0532 | 55.6509 | 348.2265 | 15.2217 | 18.3722 | 2.2924 | 0.082292 | -38.3162 | 3.1242 | 1452.52 | 50.11 | -1.228 | 0.73364 | 0.30125 | 0.29374 | 0.93215 | 0.73968 | 1.1837 | -2.8429 | -2.9172 | -0.049824 | -7.8129 | -5.5466 | -4.3573 | -2.2898
42810.4482 | 708 | 18.5427 | 18.5593 | 18.5246 | 18.5259 | 17.8018 | 16.3935 | 14.4331 | 16.6053 | 17.1085 | 17.2028 | 17.2229 | 16.7364 | 15.7564 | 14.3812 | 14.9124 | 14.9956 | 15.8498 | 13.3641 | 13.8363 | 20.7145 |  |  |  | 16.6418 | 17.1451 | 29.7208 | 364.2492 | 315.249 | 469.7594 | 17.2429 | 17.0266 | 24.9935 | 16.8462 | 17.055 | 26.6517 | 163.2485 | 615.7204 |  | 249.2855 | 368.1174 | 353.986 | 393.0891 |  | 11.5629 | 17.9252 | 13.4199 | 19.8732 | 22.7716 | 43.6536 | 278.5486 | 5.42 | 9.9337 | 6.1029 | 14.7518 | 9.5283 | 42.6689 | 46.9964 | 43.2263 | 14.7986 |  |  | -0.90726 | 0.24256 | -0.17228 | -0.32199 | 0.4194 | 0.24727 | 0.39286 | 2.0842 | -0.098452 | 0.7977 | 7.1948 | 0.0082829 | 0.008232 | 0.69081 | 16.2636 | 16.6211 | 17.1512 | 17.4682 | 17.4081 | 16.3429 | 14.6848 | 16.7584 | 17.0935 | 17.3867 | 17.4262 | 17.12 | 16.2736 | 14.4563 | 152.9849 | 48.5708 | 94.2274 | 58.0265 | 53.9994 | 72.8114 | 38.1204 | 15.8455 | 15.675 | 15.992 | 14.4597 | 16.9305 | 21.9252 |  |  |  | 121.4889 | 392.557 | 327.9693 | 255.1479 | 4.7853 | 3.5499 | 127.0369 |  |  | 15.7669 |  |  | 16.9995 | 18.1133 | 38.0874 | 16.3715 | 16.6116 | 24.3182 | 508.9888 | 749.2946 | 269.5705 | 279.3173 | 307.8373 |  | 142.6662 | 265.6407 | 113.9041 | 368.5079 | 233.3643 | 404.8528 |  | 174.7071 |  |  | 54.1637 | 80.3764 | 211.1612 | [6 empty] | 296.6251 |  |  | 136.5018 |  |  | 59.0459 | 256.0126 | 588.4718 | 25.1333 | 190.9721 | 413.9049 | 42.1558 | 200.738 | 571.0068 | 120.3115 | 358.944 | 35.9475 | 274.047 | 62.5949 | 310.9935 | 28.8408 | 177.296 | 357.4931 | 86.4398 | 198.4862 | 404.5422 | 40.921 | 179.3805 | 429.1101 | 40.8296 | 265.686 | 88.1808 | 247.754 | 57.1157 | 352.9496 | 16.1472 | 18.3523 | 2.3065 | 0.080924 | -38.368 | 3.1242 | 1512.73 | 48.73 | -1.8093 | 0.58557 | -0.49351 | -0.67466 | 0.8033 | 0.61681 | 0.77746 | -2.893 | -2.9424 | -0.02192 | -8.0959 | -5.7018 | -4.328 | -2.3375
42810.4482 | 709 | 18.5448 | 18.5636 | 18.5356 | 18.5323 | 17.808 | 16.3918 | 14.4369 | 16.6098 | 17.1192 | 17.2067 | 17.227 | 16.7357 | 15.7564 | 14.3842 | 14.9172 | 15.0018 | 15.8582 | 13.367 | 13.8319 | 20.7514 |  |  |  | 16.6406 | 17.1561 | 29.7988 | 369.4024 | 319.9684 | 482.6657 | 17.237 | 17.0287 | 25.0663 | 16.8469 | 17.0546 | 26.7017 | 165.6262 | 619.8666 |  | 253.2941 | 373.9547 | 357.4281 | 395.7256 |  | 11.7214 | 18.2832 | 13.618 | 20.2658 | 23.2556 | 44.2917 | 281.5588 | 5.4691 | 9.9942 | 6.1773 | 14.9112 | 9.5364 | 42.6694 | 47.0111 | 43.2278 | 14.7944 |  |  | -0.66018 | 0.051343 | -0.06386 | -0.07557 | 0.45094 | -0.10231 | 0.76018 | 2.1512 | -0.3273 | 0.98085 | 7.5201 | 0.0079987 | 0.0079642 | 0.66067 | 16.2662 | 16.627 | 17.1467 | 17.4721 | 17.4072 | 16.3454 | 14.6752 | 16.7551 | 17.1001 | 17.3875 | 17.4275 | 17.1291 | 16.2797 | 14.454 | 154.0881 | 50.2918 | 98.9946 | 59.9604 | 56.4574 | 73.7092 | 38.5923 | 15.8454 | 15.6793 | 16.0047 | 14.4652 | 16.9531 | 21.9668 |  |  |  | 123.2272 | 402.4476 | 335.3744 | 258.286 | 5.432 | 3.85 | 129.0935 |  |  | 15.9661 |  |  | 16.9993 | 18.1334 | 38.4043 | 16.38 | 16.623 | 24.367 | 521.2083 | 751.7054 | 272.302 | 281.7694 | 313.5229 |  | 145.2389 | 267.4256 | 115.4397 | 373.6683 | 236.6492 | 416.1654 |  | 176.842 |  |  | 55.3932 | 82.5997 | 215.8284 | [6 empty] | 302.5099 |  |  | 139.6455 |  |  | 60.3603 | 260.5629 | 598.9535 | 25.7609 | 192.9359 | 418.9006 | 43.3404 | 204.2115 | 577.2612 | 123.4369 | 366.4529 | 36.8506 | 277.7853 | 64.3349 | 315.6265 | 29.5101 | 179.633 | 360.3791 | 87.7875 | 202.8631 | 410.2597 | 41.9401 | 183.244 | 434.1183 | 41.8276 | 268.9627 | 89.9958 | 252.0622 | 58.6444 | 357.124 | 14.4837 | 18.3348 | 2.3239 | 0.082704 | -38.2777 | 3.1242 | 1578.89 | 49.22 | -1.5567 | 0.26957 | -0.30064 | -0.32705 | 0.8338 | -0.39716 | 1.0826 | -2.9371 | -2.929 | 0.023744 | -8.1103 | -6.1759 | -4.29 | -2.352
42810.4483 | 710 | 18.545 | 18.5622 | 18.5381 | 18.5295 | 17.8108 | 16.3829 | 14.4372 | 16.6059 | 17.1148 | 17.2131 | 17.2192 | 16.7314 | 15.7525 | 14.383 | 14.9135 | 15.0005 | 15.8515 | 13.3648 | 13.8254 | 20.785 |  |  |  | 16.6437 | 17.1565 | 29.8647 | 375.2661 | 324.7348 | 490.0087 | 17.2458 | 17.0387 | 25.1255 | 16.8527 | 17.0676 | 26.7586 | 168.1916 | 626.9279 |  | 257.2443 | 378.925 | 360.878 | 400.4675 |  | 11.9376 | 18.7745 | 13.8961 | 20.8421 | 23.8853 | 45.0532 | 286.1517 | 5.5665 | 10.0854 | 6.241 | 15.1155 | 9.5574 | 42.686 | 47.0228 | 43.2395 | 14.8007 |  |  | -0.45056 | 0.28265 | 0.012364 | -0.27467 | 0.77228 | 0.78611 | 0.44346 | 2.2137 | 0.6599 | 0.66636 | 8.0176 | 0.0077425 | 0.0077244 | 0.61776 | 16.2638 | 16.6156 | 17.1444 | 17.4667 | 17.407 | 16.3406 | 14.6686 | 16.7507 | 17.0868 | 17.3855 | 17.4228 | 17.1301 | 16.2761 | 14.4513 | 155.754 | 54.6846 | 101.8113 | 63.444 | 57.8156 | 74.6616 | 39.0265 | 15.8594 | 15.6852 | 16.0107 | 14.4681 | 16.9773 | 22.0119 |  |  |  | 125.0032 | 414.0572 | 342.8909 | 260.5968 | 6.4239 | 2.67 | 131.6882 |  |  | 16.1695 |  |  | 16.9945 | 18.137 | 38.7325 | 16.376 | 16.616 | 24.4174 | 530.0738 | 759.0872 | 275.9512 | 285.1566 | 316.9333 |  | 147.7752 | 276.1869 | 116.9461 | 379.7108 | 240.0332 | 436.8944 |  | 179.2175 |  |  | 56.5405 | 84.473 | 220.1278 | [6 empty] | 308.1107 |  |  | 142.7815 |  |  | 61.7468 | 265.4842 | 606.5221 | 26.3933 | 195.5198 | 423.4085 | 44.5054 | 207.5393 | 583.4574 | 126.6788 | 373.3519 | 37.8308 | 281.4951 | 66.0537 | 319.3918 | 30.1579 | 181.9366 | 365.0704 | 89.2826 | 207.4857 | 416.2899 | 43.0764 | 186.7662 | 439.6217 | 42.8517 | 272.3239 | 91.8117 | 256.2092 | 60.1345 | 361.8421 | 17.163 | 18.3157 | 2.3404 | 0.082675 | -38.3649 | 3.1242 | 1663.75 | 49.85 | -1.2923 | 0.63303 | 0.1324 | -0.62404 | 1.0925 | 1.1022 | 0.82784 | -2.9189 | -3.1103 | 0.052603 | -8.1805 | -6.4376 | -4.3009 | -2.3416
42810.4483 | 711 | 18.5422 | 18.5572 | 18.5357 | 18.5275 | 17.8016 | 16.3851 | 14.4309 | 16.6055 | 17.1117 | 17.2069 | 17.22 | 16.7312 | 15.746 | 14.3755 | 14.9089 | 15.0007 | 15.8547 | 13.3624 | 13.8334 | 20.8191 |  |  |  | 16.6466 | 17.1605 | 29.9332 | 380.2098 | 329.379 | 489.7138 | 17.2468 | 17.0426 | 25.17 | 16.857 | 17.08 | 26.8198 | 170.8927 | 634.74 |  | 261.4039 | 383.453 | 364.6501 | 406.2005 |  | 12.1562 | 19.2187 | 14.1651 | 21.4394 | 24.5696 | 45.826 | 289.8873 | 5.5952 | 10.1554 | 6.2506 | 15.2906 | 9.561 | 42.6903 | 47.0296 | 43.2386 | 14.7974 |  |  | -0.60236 | 0.32667 | 0.07676 | -0.19779 | 0.61785 | 0.31036 | 0.54662 | 2.4962 | -0.13367 | 1.4292 | 8.083 | 0.0075108 | 0.007501 | 0.59461 | 16.2669 | 16.6222 | 17.1453 | 17.4656 | 17.4087 | 16.339 | 14.6723 | 16.7545 | 17.0845 | 17.3921 | 17.4209 | 17.1236 | 16.276 | 14.4561 | 160.8906 | 53.2804 | 99.4489 | 61.6227 | 57.3605 | 75.7148 | 39.4288 | 15.8492 | 15.6916 | 16.0149 | 14.4713 | 16.9906 | 22.0542 |  |  |  | 126.9254 | 426.8905 | 350.354 | 263.7352 | 6.2211 | 2.2006 | 134.7467 |  |  | 16.4064 |  |  | 17.0015 | 18.1518 | 39.0654 | 16.3775 | 16.6312 | 24.457 | 538.6169 | 762.5019 | 281.7256 | 290.2528 | 322.9997 |  | 150.6252 | 285.2021 | 118.7811 | 386.6174 | 243.9893 | 453.5548 |  | 182.1988 |  |  | 57.6728 | 86.5344 | 224.1803 | [6 empty] | 314.3352 |  |  | 145.9253 |  |  | 63.1361 | 270.7827 | 611.0638 | 27.073 | 198.3036 | 428.9741 | 45.8236 | 210.9241 | 589.0207 | 130.0489 | 380.8033 | 38.9386 | 285.4463 | 67.9775 | 323.4971 | 30.79 | 184.4819 | 369.203 | 90.6978 | 211.6271 | 425.3229 | 44.3058 | 189.992 | 444.3969 | 43.8696 | 275.8551 | 93.6533 | 261.1624 | 61.7706 | 367.0744 | 18.4948 | 18.2967 | 2.3571 | 0.082588 | -38.2949 | 3.1242 | 1713.14 | 48.78 | -1.4939 | 0.68107 | 0.33014 | -0.52995 | 0.97834 | 0.69339 | 0.92021 | -2.9596 | -3.2849 | 0.093319 | -8.6241 | -6.1276 | -4.332 | -2.3477
42810.4483 | 712 | 18.5391 | 18.5595 | 18.5258 | 18.5257 | 17.8032 | 16.383 | 14.4239 | 16.5992 | 17.1025 | 17.2035 | 17.212 | 16.7307 | 15.7428 | 14.374 | 14.9069 | 15.0018 | 15.8625 | 13.3607 | 13.8279 | 20.857 |  |  |  | 16.6545 | 17.1748 | 30.0063 | 384.6756 | 334.1091 | 491.0539 | 17.2468 | 17.0511 | 25.227 | 16.8624 | 17.088 | 26.8838 | 173.5007 | 637.8089 |  | 265.6745 | 389.6797 | 368.0046 | 411.7623 |  | 12.3846 | 19.7133 | 14.5181 | 22.0548 | 25.2736 | 46.541 | 293.1506 | 5.6014 | 10.2403 | 6.2566 | 15.507 | 9.5679 | 42.7077 | 47.0381 | 43.2474 | 14.7922 |  |  | -0.95194 | 0.29316 | 0.001192 | -0.81942 | 0.64217 | 0.50815 | 1.2504 | 2.4916 | -0.046494 | -0.008145 | 8.5857 | 0.007294 | 0.0073383 | 0.54655 | 16.2737 | 16.6261 | 17.1439 | 17.4675 | 17.4111 | 16.3492 | 14.68 | 16.7496 | 17.088 | 17.3917 | 17.4172 | 17.1226 | 16.2699 | 14.4597 | 164.9928 | 53.5721 | 99.498 | 60.0897 | 56.5713 | 76.8859 | 39.8072 | 15.8469 | 15.6952 | 16.0236 | 14.4678 | 17.0106 | 22.1029 |  |  |  | 129.2838 | 443.4849 | 360.4268 | 269.7868 | 6.9006 | 2.9775 | 137.0924 |  |  | 16.6611 |  |  | 16.9962 | 18.1571 | 39.4061 | 16.3834 | 16.6393 | 24.507 | 546.0543 | 764.4718 | 285.5425 | 294.2823 | 330.4699 |  | 153.4816 | 290.8712 | 120.6461 | 395.7676 | 248.0888 | 468.1033 |  | 185.1437 |  |  | 58.8071 | 88.6672 | 228.622 | [6 empty] | 321.9472 |  |  | 149.5174 |  |  | 64.5888 | 276.0813 | 616.81 | 27.813 | 201.7836 | 436.3196 | 47.1929 | 214.5831 | 595.7784 | 133.2973 | 387.6782 | 40.0544 | 290.0527 | 69.9106 | 327.6494 | 31.4927 | 187.5606 | 372.1833 | 92.3197 | 215.6692 | 436.6534 | 45.4884 | 193.3905 | 450.2492 | 44.9904 | 279.4318 | 95.5601 | 265.6804 | 63.4153 | 372.167 | 17.213 | 18.2755 | 2.3911 | 0.081604 | -38.2122 | 3.1242 | 1762.07 | 49.62 | -1.8796 | 0.64573 | 0.041175 | -1.0796 | 0.99852 | 0.88823 | 1.3933 | -3.0379 | -3.3649 | 0.083147 | -8.9385 | -6.0884 | -4.3618 | -2.4157
42810.4483 | 713 | 18.5441 | 18.5663 | 18.5285 | 18.5313 | 17.8129 | 16.3886 | 14.4315 | 16.5988 | 17.1123 | 17.204 | 17.2131 | 16.7351 | 15.745 | 14.3716 | 14.9139 | 15.0041 | 15.8676 | 13.3629 | 13.8294 | 20.8975 |  |  |  | 16.6632 | 17.1833 | 30.0813 | 389.89 | 338.7086 | 500.436 | 17.2586 | 17.0532 | 25.3025 | 16.8548 | 17.0977 | 26.9604 | 176.3355 | 636.8003 |  | 269.8357 | 396.7907 | 372.0277 | 415.0274 |  | 12.6396 | 20.2545 | 14.8367 | 22.6488 | 26.0479 | 49.1256 | 297.8119 | 5.5836 | 10.3386 | 6.3021 | 15.7374 | 9.5814 | 42.6989 | 47.0463 | 43.2482 | 14.7959 |  |  | -0.87309 | 0.099311 | -0.080288 | -0.23656 | 1.0726 | 0.86628 | 1.025 | 2.4193 | 0.13312 | 1.0098 | 9.2146 | 0.0070837 | 0.0070738 | 0.55459 | 16.2777 | 16.6269 | 17.1533 | 17.4705 | 17.4097 | 16.3454 | 14.6876 | 16.7469 | 17.0877 | 17.3905 | 17.4205 | 17.1218 | 16.2792 | 14.4647 | 177.0112 | 51.671 | 99.1865 | 59.8143 | 57.7865 | 78.2126 | 40.1376 | 15.8512 | 15.6926 | 16.0234 | 14.4878 | 17.0312 | 22.1487 |  |  |  | 131.4112 | 458.4089 | 372.876 | 276.3565 | 9.3816 | 1.8726 | 140.153 |  |  | 16.9338 |  |  | 16.9979 | 18.1547 | 39.7433 | 16.3803 | 16.6321 | 24.5528 | 558.1303 | 767.306 | 290.255 | 298.2602 | 335.9241 |  | 156.3362 | 296.223 | 122.4277 | 403.7477 | 252.0685 | 485.3032 |  | 187.8694 |  |  | 59.9793 | 90.8425 | 234.2787 | [6 empty] | 329.3379 |  |  | 153.1505 |  |  | 66.0712 | 281.3967 | 626.901 | 28.5892 | 205.7913 | 443.3261 | 48.61 | 218.3019 | 602.1052 | 136.7426 | 395.0136 | 41.2467 | 294.4274 | 71.9446 | 332.2173 | 32.2579 | 190.6399 | 375.5137 | 93.9731 | 220.4 | 447.2363 | 46.6805 | 197.2918 | 455.5711 | 46.185 | 283.2589 | 97.5999 | 269.8438 | 65.1935 | 375.5357 | 18.8143 | 18.2576 | 2.4143 | 0.083507 | -38.2162 | 3.1243 | 1838.22 | 49.65 | -1.8111 | 0.37618 | -0.33824 | -0.58059 | 1.2957 | 1.1644 | 1.2666 | -3.0593 | -3.4393 | 0.10131 | -10.1134 | -6.0148 | -4.3159 | -2.5074
42810.4483 | 714 | 18.5436 | 18.5647 | 18.5345 | 18.5289 | 17.8057 | 16.3833 | 14.4347 | 16.6023 | 17.1147 | 17.2089 | 17.2169 | 16.725 | 15.7539 | 14.3766 | 14.9132 | 15.0041 | 15.87 | 13.3641 | 13.8203 | 20.9308 |  |  |  | 16.656 | 17.1919 | 30.1536 | 396.1171 | 344.8213 | 511.0362 | 17.2418 | 17.0514 | 25.3298 | 16.8504 | 17.0897 | 27.0264 | 179.2357 | 648.0371 |  | 274.5769 | 404.0985 | 375.5554 | 424.6295 |  | 12.8601 | 20.7198 | 15.1301 | 23.2177 | 26.78 | 53.9914 | 301.7254 | 5.5992 | 10.4241 | 6.358 | 15.928 | 9.5974 | 42.6959 | 47.0445 | 43.2539 | 14.7837 |  |  | -0.87506 | 0.49227 | -0.11643 | -0.26219 | 1.0975 | 1.4702 | 1.2313 | 2.5389 | -0.047662 | 0.81217 | 9.8294 | 0.0069129 | 0.0069145 | 0.52267 | 16.2835 | 16.6273 | 17.1477 | 17.4687 | 17.4124 | 16.3464 | 14.6762 | 16.7458 | 17.0886 | 17.3889 | 17.4212 | 17.1232 | 16.2861 | 14.4597 | 191.1333 | 52.5153 | 96.1565 | 57.295 | 56.266 | 79.7766 | 40.4691 | 15.8556 | 15.6952 | 16.0282 | 14.4856 | 17.056 | 22.1865 |  |  |  | 133.6536 | 475.7229 | 386.9292 | 284.8416 | 7.4754 | 2.4084 | 143.8675 |  |  | 17.1963 |  |  | 17.0017 | 18.1736 | 40.1082 | 16.382 | 16.6412 | 24.6063 | 567.9215 | 772.8332 | 296.1669 | 303.3248 | 341.7704 |  | 159.4201 | 305.1997 | 124.4011 | 410.8806 | 256.4832 | 501.7066 |  | 191.0207 |  |  | 61.5806 | 93.0744 | 240.1807 | [6 empty] | 338.6867 |  |  | 156.3688 |  |  | 67.706 | 286.9825 | 637.4477 | 29.3606 | 209.4465 | 452.5031 | 50.1223 | 222.4262 | 608.7212 | 140.3833 | 402.7751 | 42.5829 | 299.2123 | 74.0726 | 337.284 | 32.9312 | 193.6318 | 380.7143 | 95.6799 | 225.8949 | 458.1791 | 47.9303 | 201.2237 | 461.4423 | 47.3391 | 286.811 | 99.7 | 274.8599 | 67.0776 | 378.5729 | 20.3075 | 18.2351 | 2.4312 | 0.083551 | -38.2239 | 3.1242 | 1891.13 | 48.91 | -1.8256 | 0.83819 | -0.40764 | -0.61172 | 1.3205 | 1.5283 | 1.3987 | -3.0801 | -3.6059 | 0.17272 | -11.4933 | -5.639 | -4.4417 | -2.6468
42810.4483 | 715 | 18.5347 | 18.5668 | 18.5275 | 18.5211 | 17.8012 | 16.3797 | 14.4266 | 16.597 | 17.1012 | 17.2002 | 17.21 | 16.7257 | 15.7386 | 14.3729 | 14.9056 | 14.9978 | 15.8653 | 13.3586 | 13.8023 | 20.9596 |  |  |  | 16.6508 | 17.1949 | 30.2195 | 403.0306 | 351.3009 | 524.1941 | 17.2545 | 17.0616 | 25.3876 | 16.8601 | 17.0942 | 27.1052 | 182.1047 | 661.5396 |  | 279.071 | 410.4429 | 379.2632 | 428.5034 |  | 13.1551 | 21.3339 | 15.5053 | 23.9241 | 27.5663 | 62.2291 | 306.1066 | 5.6856 | 10.5265 | 6.4411 | 16.1849 | 9.6147 | 42.7002 | 47.058 | 43.2705 | 14.7852 |  |  | -0.5465 | 0.16502 | -0.23537 | -0.46852 | 2.1312 | 1.7225 | 1.8392 | 2.9687 | -0.57075 | 1.2213 | 10.3216 | 0.0066517 | 0.0066796 | 0.50365 | 16.2865 | 16.626 | 17.1475 | 17.464 | 17.4084 | 16.3492 | 14.6751 | 16.7436 | 17.0934 | 17.384 | 17.4205 | 17.1239 | 16.2809 | 14.4547 | 192.5727 | 53.5501 | 94.6671 | 55.907 | 52.8702 | 81.1657 | 40.8122 | 15.859 | 15.6927 | 16.0388 | 14.4852 | 17.0761 | 22.2344 |  |  |  | 136.0296 | 494.2629 | 397.8279 | 294.0039 | 6.6068 | 4.5129 | 147.7672 |  |  | 17.4687 |  |  | 17.0025 | 18.1888 | 40.4853 | 16.3833 | 16.6501 | 24.6623 | 576.827 | 773.1114 | 302.331 | 309.3168 | 346.9721 |  | 162.8976 | 316.2767 | 126.6967 | 421.7385 | 261.4538 | 523.367 |  | 194.8028 |  |  | 63.3804 | 95.5511 | 245.9124 | [6 empty] | 348.9129 |  |  | 159.7528 |  |  | 69.3823 | 292.874 | 646.699 | 30.2217 | 213.6778 | 461.3111 | 51.7042 | 227.3103 | 615.4254 | 144.0859 | 410.8267 | 44.01 | 304.0195 | 76.3935 | 343.2227 | 33.6125 | 196.8596 | 385.5046 | 97.689 | 232.1318 | 468.076 | 49.1713 | 205.5346 | 467.2884 | 48.5483 | 290.5924 | 102.0103 | 280.3195 | 69.0276 | 383.758 | 20.8532 | 18.2135 | 2.4693 | 0.082292 | -38.2715 | 3.1243 | 1914.49 | 49.99 | -1.4547 | 0.48581 | -0.58019 | -0.81858 | 1.8631 | 1.675 | 1.7308 | -3.0633 | -3.8168 | 0.17904 | -11.485 | -5.433 | -4.4088 | -2.7988
42810.4483 | 716 | 18.5419 | 18.5729 | 18.5362 | 18.5264 | 17.8076 | 16.3864 | 14.4346 | 16.6046 | 17.1089 | 17.2089 | 17.2205 | 16.7264 | 15.7475 | 14.3765 | 14.9017 | 15.0059 | 15.8761 | 13.3622 | 13.802 | 20.9936 |  |  |  | 16.6576 | 17.1924 | 30.3047 | 409.3154 | 357.3244 | 526.3037 | 17.2582 | 17.0727 | 25.4523 | 16.8582 | 17.1072 | 27.1782 | 185.1611 | 676.1274 |  | 284.1178 | 417.146 | 383.2743 | 434.5395 |  | 13.3906 | 21.8844 | 15.8275 | 24.518 | 28.3481 | 70.4404 | 311.7615 | 5.6238 | 10.6136 | 6.465 | 16.4035 | 9.6211 | 42.6853 | 47.0532 | 43.2663 | 14.7808 |  |  | -0.39734 | 0.045431 | -0.25902 | -0.2957 | 2.3691 | 1.8 | 0.92906 | 3.5621 | 0.23373 | 0.41607 | 10.9584 | 0.0065137 | 0.0065367 | 0.47599 | 16.2762 | 16.613 | 17.1409 | 17.4644 | 17.4056 | 16.3463 | 14.6664 | 16.7358 | 17.0879 | 17.3838 | 17.4138 | 17.1154 | 16.2723 | 14.4523 | 196.0019 | 57.5126 | 106.3807 | 58.0381 | 54.6838 | 82.5912 | 41.3545 | 15.8588 | 15.6997 | 16.0409 | 14.4847 | 17.0986 | 22.285 |  |  |  | 138.65 | 513.1289 | 408.5776 | 302.5499 | 6.7237 | 4.5328 | 151.8081 |  |  | 17.8177 |  |  | 17.0046 | 18.2025 | 40.8654 | 16.3834 | 16.6572 | 24.7102 | 584.0399 | 774.597 | 307.9131 | 315.2889 | 353.3779 |  | 166.1712 | 323.1563 | 128.8205 | 433.6619 | 266.1623 | 551.4731 |  | 198.7383 |  |  | 65.135 | 98.343 | 251.8166 | [6 empty] | 359.2555 |  |  | 164.3984 |  |  | 71.1356 | 299.4222 | 655.3616 | 31.0731 | 218.0582 | 469.5026 | 53.3346 | 232.4083 | 622.3294 | 148.1811 | 417.8608 | 45.5479 | 309.9505 | 78.9002 | 351.0022 | 34.3939 | 200.2851 | 389.6544 | 100.0247 | 238.7374 | 477.4212 | 50.524 | 210.1725 | 474.7755 | 49.8469 | 294.6611 | 104.7781 | 285.6166 | 71.0591 | 391.2867 | 21.6382 | 18.1882 | 2.4878 | 0.081192 | -38.2189 | 3.1243 | 1931.65 | 49.2 | -1.2421 | 0.25514 | -0.60922 | -0.65092 | 1.9883 | 1.7331 | 1.2451 | -3.0881 | -3.9179 | 0.14396 | -11.6931 | -6.6704 | -4.4255 | -2.9222
42810.4483 | 717 | 18.5468 | 18.5669 | 18.5346 | 18.5268 | 17.8101 | 16.3818 | 14.4349 | 16.6031 | 17.1171 | 17.2063 | 17.2212 | 16.7287 | 15.7472 | 14.3749 | 14.9035 | 15.0012 | 15.8748 | 13.3675 | 13.8031 | 21.0364 |  |  |  | 16.6565 | 17.2076 | 30.3897 | 414.4506 | 367.8418 | 525.307 | 17.257 | 17.0678 | 25.5175 | 16.859 | 17.1171 | 27.2587 | 188.3371 | 685.5134 |  | 289.3176 | 424.1053 | 386.8812 | 437.7872 |  | 13.6968 | 22.5275 | 16.2116 | 25.2368 | 29.3396 | 79.5111 | 317.0603 | 5.4597 | 10.7116 | 6.5234 | 16.6516 | 9.6314 | 42.6825 | 47.05 | 43.2699 | 14.7759 |  |  | -0.46831 | 0.15648 | -0.11774 | -0.757 | 2.3296 | 1.3138 | 0.96586 | 3.7224 | 0.12281 | 1.6629 | 11.2608 | 0.0063017 | 0.0062344 | 0.51131 | 16.2861 | 16.6212 | 17.1435 | 17.4536 | 17.4081 | 16.3417 | 14.6673 | 16.7369 | 17.0906 | 17.3767 | 17.4172 | 17.1101 | 16.2687 | 14.4474 | 198.236 | 58.5947 | 112.9222 | 60.6453 | 55.5012 | 84.024 | 41.8811 | 15.8574 | 15.6973 | 16.0416 | 14.4841 | 17.1174 | 22.332 |  |  |  | 141.6335 | 534.8498 | 425.9238 | 308.1914 | 6.4587 | 4.5334 | 156.1551 |  |  | 18.1934 |  |  | 17.0075 | 18.2165 | 41.26 | 16.382 | 16.6621 | 24.7703 | 590.9848 | 777.7537 | 315.4966 | 322.5396 | 362.019 |  | 169.48 | 331.7059 | 131.1941 | 441.1527 | 271.2317 | 574.0993 |  | 203.2125 |  |  | 66.9033 | 101.4884 | 258.366 | [6 empty] | 376.0809 |  |  | 169.3144 |  |  | 73.0731 | 306.6697 | 661.4858 | 31.919 | 222.3233 | 477.1877 | 55.0817 | 238.4852 | 630.6458 | 152.6717 | 425.1536 | 47.2341 | 315.995 | 81.6053 | 360.9454 | 35.292 | 204.4521 | 393.7554 | 102.6535 | 245.5749 | 489.4565 | 52.0841 | 214.6931 | 481.4358 | 51.2569 | 299.3995 | 107.9493 | 292.4654 | 73.2863 | 396.7256 | 22.5744 | 18.1676 | 2.5164 | 0.083783 | -38.2205 | 3.1243 | 1964.85 | 49.04 | -1.3476 | 0.47403 | -0.41119 | -1.0426 | 1.9975 | 1.5001 | 1.2862 | -3.1719 | -4.0542 | 0.2596 | -11.7674 | -7.335 | -4.3575 | -2.9483
42810.4483 | 718 | 18.5415 | 18.5702 | 18.5319 | 18.5264 | 17.8044 | 16.3818 | 14.4304 | 16.5998 | 17.1123 | 17.2036 | 17.2157 | 16.7288 | 15.7476 | 14.3663 | 14.8975 | 15.0036 | 15.8691 | 13.3631 | 13.7892 | 21.0705 |  |  |  | 16.6569 | 17.2122 | 30.4655 | 419.1308 | 379.4746 | 528.8975 | 17.2588 | 17.0757 | 25.5889 | 16.8648 | 17.122 | 27.3488 | 191.5002 | 696.3718 |  | 294.6922 | 432.6291 | 390.0477 | 437.3048 |  | 14.0454 | 23.2724 | 16.6675 | 26.1099 | 30.5485 | 83.4316 | 321.6547 | 5.3461 | 10.8176 | 6.5429 | 16.9291 | 9.6403 | 42.6626 | 47.0462 | 43.28 | 14.7701 |  |  | -0.72655 | 0.3569 | -0.65461 | -1.0139 | 2.4591 | 1.8546 | 1.416 | 3.7566 | 0.224 | 1.0761 | 11.0186 | 0.0061703 | 0.0062048 | 0.5276 | 16.2966 | 16.6258 | 17.1398 | 17.4653 | 17.4082 | 16.3458 | 14.6758 | 16.7457 | 17.0866 | 17.3784 | 17.4224 | 17.1211 | 16.2712 | 14.4503 | 200.6447 | 57.2061 | 116.181 | 62.3871 | 56.736 | 85.4042 | 42.3924 | 15.8595 | 15.7011 | 16.0438 | 14.4875 | 17.1386 | 22.3728 |  |  |  | 144.5944 | 555.3771 | 445.9629 | 314.7996 | 8.1849 | 5.092 | 161.756 |  |  | 18.5898 |  |  | 17.0089 | 18.2326 | 41.6765 | 16.3939 | 16.6761 | 24.8194 | 597.5901 | 780.3727 | 325.1211 | 331.6901 | 369.4419 |  | 173.5743 | 344.1918 | 134.1514 | 444.3468 | 277.5799 | 611.2912 |  | 209.2507 |  |  | 68.982 | 104.9898 | 265.4797 | [6 empty] | 408.5013 |  |  | 175.1224 |  |  | 75.2366 | 314.0777 | 667.459 | 32.9047 | 227.0364 | 483.7702 | 56.9124 | 244.225 | 639.8375 | 157.6136 | 432.1465 | 49.0203 | 321.8682 | 84.3146 | 369.12 | 36.3381 | 209.2911 | 400.6037 | 105.3245 | 251.7343 | 503.8449 | 53.6264 | 219.1902 | 486.0529 | 52.7777 | 304.8128 | 111.4916 | 301.201 | 75.5782 | 401.3072 | 22.939 | 18.14 | 2.5481 | 0.083963 | -38.2809 | 3.1243 | 2039.78 | 49.65 | -1.6823 | 0.7168 | -0.97076 | -1.2082 | 2.0636 | 1.7921 | 1.5659 | -3.1827 | -4.274 | 0.58358 | -11.8674 | -7.6366 | -4.185 | -3.0012
42810.4484 | 719 | 18.5444 | 18.5658 | 18.5371 | 18.531 | 17.8024 | 16.3855 | 14.429 | 16.5965 | 17.1105 | 17.2107 | 17.2115 | 16.7287 | 15.7511 | 14.3628 | 14.9036 | 15.0129 | 15.8842 | 13.3667 | 13.7977 | 21.1072 |  |  |  | 16.663 | 17.2275 | 30.5605 | 424.1856 | 390.4141 | 533.6388 | 17.2548 | 17.0887 | 25.6482 | 16.8602 | 17.1236 | 27.4284 | 194.6863 | 708.7346 |  | 300.2671 | 441.3093 | 392.855 | 440.2903 |  | 14.3703 | 23.9454 | 17.1088 | 26.9147 | 31.8919 | 88.3091 | 326.9964 | 5.3063 | 10.9191 | 6.5148 | 17.1796 | 9.6625 | 42.6431 | 47.0623 | 43.2918 | 14.7832 |  |  | -0.9112 | 0.23665 | -0.48704 | -0.54081 | 2.1824 | 2.1601 | 1.4429 | 4.8329 | -0.21833 | 1.3816 | 11.8531 | 0.0059633 | 0.005988 | 0.51981 | 16.3025 | 16.6328 | 17.1472 | 17.4721 | 17.4153 | 16.3544 | 14.672 | 16.7573 | 17.1029 | 17.3882 | 17.4281 | 17.1241 | 16.2837 | 14.4577 | 208.4893 | 59.9338 | 120.6592 | 61.9456 | 58.167 | 87.0098 | 42.9956 | 15.8604 | 15.7028 | 16.0495 | 14.4876 | 17.1651 | 22.423 |  |  |  | 147.8062 | 574.1181 | 466.8228 | 325.978 | 9.5312 | 5.7183 | 167.2875 |  |  | 18.9837 |  |  | 17.0098 | 18.23 | 42.1095 | 16.3796 | 16.6681 | 24.8731 | 605.8002 | 784.0551 | 334.4926 | 341.2915 | 376.5306 |  | 177.1821 | 356.3135 | 137.0032 | 454.7031 | 283.6981 | 629.9204 |  | 215.14 |  |  | 70.994 | 108.1989 | 272.364 | [6 empty] | 461.8534 |  |  | 180.6537 |  |  | 77.4821 | 322.2812 | 674.6807 | 33.9598 | 231.8802 | 489.104 | 58.7054 | 250.2617 | 646.5067 | 163.2282 | 439.6518 | 50.7543 | 328.9079 | 86.9108 | 376.9883 | 37.4586 | 213.7479 | 408.6735 | 108.3805 | 258.019 | 515.8746 | 55.2079 | 223.6743 | 492.4249 | 54.4219 | 310.0635 | 115.1955 | 309.8974 | 77.9943 | 409.0039 | 26.9228 | 18.1119 | 2.5637 | 0.083811 | -38.2577 | 3.1243 | 2111.35 | 48.97 | -1.8895 | 0.58434 | -0.8383 | -0.88336 | 1.9573 | 1.9473 | 1.5915 | -3.2055 | -4.4873 | 0.70154 | -12.5437 | -8.0629 | -4.1062 | -3.1688
42810.4484 | 720 | 18.5395 | 18.5636 | 18.5204 | 18.5258 | 17.8007 | 16.3853 | 14.4218 | 16.5932 | 17.1002 | 17.1972 | 17.2031 | 16.7252 | 15.7405 | 14.358 | 14.9046 | 15.0002 | 15.8823 | 13.3659 | 13.7922 | 21.1485 |  |  |  | 16.6583 | 17.2273 | 30.6218 | 431.4466 | 400.492 | 551.6132 | 17.2417 | 17.0854 | 25.6889 | 16.8535 | 17.1233 | 27.5109 | 197.9955 | 718.1977 |  | 305.9424 | 450.4233 | 397.1999 | 444.3241 |  | 14.8024 | 24.7988 | 17.6156 | 27.8382 | 33.4482 | 97.0324 | 334.208 | 5.3369 | 11.0513 | 6.5455 | 17.5032 | 9.6729 | 42.6216 | 47.0702 | 43.2887 | 14.7768 |  |  | -0.79818 | 0.16699 | -0.61124 | -0.28913 | 3.1359 | 1.4984 | 1.1669 | 4.4971 | 1.7734 | 1.4093 | 13.6073 | 0.005896 | 0.0058779 | 0.49457 | 16.3048 | 16.6285 | 17.1431 | 17.4678 | 17.411 | 16.3379 | 14.6767 | 16.7495 | 17.0987 | 17.3905 | 17.4212 | 17.1212 | 16.2757 | 14.4573 | 218.1552 | 59.399 | 131.4541 | 65.3755 | 62.0594 | 88.8163 | 43.7288 | 15.8465 | 15.69 | 16.0416 | 14.4866 | 17.1723 | 22.471 |  |  |  | 151.2295 | 589.4174 | 486.9725 | 340.0364 | 7.6735 | 5.3059 | 173.7899 |  |  | 19.4058 |  |  | 17.0073 | 18.2488 | 42.5571 | 16.3945 | 16.6866 | 24.9318 | 615.7363 | 787.7494 | 346.3773 | 354.3005 | 384.6192 |  | 180.9466 | 365.5071 | 139.8836 | 477.4716 | 290.3992 | 641.3423 |  | 220.9081 |  |  | 73.117 | 111.8943 | 281.0273 | [6 empty] | 480.6216 |  |  | 187.3187 |  |  | 79.8174 | 331.6575 | 687.1307 | 35.1215 | 237.8092 | 496.0463 | 60.7449 | 256.4693 | 653.3089 | 169.7519 | 450.4095 | 52.6304 | 335.6706 | 90.0144 | 388.1269 | 38.5097 | 219.5511 | 415.3941 | 111.3051 | 266.4004 | 528.707 | 57.0186 | 229.2157 | 497.9128 | 55.9269 | 315.3321 | 119.3936 | 318.3372 | 80.5728 | 414.5118 | 27.4043 | 18.0972 | 2.579 | 0.082777 | -38.2917 | 3.1243 | 2199.62 | 49.38 | -1.7881 | 0.49157 | -0.94047 | -0.64682 | 2.3744 | 1.6413 | 1.4484 | -3.2467 | -4.6172 | 0.52241 | -13.3977 | -9.1756 | -4.0486 | -3.4056
42810.4484 | 721 | 18.5399 | 18.5618 | 18.5263 | 18.5219 | 17.8021 | 16.3771 | 14.4251 | 16.5971 | 17.1012 | 17.203 | 17.2092 | 16.7208 | 15.7479 | 14.3628 | 14.9052 | 15.0132 | 15.8848 | 13.376 | 13.7946 | 21.1962 |  |  |  | 16.6594 | 17.2396 | 30.6854 | 440.7524 | 414.7356 | 574.9747 | 17.2551 | 17.0859 | 25.7549 | 16.8596 | 17.1313 | 27.6114 | 201.9303 | 738.4664 |  | 312.8778 | 461.2775 | 401.0356 | 454.5695 |  | 15.1454 | 25.5352 | 18.0448 | 28.7545 | 35.4917 | 104.9208 | 339.7709 | 5.4396 | 11.1665 | 6.6201 | 17.8051 | 9.6826 | 42.6124 | 47.0825 | 43.296 | 14.7908 |  |  | -0.53139 | 0.24191 | -0.92206 | -0.68471 | 2.601 | 1.9617 | 1.642 | 4.9459 | 0.26895 | 2.6269 | 14.5497 | 0.005707 | 0.0057399 | 0.44362 | 16.3024 | 16.6251 | 17.1416 | 17.4608 | 17.408 | 16.3384 | 14.6702 | 16.7489 | 17.0877 | 17.3869 | 17.4156 | 17.1181 | 16.273 | 14.4483 | 221.7613 | 57.3524 | 133.5433 | 68.2958 | 64.9922 | 90.4751 | 44.4104 | 15.8591 | 15.7092 | 16.0591 | 14.504 | 17.212 | 22.5338 |  |  |  | 155.5185 | 603.5402 | 513.4704 | 366.1526 | 8.04 | 4.8528 | 180.3793 |  |  | 19.9022 |  |  | 17.0149 | 18.2523 | 43.0262 | 16.3883 | 16.6956 | 24.9887 | 624.6688 | 791.2142 | 356.2012 | 365.4982 | 393.0273 |  | 185.4176 | 376.8415 | 143.4218 | 553.4733 | 299.0851 | 638.5751 |  | 227.5465 |  |  | 75.7172 | 116.2255 | 292.3142 | [6 empty] | 497.4157 |  |  | 194.3808 |  |  | 82.6061 | 342.3479 | 699.623 | 36.5281 | 245.264 | 506.8021 | 63.1346 | 263.7655 | 663.3039 | 177.237 | 463.4475 | 54.9599 | 344.188 | 93.5178 | 400.8338 | 40.0422 | 224.3046 | 421.5155 | 114.8959 | 273.9183 | 542.8353 | 58.9108 | 235.3636 | 508.2514 | 57.7991 | 321.9657 | 124.2458 | 327.4979 | 83.8278 | 423.1532 | 29.0475 | 18.0699 | 2.5971 | 0.084629 | -38.2346 | 3.1243 | 2252.61 | 50.02 | -1.4795 | 0.59238 | -1.1565 | -0.99662 | 2.1854 | 1.8979 | 1.7364 | -3.2597 | -4.7765 | -0.98666 | -13.5961 | -9.327 | -4.1294 | -3.9364
42810.4484 | 722 | 18.5353 | 18.5567 | 18.5286 | 18.5182 | 17.8019 | 16.3785 | 14.4202 | 16.5923 | 17.1029 | 17.2004 | 17.2057 | 16.7264 | 15.7441 | 14.3534 | 14.9072 | 15.016 | 15.8938 | 13.3745 | 13.7866 | 21.236 |  |  |  | 16.6611 | 17.2455 | 30.7296 | 452.8366 | 426.48 | 603.0397 | 17.2547 | 17.0878 | 25.8548 | 16.8567 | 17.1457 | 27.7229 | 205.7588 | 754.0553 |  | 319.2526 | 473.3998 | 407.1215 | 462.8728 |  | 15.5338 | 26.3561 | 18.517 | 29.6788 | 37.1537 | 115.0123 | 346.0256 | 5.5788 | 11.2927 | 6.658 | 18.1329 | 9.702 | 42.6147 | 47.098 | 43.3015 | 14.805 |  |  | -1.6288 | -0.10308 | -0.53567 | -0.84242 | 2.5458 | 2.0734 | 2.5272 | 6.0256 | 0.43689 | 2.4362 | 15.4359 | 0.0055888 | 0.0056167 | 0.37432 | 16.3104 | 16.627 | 17.1496 | 17.4631 | 17.4048 | 16.3438 | 14.6771 | 16.7543 | 17.0911 | 17.3836 | 17.4234 | 17.1263 | 16.2708 | 14.4512 | 219.4913 | 57.1584 | 131.9906 | 68.0674 | 62.7279 | 91.9852 | 45.0728 | 15.8505 | 15.7055 | 16.0605 | 14.5035 | 17.2282 | 22.5783 |  |  |  | 160.3253 | 615.3669 | 538.9468 | 387.2287 | 8.8403 | 5.0449 | 188.4793 |  |  | 20.368 |  |  | 17.0142 | 18.2585 | 43.5029 | 16.3818 | 16.6921 | 25.0463 | 629.7322 | 795.3633 | 368.1844 | 379.3551 | 402.8051 |  | 190.3115 | 388.2593 | 147.0295 | 659.9495 | 310.0057 | 638.0689 |  | 234.404 |  |  | 78.6845 | 120.9468 | 305.1149 | [6 empty] | 513.4538 |  |  | 202.0269 |  |  | 85.4905 | 352.5294 | 715.6602 | 38.1194 | 250.7244 | 516.964 | 65.5777 | 270.3975 | 675.0242 | 185.3598 | 476.4664 | 57.5141 | 352.1906 | 97.1679 | 411.2114 | 41.5781 | 229.383 | 429.7124 | 118.4817 | 281.2397 | 557.5349 | 61.0422 | 242.3391 | 521.5684 | 60.0696 | 328.5741 | 129.1216 | 334.9248 | 87.3603 | 430.2565 | 31.7139 | 18.0394 | 2.616 | 0.084709 | -38.1868 | 3.1243 | 2307.92 | 48.98 | -2.6327 | -0.38722 | -0.88271 | -1.107 | 2.1907 | 1.977 | 2.1827 | -3.2866 | -4.9335 | -3.1634 | -13.1595 | -9.0761 | -4.1595 | -4.301
42810.4484 | 723 | 18.5386 | 18.5625 | 18.5282 | 18.5255 | 17.8004 | 16.3893 | 14.4282 | 16.5947 | 17.102 | 17.2071 | 17.2076 | 16.7287 | 15.745 | 14.3622 | 14.9124 | 15.0185 | 15.8996 | 13.3768 | 13.7954 | 21.2745 |  |  |  | 16.6684 | 17.2548 | 30.7602 | 469.0612 | 437.8721 | 638.8904 | 17.2503 | 17.0952 | 25.9395 | 16.8573 | 17.1447 | 27.825 | 209.8257 | 789.3023 |  | 326.5874 | 486.8929 | 414.3713 | 469.2796 |  | 16.0163 | 27.3791 | 19.1295 | 30.8005 | 39.7064 | 124.5979 | 353.6141 | 5.7904 | 11.4607 | 6.7511 | 18.5391 | 9.7103 | 42.6189 | 47.1011 | 43.2944 | 14.8202 |  |  | -0.73115 | 0.088799 | -0.82874 | -0.69786 | 3.1149 | 2.8619 | 2.9044 | 6.247 | 0.9195 | 2.0139 | 15.9263 | 0.0054048 | 0.0054639 | 0.32905 | 16.3055 | 16.6149 | 17.1358 | 17.4595 | 17.3964 | 16.3437 | 14.6656 | 16.7477 | 17.0878 | 17.3766 | 17.4176 | 17.1156 | 16.2616 | 14.4501 | 221.9163 | 56.2046 | 131.089 | 68.8295 | 61.2487 | 93.6781 | 45.7078 | 15.8519 | 15.7061 | 16.0659 | 14.5064 | 17.2568 | 22.638 |  |  |  | 165.2605 | 626.3474 | 564.3587 | 404.7321 | 10.7368 | 3.0775 | 196.6469 |  |  | 20.8823 |  |  | 17.0187 | 18.2788 | 44.0331 | 16.3996 | 16.7034 | 25.1197 | 635.9833 | 798.9827 | 380.7067 | 394.3386 | 418.2974 |  | 195.2674 | 406.9934 | 150.9233 | 731.6086 | 323.4938 | 645.3968 |  | 241.282 |  |  | 81.6011 | 126.383 | 324.0388 | [6 empty] | 532.1383 |  |  | 211.4554 |  |  | 88.4664 | 363.2424 | 732.1434 | 39.7427 | 257.1973 | 525.9759 | 68.1195 | 277.9768 | 685.7704 | 195.0204 | 489.6474 | 60.6262 | 362.1413 | 101.2594 | 425.0463 | 43.0973 | 234.9748 | 440.2817 | 122.261 | 288.2799 | 571.7189 | 63.3433 | 249.2521 | 533.0244 | 62.8031 | 335.2133 | 134.2092 | 344.2478 | 90.8853 | 440.0611 | 42.492 | 18.0053 | 2.657 | 0.083117 | -38.2076 | 3.1243 | 2377.22 | 49.57 | -1.7996 | 0.36001 | -1.0998 | -1.0092 | 2.453 | 2.3513 | 2.3686 | -3.4656 | -5.2793 | -4.1512 | -13.222 | -8.9007 | -4.1218 | -4.5574
42810.4484 | 724 | 18.5418 | 18.5631 | 18.5327 | 18.5273 | 17.7983 | 16.3838 | 14.4314 | 16.5926 | 17.104 | 17.2046 | 17.2119 | 16.7303 | 15.7427 | 14.3654 | 14.9101 | 15.0109 | 15.894 | 13.3742 | 13.7875 | 21.3019 |  |  |  | 16.6653 | 17.2599 | 30.8063 | 487.682 | 452.4373 | 674.216 | 17.2474 | 17.1053 | 26.0332 | 16.8569 | 17.1438 | 27.9246 | 214.291 | 802.9855 |  | 334.4114 | 502.4975 | 422.36 | 481.5454 |  | 16.4869 | 28.422 | 19.7079 | 31.9634 | 41.3892 | 133.9586 | 362.1894 | 6.0201 | 11.6151 | 6.8697 | 18.9273 | 9.7319 | 42.6294 | 47.0876 | 43.2913 | 14.8426 |  |  | -1.2825 | 0.23665 | -0.36088 | -0.68274 | 3.1477 | 2.5137 | 2.9885 | 6.9672 | 0.89323 | 2.0244 | 17.649 | 0.0053686 | 0.0053062 | 0.29919 | 16.3172 | 16.6278 | 17.1465 | 17.4708 | 17.4157 | 16.3444 | 14.6676 | 16.7523 | 17.0863 | 17.3858 | 17.4244 | 17.1185 | 16.2756 | 14.4515 | 233.4362 | 61.7706 | 126.6873 | 64.3171 | 57.9892 | 95.6041 | 46.3093 | 15.8581 | 15.7111 | 16.0673 | 14.5037 | 17.2822 | 22.6951 |  |  |  | 171.0084 | 636.6907 | 589.8415 | 426.1482 | 12.1244 | 5.8399 | 208.6858 |  |  | 21.4565 |  |  | 17.0121 | 18.2865 | 44.5374 | 16.391 | 16.7045 | 25.1715 | 644.6996 | 803.2323 | 393.6151 | 410.5805 | 466.7244 |  | 201.9553 | 439.8063 | 156.1673 | 800.302 | 340.03 | 647.2727 |  | 248.8844 |  |  | 84.7163 | 133.1368 | 346.58 | [6 empty] | 550.6426 |  |  | 221.9842 |  |  | 91.6071 | 375.5005 | 748.3467 | 41.6045 | 263.8874 | 533.1181 | 70.83 | 286.1065 | 696.5258 | 206.0011 | 506.2916 | 63.8051 | 373.9076 | 105.8009 | 437.4202 | 44.8905 | 240.9448 | 450.3096 | 126.4681 | 296.7688 | 589.165 | 65.7833 | 256.2021 | 542.0541 | 65.5597 | 343.6113 | 139.9586 | 356.9215 | 94.95 | 448.152 | 57.4063 | 17.9727 | 2.7022 | 0.085592 | -38.2928 | 3.1243 | 2418.54 | 50.09 | -2.4291 | 0.58873 | -0.72701 | -0.99998 | 2.4947 | 2.2293 | 2.4308 | -4.4657 | -5.9527 | -4.7698 | -14.2663 | -8.3403 | -4.2228 | -4.8806
42810.4484 | 725 | 18.5404 | 18.5594 | 18.5267 | 18.5255 | 17.8019 | 16.379 | 14.4308 | 16.5946 | 17.1033 | 17.1947 | 17.211 | 16.7256 | 15.7376 | 14.3618 | 14.9032 | 15.012 | 15.8904 | 13.3778 | 13.7768 | 21.3388 |  |  |  | 16.6565 | 17.2599 | 30.8606 | 508.7512 | 469.1564 | 711.3076 | 17.2448 | 17.1031 | 26.1011 | 16.8588 | 17.1575 | 28.0186 | 219.0546 | 806.0141 |  | 342.3109 | 518.9229 | 429.3905 | 501.1068 |  | 17.0831 | 29.7584 | 20.505 | 33.5438 | 43.8065 | 145.7268 | 374.973 | 6.1449 | 11.8266 | 6.8954 | 19.4308 | 9.7513 | 42.6522 | 47.0643 | 43.298 | 14.8495 |  |  | -0.89674 | 0.45284 | 0.002508 | -0.25956 | 3.8561 | 2.4907 | 3.4806 | 7.2689 | 1.8651 | 2.2371 | 19.1438 | 0.0052388 | 0.0052208 | 0.28233 | 16.3058 | 16.622 | 17.1436 | 17.4568 | 17.4011 | 16.3412 | 14.6666 | 16.7468 | 17.0807 | 17.382 | 17.412 | 17.1151 | 16.2673 | 14.4376 | 254.2267 | 71.6666 | 142.9324 | 69.8543 | 58.1075 | 98.2102 | 47.2575 | 15.8579 | 15.7087 | 16.0772 | 14.508 | 17.3098 | 22.7567 |  |  |  | 177.0125 | 646.7163 | 616.9303 | 444.3193 | 16.7652 | 11.7881 | 221.9208 |  |  | 22.0507 |  |  | 17.0174 | 18.3043 | 45.0719 | 16.3837 | 16.7144 | 25.2468 | 647.7869 | 808.8065 | 405.0333 | 425.0194 | 540.0106 |  | 210.7637 | 452.8276 | 161.8406 | 865.8485 | 362.3563 | 645.0596 |  | 257.7895 |  |  | 88.3325 | 140.2006 | 371.8441 | [6 empty] | 574.9708 |  |  | 233.5317 |  |  | 95.3253 | 390.1911 | 765.2744 | 43.627 | 271.0875 | 540.1627 | 73.9863 | 294.8964 | 703.6685 | 218.8884 | 528.3953 | 67.5434 | 385.2894 | 110.8526 | 448.8423 | 46.8932 | 247.0677 | 461.0016 | 131.2955 | 306.5639 | 609.2907 | 68.395 | 263.0833 | 549.268 | 69.1012 | 351.1074 | 146.5292 | 371.0277 | 100.4616 | 456.5412 | 52.2481 | 17.9451 | 2.7576 | 0.085838 | -38.252 | 3.1243 | 2517.29 | 48.83 | -2.0706 | 0.8162 | 0.060742 | -0.61794 | 2.8008 | 2.251 | 2.661 | -6.0365 | -6.0529 | -4.7376 | -16.2568 | -10.033 | -4.5069 | -5.0968
42810.4484 | 726 | 18.5315 | 18.5703 | 18.5363 | 18.5276 | 17.8018 | 16.3789 | 14.4262 | 16.5943 | 17.1004 | 17.2012 | 17.2145 | 16.7226 | 15.7388 | 14.3599 | 14.9002 | 15.0109 | 15.8909 | 13.3729 | 13.7696 | 21.3781 |  |  |  | 16.6558 | 17.2663 | 30.9287 | 531.2544 | 486.8538 | 726.2495 | 17.2458 | 17.1079 | 26.2056 | 16.8632 | 17.1729 | 28.1225 | 224.4547 | 820.275 |  | 350.8924 | 535.0212 | 437.309 | 534.6145 |  | 17.6462 | 31.0533 | 21.3465 | 35.1485 | 45.9773 | 156.062 | 385.8129 | 6.2824 | 12.0261 | 6.9818 | 19.9195 | 9.7699 | 42.6757 | 47.0485 | 43.3027 | 14.8542 |  |  | -1.0098 | 0.62829 | -0.044804 | -0.53358 | 4.1091 | 3.523 | 3.6495 | 7.6664 | 1.399 | 2.7514 | 21.0414 | 0.0050549 | 0.0051304 | 0.25086 | 16.3175 | 16.6226 | 17.1414 | 17.4584 | 17.4077 | 16.3453 | 14.6663 | 16.7461 | 17.084 | 17.3833 | 17.4174 | 17.1178 | 16.2671 | 14.4461 | 290.6244 | 86.3995 | 165.8039 | 86.942 | 67.0601 | 101.3464 | 48.5068 | 15.8492 | 15.7152 | 16.0763 | 14.5114 | 17.3499 | 22.824 |  |  |  | 184.4818 | 658.3859 | 641.7984 | 462.8502 | 17.5367 | 4.9525 | 235.5494 |  |  | 22.7235 |  |  | 17.0176 | 18.3233 | 45.6392 | 16.3935 | 16.7163 | 25.3367 | 652.1924 | 813.6553 | 418.5742 | 440.1967 | 596.6286 |  | 219.202 | 476.072 | 167.741 | 894.6021 | 386.3517 | 649.7838 |  | 266.0929 |  |  | 92.5394 | 148.031 | 393.0666 | [6 empty] | 603.6103 |  |  | 246.2853 |  |  | 99.7126 | 408.3565 | 782.8813 | 45.8628 | 278.8347 | 548.6914 | 77.4385 | 304.4347 | 707.6594 | 233.8116 | 554.962 | 72.047 | 398.3451 | 116.5908 | 460.0954 | 48.7997 | 253.3611 | 471.7003 | 136.5715 | 318.077 | 628.0275 | 71.3729 | 271.2335 | 555.2766 | 72.7939 | 359.0602 | 154.264 | 386.7191 | 106.0133 | 464.5095 | 71.143 | 17.9146 | 2.8065 | 0.084933 | -38.2634 | 3.1243 | 2631.45 | 49.49 | -2.2138 | 0.96345 | -0.25728 | -0.88787 | 2.9267 | 2.7099 | 2.7582 | -7.1522 | -6.4223 | -3.3918 | -19.9156 | -12.4261 | -5.1392 | -5.2456
42810.4484 | 727 | 18.5342 | 18.5633 | 18.5314 | 18.5184 | 17.7968 | 16.3802 | 14.4274 | 16.5928 | 17.1033 | 17.2035 | 17.2072 | 16.7202 | 15.7371 | 14.3555 | 14.8966 | 15.0157 | 15.9001 | 13.3697 | 13.7781 | 21.4164 |  |  |  | 16.6582 | 17.2742 | 31.0123 | 554.4799 | 509.4855 | 753.647 | 17.2518 | 17.1204 | 26.2962 | 16.8678 | 17.1723 | 28.2351 | 230.6097 | 813.3361 |  | 360.0239 | 551.3346 | 445.3196 | 561.206 |  | 18.252 | 32.6769 | 22.3313 | 37.0136 | 48.7232 | 168.7968 | 396.0617 | 6.4731 | 12.272 | 7.3504 | 20.506 | 9.7847 | 42.7067 | 47.0502 | 43.311 | 14.8658 |  |  | -1.0229 | 0.41275 | 0.028136 | -0.40544 | 4.6039 | 3.0216 | 3.4268 | 7.8537 | 1.333 | 5.1708 | 22.5351 | 0.0049218 | 0.0049744 | 0.2013 | 16.3237 | 16.6307 | 17.1455 | 17.4598 | 17.41 | 16.3422 | 14.6713 | 16.754 | 17.0966 | 17.3812 | 17.4161 | 17.1186 | 16.278 | 14.4522 | 321.9246 | 85.6808 | 158.3885 | 91.1296 | 74.2382 | 104.7097 | 49.3894 | 15.8511 | 15.714 | 16.0785 | 14.514 | 17.3589 | 22.8904 |  |  |  | 192.5139 | 670.3736 | 666.5801 | 499.8576 | 16.2105 | 9.6682 | 256.0956 |  |  | 23.4783 |  |  | 17.0166 | 18.3239 | 46.2193 | 16.3987 | 16.7222 | 25.4076 | 660.184 | 818.7331 | 431.8567 | 454.8763 | 656.5741 |  | 228.2484 | 544.3642 | 175.5729 | 916.5477 | 412.9099 | 669.7553 |  | 275.5052 |  |  | 96.9653 | 158.306 | 408.5607 | [6 empty] | 634.3881 |  |  | 261.5983 |  |  | 104.7413 | 432.1262 | 799.1318 | 48.5186 | 287.9087 | 558.5355 | 81.193 | 314.6837 | 712.6589 | 251.5614 | 588.0743 | 76.6894 | 415.8676 | 123.2306 | 471.4188 | 50.8915 | 260.8429 | 482.6119 | 142.3229 | 331.4338 | 644.0149 | 74.701 | 280.7207 | 563.6442 | 76.4427 | 367.6138 | 163.0392 | 404.4622 | 112.0797 | 472.1763 | 53.8386 | 17.889 | 2.8735 | 0.085896 | -38.3007 | 3.1244 | 2765.04 | 49.49 | -2.2585 | 0.78298 | 0.20443 | -0.77601 | 3.1435 | 2.5467 | 2.712 | -8.3144 | -7.9454 | -1.4287 | -22.9791 | -11.4974 | -5.5317 | -5.8712
42810.4485 | 728 | 18.5382 | 18.5688 | 18.5377 | 18.5279 | 17.8007 | 16.3703 | 14.4345 | 16.5999 | 17.1047 | 17.2069 | 17.2111 | 16.7283 | 15.7345 | 14.3647 | 14.8943 | 15.0175 | 15.9076 | 13.3732 | 13.7833 | 21.4644 |  |  |  | 16.6617 | 17.2868 | 31.1149 | 580.3301 | 534.2385 | 789.9345 | 17.2516 | 17.1161 | 26.3823 | 16.8633 | 17.1746 | 28.3754 | 238.2067 | 810.8262 |  | 370.7622 | 568.7154 | 456.1101 | 583.1097 |  | 19.0479 | 34.7172 | 23.6046 | 39.3293 | 51.6254 | 181.3377 | 408.6644 | 6.5867 | 12.5952 | 7.8252 | 21.2725 | 9.8062 | 42.741 | 47.0601 | 43.3273 | 14.8758 |  |  | -0.83235 | 0.53301 | -0.053348 | -0.14194 | 4.4574 | 3.3521 | 3.6719 | 8.087 | 1.3735 | 4.4417 | 24.1151 | 0.0049021 | 0.0048709 | 0.19673 | 16.3253 | 16.627 | 17.1395 | 17.4632 | 17.4053 | 16.3439 | 14.6663 | 16.7434 | 17.0915 | 17.3841 | 17.4139 | 17.1127 | 16.2723 | 14.4496 | 339.846 | 92.0221 | 177.3143 | 98.4932 | 81.4444 | 108.156 | 50.8244 | 15.8475 | 15.7078 | 16.0871 | 14.5075 | 17.3767 | 22.959 |  |  |  | 200.9546 | 682.5579 | 691.4301 | 526.2554 | 17.0983 | 10.0371 | 281.2446 |  |  | 24.3199 |  |  | 17.0234 | 18.3368 | 46.8201 | 16.3926 | 16.7282 | 25.4916 | 667.2014 | 824.6687 | 444.5609 | 469.6645 | 706.2613 |  | 240.0168 | 574.8678 | 184.8138 | 938.9118 | 447.0991 | 698.5991 |  | 287.3455 |  |  | 101.5519 | 169.9455 | 424.6118 | [6 empty] | 669.6127 |  |  | 277.5999 |  |  | 110.5611 | 464.4998 | 814.8297 | 51.5713 | 298.0286 | 566.5796 | 85.391 | 326.3219 | 718.2837 | 271.8739 | 630.1495 | 82.6005 | 434.8537 | 130.348 | 485.2318 | 53.3012 | 268.7695 | 493.2225 | 148.4603 | 346.0066 | 659.4607 | 78.422 | 291.3354 | 573.3293 | 80.9477 | 376.0589 | 174.0082 | 425.4881 | 119.7019 | 481.1232 | 75.243 | 17.8547 | 2.9285 | 0.087097 | -38.266 | 3.1243 | 2946.52 | 48.75 | -2.073 | 0.89272 | -0.28243 | -0.46068 | 3.1367 | 2.7201 | 2.8469 | -9.0192 | -8.3408 | 1.5971 | -24.5447 | -13.4298 | -5.7038 | -6.1714
42810.4485 | 729 | 18.5347 | 18.5616 | 18.5297 | 18.52 | 17.7989 | 16.3715 | 14.4298 | 16.5881 | 17.1008 | 17.1971 | 17.2056 | 16.7204 | 15.7378 | 14.3589 | 14.8988 | 15.0104 | 15.9078 | 13.3676 | 13.7765 | 21.509 |  |  |  | 16.6623 | 17.2894 | 31.2418 | 608.9158 | 554.8531 | 823.6376 | 17.2517 | 17.1335 | 26.4739 | 16.8716 | 17.1809 | 28.522 | 245.7403 | 813.0476 |  | 381.1156 | 583.9094 | 467.0452 | 603.0763 |  | 19.8108 | 36.6049 | 24.809 | 41.4478 | 54.2879 | 194.4333 | 424.5293 | 6.7562 | 12.9134 | 8.3243 | 22.0292 | 9.8172 | 42.7643 | 47.0674 | 43.3494 | 14.8809 |  |  | -1.4711 | 0.63749 | -0.10592 | -0.67223 | 4.6591 | 3.8581 | 3.6357 | 8.7631 | 1.319 | 5.1792 | 26.091 | 0.0047641 | 0.0048052 | 0.24968 | 16.3289 | 16.6265 | 17.1427 | 17.4624 | 17.4025 | 16.3472 | 14.6696 | 16.7493 | 17.0841 | 17.3858 | 17.4161 | 17.1112 | 16.2716 | 14.4438 | 343.9008 | 98.8317 | 192.4603 | 102.5955 | 81.8999 | 112.0155 | 52.2976 | 15.8509 | 15.7121 | 16.0932 | 14.5143 | 17.405 | 23.034 |  |  |  | 210.8013 | 694.7365 | 717.1438 | 567.0644 | 20.9331 | 10.7446 | 301.5097 |  |  | 25.3449 |  |  | 17.027 | 18.3591 | 47.4703 | 16.3964 | 16.7389 | 25.5871 | 671.5738 | 832.8225 | 456.2508 | 484.4001 | 727.148 |  | 251.1386 | 615.7319 | 193.8486 | 959.3117 | 478.4283 | 715.2763 |  | 298.1993 |  |  | 106.7002 | 181.1945 | 444.4528 | [6 empty] | 702.3948 |  |  | 294.1554 |  |  | 117.4316 | 502.5262 | 831.9933 | 54.5783 | 309.1799 | 573.2161 | 89.932 | 340.0313 | 722.204 | 294.0505 | 674.7689 | 90.1118 | 450.929 | 138.2566 | 501.363 | 55.7713 | 276.8571 | 504.007 | 155.1589 | 362.1972 | 675.5938 | 82.5527 | 302.586 | 583.1584 | 87.3304 | 385.6547 | 186.0594 | 447.7643 | 127.7179 | 491.2233 | 86.3393 | 17.8147 | 2.9901 | 0.087408 | -38.2998 | 3.1244 | 3149.99 | 50.01 | -2.7993 | 0.97929 | -0.39917 | -1.0056 | 3.2527 | 2.96 | 2.8734 | -8.9383 | -9.0222 | 4.7338 | -24.5172 | -14.9376 | -5.8156 | -6.786
42810.4485 | 730 | 18.5345 | 18.5669 | 18.5311 | 18.5258 | 17.8027 | 16.3785 | 14.4277 | 16.5892 | 17.0958 | 17.1991 | 17.2105 | 16.7304 | 15.7434 | 14.3637 | 14.9074 | 15.0157 | 15.9159 | 13.3745 | 13.7776 | 21.5617 |  |  |  | 16.6691 | 17.2941 | 31.3872 | 638.0247 | 575.3023 | 858.2087 | 17.2579 | 17.1368 | 26.561 | 16.8646 | 17.1946 | 28.698 | 253.9772 | 819.9644 |  | 391.5927 | 597.3 | 477.9282 | 627.2586 |  | 20.6849 | 38.9357 | 26.303 | 44.0216 | 58.1994 | 210.2034 | 439.6637 | 7.1656 | 13.3562 | 9.0966 | 23.0663 | 9.8302 | 42.8046 | 47.0676 | 43.3872 | 14.8944 |  |  | -0.79423 | 0.3753 | -0.34839 | -0.80562 | 4.3989 | 3.2523 | 3.9774 | 8.6127 | 1.1285 | 5.7943 | 28.4802 | 0.0047132 | 0.0046935 | 0.30339 | 16.3216 | 16.6238 | 17.1391 | 17.4524 | 17.398 | 16.3396 | 14.6691 | 16.7415 | 17.0857 | 17.3777 | 17.4103 | 17.1103 | 16.2674 | 14.4443 | 384.6791 | 108.2656 | 208.4766 | 111.4616 | 88.3973 | 116.6681 | 54.0174 | 15.8469 | 15.7219 | 16.093 | 14.5205 | 17.4455 | 23.1029 |  |  |  | 222.1637 | 706.5183 | 736.3311 | 601.4274 | 17.0189 | 15.7424 | 321.3725 |  |  | 26.2963 |  |  | 17.03 | 18.369 | 48.1829 | 16.4022 | 16.745 | 25.674 | 677.2642 | 839.3062 | 467.2702 | 499.4987 | 750.7397 |  | 263.3328 | 640.3543 | 202.9733 | 956.456 | 508.3478 | 722.5299 |  | 308.9445 |  |  | 112.7827 | 192.9625 | 463.4391 | [6 empty] | 729.18 |  |  | 311.2627 |  |  | 124.8383 | 539.3202 | 849.4095 | 57.7026 | 321.1402 | 581.2565 | 94.9697 | 355.159 | 726.0541 | 318.1319 | 719.8222 | 99.3442 | 466.3932 | 147.5793 | 519.4885 | 58.3977 | 285.0619 | 515.6236 | 162.5215 | 379.7478 | 692.4199 | 87.2275 | 316.1421 | 593.4178 | 94.6621 | 396.2279 | 198.6038 | 469.3814 | 137.333 | 504.2514 | 85.4647 | 17.7758 | 3.0472 | 0.08772 | -38.3282 | 3.1244 | 3380.48 | 49.14 | -2.089 | 0.75421 | -0.72667 | -1.105 | 3.2134 | 2.7631 | 3.0556 | -8.8422 | -9.2357 | 8.7018 | -28.4697 | -16.5125 | -5.9912 | -7.1224
42810.4485 | 731 | 18.5409 | 18.5713 | 18.5316 | 18.5269 | 17.8021 | 16.3858 | 14.428 | 16.5893 | 17.1013 | 17.2003 | 17.2128 | 16.7314 | 15.7438 | 14.3631 | 14.8958 | 15.014 | 15.9185 | 13.3753 | 13.7713 | 21.6085 |  |  |  | 16.6698 | 17.2992 | 31.5901 | 666.7847 | 597.7632 | 881.5823 | 17.2514 | 17.1391 | 26.6557 | 16.8648 | 17.1907 | 28.907 | 263.1189 | 818.8236 |  | 401.9528 | 611.4173 | 488.797 | 648.5758 |  | 21.6327 | 41.0856 | 27.5986 | 46.5417 | 61.8956 | 223.2869 | 453.3289 | 7.6076 | 13.8138 | 9.8497 | 24.156 | 9.8464 | 42.8486 | 47.0643 | 43.4491 | 14.9103 |  |  | -1.5624 | 0.23139 | -0.20777 | -0.26547 | 4.8017 | 3.6426 | 4.1884 | 9.1811 | 2.4759 | 6.2441 | 29.6092 | 0.0045785 | 0.0045259 | 0.32447 | 16.34 | 16.6225 | 17.1424 | 17.4518 | 17.4022 | 16.343 | 14.6647 | 16.7416 | 17.0891 | 17.3846 | 17.4198 | 17.1101 | 16.2708 | 14.4437 | 387.9474 | 112.1114 | 238.6791 | 125.0229 | 95.8626 | 120.9246 | 56.2897 | 15.8468 | 15.7206 | 16.1021 | 14.5222 | 17.4704 | 23.1813 |  |  |  | 236.3508 | 720.3141 | 745.8256 | 638.8579 | 20.1026 | 15.5092 | 337.6649 |  |  | 27.3504 |  |  | 17.0264 | 18.3906 | 49.5237 | 16.3979 | 16.7449 | 25.7735 | 684.587 | 844.8187 | 478.3933 | 514.6617 | 777.5415 |  | 277.0155 | 653.8356 | 213.2707 | 957.4091 | 540.725 | 722.0863 |  | 320.7028 |  |  | 118.9886 | 205.7991 | 477.4672 | [6 empty] | 752.3554 |  |  | 329.0295 |  |  | 132.6434 | 577.0177 | 867.6157 | 61.2061 | 333.4246 | 590.5148 | 100.3916 | 369.5434 | 731.2851 | 343.7923 | 768.4625 | 109.5009 | 484.3378 | 157.7653 | 539.9975 | 61.2813 | 293.4674 | 525.8002 | 170.2906 | 398.7902 | 708.9025 | 92.255 | 330.3883 | 603.1427 | 103.0122 | 406.724 | 213.1018 | 491.6353 | 147.2706 | 518.0824 | 87.5284 | 17.722 | 3.1231 | 0.090369 | -38.2565 | 3.1243 | 3550.22 | 49.07 | -2.9601 | 0.59425 | -0.5631 | -0.63651 | 3.4025 | 2.9635 | 3.1778 | -8.7088 | -9.0637 | 13.3033 | -28.3018 | -19.5976 | -6.0178 | -7.3599
42810.4485 | 732 | 18.5412 | 18.569 | 18.5295 | 18.5226 | 17.7945 | 16.3787 | 14.4253 | 16.5909 | 17.1028 | 17.1978 | 17.2084 | 16.7183 | 15.7374 | 14.3565 | 14.8955 | 15.0106 | 15.9134 | 13.3702 | 13.7685 | 21.6493 |  |  |  | 16.6685 | 17.299 | 32.5025 | 693.4283 | 617.6266 | 903.1301 | 17.2526 | 17.1399 | 26.7427 | 16.8709 | 17.1958 | 29.1313 | 272.6787 | 822.3259 |  | 412.6135 | 623.7175 | 499.0708 | 660.0813 |  | 22.6154 | 43.3055 | 28.9006 | 49.0774 | 68.7535 | 237.9959 | 467.1758 | 8.0732 | 14.323 | 10.7448 | 25.367 | 9.8733 | 42.8905 | 47.0616 | 43.5411 | 14.9285 |  |  | -1.3324 | 0.51855 | -0.12826 | -0.22671 | 4.5625 | 3.2542 | 3.6922 | 10.5794 | 2.6209 | 7.6374 | 29.5667 | 0.0045275 | 0.0045867 | 0.367 | 16.3427 | 16.637 | 17.1529 | 17.4661 | 17.4053 | 16.3422 | 14.6819 | 16.7554 | 17.1033 | 17.3961 | 17.4246 | 17.1267 | 16.2797 | 14.4591 | 397.6312 | 107.4367 | 262.3576 | 139.0403 | 108.4067 | 125.6202 | 58.8088 | 15.8493 | 15.7239 | 16.1079 | 14.5277 | 17.5047 | 23.2533 |  |  |  | 250.1373 | 733.4045 | 750.2727 | 674.0904 | 22.686 | 14.5283 | 355.0415 |  |  | 28.1908 |  |  | 17.0323 | 18.3979 | 55.2534 | 16.3999 | 16.7528 | 25.8703 | 689.3806 | 847.688 | 489.6796 | 527.572 | 771.3742 |  | 290.7971 | 688.3709 | 224.7124 | 956.2906 | 571.4268 | 737.1986 |  | 333.0146 |  |  | 124.9069 | 221.1472 | 490.2812 | [6 empty] | 771.4136 |  |  | 365.2794 |  |  | 141.3481 | 619.0757 | 886.326 | 64.7744 | 347.267 | 597.9269 | 106.0101 | 384.6212 | 735.509 | 369.0399 | 810.995 | 120.2612 | 502.8073 | 169.0308 | 559.9688 | 64.311 | 302.8648 | 534.41 | 178.6232 | 418.7416 | 722.0983 | 97.3472 | 345.4268 | 612.839 | 112.0809 | 417.9905 | 233.8739 | 515.6964 | 158.321 | 531.6724 | 96.3329 | 17.6774 | 3.1905 | 0.092055 | -38.3018 | 3.1244 | 3734.56 | 50.39 | -2.7589 | 0.89273 | -0.44399 | -0.59028 | 3.3654 | 2.8423 | 3.0275 | -7.6143 | -9.3959 | 18.1589 | -28.7897 | -21.928 | -5.7284 | -7.525
42810.4485 | 733 | 18.5352 | 18.5673 | 18.5296 | 18.5227 | 17.7954 | 16.375 | 14.4254 | 16.5953 | 17.1078 | 17.1926 | 17.2007 | 16.7159 | 15.7415 | 14.3573 | 14.9067 | 15.0166 | 15.9198 | 13.3742 | 13.765 | 21.7086 |  |  |  | 16.6653 | 17.3058 | 34.7031 | 718.7311 | 634.9867 | 923.9777 | 17.2533 | 17.1427 | 26.8326 | 16.8659 | 17.2024 | 29.3533 | 282.9963 | 813.0558 |  | 423.1397 | 634.1892 | 510.1564 | 678.0057 |  | 23.7057 | 45.9981 | 30.3984 | 51.7258 | 75.2446 | 252.3581 | 481.5403 | 8.5994 | 14.935 | 11.7656 | 26.8417 | 9.8869 | 42.9172 | 47.0604 | 43.6579 | 14.9422 |  |  | -1.8515 | 0.46795 | -0.11577 | -0.06571 | 5.3931 | 3.8213 | 4.2416 | 11.6222 | 2.876 | 6.8972 | 31.5085 | 0.0043895 | 0.0044109 | 0.41147 | 16.3444 | 16.637 | 17.1428 | 17.4587 | 17.4032 | 16.3407 | 14.6736 | 16.7491 | 17.0888 | 17.387 | 17.4257 | 17.1174 | 16.2745 | 14.4606 | 403.0182 | 107.3138 | 263.3039 | 149.6438 | 119.945 | 130.3841 | 61.1579 | 15.8475 | 15.7308 | 16.1161 | 14.5338 | 17.5345 | 23.3208 |  |  |  | 264.4132 | 743.702 | 761.7522 | 710.6897 | 20.6995 | 11.5457 | 372.0054 |  |  | 29.1027 |  |  | 17.0398 | 18.409 | 67.468 | 16.4042 | 16.7628 | 25.977 | 694.4405 | 848.6985 | 500.0139 | 539.2047 | 779.8513 |  | 304.1635 | 712.5868 | 235.4455 | 960.0181 | 597.6257 | 729.7112 |  | 343.8629 |  |  | 130.8441 | 244.7889 | 503.621 | [6 empty] | 786.8516 |  |  | 414.9762 |  |  | 150.3514 | 657.3584 | 903.4517 | 68.1872 | 360.7034 | 602.7182 | 111.5557 | 401.1354 | 740.4325 | 396.5053 | 847.3595 | 132.5109 | 522.0705 | 178.9735 | 578.8308 | 67.236 | 313.421 | 542.7756 | 187.6116 | 440.4094 | 739.9044 | 102.9399 | 359.3439 | 624.1015 | 120.38 | 430.1382 | 252.2176 | 537.0326 | 170.4053 | 546.3446 | 98.2418 | 17.6184 | 3.2603 | 0.090904 | -38.3655 | 3.1244 | 3934.76 | 49.03 | -3.281 | 0.85166 | -0.42361 | -0.31914 | 3.71 | 3.1229 | 3.2902 | -6.9152 | -9.4601 | 22.5328 | -28.7892 | -21.7524 | -5.5482 | -7.6618
42810.4485 | 734 | 18.5343 | 18.5685 | 18.5311 | 18.5201 | 17.8038 | 16.3854 | 14.423 | 16.5878 | 17.1001 | 17.1977 | 17.2036 | 16.7188 | 15.7478 | 14.3579 | 14.8986 | 15.0125 | 15.9213 | 13.3754 | 13.7617 | 21.7443 |  |  |  | 16.6686 | 17.3133 | 38.8107 | 741.3544 | 648.4508 | 939.7148 | 17.2538 | 17.1489 | 26.8911 | 16.8668 | 17.2052 | 29.6201 | 294.8868 | 799.9058 |  | 433.4629 | 644.1257 | 524.6176 | 716.1406 |  | 24.6397 | 48.2658 | 31.6858 | 53.923 | 82.1168 | 263.79 | 491.6013 | 9.0008 | 15.456 | 12.5901 | 28.1274 | 9.9154 | 42.9569 | 47.0694 | 43.7887 | 14.9741 |  |  | -1.9008 | 0.57244 | -0.12432 | -0.20305 | 5.5213 | 4.6611 | 4.7995 | 12.3746 | 3.0434 | 7.7465 | 33.6325 | 0.00436 | 0.0043156 | 0.40111 | 16.3372 | 16.6264 | 17.1386 | 17.4561 | 17.3957 | 16.3371 | 14.6632 | 16.7511 | 17.0793 | 17.3857 | 17.4124 | 17.117 | 16.2701 | 14.4458 | 396.2954 | 103.8603 | 257.4271 | 157.5076 | 129.0767 | 134.5701 | 63.2742 | 15.8458 | 15.7272 | 16.1165 | 14.5322 | 17.5591 | 23.381 |  |  |  | 278.8721 | 749.5663 | 785.6201 | 732.7627 | 17.37 | 12.252 | 389.9086 |  |  | 30.1277 |  |  | 17.0444 | 18.4272 | 74.518 | 16.3985 | 16.762 | 26.0892 | 699.3084 | 852.2919 | 510.5651 | 550.9053 | 775.6079 |  | 318.0263 | 729.6947 | 246.8308 | 965.3653 | 623.6448 | 729.4425 |  | 355.2922 |  |  | 136.7854 | 257.1248 | 512.862 | [6 empty] | 802.7396 |  |  | 454.8181 |  |  | 160.0364 | 700.2525 | 920.7698 | 71.6166 | 374.9657 | 608.8801 | 117.6002 | 418.2013 | 745.1521 | 423.9021 | 881.7588 | 144.8797 | 540.7659 | 190.5123 | 596.5261 | 70.0659 | 324.0717 | 551.4498 | 197.4193 | 463.0128 | 756.6819 | 108.6456 | 373.646 | 636.9105 | 131.5094 | 443.4622 | 274.6942 | 560.139 | 183.5093 | 559.7922 | 104.707 | 17.5573 | 3.3191 | 0.091085 | -38.3139 | 3.1244 | 4153.2 | 49.47 | -3.3461 | 0.94529 | -0.44052 | -0.56299 | 3.7944 | 3.4864 | 3.5377 | -5.7851 | -9.2678 | 27.1815 | -27.5137 | -20.8462 | -5.7983 | -7.3429
42810.4485 | 735 | 18.5318 | 18.5673 | 18.5311 | 18.5184 | 17.8016 | 16.3757 | 14.4204 | 16.5981 | 17.1054 | 17.1953 | 17.2076 | 16.7197 | 15.7376 | 14.3567 | 14.8998 | 15.0135 | 15.9236 | 13.3804 | 13.7695 | 21.8188 |  |  |  | 16.6702 | 17.3228 | 43.7581 | 747.8795 | 662.9379 | 947.3876 | 17.2487 | 17.147 | 26.9623 | 16.869 | 17.2207 | 30.0432 | 308.6837 | 794.5003 |  | 439.6504 | 654.0639 | 540.456 | 749.9141 |  | 25.831 | 51.2481 | 33.4949 | 56.9693 | 90.7507 | 279.0419 | 501.9739 | 9.5193 | 16.1834 | 14.0911 | 29.8227 | 9.9439 | 42.9879 | 47.082 | 43.9279 | 14.9996 |  |  | -0.80278 | 0.52447 | 0.00908 | -0.23196 | 6.0739 | 5.0061 | 4.3244 | 14.8553 | 4.0631 | 9.2627 | 36.1551 | 0.0042466 | 0.0043107 | 0.38553 | 16.3355 | 16.6202 | 17.1391 | 17.4564 | 17.3984 | 16.3345 | 14.6604 | 16.7467 | 17.0818 | 17.3868 | 17.4135 | 17.1158 | 16.2686 | 14.4471 | 376.5543 | 100.5168 | 247.9907 | 164.6775 | 134.5687 | 138.1883 | 65.3295 | 15.8277 | 15.7088 | 16.1108 | 14.5196 | 17.5739 | 23.4336 |  |  |  | 295.6076 | 756.3475 | 816.5025 | 763.7569 | 14.876 | 6.2895 | 402.5679 |  |  | 31.3408 |  |  | 17.0502 | 18.4398 | 81.1614 | 16.3973 | 16.7707 | 26.1937 | 703.9739 | 858.1327 | 522.8271 | 563.009 | 767.1712 |  | 333.9111 | 722.7423 | 260.3279 | 967.3493 | 650.8274 | 742.5897 |  | 368.6325 |  |  | 143.5475 | 282.4243 | 526.6423 | [6 empty] | 822.854 |  |  | 485.2152 |  |  | 172.2239 | 744.0206 | 938.5416 | 76.0231 | 390.7111 | 615.8465 | 124.6538 | 438.86 | 750.4264 | 454.0221 | 917.5034 | 159.2674 | 559.6066 | 204.2438 | 616.1481 | 73.1272 | 335.3259 | 558.3323 | 208.1658 | 487.7819 | 771.587 | 115.0986 | 391.8517 | 649.9161 | 142.6351 | 456.3022 | 302.8048 | 586.8858 | 197.8196 | 577.5964 | 118.7003 | 17.4897 | 3.3908 | 0.092721 | -38.308 | 3.1243 | 4424.92 | 50.19 | -2.1814 | 0.909 | 0.1196 | -0.60453 | 4.0359 | 3.6641 | 3.4054 | -4.3346 | -8.2524 | 32.5342 | -24.8619 | -19.5515 | -5.7584 | -7.0709
42810.4486 | 736 | 18.5241 | 18.5672 | 18.5211 | 18.5218 | 17.797 | 16.3686 | 14.4207 | 16.5821 | 17.095 | 17.1939 | 17.1991 | 16.7181 | 15.7285 | 14.3553 | 14.9034 | 15.015 | 15.9317 | 13.3843 | 13.7675 | 21.8645 |  |  |  | 16.6646 | 17.3284 | 47.8165 | 760.1354 | 672.6106 | 953.0785 | 17.2376 | 17.1528 | 27.0355 | 16.8626 | 17.2168 | 32.5157 | 323.2823 | 787.3672 |  |  | 663.0984 | 554.1109 | 757.1145 |  | 27.0186 | 54.267 | 35.4357 | 60.432 | 102.9795 | 296.1265 | 513.6496 | 9.9042 | 16.9011 | 15.7371 | 31.505 | 9.9703 | 43.0146 | 47.092 | 44.0746 | 15.0404 |  |  | -1.6958 | 0.72423 | -0.13483 | -0.15442 | 6.9111 | 6.1994 | 5.042 | 19.4005 | 3.7478 | 10.1059 | 39.1798 | 0.004153 | 0.0041661 | 0.36806 | 16.348 | 16.6267 | 17.141 | 17.4638 | 17.404 | 16.3375 | 14.6688 | 16.7475 | 17.092 | 17.3879 | 17.4271 | 17.1192 | 16.2802 | 14.4519 | 353.8184 | 94.6722 | 228.0465 | 159.6718 | 133.226 | 141.5022 | 67.0195 | 15.8448 | 15.7327 | 16.1244 | 14.5248 | 17.6143 | 23.5056 |  |  |  | 314.1812 | 771.0364 | 855.585 | 792.9954 | 16.5142 | 8.5812 | 413.9292 |  |  | 32.5602 |  |  | 17.0647 | 18.4582 | 87.7289 | 16.4064 | 16.7805 | 26.3197 | 710.2814 | 864.7695 | 534.7791 | 575.23 | 758.962 |  | 348.3729 | 719.2095 | 272.9086 | 958.2323 | 674.4641 | 752.9038 |  | 380.3204 |  |  | 150.4998 | 309.1293 | 537.7653 | [6 empty] | 844.9698 |  |  | 505.3271 |  |  | 185.4977 | 789.7393 | 953.3078 | 81.0872 | 408.3456 | 624.0598 | 132.6102 | 459.0405 | 756.3306 | 485.2859 | 955.8033 | 176.6388 | 578.4803 | 219.0408 | 642.237 | 76.9704 | 348.5646 | 564.831 | 220.216 | 517.9119 | 789.2402 | 122.1942 | 411.3759 | 660.3996 | 155.2008 | 468.8482 | 338.0833 | 611.6868 | 215.2103 | 595.52 | 116.2715 | 17.4239 | 3.439 | 0.094067 | -38.2994 | 3.1244 | 4655.96 | 49.25 | -3.1779 | 1.0731 | -0.46303 | -0.49553 | 4.3712 | 4.14 | 3.7336 | -2.9445 | -7.356 | 37.8379 | -21.9145 | -17.1327 | -4.8758 | -6.5533
42810.4486 | 737 | 18.5331 | 18.57 | 18.5312 | 18.5166 | 17.7952 | 16.3725 | 14.4194 | 16.5942 | 17.1057 | 17.2011 | 17.204 | 16.7161 | 15.7361 | 14.3541 | 14.8965 | 15.0189 | 15.9185 | 13.3749 | 13.7648 | 21.9184 |  |  |  | 16.6638 | 17.3375 | 50.2491 | 790.5678 | 682.2945 | 952.2082 | 17.249 | 17.1564 | 27.0964 | 16.8679 | 17.2234 | 40.0096 | 336.8252 | 794.3366 |  |  | 673.7921 | 565.3937 | 753.1163 |  | 28.5097 | 57.9545 | 38.0197 | 65.0472 | 119.2244 | 316.2883 | 528.2647 | 10.3809 | 17.7405 | 17.3766 | 33.476 | 9.9993 | 43.0277 | 47.1101 | 44.2423 | 15.0821 |  |  | -0.38682 | 0.77417 | -0.008664 | -0.31607 | 7.8619 | 7.4112 | 5.4152 | 24.3631 | 4.6856 | 12.9581 | 42.1106 | 0.0041168 | 0.0041349 | 0.39427 | 16.357 | 16.6299 | 17.1443 | 17.4651 | 17.4 | 16.3386 | 14.6701 | 16.748 | 17.0863 | 17.3912 | 17.4191 | 17.1288 | 16.2712 | 14.4532 | 340.0424 | 98.6784 | 220.2331 | 152.0239 | 129.3617 | 144.8791 | 68.8693 | 15.8445 | 15.7322 | 16.1309 | 14.5405 | 17.6547 | 23.5911 |  |  |  | 333.0006 | 793.5458 | 886.017 | 833.2397 | 18.8978 | 7.9773 | 425.1648 |  |  | 33.8012 |  |  | 17.0772 | 18.4695 | 95.027 | 16.4038 | 16.7812 | 26.4501 | 714.9535 | 869.6888 | 547.4541 | 588.7723 | 763.9424 |  | 363.4944 | 729.3789 | 285.8198 | 936.8231 | 697.7115 | 766.7392 |  | 392.3623 |  |  | 160.1971 | 341.8836 | 550.3689 | [6 empty] | 867.1666 |  |  | 523.2435 |  |  | 200.3356 | 840.5873 | 968.1111 | 88.4574 | 428.3472 | 631.6205 | 142.0822 | 480.6637 | 763.746 | 524.1088 | 991.5591 | 193.8858 | 602.1774 | 237.5906 | 672.7636 | 81.1956 | 363.6345 | 572.4624 | 233.5978 | 553.1615 | 800.3195 | 130.4247 | 431.9842 | 668.9727 | 168.5949 | 483.57 | 373.2121 | 639.2193 | 239.2112 | 619.4843 | 127.6637 | 17.3569 | 3.4809 | 0.095261 | -38.3045 | 3.1244 | 4962.32 | 49.07 | -1.5172 | 1.1158 | -0.11803 | -0.71293 | 4.7441 | 4.6061 | 3.9373 | -1.8088 | -6.7858 | 43.7327 | -19.9534 | -16.0423 | -3.7143 | -6.2412
42810.4486 | 738 | 18.52 | 18.5589 | 18.5245 | 18.5148 | 17.7935 | 16.3694 | 14.4173 | 16.5832 | 17.0897 | 17.1866 | 17.1927 | 16.7109 | 15.7321 | 14.3453 | 14.8912 | 15.0155 | 15.9236 | 13.3743 | 13.7602 | 21.9655 |  |  |  | 16.6632 | 17.3461 | 51.9839 | 824.232 | 689.8329 | 943.9052 | 17.2494 | 17.163 | 27.1465 | 16.8715 | 17.2276 | 49.8444 | 350.9843 | 790.9161 |  |  | 685.8232 | 575.7402 | 752.7437 |  | 30.803 | 63.1695 | 42.1146 | 73.0915 | 146.5509 | 343.0103 | 546.955 | 10.9362 | 18.8205 | 19.9535 | 36.1059 | 10.0337 | 43.0358 | 47.1385 | 44.4233 | 15.1299 |  |  | 0.49831 | 0.55601 | 0.078732 | -0.060454 | 7.946 | 7.86 | 6.5763 | 28.1231 | 5.7522 | 17.0169 | 46.0083 | 0.004061 | 0.0040626 | 0.43109 | 16.3604 | 16.6332 | 17.1529 | 17.4734 | 17.4072 | 16.3386 | 14.6779 | 16.7514 | 17.0919 | 17.3904 | 17.4246 | 17.1253 | 16.2732 | 14.4568 | 329.1043 | 97.638 | 211.4859 | 146.5513 | 124.9264 | 148.2206 | 70.5162 | 15.8409 | 15.7339 | 16.137 | 14.5446 | 17.6934 | 23.6782 |  |  |  | 355.4336 | 820.0655 | 908.9189 | 884.1556 | 19.7515 | 10.5586 | 437.8995 |  |  | 35.3171 |  |  | 17.0935 | 18.4872 | 102.8054 | 16.4071 | 16.7871 | 26.5915 | 720.13 | 872.8577 | 567.1915 | 611.5533 | 765.3694 |  | 382.0259 | 721.8629 | 301.2039 | 919.7614 | 724.1519 | 785.1734 |  | 407.476 |  |  | 173.4331 | 368.5484 | 564.8509 | [6 empty] | 884.3824 |  |  | 543.1717 |  |  | 214.9906 | 892.0605 | 983.6575 | 97.7635 | 450.6535 | 641.5477 | 153.6605 | 506.6846 | 771.8136 | 567.2532 | 1022.1583 | 216.7976 | 624.7315 | 263.3418 | 704.1893 | 86.1673 | 380.2624 | 581.5121 | 248.2022 | 591.744 | 816.7425 | 140.0711 | 460.6293 | 675.5541 | 185.4953 | 501.044 | 411.9223 | 669.1347 | 263.8855 | 644.7391 | 162.413 | 17.2982 | 3.5155 | 0.094465 | -38.3486 | 3.1244 | 5352.95 | 50.29 | 1.7162 | 0.95298 | 0.35861 | -0.31424 | 4.8763 | 4.8498 | 4.4361 | -0.20087 | -5.5147 | 50.657 | -18.3107 | -14.8724 | -2.5561 | -5.8349
42810.4486 | 739 | 18.5265 | 18.5591 | 18.5262 | 18.5164 | 17.7904 | 16.3712 | 14.418 | 16.5832 | 17.0919 | 17.1879 | 17.1935 | 16.7102 | 15.7311 | 14.3448 | 14.8988 | 15.0146 | 15.9434 | 13.3825 | 13.7674 | 22.0217 |  |  |  | 16.6665 | 17.3696 | 53.4162 | 847.6214 | 696.1163 | 933.7332 | 17.2495 | 17.1716 | 27.1679 | 16.8729 | 17.2418 | 58.5402 | 365.6059 | 773.2702 |  |  | 699.6313 | 585.5674 | 755.0762 |  | 33.9119 | 69.4996 | 47.0647 | 87.7179 | 178.2086 | 375.6796 | 570.3071 | 11.6015 | 19.9489 | 22.6018 | 38.9321 | 10.0716 | 43.0285 | 47.1563 | 44.6162 | 15.1728 |  |  | 2.5873 | 0.38581 | -0.24522 | -1.1657 | 8.1852 | 9.0645 | 7.0015 | 34.4938 | 8.5062 | 20.3804 | 55.4696 | 0.0039213 | 0.004038 | 0.44417 | 16.3539 | 16.6285 | 17.1426 | 17.452 | 17.3927 | 16.3405 | 14.6574 | 16.7477 | 17.0731 | 17.3825 | 17.4201 | 17.1074 | 16.2679 | 14.4522 | 322.9897 | 105.5577 | 222.6878 | 149.6352 | 131.877 | 151.9676 | 72.7069 | 15.8395 | 15.7384 | 16.1433 | 14.5468 | 17.7234 | 23.763 |  |  |  | 379.5691 | 855.4236 | 925.6581 | 890.2848 | 21.1568 | 20.7129 | 445.4033 |  |  | 37.0851 |  |  | 17.1123 | 18.502 | 113.541 | 16.3985 | 16.7916 | 26.7289 | 726.6851 | 876.0823 | 588.5787 | 636.5564 | 773.4455 |  | 400.4409 | 717.0859 | 314.7885 | 913.881 | 747.7382 | 789.1559 |  | 421.7399 |  |  | 191.686 | 405.6532 | 582.3608 | [6 empty] | 900.7504 |  |  | 566.63 |  |  | 232.7044 | 937.1254 | 998.9752 | 108.6972 | 477.485 | 647.1712 | 167.3446 | 538.2081 | 779.4091 | 618.7177 | 1046.8429 | 245.5239 | 650.9184 | 293.8212 | 741.1869 | 92.1065 | 402.8894 | 591.8988 | 265.5206 | 627.0413 | 827.8686 | 151.8569 | 489.5333 | 680.5737 | 203.1596 | 521.5305 | 456.1762 | 699.4547 | 293.8341 | 670.3203 | 149.2473 | 17.2572 | 3.5653 | 0.094023 | -38.302 | 3.1244 | 5698.5 | 48.84 | 3.8942 | 0.80128 | -0.63881 | -1.3928 | 5.0786 | 5.3445 | 4.6971 | 1.3114 | -4.3999 | 56.9729 | -17.1505 | -15.8533 | -1.3797 | -3.8948
42810.4486 | 740 | 18.5297 | 18.5611 | 18.528 | 18.5234 | 17.7937 | 16.3738 | 14.4169 | 16.5868 | 17.0966 | 17.1939 | 17.1948 | 16.7177 | 15.7307 | 14.3476 | 14.8988 | 15.0124 | 15.9472 | 13.3805 | 13.77 | 22.0835 |  |  |  | 16.6662 | 17.3812 | 56.1059 | 861.7044 | 702.0309 | 932.5609 | 17.2537 | 17.1747 | 27.2128 | 16.8675 | 17.2511 | 65.4064 | 380.7807 | 764.051 |  |  | 713.0734 | 596.039 | 762.4344 |  | 38.2152 | 77.95 | 53.6183 | 106.7884 | 216.2667 | 419.2052 | 595.3144 | 12.4362 | 21.5451 | 25.2282 | 42.849 | 10.1079 | 43.0112 | 47.167 | 44.7792 | 15.227 |  |  | 3.5473 | 0.10851 | -1.1139 | -0.79839 | 8.9363 | 8.6393 | 6.7912 | 40.237 | 8.1055 | 21.7454 | 74.443 | 0.0039345 | 0.0039164 | 0.42577 | 16.357 | 16.6225 | 17.1407 | 17.4596 | 17.3975 | 16.3402 | 14.672 | 16.7488 | 17.0852 | 17.3843 | 17.426 | 17.116 | 16.2696 | 14.4424 | 314.5444 | 116.8714 | 248.7153 | 159.7279 | 141.7948 | 156.152 | 75.6743 | 15.8425 | 15.7474 | 16.1481 | 14.5472 | 17.7562 | 23.8616 |  |  |  | 406.3174 | 869.3188 | 917.1426 | 925.3507 | 32.1608 | 15.0652 | 454.1049 |  |  | 38.8337 |  |  | 17.1421 | 18.5249 | 123.4805 | 16.4063 | 16.8018 | 26.8909 | 731.8714 | 881.0024 | 605.0172 | 655.6713 | 783.2563 |  | 418.551 | 731.7253 | 329.5769 | 914.5835 | 767.1631 | 792.0298 |  | 436.0435 |  |  | 213.3883 | 444.5826 | 598.8517 | [6 empty] | 915.0985 |  |  | 589.7489 |  |  | 258.2075 | 981.0581 | 1013.8454 | 120.9157 | 507.3187 | 654.1295 | 184.1025 | 573.1758 | 785.4301 | 681.3285 | 1067.345 | 276.6814 | 676.8267 | 330.2734 | 775.6426 | 98.7068 | 428.4467 | 602.227 | 286.6992 | 662.7017 | 839.9931 | 170.1993 | 520.8591 | 688.1673 | 226.3506 | 545.7275 | 502.8916 | 727.6444 | 336.0121 | 698.3267 | 165.6562 | 17.1826 | 3.6066 | 0.098641 | -38.2368 | 3.1244 | 6073.45 | 49.57 | 4.5576 | 0.43015 | -1.3782 | -1.1668 | 5.4816 | 5.3898 | 4.7786 | 2.8488 | -3.688 | 62.3159 | -15.6733 | -18.3873 | -0.23313 | -2.3323
42810.4486 | 741 | 18.526 | 18.5664 | 18.5239 | 18.5257 | 17.7944 | 16.3786 | 14.4235 | 16.5888 | 17.1004 | 17.1987 | 17.2064 | 16.7178 | 15.7335 | 14.3511 | 14.8914 | 15.0127 | 15.9438 | 13.3805 | 13.7606 | 22.1427 |  |  |  | 16.6741 | 17.3942 | 59.4004 | 865.4537 | 705.5805 | 920.7047 | 17.2549 | 17.168 | 27.2828 | 16.8692 | 17.2536 | 71.1669 | 396.6477 | 800.4966 |  |  | 727.1124 | 607.8951 | 763.4212 |  | 42.0436 | 85.9379 | 59.3091 | 126.3743 | 256.8696 | 461.4356 | 619.0994 | 13.5523 | 23.1695 | 27.5002 | 46.7515 | 10.1615 | 43.0306 | 47.1819 | 44.9544 | 15.306 |  |  | 3.4047 | -0.95536 | -1.5825 | -1.7637 | 7.7449 | 6.0588 | 5.3889 | 42.2905 | 9.1388 | 23.0474 | 87.8819 | 0.0038376 | 0.0038162 | 0.36891 | 16.3609 | 16.6332 | 17.1449 | 17.4601 | 17.4093 | 16.3406 | 14.6675 | 16.7504 | 17.0864 | 17.3877 | 17.4276 | 17.1193 | 16.27 | 14.4466 | 336.6314 | 150.7024 | 263.3299 | 167.1834 | 145.8777 | 162.3798 | 79.0392 | 15.8345 | 15.7408 | 16.1517 | 14.5568 | 17.7927 | 23.9785 |  |  |  | 430.665 | 860.3951 | 902.5756 | 903.1575 | 49.6083 | 26.9049 | 463.3067 |  |  | 42.0782 |  |  | 17.1783 | 18.5432 | 130.8612 | 16.4103 | 16.8078 | 27.0504 | 735.7839 | 884.8895 | 620.9532 | 673.6091 | 795.0761 |  | 438.9674 | 737.4539 | 345.5972 | 914.9489 | 783.9722 | 807.6034 |  | 453.4766 |  |  | 236.9902 | 474.4142 | 611.9092 | [6 empty] | 920.9849 |  |  | 609.9467 |  |  | 296.4591 | 1020.3358 | 1024.7047 | 135.7223 | 543.5275 | 661.2517 | 218.759 | 614.0308 | 796.4224 | 739.5926 | 1082.4705 | 311.1409 | 705.129 | 377.0399 | 811.2048 | 106.8832 | 460.7873 | 611.0301 | 316.5266 | 698.2818 | 853.4787 | 196.5009 | 565.094 | 697.6429 | 256.4839 | 573.3287 | 546.1107 | 758.0928 | 394.262 | 731.4883 | 162.9612 | 17.1155 | 3.6449 | 0.099111 | -38.1865 | 3.1245 | 6477.55 | 50.21 | 4.4431 | -1.2908 | -1.6612 | -1.7538 | 5.2565 | 4.6492 | 4.3847 | 4.6892 | -2.5742 | 67.17 | -17.3212 | -19.6044 | 1.2237 | 0.78809
42810.4486 | 742 | 18.5261 | 18.5671 | 18.513 | 18.5163 | 17.7904 | 16.37 | 14.4153 | 16.5894 | 17.0921 | 17.1982 | 17.2037 | 16.7177 | 15.7267 | 14.3499 | 14.8893 | 15.0106 | 15.9453 | 13.3809 | 13.7616 | 22.2044 |  |  |  | 16.6749 | 17.4074 | 61.1988 | 861.9532 | 704.7952 | 905.271 | 17.2522 | 17.1828 | 27.387 | 16.8709 | 17.2534 | 77.7986 | 412.5909 | 829.696 |  |  | 739.6507 | 617.7238 | 765.454 |  | 45.8698 | 94.1232 | 64.4881 | 144.4047 | 295.7446 | 505.318 | 642.9839 | 15.1038 | 24.9099 | 28.8954 | 50.9198 | 10.1924 | 43.0533 | 47.1754 | 45.1348 | 15.3944 |  |  | 5.4385 | -0.38038 | -1.4832 | -1.947 | 5.6638 | 6.1515 | 5.4303 | 35.9204 | 8.1016 | 19.6354 | 93.2405 | 0.0037538 | 0.0038063 | 0.32552 | 16.3658 | 16.6275 | 17.1431 | 17.4609 | 17.4019 | 16.3386 | 14.6606 | 16.7495 | 17.0785 | 17.3767 | 17.4191 | 17.1124 | 16.2726 | 14.4448 | 404.1584 | 200.4438 | 289.9839 | 186.9622 | 162.7403 | 171.6911 | 83.401 | 15.8285 | 15.7414 | 16.1551 | 14.5544 | 17.822 | 24.068 |  |  |  | 450.555 | 853.4039 | 894.3607 | 879.5633 | 55.9136 | 24.1066 | 472.4053 |  |  | 55.3546 |  |  | 17.207 | 18.5542 | 143.656 | 16.4129 | 16.8149 | 27.2252 | 739.3197 | 872.2566 | 636.1008 | 689.6659 | 800.9051 |  | 459.8154 | 757.0565 | 363.1108 | 895.4634 | 794.5941 | 805.2066 |  | 469.9871 |  |  | 267.5674 | 495.5692 | 624.793 | [6 empty] | 904.3597 |  |  | 614.6852 |  |  | 344.8011 | 1046.9373 | 1025.5344 | 154.295 | 583.8006 | 670.8254 | 271.171 | 655.8913 | 815.2023 | 790.1882 | 1090.0933 | 350.8861 | 733.2767 | 431.4577 | 841.8446 | 118.8951 | 496.4544 | 622.111 | 361.3326 | 728.6523 | 861.7008 | 229.8415 | 611.8826 | 708.0846 | 288.4502 | 602.7452 | 583.0415 | 789.2923 | 453.2543 | 762.5765 | 161.2443 | 17.0501 | 3.6816 | 0.099263 | -38.2864 | 3.1245 | 6897.3 | 48.05 | 5.579 | -0.8237 | -1.6265 | -1.8636 | 4.6275 | 4.8225 | 4.5311 | 6.8903 | -1.6506 | 70.8954 | -23.6094 | -22.0373 | 2.7361 | 3.6366
42810.4486 | 743 | 18.5285 | 18.5706 | 18.5189 | 18.5134 | 17.7944 | 16.3747 | 14.4099 | 16.5877 | 17.0993 | 17.1911 | 17.1996 | 16.7124 | 15.7328 | 14.3499 | 14.8772 | 15.0064 | 15.9391 | 13.3752 | 13.7568 | 22.2634 |  |  |  | 16.6646 | 17.4134 | 61.7813 | 850.5622 | 698.0086 | 888.3238 | 17.2405 | 17.1768 | 27.5042 | 16.8688 | 17.261 | 74.6088 | 428.0185 | 839.4563 |  |  | 744.5332 | 623.7887 | 752.7766 |  | 49.8444 | 102.0035 | 69.5472 | 155.1805 | 329.3614 | 546.6275 | 672.9931 | 16.2722 | 26.7853 | 29.4523 | 55.4359 | 10.2334 | 43.0947 | 47.1742 | 45.3183 | 15.4553 |  |  | 3.1833 | -0.057737 | -1.3479 | -1.1513 | 6.7139 | 5.9228 | 4.8336 | 28.2979 | 8.2651 | 21.5981 | 92.9446 | 0.0036651 | 0.0037193 | 0.22746 | 16.3768 | 16.6292 | 17.1439 | 17.4605 | 17.4025 | 16.3369 | 14.6652 | 16.7461 | 17.0823 | 17.3853 | 17.4245 | 17.1187 | 16.2716 | 14.4515 | 467.5991 | 205.9408 | 320.9501 | 196.0384 | 167.6334 | 182.8632 | 88.2573 | 15.8286 | 15.739 | 16.1562 | 14.5543 | 17.8516 | 24.1789 |  |  |  | 471.0093 | 855.6197 | 887.7516 | 888.6527 | 64.1361 | 28.4402 | 484.0215 |  |  | 75.3466 |  |  | 17.2364 | 18.5712 | 150.1111 | 16.4102 | 16.8268 | 27.4412 | 747.1999 | 842.735 | 641.7873 | 694.2838 | 812.4787 |  | 478.9812 | 763.4077 | 379.6744 | 862.0622 | 799.5618 | 798.4067 |  | 482.9478 |  |  | 300.5802 | 510.1386 | 643.2542 | [6 empty] | 868.8091 |  |  | 598.1553 |  |  | 401.492 | 1057.6683 | 1015.1442 | 179.6757 | 623.2754 | 679.8173 | 312.8238 | 694.6714 | 838.3679 | 823.624 | 1084.2575 | 399.9569 | 758.5566 | 482.1238 | 866.6228 | 132.2787 | 532.3149 | 636.0019 | 401.3146 | 750.7955 | 864.0647 | 275.4352 | 647.8074 | 717.0034 | 325.1882 | 628.3326 | 605.0995 | 811.5666 | 497.508 | 787.6862 | 158.4705 | 16.9902 | 3.7039 | 0.099813 | -38.2484 | 3.1244 | 7373.93 | 43.83 | 4.2375 | -0.32434 | -1.5671 | -1.4483 | 5.1701 | 4.856 | 4.3868 | 8.8812 | -0.36089 | 73.3423 | -29.1855 | -24.8874 | 4.6837 | 5.7867
42810.4486 | 744 | 18.5271 | 18.5622 | 18.5178 | 18.5142 | 17.7955 | 16.3728 | 14.4163 | 16.5854 | 17.0964 | 17.1944 | 17.2025 | 16.7107 | 15.7236 | 14.3433 | 14.8829 | 15.009 | 15.9527 | 13.3806 | 13.7589 | 22.3275 |  |  |  | 16.6716 | 17.4217 | 60.5407 | 834.1431 | 686.5075 | 866.7748 | 17.2427 | 17.1773 | 27.6494 | 16.8698 | 17.2619 | 77.4353 | 441.1165 | 844.8913 |  | 256.488 | 755.3945 | 625.8879 | 754.0218 |  | 52.6567 | 107.6763 | 73.4461 | 162.9694 | 349.3843 | 572.7697 | 692.6336 | 16.6546 | 28.4502 | 30.8115 | 59.4778 | 10.2876 | 43.13 | 47.1567 | 45.5008 | 15.5322 |  |  | 3.1866 | -0.11688 | -0.83006 | -1.3293 | 6.8677 | 5.9037 | 5.4796 | 24.8322 | 7.8722 | 23.5532 | 91.7226 | 0.0036437 | 0.0036437 | 0.12938 | 16.3768 | 16.6324 | 17.143 | 17.4536 | 17.4025 | 16.3414 | 14.663 | 16.7413 | 17.0901 | 17.3814 | 17.4244 | 17.1198 | 16.2738 | 14.4514 | 541.5427 | 200.1525 | 371.4053 | 216.684 | 188.7634 | 195.3938 | 93.8752 | 15.8341 | 15.7447 | 16.1676 | 14.5523 | 17.8975 | 24.3003 |  |  |  | 490.7941 | 839.3112 | 865.8803 | 866.6661 | 62.5968 | 33.2209 | 497.1339 |  |  | 84.3142 |  |  | 17.2631 | 18.5918 | 147.1299 | 16.4101 | 16.8334 | 27.6813 | 760.957 | 814.0243 | 644.983 | 697.2977 | 828.6446 |  | 498.973 | 771.4772 | 396.8914 | 827.1593 | 803.5101 | 805.7172 |  | 498.7053 |  |  | 321.2705 | 521.8631 | 669.9676 | [6 empty] | 834.1863 |  |  | 571.9742 |  |  | 450.8666 | 1049.7042 | 1000.2701 | 216.061 | 670.2741 | 693.9099 | 344.0495 | 731.0065 | 865.1491 | 833.0173 | 1068.5097 | 462.6333 | 787.8421 | 522.1569 | 888.2693 | 142.5838 | 565.8035 | 648.1419 | 426.8552 | 763.8784 | 858.8407 | 321.4441 | 672.5021 | 727.7154 | 372.2175 | 648.7781 | 617.5843 | 822.8529 | 530.6763 | 809.2891 | 196.0412 | 16.9311 | 3.7177 | 0.10308 | -38.245 | 3.1244 | 7805.9 | 31.95 | 4.2002 | -0.46494 | -1.239 | -1.568 | 5.3117 | 4.9249 | 4.7447 | 10.995 | 1.0234 | 75.533 | -35.7283 | -29.8078 | 6.0661 | 8.8712
42810.4487 | 745 | 18.5323 | 18.5703 | 18.5216 | 18.5153 | 17.7952 | 16.3714 | 14.418 | 16.5894 | 17.1003 | 17.1962 | 17.2015 | 16.72 | 15.7277 | 14.3439 | 14.8916 | 15.0166 | 15.9631 | 13.3903 | 13.7666 | 22.389 |  |  |  | 16.6767 | 17.4348 | 58.4814 | 817.7694 | 671.4981 | 846.1953 | 17.2657 | 17.2374 | 27.8075 | 16.915 | 17.6112 | 81.438 | 454.125 | 833.1228 |  | 121.291 | 773.51 | 631.9437 | 761.1182 |  | 56.0299 | 114.8337 | 78.5377 | 171.252 | 363.6332 | 598.287 | 714.7871 | 17.6201 | 30.5272 | 32.6627 | 64.4766 | 10.3398 | 43.1904 | 47.1364 | 45.7098 | 15.6091 |  |  | 4.1144 | 0.001403 | -0.42068 | -1.0113 | 6.1133 | 4.0191 | 5.3528 | 19.7422 | 8.6369 | 23.4406 | 95.4377 | 0.0036158 | 0.0036289 | 0.052753 | 16.3758 | 16.6247 | 17.1424 | 17.4651 | 17.4008 | 16.3456 | 14.6651 | 16.7492 | 17.0921 | 17.3942 | 17.4245 | 17.1173 | 16.2693 | 14.4512 | 572.8429 | 215.5818 | 411.5208 | 234.2196 | 202.0786 | 208.379 | 99.8853 | 15.8439 | 15.7596 | 16.1788 | 14.5754 | 17.9494 | 24.4509 |  |  |  | 505.7973 | 802.1258 | 830.5658 | 799.4318 | 64.409 | 32.5315 | 515.8075 |  |  | 95.3605 |  |  | 17.2892 | 18.6084 | 140.4038 | 16.4193 | 16.8373 | 27.9391 | 777.2439 | 791.6817 | 654.6765 | 706.287 | 860.5664 |  | 524.3207 | 803.1047 | 418.7339 | 794.9577 | 807.2339 | 816.5209 |  | 519.1562 |  |  | 334.6082 | 536.9961 | 706.1698 | [6 empty] | 806.0635 |  |  | 546.0555 |  |  | 491.5025 | 1028.7203 | 987.3816 | 254.0305 | 724.4494 | 712.4216 | 371.2476 | 764.9406 | 885.2086 | 832.3489 | 1047.3501 | 531.4131 | 815.0873 | 558.1333 | 905.274 | 150.9788 | 593.6543 | 658.57 | 447.664 | 771.2238 | 848.6699 | 360.5214 | 690.7342 | 737.2324 | 419.4447 | 669.0585 | 626.8564 | 825.2922 | 561.1448 | 822.2689 | 192.3059 | 16.8868 | 3.7282 | 0.10516 | -38.2893 | 3.1244 | 8207.98 | 24.84 | 4.7294 | 0.051417 | -0.89032 | -1.3804 | 5.0865 | 4.1243 | 4.7596 | 13.5918 | 2.3162 | 77.5905 | -37.4476 | -33.5282 | 7.3351 | 12.718
42810.4487 | 746 | 18.5142 | 18.5587 | 18.5155 | 18.5118 | 17.7903 | 16.3693 | 14.4144 | 16.5847 | 17.0928 | 17.1951 | 17.1966 | 16.7103 | 15.7274 | 14.3377 | 14.8881 | 15.0213 | 15.9597 | 13.3827 | 13.7664 | 22.4492 |  |  |  | 16.6727 | 17.4405 | 57.0352 | 802.995 | 655.8502 | 829.3921 | 17.2452 | 17.2494 | 27.9257 | 16.9181 | 17.7214 | 82.9338 | 466.0239 | 822.0908 |  | 433.8578 | 791.4552 | 634.0794 | 742.7974 |  | 59.1238 | 121.3574 | 83.2597 | 178.5971 | 375.2947 | 609.8027 | 735.4916 | 18.6064 | 32.4654 | 33.8879 | 69.1504 | 10.4127 | 43.2858 | 47.1532 | 45.892 | 15.6982 |  |  | 3.2654 | 0.080255 | -0.67695 | -1.2643 | 6.384 | 4.7084 | 6.7689 | 18.0153 | 10.1266 | 26.0383 | 99.1305 | 0.0035008 | 0.0035336 | 0.0020239 | 16.3802 | 16.6384 | 17.1421 | 17.462 | 17.4097 | 16.3447 | 14.6794 | 16.752 | 17.0893 | 17.3897 | 17.4261 | 17.1212 | 16.2746 | 14.4551 | 591.897 | 229.5468 | 424.6062 | 257.7724 | 219.6082 | 221.3432 | 105.9602 | 15.825 | 15.742 | 16.1676 | 14.5628 | 17.973 | 24.5639 |  |  |  | 514.5433 | 772.5251 | 803.6745 | 756.0655 | 73.3872 | 33.0425 | 543.0077 |  |  | 105.399 |  |  | 17.3002 | 18.6128 | 134.699 | 16.4152 | 16.8427 | 28.2146 | 793.6422 | 769.542 | 667.8158 | 721.6553 | 921.8605 |  | 549.1151 | 851.7496 | 441.1518 | 769.3125 | 808.9716 | 831.941 |  | 537.7972 |  |  | 351.3541 | 556.8132 | 746.0235 | [6 empty] | 779.8643 |  |  | 523.4901 |  |  | 528.232 | 1005.8597 | 974.6271 | 294.1665 | 774.3149 | 729.2354 | 400.9099 | 797.237 | 895.0444 | 831.0414 | 1025.0339 | 586.8151 | 840.8305 | 593.3031 | 919.488 | 157.8991 | 615.7835 | 667.8141 | 462.5517 | 774.5587 | 837.8288 | 391.8907 | 711.5425 | 745.775 | 459.2861 | 689.8526 | 634.8221 | 824.1933 | 590.8595 | 835.1581 | 186.6954 | 16.8392 | 3.7359 | 0.10584 | -38.2934 | 3.1245 | 8646.1 | 19.94 | 4.1815 | 0.39213 | -1.1389 | -1.5564 | 5.2322 | 4.4934 | 5.3876 | 15.5657 | 3.3553 | 78.8493 | -37.7825 | -34.2339 | 9.2384 | 15.1189
42810.4487 | 747 | 18.5249 | 18.5625 | 18.5239 | 18.5197 | 17.7985 | 16.3749 | 14.4211 | 16.5876 | 17.1078 | 17.194 | 17.2037 | 16.7184 | 15.73 | 14.3438 | 14.8697 | 15.0092 | 15.9552 | 13.3788 | 13.7626 | 22.5204 |  |  |  | 16.6696 | 17.4418 | 56.6508 | 790.9311 | 644.3306 | 817.3889 | 17.2453 | 17.1931 | 28.0616 | 16.8689 | 17.2829 | 82.4591 | 476.2288 | 814.1045 |  | 599.7691 | 802.7993 | 628.4555 | 724.657 |  | 62.182 | 127.9482 | 87.9487 | 185.9288 | 392.8659 | 625.7688 | 756.7578 | 18.7885 | 34.5577 | 35.6975 | 74.1762 | 10.4955 | 43.4079 | 47.1958 | 46.0704 | 15.8025 |  |  | 3.3923 | 0.10851 | -0.59875 | -0.82271 | 6.1468 | 5.194 | 5.2654 | 13.2933 | 9.8427 | 26.4143 | 94.5888 | 0.0034285 | 0.0034564 | -0.00083125 | 16.3759 | 16.6322 | 17.1386 | 17.4526 | 17.4006 | 16.3356 | 14.662 | 16.7464 | 17.0848 | 17.3777 | 17.423 | 17.113 | 16.2698 | 14.4426 | 618.2976 | 252.4547 | 452.1842 | 271.6477 | 236.0842 | 235.8954 | 112.4825 | 15.8281 | 15.7537 | 16.1783 | 14.581 | 18.0291 | 24.6893 |  |  |  | 521.5516 | 748.596 | 780.2183 | 721.829 | 78.0371 | 35.9679 | 583.0527 |  |  | 116.3212 |  |  | 17.3182 | 18.6231 | 132.7855 | 16.4188 | 16.8561 | 28.5053 | 805.7602 | 750.1269 | 683.1477 | 741.5057 | 960.1788 |  | 574.2912 | 904.9172 | 466.8962 | 746.7052 | 810.0548 | 856.2607 |  | 557.4923 |  |  | 370.9224 | 576.9772 | 774.187 | [6 empty] | 755.7342 |  |  | 505.7164 |  |  | 565.0882 | 986.3383 | 961.619 | 348.1571 | 811.2149 | 744.5013 | 434.2411 | 823.7591 | 903.4675 | 832.2736 | 1005.9362 | 632.9965 | 859.4918 | 628.1345 | 932.1518 | 164.8653 | 636.123 | 674.7941 | 476.2538 | 778.5087 | 828.6093 | 420.1566 | 725.7276 | 755.8961 | 494.8648 | 706.4038 | 645.4376 | 821.642 | 613.1744 | 848.4989 | 184.475 | 16.7888 | 3.7425 | 0.10628 | -38.3096 | 3.1245 | 9068.9 | 16.44 | 4.2387 | 0.45976 | -1.08 | -1.2659 | 5.1803 | 4.7619 | 4.7945 | 18.5239 | 4.8394 | 79.8192 | -38.6819 | -36.4907 | 10.9801 | 17.0519
42810.4487 | 748 | 18.527 | 18.5598 | 18.5257 | 18.5216 | 17.7928 | 16.3787 | 14.4175 | 16.5813 | 17.1003 | 17.1946 | 17.2023 | 16.7173 | 15.7307 | 14.3471 | 14.8801 | 15.0158 | 15.9655 | 13.3834 | 13.7618 | 22.6024 |  |  |  | 16.674 | 17.4516 | 56.1419 | 780.3119 | 638.1325 | 806.5605 | 17.2429 | 17.1987 | 28.2451 | 16.8654 | 17.2868 | 82.2262 | 485.6981 | 807.1376 |  | 595.3874 | 814.5004 | 629.0692 | 715.9196 |  | 65.3436 | 134.6718 | 92.3799 | 192.2669 | 398.4758 | 637.2464 | 775.2955 | 18.436 | 36.9209 | 37.601 | 79.8881 | 10.597 | 43.5219 | 47.2418 | 46.2471 | 15.9527 |  |  | 5.7441 | 0.1854 | -1.1823 | -1.5994 | 6.1199 | 3.2352 | 5.2095 | 9.1272 | 9.9844 | 26.3432 | 123.3036 | 0.0033809 | 0.0034203 | -0.00085753 | 16.3883 | 16.6291 | 17.147 | 17.4654 | 17.3977 | 16.3393 | 14.6626 | 16.7445 | 17.0854 | 17.3776 | 17.4192 | 17.1141 | 16.2674 | 14.4434 | 658.7394 | 290.3649 | 469.8488 | 279.1408 | 234.1492 | 251.9855 | 119.3858 | 15.8301 | 15.7511 | 16.1825 | 14.5878 | 18.0741 | 24.8176 |  |  |  | 527.8618 | 730.0527 | 760.9202 | 701.8831 | 74.805 | 34.5244 | 621.4428 |  |  | 135.1679 |  |  | 17.34 | 18.6402 | 131.8084 | 16.4266 | 16.8665 | 28.8439 | 815.0659 | 736.9055 | 702.9366 | 764.5392 | 954.6139 |  | 599.7315 | 904.0281 | 495.0005 | 729.7309 | 812.0239 | 874.12 |  | 579.7624 |  |  | 383.1258 | 601.171 | 791.4933 | [6 empty] | 740.6748 |  |  | 489.6988 |  |  | 598.778 | 968.3682 | 952.6617 | 389.9177 | 839.6484 | 766.599 | 471.8121 | 846.4361 | 909.4762 | 831.9677 | 989.6663 | 667.9021 | 875.9819 | 660.7643 | 944.2557 | 173.3752 | 657.4644 | 681.4349 | 487.6933 | 776.7542 | 819.6267 | 450.7052 | 739.178 | 763.5669 | 521.525 | 723.6353 | 653.3076 | 814.2727 | 643.5628 | 860.0724 | 215.5109 | 16.7465 | 3.7492 | 0.10585 | -38.3062 | 3.1245 | 9466.41 | 13.87 | 5.4882 | 0.60597 | -1.5302 | -1.7798 | 5.2018 | 3.7821 | 4.7993 | 23.0579 | 8.3791 | 80.9145 | -40.883 | -37.5942 | 12.4069 | 18.5081
42810.4487 | 749 | 18.5225 | 18.5558 | 18.5255 | 18.5214 | 17.7906 | 16.3728 | 14.4148 | 16.5873 | 17.0942 | 17.1936 | 17.2002 | 16.7114 | 15.728 | 14.339 | 14.8899 | 15.0235 | 15.9747 | 13.3923 | 13.774 | 22.6692 |  |  |  | 16.6863 | 17.4738 | 57.3531 | 771.589 | 634.7176 | 797.5472 | 17.2332 | 17.2045 | 28.3702 | 16.8714 | 17.2931 | 92.1183 | 495.4381 | 805.3517 |  | 582.5127 | 820.7336 | 631.295 | 725.6913 |  | 67.9211 | 139.8732 | 95.8459 | 197.4056 | 409.116 | 650.0802 | 793.5982 | 18.4941 | 38.9815 | 38.2896 | 84.8199 | 10.6918 | 43.6288 | 47.2871 | 46.4063 | 16.0741 |  |  | 3.9166 | 0.3247 | -1.706 | -1.5363 | 5.6507 | 4.1584 | 5.0078 | 8.1211 | 11.1675 | 24.751 | 150.9004 | 0.0032659 | 0.0033841 | -0.00082632 | 16.3903 | 16.634 | 17.1437 | 17.4642 | 17.395 | 16.3373 | 14.6714 | 16.7463 | 17.0838 | 17.3819 | 17.4167 | 17.1201 | 16.2689 | 14.4504 | 695.1061 | 288.155 | 476.9395 | 271.9259 | 239.9034 | 266.9699 | 126.5137 | 15.8333 | 15.7401 | 16.1874 | 14.5872 | 18.1174 | 24.9404 |  |  |  | 534.0484 | 715.8779 | 746.6639 | 691.8499 | 59.3894 | 24.8767 | 648.2819 |  |  | 156.0309 |  |  | 17.3507 | 18.6461 | 134.9316 | 16.4233 | 16.8704 | 29.2246 | 823.8802 | 727.2528 | 722.6583 | 787.2017 | 929.697 |  | 620.1534 | 914.1338 | 520.2372 | 718.4377 | 814.686 | 887.1596 |  | 600.3649 |  |  | 383.1853 | 611.748 | 798.7068 | [6 empty] | 727.3676 |  |  | 476.1297 |  |  | 626.6769 | 948.9979 | 948.338 | 436.9191 | 864.9195 | 791.4897 | 518.8312 | 867.8026 | 919.2276 | 824.5391 | 974.6673 | 714.3815 | 901.9112 | 696.5348 | 957.2102 | 179.6872 | 676.4649 | 689.5812 | 495.7561 | 772.2717 | 811.085 | 484.8752 | 770.0059 | 776.9076 | 547.288 | 739.8192 | 655.7219 | 805.947 | 673.7848 | 869.6109 | 184.5568 | 16.7136 | 3.7601 | 0.10504 | -38.2576 | 3.1245 | 9828.83 | 12.55 | 4.5129 | 0.80704 | -1.8499 | -1.7555 | 5.0335 | 4.318 | 4.7385 | 27.5075 | 11.5243 | 82.0765 | -42.7452 | -37.4896 | 13.3901 | 19.6882
42810.4487 | 750 | 18.5247 | 18.5627 | 18.5206 | 18.5172 | 17.7958 | 16.3688 | 14.4164 | 16.5968 | 17.095 | 17.1903 | 17.2027 | 16.7103 | 15.7221 | 14.3408 | 14.8886 | 15.0219 | 15.9761 | 13.3919 | 13.7723 | 22.7516 |  |  |  | 16.6851 | 17.4842 | 56.7756 | 760.3557 | 631.9658 | 782.3333 | 17.254 | 18.0163 | 29.7183 | 17.8889 | 18.2154 | 91.2285 | 507.0249 | 812.5698 |  | 521.7094 | 828.6478 | 638.6871 | 724.3452 |  | 70.3587 | 144.5415 | 98.5113 | 202.3869 | 417.6235 | 660.6972 | 811.4643 | 19.162 | 41.3953 | 38.2247 | 90.4123 | 10.8003 | 43.7568 | 47.3498 | 46.5396 | 16.1917 |  |  | 3.3916 | -0.013053 | -1.4149 | -1.8018 | 5.4674 | 4.9089 | 5.6991 | 5.6937 | 10.6964 | 24.7088 | 159.3923 | 0.0032544 | 0.0032642 | -0.00080989 | 16.3897 | 16.6268 | 17.1374 | 17.4569 | 17.3863 | 16.3333 | 14.6649 | 16.7371 | 17.0818 | 17.3812 | 17.4114 | 17.1126 | 16.2621 | 14.4351 | 677.3389 | 287.5178 | 463.4783 | 253.9739 | 222.7424 | 280.6879 | 132.2361 | 15.8314 | 15.7485 | 16.1877 | 14.599 | 18.173 | 25.1182 |  |  |  | 540.6811 | 706.9592 | 737.2862 | 692.61 | 68.2199 | 32.5283 | 675.0634 |  |  | 173.9249 |  |  | 17.3622 | 18.6638 | 136.5336 | 16.4226 | 16.8781 | 29.6297 | 834.9907 | 717.5307 | 741.6454 | 800.1303 | 924.9108 |  | 639.1434 | 898.0282 | 542.4913 | 706.595 | 816.6714 | 891.461 |  | 619.4129 |  |  | 385.3908 | 624.439 | 812.403 | [6 empty] | 714.8517 |  |  | 462.3919 |  |  | 625.4136 | 929.1899 | 945.2982 | 488.3754 | 893.4381 | 805.9618 | 581.5844 | 889.887 | 927.1486 | 809.3612 | 961.8365 | 755.3559 | 927.7716 | 742.6619 | 970.9565 | 185.3207 | 697.2197 | 693.889 | 501.0394 | 764.7001 | 803.0836 | 512.0959 | 806.2464 | 788.4151 | 571.5918 | 749.7202 | 652.5442 | 796.3185 | 701.4849 | 885.0852 | 203.103 | 16.6974 | 3.7725 | 0.10613 | -38.2535 | 3.1245 | 10149.93 | 11.53 | 4.1696 | -0.16272 | -1.6942 | -1.9118 | 4.9796 | 4.7184 | 5.084 | 31.3375 | 15.2185 | 83.0419 | -38.7376 | -35.2734 | 14.9697 | 20.6523
42810.4487 | 751 | 18.5282 | 18.5628 | 18.5164 | 18.5189 | 17.7956 | 16.3735 | 14.4199 | 16.5848 | 17.0985 | 17.1933 | 17.202 | 16.7064 | 15.7316 | 14.3451 | 14.8854 | 15.026 | 15.968 | 13.3857 | 13.7741 | 22.8356 |  |  |  | 16.6824 | 17.4863 | 55.5317 | 747.6176 | 628.2722 | 774.584 | 24.198 | 23.7429 | 47.6822 | 25.0627 | 30.7082 | 94.909 | 524.0136 | 785.6057 |  | 325.641 | 867.2287 | 671.218 | 753.1663 |  | 72.1316 | 148.0858 | 100.4448 | 206.2781 | 422.1084 | 668.0442 | 824.6785 | 20.8172 | 43.631 | 38.0329 | 95.5526 | 10.9136 | 43.9085 | 47.4232 | 46.671 | 16.3365 |  |  | 3.18 | 0.16831 | -1.4155 | -1.4378 | 5.9425 | 4.1709 | 6.4265 | 3.1684 | 10.5503 | 24.4973 | 148.7465 | 0.0032396 | 0.0032511 | -0.00083125 | 16.3936 | 16.6144 | 17.1405 | 17.4515 | 17.3856 | 16.3308 | 14.6576 | 16.7372 | 17.0806 | 17.3703 | 17.4058 | 17.1125 | 16.2575 | 14.431 | 686.0232 | 282.946 | 445.8547 | 248.0426 | 216.4519 | 295.3413 | 137.8379 | 15.8251 | 15.7389 | 16.1937 | 14.5953 | 18.2183 | 25.2779 |  |  |  | 546.7577 | 703.7942 | 733.6308 | 702.274 | 94.4807 | 22.8752 | 687.0013 |  |  | 183.2227 |  |  | 17.3734 | 18.678 | 129.927 | 16.4297 | 16.8807 | 30.0772 | 843.0197 | 708.294 | 760.7543 | 808.6546 | 917.5457 |  | 658.9709 | 893.9791 | 564.8567 | 695.0303 | 817.3474 | 885.296 |  | 638.7389 |  |  | 386.9556 | 631.9638 | 822.7876 | [6 empty] | 704.4963 |  |  | 448.2458 |  |  | 619.6773 | 909.0893 | 941.2074 | 547.785 | 919.5725 | 815.3059 | 641.9597 | 911.6067 | 933.9804 | 793.3858 | 945.5595 | 777.1946 | 949.9351 | 789.2839 | 988.0666 | 189.6253 | 715.779 | 696.9029 | 502.784 | 755.2329 | 793.1169 | 533.2853 | 821.1073 | 797.0636 | 599.2783 | 759.3118 | 648.9381 | 786.4423 | 731.9977 | 891.8653 | 213.6583 | 16.6784 | 3.787 | 0.10681 | -38.3013 | 3.1246 | 10424.91 | 9.03 | 4.0226 | 0.58679 | -1.7017 | -1.715 | 5.2118 | 4.3664 | 5.4199 | 35.6202 | 18.82 | 83.5806 | -37.487 | -32.6064 | 16.5313 | 21.3039
42810.4487 | 752 | 18.5256 | 18.5548 | 18.5178 | 18.5191 | 17.7946 | 16.373 | 14.4175 | 16.5953 | 17.0967 | 17.1885 | 17.1976 | 16.7121 | 15.7222 | 14.3485 | 14.8753 | 15.0242 | 15.9853 | 13.3905 | 13.77 | 22.9202 |  |  |  | 16.6763 | 17.5019 | 56.1352 | 744.3207 | 626.516 | 769.3798 | 38.4411 | 16.7295 | 57.6703 | 16.3819 | 35.4428 | 94.0987 | 523.4259 | 685.0391 |  | 345.25 | 844.0761 | 643.6659 | 731.0284 |  | 74.028 | 151.8904 | 102.5323 | 210.1546 | 428.9566 | 676.9967 | 837.9416 | 22.3142 | 45.8785 | 38.3946 | 100.6584 | 11.0227 | 44.0614 | 47.4833 | 46.8198 | 16.476 |  |  | 2.289 | 0.014543 | -1.5496 | -1.4884 | 5.1283 | 2.8889 | 6.37 | 1.9311 | 11.2401 | 26.1151 | 153.0074 | 0.0031279 | 0.0032149 | -0.00081154 | 16.3917 | 16.62 | 17.1455 | 17.4544 | 17.3883 | 16.3245 | 14.6616 | 16.7428 | 17.0803 | 17.3746 | 17.4132 | 17.1111 | 16.2592 | 14.4361 | 744.3208 | 301.8115 | 418.0668 | 235.4565 | 203.0809 | 313.1196 | 143.544 | 15.8313 | 15.7486 | 16.2049 | 14.6066 | 18.2823 | 25.4845 |  |  |  | 552.679 | 699.4506 | 728.0943 | 701.7423 | 112.1339 | 57.7784 | 700.2701 |  |  | 197.3055 |  |  | 17.3795 | 18.6826 | 129.4066 | 16.4266 | 16.8814 | 30.6599 | 844.4834 | 699.9427 | 783.9075 | 823.0184 | 909.8665 |  | 678.65 | 900.6202 | 586.2142 | 684.0293 | 816.903 | 881.8727 |  | 657.8372 |  |  | 389.6453 | 636.2974 | 824.6421 | [6 empty] | 696.0221 |  |  | 435.8391 |  |  | 614.3555 | 888.4222 | 935.2544 | 605.4632 | 936.6283 | 824.771 | 709.564 | 937.6426 | 941.4522 | 778.8733 | 925.6402 | 793.9696 | 966.8124 | 838.4274 | 1007.982 | 196.1287 | 732.9067 | 700.903 | 504.4892 | 745.1284 | 785.3692 | 550.1858 | 835.9943 | 804.4968 | 617.6674 | 772.7147 | 643.4155 | 777.9387 | 762.1296 | 896.9289 | 201.0349 | 16.6635 | 3.8181 | 0.10595 | -38.2826 | 3.1246 | 10724.04 | 8.97 | 3.4043 | 0.17326 | -1.7885 | -1.7528 | 4.8646 | 3.6511 | 5.4217 | 40.1108 | 22.1902 | 83.7432 | -41.2128 | -28.7931 | 17.0625 | 22.2314
42810.4488 | 753 | 18.5269 | 18.5597 | 18.5234 | 18.5202 | 17.7913 | 16.3745 | 14.4161 | 16.5943 | 17.0989 | 17.1902 | 17.2032 | 16.7168 | 15.7242 | 14.3411 | 14.8905 | 15.0242 | 15.9931 | 13.4023 | 13.7819 | 23.0103 |  |  |  | 16.6881 | 17.509 | 57.3109 | 741.9055 | 625.3896 | 767.7379 | 17.242 | 17.2348 | 29.1287 | 16.8726 | 17.3277 | 99.1259 | 532.6306 | 814.2605 |  | 358.7298 | 840.7711 | 648.8982 | 730.0452 |  | 76.6307 | 156.9342 | 105.4586 | 213.6463 | 430.471 | 679.4184 | 849.8349 | 23.3876 | 48.5231 | 40.4396 | 106.5767 | 11.1218 | 44.1865 | 47.5374 | 46.9493 | 16.6346 |  |  | 0.47334 | 0.18868 | -1.3367 | -1.4404 | 4.9206 | 4.6158 | 5.4927 | 0.58138 | 11.3324 | 27.3072 | 164.2443 | 0.0031213 | 0.0031476 | -0.00080168 | 16.3951 | 16.625 | 17.1397 | 17.4567 | 17.3905 | 16.3425 | 14.6663 | 16.742 | 17.0839 | 17.3721 | 17.4133 | 17.1062 | 16.254 | 14.4299 | 787.495 | 319.8093 | 488.6904 | 255.0143 | 212.4102 | 333.6155 | 152.6948 | 15.828 | 15.7613 | 16.2084 | 14.6203 | 18.3455 | 25.7193 |  |  |  | 557.2596 | 690.8232 | 719.2096 | 689.5692 | 105.9179 | 41.3867 | 716.6249 |  |  | 219.9514 |  |  | 17.3967 | 18.6967 | 131.7028 | 16.4249 | 16.8888 | 31.2926 | 846.6985 | 691.7304 | 807.185 | 840.4268 | 900.2817 |  | 695.3937 | 919.659 | 605.2897 | 674.8237 | 815.7137 | 878.0831 |  | 674.6531 |  |  | 393.0866 | 639.3884 | 821.796 | [6 empty] | 688.6622 |  |  | 425.7381 |  |  | 610.1374 | 870.2508 | 925.3516 | 657.769 | 950.8311 | 836.3079 | 771.0333 | 966.7672 | 949.5092 | 765.6441 | 908.2275 | 808.9342 | 984.6452 | 890.9718 | 1027.1824 | 203.314 | 755.6012 | 707.6936 | 505.7234 | 735.4781 | 777.0981 | 567.6688 | 853.6802 | 812.4401 | 640.039 | 788.9088 | 638.3311 | 770.8493 | 788.2761 | 903.7232 | 183.6599 | 16.6477 | 3.8657 | 0.10538 | -38.3328 | 3.1246 | 11025.22 | 8.97 | 1.5469 | 0.62778 | -1.6709 | -1.7345 | 4.7712 | 4.621 | 5.0409 | 44.204 | 25.0297 | 83.6171 | -42.7457 | -35.4682 | 18.4191 | 23.2868
42810.4488 | 754 | 18.5262 | 18.5648 | 18.5257 | 18.5165 | 17.7967 | 16.3713 | 14.4246 | 16.5936 | 17.0975 | 17.1933 | 17.206 | 16.7143 | 15.7306 | 14.341 | 14.884 | 15.025 | 15.9878 | 13.3951 | 13.7777 | 23.1002 |  |  |  | 16.6864 | 17.5165 | 56.6539 | 738.6942 | 625.2543 | 762.5433 | 17.2415 | 17.2422 | 29.3455 | 16.8791 | 17.334 | 102.1855 | 540.8866 | 818.5947 |  | 373.8634 | 844.9349 | 654.4768 | 727.2137 |  | 78.7864 | 161.2989 | 108.2852 | 216.7046 | 432.7221 | 685.7617 | 858.7714 | 23.9187 | 50.7885 | 42.6007 | 111.6975 | 11.2277 | 44.2967 | 47.5873 | 47.0821 | 16.7965 |  |  | 0.8295 | 0.009943 | -0.91023 | -1.1559 | 5.1112 | 4.2971 | 5.7378 | -0.66122 | 11.6926 | 27.0005 | 183.498 | 0.003054 | 0.0030638 | -0.00082796 | 16.4071 | 16.6231 | 17.1369 | 17.4589 | 17.3884 | 16.3316 | 14.6583 | 16.7439 | 17.0812 | 17.372 | 17.4098 | 17.1126 | 16.2584 | 14.4348 | 822.1234 | 348.7095 | 505.6509 | 273.0985 | 224.434 | 353.2706 | 160.4477 | 15.8201 | 15.7544 | 16.2117 | 14.6136 | 18.4195 | 25.9836 |  |  |  | 560.8585 | 678.9624 | 707.5075 | 670.8384 | 98.8522 | 39.2866 | 736.1644 |  |  | 245.3241 |  |  | 17.4122 | 18.7114 | 131.7027 | 16.4296 | 16.8961 | 31.9794 | 847.7595 | 682.5257 | 826.9178 | 854.281 | 889.6262 |  | 711.2433 | 934.4906 | 623.7401 | 663.7559 | 813.4297 | 868.2041 |  | 691.8475 |  |  | 394.942 | 644.8918 | 824.3759 | [6 empty] | 679.7036 |  |  | 418.5117 |  |  | 606.0261 | 852.9367 | 913.0955 | 703.8837 | 962.2605 | 850.1013 | 823.761 | 997.8951 | 955.557 | 752.6706 | 892.1875 | 823.8739 | 997.7937 | 935.2261 | 1048.0709 | 212.0348 | 778.9617 | 716.8319 | 506.4284 | 725.8171 | 770.0302 | 592.7191 | 877.7819 | 821.9169 | 661.4966 | 803.1096 | 633.7706 | 764.3298 | 812.7224 | 917.3158 | 186.529 | 16.6329 | 3.9241 | 0.10492 | -38.3538 | 3.1246 | 11255.52 | 6.24 | 2.0426 | 0.14484 | -1.3858 | -1.5617 | 4.8789 | 4.4735 | 5.1693 | 48.2873 | 28.0574 | 83.1944 | -43.3641 | -36.3518 | 19.7219 | 24.3775
42810.4488 | 755 | 18.5128 | 18.5531 | 18.5169 | 18.5132 | 17.7934 | 16.3682 | 14.4169 | 16.5895 | 17.0964 | 17.1983 | 17.1987 | 16.7093 | 15.7221 | 14.3355 | 14.8808 | 15.0307 | 16.0011 | 13.3995 | 13.7795 | 23.2027 |  |  |  | 16.6927 | 17.5301 | 56.0752 | 731.641 | 624.5297 | 753.5539 | 53.0124 | 49.2886 | 62.861 | 37.2207 | 44.8918 | 134.9098 | 565.7687 | 678.834 |  | 407.7292 | 875.6601 | 681.077 | 753.5866 |  | 82.0612 | 167.3625 | 112.2837 | 222.3033 | 442.6607 | 692.6064 | 864.9527 | 23.8457 | 53.4178 | 44.7547 | 117.6804 | 11.3574 | 44.4088 | 47.6576 | 47.2029 | 16.964 |  |  | -0.94143 | 0.24913 | -0.52713 | -1.1381 | 4.7636 | 3.1445 | 5.7878 | -3.0216 | 10.4074 | 28.1676 | 196.9158 | 0.0030457 | 0.0030704 | -0.00082632 | 16.4019 | 16.6191 | 17.1399 | 17.4492 | 17.3875 | 16.3306 | 14.6578 | 16.7297 | 17.0815 | 17.3702 | 17.4073 | 17.1048 | 16.2598 | 14.4292 | 842.414 | 377.9583 | 536.4645 | 287.9641 | 238.6922 | 373.0363 | 168.9578 | 15.8185 | 15.7503 | 16.2123 | 14.615 | 18.4943 | 26.2721 |  |  |  | 563.3761 | 666.8954 | 695.9836 | 658.5193 | 98.8423 | 60.3522 | 755.4124 |  |  | 272.0588 |  |  | 17.4206 | 18.7273 | 128.0743 | 16.4316 | 16.9018 | 32.7951 | 841.685 | 673.2552 | 841.9019 | 865.8435 | 873.8705 |  | 727.1529 | 946.0075 | 645.5208 | 652.94 | 810.1385 | 859.1717 |  | 711.1979 |  |  | 396.1251 | 651.9397 | 822.4169 | [6 empty] | 670.6964 |  |  | 411.7408 |  |  | 602.6768 | 836.1067 | 899.6934 | 749.988 | 974.3406 | 864.9209 | 869.3455 | 1030.3704 | 958.4881 | 739.852 | 874.4062 | 840.0746 | 1014.4436 | 973.5992 | 1071.7643 | 223.0569 | 800.2067 | 725.9949 | 506.8084 | 717.0596 | 762.7087 | 617.7517 | 900.6163 | 829.6918 | 685.6565 | 818.5149 | 629.7472 | 757.4061 | 832.4378 | 933.5419 | 174.3396 | 16.6106 | 4.0109 | 0.10678 | -38.275 | 3.1246 | 11557.37 | 5.84 | -2.1666 | 0.73007 | -1.062 | -1.5604 | 4.7268 | 3.8404 | 5.2102 | 52.6932 | 32.0384 | 82.4502 | -42.2672 | -38.6679 | 22.8671 | 25.1224
42810.4488 | 756 | 18.5115 | 18.5671 | 18.5234 | 18.5227 | 17.8 | 16.3797 | 14.417 | 16.5956 | 17.099 | 17.1967 | 17.2037 | 16.7115 | 15.7263 | 14.3448 | 14.8801 | 15.0301 | 16.0051 | 13.4031 | 13.7837 | 23.3068 |  |  |  | 16.6879 | 17.5465 | 55.7944 | 725.3763 | 626.6385 | 745.336 | 67.033 | 71.0674 | 73.4006 | 54.3352 | 47.9837 | 131.5982 | 571.307 | 633.8936 |  | 419.123 | 883.4381 | 700.5419 | 767.5799 |  | 85.3604 | 174.1801 | 117.1292 | 230.4416 | 454.3594 | 698.2094 | 874.9189 | 23.7356 | 55.875 | 46.182 | 123.3358 | 11.4742 | 44.5497 | 47.741 | 47.2937 | 17.1343 |  |  | -1.7648 | -0.13659 | -0.77749 | -1.9089 | 4.9233 | 4.1663 | 4.2823 | -5.1914 | 11.3329 | 29.5057 | 201.1121 | 0.0029899 | 0.0030474 | -0.00084768 | 16.412 | 16.6323 | 17.1473 | 17.4578 | 17.3944 | 16.3388 | 14.6585 | 16.7413 | 17.0845 | 17.3756 | 17.4085 | 17.1087 | 16.2585 | 14.4373 | 861.518 | 348.3645 | 597.6267 | 336.9485 | 280.5225 | 391.6372 | 179.1936 | 15.8243 | 15.7569 | 16.2201 | 14.626 | 18.5823 | 26.5665 |  |  |  | 565.1473 | 656.3845 | 685.7422 | 646.2929 | 73.5548 | 35.7695 | 768.2127 |  |  | 299.1633 |  |  | 17.4289 | 18.7479 | 126.6828 | 16.4304 | 16.9082 | 33.6869 | 832.1006 | 664.528 | 848.14 | 868.0943 | 867.4557 |  | 739.0745 | 931.5835 | 662.6443 | 644.1699 | 807.0111 | 856.3089 |  | 727.0371 |  |  | 405.1147 | 651.7916 | 813.0753 | [6 empty] | 661.9916 |  |  | 405.1329 |  |  | 597.6147 | 820.7385 | 886.4953 | 791.3092 | 986.2962 | 879.0809 | 894.0924 | 1056.9689 | 962.5926 | 726.6925 | 858.7245 | 852.1941 | 1031.2083 | 998.5955 | 1091.9534 | 233.5426 | 822.0661 | 736.7384 | 507.8236 | 708.7611 | 755.0459 | 648.879 | 919.3666 | 833.7646 | 708.3087 | 835.5398 | 625.6177 | 750.0889 | 848.5294 | 948.1662 | 228.0422 | 16.5853 | 4.1081 | 0.10638 | -38.3225 | 3.1246 | 11923.74 | 5.96 | -2.9546 | -0.54475 | -1.2997 | -2.0365 | 4.8193 | 4.4334 | 4.4947 | 55.9576 | 36.011 | 81.7091 | -41.1348 | -44.1187 | 23.3812 | 25.7471
42810.4488 | 757 | 18.5139 | 18.5567 | 18.5161 | 18.5086 | 17.7838 | 16.3748 | 14.4242 | 16.5886 | 17.0863 | 17.1912 | 17.2015 | 16.7057 | 15.7175 | 14.3279 | 14.8822 | 15.0272 | 16.0032 | 13.3958 | 13.7839 | 23.4113 |  |  |  | 16.6859 | 17.5515 | 55.9663 | 721.0043 | 630.3845 | 740.3547 | 65.4835 | 53.062 | 82.5001 | 69.3418 | 57.0132 | 133.0966 | 596.4371 | 629.2993 |  | 413.5709 | 864.8738 | 677.8903 | 750.7493 |  | 88.5964 | 180.6455 | 121.6245 | 237.6581 | 463.7687 | 705.5411 | 884.1987 | 23.6192 | 58.2714 | 45.9308 | 128.8555 | 11.5912 | 44.7653 | 47.8618 | 47.3902 | 17.3148 |  |  | -0.054977 | -0.010425 | -0.6303 | -1.671 | 6.9209 | 3.6202 | 2.6481 | -6.2625 | 11.6964 | 30.1953 | 199.996 | 0.003003 | 0.0029307 | -0.00082796 | 16.4118 | 16.6236 | 17.1411 | 17.4531 | 17.3958 | 16.3326 | 14.6534 | 16.7404 | 17.0778 | 17.373 | 17.4088 | 17.1095 | 16.2544 | 14.4348 | 799.0082 | 328.0246 | 559.1946 | 310.7172 | 260.7703 | 406.4283 | 186.5948 | 15.8287 | 15.7597 | 16.2325 | 14.6344 | 18.6781 | 26.8914 |  |  |  | 566.6752 | 649.3732 | 676.5787 | 636.372 | 58.1284 | 29.5619 | 775.3485 |  |  | 326.4939 |  |  | 17.4429 | 18.761 | 126.9004 | 16.4351 | 16.9174 | 34.7293 | 824.3688 | 655.9352 | 856.4728 | 871.5611 | 859.4092 |  | 749.0794 | 939.0564 | 679.6293 | 635.5773 | 803.5391 | 856.4466 |  | 741.9586 |  |  | 417.0849 | 654.603 | 802.5841 | [6 empty] | 653.3241 |  |  | 398.192 |  |  | 592.2941 | 805.7713 | 874.3814 | 819.9377 | 997.7019 | 890.4498 | 892.225 | 1067.3526 | 967.4356 | 714.5209 | 843.6866 | 864.5859 | 1044.8353 | 998.1076 | 1096.3298 | 244.9827 | 842.7923 | 747.4258 | 508.0553 | 700.0105 | 748.9416 | 683.0803 | 930.7226 | 837.8361 | 727.5544 | 852.4245 | 620.6762 | 741.8878 | 857.7338 | 954.6765 | 222.6991 | 16.5723 | 4.2329 | 0.10631 | -38.2691 | 3.1246 | 12281.7 | 5.81 | -0.5202 | -0.15158 | -1.1786 | -1.9191 | 5.7355 | 4.1482 | 3.5478 | 58.8475 | 39.519 | 80.8638 | -31.5268 | -38.8669 | 28.1352 | 26.2698
42810.4488 | 758 | 18.5154 | 18.5593 | 18.5213 | 18.51 | 17.7927 | 16.3687 | 14.4193 | 16.5864 | 17.0924 | 17.1923 | 17.1965 | 16.7033 | 15.7257 | 14.3369 | 14.883 | 15.0345 | 16.0169 | 13.4046 | 13.7926 | 23.5286 |  |  |  | 16.6946 | 17.566 | 56.0842 | 715.5514 | 632.4122 | 732.1322 | 41.7988 | 44.0481 | 48.8621 | 40.2174 | 43.4851 | 140.7584 | 598.2858 | 686.2018 |  | 422.2366 | 860.4046 | 669.6173 | 749.6564 |  | 92.2454 | 187.9974 | 127.3323 | 246.3804 | 472.2259 | 714.5199 | 892.9226 | 24.3087 | 60.9811 | 45.7491 | 135.1618 | 11.718 | 45.0219 | 47.9937 | 47.4772 | 17.4929 |  |  | -1.3232 | 0.055943 | -0.77355 | -2.2572 | 6.6357 | 3.5053 | 2.5554 | -8.7076 | 11.056 | 29.1385 | 207.4236 | 0.0028634 | 0.0028864 | -0.00080168 | 16.4185 | 16.629 | 17.1424 | 17.4519 | 17.3953 | 16.3304 | 14.6632 | 16.7414 | 17.0827 | 17.3767 | 17.4147 | 17.1117 | 16.2576 | 14.4413 | 747.9147 | 325.6369 | 516.3406 | 299.8747 | 248.9996 | 417.8873 | 193.0646 | 15.8275 | 15.7615 | 16.2364 | 14.6347 | 18.767 | 27.2299 |  |  |  | 568.013 | 646.0851 | 668.1695 | 627.8519 | 50.3018 | 20.9256 | 785.8654 |  |  | 345.5332 |  |  | 17.4573 | 18.7766 | 126.1171 | 16.4401 | 16.9266 | 35.9197 | 827.0914 | 646.0307 | 858.9713 | 869.6195 | 866.9586 |  | 762.2256 | 929.6146 | 698.247 | 624.4216 | 799.0221 | 849.3203 |  | 756.7036 |  |  | 427.6198 | 663.3969 | 805.4699 | [6 empty] | 643.0307 |  |  | 391.2052 |  |  | 586.905 | 791.2745 | 862.7399 | 848.9246 | 1009.0396 | 900.9629 | 878.3501 | 1057.2467 | 964.6834 | 702.909 | 827.983 | 883.6259 | 1055.5724 | 982.8144 | 1080.6266 | 253.1823 | 861.8287 | 757.5658 | 507.3212 | 691.8555 | 744.0408 | 711.7962 | 934.2379 | 837.6702 | 743.0358 | 868.6429 | 616.1049 | 735.3611 | 869.4712 | 953.6093 | 232.28 | 16.5435 | 4.355 | 0.10632 | -38.2691 | 3.1246 | 12539.16 | 5.99 | -2.5417 | 0.35396 | -1.3162 | -2.2484 | 5.6418 | 4.1005 | 3.5011 | 62.2498 | 44.059 | 79.7775 | -23.74 | -33.2408 | 28.4935 | 26.7238
42810.4488 | 759 | 18.5156 | 18.5636 | 18.5256 | 18.5165 | 17.7894 | 16.3687 | 14.4229 | 16.5888 | 17.0954 | 17.1914 | 17.1975 | 16.7111 | 15.725 | 14.3377 | 14.8831 | 15.0409 | 16.0185 | 13.4109 | 13.7928 | 23.6552 |  |  |  | 16.696 | 17.5803 | 56.1631 | 706.0329 | 635.1615 | 717.9008 | 17.2367 | 17.275 | 30.9219 | 27.9104 | 37.1491 | 137.5672 | 590.0776 | 750.6 |  | 435.5593 | 873.6254 | 680.0273 | 746.9762 |  | 95.5952 | 194.5554 | 132.4117 | 254.989 | 489.3788 | 726.2228 | 899.947 | 25.2232 | 63.2889 | 45.2171 | 140.5357 | 11.8588 | 45.2452 | 48.1482 | 47.5663 | 17.678 |  |  | -1.7996 | -0.24765 | -0.91417 | -1.8084 | 6.7987 | 3.5605 | 3.2408 | -9.3411 | 12.6977 | 29.9383 | 205.2983 | 0.0028272 | 0.0029455 | -0.00083454 | 16.4207 | 16.6287 | 17.1345 | 17.4495 | 17.3919 | 16.3359 | 14.6611 | 16.7373 | 17.0778 | 17.3674 | 17.413 | 17.1146 | 16.2522 | 14.4304 | 675.0765 | 307.9356 | 449.1425 | 276.2843 | 234.3031 | 426.8819 | 197.7756 | 15.8211 | 15.7683 | 16.2396 | 14.6393 | 18.8867 | 27.6289 |  |  |  | 569.2261 | 643.708 | 665.4155 | 622.9652 | 37.1624 | 11.6202 | 791.2535 |  |  | 357.8521 |  |  | 17.4513 | 18.7854 | 124.595 | 16.4339 | 16.9274 | 37.4234 | 834.1862 | 635.8724 | 859.466 | 867.8821 | 875.105 |  | 774.8971 | 922.139 | 714.0162 | 612.9329 | 794.2589 | 846.008 |  | 771.2968 |  |  | 434.9249 | 672.4489 | 817.7143 | [6 empty] | 631.6232 |  |  | 384.5228 |  |  | 580.9441 | 777.5142 | 849.771 | 879.015 | 1023.4403 | 910.7819 | 862.3904 | 1038.5602 | 954.6845 | 691.1105 | 813.8001 | 900.8709 | 1068.3785 | 964.1294 | 1059.8212 | 265.0823 | 878.3919 | 768.7289 | 506.2877 | 684.3629 | 737.8677 | 735.6429 | 937.0777 | 833.738 | 759.3838 | 885.3548 | 611.4242 | 728.8578 | 890.2608 | 950.95 | 233.1743 | 16.4904 | 4.4677 | 0.10669 | -38.3228 | 3.1246 | 12882.53 | 5.59 | -2.9431 | -0.75001 | -1.441 | -2.0267 | 5.7444 | 4.157 | 3.966 | 65.6244 | 48.0637 | 78.6417 | -13.961 | -25.141 | 27.1253 | 27.0573
42810.4488 | 760 | 18.5166 | 18.5599 | 18.5252 | 18.5178 | 17.7898 | 16.3647 | 14.4186 | 16.5889 | 17.0918 | 17.1855 | 17.2008 | 16.7113 | 15.7196 | 14.3337 | 14.8777 | 15.0419 | 16.0237 | 13.4151 | 13.7944 | 23.7897 |  |  |  | 16.6986 | 17.5788 | 56.8311 | 696.5048 | 642.3612 | 706.2567 | 17.2605 | 18.9967 | 32.2908 | 39.472 | 74.7225 | 176.8206 | 619.9179 | 620.2314 |  | 447.1916 | 891.1845 | 709.1733 | 769.3119 |  | 99.3646 | 201.8414 | 138.1315 | 263.9011 | 505.1641 | 739.1757 | 904.8347 | 25.6112 | 65.9706 | 44.7013 | 146.8559 | 11.9998 | 45.4275 | 48.2782 | 47.6112 | 17.8794 |  |  | -1.9291 | -0.22399 | -0.57641 | -1.4141 | 7.2271 | 3.4967 | 3.3059 | -8.9337 | 12.3126 | 30.7475 | 216.3069 | 0.0028026 | 0.0027812 | -0.00080004 | 16.429 | 16.6283 | 17.1438 | 17.4581 | 17.3917 | 16.33 | 14.6527 | 16.741 | 17.0786 | 17.3806 | 17.4093 | 17.1024 | 16.2566 | 14.4301 | 604.9877 | 269.2588 | 376.7539 | 250.5511 | 213.9689 | 433.0124 | 200.8645 | 15.8208 | 15.7611 | 16.2376 | 14.6339 | 19.0167 | 28.0257 |  |  |  | 569.8183 | 637.9851 | 670.4973 | 613.4976 | 47.1558 | 15.5805 | 798.9953 |  |  | 366.1214 |  |  | 17.4563 | 18.7979 | 124.7448 | 16.4368 | 16.935 | 39.2007 | 843.312 | 626.4915 | 864.7389 | 869.9884 | 891.2018 |  | 787.9591 | 927.5431 | 729.3341 | 603.5545 | 789.7258 | 839.4827 |  | 783.694 |  |  | 440.7138 | 674.5374 | 824.3222 | [6 empty] | 620.4762 |  |  | 377.5339 |  |  | 575.4381 | 764.7179 | 836.4678 | 902.7154 | 1034.4843 | 918.2712 | 848.358 | 1021.2933 | 941.7047 | 681.0863 | 801.1671 | 919.3848 | 1077.4696 | 948.5871 | 1042.3744 | 278.1644 | 888.0989 | 781.9907 | 505.1369 | 676.2825 | 729.8012 | 761.1303 | 944.5497 | 829.8691 | 776.88 | 901.2727 | 606.577 | 721.2206 | 917.2031 | 950.2983 | 175.0643 | 16.4266 | 4.5673 | 0.10701 | -38.2586 | 3.1245 | 13107.74 | 2.4 | -3.0292 | -0.71883 | -1.1531 | -1.8061 | 5.9609 | 4.1463 | 4.0315 | 69.0147 | 51.7597 | 77.5339 | -5.0089 | -16.6807 | 31.9181 | 27.4171
42810.4488 | 761 | 18.5205 | 18.5594 | 18.5322 | 18.5198 | 17.7871 | 16.3719 | 14.4252 | 16.594 | 17.0913 | 17.1932 | 17.204 | 16.7116 | 15.7197 | 14.3317 | 14.8798 | 15.0355 | 16.017 | 13.4152 | 13.7874 | 23.9292 |  |  |  | 16.698 | 17.5796 | 57.7448 | 690.4221 | 647.2505 | 700.0078 | 34.8858 | 46.2709 | 72.7408 | 54.4288 | 54.3647 | 192.5605 | 637.0797 | 531.8795 |  | 474.2298 | 915.8576 | 746.1997 | 814.6582 |  | 102.8884 | 208.7115 | 143.5405 | 272.2144 | 523.3733 | 752.0807 | 909.1989 | 25.9375 | 68.4943 | 44.6093 | 152.9072 | 12.1164 | 45.5271 | 48.3804 | 47.6666 | 18.0757 |  |  | -2.2813 | -0.17142 | -0.92534 | -1.3918 | 6.8427 | 3.3567 | 4.6589 | -10.4746 | 12.6099 | 31.1096 | 209.3204 | 0.0028042 | 0.0028371 | -0.00076882 | 16.4288 | 16.6258 | 17.1342 | 17.4571 | 17.397 | 16.3255 | 14.6582 | 16.7345 | 17.0803 | 17.3797 | 17.4152 | 17.1086 | 16.2579 | 14.4357 | 572.3695 | 266.259 | 360.657 | 236.5939 | 211.4079 | 439.7828 | 204.0165 | 15.8246 | 15.7653 | 16.2479 | 14.6471 | 19.1555 | 28.4522 |  |  |  | 569.8238 | 632.4849 | 676.0812 | 604.5126 | 74.6535 | 27.4637 | 809.888 |  |  | 384.9019 |  |  | 17.4706 | 18.8172 | 124.8635 | 16.4355 | 16.9441 | 41.1329 | 845.0317 | 617.7586 | 869.8585 | 869.3725 | 900.7483 |  | 801.7935 | 929.9368 | 744.5489 | 594.1137 | 784.7248 | 833.7258 |  | 794.187 |  |  | 443.0227 | 682.7492 | 840.2381 | [6 empty] | 610.0117 |  |  | 370.7265 |  |  | 569.8144 | 753.3817 | 822.9723 | 928.2718 | 1044.7192 | 922.8494 | 835.2287 | 1005.5886 | 929.8389 | 671.2061 | 789.2225 | 932.8456 | 1087.1531 | 931.9188 | 1026.9794 | 290.0179 | 896.6664 | 793.469 | 504.9439 | 669.9492 | 722.4714 | 782.9169 | 954.446 | 827.277 | 795.0114 | 914.2118 | 602.8195 | 716.953 | 940.916 | 952.3347 | 175.9384 | 16.3414 | 4.6665 | 0.10756 | -38.2745 | 3.1246 | 13261.6 | 2.23 | -3.2836 | -0.63337 | -1.4716 | -1.8047 | 5.837 | 4.0882 | 4.8163 | 72.9564 | 55.6723 | 76.3049 | -0.083879 | -14.4651 | 33.9885 | 27.6676
42810.4489 | 762 | 18.5073 | 18.5582 | 18.5268 | 18.5134 | 17.7904 | 16.3641 | 14.4264 | 16.5929 | 17.0948 | 17.1865 | 17.1997 | 16.7053 | 15.7183 | 14.3271 | 14.8803 | 15.0344 | 16.034 | 13.4159 | 13.7941 | 24.0787 |  |  |  | 16.699 | 17.5952 | 58.0753 | 686.2027 | 650.911 | 694.5001 | 78.5867 | 48.0882 | 110.7654 | 59.9816 | 34.4252 | 217.9609 | 669.8824 | 491.4813 |  | 498.7181 | 941.1923 | 768.7555 | 741.9892 |  | 106.4185 | 215.5481 | 148.3331 | 280.0058 | 539.7236 | 760.8482 | 919.2806 | 26.5381 | 71.0045 | 45.7753 | 158.7993 | 12.2636 | 45.5704 | 48.5072 | 47.7243 | 18.2861 |  |  | -2.3128 | -0.21873 | -0.89314 | -1.7105 | 7.3855 | 3.7727 | 4.3336 | -10.6251 | 12.7086 | 31.9935 | 189.4542 | 0.0027172 | 0.0027763 | -0.00081975 | 16.4419 | 16.6293 | 17.1365 | 17.4592 | 17.3964 | 16.327 | 14.656 | 16.7408 | 17.0772 | 17.3754 | 17.411 | 17.1089 | 16.2557 | 14.4393 | 599.2218 | 285.8466 | 395.7342 | 253.2906 | 222.4924 | 450.3215 | 208.706 | 15.8212 | 15.7655 | 16.2542 | 14.6529 | 19.2929 | 28.8835 |  |  |  | 569.5129 | 626.9419 | 677.6987 | 595.2277 | 90.5165 | 38.5784 | 816.3403 |  |  | 406.011 |  |  | 17.4729 | 18.8306 | 124.2975 | 16.4313 | 16.9452 | 43.1114 | 836.3814 | 611.4995 | 874.6786 | 871.1745 | 877.8406 |  | 810.9135 | 923.1698 | 758.9414 | 586.659 | 780.2063 | 832.9767 |  | 806.1067 |  |  | 438.7727 | 673.9671 | 827.5325 | [6 empty] | 601.6031 |  |  | 364.3687 |  |  | 563.6529 | 742.3302 | 810.9477 | 952.2565 | 1052.9483 | 928.6396 | 821.5626 | 988.322 | 921.4186 | 661.9484 | 778.8042 | 947.5205 | 1096.2013 | 915.6566 | 1010.5683 | 302.8825 | 911.6356 | 802.9536 | 503.5904 | 664.3567 | 717.185 | 813.0954 | 967.1426 | 823.8024 | 812.2559 | 931.6406 | 598.6839 | 713.9798 | 957.4989 | 951.166 | 209.867 | 16.2388 | 4.7813 | 0.10881 | -38.2885 | 3.1245 | 13334.66 | 2.63 | -3.2968 | -0.72052 | -1.456 | -2.0149 | 6.09 | 4.3526 | 4.665 | 76.4482 | 59.7743 | 75.181 | -1.011 | -17.7242 | 42.8395 | 27.8747
42810.4489 | 763 | 18.5067 | 18.5548 | 18.5195 | 18.5114 | 17.7863 | 16.3609 | 14.4211 | 16.5862 | 17.091 | 17.1873 | 17.1963 | 16.7005 | 15.7164 | 14.3194 | 14.8761 | 15.0363 | 16.0422 | 13.4093 | 13.7877 | 24.2418 |  |  |  | 16.6954 | 17.6059 | 58.5658 | 680.4369 | 652.5498 | 686.6384 | 40.9676 | 19.2733 | 119.51 | 40.1837 | 31.6113 | 219.382 | 688.8059 | 505.9073 |  | 541.6938 | 937.1752 | 767.9709 | 537.5901 |  | 110.757 | 223.359 | 154.1045 | 291.667 | 563.2447 | 778.5738 | 931.6211 | 28.3621 | 73.9361 | 47.6263 | 165.4702 | 12.4145 | 45.5324 | 48.634 | 47.7887 | 18.5018 |  |  | -0.66412 | -0.29364 | -0.51004 | -1.2669 | 7.0563 | 3.7464 | 3.8177 | -12.5701 | 13.4426 | 33.4904 | 146.9904 | 0.0027205 | 0.0027599 | -0.00085918 | 16.4383 | 16.6242 | 17.1379 | 17.452 | 17.3944 | 16.3284 | 14.656 | 16.7396 | 17.0811 | 17.3721 | 17.4095 | 17.1068 | 16.2537 | 14.4345 | 657.6276 | 306.2776 | 445.2284 | 257.0103 | 228.2019 | 462.4394 | 214.3469 | 15.8152 | 15.7694 | 16.2527 | 14.649 | 19.4508 | 29.358 |  |  |  | 569.0495 | 622.0791 | 677.3481 | 589.1216 | 96.2144 | 43.96 | 823.3613 |  |  | 419.2279 |  |  | 17.4772 | 18.8463 | 124.0097 | 16.433 | 16.9547 | 45.1469 | 836.2876 | 605.885 | 881.199 | 877.7616 | 882.6454 |  | 819.8656 | 928.432 | 771.7379 | 581.1288 | 776.3016 | 828.6387 |  | 816.684 |  |  | 433.2618 | 679.8997 | 828.3633 | [6 empty] | 595.0779 |  |  | 360.4023 |  |  | 558.1849 | 733.273 | 799.5606 | 973.3471 | 1064.0787 | 933.9764 | 806.8975 | 973.5601 | 912.7208 | 653.7094 | 768.9811 | 967.8705 | 1106.9488 | 898.4429 | 997.8201 | 316.5367 | 932.7803 | 810.7835 | 501.3481 | 658.0747 | 711.0026 | 852.5612 | 973.9071 | 820.1184 | 821.8644 | 951.4311 | 594.7736 | 708.328 | 974.4871 | 956.6814 | 213.0408 | 16.1209 | 4.9109 | 0.11144 | -38.3169 | 3.1246 | 13384.43 | 2.57 | -1.7595 | -0.84147 | -1.109 | -1.7479 | 6.0035 | 4.3745 | 4.4159 | 79.1822 | 63.2342 | 74.1968 | -5.0869 | -22.4511 | 52.7521 | 27.9686
42810.4489 | 764 | 18.5081 | 18.5593 | 18.5246 | 18.5141 | 17.7856 | 16.3644 | 14.4231 | 16.5869 | 17.089 | 17.1819 | 17.1863 | 16.7094 | 15.7069 | 14.3246 | 14.88 | 15.0541 | 16.0424 | 13.4204 | 13.8042 | 24.4185 |  |  |  | 16.7033 | 17.6195 | 59.1583 | 675.2959 | 653.344 | 682.4176 | 21.1495 | 32.1776 | 122.9375 | 15.602 | 17.3414 | 226.779 | 602.2732 | 512.3985 |  | 560.86 | 935.0167 | 760.5845 | 801.7661 |  | 114.3863 | 230.316 | 159.3167 | 299.9912 | 572.1777 | 789.811 | 939.3372 | 29.5129 | 76.459 | 48.4008 | 171.1153 | 12.5548 | 45.4495 | 48.7773 | 47.8787 | 18.727 |  |  | -0.21729 | -0.082053 | -0.73018 | -1.3201 | 6.7599 | 4.462 | 2.6809 | -12.4059 | 13.3157 | 31.5319 | 154.5998 | 0.0026531 | 0.0026662 | -0.00084439 | 16.436 | 16.6273 | 17.1407 | 17.4493 | 17.3955 | 16.3289 | 14.657 | 16.7427 | 17.0842 | 17.3791 | 17.4131 | 17.111 | 16.257 | 14.4425 | 709.9232 | 331.9563 | 491.941 | 275.4554 | 230.2504 | 475.2072 | 220.7322 | 15.8128 | 15.7705 | 16.2711 | 14.6741 | 19.6546 | 29.906 |  |  |  | 568.4435 | 616.0093 | 675.085 | 582.358 | 85.6921 | 28.1854 | 837.4913 |  |  | 431.5548 |  |  | 17.4798 | 18.8613 | 123.7072 | 16.436 | 16.964 | 47.2983 | 844.6974 | 601.1282 | 889.3392 | 884.1029 | 889.9634 |  | 830.0153 | 939.649 | 785.0446 | 575.375 | 772.3083 | 829.9113 |  | 828.4635 |  |  | 425.3853 | 683.2771 | 837.0441 | [6 empty] | 588.616 |  |  | 355.0615 |  |  | 552.0019 | 724.6756 | 786.8983 | 993.9129 | 1077.3613 | 939.7209 | 792.2865 | 956.8265 | 905.1136 | 647.4787 | 758.0171 | 985.3814 | 1118.0397 | 882.9646 | 986.5197 | 330.5087 | 949.2143 | 817.0565 | 500.6348 | 652.4852 | 704.6942 | 884.1349 | 990.712 | 817.9538 | 828.5688 | 963.2798 | 591.07 | 701.3788 | 998.3308 | 971.2372 | 180.763 | 16.0146 | 5.0726 | 0.11308 | -38.3156 | 3.1246 | 13409.11 | 2.44 | -1.0042 | -0.44792 | -1.3362 | -1.7966 | 5.9074 | 4.7994 | 3.7202 | 82.3089 | 66.8014 | 73.2049 | -8.296 | -26.7608 | 27.7594 | 28.0576
42810.4489 | 765 | 18.5036 | 18.5581 | 18.5194 | 18.5151 | 17.785 | 16.3689 | 14.4205 | 16.5806 | 17.0888 | 17.1879 | 17.1888 | 16.7016 | 15.7069 | 14.3108 | 14.8782 | 15.0458 | 16.0461 | 13.4211 | 13.8016 | 24.5953 |  |  |  | 16.7118 | 17.6201 | 59.583 | 668.4489 | 651.0321 | 674.2916 | 47.813 | 25.3725 | 110.5687 | 28.5958 | 26.9603 | 237.4161 | 653.7478 | 566.6526 |  | 512.8301 | 921.7439 | 729.3682 | 854.7005 |  | 118.5561 | 238.3959 | 165.4845 | 308.9489 | 580.2795 | 801.016 | 944.1096 | 29.0759 | 79.2696 | 48.8548 | 177.407 | 12.7091 | 45.3958 | 48.9305 | 47.9887 | 18.9666 |  |  | -0.55833 | -0.49209 | -1.2033 | -1.2222 | 7.0602 | 6.0995 | 3.5319 | -12.3953 | 13.6356 | 32.7351 | 139.6164 | 0.0025677 | 0.0026975 | -0.00082632 | 16.4378 | 16.628 | 17.1316 | 17.449 | 17.3928 | 16.3251 | 14.6597 | 16.7423 | 17.0819 | 17.3696 | 17.4057 | 17.1067 | 16.2486 | 14.4296 | 735.1997 | 330.1005 | 458.9133 | 263.3808 | 223.2614 | 486.8699 | 225.3829 | 15.8172 | 15.7784 | 16.2743 | 14.6798 | 19.8312 | 30.4151 |  |  |  | 567.9 | 611.3648 | 671.8597 | 579.2545 | 102.3248 | 35.2591 | 848.5549 |  |  | 446.3433 |  |  | 17.4771 | 18.8731 | 122.8538 | 16.4392 | 16.9742 | 49.4699 | 848.539 | 600.3128 | 890.2683 | 882.6295 | 905.1803 |  | 842.4883 | 921.608 | 799.6743 | 573.9112 | 768.7198 | 831.0917 |  | 841.7678 |  |  | 419.2924 | 696.6476 | 848.6753 | [6 empty] | 587.7697 |  |  | 349.4664 |  |  | 546.0455 | 716.9481 | 776.1615 | 1008.249 | 1088.3809 | 944.9055 | 778.4561 | 940.9761 | 898.9723 | 641.3705 | 749.9241 | 991.2124 | 1120.3513 | 868.3047 | 975.0242 | 345.8706 | 960.4349 | 823.7796 | 499.3253 | 647.1246 | 698.4204 | 906.602 | 987.0291 | 816.916 | 835.3994 | 974.4982 | 586.2246 | 695.3942 | 1016.8289 | 968.0257 | 173.8409 | 15.8811 | 5.2456 | 0.11457 | -38.2266 | 3.1245 | 13452.68 | 2.31 | -1.6028 | -1.1057 | -1.729 | -1.7426 | 6.0689 | 5.6409 | 4.2925 | 86.0954 | 71.7229 | 72.2206 | -8.6739 | -22.4455 | 36.2694 | 28.0553
42810.4489 | 766 | 18.5033 | 18.5539 | 18.5198 | 18.512 | 17.788 | 16.3641 | 14.4288 | 16.587 | 17.0902 | 17.1859 | 17.1948 | 16.6977 | 15.7152 | 14.3254 | 14.8654 | 15.0382 | 16.0366 | 13.4165 | 13.7992 | 24.7823 |  |  |  | 16.7067 | 17.6275 | 60.0114 | 659.3392 | 647.0576 | 663.7123 | 48.5351 | 80.8622 | 101.7284 | 63.9467 | 74.5036 | 229.7832 | 693.0747 | 508.9889 |  | 565.7397 | 920.0476 | 770.9078 | 878.9783 |  | 122.1767 | 245.8469 | 170.7549 | 317.9512 | 591.1699 | 816.5561 | 949.3802 | 29.0471 | 81.9647 | 49.788 | 183.2811 | 12.9019 | 45.4228 | 49.0708 | 48.1158 | 19.1984 |  |  | -1.4461 | -0.10111 | -0.35694 | -1.332 | 7.2212 | 5.8538 | 2.4864 | -13.059 | 13.824 | 33.5657 | 115.9769 | 0.0026038 | 0.0026005 | -0.00082304 | 16.4477 | 16.6334 | 17.1413 | 17.4546 | 17.3938 | 16.3348 | 14.6643 | 16.7453 | 17.0822 | 17.3695 | 17.4138 | 17.1105 | 16.2587 | 14.4311 | 762.2479 | 363.6027 | 477.8889 | 263.6033 | 226.9527 | 499.2151 | 230.8467 | 15.8144 | 15.7744 | 16.2774 | 14.6849 | 20.0271 | 30.9335 |  |  |  | 567.2768 | 606.1527 | 667.4465 | 575.3381 | 83.625 | 45.0756 | 850.2676 |  |  | 461.2748 |  |  | 17.4747 | 18.8857 | 121.7944 | 16.4387 | 16.9867 | 52.2061 | 843.2485 | 599.6532 | 884.05 | 874.7148 | 890.0531 |  | 849.4767 | 905.6059 | 810.5922 | 573.1304 | 765.9878 | 830.3214 |  | 850.6018 |  |  | 415.9701 | 693.9061 | 845.9578 | [6 empty] | 587.5425 |  |  | 344.9619 |  |  | 540.6114 | 709.8572 | 767.1153 | 1013.969 | 1089.0059 | 945.6873 | 766.6118 | 921.8271 | 893.0809 | 634.4008 | 743.6073 | 991.0322 | 1116.4515 | 853.7069 | 958.4152 | 365.3906 | 968.1327 | 835.8355 | 497.2194 | 641.9886 | 691.3547 | 930.0122 | 982.5413 | 816.7073 | 842.5656 | 992.3051 | 582.6659 | 689.6927 | 1033.9991 | 965.6898 | 147.838 | 15.7743 | 5.4186 | 0.11519 | -38.1879 | 3.1246 | 13491.51 | 2.68 | -2.5651 | -0.50483 | -0.94852 | -1.8323 | 6.182 | 5.566 | 3.6275 | 88.9313 | 75.5752 | 71.4684 | -9.0481 | -23.7907 | 44.2552 | 28.0628
42810.4489 | 767 | 18.4982 | 18.5563 | 18.5219 | 18.5168 | 17.7852 | 16.3661 | 14.4267 | 16.587 | 17.0898 | 17.1857 | 17.1937 | 16.699 | 15.7163 | 14.324 | 14.8583 | 15.0313 | 16.0358 | 13.4284 | 13.7966 | 24.9871 |  |  |  | 16.7057 | 17.6237 | 60.3894 | 654.4513 | 646.9304 | 659.0207 | 32.0147 | 62.5991 | 100.5552 | 47.8135 | 75.3088 | 270.2168 | 700.9228 | 520.0043 |  | 584.0775 | 938.6707 | 763.4882 | 898.0011 |  | 125.6108 | 253.1738 | 175.8507 | 327.3381 | 603.3037 | 829.5257 | 954.3411 | 29.6321 | 84.6855 | 51.024 | 189.0063 | 13.1148 | 45.54 | 49.1987 | 48.2141 | 19.4389 |  |  | -1.8699 | 0.19197 | -0.43973 | -1.4424 | 7.0812 | 6.1475 | 4.1364 | -11.961 | 13.0983 | 33.4988 | 93.378 | 0.002589 | 0.0025463 | -0.00084439 | 16.4498 | 16.6255 | 17.1426 | 17.4638 | 17.4096 | 16.3401 | 14.6601 | 16.7406 | 17.0826 | 17.3754 | 17.4148 | 17.1112 | 16.2614 | 14.4432 | 748.9422 | 389.7197 | 505.5284 | 284.4122 | 243.2421 | 509.5326 | 236.983 | 15.8158 | 15.7776 | 16.2885 | 14.6869 | 20.2318 | 31.4752 |  |  |  | 566.5742 | 600.3897 | 661.0934 | 571.301 | 68.9809 | 31.3639 | 845.2744 |  |  | 466.244 |  |  | 17.4759 | 18.9004 | 120.293 | 16.4395 | 16.9895 | 56.8053 | 833.4069 | 597.1536 | 878.1386 | 867.5089 | 872.2798 |  | 854.6611 | 887.3271 | 819.0882 | 570.6613 | 763.0763 | 827.1366 |  | 858.4096 |  |  | 413.7286 | 681.2493 | 833.1293 | [6 empty] | 585.0721 |  |  | 340.3593 |  |  | 535.444 | 703.5313 | 758.1085 | 1014.1695 | 1087.5456 | 945.2668 | 755.6735 | 904.1625 | 887.8843 | 626.7773 | 737.4056 | 1003.813 | 1114.6669 | 838.3976 | 946.683 | 382.3002 | 982.3523 | 849.2454 | 496.1497 | 637.3742 | 684.5731 | 953.5075 | 986.0994 | 821.81 | 854.1669 | 1011.3979 | 579.3558 | 686.7116 | 1044.565 | 977.6606 | 118.2837 | 15.6463 | 5.5811 | 0.11629 | -38.187 | 3.1246 | 13559.39 | 2.49 | -2.9096 | 0.7005 | -1.0602 | -1.9201 | 6.1581 | 5.7377 | 4.7066 | 91.2442 | 78.8006 | 70.7183 | -5.3233 | -25.9985 | 45.5701 | 28.061
42810.4489 | 768 | 18.5024 | 18.5479 | 18.518 | 18.5186 | 17.7824 | 16.3671 | 14.4262 | 16.5784 | 17.083 | 17.1824 | 17.1922 | 16.6956 | 15.7027 | 14.3228 | 14.8658 | 15.0405 | 16.0458 | 13.4388 | 13.8032 | 25.1915 |  |  |  | 16.7128 | 17.635 | 61.0325 | 654.3179 | 647.6231 | 660.2827 | 47.4017 | 35.3175 | 53.6788 | 36.4892 | 42.6613 | 257.9819 | 687.2075 | 639.6411 |  | 555.6735 | 920.0827 | 744.4893 | 876.2844 |  | 128.9858 | 261.6175 | 182.0828 | 338.6835 | 622.3006 | 840.0059 | 954.7624 | 30.1981 | 87.7347 | 51.709 | 195.3864 | 13.3216 | 45.6843 | 49.3264 | 48.2979 | 19.684 |  |  | -1.2325 | 0.096683 | -0.19331 | -0.61112 | 7.7173 | 4.5672 | 2.6185 | -11.5799 | 12.801 | 33.8112 | 92.2495 | 0.0024609 | 0.002571 | -0.00082139 | 16.4454 | 16.6187 | 17.1371 | 17.4457 | 17.3895 | 16.3245 | 14.6552 | 16.7284 | 17.0683 | 17.3695 | 17.4028 | 17.1052 | 16.2534 | 14.4354 | 715.8745 | 383.1334 | 482.5151 | 279.5365 | 240.6996 | 518.2452 | 241.9551 | 15.8117 | 15.7711 | 16.2796 | 14.6933 | 20.446 | 32.0689 |  |  |  | 565.6365 | 593.5182 | 651.7186 | 565.8967 | 71.5989 | 27.1332 | 836.2154 |  |  | 463.2233 |  |  | 17.4762 | 18.9175 | 119.4142 | 16.4458 | 16.9974 | 63.1874 | 819.1371 | 593.2762 | 869.3385 | 857.3702 | 850.168 |  | 857.4493 | 873.8839 | 826.9162 | 566.323 | 759.2922 | 822.3062 |  | 865.322 |  |  | 412.6029 | 668.3534 | 818.1099 | [6 empty] | 580.6241 |  |  | 336.6084 |  |  | 530.5715 | 697.118 | 749.3513 | 1015.778 | 1093.5711 | 943.3735 | 744.0199 | 888.1873 | 883.9266 | 620.8272 | 730.6439 | 1013.3939 | 1115.7255 | 821.8832 | 935.7841 | 402.2045 | 993.6696 | 864.3731 | 494.5819 | 634.9922 | 680.2919 | 969.9581 | 982.7249 | 828.3284 | 860.8095 | 1026.7458 | 576.5618 | 686.8578 | 1047.7002 | 986.4173 | 96.582 | 15.5101 | 5.7433 | 0.11554 | -38.1543 | 3.1246 | 13678.36 | 2.5 | -2.3638 | 0.5011 | -0.70856 | -1.2598 | 6.4592 | 4.969 | 3.7625 | 92.8464 | 81.7298 | 69.784 | 0.28232 | -22.7371 | 42.9776 | 28.0593
42810.4489 | 769 | 18.5042 | 18.5512 | 18.522 | 18.5133 | 17.7828 | 16.3643 | 14.4318 | 16.578 | 17.0875 | 17.1878 | 17.1936 | 16.6976 | 15.7048 | 14.3178 | 14.8647 | 15.0448 | 16.0482 | 13.4351 | 13.8079 | 25.4098 |  |  |  | 16.7048 | 17.6469 | 61.6333 | 654.5886 | 651.3969 | 661.164 | 26.8366 | 18.1492 | 37.0741 | 16.9041 | 17.367 | 259.8483 | 667.0417 | 781.796 |  | 546.118 | 911.7411 | 734.8297 | 838.6828 |  | 132.1134 | 268.8228 | 187.0456 | 346.8341 | 626.4934 | 843.0273 | 956.9365 | 30.4345 | 90.3263 | 51.9336 | 200.7689 | 13.5539 | 45.8469 | 49.4306 | 48.3693 | 19.9384 |  |  | -0.48079 | 0.081571 | -0.71506 | -1.4779 | 6.7027 | 5.4207 | 2.7802 | -12.9848 | 13.2914 | 34.9382 | 82.0729 | 0.0024642 | 0.00252 | -0.00082632 | 16.4523 | 16.6201 | 17.1373 | 17.4552 | 17.3942 | 16.3379 | 14.6558 | 16.7383 | 17.0754 | 17.3718 | 17.4074 | 17.108 | 16.2498 | 14.4301 | 696.3221 | 368.0375 | 477.0512 | 277.1832 | 244.7393 | 527.0448 | 246.6739 | 15.8132 | 15.7744 | 16.2918 | 14.7101 | 20.7032 | 32.7007 |  |  |  | 564.3777 | 585.805 | 641.5797 | 555.6307 | 102.5029 | 51.0498 | 824.0372 |  |  | 463.5397 |  |  | 17.4725 | 18.9265 | 119.5233 | 16.4508 | 17.0031 | 72.628 | 800.8565 | 588.8006 | 852.6758 | 839.8942 | 825.8301 |  | 856.9067 | 850.0083 | 831.3258 | 562.303 | 755.4673 | 816.1403 |  | 869.0705 |  |  | 410.4119 | 654.638 | 798.9514 | [6 empty] | 575.7485 |  |  | 334.5277 |  |  | 526.6458 | 691.8953 | 741.7835 | 1014.8948 | 1095.0183 | 943.8862 | 731.5498 | 871.3259 | 877.1981 | 616.8356 | 725.4286 | 1017.439 | 1115.2009 | 806.0996 | 920.877 | 428.5289 | 998.9906 | 880.6662 | 493.2189 | 635.6203 | 677.2242 | 976.1548 | 988.789 | 839.8424 | 864.273 | 1039.3682 | 575.02 | 686.6939 | 1054.8665 | 1003.2112 | 94.3742 | 15.3567 | 5.908 | 0.11667 | -38.1643 | 3.1246 | 13796.5 | 2.64 | -1.477 | 0.46337 | -1.3719 | -1.9723 | 6.0278 | 5.4208 | 3.8821 | 93.3297 | 83.8549 | 68.84 | 4.4384 | -21.4574 | 39.5368 | 28.1414
42810.4489 | 770 | 18.4958 | 18.5571 | 18.5244 | 18.5182 | 17.7882 | 16.3613 | 14.4315 | 16.5884 | 17.0911 | 17.1862 | 17.1939 | 16.7018 | 15.7104 | 14.3199 | 14.8539 | 15.0413 | 16.0464 | 13.4312 | 13.8057 | 25.6335 |  |  |  | 16.7016 | 17.6511 | 62.7921 | 657.7904 | 657.4665 | 665.9203 | 17.2341 | 17.3369 | 37.4177 | 16.9044 | 17.4472 | 302.6807 | 676.7897 | 822.6769 |  | 558.9448 | 936.4367 | 744.4189 | 828.6238 |  | 136.2164 | 276.6506 | 192.6756 | 355.5891 | 637.3366 | 849.6545 | 958.8672 | 30.7656 | 93.3601 | 52.2847 | 207.0132 | 13.7737 | 45.9935 | 49.4922 | 48.4206 | 20.1907 |  |  | 0.82622 | 0.16042 | -0.93388 | -1.4003 | 6.8197 | 6.1764 | 3.7941 | -11.9892 | 14.3144 | 37.6812 | 68.5778 | 0.002451 | 0.0024215 | -0.00084932 | 16.465 | 16.6247 | 17.1413 | 17.4626 | 17.399 | 16.3391 | 14.662 | 16.7378 | 17.0812 | 17.3775 | 17.4102 | 17.1117 | 16.2532 | 14.4366 | 749.5446 | 387.9734 | 556.0096 | 299.0739 | 257.2906 | 538.8489 | 253.6362 | 15.8114 | 15.7806 | 16.2961 | 14.7155 | 20.935 | 33.2806 |  |  |  | 562.8415 | 579.4005 | 632.341 | 544.2239 | 85.4306 | 48.5317 | 807.4191 |  |  | 468.3497 |  |  | 17.4676 | 18.9392 | 120.5652 | 16.447 | 17.0077 | 89.4286 | 782.7705 | 584.2048 | 840.456 | 828.0379 | 802.3929 |  | 854.5689 | 833.8477 | 833.9935 | 557.9686 | 751.7014 | 809.2536 |  | 873.095 |  |  | 406.7195 | 638.5362 | 778.5833 | [6 empty] | 570.7031 |  |  | 332.7966 |  |  | 521.9535 | 687.3846 | 734.4729 | 1011.3289 | 1092.6749 | 941.0325 | 719.0079 | 856.9301 | 868.3492 | 612.9056 | 720.0497 | 1021.3079 | 1114.014 | 791.1163 | 908.8987 | 462.9248 | 1002.9867 | 897.3496 | 492.3069 | 636.2728 | 675.5283 | 978.2763 | 996.8453 | 849.7249 | 869.1359 | 1048.5818 | 574.0899 | 686.0891 | 1051.4691 | 1010.8066 | 103.774 | 15.214 | 6.0811 | 0.11927 | -38.2775 | 3.1246 | 13935.29 | 2.17 | 1.9412 | 0.65449 | -1.5791 | -1.9337 | 6.0982 | 5.8035 | 4.5485 | 93.153 | 85.196 | 67.9314 | 1.2387 | -29.2307 | 41.9532 | 28.2115
42810.449 | 771 | 18.4904 | 18.5494 | 18.5296 | 18.515 | 17.7838 | 16.3673 | 14.4279 | 16.5771 | 17.0866 | 17.183 | 17.1896 | 16.6992 | 15.7056 | 14.3247 | 14.8531 | 15.0367 | 16.0539 | 13.438 | 13.8055 | 25.8765 |  |  |  | 16.7115 | 17.6721 | 63.9034 | 659.0274 | 660.0565 | 666.555 | 17.2233 | 17.3314 | 38.3154 | 55.2492 | 50.5945 | 357.0167 | 689.5932 | 694.2786 |  | 570.1185 | 939.9716 | 774.0876 | 833.0746 |  | 139.6684 | 283.4199 | 198.608 | 364.3417 | 644.0352 | 857.9385 | 959.9297 | 30.9817 | 96.3143 | 52.7639 | 212.9738 | 13.9607 | 46.1086 | 49.5093 | 48.4647 | 20.4535 |  |  | 1.9519 | 0.72226 | -0.69404 | -1.3491 | 7.7508 | 6.2257 | 3.8624 | -11.7376 | 15.1169 | 38.0441 | 52.2649 | 0.0024067 | 0.0024527 | -0.00084275 | 16.4666 | 16.628 | 17.1353 | 17.4571 | 17.3981 | 16.3341 | 14.6579 | 16.7324 | 17.0801 | 17.3713 | 17.4083 | 17.1104 | 16.2509 | 14.4377 | 759.2188 | 391.6648 | 560.3977 | 311.3717 | 266.0115 | 548.3073 | 259.3987 | 15.8184 | 15.7878 | 16.3043 | 14.7319 | 21.1862 | 33.8874 |  |  |  | 561.453 | 571.9099 | 621.7483 | 540.7998 | 88.1359 | 39.9084 | 799.8059 |  |  | 471.1998 |  |  | 17.4665 | 18.9577 | 121.9734 | 16.4479 | 17.0166 | 111.9213 | 769.7756 | 581.0644 | 837.7116 | 824.9617 | 784.9503 |  | 851.8938 | 832.6809 | 837.6262 | 555.0103 | 747.7464 | 808.9161 |  | 877.2926 |  |  | 404.2608 | 627.4203 | 762.577 | [6 empty] | 567.3242 |  |  | 331.5643 |  |  | 516.8497 | 682.8209 | 727.0503 | 1008.1519 | 1092.3863 | 937.8275 | 706.8749 | 843.0209 | 860.5062 | 608.0069 | 714.5016 | 1019.8426 | 1112.8402 | 776.5276 | 897.3004 | 508.1263 | 1006.3646 | 919.8313 | 491.989 | 635.327 | 675.2322 | 971.0152 | 981.5916 | 855.6555 | 874.0354 | 1053.7156 | 573.0363 | 685.2185 | 1030.909 | 1001.995 | 98.424 | 15.0386 | 6.2716 | 0.1248 | -38.2517 | 3.1245 | 14020.98 | 2.75 | 2.9846 | 1.3972 | -1.3697 | -1.9096 | 6.5251 | 5.848 | 4.6062 | 92.6961 | 86.453 | 66.9437 | 2.3834 | -28.8838 | 44.7252 | 28.0845
42810.449 | 772 | 18.4907 | 18.5509 | 18.5186 | 18.5116 | 17.7788 | 16.3616 | 14.4261 | 16.577 | 17.0821 | 17.1782 | 17.1902 | 16.6933 | 15.7069 | 14.3152 | 14.8554 | 15.0465 | 16.0711 | 13.4551 | 13.8238 | 26.1426 |  |  |  | 16.7196 | 17.6909 | 64.8751 | 655.667 | 660.7617 | 661.9135 | 55.4986 | 62.0549 | 79.0598 | 65.8802 | 63.2172 | 398.4077 | 716.3643 | 645.9948 |  | 567.3104 | 924.9303 | 760.3052 | 792.5214 |  | 143.1429 | 291.5559 | 204.1585 | 374.6063 | 661.4142 | 868.0754 | 963.0253 | 30.9852 | 99.2917 | 53.7159 | 218.9037 | 14.1686 | 46.187 | 49.4908 | 48.4818 | 20.7165 |  |  | 1.3618 | 0.65786 | -0.84583 | -1.3944 | 7.4933 | 5.7046 | 3.5713 | -12.1351 | 16.706 | 41.9086 | 39.6523 | 0.0023673 | 0.0024576 | -0.00086411 | 16.4662 | 16.6197 | 17.1269 | 17.4498 | 17.3842 | 16.3303 | 14.6521 | 16.7239 | 17.0737 | 17.3638 | 17.398 | 17.099 | 16.2415 | 14.4269 | 749.8335 | 398.2862 | 570.2919 | 315.7889 | 257.1523 | 557.5813 | 264.9268 | 15.8108 | 15.7855 | 16.3227 | 14.7431 | 21.4495 | 34.4945 |  |  |  | 560.5547 | 565.3401 | 610.2162 | 541.8801 | 98.8589 | 44.3415 | 802.2442 |  |  | 493.5432 |  |  | 17.4625 | 18.976 | 122.8054 | 16.446 | 17.0208 | 139.0746 | 761.1171 | 578.6812 | 837.5759 | 824.0178 | 772.5233 |  | 849.1502 | 836.0101 | 842.5592 | 553.2869 | 743.9879 | 815.0819 |  | 882.4268 |  |  | 402.3486 | 619.8746 | 752.2845 | [6 empty] | 565.3822 |  |  | 330.9281 |  |  | 512.2458 | 677.6389 | 720.1826 | 994.9098 | 1090.3799 | 935.7968 | 695.2886 | 829.8107 | 853.6626 | 603.5983 | 708.919 | 1018.2432 | 1112.7948 | 762.5263 | 889.3229 | 553.5071 | 1009.1336 | 940.588 | 491.2428 | 633.5064 | 672.8474 | 958.2467 | 954.4341 | 860.4198 | 877.1955 | 1059.2693 | 571.6773 | 682.7499 | 998.7854 | 987.8843 | 117.7082 | 14.8435 | 6.4949 | 0.13354 | -38.1453 | 3.1245 | 14111.49 | 2.86 | 2.4868 | 1.3432 | -1.5231 | -1.9556 | 6.4445 | 5.623 | 4.4491 | 92.0823 | 88.0411 | 65.9852 | 5.6425 | -29.1765 | 52.2435 | 27.9113
42810.449 | 773 | 18.4973 | 18.5509 | 18.5234 | 18.509 | 17.7813 | 16.3661 | 14.4358 | 16.5842 | 17.0906 | 17.1785 | 17.1923 | 16.7028 | 15.7095 | 14.3115 | 14.8588 | 15.0489 | 16.0766 | 13.4595 | 13.8317 | 26.4085 |  |  |  | 16.7221 | 17.7064 | 65.7438 | 651.4798 | 659.2828 | 656.8467 | 22.6008 | 32.3945 | 63.4047 | 39.1983 | 29.574 | 392.6004 | 702.8914 | 665.7032 |  | 563.7412 | 930.5947 | 771.0713 | 768.5807 |  | 147.7965 | 299.9861 | 210.4035 | 385.4617 | 677.9505 | 878.6842 | 965.9511 | 31.152 | 102.88 | 55.569 | 226.0612 | 14.3922 | 46.248 | 49.4399 | 48.4487 | 20.9859 |  |  | 0.92741 | 0.50147 | -0.73543 | -1.1592 | 7.4492 | 5.5909 | 3.0798 | -11.6659 | 15.6534 | 39.5775 | 30.6237 | 0.0024116 | 0.0023459 | -0.00084768 | 16.477 | 16.6235 | 17.1347 | 17.4451 | 17.3891 | 16.3291 | 14.6654 | 16.7322 | 17.0703 | 17.3713 | 17.4038 | 17.1074 | 16.2441 | 14.4272 | 766.8182 | 411.6178 | 604.771 | 326.9819 | 255.3797 | 567.7361 | 271.2623 | 15.8087 | 15.7935 | 16.3279 | 14.7431 | 21.7497 | 35.1782 |  |  |  | 559.5088 | 557.3855 | 598.4801 | 540.2056 | 85.6855 | 49.7925 | 805.5664 |  |  | 504.1642 |  |  | 17.468 | 18.9883 | 122.9372 | 16.4506 | 17.0306 | 172.1314 | 757.3739 | 577.1323 | 840.5938 | 826.8614 | 765.8997 |  | 847.1339 | 839.3043 | 847.1551 | 551.33 | 740.7749 | 816.4435 |  | 886.1346 |  |  | 401.5356 | 615.3242 | 745.2601 | [6 empty] | 563.5077 |  |  | 328.6609 |  |  | 508.5892 | 672.822 | 713.1858 | 986.7732 | 1088.3317 | 939.8898 | 684.477 | 818.4862 | 848.53 | 599.9813 | 702.7299 | 1018.6286 | 1111.5001 | 750.5043 | 885.1598 | 586.6385 | 1012.1589 | 955.2162 | 490.4893 | 631.2795 | 669.0023 | 937.8376 | 924.7256 | 861.3083 | 878.9552 | 1065.2382 | 570.2164 | 679.9514 | 961.9862 | 971.2581 | 122.4333 | 14.6804 | 6.7649 | 0.14225 | -38.1857 | 3.1245 | 14158.2 | 2.47 | 2.0467 | 1.1815 | -1.4308 | -1.7962 | 6.4553 | 5.5925 | 4.1507 | 91.5655 | 89.5339 | 65.1871 | 6.2284 | -32.0758 | 49.6337 | 27.7915
42810.449 | 774 | 18.4937 | 18.5494 | 18.5222 | 18.5159 | 17.7782 | 16.3665 | 14.4304 | 16.5843 | 17.0875 | 17.178 | 17.1876 | 16.6938 | 15.7045 | 14.3161 | 14.8571 | 15.0577 | 16.0778 | 13.4653 | 13.83 | 26.6823 |  |  |  | 16.7215 | 17.7115 | 66.33 | 646.4917 | 655.46 | 651.6514 | 19.1179 | 17.4088 | 41.6748 | 16.9236 | 17.4808 | 389.6537 | 698.8933 | 698.7593 |  | 565.773 | 942.2604 | 790.296 | 758.6711 |  | 151.9119 | 306.9088 | 215.7731 | 394.3932 | 684.6465 | 881.9106 | 965.4463 | 31.0228 | 105.8414 | 57.7293 | 231.8888 | 14.6363 | 46.3541 | 49.3615 | 48.4034 | 21.2679 |  |  | 0.23941 | 0.38056 | -0.95885 | -1.3182 | 6.572 | 4.6808 | 3.1343 | -11.1409 | 16.5618 | 39.0889 | 22.3622 | 0.0023705 | 0.0023755 | -0.00085425 | 16.4766 | 16.6343 | 17.147 | 17.455 | 17.3968 | 16.335 | 14.6633 | 16.743 | 17.0735 | 17.3746 | 17.4083 | 17.114 | 16.2546 | 14.4384 | 779.8461 | 414.0651 | 611.2837 | 317.9808 | 246.852 | 576.6481 | 277.3754 | 15.8085 | 15.7901 | 16.3221 | 14.7499 | 22.0358 | 35.8227 |  |  |  | 558.0453 | 549.8772 | 589.6436 | 530.4708 | 90.1666 | 30.2855 | 811.0553 |  |  | 492.7569 |  |  | 17.4579 | 19.0059 | 122.6284 | 16.4512 | 17.039 | 213.4332 | 759.1723 | 576.154 | 840.347 | 828.1533 | 768.7667 |  | 846.5571 | 837.0144 | 851.8683 | 550.601 | 737.8481 | 816.2999 |  | 892.2236 |  |  | 401.2601 | 619.4499 | 746.9144 | [6 empty] | 562.2133 |  |  | 326.5832 |  |  | 504.8647 | 668.5541 | 706.4234 | 980.0712 | 1089.1722 | 951.0821 | 674.5455 | 808.3027 | 846.2989 | 596.7415 | 697.3037 | 1018.0732 | 1111.627 | 739.0306 | 879.0637 | 627.4074 | 1015.1328 | 966.6147 | 489.0906 | 628.5423 | 664.1609 | 910.9974 | 899.9048 | 861.344 | 886.4747 | 1070.2484 | 567.8881 | 676.5001 | 929.3636 | 956.5719 | 110.1027 | 14.4751 | 7.0851 | 0.15066 | -38.218 | 3.1245 | 14170.96 | 2.49 | 1.037 | 1.0354 | -1.6435 | -1.927 | 6.0718 | 5.1243 | 4.1932 | 91.2861 | 91.241 | 64.4371 | 6.9921 | -31.8927 | 48.9599 | 27.8302
42810.449 | 775 | 18.4843 | 18.5576 | 18.526 | 18.5127 | 17.778 | 16.3666 | 14.4347 | 16.5874 | 17.0882 | 17.173 | 17.1871 | 16.702 | 15.7032 | 14.3167 | 14.8481 | 15.0622 | 16.0736 | 13.4655 | 13.8306 | 26.9608 |  |  |  | 16.7212 | 17.7084 | 66.9363 | 644.1511 | 653.3492 | 649.7774 | 17.2078 | 17.3676 | 42.6397 | 16.9058 | 17.4776 | 403.1204 | 701.941 | 769.5005 |  | 568.5002 | 948.6304 | 810.2791 | 764.8358 |  | 156.4065 | 315.4214 | 222.2367 | 404.8156 | 694.1926 | 878.131 | 960.6394 | 31.1361 | 109.1604 | 58.5881 | 238.4478 | 14.9066 | 46.4663 | 49.2639 | 48.3144 | 21.553 |  |  | 1.4531 | 0.40093 | -0.74989 | -1.1992 | 6.6081 | 6.1889 | 3.089 | -10.2847 | 14.4644 | 37.8884 | 20.2109 | 0.0022654 | 0.0023623 | -0.00086246 | 16.4795 | 16.6335 | 17.143 | 17.4511 | 17.3954 | 16.3343 | 14.6609 | 16.7348 | 17.0723 | 17.3731 | 17.4123 | 17.1176 | 16.2503 | 14.4351 | 773.7522 | 393.305 | 540.4763 | 287.4316 | 227.1594 | 584.7922 | 281.233 | 15.8055 | 15.7892 | 16.3275 | 14.7696 | 22.3224 | 36.4472 |  |  |  | 556.3056 | 544.4465 | 582.4133 | 520.1565 | 94.9781 | 27.29 | 814.0152 |  |  | 481.8271 |  |  | 17.4527 | 19.0258 | 122.1253 | 16.4384 | 17.0417 | 262.6612 | 759.5429 | 575.9653 | 839.3569 | 828.0716 | 771.8022 |  | 846.2368 | 833.2983 | 856.0917 | 550.2601 | 734.6291 | 816.8493 |  | 897.8136 |  |  | 401.5124 | 622.4462 | 749.5547 | [6 empty] | 561.9121 |  |  | 325.2228 |  |  | 501.3021 | 663.9477 | 700.1052 | 963.4046 | 1089.289 | 957.3224 | 664.9745 | 797.2078 | 840.8087 | 593.6801 | 692.8331 | 1009.8078 | 1104.8574 | 728.6328 | 871.1874 | 669.4083 | 1015.0109 | 979.4842 | 487.5676 | 625.3367 | 659.831 | 881.022 | 881.2202 | 863.2363 | 892.5954 | 1070.4135 | 564.9665 | 673.7957 | 901.1474 | 945.0038 | 112.5583 | 14.2869 | 7.4419 | 0.17103 | -38.14 | 3.1245 | 14105 | 2.77 | 2.5521 | 1.0705 | -1.4641 | -1.8515 | 6.0785 | 5.8825 | 4.1559 | 91.0909 | 92.8331 | 63.6064 | 9.724 | -23.449 | 49.5112 | 27.8425
42810.449 | 776 | 18.4832 | 18.5529 | 18.524 | 18.5072 | 17.778 | 16.3617 | 14.4355 | 16.5839 | 17.0897 | 17.1755 | 17.1865 | 16.7029 | 15.7054 | 14.3161 | 14.8448 | 15.0649 | 16.0835 | 13.4776 | 13.8427 | 27.2587 |  |  |  | 16.7283 | 17.7354 | 67.917 | 643.7349 | 655.5226 | 649.3783 | 17.2092 | 17.3668 | 43.847 | 16.9044 | 17.4808 | 432.7896 | 705.9474 | 805.422 |  | 577.2178 | 954.9044 | 831.8627 | 781.6271 |  | 160.7268 | 323.4508 | 227.7644 | 413.8769 | 703.0273 | 877.016 | 955.4479 | 31.4398 | 112.2709 | 58.6845 | 244.5014 | 15.1996 | 46.5858 | 49.1445 | 48.1822 | 21.8447 |  |  | 1.9597 | 0.13808 | -1.0187 | -1.6809 | 5.079 | 5.3169 | 3.0456 | -10.6625 | 15.3972 | 37.7808 | 19.0556 | 0.0022211 | 0.0022999 | -0.00084111 | 16.4794 | 16.6311 | 17.1352 | 17.4428 | 17.3894 | 16.3251 | 14.6516 | 16.7338 | 17.0774 | 17.3697 | 17.3977 | 17.0988 | 16.2506 | 14.4314 | 793.6279 | 383.4124 | 506.7327 | 272.9184 | 214.4158 | 593.6471 | 285.1967 | 15.8063 | 15.7881 | 16.3399 | 14.7866 | 22.6209 | 37.0791 |  |  |  | 554.4661 | 538.8448 | 576.1377 | 512.6388 | 82.131 | 42.8805 | 814.8631 |  |  | 475.1689 |  |  | 17.4591 | 19.0515 | 122.1776 | 16.4456 | 17.0542 | 326.2373 | 756.1373 | 574.8681 | 837.1321 | 825.2144 | 767.0501 |  | 844.9936 | 828.8099 | 859.2018 | 549.8818 | 731.9585 | 815.3782 |  | 899.5309 |  |  | 399.2941 | 619.9826 | 745.6102 | [6 empty] | 561.6042 |  |  | 323.3806 |  |  | 498.1123 | 659.9755 | 694.4107 | 941.8624 | 1075.674 | 958.2973 | 655.6868 | 787.7065 | 833.9781 | 591.2011 | 689.7048 | 994.5894 | 1090.6597 | 718.7656 | 860.7474 | 701.2604 | 1010.0618 | 989.5099 | 486.2206 | 621.9642 | 656.522 | 851.8186 | 865.3643 | 866.5051 | 896.1824 | 1066.4237 | 561.7185 | 671.3481 | 874.0236 | 930.0866 | 97.132 | 14.174 | 7.8281 | 0.18823 | -38.2481 | 3.1245 | 14044.78 | 1.24 | 2.9632 | 0.63253 | -1.718 | -2.2069 | 5.3264 | 5.4498 | 4.1246 | 90.7936 | 94.0641 | 62.9252 | 9.7875 | -19.1045 | 50.0037 | 27.7629
42810.449 | 777 | 18.4807 | 18.5495 | 18.5186 | 18.5036 | 17.7731 | 16.358 | 14.4289 | 16.5789 | 17.0829 | 17.1796 | 17.1858 | 16.6888 | 15.7039 | 14.3145 | 14.8428 | 15.0604 | 16.0828 | 13.4772 | 13.8456 | 27.5592 |  |  |  | 16.7341 | 17.7384 | 68.9522 | 641.8848 | 657.3506 | 645.8753 | 17.21 | 17.3729 | 45.1093 | 16.9018 | 17.4981 | 463.4674 | 710.9628 | 807.8583 |  | 587.6807 | 953.5105 | 849.3379 | 785.963 |  | 164.0821 | 330.4752 | 231.6231 | 419.3769 | 704.5288 | 873.3468 | 945.6033 | 31.4659 | 115.2011 | 57.9139 | 250.084 | 15.5447 | 46.7511 | 49.0371 | 48.0665 | 22.1527 |  |  | 1.2179 | 0.21562 | -0.62175 | -0.94493 | 5.3557 | 4.8464 | 3.8184 | -9.3595 | 14.885 | 38.0502 | 16.2011 | 0.0022211 | 0.0022309 | -0.00081975 | 16.4828 | 16.6206 | 17.1362 | 17.4528 | 17.3901 | 16.3279 | 14.6538 | 16.7313 | 17.0794 | 17.3673 | 17.4054 | 17.0969 | 16.2539 | 14.4281 | 801.0963 | 387.5956 | 532.8736 | 284.608 | 223.8118 | 600.7565 | 289.815 | 15.7991 | 15.797 | 16.3514 | 14.8052 | 22.9346 | 37.6934 |  |  |  | 552.6111 | 533.5159 | 570.2614 | 505.7256 | 63.8164 | 25.413 | 812.5865 |  |  | 465.3905 |  |  | 17.455 | 19.0663 | 122.7944 | 16.4486 | 17.0578 | 403.8164 | 751.3487 | 571.1234 | 829.6772 | 817.5424 | 761.4351 |  | 843.6951 | 821.6168 | 861.4375 | 546.6852 | 728.8566 | 816.2932 |  | 900.2251 |  |  | 397.3932 | 618.4998 | 742.2451 | [6 empty] | 557.4662 |  |  | 321.7327 |  |  | 494.5947 | 656.3419 | 689.2509 | 923.2401 | 1059.2868 | 960.4478 | 647.298 | 779.1858 | 825.3033 | 588.2984 | 686.0827 | 986.1791 | 1076.8602 | 709.8785 | 853.2976 | 730.955 | 1007.3138 | 995.6562 | 484.9301 | 619.3478 | 654.1317 | 824.5252 | 847.4372 | 862.1692 | 898.7885 | 1061.9664 | 558.98 | 668.6431 | 848.2043 | 915.5765 | 79.569 | 13.9327 | 8.2225 | 0.20764 | -38.23 | 3.1245 | 13893.91 | 0.28 | 2.3315 | 0.79506 | -1.3501 | -1.6644 | 5.4608 | 5.1947 | 4.611 | 90.5025 | 95.0644 | 62.2168 | 10.8107 | -21.3113 | 51.0984 | 27.6657
42810.449 | 778 | 18.4728 | 18.546 | 18.521 | 18.5142 | 17.7731 | 16.3526 | 14.4359 | 16.5846 | 17.0807 | 17.1766 | 17.1865 | 16.6907 | 15.6929 | 14.3159 | 14.8419 | 15.0633 | 16.0952 | 13.5018 | 13.8526 | 27.898 |  |  |  | 16.7388 | 17.7592 | 69.7196 | 638.4116 | 657.376 | 641.7227 | 17.1938 | 17.3645 | 46.3475 | 16.8924 | 17.4885 | 488.1021 | 714.8696 | 801.5439 |  | 594.1876 | 950.394 | 864.0803 | 768.9691 |  | 168.3168 | 339.5739 | 236.5282 | 425.59 | 704.9888 | 873.6982 | 937.1178 | 31.6698 | 118.541 | 57.0819 | 256.3748 | 15.8847 | 46.9076 | 48.9365 | 47.9769 | 22.4688 |  |  | 1.8776 | 0.040831 | -1.1093 | -1.2393 | 5.9457 | 5.2617 | 3.6804 | -9.8122 | 15.0035 | 38.6964 | 15.0604 | 0.0021948 | 0.0022654 | -0.00079839 | 16.4838 | 16.6238 | 17.1331 | 17.4467 | 17.3859 | 16.3187 | 14.6496 | 16.7323 | 17.078 | 17.3716 | 17.4101 | 17.1052 | 16.2497 | 14.4313 | 755.8498 | 363.6771 | 492.8034 | 270.7343 | 212.3576 | 604.7844 | 292.8111 | 15.8035 | 15.8021 | 16.3479 | 14.8272 | 23.2918 | 38.4124 |  |  |  | 550.4323 | 527.2941 | 563.3232 | 501.0049 | 60.2926 | 35.3893 | 805.6718 |  |  | 447.1946 |  |  | 17.453 | 19.0869 | 123.0175 | 16.4502 | 17.0633 | 484.8292 | 742.3068 | 567.936 | 830.0505 | 818.7154 | 750.4501 |  | 840.8943 | 816.1719 | 863.6371 | 543.5511 | 725.4682 | 816.9588 |  | 900.2968 |  |  | 394.3499 | 616.4985 | 735.2798 | [6 empty] | 554.0213 |  |  | 320.099 |  |  | 490.5267 | 652.2492 | 683.0583 | 907.3699 | 1058.0724 | 954.3886 | 638.0415 | 775.7074 | 815.8335 | 584.5032 | 680.8498 | 984.7484 | 1072.3603 | 702.6709 | 843.4943 | 756.6134 | 1001.7339 | 1000.4388 | 484.2022 | 616.8269 | 651.291 | 796.9799 | 829.6482 | 856.5984 | 900.5168 | 1057.0788 | 556.7628 | 665.1983 | 823.6635 | 899.0291 | 86.2511 | 13.6778 | 8.624 | 0.22685 | -38.2442 | 3.1245 | 13743.08 | 0.24 | 2.8883 | 0.34857 | -1.8169 | -1.9204 | 5.7547 | 5.4136 | 4.5276 | 89.8483 | 96.0075 | 61.4405 | 16.8995 | -16.404 | 52.5285 | 27.4592
42810.4491 | 779 | 18.4757 | 18.548 | 18.5185 | 18.5082 | 17.7686 | 16.3561 | 14.4464 | 16.5816 | 17.0818 | 17.1777 | 17.1904 | 16.686 | 15.6896 | 14.3129 | 14.846 | 15.0605 | 16.1046 | 13.501 | 13.8589 | 28.2413 |  |  |  | 16.7274 | 17.7733 | 70.3837 | 634.3129 | 654.9456 | 637.6138 | 17.1998 | 17.377 | 47.7446 | 16.8954 | 17.5027 | 503.1728 | 717.2924 | 783.286 |  | 593.7971 | 946.5482 | 875.2959 | 749.4791 |  | 172.2845 | 347.6659 | 242.0373 | 431.7366 | 706.2971 | 872.182 | 929.7575 | 31.6423 | 121.342 | 56.4683 | 261.6731 | 16.2198 | 47.0466 | 48.8396 | 47.9047 | 22.7934 |  |  | 1.9985 | 0.39304 | -0.84846 | -1.1677 | 5.8669 | 5.2847 | 4.0891 | -9.5395 | 15.8401 | 38.8063 | 15.1828 | 0.0022194 | 0.0021849 | -0.00085425 | 16.4842 | 16.6157 | 17.1283 | 17.446 | 17.3815 | 16.3211 | 14.6491 | 16.7339 | 17.0779 | 17.3686 | 17.4111 | 17.0998 | 16.2493 | 14.4323 | 734.6651 | 347.7198 | 480.2006 | 273.4809 | 222.1736 | 607.2522 | 295.8493 | 15.8076 | 15.8108 | 16.3648 | 14.8494 | 23.6213 | 39.0331 |  |  |  | 548.7063 | 522.5441 | 555.1369 | 501.4538 | 62.7236 | 17.963 | 810.8098 |  |  | 428.9433 |  |  | 17.4466 | 19.1103 | 122.9926 | 16.4478 | 17.071 | 570.7642 | 731.8901 | 565.4142 | 837.4507 | 825.9533 | 736.7347 |  | 837.0451 | 822.6134 | 868.1051 | 541.6181 | 722.2373 | 828.9389 |  | 900.8519 |  |  | 391.0484 | 609.1139 | 722.8716 | [6 empty] | 551.8564 |  |  | 318.9 |  |  | 486.8826 | 648.9075 | 677.2496 | 917.9578 | 1062.0417 | 951.6303 | 630.0969 | 769.0028 | 806.1991 | 581.3637 | 676.6071 | 991.2033 | 1069.9515 | 694.0503 | 832.1556 | 780.4762 | 1005.284 | 1005.7408 | 483.3302 | 614.0159 | 648.2825 | 774.2054 | 813.5091 | 847.9916 | 907.3922 | 1058.4289 | 554.6647 | 661.863 | 803.4475 | 883.666 | 90.9519 | 13.3536 | 9.0304 | 0.24836 | -38.2063 | 3.1245 | 13563.59 | 0.26 | 2.9732 | 1.0886 | -1.5994 | -1.8763 | 5.7126 | 5.4218 | 4.7692 | 88.9215 | 97.4501 | 60.6782 | 19.9079 | -14.5401 | 53.6691 | 27.1808
42810.4491 | 780 | 18.4732 | 18.5478 | 18.52 | 18.5129 | 17.7852 | 16.3558 | 14.4393 | 16.5793 | 17.0892 | 17.1832 | 17.1853 | 16.6918 | 15.6907 | 14.3142 | 14.8325 | 15.0561 | 16.0982 | 13.5017 | 13.8646 | 28.5787 |  |  |  | 16.7304 | 17.775 | 70.7552 | 631.7387 | 652.7427 | 634.9912 | 17.204 | 17.3836 | 49.8058 | 16.8993 | 17.5152 | 515.5947 | 718.9116 | 734.268 |  | 591.2611 | 937.0019 | 883.0533 | 730.147 |  | 177.484 | 356.1882 | 247.6171 | 440.3109 | 705.8091 | 870.3224 | 923.7065 | 31.5712 | 124.567 | 56.0587 | 267.7615 | 16.5631 | 47.1452 | 48.7412 | 47.8635 | 23.1252 |  |  | 0.43983 | 0.41473 | -0.25705 | -1.6848 | 7.0964 | 5.1204 | 4.3671 | -10.0107 | 15.8599 | 41.8161 | 14.4809 | 0.0021701 | 0.0021307 | -0.00081646 | 16.4947 | 16.6188 | 17.1298 | 17.4452 | 17.375 | 16.3196 | 14.6456 | 16.7262 | 17.0746 | 17.3681 | 17.4069 | 17.1039 | 16.2511 | 14.4326 | 721.7467 | 334.2067 | 429.9849 | 259.3089 | 214.1227 | 609.6766 | 297.6624 | 15.806 | 15.8141 | 16.3765 | 14.8701 | 23.9556 | 39.6473 |  |  |  | 547.3365 | 518.1934 | 548.781 | 504.2234 | 72.249 | 31.4836 | 819.7284 |  |  | 412.1804 |  |  | 17.4456 | 19.1319 | 122.4675 | 16.4485 | 17.0771 | 650.8735 | 726.7641 | 562.8527 | 832.9363 | 820.7643 | 730.5844 |  | 833.8287 | 817.4384 | 871.2372 | 539.2214 | 719.05 | 828.6299 |  | 900.6015 |  |  | 387.9172 | 601.792 | 714.7061 | [6 empty] | 549.2891 |  |  | 319.3307 |  |  | 483.7001 | 646.0326 | 671.5682 | 932.3611 | 1063.2016 | 951.0838 | 622.3607 | 761.1722 | 797.5893 | 577.2125 | 672.1601 | 1000.6059 | 1066.9689 | 686.5293 | 824.7481 | 795.9321 | 1005.1196 | 1010.8437 | 482.1513 | 611.4127 | 644.1967 | 753.4105 | 799.0947 | 843.8644 | 907.705 | 1056.0432 | 552.6375 | 659.1255 | 786.0221 | 868.248 | 73.2105 | 13.0215 | 9.4409 | 0.27211 | -38.2571 | 3.1244 | 13364.32 | 0.33 | 1.3928 | 1.1259 | -0.88638 | -2.2693 | 6.2777 | 5.3325 | 4.9247 | 88.0092 | 98.7411 | 59.9468 | 21.9895 | -8.683 | 54.6088 | 26.8938
42810.4491 | 781 | 18.4689 | 18.5442 | 18.5185 | 18.5027 | 17.7687 | 16.3565 | 14.4424 | 16.5774 | 17.0788 | 17.1731 | 17.177 | 16.6897 | 15.6932 | 14.3071 | 14.8358 | 15.063 | 16.1089 | 13.519 | 13.884 | 28.93 |  |  |  | 16.7372 | 17.7847 | 71.1948 | 629.8838 | 650.5087 | 631.9461 | 17.1999 | 17.3892 | 53.8161 | 16.8979 | 17.5221 | 523.5512 | 719.5551 | 713.317 |  | 588.5823 | 918.9708 | 883.9213 | 717.4717 |  | 182.3224 | 364.425 | 253.056 | 447.9114 | 710.5838 | 872.0511 | 924.921 | 31.4357 | 127.6668 | 55.843 | 273.6549 | 16.9123 | 47.2329 | 48.6421 | 47.8367 | 23.4558 |  |  | 0.12836 | -0.12674 | -0.34642 | -1.558 | 6.0108 | 4.7636 | 4.1095 | -9.6736 | 15.7624 | 37.8029 | 14.1054 | 0.0021307 | 0.0021406 | -0.00080332 | 16.4943 | 16.618 | 17.1282 | 17.4465 | 17.3764 | 16.3162 | 14.6454 | 16.7285 | 17.0722 | 17.3633 | 17.3989 | 17.0968 | 16.2484 | 14.4268 | 743.492 | 332.9492 | 452.3732 | 256.7652 | 212.0694 | 613.3248 | 300.3393 | 15.8004 | 15.8118 | 16.3743 | 14.8836 | 24.2847 | 40.2602 |  |  |  | 545.7869 | 514.0507 | 543.9386 | 500.1157 | 70.9086 | 28.8991 | 812.6685 |  |  | 397.4739 |  |  | 17.442 | 19.1543 | 121.8885 | 16.4488 | 17.088 | 714.5573 | 720.0099 | 561.7127 | 823.0862 | 812.2534 | 724.8308 |  | 830.3018 | 802.7821 | 872.3824 | 538.5631 | 715.7438 | 827.3407 |  | 900.2207 |  |  | 384.7084 | 598.2265 | 710.873 | [6 empty] | 548.5026 |  |  | 319.4207 |  |  | 481.2782 | 642.7113 | 665.5886 | 930.3617 | 1059.2709 | 951.5225 | 614.3052 | 752.6871 | 791.1618 | 574.2115 | 667.9594 | 1001.1734 | 1062.535 | 678.8546 | 817.3583 | 815.1283 | 1000.4765 | 1014.7733 | 480.1635 | 608.4068 | 640.6384 | 734.0258 | 786.8126 | 836.444 | 910.5115 | 1054.7462 | 550.8529 | 656.5988 | 769.2797 | 855.891 | 70.8096 | 12.6292 | 9.8493 | 0.29689 | -38.1994 | 3.1245 | 13166.91 | 0.3 | 0.75114 | -0.62645 | -1.0357 | -2.1964 | 5.7819 | 5.1473 | 4.7808 | 86.9911 | 99.5699 | 59.1445 | 20.5515 | -10.7595 | 55.1214 | 26.7713
42810.4491 | 782 | 18.4602 | 18.5421 | 18.5219 | 18.5003 | 17.7646 | 16.3557 | 14.4329 | 16.576 | 17.0757 | 17.1746 | 17.1782 | 16.6845 | 15.6865 | 14.3025 | 14.8347 | 15.0627 | 16.1046 | 13.5266 | 13.894 | 29.2885 |  |  |  | 16.7363 | 17.7944 | 71.8831 | 628.2455 | 648.8766 | 629.0977 | 17.1998 | 17.397 | 60.1039 | 16.9042 | 17.523 | 528.3813 | 719.6371 | 714.6455 |  | 587.0352 | 908.5849 | 877.8655 | 704.6159 |  | 186.6334 | 372.1775 | 258.9006 | 454.849 | 709.3509 | 874.1934 | 925.4091 | 30.9799 | 130.5921 | 55.5493 | 279.1159 | 17.3409 | 47.3094 | 48.5685 | 47.8263 | 23.8116 |  |  | 0.29132 | 0.18408 | -1.0594 | -1.8603 | 5.1927 | 4.255 | 5.0347 | -8.3462 | 15.9247 | 38.6874 | 13.2244 | 0.0020765 | 0.0021389 | -0.00081154 | 16.5066 | 16.6238 | 17.1289 | 17.445 | 17.3946 | 16.3239 | 14.6558 | 16.7387 | 17.0815 | 17.3707 | 17.4088 | 17.1044 | 16.2555 | 14.433 | 745.5265 | 328.1932 | 466.9238 | 267.5793 | 212.5669 | 616.508 | 302.9922 | 15.8053 | 15.81 | 16.3787 | 14.9049 | 24.6436 | 40.8916 |  |  |  | 544.1792 | 510.1705 | 539.1733 | 496.638 | 60.1076 | 39.0175 | 802.0815 |  |  | 388.1093 |  |  | 17.433 | 19.1691 | 121.9166 | 16.4427 | 17.0849 | 759.6701 | 710.5804 | 562.1828 | 822.657 | 811.556 | 713.32 |  | 825.5675 | 799.8633 | 873.438 | 540.9464 | 712.5881 | 824.4867 |  | 900.4073 |  |  | 381.0791 | 591.6897 | 702.0149 | [6 empty] | 549.6947 |  |  | 320.555 |  |  | 479.0073 | 639.6949 | 661.0653 | 919.6865 | 1056.0396 | 951.364 | 606.3771 | 744.0512 | 784.1385 | 571.6434 | 665.8859 | 992.9421 | 1056.4746 | 670.7924 | 807.2241 | 828.4624 | 998.6845 | 1019.7798 | 478.8764 | 605.3195 | 637.327 | 716.5437 | 775.1766 | 831.6964 | 910.7759 | 1050.7051 | 548.8205 | 654.0617 | 753.426 | 844.9774 | 74.5476 | 12.2451 | 10.2611 | 0.3301 | -38.2219 | 3.1244 | 12959.61 | 0.32 | 1.1298 | 0.75955 | -1.8222 | -2.4146 | 5.3791 | 4.8693 | 5.2967 | 85.746 | 100.0407 | 58.3018 | 21.1848 | -11.9672 | 55.499 | 26.6235
42810.4491 | 783 | 18.4553 | 18.5422 | 18.5249 | 18.5041 | 17.7679 | 16.3556 | 14.4396 | 16.576 | 17.0775 | 17.1773 | 17.1787 | 16.6868 | 15.6873 | 14.3069 | 14.8291 | 15.0726 | 16.1182 | 13.5415 | 13.9141 | 29.6667 |  |  |  | 16.7505 | 17.8124 | 72.5637 | 627.6549 | 646.7477 | 627.2671 | 17.1963 | 17.4003 | 67.5857 | 16.9083 | 17.5353 | 528.8802 | 719.1014 | 713.4152 |  | 586.4063 | 902.0144 | 871.0972 | 696.143 |  | 191.0292 | 380.0726 | 264.2945 | 460.8155 | 707.3482 | 871.4706 | 913.7439 | 30.4461 | 133.9728 | 55.3358 | 285.4889 | 17.7597 | 47.3176 | 48.4951 | 47.8069 | 24.1549 |  |  | 0.35835 | -0.26867 | -1.4615 | -1.581 | 6.0883 | 4.6578 | 3.8414 | -9.1459 | 15.7523 | 38.8657 | 12.6543 | 0.0020699 | 0.002042 | -0.00082304 | 16.5157 | 16.6357 | 17.1422 | 17.4508 | 17.3947 | 16.3283 | 14.6594 | 16.7363 | 17.081 | 17.377 | 17.4158 | 17.1114 | 16.2635 | 14.4341 | 742.771 | 328.2144 | 488.0607 | 280.5737 | 212.4947 | 619.0105 | 305.8862 | 15.8061 | 15.8151 | 16.3937 | 14.9333 | 25.0259 | 41.5341 |  |  |  | 542.5059 | 506.7748 | 535.1746 | 492.6119 | 69.4382 | 30.0772 | 801.9194 |  |  | 379.1928 |  |  | 17.4295 | 19.2002 | 121.5204 | 16.4496 | 17.1017 | 786.3922 | 702.447 | 562.2674 | 823.532 | 813.2542 | 702.9572 |  | 821.0903 | 799.9603 | 875.959 | 542.5341 | 709.9528 | 824.0238 |  | 900.6597 |  |  | 378.1749 | 583.4185 | 692.3779 | [6 empty] | 550.3459 |  |  | 321.8145 |  |  | 476.0565 | 637.5552 | 657.0559 | 909.5227 | 1052.1944 | 950.5002 | 599.1607 | 735.0733 | 777.4097 | 568.7543 | 664.2922 | 983.838 | 1055.6433 | 663.1639 | 796.8651 | 838.043 | 996.0456 | 1022.8852 | 477.6039 | 602.7753 | 634.5676 | 701.3006 | 764.3285 | 825.7846 | 911.8401 | 1047.1214 | 546.7133 | 652.6295 | 738.9361 | 833.526 | 78.2618 | 11.9064 | 10.6693 | 0.36736 | -38.1479 | 3.1245 | 12741.39 | 0.26 | 1.2518 | -0.92323 | -2.1533 | -2.2396 | 5.8176 | 5.0885 | 4.6211 | 84.5709 | 100.9728 | 57.6143 | 22.1704 | -13.8677 | 55.6007 | 26.4823
42810.4491 | 784 | 18.4425 | 18.5353 | 18.511 | 18.4952 | 17.7615 | 16.3476 | 14.4381 | 16.5635 | 17.0732 | 17.1754 | 17.1711 | 16.6793 | 15.6857 | 14.3013 | 14.8241 | 15.0722 | 16.1223 | 13.5508 | 13.9305 | 30.0438 |  |  |  | 16.7583 | 17.8221 | 73.0515 | 626.7412 | 644.4172 | 624.3186 | 17.191 | 17.4014 | 76.4228 | 16.9079 | 17.5444 | 530.2926 | 718.4113 | 730.5036 |  | 585.6993 | 895.4361 | 865.8739 | 690.5378 |  | 194.555 | 385.4719 | 267.8495 | 465.193 | 700.5995 | 867.5087 | 904.1854 | 30.3372 | 136.6901 | 54.6515 | 290.7349 | 18.1012 | 47.3289 | 48.4244 | 47.785 | 24.5103 |  |  | 1.1397 | 0.88259 | -1.3032 | -1.6862 | 6.9827 | 4.7485 | 3.4024 | -8.885 | 15.9452 | 38.1014 | 12.7368 | 0.002042 | 0.0020321 | -0.00083618 | 16.5106 | 16.6244 | 17.1302 | 17.4476 | 17.396 | 16.3277 | 14.6513 | 16.7391 | 17.0721 | 17.3738 | 17.41 | 17.1067 | 16.2537 | 14.4241 | 751.4836 | 322.1837 | 482.6059 | 272.2883 | 202.2779 | 621.7622 | 308.3472 | 15.798 | 15.8198 | 16.3913 | 14.951 | 25.3775 | 42.1135 |  |  |  | 541.1461 | 504.7389 | 532.2019 | 495.2918 | 70.9421 | 31.6312 | 806.5684 |  |  | 369.094 |  |  | 17.4334 | 19.2299 | 121.2813 | 16.4584 | 17.1096 | 803.1844 | 698.8624 | 561.3379 | 824.2488 | 814.1279 | 698.3639 |  | 817.1722 | 800.2195 | 878.5858 | 542.439 | 707.2448 | 823.3009 |  | 899.9094 |  |  | 375.7111 | 578.3732 | 686.2033 | [6 empty] | 550.0259 |  |  | 321.8873 |  |  | 472.5361 | 636.3737 | 653.0534 | 897.0327 | 1046.2936 | 954.0095 | 592.5167 | 726.6373 | 771.9257 | 565.5533 | 662.0929 | 975.044 | 1056.4129 | 656.5398 | 789.4422 | 843.1992 | 993.8679 | 1025.0554 | 476.166 | 600.3861 | 632.478 | 686.4731 | 753.9199 | 820.4307 | 908.9604 | 1046.217 | 544.2165 | 650.2714 | 725.0318 | 824.1939 | 85.0639 | 11.5009 | 11.0625 | 0.40261 | -38.1856 | 3.1244 | 12553.84 | 0.23 | 2.2288 | 1.6802 | -2.0417 | -2.3224 | 6.2195 | 5.1289 | 4.3415 | 83.4316 | 101.9456 | 56.9605 | 21.9533 | -12.8791 | 55.5844 | 26.2032
42810.4491 | 785 | 18.4464 | 18.5316 | 18.509 | 18.4917 | 17.756 | 16.3475 | 14.4337 | 16.5643 | 17.0755 | 17.1719 | 17.1747 | 16.6759 | 15.686 | 14.2964 | 14.819 | 15.0633 | 16.1167 | 13.5608 | 13.9404 | 30.4234 |  |  |  | 16.755 | 17.8331 | 73.595 | 624.947 | 642.132 | 621.075 | 17.1866 | 17.4066 | 86.935 | 16.9086 | 17.5541 | 534.3327 | 717.8418 | 732.356 |  | 584.5744 | 887.5491 | 862.7746 | 684.7317 |  | 198.3066 | 390.8767 | 272.0268 | 469.7751 | 708.0801 | 871.5163 | 903.1362 | 30.4267 | 139.6644 | 54.8135 | 296.4034 | 18.4987 | 47.334 | 48.3359 | 47.7558 | 24.8675 |  |  | 1.5149 | -0.40995 | -1.0016 | -1.3458 | 6.0443 | 5.907 | 5.5558 | -6.6719 | 15.5067 | 37.8484 | 12.583 | 0.0020814 | 0.0020962 | -0.00080168 | 16.505 | 16.6179 | 17.1237 | 17.4427 | 17.3824 | 16.3209 | 14.6509 | 16.7286 | 17.0676 | 17.3652 | 17.4036 | 17.0967 | 16.2408 | 14.4222 | 744.1465 | 325.1062 | 486.9488 | 276.3443 | 207.6058 | 624.3736 | 310.9305 | 15.7998 | 15.8229 | 16.3972 | 14.9934 | 25.7354 | 42.703 |  |  |  | 540.1106 | 502.1546 | 528.071 | 499.7305 | 81.9955 | 36.0027 | 809.4687 |  |  | 360.8008 |  |  | 17.4353 | 19.2512 | 120.9431 | 16.4522 | 17.1104 | 815.914 | 698.5444 | 559.7455 | 824.2047 | 814.1535 | 696.1286 |  | 813.2278 | 794.3327 | 880.5518 | 542.0812 | 704.104 | 816.1548 |  | 899.5597 |  |  | 371.8859 | 575.4339 | 683.9079 | [6 empty] | 549.1916 |  |  | 321.4503 |  |  | 469.1386 | 634.994 | 649.2329 | 888.2782 | 1040.0354 | 959.0412 | 586.3393 | 719.7173 | 767.9103 | 562.7697 | 659.5769 | 967.2854 | 1057.0406 | 650.1646 | 784.1948 | 841.5392 | 993.4027 | 1027.2216 | 474.7514 | 597.0606 | 630.1086 | 673.0292 | 743.7036 | 817.5273 | 906.2007 | 1046.3343 | 541.7317 | 647.1783 | 712.8269 | 817.6594 | 83.9632 | 11.1478 | 11.4492 | 0.43799 | -38.2843 | 3.1245 | 12375.56 | 0.24 | 2.5649 | -1.1498 | -1.7972 | -2.0833 | 5.7967 | 5.7305 | 5.5575 | 82.2308 | 102.8467 | 56.2152 | 23.485 | -12.9587 | 55.6041 | 25.9245
42810.4491 | 786 | 18.4448 | 18.5384 | 18.5087 | 18.4873 | 17.7579 | 16.3446 | 14.4361 | 16.5716 | 17.073 | 17.1634 | 17.1664 | 16.6802 | 15.6841 | 14.2991 | 14.8152 | 15.0658 | 16.125 | 13.5773 | 13.9581 | 30.8225 |  |  |  | 16.7559 | 17.8448 | 74.1621 | 624.5421 | 640.4592 | 620.8228 | 17.1912 | 17.4138 | 100.9762 | 16.9071 | 17.5552 | 532.305 | 716.7437 | 695.0268 |  | 581.8275 | 887.6872 | 855.9832 | 673.5504 |  | 201.9438 | 396.3179 | 276.4607 | 474.3889 | 710.6915 | 871.5197 | 908.325 | 30.4915 | 142.4634 | 55.133 | 301.6768 | 18.9297 | 47.35 | 48.2855 | 47.7185 | 25.2276 |  |  | 1.1199 | -0.14842 | -0.83663 | -1.2492 | 6.4866 | 5.5016 | 3.2704 | -8.9323 | 15.0266 | 37.695 | 12.4023 | 0.0019878 | 0.0019631 | -0.00083125 | 16.5117 | 16.6235 | 17.1318 | 17.4473 | 17.38 | 16.3285 | 14.6526 | 16.7321 | 17.0709 | 17.3681 | 17.3984 | 17.0973 | 16.2481 | 14.4293 | 762.1517 | 323.9484 | 500.259 | 287.1846 | 226.7135 | 628.2581 | 313.8136 | 15.7977 | 15.8212 | 16.4052 | 15.024 | 26.1006 | 43.2725 |  |  |  | 539.1008 | 498.7655 | 523.5674 | 499.8314 | 78.0679 | 35.7341 | 810.609 |  |  | 354.0485 |  |  | 17.4316 | 19.282 | 121.0277 | 16.4539 | 17.1248 | 829.2002 | 699.804 | 557.9474 | 819.0996 | 807.8148 | 698.4226 |  | 810.5862 | 787.9588 | 881.3097 | 542.0022 | 701.649 | 810.1756 |  | 899.8453 |  |  | 367.8422 | 573.1023 | 683.673 | [6 empty] | 548.1252 |  |  | 321.4586 |  |  | 465.7865 | 633.4324 | 645.7521 | 879.9361 | 1034.9693 | 963.7792 | 580.3974 | 714.0019 | 765.7708 | 560.0032 | 657.3571 | 964.3847 | 1058.7636 | 643.711 | 780.3499 | 838.7636 | 992.3065 | 1028.8884 | 473.4959 | 594.2624 | 627.3857 | 659.6581 | 734.7971 | 816.9651 | 904.2818 | 1044.7382 | 540.2543 | 644.2359 | 701.4499 | 810.0536 | 74.5996 | 10.7349 | 11.8266 | 0.47236 | -38.3447 | 3.1245 | 12211.85 | 0.22 | 2.2051 | -0.69467 | -1.6493 | -2.0153 | 6.005 | 5.5303 | 4.2639 | 81.3284 | 103.309 | 55.6315 | 22.5572 | -13.986 | 55.6422 | 25.7707
42810.4491 | 787 | 18.4334 | 18.5319 | 18.506 | 18.4798 | 17.7585 | 16.3416 | 14.4369 | 16.5665 | 17.0675 | 17.164 | 17.1759 | 16.6742 | 15.6768 | 14.2997 | 14.8072 | 15.0711 | 16.1217 | 13.5887 | 13.9709 | 31.2236 |  |  |  | 16.7575 | 17.8536 | 74.5529 | 624.7553 | 638.0665 | 620.0034 | 17.1778 | 17.4164 | 119.4023 | 16.9 | 17.5459 | 525.9349 | 714.8223 | 691.3406 |  | 578.2251 | 889.8083 | 850.2334 | 660.3507 |  | 205.4633 | 402.389 | 281.0006 | 480.2719 | 721.432 | 878.022 | 912.0476 | 30.4997 | 145.0064 | 55.6594 | 306.3768 | 19.3412 | 47.3513 | 48.2551 | 47.6689 | 25.5925 |  |  | 1.2494 | -0.36264 | -0.81757 | -1.4811 | 6.2868 | 4.3621 | 4.7003 | -7.5498 | 13.7709 | 36.3066 | 12.1353 | 0.0019993 | 0.0019976 | -0.00083618 | 16.5117 | 16.6156 | 17.1333 | 17.4488 | 17.3856 | 16.3249 | 14.648 | 16.7321 | 17.0706 | 17.3705 | 17.4033 | 17.1018 | 16.2505 | 14.4249 | 782.161 | 317.1062 | 502.2732 | 295.1319 | 244.1831 | 631.5659 | 316.847 | 15.7971 | 15.8287 | 16.4132 | 15.0595 | 26.4909 | 43.8718 |  |  |  | 537.6357 | 495.114 | 520.2061 | 493.9164 | 70.3614 | 36.428 | 805.794 |  |  | 348.8068 |  |  | 17.4241 | 19.3069 | 120.8113 | 16.4531 | 17.1276 | 841.6567 | 699.49 | 557.302 | 820.8257 | 810.2155 | 696.5875 |  | 807.9044 | 784.716 | 882.5601 | 542.3756 | 699.4909 | 808.3988 |  | 900.9776 |  |  | 363.5681 | 569.5573 | 682.8596 | [6 empty] | 547.3117 |  |  | 321.1877 |  |  | 462.8237 | 631.1153 | 642.9598 | 868.2334 | 1036.6163 | 967.7054 | 573.7174 | 708.1841 | 763.9367 | 557.4131 | 655.4744 | 967.844 | 1058.258 | 637.3859 | 776.2507 | 835.4768 | 988.8719 | 1029.435 | 472.1851 | 591.9208 | 625.2236 | 646.2114 | 726.8288 | 812.351 | 902.3232 | 1040.764 | 538.4538 | 641.8153 | 691.4652 | 801.0167 | 75.3669 | 10.3987 | 12.1974 | 0.51651 | -38.2543 | 3.1245 | 12066.95 | 0.25 | 2.328 | -1.0908 | -1.6378 | -2.2044 | 5.9286 | 4.9384 | 5.1262 | 80.5335 | 103.8709 | 55.1093 | 21.2539 | -13.7325 | 55.534 | 25.7168
42810.4492 | 788 | 18.4323 | 18.5372 | 18.5058 | 18.4895 | 17.7581 | 16.3493 | 14.4426 | 16.5662 | 17.0649 | 17.1684 | 17.171 | 16.6727 | 15.6837 | 14.3005 | 14.8 | 15.0583 | 16.1195 | 13.6015 | 13.9847 | 31.6283 |  |  |  | 16.7561 | 17.864 | 74.9326 | 623.5616 | 634.4403 | 617.406 | 17.1798 | 17.4206 | 139.0729 | 16.9081 | 17.5547 | 519.6223 | 712.5862 | 688.2232 |  | 574.0454 | 882.8795 | 841.9486 | 650.1542 |  | 208.275 | 409.2532 | 284.5176 | 484.8653 | 717.3392 | 881.418 | 908.4813 | 29.8732 | 147.9879 | 55.0329 | 311.7171 | 19.7341 | 47.3596 | 48.224 | 47.6185 | 25.9602 |  |  | 0.88207 | -0.009769 | -1.0975 | -1.2446 | 5.9766 | 4.2623 | 3.022 | -8.176 | 15.1451 | 36.6487 | 12.3394 | 0.0019582 | 0.0019976 | -0.00087232 | 16.5167 | 16.6176 | 17.1317 | 17.441 | 17.3832 | 16.3285 | 14.6554 | 16.734 | 17.0764 | 17.3685 | 17.408 | 17.1087 | 16.2459 | 14.4217 | 768.8362 | 317.536 | 495.6489 | 280.2656 | 235.6193 | 633.9398 | 319.4696 | 15.7982 | 15.8266 | 16.4158 | 15.0948 | 26.8859 | 44.4546 |  |  |  | 536.2025 | 493.0993 | 517.9517 | 493.429 | 67.2428 | 26.332 | 810.9329 |  |  | 343.3578 |  |  | 17.4218 | 19.3385 | 120.0474 | 16.4488 | 17.1386 | 839.6587 | 699.6114 | 557.1202 | 833.6455 | 825.204 | 695.4645 |  | 804.9245 | 794.1149 | 885.1612 | 542.0508 | 697.1695 | 810.5092 |  | 901.8831 |  |  | 358.6239 | 563.4986 | 681.0541 | [6 empty] | 546.8577 |  |  | 319.8196 |  |  | 460.2552 | 628.6384 | 639.893 | 856.8074 | 1039.8262 | 968.6874 | 567.1879 | 702.7533 | 762.747 | 555.3375 | 653.0297 | 974.1048 | 1055.9229 | 631.5554 | 775.6069 | 844.6362 | 982.5174 | 1026.4685 | 470.5391 | 589.4558 | 623.0694 | 635.1584 | 719.2281 | 807.6912 | 900.5917 | 1034.7397 | 536.4386 | 639.4708 | 683.2342 | 794.1946 | 74.79 | 9.9592 | 12.5673 | 0.5697 | -38.2883 | 3.1244 | 11958.84 | 0.32 | 1.9532 | -0.17993 | -1.9072 | -2.0309 | 5.789 | 4.8887 | 4.1164 | 79.6316 | 104.5958 | 54.5711 | 23.3985 | -12.5821 | 55.2677 | 25.5177
42810.4492 | 789 | 18.4365 | 18.5327 | 18.5171 | 18.5039 | 17.7657 | 16.3517 | 14.4483 | 16.5722 | 17.0767 | 17.1754 | 17.1763 | 16.681 | 15.6911 | 14.3019 | 14.8018 | 15.0637 | 16.1248 | 13.6207 | 14.0037 | 32.0502 |  |  |  | 16.7651 | 17.8815 | 75.06 | 621.9954 | 630.5805 | 614.6954 | 17.1752 | 17.4282 | 158.6381 | 16.9002 | 17.5615 | 515.1948 | 710.4044 | 706.5661 |  | 570.6046 | 879.6872 | 840.0698 | 648.4334 |  | 211.435 | 414.3393 | 287.9685 | 488.66 | 712.7301 | 877.3977 | 908.3839 | 29.2586 | 150.5384 | 53.6149 | 316.0707 | 20.1089 | 47.3906 | 48.1971 | 47.5599 | 26.3167 |  |  | 0.97143 | -0.28247 | -0.82743 | -1.2373 | 5.3057 | 3.7589 | 4.8041 | -8.0255 | 13.4624 | 33.7772 | 12.4004 | 0.0018974 | 0.0019286 | -0.00086411 | 16.5244 | 16.6192 | 17.1318 | 17.4406 | 17.3877 | 16.3277 | 14.6542 | 16.7334 | 17.0742 | 17.3645 | 17.3957 | 17.0977 | 16.2472 | 14.425 | 751.2461 | 306.5638 | 469.1812 | 277.7521 | 231.023 | 634.9905 | 321.1574 | 15.7909 | 15.8225 | 16.4157 | 15.1222 | 27.251 | 44.9914 |  |  |  | 535.0084 | 491.2471 | 514.5091 | 493.1652 | 51.0682 | 21.9103 | 826.8904 |  |  | 337.9413 |  |  | 17.4188 | 19.3706 | 119.0074 | 16.4521 | 17.138 | 840.1531 | 698.6303 | 558.2641 | 840.2813 | 830.45 | 690.2824 |  | 801.8275 | 802.6116 | 888.87 | 542.5526 | 695.056 | 820.2578 |  | 902.8221 |  |  | 353.2448 | 555.5202 | 678.373 | [6 empty] | 547.6387 |  |  | 318.2923 |  |  | 457.8069 | 626.4466 | 636.3617 | 854.2148 | 1040.8862 | 971.6572 | 560.7111 | 699.9513 | 761.4374 | 553.6712 | 649.8944 | 980.1812 | 1050.9001 | 626.1782 | 774.4768 | 845.2273 | 981.4248 | 1024.1109 | 469.1239 | 586.8011 | 620.8974 | 624.5748 | 711.9137 | 804.2544 | 899.2358 | 1032.4396 | 534.2956 | 637.2578 | 674.5323 | 787.7854 | 70.652 | 9.547 | 12.9498 | 0.63823 | -38.2705 | 3.1244 | 11830.18 | 0.29 | 2.0466 | -0.97115 | -1.6621 | -2.0326 | 5.4449 | 4.583 | 5.1811 | 78.8132 | 105.7763 | 54.062 | 25.6479 | -9.3737 | 54.7826 | 25.3486
42810.4492 | 790 | 18.435 | 18.5308 | 18.5129 | 18.4983 | 17.7644 | 16.3479 | 14.4472 | 16.5688 | 17.0696 | 17.1718 | 17.1757 | 16.6795 | 15.6825 | 14.2959 | 14.8016 | 15.0697 | 16.1277 | 13.6341 | 14.0169 | 32.4724 |  |  |  | 16.7671 | 17.8928 | 75.5294 | 621.2529 | 629.1589 | 613.9474 | 17.1718 | 17.4291 | 183.9106 | 16.9058 | 17.5677 | 517.1835 | 708.6238 | 703.872 |  | 569.5749 | 881.7215 | 844.1513 | 646.6714 |  | 214.8267 | 419.2424 | 291.1032 | 492.9126 | 707.1217 | 875.8529 | 905.6921 | 28.7567 | 153.1959 | 51.6824 | 320.5817 | 20.532 | 47.4428 | 48.1942 | 47.5065 | 26.6838 |  |  | 0.79533 | -0.16485 | -1.1474 | -1.6158 | 6.7468 | 5.035 | 3.5247 | -7.0812 | 14.4683 | 36.8097 | 11.7065 | 0.001904 | 0.0019188 | -0.00082632 | 16.521 | 16.6187 | 17.1309 | 17.4399 | 17.3796 | 16.3198 | 14.6429 | 16.7264 | 17.0648 | 17.359 | 17.3994 | 17.0921 | 16.242 | 14.4193 | 728.4049 | 280.7244 | 441.961 | 264.2257 | 228.6168 | 635.2373 | 322.1825 | 15.7901 | 15.8267 | 16.4269 | 15.1643 | 27.6229 | 45.5214 |  |  |  | 533.7897 | 489.0817 | 511.3939 | 492.3542 | 70.4175 | 26.0821 | 832.464 |  |  | 334.386 |  |  | 17.4167 | 19.4014 | 117.8826 | 16.4565 | 17.1453 | 850.7666 | 693.7466 | 559.1735 | 835.6903 | 825.8166 | 681.6874 |  | 798.7612 | 797.8388 | 891.1146 | 543.2945 | 693.1317 | 826.0897 |  | 903.3495 |  |  | 348.8104 | 543.8373 | 671.8438 | [6 empty] | 548.7187 |  |  | 316.7037 |  |  | 455.3859 | 624.183 | 633.3261 | 851.9118 | 1038.3683 | 977.5597 | 554.2639 | 696.4415 | 760.1534 | 551.7812 | 647.2169 | 981.7548 | 1041.4457 | 621.2086 | 770.1862 | 846.8269 | 981.7259 | 1022.0615 | 468.3574 | 584.3206 | 619.0511 | 613.6413 | 704.7358 | 800.3927 | 899.9393 | 1030.7133 | 532.8004 | 635.3941 | 665.4042 | 781.6521 | 73.396 | 9.1645 | 13.3311 | 0.72627 | -38.2494 | 3.1244 | 11678.85 | 0.26 | 1.8511 | -0.74454 | -1.9643 | -2.331 | 6.1359 | 5.3006 | 4.4349 | 78.1066 | 106.7723 | 53.593 | 28.2552 | -6.1864 | 54.3988 | 25.1917
42810.4492 | 791 | 18.4274 | 18.53 | 18.5097 | 18.4841 | 17.759 | 16.345 | 14.439 | 16.5633 | 17.0661 | 17.1674 | 17.1732 | 16.6778 | 15.6794 | 14.2952 | 14.7879 | 15.0634 | 16.1404 | 13.6439 | 14.0423 | 32.9063 |  |  |  | 16.7731 | 17.8998 | 76.0463 | 620.8005 | 630.9373 | 613.847 | 17.1702 | 17.433 | 211.9853 | 16.9082 | 17.5763 | 531.2829 | 707.2213 | 665.7543 |  | 569.8401 | 870.3248 | 833.9714 | 649.3345 |  | 217.2147 | 423.9425 | 294.5816 | 495.0727 | 702.748 | 880.3281 | 907.2423 | 29.5062 | 155.747 | 50.9756 | 325.1323 | 20.9084 | 47.4957 | 48.1802 | 47.4585 | 27.0487 |  |  | 0.75065 | -0.11819 | -0.97002 | -1.8222 | 7.0845 | 5.292 | 5.4835 | -6.9708 | 14.2194 | 36.6108 | 12.2537 | 0.0018334 | 0.0019319 | -0.00080661 | 16.535 | 16.6249 | 17.1338 | 17.4507 | 17.3843 | 16.328 | 14.6539 | 16.7367 | 17.073 | 17.3674 | 17.4048 | 17.1021 | 16.2458 | 14.4298 | 726.4189 | 267.6452 | 425.6107 | 255.9713 | 225.5671 | 636.6259 | 323.1157 | 15.7858 | 15.8137 | 16.4191 | 15.1989 | 27.9864 | 46.0254 |  |  |  | 532.6631 | 486.5929 | 509.1053 | 491.8819 | 63.7344 | 22.1273 | 826.9414 |  |  | 331.8078 |  |  | 17.419 | 19.4453 | 117.817 | 16.4648 | 17.1569 | 846.6356 | 691.1049 | 558.6765 | 843.0904 | 839.6924 | 677.496 |  | 795.7543 | 801.8431 | 893.1028 | 542.1849 | 691.04 | 830.0691 |  | 903.3657 |  |  | 343.8526 | 535.5147 | 665.8722 | [6 empty] | 547.9109 |  |  | 316.282 |  |  | 452.6676 | 622.0728 | 630.8096 | 844.2629 | 1034.673 | 973.5526 | 548.0864 | 691.4809 | 757.9783 | 550.3461 | 646.1757 | 974.7976 | 1033.6752 | 616.2724 | 766.3038 | 842.5161 | 979.9597 | 1019.2066 | 467.2702 | 582.4035 | 617.6721 | 604.965 | 697.5359 | 800.3981 | 897.4263 | 1028.8359 | 531.1848 | 633.4121 | 657.2898 | 776.4962 | 75.0468 | 8.8032 | 13.7283 | 0.83399 | -38.1628 | 3.1244 | 11508.2 | 0.25 | 1.7982 | -0.63257 | -1.8122 | -2.4838 | 6.2998 | 5.4448 | 5.5425 | 77.3031 | 107.4298 | 53.1391 | 28.8667 | -4.2213 | 53.9855 | 25.0396
42810.4492 | 792 | 18.421 | 18.523 | 18.503 | 18.4918 | 17.7538 | 16.3446 | 14.4411 | 16.5613 | 17.0677 | 17.1626 | 17.1669 | 16.6726 | 15.676 | 14.2904 | 14.7869 | 15.0691 | 16.1377 | 13.669 | 14.083 | 33.3635 |  |  |  | 16.7767 | 17.9192 | 80.1498 | 621.2611 | 636.3039 | 616.9436 | 18.4299 | 36.3498 | 259.0628 | 26.368 | 18.0831 | 549.5663 | 706.4846 | 626.2504 |  | 575.254 | 850.3044 | 817.1357 | 669.8837 |  | 219.6193 | 429.0214 | 297.8775 | 500.1832 | 701.8984 | 888.6239 | 910.58 | 29.5161 | 158.073 | 50.5523 | 329.3385 | 21.2093 | 47.5389 | 48.1782 | 47.428 | 27.4135 |  |  | 1.0634 | -0.22004 | -1.1612 | -1.608 | 6.1376 | 6.3249 | 5.6531 | -6.8085 | 13.9752 | 35.4787 | 12.7839 | 0.0018826 | 0.0019073 | -0.00082304 | 16.5301 | 16.6204 | 17.1334 | 17.4495 | 17.3808 | 16.3214 | 14.6473 | 16.7346 | 17.0733 | 17.3631 | 17.3987 | 17.0955 | 16.2462 | 14.4265 | 719.1068 | 263.6324 | 425.4934 | 259.8922 | 228.986 | 637.8375 | 324.1543 | 15.7833 | 15.8293 | 16.4319 | 15.2558 | 28.4173 | 46.6047 |  |  |  | 531.2878 | 483.8122 | 507.5742 | 489.0638 | 60.7825 | 27.9963 | 836.4765 |  |  | 330.1769 |  |  | 17.4159 | 19.4796 | 124.0276 | 16.4666 | 17.1624 | 836.2904 | 688.6088 | 558.2939 | 855.1707 | 851.0208 | 676.2522 |  | 792.8093 | 820.2273 | 896.6317 | 541.0127 | 688.9607 | 846.173 |  | 902.8937 |  |  | 340.3146 | 532.8947 | 663.0318 | [6 empty] | 547.8822 |  |  | 315.5138 |  |  | 450.6106 | 620.4932 | 627.9051 | 828.7138 | 1027.5412 | 968.9971 | 542.5902 | 686.5461 | 756.9746 | 549.3997 | 645.5258 | 973.1478 | 1026.4183 | 611.2201 | 767.3188 | 849.9541 | 979.4815 | 1016.9826 | 466.3836 | 580.9277 | 617.1115 | 596.6581 | 691.6194 | 802.9881 | 893.658 | 1026.7682 | 529.9317 | 631.1197 | 649.7029 | 774.8012 | 69.8562 | 8.3981 | 14.1442 | 0.98369 | -38.1617 | 3.1244 | 11367.34 | 0.29 | 2.1441 | -0.86625 | -1.99 | -2.3417 | 5.8848 | 5.9739 | 5.6477 | 76.4435 | 108.2925 | 52.6926 | 30.0211 | -4.0428 | 53.237 | 24.9168
42810.4492 | 793 | 18.4168 | 18.5249 | 18.5104 | 18.5013 | 17.7616 | 16.348 | 14.4444 | 16.5628 | 17.0691 | 17.1743 | 17.1736 | 16.6763 | 15.6739 | 14.2924 | 14.7877 | 15.0677 | 16.1481 | 13.7009 | 14.1297 | 33.8512 |  |  |  | 16.7859 | 17.9434 | 79.8171 | 623.3731 | 639.5306 | 620.1218 | 45.2767 | 59.718 | 301.3127 | 65.1086 | 58.9873 | 579.6444 | 727.1048 | 586.5915 |  | 596.9899 | 842.5869 | 798.5727 | 702.5306 |  | 223.267 | 434.8633 | 301.56 | 505.0989 | 708.1915 | 889.9515 | 907.3554 | 28.6602 | 160.6721 | 49.8904 | 334.0595 | 21.4932 | 47.5421 | 48.1711 | 47.3958 | 27.7632 |  |  | 0.91624 | -0.32124 | -0.926 | -0.9929 | 5.6349 | 3.4021 | 4.3914 | -6.2112 | 12.6515 | 33.1442 | 13.2132 | 0.0018892 | 0.0018169 | -0.00084768 | 16.5274 | 16.6151 | 17.1253 | 17.4404 | 17.3815 | 16.3209 | 14.6476 | 16.7277 | 17.0688 | 17.3628 | 17.4057 | 17.0998 | 16.2477 | 14.4262 | 721.9955 | 260.7963 | 436.6864 | 264.5351 | 225.609 | 638.2342 | 325.3083 | 15.7836 | 15.8344 | 16.4484 | 15.3127 | 28.8027 | 47.1109 |  |  |  | 530.0657 | 481.9209 | 505.8961 | 488.2853 | 52.0194 | 21.4631 | 845.3835 |  |  | 326.727 |  |  | 17.4086 | 19.5044 | 123.0221 | 16.4538 | 17.1594 | 809.6044 | 685.1836 | 557.509 | 847.9542 | 842.3715 | 671.7855 |  | 790.364 | 815.4628 | 899.0451 | 540.711 | 687.1815 | 845.834 |  | 903.0989 |  |  | 336.9255 | 532.0941 | 661.3745 | [6 empty] | 547.3423 |  |  | 315.2318 |  |  | 448.8415 | 618.9119 | 625.7611 | 815.9141 | 1026.6104 | 969.704 | 537.047 | 685.1442 | 758.612 | 548.0242 | 644.0181 | 971.5678 | 1020.939 | 607.2001 | 764.9707 | 844.9927 | 976.6756 | 1014.8961 | 465.5764 | 578.903 | 617.7146 | 588.4268 | 686.2451 | 805.957 | 893.1209 | 1024.272 | 528.9019 | 630.2157 | 641.743 | 772.018 | 69.3423 | 8.0518 | 14.5779 | 1.207 | -38.2115 | 3.1244 | 11274.81 | 0.24 | 1.9937 | -1.051 | -1.7844 | -1.8477 | 5.6418 | 4.3838 | 4.9806 | 75.8302 | 109.3708 | 52.2931 | 29.8123 | -5.1023 | 57.4404 | 24.7606
42810.4492 | 794 | 18.412 | 18.5227 | 18.5115 | 18.4871 | 17.7585 | 16.3472 | 14.4532 | 16.5649 | 17.0719 | 17.1641 | 17.1653 | 16.6739 | 15.6793 | 14.2951 | 14.7828 | 15.0642 | 16.1433 | 13.7185 | 14.1306 | 34.3023 |  |  |  | 16.7887 | 17.9503 | 80.2491 | 624.8776 | 642.5658 | 621.6105 | 71.7958 | 69.0095 | 331.8905 | 83.5308 | 87.2588 | 630.7334 | 763.0448 | 543.7468 |  | 608.873 | 827.8517 | 800.8166 | 689.6067 |  | 226.2178 | 438.1179 | 302.9309 | 505.8997 | 708.1471 | 881.6789 | 900.8065 | 27.6666 | 162.642 | 48.8255 | 337.7077 | 21.7712 | 47.5255 | 48.1899 | 47.3855 | 28.1028 |  |  | 0.98589 | -0.38104 | -1.3643 | -1.65 | 5.012 | 4.5494 | 4.7154 | -6.3512 | 13.4638 | 32.8069 | 13.0384 | 0.0018646 | 0.0018859 | -0.00082304 | 16.5293 | 16.6138 | 17.1193 | 17.4343 | 17.3766 | 16.3146 | 14.6468 | 16.7283 | 17.0695 | 17.3585 | 17.3995 | 17.0928 | 16.242 | 14.4193 | 683.409 | 249.5897 | 407.5557 | 253.7445 | 213.9262 | 636.863 | 325.5551 | 15.7852 | 15.8433 | 16.4574 | 15.3628 | 29.1833 | 47.5903 |  |  |  | 529.2668 | 481.5972 | 504.4643 | 494.3948 | 55.2934 | 21.142 | 836.7433 |  |  | 325.1022 |  |  | 17.4079 | 19.5426 | 122.2627 | 16.4579 | 17.165 | 781.9074 | 683.9452 | 557.0399 | 847.1941 | 845.8057 | 667.7067 |  | 787.8104 | 813.5454 | 900.6373 | 539.9527 | 685.4815 | 844.3596 |  | 903.0513 |  |  | 333.9931 | 529.1642 | 658.2878 | [6 empty] | 546.5934 |  |  | 312.7975 |  |  | 447.1541 | 616.6144 | 623.868 | 802.2456 | 1024.4605 | 969.0518 | 532.3178 | 681.7749 | 756.3435 | 546.0004 | 641.7678 | 966.0701 | 1012.9944 | 602.9151 | 760.3842 | 841.8762 | 975.8737 | 1012.4823 | 465.2016 | 577.6846 | 618.995 | 580.7166 | 681.3034 | 809.5777 | 893.8358 | 1024.2406 | 528.0992 | 630.7544 | 635.4867 | 773.7789 | 73.0345 | 7.7868 | 15.0127 | 1.4852 | -38.2761 | 3.1244 | 11199.76 | 0.26 | 2.0698 | -1.1473 | -2.1709 | -2.3874 | 5.3019 | 5.0513 | 5.1426 | 75.1784 | 110.051 | 51.9264 | 33.7124 | -1.8261 | 67.4055 | 24.4749
42810.4492 | 795 | 18.3983 | 18.5186 | 18.5016 | 18.4847 | 17.7478 | 16.334 | 14.4399 | 16.5669 | 17.0657 | 17.1602 | 17.1631 | 16.6687 | 15.6696 | 14.2977 | 14.7835 | 15.0713 | 16.1521 | 13.7465 | 14.1643 | 34.7947 |  |  |  | 16.7963 | 17.9766 | 81.0421 | 626.1952 | 645.3309 | 623.6285 | 67.9398 | 75.591 | 360.6216 | 75.057 | 77.9064 | 640.3581 | 766.443 | 523.498 |  | 646.4495 | 807.983 | 785.6471 | 711.5519 |  | 227.9709 | 440.7578 | 303.8033 | 504.3192 | 703.2537 | 870.9912 | 895.3774 | 26.2557 | 164.8129 | 47.4376 | 341.7351 | 22.0504 | 47.5171 | 48.2031 | 47.3823 | 28.3571 |  |  | 0.65142 | -0.49275 | -1.2421 | -1.9464 | 6.0069 | 5.3563 | 4.2928 | -5.7979 | 13.8592 | 34.9798 | 13.2138 | 0.0017512 | 0.0017644 | -0.00084111 | 16.5373 | 16.6139 | 17.1248 | 17.4365 | 17.3801 | 16.3158 | 14.6516 | 16.7235 | 17.0719 | 17.3595 | 17.3942 | 17.0889 | 16.2381 | 14.4138 | 668.4902 | 250.8648 | 408.0399 | 236.3841 | 196.8618 | 636.3257 | 325.9673 | 15.7839 | 15.8414 | 16.4635 | 15.4056 | 29.5624 | 48.0539 |  |  |  | 528.9932 | 482.9748 | 503.7427 | 503.8109 | 70.9848 | 28.6473 | 839.6671 |  |  | 324.2755 |  |  | 17.407 | 19.5895 | 121.9205 | 16.4554 | 17.1827 | 778.5616 | 686.7293 | 558.1141 | 853.2493 | 853.5547 | 672.4409 |  | 785.4721 | 822.0221 | 903.8141 | 541.0558 | 683.5206 | 849.268 |  | 902.4191 |  |  | 332.0619 | 527.2009 | 659.3159 | [6 empty] | 547.4105 |  |  | 312.1231 |  |  | 445.8301 | 614.4415 | 622.0139 | 794.4605 | 1020.201 | 964.6633 | 527.8126 | 679.1362 | 757.1549 | 545.0617 | 639.3122 | 961.1675 | 1005.2063 | 598.7586 | 763.6879 | 838.6735 | 978.2191 | 1010.6305 | 464.7509 | 576.8927 | 619.1076 | 573.0518 | 677.0603 | 811.9602 | 892.6566 | 1023.9007 | 527.6821 | 629.6377 | 629.8004 | 773.0506 | 70.6647 | 7.4279 | 15.4152 | 1.8157 | -38.2593 | 3.1245 | 11134.82 | 0.26 | 1.6844 | -1.3071 | -2.0752 | -2.5978 | 5.7774 | 5.4556 | 4.884 | 74.3507 | 111.0737 | 51.4507 | 35.2187 | -1.814 | 67.752 | 24.1737
42810.4492 | 796 | 18.3993 | 18.5111 | 18.4974 | 18.4801 | 17.7452 | 16.3388 | 14.4415 | 16.5615 | 17.0623 | 17.1634 | 17.1603 | 16.6669 | 15.6807 | 14.2882 | 14.7779 | 15.0618 | 16.147 | 13.7677 | 14.1812 | 35.2874 |  |  |  | 16.7984 | 17.9852 | 83.2971 | 626.9047 | 649.6922 | 625.6361 | 59.8326 | 66.1123 | 394.0569 | 79.3331 | 83.4753 | 657.8349 | 765.0394 | 545.8115 |  | 646.7073 | 790.8149 | 777.6377 | 714.3156 |  | 229.5593 | 443.0196 | 304.8392 | 504.0786 | 703.6026 | 870.9783 | 894.5365 | 26.7409 | 167.0097 | 46.3729 | 345.8388 | 22.2785 | 47.509 | 48.198 | 47.3714 | 28.4967 |  |  | 1.1889 | -0.041969 | -0.78406 | -2.0443 | 6.4537 | 5.3288 | 5.6077 | -6.3242 | 13.6491 | 33.4627 | 14.4313 | 0.0017676 | 0.0017594 | -0.00084439 | 16.5373 | 16.6102 | 17.1214 | 17.4349 | 17.3779 | 16.3209 | 14.657 | 16.7235 | 17.0611 | 17.3608 | 17.3925 | 17.0964 | 16.2391 | 14.4133 | 691.6172 | 240.4952 | 415.5688 | 229.1925 | 190.7192 | 636.6317 | 326.7395 | 15.7769 | 15.8437 | 16.4711 | 15.4572 | 29.9492 | 48.5239 |  |  |  | 528.6925 | 482.0813 | 501.0518 | 505.7346 | 48.2987 | 23.9266 | 847.8874 |  |  | 320.4016 |  |  | 17.4105 | 19.6293 | 125.3823 | 16.4501 | 17.1898 | 789.4882 | 690.4336 | 558.8065 | 851.5295 | 851.4509 | 677.4303 |  | 783.8155 | 821.37 | 906.0616 | 542.3716 | 682.0667 | 848.4765 |  | 901.8778 |  |  | 329.5913 | 526.5639 | 661.5488 | [6 empty] | 548.3516 |  |  | 312.6371 |  |  | 444.5918 | 612.5843 | 620.1645 | 788.6856 | 1016.9387 | 959.9795 | 523.5233 | 677.5906 | 757.5581 | 544.1343 | 636.9246 | 955.949 | 1002.2003 | 595.0497 | 766.4297 | 832.4695 | 974.9962 | 1007.2215 | 464.7626 | 576.3958 | 619.2561 | 565.9294 | 672.7181 | 811.8083 | 891.4423 | 1020.9238 | 527.7178 | 628.2842 | 624.1687 | 770.3219 | 72.0728 | 7.0407 | 15.7729 | 2.1629 | -38.2344 | 3.1245 | 11063.94 | 0.32 | 2.2781 | -0.38207 | -1.6514 | -2.6665 | 5.9884 | 5.4415 | 5.5821 | 73.7214 | 111.9877 | 51.0857 | 32.7352 | -2.527 | 67.2793 | 24.0767
42810.4493 | 797 | 18.394 | 18.5047 | 18.4934 | 18.4741 | 17.7411 | 16.3335 | 14.4379 | 16.5583 | 17.0561 | 17.1564 | 17.1554 | 16.6642 | 15.6699 | 14.2794 | 14.7822 | 15.0637 | 16.1541 | 13.8029 | 14.2261 | 35.7961 |  |  |  | 16.8009 | 18.0058 | 84.4063 | 628.6212 | 653.6242 | 629.1631 | 58.2548 | 61.9305 | 421.6302 | 67.3403 | 75.8974 | 673.5916 | 768.3148 | 555.4129 |  | 653.953 | 801.7574 | 772.3253 | 750.0069 |  | 231.1338 | 445.7975 | 305.7585 | 507.7691 | 703.7785 | 868.0343 | 895.6792 | 27.056 | 168.8743 | 45.8106 | 349.3714 | 22.5091 | 47.4948 | 48.1584 | 47.3768 | 28.5036 |  |  | 1.4104 | -0.73983 | -0.73938 | -1.6993 | 5.907 | 5.108 | 5.339 | -5.8505 | 13.0226 | 33.5118 | 14.1026 | 0.001789 | 0.001743 | -0.00081482 | 16.5482 | 16.6145 | 17.1212 | 17.4418 | 17.3844 | 16.3142 | 14.6462 | 16.7208 | 17.0567 | 17.3575 | 17.3933 | 17.0944 | 16.2358 | 14.413 | 673.9879 | 242.6294 | 417.0289 | 234.052 | 193.2407 | 635.5265 | 327.1751 | 15.7659 | 15.8472 | 16.469 | 15.5111 | 30.3827 | 49.0228 |  |  |  | 528.1348 | 480.9012 | 499.4481 | 504.7027 | 62.0929 | 32.5421 | 847.9318 |  |  | 316.1834 |  |  | 17.4099 | 19.6651 | 126.7155 | 16.4568 | 17.1978 | 763.9799 | 691.44 | 559.1788 | 854.1227 | 856.1241 | 678.3676 |  | 782.1576 | 823.5529 | 908.1417 | 542.6155 | 680.7604 | 848.2673 |  | 901.1179 |  |  | 326.8848 | 524.7796 | 661.876 | [6 empty] | 548.4723 |  |  | 313.1722 |  |  | 443.5646 | 610.9251 | 618.5141 | 779.7879 | 1011.1805 | 956.9577 | 519.4135 | 675.4349 | 759.0769 | 543.8512 | 636.327 | 952.5419 | 1002.663 | 591.5849 | 767.5676 | 823.4615 | 973.2441 | 1003.7878 | 464.8793 | 575.8095 | 619.9392 | 559.1227 | 669.6601 | 813.8677 | 886.9243 | 1019.7732 | 527.4359 | 627.1466 | 619.3494 | 770.4306 | 79.5659 | 6.5414 | 16.089 | 2.4939 | -38.1763 | 3.1245 | 10980.31 | 0.31 | 2.4861 | -1.6072 | -1.6067 | -2.4359 | 5.7217 | 5.3207 | 5.4397 | 73.2064 | 112.7605 | 50.785 | 34.3828 | -2.6195 | 67.214 | 24.0248
42810.4493 | 798 | 18.3895 | 18.5164 | 18.5039 | 18.4842 | 17.7493 | 16.3338 | 14.4483 | 16.5613 | 17.0654 | 17.1627 | 17.1597 | 16.6696 | 15.6728 | 14.2876 | 14.7803 | 15.0637 | 16.1571 | 13.8291 | 14.2554 | 36.3029 |  |  |  | 16.8127 | 18.0228 | 86.0534 | 629.1729 | 656.9369 | 629.7587 | 79.7852 | 58.25 | 440.2051 | 59.8068 | 58.311 | 674.1809 | 761.0586 | 559.6253 |  | 654.3942 | 792.3469 | 770.183 | 746.0087 |  | 232.8346 | 449.0187 | 307.0706 | 511.6736 | 702.9019 | 865.0997 | 893.7789 | 26.6595 | 171.2576 | 46.2716 | 353.4215 | 22.776 | 47.4204 | 48.1041 | 47.3711 | 28.3781 |  |  | 1.8066 | -0.19705 | -1.2329 | -1.629 | 6.1304 | 5.2256 | 5.8108 | -5.6336 | 13.5457 | 33.6895 | 14.7991 | 0.0017479 | 0.0017972 | -0.00083125 | 16.5391 | 16.6124 | 17.1165 | 17.4417 | 17.3716 | 16.3235 | 14.6487 | 16.7336 | 17.0626 | 17.3567 | 17.3974 | 17.0903 | 16.2394 | 14.4102 | 678.3856 | 252.6105 | 431.2775 | 247.7913 | 212.0759 | 635.433 | 328.0992 | 15.7741 | 15.8505 | 16.4849 | 15.5712 | 30.7572 | 49.4532 |  |  |  | 527.5694 | 479.6544 | 499.9385 | 502.2624 | 72.0422 | 30.6068 | 853.3333 |  |  | 313.7251 |  |  | 17.4103 | 19.7213 | 130.5604 | 16.4536 | 17.2175 | 775.1477 | 692.0298 | 558.9449 | 855.2782 | 858.2048 | 677.2002 |  | 780.4231 | 826.1214 | 910.6718 | 541.4841 | 679.2233 | 848.0958 |  | 900.5607 |  |  | 325.5079 | 522.7509 | 661.5723 | [6 empty] | 547.8446 |  |  | 311.8348 |  |  | 442.7794 | 609.9315 | 617.6426 | 770.1619 | 1006.7457 | 955.482 | 515.8552 | 674.0463 | 760.8081 | 543.5356 | 636.7122 | 946.8693 | 1002.5954 | 589.2477 | 770.5082 | 817.2967 | 974.6065 | 1002.1089 | 464.503 | 575.396 | 620.7028 | 553.79 | 667.7909 | 817.7461 | 883.3023 | 1018.4793 | 526.6045 | 625.898 | 615.7812 | 772.6202 | 77.8549 | 6.1319 | 16.3649 | 2.8192 | -38.2096 | 3.1245 | 10921.51 | 0.28 | 2.8146 | -0.83132 | -2.0794 | -2.3903 | 5.8214 | 5.3747 | 5.6676 | 72.7294 | 113.7084 | 50.4718 | 33.8679 | -4.0545 | 65.2838 | 24.0109
42810.4493 | 799 | 18.382 | 18.5114 | 18.4953 | 18.4691 | 17.7501 | 16.3275 | 14.4359 | 16.5592 | 17.0667 | 17.1537 | 17.1573 | 16.667 | 15.6706 | 14.2834 | 14.7745 | 15.0699 | 16.1647 | 13.8607 | 14.2795 | 36.8171 |  |  |  | 16.8192 | 18.0398 | 86.7959 | 629.2166 | 661.4921 | 631.5951 | 82.0951 | 67.4182 | 448.8506 | 71.7704 | 73.889 | 695.2394 | 760.7985 | 571.367 |  | 652.4273 | 788.573 | 767.468 | 746.9383 |  | 233.6697 | 451.3641 | 307.6833 | 511.5562 | 700.3607 | 861.56 | 886.2236 | 26.4894 | 173.175 | 46.1219 | 356.7977 | 22.9863 | 47.3778 | 48.0843 | 47.3751 | 28.2261 |  |  | 0.75525 | 0.14203 | -0.91088 | -1.7532 | 5.9753 | 4.625 | 4.996 | -5.9168 | 13.285 | 33.3196 | 14.2958 | 0.0017463 | 0.0017282 | -0.00083289 | 16.5523 | 16.6154 | 17.1306 | 17.4435 | 17.3802 | 16.3204 | 14.6494 | 16.7281 | 17.0752 | 17.3693 | 17.4044 | 17.1025 | 16.2498 | 14.4198 | 706.3398 | 255.7297 | 449.2829 | 248.9644 | 202.4702 | 636.2199 | 329.0692 | 15.7729 | 15.8478 | 16.4895 | 15.6325 | 31.1335 | 49.8834 |  |  |  | 527.0308 | 479.5331 | 500.4683 | 500.0308 | 66.0493 | 28.6305 | 855.0663 |  |  | 311.1968 |  |  | 17.4162 | 19.779 | 130.0473 | 16.4656 | 17.2408 | 751.4 | 692.3227 | 558.3442 | 855.3289 | 859.212 | 675.4454 |  | 779.1241 | 825.9881 | 912.855 | 540.597 | 677.8056 | 845.1033 |  | 900.2476 |  |  | 325.1013 | 520.7561 | 661.4608 | [6 empty] | 547.0307 |  |  | 310.5116 |  |  | 441.4943 | 609.0857 | 616.6477 | 759.7404 | 1002.944 | 953.2321 | 512.601 | 674.3993 | 761.0776 | 542.4114 | 636.3707 | 939.5388 | 1002.0695 | 588.1658 | 771.0756 | 811.5317 | 975.1415 | 1000.6919 | 463.5226 | 575.187 | 620.6375 | 548.6421 | 665.9459 | 822.4551 | 881.2195 | 1017.0254 | 526.0199 | 624.8482 | 612.0244 | 773.9255 | 74.9172 | 5.6343 | 16.562 | 3.1299 | -38.2308 | 3.1245 | 10791.95 | 0.3 | 1.8217 | 0.70693 | -1.7903 | -2.4837 | 5.7384 | 5.0485 | 5.2471 | 72.3982 | 114.5965 | 50.18 | 30.9833 | -5.8994 | 65.1856 | 23.9953
42810.4493 | 800 | 18.381 | 18.5114 | 18.4986 | 18.4799 | 17.7505 | 16.3352 | 14.4476 | 16.5598 | 17.0621 | 17.1583 | 17.1623 | 16.6696 | 15.6696 | 14.2899 | 14.7695 | 15.0684 | 16.17 | 13.8965 | 14.3019 | 37.32 |  |  |  | 16.8216 | 18.055 | 88.7981 | 630.5277 | 665.3768 | 634.3012 | 71.351 | 78.342 | 467.6788 | 80.8986 | 78.4731 | 709.0667 | 758.9384 | 579.2357 |  | 660.4008 | 798.733 | 769.8402 | 753.1282 |  | 234.5608 | 453.9981 | 308.3319 | 515.6391 | 709.7718 | 861.1105 | 885.8261 | 26.5405 | 175.2575 | 45.6309 | 360.5388 | 23.1489 | 47.3541 | 48.061 | 47.3898 | 28.0772 |  |  | 0.382 | -0.61235 | -0.83334 | -1.5791 | 5.9609 | 4.9411 | 6.4502 | -4.9726 | 13.0254 | 31.547 | 15.0059 | 0.0017414 | 0.0017331 | -0.00080825 | 16.5522 | 16.6083 | 17.1216 | 17.4372 | 17.3772 | 16.3117 | 14.6514 | 16.7187 | 17.0699 | 17.3561 | 17.3962 | 17.0907 | 16.2383 | 14.4124 | 716.9249 | 277.7741 | 449.6625 | 259.7244 | 218.9402 | 636.2541 | 329.8468 | 15.7711 | 15.8501 | 16.4865 | 15.693 | 31.5118 | 50.3077 |  |  |  | 526.5047 | 479.2902 | 500.6404 | 498.7709 | 51.442 | 21.4868 | 856.6954 |  |  | 309.2141 |  |  | 17.4077 | 19.8169 | 135.0017 | 16.4612 | 17.2449 | 764.0327 | 694.8559 | 558.6197 | 852.7315 | 858.2418 | 675.765 |  | 778.2175 | 824.5135 | 914.2971 | 540.6021 | 676.6504 | 840.6058 |  | 900.1115 |  |  | 324.2777 | 518.8839 | 662.5354 | [6 empty] | 546.824 |  |  | 310.3221 |  |  | 440.0972 | 608.1334 | 615.3721 | 752.101 | 1000.3468 | 952.14 | 509.5352 | 674.0118 | 760.9222 | 541.5337 | 635.2706 | 935.978 | 1004.6958 | 586.3948 | 770.8656 | 812.6603 | 977.0357 | 997.9292 | 462.4958 | 575.4685 | 621.5862 | 543.1292 | 663.873 | 824.3842 | 881.5432 | 1014.6486 | 525.7357 | 624.3228 | 607.9065 | 772.9912 | 72.6146 | 5.2179 | 16.7713 | 3.4363 | -38.2856 | 3.1244 | 10666.86 | 0.3 | 1.2975 | -1.4705 | -1.7155 | -2.3614 | 5.7303 | 5.2171 | 5.9609 | 72.1249 | 115.2242 | 49.9228 | 29.8168 | -5.8166 | 64.4969 | 23.9546
42810.4493 | 801 | 18.3965 | 18.5191 | 18.5034 | 18.4944 | 17.7552 | 16.3503 | 14.4538 | 16.573 | 17.0685 | 17.1752 | 17.1697 | 16.6715 | 15.6778 | 14.3009 | 14.7626 | 15.0618 | 16.175 | 13.9315 | 14.3286 | 37.8116 |  |  |  | 16.8239 | 18.0694 | 89.1075 | 629.9944 | 667.2733 | 633.3952 | 85.3067 | 82.4515 | 486.0449 | 62.1269 | 96.7905 | 740.0583 | 743.3576 | 552.6097 |  | 672.9982 | 788.0971 | 756.5459 | 745.4461 |  | 236.768 | 456.6169 | 309.6171 | 515.9097 | 715.4885 | 860.3062 | 886.633 | 26.7115 | 177.31 | 46.0657 | 363.9962 | 23.3402 | 47.2963 | 48.0352 | 47.4085 | 27.9296 |  |  | 0.77562 | -0.88636 | -0.83597 | -1.3839 | 6.5884 | 5.9083 | 5.4848 | -5.0363 | 13.0047 | 33.156 | 14.9628 | 0.0017151 | 0.0017167 | -0.00083454 | 16.5482 | 16.6079 | 17.1145 | 17.4282 | 17.3696 | 16.3148 | 14.6466 | 16.7198 | 17.0628 | 17.3609 | 17.3947 | 17.0873 | 16.2371 | 14.4122 | 685.3954 | 275.2024 | 424.9601 | 255.7256 | 216.1013 | 635.2166 | 330.0857 | 15.7668 | 15.8519 | 16.5071 | 15.7656 | 31.911 | 50.7511 |  |  |  | 525.9711 | 479.2055 | 500.693 | 495.5594 | 58.9708 | 26.2458 | 856.6242 |  |  | 310.443 |  |  | 17.3971 | 19.8568 | 134.807 | 16.4529 | 17.2431 | 753.976 | 696.2474 | 559.9521 | 845.5802 | 851.6878 | 676.7162 |  | 777.3321 | 819.2373 | 915.779 | 541.4269 | 675.5733 | 836.7081 |  | 900.501 |  |  | 323.0746 | 517.3384 | 663.4108 | [6 empty] | 547.7988 |  |  | 310.2427 |  |  | 438.7496 | 607.7316 | 614.465 | 746.4707 | 997.6267 | 951.9977 | 506.6406 | 672.9784 | 762.4386 | 540.9489 | 634.9486 | 929.6157 | 1008.047 | 584.517 | 771.1048 | 815.2353 | 975.511 | 994.0023 | 462.1474 | 575.6781 | 622.7632 | 537.9154 | 662.0315 | 821.6012 | 879.8133 | 1011.5067 | 525.4866 | 623.9511 | 604.4608 | 770.7974 | 73.7833 | 4.7514 | 16.9199 | 3.7395 | -38.2966 | 3.1245 | 10521.43 | 0.31 | 1.8479 | -1.7724 | -1.7213 | -2.2147 | 6.0223 | 5.703 | 5.4948 | 71.8408 | 115.9757 | 49.661 | 33.0282 | -3.0335 | 60.4796 | 23.9672
42810.4493 | 802 | 18.377 | 18.5173 | 18.505 | 18.4803 | 17.7451 | 16.34 | 14.4429 | 16.567 | 17.0572 | 17.1652 | 17.162 | 16.6717 | 15.6734 | 14.2894 | 14.7604 | 15.0643 | 16.177 | 13.9705 | 14.3654 | 38.3188 |  |  |  | 16.836 | 18.0868 | 89.3682 | 627.7014 | 666.9957 | 631.1117 | 76.8057 | 91.3231 | 512.1462 | 73.689 | 84.3121 | 737.7042 | 699.5359 | 511.8334 |  | 658.7253 | 801.0702 | 776.1249 | 716.9312 |  | 238.6698 | 459.1444 | 311.0736 | 516.6253 | 713.7686 | 858.2107 | 885.7742 | 27.1248 | 179.1898 | 46.846 | 366.8893 | 23.4945 | 47.2437 | 48.0082 | 47.419 | 27.8067 |  |  | 1.0917 | -0.97836 | -1.0725 | -1.4194 | 6.3282 | 5.8065 | 5.2273 | -5.0304 | 13.592 | 33.5913 | 14.8692 | 0.0016099 | 0.0017479 | -0.00082796 | 16.5547 | 16.6075 | 17.119 | 17.4271 | 17.3719 | 16.3091 | 14.649 | 16.7251 | 17.0587 | 17.362 | 17.3969 | 17.0857 | 16.2419 | 14.4147 | 690.8252 | 280.4374 | 423.0412 | 254.324 | 214.3425 | 634.3416 | 330.3488 | 15.7744 | 15.8571 | 16.5144 | 15.8458 | 32.3329 | 51.1988 |  |  |  | 525.3639 | 478.572 | 501.8456 | 492.7918 | 56.0657 | 20.1047 | 852.5196 |  |  | 306.5733 |  |  | 17.3976 | 19.9111 | 135.3738 | 16.4553 | 17.2625 | 760.9424 | 696.9983 | 561.7974 | 844.8941 | 852.327 | 679.0065 |  | 776.3651 | 816.629 | 917.1629 | 543.6763 | 674.6769 | 832.6429 |  | 901.6335 |  |  | 323.5061 | 517.9614 | 664.2344 | [6 empty] | 549.2858 |  |  | 311.1404 |  |  | 437.5992 | 607.8245 | 615.0066 | 739.2317 | 990.9621 | 954.2822 | 503.9955 | 671.9535 | 764.7892 | 540.6899 | 635.8505 | 925.8448 | 1007.5495 | 582.6797 | 769.7509 | 810.6148 | 973.2685 | 992.7153 | 462.226 | 575.6459 | 622.0115 | 533.7284 | 660.6702 | 817.2765 | 877.0927 | 1008.5328 | 525.8463 | 623.0681 | 601.6676 | 768.2556 | 71.4188 | 4.3089 | 17.0542 | 4.039 | -38.2124 | 3.1244 | 10403.28 | 0.28 | 2.1896 | -1.8653 | -1.9531 | -2.2468 | 5.8967 | 5.6484 | 5.3593 | 71.4964 | 116.615 | 49.4003 | 32.1791 | -2.7779 | 50.2712 | 23.957
42810.4493 | 803 | 18.3694 | 18.4953 | 18.4924 | 18.4744 | 17.74 | 16.3316 | 14.4465 | 16.5531 | 17.0584 | 17.1613 | 17.1571 | 16.6666 | 15.6624 | 14.2797 | 14.7586 | 15.056 | 16.1735 | 14.0018 | 14.3997 | 38.8207 |  |  |  | 16.8431 | 18.109 | 94.5841 | 626.5971 | 667.5526 | 631.7389 | 76.4133 | 83.0467 | 534.6527 | 80.6784 | 86.4208 | 732.7503 | 760.2553 | 530.1381 |  | 640.0975 | 780.8818 | 770.6913 | 715.7046 |  | 240.852 | 462.0977 | 311.9748 | 521.6337 | 720.6642 | 852.5608 | 886.5433 | 28.0795 | 181.3364 | 46.7217 | 370.1804 | 23.6973 | 47.2742 | 47.9868 | 47.4357 | 27.7286 |  |  | 0.90572 | -0.58737 | -0.88986 | -1.5508 | 5.8216 | 5.1434 | 5.8305 | -4.7465 | 12.8105 | 34.1318 | 16.4576 | 0.0016757 | 0.0016642 | -0.00084439 | 16.5641 | 16.6073 | 17.113 | 17.4334 | 17.3681 | 16.311 | 14.6469 | 16.7236 | 17.0663 | 17.3579 | 17.3891 | 17.0897 | 16.2434 | 14.4095 | 693.6789 | 268.7536 | 411.7287 | 250.2727 | 212.9647 | 633.8746 | 330.7141 | 15.7638 | 15.8555 | 16.5236 | 15.9088 | 32.7152 | 51.5871 |  |  |  | 524.6979 | 478.2785 | 502.4895 | 491.4861 | 68.6446 | 31.7725 | 853.2231 |  |  | 301.846 |  |  | 17.4018 | 19.9674 | 133.644 | 16.4607 | 17.2798 | 769.4332 | 695.5074 | 561.3825 | 839.5074 | 846.7876 | 677.5317 |  | 775.3967 | 814.3697 | 917.8346 | 543.7329 | 673.6871 | 831.6675 |  | 901.795 |  |  | 323.4679 | 516.4833 | 663.2575 | [6 empty] | 549.0298 |  |  | 311.8118 |  |  | 436.8436 | 608.2486 | 615.7544 | 733.5968 | 988.5856 | 954.6596 | 501.5934 | 669.7115 | 765.7695 | 540.581 | 637.0982 | 923.9953 | 1006.7749 | 580.5407 | 766.9461 | 807.0663 | 971.8971 | 990.1254 | 462.6255 | 575.6927 | 620.8477 | 530.1079 | 659.7905 | 818.2462 | 873.854 | 1004.0655 | 526.5384 | 622.6047 | 599.7435 | 769.4955 | 69.6116 | 3.9088 | 17.1545 | 4.3051 | -38.2713 | 3.1245 | 10330.37 | 0.26 | 1.9951 | -1.4482 | -1.7826 | -2.3532 | 5.6416 | 5.3028 | 5.6459 | 71.2569 | 116.9535 | 49.1804 | 31.731 | -1.4622 | 65.902 | 23.898
42810.4493 | 804 | 18.3662 | 18.4992 | 18.4885 | 18.4732 | 17.741 | 16.331 | 14.4467 | 16.5558 | 17.051 | 17.1544 | 17.1519 | 16.6636 | 15.6641 | 14.2788 | 14.7546 | 15.0589 | 16.1835 | 14.0348 | 14.4603 | 39.3207 |  |  |  | 16.8432 | 18.1285 | 96.9737 | 629.5433 | 672.5305 | 634.936 | 59.4812 | 56.4172 | 561.2466 | 62.1502 | 70.3915 | 725.6781 | 757.4692 | 581.8963 |  | 636.2475 | 775.6522 | 749.234 | 742.431 |  | 242.7651 | 464.8999 | 312.7217 | 523.1583 | 723.9232 | 856.2569 | 885.1227 | 28.4644 | 183.0421 | 47.5042 | 372.8315 | 23.8904 | 47.3248 | 47.9757 | 47.4572 | 27.629 |  |  | 0.9399 | -0.23713 | -1.0515 | -1.8432 | 5.6724 | 4.8379 | 5.6997 | -4.7058 | 13.1098 | 34.0993 | 16.6986 | 0.0016625 | 0.001697 | -0.00084111 | 16.5713 | 16.6087 | 17.1152 | 17.4338 | 17.3758 | 16.3204 | 14.64 | 16.7244 | 17.0697 | 17.3597 | 17.3963 | 17.0947 | 16.2386 | 14.411 | 724.2875 | 274.9129 | 460.3162 | 270.658 | 220.806 | 634.3847 | 331.8748 | 15.7576 | 15.8497 | 16.5259 | 15.9744 | 33.0873 | 51.9568 |  |  |  | 524.0653 | 477.7909 | 501.2023 | 491.1234 | 62.9185 | 30.2012 | 849.5319 |  |  | 296.9296 |  |  | 17.4202 | 20.037 | 141.6314 | 16.4593 | 17.2901 | 782.2446 | 694.16 | 559.3517 | 838.9157 | 848.224 | 673.6725 |  | 774.2066 | 814.182 | 918.4858 | 541.9848 | 672.4348 | 831.0452 |  | 901.904 |  |  | 323.3279 | 515.0257 | 661.131 | [6 empty] | 547.1 |  |  | 313.1988 |  |  | 436.3236 | 608.2846 | 616.0612 | 731.0976 | 989.1381 | 953.1704 | 499.3077 | 667.3857 | 765.9845 | 540.1051 | 636.9353 | 923.145 | 1008.2366 | 578.9551 | 763.1024 | 802.6049 | 966.2633 | 986.6273 | 462.7038 | 575.4364 | 621.5643 | 526.3014 | 659.23 | 822.7563 | 871.1057 | 1002.9922 | 526.1246 | 622.7852 | 597.7076 | 772.2865 | 66.1512 | 3.5219 | 17.2426 | 4.5209 | -38.2535 | 3.1244 | 10258.1 | 0.22 | 2.036 | -0.92194 | -1.9414 | -2.5704 | 5.578 | 5.1513 | 5.5914 | 71.0204 | 117.2266 | 48.9535 | 28.4732 | -6.6737 | 64.3877 | 23.8177
42810.4494 | 805 | 18.3652 | 18.5004 | 18.488 | 18.4693 | 17.7374 | 16.3312 | 14.442 | 16.5542 | 17.0522 | 17.1496 | 17.1524 | 16.6582 | 15.6633 | 14.2755 | 14.7534 | 15.0606 | 16.1915 | 14.0778 | 14.4996 | 39.8168 |  |  |  | 16.8523 | 18.1508 | 98.6797 | 633.4661 | 676.0779 | 639.1763 | 55.5776 | 30.7101 | 582.9192 | 37.2424 | 46.4173 | 708.444 | 747.7397 | 590.3115 |  | 647.6683 | 801.7277 | 768.2188 | 721.0531 |  | 245.3291 | 467.9551 | 314.1636 | 522.9881 | 722.5807 | 854.5829 | 885.6591 | 28.5502 | 184.9585 | 48.3559 | 375.7009 | 24.047 | 47.3541 | 47.973 | 47.4727 | 27.5439 |  |  | 0.48977 | -0.17733 | -1.175 | -1.6914 | 6.4596 | 5.2874 | 6.1479 | -4.3542 | 13.4535 | 34.2908 | 16.0074 | 0.0016297 | 0.001582 | -0.00084768 | 16.5729 | 16.6118 | 17.1293 | 17.4428 | 17.3815 | 16.3201 | 14.6464 | 16.7246 | 17.0653 | 17.3703 | 17.4011 | 17.0954 | 16.2419 | 14.4148 | 729.9675 | 282.1386 | 460.8527 | 288.5689 | 214.6516 | 634.9369 | 333.0417 | 15.7598 | 15.8621 | 16.5379 | 16.0501 | 33.4604 | 52.3324 |  |  |  | 523.767 | 478.7466 | 499.5085 | 495.0696 | 73.5513 | 36.3493 | 850.3274 |  |  | 292.4592 |  |  | 17.4026 | 20.085 | 152.8369 | 16.4543 | 17.3052 | 782.7702 | 693.3758 | 556.9783 | 835.2643 | 843.9258 | 671.2418 |  | 772.8716 | 813.9183 | 919.4287 | 540.1067 | 670.8728 | 833.9104 |  | 902.4803 |  |  | 323.0606 | 514.6745 | 660.545 | [6 empty] | 544.6862 |  |  | 314.2949 |  |  | 435.9008 | 607.674 | 615.5847 | 733.906 | 992.0538 | 951.8273 | 497.2358 | 666.4633 | 766.6341 | 540.4172 | 634.9603 | 929.0462 | 1010.9994 | 577.8782 | 764.3789 | 800.2844 | 963.9818 | 986.1337 | 462.2221 | 575.5564 | 624.0079 | 522.6306 | 658.4556 | 826.6726 | 873.0746 | 1005.7523 | 526.044 | 622.9674 | 595.4675 | 774.0841 | 71.1537 | 3.1545 | 17.329 | 4.6986 | -38.2429 | 3.1244 | 10194.6 | 0.29 | 1.4731 | -0.79892 | -2.0565 | -2.4674 | 5.948 | 5.3813 | 5.8027 | 70.7036 | 117.6223 | 48.6635 | 27.9971 | -6.5449 | 62.3296 | 23.6655
42810.4494 | 806 | 18.3634 | 18.5033 | 18.5001 | 18.473 | 17.7405 | 16.3313 | 14.439 | 16.5586 | 17.054 | 17.1552 | 17.1578 | 16.663 | 15.663 | 14.2768 | 14.7367 | 15.0686 | 16.1994 | 14.1311 | 14.5468 | 40.33 |  |  |  | 16.8651 | 18.1655 | 97.5137 | 635.1975 | 678.1476 | 641.7912 | 78.7157 | 54.9772 | 598.7685 | 35.7724 | 42.7927 | 712.23 | 735.0881 | 586.2332 |  | 657.5882 | 801.0937 | 770.4135 | 709.4963 |  | 247.2009 | 470.3594 | 315.5177 | 524.219 | 724.4267 | 855.5659 | 888.9323 | 28.5154 | 186.8484 | 48.613 | 378.586 | 24.2023 | 47.3652 | 47.9714 | 47.4981 | 27.4824 |  |  | 1.0864 | 0.013231 | -1.3308 | -1.3701 | 6.8059 | 5.1402 | 4.1962 | -6.4268 | 14.7349 | 37.8643 | 15.9132 | 0.0016132 | 0.001628 | -0.00083782 | 16.5658 | 16.6093 | 17.1189 | 17.4326 | 17.3842 | 16.3132 | 14.6509 | 16.7207 | 17.0621 | 17.3566 | 17.3912 | 17.0886 | 16.2366 | 14.4098 | 733.336 | 294.006 | 477.622 | 286.0282 | 222.4832 | 636.0095 | 334.6199 | 15.7677 | 15.8625 | 16.548 | 16.1418 | 33.881 | 52.7569 |  |  |  | 523.7662 | 480.3802 | 498.3403 | 501.5247 | 64.7403 | 32.9631 | 847.4564 |  |  | 288.8863 |  |  | 17.4057 | 20.1493 | 146.3825 | 16.4679 | 17.3282 | 781.448 | 691.5154 | 555.9126 | 829.8037 | 841.2866 | 667.717 |  | 771.508 | 811.6265 | 920.3475 | 539.468 | 669.5647 | 833.1592 |  | 903.7048 |  |  | 323.1209 | 514.9124 | 657.6043 | [6 empty] | 543.4349 |  |  | 314.3883 |  |  | 435.4044 | 606.8749 | 614.924 | 734.9649 | 996.1857 | 951.6808 | 495.6115 | 665.9121 | 768.0443 | 540.7093 | 632.7216 | 932.2274 | 1013.08 | 576.8108 | 767.2853 | 799.4981 | 966.083 | 984.6933 | 461.4543 | 575.5228 | 625.9667 | 519.2462 | 657.626 | 829.2865 | 874.4026 | 1006.7933 | 525.7191 | 623.6227 | 593.0624 | 771.999 | 70.0727 | 2.8024 | 17.3646 | 4.8337 | -38.3037 | 3.1244 | 10175.5 | 0.28 | 2.1972 | 0.21858 | -2.1921 | -2.2243 | 6.108 | 5.3082 | 4.7961 | 70.4104 | 118.0654 | 48.3959 | 27.9245 | -8.1527 | 59.3025 | 23.4861
42810.4494 | 807 | 18.3536 | 18.4973 | 18.4815 | 18.4652 | 17.7415 | 16.3224 | 14.4417 | 16.5475 | 17.0515 | 17.1473 | 17.1513 | 16.656 | 15.6601 | 14.2738 | 14.7506 | 15.0673 | 16.2001 | 14.1749 | 14.584 | 40.8518 |  |  |  | 16.8759 | 18.1907 | 101.5208 | 634.7318 | 678.0341 | 641.0813 | 56.038 | 76.1808 | 609.7035 | 61.6171 | 50.308 | 709.401 | 718.6453 | 610.9091 |  | 652.2047 | 808.6658 | 778.349 | 721.1445 |  | 248.1011 | 472.608 | 316.9525 | 525.2726 | 729.7896 | 861.1052 | 892.7109 | 29.1551 | 188.5547 | 49.4786 | 381.3963 | 24.3908 | 47.382 | 47.9605 | 47.5218 | 27.4306 |  |  | 0.97406 | -0.017653 | -0.70455 | -0.9607 | 6.3893 | 4.8648 | 5.2148 | -5.0744 | 12.9586 | 34.0441 | 15.9243 | 0.0015984 | 0.0015935 | -0.00083289 | 16.5681 | 16.6077 | 17.1158 | 17.4232 | 17.3724 | 16.3109 | 14.6464 | 16.7158 | 17.0631 | 17.3513 | 17.3913 | 17.0917 | 16.2369 | 14.4091 | 720.9184 | 289.7226 | 480.5807 | 296.4057 | 237.9884 | 636.2165 | 336.1756 | 15.7501 | 15.8565 | 16.5485 | 16.2152 | 34.2696 | 53.1338 |  |  |  | 523.9441 | 482.2337 | 497.3567 | 507.829 | 52.235 | 25.5036 | 845.3335 |  |  | 286.2096 |  |  | 17.3986 | 20.2015 | 149.7741 | 16.4511 | 17.3305 | 779.2981 | 694.3077 | 556.7035 | 833.5578 | 845.1104 | 673.3947 |  | 770.7406 | 816.4145 | 922.4685 | 540.0187 | 668.4014 | 837.9055 |  | 904.9325 |  |  | 324.7697 | 520.569 | 659.7492 | [6 empty] | 544.0983 |  |  | 314.6187 |  |  | 435.0548 | 605.5593 | 614.065 | 732.5547 | 996.818 | 952.9166 | 493.8426 | 666.9782 | 769.3135 | 540.2843 | 630.8448 | 932.839 | 1015.0159 | 575.6217 | 768.822 | 795.5541 | 967.5124 | 985.7762 | 461.859 | 575.3851 | 627.9354 | 516.723 | 656.4733 | 830.0409 | 878.5022 | 1010.1703 | 526.3907 | 623.9549 | 591.1352 | 771.9989 | 70.7358 | 2.4777 | 17.4193 | 4.9388 | -38.4483 | 3.1244 | 10139.52 | 0.31 | 2.0796 | -0.25286 | -1.5974 | -1.8653 | 5.9327 | 5.1767 | 5.3597 | 70.0332 | 118.8113 | 48.1276 | 29.3625 | -8.2291 | 54.7925 | 23.3364
42810.4494 | 808 | 18.3514 | 18.4979 | 18.4828 | 18.466 | 17.7349 | 16.3229 | 14.45 | 16.5488 | 17.0531 | 17.15 | 17.1546 | 16.6622 | 15.6534 | 14.2698 | 14.7418 | 15.0601 | 16.1968 | 14.2173 | 14.6316 | 41.3562 |  |  |  | 16.8742 | 18.2119 | 100.5712 | 631.753 | 677.2267 | 637.0606 | 71.2388 | 77.3842 | 622.8417 | 85.4431 | 83.0115 | 752.8235 | 752.0235 | 592.8621 |  | 659.1903 | 799.9858 | 754.2761 | 737.8303 |  | 249.7439 | 475.604 | 319.2553 | 526.4259 | 729.0898 | 863.769 | 893.2262 | 30.2074 | 190.5704 | 50.3144 | 384.5223 | 24.6047 | 47.4311 | 47.9585 | 47.54 | 27.4115 |  |  | 0.7605 | -0.22596 | -1.3531 | -1.4108 | 6.7113 | 5.7513 | 5.9744 | -4.4377 | 13.6055 | 33.9236 | 15.9243 | 0.0015064 | 0.0016231 | -0.00082961 | 16.5731 | 16.6044 | 17.1159 | 17.4293 | 17.3711 | 16.3071 | 14.6472 | 16.724 | 17.0641 | 17.354 | 17.391 | 17.0831 | 16.237 | 14.4061 | 690.8777 | 281.4097 | 470.2965 | 294.071 | 229.1699 | 635.5338 | 337.1671 | 15.7516 | 15.8645 | 16.559 | 16.2972 | 34.6495 | 53.4874 |  |  |  | 524.2197 | 484.1853 | 497.3622 | 511.7424 | 69.1926 | 41.8536 | 851.9137 |  |  | 286.5148 |  |  | 17.4031 | 20.2747 | 153.2886 | 16.4499 | 17.3601 | 765.6881 | 694.5855 | 558.1447 | 829.1047 | 838.8774 | 676.4586 |  | 769.8272 | 819.3598 | 924.5108 | 540.6091 | 667.1878 | 844.1119 |  | 906.3577 |  |  | 325.4264 | 526.8797 | 662.1255 | [6 empty] | 545.1992 |  |  | 314.5542 |  |  | 435.3315 | 604.3796 | 612.9142 | 732.6145 | 997.7908 | 955.7818 | 492.3681 | 666.7779 | 768.365 | 539.8827 | 629.7677 | 933.2826 | 1014.1731 | 574.788 | 769.4445 | 792.3492 | 967.7947 | 983.0638 | 462.5031 | 574.8195 | 627.9421 | 514.0208 | 655.214 | 829.3238 | 879.8361 | 1006.1267 | 526.5894 | 623.1606 | 589.2802 | 769.9594 | 66.8233 | 2.2306 | 17.4785 | 5.0272 | -38.3475 | 3.1244 | 10116.91 | 0.27 | 1.8335 | -0.90647 | -2.2182 | -2.265 | 6.0874 | 5.6353 | 5.7435 | 69.6873 | 119.5799 | 47.8482 | 32.5082 | -6.9252 | 63.0228 | 23.267
42810.4494 | 809 | 18.3561 | 18.4919 | 18.4845 | 18.4704 | 17.7424 | 16.3253 | 14.4517 | 16.5587 | 17.0584 | 17.1656 | 17.1656 | 16.6612 | 15.6649 | 14.2807 | 14.7376 | 15.0651 | 16.1974 | 14.2663 | 14.6916 | 41.8529 |  |  |  | 16.8888 | 18.2331 | 104.5568 | 629.2371 | 678.2096 | 635.2015 | 81.2836 | 76.9365 | 630.3974 | 67.9552 | 83.4923 | 759.8203 | 765.884 | 552.155 |  | 672.9358 | 794.1068 | 766.8173 | 704.7378 |  | 251.1897 | 477.9484 | 320.5949 | 526.7947 | 725.9147 | 862.6056 | 892.398 | 31.1668 | 192.1732 | 51.8544 | 387.0892 | 24.7982 | 47.4903 | 47.9357 | 47.5424 | 27.3931 |  |  | 0.60411 | 0.020459 | -1.7954 | -1.4299 | 5.7552 | 6.1298 | 5.8535 | -4.7465 | 14.1939 | 34.9777 | 16.3052 | 0.0015492 | 0.0014719 | -0.00081646 | 16.5739 | 16.5988 | 17.1132 | 17.4259 | 17.3707 | 16.3106 | 14.6444 | 16.7267 | 17.059 | 17.3561 | 17.3928 | 17.0811 | 16.2366 | 14.4058 | 700.7522 | 282.0336 | 502.2496 | 313.2526 | 238.4039 | 635.9142 | 338.8506 | 15.7486 | 15.8686 | 16.5688 | 16.3764 | 35.0217 | 53.8409 |  |  |  | 524.2314 | 483.8207 | 496.6454 | 510.3052 | 64.5265 | 29.9799 | 848.4541 |  |  | 287.181 |  |  | 17.4073 | 20.3489 | 155.4822 | 16.4649 | 17.379 | 745.9809 | 692.721 | 556.7435 | 823.7918 | 833 | 675.0501 |  | 768.5452 | 820.2126 | 925.5528 | 538.3468 | 665.6324 | 842.5165 |  | 907.7223 |  |  | 324.8542 | 528.3922 | 662.0622 | [6 empty] | 544.0132 |  |  | 314.0393 |  |  | 435.0851 | 603.6948 | 612.0731 | 734.7419 | 998.9227 | 957.3303 | 490.7938 | 666.7663 | 768.9115 | 539.6395 | 629.4246 | 936.4107 | 1013.0127 | 573.6125 | 768.6942 | 788.4863 | 968.2869 | 978.0239 | 462.2795 | 574.2597 | 626.6435 | 511.3687 | 654.1631 | 829.9747 | 879.0274 | 1002.7526 | 526.7526 | 622.6062 | 587.5339 | 768.4952 | 70.7449 | 1.9639 | 17.5054 | 5.1137 | -38.4753 | 3.1244 | 10134.86 | 0.27 | 1.6325 | 0.27319 | -2.5591 | -2.2838 | 5.6343 | 5.8148 | 5.6822 | 69.3616 | 119.9917 | 47.5753 | 31.5181 | -10.2014 | 67.7834 | 23.3086
42810.4494 | 810 | 18.3433 | 18.4905 | 18.483 | 18.4649 | 17.7434 | 16.3292 | 14.4485 | 16.5502 | 17.0529 | 17.1575 | 17.1485 | 16.6632 | 15.661 | 14.2824 | 14.7268 | 15.0663 | 16.2033 | 14.3116 | 14.7516 | 42.3432 |  |  |  | 16.892 | 18.2447 | 103.0089 | 628.6474 | 677.9194 | 635.6025 | 77.9179 | 86.7563 | 639.17 | 78.1097 | 80.0382 | 753.8211 | 760.4044 | 528.553 |  | 645.737 | 788.2904 | 774.7525 | 693.7407 |  | 252.0513 | 480.1251 | 321.3841 | 527.3268 | 729.9414 | 863.4224 | 891.0115 | 32.2106 | 193.9069 | 53.1183 | 389.9559 | 24.9639 | 47.576 | 47.9161 | 47.5363 | 27.3992 |  |  | 0.7145 | -0.42441 | -0.82743 | -1.857 | 6.3952 | 5.6245 | 5.3068 | -3.4454 | 14.0663 | 36.6729 | 16.7974 | 0.001559 | 0.0015672 | -0.00082139 | 16.5848 | 16.6055 | 17.1168 | 17.4293 | 17.3666 | 16.3168 | 14.6436 | 16.7227 | 17.0587 | 17.356 | 17.3941 | 17.0883 | 16.2403 | 14.4078 | 705.8183 | 269.6545 | 492.3371 | 312.087 | 243.5531 | 635.9432 | 339.9748 | 15.736 | 15.8625 | 16.571 | 16.4568 | 35.3938 | 54.1806 |  |  |  | 524.001 | 482.0283 | 496.3759 | 506.4706 | 66.3696 | 33.3363 | 844.7573 |  |  | 289.779 |  |  | 17.3946 | 20.4024 | 154.7408 | 16.4574 | 17.3896 | 756.4448 | 691.4767 | 554.9046 | 825.3819 | 836.2311 | 675.222 |  | 767.3834 | 817.9158 | 926.7421 | 536.2568 | 664.0945 | 839.1375 |  | 908.8497 |  |  | 323.5477 | 528.4153 | 661.2735 | [6 empty] | 541.9614 |  |  | 313.0402 |  |  | 434.8872 | 602.8157 | 611.6261 | 732.9344 | 1000.6264 | 958.9648 | 488.9747 | 665.2845 | 770.2451 | 539.5104 | 628.8542 | 932.538 | 1015.5534 | 572.79 | 766.397 | 789.362 | 970.9849 | 976.7927 | 461.8561 | 574.5522 | 625.8957 | 509.453 | 653.1796 | 828.6515 | 877.981 | 1001.8726 | 527.1546 | 622.7424 | 585.9007 | 770.9051 | 74.5722 | 1.7791 | 17.5395 | 5.1884 | -38.3785 | 3.1244 | 10169.61 | 0.33 | 1.7758 | -1.2461 | -1.7398 | -2.6065 | 5.9415 | 5.5719 | 5.4123 | 69.0272 | 120.5538 | 47.3027 | 30.9633 | -8.9164 | 66.5536 | 23.3822
42810.4494 | 811 | 18.3356 | 18.4916 | 18.4771 | 18.4621 | 17.7364 | 16.3214 | 14.4469 | 16.5565 | 17.0505 | 17.1552 | 17.1543 | 16.6601 | 15.6602 | 14.2835 | 14.72 | 15.0594 | 16.2057 | 14.3585 | 14.8234 | 42.8381 |  |  |  | 16.8887 | 18.2651 | 105.3125 | 628.2399 | 678.0874 | 635.2345 | 49.4635 | 53.7593 | 663.1199 | 51.6673 | 56.1353 | 733.5025 | 751.4564 | 565.4292 |  | 666.0456 | 787.6475 | 769.9278 | 690.9739 |  | 253.2949 | 482.4416 | 321.8518 | 528.8433 | 732.8917 | 866.2076 | 894.0633 | 34.3272 | 195.7512 | 53.8312 | 392.7301 | 25.1601 | 47.6208 | 47.8868 | 47.5208 | 27.3727 |  |  | 1.0424 | 0.008631 | -1.6758 | -1.4995 | 7.0799 | 6.9275 | 6.1216 | -4.4114 | 14.5061 | 36.0661 | 16.9715 | 0.0015344 | 0.0015459 | -0.00085918 | 16.5788 | 16.5982 | 17.0988 | 17.4271 | 17.3644 | 16.3084 | 14.6427 | 16.7133 | 17.0541 | 17.3528 | 17.3917 | 17.0887 | 16.2345 | 14.4051 | 704.177 | 292.5716 | 498.3398 | 302.9527 | 252.9443 | 636.4665 | 341.6219 | 15.731 | 15.8595 | 16.5811 | 16.5525 | 35.8116 | 54.5687 |  |  |  | 523.7285 | 480.1124 | 494.6794 | 505.3658 | 66.1607 | 35.4812 | 848.2569 |  |  | 292.3176 |  |  | 17.3895 | 20.4765 | 157.7195 | 16.4563 | 17.4055 | 779.2488 | 694.9785 | 553.2899 | 825.008 | 836.0356 | 679.9814 |  | 766.6624 | 817.472 | 928.1218 | 534.9496 | 662.7079 | 837.9484 |  | 909.9016 |  |  | 324.0769 | 532.3947 | 664.0306 | [6 empty] | 540.5343 |  |  | 312.9963 |  |  | 434.612 | 601.8369 | 612.5876 | 728.1822 | 997.4964 | 960.7914 | 487.9729 | 664.0687 | 770.8176 | 539.1235 | 629.3752 | 927.2552 | 1014.784 | 572.554 | 763.7833 | 796.3906 | 973.7624 | 976.2711 | 461.8657 | 575.3915 | 625.7388 | 508.0012 | 652.4785 | 826.5668 | 879.7879 | 1000.3152 | 527.4315 | 622.5493 | 584.3467 | 772.9868 | 79.6193 | 1.5759 | 17.5708 | 5.2587 | -38.5469 | 3.1244 | 10244.18 | 0.27 | 2.1445 | 0.17797 | -2.4798 | -2.3458 | 6.2591 | 6.1914 | 5.8201 | 68.6909 | 121.146 | 47.0422 | 31.2931 | -9.314 | 64.1702 | 23.374
42810.4494 | 812 | 18.3356 | 18.4886 | 18.4791 | 18.4618 | 17.7392 | 16.3271 | 14.4468 | 16.5557 | 17.0544 | 17.1553 | 17.1603 | 16.6599 | 15.6598 | 14.2798 | 14.7207 | 15.062 | 16.2074 | 14.415 | 14.902 | 43.3334 |  |  |  | 16.8942 | 18.2885 | 105.1671 | 629.6364 | 677.8819 | 637.4031 | 46.653 | 35.57 | 672.9762 | 43.3675 | 50.4814 | 722.5773 | 750.9669 | 566.5945 |  | 638.797 | 785.6369 | 764.5201 | 701.8715 |  | 254.454 | 484.5623 | 322.7834 | 529.1255 | 735.8906 | 868.8978 | 898.047 | 34.8179 | 197.4773 | 55.4213 | 395.2354 | 25.3828 | 47.6346 | 47.843 | 47.513 | 27.407 |  |  | 1.0759 | -0.15696 | -1.4714 | -1.6862 | 6.595 | 6.1705 | 6.1012 | -3.4185 | 14.4843 | 35.8215 | 17.2608 | 0.0014703 | 0.0015409 | -0.00088875 | 16.5879 | 16.6058 | 17.1179 | 17.4323 | 17.3745 | 16.3152 | 14.6435 | 16.7243 | 17.0595 | 17.3596 | 17.3909 | 17.0826 | 16.2338 | 14.4068 | 715.5664 | 298.4102 | 524.6232 | 317.8451 | 258.0952 | 637.2468 | 343.7138 | 15.7379 | 15.8742 | 16.5944 | 16.6504 | 36.1827 | 54.9209 |  |  |  | 523.8472 | 480.708 | 494.2678 | 508.8194 | 83.1457 | 54.8349 | 847.1528 |  |  | 300.4327 |  |  | 17.4061 | 20.5627 | 159.2993 | 16.4725 | 17.4395 | 757.2519 | 697.787 | 552.2625 | 821.3747 | 831.7662 | 685.2606 |  | 766.5831 | 815.518 | 928.4361 | 533.3588 | 661.3295 | 835.9319 |  | 910.8859 |  |  | 325.1785 | 538.6076 | 668.8501 | [6 empty] | 539.3871 |  |  | 313.252 |  |  | 434.3148 | 600.888 | 612.7019 | 724.8325 | 994.9997 | 964.561 | 487.3714 | 661.9632 | 770.0908 | 538.6151 | 628.6985 | 921.3295 | 1012.6783 | 571.767 | 758.6559 | 799.3496 | 975.0987 | 976.4912 | 462.1096 | 575.7683 | 625.888 | 506.4167 | 651.7936 | 824.6701 | 882.5257 | 1000.4578 | 527.5203 | 622.1257 | 582.937 | 773.3257 | 70.0149 | 1.4043 | 17.6022 | 5.3136 | -38.404 | 3.1244 | 10341.73 | 0.25 | 2.1813 | -0.76 | -2.3269 | -2.491 | 6.0481 | 5.8502 | 5.8172 | 68.5219 | 121.3326 | 46.7924 | 30.2477 | -11.8911 | 63.7345 | 23.295
42810.4494 | 813 | 18.3305 | 18.4854 | 18.4708 | 18.4599 | 17.732 | 16.3213 | 14.4452 | 16.5512 | 17.0478 | 17.1478 | 17.1536 | 16.653 | 15.6588 | 14.2703 | 14.7162 | 15.0673 | 16.2171 | 14.4725 | 14.9832 | 43.8279 |  |  |  | 16.9022 | 18.3172 | 107.6712 | 630.2623 | 678.8018 | 638.146 | 66.7612 | 31.2314 | 678.8913 | 38.1464 | 51.3436 | 718.751 | 730.9555 | 566.8715 |  | 638.228 | 782.4168 | 760.245 | 691.8639 |  | 255.8359 | 486.8008 | 323.3504 | 531.8264 | 745.1988 | 874.8086 | 902.0392 | 33.5576 | 199.5152 | 56.9334 | 398.4801 | 25.6416 | 47.6474 | 47.8123 | 47.51 | 27.5182 |  |  | 1.005 | 0.19788 | -1.8552 | -1.8196 | 6.6627 | 6.2224 | 6.3003 | -3.9323 | 13.8925 | 35.5112 | 17.321 | 0.0014867 | 0.0014982 | -0.00082304 | 16.5875 | 16.5995 | 17.1157 | 17.4363 | 17.37 | 16.3144 | 14.6407 | 16.7195 | 17.0568 | 17.3539 | 17.3956 | 17.0867 | 16.2324 | 14.4044 | 747.1562 | 306.9601 | 589.4298 | 351.9113 | 270.9015 | 639.4612 | 347.0681 | 15.7385 | 15.8826 | 16.6101 | 16.7459 | 36.5384 | 55.2535 |  |  |  | 524.152 | 482.3324 | 495.2473 | 513.8503 | 83.0561 | 50.8056 | 843.733 |  |  | 306.4912 |  |  | 17.4056 | 20.6308 | 159.9616 | 16.4543 | 17.452 | 778.9086 | 698.4265 | 551.411 | 817.6818 | 829.6421 | 687.9486 |  | 766.4352 | 811.5183 | 927.9965 | 532.3367 | 660.1807 | 833.1887 |  | 911.0258 |  |  | 325.3848 | 544.2473 | 671.8458 | [6 empty] | 538.295 |  |  | 312.5578 |  |  | 434.1668 | 600.1114 | 611.5175 | 722.3896 | 990.0263 | 966.551 | 486.4493 | 659.2533 | 766.3158 | 538.0919 | 626.798 | 914.7125 | 1009.6486 | 570.9818 | 753.3611 | 802.6255 | 977.7935 | 976.8525 | 462.2195 | 575.225 | 626.5916 | 504.7496 | 651.1156 | 823.8614 | 884.7311 | 1001.8592 | 527.5174 | 621.8296 | 581.9034 | 772.6605 | 67.8166 | 1.3281 | 17.6338 | 5.3415 | -38.4988 | 3.1244 | 10450.77 | 0.29 | 2.109 | 0.85459 | -2.6167 | -2.5914 | 6.0947 | 5.8899 | 5.9267 | 68.4054 | 121.2586 | 46.5767 | 27.3641 | -18.5391 | 58.7228 | 23.1988
42810.4495 | 814 | 18.3162 | 18.4806 | 18.4643 | 18.4572 | 17.7235 | 16.3145 | 14.4428 | 16.5449 | 17.0423 | 17.1415 | 17.1463 | 16.6478 | 15.6597 | 14.2662 | 14.7161 | 15.0636 | 16.2246 | 14.5279 | 15.069 | 44.3143 |  |  |  | 16.9109 | 18.3438 | 111.8213 | 633.2109 | 681.3742 | 643.3487 | 47.6004 | 38.3368 | 682.358 | 21.8388 | 24.9475 | 708.2856 | 710.3066 | 608.3707 |  | 632.3274 | 795.695 | 770.9303 | 689.4558 |  | 257.2875 | 488.6557 | 325.017 | 534.7279 | 746.3997 | 875.3472 | 904.1838 | 31.4852 | 201.0674 | 56.6714 | 400.9575 | 25.9027 | 47.6794 | 47.7765 | 47.52 | 27.6639 |  |  | 1.3499 | -0.2805 | -1.3452 | -1.905 | 6.6817 | 6.6739 | 5.6656 | -4.6013 | 12.2989 | 34.5084 | 17.56 | 0.0014029 | 0.0015442 | -0.00084111 | 16.5864 | 16.5989 | 17.1085 | 17.4284 | 17.3631 | 16.3102 | 14.6358 | 16.7083 | 17.0529 | 17.3499 | 17.3916 | 17.0824 | 16.2285 | 14.4068 | 775.6181 | 315.3764 | 608.5879 | 362.6276 | 289.0501 | 642.0635 | 350.4664 | 15.7379 | 15.8809 | 16.6164 | 16.8352 | 36.9024 | 55.5796 |  |  |  | 524.7 | 485.4598 | 497.0454 | 520.6375 | 76.576 | 29.2768 | 840.1977 |  |  | 307.5277 |  |  | 17.4137 | 20.715 | 162.0513 | 16.4658 | 17.4725 | 776.4291 | 696.8057 | 549.5918 | 812.6635 | 824.2062 | 687.353 |  | 765.7757 | 806.9346 | 927.0369 | 530.7314 | 658.8218 | 829.2963 |  | 910.8054 |  |  | 325.7324 | 546.484 | 672.1503 | [6 empty] | 536.4208 |  |  | 311.6592 |  |  | 434.4944 | 599.4223 | 609.4831 | 720.9704 | 982.6196 | 965.1235 | 485.4776 | 657.3753 | 762.5204 | 537.9023 | 624.8691 | 912.6276 | 1002.789 | 570.6316 | 749.7225 | 801.2748 | 977.1064 | 976.9149 | 462.9515 | 574.5477 | 627.8169 | 503.4787 | 651.0948 | 825.8834 | 884.6197 | 1001.5445 | 527.8475 | 621.2467 | 581.2178 | 773.9726 | 64.7691 | 1.1837 | 17.6634 | 5.3513 | -38.4782 | 3.1244 | 10553.51 | 0.38 | 2.4513 | -1.0187 | -2.2309 | -2.6548 | 6.1049 | 6.1013 | 5.6215 | 68.2357 | 120.9826 | 46.3335 | 24.9413 | -20.1048 | 53.6192 | 23.0885
42810.4495 | 815 | 18.3248 | 18.4811 | 18.4719 | 18.4619 | 17.7319 | 16.3216 | 14.4466 | 16.5468 | 17.05 | 17.1464 | 17.1502 | 16.6484 | 15.6647 | 14.2671 | 14.7096 | 15.0622 | 16.2298 | 14.5869 | 15.1709 | 44.8075 |  |  |  | 16.919 | 18.366 | 112.6048 | 639.0834 | 682.5369 | 650.1125 | 36.6134 | 32.706 | 685.7023 | 34.5896 | 33.6226 | 710.3348 | 706.872 | 647.0056 |  | 627.9142 | 818.7447 | 781.5393 | 687.0574 |  | 258.5546 | 490.8619 | 326.2948 | 535.6867 | 745.6369 | 872.397 | 903.4091 | 29.5196 | 202.6861 | 54.6958 | 403.507 | 26.1519 | 47.7224 | 47.7459 | 47.5175 | 27.833 |  |  | 1.5188 | 0.013887 | -1.1823 | -1.5101 | 6.6778 | 5.52 | 5.4645 | -4.1866 | 13.8413 | 35.1359 | 18.2328 | 0.0015081 | 0.0014522 | -0.00083782 | 16.5933 | 16.597 | 17.108 | 17.427 | 17.3652 | 16.3076 | 14.6451 | 16.7135 | 17.0573 | 17.3527 | 17.3916 | 17.0892 | 16.232 | 14.4082 | 777.2868 | 290.3735 | 530.3798 | 339.4219 | 278.5839 | 643.8146 | 351.747 | 15.7264 | 15.8768 | 16.6202 | 16.9338 | 37.2798 | 55.9158 |  |  |  | 525.4916 | 488.5298 | 498.427 | 527.733 | 84.1015 | 26.4442 | 834.6681 |  |  | 308.4083 |  |  | 17.4163 | 20.7817 | 165.8991 | 16.4725 | 17.4993 | 779.7405 | 693.2109 | 546.364 | 813.0427 | 823.919 | 681.5911 |  | 764.5023 | 805.0307 | 925.9615 | 527.7105 | 657.07 | 828.9159 |  | 909.9895 |  |  | 325.75 | 543.9539 | 669.2995 | [6 empty] | 533.531 |  |  | 311.0696 |  |  | 434.7666 | 598.73 | 607.9787 | 725.2252 | 978.2914 | 960.4985 | 484.5692 | 656.0386 | 760.7774 | 538.3336 | 623.9586 | 915.7964 | 999.0023 | 570.437 | 747.8468 | 796.5084 | 976.5411 | 975.9289 | 464.118 | 574.1697 | 632.1839 | 502.387 | 651.3376 | 828.1733 | 886.4598 | 1000.4616 | 528.8232 | 621.0037 | 580.7992 | 775.9032 | 72.8072 | 1.0696 | 17.6906 | 5.3516 | -38.497 | 3.1244 | 10640.83 | 0.33 | 2.6096 | 0.227 | -2.0945 | -2.3671 | 6.0952 | 5.5417 | 5.5138 | 68.0371 | 120.5845 | 46.048 | 25.2558 | -11.2021 | 52.8534 | 23.0047
42810.4495 | 816 | 18.3105 | 18.4744 | 18.4675 | 18.4555 | 17.7233 | 16.3129 | 14.4491 | 16.5453 | 17.0423 | 17.1385 | 17.1493 | 16.6516 | 15.6469 | 14.256 | 14.703 | 15.0575 | 16.228 | 14.6483 | 15.2679 | 45.3111 |  |  |  | 16.913 | 18.3815 | 116.4769 | 643.4775 | 682.7563 | 654.0365 | 43.9869 | 30.2086 | 695.3045 | 35.2028 | 38.3673 | 723.8317 | 716.8402 | 615.1431 |  | 630.5722 | 807.4974 | 797.559 | 679.8909 |  | 260.0165 | 493.5773 | 327.3099 | 536.9496 | 751.3407 | 876.7689 | 906.3078 | 28.496 | 204.3475 | 51.3962 | 406.3225 | 26.4126 | 47.7854 | 47.7067 | 47.5237 | 27.9717 |  |  | 1.2468 | -0.79239 | -1.6055 | -1.7742 | 6.4011 | 5.4313 | 6.3713 | -4.1794 | 14.5086 | 35.3205 | 19.0091 | 0.0014555 | 0.0014506 | -0.00083618 | 16.5856 | 16.5944 | 17.1033 | 17.4209 | 17.3661 | 16.3046 | 14.6408 | 16.709 | 17.0508 | 17.3472 | 17.3804 | 17.0805 | 16.2296 | 14.4059 | 783.024 | 275.7165 | 491.0154 | 309.7761 | 257.0092 | 646.1773 | 352.9854 | 15.7262 | 15.8784 | 16.6311 | 17.0408 | 37.6853 | 56.2601 |  |  |  | 526.641 | 495.568 | 502.8799 | 538.7293 | 77.4076 | 34.4314 | 832.8756 |  |  | 303.3677 |  |  | 17.4166 | 20.8645 | 165.5563 | 16.4642 | 17.5197 | 764.8277 | 690.8905 | 543.0584 | 802.0625 | 810.2352 | 677.6864 |  | 763.3751 | 797.0325 | 923.8336 | 524.8868 | 655.4523 | 822.0601 |  | 909.4967 |  |  | 325.4779 | 540.8473 | 666.0706 | [6 empty] | 530.2819 |  |  | 310.7345 |  |  | 434.9052 | 598.4723 | 607.6565 | 728.8708 | 979.2668 | 958.407 | 483.5023 | 655.0922 | 759.0718 | 539.3298 | 623.7058 | 917.3976 | 997.6956 | 569.8647 | 746.0529 | 791.7785 | 975.3484 | 975.9266 | 464.9986 | 574.2811 | 636.1923 | 501.5556 | 651.34 | 831.1215 | 886.8812 | 1000.3968 | 529.7688 | 621.8106 | 580.1358 | 776.8384 | 69.47 | 0.97051 | 17.72 | 5.3403 | -38.4577 | 3.1244 | 10660.8 | 0.32 | 2.3694 | -1.7177 | -2.445 | -2.5703 | 5.979 | 5.5075 | 5.9651 | 67.8291 | 119.9177 | 45.787 | 25.2956 | -6.6219 | 55.49 | 22.8643
42810.4495 | 817 | 18.3092 | 18.4753 | 18.4681 | 18.4589 | 17.7237 | 16.3148 | 14.447 | 16.5451 | 17.035 | 17.1433 | 17.148 | 16.6504 | 15.6499 | 14.2584 | 14.7049 | 15.0668 | 16.234 | 14.7136 | 15.363 | 45.8105 |  |  |  | 16.9258 | 18.4101 | 123.1485 | 645.7491 | 685.3805 | 657.3371 | 18.7121 | 20.7528 | 717.4427 | 16.8039 | 17.7758 | 717.2023 | 706.7178 | 651.3402 |  | 616.8716 | 849.1097 | 826.4913 | 676.0675 |  | 259.9855 | 495.0125 | 327.1601 | 537.3337 | 757.8988 | 875.6694 | 905.9304 | 28.0298 | 205.8592 | 49.2163 | 408.8061 | 26.6993 | 47.871 | 47.6591 | 47.5125 | 28.207 |  |  | 1.1876 | -0.42178 | -1.2197 | -1.0573 | 6.3932 | 5.5785 | 7.0015 | -3.6406 | 13.5913 | 33.451 | 19.4876 | 0.0014227 | 0.0014522 | -0.00084275 | 16.5953 | 16.5976 | 17.103 | 17.4221 | 17.3571 | 16.3076 | 14.6395 | 16.7162 | 17.0547 | 17.3542 | 17.3899 | 17.0778 | 16.2297 | 14.4031 | 779.1285 | 275.4941 | 509.8009 | 315.3035 | 261.2184 | 648.3397 | 354.6973 | 15.7281 | 15.8866 | 16.6463 | 17.1484 | 38.0573 | 56.586 |  |  |  | 527.873 | 502.788 | 507.7237 | 545.5892 | 79.2481 | 37.1355 | 820.5357 |  |  | 300.2668 |  |  | 17.3997 | 20.9472 | 176.749 | 16.4651 | 17.5358 | 809.9287 | 690.4382 | 540.457 | 796.467 | 804.9862 | 679.1387 |  | 762.4937 | 789.2029 | 921.9365 | 522.8561 | 653.9829 | 814.0216 |  | 909.2813 |  |  | 325.8041 | 542.6555 | 666.0246 | [6 empty] | 527.7641 |  |  | 310.2662 |  |  | 434.9328 | 598.727 | 607.9147 | 728.357 | 979.1539 | 955.6816 | 482.4051 | 653.5428 | 757.5517 | 539.9029 | 623.8256 | 919.1551 | 995.5688 | 569.1846 | 743.644 | 790.7512 | 973.8555 | 976.5399 | 465.265 | 574.3558 | 639.1773 | 500.5926 | 651.4048 | 835.471 | 884.224 | 998.4813 | 530.481 | 622.5563 | 579.1144 | 776.7421 | 69.726 | 0.87172 | 17.7469 | 5.3128 | -38.4764 | 3.1244 | 10682.41 | 0.33 | 2.3167 | -1.2544 | -2.1332 | -1.9861 | 5.9725 | 5.5789 | 6.2501 | 67.542 | 119.3463 | 45.5363 | 26.3511 | -8.4233 | 53.1214 | 22.8512
42810.4495 | 818 | 18.3096 | 18.4754 | 18.4757 | 18.4562 | 17.7349 | 16.317 | 14.4538 | 16.548 | 17.0452 | 17.1489 | 17.1503 | 16.6518 | 15.6572 | 14.2697 | 14.7043 | 15.0602 | 16.2344 | 14.7843 | 15.4673 | 46.3085 |  |  |  | 16.9346 | 18.44 | 119.8511 | 646.7083 | 687.4543 | 657.8681 | 17.092 | 17.5195 | 745.7555 | 16.9028 | 17.9267 | 719.3559 | 707.197 | 662.7018 |  | 554.0262 | 824.0973 | 798.372 | 673.1011 |  | 260.2445 | 496.2098 | 327.5474 | 536.2027 | 753.5511 | 872.0845 | 905.314 | 27.6261 | 207.4737 | 47.3077 | 411.7556 | 27.0462 | 47.9879 | 47.6342 | 47.5231 | 28.4236 |  |  | 0.16975 | -0.56372 | -1.2118 | -1.7354 | 6.3466 | 6.114 | 6.1834 | -3.5644 | 13.4901 | 33.9002 | 19.8069 | 0.0013652 | 0.0015048 | -0.00083618 | 16.6065 | 16.595 | 17.1047 | 17.426 | 17.3632 | 16.3068 | 14.6442 | 16.7214 | 17.0606 | 17.3601 | 17.3874 | 17.0842 | 16.2346 | 14.4023 | 784.4658 | 270.5795 | 528.1397 | 321.3424 | 254.8691 | 650.2718 | 356.3949 | 15.7344 | 15.8897 | 16.6624 | 17.2437 | 38.4072 | 56.8954 |  |  |  | 529.0254 | 507.4766 | 511.7334 | 546.5377 | 72.0389 | 35.1983 | 815.9907 |  |  | 298.2768 |  |  | 17.399 | 21.0147 | 188.3572 | 16.462 | 17.5614 | 805.2005 | 692.2795 | 538.2316 | 796.1006 | 805.7169 | 682.5752 |  | 761.6546 | 787.1083 | 921.1194 | 522.2304 | 652.5312 | 813.8379 |  | 909.1738 |  |  | 326.7601 | 546.3702 | 667.4171 | [6 empty] | 525.8046 |  |  | 310.8079 |  |  | 433.9692 | 599.5502 | 608.9965 | 729.2209 | 981.7965 | 954.0131 | 481.8044 | 651.907 | 757.3523 | 540.5671 | 624.0036 | 920.5523 | 993.8199 | 568.6683 | 741.0242 | 795.1044 | 972.8263 | 976.3567 | 464.8447 | 574.3087 | 641.1384 | 499.348 | 650.8639 | 835.6133 | 883.8226 | 998.854 | 530.7081 | 622.7305 | 578.1072 | 773.0242 | 75.9849 | 0.79472 | 17.7738 | 5.28 | -38.5077 | 3.1244 | 10669.84 | 0.29 | 0.87611 | -1.4513 | -2.1279 | -2.5465 | 5.9413 | 5.8315 | 5.8644 | 67.2121 | 119.0658 | 45.2516 | 26.3167 | -10.1766 | 53.3195 | 22.9915
42810.4495 | 819 | 18.2991 | 18.4697 | 18.4643 | 18.4491 | 17.7249 | 16.3132 | 14.4507 | 16.5452 | 17.0457 | 17.1469 | 17.1471 | 16.6552 | 15.6528 | 14.27 | 14.7062 | 15.0722 | 16.2505 | 14.8585 | 15.56 | 46.7999 |  |  |  | 16.9362 | 18.469 | 117.9882 | 642.0855 | 687.6175 | 650.8958 | 17.0886 | 17.5283 | 762.3833 | 16.9063 | 17.9559 | 718.8283 | 707.4144 | 659.3881 |  | 543.2582 | 829.2291 | 792.0051 | 673.4371 |  | 261.8822 | 497.2334 | 328.9337 | 535.7799 | 758.9112 | 873.2039 | 905.3107 | 28.3713 | 208.9953 | 46.7305 | 414.0521 | 28.7254 | 48.1196 | 47.5997 | 47.5194 | 28.622 |  |  | 1.0733 | -0.38038 | -0.96871 | -1.284 | 6.8112 | 6.0634 | 6.5119 | -3.8167 | 14.14 | 35.3031 | 20.345 | 0.0014243 | 0.0014243 | 0.033986 | 16.6086 | 16.6008 | 17.1076 | 17.4325 | 17.3609 | 16.3057 | 14.6433 | 16.7161 | 17.0568 | 17.3526 | 17.3967 | 17.0823 | 16.236 | 14.4138 | 782.0495 | 276.82 | 544.6336 | 326.0605 | 251.8752 | 651.6413 | 358.1088 | 15.7239 | 15.8898 | 16.6591 | 17.3462 | 38.7642 | 57.1963 |  |  |  | 530.004 | 508.6177 | 512.712 | 545.2314 | 76.9891 | 38.9113 | 816.3479 |  |  | 296.3254 |  |  | 17.3937 | 21.1009 | 179.1922 | 16.4702 | 17.5823 | 810.2133 | 695.3384 | 535.7574 | 799.0381 | 809.4447 | 687.456 |  | 761.2947 | 791.2195 | 921.2633 | 520.9821 | 650.9152 | 818.8862 |  | 909.735 |  |  | 329.7531 | 551.7948 | 670.1256 | [6 empty] | 524.316 |  |  | 312.3072 |  |  | 433.1298 | 599.6993 | 609.9693 | 729.6015 | 983.5959 | 955.0527 | 481.2293 | 651.2305 | 756.825 | 541.8402 | 623.3946 | 919.9246 | 993.9878 | 568.9929 | 740.2032 | 796.5415 | 973.3393 | 975.5251 | 464.967 | 574.4414 | 640.9555 | 498.2394 | 650.3809 | 833.0993 | 885.8649 | 997.9634 | 531.2039 | 623.0309 | 577.3122 | 770.4935 | 75.2729 | 0.73368 | 17.7987 | 5.2423 | -38.5362 | 3.1244 | 10640.89 | 0.27 | 2.1947 | -1.193 | -1.9038 | -2.1918 | 6.158 | 5.8101 | 6.0212 | 66.9761 | 119.0112 | 44.9515 | 26.9825 | -11.7214 | 53.3627 | 23.1698
42810.4495 | 820 | 18.2896 | 18.4655 | 18.4573 | 18.4491 | 17.7184 | 16.3108 | 14.4466 | 16.5393 | 17.0385 | 17.1369 | 17.142 | 16.6463 | 15.6468 | 14.2643 | 14.6917 | 15.07 | 16.2562 | 14.936 | 15.7047 | 47.2773 |  |  |  | 16.9404 | 18.5018 | 121.8581 | 637.7604 | 688.4116 | 645.6509 | 17.0845 | 17.5347 | 784.765 | 16.8989 | 17.9637 | 718.3935 | 707.4216 | 666.615 |  | 540.3352 | 850.0294 | 809.2349 | 669.2781 |  | 263.1513 | 499.1088 | 330.3497 | 535.7584 | 761.8732 | 872.2729 | 907.1992 | 30.6942 | 210.7286 | 47.259 | 416.6949 | 27.2811 | 48.247 | 47.5704 | 47.5081 | 28.891 |  |  | 1.0891 | -1.14 | -1.5897 | -1.9582 | 5.5193 | 6.1252 | 6.0552 | -3.3554 | 13.6438 | 32.8 | 21.4144 | 0.0014161 | 0.001375 | 0.67875 | 16.6135 | 16.5972 | 17.1089 | 17.4209 | 17.3702 | 16.3028 | 14.6477 | 16.7154 | 17.0595 | 17.364 | 17.391 | 17.0877 | 16.2348 | 14.4081 | 775.4569 | 286.7557 | 556.1746 | 332.4643 | 266.9723 | 653.3572 | 360.005 | 15.7144 | 15.8924 | 16.671 | 17.4526 | 39.1535 | 57.5272 |  |  |  | 530.8178 | 508.6349 | 513.1258 | 542.972 | 76.363 | 42.3757 | 818.9975 |  |  | 298.5178 |  |  | 17.4056 | 21.2082 | 184.4264 | 16.4742 | 17.6317 | 822.4531 | 699.9706 | 534.1802 | 794.8039 | 804.8789 | 690.0205 |  | 761.6663 | 790.7669 | 920.4411 | 519.8016 | 649.5087 | 817.4505 |  | 910.4116 |  |  | 331.2835 | 554.397 | 675.3655 | [6 empty] | 523.0952 |  |  | 313.5784 |  |  | 433.2565 | 599.2975 | 609.5488 | 732.3369 | 980.643 | 956.0278 | 480.7337 | 651.0633 | 756.4701 | 542.859 | 621.9106 | 920.6018 | 995.2704 | 569.0953 | 738.9948 | 797.1678 | 976.9165 | 973.58 | 464.457 | 574.1841 | 638.3892 | 497.0456 | 649.842 | 832.8537 | 886.1281 | 999.9862 | 531.3331 | 622.0993 | 576.8171 | 767.8757 | 72.0742 | 0.6867 | 17.8239 | 5.1996 | -38.5513 | 3.1244 | 10630.45 | 0.31 | 2.2045 | -2.0678 | -2.4418 | -2.7101 | 5.541 | 5.8373 | 5.8038 | 67.0085 | 118.6835 | 44.694 | 28.2143 | -12.6844 | 53.4799 | 23.3509
42810.4495 | 821 | 18.2863 | 18.4607 | 18.4607 | 18.4482 | 17.7232 | 16.3104 | 14.4423 | 16.5442 | 17.0387 | 17.1426 | 17.1406 | 16.646 | 15.648 | 14.2674 | 14.6829 | 15.0662 | 16.2505 | 14.9935 | 15.8457 | 47.7679 |  |  |  | 16.9546 | 18.5238 | 118.3233 | 636.6723 | 686.6191 | 644.5115 | 17.1781 | 17.5458 | 769.8876 | 16.901 | 17.9865 | 716.355 | 707.5009 | 659.9812 |  | 541.2739 | 823.1903 | 797.1777 | 672.9411 |  | 263.5534 | 500.2479 | 331.3239 | 536.3974 | 757.4404 | 869.9028 | 909.7198 | 31.026 | 212.377 | 49.5873 | 419.1262 | 24.3853 | 48.374 | 47.5533 | 47.4896 | 29.1437 |  |  | 0.73225 | -0.48355 | -1.313 | -1.468 | 6.2277 | 6.5589 | 6.6144 | -3.1891 | 13.0086 | 32.9292 | 20.6355 | 0.0013602 | 0.0013701 | 1.3255 | 16.6136 | 16.5893 | 17.1055 | 17.4222 | 17.3596 | 16.3046 | 14.6414 | 16.7137 | 17.0607 | 17.3595 | 17.3956 | 17.0872 | 16.2319 | 14.4087 | 778.7587 | 294.2658 | 560.261 | 328.51 | 267.5446 | 655.2219 | 362.1563 | 15.7213 | 15.9023 | 16.6897 | 17.5771 | 39.5366 | 57.8544 |  |  |  | 531.2244 | 508.0442 | 512.6419 | 536.4407 | 74.4286 | 38.7867 | 815.6537 |  |  | 295.7664 |  |  | 17.4083 | 21.2857 | 188.8724 | 16.4734 | 17.6542 | 800.1547 | 701.1 | 533.0476 | 795.0638 | 804.8292 | 689.8666 |  | 761.7718 | 791.5116 | 920.161 | 519.3624 | 648.1447 | 818.8347 |  | 910.8345 |  |  | 331.5472 | 552.8769 | 676.5422 | [6 empty] | 521.8416 |  |  | 313.2672 |  |  | 432.9697 | 598.7243 | 608.09 | 736.0187 | 981.0101 | 956.9919 | 480.6355 | 650.3957 | 756.95 | 543.5928 | 620.4562 | 919.3019 | 995.7281 | 569.2191 | 739.0934 | 801.055 | 976.5257 | 974.6624 | 464.0923 | 574.0063 | 636.9894 | 497.1474 | 650.7718 | 833.2808 | 887.8539 | 998.5356 | 530.8475 | 621.4876 | 577.3837 | 767.1024 | 73.2785 | 0.64054 | 17.8477 | 5.1559 | -38.5595 | 3.1244 | 10664.39 | 0.32 | 1.8065 | -1.3477 | -2.2208 | -2.3482 | 5.8798 | 6.0341 | 6.0596 | 67.0423 | 118.5471 | 44.4259 | 28.392 | -12.775 | 53.3974 | 23.5916
42810.4495 | 822 | 18.2874 | 18.4639 | 18.4635 | 18.4508 | 17.7257 | 16.3098 | 14.4576 | 16.546 | 17.0478 | 17.1455 | 17.1428 | 16.6524 | 15.6514 | 14.2721 | 14.6878 | 15.0738 | 16.2606 | 15.0803 | 15.9239 | 48.2785 |  |  |  | 16.9554 | 18.5668 | 119.0953 | 636.5099 | 685.4426 | 645.6757 | 17.1712 | 24.3108 | 726.6231 | 17.317 | 18.0311 | 714.954 | 707.8325 | 672.1523 |  | 543.256 | 848.7844 | 825.2952 | 679.6618 |  | 263.7065 | 501.2992 | 332.4966 | 540.407 | 754.3319 | 862.6062 | 909.6467 | 30.4595 | 213.7919 | 50.7068 | 421.0111 | 22.4062 | 48.4756 | 47.5417 | 47.4706 | 29.3904 |  |  | 1.1528 | -0.22267 | -1.1087 | -1.1677 | 6.6981 | 6.093 | 5.7845 | -3.3705 | 13.2984 | 33.4518 | 20.6742 | 0.0013405 | 0.001352 | 1.4779 | 16.6149 | 16.5882 | 17.102 | 17.4189 | 17.3612 | 16.3035 | 14.6326 | 16.7143 | 17.0565 | 17.3552 | 17.3883 | 17.0763 | 16.2307 | 14.4056 | 775.1037 | 313.3277 | 563.3405 | 328.3261 | 264.1476 | 656.3251 | 364.2464 | 15.7237 | 15.9075 | 16.699 | 17.6913 | 39.8842 | 58.1443 |  |  |  | 531.5742 | 507.2855 | 511.854 | 534.8181 | 67.8362 | 36.9911 | 816.8365 |  |  | 294.8953 |  |  | 17.3997 | 21.3701 | 182.1432 | 16.4701 | 17.6738 | 783.5525 | 700.1967 | 533.0718 | 798.7349 | 809.6543 | 687.9021 |  | 761.7199 | 804.1561 | 920.231 | 519.5726 | 646.9288 | 833.834 |  | 911.3828 |  |  | 332.0461 | 550.8796 | 675.4959 | [6 empty] | 521.9027 |  |  | 311.8213 |  |  | 433.1483 | 598.4181 | 606.7567 | 734.1764 | 975.8601 | 957.9177 | 480.4309 | 650.2942 | 759.3165 | 544.2584 | 620.2238 | 916.5492 | 993.525 | 568.6602 | 738.8173 | 796.4285 | 972.1042 | 976.563 | 464.1286 | 573.7264 | 636.5134 | 496.6032 | 651.6364 | 832.9629 | 886.1485 | 995.1438 | 529.6408 | 622.6173 | 577.3883 | 769.2047 | 69.1289 | 0.60097 | 17.8732 | 5.1142 | -38.5213 | 3.1244 | 10684.16 | 0.17 | 2.2681 | -0.91516 | -2.042 | -2.0957 | 6.0784 | 5.7973 | 5.6486 | 67.0823 | 118.2247 | 44.1711 | 29.1212 | -12.7627 | 53.2908 | 23.6877
42810.4496 | 823 | 18.2813 | 18.4676 | 18.4669 | 18.4508 | 17.7225 | 16.3161 | 14.4487 | 16.545 | 17.0472 | 17.1525 | 17.142 | 16.6487 | 15.6496 | 14.2762 | 14.6795 | 15.0711 | 16.2621 | 15.1472 | 16.0296 | 48.7453 |  |  |  | 16.9526 | 18.5923 | 120.6103 | 638.5429 | 685.2368 | 648.9142 | 17.0717 | 18.1071 | 776.0415 | 16.936 | 18.0314 | 720.8282 | 708.5601 | 728.3933 |  | 546.8768 | 882.2742 | 859.5826 | 688.3213 |  | 263.6375 | 502.513 | 333.5922 | 545.9293 | 752.3632 | 864.3219 | 910.2897 | 29.5716 | 215.495 | 50.0168 | 423.1176 | 21.0669 | 48.5474 | 47.5153 | 47.4674 | 29.6318 |  |  | 1.5734 | 0.11377 | -1.018 | -1.2814 | 6.0647 | 6.5286 | 6.3174 | -2.9138 | 13.2406 | 33.6922 | 22.7471 | 0.0013504 | 0.0012633 | 1.5296 | 16.6175 | 16.5863 | 17.1017 | 17.4214 | 17.361 | 16.3084 | 14.6415 | 16.72 | 17.0586 | 17.3543 | 17.3927 | 17.0803 | 16.2319 | 14.4114 | 753.3669 | 274.6505 | 531.5159 | 318.6083 | 257.9906 | 656.5838 | 365.7642 | 15.7192 | 15.9112 | 16.7123 | 17.8075 | 40.2324 | 58.4388 |  |  |  | 532.0776 | 507.6663 | 511.5855 | 535.2305 | 67.915 | 33.6792 | 820.6204 |  |  | 296.7276 |  |  | 17.3985 | 21.4615 | 181.7233 | 16.4752 | 17.6963 | 842.5822 | 699.6544 | 533.5036 | 797.7286 | 809.0713 | 688.116 |  | 761.4382 | 809.4717 | 919.5412 | 520.2103 | 646.1371 | 835.38 |  | 911.629 |  |  | 332.9005 | 549.6274 | 674.3421 | [6 empty] | 522.4111 |  |  | 310.6413 |  |  | 433.4112 | 598.8464 | 606.5903 | 736.8508 | 973.0791 | 957.3847 | 479.8828 | 649.723 | 758.6777 | 544.5631 | 622.3792 | 918.5596 | 988.8383 | 568.0292 | 736.3398 | 790.4024 | 970.7005 | 976.8452 | 464.1556 | 573.1068 | 637.3893 | 496.3228 | 652.1443 | 832.0582 | 885.8273 | 1000.2548 | 529.6419 | 623.3692 | 577.2431 | 770.8068 | 67.7715 | 0.57128 | 17.8984 | 5.0657 | -38.4668 | 3.1243 | 10724.22 | 0.25 | 2.6544 | 0.65467 | -1.9583 | -2.1971 | 5.7882 | 6.0055 | 5.9075 | 66.9978 | 117.7923 | 43.9917 | 31.6123 | -8.9686 | 53.2265 | 23.7498
42810.4496 | 824 | 18.291 | 18.4703 | 18.4701 | 18.4501 | 17.7239 | 16.3209 | 14.4602 | 16.5618 | 17.0483 | 17.1499 | 17.1467 | 16.6637 | 15.6605 | 14.2712 | 14.6717 | 15.0764 | 16.2566 | 15.2266 | 16.1347 | 49.2194 |  |  |  | 16.958 | 18.6189 | 121.8633 | 641.9385 | 684.0471 | 653.9285 | 17.069 | 17.5931 | 800.7283 | 16.892 | 18.0525 | 722.8493 | 710.1728 | 720.6541 |  | 550.8941 | 889.418 | 868.8867 | 704.3149 |  | 263.5058 | 503.1463 | 335.6099 | 546.6209 | 751.7551 | 861.9003 | 910.2541 | 29.135 | 216.8772 | 49.4292 | 424.7766 | 20.135 | 48.6177 | 47.4751 | 47.4739 | 29.8613 |  |  | 1.2119 | -0.13659 | -0.99302 | -1.2873 | 6.7021 | 6.1133 | 6.2445 | -3.6044 | 14.0861 | 34.8801 | 22.9303 | 0.0012978 | 0.0014194 | 1.5564 | 16.6206 | 16.5867 | 17.1034 | 17.4212 | 17.3648 | 16.3033 | 14.6428 | 16.7152 | 17.0483 | 17.3512 | 17.3891 | 17.0768 | 16.2304 | 14.4129 | 751.4972 | 239.9392 | 519.1844 | 316.0844 | 268.6316 | 657.4173 | 367.1943 | 15.7126 | 15.9132 | 16.7224 | 17.9241 | 40.5825 | 58.7301 |  |  |  | 532.8157 | 509.3919 | 513.2755 | 543.0974 | 73.9766 | 28.1011 | 819.5446 |  |  | 296.518 |  |  | 17.404 | 21.5546 | 183.4602 | 16.4767 | 17.7298 | 852.9491 | 699.9397 | 533.1136 | 794.8432 | 805.2696 | 689.7193 |  | 761.0507 | 806.3367 | 918.2723 | 520.5236 | 645.3294 | 830.8368 |  | 910.896 |  |  | 334.1465 | 550.1085 | 673.8306 | [6 empty] | 522.4336 |  |  | 309.9609 |  |  | 433.7477 | 599.8864 | 607.0368 | 736.9214 | 972.3465 | 953.7328 | 479.2266 | 649.0898 | 756.5955 | 544.663 | 623.5726 | 919.353 | 985.3415 | 567.3239 | 735.8334 | 788.5494 | 971.7681 | 978.3013 | 464.7952 | 573.7107 | 639.752 | 496.3821 | 653.1565 | 833.861 | 886.6799 | 1002.8875 | 530.102 | 624.7487 | 577.6745 | 777.366 | 68.467 | 0.54379 | 17.922 | 5.0138 | -38.4842 | 3.1243 | 10719.76 | 0.32 | 2.336 | -0.71762 | -1.9349 | -2.203 | 6.0783 | 5.8052 | 5.8671 | 66.8452 | 117.3566 | 43.8184 | 32.0648 | -7.3546 | 53.1739 | 23.6393
42810.4496 | 825 | 18.2806 | 18.4616 | 18.4605 | 18.4495 | 17.7248 | 16.3056 | 14.4535 | 16.5471 | 17.0423 | 17.1502 | 17.1438 | 16.6561 | 15.6483 | 14.2616 | 14.6679 | 15.0679 | 16.2656 | 15.3065 | 16.2496 | 49.7043 |  |  |  | 16.9612 | 18.6523 | 119.5445 | 643.939 | 684.5658 | 656.3052 | 17.0722 | 17.6155 | 814.8202 | 16.8972 | 18.0941 | 730.2067 | 711.7811 | 750.3274 |  | 555.577 | 890.3509 | 869.727 | 702.4525 |  | 264.2599 | 503.1407 | 336.1431 | 547.8186 | 748.0078 | 861.1087 | 910.5648 | 28.8474 | 218.4127 | 48.8558 | 426.7272 | 19.4289 | 48.6993 | 47.4556 | 47.4785 | 30.1274 |  |  | 0.19933 | -0.14513 | -1.3755 | -2.2099 | 5.8524 | 4.9273 | 5.703 | -4.1124 | 13.6317 | 32.7559 | 22.4244 | 0.0012633 | 0.0013011 | 1.5614 | 16.628 | 16.5858 | 17.1029 | 17.4201 | 17.3637 | 16.2958 | 14.6445 | 16.713 | 17.0525 | 17.35 | 17.3851 | 17.076 | 16.23 | 14.4138 | 764.1007 | 226.365 | 495.0731 | 313.0544 | 261.6419 | 658.3961 | 368.1348 | 15.7049 | 15.9152 | 16.7364 | 18.0415 | 40.9754 | 59.0443 |  |  |  | 534.1934 | 513.4812 | 516.2016 | 551.6135 | 64.3144 | 29.2203 | 816.2808 |  |  | 298.042 |  |  | 17.4086 | 21.646 | 180.7337 | 16.4766 | 17.7632 | 875.0273 | 700.3235 | 532.0892 | 792.7628 | 802.0538 | 691.3366 |  | 760.6816 | 802.5648 | 917.0524 | 521.151 | 643.9806 | 825.5484 |  | 910.2765 |  |  | 334.4906 | 550.5239 | 674.5326 | [6 empty] | 521.4353 |  |  | 309.6267 |  |  | 433.9542 | 600.5319 | 608.0524 | 739.3363 | 971.2149 | 953.5424 | 478.9365 | 648.6071 | 756.5548 | 544.7336 | 624.3403 | 919.7052 | 983.8167 | 567.2004 | 735.8533 | 784.4211 | 974.7914 | 981.5298 | 465.0054 | 574.7059 | 641.4303 | 496.2266 | 654.2583 | 836.3759 | 884.8854 | 1006.0588 | 530.7352 | 625.5 | 578.0217 | 780.2298 | 80.5334 | 0.5185 | 17.9472 | 4.9613 | -38.5976 | 3.1244 | 10639.82 | 0.29 | 0.94856 | -0.73971 | -2.2772 | -2.8864 | 5.6779 | 5.2099 | 5.605 | 66.6975 | 116.9603 | 43.527 | 30.9524 | -4.515 | 53.618 | 23.605
42810.4496 | 826 | 18.2702 | 18.4599 | 18.457 | 18.4435 | 17.7243 | 16.3084 | 14.4653 | 16.538 | 17.0406 | 17.1428 | 17.137 | 16.644 | 15.6411 | 14.2619 | 14.6613 | 15.0659 | 16.2581 | 15.3803 | 16.4068 | 50.1764 |  |  |  | 16.9579 | 18.6897 | 121.3297 | 645.0172 | 685.5649 | 656.4007 | 17.0713 | 17.6303 | 818.8373 | 16.9017 | 18.1182 | 731.0438 | 712.3941 | 745.6485 |  | 557.7513 | 886.1243 | 863.6859 | 693.2163 |  | 263.8889 | 503.856 | 337.7055 | 547.1997 | 743.2884 | 857.9865 | 909.2583 | 28.6574 | 220.0207 | 48.2622 | 428.8258 | 18.8772 | 48.7526 | 47.4427 | 47.4799 | 30.4293 |  |  | 0.97866 | -0.14317 | -0.91286 | -1.1335 | 6.156 | 6.7231 | 7.0186 | -2.6214 | 14.5279 | 34.8187 | 22.5128 | 0.0013356 | 0.0012994 | 1.5709 | 16.6339 | 16.5924 | 17.1012 | 17.423 | 17.3712 | 16.303 | 14.6396 | 16.7192 | 17.068 | 17.3572 | 17.396 | 17.0882 | 16.2407 | 14.4125 | 754.8419 | 219.8172 | 482.9011 | 316.677 | 267.0682 | 658.3867 | 368.911 | 15.7007 | 15.9227 | 16.7523 | 18.1596 | 41.3337 | 59.3346 |  |  |  | 535.2337 | 514.549 | 517.2963 | 551.0223 | 72.8959 | 32.2319 | 814.201 |  |  | 303.8382 |  |  | 17.4194 | 21.7564 | 186.8 | 16.4856 | 17.8052 | 866.5162 | 700.7625 | 532.3079 | 793.995 | 804.0493 | 694.7152 |  | 760.5263 | 803.7336 | 916.4531 | 521.53 | 642.9865 | 823.4752 |  | 910.4435 |  |  | 334.7705 | 551.3792 | 676.7172 | [6 empty] | 522.054 |  |  | 309.9298 |  |  | 433.7848 | 600.4019 | 609.1611 | 740.6059 | 971.6837 | 952.7897 | 478.9424 | 647.5209 | 758.537 | 544.694 | 623.8926 | 919.4714 | 984.2934 | 567.0169 | 735.0667 | 782.2816 | 981.5003 | 983.374 | 465.2072 | 574.9143 | 642.8233 | 496.322 | 654.6562 | 837.4414 | 883.1492 | 1010.2301 | 531.2011 | 627.025 | 577.968 | 778.7136 | 71.1112 | 0.46579 | 17.9731 | 4.8986 | -38.6236 | 3.1244 | 10561.22 | 0.3 | 2.1019 | -0.73502 | -1.856 | -2.0682 | 5.8153 | 6.0773 | 6.2094 | 66.5604 | 116.6822 | 43.3152 | 31.9783 | -3.0298 | 54.0245 | 23.7747
42810.4496 | 827 | 18.2704 | 18.4589 | 18.46 | 18.4432 | 17.7221 | 16.3137 | 14.4703 | 16.5446 | 17.0427 | 17.1398 | 17.1443 | 16.646 | 15.6446 | 14.2671 | 14.6526 | 15.0601 | 16.2687 | 15.4674 | 16.6028 | 50.6534 |  |  |  | 16.9676 | 18.7269 | 120.991 | 645.0625 | 684.0803 | 655.7601 | 17.0617 | 17.6506 | 821.7031 | 16.9017 | 18.1452 | 726.5069 | 712.3992 | 727.6294 |  | 558.818 | 882.6743 | 864.2144 | 681.8726 |  | 264.4108 | 504.5114 | 338.3316 | 545.2313 | 741.9149 | 855.91 | 910.6422 | 29.0092 | 221.4143 | 48.2903 | 430.7113 | 18.4001 | 48.7748 | 47.438 | 47.4717 | 30.7146 |  |  | 0.35769 | 0.17685 | -0.78669 | -1.0639 | 7.1378 | 6.1725 | 6.0427 | -2.9224 | 13.4317 | 35.1587 | 22.0532 | 0.0012534 | 0.0013734 | 1.5751 | 16.6319 | 16.5806 | 17.0966 | 17.4177 | 17.3537 | 16.2928 | 14.6361 | 16.7111 | 17.0612 | 17.3563 | 17.3877 | 17.0849 | 16.2243 | 14.4102 | 755.888 | 227.5825 | 473.5079 | 301.2198 | 256.6549 | 659.3473 | 369.5226 | 15.7 | 15.9275 | 16.7633 | 18.2766 | 41.6779 | 59.6144 |  |  |  | 535.9907 | 514.0114 | 517.4655 | 547.6489 | 87.0787 | 33.7834 | 815.6419 |  |  | 315.4189 |  |  | 17.4025 | 21.8395 | 186.2047 | 16.4838 | 17.8397 | 858.5541 | 702.6746 | 532.4572 | 797.0565 | 806.0449 | 702.0323 |  | 760.8008 | 807.6383 | 916.2787 | 521.4122 | 642.2534 | 824.1243 |  | 910.5514 |  |  | 335.6936 | 555.9036 | 680.9372 | [6 empty] | 522.2376 |  |  | 310.8678 |  |  | 433.4254 | 599.9036 | 609.7563 | 736.5833 | 968.7864 | 953.557 | 479.0078 | 646.3572 | 759.6214 | 545.251 | 624.0719 | 916.8546 | 985.2837 | 566.5992 | 734.6549 | 780.1369 | 983.4748 | 984.3239 | 465.1126 | 574.9862 | 643.1291 | 496.7172 | 654.6051 | 838.6882 | 883.9928 | 1013.2464 | 531.5197 | 627.0369 | 577.7105 | 777.2979 | 67.1802 | 0.48289 | 17.9972 | 4.8401 | -38.5374 | 3.1243 | 10487.61 | 0.32 | 1.2703 | 0.81727 | -1.7237 | -2.0045 | 6.2561 | 5.8178 | 5.7563 | 66.4336 | 116.5023 | 43.1705 | 32.1452 | -1.8813 | 54.3409 | 23.9803
42810.4496 | 828 | 18.2662 | 18.4515 | 18.4589 | 18.4433 | 17.718 | 16.3081 | 14.4668 | 16.5436 | 17.0369 | 17.1367 | 17.1409 | 16.6387 | 15.6453 | 14.2598 | 14.6486 | 15.0578 | 16.2749 | 15.5563 | 16.798 | 51.1118 |  |  |  | 16.9725 | 18.7665 | 119.5397 | 646.5818 | 682.5887 | 657.1253 | 17.0635 | 17.6769 | 826.3594 | 16.9018 | 18.1802 | 722.3354 | 712.1799 | 737.9756 |  | 557.9169 | 885.5322 | 870.0314 | 679.0841 |  | 265.9582 | 506.1189 | 340.4087 | 546.9666 | 748.2903 | 856.0896 | 912.7065 | 30.0401 | 223.1745 | 48.358 | 432.7992 | 17.9886 | 48.7804 | 47.4574 | 47.4737 | 30.9974 |  |  | 0.23547 | -0.13068 | -0.66578 | -1.5804 | 6.9984 | 6.7862 | 6.2839 | -2.8271 | 13.1157 | 33.7606 | 22.6149 | 0.0012863 | 0.0012469 | 1.5744 | 16.636 | 16.5765 | 17.0963 | 17.412 | 17.3571 | 16.2963 | 14.6355 | 16.7144 | 17.0558 | 17.3466 | 17.3903 | 17.08 | 16.2358 | 14.4136 | 780.8862 | 231.3728 | 478.9485 | 295.681 | 247.8507 | 661.4216 | 370.5796 | 15.6781 | 15.9208 | 16.7667 | 18.3837 | 42.0112 | 59.8847 |  |  |  | 536.6777 | 513.7838 | 516.9109 | 545.9837 | 84.4407 | 33.9391 | 817.0777 |  |  | 331.5501 |  |  | 17.4146 | 21.9416 | 184.0411 | 16.475 | 17.8819 | 858.783 | 699.7394 | 531.9817 | 796.3928 | 803.9553 | 695.4457 |  | 760.4433 | 811.0241 | 915.981 | 521.241 | 641.3689 | 823.6437 |  | 911.0265 |  |  | 336.8583 | 555.8302 | 679.4255 | [6 empty] | 522.0482 |  |  | 313.0963 |  |  | 433.7633 | 599.8756 | 609.8267 | 733.1515 | 965.8516 | 954.8467 | 479.0061 | 645.7526 | 759.1174 | 546.141 | 624.4657 | 914.8673 | 988.8993 | 566.2683 | 733.7542 | 779.3183 | 982.766 | 982.9243 | 465.4817 | 575.2453 | 645.274 | 497.467 | 653.9394 | 839.1278 | 887.8341 | 1017.371 | 532.0586 | 627.9044 | 577.9093 | 774.5913 | 72.6375 | 0.46391 | 18.0222 | 4.7796 | -38.5871 | 3.1244 | 10487.5 | 0.26 | 1.0314 | -0.70325 | -1.5874 | -2.4456 | 6.1953 | 6.1006 | 5.8705 | 66.517 | 116.2864 | 42.997 | 29.9809 | -2.3046 | 54.3646 | 24.1282
42810.4496 | 829 | 18.2605 | 18.4477 | 18.4503 | 18.441 | 17.7092 | 16.3048 | 14.4528 | 16.5315 | 17.0392 | 17.1299 | 17.1353 | 16.643 | 15.6378 | 14.2561 | 14.6493 | 15.0654 | 16.2772 | 15.6455 | 16.9604 | 51.5649 |  |  |  | 16.9732 | 18.8102 | 119.7161 | 647.3264 | 682.0697 | 657.8564 | 17.0622 | 17.6886 | 823.489 | 16.8985 | 18.2118 | 721.1923 | 712.0589 | 744.4002 |  | 561.0169 | 895.3448 | 867.1349 | 676.4763 |  | 267.3694 | 508.2267 | 342.104 | 548.9692 | 746.2231 | 859.8861 | 914.6012 | 30.0655 | 224.483 | 48.5254 | 434.6197 | 17.6594 | 48.7494 | 47.4666 | 47.4582 | 31.277 |  |  | 0.58242 | 0.67298 | -0.76829 | -1.3155 | 6.4333 | 7.1733 | 7.4141 | -3.0268 | 15.0862 | 36.8726 | 23.5653 | 0.0013553 | 0.0012682 | 1.5781 | 16.6433 | 16.5787 | 17.1018 | 17.4206 | 17.3655 | 16.3001 | 14.6446 | 16.7189 | 17.0645 | 17.3604 | 17.3894 | 17.0854 | 16.2351 | 14.4162 | 791.2432 | 234.8136 | 488.9433 | 301.1567 | 253.7073 | 663.842 | 371.9246 | 15.6904 | 15.9322 | 16.7965 | 18.5098 | 42.3702 | 60.176 |  |  |  | 537.5606 | 513.3994 | 516.9737 | 548.3808 | 104.9661 | 42.0817 | 815.2503 |  |  | 337.8087 |  |  | 17.4211 | 22.0359 | 183.332 | 16.4801 | 17.9106 | 852.3221 | 699.1828 | 531.5283 | 795.5386 | 804.5011 | 694.4101 |  | 760.19 | 813.3019 | 915.6666 | 520.6806 | 640.2225 | 824.4509 |  | 911.4008 |  |  | 338.4112 | 555.6186 | 677.5703 | [6 empty] | 521.9956 |  |  | 314.4131 |  |  | 434.5956 | 600.2841 | 609.8479 | 731.2459 | 966.3752 | 955.4583 | 478.7539 | 644.8772 | 757.8714 | 546.4884 | 624.8497 | 912.6021 | 989.4051 | 565.7146 | 733.7545 | 779.3599 | 983.4409 | 983.2679 | 466.3684 | 575.5902 | 648.2705 | 498.2962 | 653.205 | 838.7447 | 889.7856 | 1022.0153 | 532.719 | 629.2721 | 577.969 | 770.543 | 70.5783 | 0.44933 | 18.0484 | 4.7155 | -38.631 | 3.1243 | 10457.99 | 0.24 | 1.6228 | 1.5981 | -1.7075 | -2.2343 | 5.9499 | 6.2827 | 6.3873 | 66.4754 | 116.0946 | 42.7822 | 29.5489 | -3.1841 | 54.4075 | 24.1927
42810.4496 | 830 | 18.2618 | 18.4579 | 18.4601 | 18.4391 | 17.7254 | 16.3051 | 14.4672 | 16.5462 | 17.0389 | 17.1393 | 17.1377 | 16.6452 | 15.6404 | 14.271 | 14.6517 | 15.0787 | 16.2862 | 15.7346 | 17.139 | 52.0227 |  |  |  | 16.9832 | 18.8545 | 123.8264 | 646.293 | 682.7793 | 656.1249 | 17.0508 | 17.7178 | 817.5619 | 16.896 | 18.2312 | 722.7436 | 711.9896 | 737.7429 |  | 563.3284 | 898.4456 | 875.7657 | 675.7381 |  | 268.4406 | 509.8202 | 343.546 | 549.3641 | 742.3396 | 860.082 | 915.8772 | 30.3188 | 226.1082 | 49.595 | 436.5968 | 17.4226 | 48.7326 | 47.4927 | 47.4454 | 31.5717 |  |  | 1.1719 | 0.085515 | -0.49427 | -1.763 | 7.1003 | 5.9694 | 6.2754 | -2.8415 | 14.1003 | 35.6031 | 23.4546 | 0.0012847 | 0.0012551 | 1.5796 | 16.647 | 16.59 | 17.1007 | 17.4219 | 17.37 | 16.3065 | 14.6434 | 16.7175 | 17.0643 | 17.3604 | 17.3903 | 17.0933 | 16.2366 | 14.4172 | 815.4114 | 247.8422 | 509.7988 | 302.7149 | 259.1351 | 667.55 | 373.6221 | 15.6887 | 15.9475 | 16.8058 | 18.6488 | 42.7538 | 60.4748 |  |  |  | 538.6821 | 515.8234 | 519.0022 | 550.4998 | 78.5031 | 32.3716 | 816.0919 |  |  | 339.3718 |  |  | 17.4156 | 22.1371 | 186.8678 | 16.4767 | 17.9531 | 852.2567 | 698.7102 | 531.2759 | 797.2901 | 807.6787 | 695.4213 |  | 760.0152 | 819.8345 | 915.582 | 519.5799 | 639.2129 | 826.0559 |  | 911.324 |  |  | 339.4143 | 555.5417 | 677.0583 | [6 empty] | 521.1694 |  |  | 313.8985 |  |  | 435.3136 | 600.505 | 610.4468 | 729.8155 | 966.5194 | 955.0834 | 478.4958 | 643.6982 | 756.1536 | 546.9876 | 625.2888 | 911.8738 | 987.649 | 565.3309 | 732.2609 | 778.0677 | 982.1333 | 982.3112 | 467.6257 | 576.0154 | 648.2808 | 498.9888 | 653.1582 | 836.5363 | 890.2031 | 1022.9548 | 533.6638 | 629.2053 | 578.2924 | 768.1285 | 71.4086 | 0.43877 | 18.0745 | 4.6561 | -38.6669 | 3.1243 | 10463.93 | 0.24 | 2.2997 | 0.57024 | -1.371 | -2.5892 | 6.2512 | 5.7318 | 5.8769 | 66.3987 | 115.8785 | 42.6106 | 27.9714 | -5.209 | 54.411 | 24.3008
42810.4497 | 831 | 18.2437 | 18.4442 | 18.4468 | 18.4366 | 17.7101 | 16.3072 | 14.4493 | 16.5395 | 17.0223 | 17.1255 | 17.1353 | 16.6386 | 15.6335 | 14.2648 | 14.6496 | 15.0748 | 16.2878 | 15.8268 | 17.3557 | 52.4694 |  |  |  | 16.9826 | 18.9022 | 127.9306 | 645.3848 | 683.4121 | 653.7696 | 17.0608 | 17.7405 | 836.9576 | 16.8934 | 18.2652 | 725.0291 | 712.0868 | 716.0627 |  | 564.0941 | 898.1734 | 878.2578 | 674.339 |  | 269.0785 | 511.7528 | 345.748 | 549.3734 | 736.3691 | 857.2247 | 916.2503 | 30.2018 | 227.7093 | 50.1861 | 438.3504 | 17.2421 | 48.7459 | 47.5125 | 47.4284 | 31.8706 |  |  | 0.76181 | -0.42375 | -0.87737 | -0.99619 | 6.5207 | 7.4263 | 6.1157 | -2.5991 | 13.9207 | 33.494 | 22.9644 | 0.0012633 | 0.0012189 | 1.5719 | 16.6486 | 16.5898 | 17.099 | 17.4232 | 17.3688 | 16.3033 | 14.6416 | 16.7147 | 17.0604 | 17.3587 | 17.3925 | 17.0956 | 16.2404 | 14.4137 | 806.6261 | 244.2766 | 493.3639 | 300.4825 | 249.9288 | 669.225 | 374.5308 | 15.68 | 15.9481 | 16.8215 | 18.7699 | 43.0971 | 60.745 |  |  |  | 539.4096 | 515.939 | 519.1055 | 548.6796 | 71.1671 | 30.0934 | 818.9617 |  |  | 337.3927 |  |  | 17.4197 | 22.2432 | 192.7214 | 16.4846 | 17.9989 | 858.3607 | 697.1212 | 531.7227 | 800.2492 | 809.3428 | 690.0298 |  | 759.422 | 832.2736 | 916.6844 | 520.2062 | 638.5277 | 831.5043 |  | 911.9862 |  |  | 339.401 | 551.4122 | 674.5576 | [6 empty] | 521.5138 |  |  | 314.6047 |  |  | 435.8602 | 600.6824 | 610.0407 | 730.8522 | 967.8932 | 954.6264 | 478.3694 | 643.1205 | 753.9375 | 548.1781 | 625.2847 | 914.0433 | 987.7582 | 565.2934 | 731.8081 | 776.8116 | 979.1653 | 981.1674 | 468.3159 | 576.3426 | 649.2034 | 499.4176 | 653.6738 | 834.8097 | 892.4419 | 1022.799 | 534.4662 | 628.6548 | 578.8088 | 766.7922 | 67.905 | 0.42984 | 18.0978 | 4.5926 | -38.6238 | 3.1243 | 10473.04 | 0.22 | 1.8519 | -1.271 | -1.8288 | -1.9487 | 5.9831 | 6.385 | 5.7943 | 66.3837 | 115.9842 | 42.4562 | 29.4508 | -3.2261 | 54.4737 | 24.46
42810.4497 | 832 | 18.245 | 18.4361 | 18.444 | 18.4346 | 17.7124 | 16.3011 | 14.4576 | 16.5391 | 17.0259 | 17.1369 | 17.1405 | 16.638 | 15.6455 | 14.2571 | 14.6328 | 15.0635 | 16.2911 | 15.9162 | 17.5807 | 52.9085 |  |  |  | 16.9815 | 18.9429 | 124.89 | 645.3931 | 683.8485 | 653.0492 | 17.0502 | 17.7476 | 832.0781 | 16.8948 | 18.2839 | 727.4485 | 712.3485 | 707.2367 |  | 546.6133 | 887.9997 | 873.0875 | 659.6704 |  | 270.255 | 512.6953 | 347.3593 | 550.6351 | 735.8882 | 861.4601 | 917.5186 | 30.7861 | 228.9566 | 50.1611 | 439.9144 | 17.0015 | 48.7742 | 47.516 | 47.3901 | 32.1501 |  |  | 0.79467 | -0.11754 | -1.1225 | -1.307 | 7.0812 | 7.0097 | 5.9705 | -3.2069 | 14.0106 | 35.0205 | 23.3028 | 0.0012617 | 0.0012797 | 1.5618 | 16.6521 | 16.5768 | 17.0999 | 17.4102 | 17.3562 | 16.297 | 14.6431 | 16.7155 | 17.0532 | 17.3543 | 17.3926 | 17.079 | 16.2391 | 14.4055 | 776.8175 | 237.6482 | 471.7832 | 300.6614 | 243.0119 | 669.9457 | 374.9724 | 15.6721 | 15.9395 | 16.83 | 18.8862 | 43.4349 | 61.0028 |  |  |  | 540.0946 | 517.3159 | 520.1472 | 549.3697 | 73.9053 | 30.82 | 821.3816 |  |  | 344.436 |  |  | 17.429 | 22.3425 | 197.044 | 16.4856 | 18.042 | 853.4461 | 695.9753 | 533.5 | 799.4346 | 807.9377 | 682.9141 |  | 758.7099 | 836.4246 | 917.1897 | 522.751 | 638.082 | 830.3846 |  | 912.803 |  |  | 339.3439 | 547.3379 | 671.0867 | [6 empty] | 523.1507 |  |  | 314.6971 |  |  | 435.9793 | 601.0679 | 609.2088 | 737.4671 | 971.6961 | 954.464 | 478.4349 | 642.4536 | 752.5249 | 549.3459 | 625.3351 | 918.6115 | 989.4624 | 565.0583 | 733.1175 | 777.922 | 979.4473 | 983.1903 | 468.7018 | 576.2373 | 649.5114 | 499.8186 | 654.8311 | 834.3251 | 900.8686 | 1021.6435 | 534.7462 | 627.7717 | 579.5125 | 767.5096 | 71.2751 | 0.42276 | 18.1206 | 4.5231 | -38.6133 | 3.1244 | 10414.2 | 0.3 | 1.8907 | -0.66977 | -2.0698 | -2.2334 | 6.2466 | 6.215 | 5.7358 | 66.384 | 116.0761 | 42.2966 | 32.9799 | -0.75189 | 54.9452 | 24.5433
42810.4497 | 833 | 18.2337 | 18.44 | 18.4456 | 18.4232 | 17.7119 | 16.2925 | 14.4548 | 16.5358 | 17.0359 | 17.1328 | 17.1338 | 16.6364 | 15.6369 | 14.2563 | 14.6305 | 15.0727 | 16.2965 | 16.0085 | 17.8466 | 53.3586 |  |  |  | 16.9894 | 19.0074 | 124.9507 | 647.4079 | 683.348 | 657.2057 | 17.0485 | 17.7801 | 836.6682 | 16.9011 | 18.3291 | 732.4934 | 713.0868 | 739.2147 |  | 525.1244 | 876.5391 | 861.8874 | 617.7116 |  | 271.6328 | 514.6905 | 348.6047 | 553.3086 | 730.0195 | 864.2896 | 917.2123 | 31.4536 | 230.4923 | 51.798 | 441.7013 | 16.8005 | 48.8425 | 47.5167 | 47.3784 | 32.4788 |  |  | 1.1627 | -0.39484 | -1.3781 | -1.2236 | 7.055 | 6.7527 | 6.6447 | -2.8974 | 14.4997 | 35.6121 | 22.783 | 0.0011992 | 0.0011598 | 1.5592 | 16.6468 | 16.5817 | 17.095 | 17.4127 | 17.3508 | 16.3034 | 14.6345 | 16.7117 | 17.0478 | 17.3429 | 17.385 | 17.0774 | 16.2314 | 14.4113 | 758.8984 | 236.4624 | 469.416 | 297.037 | 238.683 | 670.5934 | 375.4883 | 15.6777 | 15.9513 | 16.8534 | 19.0115 | 43.7782 | 61.2732 |  |  |  | 540.815 | 519.0062 | 521.1444 | 550.7853 | 79.1559 | 38.6635 | 820.7109 |  |  | 356.2702 |  |  | 17.4249 | 22.4495 | 192.0439 | 16.4861 | 18.0908 | 858.3548 | 696.2876 | 534.1052 | 798.274 | 807.5757 | 683.1278 |  | 758.2052 | 838.4417 | 917.2491 | 523.849 | 637.6335 | 828.4388 |  | 913.5793 |  |  | 340.0096 | 546.1232 | 669.9031 | [6 empty] | 524.1039 |  |  | 315.2594 |  |  | 436.1412 | 601.7251 | 608.4196 | 744.0766 | 973.5956 | 955.0917 | 478.7027 | 642.4596 | 753.6575 | 550.315 | 625.7175 | 918.7982 | 989.5331 | 565.3424 | 735.6581 | 779.331 | 980.2275 | 982.6409 | 468.9365 | 575.8783 | 650.8344 | 500.1192 | 656.0506 | 837.7377 | 905.5858 | 1019.4464 | 534.7799 | 627.9659 | 580.348 | 769.7917 | 69.9305 | 0.41068 | 18.1431 | 4.4595 | -38.5804 | 3.1244 | 10373.33 | 0.34 | 2.292 | -1.2291 | -2.2963 | -2.1637 | 6.2428 | 6.1076 | 6.0585 | 66.2384 | 116.0444 | 42.1768 | 35.1662 | -0.39965 | 56.2917 | 24.612
42810.4497 | 834 | 18.2368 | 18.4364 | 18.4518 | 18.426 | 17.7123 | 16.2972 | 14.4647 | 16.5372 | 17.0395 | 17.1383 | 17.1374 | 16.6425 | 15.6405 | 14.2647 | 14.6278 | 15.0829 | 16.3056 | 16.1109 | 18.1503 | 53.8096 |  |  |  | 16.9914 | 19.0631 | 127.8012 | 648.8223 | 683.0506 | 662.1434 | 17.0391 | 17.81 | 837.4297 | 16.8967 | 18.3625 | 740.1824 | 714.7718 | 731.0709 |  | 516.2943 | 872.3342 | 861.0074 | 609.8091 |  | 271.5701 | 515.8207 | 349.3597 | 554.7197 | 731.8698 | 865.5914 | 916.4743 | 31.2639 | 231.7747 | 53.2251 | 443.2026 | 16.6159 | 48.8846 | 47.5206 | 47.3596 | 32.7862 |  |  | 1.2763 | -0.67346 | -1.2263 | -1.052 | 7.4703 | 6.1488 | 6.3043 | -3.2864 | 14.0171 | 33.704 | 23.4258 | 0.0011845 | 0.0012518 | 1.554 | 16.6556 | 16.5825 | 17.091 | 17.4217 | 17.3589 | 16.2974 | 14.6326 | 16.7067 | 17.0471 | 17.3503 | 17.3894 | 17.0867 | 16.2282 | 14.4126 | 747.8817 | 234.9309 | 508.8096 | 315.2777 | 251.3357 | 671.2007 | 376.7618 | 15.6737 | 15.9574 | 16.8673 | 19.1442 | 44.145 | 61.5565 |  |  |  | 541.7677 | 522.2892 | 522.6956 | 555.2856 | 80.8668 | 37.7586 | 820.0995 |  |  | 360.0624 |  |  | 17.415 | 22.5484 | 195.6452 | 16.4869 | 18.1252 | 853.1429 | 695.5857 | 534.4314 | 796.8544 | 805.8494 | 683.7218 |  | 757.8085 | 836.3551 | 917.2966 | 523.7615 | 637.0472 | 828.0881 |  | 914.1662 |  |  | 341.2156 | 549.0576 | 670.179 | [6 empty] | 524.1153 |  |  | 316.217 |  |  | 436.7231 | 602.107 | 610.339 | 747.336 | 974.8372 | 957.2608 | 479.0554 | 642.5393 | 757.053 | 551.408 | 627.113 | 918.7589 | 989.5008 | 565.7645 | 738.6989 | 780.3378 | 978.8453 | 982.2111 | 468.9069 | 575.8615 | 652.7258 | 500.8839 | 657.1122 | 839.9242 | 903.9294 | 1016.3236 | 534.9232 | 628.032 | 581.8016 | 773.668 | 64.8193 | 0.40229 | 18.1653 | 4.3961 | -38.6109 | 3.1243 | 10365.14 | 0.32 | 2.4078 | -1.6064 | -2.1677 | -2.0078 | 6.4276 | 5.8314 | 5.9047 | 66.1122 | 116.1219 | 42.0625 | 36.5736 | -4.5562 | 56.9255 | 24.6301
42810.4497 | 835 | 18.2432 | 18.4334 | 18.4537 | 18.4337 | 17.7131 | 16.3052 | 14.4684 | 16.5473 | 17.0369 | 17.1425 | 17.1376 | 16.6411 | 15.6372 | 14.2696 | 14.6296 | 15.0759 | 16.3152 | 16.2002 | 18.4177 | 54.2719 |  |  |  | 16.994 | 19.1144 | 135.0168 | 650.3853 | 684.3913 | 665.9224 | 17.0344 | 17.8341 | 837.2006 | 16.8986 | 18.3986 | 747.8063 | 716.8599 | 744.0702 |  | 521.7393 | 873.7993 | 859.6363 | 603.6594 |  | 271.9054 | 517.0287 | 349.9455 | 555.8651 | 735.6919 | 867.4754 | 915.1182 | 30.9572 | 233.1861 | 54.1861 | 444.5996 | 16.4497 | 48.8995 | 47.5264 | 47.3429 | 33.0781 |  |  | -0.046437 | -0.3863 | -1.0141 | -1.6106 | 7.1943 | 5.8676 | 6.2675 | -3.8706 | 14.0945 | 35.9251 | 23.9297 | 0.0011302 | 0.0011861 | 1.5543 | 16.6524 | 16.5731 | 17.0935 | 17.4108 | 17.3533 | 16.2936 | 14.6349 | 16.698 | 17.0427 | 17.3481 | 17.3847 | 17.0848 | 16.2268 | 14.4005 | 757.5262 | 221.3032 | 529.8932 | 318.8738 | 265.9924 | 672.0505 | 378.2058 | 15.6675 | 15.9601 | 16.888 | 19.2903 | 44.5124 | 61.8363 |  |  |  | 542.7408 | 524.789 | 525.7456 | 554.6104 | 75.7822 | 36.8304 | 818.5185 |  |  | 366.4652 |  |  | 17.4115 | 22.6447 | 203.7595 | 16.4888 | 18.1749 | 854.261 | 695.5393 | 534.9953 | 793.6588 | 802.1801 | 687.0496 |  | 757.4488 | 831.4686 | 916.5881 | 524.3839 | 636.4836 | 825.8291 |  | 914.0353 |  |  | 342.6933 | 553.2764 | 671.0904 | [6 empty] | 524.6693 |  |  | 317.9317 |  |  | 436.6163 | 602.4329 | 611.9733 | 746.5328 | 973.7511 | 957.5302 | 479.3371 | 643.7671 | 759.2811 | 552.5526 | 627.7977 | 914.3253 | 989.5725 | 566.4419 | 744.7198 | 783.3623 | 977.7833 | 984.8053 | 469.5608 | 575.6902 | 653.9294 | 501.5432 | 657.8949 | 841.4996 | 904.0073 | 1013.5464 | 535.0291 | 629.5932 | 582.6858 | 774.8003 | 70.0226 | 0.39082 | 18.1871 | 4.3374 | -38.5676 | 3.1244 | 10380.08 | 0.26 | -0.4602 | -1.2176 | -1.9727 | -2.4861 | 6.3129 | 5.7012 | 5.8923 | 65.9204 | 115.9671 | 41.9333 | 35.759 | -6.6481 | 57.6124 | 24.7956
42810.4497 | 836 | 18.2347 | 18.4441 | 18.4486 | 18.4313 | 17.7161 | 16.2997 | 14.4724 | 16.5397 | 17.0423 | 17.1372 | 17.1354 | 16.6483 | 15.6439 | 14.2656 | 14.6279 | 15.0725 | 16.3226 | 16.3138 | 18.6577 | 54.7482 |  |  |  | 16.9953 | 19.1828 | 129.2747 | 649.9317 | 686.2707 | 662.4234 | 17.0286 | 17.8537 | 835.7596 | 16.8937 | 18.4308 | 752.1054 | 718.8142 | 753.6837 |  | 549.8666 | 887.6924 | 869.263 | 605.0621 |  | 273.6215 | 518.5209 | 350.2578 | 561.3178 | 742.5104 | 874.7946 | 915.4701 | 30.5712 | 234.7317 | 54.4517 | 446.1011 | 16.3284 | 48.8834 | 47.5317 | 47.3243 | 33.3549 |  |  | 0.5982 | -0.29627 | -0.47982 | -1.2282 | 7.074 | 6.1179 | 6.6427 | -3.3199 | 14.3158 | 36.0489 | 24.5837 | 0.0012206 | 0.0011532 | 1.5455 | 16.663 | 16.5739 | 17.1012 | 17.409 | 17.3498 | 16.2952 | 14.6368 | 16.7088 | 17.0535 | 17.3446 | 17.3875 | 17.0876 | 16.2246 | 14.4071 | 771.162 | 208.2239 | 539.6922 | 311.5913 | 259.2161 | 673.2364 | 379.6479 | 15.6611 | 15.9711 | 16.9073 | 19.4131 | 44.8559 | 62.0983 |  |  |  | 543.5364 | 526.1905 | 528.057 | 553.7354 | 81.5502 | 44.0661 | 815.8535 |  |  | 369.0848 |  |  | 17.4134 | 22.7544 | 208.8752 | 16.4836 | 18.2283 | 858.298 | 695.9235 | 535.7823 | 796.4028 | 805.0049 | 688.6066 |  | 756.9688 | 829.6018 | 916.3158 | 525.1061 | 636.1386 | 824.4168 |  | 914.0908 |  |  | 344.2499 | 557.3681 | 671.8628 | [6 empty] | 525.072 |  |  | 317.5903 |  |  | 436.4523 | 602.5034 | 615.7279 | 743.794 | 973.2098 | 957.261 | 479.5728 | 644.9211 | 761.114 | 553.1438 | 629.1046 | 910.8384 | 990.523 | 566.7383 | 744.8746 | 784.9745 | 980.1966 | 983.1956 | 469.5464 | 575.4272 | 653.4353 | 501.7608 | 658.3074 | 841.1493 | 905.4912 | 1015.2908 | 535.2598 | 629.3438 | 583.595 | 775.5818 | 79.0554 | 0.3794 | 18.2088 | 4.273 | -38.6198 | 3.1243 | 10382.98 | 0.2 | 1.6486 | -1.0673 | -1.3582 | -2.173 | 6.28 | 5.8402 | 6.0855 | 65.7447 | 115.9074 | 41.8448 | 34.6032 | -7.486 | 58.0591 | 24.9401
42810.4497 | 837 | 18.2369 | 18.4365 | 18.4531 | 18.4378 | 17.7146 | 16.3029 | 14.4718 | 16.5373 | 17.0406 | 17.1379 | 17.1419 | 16.6534 | 15.6424 | 14.2657 | 14.6123 | 15.0778 | 16.3211 | 16.4193 | 18.9214 | 55.2114 |  |  |  | 16.9991 | 19.251 | 125.8943 | 647.7704 | 684.8093 | 659.9538 | 17.0346 | 17.8752 | 837.2375 | 16.8933 | 18.4676 | 756.6358 | 720.3711 | 776.1654 |  | 537.9603 | 901.7774 | 883.5858 | 598.6382 |  | 275.1534 | 520.8469 | 351.5192 | 563.4311 | 742.2768 | 878.6384 | 918.478 | 30.2634 | 236.095 | 54.782 | 447.4464 | 16.185 | 48.8617 | 47.5535 | 47.3124 | 33.6044 |  |  | 1.0477 | 0.31485 | -0.81297 | -1.169 | 6.7974 | 5.7145 | 5.2056 | -3.7234 | 14.0978 | 36.3135 | 24.257 | 0.0011992 | 0.0011483 | 1.5618 | 16.668 | 16.5822 | 17.095 | 17.4099 | 17.3525 | 16.295 | 14.6353 | 16.7093 | 17.0514 | 17.3467 | 17.3821 | 17.0856 | 16.2261 | 14.4027 | 781.1654 | 212.8229 | 553.6614 | 316.7199 | 257.0859 | 674.3329 | 381.3843 | 15.6654 | 15.9832 | 16.9282 | 19.5406 | 45.2063 | 62.3568 |  |  |  | 544.0936 | 525.9481 | 527.889 | 550.6773 | 76.0693 | 41.3767 | 818.2893 |  |  | 364.1526 |  |  | 17.414 | 22.8544 | 199.7978 | 16.4825 | 18.2818 | 874.0969 | 698.9632 | 536.8675 | 805.154 | 812.6786 | 696.8627 |  | 757.1834 | 834.0314 | 916.988 | 526.5163 | 635.8496 | 825.4148 |  | 915.1925 |  |  | 345.4488 | 563.2963 | 675.2899 | [6 empty] | 525.5505 |  |  | 318.1899 |  |  | 436.3124 | 602.7974 | 618.1171 | 742.6834 | 974.638 | 959.7858 | 480.1007 | 645.6292 | 761.0993 | 553.5319 | 629.389 | 912.7926 | 992.1409 | 567.6428 | 742.0296 | 785.055 | 979.556 | 984.2987 | 469.6807 | 575.3167 | 652.0103 | 502.0815 | 659.9408 | 841.8172 | 898.9161 | 1017.0324 | 535.4811 | 628.9422 | 584.3004 | 777.4598 | 71.7425 | 0.36946 | 18.2306 | 4.219 | -38.6438 | 3.1243 | 10403.83 | 0.26 | 2.1789 | 1.1019 | -1.7706 | -2.1232 | 6.1663 | 5.6538 | 5.3962 | 65.5746 | 116.0598 | 41.7483 | 33.8247 | -8.7352 | 58.6263 | 25.1095
42810.4497 | 838 | 18.212 | 18.4292 | 18.4402 | 18.4189 | 17.7052 | 16.292 | 14.4599 | 16.5377 | 17.0232 | 17.1293 | 17.1317 | 16.6296 | 15.6365 | 14.2526 | 14.6069 | 15.0835 | 16.3282 | 16.5222 | 19.1705 | 55.6714 |  |  |  | 17.004 | 19.3251 | 127.1911 | 647.1705 | 685.3407 | 659.4215 | 17.0221 | 17.9205 | 847.8617 | 16.905 | 18.5191 | 758.4388 | 721.5175 | 737.2641 |  | 524.8235 | 898.2026 | 879.6788 | 578.4006 |  | 276.6515 | 522.8987 | 351.8409 | 564.1751 | 743.4844 | 881.9147 | 919.5234 | 29.9034 | 237.7177 | 54.7629 | 449.002 | 15.9903 | 48.8166 | 47.5573 | 47.3005 | 33.8572 |  |  | 0.69348 | 0.47584 | -1.1915 | -1.8281 | 6.844 | 5.5325 | 6.1203 | -3.8673 | 14.9381 | 37.7974 | 23.8481 | 0.0011746 | 0.0011845 | 1.5686 | 16.676 | 16.5785 | 17.0932 | 17.4072 | 17.3596 | 16.2954 | 14.6364 | 16.7173 | 17.0528 | 17.3506 | 17.3855 | 17.0921 | 16.2348 | 14.407 | 773.8264 | 228.6714 | 561.6916 | 326.7648 | 262.2061 | 674.8815 | 383.0469 | 15.6701 | 15.9901 | 16.9444 | 19.6754 | 45.5433 | 62.618 |  |  |  | 544.6151 | 525.5108 | 527.8775 | 549.7345 | 68.4689 | 30.6452 | 824.3191 |  |  | 367.9894 |  |  | 17.4217 | 22.9598 | 200.9959 | 16.4895 | 18.335 | 860.9303 | 700.9426 | 539.2941 | 812.2307 | 815.1042 | 699.5277 |  | 757.6171 | 844.4129 | 917.7503 | 528.7777 | 635.6567 | 829.6656 |  | 916.4543 |  |  | 346.26 | 565.8453 | 679.7922 | [6 empty] | 527.5954 |  |  | 320.2675 |  |  | 436.5508 | 602.6761 | 618.7168 | 745.5825 | 976.517 | 961.8554 | 480.6876 | 646.5318 | 761.7324 | 553.9938 | 628.8219 | 915.912 | 993.708 | 568.8829 | 741.5505 | 781.3349 | 981.0512 | 985.6622 | 469.927 | 575.4052 | 651.0035 | 502.8099 | 660.1156 | 843.5099 | 895.0106 | 1018.0982 | 535.4505 | 628.4537 | 584.7938 | 782.8197 | 72.5721 | 0.35825 | 18.2519 | 4.1679 | -38.6541 | 3.1243 | 10391.86 | 0.35 | 1.7722 | 1.3563 | -2.1462 | -2.6585 | 6.1962 | 5.5709 | 5.8594 | 65.6203 | 116.0844 | 41.6473 | 34.8071 | -9.3366 | 59.4757 | 25.2148
42810.4497 | 839 | 18.2236 | 18.4342 | 18.4416 | 18.4352 | 17.7135 | 16.312 | 14.4713 | 16.5449 | 17.0371 | 17.1383 | 17.1436 | 16.6496 | 15.6459 | 14.2615 | 14.6038 | 15.0814 | 16.3298 | 16.6239 | 19.339 | 56.0992 |  |  |  | 17.0016 | 19.3916 | 130.9178 | 648.0593 | 685.3388 | 659.4886 | 17.0239 | 17.9953 | 802.0959 | 17.0431 | 18.787 | 744.1406 | 726.2259 | 638.5391 |  | 453.3766 | 853.3186 | 845.0111 | 557.0699 |  | 277.217 | 523.0685 | 352.1587 | 563.2157 | 740.9348 | 886.7321 | 920.1754 | 29.4388 | 239.1676 | 54.5764 | 450.5641 | 15.8185 | 48.7718 | 47.5571 | 47.2797 | 34.1708 |  |  | 0.056075 | 0.036887 | -0.39965 | -1.2098 | 7.6418 | 6.3 | 6.4843 | -2.5688 | 14.2529 | 36.2417 | 24.314 | 0.0011631 | 0.0010793 | 1.5658 | 16.6772 | 16.5665 | 17.0949 | 17.4094 | 17.3574 | 16.2962 | 14.6373 | 16.7101 | 17.0528 | 17.3439 | 17.381 | 17.0948 | 16.2424 | 14.4083 | 760.8462 | 248.2 | 533.1408 | 309.4373 | 244.759 | 675.3273 | 384.0949 | 15.6491 | 15.9837 | 16.9548 | 19.8115 | 45.9044 | 62.8941 |  |  |  | 545.3013 | 525.4871 | 527.5362 | 551.6873 | 80.1778 | 39.255 | 826.6012 |  |  | 381.611 |  |  | 17.4254 | 23.0732 | 209.1342 | 16.4935 | 18.3942 | 815.2207 | 701.4867 | 542.5911 | 817.8403 | 819.196 | 695.8066 |  | 757.6755 | 857.8507 | 918.3158 | 531.7379 | 635.6756 | 833.2527 |  | 917.8945 |  |  | 346.3275 | 565.4717 | 679.1696 | [6 empty] | 530.6121 |  |  | 321.5461 |  |  | 436.6267 | 602.2853 | 618.6079 | 746.0779 | 977.5185 | 963.9646 | 480.9784 | 647.1569 | 762.552 | 554.4302 | 628.7099 | 915.9131 | 995.8174 | 570.0167 | 742.5034 | 782.2854 | 983.5742 | 986.409 | 470.2143 | 575.33 | 652.1165 | 503.3672 | 660.3803 | 843.177 | 890.7254 | 1015.4919 | 535.1343 | 628.4696 | 585.0097 | 779.7988 | 73.5077 | 0.34993 | 18.2712 | 4.1212 | -38.5884 | 3.1243 | 10344.25 | 0.26 | 0.50397 | 0.37768 | -1.2431 | -2.1629 | 6.561 | 5.9572 | 6.0437 | 65.7398 | 115.9436 | 41.5688 | 36.385 | -5.9805 | 61.2574 | 25.2648
42810.4498 | 840 | 18.2121 | 18.4239 | 18.4428 | 18.4189 | 17.7059 | 16.293 | 14.4657 | 16.5446 | 17.0382 | 17.1349 | 17.1369 | 16.6362 | 15.642 | 14.259 | 14.6056 | 15.0864 | 16.3439 | 16.733 | 19.4847 | 56.5248 |  |  |  | 17.0034 | 19.4712 | 128.5603 | 644.8831 | 684.5108 | 654.7513 | 17.0362 | 18.1291 | 807.1843 | 17.2833 | 19.4049 | 746.5266 | 723.2584 | 632.3051 |  | 455.679 | 825.4647 | 818.2212 | 538.4552 |  | 277.3456 | 524.8381 | 353.728 | 563.7342 | 740.1257 | 887.0302 | 920.5871 | 29.0882 | 240.6272 | 54.0834 | 452.1977 | 15.6451 | 48.7395 | 47.5597 | 47.2574 | 34.4751 |  |  | 0.19144 | -0.018313 | -0.949 | -1.332 | 6.1613 | 5.9648 | 6.7478 | -3.2371 | 14.6413 | 37.2368 | 25.7369 | 0.0011943 | 0.0012173 | 1.5607 | 16.6715 | 16.5657 | 17.0812 | 17.4027 | 17.3484 | 16.2871 | 14.6324 | 16.6986 | 17.0506 | 17.345 | 17.3763 | 17.0783 | 16.2282 | 14.4068 | 759.2134 | 269.9338 | 521.3001 | 305.9586 | 237.1069 | 675.6127 | 385.2167 | 15.6626 | 15.9965 | 16.9792 | 19.9485 | 46.269 | 63.1574 |  |  |  | 546.0308 | 526.4535 | 528.1241 | 553.2558 | 67.4377 | 33.4275 | 828.8625 |  |  | 380.7592 |  |  | 17.4268 | 23.1806 | 205.2244 | 16.4896 | 18.4494 | 810.6718 | 703.7173 | 545.4177 | 821.7962 | 821.0511 | 698.1228 |  | 757.8854 | 870.6248 | 918.7516 | 534.1119 | 635.7125 | 835.708 |  | 919.6656 |  |  | 346.8219 | 566.7953 | 680.6437 | [6 empty] | 533.5448 |  |  | 322.3139 |  |  | 436.8216 | 602.3859 | 618.7596 | 742.4271 | 982.2019 | 964.5845 | 481.3039 | 647.6382 | 761.1538 | 554.9333 | 628.9142 | 914.2598 | 997.3613 | 571.0148 | 742.8246 | 784.9923 | 981.0389 | 984.4679 | 469.8936 | 574.9787 | 651.5056 | 504.1014 | 660.3194 | 839.1775 | 889.3329 | 1010.2961 | 534.5175 | 628.4507 | 585.8692 | 775.8083 | 66.6124 | 0.33655 | 18.2755 | 4.0753 | -38.6305 | 3.1243 | 10321.44 | 0.27 | 0.92882 | -0.26641 | -1.9178 | -2.272 | 5.892 | 5.7973 | 6.1661 | 65.7334 | 115.7681 | 41.5102 | 36.6534 | -4.4678 | 61.0232 | 25.3323
42810.4498 | 841 | 18.2056 | 18.4158 | 18.4373 | 18.4111 | 17.7008 | 16.2861 | 14.4568 | 16.5382 | 17.0272 | 17.1289 | 17.1292 | 16.6332 | 15.6382 | 14.2557 | 14.5942 | 15.0857 | 16.3483 | 16.8375 | 19.6371 | 56.9427 |  |  |  | 17.0017 | 19.5474 | 129.0342 | 641.5294 | 684.9257 | 652.1267 | 17.5676 | 18.2469 | 817.5976 | 17.3562 | 19.468 | 750.8925 | 725.8755 | 635.5518 |  | 457.153 | 831.1442 | 816.2646 | 527.4029 |  | 278.4184 | 526.4837 | 355.6804 | 565.5448 | 742.4652 | 889.6946 | 923.087 | 28.9371 | 242.1939 | 53.1847 | 454.0989 | 15.5142 | 48.7147 | 47.5701 | 47.2325 | 34.7642 |  |  | 0.51211 | 0.004687 | -0.98908 | -1.5725 | 5.6553 | 6.2605 | 6.1866 | -3.6899 | 14.5835 | 37.3031 | 25.4981 | 0.0011319 | 0.0012009 | 1.557 | 16.6779 | 16.566 | 17.0796 | 17.4003 | 17.342 | 16.2832 | 14.6239 | 16.6974 | 17.0484 | 17.3444 | 17.3729 | 17.0798 | 16.2274 | 14.4034 | 743.8257 | 269.6534 | 517.294 | 304.4182 | 236.972 | 675.3928 | 386.3189 | 15.6551 | 16.0028 | 16.9924 | 20.0856 | 46.6028 | 63.3991 |  |  |  | 546.6313 | 527.4103 | 529.2482 | 553.2157 | 67.9095 | 37.37 | 830.3322 |  |  | 374.431 |  |  | 17.4263 | 23.3007 | 205.6752 | 16.4892 | 18.5099 | 822.8265 | 704.5605 | 547.452 | 816.8607 | 815.8781 | 698.6596 |  | 758.1015 | 862.6468 | 919.4062 | 535.9089 | 635.7254 | 834.461 |  | 921.3359 |  |  | 346.7261 | 566.4519 | 682.1636 | [6 empty] | 535.9832 |  |  | 323.5158 |  |  | 437.2139 | 602.6012 | 618.935 | 742.0863 | 985.5027 | 965.6987 | 481.7847 | 648.0808 | 761.5689 | 555.2097 | 629.1044 | 914.1894 | 998.843 | 571.7575 | 744.7274 | 785.7106 | 981.6714 | 982.4679 | 469.4232 | 574.6947 | 649.6055 | 505.4735 | 660.6616 | 839.8092 | 889.5135 | 1008.7466 | 534.22 | 627.1499 | 587.1706 | 773.5555 | 66.4643 | 0.32376 | 18.2757 | 4.0394 | -38.6405 | 3.1244 | 10302.9 | 0.22 | 1.517 | 0.13491 | -1.9599 | -2.4712 | 5.6514 | 5.9461 | 5.9109 | 65.7782 | 116.2595 | 41.4628 | 38.2961 | -3.8287 | 61.9924 | 25.4251
42810.4498 | 842 | 18.199 | 18.4083 | 18.4322 | 18.4204 | 17.6963 | 16.2947 | 14.4588 | 16.5306 | 17.0202 | 17.1297 | 17.1306 | 16.6321 | 15.6341 | 14.2629 | 14.5901 | 15.0892 | 16.3504 | 16.9526 | 19.8712 | 57.3716 |  |  |  | 17.0049 | 19.6336 | 129.289 | 641.3211 | 686.3039 | 654.147 | 28.7729 | 18.6755 | 819.1483 | 19.6808 | 19.4063 | 756.155 | 730.6746 | 641.9153 |  | 452.9125 | 842.3381 | 823.3554 | 541.672 |  | 279.1855 | 526.9648 | 357.2439 | 564.6451 | 737.0295 | 882.978 | 922.572 | 28.5721 | 243.4552 | 52.0717 | 455.6589 | 15.403 | 48.6897 | 47.5549 | 47.1997 | 35.0701 |  |  | 0.023875 | 0.39896 | -1.2184 | -1.4936 | 6.5372 | 4.6007 | 5.9731 | -3.3561 | 15.2798 | 36.5638 | 25.1754 | 0.0010957 | 0.0011335 | 1.5619 | 16.6857 | 16.566 | 17.0842 | 17.4039 | 17.3456 | 16.2921 | 14.635 | 16.7101 | 17.0544 | 17.3573 | 17.3921 | 17.0841 | 16.234 | 14.4173 | 738.0309 | 348.8106 | 534.5178 | 309.3458 | 233.816 | 675.2614 | 387.5785 | 15.6578 | 16.004 | 17.0137 | 20.2107 | 46.9395 | 63.6442 |  |  |  | 547.0833 | 526.3182 | 528.7767 | 551.159 | 68.3855 | 32.8658 | 826.6034 |  |  | 369.1937 |  |  | 17.4289 | 23.4046 | 206.817 | 16.4913 | 18.5732 | 820.0172 | 704.0551 | 549.1309 | 810.5042 | 810.8356 | 694.4904 |  | 758.0334 | 840.1236 | 919.4592 | 538.3772 | 635.8849 | 827.4866 |  | 921.7805 |  |  | 346.5423 | 563.0581 | 681.2525 | [6 empty] | 537.9173 |  |  | 325.0534 |  |  | 437.7361 | 602.7466 | 620.4505 | 742.0403 | 985.6426 | 965.7131 | 481.9846 | 648.2948 | 762.3234 | 555.3865 | 630.2618 | 913.6273 | 998.2698 | 572.2473 | 743.0171 | 787.3779 | 985.9403 | 983.2103 | 469.655 | 574.7417 | 648.5006 | 506.413 | 661.8532 | 842.5341 | 891.4206 | 1008.4865 | 534.8018 | 626.4076 | 588.5539 | 775.2909 | 71.1175 | 0.31135 | 18.2766 | 3.9943 | -38.6692 | 3.1243 | 10300.42 | 0.21 | 0.32791 | 1.2451 | -2.1759 | -2.4092 | 6.0585 | 5.0825 | 5.7912 | 65.8752 | 116.907 | 41.4259 | 38.9 | -5.5203 | 62.8225 | 25.5513
42810.4498 | 843 | 18.1916 | 18.4072 | 18.4305 | 18.4271 | 17.6957 | 16.3026 | 14.4641 | 16.532 | 17.0319 | 17.1364 | 17.1352 | 16.6386 | 15.6348 | 14.2692 | 14.5869 | 15.0942 | 16.3639 | 17.0685 | 20.168 | 57.8182 |  |  |  | 17.016 | 19.7203 | 133.2417 | 644.9182 | 689.2172 | 660.5037 | 39.7526 | 45.4881 | 812.2349 | 25.5756 | 19.0419 | 764.6642 | 727.8971 | 670.1974 |  | 451.0453 | 859.3617 | 838.8127 | 559.949 |  | 279.5859 | 528.5981 | 357.6406 | 562.8087 | 731.875 | 877.1794 | 925.6663 | 28.2217 | 245.031 | 50.806 | 457.4188 | 15.3144 | 48.6762 | 47.558 | 47.1757 | 35.3667 |  |  | -0.095721 | -0.38893 | -0.95951 | -0.90682 | 6.9544 | 6.2349 | 6.4521 | -1.9906 | 13.3867 | 35.769 | 26.6807 | 0.0011368 | 0.001053 | 1.568 | 16.6806 | 16.5594 | 17.0803 | 17.3981 | 17.3452 | 16.2922 | 14.6207 | 16.7047 | 17.0381 | 17.3478 | 17.3899 | 17.0776 | 16.2209 | 14.4147 | 740.2203 | 408.1045 | 521.5027 | 305.4341 | 234.3088 | 675.424 | 388.4882 | 15.6545 | 16.02 | 17.0326 | 20.3501 | 47.2909 | 63.8942 |  |  |  | 547.5834 | 526.9822 | 530.2521 | 550.8127 | 73.4353 | 39.6797 | 822.4667 |  |  | 366.2476 |  |  | 17.4297 | 23.5062 | 212.3994 | 16.4916 | 18.6313 | 833.2431 | 704.3574 | 550.2175 | 807.6985 | 808.0491 | 693.417 |  | 757.9495 | 831.2048 | 919.3868 | 539.8866 | 635.9532 | 826.7773 |  | 921.7803 |  |  | 347.114 | 560.7066 | 680.2139 | [6 empty] | 539.2007 |  |  | 326.8285 |  |  | 438.3485 | 603.2415 | 623.0634 | 739.7474 | 987.1387 | 966.0408 | 482.3837 | 647.7897 | 760.9832 | 555.6874 | 631.8291 | 914.132 | 996.3475 | 572.2936 | 741.3222 | 786.8748 | 988.1639 | 985.4305 | 470.284 | 575.0119 | 649.5346 | 507.0062 | 663.3061 | 844.8539 | 897.092 | 1008.461 | 535.186 | 626.6398 | 589.9738 | 776.9063 | 76.6055 | 0.29686 | 18.2765 | 3.9522 | -38.6028 | 3.1242 | 10293.4 | 0.22 | -0.65882 | -1.2306 | -1.9329 | -1.8791 | 6.2332 | 5.9019 | 6.0038 | 65.8818 | 117.1249 | 41.3975 | 38.7062 | -3.9135 | 61.6031 | 25.6374
42810.4498 | 844 | 18.189 | 18.4068 | 18.4265 | 18.4229 | 17.6911 | 16.2896 | 14.4618 | 16.5305 | 17.0349 | 17.1287 | 17.1192 | 16.6368 | 15.633 | 14.2653 | 14.5819 | 15.1024 | 16.3718 | 17.189 | 20.449 | 58.2579 |  |  |  | 17.0172 | 19.8221 | 135.2108 | 649.7435 | 691.7032 | 665.7433 | 27.7874 | 53.5012 | 806.3152 | 48.4528 | 25.6366 | 764.9576 | 728.9871 | 665.1369 |  | 448.1467 | 853.9486 | 842.7259 | 556.8393 |  | 279.9057 | 530.4897 | 358.1594 | 561.0807 | 733.5431 | 873.4097 | 925.4076 | 27.7763 | 246.3369 | 49.7886 | 459.1002 | 15.2271 | 48.6637 | 47.5629 | 47.1593 | 35.6656 |  |  | 0.084987 | -0.061025 | -0.87146 | -1.535 | 5.61 | 6.1271 | 6.5737 | -3.7799 | 14.6335 | 35.6459 | 26.6944 | 0.001058 | 0.0010908 | 1.5678 | 16.6822 | 16.5584 | 17.0784 | 17.3969 | 17.3456 | 16.2832 | 14.6273 | 16.7062 | 17.0434 | 17.3398 | 17.386 | 17.0745 | 16.2292 | 14.4027 | 744.1121 | 400.2585 | 550.0948 | 307.8279 | 238.6343 | 675.8161 | 389.8263 | 15.6459 | 16.016 | 17.0461 | 20.4988 | 47.6674 | 64.1806 |  |  |  | 548.4008 | 530.7758 | 532.9756 | 554.738 | 67.9357 | 36.6264 | 820.1242 |  |  | 365.294 |  |  | 17.4327 | 23.6177 | 213.7011 | 16.4978 | 18.6923 | 836.1578 | 704.3183 | 551.1322 | 803.0769 | 803.4509 | 695.9565 |  | 758.1842 | 826.1802 | 918.6898 | 540.8142 | 635.9487 | 822.8243 |  | 921.27 |  |  | 348.3951 | 560.4897 | 680.8387 | [6 empty] | 540.1238 |  |  | 328.9295 |  |  | 438.59 | 604.084 | 625.898 | 737.4716 | 987.8302 | 965.5772 | 482.5581 | 647.146 | 759.057 | 556.4577 | 633.2859 | 912.4218 | 993.8534 | 572.126 | 739.6942 | 787.4831 | 988.2184 | 987.7201 | 470.3511 | 575.2109 | 652.7214 | 508.0069 | 664.2732 | 846.6595 | 902.4954 | 1009.1064 | 535.1962 | 627.0566 | 590.996 | 776.9011 | 66.4027 | 0.2805 | 18.2768 | 3.912 | -38.5349 | 3.1242 | 10256.55 | 0.31 | 0.62252 | -0.48804 | -1.8443 | -2.4477 | 5.5891 | 5.8411 | 6.0502 | 65.8762 | 116.9772 | 41.3708 | 38.3933 | -6.8536 | 61.9681 | 25.6537
42810.4498 | 845 | 18.1865 | 18.4082 | 18.4317 | 18.4253 | 17.698 | 16.301 | 14.4687 | 16.5322 | 17.0318 | 17.1347 | 17.1364 | 16.6456 | 15.6392 | 14.2625 | 14.5759 | 15.1031 | 16.3758 | 17.3046 | 20.6983 | 58.6924 |  |  |  | 17.0111 | 19.9186 | 134.2134 | 650.3212 | 692.8817 | 664.1685 | 43.1044 | 44.8651 | 821.9142 | 33.2979 | 59.2954 | 763.7455 | 754.8451 | 629.599 |  | 450.6819 | 873.8471 | 858.7891 | 550.0819 |  | 280.3775 | 531.0873 | 359.2999 | 561.3074 | 739.1633 | 873.7226 | 923.5578 | 27.4508 | 247.5909 | 48.7452 | 460.753 | 15.1374 | 48.6462 | 47.5891 | 47.147 | 35.9314 |  |  | 0.054759 | -0.66426 | -1.409 | -1.8596 | 7.2968 | 6.2783 | 6.8707 | -2.6332 | 14.1632 | 35.263 | 25.4438 | 0.0010629 | 0.0010645 | 1.5636 | 16.6898 | 16.5521 | 17.0791 | 17.3978 | 17.3405 | 16.2828 | 14.6306 | 16.7073 | 17.0478 | 17.34 | 17.3818 | 17.0738 | 16.2327 | 14.4047 | 738.924 | 351.6141 | 536.7882 | 302.0798 | 228.786 | 675.7765 | 390.7892 | 15.6377 | 16.0254 | 17.0697 | 20.6375 | 48.0081 | 64.4157 |  |  |  | 549.3043 | 534.529 | 535.4 | 559.9745 | 68.9375 | 24.4786 | 816.3428 |  |  | 364.9926 |  |  | 17.4238 | 23.7241 | 214.9033 | 16.4955 | 18.7576 | 837.887 | 703.009 | 552.5636 | 799.861 | 800.7954 | 695.0717 |  | 758.1221 | 816.0734 | 918.4079 | 542.2947 | 635.9627 | 819.7942 |  | 921.0196 |  |  | 349.0723 | 558.9786 | 680.0354 | [6 empty] | 541.5992 |  |  | 331.272 |  |  | 438.767 | 605.0763 | 627.5878 | 737.5897 | 988.3643 | 964.8952 | 482.5294 | 647.1925 | 757.5575 | 557.4877 | 634.1087 | 913.8618 | 996.3251 | 572.1364 | 738.7752 | 785.6898 | 987.3794 | 989.5619 | 470.172 | 575.145 | 654.6527 | 508.8583 | 664.9771 | 846.574 | 903.1493 | 1013.1599 | 535.416 | 626.7121 | 591.6969 | 775.3708 | 70.1305 | 0.27071 | 18.277 | 3.8731 | -38.5808 | 3.1242 | 10228.68 | 0.24 | 0.49927 | -1.6107 | -2.3459 | -2.6951 | 6.3751 | 5.9135 | 6.1862 | 65.8836 | 117.142 | 41.3325 | 38.9577 | -5.2043 | 69.0088 | 25.6472
42810.4498 | 846 | 18.1906 | 18.4138 | 18.4376 | 18.4268 | 17.7048 | 16.3014 | 14.4705 | 16.5449 | 17.0396 | 17.1369 | 17.1351 | 16.6444 | 15.6453 | 14.2702 | 14.5801 | 15.1116 | 16.3817 | 17.4301 | 20.9569 | 59.1186 |  |  |  | 17.0091 | 20.0293 | 133.5084 | 649.2098 | 692.9597 | 661.6536 | 73.1359 | 88.2667 | 843.2317 | 78.0855 | 94.206 | 782.1813 | 824.9625 | 585.8878 |  | 429.8659 | 882.2567 | 851.2345 | 531.618 |  | 281.4307 | 531.2915 | 360.0111 | 564.1968 | 737.7871 | 869.194 | 921.1905 | 27.0514 | 248.8793 | 48.207 | 462.5343 | 15.0585 | 48.6181 | 47.6412 | 47.1262 | 36.2164 |  |  | 0.35046 | -0.087965 | -0.85832 | -1.2577 | 6.8861 | 6.6982 | 6.0723 | -2.9749 | 15.0323 | 37.467 | 25.3999 | 0.0011056 | 0.0010744 | 1.5623 | 16.6945 | 16.5506 | 17.0715 | 17.4012 | 17.3402 | 16.2857 | 14.6307 | 16.6986 | 17.0496 | 17.3485 | 17.3849 | 17.0814 | 16.2221 | 14.4081 | 742.9271 | 324.2699 | 507.4068 | 289.7381 | 224.2963 | 675.5485 | 391.1475 | 15.6318 | 16.0409 | 17.0969 | 20.7741 | 48.3395 | 64.6551 |  |  |  | 550.0863 | 535.7643 | 536.1401 | 559.1592 | 81.0429 | 39.8521 | 814.4542 |  |  | 365.2174 |  |  | 17.4226 | 23.8431 | 214.1146 | 16.5032 | 18.8392 | 834.4804 | 702.2908 | 554.8099 | 801.6082 | 802.3278 | 691.7733 |  | 757.8559 | 809.9797 | 919.1529 | 544.5878 | 636.1256 | 820.229 |  | 921.5643 |  |  | 349.9143 | 557.7351 | 677.4541 | [6 empty] | 543.966 |  |  | 333.4368 |  |  | 439.0756 | 605.8024 | 628.0782 | 738.9949 | 992.2471 | 966.3353 | 482.7511 | 648.0845 | 757.3502 | 558.2236 | 634.5939 | 918.2006 | 998.9257 | 572.3544 | 739.5534 | 784.9157 | 989.8868 | 990.8774 | 470.5111 | 575.2953 | 653.7261 | 509.2785 | 665.3003 | 847.0512 | 903.5414 | 1015.4176 | 535.9737 | 625.353 | 592.1926 | 774.5206 | 73.187 | 0.25922 | 18.2772 | 3.8275 | -38.5794 | 3.1242 | 10225.3 | 0.27 | 1.2614 | -0.58623 | -1.8312 | -2.2167 | 6.1809 | 6.096 | 5.8042 | 65.9016 | 117.618 | 41.3011 | 38.4434 | -1.8761 | 90.5946 | 25.7904
42810.4498 | 847 | 18.1843 | 18.4097 | 18.4318 | 18.4184 | 17.6987 | 16.289 | 14.4755 | 16.5393 | 17.0265 | 17.1374 | 17.132 | 16.6414 | 15.6429 | 14.2608 | 14.5778 | 15.1123 | 16.3962 | 17.5581 | 21.1963 | 59.5314 |  |  |  | 17.019 | 20.1447 | 132.963 | 648.1493 | 690.6575 | 660.0436 | 41.7551 | 58.4564 | 858.524 | 71.8159 | 88.3866 | 781.2468 | 810.0882 | 604.6775 |  | 389.7698 | 882.0265 | 860.2775 | 511.9586 |  | 283.4047 | 531.9697 | 360.7689 | 566.5587 | 735.3787 | 868.421 | 918.7819 | 27.269 | 250.0264 | 48.4741 | 464.2475 | 15.0087 | 48.588 | 47.6819 | 47.1172 | 36.4802 |  |  | -0.087833 | -0.044597 | -0.93388 | -1.719 | 7.3487 | 6.2231 | 6.6019 | -2.8803 | 15.3779 | 37.1434 | 27.1749 | 0.0010284 | 0.0010957 | 1.5702 | 16.7072 | 16.5541 | 17.0727 | 17.3984 | 17.3468 | 16.2944 | 14.638 | 16.6998 | 17.0521 | 17.3492 | 17.3897 | 17.0868 | 16.2332 | 14.4155 | 743.5953 | 359.3523 | 523.1438 | 301.8881 | 240.3487 | 676.2099 | 392.3979 | 15.6376 | 16.0524 | 17.1215 | 20.9161 | 48.6785 | 64.8981 |  |  |  | 550.5473 | 533.728 | 535.3138 | 553.9943 | 77.2834 | 36.7504 | 816.164 |  |  | 363.8193 |  |  | 17.4341 | 23.9574 | 212.0155 | 16.5062 | 18.9132 | 847.5543 | 703.847 | 556.9859 | 804.5985 | 804.8243 | 694.3435 |  | 757.9745 | 810.6769 | 920.3724 | 547.1831 | 636.3835 | 823.1109 |  | 922.0553 |  |  | 351.1296 | 559.6892 | 678.0572 | [6 empty] | 546.7168 |  |  | 336.2424 |  |  | 439.4172 | 606.5682 | 628.6598 | 740.4134 | 990.8806 | 967.7237 | 483.0432 | 649.4044 | 759.5814 | 558.7685 | 635.0426 | 918.6115 | 999.0882 | 572.6211 | 742.8939 | 782.024 | 995.4835 | 995.2997 | 471.0025 | 575.7562 | 653.4536 | 509.1068 | 665.4153 | 844.8534 | 904.4124 | 1018.2323 | 536.5982 | 625.4346 | 592.73 | 771.6799 | 74.2419 | 0.24637 | 18.2767 | 3.7917 | -38.6263 | 3.1241 | 10257.98 | 0.26 | -0.63093 | -0.41759 | -1.9109 | -2.5926 | 6.383 | 5.8738 | 6.05 | 65.863 | 118.1021 | 41.2801 | 38.5709 | -3.4023 | 86.3504 | 26.005
42810.4498 | 848 | 18.179 | 18.4085 | 18.4328 | 18.4183 | 17.6921 | 16.2876 | 14.4706 | 16.5367 | 17.03 | 17.1296 | 17.1331 | 16.6457 | 15.6411 | 14.2631 | 14.5775 | 15.1155 | 16.4069 | 17.6842 | 21.44 | 59.9341 |  |  |  | 17.0212 | 20.259 | 133.1014 | 644.6946 | 690.6043 | 654.8535 | 32.8165 | 44.0419 | 861.3819 | 51.0334 | 47.2887 | 783.1154 | 778.1967 | 650.7596 |  | 385.7325 | 871.8157 | 858.2972 | 495.4621 |  | 284.4133 | 533.9115 | 361.373 | 567.713 | 735.8037 | 873.2465 | 918.742 | 27.5774 | 251.5548 | 47.389 | 466.1844 | 14.9611 | 48.5655 | 47.7079 | 47.1198 | 36.7091 |  |  | -0.10755 | -0.79634 | -0.68418 | -1.2098 | 6.6101 | 5.4201 | 7.0521 | -2.6503 | 14.6799 | 35.883 | 28.3224 | 0.0011023 | 0.0010744 | 1.5647 | 16.7165 | 16.5623 | 17.0808 | 17.4041 | 17.3479 | 16.2908 | 14.6448 | 16.7188 | 17.052 | 17.3502 | 17.3849 | 17.088 | 16.2375 | 14.4094 | 754.4209 | 350.7749 | 526.5254 | 304.7604 | 227.8375 | 677.2443 | 393.4874 | 15.6223 | 16.0583 | 17.1389 | 21.0577 | 49.0294 | 65.1378 |  |  |  | 550.9402 | 532.4861 | 534.9591 | 551.8199 | 90.248 | 44.9 | 819.1111 |  |  | 366.0873 |  |  | 17.4388 | 24.0706 | 214.9847 | 16.5004 | 18.9811 | 856.3359 | 703.9797 | 558.9193 | 807.1835 | 806.9445 | 695.1439 |  | 757.9876 | 822.3292 | 921.3003 | 549.9057 | 636.7991 | 828.2544 |  | 922.5263 |  |  | 351.8571 | 563.088 | 678.3422 | [6 empty] | 549.1672 |  |  | 338.9508 |  |  | 440.0047 | 607.6886 | 630.1586 | 741.7486 | 989.65 | 968.4377 | 483.2705 | 649.9973 | 761.6763 | 560.0328 | 635.9544 | 923.7571 | 1000.2916 | 572.736 | 745.1613 | 783.2351 | 1001.166 | 998.6558 | 471.5892 | 576.4264 | 652.1397 | 509.9965 | 665.8539 | 840.3973 | 904.6002 | 1023.9354 | 536.781 | 624.9859 | 593.9978 | 773.0842 | 72.4419 | 0.23701 | 18.2768 | 3.7513 | -38.6455 | 3.1242 | 10269.03 | 0.36 | -0.69622 | -1.7667 | -1.6376 | -2.1775 | 6.0665 | 5.4934 | 6.266 | 65.8444 | 118.1624 | 41.287 | 37.6841 | -3.584 | 77.1272 | 26.1262
42810.4499 | 849 | 18.1676 | 18.3966 | 18.4212 | 18.4075 | 17.6813 | 16.2882 | 14.471 | 16.5224 | 17.0193 | 17.1232 | 17.1245 | 16.6315 | 15.6326 | 14.2577 | 14.5563 | 15.123 | 16.4 | 17.786 | 21.5894 | 60.3191 |  |  |  | 17.009 | 20.3704 | 143.4716 | 644.2305 | 692.0309 | 656.3878 | 38.472 | 43.1489 | 847.6008 | 39.2512 | 38.8262 | 778.9588 | 772.475 | 643.3942 |  | 384.6801 | 867.509 | 851.4305 | 504.6514 |  | 285.0585 | 535.3653 | 361.893 | 567.2044 | 732.6493 | 866.4104 | 916.4816 | 28.1204 | 252.8594 | 46.8139 | 467.8604 | 14.9276 | 48.5274 | 47.736 | 47.1111 | 36.8674 |  |  | 0.090903 | -0.26605 | -0.55473 | -0.71889 | 7.1824 | 5.5785 | 6.4646 | -3.2535 | 15.6394 | 38.4436 | 27.5141 | 0.0010267 | 0.0010054 | 1.5716 | 16.7101 | 16.5579 | 17.0677 | 17.3931 | 17.3456 | 16.2866 | 14.628 | 16.7023 | 17.0487 | 17.3492 | 17.386 | 17.0822 | 16.2247 | 14.4057 | 771.0918 | 409.93 | 552.3482 | 305.1164 | 228.7626 | 678.9068 | 395.427 | 15.6224 | 16.0616 | 17.1661 | 21.2093 | 49.3939 | 65.3929 |  |  |  | 551.3176 | 531.2 | 534.5625 | 549.2237 | 83.8633 | 44.9825 | 821.2265 |  |  | 375.4635 |  |  | 17.4361 | 24.1801 | 223.2618 | 16.4974 | 19.0548 | 841.9981 | 704.9696 | 560.4374 | 806.127 | 805.1742 | 695.9365 |  | 757.9401 | 830.4548 | 921.205 | 552.1814 | 637.2381 | 833.2386 |  | 923.1323 |  |  | 352.5301 | 562.9668 | 678.0574 | [6 empty] | 550.8975 |  |  | 340.2294 |  |  | 440.8696 | 608.0329 | 630.3769 | 741.961 | 992.7315 | 968.8795 | 483.4881 | 650.9069 | 761.6159 | 560.1929 | 636.2855 | 927.1784 | 1000.0181 | 572.905 | 746.0922 | 782.2636 | 1002.6628 | 1000.3537 | 472.0807 | 576.4816 | 650.9067 | 511.7009 | 666.9601 | 841.3559 | 907.0723 | 1024.1994 | 536.665 | 624.6258 | 595.2016 | 774.7893 | 76.0961 | 0.2232 | 18.2766 | 3.7254 | -38.569 | 3.1242 | 10294.86 | 0.24 | 0.6406 | -1.0221 | -1.4759 | -1.6801 | 6.3048 | 5.5564 | 5.9815 | 65.8092 | 117.8972 | 41.3111 | 36.341 | -6.1068 | 75.2173 | 26.2567
42810.4499 | 850 | 18.1655 | 18.3993 | 18.4187 | 18.4106 | 17.6905 | 16.2912 | 14.4749 | 16.5254 | 17.022 | 17.1333 | 17.1252 | 16.6329 | 15.6425 | 14.2563 | 14.5624 | 15.1331 | 16.4148 | 17.9339 | 22.0332 | 60.7651 |  |  |  | 17.0192 | 20.4955 | 141.8928 | 649.7331 | 693.3766 | 665.0044 | 73.9309 | 61.369 | 854.0982 | 44.2088 | 42.4588 | 794.1719 | 774.825 | 645.5421 |  | 379.3304 | 874.9542 | 863.2948 | 512.5798 |  | 286.2124 | 536.7535 | 362.5742 | 567.6768 | 730.9144 | 861.7144 | 915.7334 | 28.7655 | 254.1949 | 47.0551 | 469.622 | 14.8954 | 48.5005 | 47.748 | 47.1022 | 37.1402 |  |  | 0.13427 | 0.063827 | -0.69009 | -0.97976 | 6.8223 | 6.3361 | 6.4548 | -2.8632 | 14.0824 | 36.3966 | 26.6605 | 0.0010333 | 0.00098075 | 1.5775 | 16.7229 | 16.5541 | 17.0634 | 17.3919 | 17.3421 | 16.2795 | 14.6244 | 16.7065 | 17.0407 | 17.343 | 17.3856 | 17.0775 | 16.2344 | 14.4054 | 771.0514 | 406.2781 | 538.5739 | 303.732 | 229.6936 | 680.002 | 396.8683 | 15.6177 | 16.0804 | 17.1891 | 21.3527 | 49.7328 | 65.6257 |  |  |  | 551.8216 | 531.7448 | 534.5275 | 554.4284 | 71.3947 | 30.3866 | 818.9298 |  |  | 379.6054 |  |  | 17.4328 | 24.2905 | 224.2028 | 16.4984 | 19.1307 | 848.9507 | 706.2207 | 561.2029 | 802.763 | 801.5691 | 697.7408 |  | 758.1083 | 826.8729 | 920.9544 | 552.9046 | 637.4521 | 834.8064 |  | 924.0565 |  |  | 353.7842 | 561.1709 | 678.6425 | [6 empty] | 551.8267 |  |  | 340.8802 |  |  | 441.0399 | 608.8482 | 629.7266 | 745.8017 | 994.6944 | 969.4812 | 483.9672 | 652.0625 | 760.9498 | 560.6717 | 636.1498 | 930.7016 | 1000.6567 | 573.5367 | 745.9588 | 782.3359 | 1008.4944 | 999.2798 | 472.4788 | 576.8112 | 654.3842 | 512.3969 | 666.9918 | 843.4558 | 911.0494 | 1025.1424 | 536.6509 | 627.2451 | 595.9498 | 778.8202 | 72.9836 | 0.21868 | 18.2767 | 3.6965 | -38.5666 | 3.1242 | 10292.04 | 0.24 | 0.78216 | 0.50106 | -1.6475 | -1.9631 | 6.132 | 5.9095 | 5.9646 | 65.8056 | 117.8929 | 41.3336 | 36.6819 | -4.3181 | 75.6737 | 26.1903
42810.4499 | 851 | 18.1624 | 18.4047 | 18.4275 | 18.4066 | 17.69 | 16.2941 | 14.4814 | 16.5338 | 17.0294 | 17.1444 | 17.1283 | 16.6385 | 15.6456 | 14.2602 | 14.5535 | 15.1409 | 16.4277 | 18.0535 | 22.6518 | 61.1858 |  |  |  | 17.0239 | 20.6248 | 147.213 | 653.0454 | 693.6651 | 669.6368 | 77.7086 | 107.6461 | 856.0139 | 68.7108 | 48.6677 | 804.1768 | 762.2591 | 670.6813 |  | 388.5641 | 882.4078 | 874.6391 | 510.5768 |  | 287.6721 | 539.2301 | 362.584 | 566.5716 | 730.9924 | 857.6191 | 914.6784 | 29.1842 | 255.5596 | 47.7494 | 471.1006 | 14.8243 | 48.4936 | 47.749 | 47.0915 | 37.3841 |  |  | -0.1956 | -0.18653 | -0.96608 | -1.6066 | 7.2114 | 6.9663 | 7.012 | -4.0073 | 15.1438 | 37.7357 | 26.451 | 0.00099717 | 0.0010399 | 1.5813 | 16.7297 | 16.5486 | 17.0721 | 17.3943 | 17.3429 | 16.2855 | 14.6258 | 16.711 | 17.0497 | 17.3512 | 17.3841 | 17.0821 | 16.2367 | 14.4175 | 767.9107 | 386.401 | 511.8115 | 298.1256 | 222.5294 | 680.3354 | 397.5032 | 15.614 | 16.0844 | 17.2132 | 21.4925 | 50.0628 | 65.848 |  |  |  | 552.8104 | 535.8327 | 536.8983 | 565.1832 | 80.0797 | 41.0357 | 815.723 |  |  | 376.9269 |  |  | 17.4395 | 24.413 | 224.6293 | 16.5046 | 19.2063 | 860.5551 | 707.4959 | 562.425 | 802.2876 | 800.9928 | 696.9859 |  | 758.3125 | 821.9596 | 920.7511 | 553.8819 | 637.6803 | 832.4838 |  | 925.0329 |  |  | 354.8013 | 559.7632 | 680.0096 | [6 empty] | 553.0373 |  |  | 341.2188 |  |  | 441.2065 | 609.6095 | 631.6579 | 751.7457 | 995.9929 | 970.6216 | 484.4108 | 653.5495 | 762.284 | 561.6033 | 637.1722 | 930.0145 | 1002.8232 | 574.3337 | 747.0584 | 784.2323 | 1014.763 | 1000.8665 | 472.7862 | 577.1969 | 657.4694 | 513.5918 | 667.7639 | 845.3571 | 914.3161 | 1028.3869 | 536.8161 | 627.6699 | 596.5993 | 781.7072 | 73.7028 | 0.20939 | 18.277 | 3.6698 | -38.574 | 3.1242 | 10290.72 | 0.26 | -0.94637 | -0.85788 | -1.9523 | -2.5177 | 6.2931 | 6.1852 | 6.2055 | 65.8831 | 117.9453 | 41.3518 | 37.1334 | -1.2306 | 72.1586 | 26.0451
42810.4499 | 852 | 18.1556 | 18.3937 | 18.419 | 18.4098 | 17.6929 | 16.2874 | 14.4801 | 16.5327 | 17.0335 | 17.1283 | 17.1336 | 16.635 | 15.6393 | 14.2687 | 14.5388 | 15.1288 | 16.4374 | 18.1853 | 22.8235 | 61.6163 |  |  |  | 17.0234 | 20.767 | 140.4233 | 654.5449 | 694.0917 | 669.3529 | 59.1588 | 67.0107 | 863.1518 | 76.1566 | 92.7502 | 802.45 | 803.0048 | 641.6541 |  | 387.1904 | 880.339 | 872.7161 | 517.0096 |  | 288.4212 | 541.217 | 363.0491 | 566.9518 | 731.4662 | 859.1828 | 916.0146 | 30.0287 | 256.8843 | 49.2854 | 472.5321 | 14.7422 | 48.528 | 47.7584 | 47.0918 | 37.5919 |  |  | 0.20589 | -0.72471 | -0.88394 | -1.0067 | 5.702 | 5.5331 | 5.0295 | -3.335 | 14.3387 | 35.1096 | 26.4727 | 0.0010645 | 0.0010415 | 1.5864 | 16.7282 | 16.5417 | 17.0622 | 17.3848 | 17.336 | 16.277 | 14.6244 | 16.6987 | 17.0432 | 17.3401 | 17.3771 | 17.0766 | 16.2244 | 14.4112 | 769.4284 | 440.6169 | 540.5533 | 308.1516 | 238.5925 | 681.5119 | 399.0073 | 15.6164 | 16.0987 | 17.2327 | 21.6302 | 50.3913 | 66.08 |  |  |  | 553.9012 | 538.9835 | 539.2206 | 568.8946 | 68.8194 | 29.2185 | 815.272 |  |  | 375.3033 |  |  | 17.4429 | 24.536 | 224.2147 | 16.5114 | 19.2888 | 865.337 | 709.6755 | 564.9071 | 800.6146 | 799.3031 | 699.3992 |  | 758.8386 | 816.0429 | 921.3373 | 556.5951 | 638.225 | 828.4797 |  | 926.0153 |  |  | 356.4927 | 560.2176 | 681.1011 | [6 empty] | 555.6983 |  |  | 343.0815 |  |  | 441.5973 | 610.6304 | 633.5916 | 750.6447 | 994.2395 | 971.4675 | 484.4482 | 655.0471 | 765.3474 | 562.7078 | 638.7629 | 928.1105 | 1001.5857 | 574.735 | 750.262 | 785.132 | 1014.5338 | 1002.1647 | 473.4872 | 577.6086 | 659.1639 | 514.5903 | 669.2061 | 846.923 | 915.4217 | 1028.1374 | 537.974 | 626.4869 | 597.0282 | 782.6111 | 70.9428 | 0.1939 | 18.2771 | 3.6573 | -38.6139 | 3.1241 | 10278.32 | 0.27 | 0.9708 | -1.693 | -1.8698 | -1.9954 | 5.5997 | 5.5162 | 5.2591 | 65.9617 | 118.3523 | 41.385 | 37.3272 | -4.1538 | 83.9913 | 26.112
42810.4499 | 853 | 18.1637 | 18.3933 | 18.4223 | 18.4063 | 17.6955 | 16.2893 | 14.4816 | 16.5382 | 17.0322 | 17.134 | 17.1356 | 16.6399 | 15.6455 | 14.268 | 14.5449 | 15.1517 | 16.4547 | 18.329 | 22.9955 | 62.043 |  |  |  | 17.0277 | 20.9138 | 141.7536 | 655.7383 | 695.2003 | 671.5078 | 67.1585 | 69.2441 | 871.8174 | 67.0232 | 85.2645 | 797.1955 | 812.9192 | 616.3797 |  | 368.8892 | 882.0864 | 867.6875 | 545.8522 |  | 288.3183 | 542.87 | 363.3368 | 568.5471 | 730.8996 | 856.2227 | 914.9268 | 30.9329 | 258.3177 | 49.8174 | 473.9319 | 14.6843 | 48.5877 | 47.7742 | 47.1049 | 37.7592 |  |  | -0.20217 | 0.13479 | -0.88591 | -1.1861 | 6.7875 | 6.2191 | 6.4252 | -3.6846 | 14.7869 | 36.1179 | 28.0075 | 0.00099225 | 0.00096596 | 1.587 | 16.7349 | 16.5279 | 17.0626 | 17.3812 | 17.3351 | 16.2712 | 14.6202 | 16.6931 | 17.042 | 17.337 | 17.3757 | 17.0818 | 16.2261 | 14.4092 | 757.1494 | 365.0234 | 505.0998 | 301.7484 | 225.6688 | 681.2881 | 399.4301 | 15.6164 | 16.0972 | 17.257 | 21.7877 | 50.75 | 66.3133 |  |  |  | 554.7596 | 539.6262 | 540.0989 | 564.2855 | 72.2505 | 30.0288 | 814.3305 |  |  | 380.4054 |  |  | 17.4403 | 24.6496 | 222.6742 | 16.5121 | 19.3755 | 859.3488 | 711.3356 | 567.6352 | 797.7476 | 796.4969 | 701.882 |  | 759.2436 | 815.9634 | 920.9257 | 559.4148 | 638.8836 | 825.5496 |  | 925.8408 |  |  | 357.8103 | 563.1638 | 683.0385 | [6 empty] | 558.7655 |  |  | 345.8878 |  |  | 441.7528 | 612.5447 | 635.1201 | 746.7326 | 989.1565 | 970.2181 | 484.6717 | 656.8304 | 767.2639 | 564.0829 | 641.4094 | 926.1922 | 998.9141 | 575.414 | 749.671 | 785.2709 | 1010.4816 | 1002.8052 | 474.3594 | 578.4248 | 659.9637 | 515.2625 | 670.4352 | 848.2048 | 918.0501 | 1025.4312 | 539.3372 | 625.9184 | 597.8005 | 786.3811 | 71.2776 | 0.18433 | 18.2766 | 3.6411 | -38.6052 | 3.1241 | 10240.38 | 0.22 | -0.96309 | 0.73089 | -1.8738 | -2.1681 | 6.1016 | 5.8405 | 5.9365 | 66.005 | 118.1841 | 41.4382 | 38.6225 | -0.13837 | 86.3069 | 26.3742
42810.4499 | 854 | 18.1579 | 18.3981 | 18.4204 | 18.4079 | 17.6983 | 16.2875 | 14.4815 | 16.5395 | 17.0369 | 17.1348 | 17.1353 | 16.6392 | 15.6386 | 14.2663 | 14.5452 | 15.1516 | 16.4562 | 18.4708 | 23.1221 | 62.4438 |  |  |  | 17.0258 | 21.0641 | 139.8908 | 657.6709 | 694.8932 | 672.4148 | 57.067 | 70.7278 | 861.9585 | 66.8029 | 62.4515 | 800.8549 | 788.1992 | 624.2571 |  | 334.0903 | 871.5473 | 872.6724 | 512.3018 |  | 288.8386 | 543.5634 | 364.0138 | 569.9413 | 732.3347 | 854.9054 | 917.0993 | 31.5689 | 259.5182 | 50.17 | 474.9811 | 14.6032 | 48.6677 | 47.8028 | 47.0966 | 38.025 |  |  | -0.19757 | -0.026853 | -0.71244 | -1.3155 | 7.4834 | 7.1214 | 6.4127 | -2.8323 | 14.731 | 36.9169 | 27.8702 | 0.00095939 | 0.0010695 | 1.5835 | 16.7329 | 16.5303 | 17.0676 | 17.3834 | 17.3317 | 16.268 | 14.6238 | 16.6947 | 17.0445 | 17.3377 | 17.3836 | 17.0861 | 16.2307 | 14.4127 | 741.9991 | 399.9679 | 498.8016 | 303.7862 | 223.0533 | 681.9835 | 400.0856 | 15.6094 | 16.1193 | 17.2917 | 21.943 | 51.1015 | 66.544 |  |  |  | 555.3434 | 539.161 | 539.7206 | 562.3451 | 79.9462 | 38.9294 | 812.1979 |  |  | 384.4055 |  |  | 17.435 | 24.7547 | 224.7881 | 16.496 | 19.4573 | 860.8679 | 712.0362 | 569.5888 | 795.3651 | 793.9424 | 703.9251 |  | 759.5137 | 820.8872 | 920.6393 | 561.2467 | 639.4132 | 826.1874 |  | 925.6763 |  |  | 358.8647 | 566.6043 | 684.747 | [6 empty] | 560.9031 |  |  | 347.4915 |  |  | 441.9803 | 614.5001 | 636.2738 | 742.8896 | 986.6891 | 969.2495 | 484.9881 | 659.3264 | 767.8255 | 565.3362 | 643.1249 | 923.4341 | 998.1782 | 576.6446 | 752.3745 | 781.688 | 1011.1621 | 1003.1897 | 475.3759 | 579.6897 | 662.9516 | 515.9405 | 671.5393 | 848.9354 | 918.6457 | 1025.4346 | 540.4982 | 626.7286 | 598.7527 | 788.59 | 72.71 | 0.17184 | 18.2771 | 3.6274 | -38.6985 | 3.1242 | 10198.99 | 0.24 | -0.95253 | -0.32636 | -1.681 | -2.2843 | 6.403 | 6.2462 | 5.9272 | 66.0232 | 117.9288 | 41.4932 | 40.5205 | 0.67955 | 79.6114 | 26.5195
42810.4499 | 855 | 18.1527 | 18.3941 | 18.4218 | 18.4069 | 17.6969 | 16.2833 | 14.4824 | 16.5293 | 17.036 | 17.1279 | 17.1283 | 16.641 | 15.6345 | 14.2702 | 14.5456 | 15.1682 | 16.4788 | 18.6175 | 23.23 | 62.8504 |  |  |  | 17.0344 | 21.2326 | 138.7504 | 658.4026 | 692.7529 | 672.7837 | 45.4855 | 51.4116 | 881.6407 | 56.189 | 70.3553 | 811.5187 | 785.8823 | 685.103 |  | 352.6226 | 876.9374 | 871.0041 | 480.7827 |  | 289.7154 | 544.8219 | 366.1406 | 570.976 | 734.9621 | 862.4304 | 917.7836 | 32.0184 | 260.7894 | 50.618 | 476.1892 | 14.5323 | 48.7236 | 47.8318 | 47.1026 | 38.3013 |  |  | -0.025409 | -0.44872 | -0.49559 | -1.3116 | 6.3873 | 5.177 | 5.6104 | -3.9461 | 14.8713 | 37.0772 | 27.7634 | 0.00099389 | 0.00099717 | 1.5792 | 16.7477 | 16.5336 | 17.0683 | 17.3875 | 17.3412 | 16.2713 | 14.6296 | 16.6943 | 17.0463 | 17.3572 | 17.3877 | 17.084 | 16.241 | 14.4201 | 754.6794 | 420.1074 | 514.7098 | 318.0349 | 236.304 | 683.0117 | 400.9488 | 15.6041 | 16.1297 | 17.3107 | 22.0836 | 51.4309 | 66.7671 |  |  |  | 556.123 | 541.8059 | 541.2663 | 565.8262 | 87.1815 | 34.3719 | 809.7494 |  |  | 381.8767 |  |  | 17.4418 | 24.8721 | 222.9625 | 16.4954 | 19.5413 | 864.3425 | 712.7289 | 570.9418 | 794.1592 | 793.0172 | 702.8765 |  | 759.7322 | 819.4643 | 920.7495 | 562.0898 | 639.8072 | 825.576 |  | 926.0046 |  |  | 359.4546 | 567.4991 | 685.4807 | [6 empty] | 562.3018 |  |  | 348.4969 |  |  | 442.3923 | 615.8732 | 637.1582 | 741.474 | 985.7272 | 969.6244 | 485.5048 | 661.6051 | 767.9469 | 566.3298 | 644.0634 | 920.514 | 997.9153 | 578.0547 | 754.1385 | 780.2566 | 1013.9929 | 1002.1278 | 476.5328 | 581.0036 | 664.0953 | 516.9531 | 672.2124 | 847.4859 | 918.4503 | 1027.6395 | 541.1609 | 627.7439 | 599.6997 | 786.5544 | 78.1037 | 0.15956 | 18.2764 | 3.6091 | -38.6874 | 3.1241 | 10161.56 | 0.28 | -0.34166 | -1.3351 | -1.4031 | -2.2826 | 5.9352 | 5.3433 | 5.5625 | 66.113 | 118.0139 | 41.5487 | 39.4293 | -0.93226 | 79.7964 | 26.5452
42810.4499 | 856 | 18.1505 | 18.389 | 18.4246 | 18.4071 | 17.6922 | 16.2849 | 14.4807 | 16.5304 | 17.0311 | 17.1325 | 17.132 | 16.6433 | 15.6377 | 14.2731 | 14.5354 | 15.1679 | 16.4835 | 18.743 | 23.18 | 63.2176 |  |  |  | 17.0314 | 21.3912 | 138.1702 | 657.129 | 688.8397 | 671.1782 | 68.3942 | 52.6058 | 890.6962 | 46.3632 | 68.84 | 814.7832 | 785.2063 | 687.0322 |  | 368.639 | 891.9363 | 874.4549 | 485.3117 |  | 290.727 | 545.9884 | 369.4036 | 571.7329 | 729.5264 | 860.6158 | 915.8263 | 32.5609 | 262.0444 | 51.4644 | 477.1948 | 14.4908 | 48.7401 | 47.8618 | 47.0978 | 38.519 |  |  | -0.090461 | -0.44478 | -0.69404 | -1.3556 | 5.725 | 6.3854 | 6.7426 | -2.4499 | 13.6477 | 35.4006 | 27.7201 | 0.001007 | 0.00099882 | 1.5798 | 16.7509 | 16.5368 | 17.0582 | 17.3893 | 17.3384 | 16.2725 | 14.6223 | 16.7004 | 17.044 | 17.3481 | 17.3832 | 17.08 | 16.2351 | 14.4077 | 767.2458 | 387.0169 | 503.7093 | 316.2843 | 242.8475 | 684.1602 | 401.4799 | 15.6012 | 16.1455 | 17.3436 | 22.2304 | 51.7604 | 66.9872 |  |  |  | 557.1188 | 545.1037 | 543.7444 | 570.6643 | 66.4731 | 30.7476 | 809.0528 |  |  | 378.3672 |  |  | 17.4441 | 24.9943 | 220.969 | 16.4982 | 19.6272 | 867.5863 | 715.8861 | 572.1236 | 795.1114 | 793.7658 | 705.7559 |  | 760.4361 | 813.8731 | 922.0198 | 563.2608 | 640.1768 | 823.5091 |  | 926.4415 |  |  | 360.2347 | 568.5391 | 686.7959 | [6 empty] | 563.544 |  |  | 349.5145 |  |  | 442.7392 | 616.6724 | 637.8564 | 740.3805 | 985.89 | 970.4473 | 486.3416 | 663.024 | 769.7598 | 567.27 | 644.3808 | 918.7064 | 999.0099 | 579.4858 | 755.5805 | 783.7573 | 1013.5794 | 999.5954 | 477.1038 | 582.1638 | 665.6444 | 518.1422 | 672.6694 | 844.7426 | 919.8174 | 1025.4576 | 542.04 | 629.104 | 600.8756 | 783.4987 | 75.6552 | 0.14764 | 18.2765 | 3.597 | -38.5646 | 3.1241 | 10180.44 | 0.39 | -0.64411 | -1.3302 | -1.6616 | -2.3223 | 5.6145 | 5.9296 | 6.0931 | 66.2286 | 118.6956 | 41.5903 | 38.3888 | 0.38597 | 79.4699 | 26.5675
42810.45 | 857 | 18.1412 | 18.3807 | 18.4123 | 18.3947 | 17.687 | 16.279 | 14.4735 | 16.5225 | 17.0268 | 17.1258 | 17.1241 | 16.6375 | 15.631 | 14.2645 | 14.5392 | 15.1774 | 16.4929 | 18.8829 | 23.0669 | 63.5842 |  |  |  | 17.0278 | 21.5664 | 140.9972 | 654.5344 | 688.7273 | 668.0098 | 82.0203 | 61.0957 | 886.491 | 42.8755 | 58.5947 | 799.424 | 776.3544 | 699.5529 |  | 361.6985 | 895.4601 | 886.4252 | 498.5323 |  | 291.5937 | 545.728 | 370.8429 | 572.3546 | 726.0159 | 854.1104 | 911.6088 | 32.5628 | 263.012 | 52.5023 | 477.9948 | 14.3734 | 48.7049 | 47.8878 | 47.1062 | 38.8128 |  |  | 0.53248 | -0.96653 | -1.0285 | -1.196 | 6.4307 | 5.8722 | 5.8601 | -3.8896 | 14.8305 | 38.4656 | 29.1196 | 0.00093639 | 0.00099717 | 1.5831 | 16.7735 | 16.536 | 17.0623 | 17.3938 | 17.3397 | 16.2721 | 14.6293 | 16.7042 | 17.0544 | 17.3507 | 17.3883 | 17.091 | 16.2415 | 14.4116 | 758.5151 | 469.6483 | 508.9317 | 312.3721 | 252.2398 | 684.2784 | 401.8141 | 15.6014 | 16.1504 | 17.3667 | 22.3815 | 52.0902 | 67.204 |  |  |  | 558.2167 | 549.9135 | 547.0583 | 575.0377 | 84.48 | 31.171 | 809.9756 |  |  | 380.0562 |  |  | 17.4401 | 25.1124 | 225.2722 | 16.5017 | 19.7219 | 870.3964 | 719.6786 | 573.3963 | 794.0627 | 792.6825 | 712.0873 |  | 761.4081 | 809.4827 | 922.6805 | 564.5402 | 640.7114 | 820.465 |  | 926.6589 |  |  | 361.3092 | 572.6982 | 690.826 | [6 empty] | 564.7545 |  |  | 350.9302 |  |  | 443.1224 | 617.122 | 638.3034 | 741.5306 | 986.0047 | 970.9961 | 487.2214 | 664.1567 | 771.943 | 568.0829 | 644.8676 | 917.1321 | 1000.4569 | 580.7644 | 755.8826 | 785.7059 | 1012.1815 | 998.3423 | 477.5885 | 583.3826 | 665.9819 | 519.1715 | 672.9411 | 843.5348 | 923.6052 | 1024.8525 | 543.0345 | 629.7276 | 602.0792 | 782.4607 | 73.2829 | 0.13441 | 18.2759 | 3.5684 | -38.5679 | 3.1241 | 10263.09 | 0.27 | 1.5601 | -1.9606 | -2.0225 | -2.1809 | 5.9335 | 5.6699 | 5.6641 | 66.3235 | 119.092 | 41.662 | 39.3955 | -0.13387 | 76.5065 | 26.6193
42810.45 | 858 | 18.1372 | 18.3806 | 18.4102 | 18.3948 | 17.6873 | 16.2832 | 14.4738 | 16.5303 | 17.0292 | 17.121 | 17.1233 | 16.6367 | 15.6299 | 14.2637 | 14.5305 | 15.1846 | 16.4999 | 19.04 | 23.0533 | 63.9626 |  |  |  | 17.0285 | 21.7447 | 142.5679 | 654.9119 | 689.1814 | 669.8493 | 64.3535 | 74.966 | 876.7646 | 59.1871 | 53.4452 | 794.7704 | 766.8209 | 704.7667 |  | 349.4337 | 891.6707 | 881.1951 | 485.5442 |  | 292.7682 | 547.4589 | 370.7556 | 569.8685 | 720.4564 | 855.2009 | 910.8168 | 32.9585 | 264.2732 | 53.9496 | 479.085 | 14.2282 | 48.6609 | 47.9234 | 47.1161 | 39.0266 |  |  | 0.53971 | -0.58737 | -0.74398 | -1.5488 | 7.5793 | 6.8191 | 6.6315 | -2.2659 | 14.8316 | 37.7517 | 28.7746 | 0.0009446 | 0.00098732 | 1.583 | 16.7681 | 16.545 | 17.0624 | 17.3896 | 17.3335 | 16.2831 | 14.6297 | 16.704 | 17.0502 | 17.353 | 17.3896 | 17.0908 | 16.2355 | 14.4211 | 775.5976 | 450.531 | 501.6703 | 320.3899 | 262.4388 | 685.8799 | 402.6116 | 15.6 | 16.1677 | 17.4028 | 22.5513 | 52.4624 | 67.4405 |  |  |  | 559.2341 | 552.332 | 548.3427 | 575.7406 | 94.8077 | 40.9168 | 809.3643 |  |  | 385.2346 |  |  | 17.4358 | 25.2306 | 230.639 | 16.5046 | 19.8182 | 863.1464 | 720.4243 | 574.6792 | 790.5718 | 789.6476 | 715.7825 |  | 762.1543 | 807.8472 | 921.9413 | 565.4255 | 641.4078 | 816.3924 |  | 927.0186 |  |  | 362.4681 | 575.2185 | 693.3682 | [6 empty] | 565.7774 |  |  | 351.5734 |  |  | 443.67 | 617.6301 | 638.5035 | 745.834 | 984.1401 | 971.6809 | 487.8843 | 664.7438 | 772.5415 | 568.7974 | 645.5939 | 917.4608 | 1003.0123 | 581.6857 | 753.8405 | 785.4222 | 1014.0934 | 998.8441 | 477.7693 | 584.1436 | 666.3507 | 520.2986 | 673.1874 | 842.8341 | 928.1538 | 1026.1935 | 543.4787 | 629.9655 | 603.2566 | 782.4254 | 76.0471 | 0.11881 | 18.2769 | 3.5597 | -38.6676 | 3.1241 | 10307.11 | 0.36 | 1.5722 | -1.53 | -1.7219 | -2.4845 | 6.4447 | 6.113 | 6.0283 | 66.4292 | 118.8304 | 41.7775 | 37.9949 | 0.81729 | 74.1368 | 26.7609
42810.45 | 859 | 18.1359 | 18.3851 | 18.4038 | 18.3968 | 17.6789 | 16.2825 | 14.4769 | 16.5299 | 17.0281 | 17.1246 | 17.1236 | 16.6339 | 15.6359 | 14.268 | 14.522 | 15.1919 | 16.5209 | 19.1944 | 23.1617 | 64.3468 |  |  |  | 17.0397 | 21.9339 | 142.0769 | 654.8248 | 689.2861 | 669.9135 | 74.3759 | 78.2726 | 857.8214 | 81.5627 | 79.6502 | 808.5883 | 776.2205 | 699.9853 |  | 345.9774 | 888.992 | 886.1547 | 486.1817 |  | 293.2109 | 549.1302 | 371.2044 | 570.6432 | 725.0837 | 859.9932 | 912.9795 | 33.5777 | 265.3553 | 55.0293 | 480.0013 | 14.1576 | 48.6589 | 47.9468 | 47.1351 | 39.1554 |  |  | -0.10623 | 0.20117 | -0.97528 | -1.809 | 7.1956 | 6.6325 | 6.6355 | -3.1464 | 14.9939 | 37.2272 | 29.7747 | 0.00094953 | 0.0009791 | 1.5842 | 16.7748 | 16.5424 | 17.0702 | 17.3952 | 17.3305 | 16.2819 | 14.6397 | 16.7065 | 17.0546 | 17.3524 | 17.3943 | 17.092 | 16.2407 | 14.4194 | 799.5417 | 471.2543 | 528.6996 | 340.8735 | 269.3896 | 688.2833 | 404.0038 | 15.5986 | 16.1756 | 17.4357 | 22.7043 | 52.795 | 67.6588 |  |  |  | 559.954 | 552.1352 | 547.588 | 572.2037 | 75.3717 | 36.9836 | 806.3129 |  |  | 383.7189 |  |  | 17.4344 | 25.3404 | 228.9996 | 16.4946 | 19.9147 | 858.8571 | 720.2631 | 575.217 | 789.1328 | 788.3614 | 713.9669 |  | 762.5908 | 804.2701 | 921.2331 | 565.4273 | 641.9045 | 812.0626 |  | 927.2759 |  |  | 363.7355 | 574.8126 | 693.0515 | [6 empty] | 566.0913 |  |  | 351.3665 |  |  | 444.0172 | 617.6912 | 638.9925 | 749.7536 | 985.3754 | 971.9503 | 488.7892 | 665.5858 | 772.7575 | 569.398 | 645.9506 | 920.2808 | 1004.9014 | 582.8999 | 753.1599 | 785.5226 | 1014.0833 | 997.5475 | 478.4527 | 584.5988 | 667.09 | 521.6483 | 674.1092 | 840.508 | 937.6951 | 1024.6474 | 542.8662 | 630.3229 | 604.4925 | 781.6579 | 81.0282 | 0.10911 | 18.2763 | 3.5368 | -38.7107 | 3.1241 | 10402.24 | 0.21 | -0.69754 | 0.8963 | -1.9735 | -2.6878 | 6.2928 | 6.0415 | 6.0429 | 66.6017 | 118.6362 | 41.8775 | 36.0842 | -1.9336 | 76.8107 | 26.9734
42810.45 | 860 | 18.1375 | 18.3815 | 18.4096 | 18.3982 | 17.6879 | 16.2805 | 14.4867 | 16.5466 | 17.0303 | 17.1323 | 17.1354 | 16.6401 | 15.6399 | 14.2676 | 14.5213 | 15.201 | 16.5336 | 19.3462 | 23.2982 | 64.7148 |  |  |  | 17.0352 | 22.1289 | 144.1468 | 653.5609 | 689.61 | 667.2773 | 76.6141 | 73.4372 | 884.7904 | 55.1261 | 87.5931 | 791.1548 | 716.4271 | 679.4497 |  | 341.9048 | 891.3952 | 886.2767 | 499.4998 |  | 293.2476 | 549.7539 | 372.0032 | 572.329 | 730.2163 | 861.8691 | 916.2306 | 33.8399 | 266.4546 | 54.7705 | 480.8102 | 14.1338 | 48.6707 | 47.9483 | 47.1617 | 39.1296 |  |  | -0.23766 | 0.28922 | -0.82809 | -1.5495 | 5.9418 | 5.3682 | 5.8863 | -3.5979 | 14.767 | 37.3067 | 30.8809 | 0.00088218 | 0.00098239 | 1.5818 | 16.7818 | 16.5358 | 17.0611 | 17.3889 | 17.3285 | 16.2738 | 14.6354 | 16.7003 | 17.0468 | 17.35 | 17.3879 | 17.0851 | 16.2403 | 14.4197 | 790.094 | 444.5951 | 552.0609 | 337.5387 | 266.4886 | 689.4536 | 405.5305 | 15.5907 | 16.185 | 17.4539 | 22.8406 | 53.1108 | 67.8682 |  |  |  | 560.566 | 550.447 | 546.5541 | 569.0673 | 73.474 | 39.5501 | 804.4902 |  |  | 380.0744 |  |  | 17.4387 | 25.4606 | 232.4972 | 16.5122 | 20.0168 | 859.294 | 722.906 | 574.7641 | 789.5394 | 788.3073 | 716.1748 |  | 763.3773 | 802.4137 | 921.1658 | 564.7457 | 642.1187 | 811.1382 |  | 927.2542 |  |  | 365.7187 | 576.4207 | 694.4022 | [6 empty] | 565.5636 |  |  | 351.0695 |  |  | 444.3459 | 617.7313 | 638.9455 | 749.634 | 990.0445 | 970.175 | 489.9783 | 666.8373 | 772.4533 | 570.1627 | 646.2798 | 924.58 | 1004.6932 | 584.1807 | 753.0767 | 787.8356 | 1021.0125 | 996.8025 | 479.1479 | 584.8196 | 666.4824 | 522.9913 | 675.3745 | 840.6498 | 946.6297 | 1026.5554 | 542.7196 | 630.1606 | 605.8311 | 780.3244 | 75.5562 | 0.095325 | 18.2762 | 3.5064 | -38.6512 | 3.1241 | 10501.48 | 0.23 | -1.0418 | 1.0751 | -1.8192 | -2.4885 | 5.7231 | 5.4398 | 5.6963 | 66.7606 | 118.6599 | 41.9396 | 37.5003 | -4.2517 | 60.3986 | 27.1579
42810.45 | 861 | 18.1301 | 18.3799 | 18.4157 | 18.4005 | 17.6895 | 16.2859 | 14.4876 | 16.5311 | 17.0273 | 17.1318 | 17.1299 | 16.6408 | 15.6469 | 14.2633 | 14.5189 | 15.204 | 16.5436 | 19.4988 | 23.4777 | 65.1003 |  |  |  | 17.0345 | 22.3282 | 143.6533 | 651.8003 | 689.732 | 664.244 | 72.9177 | 80.8472 | 874.8296 | 67.9303 | 81.4344 | 803.64 | 794.8848 | 665.7078 |  | 316.1788 | 874.4128 | 878.1387 | 499.2511 |  | 293.3836 | 550.3978 | 372.2859 | 570.4022 | 738.3334 | 866.371 | 918.9418 | 34.1482 | 267.6493 | 53.9088 | 481.587 | 14.1159 | 48.6792 | 47.9349 | 47.1789 | 38.8965 |  |  | 0.1277 | 0.22022 | -0.89183 | -1.3359 | 6.7244 | 6.48 | 6.0592 | -2.693 | 15.2086 | 37.7137 | 29.2897 | 0.00089532 | 0.00093146 | 1.5816 | 16.7871 | 16.5289 | 17.0564 | 17.3822 | 17.3277 | 16.2726 | 14.6263 | 16.6997 | 17.0482 | 17.3472 | 17.3886 | 17.0809 | 16.2354 | 14.4187 | 790.2042 | 423.4469 | 552.8782 | 339.2712 | 266.0154 | 690.2511 | 406.7088 | 15.5866 | 16.1984 | 17.4798 | 22.9865 | 53.4246 | 68.0854 |  |  |  | 561.0376 | 547.1914 | 544.5853 | 566.5025 | 77.8282 | 40.211 | 804.2658 |  |  | 379.0084 |  |  | 17.4352 | 25.585 | 233.8113 | 16.5035 | 20.1059 | 856.7393 | 726.7301 | 574.625 | 788.2331 | 786.0581 | 721.3171 |  | 764.6185 | 799.9455 | 920.626 | 563.8663 | 642.305 | 810.3432 |  | 927.1068 |  |  | 368.1785 | 580.922 | 698.973 | [6 empty] | 565.0695 |  |  | 351.6745 |  |  | 444.6766 | 618.7815 | 638.0728 | 750.6145 | 991.5953 | 969.6564 | 491.1195 | 667.7782 | 773.396 | 571.1821 | 646.4071 | 925.4201 | 1005.9844 | 585.1453 | 754.9905 | 791.0982 | 1029.112 | 998.1801 | 479.912 | 584.9731 | 666.3667 | 524.5397 | 677.2382 | 841.3011 | 948.2404 | 1028.2084 | 543.1168 | 630.7603 | 607.5467 | 781.9167 | 75.5034 | 0.088212 | 18.2758 | 3.4795 | -38.6706 | 3.124 | 10517.35 | 0.3 | 0.76247 | 0.93852 | -1.8887 | -2.3115 | 6.1004 | 5.9885 | 5.7907 | 66.9663 | 118.505 | 42.0016 | 37.7381 | -4.1279 | 81.9897 | 27.3042
42810.45 | 862 | 18.1189 | 18.3725 | 18.4028 | 18.3866 | 17.6789 | 16.2745 | 14.4812 | 16.5245 | 17.0157 | 17.127 | 17.1267 | 16.6329 | 15.6361 | 14.2653 | 14.5084 | 15.2204 | 16.5593 | 19.659 | 23.5748 | 65.5002 |  |  |  | 17.0356 | 22.5564 | 151.6441 | 652.6407 | 690.6065 | 667.62 | 65.6315 | 80.7851 | 873.3148 | 74.4264 | 81.0782 | 816.6747 | 788.6457 | 697.3857 |  | 321.7156 | 864.921 | 862.1188 | 489.4669 |  | 294.0696 | 550.908 | 372.5894 | 568.5342 | 740.8685 | 867.5964 | 919.2782 | 34.2272 | 268.6783 | 54.9304 | 482.4596 | 14.0649 | 48.6862 | 47.9179 | 47.2023 | 38.7043 |  |  | 0.14478 | -0.28576 | -0.94242 | -1.5475 | 7.2376 | 6.8132 | 7.083 | -3.1241 | 14.1305 | 36.2029 | 31.3718 | 0.00099389 | 0.00080004 | 1.5791 | 16.7944 | 16.528 | 17.0554 | 17.3888 | 17.3328 | 16.2727 | 14.63 | 16.7075 | 17.0514 | 17.3563 | 17.3947 | 17.0885 | 16.2394 | 14.4171 | 780.8345 | 433.7232 | 549.5192 | 328.8536 | 260.4538 | 691.0433 | 407.897 | 15.5843 | 16.2145 | 17.5134 | 23.1365 | 53.7462 | 68.2954 |  |  |  | 561.578 | 545.8124 | 543.5241 | 566.5357 | 68.5256 | 37.9888 | 801.9211 |  |  | 378.2776 |  |  | 17.4335 | 25.7073 | 240.705 | 16.4887 | 20.2055 | 854.8576 | 728.2863 | 575.2518 | 786.0634 | 783.8394 | 723.0531 |  | 765.8041 | 793.486 | 919.7824 | 564.6251 | 642.7376 | 805.9414 |  | 927.0147 |  |  | 370.4878 | 585.6613 | 701.5766 | [6 empty] | 565.7582 |  |  | 353.0406 |  |  | 445.0806 | 620.1054 | 638.25 | 751.6598 | 991.6551 | 969.5205 | 492.2099 | 669.2929 | 775.1648 | 572.2306 | 646.2518 | 924.3909 | 1007.7563 | 586.6795 | 755.4016 | 789.4841 | 1028.3922 | 999.4969 | 480.5476 | 585.5875 | 665.7385 | 525.7591 | 679.2925 | 843.3868 | 948.4899 | 1027.7957 | 543.8319 | 631.0755 | 608.9441 | 785.7596 | 77.778 | 0.076615 | 18.2753 | 3.4602 | -38.6967 | 3.124 | 10599.54 | 0.3 | 0.81333 | -1.0694 | -1.9421 | -2.4886 | 6.3323 | 6.1438 | 6.2642 | 67.2521 | 118.3358 | 42.0678 | 39.0281 | -3.5377 | 80.3792 | 27.3895
42810.45 | 863 | 18.1223 | 18.3827 | 18.4079 | 18.3992 | 17.6896 | 16.2808 | 14.4917 | 16.5301 | 17.0283 | 17.135 | 17.1332 | 16.642 | 15.6389 | 14.2774 | 14.5062 | 15.2295 | 16.5751 | 19.8193 | 23.6706 | 65.9193 |  |  |  | 17.0348 | 22.816 | 153.2807 | 653.841 | 692.7341 | 666.9453 | 62.7623 | 59.7188 | 868.5467 | 64.6735 | 68.6153 | 815.6346 | 781.9199 | 696.7567 |  | 337.0698 | 861.3325 | 855.4722 | 469.0157 |  | 295.2084 | 549.439 | 372.1543 | 565.7696 | 736.3297 | 872.8844 | 922.019 | 34.0949 | 269.8166 | 55.7149 | 483.6258 | 14.0335 | 48.6951 | 47.9273 | 47.2368 | 38.3159 |  |  | 0.060675 | 0.24913 | -1.0187 | -1.65 | 6.2119 | 5.7973 | 5.5427 | -2.6805 | 13.2221 | 37.216 | 31.1833 | 0.00090682 | 0.00097089 | 1.5803 | 16.7974 | 16.5223 | 17.0553 | 17.383 | 17.3323 | 16.2707 | 14.6227 | 16.6998 | 17.0414 | 17.3462 | 17.3905 | 17.0857 | 16.2401 | 14.4163 | 762.4406 | 397.7032 | 539.6571 | 321.9829 | 253.2725 | 691.2529 | 408.8816 | 15.5648 | 16.2268 | 17.5325 | 23.2974 | 54.0914 | 68.5231 |  |  |  | 562.3595 | 544.9207 | 542.317 | 572.4541 | 66.4403 | 35.6363 | 800.3776 |  |  | 378.6951 |  |  | 17.4371 | 25.83 | 252.717 | 16.5034 | 20.3115 | 851.2883 | 728.2814 | 576.3612 | 786.9835 | 785.1837 | 722.8732 |  | 766.6234 | 793.1069 | 920.6383 | 565.2996 | 643.107 | 807.2447 |  | 927.6165 |  |  | 372.3736 | 588.8887 | 702.5473 | [6 empty] | 566.7334 |  |  | 354.1759 |  |  | 445.1258 | 621.0737 | 639.6374 | 751.8771 | 989.9876 | 972.1456 | 493.2413 | 670.4359 | 777.9472 | 573.0913 | 646.9688 | 922.4871 | 1008.4588 | 588.4615 | 756.0629 | 788.0324 | 1025.4104 | 998.7496 | 481.4356 | 586.0994 | 668.4516 | 527.1136 | 680.5442 | 843.8476 | 950.7499 | 1028.1497 | 544.914 | 633.688 | 610.2859 | 785.6255 | 82.5944 | 0.064963 | 18.2756 | 3.4441 | -38.7489 | 3.124 | 10628.12 | 0.31 | 0.52633 | 0.99764 | -2.0173 | -2.5675 | 5.88 | 5.6804 | 5.5542 | 67.4885 | 118.7001 | 42.1238 | 41.1378 | -2.2618 | 78.9518 | 27.3501
42810.45 | 864 | 18.1174 | 18.3815 | 18.4074 | 18.4055 | 17.6944 | 16.2824 | 14.4975 | 16.5374 | 17.0349 | 17.1403 | 17.1307 | 16.6423 | 15.6522 | 14.2737 | 14.5106 | 15.2479 | 16.5891 | 19.9868 | 23.8458 | 66.3398 |  |  |  | 17.0416 | 23.0997 | 148.2886 | 652.972 | 694.2779 | 664.7291 | 69.9715 | 52.3917 | 864.3695 | 63.4217 | 61.8108 | 813.5752 | 788.1248 | 691.8963 |  | 337.817 | 858.7796 | 856.262 | 478.0349 |  | 295.4221 | 549.9844 | 373.3312 | 566.3539 | 731.6898 | 879.3213 | 924.1233 | 34.1054 | 270.86 | 55.3031 | 484.6022 | 14.0042 | 48.7152 | 47.9623 | 47.27 | 37.87 |  |  | 0.11324 | 0.18211 | -0.8202 | -1.3714 | 7.1752 | 6.068 | 5.9277 | -2.4722 | 15.6252 | 38.4171 | 30.7499 | 0.00092653 | 0.00088054 | 1.5822 | 16.8081 | 16.523 | 17.0537 | 17.384 | 17.3337 | 16.2782 | 14.6273 | 16.709 | 17.0506 | 17.3532 | 17.3867 | 17.0904 | 16.2405 | 14.4261 | 744.6033 | 364.0734 | 513.5078 | 315.8216 | 246.0404 | 690.7643 | 409.2526 | 15.5699 | 16.2389 | 17.5689 | 23.4465 | 54.4014 | 68.7338 |  |  |  | 563.3795 | 545.8625 | 542.0492 | 575.8068 | 75.4819 | 33.5279 | 802.4115 |  |  | 377.5713 |  |  | 17.4428 | 25.9517 | 248.6124 | 16.5122 | 20.4184 | 849.0478 | 730.2787 | 577.26 | 788.1518 | 786.1718 | 725.5288 |  | 767.6692 | 795.6835 | 921.6406 | 566.1632 | 643.5158 | 811.0636 |  | 928.1917 |  |  | 374.5824 | 595.3687 | 704.5853 | [6 empty] | 568.1656 |  |  | 354.4498 |  |  | 445.6054 | 621.0574 | 640.3934 | 752.0481 | 988.6121 | 975.9592 | 494.7642 | 672.5213 | 781.2046 | 573.6608 | 646.3949 | 927.2956 | 1008.7442 | 590.5287 | 757.5017 | 788.2812 | 1024.4785 | 1000.6292 | 481.8225 | 586.3815 | 667.4765 | 529.573 | 682.4454 | 845.0508 | 954.903 | 1027.0863 | 546.1903 | 634.2874 | 611.8294 | 788.1848 | 85.6242 | 0.056306 | 18.2753 | 3.4264 | -38.6839 | 3.124 | 10633.45 | 0.37 | 0.7182 | 0.85324 | -1.8108 | -2.3414 | 6.3372 | 5.8278 | 5.7601 | 67.7108 | 119.0436 | 42.1825 | 42.9661 | 0.71157 | 80.541 | 27.4205
42810.45 | 865 | 18.1098 | 18.3818 | 18.4065 | 18.4027 | 17.6894 | 16.281 | 14.491 | 16.5309 | 17.0324 | 17.1397 | 17.1314 | 16.6391 | 15.6459 | 14.2737 | 14.4983 | 15.2551 | 16.5876 | 20.152 | 23.8587 | 66.7371 |  |  |  | 17.0283 | 23.4069 | 157.3186 | 652.6916 | 695.0741 | 667.0494 | 79.9782 | 72.6321 | 859.8704 | 66.469 | 68.8188 | 806.739 | 784.5316 | 698.8507 |  | 342.4897 | 866.1222 | 859.566 | 489.9492 |  | 295.0334 | 553.3384 | 375.5788 | 568.4537 | 738.266 | 883.8294 | 925.8146 | 34.5475 | 271.959 | 54.246 | 485.7678 | 13.9126 | 48.687 | 47.9822 | 47.2908 | 37.4276 |  |  | 0.063959 | 0.36282 | -0.62898 | -1.2492 | 6.3985 | 5.6744 | 5.9021 | -3.1826 | 15.8708 | 38.8789 | 32.7319 | 0.00096596 | 0.00093803 | 1.5839 | 16.8134 | 16.5138 | 17.0481 | 17.3821 | 17.3325 | 16.2671 | 14.6295 | 16.6991 | 17.0438 | 17.3461 | 17.3827 | 17.086 | 16.2389 | 14.4225 | 748.3066 | 357.0892 | 502.522 | 319.4141 | 249.7376 | 691.1028 | 409.9845 | 15.5713 | 16.2577 | 17.6018 | 23.5975 | 54.717 | 68.9333 |  |  |  | 564.0631 | 544.8113 | 541.5644 | 572.5058 | 86.1561 | 37.6459 | 803.8239 |  |  | 380.4625 |  |  | 17.4492 | 26.0701 | 249.3486 | 16.5189 | 20.5344 | 849.1986 | 733.4165 | 577.7436 | 790.1076 | 787.5952 | 729.4783 |  | 769.1568 | 801.0344 | 921.7058 | 566.7299 | 643.99 | 815.032 |  | 928.1739 |  |  | 376.9064 | 601.3396 | 709.1358 | [6 empty] | 568.2479 |  |  | 355.7348 |  |  | 446.0667 | 620.8018 | 641.8872 | 751.5617 | 988.7444 | 975.537 | 496.5772 | 673.9301 | 781.478 | 573.8387 | 646.4593 | 928.2705 | 1012.8575 | 592.2757 | 757.7753 | 787.5623 | 1023.333 | 1004.7148 | 482.3789 | 587.0125 | 666.3052 | 531.5664 | 683.3572 | 845.5638 | 956.6384 | 1030.7215 | 547.8683 | 634.8573 | 613.3062 | 786.4296 | 84.2153 | 0.048358 | 18.2761 | 3.4148 | -38.5712 | 3.124 | 10624.54 | 0.26 | 0.54042 | 1.2068 | -1.5889 | -2.2392 | 5.9961 | 5.6466 | 5.7588 | 68.0236 | 118.922 | 42.2628 | 42.661 | 2.0664 | 79.1411 | 27.622
42810.4501 | 866 | 18.1079 | 18.3706 | 18.4013 | 18.3955 | 17.686 | 16.2769 | 14.4906 | 16.5336 | 17.0261 | 17.129 | 17.1279 | 16.6337 | 15.6364 | 14.269 | 14.4971 | 15.2654 | 16.6188 | 20.3283 | 24.0684 | 67.1572 |  |  |  | 17.0377 | 23.73 | 152.6031 | 652.3549 | 695.3927 | 664.3227 | 79.1525 | 82.7721 | 855.8206 | 74.0395 | 79.305 | 812.086 | 773.4572 | 706.773 |  | 341.7197 | 872.4246 | 862.0694 | 487.0794 |  | 295.66 | 556.9437 | 375.8087 | 571.6344 | 743.9302 | 881.7185 | 928.3376 | 35.1929 | 273.2276 | 53.7539 | 487.4755 | 13.8576 | 48.6746 | 48.009 | 47.3252 | 37.1983 |  |  | 0.14544 | -0.059053 | -0.87868 | -1.466 | 6.1889 | 5.2164 | 6.1702 | -2.6135 | 15.1035 | 37.63 | 32.3202 | 0.00090025 | 0.00086739 | 1.5866 | 16.8211 | 16.5177 | 17.0477 | 17.3812 | 17.3327 | 16.2671 | 14.6201 | 16.6996 | 17.0491 | 17.3475 | 17.3778 | 17.0866 | 16.2428 | 14.4209 | 763.0189 | 345.943 | 519.0572 | 318.0069 | 252.2734 | 692.5759 | 411.2588 | 15.5779 | 16.2779 | 17.6418 | 23.7555 | 55.0328 | 69.1329 |  |  |  | 564.6536 | 543.7296 | 541.4928 | 571.5293 | 80.8934 | 37.4816 | 805.9615 |  |  | 391.4385 |  |  | 17.4461 | 26.1855 | 251.6844 | 16.5204 | 20.6394 | 845.4242 | 735.27 | 578.1389 | 796.3245 | 793.7833 | 731.7483 |  | 770.7545 | 816.7767 | 922.6925 | 566.9496 | 644.4292 | 824.8305 |  | 928.3366 |  |  | 378.3772 | 603.079 | 711.6077 | [6 empty] | 568.7496 |  |  | 357.2812 |  |  | 446.0493 | 621.0854 | 643.2013 | 750.4624 | 989.7078 | 974.6819 | 498.1702 | 675.5729 | 780.0312 | 574.0979 | 647.1747 | 924.6485 | 1013.8332 | 594.2997 | 760.3645 | 789.3212 | 1021.9045 | 1007.0804 | 484.2656 | 588.0443 | 667.6254 | 533.7246 | 684.6844 | 841.8129 | 955.9674 | 1033.0754 | 549.1541 | 634.6095 | 615.3508 | 784.5239 | 78.7358 | 0.041953 | 18.276 | 3.402 | -38.665 | 3.124 | 10657.71 | 0.3 | 0.81375 | -0.48792 | -1.8821 | -2.4311 | 5.8917 | 5.409 | 5.8828 | 68.4162 | 118.8943 | 42.3458 | 41.4902 | 0.46312 | 75.9877 | 27.7442
42810.4501 | 867 | 18.1086 | 18.3742 | 18.3981 | 18.3908 | 17.6895 | 16.2786 | 14.4936 | 16.5344 | 17.0272 | 17.1269 | 17.1388 | 16.6372 | 15.6454 | 14.2851 | 14.4938 | 15.2694 | 16.6307 | 20.505 | 24.1636 | 67.5533 |  |  |  | 17.0279 | 24.0733 | 147.2687 | 647.8573 | 693.4594 | 657.7017 | 69.5874 | 73.8062 | 850.777 | 76.0573 | 85.1556 | 788.7637 | 794.0358 | 691.4026 |  | 341.0102 | 865.3708 | 855.9438 | 486.6397 |  | 295.8991 | 561.6818 | 375.3306 | 571.3093 | 746.243 | 881.1317 | 928.0235 | 35.2104 | 274.1678 | 53.3707 | 488.9752 | 13.7878 | 48.6561 | 48.0144 | 47.3439 | 36.9297 |  |  | 0.076443 | -0.082053 | -1.1961 | -1.0488 | 6.9676 | 5.4779 | 5.4441 | -2.994 | 14.6746 | 38.1249 | 32.2102 | 0.00084932 | 0.00083454 | 1.5862 | 16.8277 | 16.5208 | 17.0505 | 17.3802 | 17.3353 | 16.2707 | 14.6228 | 16.7039 | 17.0443 | 17.3468 | 17.382 | 17.0897 | 16.2412 | 14.4197 | 772.7427 | 359.0812 | 532.1554 | 322.8042 | 257.8263 | 693.2737 | 412.1702 | 15.5708 | 16.2869 | 17.677 | 23.9061 | 55.3576 | 69.3369 |  |  |  | 565.2549 | 543.6942 | 541.3977 | 570.4866 | 74.0287 | 39.4626 | 810.1958 |  |  | 398.2898 |  |  | 17.4399 | 26.3093 | 244.5686 | 16.5158 | 20.7524 | 840.7704 | 735.1907 | 578.9526 | 802.0511 | 798.8183 | 729.5638 |  | 772.1011 | 829.0473 | 924.1918 | 567.1281 | 644.8189 | 833.0163 |  | 928.7164 |  |  | 380.092 | 602.3712 | 711.5279 | [6 empty] | 569.4745 |  |  | 357.8426 |  |  | 446.2445 | 621.3297 | 643.4081 | 749.1584 | 987.966 | 976.9792 | 499.6911 | 676.8788 | 779.3941 | 574.3859 | 647.8482 | 922.8231 | 1015.8638 | 595.9709 | 760.0219 | 790.3347 | 1020.9963 | 1010.4964 | 485.565 | 588.2004 | 665.7224 | 536.1221 | 686.5849 | 837.9787 | 956.939 | 1034.3525 | 549.2881 | 634.0023 | 618.1413 | 787.269 | 76.129 | 0.03218 | 18.2765 | 3.3907 | -38.7365 | 3.124 | 10684.73 | 0.39 | 0.58786 | -0.57678 | -2.2021 | -2.0621 | 6.2498 | 5.5415 | 5.5244 | 68.8624 | 119.1777 | 42.42 | 40.63 | -0.82457 | 82.0821 | 27.8702
42810.4501 | 868 | 18.109 | 18.3754 | 18.4008 | 18.4001 | 17.6881 | 16.2838 | 14.5017 | 16.5306 | 17.0318 | 17.1312 | 17.139 | 16.6409 | 15.6398 | 14.2764 | 14.4908 | 15.286 | 16.6497 | 20.6882 | 24.0984 | 67.9365 |  |  |  | 17.0343 | 24.4448 | 145.7682 | 644.963 | 693.9069 | 654.5198 | 76.5156 | 72.6243 | 839.9334 | 71.9812 | 80.9063 | 785.6036 | 801.8781 | 647.6372 |  | 330.0606 | 867.6792 | 860.2268 | 515.3289 |  | 297.4736 | 563.9339 | 376.2288 | 571.7399 | 748.3237 | 883.1425 | 930.3746 | 35.2414 | 275.3413 | 53.4693 | 490.6527 | 13.766 | 48.6263 | 48.0446 | 47.3739 | 36.7044 |  |  | 0.039647 | -0.51838 | -0.50413 | -1.1335 | 6.8414 | 5.3623 | 6.4955 | -2.578 | 15.8803 | 39.6438 | 33.645 | 0.00090025 | 0.00078525 | 1.5865 | 16.8367 | 16.5216 | 17.056 | 17.3843 | 17.3305 | 16.2766 | 14.6333 | 16.699 | 17.0498 | 17.3481 | 17.3941 | 17.0956 | 16.2475 | 14.4284 | 767.0452 | 350.4649 | 549.6993 | 335.7164 | 284.4263 | 693.7063 | 413.3721 | 15.5685 | 16.3035 | 17.7089 | 24.0792 | 55.6863 | 69.5588 |  |  |  | 565.534 | 542.1022 | 540.0967 | 564.6625 | 79.1512 | 38.5492 | 813.0611 |  |  | 398.3844 |  |  | 17.4397 | 26.4363 | 241.5448 | 16.5023 | 20.8665 | 839.9331 | 734.4202 | 579.8679 | 803.3033 | 799.9876 | 728.2557 |  | 773.1009 | 832.1996 | 925.2403 | 568.1807 | 645.2387 | 834.2642 |  | 929.3446 |  |  | 382.1227 | 602.5924 | 710.741 | [6 empty] | 570.6986 |  |  | 359.1187 |  |  | 446.6732 | 621.6032 | 642.0192 | 748.6158 | 986.2227 | 978.7648 | 500.6048 | 678.4083 | 777.9338 | 574.9269 | 647.5734 | 920.0952 | 1016.1107 | 597.5265 | 760.7771 | 790.4713 | 1020.5223 | 1010.4112 | 486.1317 | 588.0805 | 662.3659 | 538.2679 | 689.7169 | 840.8137 | 962.8801 | 1033.5439 | 550.2788 | 632.7161 | 620.3696 | 792.3657 | 76.2821 | 0.029528 | 18.2757 | 3.3881 | -38.7281 | 3.124 | 10711.33 | 0.27 | 0.42264 | -1.4517 | -1.4316 | -2.1467 | 6.1983 | 5.4875 | 6.0396 | 69.1859 | 119.528 | 42.4762 | 41.3998 | -2.5524 | 83.6887 | 28.077
42810.4501 | 869 | 18.0991 | 18.3576 | 18.4008 | 18.3843 | 17.6828 | 16.2754 | 14.4929 | 16.5304 | 17.0223 | 17.1314 | 17.1306 | 16.6414 | 15.6418 | 14.2743 | 14.4819 | 15.2907 | 16.6684 | 20.8615 | 23.9269 | 68.3367 |  |  |  | 17.0327 | 24.8277 | 149.8652 | 647.4246 | 696.1656 | 659.0176 | 62.2941 | 77.1182 | 848.3521 | 76.2014 | 76.0371 | 800.4828 | 800.677 | 655.7364 |  | 298.5594 | 851.1232 | 856.0331 | 516.0167 |  | 298.6487 | 564.2671 | 377.5739 | 573.9981 | 747.508 | 879.4262 | 930.7462 | 35.8685 | 276.3821 | 54.0266 | 491.8887 | 13.7416 | 48.6279 | 48.0972 | 47.4229 | 36.4714 |  |  | 0.15464 | -0.11031 | -0.33985 | -1.1592 | 7.0116 | 5.9011 | 6.1794 | -3.0203 | 15.6028 | 39.5272 | 32.7836 | 0.00087232 | 0.00078854 | 1.5859 | 16.8403 | 16.5169 | 17.0512 | 17.3836 | 17.3298 | 16.2759 | 14.6292 | 16.7012 | 17.053 | 17.3489 | 17.3911 | 17.0916 | 16.2425 | 14.4301 | 775.3789 | 357.9384 | 542.6266 | 328.9072 | 277.9099 | 694.6003 | 414.5385 | 15.5645 | 16.3207 | 17.7464 | 24.2297 | 55.9856 | 69.7642 |  |  |  | 565.456 | 538.0473 | 538.2157 | 556.5373 | 76.8718 | 33.123 | 813.7832 |  |  | 396.6085 |  |  | 17.4435 | 26.5581 | 249.4028 | 16.5105 | 20.9809 | 844.3799 | 733.8355 | 580.2852 | 804.1832 | 800.3589 | 727.6482 |  | 773.8309 | 844.2152 | 925.3425 | 568.7573 | 645.6261 | 834.9342 |  | 929.7813 |  |  | 383.7962 | 604.3785 | 710.3109 | [6 empty] | 571.3897 |  |  | 360.381 |  |  | 447.2653 | 621.9674 | 640.9063 | 748.4492 | 984.0375 | 981.0233 | 501.367 | 680.0247 | 778.1439 | 575.7044 | 647.1026 | 918.0136 | 1016.0462 | 598.9208 | 764.3495 | 793.109 | 1023.2448 | 1010.2724 | 486.8857 | 588.1753 | 661.5599 | 540.157 | 691.6345 | 843.9564 | 964.8851 | 1034.1919 | 550.5697 | 631.6486 | 622.1454 | 795.489 | 75.6458 | 0.02567 | 18.2757 | 3.3851 | -38.683 | 3.1239 | 10682.86 | 0.21 | 0.83672 | -0.6698 | -1.1757 | -2.1712 | 6.2648 | 5.7474 | 5.8813 | 69.4128 | 119.237 | 42.539 | 40.7567 | -1.5511 | 83.2984 | 28.2901
42810.4501 | 870 | 18.096 | 18.3558 | 18.3935 | 18.3856 | 17.6745 | 16.2735 | 14.4913 | 16.5297 | 17.0217 | 17.1311 | 17.1301 | 16.6398 | 15.6347 | 14.2782 | 14.4807 | 15.3092 | 16.6814 | 21.049 | 23.7724 | 68.7521 |  |  |  | 17.0324 | 25.2279 | 155.0135 | 650.4545 | 698.2248 | 661.7362 | 58.782 | 69.9499 | 861.8157 | 70.4933 | 74.9247 | 813.946 | 800.7217 | 682.2147 |  | 307.9719 | 850.7822 | 842.146 | 493.7541 |  | 298.6004 | 566.9322 | 379.3146 | 574.1092 | 747.6882 | 874.2708 | 930.9808 | 36.4752 | 277.3906 | 54.9276 | 492.9023 | 13.6968 | 48.6728 | 48.1481 | 47.4751 | 36.2439 |  |  | -0.2554 | 0.12625 | -0.96345 | -1.0389 | 6.9991 | 6.3644 | 7.0534 | -2.9237 | 15.8239 | 39.5236 | 31.2506 | 0.0008329 | 0.00089861 | 1.5859 | 16.8463 | 16.5175 | 17.0416 | 17.3768 | 17.3262 | 16.2684 | 14.6171 | 16.6977 | 17.0487 | 17.3503 | 17.3854 | 17.0908 | 16.2424 | 14.4304 | 781.0547 | 362.4438 | 520.5457 | 319.1786 | 267.3835 | 695.7839 | 415.5456 | 15.57 | 16.3392 | 17.7814 | 24.3795 | 56.285 | 69.9629 |  |  |  | 565.5217 | 536.0486 | 536.3998 | 556.4794 | 85.6261 | 37.8393 | 814.7661 |  |  | 403.2028 |  |  | 17.4416 | 26.6767 | 255.2775 | 16.5194 | 21.0903 | 850.893 | 732.7014 | 580.7638 | 803.3634 | 800.0113 | 726.4093 |  | 774.2073 | 853.4972 | 924.7658 | 569.7892 | 646.0501 | 837.1997 |  | 930.0333 |  |  | 384.8164 | 605.8868 | 709.651 | [6 empty] | 571.9688 |  |  | 361.3652 |  |  | 447.9696 | 622.4964 | 641.103 | 748.6195 | 980.6995 | 984.5866 | 502.1302 | 681.2905 | 779.4651 | 576.5382 | 647.4233 | 914.2047 | 1016.9073 | 599.9505 | 766.7966 | 793.8996 | 1027.8006 | 1011.2937 | 487.3537 | 588.2389 | 663.5296 | 541.7658 | 693.0034 | 845.1749 | 963.9152 | 1036.6996 | 550.1301 | 631.1792 | 623.8598 | 794.2102 | 76.3749 | 0.016957 | 18.2759 | 3.3834 | -38.7359 | 3.124 | 10683.25 | 0.27 | -1.0768 | 0.71772 | -1.9826 | -2.0588 | 6.2452 | 5.9553 | 6.2694 | 69.5557 | 118.7381 | 42.5968 | 40.5012 | 1.0887 | 83.9306 | 28.3023
42810.4501 | 871 | 18.0807 | 18.3486 | 18.3936 | 18.3786 | 17.6691 | 16.2672 | 14.4867 | 16.5233 | 17.0203 | 17.1283 | 17.129 | 16.6322 | 15.6303 | 14.2711 | 14.4773 | 15.3319 | 16.6988 | 21.2507 | 23.8183 | 69.17 |  |  |  | 17.0447 | 25.6868 | 152.0071 | 651.5612 | 697.9849 | 661.3515 | 69.9712 | 56.4023 | 860.3759 | 50.0552 | 56.2677 | 812.3385 | 795.4331 | 688.7085 |  | 296.3219 | 862.4371 | 881.4557 | 472.3198 |  | 299.8202 | 568.5091 | 380.5572 | 574.3249 | 745.9064 | 874.4934 | 932.7331 | 36.7795 | 278.5314 | 55.5929 | 494.0033 | 13.6558 | 48.749 | 48.1735 | 47.527 | 35.9917 |  |  | 0.083015 | -0.15565 | -1.2092 | -1.4108 | 6.1626 | 6.003 | 6.8845 | -3.2457 | 16.2343 | 40.4153 | 28.63 | 0.00079347 | 0.00084932 | 1.5837 | 16.865 | 16.516 | 17.0401 | 17.3816 | 17.3365 | 16.2725 | 14.6281 | 16.7095 | 17.0568 | 17.3533 | 17.3975 | 17.0974 | 16.2459 | 14.4286 | 790.2031 | 380.5654 | 528.4904 | 320.1009 | 267.8624 | 697.3261 | 416.6218 | 15.5678 | 16.3565 | 17.8146 | 24.5323 | 56.5848 | 70.1619 |  |  |  | 565.7678 | 535.3724 | 535.3431 | 557.4202 | 85.8597 | 41.2243 | 813.9152 |  |  | 408.2826 |  |  | 17.4373 | 26.8043 | 253.1728 | 16.524 | 21.1999 | 847.4222 | 731.6266 | 581.0342 | 801.4117 | 799.3289 | 724.7592 |  | 774.3612 | 856.7193 | 924.0667 | 570.4922 | 646.3954 | 836.861 |  | 930.6964 |  |  | 386.2991 | 608.2874 | 709.0894 | [6 empty] | 572.4614 |  |  | 361.9423 |  |  | 448.9266 | 622.8054 | 642.2419 | 749.2958 | 979.8082 | 986.6416 | 502.8609 | 681.7894 | 780.8288 | 576.7097 | 648.7798 | 912.4238 | 1017.989 | 600.4439 | 766.0523 | 794.3817 | 1028.7768 | 1011.0927 | 487.5081 | 588.7266 | 664.5031 | 543.2252 | 693.9407 | 845.2635 | 963.8514 | 1035.5271 | 549.619 | 631.8649 | 625.3357 | 792.9131 | 78.0987 | 0.0083002 | 18.2767 | 3.3822 | -38.7283 | 3.124 | 10662.86 | 0.29 | 0.61381 | -0.79764 | -2.2232 | -2.4014 | 5.8607 | 5.7843 | 6.1945 | 69.6459 | 118.3569 | 42.6477 | 39.9751 | 0.40542 | 82.9046 | 28.316
42810.4501 | 872 | 18.0786 | 18.3471 | 18.3904 | 18.3803 | 17.6641 | 16.2686 | 14.4919 | 16.5234 | 17.0242 | 17.1249 | 17.123 | 16.6332 | 15.6291 | 14.2693 | 14.4761 | 15.3538 | 16.7221 | 21.4554 | 23.7424 | 69.5777 |  |  |  | 17.0589 | 26.1928 | 148.7529 | 649.565 | 697.5866 | 658.5991 | 101.3808 | 120.7094 | 936.6974 | 43.6051 | 84.1368 | 859.7017 | 678.0109 | 836.448 |  | 286.1656 | 919.9442 | 932.7251 | 463.1612 |  | 300.1432 | 568.5463 | 382.6584 | 575.2988 | 742.6634 | 870.7265 | 933.4054 | 36.9137 | 279.4962 | 57.0674 | 495.2308 | 13.6069 | 48.8207 | 48.1929 | 47.5815 | 35.836 |  |  | 0.34784 | 0.21102 | -0.89708 | -1.6494 | 7.3086 | 6.1593 | 6.4567 | -2.7252 | 16.0477 | 41.0115 | 26.4282 | 0.00085918 | 0.00080004 | 1.5839 | 16.866 | 16.5035 | 17.0434 | 17.3733 | 17.3315 | 16.2683 | 14.6217 | 16.6995 | 17.0528 | 17.343 | 17.3887 | 17.0925 | 16.2438 | 14.425 | 799.4246 | 408.1375 | 537.5257 | 324.2477 | 271.0019 | 699.2278 | 417.942 | 15.5599 | 16.3612 | 17.8474 | 24.7048 | 56.9107 | 70.3667 |  |  |  | 566.0765 | 535.99 | 535.3823 | 560.215 | 100.1941 | 47.0047 | 812.7831 |  |  | 404.7996 |  |  | 17.4467 | 26.9275 | 249.3761 | 16.5355 | 21.3066 | 852.7791 | 731.5096 | 580.655 | 804.1534 | 801.8721 | 725.8083 |  | 774.6883 | 866.5479 | 924.1064 | 570.1185 | 646.6178 | 834.6185 |  | 931.5365 |  |  | 387.7774 | 611.6934 | 709.9063 | [6 empty] | 572.2333 |  |  | 362.1859 |  |  | 449.632 | 622.6959 | 643.1741 | 747.9671 | 980.5568 | 988.4587 | 503.434 | 682.451 | 784.3705 | 576.3265 | 649.7617 | 914.5477 | 1018.4228 | 601.09 | 765.3389 | 795.1111 | 1027.2519 | 1010.8677 | 487.298 | 589.392 | 663.9854 | 544.4799 | 694.3023 | 845.8373 | 964.0651 | 1033.7028 | 549.862 | 632.3569 | 626.431 | 792.414 | 83.9618 | 0.0042383 | 18.2764 | 3.3825 | -38.7578 | 3.124 | 10637.88 | 0.23 | 1.2546 | 0.92877 | -1.915 | -2.5966 | 6.372 | 5.8496 | 5.9891 | 69.7112 | 118.1004 | 42.7035 | 39.5571 | -0.35326 | 52.3767 | 28.2883
42810.4501 | 873 | 18.0801 | 18.3533 | 18.3917 | 18.3887 | 17.679 | 16.2793 | 14.5003 | 16.5246 | 17.0268 | 17.1359 | 17.1307 | 16.6417 | 15.644 | 14.2791 | 14.4701 | 15.3566 | 16.7358 | 21.6461 | 23.7129 | 69.9722 |  |  |  | 17.0516 | 26.7156 | 151.6356 | 649.9997 | 698.9393 | 660.0659 | 120.8365 | 139.038 | 959.0829 | 21.1279 | 115.4804 | 884.8673 | 500.1586 | 910.9754 |  | 279.0231 | 939.4978 | 935.3457 | 464.6463 |  | 300.0992 | 569.7124 | 383.0559 | 576.2494 | 743.9788 | 872.4182 | 932.7105 | 37.164 | 280.7225 | 58.7706 | 496.764 | 13.5669 | 48.8533 | 48.2064 | 47.6338 | 35.6269 |  |  | 0.095499 | 0.044115 | -0.93322 | -1.1986 | 6.5575 | 5.1047 | 6.5244 | -3.0038 | 17.2579 | 40.5506 | 27.0048 | 0.00077047 | 0.00084604 | 1.5865 | 16.8825 | 16.5103 | 17.0422 | 17.3812 | 17.3303 | 16.2713 | 14.6281 | 16.6993 | 17.0477 | 17.3469 | 17.3884 | 17.0919 | 16.2503 | 14.4326 | 821.1336 | 420.6608 | 565.6186 | 330.8956 | 278.6086 | 701.9741 | 420.0398 | 15.5616 | 16.3904 | 17.8855 | 24.8633 | 57.2274 | 70.5624 |  |  |  | 566.4287 | 536.2297 | 535.2737 | 560.9344 | 91.7647 | 49.4198 | 815.7368 |  |  | 407.8765 |  |  | 17.4488 | 27.0646 | 255.3624 | 16.5391 | 21.4417 | 853.0486 | 734.2292 | 580.3703 | 807.5518 | 806.5922 | 728.4624 |  | 775.3548 | 875.1435 | 924.817 | 569.5946 | 646.849 | 836.332 |  | 931.943 |  |  | 389.1389 | 615.4251 | 712.1583 | [6 empty] | 571.7788 |  |  | 362.1417 |  |  | 449.6223 | 622.6198 | 643.5836 | 747.4137 | 982.4433 | 989.5668 | 504.3773 | 683.3185 | 786.2329 | 575.8921 | 649.6398 | 918.5455 | 1019.4412 | 602.0138 | 765.9165 | 796.9176 | 1024.3821 | 1012.8729 | 487.0524 | 589.9009 | 662.9111 | 545.5073 | 694.2016 | 848.2584 | 963.4348 | 1032.9601 | 550.1122 | 631.8453 | 627.2293 | 792.4299 | 81.0166 | 0.0039647 | 18.2764 | 3.3838 | -38.7937 | 3.1239 | 10659.15 | 0.27 | 0.6579 | 0.42495 | -1.9545 | -2.215 | 6.0401 | 5.3292 | 6.0249 | 69.83 | 118.1582 | 42.7653 | 38.0252 | -3.0839 | 21.263 | 28.3253
42810.4502 | 874 | 18.0702 | 18.3503 | 18.3887 | 18.3946 | 17.6729 | 16.2809 | 14.4993 | 16.5237 | 17.0312 | 17.1309 | 17.1333 | 16.6413 | 15.6404 | 14.271 | 14.469 | 15.3854 | 16.7637 | 21.8518 | 23.7562 | 70.3607 |  |  |  | 17.0456 | 27.2842 | 152.641 | 653.558 | 699.8549 | 665.8304 | 115.6347 | 127.5392 | 954.915 | 12.5915 | 130.8487 | 898.7827 | 599.3239 | 913.508 |  | 287.0888 | 930.5007 | 927.8841 | 496.2803 |  | 300.9645 | 570.66 | 383.2011 | 575.163 | 745.8306 | 871.3025 | 936.654 | 37.1165 | 281.8334 | 59.0271 | 498.0702 | 13.4973 | 48.8732 | 48.2416 | 47.6737 | 35.5961 |  |  | 0.40238 | 0.35953 | -0.48244 | -1.1953 | 6.9846 | 6.392 | 6.7038 | -3.1859 | 16.3696 | 40.393 | 27.1823 | 0.00079675 | 0.00085754 | 1.5909 | 16.887 | 16.5019 | 17.0355 | 17.3756 | 17.324 | 16.2699 | 14.6256 | 16.693 | 17.0524 | 17.3486 | 17.3885 | 17.0892 | 16.2481 | 14.4312 | 823.0902 | 410.882 | 584.5906 | 331.8891 | 278.0712 | 704.202 | 422.2933 | 15.5519 | 16.4 | 17.9147 | 25.0205 | 57.5174 | 70.7438 |  |  |  | 566.5524 | 534.6512 | 534.732 | 558.3084 | 73.3972 | 42.9934 | 819.94 |  |  | 416.4384 |  |  | 17.4486 | 27.1743 | 257.2612 | 16.5435 | 21.5499 | 855.5623 | 734.4079 | 580.4363 | 809.8494 | 809.191 | 731.9851 |  | 776.1926 | 880.613 | 925.3887 | 569.5153 | 647.2152 | 841.9478 |  | 931.77 |  |  | 390.4797 | 618.0575 | 714.0321 | [6 empty] | 571.6344 |  |  | 361.8368 |  |  | 449.7037 | 622.8227 | 644.1722 | 745.8334 | 984.0416 | 989.6304 | 505.1451 | 683.1766 | 785.9315 | 575.7866 | 649.3633 | 916.9863 | 1016.9138 | 602.4979 | 765.5854 | 799.34 | 1022.3473 | 1014.6538 | 487.2155 | 590.0796 | 664.4411 | 546.4744 | 694.7886 | 851.1293 | 963.7961 | 1032.318 | 550.2012 | 632.2606 | 627.8731 | 798.4815 | 78.5891 | -0.00027956 | 18.2771 | 3.3848 | -38.7883 | 3.1239 | 10700.22 | 0.21 | 1.3546 | 1.2138 | -1.4061 | -2.2132 | 6.2307 | 5.9605 | 6.1042 | 69.9748 | 118.2452 | 42.8424 | 38.5255 | -4.7704 | 35.7167 | 28.4183
42810.4502 | 875 | 18.0774 | 18.3417 | 18.3836 | 18.3864 | 17.6719 | 16.2789 | 14.4935 | 16.5252 | 17.0275 | 17.1269 | 17.1324 | 16.6355 | 15.635 | 14.2743 | 14.4638 | 15.3965 | 16.7822 | 22.0569 | 23.6756 | 70.7828 |  |  |  | 17.0496 | 27.8969 | 153.367 | 657.3986 | 699.0846 | 670.6835 | 114.6711 | 120.0649 | 956.5314 | 18.6372 | 129.6138 | 902.5529 | 449.204 | 922.8279 |  | 275.549 | 931.6963 | 940.1203 | 483.8323 |  | 301.5015 | 571.1246 | 384.3476 | 576.6063 | 745.9725 | 871.6833 | 938.0683 | 36.9065 | 282.922 | 59.2427 | 499.2556 | 13.4791 | 48.9025 | 48.2717 | 47.7174 | 35.5541 |  |  | 0.53708 | 0.50015 | -0.58627 | -1.1808 | 6.3768 | 6.3959 | 6.4712 | -3.176 | 16.3003 | 40.984 | 28.3087 | 0.0008214 | 0.00078854 | 1.5918 | 16.8913 | 16.4953 | 17.0336 | 17.3675 | 17.3195 | 16.2652 | 14.6197 | 16.7002 | 17.0462 | 17.3458 | 17.385 | 17.0893 | 16.245 | 14.4304 | 807.6693 | 429.7636 | 575.2686 | 330.8424 | 267.9464 | 705.6168 | 423.8954 | 15.5515 | 16.4223 | 17.9564 | 25.1808 | 57.8154 | 70.929 |  |  |  | 566.959 | 535.7988 | 537.9578 | 563.7505 | 98.3524 | 50.7542 | 820.9586 |  |  | 415.3224 |  |  | 17.4545 | 27.2972 | 256.6871 | 16.5348 | 21.681 | 861.9906 | 732.4607 | 580.8337 | 806.7278 | 804.7442 | 728.594 |  | 776.6129 | 866.7588 | 924.7306 | 569.4613 | 647.5778 | 838.4831 |  | 931.0294 |  |  | 391.1645 | 616.8969 | 712.5401 | [6 empty] | 571.9671 |  |  | 362.5007 |  |  | 449.9258 | 623.115 | 644.2845 | 743.5392 | 978.8887 | 988.6205 | 505.7775 | 682.4855 | 785.5609 | 576.468 | 649.1233 | 910.3965 | 1016.0052 | 602.6399 | 763.5252 | 801.2423 | 1019.5735 | 1014.9435 | 487.9992 | 590.3331 | 668.3519 | 547.4631 | 696.1629 | 852.7163 | 963.1955 | 1029.3745 | 549.9721 | 635.0993 | 628.7554 | 800.5377 | 82.9615 | -0.0010162 | 18.2773 | 3.3851 | -38.8049 | 3.1239 | 10751.26 | 0.34 | 1.569 | 1.4321 | -1.5504 | -2.2004 | 5.9544 | 5.9633 | 5.9983 | 70.1908 | 118.355 | 42.9181 | 40.6964 | -3.434 | 14.4758 | 28.3331
42810.4502 | 876 | 18.0724 | 18.3432 | 18.388 | 18.3809 | 17.6744 | 16.2747 | 14.5009 | 16.5326 | 17.0249 | 17.1288 | 17.1343 | 16.6346 | 15.639 | 14.2757 | 14.4625 | 15.4136 | 16.7996 | 22.2703 | 23.7362 | 71.2212 |  |  |  | 17.0562 | 28.5584 | 153.2439 | 657.4161 | 698.8451 | 670.1538 | 111.1702 | 117.5496 | 958.4907 | 39.5137 | 124.1127 | 895.7881 | 534.1518 | 923.7772 |  | 262.7945 | 945.7755 | 946.6318 | 475.8699 |  | 302.2791 | 572.1757 | 385.257 | 581.4716 | 744.8943 | 876.1788 | 938.276 | 37.0432 | 284.086 | 60.0928 | 500.3671 | 13.4743 | 48.9317 | 48.314 | 47.7766 | 35.3517 |  |  | 0.037019 | 0.007315 | -0.87803 | -1.5482 | 6.2099 | 5.9878 | 5.9468 | -2.6142 | 16.1625 | 39.959 | 27.2935 | 0.00079511 | 0.00077704 | 1.5906 | 16.8999 | 16.5011 | 17.0271 | 17.369 | 17.3188 | 16.2696 | 14.6222 | 16.6993 | 17.0465 | 17.3467 | 17.3876 | 17.0917 | 16.2533 | 14.426 | 828.1744 | 441.6636 | 599.599 | 345.741 | 281.8899 | 707.969 | 426.0894 | 15.5437 | 16.4396 | 17.9923 | 25.3331 | 58.1049 | 71.1204 |  |  |  | 567.9581 | 542.4483 | 544.4246 | 575.2794 | 83.5616 | 39.7535 | 815.6464 |  |  | 409.7007 |  |  | 17.4478 | 27.4164 | 255.9791 | 16.4192 | 21.8002 | 865.5685 | 731.0827 | 581.3897 | 804.0969 | 800.4587 | 726.5585 |  | 776.9831 | 845.5991 | 923.7712 | 570.1042 | 647.8984 | 830.7867 |  | 930.7148 |  |  | 391.3827 | 616.0272 | 710.7773 | [6 empty] | 572.69 |  |  | 363.425 |  |  | 451.0905 | 624.4867 | 644.2909 | 744.3765 | 971.5216 | 988.0317 | 506.2754 | 682.2104 | 783.9755 | 577.5393 | 649.0665 | 907.8323 | 1012.2149 | 603.0028 | 761.8656 | 799.1573 | 1016.625 | 1014.0182 | 488.1432 | 590.9081 | 670.4075 | 548.3617 | 697.2677 | 853.0002 | 963.1243 | 1027.2093 | 550.5815 | 636.3824 | 630.0847 | 798.5365 | 81.0052 | 0.0016005 | 18.2773 | 3.3815 | -38.8152 | 3.1239 | 10751.37 | 0.29 | 0.41182 | 0.1733 | -1.8986 | -2.5211 | 5.8875 | 5.7813 | 5.7614 | 70.3548 | 118.5426 | 42.9659 | 39.1814 | -5.7243 | 25.7028 | 28.1752
42810.4502 | 877 | 18.0707 | 18.3422 | 18.3917 | 18.3821 | 17.6791 | 16.2722 | 14.5052 | 16.5328 | 17.0278 | 17.1315 | 17.1366 | 16.6379 | 15.6373 | 14.2803 | 14.46 | 15.4422 | 16.8215 | 22.4763 | 23.7977 | 71.5883 |  |  |  | 17.0609 | 29.2678 | 152.2912 | 655.0358 | 699.015 | 665.9096 | 107.3877 | 114.3076 | 964.4039 | 53.2497 | 127.2914 | 900.1225 | 479.7167 | 920.0477 |  | 255.6628 | 950.1578 | 957.8156 | 447.1202 |  | 303.0809 | 572.7156 | 386.5565 | 581.2116 | 742.4432 | 879.7322 | 937.0554 | 37.6785 | 285.0111 | 61.6279 | 501.4479 | 13.465 | 48.9815 | 48.3558 | 47.8237 | 35.1607 |  |  | -0.58593 | 0.17882 | -0.55998 | -1.0376 | 6.568 | 5.2808 | 6.9476 | -2.6267 | 16.2478 | 41.0151 | 28.41 | 0.00072447 | 0.00083125 | 1.59 | 16.9116 | 16.5039 | 17.0331 | 17.3687 | 17.3232 | 16.2593 | 14.6164 | 16.6967 | 17.0449 | 17.3466 | 17.391 | 17.0891 | 16.2488 | 14.4302 | 824.5915 | 461.4663 | 582.8917 | 349.767 | 282.788 | 709.4842 | 427.553 | 15.544 | 16.4605 | 18.0415 | 25.5133 | 58.4314 | 71.3359 |  |  |  | 568.9648 | 545.8887 | 547.4053 | 573.1942 | 88.8069 | 49.0924 | 811.4555 |  |  | 406.5726 |  |  | 17.4518 | 27.5323 | 255.621 | 16.5128 | 21.9129 | 871.2651 | 731.5081 | 581.9465 | 803.0745 | 798.1524 | 726.2024 |  | 777.3747 | 833.8513 | 923.3401 | 570.8614 | 648.1167 | 826.6641 |  | 930.0816 |  |  | 392.076 | 615.1406 | 710.4136 | [6 empty] | 573.3421 |  |  | 365.2222 |  |  | 452.2777 | 625.9489 | 644.1106 | 752.2044 | 970.1367 | 988.3034 | 506.6931 | 682.02 | 782.7046 | 578.751 | 649.1016 | 909.9661 | 1010.5498 | 603.7108 | 760.508 | 799.9834 | 1014.5978 | 1015.9306 | 488.0034 | 591.9317 | 668.6383 | 550.068 | 698.7163 | 853.8579 | 964.5467 | 1026.897 | 551.477 | 635.4522 | 631.425 | 798.3303 | 79.8816 | 0.00028867 | 18.2773 | 3.3754 | -38.7961 | 3.1239 | 10748.74 | 0.32 | -1.6347 | 0.8571 | -1.5167 | -2.0646 | 6.0643 | 5.4376 | 6.237 | 70.4785 | 118.6894 | 42.9896 | 40.0731 | -3.5914 | 19.1216 | 28.3972
42810.4502 | 878 | 18.0674 | 18.3422 | 18.3914 | 18.3841 | 17.6708 | 16.2725 | 14.5076 | 16.5298 | 17.0259 | 17.1302 | 17.1397 | 16.6422 | 15.6395 | 14.2866 | 14.4523 | 15.4512 | 16.8334 | 22.6796 | 23.7802 | 71.9281 |  |  |  | 17.0621 | 30.0352 | 152.7693 | 655.4597 | 699.0153 | 665.4598 | 117.1881 | 115.1794 | 966.6717 | 59.3947 | 122.5926 | 894.3994 | 349.0948 | 915.7581 |  | 267.3411 | 945.0389 | 950.821 | 456.9115 |  | 303.6594 | 574.7812 | 388.7538 | 580.8822 | 741.8084 | 872.2148 | 937.498 | 38.5395 | 286.1182 | 61.714 | 502.7167 | 13.3873 | 49.0487 | 48.4001 | 47.879 | 35.0495 |  |  | -0.12135 | 0.39304 | -0.77355 | -1.0415 | 6.5641 | 5.2768 | 5.9652 | -2.8442 | 16.1226 | 39.3902 | 28.0822 | 0.00080168 | 0.00074418 | 1.3926 | 16.923 | 16.5084 | 17.0365 | 17.3703 | 17.3218 | 16.2691 | 14.6209 | 16.6943 | 17.0536 | 17.3587 | 17.3977 | 17.1026 | 16.2474 | 14.4354 | 815.9097 | 468.0417 | 593.6453 | 351.8773 | 289.3913 | 711.0978 | 429.6514 | 15.5484 | 16.483 | 18.0875 | 25.6742 | 58.725 | 71.5078 |  |  |  | 569.2424 | 543.755 | 547.145 | 566.0205 | 78.2573 | 39.3733 | 809.4332 |  |  | 404.4011 |  |  | 17.452 | 27.6658 | 256.4206 | 16.5536 | 22.0488 | 874.4482 | 732.0473 | 583.414 | 798.7143 | 793.2988 | 727.2178 |  | 777.9495 | 824.739 | 923.2904 | 572.5217 | 648.4522 | 821.1686 |  | 930.14 |  |  | 392.3508 | 614.1397 | 711.528 | [6 empty] | 575.0109 |  |  | 368.2177 |  |  | 452.9251 | 626.7551 | 643.4232 | 750.0735 | 972.6583 | 990.0022 | 507.2041 | 682.0566 | 783.9619 | 580.895 | 649.0196 | 908.5595 | 1016.238 | 604.0564 | 758.7974 | 803.5816 | 1015.5915 | 1016.3566 | 488.4855 | 592.8395 | 666.7866 | 551.3807 | 700.0372 | 853.7005 | 966.4544 | 1026.3873 | 552.3198 | 635.4992 | 633.2063 | 797.2684 | 81.7102 | 0.00015539 | 18.2775 | 3.3576 | -38.7608 | 3.1239 | 10778.4 | 0.32 | -0.74375 | 1.2722 | -1.7848 | -2.071 | 6.0426 | 5.4178 | 5.7604 | 70.6176 | 118.9218 | 43.0124 | 41.5652 | -4.3886 | 5.5053 | 28.6418
42810.4502 | 879 | 18.062 | 18.3412 | 18.3861 | 18.3809 | 17.6657 | 16.2802 | 14.5045 | 16.526 | 17.0284 | 17.1317 | 17.1368 | 16.6389 | 15.6415 | 14.2807 | 14.4439 | 15.4615 | 16.8622 | 22.9051 | 23.8143 | 72.3143 |  |  |  | 17.0695 | 30.8609 | 153.9357 | 654.1964 | 698.3938 | 662.7916 | 121.9561 | 111.5004 | 945.2909 | 74.4106 | 103.5217 | 874.8545 | 649.8321 | 904.1115 |  | 278.259 | 938.6809 | 943.8494 | 484.6458 | 1106.7445 | 304.0828 | 578.4536 | 389.7228 | 580.8642 | 747.2826 | 872.0203 | 937.9298 | 37.771 | 287.094 | 61.4465 | 503.608 | 13.3379 | 49.0693 | 48.4182 | 47.9061 | 34.9641 |  |  | 0.21115 | 0.040171 | -0.13089 | -1.0547 | 6.342 | 6.1403 | 6.0506 | -2.0937 | 16.1709 | 40.979 | 27.887 | 0.00071297 | 0.00078197 | 0.24715 | 16.9344 | 16.5062 | 17.0391 | 17.3714 | 17.3249 | 16.2782 | 14.6195 | 16.7072 | 17.06 | 17.3565 | 17.401 | 17.0965 | 16.2553 | 14.4404 | 807.5918 | 478.7434 | 570.8739 | 340.6036 | 281.0745 | 712.2321 | 431.1736 | 15.5483 | 16.5055 | 18.136 | 25.8418 | 59.0179 | 71.6924 |  |  |  | 569.3785 | 541.2872 | 545.8883 | 563.5245 | 99.114 | 41.5902 | 805.4439 |  |  | 404.5327 |  |  | 17.4555 | 27.7834 | 256.9808 | 16.5508 | 22.1615 | 869.3284 | 732.6066 | 585.3309 | 793.313 | 787.8429 | 727.301 |  | 778.4586 | 814.3704 | 922.6732 | 575.2855 | 648.928 | 817.8845 |  | 930.6981 |  |  | 392.9784 | 613.0473 | 711.6697 | [6 empty] | 577.7078 |  |  | 371.9366 |  |  | 453.7632 | 626.7041 | 642.4932 | 750.1707 | 978.2569 | 992.0081 | 507.5693 | 681.8831 | 784.0299 | 582.1251 | 649.0284 | 907.9879 | 1019.9164 | 604.7977 | 760.5666 | 801.7911 | 1025.5425 | 1017.3148 | 488.6363 | 593.3784 | 667.5427 | 552.2967 | 701.3949 | 854.1166 | 966.1582 | 1030.4698 | 552.6968 | 637.2765 | 634.574 | 798.1131 | 80.8845 | -0.00010418 | 18.2776 | 3.3316 | -38.7623 | 3.1239 | 10831.67 | 0.33 | 0.9797 | 0.40761 | -0.73576 | -2.0885 | 5.939 | 5.8438 | 5.801 | 70.7635 | 118.9531 | 43.0333 | 42.8611 | -1.5691 | 45.7372 | 28.7333
42810.4502 | 880 | 18.0549 | 18.3291 | 18.3739 | 18.3744 | 17.6606 | 16.2691 | 14.5042 | 16.5209 | 17.0252 | 17.129 | 17.1292 | 16.6296 | 15.6408 | 14.2754 | 14.4416 | 15.4739 | 16.8773 | 23.1209 | 23.8899 | 72.637 |  |  |  | 17.0586 | 31.6546 | 154.4856 | 651.9051 | 698.8456 | 661.9092 | 108.4774 | 117.058 | 945.9398 | 92.8543 | 93.4766 | 865.1581 | 806.7968 | 891.6828 |  | 273.9482 | 927.1087 | 935.3148 | 479.5429 | 1315.9745 | 304.7963 | 579.9522 | 390.6254 | 580.0685 | 753.324 | 872.3826 | 933.5875 | 37.7349 | 288.2623 | 61.0426 | 504.4084 | 13.3641 | 49.0946 | 48.4489 | 47.9409 | 34.89 |  |  | -0.20809 | 0.80571 | -0.64146 | -1.4555 | 6.7586 | 5.1001 | 5.632 | -2.835 | 16.376 | 41.543 | 26.6559 | 0.00080497 | 0.00074418 | 0.0069917 | 16.939 | 16.5002 | 17.0334 | 17.3728 | 17.322 | 16.2706 | 14.6196 | 16.7015 | 17.0537 | 17.3511 | 17.4013 | 17.1006 | 16.2505 | 14.4461 | 814.5513 | 473.8503 | 552.9198 | 335.0518 | 272.291 | 714.308 | 432.5059 | 15.5322 | 16.5159 | 18.1658 | 25.9993 | 59.2802 | 71.8612 |  |  |  | 569.6602 | 541.1369 | 545.4356 | 565.4594 | 82.5395 | 39.3609 | 800.7886 |  |  | 403.9954 |  |  | 17.4518 | 27.907 | 262.7246 | 16.5537 | 22.2792 | 864.4654 | 735.8084 | 586.6391 | 790.0745 | 785.3443 | 729.8941 |  | 779.1077 | 814.2165 | 921.5611 | 576.7369 | 649.2785 | 815.5695 |  | 930.7162 |  |  | 394.1629 | 615.6303 | 712.7675 | [6 empty] | 579.3754 |  |  | 373.9755 |  |  | 454.9328 | 625.8843 | 641.6615 | 749.6407 | 977.3077 | 992.0445 | 508.349 | 682.8662 | 784.4035 | 582.1194 | 648.6509 | 907.0392 | 1019.9671 | 605.6675 | 762.7727 | 803.4229 | 1030.111 | 1017.5662 | 488.2042 | 593.197 | 665.3412 | 552.8676 | 702.3928 | 855.9278 | 961.2435 | 1029.4472 | 552.3702 | 635.8192 | 635.2502 | 796.9105 | 81.4625 | 0.00026063 | 18.2777 | 3.3133 | -38.7173 | 3.1239 | 10871.27 | 0.36 | -0.97209 | 1.8271 | -1.6302 | -2.4557 | 6.132 | 5.3267 | 5.5976 | 70.8809 | 118.4958 | 43.0651 | 42.7704 | 0.67969 | 86.2149 | 28.7257
42810.4502 | 881 | 18.0492 | 18.3313 | 18.375 | 18.3785 | 17.6709 | 16.2712 | 14.5096 | 16.5224 | 17.0263 | 17.1274 | 17.1279 | 16.6428 | 15.6447 | 14.2811 | 14.4424 | 15.5015 | 16.9093 | 23.3592 | 23.8287 | 72.9565 |  |  |  | 17.0615 | 32.5316 | 156.1275 | 654.3509 | 698.9711 | 662.9746 | 98.4789 | 114.9773 | 950.254 | 64.5034 | 108.0088 | 870.0132 | 812.9798 | 883.1196 |  | 256.6718 | 926.6254 | 937.4114 | 455.3366 | 1176.296 | 306.8206 | 579.4857 | 390.9889 | 579.5395 | 754.9722 | 868.8362 | 931.079 | 37.9966 | 289.5663 | 59.5996 | 505.5827 | 13.4012 | 49.1173 | 48.4826 | 47.9809 | 34.9351 |  |  | -0.31717 | 0.69006 | -1.1409 | -1.6816 | 6.5503 | 5.2716 | 7.4424 | -2.1016 | 17.3554 | 41.6011 | 28.0685 | 0.00076883 | 0.00075404 | -0.00079839 | 16.9558 | 16.4947 | 17.0326 | 17.3646 | 17.3182 | 16.2721 | 14.6277 | 16.7013 | 17.0491 | 17.3469 | 17.4001 | 17.0993 | 16.2449 | 14.4478 | 802.9898 | 485.8388 | 548.4571 | 337.7185 | 260.4053 | 715.3417 | 433.5935 | 15.5391 | 16.5546 | 18.207 | 26.1646 | 59.574 | 72.0498 |  |  |  | 569.8945 | 540.2506 | 544.5984 | 564.0607 | 72.5428 | 40.7258 | 799.0689 |  |  | 398.104 |  |  | 17.4412 | 28.0281 | 266.2952 | 16.5508 | 22.4178 | 861.9335 | 738.0437 | 587.2717 | 790.3881 | 785.9383 | 734.4527 |  | 779.9623 | 820.579 | 920.6952 | 577.4691 | 649.6145 | 813.0685 |  | 931.1077 |  |  | 395.8751 | 621.4617 | 716.905 | [6 empty] | 580.1355 |  |  | 374.537 |  |  | 456.1696 | 624.9875 | 641.8005 | 749.7701 | 979.0177 | 995.212 | 509.1893 | 683.5457 | 784.3683 | 581.7981 | 648.6145 | 908.1944 | 1022.8823 | 606.872 | 764.0532 | 803.0427 | 1025.8686 | 1016.2136 | 487.9481 | 592.6869 | 664.5709 | 553.354 | 703.4175 | 856.2154 | 958.7848 | 1028.2195 | 552.2712 | 634.696 | 635.3561 | 797.2938 | 79.0311 | -0.001388 | 18.2777 | 3.2972 | -38.8007 | 3.1239 | 10947.21 | 0.34 | -1.2008 | 1.6904 | -2.1735 | -2.6388 | 6.0274 | 5.4071 | 6.4247 | 71.0041 | 117.9605 | 43.114 | 44.396 | 1.3833 | 88.8405 | 28.8028
42810.4502 | 882 | 18.0522 | 18.3276 | 18.3765 | 18.3759 | 17.6713 | 16.2734 | 14.5125 | 16.5277 | 17.0195 | 17.1266 | 17.1363 | 16.6414 | 15.6357 | 14.2801 | 14.4438 | 15.5315 | 16.944 | 23.5936 | 23.7873 | 73.3362 |  |  |  | 17.0773 | 33.4567 | 155.1731 | 654.3974 | 699.5535 | 662.1961 | 114.8019 | 118.3192 | 960.9159 | 63.4266 | 124.9322 | 888.7127 | 286.2113 | 902.3337 |  | 251.9024 | 926.3277 | 941.1755 | 455.983 | 1016.378 | 308.7084 | 578.094 | 390.6471 | 577.709 | 749.5699 | 863.2786 | 928.993 | 37.4534 | 290.6869 | 58.1012 | 506.6708 | 13.4564 | 49.1527 | 48.5136 | 48.0265 | 35.1663 |  |  | 0.77101 | -0.28904 | -0.86094 | -1.3885 | 6.9525 | 6.3328 | 7.2361 | -2.4019 | 16.7631 | 41.9384 | 27.2017 | 0.00078525 | 0.00074418 | -0.00057169 | 16.9594 | 16.4969 | 17.0299 | 17.3626 | 17.3118 | 16.2644 | 14.6261 | 16.6939 | 17.0467 | 17.346 | 17.3951 | 17.106 | 16.2465 | 14.4446 | 795.1708 | 483.6035 | 544.3309 | 349.2349 | 275.4291 | 716.0207 | 434.6431 | 15.5248 | 16.5669 | 18.2527 | 26.3335 | 59.8723 | 72.2294 |  |  |  | 570.1983 | 541.2342 | 544.662 | 564.8405 | 98.321 | 45.1759 | 799.2522 |  |  | 392.5946 |  |  | 17.4388 | 28.1443 | 263.3983 | 16.5602 | 22.5452 | 862.354 | 738.4845 | 587.4 | 790.4202 | 785.785 | 736.4796 |  | 780.8189 | 822.6836 | 920.5076 | 577.3471 | 649.9401 | 812.0344 |  | 931.6557 |  |  | 397.556 | 626.6706 | 718.9398 | [6 empty] | 580.2294 |  |  | 374.1633 |  |  | 456.5919 | 624.2482 | 641.1713 | 749.2358 | 982.4666 | 997.1853 | 509.9033 | 684.0346 | 786.468 | 581.133 | 648.1495 | 911.7706 | 1027.676 | 607.9276 | 764 | 805.2723 | 1024.2603 | 1018.2371 | 487.7676 | 592.2472 | 664.8973 | 553.7287 | 704.4678 | 856.7978 | 959.5856 | 1032.7329 | 552.2501 | 634.2447 | 635.1098 | 798.8453 | 75.3357 | 0.00013432 | 18.2777 | 3.2825 | -38.8685 | 3.1238 | 10992.14 | 0.23 | 1.8715 | -1.0931 | -1.8866 | -2.3959 | 6.1945 | 5.912 | 6.3196 | 71.1988 | 117.8244 | 43.1844 | 45.4891 | 2.0426 | 0.83489 | 28.8309
42810.4503 | 883 | 18.0403 | 18.3191 | 18.3647 | 18.3675 | 17.6673 | 16.2652 | 14.5 | 16.5252 | 17.0261 | 17.1256 | 17.1258 | 16.6288 | 15.6416 | 14.2742 | 14.4364 | 15.547 | 16.9617 | 23.8071 | 23.7793 | 73.6862 |  |  |  | 17.0569 | 34.3961 | 156.0002 | 655.8567 | 699.7329 | 665.1951 | 113.7922 | 118.7555 | 960.8432 | 40.7408 | 120.8598 | 884.4034 | 375.1732 | 905.8806 | 1316.7711 | 247.5349 | 925.9262 | 923.6793 | 484.7201 | 751.055 | 309.7083 | 576.5658 | 392.2904 | 577.8468 | 748.1797 | 864.0065 | 932.9313 | 37.4568 | 292.1033 | 57.1031 | 508.013 | 13.5222 | 49.178 | 48.5448 | 48.0702 | 35.4209 |  |  | 0.20064 | 0.54615 | -1.1488 | -1.9089 | 6.2401 | 5.4142 | 6.4929 | -2.4282 | 16.7695 | 41.5098 | 27.7857 | 0.00072611 | 0.00078197 | 0.0019237 | 16.9648 | 16.496 | 17.0221 | 17.3551 | 17.3126 | 16.2566 | 14.6217 | 16.6924 | 17.0434 | 17.3486 | 17.394 | 17.0994 | 16.2423 | 14.4386 | 826.3735 | 520.176 | 575.0014 | 352.5505 | 268.566 | 718.3926 | 436.3905 | 15.5319 | 16.5939 | 18.3 | 26.4953 | 60.1488 | 72.4024 |  |  |  | 570.6069 | 543.6176 | 547.1653 | 568.1638 | 92.27 | 41.6837 | 799.7048 |  |  | 394.4503 |  |  | 17.4589 | 28.287 | 264.4601 | 16.5666 | 22.6965 | 862.0706 | 737.4819 | 586.5867 | 792.5624 | 789.949 | 735.1593 |  | 781.2695 | 830.4411 | 920.6197 | 576.714 | 650.0958 | 813.9088 |  | 932.8354 |  |  | 399.2279 | 629.056 | 719.4503 | [6 empty] | 579.3232 |  |  | 372.9996 |  |  | 456.37 | 623.9233 | 640.6549 | 748.6317 | 987.5833 | 999.655 | 510.6526 | 684.1612 | 786.8381 | 580.74 | 647.5715 | 911.3419 | 1031.1304 | 608.4489 | 762.6211 | 808.5557 | 1024.7774 | 1021.7787 | 487.9374 | 592.2575 | 666.6318 | 554.1535 | 705.3838 | 858.4226 | 960.5541 | 1039.2526 | 552.3966 | 635.8636 | 635.3832 | 797.85 | 79.7418 | -0.0010302 | 18.2773 | 3.2684 | -38.835 | 3.1239 | 10995.27 | 0.22 | 0.95622 | 1.5013 | -2.1773 | -2.8067 | 5.8705 | 5.4682 | 5.9882 | 71.3677 | 117.6553 | 43.2341 | 42.8082 | -1.0301 | 6.9743 | 28.8056
42810.4503 | 884 | 18.041 | 18.325 | 18.3698 | 18.3728 | 17.6697 | 16.2695 | 14.5024 | 16.5239 | 17.0279 | 17.1281 | 17.1305 | 16.6391 | 15.6401 | 14.2793 | 14.4351 | 15.5715 | 16.9862 | 24.0491 | 23.7332 | 74.0278 |  |  |  | 17.0655 | 35.3556 | 159.4839 | 657.1244 | 699.5957 | 667.5912 | 101.2485 | 115.602 | 952.3067 | 85.6305 | 115.3918 | 881.4145 | 526.6543 | 902.5372 | 1030.9417 | 246.7442 | 928.7717 | 937.7389 | 483.7287 | 1007.5087 | 310.0845 | 576.4019 | 393.9011 | 579.8555 | 746.1628 | 865.7419 | 934.8706 | 37.5803 | 293.3037 | 57.4111 | 509.4683 | 13.5644 | 49.2288 | 48.5767 | 48.1166 | 35.639 |  |  | 0.050819 | 0.27147 | -1.2197 | -1.4207 | 6.8138 | 6.5234 | 6.8779 | -3.038 | 17.335 | 41.7828 | 26.9774 | 0.00072283 | 0.00079183 | 0.0038605 | 16.9845 | 16.4961 | 17.0265 | 17.3582 | 17.3147 | 16.2614 | 14.6246 | 16.696 | 17.0538 | 17.3556 | 17.4056 | 17.1026 | 16.2547 | 14.4417 | 822.5816 | 513.5396 | 578.0817 | 338.8672 | 253.8024 | 720.0507 | 437.6054 | 15.5261 | 16.6054 | 18.3353 | 26.6536 | 60.4203 | 72.5648 |  |  |  | 571.2239 | 547.0942 | 550.2725 | 571.8953 | 87.118 | 41.4883 | 802.8892 |  |  | 402.2218 |  |  | 17.4526 | 28.409 | 262.501 | 16.3604 | 22.815 | 859.6397 | 737.1772 | 585.1145 | 800.3009 | 796.8666 | 734.1251 |  | 781.5857 | 847.6232 | 921.0193 | 575.8683 | 650.16 | 819.965 |  | 933.5744 |  |  | 399.7894 | 629.2802 | 719.0163 | [6 empty] | 577.7824 |  |  | 372.5976 |  |  | 456.4586 | 623.7395 | 640.734 | 746.9555 | 985.0139 | 1000.511 | 510.9875 | 684.0771 | 786.883 | 580.5897 | 648.2113 | 911.285 | 1030.9608 | 608.8939 | 762.9625 | 808.0254 | 1024.6551 | 1025.2835 | 488.5697 | 592.3365 | 668.3218 | 555.1507 | 706.0274 | 858.7862 | 959.9138 | 1043.9671 | 552.6708 | 637.8529 | 636.2741 | 800.002 | 79.7686 | -2.7032e-05 | 18.2767 | 3.249 | -38.8035 | 3.1239 | 11012.2 | 0.25 | 0.48185 | 1.0583 | -2.2433 | -2.4211 | 6.1391 | 6.0068 | 6.1679 | 71.4894 | 117.3434 | 43.2709 | 43.7813 | -1.1386 | 24.394 | 28.8032
42810.4503 | 885 | 18.0389 | 18.3226 | 18.3674 | 18.3774 | 17.6667 | 16.2703 | 14.5072 | 16.5237 | 17.0187 | 17.1284 | 17.1287 | 16.6376 | 15.6384 | 14.2846 | 14.4312 | 15.5984 | 17.0096 | 24.3042 | 23.7213 | 74.3902 |  |  |  | 17.0771 | 36.3152 | 163.7968 | 659.7228 | 700.3953 | 671.6878 | 101.7781 | 109.2645 | 946.5659 | 99.6066 | 112.7194 | 884.5786 | 592.591 | 902.4523 | 590.9178 | 249.4476 | 933.6547 | 947.3484 | 463.7061 | 1029.1296 | 311.1686 | 576.9292 | 394.2744 | 581.0211 | 747.271 | 871.4462 | 937.0555 | 38.1968 | 294.4183 | 58.5599 | 510.9935 | 13.5972 | 49.2871 | 48.6012 | 48.1475 | 35.887 |  |  | 0.11587 | 0.4673 | -1.2178 | -1.742 | 7.0372 | 5.7933 | 6.6532 | -3.1057 | 17.3496 | 42.5741 | 26.5472 | 0.00075076 | 0.00073597 | 0.0059666 | 16.9829 | 16.486 | 17.0199 | 17.3602 | 17.311 | 16.2532 | 14.6209 | 16.6978 | 17.0487 | 17.3478 | 17.398 | 17.104 | 16.2536 | 14.4418 | 812.1533 | 493.596 | 566.6531 | 330.8607 | 261.5932 | 721.559 | 438.7533 | 15.5295 | 16.6376 | 18.3885 | 26.8236 | 60.6934 | 72.7304 |  |  |  | 571.9032 | 549.5952 | 553.5444 | 575.1215 | 93.7064 | 42.3181 | 807.2789 |  |  | 401.7394 |  |  | 17.4515 | 28.53 | 269.0722 | 16.5264 | 22.9438 | 867.2892 | 736.7273 | 583.2637 | 802.2695 | 798.696 | 736.2675 |  | 782.1211 | 851.751 | 921.0598 | 574.4259 | 650.1053 | 825.7044 |  | 934.406 |  |  | 399.7499 | 630.2439 | 719.3536 | [6 empty] | 575.9084 |  |  | 371.9429 |  |  | 456.6923 | 623.8876 | 641.9888 | 748.3442 | 984.6199 | 1001.5337 | 511.6376 | 684.6651 | 786.8591 | 580.356 | 650.359 | 915.4177 | 1034.2986 | 609.4329 | 764.9554 | 811.5163 | 1025.4078 | 1027.819 | 488.8811 | 592.3285 | 670.1025 | 555.3718 | 706.6991 | 859.7473 | 959.9952 | 1049.3642 | 552.9958 | 639.5525 | 636.5706 | 804.5647 | 79.2649 | -0.0005181 | 18.2762 | 3.2342 | -38.8275 | 3.1239 | 10982.4 | 0.28 | 0.72918 | 1.389 | -2.2422 | -2.6818 | 6.2545 | 5.6749 | 6.0815 | 71.5873 | 117.2455 | 43.2996 | 45.4435 | 0.35246 | 35.432 | 28.8253
42810.4503 | 886 | 18.0252 | 18.3182 | 18.3668 | 18.3761 | 17.6675 | 16.269 | 14.5096 | 16.5233 | 17.0189 | 17.1287 | 17.1216 | 16.6388 | 15.6394 | 14.2826 | 14.4327 | 15.6224 | 17.0357 | 24.5614 | 24.0257 | 74.7616 |  |  |  | 17.0691 | 37.2863 | 162.1307 | 660.3378 | 700.2061 | 672.5035 | 105.2941 | 105.4727 | 945.5742 | 100.6335 | 106.2264 | 877.5694 | 656.1066 | 904.2827 | 423.8037 | 249.7579 | 931.6038 | 943.9191 | 455.3989 | 903.7854 | 311.7743 | 577.561 | 395.055 | 582.9428 | 748.8279 | 877.7071 | 942.9301 | 38.1445 | 295.6075 | 59.2134 | 512.3919 | 13.6248 | 49.3187 | 48.6242 | 48.1717 | 36.0676 |  |  | 0.35769 | 0.069087 | -0.34445 | -0.85557 | 7.2166 | 6.6772 | 6.7616 | -3.0275 | 16.6284 | 42.0213 | 26.4681 | 0.00075733 | 0.0007064 | 0.0087906 | 17 | 16.484 | 17.0138 | 17.3503 | 17.3151 | 16.2588 | 14.6188 | 16.6948 | 17.0457 | 17.3543 | 17.391 | 17.1017 | 16.2547 | 14.4492 | 809.073 | 521.9842 | 561.7179 | 336.4096 | 261.6137 | 723.2553 | 439.9673 | 15.5211 | 16.6636 | 18.4424 | 26.9966 | 60.9928 | 72.9081 |  |  |  | 572.9333 | 553.2286 | 556.4485 | 580.3015 | 94.7678 | 43.0815 | 808.6617 |  |  | 412.5074 |  |  | 17.4597 | 28.67 | 269.2399 | 16.5607 | 23.0766 | 864.7278 | 736.0236 | 582.8698 | 804.2838 | 801.6944 | 734.7883 |  | 782.3772 | 858.8314 | 921.7826 | 573.6235 | 650.218 | 830.1542 |  | 935.8335 |  |  | 399.5165 | 631.712 | 719.4411 | [6 empty] | 575.0559 |  |  | 372.3918 |  |  | 456.6123 | 624.5384 | 644.581 | 756.4495 | 988.6204 | 1002.6312 | 512.4974 | 685.3406 | 787.3347 | 580.4208 | 652.6755 | 922.2535 | 1038.2531 | 609.816 | 765.4819 | 813.9179 | 1028.1135 | 1032.7841 | 489.0753 | 592.4172 | 671.9297 | 555.0107 | 707.4331 | 859.9558 | 962.2051 | 1053.0489 | 553.2096 | 640.0337 | 636.5686 | 805.7458 | 80.8731 | 0.00030269 | 18.2757 | 3.2179 | -38.9143 | 3.1238 | 10948.39 | 0.26 | 1.2817 | 0.53426 | -1.1929 | -1.8801 | 6.351 | 6.109 | 6.1476 | 71.7038 | 117.3483 | 43.3452 | 46.3538 | 1.1353 | 47.8543 | 28.8513
42810.4503 | 887 | 18.0239 | 18.3203 | 18.3666 | 18.3712 | 17.6675 | 16.2645 | 14.5216 | 16.524 | 17.0233 | 17.1265 | 17.1248 | 16.6408 | 15.636 | 14.2877 | 14.428 | 15.6451 | 17.0621 | 24.825 | 24.1259 | 75.1004 |  |  |  | 17.0779 | 38.1853 | 162.9445 | 658.9038 | 700.8122 | 671.8631 | 115.3475 | 109.9813 | 950.1621 | 99.5796 | 105.5126 | 882.0386 | 536.0471 | 903.2994 | 452.8674 | 252.988 | 924.5858 | 941.7292 | 451.8812 | 434.4457 | 313.1529 | 580.2379 | 396.1343 | 583.527 | 751.1422 | 881.2436 | 945.9411 | 37.6063 | 296.6377 | 59.6071 | 513.333 | 13.6476 | 49.3777 | 48.6521 | 48.175 | 36.3556 |  |  | 0.21838 | 0.078943 | -0.46864 | -0.75634 | 6.5457 | 6.1271 | 6.5507 | -2.8849 | 16.8497 | 41.5713 | 24.8128 | 0.00069819 | 0.0007179 | 0.0093294 | 17.0098 | 16.4861 | 17.0128 | 17.3536 | 17.3103 | 16.258 | 14.6137 | 16.6951 | 17.0478 | 17.3527 | 17.398 | 17.0978 | 16.2558 | 14.4414 | 813.1099 | 525.8974 | 569.2997 | 340.2328 | 267.4005 | 724.4767 | 441.1848 | 15.5256 | 16.6897 | 18.4832 | 27.1759 | 61.2662 | 73.0836 |  |  |  | 573.7655 | 554.1067 | 557.1158 | 579.7685 | 86.2061 | 41.9423 | 812.1319 |  |  | 411.0245 |  |  | 17.4587 | 28.7911 | 272.3755 | 16.5656 | 23.1889 | 860.4234 | 735.8796 | 583.0383 | 804.9728 | 802.2278 | 733.3852 |  | 782.5915 | 863.1914 | 923.2739 | 573.8253 | 650.4174 | 831.4397 |  | 937.2033 |  |  | 399.6554 | 631.5499 | 719.3138 | [6 empty] | 575.3769 |  |  | 373.8052 |  |  | 456.8732 | 625.4418 | 646.3039 | 762.8431 | 996.5326 | 1002.9 | 513.0025 | 685.7779 | 786.5467 | 580.8854 | 654.4007 | 925.9703 | 1039.5931 | 610.0319 | 765.2043 | 814.33 | 1031.0222 | 1036.5507 | 489.2165 | 592.7714 | 671.3688 | 555.1953 | 708.4024 | 860.5668 | 964.7426 | 1055.5883 | 553.63 | 639.8036 | 636.8596 | 808.965 | 84.9121 | 0.00092006 | 18.2762 | 3.2041 | -38.9104 | 3.1239 | 10912.95 | 0.27 | 1.0011 | 0.572 | -1.3937 | -1.7705 | 6.0579 | 5.861 | 6.0602 | 71.8059 | 117.8468 | 43.3807 | 46.3155 | 0.52854 | 26.6488 | 29.0037
42810.4503 | 888 | 18.0279 | 18.3177 | 18.3671 | 18.3633 | 17.6646 | 16.2711 | 14.5144 | 16.5234 | 17.0286 | 17.1289 | 17.1251 | 16.6385 | 15.6409 | 14.2846 | 14.4239 | 15.6738 | 17.0861 | 25.0885 | 23.8675 | 75.4439 |  |  |  | 17.078 | 39.0408 | 165.0419 | 660.633 | 702.2644 | 673.8523 | 110.7692 | 114.2228 | 952.9131 | 102.935 | 113.1183 | 881.7697 | 660.4408 | 898.0232 | 973.6374 | 269.3354 | 909.9046 | 925.134 | 453.829 | 261.2668 | 316.0071 | 583.1648 | 399.0527 | 582.501 | 751.5458 | 877.2847 | 946.1002 | 37.2371 | 297.8685 | 62.1526 | 514.6102 | 13.6718 | 49.4648 | 48.6888 | 48.1913 | 36.6645 |  |  | -0.23766 | 0.1256 | -0.57772 | -0.97319 | 7.2698 | 5.2092 | 5.9724 | -3.4783 | 16.6702 | 42.6467 | 24.4299 | 0.0007064 | 0.0006604 | 0.0040708 | 17.0277 | 16.4881 | 17.0201 | 17.3599 | 17.3138 | 16.2528 | 14.6177 | 16.6963 | 17.049 | 17.3498 | 17.3986 | 17.0985 | 16.2575 | 14.4495 | 805.8888 | 514.5776 | 568.1321 | 354.2575 | 277.0208 | 725.4486 | 442.3392 | 15.5283 | 16.7092 | 18.53 | 27.3346 | 61.5216 | 73.2478 |  |  |  | 574.3294 | 553.6811 | 556.776 | 578.3734 | 80.0777 | 41.481 | 812.9129 |  |  | 412.958 |  |  | 17.4661 | 28.9032 | 275.6725 | 16.5767 | 23.3211 | 857.8014 | 737.4334 | 583.1753 | 807.9693 | 805.8276 | 732.879 |  | 782.8634 | 863.9608 | 924.2727 | 574.1602 | 650.5672 | 831.922 |  | 938.3452 |  |  | 399.6764 | 630.8326 | 719.2698 | [6 empty] | 575.5842 |  |  | 375.032 |  |  | 457.624 | 626.2439 | 646.7572 | 765.3939 | 1001.5399 | 1003.2303 | 513.1352 | 686.601 | 785.4617 | 581.5464 | 655.557 | 925.6664 | 1040.623 | 610.6657 | 765.7396 | 812.2077 | 1032.2683 | 1036.0899 | 489.8558 | 593.6642 | 671.7246 | 555.2184 | 708.7014 | 861.5242 | 965.0857 | 1054.656 | 554.5847 | 639.7102 | 636.4866 | 810.4675 | 83.8927 | -0.0010793 | 18.2773 | 3.185 | -38.7999 | 3.1239 | 10939.25 | 0.31 | -1.0455 | 0.72273 | -1.55 | -2.0118 | 6.3732 | 5.3949 | 5.7766 | 71.9001 | 118.2416 | 43.4024 | 47.445 | 0.88221 | 48.8126 | 29.1359
42810.4503 | 889 | 18.0278 | 18.3173 | 18.3675 | 18.3679 | 17.6579 | 16.2662 | 14.5091 | 16.5208 | 17.0273 | 17.1334 | 17.1276 | 16.6454 | 15.6383 | 14.2809 | 14.4289 | 15.6937 | 17.1269 | 25.3763 | 23.7337 | 75.7836 |  |  |  | 17.081 | 39.9377 | 168.4922 | 662.5397 | 702.7232 | 674.985 | 103.193 | 108.8451 | 942.6905 | 101.7098 | 118.3538 | 887.621 | 528.4048 | 887.4628 |  | 276.5774 | 906.3429 | 912.3135 | 479.1786 | 595.4105 | 317.6671 | 585.3825 | 402.5667 | 582.747 | 749.5429 | 872.7088 | 944.6148 | 36.9349 | 299.0628 | 62.3579 | 515.6666 | 13.6927 | 49.5403 | 48.7342 | 48.2022 | 37.0386 |  |  | -0.060893 | -0.049853 | -0.88263 | -0.98962 | 6.3564 | 6.0654 | 6.6401 | -2.6109 | 16.5278 | 40.4298 | 24.3859 | 0.00069983 | 0.0006949 | 0.0004337 | 17.0376 | 16.4827 | 17.0181 | 17.3606 | 17.3121 | 16.2543 | 14.62 | 16.6977 | 17.0523 | 17.3519 | 17.395 | 17.1003 | 16.2519 | 14.454 | 799.5966 | 516.631 | 552.2371 | 353.6565 | 285.1263 | 725.962 | 443.2901 | 15.5335 | 16.7382 | 18.5795 | 27.497 | 61.7751 | 73.4137 |  |  |  | 574.9165 | 553.57 | 557.522 | 577.5316 | 83.7865 | 41.7085 | 817.8557 |  |  | 407.4992 |  |  | 17.4476 | 29.0298 | 281.0301 | 16.5688 | 23.4723 | 855.5561 | 739.7294 | 584.052 | 813.1311 | 810.6605 | 736.7888 |  | 783.6665 | 866.6936 | 926.6552 | 574.7082 | 650.8148 | 832.1149 |  | 940.7004 |  |  | 400.0383 | 629.237 | 720.7884 | [6 empty] | 576.5462 |  |  | 376.5415 |  |  | 458.3973 | 626.9036 | 647.5791 | 766.5773 | 1003.0035 | 1005.966 | 513.4343 | 687.734 | 784.6879 | 582.2777 | 656.9318 | 924.837 | 1041.303 | 611.571 | 767.5208 | 811.4133 | 1032.1101 | 1036.4804 | 490.7957 | 594.4365 | 674.1395 | 555.1466 | 708.1374 | 861.5264 | 967.9356 | 1053.0328 | 555.4126 | 639.6555 | 635.9202 | 811.3545 | 84.0693 | -0.0010022 | 18.2772 | 3.165 | -38.8483 | 3.1239 | 10953.15 | 0.32 | -0.52952 | -0.45592 | -1.9184 | -2.0313 | 5.9476 | 5.8098 | 6.0788 | 72.0285 | 119.1624 | 43.4383 | 48.3172 | 2.8331 | 24.7728 | 29.2567
42810.4503 | 890 | 18.0111 | 18.3078 | 18.3526 | 18.3546 | 17.6602 | 16.2594 | 14.5118 | 16.5196 | 17.0136 | 17.128 | 17.1242 | 16.6286 | 15.6363 | 14.2847 | 14.4212 | 15.7237 | 17.1572 | 25.6502 | 23.834 | 76.0651 |  |  |  | 17.0859 | 40.8417 | 166.4663 | 661.9713 | 701.138 | 674.3739 | 98.7222 | 102.8169 | 935.9885 | 101.2576 | 116.7526 | 884.7301 | 542.7877 | 898.7711 | 963.2244 | 249.9834 | 910.7883 | 920.5733 | 471.2038 | 970.1276 | 317.9602 | 586.8794 | 405.3203 | 584.6051 | 747.2026 | 870.0925 | 944.1162 | 36.873 | 300.266 | 61.4237 | 516.5932 | 13.7127 | 49.6161 | 48.7647 | 48.2325 | 37.5977 |  |  | 0.25584 | 0.48767 | -0.87868 | -0.69326 | 7.0858 | 7.6641 | 6.7892 | -3.427 | 17.7868 | 44.6226 | 25.8684 | 0.0007064 | 0.00070804 | -0.00053226 | 17.0458 | 16.4778 | 17.0149 | 17.3553 | 17.3079 | 16.2521 | 14.6257 | 16.6968 | 17.0519 | 17.3508 | 17.3945 | 17.0973 | 16.2519 | 14.4511 | 801.5079 | 529.5556 | 555.373 | 355.676 | 291.2016 | 726.8957 | 444.3663 | 15.5273 | 16.7636 | 18.631 | 27.6639 | 62.0235 | 73.5844 |  |  |  | 575.5152 | 553.793 | 557.72 | 577.0373 | 107.807 | 43.0455 | 823.2553 |  |  | 400.6055 |  |  | 17.452 | 29.1595 | 279.3138 | 16.5734 | 23.6106 | 860.1555 | 739.8538 | 585.8092 | 819.5311 | 816.5923 | 733.9255 |  | 784.1173 | 873.9516 | 928.8695 | 576.2127 | 651.4114 | 833.2625 |  | 942.3091 |  |  | 400.1546 | 625.2757 | 720.9435 | [6 empty] | 578.2959 |  |  | 377.6559 |  |  | 458.9357 | 627.5125 | 647.4707 | 765.8781 | 1000.7245 | 1008.3145 | 513.6115 | 688.681 | 784.9648 | 583.0089 | 657.7684 | 922.115 | 1042.5437 | 612.0347 | 767.8127 | 813.6169 | 1034.0221 | 1036.7043 | 491.4928 | 595.1148 | 675.4958 | 555.6291 | 707.5006 | 860.8893 | 968.4178 | 1054.6129 | 556.1564 | 640.1816 | 635.6148 | 810.6102 | 75.6812 | 0.00042899 | 18.2773 | 3.153 | -38.7873 | 3.1238 | 11001.02 | 0.26 | 1.085 | 1.4272 | -1.9158 | -1.7017 | 6.2724 | 6.5233 | 6.1397 | 72.2413 | 119.8921 | 43.5199 | 48.4201 | 2.6942 | 27.1195 | 29.37
42810.4503 | 891 | 18.0057 | 18.3006 | 18.3492 | 18.3621 | 17.6606 | 16.2644 | 14.5141 | 16.5146 | 17.0181 | 17.1183 | 17.1267 | 16.6376 | 15.6465 | 14.2784 | 14.4254 | 15.7569 | 17.1827 | 25.9228 | 23.8525 | 76.3645 |  |  |  | 17.0958 | 41.7346 | 164.7638 | 661.7328 | 698.8034 | 674.2672 | 93.0889 | 102.1369 | 947.0525 | 96.0888 | 105.5098 | 870.0943 | 641.8966 | 891.6594 | 903.0492 | 218.0641 | 926.5276 | 937.5418 | 480.2685 | 1141.3502 | 318.8577 | 588.529 | 406.9042 | 585.6425 | 745.7425 | 877.2586 | 948.561 | 38.2433 | 301.6981 | 61.4051 | 517.9511 | 13.7363 | 49.7106 | 48.7982 | 48.2694 | 38.1056 |  |  | -0.014237 | 0.47387 | -1.3512 | -0.92456 | 5.8616 | 5.8236 | 6.2714 | -2.8488 | 17.233 | 42.2376 | 26.8131 | 0.00071626 | 0.0007869 | -0.00076061 | 17.0647 | 16.4792 | 17.0194 | 17.3571 | 17.3079 | 16.2569 | 14.62 | 16.7017 | 17.0481 | 17.3491 | 17.3992 | 17.094 | 16.2566 | 14.447 | 825.0658 | 543.0162 | 529.7137 | 344.6442 | 293.6476 | 729.5217 | 445.3624 | 15.5239 | 16.7814 | 18.6782 | 27.8503 | 62.2893 | 73.7618 |  |  |  | 576.1566 | 554.8792 | 558.2671 | 577.5758 | 104.0929 | 35.8408 | 826.6341 |  |  | 405.8182 |  |  | 17.4686 | 29.2866 | 277.2485 | 16.5715 | 23.7636 | 865.5082 | 737.6189 | 587.3832 | 816.5013 | 812.7378 | 730.1089 |  | 784.3462 | 873.5525 | 929.8073 | 577.4375 | 652.0098 | 835.2863 |  | 943.0159 |  |  | 399.892 | 620.6851 | 718.863 | [6 empty] | 580.1077 |  |  | 377.9171 |  |  | 459.3746 | 628.8338 | 647.5141 | 763.9743 | 996.4917 | 1009.5435 | 513.445 | 689.1827 | 784.9185 | 583.8881 | 658.4125 | 919.2127 | 1042.2946 | 612.3845 | 767.8716 | 813.1557 | 1036.8837 | 1038.3882 | 492.3604 | 595.824 | 675.8479 | 556.3879 | 707.0178 | 861.4755 | 967.177 | 1054.9114 | 556.8825 | 641.4754 | 635.6449 | 810.9334 | 84.4555 | 0.00060437 | 18.2769 | 3.1408 | -38.934 | 3.1238 | 10954.46 | 0.29 | -0.25595 | 1.4082 | -2.3779 | -1.967 | 5.7227 | 5.7041 | 5.9194 | 72.4151 | 120.2991 | 43.6099 | 46.6924 | 5.7396 | 44.2414 | 29.4619
42810.4504 | 892 | 18.0043 | 18.3074 | 18.3633 | 18.3628 | 17.6597 | 16.2673 | 14.5178 | 16.5188 | 17.0256 | 17.13 | 17.1296 | 16.6405 | 15.643 | 14.2881 | 14.4092 | 15.7657 | 17.207 | 26.1987 | 23.6557 | 76.6225 |  |  |  | 17.0828 | 42.6501 | 162.3394 | 661.3433 | 696.7571 | 673.4576 | 89.4368 | 95.9491 | 946.5923 | 93.8271 | 101.5298 | 871.8917 | 549.2146 | 889.3014 | 895.3772 | 218.7124 | 933.7997 | 950.626 | 444.6608 | 670.5516 | 319.3872 | 588.5364 | 408.6713 | 586.3236 | 741.6116 | 876.1332 | 948.436 | 39.447 | 302.8041 | 61.1281 | 519.0422 | 13.7551 | 49.7648 | 48.8097 | 48.287 | 38.4745 |  |  | -0.21466 | 0.47387 | -0.75383 | -0.82862 | 7.0398 | 6.4649 | 6.5559 | -3.013 | 16.2452 | 42.0144 | 26.5401 | 0.00072283 | 0.0007064 | -0.00080661 | 17.0698 | 16.4775 | 17.0159 | 17.3504 | 17.3135 | 16.2572 | 14.6247 | 16.6969 | 17.0431 | 17.355 | 17.4054 | 17.0992 | 16.2565 | 14.4502 | 838.0029 | 569.9082 | 541.5208 | 342.3755 | 291.8693 | 732.1342 | 446.3243 | 15.5199 | 16.8215 | 18.7426 | 28.0177 | 62.5413 | 73.9213 |  |  |  | 576.8259 | 557.0948 | 559.1903 | 579.6927 | 86.5546 | 44.8163 | 822.3722 |  |  | 413.7079 |  |  | 17.4612 | 29.4035 | 272.1361 | 16.4889 | 23.8834 | 868.7156 | 736.4999 | 587.3091 | 809.4929 | 805.4002 | 727.1682 |  | 784.348 | 862.8221 | 929.6618 | 577.26 | 652.4669 | 834.0094 |  | 942.7301 |  |  | 400.023 | 617.8311 | 715.5552 | [6 empty] | 580.2844 |  |  | 376.6769 |  |  | 459.3778 | 630.3544 | 647.6805 | 762.8782 | 991.9934 | 1007.8037 | 513.5518 | 690.4654 | 783.2747 | 584.8834 | 658.9451 | 915.5553 | 1040.2884 | 612.8809 | 766.1228 | 812.6682 | 1034.6965 | 1035.9827 | 492.8032 | 596.4609 | 676.4859 | 557.1879 | 706.3961 | 860.2281 | 968.6563 | 1050.1366 | 557.1963 | 642.7173 | 636.0955 | 808.4769 | 83.5262 | 0.0014883 | 18.2778 | 3.1293 | -39.0441 | 3.1238 | 10879.61 | 0.25 | -0.9934 | 1.4082 | -1.7761 | -1.8622 | 6.2685 | 6.0071 | 6.0492 | 72.4973 | 120.5356 | 43.7097 | 46.1448 | 4.6156 | 28.8365 | 29.5148
42810.4504 | 893 | 17.9999 | 18.3016 | 18.3617 | 18.3538 | 17.6511 | 16.2586 | 14.5129 | 16.5193 | 17.0206 | 17.1239 | 17.1208 | 16.6317 | 15.6375 | 14.2928 | 14.4145 | 15.7992 | 17.2504 | 26.5187 | 23.6444 | 76.9082 |  |  |  | 17.0849 | 43.6364 | 175.2522 | 660.1669 | 698.1805 | 672.8185 | 94.7142 | 95.2026 | 954.9544 | 90.7149 | 95.4492 | 868.8211 | 609.2861 | 891.076 | 1080.9293 | 222.4478 | 936.043 | 956.335 | 449.7952 | 477.5832 | 319.9489 | 588.3225 | 408.6413 | 588.2666 | 744.428 | 878.5494 | 949.8134 | 41.0317 | 303.7354 | 61.1115 | 520.0601 | 13.7714 | 49.7746 | 48.816 | 48.3033 | 38.8521 |  |  | -0.090461 | 0.050027 | -1.1796 | -1.2558 | 6.5602 | 5.6034 | 6.2885 | -3.042 | 16.1617 | 41.6481 | 25.3089 | 0.00063412 | 0.00071461 | -0.00081646 | 17.0836 | 16.4738 | 17.0109 | 17.3533 | 17.3018 | 16.2539 | 14.6254 | 16.6917 | 17.0509 | 17.3414 | 17.3966 | 17.1013 | 16.2591 | 14.4539 | 835.065 | 571.1305 | 546.8984 | 346.119 | 294.8308 | 733.4839 | 447.2815 | 15.5189 | 16.844 | 18.7918 | 28.1837 | 62.7824 | 74.0749 |  |  |  | 577.4327 | 557.9302 | 559.0019 | 580.0217 | 82.404 | 42.731 | 815.5321 |  |  | 414.5747 |  |  | 17.4798 | 29.5258 | 284.9522 | 16.5752 | 24.0067 | 879.6366 | 739.2048 | 586.5104 | 803.1866 | 798.8275 | 732.5831 |  | 784.9845 | 854.429 | 928.6487 | 576.367 | 652.6512 | 831.2838 |  | 942.1749 |  |  | 400.573 | 618.1168 | 717.1229 | [6 empty] | 579.1716 |  |  | 375.0695 |  |  | 459.4802 | 631.3324 | 647.5523 | 760.2594 | 987.2083 | 1009.143 | 513.4726 | 691.2158 | 784.4196 | 585.371 | 659.5528 | 915.552 | 1040.5608 | 613.2607 | 768.9442 | 815.0515 | 1030.9835 | 1031.0015 | 493.7083 | 597.1969 | 676.0937 | 558.1982 | 706.6129 | 861.9419 | 963.9464 | 1046.6783 | 558.1948 | 642.8665 | 636.8072 | 808.7192 | 84.2471 | -0.024188 | 18.2776 | 3.1242 | -39.1593 | 3.1238 | 10796.59 | 0.33 | -0.64467 | 0.4575 | -2.2216 | -2.2921 | 6.0575 | 5.5984 | 5.9308 | 72.5355 | 120.3413 | 43.7727 | 46.9328 | 4.2055 | 38.8111 | 29.6071
42810.4504 | 894 | 18.0045 | 18.3036 | 18.3529 | 18.3535 | 17.651 | 16.2622 | 14.5144 | 16.5202 | 17.0207 | 17.1236 | 17.1344 | 16.6389 | 15.6407 | 14.2882 | 14.4039 | 15.8352 | 17.2735 | 26.8456 | 23.7185 | 77.2571 |  |  |  | 17.092 | 44.637 | 172.1927 | 662.2711 | 700.2498 | 674.7079 | 105.9519 | 106.8156 | 966.3156 | 91.1319 | 100.5557 | 867.0001 | 784.7641 | 886.0365 | 1023.2728 | 229.582 | 939.4429 | 958.8038 | 461.5389 | 619.5554 | 320.1618 | 588.8609 | 408.3439 | 587.7582 | 748.2458 | 881.845 | 949.8777 | 41.8796 | 304.5469 | 60.8125 | 520.7361 | 13.7777 | 49.7866 | 48.84 | 48.3407 | 39.2704 |  |  | 0.070531 | -0.070225 | -0.7742 | -1.1565 | 7.2508 | 6.204 | 7.0619 | -2.5524 | 17.1707 | 43.2721 | 27.3792 | 0.00068012 | 0.00070311 | -0.00079018 | 17.102 | 16.481 | 17.0213 | 17.3577 | 17.3128 | 16.2617 | 14.6317 | 16.7009 | 17.0517 | 17.358 | 17.4054 | 17.1077 | 16.2687 | 14.455 | 821.904 | 564.8992 | 559.7707 | 347.1641 | 289.6528 | 733.6616 | 448.2391 | 15.5168 | 16.8732 | 18.8403 | 28.3543 | 63.0205 | 74.2091 |  |  |  | 577.9381 | 558.0363 | 558.7338 | 579.9771 | 94.426 | 38.266 | 811.0254 |  |  | 411.8168 |  |  | 17.4749 | 29.6822 | 285.4297 | 16.5848 | 24.1608 | 882.8093 | 740.7323 | 586.828 | 798.6392 | 796.9279 | 736.7825 |  | 785.7469 | 853.6772 | 927.0927 | 576.1867 | 652.9603 | 827.5511 |  | 942.0099 |  |  | 401.2757 | 621.5298 | 720.3929 | [6 empty] | 579.2632 |  |  | 375.4514 |  |  | 459.8671 | 631.8399 | 648.8452 | 757.2294 | 991.193 | 1010.1155 | 513.9719 | 692.3185 | 789.1274 | 585.652 | 659.233 | 908.1245 | 1042.3711 | 613.3824 | 768.612 | 815.3801 | 1033.6263 | 1032.7617 | 494.4916 | 598.1348 | 676.5953 | 558.5159 | 707.2737 | 862.2085 | 960.0217 | 1047.4676 | 558.9474 | 642.8422 | 637.3376 | 812.3076 | 80.99 | 0.0020004 | 18.2767 | 3.1225 | -39.1358 | 3.1238 | 10755.22 | 0.35 | 0.56981 | -0.54221 | -1.8003 | -2.2004 | 6.3775 | 5.8992 | 6.2939 | 72.6451 | 119.7076 | 43.842 | 48.456 | 2.963 | 79.9991 | 29.693
42810.4504 | 895 | 17.994 | 18.296 | 18.3495 | 18.3551 | 17.6496 | 16.2558 | 14.5172 | 16.5201 | 17.0233 | 17.12 | 17.1278 | 16.6358 | 15.639 | 14.288 | 14.41 | 15.8671 | 17.3142 | 27.16 | 23.7014 | 77.5888 |  |  |  | 17.0915 | 45.6452 | 169.822 | 664.6645 | 699.3032 | 676.8463 | 98.1158 | 107.1566 | 982.0908 | 101.3125 | 107.294 | 869.1393 | 774.4463 | 870.3497 |  | 235.815 | 929.7323 | 953.4302 | 453.5944 | 762.4892 | 320.7427 | 589.5921 | 407.8554 | 586.1844 | 742.4839 | 879.3131 | 948.7248 | 42.3165 | 305.4041 | 62.8163 | 521.4251 | 13.7766 | 49.8323 | 48.8702 | 48.3711 | 39.6458 |  |  | 0.2105 | -0.004513 | -0.9122 | -1.0994 | 7.0168 | 5.4897 | 6.3365 | -2.5517 | 17.6818 | 44.3723 | 27.8753 | 0.00064397 | 0.00072119 | -0.00084932 | 17.1163 | 16.475 | 17.014 | 17.355 | 17.3125 | 16.2589 | 14.6271 | 16.6949 | 17.0497 | 17.3587 | 17.398 | 17.1048 | 16.2582 | 14.4529 | 815.7013 | 567.9897 | 555.23 | 342.8528 | 285.5901 | 735.3835 | 449.5285 | 15.515 | 16.9001 | 18.894 | 28.5304 | 63.2725 | 74.3589 |  |  |  | 578.4705 | 557.7294 | 558.8632 | 580.9772 | 113.2387 | 55.0054 | 813.2145 |  |  | 416.5972 |  |  | 17.4777 | 29.8179 | 282.5363 | 16.5964 | 24.3053 | 884.8959 | 742.176 | 587.7327 | 804.4892 | 802.1333 | 737.7172 |  | 786.2525 | 867.1092 | 925.6796 | 576.731 | 653.469 | 825.6868 |  | 942.4111 |  |  | 402.7802 | 625.2979 | 721.6321 | [6 empty] | 579.9203 |  |  | 376.3837 |  |  | 460.2269 | 631.8692 | 650.2933 | 751.6207 | 984.1977 | 1008.3983 | 514.4195 | 692.925 | 792.2014 | 586.1248 | 659.5561 | 903.3177 | 1041.9356 | 613.7001 | 768.7856 | 815.6465 | 1040.177 | 1035.8016 | 495.4085 | 598.8297 | 677.2365 | 558.5964 | 708.7158 | 861.4085 | 958.5412 | 1052.1456 | 559.346 | 644.2353 | 637.6116 | 814.2894 | 78.3242 | 0.00018343 | 18.2759 | 3.1371 | -39.1175 | 3.1238 | 10751.73 | 0.22 | 0.98548 | -0.13751 | -1.955 | -2.1462 | 6.2669 | 5.5431 | 5.9553 | 72.7694 | 118.742 | 43.9327 | 49.7361 | 3.7209 | 77.2028 | 29.7545
42810.4504 | 896 | 17.9963 | 18.289 | 18.3453 | 18.3495 | 17.6527 | 16.2556 | 14.512 | 16.5164 | 17.0116 | 17.1206 | 17.1287 | 16.6394 | 15.6387 | 14.2878 | 14.4105 | 15.8895 | 17.349 | 27.4816 | 23.6666 | 77.834 |  |  |  | 17.0979 | 46.628 | 169.0994 | 663.1882 | 698.0647 | 676.4366 | 98.6918 | 108.5427 | 974.3417 | 106.8077 | 114.0321 | 869.356 | 481.7649 | 865.5467 |  | 243.8095 | 918.2942 | 935.3824 | 475.6595 | 1095.9724 | 321.3936 | 590.9312 | 408.7814 | 586.6803 | 742.0775 | 886.4969 | 949.6836 | 41.2383 | 306.2943 | 63.874 | 522.5027 | 13.7817 | 49.8894 | 48.909 | 48.4061 | 40.0049 |  |  | -0.038549 | -0.55123 | -1.4267 | -1.1907 | 7.9585 | 6.0003 | 7.033 | -2.7114 | 16.7337 | 43.1215 | 28.9684 | 0.00069819 | 0.00064397 | -0.00079182 | 17.1251 | 16.473 | 17.0096 | 17.3589 | 17.3147 | 16.2566 | 14.6229 | 16.6974 | 17.0527 | 17.3616 | 17.4041 | 17.1057 | 16.2628 | 14.4531 | 845.4397 | 590.7139 | 609.7171 | 364.4428 | 315.3906 | 738.3026 | 451.948 | 15.5129 | 16.9228 | 18.9503 | 28.7213 | 63.5276 | 74.5227 |  |  |  | 579.3177 | 559.3486 | 559.4397 | 585.2502 | 98.9418 | 51.1622 | 817.4442 |  |  | 411.0671 |  |  | 17.4847 | 29.9199 | 276.7319 | 16.6079 | 24.433 | 883.3495 | 740.8902 | 588.3565 | 807.4143 | 803.3297 | 737.2601 |  | 786.2885 | 864.3255 | 924.7074 | 576.9251 | 653.8643 | 824.0872 |  | 943.0374 |  |  | 403.7567 | 627.6416 | 721.4933 | [6 empty] | 580.4924 |  |  | 376.77 |  |  | 460.796 | 631.9276 | 650.1837 | 749.677 | 980.7858 | 1009.5272 | 514.8882 | 693.3759 | 794.6386 | 586.6606 | 659.8748 | 903.9958 | 1042.2539 | 614.2264 | 769.3216 | 815.1483 | 1040.9387 | 1036.5936 | 495.5884 | 599.4958 | 677.9354 | 558.9278 | 709.819 | 860.4235 | 960.5046 | 1051.4401 | 559.8081 | 644.6691 | 637.7976 | 812.4425 | 80.7562 | -0.00092497 | 18.2768 | 3.1699 | -39.007 | 3.1238 | 10763.92 | 0.29 | -0.42164 | -1.5209 | -2.4469 | -2.2353 | 6.6949 | 5.8132 | 6.2936 | 72.7928 | 118.4129 | 44.0097 | 47.4383 | -1.8563 | 18.5847 | 29.7782
42810.4504 | 897 | 17.9912 | 18.2905 | 18.3379 | 18.3438 | 17.6453 | 16.2548 | 14.5176 | 16.517 | 17.0182 | 17.1215 | 17.1255 | 16.6271 | 15.6488 | 14.2911 | 14.4036 | 15.9269 | 17.3926 | 27.8287 | 23.6768 | 78.0769 |  |  |  | 17.0987 | 47.5933 | 175.5604 | 661.1811 | 698.5993 | 673.014 | 94.8019 | 96.6072 | 962.2697 | 97.6338 | 106.5348 | 867.5921 | 347.3582 | 870.7457 |  | 232.953 | 922.1942 | 937.5066 | 481.9876 | 1108.7508 | 322.2144 | 591.0391 | 408.8426 | 585.8984 | 741.276 | 890.6529 | 952.2739 | 40.316 | 307.1161 | 63.2128 | 523.5078 | 13.7812 | 49.9443 | 48.9482 | 48.4312 | 40.2648 |  |  | -0.35594 | -0.31467 | -1.1238 | -1.0271 | 6.9393 | 5.3353 | 6.228 | -2.4459 | 17.3792 | 43.3502 | 29.6902 | 0.00061769 | 0.00073597 | -0.00082468 | 17.1403 | 16.4717 | 17.0052 | 17.3531 | 17.313 | 16.2627 | 14.6236 | 16.6993 | 17.0544 | 17.36 | 17.4052 | 17.1021 | 16.2663 | 14.4613 | 846.9848 | 598.7636 | 634.7181 | 377.2176 | 324.1649 | 740.5116 | 454.1082 | 15.5199 | 16.9565 | 19.0053 | 28.8932 | 63.7724 | 74.6624 |  |  |  | 580.0179 | 558.8504 | 559.454 | 584.2663 | 93.7038 | 47.5887 | 817.4505 |  |  | 406.7238 |  |  | 17.4656 | 30.0648 | 286.4568 | 16.5927 | 24.5978 | 876.6004 | 741.9648 | 589.0975 | 808.2733 | 804.5385 | 737.7538 |  | 786.5536 | 861.7496 | 924.2895 | 577.4441 | 654.3334 | 822.0924 |  | 944.1482 |  |  | 404.9555 | 629.8603 | 721.5874 | [6 empty] | 581.2213 |  |  | 377.5757 |  |  | 461.192 | 632.1528 | 650.1594 | 747.7656 | 979.7338 | 1012.4362 | 515.2746 | 693.3077 | 796.2503 | 586.8382 | 659.7189 | 901.6142 | 1044.5305 | 615.087 | 769.8785 | 818.0671 | 1038.9853 | 1038.284 | 495.901 | 600.1835 | 677.3629 | 559.3465 | 710.0172 | 856.8004 | 958.3349 | 1051.0843 | 560.3169 | 645.1152 | 637.7581 | 809.4761 | 78.9523 | -0.0011705 | 18.2771 | 3.2228 | -39.0857 | 3.1238 | 10814.62 | 0.36 | -1.2789 | -1.1492 | -2.1718 | -2.0762 | 6.2627 | 5.4914 | 5.9331 | 72.858 | 118.3101 | 44.0931 | 48.0322 | -4.2065 | 4.666 | 29.9234
42810.4504 | 898 | 17.9916 | 18.2935 | 18.3514 | 18.3596 | 17.6583 | 16.2577 | 14.5307 | 16.522 | 17.0247 | 17.1281 | 17.1394 | 16.6441 | 15.646 | 14.2986 | 14.4065 | 15.9648 | 17.4308 | 28.1722 | 23.8359 | 78.3307 |  |  |  | 17.0961 | 48.5101 | 172.4561 | 660.6121 | 698.8863 | 670.4921 | 88.3601 | 103.5216 | 957.4322 | 94.4234 | 103.2732 | 854.7505 | 462.8681 | 871.5008 | 1339.0005 | 220.3301 | 927.9266 | 943.9426 | 460.3801 | 1371.427 | 323.5376 | 591.442 | 409.9085 | 583.548 | 739.6997 | 892.5687 | 952.7341 | 39.6144 | 308.173 | 62.0324 | 524.3361 | 13.7759 | 49.9649 | 48.9782 | 48.4512 | 40.6131 |  |  | -0.16603 | -0.16025 | -1.1185 | -0.53292 | 6.2651 | 6.2329 | 6.9594 | -2.398 | 16.4241 | 41.6869 | 30.3233 | 0.00065219 | 0.00065712 | -0.00083125 | 17.166 | 16.4739 | 17.0087 | 17.3589 | 17.3115 | 16.2639 | 14.6228 | 16.7058 | 17.0586 | 17.361 | 17.4082 | 17.1071 | 16.2705 | 14.471 | 853.6527 | 603.2849 | 644.0908 | 377.3335 | 311.4143 | 742.6944 | 455.9466 | 15.5106 | 16.9802 | 19.0567 | 29.0614 | 63.9997 | 74.7933 |  |  |  | 580.4255 | 557.1764 | 558.4724 | 581.3119 | 99.1399 | 47.3444 | 817.1496 |  |  | 412.4186 |  |  | 17.4742 | 30.1753 | 282.697 | 16.5925 | 24.722 | 870.3212 | 742.4062 | 589.3436 | 823.0138 | 817.5562 | 739.4911 |  | 786.9182 | 865.1516 | 924.255 | 577.5668 | 654.8594 | 825.9899 |  | 945.0822 |  |  | 406.8211 | 631.7349 | 723.1204 | [6 empty] | 581.5231 |  |  | 378.2088 |  |  | 461.6571 | 632.7058 | 649.5472 | 748.0871 | 976.4848 | 1013.6885 | 515.7971 | 693.9826 | 795.8809 | 587.0261 | 659.1569 | 902.7215 | 1042.5163 | 615.8453 | 772.42 | 821.214 | 1036.4482 | 1039.3562 | 496.3737 | 600.7369 | 676.5728 | 559.8841 | 709.8071 | 854.49 | 954.5773 | 1050.6487 | 560.9297 | 646.2543 | 637.5335 | 807.2302 | 96.5667 | 0.0007096 | 18.2776 | 3.2838 | -39.0574 | 3.1237 | 10821.87 | 0.37 | -0.8723 | -0.8203 | -2.1672 | -1.4959 | 5.9556 | 5.9403 | 6.277 | 72.9183 | 118.2012 | 44.1996 | 48.0511 | -4.8827 | 16.7085 | 30.0743
42810.4504 | 899 | 17.9896 | 18.2985 | 18.3603 | 18.3571 | 17.661 | 16.2675 | 14.5296 | 16.5259 | 17.0291 | 17.1332 | 17.1348 | 16.6443 | 15.6493 | 14.3002 | 14.4034 | 15.9999 | 17.4651 | 28.5197 | 23.9346 | 78.5814 |  |  |  | 17.0994 | 49.3778 | 176.6796 | 660.0211 | 699.4748 | 669.1156 | 88.9545 | 95.0862 | 954.5011 | 93.9276 | 105.3573 | 851.0958 | 627.7241 | 864.1355 | 806.1914 | 226.2289 | 933.7701 | 952.386 | 445.4986 |  | 324.4496 | 591.1224 | 411.3731 | 582.6444 | 743.5018 | 887.5739 | 951.8054 | 39.2744 | 309.0503 | 60.8186 | 524.9045 | 13.7764 | 49.9847 | 49.0092 | 48.4855 | 41.0279 |  |  | -0.14894 | 0.021115 | -1.1941 | -1.3261 | 6.756 | 5.7782 | 5.9185 | -1.7356 | 17.5348 | 43.6191 | 29.2996 | 0.00064562 | 0.00066533 | -0.00084111 | 17.1693 | 16.4637 | 17.0104 | 17.3521 | 17.309 | 16.265 | 14.6209 | 16.7053 | 17.0557 | 17.3606 | 17.4082 | 17.1147 | 16.2683 | 14.4603 | 852.0213 | 598.3352 | 630.06 | 374.5922 | 313.8908 | 744.6009 | 457.7913 | 15.5075 | 17.0083 | 19.1068 | 29.2343 | 64.2293 | 74.9359 |  |  |  | 580.8187 | 556.5129 | 558.3344 | 580.2374 | 104.0015 | 52.0215 | 827.1913 |  |  | 408.1476 |  |  | 17.4872 | 30.2962 | 288.2151 | 16.5896 | 24.8954 | 871.0187 | 743.9028 | 588.4943 | 824.4225 | 818.5424 | 742.503 |  | 787.6233 | 869.7139 | 923.8961 | 575.5656 | 655.0839 | 833.3729 |  | 945.2194 |  |  | 408.1552 | 635.169 | 724.9511 | [6 empty] | 580.1517 |  |  | 377.5646 |  |  | 462.1473 | 632.8388 | 648.3747 | 752.5643 | 975.807 | 1013.5231 | 516.6214 | 695.7199 | 796.8723 | 587.6432 | 658.6637 | 908.3594 | 1041.8491 | 616.6965 | 771.9456 | 822.7283 | 1034.6618 | 1038.0911 | 496.8742 | 601.5091 | 676.3351 | 559.8705 | 709.3582 | 854.1208 | 956.0929 | 1049.5923 | 561.2599 | 648.0889 | 637.5642 | 805.2828 | 89.8594 | -0.0010022 | 18.2776 | 3.3545 | -38.8911 | 3.1238 | 10855.3 | 0.42 | -0.82559 | 0.29771 | -2.2388 | -2.3592 | 6.1713 | 5.7073 | 5.7762 | 73.0449 | 117.9248 | 44.3021 | 48.8988 | -2.956 | 42.4074 | 30.1706
42810.4505 | 900 | 17.9846 | 18.2953 | 18.354 | 18.3538 | 17.6569 | 16.2599 | 14.5266 | 16.5237 | 17.0277 | 17.1289 | 17.131 | 16.6417 | 15.646 | 14.2972 | 14.4084 | 16.0341 | 17.5009 | 28.8838 | 23.7671 | 78.875 |  |  |  | 17.1128 | 50.2031 | 176.3764 | 659.2895 | 699.5291 | 668.5839 | 96.2446 | 91.8982 | 949.4087 | 85.5898 | 101.0353 | 849.4325 | 653.1236 | 863.8647 | 880.9236 | 232.7927 | 929.3702 | 947.6251 | 445.0157 | 1352.6409 | 324.3917 | 588.5318 | 411.1773 | 583.9105 | 742.7382 | 886.1183 | 951.9337 | 40.1542 | 309.9171 | 60.3534 | 525.6985 | 13.7791 | 50.038 | 49.0315 | 48.5147 | 41.3801 |  |  | 0.40106 | 0.4535 | -0.61912 | -1.0619 | 7.2712 | 5.7769 | 6.2386 | -1.7054 | 17.7444 | 44.4885 | 29.0705 | 0.00063905 | 0.00058319 | -0.00084275 | 17.1834 | 16.4621 | 16.9982 | 17.3452 | 17.3031 | 16.2474 | 14.6235 | 16.7055 | 17.0389 | 17.355 | 17.3962 | 17.1 | 16.2684 | 14.4562 | 856.3754 | 603.1959 | 638.7402 | 394.7067 | 323.9059 | 746.6002 | 459.8314 | 15.5108 | 17.0473 | 19.1685 | 29.4103 | 64.455 | 75.0832 |  |  |  | 581.2839 | 555.9982 | 558.3128 | 578.3273 | 88.5251 | 40.843 | 828.9208 |  |  | 416.3989 |  |  | 17.4805 | 30.4361 | 291.3109 | 16.5297 | 25.0357 | 874.6803 | 746.5038 | 586.8518 | 824.7196 | 819.3133 | 750.4281 |  | 789.0032 | 869.2719 | 924.3689 | 573.5945 | 655.1224 | 833.3605 |  | 945.7442 |  |  | 409.3758 | 640.6867 | 729.0681 | [6 empty] | 578.1821 |  |  | 376.3636 |  |  | 462.9529 | 632.7848 | 647.7829 | 756.3727 | 979.4042 | 1014.3263 | 517.5899 | 696.4715 | 797.6327 | 588.07 | 658.9401 | 915.7472 | 1044.479 | 617.3714 | 772.2896 | 821.1323 | 1033.3039 | 1037.1601 | 497.4912 | 602.3756 | 675.3461 | 560.4292 | 709.4199 | 854.3835 | 961.018 | 1049.6642 | 561.5469 | 648.4007 | 637.9124 | 803.9593 | 90.4159 | -0.00021643 | 18.278 | 3.4187 | -39.1348 | 3.1237 | 10867.61 | 0.25 | 1.3544 | 1.3776 | -1.6096 | -2.1081 | 6.3982 | 5.703 | 5.9265 | 73.2374 | 118.1342 | 44.3649 | 49.1165 | -3.5123 | 47.5196 | 30.3023
42810.4505 | 901 | 17.9785 | 18.2898 | 18.3499 | 18.355 | 17.6536 | 16.2581 | 14.5303 | 16.5232 | 17.0171 | 17.1314 | 17.1332 | 16.6386 | 15.6475 | 14.3056 | 14.4025 | 16.0695 | 17.5325 | 29.2427 | 23.551 | 79.1659 |  |  |  | 17.1096 | 51.0079 | 176.8278 | 658.9396 | 701.2295 | 669.5378 | 102.8139 | 99.1592 | 950.6812 | 89.0738 | 98.8794 | 849.2885 | 646.4465 | 867.7532 | 1153.8994 | 229.6832 | 926.849 | 944.1215 | 461.1704 | 1035.4264 | 324.6063 | 587.9503 | 411.6757 | 583.7508 | 739.2827 | 890.8091 | 954.5423 | 41.9783 | 311.0991 | 59.7705 | 526.8239 | 13.7658 | 50.0817 | 49.0464 | 48.5629 | 41.7699 |  |  | -0.17129 | 0.52249 | -0.83466 | -1.4529 | 6.1994 | 5.8998 | 7.1283 | -3.2647 | 18.7785 | 46.3675 | 29.0796 | 0.00064397 | 0.00059469 | -0.00083782 | 17.1905 | 16.4581 | 16.9931 | 17.3461 | 17.2901 | 16.2445 | 14.617 | 16.6829 | 17.036 | 17.3552 | 17.3927 | 17.0979 | 16.2604 | 14.4626 | 850.0612 | 595.487 | 614.4223 | 387.4787 | 324.2602 | 748.0318 | 461.1912 | 15.504 | 17.0828 | 19.2281 | 29.6108 | 64.6912 | 75.2288 |  |  |  | 581.5295 | 554.1074 | 556.8057 | 575.2637 | 108.5947 | 58.4982 | 830.461 |  |  | 416.7782 |  |  | 17.508 | 30.5549 | 284.0525 | 16.6266 | 25.1671 | 872.0605 | 747.7582 | 585.6342 | 825.0714 | 819.1836 | 750.1998 |  | 790.1066 | 876.8431 | 926.5281 | 572.0073 | 655.0952 | 835.6064 |  | 946.9452 |  |  | 410.0692 | 641.9755 | 731.4834 | [6 empty] | 576.5858 |  |  | 375.5968 |  |  | 463.2776 | 633.1788 | 648.224 | 755.2549 | 983.3634 | 1016.9414 | 518.5109 | 696.8418 | 796.8625 | 588.3401 | 659.0662 | 916.1845 | 1048.2726 | 617.9673 | 772.6946 | 819.2601 | 1035.0713 | 1036.1675 | 497.6942 | 602.9914 | 674.8833 | 561.0643 | 709.4559 | 856.8687 | 964.2372 | 1049.3886 | 561.8297 | 649.2019 | 638.2701 | 803.3756 | 83.0626 | -0.00026554 | 18.2768 | 3.4659 | -39.1191 | 3.1238 | 10877.11 | 0.23 | -0.88556 | 1.4782 | -1.8683 | -2.465 | 5.9198 | 5.775 | 6.3479 | 73.5747 | 118.8272 | 44.4033 | 50.3222 | -0.53742 | 45.6948 | 30.429
42810.4505 | 902 | 17.9753 | 18.2782 | 18.345 | 18.3509 | 17.6441 | 16.2586 | 14.5258 | 16.5171 | 17.013 | 17.1235 | 17.1255 | 16.6392 | 15.6455 | 14.3008 | 14.399 | 16.1109 | 17.5754 | 29.638 | 23.5341 | 79.4552 |  |  |  | 17.1175 | 51.7787 | 178.1786 | 659.0314 | 702.8941 | 669.569 | 100.7936 | 111.1693 | 955.4066 | 90.3168 | 97.1599 | 852.6864 | 753.3834 | 866.668 |  | 239.9823 | 925.453 | 948.0706 | 451.1124 | 838.7939 | 325.95 | 589.226 | 413.2334 | 584.6019 | 746.4839 | 896.9624 | 958.9944 | 43.7353 | 312.2886 | 59.4632 | 527.714 | 13.7602 | 50.1285 | 49.046 | 48.6112 | 42.1947 |  |  | -0.062205 | 0.48175 | -1.4668 | -1.2564 | 7.3783 | 6.3532 | 6.7275 | -3.2884 | 16.9818 | 44.8597 | 28.9527 | 0.00065876 | 0.0006489 | -0.00084439 | 17.1962 | 16.4536 | 16.9864 | 17.3372 | 17.2882 | 16.2537 | 14.6114 | 16.6932 | 17.043 | 17.3559 | 17.3965 | 17.1003 | 16.2577 | 14.462 | 856.6808 | 606.8812 | 649.1668 | 411.8531 | 334.4235 | 750.3271 | 463.9257 | 15.5038 | 17.1131 | 19.2898 | 29.7812 | 64.9123 | 75.3635 |  |  |  | 581.833 | 553.984 | 556.3213 | 576.4083 | 98.0773 | 45.6696 | 831.6547 |  |  | 421.6039 |  |  | 17.5052 | 30.7034 | 294.887 | 16.6155 | 25.3425 | 868.4142 | 746.1624 | 585.2817 | 821.027 | 815.1417 | 745.3639 |  | 791.0288 | 872.4959 | 928.1583 | 571.1464 | 655.2459 | 837.3657 |  | 948.4469 |  |  | 410.3128 | 637.3473 | 730.437 | [6 empty] | 575.9982 |  |  | 375.3473 |  |  | 463.3977 | 633.645 | 648.8612 | 756.9187 | 991.0976 | 1021.021 | 519.2163 | 697.2849 | 796.4881 | 588.885 | 659.4899 | 918.9251 | 1052.2733 | 618.6863 | 774.8982 | 819.0974 | 1037.8031 | 1036.2644 | 498.0616 | 603.3907 | 674.6419 | 560.9859 | 709.3466 | 859.8078 | 967.2735 | 1050.9026 | 562.3448 | 649.6535 | 638.5096 | 802.0146 | 82.3365 | -0.001416 | 18.2758 | 3.4994 | -39.0761 | 3.1238 | 10860.49 | 0.35 | -0.53367 | 1.4205 | -2.4786 | -2.2939 | 6.4753 | 6.0086 | 6.1831 | 73.9864 | 119.6329 | 44.4588 | 50.398 | -3.8471 | 71.358 | 30.4486
42810.4505 | 903 | 17.9689 | 18.2804 | 18.3427 | 18.3548 | 17.6468 | 16.2646 | 14.5378 | 16.5224 | 17.0197 | 17.1326 | 17.1329 | 16.6372 | 15.6434 | 14.3008 | 14.3883 | 16.1362 | 17.6128 | 30.0386 | 23.7631 | 79.7146 |  |  |  | 17.1163 | 52.5034 | 179.7422 | 658.9875 | 703.4231 | 668.4449 | 96.0223 | 106.7313 | 964.1386 | 102.9744 | 112.3033 | 867.8042 | 525.9239 | 875.0849 |  | 248.1021 | 917.1124 | 936.1624 | 475.0361 |  | 327.2924 | 590.4672 | 414.7925 | 587.4261 | 748.9371 | 898.8727 | 961.3239 | 45.8096 | 313.4439 | 59.6335 | 528.5198 | 13.767 | 50.1682 | 49.0548 | 48.6411 | 42.5402 |  |  | -0.59513 | 0.35165 | -1.0791 | -1.0816 | 6.9051 | 5.5318 | 6.7702 | -3.2049 | 18.3817 | 43.5403 | 28.3903 | 0.00062426 | 0.00068176 | -0.00082139 | 17.2196 | 16.4601 | 16.9972 | 17.3391 | 17.2946 | 16.2498 | 14.616 | 16.6994 | 17.0486 | 17.3589 | 17.3965 | 17.1064 | 16.2608 | 14.4607 | 851.3874 | 607.2685 | 629.5898 | 398.509 | 312.0363 | 752.3612 | 465.903 | 15.5042 | 17.1409 | 19.348 | 29.9555 | 65.1225 | 75.4934 |  |  |  | 582.2963 | 554.5715 | 556.5092 | 578.1069 | 111.2655 | 52.9778 | 827.0641 |  |  | 418.0222 |  |  | 17.5 | 30.8187 | 292.4971 | 16.6199 | 25.4613 | 875.5943 | 743.8874 | 585.196 | 818.5079 | 812.2483 | 739.2307 |  | 791.3896 | 866.2962 | 929.8863 | 570.5891 | 655.4961 | 837.0251 |  | 949.2123 |  |  | 410.519 | 631.7848 | 727.0957 | [6 empty] | 575.5901 |  |  | 374.7053 |  |  | 463.8531 | 634.2414 | 650.3037 | 756.6777 | 994.5619 | 1023.0614 | 519.6072 | 697.9244 | 797.7274 | 589.533 | 659.9999 | 918.5549 | 1054.1329 | 619.5168 | 775.9817 | 820.0752 | 1042.8948 | 1038.5016 | 499.0447 | 603.5795 | 674.015 | 561.1363 | 709.5995 | 860.1273 | 967.3235 | 1056.2347 | 562.6459 | 649.2606 | 638.9327 | 801.4031 | 84.5506 | -0.00017432 | 18.2767 | 3.5159 | -38.9869 | 3.1238 | 10825.81 | 0.26 | -1.6497 | 1.2145 | -2.1274 | -2.1299 | 6.2693 | 5.6114 | 6.2078 | 74.2655 | 120.534 | 44.5266 | 51.7082 | -1.2719 | 24.5305 | 30.48
42810.4505 | 904 | 17.9664 | 18.2895 | 18.3551 | 18.3433 | 17.6506 | 16.256 | 14.5413 | 16.5208 | 17.0163 | 17.1272 | 17.1263 | 16.6402 | 15.6498 | 14.3017 | 14.3844 | 16.176 | 17.6476 | 30.4462 | 23.783 | 79.9557 |  |  |  | 17.1202 | 53.1948 | 179.428 | 658.1817 | 704.081 | 667.1454 | 89.6295 | 95.3311 | 965.9298 | 96.4765 | 108.5647 | 865.553 | 625.6764 | 868.0238 |  | 248.0031 | 928.6263 | 945.9461 | 495.4434 |  | 327.6214 | 590.8598 | 416.1054 | 591.2098 | 749.0746 | 896.922 | 962.8814 | 47.6281 | 314.4568 | 60.3095 | 529.2822 | 13.7676 | 50.2052 | 49.0569 | 48.6898 | 42.8867 |  |  | -0.033949 | 0.4213 | -0.5981 | -1.4187 | 6.6357 | 5.5555 | 6.9344 | -2.946 | 18.0939 | 44.087 | 28.6326 | 0.00061276 | 0.00064233 | -0.0008871 | 17.2392 | 16.4617 | 17.0043 | 17.3476 | 17.3071 | 16.2571 | 14.6332 | 16.7077 | 17.0553 | 17.3592 | 17.3996 | 17.1204 | 16.2709 | 14.4701 | 859.5363 | 617.4868 | 643.0034 | 405.8906 | 312.3645 | 754.8862 | 468.5754 | 15.5129 | 17.1868 | 19.4203 | 30.1555 | 65.3469 | 75.6315 |  |  |  | 582.5872 | 552.9533 | 555.1479 | 576.4536 | 102.0156 | 56.0861 | 823.8886 |  |  | 413.9178 |  |  | 17.5107 | 30.9516 | 295.2202 | 16.6256 | 25.6332 | 885.4716 | 743.116 | 585.298 | 812.0193 | 805.611 | 736.7027 |  | 791.7547 | 858.6636 | 930.5379 | 569.8851 | 655.7054 | 833.8493 |  | 949.7694 |  |  | 410.7385 | 627.5906 | 724.6829 | [6 empty] | 575.4146 |  |  | 373.5347 |  |  | 464.325 | 634.4723 | 651.4954 | 754.0045 | 992.4924 | 1024.7371 | 519.6591 | 697.9849 | 799.2285 | 590.0585 | 660.6542 | 915.1908 | 1055.2696 | 620.1766 | 775.0038 | 821.2518 | 1044.7379 | 1040.4754 | 499.4229 | 603.8574 | 673.7152 | 561.4597 | 710.6116 | 860.5097 | 965.5322 | 1057.9172 | 563.0468 | 649.6363 | 639.2983 | 803.6282 | 79.4294 | -0.00087586 | 18.2777 | 3.5214 | -38.9306 | 3.1238 | 10854.14 | 0.31 | -0.39374 | 1.3296 | -1.5842 | -2.4399 | 6.1407 | 5.6187 | 6.2774 | 74.4458 | 121.0216 | 44.59 | 51.7033 | -2.2194 | 40.6248 | 30.5754
42810.4505 | 905 | 17.9678 | 18.2795 | 18.3501 | 18.3497 | 17.653 | 16.2614 | 14.5423 | 16.5262 | 17.0308 | 17.1323 | 17.1329 | 16.6473 | 15.6577 | 14.3062 | 14.393 | 16.2247 | 17.6987 | 30.8698 | 23.8033 | 80.2021 |  |  |  | 17.1293 | 53.8515 | 178.8476 | 659.8281 | 703.5637 | 669.5645 | 84.1876 | 93.9176 | 965.8713 | 90.1086 | 102.0667 | 861.4089 | 578.8836 | 873.6925 |  | 236.7894 | 932.1172 | 950.0112 | 486.968 |  | 327.5866 | 590.9392 | 417.8631 | 592.8996 | 745.4309 | 890.2837 | 962.5003 | 49.1351 | 315.3077 | 61.9549 | 530.1614 | 13.7668 | 50.2525 | 49.0905 | 48.7372 | 43.1958 |  |  | -0.26328 | 0.083543 | -1.0456 | -1.0047 | 6.5437 | 6.5076 | 7.1539 | -2.3986 | 17.7061 | 44.0207 | 27.9983 | 0.0006029 | 0.00059962 | -0.00085918 | 17.2538 | 16.4606 | 17.0009 | 17.3466 | 17.3086 | 16.2635 | 14.633 | 16.6992 | 17.0559 | 17.3598 | 17.4066 | 17.1157 | 16.276 | 14.4719 | 873.7647 | 630.847 | 631.5147 | 414.4924 | 330.4707 | 757.2616 | 470.9316 | 15.514 | 17.2177 | 19.4789 | 30.339 | 65.5736 | 75.7633 |  |  |  | 582.9162 | 551.0555 | 553.9834 | 578.6942 | 101.8554 | 52.1344 | 817.6721 |  |  | 411.9336 |  |  | 17.4868 | 31.0787 | 297.3669 | 16.6038 | 25.7725 | 887.534 | 741.6093 | 585.6797 | 804.7041 | 798.0508 | 735.6304 |  | 791.8503 | 850.8378 | 929.8993 | 569.6319 | 655.9812 | 834.6128 |  | 950.0024 |  |  | 411.894 | 625.7283 | 723.5493 | [6 empty] | 575.4554 |  |  | 372.34 |  |  | 465.0793 | 634.3713 | 650.8837 | 750.3356 | 992.5661 | 1024.3267 | 519.3991 | 697.9029 | 799.1689 | 590.4385 | 660.5184 | 913.7829 | 1053.3433 | 620.4027 | 775.5985 | 821.8611 | 1046.3586 | 1040.598 | 499.9857 | 604.2771 | 674.4854 | 561.3398 | 710.8059 | 861.3793 | 962.8289 | 1057.5091 | 563.5488 | 651.1414 | 639.1332 | 801.9909 | 80.0162 | -0.0020053 | 18.2774 | 3.5228 | -38.9428 | 3.1238 | 10914.25 | 0.26 | -1.0979 | 0.59211 | -2.0947 | -2.0534 | 6.0807 | 6.0639 | 6.3578 | 74.5044 | 120.9689 | 44.6549 | 50.9736 | -0.46194 | 32.4352 | 30.569
42810.4505 | 906 | 17.9646 | 18.2813 | 18.3477 | 18.3468 | 17.6528 | 16.2618 | 14.5497 | 16.5304 | 17.033 | 17.1386 | 17.1387 | 16.6483 | 15.6542 | 14.3095 | 14.3863 | 16.2627 | 17.7407 | 31.2826 | 23.6878 | 80.4396 |  |  |  | 17.1385 | 54.4675 | 181.5533 | 660.5078 | 703.0964 | 669.5172 | 84.1271 | 90.7727 | 956.8478 | 95.1788 | 105.0901 | 857.6366 | 457.5269 | 872.3956 |  | 227.5242 | 947.4445 | 964.036 | 465.4186 |  | 328.0469 | 591.9622 | 418.2232 | 594.4394 | 740.581 | 892.2567 | 961.1814 | 49.7168 | 316.139 | 63.945 | 531.5455 | 13.7832 | 50.3008 | 49.1222 | 48.7699 | 43.5397 |  |  | 0.083671 | -0.15893 | -0.59481 | -0.26022 | 7.4039 | 5.9169 | 6.416 | -2.5682 | 16.9471 | 42.9018 | 27.8177 | 0.00059305 | 0.00056512 | -0.00087068 | 17.2664 | 16.4567 | 16.9916 | 17.3431 | 17.3003 | 16.2551 | 14.628 | 16.6998 | 17.0536 | 17.3583 | 17.3967 | 17.1086 | 16.2711 | 14.4663 | 865.4318 | 618.339 | 616.547 | 416.7556 | 336.5708 | 758.6496 | 472.8097 | 15.5096 | 17.2543 | 19.5424 | 30.5273 | 65.7829 | 75.8993 |  |  |  | 583.4542 | 551.6466 | 554.116 | 582.5771 | 88.4957 | 42.6678 | 810.0472 |  |  | 411.6947 |  |  | 17.5013 | 31.19 | 297.4343 | 16.6193 | 25.9236 | 884.082 | 741.3088 | 585.8262 | 799.0337 | 791.9035 | 735.1631 |  | 791.9404 | 837.2554 | 929.2605 | 569.6398 | 656.167 | 830.7765 |  | 950.5164 |  |  | 413.2723 | 626.5372 | 722.7718 | [6 empty] | 575.6561 |  |  | 371.6424 |  |  | 465.254 | 634.5932 | 650.1268 | 748.1061 | 991.3415 | 1024.9386 | 519.5442 | 697.7017 | 798.4311 | 590.5058 | 660.2088 | 909.7327 | 1055.0943 | 620.7135 | 775.1344 | 827.7201 | 1048.5075 | 1038.8486 | 500.4601 | 604.5749 | 676.3982 | 561.4571 | 710.6813 | 861.9616 | 966.4592 | 1055.0628 | 564.2625 | 652.0288 | 639.3423 | 800.6737 | 79.1212 | -0.0019211 | 18.2774 | 3.5226 | -38.8529 | 3.1237 | 10984.12 | 0.31 | 0.61892 | -0.81717 | -1.5809 | -1.0456 | 6.4734 | 5.787 | 6.0261 | 74.5446 | 121.0764 | 44.6936 | 52.3988 | 1.586 | 15.9424 | 30.5528
42810.4505 | 907 | 17.9572 | 18.2749 | 18.3364 | 18.3399 | 17.6433 | 16.2525 | 14.5344 | 16.5197 | 17.0236 | 17.1374 | 17.1361 | 16.6416 | 15.6494 | 14.3077 | 14.3916 | 16.2916 | 17.7887 | 31.6955 | 23.9927 | 80.672 |  |  |  | 17.127 | 55.1005 | 183.2202 | 660.5154 | 703.126 | 671.7392 | 90.1374 | 93.9055 | 960.9925 | 90.7916 | 99.6916 | 858.0681 | 632.5211 | 871.6672 |  | 229.5966 | 950.2271 | 968.4477 | 444.5111 |  | 329.8473 | 591.8001 | 419.2632 | 594.3032 | 736.5547 | 893.4996 | 960.2089 | 49.5679 | 316.962 | 63.6749 | 532.5502 | 13.7851 | 50.3402 | 49.1579 | 48.8293 | 43.89 |  |  | 0.061987 | -0.6682 | -0.98514 | -0.93639 | 7.0471 | 6.3604 | 7.4049 | -2.5931 | 18.1093 | 45.1043 | 28.2308 | 0.00060948 | 0.00062919 | -0.00086082 | 17.2845 | 16.4551 | 16.9945 | 17.3486 | 17.296 | 16.2495 | 14.6187 | 16.6945 | 17.0476 | 17.3632 | 17.3938 | 17.1109 | 16.2689 | 14.4678 | 839.6433 | 603.1824 | 602.2409 | 397.8705 | 327.9037 | 758.8224 | 474.1167 | 15.5062 | 17.2835 | 19.607 | 30.7073 | 65.99 | 76.0191 |  |  |  | 584.0867 | 552.1577 | 553.9081 | 584.9955 | 96.6528 | 45.9908 | 803.3457 |  |  | 413.724 |  |  | 17.5112 | 31.3295 | 295.8758 | 16.6117 | 26.0986 | 889.1494 | 743.3617 | 585.9653 | 794.6318 | 786.678 | 737.6234 |  | 792.1988 | 824.2725 | 929.846 | 570.338 | 656.3413 | 823.0571 |  | 951.3198 |  |  | 413.8631 | 626.1157 | 724.3184 | [6 empty] | 576.1278 |  |  | 372.5554 |  |  | 465.5563 | 634.6508 | 650.0007 | 749.7878 | 989.0254 | 1025.5559 | 519.8329 | 696.9533 | 800.7042 | 590.7428 | 660.6719 | 905.637 | 1053.5506 | 620.407 | 776.0084 | 829.2894 | 1048.581 | 1034.6149 | 500.7325 | 605.0615 | 676.2773 | 561.6035 | 711.1492 | 864.5254 | 970.1165 | 1052.5039 | 564.8216 | 651.6835 | 639.7623 | 801.7604 | 84.9807 | -0.0013038 | 18.2766 | 3.5194 | -38.8281 | 3.1237 | 11089.29 | 0.31 | 0.53334 | -1.6754 | -2.0343 | -1.9833 | 6.3189 | 6.0032 | 6.4774 | 74.5542 | 121.6843 | 44.7108 | 55.3265 | 3.4441 | 43.3699 | 30.5934
42810.4505 | 908 | 17.9566 | 18.2667 | 18.335 | 18.3376 | 17.645 | 16.2472 | 14.5346 | 16.52 | 17.0259 | 17.1299 | 17.1352 | 16.6432 | 15.6516 | 14.3082 | 14.3938 | 16.3387 | 17.8316 | 32.1907 | 24.099 | 80.9358 |  |  |  | 17.1359 | 55.7513 | 183.3389 | 661.1965 | 704.5236 | 672.5018 | 95.666 | 96.6089 | 965.242 | 90.2854 | 97.6556 | 856.8007 | 719.248 | 876.5789 | 1334.0365 | 229.2056 | 950.1487 | 960.9515 | 456.3823 | 1194.9182 | 332.0975 | 592.1584 | 421.6035 | 596.2563 | 740.3044 | 900.2229 | 958.8836 | 49.6027 | 317.9956 | 64.0853 | 533.5313 | 13.7867 | 50.4221 | 49.1795 | 48.8809 | 44.2462 |  |  | -0.44925 | -0.33832 | -0.64738 | -1.6382 | 7.398 | 6.1784 | 6.3812 | -2.2376 | 18.7151 | 46.4449 | 28.9107 | 0.00058155 | 0.00051912 | -0.00087561 | 17.2963 | 16.4482 | 16.9889 | 17.3307 | 17.2961 | 16.2489 | 14.6155 | 16.6939 | 17.0447 | 17.3579 | 17.4004 | 17.1097 | 16.2752 | 14.4651 | 844.7083 | 604.5313 | 606.1914 | 387.7402 | 319.0955 | 760.2536 | 475.735 | 15.5117 | 17.3235 | 19.6702 | 30.8944 | 66.2017 | 76.1441 |  |  |  | 584.5387 | 552.5746 | 554.3384 | 583.6339 | 119.8957 | 54.629 | 797.5013 |  |  | 409.3619 |  |  | 17.5017 | 31.4453 | 299.0578 | 16.5932 | 26.2286 | 887.1624 | 742.9645 | 587.4475 | 790.7333 | 782.6146 | 738.8624 |  | 792.2866 | 812.6104 | 930.3297 | 571.7498 | 656.8167 | 814.4522 |  | 951.4651 |  |  | 414.4902 | 628.9354 | 725.1416 | [6 empty] | 577.6507 |  |  | 374.0855 |  |  | 465.9753 | 634.9324 | 652.9605 | 750.8355 | 986.8828 | 1024.5757 | 520.0989 | 696.5565 | 803.5726 | 591.0286 | 663.765 | 904.8574 | 1049.6874 | 620.8745 | 775.0324 | 829.661 | 1046.7029 | 1032.3932 | 500.5642 | 605.1837 | 676.0546 | 561.6623 | 711.9116 | 864.9335 | 976.1127 | 1052.7118 | 565.3813 | 651.2877 | 640.4974 | 802.6712 | 90.2812 | -0.00069348 | 18.2757 | 3.515 | -38.9788 | 3.1237 | 11254.52 | 0.32 | -1.4364 | -1.1924 | -1.6494 | -2.6238 | 6.4929 | 5.9337 | 6.0302 | 74.5463 | 122.2128 | 44.7714 | 55.2802 | 3.3386 | 62.2973 | 30.7084
42810.4506 | 909 | 17.9558 | 18.2673 | 18.336 | 18.3351 | 17.6513 | 16.2584 | 14.5356 | 16.5261 | 17.0266 | 17.1319 | 17.1371 | 16.6429 | 15.6549 | 14.3107 | 14.3847 | 16.3847 | 17.8855 | 32.68 | 24.1094 | 81.1899 |  |  |  | 17.1546 | 56.3877 | 187.6416 | 662.2429 | 705.3821 | 673.5719 | 103.5537 | 104.8278 | 971.4625 | 90.2639 | 94.913 | 854.6882 | 791.7451 | 868.5775 |  | 235.8189 | 948.1767 | 955.9408 | 464.4261 | 1184.9252 | 332.9062 | 594.1005 | 422.6211 | 598.6265 | 747.4003 | 904.9279 | 961.6466 | 50.0237 | 319.1105 | 66.2881 | 534.4278 | 13.7875 | 50.5042 | 49.1827 | 48.9041 | 44.6318 |  |  | -0.4453 | -0.43295 | -1.0423 | -1.4305 | 7.5642 | 6.2198 | 6.8438 | -2.0234 | 19.2317 | 46.5121 | 28.0861 | 0.00057826 | 0.00061769 | -0.00086246 | 17.3089 | 16.4418 | 16.9832 | 17.332 | 17.2896 | 16.2422 | 14.608 | 16.6905 | 17.0408 | 17.3492 | 17.403 | 17.1073 | 16.2684 | 14.462 | 867.3895 | 629.5847 | 635.9497 | 391.064 | 324.3827 | 763.1133 | 478.2832 | 15.5118 | 17.3607 | 19.7271 | 31.0728 | 66.4039 | 76.2689 |  |  |  | 584.7936 | 551.9899 | 554.589 | 580.5308 | 112.8375 | 59.2789 | 793.5645 |  |  | 405.5469 |  |  | 17.5309 | 31.5746 | 306.1992 | 16.6667 | 26.3889 | 884.1668 | 743.415 | 588.9803 | 790.8483 | 782.167 | 739.8704 |  | 792.7029 | 805.3944 | 930.6623 | 573.2332 | 657.4566 | 807.898 |  | 951.0558 |  |  | 415.7735 | 630.8508 | 725.2626 | [6 empty] | 579.0139 |  |  | 374.235 |  |  | 466.1541 | 635.9008 | 655.1277 | 748.1275 | 984.3981 | 1023.9819 | 520.6869 | 697.3124 | 803.3468 | 591.4258 | 663.6645 | 899.8463 | 1042.9827 | 621.9718 | 776.3845 | 832.513 | 1047.2223 | 1036.9847 | 500.7984 | 605.2283 | 675.0124 | 562.0517 | 712.7802 | 868.5601 | 970.9688 | 1058.47 | 565.8751 | 651.3559 | 641.2029 | 803.7315 | 86.0523 | 0.0017128 | 18.2774 | 3.5042 | -39.1212 | 3.1237 | 11413.14 | 0.29 | -1.4309 | -1.3504 | -2.0953 | -2.4546 | 6.5786 | 5.9654 | 6.2575 | 74.6442 | 122.554 | 44.8649 | 53.7966 | 0.55926 | 82.0061 | 30.8382
42810.4506 | 910 | 17.9478 | 18.263 | 18.3322 | 18.3328 | 17.6426 | 16.2465 | 14.544 | 16.5166 | 17.0273 | 17.1306 | 17.1342 | 16.6369 | 15.6548 | 14.3051 | 14.3927 | 16.4279 | 17.9361 | 33.1913 | 23.8768 | 81.4404 |  |  |  | 17.1408 | 57.0294 | 187.9513 | 665.6935 | 706.1596 | 676.7176 | 93.5932 | 109.1932 | 974.3815 | 101.32 | 105.6545 | 861.9026 | 692.962 | 869.2483 |  | 250.6508 | 934.764 | 947.6581 | 465.0465 | 1358.969 | 335.0069 | 596.3946 | 423.2819 | 600.0371 | 752.1384 | 906.7781 | 965.2871 | 50.92 | 320.2048 | 68.8817 | 535.5448 | 13.7908 | 50.5723 | 49.1707 | 48.9318 | 45.0431 |  |  | 0.25124 | -0.57686 | -1.4924 | -1.4174 | 7.2015 | 5.4503 | 7.1388 | -2.7561 | 18.3619 | 45.4429 | 26.6442 | 0.00055362 | 0.00063083 | -0.00084768 | 17.3306 | 16.4486 | 16.9903 | 17.3337 | 17.2953 | 16.2552 | 14.6234 | 16.6942 | 17.0511 | 17.3617 | 17.4127 | 17.1149 | 16.277 | 14.4759 | 872.8567 | 631.2495 | 673.3173 | 434.2968 | 351.6824 | 765.5919 | 481.4052 | 15.5129 | 17.4127 | 19.8033 | 31.2959 | 66.6471 | 76.4178 |  |  |  | 584.9717 | 550.7999 | 554.1661 | 578.3903 | 101.9729 | 47.5354 | 794.0497 |  |  | 405.021 |  |  | 17.516 | 31.7208 | 302.3533 | 16.6346 | 26.5453 | 875.607 | 744.2405 | 589.8814 | 790.5097 | 782.9925 | 738.9511 |  | 793.2408 | 810.7378 | 930.4936 | 574.4364 | 657.8338 | 807.0684 |  | 950.7432 |  |  | 417.1178 | 630.3393 | 726.1234 | [6 empty] | 580.1604 |  |  | 374.7552 |  |  | 466.4545 | 636.4535 | 654.4517 | 743.3046 | 980.5203 | 1023.6772 | 521.2174 | 697.9001 | 803.3429 | 592.2311 | 663.5175 | 896.1204 | 1040.6716 | 622.5859 | 777.8874 | 838.5561 | 1048.1942 | 1038.7176 | 502.0829 | 605.1958 | 676.2353 | 562.4544 | 713.4436 | 873.3311 | 968.0759 | 1060.5007 | 566.2147 | 652.0044 | 641.4626 | 804.109 | 83.5928 | -0.0010372 | 18.2774 | 3.5 | -39.0634 | 3.1237 | 11544.41 | 0.29 | 1.0766 | -1.5608 | -2.5105 | -2.4466 | 6.424 | 5.5886 | 6.396 | 74.8325 | 122.3342 | 44.9109 | 54.0923 | -2.9435 | 55.7271 | 30.9281
42810.4506 | 911 | 17.9501 | 18.257 | 18.3312 | 18.333 | 17.6421 | 16.2516 | 14.541 | 16.5236 | 17.0235 | 17.1348 | 17.1351 | 16.6417 | 15.6495 | 14.3076 | 14.3963 | 16.4719 | 17.9758 | 33.7127 | 23.7602 | 81.6586 |  |  |  | 17.1491 | 57.6572 | 194.9389 | 669.0509 | 707.6489 | 680.3234 | 93.4887 | 99.4948 | 957.2241 | 102.9304 | 111.8768 | 875.7807 | 495.4958 | 875.6612 |  | 253.5086 | 928.1257 | 935.3487 | 480.9663 | 1209.2082 | 336.7889 | 597.5898 | 423.6237 | 599.9735 | 750.584 | 904.0077 | 963.9451 | 50.0486 | 321.2438 | 71.6658 | 536.9943 | 13.8007 | 50.6476 | 49.1656 | 48.9521 | 45.4023 |  |  | 0.69019 | 0.30039 | -0.78406 | -0.90551 | 7.555 | 6.7153 | 6.2129 | -2.4965 | 18.6516 | 45.6613 | 25.8116 | 0.00057005 | 0.00056512 | -0.00084604 | 17.347 | 16.4488 | 16.9848 | 17.3316 | 17.3004 | 16.2502 | 14.6259 | 16.697 | 17.0481 | 17.3649 | 17.4105 | 17.1164 | 16.2778 | 14.4748 | 883.622 | 619.6366 | 643.9635 | 426.5122 | 340.1 | 767.3978 | 482.9529 | 15.5037 | 17.4388 | 19.8652 | 31.4749 | 66.836 | 76.5529 |  |  |  | 585.3281 | 552.6259 | 554.878 | 581.3588 | 88.0774 | 45.1618 | 794.8906 |  |  | 404.0903 |  |  | 17.5164 | 31.8404 | 309.6446 | 16.6426 | 26.694 | 867.2337 | 745.2665 | 591.5361 | 789.4301 | 782.4714 | 738.647 |  | 793.9646 | 823.601 | 929.8874 | 576.0118 | 658.2676 | 811.2749 |  | 950.6445 |  |  | 417.716 | 630.5387 | 726.8549 | [6 empty] | 582.0348 |  |  | 376.397 |  |  | 467.0578 | 637.0242 | 654.2285 | 740.7318 | 978.8416 | 1024.5952 | 521.4517 | 697.9711 | 803.3107 | 593.1179 | 663.6865 | 899.4831 | 1042.1047 | 623.136 | 777.99 | 839.6308 | 1047.354 | 1040.9699 | 502.8443 | 605.2889 | 678.7498 | 562.379 | 713.9005 | 875.1452 | 964.9591 | 1061.9693 | 566.2047 | 652.6432 | 641.6638 | 805.7761 | 81.5095 | 0.00030269 | 18.2776 | 3.4951 | -39.0835 | 3.1237 | 11555.7 | 0.37 | 1.7877 | 1.1271 | -1.8209 | -1.9568 | 6.5721 | 6.1961 | 5.9598 | 75.0603 | 121.7204 | 44.9586 | 53.557 | 0.64127 | 20.1955 | 30.9067
42810.4506 | 912 | 17.9393 | 18.261 | 18.3223 | 18.3393 | 17.6324 | 16.2509 | 14.5511 | 16.5181 | 17.0248 | 17.1306 | 17.1338 | 16.6448 | 15.656 | 14.3011 | 14.3871 | 16.5085 | 18.0129 | 34.2418 | 23.9218 | 81.8665 |  |  |  | 17.1471 | 58.2506 | 193.9939 | 670.4309 | 706.4343 | 682.1771 | 89.3796 | 102.6475 | 946.8807 | 97.0532 | 107.303 | 880.2948 | 462.7396 | 895.3973 |  | 233.3924 | 931.9271 | 939.5243 | 481.0667 |  | 338.2144 | 598.3764 | 424.3575 | 605.0836 | 754.693 | 906.4591 | 966.4081 | 48.8598 | 321.9034 | 72.7252 | 538.3386 | 13.8051 | 50.727 | 49.15 | 48.9645 | 45.7418 |  |  | 0.56008 | 0.019803 | -0.50413 | -0.99027 | 6.7435 | 5.6383 | 6.3628 | -3.3449 | 17.8182 | 46.9273 | 25.3109 | 0.00056183 | 0.00058812 | -0.00086246 | 17.363 | 16.4417 | 16.9793 | 17.3294 | 17.286 | 16.2426 | 14.6221 | 16.6957 | 17.0448 | 17.3603 | 17.4042 | 17.1135 | 16.2705 | 14.481 | 858.3455 | 614.7078 | 636.47 | 411.1997 | 320.961 | 768.7074 | 484.6691 | 15.5077 | 17.4774 | 19.9359 | 31.6646 | 67.0246 | 76.6704 |  |  |  | 585.8512 | 555.5236 | 556.5628 | 584.7792 | 121.8909 | 59.6683 | 793.2443 |  |  | 401.8982 |  |  | 17.5031 | 31.9494 | 308.5953 | 16.6302 | 26.8498 | 865.6857 | 745.2557 | 592.9731 | 786.8571 | 779.8361 | 738.398 |  | 794.3817 | 822.3156 | 929.6002 | 577.7155 | 658.8603 | 811.83 |  | 951.3911 |  |  | 418.1118 | 629.7385 | 726.6209 | [6 empty] | 583.7374 |  |  | 377.6488 |  |  | 467.6904 | 637.4011 | 654.3662 | 740.2163 | 980.954 | 1027.7969 | 521.5521 | 697.5239 | 802.5193 | 593.6661 | 663.7739 | 904.6668 | 1049.1949 | 623.4379 | 777.2631 | 840.5283 | 1047.6822 | 1048.3271 | 502.9471 | 605.2555 | 680.5997 | 562.8623 | 714.7583 | 875.8615 | 963.2539 | 1066.1876 | 566.7288 | 653.8518 | 642.3192 | 810.2615 | 82.5297 | -0.0017388 | 18.277 | 3.4946 | -39.0924 | 3.1236 | 11544.9 | 0.28 | 1.612 | 0.28952 | -1.4608 | -2.0473 | 6.2155 | 5.6834 | 6.0375 | 75.1938 | 121.6348 | 45.0365 | 56.8463 | 1.8334 | 16.1187 | 30.9013
42810.4506 | 913 | 17.9373 | 18.2618 | 18.3286 | 18.3386 | 17.6472 | 16.253 | 14.5466 | 16.5206 | 17.0231 | 17.1368 | 17.13 | 16.6472 | 15.6569 | 14.3128 | 14.3815 | 16.5574 | 18.0692 | 34.7939 | 24.0793 | 82.0859 |  |  |  | 17.1535 | 58.8345 | 196.3758 | 672.5799 | 707.2213 | 685.1177 | 89.4415 | 101.5835 | 951.9174 | 100.2533 | 107.1544 | 884.4866 | 527.9997 | 907.7858 |  | 223.1343 | 942.3191 | 949.5209 | 471.1601 |  | 340.4477 | 600.0053 | 426.6662 | 608.3861 | 759.6958 | 904.9099 | 968.6263 | 47.5378 | 322.7005 | 72.0614 | 539.5281 | 13.8052 | 50.8299 | 49.1398 | 48.9693 | 46.1269 |  |  | 0.88076 | -0.005169 | -0.8524 | -0.68209 | 6.5989 | 5.0672 | 6.5717 | -1.7993 | 18.8176 | 43.8354 | 24.9234 | 0.00054376 | 0.00060619 | -0.00085589 | 17.3803 | 16.4404 | 16.9822 | 17.337 | 17.2893 | 16.2507 | 14.6211 | 16.6995 | 17.0526 | 17.3612 | 17.4071 | 17.1257 | 16.2767 | 14.4752 | 873.0584 | 629.0655 | 669.0531 | 404.0118 | 323.7587 | 771.3813 | 487.4307 | 15.5093 | 17.5095 | 19.9959 | 31.849 | 67.2074 | 76.7821 |  |  |  | 586.5548 | 559.397 | 559.8412 | 588.5463 | 85.1621 | 45.6541 | 790.5849 |  |  | 398.1135 |  |  | 17.514 | 32.1085 | 310.8384 | 16.6356 | 27.0255 | 866.3189 | 744.9395 | 593.5857 | 784.1321 | 777.1899 | 737.9888 |  | 794.6017 | 815.6865 | 929.5698 | 578.3159 | 659.2448 | 809.0532 |  | 952.3822 |  |  | 418.5306 | 629.5707 | 726.7854 | [6 empty] | 584.5162 |  |  | 378.4818 |  |  | 468.1829 | 637.9985 | 654.9565 | 742.8477 | 988.6198 | 1029.5952 | 521.8214 | 697.7585 | 802.7889 | 594.0208 | 663.8069 | 907.2039 | 1051.839 | 623.9741 | 777.2062 | 842.9289 | 1048.1516 | 1055.983 | 503.6434 | 606.1213 | 682.0887 | 563.3954 | 715.8644 | 876.2262 | 961.5556 | 1069.8991 | 567.4834 | 655.8807 | 642.9239 | 815.1025 | 87.064 | 9.9273e-05 | 18.2762 | 3.5032 | -39.2373 | 3.1237 | 11459.12 | 0.27 | 2.0246 | -0.14805 | -1.9012 | -1.7007 | 6.1445 | 5.3844 | 6.1318 | 75.272 | 121.8061 | 45.1011 | 56.1971 | -1.206 | 24.937 | 30.9175
42810.4506 | 914 | 17.9369 | 18.2664 | 18.3309 | 18.3419 | 17.6417 | 16.256 | 14.5475 | 16.5238 | 17.0208 | 17.1309 | 17.1321 | 16.6525 | 15.6568 | 14.3108 | 14.3889 | 16.6095 | 18.1253 | 35.3698 | 24.0841 | 82.3223 |  |  |  | 17.16 | 59.4141 | 196.4256 | 673.6834 | 706.9139 | 686.8987 | 93.3641 | 103.9322 | 952.1956 | 99.8878 | 109.0345 | 885.5956 | 598.1418 | 900.2035 | 680.4341 | 223.7874 | 943.233 | 954.2097 | 446.7866 | 1376.0371 | 341.6841 | 601.761 | 430.0397 | 608.0206 | 755.8891 | 900.1955 | 967.2774 | 46.8384 | 323.3696 | 70.2231 | 540.3653 | 13.7973 | 50.9433 | 49.1105 | 48.9961 | 46.4671 |  |  | 0.10667 | 0.31485 | -1.1021 | -0.93311 | 6.1133 | 5.3879 | 6.0769 | -3.0157 | 18.992 | 45.3565 | 25.8659 | 0.00052077 | 0.00053062 | -0.00085753 | 17.3927 | 16.4301 | 16.971 | 17.3292 | 17.2769 | 16.2416 | 14.5973 | 16.6855 | 17.0508 | 17.3536 | 17.4043 | 17.1117 | 16.2757 | 14.4747 | 846.5915 | 616.497 | 641.7188 | 390.9151 | 325.6982 | 771.682 | 488.5142 | 15.5175 | 17.5542 | 20.0705 | 32.057 | 67.414 | 76.9144 |  |  |  | 587.2946 | 563.214 | 563.2885 | 588.3796 | 97.088 | 56.8748 | 787.7348 |  |  | 393.3461 |  |  | 17.5165 | 32.2211 | 309.654 | 16.6475 | 27.1676 | 860.6715 | 746.1437 | 593.5181 | 781.9775 | 774.9772 | 739.9274 |  | 794.9561 | 808.9368 | 929.4731 | 578.4345 | 659.4836 | 805.4905 |  | 953.0575 |  |  | 419.3818 | 633.6773 | 728.4171 | [6 empty] | 584.7305 |  |  | 378.8426 |  |  | 468.634 | 638.0866 | 655.714 | 742.2868 | 990.2491 | 1030.4324 | 522.4294 | 698.7544 | 805.1944 | 594.3693 | 663.9735 | 906.3202 | 1049.6295 | 624.6684 | 777.7435 | 844.7401 | 1049.7775 | 1059.9935 | 504.4246 | 607.0652 | 683.793 | 563.7292 | 716.6904 | 876.7653 | 957.4434 | 1071.5469 | 568.0107 | 656.5605 | 643.1432 | 819.8209 | 86.42 | -0.0057375 | 18.2771 | 3.5257 | -39.2795 | 3.1236 | 11409.56 | 0.24 | 0.70524 | 1.1566 | -2.164 | -1.9912 | 5.9023 | 5.541 | 5.8847 | 75.3259 | 121.9527 | 45.1484 | 59.2491 | 2.0599 | 36.881 | 31.0494
42810.4506 | 915 | 17.9336 | 18.258 | 18.3257 | 18.3364 | 17.6413 | 16.2473 | 14.5522 | 16.518 | 17.0192 | 17.1316 | 17.1382 | 16.6445 | 15.6481 | 14.3082 | 14.3856 | 16.6558 | 18.1721 | 35.9486 | 24.1427 | 82.5111 |  |  |  | 17.1645 | 59.9612 | 195.9624 | 672.9387 | 706.4379 | 685.6558 | 98.7567 | 102.5583 | 950.0174 | 97.4058 | 106.5056 | 882.2789 | 535.3502 | 891.4351 | 594.8343 | 231.5701 | 937.2748 | 946.4189 | 452.4248 | 838.5668 | 341.6424 | 603.5014 | 431.6739 | 608.8966 | 762.7866 | 900.5637 | 970.1096 | 45.9945 | 324.3043 | 67.8622 | 541.2492 | 13.8011 | 51.0441 | 49.1 | 49.0226 | 46.7917 |  |  | 0.33995 | -0.30547 | -0.9766 | -1.0514 | 6.9485 | 5.5049 | 5.0833 | -0.97072 | 17.1945 | 43.9563 | 26.184 | 0.00056841 | 0.00056841 | -0.00083946 | 17.418 | 16.4415 | 16.9773 | 17.3262 | 17.2813 | 16.2518 | 14.6231 | 16.7007 | 17.0544 | 17.3671 | 17.4071 | 17.1176 | 16.2833 | 14.4795 | 835.8965 | 618.9366 | 656.5684 | 410.0504 | 336.6937 | 771.9343 | 490.4508 | 15.5147 | 17.598 | 20.1465 | 32.2745 | 67.6297 | 77.0276 |  |  |  | 588.0678 | 567.4355 | 566.9851 | 592.0887 | 75.3525 | 41.2429 | 786.5288 |  |  | 392.2388 |  |  | 17.5323 | 32.351 | 307.5383 | 16.6308 | 27.3472 | 860.0435 | 746.0707 | 593.7632 | 784.4401 | 778.1376 | 741.2973 |  | 795.2548 | 812.1552 | 929.7976 | 578.9034 | 659.8529 | 807.2841 |  | 953.7071 |  |  | 421.2263 | 638.7164 | 730.175 | [6 empty] | 584.9064 |  |  | 379.4412 |  |  | 469.1269 | 638.2293 | 655.564 | 740.5388 | 988.0803 | 1029.0007 | 523.266 | 700.0027 | 805.0494 | 594.7926 | 664.4203 | 905.7244 | 1046.9464 | 625.6949 | 778.3742 | 845.1619 | 1049.9019 | 1060.935 | 504.3818 | 607.5644 | 684.851 | 563.7425 | 716.7497 | 876.8833 | 955.0817 | 1071.2762 | 568.6357 | 657.0813 | 643.2623 | 818.9209 | 92.3455 | -0.0002375 | 18.2774 | 3.55 | -39.3569 | 3.1236 | 11368.59 | 0.24 | 1.2582 | -1.1404 | -2.0391 | -2.1157 | 6.2935 | 5.6017 | 5.383 | 75.3787 | 122.0004 | 45.2136 | 60.5307 | 0.8199 | 26.5307 | 31.0797
42810.4506 | 916 | 17.9287 | 18.2518 | 18.3128 | 18.3301 | 17.6354 | 16.2376 | 14.5532 | 16.5174 | 17.0186 | 17.1253 | 17.1275 | 16.6418 | 15.6484 | 14.3066 | 14.3746 | 16.7022 | 18.2185 | 36.5058 | 24.1806 | 82.6654 |  |  |  | 17.1659 | 60.4606 | 196.5987 | 672.5042 | 705.3477 | 685.2092 | 104.5196 | 104.5741 | 945.5522 | 94.9264 | 102.3358 | 878.6178 | 493.1451 | 882.6794 | 703.7242 | 230.4522 | 934.3418 | 945.1408 | 450.4713 | 276.0857 | 341.8314 | 605.3586 | 430.674 | 608.0563 | 765.823 | 904.1174 | 973.4782 | 43.0479 | 325.2506 | 67.7556 | 542.3051 | 13.7884 | 51.1056 | 49.1081 | 49.0579 | 47.1297 |  |  | 0.007447 | -0.56241 | -0.98842 | -0.70311 | 5.9937 | 5.6317 | 7.3169 | -2.1752 | 18.0124 | 46.3669 | 26.4582 | 0.00052734 | 0.00063576 | -0.00085918 | 17.4395 | 16.4419 | 16.982 | 17.3302 | 17.2841 | 16.2443 | 14.6186 | 16.6985 | 17.0566 | 17.3721 | 17.4107 | 17.1224 | 16.2802 | 14.4815 | 805.6378 | 587.8253 | 571.4465 | 391.3947 | 328.0226 | 770.3022 | 490.4812 | 15.5203 | 17.6461 | 20.2169 | 32.4728 | 67.8156 | 77.1467 |  |  |  | 588.6893 | 569.6639 | 569.0044 | 591.2972 | 92.5816 | 42.4186 | 790.1472 |  |  | 396.5528 |  |  | 17.5368 | 32.4908 | 307.806 | 16.5519 | 27.4892 | 861.3507 | 747.3108 | 594.0211 | 788.0261 | 781.744 | 743.4441 |  | 795.7357 | 815.3433 | 931.1253 | 578.9997 | 660.1937 | 809.0375 |  | 954.2305 |  |  | 423.0345 | 642.9305 | 731.2073 | [6 empty] | 585.2698 |  |  | 380.7194 |  |  | 469.5286 | 638.6493 | 654.855 | 739.7304 | 988.2073 | 1027.5205 | 524.3194 | 701.5984 | 803.504 | 595.3614 | 664.6204 | 907.2426 | 1048.7332 | 626.6644 | 779.2019 | 846.6199 | 1051.4848 | 1061.449 | 504.5192 | 608.0844 | 685.586 | 563.677 | 716.3149 | 875.637 | 954.5254 | 1074.5164 | 569.3561 | 656.7489 | 643.3921 | 818.9503 | 90.5651 | -0.00073558 | 18.2776 | 3.5683 | -39.3299 | 3.1236 | 11372.26 | 0.24 | 0.18618 | -1.549 | -2.0536 | -1.732 | 5.854 | 5.6744 | 6.468 | 75.4656 | 122.4738 | 45.2832 | 63.2899 | 10.2843 | 20.7363 | 31.2091
42810.4506 | 917 | 17.9292 | 18.2409 | 18.3189 | 18.3367 | 17.6313 | 16.2374 | 14.5512 | 16.5146 | 17.0218 | 17.13 | 17.1254 | 16.6341 | 15.6556 | 14.3076 | 14.3787 | 16.7536 | 18.2766 | 37.061 | 24.1312 | 82.8056 |  |  |  | 17.183 | 60.9416 | 195.8603 | 672.3511 | 703.8488 | 684.5706 | 100.6607 | 109.3166 | 952.3508 | 96.0347 | 100.9767 | 869.3393 | 661.3325 | 874.9379 | 1208.0094 | 241.0956 | 932.0921 | 943.4204 | 464.9053 | 241.6768 | 342.9225 | 606.37 | 430.7384 | 606.6333 | 769.6979 | 903.0097 | 971.2457 | 43.1752 | 326.2266 | 66.0022 | 543.4659 | 13.7781 | 51.1481 | 49.1222 | 49.1016 | 47.4655 |  |  | 0.16121 | 0.057259 | -1.1264 | -1.24 | 6.3019 | 4.7314 | 6.3338 | -2.2764 | 18.8342 | 47.389 | 27.4485 | 0.00048298 | 0.00054048 | -0.00087396 | 17.4514 | 16.4396 | 16.9773 | 17.3267 | 17.2853 | 16.2514 | 14.6211 | 16.6971 | 17.0528 | 17.3617 | 17.411 | 17.1199 | 16.2816 | 14.482 | 802.8649 | 596.2216 | 571.8704 | 392.0098 | 326.7048 | 770.5509 | 491.3314 | 15.5186 | 17.6852 | 20.2951 | 32.6686 | 67.9971 | 77.257 |  |  |  | 589.1621 | 570.6697 | 569.8925 | 589.727 | 111.5285 | 55.7085 | 791.9431 |  |  | 396.2674 |  |  | 17.5495 | 32.6074 | 307.7839 | 16.6734 | 27.6441 | 866.094 | 751.1434 | 594.7737 | 788.6615 | 782.4298 | 747.6078 |  | 796.7373 | 812.7181 | 931.9239 | 579.5035 | 660.5641 | 809.0908 |  | 954.6362 |  |  | 423.6356 | 645.3173 | 733.8205 | [6 empty] | 585.9257 |  |  | 382.2588 |  |  | 470.3445 | 639.3722 | 654.1709 | 741.9872 | 988.7921 | 1027.6101 | 525.3214 | 703.0652 | 802.5845 | 596.188 | 664.7806 | 909.4711 | 1053.2312 | 626.9812 | 780.7229 | 847.4434 | 1051.349 | 1062.8774 | 505.0945 | 608.4866 | 687.4529 | 564.2865 | 716.3131 | 873.1085 | 955.3533 | 1076.9273 | 569.8008 | 656.2124 | 643.8617 | 820.109 | 87.7374 | -0.00022343 | 18.2771 | 3.5826 | -39.2095 | 3.1237 | 11409.87 | 0.32 | 0.86593 | 0.49455 | -2.1935 | -2.3014 | 5.9998 | 5.1987 | 6.015 | 75.6555 | 122.8855 | 45.3479 | 63.6897 | 10.4177 | 48.6945 | 31.3346
42810.4507 | 918 | 17.9114 | 18.2533 | 18.3141 | 18.3296 | 17.6251 | 16.2358 | 14.5386 | 16.5058 | 17.0187 | 17.1162 | 17.1258 | 16.631 | 15.6494 | 14.3037 | 14.3881 | 16.8154 | 18.3391 | 37.6536 | 24.0135 | 82.9767 |  |  |  | 17.1931 | 61.4109 | 196.3186 | 672.9841 | 703.5972 | 685.3808 | 99.6067 | 111.809 | 963.2459 | 104.0709 | 112.8112 | 878.1998 | 591.367 | 876.2277 | 907.2161 | 237.6104 | 930.8175 | 937.0357 | 468.6075 | 478.916 | 343.7685 | 607.4215 | 431.3056 | 605.4252 | 765.2545 | 900.1493 | 968.0113 | 44.1478 | 327.5004 | 66.9191 | 544.8253 | 13.77 | 51.1645 | 49.132 | 49.1374 | 47.8391 |  |  | 0.25715 | 0.35428 | -0.25508 | -0.92456 | 6.9991 | 5.5752 | 6.2425 | -0.81433 | 18.0451 | 46.3675 | 27.3261 | 0.00052405 | 0.00047641 | -0.00086575 | 17.4718 | 16.4392 | 16.9879 | 17.3314 | 17.2935 | 16.2565 | 14.6327 | 16.6999 | 17.0528 | 17.3617 | 17.4143 | 17.1238 | 16.284 | 14.4867 | 836.8747 | 612.9654 | 616.2665 | 402.7357 | 344.6841 | 772.4099 | 493.2405 | 15.5251 | 17.737 | 20.3618 | 32.8647 | 68.1772 | 77.3701 |  |  |  | 589.748 | 571.7311 | 570.9271 | 590.4498 | 100.4611 | 44.6973 | 791.4521 |  |  | 398.7926 |  |  | 17.5405 | 32.757 | 305.5001 | 16.6627 | 27.8006 | 865.5817 | 752.2263 | 596.4814 | 788.3547 | 782.3324 | 749.2917 |  | 797.5717 | 808.9046 | 932.1129 | 580.8198 | 661.1176 | 808.1393 |  | 955.0962 |  |  | 423.58 | 646.3283 | 735.1824 | [6 empty] | 587.5484 |  |  | 384.0614 |  |  | 471.7262 | 640.4312 | 654.3405 | 745.7693 | 991.5089 | 1029.1091 | 525.9691 | 703.5416 | 802.014 | 597.2699 | 666.1232 | 910.218 | 1058.6199 | 627.151 | 780.1836 | 849.1204 | 1052.5954 | 1065.1839 | 505.3166 | 608.8579 | 688.7726 | 565.0612 | 717.0532 | 871.7457 | 960.8153 | 1079.153 | 570.3673 | 656.9182 | 644.4138 | 820.6499 | 94.5876 | -0.0008338 | 18.2763 | 3.6049 | -39.3002 | 3.1236 | 11373.53 | 0.26 | 1.0941 | 1.2309 | -1.0444 | -1.9885 | 6.3153 | 5.6364 | 5.9642 | 75.864 | 123.0717 | 45.4289 | 60.5981 | 5.8911 | 35.0821 | 31.4161
42810.4507 | 919 | 17.9086 | 18.2451 | 18.3104 | 18.3231 | 17.6292 | 16.2346 | 14.5502 | 16.508 | 17.0161 | 17.1259 | 17.1281 | 16.6435 | 15.6552 | 14.3085 | 14.3805 | 16.8645 | 18.3979 | 38.28 | 24.0821 | 83.179 |  |  |  | 17.1986 | 61.8685 | 196.8718 | 673.8708 | 703.011 | 686.4057 | 93.2479 | 109.0197 | 954.3515 | 101.0915 | 113.9713 | 877.3552 | 551.052 | 876.7914 | 885.3833 | 239.389 | 926.4763 | 933.6359 | 474.0124 | 883.2168 | 344.357 | 606.8269 | 432.9334 | 607.5349 | 763.3803 | 904.4877 | 970.3046 | 43.5936 | 328.4742 | 69.0511 | 545.94 | 13.7458 | 51.1524 | 49.1417 | 49.1825 | 48.1375 |  |  | -0.058921 | -0.22859 | -0.69075 | -1.5409 | 7.026 | 5.6803 | 5.5775 | -2.2232 | 19.6747 | 48.6558 | 27.1854 | 0.00048627 | 0.00048298 | -0.00085753 | 17.4945 | 16.4312 | 16.98 | 17.3348 | 17.2898 | 16.2504 | 14.6295 | 16.6981 | 17.0515 | 17.3612 | 17.4094 | 17.1298 | 16.2887 | 14.4879 | 852.76 | 605.6732 | 592.5948 | 382.7587 | 339.9836 | 773.941 | 494.0697 | 15.5138 | 17.7665 | 20.4321 | 33.073 | 68.3561 | 77.484 |  |  |  | 590.3871 | 572.8307 | 571.4421 | 591.2595 | 110.7688 | 50.5793 | 790.7977 |  |  | 402.1583 |  |  | 17.5505 | 32.8877 | 305.8794 | 16.6714 | 27.9524 | 862.2877 | 753.9994 | 597.4488 | 789.2291 | 783.4767 | 751.9075 |  | 798.6532 | 807.357 | 933.1298 | 582.0982 | 661.6973 | 808.3696 |  | 956.2398 |  |  | 424.3888 | 649.2622 | 736.2893 | [6 empty] | 588.6742 |  |  | 385.3013 |  |  | 472.8629 | 642.5075 | 655.075 | 746.0837 | 990.5509 | 1031.3921 | 526.6026 | 703.8688 | 804.3346 | 598.5406 | 667.9214 | 909.7253 | 1058.0671 | 627.4966 | 783.4999 | 852.3697 | 1054.7963 | 1065.6522 | 505.7629 | 609.3363 | 689.8569 | 565.5493 | 717.8064 | 870.4715 | 958.9433 | 1081.8993 | 571.1001 | 657.0717 | 644.9242 | 824.1605 | 90.8147 | 0.00097618 | 18.2769 | 3.6265 | -39.3111 | 3.1236 | 11345.83 | 0.39 | -0.52401 | -0.98839 | -1.7182 | -2.5662 | 6.3391 | 5.6998 | 5.648 | 76.1229 | 123.5473 | 45.5169 | 59.401 | 8.6982 | 28.3048 | 31.5045
42810.4507 | 920 | 17.9142 | 18.2379 | 18.3198 | 18.329 | 17.6323 | 16.24 | 14.5516 | 16.5137 | 17.0142 | 17.1291 | 17.1307 | 16.6435 | 15.6496 | 14.3203 | 14.3855 | 16.9167 | 18.455 | 38.9085 | 24.0959 | 83.3151 |  |  |  | 17.2061 | 62.3128 | 199.6072 | 671.1946 | 704.3771 | 683.5287 | 93.3411 | 102.3137 | 944.6368 | 93.4764 | 107.0595 | 870.7792 | 322.5363 | 879.2631 | 836.0429 | 232.7565 | 929.5786 | 928.8062 | 494.4079 | 1394.369 | 346.2804 | 605.6428 | 433.5627 | 609.2887 | 760.3713 | 905.1916 | 970.85 | 42.6933 | 329.4681 | 69.07 | 546.974 | 13.7341 | 51.1088 | 49.1509 | 49.2334 | 48.4539 |  |  | -0.17129 | -0.20822 | -0.88854 | -1.0442 | 7.1568 | 5.426 | 6.7215 | -1.9275 | 18.7497 | 46.7932 | 27.4519 | 0.00048791 | 0.00045013 | -0.00082304 | 17.5062 | 16.4262 | 16.9656 | 17.3196 | 17.2809 | 16.2336 | 14.6123 | 16.6856 | 17.0426 | 17.3557 | 17.4029 | 17.1189 | 16.2778 | 14.4842 | 868.3775 | 616.0331 | 614.1696 | 388.5618 | 345.2405 | 776.1905 | 495.5509 | 15.5103 | 17.8159 | 20.4978 | 33.2793 | 68.5308 | 77.5933 |  |  |  | 591.1414 | 573.3126 | 571.6487 | 594.6601 | 100.2802 | 50.1732 | 792.2679 |  |  | 418.045 |  |  | 17.5477 | 33.0034 | 304.9488 | 16.6941 | 28.1205 | 863.8278 | 758.2986 | 598.1055 | 792.7246 | 790.6672 | 754.8414 |  | 799.9323 | 814.7276 | 934.0731 | 583.0034 | 662.2114 | 807.8238 |  | 957.2835 |  |  | 425.7271 | 652.1051 | 739.9163 | [6 empty] | 589.4164 |  |  | 386.3247 |  |  | 473.0513 | 644.6211 | 655.64 | 746.9174 | 989.3559 | 1033.2314 | 526.7641 | 703.7873 | 806.1833 | 599.7219 | 668.8788 | 907.8937 | 1061.406 | 627.5266 | 783.1127 | 856.0745 | 1060.4468 | 1068.1076 | 506.4644 | 610.1175 | 690.3771 | 565.6842 | 720.0264 | 869.3706 | 960.9907 | 1082.7836 | 572.1012 | 656.7169 | 645.3891 | 824.4594 | 92.9788 | 0.00021853 | 18.2777 | 3.6599 | -39.2151 | 3.1237 | 11332.52 | 0.21 | -0.8921 | -0.94269 | -1.9474 | -2.111 | 6.3997 | 5.5724 | 6.2021 | 76.4348 | 123.7448 | 45.6013 | 58.5032 | 6.6178 | 2.3651 | 31.5413
42810.4507 | 921 | 17.9127 | 18.2392 | 18.3182 | 18.3253 | 17.63 | 16.2402 | 14.5526 | 16.5099 | 17.0116 | 17.129 | 17.1318 | 16.6397 | 15.6523 | 14.3192 | 14.381 | 16.9656 | 18.5066 | 39.5236 | 24.1035 | 83.4709 |  |  |  | 17.2208 | 62.7072 | 201.1974 | 669.1181 | 704.862 | 680.7053 | 88.0194 | 97.9813 | 942.8202 | 92.4366 | 103.0192 | 866.6647 | 468.5106 | 877.3474 | 771.6368 | 228.0872 | 933.7439 | 934.9525 | 462.3536 | 959.2041 | 348.7699 | 607.4854 | 435.3481 | 613.0893 | 760.547 | 898.0654 | 970.3905 | 41.6799 | 330.6771 | 66.6087 | 548.3303 | 13.7189 | 51.0945 | 49.1609 | 49.2739 | 48.7932 |  |  | -0.16275 | -0.007797 | -0.41542 | -1.2952 | 7.8678 | 6.6108 | 5.5696 | -1.6824 | 18.7445 | 46.0988 | 27.6679 | 0.00051255 | 0.00049777 | -0.00081975 | 17.5237 | 16.4338 | 16.9708 | 17.3252 | 17.2871 | 16.2417 | 14.6185 | 16.692 | 17.0534 | 17.3629 | 17.4109 | 17.12 | 16.2892 | 14.4862 | 863.0189 | 619.4941 | 596.959 | 386.1721 | 344.1663 | 777.7675 | 496.8461 | 15.5183 | 17.862 | 20.5727 | 33.4808 | 68.7067 | 77.7066 |  |  |  | 591.8351 | 573.5685 | 571.8185 | 596.366 | 101.6445 | 53.5377 | 798.786 |  |  | 431.1306 |  |  | 17.5515 | 33.1539 | 313.2913 | 16.6822 | 28.2876 | 858.8457 | 759.4387 | 599.1558 | 804.4361 | 804.9451 | 756.0452 |  | 801.1578 | 828.9773 | 935.7637 | 583.7299 | 662.8868 | 809.4205 |  | 958.2944 |  |  | 426.2048 | 652.8455 | 740.9935 | [6 empty] | 590.3207 |  |  | 387.5409 |  |  | 472.9417 | 646.005 | 656.037 | 744.7274 | 986.6864 | 1035.5111 | 527.0105 | 704.0458 | 810.382 | 600.9811 | 668.8852 | 904.2641 | 1060.6602 | 627.6758 | 785.2207 | 870.7323 | 1061.2496 | 1070.6626 | 507.6494 | 610.8535 | 689.0221 | 566.1321 | 721.7035 | 867.7126 | 962.8554 | 1082.4974 | 572.4528 | 656.9123 | 645.3758 | 823.3274 | 87.346 | -0.00086184 | 18.2773 | 3.6911 | -39.181 | 3.1236 | 11327.69 | 0.25 | -0.86828 | -0.18261 | -1.3329 | -2.3536 | 6.6898 | 6.1321 | 5.6286 | 76.7794 | 124.0719 | 45.7254 | 59.688 | 8.8077 | 17.3265 | 31.6149
42810.4507 | 922 | 17.9034 | 18.2393 | 18.3131 | 18.3273 | 17.6352 | 16.2434 | 14.5546 | 16.5174 | 17.0197 | 17.1339 | 17.1377 | 16.6432 | 15.6558 | 14.3174 | 14.3846 | 17.0275 | 18.5674 | 40.2514 | 24.1767 | 83.6659 |  |  |  | 17.2142 | 63.1198 | 200.4148 | 667.3736 | 703.9692 | 679.347 | 90.5478 | 97.5466 | 941.0079 | 89.8674 | 98.4436 | 860.6387 | 597.6354 | 867.9864 | 734.3749 | 235.613 | 933.0455 | 940.7284 | 446.5331 | 871.7357 | 349.1375 | 608.9186 | 437.1286 | 616.1773 | 764.8375 | 897.2262 | 970.5108 | 40.1179 | 331.7104 | 65.748 | 549.3959 | 13.6991 | 51.1144 | 49.1685 | 49.3164 | 49.1195 |  |  | -0.49262 | -0.44806 | -0.97331 | -1.5751 | 7.329 | 5.5443 | 5.059 | -2.7686 | 18.7451 | 47.9045 | 27.6319 | 0.00051912 | 0.00049284 | -0.00085589 | 17.539 | 16.4212 | 16.9691 | 17.3088 | 17.2788 | 16.2326 | 14.6079 | 16.6861 | 17.0421 | 17.3564 | 17.3997 | 17.1092 | 16.2743 | 14.4762 | 879.9065 | 628.7424 | 637.1638 | 401.7548 | 349.6 | 779.9015 | 498.6981 | 15.5274 | 17.9153 | 20.6636 | 33.692 | 68.8855 | 77.8244 |  |  |  | 592.469 | 573.9225 | 572.2478 | 596.2696 | 115.0742 | 61.2093 | 808.5819 |  |  | 437.9275 |  |  | 17.5511 | 33.2565 | 311.9501 | 16.6947 | 28.4351 | 861.117 | 761.0839 | 599.5575 | 818.9361 | 819.7897 | 756.7257 |  | 802.4401 | 839.3188 | 936.403 | 583.5357 | 663.5702 | 813.0417 |  | 959.0472 |  |  | 426.4136 | 650.4143 | 742.7741 | [6 empty] | 590.45 |  |  | 388.3461 |  |  | 473.2785 | 647.2229 | 655.222 | 742.7237 | 985.3801 | 1038.0924 | 527.2054 | 704.7453 | 817.9202 | 602.3584 | 669.2339 | 905.2126 | 1060.2875 | 628.0285 | 785.9282 | 879.6544 | 1060.9917 | 1070.3518 | 508.1699 | 611.2955 | 687.4505 | 565.6325 | 722.5019 | 866.1511 | 967.8055 | 1079.7021 | 572.9709 | 658.376 | 645.0737 | 819.9937 | 89.263 | -0.00096006 | 18.2768 | 3.7127 | -39.3153 | 3.1236 | 11284.68 | 0.37 | -1.5096 | -1.3854 | -2.0419 | -2.5976 | 6.4543 | 5.6137 | 5.3625 | 77.1573 | 124.0588 | 45.877 | 58.6122 | 4.7388 | 36.798 | 31.7284
42810.4507 | 923 | 17.8961 | 18.2379 | 18.3186 | 18.3216 | 17.6384 | 16.2479 | 14.558 | 16.5207 | 17.0247 | 17.1314 | 17.1333 | 16.6435 | 15.6645 | 14.3198 | 14.384 | 17.0854 | 18.6322 | 40.9448 | 24.3192 | 83.8038 |  |  |  | 17.2228 | 63.4798 | 201.0067 | 665.7543 | 703.1775 | 677.3657 | 96.8159 | 97.1262 | 944.0682 | 85.1806 | 96.9291 | 857.132 | 662.139 | 863.1309 | 619.2949 | 237.848 | 933.4621 | 938.4431 | 464.2814 | 1069.6722 | 349.5906 | 610.0877 | 437.6112 | 616.4145 | 772.346 | 898.9282 | 970.3402 | 39.4135 | 332.9843 | 64.573 | 550.4976 | 13.6736 | 51.1796 | 49.1669 | 49.3679 | 49.4164 |  |  | 0.18224 | 0.35099 | -0.24917 | -0.94165 | 7.0556 | 4.2018 | 6.1426 | -1.4728 | 18.3829 | 44.6025 | 28.1338 | 0.00055362 | 0.00051912 | -0.00085425 | 17.5631 | 16.4248 | 16.9645 | 17.3217 | 17.2888 | 16.2391 | 14.6161 | 16.7034 | 17.0536 | 17.3583 | 17.4034 | 17.1221 | 16.2774 | 14.4934 | 878.8561 | 632.948 | 635.3235 | 411.5688 | 343.9143 | 781.4127 | 500.5569 | 15.5347 | 17.9667 | 20.7438 | 33.9029 | 69.0534 | 77.9303 |  |  |  | 592.9995 | 573.2882 | 571.7637 | 594.6742 | 82.4295 | 29.8026 | 817.1824 |  |  | 430.2504 |  |  | 17.5592 | 33.3863 | 312.2394 | 16.673 | 28.6258 | 865.1161 | 761.4115 | 599.5653 | 819.0187 | 817.9891 | 755.7389 |  | 803.1269 | 846.8194 | 936.0352 | 582.4476 | 664.1657 | 817.6071 |  | 959.9934 |  |  | 426.8794 | 647.6822 | 742.4386 | [6 empty] | 589.9108 |  |  | 387.4766 |  |  | 473.8805 | 648.5724 | 656.1283 | 742.5979 | 985.1245 | 1037.6627 | 527.4767 | 705.4963 | 820.4516 | 603.4346 | 671.6717 | 904.8909 | 1058.9492 | 628.7412 | 784.9346 | 876.1588 | 1064.1418 | 1069.6663 | 508.7797 | 612.1711 | 685.929 | 566.041 | 722.5462 | 867.6847 | 967.7949 | 1083.0224 | 573.5199 | 658.8339 | 645.6019 | 822.2706 | 85.6444 | -0.0010933 | 18.2767 | 3.7335 | -39.4448 | 3.1236 | 11242.84 | 0.35 | 0.91721 | 1.227 | -1.0338 | -2.0098 | 6.3374 | 4.8906 | 5.9132 | 77.3978 | 123.6927 | 46.0349 | 59.2979 | 5.3443 | 48.8837 | 31.8655
42810.4507 | 924 | 17.8978 | 18.2369 | 18.3111 | 18.3222 | 17.63 | 16.2426 | 14.5621 | 16.5172 | 17.0185 | 17.1296 | 17.1295 | 16.6408 | 15.6579 | 14.3252 | 14.3855 | 17.1459 | 18.693 | 41.6544 | 24.2014 | 83.9539 |  |  |  | 17.2404 | 63.8353 | 206.8646 | 666.5758 | 703.6784 | 678.3212 | 93.3 | 105.299 | 950.5305 | 87.093 | 94.9018 | 846.0128 | 792.0146 | 852.0311 | 1023.9873 | 247.6017 | 934.2145 | 940.3684 | 466.0784 | 1336.7412 | 350.6953 | 610.8254 | 438.5128 | 616.3648 | 768.8837 | 892.1842 | 962.6187 | 39.536 | 334.1255 | 63.0383 | 551.7663 | 13.6426 | 51.271 | 49.1572 | 49.4219 | 49.7428 |  |  | 0.60345 | -0.20559 | -0.31948 | -1.3261 | 7.3106 | 4.7255 | 5.8528 | -1.984 | 19.5425 | 46.4112 | 27.5866 | 0.0004567 | 0.0004797 | -0.00086246 | 17.591 | 16.4298 | 16.9739 | 17.3277 | 17.2913 | 16.2505 | 14.6241 | 16.7041 | 17.0586 | 17.3682 | 17.4174 | 17.1323 | 16.2934 | 14.4973 | 850.1676 | 588.3662 | 535.8742 | 378.7064 | 321.0312 | 780.7018 | 499.8727 | 15.5332 | 18.014 | 20.8328 | 34.1241 | 69.2433 | 78.0514 |  |  |  | 593.3138 | 570.4053 | 569.9914 | 589.6814 | 91.8727 | 35.7292 | 818.1529 |  |  | 428.8145 |  |  | 17.5646 | 33.5179 | 320.5809 | 16.6697 | 28.7699 | 865.3451 | 761.7721 | 598.3314 | 815.2539 | 812.0421 | 755.4478 |  | 803.7296 | 849.4394 | 935.5326 | 580.4467 | 664.3603 | 820.2382 |  | 960.7128 |  |  | 426.7039 | 648.3562 | 743.3562 | [6 empty] | 588.2844 |  |  | 385.4866 |  |  | 474.5008 | 649.6459 | 657.4732 | 742.7127 | 983.7972 | 1038.5461 | 528.0613 | 705.2116 | 820.7579 | 603.4759 | 672.7526 | 901.2746 | 1058.7648 | 629.1631 | 783.6995 | 877.8455 | 1064.1142 | 1069.0703 | 509.5288 | 612.7977 | 685.1212 | 566.5742 | 723.3561 | 868.7402 | 965.3574 | 1081.0637 | 573.8675 | 658.9503 | 646.0116 | 823.3846 | 86.81 | -0.00072152 | 18.2779 | 3.744 | -39.4475 | 3.1236 | 11178.71 | 0.3 | 1.6699 | -0.93948 | -1.1711 | -2.386 | 6.4323 | 5.1715 | 5.7554 | 77.5932 | 123.4045 | 46.1323 | 62.2176 | 16.2464 | 82.0415 | 32.0593
42810.4507 | 925 | 17.8883 | 18.2302 | 18.2964 | 18.3221 | 17.6221 | 16.2428 | 14.5541 | 16.5125 | 17.009 | 17.123 | 17.1171 | 16.6439 | 15.6483 | 14.3194 | 14.3795 | 17.1993 | 18.756 | 42.4147 | 24.2622 | 84.0932 |  |  |  | 17.2475 | 64.1976 | 204.7878 | 666.9053 | 704.2905 | 679.8062 | 90.1235 | 107.1599 | 960.1692 | 97.3148 | 102.6652 | 851.0594 | 663.5562 | 854.1 | 1261.788 | 251.5768 | 935.7376 | 942.3264 | 481.8881 | 1100.7126 | 351.6964 | 611.5 | 439.355 | 616.4199 | 761.0075 | 884.9599 | 956.0995 | 41.5863 | 335.2258 | 63.3822 | 553.4332 | 13.633 | 51.3495 | 49.15 | 49.4581 | 50.0401 |  |  | 0.22035 | 0.007975 | -0.13549 | -0.87593 | 8.2371 | 6.4807 | 7.0869 | -1.8138 | 19.654 | 48.9294 | 27.2436 | 0.00048134 | 0.00051419 | -0.00086082 | 17.5995 | 16.4148 | 16.9674 | 17.3195 | 17.2876 | 16.2444 | 14.6199 | 16.6936 | 17.0534 | 17.3624 | 17.4099 | 17.1275 | 16.2871 | 14.4893 | 843.7152 | 589.5264 | 554.2374 | 357.8857 | 313.8396 | 780.8536 | 499.6606 | 15.5339 | 18.0594 | 20.9084 | 34.333 | 69.4168 | 78.1554 |  |  |  | 593.355 | 566.9927 | 567.9134 | 584.986 | 101.2393 | 51.0431 | 815.4693 |  |  | 424.72 |  |  | 17.5783 | 33.6552 | 317.2887 | 16.7282 | 28.9331 | 868.2168 | 760.5014 | 596.6699 | 811.439 | 807.1741 | 755.0637 |  | 804.1052 | 847.2747 | 934.8666 | 577.9341 | 664.2865 | 819.6519 |  | 961.4055 |  |  | 427.8251 | 652.3459 | 744.0376 | [6 empty] | 586.2934 |  |  | 383.836 |  |  | 474.8292 | 649.9141 | 657.3946 | 741.1503 | 982.5727 | 1038.7501 | 528.871 | 704.7743 | 822.1072 | 602.535 | 672.3383 | 901.6587 | 1060.5685 | 629.345 | 782.5706 | 878.3164 | 1063.9409 | 1068.7542 | 510.1805 | 613.4676 | 685.3041 | 566.1458 | 723.6125 | 869.3387 | 964.6216 | 1083.5984 | 574.7256 | 661.0557 | 645.9693 | 822.9329 | 83.4462 | 8.0602e-06 | 18.2772 | 3.7494 | -39.3824 | 3.1236 | 11145.33 | 0.19 | 1.0099 | 0.1851 | -0.76296 | -1.9399 | 6.8066 | 6.0374 | 6.3135 | 77.7208 | 123.1797 | 46.1862 | 62.9918 | 14.1603 | 48.6976 | 32.1969
42810.4508 | 926 | 17.8927 | 18.2241 | 18.3059 | 18.3242 | 17.6303 | 16.2354 | 14.5643 | 16.5122 | 17.0184 | 17.1331 | 17.1289 | 16.6438 | 15.6541 | 14.321 | 14.3905 | 17.2585 | 18.8147 | 43.1894 | 24.1994 | 84.2168 |  |  |  | 17.2627 | 64.5412 | 207.6899 | 667.8717 | 706.3075 | 680.8378 | 89.8326 | 96.7756 | 953.3993 | 90.7684 | 102.8281 | 860.4888 | 382.4785 | 865.9486 | 1317.9301 | 242.1614 | 932.7556 | 934.1963 | 470.3681 | 1053.998 | 352.8787 | 611.3602 | 440.7798 | 617.3799 | 756.7066 | 888.33 | 961.1899 | 42.0561 | 336.5912 | 67.8635 | 555.3751 | 13.6207 | 51.3828 | 49.1498 | 49.5003 | 50.2729 |  |  | 0.8571 | -0.14777 | -0.7972 | -0.73203 | 7.4006 | 5.6133 | 6.2169 | -2.2856 | 20.5792 | 50.5377 | 27.5461 | 0.00044191 | 0.00057005 | -0.00084439 | 17.6344 | 16.4235 | 16.9693 | 17.3224 | 17.2905 | 16.2474 | 14.6278 | 16.6964 | 17.0666 | 17.3737 | 17.4151 | 17.1327 | 16.2964 | 14.5 | 851.4389 | 584.8634 | 549.8919 | 353.8315 | 297.0314 | 781.1667 | 499.7082 | 15.536 | 18.1047 | 20.9774 | 34.5347 | 69.5729 | 78.2585 |  |  |  | 593.4976 | 565.2078 | 565.9336 | 584.8813 | 93.7279 | 31.3223 | 812.7816 |  |  | 421.2773 |  |  | 17.5757 | 33.7926 | 321.3479 | 16.704 | 29.0962 | 865.0477 | 757.7277 | 594.8777 | 809.1258 | 806.387 | 753.4244 |  | 804.2013 | 842.1155 | 933.8026 | 574.5945 | 664.0026 | 817.5198 |  | 961.9484 |  |  | 428.7439 | 655.562 | 742.6024 | [6 empty] | 584.0151 |  |  | 381.3794 |  |  | 475.0335 | 649.4386 | 656.6352 | 740.5719 | 983.7655 | 1039.047 | 529.5444 | 703.6779 | 820.914 | 601.8215 | 671.1176 | 900.9334 | 1062.3595 | 629.4893 | 780.0324 | 881.6697 | 1063.2972 | 1066.7053 | 510.9615 | 614.4699 | 684.9468 | 565.404 | 722.8883 | 868.9151 | 967.4441 | 1083.5457 | 575.3227 | 663.0552 | 645.5628 | 821.6553 | 83.3446 | -0.00051109 | 18.2776 | 3.751 | -39.4171 | 3.1236 | 11085.71 | 0.29 | 1.9928 | -0.79672 | -1.8506 | -1.7733 | 6.4611 | 5.6271 | 5.9219 | 77.7962 | 122.8686 | 46.2181 | 62.2515 | 14.6534 | 8.0351 | 32.2248
42810.4508 | 927 | 17.8917 | 18.2281 | 18.3045 | 18.3286 | 17.6308 | 16.2465 | 14.5661 | 16.5157 | 17.0183 | 17.1373 | 17.1347 | 16.6509 | 15.661 | 14.3259 | 14.39 | 17.3251 | 18.8806 | 43.9945 | 24.0875 | 84.3631 |  |  |  | 17.2681 | 64.8643 | 215.3195 | 669.9213 | 707.4316 | 683.9328 | 85.923 | 96.4695 | 943.1875 | 89.4695 | 99.6454 | 858.2172 | 486.9538 | 865.8308 | 1172.4708 | 237.25 | 931.1268 | 932.9098 | 472.6325 | 1305.2401 | 355.036 | 614.7017 | 443.1194 | 618.3969 | 757.9648 | 891.3157 | 966.0679 | 41.1975 | 337.8242 | 70.6178 | 556.9907 | 13.6042 | 51.4433 | 49.1621 | 49.5445 | 50.2286 |  |  | 0.11784 | -0.54269 | -1.1284 | -0.75897 | 7.3461 | 4.3063 | 6.023 | -2.7896 | 18.7355 | 47.1264 | 27.7915 | 0.0004567 | 0.00056348 | -0.00085261 | 17.6494 | 16.4212 | 16.9627 | 17.316 | 17.2858 | 16.2386 | 14.6268 | 16.6922 | 17.0527 | 17.3665 | 17.4081 | 17.1248 | 16.286 | 14.4929 | 832.107 | 553.392 | 509.4959 | 337.116 | 277.3598 | 781.1273 | 499.1543 | 15.5344 | 18.1527 | 21.0531 | 34.7266 | 69.7229 | 78.3602 |  |  |  | 593.9682 | 565.6283 | 566.1221 | 589.3097 | 93.5796 | 40.719 | 812.1119 |  |  | 422.6665 |  |  | 17.5885 | 33.9148 | 329.8244 | 16.7183 | 29.2498 | 859.555 | 754.2954 | 593.1043 | 810.9539 | 808.2446 | 750.2475 |  | 803.7453 | 844.6786 | 933.4152 | 572.6861 | 663.6479 | 816.5119 |  | 962.8662 |  |  | 429.7476 | 656.1462 | 739.7735 | [6 empty] | 581.917 |  |  | 380.0822 |  |  | 475.6205 | 648.3479 | 656.6851 | 741.802 | 984.4929 | 1038.7823 | 530.4306 | 703.0585 | 819.7446 | 601.3303 | 670.0817 | 901.0251 | 1059.2146 | 629.7941 | 779.2813 | 891.3518 | 1062.6602 | 1064.2958 | 511.6251 | 615.2796 | 685.6703 | 564.9973 | 722.8656 | 869.2094 | 968.1675 | 1081.1265 | 575.7248 | 664.0607 | 645.5823 | 820.7636 | 88.727 | 0.00061137 | 18.2763 | 3.7472 | -39.3919 | 3.1236 | 11058.12 | 0.26 | 0.74011 | -1.5297 | -2.2058 | -1.809 | 6.4455 | 4.9349 | 5.8363 | 77.7426 | 122.6322 | 46.1951 | 64.3847 | 19.0224 | 19.3245 | 32.1844
42810.4508 | 928 | 17.8898 | 18.2296 | 18.3071 | 18.3161 | 17.6262 | 16.2352 | 14.5682 | 16.5116 | 17.0183 | 17.132 | 17.1365 | 16.6499 | 15.6569 | 14.322 | 14.3851 | 17.3912 | 18.9439 | 44.8235 | 24.1231 | 84.5147 |  |  |  | 17.2714 | 65.196 | 220.3346 | 670.5713 | 709.2918 | 683.5321 | 88.1718 | 97.6751 | 944.0116 | 89.2761 | 98.2827 | 850.4336 | 724.0675 | 865.0752 | 786.4651 | 230.8289 | 943.1042 | 945.109 | 456.0821 | 1279.1935 | 355.96 | 616.9646 | 445.7419 | 616.8578 | 754.924 | 881.9455 | 963.2691 | 40.5503 | 339.0944 | 69.4922 | 558.4653 | 13.5954 | 51.4706 | 49.1857 | 49.5793 | 49.7169 |  |  | -0.039865 | 0.002715 | -1.545 | -1.7216 | 6.6843 | 5.2078 | 5.2378 | -2.2764 | 19.9901 | 49.8768 | 26.9877 | 0.00051419 | 0.00041891 | -0.00084439 | 17.6718 | 16.4205 | 16.9672 | 17.3141 | 17.2756 | 16.2373 | 14.6238 | 16.6939 | 17.0472 | 17.3622 | 17.404 | 17.1242 | 16.2859 | 14.4905 | 831.3223 | 565.3223 | 547.4728 | 338.1228 | 277.5741 | 781.2891 | 499.0166 | 15.5267 | 18.2074 | 21.1387 | 34.9383 | 69.8805 | 78.4674 |  |  |  | 594.7994 | 567.5017 | 568.1802 | 593.4153 | 104.8233 | 58.8473 | 812.9421 |  |  | 421.1581 |  |  | 17.576 | 34.04 | 335.8735 | 16.7178 | 29.4228 | 862.7363 | 754.3052 | 590.9604 | 807.4994 | 804.3115 | 749.5026 |  | 803.7901 | 841.9013 | 932.9947 | 570.5222 | 663.0521 | 815.4707 |  | 963.319 |  |  | 431.8706 | 656.3572 | 739.1384 | [6 empty] | 579.9881 |  |  | 379.8951 |  |  | 476.4821 | 647.5464 | 658.3564 | 741.9736 | 983.4102 | 1039.7214 | 531.3212 | 702.4977 | 822.0217 | 601.1026 | 670.7004 | 901.6626 | 1056.6479 | 630.1885 | 779.0722 | 896.2608 | 1059.7123 | 1063.7188 | 512.2838 | 616.0224 | 686.9031 | 564.3743 | 722.9504 | 869.8407 | 969.5341 | 1079.7251 | 575.8557 | 664.0469 | 646.1784 | 820.4072 | 88.8546 | -9.7173e-05 | 18.2768 | 3.7326 | -39.3598 | 3.1235 | 11099.08 | 0.27 | -0.43037 | 0.10834 | -2.5844 | -2.7281 | 6.1236 | 5.4051 | 5.4206 | 77.7772 | 122.5302 | 46.1276 | 64.5328 | 14.773 | 63.5156 | 32.2166
42810.4508 | 929 | 17.8869 | 18.2225 | 18.2983 | 18.308 | 17.6253 | 16.2351 | 14.5729 | 16.5107 | 17.0206 | 17.1294 | 17.1333 | 16.6486 | 15.6574 | 14.3267 | 14.3837 | 17.4525 | 19.0092 | 45.6601 | 24.164 | 84.6582 |  |  |  | 17.2764 | 65.5377 | 221.2729 | 670.622 | 711.5253 | 681.0945 | 89.8732 | 99.5104 | 941.654 | 88.1383 | 98.945 | 854.8496 | 689.3702 | 865.811 | 965.6452 | 239.3368 | 937.2215 | 940.882 | 448.5573 | 1263.7314 | 356.8268 | 618.1644 | 447.3599 | 619.0471 | 750.446 | 877.0613 | 961.4393 | 40.9545 | 340.3749 | 68.2878 | 559.6682 | 13.5941 | 51.507 | 49.1908 | 49.6155 | 49.1697 |  |  | 0.50226 | -0.22333 | -0.87474 | -1.8826 | 8.7411 | 5.909 | 6.1939 | -2.4321 | 20.3478 | 49.2951 | 27.135 | 0.00044355 | 0.00048134 | -0.00085261 | 17.6839 | 16.4166 | 16.9547 | 17.3041 | 17.2706 | 16.241 | 14.6202 | 16.6885 | 17.045 | 17.3564 | 17.4068 | 17.1165 | 16.279 | 14.491 | 847.7373 | 599.4386 | 615.3307 | 365.3705 | 305.4391 | 782.0283 | 500.2428 | 15.5425 | 18.2659 | 21.2289 | 35.1713 | 70.0635 | 78.5721 |  |  |  | 595.5978 | 568.6792 | 569.0662 | 593.724 | 103.0209 | 49.7912 | 809.9326 |  |  | 421.4611 |  |  | 17.575 | 34.1666 | 336.2814 | 16.705 | 29.5966 | 861.8253 | 756.4547 | 589.5379 | 807.1019 | 803.8055 | 751.8266 |  | 804.6167 | 847.5825 | 933.0237 | 569.0482 | 662.5595 | 818.7625 |  | 964.356 |  |  | 434.0504 | 657.0525 | 741.3191 | [6 empty] | 578.4568 |  |  | 379.2656 |  |  | 477.1809 | 646.9481 | 659.6813 | 739.6722 | 982.8349 | 1041.0595 | 531.8268 | 702.3584 | 822.8613 | 600.6244 | 671.3098 | 901.2287 | 1059.7966 | 630.7094 | 780.0871 | 894.3545 | 1059.1538 | 1064.4676 | 512.2885 | 616.7736 | 686.8806 | 563.5057 | 723.2304 | 871.2628 | 972.1818 | 1082.6934 | 576.1146 | 663.2971 | 646.635 | 821.3134 | 80.8173 | 0.00033778 | 18.2774 | 3.7284 | -39.6031 | 3.1236 | 11168.17 | 0.28 | 1.5257 | -0.98324 | -1.9459 | -2.8547 | 6.9878 | 5.7453 | 5.8822 | 77.97 | 122.3848 | 46.0633 | 62.9879 | 7.4979 | 55.3549 | 32.3487
42810.4508 | 930 | 17.8806 | 18.2142 | 18.2972 | 18.3129 | 17.6238 | 16.2317 | 14.5781 | 16.5146 | 17.0173 | 17.1294 | 17.1305 | 16.6529 | 15.6611 | 14.3222 | 14.388 | 17.5125 | 19.0786 | 46.483 | 24.1454 | 84.8071 |  |  |  | 17.2843 | 65.8657 | 225.2019 | 671.4056 | 714.0401 | 681.2063 | 93.5048 | 99.8082 | 949.372 | 88.6878 | 98.4168 | 859.1502 | 658.1423 | 870.4684 | 1146.9029 | 240.4603 | 943.9805 | 947.5669 | 460.3761 | 968.5402 | 357.7066 | 619.1412 | 447.8304 | 621.1215 | 752.3104 | 886.5529 | 966.8869 | 41.4884 | 341.5204 | 67.5682 | 560.7346 | 13.5823 | 51.5351 | 49.1856 | 49.6361 | 48.6156 |  |  | 0.071187 | -1.8983 | -0.3819 | -1.3438 | 8.5184 | 5.8216 | 6.4534 | -2.1752 | 20.1145 | 49.1333 | 27.7746 | 0.00039263 | 0.00050269 | -0.00083289 | 17.709 | 16.4215 | 16.9532 | 17.3141 | 17.2849 | 16.2477 | 14.6301 | 16.6981 | 17.0494 | 17.3703 | 17.4158 | 17.1205 | 16.2908 | 14.495 | 853.3648 | 611.0112 | 611.8395 | 368.1275 | 319.7763 | 783.1964 | 501.3754 | 15.5382 | 18.3158 | 21.3073 | 35.3777 | 70.2225 | 78.6661 |  |  |  | 596.0106 | 568.2343 | 568.5826 | 590.1881 | 100.9003 | 45.5121 | 810.6539 |  |  | 421.2793 |  |  | 17.5872 | 34.2959 | 343.1521 | 16.7117 | 29.7539 | 870.3533 | 756.081 | 588.5274 | 808.004 | 803.9064 | 751.9395 |  | 805.046 | 853.3706 | 934.3297 | 567.4741 | 662.2364 | 830.4181 |  | 966.0061 |  |  | 434.3773 | 655.2434 | 741.8731 | [6 empty] | 576.9642 |  |  | 378.2207 |  |  | 477.2623 | 645.9403 | 659.1567 | 738.801 | 984.9626 | 1042.9256 | 532.0089 | 702.6706 | 822.996 | 599.9539 | 670.6153 | 902.0186 | 1059.7245 | 630.9749 | 782.0099 | 891.2197 | 1063.8329 | 1067.2727 | 512.4589 | 617.5447 | 686.0447 | 563.0388 | 723.4208 | 873.6124 | 976.1585 | 1088.6898 | 576.9808 | 663.441 | 646.9263 | 823.4588 | 78.9847 | -0.0017668 | 18.2777 | 3.7094 | -39.493 | 3.1236 | 11189.18 | 0.38 | 0.57441 | -2.8682 | -1.2865 | -2.4132 | 6.9266 | 5.7261 | 6.0289 | 78.1008 | 122.7809 | 46.038 | 62.8041 | 8.1307 | 48.1443 | 32.5199
42810.4508 | 931 | 17.8817 | 18.2173 | 18.2913 | 18.3149 | 17.6289 | 16.2345 | 14.5731 | 16.5113 | 17.0151 | 17.1288 | 17.1282 | 16.6484 | 15.6548 | 14.3169 | 14.3895 | 17.581 | 19.1475 | 47.2983 | 24.1119 | 84.9632 |  |  |  | 17.2996 | 66.1831 | 225.7403 | 673.0701 | 714.5285 | 684.3816 | 96.6306 | 101.7112 | 969.585 | 89.6189 | 97.5229 | 862.0542 | 759.1925 | 870.5774 |  | 253.4714 | 955.4831 | 958.7943 | 470.2186 | 786.8272 | 359.8268 | 620.966 | 450.2737 | 623.4531 | 752.997 | 893.8403 | 973.865 | 41.6555 | 342.6842 | 67.5199 | 562.223 | 13.5733 | 51.562 | 49.1816 | 49.6547 | 48.0505 |  |  | -0.21466 | -0.78319 | -1.0324 | -1.4115 | 8.4224 | 6.0917 | 6.8549 | -2.1489 | 20.2528 | 49.8072 | 27.4131 | 0.00047477 | 0.00047805 | -0.00085096 | 17.7339 | 16.4189 | 16.9642 | 17.3115 | 17.2844 | 16.2495 | 14.6253 | 16.7016 | 17.05 | 17.3644 | 17.4125 | 17.1287 | 16.2974 | 14.5012 | 864.6765 | 603.7938 | 602.3691 | 350.1957 | 310.3578 | 784.7225 | 501.8946 | 15.5387 | 18.3633 | 21.3899 | 35.5832 | 70.3734 | 78.7636 |  |  |  | 596.2819 | 567.5216 | 568.2264 | 589.8075 | 117.8172 | 53.4942 | 812.3459 |  |  | 420.2017 |  |  | 17.6041 | 34.4278 | 342.4983 | 16.7013 | 29.9436 | 888.3905 | 752.3846 | 587.0843 | 805.5554 | 800.7265 | 747.204 |  | 804.8518 | 849.2324 | 935.5848 | 565.6971 | 661.7177 | 833.0977 |  | 967.3509 |  |  | 433.0715 | 651.0015 | 739.0208 | [6 empty] | 575.341 |  |  | 377.5384 |  |  | 477.438 | 645.2602 | 658.2037 | 742.1234 | 992.4106 | 1040.9262 | 532.2313 | 702.7667 | 821.6097 | 599.9618 | 670.9836 | 906.0106 | 1058.5541 | 631.2281 | 781.3423 | 887.9329 | 1067.7113 | 1070.1058 | 513.311 | 619.3361 | 686.6816 | 562.2064 | 723.173 | 874.7903 | 977.5986 | 1092.6228 | 577.5437 | 664.5731 | 647.1495 | 823.1928 | 83.535 | -0.00095305 | 18.2774 | 3.7061 | -39.4749 | 3.1235 | 11222.07 | 0.36 | -0.99912 | -1.8442 | -2.1174 | -2.4757 | 6.9091 | 5.8758 | 6.2331 | 78.1717 | 123.4326 | 45.9768 | 62.1257 | 9.2954 | 72.4259 | 32.5784
42810.4508 | 932 | 17.8839 | 18.2267 | 18.2962 | 18.3218 | 17.636 | 16.2436 | 14.5881 | 16.5168 | 17.0221 | 17.1305 | 17.1418 | 16.6502 | 15.6587 | 14.3295 | 14.3918 | 17.6493 | 19.2196 | 48.1256 | 24.1675 | 85.1094 |  |  |  | 17.3171 | 66.4911 | 224.5376 | 672.0809 | 713.3201 | 683.6601 | 91.9642 | 106.5262 | 983.7501 | 95.2631 | 107.0628 | 868.1863 | 634.2305 | 877.3174 |  | 257.3875 | 958.1791 | 959.6926 | 481.8717 | 966.3147 | 361.0187 | 622.9523 | 452.0283 | 627.0363 | 754.7065 | 899.6537 | 976.1686 | 41.6607 | 343.6684 | 69.0726 | 563.4136 | 13.5806 | 51.5887 | 49.1936 | 49.6608 | 47.3102 |  |  | 0.47334 | -0.83445 | -1.2716 | -1.2439 | 7.4689 | 4.4219 | 6.7557 | -2.8934 | 19.9119 | 48.7477 | 28.2602 | 0.00040906 | 0.0004797 | -0.00085753 | 17.7527 | 16.4124 | 16.9479 | 17.3133 | 17.2798 | 16.2419 | 14.6214 | 16.6947 | 17.0521 | 17.3644 | 17.413 | 17.1274 | 16.2948 | 14.4987 | 879.2574 | 619.9436 | 614.7919 | 364.6055 | 313.2408 | 787.5389 | 502.9347 | 15.5415 | 18.4163 | 21.4749 | 35.8003 | 70.5236 | 78.858 |  |  |  | 596.8483 | 567.8496 | 568.6224 | 593.6233 | 109.8923 | 54.6661 | 809.4407 |  |  | 417.9493 |  |  | 17.5929 | 34.5568 | 340.2529 | 16.6715 | 30.0926 | 894.1785 | 749.0056 | 585.6942 | 802.2922 | 796.8022 | 741.9149 |  | 804.2711 | 837.8743 | 936.4573 | 564.8415 | 661.1777 | 827.8194 |  | 967.8792 |  |  | 431.9234 | 647.1221 | 735.1373 | [6 empty] | 574.2238 |  |  | 377.9003 |  |  | 478.4763 | 645.4776 | 658.6997 | 747.7242 | 998.4409 | 1039.8853 | 532.5925 | 702.7468 | 818.4642 | 600.0894 | 672.6151 | 910.7844 | 1060.3718 | 631.6507 | 780.9378 | 887.5364 | 1065.8542 | 1070.3461 | 513.3034 | 621.1776 | 687.2854 | 562.1584 | 723.2156 | 874.3756 | 978.3721 | 1093.0596 | 577.6358 | 665.42 | 647.6757 | 822.6283 | 81.5274 | -0.0031979 | 18.2758 | 3.7104 | -39.5149 | 3.1235 | 11218.02 | 0.1 | 1.4831 | -1.9057 | -2.3525 | -2.3267 | 6.5224 | 5.0186 | 6.2032 | 78.1377 | 124.1222 | 45.8856 | 61.5778 | 8.1407 | 42.6684 | 32.5726
42810.4508 | 933 | 17.8726 | 18.2201 | 18.2953 | 18.3125 | 17.6186 | 16.2275 | 14.5751 | 16.513 | 17.0106 | 17.1262 | 17.1315 | 16.6446 | 15.6629 | 14.3208 | 14.3927 | 17.7177 | 19.2893 | 48.9454 | 24.1916 | 85.2471 |  |  |  | 17.3225 | 66.7916 | 225.1616 | 671.129 | 713.1882 | 682.3101 | 92.107 | 102.8012 | 983.0246 | 95.7757 | 106.1025 | 871.6251 | 591.0178 | 880.115 |  | 247.4995 | 958.8095 | 957.4597 | 485.1165 |  | 362.0213 | 624.3538 | 452.2919 | 628.8978 | 756.3844 | 898.4638 | 976.8895 | 41.4538 | 344.8702 | 71.3162 | 564.7457 | 13.5672 | 51.5682 | 49.2008 | 49.6655 | 46.8703 |  |  | 0.11259 | 0.72883 | -1.3314 | -1.4411 | 7.9086 | 5.0876 | 6.4955 | -2.5485 | 20.2176 | 48.7588 | 29.7047 | 0.00043534 | 0.00051091 | -0.00080989 | 17.7752 | 16.4133 | 16.9542 | 17.3159 | 17.2792 | 16.2438 | 14.6207 | 16.6943 | 17.0508 | 17.358 | 17.4106 | 17.1292 | 16.2944 | 14.5079 | 881.5452 | 616.0137 | 615.0836 | 367.8413 | 320.185 | 789.4827 | 504.1625 | 15.5565 | 18.4805 | 21.5654 | 36.0233 | 70.693 | 78.9701 |  |  |  | 597.5665 | 568.8539 | 569.3859 | 595.4607 | 106.6803 | 43.2661 | 805.3612 |  |  | 415.0566 |  |  | 17.6054 | 34.6845 | 338.727 | 16.7432 | 30.2576 | 891.8393 | 746.6522 | 584.4136 | 798.0226 | 792.4662 | 739.5442 |  | 803.5672 | 829.1271 | 937.0672 | 564.2919 | 660.6073 | 825.4987 |  | 969.0465 |  |  | 431.9851 | 645.9672 | 732.2546 | [6 empty] | 573.1827 |  |  | 378.6449 |  |  | 479.6598 | 646.0988 | 659.472 | 756.5413 | 1000.6894 | 1039.0305 | 532.8751 | 701.8365 | 815.6418 | 599.7005 | 673.516 | 915.1043 | 1061.915 | 630.8705 | 778.7669 | 887.2416 | 1064.3892 | 1067.4036 | 512.2795 | 621.3929 | 686.6647 | 562.5533 | 723.6288 | 872.4319 | 975.2495 | 1090.6947 | 577.6627 | 666.077 | 648.5019 | 821.2203 | 78.7485 | 0.00016941 | 18.2774 | 3.7417 | -39.4804 | 3.1235 | 11223.94 | 0.37 | 0.7228 | 1.7824 | -2.409 | -2.5063 | 6.7082 | 5.3804 | 6.0795 | 77.9845 | 124.6271 | 45.7796 | 62.0671 | 8.3752 | 34.5627 | 32.6489
42810.4508 | 934 | 17.8789 | 18.212 | 18.2951 | 18.3067 | 17.6246 | 16.2371 | 14.5702 | 16.516 | 17.0112 | 17.1329 | 17.136 | 16.6443 | 15.6599 | 14.322 | 14.3931 | 17.7887 | 19.364 | 49.7211 | 24.2165 | 85.3722 |  |  |  | 17.3363 | 67.0693 | 225.7149 | 670.517 | 712.67 | 680.5526 | 89.7598 | 103.6199 | 971.8021 | 91.7853 | 103.8977 | 870.1051 | 624.3627 | 880.9683 |  | 239.7865 | 954.4126 | 953.327 | 494.5188 |  | 362.6029 | 623.5325 | 452.6625 | 628.3747 | 753.5626 | 893.5728 | 974.9837 | 41.1775 | 345.9922 | 72.1786 | 566.0447 | 13.5254 | 51.5449 | 49.1952 | 49.6802 | 46.5445 |  |  | 0.22364 | 0.76431 | -0.95425 | -0.95347 | 7.3467 | 5.5127 | 6.0835 | -2.076 | 19.9932 | 50.1057 | 31.3285 | 0.0004337 | 0.0004567 | -0.00082139 | 17.804 | 16.4118 | 16.9554 | 17.314 | 17.2827 | 16.244 | 14.6217 | 16.691 | 17.0552 | 17.3619 | 17.413 | 17.1303 | 16.2923 | 14.5076 | 883.0318 | 621.9717 | 628.9668 | 361.3172 | 304.8585 | 791.5705 | 504.8812 | 15.5554 | 18.5389 | 21.6545 | 36.2558 | 70.8435 | 79.0766 |  |  |  | 598.0307 | 568.6528 | 569.9835 | 593.616 | 103.2752 | 53.4868 | 801.1193 |  |  | 414.0642 |  |  | 17.6108 | 34.8209 | 338.4302 | 16.7389 | 30.4144 | 885.0014 | 744.3042 | 583.7838 | 793.3461 | 787.9529 | 737.6092 |  | 802.8233 | 822.8648 | 936.3866 | 564.5627 | 660.0881 | 823.935 |  | 969.7214 |  |  | 432.8237 | 644.5606 | 730.1915 | [6 empty] | 572.9717 |  |  | 380.8425 |  |  | 479.9866 | 646.1204 | 660.4894 | 760.239 | 1004.8981 | 1036.0277 | 532.996 | 699.8876 | 812.803 | 599.1119 | 673.8949 | 915.3058 | 1059.5435 | 629.4749 | 776.0154 | 886.4395 | 1062.1428 | 1063.3561 | 512.0331 | 621.2027 | 686.1839 | 563.05 | 724.511 | 870.4314 | 968.4811 | 1087.2383 | 578.1522 | 666.5687 | 649.3677 | 820.6676 | 73.7675 | -2.7032e-05 | 18.2774 | 3.7783 | -39.4368 | 3.1235 | 11269.02 | 0.32 | 1.0178 | 1.8244 | -2.0385 | -2.0377 | 6.452 | 5.589 | 5.8712 | 77.8072 | 124.5088 | 45.6618 | 62.7037 | 6.9891 | 40.3981 | 32.7826
42810.4509 | 935 | 17.8736 | 18.2123 | 18.2952 | 18.3081 | 17.6238 | 16.2425 | 14.5768 | 16.519 | 17.0214 | 17.129 | 17.1376 | 16.6463 | 15.6551 | 14.3281 | 14.3962 | 17.8529 | 19.4298 | 50.4681 | 24.2554 | 85.4908 |  |  |  | 17.3383 | 67.3576 | 226.6905 | 670.7493 | 713.2566 | 680.5013 | 89.3699 | 100.0557 | 969.7948 | 93.1647 | 102.8657 | 872.9819 | 515.0343 | 885.2126 |  | 234.2558 | 960.9804 | 958.3916 | 482.3319 |  | 363.007 | 624.109 | 452.868 | 627.9002 | 751.1527 | 891.9404 | 973.7122 | 40.3648 | 347.0496 | 71.9163 | 567.2313 | 13.5134 | 51.51 | 49.1901 | 49.6954 | 46.1555 |  |  | 0.32812 | 0.96671 | -1.0311 | -1.717 | 6.7698 | 6.0003 | 6.0243 | -2.9868 | 20.3978 | 49.9654 | 30.0109 | 0.00043205 | 0.00049612 | -0.00083454 | 17.8138 | 16.3985 | 16.9399 | 17.3047 | 17.2715 | 16.2336 | 14.609 | 16.6816 | 17.0496 | 17.3617 | 17.409 | 17.1268 | 16.2862 | 14.4978 | 884.3111 | 621.1496 | 636.477 | 366.977 | 303.8103 | 793.0861 | 506.0672 | 15.5537 | 18.5924 | 21.74 | 36.4583 | 70.9844 | 79.1696 |  |  |  | 598.4823 | 569.1328 | 570.5546 | 595.4199 | 103.4282 | 47.5497 | 796.4726 |  |  | 416.2159 |  |  | 17.6096 | 34.9467 | 338.6853 | 16.7401 | 30.5779 | 885.8524 | 740.0756 | 583.5277 | 788.8412 | 783.2171 | 733.0747 |  | 801.5301 | 814.1024 | 934.8159 | 565.1684 | 659.7762 | 817.1503 |  | 969.3765 |  |  | 433.4149 | 639.7827 | 726.0194 | [6 empty] | 573.0483 |  |  | 383.2909 |  |  | 479.762 | 646.8698 | 660.0245 | 761.1392 | 1002.859 | 1035.6878 | 533.0752 | 698.3338 | 811.5828 | 599.6171 | 673.5402 | 915.5652 | 1052.383 | 628.5279 | 774.5325 | 886.245 | 1059.3355 | 1060.7285 | 512.0854 | 621.0215 | 685.5666 | 563.2722 | 725.5529 | 874.5592 | 965.0766 | 1086.3015 | 578.0056 | 666.5685 | 650.0867 | 821.0984 | 77.6313 | 0.00033077 | 18.278 | 3.8137 | -39.4983 | 3.1234 | 11286.25 | 0.43 | 1.2328 | 2.0525 | -2.1197 | -2.7354 | 6.1892 | 5.8269 | 5.8385 | 77.5326 | 124.0794 | 45.5789 | 63.1458 | 6.4134 | 22.7908 | 32.8128
42810.4509 | 936 | 17.8726 | 18.2116 | 18.2931 | 18.3096 | 17.6284 | 16.2432 | 14.5832 | 16.5209 | 17.0214 | 17.1285 | 17.1392 | 16.652 | 15.6634 | 14.3411 | 14.4051 | 17.9312 | 19.5069 | 51.292 | 24.2835 | 85.602 |  |  |  | 17.3663 | 67.6387 | 244.2889 | 673.9404 | 718.3608 | 684.4383 | 88.8709 | 96.5098 | 980.7713 | 92.0309 | 102.0352 | 879.9904 | 625.2937 | 889.7222 |  | 241.2672 | 970.3364 | 967.3762 | 453.9014 | 1195.0375 | 363.9172 | 625.4863 | 453.7517 | 627.9826 | 751.1929 | 899.4829 | 979.4209 | 39.6204 | 348.3614 | 71.6144 | 568.7129 | 13.5175 | 51.4903 | 49.1865 | 49.7043 | 45.7654 |  |  | 0.86235 | -0.60183 | -0.89577 | -1.1 | 6.34 | 4.9746 | 5.5834 | -2.3356 | 21.2797 | 51.8452 | 28.0043 | 0.0004452 | 0.00049777 | -0.00085425 | 17.8403 | 16.4048 | 16.945 | 17.3048 | 17.2729 | 16.2396 | 14.6115 | 16.6841 | 17.0454 | 17.3561 | 17.4061 | 17.1233 | 16.292 | 14.5167 | 875.8728 | 613.6219 | 616.9963 | 370.57 | 305.9336 | 794.0481 | 506.7254 | 15.5526 | 18.6439 | 21.8245 | 36.6799 | 71.1299 | 79.264 |  |  |  | 598.9259 | 570.5408 | 571.337 | 595.8716 | 103.4247 | 39.351 | 791.1766 |  |  | 415.9648 |  |  | 17.6091 | 35.0758 | 344.6903 | 16.7419 | 30.7316 | 897.1085 | 738.0089 | 582.9692 | 786.5773 | 780.6201 | 729.7282 |  | 800.1418 | 805.7412 | 933.6318 | 565.026 | 659.3732 | 808.9018 |  | 969.4309 |  |  | 432.6426 | 635.5029 | 722.3461 | [6 empty] | 572.7617 |  |  | 385.4794 |  |  | 480.7356 | 646.9272 | 660.0619 | 762.9512 | 999.8249 | 1033.6189 | 533.026 | 698.1342 | 811.1314 | 600.3015 | 672.1724 | 918.5069 | 1055.6085 | 628.3828 | 773.7939 | 886.0669 | 1061.3034 | 1062.4683 | 512.0256 | 620.5301 | 685.9427 | 563.6646 | 726.6578 | 877.3939 | 968.6366 | 1088.6974 | 577.9546 | 666.5651 | 650.807 | 823.9337 | 83.5491 | 0.00068853 | 18.2769 | 3.8472 | -39.5018 | 3.1235 | 11273.06 | 0.28 | 2.0026 | -1.6207 | -1.9772 | -2.1911 | 6.0089 | 5.3226 | 5.6389 | 77.1969 | 123.8061 | 45.4975 | 64.4551 | 8.7218 | 41.7051 | 32.8793
42810.4509 | 937 | 17.8697 | 18.2177 | 18.2941 | 18.3095 | 17.627 | 16.2395 | 14.5829 | 16.52 | 17.027 | 17.1303 | 17.1343 | 16.6561 | 15.666 | 14.3422 | 14.4114 | 18.0145 | 19.5825 | 52.2185 | 24.4605 | 85.7464 |  |  |  | 17.3797 | 67.9194 | 241.3978 | 678.3196 | 720.4379 | 687.0885 | 93.6649 | 99.5013 | 981.2684 | 89.6564 | 100.7091 | 878.7674 | 682.8046 | 888.8585 |  | 246.9775 | 965.5994 | 961.8224 | 465.3558 | 1089.4895 | 364.4035 | 625.8602 | 455.2762 | 628.8557 | 753.0711 | 907.1062 | 982.3992 | 40.0698 | 349.6298 | 71.8283 | 569.9397 | 13.5136 | 51.4837 | 49.1845 | 49.7213 | 45.4728 |  |  | 0.60608 | -1.0552 | -0.38059 | -1.4082 | 6.1508 | 5.0429 | 6.5336 | -1.8874 | 20.088 | 49.7524 | 28.4408 | 0.00041727 | 0.00047477 | -0.00084439 | 17.8634 | 16.4108 | 16.9378 | 17.2981 | 17.2761 | 16.247 | 14.6142 | 16.6913 | 17.0518 | 17.3587 | 17.4077 | 17.1276 | 16.2992 | 14.5074 | 873.7469 | 588.9441 | 559.2319 | 366.5637 | 294.1596 | 795.5724 | 506.7275 | 15.5556 | 18.6931 | 21.9041 | 36.8988 | 71.2773 | 79.3557 |  |  |  | 599.5176 | 572.7419 | 572.9927 | 598.7864 | 122.1634 | 46.049 | 787.9306 |  |  | 413.5164 |  |  | 17.6069 | 35.2006 | 352.44 | 16.7421 | 30.911 | 896.9176 | 738.9353 | 582.0298 | 786.1387 | 779.7526 | 731.8055 |  | 799.4732 | 800.7486 | 933.5853 | 564.535 | 658.9168 | 803.7209 |  | 969.8963 |  |  | 432.1315 | 637.7744 | 722.7719 | [6 empty] | 572.023 |  |  | 385.6364 |  |  | 481.1261 | 646.2479 | 659.778 | 764.1063 | 1004.0417 | 1033.6022 | 533.4862 | 699.1309 | 811.0491 | 600.3126 | 670.4193 | 925.7771 | 1059.0543 | 628.9848 | 775.9321 | 888.1589 | 1064.4778 | 1068.3955 | 511.7905 | 620.0244 | 689.5533 | 563.0711 | 727.5529 | 879.5226 | 966.5625 | 1090.2765 | 577.4336 | 666.3654 | 650.6306 | 823.1053 | 81.9008 | -0.008256 | 18.2763 | 3.8589 | -39.4846 | 3.1235 | 11290.31 | 0.29 | 1.6812 | -2.1465 | -1.2891 | -2.4796 | 5.9377 | 5.3764 | 6.1197 | 76.9333 | 123.925 | 45.4146 | 65.2818 | 15.1405 | 53.3916 | 32.9038
42810.4509 | 938 | 17.8657 | 18.2088 | 18.2866 | 18.3035 | 17.6161 | 16.2334 | 14.5754 | 16.5183 | 17.019 | 17.1293 | 17.1248 | 16.6475 | 15.6619 | 14.3342 | 14.4124 | 18.0915 | 19.6629 | 53.116 | 24.4868 | 85.8263 |  |  |  | 17.3997 | 68.2003 | 242.3241 | 678.7384 | 723.1842 | 687.4038 | 94.5589 | 103.4135 | 976.0114 | 90.2403 | 99.217 | 876.5159 | 796.7596 | 888.2377 |  | 245.7488 | 959.672 | 955.5721 | 469.9105 | 1120.8899 | 364.8584 | 627.3614 | 456.035 | 628.4609 | 747.749 | 901.0259 | 978.2466 | 40.0486 | 350.9728 | 71.2545 | 570.9659 | 13.5072 | 51.5077 | 49.1849 | 49.7135 | 45.2574 |  |  | 0.46152 | -0.86796 | -0.69666 | -1.0369 | 6.6824 | 5.5739 | 6.5783 | -2.8402 | 20.4906 | 49.5653 | 29.7433 | 0.00041398 | 0.0004452 | -0.00084439 | 17.8846 | 16.4007 | 16.9431 | 17.3035 | 17.2659 | 16.2299 | 14.6192 | 16.6944 | 17.0424 | 17.3614 | 17.4076 | 17.1258 | 16.2927 | 14.5022 | 892.91 | 609.7333 | 596.9756 | 369.6453 | 286.7689 | 798.3022 | 507.8561 | 15.571 | 18.7579 | 21.9982 | 37.1436 | 71.4453 | 79.4621 |  |  |  | 600.416 | 575.9332 | 575.5362 | 602.4856 | 108.4867 | 52.4724 | 787.0688 |  |  | 412.0823 |  |  | 17.6286 | 35.3266 | 354.1997 | 16.7538 | 31.0885 | 889.7703 | 740.0952 | 581.242 | 787.4932 | 781.0567 | 735.0867 |  | 799.0852 | 799.4014 | 933.8009 | 563.8521 | 658.4501 | 803.0201 |  | 970.6299 |  |  | 432.8121 | 643.0687 | 724.8964 | [6 empty] | 571.1732 |  |  | 383.8563 |  |  | 481.6665 | 645.1915 | 659.6365 | 767.077 | 1019.0172 | 1033.5081 | 534.3391 | 699.781 | 812.5447 | 599.9265 | 670.0052 | 928.902 | 1065.4443 | 629.6868 | 777.3811 | 887.4081 | 1063.3042 | 1067.9888 | 511.8306 | 619.8195 | 691.1316 | 562.2658 | 727.5471 | 881.7559 | 963.7174 | 1089.6613 | 578.4567 | 667.0033 | 649.8325 | 822.4613 | 81.4848 | -0.00033568 | 18.2775 | 3.8617 | -39.4889 | 3.1234 | 11300.94 | 0.31 | 1.4673 | -1.9483 | -1.7455 | -2.1295 | 6.173 | 5.6378 | 6.1248 | 76.7228 | 124.0543 | 45.3349 | 64.2145 | 11.1939 | 83.3762 | 32.9617
42810.4509 | 939 | 17.8525 | 18.201 | 18.2795 | 18.2985 | 17.6096 | 16.2244 | 14.5795 | 16.5041 | 17.014 | 17.12 | 17.1265 | 16.6368 | 15.6587 | 14.3254 | 14.4262 | 18.1723 | 19.7467 | 53.9911 | 24.4521 | 85.9439 |  |  |  | 17.4297 | 68.4619 | 249.8444 | 680.3969 | 725.1619 | 687.5746 | 91.2825 | 106.6984 | 972.408 | 92.6234 | 100.3025 | 875.7056 | 712.2849 | 880.419 |  | 258.1535 | 950.44 | 945.8439 | 481.0121 |  | 365.5225 | 629.696 | 457.7968 | 629.3342 | 750.9543 | 904.4294 | 982.1633 | 39.671 | 352.2672 | 72.3831 | 572.0554 | 13.4992 | 51.5031 | 49.1736 | 49.6997 | 45.1602 |  |  | -0.15157 | -1.1098 | -0.55473 | -0.76554 | 7.762 | 5.5936 | 5.7234 | -2.1608 | 21.2677 | 51.8383 | 29.8546 | 0.00042877 | 0.0004107 | -0.00084439 | 17.9043 | 16.3911 | 16.9353 | 17.2971 | 17.2611 | 16.2284 | 14.6118 | 16.6891 | 17.039 | 17.3534 | 17.4083 | 17.1194 | 16.2874 | 14.5043 | 886.228 | 612.7436 | 628.9269 | 376.0769 | 290.8415 | 799.9565 | 509.0332 | 15.5649 | 18.8186 | 22.0904 | 37.3737 | 71.5965 | 79.5552 |  |  |  | 601.1054 | 577.5372 | 576.896 | 602.5032 | 113.7553 | 47.7083 | 788.8554 |  |  | 415.5946 |  |  | 17.6464 | 35.4628 | 365.3391 | 16.7464 | 31.2685 | 884.3264 | 740.6405 | 580.9521 | 788.7278 | 783.2977 | 738.0649 |  | 798.791 | 806.0534 | 934.5273 | 563.7079 | 658.2072 | 807.8563 |  | 972.6591 |  |  | 434.8683 | 648.7297 | 727.0382 | [6 empty] | 571.0157 |  |  | 383.85 |  |  | 481.7905 | 644.24 | 660.9135 | 768.8003 | 1029.7968 | 1036.3547 | 534.9138 | 699.4186 | 811.3299 | 599.4639 | 670.5649 | 935.6949 | 1065.8447 | 629.9195 | 775.1897 | 884.7273 | 1064.7838 | 1067.4496 | 512.5871 | 620.1316 | 690.991 | 562.3775 | 726.359 | 879.4691 | 962.3872 | 1091.1081 | 579.4665 | 667.5775 | 649.0711 | 822.3673 | 83.3216 | -0.0002375 | 18.2778 | 3.8628 | -39.4638 | 3.1234 | 11290.27 | 0.36 | -0.84096 | -2.2059 | -1.5596 | -1.8321 | 6.6627 | 5.656 | 5.7212 | 76.5497 | 124.1797 | 45.2877 | 65.6033 | 7.902 | 59.8924 | 33.0847
42810.4509 | 940 | 17.8426 | 18.1928 | 18.2838 | 18.2987 | 17.6167 | 16.2243 | 14.5888 | 16.5124 | 17.0033 | 17.1252 | 17.1358 | 16.6441 | 15.6638 | 14.3292 | 14.4231 | 18.2438 | 19.823 | 54.8738 | 24.4558 | 86.0329 |  |  |  | 17.4361 | 68.7285 | 246.9557 | 678.8632 | 723.3426 | 685.1075 | 91.4929 | 99.5833 | 970.2615 | 93.9196 | 103.5205 | 871.4745 | 678.7264 | 873.1594 |  | 256.9327 | 951.583 | 947.9785 | 466.2409 | 1250.3512 | 366.8053 | 631.2511 | 460.2291 | 631.4918 | 758.3035 | 908.85 | 987.6432 | 39.5396 | 353.5942 | 72.9902 | 573.1991 | 13.4992 | 51.4894 | 49.1547 | 49.6915 | 45.1254 |  |  | -0.063521 | -1.6322 | -0.55407 | -0.85754 | 8.2463 | 5.9977 | 6.8694 | -2.2508 | 20.8201 | 50.103 | 29.1484 | 0.00045505 | 0.00043534 | -0.00082961 | 17.9267 | 16.3929 | 16.9355 | 17.2948 | 17.264 | 16.2258 | 14.615 | 16.6781 | 17.0431 | 17.3577 | 17.4106 | 17.1219 | 16.2951 | 14.5076 | 884.721 | 612.5486 | 626.307 | 373.8919 | 294.747 | 802.2168 | 510.1324 | 15.5736 | 18.8796 | 22.1828 | 37.5991 | 71.7427 | 79.6626 |  |  |  | 601.624 | 577.489 | 577.6229 | 601.2797 | 118.6469 | 47.4008 | 791.8528 |  |  | 420.657 |  |  | 17.6558 | 35.5961 | 359.3439 | 16.7547 | 31.4276 | 887.2073 | 741.3215 | 580.9007 | 791.1425 | 786.0934 | 739.325 |  | 798.5296 | 818.4218 | 936.8517 | 563.6359 | 658.0908 | 815.4641 |  | 974.3482 |  |  | 437.0114 | 652.3585 | 728.1104 | [6 empty] | 570.9524 |  |  | 382.959 |  |  | 481.4255 | 643.3063 | 660.6117 | 773.7844 | 1036.4626 | 1037.3189 | 535.2661 | 699.2178 | 810.0939 | 599.4403 | 670.0685 | 942.5701 | 1068.8301 | 630.0411 | 774.5158 | 880.4506 | 1064.4739 | 1069.6211 | 512.1247 | 620.3453 | 691.4369 | 562.7314 | 724.8476 | 878.27 | 956.5577 | 1091.8029 | 579.5356 | 668.5521 | 648.4059 | 819.3823 | 82.9882 | 0.0016216 | 18.2775 | 3.8621 | -39.337 | 3.1234 | 11320.84 | 0.36 | -0.54371 | -2.6775 | -1.56 | -1.9408 | 6.8803 | 5.8677 | 6.2796 | 76.4345 | 124.8319 | 45.2651 | 66.6574 | 8.4348 | 52.4508 | 33.2117
42810.4509 | 941 | 17.8418 | 18.1988 | 18.2746 | 18.2986 | 17.6163 | 16.228 | 14.5863 | 16.5045 | 17.0111 | 17.1196 | 17.1307 | 16.6459 | 15.6615 | 14.3347 | 14.4219 | 18.3213 | 19.8943 | 55.6822 | 24.524 | 86.0926 |  |  |  | 17.4467 | 68.9863 | 244.4391 | 676.3461 | 720.2887 | 683.1049 | 90.5118 | 100.5561 | 979.3324 | 91.453 | 103.2375 | 869.9806 | 505.5825 | 877.5964 |  | 241.5536 | 959.468 | 952.082 | 478.2682 | 1268.5877 | 368.32 | 631.4819 | 460.1123 | 628.1901 | 756.0085 | 911.1702 | 989.8071 | 39.2014 | 355.3337 | 75.4167 | 574.592 | 13.5125 | 51.4781 | 49.1273 | 49.6705 | 45.0484 |  |  | 0.39909 | -1.1367 | -0.56853 | -1.1053 | 7.7574 | 5.2893 | 6.188 | -2.2482 | 21.4728 | 52.0193 | 28.0973 | 0.00048791 | 0.00044191 | -0.00084768 | 17.9621 | 16.4054 | 16.9411 | 17.2996 | 17.2732 | 16.2375 | 14.621 | 16.6865 | 17.0515 | 17.3614 | 17.416 | 17.1313 | 16.3044 | 14.5165 | 885.2971 | 621.2774 | 615.8739 | 374.3295 | 293.2115 | 804.2602 | 510.8109 | 15.5749 | 18.9386 | 22.2656 | 37.8233 | 71.8847 | 79.7594 |  |  |  | 602.0345 | 577.1895 | 578.181 | 599.4868 | 109.4638 | 41.52 | 794.5756 |  |  | 421.9278 |  |  | 17.6522 | 35.7177 | 355.2882 | 16.7823 | 31.5976 | 891.8608 | 743.1598 | 580.8334 | 791.2164 | 786.1975 | 741.8596 |  | 798.6941 | 824.5863 | 937.8603 | 563.4073 | 657.873 | 819.8601 |  | 975.4803 |  |  | 437.5288 | 654.0366 | 729.9103 | [6 empty] | 570.6152 |  |  | 383.2832 |  |  | 481.6214 | 642.6821 | 659.3753 | 777.4918 | 1036.2726 | 1038.3909 | 535.3298 | 699.937 | 811.4569 | 599.7577 | 669.3863 | 942.1561 | 1071.0971 | 630.0842 | 776.5059 | 876.908 | 1063.2826 | 1070.4527 | 512.2489 | 620.1683 | 690.6662 | 563.0052 | 723.945 | 876.6035 | 953.7677 | 1091.2116 | 579.7597 | 668.2997 | 648.0324 | 820.1792 | 82.0062 | -0.00060927 | 18.2762 | 3.8375 | -39.4481 | 3.1234 | 11298.71 | 0.36 | 1.3614 | -2.2348 | -1.5804 | -2.2036 | 6.6797 | 5.5157 | 5.9659 | 76.4146 | 125.0944 | 45.2255 | 67.3984 | 9.7434 | 21.6102 | 33.3353
42810.4509 | 942 | 17.841 | 18.1951 | 18.2808 | 18.3036 | 17.6163 | 16.2265 | 14.5856 | 16.5137 | 17.0175 | 17.1284 | 17.1357 | 16.6541 | 15.6618 | 14.3365 | 14.4189 | 18.3951 | 19.9695 | 56.3722 | 24.5798 | 86.1744 |  |  |  | 17.4625 | 69.2191 | 242.9791 | 675.5604 | 716.6308 | 682.9178 | 91.3891 | 104.6048 | 979.7118 | 94.5809 | 106.1046 | 870.385 | 524.6518 | 882.0745 |  | 225.9813 | 963.1422 | 955.1651 | 472.8929 | 1285.7668 | 369.501 | 632.91 | 459.1726 | 625.5784 | 750.5654 | 912.0415 | 989.7018 | 39.8091 | 356.742 | 76.6903 | 575.7579 | 13.4967 | 51.5302 | 49.0961 | 49.6515 | 44.9937 |  |  | -0.025409 | -0.95733 | -0.94045 | -1.4463 | 6.3308 | 5.267 | 6.1669 | -2.4492 | 19.7003 | 50.7221 | 27.9041 | 0.00040248 | 0.00044355 | -0.00084275 | 17.983 | 16.4002 | 16.9351 | 17.2933 | 17.2706 | 16.2352 | 14.6216 | 16.6914 | 17.0544 | 17.3634 | 17.41 | 17.1306 | 16.3015 | 14.5152 | 882.7468 | 605.8033 | 575.0598 | 371.3635 | 286.2201 | 805.4311 | 510.7053 | 15.5781 | 19.001 | 22.3557 | 38.0407 | 72.0203 | 79.8508 |  |  |  | 602.327 | 576.209 | 577.5473 | 597.1111 | 103.6938 | 42.3887 | 794.1881 |  |  | 420.363 |  |  | 17.6455 | 35.8575 | 353.6956 | 16.7709 | 31.7595 | 890.8694 | 743.7454 | 581.2163 | 789.9718 | 784.8982 | 742.4873 |  | 798.6838 | 822.8067 | 939.3611 | 563.0397 | 657.6284 | 821.4225 |  | 976.6191 |  |  | 437.0799 | 653.5163 | 730.9263 | [6 empty] | 570.7389 |  |  | 384.7469 |  |  | 481.8924 | 642.5072 | 658.8812 | 780.2575 | 1032.9108 | 1040.2562 | 535.1929 | 699.9207 | 811.7529 | 599.9097 | 669.6201 | 941.8114 | 1072.0927 | 630.0871 | 776.4062 | 875.981 | 1063.6146 | 1070.5162 | 513.2105 | 620.1117 | 690.1405 | 563.5737 | 723.9276 | 874.5394 | 952.1225 | 1090.1533 | 580.1044 | 668.1673 | 648.095 | 824.3606 | 81.3875 | -0.00028661 | 18.2773 | 3.8147 | -39.3856 | 3.1234 | 11275.26 | 0.33 | -0.34348 | -2.0525 | -2.0343 | -2.5228 | 6.0366 | 5.5061 | 5.9579 | 76.394 | 125.7912 | 45.1842 | 68.1445 | 14.2551 | 24.4079 | 33.4539
42810.4509 | 943 | 17.8432 | 18.2 | 18.2829 | 18.3036 | 17.614 | 16.2296 | 14.5871 | 16.5162 | 17.0189 | 17.1309 | 17.1389 | 16.6538 | 15.6699 | 14.3398 | 14.4263 | 18.4786 | 20.0513 | 56.9838 | 24.6325 | 86.2578 |  |  |  | 17.483 | 69.4375 | 243.7555 | 675.5706 | 714.3476 | 684.0256 | 89.2234 | 101.1666 | 973.1472 | 91.5464 | 103.6305 | 869.1828 | 723.3991 | 874.2601 | 1146.7947 | 232.9643 | 959.4252 | 954.9813 | 453.5214 | 1391.9775 | 370.9572 | 633.9356 | 458.7332 | 624.907 | 749.3468 | 912.4315 | 989.7322 | 41.0456 | 357.93 | 76.1992 | 576.724 | 13.5023 | 51.5788 | 49.0569 | 49.6376 | 44.9078 |  |  | 0.24007 | -1.0401 | -0.47587 | -1.006 | 7.0996 | 5.4667 | 6.4423 | -2.0031 | 19.4425 | 49.4499 | 28.6137 | 0.00043698 | 0.00047641 | -0.00084275 | 18.0095 | 16.3949 | 16.9397 | 17.299 | 17.2666 | 16.2311 | 14.6168 | 16.6913 | 17.0486 | 17.3676 | 17.4072 | 17.1343 | 16.298 | 14.521 | 876.6399 | 605.9108 | 572.6578 | 370.0223 | 288.0488 | 806.2549 | 510.6312 | 15.575 | 19.0659 | 22.4433 | 38.2922 | 72.1674 | 79.9464 |  |  |  | 602.7276 | 575.8824 | 577.4412 | 597.0078 | 110.1747 | 51.0401 | 792.6971 |  |  | 419.025 |  |  | 17.6629 | 35.9769 | 351.5948 | 16.7836 | 31.9252 | 885.7601 | 743.474 | 582.0161 | 787.2557 | 781.9125 | 741.6372 |  | 798.4552 | 816.6829 | 939.6726 | 563.2841 | 657.4149 | 818.7294 |  | 977.275 |  |  | 436.604 | 651.9754 | 730.3107 | [6 empty] | 571.1252 |  |  | 385.6205 |  |  | 482.1037 | 642.4638 | 657.9931 | 782.1613 | 1031.3433 | 1041.0223 | 535.2218 | 700.238 | 810.6225 | 599.8211 | 669.2876 | 941.1176 | 1069.331 | 630.378 | 777.5133 | 873.9305 | 1059.8894 | 1068.3007 | 514.2938 | 620.4193 | 691.685 | 564.5922 | 724.5026 | 873.6923 | 949.3934 | 1087.6443 | 580.3847 | 669.8951 | 648.4671 | 826.6655 | 80.443 | -0.0015073 | 18.2778 | 3.8047 | -39.3217 | 3.1234 | 11236.83 | 0.31 | 1.0564 | -2.1406 | -1.4479 | -2.1052 | 6.3937 | 5.6104 | 6.0905 | 76.3474 | 126.0959 | 45.1324 | 69.1493 | 14.5056 | 63.418 | 33.5289
42810.451 | 944 | 17.8338 | 18.184 | 18.2646 | 18.2918 | 17.6052 | 16.2211 | 14.5802 | 16.503 | 17.0069 | 17.1258 | 17.1304 | 16.6406 | 15.6589 | 14.334 | 14.4292 | 18.5608 | 20.1331 | 57.6763 | 24.698 | 86.3675 |  |  |  | 17.4968 | 69.6519 | 250.935 | 677.9772 | 717.1802 | 688.7659 | 92.539 | 101.8963 | 965.5052 | 91.0224 | 105.16 | 877.2589 | 643.4584 | 886.1928 | 1198.2811 | 241.8514 | 948.5872 | 945.1083 | 460.4385 | 1092.9773 | 372.6618 | 634.897 | 458.7822 | 625.5577 | 747.7845 | 904.6728 | 983.662 | 42.7545 | 358.8257 | 74.9259 | 577.2787 | 13.5148 | 51.6527 | 49.0339 | 49.6212 | 44.8134 |  |  | 0.45297 | -0.50195 | -0.76895 | -1.4325 | 7.1654 | 4.876 | 6.3595 | -2.9421 | 19.7239 | 48.7324 | 29.206 | 0.00048298 | 0.00040248 | -0.00082632 | 18.0414 | 16.3886 | 16.9405 | 17.2936 | 17.2592 | 16.2312 | 14.6131 | 16.6885 | 17.0496 | 17.3737 | 17.4175 | 17.1345 | 16.2908 | 14.5141 | 887.8103 | 606.2384 | 552.5058 | 359.1662 | 276.8722 | 807.0008 | 510.5681 | 15.5803 | 19.1304 | 22.5454 | 38.511 | 72.3079 | 80.0492 |  |  |  | 603.4033 | 578.8553 | 580.2346 | 603.8115 | 89.2139 | 34.4233 | 789.4983 |  |  | 418.1775 |  |  | 17.6675 | 36.1107 | 356.8372 | 16.7947 | 32.1089 | 880.0163 | 742.4308 | 583.1242 | 783.4154 | 778.0734 | 740.0207 |  | 798.1116 | 809.787 | 938.5965 | 563.9616 | 657.2394 | 816.4802 |  | 977.4 |  |  | 437.0626 | 651.4285 | 729.3576 | [6 empty] | 572.0194 |  |  | 385.9097 |  |  | 482.1375 | 642.1951 | 657.2259 | 782.5851 | 1030.1477 | 1039.0164 | 535.5405 | 700.6411 | 811.3531 | 599.939 | 668.8034 | 944.0759 | 1062.8143 | 630.7998 | 781.21 | 872.2352 | 1056.3133 | 1065.8803 | 514.5582 | 620.8802 | 693.6154 | 565.0523 | 725.1463 | 876.9131 | 949.2503 | 1086.2904 | 580.4067 | 672.1407 | 648.7598 | 828.9261 | 80.8654 | -8.3153e-05 | 18.2775 | 3.789 | -39.3109 | 3.1234 | 11143.44 | 0.38 | 1.4547 | -1.4878 | -1.8415 | -2.5135 | 6.4022 | 5.2813 | 6.0314 | 76.2869 | 125.8228 | 45.0767 | 68.204 | 16.7308 | 45.1077 | 33.4618
42810.451 | 945 | 17.8343 | 18.1912 | 18.266 | 18.2921 | 17.6062 | 16.2223 | 14.5874 | 16.5094 | 17.006 | 17.1306 | 17.132 | 16.6476 | 15.667 | 14.3358 | 14.4453 | 18.6508 | 20.222 | 58.5311 | 24.7891 | 86.4973 |  |  |  | 17.5181 | 69.8875 | 253.3188 | 681.2684 | 720.1282 | 692.0196 | 97.4704 | 104.2694 | 962.9752 | 90.9661 | 103.1986 | 879.4015 | 616.2111 | 888.8787 | 1246.7448 | 235.4411 | 952.9746 | 949.1689 | 473.4711 | 669.8919 | 373.3715 | 635.2738 | 460.2189 | 626.188 | 745.461 | 897.8901 | 975.0145 | 44.1448 | 359.6806 | 73.5877 | 577.9193 | 13.5244 | 51.7366 | 49.0038 | 49.6071 | 44.7624 |  |  | -0.10032 | -0.14645 | -1.4372 | -1.7302 | 7.647 | 5.7953 | 6.5829 | -3.4323 | 21.3099 | 51.1409 | 30.6583 | 0.00050269 | 0.00035977 | -0.00086082 | 18.0597 | 16.3991 | 16.9381 | 17.2907 | 17.2657 | 16.2269 | 14.6276 | 16.693 | 17.0517 | 17.3699 | 17.4197 | 17.1361 | 16.2955 | 14.5231 | 865.9246 | 599.8022 | 553.2645 | 348.9111 | 273.9813 | 806.8074 | 510.079 | 15.5888 | 19.1909 | 22.6394 | 38.7347 | 72.4427 | 80.1242 |  |  |  | 604.1447 | 581.2259 | 582.3088 | 606.5961 | 121.1328 | 55.8815 | 785.6586 |  |  | 418.6464 |  |  | 17.669 | 36.2358 | 363.8795 | 16.7955 | 32.2794 | 881.7907 | 741.7927 | 584.643 | 780.8526 | 776.039 | 739.1575 |  | 797.722 | 804.4297 | 937.1524 | 565.4631 | 657.2942 | 814.3822 |  | 976.8194 |  |  | 438.0165 | 652.1601 | 728.6948 | [6 empty] | 573.4809 |  |  | 386.0636 |  |  | 482.4189 | 642.0981 | 659.752 | 781.6991 | 1026.8672 | 1034.9232 | 535.6222 | 701.2528 | 814.3961 | 600.4812 | 669.7203 | 948.4228 | 1059.8408 | 630.9699 | 784.1692 | 869.0038 | 1054.6689 | 1064.4798 | 514.1031 | 621.1316 | 696.2334 | 565.3281 | 725.5648 | 878.3627 | 954.1899 | 1085.4979 | 580.0752 | 672.335 | 649.0154 | 827.3769 | 77.5652 | -0.00072152 | 18.2767 | 3.7775 | -39.3827 | 3.1234 | 11066.64 | 0.35 | -0.68575 | -0.80381 | -2.5181 | -2.7629 | 6.5948 | 5.741 | 6.1187 | 76.1915 | 125.3498 | 45.0465 | 70.559 | 16.5388 | 39.4378 | 33.5184
42810.451 | 946 | 17.8378 | 18.1978 | 18.2756 | 18.2986 | 17.6193 | 16.2316 | 14.6037 | 16.5154 | 17.0121 | 17.1347 | 17.1401 | 16.6534 | 15.6666 | 14.3434 | 14.4501 | 18.7414 | 20.2958 | 59.4404 | 24.9513 | 86.6163 |  |  |  | 17.5414 | 70.134 | 251.5681 | 682.0119 | 720.48 | 691.4834 | 93.9654 | 106.4965 | 979.9998 | 93.9099 | 104.3333 | 879.0859 | 596.2837 | 885.8724 |  | 242.656 | 958.282 | 955.2055 | 472.7285 | 651.7661 | 371.3618 | 636.4517 | 459.4579 | 626.1334 | 745.6933 | 907.6976 | 976.3402 | 45.8687 | 360.9258 | 73.1975 | 578.9879 | 13.551 | 51.8265 | 48.9819 | 49.5788 | 44.8337 |  |  | -0.19888 | 0.10325 | -0.36022 | -1.2387 | 7.6779 | 5.1494 | 5.1596 | -2.6615 | 19.1438 | 48.4145 | 30.6996 | 0.00039098 | 0.00041234 | -0.00084111 | 18.085 | 16.3961 | 16.9368 | 17.2933 | 17.2724 | 16.2307 | 14.6151 | 16.6919 | 17.0519 | 17.3692 | 17.4251 | 17.1368 | 16.3054 | 14.5336 | 886.8788 | 626.7408 | 594.1012 | 351.803 | 269.7158 | 808.3021 | 510.9943 | 15.5987 | 19.2695 | 22.7322 | 38.9649 | 72.5856 | 80.2092 |  |  |  | 604.8814 | 582.9064 | 583.7849 | 607.3625 | 91.2746 | 50.247 | 785.2529 |  |  | 420.9812 |  |  | 17.6677 | 36.3619 | 360.5632 | 16.7988 | 32.4432 | 889.2699 | 741.0258 | 586.2708 | 781.7741 | 778.6651 | 740.086 |  | 797.3146 | 819.2319 | 936.1181 | 567.3969 | 657.6195 | 815.7574 |  | 976.4047 |  |  | 438.7702 | 655.1835 | 728.8853 | [6 empty] | 575.0719 |  |  | 386.3311 |  |  | 482.6283 | 642.7489 | 662.6569 | 780.3293 | 1023.3777 | 1032.519 | 535.697 | 701.6442 | 815.0007 | 600.8995 | 670.7397 | 945.9951 | 1058.4187 | 631.1364 | 784.2994 | 866.7938 | 1057.0324 | 1065.837 | 513.833 | 621.0076 | 697.1336 | 565.8367 | 725.9097 | 877.7234 | 966.0258 | 1085.9458 | 579.6798 | 672.1011 | 649.2961 | 825.1817 | 84.7966 | -0.00018839 | 18.2765 | 3.7769 | -39.4213 | 3.1234 | 11033.06 | 0.29 | -0.96527 | 0.67538 | -1.2615 | -2.3392 | 6.6357 | 5.4343 | 5.4396 | 76.041 | 124.4945 | 45.0613 | 68.8247 | 12.203 | 35.8309 | 33.6306
42810.451 | 947 | 17.8325 | 18.1862 | 18.2701 | 18.2932 | 17.6175 | 16.2288 | 14.5884 | 16.5072 | 17.0222 | 17.1291 | 17.1341 | 16.6471 | 15.6629 | 14.3409 | 14.4553 | 18.8323 | 20.3821 | 60.274 | 25.0975 | 86.6769 |  |  |  | 17.5663 | 70.3773 | 253.1125 | 680.6181 | 720.3293 | 689.278 | 92.7551 | 108.0356 | 997.5823 | 95.8172 | 107.9165 | 878.7194 | 758.7953 | 881.8131 | 1229.3317 | 248.9544 | 958.5716 | 954.1107 | 477.8478 | 900.2138 | 371.2137 | 639.7221 | 457.8786 | 626.0062 | 751.6169 | 908.8115 | 976.9525 | 45.3409 | 361.7719 | 73.4079 | 579.4601 | 13.5638 | 51.9038 | 48.9687 | 49.5589 | 44.96 |  |  | 0.61068 | 0.44495 | -0.80049 | -1.2111 | 7.833 | 4.1374 | 5.0827 | -3.3363 | 20.1349 | 48.2715 | 29.4888 | 0.00039098 | 0.00040248 | -0.00083454 | 18.1088 | 16.3922 | 16.9285 | 17.2894 | 17.2631 | 16.2309 | 14.6151 | 16.684 | 17.0485 | 17.3625 | 17.4123 | 17.1363 | 16.306 | 14.5253 | 879.6027 | 624.3329 | 608.7799 | 342.9975 | 260.6489 | 808.041 | 511.1596 | 15.5971 | 19.3112 | 22.8165 | 39.1906 | 72.7043 | 80.2933 |  |  |  | 605.3033 | 582.3058 | 584.208 | 602.7707 | 99.2088 | 42.6343 | 790.3821 |  |  | 423.6589 |  |  | 17.6809 | 36.4993 | 361.3017 | 16.7882 | 32.6232 | 895.4404 | 739.8382 | 588.0177 | 785.9247 | 784.0725 | 738.2579 |  | 796.7588 | 836.5135 | 935.6208 | 569.0134 | 657.9925 | 823.961 |  | 976.4426 |  |  | 439.6725 | 656.5116 | 727.9614 | [6 empty] | 576.8152 |  |  | 386.2965 |  |  | 482.5716 | 643.2688 | 663.3777 | 778.6611 | 1017.078 | 1032.1355 | 536.359 | 701.4506 | 815.0291 | 600.6352 | 670.9495 | 940.58 | 1057.2752 | 631.917 | 783.6783 | 863.8597 | 1059.0046 | 1068.2852 | 513.9141 | 620.8891 | 697.742 | 566.2887 | 726.493 | 876.2973 | 972.1909 | 1085.6669 | 580.3304 | 671.8757 | 649.8183 | 826.0793 | 86.6937 | 0.00082184 | 18.2776 | 3.788 | -39.4496 | 3.1233 | 10978.71 | 0.39 | 1.6895 | 1.4045 | -1.8839 | -2.3172 | 6.7055 | 4.8734 | 5.4015 | 75.9218 | 123.8013 | 45.095 | 69.5292 | 10.6085 | 72.1039 | 33.8346
42810.451 | 948 | 17.8263 | 18.1815 | 18.2711 | 18.2896 | 17.6052 | 16.2232 | 14.5937 | 16.5008 | 17.008 | 17.1288 | 17.1337 | 16.6487 | 15.6629 | 14.3376 | 14.4568 | 18.9091 | 20.4632 | 61.0223 | 25.1597 | 86.7385 |  |  |  | 17.5858 | 70.5852 | 252.8233 | 681.5763 | 719.3649 | 690.5227 | 91.5417 | 104.6087 | 990.1452 | 94.9805 | 110.3477 | 878.2082 | 629.3086 | 880.0723 | 1246.5765 | 249.4483 | 961.9749 | 955.2967 | 484.622 | 1393.8052 | 371.4148 | 640.4206 | 458.4625 | 624.0822 | 750.5951 | 898.4555 | 974.7744 | 44.2121 | 362.8025 | 73.2512 | 579.8613 | 13.5418 | 51.9416 | 48.9646 | 49.545 | 45.1415 |  |  | 0.52788 | -0.3771 | -0.80246 | -0.93442 | 6.8401 | 3.8877 | 5.293 | -2.3014 | 19.4561 | 49.7837 | 29.6902 | 0.00037949 | 0.00032363 | -0.00084932 | 18.1376 | 16.3877 | 16.9223 | 17.2863 | 17.2606 | 16.2247 | 14.6209 | 16.6803 | 17.056 | 17.3652 | 17.4048 | 17.1367 | 16.3048 | 14.5139 | 877.9047 | 616.8428 | 586.0383 | 333.3364 | 256.6783 | 807.8719 | 510.9252 | 15.6005 | 19.3996 | 22.9159 | 39.4403 | 72.857 | 80.3884 |  |  |  | 605.523 | 580.9176 | 583.453 | 599.6476 | 84.7389 | 41.4656 | 795.4149 |  |  | 427.7769 |  |  | 17.6904 | 36.6275 | 361.2013 | 16.8105 | 32.795 | 896.0468 | 740.9508 | 589.2938 | 789.6412 | 787.7551 | 738.9241 |  | 796.7822 | 840.3572 | 935.7528 | 570.4116 | 658.2471 | 831.6276 |  | 976.4054 |  |  | 440.5259 | 656.9713 | 728.5254 | [6 empty] | 578.3329 |  |  | 386.8432 |  |  | 482.6908 | 643.4264 | 662.7854 | 776.3172 | 1011.1362 | 1031.7144 | 537.4113 | 701.8385 | 817.6825 | 600.6837 | 670.4823 | 936.5996 | 1056.9135 | 632.7556 | 783.3838 | 861.5212 | 1059.9431 | 1067.9524 | 514.5173 | 620.9747 | 697.67 | 567.0097 | 726.9337 | 878.2966 | 972.471 | 1083.6649 | 581.154 | 671.8887 | 650.2194 | 826.9359 | 85.8984 | 0.0014111 | 18.2777 | 3.8106 | -39.5088 | 3.1233 | 10922.72 | 0.3 | 1.5718 | -1.2935 | -1.8869 | -2.0361 | 6.2386 | 4.7033 | 5.4879 | 75.9105 | 123.7511 | 45.1099 | 69.6507 | 13.0837 | 41.6281 | 33.9613
42810.451 | 949 | 17.8228 | 18.1911 | 18.2651 | 18.2924 | 17.6115 | 16.2264 | 14.6048 | 16.5184 | 17.0209 | 17.1361 | 17.1346 | 16.655 | 15.6684 | 14.3454 | 14.4601 | 18.9904 | 20.5485 | 61.7063 | 25.1467 | 86.7823 |  |  |  | 17.5978 | 70.7853 | 255.3707 | 682.477 | 718.2531 | 691.5732 | 88.8328 | 105.2654 | 992.0912 | 90.8694 | 103.4909 | 870.4913 | 621.5661 | 876.425 | 1206.2251 | 252.4649 | 959.6074 | 954.1674 | 493.1589 |  | 372.2774 | 642.3497 | 457.4875 | 621.2091 | 743.0157 | 890.4222 | 974.8363 | 43.4764 | 363.7936 | 72.2377 | 580.0909 | 13.5576 | 51.9343 | 48.9642 | 49.5456 | 45.3669 |  |  | 0.26767 | 0.007975 | -0.66381 | -1.1348 | 8.5565 | 5.4109 | 6.8438 | -2.4492 | 20.124 | 50 | 29.452 | 0.00040741 | 0.00044191 | -0.00084111 | 18.1622 | 16.3833 | 16.9249 | 17.2807 | 17.2583 | 16.2246 | 14.6169 | 16.6862 | 17.051 | 17.3683 | 17.4109 | 17.1313 | 16.3079 | 14.5168 | 854.0891 | 604.1684 | 574.6534 | 328.9862 | 267.0815 | 806.539 | 510.6159 | 15.6085 | 19.4582 | 23.0149 | 39.6623 | 72.9753 | 80.4762 |  |  |  | 605.9338 | 582.5672 | 584.2915 | 603.1673 | 112.3768 | 57.596 | 797.4745 |  |  | 432.9914 |  |  | 17.6967 | 36.7559 | 359.5491 | 16.8247 | 32.9609 | 897.1089 | 742.7158 | 590.5223 | 791.7774 | 790.8432 | 741.1605 |  | 797.1722 | 839.0211 | 936.5687 | 572.4054 | 658.6637 | 833.7309 |  | 976.2306 |  |  | 441.3802 | 656.8815 | 730.3357 | [6 empty] | 579.7289 |  |  | 387.1719 |  |  | 482.8763 | 643.5977 | 662.1389 | 776.2199 | 1008.0507 | 1031.325 | 538.2869 | 701.7288 | 817.989 | 601.2791 | 669.984 | 942.3824 | 1053.6941 | 633.9119 | 782.826 | 857.4212 | 1059.1755 | 1067.4121 | 515.7227 | 621.3071 | 699.8957 | 568.0098 | 727.0931 | 875.9383 | 971.4089 | 1084.4327 | 581.8246 | 672.8878 | 650.9961 | 832.512 | 85.0614 | -0.0010442 | 18.2772 | 3.8392 | -39.5141 | 3.1233 | 10913.87 | 0.32 | 1.1199 | 0.1883 | -1.718 | -2.2463 | 6.9536 | 5.5297 | 6.2189 | 75.9676 | 124.1382 | 45.1425 | 71.7675 | 14.2805 | 39.9018 | 33.9382
42810.451 | 950 | 17.8206 | 18.1859 | 18.2721 | 18.2947 | 17.6102 | 16.2312 | 14.6055 | 16.509 | 17.0128 | 17.1285 | 17.1375 | 16.6538 | 15.6711 | 14.3489 | 14.471 | 19.0983 | 20.6495 | 62.3608 | 25.1544 | 86.8523 |  |  |  | 17.6265 | 70.9814 | 252.3562 | 682.3011 | 718.0165 | 693.016 | 88.7645 | 103.5599 | 984.2078 | 93.3907 | 105.1076 | 874.7141 | 593.3132 | 878.906 | 1281.5757 | 263.9574 | 953.6158 | 950.8674 | 484.3136 |  | 373.9032 | 642.9919 | 458.4057 | 623.3946 | 747.2299 | 897.0878 | 977.0457 | 42.4861 | 364.6627 | 71.8701 | 580.4356 | 13.5918 | 51.9288 | 48.958 | 49.5292 | 45.705 |  |  | 0.43589 | -0.44544 | -0.37599 | -0.41398 | 7.739 | 4.6506 | 6.9246 | -3.1083 | 20.831 | 51.2219 | 30.1119 | 0.00033184 | 0.00044027 | -0.00083454 | 18.1873 | 16.3892 | 16.9293 | 17.2862 | 17.2659 | 16.2291 | 14.6097 | 16.6858 | 17.0571 | 17.3697 | 17.4159 | 17.1342 | 16.3013 | 14.524 | 859.2275 | 627.5964 | 658.2139 | 360.333 | 297.1428 | 807.4627 | 512.6063 | 15.609 | 19.5225 | 23.0983 | 39.8798 | 73.0969 | 80.5517 |  |  |  | 606.6413 | 585.2014 | 586.6579 | 608.0222 | 113.3394 | 58.3942 | 799.9976 |  |  | 438.4936 |  |  | 17.7013 | 36.8888 | 360.0395 | 16.8209 | 33.1345 | 892.7873 | 742.7074 | 591.3319 | 795.531 | 795.9675 | 740.9811 |  | 797.2924 | 847.594 | 936.7139 | 573.2182 | 658.942 | 837.0053 |  | 975.2467 |  |  | 441.6838 | 654.6546 | 731.618 | [6 empty] | 580.5833 |  |  | 387.8472 |  |  | 483.4012 | 644.2139 | 660.912 | 777.7379 | 1011.5179 | 1030.5652 | 539.0415 | 702.0059 | 815.6056 | 601.893 | 669.9733 | 940.9689 | 1044.1985 | 634.9909 | 782.7967 | 852.8437 | 1062.5743 | 1067.0441 | 516.5953 | 621.5129 | 702.612 | 569.6196 | 727.8835 | 876.9056 | 976.6487 | 1085.7944 | 582.3504 | 673.5401 | 652.434 | 837.2426 | 81.5407 | 0.00015539 | 18.2766 | 3.8706 | -39.54 | 3.1233 | 10954.61 | 0.27 | 1.4301 | -1.4078 | -1.2934 | -1.3572 | 6.632 | 5.1411 | 6.2734 | 76.0093 | 123.9623 | 45.1787 | 71.5633 | 5.4354 | 34.9861 | 33.9321
42810.451 | 951 | 17.8178 | 18.1792 | 18.2687 | 18.2894 | 17.6034 | 16.2272 | 14.6004 | 16.5111 | 17.0119 | 17.1299 | 17.137 | 16.6493 | 15.6698 | 14.3437 | 14.4789 | 19.1955 | 20.74 | 63.0398 | 25.1297 | 86.9482 |  |  |  | 17.6653 | 71.1478 | 259.6402 | 684.8197 | 721.073 | 695.9355 | 91.2506 | 104.6181 | 985.1167 | 92.3904 | 105.3657 | 881.1755 | 603.961 | 888.0627 |  | 283.8393 | 959.4965 | 957.975 | 455.868 | 1162.1453 | 375.0324 | 642.8764 | 459.2015 | 624.9204 | 750.0267 | 899.3293 | 978.5734 | 40.906 | 365.8837 | 71.1305 | 580.9742 | 13.6096 | 51.9063 | 48.9586 | 49.5215 | 46.1045 |  |  | 0.094187 | -0.74245 | -0.36219 | -0.87133 | 7.5807 | 5.6915 | 6.8148 | -2.3947 | 18.6978 | 48.3627 | 29.6451 | 0.00042713 | 0.00038277 | -0.00082632 | 18.2111 | 16.3772 | 16.9139 | 17.2803 | 17.2429 | 16.2148 | 14.6012 | 16.6842 | 17.0392 | 17.3552 | 17.4044 | 17.1296 | 16.2955 | 14.5066 | 873.2846 | 624.582 | 639.5178 | 372.809 | 296.2919 | 808.593 | 513.7814 | 15.6202 | 19.5975 | 23.2009 | 40.1107 | 73.2309 | 80.6337 |  |  |  | 607.5209 | 588.114 | 589.6968 | 612.4933 | 97.369 | 39.6444 | 804.6463 |  |  | 440.9731 |  |  | 17.7124 | 37.0154 | 363.5471 | 16.8355 | 33.3024 | 897.8382 | 740.9781 | 591.582 | 798.8647 | 798.7025 | 739.0964 |  | 797.2003 | 853.3604 | 936.7585 | 573.664 | 659.0258 | 841.08 |  | 973.7297 |  |  | 441.9736 | 652.5064 | 730.2077 | [6 empty] | 580.9006 |  |  | 388.9259 |  |  | 484.3136 | 644.8601 | 660.9064 | 779.6356 | 1009.8495 | 1022.4061 | 539.5493 | 702.7677 | 814.7577 | 602.4515 | 670.0545 | 938.2365 | 1033.6728 | 635.6759 | 783.6657 | 850.3602 | 1063.9206 | 1063.5358 | 517.687 | 621.8306 | 705.6236 | 571.4208 | 728.7202 | 879.3163 | 972.5896 | 1083.3787 | 583.1014 | 675.0466 | 654.596 | 842.9835 | 82.7176 | -0.0032751 | 18.2777 | 3.8987 | -39.579 | 3.1233 | 11047.7 | 0.38 | 0.6658 | -1.8174 | -1.2694 | -1.9689 | 6.5701 | 5.6929 | 6.2294 | 76.0335 | 123.8213 | 45.184 | 70.451 | 7.7728 | 37.6721 | 33.9684
42810.4511 | 952 | 17.8093 | 18.1727 | 18.2573 | 18.2861 | 17.5978 | 16.2223 | 14.5967 | 16.5101 | 17.0089 | 17.1301 | 17.1336 | 16.6469 | 15.6636 | 14.3445 | 14.4866 | 19.2778 | 20.8098 | 63.7487 | 25.0849 | 87.024 |  |  |  | 17.6801 | 71.3294 | 260.8639 | 686.2693 | 721.9499 | 696.2604 | 94.9621 | 103.462 | 992.0605 | 90.8901 | 104.1161 | 883.3187 | 649.3411 | 891.2216 | 1223.6702 | 276.1576 | 965.7281 | 963.3046 | 470.5719 | 954.3324 | 375.1389 | 643.6937 | 459.8261 | 626.5046 | 749.0667 | 897.78 | 978.493 | 39.1365 | 366.8183 | 69.7019 | 581.3813 | 13.6248 | 51.8616 | 48.9423 | 49.5155 | 46.4205 |  |  | 0.3958 | -0.36593 | -0.54487 | -0.87593 | 6.0949 | 5.3117 | 7.2479 | -2.6089 | 19.3265 | 46.4036 | 30.2375 | 0.00035484 | 0.00040577 | -0.00084275 | 18.2385 | 16.3815 | 16.9174 | 17.2844 | 17.2508 | 16.2157 | 14.607 | 16.6876 | 17.0453 | 17.3616 | 17.412 | 17.1262 | 16.2984 | 14.5197 | 861.812 | 599.6869 | 578.3076 | 372.5604 | 303.8553 | 808.3351 | 513.8228 | 15.621 | 19.6653 | 23.2966 | 40.3537 | 73.3638 | 80.6943 |  |  |  | 608.4721 | 590.6287 | 591.5341 | 614.2713 | 99.4145 | 46.1073 | 806.87 |  |  | 440.6372 |  |  | 17.714 | 37.15 | 367.8183 | 16.8461 | 33.483 | 906.9225 | 740.1787 | 592.3467 | 799.374 | 798.4294 | 738.091 |  | 797.0682 | 846.3055 | 936.4268 | 574.3244 | 659.1676 | 839.9093 |  | 972.5178 |  |  | 443.138 | 653.0394 | 728.9239 | [6 empty] | 581.5752 |  |  | 390.0904 |  |  | 484.6337 | 645.1174 | 664.03 | 777.5957 | 1008.8422 | 1017.1724 | 539.855 | 703.7872 | 817.1804 | 602.8074 | 672.1112 | 935.2925 | 1033.698 | 636.2692 | 786.1639 | 847.1632 | 1062.5391 | 1061.2089 | 518.1179 | 622.3912 | 706.4817 | 572.6272 | 729.2099 | 880.6998 | 966.3025 | 1079.4988 | 583.7739 | 674.3728 | 655.5253 | 841.6645 | 87.0806 | 0.00023255 | 18.2774 | 3.9254 | -39.6124 | 3.1233 | 11096.25 | 0.36 | 1.3651 | -1.2765 | -1.5576 | -1.9749 | 5.8873 | 5.496 | 6.42 | 76.021 | 123.8749 | 45.1957 | 71.623 | 14.5832 | 46.027 | 34.093
42810.4511 | 953 | 17.799 | 18.164 | 18.2522 | 18.2837 | 17.6063 | 16.219 | 14.601 | 16.5018 | 16.9978 | 17.1244 | 17.1269 | 16.6458 | 15.6604 | 14.3382 | 14.4986 | 19.376 | 20.9174 | 64.4194 | 25.1833 | 87.0944 |  |  |  | 17.7149 | 71.5329 | 259.6792 | 685.5833 | 719.9882 | 696.2711 | 95.7139 | 107.1198 | 1002.8396 | 93.2041 | 105.9788 | 882.3209 | 642.4548 | 889.1967 | 904.5575 | 259.1448 | 967.4481 | 967.0383 | 459.748 | 857.4794 | 374.7152 | 643.2894 | 461.313 | 626.6835 | 749.0084 | 887.2383 | 972.5557 | 38.6585 | 367.6704 | 68.8625 | 581.9486 | 13.6465 | 51.779 | 48.9402 | 49.5135 | 46.7825 |  |  | 0.26438 | -0.91331 | -1.1606 | -0.68011 | 7.0188 | 3.8798 | 6.1873 | -3.4336 | 20.0131 | 48.1892 | 30.1715 | 0.00041891 | 0.00042713 | -0.00085589 | 18.2629 | 16.3722 | 16.9227 | 17.2775 | 17.2553 | 16.2139 | 14.6115 | 16.6853 | 17.0415 | 17.3558 | 17.4121 | 17.1294 | 16.3019 | 14.5218 | 852.0969 | 609.3557 | 589.3331 | 383.8045 | 300.8936 | 807.8561 | 514.1897 | 15.6264 | 19.7369 | 23.3965 | 40.6088 | 73.4934 | 80.7685 |  |  |  | 608.9845 | 589.4434 | 590.9148 | 608.8656 | 92.9849 | 38.2938 | 805.7644 |  |  | 443.3889 |  |  | 17.7138 | 37.2764 | 366.7615 | 16.8516 | 33.6625 | 911.4788 | 742.015 | 593.6347 | 799.8798 | 798.2256 | 741.0651 |  | 797.1783 | 837.9756 | 936.9128 | 575.9344 | 659.5646 | 835.7101 |  | 971.8629 |  |  | 444.0851 | 657.146 | 730.1541 | [6 empty] | 582.9896 |  |  | 391.388 |  |  | 484.7102 | 645.3852 | 665.7274 | 773.7498 | 1004.1415 | 1014.9627 | 540.2314 | 705.1135 | 816.6037 | 603.44 | 673.0042 | 933.3743 | 1038.2839 | 636.9259 | 787.3761 | 846.4091 | 1060.1874 | 1059.4281 | 518.5027 | 622.5044 | 707.4651 | 573.0343 | 729.0829 | 878.7741 | 966.8981 | 1076.4464 | 584.0569 | 674.6148 | 656.0304 | 837.9069 | 89.7458 | -0.0011635 | 18.2778 | 3.9399 | -39.5602 | 3.1232 | 11098.13 | 0.23 | 1.1157 | -2.0162 | -2.2728 | -1.7398 | 6.2893 | 4.676 | 5.905 | 75.9721 | 124.315 | 45.235 | 72.5119 | 13.4394 | 44.924 | 34.3371
42810.4511 | 954 | 17.8126 | 18.1705 | 18.2608 | 18.2884 | 17.6109 | 16.218 | 14.6082 | 16.5066 | 17.008 | 17.1316 | 17.1348 | 16.6555 | 15.669 | 14.3475 | 14.5035 | 19.474 | 21.0106 | 64.9806 | 25.274 | 87.1495 |  |  |  | 17.743 | 71.7126 | 257.3258 | 683.558 | 714.9759 | 694.0006 | 95.287 | 109.1492 | 1010.6597 | 95.5716 | 108.5815 | 881.3356 | 601.2847 | 884.0744 | 896.0585 | 279.4121 | 970.2467 | 971.7705 | 455.3576 | 831.9705 | 374.0443 | 642.8939 | 461.5735 | 624.5908 | 744.2295 | 884.4747 | 972.4817 | 39.2056 | 368.5885 | 68.7529 | 582.6628 | 13.682 | 51.7452 | 48.9368 | 49.5145 | 47.1477 |  |  | 0.092215 | -1.1788 | -1.1928 | -1.5909 | 6.2533 | 6.1948 | 6.577 | -2.2376 | 20.5535 | 51.358 | 29.7499 | 0.00041398 | 0.0003647 | -0.00084275 | 18.2949 | 16.3733 | 16.9216 | 17.2833 | 17.252 | 16.2145 | 14.6121 | 16.6869 | 17.0481 | 17.3627 | 17.4192 | 17.1433 | 16.3071 | 14.5232 | 849.5449 | 587.6144 | 544.8766 | 371.9194 | 292.1282 | 806.8259 | 513.5891 | 15.6331 | 19.8064 | 23.4893 | 40.8347 | 73.6121 | 80.8495 |  |  |  | 609.2835 | 589.315 | 590.2833 | 607.1364 | 108.2243 | 43.1931 | 804.6617 |  |  | 445.2286 |  |  | 17.7301 | 37.4002 | 363.6884 | 16.8505 | 33.8352 | 920.9232 | 744.2794 | 595.3951 | 800.9667 | 798.921 | 745.9969 |  | 797.6485 | 830.89 | 937.899 | 577.8839 | 660.081 | 831.9906 |  | 972.0336 |  |  | 444.8882 | 661.6295 | 733.1832 | [6 empty] | 584.533 |  |  | 392.9831 |  |  | 484.8944 | 646.5635 | 666.4191 | 773.3806 | 1003.1346 | 1018.0788 | 540.4427 | 705.5427 | 815.3864 | 604.1827 | 673.8331 | 934.0811 | 1046.3269 | 637.3791 | 787.5836 | 845.9072 | 1059.5627 | 1058.1517 | 518.7834 | 622.7197 | 707.7093 | 573.7248 | 729.1914 | 879.1648 | 966.4911 | 1077.5865 | 584.2572 | 674.5622 | 656.5272 | 836.9639 | 86.3 | 0.0012287 | 18.2759 | 3.9468 | -39.6712 | 3.1232 | 11082.72 | 0.36 | 0.65813 | -2.29 | -2.3036 | -2.6604 | 5.9293 | 5.9015 | 6.0808 | 75.979 | 124.936 | 45.2903 | 72.3863 | 18.2459 | 37.2042 | 34.44
42810.4511 | 955 | 17.8061 | 18.1721 | 18.2602 | 18.28 | 17.6032 | 16.2277 | 14.6124 | 16.5114 | 17.0101 | 17.1274 | 17.1328 | 16.6581 | 15.6709 | 14.3492 | 14.51 | 19.5637 | 21.0884 | 65.5384 | 25.3579 | 87.1995 |  |  |  | 17.7537 | 71.8845 | 255.3497 | 682.2764 | 712.376 | 692.3053 | 94.3071 | 107.7828 | 1030.1626 | 95.3579 | 108.4911 | 877.6863 | 519.1152 | 879.7027 | 1156.6807 | 282.9543 | 981.2364 | 980.5187 | 474.184 | 611.1865 | 373.3716 | 642.3393 | 461.1762 | 623.9393 | 741.6775 | 892.9121 | 973.7775 | 39.9796 | 369.3639 | 68.4177 | 583.2204 | 13.7198 | 51.7472 | 48.9285 | 49.5214 | 47.5426 |  |  | 0.12507 | -0.034741 | -0.78932 | -1.328 | 6.7533 | 4.8675 | 6.6742 | -2.4551 | 20.4157 | 50.235 | 30.6263 | 0.0003762 | 0.00035649 | -0.00083125 | 18.3225 | 16.3735 | 16.9191 | 17.2801 | 17.2544 | 16.2226 | 14.6132 | 16.6862 | 17.0481 | 17.3597 | 17.4172 | 17.1405 | 16.3068 | 14.5271 | 852.4289 | 591.7433 | 577.8281 | 365.5002 | 285.5769 | 807.5507 | 513.9223 | 15.6343 | 19.8735 | 23.5851 | 41.0546 | 73.7265 | 80.934 |  |  |  | 609.8108 | 591.8307 | 591.7315 | 609.9302 | 101.9569 | 44.5763 | 804.7287 |  |  | 446.8007 |  |  | 17.744 | 37.5322 | 360.3279 | 16.8347 | 34.0093 | 935.316 | 744.5356 | 597.5909 | 801.9816 | 799.6645 | 746.11 |  | 798.0781 | 828.4348 | 938.8933 | 580.5083 | 660.6933 | 831.7408 |  | 972.4313 |  |  | 444.9083 | 662.2758 | 734.4832 | [6 empty] | 587.1668 |  |  | 395.6558 |  |  | 485.3195 | 647.8713 | 667.0438 | 777.1583 | 1007.1787 | 1019.7756 | 540.6119 | 706.4787 | 814.4275 | 605.2518 | 674.0494 | 936.0505 | 1050.0343 | 637.7558 | 789.6829 | 843.4161 | 1060.5884 | 1059.1306 | 518.9951 | 622.6292 | 709.2585 | 575.0703 | 729.548 | 879.5604 | 968.3719 | 1079.7834 | 583.7805 | 675.8728 | 657.1327 | 834.4818 | 84.5437 | -0.001837 | 18.2769 | 3.9497 | -39.6596 | 3.1232 | 11053.33 | 0.27 | 0.76579 | -0.39302 | -1.8734 | -2.43 | 6.1843 | 5.2502 | 6.1479 | 76.1075 | 125.4329 | 45.3474 | 72.3536 | 14.6585 | 23.5872 | 34.4593
42810.4511 | 956 | 17.8016 | 18.1652 | 18.2548 | 18.2822 | 17.6046 | 16.2259 | 14.6065 | 16.5072 | 17.0077 | 17.1262 | 17.1388 | 16.6512 | 15.6661 | 14.3508 | 14.5119 | 19.6615 | 21.1815 | 66.1052 | 25.466 | 87.24 |  |  |  | 17.783 | 72.0436 | 256.0354 | 680.8557 | 712.2599 | 690.6618 | 91.7379 | 106.4538 | 1048.7331 | 94.8875 | 108.499 | 880.4123 | 530.015 | 884.3353 | 1114.833 | 276.1349 | 1001.2518 | 1000.2806 | 499.2741 | 1058.6363 | 374.9885 | 642.6393 | 461.7893 | 624.6846 | 742.1914 | 896.912 | 975.3703 | 41.0531 | 370.2246 | 68.1515 | 583.7905 | 13.7545 | 51.7465 | 48.9147 | 49.5219 | 47.9793 |  |  | -0.024093 | 0.54155 | -0.47784 | -1.2387 | 7.3303 | 5.5699 | 6.573 | -1.7356 | 20.7234 | 50.6088 | 29.6779 | 0.00030063 | 0.00036141 | -0.00082961 | 18.3469 | 16.3735 | 16.9168 | 17.2846 | 17.2545 | 16.2209 | 14.617 | 16.6884 | 17.0515 | 17.3656 | 17.4145 | 17.1396 | 16.3057 | 14.5298 | 856.7868 | 597.5391 | 588.8578 | 361.363 | 277.1449 | 808.0583 | 514.2963 | 15.6416 | 19.9505 | 23.6767 | 41.2911 | 73.851 | 81.0048 |  |  |  | 610.5301 | 595.3505 | 593.8822 | 613.3543 | 105.0656 | 53.3623 | 805.2262 |  |  | 447.1823 |  |  | 17.7464 | 37.6508 | 360.4539 | 16.8518 | 34.1774 | 956.4746 | 744.118 | 599.4634 | 801.4381 | 798.5967 | 742.9193 |  | 798.4903 | 826.2433 | 939.5975 | 582.947 | 661.3032 | 831.4799 |  | 972.4617 |  |  | 444.7292 | 659.4665 | 733.6743 | [6 empty] | 589.6038 |  |  | 398.0736 |  |  | 485.6781 | 648.8061 | 668.0642 | 780.9434 | 1010.6873 | 1018.9452 | 540.6635 | 707.6144 | 812.7195 | 606.0125 | 674.1302 | 939.832 | 1048.5799 | 637.9728 | 789.8794 | 844.7279 | 1062.0229 | 1060.8517 | 518.301 | 622.2208 | 710.4436 | 576.9531 | 729.9747 | 880.5852 | 974.1807 | 1083.9717 | 583.8638 | 676.5308 | 658.3795 | 834.0826 | 88.7372 | -0.00013927 | 18.2774 | 3.9515 | -39.6874 | 3.1232 | 11041.82 | 0.34 | -0.33582 | 1.552 | -1.4578 | -2.3472 | 6.454 | 5.6259 | 6.1116 | 76.3226 | 125.7979 | 45.4094 | 72.0712 | 13.5159 | 24.4479 | 34.4966
42810.4511 | 957 | 17.8032 | 18.1677 | 18.2589 | 18.2874 | 17.607 | 16.2216 | 14.6102 | 16.5134 | 17.0106 | 17.1294 | 17.1361 | 16.6498 | 15.6701 | 14.3554 | 14.5237 | 19.7694 | 21.2803 | 66.627 | 25.5077 | 87.2997 |  |  |  | 17.813 | 72.2138 | 257.7821 | 680.143 | 711.004 | 690.7389 | 92.6602 | 108.5253 | 1079.5207 | 96.6701 | 109.9555 | 887.0315 | 634.6398 | 894.2828 | 588.1577 | 255.3458 | 1010.6623 | 1007.9986 | 512.5251 |  | 376.184 | 643.2304 | 462.7289 | 624.7342 | 745.545 | 899.7314 | 978.9161 | 41.7736 | 370.8782 | 68.2405 | 584.1935 | 13.7633 | 51.7382 | 48.9016 | 49.5275 | 48.2984 |  |  | 0.10339 | -0.23976 | -0.39833 | -1.4535 | 6.252 | 5.6672 | 6.1696 | -2.3027 | 20.2861 | 49.8298 | 31.0726 | 0.0003072 | 0.00038277 | -0.00083454 | 18.3696 | 16.366 | 16.9103 | 17.2722 | 17.2479 | 16.2163 | 14.6125 | 16.6806 | 17.0496 | 17.3667 | 17.4157 | 17.1316 | 16.2986 | 14.5304 | 852.7422 | 589.8342 | 592.423 | 363.9013 | 292.3812 | 808.3599 | 514.6568 | 15.6526 | 20.0226 | 23.7887 | 41.5452 | 73.9809 | 81.0913 |  |  |  | 611.0902 | 595.9891 | 594.2421 | 612.6439 | 107.4105 | 36.6693 | 804.6692 |  |  | 446.3508 |  |  | 17.7494 | 37.782 | 360.301 | 16.8759 | 34.351 | 975.7655 | 743.8289 | 600.8337 | 801.504 | 798.0199 | 740.827 |  | 798.7315 | 823.2749 | 940.4725 | 584.6907 | 661.7771 | 830.9287 |  | 972.066 |  |  | 444.781 | 656.3659 | 732.4248 | [6 empty] | 591.4895 |  |  | 400.2145 |  |  | 485.8796 | 649.5998 | 668.9068 | 786.2761 | 1009.7469 | 1015.5517 | 540.9275 | 708.5729 | 810.8092 | 606.76 | 674.5716 | 941.8808 | 1042.8409 | 638.4963 | 789.0461 | 846.2812 | 1065.0244 | 1063.9947 | 518.2434 | 622.0296 | 710.408 | 578.5184 | 730.6419 | 881.8057 | 977.3003 | 1088.9617 | 584.248 | 675.582 | 659.7673 | 836.4337 | 84.5857 | -0.00084081 | 18.2782 | 3.952 | -39.6824 | 3.1232 | 11097.11 | 0.28 | 0.69569 | -1.033 | -1.3315 | -2.5434 | 5.9676 | 5.6817 | 5.9282 | 76.4547 | 126.259 | 45.4618 | 72.6407 | 13.1998 | 41.8977 | 34.6197
42810.4511 | 958 | 17.8008 | 18.1675 | 18.2599 | 18.2869 | 17.6032 | 16.2135 | 14.6177 | 16.5063 | 17.0136 | 17.1323 | 17.1356 | 16.6511 | 15.672 | 14.3587 | 14.5375 | 19.867 | 21.3767 | 67.1325 | 25.6134 | 87.3683 |  |  |  | 17.8519 | 72.3858 | 260.4821 | 680.6005 | 710.7612 | 692.4229 | 91.3102 | 108.3623 | 1084.9921 | 95.4133 | 109.8901 | 892.7482 | 706.6591 | 899.9889 | 417.6795 | 257.5176 | 1015.6775 | 1015.7279 | 484.3341 |  | 376.8428 | 644.597 | 463.6852 | 624.2089 | 745.9644 | 903.1344 | 978.1922 | 42.3079 | 371.5332 | 68.2245 | 584.6444 | 13.774 | 51.7266 | 48.8917 | 49.5478 | 48.7771 |  |  | -0.18246 | 1.1875 | -1.0049 | -1.6342 | 5.3977 | 3.9087 | 5.0019 | -2.5544 | 19.9035 | 49.966 | 31.4889 | 0.00031377 | 0.00039263 | -0.00079347 | 18.4045 | 16.3664 | 16.9118 | 17.2723 | 17.2501 | 16.2103 | 14.6027 | 16.6844 | 17.0478 | 17.3608 | 17.4159 | 17.136 | 16.3056 | 14.5327 | 855.7382 | 581.5259 | 574.2493 | 358.9155 | 287.7992 | 808.4748 | 514.2023 | 15.6453 | 20.0959 | 23.8752 | 41.7714 | 74.1024 | 81.1587 |  |  |  | 611.6856 | 597.859 | 595.8256 | 617.1031 | 92.8921 | 34.5468 | 804.4842 |  |  | 443.9799 |  |  | 17.7571 | 37.9197 | 360.7999 | 16.8833 | 34.5141 | 980.4966 | 742.846 | 601.975 | 800.8611 | 796.9035 | 740.4483 |  | 799.0158 | 819.8231 | 940.7161 | 585.9974 | 662.1735 | 829.7335 |  | 971.262 |  |  | 445.2089 | 653.8937 | 731.6398 | [6 empty] | 592.9932 |  |  | 401.8938 |  |  | 486.1596 | 650.4548 | 669.5142 | 793.4024 | 1007.8377 | 1012.6331 | 541.3575 | 709.8544 | 808.5775 | 607.6452 | 674.9757 | 944.1335 | 1041.8335 | 639.8303 | 789.1721 | 844.989 | 1067.5419 | 1064.0023 | 518.9153 | 622.3208 | 712.0628 | 579.6437 | 731.0973 | 881.9538 | 980.5831 | 1090.3826 | 584.6932 | 676.0526 | 660.7853 | 836.6444 | 87.1473 | 0.00019044 | 18.2765 | 3.9464 | -39.5407 | 3.1231 | 11144.94 | 0.28 | -0.92501 | 2.3006 | -2.1163 | -2.6989 | 5.553 | 4.7254 | 5.3455 | 76.5526 | 126.4605 | 45.5101 | 72.3535 | 15.1182 | 58.4332 | 34.6058
42810.4511 | 959 | 17.7962 | 18.1649 | 18.257 | 18.2802 | 17.5983 | 16.2184 | 14.6262 | 16.5114 | 17.0108 | 17.1324 | 17.1289 | 16.6567 | 15.678 | 14.349 | 14.5436 | 19.9705 | 21.477 | 67.6822 | 25.7493 | 87.4443 |  |  |  | 17.8869 | 72.5594 | 262.3481 | 681.0194 | 711.3619 | 692.3056 | 94.4844 | 107.6891 | 1091.7464 | 93.9947 | 108.2245 | 891.3816 | 706.2798 | 896.3656 | 548.3141 | 263.5418 | 1008.0833 | 1009.0027 | 477.0525 | 1151.5642 | 376.8046 | 645.0657 | 463.7201 | 623.8242 | 747.5051 | 905.8322 | 979.6084 | 42.8756 | 372.2396 | 69.1368 | 585.2293 | 13.775 | 51.7331 | 48.8713 | 49.5542 | 49.203 |  |  | -0.15683 | -0.9731 | -0.72689 | -0.88579 | 5.9044 | 4.6605 | 7.0961 | -1.9663 | 20.1324 | 49.7505 | 33.2313 | 0.00034663 | 0.00037456 | -0.00081154 | 18.4378 | 16.3671 | 16.9101 | 17.2691 | 17.2454 | 16.2222 | 14.614 | 16.6864 | 17.0489 | 17.375 | 17.4281 | 17.1396 | 16.3162 | 14.5344 | 847.2536 | 563.0699 | 522.0853 | 352.9395 | 291.0576 | 808.2526 | 513.2678 | 15.6582 | 20.169 | 23.9744 | 42.0104 | 74.2212 | 81.2302 |  |  |  | 612.6314 | 602.2226 | 598.9896 | 622.625 | 117.508 | 45.8463 | 803.2412 |  |  | 442.2566 |  |  | 17.7728 | 38.0433 | 363.0986 | 16.9079 | 34.6814 | 978.8155 | 741.0199 | 603.0481 | 798.6738 | 794.4899 | 737.3762 |  | 798.9647 | 815.3396 | 940.7815 | 587.3679 | 662.6176 | 826.4573 |  | 971.0567 |  |  | 445.4254 | 650.5978 | 730.0933 | [6 empty] | 594.2546 |  |  | 403.1407 |  |  | 486.3915 | 651.1785 | 670.0291 | 798.7775 | 1008.4852 | 1014.0018 | 541.9479 | 712.3449 | 806.7045 | 608.2758 | 675.2476 | 945.8278 | 1044.5519 | 641.5163 | 790.9329 | 843.1089 | 1069.8184 | 1064.2419 | 519.6235 | 622.7743 | 713.5136 | 581.1587 | 731.4201 | 881.4489 | 980.9777 | 1092.881 | 585.2059 | 677.5152 | 661.8343 | 835.9187 | 83.828 | 0.00010628 | 18.2767 | 3.9289 | -39.5995 | 3.1231 | 11209.41 | 0.34 | -0.85754 | -2.0831 | -1.8004 | -1.9875 | 5.8144 | 5.1658 | 6.3743 | 76.6222 | 126.6133 | 45.5668 | 73.2078 | 20.7071 | 58.5441 | 34.6275
42810.4511 | 960 | 17.7973 | 18.172 | 18.2605 | 18.2867 | 17.5971 | 16.2254 | 14.6303 | 16.5186 | 17.0119 | 17.1336 | 17.1353 | 16.6601 | 15.6773 | 14.3533 | 14.5478 | 20.0723 | 21.5694 | 68.2256 | 25.8011 | 87.5131 |  |  |  | 17.9048 | 72.7354 | 260.2468 | 679.0757 | 709.6751 | 689.5858 | 96.4159 | 107.4241 | 1076.4227 | 89.8613 | 104.9584 | 882.1236 | 772.4255 | 883.0883 | 1148.5204 | 267.7357 | 994.5346 | 995.2493 | 485.7523 | 933.4712 | 376.9127 | 644.394 | 463.5317 | 622.0209 | 751.0912 | 901.4254 | 980.4484 | 43.2808 | 372.8434 | 70.1209 | 585.82 | 13.7807 | 51.7749 | 48.8642 | 49.567 | 49.6212 |  |  | -0.145 | -0.51706 | -1.0929 | -0.91931 | 6.6771 | 3.8266 | 5.6182 | -1.9235 | 20.1944 | 49.6654 | 33.6162 | 0.00037456 | 0.00040577 | -0.00083946 | 18.4562 | 16.3576 | 16.8992 | 17.2598 | 17.2398 | 16.2008 | 14.6002 | 16.677 | 17.0388 | 17.3528 | 17.4079 | 17.1321 | 16.2989 | 14.5232 | 863.6681 | 579.3296 | 554.7513 | 354.2009 | 303.3488 | 810.0441 | 513.5094 | 15.6614 | 20.2441 | 24.0791 | 42.2451 | 74.3361 | 81.3064 |  |  |  | 613.3722 | 603.3452 | 600.0633 | 620.5788 | 122.1192 | 44.1956 | 800.8536 |  |  | 442.1597 |  |  | 17.7768 | 38.1638 | 360.8319 | 16.9028 | 34.8566 | 965.5204 | 740.9856 | 604.2468 | 797.2728 | 792.6542 | 737.2402 |  | 799.0602 | 812.1618 | 941.6079 | 588.6768 | 663.0582 | 824.5087 |  | 971.3459 |  |  | 446.0673 | 650.001 | 729.1175 | [6 empty] | 595.5937 |  |  | 404.7398 |  |  | 486.4675 | 651.7664 | 670.5534 | 801.0576 | 1009.435 | 1015.8228 | 542.6145 | 714.943 | 806.302 | 608.8842 | 675.895 | 947.4625 | 1049.4392 | 642.7976 | 792.6696 | 840.3144 | 1069.9998 | 1066.491 | 520.2441 | 623.1942 | 712.2717 | 583.0091 | 731.8563 | 878.8261 | 981.2123 | 1094.936 | 585.7944 | 677.8593 | 663.3476 | 834.8693 | 85.149 | -0.0015213 | 18.2781 | 3.9181 | -39.6491 | 3.1231 | 11244.42 | 0.36 | -0.8234 | -1.5179 | -2.2068 | -2.024 | 6.1717 | 4.6721 | 5.6612 | 76.6554 | 127.0602 | 45.6246 | 72.0981 | 17.1311 | 75.728 | 34.8219
42810.4512 | 961 | 17.7824 | 18.1598 | 18.2535 | 18.2778 | 17.5998 | 16.2182 | 14.6271 | 16.5149 | 17.0134 | 17.1267 | 17.1389 | 16.6522 | 15.6681 | 14.3574 | 14.5661 | 20.1723 | 21.6643 | 68.761 | 25.8633 | 87.551 |  |  |  | 17.9408 | 72.9083 | 256.1164 | 676.0736 | 707.7385 | 686.0838 | 92.87 | 109.1629 | 1057.8658 | 92.7554 | 103.1165 | 876.0799 | 833.4002 | 878.8629 |  | 279.6654 | 984.1871 | 986.5904 | 493.7929 | 1109.6983 | 376.6127 | 643.3845 | 463.8477 | 621.8291 | 744.7718 | 890.2014 | 979.8388 | 44.0278 | 373.4544 | 71.2068 | 586.5602 | 13.7926 | 51.843 | 48.835 | 49.5729 | 49.9726 |  |  | 0.12442 | -0.75757 | -0.69601 | -1.0737 | 6.1987 | 4.1328 | 7.0376 | -2.9197 | 19.9837 | 49.0911 | 31.6677 | 0.00034992 | 0.00032035 | -0.00081811 | 18.4946 | 16.365 | 16.9025 | 17.2631 | 17.2375 | 16.203 | 14.601 | 16.6799 | 17.0487 | 17.3606 | 17.4141 | 17.1383 | 16.311 | 14.5337 | 876.2925 | 595.3604 | 573.3163 | 356.8821 | 298.5664 | 811.819 | 513.8956 | 15.6691 | 20.3236 | 24.1715 | 42.4834 | 74.4483 | 81.3834 |  |  |  | 613.7517 | 600.8899 | 598.6586 | 614.8981 | 121.2576 | 43.7857 | 799.0524 |  |  | 440.9446 |  |  | 17.7849 | 38.2933 | 356.3889 | 16.9033 | 35.0299 | 948.9553 | 743.2557 | 605.5639 | 796.6283 | 792.023 | 741.5407 |  | 799.3171 | 809.4508 | 942.8981 | 590.4119 | 663.5592 | 822.2375 |  | 971.4147 |  |  | 447.0217 | 653.2454 | 730.713 | [6 empty] | 597.1996 |  |  | 406.3958 |  |  | 486.9663 | 652.4376 | 670.7111 | 803.5765 | 1017.0539 | 1016.17 | 543.0333 | 716.8215 | 806.0679 | 609.8392 | 676.6894 | 950.8279 | 1056.2517 | 643.6722 | 793.4696 | 840.8485 | 1066.8519 | 1064.9587 | 520.983 | 623.3539 | 709.5999 | 585.391 | 732.1367 | 877.2308 | 979.327 | 1093.0174 | 586.1067 | 676.6091 | 664.8397 | 836.6156 | 88.9053 | 0.0054379 | 18.2779 | 3.9056 | -39.6289 | 3.1231 | 11284.36 | 0.4 | 0.76132 | -1.8363 | -1.7601 | -2.1862 | 5.918 | 4.8322 | 6.3057 | 76.6149 | 127.6967 | 45.6837 | 71.4055 | 15.1539 | 94.443 | 35.0502
42810.4512 | 962 | 17.7874 | 18.1516 | 18.2405 | 18.2728 | 17.5892 | 16.2069 | 14.6164 | 16.5069 | 17.0125 | 17.1294 | 17.1353 | 16.6422 | 15.6641 | 14.3467 | 14.5752 | 20.2774 | 21.767 | 69.2857 | 25.9717 | 87.6035 |  |  |  | 17.9747 | 73.0645 | 258.1798 | 675.3282 | 708.4556 | 686.0129 | 92.7689 | 109.1047 | 1056.1281 | 97.4187 | 110.3018 | 885.411 | 770.409 | 886.7475 | 1249.3265 | 291.4753 | 980.0641 | 981.9984 | 496.4606 | 1335.6573 | 376.6766 | 642.3689 | 464.1478 | 621.254 | 741.8229 | 884.1692 | 978.0791 | 44.4325 | 373.8359 | 71.2704 | 587.2387 | 13.7942 | 51.886 | 48.7919 | 49.5854 | 50.2568 |  |  | 0.29526 | -0.44347 | -0.85437 | -0.87856 | 5.2282 | 4.3023 | 7.3695 | -2.2238 | 20.0695 | 48.651 | 30.9778 | 0.00031542 | 0.00039098 | -0.00081646 | 18.5264 | 16.3674 | 16.9086 | 17.267 | 17.246 | 16.2031 | 14.6084 | 16.6951 | 17.051 | 17.3711 | 17.428 | 17.1414 | 16.3211 | 14.5403 | 883.8169 | 597.6213 | 529.2509 | 340.1276 | 283.5332 | 813.3441 | 513.5756 | 15.68 | 20.4122 | 24.2783 | 42.7438 | 74.5784 | 81.4503 |  |  |  | 613.8871 | 598.4493 | 596.8599 | 610.5999 | 85.9373 | 26.1243 | 797.8735 |  |  | 442.4317 |  |  | 17.8048 | 38.4246 | 357.7034 | 16.9214 | 35.213 | 945.0173 | 745.8107 | 606.5274 | 796.5833 | 792.4482 | 745.3468 |  | 799.7067 | 808.0378 | 943.071 | 591.5155 | 664.0592 | 820.4849 |  | 972.1272 |  |  | 447.3086 | 656.8215 | 733.4681 | [6 empty] | 598.2922 |  |  | 407.6943 |  |  | 487.1159 | 653.1197 | 669.8216 | 806.898 | 1021.9117 | 1020.7259 | 543.2067 | 718.337 | 806.3412 | 610.666 | 676.6561 | 953.7586 | 1064.946 | 644.3663 | 794.8934 | 843.2699 | 1062.2856 | 1066.6148 | 521.3771 | 623.4862 | 709.1193 | 586.8853 | 733.3931 | 878.4498 | 978.8737 | 1093.1964 | 586.5215 | 676.7513 | 665.8946 | 840.6156 | 87.9876 | 0.0055501 | 18.2765 | 3.8989 | -39.5846 | 3.123 | 11286.19 | 0.36 | 1.1728 | -1.4042 | -1.9491 | -1.9765 | 5.4209 | 4.9175 | 6.4359 | 76.629 | 127.8113 | 45.7602 | 71.1816 | 19.9791 | 74.8533 | 35.1948
42810.4512 | 963 | 17.7863 | 18.1479 | 18.2464 | 18.2674 | 17.591 | 16.2054 | 14.6232 | 16.498 | 16.9978 | 17.1201 | 17.1293 | 16.6518 | 15.6625 | 14.3428 | 14.5853 | 20.3948 | 21.871 | 69.821 | 26.051 | 87.6916 |  |  |  | 18.0209 | 73.216 | 265.8307 | 675.4588 | 709.9884 | 687.2629 | 93.4934 | 108.2016 | 1047.7453 | 93.1299 | 110.1753 | 887.9274 | 695.5921 | 889.5778 | 1253.6297 | 288.8362 | 975.0553 | 977.734 | 528.4946 |  | 377.3905 | 642.2633 | 463.5359 | 620.7683 | 737.8601 | 885.6432 | 980.3149 | 44.064 | 374.1713 | 70.5849 | 587.776 | 13.7784 | 51.8821 | 48.7506 | 49.6118 | 50.6547 |  |  | 0.20458 | -0.65834 | -1.0009 | -1.217 | 5.7052 | 5.1842 | 6.8214 | -2.2942 | 21.2394 | 50.9516 | 30.769 | 0.00031542 | 0.00036141 | -0.00082468 | 18.5515 | 16.3647 | 16.9038 | 17.2606 | 17.2413 | 16.2091 | 14.6144 | 16.6919 | 17.0451 | 17.3721 | 17.4241 | 17.138 | 16.3143 | 14.541 | 832.8242 | 552.7057 | 456.554 | 322.5724 | 266.9298 | 812.3375 | 511.6809 | 15.6888 | 20.4839 | 24.379 | 42.9749 | 74.6871 | 81.5157 |  |  |  | 614.1953 | 598.9043 | 596.5553 | 611.3668 | 107.6007 | 38.7297 | 797.5412 |  |  | 446.4728 |  |  | 17.8095 | 38.549 | 362.9503 | 16.9176 | 35.387 | 941.8247 | 747.8873 | 607.4205 | 797.1812 | 793.2883 | 747.8146 |  | 800.3374 | 807.7598 | 943.551 | 592.4179 | 664.6279 | 819.1389 |  | 973.3511 |  |  | 447.8 | 660.5512 | 736.3565 | [6 empty] | 599.1268 |  |  | 408.5185 |  |  | 487.224 | 653.5417 | 669.6707 | 809.686 | 1029.0351 | 1025.9907 | 543.8145 | 719.8013 | 807.5015 | 610.9878 | 676.4122 | 954.9929 | 1068.2713 | 644.9558 | 797.1756 | 847.5011 | 1061.0436 | 1069.4733 | 522.0085 | 623.9272 | 709.11 | 587.6395 | 734.4188 | 880.3788 | 981.1496 | 1097.8979 | 586.6054 | 676.6604 | 666.452 | 841.2736 | 91.0859 | -0.001381 | 18.2766 | 3.8968 | -39.6389 | 3.1231 | 11291.42 | 0.33 | 0.97686 | -1.7108 | -2.1095 | -2.326 | 5.6664 | 5.4014 | 6.1959 | 76.7548 | 128.0283 | 45.8572 | 76.4432 | 27.6375 | 54.5778 | 35.2309
42810.4512 | 964 | 17.7815 | 18.1547 | 18.2543 | 18.2829 | 17.5979 | 16.2194 | 14.6364 | 16.5102 | 17.0118 | 17.1257 | 17.1351 | 16.6557 | 15.6685 | 14.3636 | 14.5986 | 20.4899 | 21.9605 | 70.2676 | 26.1411 | 87.7459 |  |  |  | 18.0516 | 73.3566 | 266.7921 | 676.6653 | 711.5178 | 689.5611 | 87.914 | 105.5356 | 1036.8953 | 89.9679 | 103.434 | 882.5268 | 808.7368 | 889.2201 |  | 253.5955 | 974.3123 | 973.5832 | 529.5931 |  | 377.9297 | 641.238 | 463.4596 | 619.9161 | 741.1532 | 894.003 | 982.3372 | 44.9977 | 374.7966 | 70.718 | 588.3829 | 13.7726 | 51.8819 | 48.7003 | 49.6211 | 51.0156 |  |  | 0.21181 | -0.59 | -0.88526 | -1.0323 | 6.7954 | 5.2203 | 6.6959 | -2.8054 | 21.7234 | 53.1707 | 31.3025 | 0.00034827 | 0.00032692 | -0.00085425 | 18.5781 | 16.3612 | 16.8928 | 17.2548 | 17.2384 | 16.2085 | 14.6108 | 16.6805 | 17.0441 | 17.3652 | 17.4146 | 17.1345 | 16.3105 | 14.5392 | 826.8208 | 556.8112 | 472.7033 | 324.692 | 271.0099 | 812.9377 | 511.1198 | 15.697 | 20.563 | 24.4828 | 43.2068 | 74.7961 | 81.5795 |  |  |  | 614.4758 | 597.6606 | 595.9474 | 609.9264 | 116.7892 | 47.5186 | 798.1947 |  |  | 448.4764 |  |  | 17.8127 | 38.6689 | 365.8279 | 16.9265 | 35.5463 | 937.6649 | 749.9784 | 608.4503 | 799.8299 | 797.1497 | 750.177 |  | 801.0122 | 812.3166 | 944.4017 | 593.4604 | 665.2114 | 820.6115 |  | 973.7787 |  |  | 448.2454 | 664.421 | 739.0151 | [6 empty] | 600.226 |  |  | 408.6387 |  |  | 487.5912 | 654.0551 | 671.0632 | 812.7092 | 1028.6989 | 1025.872 | 544.8865 | 721.5978 | 809.2228 | 610.962 | 677.4953 | 953.0686 | 1061.9508 | 645.4456 | 800.9461 | 848.0985 | 1065.0888 | 1072.1232 | 522.4094 | 623.5407 | 708.6665 | 588.6518 | 735.2402 | 880.9802 | 984.489 | 1101.0235 | 586.1512 | 678.1291 | 667.4156 | 839.9105 | 88.2297 | -0.0015564 | 18.2776 | 3.896 | -39.5875 | 3.123 | 11295.84 | 0.35 | 0.99515 | -1.6187 | -1.9827 | -2.1411 | 6.2064 | 5.4398 | 6.1608 | 76.8974 | 128.2732 | 45.9537 | 77.3512 | 25.7194 | 85.4342 | 35.3231
42810.4512 | 965 | 17.7797 | 18.1562 | 18.2419 | 18.2768 | 17.5921 | 16.2205 | 14.6372 | 16.509 | 17.0116 | 17.1266 | 17.1339 | 16.6595 | 15.6685 | 14.3602 | 14.6048 | 20.6028 | 22.0657 | 70.7498 | 26.1716 | 87.807 |  |  |  | 18.0904 | 73.5408 | 261.1336 | 677.402 | 710.6883 | 689.4996 | 81.2872 | 102.3756 | 1043.5451 | 92.2113 | 105.9716 | 884.89 | 806.4413 | 886.1578 |  | 249.7542 | 986.1198 | 989.8355 | 482.9048 |  | 379.0741 | 640.3812 | 464.5527 | 621.6718 | 742.8774 | 898.3553 | 982.2146 | 46.5139 | 375.4587 | 73.23 | 589.2406 | 13.7676 | 51.9312 | 48.6765 | 49.6396 | 51.4403 |  |  | 0.006135 | -1.0092 | -1.3025 | -1.0908 | 5.7072 | 4.6782 | 6.5021 | -2.0727 | 21.0676 | 53.7823 | 34.1286 | 0.00040084 | 0.00037784 | -0.00083289 | 18.6163 | 16.3542 | 16.8973 | 17.2675 | 17.2347 | 16.2086 | 14.6074 | 16.6885 | 17.0459 | 17.3627 | 17.4261 | 17.1416 | 16.3108 | 14.5312 | 847.0614 | 581.3426 | 537.3207 | 347.5132 | 284.1448 | 814.4731 | 511.3952 | 15.697 | 20.6288 | 24.5684 | 43.4291 | 74.8924 | 81.6257 |  |  |  | 614.7171 | 596.7543 | 596.1432 | 609.4594 | 120.6868 | 54.3091 | 801.6317 |  |  | 446.1062 |  |  | 17.8206 | 38.7963 | 362.4925 | 16.9389 | 35.7174 | 941.7632 | 750.4252 | 609.0503 | 803.6165 | 802.239 | 750.6843 |  | 801.6834 | 824.8944 | 946.0709 | 594.3509 | 665.7347 | 827.5973 |  | 974.3852 |  |  | 448.7528 | 665.5541 | 740.9601 | [6 empty] | 600.8496 |  |  | 409.0441 |  |  | 487.6323 | 654.4439 | 672.1783 | 817.6838 | 1024.8518 | 1025.0506 | 545.5908 | 723.2285 | 810.7258 | 611.1501 | 679.8062 | 954.6629 | 1058.3114 | 645.7574 | 802.4603 | 848.5817 | 1069.0268 | 1073.7931 | 522.508 | 623.4371 | 710.0793 | 589.9316 | 737.2188 | 881.9843 | 987.4072 | 1104.8698 | 586.1159 | 679.7525 | 668.3427 | 840.7548 | 83.9264 | 0.0003939 | 18.2773 | 3.8964 | -39.5459 | 3.123 | 11332.41 | 0.3 | 0.16936 | -2.1161 | -2.4039 | -2.1999 | 5.6984 | 5.1592 | 6.0823 | 77.0908 | 128.6549 | 46.0416 | 75.7199 | 18.6004 | 86.0101 | 35.3811
42810.4512 | 966 | 17.7671 | 18.1424 | 18.2357 | 18.2632 | 17.5871 | 16.2071 | 14.6316 | 16.5014 | 17.0064 | 17.125 | 17.1255 | 16.6467 | 15.6612 | 14.3503 | 14.6206 | 20.7233 | 22.1744 | 71.2681 | 26.1869 | 87.8712 |  |  |  | 18.1342 | 73.6963 | 262.3173 | 677.153 | 710.7201 | 691.0675 | 89.908 | 104.5506 | 1058.0428 | 92.7993 | 107.7473 | 884.5552 | 702.1495 | 886.146 |  | 245.7801 | 990.8102 | 994.8518 | 464.7116 |  | 379.9846 | 639.5052 | 464.81 | 622.1401 | 739.1284 | 900.0126 | 987.8022 | 48.6123 | 376.1875 | 74.9837 | 590.5114 | 13.7462 | 51.9666 | 48.6403 | 49.6515 | 51.8929 |  |  | 0.035703 | -0.88111 | -0.2242 | -0.72349 | 5.5758 | 5.6842 | 7.1736 | -2.1226 | 20.6074 | 54.0435 | 34.736 | 0.00027106 | 0.00034827 | -0.00083946 | 18.6429 | 16.3597 | 16.8982 | 17.2504 | 17.2392 | 16.1989 | 14.6076 | 16.6799 | 17.0379 | 17.3621 | 17.4185 | 17.1387 | 16.3244 | 14.534 | 876.3124 | 568.2182 | 588.2396 | 369.2007 | 296.6366 | 816.2414 | 512.2383 | 15.6902 | 20.7018 | 24.6712 | 43.6799 | 75.0076 | 81.6882 |  |  |  | 615.2791 | 598.2694 | 597.4822 | 613.6865 | 119.4599 | 48.4606 | 806.9814 |  |  | 446.3028 |  |  | 17.8284 | 38.9238 | 360.9468 | 16.9464 | 35.8899 | 952.595 | 749.0717 | 609.7661 | 807.5725 | 807.2652 | 748.4801 |  | 801.8637 | 839.4812 | 947.9777 | 594.9841 | 666.3598 | 838.8262 |  | 975.1561 |  |  | 448.8752 | 664.7508 | 739.6024 | [6 empty] | 601.5456 |  |  | 409.6313 |  |  | 487.7834 | 655.0554 | 671.9024 | 821.3036 | 1023.8975 | 1027.8014 | 546.1618 | 724.1296 | 811.5447 | 611.3704 | 680.5309 | 958.3881 | 1058.3628 | 645.7967 | 800.4601 | 848.7142 | 1073.3293 | 1077.2681 | 523.3344 | 623.6723 | 711.0194 | 591.3115 | 738.23 | 882.358 | 987.6942 | 1108.3795 | 586.2038 | 679.7073 | 669.4239 | 838.6623 | 85.2494 | -0.00022343 | 18.2766 | 3.897 | -39.617 | 3.123 | 11383.53 | 0.46 | 0.40889 | -1.9762 | -0.99686 | -1.7908 | 5.6364 | 5.6909 | 6.3932 | 77.2078 | 129.0883 | 46.1589 | 73.1835 | 13.1289 | 57.8976 | 35.3686
42810.4512 | 967 | 17.7666 | 18.1375 | 18.2382 | 18.266 | 17.588 | 16.2132 | 14.6374 | 16.4985 | 17.004 | 17.1247 | 17.1302 | 16.6451 | 15.6715 | 14.3592 | 14.6412 | 20.84 | 22.2827 | 71.7355 | 26.3192 | 87.943 |  |  |  | 18.1704 | 73.8723 | 262.4169 | 676.2953 | 710.601 | 687.6655 | 96.2858 | 108.2808 | 1068.4758 | 94.459 | 108.1394 | 883.2233 | 681.1039 | 883.8216 | 1204.7484 | 245.4666 | 994.9303 | 997.5874 | 479.4416 |  | 380.8955 | 640.9162 | 465.2503 | 622.6339 | 741.6196 | 903.0892 | 990.2718 | 48.8235 | 376.8013 | 74.8095 | 591.2511 | 13.7281 | 51.9453 | 48.6202 | 49.6645 | 52.2972 |  |  | -0.22714 | -0.97705 | -0.28071 | -1.104 | 6.3295 | 5.0035 | 6.7097 | -3.4829 | 21.876 | 52.329 | 32.8019 | 0.00035156 | 0.00034992 | -0.00079839 | 18.6804 | 16.3573 | 16.8883 | 17.2616 | 17.2329 | 16.2035 | 14.6104 | 16.677 | 17.0406 | 17.3623 | 17.4167 | 17.1342 | 16.3109 | 14.5357 | 886.2568 | 596.8137 | 604.2868 | 377.2662 | 285.4036 | 818.334 | 513.1714 | 15.7137 | 20.8026 | 24.8008 | 43.9545 | 75.1324 | 81.7637 |  |  |  | 615.8267 | 598.7105 | 597.4085 | 613.883 | 106.9947 | 54.6526 | 812.0534 |  |  | 448.7006 |  |  | 17.8433 | 39.0519 | 360.0356 | 16.9572 | 36.0601 | 958.1406 | 747.4759 | 610.28 | 808.8135 | 808.8922 | 746.6245 |  | 801.8831 | 846.3364 | 948.0438 | 595.5984 | 666.9214 | 849.0755 |  | 975.391 |  |  | 448.8239 | 664.4635 | 737.7968 | [6 empty] | 602.2196 |  |  | 410.1363 |  |  | 487.5673 | 655.8403 | 672.5373 | 825.7467 | 1025.4019 | 1026.7521 | 546.6283 | 723.9739 | 811.4439 | 611.7062 | 681.5973 | 961.8785 | 1064.6227 | 646.0652 | 799.3592 | 848.8706 | 1076.8215 | 1078.2586 | 523.616 | 623.7172 | 711.0527 | 592.4128 | 738.2767 | 882.0451 | 989.7875 | 1108.183 | 586.192 | 679.7097 | 670.2223 | 834.6969 | 84.5932 | -0.00071451 | 18.2759 | 3.8975 | -39.6095 | 3.123 | 11435.42 | 0.32 | -1.0295 | -2.0826 | -1.1163 | -2.2138 | 6.0131 | 5.3463 | 6.1911 | 77.2654 | 128.9271 | 46.2631 | 72.9265 | 11.5523 | 52.617 | 35.4655
42810.4512 | 968 | 17.761 | 18.1499 | 18.2401 | 18.2664 | 17.5917 | 16.2111 | 14.6348 | 16.5023 | 17.0024 | 17.1179 | 17.1301 | 16.6494 | 15.675 | 14.3541 | 14.645 | 20.947 | 22.3718 | 72.1372 | 26.4124 | 87.9874 |  |  |  | 18.2064 | 74.0431 | 261.0848 | 674.3678 | 709.6568 | 683.748 | 95.3224 | 110.6459 | 1077.7625 | 94.1003 | 107.2379 | 879.2191 | 744.0325 | 879.1738 | 1025.8778 | 245.5372 | 998.0725 | 1000.114 | 483.3935 |  | 382.1931 | 643.3561 | 465.3202 | 622.0986 | 744.6092 | 903.5089 | 991.049 | 47.4292 | 377.2884 | 75.301 | 591.7098 | 13.7011 | 51.9055 | 48.5897 | 49.6712 | 52.5803 |  |  | -0.20874 | -1.3621 | -0.59744 | -0.61637 | 5.0264 | 5.4418 | 6.849 | -2.4755 | 20.8919 | 52.1941 | 31.5984 | 0.00032692 | 0.00031542 | -0.00084932 | 18.708 | 16.3584 | 16.8883 | 17.257 | 17.2305 | 16.2079 | 14.6157 | 16.6728 | 17.0488 | 17.3611 | 17.4181 | 17.1395 | 16.3147 | 14.5443 | 868.6235 | 609.1339 | 614.3261 | 371.6062 | 278.883 | 818.708 | 514.2635 | 15.7212 | 20.8769 | 24.8857 | 44.1904 | 75.2351 | 81.8268 |  |  |  | 616.1496 | 597.7943 | 596.3242 | 612.3678 | 103.3747 | 52.2485 | 813.6677 |  |  | 451.5795 |  |  | 17.8496 | 39.1833 | 357.6221 | 16.9646 | 36.2457 | 959.7604 | 746.3608 | 610.0689 | 808.2606 | 807.7304 | 745.9376 |  | 801.8184 | 845.2708 | 947.8564 | 595.4849 | 667.3653 | 853.5211 |  | 976.2181 |  |  | 449.0955 | 663.9924 | 736.7773 | [6 empty] | 602.0905 |  |  | 410.4813 |  |  | 487.5475 | 656.2995 | 672.3926 | 828.6605 | 1026.6662 | 1029.0259 | 546.8165 | 723.4484 | 809.3237 | 611.9584 | 681.1877 | 963.6439 | 1066.2897 | 646.0225 | 798.6446 | 848.1895 | 1079.5899 | 1077.5708 | 523.4451 | 623.5687 | 709.5412 | 592.5806 | 738.5869 | 878.3769 | 992.5594 | 1108.1059 | 586.9368 | 677.6679 | 670.3136 | 832.049 | 85.4526 | -0.0010022 | 18.2769 | 3.9032 | -39.6424 | 3.123 | 11455.9 | 0.38 | -0.98494 | -2.4623 | -1.6307 | -1.6564 | 5.3595 | 5.5765 | 6.2561 | 77.2644 | 128.874 | 46.3623 | 75.0376 | 10.6788 | 67.9385 | 35.568
42810.4512 | 969 | 17.7618 | 18.1462 | 18.2391 | 18.2672 | 17.5878 | 16.2104 | 14.6463 | 16.5015 | 17.0062 | 17.1153 | 17.1318 | 16.6527 | 15.6688 | 14.3547 | 14.6549 | 21.0637 | 22.473 | 72.5261 | 26.4993 | 88.0311 |  |  |  | 18.2482 | 74.1946 | 259.4971 | 671.9475 | 707.6683 | 680.4825 | 93.815 | 110.6021 | 1073.9368 | 96.0374 | 109.4297 | 878.2251 | 696.0527 | 870.8994 | 1322.4586 | 264.9863 | 993.8612 | 996.6888 | 482.463 | 1123.3273 | 383.6265 | 645.2202 | 465.7779 | 622.1183 | 748.8823 | 901.3292 | 985.3921 | 46.8975 | 377.7271 | 76.1687 | 592.2125 | 13.6718 | 51.8888 | 48.5773 | 49.6756 | 53.1249 |  |  | -0.054977 | -1.2386 | -0.80114 | -1.1309 | 4.8832 | 3.5276 | 6.688 | -2.373 | 20.8818 | 51.588 | 31.7168 | 0.0003647 | 0.00037291 | -0.00084932 | 18.7372 | 16.3529 | 16.8896 | 17.257 | 17.2351 | 16.2053 | 14.6129 | 16.6816 | 17.0462 | 17.3598 | 17.4189 | 17.1411 | 16.3108 | 14.544 | 848.0394 | 579.7837 | 606.3601 | 375.6884 | 284.732 | 818.6583 | 515.0724 | 15.7233 | 20.9528 | 24.983 | 44.4366 | 75.3523 | 81.8978 |  |  |  | 616.3147 | 595.9615 | 594.6006 | 609.7271 | 87.7635 | 41.0965 | 812.613 |  |  | 452.6996 |  |  | 17.8543 | 39.2982 | 356.1213 | 16.9721 | 36.4122 | 957.1092 | 746.1764 | 609.5288 | 807.1628 | 806.2514 | 746.2192 |  | 801.656 | 840.621 | 948.3473 | 594.913 | 667.7174 | 850.7721 |  | 977.3955 |  |  | 449.7407 | 665.3785 | 736.6012 | [6 empty] | 601.6538 |  |  | 410.3426 |  |  | 487.4639 | 656.3202 | 671.3315 | 832.083 | 1027.8705 | 1029.7429 | 547.1762 | 722.9425 | 807.7848 | 611.9813 | 679.9401 | 967.1437 | 1067.6202 | 645.9778 | 796.4109 | 850.61 | 1081.2384 | 1076.2197 | 524.1691 | 623.5595 | 707.031 | 592.8655 | 738.9475 | 878.0005 | 996.2039 | 1109.0401 | 587.4749 | 675.8909 | 670.4749 | 830.9889 | 82.4584 | 0.00058329 | 18.2777 | 3.9119 | -39.5507 | 3.123 | 11395.9 | 0.3 | -0.5046 | -2.3504 | -1.8903 | -2.2459 | 5.2777 | 4.4857 | 6.1764 | 77.2064 | 129.2196 | 46.4544 | 77.3046 | 11.7435 | 55.9643 | 35.6723
42810.4513 | 970 | 17.7641 | 18.1359 | 18.2456 | 18.2679 | 17.5903 | 16.2138 | 14.6491 | 16.5127 | 17.0019 | 17.1228 | 17.138 | 16.6547 | 15.6772 | 14.3583 | 14.6759 | 21.1806 | 22.5808 | 72.9257 | 26.6002 | 88.0875 |  |  |  | 18.2938 | 74.3479 | 260.7985 | 671.0271 | 706.9728 | 679.6325 | 92.5806 | 105.5318 | 1057.1592 | 94.2416 | 109.9766 | 875.6858 | 554.1088 | 870.2172 |  | 270.4732 | 983.5949 | 983.0722 | 494.4622 | 1093.9442 | 384.7684 | 645.2663 | 467.831 | 624.9621 | 748.7035 | 899.6544 | 982.1316 | 46.9577 | 378.278 | 75.2739 | 592.7847 | 13.6613 | 51.8993 | 48.5745 | 49.6904 | 53.5169 |  |  | -0.2692 | -1.393 | -1.5529 | -1.6776 | 5.8071 | 4.7879 | 7.0271 | -2.6477 | 21.6586 | 52.8694 | 31.7514 | 0.00028913 | 0.00038113 | -0.00082139 | 18.7747 | 16.3586 | 16.8907 | 17.2629 | 17.2373 | 16.2091 | 14.6141 | 16.6864 | 17.0549 | 17.3645 | 17.4264 | 17.1378 | 16.3172 | 14.5455 | 850.1011 | 554.6896 | 570.5146 | 376.3811 | 287.3633 | 818.0075 | 514.9263 | 15.7332 | 21.0298 | 25.0829 | 44.6788 | 75.4539 | 81.9623 |  |  |  | 616.2928 | 594.1883 | 592.8224 | 606.7844 | 108.062 | 44.582 | 810.7589 |  |  | 452.2835 |  |  | 17.8687 | 39.4312 | 356.9012 | 16.981 | 36.5877 | 945.5397 | 745.2269 | 609.2763 | 806.0296 | 805.269 | 745.1674 |  | 801.4441 | 837.9155 | 948.2649 | 594.6793 | 668.0028 | 848.515 |  | 978.1484 |  |  | 449.8373 | 664.663 | 736.4242 | [6 empty] | 601.4241 |  |  | 410.8268 |  |  | 487.357 | 655.8713 | 670.0214 | 835.8523 | 1028.5431 | 1030.4169 | 547.3084 | 722.1155 | 806.7952 | 611.9296 | 678.7202 | 969.2725 | 1065.0521 | 645.8482 | 794.8414 | 854.2638 | 1084.9347 | 1076.9766 | 524.9497 | 623.5976 | 705.5922 | 593.588 | 739.5363 | 878.6084 | 999.939 | 1110.8408 | 587.9229 | 675.3567 | 671.2461 | 833.2188 | 82.2431 | -0.0019211 | 18.2776 | 3.9303 | -39.6436 | 3.123 | 11348.41 | 0.34 | -1.1161 | -2.4927 | -2.6318 | -2.7355 | 5.7512 | 5.2222 | 6.3266 | 77.17 | 129.2585 | 46.5228 | 76.8112 | 15.6939 | 28.212 | 35.75
42810.4513 | 971 | 17.7602 | 18.1399 | 18.2512 | 18.2725 | 17.5892 | 16.2114 | 14.6465 | 16.5077 | 17.0121 | 17.1235 | 17.1402 | 16.6575 | 15.6846 | 14.3639 | 14.686 | 21.2979 | 22.6964 | 73.3191 | 26.5995 | 88.1416 |  |  |  | 18.3374 | 74.5062 | 258.8521 | 670.7199 | 705.7272 | 678.7588 | 87.7145 | 107.823 | 1041.2154 | 93.2581 | 106.5991 | 876.5829 | 635.8417 | 877.0679 |  | 244.4929 | 976.6002 | 978.1167 | 508.5257 |  | 386.1359 | 644.5645 | 470.2471 | 627.8495 | 750.9755 | 898.0911 | 985.0066 | 45.6541 | 379.0975 | 74.2272 | 593.4316 | 13.6528 | 51.916 | 48.5754 | 49.6872 | 53.8725 |  |  | 0.1737 | -0.82722 | -1.0206 | -0.83388 | 4.9075 | 4.6572 | 7.6625 | -2.0438 | 21.4862 | 52.6378 | 31.7271 | 0.00034992 | 0.00032035 | -0.00078854 | 18.8027 | 16.3488 | 16.8894 | 17.259 | 17.2324 | 16.1984 | 14.6132 | 16.6812 | 17.0466 | 17.3677 | 17.4205 | 17.1428 | 16.3158 | 14.5447 | 850.6066 | 560.4709 | 583.7299 | 372.0059 | 283.1673 | 818.2838 | 515.0007 | 15.7481 | 21.1224 | 25.2024 | 44.9619 | 75.5752 | 82.0308 |  |  |  | 616.4344 | 594.7383 | 594.5346 | 607.9194 | 126.9494 | 52.1077 | 810.1866 |  |  | 453.4021 |  |  | 17.8733 | 39.5492 | 355.8334 | 16.9864 | 36.7496 | 933.8507 | 743.4183 | 608.6936 | 807.9608 | 807.4502 | 742.697 |  | 801.0406 | 843.3127 | 948.6832 | 594.0868 | 668.2418 | 851.8958 |  | 978.5386 |  |  | 449.3274 | 661.1815 | 734.6212 | [6 empty] | 600.9215 |  |  | 410.8421 |  |  | 487.2466 | 655.3072 | 669.2287 | 842.3487 | 1028.1248 | 1025.0179 | 547.6967 | 722.4315 | 805.8152 | 611.4632 | 678.283 | 972.8509 | 1059.5305 | 646.0864 | 795.079 | 857.7328 | 1087.5321 | 1076.6293 | 525.197 | 623.4391 | 705.8347 | 595.1088 | 740.4152 | 879.1937 | 1000.6715 | 1110.9455 | 587.7598 | 674.8627 | 672.4732 | 838.2464 | 85.7823 | -0.00037077 | 18.2773 | 3.9311 | -39.6332 | 3.123 | 11302.11 | 0.24 | 0.89611 | -1.9201 | -2.1328 | -1.9278 | 5.2835 | 5.147 | 6.602 | 77.114 | 129.2931 | 46.5911 | 76.8672 | 14.242 | 42.2465 | 35.745
42810.4513 | 972 | 17.7615 | 18.1397 | 18.2439 | 18.2677 | 17.589 | 16.2142 | 14.6521 | 16.5101 | 17.0117 | 17.1293 | 17.1409 | 16.6581 | 15.6793 | 14.3668 | 14.7071 | 21.4214 | 22.8084 | 73.7117 | 26.5767 | 88.2241 |  |  |  | 18.3823 | 74.6768 | 260.977 | 669.9318 | 705.5378 | 677.9817 | 87.2744 | 107.4098 | 1036.2279 | 94.3765 | 109.3475 | 879.5994 | 834.7893 | 878.8051 | 1314.8425 | 241.6533 | 980.2858 | 983.8444 | 491.527 |  | 386.8287 | 643.9125 | 470.2832 | 628.4007 | 752.3894 | 902.658 | 988.1374 | 45.0617 | 379.7135 | 74.9452 | 594.0701 | 13.6527 | 51.9111 | 48.5723 | 49.6918 | 54.2014 |  |  | 0.13559 | -1.0467 | -0.40096 | -0.96267 | 4.7261 | 3.7484 | 6.2964 | -2.8921 | 22.5349 | 55.8024 | 32.9296 | 0.00028585 | 0.00032527 | -0.00081975 | 18.8198 | 16.3393 | 16.877 | 17.2441 | 17.2189 | 16.1942 | 14.5973 | 16.6707 | 17.0366 | 17.3573 | 17.4028 | 17.1424 | 16.3069 | 14.5355 | 865.9404 | 573.7338 | 618.6647 | 392.3794 | 281.388 | 821.0059 | 516.0842 | 15.7411 | 21.1962 | 25.3019 | 45.2293 | 75.6904 | 82.0914 |  |  |  | 616.7158 | 596.916 | 596.5173 | 610.8113 | 131.2002 | 52.2714 | 812.8979 |  |  | 453.8018 |  |  | 17.8818 | 39.6596 | 354.7275 | 16.9997 | 36.922 | 930.0394 | 742.4956 | 607.4492 | 811.5469 | 810.2575 | 741.386 |  | 800.7507 | 848.1993 | 950.8836 | 592.4201 | 668.3122 | 854.6607 |  | 979.0316 |  |  | 449.278 | 660.1792 | 733.4547 | [6 empty] | 599.5871 |  |  | 409.6513 |  |  | 486.9854 | 654.8654 | 668.4107 | 843.0428 | 1028.2737 | 1019.562 | 548.3202 | 723.9056 | 806.2772 | 610.9017 | 677.9906 | 975.1752 | 1054.7487 | 646.8116 | 798.0102 | 856.5319 | 1088.0673 | 1074.4005 | 525.3009 | 622.9886 | 706.0159 | 596.2503 | 741.2888 | 880.1062 | 1003.5532 | 1109.7304 | 587.4551 | 673.7392 | 673.4677 | 842.5051 | 89.0985 | -0.0007075 | 18.2763 | 3.9296 | -39.6711 | 3.123 | 11292.93 | 0.28 | 0.7914 | -2.1591 | -1.3363 | -2.0706 | 5.195 | 4.6266 | 5.9963 | 77.0609 | 130.1313 | 46.6527 | 76.2716 | 10.6014 | 94.9722 | 35.7174
42810.4513 | 973 | 17.7501 | 18.1289 | 18.2314 | 18.2571 | 17.5776 | 16.2037 | 14.6486 | 16.4965 | 17.0078 | 17.1204 | 17.131 | 16.6438 | 15.6721 | 14.3527 | 14.7173 | 21.5267 | 22.9055 | 74.1011 | 26.6076 | 88.2912 |  |  |  | 18.4121 | 74.836 | 263.5057 | 669.6142 | 706.6913 | 677.5598 | 90.8823 | 105.3562 | 1036.0771 | 92.7955 | 109.0261 | 881.2027 | 757.1039 | 880.9246 |  | 253.9126 | 979.7634 | 985.8342 | 469.0763 |  | 387.1483 | 644.436 | 471.8826 | 629.3882 | 754.5477 | 912.7716 | 988.7098 | 44.8544 | 380.5838 | 77.4502 | 595.0678 | 13.6767 | 51.8888 | 48.5772 | 49.6928 | 54.6346 |  |  | 0.30249 | -1.3989 | -0.59547 | -1.5626 | 6.756 | 5.0324 | 7.1053 | -2.2863 | 22.408 | 54.8978 | 32.5617 | 0.00034499 | 0.00029406 | -0.00079511 | 18.8642 | 16.3561 | 16.8953 | 17.256 | 17.2368 | 16.2074 | 14.6131 | 16.6936 | 17.0596 | 17.3715 | 17.4325 | 17.153 | 16.3238 | 14.5574 | 896.8025 | 550.1397 | 599.4454 | 390.6022 | 276.3515 | 823.9984 | 516.8642 | 15.7465 | 21.2768 | 25.3914 | 45.4908 | 75.7909 | 82.1413 |  |  |  | 616.8706 | 596.8966 | 596.6596 | 610.5374 | 121.4944 | 49.1351 | 815.864 |  |  | 452.3336 |  |  | 17.885 | 39.7954 | 356.1621 | 17.0205 | 37.0973 | 933.1469 | 742.5708 | 606.4158 | 812.7494 | 810.4974 | 741.4224 |  | 800.8007 | 846.0791 | 953.2332 | 590.9732 | 668.3755 | 852.9506 |  | 979.273 |  |  | 449.6937 | 660.8983 | 733.796 | [6 empty] | 598.2527 |  |  | 408.122 |  |  | 486.3647 | 654.1074 | 667.3861 | 842.9711 | 1038.6311 | 1014.8535 | 548.6564 | 726.0427 | 806.9326 | 610.4544 | 677.3627 | 976.4513 | 1054.8052 | 647.6112 | 800.4361 | 854.8397 | 1090.1954 | 1072.6066 | 525.6731 | 622.5937 | 705.7947 | 596.8692 | 742.1245 | 881.2788 | 1007.7022 | 1108.6906 | 587.3954 | 671.9808 | 673.8785 | 845.6167 | 88.0188 | -0.00010418 | 18.2756 | 3.9313 | -39.7025 | 3.1229 | 11271.93 | 0.27 | 1.1818 | -2.4968 | -1.629 | -2.6389 | 6.2379 | 5.3837 | 6.3971 | 77.0753 | 131.2355 | 46.7066 | 74.0676 | 12.9106 | 71.8801 | 35.7541
42810.4513 | 974 | 17.7461 | 18.1258 | 18.235 | 18.2558 | 17.5857 | 16.2042 | 14.65 | 16.5005 | 17.0033 | 17.1179 | 17.1272 | 16.6434 | 15.6694 | 14.353 | 14.7378 | 21.6481 | 23.0099 | 74.479 | 26.7118 | 88.3385 |  |  |  | 18.4593 | 75.0018 | 260.3637 | 670.063 | 706.2952 | 678.0453 | 95.1806 | 106.3701 | 1043.0587 | 89.5949 | 106.5468 | 878.7076 | 703.2797 | 879.0607 |  | 256.1694 | 984.4468 | 987.9455 | 486.0013 | 1345.1821 | 388.7378 | 647.9448 | 474.7229 | 629.2994 | 756.1733 | 912.2394 | 987.4303 | 44.8023 | 381.4758 | 78.1451 | 595.7832 | 13.6869 | 51.8477 | 48.5921 | 49.6994 | 55.0403 |  |  | 0.15661 | -1.322 | -1.3452 | -1.2433 | 5.6619 | 4.025 | 6.7846 | -2.4965 | 21.5156 | 53.4395 | 31.8143 | 0.00030063 | 0.00032363 | -0.00084275 | 18.9073 | 16.3528 | 16.8888 | 17.2533 | 17.2405 | 16.2067 | 14.6149 | 16.6849 | 17.052 | 17.3621 | 17.425 | 17.1516 | 16.3225 | 14.5571 | 893.9514 | 554.964 | 606.4569 | 377.1747 | 263.0226 | 825.7685 | 517.8021 | 15.7609 | 21.3696 | 25.5002 | 45.771 | 75.9119 | 82.1907 |  |  |  | 616.8892 | 595.0319 | 595.0023 | 608.1908 | 98.7088 | 45.238 | 815.7253 |  |  | 451.4217 |  |  | 17.9007 | 39.9244 | 357.6457 | 17.0243 | 37.2635 | 938.7773 | 742.7624 | 605.8457 | 812.3818 | 809.6521 | 740.9875 |  | 800.9095 | 840.4962 | 954.5241 | 590.3206 | 668.509 | 848.0392 |  | 979.6601 |  |  | 449.6791 | 660.8919 | 734.2306 | [6 empty] | 597.4555 |  |  | 407.3577 |  |  | 485.5162 | 653.2192 | 667.0464 | 844.1835 | 1047.341 | 1012.6313 | 549.0982 | 727.1785 | 806.0517 | 610.227 | 677.0825 | 978.7497 | 1057.2473 | 647.641 | 798.8216 | 855.9983 | 1091.5971 | 1071.5954 | 526.1046 | 622.2157 | 705.9557 | 597.1688 | 742.5725 | 879.1245 | 1009.4376 | 1109.2468 | 587.0674 | 670.1075 | 674.0755 | 844.4575 | 86.2472 | -0.00034273 | 18.2778 | 3.933 | -39.6407 | 3.123 | 11261.17 | 0.41 | 0.85058 | -2.4319 | -2.4531 | -2.3583 | 5.7092 | 4.8137 | 6.2497 | 77.121 | 131.9673 | 46.7537 | 75.1126 | 12.3408 | 57.5758 | 35.8227
42810.4513 | 975 | 17.7485 | 18.1295 | 18.2407 | 18.2672 | 17.5857 | 16.212 | 14.6531 | 16.5093 | 17.0095 | 17.1299 | 17.1388 | 16.6566 | 15.6741 | 14.3636 | 14.7618 | 21.7766 | 23.1238 | 74.8402 | 26.8045 | 88.3863 |  |  |  | 18.511 | 75.1583 | 256.1422 | 668.7797 | 703.8949 | 676.5779 | 93.6593 | 108.241 | 1054.642 | 90.7436 | 104.9768 | 872.7586 | 804.7102 | 870.4657 |  | 269.8858 | 990.0544 | 993.0309 | 494.4726 | 1296.835 | 390.2053 | 649.1881 | 475.6601 | 629.6236 | 756.2537 | 913.5375 | 987.6811 | 44.7932 | 382.1714 | 79.2153 | 596.5952 | 13.6934 | 51.7803 | 48.5821 | 49.6979 | 55.4652 |  |  | -0.14763 | -1.2215 | -1.2164 | -1.397 | 8.2161 | 5.842 | 7.5988 | -2.1962 | 23.0445 | 56.4161 | 31.8646 | 0.0003647 | 0.00028749 | -0.00084111 | 18.9431 | 16.3503 | 16.8777 | 17.2537 | 17.2366 | 16.2061 | 14.6104 | 16.6795 | 17.0483 | 17.3669 | 17.4262 | 17.147 | 16.322 | 14.555 | 868.6107 | 535.718 | 572.8472 | 369.319 | 251.7773 | 826.4017 | 517.8904 | 15.7765 | 21.4472 | 25.6029 | 46.0455 | 76.0289 | 82.2601 |  |  |  | 616.9641 | 593.8712 | 593.7924 | 607.9391 | 140.1622 | 46.5421 | 814.7046 |  |  | 454.4039 |  |  | 17.9055 | 40.0419 | 354.9087 | 17.022 | 37.4377 | 944.9415 | 743.7986 | 605.6203 | 812.4405 | 809.0991 | 741.9342 |  | 801.1204 | 836.0435 | 956.3595 | 589.8126 | 668.5817 | 844.4139 |  | 980.487 |  |  | 449.7012 | 661.3713 | 735.4004 | [6 empty] | 597.1179 |  |  | 407.5217 |  |  | 484.6751 | 652.8674 | 667.3095 | 845.3917 | 1049.0371 | 1013.5478 | 549.4658 | 726.3985 | 804.502 | 610.1619 | 677.4194 | 982.7935 | 1059.8872 | 647.3075 | 798.7223 | 856.7964 | 1090.691 | 1074.1922 | 526.2525 | 621.8494 | 705.6042 | 597.3043 | 742.797 | 879.1364 | 1011.3099 | 1111.602 | 586.613 | 669.2853 | 674.2717 | 841.3497 | 85.8967 | 0.00026764 | 18.2779 | 3.9356 | -39.7546 | 3.1229 | 11218.45 | 0.3 | -0.8252 | -2.3391 | -2.3343 | -2.5016 | 6.8813 | 5.8025 | 6.6177 | 77.1598 | 132.9139 | 46.7836 | 78.1893 | 16.095 | 85.1479 | 35.8438
42810.4513 | 976 | 17.7499 | 18.1329 | 18.2392 | 18.263 | 17.5812 | 16.2141 | 14.6651 | 16.5079 | 17.0091 | 17.1358 | 17.1379 | 16.6588 | 15.6765 | 14.3669 | 14.7811 | 21.8935 | 23.232 | 75.152 | 26.8621 | 88.4461 |  |  |  | 18.5646 | 75.3001 | 254.0483 | 666.4457 | 702.6623 | 674.2954 | 92.3966 | 111.1287 | 1058.7491 | 94.7436 | 108.575 | 871.515 | 841.7728 | 867.1648 |  | 277.3118 | 991.0678 | 996.2867 | 487.6436 |  | 391.545 | 652.5986 | 476.5816 | 631.4108 | 763.4175 | 930.7182 | 996.1915 | 45.2195 | 383.2317 | 79.3628 | 597.7969 | 13.7114 | 51.8018 | 48.5682 | 49.6923 | 55.8536 |  |  | 0.26175 | -1.2655 | -0.54553 | -1.2932 | 7.7975 | 5.5226 | 8.0936 | -1.9433 | 23.6887 | 55.7989 | 31.3536 | 0.00026449 | 0.00032035 | -0.00080825 | 18.9784 | 16.3526 | 16.8879 | 17.2529 | 17.2352 | 16.203 | 14.6126 | 16.6773 | 17.047 | 17.3694 | 17.422 | 17.1499 | 16.3251 | 14.5554 | 902.8619 | 536.1308 | 558.4604 | 367.789 | 260.6006 | 830.0894 | 518.4763 | 15.7849 | 21.546 | 25.7235 | 46.3525 | 76.1311 | 82.3293 |  |  |  | 617.07 | 593.0909 | 592.991 | 607.8287 | 140.6075 | 52.8673 | 814.3555 |  |  | 456.366 |  |  | 17.9162 | 40.1716 | 351.5408 | 17.0406 | 37.6174 | 946.875 | 743.323 | 605.5955 | 813.8368 | 812.0704 | 741.4897 |  | 801.3895 | 834.7869 | 957.8042 | 589.6074 | 668.682 | 845.2756 |  | 981.3471 |  |  | 449.1472 | 661.105 | 735.8062 | [6 empty] | 597.078 |  |  | 408.3408 |  |  | 484.2079 | 653.0902 | 667.2632 | 844.7712 | 1048.7102 | 1015.8549 | 549.5253 | 725.3082 | 803.5608 | 610.2716 | 677.8927 | 986.1426 | 1063.6243 | 647.616 | 799.2676 | 857.8928 | 1090.613 | 1076.6121 | 526.2312 | 621.3216 | 704.1712 | 597.7051 | 743.4712 | 880.9074 | 1012.9605 | 1112.5615 | 586.307 | 668.5824 | 674.2942 | 842.2633 | 86.2669 | -0.00073558 | 18.2777 | 3.9347 | -39.7401 | 3.1229 | 11199.17 | 0.25 | 1.0975 | -2.3853 | -1.5661 | -2.4113 | 6.752 | 5.6824 | 6.879 | 77.2553 | 133.5991 | 46.8111 | 75.9108 | 17.8244 | 97.4486 | 35.8667
42810.4513 | 977 | 17.7408 | 18.1236 | 18.2298 | 18.2621 | 17.5751 | 16.203 | 14.6556 | 16.4996 | 17.0059 | 17.1149 | 17.1289 | 16.6477 | 15.6636 | 14.3523 | 14.8007 | 22.0229 | 23.3372 | 75.4601 | 26.963 | 88.5098 |  |  |  | 18.6183 | 75.4482 | 254.6746 | 666.5816 | 702.5074 | 675.146 | 92.7573 | 107.8338 | 1054.4384 | 95.5708 | 112.4747 | 875.3387 | 675.7727 | 871.8709 |  | 258.525 | 986.0241 | 989.0227 | 493.689 |  | 394.4222 | 654.4118 | 479.2259 | 634.0807 | 769.006 | 938.7323 | 1000.9418 | 46.6161 | 384.0432 | 79.1818 | 598.9868 | 13.7126 | 51.8902 | 48.559 | 49.689 | 56.2462 |  |  | -0.57344 | -1.1295 | -1.2197 | -1.7808 | 5.8728 | 5.0462 | 6.5356 | -3.3153 | 22.8132 | 55.1319 | 30.3913 | 0.00031542 | 0.00027763 | -0.00083125 | 19.0066 | 16.3483 | 16.8865 | 17.2486 | 17.2318 | 16.2033 | 14.6112 | 16.6798 | 17.0435 | 17.365 | 17.4212 | 17.1461 | 16.3189 | 14.5529 | 928.5491 | 551.7882 | 562.33 | 368.1817 | 268.722 | 833.7776 | 519.3489 | 15.7825 | 21.6271 | 25.8165 | 46.6202 | 76.2317 | 82.3762 |  |  |  | 617.0119 | 591.677 | 591.6115 | 606.2233 | 110.6367 | 48.3409 | 816.6557 |  |  | 457.4256 |  |  | 17.9319 | 40.2909 | 351.045 | 17.0502 | 37.7906 | 939.7539 | 742.7515 | 606.2398 | 815.9038 | 814.8069 | 739.4781 |  | 801.5805 | 841.2953 | 958.8873 | 589.771 | 668.8635 | 850.6586 |  | 982.3411 |  |  | 448.6388 | 656.7197 | 734.5408 | [6 empty] | 597.6163 |  |  | 409.2868 |  |  | 484.2077 | 653.7105 | 666.8686 | 847.4756 | 1046.1781 | 1017.0442 | 549.2644 | 724.3437 | 803.349 | 611.2967 | 678.2429 | 989.3883 | 1066.094 | 647.655 | 798.7169 | 862.3094 | 1093.0619 | 1076.8139 | 525.9496 | 621.1368 | 702.2116 | 598.1866 | 743.3538 | 880.7575 | 1012.453 | 1114.0423 | 586.1778 | 667.5573 | 673.8396 | 841.3494 | 89.7381 | -0.0012617 | 18.2771 | 3.9302 | -39.6886 | 3.123 | 11184.53 | 0.23 | -1.6251 | -2.2557 | -2.3441 | -2.8323 | 5.8792 | 5.4498 | 6.2021 | 77.3703 | 133.9071 | 46.846 | 74.5954 | 17.5898 | 51.0313 | 35.9004
42810.4514 | 978 | 17.7415 | 18.1307 | 18.2375 | 18.2578 | 17.5807 | 16.2131 | 14.6576 | 16.505 | 17.0065 | 17.1228 | 17.1306 | 16.6497 | 15.6745 | 14.3583 | 14.8179 | 22.1343 | 23.4601 | 75.7742 | 27.0766 | 88.567 |  |  |  | 18.6674 | 75.5945 | 253.4301 | 667.503 | 702.0518 | 676.1487 | 92.5346 | 109.7792 | 1033.6546 | 92.8402 | 108.5094 | 875.8254 | 711.2777 | 876.6418 |  | 249.0801 | 976.2634 | 980.1298 | 505.725 |  | 397.6132 | 656.3445 | 480.4337 | 634.3507 | 773.8741 | 937.2119 | 1002.0456 | 47.4582 | 384.899 | 78.0117 | 600.4108 | 13.72 | 52.0001 | 48.5507 | 49.6951 | 56.5598 |  |  | -0.38222 | -0.95207 | -0.72689 | -1.6165 | 6.0187 | 5.0633 | 6.6979 | -2.1838 | 21.6701 | 53.6946 | 30.731 | 0.00032692 | 0.00035156 | -0.00080332 | 19.0356 | 16.3474 | 16.8813 | 17.2556 | 17.2319 | 16.2073 | 14.6119 | 16.6782 | 17.0453 | 17.3653 | 17.4249 | 17.1508 | 16.3214 | 14.5543 | 913.837 | 571.914 | 563.2729 | 365.8291 | 278.1149 | 835.085 | 519.5914 | 15.7941 | 21.7111 | 25.927 | 46.9018 | 76.3411 | 82.4335 |  |  |  | 616.8709 | 589.8598 | 589.6456 | 603.7183 | 91.5771 | 32.2394 | 819.2124 |  |  | 456.902 |  |  | 17.945 | 40.4106 | 350.0089 | 17.0633 | 37.9642 | 923.9898 | 743.8332 | 607.7791 | 819.0922 | 817.7702 | 738.8211 |  | 801.895 | 845.9182 | 960.2532 | 590.7752 | 669.2383 | 856.2574 |  | 983.3654 |  |  | 448.2963 | 653.4781 | 734.5054 | [6 empty] | 599.1215 |  |  | 410.2806 |  |  | 484.7411 | 653.9387 | 666.6121 | 847.751 | 1050.4046 | 1017.411 | 548.4433 | 724.0559 | 803.4679 | 613.0326 | 678.511 | 986.4181 | 1063.536 | 647.4449 | 800.1945 | 862.5657 | 1099.1704 | 1080.5419 | 525.7973 | 621.308 | 702.8621 | 598.2169 | 743.2904 | 882.4247 | 1015.3757 | 1118.3489 | 586.0442 | 667.6152 | 673.2529 | 845.2448 | 92.0819 | -0.0016475 | 18.2754 | 3.9244 | -39.7473 | 3.1229 | 11180.22 | 0.34 | -1.3275 | -2.0731 | -1.8114 | -2.7013 | 5.9481 | 5.4556 | 6.2747 | 77.4858 | 134.397 | 46.8996 | 76.7782 | 17.5393 | 58.9596 | 35.9435
42810.4514 | 979 | 17.7402 | 18.1226 | 18.2279 | 18.2538 | 17.5818 | 16.2107 | 14.6754 | 16.5012 | 17.0042 | 17.1306 | 17.135 | 16.6541 | 15.6819 | 14.3669 | 14.8144 | 22.258 | 23.5637 | 76.1133 | 27.1634 | 88.6263 |  |  |  | 18.708 | 75.7302 | 252.3985 | 667.1081 | 701.1617 | 676.0565 | 88.2408 | 109.3287 | 1022.5725 | 94.6187 | 108.8832 | 871.6328 | 764.7805 | 873.2198 |  | 234.0283 | 979.9202 | 984.0646 | 477.4186 |  | 399.0587 | 657.6095 | 481.294 | 632.9286 | 773.8192 | 937.7351 | 1004.0237 | 46.9298 | 385.6263 | 77.7312 | 601.6736 | 13.7287 | 52.0814 | 48.5304 | 49.6828 | 56.8569 |  |  | 0.10996 | -1.3608 | -0.97594 | -1.0961 | 5.8018 | 6.003 | 6.922 | -2.3441 | 22.8579 | 55.8708 | 30.9556 | 0.00034334 | 0.00034663 | -0.00081975 | 19.0742 | 16.3514 | 16.8836 | 17.2583 | 17.234 | 16.2045 | 14.6198 | 16.6822 | 17.0485 | 17.3729 | 17.4324 | 17.1551 | 16.3279 | 14.5556 | 870.0786 | 557.815 | 528.1478 | 347.8501 | 265.4649 | 834.5582 | 518.9432 | 15.817 | 21.7983 | 26.0379 | 47.1841 | 76.446 | 82.4881 |  |  |  | 616.7447 | 588.5813 | 587.6657 | 602.8077 | 127.3153 | 51.0747 | 823.3035 |  |  | 457.948 |  |  | 17.9531 | 40.5428 | 348.959 | 17.0599 | 38.1326 | 920.4521 | 745.7077 | 609.0381 | 820.1861 | 818.7001 | 740.9823 |  | 802.6061 | 859.8021 | 962.0434 | 592.503 | 669.73 | 866.7131 |  | 983.598 |  |  | 448.0907 | 654.8123 | 735.9987 | [6 empty] | 600.6664 |  |  | 411.6534 |  |  | 485.546 | 654.4578 | 667.1609 | 846.2719 | 1045.2686 | 1015.6223 | 547.8158 | 724.5542 | 804.5139 | 614.4382 | 678.889 | 980.6563 | 1056.1541 | 646.9335 | 801.0583 | 867.0988 | 1105.7217 | 1081.9186 | 526.234 | 621.2762 | 704.8858 | 598.5764 | 743.55 | 881.8378 | 1016.8057 | 1121.2795 | 585.7815 | 668.8376 | 672.8994 | 849.3515 | 83.6456 | -0.0013599 | 18.2769 | 3.917 | -39.7646 | 3.1229 | 11221.98 | 0.31 | 0.71197 | -2.4802 | -2.1004 | -2.2259 | 5.8412 | 5.9416 | 6.3802 | 77.6461 | 134.8245 | 46.9587 | 81.4192 | 21.297 | 73.7868 | 35.9452
42810.4514 | 980 | 17.739 | 18.1234 | 18.2266 | 18.2484 | 17.5772 | 16.2089 | 14.6627 | 16.4945 | 17.0039 | 17.1315 | 17.1306 | 16.6548 | 15.6751 | 14.3707 | 14.8516 | 22.3876 | 23.6759 | 76.4305 | 27.2086 | 88.703 |  |  |  | 18.7808 | 75.8851 | 257.8239 | 666.9301 | 701.0036 | 678.0649 | 88.1232 | 106.8161 | 1017.5609 | 91.0892 | 108.89 | 868.6231 | 732.2838 | 869.5737 |  | 242.9729 | 974.2658 | 978.6256 | 466.5441 |  | 400.0805 | 658.0483 | 482.434 | 631.8375 | 766.1059 | 937.6894 | 1007.1001 | 46.3552 | 386.3067 | 78.8139 | 602.7718 | 13.7421 | 52.1727 | 48.5102 | 49.6866 | 57.382 |  |  | 0.16384 | -1.7544 | -0.86094 | -0.73137 | 4.9719 | 4.9266 | 7.2308 | -2.1844 | 22.8861 | 56.6192 | 30.1119 | 0.00026285 | 0.00038277 | -0.00078361 | 19.1082 | 16.3429 | 16.872 | 17.2448 | 17.2257 | 16.1939 | 14.608 | 16.674 | 17.037 | 17.3706 | 17.4173 | 17.1423 | 16.3222 | 14.5592 | 883.4585 | 602.01 | 593.1942 | 347.8181 | 266.9788 | 836.9352 | 520.3891 | 15.819 | 21.8791 | 26.1416 | 47.4701 | 76.5444 | 82.5339 |  |  |  | 616.6874 | 587.5633 | 585.8848 | 603.5811 | 145.9837 | 70.3689 | 826.5732 |  |  | 459.894 |  |  | 17.9625 | 40.6599 | 352.6576 | 17.0877 | 38.298 | 914.5828 | 746.1121 | 609.9729 | 816.4491 | 814.5898 | 741.261 |  | 803.2756 | 860.2152 | 961.1228 | 593.5449 | 670.1021 | 872.9628 |  | 982.7093 |  |  | 448.1236 | 655.4451 | 737.5052 | [6 empty] | 601.6316 |  |  | 412.2287 |  |  | 486.073 | 655.1464 | 668.7744 | 848.1758 | 1045.6647 | 1010.9634 | 547.4239 | 725.1719 | 806.0849 | 614.974 | 680.2328 | 981.2531 | 1052.9368 | 646.2354 | 801.3467 | 871.1833 | 1105.5006 | 1080.7201 | 526.5886 | 621.2023 | 704.2496 | 598.9054 | 743.3848 | 882.4899 | 1015.4588 | 1122.6498 | 585.5001 | 669.9389 | 672.5623 | 847.4635 | 84.3983 | -0.001395 | 18.2782 | 3.9059 | -39.6478 | 3.1229 | 11339.51 | 0.27 | 0.87 | -2.8168 | -1.9732 | -1.8187 | 5.4072 | 5.3825 | 6.5208 | 77.8462 | 134.3944 | 47.0109 | 80.9318 | 14.3936 | 65.3241 | 35.9129
42810.4514 | 981 | 17.7335 | 18.1165 | 18.2281 | 18.2464 | 17.5757 | 16.2085 | 14.6611 | 16.4933 | 17.0083 | 17.125 | 17.1354 | 16.6536 | 15.6749 | 14.3684 | 14.8706 | 22.5075 | 23.7916 | 76.7159 | 27.3071 | 88.7574 |  |  |  | 18.815 | 76.0132 | 254.1599 | 665.8429 | 700.2613 | 676.4865 | 92.4082 | 106.1468 | 1009.1388 | 90.3118 | 106.7419 | 863.6566 | 802.8945 | 863.8531 |  | 253.254 | 971.0137 | 975.0972 | 474.8284 |  | 400.7691 | 661.0396 | 486.1273 | 631.7381 | 767.4936 | 941.6068 | 1009.818 | 44.9993 | 387.3291 | 78.2798 | 603.8309 | 13.7473 | 52.2605 | 48.4769 | 49.7035 | 57.7999 |  |  | -0.064837 | -0.87585 | -0.63818 | -1.1184 | 7.1161 | 6.2697 | 7.742 | -2.555 | 22.7079 | 56.6683 | 26.4125 | 0.0003417 | 0.00025463 | -0.00082468 | 19.144 | 16.3442 | 16.8817 | 17.2492 | 17.2304 | 16.1927 | 14.6071 | 16.6787 | 17.0442 | 17.3705 | 17.4245 | 17.1586 | 16.3254 | 14.5609 | 914.0323 | 634.7968 | 660.9038 | 374.5994 | 284.3839 | 840.9785 | 524.0074 | 15.8328 | 21.9744 | 26.2553 | 47.782 | 76.6528 | 82.602 |  |  |  | 616.5916 | 585.7061 | 583.5628 | 602.313 | 141.8592 | 70.6492 | 823.0299 |  |  | 461.3624 |  |  | 17.9786 | 40.7867 | 352.2519 | 17.0965 | 38.4726 | 910.4274 | 746.5739 | 610.3967 | 813.2208 | 811.0205 | 741.0085 |  | 803.6421 | 853.5782 | 960.1584 | 593.9834 | 670.4499 | 875.3314 |  | 982.0767 |  |  | 447.3865 | 653.7916 | 737.0372 | [6 empty] | 602.2273 |  |  | 412.286 |  |  | 486.2304 | 655.8489 | 671.0579 | 850.8269 | 1052.1397 | 1010.9329 | 546.8144 | 725.509 | 806.6387 | 615.1022 | 681.6169 | 984.5037 | 1054.6642 | 645.9457 | 802.822 | 869.1879 | 1105.1055 | 1082.9251 | 527.0786 | 620.9047 | 703.2344 | 599.9181 | 742.6572 | 881.5459 | 1016.7408 | 1121.5747 | 585.3096 | 670.0014 | 673.0686 | 845.0455 | 93.1546 | 0.00096913 | 18.2768 | 3.8935 | -39.6286 | 3.1228 | 11438.77 | 0.35 | -0.54684 | -1.9934 | -1.7016 | -2.2526 | 6.4794 | 6.0819 | 6.7583 | 77.9671 | 134.1412 | 47.0746 | 79.2452 | 7.6853 | 85.1288 | 35.9302
42810.4514 | 982 | 17.7309 | 18.1142 | 18.2222 | 18.2482 | 17.5843 | 16.2075 | 14.6662 | 16.4975 | 17.004 | 17.1232 | 17.1326 | 16.6474 | 15.6796 | 14.3675 | 14.9017 | 22.6501 | 23.9151 | 76.9884 | 27.4374 | 88.8064 |  |  |  | 18.8849 | 76.168 | 253.0798 | 663.4864 | 698.5972 | 673.4212 | 94.9012 | 108.1627 | 1008.4339 | 88.28 | 105.1893 | 860.5607 | 843.5328 | 862.2959 |  | 253.1851 | 970.934 | 974.7721 | 499.692 |  | 401.5679 | 662.0944 | 487.868 | 634.2715 | 765.7759 | 944.0474 | 1011.9249 | 44.6526 | 388.2518 | 78.2644 | 604.7007 | 13.7466 | 52.3207 | 48.4325 | 49.7017 | 58.2014 |  |  | 0.058047 | -0.61235 | -0.51004 | -1.4246 | 6.8572 | 5.8426 | 8.2395 | -2.9302 | 23.2849 | 56.3815 | 24.1884 | 0.00027763 | 0.00032363 | -0.00080497 | 19.1851 | 16.3398 | 16.875 | 17.2508 | 17.2259 | 16.195 | 14.6038 | 16.6764 | 17.0465 | 17.361 | 17.4277 | 17.145 | 16.3242 | 14.5605 | 928.3354 | 636.9315 | 672.4995 | 390.9334 | 294.4873 | 844.754 | 527.5693 | 15.843 | 22.0582 | 26.3701 | 48.0662 | 76.7433 | 82.6652 |  |  |  | 616.4265 | 583.8113 | 582.0452 | 599.9885 | 134.3696 | 49.201 | 819.3588 |  |  | 462.4068 |  |  | 17.9885 | 40.9124 | 350.8602 | 17.1128 | 38.6426 | 911.2312 | 747.6553 | 610.1279 | 811.5499 | 809.7981 | 743.0657 |  | 804.1455 | 852.2177 | 960.3949 | 593.6823 | 670.7674 | 879.6491 |  | 982.3614 |  |  | 447.3356 | 655.9058 | 737.8071 | [6 empty] | 602.0109 |  |  | 411.9661 |  |  | 486.1269 | 656.5398 | 670.8533 | 850.6403 | 1049.3911 | 1012.1593 | 546.4424 | 726.0899 | 806.9875 | 614.509 | 681.6741 | 984.1878 | 1054.0127 | 645.6047 | 801.6775 | 863.5504 | 1102.2474 | 1080.8201 | 526.6943 | 620.4274 | 700.765 | 601.0466 | 743.2864 | 882.6685 | 1014.0411 | 1116.6111 | 585.0619 | 669.0638 | 675.1262 | 845.7718 | 90.5201 | -0.0004339 | 18.2764 | 3.8801 | -39.6684 | 3.1228 | 11551.86 | 0.34 | 0.51658 | -1.6677 | -1.5221 | -2.5438 | 6.3668 | 5.8769 | 6.9791 | 78.0666 | 134.2862 | 47.1523 | 79.2657 | 7.2046 | 97.7174 | 35.9638
42810.4514 | 983 | 17.7257 | 18.1073 | 18.2203 | 18.2458 | 17.5777 | 16.2008 | 14.6711 | 16.5017 | 17.0016 | 17.1187 | 17.1245 | 16.6468 | 15.6771 | 14.3649 | 14.9164 | 22.7685 | 24.0212 | 77.2567 | 27.5115 | 88.8569 |  |  |  | 18.9378 | 76.3052 | 253.1377 | 661.2084 | 698.0942 | 670.2677 | 92.4176 | 114.1096 | 1018.0842 | 92.6951 | 107.8615 | 859.9715 | 852.5791 | 866.3593 |  | 258.8037 | 976.5294 | 980.7403 | 508.1035 |  | 402.2645 | 663.1103 | 488.694 | 636.2588 | 765.2845 | 945.6593 | 1013.9818 | 45.3897 | 389.0525 | 77.0286 | 605.445 | 13.7459 | 52.278 | 48.3984 | 49.7014 | 58.5947 |  |  | 0.084331 | -1.1564 | -0.65592 | -1.0869 | 6.1987 | 4.3687 | 7.5935 | -3.7267 | 22.4419 | 55.5135 | 24.6276 | 0.0002957 | 0.00033677 | -0.00081318 | 19.2145 | 16.3412 | 16.866 | 17.2439 | 17.2255 | 16.1957 | 14.6018 | 16.674 | 17.0472 | 17.3612 | 17.4244 | 17.1439 | 16.3237 | 14.5549 | 931.2221 | 620.426 | 627.0075 | 393.1741 | 291.1317 | 847.5361 | 529.2689 | 15.8555 | 22.1421 | 26.4688 | 48.3384 | 76.828 | 82.7283 |  |  |  | 616.0851 | 581.0583 | 580.64 | 595.5021 | 135.1819 | 56.493 | 818.6238 |  |  | 463.2797 |  |  | 17.9991 | 41.0383 | 350.3588 | 17.1286 | 38.8168 | 912.8494 | 748.637 | 609.9051 | 810.2979 | 808.7905 | 745.5967 |  | 804.837 | 854.3603 | 959.701 | 593.1224 | 671.0998 | 878.1704 |  | 982.6496 |  |  | 447.7222 | 659.6559 | 739.5212 | [6 empty] | 601.5843 |  |  | 410.5277 |  |  | 485.7966 | 656.719 | 670.0733 | 850.5418 | 1047.6171 | 1011.203 | 546.407 | 725.5007 | 805.8118 | 613.6227 | 681.3847 | 987.4295 | 1057.0382 | 645.028 | 801.248 | 863.4544 | 1100.4507 | 1075.3 | 526.8314 | 619.8352 | 698.3848 | 601.3874 | 744.6258 | 883.0684 | 1015.0514 | 1113.0873 | 584.5631 | 667.9493 | 675.8694 | 846.1703 | 86.6563 | -0.00081974 | 18.2773 | 3.8634 | -39.7353 | 3.1228 | 11609.73 | 0.31 | 0.6216 | -2.2931 | -1.727 | -2.2231 | 6.0574 | 5.0852 | 6.7044 | 78.2118 | 133.9123 | 47.2405 | 80.1389 | 12.6467 | 100.6269 | 36.0245
42810.4514 | 984 | 17.7255 | 18.116 | 18.215 | 18.236 | 17.5714 | 16.2014 | 14.6645 | 16.4941 | 16.9959 | 17.1208 | 17.1368 | 16.6579 | 15.6754 | 14.3607 | 14.9409 | 22.8986 | 24.149 | 77.5348 | 27.5982 | 88.9325 |  |  |  | 19.0025 | 76.4413 | 256.1643 | 659.7283 | 700.4063 | 668.2753 | 91.2379 | 111.7572 | 1026.4251 | 97.7751 | 112.5333 | 868.9826 | 771.6955 | 870.4555 |  | 265.2191 | 984.5398 | 988.7798 | 507.4035 |  | 401.6395 | 664.0926 | 488.7678 | 636.5038 | 763.9439 | 942.342 | 1012.622 | 45.6156 | 389.8864 | 76.153 | 606.5062 | 13.7575 | 52.2497 | 48.3977 | 49.7082 | 58.9594 |  |  | 0.063959 | -0.64389 | -1.4642 | -1.0225 | 6.4596 | 4.167 | 7.9287 | -2.007 | 22.0048 | 54.1735 | 25.3095 | 0.00032692 | 0.00029077 | -0.00080168 | 19.25 | 16.3467 | 16.8683 | 17.2442 | 17.2268 | 16.1974 | 14.6132 | 16.6807 | 17.0512 | 17.3669 | 17.4177 | 17.1519 | 16.33 | 14.5604 | 934.283 | 640.7113 | 615.6664 | 387.9047 | 289.8788 | 850.326 | 531.015 | 15.8679 | 22.225 | 26.5786 | 48.6046 | 76.9203 | 82.7741 |  |  |  | 615.6042 | 577.7556 | 578.6177 | 591.5349 | 130.5401 | 45.997 | 817.5824 |  |  | 464.9926 |  |  | 18.0098 | 41.1633 | 354.6137 | 17.1373 | 38.9924 | 920.3423 | 748.6589 | 609.8366 | 809.5062 | 808.2013 | 746.0507 |  | 805.2265 | 850.1113 | 958.7222 | 593.0728 | 671.3423 | 872.8145 |  | 983.2874 |  |  | 447.963 | 661.6006 | 740.421 | [6 empty] | 601.5461 |  |  | 409.8037 |  |  | 485.5048 | 656.8037 | 669.2665 | 852.3291 | 1049.1444 | 1014.4199 | 546.6739 | 725.129 | 804.3603 | 613.0921 | 680.9553 | 988.6881 | 1057.8602 | 645.1263 | 800.9194 | 866.1089 | 1101.6938 | 1075.1226 | 526.6664 | 619.6597 | 695.6195 | 601.5916 | 745.0156 | 885.0017 | 1018.0391 | 1114.7797 | 584.0615 | 666.4868 | 676.4614 | 845.7569 | 88.2847 | -9.7173e-05 | 18.2776 | 3.8567 | -39.7501 | 3.1229 | 11603.45 | 0.3 | 0.54077 | -1.712 | -2.5816 | -2.1573 | 6.1751 | 4.9597 | 6.8414 | 78.3207 | 133.5877 | 47.295 | 81.0028 | 14.306 | 74.9173 | 36.0447
42810.4514 | 985 | 17.7235 | 18.106 | 18.221 | 18.2412 | 17.5771 | 16.1981 | 14.67 | 16.5066 | 17.0011 | 17.1263 | 17.1294 | 16.6561 | 15.6776 | 14.3726 | 14.9642 | 23.0299 | 24.27 | 77.8143 | 27.7046 | 88.9964 |  |  |  | 19.0588 | 76.5725 | 259.4779 | 660.1264 | 702.9293 | 668.0095 | 93.0766 | 107.503 | 1027.5271 | 94.2371 | 112.0351 | 874.1781 | 604.9671 | 876.2082 |  | 261.2845 | 982.684 | 988.7648 | 517.4892 |  | 401.0817 | 664.2405 | 488.7715 | 636.4835 | 764.0143 | 938.4592 | 1008.6327 | 45.5612 | 390.5254 | 75.3153 | 607.4944 | 13.7268 | 52.2915 | 48.4058 | 49.7101 | 59.2872 |  |  | -0.20415 | -1.2294 | -1.181 | -1.2669 | 6.1179 | 5.5187 | 7.5883 | -3.5538 | 21.7516 | 54.0678 | 23.9397 | 0.0002957 | 0.00033184 | -0.00083618 | 19.2882 | 16.35 | 16.8799 | 17.2436 | 17.234 | 16.2027 | 14.618 | 16.6893 | 17.0536 | 17.3753 | 17.4267 | 17.1583 | 16.3293 | 14.5706 | 923.8961 | 618.5662 | 595.2907 | 377.4017 | 283.4035 | 852.2634 | 532.1676 | 15.8749 | 22.322 | 26.6984 | 48.8978 | 77.0136 | 82.8234 |  |  |  | 614.9577 | 574.3375 | 576.0868 | 586.2745 | 123.4076 | 53.9451 | 815.8374 |  |  | 467.5779 |  |  | 18.0299 | 41.2743 | 360.0254 | 17.1491 | 39.1567 | 922.3239 | 748.8033 | 609.5553 | 807.3952 | 805.9842 | 746.7174 |  | 805.702 | 845.3666 | 957.9671 | 592.6981 | 671.5134 | 866.6033 |  | 984.0023 |  |  | 448.3922 | 663.0242 | 740.6444 | [6 empty] | 601.2814 |  |  | 410.0506 |  |  | 485.3081 | 656.7512 | 667.9405 | 854.2961 | 1046.8113 | 1015.3437 | 546.9402 | 725.0534 | 803.3806 | 612.5861 | 679.8842 | 988.9888 | 1056.4187 | 645.5474 | 801.6283 | 867.5248 | 1105.3171 | 1076.6681 | 526.4549 | 619.417 | 692.9001 | 601.9151 | 745.3902 | 885.3467 | 1022.9464 | 1115.6713 | 583.574 | 665.235 | 677.2809 | 847.1608 | 87.0914 | -0.0015143 | 18.2774 | 3.8484 | -39.7185 | 3.1229 | 11647.47 | 0.31 | -0.96598 | -2.3658 | -2.3187 | -2.4016 | 6 | 5.6986 | 6.6822 | 78.4507 | 133.3786 | 47.3428 | 82.9968 | 16.8343 | 36.1426 | 36.07
42810.4514 | 986 | 17.7247 | 18.1065 | 18.2245 | 18.2479 | 17.5717 | 16.1976 | 14.6792 | 16.5027 | 16.9973 | 17.1182 | 17.1257 | 16.6561 | 15.6742 | 14.3694 | 14.995 | 23.1514 | 24.3783 | 78.073 | 27.8286 | 89.0447 |  |  |  | 19.1196 | 76.6905 | 259.9559 | 661.3876 | 704.2968 | 669.7975 | 92.0834 | 110.475 | 1019.8893 | 93.8888 | 110.7947 | 875.4131 | 779.6935 | 884.4918 |  | 245.2568 | 984.162 | 985.3924 | 535.4689 |  | 402.0712 | 663.8286 | 488.6235 | 638.0709 | 763.7515 | 942.7838 | 1009.1014 | 45.4465 | 391.2362 | 73.9728 | 608.2538 | 13.6989 | 52.4356 | 48.4117 | 49.7094 | 59.6143 |  |  | -0.074693 | -1.0263 | -0.83597 | -1.1736 | 6.0627 | 5.3859 | 6.7544 | -2.8001 | 21.8587 | 53.6723 | 23.0737 | 0.0002842 | 0.0002957 | -0.00080332 | 19.3285 | 16.3427 | 16.8753 | 17.2477 | 17.2352 | 16.205 | 14.6185 | 16.6883 | 17.0492 | 17.3698 | 17.4281 | 17.1598 | 16.3276 | 14.5675 | 914.2002 | 585.5331 | 614.6433 | 375.1397 | 279.4881 | 854.6409 | 533.4587 | 15.8793 | 22.4059 | 26.7942 | 49.1772 | 77.0981 | 82.8784 |  |  |  | 614.1495 | 570.8043 | 573.7533 | 581.0911 | 146.7767 | 63.0427 | 812.9651 |  |  | 468.7209 |  |  | 18.0335 | 41.3976 | 361.5843 | 17.1554 | 39.3359 | 915.1747 | 747.0297 | 609.2589 | 805.4471 | 804.3334 | 744.9596 |  | 805.7972 | 842.2848 | 956.2557 | 592.2045 | 671.6371 | 863.3864 |  | 984.5163 |  |  | 448.5104 | 660.3295 | 739.5451 | [6 empty] | 600.9576 |  |  | 410.2217 |  |  | 485.2278 | 656.1182 | 666.3698 | 856.6384 | 1044.9249 | 1016.1996 | 547.1312 | 725.2561 | 802.5871 | 612.2926 | 678.7424 | 988.202 | 1057.784 | 645.5286 | 802.4521 | 867.9553 | 1107.5121 | 1075.4746 | 526.1688 | 619.4067 | 691.7444 | 602.7282 | 745.27 | 885.8123 | 1030.4357 | 1114.1462 | 583.1221 | 664.7126 | 678.5649 | 845.6943 | 86.1875 | 0.00065348 | 18.2767 | 3.8247 | -39.7316 | 3.1228 | 11694.9 | 0.28 | -0.58486 | -2.1611 | -1.9504 | -2.311 | 5.9835 | 5.6396 | 6.3156 | 78.5293 | 132.6939 | 47.3836 | 85.1093 | 14.9808 | 76.4528 | 36.0633
42810.4515 | 987 | 17.7291 | 18.1113 | 18.2277 | 18.2522 | 17.5775 | 16.2028 | 14.6872 | 16.5053 | 17.0109 | 17.1283 | 17.1399 | 16.6602 | 15.6861 | 14.3783 | 15.0197 | 23.2814 | 24.4951 | 78.3221 | 27.9008 | 89.0933 |  |  |  | 19.1808 | 76.8119 | 260.1438 | 662.4884 | 704.0842 | 672.4419 | 88.5159 | 111.152 | 1010.9601 | 94.4059 | 112.708 | 884.4407 | 868.77 | 892.0696 |  | 252.1688 | 990.0531 | 994.4019 | 530.148 |  | 401.7501 | 664.4592 | 488.0861 | 638.0523 | 766.5591 | 947.9389 | 1009.4432 | 45.4125 | 391.8899 | 73.9998 | 608.8273 | 13.6517 | 52.5698 | 48.4332 | 49.7069 | 59.9008 |  |  | 0.13362 | -1.1985 | -0.90234 | -1.236 | 7.074 | 5.7644 | 7.5265 | -3.0137 | 22.0355 | 55.0463 | 23.1673 | 0.00030556 | 0.00027928 | -0.00084111 | 19.3589 | 16.3336 | 16.8619 | 17.2431 | 17.2157 | 16.1983 | 14.6092 | 16.677 | 17.0431 | 17.3688 | 17.4206 | 17.1532 | 16.3282 | 14.5631 | 927.3502 | 597.6039 | 644.8981 | 390.1959 | 285.9557 | 857.8745 | 535.8185 | 15.893 | 22.5043 | 26.907 | 49.4722 | 77.1947 | 82.9242 |  |  |  | 613.5226 | 567.9112 | 571.5405 | 580.6025 | 128.2343 | 57.7554 | 810.8224 |  |  | 471.4239 |  |  | 18.0348 | 41.5039 | 359.7388 | 17.1548 | 39.4916 | 911.9713 | 745.6821 | 609.5577 | 804.3332 | 803.2491 | 742.9918 |  | 805.8039 | 839.0331 | 955.2623 | 592.641 | 671.8767 | 860.0091 |  | 984.9397 |  |  | 448.2667 | 656.357 | 737.4462 | [6 empty] | 601.1779 |  |  | 410.7738 |  |  | 485.1052 | 655.5403 | 665.5944 | 856.1064 | 1041.8397 | 1015.7974 | 547.0931 | 725.2387 | 801.6095 | 612.1701 | 678.3539 | 985.7634 | 1053.5924 | 645.1936 | 802.7842 | 868.9558 | 1110.5591 | 1074.4065 | 525.9991 | 619.987 | 692.0591 | 604.6069 | 745.7603 | 887.5262 | 1034.7682 | 1114.163 | 582.5136 | 665.9634 | 680.9614 | 847.5464 | 87.139 | -0.00020241 | 18.277 | 3.8159 | -39.7252 | 3.1229 | 11700.65 | 0.34 | 0.78333 | -2.3361 | -2.027 | -2.3724 | 6.477 | 5.8468 | 6.6809 | 78.5861 | 132.3385 | 47.424 | 85.064 | 12.1634 | 105.817 | 35.9603
42810.4515 | 988 | 17.7219 | 18.1108 | 18.2212 | 18.2518 | 17.5712 | 16.1989 | 14.6827 | 16.4943 | 17.0094 | 17.1276 | 17.1362 | 16.6602 | 15.6821 | 14.3715 | 15.0443 | 23.422 | 24.6224 | 78.6236 | 27.9929 | 89.1568 |  |  |  | 19.2503 | 76.9451 | 260.7997 | 664.1153 | 704.4771 | 675.4224 | 94.0608 | 112.0838 | 1017.3107 | 98.5494 | 115.8502 | 899.2189 | 867.856 | 909.1586 |  | 260.6167 | 998.4172 | 1004.0819 | 519.8383 |  | 401.0413 | 665.6573 | 487.385 | 640.8795 | 772.4164 | 950.5838 | 1009.1244 | 45.1906 | 392.7373 | 74.2073 | 609.538 | 13.6277 | 52.6777 | 48.4515 | 49.7068 | 60.2534 |  |  | 0.41289 | -0.82394 | -1.1586 | -1.2387 | 6.2152 | 5.6251 | 7.2735 | -3.2798 | 21.9886 | 53.4009 | 22.3805 | 0.00032856 | 0.00023492 | -0.00082961 | 19.3976 | 16.3415 | 16.8661 | 17.2414 | 17.2241 | 16.2039 | 14.6217 | 16.6768 | 17.0579 | 17.3755 | 17.4293 | 17.1509 | 16.3334 | 14.5687 | 918.622 | 566.4769 | 655.0457 | 391.3293 | 298.1723 | 859.8911 | 537.7816 | 15.8969 | 22.5873 | 27.0144 | 49.7523 | 77.2798 | 82.9671 |  |  |  | 613.274 | 566.3702 | 570.4631 | 586.3875 | 112.0297 | 58.5603 | 809.1657 |  |  | 473.6833 |  |  | 18.0553 | 41.6445 | 357.0252 | 17.1829 | 39.673 | 919.701 | 744.4353 | 609.8329 | 802.5677 | 801.8321 | 741.2894 |  | 805.862 | 835.5961 | 955.1082 | 593.0685 | 672.0766 | 854.6323 |  | 985.1847 |  |  | 447.6184 | 651.9017 | 735.8486 | [6 empty] | 601.5628 |  |  | 411.6467 |  |  | 484.9364 | 655.1817 | 665.859 | 857.1546 | 1036.6458 | 1011.313 | 546.7901 | 725.2557 | 801.0047 | 611.802 | 678.5171 | 985.2996 | 1045.2159 | 644.5176 | 801.2043 | 869.661 | 1110.6848 | 1074.0814 | 525.6818 | 620.4728 | 693.9529 | 605.8839 | 747.999 | 889.0822 | 1035.1691 | 1113.7879 | 582.1586 | 668.1188 | 682.961 | 855.9304 | 85.9158 | -0.0017949 | 18.2776 | 3.8151 | -39.8115 | 3.1228 | 11742.54 | 0.34 | 1.3792 | -1.9382 | -2.2984 | -2.3765 | 6.0777 | 5.782 | 6.5748 | 78.6515 | 132.3649 | 47.456 | 86.9214 | 11.4906 | 105.7697 | 35.7534
42810.4515 | 989 | 17.7216 | 18.11 | 18.2155 | 18.2451 | 17.5733 | 16.1953 | 14.6849 | 16.4974 | 17.0004 | 17.1231 | 17.1408 | 16.6634 | 15.684 | 14.3708 | 15.0772 | 23.5605 | 24.7441 | 78.9418 | 28.1075 | 89.2262 |  |  |  | 19.3205 | 77.0896 | 260.8089 | 666.1706 | 706.8518 | 677.31 | 102.2395 | 116.4523 | 1037.81 | 98.6166 | 117.0947 | 902.0712 | 868.2747 | 912.0114 |  | 255.8837 | 1008.8718 | 1013.3715 | 512.4255 |  | 402.3279 | 665.0719 | 487.2493 | 641.6499 | 772.3253 | 952.117 | 1006.0511 | 45.596 | 393.5971 | 74.1012 | 610.1562 | 13.617 | 52.748 | 48.4742 | 49.7045 | 60.5847 |  |  | 0.38332 | -0.3771 | -0.95885 | -0.63609 | 6.8145 | 6.0831 | 6.939 | -2.3868 | 22.2644 | 54.2625 | 22.2418 | 0.00022013 | 0.00026285 | -0.00082304 | 19.4381 | 16.3357 | 16.8746 | 17.244 | 17.2291 | 16.198 | 14.6138 | 16.6841 | 17.0529 | 17.3733 | 17.4408 | 17.1593 | 16.3348 | 14.5781 | 909.4785 | 557.5707 | 638.6818 | 375.858 | 301.2133 | 860.6225 | 539.3542 | 15.9155 | 22.6823 | 27.1265 | 50.0479 | 77.3709 | 83.0314 |  |  |  | 613.4065 | 567.2112 | 570.8776 | 594.4833 | 122.1227 | 39.1688 | 807.3107 |  |  | 474.7003 |  |  | 18.0578 | 41.7601 | 355.7988 | 17.1794 | 39.8288 | 933.6842 | 743.0352 | 610.267 | 802.8662 | 802.4834 | 739.3153 |  | 805.7704 | 831.8516 | 954.9346 | 593.5495 | 672.3177 | 847.6685 |  | 985.0218 |  |  | 446.9695 | 650.364 | 734.5466 | [6 empty] | 601.9384 |  |  | 412.1715 |  |  | 484.7653 | 655.4398 | 666.3849 | 861.8445 | 1033.2625 | 1007.4519 | 546.4567 | 724.0156 | 800.1426 | 611.2782 | 678.8947 | 986.2052 | 1040.2946 | 643.728 | 799.1956 | 867.7577 | 1110.9931 | 1075.614 | 525.3719 | 620.7927 | 696.8992 | 606.4691 | 749.7959 | 889.9428 | 1036.3582 | 1115.7353 | 582.1177 | 670.2274 | 685.2926 | 858.6716 | 83.3363 | 0.0028423 | 18.2777 | 3.8236 | -39.7475 | 3.1228 | 11836.71 | 0.23 | 1.3302 | -1.3108 | -2.0902 | -1.7025 | 6.3679 | 6.0165 | 6.4259 | 78.6777 | 132.3912 | 47.4955 | 88.2602 | 13.6743 | 106.1284 | 35.5531
42810.4515 | 990 | 17.715 | 18.1058 | 18.2176 | 18.2498 | 17.5638 | 16.1938 | 14.6801 | 16.4971 | 16.9997 | 17.1199 | 17.1367 | 16.6626 | 15.6839 | 14.3726 | 15.1069 | 23.6886 | 24.8644 | 79.1855 | 28.237 | 89.2622 |  |  |  | 19.3782 | 77.2434 | 260.1945 | 666.5291 | 707.7768 | 677.1025 | 99.313 | 118.9238 | 1048.0571 | 98.1382 | 113.9391 | 895.2069 | 877.5504 | 901.6137 |  | 277.0789 | 1003.6604 | 1013.4034 | 511.7289 |  | 402.7223 | 664.0215 | 486.4838 | 639.8062 | 768.2831 | 950.8453 | 1006.6514 | 45.7048 | 394.3158 | 74.7941 | 610.6483 | 13.5888 | 52.7805 | 48.4853 | 49.7052 | 60.8792 |  |  | -0.074033 | 0.023743 | 0.08202 | -0.94953 | 6.8946 | 4.489 | 7.7282 | -3.7339 | 23.322 | 55.7512 | 22.1673 | 0.00024313 | 0.00026613 | -0.00080989 | 19.4651 | 16.3283 | 16.8625 | 17.2344 | 17.2134 | 16.187 | 14.6023 | 16.6811 | 17.043 | 17.3665 | 17.4218 | 17.1463 | 16.3267 | 14.5622 | 907.7576 | 575.1731 | 576.5863 | 353.0657 | 287.6111 | 861.8832 | 539.4433 | 15.9269 | 22.7802 | 27.2396 | 50.4005 | 77.4878 | 83.0894 |  |  |  | 613.9266 | 572.3554 | 574.1762 | 602.2287 | 127.0529 | 57.2512 | 807.2065 |  |  | 472.6229 |  |  | 18.0725 | 41.8821 | 357.4039 | 17.2005 | 39.9993 | 936.271 | 742.9682 | 610.5838 | 805.4752 | 805.0218 | 739.6053 |  | 805.7176 | 829.6706 | 955.8976 | 594.12 | 672.5047 | 841.1373 |  | 984.9616 |  |  | 446.8516 | 652.9686 | 734.3642 | [6 empty] | 602.2342 |  |  | 412.613 |  |  | 484.4224 | 656.1241 | 666.4054 | 861.2273 | 1037.2227 | 1005.1642 | 546.0833 | 722.8708 | 798.8105 | 611.332 | 678.8288 | 987.1694 | 1043.8091 | 643.5419 | 798.0738 | 867.9156 | 1112.6709 | 1076.9467 | 525.5364 | 621.3899 | 697.9524 | 610.5257 | 756.3602 | 888.4602 | 1038.4453 | 1116.0122 | 582.0874 | 670.6069 | 696.2596 | 864.1506 | 94.608 | -0.00073558 | 18.276 | 3.8618 | -39.8341 | 3.1229 | 11864.81 | 0.33 | -0.58452 | 0.32873 | 0.61099 | -2.0789 | 6.4019 | 5.1657 | 6.7779 | 78.6531 | 132.8836 | 47.5207 | 89.0088 | 20.5946 | 109.5722 | 35.4347
42810.4515 | 991 | 17.706 | 18.09 | 18.2112 | 18.2408 | 17.5566 | 16.1897 | 14.6787 | 16.492 | 16.9959 | 17.1157 | 17.1215 | 16.6494 | 15.6662 | 14.3706 | 15.1462 | 23.8247 | 24.984 | 79.4172 | 28.3378 | 89.2728 |  |  |  | 19.456 | 77.4004 | 259.7581 | 665.8323 | 708.6472 | 676.017 | 99.9903 | 119.7083 | 1057.4897 | 101.721 | 117.698 | 897.6906 | 772.6676 | 903.7733 |  | 249.9629 | 1018.5094 | 1023.2248 | 508.7229 |  | 402.9539 | 665.6556 | 488.7819 | 642.9255 | 769.6917 | 948.464 | 1008.305 | 46.0626 | 395.3084 | 75.6258 | 611.2146 | 13.5215 | 52.8195 | 48.4984 | 49.7169 | 61.2121 |  |  | 0.41618 | -0.79305 | -0.82217 | -0.734 | 7.2074 | 5.5495 | 6.9022 | -2.9697 | 21.2585 | 55.5784 | 22.0363 | 0.00028913 | 0.00026613 | -0.00083125 | 19.5103 | 16.3377 | 16.8644 | 17.2383 | 17.2211 | 16.195 | 14.6176 | 16.6796 | 17.0493 | 17.3691 | 17.4262 | 17.1534 | 16.3289 | 14.5687 | 932.4185 | 565.6125 | 600.6151 | 370.6371 | 292.433 | 863.6258 | 540.4766 | 15.9397 | 22.8658 | 27.3562 | 50.7411 | 77.5866 | 83.1582 |  |  |  | 614.2549 | 574.6018 | 575.4788 | 603.5714 | 124.1345 | 54.722 | 808.6111 |  |  | 467.9134 |  |  | 18.0797 | 42.0006 | 356.3776 | 17.211 | 40.1679 | 947.161 | 742.9182 | 610.8554 | 808.6486 | 808.7816 | 739.071 |  | 805.7705 | 830.1733 | 957.5953 | 594.734 | 672.6506 | 838.1537 |  | 985.3966 |  |  | 446.6578 | 654.4103 | 734.5381 | [6 empty] | 602.6163 |  |  | 413.9737 |  |  | 484.1515 | 656.3641 | 665.7507 | 861.2268 | 1043.9304 | 1006.2899 | 545.8061 | 722.9603 | 797.9537 | 611.5112 | 678.3003 | 999.8431 | 1050.8553 | 643.5919 | 798.3139 | 867.2435 | 1111.949 | 1075.1945 | 525.5554 | 621.7434 | 696.1757 | 612.1345 | 769.3021 | 888.009 | 1039.5719 | 1112.5965 | 582.0696 | 669.4143 | 700.3464 | 866.9647 | 96.5355 | -0.001416 | 18.2775 | 3.9231 | -39.8491 | 3.1228 | 11985.13 | 0.17 | 1.3851 | -1.9015 | -1.9361 | -1.8294 | 6.5392 | 5.738 | 6.3993 | 78.6845 | 133.6331 | 47.5357 | 87.0416 | 18.1655 | 75.1594 | 35.4585
42810.4515 | 992 | 17.6949 | 18.0837 | 18.2124 | 18.2331 | 17.5588 | 16.1897 | 14.6806 | 16.4844 | 16.9861 | 17.1144 | 17.119 | 16.6432 | 15.6654 | 14.3613 | 15.1719 | 23.9591 | 25.1004 | 79.6226 | 28.4086 | 89.2679 |  |  |  | 19.5138 | 77.5392 | 261.9404 | 666.0019 | 709.8838 | 675.1351 | 98.4431 | 118.4932 | 1064.2881 | 101.035 | 118.4127 | 893.7576 | 710.4954 | 903.6616 |  | 244.1727 | 1020.1438 | 1024.1187 | 516.3028 |  | 403.7531 | 666.7962 | 491.6754 | 646.8745 | 775.1217 | 951.9037 | 1011.2574 | 46.3638 | 396.025 | 75.9129 | 611.5308 | 13.4432 | 52.7968 | 48.4915 | 49.7068 | 61.4793 |  |  | 0.58637 | -1.6151 | -0.53764 | -1.0829 | 5.8623 | 5.9872 | 7.4555 | -3.5177 | 21.788 | 54.3842 | 22.3622 | 0.0002957 | 0.00032199 | -0.00080989 | 19.5448 | 16.3394 | 16.8649 | 17.2358 | 17.2244 | 16.1907 | 14.6172 | 16.6834 | 17.0515 | 17.3704 | 17.4326 | 17.1584 | 16.3313 | 14.5662 | 933.7486 | 554.5459 | 610.9561 | 378.7485 | 304.7188 | 864.7106 | 541.6614 | 15.9526 | 22.95 | 27.4671 | 51.091 | 77.6871 | 83.2198 |  |  |  | 614.2078 | 574.2842 | 575.3227 | 599.5707 | 128.8605 | 57.3579 | 811.954 |  |  | 470.1077 |  |  | 18.0953 | 42.1228 | 360.1082 | 17.2265 | 40.3403 | 945.8157 | 745.9501 | 610.9365 | 810.6641 | 810.9059 | 741.4375 |  | 806.416 | 833.401 | 959.503 | 595.1276 | 672.7548 | 838.3331 |  | 985.7591 |  |  | 447.2523 | 659.576 | 736.5581 | [6 empty] | 602.8238 |  |  | 415.2675 |  |  | 484.6427 | 656.3235 | 664.8773 | 861.9907 | 1052.9724 | 1008.9705 | 545.3254 | 723.7613 | 797.6573 | 612.2128 | 677.6415 | 1004.2255 | 1058.9161 | 643.5488 | 799.2736 | 868.7915 | 1109.6135 | 1071.5975 | 525.8342 | 621.6835 | 694.7008 | 612.6498 | 770.2616 | 887.8538 | 1038.6613 | 1111.1124 | 582.0876 | 667.6777 | 699.8669 | 864.3027 | 93.6488 | -0.00048301 | 18.2775 | 3.9776 | -39.8725 | 3.1228 | 12039.75 | 0.37 | 1.6433 | -2.7153 | -1.5666 | -2.2234 | 5.9058 | 5.9684 | 6.6601 | 78.8208 | 134.4049 | 47.5476 | 87.3763 | 17.2932 | 58.475 | 35.5609
42810.4515 | 993 | 17.6933 | 18.0945 | 18.2152 | 18.2327 | 17.5635 | 16.1941 | 14.6868 | 16.4909 | 16.9956 | 17.1114 | 17.1251 | 16.6532 | 15.6725 | 14.3726 | 15.1962 | 24.0983 | 25.2202 | 79.8286 | 28.494 | 89.2708 |  |  |  | 19.5826 | 77.6672 | 264.5535 | 665.0616 | 710.5796 | 673.1521 | 95.9082 | 118.2035 | 1058.3813 | 98.6104 | 116.2291 | 886.7457 | 720.92 | 897.7111 |  | 236.5724 | 1026.6235 | 1028.3977 | 513.4472 |  | 404.9845 | 667.687 | 493.7607 | 647.9606 | 778.6656 | 955.6518 | 1012.0327 | 46.6582 | 396.5603 | 76.1948 | 611.8313 | 13.4045 | 52.7571 | 48.5004 | 49.6934 | 61.2662 |  |  | -0.30205 | -0.67609 | -1.0344 | -1.5731 | 6.4879 | 5.7467 | 7.6625 | -3.0058 | 23.0996 | 56.4291 | 21.9407 | 0.00025792 | 0.00026449 | -0.00084275 | 19.5774 | 16.3317 | 16.862 | 17.2299 | 17.2147 | 16.184 | 14.6095 | 16.6771 | 17.043 | 17.3653 | 17.4313 | 17.1518 | 16.3244 | 14.5659 | 922.8073 | 551.589 | 618.9248 | 380.4314 | 311.8996 | 865.247 | 543.1617 | 15.9547 | 23.0353 | 27.572 | 51.4516 | 77.7806 | 83.2735 |  |  |  | 613.7839 | 571.904 | 573.483 | 593.0873 | 113.6712 | 48.1536 | 813.8346 |  |  | 470.8855 |  |  | 18.1046 | 42.2384 | 363.9787 | 17.2334 | 40.5005 | 950.0435 | 749.9757 | 611.159 | 813.3673 | 814.1365 | 747.5357 |  | 807.7375 | 839.8177 | 961.2338 | 595.3022 | 673.0182 | 843.3793 |  | 986.2038 |  |  | 448.6282 | 666.0169 | 741.5215 | [6 empty] | 603.155 |  |  | 416.7201 |  |  | 485.4126 | 656.6932 | 663.6626 | 860.8211 | 1057.8426 | 1016.8645 | 544.6667 | 724.9627 | 796.839 | 613.5604 | 677.9299 | 1004.2085 | 1064.9216 | 643.5795 | 799.9358 | 869.9991 | 1108.8489 | 1069.9396 | 525.5179 | 621.327 | 692.7756 | 613.1432 | 770.1832 | 888.742 | 1038.5745 | 1112.6279 | 581.7922 | 666.8462 | 698.9231 | 865.3034 | 96.0122 | -0.00020942 | 18.2772 | 4.0212 | -39.8842 | 3.1228 | 12097.99 | 0.29 | -1.1782 | -1.7576 | -2.1741 | -2.6811 | 6.2224 | 5.8562 | 6.7623 | 79.0659 | 135.0115 | 47.6007 | 88.831 | 16.7591 | 61.1301 | 35.6621
42810.4515 | 994 | 17.7001 | 18.0904 | 18.2114 | 18.2402 | 17.5668 | 16.193 | 14.6975 | 16.5008 | 16.9977 | 17.1224 | 17.1267 | 16.6556 | 15.6811 | 14.3745 | 15.2351 | 24.2347 | 25.354 | 80.0315 | 28.6174 | 89.2864 |  |  |  | 19.665 | 77.8314 | 265.0673 | 663.2391 | 710.4364 | 669.9667 | 93.9209 | 115.7425 | 1041.3288 | 97.9065 | 114.8263 | 878.5286 | 687.7834 | 888.0081 |  | 234.8909 | 1017.6642 | 1022.6505 | 497.0431 |  | 405.9482 | 666.601 | 493.0876 | 646.8905 | 772.0909 | 956.3093 | 1011.365 | 46.8372 | 397.3251 | 76.8674 | 612.4004 | 13.3697 | 52.7503 | 48.5034 | 49.6839 | 60.7364 |  |  | -0.077977 | -0.4934 | -1.135 | -0.80037 | 6.9308 | 5.0817 | 7.472 | -3.2529 | 23.4291 | 57.2066 | 21.8229 | 0.00026449 | 0.00027435 | -0.00084768 | 19.6194 | 16.3291 | 16.8564 | 17.2329 | 17.2143 | 16.1922 | 14.6085 | 16.6716 | 17.0449 | 17.3619 | 17.4308 | 17.1486 | 16.321 | 14.566 | 910.2405 | 516.8893 | 605.978 | 369.3964 | 303.763 | 865.5034 | 543.8815 | 15.9662 | 23.1366 | 27.6827 | 51.8232 | 77.8796 | 83.3346 |  |  |  | 613.2037 | 568.9435 | 571.3334 | 588.019 | 144.4964 | 58.5268 | 819.0073 |  |  | 468.5196 |  |  | 18.1295 | 42.3652 | 366.4292 | 17.2548 | 40.6794 | 943.1845 | 751.4449 | 612.095 | 813.9122 | 814.9623 | 749.1042 |  | 808.6805 | 847.5632 | 961.9954 | 595.7254 | 673.3513 | 850.508 |  | 987.2055 |  |  | 448.1074 | 668.163 | 744.0641 | [6 empty] | 604.014 |  |  | 417.7112 |  |  | 485.4663 | 657.1718 | 662.8071 | 863.5874 | 1061.209 | 1020.1425 | 543.8573 | 726.4842 | 796.4067 | 613.6373 | 678.43 | 1008.0494 | 1072.138 | 642.8489 | 802.3838 | 874.0538 | 1112.0443 | 1072.1392 | 525.2639 | 621.1827 | 690.059 | 613.238 | 767.9913 | 885.5665 | 1042.5855 | 1115.5765 | 581.3121 | 665.1694 | 700.2079 | 859.9247 | 95.1434 | -0.00018138 | 18.2765 | 4.0549 | -39.8167 | 3.1228 | 12067.92 | 0.3 | -0.59763 | -1.5006 | -2.276 | -1.9113 | 6.433 | 5.5084 | 6.6795 | 79.3189 | 135.1427 | 47.6622 | 90.3416 | 18.3665 | 53.6439 | 35.695
42810.4516 | 995 | 17.6947 | 18.0863 | 18.2089 | 18.2345 | 17.5624 | 16.1895 | 14.7002 | 16.4984 | 16.9948 | 17.1114 | 17.1336 | 16.6562 | 15.6791 | 14.3707 | 15.2722 | 24.3754 | 25.4904 | 80.2311 | 28.7253 | 89.3079 |  |  |  | 19.743 | 77.975 | 265.377 | 661.918 | 709.3325 | 668.8374 | 93.2972 | 113.1689 | 1029.7578 | 95.4985 | 113.5435 | 870.4603 | 683.756 | 879.4019 |  | 238.7109 | 1013.3088 | 1019.006 | 480.4344 |  | 405.6602 | 666.1118 | 492.5906 | 647.9773 | 767.8879 | 955.025 | 1012.2151 | 47.1177 | 398.1048 | 77.5207 | 612.8956 | 13.3317 | 52.7622 | 48.495 | 49.6572 | 59.9474 |  |  | -0.050377 | -0.83642 | -1.3965 | -0.25627 | 6.9728 | 5.8354 | 7.8932 | -2.4427 | 22.3432 | 56.6047 | 21.4662 | 0.00024313 | 0.00023985 | -0.00084275 | 19.6645 | 16.332 | 16.8523 | 17.2379 | 17.2129 | 16.1885 | 14.6144 | 16.6715 | 17.047 | 17.3674 | 17.4316 | 17.1534 | 16.3324 | 14.5714 | 927.6591 | 505.707 | 610.3143 | 374.1698 | 304.1383 | 868.4579 | 545.149 | 15.9835 | 23.2294 | 27.8059 | 52.1944 | 77.9733 | 83.4015 |  |  |  | 612.3249 | 565.4316 | 569.2116 | 581.0138 | 138.4415 | 50.7858 | 820.2812 |  |  | 469.3268 |  |  | 18.1349 | 42.4775 | 367.3299 | 17.2387 | 40.8461 | 937.516 | 752.9276 | 613.1214 | 815.3359 | 817.5468 | 750.883 |  | 809.7065 | 854.572 | 962.4054 | 596.4497 | 673.7703 | 856.8861 |  | 988.1675 |  |  | 448.1682 | 669.7319 | 745.5715 | [6 empty] | 604.8809 |  |  | 418.0526 |  |  | 485.2329 | 656.5098 | 662.0429 | 864.7927 | 1064.8464 | 1021.2601 | 543.3381 | 727.3426 | 796.173 | 612.9675 | 677.929 | 1014.7313 | 1070.8831 | 642.8661 | 804.9025 | 875.7181 | 1114.7373 | 1073.9718 | 524.7622 | 621.0291 | 686.7817 | 613.7424 | 774.6414 | 884.7295 | 1044.809 | 1116.8288 | 580.6648 | 664.1698 | 698.8347 | 862.9677 | 94.841 | -4.8061e-05 | 18.2776 | 4.0726 | -39.737 | 3.1228 | 11957.93 | 0.31 | -0.48007 | -1.9533 | -2.5239 | -1.0812 | 6.4491 | 5.8997 | 6.8616 | 79.5931 | 135.1347 | 47.7344 | 89.7276 | 18.1827 | 53.1879 | 35.7266
42810.4516 | 996 | 17.6922 | 18.083 | 18.2047 | 18.2309 | 17.5655 | 16.1844 | 14.6964 | 16.4949 | 16.9934 | 17.1105 | 17.1345 | 16.6548 | 15.6705 | 14.3736 | 15.3035 | 24.5227 | 25.611 | 80.4219 | 28.8276 | 89.3183 |  |  |  | 19.8154 | 78.1115 | 267.0035 | 661.5703 | 708.0171 | 668.2096 | 95.7513 | 112.891 | 1021.1151 | 93.3328 | 111.9538 | 864.6487 | 818.5347 | 874.2062 |  | 241.3779 | 1009.6463 | 1015.672 | 487.9116 |  | 405.8386 | 666.1243 | 492.5271 | 651.2725 | 773.2881 | 959.8474 | 1014.3289 | 46.7238 | 398.8749 | 78.2143 | 613.4707 | 13.294 | 52.7843 | 48.5049 | 49.6374 | 59.0892 |  |  | 0.19604 | -0.76611 | -0.50742 | -0.61572 | 6.9603 | 5.5141 | 8.252 | -3.4632 | 23.3195 | 57.1693 | 20.8994 | 0.00024971 | 0.00028913 | -0.00080661 | 19.7108 | 16.3334 | 16.8592 | 17.2322 | 17.2155 | 16.1927 | 14.6181 | 16.6805 | 17.0484 | 17.3707 | 17.4327 | 17.1561 | 16.3403 | 14.5693 | 938.0965 | 496.1055 | 603.7854 | 370.2692 | 303.9178 | 871.1678 | 546.3253 | 15.9877 | 23.3173 | 27.91 | 52.5059 | 78.0517 | 83.4575 |  |  |  | 611.3307 | 562.1928 | 567.5138 | 574.5842 | 141.9659 | 59.0619 | 823.6334 |  |  | 472.018 |  |  | 18.1549 | 42.5942 | 368.8656 | 17.2767 | 41.0221 | 929.7206 | 752.6838 | 614.3705 | 819.2753 | 822.5472 | 750.7368 |  | 810.4879 | 868.4897 | 962.9337 | 597.766 | 674.3507 | 865.6035 |  | 989.0328 |  |  | 447.7219 | 668.1787 | 745.6018 | [6 empty] | 606.2673 |  |  | 418.7355 |  |  | 485.2193 | 655.6134 | 661.2224 | 865.6634 | 1069.1483 | 1022.9804 | 542.7522 | 729.5721 | 796.9987 | 612.2189 | 677.156 | 1015.949 | 1073.7065 | 642.5209 | 807.7366 | 873.8449 | 1116.1808 | 1079.3606 | 524.2476 | 621.077 | 684.9325 | 613.4161 | 772.3133 | 882.2452 | 1043.8192 | 1119.0496 | 580.388 | 663.8328 | 698.1324 | 862.6119 | 84.9514 | 0.00021152 | 18.2774 | 4.0881 | -39.8431 | 3.1227 | 11826.9 | 0.3 | 0.94671 | -1.8694 | -1.5214 | -1.6759 | 6.456 | 5.7462 | 7.0295 | 79.8441 | 134.9889 | 47.8258 | 89.7866 | 19.1853 | 89.7166 | 35.7213
42810.4516 | 997 | 17.6849 | 18.0887 | 18.2015 | 18.2398 | 17.5666 | 16.1866 | 14.7054 | 16.4987 | 16.9961 | 17.1249 | 17.1338 | 16.6533 | 15.6793 | 14.3796 | 15.344 | 24.6693 | 25.7414 | 80.619 | 28.9327 | 89.3452 |  |  |  | 19.8882 | 78.2473 | 267.3708 | 661.675 | 708.5467 | 668.7487 | 97.5365 | 115.6062 | 1024.2282 | 93.7283 | 112.8195 | 868.7455 | 878.6136 | 878.0542 |  | 255.0495 | 1014.4783 | 1020.2319 | 506.4529 |  | 406.6015 | 667.3573 | 492.0065 | 649.6322 | 777.9644 | 963.5642 | 1016.4419 | 45.8624 | 399.7797 | 78.0924 | 614.2409 | 13.2496 | 52.7849 | 48.4872 | 49.6024 | 58.3729 |  |  | 0.16318 | -0.064965 | -0.97528 | -0.82337 | 8.1201 | 5.0672 | 6.9798 | -3.6373 | 23.9535 | 57.5606 | 20.6303 | 0.00024313 | 0.00024971 | -0.00081318 | 19.7504 | 16.3284 | 16.8533 | 17.234 | 17.2111 | 16.1888 | 14.6166 | 16.6824 | 17.0441 | 17.3713 | 17.4296 | 17.1596 | 16.3379 | 14.574 | 937.7289 | 495.4506 | 627.4193 | 388.0462 | 313.9097 | 873.6907 | 548.1987 | 16.0077 | 23.4107 | 28.021 | 52.8324 | 78.1313 | 83.5153 |  |  |  | 610.3018 | 559.286 | 566.0324 | 570.0154 | 117.2558 | 45.1524 | 829.1068 |  |  | 472.8596 |  |  | 18.1629 | 42.7152 | 368.6777 | 17.2924 | 41.1823 | 936.9643 | 752.1211 | 615.8922 | 821.1421 | 826.6521 | 750.3084 |  | 810.929 | 874.3385 | 963.1373 | 598.7643 | 674.7801 | 870.2586 |  | 990.5747 |  |  | 447.4287 | 667.6508 | 745.1256 | [6 empty] | 607.7351 |  |  | 420.0288 |  |  | 485.1516 | 654.9513 | 661.1208 | 869.9603 | 1068.397 | 1026.902 | 541.7772 | 728.33 | 796.9444 | 611.4654 | 677.3593 | 1020.904 | 1074.1786 | 641.6013 | 806.5046 | 874.4174 | 1118.4135 | 1079.8754 | 524.0106 | 621.0172 | 684.2564 | 613.3917 | 772.9205 | 883.021 | 1044.7748 | 1119.3614 | 579.8639 | 663.6584 | 698.9513 | 873.1576 | 83.864 | 0.00069554 | 18.2768 | 4.0963 | -39.8743 | 3.1227 | 11771.97 | 0.26 | 0.86399 | -0.54474 | -2.1106 | -1.9393 | 6.9837 | 5.5168 | 6.4747 | 79.9956 | 134.9193 | 47.8929 | 90.968 | 17.0021 | 110.1162 | 35.6584
42810.4516 | 998 | 17.6904 | 18.0875 | 18.1985 | 18.228 | 17.5609 | 16.1888 | 14.7007 | 16.4973 | 16.9929 | 17.1198 | 17.1312 | 16.654 | 15.6834 | 14.3748 | 15.3823 | 24.8096 | 25.8731 | 80.8493 | 29.0784 | 89.4102 |  |  |  | 19.9692 | 78.383 | 269.0949 | 663.4285 | 708.6733 | 671.7973 | 95.3908 | 115.7974 | 1033.1466 | 96.5943 | 114.5178 | 875.5079 | 881.322 | 881.076 |  | 267.9639 | 1014.0293 | 1011.0001 | 527.1953 |  | 408.606 | 668.1479 | 493.3308 | 650.6166 | 784.0358 | 965.415 | 1017.1947 | 44.9993 | 400.8796 | 75.9553 | 614.8443 | 13.2367 | 52.7943 | 48.4927 | 49.5908 | 57.563 |  |  | 0.15924 | -0.016341 | -0.40162 | -0.78591 | 7.7226 | 5.3787 | 7.376 | -2.4584 | 22.3047 | 54.5709 | 20.0746 | 0.00019056 | 0.00023985 | -0.00081646 | 19.793 | 16.3275 | 16.8497 | 17.2323 | 17.2149 | 16.1874 | 14.6136 | 16.6823 | 17.0445 | 17.3694 | 17.434 | 17.1622 | 16.3325 | 14.5744 | 923.9031 | 484.1214 | 604.9246 | 372.4909 | 295.8037 | 874.3027 | 548.8346 | 16.0246 | 23.5004 | 28.1334 | 53.1427 | 78.2135 | 83.5715 |  |  |  | 609.4134 | 557.2666 | 564.8005 | 569.5666 | 117.3012 | 62.282 | 832.8403 |  |  | 481.2592 |  |  | 18.1699 | 42.8386 | 368.5233 | 17.3032 | 41.348 | 943.2902 | 750.6577 | 616.1954 | 832.9024 | 840.226 | 748.6697 |  | 810.7922 | 889.1273 | 964.4025 | 599.2331 | 675.2095 | 876.015 |  | 992.9071 |  |  | 446.6454 | 666.8711 | 743.7622 | [6 empty] | 608.3542 |  |  | 419.8918 |  |  | 485.2048 | 655.0884 | 660.9965 | 875.258 | 1069.9277 | 1027.6604 | 540.9083 | 727.3331 | 797.6756 | 610.9023 | 677.1217 | 1031.1898 | 1069.3085 | 640.9221 | 807.3471 | 874.023 | 1120.3288 | 1078.6532 | 523.5449 | 620.9786 | 683.846 | 614.012 | 775.1228 | 885.864 | 1048.7906 | 1118.7795 | 579.355 | 664.2857 | 701.402 | 875.5712 | 82.7157 | -0.00027956 | 18.2771 | 4.0993 | -39.8669 | 3.1227 | 11688.55 | 0.28 | 0.85487 | -0.27332 | -1.355 | -1.8955 | 6.8157 | 5.6881 | 6.661 | 79.9978 | 135.0867 | 47.9748 | 92.7818 | 19.6522 | 110.5571 | 35.5075
42810.4516 | 999 | 17.6936 | 18.0891 | 18.2012 | 18.2317 | 17.5578 | 16.1801 | 14.6956 | 16.4869 | 16.9899 | 17.1199 | 17.1226 | 16.6523 | 15.6761 | 14.3776 | 15.4244 | 24.9505 | 26.0009 | 81.0738 | 29.1836 | 89.4644 |  |  |  | 20.0509 | 78.5267 | 269.3443 | 664.2732 | 709.5908 | 674.0489 | 97.4008 | 116.285 | 1027.1352 | 101.8108 | 120.6619 | 897.7958 | 810.2758 | 904.9531 |  | 270.1458 | 1006.7213 | 1014.8263 | 566.3366 |  | 408.4483 | 669.0262 | 495.194 | 654.4457 | 780.3537 | 965.4877 | 1014.3297 | 44.6718 | 401.9922 | 74.3067 | 615.8059 | 13.2242 | 52.8541 | 48.4862 | 49.5794 | 56.9194 |  |  | 0.26044 | 0.063827 | -0.27085 | -0.33053 | 7.3717 | 6.1041 | 7.3773 | -3.1425 | 22.6766 | 55.0574 | 20.1578 | 0.00023492 | 0.00025299 | -0.00080332 | 19.8392 | 16.3333 | 16.853 | 17.2324 | 17.2205 | 16.2007 | 14.6182 | 16.6837 | 17.0487 | 17.3791 | 17.433 | 17.1619 | 16.3412 | 14.5798 | 910.4245 | 472.8891 | 609.4054 | 385.7694 | 300.5613 | 873.7402 | 549.8085 | 16.0415 | 23.5943 | 28.2572 | 53.4715 | 78.2801 | 83.6391 |  |  |  | 608.7485 | 555.8004 | 564.1553 | 572.5676 | 104.8919 | 42.3441 | 845.0311 |  |  | 485.0542 |  |  | 18.1891 | 42.9491 | 367.9869 | 17.3257 | 41.5132 | 934.0979 | 748.8469 | 615.7753 | 844.04 | 853.2888 | 746.5167 |  | 810.3835 | 903.2004 | 966.7407 | 598.9257 | 675.5553 | 887.0923 |  | 994.5864 |  |  | 446.1685 | 664.9198 | 741.9421 | [6 empty] | 607.6786 |  |  | 418.7776 |  |  | 485.3159 | 655.6412 | 661.1844 | 878.655 | 1076.4282 | 1024.866 | 539.8616 | 727.4802 | 798.7287 | 610.5422 | 676.576 | 1037.3322 | 1065.6985 | 640.6353 | 808.5317 | 878.0356 | 1122.7798 | 1076.455 | 523.0033 | 621.0172 | 684.2974 | 613.8852 | 780.3505 | 888.7401 | 1051.7187 | 1118.9879 | 579.1174 | 664.655 | 701.9678 | 879.1581 | 88.4005 | 0.00033778 | 18.2774 | 4.1072 | -39.7675 | 3.1226 | 11664.8 | 0.36 | 1.0946 | 0.54042 | -1.1133 | -1.2298 | 6.6592 | 6.0597 | 6.6618 | 79.9283 | 135.7687 | 48.0599 | 94.0243 | 19.3854 | 84.8993 | 35.3021
42810.4516 | 1000 | 17.6784 | 18.0814 | 18.1882 | 18.2286 | 17.551 | 16.1825 | 14.6998 | 16.4893 | 16.9886 | 17.1105 | 17.1264 | 16.6528 | 15.6728 | 14.3757 | 15.4584 | 25.0928 | 26.1199 | 81.286 | 29.2719 | 89.505 |  |  |  | 20.1258 | 78.6624 | 271.0874 | 665.6244 | 711.5177 | 675.9269 | 87.2089 | 120.482 | 1025.6536 | 90.9623 | 113.6955 | 896.6087 | 876.3064 | 909.8427 |  | 267.0455 | 1013.1093 | 1012.1842 | 573.999 |  | 409.0911 | 669.13 | 497.5751 | 657.0352 | 783.2389 | 965.4142 | 1012.8726 | 45.2702 | 402.9964 | 73.2047 | 617.0111 | 13.2226 | 52.9403 | 48.498 | 49.5813 | 56.4391 |  |  | -0.28234 | -0.65046 | -0.65921 | -0.96925 | 6.7356 | 5.5088 | 7.5357 | -3.0262 | 23.4657 | 57.7125 | 20.1421 | 0.00022013 | 0.0002727 | -0.00080825 | 19.8727 | 16.3304 | 16.8483 | 17.223 | 17.2239 | 16.2012 | 14.6192 | 16.6808 | 17.0477 | 17.3731 | 17.4365 | 17.1628 | 16.3432 | 14.5747 | 892.3535 | 451.5474 | 564.2913 | 378.465 | 294.3086 | 872.3999 | 549.613 | 16.0559 | 23.7047 | 28.3738 | 53.8302 | 78.3788 | 83.7022 |  |  |  | 608.1819 | 554.9441 | 564.3547 | 572.7289 | 114.555 | 45.9784 | 856.6979 |  |  | 484.7926 |  |  | 18.1919 | 43.069 | 368.9643 | 17.3263 | 41.6741 | 935.5404 | 746.4207 | 615.6326 | 846.2006 | 852.2746 | 742.8406 |  | 809.9277 | 915.5328 | 968.7812 | 598.6978 | 675.8947 | 900.279 |  | 995.4886 |  |  | 445.4355 | 662.4379 | 739.6171 | [6 empty] | 607.2225 |  |  | 417.4864 |  |  | 485.5043 | 656.4212 | 661.1973 | 881.8064 | 1077.8873 | 1021.9832 | 539.0943 | 728.0361 | 799.3366 | 610.607 | 676.4676 | 1043.678 | 1066.295 | 639.7494 | 808.8126 | 880.65 | 1124.0577 | 1076.6156 | 522.6724 | 621.1891 | 684.3575 | 612.4038 | 780.6183 | 892.6249 | 1053.8056 | 1119.0622 | 578.81 | 664.7647 | 701.2556 | 881.0455 | 88.9257 | -0.0010442 | 18.2772 | 4.1242 | -39.8668 | 3.1226 | 11660.15 | 0.31 | -1.1408 | -1.7253 | -1.7369 | -2.1061 | 6.3652 | 5.7565 | 6.7327 | 79.8863 | 136.3671 | 48.1414 | 95.4255 | 24.3516 | 107.3787 | 35.1939
42810.4516 | 1001 | 17.6838 | 18.0809 | 18.203 | 18.2402 | 17.5597 | 16.1994 | 14.7081 | 16.5038 | 16.995 | 17.1232 | 17.1375 | 16.6533 | 15.6844 | 14.3835 | 15.4987 | 25.2408 | 26.2489 | 81.486 | 29.3578 | 89.531 |  |  |  | 20.2087 | 78.8047 | 272.2849 | 666.6647 | 712.684 | 676.8019 | 85.8453 | 111.7733 | 1021.0615 | 98.0092 | 114.5936 | 889.9997 | 888.4271 | 908.0956 |  | 253.4214 | 1020.7709 | 1026.8683 | 541.3402 |  | 408.3441 | 670.4328 | 499.2302 | 661.075 | 777.4141 | 963.005 | 1013.1167 | 45.5323 | 404.1574 | 72.8365 | 618.4162 | 13.2162 | 53.0017 | 48.494 | 49.5792 | 55.9299 |  |  | -0.21203 | 0.15911 | -0.60992 | -1.1105 | 7.3658 | 6.0673 | 7.8327 | -2.8507 | 22.9976 | 56.3829 | 19.6956 | 0.00025299 | 0.00027599 | -0.00082796 | 19.9108 | 16.3285 | 16.8557 | 17.2261 | 17.2207 | 16.1947 | 14.6249 | 16.6811 | 17.0505 | 17.3676 | 17.432 | 17.1591 | 16.3392 | 14.5773 | 877.0507 | 451.9167 | 572.7103 | 382.0707 | 292.4418 | 871.022 | 549.9586 | 16.0649 | 23.7892 | 28.4855 | 54.1614 | 78.4628 | 83.7503 |  |  |  | 607.6278 | 554.8717 | 563.9546 | 573.6775 | 115.6676 | 50.0238 | 858.7374 |  |  | 487.5665 |  |  | 18.2152 | 43.1938 | 370.3679 | 17.3499 | 41.838 | 940.6098 | 747.1421 | 615.8271 | 843.8462 | 850.9064 | 741.5655 |  | 809.9564 | 922.0678 | 969.1718 | 598.7516 | 676.2696 | 903.7876 |  | 996.1505 |  |  | 445.1243 | 660.8862 | 738.6528 | [6 empty] | 607.3835 |  |  | 416.9647 |  |  | 485.7937 | 657.4739 | 660.8621 | 886.0984 | 1083.9831 | 1024.2054 | 538.3948 | 728.1166 | 799.7967 | 611.0785 | 676.6568 | 1045.1255 | 1073.9732 | 638.6348 | 808.4659 | 881.8186 | 1123.9508 | 1079.9586 | 522.3913 | 621.5361 | 684.6776 | 611.3868 | 780.9455 | 896.4641 | 1056.2651 | 1119.7586 | 578.7086 | 665.1163 | 700.929 | 886.1882 | 91.8602 | -9.0163e-05 | 18.2761 | 4.1383 | -39.881 | 3.1226 | 11616.22 | 0.33 | -0.98904 | 0.8539 | -1.6718 | -2.2559 | 6.6499 | 6.0354 | 6.8574 | 79.9308 | 136.3662 | 48.223 | 96.5038 | 23.4983 | 112.864 | 35.0662
42810.4516 | 1002 | 17.6748 | 18.0786 | 18.196 | 18.229 | 17.5523 | 16.1913 | 14.7075 | 16.4903 | 16.9951 | 17.115 | 17.1315 | 16.6554 | 15.682 | 14.3833 | 15.5382 | 25.3765 | 26.3777 | 81.6583 | 29.4411 | 89.5411 |  |  |  | 20.2889 | 78.9463 | 274.0706 | 667.5347 | 713.907 | 677.1649 | 86.0514 | 107.9295 | 1025.0758 | 98.6685 | 118.1291 | 892.5203 | 865.2633 | 904.8754 |  | 248.1658 | 1027.2708 | 1037.9235 | 487.2066 |  | 408.185 | 670.3118 | 499.5833 | 662.6301 | 772.6259 | 965.1215 | 1013.97 | 45.1315 | 404.9464 | 73.2304 | 619.4732 | 13.2143 | 53.028 | 48.4883 | 49.5838 | 55.4629 |  |  | -0.14172 | 0.23928 | -0.73083 | -0.95216 | 8.2844 | 6.6837 | 8.1961 | -3.1721 | 22.3483 | 56.6758 | 19.3461 | 0.00022999 | 0.00026449 | -0.00084275 | 19.9518 | 16.3282 | 16.8448 | 17.2198 | 17.2192 | 16.1903 | 14.6169 | 16.6761 | 17.0431 | 17.357 | 17.428 | 17.1576 | 16.3348 | 14.5812 | 868.5151 | 428.9864 | 552.4994 | 380.3347 | 297.3286 | 869.7138 | 549.9981 | 16.0806 | 23.8781 | 28.5927 | 54.5073 | 78.5451 | 83.8113 |  |  |  | 607.4045 | 555.6986 | 564.5027 | 578.7938 | 110.7609 | 46.852 | 860.1656 |  |  | 497.5005 |  |  | 18.2213 | 43.3017 | 372.9695 | 17.3603 | 42.0053 | 948.8942 | 748.0863 | 616.1592 | 852.4813 | 862.455 | 742.7279 |  | 810.2827 | 928.1089 | 969.5093 | 599.1096 | 676.6243 | 906.9566 |  | 997.5948 |  |  | 445.1201 | 661.6406 | 739.9358 | [6 empty] | 607.8735 |  |  | 418.4742 |  |  | 485.9779 | 658.7263 | 660.3296 | 888.9267 | 1086.1127 | 1027.9774 | 537.6277 | 727.7369 | 800.4035 | 611.8991 | 677.0105 | 1041.1179 | 1077.8137 | 637.6613 | 808.2449 | 881.8386 | 1123.7857 | 1082.6817 | 522.2932 | 621.9483 | 684.93 | 609.9697 | 780.0274 | 897.4092 | 1056.4133 | 1120.2852 | 578.4468 | 666.358 | 699.4733 | 884.9089 | 93.2848 | -0.00049002 | 18.2773 | 4.1629 | -39.8466 | 3.1226 | 11580.66 | 0.27 | -0.80875 | 1.0471 | -1.8299 | -2.0887 | 7.0584 | 6.3399 | 7.0207 | 80.0017 | 136.3546 | 48.2918 | 96.8631 | 25.7533 | 105.7336 | 34.8833
42810.4516 | 1003 | 17.6685 | 18.0696 | 18.1831 | 18.2255 | 17.5474 | 16.1896 | 14.7072 | 16.4876 | 16.987 | 17.113 | 17.1283 | 16.6536 | 15.6729 | 14.3765 | 15.5773 | 25.5223 | 26.516 | 81.8277 | 29.5256 | 89.5448 |  |  |  | 20.3731 | 79.0921 | 275.2766 | 668.1078 | 714.4691 | 676.9363 | 98.6741 | 114.3942 | 1032.5449 | 94.7776 | 114.8317 | 881.0044 | 832.5525 | 894.0046 |  | 255.0884 | 1029.701 | 1039.4672 | 499.4629 |  | 408.5738 | 670.7395 | 500.3999 | 662.5729 | 771.4611 | 966.7549 | 1015.2195 | 44.4044 | 405.6699 | 74.2042 | 620.1604 | 13.2757 | 53.0105 | 48.4971 | 49.5825 | 54.9996 |  |  | -0.168 | 0.3569 | -0.64606 | -1.2551 | 6.3558 | 5.4694 | 6.6539 | -3.7227 | 22.8406 | 56.5252 | 19.7447 | 0.00021192 | 0.00022342 | -0.00082139 | 19.9961 | 16.3376 | 16.8468 | 17.2335 | 17.2201 | 16.1926 | 14.6176 | 16.6864 | 17.0398 | 17.3714 | 17.4317 | 17.167 | 16.3409 | 14.5809 | 870.0025 | 427.3568 | 574.2217 | 367.1826 | 287.6208 | 868.659 | 549.9176 | 16.1005 | 23.9854 | 28.7158 | 54.8712 | 78.6422 | 83.8758 |  |  |  | 607.3856 | 556.8253 | 564.8346 | 582.6268 | 106.1317 | 45.6553 | 867.2246 |  |  | 509.6648 |  |  | 18.2396 | 43.4169 | 374.304 | 17.3722 | 42.1716 | 944.8217 | 748.8723 | 616.5291 | 868.4467 | 879.7468 | 743.6101 |  | 810.6856 | 926.1704 | 971.4753 | 599.341 | 677.0179 | 906.8262 |  | 999.4526 |  |  | 445.0837 | 663.2163 | 741.171 | [6 empty] | 608.3933 |  |  | 419.9801 |  |  | 485.8588 | 659.4522 | 659.8634 | 889.9178 | 1081.6422 | 1028.3879 | 536.6841 | 727.3783 | 800.6319 | 612.5632 | 677.4807 | 1038.7577 | 1073.3029 | 636.7828 | 807.601 | 885.0167 | 1126.0541 | 1082.0889 | 522.1784 | 622.2313 | 685.0451 | 608.6851 | 777.4831 | 898.8253 | 1055.8219 | 1121.7953 | 578.3382 | 668.0974 | 697.5174 | 883.225 | 98.2919 | -0.0010583 | 18.2776 | 4.1751 | -39.8316 | 3.1226 | 11548.63 | 0.27 | -0.88045 | 1.2791 | -1.7209 | -2.3986 | 6.1865 | 5.7389 | 6.3299 | 80.1046 | 137.3207 | 48.3728 | 96.224 | 23.3206 | 94.0018 | 34.7733
42810.4517 | 1004 | 17.6693 | 18.0645 | 18.1845 | 18.2192 | 17.5511 | 16.1815 | 14.7091 | 16.4848 | 16.9839 | 17.1143 | 17.1234 | 16.6524 | 15.6793 | 14.3755 | 15.6201 | 25.6721 | 26.6468 | 82.0017 | 29.6363 | 89.5355 |  |  |  | 20.4629 | 79.2402 | 277.3357 | 668.1134 | 714.8418 | 676.1886 | 98.9215 | 117.4273 | 1040.2947 | 95.3837 | 114.6156 | 875.6287 | 794.3659 | 887.8881 |  | 255.1481 | 1037.1108 | 1045.9022 | 520.7894 |  | 409.2108 | 671.1728 | 500.1807 | 662.1312 | 767.2415 | 964.7683 | 1014.6836 | 44.2313 | 406.5975 | 75.7634 | 620.8629 | 13.3936 | 52.9264 | 48.4801 | 49.5851 | 54.7542 |  |  | 0.16515 | -0.9547 | -0.71046 | -0.95676 | 8.2634 | 5.171 | 7.6303 | -3.1287 | 23.4341 | 57.3904 | 20.0026 | 0.00024806 | 0.00028585 | -0.00080825 | 20.0362 | 16.3259 | 16.8455 | 17.2149 | 17.2083 | 16.1874 | 14.6175 | 16.6788 | 17.0448 | 17.3627 | 17.4281 | 17.1635 | 16.3361 | 14.5846 | 871.6639 | 419.7097 | 556.8302 | 343.876 | 278.7143 | 866.8938 | 549.1589 | 16.1082 | 24.0755 | 28.8348 | 55.2779 | 78.7238 | 83.9335 |  |  |  | 607.3548 | 557.4708 | 564.524 | 583.8099 | 108.5233 | 37.0449 | 886.2883 |  |  | 512.6042 |  |  | 18.2518 | 43.5258 | 376.8302 | 17.4091 | 42.3284 | 953.6004 | 750.1713 | 616.6446 | 872.6222 | 880.8189 | 744.6407 |  | 811.2538 | 928.4379 | 974.1566 | 599.3856 | 677.3804 | 907.9354 |  | 999.9317 |  |  | 444.7299 | 663.6252 | 742.2108 | [6 empty] | 608.6126 |  |  | 420.2969 |  |  | 485.6019 | 659.6835 | 659.2118 | 889.9818 | 1074.2334 | 1025.7491 | 536.028 | 727.0486 | 801.0826 | 613.2858 | 678.2334 | 1035.6786 | 1067.9079 | 636.0031 | 808.665 | 886.7388 | 1126.5635 | 1080.4877 | 522.5236 | 622.7316 | 684.552 | 607.2257 | 775.0374 | 900.6184 | 1054.8615 | 1121.3596 | 578.4987 | 668.3199 | 694.8575 | 881.7935 | 87.0787 | -0.00031465 | 18.277 | 4.1959 | -39.9011 | 3.1226 | 11545.93 | 0.36 | 0.87262 | -2.0925 | -1.8051 | -2.0947 | 7.0484 | 5.5757 | 6.7731 | 80.256 | 138.5085 | 48.4523 | 95.2488 | 25.0729 | 81.2337 | 34.7348
42810.4517 | 1005 | 17.6678 | 18.0658 | 18.1868 | 18.2252 | 17.5491 | 16.1822 | 14.7148 | 16.488 | 16.9864 | 17.12 | 17.1305 | 16.6528 | 15.6778 | 14.3742 | 15.6651 | 25.8256 | 26.7758 | 82.1731 | 29.7535 | 89.5488 |  |  |  | 20.5431 | 79.3851 | 278.5254 | 668.1125 | 714.2947 | 676.1169 | 94.0846 | 118.8581 | 1040.0771 | 97.5706 | 113.1979 | 867.025 | 877.0282 | 878.4779 |  | 262.4312 | 1026.3924 | 1036.6212 | 507.9644 |  | 410.6559 | 672.3651 | 500.6061 | 659.9454 | 770.3524 | 963.4357 | 1014.5034 | 44.4409 | 407.5557 | 76.7267 | 621.5251 | 13.4136 | 52.8145 | 48.4694 | 49.5752 | 54.7758 |  |  | -0.092433 | -1.0901 | -0.55801 | -1.0047 | 7.0858 | 5.633 | 7.0521 | -3.2595 | 23.0918 | 57.2205 | 20.3456 | 0.00022835 | 0.00022013 | -0.00080497 | 20.081 | 16.3341 | 16.8491 | 17.2312 | 17.218 | 16.192 | 14.6227 | 16.6821 | 17.0497 | 17.3707 | 17.4405 | 17.1662 | 16.3418 | 14.5894 | 874.8414 | 392.256 | 527.8277 | 322.9283 | 264.1333 | 865.6123 | 547.6988 | 16.1155 | 24.1693 | 28.9423 | 55.6842 | 78.8059 | 83.9841 |  |  |  | 606.9529 | 556.2567 | 563.344 | 579.5636 | 116.1097 | 41.5442 | 887.1703 |  |  | 513.7562 |  |  | 18.261 | 43.6594 | 378.5912 | 17.401 | 42.495 | 945.7195 | 751.023 | 617.273 | 877.6635 | 887.452 | 745.3309 |  | 811.9029 | 929.4236 | 975.5967 | 599.8181 | 677.8101 | 905.7008 |  | 999.702 |  |  | 443.9258 | 661.5927 | 742.9015 | [6 empty] | 609.1897 |  |  | 420.2631 |  |  | 485.5815 | 660.0644 | 658.4412 | 889.8141 | 1070.6016 | 1024.0886 | 535.2401 | 726.5445 | 801.478 | 613.1152 | 678.9817 | 1040.8285 | 1068.0497 | 635.2814 | 809.3303 | 885.613 | 1124.6501 | 1078.2227 | 522.6936 | 623.1003 | 684.3447 | 604.9015 | 771.9277 | 898.13 | 1054.228 | 1120.2329 | 578.4108 | 669.2052 | 691.2763 | 876.4856 | 91.1031 | 0.00012731 | 18.2761 | 4.2235 | -39.9628 | 3.1226 | 11535.03 | 0.3 | -0.65279 | -2.2373 | -1.6007 | -2.148 | 6.5234 | 5.8163 | 6.5078 | 80.4427 | 139.156 | 48.5359 | 94.3234 | 27.9495 | 109.4819 | 34.7794
42810.4517 | 1006 | 17.6702 | 18.0734 | 18.1861 | 18.2227 | 17.5484 | 16.1866 | 14.7246 | 16.491 | 16.9896 | 17.1247 | 17.1347 | 16.661 | 15.6832 | 14.3935 | 15.7134 | 25.9754 | 26.9067 | 82.3183 | 29.8664 | 89.5952 |  |  |  | 20.6342 | 79.5339 | 278.6339 | 666.9397 | 713.0595 | 674.5907 | 93.4393 | 115.6504 | 1034.405 | 98.5055 | 116.4059 | 866.201 | 840.0102 | 872.0245 |  | 265.0973 | 1020.1666 | 1031.5034 | 504.9809 |  | 413.334 | 671.8233 | 502.43 | 661.2761 | 766.8356 | 962.4356 | 1013.3197 | 44.8108 | 408.599 | 77.4177 | 622.4043 | 13.464 | 52.6941 | 48.4703 | 49.5734 | 54.8284 |  |  | -0.12003 | -1.2267 | -0.73215 | -0.63937 | 7.3237 | 5.4674 | 7.3254 | -3.6156 | 23.1035 | 57.0084 | 20.6552 | 0.00019056 | 0.00027763 | -0.00078197 | 20.1163 | 16.3292 | 16.8444 | 17.2213 | 17.2103 | 16.1882 | 14.615 | 16.6775 | 17.0498 | 17.3659 | 17.4353 | 17.1598 | 16.3396 | 14.5852 | 875.9303 | 397.4101 | 541.6707 | 339.4759 | 280.6911 | 865.0818 | 547.2959 | 16.1465 | 24.2711 | 29.0642 | 56.0622 | 78.8997 | 84.0341 |  |  |  | 606.3714 | 554.7986 | 562.2498 | 575.0128 | 116.2177 | 50.3654 | 892.7712 |  |  | 517.5803 |  |  | 18.2842 | 43.7716 | 378.845 | 17.4235 | 42.6515 | 941.1482 | 750.186 | 618.486 | 875.5455 | 883.7218 | 744.0402 |  | 812.2277 | 926.7219 | 976.7085 | 601.2056 | 678.439 | 902.502 |  | 1001.0564 |  |  | 443.4033 | 658.5034 | 741.9705 | [6 empty] | 610.3026 |  |  | 420.8066 |  |  | 485.7656 | 660.3564 | 658.6739 | 891.0037 | 1074.5796 | 1024.328 | 534.2331 | 726.0383 | 801.2733 | 613.0872 | 679.7454 | 1039.5918 | 1069.0124 | 634.7249 | 809.6812 | 884.8121 | 1124.4138 | 1075.7421 | 522.7688 | 623.6578 | 683.7294 | 602.9248 | 768.5579 | 893.5162 | 1053.053 | 1119.342 | 578.4532 | 669.8667 | 688.9299 | 871.4429 | 92.9927 | -0.0019001 | 18.2773 | 4.254 | -39.8812 | 3.1226 | 11491.89 | 0.36 | -0.7433 | -2.3728 | -1.8331 | -1.713 | 6.6293 | 5.7279 | 6.6301 | 80.5818 | 139.7536 | 48.6376 | 93.9659 | 26.3161 | 96.3654 | 34.7999
42810.4517 | 1007 | 17.6599 | 18.0632 | 18.1811 | 18.2217 | 17.5454 | 16.1918 | 14.714 | 16.4926 | 16.9904 | 17.1291 | 17.1287 | 16.6532 | 15.6703 | 14.3849 | 15.7682 | 26.1256 | 27.0352 | 82.4631 | 29.9844 | 89.6235 |  |  |  | 20.7268 | 79.6665 | 279.9056 | 666.356 | 712.5381 | 674.4052 | 92.8881 | 111.84 | 1023.2938 | 92.2684 | 116.3374 | 863.444 | 748.5188 | 874.3155 |  | 262.6051 | 1017.9075 | 1028.1317 | 528.2726 |  | 413.3837 | 670.482 | 501.4056 | 659.067 | 761.7126 | 954.1828 | 1010.4473 | 44.9591 | 409.28 | 77.5321 | 622.8956 | 13.5175 | 52.5964 | 48.4745 | 49.5746 | 54.6468 |  |  | 0.13493 | -1.8707 | -0.65855 | -1.1368 | 7.1509 | 5.3156 | 8.1889 | -2.8198 | 22.1817 | 56.2212 | 20.8942 | 0.00021356 | 0.00019056 | -0.00082304 | 20.1559 | 16.3258 | 16.8413 | 17.2139 | 17.2102 | 16.1826 | 14.6156 | 16.6737 | 17.0449 | 17.3666 | 17.4328 | 17.1629 | 16.3378 | 14.5885 | 879.9923 | 420.2126 | 574.2317 | 352.9475 | 292.0531 | 864.4202 | 547.0923 | 16.1592 | 24.3648 | 29.1756 | 56.4311 | 78.9841 | 84.0958 |  |  |  | 605.6199 | 552.7291 | 561.5812 | 569.9765 | 128.4387 | 47.5198 | 889.3132 |  |  | 513.6229 |  |  | 18.2881 | 43.8706 | 380.4571 | 17.4335 | 42.8223 | 938.6684 | 750.51 | 619.9925 | 872.0443 | 878.0887 | 744.7833 |  | 812.5134 | 923.7298 | 978.3242 | 602.5674 | 679.0108 | 904.1197 |  | 1002.8728 |  |  | 442.8514 | 654.6434 | 741.6061 | [6 empty] | 611.9437 |  |  | 421.7459 |  |  | 486.5709 | 660.5971 | 658.8484 | 890.8865 | 1073.5032 | 1026.6537 | 533.3939 | 726.1878 | 801.2765 | 614.3003 | 680.5096 | 1038.5471 | 1071.6681 | 634.7198 | 810.8409 | 884.9454 | 1125.0446 | 1075.537 | 522.8307 | 623.7271 | 682.3755 | 602.0504 | 767.5744 | 894.229 | 1053.2544 | 1119.9561 | 578.088 | 669.7004 | 688.8393 | 874.8886 | 90.4463 | -0.0005181 | 18.2774 | 4.2969 | -39.836 | 3.1226 | 11459.98 | 0.27 | 0.78799 | -2.928 | -1.7373 | -2.2825 | 6.5287 | 5.6289 | 6.9865 | 80.6519 | 140.5984 | 48.7275 | 93.22 | 22.6501 | 67.8945 | 34.8031
42810.4517 | 1008 | 17.6577 | 18.061 | 18.1874 | 18.2185 | 17.5416 | 16.1787 | 14.73 | 16.4896 | 16.992 | 17.1235 | 17.1251 | 16.6572 | 15.6763 | 14.386 | 15.8205 | 26.2839 | 27.1802 | 82.6137 | 30.1286 | 89.6751 |  |  |  | 20.8249 | 79.823 | 280.3015 | 665.9117 | 711.722 | 674.3293 | 91.8917 | 114.9694 | 1027.9858 | 94.6933 | 114.266 | 858.7128 | 791.7098 | 872.3067 |  | 241.3732 | 1020.2223 | 1030.354 | 519.5693 |  | 412.0161 | 671.2159 | 501.9751 | 659.0998 | 763.7557 | 951.8577 | 1009.9615 | 45.1076 | 409.7831 | 77.0034 | 623.1768 | 13.5716 | 52.5243 | 48.4716 | 49.5912 | 54.4743 |  |  | -0.30271 | -0.18982 | -0.66906 | -0.17677 | 6.9557 | 5.1342 | 8.1784 | -2.9966 | 22.7945 | 55.7015 | 20.6015 | 0.00024971 | 0.00018071 | -0.00081811 | 20.2096 | 16.3388 | 16.8486 | 17.225 | 17.2178 | 16.1959 | 14.6259 | 16.6839 | 17.0558 | 17.3751 | 17.4422 | 17.1737 | 16.3518 | 14.6023 | 897.1296 | 459.0924 | 584.2359 | 357.5891 | 287.8062 | 865.5798 | 547.3396 | 16.1748 | 24.4583 | 29.2874 | 56.7974 | 79.0608 | 84.1366 |  |  |  | 604.7825 | 550.7784 | 560.9336 | 566.1993 | 149.1218 | 61.683 | 883.6215 |  |  | 509.3056 |  |  | 18.3031 | 44.0064 | 380.3687 | 17.4545 | 42.9744 | 938.1697 | 749.0778 | 620.9694 | 861.6039 | 864.6566 | 743.3157 |  | 812.5744 | 911.7436 | 979.4643 | 603.4396 | 679.5382 | 899.8817 |  | 1004.148 |  |  | 442.1059 | 650.6459 | 740.9712 | [6 empty] | 612.9621 |  |  | 421.6732 |  |  | 487.0801 | 660.7011 | 659.3136 | 889.7478 | 1072.5742 | 1030.0818 | 532.4419 | 725.7612 | 802.1087 | 614.2206 | 680.8706 | 1037.7077 | 1078.6481 | 634.4669 | 812.0568 | 881.6777 | 1124.4285 | 1074.8925 | 522.4826 | 623.8959 | 682.0918 | 601.8915 | 767.3934 | 895.8973 | 1051.3429 | 1121.5444 | 577.6173 | 669.4099 | 689.849 | 875.0182 | 93.3135 | 0.00040091 | 18.2774 | 4.3418 | -39.827 | 3.1226 | 11499.22 | 0.24 | -1.1802 | -0.93305 | -1.7517 | -0.9004 | 6.4329 | 5.5268 | 6.9754 | 80.7121 | 141.4705 | 48.8213 | 91.8324 | 21.597 | 80.4637 | 34.7561
42810.4517 | 1009 | 17.6597 | 18.0619 | 18.1784 | 18.2129 | 17.5383 | 16.1795 | 14.7186 | 16.4836 | 16.9817 | 17.1103 | 17.1204 | 16.6498 | 15.6728 | 14.3817 | 15.8724 | 26.4316 | 27.3067 | 82.754 | 30.2505 | 89.7297 |  |  |  | 20.9174 | 79.9878 | 281.349 | 666.0721 | 712.1464 | 674.5524 | 89.8397 | 113.7124 | 1027.2024 | 95.055 | 116.5024 | 860.4796 | 762.7022 | 871.8888 |  | 249.6008 | 1023.2975 | 1038.3586 | 484.3281 |  | 411.4375 | 672.4429 | 503.4095 | 660.1034 | 764.5499 | 947.9078 | 1009.2167 | 45.58 | 410.2996 | 78.377 | 623.6494 | 13.6218 | 52.4651 | 48.4656 | 49.6019 | 54.3078 |  |  | 0.019275 | -0.69711 | -0.67958 | -1.0008 | 6.9656 | 5.4096 | 8.1462 | -2.9513 | 22.9194 | 56.1119 | 20.9701 | 0.00018728 | 0.00024478 | -0.00080497 | 20.2411 | 16.3283 | 16.836 | 17.2186 | 17.2112 | 16.1838 | 14.6145 | 16.6766 | 17.0547 | 17.3681 | 17.4251 | 17.1643 | 16.3481 | 14.5928 | 921.8636 | 516.4276 | 590.7547 | 355.9866 | 294.5436 | 868.3915 | 548.5765 | 16.1977 | 24.5677 | 29.4169 | 57.1687 | 79.1374 | 84.189 |  |  |  | 603.8008 | 549.0027 | 560.3238 | 563.7502 | 138.9346 | 55.8661 | 870.6148 |  |  | 506.3185 |  |  | 18.3124 | 44.1168 | 382.2702 | 17.4595 | 43.1424 | 940.5817 | 749.3245 | 622.0928 | 851.4752 | 854.1916 | 741.1654 |  | 812.9134 | 897.12 | 979.3034 | 604.3051 | 680.2097 | 892.4563 |  | 1005.6467 |  |  | 441.898 | 648.5883 | 739.5016 | [6 empty] | 613.9364 |  |  | 421.7243 |  |  | 487.1452 | 659.8201 | 659.853 | 891.3649 | 1073.2506 | 1037.4512 | 531.046 | 725.3283 | 804.3294 | 613.1583 | 680.4601 | 1034.7053 | 1088.4671 | 633.7368 | 813.2527 | 881.7968 | 1124.9409 | 1074.4021 | 521.6975 | 623.7845 | 681.5859 | 601.5819 | 769.8933 | 895.2569 | 1051.7562 | 1125.382 | 577.3257 | 668.3164 | 691.2165 | 879.8918 | 94.8137 | 0.001825 | 18.2764 | 4.3916 | -39.8324 | 3.1226 | 11505.63 | 0.2 | 0.29785 | -1.7892 | -1.7666 | -2.1438 | 6.4271 | 5.6639 | 6.9504 | 80.8797 | 141.8006 | 48.9478 | 90.3417 | 21.1654 | 73.0117 | 34.6464
42810.4517 | 1010 | 17.6587 | 18.0629 | 18.1806 | 18.2172 | 17.5413 | 16.1746 | 14.7187 | 16.4845 | 16.9833 | 17.1175 | 17.1165 | 16.6532 | 15.6748 | 14.3774 | 15.9165 | 26.5772 | 27.4439 | 82.8973 | 30.3679 | 89.7928 |  |  |  | 21.0197 | 80.1322 | 285.343 | 667.0572 | 714.8585 | 675.9319 | 95.1677 | 113.0393 | 1022.8327 | 92.125 | 114.4065 | 861.5905 | 788.0566 | 875.5838 |  | 258.2838 | 1017.0244 | 1031.091 | 499.303 |  | 412.5247 | 671.7056 | 504.7989 | 659.9612 | 760.5425 | 944.2376 | 1007.6676 | 45.7132 | 410.7554 | 79.7458 | 624.2683 | 13.6721 | 52.4503 | 48.4705 | 49.6104 | 54.2026 |  |  | 0.37609 | -0.2943 | -0.91614 | -0.81022 | 7.806 | 5.2538 | 7.8156 | -3.2384 | 23.149 | 56.6496 | 20.6271 | 0.00026449 | 0.00026613 | -0.00079182 | 20.2928 | 16.3214 | 16.8368 | 17.2136 | 17.2041 | 16.1853 | 14.6153 | 16.6702 | 17.0405 | 17.3673 | 17.4251 | 17.1628 | 16.3411 | 14.5819 | 935.1106 | 615.1306 | 623.0618 | 367.6665 | 301.577 | 871.2489 | 550.3918 | 16.2055 | 24.6643 | 29.5292 | 57.5063 | 79.2161 | 84.2423 |  |  |  | 603.0528 | 548.1893 | 560.021 | 564.0421 | 134.8642 | 57.3239 | 860.9911 |  |  | 503.8143 |  |  | 18.3355 | 44.231 | 385.2879 | 17.4871 | 43.3086 | 936.3402 | 752.6507 | 622.7795 | 848.1972 | 853.2379 | 744.6685 |  | 813.9899 | 894.2313 | 979.1435 | 605.0599 | 680.9328 | 888.0242 |  | 1007.051 |  |  | 441.5782 | 650.4872 | 742.0629 | [6 empty] | 614.7454 |  |  | 420.8544 |  |  | 486.8723 | 659.8557 | 659.6144 | 890.4534 | 1073.3421 | 1044.599 | 529.9851 | 726.5606 | 807.0364 | 613.2096 | 679.9461 | 1036.972 | 1092.6503 | 633.7605 | 817.1704 | 883.8738 | 1125.965 | 1074.5877 | 520.8722 | 623.5815 | 681.2224 | 599.8785 | 770.3017 | 897.8948 | 1053.3468 | 1127.2741 | 576.9919 | 668.1316 | 689.4462 | 882.8534 | 103.9791 | -0.00040586 | 18.2769 | 4.4413 | -39.9096 | 3.1226 | 11483.18 | 0.38 | 1.3166 | -1.1621 | -2.0504 | -1.9282 | 6.7936 | 5.5734 | 6.7977 | 81.1255 | 141.8052 | 49.0891 | 90.1549 | 18.0066 | 79.9299 | 34.5033
42810.4517 | 1011 | 17.6575 | 18.0579 | 18.1835 | 18.2195 | 17.5483 | 16.1828 | 14.7212 | 16.4866 | 16.9829 | 17.1198 | 17.1237 | 16.6616 | 15.6784 | 14.3858 | 15.9774 | 26.747 | 27.5815 | 83.0502 | 30.5079 | 89.8762 |  |  |  | 21.1136 | 80.2921 | 286.9765 | 668.2418 | 714.5038 | 676.659 | 98.0195 | 115.6357 | 1015.3916 | 91.1966 | 110.8079 | 856.8235 | 867.9427 | 873.6936 |  | 250.4574 | 1011.36 | 1024.0282 | 511.9914 |  | 413.6708 | 671.0708 | 507.6929 | 663.4364 | 763.7289 | 937.97 | 1004.4935 | 46.0554 | 411.3635 | 79.8965 | 625.1583 | 13.7028 | 52.4408 | 48.4621 | 49.6161 | 54.3173 |  |  | 0.25912 | -0.32321 | -0.4969 | -0.75568 | 5.8623 | 5.7178 | 7.4181 | -3.4323 | 23.8547 | 57.9212 | 20.65 | 0.00022342 | 0.00024313 | -0.00083454 | 20.3479 | 16.3268 | 16.8432 | 17.2231 | 17.2109 | 16.1892 | 14.6215 | 16.6762 | 17.0576 | 17.3708 | 17.4357 | 17.1718 | 16.3483 | 14.5925 | 936.5361 | 587.1098 | 633.6766 | 374.317 | 297.6838 | 874.0265 | 552.2557 | 16.2166 | 24.7548 | 29.6446 | 57.8377 | 79.2895 | 84.2788 |  |  |  | 602.4837 | 547.8318 | 560.1106 | 566.5256 | 172.1229 | 61.2444 | 858.2847 |  |  | 509.9264 |  |  | 18.3445 | 44.3342 | 389.3193 | 17.4888 | 43.4642 | 931.8917 | 754.9853 | 622.727 | 855.7065 | 862.9946 | 749.8395 |  | 815.206 | 897.3189 | 979.5833 | 604.7689 | 681.5084 | 888.8489 |  | 1007.9531 |  |  | 441.3247 | 653.7226 | 745.2682 | [6 empty] | 614.686 |  |  | 419.3797 |  |  | 486.4509 | 660.9609 | 660.0637 | 886.2086 | 1078.1732 | 1046.273 | 529.6034 | 728.3341 | 808.4554 | 613.9794 | 680.1893 | 1032.4632 | 1094.9005 | 633.2138 | 818.224 | 884.86 | 1127.0547 | 1074.1507 | 520.4741 | 623.8193 | 681.4696 | 599.4819 | 767.4625 | 895.0354 | 1053.3449 | 1132.4006 | 577.1457 | 668.5415 | 689.8254 | 879.4741 | 87.0978 | -0.00053913 | 18.2772 | 4.4825 | -39.9617 | 3.1225 | 11454.12 | 0.33 | 1.0933 | -1.2174 | -1.5095 | -1.8615 | 5.8721 | 5.7993 | 6.6055 | 81.3707 | 141.9276 | 49.2267 | 91.2528 | 17.2712 | 106.0193 | 34.3317
42810.4517 | 1012 | 17.6555 | 18.0599 | 18.1787 | 18.216 | 17.5499 | 16.1828 | 14.7244 | 16.4843 | 16.9843 | 17.1224 | 17.1294 | 16.6534 | 15.6823 | 14.3892 | 16.0281 | 26.904 | 27.7138 | 83.1977 | 30.637 | 89.9267 |  |  |  | 21.2072 | 80.4506 | 285.2908 | 666.8377 | 713.2981 | 675.7381 | 95.6598 | 118.5864 | 1017.2109 | 93.1261 | 108.9297 | 854.0859 | 896.9984 | 872.978 |  | 260.7449 | 1011.569 | 1025.8885 | 508.368 |  | 413.4898 | 670.6815 | 507.4893 | 666.7836 | 772.0026 | 941.2194 | 1011.6058 | 46.7501 | 411.8601 | 81.3171 | 625.9762 | 13.738 | 52.4962 | 48.4729 | 49.6393 | 54.4675 |  |  | 0.12639 | -0.8351 | -0.10066 | -1.3458 | 7.0957 | 5.9136 | 7.4463 | -2.555 | 23.4419 | 56.8472 | 20.4771 | 0.00024478 | 0.00023328 | -0.00079347 | 20.3865 | 16.3305 | 16.8453 | 17.2235 | 17.2071 | 16.1888 | 14.6248 | 16.6833 | 17.0512 | 17.376 | 17.4432 | 17.1719 | 16.353 | 14.6009 | 962.3487 | 639.7255 | 655.3462 | 388.5724 | 293.5262 | 879.3349 | 555.6118 | 16.2316 | 24.8514 | 29.7546 | 58.1936 | 79.347 | 84.3263 |  |  |  | 601.9315 | 547.8621 | 560.462 | 567.6349 | 139.8384 | 66.7527 | 865.6852 |  |  | 507.4911 |  |  | 18.3569 | 44.4554 | 386.5304 | 17.5186 | 43.6131 | 928.5917 | 755.048 | 623.8276 | 855.8325 | 862.102 | 752.1483 |  | 816.0972 | 904.4774 | 980.6386 | 605.5778 | 682.2571 | 899.4226 |  | 1008.915 |  |  | 440.7927 | 654.8989 | 747.1306 | [6 empty] | 615.3808 |  |  | 419.051 |  |  | 486.1025 | 661.8921 | 660.6062 | 885.6445 | 1077.6318 | 1047.5151 | 528.4864 | 727.9533 | 809.2471 | 614.0123 | 681.3474 | 1030.8897 | 1091.3941 | 632.0482 | 817.748 | 883.7666 | 1127.832 | 1075.5617 | 520.8691 | 624.8938 | 680.9627 | 598.9845 | 768.0033 | 897.2166 | 1052.4839 | 1133.2163 | 577.5783 | 668.2393 | 690.5868 | 882.9867 | 94.2191 | 3.6099e-05 | 18.2776 | 4.5205 | -39.9234 | 3.1226 | 11385.38 | 0.37 | 0.76318 | -1.9565 | -0.67927 | -2.4837 | 6.469 | 5.9057 | 6.627 | 81.5922 | 142.2292 | 49.3729 | 90.8048 | 15.6671 | 117.0986 | 34.2016
42810.4518 | 1013 | 17.6525 | 18.0532 | 18.1787 | 18.2179 | 17.5512 | 16.1795 | 14.7304 | 16.4835 | 16.9845 | 17.1173 | 17.1228 | 16.6533 | 15.6776 | 14.3944 | 16.0872 | 27.0568 | 27.8463 | 83.3177 | 30.7683 | 89.9635 |  |  |  | 21.3026 | 80.597 | 286.9787 | 667.1313 | 714.7476 | 675.8835 | 91.6206 | 118.2479 | 1022.2276 | 98.5093 | 117.6638 | 867.6529 | 878.116 | 877.6274 |  | 272.6417 | 997.8345 | 1018.3042 | 519.8034 |  | 414.0666 | 671.3667 | 509.1762 | 668.3547 | 776.7841 | 950.4687 | 1018.0402 | 47.2484 | 412.2987 | 81.5795 | 626.9363 | 13.76 | 52.5938 | 48.4913 | 49.6536 | 54.6708 |  |  | -0.056293 | -1.0815 | -0.80706 | -0.72611 | 7.5728 | 5.7651 | 7.5534 | -1.6226 | 23.4086 | 58.6586 | 20.2965 | 0.00020535 | 0.00023492 | -0.00083125 | 20.4239 | 16.3274 | 16.8322 | 17.209 | 17.2066 | 16.1778 | 14.6215 | 16.6783 | 17.0433 | 17.3719 | 17.4333 | 17.162 | 16.3467 | 14.5883 | 957.8959 | 675.7498 | 636.2068 | 396.3878 | 295.8709 | 882.4179 | 557.9808 | 16.2563 | 24.954 | 29.8702 | 58.6024 | 79.4353 | 84.3666 |  |  |  | 601.3983 | 548.5667 | 561.0774 | 569.1016 | 129.4639 | 57.0653 | 868.3237 |  |  | 503.9382 |  |  | 18.3727 | 44.5733 | 387.8043 | 17.5386 | 43.7751 | 927.942 | 752.6222 | 625.1428 | 849.9524 | 853.3918 | 748.4953 |  | 816.2714 | 904.4946 | 981.521 | 607.1479 | 683.1192 | 901.4128 |  | 1009.813 |  |  | 440.076 | 651.1607 | 745.0518 | [6 empty] | 616.555 |  |  | 419.2359 |  |  | 485.9037 | 663.1034 | 660.933 | 889.5985 | 1076.1875 | 1046.9552 | 527.7652 | 726.0501 | 810.2485 | 614.555 | 682.8299 | 1037.7302 | 1095.1048 | 631.3726 | 817.3925 | 883.5156 | 1128.6575 | 1079.16 | 520.9556 | 625.3773 | 680.0331 | 597.8838 | 770.5804 | 904.2541 | 1052.151 | 1132.8689 | 577.4257 | 667.1104 | 691.3776 | 892.5302 | 87.9876 | -0.0013249 | 18.2766 | 4.5446 | -39.968 | 3.1225 | 11336.6 | 0.18 | -0.50937 | -2.2274 | -1.9241 | -1.825 | 6.7084 | 5.8532 | 6.6998 | 81.7495 | 142.6481 | 49.524 | 92.7168 | 18.364 | 109.5592 | 34.065
42810.4518 | 1014 | 17.6578 | 18.059 | 18.175 | 18.2146 | 17.5502 | 16.1788 | 14.7488 | 16.4848 | 16.9917 | 17.1153 | 17.1262 | 16.6525 | 15.682 | 14.3884 | 16.1428 | 27.2145 | 27.9866 | 83.4517 | 30.894 | 89.999 |  |  |  | 21.3985 | 80.7645 | 290.884 | 668.7569 | 718.088 | 676.9248 | 95.153 | 116.5589 | 1011.3498 | 96.9752 | 119.9677 | 876.8232 | 736.8565 | 894.053 |  | 271.0733 | 999.4308 | 1009.1443 | 519.8524 |  | 414.9188 | 672.25 | 510.4799 | 670.0483 | 775.198 | 954.6541 | 1018.8185 | 47.628 | 412.8511 | 80.6443 | 627.761 | 13.7757 | 52.6652 | 48.5014 | 49.6662 | 54.8158 |  |  | -0.22386 | -0.79568 | -0.30108 | -0.55132 | 6.9827 | 5.5896 | 7.2801 | -2.4098 | 23.9664 | 59.6842 | 20.1709 | 0.00019056 | 0.00021192 | -0.00080825 | 20.4718 | 16.3226 | 16.8361 | 17.217 | 17.2086 | 16.1865 | 14.6249 | 16.6784 | 17.0473 | 17.377 | 17.4347 | 17.1653 | 16.347 | 14.5939 | 932.1598 | 686.5707 | 622.8769 | 380.8804 | 285.0147 | 883.7735 | 559.6594 | 16.2643 | 25.0517 | 29.9914 | 59.0351 | 79.5082 | 84.4094 |  |  |  | 600.8748 | 549.3209 | 561.9417 | 570.2094 | 131.9431 | 54.2204 | 862.624 |  |  | 505.7473 |  |  | 18.3806 | 44.684 | 392.9189 | 17.538 | 43.9286 | 922.4296 | 753.3498 | 625.2559 | 843.519 | 847.2877 | 747.4041 |  | 816.867 | 901.8128 | 980.9723 | 607.6227 | 683.7501 | 900.7773 |  | 1010.499 |  |  | 439.7242 | 648.7859 | 744.0325 | [6 empty] | 616.8325 |  |  | 419.176 |  |  | 485.8423 | 664.1346 | 661.5839 | 889.7569 | 1080.5647 | 1046.3892 | 526.9396 | 724.5717 | 811.5036 | 614.5181 | 683.7251 | 1036.979 | 1104.5552 | 630.5741 | 818.0332 | 884.9065 | 1128.4236 | 1078.5518 | 520.9388 | 625.145 | 679.6181 | 598.4075 | 771.4398 | 910.0249 | 1055.0084 | 1129.7841 | 577.0916 | 665.8041 | 696.7861 | 893.4742 | 92.3544 | 0.00015539 | 18.2763 | 4.5784 | -39.9182 | 3.1225 | 11346.37 | 0.31 | -1.0163 | -1.9114 | -1.1758 | -1.591 | 6.4527 | 5.7733 | 6.5887 | 81.9712 | 142.4617 | 49.6536 | 96.2022 | 20.2509 | 65.0317 | 33.9404
42810.4518 | 1015 | 17.6447 | 18.0454 | 18.1621 | 18.2093 | 17.5408 | 16.1695 | 14.7405 | 16.4794 | 16.9885 | 17.1134 | 17.1121 | 16.6409 | 15.6733 | 14.3827 | 16.1998 | 27.3691 | 28.1223 | 83.5977 | 31.0317 | 90.0188 |  |  |  | 21.4986 | 80.9485 | 295.7008 | 670.7594 | 721.6458 | 678.1976 | 94.8414 | 118.3508 | 1005.2241 | 95.5151 | 116.1719 | 880.0277 | 774.0782 | 902.1772 |  | 240.6404 | 996.0896 | 1008.2486 | 542.7726 |  | 415.7979 | 671.6318 | 510.9307 | 668.8215 | 773.11 | 954.0732 | 1017.6915 | 48.4557 | 413.4567 | 79.926 | 628.5339 | 13.7981 | 52.7224 | 48.5145 | 49.6846 | 55.0996 |  |  | -0.037237 | -0.30941 | 0.22067 | -0.57695 | 7.6142 | 4.9299 | 6.943 | -2.6444 | 23.5168 | 58.6268 | 20.1826 | 0.00020206 | 0.00019714 | -0.00081482 | 20.524 | 16.3248 | 16.8431 | 17.2181 | 17.2086 | 16.1862 | 14.6238 | 16.6758 | 17.0519 | 17.3827 | 17.439 | 17.1689 | 16.3546 | 14.5979 | 943.5194 | 669.4256 | 595.3286 | 369.7561 | 286.2603 | 885.0675 | 560.6964 | 16.2775 | 25.1485 | 30.1011 | 59.4298 | 79.5845 | 84.4443 |  |  |  | 600.3325 | 549.1462 | 562.4481 | 569.3693 | 141.1829 | 54.859 | 857.6365 |  |  | 506.5486 |  |  | 18.4092 | 44.7998 | 398.2076 | 17.566 | 44.098 | 918.6093 | 753.2668 | 624.9085 | 841.5372 | 846.249 | 747.8138 |  | 817.2889 | 901.8109 | 980.598 | 607.2615 | 684.2541 | 900.6594 |  | 1011.4663 |  |  | 439.5784 | 648.6577 | 744.2981 | [6 empty] | 616.3901 |  |  | 418.7149 |  |  | 485.9374 | 664.9934 | 662.2224 | 888.7592 | 1077.9919 | 1047.6266 | 526.0393 | 724.5732 | 812.3359 | 614.1349 | 683.9904 | 1033.0092 | 1104.3019 | 630.2761 | 819.4063 | 886.6826 | 1129.917 | 1077.2185 | 520.9603 | 624.7812 | 679.5665 | 600.167 | 775.6373 | 914.4689 | 1061.3831 | 1128.9644 | 576.6122 | 666.1253 | 705.1741 | 896.8078 | 101.0262 | -0.00025152 | 18.2777 | 4.6107 | -39.9243 | 3.1226 | 11324.35 | 0.39 | -0.41479 | -1.1915 | 1.0063 | -1.627 | 6.7366 | 5.4206 | 6.4328 | 82.0955 | 142.284 | 49.7778 | 95.539 | 23.5631 | 74.6195 | 33.8666
42810.4518 | 1016 | 17.6449 | 18.0478 | 18.1721 | 18.2116 | 17.5409 | 16.1783 | 14.743 | 16.4843 | 16.9873 | 17.1111 | 17.1234 | 16.6406 | 15.672 | 14.3877 | 16.2641 | 27.531 | 28.2535 | 83.7366 | 31.1694 | 90.0393 |  |  |  | 21.6017 | 81.1353 | 299.8956 | 673.1212 | 723.6723 | 679.7732 | 91.7034 | 118.1225 | 1001.3658 | 95.4539 | 116.1975 | 880.6645 | 921.1525 | 897.7409 |  | 247.1857 | 993.4759 | 1010.1128 | 526.9887 |  | 415.5056 | 674.9243 | 513.3085 | 668.7145 | 771.1209 | 954.5332 | 1017.4514 | 50.8301 | 414.2283 | 79.6694 | 629.1308 | 13.8126 | 52.8188 | 48.5161 | 49.6968 | 55.4219 |  |  | -0.074693 | -0.67806 | 0.087932 | -0.68011 | 6.8927 | 5.4641 | 8.0016 | -2.4216 | 22.9112 | 57.313 | 20.4241 | 0.00020371 | 0.00019714 | -0.00082468 | 20.5682 | 16.3272 | 16.8343 | 17.222 | 17.2125 | 16.179 | 14.6308 | 16.6813 | 17.0587 | 17.3789 | 17.4447 | 17.1758 | 16.3585 | 14.5962 | 954.0737 | 664.5482 | 586.1425 | 366.1905 | 287.1794 | 886.9942 | 561.6316 | 16.2936 | 25.2491 | 30.2212 | 59.8322 | 79.6621 | 84.4813 |  |  |  | 599.8062 | 548.8075 | 562.2749 | 568.6283 | 135.1266 | 55.1914 | 856.2429 |  |  | 512.6404 |  |  | 18.4166 | 44.9094 | 404.7227 | 17.5838 | 44.2532 | 916.8198 | 754.5407 | 625.523 | 850.8852 | 860.7066 | 749.9576 |  | 818.0607 | 913.9614 | 981.2654 | 608.1373 | 684.9028 | 897.4639 |  | 1012.5629 |  |  | 439.6199 | 652.13 | 745.7303 | [6 empty] | 616.8239 |  |  | 419.5529 |  |  | 486.4474 | 665.2984 | 662.6361 | 890.3003 | 1076.6024 | 1048.3663 | 525.6978 | 726.5327 | 813.8526 | 613.6779 | 684.1232 | 1036.7814 | 1102.0478 | 630.4801 | 823.0169 | 887.4675 | 1132.1908 | 1079.6621 | 520.8747 | 624.7916 | 680.4314 | 601.0443 | 779.9377 | 914.9777 | 1064.0661 | 1129.766 | 576.3756 | 668.5688 | 707.4423 | 900.5484 | 94.3919 | -2.7032e-05 | 18.278 | 4.6346 | -39.9085 | 3.1225 | 11322.6 | 0.35 | -0.58794 | -1.7669 | 0.6363 | -1.7696 | 6.4107 | 5.7078 | 6.9071 | 82.2846 | 142.2635 | 49.9008 | 95.261 | 24.8109 | 126.3051 | 33.7931
42810.4518 | 1017 | 17.6396 | 18.0394 | 18.1651 | 18.2064 | 17.5373 | 16.1748 | 14.7397 | 16.4858 | 16.9835 | 17.1089 | 17.1239 | 16.6448 | 15.6779 | 14.3875 | 16.3179 | 27.6849 | 28.3921 | 83.8618 | 31.3139 | 90.0442 |  |  |  | 21.6983 | 81.3137 | 301.2186 | 673.4324 | 723.3179 | 679.9575 | 90.9233 | 117.1755 | 998.4852 | 95.5417 | 117.8589 | 882.3609 | 922.9881 | 897.0109 |  | 262.9408 | 989.6639 | 1008.4048 | 505.541 |  | 417.0668 | 678.0564 | 514.3341 | 668.7206 | 770.9914 | 953.3463 | 1011.8697 | 53.3361 | 414.7526 | 79.6507 | 629.4351 | 13.8214 | 52.9272 | 48.5079 | 49.7248 | 55.9858 |  |  | 0.077103 | -1.3647 | -0.98711 | -1.3031 | 6.9965 | 4.5317 | 7.5048 | -3.1096 | 22.8143 | 57.2129 | 19.9327 | 0.00023492 | 0.00019878 | -0.00080825 | 20.6087 | 16.3322 | 16.8414 | 17.2173 | 17.2111 | 16.1875 | 14.6244 | 16.681 | 17.0529 | 17.3737 | 17.4369 | 17.1719 | 16.3581 | 14.6001 | 955.4639 | 648.6016 | 581.1518 | 363.048 | 288.3902 | 887.899 | 561.8824 | 16.3219 | 25.3539 | 30.3468 | 60.225 | 79.7428 | 84.531 |  |  |  | 599.5321 | 549.2554 | 561.2667 | 572.2122 | 108.0928 | 42.1979 | 865.1057 |  |  | 512.0333 |  |  | 18.4221 | 45.0243 | 407.2502 | 17.5969 | 44.4123 | 914.5683 | 755.0242 | 626.4009 | 861.3855 | 873.187 | 749.8396 |  | 818.9216 | 921.0231 | 982.9759 | 609.1378 | 685.5054 | 899.7468 |  | 1014.0492 |  |  | 439.2291 | 653.7458 | 746.7774 | [6 empty] | 617.7984 |  |  | 421.278 |  |  | 486.9111 | 665.3638 | 662.8437 | 896.4693 | 1080.789 | 1049.9022 | 525.833 | 731.0154 | 815.6169 | 613.2155 | 684.4444 | 1043.2146 | 1108.6561 | 631.495 | 827.5867 | 887.0951 | 1133.5687 | 1081.6315 | 520.9555 | 625.5794 | 681.5741 | 600.848 | 779.8195 | 914.3216 | 1063.0155 | 1129.6463 | 576.2753 | 670.1312 | 706.5605 | 900.8682 | 92.8135 | -0.00034273 | 18.2771 | 4.6671 | -39.8893 | 3.1225 | 11366.29 | 0.39 | 0.59741 | -2.5109 | -2.1354 | -2.4535 | 6.4556 | 5.1955 | 6.6861 | 82.5658 | 142.8822 | 50.01 | 95.5279 | 25.4264 | 127.6626 | 33.6446
42810.4518 | 1018 | 17.6304 | 18.0374 | 18.1577 | 18.1983 | 17.5364 | 16.1749 | 14.7395 | 16.4804 | 16.9725 | 17.1028 | 17.12 | 16.6491 | 15.6784 | 14.385 | 16.3873 | 27.8467 | 28.532 | 83.9795 | 31.4671 | 90.0605 |  |  |  | 21.8098 | 81.5026 | 301.7147 | 672.1886 | 722.073 | 679.4782 | 98.7095 | 115.9962 | 994.8809 | 92.4068 | 113.6854 | 882.5884 | 904.8926 | 898.8151 |  | 262.402 | 991.0529 | 1008.3109 | 514.7155 |  | 417.7614 | 679.3903 | 516.685 | 669.8503 | 768.1113 | 952.5611 | 1010.5494 | 53.4153 | 415.292 | 80.6035 | 629.6159 | 13.8111 | 52.9838 | 48.5031 | 49.7429 | 56.4535 |  |  | 0.39449 | -0.60775 | -0.16308 | -0.25956 | 5.6395 | 5.9911 | 6.8405 | -2.5195 | 23.8611 | 58.7837 | 19.8063 | 0.00020206 | 0.00020864 | -0.00079018 | 20.6655 | 16.321 | 16.8281 | 17.2074 | 17.2061 | 16.1891 | 14.6185 | 16.6735 | 17.051 | 17.3659 | 17.4404 | 17.1748 | 16.3555 | 14.5983 | 921.162 | 634.9497 | 581.9972 | 369.0597 | 298.4831 | 887.4916 | 562.1148 | 16.3416 | 25.4648 | 30.473 | 60.622 | 79.8203 | 84.5968 |  |  |  | 599.4824 | 549.5691 | 560.458 | 575.4165 | 160.6689 | 72.6464 | 873.9504 |  |  | 513.026 |  |  | 18.4536 | 45.139 | 406.5542 | 17.6169 | 44.5734 | 920.0939 | 755.7939 | 627.5974 | 866.3821 | 879.1825 | 749.7015 |  | 819.6571 | 925.207 | 984.077 | 609.9798 | 686.2313 | 901.3924 |  | 1015.3013 |  |  | 438.5964 | 653.8967 | 747.234 | [6 empty] | 619.1032 |  |  | 421.9837 |  |  | 487.0213 | 665.1989 | 663.2406 | 900.775 | 1085.043 | 1054.7191 | 525.8316 | 735.3903 | 817.78 | 613.1456 | 684.9879 | 1043.1346 | 1115.327 | 631.9869 | 831.5723 | 889.4151 | 1135.7755 | 1082.0911 | 520.9411 | 625.666 | 681.3194 | 599.6516 | 777.8825 | 914.4256 | 1063.2407 | 1130.6866 | 575.9806 | 669.5572 | 703.9675 | 901.0141 | 89.9438 | -0.0030716 | 18.2762 | 4.7006 | -39.9302 | 3.1225 | 11428.78 | 0.33 | 1.351 | -1.6768 | -0.86859 | -1.0958 | 5.7941 | 5.9719 | 6.3812 | 82.8075 | 143.2922 | 50.152 | 99.1494 | 25.389 | 120.0394 | 33.5467
42810.4518 | 1019 | 17.6381 | 18.0453 | 18.1621 | 18.2004 | 17.5399 | 16.1731 | 14.7468 | 16.4824 | 16.9792 | 17.1099 | 17.1271 | 16.6472 | 15.6766 | 14.3884 | 16.4474 | 28.009 | 28.6636 | 84.0948 | 31.5535 | 90.0437 |  |  |  | 21.9158 | 81.619 | 302.6567 | 671.5143 | 722.3364 | 679.8854 | 100.6607 | 120.6281 | 1002.0303 | 94.317 | 113.7472 | 884.8633 | 910.8743 | 902.3681 |  | 257.5143 | 990.7999 | 1007.6182 | 517.1606 |  | 419.1113 | 680.0789 | 517.6225 | 671.9624 | 783.6125 | 960.6085 | 1018.0937 | 52.3015 | 416.0848 | 82.5203 | 629.8864 | 13.8213 | 52.9975 | 48.5015 | 49.7663 | 56.7984 |  |  | 0.045559 | -0.56241 | -0.60664 | -1.5271 | 6.1251 | 5.8354 | 7.0678 | -2.2232 | 23.5836 | 57.8881 | 20.3829 | 0.00015442 | 0.00027599 | -0.00076882 | 20.7009 | 16.325 | 16.8284 | 17.2139 | 17.207 | 16.1821 | 14.6215 | 16.6805 | 17.0473 | 17.3721 | 17.4404 | 17.1736 | 16.3564 | 14.601 | 943.8002 | 656.0281 | 631.9307 | 395.4586 | 307.6515 | 890.6048 | 564.3451 | 16.3567 | 25.5595 | 30.5861 | 60.9856 | 79.8903 | 84.6325 |  |  |  | 599.0257 | 548.5467 | 560.2471 | 572.0801 | 144.0618 | 52.2387 | 879.7658 |  |  | 514.8094 |  |  | 18.4599 | 45.2485 | 407.2591 | 17.6189 | 44.7121 | 920.9025 | 756.1891 | 629.6728 | 876.5846 | 893.8259 | 751.0025 |  | 820.0264 | 931.4336 | 985.3082 | 611.9379 | 687.3026 | 902.2181 |  | 1016.8963 |  |  | 438.3005 | 656.6964 | 747.6219 | [6 empty] | 621.1508 |  |  | 422.7464 |  |  | 487.2202 | 665.3401 | 663.6859 | 900.3 | 1083.4843 | 1060.9852 | 525.3371 | 736.9008 | 819.7618 | 613.0349 | 685.3663 | 1045.0247 | 1119.4406 | 631.4713 | 832.3739 | 891.1745 | 1135.6113 | 1084.8161 | 520.7499 | 624.9965 | 680.4046 | 599.0693 | 777.0322 | 917.2032 | 1062.2369 | 1131.5458 | 576.1838 | 669.1419 | 703.1951 | 903.8091 | 95.8566 | -0.00075661 | 18.2777 | 4.7369 | -39.9412 | 3.1224 | 11494.29 | 0.26 | 0.45921 | -1.6136 | -1.6758 | -2.6589 | 6.0582 | 5.9131 | 6.5077 | 82.891 | 143.7092 | 50.3423 | 98.0884 | 20.3846 | 122.3725 | 33.5579
42810.4518 | 1020 | 17.6353 | 18.0429 | 18.1679 | 18.2022 | 17.536 | 16.1703 | 14.7475 | 16.4895 | 16.9835 | 17.1045 | 17.1216 | 16.6473 | 15.6737 | 14.384 | 16.5064 | 28.1672 | 28.8074 | 84.2133 | 31.6238 | 90.0361 |  |  |  | 22.0153 | 81.6292 | 305.1517 | 674.114 | 723.9264 | 683.0983 | 98.021 | 123.6461 | 999.6007 | 100.7172 | 120.8496 | 887.2146 | 910.0105 | 903.2684 |  | 268.9849 | 982.754 | 1000.8507 | 517.7652 |  | 420.2024 | 681.2866 | 519.5296 | 672.8827 | 790.8271 | 966.1689 | 1021.054 | 52.3915 | 416.7076 | 83.4148 | 630.1539 | 13.8305 | 53.0124 | 48.4809 | 49.7923 | 57.1732 |  |  | 0.20852 | -0.21742 | -0.64081 | -0.98239 | 7.1115 | 5.8341 | 7.748 | -2.7647 | 24.4104 | 58.0374 | 20.6126 | 0.00024642 | 0.00017414 | -0.00082961 | 20.7421 | 16.3238 | 16.8253 | 17.2117 | 17.1985 | 16.1829 | 14.6235 | 16.6722 | 17.0501 | 17.3722 | 17.4386 | 17.1683 | 16.3544 | 14.5973 | 959.5224 | 664.0693 | 617.9496 | 383.2048 | 307.2052 | 892.9946 | 565.3066 | 16.3748 | 25.6581 | 30.7103 | 61.3495 | 79.9464 | 84.6774 |  |  |  | 598.4852 | 548.0266 | 560.4864 | 570.8827 | 152.5467 | 76.3104 | 890.4235 |  |  | 518.9613 |  |  | 18.4783 | 45.3687 | 410.8324 | 17.6649 | 44.8656 | 912.723 | 758.5763 | 631.1836 | 883.5015 | 900.5337 | 753.42 |  | 820.7789 | 939.6373 | 988.0619 | 613.4644 | 688.2304 | 905.7707 |  | 1018.422 |  |  | 439.4288 | 662.5914 | 749.248 | [6 empty] | 622.9163 |  |  | 423.2957 |  |  | 487.1305 | 665.627 | 664.2227 | 901.525 | 1082.6731 | 1062.902 | 524.7856 | 737.1857 | 820.9231 | 611.9893 | 686.0998 | 1049.2638 | 1114.1094 | 631.3403 | 833.6951 | 893.6287 | 1131.1331 | 1085.8286 | 520.779 | 624.4629 | 680.7573 | 597.8922 | 776.2595 | 919.1556 | 1059.6921 | 1129.6436 | 576.2933 | 669.6972 | 701.4112 | 901.5039 | 93.7205 | 4.3152e-05 | 18.2775 | 4.7733 | -39.8659 | 3.1224 | 11593.21 | 0.32 | 0.98408 | -1.0039 | -1.7235 | -2.1339 | 6.5424 | 5.9258 | 6.8289 | 83.068 | 144.8066 | 50.5124 | 97.4639 | 22.1732 | 122.0069 | 33.4949
42810.4519 | 1021 | 17.634 | 18.0388 | 18.1689 | 18.1959 | 17.5318 | 16.173 | 14.7493 | 16.4819 | 16.9794 | 17.1102 | 17.1211 | 16.6527 | 15.6732 | 14.3902 | 16.5769 | 28.3187 | 28.9458 | 84.3367 | 31.6872 | 90.0406 |  |  |  | 22.122 | 81.7697 | 306.5071 | 675.1934 | 723.6924 | 684.0339 | 98.2565 | 120.2784 | 997.5231 | 101.889 | 122.9489 | 891.6044 | 899.029 | 902.68 |  | 280.2032 | 979.5988 | 1002.8208 | 537.4893 |  | 420.5028 | 680.598 | 521.5695 | 674.3701 | 797.5855 | 970.5575 | 1024.8121 | 54.4234 | 417.3943 | 83.681 | 630.6332 | 13.8687 | 53.035 | 48.4545 | 49.8226 | 57.5833 |  |  | 0.26635 | -0.35213 | -0.96871 | -0.81614 | 7.6391 | 5.3872 | 7.4023 | -2.8553 | 24.122 | 58.2737 | 21.1205 | 0.00015935 | 0.00018399 | -0.00082632 | 20.7957 | 16.3239 | 16.8248 | 17.2093 | 17.2033 | 16.181 | 14.6233 | 16.6789 | 17.0532 | 17.3758 | 17.4386 | 17.1673 | 16.3608 | 14.601 | 962.9775 | 697.8051 | 665.2058 | 394.9156 | 317.9274 | 895.5733 | 568.024 | 16.3911 | 25.759 | 30.8248 | 61.7345 | 80.0146 | 84.713 |  |  |  | 598.3406 | 549.297 | 560.7128 | 574.1057 | 137.0356 | 60.6548 | 896.9038 |  |  | 519.139 |  |  | 18.4927 | 45.4801 | 411.6583 | 17.689 | 45.0237 | 912.7831 | 760.445 | 631.2364 | 888.5423 | 903.6772 | 755.6347 |  | 821.9106 | 941.0368 | 991.4773 | 613.815 | 688.7882 | 907.688 |  | 1019.4689 |  |  | 439.0197 | 663.1465 | 752.0341 | [6 empty] | 623.2 |  |  | 423.9874 |  |  | 486.6249 | 665.5166 | 665.2062 | 908.0709 | 1081.3906 | 1058.2682 | 524.4669 | 738.0913 | 821.2792 | 611.5185 | 687.1795 | 1057.4618 | 1106.6623 | 631.9594 | 836.1765 | 893.4023 | 1128.6657 | 1087.3252 | 520.8013 | 624.4608 | 683.0035 | 599.7437 | 776.3073 | 918.3003 | 1057.8345 | 1128.6483 | 576.5066 | 669.9041 | 704.9171 | 900.4356 | 87.3601 | -0.0011986 | 18.2774 | 4.8174 | -39.9841 | 3.1224 | 11716.63 | 0.27 | 1.1127 | -1.2771 | -2.1183 | -1.9443 | 6.7928 | 5.7044 | 6.6867 | 83.3744 | 146.4229 | 50.6306 | 98.2971 | 17.5895 | 117.0859 | 33.3797
42810.4519 | 1022 | 17.626 | 18.0323 | 18.1549 | 18.2041 | 17.5325 | 16.1739 | 14.7464 | 16.4768 | 16.9744 | 17.1076 | 17.1265 | 16.6482 | 15.6796 | 14.3988 | 16.6306 | 28.4778 | 29.0784 | 84.4222 | 31.8034 | 90.0378 |  |  |  | 22.2158 | 81.9638 | 308.6272 | 675.3859 | 723.4797 | 683.4396 | 96.4985 | 121.2251 | 992.8482 | 95.156 | 121.1158 | 894.2919 | 833.8867 | 911.0805 |  | 256.0882 | 975.5301 | 992.3935 | 565.2357 |  | 421.0395 | 680.8635 | 522.4491 | 675.9948 | 802.8656 | 972.8917 | 1027.0439 | 55.3508 | 417.9114 | 83.6041 | 631.2505 | 13.9038 | 53.0496 | 48.4029 | 49.8517 | 57.9184 |  |  | 0.11653 | -0.7326 | -0.64738 | -0.85885 | 6.9616 | 6.1659 | 7.8209 | -3.1372 | 23.8907 | 59.0057 | 20.5812 | 0.00019549 | 0.00022835 | -0.00081811 | 20.8416 | 16.3212 | 16.8318 | 17.2074 | 17.2012 | 16.1786 | 14.6246 | 16.6813 | 17.0522 | 17.3747 | 17.4387 | 17.1679 | 16.359 | 14.602 | 942.7871 | 700.7856 | 667.3984 | 389.2779 | 324.4304 | 896.7001 | 570.1995 | 16.4057 | 25.8567 | 30.934 | 62.1203 | 80.0852 | 84.7552 |  |  |  | 598.3309 | 550.0599 | 560.9935 | 575.64 | 136.9676 | 51.7872 | 900.6561 |  |  | 523.5092 |  |  | 18.505 | 45.5821 | 413.0234 | 17.699 | 45.1782 | 908.6694 | 759.3796 | 631.1503 | 888.3109 | 902.3414 | 754.1949 |  | 822.5531 | 935.1121 | 995.7138 | 613.4534 | 689.3243 | 905.8668 |  | 1020.8505 |  |  | 437.5908 | 660.1749 | 751.3876 | [6 empty] | 622.9635 |  |  | 424.2933 |  |  | 486.6795 | 665.3924 | 665.7755 | 915.6799 | 1093.5584 | 1055.817 | 524.6406 | 740.0631 | 821.6747 | 611.7073 | 687.3735 | 1059.5829 | 1110.6656 | 633.2019 | 837.3952 | 894.9664 | 1128.4221 | 1086.1244 | 521.1752 | 624.4348 | 683.7993 | 601.512 | 781.1572 | 917.1695 | 1058.2598 | 1127.6741 | 576.6509 | 670.5927 | 707.3102 | 903.9608 | 89.3876 | -0.00098109 | 18.2761 | 4.8612 | -39.8142 | 3.1225 | 11895.75 | 0.27 | 0.73577 | -1.8424 | -1.7319 | -1.9948 | 6.4907 | 6.1085 | 6.8796 | 83.6238 | 148.6583 | 50.7639 | 101.0742 | 17.8824 | 92.6216 | 33.3353
42810.4519 | 1023 | 17.6235 | 18.0356 | 18.1558 | 18.2025 | 17.5352 | 16.1682 | 14.7602 | 16.4874 | 16.9797 | 17.102 | 17.1267 | 16.6555 | 15.6781 | 14.3897 | 16.7189 | 28.6544 | 29.2315 | 84.5199 | 31.9304 | 90.0412 |  |  |  | 22.3304 | 82.1217 | 312.3228 | 677.1106 | 725.6874 | 685.0251 | 93.4348 | 122.2654 | 990.225 | 98.8234 | 118.3341 | 893.0734 | 917.9132 | 910.5158 |  | 245.7054 | 983.4059 | 1001.2937 | 556.7418 |  | 421.944 | 680.869 | 523.2927 | 678.2789 | 797.3665 | 965.5996 | 1024.3075 | 54.3699 | 418.2689 | 85.4455 | 632.1172 | 13.9202 | 53.0992 | 48.3627 | 49.878 | 58.3605 |  |  | 0.25781 | -1.2018 | -0.66578 | -0.63083 | 7.6168 | 6.9446 | 7.9004 | -2.3316 | 23.7574 | 58.6863 | 20.5433 | 0.00019714 | 0.00015607 | -0.00079018 | 20.8881 | 16.3148 | 16.8269 | 17.2109 | 17.1959 | 16.1765 | 14.6242 | 16.6781 | 17.0479 | 17.3732 | 17.44 | 17.1727 | 16.3573 | 14.6066 | 929.2814 | 670.1366 | 621.8487 | 381.5508 | 312.44 | 897.521 | 571.3293 | 16.4346 | 25.9682 | 31.0693 | 62.5388 | 80.1561 | 84.8138 |  |  |  | 598.1712 | 549.8571 | 560.5948 | 575.907 | 146.4503 | 57.2599 | 900.9411 |  |  | 528.4871 |  |  | 18.5204 | 45.6873 | 415.3791 | 17.7203 | 45.3289 | 909.4585 | 757.9764 | 631.405 | 886.3577 | 902.6258 | 750.8768 |  | 822.8458 | 933.753 | 997.6522 | 613.3579 | 689.885 | 906.0388 |  | 1022.7861 |  |  | 437.1803 | 655.3851 | 749.4626 | [6 empty] | 623.0474 |  |  | 424.3817 |  |  | 486.6194 | 665.1103 | 666.3974 | 919.9687 | 1095.3333 | 1062.963 | 524.3162 | 739.6923 | 822.0813 | 611.2611 | 687.4689 | 1057.8748 | 1111.1686 | 632.8042 | 833.6842 | 896.9636 | 1129.36 | 1084.142 | 521.1638 | 624.946 | 684.2018 | 601.9834 | 783.57 | 916.6002 | 1059.8179 | 1127.2199 | 576.8643 | 671.4414 | 707.0223 | 911.0232 | 95.1916 | -0.0013108 | 18.2766 | 4.9026 | -39.8942 | 3.1225 | 11990.74 | 0.31 | 1.0953 | -2.3597 | -1.7563 | -1.7096 | 6.7693 | 6.4637 | 6.8942 | 83.8114 | 149.65 | 50.8956 | 102.9644 | 23.223 | 124.1422 | 33.2995
42810.4519 | 1024 | 17.6115 | 18.0306 | 18.1528 | 18.1936 | 17.5192 | 16.1594 | 14.756 | 16.4721 | 16.9724 | 17.1011 | 17.1204 | 16.6445 | 15.6701 | 14.3816 | 16.7792 | 28.817 | 29.3726 | 84.6489 | 32.0185 | 90.0338 |  |  |  | 22.4531 | 82.2072 | 313.6355 | 678.4477 | 725.3494 | 686.5799 | 83.4547 | 115.8289 | 989.8995 | 96.0551 | 112.0226 | 888.1118 | 937.7776 | 898.3437 |  | 270.9548 | 983.5184 | 1003.3126 | 527.557 |  | 421.8857 | 682.4835 | 524.0949 | 679.8226 | 798.4028 | 972.8639 | 1026.4898 | 52.4564 | 418.6774 | 86.5586 | 632.9332 | 13.9457 | 53.1935 | 48.3401 | 49.9109 | 58.8658 |  |  | 0.22495 | -0.30941 | -0.25377 | -0.19056 | 7.7167 | 7.5327 | 8.7639 | -2.6345 | 23.7823 | 58.8632 | 20.8489 | 0.00015771 | 0.00020864 | -0.00078361 | 20.93 | 16.3175 | 16.8154 | 17.2015 | 17.1853 | 16.1703 | 14.616 | 16.6689 | 17.0483 | 17.3698 | 17.4421 | 17.1679 | 16.3534 | 14.6036 | 938.1082 | 675.5599 | 638.2189 | 391.8074 | 322.6153 | 900.115 | 573.5539 | 16.4487 | 26.0682 | 31.181 | 62.8674 | 80.2058 | 84.8492 |  |  |  | 598.0786 | 549.5297 | 560.2184 | 577.0291 | 192.9389 | 89.8205 | 901.7183 |  |  | 549.3086 |  |  | 18.5363 | 45.8181 | 416.0771 | 17.7359 | 45.4861 | 914.1314 | 758.0574 | 631.3052 | 887.8119 | 901.4903 | 750.8757 |  | 823.3783 | 936.6899 | 998.6555 | 613.3106 | 690.2936 | 911.3974 |  | 1024.7672 |  |  | 438.2141 | 652.9943 | 748.8128 | [6 empty] | 622.9879 |  |  | 424.6614 |  |  | 486.5048 | 665.2418 | 666.5934 | 929.1298 | 1093.1678 | 1066.5775 | 523.6581 | 739.2408 | 822.5384 | 610.6267 | 688.0421 | 1067.1583 | 1112.531 | 632.4752 | 835.6458 | 896.5462 | 1130.5598 | 1084.5294 | 520.8166 | 626.3177 | 686.3982 | 601.4279 | 783.1193 | 917.5989 | 1063.5545 | 1128.5359 | 576.4946 | 673.5787 | 705.372 | 909.5737 | 99.0058 | 0.00044301 | 18.2774 | 4.9451 | -39.9136 | 3.1224 | 12013.76 | 0.21 | 1.024 | -1.1983 | -1.0853 | -0.94044 | 6.8335 | 6.7516 | 7.2824 | 83.9854 | 150.0639 | 50.9911 | 103.2189 | 21.9563 | 133.3096 | 33.2519
42810.4519 | 1025 | 17.6144 | 18.0268 | 18.149 | 18.188 | 17.5234 | 16.1585 | 14.755 | 16.4705 | 16.9762 | 17.1081 | 17.1182 | 16.6478 | 15.6703 | 14.3835 | 16.85 | 28.9816 | 29.5134 | 84.7253 | 32.0962 | 90.0255 |  |  |  | 22.5628 | 82.3791 | 314.6397 | 678.2405 | 724.0818 | 686.5322 | 86.7866 | 109.8895 | 981.9007 | 90.2768 | 112.4356 | 882.1982 | 941.9734 | 896.0067 |  | 288.8229 | 975.9268 | 994.6344 | 520.4557 |  | 423.1861 | 684.7269 | 525.7689 | 679.6294 | 814.144 | 983.9907 | 1032.6466 | 51.0102 | 419.1385 | 85.9506 | 633.3905 | 13.9661 | 53.2791 | 48.3236 | 49.945 | 59.2528 |  |  | 0.1599 | -0.84759 | -0.28005 | -0.60915 | 6.7297 | 6.7961 | 8.4925 | -3.2128 | 24.3604 | 60.8569 | 21.1599 | 0.00013471 | 0.00019714 | -0.00084439 | 20.9912 | 16.3194 | 16.8274 | 17.2176 | 17.196 | 16.1845 | 14.6249 | 16.6813 | 17.0536 | 17.3763 | 17.4449 | 17.1799 | 16.3597 | 14.6102 | 982.7066 | 714.7437 | 699.0782 | 397.3481 | 314.9846 | 906.4783 | 578.4916 | 16.4707 | 26.1667 | 31.2945 | 63.2107 | 80.2666 | 84.8922 |  |  |  | 598.1145 | 549.5354 | 560.2801 | 577.8024 | 185.4285 | 57.2488 | 901.8676 |  |  | 546.4411 |  |  | 18.5538 | 45.923 | 416.3562 | 17.7667 | 45.6351 | 909.0492 | 759.1225 | 631.0544 | 889.8703 | 903.0441 | 753.0687 |  | 824.0696 | 935.0148 | 1000.724 | 612.9048 | 690.65 | 909.2328 |  | 1026.8797 |  |  | 439.7594 | 656.4275 | 749.9706 | [6 empty] | 622.7143 |  |  | 424.3856 |  |  | 486.5427 | 666.6996 | 666.8716 | 951.8644 | 1101.1765 | 1065.9348 | 523.9379 | 741.4302 | 823.5565 | 609.8852 | 688.5632 | 1081.4944 | 1121.1897 | 633.1768 | 840.0197 | 908.4135 | 1131.7512 | 1083.6841 | 520.7087 | 627.5998 | 687.7344 | 603.3189 | 780.2087 | 915.4842 | 1075.4426 | 1127.2143 | 577.3227 | 674.4905 | 705.6437 | 903.9336 | 102.4179 | -0.0025315 | 18.2775 | 4.9813 | -40.0033 | 3.1224 | 11973.96 | 0.25 | 0.86328 | -1.9857 | -1.1414 | -1.6834 | 6.41 | 6.4415 | 7.2007 | 84.1506 | 151.1353 | 51.0846 | 101.3204 | 16.4286 | 135.322 | 33.2368
42810.4519 | 1026 | 17.6136 | 18.0255 | 18.1424 | 18.1914 | 17.5289 | 16.1639 | 14.7557 | 16.4748 | 16.9746 | 17.1106 | 17.112 | 16.6484 | 15.671 | 14.39 | 16.9353 | 29.1494 | 29.6635 | 84.8006 | 32.2325 | 90.0262 |  |  |  | 22.6809 | 82.5867 | 315.312 | 676.8782 | 722.7441 | 685.1011 | 98.5342 | 119.1359 | 983.7553 | 94.8051 | 117.8178 | 883.9757 | 928.1518 | 898.5182 |  | 266.3907 | 972.4258 | 987.6552 | 515.9043 |  | 425.3897 | 688.9154 | 528.3544 | 678.2895 | 821.0096 | 991.911 | 1043.6139 | 50.4718 | 419.7338 | 85.0235 | 633.9329 | 13.9808 | 53.3261 | 48.3149 | 49.9693 | 59.3581 |  |  | 0.19604 | -0.66229 | -0.11972 | -0.91865 | 8.0682 | 6.8395 | 7.5751 | -3.4132 | 24.2696 | 60.3809 | 19.6871 | 0.00019878 | 0.00015278 | -0.00079347 | 21.0276 | 16.3157 | 16.8257 | 17.2078 | 17.1903 | 16.1771 | 14.6244 | 16.6809 | 17.0482 | 17.3715 | 17.4375 | 17.1664 | 16.3597 | 14.6049 | 1006.4241 | 710.1585 | 646.2211 | 383.6556 | 304.6033 | 912.8976 | 580.5726 | 16.4925 | 26.2629 | 31.4109 | 63.5787 | 80.3299 | 84.9355 |  |  |  | 598.0768 | 549.1803 | 560.2117 | 575.7516 | 156.2261 | 48.9268 | 902.5653 |  |  | 543.7969 |  |  | 18.5776 | 46.0422 | 416.2994 | 17.7741 | 45.8074 | 901.9111 | 760.8925 | 632.3047 | 892.045 | 906.591 | 756.6722 |  | 825.1379 | 932.6548 | 1004.8133 | 613.8135 | 691.3417 | 910.3536 |  | 1031.487 |  |  | 440.5267 | 659.6909 | 751.9456 | [6 empty] | 623.7472 |  |  | 424.5561 |  |  | 486.6494 | 667.0321 | 667.1649 | 953.0453 | 1114.5837 | 1072.6358 | 524.1556 | 744.0299 | 825.6293 | 609.6829 | 689.4372 | 1086.4912 | 1134.6767 | 634.2906 | 845.9778 | 936.1696 | 1136.1032 | 1081.8019 | 520.8007 | 628.961 | 687.6916 | 602.2033 | 777.6029 | 913.4207 | 1097.6452 | 1132.7565 | 578.3605 | 674.9008 | 702.3613 | 899.6948 | 101.1075 | 2.208e-05 | 18.2773 | 5.0138 | -39.9312 | 3.1224 | 11975.15 | 0.28 | 0.95516 | -1.7591 | -0.7479 | -2.0718 | 7.0406 | 6.4824 | 6.8221 | 84.4007 | 153.2409 | 51.2192 | 101.8078 | 22.8254 | 129.5355 | 33.287
42810.4519 | 1027 | 17.6125 | 18.0162 | 18.1508 | 18.1951 | 17.5225 | 16.1662 | 14.7575 | 16.4739 | 16.9757 | 17.108 | 17.1133 | 16.6388 | 15.6697 | 14.3885 | 17.0009 | 29.3159 | 29.7943 | 84.871 | 32.431 | 90.0162 |  |  |  | 22.7902 | 82.8086 | 316.6329 | 676.8453 | 723.2215 | 686.2564 | 99.9806 | 123.2993 | 979.2017 | 97.5723 | 117.9129 | 878.4917 | 938.2929 | 891.5251 |  | 258.3339 | 961.8559 | 975.0312 | 508.9532 |  | 427.448 | 693.2424 | 531.8973 | 678.7399 | 833.5695 | 1001.8014 | 1052.1678 | 50.2452 | 420.2678 | 86.1776 | 634.733 | 13.992 | 53.3598 | 48.3102 | 50.0028 | 59.2534 |  |  | 0.51474 | -0.55714 | -0.52976 | -0.63215 | 7.7324 | 5.3531 | 6.8332 | -2.9394 | 23.3522 | 61.0223 | 19.1512 | 0.00015278 | 0.00014621 | -0.00082468 | 21.0801 | 16.3187 | 16.8263 | 17.2069 | 17.1892 | 16.1777 | 14.6219 | 16.6862 | 17.0502 | 17.3786 | 17.441 | 17.1707 | 16.3568 | 14.6097 | 979.596 | 673.2162 | 583.7913 | 380.8028 | 307.2295 | 916.4175 | 581.16 | 16.5126 | 26.362 | 31.5381 | 63.9527 | 80.3894 | 84.9795 |  |  |  | 597.8638 | 548.1852 | 561.0623 | 572.3845 | 131.8311 | 32.4137 | 904.8786 |  |  | 541.4056 |  |  | 18.5936 | 46.1539 | 417.879 | 17.8024 | 45.9441 | 891.6542 | 762.4015 | 635.1141 | 893.696 | 910.759 | 759.9516 |  | 826.2225 | 934.8975 | 1007.676 | 616.256 | 692.2563 | 908.3757 |  | 1034.988 |  |  | 440.5141 | 662.7595 | 754.222 | [6 empty] | 626.6656 |  |  | 427.0742 |  |  | 486.7518 | 668.5891 | 667.446 | 951.086 | 1125.6574 | 1083.916 | 524.2719 | 748.4381 | 829.9833 | 611.0215 | 691.54 | 1086.5291 | 1139.4887 | 635.0371 | 849.5681 | 980.9915 | 1147.5523 | 1081.2933 | 520.8025 | 629.9686 | 686.9254 | 598.6216 | 773.7091 | 909.826 | 1126.6517 | 1138.0647 | 579.3038 | 675.7795 | 697.6861 | 893.4311 | 94.6664 | -0.0011074 | 18.276 | 5.0474 | -39.8591 | 3.1225 | 11942.09 | 0.35 | 1.5487 | -1.6171 | -1.5768 | -1.7225 | 6.9195 | 5.7572 | 6.5047 | 84.6661 | 154.6178 | 51.3631 | 106.5177 | 29.9103 | 134.0484 | 33.3427
42810.4519 | 1028 | 17.609 | 18.0186 | 18.1465 | 18.191 | 17.5159 | 16.1549 | 14.7621 | 16.4683 | 16.9724 | 17.0971 | 17.1182 | 16.6449 | 15.6658 | 14.3814 | 17.0787 | 29.4944 | 29.9414 | 84.9601 | 32.6291 | 90.0461 |  |  |  | 22.9033 | 83.0321 | 317.9815 | 676.9689 | 721.5404 | 688.37 | 97.5894 | 121.2513 | 962.7555 | 98.7075 | 119.1428 | 868.4173 | 786.4406 | 880.3854 |  | 257.3374 | 937.2884 | 951.2275 | 510.142 |  | 430.4385 | 696.4683 | 534.256 | 683.615 | 837.3867 | 1002.9215 | 1058.8157 | 49.4418 | 420.7241 | 87.6653 | 635.5863 | 14.0067 | 53.4005 | 48.3009 | 50.0239 | 59.0601 |  |  | 0.4004 | -0.41981 | -0.10854 | -0.84439 | 7.7318 | 5.6803 | 6.1104 | -2.8724 | 23.7574 | 60.6801 | 19.0882 | 0.00017578 | 0.00020206 | -0.00082632 | 21.1299 | 16.3224 | 16.8233 | 17.1989 | 17.1878 | 16.1763 | 14.6265 | 16.6847 | 17.0544 | 17.3809 | 17.4441 | 17.1721 | 16.3646 | 14.6121 | 935.8449 | 632.265 | 519.6347 | 352.4556 | 296.7268 | 916.7224 | 579.8831 | 16.5292 | 26.4796 | 31.6593 | 64.3395 | 80.4517 | 85.012 |  |  |  | 597.5543 | 547.8937 | 563.1855 | 572.888 | 150.5454 | 37.8685 | 909.7688 |  |  | 545.1723 |  |  | 18.6081 | 46.2554 | 420.5818 | 17.814 | 46.0825 | 872.5821 | 761.8398 | 637.2755 | 897.5164 | 915.4414 | 760.3621 |  | 826.9007 | 936.1468 | 1011.1828 | 617.9558 | 693.2754 | 904.8333 |  | 1036.8691 |  |  | 440.7295 | 662.9297 | 754.1859 | [6 empty] | 628.9564 |  |  | 428.599 |  |  | 486.8678 | 671.3598 | 669.1028 | 947.3149 | 1125.342 | 1085.4588 | 524.0172 | 748.8583 | 833.6025 | 612.9843 | 695.5862 | 1079.9646 | 1136.6567 | 634.5902 | 846.7907 | 1021.8886 | 1158.3316 | 1079.2455 | 521.4086 | 631.0878 | 686.3949 | 595.3408 | 770.406 | 904.5536 | 1143.2686 | 1138.7697 | 580.3219 | 677.0646 | 693.4616 | 884.9696 | 102.3729 | 0.00019044 | 18.2778 | 5.0795 | -39.9529 | 3.1224 | 11916.59 | 0.36 | 1.3674 | -1.406 | -0.71494 | -1.9941 | 6.9222 | 5.9332 | 6.1538 | 84.8781 | 156.3586 | 51.5525 | 111.5293 | 36.7167 | 79.1469 | 33.2738
42810.4519 | 1029 | 17.6122 | 18.0337 | 18.1564 | 18.1906 | 17.5274 | 16.1602 | 14.7646 | 16.4752 | 16.9743 | 17.1112 | 17.1286 | 16.647 | 15.6788 | 14.3961 | 17.1524 | 29.6507 | 30.0841 | 85.0333 | 32.7372 | 90.0739 |  |  |  | 23.0119 | 83.2262 | 317.7107 | 676.1489 | 719.2771 | 688.8619 | 94.9375 | 120.3346 | 941.8895 | 97.4961 | 119.0789 | 857.3141 | 794.2579 | 871.4384 |  | 246.6365 | 921.134 | 932.0994 | 471.0574 |  | 433.5612 | 699.7081 | 538.0352 | 690.7432 | 836.3865 | 1000.8483 | 1062.5162 | 49.756 | 421.2518 | 87.4174 | 636.4573 | 14.013 | 53.5044 | 48.2871 | 50.0469 | 58.796 |  |  | 0.090903 | 0.23336 | -0.4693 | -0.62295 | 7.6273 | 5.2768 | 6.8852 | -2.6575 | 24.4509 | 61.3733 | 18.6819 | 0.00016264 | 0.00019714 | -0.00084275 | 21.184 | 16.3237 | 16.8189 | 17.2015 | 17.1914 | 16.1765 | 14.6346 | 16.6911 | 17.0609 | 17.3776 | 17.4428 | 17.1781 | 16.3626 | 14.6152 | 929.0626 | 632.3774 | 523.3799 | 327.3681 | 275.3719 | 918.0844 | 578.7763 | 16.5537 | 26.5851 | 31.7719 | 64.7153 | 80.5192 | 85.0525 |  |  |  | 597.5177 | 549.5616 | 565.6775 | 578.8016 | 133.4217 | 40.2564 | 914.7017 |  |  | 542.4355 |  |  | 18.6326 | 46.3747 | 420.1303 | 17.8394 | 46.2486 | 852.8724 | 761.5175 | 637.5045 | 898.1288 | 915.6548 | 760.6756 |  | 827.4972 | 938.2972 | 1015.3482 | 618.3697 | 694.2055 | 905.5302 |  | 1037.7064 |  |  | 440.9527 | 661.3017 | 753.5284 | [6 empty] | 629.1298 |  |  | 428.4275 |  |  | 487.0067 | 673.7096 | 671.9482 | 944.8327 | 1118.8721 | 1081.3848 | 523.3662 | 747.5552 | 834.5419 | 614.5648 | 700.1534 | 1074.9787 | 1131.2041 | 633.5971 | 843.745 | 1051.0508 | 1153.8052 | 1073.6531 | 522.4215 | 633.2154 | 686.0274 | 592.0617 | 766.6655 | 897.6116 | 1147.5915 | 1128.1116 | 582.2576 | 679.0501 | 689.3646 | 875.2475 | 95.8674 | 4.3152e-05 | 18.2773 | 5.1098 | -39.9782 | 3.1224 | 11882.24 | 0.26 | 0.6517 | 1.05 | -1.4891 | -1.7156 | 6.8697 | 5.714 | 6.5269 | 85.0662 | 158.4257 | 51.7575 | 112.9554 | 36.0221 | 82.5824 | 33.103
42810.452 | 1030 | 17.6099 | 18.0274 | 18.1531 | 18.1928 | 17.5341 | 16.1595 | 14.7752 | 16.4782 | 16.9758 | 17.1077 | 17.1271 | 16.6471 | 15.6763 | 14.3929 | 17.2303 | 29.8203 | 30.231 | 85.111 | 32.8169 | 90.1057 |  |  |  | 23.1258 | 83.4039 | 318.3135 | 675.0248 | 717.4003 | 687.4105 | 94.7501 | 118.6402 | 923.1532 | 96.805 | 118.1705 | 845.6797 | 713.5613 | 863.6431 |  | 239.1579 | 904.3469 | 913.3127 | 497.4265 |  | 435.0129 | 701.3647 | 538.5774 | 691.3225 | 837.7747 | 1004.0302 | 1063.8127 | 50.4546 | 421.7311 | 86.4683 | 637.0939 | 14.029 | 53.6125 | 48.2759 | 50.0748 | 58.6107 |  |  | 0.14544 | -0.19705 | -0.68549 | -0.40413 | 7.9322 | 4.8221 | 6.7196 | -3.9764 | 25.1394 | 62.7602 | 18.6072 | 0.00018071 | 0.00017085 | -0.00081975 | 21.2358 | 16.3222 | 16.8235 | 17.2028 | 17.2 | 16.1742 | 14.6257 | 16.6876 | 17.0543 | 17.3797 | 17.443 | 17.1839 | 16.3634 | 14.6154 | 914.1393 | 614.0854 | 503.4777 | 320.5043 | 272.1463 | 918.5426 | 578.0602 | 16.5729 | 26.6899 | 31.8992 | 65.0936 | 80.5819 | 85.0875 |  |  |  | 597.9348 | 553.1521 | 568.7422 | 586.0048 | 140.6282 | 44.8225 | 916.5621 |  |  | 543.8532 |  |  | 18.6479 | 46.4827 | 420.8573 | 17.8652 | 46.3915 | 835.3766 | 762.2705 | 635.8598 | 900.6876 | 922.9365 | 762.1675 |  | 828.5245 | 937.1667 | 1017.0127 | 616.5837 | 694.5981 | 907.6385 |  | 1038.586 |  |  | 441.2158 | 658.8685 | 753.8133 | [6 empty] | 627.3055 |  |  | 426.7792 |  |  | 487.4209 | 675.0149 | 674.3573 | 940.8641 | 1115.8235 | 1075.8546 | 523.0316 | 746.3215 | 834.5851 | 615.9191 | 702.1233 | 1069.7065 | 1125.9982 | 633.4936 | 840.0338 | 1066.0733 | 1147.3124 | 1065.3052 | 523.5175 | 636.0532 | 685.6325 | 588.8738 | 762.0678 | 890.0662 | 1151.8351 | 1117.1917 | 584.3455 | 680.1739 | 684.8961 | 866.0304 | 97.6682 | 0.00021152 | 18.278 | 5.1405 | -39.9644 | 3.1223 | 11860.76 | 0.3 | 0.82371 | -0.9657 | -1.8012 | -1.383 | 7.0144 | 5.469 | 6.456 | 85.3643 | 159.3125 | 51.8987 | 114.8403 | 38.0536 | 59.7494 | 32.977
42810.452 | 1031 | 17.6071 | 18.0242 | 18.1557 | 18.1973 | 17.5384 | 16.1608 | 14.7815 | 16.4784 | 16.9737 | 17.1073 | 17.1212 | 16.6487 | 15.6761 | 14.3923 | 17.3093 | 29.9935 | 30.3809 | 85.1968 | 32.9044 | 90.1408 |  |  |  | 23.2457 | 83.5822 | 318.9412 | 673.7423 | 715.0464 | 684.9328 | 89.8781 | 115.8064 | 905.3473 | 93.576 | 115.2999 | 834.9014 | 804.3626 | 853.6126 |  | 241.79 | 889.3597 | 898.6399 | 468.1322 |  | 436.7242 | 701.9822 | 539.8081 | 690.3563 | 839.9893 | 1005.1013 | 1065.8511 | 51.07 | 422.345 | 84.8836 | 637.7979 | 14.0407 | 53.6817 | 48.27 | 50.1089 | 58.5188 |  |  | 0.004163 | 0.38319 | 0.00908 | -0.55066 | 7.8678 | 5.7565 | 6.688 | -3.132 | 24.7399 | 61.0684 | 18.1321 | 0.00014621 | 0.00012157 | -0.00081318 | 21.2732 | 16.3151 | 16.8158 | 17.1908 | 17.1876 | 16.1616 | 14.6186 | 16.6741 | 17.0422 | 17.376 | 17.4315 | 17.1732 | 16.3532 | 14.6089 | 914.3704 | 613.9348 | 509.278 | 319.132 | 273.1685 | 918.5859 | 577.2483 | 16.5964 | 26.7848 | 32.0209 | 65.451 | 80.6329 | 85.127 |  |  |  | 598.5099 | 556.2388 | 571.2671 | 589.8691 | 122.9377 | 32.7858 | 919.9232 |  |  | 546.7857 |  |  | 18.6579 | 46.592 | 422.0121 | 17.8784 | 46.5376 | 819.5396 | 763.7347 | 633.0547 | 899.1733 | 920.2897 | 764.2392 |  | 829.5846 | 937.2685 | 1016.3728 | 613.233 | 694.5544 | 906.0008 |  | 1038.9036 |  |  | 441.559 | 659.6216 | 755.2386 | [6 empty] | 624.1048 |  |  | 423.4804 |  |  | 487.9275 | 675.4915 | 675.5143 | 936.1466 | 1107.4621 | 1071.5834 | 523.4815 | 744.7323 | 833.9322 | 617.0996 | 702.8208 | 1064.2987 | 1123.3523 | 634.2917 | 837.0827 | 1080.5384 | 1142.7245 | 1056.4608 | 524.1622 | 637.8563 | 684.8304 | 585.611 | 757.2237 | 882.6378 | 1157.2234 | 1108.1262 | 584.8697 | 680.4871 | 680.4275 | 857.0639 | 98.1694 | -0.00012525 | 18.2765 | 5.1682 | -39.9314 | 3.1223 | 11857.78 | 0.29 | 0.13918 | 1.3471 | 0.20737 | -1.6149 | 6.9888 | 5.978 | 6.4435 | 85.6582 | 158.9804 | 51.9815 | 114.836 | 37.2055 | 85.7712 | 32.9719
42810.452 | 1032 | 17.612 | 18.0246 | 18.1556 | 18.1868 | 17.5306 | 16.1596 | 14.7821 | 16.4752 | 16.9743 | 17.1083 | 17.1253 | 16.6518 | 15.6751 | 14.396 | 17.3873 | 30.1538 | 30.5195 | 85.2662 | 32.9788 | 90.1881 |  |  |  | 23.356 | 83.7615 | 318.8484 | 672.0364 | 712.2175 | 681.8699 | 91.2612 | 115.116 | 891.0986 | 90.7203 | 114.2851 | 827.3214 | 838.1973 | 846.9685 |  | 251.2392 | 876.0369 | 885.1087 | 464.5851 |  | 439.3533 | 703.359 | 540.6729 | 692.9672 | 847.077 | 1006.6196 | 1064.9797 | 52.1725 | 422.8105 | 83.5875 | 638.3559 | 14.0622 | 53.6869 | 48.2732 | 50.1388 | 58.5572 |  |  | 0.14873 | 0.76234 | -0.90168 | -0.68866 | 6.4806 | 6.0003 | 7.8741 | -4.1216 | 24.2657 | 59.8965 | 18.3133 | 0.00017085 | 0.00020699 | -0.00077047 | 21.3265 | 16.3124 | 16.809 | 17.1829 | 17.18 | 16.1582 | 14.6124 | 16.6675 | 17.0463 | 17.3718 | 17.4423 | 17.1827 | 16.3522 | 14.6032 | 904.5501 | 597.1094 | 501.0452 | 312.6801 | 262.5256 | 918.4992 | 576.3155 | 16.6101 | 26.8883 | 32.1356 | 65.8124 | 80.6934 | 85.1557 |  |  |  | 599.055 | 557.7173 | 571.7333 | 592.1189 | 164.7134 | 66.8054 | 916.324 |  |  | 546.096 |  |  | 18.6699 | 46.694 | 422.2592 | 17.8881 | 46.6802 | 806.5189 | 765.2196 | 629.7363 | 894.651 | 912.9335 | 767.1145 |  | 830.5204 | 929.1293 | 1014.7662 | 609.401 | 694.1435 | 905.5115 |  | 1038.7769 |  |  | 442.1509 | 665.2896 | 757.4567 | [6 empty] | 620.396 |  |  | 420.6123 |  |  | 488.4683 | 675.3824 | 675.8536 | 931.223 | 1097.536 | 1072.7783 | 524.1607 | 743.2749 | 833.6556 | 617.7408 | 702.4718 | 1056.477 | 1118.4183 | 635.2091 | 834.4163 | 1103.1095 | 1137.0803 | 1050.2724 | 524.744 | 638.6221 | 684.1026 | 582.4135 | 752.5796 | 875.572 | 1156.7427 | 1100.6338 | 585.1688 | 680.7132 | 676.6966 | 848.1924 | 91.1945 | -0.0012898 | 18.2765 | 5.2034 | -39.9352 | 3.1223 | 11775.63 | 0.33 | 0.83055 | 1.9014 | -2.0679 | -1.8072 | 6.3466 | 6.1069 | 6.9957 | 85.8893 | 158.382 | 51.9922 | 115.8843 | 37.8868 | 96.8714 | 33.0065
42810.452 | 1033 | 17.6013 | 18.0222 | 18.1467 | 18.1812 | 17.5232 | 16.1587 | 14.7872 | 16.4668 | 16.9724 | 17.1034 | 17.1193 | 16.6498 | 15.6766 | 14.3971 | 17.471 | 30.3275 | 30.664 | 85.327 | 33.0925 | 90.2293 |  |  |  | 23.4707 | 83.9214 | 318.3687 | 670.0671 | 709.4339 | 679.5183 | 94.1854 | 115.3028 | 878.9536 | 89.4367 | 110.2354 | 821.6857 | 821.2159 | 844.7486 |  | 256.1019 | 865.9737 | 873.7309 | 487.9324 |  | 439.5816 | 703.0382 | 540.9691 | 695.8446 | 854.9116 | 1010.2943 | 1066.8467 | 53.7504 | 423.0925 | 83.3253 | 639.1581 | 14.0632 | 53.6661 | 48.2773 | 50.1736 | 58.6844 |  |  | 0.66654 | -0.16813 | -0.33525 | -0.72349 | 6.7146 | 4.6053 | 5.5755 | -4.1137 | 24.031 | 60.3014 | 18.2956 | 0.00011171 | 0.00018564 | -0.00082468 | 21.385 | 16.3128 | 16.8239 | 17.1986 | 17.1925 | 16.1755 | 14.6278 | 16.6854 | 17.0514 | 17.378 | 17.4473 | 17.1828 | 16.3621 | 14.6165 | 930.006 | 627.6067 | 597.0543 | 353.6451 | 270.5838 | 920.3208 | 578.3296 | 16.6403 | 27.0039 | 32.2676 | 66.1851 | 80.7538 | 85.2099 |  |  |  | 599.394 | 557.3263 | 571.2307 | 590.6843 | 126.6376 | 51.1422 | 909.8729 |  |  | 549.0051 |  |  | 18.6872 | 46.8055 | 421.6434 | 17.9123 | 46.842 | 796.8858 | 764.1685 | 627.1684 | 892.7521 | 914.065 | 766.9492 |  | 830.9362 | 924.5965 | 1013.455 | 605.1807 | 693.6635 | 903.1044 |  | 1037.8763 |  |  | 442.4537 | 668.3785 | 757.9652 | [6 empty] | 617.3088 |  |  | 419.4149 |  |  | 488.9269 | 674.4397 | 675.61 | 925.8652 | 1088.1945 | 1072.284 | 525.0335 | 741.7641 | 832.7408 | 617.5344 | 701.0575 | 1049.4114 | 1111.436 | 635.7376 | 829.4688 | 1112.9161 | 1131.6676 | 1045.386 | 525.7163 | 638.8505 | 683.2795 | 579.7324 | 747.9404 | 869.3816 | 1151.8315 | 1095.4295 | 585.2901 | 681.7718 | 673.3231 | 841.1582 | 85.2474 | -0.00010418 | 18.2774 | 5.2337 | -39.9874 | 3.1223 | 11630.79 | 0.3 | 1.7561 | -0.89281 | -1.2607 | -1.852 | 6.4694 | 5.3578 | 5.8952 | 86.0323 | 157.8372 | 51.9976 | 113.9589 | 27.7239 | 90.5846 | 33.1068
42810.452 | 1034 | 17.5925 | 18.0225 | 18.1397 | 18.1806 | 17.515 | 16.1571 | 14.7769 | 16.469 | 16.9729 | 17.1015 | 17.1071 | 16.6457 | 15.6677 | 14.3871 | 17.5633 | 30.4972 | 30.821 | 85.3829 | 33.1649 | 90.3011 |  |  |  | 23.6031 | 84.0591 | 318.4881 | 668.3769 | 707.5845 | 678.299 | 92.7204 | 118.5114 | 873.6505 | 91.5867 | 109.9758 | 817.0617 | 881.8599 | 841.0026 |  | 257.6019 | 858.8312 | 865.3279 | 494.9666 |  | 440.1453 | 703.8806 | 542.3396 | 696.9741 | 849.383 | 1009.0859 | 1067.882 | 55.7641 | 423.4465 | 84.323 | 639.9319 | 14.0635 | 53.6326 | 48.2779 | 50.2027 | 58.8651 |  |  | 0.65668 | -0.52363 | -0.37008 | -0.49744 | 7.0609 | 6.7475 | 7.1237 | -3.9902 | 23.3547 | 58.4623 | 17.465 | 0.00022671 | 0.00016428 | -0.00077375 | 21.4322 | 16.316 | 16.8137 | 17.185 | 17.1922 | 16.1725 | 14.6193 | 16.6733 | 17.0496 | 17.3775 | 17.4454 | 17.177 | 16.3594 | 14.615 | 922.3421 | 631.7832 | 585.2724 | 364.7756 | 272.6657 | 920.2106 | 578.5381 | 16.6629 | 27.1066 | 32.3891 | 66.51 | 80.8129 | 85.247 |  |  |  | 599.3994 | 556.2661 | 569.9306 | 587.6948 | 140.8044 | 38.9951 | 908.2963 |  |  | 551.0592 |  |  | 18.7058 | 46.9115 | 421.1521 | 17.9263 | 46.9859 | 788.5264 | 760.7637 | 625.0889 | 894.7106 | 920.0489 | 762.9224 |  | 830.3898 | 923.4602 | 1013.4229 | 602.3794 | 693.2696 | 910.0606 |  | 1037.479 |  |  | 442.089 | 665.4146 | 755.1501 | [6 empty] | 614.9077 |  |  | 419.26 |  |  | 489.055 | 673.0549 | 675.0642 | 922.5355 | 1081.1496 | 1071.2993 | 525.6396 | 740.0025 | 831.2285 | 616.8256 | 700.2552 | 1045.331 | 1112.9013 | 636.3074 | 825.5569 | 1111.7907 | 1126.4866 | 1041.2283 | 526.4822 | 639.546 | 682.1772 | 577.7236 | 743.5939 | 864.49 | 1151.7434 | 1092.5851 | 585.4878 | 682.7037 | 670.3513 | 836.6496 | 87.8568 | -0.00049703 | 18.2776 | 5.2603 | -40.026 | 3.1223 | 11524.22 | 0.37 | 1.742 | -1.5763 | -1.3252 | -1.5364 | 6.631 | 6.4822 | 6.6605 | 85.9623 | 157.8523 | 51.9838 | 114.7558 | 29.0853 | 111.6551 | 33.1908
42810.452 | 1035 | 17.5995 | 18.019 | 18.1433 | 18.1801 | 17.5355 | 16.1609 | 14.7865 | 16.4808 | 16.9731 | 17.1023 | 17.1199 | 16.6484 | 15.6804 | 14.4007 | 17.6453 | 30.6661 | 30.9704 | 85.4458 | 33.2009 | 90.3711 |  |  |  | 23.7083 | 84.1863 | 319.7105 | 667.352 | 706.9018 | 677.7024 | 88.7071 | 119.6727 | 870.8618 | 95.0653 | 116.6992 | 821.8858 | 894.5036 | 842.6251 |  | 265.0432 | 854.398 | 862.3009 | 499.3391 |  | 440.5398 | 705.3065 | 544.3378 | 699.4194 | 850.4419 | 1010.3619 | 1065.9165 | 56.8967 | 423.6986 | 84.9517 | 640.1517 | 14.0549 | 53.6161 | 48.2693 | 50.2311 | 59.1055 |  |  | 0.26701 | 0.45744 | -0.79786 | -1.1362 | 7.2646 | 5.8045 | 6.0434 | -3.1655 | 23.4579 | 58.443 | 17.2916 | 0.00012814 | 0.00018892 | -0.00083125 | 21.4726 | 16.3134 | 16.8085 | 17.1873 | 17.1849 | 16.1717 | 14.6176 | 16.6725 | 17.0462 | 17.3692 | 17.4457 | 17.1734 | 16.3566 | 14.6116 | 912.6859 | 603.3595 | 522.6937 | 347.6896 | 280.1058 | 919.7329 | 577.4216 | 16.6894 | 27.2165 | 32.5044 | 66.8096 | 80.8748 | 85.2787 |  |  |  | 599.509 | 555.2014 | 568.0266 | 586.9612 | 115.964 | 35.0143 | 913.6832 |  |  | 549.6258 |  |  | 18.7178 | 47.0214 | 422.3023 | 17.9499 | 47.1164 | 783.192 | 757.9466 | 622.5132 | 898.936 | 925.2326 | 760.0143 |  | 829.7499 | 930.354 | 1012.8873 | 599.5382 | 692.6227 | 917.6054 |  | 1037.0284 |  |  | 442.1274 | 660.031 | 752.1249 | [6 empty] | 612.2373 |  |  | 419.1165 |  |  | 489.0364 | 671.5979 | 674.5756 | 920.498 | 1075.7187 | 1073.8987 | 525.7298 | 738.724 | 830.7712 | 615.5966 | 699.5739 | 1042.0812 | 1105.276 | 636.9876 | 823.2889 | 1114.3397 | 1129.125 | 1038.7973 | 526.373 | 641.025 | 680.8583 | 575.7806 | 740.216 | 860.864 | 1157.506 | 1094.6737 | 585.8817 | 682.4869 | 667.6496 | 833.5866 | 88.3762 | -0.00030063 | 18.2778 | 5.284 | -39.9836 | 3.1223 | 11365.35 | 0.27 | 1.1104 | 1.4744 | -1.9472 | -2.3236 | 6.7293 | 6.0152 | 6.1377 | 85.8304 | 157.3874 | 51.9125 | 115.5916 | 35.7583 | 116.3764 | 33.2308
42810.452 | 1036 | 17.5921 | 18.0096 | 18.1421 | 18.1815 | 17.519 | 16.1616 | 14.7785 | 16.4752 | 16.9758 | 17.1145 | 17.115 | 16.6543 | 15.6798 | 14.393 | 17.7306 | 30.8347 | 31.1164 | 85.5148 | 33.2818 | 90.4429 |  |  |  | 23.8412 | 84.2873 | 321.8034 | 667.3627 | 706.7906 | 678.3207 | 88.9558 | 114.3074 | 862.3201 | 95.0559 | 118.0437 | 820.6245 | 811.1972 | 844.3721 |  | 260.2162 | 847.6906 | 853.0325 | 491.4212 |  | 441.3495 | 706.4092 | 544.1587 | 698.4935 | 845.2411 | 1008.4283 | 1064.5346 | 59.0155 | 423.6871 | 87.4046 | 640.4676 | 14.0679 | 53.5571 | 48.2627 | 50.2615 | 59.428 |  |  | 0.66851 | -0.59855 | -0.29648 | -0.66829 | 7.9624 | 6.1902 | 7.0153 | -4.1039 | 22.1323 | 58.5378 | 17.3152 | 0.00013471 | 0.00014949 | -0.00083125 | 21.524 | 16.3139 | 16.809 | 17.1879 | 17.1829 | 16.1668 | 14.6207 | 16.6715 | 17.0426 | 17.3713 | 17.441 | 17.1716 | 16.3596 | 14.6115 | 886.3417 | 584.0124 | 498.7956 | 338.7306 | 270.0245 | 917.7782 | 575.8227 | 16.724 | 27.3161 | 32.6285 | 67.0832 | 80.9267 | 85.3022 |  |  |  | 599.5038 | 552.8839 | 566.0911 | 584.4215 | 119.7089 | 45.692 | 923.6143 |  |  | 558.8382 |  |  | 18.7387 | 47.1301 | 424.6669 | 17.995 | 47.2681 | 778.0818 | 756.1121 | 619.6117 | 895.8783 | 918.3508 | 758.7357 |  | 829.1047 | 941.3879 | 1011.3628 | 595.8113 | 691.4087 | 924.4564 |  | 1035.2771 |  |  | 442.5134 | 658.8817 | 750.5276 | [6 empty] | 609.2991 |  |  | 418.807 |  |  | 489.452 | 670.4163 | 674.2486 | 920.431 | 1068.3536 | 1069.1309 | 525.6218 | 738.1409 | 829.5255 | 614.5788 | 698.3562 | 1039.0058 | 1099.4993 | 637.3447 | 822.1688 | 1120.8197 | 1131.5789 | 1038.264 | 526.2506 | 641.8954 | 679.5182 | 572.949 | 737.563 | 858.6572 | 1165.2424 | 1097.7611 | 585.9002 | 682.6948 | 665.2993 | 830.48 | 81.8583 | -0.00044792 | 18.2769 | 5.2968 | -40.0184 | 3.1223 | 11150.97 | 0.33 | 1.7576 | -1.6874 | -1.1876 | -1.783 | 7.0398 | 6.2072 | 6.6079 | 85.6519 | 156.3045 | 51.7347 | 117.5508 | 38.0135 | 87.2719 | 33.3004
42810.452 | 1037 | 17.5867 | 18.012 | 18.1389 | 18.1785 | 17.5212 | 16.152 | 14.7882 | 16.4738 | 16.9627 | 17.1013 | 17.1203 | 16.6463 | 15.6694 | 14.3889 | 17.8066 | 31.0087 | 31.2584 | 85.5746 | 33.3783 | 90.4912 |  |  |  | 23.9624 | 84.3712 | 323.5762 | 667.6317 | 706.1665 | 678.5925 | 88.077 | 116.4643 | 855.7233 | 91.5023 | 115.6104 | 819.3946 | 796.7856 | 845.4487 |  | 248.1148 | 844.3605 | 850.0527 | 500.3025 |  | 442.3889 | 707.8674 | 543.4946 | 697.3512 | 848.3778 | 1011.4215 | 1065.3447 | 59.6134 | 423.7291 | 90.2673 | 641.1803 | 14.0866 | 53.5272 | 48.2558 | 50.2957 | 59.7227 |  |  | 0.61922 | -0.57949 | -0.58495 | -1.2676 | 7.9473 | 5.4871 | 6.1919 | -4.3049 | 22.4522 | 56.483 | 16.9426 | 0.00016264 | 0.000138 | -0.00082304 | 21.5812 | 16.3116 | 16.8086 | 17.1913 | 17.1789 | 16.1744 | 14.622 | 16.6738 | 17.0443 | 17.372 | 17.4413 | 17.1711 | 16.3587 | 14.6149 | 882.0878 | 593.4559 | 500.4249 | 342.6078 | 274.5774 | 915.5513 | 574.7648 | 16.7457 | 27.4261 | 32.7619 | 67.3406 | 81.0001 | 85.3392 |  |  |  | 599.2947 | 550.0911 | 563.5601 | 580.7523 | 96.6769 | 34.2361 | 922.7562 |  |  | 582.857 |  |  | 18.756 | 47.2448 | 427.1609 | 18.0119 | 47.4122 | 772.74 | 754.3536 | 616.3486 | 895.0903 | 918.4661 | 757.3005 |  | 828.4235 | 930.5804 | 1009.0964 | 592.4538 | 690.1881 | 912.0627 |  | 1033.8444 |  |  | 443.1804 | 661.2218 | 749.6772 | [6 empty] | 605.8754 |  |  | 419.364 |  |  | 489.7311 | 669.2682 | 673.6905 | 927.639 | 1065.5507 | 1064.7165 | 525.2954 | 737.0633 | 828.5259 | 613.7793 | 695.3028 | 1043.3829 | 1098.7721 | 636.6463 | 819.4407 | 1116.5699 | 1146.6887 | 1037.6546 | 525.5309 | 642.0386 | 678.7304 | 570.5528 | 735.5391 | 855.4027 | 1174.0557 | 1104.9769 | 586.0514 | 683.0961 | 664.0431 | 827.5409 | 86.2992 | -0.00053212 | 18.2757 | 5.3206 | -40.0605 | 3.1223 | 11006.01 | 0.35 | 1.6918 | -1.6616 | -1.6694 | -2.4575 | 7.0414 | 5.8508 | 6.2152 | 85.4661 | 155.4552 | 51.5461 | 116.9254 | 37.5684 | 82.5399 | 33.365
42810.452 | 1038 | 17.5843 | 18.0083 | 18.1354 | 18.18 | 17.5204 | 16.1603 | 14.7891 | 16.4716 | 16.9693 | 17.1091 | 17.1204 | 16.6514 | 15.6774 | 14.3973 | 17.9084 | 31.1968 | 31.4177 | 85.6546 | 33.4458 | 90.5607 |  |  |  | 24.0943 | 84.4793 | 324.9987 | 667.0505 | 705.772 | 677.5374 | 88.2036 | 113.9204 | 852.1764 | 91.3524 | 114.3705 | 815.8074 | 833.5344 | 844.3384 |  | 247.8013 | 845.4875 | 853.4223 | 491.35 |  | 443.2047 | 709.3439 | 543.5453 | 699.1892 | 854.6453 | 1015.0281 | 1066.5983 | 59.4615 | 423.6641 | 92.6226 | 641.6027 | 14.0836 | 53.489 | 48.2429 | 50.3144 | 59.9845 |  |  | 0.6074 | -0.020281 | -0.83072 | -0.80497 | 7.4065 | 5.0357 | 7.2985 | -4.8142 | 22.1829 | 56.6219 | 16.3936 | 0.00021356 | 0.00014457 | -0.00080497 | 21.619 | 16.318 | 16.7961 | 17.184 | 17.1765 | 16.1679 | 14.6191 | 16.6656 | 17.0346 | 17.3677 | 17.4372 | 17.1675 | 16.3528 | 14.6133 | 856.0425 | 577.565 | 462.7635 | 328.9771 | 263.0978 | 910.7458 | 572.7429 | 16.757 | 27.5304 | 32.8774 | 67.5502 | 81.0424 | 85.3587 |  |  |  | 599.2078 | 548.8332 | 562.0744 | 580.6152 | 88.7575 | 35.7422 | 918.3155 |  |  | 590.0018 |  |  | 18.7762 | 47.3487 | 428.687 | 18.0261 | 47.5555 | 771.1491 | 752.0422 | 613.619 | 899.7278 | 923.2562 | 755.1503 |  | 827.5756 | 922.6441 | 1007.0362 | 589.4032 | 688.9368 | 901.6392 |  | 1033.2825 |  |  | 443.6073 | 661.3457 | 747.7748 | [6 empty] | 602.7243 |  |  | 420.3963 |  |  | 489.6297 | 667.9312 | 672.2175 | 934.0098 | 1064.0384 | 1062.7774 | 525.1867 | 734.6912 | 826.6125 | 613.5417 | 693.2235 | 1052.7913 | 1097.8728 | 635.8456 | 816.1412 | 1112.9301 | 1156.69 | 1039.4569 | 525.5157 | 642.4414 | 678.1973 | 568.2576 | 734.6378 | 853.3982 | 1175.2587 | 1108.4643 | 586.4108 | 683.1776 | 663.4193 | 826.0959 | 84.9395 | -5.9595e-06 | 18.277 | 5.3305 | -40.0083 | 3.1222 | 10867.58 | 0.37 | 1.6746 | -0.31108 | -1.9909 | -1.9598 | 6.8071 | 5.6129 | 6.7573 | 85.2455 | 154.6357 | 51.3429 | 117.4658 | 41.2498 | 94.5559 | 33.3533
42810.4521 | 1039 | 17.5817 | 18.0115 | 18.135 | 18.1776 | 17.5123 | 16.1631 | 14.7929 | 16.4751 | 16.9683 | 17.1016 | 17.1222 | 16.6494 | 15.6793 | 14.3991 | 18.0092 | 31.3682 | 31.5751 | 85.7331 | 33.5213 | 90.6316 |  |  |  | 24.2227 | 84.615 | 327.1892 | 666.8849 | 705.8494 | 677.2447 | 89.0773 | 114.3736 | 849.9536 | 89.0612 | 112.9972 | 815.3229 | 832.5104 | 844.7639 |  | 259.3317 | 847.5796 | 854.2878 | 478.7043 |  | 445.6188 | 710.891 | 543.6271 | 701.8163 | 856.8849 | 1018.2109 | 1068.6576 | 56.8622 | 423.6086 | 94.2943 | 641.9279 | 14.0604 | 53.4127 | 48.2409 | 50.3285 | 60.3063 |  |  | 0.69545 | 0.59018 | -0.66249 | -1.1132 | 6.6981 | 5.7697 | 6.9298 | -4.2182 | 22.0291 | 56.7851 | 16.8425 | 0.00011664 | 0.00014128 | -0.00080825 | 21.6735 | 16.3245 | 16.8083 | 17.1919 | 17.1817 | 16.1727 | 14.6171 | 16.6696 | 17.0496 | 17.368 | 17.4423 | 17.1811 | 16.3573 | 14.6179 | 814.7518 | 566.1439 | 480.8256 | 316.0948 | 259.603 | 904.9791 | 570.8099 | 16.7822 | 27.6436 | 33.0007 | 67.7843 | 81.094 | 85.3995 |  |  |  | 599.1942 | 548.2217 | 560.8473 | 580.2691 | 113.2366 | 39.6865 | 918.2449 |  |  | 593.6191 |  |  | 18.796 | 47.4558 | 430.7384 | 18.054 | 47.6971 | 772.358 | 749.5427 | 612.5112 | 902.1632 | 923.5802 | 753.3486 |  | 826.5584 | 918.0957 | 1006.5777 | 587.3255 | 687.969 | 896.1746 |  | 1034.925 |  |  | 443.7083 | 662.8889 | 746.2789 | [6 empty] | 601.6178 |  |  | 421.5318 |  |  | 489.8892 | 666.6179 | 670.6428 | 937.9033 | 1070.3854 | 1063.7809 | 525.6707 | 733.5211 | 824.829 | 613.3777 | 691.5574 | 1056.3809 | 1102.4955 | 635.9791 | 814.6324 | 1115.7054 | 1163.6517 | 1041.3579 | 525.9202 | 643.2651 | 677.253 | 567.0237 | 733.8096 | 851.7149 | 1185.8413 | 1118.1018 | 586.6615 | 682.5745 | 662.2933 | 824.9985 | 85.9316 | 0.00032376 | 18.2774 | 5.3419 | -39.9692 | 3.1222 | 10753.12 | 0.37 | 1.7916 | 1.6794 | -1.7794 | -2.3065 | 6.4814 | 6.0154 | 6.5925 | 84.9601 | 154.5313 | 51.1785 | 119.2584 | 38.7636 | 94.5644 | 33.3605
42810.4521 | 1040 | 17.5834 | 18.0042 | 18.1358 | 18.176 | 17.5129 | 16.1522 | 14.7988 | 16.4673 | 16.9618 | 17.0981 | 17.1153 | 16.6367 | 15.6752 | 14.3887 | 18.0931 | 31.5389 | 31.7273 | 85.7947 | 33.572 | 90.6859 |  |  |  | 24.3446 | 84.7641 | 329.2518 | 666.9688 | 706.1878 | 677.4711 | 92.3443 | 115.7778 | 852.7511 | 89.168 | 113.1345 | 815.9824 | 868.4079 | 844.432 |  | 254.9029 | 846.6665 | 852.7229 | 473.3117 |  | 446.3306 | 710.782 | 543.9187 | 700.493 | 850.0319 | 1016.1488 | 1064.5681 | 54.2791 | 423.5858 | 92.3933 | 641.9626 | 14.0481 | 53.3189 | 48.2453 | 50.3401 | 60.68 |  |  | 0.12244 | -0.001225 | -0.28268 | -0.38375 | 8.0065 | 6.1337 | 7.3931 | -3.475 | 21.1118 | 54.698 | 17.0573 | 0.00019056 | 7.721e-05 | -0.00082961 | 21.7301 | 16.3122 | 16.7967 | 17.1841 | 17.1809 | 16.1709 | 14.6273 | 16.6599 | 17.0443 | 17.3668 | 17.4342 | 17.1733 | 16.3566 | 14.6126 | 822.6719 | 564.1893 | 508.223 | 304.1365 | 260.9204 | 900.9003 | 568.8207 | 16.8047 | 27.7449 | 33.1111 | 68.0407 | 81.1316 | 85.4176 |  |  |  | 598.9968 | 547.523 | 559.0464 | 578.632 | 101.9775 | 39.6146 | 916.9696 |  |  | 597.7684 |  |  | 18.8108 | 47.5676 | 433.1521 | 18.0861 | 47.835 | 771.7779 | 745.9784 | 612.0177 | 897.6827 | 916.7923 | 749.8545 |  | 825.291 | 917.1003 | 1008.3907 | 585.9568 | 687.0938 | 899.5052 |  | 1035.8209 |  |  | 443.8164 | 660.9936 | 743.3824 | [6 empty] | 600.7694 |  |  | 422.1276 |  |  | 490.5788 | 665.8387 | 669.5559 | 934.9717 | 1071.0926 | 1063.4652 | 526.3605 | 731.9291 | 823.2766 | 613.2702 | 691.1219 | 1051.6891 | 1100.3251 | 635.356 | 812.0032 | 1125.3446 | 1177.2625 | 1047.1575 | 525.2756 | 643.7283 | 676.4852 | 565.3917 | 733.3246 | 849.2915 | 1192.4728 | 1130.551 | 586.1666 | 682.348 | 661.2646 | 823.9969 | 82.7411 | 0.00024657 | 18.2777 | 5.3512 | -39.9061 | 3.1223 | 10673.84 | 0.39 | 0.75186 | -0.07651 | -1.1622 | -1.3542 | 7.0805 | 6.1973 | 6.8039 | 84.6403 | 155.4729 | 51.0162 | 116.4204 | 35.2282 | 107.2635 | 33.3708
42810.4521 | 1041 | 17.5874 | 18.0027 | 18.139 | 18.178 | 17.5193 | 16.1539 | 14.8094 | 16.4634 | 16.9691 | 17.0989 | 17.121 | 16.6497 | 15.6855 | 14.3952 | 18.1766 | 31.7111 | 31.8714 | 85.8548 | 33.6575 | 90.728 |  |  |  | 24.4658 | 84.9043 | 331.4887 | 667.3643 | 706.7874 | 678.1095 | 93.7751 | 118.6312 | 854.0412 | 91.5235 | 114.4175 | 813.069 | 896.2341 | 841.8434 |  | 275.2869 | 842.408 | 848.1867 | 479.6514 |  | 447.6279 | 711.5802 | 545.0336 | 701.5189 | 847.9274 | 1015.4278 | 1064.516 | 53.678 | 423.651 | 91.4545 | 641.8287 | 14.0465 | 53.1919 | 48.2453 | 50.3372 | 61.0544 |  |  | 0.030447 | -0.021597 | -0.035604 | -0.69917 | 7.3822 | 6.8132 | 6.2491 | -4.3286 | 21.0009 | 56.593 | 16.2541 | 0.00015442 | 0.00015114 | -0.00081975 | 21.781 | 16.318 | 16.7963 | 17.1816 | 17.1771 | 16.1636 | 14.6212 | 16.6683 | 17.045 | 17.3719 | 17.4333 | 17.1662 | 16.3649 | 14.6089 | 813.7847 | 564.0681 | 512.3914 | 299.5732 | 256.2415 | 896.1468 | 566.8573 | 16.8328 | 27.8447 | 33.2281 | 68.2976 | 81.1851 | 85.4595 |  |  |  | 598.7427 | 547.7052 | 558.2835 | 577.9233 | 93.6017 | 34.1566 | 912.4216 |  |  | 593.7096 |  |  | 18.8389 | 47.6755 | 435.5021 | 18.1081 | 47.9915 | 768.0712 | 741.1988 | 613.3474 | 890.9575 | 909.7598 | 744.2176 |  | 824.0548 | 914.4461 | 1007.75 | 586.4784 | 686.7713 | 892.1355 |  | 1035.2197 |  |  | 443.3301 | 653.4805 | 738.678 | [6 empty] | 601.6673 |  |  | 422.8278 |  |  | 491.2799 | 665.1259 | 668.7747 | 936.2312 | 1066.5157 | 1061.0268 | 526.2955 | 729.4576 | 821.881 | 613.172 | 690.475 | 1050.6733 | 1099.5669 | 634.5362 | 808.2916 | 1129.8549 | 1179.6475 | 1050.748 | 524.6619 | 643.6084 | 675.9172 | 563.8185 | 732.7499 | 847.537 | 1190.6723 | 1130.9465 | 585.4395 | 682.1922 | 660.2146 | 824.0238 | 76.0217 | -0.00059525 | 18.2774 | 5.3584 | -39.9068 | 3.1223 | 10649.18 | 0.3 | 0.37505 | -0.32138 | -0.41264 | -1.8286 | 6.797 | 6.5298 | 6.2536 | 84.3916 | 155.2232 | 50.9281 | 115.1455 | 34.2821 | 117.5976 | 33.3452
42810.4521 | 1042 | 17.5751 | 17.9981 | 18.137 | 18.1759 | 17.5171 | 16.1436 | 14.8055 | 16.4619 | 16.9654 | 17.1 | 17.1187 | 16.6491 | 15.6734 | 14.391 | 18.2679 | 31.8856 | 32.0295 | 85.9099 | 33.7657 | 90.771 |  |  |  | 24.5988 | 85.0709 | 333.9245 | 668.2341 | 707.7271 | 679.2582 | 90.8601 | 120.3891 | 851.9811 | 93.3108 | 116.8356 | 814.4278 | 896.8948 | 839.9726 |  | 273.7374 | 837.852 | 842.6535 | 493.8671 |  | 449.4965 | 712.5301 | 547.5576 | 700.479 | 852.692 | 1018.6688 | 1066.082 | 55.4064 | 423.4949 | 88.0713 | 641.8251 | 14.0249 | 53.0207 | 48.2308 | 50.3318 | 61.4499 |  |  | 0.31892 | 0.67955 | -0.31094 | -0.52109 | 7.0431 | 6.4721 | 5.7378 | -3.9199 | 22.308 | 57.2094 | 15.4582 | 0.00014949 | 0.00020699 | -0.00078361 | 21.8356 | 16.3171 | 16.8008 | 17.1832 | 17.1802 | 16.1666 | 14.6246 | 16.6741 | 17.0502 | 17.3753 | 17.4376 | 17.1727 | 16.3638 | 14.617 | 788.8949 | 552.4449 | 494.6628 | 289.3652 | 248.4996 | 890.8226 | 564.6255 | 16.8578 | 27.9687 | 33.3628 | 68.5972 | 81.2575 | 85.496 |  |  |  | 598.3651 | 547.2918 | 557.7379 | 574.8626 | 85.2296 | 29.707 | 907.4297 |  |  | 595.727 |  |  | 18.855 | 47.7793 | 437.9148 | 18.1251 | 48.1463 | 763.7289 | 736.2543 | 615.2167 | 890.4604 | 911.8929 | 736.006 |  | 822.5976 | 912.6135 | 1006.5722 | 587.9238 | 686.7872 | 887.9916 |  | 1034.0996 |  |  | 442.9266 | 642.4034 | 732.5711 | [6 empty] | 603.4016 |  |  | 422.9866 |  |  | 492.1341 | 664.2611 | 668.0482 | 937.015 | 1064.9469 | 1059.3018 | 525.627 | 726.5088 | 821.3473 | 613.2022 | 690.4143 | 1049.777 | 1099.5597 | 632.8764 | 805.3123 | 1133.6307 | 1175.3331 | 1050.8249 | 524.2898 | 642.5596 | 675.8994 | 562.6046 | 732.1877 | 848.2408 | 1184.6248 | 1128.0661 | 584.1467 | 682.5035 | 659.3034 | 825.4457 | 80.4386 | -0.0012267 | 18.2777 | 5.3671 | -39.9529 | 3.1222 | 10624.59 | 0.35 | 1.2146 | 1.8036 | -1.22 | -1.5794 | 6.6474 | 6.3722 | 5.9999 | 84.1436 | 154.6808 | 50.8916 | 115.4021 | 35.7051 | 117.4609 | 33.363
42810.4521 | 1043 | 17.5824 | 17.9953 | 18.1369 | 18.1724 | 17.5162 | 16.1553 | 14.7981 | 16.4737 | 16.9584 | 17.0967 | 17.1179 | 16.6484 | 15.6791 | 14.3965 | 18.3563 | 32.0586 | 32.1803 | 85.9446 | 33.9235 | 90.8206 |  |  |  | 24.7222 | 85.2663 | 337.7631 | 669.9507 | 709.7095 | 681.4423 | 90.81 | 117.6331 | 847.6858 | 96.4924 | 119.0267 | 822.7005 | 631.5759 | 851.39 |  | 268.469 | 834.9516 | 839.8604 | 491.4036 |  | 449.9973 | 711.4494 | 547.4292 | 698.6452 | 860.3083 | 1021.8751 | 1065.5217 | 57.486 | 423.0755 | 85.0337 | 641.7165 | 14.0104 | 52.8313 | 48.2179 | 50.3391 | 61.8252 |  |  | 0.65931 | -0.009113 | -0.36679 | -0.93771 | 7.6621 | 5.7151 | 7.5876 | -3.0216 | 21.6818 | 56.474 | 15.629 | 0.00012321 | 0.00011992 | -0.00081482 | 21.8927 | 16.3209 | 16.8044 | 17.1828 | 17.1799 | 16.1707 | 14.6275 | 16.6769 | 17.0552 | 17.3765 | 17.4407 | 17.1777 | 16.3657 | 14.622 | 783.1941 | 544.6052 | 464.8472 | 293.122 | 243.7888 | 885.3181 | 561.8322 | 16.8873 | 28.0755 | 33.4828 | 68.8772 | 81.3183 | 85.54 |  |  |  | 598.0047 | 547.0184 | 557.3059 | 573.1401 | 98.2436 | 33.1725 | 906.9754 |  |  | 598.0367 |  |  | 18.8666 | 47.8766 | 442.0512 | 18.1571 | 48.2687 | 760.964 | 732.9653 | 615.9686 | 886.3435 | 906.5595 | 727.7164 |  | 821.0722 | 912.644 | 1008.1867 | 589.0709 | 686.682 | 886.6541 |  | 1034.1767 |  |  | 441.8744 | 632.35 | 726.9124 | [6 empty] | 604.1066 |  |  | 423.2573 |  |  | 492.9382 | 664.0451 | 667.617 | 936.6865 | 1064.3418 | 1063.3469 | 524.4647 | 723.4992 | 821.9521 | 613.4181 | 691.2777 | 1048.5037 | 1104.9896 | 631.183 | 803.8211 | 1134.6256 | 1170.3614 | 1051.643 | 524.2004 | 641.5036 | 676.4066 | 561.3415 | 731.8235 | 851.8691 | 1182.6345 | 1126.3423 | 583.5137 | 683.7416 | 658.4792 | 828.0039 | 75.1999 | 5.7172e-05 | 18.2771 | 5.3716 | -39.9455 | 3.1222 | 10672.59 | 0.4 | 1.7483 | -0.20875 | -1.3244 | -2.1175 | 6.9419 | 5.9954 | 6.9081 | 83.8772 | 155.4936 | 50.8357 | 113.4691 | 38.3369 | 41.8821 | 33.3468
42810.4521 | 1044 | 17.5711 | 17.9921 | 18.1303 | 18.1743 | 17.5057 | 16.1422 | 14.7975 | 16.4638 | 16.9542 | 17.0989 | 17.1106 | 16.6359 | 15.6755 | 14.3925 | 18.445 | 32.2309 | 32.3241 | 85.9819 | 34.0588 | 90.8644 |  |  |  | 24.8518 | 85.4647 | 341.8021 | 671.8365 | 711.2688 | 683.8683 | 90.7651 | 119.0066 | 845.8097 | 93.1137 | 117.0001 | 825.9235 | 639.9261 | 858.3563 |  | 248.2802 | 837.6347 | 840.8392 | 514.3624 |  | 450.0501 | 712.1795 | 549.4151 | 695.5859 | 859.1676 | 1018.5073 | 1063.0472 | 59.2703 | 422.6683 | 85.0644 | 641.6671 | 13.9841 | 52.657 | 48.1918 | 50.3245 | 62.1314 |  |  | 0.47597 | 0.14137 | -0.58036 | -1.3136 | 6.4938 | 5.4181 | 6.9029 | -3.6859 | 21.4739 | 55.5238 | 16.546 | 0.00015114 | 0.00015771 | -0.00079182 | 21.9518 | 16.3212 | 16.807 | 17.1905 | 17.1806 | 16.1797 | 14.6261 | 16.6832 | 17.051 | 17.3819 | 17.4478 | 17.1812 | 16.3686 | 14.6283 | 788.065 | 544.5768 | 488.0923 | 308.763 | 250.4884 | 881.0182 | 559.7121 | 16.9173 | 28.1846 | 33.6061 | 69.1356 | 81.3802 | 85.5712 |  |  |  | 597.834 | 547.1333 | 556.9703 | 574.778 | 91.808 | 39.4974 | 902.5694 |  |  | 596.9107 |  |  | 18.8873 | 47.9755 | 446.8484 | 18.1791 | 48.4106 | 761.0323 | 730.677 | 617.1885 | 879.9899 | 899.3922 | 725.3634 |  | 819.6265 | 908.056 | 1008.9652 | 590.3723 | 686.5447 | 883.3475 |  | 1034.4105 |  |  | 440.0767 | 628.0345 | 723.3768 | [6 empty] | 605.3567 |  |  | 423.2782 |  |  | 493.4091 | 664.1879 | 668.0988 | 932.9234 | 1067.728 | 1067.7123 | 522.8153 | 721.4368 | 822.1656 | 613.9198 | 692.4876 | 1045.9083 | 1103.8955 | 629.8525 | 802.8314 | 1138.3917 | 1170.9726 | 1053.765 | 524.4392 | 641.0739 | 677.2818 | 559.5009 | 731.3284 | 853.8074 | 1186.3742 | 1127.8007 | 583.7528 | 685.1446 | 656.9851 | 828.9208 | 71.2421 | 0.00037988 | 18.2761 | 5.3804 | -39.967 | 3.1222 | 10722.97 | 0.31 | 1.4874 | 0.82249 | -1.6665 | -2.5072 | 6.3825 | 5.8299 | 6.5805 | 83.4737 | 156.0145 | 50.7682 | 110.9424 | 35.2397 | 42.8983 | 33.2709
42810.4521 | 1045 | 17.5766 | 17.9985 | 18.137 | 18.1709 | 17.5118 | 16.1493 | 14.8078 | 16.4628 | 16.9679 | 17.1031 | 17.1141 | 16.6431 | 15.6743 | 14.394 | 18.5425 | 32.4093 | 32.4852 | 86.0344 | 34.1391 | 90.9109 |  |  |  | 24.9834 | 85.6513 | 344.5027 | 672.6422 | 711.9521 | 684.0799 | 87.6441 | 118.5673 | 846.6886 | 91.4772 | 114.5735 | 823.1669 | 828.0355 | 857.502 |  | 242.1689 | 841.2381 | 845.4142 | 500.4788 |  | 450.6139 | 712.9632 | 551.5373 | 696.0566 | 851.0144 | 1016.2686 | 1061.7778 | 59.8721 | 422.2754 | 87.8667 | 641.6203 | 13.9315 | 52.5294 | 48.1679 | 50.316 | 62.4046 |  |  | 0.18224 | -1.1663 | -1.0456 | -0.60717 | 6.4353 | 6.5891 | 7.516 | -4.0322 | 21.1297 | 54.7167 | 16.6233 | 0.00013307 | 0.000138 | -0.00082796 | 21.9982 | 16.3135 | 16.7886 | 17.1808 | 17.1761 | 16.1654 | 14.6248 | 16.6711 | 17.0457 | 17.3744 | 17.4364 | 17.1757 | 16.3626 | 14.6232 | 783.8884 | 539.0731 | 494.0477 | 330.4856 | 259.6896 | 876.6409 | 557.8781 | 16.9412 | 28.2773 | 33.7115 | 69.3717 | 81.4321 | 85.5994 |  |  |  | 597.9574 | 547.9099 | 556.5454 | 579.2591 | 103.7839 | 36.2475 | 897.2796 |  |  | 601.2284 |  |  | 18.9016 | 48.082 | 449.7441 | 18.1993 | 48.5542 | 761.3666 | 728.0324 | 618.1737 | 880.0138 | 897.9827 | 724.1235 |  | 817.5866 | 903.0776 | 1009.4992 | 590.7191 | 686.3515 | 887.1112 |  | 1033.9664 |  |  | 438.5487 | 628.5429 | 720.816 | [6 empty] | 606.2246 |  |  | 422.1158 |  |  | 494.0678 | 664.0352 | 668.8241 | 937.1644 | 1067.8672 | 1065.1438 | 521.0187 | 719.5242 | 821.0372 | 614.001 | 693.0228 | 1046.872 | 1102.2152 | 628.4168 | 801.3139 | 1143.0556 | 1177.1091 | 1056.8522 | 525.048 | 641.3453 | 678.1095 | 557.2704 | 730.5387 | 853.1375 | 1185.9151 | 1130.8985 | 584.1741 | 686.226 | 655.3313 | 829.2009 | 74.764 | 0.00032376 | 18.2758 | 5.3827 | -40.0421 | 3.1222 | 10766 | 0.25 | 0.92044 | -2.3634 | -2.2377 | -1.7052 | 6.3482 | 6.4236 | 6.8605 | 82.8494 | 156.423 | 50.7144 | 109.4024 | 34.1347 | 92.4717 | 33.1684
42810.4521 | 1046 | 17.5696 | 17.9951 | 18.1283 | 18.1712 | 17.5089 | 16.1518 | 14.8073 | 16.4549 | 16.9616 | 17.0954 | 17.1098 | 16.6415 | 15.6715 | 14.3976 | 18.6443 | 32.587 | 32.6379 | 86.0944 | 34.181 | 90.9453 |  |  |  | 25.112 | 85.8475 | 347.416 | 672.9443 | 712.3676 | 683.5047 | 87.327 | 117.3582 | 845.1489 | 93.0417 | 116.6832 | 823.9678 | 789.9165 | 852.4575 |  | 242.7465 | 837.1148 | 844.0716 | 462.9924 |  | 450.9556 | 711.6979 | 551.2377 | 696.812 | 850.6793 | 1017.2313 | 1060.924 | 58.0242 | 422.0748 | 90.3627 | 641.2655 | 13.9267 | 52.3735 | 48.1363 | 50.3186 | 62.5468 |  |  | 0.20458 | -0.40075 | -0.48442 | -0.11631 | 7.9638 | 7.5202 | 6.8838 | -3.68 | 21.8777 | 53.7546 | 15.9877 | 0.000138 | 0.00017085 | -0.00081154 | 22.0521 | 16.3161 | 16.7886 | 17.1873 | 17.1808 | 16.167 | 14.6238 | 16.6662 | 17.0509 | 17.3748 | 17.448 | 17.1756 | 16.3579 | 14.6343 | 787.9314 | 548.4628 | 508.3437 | 330.3186 | 259.8328 | 873.1376 | 556.1798 | 16.9563 | 28.3951 | 33.8392 | 69.6131 | 81.4803 | 85.6436 |  |  |  | 598.255 | 549.6924 | 557.4746 | 583.5139 | 85.9993 | 35.1878 | 896.9815 |  |  | 603.0516 |  |  | 18.9272 | 48.1896 | 452.671 | 18.2289 | 48.6898 | 759.2135 | 726.1843 | 618.2529 | 882.4285 | 900.5501 | 722.7961 |  | 815.0584 | 900.3635 | 1010.45 | 590.4893 | 686.0326 | 884.8224 |  | 1033.8389 |  |  | 438.3001 | 630.9227 | 718.6288 | [6 empty] | 605.9498 |  |  | 421.2296 |  |  | 494.9173 | 663.1173 | 668.7895 | 939.3111 | 1065.0847 | 1063.7825 | 520.0201 | 717.3117 | 820.014 | 613.529 | 692.1637 | 1050.4967 | 1107.4211 | 626.8736 | 798.9476 | 1139.1986 | 1178.1592 | 1058.6593 | 525.1611 | 642.2286 | 678.3582 | 555.0852 | 729.5402 | 852.7438 | 1180.4369 | 1131.5594 | 583.8952 | 686.5276 | 654.0059 | 829.2177 | 86.8349 | 0.00028867 | 18.2771 | 5.3876 | -40.046 | 3.1222 | 10830.84 | 0.32 | 0.97494 | -1.3845 | -1.5222 | -0.74586 | 7.0646 | 6.865 | 6.5681 | 82.0746 | 156.9804 | 50.6481 | 107.3617 | 32.1372 | 81.4956 | 33.1031
42810.4522 | 1047 | 17.5763 | 17.9985 | 18.1359 | 18.1721 | 17.5121 | 16.1529 | 14.8192 | 16.4658 | 16.9662 | 17.1039 | 17.1129 | 16.6455 | 15.6802 | 14.4046 | 18.7349 | 32.7611 | 32.788 | 86.1343 | 34.2496 | 90.9749 |  |  |  | 25.2336 | 86.0828 | 348.6418 | 672.7363 | 711.1104 | 682.8363 | 92.824 | 117.4563 | 837.9943 | 90.2802 | 115.7914 | 817.4022 | 762.078 | 846.1145 |  | 256.7503 | 830.5754 | 836.751 | 469.0871 |  | 451.3167 | 709.956 | 549.5794 | 694.4773 | 855.3825 | 1018.8647 | 1061.8019 | 58.3581 | 421.8725 | 93.7123 | 640.8635 | 13.9107 | 52.2471 | 48.1141 | 50.3123 | 62.7085 |  |  | 0.29921 | -0.062997 | -0.81034 | -1.029 | 7.6503 | 6.4478 | 6.5717 | -4.7097 | 20.3573 | 54.4064 | 16.2345 | 0.00014621 | 8.378e-05 | -0.00078361 | 22.0986 | 16.3017 | 16.7823 | 17.1716 | 17.1692 | 16.15 | 14.6186 | 16.6689 | 17.0381 | 17.3654 | 17.4378 | 17.1693 | 16.3651 | 14.611 | 778.51 | 538.1483 | 478.9745 | 325.7224 | 258.383 | 868.305 | 553.9285 | 16.9932 | 28.5196 | 33.9833 | 69.8794 | 81.5424 | 85.6899 |  |  |  | 598.4941 | 551.0767 | 558.595 | 584.1184 | 96.4632 | 29.6221 | 898.4697 |  |  | 607.2165 |  |  | 18.9436 | 48.2965 | 454.3927 | 18.2563 | 48.8265 | 754.8606 | 727.0214 | 619.228 | 887.2883 | 907.57 | 724.3398 |  | 813.542 | 901.2471 | 1011.4773 | 591.4132 | 685.6851 | 883.3742 |  | 1034.7122 |  |  | 438.8614 | 634.4414 | 718.5372 | [6 empty] | 606.6679 |  |  | 421.2076 |  |  | 495.3873 | 661.6328 | 668.1201 | 937.8706 | 1066.2992 | 1068.0498 | 519.5664 | 715.8845 | 819.7669 | 612.7476 | 690.3088 | 1054.31 | 1107.6437 | 626.034 | 798.9243 | 1143.1377 | 1174.5112 | 1058.7115 | 524.3329 | 642.7291 | 678.453 | 553.0638 | 728.3845 | 851.3345 | 1182.9181 | 1127.9895 | 583.085 | 686.9155 | 652.7385 | 827.3363 | 91.0281 | -0.0018089 | 18.277 | 5.4047 | -40.0378 | 3.1222 | 10776.93 | 0.28 | 1.1786 | -0.54844 | -1.967 | -2.2166 | 6.9285 | 6.3607 | 6.4216 | 81.5473 | 157.4777 | 50.5433 | 106.2311 | 34.8602 | 73.2606 | 33.1289
42810.4522 | 1048 | 17.5704 | 17.99 | 18.1308 | 18.1716 | 17.5046 | 16.146 | 14.8221 | 16.4618 | 16.9587 | 17.0959 | 17.1081 | 16.6383 | 15.6717 | 14.394 | 18.8427 | 32.9402 | 32.9591 | 86.1797 | 34.3763 | 90.9944 |  |  |  | 25.374 | 86.3031 | 348.3953 | 671.5803 | 708.9687 | 681.5358 | 93.1721 | 117.6679 | 833.3718 | 88.3462 | 109.9191 | 810.2026 | 828.2561 | 839.1952 |  | 264.82 | 825.3011 | 830.8521 | 488.6291 |  | 452.6739 | 708.9747 | 550.393 | 691.0238 | 858.1727 | 1017.9018 | 1060.828 | 59.3781 | 421.7508 | 95.921 | 640.449 | 13.9382 | 52.127 | 48.113 | 50.3145 | 62.8647 |  |  | 0.5292 | -0.16419 | 0.09976 | -1.2682 | 7.6779 | 6.6259 | 7.3379 | -2.9256 | 20.9907 | 54.1928 | 16.2345 | 0.00011992 | 9.528e-05 | -0.00080004 | 22.1532 | 16.3121 | 16.7839 | 17.1809 | 17.1744 | 16.1602 | 14.6181 | 16.6756 | 17.0336 | 17.3696 | 17.4434 | 17.1769 | 16.3626 | 14.6214 | 774.4876 | 535.5616 | 461.1284 | 309.9792 | 256.8098 | 864.4634 | 551.3994 | 17.0304 | 28.6187 | 34.102 | 70.1406 | 81.6015 | 85.7213 |  |  |  | 598.6482 | 551.195 | 558.5763 | 585.1524 | 95.6716 | 32.4162 | 902.3745 |  |  | 609.1435 |  |  | 18.9592 | 48.3992 | 453.5367 | 18.278 | 48.972 | 750.7922 | 729.7703 | 620.5743 | 893.9356 | 915.7956 | 729.0194 |  | 812.9755 | 909.2436 | 1012.7796 | 593.6447 | 685.4646 | 887.7084 |  | 1035.5628 |  |  | 439.3012 | 639.8732 | 721.9914 | [6 empty] | 608.3656 |  |  | 422.3431 |  |  | 495.8796 | 660.3288 | 667.609 | 934.5748 | 1068.4439 | 1067.478 | 519.181 | 715.6389 | 819.4361 | 612.5144 | 689.3166 | 1053.436 | 1105.0518 | 625.9594 | 799.0478 | 1151.0266 | 1173.7437 | 1055.3321 | 523.3199 | 642.8318 | 678.9109 | 550.8561 | 727.2111 | 849.095 | 1182.5751 | 1122.976 | 582.3616 | 688.2318 | 651.5553 | 825.1249 | 87.8402 | 0.0022951 | 18.2773 | 5.425 | -39.9649 | 3.1222 | 10700.52 | 0.28 | 1.5664 | -0.88496 | 0.68981 | -2.4595 | 6.9384 | 6.4456 | 6.7831 | 81.2368 | 157.9189 | 50.4311 | 104.9619 | 36.2391 | 92.8738 | 33.1276
42810.4522 | 1049 | 17.5554 | 17.9835 | 18.1245 | 18.1636 | 17.4999 | 16.1403 | 14.8228 | 16.4554 | 16.9563 | 17.0876 | 17.1107 | 16.6327 | 15.6702 | 14.3887 | 18.9417 | 33.1162 | 33.1166 | 86.2153 | 34.5465 | 91.0223 |  |  |  | 25.4972 | 86.5037 | 349.1958 | 670.7023 | 707.6738 | 680.6439 | 87.531 | 120.3878 | 835.1726 | 92.4172 | 113.9559 | 809.1356 | 877.9804 | 834.0059 |  | 255.2072 | 827.2897 | 832.5087 | 478.0039 |  | 452.2151 | 709.41 | 553.6487 | 692.8414 | 861.3938 | 1019.4823 | 1059.8215 | 57.6114 | 421.5544 | 95.4807 | 640.1846 | 13.9528 | 52.0059 | 48.1057 | 50.2994 | 62.7809 |  |  | 0.22889 | -0.18653 | -0.55144 | -0.80891 | 7.8895 | 5.7638 | 6.3444 | -4.4495 | 21.5572 | 55.7512 | 16.8681 | 0.0001265 | 0.00016264 | -0.00081154 | 22.2114 | 16.3107 | 16.7881 | 17.1871 | 17.1715 | 16.1616 | 14.6207 | 16.6723 | 17.0418 | 17.3727 | 17.4477 | 17.1796 | 16.3658 | 14.6257 | 776.4476 | 537.4951 | 460.5033 | 303.9346 | 258.0574 | 860.8888 | 549.1877 | 17.0497 | 28.7198 | 34.2144 | 70.3935 | 81.6553 | 85.7467 |  |  |  | 599.0862 | 552.5 | 559.5909 | 588.9533 | 81.4602 | 28.6294 | 908.2347 |  |  | 618.4588 |  |  | 18.9865 | 48.5049 | 453.114 | 18.3078 | 49.1198 | 750.0783 | 731.0431 | 621.2692 | 896.2209 | 918.3233 | 732.7128 |  | 812.594 | 911.8289 | 1015.6778 | 595.2669 | 685.2144 | 888.2173 |  | 1035.458 |  |  | 439.384 | 643.3137 | 724.8186 | [6 empty] | 609.0066 |  |  | 423.4106 |  |  | 496.501 | 659.38 | 667.0783 | 935.7747 | 1069.7259 | 1067.5058 | 519.1004 | 715.2638 | 818.3134 | 612.5007 | 688.8209 | 1053.9886 | 1107.9669 | 625.3416 | 797.4543 | 1149.6104 | 1173.1008 | 1052.0277 | 522.5824 | 643.3838 | 679.1332 | 549.1632 | 725.7693 | 847.2553 | 1177.1634 | 1122.648 | 581.4287 | 689.1895 | 650.0548 | 824.0952 | 79.7724 | 0.0041892 | 18.2775 | 5.434 | -39.9263 | 3.1222 | 10557.46 | 0.25 | 1.0297 | -0.94346 | -1.6222 | -1.9647 | 7.0377 | 6.0153 | 6.311 | 81.0129 | 159.3301 | 50.3291 | 103.159 | 35.7827 | 110.6696 | 33.1
42810.4522 | 1050 | 17.5623 | 17.9953 | 18.1341 | 18.1695 | 17.5087 | 16.1405 | 14.8249 | 16.4741 | 16.9702 | 17.1042 | 17.1119 | 16.6495 | 15.6683 | 14.3944 | 19.0412 | 33.2998 | 33.2712 | 86.253 | 34.6937 | 91.0695 |  |  |  | 25.6297 | 86.7036 | 350.6342 | 670.0183 | 707.525 | 679.7403 | 90.7409 | 118.5369 | 838.5674 | 95.1355 | 118.1628 | 815.7421 | 754.5926 | 840.8631 |  | 256.393 | 829.484 | 833.9574 | 478.0785 |  | 453.0898 | 710.7388 | 555.0828 | 698.8618 | 873.7215 | 1021.2516 | 1060.1046 | 55.8461 | 421.5026 | 97.3179 | 639.9846 | 13.9184 | 51.9278 | 48.1158 | 50.2748 | 62.5779 |  |  | 1.0884 | 0.66443 | -0.57838 | -1.0172 | 7.2252 | 5.47 | 6.7748 | -3.3501 | 20.3355 | 54.0395 | 17.34 | 0.00011828 | 0.00022342 | -0.00082304 | 22.2696 | 16.3126 | 16.7857 | 17.1785 | 17.1696 | 16.158 | 14.6222 | 16.6648 | 17.0442 | 17.3746 | 17.4409 | 17.1776 | 16.3639 | 14.6243 | 763.7349 | 521.885 | 431.1181 | 294.3553 | 254.7068 | 856.0336 | 546.2654 | 17.0719 | 28.8244 | 34.3236 | 70.6271 | 81.7064 | 85.7707 |  |  |  | 599.5916 | 553.8816 | 560.5461 | 591.3916 | 90.5904 | 23.5205 | 909.2836 |  |  | 625.8842 |  |  | 19.0029 | 48.6044 | 454.3557 | 18.3316 | 49.2551 | 752.4324 | 730.4893 | 622.2185 | 892.0369 | 912.3176 | 732.8459 |  | 812.0264 | 909.8087 | 1018.8477 | 596.8681 | 685.4094 | 884.0061 |  | 1035.6591 |  |  | 438.7652 | 641.9095 | 725.3022 | [6 empty] | 610.5204 |  |  | 423.7572 |  |  | 496.7669 | 658.51 | 666.3713 | 946.7533 | 1077.0167 | 1067.7435 | 518.4853 | 713.6462 | 817.2328 | 612.0416 | 688.6687 | 1058.6116 | 1114.9683 | 624.3472 | 795.5127 | 1151.3271 | 1183.0139 | 1054.1884 | 522.6004 | 643.2067 | 679.0428 | 548.1727 | 724.3716 | 846.7544 | 1180.0783 | 1137.3917 | 581.4885 | 689.0392 | 648.7009 | 823.5253 | 76.4059 | 0.010103 | 18.2781 | 5.4391 | -40.0346 | 3.1222 | 10399.75 | 0.32 | 2.2443 | 1.7818 | -1.6624 | -2.2047 | 6.7395 | 5.864 | 6.526 | 80.8288 | 161.019 | 50.329 | 102.4364 | 38.3564 | 70.9397 | 33.1225
42810.4522 | 1051 | 17.554 | 17.9813 | 18.1241 | 18.157 | 17.4925 | 16.1299 | 14.8193 | 16.4555 | 16.9604 | 17.0891 | 17.1027 | 16.6354 | 15.6644 | 14.3943 | 19.153 | 33.4805 | 33.4323 | 86.2976 | 34.8227 | 91.1294 |  |  |  | 25.7804 | 86.8964 | 353.7659 | 670.4757 | 708.8388 | 680.5715 | 91.0338 | 118.222 | 837.1904 | 91.6252 | 118.6468 | 818.1607 | 753.7512 | 847.4933 |  | 256.5379 | 830.2632 | 830.7728 | 507.8773 |  | 455.0225 | 711.5843 | 555.0193 | 700.1715 | 876.5248 | 1019.1484 | 1058.3253 | 53.1704 | 421.2827 | 96.5747 | 639.7675 | 13.8692 | 51.8579 | 48.1146 | 50.2382 | 62.2389 |  |  | 0.80913 | 0.34441 | -0.14009 | -0.97319 | 7.2252 | 5.7592 | 6.7183 | -3.4894 | 20.2016 | 54.8577 | 16.8242 | 0.00011007 | 0.00015771 | -0.00077704 | 22.3219 | 16.3143 | 16.7877 | 17.1833 | 17.1752 | 16.1558 | 14.6248 | 16.6689 | 17.0468 | 17.3776 | 17.4394 | 17.1747 | 16.3656 | 14.6219 | 764.6853 | 526.0146 | 431.4848 | 284.0287 | 243.0797 | 851.6909 | 543.2823 | 17.1111 | 28.9457 | 34.4573 | 70.8905 | 81.7672 | 85.8045 |  |  |  | 600.1175 | 555.5488 | 561.8427 | 592.7572 | 88.2741 | 36.3034 | 903.9086 |  |  | 626.4352 |  |  | 19.0162 | 48.7074 | 456.7756 | 18.3489 | 49.3821 | 753.3534 | 728.9861 | 621.8418 | 892.4769 | 914.7616 | 729.8188 |  | 811.2697 | 905.3799 | 1021.4202 | 596.9386 | 685.6574 | 881.5295 |  | 1036.503 |  |  | 437.9562 | 636.9078 | 723.4356 | [6 empty] | 610.7369 |  |  | 421.9632 |  |  | 497.2924 | 657.6716 | 665.8839 | 954.5684 | 1086.3377 | 1071.2118 | 517.4899 | 711.028 | 816.3177 | 611.4639 | 689.0259 | 1062.3302 | 1123.5932 | 623.5511 | 791.7247 | 1150.7395 | 1188.963 | 1062.9647 | 522.4557 | 642.9497 | 678.6149 | 546.8044 | 723.8882 | 847.8301 | 1177.1587 | 1142.9055 | 582.1235 | 687.9534 | 647.3706 | 826.1257 | 77.9984 | -0.0042993 | 18.2777 | 5.449 | -40.0715 | 3.1221 | 10214.48 | 0.14 | 1.9359 | 1.2834 | -0.81852 | -2.1574 | 6.734 | 6.0121 | 6.4935 | 80.6727 | 162.4755 | 50.3835 | 100.4384 | 37.614 | 69.8817 | 33.1785
42810.4522 | 1052 | 17.5617 | 17.9919 | 18.1256 | 18.1634 | 17.4967 | 16.1398 | 14.8307 | 16.4617 | 16.9658 | 17.0968 | 17.1094 | 16.6404 | 15.6759 | 14.3961 | 19.2505 | 33.6687 | 33.5943 | 86.3489 | 34.8959 | 91.1519 |  |  |  | 25.904 | 87.0558 | 357.105 | 671.6663 | 710.0936 | 682.2347 | 88.7899 | 117.9509 | 837.7987 | 90.5185 | 114.2305 | 815.6051 | 628.8769 | 847.801 |  | 237.9118 | 833.3313 | 836.4659 | 483.2229 |  | 452.8941 | 709.3153 | 555.0515 | 700.6828 | 872.8394 | 1017.1801 | 1056.6415 | 52.8419 | 421.1594 | 93.618 | 639.4841 | 13.8935 | 51.7868 | 48.1156 | 50.2272 | 61.8206 |  |  | 0.45231 | 0.057915 | -0.61321 | -0.46261 | 8.0801 | 5.8735 | 8.2828 | -3.0045 | 21.6541 | 53.9163 | 17.2471 | 0.00016099 | 0.00013964 | -0.00079511 | 22.3812 | 16.3218 | 16.7976 | 17.1816 | 17.178 | 16.1587 | 14.6247 | 16.6724 | 17.0457 | 17.3797 | 17.4473 | 17.1789 | 16.3677 | 14.6237 | 763.1148 | 530.4241 | 463.7915 | 281.8645 | 240.767 | 847.6751 | 540.8382 | 17.1444 | 29.0681 | 34.585 | 71.1501 | 81.8144 | 85.8424 |  |  |  | 600.2567 | 554.97 | 561.3896 | 588.8338 | 80.6632 | 29.4657 | 902.9395 |  |  | 637.15 |  |  | 19.045 | 48.8191 | 460.0549 | 18.3755 | 49.5199 | 752.8257 | 726.856 | 620.393 | 902.0422 | 926.8283 | 726.151 |  | 810.2778 | 906.2811 | 1023.3947 | 595.505 | 685.6769 | 880.8243 |  | 1037.8509 |  |  | 437.5076 | 631.0551 | 720.448 | [6 empty] | 608.2609 |  |  | 419.2036 |  |  | 497.4628 | 657.6464 | 665.2446 | 964.7936 | 1090.6841 | 1077.3996 | 516.6538 | 708.4979 | 815.2854 | 612.1618 | 689.5386 | 1066.402 | 1124.9576 | 622.446 | 789.3838 | 1149.3739 | 1189.7587 | 1063.7812 | 523.2302 | 642.7499 | 678.4221 | 545.128 | 723.5063 | 847.8715 | 1182.7438 | 1147.7484 | 582.1131 | 688.0293 | 646.2543 | 826.6067 | 79.7025 | -0.00032867 | 18.2767 | 5.4503 | -39.968 | 3.1221 | 10028.16 | 0.31 | 1.4487 | 0.52568 | -1.7105 | -1.4857 | 7.1158 | 6.0669 | 7.2046 | 80.4606 | 163.4792 | 50.4278 | 98.8773 | 33.4525 | 41.5831 | 33.3124
42810.4522 | 1053 | 17.5514 | 17.9902 | 18.1263 | 18.1643 | 17.5015 | 16.1384 | 14.8379 | 16.4605 | 16.9592 | 17.0969 | 17.1152 | 16.641 | 15.6722 | 14.3958 | 19.3512 | 33.8322 | 33.7447 | 86.3968 | 34.9685 | 91.1913 |  |  |  | 26.0384 | 87.2357 | 359.6442 | 672.46 | 710.3752 | 683.4988 | 86.374 | 116.3446 | 837.9688 | 89.9276 | 113.8094 | 814.7172 | 845.5123 | 845.8862 |  | 246.2937 | 836.0811 | 839.5764 | 471.5703 |  | 452.7395 | 708.9845 | 555.0137 | 702.1146 | 871.8221 | 1018.213 | 1056.8778 | 54.4719 | 420.9788 | 88.9221 | 639.4491 | 13.9358 | 51.6962 | 48.1314 | 50.2172 | 61.3715 |  |  | 0.10536 | -0.16091 | -0.13746 | -0.95676 | 7.8166 | 5.1362 | 6.119 | -3.8147 | 21.5156 | 55.1084 | 17.077 | 0.00016099 | 5.914e-05 | -0.00081811 | 22.424 | 16.3152 | 16.7796 | 17.1724 | 17.1696 | 16.1555 | 14.6112 | 16.6695 | 17.037 | 17.3689 | 17.4408 | 17.1659 | 16.3644 | 14.6189 | 757.6258 | 528.9162 | 448.8552 | 270.6145 | 229.1856 | 843.52 | 538.0822 | 17.1669 | 29.1684 | 34.699 | 71.3884 | 81.8587 | 85.8604 |  |  |  | 600.1369 | 553.3201 | 559.3519 | 585.9127 | 91.7138 | 35.4409 | 909.9232 |  |  | 642.1904 |  |  | 19.0656 | 48.9171 | 463.1235 | 18.4117 | 49.6459 | 753.98 | 724.5747 | 619.8392 | 909.6309 | 935.6107 | 722.719 |  | 809.0963 | 908.2412 | 1024.8939 | 595.0586 | 685.5842 | 891.5568 |  | 1039.1878 |  |  | 437.3021 | 625.7567 | 717.2183 | [6 empty] | 607.6662 |  |  | 417.5014 |  |  | 498.6177 | 658.9183 | 664.7769 | 964.6349 | 1094.3436 | 1077.3945 | 516.5356 | 706.6157 | 815.9775 | 613.1136 | 689.4905 | 1064.6007 | 1128.198 | 621.0106 | 789.7328 | 1149.8853 | 1194.5209 | 1069.5916 | 523.6453 | 642.5376 | 678.5933 | 543.2065 | 722.484 | 847.9295 | 1181.446 | 1154.4207 | 581.9625 | 688.1616 | 644.575 | 824.9641 | 82.0412 | 0.00074465 | 18.2754 | 5.4498 | -40.0761 | 3.1221 | 9891.05 | 0.22 | 0.69965 | -0.87607 | -0.80973 | -2.1363 | 7.0016 | 5.6756 | 6.1948 | 80.1829 | 164.2087 | 50.4191 | 97.706 | 34.4705 | 99.1803 | 33.3721
42810.4522 | 1054 | 17.5591 | 17.9857 | 18.1257 | 18.1686 | 17.5005 | 16.145 | 14.8411 | 16.465 | 16.9666 | 17.0967 | 17.1136 | 16.6484 | 15.6746 | 14.3996 | 19.458 | 34.0166 | 33.9067 | 86.4426 | 35.0389 | 91.2213 |  |  |  | 26.1735 | 87.3981 | 360.9444 | 672.4417 | 709.565 | 683.4444 | 87.9091 | 117.3527 | 839.8485 | 88.8697 | 114.7499 | 813.7393 | 874.4135 | 846.1443 |  | 250.7385 | 840.8744 | 844.2499 | 469.0947 |  | 451.7765 | 711.1207 | 556.0608 | 704.1505 | 876.236 | 1021.9651 | 1062.9595 | 55.8607 | 420.7566 | 84.8397 | 639.315 | 13.8984 | 51.5953 | 48.1504 | 50.2252 | 61.084 |  |  | 0.1875 | -0.17208 | 0.37312 | -1.2748 | 7.8389 | 5.2499 | 7.2492 | -3.4067 | 20.6714 | 53.7525 | 17.3754 | 0.0001035 | 0.00016099 | -0.00083782 | 22.4941 | 16.312 | 16.7822 | 17.1695 | 17.1709 | 16.1539 | 14.6132 | 16.6631 | 17.0394 | 17.3746 | 17.441 | 17.1779 | 16.3604 | 14.6188 | 761.0068 | 525.1031 | 470.5932 | 282.494 | 238.3253 | 839.9445 | 535.8645 | 17.1897 | 29.2702 | 34.8236 | 71.5892 | 81.9141 | 85.9024 |  |  |  | 600.1586 | 552.3355 | 557.7139 | 585.9777 | 79.5919 | 28.617 | 916.8322 |  |  | 645.9447 |  |  | 19.0784 | 49.0152 | 464.7439 | 18.4359 | 49.7778 | 756.4183 | 722.8791 | 620.2247 | 912.4122 | 938.663 | 720.0619 |  | 808.2458 | 909.9449 | 1027.9906 | 595.6914 | 685.5137 | 891.7946 |  | 1040.1142 |  |  | 436.8623 | 620.9479 | 714.7711 | [6 empty] | 607.8766 |  |  | 418.0611 |  |  | 499.2653 | 660.1574 | 664.7869 | 972.3085 | 1091.1321 | 1076.6515 | 516.3702 | 705.3571 | 816.1385 | 613.7909 | 689.7471 | 1067.2727 | 1133.6651 | 620.6048 | 791.142 | 1150.0733 | 1193.9781 | 1072.5802 | 523.5134 | 642.6122 | 678.741 | 541.5173 | 721.018 | 846.3272 | 1183.9599 | 1155.1808 | 582.4898 | 688.1914 | 643.3586 | 823.5108 | 89.4708 | 0.00033778 | 18.2766 | 5.4495 | -40.0065 | 3.1221 | 9813.97 | 0.25 | 0.93332 | -0.90695 | 1.3355 | -2.4686 | 7.0218 | 5.7464 | 6.7525 | 79.9888 | 165.789 | 50.3854 | 95.8093 | 31.5413 | 109.5897 | 33.3742
42810.4522 | 1055 | 17.5547 | 17.9824 | 18.1201 | 18.1644 | 17.506 | 16.1383 | 14.8387 | 16.4644 | 16.9661 | 17.0984 | 17.1114 | 16.6489 | 15.6824 | 14.4055 | 19.579 | 34.2069 | 34.0749 | 86.5085 | 35.1355 | 91.2589 |  |  |  | 26.3232 | 87.5548 | 361.7348 | 672.0903 | 708.7959 | 683.1134 | 93.7087 | 121.0342 | 842.7982 | 90.5694 | 116.3302 | 814.2073 | 889.3386 | 845.0133 |  | 261.462 | 837.5763 | 840.2383 | 481.5297 |  | 452.3428 | 712.8976 | 558.0485 | 705.6095 | 878.6252 | 1021.3338 | 1064.2081 | 55.8816 | 420.4601 | 84.2677 | 638.9578 | 13.8874 | 51.4901 | 48.1565 | 50.2257 | 60.8941 |  |  | 0.24467 | -0.2759 | -0.07766 | -0.87462 | 7.9033 | 5.0475 | 6.4258 | -3.5814 | 20.6477 | 53.5479 | 17.5926 | 6.571e-05 | 0.00015607 | -0.00084111 | 22.5506 | 16.3151 | 16.7782 | 17.1666 | 17.1721 | 16.1648 | 14.6238 | 16.6675 | 17.0455 | 17.3719 | 17.4396 | 17.1811 | 16.3707 | 14.6321 | 756.3241 | 506.767 | 451.3107 | 276.8833 | 244.3346 | 836.0845 | 533.1681 | 17.2264 | 29.3822 | 34.9458 | 71.7897 | 81.9602 | 85.9386 |  |  |  | 600.2195 | 551.2715 | 556.4165 | 586.141 | 86.1916 | 35.8736 | 922.1815 |  |  | 663.8171 |  |  | 19.1029 | 49.1246 | 465.3684 | 18.4547 | 49.9275 | 755.1758 | 722.582 | 621.7591 | 913.6664 | 937.5031 | 719.4006 |  | 807.857 | 911.9976 | 1031.6447 | 597.8134 | 685.668 | 887.7893 |  | 1041.7022 |  |  | 436.542 | 616.8225 | 713.2096 | [6 empty] | 609.9507 |  |  | 420.0296 |  |  | 499.0679 | 660.5887 | 665.297 | 968.394 | 1088.5616 | 1080.0489 | 515.7242 | 705.4352 | 817.642 | 613.936 | 690.8151 | 1063.1167 | 1133.7319 | 620.373 | 793.8386 | 1154.5608 | 1196.2558 | 1076.1354 | 524.1689 | 643.0177 | 679.0516 | 539.7324 | 719.7673 | 846.3487 | 1185.5889 | 1157.3081 | 583.2737 | 688.4911 | 642.516 | 823.3769 | 79.9604 | -0.00061633 | 18.2773 | 5.4505 | -40.063 | 3.1221 | 9755.63 | 0.29 | 1.066 | -1.1495 | -0.60984 | -2.0466 | 7.0489 | 5.6332 | 6.3559 | 79.885 | 167.6668 | 50.3616 | 94.6996 | 33.062 | 114.8751 | 33.3805
42810.4523 | 1056 | 17.5399 | 17.9702 | 18.1046 | 18.1477 | 17.4911 | 16.136 | 14.8332 | 16.4593 | 16.9516 | 17.0963 | 17.1073 | 16.6343 | 15.671 | 14.3977 | 19.6683 | 34.3691 | 34.2192 | 86.551 | 35.2558 | 91.2707 |  |  |  | 26.454 | 87.6767 | 363.406 | 672.2884 | 708.6483 | 683.5873 | 92.5145 | 121.363 | 840.692 | 92.6857 | 115.6375 | 813.7944 | 882.8391 | 841.9197 |  | 279.5005 | 828.461 | 835.6046 | 485.7624 |  | 453.5342 | 715.4429 | 559.9722 | 705.8662 | 869.0293 | 1017.5764 | 1063.6705 | 55.3328 | 420.1103 | 87.1527 | 638.4112 | 13.9352 | 51.4132 | 48.1637 | 50.2332 | 60.8097 |  |  | 0.55088 | -0.40207 | -0.35891 | -0.62755 | 8.3101 | 5.1204 | 7.0021 | -3.473 | 20.6638 | 54.1326 | 19.7584 | 0.00016099 | 8.378e-05 | -0.00080661 | 22.6071 | 16.3197 | 16.7819 | 17.175 | 17.1725 | 16.1588 | 14.6222 | 16.6735 | 17.0445 | 17.3806 | 17.4432 | 17.1846 | 16.3667 | 14.6337 | 748.0366 | 512.7871 | 461.371 | 276.8899 | 255.3226 | 832.1777 | 531.0079 | 17.263 | 29.5014 | 35.0796 | 72.0244 | 82.0138 | 85.9568 |  |  |  | 600.2605 | 549.99 | 554.823 | 584.7 | 75.5986 | 31.0986 | 923.67 |  |  | 680.9942 |  |  | 19.1197 | 49.2226 | 466.583 | 18.4896 | 50.0606 | 751.4782 | 722.6783 | 623.6728 | 913.5462 | 939.9193 | 720.7016 |  | 807.4898 | 912.6022 | 1033.8764 | 600.0332 | 686.1017 | 890.0269 |  | 1043.0978 |  |  | 436.6818 | 616.2471 | 713.3715 | [6 empty] | 611.9779 |  |  | 420.7388 |  |  | 499.163 | 660.927 | 665.8339 | 964.5172 | 1083.3456 | 1082.9162 | 514.5569 | 704.9562 | 818.8259 | 614.3128 | 692.0537 | 1059.1506 | 1128.4031 | 619.4284 | 792.673 | 1150.794 | 1197.5488 | 1081.1172 | 524.6037 | 643.3347 | 679.451 | 538.5304 | 718.8078 | 846.4788 | 1182.7618 | 1160.1063 | 583.6533 | 689.658 | 641.682 | 822.7942 | 88.7695 | -0.000476 | 18.2775 | 5.4485 | -40.0888 | 3.1221 | 9743.04 | 0.22 | 1.5999 | -1.3894 | -1.3127 | -1.7358 | 7.2175 | 5.6655 | 6.6252 | 79.7335 | 168.8392 | 50.3988 | 93.9835 | 31.4484 | 112.2806 | 33.4279
42810.4523 | 1057 | 17.5493 | 17.9809 | 18.1191 | 18.1546 | 17.5022 | 16.145 | 14.8505 | 16.4722 | 16.9593 | 17.1011 | 17.124 | 16.6454 | 15.6787 | 14.4016 | 19.7782 | 34.5501 | 34.376 | 86.6093 | 35.3922 | 91.2934 |  |  |  | 26.5896 | 87.729 | 365.3259 | 672.6308 | 708.6535 | 684.0608 | 89.0714 | 119.7974 | 837.4407 | 94.5498 | 119.3126 | 818.4069 | 788.5455 | 843.8211 |  | 278.8919 | 827.5415 | 829.0599 | 493.3334 |  | 455.4949 | 716.5165 | 560.3618 | 705.4101 | 869.8005 | 1017.275 | 1064.3077 | 54.8366 | 419.8962 | 90.2818 | 637.933 | 13.9531 | 51.3489 | 48.1555 | 50.2337 | 60.8059 |  |  | 0.21312 | -0.25093 | -0.22486 | -0.92325 | 7.6227 | 6.5766 | 7.2098 | -3.726 | 20.5183 | 52.942 | 19.1327 | 0.00016757 | 8.707e-05 | -0.00080332 | 22.6539 | 16.3152 | 16.7785 | 17.1675 | 17.158 | 16.1493 | 14.6186 | 16.663 | 17.0379 | 17.3737 | 17.4423 | 17.181 | 16.3628 | 14.6205 | 734.8659 | 512.2881 | 452.8076 | 271.8439 | 253.1582 | 827.9155 | 528.6836 | 17.2854 | 29.5975 | 35.1956 | 72.2195 | 82.0554 | 85.9847 |  |  |  | 600.4254 | 550.1914 | 554.2609 | 586.2245 | 67.8348 | 23.6688 | 922.0384 |  |  | 693.3996 |  |  | 19.1342 | 49.3179 | 468.6888 | 18.5156 | 50.1893 | 748.9947 | 723.6573 | 625.5067 | 917.0067 | 945.8624 | 722.3765 |  | 806.9913 | 913.4112 | 1034.3723 | 601.7318 | 686.4147 | 883.2062 |  | 1043.5065 |  |  | 437.4318 | 618.8586 | 713.4272 | [6 empty] | 613.9883 |  |  | 421.5723 |  |  | 499.8504 | 661.9868 | 666.6229 | 967.5875 | 1081.6698 | 1083.1811 | 513.8915 | 704.2164 | 818.1487 | 615.3284 | 693.4417 | 1062.2204 | 1122.8714 | 619.0178 | 792.639 | 1145.124 | 1199.1301 | 1082.5215 | 524.9147 | 643.4014 | 679.7518 | 537.7255 | 718.2362 | 845.725 | 1179.6245 | 1164.35 | 583.3355 | 690.2523 | 641.3202 | 822.467 | 83.8781 | -0.00037778 | 18.2777 | 5.4471 | -39.9853 | 3.1222 | 9767.18 | 0.3 | 0.99537 | -1.0982 | -1.0396 | -2.1065 | 6.9117 | 6.42 | 6.7219 | 79.5305 | 169.0817 | 50.423 | 93.6754 | 31.8686 | 80.2419 | 33.415
42810.4523 | 1058 | 17.546 | 17.9813 | 18.1256 | 18.1656 | 17.499 | 16.1475 | 14.8538 | 16.4693 | 16.9598 | 17.103 | 17.1173 | 16.6464 | 15.6742 | 14.3998 | 19.89 | 34.7361 | 34.5479 | 86.6748 | 35.4648 | 91.3141 |  |  |  | 26.7341 | 87.7734 | 366.6249 | 672.6536 | 708.3962 | 683.8083 | 91.5747 | 116.3394 | 832.4187 | 93.0455 | 119.8033 | 819.7761 | 680.7544 | 850.2795 |  | 270.2173 | 825.3316 | 828.1569 | 517.3437 |  | 457.0208 | 716.3109 | 559.7637 | 703.4059 | 873.7691 | 1020.3738 | 1065.9307 | 53.6188 | 419.6651 | 92.2685 | 637.3567 | 13.9641 | 51.322 | 48.1577 | 50.2379 | 60.8851 |  |  | 0.35309 | 0.018487 | -0.40819 | -1.0862 | 7.1746 | 5.9313 | 6.3404 | -3.9238 | 19.856 | 52.8354 | 17.8145 | 0.00013307 | 0.00012157 | -0.00080168 | 22.7038 | 16.3184 | 16.771 | 17.1613 | 17.1561 | 16.1452 | 14.613 | 16.6621 | 17.0354 | 17.367 | 17.4394 | 17.1798 | 16.3587 | 14.6233 | 703.8523 | 485.5512 | 404.8911 | 267.6555 | 240.3695 | 822.6498 | 525.862 | 17.3216 | 29.7097 | 35.3144 | 72.402 | 82.0995 | 86.0182 |  |  |  | 600.6432 | 550.2056 | 554.3113 | 587.2562 | 75.9592 | 23.9552 | 923.0372 |  |  | 705.4124 |  |  | 19.1589 | 49.4241 | 469.8481 | 18.5386 | 50.3234 | 748.4376 | 725.6694 | 626.4132 | 924.0444 | 956.5559 | 725.799 |  | 806.9158 | 907.6574 | 1034.4117 | 603.002 | 686.5666 | 875.8226 |  | 1044.2037 |  |  | 437.8622 | 623.9036 | 715.7927 | [6 empty] | 615.4204 |  |  | 422.5805 |  |  | 500.5406 | 662.9786 | 666.9404 | 974.782 | 1086.916 | 1082.526 | 513.5654 | 703.7309 | 818.3599 | 615.8621 | 693.9225 | 1064.4869 | 1120.4475 | 617.9621 | 794.3587 | 1138.923 | 1195.2402 | 1082.2964 | 524.8564 | 643.4546 | 679.9162 | 536.9493 | 718.3742 | 845.6844 | 1173.3665 | 1161.6892 | 583.1484 | 690.5073 | 641.2239 | 823.4528 | 84.3969 | 0.00021853 | 18.2776 | 5.4454 | -40.0371 | 3.1221 | 9808.05 | 0.35 | 1.281 | 0.29806 | -1.4005 | -2.2847 | 6.7135 | 6.1042 | 6.3112 | 79.4118 | 169.2627 | 50.4223 | 94.9535 | 36.551 | 51.4856 | 33.4254
42810.4523 | 1059 | 17.5407 | 17.9661 | 18.113 | 18.1537 | 17.4935 | 16.1322 | 14.8469 | 16.4594 | 16.955 | 17.0891 | 17.1045 | 16.6292 | 15.6703 | 14.3941 | 20.0034 | 34.9254 | 34.7169 | 86.7487 | 35.5807 | 91.3368 |  |  |  | 26.8877 | 87.8901 | 368.3217 | 672.975 | 708.6856 | 683.9672 | 91.0482 | 118.4068 | 833.7403 | 89.6611 | 117.0925 | 821.7638 | 735.259 | 853.5594 |  | 247.9864 | 834.1429 | 834.7785 | 512.9783 |  | 457.2501 | 715.0125 | 560.7866 | 703.9413 | 877.3857 | 1024.0052 | 1063.2038 | 53.2148 | 419.2607 | 93.5962 | 636.5302 | 13.9848 | 51.2565 | 48.1767 | 50.2733 | 61.0264 |  |  | 0.65076 | 0.10983 | -0.7144 | -0.61046 | 6.9906 | 6.2211 | 6.7551 | -3.316 | 20.1843 | 51.9717 | 17.8094 | 2.957e-05 | 0.00010185 | -0.00081646 | 22.7679 | 16.3168 | 16.7714 | 17.1611 | 17.1605 | 16.1524 | 14.6204 | 16.6645 | 17.0394 | 17.3682 | 17.4376 | 17.1776 | 16.3763 | 14.6315 | 692.9801 | 495.003 | 407.5592 | 263.9413 | 233.7623 | 818.6235 | 523.402 | 17.3532 | 29.8194 | 35.4392 | 72.6049 | 82.1514 | 86.054 |  |  |  | 600.6761 | 549.3225 | 553.8334 | 586.3332 | 87.6213 | 34.3439 | 926.8225 |  |  | 708.907 |  |  | 19.1791 | 49.5177 | 470.9508 | 18.5652 | 50.4465 | 751.1482 | 727.8474 | 626.3977 | 928.3989 | 965.9051 | 729.2776 |  | 806.7876 | 901.3646 | 1034.7398 | 603.1259 | 686.6882 | 866.8109 |  | 1044.8868 |  |  | 438.126 | 629.5592 | 718.2403 | [6 empty] | 615.5512 |  |  | 422.7634 |  |  | 501.1453 | 663.59 | 666.62 | 978.1134 | 1091.5726 | 1085.462 | 513.3466 | 703.0152 | 818.7935 | 616.2254 | 694.001 | 1063.4247 | 1120.6869 | 617.0046 | 793.8804 | 1136.2234 | 1189.6107 | 1080.0166 | 525.0589 | 644.1818 | 680.1096 | 535.7479 | 718.6925 | 846.1564 | 1167.3074 | 1157.6479 | 583.5024 | 691.1127 | 640.6098 | 824.371 | 90.0823 | -9.0163e-05 | 18.2748 | 5.4422 | -40.0654 | 3.1221 | 9813.5 | 0.21 | 1.7392 | 0.726 | -1.8516 | -1.7116 | 6.6362 | 6.2603 | 6.5234 | 79.275 | 169.613 | 50.4467 | 94.5192 | 35.6979 | 64.8058 | 33.4569
42810.4523 | 1060 | 17.5365 | 17.9676 | 18.1103 | 18.1519 | 17.492 | 16.134 | 14.8428 | 16.4565 | 16.9477 | 17.0891 | 17.104 | 16.6364 | 15.6635 | 14.3959 | 20.1072 | 35.0971 | 34.875 | 86.8089 | 35.7048 | 91.3478 |  |  |  | 27.0242 | 87.9947 | 370.4935 | 673.5207 | 709.0322 | 684.3047 | 85.2222 | 111.5257 | 833.7195 | 86.3887 | 118.7217 | 823.6146 | 885.4314 | 851.7675 |  | 253.7552 | 837.1305 | 839.2081 | 503.2212 |  | 456.42 | 712.7723 | 559.845 | 702.9072 | 877.5183 | 1024.3112 | 1061.4883 | 53.6348 | 418.836 | 93.7716 | 636.0016 | 13.977 | 51.1678 | 48.1973 | 50.3298 | 61.2304 |  |  | 0.78021 | 0.50541 | -0.77749 | -0.79643 | 8.1366 | 6.3033 | 6.5579 | -4.1052 | 21.0162 | 53.6952 | 18.1267 | 0.00015114 | 7.393e-05 | -0.00078361 | 22.8329 | 16.3263 | 16.7771 | 17.1636 | 17.1597 | 16.1549 | 14.6243 | 16.6723 | 17.0455 | 17.3724 | 17.4438 | 17.1802 | 16.3714 | 14.6275 | 713.245 | 497.5137 | 442.613 | 273.0635 | 239.4048 | 816.171 | 521.5771 | 17.3864 | 29.9321 | 35.5647 | 72.8005 | 82.2019 | 86.0804 |  |  |  | 600.8623 | 549.654 | 552.9803 | 587.8684 | 93.6017 | 36.4832 | 930.9049 |  |  | 714.0238 |  |  | 19.1975 | 49.6199 | 472.9374 | 18.5862 | 50.5803 | 754.4013 | 730.8914 | 626.3132 | 931.8116 | 966.6143 | 733.3074 |  | 807.0943 | 894.9846 | 1034.0992 | 602.8534 | 686.7129 | 861.1986 |  | 1046.7288 |  |  | 438.7003 | 635.2427 | 721.2838 | [6 empty] | 615.2107 |  |  | 422.1805 |  |  | 501.9763 | 663.9822 | 666.7701 | 975.6773 | 1092.9653 | 1086.9738 | 513.3558 | 702.33 | 818.4792 | 616.2406 | 694.3303 | 1060.2249 | 1125.0029 | 616.849 | 794.3773 | 1137.8301 | 1185.0978 | 1077.7593 | 525.6578 | 645.4258 | 680.9296 | 535.0655 | 718.4443 | 845.265 | 1166.895 | 1155.5365 | 584.155 | 692.0193 | 640.2416 | 823.9533 | 87.6155 | -0.00097408 | 18.2607 | 5.4402 | -40.0145 | 3.1221 | 9803.3 | 0.33 | 1.9047 | 1.5556 | -1.9295 | -1.9528 | 7.1604 | 6.3023 | 6.4283 | 79.2592 | 169.4476 | 50.4599 | 91.2736 | 31.3918 | 112.7789 | 33.4476
42810.4523 | 1061 | 17.5418 | 17.973 | 18.1177 | 18.1572 | 17.4969 | 16.1394 | 14.8521 | 16.4616 | 16.9572 | 17.0963 | 17.1119 | 16.6468 | 15.6723 | 14.4026 | 20.2225 | 35.2759 | 35.0336 | 86.8588 | 35.8139 | 91.3494 |  |  |  | 27.1617 | 88.0886 | 372.2884 | 673.2951 | 709.0072 | 683.5322 | 83.5274 | 111.6031 | 835.963 | 89.4436 | 114.7029 | 819.2891 | 841.2556 | 849.5274 |  | 249.382 | 838.5465 | 842.6223 | 476.8873 |  | 456.9641 | 711.3257 | 558.7941 | 700.3919 | 871.8248 | 1025.1253 | 1062.5313 | 54.3712 | 418.5683 | 93.7774 | 635.5014 | 13.969 | 51.0677 | 48.2014 | 50.3857 | 61.4768 |  |  | 0.47006 | 0.012575 | -1.0344 | -0.74188 | 7.8494 | 5.6652 | 5.7129 | -3.8318 | 21.3348 | 52.2308 | 19.8882 | 8.543e-05 | 0.00011828 | -0.00077375 | 22.8863 | 16.3257 | 16.7724 | 17.1674 | 17.1678 | 16.1513 | 14.6217 | 16.6721 | 17.0405 | 17.3778 | 17.4427 | 17.1837 | 16.3704 | 14.633 | 733.5824 | 514.653 | 479.7781 | 297.448 | 252.2259 | 814.5436 | 520.2447 | 17.4293 | 30.0607 | 35.6912 | 73.0114 | 82.2435 | 86.1231 |  |  |  | 601.3319 | 551.6293 | 554.2601 | 592.2499 | 92.9015 | 27.3707 | 933.9617 |  |  | 713.3967 |  |  | 19.2251 | 49.719 | 474.4776 | 18.6085 | 50.7204 | 755.7876 | 732.8289 | 625.8947 | 930.0695 | 954.9211 | 736.3485 |  | 807.4158 | 896.6206 | 1035.4714 | 602.7206 | 686.6614 | 870.9834 |  | 1047.8706 |  |  | 438.2576 | 637.6787 | 724.6733 | [6 empty] | 614.6282 |  |  | 421.9296 |  |  | 502.6834 | 663.8093 | 666.8274 | 973.6854 | 1088.5566 | 1088 | 513.3355 | 703.2142 | 818.4698 | 615.9567 | 693.9846 | 1058.1713 | 1124.5139 | 616.888 | 794.8411 | 1136.9159 | 1182.4299 | 1078.8745 | 525.8032 | 646.7156 | 681.4281 | 534.614 | 718.7766 | 844.8488 | 1166.417 | 1156.3253 | 584.7931 | 692.5964 | 640.3495 | 825.2729 | 82.4133 | -0.00074259 | 18.2447 | 5.4388 | -40.0017 | 3.122 | 9792.36 | 0.29 | 1.4778 | 0.2452 | -2.2239 | -1.8834 | 7.0351 | 5.9766 | 6.0017 | 79.2756 | 170.1366 | 50.4518 | 88.3571 | 26.963 | 97.5706 | 33.4101
42810.4523 | 1062 | 17.5419 | 17.9734 | 18.1165 | 18.1562 | 17.4931 | 16.1404 | 14.8595 | 16.465 | 16.9622 | 17.0971 | 17.1144 | 16.6474 | 15.6742 | 14.4087 | 20.3329 | 35.4534 | 35.1851 | 86.8947 | 35.9413 | 91.359 |  |  |  | 27.3006 | 88.1838 | 374.4257 | 673.5147 | 709.4187 | 683.6487 | 93.045 | 118.6355 | 840.05 | 90.8106 | 116.2452 | 818.3898 | 732.339 | 850.7047 |  | 236.9923 | 840.3443 | 843.3391 | 472.4327 |  | 454.8714 | 708.8166 | 557.7828 | 699.5694 | 868.3393 | 1023.4476 | 1061.4452 | 54.2225 | 418.3118 | 92.2707 | 634.9886 | 13.9727 | 50.9546 | 48.1816 | 50.4463 | 61.7364 |  |  | 0.062647 | 0.36282 | -0.34379 | -0.33907 | 7.5209 | 5.4983 | 7.2926 | -3.8673 | 20.2715 | 52.3594 | 20.8195 | 8.05e-05 | 0.00016592 | -0.00082468 | 22.948 | 16.3214 | 16.7787 | 17.1691 | 17.1595 | 16.1601 | 14.6252 | 16.6705 | 17.0457 | 17.379 | 17.4423 | 17.181 | 16.3741 | 14.6376 | 754.8151 | 515.5471 | 455.94 | 291.3827 | 246.544 | 812.7027 | 518.0835 | 17.4711 | 30.1801 | 35.8203 | 73.2147 | 82.2934 | 86.163 |  |  |  | 601.7742 | 552.7938 | 555.2878 | 593.4495 | 79.9843 | 28.7483 | 931.107 |  |  | 698.8588 |  |  | 19.2488 | 49.817 | 476.3062 | 18.6486 | 50.8396 | 756.6714 | 732.6752 | 624.8972 | 921.6422 | 940.7576 | 734.911 |  | 807.5281 | 914.9379 | 1037.5092 | 602.1428 | 686.4474 | 882.4549 |  | 1048.3118 |  |  | 436.6958 | 633.792 | 725.3267 | [6 empty] | 613.3887 |  |  | 422.6595 |  |  | 503.5979 | 663.3261 | 666.9577 | 975.086 | 1087.6056 | 1088.0908 | 513.0063 | 704.4647 | 817.9694 | 615.746 | 693.5163 | 1059.5033 | 1122.3701 | 617.0017 | 794.694 | 1133.9071 | 1178.8951 | 1082.6127 | 525.8254 | 647.8613 | 681.3033 | 533.4482 | 719.2385 | 846.9509 | 1159.1512 | 1158.792 | 585.4253 | 693.1313 | 639.9917 | 825.9828 | 86.0128 | -0.0010863 | 18.2324 | 5.4398 | -40.0867 | 3.1221 | 9671.43 | 0.32 | 0.53954 | 1.3154 | -1.2805 | -1.2716 | 6.8818 | 5.8841 | 6.7766 | 79.3508 | 170.7226 | 50.419 | 85.2575 | 29.1278 | 65.1748 | 33.4562
42810.4523 | 1063 | 17.5366 | 17.9658 | 18.1097 | 18.153 | 17.4898 | 16.1357 | 14.8562 | 16.4583 | 16.9557 | 17.0958 | 17.107 | 16.6417 | 15.6668 | 14.3981 | 20.4506 | 35.6375 | 35.3602 | 86.9359 | 36.0911 | 91.3795 |  |  |  | 27.4408 | 88.2953 | 376.5027 | 674.0658 | 709.691 | 683.8513 | 94.4473 | 123.0877 | 844.996 | 93.6413 | 118.1733 | 819.4495 | 815.2016 | 850.665 |  | 245.7468 | 840.2211 | 843.1438 | 479.3529 |  | 454.0134 | 707.6177 | 557.8981 | 702.4069 | 872.6723 | 1021.1966 | 1060.0316 | 52.4566 | 418.1395 | 91.8858 | 634.5915 | 13.9573 | 50.8513 | 48.1599 | 50.4904 | 61.9656 |  |  | 0.22561 | -0.24305 | -0.67892 | -0.6696 | 8.2443 | 4.8471 | 6.2681 | -4.0132 | 20.7765 | 53.6753 | 19.2251 | 4.764e-05 | 0.00015442 | -0.00084604 | 23.0097 | 16.324 | 16.7728 | 17.1584 | 17.1621 | 16.1559 | 14.6255 | 16.6691 | 17.0417 | 17.3804 | 17.4433 | 17.1848 | 16.3729 | 14.6363 | 749.5379 | 518.3839 | 471.2927 | 295.023 | 242.6128 | 810.4375 | 516.2188 | 17.5003 | 30.279 | 35.9378 | 73.4293 | 82.3452 | 86.1767 |  |  |  | 601.9228 | 552.682 | 555.745 | 591.0877 | 78.6038 | 32.5018 | 924.7167 |  |  | 688.1396 |  |  | 19.262 | 49.9142 | 478.4029 | 18.6915 | 50.9568 | 756.9037 | 732.919 | 624.2131 | 915.718 | 932.8175 | 732.5129 |  | 807.5605 | 914.504 | 1038.4197 | 601.792 | 686.1527 | 885.5533 |  | 1048.4043 |  |  | 435.1282 | 628.9805 | 724.128 | [6 empty] | 612.7825 |  |  | 423.4981 |  |  | 504.3863 | 662.668 | 666.969 | 976.0126 | 1086.5734 | 1087.0734 | 512.6166 | 705.6578 | 818.363 | 615.3326 | 693.3861 | 1058.633 | 1124.5942 | 617.2009 | 795.5446 | 1132.4451 | 1175.5582 | 1084.1583 | 525.4212 | 648.9786 | 681.916 | 532.2493 | 718.912 | 848.2439 | 1155.7898 | 1162.8983 | 586.0896 | 694.7186 | 639.5221 | 825.7443 | 90.3733 | -0.00049703 | 18.2191 | 5.4397 | -40.0528 | 3.1221 | 9550.89 | 0.32 | 1.024 | -1.076 | -1.7983 | -1.7859 | 7.199 | 5.5199 | 6.2771 | 79.4276 | 171.2253 | 50.3615 | 84.9364 | 27.006 | 88.8827 | 33.5485
42810.4523 | 1064 | 17.5359 | 17.9624 | 18.109 | 18.1517 | 17.49 | 16.131 | 14.8551 | 16.4528 | 16.9478 | 17.089 | 17.098 | 16.6362 | 15.667 | 14.4024 | 20.5679 | 35.8267 | 35.5228 | 86.9808 | 36.1765 | 91.4203 |  |  |  | 27.5951 | 88.3974 | 377.736 | 674.1648 | 709.2908 | 683.8495 | 92.9956 | 122.882 | 845.1467 | 95.3094 | 120.1555 | 820.4317 | 833.1058 | 849.5658 |  | 249.1499 | 839.015 | 841.4673 | 479.6721 |  | 453.6859 | 708.4535 | 556.7339 | 704.7169 | 868.2678 | 1014.9624 | 1058.4381 | 50.1992 | 418.2461 | 91.084 | 634.4761 | 13.9633 | 50.7707 | 48.1475 | 50.5173 | 62.2047 |  |  | 0.3544 | -0.49932 | 0.11028 | -0.60126 | 7.7134 | 6.1409 | 7.0619 | -3.2884 | 19.8862 | 52.6565 | 17.4239 | 0.00011171 | 2.3e-05 | -0.00080661 | 23.0665 | 16.3229 | 16.7745 | 17.1595 | 17.1606 | 16.1518 | 14.6226 | 16.6688 | 17.0397 | 17.3782 | 17.443 | 17.1778 | 16.367 | 14.6368 | 749.8686 | 509.1613 | 455.4811 | 299.6467 | 239.8455 | 807.7539 | 514.2233 | 17.5299 | 30.3815 | 36.0539 | 73.6409 | 82.3979 | 86.1873 |  |  |  | 602.1319 | 553.4651 | 556.384 | 591.9103 | 75.2617 | 27.9044 | 919.9883 |  |  | 691.8998 |  |  | 19.2852 | 50.0224 | 479.7488 | 18.7172 | 51.086 | 756.0466 | 736.6083 | 624.179 | 917.3744 | 938.4408 | 735.0354 |  | 807.9693 | 917.5062 | 1037.4032 | 601.5582 | 685.9096 | 885.1019 |  | 1048.4788 |  |  | 433.9481 | 630.0279 | 725.6495 | [6 empty] | 612.2904 |  |  | 423.7895 |  |  | 504.6472 | 661.7218 | 667.1673 | 977.9531 | 1083.3009 | 1087.4327 | 512.2242 | 707.2646 | 821.4061 | 614.6199 | 693.3838 | 1062.9991 | 1125.9925 | 617.7259 | 798.7445 | 1132.027 | 1177.2612 | 1087.7335 | 525.3708 | 650.5155 | 682.7706 | 532.2144 | 718.1256 | 849.264 | 1159.4115 | 1170.7736 | 586.557 | 695.7231 | 639.4969 | 825.618 | 87.4115 | -0.0011144 | 18.2051 | 5.4412 | -39.986 | 3.1221 | 9392.61 | 0.28 | 1.2834 | -1.5429 | 0.72506 | -1.693 | 6.9465 | 6.1981 | 6.6467 | 79.486 | 170.5942 | 50.3126 | 83.83 | 28.3193 | 94.7367 | 33.5633
42810.4524 | 1065 | 17.5271 | 17.9567 | 18.1079 | 18.1602 | 17.4931 | 16.1312 | 14.8694 | 16.4633 | 16.9562 | 17.084 | 17.1065 | 16.6403 | 15.6739 | 14.3968 | 20.682 | 35.9994 | 35.6858 | 87.0147 | 36.231 | 91.4248 |  |  |  | 27.7302 | 88.4928 | 378.7028 | 673.9767 | 709.3915 | 683.5352 | 92.2237 | 122.9878 | 845.7182 | 95.4799 | 121.7071 | 824.0846 | 823.1212 | 852.8616 |  | 256.7992 | 837.3683 | 841.6892 | 490.4995 |  | 453.9476 | 710.0024 | 557.5224 | 705.6594 | 871.5066 | 1017.489 | 1058.6994 | 48.9762 | 418.3206 | 91.8508 | 634.2497 | 13.9651 | 50.6979 | 48.1589 | 50.5391 | 62.4221 |  |  | 0.32023 | -0.60052 | -0.11183 | -1.2597 | 7.8205 | 6.093 | 6.968 | -4.3444 | 20.2433 | 53.4795 | 20.3966 | 7.228e-05 | 0.0001035 | -0.00080661 | 23.1304 | 16.3264 | 16.7794 | 17.1618 | 17.1572 | 16.1522 | 14.6241 | 16.6671 | 17.0493 | 17.3751 | 17.4482 | 17.1797 | 16.3747 | 14.6436 | 747.0176 | 492.204 | 426.7987 | 293.7396 | 232.7611 | 805.2136 | 512.1632 | 17.564 | 30.4879 | 36.1758 | 73.8174 | 82.4312 | 86.2175 |  |  |  | 602.5632 | 555.6192 | 557.7231 | 594.4549 | 79.3568 | 30.776 | 921.256 |  |  | 694.5284 |  |  | 19.31 | 50.1191 | 480.6075 | 18.7322 | 51.216 | 756.7744 | 740.2802 | 624.9102 | 921.3201 | 946.3423 | 740.2439 |  | 808.7198 | 921.7511 | 1035.6902 | 602.2962 | 685.7903 | 882.2664 |  | 1049.198 |  |  | 434.0974 | 636.769 | 731.2236 | [6 empty] | 613.3565 |  |  | 424.6793 |  |  | 504.1286 | 660.8685 | 667.4883 | 984.7709 | 1087.0146 | 1088.0637 | 512.6786 | 709.7303 | 826.7581 | 614.1881 | 693.6869 | 1070.9931 | 1128.3067 | 619.0089 | 802.9468 | 1133.6601 | 1179.9823 | 1092.078 | 525.955 | 651.2426 | 683.1387 | 532.8576 | 717.8787 | 851.0672 | 1160.0427 | 1173.888 | 586.7886 | 696.2865 | 639.9004 | 827.8152 | 77.0469 | -0.00077063 | 18.1903 | 5.4507 | -40.0273 | 3.122 | 9303.99 | 0.29 | 1.2198 | -1.6933 | -0.73074 | -2.4525 | 7.0014 | 6.1799 | 6.6088 | 79.5774 | 169.5558 | 50.2649 | 83.1395 | 31.0502 | 91.1341 | 33.5702
42810.4524 | 1066 | 17.5374 | 17.9597 | 18.1032 | 18.1473 | 17.4942 | 16.1345 | 14.8704 | 16.4642 | 16.9541 | 17.0893 | 17.1085 | 16.6416 | 15.6706 | 14.4036 | 20.8076 | 36.1959 | 35.8582 | 87.0462 | 36.325 | 91.4252 |  |  |  | 27.8868 | 88.6104 | 383.4577 | 675.4891 | 712.1335 | 685.2829 | 92.7622 | 121.899 | 845.23 | 93.9683 | 119.9892 | 829.1335 | 654.9241 | 859.836 |  | 254.9265 | 842.197 | 842.2314 | 517.6401 |  | 455.2207 | 711.3349 | 558.5711 | 706.7348 | 872.7648 | 1017.0065 | 1058.6939 | 49.0209 | 418.2109 | 90.2502 | 633.8093 | 14.0277 | 50.641 | 48.1719 | 50.5456 | 62.6305 |  |  | 0.50685 | -0.27853 | -0.082916 | -1.0008 | 7.9355 | 5.8564 | 6.3168 | -3.3587 | 20.1701 | 52.1706 | 23.7334 | 7.886e-05 | 5.421e-05 | -0.00079839 | 23.1843 | 16.3251 | 16.7661 | 17.1565 | 17.1612 | 16.1528 | 14.6285 | 16.6666 | 17.0458 | 17.3727 | 17.4454 | 17.1778 | 16.3756 | 14.6409 | 739.7963 | 489.1043 | 436.1771 | 295.8622 | 232.3503 | 802.25 | 510.2729 | 17.6072 | 30.619 | 36.3117 | 73.9809 | 82.4746 | 86.2551 |  |  |  | 602.8652 | 556.557 | 558.4908 | 593.6918 | 73.7009 | 25.5111 | 926.1207 |  |  | 694.9682 |  |  | 19.3304 | 50.2109 | 484.2858 | 18.7567 | 51.3379 | 759.4502 | 738.998 | 625.9435 | 923.3722 | 944.8831 | 739.4665 |  | 808.5783 | 917.0736 | 1034.2425 | 603.1375 | 685.9148 | 881.6417 |  | 1049.9503 |  |  | 434.0124 | 641.6473 | 732.9098 | [6 empty] | 614.0215 |  |  | 424.3263 |  |  | 504.1703 | 659.9932 | 668.4804 | 987.2113 | 1097.8515 | 1085.2366 | 513.2171 | 710.5462 | 829.6968 | 613.8164 | 693.4455 | 1071.7043 | 1126.3389 | 619.3568 | 805.568 | 1137.176 | 1180.9609 | 1096.4815 | 525.9054 | 651.6915 | 683.577 | 533.0743 | 718.269 | 855.296 | 1162.9348 | 1177.363 | 586.7335 | 697.0237 | 640.1635 | 829.5242 | 72.4711 | -0.0011635 | 18.1773 | 5.4631 | -40.0418 | 3.122 | 9300.3 | 0.4 | 1.536 | -1.154 | -0.62964 | -2.1875 | 7.0514 | 6.0576 | 6.2912 | 79.5545 | 168.9106 | 50.2699 | 82.7732 | 29.5912 | 45.8777 | 33.6458
42810.4524 | 1067 | 17.535 | 17.961 | 18.1009 | 18.1514 | 17.4946 | 16.1354 | 14.8851 | 16.4607 | 16.9562 | 17.0951 | 17.1107 | 16.6445 | 15.6727 | 14.4073 | 20.9171 | 36.374 | 36.0047 | 87.0749 | 36.4384 | 91.4423 |  |  |  | 28.0188 | 88.7186 | 387.9682 | 677.8058 | 714.994 | 688.0697 | 90.3571 | 120.2873 | 849.4381 | 93.6741 | 120.107 | 831.4494 | 796.1708 | 864.8683 |  | 245.296 | 849.3935 | 851.4131 | 499.7356 |  | 454.5448 | 715.0548 | 559.3594 | 709.5165 | 876.4371 | 1017.6627 | 1056.6188 | 48.7453 | 417.9605 | 86.963 | 633.3209 | 14.0771 | 50.5749 | 48.178 | 50.5356 | 62.616 |  |  | 1.0536 | 0.12757 | -0.85568 | -0.89171 | 7.8067 | 5.9228 | 7.5206 | -3.8614 | 19.9605 | 53.8832 | 22.1599 | 5.75e-05 | 3.614e-05 | -0.00083946 | 23.2325 | 16.3161 | 16.7635 | 17.1508 | 17.1471 | 16.1407 | 14.616 | 16.6626 | 17.035 | 17.3712 | 17.4391 | 17.1844 | 16.3696 | 14.6302 | 731.8275 | 500.9817 | 432.8549 | 282.0053 | 219.059 | 799.2433 | 508.0379 | 17.6445 | 30.7268 | 36.4351 | 74.1579 | 82.5186 | 86.278 |  |  |  | 603.1652 | 558.2444 | 560.1439 | 594.9483 | 91.3427 | 37.7234 | 928.3961 |  |  | 699.3215 |  |  | 19.3502 | 50.3033 | 488.9625 | 18.7959 | 51.4699 | 764.8103 | 734.5356 | 625.447 | 925.4254 | 945.5765 | 734.6787 |  | 807.6728 | 918.1481 | 1035.0536 | 602.7923 | 685.9603 | 878.8105 |  | 1049.4554 |  |  | 433.6462 | 639.7907 | 728.6619 | [6 empty] | 613.1755 |  |  | 423.2144 |  |  | 504.7801 | 659.5092 | 669.1727 | 990.1311 | 1102.2252 | 1082.4187 | 513.2999 | 709.7255 | 828.9915 | 613.5219 | 693.8578 | 1065.1841 | 1120.6252 | 619.1959 | 803.8309 | 1131.7113 | 1182.1213 | 1100.8261 | 526.3794 | 652.0095 | 684.5138 | 533.6156 | 719.4569 | 857.8058 | 1156.3762 | 1176.4923 | 586.4198 | 697.4197 | 640.8852 | 830.739 | 78.1902 | 0.00010628 | 18.1631 | 5.4823 | -40.0496 | 3.122 | 9372.61 | 0.29 | 2.2177 | 0.78246 | -2.0265 | -2.0687 | 6.9957 | 6.0934 | 6.8663 | 79.4027 | 169.3148 | 50.2899 | 82.48 | 29.4693 | 82.3679 | 33.665
42810.4524 | 1068 | 17.529 | 17.9593 | 18.1015 | 18.1465 | 17.4853 | 16.1347 | 14.8742 | 16.4529 | 16.9547 | 17.0937 | 17.1068 | 16.6495 | 15.668 | 14.4072 | 21.0422 | 36.5638 | 36.18 | 87.1156 | 36.5663 | 91.4759 |  |  |  | 28.1854 | 88.8067 | 392.2423 | 679.7469 | 718.1963 | 689.9043 | 90.7084 | 119.235 | 855.3286 | 94.4728 | 121.1388 | 837.6122 | 827.1059 | 870.7545 |  | 243.8563 | 856.4865 | 860.4551 | 469.9861 |  | 454.6934 | 717.433 | 558.9657 | 708.6999 | 877.8214 | 1018.1038 | 1055.1303 | 47.8892 | 417.6603 | 85.1053 | 632.9272 | 14.1032 | 50.5163 | 48.1769 | 50.5328 | 62.4275 |  |  | 0.91098 | -0.26867 | -0.83532 | -0.62623 | 7.513 | 5.336 | 6.6552 | -2.4473 | 20.1695 | 53.7202 | 21.1094 | 0.0001035 | 7.228e-05 | -0.00081482 | 23.291 | 16.3191 | 16.7597 | 17.1568 | 17.1538 | 16.1446 | 14.6167 | 16.665 | 17.0397 | 17.3677 | 17.4405 | 17.1791 | 16.3693 | 14.634 | 741.4374 | 508.5167 | 461.5108 | 291.8931 | 221.5932 | 797.3183 | 506.8546 | 17.6801 | 30.8317 | 36.547 | 74.3221 | 82.554 | 86.3052 |  |  |  | 603.4909 | 560.2005 | 562.5818 | 595.1666 | 72.4146 | 32.1625 | 930.5478 |  |  | 703.1523 |  |  | 19.364 | 50.4043 | 494.2368 | 18.8231 | 51.6047 | 771.3284 | 731.1483 | 624.4892 | 921.2587 | 935.2025 | 730.1552 |  | 806.5825 | 920.5445 | 1036.6211 | 601.8652 | 685.8244 | 882.1624 |  | 1048.3057 |  |  | 433.7633 | 636.3204 | 723.9939 | [6 empty] | 611.8192 |  |  | 422.4881 |  |  | 505.1249 | 659.7619 | 668.9484 | 985.1884 | 1101.034 | 1077.7762 | 513.8295 | 708.9659 | 827.7046 | 613.2949 | 693.8618 | 1063.5318 | 1120.1113 | 619.3726 | 803.3616 | 1129.216 | 1178.5323 | 1100.5638 | 525.9222 | 651.7472 | 685.6928 | 534.6357 | 721.0445 | 861.3995 | 1148.1677 | 1172.6189 | 585.9376 | 697.883 | 642.068 | 836.7613 | 85.0932 | -0.00049002 | 18.1488 | 5.5187 | -39.9622 | 3.122 | 9467.49 | 0.33 | 2.0642 | -1.1369 | -2.0046 | -1.7357 | 6.864 | 5.7847 | 6.4603 | 79.1863 | 170.0891 | 50.2847 | 80.6613 | 26.0262 | 93.0117 | 33.7178
42810.4524 | 1069 | 17.5188 | 17.9547 | 18.0965 | 18.1348 | 17.4814 | 16.1277 | 14.8739 | 16.4534 | 16.9518 | 17.0903 | 17.1036 | 16.6402 | 15.6638 | 14.4036 | 21.1553 | 36.7305 | 36.3323 | 87.1575 | 36.7105 | 91.4994 |  |  |  | 28.3354 | 88.9126 | 396.0674 | 682.1144 | 720.2247 | 691.8197 | 96.6622 | 122.8575 | 862.1411 | 93.8289 | 121.0933 | 843.0565 | 849.9791 | 876.4062 |  | 251.3811 | 860.9992 | 865.3039 | 482.8073 |  | 455.4956 | 715.4093 | 558.8703 | 705.4316 | 871.5663 | 1011.3232 | 1052.5027 | 45.9674 | 417.4122 | 82.2993 | 632.3972 | 14.1186 | 50.4514 | 48.1808 | 50.5154 | 62.0739 |  |  | 0.79993 | -0.58737 | -0.19003 | -0.63149 | 7.8566 | 5.7592 | 7.1033 | -3.1228 | 20.4638 | 53.4969 | 19.4031 | 4.928e-05 | 9.2e-05 | -0.00083125 | 23.3549 | 16.3181 | 16.7663 | 17.1594 | 17.1519 | 16.1415 | 14.6283 | 16.6631 | 17.0462 | 17.3757 | 17.4523 | 17.1776 | 16.3713 | 14.6342 | 724.3107 | 499.4372 | 456.258 | 292.0783 | 225.3043 | 794.773 | 505.5538 | 17.7116 | 30.9408 | 36.6596 | 74.4761 | 82.5848 | 86.3305 |  |  |  | 603.8106 | 561.7234 | 563.8101 | 595.3544 | 83.5855 | 37.8764 | 925.9623 |  |  | 691.6619 |  |  | 19.3962 | 50.5088 | 497.6268 | 18.8623 | 51.7241 | 777.0969 | 732.5978 | 624.3273 | 912.8651 | 926.0731 | 729.6258 |  | 806.3776 | 917.3853 | 1035.5215 | 601.7343 | 685.7965 | 889.44 |  | 1048.0033 |  |  | 434.3128 | 634.3448 | 723.1585 | [6 empty] | 611.8402 |  |  | 421.7875 |  |  | 505.9653 | 660.186 | 668.7013 | 976.0447 | 1099.4427 | 1080.8523 | 514.0807 | 708.6865 | 828.8157 | 613.3824 | 693.5329 | 1059.4391 | 1121.6148 | 619.7591 | 804.4225 | 1132.1752 | 1176.4983 | 1103.0655 | 525.9255 | 651.9801 | 687.1495 | 535.0387 | 722.9364 | 866.8461 | 1148.1434 | 1171.4303 | 585.7434 | 698.9215 | 642.8712 | 842.1528 | 96.9905 | -0.00069348 | 18.135 | 5.5495 | -40.0163 | 3.122 | 9535.21 | 0.23 | 1.9362 | -1.6793 | -0.95516 | -1.7412 | 7.0008 | 5.9939 | 6.6567 | 79.1369 | 169.5867 | 50.282 | 81.5759 | 26.3257 | 100.419 | 33.7703
42810.4524 | 1070 | 17.5265 | 17.9613 | 18.1084 | 18.1426 | 17.4864 | 16.1306 | 14.8822 | 16.4644 | 16.9527 | 17.0953 | 17.1095 | 16.6395 | 15.6726 | 14.4106 | 21.2755 | 36.9122 | 36.4907 | 87.2041 | 36.8452 | 91.4996 |  |  |  | 28.4766 | 89.0033 | 398.9133 | 683.9099 | 721.6949 | 693.0397 | 97.9791 | 124.6609 | 868.1593 | 94.0995 | 120.1045 | 843.0916 | 867.5103 | 876.9205 |  | 257.1884 | 866.1065 | 868.4219 | 519.5941 |  | 456.6585 | 714.1194 | 559.095 | 704.5083 | 868.7524 | 1011.0597 | 1051.8718 | 44.7277 | 417.3403 | 81.1412 | 631.974 | 14.1147 | 50.3874 | 48.1903 | 50.501 | 61.7298 |  |  | 0.46874 | -0.92382 | -0.8248 | -0.88579 | 7.6102 | 5.5108 | 6.9436 | -3.705 | 20.5663 | 53.2211 | 18.8925 | 0.00016099 | 7.228e-05 | -0.00082796 | 23.4185 | 16.3271 | 16.7636 | 17.1573 | 17.1537 | 16.1487 | 14.6176 | 16.6644 | 17.0421 | 17.3742 | 17.4512 | 17.1847 | 16.3676 | 14.6362 | 725.4494 | 497.6216 | 454.1654 | 297.4953 | 228.4927 | 792.9178 | 504.3444 | 17.7573 | 31.0543 | 36.7926 | 74.6555 | 82.6256 | 86.3479 |  |  |  | 604.3069 | 563.9647 | 565.7681 | 599.2969 | 79.5084 | 28.4135 | 920.1347 |  |  | 680.8407 |  |  | 19.4169 | 50.6041 | 500.4463 | 18.895 | 51.8534 | 782.8732 | 737.6 | 624.4434 | 908.2536 | 921.0721 | 734.8035 |  | 807.2693 | 914.0844 | 1033.7036 | 602.2707 | 685.8577 | 880.92 |  | 1047.8644 |  |  | 434.9822 | 635.3192 | 727.4499 | [6 empty] | 612.2758 |  |  | 422.1571 |  |  | 506.683 | 660.3027 | 668.8007 | 967.7389 | 1091.5988 | 1084.4961 | 514.7928 | 708.8366 | 830.6205 | 613.3958 | 692.6782 | 1056.5101 | 1116.3768 | 620.065 | 804.5552 | 1126.3764 | 1177.6297 | 1100.9969 | 526.2487 | 652.2089 | 689.2678 | 534.7818 | 723.958 | 868.4506 | 1149.1543 | 1167.5637 | 586.1097 | 700.0329 | 643.5672 | 843.8671 | 87.2432 | 0.00026764 | 18.1215 | 5.5757 | -40.0594 | 3.122 | 9534.4 | 0.31 | 1.4831 | -2.1046 | -1.9887 | -2.0609 | 6.8894 | 5.8626 | 6.5808 | 79.2725 | 168.7057 | 50.281 | 80.7321 | 26.2946 | 105.6504 | 33.7505
42810.4524 | 1071 | 17.5258 | 17.955 | 18.1015 | 18.1423 | 17.4862 | 16.1307 | 14.8807 | 16.4679 | 16.956 | 17.0961 | 17.1095 | 16.6398 | 15.6745 | 14.4137 | 21.3946 | 37.0904 | 36.6481 | 87.2507 | 36.9504 | 91.5008 |  |  |  | 28.6188 | 89.0891 | 402.7138 | 685.2342 | 722.8306 | 694.2999 | 91.907 | 125.8028 | 874.7566 | 93.6264 | 118.5229 | 842.6568 | 891.9436 | 871.5441 |  | 266.5417 | 870.9159 | 872.2706 | 508.9191 |  | 457.2919 | 713.1807 | 557.5014 | 702.0825 | 866.1979 | 1010.7131 | 1051.9318 | 44.1072 | 417.4099 | 78.5998 | 631.4823 | 14.1415 | 50.3537 | 48.2131 | 50.4957 | 61.4306 |  |  | 0.71647 | -0.44609 | -0.4417 | -0.58812 | 8.2687 | 5.8262 | 6.9003 | -2.5557 | 19.8502 | 52.6275 | 18.9102 | 0.00011007 | 0.00012814 | -0.0007754 | 23.4855 | 16.3303 | 16.7671 | 17.1557 | 17.1556 | 16.1512 | 14.6211 | 16.6664 | 17.044 | 17.3731 | 17.4527 | 17.187 | 16.3714 | 14.6406 | 722.3505 | 489.4379 | 428.4827 | 284.0756 | 221.6815 | 790.9345 | 502.8322 | 17.8002 | 31.1781 | 36.9173 | 74.8261 | 82.6751 | 86.3788 |  |  |  | 605.1196 | 567.5109 | 568.5528 | 602.9823 | 73.5088 | 26.2253 | 916.9395 |  |  | 682.4008 |  |  | 19.4308 | 50.6991 | 503.7065 | 18.9291 | 51.9754 | 787.0203 | 740.5797 | 625.5357 | 906.699 | 915.8181 | 741.32 |  | 808.1705 | 927.1354 | 1033.0292 | 602.936 | 686.1706 | 880.8925 |  | 1047.8801 |  |  | 435.5177 | 641.8984 | 732.5339 | [6 empty] | 613.0381 |  |  | 422.4986 |  |  | 506.8966 | 660.0111 | 669.3692 | 964.0691 | 1087.7719 | 1085.9244 | 515.4198 | 709.4374 | 831.2849 | 613.2497 | 691.8 | 1060.6641 | 1115.1547 | 620.8135 | 805.6252 | 1123.833 | 1176.8194 | 1096.4982 | 526.6994 | 652.122 | 690.8932 | 534.5836 | 725.3269 | 869.5787 | 1148.3367 | 1164.0977 | 586.5292 | 701.1327 | 644.3823 | 845.3077 | 86.3514 | -0.00072857 | 18.1089 | 5.6022 | -40.0288 | 3.1219 | 9459.55 | 0.2 | 1.8348 | -1.4618 | -1.4546 | -1.6785 | 7.1803 | 6.0272 | 6.5593 | 79.3747 | 167.9834 | 50.3338 | 80.3126 | 28.8195 | 115.1179 | 33.7954
42810.4524 | 1072 | 17.5181 | 17.9608 | 18.1062 | 18.1516 | 17.485 | 16.1336 | 14.8884 | 16.4713 | 16.9604 | 17.1011 | 17.105 | 16.6461 | 15.6732 | 14.412 | 21.5119 | 37.2695 | 36.8113 | 87.2754 | 37.1009 | 91.5026 |  |  |  | 28.7547 | 89.1496 | 404.7273 | 685.9337 | 722.954 | 695.1946 | 90.8417 | 124.1746 | 880.9425 | 98.5956 | 124.4985 | 845.764 | 755.0224 | 874.7929 |  | 250.7016 | 880.3751 | 879.246 | 499.1877 |  | 456.5427 | 713.2397 | 555.5707 | 700.8899 | 866.3905 | 1010.9595 | 1051.0777 | 44.4412 | 417.2853 | 75.8443 | 631.267 | 14.167 | 50.3486 | 48.2178 | 50.4845 | 61.2649 |  |  | 0.30446 | -0.47567 | -0.23011 | -0.36733 | 8.4211 | 5.7138 | 7.0981 | -3.3909 | 20.3534 | 52.414 | 20.0962 | 8.05e-05 | 0.00013635 | -0.00080497 | 23.5479 | 16.3353 | 16.7673 | 17.1553 | 17.1569 | 16.1462 | 14.6253 | 16.6712 | 17.0444 | 17.3755 | 17.4512 | 17.1872 | 16.3747 | 14.6412 | 711.7847 | 487.9586 | 423.7357 | 274.8311 | 218.1047 | 788.5524 | 501.0408 | 17.8452 | 31.2923 | 37.0387 | 75.0162 | 82.7131 | 86.4172 |  |  |  | 605.7174 | 569.7513 | 571.0477 | 602.2751 | 81.8733 | 30.2756 | 916.3367 |  |  | 673.6595 |  |  | 19.4662 | 50.7995 | 506.0998 | 18.9714 | 52.0992 | 793.9732 | 741.6523 | 626.5146 | 899.1378 | 901.4371 | 742.4335 |  | 808.3733 | 950.6048 | 1033.9211 | 603.5219 | 686.6283 | 903.4716 |  | 1048.6323 |  |  | 436.2363 | 647.5991 | 734.6213 | [6 empty] | 613.9393 |  |  | 421.9029 |  |  | 507.4312 | 659.6775 | 669.4398 | 961.3202 | 1086.6108 | 1089.5924 | 516.3633 | 709.8699 | 831.8161 | 613.5112 | 691.9251 | 1056.7921 | 1119.1348 | 621.4702 | 805.521 | 1122.6629 | 1175.7682 | 1093.0364 | 527.3196 | 652.4484 | 692.3321 | 535.1278 | 727.2597 | 869.8734 | 1144.9433 | 1165.7306 | 587.9441 | 702.4921 | 645.201 | 847.448 | 89.4186 | 0.00046404 | 18.0963 | 5.6222 | -40.0826 | 3.1219 | 9371.3 | 0.32 | 1.1966 | -1.5095 | -1.0499 | -1.3265 | 7.2469 | 5.9694 | 6.6533 | 79.4075 | 167.8075 | 50.422 | 80.5731 | 28.9587 | 70.4711 | 33.9236
42810.4525 | 1073 | 17.5172 | 17.9533 | 18.0933 | 18.139 | 17.4817 | 16.1219 | 14.8917 | 16.4564 | 16.9485 | 17.0895 | 17.1035 | 16.6433 | 15.6716 | 14.4047 | 21.6361 | 37.4527 | 36.9765 | 87.2794 | 37.2604 | 91.5055 |  |  |  | 28.9097 | 89.2094 | 405.9181 | 686.1866 | 722.6021 | 695.0215 | 94.7487 | 125.4316 | 888.8568 | 96.7838 | 124.077 | 844.6727 | 841.79 | 874.2745 |  | 249.1008 | 890.8652 | 890.0432 | 508.9987 |  | 458.4469 | 713.4783 | 555.7066 | 703.1215 | 875.1918 | 1013.0497 | 1053.5567 | 44.7994 | 417.0776 | 74.9445 | 631.4899 | 14.1638 | 50.3303 | 48.2126 | 50.4613 | 61.1684 |  |  | 0.64813 | -0.2437 | -0.72755 | -0.88711 | 7.8645 | 5.1934 | 6.9371 | -3.1188 | 20.2137 | 52.9343 | 20.1453 | 0.00010843 | 8.707e-05 | -0.00085261 | 23.6007 | 16.323 | 16.7591 | 17.1493 | 17.1512 | 16.1369 | 14.6265 | 16.6636 | 17.041 | 17.3702 | 17.446 | 17.1781 | 16.3714 | 14.6425 | 712.0873 | 485.5135 | 437.8594 | 273.0704 | 216.8732 | 786.7189 | 499.5305 | 17.8838 | 31.4047 | 37.1653 | 75.1915 | 82.7538 | 86.4455 |  |  |  | 606.216 | 570.8651 | 573.2646 | 601.3055 | 61.0489 | 31.6349 | 909.1985 |  |  | 655.188 |  |  | 19.4947 | 50.9008 | 506.4619 | 18.9833 | 52.2402 | 801.3957 | 743.8617 | 626.5507 | 889.7441 | 888.1472 | 745.5782 |  | 808.981 | 960.5284 | 1034.7881 | 603.8556 | 686.9907 | 943.0154 |  | 1048.8645 |  |  | 436.9495 | 652.9625 | 736.0538 | [6 empty] | 613.8708 |  |  | 421.0482 |  |  | 508.5369 | 659.7055 | 669.7235 | 960.2685 | 1081.0515 | 1088.9828 | 517.1319 | 709.1348 | 832.1304 | 613.8563 | 693.0348 | 1056.4407 | 1123.4869 | 620.9844 | 804.8187 | 1121.8792 | 1172.57 | 1092.9108 | 528.1044 | 653.3577 | 693.5972 | 535.5124 | 728.9584 | 870.0583 | 1143.6677 | 1166.4623 | 589.0894 | 703.7346 | 645.843 | 851.1143 | 94.8715 | -0.0001954 | 18.0842 | 5.6422 | -40.0882 | 3.1219 | 9299.13 | 0.26 | 1.7457 | -1.0806 | -1.8671 | -2.0617 | 7.009 | 5.6957 | 6.5828 | 79.5116 | 167.9954 | 50.4955 | 79.8395 | 27.0631 | 96.8613 | 34.0413
42810.4525 | 1074 | 17.5198 | 17.9442 | 18.0903 | 18.1374 | 17.4837 | 16.1299 | 14.8983 | 16.4514 | 16.9476 | 17.0828 | 17.1044 | 16.6379 | 15.6726 | 14.4068 | 21.7518 | 37.6341 | 37.1336 | 87.2852 | 37.438 | 91.5294 |  |  |  | 29.0716 | 89.2783 | 406.647 | 686.1856 | 721.3547 | 695.1415 | 92.2719 | 124.7299 | 893.1554 | 95.2639 | 121.8665 | 841.1377 | 812.9517 | 871.7612 |  | 245.3316 | 893.7615 | 892.8989 | 508.8951 |  | 460.1746 | 713.3502 | 557.0104 | 703.9881 | 871.8876 | 1009.0411 | 1053.4156 | 42.888 | 417.0243 | 76.2983 | 631.3606 | 14.1658 | 50.3088 | 48.2108 | 50.4457 | 61.2066 |  |  | 0.87484 | -0.089937 | -0.39308 | -0.94887 | 8.1556 | 6.0135 | 7.4891 | -2.5787 | 19.4489 | 51.7789 | 21.2743 | 5.914e-05 | 7.886e-05 | -0.00084768 | 23.6605 | 16.325 | 16.7586 | 17.1485 | 17.1495 | 16.1411 | 14.6282 | 16.6609 | 17.0425 | 17.3732 | 17.442 | 17.1832 | 16.376 | 14.6423 | 694.5062 | 483.8278 | 434.996 | 269.3474 | 213.305 | 783.5627 | 497.7428 | 17.9221 | 31.5114 | 37.2782 | 75.3515 | 82.7842 | 86.4543 |  |  |  | 606.7923 | 572.1281 | 574.8377 | 603.1724 | 68.9009 | 24.2808 | 900.3 |  |  | 637.8125 |  |  | 19.5117 | 50.9996 | 506.0572 | 19.0365 | 52.3529 | 805.9471 | 747.1432 | 624.7441 | 881.6894 | 878.1326 | 749.8844 |  | 809.9483 | 966.4763 | 1036.6878 | 602.6637 | 686.9407 | 969.0505 |  | 1049.2449 |  |  | 438.7437 | 659.6923 | 739.2991 | [6 empty] | 612.2521 |  |  | 420.2194 |  |  | 509.5696 | 659.9034 | 669.9532 | 964.2198 | 1079.4751 | 1087.6774 | 517.4837 | 707.8389 | 833.2834 | 613.9017 | 694.1621 | 1059.0107 | 1125.2554 | 620.5745 | 804.3964 | 1124.4055 | 1171.2804 | 1094.3662 | 527.6493 | 654.8052 | 695.2399 | 535.7755 | 729.9231 | 870.3476 | 1147.6641 | 1166.0591 | 589.966 | 705.9734 | 646.0377 | 853.1268 | 96.8075 | 0.0011656 | 18.0722 | 5.6623 | -40.052 | 3.1219 | 9186.36 | 0.25 | 2.0283 | -0.65642 | -1.3723 | -2.1322 | 7.1264 | 6.1194 | 6.829 | 79.6972 | 168.8491 | 50.5172 | 80.5938 | 26.9962 | 87.3438 | 34.0944
42810.4525 | 1075 | 17.5208 | 17.9492 | 18.0936 | 18.1424 | 17.4826 | 16.1312 | 14.8937 | 16.4612 | 16.9455 | 17.0909 | 17.1136 | 16.6404 | 15.6762 | 14.4142 | 21.881 | 37.821 | 37.2986 | 87.3022 | 37.5731 | 91.5496 |  |  |  | 29.2215 | 89.348 | 407.0757 | 685.4857 | 719.7253 | 694.7368 | 91.909 | 120.6479 | 894.11 | 94.8055 | 122.0991 | 841.4407 | 778.1454 | 869.7665 |  | 251.8648 | 895.319 | 896.4407 | 485.1366 |  | 461.0109 | 714.1458 | 556.5401 | 703.0416 | 872.0711 | 1011.3118 | 1054.3231 | 42.7121 | 417.2195 | 76.9467 | 631.0519 | 14.1661 | 50.2948 | 48.2195 | 50.4444 | 61.299 |  |  | 0.32549 | 0.34705 | 0.051792 | -0.47444 | 8.0137 | 6.1488 | 7.1638 | -3.0682 | 19.7566 | 52.6074 | 22.2869 | 2.464e-05 | 0.00013635 | -0.00082632 | 23.7213 | 16.3328 | 16.757 | 17.1442 | 17.1618 | 16.1478 | 14.6247 | 16.6621 | 17.045 | 17.3689 | 17.4431 | 17.1872 | 16.372 | 14.6453 | 693.5044 | 471.1751 | 405.0089 | 258.9343 | 207.6755 | 780.9373 | 495.565 | 17.9597 | 31.6358 | 37.4059 | 75.5145 | 82.8192 | 86.4733 |  |  |  | 607.9757 | 576.4573 | 579.4458 | 611.0557 | 85.7649 | 27.4401 | 894.1452 |  |  | 623.2653 |  |  | 19.5415 | 51.0948 | 504.4171 | 19.0564 | 52.4536 | 807.3064 | 750.46 | 623.6742 | 873.0877 | 865.9997 | 752.575 |  | 811.2274 | 975.0444 | 1037.8698 | 601.4687 | 686.809 | 991.0238 |  | 1049.5449 |  |  | 440.9076 | 664.4281 | 743.0452 | [6 empty] | 610.8519 |  |  | 419.6043 |  |  | 510.0446 | 660.6461 | 670.4858 | 965.137 | 1087.8395 | 1087.7994 | 517.9392 | 707.5822 | 835.1314 | 614.3124 | 695.603 | 1058.7703 | 1125.9059 | 620.7937 | 806.7343 | 1127.9262 | 1169.022 | 1096.2659 | 527.7666 | 656.572 | 696.9483 | 536.3341 | 730.7872 | 870.4035 | 1144.6018 | 1165.4432 | 590.7977 | 708.4208 | 646.2783 | 854.4778 | 90.9118 | -0.00056722 | 18.0602 | 5.6686 | -40.0095 | 3.1219 | 9134.06 | 0.26 | 1.2369 | 1.29 | 0.49834 | -1.5083 | 7.0704 | 6.1933 | 6.685 | 80.0272 | 169.2471 | 50.5203 | 79.7134 | 29.8608 | 77.3991 | 34.0915
42810.4525 | 1076 | 17.5147 | 17.9523 | 18.0933 | 18.1399 | 17.4846 | 16.1309 | 14.8949 | 16.4635 | 16.9562 | 17.0974 | 17.1171 | 16.6424 | 15.6758 | 14.4113 | 22.0123 | 38.0029 | 37.4628 | 87.3267 | 37.7249 | 91.5686 |  |  |  | 29.3841 | 89.4066 | 407.8451 | 685.0102 | 719.3491 | 694.2349 | 93.4173 | 121.3541 | 896.0178 | 93.0616 | 120.7047 | 840.1691 | 800.8831 | 869.0596 |  | 256.4728 | 901.7512 | 903.6236 | 481.0267 |  | 461.8792 | 714.4801 | 557.2565 | 702.3746 | 879.2399 | 1014.5577 | 1054.3572 | 43.6948 | 417.3 | 75.7796 | 630.5554 | 14.1896 | 50.2602 | 48.2072 | 50.4369 | 61.4303 |  |  | 0.7375 | -0.73983 | -0.03232 | -0.73728 | 8.1221 | 5.5837 | 7.7098 | -2.9099 | 19.0907 | 52.4727 | 21.9237 | 4.928e-05 | 1.314e-05 | -0.00080004 | 23.7831 | 16.3253 | 16.7598 | 17.1399 | 17.1499 | 16.1413 | 14.6235 | 16.6562 | 17.0479 | 17.3669 | 17.4391 | 17.1867 | 16.3714 | 14.6425 | 714.772 | 471.9742 | 399.5412 | 257.6012 | 206.6099 | 779.2558 | 493.6682 | 18.006 | 31.747 | 37.5236 | 75.6522 | 82.8486 | 86.4944 |  |  |  | 609.143 | 579.6658 | 582.7059 | 615.5574 | 72.4607 | 24.1909 | 886.0924 |  |  | 609.5777 |  |  | 19.5534 | 51.189 | 504.9059 | 19.0955 | 52.5777 | 811.9796 | 752.879 | 624.1865 | 864.9739 | 856.7766 | 756.0918 |  | 812.8842 | 974.8245 | 1037.7663 | 602.1097 | 686.9239 | 998.7506 |  | 1049.6409 |  |  | 441.8319 | 664.8251 | 745.9544 | [6 empty] | 611.2649 |  |  | 419.433 |  |  | 511.0029 | 661.7489 | 671.1595 | 962.4562 | 1090.2854 | 1091.0403 | 518.5371 | 708.4197 | 836.3928 | 614.8992 | 696.4618 | 1062.018 | 1125.181 | 621.014 | 808.3917 | 1127.2997 | 1163.9838 | 1099.9832 | 527.8219 | 658.0718 | 698.052 | 536.3728 | 731.1186 | 870.0358 | 1142.3782 | 1166.2368 | 591.6454 | 709.8263 | 646.4109 | 853.0962 | 94.0483 | -0.00053212 | 18.0476 | 5.6895 | -40.0419 | 3.1219 | 9091.78 | 0.28 | 1.8614 | -1.8838 | -0.39373 | -1.8805 | 7.1271 | 5.9093 | 6.9438 | 80.4558 | 169.1975 | 50.5287 | 76.7179 | 30.0629 | 84.3339 | 34.1803
42810.4525 | 1077 | 17.5189 | 17.9534 | 18.099 | 18.1434 | 17.4822 | 16.123 | 14.9038 | 16.4663 | 16.9532 | 17.0979 | 17.1159 | 16.6462 | 15.6758 | 14.4195 | 22.1291 | 38.1747 | 37.6199 | 87.3349 | 37.8299 | 91.586 |  |  |  | 29.5237 | 89.4574 | 409.199 | 684.8299 | 719.5195 | 694.0325 | 95.66 | 121.8176 | 907.0752 | 91.964 | 118.4052 | 838.3734 | 858.2767 | 868.7676 |  | 251.1991 | 913.5641 | 912.5754 | 497.7219 |  | 462.2654 | 715.1452 | 559.708 | 703.6922 | 881.9123 | 1011.069 | 1051.842 | 43.5678 | 417.247 | 74.2883 | 630.1864 | 14.1998 | 50.2056 | 48.1966 | 50.4461 | 61.6182 |  |  | 0.82753 | -0.63666 | -0.87803 | -0.98173 | 8.2851 | 5.9997 | 6.9193 | -3.6991 | 19.3145 | 51.6593 | 23.4513 | 0.00010185 | 0.00011664 | -0.00082139 | 23.8481 | 16.3324 | 16.7583 | 17.1415 | 17.1567 | 16.1376 | 14.6224 | 16.6653 | 17.0453 | 17.3755 | 17.4467 | 17.1802 | 16.3776 | 14.6467 | 711.7894 | 472.0173 | 384.7771 | 252.5525 | 208.7548 | 776.713 | 491.6777 | 18.0479 | 31.858 | 37.6473 | 75.797 | 82.8824 | 86.5065 |  |  |  | 610.1825 | 581.9802 | 585.4167 | 615.7122 | 71.5703 | 21.5642 | 879.0795 |  |  | 599.1219 |  |  | 19.5752 | 51.2815 | 506.2675 | 19.1386 | 52.7111 | 822.1954 | 753.7714 | 624.6506 | 862.923 | 855.1649 | 757.6678 |  | 813.906 | 977.8347 | 1037.7014 | 602.9287 | 687.179 | 998.6842 |  | 1050.0895 |  |  | 442.4879 | 663.8865 | 747.3874 | [6 empty] | 611.6099 |  |  | 419.7616 |  |  | 511.4133 | 662.5676 | 671.8126 | 966.3931 | 1090.2643 | 1090.3168 | 519.1383 | 709.1377 | 836.3598 | 615.4178 | 697.6499 | 1068.2268 | 1129.8109 | 621.3366 | 808.3083 | 1124.942 | 1162.0991 | 1103.4349 | 528.5521 | 658.9508 | 698.3578 | 536.9161 | 730.5269 | 869.2911 | 1141.798 | 1167.4294 | 592.6675 | 710.5592 | 646.3209 | 852.2284 | 87.0862 | -0.001402 | 18.0343 | 5.6922 | -40.132 | 3.1218 | 9105.39 | 0.26 | 1.9716 | -1.7481 | -2.0529 | -2.1707 | 7.1884 | 6.1172 | 6.5693 | 80.7376 | 169.079 | 50.5643 | 76.097 | 31.2794 | 102.931 | 34.3671
42810.4525 | 1078 | 17.52 | 17.9538 | 18.0988 | 18.1424 | 17.4817 | 16.133 | 14.9127 | 16.4703 | 16.9585 | 17.099 | 17.1083 | 16.6531 | 15.677 | 14.4175 | 22.2652 | 38.355 | 37.7838 | 87.372 | 37.9704 | 91.6177 |  |  |  | 29.6825 | 89.5101 | 410.0641 | 684.6594 | 718.99 | 694.125 | 95.5544 | 124.91 | 912.2958 | 91.0421 | 118.5941 | 833.9566 | 897.4019 | 861.6902 |  | 276.2085 | 911.3953 | 913.7995 | 504.9809 |  | 462.792 | 715.115 | 559.7546 | 702.8896 | 878.2496 | 1011.4512 | 1049.9408 | 43.8944 | 417.2921 | 74.5843 | 629.9442 | 14.212 | 50.1049 | 48.194 | 50.4487 | 61.8083 |  |  | 0.9399 | -0.50589 | -1.0167 | -1.1874 | 7.1614 | 5.7828 | 6.7478 | -2.5977 | 19.2362 | 51.6301 | 24.132 | 6.736e-05 | 9.693e-05 | -0.00078032 | 23.9111 | 16.3303 | 16.7583 | 17.1428 | 17.152 | 16.1375 | 14.6254 | 16.6664 | 17.0429 | 17.3798 | 17.4504 | 17.1871 | 16.3751 | 14.6468 | 710.1257 | 461.7273 | 374.8031 | 245.5503 | 205.2901 | 774.3822 | 489.4574 | 18.0879 | 31.9658 | 37.7649 | 75.9482 | 82.9151 | 86.5172 |  |  |  | 610.7936 | 583.8504 | 587.6715 | 611.374 | 79.5605 | 29.3171 | 877.5666 |  |  | 591.5377 |  |  | 19.6045 | 51.3808 | 507.0034 | 19.1681 | 52.8345 | 825.0139 | 752.2414 | 625.5482 | 859.5087 | 849.4403 | 757.6709 |  | 814.4157 | 985.0451 | 1037.2918 | 603.6104 | 687.371 | 997.6646 |  | 1051.322 |  |  | 442.8941 | 660.1926 | 747.5943 | [6 empty] | 612.1291 |  |  | 420.421 |  |  | 511.5323 | 663.8396 | 672.8775 | 978.0098 | 1101.3034 | 1088.0777 | 519.3474 | 710.292 | 835.9242 | 616.3365 | 699.8251 | 1073.9172 | 1135.035 | 621.7808 | 809.5317 | 1121.2562 | 1163.5515 | 1102.1755 | 530.1957 | 659.484 | 698.2503 | 537.3831 | 730.2088 | 868.279 | 1140.018 | 1168.1305 | 593.9834 | 711.0776 | 645.7757 | 850.2876 | 85.2107 | 4.3152e-05 | 18.0216 | 5.6938 | -40.088 | 3.1218 | 9131.61 | 0.24 | 2.1013 | -1.5582 | -2.209 | -2.3873 | 6.6842 | 6.0065 | 6.4883 | 80.9003 | 168.6581 | 50.5893 | 75.4132 | 31.9167 | 117.3506 | 34.6002
42810.4525 | 1079 | 17.5097 | 17.9398 | 18.0934 | 18.1294 | 17.483 | 16.1285 | 14.9122 | 16.4551 | 16.9455 | 17.0903 | 17.1078 | 16.6377 | 15.6722 | 14.4142 | 22.3793 | 38.5303 | 37.9401 | 87.4167 | 38.1125 | 91.6298 |  |  |  | 29.8479 | 89.5538 | 411.7639 | 684.5113 | 718.7205 | 694.1422 | 88.4539 | 122.9362 | 914.433 | 94.3508 | 121.3392 | 837.9888 | 891.4842 | 862.2839 |  | 290.4832 | 906.9031 | 910.7511 | 510.408 |  | 463.2545 | 714.9596 | 558.4874 | 702.1856 | 877.2674 | 1013.1802 | 1047.6663 | 44.1476 | 417.2791 | 75.6812 | 629.6098 | 14.2073 | 49.9925 | 48.1871 | 50.4511 | 62.0184 |  |  | 0.95172 | 0.054627 | -0.23931 | -0.57695 | 8.0459 | 6.0923 | 7.834 | -2.8718 | 20.8047 | 54.0359 | 26.796 | 3.779e-05 | 9.2e-05 | -0.00082796 | 23.9717 | 16.3385 | 16.7551 | 17.1449 | 17.1549 | 16.1451 | 14.6252 | 16.6662 | 17.0456 | 17.3762 | 17.4539 | 17.1965 | 16.3793 | 14.648 | 718.4995 | 476.6301 | 426.6647 | 254.1913 | 213.303 | 772.8348 | 488.0142 | 18.1507 | 32.0949 | 37.8983 | 76.1063 | 82.9723 | 86.5442 |  |  |  | 611.0437 | 582.5833 | 587.5523 | 605.765 | 79.5584 | 40.5007 | 874.6603 |  |  | 583.5926 |  |  | 19.6328 | 51.4847 | 508.3518 | 19.201 | 52.9594 | 823.7033 | 748.5602 | 627.1704 | 853.0369 | 840.6051 | 753.1435 |  | 814.2911 | 982.8514 | 1036.1794 | 605.7914 | 687.8811 | 996.881 |  | 1051.5396 |  |  | 442.2422 | 652.7425 | 744.1447 | [6 empty] | 613.6098 |  |  | 423.1461 |  |  | 511.9193 | 665.5113 | 674.0117 | 986.2301 | 1103.261 | 1083.0747 | 519.3034 | 711.9091 | 835.5124 | 616.9173 | 700.8543 | 1076.1315 | 1131.29 | 622.1511 | 809.8985 | 1121.3499 | 1164.0923 | 1099.858 | 532.2132 | 659.9294 | 698.3694 | 538.4694 | 729.5122 | 866.4763 | 1139.2715 | 1165.0587 | 595.0395 | 710.865 | 645.3892 | 848.0559 | 82.8846 | -0.00017432 | 18.0092 | 5.6977 | -40.0627 | 3.1218 | 9155.97 | 0.36 | 2.1145 | 0.512 | -1.0716 | -1.6639 | 7.0897 | 6.1693 | 6.9958 | 80.9863 | 168.1211 | 50.6455 | 73.9083 | 25.8491 | 114.8991 | 34.8022
42810.4525 | 1080 | 17.5165 | 17.949 | 18.0891 | 18.1328 | 17.488 | 16.1248 | 14.9092 | 16.456 | 16.9492 | 17.0982 | 17.1036 | 16.6391 | 15.6725 | 14.4122 | 22.521 | 38.7201 | 38.114 | 87.4359 | 38.3299 | 91.6384 |  |  |  | 29.9933 | 89.5999 | 411.1996 | 683.7676 | 716.9196 | 693.4782 | 92.5754 | 118.3623 | 905.6122 | 94.1304 | 123.7764 | 839.4145 | 738.2355 | 867.3669 |  | 254.1367 | 905.7562 | 905.5829 | 496.9303 |  | 464.7598 | 715.489 | 558.296 | 703.2978 | 885.6011 | 1018.5672 | 1050.0476 | 44.9692 | 417.1149 | 77.3211 | 629.3158 | 14.1772 | 49.9266 | 48.1691 | 50.4568 | 62.2332 |  |  | 1.3611 | -0.78648 | 0.034708 | -0.72414 | 7.9026 | 6.2993 | 7.2117 | -2.9434 | 20.8644 | 55.622 | 25.7677 | 0.00010185 | 5.093e-05 | -0.00077211 | 24.0351 | 16.3335 | 16.749 | 17.1387 | 17.1488 | 16.1408 | 14.6167 | 16.6607 | 17.0445 | 17.3758 | 17.4465 | 17.1878 | 16.3762 | 14.6473 | 708.9365 | 475.1452 | 449.0991 | 290.5496 | 241.7606 | 771.7276 | 487.5566 | 18.1912 | 32.2133 | 38.0294 | 76.2305 | 83.0046 | 86.5599 |  |  |  | 611.3834 | 580.4261 | 585.7059 | 605.7589 | 88.1007 | 31.6993 | 868.7708 |  |  | 577.0561 |  |  | 19.6499 | 51.5627 | 507.5085 | 19.2375 | 53.0613 | 820.898 | 746.4336 | 627.7876 | 847.9886 | 835.6101 | 749.0176 |  | 813.9748 | 979.3022 | 1033.9977 | 607.3692 | 688.5503 | 996.6359 |  | 1051.4044 |  |  | 441.2524 | 647.9217 | 740.3281 | [6 empty] | 615.2422 |  |  | 424.6589 |  |  | 512.2952 | 666.3769 | 674.767 | 985.6116 | 1099.3925 | 1082.8039 | 518.7989 | 712.7938 | 836.1721 | 617.4009 | 701.4226 | 1076.5797 | 1128.8648 | 622.5378 | 809.3695 | 1115.2334 | 1164.1334 | 1095.8597 | 532.7705 | 660.7794 | 698.6108 | 539.3927 | 728.4233 | 865.2496 | 1134.6086 | 1160.1068 | 595.9929 | 711.2612 | 645.1634 | 847.9291 | 87.7081 | 0.0012989 | 17.9972 | 5.7104 | -40.1311 | 3.1218 | 9183.94 | 0.33 | 2.5278 | -1.9433 | 0.40823 | -1.8647 | 7.041 | 6.2863 | 6.7262 | 80.9999 | 167.0512 | 50.7551 | 74.5609 | 23.2599 | 66.0296 | 34.8651
42810.4525 | 1081 | 17.51 | 17.9413 | 18.0876 | 18.1297 | 17.4828 | 16.1212 | 14.9081 | 16.4598 | 16.9425 | 17.0874 | 17.1026 | 16.6303 | 15.6697 | 14.4097 | 22.6448 | 38.9048 | 38.2759 | 87.4433 | 38.4619 | 91.6539 |  |  |  | 30.1591 | 89.6403 | 410.6286 | 682.6342 | 715.4946 | 692.8215 | 91.4233 | 122.8633 | 900.2506 | 90.2084 | 117.2603 | 834.9932 | 739.3591 | 865.5385 |  | 258.5391 | 901.0522 | 898.8348 | 520.1984 |  | 466.3309 | 717.6889 | 558.1829 | 704.0994 | 892.6677 | 1022.7067 | 1052.7039 | 45.3943 | 416.977 | 78.8467 | 629.0919 | 14.1281 | 49.8855 | 48.1634 | 50.4705 | 62.4393 |  |  | 0.75787 | -1.092 | -0.21106 | -1.3057 | 7.0458 | 4.6644 | 6.7997 | -2.7476 | 20.1298 | 54.3254 | 24.9914 | 1.807e-05 | 8.214e-05 | -0.00078361 | 24.102 | 16.3318 | 16.7539 | 17.1379 | 17.1478 | 16.1313 | 14.6194 | 16.6595 | 17.042 | 17.3728 | 17.4401 | 17.1804 | 16.3715 | 14.6353 | 709.7641 | 482.1975 | 452.6803 | 288.46 | 239.8418 | 771.0002 | 486.828 | 18.2356 | 32.3184 | 38.1429 | 76.335 | 83.0333 | 86.576 |  |  |  | 611.78 | 579.5732 | 584.3559 | 606.0624 | 69.3934 | 27.4499 | 864.7727 |  |  | 571.4312 |  |  | 19.6728 | 51.6607 | 506.2155 | 19.2614 | 53.1923 | 818.4588 | 747.1185 | 628.3153 | 845.0461 | 833.2448 | 748.0438 |  | 813.976 | 976.8663 | 1032.5462 | 607.2935 | 689.1218 | 999.0711 |  | 1051.2273 |  |  | 440.3137 | 647.5364 | 739.6138 | [6 empty] | 615.5208 |  |  | 424.9751 |  |  | 512.5789 | 667.2636 | 675.9803 | 988.4936 | 1105.6381 | 1082.7477 | 518.2935 | 713.0117 | 839.0321 | 617.9813 | 702.8143 | 1075.6334 | 1133.0433 | 622.8724 | 809.5863 | 1117.4312 | 1163.7366 | 1091.4484 | 533.2252 | 661.6318 | 698.7369 | 540.0435 | 727.5237 | 865.5731 | 1141.8621 | 1157.0508 | 596.5935 | 710.9278 | 645.0446 | 846.739 | 86.1201 | 0.00087095 | 17.9866 | 5.7171 | -40.0868 | 3.1218 | 9260.14 | 0.38 | 1.8856 | -2.2924 | -1.0078 | -2.5066 | 6.659 | 5.4181 | 6.5417 | 81.0273 | 166.3445 | 50.8884 | 74.2001 | 22.7084 | 65.6785 | 34.9299
42810.4526 | 1082 | 17.5127 | 17.945 | 18.0876 | 18.1289 | 17.4829 | 16.1291 | 14.9107 | 16.464 | 16.9547 | 17.0947 | 17.1109 | 16.6456 | 15.6817 | 14.4131 | 22.7722 | 39.0939 | 38.4531 | 87.4795 | 38.6386 | 91.6712 |  |  |  | 30.309 | 89.6754 | 411.5835 | 682.6512 | 715.769 | 692.8272 | 81.0654 | 120.915 | 903.8383 | 93.2341 | 119.3804 | 832.9686 | 902.813 | 862.8655 |  | 250.2965 | 905.2007 | 905.9767 | 511.8216 |  | 466.695 | 719.6669 | 559.4745 | 704.2916 | 890.4551 | 1020.1057 | 1053.5616 | 45.1802 | 416.7098 | 81.8965 | 628.7362 | 14.1483 | 49.8475 | 48.1641 | 50.4889 | 62.6784 |  |  | 0.97341 | -0.54598 | -0.18214 | -0.7202 | 7.1509 | 4.8458 | 7.1809 | -2.9684 | 19.5886 | 52.4935 | 24.9908 | 8.543e-05 | 0.00012814 | -0.00079347 | 24.1577 | 16.3383 | 16.7419 | 17.1349 | 17.1481 | 16.131 | 14.6246 | 16.6549 | 17.0344 | 17.3748 | 17.4405 | 17.1781 | 16.376 | 14.6394 | 704.9899 | 478.8658 | 445.9947 | 286.4195 | 229.8457 | 769.2058 | 485.4507 | 18.2876 | 32.4348 | 38.2701 | 76.4729 | 83.0802 | 86.602 |  |  |  | 612.1971 | 578.43 | 582.9417 | 607.9948 | 76.7528 | 30.5776 | 860.907 |  |  | 568.6296 |  |  | 19.6939 | 51.7606 | 506.5092 | 19.2944 | 53.3033 | 818.4097 | 748.3733 | 630.1807 | 844.2192 | 832.8517 | 748.6439 |  | 814.2002 | 974.4318 | 1033.2081 | 607.3406 | 689.6515 | 1003.2094 |  | 1051.7396 |  |  | 440.2149 | 648.8442 | 741.2224 | [6 empty] | 616.8613 |  |  | 424.3217 |  |  | 513.2745 | 668.4473 | 677.3574 | 1001.2632 | 1113.3849 | 1087.4757 | 517.7587 | 713.0777 | 847.6526 | 619.3959 | 704.0678 | 1079.3956 | 1137.762 | 622.7253 | 811.4089 | 1121.2561 | 1165.8748 | 1093.5509 | 533.4299 | 662.0013 | 698.7174 | 540.9593 | 728.0831 | 869.7072 | 1140.8958 | 1157.2735 | 597.5283 | 710.7043 | 645.5525 | 849.5844 | 84.9445 | -0.0001603 | 17.9755 | 5.7209 | -40.1058 | 3.1218 | 9348.03 | 0.28 | 2.137 | -1.6225 | -0.93714 | -1.8635 | 6.7018 | 5.5168 | 6.7158 | 81.0822 | 166.765 | 51.009 | 74.0691 | 23.1614 | 119.2929 | 34.9535
42810.4526 | 1083 | 17.5093 | 17.9381 | 18.0883 | 18.1314 | 17.4782 | 16.1241 | 14.9095 | 16.4518 | 16.9455 | 17.0956 | 17.1096 | 16.6411 | 15.6761 | 14.4141 | 22.903 | 39.2778 | 38.6068 | 87.5323 | 38.833 | 91.7096 |  |  |  | 30.4744 | 89.6931 | 414.4564 | 683.4881 | 717.4978 | 692.929 | 87.7613 | 117.7234 | 902.7135 | 91.4263 | 122.0491 | 841.489 | 888.2918 | 869.1053 |  | 271.7983 | 899.3674 | 904.7736 | 494.1341 |  | 467.4894 | 720.1908 | 560.6968 | 702.4127 | 883.9735 | 1015.1017 | 1051.683 | 44.5195 | 416.5402 | 82.1374 | 628.3002 | 14.1747 | 49.8081 | 48.1675 | 50.5002 | 62.9108 |  |  | 0.52394 | 0.062515 | -0.44696 | -0.60126 | 7.8553 | 5.6363 | 7.1986 | -3.3482 | 19.9784 | 52.7775 | 26.6428 | 6.243e-05 | 5.093e-05 | -0.00078197 | 24.2198 | 16.3272 | 16.7518 | 17.1395 | 17.1427 | 16.1353 | 14.6288 | 16.6588 | 17.0346 | 17.3714 | 17.4415 | 17.1823 | 16.3739 | 14.6412 | 708.6357 | 476.8016 | 447.7542 | 282.116 | 225.1101 | 767.3198 | 483.9567 | 18.3279 | 32.5467 | 38.3823 | 76.602 | 83.1147 | 86.622 |  |  |  | 612.7539 | 577.397 | 582.2967 | 609.4536 | 69.6584 | 23.7785 | 859.9678 |  |  | 566.0827 |  |  | 19.7201 | 51.8506 | 509.2269 | 19.3251 | 53.4351 | 817.1235 | 746.6744 | 632.0041 | 843.4746 | 832.2813 | 745.9525 |  | 814.0614 | 972.327 | 1034.9133 | 609.2942 | 690.5144 | 1003.7835 |  | 1051.8887 |  |  | 439.9911 | 647.1224 | 740.7564 | [6 empty] | 619.2049 |  |  | 424.7045 |  |  | 514.0788 | 669.5502 | 678.5941 | 1003.8647 | 1114.2526 | 1087.2366 | 517.458 | 713.4 | 849.4392 | 620.7921 | 705.0474 | 1075.7902 | 1135.7625 | 622.9425 | 812.7452 | 1113.0861 | 1163.6968 | 1093.8281 | 533.6033 | 662.3065 | 699.0379 | 541.2718 | 728.8183 | 871.5773 | 1138.2461 | 1154.6447 | 598.4277 | 710.38 | 645.8852 | 848.776 | 86.3127 | -0.00014628 | 17.9646 | 5.7229 | -40.134 | 3.1218 | 9402.33 | 0.31 | 1.5679 | 0.54917 | -1.4684 | -1.7031 | 7.0105 | 5.9383 | 6.7111 | 81.1127 | 167.7347 | 51.1536 | 72.9714 | 22.6524 | 114.1235 | 35.0161
42810.4526 | 1084 | 17.502 | 17.9387 | 18.0833 | 18.1251 | 17.4768 | 16.1197 | 14.9108 | 16.4521 | 16.9466 | 17.0927 | 17.1066 | 16.6381 | 15.6705 | 14.4118 | 23.0279 | 39.4528 | 38.7656 | 87.5735 | 38.9444 | 91.7113 |  |  |  | 30.6346 | 89.7162 | 417.517 | 684.3218 | 718.981 | 692.8797 | 91.1128 | 119.2242 | 900.5872 | 84.9567 | 110.6492 | 836.9095 | 886.8528 | 862.3579 |  | 289.0684 | 893.3688 | 896.4985 | 522.1169 |  | 467.9431 | 721.7438 | 562.56 | 702.5852 | 886.1504 | 1017.3065 | 1051.4837 | 44.776 | 416.0984 | 79.7135 | 627.7257 | 14.185 | 49.7661 | 48.1796 | 50.4966 | 63.1542 |  |  | 1.0444 | 0.14334 | -0.26757 | -0.52832 | 7.9296 | 5.7454 | 7.3353 | -3.2424 | 19.9714 | 53.3096 | 25.8384 | 0.00012157 | 8.707e-05 | -0.00079511 | 24.291 | 16.3333 | 16.7489 | 17.1432 | 17.147 | 16.1416 | 14.6375 | 16.6687 | 17.0464 | 17.375 | 17.452 | 17.1898 | 16.3751 | 14.6481 | 696.4041 | 471.162 | 417.5088 | 263.5902 | 214.5983 | 765.0647 | 482.012 | 18.3793 | 32.6669 | 38.5043 | 76.7332 | 83.1576 | 86.6316 |  |  |  | 613.3128 | 577.1823 | 582.383 | 609.8591 | 75.584 | 27.8796 | 860.4088 |  |  | 564.9173 |  |  | 19.75 | 51.9512 | 512.7453 | 19.3501 | 53.5445 | 817.9779 | 745.2955 | 631.7395 | 843.8065 | 831.8938 | 743.9043 |  | 813.8712 | 973.1983 | 1036.496 | 609.56 | 691.1337 | 1003.2301 |  | 1051.544 |  |  | 439.8295 | 643.8367 | 738.2011 | [6 empty] | 619.4398 |  |  | 425.2827 |  |  | 514.0685 | 670.0345 | 678.9867 | 1007.9075 | 1115.6081 | 1085.3159 | 517.5856 | 713.5221 | 848.6519 | 621.2297 | 704.9535 | 1077.4935 | 1136.1764 | 623.0469 | 812.1062 | 1113.2231 | 1162.7591 | 1092.1953 | 533.9507 | 661.9965 | 699.3912 | 542.4213 | 729.1348 | 872.9755 | 1139.2168 | 1153.8575 | 599.3835 | 709.1979 | 646.1404 | 848.8008 | 90.1763 | -0.00032867 | 17.9543 | 5.7241 | -40.1014 | 3.1218 | 9438.95 | 0.31 | 2.2136 | 0.83222 | -1.137 | -1.5977 | 7.0496 | 6.0006 | 6.7803 | 81.1089 | 168.5593 | 51.2892 | 73.5056 | 25.6063 | 112.7958 | 35.1086
42810.4526 | 1085 | 17.5021 | 17.9333 | 18.0775 | 18.1279 | 17.4755 | 16.1216 | 14.9103 | 16.4529 | 16.9458 | 17.0925 | 17.1008 | 16.6422 | 15.6743 | 14.4167 | 23.167 | 39.6324 | 38.9328 | 87.6337 | 39.0686 | 91.7263 |  |  |  | 30.7985 | 89.731 | 419.9671 | 684.904 | 719.5332 | 693.7374 | 93.1983 | 116.5499 | 900.6366 | 82.9121 | 106.707 | 833.0917 | 891.6929 | 849.2888 |  | 297.2558 | 896.9859 | 896.3462 | 534.9899 |  | 469.01 | 722.8278 | 563.0174 | 708.407 | 892.1561 | 1019.7678 | 1051.7828 | 44.9468 | 415.7966 | 77.906 | 627.255 | 14.1897 | 49.7138 | 48.1908 | 50.4849 | 63.3938 |  |  | 0.93858 | -0.49603 | -0.73478 | -0.83717 | 7.233 | 5.9826 | 6.232 | -2.8757 | 19.7227 | 52.5203 | 24.2715 | 1.479e-05 | 0.00012814 | -0.00080004 | 24.3621 | 16.3458 | 16.7531 | 17.1422 | 17.1456 | 16.1407 | 14.633 | 16.6697 | 17.0417 | 17.3716 | 17.4465 | 17.1894 | 16.3859 | 14.6471 | 694.8898 | 474.575 | 423.2026 | 259.3584 | 212.1822 | 763.1692 | 480.5243 | 18.4281 | 32.775 | 38.6228 | 76.8518 | 83.1959 | 86.6572 |  |  |  | 613.7676 | 577.4265 | 581.8449 | 609.7479 | 57.3494 | 21.7273 | 860.8634 |  |  | 563.5804 |  |  | 19.775 | 52.0362 | 515.8248 | 19.3904 | 53.6676 | 818.7482 | 746.8655 | 629.5636 | 843.6456 | 831.3883 | 747.2321 |  | 814.1659 | 970.1728 | 1036.6921 | 607.7204 | 691.4116 | 1001.3559 |  | 1051.9176 |  |  | 440.3118 | 647.286 | 738.6593 | [6 empty] | 617.5581 |  |  | 424.1904 |  |  | 513.7729 | 669.5996 | 678.8103 | 1014.1916 | 1123.0875 | 1087.9288 | 517.9876 | 713.0835 | 849.9021 | 621.0019 | 704.4547 | 1083.8209 | 1139.4575 | 623.4097 | 812.1591 | 1115.0746 | 1167.1415 | 1090.4912 | 534.6378 | 661.4772 | 699.0426 | 543.0413 | 730.1913 | 872.9774 | 1142.5928 | 1153.2244 | 599.9874 | 707.9278 | 646.7132 | 850.7113 | 95.8046 | 0.00045002 | 17.9436 | 5.7245 | -39.9903 | 3.1218 | 9417.17 | 0.34 | 2.0994 | -1.549 | -1.8853 | -2.0123 | 6.7393 | 6.1291 | 6.2556 | 81.1105 | 168.7487 | 51.4046 | 72.9835 | 24.6635 | 114.2969 | 35.1962
42810.4526 | 1086 | 17.5056 | 17.9343 | 18.0885 | 18.1294 | 17.4781 | 16.1239 | 14.9159 | 16.4621 | 16.9457 | 17.0972 | 17.1072 | 16.6448 | 15.6763 | 14.417 | 23.3037 | 39.8092 | 39.0983 | 87.6706 | 39.2094 | 91.7366 |  |  |  | 30.9529 | 89.7265 | 421.8779 | 685.4906 | 719.7434 | 694.5877 | 78.4918 | 120.4019 | 906.1588 | 95.1266 | 119.0121 | 840.7473 | 903.8665 | 862.4018 |  | 284.7212 | 895.7638 | 903.0315 | 506.8791 |  | 469.5408 | 721.7279 | 562.9485 | 708.011 | 891.8086 | 1019.0253 | 1050.1704 | 43.6964 | 415.6222 | 76.4299 | 626.8627 | 14.1956 | 49.6363 | 48.2021 | 50.4721 | 63.4565 |  |  | 0.55614 | -0.3541 | -1.1159 | -0.73334 | 7.2206 | 5.2394 | 6.8589 | -2.7699 | 20.3713 | 53.7353 | 25.2533 | 7.064e-05 | 3.45e-05 | -0.00077211 | 24.4229 | 16.3436 | 16.7524 | 17.1381 | 17.1453 | 16.1312 | 14.6328 | 16.6655 | 17.0411 | 17.3816 | 17.4509 | 17.1959 | 16.3809 | 14.6506 | 673.9594 | 455.2086 | 382.6182 | 254.5609 | 208.6402 | 760.2281 | 478.6451 | 18.4795 | 32.8981 | 38.7597 | 76.9639 | 83.2224 | 86.6985 |  |  |  | 614.1935 | 577.7962 | 581.6187 | 609.7919 | 67.6006 | 23.8269 | 860.2673 |  |  | 562.2418 |  |  | 19.7948 | 52.1342 | 517.6054 | 19.4188 | 53.7899 | 818.0763 | 749.7799 | 629.5641 | 846.152 | 837.6401 | 752.0062 |  | 815.0822 | 967.1185 | 1036.3868 | 606.6762 | 691.7825 | 1002.063 |  | 1052.4154 |  |  | 441.0406 | 653.0627 | 741.833 | [6 empty] | 616.7931 |  |  | 422.5931 |  |  | 514.0159 | 669.2083 | 679.2001 | 1024.1379 | 1126.1961 | 1089.9323 | 518.384 | 713.6851 | 852.1311 | 620.5846 | 704.6796 | 1087.9399 | 1138.4064 | 623.9486 | 813.5313 | 1122.5236 | 1171.1376 | 1089.3063 | 535.7947 | 661.0303 | 699.1169 | 543.6136 | 731.172 | 873.0719 | 1147.2245 | 1152.2614 | 600.6134 | 707.5714 | 647.4123 | 850.9842 | 89.9166 | -0.0053095 | 17.9324 | 5.7232 | -40.0896 | 3.1218 | 9377.18 | 0.42 | 1.6167 | -1.308 | -2.322 | -1.8824 | 6.7315 | 5.7341 | 6.5608 | 81.2708 | 168.6695 | 51.5194 | 74.2431 | 28.7823 | 119.8486 | 35.2743
42810.4526 | 1087 | 17.5074 | 17.9384 | 18.0832 | 18.1331 | 17.4772 | 16.1276 | 14.9234 | 16.4535 | 16.9406 | 17.0903 | 17.1061 | 16.6419 | 15.674 | 14.4167 | 23.4306 | 39.9959 | 39.2707 | 87.711 | 39.3723 | 91.7532 |  |  |  | 31.1153 | 89.7372 | 423.6984 | 686.508 | 720.7014 | 695.6448 | 93.0352 | 121.9116 | 903.5901 | 96.4309 | 124.743 | 845.8177 | 906.3522 | 867.5362 |  | 295.2653 | 888.4126 | 893.9995 | 529.3249 |  | 467.7801 | 718.1951 | 562.5117 | 708.5665 | 884.6497 | 1019.0593 | 1049.9622 | 42.5037 | 415.7922 | 73.3465 | 626.4452 | 14.2088 | 49.5832 | 48.2305 | 50.4656 | 63.2747 |  |  | 1.1659 | -0.28576 | -0.6533 | -0.41135 | 6.9735 | 5.813 | 7.7322 | -3.0413 | 20.031 | 51.6226 | 26.0872 | 7.721e-05 | 0.00015114 | -0.00077704 | 24.4776 | 16.3406 | 16.7507 | 17.1444 | 17.1429 | 16.1373 | 14.6317 | 16.6568 | 17.0389 | 17.3744 | 17.449 | 17.183 | 16.3785 | 14.6527 | 667.6174 | 453.0102 | 375.3075 | 256.4378 | 214.727 | 757.2625 | 476.8154 | 18.5358 | 33.0127 | 38.8784 | 77.0998 | 83.2605 | 86.7176 |  |  |  | 614.723 | 577.5203 | 581.4107 | 611.3086 | 55.15 | 22.3815 | 863.5823 |  |  | 563.9058 |  |  | 19.8249 | 52.2224 | 519.311 | 19.4562 | 53.8891 | 815.5771 | 750.9521 | 629.4489 | 849.9371 | 841.353 | 755.1212 |  | 815.9328 | 969.4698 | 1038.0163 | 607.2578 | 692.4772 | 1005.6214 |  | 1053.8668 |  |  | 441.8663 | 657.4174 | 744.2786 | [6 empty] | 617.1193 |  |  | 420.8572 |  |  | 514.3196 | 669.0919 | 680.1176 | 1026.8043 | 1125.5897 | 1089.9123 | 518.6392 | 715.0825 | 852.1342 | 620.2337 | 704.7351 | 1087.8317 | 1137.797 | 624.3286 | 815.1984 | 1125.8064 | 1172.5261 | 1089.5811 | 536.7875 | 660.8926 | 699.7574 | 543.5932 | 731.078 | 874.2392 | 1149.1353 | 1153.8056 | 600.9471 | 708.6312 | 647.7331 | 850.0925 | 89.2165 | -0.0015564 | 17.9219 | 5.7217 | -40.0488 | 3.1218 | 9315.14 | 0.29 | 2.3422 | -1.1729 | -1.7735 | -1.4073 | 6.6154 | 6.04 | 6.966 | 81.4568 | 169.481 | 51.6643 | 73.8792 | 29.2156 | 120.2163 | 35.3308
42810.4526 | 1088 | 17.4945 | 17.9375 | 18.0799 | 18.1246 | 17.4689 | 16.119 | 14.9254 | 16.4563 | 16.945 | 17.087 | 17.1023 | 16.6372 | 15.6686 | 14.4099 | 23.5651 | 40.1693 | 39.433 | 87.7504 | 39.5153 | 91.7657 |  |  |  | 31.2808 | 89.7511 | 425.5336 | 687.4813 | 721.0707 | 696.32 | 91.7729 | 114.8548 | 892.2663 | 85.6854 | 117.8463 | 843.4054 | 871.0998 | 872.442 |  | 267.9148 | 897.5641 | 894.2637 | 527.4602 |  | 466.5511 | 716.8891 | 564.8933 | 708.0147 | 884.1098 | 1017.6378 | 1048.8204 | 42.3593 | 415.862 | 70.5527 | 626.3487 | 14.2254 | 49.5563 | 48.2511 | 50.4672 | 62.945 |  |  | 0.73488 | -0.26342 | -0.2196 | -0.53161 | 7.944 | 6.6515 | 8.5667 | -3.3718 | 19.7867 | 52.9475 | 28.6286 | 7.721e-05 | 5.421e-05 | -0.00077047 | 24.548 | 16.3507 | 16.7533 | 17.148 | 17.1398 | 16.1405 | 14.6332 | 16.6671 | 17.0473 | 17.3759 | 17.4462 | 17.1885 | 16.3776 | 14.6536 | 659.5408 | 452.2563 | 390.2224 | 258.4774 | 218.3339 | 753.8984 | 474.7165 | 18.5772 | 33.1182 | 38.9803 | 77.2182 | 83.3138 | 86.7384 |  |  |  | 615.5171 | 578.6496 | 582.5121 | 615.7362 | 69.8474 | 25.5216 | 866.6022 |  |  | 574.5551 |  |  | 19.848 | 52.3131 | 521.5078 | 19.4825 | 54.0042 | 815.4535 | 749.6478 | 628.9233 | 847.1244 | 833.3137 | 753.4807 |  | 816.097 | 964.0462 | 1040.6323 | 605.7201 | 692.8466 | 1002.5632 |  | 1054.2578 |  |  | 442.4128 | 657.4489 | 743.9395 | [6 empty] | 616.1956 |  |  | 418.56 |  |  | 514.7442 | 669.2976 | 680.9143 | 1028.7582 | 1126.3738 | 1086.8098 | 518.7908 | 716.632 | 851.3703 | 620.4687 | 705.2628 | 1085.6221 | 1135.3106 | 624.839 | 815.5313 | 1119.6999 | 1174.2915 | 1092.0812 | 537.4638 | 661.5093 | 700.6665 | 543.3431 | 730.9001 | 873.6553 | 1148.8698 | 1156.9846 | 601.4541 | 709.8891 | 647.9951 | 848.5493 | 94.4427 | -0.0010442 | 17.9131 | 5.7213 | -40.0723 | 3.1218 | 9275.98 | 0.27 | 1.8601 | -1.1254 | -1.0276 | -1.5988 | 7.0569 | 6.4574 | 7.3283 | 81.5551 | 171.0457 | 51.7927 | 73.5722 | 27.1252 | 106.7456 | 35.3561
42810.4526 | 1089 | 17.4947 | 17.9331 | 18.075 | 18.1246 | 17.4698 | 16.1244 | 14.9361 | 16.4557 | 16.9491 | 17.0853 | 17.1061 | 16.6372 | 15.676 | 14.4153 | 23.7048 | 40.3549 | 39.6027 | 87.7967 | 39.6841 | 91.7805 |  |  |  | 31.4464 | 89.7739 | 426.0433 | 687.1003 | 720.0035 | 695.2538 | 87.0495 | 122.3606 | 901.8553 | 91.6118 | 118.8525 | 836.4299 | 905.0212 | 866.0826 |  | 254.2321 | 901.8205 | 900.9666 | 506.6358 |  | 467.4155 | 716.7243 | 567.8507 | 709.1729 | 885.0711 | 1020.038 | 1049.4107 | 42.0878 | 415.9105 | 68.855 | 626.7725 | 14.2521 | 49.5297 | 48.2659 | 50.4899 | 62.5537 |  |  | 0.42734 | -0.010425 | -0.284 | -0.66829 | 7.7732 | 6.2487 | 8.0601 | -3.4145 | 20.5515 | 52.8237 | 25.1289 | 6.243e-05 | 5.093e-05 | -0.00077375 | 24.6167 | 16.3554 | 16.7515 | 17.1466 | 17.146 | 16.143 | 14.6386 | 16.6682 | 17.0466 | 17.3806 | 17.454 | 17.1965 | 16.386 | 14.6572 | 674.2703 | 458.0758 | 406.4893 | 265.1722 | 223.0753 | 751.9023 | 473.1239 | 18.6358 | 33.2484 | 39.1263 | 77.3565 | 83.3493 | 86.7565 |  |  |  | 616.3347 | 580.3332 | 583.2985 | 615.5061 | 90.7099 | 31.1592 | 860.3272 |  |  | 577.0071 |  |  | 19.8674 | 52.4147 | 521.8105 | 19.5211 | 54.1331 | 815.6365 | 749.9208 | 627.4081 | 840.1113 | 824.1292 | 751.269 |  | 816.6081 | 949.7881 | 1042.0229 | 604.03 | 693.1625 | 995.9551 |  | 1053.7278 |  |  | 442.1304 | 654.4855 | 742.8531 | [6 empty] | 614.7741 |  |  | 417.5346 |  |  | 515.3655 | 669.9486 | 681.7818 | 1036.2439 | 1127.5492 | 1084.2436 | 519.2522 | 716.9145 | 850.1066 | 620.7546 | 705.9024 | 1081.8111 | 1134.1778 | 625.1501 | 815.012 | 1110.8831 | 1174.1905 | 1091.4609 | 538.3019 | 662.6325 | 701.2321 | 543.8302 | 731.5022 | 871.419 | 1143.0731 | 1156.9012 | 602.4101 | 710.2047 | 648.7684 | 848.9984 | 98.4436 | 0.00019044 | 17.9054 | 5.7196 | -40.0257 | 3.1218 | 9220.1 | 0.29 | 1.4177 | -0.22387 | -1.1685 | -1.7924 | 6.9871 | 6.2646 | 7.1149 | 81.7806 | 172.1967 | 51.9131 | 71.2247 | 24.9902 | 120.3151 | 35.5155
42810.4527 | 1090 | 17.4958 | 17.9365 | 18.0784 | 18.1199 | 17.4649 | 16.1191 | 14.9328 | 16.4498 | 16.9509 | 17.0848 | 17.1062 | 16.6465 | 15.6746 | 14.4137 | 23.8369 | 40.534 | 39.7605 | 87.8363 | 39.9017 | 91.7831 |  |  |  | 31.607 | 89.7723 | 426.3856 | 686.2907 | 719.054 | 693.8738 | 87.9972 | 120.8551 | 902.2287 | 93.7144 | 123.3668 | 842.3109 | 861.3812 | 868.4435 |  | 278.4285 | 906.526 | 908.249 | 492.0636 |  | 467.3295 | 717.2276 | 567.8052 | 709.8151 | 892.1249 | 1021.3905 | 1048.3979 | 42.5212 | 416.041 | 69.5014 | 627.1745 | 14.2521 | 49.4872 | 48.2679 | 50.5288 | 62.2354 |  |  | 1.1686 | -0.39484 | -0.89314 | -0.59272 | 7.0418 | 5.447 | 7.4733 | -3.1208 | 19.9119 | 53.0318 | 24.1884 | 0.00012321 | 5.257e-05 | -0.00079182 | 24.671 | 16.3508 | 16.7374 | 17.1307 | 17.1349 | 16.1306 | 14.6296 | 16.655 | 17.0387 | 17.3763 | 17.4481 | 17.1881 | 16.3753 | 14.6449 | 718.6942 | 478.9603 | 434.4208 | 269.0262 | 219.0847 | 752.3338 | 472.066 | 18.6837 | 33.3708 | 39.2427 | 77.4703 | 83.3924 | 86.7715 |  |  |  | 616.6586 | 579.374 | 582.1953 | 611.7225 | 82.2905 | 31.4836 | 853.7934 |  |  | 577.5799 |  |  | 19.8877 | 52.4926 | 521.4783 | 19.535 | 54.2398 | 819.4778 | 752.9106 | 624.9543 | 834.6939 | 817.123 | 755.6092 |  | 817.9571 | 941.4023 | 1044.2843 | 601.8119 | 693.4331 | 996.9145 |  | 1054.4995 |  |  | 442.7128 | 656.9685 | 744.9008 | [6 empty] | 612.587 |  |  | 417.3509 |  |  | 515.5271 | 670.3333 | 682.306 | 1036.4824 | 1128.0376 | 1084.9402 | 519.8659 | 716.1929 | 850.2958 | 620.3306 | 705.9403 | 1081.551 | 1134.9077 | 625.4834 | 814.7803 | 1101.5003 | 1170.1436 | 1089.1775 | 538.7919 | 663.7024 | 701.3183 | 545.1721 | 733.4279 | 871.2443 | 1135.2403 | 1155.0472 | 603.4005 | 710.3973 | 650.2364 | 852.0703 | 98.9556 | -0.00040586 | 17.8978 | 5.7182 | -40.1488 | 3.1218 | 9184.01 | 0.38 | 2.3427 | -1.3781 | -2.0727 | -1.6885 | 6.6538 | 5.852 | 6.8546 | 82.0942 | 173.6622 | 52.0376 | 66.4422 | 21.6697 | 104.1984 | 35.6814
42810.4527 | 1091 | 17.495 | 17.9353 | 18.078 | 18.1236 | 17.4689 | 16.1209 | 14.932 | 16.4499 | 16.9432 | 17.0885 | 17.1057 | 16.6444 | 15.6712 | 14.418 | 23.9633 | 40.7168 | 39.9244 | 87.8854 | 40.0651 | 91.8117 |  |  |  | 31.7692 | 89.7417 | 428.5672 | 687.1259 | 720.2246 | 694.8772 | 95.9135 | 124.1515 | 903.3437 | 91.74 | 121.1166 | 842.4175 | 845.3845 | 875.0349 |  | 257.8279 | 906.8795 | 905.568 | 508.4125 |  | 468.0023 | 715.7944 | 567.3975 | 710.4897 | 886.397 | 1016.4927 | 1047.1727 | 42.6838 | 416.1116 | 71.4418 | 627.2521 | 14.2019 | 49.4374 | 48.2638 | 50.5584 | 62.038 |  |  | 1.2547 | -0.15762 | -0.086204 | -0.87462 | 8.0893 | 6.2803 | 7.1434 | -2.9881 | 19.6976 | 52.0296 | 24.2492 | 8.214e-05 | 0.0001035 | -0.00081811 | 24.7452 | 16.3446 | 16.7499 | 17.1327 | 17.1352 | 16.1411 | 14.633 | 16.661 | 17.0352 | 17.3731 | 17.4489 | 17.1819 | 16.3788 | 14.6472 | 732.0714 | 480.5913 | 430.2236 | 264.7556 | 216.3558 | 752.0825 | 471.1462 | 18.7416 | 33.477 | 39.3657 | 77.5761 | 83.4305 | 86.8022 |  |  |  | 617.0618 | 579.4557 | 582.1104 | 612.7963 | 63.02 | 25.4161 | 847.8405 |  |  | 577.5481 |  |  | 19.923 | 52.5945 | 522.5841 | 19.5896 | 54.3727 | 820.2154 | 757.364 | 623.76 | 827.6999 | 808.3085 | 760.1696 |  | 819.5614 | 932.5223 | 1045.9442 | 599.7608 | 693.5383 | 994.3377 |  | 1054.9687 |  |  | 444.6694 | 662.6263 | 749.0832 | [6 empty] | 610.9253 |  |  | 415.8502 |  |  | 515.0958 | 670.4933 | 682.4709 | 1034.3051 | 1127.9096 | 1086.4324 | 520.3127 | 716.4671 | 851.6726 | 620.0608 | 705.5984 | 1081.486 | 1134.9102 | 626.1913 | 816.3065 | 1098.6395 | 1162.1654 | 1086.1774 | 539.3471 | 664.7644 | 702.0595 | 545.9908 | 735.0639 | 873.3901 | 1132.7847 | 1157.9379 | 603.985 | 711.9531 | 651.2888 | 854.292 | 95.9564 | -0.00035675 | 17.8884 | 5.7095 | -40.0884 | 3.1218 | 9160.52 | 0.37 | 2.4287 | -0.87008 | -0.64345 | -2.0496 | 7.118 | 6.2718 | 6.6889 | 82.4858 | 174.8174 | 52.119 | 64.8664 | 21.9477 | 98.1128 | 35.7272
42810.4527 | 1092 | 17.4911 | 17.937 | 18.0809 | 18.1219 | 17.4743 | 16.1179 | 14.9336 | 16.4497 | 16.9418 | 17.0881 | 17.1054 | 16.6455 | 15.6698 | 14.4181 | 24.1042 | 40.8965 | 40.092 | 87.9174 | 40.238 | 91.8467 |  |  |  | 31.9319 | 89.7275 | 434.2934 | 689.5453 | 723.0118 | 697.5468 | 96.6427 | 127.4596 | 906.5629 | 93.125 | 120.1648 | 844.1632 | 901.5107 | 874.3497 |  | 247.5392 | 908.6221 | 908.5612 | 516.5165 |  | 468.7471 | 716.1091 | 567.1618 | 712.2579 | 889.1529 | 1016.2589 | 1046.5232 | 41.9346 | 416.0737 | 72.884 | 627.0328 | 14.1912 | 49.3671 | 48.2503 | 50.5847 | 61.9533 |  |  | 0.87221 | -0.69711 | -0.65658 | -1.4115 | 8.0321 | 5.5193 | 7.6205 | -3.3975 | 19.4732 | 50.5113 | 23.8133 | 3.45e-05 | 4.271e-05 | -0.00081318 | 24.8096 | 16.3478 | 16.7423 | 17.133 | 17.1316 | 16.1261 | 14.6305 | 16.6648 | 17.0297 | 17.3778 | 17.4443 | 17.1816 | 16.3773 | 14.6495 | 711.609 | 468.3749 | 414.0872 | 260.5433 | 216.7563 | 750.508 | 469.8485 | 18.79 | 33.585 | 39.4757 | 77.6625 | 83.461 | 86.8336 |  |  |  | 617.7093 | 581.1345 | 583.449 | 615.588 | 67.6466 | 26.007 | 840.0104 |  |  | 575.3891 |  |  | 19.9646 | 52.6872 | 527.8017 | 19.6393 | 54.4738 | 820.5741 | 759.6551 | 623.6956 | 821.8167 | 801.8615 | 762.7281 |  | 821.3963 | 925.1423 | 1048.4451 | 598.7937 | 693.5812 | 997.0662 |  | 1054.8923 |  |  | 445.9724 | 663.3085 | 752.9146 | [6 empty] | 610.2571 |  |  | 414.1017 |  |  | 515.2421 | 670.6677 | 682.612 | 1025.9195 | 1123.3106 | 1086.1855 | 521.2965 | 717.0028 | 852.2676 | 620.572 | 705.6144 | 1081.9584 | 1129.9536 | 626.7326 | 818.4258 | 1102.0918 | 1159.7254 | 1088.5012 | 540.2493 | 666.0368 | 703.2165 | 546.0721 | 735.4512 | 874.3036 | 1123.4323 | 1160.4256 | 604.1634 | 713.4145 | 651.8092 | 853.3193 | 86.3158 | 0.00040091 | 17.8794 | 5.6981 | -40.1393 | 3.1217 | 9192.55 | 0.31 | 2.0278 | -1.8301 | -1.7761 | -2.6041 | 7.0921 | 5.879 | 6.908 | 83.01 | 176.3974 | 52.1559 | 66.5812 | 23.4753 | 118.6468 | 35.7714
42810.4527 | 1093 | 17.4929 | 17.9307 | 18.0798 | 18.115 | 17.4715 | 16.1155 | 14.9464 | 16.4535 | 16.9427 | 17.09 | 17.1021 | 16.6427 | 15.6737 | 14.4098 | 24.2533 | 41.078 | 40.2596 | 87.9674 | 40.4585 | 91.8557 |  |  |  | 32.1011 | 89.7273 | 436.2069 | 690.5721 | 723.8387 | 698.1127 | 93.8245 | 129.8854 | 915.7573 | 96.1178 | 123.0019 | 849.7031 | 911.3566 | 872.2598 |  | 279.6622 | 908.4296 | 910.4632 | 515.201 |  | 468.3441 | 715.5593 | 567.4998 | 710.8818 | 883.737 | 1012.2783 | 1043.3033 | 40.5429 | 416.0923 | 75.3908 | 626.8172 | 14.2031 | 49.3394 | 48.227 | 50.599 | 61.9761 |  |  | 0.81504 | -0.40733 | -0.19134 | -0.7616 | 8.4625 | 5.8183 | 7.8735 | -2.8054 | 19.6176 | 52.6282 | 24.2735 | 5.257e-05 | 1.15e-05 | -0.00076225 | 24.8838 | 16.3594 | 16.7476 | 17.1392 | 17.1421 | 16.135 | 14.6285 | 16.6683 | 17.0374 | 17.3793 | 17.4457 | 17.193 | 16.3824 | 14.6544 | 698.7324 | 456.3124 | 404.42 | 247.9414 | 209.5333 | 748.5288 | 468.3185 | 18.8504 | 33.7059 | 39.5953 | 77.7637 | 83.5003 | 86.8702 |  |  |  | 618.3362 | 582.6575 | 584.7466 | 615.1362 | 62.661 | 25.9016 | 833.891 |  |  | 573.2784 |  |  | 19.9731 | 52.7648 | 531.3593 | 19.6605 | 54.5801 | 822.9449 | 757.1663 | 623.7708 | 814.8092 | 795.0044 | 756.9609 |  | 822.7727 | 918.6062 | 1050.8153 | 599.6111 | 693.7041 | 995.1527 |  | 1053.6577 |  |  | 445.1593 | 657.3751 | 752.2475 | [6 empty] | 610.7123 |  |  | 415.5425 |  |  | 515.9546 | 670.846 | 683.3469 | 1012.7254 | 1117.8396 | 1081.8996 | 522.6611 | 717.5491 | 851.5829 | 620.8729 | 706.4172 | 1078.1137 | 1120.2613 | 627.6074 | 819.2476 | 1104.1189 | 1153.5147 | 1092.6243 | 540.3345 | 666.9418 | 704.108 | 546.8885 | 736.2852 | 875.9438 | 1117.7261 | 1162.2745 | 604.4685 | 713.9966 | 652.5227 | 854.8901 | 88.4404 | -0.00087586 | 17.8697 | 5.677 | -40.138 | 3.1217 | 9224.71 | 0.29 | 1.9608 | -1.3985 | -0.95853 | -1.9123 | 7.2684 | 6.0268 | 7.0109 | 83.6186 | 177.889 | 52.1618 | 67.3119 | 24.2376 | 122.622 | 35.902
42810.4527 | 1094 | 17.491 | 17.9276 | 18.0735 | 18.118 | 17.4638 | 16.1146 | 14.9489 | 16.4568 | 16.9397 | 17.0914 | 17.1045 | 16.6369 | 15.6762 | 14.414 | 24.3801 | 41.2522 | 40.431 | 88.0183 | 40.6521 | 91.8717 |  |  |  | 32.2686 | 89.7026 | 437.9559 | 690.8611 | 723.7965 | 698.0581 | 92.8583 | 126.884 | 916.0688 | 99.6246 | 127.4785 | 854.2278 | 894.5432 | 879.1955 |  | 273.1663 | 910.2699 | 906.8179 | 520.8051 |  | 467.9933 | 715.3806 | 567.2053 | 712.5846 | 882.4608 | 1009.5118 | 1041.6362 | 40.4278 | 416.2619 | 76.7041 | 626.7314 | 14.1637 | 49.3676 | 48.2021 | 50.5993 | 62.0358 |  |  | 1.0877 | -0.15105 | -0.10526 | -1.0323 | 7.6477 | 6.1521 | 7.9747 | -2.7896 | 19.8932 | 53.8798 | 23.6045 | -6.57e-06 | 5.093e-05 | -0.00078197 | 24.9554 | 16.3686 | 16.7514 | 17.1467 | 17.1471 | 16.135 | 14.6354 | 16.67 | 17.041 | 17.3832 | 17.4519 | 17.1953 | 16.3868 | 14.658 | 687.7226 | 456.0384 | 413.1361 | 245.9858 | 203.4662 | 746.794 | 467.0889 | 18.9013 | 33.8255 | 39.7362 | 77.8777 | 83.5332 | 86.8879 |  |  |  | 618.7569 | 582.4982 | 584.4898 | 613.0768 | 79.481 | 28.2727 | 828.0697 |  |  | 571.8527 |  |  | 20.012 | 52.8552 | 532.8007 | 19.7019 | 54.6941 | 822.2819 | 753.8397 | 623.7599 | 811.2275 | 791.4407 | 750.6761 |  | 823.1471 | 913.1816 | 1049.759 | 600.4179 | 693.9947 | 988.156 |  | 1052.4489 |  |  | 444.6318 | 652.5461 | 747.9491 | [6 empty] | 611.4247 |  |  | 417.1113 |  |  | 516.6291 | 670.9234 | 684.052 | 1000.5727 | 1112.2556 | 1079.6826 | 523.3057 | 719.2779 | 851.4758 | 621.233 | 706.7835 | 1068.2628 | 1113.5345 | 628.1107 | 821.158 | 1098.3877 | 1149.9082 | 1097.5949 | 540.4685 | 667.568 | 704.6299 | 547.4079 | 737.6766 | 876.7174 | 1119.4848 | 1162.2182 | 604.9848 | 714.2105 | 653.5673 | 855.0602 | 91.364 | 0.0019092 | 17.861 | 5.6665 | -40.0341 | 3.1217 | 9197.37 | 0.29 | 2.2651 | -0.85157 | -0.71088 | -2.2262 | 6.9022 | 6.1906 | 7.0482 | 83.9154 | 177.4551 | 52.207 | 67.9239 | 23.0191 | 115.7956 | 36.0385
42810.4527 | 1095 | 17.4929 | 17.9285 | 18.0719 | 18.1128 | 17.4665 | 16.1141 | 14.9387 | 16.4451 | 16.9396 | 17.0757 | 17.0964 | 16.6326 | 15.6722 | 14.4072 | 24.535 | 41.4534 | 40.6006 | 88.0654 | 40.8432 | 91.8712 |  |  |  | 32.4584 | 89.6679 | 438.9067 | 690.6613 | 723.5966 | 698.2252 | 94.8477 | 122.8134 | 907.8545 | 95.835 | 126.685 | 856.5029 | 761.6418 | 883.778 |  | 259.8263 | 909.5563 | 910.6619 | 528.2462 |  | 469.2286 | 716.2454 | 566.572 | 712.8944 | 889.5067 | 1013.6371 | 1043.8168 | 40.803 | 416.3403 | 75.4735 | 626.6003 | 14.134 | 49.3875 | 48.1857 | 50.6017 | 62.1388 |  |  | 1.0799 | -0.26145 | -0.50019 | -1.0507 | 8.2825 | 5.8656 | 7.0278 | -2.6076 | 19.4925 | 52.8715 | 23.4107 | 1.314e-05 | 9.528e-05 | -0.00079675 | 25.0139 | 16.3529 | 16.7413 | 17.1312 | 17.1327 | 16.1259 | 14.6292 | 16.6615 | 17.0394 | 17.3802 | 17.448 | 17.1899 | 16.3823 | 14.6576 | 693.0799 | 467.4592 | 429.5125 | 253.6904 | 206.013 | 746.2999 | 466.2774 | 18.951 | 33.9366 | 39.8503 | 77.9654 | 83.5667 | 86.9168 |  |  |  | 619.1346 | 582.027 | 584.1516 | 613.1078 | 78.385 | 36.8998 | 825.1814 |  |  | 571.6254 |  |  | 20.0303 | 52.9607 | 533.2343 | 19.7566 | 54.7997 | 824.5348 | 752.5992 | 623.5166 | 808.4718 | 787.2492 | 748.473 |  | 823.5895 | 905.8652 | 1049.1745 | 600.4868 | 694.2561 | 989.5112 |  | 1052.8633 |  |  | 445.0036 | 648.8317 | 745.353 | [6 empty] | 611.0287 |  |  | 417.3396 |  |  | 517.2672 | 670.702 | 684.1111 | 983.0297 | 1104.9576 | 1079.783 | 523.4591 | 721.1917 | 852.1737 | 621.8018 | 706.1408 | 1061.1764 | 1108.5016 | 628.3294 | 822.0831 | 1103.3407 | 1149.1677 | 1102.9324 | 540.3067 | 667.9603 | 704.5326 | 548.7511 | 739.0774 | 877.9484 | 1121.9796 | 1164.7551 | 605.325 | 714.6545 | 654.8503 | 857.7133 | 90.0817 | 7.8201e-05 | 17.8525 | 5.653 | -39.9986 | 3.1217 | 9162.15 | 0.29 | 2.2571 | -1.1208 | -1.5503 | -2.247 | 7.1945 | 6.0545 | 6.6272 | 84.1212 | 177.3353 | 52.266 | 67.1549 | 21.0348 | 71.4954 | 36.1089
42810.4527 | 1096 | 17.4897 | 17.9247 | 18.0688 | 18.1173 | 17.4659 | 16.1171 | 14.9534 | 16.4476 | 16.9373 | 17.0826 | 17.0953 | 16.6386 | 15.6662 | 14.4168 | 24.6675 | 41.6218 | 40.762 | 88.0872 | 41.063 | 91.8656 |  |  |  | 32.6152 | 89.6201 | 441.6089 | 691.499 | 724.7385 | 699.5152 | 92.3794 | 124.8032 | 916.2245 | 91.564 | 118.2849 | 850.9345 | 887.7238 | 882.7063 |  | 244.8416 | 914.5503 | 913.487 | 536.8887 |  | 470.8167 | 716.7832 | 567.8063 | 712.6125 | 893.8589 | 1016.4096 | 1044.782 | 41.8898 | 416.3228 | 75.2633 | 626.6032 | 14.1905 | 49.3634 | 48.192 | 50.5974 | 62.3466 |  |  | 0.56337 | 0.038859 | -0.38585 | -1.1007 | 8.0262 | 5.6258 | 7.5272 | -2.8698 | 20.0952 | 53.246 | 26.0381 | 5.914e-05 | -8.21e-06 | -0.00077704 | 25.0737 | 16.3444 | 16.7433 | 17.1313 | 17.1318 | 16.1316 | 14.6313 | 16.6616 | 17.0432 | 17.3797 | 17.4496 | 17.1833 | 16.3861 | 14.654 | 712.0571 | 480.5608 | 447.1009 | 269.9907 | 217.8251 | 745.9983 | 465.7572 | 19.0071 | 34.0467 | 39.9602 | 78.0509 | 83.5891 | 86.9453 |  |  |  | 619.6312 | 584.0006 | 585.8765 | 615.1541 | 66.7695 | 26.2637 | 820.7244 |  |  | 569.168 |  |  | 20.0477 | 53.0446 | 535.4225 | 19.7847 | 54.9117 | 828.0167 | 751.8232 | 624.5959 | 802.732 | 780.8272 | 747.3148 |  | 823.96 | 901.727 | 1050.7724 | 601.5191 | 694.596 | 994.8237 |  | 1053.6519 |  |  | 445.1994 | 647.9034 | 744.8913 | [6 empty] | 612.7059 |  |  | 419.3534 |  |  | 518.1056 | 670.6147 | 683.9239 | 982.3854 | 1097.1891 | 1079.6017 | 523.7521 | 722.3727 | 852.0701 | 621.8838 | 706.2774 | 1063.6941 | 1102.535 | 628.8094 | 822.0488 | 1101.4892 | 1152.5585 | 1109.0133 | 539.2099 | 668.041 | 704.894 | 548.2906 | 740.618 | 879.206 | 1125.8132 | 1166.8793 | 604.8953 | 714.9213 | 655.8127 | 858.7318 | 86.6035 | -4.1051e-05 | 17.8437 | 5.6337 | -40.0555 | 3.1217 | 9086.63 | 0.34 | 1.6313 | 0.43223 | -1.362 | -2.3004 | 7.0899 | 5.9358 | 6.866 | 84.2745 | 178.3342 | 52.3166 | 64.9404 | 18.9751 | 112.7184 | 36.146
42810.4527 | 1097 | 17.4843 | 17.919 | 18.0686 | 18.1139 | 17.4633 | 16.1146 | 14.9473 | 16.4525 | 16.9368 | 17.0895 | 17.1007 | 16.639 | 15.6664 | 14.4187 | 24.808 | 41.7994 | 40.9317 | 88.1029 | 41.3289 | 91.8776 |  |  |  | 32.7893 | 89.5823 | 444.5806 | 692.4685 | 725.6934 | 700.2175 | 88.8492 | 122.8508 | 914.5222 | 93.966 | 124.5968 | 848.4445 | 857.3911 | 875.8042 |  | 244.7503 | 916.6646 | 917.2061 | 510.1588 |  | 470.0642 | 716.7534 | 569.7302 | 716.848 | 896.5064 | 1017.5986 | 1045.3526 | 43.788 | 416.2189 | 73.6238 | 626.345 | 14.2378 | 49.3045 | 48.2218 | 50.5872 | 62.5456 |  |  | 0.41946 | -0.15631 | -0.76303 | -0.84505 | 8.4395 | 5.7736 | 8.1146 | -3.3166 | 20.0913 | 52.5245 | 23.5017 | 4.6e-05 | 4.6e-05 | -0.0007639 | 25.1405 | 16.3419 | 16.7383 | 17.1278 | 17.1304 | 16.1332 | 14.6304 | 16.6661 | 17.0401 | 17.3716 | 17.4432 | 17.1862 | 16.3844 | 14.655 | 699.6403 | 465.0846 | 410.5912 | 266.0453 | 214.7306 | 744.0893 | 464.4268 | 19.0683 | 34.1649 | 40.0769 | 78.1536 | 83.6324 | 86.9831 |  |  |  | 620.1889 | 586.0972 | 588.6806 | 617.2044 | 52.2163 | 18.9971 | 814.7039 |  |  | 567.3578 |  |  | 20.0834 | 53.1476 | 538.7367 | 19.8313 | 55.0341 | 827.5874 | 751.0464 | 626.1423 | 798.0981 | 775.9288 | 745.8908 |  | 824.3736 | 899.916 | 1051.7511 | 603.0732 | 695.207 | 998.0774 |  | 1051.5447 |  |  | 444.8298 | 647.2375 | 744.1403 | [6 empty] | 614.0685 |  |  | 421.0321 |  |  | 518.828 | 671.0347 | 683.865 | 982.3237 | 1097.7662 | 1077.5764 | 523.9498 | 722.8407 | 851.2939 | 622.2337 | 706.4033 | 1063.0286 | 1103.5775 | 629.5912 | 820.4094 | 1104.3121 | 1156.2301 | 1109.101 | 539.4457 | 667.8011 | 704.8906 | 548.5306 | 741.5646 | 879.1401 | 1129.3022 | 1165.2678 | 604.6574 | 714.404 | 656.7538 | 857.5134 | 88.2969 | 0.00021853 | 17.8363 | 5.6152 | -40.1649 | 3.1217 | 9012.35 | 0.24 | 1.4082 | -0.86686 | -1.9153 | -2.0156 | 7.2735 | 6.0161 | 7.1322 | 84.4495 | 178.9273 | 52.4161 | 65.6509 | 22.7625 | 102.2704 | 36.1946
42810.4527 | 1098 | 17.4865 | 17.9274 | 18.0723 | 18.1095 | 17.4657 | 16.1139 | 14.9577 | 16.4509 | 16.9404 | 17.0884 | 17.0971 | 16.64 | 15.6727 | 14.4139 | 24.9506 | 41.9878 | 41.098 | 88.113 | 41.5763 | 91.8948 |  |  |  | 32.9593 | 89.5325 | 446.3295 | 692.8427 | 725.9301 | 700.1648 | 91.2798 | 122.7277 | 915.3151 | 96.0594 | 124.7039 | 847.3896 | 828.0003 | 876.008 |  | 251.7269 | 918.3785 | 920.0408 | 487.4092 |  | 470.6977 | 717.0947 | 569.7956 | 718.6171 | 900.2639 | 1016.6695 | 1044.2469 | 45.2448 | 415.9569 | 72.7858 | 625.9485 | 14.2851 | 49.2418 | 48.2568 | 50.5784 | 62.7387 |  |  | 0.8479 | -1.255 | -0.64212 | -1.0074 | 8.086 | 5.1809 | 7.424 | -2.2994 | 20.7664 | 53.3304 | 23.3165 | 3.286e-05 | 9.364e-05 | -0.00078689 | 25.2188 | 16.3591 | 16.732 | 17.1244 | 17.1308 | 16.1282 | 14.6212 | 16.6621 | 17.039 | 17.3641 | 17.4429 | 17.1889 | 16.3739 | 14.653 | 664.8212 | 444.4642 | 379.7844 | 259.7531 | 221.1055 | 741.4628 | 462.6828 | 19.1289 | 34.2842 | 40.2136 | 78.2686 | 83.6804 | 87.017 |  |  |  | 620.418 | 585.834 | 589.6267 | 613.441 | 85.2002 | 28.2003 | 809.0744 |  |  | 565.9382 |  |  | 20.1097 | 53.2312 | 540.6485 | 19.8801 | 55.1465 | 829.3857 | 749.1958 | 627.6022 | 793.8278 | 772.7118 | 744.403 |  | 824.2993 | 901.5895 | 1050.7565 | 605.1681 | 695.798 | 1001.4359 |  | 1050.1734 |  |  | 444.8092 | 647.1995 | 742.8417 | [6 empty] | 615.349 |  |  | 422.8331 |  |  | 519.777 | 670.9817 | 683.7707 | 982.7928 | 1104.2132 | 1077.3222 | 524.1437 | 721.5318 | 849.9556 | 622.1638 | 705.7638 | 1062.7158 | 1113.779 | 629.3831 | 818.6226 | 1110.1485 | 1154.4011 | 1106.7158 | 539.626 | 667.0404 | 704.8467 | 548.9983 | 742.2855 | 877.9885 | 1132.4649 | 1162.7051 | 604.4747 | 713.3047 | 657.5842 | 856.0703 | 91.413 | -0.0024122 | 17.8294 | 5.5981 | -40.1194 | 3.1217 | 8941.15 | 0.3 | 2.002 | -2.4568 | -1.7573 | -2.2011 | 7.117 | 5.6968 | 6.8195 | 84.4665 | 178.3292 | 52.4962 | 68.6033 | 25.8336 | 92.8231 | 36.3426
42810.4528 | 1099 | 17.482 | 17.9198 | 18.0674 | 18.106 | 17.4663 | 16.1095 | 14.9543 | 16.4502 | 16.9408 | 17.0793 | 17.0972 | 16.6334 | 15.6683 | 14.4181 | 25.0932 | 42.1722 | 41.2694 | 88.113 | 41.8116 | 91.9133 |  |  |  | 33.1307 | 89.4503 | 447.2256 | 692.7605 | 725.279 | 700.2256 | 95.9131 | 125.086 | 920.9003 | 95.9533 | 125.0412 | 846.3753 | 895.8454 | 874.2115 |  | 248.399 | 922.7563 | 922.5663 | 503.7353 |  | 472.9491 | 716.8443 | 569.2731 | 723.1005 | 903.3487 | 1017.8467 | 1046.4819 | 46.0883 | 415.7672 | 74.7088 | 626.0164 | 14.314 | 49.22 | 48.2886 | 50.5639 | 62.95 |  |  | 1.1863 | -0.98099 | 0.020248 | -1.0593 | 7.944 | 4.8727 | 7.1303 | -2.6293 | 20.3523 | 51.5831 | 22.4584 | 1.971e-05 | 7.228e-05 | -0.00079018 | 25.2826 | 16.3675 | 16.7354 | 17.1337 | 17.147 | 16.134 | 14.6306 | 16.6667 | 17.0424 | 17.3802 | 17.457 | 17.1924 | 16.3843 | 14.6592 | 702.2815 | 473.1128 | 412.6747 | 259.1627 | 220.2605 | 741.6365 | 461.7595 | 19.2005 | 34.4052 | 40.3389 | 78.3941 | 83.734 | 87.0489 |  |  |  | 620.4531 | 583.6015 | 588.2677 | 610.4051 | 80.4896 | 32.5148 | 807.1549 |  |  | 566.6765 |  |  | 20.1419 | 53.313 | 541.556 | 19.9351 | 55.2612 | 834.1536 | 750.0868 | 626.1922 | 793.4883 | 771.9217 | 746.2274 |  | 824.4222 | 907.6409 | 1048.4624 | 605.4598 | 696.1511 | 1005.1025 |  | 1050.1468 |  |  | 445.2431 | 649.0784 | 742.5895 | [6 empty] | 614.8931 |  |  | 423.2828 |  |  | 520.0773 | 670.6856 | 682.8092 | 987.7866 | 1104.4493 | 1079.8319 | 524.3397 | 720.712 | 849.8258 | 622.279 | 704.9881 | 1067.314 | 1117.9905 | 629.2505 | 818.2297 | 1106.3551 | 1152.6351 | 1105.6744 | 539.5986 | 666.6456 | 704.759 | 550.4063 | 743.1064 | 878.5289 | 1128.4028 | 1160.7185 | 604.3794 | 713.6059 | 658.2318 | 857.9404 | 94.3081 | -0.00055315 | 17.8233 | 5.5831 | -40.047 | 3.1217 | 8877.35 | 0.34 | 2.3681 | -2.1718 | 0.31201 | -2.2568 | 7.0575 | 5.5273 | 6.6862 | 84.4561 | 176.8932 | 52.5708 | 64.5015 | 21.9932 | 116.7769 | 36.4336
42810.4528 | 1100 | 17.4793 | 17.9179 | 18.0722 | 18.1115 | 17.4679 | 16.1116 | 14.9609 | 16.4545 | 16.9335 | 17.0857 | 17.1027 | 16.6363 | 15.6637 | 14.4199 | 25.2383 | 42.3505 | 41.432 | 88.1181 | 42.1114 | 91.9505 |  |  |  | 33.3119 | 89.3621 | 447.5541 | 692.2972 | 724.0083 | 700.0485 | 97.5883 | 128.8716 | 925.3841 | 94.6901 | 124.4829 | 846.8606 | 911.737 | 872.5177 |  | 253.48 | 923.6805 | 924.0042 | 502.237 |  | 474.3476 | 717.8798 | 569.5641 | 722.1701 | 892.6239 | 1014.0513 | 1047.5801 | 46.4614 | 415.4968 | 78.2581 | 626.1014 | 14.3163 | 49.21 | 48.2987 | 50.5447 | 63.1637 |  |  | 0.77496 | -0.33636 | -0.33919 | -0.54475 | 7.5511 | 5.9031 | 7.7447 | -3.3863 | 19.1169 | 49.9398 | 21.999 | 5.586e-05 | 6.57e-06 | -0.00081811 | 25.3501 | 16.3624 | 16.7421 | 17.1348 | 17.1362 | 16.1353 | 14.6337 | 16.6648 | 17.047 | 17.3818 | 17.4534 | 17.1904 | 16.3788 | 14.6638 | 711.6337 | 473.418 | 423.3 | 262.8659 | 212.247 | 741.3569 | 460.9806 | 19.2576 | 34.5204 | 40.4594 | 78.4783 | 83.7634 | 87.0738 |  |  |  | 620.5204 | 583.8343 | 588.9751 | 609.7741 | 50.4146 | 18.7807 | 804.6722 |  |  | 567.0931 |  |  | 20.1786 | 53.4037 | 540.7949 | 19.9857 | 55.3647 | 835.2059 | 752.5244 | 624.9999 | 792.661 | 771.7135 | 750.2799 |  | 824.8329 | 906.9095 | 1046.9861 | 604.5819 | 696.2341 | 1006.0933 |  | 1050.5197 |  |  | 446.0523 | 653.5617 | 744.945 | [6 empty] | 613.5831 |  |  | 423.388 |  |  | 520.517 | 670.6 | 682.3972 | 998.0089 | 1105.4337 | 1079.4617 | 524.4293 | 720.782 | 850.1845 | 622.7575 | 705.0225 | 1068.6563 | 1115.5235 | 629.6407 | 818.1656 | 1105.1465 | 1149.3455 | 1103.4318 | 540.257 | 666.8368 | 705.3105 | 551.3314 | 744.2284 | 878.3033 | 1124.6228 | 1159.1104 | 604.4945 | 714.5348 | 658.8197 | 858.1662 | 93.2194 | -0.0012828 | 17.8186 | 5.5652 | -40.085 | 3.1217 | 8836.16 | 0.4 | 1.9138 | -1.2724 | -1.2777 | -1.6192 | 6.8706 | 6.0748 | 6.9581 | 84.4782 | 176.1009 | 52.6146 | 63.365 | 20.6561 | 123.1361 | 36.4638
42810.4528 | 1101 | 17.481 | 17.9224 | 18.0749 | 18.1142 | 17.4637 | 16.127 | 14.9695 | 16.4615 | 16.9398 | 17.0929 | 17.1114 | 16.6351 | 15.6819 | 14.4274 | 25.3723 | 42.5237 | 41.589 | 88.1255 | 42.3695 | 91.9733 |  |  |  | 33.4885 | 89.3005 | 449.1628 | 692.1192 | 723.8604 | 699.545 | 96.6817 | 130.7632 | 930.187 | 99.0558 | 128.0281 | 849.7341 | 869.483 | 876.512 |  | 263.6655 | 925.7041 | 926.2637 | 508.147 |  | 473.8065 | 719.4386 | 569.9575 | 719.109 | 887.8273 | 1010.601 | 1045.4124 | 48.3102 | 415.0909 | 81.9056 | 626.1476 | 14.339 | 49.1776 | 48.2912 | 50.5283 | 63.3801 |  |  | 0.53117 | -0.11885 | -0.057948 | -0.96596 | 8.2128 | 5.1283 | 7.2702 | -3.519 | 19.6822 | 51.729 | 23.1856 | 4.93e-06 | 0.00011171 | -0.00079511 | 25.4251 | 16.3644 | 16.7431 | 17.1372 | 17.1324 | 16.133 | 14.6356 | 16.6671 | 17.0493 | 17.3847 | 17.4536 | 17.1952 | 16.3798 | 14.6638 | 683.7117 | 450.08 | 391.0972 | 249.3332 | 199.6458 | 739.1308 | 459.1231 | 19.3099 | 34.6315 | 40.5677 | 78.5699 | 83.7945 | 87.099 |  |  |  | 620.8572 | 585.8323 | 591.178 | 611.6128 | 83.3639 | 26.014 | 804.8156 |  |  | 568.1834 |  |  | 20.1968 | 53.4972 | 541.7533 | 20.027 | 55.4804 | 837.1603 | 754.5352 | 625.5253 | 787.9204 | 765.1989 | 754.1134 |  | 825.4416 | 907.3103 | 1046.4344 | 604.5453 | 696.246 | 992.9045 |  | 1047.8729 |  |  | 446.9544 | 658.4227 | 747.9288 | [6 empty] | 613.92 |  |  | 424.2924 |  |  | 521.3867 | 670.5634 | 682.6548 | 1007.2596 | 1102.6832 | 1077.5322 | 524.5622 | 721.3801 | 849.5517 | 622.8178 | 705.8445 | 1067.359 | 1111.1041 | 630.2536 | 817.7186 | 1107.3191 | 1145.7118 | 1098.9771 | 541.1012 | 666.8544 | 705.5854 | 551.697 | 744.4247 | 877.6013 | 1120.4688 | 1157.7219 | 604.8279 | 714.7422 | 659.062 | 856.8662 | 90.485 | -0.00071451 | 17.8113 | 5.548 | -40.139 | 3.1217 | 8764.02 | 0.29 | 1.5841 | -0.75692 | -0.52853 | -2.1579 | 7.1557 | 5.6545 | 6.7326 | 84.5715 | 175.7867 | 52.6184 | 65.6947 | 23.8617 | 106.689 | 36.4767
42810.4528 | 1102 | 17.4809 | 17.9144 | 18.0699 | 18.1124 | 17.4578 | 16.1175 | 14.9645 | 16.4536 | 16.9478 | 17.0846 | 17.108 | 16.6421 | 15.6741 | 14.4236 | 25.5048 | 42.7056 | 41.7576 | 88.1407 | 42.6406 | 91.9819 |  |  |  | 33.6607 | 89.2437 | 452.0386 | 692.4673 | 724.2726 | 699.4779 | 94.5171 | 126.0747 | 930.3976 | 97.5947 | 126.5844 | 851.3582 | 848.0499 | 866.5286 |  | 267.3464 | 924.5644 | 926.9375 | 511.504 |  | 473.8343 | 720.134 | 569.9289 | 720.5817 | 887.3168 | 1006.9484 | 1046.2128 | 50.3191 | 414.7572 | 83.5574 | 626.2228 | 14.3273 | 49.1379 | 48.2749 | 50.5086 | 63.6124 |  |  | 0.7329 | -0.20953 | 0.10568 | -0.72349 | 7.716 | 4.2787 | 6.3542 | -2.6996 | 19.9792 | 51.9142 | 23.3662 | 7.064e-05 | 5.75e-05 | -0.00080168 | 25.4952 | 16.3597 | 16.7351 | 17.1295 | 17.135 | 16.1307 | 14.6339 | 16.664 | 17.0415 | 17.3762 | 17.4482 | 17.1903 | 16.3762 | 14.6536 | 695.906 | 459.652 | 427.2959 | 250.7389 | 199.5011 | 738.4314 | 457.943 | 19.3737 | 34.7493 | 40.6864 | 78.6789 | 83.8328 | 87.1337 |  |  |  | 621.2562 | 588.0609 | 593.4115 | 611.8232 | 62.4934 | 28.8556 | 800.7446 |  |  | 566.9787 |  |  | 20.2176 | 53.5768 | 543.9005 | 20.0867 | 55.5726 | 840.0306 | 755.7255 | 626.5757 | 787.0541 | 765.3403 | 756.122 |  | 825.888 | 907.16 | 1044.0662 | 605.1663 | 696.2387 | 988.645 |  | 1046.7276 |  |  | 447.7877 | 662.1512 | 749.7599 | [6 empty] | 615.5553 |  |  | 425.4572 |  |  | 521.9283 | 670.1398 | 682.6209 | 1007.4009 | 1099.3284 | 1074.5134 | 524.4615 | 721.5253 | 848.7128 | 622.5106 | 705.9295 | 1068.1624 | 1112.1039 | 630.3645 | 816.3793 | 1108.7581 | 1142.0429 | 1096.9907 | 540.4303 | 666.7711 | 705.4807 | 552.0108 | 744.2672 | 876.5111 | 1123.8408 | 1156.3723 | 605.5159 | 714.6867 | 659.3788 | 857.1032 | 93.3896 | 0.00030269 | 17.8056 | 5.5294 | -40.1157 | 3.1216 | 8689.9 | 0.37 | 1.8606 | -1.0054 | 0.71399 | -1.8682 | 6.926 | 5.1576 | 6.2852 | 84.6624 | 174.4942 | 52.5995 | 64.0977 | 19.6037 | 98.95 | 36.5466
42810.4528 | 1103 | 17.4787 | 17.9096 | 18.064 | 18.1057 | 17.4515 | 16.1081 | 14.965 | 16.4519 | 16.9291 | 17.0838 | 17.1018 | 16.6356 | 15.668 | 14.4177 | 25.653 | 42.8825 | 41.931 | 88.1626 | 42.932 | 91.9906 |  |  |  | 33.8404 | 89.1986 | 454.633 | 693.0838 | 725.0014 | 700.1822 | 93.3657 | 124.5943 | 925.2256 | 94.3749 | 124.605 | 847.6662 | 791.2974 | 870.6761 |  | 256.5337 | 925.4662 | 924.4182 | 499.0984 |  | 476.5556 | 720.8612 | 571.8272 | 721.7233 | 886.1834 | 1006.1017 | 1049.6486 | 50.4669 | 414.5556 | 82.9075 | 626.0117 | 14.3265 | 49.1263 | 48.2781 | 50.5003 | 63.6511 |  |  | 0.81767 | -0.29299 | -0.24785 | -1.192 | 7.6122 | 5.656 | 7.0337 | -3.0275 | 19.3983 | 51.8672 | 22.0755 | 5.914e-05 | 6.9e-05 | -0.00081811 | 25.5658 | 16.3728 | 16.7411 | 17.1244 | 17.1389 | 16.1343 | 14.642 | 16.6678 | 17.041 | 17.3731 | 17.4509 | 17.1953 | 16.3817 | 14.6623 | 664.5288 | 447.324 | 418.6047 | 250.3918 | 193.9437 | 736.348 | 456.9006 | 19.4351 | 34.8755 | 40.8192 | 78.7948 | 83.8781 | 87.1717 |  |  |  | 621.4346 | 588.8166 | 594.1138 | 610.894 | 54.4745 | 21.9959 | 802.0093 |  |  | 569.0534 |  |  | 20.2501 | 53.677 | 546.2346 | 20.1395 | 55.6744 | 838.3128 | 756.3088 | 627.8154 | 785.9776 | 764.4138 | 755.8702 |  | 826.3606 | 901.8785 | 1041.5886 | 606.2627 | 696.3179 | 995.8141 |  | 1047.7388 |  |  | 447.7914 | 662.7145 | 750.602 | [6 empty] | 616.9292 |  |  | 426.3166 |  |  | 522.217 | 669.5393 | 682.1745 | 1000.6686 | 1099.3903 | 1074.9792 | 524.8603 | 721.008 | 848.6126 | 622.5196 | 705.0865 | 1068.2293 | 1118.071 | 630.3866 | 815.0572 | 1111.1084 | 1144.7754 | 1095.9 | 540.0728 | 667.3396 | 705.6222 | 552.1162 | 745.0138 | 877.3717 | 1132.5872 | 1154.6174 | 605.8798 | 715.0568 | 659.922 | 859.389 | 92.8422 | -0.00081273 | 17.8008 | 5.5065 | -40.1251 | 3.1216 | 8663.61 | 0.34 | 1.966 | -1.1893 | -1.0939 | -2.3988 | 6.877 | 5.9279 | 6.6105 | 84.8249 | 173.2915 | 52.5876 | 66.8649 | 20.3614 | 80.908 | 36.6063
42810.4528 | 1104 | 17.4788 | 17.9116 | 18.0654 | 18.1116 | 17.4558 | 16.1079 | 14.9745 | 16.4467 | 16.9365 | 17.0796 | 17.1059 | 16.6398 | 15.6686 | 14.4213 | 25.7837 | 43.0505 | 42.091 | 88.1785 | 43.2171 | 91.9945 |  |  |  | 34.0157 | 89.1389 | 456.6111 | 693.6972 | 724.9808 | 700.9315 | 90.2241 | 125.0481 | 925.2725 | 94.1704 | 125.4175 | 845.2069 | 813.0491 | 870.4329 |  | 242.7384 | 927.0384 | 925.2987 | 503.7124 |  | 476.2713 | 722.4057 | 573.5242 | 722.5328 | 884.0074 | 1004.4946 | 1049.2347 | 50.6353 | 414.2577 | 83.2312 | 625.5494 | 14.3403 | 49.139 | 48.2832 | 50.5015 | 63.7247 |  |  | 0.96749 | 0.046743 | -0.35759 | -1.2051 | 8.2227 | 5.3485 | 7.2926 | -3.1622 | 19.863 | 53.4969 | 23.3577 | 2.464e-05 | 6.9e-05 | -0.00077868 | 25.6213 | 16.3598 | 16.7287 | 17.1195 | 17.1251 | 16.1279 | 14.6331 | 16.6549 | 17.034 | 17.3677 | 17.4414 | 17.1919 | 16.3757 | 14.6499 | 637.0925 | 431.1585 | 380.5155 | 248.4557 | 206.2284 | 733.8042 | 455.3723 | 19.4973 | 34.9794 | 40.9316 | 78.8634 | 83.9043 | 87.2 |  |  |  | 621.8379 | 589.7513 | 594.7001 | 614.1105 | 82.8653 | 20.8567 | 799.6117 |  |  | 571.7373 |  |  | 20.2783 | 53.7546 | 547.7222 | 20.191 | 55.7925 | 839.5803 | 755.3623 | 628.4424 | 784.6643 | 762.6771 | 754.3125 |  | 826.6308 | 897.8245 | 1040.7958 | 607.011 | 696.5337 | 999.7276 |  | 1048.9002 |  |  | 447.4443 | 661.812 | 750.2629 | [6 empty] | 617.7699 |  |  | 426.7946 |  |  | 523.0673 | 669.192 | 681.8398 | 989.9495 | 1097.2567 | 1078.2231 | 525.3598 | 721.7878 | 849.662 | 622.9291 | 704.4257 | 1062.4138 | 1118.0594 | 631.3831 | 817.0718 | 1113.4317 | 1149.213 | 1094.3885 | 540.389 | 667.6504 | 706.5059 | 551.4994 | 745.9312 | 878.7831 | 1131.0348 | 1152.1893 | 605.8625 | 715.6989 | 660.4091 | 860.0391 | 86.8736 | -0.00058824 | 17.7967 | 5.4831 | -40.0759 | 3.1216 | 8594.56 | 0.26 | 2.1394 | 0.4754 | -1.3149 | -2.4139 | 7.143 | 5.7608 | 6.7269 | 84.9572 | 172.9738 | 52.6174 | 69.0395 | 24.2892 | 87.5188 | 36.5937
42810.4528 | 1105 | 17.48 | 17.915 | 18.0653 | 18.1086 | 17.4534 | 16.1121 | 14.967 | 16.4518 | 16.939 | 17.0824 | 17.1067 | 16.6372 | 15.6707 | 14.4174 | 25.9283 | 43.2216 | 42.2551 | 88.2 | 43.4878 | 92.0118 |  |  |  | 34.1853 | 89.0844 | 457.5036 | 693.6648 | 724.4111 | 700.7559 | 92.8269 | 123.3315 | 926.2943 | 93.2768 | 126.8424 | 843.2473 | 906.9214 | 867.0688 |  | 246.3053 | 929.2824 | 930.4288 | 488.2223 |  | 475.6659 | 722.263 | 574.2014 | 722.5593 | 885.3397 | 1002.7937 | 1046.792 | 51.7644 | 413.954 | 84.7008 | 625.2042 | 14.34 | 49.1182 | 48.2905 | 50.4893 | 63.5477 |  |  | 1.1679 | -0.52561 | -0.66249 | -0.70771 | 7.674 | 5.8387 | 7.472 | -3.3245 | 19.5022 | 52.2944 | 23.1928 | -3.943e-05 | 0.00014785 | -0.00078854 | 25.7016 | 16.376 | 16.7379 | 17.1281 | 17.1337 | 16.1395 | 14.6362 | 16.6643 | 17.0402 | 17.3814 | 17.4557 | 17.1905 | 16.3776 | 14.6611 | 667.2504 | 455.3993 | 372.3188 | 250.4828 | 200.7332 | 733.7119 | 453.8754 | 19.5598 | 35.0972 | 41.0512 | 78.9463 | 83.928 | 87.238 |  |  |  | 622.486 | 591.6799 | 596.1867 | 618.9039 | 69.531 | 25.3058 | 797.2018 |  |  | 572.3107 |  |  | 20.3007 | 53.8435 | 547.6112 | 20.2202 | 55.9076 | 842.3244 | 752.9168 | 629.0532 | 781.7679 | 760.045 | 751.6167 |  | 826.6808 | 895.5438 | 1039.6361 | 607.5485 | 696.8798 | 998.9703 |  | 1049.5751 |  |  | 447.0303 | 659.1086 | 748.6806 | [6 empty] | 618.1961 |  |  | 426.6548 |  |  | 524.0623 | 668.9342 | 681.9143 | 989.6658 | 1089.4403 | 1077.3558 | 525.6161 | 723.6537 | 849.8013 | 623.1661 | 704.6317 | 1061.2162 | 1118.2345 | 632.6207 | 817.9504 | 1106.4927 | 1147.4218 | 1092.3278 | 540.8379 | 667.2463 | 707.7335 | 551.2003 | 746.1572 | 877.9005 | 1125.2282 | 1152.4754 | 606.071 | 715.6197 | 660.6008 | 860.6562 | 83.2843 | -0.00059525 | 17.7911 | 5.4605 | -40.1075 | 3.1216 | 8590.01 | 0.34 | 2.3503 | -1.594 | -1.7896 | -1.8497 | 6.8959 | 6.0151 | 6.8046 | 85.0485 | 172.4091 | 52.6837 | 65.657 | 24.9028 | 121.5858 | 36.5841
42810.4528 | 1106 | 17.4722 | 17.9124 | 18.0578 | 18.1024 | 17.4533 | 16.1135 | 14.973 | 16.4478 | 16.9383 | 17.0816 | 17.1027 | 16.633 | 15.6693 | 14.415 | 26.0831 | 43.4053 | 42.4194 | 88.2407 | 43.7728 | 92.0427 |  |  |  | 34.3784 | 89.0295 | 458.9935 | 693.2334 | 723.5341 | 700.1927 | 95.8246 | 127.6306 | 932.2176 | 94.2653 | 126.0209 | 840.921 | 906.4142 | 865.9735 |  | 246.9015 | 927.9093 | 927.6166 | 500.603 |  | 475.5491 | 721.4014 | 573.2723 | 720.0871 | 885.6632 | 1002.5246 | 1043.823 | 52.4064 | 413.8223 | 87.2256 | 625.1558 | 14.3289 | 49.132 | 48.2965 | 50.4823 | 63.2062 |  |  | 1.4314 | -0.705 | -0.46404 | -0.63017 | 7.8888 | 5.0488 | 7.2177 | -3.9087 | 20.9958 | 53.3247 | 22.6018 | 6.736e-05 | -1.15e-05 | -0.00078361 | 25.7681 | 16.3756 | 16.7276 | 17.1193 | 17.1318 | 16.1293 | 14.6286 | 16.6584 | 17.033 | 17.3697 | 17.4389 | 17.1794 | 16.38 | 14.6556 | 687.1845 | 458.4471 | 391.6111 | 260.4724 | 213.3646 | 732.8306 | 452.7227 | 19.625 | 35.2157 | 41.1711 | 79.0462 | 83.964 | 87.2781 |  |  |  | 623.2499 | 593.3326 | 596.8132 | 621.7397 | 69.6511 | 25.3536 | 794.7237 |  |  | 572.7864 |  |  | 20.3323 | 53.9134 | 549.6966 | 20.2651 | 56.0094 | 843.2361 | 748.0812 | 627.728 | 782.6347 | 761.7323 | 745.9929 |  | 826.0007 | 898.1695 | 1036.8399 | 606.8333 | 697.2403 | 1008.2957 |  | 1049.9153 |  |  | 446.0539 | 652.6269 | 744.0616 | [6 empty] | 617.0934 |  |  | 425.2087 |  |  | 524.8972 | 669.1385 | 682.2809 | 992.7067 | 1085.2874 | 1078.102 | 525.7749 | 724.718 | 849.5424 | 623.591 | 705.4568 | 1062.2798 | 1120.6994 | 633.2407 | 817.5658 | 1108.0997 | 1146.2923 | 1095.8281 | 541.5379 | 666.2665 | 707.8351 | 551.6774 | 747.7436 | 876.7469 | 1128.6801 | 1152.707 | 606.5391 | 714.4906 | 660.9566 | 860.3544 | 85.3033 | 7.8201e-05 | 17.7864 | 5.4398 | -40.1066 | 3.1216 | 8636.35 | 0.36 | 2.6013 | -1.8453 | -1.4971 | -1.7447 | 6.9911 | 5.5928 | 6.6871 | 84.9808 | 170.8283 | 52.7883 | 63.1404 | 22.5309 | 121.0389 | 36.6511
42810.4528 | 1107 | 17.4727 | 17.9101 | 18.0646 | 18.102 | 17.4516 | 16.1135 | 14.9786 | 16.4522 | 16.9425 | 17.0804 | 17.1064 | 16.6354 | 15.6686 | 14.4269 | 26.2223 | 43.5742 | 42.5894 | 88.2701 | 44.0755 | 92.066 |  |  |  | 34.5564 | 88.972 | 458.9506 | 692.5928 | 722.7075 | 699.9725 | 96.8422 | 128.8717 | 928.2261 | 93.7256 | 122.8902 | 837.1783 | 899.5682 | 864.5892 |  | 255.3135 | 925.2742 | 925.5502 | 506.2473 |  | 475.9529 | 720.1404 | 571.4544 | 720.691 | 882.5998 | 1002.9516 | 1044.0172 | 52.5466 | 413.7011 | 89.0991 | 625.2241 | 14.3228 | 49.1399 | 48.2979 | 50.4735 | 62.7957 |  |  | 1.2133 | -0.15631 | -0.013264 | -0.73269 | 8.8075 | 6.0897 | 7.2656 | -2.4098 | 20.5984 | 53.747 | 30.407 | 4.6e-05 | 6.243e-05 | -0.00079839 | 25.833 | 16.3749 | 16.7288 | 17.1145 | 17.1292 | 16.1227 | 14.6372 | 16.6572 | 17.0364 | 17.3721 | 17.4444 | 17.1902 | 16.3783 | 14.6538 | 684.1309 | 458.8564 | 378.7313 | 254.8917 | 221.8843 | 731.918 | 451.4429 | 19.7029 | 35.3341 | 41.2998 | 79.1595 | 84.0106 | 87.3061 |  |  |  | 623.8011 | 593.6013 | 597.269 | 620.8026 | 69.8774 | 25.2885 | 795.3265 |  |  | 575.3312 |  |  | 20.3667 | 54.0139 | 548.8431 | 20.3417 | 56.1261 | 842.3223 | 747.6432 | 627.636 | 781.936 | 760.8382 | 744.5687 |  | 825.5608 | 899.781 | 1035.2116 | 605.9231 | 697.596 | 1006.8938 |  | 1049.1528 |  |  | 445.6357 | 649.0592 | 741.6263 | [6 empty] | 616.3281 |  |  | 424.1108 |  |  | 525.2439 | 670.1358 | 682.5491 | 997.0542 | 1080.7154 | 1078.7743 | 525.7052 | 724.6017 | 850.5421 | 624.5139 | 706.2114 | 1065.1151 | 1121.8835 | 633.2282 | 818.0233 | 1109.4676 | 1146.3209 | 1096.0733 | 542.4703 | 665.364 | 707.6668 | 552.482 | 749.2807 | 877.3725 | 1134.3976 | 1153.6136 | 607.2819 | 714.2469 | 661.1688 | 859.6646 | 91.0873 | -0.00034273 | 17.7811 | 5.4195 | -40.0818 | 3.1216 | 8692.01 | 0.26 | 2.3946 | -0.86834 | -0.25295 | -1.88 | 7.3881 | 6.1434 | 6.7104 | 84.8758 | 169.9096 | 52.8972 | 63.1679 | 23.7091 | 118.1658 | 36.7826
42810.4529 | 1108 | 17.4861 | 17.9171 | 18.0725 | 18.1137 | 17.4586 | 16.12 | 14.9863 | 16.4549 | 16.9463 | 17.0888 | 17.1125 | 16.6414 | 15.6777 | 14.4301 | 26.368 | 43.7497 | 42.7449 | 88.299 | 44.4758 | 92.0867 |  |  |  | 34.7445 | 88.8996 | 459.8256 | 692.8115 | 722.546 | 700.7017 | 90.6793 | 129.6107 | 932.1306 | 96.2051 | 123.4195 | 836.9424 | 908.396 | 860.4084 |  | 276.0233 | 925.1877 | 923.8893 | 503.4936 |  | 476.3954 | 720.8183 | 572.2611 | 723.4986 | 891.5612 | 1010.419 | 1045.9655 | 53.0884 | 413.5975 | 89.2972 | 625.1167 | 14.3636 | 49.1372 | 48.2971 | 50.4725 | 62.4471 |  |  | 0.87813 | -0.17273 | 0.33566 | -1.2603 | 7.8244 | 4.9601 | 7.9904 | -3.2641 | 19.7867 | 51.6075 | 29.7969 | 4.928e-05 | 7.064e-05 | -0.00078032 | 25.9027 | 16.3707 | 16.715 | 17.11 | 17.1211 | 16.1203 | 14.6295 | 16.6576 | 17.0321 | 17.3677 | 17.4388 | 17.1839 | 16.375 | 14.6538 | 699.4105 | 470.8627 | 390.5096 | 250.5636 | 225.4605 | 731.5727 | 450.1138 | 19.7638 | 35.4571 | 41.4171 | 79.2755 | 84.0456 | 87.3459 |  |  |  | 624.2843 | 593.7121 | 597.6589 | 619.3602 | 70.91 | 21.9338 | 793.5266 |  |  | 576.5108 |  |  | 20.3915 | 54.1062 | 549.4979 | 20.3681 | 56.2308 | 842.6455 | 747.949 | 628.097 | 782.326 | 762.4872 | 744.7188 |  | 825.5634 | 897.1996 | 1034.4758 | 606.0403 | 698.0185 | 997.8923 |  | 1048.8537 |  |  | 445.6404 | 646.7275 | 742.0213 | [6 empty] | 616.432 |  |  | 422.8032 |  |  | 525.7545 | 671.0811 | 683.0357 | 1007.6983 | 1079.4778 | 1083.1503 | 525.4115 | 724.8035 | 853.3384 | 625.6338 | 706.271 | 1064.964 | 1121.3845 | 632.8579 | 817.8068 | 1109.1785 | 1149.1697 | 1095.2841 | 543.88 | 665.5065 | 707.9376 | 552.629 | 749.1554 | 877.7038 | 1135.1816 | 1152.6071 | 608.0862 | 715.559 | 660.7411 | 858.5567 | 90.9596 | -0.00033568 | 17.7798 | 5.4015 | -40.0817 | 3.1216 | 8797.15 | 0.33 | 2.0379 | -0.91315 | 1.2729 | -2.4666 | 6.984 | 5.5606 | 7.0577 | 84.8725 | 169.5875 | 52.9934 | 61.3523 | 22.1383 | 121.7532 | 36.9152
42810.4529 | 1109 | 17.4661 | 17.9055 | 18.059 | 18.104 | 17.4603 | 16.1056 | 14.9738 | 16.4469 | 16.949 | 17.0901 | 17.0929 | 16.634 | 15.6721 | 14.4262 | 26.5081 | 43.9246 | 42.9229 | 88.3178 | 44.7944 | 92.0897 |  |  |  | 34.931 | 88.8313 | 459.5503 | 691.9242 | 720.8097 | 699.2593 | 92.8406 | 125.8885 | 930.2976 | 97.8371 | 127.8989 | 839.7363 | 795.1809 | 860.7154 |  | 271.5671 | 917.6036 | 920.0102 | 501.3954 |  | 477.104 | 721.694 | 572.9002 | 725.4107 | 897.7747 | 1011.9499 | 1045.6139 | 54.3923 | 413.3205 | 87.2364 | 624.8306 | 14.3706 | 49.1415 | 48.2967 | 50.4614 | 62.2541 |  |  | 1.1239 | -0.30021 | -0.36548 | -0.65646 | 8.1004 | 5.8702 | 7.8419 | -2.8869 | 19.9983 | 51.0131 | 26.1651 | 6.9e-05 | 6.9e-05 | -0.00079839 | 25.9795 | 16.379 | 16.7292 | 17.1191 | 17.1227 | 16.1266 | 14.6327 | 16.6623 | 17.0388 | 17.3726 | 17.4437 | 17.1896 | 16.3799 | 14.6569 | 692.8738 | 453.3112 | 376.3623 | 238.5634 | 219.9631 | 730.5042 | 448.6092 | 19.8257 | 35.5704 | 41.5336 | 79.3695 | 84.0752 | 87.3693 |  |  |  | 624.6994 | 592.783 | 596.8613 | 620.2011 | 66.4897 | 23.2391 | 794.8096 |  |  | 579.2081 |  |  | 20.4239 | 54.1877 | 548.5256 | 20.4286 | 56.3212 | 840.6043 | 748.5482 | 626.5965 | 784.8165 | 765.6394 | 745.806 |  | 825.6277 | 892.4216 | 1034.2447 | 604.8616 | 698.26 | 994.6857 |  | 1047.3966 |  |  | 445.5948 | 647.4933 | 742.3957 | [6 empty] | 614.8026 |  |  | 420.7693 |  |  | 525.8396 | 671.5019 | 684.5882 | 1014.1224 | 1076.0034 | 1084.402 | 524.7101 | 724.0704 | 852.1372 | 625.703 | 706.1038 | 1067.5119 | 1122.0832 | 632.7529 | 816.4126 | 1107.9998 | 1145.3828 | 1092.8168 | 544.6449 | 666.0825 | 708.8692 | 552.7151 | 747.9688 | 875.5444 | 1131.4412 | 1149.3183 | 608.7735 | 716.696 | 660.2315 | 857.0802 | 95.1979 | 0.0010393 | 17.7775 | 5.3835 | -40.1242 | 3.1216 | 8908.13 | 0.35 | 2.3038 | -1.2044 | -1.3288 | -1.7809 | 7.1103 | 6.0529 | 6.9959 | 84.8634 | 169.5966 | 53.083 | 61.7145 | 23.4144 | 82.0202 | 36.9715
42810.4529 | 1110 | 17.4682 | 17.915 | 18.0567 | 18.1039 | 17.465 | 16.1081 | 14.9819 | 16.458 | 16.9327 | 17.0882 | 17.1 | 16.6344 | 15.671 | 14.428 | 26.6672 | 44.1073 | 43.0829 | 88.3439 | 45.1481 | 92.114 |  |  |  | 35.1141 | 88.8035 | 459.4383 | 690.4685 | 718.7254 | 697.2235 | 93.6138 | 126.4642 | 920.2534 | 86.0933 | 121.0931 | 834.181 | 829.1311 | 860.504 |  | 241.2124 | 921.2941 | 921.7504 | 490.7956 |  | 477.7578 | 721.3517 | 571.5813 | 725.4472 | 895.039 | 1006.9334 | 1043.1114 | 55.9385 | 413.0348 | 85.3503 | 624.506 | 14.3563 | 49.1426 | 48.287 | 50.4348 | 62.1025 |  |  | 0.79336 | -0.78517 | -0.56064 | -0.6512 | 7.4788 | 5.2157 | 7.1999 | -3.0045 | 19.0675 | 51.2854 | 24.3094 | 3.943e-05 | -2.3e-05 | -0.0007754 | 26.049 | 16.3885 | 16.7352 | 17.126 | 17.1281 | 16.1303 | 14.635 | 16.6658 | 17.0427 | 17.3794 | 17.4541 | 17.1973 | 16.3832 | 14.6619 | 677.8081 | 456.0328 | 384.8746 | 246.5072 | 222.6475 | 729.168 | 447.3785 | 19.8881 | 35.6868 | 41.6539 | 79.4522 | 84.1177 | 87.4054 |  |  |  | 625.4671 | 593.4622 | 596.7793 | 624.4364 | 62.5548 | 22.7169 | 794.5773 |  |  | 580.3459 |  |  | 20.4582 | 54.2721 | 547.8827 | 20.4784 | 56.4149 | 837.0826 | 750.9005 | 626.834 | 785.2332 | 766.9721 | 749.3329 |  | 825.8972 | 896.932 | 1032.9307 | 603.8022 | 698.4186 | 1003.3067 |  | 1046.5979 |  |  | 447.0893 | 653.9617 | 744.3046 | [6 empty] | 614.6235 |  |  | 419.2926 |  |  | 525.4727 | 671.4938 | 685.0173 | 1015.3309 | 1075.2641 | 1086.06 | 525.4145 | 723.1484 | 851.9324 | 625.4065 | 706.1565 | 1066.839 | 1118.0793 | 632.9609 | 816.6826 | 1109.9738 | 1141.8693 | 1088.0988 | 544.8246 | 666.2611 | 709.0105 | 553.7224 | 747.01 | 873.9974 | 1134.5512 | 1144.0919 | 608.8193 | 716.6726 | 661.0059 | 856.9111 | 101.8729 | -0.0011354 | 17.7743 | 5.3676 | -40.2219 | 3.1216 | 9015.77 | 0.27 | 1.9336 | -1.9474 | -1.6456 | -1.7735 | 6.8187 | 5.6943 | 6.6904 | 84.854 | 168.7698 | 53.1498 | 62.9342 | 22.2271 | 93.1034 | 37.0014
42810.4529 | 1111 | 17.4779 | 17.9177 | 18.0598 | 18.1034 | 17.4598 | 16.1085 | 14.9959 | 16.4506 | 16.9441 | 17.0884 | 17.1052 | 16.6405 | 15.6754 | 14.439 | 26.811 | 44.2843 | 43.2618 | 88.3613 | 45.5163 | 92.1269 |  |  |  | 35.3159 | 88.7638 | 459.845 | 689.7102 | 718.2008 | 696.0925 | 93.5773 | 128.4658 | 927.0116 | 95.58 | 126.0562 | 835.7004 | 885.8874 | 861.9636 |  | 232.4998 | 924.7249 | 925.2699 | 482.359 |  | 477.3834 | 720.006 | 569.911 | 721.8041 | 889.1168 | 1004.3624 | 1041.242 | 58.1942 | 412.7564 | 85.6299 | 624.3044 | 14.371 | 49.1551 | 48.3036 | 50.4129 | 62.1052 |  |  | 1.0812 | -0.50523 | -0.43908 | -0.82862 | 7.9132 | 5.8268 | 8.2651 | -3.1333 | 20.347 | 51.5093 | 22.7916 | 7.228e-05 | 4.6e-05 | -0.00079182 | 26.1136 | 16.3874 | 16.7275 | 17.1229 | 17.1245 | 16.1216 | 14.6329 | 16.6626 | 17.0373 | 17.3732 | 17.4524 | 17.1958 | 16.3827 | 14.6627 | 664.0914 | 446.9356 | 375.4479 | 244.0958 | 226.138 | 727.8218 | 446.2318 | 19.9556 | 35.7983 | 41.7699 | 79.5176 | 84.139 | 87.445 |  |  |  | 626.2726 | 595.1981 | 597.7498 | 627.4911 | 74.9406 | 30.6328 | 797.4048 |  |  | 582.3964 |  |  | 20.4821 | 54.3623 | 547.4888 | 20.5331 | 56.5372 | 837.7503 | 753.6976 | 628.0749 | 785.0307 | 765.8492 | 753.3575 |  | 826.2956 | 901.9365 | 1031.8364 | 603.8737 | 698.8187 | 998.4729 |  | 1046.0983 |  |  | 448.9296 | 663.903 | 747.8034 | [6 empty] | 615.7742 |  |  | 419.3735 |  |  | 525.3321 | 671.1038 | 684.8367 | 1008.7347 | 1076.1494 | 1083.4576 | 526.8477 | 722.2443 | 852.0102 | 625.3967 | 705.7687 | 1066.4466 | 1111.4674 | 633.4555 | 816.7862 | 1116.0054 | 1142.7532 | 1084.0874 | 545.2385 | 666.2704 | 708.7727 | 554.8266 | 746.4104 | 874.6217 | 1133.9471 | 1139.9934 | 608.7476 | 716.598 | 661.8106 | 856.7913 | 97.3341 | -0.0010653 | 17.7729 | 5.3483 | -40.0115 | 3.1216 | 9093.61 | 0.32 | 2.256 | -1.5611 | -1.4553 | -1.9992 | 7.0069 | 6.0127 | 7.161 | 84.8733 | 168.0482 | 53.2422 | 64.0019 | 23.0501 | 113.532 | 37.0716
42810.4529 | 1112 | 17.4737 | 17.9068 | 18.0572 | 18.0976 | 17.4533 | 16.1045 | 14.9879 | 16.4465 | 16.9437 | 17.0847 | 17.095 | 16.636 | 15.6713 | 14.4261 | 26.9518 | 44.46 | 43.4186 | 88.3941 | 45.7995 | 92.1737 |  |  |  | 35.4901 | 88.7121 | 461.5607 | 690.1995 | 718.9753 | 696.633 | 94.0862 | 126.5063 | 927.1084 | 96.5165 | 127.4602 | 844.0172 | 831.2289 | 866.6545 |  | 241.1708 | 925.0567 | 926.4602 | 476.4968 |  | 476.6824 | 718.5567 | 570.6783 | 722.8562 | 892.5635 | 1006.4892 | 1041.4758 | 59.1362 | 412.3194 | 88.4841 | 624.3453 | 14.3974 | 49.1417 | 48.3255 | 50.384 | 62.1106 |  |  | 1.07 | -0.31073 | -0.95294 | -1.4811 | 8.1418 | 4.5704 | 7.3675 | -4.2169 | 19.6003 | 51.4948 | 23.2857 | 6.736e-05 | 9.693e-05 | -0.00079018 | 26.1851 | 16.3739 | 16.7187 | 17.1215 | 17.1154 | 16.1242 | 14.6348 | 16.6652 | 17.0354 | 17.3743 | 17.4504 | 17.1871 | 16.3919 | 14.6613 | 664.5087 | 454.0991 | 401.662 | 246.5165 | 221.5403 | 727.3261 | 445.9268 | 20.0299 | 35.9138 | 41.8869 | 79.6189 | 84.1651 | 87.4803 |  |  |  | 627.0507 | 596.739 | 598.8509 | 628.0321 | 68.5463 | 30.9429 | 796.5166 |  |  | 585.0457 |  |  | 20.5099 | 54.4409 | 549.1012 | 20.5633 | 56.6489 | 837.7756 | 755.9175 | 629.292 | 786.0006 | 767.1593 | 757.4812 |  | 826.7762 | 905.8867 | 1031.6886 | 603.8317 | 699.2889 | 997.2682 |  | 1045.0068 |  |  | 450.7968 | 671.1951 | 750.7764 | [6 empty] | 616.5432 |  |  | 418.7636 |  |  | 525.4544 | 670.5058 | 684.5559 | 1010.8621 | 1077.981 | 1081.3864 | 528.1717 | 722.3197 | 851.5552 | 625.3466 | 705.2492 | 1065.7383 | 1110.4019 | 634.0343 | 817.6413 | 1121.9184 | 1138.3168 | 1086.0013 | 545.3521 | 666.1723 | 708.0371 | 555.1599 | 745.5797 | 874.9418 | 1134.4559 | 1138.7186 | 608.352 | 715.9906 | 662.1278 | 855.6283 | 92.7881 | -0.001416 | 17.7714 | 5.3192 | -40.0563 | 3.1216 | 9157.94 | 0.33 | 2.2449 | -1.2233 | -2.1424 | -2.6709 | 7.1133 | 5.3295 | 6.7666 | 84.9171 | 167.8598 | 53.3544 | 63.7878 | 20.0778 | 94.1979 | 37.2068
42810.4529 | 1113 | 17.4705 | 17.9028 | 18.0505 | 18.0913 | 17.4527 | 16.1009 | 14.9901 | 16.4498 | 16.9376 | 17.078 | 17.0971 | 16.6297 | 15.6716 | 14.4203 | 27.0978 | 44.624 | 43.5785 | 88.435 | 46.1856 | 92.1997 |  |  |  | 35.685 | 88.6566 | 463.3035 | 690.5626 | 719.6048 | 697.2384 | 97.5383 | 128.6498 | 926.8482 | 94.0942 | 126.708 | 847.8413 | 850.6578 | 870.1284 |  | 255.2788 | 926.2724 | 926.175 | 492.6656 |  | 475.2255 | 717.1932 | 571.0316 | 722.1753 | 890.8781 | 1004.9232 | 1042.1629 | 59.7194 | 411.7627 | 90.2034 | 624.2282 | 14.4232 | 49.1066 | 48.3267 | 50.3404 | 62.2028 |  |  | 1.5004 | -0.18916 | -0.065832 | -1.3208 | 8.7529 | 5.0528 | 7.6691 | -2.8396 | 19.3246 | 50.3724 | 23.4481 | 3.943e-05 | 1.971e-05 | -0.00078854 | 26.2591 | 16.3875 | 16.7286 | 17.1166 | 17.1242 | 16.1187 | 14.6386 | 16.6612 | 17.044 | 17.3782 | 17.4504 | 17.198 | 16.3771 | 14.6666 | 661.6896 | 454.129 | 411.9258 | 257.712 | 226.1925 | 726.3214 | 445.6173 | 20.095 | 36.046 | 42.0129 | 79.7161 | 84.1909 | 87.5149 |  |  |  | 627.6036 | 596.0913 | 598.1656 | 624.6416 | 69.5249 | 20.907 | 797.8312 |  |  | 587.6755 |  |  | 20.5458 | 54.5404 | 550.5499 | 20.6191 | 56.764 | 839.9088 | 755.8374 | 630.4454 | 786.5209 | 767.6245 | 760.2281 |  | 827.2412 | 901.3243 | 1032.2535 | 603.7448 | 699.7003 | 997.0016 |  | 1044.8121 |  |  | 451.5989 | 674.9055 | 752.0544 | [6 empty] | 617.4835 |  |  | 417.8746 |  |  | 525.8673 | 670.4669 | 684.328 | 1014.8628 | 1087.4111 | 1080.5295 | 528.9866 | 722.0281 | 850.8462 | 625.5993 | 705.4892 | 1069.6366 | 1110.6857 | 634.259 | 816.7778 | 1124.4855 | 1138.3127 | 1092.4283 | 545.2451 | 665.7811 | 707.4786 | 555.6516 | 745.3943 | 875.2805 | 1135.323 | 1140.2447 | 608.0803 | 714.9231 | 662.7122 | 856.847 | 87.0806 | -0.00056021 | 17.7706 | 5.2968 | -40.0253 | 3.1216 | 9192.12 | 0.32 | 2.6592 | -0.95384 | -0.5627 | -2.5205 | 7.3709 | 5.6003 | 6.8995 | 84.9941 | 168.2871 | 53.4541 | 63.7615 | 18.8769 | 100.3823 | 37.4079
42810.4529 | 1114 | 17.4712 | 17.909 | 18.0536 | 18.099 | 17.4488 | 16.1031 | 14.9937 | 16.447 | 16.9373 | 17.0774 | 17.1002 | 16.6339 | 15.6752 | 14.4204 | 27.2427 | 44.7979 | 43.7408 | 88.495 | 46.6076 | 92.2093 |  |  |  | 35.876 | 88.6063 | 466.2513 | 691.1132 | 720.4454 | 697.9859 | 97.8132 | 127.9907 | 928.9299 | 93.6933 | 117.6322 | 847.5635 | 894.7819 | 866.6741 |  | 267.9493 | 927.6573 | 925.2307 | 527.9677 |  | 475.6032 | 716.0766 | 569.4399 | 721.2898 | 887.8396 | 1004.2325 | 1042.3729 | 59.2285 | 411.3395 | 91.7162 | 623.874 | 14.439 | 49.0826 | 48.3337 | 50.3145 | 62.3411 |  |  | 1.4978 | -0.37447 | -0.25311 | -1.0054 | 8.3613 | 5.6442 | 7.3911 | -2.8967 | 19.4522 | 52.792 | 25.0144 | -4.435e-05 | 1.64e-06 | -0.00074911 | 26.3328 | 16.3847 | 16.7219 | 17.1165 | 17.1216 | 16.1173 | 14.6421 | 16.6589 | 17.0456 | 17.3742 | 17.4455 | 17.1922 | 16.3849 | 14.6698 | 673.5121 | 460.3118 | 405.0345 | 254.7573 | 229.3065 | 726.0435 | 444.9047 | 20.1653 | 36.1543 | 42.1282 | 79.7888 | 84.2322 | 87.5388 |  |  |  | 627.832 | 594.3512 | 596.458 | 621.0664 | 83.2111 | 34.85 | 797.2002 |  |  | 590.1904 |  |  | 20.5829 | 54.6177 | 553.2868 | 20.6578 | 56.8483 | 844.5511 | 754.4161 | 630.4867 | 788.9953 | 771.0238 | 758.6329 |  | 827.4733 | 899.3216 | 1032.3274 | 603.537 | 699.9778 | 993.8397 |  | 1044.1007 |  |  | 451.4595 | 672.173 | 751.1883 | [6 empty] | 617.4958 |  |  | 417.4626 |  |  | 526.3612 | 671.2678 | 684.9685 | 1015.0061 | 1093.708 | 1080.5922 | 529.1887 | 721.1678 | 849.188 | 626.0249 | 706.8009 | 1073.5756 | 1114.3099 | 633.9763 | 815.1963 | 1124.8074 | 1139.2837 | 1091.1397 | 544.4644 | 665.0013 | 706.6462 | 555.9546 | 746.4427 | 875.396 | 1136.605 | 1140.8343 | 607.8384 | 712.9032 | 663.8334 | 856.8846 | 86.6912 | 0.00075871 | 17.7711 | 5.2833 | -40.1427 | 3.1217 | 9226.42 | 0.27 | 2.6579 | -1.3413 | -1.1027 | -2.1978 | 7.2022 | 5.9174 | 6.7715 | 85.115 | 168.3821 | 53.5256 | 62.3541 | 19.5035 | 115.6894 | 37.5514
42810.4529 | 1115 | 17.4713 | 17.9091 | 18.0639 | 18.1117 | 17.4552 | 16.1066 | 14.9996 | 16.4498 | 16.9382 | 17.0871 | 17.101 | 16.6365 | 15.6772 | 14.4307 | 27.3977 | 44.9669 | 43.9083 | 88.5431 | 47.0257 | 92.2073 |  |  |  | 36.0587 | 88.5677 | 467.9272 | 691.5583 | 721.0096 | 698.7209 | 91.3995 | 130.9281 | 936.0345 | 94.5192 | 118.0634 | 845.9385 | 912.5143 | 863.2986 |  | 280.4011 | 929.8963 | 928.7262 | 521.5891 |  | 476.183 | 715.2395 | 567.9343 | 718.2979 | 890.1808 | 1006.6286 | 1045.5325 | 57.8859 | 411.2814 | 92.159 | 623.5473 | 14.4489 | 49.0256 | 48.3465 | 50.305 | 62.5207 |  |  | 0.50554 | -0.44872 | 0.41518 | -0.91273 | 8.174 | 5.3333 | 7.4174 | -1.568 | 18.9957 | 50.7228 | 24.0686 | 7.228e-05 | 7.721e-05 | -0.00080004 | 26.4047 | 16.3815 | 16.7206 | 17.1127 | 17.1193 | 16.1121 | 14.6323 | 16.6558 | 17.0381 | 17.3767 | 17.4423 | 17.1906 | 16.3774 | 14.6697 | 690.369 | 472.0562 | 442.146 | 276.9335 | 238.0099 | 726.3642 | 445.0983 | 20.2264 | 36.2618 | 42.2432 | 79.8584 | 84.255 | 87.5729 |  |  |  | 627.8407 | 592.1034 | 594.5922 | 617.2259 | 70.5202 | 29.5341 | 800.3802 |  |  | 590.7788 |  |  | 20.6022 | 54.6988 | 555.0826 | 20.7242 | 56.9602 | 845.2163 | 751.7891 | 630.1662 | 789.2534 | 771.5143 | 753.664 |  | 827.4428 | 898.2049 | 1032.2289 | 604.1071 | 700.0673 | 996.2711 |  | 1044.1377 |  |  | 450.9357 | 664.6562 | 748.4986 | [6 empty] | 617.5685 |  |  | 418.9573 |  |  | 526.2139 | 672.9542 | 685.4932 | 1006.3189 | 1097.4662 | 1083.6111 | 529.3409 | 720.6127 | 848.1814 | 626.6014 | 707.9215 | 1071.3826 | 1119.5383 | 634.0271 | 814.4499 | 1129.461 | 1142.9729 | 1089.8 | 543.3856 | 664.2651 | 706.2081 | 556.6363 | 747.6866 | 875.5471 | 1137.3532 | 1141.6432 | 607.6714 | 711.6931 | 664.753 | 857.4768 | 89.418 | 0.00073764 | 17.7706 | 5.2535 | -40.0534 | 3.1216 | 9214.55 | 0.36 | 1.5447 | -1.4676 | 1.4117 | -2.0932 | 7.1278 | 5.7575 | 6.7899 | 85.243 | 168.3606 | 53.531 | 60.5894 | 15.4178 | 122.9137 | 37.6598
42810.453 | 1116 | 17.4668 | 17.9027 | 18.0479 | 18.0991 | 17.4482 | 16.1079 | 15.0021 | 16.4443 | 16.9361 | 17.0829 | 17.0914 | 16.6293 | 15.6744 | 14.4279 | 27.5401 | 45.1363 | 44.0733 | 88.5775 | 47.4528 | 92.2129 |  |  |  | 36.2522 | 88.5159 | 468.8929 | 691.8918 | 721.0551 | 699.0249 | 90.4289 | 122.1274 | 932.0199 | 95.6206 | 125.2934 | 844.8749 | 909.6761 | 860.7209 |  | 293.2327 | 917.2807 | 918.5632 | 540.6969 |  | 476.7363 | 715.2728 | 569.7523 | 717.7122 | 893.2952 | 1005.7793 | 1043.4242 | 55.8717 | 411.1648 | 91.8647 | 623.4348 | 14.4434 | 48.9643 | 48.3655 | 50.3007 | 62.7038 |  |  | 0.50028 | -0.51903 | 0.1543 | -1.4706 | 8.3232 | 5.6895 | 7.9457 | -3.1254 | 19.0484 | 50.7014 | 25.2565 | 1.807e-05 | 5.421e-05 | -0.00080825 | 26.4807 | 16.3867 | 16.724 | 17.1115 | 17.1194 | 16.1137 | 14.6346 | 16.6557 | 17.0386 | 17.3776 | 17.4498 | 17.1949 | 16.383 | 14.6685 | 695.1704 | 471.6506 | 413.1766 | 274.0929 | 243.4231 | 726.1162 | 444.6561 | 20.298 | 36.3715 | 42.3623 | 79.9196 | 84.2831 | 87.61 |  |  |  | 627.9646 | 590.8374 | 593.4197 | 616.6636 | 68.8241 | 19.0555 | 801.0292 |  |  | 593.5626 |  |  | 20.6321 | 54.7899 | 555.9663 | 20.7739 | 57.0497 | 844.3582 | 750.1042 | 631.5673 | 789.1317 | 771.0939 | 750.0307 |  | 827.2251 | 896.3212 | 1032.5237 | 605.3307 | 700.0517 | 996.7245 |  | 1045.174 |  |  | 450.482 | 658.5982 | 745.6558 | [6 empty] | 618.9048 |  |  | 421.1039 |  |  | 526.1559 | 674.637 | 685.8241 | 996.428 | 1094.0198 | 1085.0293 | 529.9024 | 720.9181 | 847.9459 | 627.6183 | 708.2406 | 1067.0885 | 1117.0657 | 634.8489 | 814.4598 | 1130.466 | 1140.5737 | 1089.8461 | 542.9957 | 664.2077 | 706.5169 | 556.801 | 748.3227 | 875.3129 | 1133.6729 | 1141.0899 | 608.0257 | 712.0633 | 664.6552 | 857.6275 | 91.1564 | 0.00066049 | 17.7682 | 5.2356 | -40.0702 | 3.1216 | 9186.37 | 0.26 | 1.5369 | -1.5785 | 0.86064 | -2.657 | 7.1901 | 5.9447 | 7.0252 | 85.2721 | 168.5699 | 53.4933 | 59.9722 | 18.5503 | 121.235 | 37.6994
42810.453 | 1117 | 17.4717 | 17.9007 | 18.0466 | 18.0899 | 17.4481 | 16.1015 | 14.997 | 16.4405 | 16.9348 | 17.079 | 17.0954 | 16.6295 | 15.6707 | 14.4254 | 27.6804 | 45.3024 | 44.233 | 88.607 | 47.8556 | 92.2196 |  |  |  | 36.4504 | 88.4537 | 468.788 | 691.5365 | 719.9375 | 698.4504 | 86.8421 | 121.9568 | 930.2269 | 91.425 | 125.6011 | 844.5197 | 856.2125 | 863.2901 |  | 260.9089 | 931.0795 | 925.4189 | 523.4004 |  | 476.2265 | 715.9984 | 571.4247 | 719.1223 | 896.4564 | 1003.2106 | 1041.4186 | 53.6543 | 410.7882 | 89.0079 | 623.2865 | 14.4439 | 48.9143 | 48.3628 | 50.308 | 62.907 |  |  | 0.84198 | -0.012397 | -0.32539 | -1.1513 | 7.4289 | 5.2098 | 6.9726 | -2.9946 | 19.7529 | 52.3483 | 23.7229 | 3.614e-05 | 3.45e-05 | -0.00080825 | 26.5514 | 16.3832 | 16.7216 | 17.1095 | 17.1187 | 16.1161 | 14.6378 | 16.6595 | 17.0357 | 17.3717 | 17.4501 | 17.198 | 16.3858 | 14.6646 | 700.5918 | 452.1725 | 376.0035 | 255.4014 | 224.755 | 725.7822 | 443.4039 | 20.3845 | 36.5053 | 42.4924 | 79.9903 | 84.3045 | 87.6479 |  |  |  | 628.2898 | 590.6904 | 593.8369 | 618.3142 | 68.7554 | 20.9318 | 799.8617 |  |  | 595.6646 |  |  | 20.6647 | 54.8599 | 555.5835 | 20.8071 | 57.1456 | 846.1401 | 750.5994 | 632.8593 | 790.22 | 772.6025 | 750.4019 |  | 827.1148 | 892.6064 | 1033.0711 | 607.6386 | 700.1645 | 990.6785 |  | 1045.3468 |  |  | 450.5192 | 659.9173 | 745.3263 | [6 empty] | 620.6755 |  |  | 424.2038 |  |  | 526.5486 | 674.9403 | 685.8067 | 993.4716 | 1089.1322 | 1084.4534 | 530.864 | 721.3454 | 847.0686 | 628.2703 | 707.4606 | 1068.8146 | 1117.681 | 635.6086 | 813.487 | 1129.9846 | 1136.2115 | 1089.6573 | 544.3171 | 665.0244 | 706.9697 | 556.6405 | 748.0583 | 874.5616 | 1130.184 | 1140.7421 | 609.1716 | 712.8163 | 664.123 | 856.9035 | 92.0946 | -0.0006654 | 17.7666 | 5.2138 | -40.0753 | 3.1216 | 9150.35 | 0.26 | 1.9933 | -0.24404 | -1.2503 | -2.3517 | 6.786 | 5.6828 | 6.5743 | 85.2254 | 168.9649 | 53.4559 | 59.2571 | 22.4368 | 101.4842 | 37.7166
42810.453 | 1118 | 17.4679 | 17.8997 | 18.0529 | 18.0879 | 17.4522 | 16.1044 | 15.0033 | 16.4466 | 16.9357 | 17.0813 | 17.1051 | 16.6473 | 15.6776 | 14.4299 | 27.8283 | 45.4804 | 44.3891 | 88.6297 | 48.2655 | 92.229 |  |  |  | 36.6437 | 88.4037 | 468.2242 | 690.7222 | 718.3536 | 697.4515 | 85.5076 | 125.0374 | 934.024 | 91.1733 | 121.905 | 835.0954 | 881.208 | 859.4854 |  | 247.7729 | 929.1556 | 926.7171 | 515.5913 |  | 475.5922 | 717.1644 | 570.0677 | 721.3904 | 898.5622 | 1001.6961 | 1041.3263 | 52.5883 | 410.4369 | 85.4541 | 623.3175 | 14.4282 | 48.8976 | 48.3664 | 50.3258 | 63.107 |  |  | 0.79073 | -0.42704 | -0.73018 | -1.3109 | 7.348 | 5.6461 | 7.3517 | -3.45 | 19.7593 | 53.3587 | 25.0347 | -1.15e-05 | 7.721e-05 | -0.00078197 | 26.6262 | 16.4042 | 16.7314 | 17.121 | 17.1245 | 16.1255 | 14.6496 | 16.6639 | 17.0393 | 17.3744 | 17.4602 | 17.1994 | 16.386 | 14.6671 | 697.6043 | 451.6609 | 362.1178 | 247.8025 | 217.2543 | 725.0927 | 442.0987 | 20.4491 | 36.6064 | 42.595 | 80.0581 | 84.33 | 87.6798 |  |  |  | 628.6485 | 591.433 | 594.3926 | 620.201 | 65.0565 | 21.5852 | 800.1219 |  |  | 597.8479 |  |  | 20.6884 | 54.9514 | 554.5588 | 20.8659 | 57.2413 | 847.6003 | 751.0669 | 633.0445 | 790.1336 | 772.856 | 751.2407 |  | 827.3261 | 890.7777 | 1032.679 | 609.0613 | 700.2624 | 992.584 |  | 1045.6098 |  |  | 451.0885 | 663.7556 | 746.1432 | [6 empty] | 621.3257 |  |  | 427.5505 |  |  | 526.7768 | 674.1417 | 685.3462 | 992.8492 | 1087.5721 | 1082.5633 | 531.5074 | 721.4967 | 846.0201 | 628.0152 | 706.5915 | 1068.7535 | 1120.9957 | 635.9696 | 812.6284 | 1128.3962 | 1135.1492 | 1087.8211 | 545.5175 | 666.5074 | 707.513 | 557.0056 | 748.2839 | 873.7172 | 1128.8939 | 1141.7933 | 609.8911 | 714.0718 | 663.9654 | 856.4163 | 90.6052 | -0.0010442 | 17.7634 | 5.1892 | -40.0503 | 3.1216 | 9127.74 | 0.4 | 1.9306 | -1.4331 | -1.874 | -2.511 | 6.745 | 5.9125 | 6.7467 | 85.2718 | 168.8066 | 53.4396 | 59.3568 | 23.726 | 110.8365 | 37.7338
42810.453 | 1119 | 17.4644 | 17.891 | 18.0506 | 18.091 | 17.4504 | 16.1029 | 15.0114 | 16.4513 | 16.9411 | 17.0841 | 17.098 | 16.638 | 15.6736 | 14.4283 | 27.9805 | 45.6501 | 44.5647 | 88.6578 | 48.7896 | 92.2503 |  |  |  | 36.8416 | 88.3533 | 467.3204 | 689.3949 | 716.3762 | 695.9017 | 79.4419 | 116.1564 | 925.7205 | 88.3472 | 120.7542 | 830.0963 | 904.7953 | 851.2061 |  | 270.3739 | 925.3387 | 922.7019 | 517.6469 |  | 474.6615 | 717.034 | 567.7274 | 721.875 | 899.5963 | 1002.1711 | 1041.4433 | 53.1558 | 410.0571 | 81.5677 | 623.0722 | 14.4144 | 48.9026 | 48.3453 | 50.3358 | 63.327 |  |  | 1.5642 | -0.83971 | -0.077004 | -0.34433 | 7.3855 | 5.1231 | 7.6921 | -3.4921 | 20.001 | 52.6953 | 23.5588 | -2.464e-05 | 7.557e-05 | -0.00079018 | 26.7036 | 16.4094 | 16.7321 | 17.1245 | 17.1275 | 16.1226 | 14.647 | 16.6628 | 17.0377 | 17.3747 | 17.4564 | 17.1955 | 16.3898 | 14.6691 | 690.8297 | 444.6348 | 355.8875 | 245.5271 | 207.2933 | 724.2367 | 440.8834 | 20.515 | 36.7286 | 42.7123 | 80.1367 | 84.363 | 87.7316 |  |  |  | 629.1092 | 592.1521 | 595.1069 | 621.7323 | 71.5669 | 23.1082 | 799.6961 |  |  | 600.2766 |  |  | 20.7182 | 55.0314 | 552.4562 | 20.9144 | 57.3517 | 845.2839 | 751.6555 | 631.6869 | 790.8215 | 773.5718 | 752.1243 |  | 827.5744 | 887.7326 | 1031.2117 | 608.8137 | 700.3252 | 996.1971 |  | 1045.4583 |  |  | 451.1303 | 665.3808 | 746.9746 | [6 empty] | 620.7842 |  |  | 429.0281 |  |  | 526.5906 | 673.762 | 685.1018 | 989.2047 | 1084.2854 | 1080.8332 | 531.646 | 721.8439 | 845.7281 | 627.5646 | 706.3359 | 1063.8384 | 1121.9355 | 636.08 | 812.5104 | 1126.6804 | 1136.1655 | 1087.3016 | 546.1297 | 668.3498 | 708.1073 | 557.6594 | 749.1382 | 872.3993 | 1129.5655 | 1143.0924 | 610.2387 | 715.3647 | 663.9688 | 855.0318 | 84.6962 | 0.00068152 | 17.7612 | 5.1802 | -40.1573 | 3.1216 | 9110.75 | 0.39 | 2.7132 | -2.0095 | -0.60853 | -1.2868 | 6.7634 | 5.633 | 6.9024 | 85.3292 | 168.1107 | 53.4613 | 59.8215 | 24.1826 | 119.9192 | 37.7807
42810.453 | 1120 | 17.4593 | 17.8902 | 18.0433 | 18.0861 | 17.446 | 16.0954 | 15.0099 | 16.4501 | 16.9383 | 17.0813 | 17.0979 | 16.6366 | 15.6719 | 14.4271 | 28.1269 | 45.8099 | 44.7259 | 88.6816 | 49.2452 | 92.2719 |  |  |  | 37.0424 | 88.3039 | 467.3258 | 688.3994 | 715.2333 | 695.2823 | 86.7446 | 108.7201 | 901.4736 | 75.0832 | 110.2696 | 827.1194 | 899.7785 | 849.1965 |  | 290.6222 | 909.0361 | 902.2949 | 520.645 |  | 474.1181 | 716.968 | 567.1192 | 720.9342 | 893.2828 | 999.7661 | 1039.6782 | 52.4293 | 409.9035 | 79.7721 | 622.4957 | 14.4145 | 48.8683 | 48.3174 | 50.3488 | 63.5695 |  |  | 1.4413 | -0.51772 | -0.59087 | -1.052 | 8.1832 | 5.6678 | 7.6665 | -2.1555 | 19.5579 | 52.5535 | 22.1416 | 8.378e-05 | -6.57e-06 | -0.00078197 | 26.7833 | 16.4171 | 16.7298 | 17.1199 | 17.1306 | 16.1295 | 14.6486 | 16.6597 | 17.0402 | 17.3792 | 17.454 | 17.1975 | 16.3859 | 14.6634 | 693.6607 | 445.4444 | 380.1366 | 249.203 | 202.4662 | 724.6615 | 440.0142 | 20.5868 | 36.8401 | 42.8262 | 80.2037 | 84.393 | 87.7789 |  |  |  | 629.6256 | 593.521 | 595.8843 | 623.9822 | 79.3368 | 30.7468 | 799.6829 |  |  | 601.2817 |  |  | 20.7408 | 55.1109 | 551.2553 | 20.9508 | 57.4491 | 840.0496 | 750.2024 | 631.6543 | 789.1952 | 771.4324 | 751.5703 |  | 827.1699 | 885.6773 | 1029.7509 | 608.4604 | 700.58 | 994.0697 |  | 1044.1758 |  |  | 450.8572 | 665.6878 | 745.7973 | [6 empty] | 620.3234 |  |  | 427.6671 |  |  | 526.7735 | 673.9945 | 684.8596 | 992.8771 | 1082.1235 | 1079.8416 | 531.4046 | 723.3253 | 849.306 | 627.5374 | 706.1392 | 1066.954 | 1120.5311 | 636.1178 | 815.2642 | 1129.5932 | 1138.2059 | 1088.2761 | 546.7457 | 668.825 | 707.9135 | 558.2634 | 749.4388 | 872.6497 | 1129.8044 | 1143.9431 | 610.4128 | 715.2409 | 664.3385 | 855.0939 | 91.2803 | -0.005506 | 17.7607 | 5.1598 | -40.1354 | 3.1216 | 9114.43 | 0.33 | 2.6036 | -1.5778 | -1.6856 | -2.2492 | 7.1126 | 5.9194 | 6.8844 | 85.2111 | 167.3932 | 53.5315 | 59.6498 | 21.3201 | 117.8486 | 37.8187
42810.453 | 1121 | 17.4617 | 17.893 | 18.0422 | 18.0841 | 17.4453 | 16.0962 | 15.0152 | 16.4566 | 16.9319 | 17.0825 | 17.0996 | 16.6319 | 15.6682 | 14.4277 | 28.278 | 45.9805 | 44.8803 | 88.7212 | 49.6804 | 92.301 |  |  |  | 37.2494 | 88.2465 | 468.4737 | 688.3333 | 715.5535 | 695.7136 | 88.5392 | 117.044 | 905.6888 | 77.9924 | 110.2179 | 827.3685 | 901.5311 | 848.0513 |  | 271.664 | 910.8134 | 906.2363 | 526.7823 |  | 473.8921 | 716.1215 | 565.8347 | 717.3916 | 883.3726 | 1000.3792 | 1040.07 | 51.8771 | 409.7119 | 79.5213 | 622.1001 | 14.4388 | 48.8316 | 48.2929 | 50.3663 | 63.8332 |  |  | 0.60674 | -0.59592 | -0.97988 | -0.72809 | 7.6391 | 5.2341 | 8.2552 | -2.9716 | 19.0362 | 50.9523 | 21.7993 | 0.00010021 | 8.214e-05 | -0.00078854 | 26.8521 | 16.4109 | 16.7244 | 17.1158 | 17.123 | 16.1263 | 14.6439 | 16.6598 | 17.0368 | 17.378 | 17.453 | 17.1962 | 16.3864 | 14.6675 | 701.8992 | 462.8221 | 403.6451 | 253.7952 | 203.875 | 724.9924 | 439.5815 | 20.665 | 36.9665 | 42.954 | 80.2874 | 84.4351 | 87.8267 |  |  |  | 630.1082 | 594.2839 | 596.2173 | 624.4455 | 68.8093 | 28.7007 | 798.1082 |  |  | 602.0727 |  |  | 20.7906 | 55.1996 | 552.6318 | 21.0067 | 57.5631 | 836.4644 | 750.8568 | 632.2279 | 787.7909 | 769.823 | 752.1755 |  | 826.8178 | 883.3106 | 1028.1421 | 608.7265 | 700.9056 | 994.4514 |  | 1043.6919 |  |  | 451.7175 | 668.3574 | 745.2517 | [6 empty] | 620.6679 |  |  | 426.3827 |  |  | 527.5783 | 674.1293 | 685.2324 | 1000.7534 | 1091.3041 | 1080.1374 | 530.8808 | 725.0046 | 853.7364 | 627.8819 | 706.8872 | 1065.9994 | 1122.8432 | 635.7502 | 818.8884 | 1133.8834 | 1135.9647 | 1090.2714 | 546.7244 | 668.04 | 707.2197 | 558.4235 | 749.2324 | 873.8613 | 1129.4661 | 1143.0744 | 610.2032 | 714.0773 | 664.4906 | 856.5267 | 95.7106 | 0.00080782 | 17.7585 | 5.1425 | -40.0526 | 3.1215 | 9170.65 | 0.28 | 1.6897 | -1.6921 | -2.1698 | -1.8703 | 6.8737 | 5.6898 | 7.1456 | 85.0781 | 166.6088 | 53.6014 | 58.8458 | 18.6244 | 118.3697 | 37.8998
42810.453 | 1122 | 17.4655 | 17.8879 | 18.0383 | 18.0875 | 17.4446 | 16.0974 | 15.0191 | 16.444 | 16.9282 | 17.0797 | 17.0972 | 16.6303 | 15.6667 | 14.4293 | 28.4382 | 46.168 | 45.0594 | 88.7829 | 50.2935 | 92.3227 |  |  |  | 37.4425 | 88.2146 | 471.4922 | 688.9456 | 716.6923 | 695.7926 | 94.6941 | 130.1866 | 924.8668 | 92.8292 | 123.2658 | 834.6428 | 907.6643 | 853.5813 |  | 260.8992 | 918.1749 | 918.7303 | 516.3865 |  | 475.0449 | 713.4485 | 564.4306 | 717.5543 | 881.3907 | 999.5133 | 1041.1916 | 51.0052 | 409.4012 | 81.1658 | 622.0109 | 14.4337 | 48.828 | 48.278 | 50.3779 | 64.0389 |  |  | 0.83213 | -0.3403 | -0.022464 | -0.64595 | 8.1813 | 6.231 | 7.8721 | -2.5294 | 20.2561 | 52.5092 | 23.4598 | 9.86e-06 | 2.3e-05 | -0.0007754 | 26.9281 | 16.4071 | 16.7274 | 17.1161 | 17.1239 | 16.1154 | 14.6512 | 16.663 | 17.0446 | 17.3808 | 17.4569 | 17.1988 | 16.3842 | 14.6705 | 697.0519 | 474.3544 | 417.4833 | 263.5 | 203.4744 | 724.7069 | 439.2691 | 20.7404 | 37.0884 | 43.0629 | 80.3822 | 84.4568 | 87.859 |  |  |  | 630.2485 | 592.5777 | 594.9403 | 619.9636 | 67.9991 | 29.3841 | 796.5189 |  |  | 603.5143 |  |  | 20.8175 | 55.281 | 555.2114 | 21.0395 | 57.6558 | 837.0988 | 754.6302 | 634.2454 | 788.9008 | 771.3871 | 756.4772 |  | 827.2131 | 884.4635 | 1026.9213 | 610.5371 | 701.2976 | 997.1461 |  | 1043.0597 |  |  | 453.1443 | 675.2714 | 748.4732 | [6 empty] | 622.6356 |  |  | 426.73 |  |  | 528.3293 | 674.5396 | 686.1743 | 1010.1628 | 1100.6414 | 1084.6074 | 530.418 | 725.2802 | 854.868 | 628.2086 | 707.08 | 1067.2829 | 1123.4738 | 635.0612 | 819.6266 | 1134.8366 | 1134.0717 | 1095.6289 | 546.9304 | 667.5218 | 706.6296 | 558.8486 | 748.1433 | 873.883 | 1131.5273 | 1142.8839 | 610.3404 | 713.3359 | 664.0226 | 854.7666 | 93.6958 | -0.0012898 | 17.7566 | 5.1306 | -40.1806 | 3.1216 | 9232.62 | 0.29 | 1.9788 | -1.2769 | -0.32808 | -1.7593 | 7.111 | 6.2059 | 6.9754 | 85.089 | 165.9336 | 53.6442 | 59.2883 | 17.0264 | 121.1013 | 38.0517
42810.453 | 1123 | 17.4624 | 17.8907 | 18.0416 | 18.0942 | 17.4448 | 16.099 | 15.0233 | 16.4489 | 16.9359 | 17.0779 | 17.1041 | 16.6348 | 15.6663 | 14.4259 | 28.5726 | 46.323 | 45.209 | 88.8409 | 50.7385 | 92.3416 |  |  |  | 37.6443 | 88.1612 | 473.1888 | 689.2908 | 716.9631 | 696.059 | 92.1642 | 125.8575 | 928.647 | 97.1085 | 127.2658 | 832.8139 | 909.8846 | 854.6486 |  | 270.902 | 913.1727 | 917.2692 | 522.3877 |  | 474.8015 | 712.8362 | 563.9692 | 718.6615 | 883.973 | 1001.8361 | 1042.8446 | 49.7287 | 409.1745 | 81.1293 | 621.9987 | 14.422 | 48.831 | 48.2749 | 50.388 | 64.2207 |  |  | 0.97538 | 0.11574 | -0.27742 | -1.3438 | 8.0577 | 5.3682 | 7.9076 | -2.6523 | 20.0471 | 53.2211 | 22.5696 | 4.6e-05 | 4.764e-05 | -0.00080989 | 26.9989 | 16.4173 | 16.7237 | 17.1162 | 17.1239 | 16.1167 | 14.6438 | 16.6647 | 17.0439 | 17.3803 | 17.4581 | 17.2073 | 16.3879 | 14.6729 | 690.9946 | 462.3983 | 408.0893 | 265.5296 | 227.9708 | 724.2726 | 438.896 | 20.8119 | 37.2021 | 43.1912 | 80.4543 | 84.497 | 87.8995 |  |  |  | 630.005 | 589.6766 | 592.6425 | 615.2084 | 77.5091 | 22.699 | 797.5622 |  |  | 606.9209 |  |  | 20.8424 | 55.3521 | 557.869 | 21.0988 | 57.7461 | 840.3583 | 758.0118 | 636.3704 | 791.3667 | 774.3369 | 761.2439 |  | 827.852 | 887.4798 | 1027.3907 | 613.1506 | 701.7462 | 991.4655 |  | 1044.3139 |  |  | 454.8194 | 682.0541 | 752.9167 | [6 empty] | 625.1217 |  |  | 428.2882 |  |  | 528.3753 | 674.3853 | 686.429 | 1023.2035 | 1100.7842 | 1086.2497 | 530.3221 | 724.3345 | 854.3622 | 628.5554 | 706.2542 | 1069.1608 | 1122.0117 | 635.3764 | 817.1669 | 1136.9587 | 1135.6543 | 1093.6416 | 547.0958 | 667.4186 | 706.3001 | 559.5389 | 747.1194 | 872.4044 | 1128.5187 | 1140.3719 | 610.7854 | 713.6842 | 663.8089 | 852.3323 | 93.7022 | -0.00093198 | 17.7566 | 5.1166 | -40.0573 | 3.1215 | 9253.5 | 0.29 | 2.1427 | 0.74446 | -1.1526 | -2.5367 | 7.0636 | 5.7654 | 6.9975 | 85.1676 | 166.0969 | 53.6783 | 59.8153 | 17.9982 | 121.8277 | 38.1363
42810.453 | 1124 | 17.4569 | 17.8851 | 18.0349 | 18.0905 | 17.44 | 16.0905 | 15.0212 | 16.4487 | 16.9293 | 17.0811 | 17.0994 | 16.6285 | 15.6696 | 14.4268 | 28.7406 | 46.5116 | 45.3873 | 88.9009 | 51.3883 | 92.3382 |  |  |  | 37.8497 | 88.1105 | 472.9709 | 688.5871 | 715.9971 | 695.3336 | 90.2582 | 122.8405 | 918.8992 | 91.404 | 129.3648 | 840.9295 | 881.7076 | 858.1864 |  | 245.4423 | 919.5145 | 914.485 | 541.2527 |  | 474.4287 | 715.8389 | 565.7461 | 721.4046 | 892.403 | 1007.5567 | 1047.0002 | 48.4749 | 409.0182 | 80.288 | 622.1466 | 14.4315 | 48.8138 | 48.2827 | 50.3965 | 64.4849 |  |  | 1.1114 | -0.55912 | -0.47324 | -0.84308 | 7.7495 | 5.8597 | 8.2395 | -2.3947 | 19.8747 | 54.3137 | 23.0646 | 5.75e-05 | 5.914e-05 | -0.00079347 | 27.0691 | 16.4124 | 16.7175 | 17.11 | 17.1173 | 16.1183 | 14.6382 | 16.6645 | 17.0396 | 17.3718 | 17.4522 | 17.202 | 16.388 | 14.674 | 703.1204 | 455.8077 | 396.7584 | 250.854 | 218.0981 | 724.6916 | 438.1133 | 20.8826 | 37.3153 | 43.3048 | 80.5114 | 84.5133 | 87.9349 |  |  |  | 629.8263 | 588.1835 | 590.5578 | 614.2852 | 70.3721 | 27.3011 | 799.9721 |  |  | 610.1555 |  |  | 20.8746 | 55.4342 | 557.8538 | 21.1324 | 57.8409 | 841.4444 | 759.3273 | 636.9982 | 792.9055 | 775.7466 | 762.7517 |  | 828.079 | 887.6881 | 1027.3007 | 614.7195 | 701.9721 | 995.4358 |  | 1044.9166 |  |  | 454.6617 | 683.6292 | 754.9743 | [6 empty] | 625.9655 |  |  | 429.9838 |  |  | 528.2125 | 673.8349 | 686.3905 | 1036.4218 | 1105.2309 | 1086.1026 | 530.7598 | 724.0131 | 852.5174 | 628.6269 | 705.4147 | 1074.898 | 1122.8534 | 636.5779 | 815.6117 | 1130.9625 | 1136.1252 | 1088.9748 | 547.4749 | 667.8286 | 705.9373 | 560.2823 | 746.5615 | 870.8348 | 1122.4489 | 1138.7911 | 610.5659 | 713.0346 | 664.3052 | 852.7365 | 91.9307 | -0.0002375 | 17.7552 | 5.1078 | -40.0874 | 3.1215 | 9268.93 | 0.39 | 2.2864 | -1.6388 | -1.5077 | -2.0123 | 6.9427 | 6.0371 | 7.1588 | 85.2007 | 166.0437 | 53.6885 | 58.6089 | 19.1062 | 110.3119 | 38.1271
42810.4531 | 1125 | 17.4616 | 17.8945 | 18.039 | 18.0841 | 17.4384 | 16.0951 | 15.03 | 16.4503 | 16.9331 | 17.0847 | 17.0995 | 16.6385 | 15.6716 | 14.432 | 28.8939 | 46.6741 | 45.5486 | 88.945 | 51.9376 | 92.3428 |  |  |  | 38.0506 | 88.0647 | 474.1297 | 688.4864 | 715.9457 | 695.3952 | 81.0053 | 125.8528 | 922.3105 | 85.6262 | 112.8168 | 832.6882 | 910.5879 | 858.5791 |  | 235.5578 | 920.1445 | 919.3846 | 529.978 |  | 474.0114 | 715.8365 | 564.4237 | 722.1611 | 899.5075 | 1009.2926 | 1050.1471 | 48.9027 | 408.865 | 80.0139 | 622.4959 | 14.4612 | 48.8187 | 48.3037 | 50.4058 | 64.7264 |  |  | 0.61462 | -0.16091 | -0.62438 | -1.2452 | 7.7824 | 6.2244 | 8.5253 | -1.7185 | 20.3291 | 53.3711 | 25.5936 | -1.643e-05 | 5.586e-05 | -0.00078525 | 27.1424 | 16.4154 | 16.7215 | 17.1109 | 17.1221 | 16.1208 | 14.6433 | 16.6727 | 17.0445 | 17.3876 | 17.4619 | 17.2024 | 16.3956 | 14.685 | 700.4499 | 457.4124 | 413.5011 | 253.2524 | 212.6433 | 724.7327 | 437.567 | 20.9577 | 37.4353 | 43.4201 | 80.5628 | 84.5401 | 87.9847 |  |  |  | 629.8031 | 587.7784 | 589.459 | 614.5678 | 82.812 | 28.2635 | 801.767 |  |  | 612.4272 |  |  | 20.9113 | 55.4991 | 558.1738 | 21.184 | 57.9325 | 841.442 | 759.7731 | 636.3559 | 793.5215 | 776.0539 | 762.9668 |  | 828.4751 | 890.6938 | 1027.8643 | 614.8531 | 702.1492 | 993.3447 |  | 1045.7694 |  |  | 454.5398 | 684.633 | 756.2165 | [6 empty] | 625.7081 |  |  | 431.1604 |  |  | 527.8579 | 673.2591 | 686.7771 | 1042.3908 | 1109.1054 | 1087.7009 | 531.6206 | 724.7555 | 853.2398 | 628.155 | 705.6635 | 1076.9608 | 1126.2885 | 637.9701 | 815.2882 | 1120.6742 | 1137.8657 | 1085.985 | 547.3766 | 668.0507 | 705.8071 | 561.0692 | 748.1778 | 873.2439 | 1124.3916 | 1137.1809 | 610.1855 | 712.7178 | 665.2987 | 857.568 | 89.9426 | 0.00028166 | 17.7564 | 5.1 | -40.0163 | 3.1215 | 9270.71 | 0.32 | 1.7003 | -0.87912 | -1.7318 | -2.4456 | 6.9621 | 6.2264 | 7.2869 | 85.3258 | 166.2572 | 53.7269 | 58.9194 | 17.1407 | 121.9007 | 38.1147
42810.4531 | 1126 | 17.4622 | 17.8947 | 18.0462 | 18.0882 | 17.4477 | 16.1015 | 15.042 | 16.4534 | 16.941 | 17.0893 | 17.1032 | 16.641 | 15.674 | 14.4391 | 29.0381 | 46.839 | 45.706 | 88.988 | 52.3021 | 92.3455 |  |  |  | 38.2518 | 88.0215 | 475.8168 | 689.4416 | 716.8199 | 696.5447 | 89.3282 | 124.1887 | 927.7389 | 92.2592 | 125.0868 | 837.9692 | 907.1822 | 856.4149 |  | 231.1052 | 928.8537 | 927.3372 | 511.1712 |  | 473.6221 | 715.7475 | 564.3607 | 721.5625 | 898.5464 | 1011.5025 | 1051.2842 | 49.8849 | 408.8689 | 79.6377 | 622.8045 | 14.4835 | 48.829 | 48.3351 | 50.4229 | 64.9856 |  |  | 0.94187 | -0.26736 | 0.16744 | -0.80299 | 8.3219 | 4.8339 | 7.1585 | -2.2646 | 20.7527 | 53.0125 | 23.8153 | 5.75e-05 | 2.464e-05 | -0.00077704 | 27.2114 | 16.4096 | 16.7105 | 17.0986 | 17.1141 | 16.1055 | 14.6271 | 16.6627 | 17.0335 | 17.3806 | 17.449 | 17.195 | 16.3879 | 14.67 | 722.3845 | 472.7904 | 432.8718 | 266.4418 | 206.3102 | 725.6838 | 437.1917 | 21.0359 | 37.5493 | 43.526 | 80.6105 | 84.562 | 88.0205 |  |  |  | 629.8373 | 587.0108 | 588.7893 | 614.7647 | 84.5033 | 33.3289 | 801.8683 |  |  | 613.126 |  |  | 20.9441 | 55.5846 | 559.6678 | 21.2407 | 58.0263 | 840.3867 | 757.2715 | 635.2796 | 793.5263 | 776.6095 | 759.7568 |  | 828.5305 | 888.6457 | 1027.3784 | 614.0632 | 702.4434 | 984.5567 |  | 1047.1688 |  |  | 453.9646 | 677.2643 | 754.4356 | [6 empty] | 624.468 |  |  | 430.3613 |  |  | 527.6658 | 672.7938 | 686.6528 | 1038.1623 | 1111.2411 | 1088.1002 | 532.3002 | 725.959 | 853.0776 | 627.4601 | 705.7986 | 1078.6852 | 1128.9948 | 639.0721 | 816.2858 | 1108.0795 | 1141.4942 | 1085.4984 | 548.0035 | 667.8589 | 706.1293 | 561.1806 | 749.0402 | 876.9598 | 1121.3095 | 1139.706 | 610.2992 | 714.5625 | 665.5926 | 856.4548 | 91.77 | -0.00084081 | 17.7575 | 5.0986 | -40.1094 | 3.1215 | 9235 | 0.25 | 2.1061 | -1.1332 | 0.89676 | -1.9638 | 7.2056 | 5.4917 | 6.683 | 85.4333 | 166.058 | 53.819 | 56.8025 | 14.9162 | 121.0528 | 38.1159
42810.4531 | 1127 | 17.4596 | 17.9007 | 18.0432 | 18.0882 | 17.4484 | 16.0997 | 15.0418 | 16.4534 | 16.9409 | 17.0921 | 17.1064 | 16.6457 | 15.6772 | 14.4397 | 29.1856 | 47.0105 | 45.876 | 89.0366 | 52.8227 | 92.3636 |  |  |  | 38.4087 | 87.9909 | 476.6216 | 689.4381 | 715.8764 | 696.1858 | 90.0746 | 124.7053 | 926.9347 | 91.4448 | 126.379 | 839.1998 | 907.9192 | 858.0155 |  | 240.7173 | 928.3397 | 928.1806 | 494.4441 |  | 473.4944 | 718.106 | 565.1057 | 725.3118 | 899.3912 | 1012.3653 | 1050.4829 | 50.2715 | 408.9447 | 78.903 | 623.1648 | 14.5147 | 48.8288 | 48.3533 | 50.4363 | 65.2441 |  |  | 0.99641 | 0.1164 | 0.20161 | -0.91208 | 8.4106 | 5.6908 | 8.3032 | -2.8126 | 20.2509 | 53.8603 | 24.894 | -1.64e-06 | 2.629e-05 | -0.00079018 | 27.2968 | 16.4179 | 16.7161 | 17.1056 | 17.1204 | 16.1074 | 14.6434 | 16.6632 | 17.0417 | 17.3798 | 17.4521 | 17.1996 | 16.392 | 14.6689 | 733.3257 | 488.8226 | 457.043 | 283.7507 | 210.9995 | 726.728 | 437.1139 | 21.1187 | 37.6734 | 43.6572 | 80.6817 | 84.5986 | 88.0761 |  |  |  | 630.0054 | 587.8683 | 588.8682 | 616.3766 | 73.6462 | 34.1696 | 801.7477 |  |  | 614.6108 |  |  | 20.9711 | 55.6819 | 560.7765 | 21.2934 | 58.1304 | 841.6853 | 755.9386 | 634.8416 | 794.5669 | 778.2266 | 757.4138 |  | 828.7333 | 888.6776 | 1026.7614 | 612.8764 | 702.5609 | 976.8738 |  | 1047.7616 |  |  | 453.5674 | 671.3205 | 752.1026 | [6 empty] | 623.6155 |  |  | 428.9074 |  |  | 527.6875 | 672.5813 | 686.416 | 1038.5182 | 1110.9521 | 1087.6238 | 532.8778 | 727.3295 | 853.0414 | 627.504 | 706.1277 | 1082.2535 | 1129.9453 | 640.4115 | 818.3231 | 1106.7891 | 1142.5803 | 1088.0303 | 548.8742 | 669.1782 | 707.1468 | 561.7267 | 748.5844 | 874.8381 | 1118.683 | 1140.5862 | 610.5195 | 716.3372 | 666.0767 | 854.3538 | 91.3394 | 0.00042899 | 17.7591 | 5.0978 | -40.0866 | 3.1215 | 9212.83 | 0.32 | 2.1658 | 0.74857 | 0.98519 | -2.0954 | 7.2463 | 5.9606 | 7.1999 | 85.5656 | 165.7324 | 53.88 | 55.9393 | 12.2155 | 121.8131 | 38.1039
42810.4531 | 1128 | 17.4621 | 17.8958 | 18.0371 | 18.0939 | 17.4466 | 16.1027 | 15.0404 | 16.4534 | 16.9379 | 17.0852 | 17.1025 | 16.6406 | 15.6752 | 14.4316 | 29.3358 | 47.1734 | 46.0279 | 89.0898 | 53.2769 | 92.3776 |  |  |  | 38.0511 | 87.9482 | 475.8536 | 688.0608 | 714.0258 | 694.5061 | 95.9765 | 124.96 | 925.2644 | 90.5036 | 124.7067 | 838.3473 | 910.0142 | 857.3951 |  | 245.269 | 923.6315 | 921.2397 | 520.7558 |  | 473.2304 | 720.1216 | 565.1755 | 727.3879 | 899.5857 | 1014.9738 | 1050.6549 | 50.336 | 408.9867 | 78.8463 | 623.5442 | 14.5227 | 48.8251 | 48.3547 | 50.4693 | 65.4937 |  |  | 1.0693 | -0.20953 | -0.51398 | -1.1914 | 7.9283 | 5.2387 | 7.426 | -2.2902 | 20.3124 | 53.7172 | 24.5032 | -9.86e-06 | 3.29e-06 | -0.00076718 | 27.3696 | 16.43 | 16.7146 | 17.1172 | 17.1213 | 16.1254 | 14.6531 | 16.6704 | 17.0467 | 17.3809 | 17.4521 | 17.2018 | 16.3921 | 14.6776 | 728.6226 | 490.3727 | 473.8924 | 293.9643 | 213.6688 | 727.3249 | 437.2439 | 21.1908 | 37.7818 | 43.7715 | 80.7437 | 84.631 | 88.1133 |  |  |  | 630.2416 | 588.4355 | 589.1306 | 616.7666 | 73.8157 | 29.6935 | 803.0046 |  |  | 617.8325 |  |  | 20.986 | 55.7626 | 559.7316 | 21.3431 | 58.2228 | 842.791 | 754.7615 | 634.7162 | 796.1014 | 780.3324 | 755.8006 |  | 828.8843 | 889.6442 | 1025.827 | 612.173 | 702.5933 | 974.6819 |  | 1048.4548 |  |  | 453.6362 | 666.8121 | 750.6908 | [6 empty] | 623.3971 |  |  | 428.215 |  |  | 527.4818 | 673.2673 | 686.5727 | 1043.1948 | 1115.8609 | 1086.9646 | 533.3169 | 728.6463 | 853.4148 | 628.0946 | 707.3323 | 1083.8781 | 1129.6424 | 641.2249 | 820.4321 | 1109.8449 | 1140.5243 | 1087.6695 | 549.3772 | 671.1067 | 707.3774 | 563.07 | 749.1243 | 873.1511 | 1115.7671 | 1139.9948 | 610.9729 | 716.3225 | 667.0603 | 856.1925 | 88.824 | -0.0072879 | 17.7611 | 5.0975 | -40.1406 | 3.1215 | 9189.34 | 0.27 | 2.2417 | -1.0054 | -1.5746 | -2.3973 | 7.0426 | 5.7248 | 6.8159 | 85.6604 | 165.2146 | 53.9072 | 56.6636 | 10.3684 | 121.9253 | 38.1391
42810.4531 | 1129 | 17.4611 | 17.8965 | 18.0428 | 18.0947 | 17.4439 | 16.1029 | 15.045 | 16.4576 | 16.9435 | 17.0863 | 17.106 | 16.6439 | 15.6711 | 14.4358 | 29.4912 | 47.3436 | 46.1894 | 89.1391 | 53.7112 | 92.3769 |  |  |  | 37.4917 | 87.9123 | 476.2267 | 687.5664 | 713.5635 | 693.88 | 100.2427 | 130.4641 | 925.7111 | 89.5593 | 123.4768 | 835.3464 | 910.5551 | 859.7295 |  | 243.1374 | 929.675 | 922.1777 | 530.2954 |  | 472.8512 | 721.5579 | 565.2857 | 723.8286 | 889.2093 | 1015.0259 | 1049.8885 | 49.899 | 408.9802 | 78.4028 | 623.8909 | 14.5182 | 48.8492 | 48.3498 | 50.4964 | 65.7603 |  |  | 1.0897 | -0.14448 | -0.29385 | -0.96925 | 8.4986 | 6.4892 | 8.4491 | -3.3225 | 20.3643 | 53.7967 | 26.3489 | -4.928e-05 | 3.29e-06 | -0.00077868 | 27.4441 | 16.4316 | 16.7118 | 17.1002 | 17.1135 | 16.1164 | 14.6457 | 16.6613 | 17.0335 | 17.3711 | 17.453 | 17.1975 | 16.3834 | 14.6723 | 724.4883 | 490.5487 | 476.4488 | 292.6132 | 215.9517 | 727.8718 | 437.415 | 21.2651 | 37.8947 | 43.8758 | 80.8059 | 84.6651 | 88.1509 |  |  |  | 630.4938 | 588.4376 | 588.9307 | 618.6634 | 77.7642 | 34.0588 | 804.9699 |  |  | 621.2508 |  |  | 21.022 | 55.8506 | 558.9911 | 21.3935 | 58.3301 | 844.3201 | 752.1394 | 634.9867 | 797.6706 | 781.5907 | 753.3489 |  | 828.5347 | 891.2217 | 1024.5275 | 612.8951 | 702.7868 | 978.62 |  | 1049.9916 |  |  | 453.8115 | 663.126 | 748.6581 | [6 empty] | 623.8174 |  |  | 428.8647 |  |  | 527.6801 | 673.7912 | 686.7279 | 1050.1702 | 1121.0694 | 1088.1317 | 533.7746 | 729.7261 | 854.0685 | 628.1045 | 707.4809 | 1085.2447 | 1128.5278 | 642.0922 | 822.2004 | 1104.6501 | 1138.8724 | 1084.1051 | 549.4225 | 671.872 | 707.2747 | 564.039 | 749.9623 | 874.0351 | 1116.1585 | 1141.4697 | 611.5704 | 716.4323 | 667.7048 | 859.9396 | 91.3215 | -0.0033032 | 17.7629 | 5.0961 | -40.1199 | 3.1215 | 9123.38 | 0.33 | 2.2623 | -0.83544 | -1.1915 | -2.1639 | 7.2917 | 6.3716 | 7.2704 | 85.6127 | 164.4897 | 53.9333 | 57.308 | 10.1173 | 121.8786 | 38.1356
42810.4531 | 1130 | 17.4575 | 17.8962 | 18.042 | 18.0879 | 17.4381 | 16.0972 | 15.0405 | 16.4558 | 16.9411 | 17.0911 | 17.1017 | 16.6349 | 15.6766 | 14.4418 | 29.6457 | 47.5089 | 46.3488 | 89.1862 | 54.3284 | 92.4034 |  |  |  | 37.6939 | 87.8902 | 477.9072 | 688.4513 | 714.2276 | 695.1374 | 89.5796 | 134.4629 | 937.4398 | 96.765 | 119.7047 | 834.4789 | 909.1995 | 854.5226 |  | 245.036 | 927.3099 | 922.3534 | 520.0853 |  | 474.0437 | 722.0208 | 566.3734 | 722.2011 | 887.6072 | 1017.8834 | 1050.9966 | 50.1795 | 408.8911 | 77.7982 | 624.031 | 14.5158 | 48.8681 | 48.336 | 50.5173 | 66.0135 |  |  | 1.162 | -0.44281 | -0.14074 | -0.48692 | 7.8547 | 5.6402 | 7.4825 | -2.7029 | 20.7401 | 53.409 | 27.245 | -1.64e-06 | -4.271e-05 | -0.00081154 | 27.5228 | 16.4253 | 16.7145 | 17.1058 | 17.1112 | 16.1159 | 14.6373 | 16.6649 | 17.0341 | 17.3718 | 17.4558 | 17.1956 | 16.3837 | 14.6756 | 721.352 | 496.4795 | 473.4643 | 295.5822 | 222.4055 | 728.4958 | 437.7128 | 21.3431 | 38.0185 | 43.9982 | 80.8787 | 84.6978 | 88.191 |  |  |  | 630.8452 | 589.808 | 589.9102 | 621.2711 | 69.7793 | 26.5645 | 807.0436 |  |  | 624.2718 |  |  | 21.0645 | 55.9371 | 560.6972 | 21.4416 | 58.42 | 844.4774 | 751.8975 | 633.5331 | 798.684 | 782.0026 | 752.8442 |  | 828.3371 | 892.131 | 1023.5765 | 613.0188 | 702.8866 | 981.6635 |  | 1051.4747 |  |  | 454.5853 | 663.6583 | 747.2187 | [6 empty] | 623.2807 |  |  | 430.261 |  |  | 527.6545 | 673.657 | 686.6185 | 1053.175 | 1123.2864 | 1089.5987 | 534.7645 | 731.0552 | 856.5838 | 627.9086 | 707.0497 | 1080.7892 | 1128.683 | 642.8658 | 824.6214 | 1096.601 | 1137.7993 | 1085.0887 | 549.6304 | 673.1049 | 707.7221 | 564.6008 | 749.9293 | 875.5988 | 1117.78 | 1143.485 | 612.0544 | 717.7677 | 667.8042 | 860.7485 | 93.1298 | -0.00064437 | 17.7631 | 5.094 | -40.0677 | 3.1215 | 9054.07 | 0.28 | 2.3376 | -1.4629 | -0.82477 | -1.5341 | 7.0178 | 5.9468 | 6.8495 | 85.5613 | 163.9672 | 53.9537 | 57.8679 | 10.5062 | 121.6155 | 38.1318
42810.4531 | 1131 | 17.4525 | 17.8839 | 18.0329 | 18.0843 | 17.434 | 16.0964 | 15.0478 | 16.4499 | 16.9293 | 17.081 | 17.0997 | 16.6313 | 15.6613 | 14.4372 | 29.8008 | 47.6754 | 46.5105 | 89.219 | 54.8897 | 92.4172 |  |  |  | 37.9036 | 87.8692 | 479.4054 | 689.206 | 715.1078 | 696.2906 | 96.9791 | 127.6732 | 928.3575 | 99.0427 | 136.4255 | 849.7386 | 832.6785 | 865.7407 |  | 243.0407 | 918.0844 | 916.1646 | 533.6203 |  | 476.4176 | 722.5902 | 567.319 | 719.6777 | 885.0728 | 1018.2402 | 1050.164 | 50.7297 | 408.85 | 79.1498 | 624.2472 | 14.5088 | 48.9024 | 48.3298 | 50.5476 | 66.2737 |  |  | 1.0036 | -0.80357 | -1.3768 | -0.94296 | 8.1681 | 5.332 | 8.0647 | -2.306 | 20.0471 | 54.3917 | 27.3714 | -4.928e-05 | 4.107e-05 | -0.00079675 | 27.6012 | 16.4199 | 16.7114 | 17.1004 | 17.1115 | 16.119 | 14.6368 | 16.6676 | 17.0431 | 17.3775 | 17.4598 | 17.2027 | 16.3906 | 14.6776 | 713.1437 | 479.7093 | 429.3147 | 282.4219 | 216.5766 | 728.3029 | 437.3089 | 21.4108 | 38.1395 | 44.1075 | 80.949 | 84.7247 | 88.2288 |  |  |  | 631.373 | 591.9891 | 591.6978 | 625.4089 | 76.7295 | 22.8136 | 808.3668 |  |  | 627.4947 |  |  | 21.0997 | 56.0173 | 562.0859 | 21.499 | 58.5079 | 841.2571 | 753.9581 | 630.8514 | 800.234 | 783.3456 | 755.4258 |  | 828.6668 | 889.4845 | 1022.311 | 611.7609 | 702.8157 | 974.9999 |  | 1050.9812 |  |  | 455.3344 | 666.9527 | 748.7088 | [6 empty] | 621.1837 |  |  | 431.4259 |  |  | 527.4533 | 673.4913 | 686.9836 | 1045.8331 | 1122.3959 | 1089.3704 | 535.5016 | 730.9034 | 858.6032 | 627.9245 | 707.353 | 1075.8563 | 1128.3109 | 642.8048 | 823.8401 | 1091.1963 | 1136.0193 | 1087.5517 | 550.3005 | 674.9277 | 708.593 | 564.9198 | 749.8825 | 877.133 | 1119.1902 | 1147.057 | 612.1612 | 719.0034 | 668.0497 | 861.2046 | 94.3538 | -0.00069348 | 17.7651 | 5.0928 | -40.0799 | 3.1215 | 8986.09 | 0.28 | 2.1738 | -1.9713 | -2.5803 | -2.1354 | 7.1574 | 5.7829 | 7.112 | 85.5987 | 163.3806 | 53.9717 | 58.7146 | 15.334 | 93.0951 | 38.12
42810.4531 | 1132 | 17.4537 | 17.8853 | 18.0373 | 18.0822 | 17.4375 | 16.0895 | 15.0482 | 16.4495 | 16.9339 | 17.0776 | 17.1019 | 16.6335 | 15.6692 | 14.4413 | 29.9422 | 47.8394 | 46.6592 | 89.2426 | 55.4645 | 92.4167 |  |  |  | 38.1027 | 87.8466 | 482.4209 | 690.7537 | 717.2033 | 698.1879 | 95.2663 | 134.4113 | 930.6765 | 92.4376 | 129.7414 | 853.35 | 715.1573 | 878.2215 |  | 233.4353 | 922.3964 | 913.7014 | 527.3528 |  | 476.96 | 722.5771 | 568.0563 | 722.2709 | 891.2166 | 1019.7464 | 1052.5009 | 50.9738 | 408.8089 | 82.0856 | 624.6255 | 14.4985 | 48.9283 | 48.3186 | 50.5771 | 66.5415 |  |  | 1.6272 | -0.15631 | -0.38716 | -0.82928 | 8.4724 | 4.9115 | 6.7531 | -3.2227 | 20.0125 | 51.409 | 29.2831 | -1.478e-05 | -6.57e-06 | -0.00079675 | 27.6739 | 16.429 | 16.7112 | 17.102 | 17.1123 | 16.114 | 14.6406 | 16.6605 | 17.0421 | 17.3826 | 17.4532 | 17.2037 | 16.395 | 14.6795 | 717.6112 | 478.2019 | 417.5318 | 264.7279 | 206.1538 | 728.7167 | 437.285 | 21.4972 | 38.2529 | 44.2228 | 81.0341 | 84.7681 | 88.2733 |  |  |  | 632.0806 | 594.0869 | 593.4503 | 628.0705 | 73.1162 | 30.5646 | 809.6167 |  |  | 629.3111 |  |  | 21.1333 | 56.0925 | 564.5146 | 21.5373 | 58.6107 | 838.7347 | 755.689 | 628.9021 | 801.7829 | 784.7971 | 758.9021 |  | 829.0451 | 886.4004 | 1021.6722 | 610.1149 | 702.7482 | 971.561 |  | 1050.4881 |  |  | 456.2535 | 671.7304 | 750.9766 | [6 empty] | 619.3143 |  |  | 431.5805 |  |  | 527.6753 | 673.6479 | 687.7463 | 1042.1612 | 1116.2574 | 1088.8824 | 536.0056 | 729.8635 | 859.0664 | 628.3134 | 707.7691 | 1074.7501 | 1123.1175 | 642.2435 | 822.9061 | 1097.3829 | 1141.1302 | 1093.0964 | 550.9979 | 676.1928 | 709.221 | 565.2627 | 750.1069 | 879.5161 | 1127.3779 | 1153.09 | 612.3677 | 719.5901 | 668.5524 | 862.0657 | 96.1413 | 0.00034479 | 17.7662 | 5.0943 | -40.1328 | 3.1214 | 8959.61 | 0.31 | 2.7706 | -0.86941 | -1.3683 | -2.0026 | 7.2938 | 5.5533 | 6.5118 | 85.6275 | 163.1338 | 54.0013 | 58.3585 | 16.6386 | 59.311 | 38.1846
42810.4531 | 1133 | 17.4481 | 17.883 | 18.0386 | 18.0801 | 17.4365 | 16.0981 | 15.053 | 16.4481 | 16.9334 | 17.0878 | 17.1026 | 16.6337 | 15.6697 | 14.4353 | 30.0902 | 47.9996 | 46.8109 | 89.2748 | 55.9779 | 92.4138 |  |  |  | 38.3081 | 87.8443 | 485.4365 | 692.2269 | 718.8846 | 699.3973 | 93.2364 | 129.0841 | 926.9919 | 96.3205 | 123.2689 | 839.6783 | 909.7605 | 872.1752 |  | 228.9086 | 930.2503 | 918.2201 | 534.192 |  | 475.9144 | 721.9409 | 568.6525 | 721.9515 | 894.8847 | 1020.8983 | 1053.3452 | 49.3852 | 408.6999 | 83.3844 | 624.9424 | 14.4882 | 48.9592 | 48.3085 | 50.6041 | 66.7908 |  |  | 1.1121 | -0.3587 | -0.52318 | -0.61637 | 8.6235 | 6.3013 | 7.1907 | -2.967 | 20.1016 | 54.3622 | 34.217 | 4.93e-06 | -3.614e-05 | -0.00076554 | 27.7385 | 16.4327 | 16.711 | 17.1029 | 17.1089 | 16.1072 | 14.6419 | 16.6558 | 17.0354 | 17.3841 | 17.4508 | 17.1976 | 16.3917 | 14.6767 | 715.7658 | 466.6819 | 405.4963 | 258.5984 | 202.1301 | 728.6294 | 437.1706 | 21.5782 | 38.3715 | 44.3341 | 81.1201 | 84.8069 | 88.3187 |  |  |  | 632.5767 | 594.6449 | 594.5908 | 626.8298 | 66.499 | 23.1268 | 810.7234 |  |  | 630.3177 |  |  | 21.1626 | 56.169 | 568.0901 | 21.5952 | 58.7067 | 839.8649 | 755.8214 | 627.9361 | 801.3452 | 784.632 | 761.6442 |  | 829.1317 | 883.7081 | 1021.2916 | 608.5763 | 702.6003 | 967.8435 |  | 1050.2731 |  |  | 457.6245 | 676.5235 | 751.788 | [6 empty] | 618.1396 |  |  | 431.3165 |  |  | 527.9301 | 674.4188 | 688.2924 | 1041.0642 | 1112.3718 | 1086.674 | 536.9903 | 728.9539 | 857.5478 | 629.1394 | 707.4406 | 1075.2119 | 1117.2957 | 642.218 | 821.156 | 1108.3227 | 1147.7684 | 1096.0269 | 551.3629 | 676.8202 | 710.133 | 565.9316 | 750.0073 | 880.2726 | 1133.2406 | 1155.5337 | 612.9368 | 720.157 | 669.1603 | 862.4808 | 96.6087 | 0.0016917 | 17.7679 | 5.095 | -40.1338 | 3.1215 | 8971.02 | 0.29 | 2.2919 | -1.3166 | -1.5901 | -1.7259 | 7.3618 | 6.293 | 6.7225 | 85.5801 | 163.0107 | 54.0088 | 58.5339 | 17.9538 | 121.4497 | 38.3164
42810.4532 | 1134 | 17.4412 | 17.8796 | 18.0287 | 18.0756 | 17.4329 | 16.0972 | 15.0487 | 16.447 | 16.9269 | 17.0772 | 17.0954 | 16.6316 | 15.6649 | 14.4275 | 30.2465 | 48.16 | 46.9867 | 89.3186 | 56.6803 | 92.4006 |  |  |  | 38.5107 | 87.8409 | 487.6925 | 693.1319 | 719.6486 | 700.1515 | 89.0121 | 123.3303 | 924.5987 | 91.8477 | 124.6762 | 844.008 | 909.7441 | 861.6157 |  | 234.743 | 931.8064 | 926.7441 | 512.9056 |  | 475.5681 | 721.3133 | 567.3225 | 722.7104 | 898.1232 | 1023.535 | 1054.7507 | 48.067 | 408.8614 | 82.9292 | 625.2456 | 14.4802 | 48.9876 | 48.2894 | 50.6251 | 67.0487 |  |  | 1.7757 | 0.20839 | -0.56458 | -0.45144 | 7.8665 | 5.0528 | 7.512 | -2.5156 | 20.1804 | 54.6544 | 36.4687 | 0 | 3.121e-05 | -0.00076882 | 27.8193 | 16.4325 | 16.6991 | 17.0968 | 17.1026 | 16.1167 | 14.6372 | 16.6585 | 17.0357 | 17.3729 | 17.4566 | 17.2017 | 16.3889 | 14.6847 | 705.6264 | 467.7608 | 402.5123 | 259.7145 | 209.8483 | 728.4629 | 436.8327 | 21.6571 | 38.4793 | 44.4472 | 81.2025 | 84.8389 | 88.3531 |  |  |  | 632.9699 | 594.6133 | 595.0696 | 625.9539 | 89.0091 | 31.4334 | 810.5944 |  |  | 631.9916 |  |  | 21.1837 | 56.2411 | 570.1314 | 21.6428 | 58.795 | 843.8933 | 755.8902 | 627.2835 | 801.2612 | 784.4986 | 762.9985 |  | 829.3088 | 884.4789 | 1020.5977 | 607.6305 | 702.3603 | 968.1738 |  | 1050.0203 |  |  | 459.2114 | 680.3887 | 752.4342 | [6 empty] | 617.55 |  |  | 432.1056 |  |  | 527.9792 | 675.0278 | 688.318 | 1043.8934 | 1114.4443 | 1084.5039 | 537.9201 | 727.7275 | 855.449 | 629.9353 | 707.9043 | 1077.2077 | 1116.9443 | 642.1483 | 818.341 | 1113.6023 | 1148.6235 | 1094.9358 | 551.9088 | 677.4961 | 710.9096 | 566.4011 | 749.6523 | 880.5918 | 1133.0338 | 1155.7744 | 613.4296 | 720.5259 | 669.7633 | 862.0185 | 89.2853 | -0.00091796 | 17.7696 | 5.0971 | -40.1641 | 3.1215 | 8994.52 | 0.36 | 2.8972 | 1.0032 | -1.6513 | -1.4766 | 7.0384 | 5.6409 | 6.878 | 85.6011 | 162.629 | 53.9778 | 59.6041 | 18.2204 | 122.0344 | 38.418
42810.4532 | 1135 | 17.447 | 17.8827 | 18.0353 | 18.0765 | 17.4341 | 16.0928 | 15.0576 | 16.4478 | 16.9263 | 17.0759 | 17.093 | 16.6354 | 15.6668 | 14.4349 | 30.4057 | 48.3282 | 47.1416 | 89.3522 | 57.3676 | 92.3913 |  |  |  | 38.7187 | 87.8207 | 489.1134 | 693.4425 | 719.8816 | 700.9131 | 91.5339 | 125.7044 | 927.628 | 92.5761 | 130.2601 | 847.0813 | 908.117 | 871.7025 |  | 230.5636 | 931.7137 | 929.2969 | 501.8443 |  | 476.2052 | 718.6097 | 565.2396 | 719.6445 | 889.2517 | 1023.7893 | 1055.9796 | 48.2677 | 409.137 | 81.5928 | 625.231 | 14.4852 | 49.0189 | 48.2725 | 50.6391 | 67.2988 |  |  | 1.1692 | -0.30219 | -0.24654 | -0.77145 | 7.9848 | 5.8696 | 8.1081 | -2.4709 | 20.7619 | 52.8466 | 34.6367 | -1.478e-05 | 6.9e-05 | -0.00079839 | 27.9046 | 16.4377 | 16.7059 | 17.1034 | 17.1145 | 16.1129 | 14.644 | 16.6585 | 17.0453 | 17.3791 | 17.4583 | 17.2043 | 16.3899 | 14.6883 | 734.1548 | 492.5181 | 431.9467 | 262.7416 | 214.4812 | 730.096 | 436.9531 | 21.7307 | 38.5924 | 44.5517 | 81.2617 | 84.8645 | 88.3927 |  |  |  | 633.3556 | 595.3263 | 595.9693 | 625.7935 | 68.6519 | 30.5368 | 810.9838 |  |  | 633.2648 |  |  | 21.2218 | 56.3211 | 571.431 | 21.6974 | 58.9009 | 845.9381 | 754.5908 | 626.0297 | 799.6528 | 782.2028 | 761.3222 |  | 829.4796 | 881.9374 | 1019.8675 | 606.6064 | 702.1557 | 963.2404 |  | 1049.7342 |  |  | 459.5834 | 676.9296 | 751.8971 | [6 empty] | 616.5158 |  |  | 433.357 |  |  | 528.3921 | 676.2265 | 687.9219 | 1047.5198 | 1119.0092 | 1084.1888 | 538.9846 | 726.6224 | 854.5239 | 630.4383 | 709.0696 | 1082.4913 | 1116.8525 | 641.7892 | 815.6269 | 1109.7193 | 1146.7755 | 1095.3603 | 552.1844 | 678.1263 | 711.4408 | 567.0226 | 750.4013 | 880.9935 | 1129.5959 | 1155.7438 | 614.3481 | 721.7495 | 670.8636 | 862.5107 | 88.3306 | -0.0005181 | 17.7719 | 5.0991 | -40.1586 | 3.1215 | 9051.49 | 0.31 | 2.3519 | -1.2064 | -1.0897 | -1.9276 | 7.0918 | 6.0804 | 7.1464 | 85.7044 | 162.321 | 53.9575 | 56.9888 | 14.9731 | 121.6869 | 38.4983
42810.4532 | 1136 | 17.4516 | 17.8875 | 18.0436 | 18.0823 | 17.44 | 16.1019 | 15.0654 | 16.4512 | 16.9331 | 17.0767 | 17.1005 | 16.6428 | 15.6754 | 14.4445 | 30.5499 | 48.5048 | 47.2993 | 89.3862 | 58.1751 | 92.4033 |  |  |  | 38.9397 | 87.8177 | 492.0489 | 694.3573 | 721.1909 | 701.7317 | 104.9917 | 132.0978 | 932.9719 | 97.883 | 130.0363 | 850.3165 | 893.2687 | 869.1202 |  | 228.5282 | 934.0576 | 930.801 | 505.5046 |  | 477.0049 | 718.8604 | 563.6134 | 715.6803 | 879.5537 | 1018.8637 | 1053.9859 | 49.1413 | 409.2776 | 79.4008 | 625.0661 | 14.5083 | 49.0465 | 48.263 | 50.6411 | 67.5485 |  |  | 1.3585 | 0.23008 | 0.27192 | -0.016426 | 8.657 | 4.9621 | 7.9747 | -2.4801 | 19.315 | 53.2876 | 31.0949 | 1.643e-05 | -4.93e-06 | -0.00080989 | 27.9857 | 16.4425 | 16.7044 | 17.1009 | 17.1103 | 16.106 | 14.6436 | 16.6592 | 17.0384 | 17.3787 | 17.4534 | 17.1958 | 16.3885 | 14.6787 | 728.471 | 485.4471 | 423.2355 | 271.387 | 221.1024 | 730.5658 | 437.2688 | 21.81 | 38.7147 | 44.6823 | 81.3268 | 84.9073 | 88.4295 |  |  |  | 633.7934 | 597.3424 | 598.2554 | 626.4283 | 88.2281 | 37.143 | 809.352 |  |  | 632.7351 |  |  | 21.2494 | 56.4022 | 573.1996 | 21.7435 | 58.9875 | 844.9 | 752.8466 | 623.8453 | 798.1716 | 780.5905 | 758.4088 |  | 829.5009 | 882.1029 | 1018.3268 | 605.3268 | 701.8845 | 968.5784 |  | 1048.6517 |  |  | 459.2424 | 672.717 | 749.9978 | [6 empty] | 614.8956 |  |  | 433.7823 |  |  | 528.8525 | 678.0464 | 687.7382 | 1039.2819 | 1119.3137 | 1082.0276 | 539.5843 | 725.8058 | 855.1544 | 630.9478 | 709.7125 | 1082.294 | 1112.3033 | 641.7232 | 813.641 | 1097.0232 | 1143.8209 | 1095.4435 | 552.2104 | 679.412 | 712.0524 | 567.7294 | 751.8564 | 883.8665 | 1119.2428 | 1154.2754 | 615.1692 | 722.239 | 672.3646 | 867.5702 | 88.9981 | 0.00061137 | 17.7737 | 5.107 | -40.1155 | 3.1215 | 9103.13 | 0.36 | 2.5361 | 1.0528 | 1.1446 | -0.28131 | 7.3703 | 5.58 | 7.0739 | 85.7924 | 161.5195 | 53.9285 | 57.7802 | 16.0017 | 115.7257 | 38.5668
42810.4532 | 1137 | 17.4446 | 17.8766 | 18.0266 | 18.0771 | 17.4316 | 16.0968 | 15.0666 | 16.439 | 16.9241 | 17.0757 | 17.0976 | 16.6341 | 15.6684 | 14.4339 | 30.7035 | 48.6533 | 47.4484 | 89.4153 | 58.8628 | 92.4022 |  |  |  | 39.0743 | 87.8056 | 496.1426 | 696.3852 | 723.7113 | 703.7303 | 97.6802 | 139.0815 | 938.9167 | 100.4822 | 125.5646 | 849.6431 | 912.6487 | 872.5434 |  | 237.4373 | 927.4523 | 926.4352 | 508.3999 |  | 479.5672 | 719.151 | 563.3694 | 714.5929 | 883.1904 | 1018.5803 | 1051.7464 | 51.5825 | 409.2953 | 77.6017 | 624.7382 | 14.5372 | 49.045 | 48.2771 | 50.6547 | 67.8101 |  |  | 0.99575 | -0.77399 | -0.94111 | -1.2584 | 8.1326 | 5.1776 | 7.7861 | -2.8428 | 19.5964 | 53.1258 | 27.4296 | -2.3e-05 | 2.464e-05 | -0.00079347 | 28.0587 | 16.4453 | 16.7056 | 17.0964 | 17.1051 | 16.1084 | 14.6429 | 16.6559 | 17.0393 | 17.3718 | 17.4523 | 17.1899 | 16.3917 | 14.6727 | 734.9493 | 497.4083 | 458.248 | 284.7751 | 221.9779 | 732.1167 | 438.2673 | 21.9068 | 38.8412 | 44.8015 | 81.4147 | 84.9422 | 88.4861 |  |  |  | 634.3293 | 599.3077 | 599.8179 | 628.4721 | 77.2895 | 35.181 | 808.4989 |  |  | 632.3267 |  |  | 21.2838 | 56.4868 | 576.9958 | 21.7871 | 59.0827 | 843.5434 | 751.824 | 620.9234 | 797.0182 | 779.4527 | 756.9455 |  | 829.301 | 879.3619 | 1016.8094 | 603.2123 | 700.8728 | 959.5324 |  | 1047.4926 |  |  | 459.9694 | 671.9983 | 748.4719 | [6 empty] | 611.7513 |  |  | 433.2582 |  |  | 529.4157 | 679.1846 | 687.7925 | 1038.8312 | 1116.1894 | 1080.6523 | 540.105 | 725.1264 | 854.1864 | 631.7746 | 709.3568 | 1080.5052 | 1113.9358 | 641.9445 | 813.0627 | 1095.6345 | 1136.4829 | 1095.8214 | 551.2844 | 679.8979 | 712.994 | 569.1975 | 753.2177 | 886.5089 | 1113.0484 | 1152.4466 | 614.8372 | 721.6679 | 673.8133 | 869.5424 | 101.1743 | 1.507e-05 | 17.7739 | 5.115 | -40.1526 | 3.1214 | 9159.97 | 0.22 | 2.1735 | -1.9313 | -2.1297 | -2.4626 | 7.1428 | 5.6992 | 6.989 | 85.7667 | 160.8135 | 53.7468 | 57.5892 | 12.3037 | 123.3346 | 38.6157
42810.4532 | 1138 | 17.45 | 17.8803 | 18.0367 | 18.0798 | 17.4338 | 16.0906 | 15.0732 | 16.4427 | 16.9325 | 17.0798 | 17.0984 | 16.6367 | 15.6721 | 14.4404 | 30.8742 | 48.8313 | 47.6104 | 89.4674 | 59.0934 | 92.3894 |  |  |  | 39.3031 | 87.808 | 499.4165 | 697.6656 | 724.9606 | 704.3914 | 96.893 | 136.2598 | 935.2257 | 105.3625 | 133.5211 | 859.121 | 916.6816 | 872.325 |  | 246.6737 | 924.9459 | 924.036 | 535.593 |  | 479.6766 | 718.3157 | 563.5665 | 716.189 | 882.1801 | 1014.399 | 1049.6737 | 52.3143 | 409.1785 | 78.2106 | 624.535 | 14.539 | 49.0326 | 48.301 | 50.6463 | 68.0409 |  |  | 1.0667 | -0.22793 | -0.062548 | -0.665 | 7.6503 | 5.5344 | 7.8682 | -2.2613 | 20.6753 | 54.9557 | 26.5917 | -5.914e-05 | 8.05e-05 | -0.00079511 | 28.1365 | 16.4505 | 16.705 | 17.1014 | 17.1062 | 16.1122 | 14.6449 | 16.6604 | 17.0376 | 17.3719 | 17.4583 | 17.1973 | 16.391 | 14.6759 | 747.9935 | 501.5897 | 469.2401 | 294.9511 | 238.6853 | 732.8944 | 438.9981 | 21.9783 | 38.9519 | 44.9037 | 81.4829 | 84.9852 | 88.5282 |  |  |  | 634.8438 | 600.6368 | 601.2784 | 630.1053 | 79.6766 | 32.4515 | 808.2549 |  |  | 632.8214 |  |  | 21.3143 | 56.5566 | 579.9652 | 21.8299 | 59.1814 | 842.4546 | 753.0121 | 618.8318 | 798.7213 | 781.4933 | 758.6133 |  | 829.3664 | 876.9877 | 1016.7757 | 601.689 | 699.6555 | 951.157 |  | 1047.5285 |  |  | 461.902 | 674.5924 | 748.363 | [6 empty] | 609.5236 |  |  | 434.5667 |  |  | 529.5389 | 679.9485 | 687.6451 | 1040.1722 | 1110.5694 | 1082.779 | 541.0091 | 726.1226 | 854.5312 | 632.4327 | 708.3841 | 1078.3026 | 1111.7432 | 642.9984 | 815.7832 | 1101.8007 | 1132.0211 | 1097.9787 | 551.8894 | 678.8981 | 714.2313 | 570.9554 | 755.723 | 891.608 | 1101.8685 | 1150.7771 | 614.2739 | 720.342 | 675.828 | 872.2349 | 92.4324 | 0.00022554 | 17.7718 | 5.1183 | -40.123 | 3.1214 | 9196.99 | 0.36 | 2.2504 | -1.0476 | -0.5488 | -1.7894 | 6.9165 | 5.8828 | 7.0143 | 85.7421 | 160.8621 | 53.5006 | 56.4057 | 11.2234 | 124.2242 | 38.6719
42810.4532 | 1139 | 17.4432 | 17.8861 | 18.0373 | 18.0817 | 17.4343 | 16.0981 | 15.0678 | 16.4504 | 16.9354 | 17.0823 | 17.1011 | 16.6358 | 15.6598 | 14.4403 | 31.0265 | 48.9856 | 47.7756 | 89.5034 | 59.7452 | 92.3908 |  |  |  | 39.5087 | 87.7925 | 502.9979 | 699.0765 | 726.9215 | 705.6418 | 96.4174 | 130.1793 | 927.0377 | 93.3952 | 134.4778 | 868.1562 | 921.7804 | 884.8242 |  | 258.3288 | 921.6498 | 913.4595 | 548.3412 |  | 478.3561 | 718.5439 | 562.518 | 716.3936 | 886.2197 | 1013.3838 | 1047.9398 | 51.6651 | 409.142 | 80.3813 | 624.694 | 14.5551 | 49.071 | 48.3216 | 50.6376 | 68.2318 |  |  | 0.51737 | -0.15105 | -0.19068 | -0.86542 | 6.7231 | 5.5903 | 8.0693 | -2.8626 | 21.033 | 55.1334 | 27.8433 | 1.479e-05 | 4.107e-05 | -0.0007524 | 28.2172 | 16.456 | 16.7 | 17.1004 | 17.1052 | 16.1107 | 14.6502 | 16.6586 | 17.0368 | 17.3769 | 17.4566 | 17.2064 | 16.3962 | 14.6808 | 748.5117 | 500.3196 | 455.7871 | 299.2199 | 247.0167 | 734.3579 | 439.6104 | 22.0518 | 39.06 | 45.018 | 81.5401 | 85.018 | 88.5657 |  |  |  | 635.3569 | 601.7872 | 602.7158 | 629.7682 | 92.2078 | 35.2139 | 809.92 |  |  | 634.8689 |  |  | 21.3532 | 56.6405 | 582.6402 | 21.8861 | 59.2706 | 845.6675 | 755.6291 | 618.7517 | 800.6751 | 783.1942 | 762.9858 |  | 829.7831 | 876.4615 | 1016.6296 | 600.9937 | 698.7228 | 951.1848 |  | 1047.5545 |  |  | 462.3872 | 679.9293 | 752.0059 | [6 empty] | 609.1001 |  |  | 435.8124 |  |  | 529.2985 | 680.175 | 687.5964 | 1035.689 | 1099.5069 | 1081.3346 | 541.7943 | 726.4897 | 856.0169 | 632.8436 | 707.7418 | 1075.8372 | 1105.7118 | 643.3657 | 817.9812 | 1096.8151 | 1126.1664 | 1100.9228 | 552.7288 | 677.8211 | 714.9715 | 571.8441 | 758.9982 | 893.25 | 1094.8176 | 1151.6427 | 614.8527 | 720.1011 | 677.4491 | 874.6504 | 88.4132 | -0.0012407 | 17.7702 | 5.1244 | -40.0243 | 3.1215 | 9224.4 | 0.38 | 1.5682 | -0.85293 | -0.95833 | -2.0416 | 6.4813 | 5.9101 | 7.1006 | 85.7589 | 160.8015 | 53.2996 | 56.8494 | 12.8364 | 125.9721 | 38.7827
42810.4532 | 1140 | 17.4553 | 17.8848 | 18.0432 | 18.0809 | 17.4343 | 16.1062 | 15.0768 | 16.4537 | 16.9375 | 17.0872 | 17.102 | 16.6441 | 15.6738 | 14.4472 | 31.1776 | 49.1585 | 47.9373 | 89.5437 | 59.7141 | 92.3887 |  |  |  | 39.7227 | 87.7793 | 505.7981 | 700.4684 | 727.877 | 707.3156 | 93.7263 | 132.3762 | 933.9923 | 95.4665 | 126.6292 | 860.3219 | 906.212 | 885.6359 |  | 237.9233 | 922.5308 | 918.5426 | 546.1612 |  | 477.0763 | 718.1892 | 561.2102 | 715.2216 | 888.4758 | 1017.2817 | 1046.8281 | 51.0723 | 409.241 | 80.9096 | 624.6296 | 14.5692 | 49.0918 | 48.3585 | 50.6493 | 68.4945 |  |  | 0.58571 | 0.21825 | -0.95425 | -1.3247 | 7.9552 | 5.2479 | 9.0504 | -2.7042 | 20.19 | 55.9317 | 27.7609 | -2.793e-05 | 2.629e-05 | -0.00077704 | 28.2987 | 16.4631 | 16.7045 | 17.099 | 17.1115 | 16.1072 | 14.6479 | 16.6625 | 17.0482 | 17.3835 | 17.4581 | 17.2077 | 16.3936 | 14.6901 | 747.9449 | 500.6187 | 461.4624 | 304.2702 | 252.1749 | 736.123 | 440.5274 | 22.1344 | 39.1666 | 45.1204 | 81.6015 | 85.0557 | 88.5863 |  |  |  | 635.6477 | 601.3618 | 602.5824 | 627.0963 | 88.4297 | 37.8461 | 810.8702 |  |  | 636.5764 |  |  | 21.3828 | 56.7165 | 585.7243 | 21.9276 | 59.3477 | 845.6134 | 754.9232 | 620.5913 | 802.4524 | 785.3647 | 762.3475 |  | 829.4547 | 875.2207 | 1015.3739 | 601.7097 | 698.5665 | 955.2373 |  | 1045.4302 |  |  | 461.9981 | 680.7771 | 752.3191 | [6 empty] | 611.1511 |  |  | 436.8675 |  |  | 529.0743 | 680.075 | 688.4537 | 1032.7847 | 1097.4205 | 1079.0417 | 542.2409 | 726.7808 | 857.5584 | 632.8053 | 707.8565 | 1078.5416 | 1110.6999 | 643.1148 | 818.7035 | 1088.644 | 1123.8479 | 1105.3372 | 553.5998 | 677.6814 | 715.4569 | 572.0905 | 761.5792 | 893.491 | 1088.9756 | 1153.6374 | 615.4517 | 720.5425 | 678.3379 | 876.3802 | 88.3281 | -0.0001603 | 17.7668 | 5.1271 | -40.1581 | 3.1214 | 9284.96 | 0.28 | 1.67 | 1.0251 | -2.1434 | -2.5255 | 7.0609 | 5.7349 | 7.5313 | 85.6676 | 160.191 | 53.2428 | 57.519 | 12.3832 | 119.6925 | 38.9145
42810.4532 | 1141 | 17.4496 | 17.8775 | 18.0336 | 18.0775 | 17.4262 | 16.0931 | 15.076 | 16.4528 | 16.9323 | 17.0755 | 17.0973 | 16.632 | 15.6688 | 14.445 | 31.3275 | 49.3237 | 48.0922 | 89.5738 | 60.0107 | 92.3766 |  |  |  | 39.9271 | 87.7695 | 506.0839 | 700.1382 | 727.0811 | 706.9779 | 90.4496 | 125.0976 | 925.8433 | 92.2484 | 128.3133 | 857.6928 | 923.0965 | 871.729 |  | 243.461 | 923.693 | 923.4378 | 528.3203 |  | 475.7198 | 716.6007 | 560.208 | 714.3257 | 886.9288 | 1019.1992 | 1046.9477 | 51.2375 | 409.3741 | 79.9585 | 624.6782 | 14.5737 | 49.1001 | 48.3931 | 50.6437 | 68.7389 |  |  | 1.5799 | 0.094711 | -0.004064 | -0.98896 | 8.1385 | 6.2375 | 8.3157 | -2.099 | 20.19 | 54.3766 | 27.8334 | 2.3e-05 | 7.228e-05 | -0.00076061 | 28.3741 | 16.4626 | 16.7092 | 17.0979 | 17.1134 | 16.1085 | 14.6395 | 16.6638 | 17.0493 | 17.3866 | 17.4633 | 17.1989 | 16.4007 | 14.6932 | 740.1428 | 507.6581 | 473.2565 | 297.3958 | 246.1695 | 737.5231 | 441.4646 | 22.2319 | 39.3062 | 45.2475 | 81.6953 | 85.1058 | 88.6501 |  |  |  | 635.971 | 602.0596 | 603.3861 | 627.3149 | 71.7845 | 29.6413 | 812.7987 |  |  | 638.8982 |  |  | 21.4133 | 56.7911 | 586.0362 | 21.9825 | 59.4261 | 843.1636 | 753.3109 | 621.0508 | 806.7758 | 790.8021 | 759.5791 |  | 828.8595 | 879.0715 | 1015.2682 | 601.3832 | 698.5833 | 964.6837 |  | 1043.2263 |  |  | 460.7911 | 677.8183 | 750.723 | [6 empty] | 611.832 |  |  | 437.0064 |  |  | 528.9907 | 679.9052 | 689.21 | 1035.0627 | 1096.8998 | 1078.5401 | 542.5806 | 727.0027 | 857.466 | 632.703 | 708.8176 | 1080.048 | 1113.0943 | 642.9787 | 819.6111 | 1075.0017 | 1123.4273 | 1107.7008 | 553.7883 | 678.1894 | 716.2928 | 572.3975 | 762.7859 | 893.7049 | 1088.3826 | 1153.0112 | 616.1602 | 721.9247 | 678.6155 | 876.5213 | 100.7257 | -0.00013226 | 17.7655 | 5.1344 | -40.129 | 3.1214 | 9354.66 | 0.31 | 2.7424 | 0.67473 | -0.13977 | -2.1803 | 7.1471 | 6.257 | 7.2245 | 85.5472 | 160.0298 | 53.2558 | 58.8686 | 11.2542 | 127.075 | 38.9724
42810.4533 | 1142 | 17.4419 | 17.8794 | 18.0357 | 18.0714 | 17.4263 | 16.0899 | 15.0744 | 16.4494 | 16.9329 | 17.0788 | 17.0984 | 16.6387 | 15.6665 | 14.4441 | 31.4844 | 49.4783 | 48.2443 | 89.6007 | 60.6429 | 92.3881 |  |  |  | 40.1404 | 87.7648 | 506.9588 | 699.7388 | 726.0825 | 706.7977 | 89.9943 | 110.6099 | 914.8596 | 84.1653 | 118.9446 | 850.4935 | 922.4498 | 873.2749 |  | 252.4875 | 912.2085 | 909.9558 | 524.5712 |  | 475.5802 | 718.3662 | 560.9191 | 714.8619 | 886.5202 | 1022.6946 | 1051.6011 | 50.7278 | 409.5053 | 80.4708 | 624.7933 | 14.6052 | 49.1221 | 48.4345 | 50.6484 | 68.9843 |  |  | 0.82555 | 0.16437 | -0.38848 | -0.98699 | 8.8811 | 6.6647 | 8.5056 | -2.2606 | 20.7253 | 53.2183 | 27.2516 | -5.421e-05 | -0.00010021 | -0.00077211 | 28.4594 | 16.4638 | 16.7081 | 17.1032 | 17.1088 | 16.1174 | 14.6465 | 16.6712 | 17.0469 | 17.3913 | 17.4678 | 17.2101 | 16.4017 | 14.6956 | 723.626 | 497.4407 | 467.2061 | 283.9213 | 238.2927 | 737.9647 | 441.8958 | 22.3171 | 39.4203 | 45.3655 | 81.7551 | 85.1384 | 88.6991 |  |  |  | 636.5267 | 604.5163 | 605.1416 | 631.019 | 91.5116 | 31.793 | 818.1519 |  |  | 644.5592 |  |  | 21.4492 | 56.8749 | 585.9604 | 22.0447 | 59.5085 | 838.8682 | 753.0713 | 619.4112 | 812.2254 | 796.3571 | 758.6192 |  | 828.7275 | 885.6059 | 1016.9014 | 599.2883 | 698.263 | 962.734 |  | 1042.4836 |  |  | 460.8991 | 677.107 | 749.317 | [6 empty] | 609.8495 |  |  | 436.345 |  |  | 529.2551 | 680.0663 | 689.7232 | 1037.6443 | 1098.2817 | 1079.9955 | 543.5364 | 727.3354 | 857.8936 | 633.0105 | 709.3285 | 1085.1794 | 1117.3825 | 643.2424 | 821.8509 | 1069.1145 | 1122.6804 | 1108.9694 | 553.6028 | 678.469 | 716.8029 | 572.2518 | 762.8417 | 892.9449 | 1085.3806 | 1152.8808 | 616.0937 | 721.3834 | 678.4696 | 874.5235 | 111.9035 | 0.00014133 | 17.7653 | 5.1427 | -40.1726 | 3.1214 | 9483.52 | 0.3 | 1.9822 | 0.88966 | -1.3677 | -2.1801 | 7.4761 | 6.4764 | 7.3164 | 85.5301 | 160.6874 | 53.2385 | 60.8563 | 12.0101 | 126.9103 | 38.9798
42810.4533 | 1143 | 17.4405 | 17.8738 | 18.0309 | 18.0677 | 17.4256 | 16.0807 | 15.0741 | 16.449 | 16.9278 | 17.0781 | 17.0973 | 16.6316 | 15.667 | 14.4325 | 31.6405 | 49.6412 | 48.408 | 89.6338 | 61.2298 | 92.3847 |  |  |  | 40.3559 | 87.7621 | 506.9394 | 698.817 | 724.7027 | 705.9001 | 92.6264 | 110.335 | 910.2726 | 78.6877 | 112.4254 | 843.4532 | 903.5521 | 866.824 |  | 241.7057 | 913.792 | 905.7009 | 535.6227 |  | 476.2623 | 720.8258 | 562.2533 | 715.4429 | 893.3276 | 1027.6568 | 1056.2334 | 51.3991 | 409.5103 | 81.8223 | 625.0377 | 14.6252 | 49.1415 | 48.4771 | 50.6547 | 69.233 |  |  | 0.76181 | -1.0106 | -0.15323 | -0.68209 | 7.6845 | 5.1783 | 7.3931 | -2.7121 | 19.8619 | 53.9835 | 27.3392 | -1.15e-05 | 8.22e-06 | -0.00076554 | 28.535 | 16.4687 | 16.7029 | 17.0964 | 17.1048 | 16.1109 | 14.6499 | 16.6632 | 17.0369 | 17.3794 | 17.4597 | 17.2014 | 16.3917 | 14.6759 | 726.1308 | 497.3641 | 466.2327 | 277.5106 | 226.3389 | 738.8163 | 442.4782 | 22.3915 | 39.5255 | 45.4715 | 81.8105 | 85.1605 | 88.7355 |  |  |  | 637.0916 | 606.5584 | 606.6344 | 632.2324 | 63.968 | 28.4662 | 823.9264 |  |  | 648.8459 |  |  | 21.4888 | 56.9552 | 585.8424 | 22.099 | 59.6053 | 834.838 | 757.1145 | 617.4053 | 817.088 | 802.1314 | 763.936 |  | 829.9143 | 895.5968 | 1019.5341 | 597.5321 | 697.5532 | 956.2551 |  | 1043.2109 |  |  | 462.333 | 680.9029 | 752.0295 | [6 empty] | 607.818 |  |  | 437.5022 |  |  | 529.7447 | 680.4046 | 690.0146 | 1036.4806 | 1104.547 | 1084.1578 | 544.2005 | 727.7811 | 859.4472 | 633.3516 | 710.0196 | 1088.6849 | 1119.8635 | 643.5756 | 826.0531 | 1071.7206 | 1122.7552 | 1108.0516 | 553.0307 | 677.5134 | 716.8126 | 571.8727 | 762.3487 | 892.1391 | 1086.382 | 1154.2559 | 615.6095 | 719.6386 | 678.3987 | 872.1781 | 110.9012 | 0.0016707 | 17.7635 | 5.1565 | -40.1415 | 3.1213 | 9527.06 | 0.37 | 1.9032 | -2.2087 | -0.86005 | -1.8146 | 6.9676 | 5.7196 | 6.8342 | 85.7761 | 161.7689 | 53.1202 | 60.8726 | 12.2314 | 118.9252 | 39.0583
42810.4533 | 1144 | 17.4464 | 17.8767 | 18.0187 | 18.071 | 17.4305 | 16.0875 | 15.0799 | 16.4525 | 16.9294 | 17.0822 | 17.097 | 16.6344 | 15.6709 | 14.4356 | 31.7917 | 49.7994 | 48.5604 | 89.6416 | 61.9316 | 92.3761 |  |  |  | 40.5658 | 87.7488 | 506.6571 | 697.5736 | 723.2409 | 704.2139 | 90.3595 | 128.8483 | 911.8155 | 79.4395 | 117.6919 | 843.5334 | 911.9984 | 867.2905 |  | 243.7277 | 908.3303 | 908.2117 | 522.9052 |  | 478.1483 | 722.0907 | 562.0364 | 714.6277 | 894.5873 | 1025.9458 | 1055.2344 | 52.0932 | 409.3487 | 81.4126 | 624.8847 | 14.6397 | 49.1623 | 48.4983 | 50.6654 | 69.4773 |  |  | 0.9399 | -1.2162 | -0.37139 | -0.86937 | 8.0853 | 5.8387 | 7.8879 | -3.1064 | 19.7772 | 52.8604 | 28.113 | -2.957e-05 | -3.45e-05 | -0.00078361 | 28.6086 | 16.4739 | 16.7029 | 17.0989 | 17.1022 | 16.1069 | 14.6435 | 16.6598 | 17.0413 | 17.3838 | 17.4625 | 17.2005 | 16.4013 | 14.6841 | 703.2953 | 485.1381 | 438.404 | 277.9786 | 221.4142 | 737.9453 | 442.3601 | 22.4764 | 39.6426 | 45.5883 | 81.8865 | 85.2066 | 88.777 |  |  |  | 637.4312 | 606.4513 | 607.4279 | 630.0878 | 72.4747 | 27.22 | 830.4596 |  |  | 652.2495 |  |  | 21.5217 | 57.0328 | 585.4326 | 22.1464 | 59.6844 | 832.4436 | 762.1863 | 615.7126 | 824.0295 | 809.7745 | 771.7947 |  | 832.2788 | 901.2111 | 1022.4725 | 596.1658 | 696.4916 | 954.042 |  | 1044.7648 |  |  | 463.4253 | 686.1459 | 757.5771 | [6 empty] | 606.1151 |  |  | 439.082 |  |  | 530.1994 | 680.8873 | 690.8654 | 1033.4977 | 1115.3465 | 1087.2458 | 544.6811 | 728.7881 | 861.7692 | 633.8006 | 711.219 | 1091.0746 | 1120.8362 | 643.9931 | 830.6272 | 1076.8282 | 1121.5623 | 1107.3672 | 553.1553 | 676.0562 | 716.3509 | 571.7079 | 762.6483 | 891.7062 | 1088.2745 | 1153.0223 | 615.4261 | 717.9786 | 679.0988 | 871.3122 | 99.073 | 0.0010814 | 17.7602 | 5.1648 | -40.1103 | 3.1214 | 9547.37 | 0.34 | 2.1122 | -2.4246 | -1.3398 | -2.0499 | 7.1423 | 6.0694 | 7.0545 | 86.3456 | 163.139 | 52.9088 | 63.1086 | 15.3005 | 122.6679 | 39.1854
42810.4533 | 1145 | 17.4392 | 17.8766 | 18.0171 | 18.0679 | 17.4261 | 16.0885 | 15.0823 | 16.4437 | 16.9311 | 17.085 | 17.0927 | 16.6299 | 15.6685 | 14.4385 | 31.9367 | 49.9548 | 48.7113 | 89.6339 | 62.6461 | 92.3642 |  |  |  | 40.7652 | 87.7359 | 507.961 | 697.1395 | 723.0216 | 703.537 | 90.5877 | 130.8129 | 922.2852 | 92.4754 | 125.8709 | 836.3396 | 912.0584 | 859.9555 |  | 254.5163 | 909.3286 | 905.6433 | 540.5963 |  | 478.6145 | 721.8589 | 562.4182 | 719.7368 | 903.1657 | 1028.8371 | 1054.5483 | 51.5281 | 409.1984 | 81.5667 | 624.8723 | 14.641 | 49.1821 | 48.5061 | 50.684 | 69.7162 |  |  | 1.3401 | -1.5244 | -0.090144 | -0.78985 | 8.1734 | 5.0554 | 7.9162 | -3.2167 | 21.3381 | 54.5743 | 29.9986 | -4.764e-05 | 2.464e-05 | -0.00080168 | 28.6889 | 16.4657 | 16.7005 | 17.0886 | 17.1024 | 16.1033 | 14.6391 | 16.6619 | 17.0344 | 17.3778 | 17.4633 | 17.1976 | 16.399 | 14.679 | 716.7829 | 490.5685 | 421.5368 | 271.4255 | 211.3612 | 737.8355 | 442.1528 | 22.5662 | 39.7575 | 45.6985 | 81.9584 | 85.2555 | 88.822 |  |  |  | 637.5305 | 605.0085 | 607.3697 | 626.141 | 80.5169 | 28.955 | 837.4188 |  |  | 654.7999 |  |  | 21.5475 | 57.1031 | 585.8802 | 22.1956 | 59.7546 | 834.2407 | 762.2652 | 616.2687 | 829.0951 | 813.0946 | 774.2861 |  | 833.9935 | 903.719 | 1025.5473 | 596.3278 | 695.7222 | 952.8349 |  |  |  |  | 464.0623 | 685.2277 | 760.7422 | [6 empty] | 606.362 |  |  | 440.3854 |  |  | 530.1003 | 681.3975 | 691.7758 | 1034.9403 | 1114.4348 | 1087.8004 | 544.7537 | 729.5948 | 863.8752 | 633.4603 | 712.3685 | 1092.8824 | 1120.6817 | 643.9662 | 831.3316 | 1076.3779 | 1118.3701 | 1106.4575 | 553.981 | 674.9946 | 715.3374 | 571.8852 | 763.7986 | 892.9653 | 1088.5332 | 1150.823 | 615.6267 | 717.0158 | 680.4716 | 872.4513 | 91.636 | 0.00019745 | 17.7574 | 5.1835 | -40.1119 | 3.1214 | 9524.76 | 0.26 | 2.5212 | -2.7141 | -0.66001 | -1.9537 | 7.189 | 5.6539 | 7.075 | 86.8505 | 164.6769 | 52.724 | 61.5721 | 17.1344 | 122.2008 | 39.3148
42810.4533 | 1146 | 17.4502 | 17.8807 | 18.0317 | 18.0777 | 17.4355 | 16.0911 | 15.1011 | 16.4492 | 16.9261 | 17.0853 | 17.1051 | 16.6344 | 15.6791 | 14.4413 | 32.0837 | 50.1066 | 48.8646 | 89.6271 | 63.3565 | 92.3539 |  |  |  | 40.9722 | 87.7302 | 510.6517 | 697.7887 | 724.0663 | 704.5203 | 89.6193 | 119.2954 | 907.9206 | 92.982 | 131.0047 | 846.0985 | 920.7548 | 864.9659 |  | 241.9577 | 915.5023 | 905.3954 | 523.0473 |  | 477.2752 | 724.5496 | 564.6248 | 722.8789 | 908.435 | 1032.2551 | 1055.5336 | 52.1946 | 409.0587 | 80.8289 | 624.8679 | 14.6486 | 49.1819 | 48.4915 | 50.6983 | 69.9406 |  |  | 0.83673 | -0.26407 | -0.27677 | -1.2564 | 7.927 | 5.0304 | 8.1514 | -2.3599 | 20.4213 | 54.5224 | 32.8498 | 1.15e-05 | -2.136e-05 | -0.00080989 | 28.7657 | 16.4707 | 16.7033 | 17.0929 | 17.0978 | 16.1075 | 14.6473 | 16.6612 | 17.04 | 17.3746 | 17.4624 | 17.199 | 16.3943 | 14.6913 | 721.5005 | 483.4583 | 416.2429 | 274.0766 | 207.4788 | 737.9948 | 441.9702 | 22.6497 | 39.8764 | 45.81 | 82.0028 | 85.2844 | 88.8667 |  |  |  | 637.3557 | 602.17 | 605.1962 | 621.6895 | 81.3079 | 34.7184 | 840.8002 |  |  | 655.5694 |  |  | 21.5855 | 57.1739 | 588.1692 | 22.2428 | 59.8435 | 836.8659 | 757.0951 | 618.0921 | 829.7034 | 813.1566 | 766.5528 |  | 834.6029 | 901.6143 | 1027.5188 | 597.7619 | 695.729 | 945.8602 |  |  |  |  | 464.8067 | 676.5116 | 756.585 | [6 empty] | 608.1329 |  |  | 441.2839 |  |  | 529.613 | 681.9942 | 692.2787 | 1045.2804 | 1113.4202 | 1087.9506 | 544.6976 | 730.1019 | 865.1246 | 633.0466 | 713.1268 | 1096.972 | 1122.9985 | 644.3852 | 830.5894 | 1077.6288 | 1119.0347 | 1105.4587 | 555.0521 | 674.2473 | 714.2889 | 572.0708 | 765.6186 | 894.4464 | 1088.5378 | 1149.5664 | 615.87 | 716.1173 | 681.9258 | 874.2512 | 90.9607 | -0.0007917 | 17.7552 | 5.189 | -40.0997 | 3.1213 | 9505.42 | 0.25 | 1.9932 | -1.1312 | -1.158 | -2.4674 | 7.0891 | 5.6473 | 7.1888 | 87.27 | 165.7717 | 52.6858 | 61.1029 | 17.6871 | 126.2499 | 39.4037
42810.4533 | 1147 | 17.4467 | 17.877 | 18.0266 | 18.0758 | 17.4315 | 16.0922 | 15.0919 | 16.4482 | 16.9264 | 17.086 | 17.1032 | 16.6336 | 15.6717 | 14.4449 | 32.2405 | 50.2592 | 49.0182 | 89.6195 | 64.0079 | 92.3575 |  |  |  | 41.1868 | 87.7244 | 513.0573 | 698.7516 | 725.145 | 705.9429 | 87.2722 | 130.7668 | 925.4368 | 94.3975 | 126.07 | 845.4209 | 890.0658 | 870.3152 |  | 237.6316 | 918.7403 | 913.0082 | 537.9729 |  | 477.3646 | 725.5739 | 563.4793 | 725.425 | 906.9125 | 1032.9072 | 1056.4302 | 52.6935 | 408.9543 | 79.8619 | 624.8483 | 14.6663 | 49.1864 | 48.4719 | 50.7215 | 70.1332 |  |  | 1.1561 | -1.1873 | 0.051136 | -0.64003 | 8.0932 | 5.6146 | 9.7154 | -2.7555 | 21.0478 | 55.5431 | 34.346 | 9.86e-06 | 7.393e-05 | -0.00080168 | 28.8463 | 16.4807 | 16.7017 | 17.0994 | 17.1014 | 16.1098 | 14.6499 | 16.6651 | 17.0454 | 17.3791 | 17.4602 | 17.2028 | 16.396 | 14.6883 | 729.8237 | 496.3673 | 446.6235 | 282.0164 | 228.7607 | 738.8726 | 442.3792 | 22.7304 | 39.9874 | 45.9174 | 82.0478 | 85.3142 | 88.8996 |  |  |  | 637.1154 | 599.4608 | 602.8136 | 619.4796 | 86.6742 | 34.9294 | 841.8498 |  |  | 655.9989 |  |  | 21.6299 | 57.2613 | 590.7525 | 22.3043 | 59.9389 | 837.1128 | 751.4545 | 618.9769 | 829.4453 | 812.8508 | 756.1187 |  | 834.6624 | 898.7428 | 1027.4237 | 598.3727 | 695.7771 | 945.1261 |  |  |  |  | 464.5793 | 666.082 | 750.1481 | [6 empty] | 608.855 |  |  | 442.15 |  |  | 528.9412 | 682.4303 | 692.417 | 1055.3409 | 1114.7685 | 1087.9895 | 544.8918 | 730.188 | 865.5579 | 632.9956 | 712.9932 | 1097.8998 | 1121.3516 | 644.5977 | 829.7547 | 1075.1114 | 1116.5494 | 1103.4101 | 555.2721 | 673.7907 | 713.7188 | 571.8947 | 768.3295 | 895.6528 | 1085.4593 | 1146.9329 | 616.1255 | 715.8295 | 683.5324 | 876.5451 | 81.6861 | 0.0020074 | 17.754 | 5.1917 | -39.9741 | 3.1213 | 9491.63 | 0.23 | 2.3446 | -2.3998 | 0.49803 | -1.7619 | 7.1649 | 5.9677 | 7.8501 | 87.5798 | 165.8014 | 52.6801 | 60.4817 | 14.3909 | 113.5868 | 39.4173
42810.4533 | 1148 | 17.4473 | 17.8726 | 18.0257 | 18.0785 | 17.4316 | 16.0923 | 15.0931 | 16.4489 | 16.9311 | 17.0825 | 17.0945 | 16.631 | 15.6717 | 14.4461 | 32.4066 | 50.4289 | 49.1883 | 89.6217 | 64.6051 | 92.3913 |  |  |  | 41.411 | 87.7231 | 515.1022 | 699.6126 | 725.9276 | 707.297 | 90.9665 | 129.4194 | 922.035 | 93.6001 | 134.2074 | 849.2442 | 909.706 | 866.3991 |  | 232.0333 | 924.2329 | 912.2085 | 622.3355 |  | 477.8302 | 725.2067 | 562.0488 | 723.0216 | 902.714 | 1031.4371 | 1054.325 | 53.0787 | 408.8085 | 79.2461 | 624.7402 | 14.6787 | 49.1689 | 48.4389 | 50.7535 | 70.2698 |  |  | 0.97078 | -0.33241 | -0.27545 | -1.4161 | 7.8205 | 5.9563 | 8.6548 | -3.1445 | 20.7823 | 54.4685 | 29.3892 | -2.3e-05 | -9.86e-06 | -0.00077047 | 28.9372 | 16.4866 | 16.708 | 17.1 | 17.1113 | 16.1094 | 14.6579 | 16.6723 | 17.0467 | 17.3833 | 17.4638 | 17.22 | 16.3956 | 14.6956 | 733.1333 | 501.9447 | 456.249 | 290.5107 | 239.0369 | 740.0939 | 443.2389 | 22.8223 | 40.1026 | 46.0203 | 82.0926 | 85.3546 | 88.9502 |  |  |  | 636.923 | 598.6268 | 602.0036 | 618.5576 | 82.4815 | 34.4852 | 841.9112 |  |  | 657.5058 |  |  | 21.6608 | 57.3387 | 592.6272 | 22.3694 | 60.0166 | 837.3258 | 746.6965 | 619.7921 | 831.3762 | 814.6178 | 748.3977 |  | 834.387 | 900.218 | 1027.4255 | 598.6664 | 695.9677 | 946.3985 |  | 299.4625 |  |  | 463.6249 | 657.1786 | 744.5546 | [6 empty] | 609.0844 |  |  | 443.1595 |  |  | 528.7594 | 682.5546 | 692.665 | 1057.7369 | 1117.6659 | 1083.1788 | 545.086 | 730.1825 | 865.9477 | 633.0588 | 712.8608 | 1092.7876 | 1116.4993 | 644.5212 | 828.6351 | 1068.0455 | 1114.3735 | 1101.5923 | 555.1406 | 673.6858 | 713.9884 | 572.1218 | 770.4602 | 899.9112 | 1086.4699 | 1146.2745 | 616.4252 | 717.0336 | 684.7488 | 880.1843 | 83.7396 | 0.0011866 | 17.7519 | 5.1958 | -40.1663 | 3.1213 | 9488.02 | 0.34 | 2.15 | -1.2695 | -1.1557 | -2.6203 | 7.0392 | 6.1432 | 7.4051 | 87.7018 | 165.7613 | 52.7165 | 60.5373 | 13.4885 | 118.9793 | 39.4046
42810.4533 | 1149 | 17.4454 | 17.8753 | 18.023 | 18.0769 | 17.4292 | 16.0888 | 15.106 | 16.4502 | 16.9311 | 17.0827 | 17.0908 | 16.6348 | 15.6695 | 14.4484 | 32.5597 | 50.5814 | 49.2983 | 89.6389 | 65.0784 | 92.4646 |  |  |  | 41.6159 | 87.7179 | 517.0176 | 700.5073 | 726.1584 | 708.1821 | 56.4364 | 94.3637 | 888.5046 | 58.377 | 97.4174 | 819.6999 | 873.6462 | 834.9982 |  | 245.5751 | 890.451 | 878.9373 | 785.8897 |  | 478.0113 | 726.0769 | 561.1827 | 721.2972 | 910.4818 | 1033.8991 | 1054.9382 | 54.8046 | 408.8244 | 78.9808 | 624.8643 | 14.6861 | 49.1703 | 48.4144 | 50.8014 | 70.491 |  |  | 0.65076 | -1.0171 | -0.1644 | -0.77014 | 8.6274 | 3.845 | 7.9852 | -2.7817 | 19.9991 | 52.7284 | 30.5647 | 4.764e-05 | -9.86e-06 | -0.00076882 | 29.0159 | 16.4819 | 16.6993 | 17.0946 | 17.0955 | 16.1069 | 14.6489 | 16.6625 | 17.0348 | 17.3755 | 17.4578 | 17.207 | 16.392 | 14.6834 | 724.7611 | 503.1944 | 466.4488 | 286.6474 | 240.3187 | 740.8033 | 444.3087 | 22.9054 | 40.2146 | 46.1221 | 82.1348 | 85.385 | 88.9958 |  |  |  | 636.7456 | 598.1563 | 602.7538 | 617.3588 | 61.5696 | 27.4618 | 843.4261 |  |  | 658.7984 |  |  | 21.6926 | 57.4095 | 594.2661 | 22.4248 | 60.0939 | 840.4397 | 743.0697 | 620.7281 | 831.7959 | 814.5054 | 741.113 |  | 833.494 | 903.7238 | 1027.9201 | 599.2652 | 696.1381 | 952.0826 |  | 301.3644 |  |  | 462.5049 | 649.5491 | 739.2384 | [6 empty] | 609.9987 |  |  | 444.0626 |  |  | 529.1469 | 683.2335 | 692.6585 | 1054.0332 | 1120.0273 | 1079.996 | 545.5039 | 730.4133 | 867.861 | 633.5022 | 712.5553 | 1088.6317 | 1117.387 | 644.946 | 828.2144 | 1064.0442 | 1113.6316 | 1102.413 | 555.6501 | 674.5894 | 715.011 | 572.0976 | 771.2087 | 904.0856 | 1085.3952 | 1147.7988 | 616.9215 | 719.334 | 685.2088 | 880.6595 | 97.3766 | -0.00036376 | 17.7508 | 5.2009 | -40.107 | 3.1213 | 9519.75 | 0.3 | 1.7611 | -2.2217 | -0.8932 | -1.9332 | 7.4004 | 4.9404 | 7.1196 | 87.6045 | 165.9246 | 52.7398 | 61.7139 | 12.5635 | 100.5058 | 39.4027
42810.4533 | 1150 | 17.4434 | 17.8736 | 18.0254 | 18.0808 | 17.4305 | 16.0889 | 15.1097 | 16.4529 | 16.9285 | 17.0842 | 17.0948 | 16.6315 | 15.6735 | 14.4475 | 32.713 | 50.7902 | 49.4963 | 89.6813 | 65.6536 | 92.4382 |  |  |  | 41.8124 | 87.733 | 519.5516 | 701.4962 | 726.7777 | 708.7753 | 20.5369 | 67.146 | 886.5893 | 52.7042 | 88.415 | 813.1077 | 894.1888 | 834.4545 |  | 247.1064 | 895.5317 | 889.2549 | 641.4901 |  | 478.5583 | 727.3346 | 562.4782 | 724.4165 | 908.8129 | 1031.5077 | 1054.3625 | 54.836 | 408.7334 | 77.7237 | 624.7181 | 14.6972 | 49.2022 | 48.4056 | 50.8557 | 70.7312 |  |  | 0.64156 | -1.3109 | -0.18477 | -1.3885 | 8.4671 | 6.3946 | 8.5234 | -3.519 | 19.3145 | 52.9752 | 34.0986 | 4.93e-06 | -6.571e-05 | -0.00076554 | 29.09 | 16.4984 | 16.6986 | 17.0891 | 17.0979 | 16.1022 | 14.6512 | 16.6594 | 17.0406 | 17.3857 | 17.458 | 17.2054 | 16.3982 | 14.6868 | 712.3684 | 486.4118 | 440.8602 | 280.5269 | 236.487 | 740.0536 | 444.2525 | 23.0051 | 40.3391 | 46.2503 | 82.2154 | 85.4125 | 89.0508 |  |  |  | 636.7923 | 597.8638 | 602.8901 | 619.3267 | 85.7497 | 33.3413 | 843.7723 |  |  | 659.7849 |  |  | 21.7292 | 57.4853 | 596.1 | 22.4713 | 60.1823 | 843.2186 | 743.3775 | 621.7737 | 831.7916 | 814.4764 | 740.9463 |  | 833.0033 | 904.7439 | 1028.6156 | 600.1538 | 696.3541 | 947.4421 |  | 303.6423 |  |  | 461.6833 | 649.5196 | 738.0597 | [6 empty] | 610.9963 |  |  | 443.6027 |  |  | 529.5918 | 683.7854 | 693.0229 | 1052.7565 | 1117.2689 | 1081.2323 | 545.8906 | 731.0136 | 871.2099 | 634.2899 | 712.2707 | 1090.4005 | 1116.1177 | 644.9917 | 831.6508 | 1072.1768 | 1114.1043 | 1103.4573 | 555.3132 | 676.487 | 716.6999 | 571.9409 | 771.4799 | 904.608 | 1084.8663 | 1147.4822 | 616.8874 | 720.6727 | 685.3524 | 881.0392 | 82.8338 | -2.0022e-05 | 17.7481 | 5.2025 | -40.1157 | 3.1213 | 9572.82 | 0.27 | 1.7491 | -2.5238 | -0.94752 | -2.5974 | 7.3246 | 6.3653 | 7.3489 | 87.4448 | 166.2633 | 52.7658 | 62.8306 | 15.3957 | 112.3055 | 39.3573
42810.4534 | 1151 | 17.4421 | 17.8731 | 18.028 | 18.0722 | 17.4345 | 16.0919 | 15.1057 | 16.4544 | 16.9275 | 17.0845 | 17.0984 | 16.6363 | 15.6727 | 14.4475 | 32.8573 | 50.8989 | 49.6364 | 89.7061 | 65.8607 | 92.3911 |  |  |  | 42.0126 | 87.724 | 521.8611 | 702.1244 | 727.3529 | 709.1909 | 71.0618 | 116.3315 | 918.398 | 83.4217 | 121.5919 | 834.5735 | 922.2957 | 862.9384 |  | 244.4278 | 925.5003 | 921.7984 | 512.6581 |  | 479.2586 | 728.384 | 562.4892 | 726.0501 | 911.0879 | 1030.3761 | 1053.3197 | 54.6888 | 408.3354 | 76.4105 | 624.385 | 14.7036 | 49.2328 | 48.4116 | 50.9059 | 70.9556 |  |  | 0.66785 | -0.11031 | -0.59547 | -0.88842 | 8.7641 | 5.8019 | 8.9104 | -3.1307 | 19.7509 | 52.8598 | 29.9507 | -2.464e-05 | 7.064e-05 | -0.00079182 | 29.183 | 16.5051 | 16.7093 | 17.0935 | 17.1135 | 16.1165 | 14.6645 | 16.6704 | 17.0444 | 17.3915 | 17.469 | 17.21 | 16.3974 | 14.6978 | 727.3017 | 478.7042 | 431.5233 | 288.3456 | 249.2265 | 740.4628 | 444.4974 | 23.0848 | 40.449 | 46.3562 | 82.2615 | 85.4778 | 89.0762 |  |  |  | 637.1193 | 599.3756 | 603.7624 | 623.0342 | 66.9871 | 27.5529 | 844.4874 |  |  | 661.023 |  |  | 21.758 | 57.5637 | 598.1868 | 22.5312 | 60.2721 | 842.1154 | 743.9352 | 623.3003 | 832.4138 | 815.5171 | 744.8328 |  | 832.6516 | 902.3192 | 1028.759 | 600.9195 | 696.7074 | 939.6975 |  | 305.1465 |  |  | 460.9719 | 653.5925 | 740.4571 | [6 empty] | 612.7382 |  |  | 441.1336 |  |  | 530.3811 | 683.6632 | 693.5234 | 1044.8707 | 1113.031 | 1080.4282 | 545.6365 | 730.5732 | 872.5304 | 634.8521 | 712.1856 | 1084.3752 | 1110.2551 | 644.6074 | 830.5644 | 1071.9244 | 1110.8883 | 1105.2194 | 555.686 | 677.9618 | 716.7487 | 571.0628 | 771.8068 | 903.5962 | 1078.4946 | 1143.9559 | 617.6054 | 719.8733 | 685.3874 | 878.4735 | 88.403 | -0.00040586 | 17.7458 | 5.2043 | -40.1201 | 3.1213 | 9632.32 | 0.31 | 1.785 | -0.7325 | -1.7019 | -2.0788 | 7.4487 | 6.0605 | 7.5106 | 87.2191 | 166.4064 | 52.8274 | 61.3133 | 16.4809 | 127.1772 | 39.3193
42810.4534 | 1152 | 17.4344 | 17.867 | 18.0257 | 18.0671 | 17.4273 | 16.0892 | 15.1095 | 16.4492 | 16.9292 | 17.0734 | 17.0997 | 16.6392 | 15.6707 | 14.4459 | 33.0399 | 51.0538 | 49.8001 | 89.7197 | 66.373 | 92.3752 |  |  |  | 42.2343 | 87.7191 | 522.9455 | 702.1842 | 727.2573 | 709.1125 | 90.8543 | 131.0959 | 927.6615 | 96.6232 | 125.6274 | 837.007 | 921.8849 | 857.1599 |  | 246.6147 | 915.8181 | 916.913 | 506.365 |  | 478.2476 | 726.9472 | 561.1091 | 724.7604 | 907.4513 | 1027.7885 | 1050.565 | 54.8464 | 407.909 | 76.1643 | 624.3302 | 14.6899 | 49.2802 | 48.4169 | 50.929 | 71.1757 |  |  | 1.1153 | -0.86796 | -0.3819 | -1.5856 | 8.8101 | 5.9905 | 8.2704 | -3.2207 | 19.9066 | 53.3497 | 31.7285 | 4.436e-05 | -3.943e-05 | -0.00073925 | 29.2546 | 16.505 | 16.7044 | 17.095 | 17.1079 | 16.1088 | 14.6584 | 16.6665 | 17.0437 | 17.3822 | 17.462 | 17.2116 | 16.3928 | 14.6848 | 695.5018 | 482.4292 | 445.9544 | 276.6507 | 229.6867 | 738.9212 | 444.4456 | 23.1716 | 40.5667 | 46.4706 | 82.3124 | 85.5217 | 89.1296 |  |  |  | 637.2765 | 599.8451 | 603.5732 | 622.8018 | 64.8531 | 27.6713 | 845.8423 |  |  | 663.2046 |  |  | 21.7918 | 57.6334 | 599.3137 | 22.5819 | 60.3557 | 839.3235 | 742.2476 | 624.3674 | 834.961 | 817.8972 | 743.948 |  | 831.5068 | 901.5064 | 1029.0902 | 601.735 | 697.0648 | 940.9867 |  | 306.5334 |  |  | 460.4584 | 654.0417 | 738.8688 | [6 empty] | 613.6157 |  |  | 439.2152 |  |  | 531.3177 | 683.1435 | 694.0969 | 1048.9498 | 1106.2872 | 1073.1538 | 547.2582 | 729.924 | 869.8132 | 635.2324 | 712.1218 | 1081.6711 | 1100.6267 | 645.8309 | 828.5266 | 1065.1328 | 1103.6294 | 1103.1905 | 556.522 | 678.2533 | 716.3566 | 571.5853 | 771.9418 | 901.7577 | 1076.5771 | 1138.5803 | 617.8215 | 719.4692 | 686.313 | 877.1779 | 91.0638 | 0.00014834 | 17.7443 | 5.2059 | -40.2266 | 3.1213 | 9580.87 | 0.38 | 2.3067 | -2.0532 | -1.362 | -2.7752 | 7.4608 | 6.1521 | 7.2287 | 86.8614 | 166.604 | 52.8886 | 64.3121 | 14.8673 | 127.1815 | 39.357
42810.4534 | 1153 | 17.437 | 17.8653 | 18.0224 | 18.0717 | 17.4307 | 16.0831 | 15.1082 | 16.462 | 16.9271 | 17.0787 | 17.0953 | 16.6267 | 15.6664 | 14.4394 | 33.1724 | 51.2109 | 49.9535 | 89.7151 | 66.4328 | 92.4042 |  |  |  | 42.4399 | 87.7267 | 523.3504 | 701.6762 | 726.4101 | 708.213 | 99.568 | 128.2138 | 924.2091 | 102.4761 | 133.9812 | 851.953 | 926.3736 | 865.6056 |  | 245.7203 | 917.9027 | 900.6209 | 560.5794 |  | 477.1355 | 725.4931 | 560.0398 | 724.5089 | 910.0748 | 1029.0571 | 1049.9688 | 54.9392 | 407.7429 | 77.416 | 624.3288 | 14.684 | 49.3218 | 48.4277 | 50.9654 | 71.3926 |  |  | 1.4367 | -0.51443 | -0.37008 | -0.48495 | 7.371 | 5.5555 | 8.7297 | -3.1261 | 19.9868 | 53.1445 | 36.0562 | 2.629e-05 | -3.28e-06 | -0.00075732 | 29.3382 | 16.4976 | 16.7018 | 17.0901 | 17.1023 | 16.1099 | 14.6572 | 16.6641 | 17.0388 | 17.3813 | 17.457 | 17.2046 | 16.3965 | 14.6895 | 673.4596 | 468.551 | 432.2214 | 269.1579 | 234.5927 | 737.2486 | 443.9375 | 23.2579 | 40.68 | 46.5815 | 82.3662 | 85.5578 | 89.1728 |  |  |  | 637.3825 | 599.8741 | 602.9755 | 623.7863 | 70.3861 | 22.7306 | 848.2547 |  |  | 666.1622 |  |  | 21.8304 | 57.702 | 599.5718 | 22.6219 | 60.4466 | 840.9476 | 741.4383 | 624.3802 | 840.869 | 824.2529 | 745.4008 |  | 830.7192 | 912.8125 | 1030.1365 | 601.9814 | 697.2353 | 939.4308 |  | 312.0284 |  |  | 461.6409 | 657.524 | 738.3193 | [6 empty] | 613.7041 |  |  | 438.5294 |  |  | 531.9454 | 682.4855 | 694.1139 | 1055.5219 | 1107.5808 | 1067.1833 | 548.648 | 730.3676 | 867.5488 | 634.9352 | 712.408 | 1079.4355 | 1096.7159 | 646.7017 | 831.9344 | 1055.8074 | 1099.9324 | 1102.2393 | 556.0604 | 677.5163 | 716.6329 | 572.968 | 772.1521 | 902.9 | 1069.2068 | 1134.5323 | 618.2638 | 718.6166 | 687.3111 | 879.08 | 85.2944 | 0.00015539 | 17.7428 | 5.2069 | -40.1918 | 3.1213 | 9534.86 | 0.34 | 2.6167 | -1.5796 | -1.3397 | -1.5336 | 6.8276 | 5.9274 | 7.4303 | 86.5586 | 166.8437 | 52.9218 | 66.1831 | 16.2942 | 127.5475 | 39.3508
42810.4534 | 1154 | 17.4273 | 17.8587 | 18.012 | 18.0647 | 17.4175 | 16.0872 | 15.1029 | 16.4455 | 16.9186 | 17.0741 | 17.0981 | 16.627 | 15.668 | 14.4352 | 33.3524 | 51.3945 | 50.1102 | 89.7148 | 66.4784 | 92.4432 |  |  |  | 42.6786 | 87.7434 | 525.611 | 701.9573 | 726.3248 | 708.5399 | 85.003 | 126.8017 | 919.8509 | 77.7779 | 112.0023 | 843.1595 | 907.1325 | 868.7189 |  | 248.9536 | 914.1358 | 902.8534 | 547.4411 |  | 477.3133 | 725.8172 | 560.3618 | 724.5394 | 916.8491 | 1031.2503 | 1048.6056 | 53.8525 | 407.4945 | 80.6734 | 624.4041 | 14.6518 | 49.3316 | 48.4528 | 50.9815 | 71.6043 |  |  | 1.2678 | -0.63337 | -0.21763 | -1.1789 | 7.2324 | 4.9174 | 7.9188 | -3.4198 | 19.2625 | 52.2528 | 32.0891 | 3.29e-06 | 3.121e-05 | -0.00078032 | 29.426 | 16.5064 | 16.7037 | 17.0892 | 17.1004 | 16.1137 | 14.6621 | 16.6636 | 17.0464 | 17.3861 | 17.46 | 17.205 | 16.4028 | 14.6926 | 669.6456 | 451.3879 | 392.5592 | 260.0445 | 229.351 | 735.8724 | 443.1329 | 23.3413 | 40.7882 | 46.6828 | 82.4298 | 85.6036 | 89.2244 |  |  |  | 637.7988 | 602.0361 | 604.1276 | 628.6895 | 74.9953 | 22.6091 | 854.9964 |  |  | 668.4787 |  |  | 21.8723 | 57.7823 | 600.3808 | 22.681 | 60.5317 | 848.3738 | 739.2305 | 623.7223 | 842.2795 | 824.5921 | 745.8552 |  | 829.7036 | 921.5097 | 1033.3379 | 602.7554 | 697.2169 | 929.6904 |  | 315.5112 |  |  | 462.6827 | 659.4645 | 738.2718 | [6 empty] | 613.421 |  |  | 440.0588 |  |  | 532.5661 | 681.7811 | 693.6388 | 1060.4945 | 1112.9997 | 1065.7288 | 549.003 | 731.0174 | 867.4142 | 634.0277 | 712.5653 | 1076.7659 | 1099.1411 | 647.0352 | 833.291 | 1050.5746 | 1097.7186 | 1103.5487 | 555.7879 | 676.9347 | 717.5119 | 573.4842 | 773.016 | 905.0838 | 1068.6389 | 1136.8003 | 618.6094 | 717.808 | 687.6363 | 879.8312 | 87.9539 | -0.00036376 | 17.7397 | 5.2089 | -40.1735 | 3.1213 | 9458.74 | 0.3 | 2.4585 | -1.753 | -1.0275 | -2.3915 | 6.7688 | 5.5814 | 7.0828 | 86.2084 | 168.3043 | 52.896 | 66.1327 | 20.5445 | 120.0254 | 39.2975
42810.4534 | 1155 | 17.4384 | 17.8663 | 18.0289 | 18.0662 | 17.4233 | 16.0877 | 15.1166 | 16.4528 | 16.9313 | 17.0753 | 17.1043 | 16.6329 | 15.6777 | 14.4451 | 33.4938 | 51.5282 | 50.2673 | 89.7254 | 66.7713 | 92.4486 |  |  |  | 42.8901 | 87.7538 | 527.593 | 702.4501 | 726.8396 | 709.3115 | 86.1134 | 126.7257 | 928.6431 | 94.8484 | 126.4154 | 833.8925 | 916.9705 | 858.7178 |  | 236.1914 | 942.1341 | 923.9429 | 532.4407 |  | 478.4704 | 727.4379 | 559.8404 | 724.021 | 920.3602 | 1030.2288 | 1049.4285 | 52.8671 | 407.2158 | 82.6878 | 624.2323 | 14.6365 | 49.3266 | 48.4794 | 50.993 | 71.8096 |  |  | 0.78941 | -0.88833 | 0.1129 | -0.94887 | 8.7891 | 6.0319 | 8.9432 | -2.9388 | 19.7509 | 52.4547 | 31.2324 | -6.078e-05 | 8.22e-06 | -0.00074254 | 29.5069 | 16.5094 | 16.7031 | 17.0869 | 17.1025 | 16.1115 | 14.664 | 16.6653 | 17.0488 | 17.3887 | 17.461 | 17.2086 | 16.4007 | 14.695 | 679.4953 | 455.9907 | 389.3521 | 252.0994 | 228.9563 | 735.1306 | 442.3286 | 23.4519 | 40.9239 | 46.8138 | 82.5117 | 85.6645 | 89.281 |  |  |  | 638.3683 | 603.5692 | 604.9555 | 631.2676 | 76.1033 | 25.9648 | 855.8804 |  |  | 666.5329 |  |  | 21.9136 | 57.8601 | 601.8762 | 22.7399 | 60.6054 | 856.3038 | 735.133 | 623.6199 | 838.7054 | 820.9831 | 741.0029 |  | 828.3568 | 911.0312 | 1035.1675 | 603.4608 | 697.2303 | 917.9812 |  | 319.8948 |  |  | 463.3096 | 654.9361 | 734.3672 | [6 empty] | 613.7255 |  |  | 440.8297 |  |  | 532.6522 | 681.7582 | 693.9803 | 1058.8194 | 1113.7573 | 1065.5103 | 549.1926 | 731.1096 | 865.7702 | 633.9277 | 713.5993 | 1078.142 | 1103.8979 | 647.1979 | 830.0939 | 1045.6054 | 1101.8817 | 1103.5109 | 555.4252 | 676.5091 | 718.1728 | 574.0336 | 773.5207 | 905.2764 | 1067.8898 | 1139.3998 | 618.8358 | 717.3757 | 687.9556 | 880.0503 | 93.6481 | -0.00096006 | 17.7371 | 5.2101 | -40.149 | 3.1213 | 9363.09 | 0.2 | 1.9408 | -2.0777 | 0.74071 | -2.1473 | 7.4589 | 6.1791 | 7.524 | 85.8968 | 169.5735 | 52.8796 | 64.7832 | 20.7446 | 124.4302 | 39.3394
42810.4534 | 1156 | 17.4403 | 17.8679 | 18.0208 | 18.0617 | 17.4257 | 16.0881 | 15.1135 | 16.4455 | 16.9267 | 17.0758 | 17.098 | 16.6324 | 15.6725 | 14.4466 | 33.6496 | 51.6826 | 50.4195 | 89.7399 | 67.0715 | 92.4666 |  |  |  | 43.1026 | 87.7586 | 529.2084 | 702.756 | 727.1966 | 709.9212 | 78.8322 | 125.6524 | 933.1525 | 93.5215 | 126.5869 | 839.0466 | 916.8027 | 842.1049 |  | 246.5054 | 937.0507 | 939.0776 | 511.8052 |  | 478.3777 | 727.6077 | 559.612 | 721.1231 | 919.3567 | 1028.993 | 1051.0477 | 53.3697 | 406.9606 | 84.4421 | 623.887 | 14.5771 | 49.3096 | 48.504 | 51.0155 | 72.0163 |  |  | 1.2303 | -0.75757 | 0.17664 | -0.68931 | 8.8055 | 5.4819 | 9.2258 | -2.8566 | 19.54 | 52.6212 | 37.2887 | -3.45e-05 | -5.421e-05 | -0.00077375 | 29.5783 | 16.5251 | 16.7052 | 17.0958 | 17.1107 | 16.1092 | 14.6703 | 16.6692 | 17.0505 | 17.3959 | 17.4685 | 17.2169 | 16.4073 | 14.6971 | 694.9449 | 458.0329 | 391.2053 | 253.0573 | 220.456 | 734.7933 | 441.6879 | 23.5364 | 41.0313 | 46.9218 | 82.5685 | 85.713 | 89.3205 |  |  |  | 638.6814 | 603.183 | 604.2248 | 629.7778 | 80.7726 | 30.6403 | 852.1066 |  |  | 663.9411 |  |  | 21.9464 | 57.9377 | 603.1272 | 22.7956 | 60.6795 | 860.3023 | 732.2565 | 624.8199 | 836.6992 | 819.8328 | 737.9701 |  | 827.4146 | 904.879 | 1034.5884 | 604.5836 | 697.432 | 909.5543 |  | 324.9319 |  |  | 464.4184 | 651.5509 | 730.8294 | [6 empty] | 614.8029 |  |  | 441.4955 |  |  | 532.9896 | 682.8433 | 695.0491 | 1060.6093 | 1108.2494 | 1064.3203 | 549.2566 | 731.4821 | 863.5421 | 634.7856 | 715.4195 | 1079.499 | 1101.7538 | 647.3343 | 830.948 | 1036.7161 | 1103.4922 | 1104.0155 | 556.2411 | 676.0517 | 718.7728 | 575.1052 | 774.3015 | 906.9019 | 1063.2918 | 1139.2188 | 619.0318 | 717.5612 | 688.2968 | 882.2978 | 86.4371 | -0.0012126 | 17.7338 | 5.2096 | -40.2155 | 3.1213 | 9356.45 | 0.45 | 2.4237 | -1.9189 | 0.92658 | -1.8304 | 7.4623 | 5.8879 | 7.6383 | 85.6696 | 169.4343 | 52.8958 | 62.9507 | 20.4143 | 124.9346 | 39.4433
42810.4534 | 1157 | 17.4399 | 17.8714 | 18.0298 | 18.0677 | 17.4223 | 16.0926 | 15.1263 | 16.452 | 16.9294 | 17.0809 | 17.1008 | 16.6419 | 15.6737 | 14.4505 | 33.7916 | 51.8369 | 50.5618 | 89.7416 | 67.469 | 92.4851 |  |  |  | 43.3067 | 87.7602 | 529.933 | 702.6211 | 726.519 | 709.7203 | 95.5365 | 119.0053 | 931.8491 | 88.2282 | 119.3842 | 840.6219 | 918.6782 | 857.1611 |  | 245.956 | 922.899 | 917.7277 | 530.883 |  | 478.4645 | 726.8466 | 559.4877 | 722.4774 | 919.7881 | 1029.8783 | 1052.5971 | 55.5726 | 406.8773 | 85.5293 | 623.7394 | 14.5335 | 49.2974 | 48.5205 | 51.029 | 72.2246 |  |  | 0.64419 | -0.11688 | -1.6048 | -1.5423 | 8.2154 | 6.2895 | 8.2658 | -3.7096 | 20.4965 | 54.2854 | 40.7401 | 2.629e-05 | 1.15e-05 | -0.00076225 | 29.6784 | 16.5246 | 16.7101 | 17.1018 | 17.1085 | 16.121 | 14.6723 | 16.6685 | 17.0496 | 17.3874 | 17.4686 | 17.2145 | 16.409 | 14.7017 | 690.9721 | 455.8368 | 394.3094 | 255.3689 | 220.4198 | 734.9 | 441.7324 | 23.623 | 41.1389 | 47.0209 | 82.6226 | 85.7506 | 89.3625 |  |  |  | 638.8319 | 601.6435 | 602.7382 | 627.8851 | 74.9438 | 33.8126 | 849.897 |  |  | 663.9211 |  |  | 21.9764 | 58.0169 | 603.8019 | 22.8403 | 60.7566 | 858.9859 | 729.5576 | 626.3312 | 837.6208 | 822.3227 | 734.4883 |  | 826.4509 | 901.4989 | 1033.4221 | 607.0607 | 697.8517 | 910.1218 |  | 327.9745 |  |  | 464.8614 | 649.1421 | 728.681 | [6 empty] | 616.6938 |  |  | 443.4005 |  |  | 533.6165 | 684.871 | 696.1501 | 1061.7806 | 1105.5606 | 1063.3549 | 548.9128 | 731.5377 | 863.2273 | 635.9289 | 717.1433 | 1076.596 | 1100.5041 | 646.8356 | 831.6777 | 1030.962 | 1104.1862 | 1104.9095 | 556.9085 | 675.4865 | 719.3997 | 575.3801 | 773.8302 | 909.1874 | 1064.1251 | 1139.5036 | 619.3567 | 718.0063 | 687.9546 | 881.0995 | 83.9225 | -0.0011354 | 17.7311 | 5.2086 | -40.2087 | 3.1213 | 9358.6 | 0.26 | 1.7536 | -0.75341 | -2.7917 | -2.7368 | 7.2104 | 6.3089 | 7.2324 | 85.4486 | 168.9051 | 52.9258 | 63.4288 | 20.0781 | 125.1752 | 39.5259
42810.4534 | 1158 | 17.4338 | 17.8618 | 18.0236 | 18.0675 | 17.4189 | 16.0902 | 15.1288 | 16.4496 | 16.9305 | 17.08 | 17.1021 | 16.6343 | 15.6703 | 14.45 | 33.9479 | 51.9919 | 50.7146 | 89.7501 | 68.075 | 92.4915 |  |  |  | 43.5262 | 87.7767 | 530.292 | 701.8043 | 725.2443 | 708.5715 | 100.5728 | 118.3197 | 924.933 | 78.9146 | 113.2309 | 832.1689 | 915.4303 | 856.657 |  | 241.3672 | 931.6301 | 921.8149 | 544.073 |  | 477.5949 | 725.4864 | 558.8421 | 723.1488 | 920.3934 | 1029.0407 | 1051.1576 | 57.8569 | 406.9929 | 90.2604 | 624.0906 | 14.5287 | 49.2812 | 48.5346 | 51.0505 | 72.4202 |  |  | 1.1515 | -0.33176 | 0.01762 | -1.01 | 8.2161 | 6.6988 | 10.1859 | -2.3448 | 19.2298 | 51.7885 | 38.8589 | -3.121e-05 | -3.28e-06 | -0.00075897 | 29.7556 | 16.5271 | 16.7026 | 17.096 | 17.1027 | 16.1166 | 14.6732 | 16.6752 | 17.0406 | 17.3878 | 17.4724 | 17.2103 | 16.4081 | 14.7001 | 686.4442 | 459.1953 | 406.2206 | 264.1229 | 218.9421 | 734.4353 | 442.1649 | 23.7049 | 41.2469 | 47.1212 | 82.6708 | 85.7815 | 89.402 |  |  |  | 638.9706 | 600.5985 | 601.4543 | 626.9993 | 69.0972 | 26.9838 | 851.4602 |  |  | 665.1857 |  |  | 22.0187 | 58.0956 | 603.9875 | 22.8858 | 60.8441 | 855.9632 | 726.9971 | 626.7065 | 839.2611 | 825.1287 | 728.6852 |  | 825.1663 | 903.1245 | 1034.9376 | 609.4466 | 698.374 | 911.1861 |  | 330.747 |  |  | 463.8912 | 644.4695 | 725.2371 | [6 empty] | 617.9418 |  |  | 446.7945 |  |  | 534.04 | 686.6685 | 697.1622 | 1066.2584 | 1111.226 | 1063.3517 | 548.6291 | 731.4079 | 863.204 | 636.6848 | 718.4576 | 1075.1035 | 1104.226 | 646.5479 | 831.2348 | 1029.4499 | 1102.914 | 1104.4402 | 557.2716 | 675.1899 | 719.5142 | 575.6983 | 772.8282 | 908.2518 | 1062.4828 | 1137.9091 | 620.0813 | 717.3617 | 687.199 | 879.6339 | 92.5056 | 0.00038689 | 17.7284 | 5.2041 | -40.2543 | 3.1213 | 9448.94 | 0.3 | 2.3431 | -1.2685 | 0.29233 | -2.2132 | 7.2084 | 6.5088 | 8.0261 | 85.1874 | 169.67 | 52.9825 | 63.7724 | 18.8385 | 123.4766 | 39.5782
42810.4534 | 1159 | 17.4357 | 17.8612 | 18.0234 | 18.0689 | 17.4239 | 16.0881 | 15.1342 | 16.4485 | 16.9269 | 17.0808 | 17.0986 | 16.636 | 15.6717 | 14.4509 | 34.1022 | 52.145 | 50.8582 | 89.7656 | 68.6291 | 92.4935 |  |  |  | 43.7421 | 87.7808 | 529.9746 | 700.3645 | 723.2775 | 706.9997 | 83.1886 | 136.9922 | 939.2828 | 89.7201 | 111.0408 | 811.4526 | 898.3391 | 831.5427 |  | 248.1003 | 923.6866 | 921.0309 | 533.5607 |  | 476.4379 | 723.8384 | 557.9454 | 720.0927 | 919.2708 | 1030.1428 | 1048.7286 | 60.2214 | 407.2687 | 99.73 | 624.5035 | 14.5193 | 49.2729 | 48.5408 | 51.0664 | 72.6146 |  |  | 1.1298 | -0.19639 | 0.51637 | -0.87725 | 7.8987 | 6.459 | 10.3179 | -3.2082 | 21.1624 | 54.8147 | 35.4619 | 8.22e-06 | 3.121e-05 | -0.00074582 | 29.8388 | 16.528 | 16.7057 | 17.0925 | 17.1057 | 16.113 | 14.6684 | 16.6768 | 17.0445 | 17.3872 | 17.4675 | 17.2132 | 16.411 | 14.7021 | 675.2816 | 452.6881 | 396.6757 | 265.1676 | 220.22 | 733.4427 | 441.8463 | 23.8032 | 41.3669 | 47.2408 | 82.7233 | 85.8209 | 89.4431 |  |  |  | 639.143 | 599.7482 | 600.2952 | 626.0815 | 77.8335 | 25.0912 | 853.5804 |  |  | 668.2516 |  |  | 22.0639 | 58.1757 | 603.2301 | 22.9356 | 60.9315 | 857.7942 | 727.9364 | 625.9757 | 841.9771 | 828.9034 | 727.0143 |  | 824.2837 | 907.297 | 1036.5181 | 610.7435 | 698.8115 | 909.1768 |  | 333.4289 |  |  | 463.7108 | 643.7842 | 724.1767 | [6 empty] | 618.061 |  |  | 449.6058 |  |  | 534.2585 | 688.0155 | 697.7853 | 1068.9996 | 1115.3873 | 1064.0942 | 548.5194 | 732.0323 | 863.5082 | 636.9934 | 718.8005 | 1074.279 | 1105.3093 | 646.4843 | 831.9453 | 1029.5106 | 1097.4571 | 1101.5648 | 558.293 | 675.0659 | 718.4903 | 576.0768 | 772.5534 | 906.5875 | 1060.0614 | 1135.878 | 620.7074 | 715.8099 | 686.6252 | 879.55 | 91.6017 | -0.00046899 | 17.7258 | 5.1939 | -40.2025 | 3.1213 | 9540.75 | 0.27 | 2.3191 | -0.97515 | 1.5812 | -2.061 | 7.0708 | 6.394 | 8.0814 | 84.9444 | 170.4018 | 53.0497 | 64.6724 | 19.8373 | 116.9241 | 39.6382
42810.4535 | 1160 | 17.4364 | 17.868 | 18.0211 | 18.0655 | 17.4198 | 16.0836 | 15.1366 | 16.4466 | 16.9274 | 17.071 | 17.0955 | 16.6324 | 15.6637 | 14.4563 | 34.2608 | 52.2929 | 51.0083 | 89.7809 | 69.0684 | 92.5256 |  |  |  | 43.9491 | 87.8066 | 529.2913 | 699.0485 | 721.4925 | 705.7522 | 84.6197 | 119.9551 | 942.5572 | 95.4799 | 121.4737 | 824.8355 | 902.1668 | 807.7855 |  | 257.0046 | 914.5104 | 916.1456 | 539.4061 |  | 478.2039 | 724.6579 | 559.0605 | 721.2561 | 924.8657 | 1033.2853 | 1049.1399 | 63.0774 | 407.5757 | 103.0982 | 625.2481 | 14.543 | 49.2879 | 48.5285 | 51.0584 | 72.7991 |  |  | 0.63762 | -0.87913 | 0.01762 | -1.2971 | 7.4223 | 5.769 | 9.0793 | -3.4218 | 19.958 | 54.5143 | 32.728 | 3.286e-05 | -1.64e-06 | -0.0007409 | 29.9169 | 16.5245 | 16.6968 | 17.0857 | 17.1003 | 16.1031 | 14.6542 | 16.6655 | 17.0371 | 17.382 | 17.4653 | 17.2137 | 16.4003 | 14.6977 | 687.0017 | 453.0403 | 391.404 | 258.7931 | 210.3798 | 733.5714 | 441.4887 | 23.9109 | 41.4934 | 47.3594 | 82.7831 | 85.8647 | 89.5148 |  |  |  | 639.0787 | 597.623 | 598.7232 | 622.0989 | 85.9912 | 37.4983 | 857.5998 |  |  | 674.9434 |  |  | 22.0996 | 58.2433 | 602.0913 | 22.99 | 60.9927 | 862.2169 | 731.6517 | 625.6358 | 848.4255 | 836.1107 | 732.9354 |  | 824.1778 | 915.2529 | 1039.1156 | 610.6844 | 699.1631 | 915.4309 |  | 334.9615 |  |  | 463.7633 | 648.3894 | 727.0483 | [6 empty] | 617.7808 |  |  | 451.614 |  |  | 534.7086 | 688.8253 | 698.095 | 1069.769 | 1117.4092 | 1064.6102 | 548.7861 | 732.3219 | 863.9287 | 637.5319 | 718.2997 | 1073.8886 | 1102.0592 | 646.1145 | 831.2029 | 1027.7158 | 1092.8709 | 1099.2913 | 558.7181 | 674.6112 | 717.2605 | 576.469 | 773.1599 | 904.9918 | 1056.7498 | 1135.156 | 620.7741 | 714.9945 | 686.5707 | 881.2853 | 94.437 | -0.00016731 | 17.7228 | 5.1894 | -40.172 | 3.1213 | 9622.28 | 0.25 | 1.7411 | -2.064 | 0.29221 | -2.5072 | 6.8625 | 6.0501 | 7.5899 | 84.7453 | 171.5802 | 53.1343 | 63.4143 | 20.3536 | 118.2706 | 39.736
42810.4535 | 1161 | 17.4418 | 17.8675 | 18.019 | 18.0644 | 17.4337 | 16.0891 | 15.1338 | 16.4563 | 16.9227 | 17.0831 | 17.0992 | 16.6327 | 15.6724 | 14.4557 | 34.4081 | 52.4458 | 51.1573 | 89.7845 | 69.5802 | 92.5453 |  |  |  | 44.1625 | 87.8075 | 529.3886 | 698.5643 | 720.822 | 705.1108 | 40.9105 | 116.3148 | 911.7718 | 74.9336 | 116.7121 | 831.4792 | 915.5865 | 831.4449 |  | 254.8835 | 907.434 | 886.4316 | 582.642 |  | 480.0387 | 725.6319 | 561.3235 | 721.3463 | 928.2789 | 1033.8469 | 1048.7732 | 65.2636 | 407.7971 | 102.7754 | 625.8574 | 14.5635 | 49.304 | 48.5167 | 51.0647 | 72.9598 |  |  | 0.7835 | -0.95207 | -0.55276 | -0.79643 | 8.2325 | 5.0271 | 8.3341 | -3.6084 | 19.1329 | 53.1623 | 32.419 | -7.721e-05 | 1.479e-05 | -0.00078197 | 29.9946 | 16.5265 | 16.6968 | 17.0772 | 17.1002 | 16.1017 | 14.6532 | 16.6599 | 17.0323 | 17.3786 | 17.4647 | 17.2072 | 16.398 | 14.6911 | 703.6813 | 481.0809 | 455.5191 | 268.5353 | 211.3117 | 733.949 | 441.843 | 23.9929 | 41.5953 | 47.4629 | 82.8328 | 85.8957 | 89.5624 |  |  |  | 638.9926 | 595.7182 | 597.8442 | 621.5628 | 57.6412 | 25.9792 | 864.6389 |  |  | 683.4706 |  |  | 22.1291 | 58.3089 | 601.7286 | 23.0486 | 61.0682 | 867.3844 | 735.5337 | 624.8421 | 853.943 | 840.4099 | 738.615 |  | 824.1848 | 919.7348 | 1042.0351 | 610.5713 | 699.3509 | 919.9799 |  | 337.4741 |  |  | 464.089 | 656.8691 | 731.1172 | [6 empty] | 617.1093 |  |  | 452.904 |  |  | 535.1762 | 689.1107 | 698.3312 | 1070.7357 | 1117.8151 | 1065.1341 | 549.5907 | 731.9927 | 862.6278 | 638.0464 | 717.059 | 1076.4529 | 1100.2634 | 646.0943 | 829.3925 | 1023.9744 | 1092.0636 | 1100.2346 | 559.114 | 674.0816 | 716.8673 | 576.5047 | 773.9837 | 903.7284 | 1057.4963 | 1135.8992 | 620.4986 | 715.5807 | 686.5019 | 880.8939 | 97.0425 | 9.9273e-05 | 17.7195 | 5.174 | -40.1497 | 3.1212 | 9637.11 | 0.26 | 1.9294 | -2.149 | -1.6375 | -1.9655 | 7.2289 | 5.6489 | 7.2733 | 84.5898 | 173.0381 | 53.1819 | 61.6904 | 13.2985 | 122.469 | 39.7337
42810.4535 | 1162 | 17.4325 | 17.8659 | 18.0135 | 18.0652 | 17.4236 | 16.0915 | 15.1393 | 16.458 | 16.9288 | 17.0766 | 17.0972 | 16.6336 | 15.6698 | 14.4527 | 34.5595 | 52.5975 | 51.3035 | 89.8002 | 70.0028 | 92.5902 |  |  |  | 44.392 | 87.8122 | 530.2605 | 698.5226 | 720.709 | 704.8285 | 51.9372 | 87.9787 | 895.167 | 27.6555 | 70.6834 | 771.8323 | 878.4517 | 802.3111 |  | 241.8059 | 887.1528 | 874.7813 | 600.0884 |  | 481.8231 | 725.39 | 561.9273 | 718.8733 | 923.9181 | 1030.8795 | 1046.3847 | 66.3193 | 408.066 | 102.0505 | 626.3318 | 14.563 | 49.3111 | 48.5091 | 51.0752 | 73.1018 |  |  | 1.1613 | -0.057737 | -0.47127 | -1.0783 | 8.3514 | 6.0483 | 8.3262 | -3.3534 | 18.956 | 51.747 | 32.5853 | -6.078e-05 | -8.21e-06 | -0.00078854 | 30.079 | 16.5322 | 16.7002 | 17.0847 | 17.0997 | 16.1106 | 14.6637 | 16.6679 | 17.0414 | 17.3841 | 17.4678 | 17.2095 | 16.4035 | 14.7024 | 673.0921 | 461.9451 | 430.4264 | 265.686 | 214.0335 | 731.8377 | 441.2228 | 24.0751 | 41.7073 | 47.5683 | 82.8792 | 85.9276 | 89.6022 |  |  |  | 639.1127 | 595.275 | 597.7317 | 623.5426 | 60.5067 | 22.5031 | 868.1445 |  |  | 690.2876 |  |  | 22.1684 | 58.3925 | 602.1531 | 23.0976 | 61.155 | 869.3326 | 738.8723 | 623.3737 | 856.1467 | 841.4172 | 743.3528 |  | 824.3116 | 922.5731 | 1044.3587 | 609.2386 | 699.0304 | 937.2423 |  | 340.0278 |  |  | 465.0525 | 663.2738 | 734.7577 | [6 empty] | 615.4011 |  |  | 452.1545 |  |  | 535.3155 | 688.5271 | 697.7088 | 1075.2753 | 1118.2134 | 1065.0473 | 551.0382 | 732.8517 | 860.831 | 638.0868 | 715.1758 | 1075.9175 | 1096.9741 | 646.5141 | 829.7224 | 1029.5112 | 1091.5286 | 1101.0196 | 560.0138 | 673.9949 | 716.8736 | 576.4368 | 773.6368 | 902.5033 | 1061.2899 | 1135.733 | 620.3877 | 716.5576 | 685.7266 | 878.5301 | 105.2717 | -0.00063035 | 17.7166 | 5.1552 | -40.1699 | 3.1213 | 9644.01 | 0.34 | 2.3486 | -0.52915 | -1.5118 | -2.2868 | 7.2726 | 6.1891 | 7.2616 | 84.4997 | 174.2258 | 53.1432 | 64.367 | 15.9663 | 107.4546 | 39.7027
42810.4535 | 1163 | 17.4347 | 17.8603 | 18.0151 | 18.0634 | 17.4171 | 16.0887 | 15.1383 | 16.4439 | 16.9235 | 17.0733 | 17.096 | 16.6363 | 15.6665 | 14.4463 | 34.7215 | 52.7679 | 51.4738 | 89.8354 | 70.137 | 92.6351 |  |  |  | 44.6013 | 87.8326 | 532.5504 | 698.9906 | 721.3005 | 705.4297 | 26.938 | 64.1622 | 883.1436 | 34.5805 | 68.696 | 778.3426 | 854.898 | 781.2792 |  | 245.9029 | 891.8221 | 882.0735 | 627.0474 |  | 480.85 | 724.9757 | 562.0744 | 717.7147 | 923.8288 | 1032.0586 | 1045.3891 | 67.0804 | 408.3408 | 102.8487 | 626.8217 | 14.5674 | 49.3057 | 48.5024 | 51.0827 | 73.2168 |  |  | 1.3887 | -1.3457 | -0.4463 | -0.36339 | 7.6306 | 6.6154 | 8.6331 | -3.477 | 19.7303 | 53.6253 | 35.2747 | -4.928e-05 | -4.271e-05 | -0.00078854 | 30.1625 | 16.5427 | 16.6919 | 17.0874 | 17.0995 | 16.1069 | 14.6522 | 16.6722 | 17.0427 | 17.3841 | 17.4643 | 17.2094 | 16.4014 | 14.698 | 656.5916 | 450.7148 | 405.2325 | 256.8792 | 210.0541 | 730.0196 | 440.4257 | 24.1648 | 41.8174 | 47.6715 | 82.9362 | 85.9541 | 89.6434 |  |  |  | 639.2646 | 595.8089 | 598.0862 | 625.0217 | 82.2151 | 27.0959 | 868.1522 |  |  | 694.3388 |  |  | 22.2125 | 58.4692 | 603.6643 | 23.143 | 61.2233 | 870.6755 | 742.2945 | 622.7757 | 861.2779 | 848.7828 | 750.3287 |  | 824.9989 | 922.5117 | 1045.6138 | 607.9036 | 698.6692 | 939.0106 |  | 342.9927 |  |  | 466.3642 | 669.7837 | 739.1169 | [6 empty] | 614.4832 |  |  | 450.08 |  |  | 534.9325 | 687.4059 | 696.5784 | 1081.1066 | 1116.5794 | 1061.2411 | 552.6523 | 733.9294 | 858.7811 | 637.7877 | 714.2736 | 1079.3188 | 1096.9121 | 647.1934 | 830.0307 | 1032.6708 | 1091.2028 | 1099.8353 | 560.7427 | 674.389 | 717.1593 | 576.7409 | 771.8028 | 900.507 | 1059.9252 | 1133.6371 | 620.7052 | 717.2332 | 684.7209 | 874.8634 | 88.8107 | -0.00017432 | 17.7134 | 5.1412 | -40.2047 | 3.1212 | 9588.95 | 0.49 | 2.569 | -2.5541 | -1.4709 | -1.3272 | 6.9548 | 6.4757 | 7.3976 | 84.5312 | 174.9144 | 53.095 | 65.5809 | 18.6112 | 98.1399 | 39.692
42810.4535 | 1164 | 17.4346 | 17.8603 | 18.0115 | 18.0655 | 17.4173 | 16.0909 | 15.1432 | 16.4508 | 16.9283 | 17.0741 | 17.0984 | 16.638 | 15.6754 | 14.4551 | 34.8835 | 52.9071 | 51.6196 | 89.8554 | 70.2887 | 92.6556 |  |  |  | 44.8145 | 87.8436 | 532.717 | 698.3781 | 719.9033 | 704.7833 | 20.7574 | 57.4653 | 887.2774 | 38.5555 | 79.7103 | 777.4086 | 862.8023 | 777.247 |  | 252.3869 | 875.0418 | 871.2355 | 689.5196 |  | 479.9308 | 723.3879 | 561.8227 | 714.3323 | 921.7642 | 1033.1162 | 1044.9623 | 68.8497 | 408.7751 | 104.8887 | 627.5351 | 14.5815 | 49.325 | 48.4973 | 51.0866 | 73.2307 |  |  | 1.1666 | -0.46384 | 0.050476 | -0.10185 | 8.1517 | 6.0115 | 8.4852 | -2.718 | 20.5694 | 54.6164 | 46.7455 | -4.107e-05 | 1.643e-05 | -0.0007754 | 30.2518 | 16.5456 | 16.6916 | 17.0796 | 17.0901 | 16.1039 | 14.6539 | 16.6612 | 17.0418 | 17.3834 | 17.4624 | 17.2071 | 16.3964 | 14.6901 | 678.4677 | 470.2837 | 423.6773 | 261.6104 | 220.0996 | 729.9454 | 440.4046 | 24.2626 | 41.923 | 47.7886 | 82.9895 | 85.9911 | 89.7005 |  |  |  | 639.5249 | 597.3209 | 599.2026 | 625.6418 | 71.9468 | 30.1404 | 873.6071 |  |  | 703.2671 |  |  | 22.2469 | 58.5424 | 603.7636 | 23.1944 | 61.2932 | 869.9813 | 742.9421 | 623.3399 | 867.5072 | 856.0342 | 754.23 |  | 825.3794 | 924.4219 | 1049.3904 | 607.408 | 698.3905 | 925.1391 |  | 345.9257 |  |  | 466.6764 | 672.2148 | 742.1604 | [6 empty] | 614.6264 |  |  | 448.3444 |  |  | 534.8211 | 686.8102 | 696.4314 | 1084.9018 | 1117.1453 | 1059.7645 | 553.4157 | 734.6761 | 857.5219 | 637.5901 | 715.2797 | 1081.609 | 1098.0165 | 647.435 | 830.5108 | 1035.5363 | 1088.676 | 1097.8155 | 560.7953 | 675.4928 | 717.3118 | 577.0336 | 769.6537 | 897.214 | 1056.7384 | 1131.5462 | 621.1611 | 717.6529 | 683.967 | 870.6557 | 83.5375 | -0.0012337 | 17.711 | 5.1289 | -40.2042 | 3.1212 | 9565.38 | 0.27 | 2.3539 | -1.4983 | 0.49426 | -0.70211 | 7.1913 | 6.1755 | 7.3369 | 84.5478 | 176.9392 | 53.043 | 63.125 | 16.5577 | 99.2246 | 39.7268
42810.4535 | 1165 | 17.435 | 17.8517 | 18.0112 | 18.0563 | 17.4157 | 16.0838 | 15.1445 | 16.4525 | 16.9238 | 17.0705 | 17.0926 | 16.6328 | 15.676 | 14.4526 | 35.0409 | 53.0557 | 51.7699 | 89.8874 | 70.4014 | 92.6624 |  |  |  | 45.0197 | 87.8549 | 530.7026 | 696.3752 | 717.2765 | 702.9065 | 21.3241 | 57.2871 | 880.2747 | 34.6883 | 74.2948 | 772.4314 | 858.5494 | 776.109 |  | 250.7018 | 869.3996 | 863.6379 | 717.5103 |  | 480.8425 | 724.3726 | 563.3942 | 714.872 | 917.7726 | 1032.0217 | 1044.3951 | 70.7621 | 408.9792 | 107.2448 | 628.2862 | 14.5251 | 49.3599 | 48.5058 | 51.0884 | 73.1816 |  |  | 0.84856 | -0.26473 | -0.32145 | -0.59995 | 8.1017 | 6.1764 | 8.043 | -2.4933 | 19.3933 | 50.4133 | 50.759 | -4.6e-05 | 4.764e-05 | -0.00077047 | 30.3375 | 16.5493 | 16.6996 | 17.0879 | 17.1059 | 16.1021 | 14.6594 | 16.6695 | 17.0408 | 17.3882 | 17.4658 | 17.2075 | 16.4053 | 14.6991 | 672.3014 | 460.8427 | 407.2478 | 259.2048 | 232.8456 | 729.5522 | 440.4532 | 24.3729 | 42.0594 | 47.905 | 83.0568 | 86.0325 | 89.7528 |  |  |  | 639.6663 | 597.4319 | 599.8882 | 624.7561 | 66.5965 | 23.7061 | 880.2977 |  |  | 711.5115 |  |  | 22.2851 | 58.6186 | 601.4572 | 23.2439 | 61.3787 | 866.0007 | 739.5158 | 623.7742 | 870.2092 | 857.0364 | 750.9361 |  | 824.8295 | 929.9045 | 1055.3337 | 607.0256 | 698.2549 | 925.751 |  | 348.704 |  |  | 466.9536 | 664.558 | 739.7438 | [6 empty] | 615.0468 |  |  | 448.1509 |  |  | 535.4657 | 687.7033 | 696.888 | 1087.8822 | 1121.134 | 1056.8339 | 553.2832 | 733.8546 | 856.264 | 637.4881 | 717.6372 | 1074.8387 | 1096.7691 | 647.0319 | 827.9461 | 1034.1975 | 1083.3352 | 1097.6132 | 559.5812 | 676.5575 | 717.3684 | 577.0781 | 767.9032 | 893.4833 | 1052.9151 | 1127.3011 | 621.7799 | 717.8319 | 683.5437 | 866.2166 | 89.214 | -0.0012267 | 17.7095 | 5.1198 | -40.1969 | 3.1212 | 9554.42 | 0.4 | 2.0056 | -1.1325 | -1.2479 | -1.7048 | 7.1662 | 6.257 | 7.1402 | 84.4588 | 180.0912 | 53.0217 | 63.6766 | 18.3926 | 96.923 | 39.7798
42810.4535 | 1166 | 17.4324 | 17.8578 | 18.0151 | 18.0576 | 17.4139 | 16.0907 | 15.154 | 16.4553 | 16.9239 | 17.0757 | 17.0941 | 16.6299 | 15.6728 | 14.4558 | 35.1936 | 53.2095 | 51.9231 | 89.9067 | 70.5203 | 92.658 |  |  |  | 45.2354 | 87.8675 | 530.8232 | 695.3076 | 716.221 | 701.7062 | 20.8623 | 57.6824 | 870.2069 | 20.9144 | 55.1637 | 756.4599 | 844.8868 | 773.673 |  | 262.8321 | 869.3291 | 864.4072 | 679.4153 |  | 481.5429 | 725.7444 | 564.3727 | 718.6135 | 922.2231 | 1031.8568 | 1043.7071 | 70.4628 | 409.129 | 108.9073 | 628.9256 | 14.5769 | 49.3807 | 48.5221 | 51.0812 | 73.0916 |  |  | 0.79336 | -0.54203 | -0.21763 | -0.74517 | 7.5103 | 5.9083 | 9.7226 | -3.4099 | 20.5875 | 53.6262 | 39.9239 | -4.271e-05 | -7.721e-05 | -0.00079182 | 30.4185 | 16.5517 | 16.6882 | 17.0841 | 17.0907 | 16.1002 | 14.6667 | 16.664 | 17.0446 | 17.3772 | 17.4625 | 17.204 | 16.4078 | 14.6923 | 659.168 | 456.1417 | 381.758 | 246.9417 | 230.6486 | 728.5151 | 440.0594 | 24.4639 | 42.1626 | 48.0098 | 83.1287 | 86.08 | 89.7932 |  |  |  | 639.723 | 596.5947 | 599.4349 | 623.8503 | 73.1056 | 25.844 | 882.6198 |  |  | 713.7838 |  |  | 22.3264 | 58.6816 | 600.4328 | 23.2986 | 61.447 | 865.9709 | 736.8786 | 623.3067 | 874.1216 | 862.2083 | 745.7074 |  | 824.1673 | 929.3882 | 1060.291 | 606.0296 | 697.9808 | 924.7321 |  | 351.7017 |  |  | 466.8178 | 656.3046 | 735.0803 | [6 empty] | 614.4903 |  |  | 448.0844 |  |  | 535.7801 | 689.7665 | 698.0363 | 1078.9149 | 1125.4202 | 1056.7565 | 553.6455 | 732.1305 | 854.9508 | 637.8454 | 719.5842 | 1066.8209 | 1095.7593 | 646.9667 | 823.9467 | 1038.8939 | 1078.6061 | 1096.4036 | 558.4015 | 676.8514 | 716.8022 | 576.8787 | 766.6253 | 890.2121 | 1054.4084 | 1125.6062 | 622.0912 | 717.2845 | 683.5357 | 863.8221 | 103.3274 | -0.00033568 | 17.7084 | 5.1052 | -40.2005 | 3.1212 | 9556.48 | 0.34 | 1.9381 | -1.6216 | -1.0275 | -1.9013 | 6.8993 | 6.1194 | 7.8499 | 84.387 | 182.8941 | 52.9848 | 64.7838 | 21.1487 | 93.1911 | 39.8163
42810.4535 | 1167 | 17.4242 | 17.8535 | 18.0144 | 18.0487 | 17.4104 | 16.0777 | 15.1504 | 16.4491 | 16.9207 | 17.0729 | 17.096 | 16.6315 | 15.6649 | 14.4533 | 35.301 | 53.3458 | 52.0679 | 89.9111 | 70.7801 | 92.6766 |  |  |  | 45.4479 | 87.8827 | 531.7497 | 695.0997 | 716.1363 | 701.6897 | 22.6842 | 58.4402 | 871.6911 | 24.9778 | 58.7537 | 755.9131 | 844.3212 | 773.3373 |  | 262.3867 | 868.3324 | 862.9314 | 686.3835 |  | 481.7822 | 726.0899 | 566.805 | 723.9142 | 925.7682 | 1033.5793 | 1043.0387 | 69.3026 | 409.317 | 103.8808 | 629.2654 | 14.6475 | 49.3734 | 48.5418 | 51.0947 | 73.0157 |  |  | 1.1173 | -0.76611 | -0.39176 | -0.73137 | 7.8238 | 5.4937 | 8.846 | -2.7962 | 20.1913 | 55.096 | 34.5763 | 8.214e-05 | 0 | -0.00076882 | 30.5103 | 16.5643 | 16.6931 | 17.0876 | 17.0941 | 16.1041 | 14.6596 | 16.6635 | 17.0437 | 17.3799 | 17.4681 | 17.2094 | 16.405 | 14.7083 | 662.4223 | 451.1035 | 372.5551 | 242.3232 | 219.1166 | 727.9218 | 439.7456 | 24.5506 | 42.272 | 48.1157 | 83.1783 | 86.1224 | 89.8469 |  |  |  | 639.6136 | 595.7225 | 598.2745 | 622.1672 | 68.3654 | 23.918 | 886.8899 |  |  | 724.9809 |  |  | 22.346 | 58.7691 | 600.968 | 23.3569 | 61.5372 | 866.4458 | 739.0296 | 622.2501 | 875.4854 | 862.9484 | 746.2106 |  | 824.5635 | 931.6631 | 1064.1408 | 604.9309 | 697.6641 | 933.5081 |  | 354.7276 |  |  | 466.7688 | 656.2721 | 734.9249 | [6 empty] | 613.3912 |  |  | 448.0837 |  |  | 535.1325 | 690.5863 | 698.3928 | 1074.9528 | 1125.2167 | 1059.8685 | 554.6482 | 730.87 | 852.8748 | 638.2736 | 719.2684 | 1065.2475 | 1096.0169 | 647.2381 | 822.5261 | 1039.6937 | 1080.9524 | 1095.2159 | 558.6336 | 676.2812 | 715.6815 | 578.4483 | 766.4992 | 891.2727 | 1055.9408 | 1128.1144 | 622.2747 | 716.4653 | 684.0263 | 868.19 | 95.5003 | -0.00042689 | 17.7066 | 5.1033 | -40.202 | 3.1212 | 9585.77 | 0.37 | 2.3 | -1.9282 | -1.3788 | -1.884 | 7.0464 | 5.9046 | 7.4926 | 84.5029 | 185.017 | 52.9407 | 64.2212 | 22.1105 | 92.8026 | 39.8411
42810.4536 | 1168 | 17.4275 | 17.8541 | 18.0133 | 18.0486 | 17.4188 | 16.0817 | 15.1504 | 16.4518 | 16.9268 | 17.0784 | 17.0948 | 16.6284 | 15.6757 | 14.4607 | 35.5018 | 53.5392 | 52.2674 | 89.9527 | 71.1071 | 92.7382 |  |  |  | 45.6431 | 87.888 | 534.4963 | 696.4401 | 717.6067 | 703.0815 | 22.3428 | 73.7419 | 874.3555 | 23.3055 | 57.5836 | 764.9743 | 846.1868 | 775.8077 |  | 251.8216 | 870.7753 | 860.3994 | 703.0613 |  | 482.744 | 725.0593 | 565.6483 | 723.6989 | 929.0041 | 1034.1063 | 1044.4016 | 67.1124 | 409.2927 | 100.9472 | 629.3591 | 14.6723 | 49.3571 | 48.5467 | 51.1086 | 72.9582 |  |  | 1.7113 | -0.10045 | -0.73806 | -1.3162 | 6.9097 | 5.7677 | 9.0819 | -4.004 | 20.274 | 53.5225 | 36.5825 | -0.00011007 | 1.807e-05 | -0.00076225 | 30.5973 | 16.564 | 16.6967 | 17.087 | 17.0973 | 16.1066 | 14.664 | 16.6706 | 17.0474 | 17.3851 | 17.4687 | 17.2129 | 16.4029 | 14.7177 | 658.8848 | 448.379 | 374.572 | 234.5966 | 211.3389 | 727.0737 | 439.2089 | 24.6413 | 42.3795 | 48.219 | 83.2174 | 86.1561 | 89.8989 |  |  |  | 639.4011 | 594.738 | 597.1367 | 620.3132 | 75.8229 | 28.6702 | 887.1051 |  |  | 732.0816 |  |  | 22.3849 | 58.8073 | 603.2057 | 23.425 | 61.606 | 864.5683 | 741.4781 | 620.5802 | 877.5248 | 864.5715 | 749.53 |  | 825.5323 | 931.1839 | 1064.8823 | 603.8081 | 697.2052 | 935.2153 |  | 359.2749 |  |  | 467.1207 | 658.6707 | 738.9029 | [6 empty] | 611.8723 |  |  | 449.213 |  |  | 534.5329 | 690.5242 | 698.3708 | 1077.746 | 1126.026 | 1061.2649 | 554.9736 | 730.8189 | 852.7732 | 638.4848 | 718.7536 | 1070.3872 | 1094.3368 | 647.1706 | 824.6181 | 1039.2715 | 1089.1541 | 1097.8003 | 559.3964 | 675.6154 | 715.5016 | 579.1619 | 767.6033 | 893.379 | 1062.5004 | 1129.9692 | 622.2013 | 717.1164 | 684.4208 | 868.8058 | 90.7556 | -0.00075661 | 17.7059 | 5.0839 | -40.152 | 3.1212 | 9567.61 | 0.23 | 2.8485 | -0.69783 | -1.8916 | -2.526 | 6.6234 | 6.0513 | 7.5934 | 84.7286 | 185.4534 | 52.864 | 64.3273 | 21.7827 | 92.9831 | 39.8501
42810.4536 | 1169 | 17.4252 | 17.8518 | 18.005 | 18.0536 | 17.4052 | 16.0926 | 15.1683 | 16.4521 | 16.9246 | 17.0769 | 17.0941 | 16.6329 | 15.6703 | 14.4425 | 35.6529 | 53.6595 | 52.3641 | 89.9604 | 71.2984 | 92.7171 |  |  |  | 45.8079 | 87.8853 | 536.1526 | 697.4915 | 718.6781 | 704.0596 | 23.5029 | 105.7309 | 917.831 | 27.0105 | 64.4771 | 755.3375 | 850.7067 | 781.1946 |  | 241.1225 | 869.7017 | 862.9353 | 620.4847 |  | 483.4142 | 722.7186 | 564.7457 | 723.2291 | 927.9396 | 1033.158 | 1045.8345 | 63.5924 | 409.3241 | 100.1011 | 629.7683 | 14.6945 | 49.3364 | 48.542 | 51.1275 | 72.9144 |  |  | 1.1226 | 0.020459 | -1.0062 | -0.92128 | 8.5538 | 6.3782 | 8.7961 | -2.5813 | 20.3168 | 53.2701 | 37.1586 | -3.45e-05 | -4.107e-05 | -0.00073925 | 30.6739 | 16.5695 | 16.698 | 17.0843 | 17.1034 | 16.1055 | 14.6683 | 16.6761 | 17.0495 | 17.3856 | 17.4718 | 17.2145 | 16.4054 | 14.7151 | 665.0805 | 476.4916 | 410.9102 | 243.628 | 223.1201 | 726.4415 | 439.0545 | 24.7451 | 42.5067 | 48.333 | 83.287 | 86.2335 | 89.9642 |  |  |  | 639.279 | 593.9656 | 596.1178 | 621.8195 | 55.7661 | 26.6426 | 888.4607 |  |  | 732.5334 |  |  | 22.4285 | 58.8795 | 605.2236 | 23.4638 | 61.6725 | 862.4631 | 741.6833 | 619.3607 | 882.6656 | 873.277 | 750.7551 |  | 825.6683 | 928.5958 | 1067.1575 | 602.2473 | 696.4738 | 922.6443 |  | 361.2204 |  |  | 466.6684 | 659.0592 | 739.7943 | [6 empty] | 610.2216 |  |  | 449.7081 |  |  | 534.465 | 690.4423 | 698.2815 | 1073.9588 | 1126.1658 | 1059.343 | 555.0721 | 731.7532 | 852.2603 | 638.8098 | 718.7952 | 1067.8875 | 1092.4278 | 647.4061 | 824.3944 | 1038.2657 | 1087.6091 | 1097.7192 | 560.7237 | 675.1528 | 716.3441 | 578.4288 | 766.7545 | 893.2189 | 1059.4088 | 1127.7514 | 622.1554 | 717.5281 | 684.1224 | 867.6915 | 92.6173 | -0.00015329 | 17.7047 | 5.0637 | -40.2102 | 3.1212 | 9512.21 | 0.2 | 2.3082 | 0.31456 | -2.206 | -2.1109 | 7.3667 | 6.3612 | 7.4702 | 84.7392 | 186.8278 | 52.7357 | 63.4253 | 17.7154 | 96.8489 | 39.7838
42810.4536 | 1170 | 17.421 | 17.8628 | 18.0031 | 18.0522 | 17.4073 | 16.0832 | 15.1566 | 16.4559 | 16.9223 | 17.0766 | 17.0979 | 16.6358 | 15.6621 | 14.4431 | 35.8153 | 53.8176 | 52.5123 | 89.9817 | 71.5849 | 92.7344 |  |  |  | 46.0481 | 87.9191 | 536.9769 | 697.3476 | 718.1902 | 704.012 | 31.7236 | 89.9837 | 885.6431 | 41.7551 | 85.3079 | 753.8389 | 848.3861 | 786.7066 |  | 244.9923 | 880.5036 | 861.9766 | 676.6496 |  | 481.8175 | 721.2493 | 564.6752 | 722.9557 | 925.7574 | 1033.8557 | 1046.0716 | 62.176 | 409.432 | 100.2188 | 630.1744 | 14.7052 | 49.293 | 48.5311 | 51.1297 | 72.9165 |  |  | 0.88207 | -0.080737 | -0.66775 | -1.033 | 8.0492 | 6.3933 | 9.5471 | -2.7331 | 19.7566 | 55.0837 | 41.3317 | 6.57e-06 | -4.764e-05 | -0.00077375 | 30.758 | 16.5709 | 16.6927 | 17.0758 | 17.0947 | 16.1023 | 14.6657 | 16.6678 | 17.0396 | 17.3838 | 17.462 | 17.2166 | 16.4059 | 14.6953 | 652.487 | 465.7723 | 402.2104 | 244.8982 | 229.621 | 724.8506 | 438.6424 | 24.8501 | 42.629 | 48.4432 | 83.3356 | 86.2478 | 90.0253 |  |  |  | 639.5063 | 595.1274 | 596.397 | 625.1162 | 82.2698 | 25.937 | 895.2085 |  |  | 738.3512 |  |  | 22.4696 | 58.9554 | 605.7899 | 23.4951 | 61.7588 | 859.0123 | 742.8489 | 620.6371 | 896.6796 | 891.1176 | 750.9274 |  | 825.7446 | 935.7866 | 1072.6531 | 602.1818 | 696.0949 | 921.0783 |  | 366.4511 |  |  | 465.4061 | 660.0527 | 739.8188 | [6 empty] | 610.8834 |  |  | 450.2122 |  |  | 534.6232 | 690.3388 | 698.8702 | 1078.876 | 1126.3031 | 1056.8585 | 555.4728 | 733.1093 | 851.9055 | 638.5457 | 719.1354 | 1062.5198 | 1093.739 | 647.6152 | 824.3101 | 1036.2836 | 1085.6749 | 1095.5443 | 561.9 | 675.441 | 716.6127 | 578.6796 | 765.5829 | 891.2682 | 1059.4573 | 1125.6923 | 622.629 | 717.9746 | 683.9553 | 866.2198 | 89.7901 | -5.5071e-05 | 17.7056 | 5.0564 | -40.2531 | 3.1212 | 9462.2 | 0.1 | 2.046 | -0.62443 | -1.7958 | -2.2335 | 7.1479 | 6.3704 | 7.7847 | 84.7596 | 189.8002 | 52.6487 | 64.2883 | 18.6025 | 94.4795 | 39.7377
42810.4536 | 1171 | 17.4297 | 17.8611 | 18.0117 | 18.0581 | 17.4159 | 16.0815 | 15.174 | 16.4556 | 16.9277 | 17.0836 | 17.0992 | 16.6374 | 15.6734 | 14.4567 | 35.9546 | 53.9472 | 52.6491 | 89.9988 | 71.8859 | 92.7554 |  |  |  | 46.2575 | 87.9159 | 536.4463 | 695.819 | 716.3171 | 702.3512 | 22.9969 | 57.6183 | 860.2362 | 21.2594 | 55.5818 | 752.4769 | 842.4532 | 769.8585 |  | 251.8229 | 858.5962 | 853.8118 | 760.8153 |  | 479.4025 | 721.9597 | 564.3684 | 723.7063 | 932.4065 | 1038.2433 | 1048.487 | 61.578 | 409.2963 | 98.091 | 630.2826 | 14.7202 | 49.2531 | 48.5303 | 51.1358 | 72.9494 |  |  | 1.1692 | -0.42638 | 0.22921 | -0.87922 | 8.7792 | 6.3217 | 9.628 | -2.8645 | 21.1342 | 54.1314 | 44.8059 | -4.93e-06 | -1.15e-05 | -0.00076061 | 30.8461 | 16.5695 | 16.6856 | 17.0774 | 17.0899 | 16.1014 | 14.6714 | 16.6595 | 17.0407 | 17.3801 | 17.4635 | 17.2056 | 16.4015 | 14.6959 | 675.7212 | 466.6625 | 390.2183 | 231.4208 | 216.4036 | 725.0749 | 438.309 | 24.9459 | 42.7373 | 48.5399 | 83.3945 | 86.2866 | 90.0834 |  |  |  | 639.6695 | 595.4228 | 596.6109 | 625.5057 | 98.3644 | 29.6487 | 909.9047 |  |  | 754.0055 |  |  | 22.5088 | 59.0006 | 604.9224 | 23.5672 | 61.8289 | 857.4638 | 744.8316 | 622.3373 | 901.8042 | 891.4923 | 752.4195 |  | 826.3696 | 953.2835 | 1079.1124 | 603.1256 | 696.1999 | 934.2723 |  | 369.6247 |  |  | 465.0883 | 662.0891 | 741.6295 | [6 empty] | 612.6495 |  |  | 450.1153 |  |  | 534.6635 | 690.0578 | 699.2366 | 1078.4302 | 1129.5733 | 1055.6237 | 555.5716 | 733.1252 | 850.9223 | 638.0726 | 718.7792 | 1059.8745 | 1098.2656 | 647.6212 | 822.5556 | 1028.692 | 1087.2931 | 1093.1164 | 562.2692 | 676.2345 | 716.4008 | 579.6203 | 764.9675 | 890.5639 | 1057.1834 | 1124.9499 | 623.2045 | 717.8702 | 683.8599 | 864.518 | 91.166 | -0.00010418 | 17.7047 | 5.0411 | -40.2468 | 3.1212 | 9399.55 | 0.3 | 2.3536 | -1.4355 | 1.0525 | -2.0613 | 7.4776 | 6.3453 | 7.8307 | 84.9237 | 193.0903 | 52.6471 | 61.7822 | 19.8706 | 90.0935 | 39.7596
42810.4536 | 1172 | 17.4252 | 17.8521 | 18.0107 | 18.0549 | 17.417 | 16.0774 | 15.1785 | 16.4538 | 16.9193 | 17.0814 | 17.0969 | 16.63 | 15.6676 | 14.4526 | 36.1094 | 54.0828 | 52.804 | 90.0167 | 72.1856 | 92.7933 |  |  |  | 46.4716 | 87.9338 | 536.5877 | 694.8994 | 715.4519 | 701.2724 | 21.1121 | 57.8744 | 860.039 | 21.1875 | 55.636 | 753.2432 | 842.0252 | 770.8258 |  | 249.2966 | 858.8542 | 853.9365 | 744.0883 |  | 478.6166 | 724.6125 | 564.201 | 732.1824 | 938.0243 | 1039.0726 | 1047.3982 | 60.484 | 409.1574 | 95.9922 | 630.3453 | 14.7101 | 49.2341 | 48.546 | 51.1443 | 72.9847 |  |  | 0.60542 | -0.12082 | 0.10896 | -0.39098 | 8.2785 | 6.3683 | 9.283 | -3.1195 | 21.0489 | 56.9517 | 39.7616 | -7.557e-05 | -6.078e-05 | -0.00078032 | 30.9421 | 16.5811 | 16.6907 | 17.0821 | 17.0934 | 16.0971 | 14.6668 | 16.668 | 17.0344 | 17.3828 | 17.4629 | 17.217 | 16.3991 | 14.706 | 710.3154 | 484.5984 | 422.6345 | 237.4163 | 207.5023 | 727.6621 | 438.7877 | 25.0483 | 42.8465 | 48.6458 | 83.4515 | 86.334 | 90.1483 |  |  |  | 639.8126 | 595.4636 | 596.3473 | 625.9156 | 92.2112 | 41.7142 | 912.9546 |  |  | 752.6176 |  |  | 22.5309 | 59.1051 | 604.6144 | 23.6186 | 61.9047 | 857.237 | 745.1555 | 623.0007 | 895.4585 | 881.7063 | 752.0136 |  | 826.6336 | 946.0632 | 1080.4079 | 603.1028 | 696.2464 | 933.0783 |  | 372.9703 |  |  | 465.0792 | 662.4284 | 742.8461 | [6 empty] | 613.2032 |  |  | 449.6054 |  |  | 534.6142 | 689.9561 | 699.3711 | 1077.8269 | 1129.3829 | 1054.7897 | 555.9821 | 732.7614 | 849.4931 | 637.9311 | 718.5022 | 1061.8445 | 1098.9091 | 647.9275 | 822.1418 | 1016.8761 | 1090.7602 | 1091.0859 | 561.4675 | 676.3088 | 715.7618 | 580.1561 | 764.1582 | 890.6649 | 1056.8598 | 1123.3754 | 623.2613 | 716.9181 | 684.0707 | 863.2609 | 94.1981 | 0.00023956 | 17.7035 | 5.0287 | -40.2599 | 3.1212 | 9368.99 | 0.18 | 1.6927 | -0.76516 | 0.72663 | -1.3764 | 7.2635 | 6.3706 | 7.6916 | 85.0219 | 194.0544 | 52.6586 | 58.8118 | 16.3612 | 90.4116 | 39.7768
42810.4536 | 1173 | 17.4196 | 17.8451 | 18.0049 | 18.0479 | 17.4127 | 16.0801 | 15.1645 | 16.4483 | 16.9212 | 17.0697 | 17.0907 | 16.6255 | 15.66 | 14.4446 | 36.264 | 54.2348 | 52.943 | 90.0421 | 72.4769 | 92.83 |  |  |  | 46.6741 | 87.9581 | 537.611 | 694.7478 | 715.7319 | 700.836 | 23.0776 | 58.0816 | 861.0074 | 21.1178 | 55.6809 | 755.0549 | 842.0031 | 773.411 |  | 251.3991 | 861.0396 | 856.2274 | 737.7213 |  | 478.4923 | 726.138 | 565.3279 | 736.626 | 941.7091 | 1040.596 | 1048.7805 | 60.8553 | 409.2595 | 94.2214 | 630.3051 | 14.7228 | 49.2514 | 48.5889 | 51.1612 | 73.0415 |  |  | 0.76839 | -0.21545 | -0.28137 | -1.0941 | 7.6516 | 5.6553 | 9.7916 | -3.2759 | 20.6253 | 54.7188 | 36.4542 | -1.478e-05 | -3.285e-05 | -0.00075075 | 31.0237 | 16.5807 | 16.6903 | 17.0805 | 17.0844 | 16.0899 | 14.6643 | 16.6664 | 17.0387 | 17.3798 | 17.4565 | 17.2082 | 16.394 | 14.7011 | 726.2015 | 501.3491 | 454.9895 | 255.5517 | 216.3425 | 729.6298 | 440.1953 | 25.1412 | 42.9483 | 48.7546 | 83.5135 | 86.356 | 90.1984 |  |  |  | 639.8666 | 595.2387 | 595.9214 | 624.636 | 74.4533 | 39.8911 | 906.2676 |  |  | 748.1337 |  |  | 22.5817 | 59.2097 | 605.2588 | 23.6596 | 61.9799 | 859.505 | 745.4042 | 624.6123 | 896.1732 | 885.4669 | 750.6722 |  | 826.9546 | 934.853 | 1077.1882 | 603.9025 | 696.2787 | 920.3695 |  | 372.0669 |  |  | 465.1538 | 660.9353 | 742.8107 | [6 empty] | 614.5205 |  |  | 450.0344 |  |  | 534.753 | 690.6228 | 699.093 | 1082.8535 | 1128.4518 | 1057.0254 | 556.7397 | 732.969 | 849.5288 | 638.1996 | 718.8321 | 1064.4612 | 1103.6939 | 648.1676 | 825.6882 | 1008.6417 | 1094.3301 | 1091.6844 | 560.7667 | 675.8542 | 714.7932 | 580.5277 | 764.3384 | 893.667 | 1060.771 | 1123.4699 | 623.3564 | 715.5367 | 685.0864 | 865.6609 | 91.213 | 0.0019232 | 17.7045 | 5.0144 | -40.1622 | 3.1211 | 9348.29 | 0.84 | 1.9065 | -1.0225 | -1.1686 | -2.3043 | 6.9871 | 6.0069 | 7.904 | 85.165 | 192.4719 | 52.6439 | 57.714 | 13.0381 | 90.5809 | 39.8232
42810.4536 | 1174 | 17.4212 | 17.8438 | 18.008 | 18.0508 | 17.4174 | 16.0762 | 15.1675 | 16.4555 | 16.9265 | 17.0731 | 17.0926 | 16.6283 | 15.6671 | 14.4516 | 36.4321 | 54.3866 | 53.0887 | 90.0551 | 72.7731 | 92.8588 |  |  |  | 46.8896 | 87.9831 | 538.8222 | 695.0566 | 716.2368 | 701.0728 | 21.6182 | 83.3469 | 883.2064 | 31.5256 | 57.5717 | 759.91 | 847.139 | 782.7814 |  | 251.2118 | 865.107 | 861.1956 | 648.306 |  | 478.5758 | 728.4393 | 565.3376 | 741.1044 | 940.0648 | 1039.8924 | 1049.7602 | 61.603 | 409.3366 | 93.0967 | 629.7908 | 14.7167 | 49.2525 | 48.6229 | 51.1703 | 73.0949 |  |  | 1.1548 | -0.66689 | -0.18871 | -1.2998 | 8.8975 | 7.0248 | 9.7653 | -2.3014 | 20.1868 | 53.5009 | 36.0459 | -6.571e-05 | -6.571e-05 | -0.00079347 | 31.1004 | 16.5842 | 16.6839 | 17.0768 | 17.0825 | 16.0852 | 14.6539 | 16.6596 | 17.0324 | 17.3745 | 17.4584 | 17.2066 | 16.3941 | 14.6963 | 703.8276 | 504.3424 | 479.2501 | 272.9037 | 233.1358 | 730.6148 | 441.312 | 25.2522 | 43.0729 | 48.8741 | 83.5803 | 86.4007 | 90.267 |  |  |  | 639.6866 | 593.955 | 594.9351 | 621.586 | 89.7715 | 39.1663 | 907.5845 |  |  | 749.9511 |  |  | 22.6375 | 59.2916 | 606.5597 | 23.7116 | 62.0554 | 863.351 | 746.7731 | 627.1471 | 900.6244 | 891.5213 | 752.4697 |  | 827.5316 | 932.1452 | 1075.6404 | 606.3034 | 696.5095 | 912.5661 |  | 371.5844 |  |  | 465.3366 | 662.8075 | 743.913 | [6 empty] | 617.3754 |  |  | 451.6413 |  |  | 535.3007 | 691.0902 | 698.3133 | 1083.6049 | 1129.6025 | 1062.1577 | 556.8961 | 732.8921 | 851.0223 | 638.7129 | 718.7969 | 1066.2097 | 1108.9496 | 647.6858 | 827.4133 | 1002.7203 | 1098.5931 | 1093.9318 | 561.1117 | 675.2663 | 714.2067 | 580.9895 | 765.7964 | 896.8446 | 1058.0728 | 1125.054 | 623.519 | 714.5176 | 686.029 | 869.235 | 94.3709 | -0.003219 | 17.7033 | 5.0093 | -40.2581 | 3.1211 | 9382.7 | 0.15 | 2.3375 | -1.8011 | -0.9581 | -2.5145 | 7.5325 | 6.693 | 7.8913 | 85.3055 | 191.6413 | 52.6314 | 60.535 | 10.5587 | 94.8338 | 39.8719
42810.4536 | 1175 | 17.4253 | 17.8498 | 18.0083 | 18.059 | 17.4105 | 16.08 | 15.1822 | 16.4571 | 16.9278 | 17.0833 | 17.0998 | 16.6298 | 15.6722 | 14.4541 | 36.5916 | 54.5352 | 53.2431 | 90.0745 | 73.0413 | 92.8859 |  |  |  | 47.0847 | 88.0033 | 539.9794 | 695.633 | 716.9095 | 701.9363 | 24.4053 | 62.3486 | 873.8087 | 25.4318 | 57.7043 | 763.9874 | 844.614 | 781.0811 |  | 246.7454 | 871.6908 | 864.6691 | 677.0203 |  | 478.9908 | 728.3027 | 565.9399 | 743.6957 | 945.1551 | 1041.0168 | 1049.5298 | 62.2509 | 409.2842 | 94.1698 | 629.2125 | 14.6925 | 49.2757 | 48.6359 | 51.1889 | 73.1621 |  |  | 1.3112 | -0.6774 | -0.37534 | -0.57366 | 7.4367 | 6.3243 | 10.2726 | -3.1681 | 20.8131 | 55.9061 | 36.4856 | -6.571e-05 | -4.107e-05 | -0.00082304 | 31.1867 | 16.5969 | 16.6922 | 17.0776 | 17.0846 | 16.0912 | 14.6591 | 16.665 | 17.0365 | 17.3785 | 17.4587 | 17.2113 | 16.4035 | 14.7078 | 730.3519 | 521.2808 | 507.1276 | 278.3812 | 246.3959 | 733.0765 | 442.9745 | 25.3332 | 43.1776 | 48.9692 | 83.6245 | 86.431 | 90.3195 |  |  |  | 639.3781 | 593.4745 | 594.2994 | 618.5813 | 112.8282 | 40.1497 | 912.0138 |  |  | 755.1869 |  |  | 22.6773 | 59.3554 | 607.5502 | 23.7413 | 62.1253 | 868.2386 | 747.3264 | 629.936 | 910.0326 | 903.5856 | 754.5048 |  | 827.7302 | 930.258 | 1076.8992 | 608.7284 | 696.8981 | 913.556 |  | 379.0468 |  |  | 466.3255 | 667.3491 | 745.271 | [6 empty] | 620.5232 |  |  | 453.0856 |  |  | 535.7543 | 691.8205 | 698.0045 | 1083.5646 | 1132.304 | 1063.7993 | 556.7312 | 732.2711 | 851.5886 | 639.2193 | 720.1148 | 1071.5918 | 1110.3824 | 647.7609 | 826.9575 | 996.6826 | 1097.8743 | 1095.3818 | 561.2421 | 674.6515 | 714.4039 | 580.9314 | 767.2473 | 898.1719 | 1052.4849 | 1125.3604 | 623.2554 | 714.6281 | 686.2167 | 871.1204 | 105.8726 | 0.00026063 | 17.7025 | 5.0077 | -40.1854 | 3.1211 | 9445.07 | 0.51 | 2.4918 | -1.8151 | -1.3511 | -1.6704 | 6.8894 | 6.3533 | 8.0972 | 85.3145 | 192.4302 | 52.6552 | 58.4282 | 7.7839 | 93.1636 | 39.8936
42810.4536 | 1176 | 17.4251 | 17.8485 | 18.0067 | 18.0502 | 17.4078 | 16.0743 | 15.1736 | 16.4512 | 16.9189 | 17.0648 | 17.0905 | 16.6262 | 15.6691 | 14.445 | 36.739 | 54.6848 | 53.3813 | 90.1046 | 73.2932 | 92.9049 |  |  |  | 47.2778 | 88.018 | 542.4176 | 696.776 | 718.4102 | 703.3381 | 21.1438 | 58.2316 | 873.9086 | 22.9427 | 59.1256 | 763.5206 | 846.7249 | 780.4381 |  | 254.1907 | 872.9627 | 866.1494 | 667.3044 |  | 479.1694 | 727.9504 | 566.1158 | 743.1682 | 946.3093 | 1041.4113 | 1052.3703 | 63.3569 | 409.3574 | 97.3264 | 629.2265 | 14.6724 | 49.3069 | 48.6264 | 51.1948 | 73.2263 |  |  | 1.2054 | -0.89951 | -0.031004 | -1.1132 | 7.5517 | 6.3263 | 8.8867 | -2.9638 | 20.3632 | 55.6524 | 45.6818 | -2.628e-05 | -8.05e-05 | -0.00075732 | 31.2811 | 16.6038 | 16.6934 | 17.0863 | 17.092 | 16.0989 | 14.6675 | 16.6743 | 17.0418 | 17.3803 | 17.4622 | 17.2111 | 16.4021 | 14.7077 | 784.5533 | 540.3379 | 520.6989 | 283.3913 | 241.1693 | 737.449 | 444.7603 | 25.4173 | 43.2841 | 49.0752 | 83.6687 | 86.4676 | 90.3717 |  |  |  | 639.1111 | 593.312 | 594.0833 | 617.8157 | 94.1637 | 38.4922 | 920.4823 |  |  | 767.8305 |  |  | 22.7122 | 59.4276 | 609.5143 | 23.8127 | 62.2002 | 870.7037 | 747.3738 | 632.1291 | 923.3798 | 923.6637 | 753.1513 |  | 827.9234 | 933.1353 | 1078.3158 | 610.4333 | 697.2731 | 901.5958 |  | 384.8356 |  |  | 467.5329 | 669.0651 | 745.4414 | [6 empty] | 622.9053 |  |  | 452.912 |  |  | 536.1216 | 693.1044 | 698.4549 | 1088.6539 | 1133.1754 | 1067.3571 | 556.5979 | 733.052 | 852.9188 | 639.8124 | 721.0999 | 1080.3503 | 1111.8605 | 648.6966 | 829.8639 | 992.5933 | 1096.5721 | 1098.4714 | 561.3058 | 673.9128 | 714.6419 | 580.5129 | 768.4359 | 900.0979 | 1052.1343 | 1128.4029 | 622.5015 | 715.0271 | 685.8629 | 872.5938 | 97.7595 | -0.0040819 | 17.7028 | 5.0069 | -40.2853 | 3.1211 | 9517.27 | 0.22 | 2.3909 | -2.0913 | -0.38825 | -2.3264 | 6.9435 | 6.3552 | 7.5323 | 85.416 | 193.1815 | 52.696 | 53.9085 | 6.6237 | 94.1626 | 39.8614
42810.4537 | 1177 | 17.4215 | 17.8452 | 18.0032 | 18.0463 | 17.4039 | 16.0765 | 15.1794 | 16.4545 | 16.9192 | 17.0689 | 17.0933 | 16.6312 | 15.6697 | 14.4493 | 36.8825 | 54.8256 | 53.5287 | 90.1408 | 73.5441 | 92.9223 |  |  |  | 47.4578 | 88.0468 | 543.8604 | 697.2612 | 718.638 | 704.0009 | 21.416 | 58.0908 | 874.3098 | 22.4151 | 57.2438 | 758.6198 | 845.3052 | 778.6466 |  | 248.0768 | 873.8462 | 866.6632 | 687.607 |  | 479.5413 | 728.2881 | 566.2236 | 739.5774 | 945.532 | 1043.0373 | 1054.9857 | 62.265 | 409.3326 | 97.1073 | 629.378 | 14.6805 | 49.3707 | 48.6014 | 51.1941 | 73.2738 |  |  | 1.1705 | -1.5829 | -0.74135 | -0.50401 | 8.0321 | 5.6974 | 9.2948 | -3.4185 | 19.9175 | 53.5244 | 63.8488 | -2.136e-05 | 2.464e-05 | -0.00078361 | 31.3656 | 16.6011 | 16.6893 | 17.0765 | 17.0874 | 16.1004 | 14.6681 | 16.6731 | 17.0403 | 17.3833 | 17.4756 | 17.2117 | 16.4081 | 14.7086 | 797.9828 | 539.8187 | 510.0144 | 282.4602 | 237.8305 | 740.3516 | 445.9652 | 25.5314 | 43.4047 | 49.1984 | 83.7342 | 86.5089 | 90.428 |  |  |  | 639.044 | 593.6263 | 594.4307 | 619.4488 | 75.0253 | 28.2938 | 934.1069 |  |  | 812.3163 |  |  | 22.7595 | 59.5131 | 611.0147 | 23.8641 | 62.2826 | 872.5984 | 746.7111 | 633.6242 | 931.6101 | 927.7116 | 752.2449 |  | 828.7541 | 952.279 | 1079.3733 | 611.7899 | 697.872 | 893.107 |  | 387.8629 |  |  | 467.6703 | 667.7196 | 745.3389 | [6 empty] | 624.2221 |  |  | 452.3443 |  |  | 536.5887 | 693.7763 | 698.4764 | 1082.804 | 1131.6808 | 1071.5995 | 556.5728 | 735.6777 | 855.0651 | 639.9475 | 720.831 | 1079.1479 | 1114.4699 | 650.0491 | 833.8887 | 991.6568 | 1099.1323 | 1103.3333 | 561.0663 | 673.3246 | 714.5173 | 580.1602 | 768.981 | 899.488 | 1052.1295 | 1131.8172 | 621.6949 | 714.9293 | 685.1028 | 872.5639 | 93.7365 | 0.0092682 | 17.7027 | 5.0064 | -40.3481 | 3.1211 | 9608.31 | 0.42 | 2.3569 | -2.7746 | -1.8988 | -1.5657 | 7.1654 | 6.0348 | 7.7081 | 85.716 | 193.2718 | 52.7992 | 53.4213 | 8.0461 | 93.1079 | 39.8026
42810.4537 | 1178 | 17.4216 | 17.8437 | 18.0016 | 18.0498 | 17.4053 | 16.0763 | 15.1833 | 16.4514 | 16.918 | 17.0672 | 17.0895 | 16.6303 | 15.6616 | 14.4559 | 37.0342 | 54.961 | 53.6684 | 90.1282 | 73.7812 | 92.9755 |  |  |  | 47.6723 | 88.0772 | 543.2356 | 696.2901 | 716.9036 | 703.1093 | 21.2092 | 57.9996 | 874.8617 | 21.3451 | 56.3479 | 754.1823 | 842.2743 | 770.659 |  | 249.6353 | 874.5502 | 867.874 | 740.4644 |  | 479.2607 | 727.6397 | 565.9104 | 735.9051 | 942.7664 | 1044.5382 | 1054.4877 | 59.0614 | 409.2018 | 98.8437 | 629.3366 | 14.6875 | 49.4089 | 48.5675 | 51.2059 | 73.3226 |  |  | 0.94647 | -0.71748 | -0.54553 | -1.0304 | 8.2358 | 6.6022 | 10.5414 | -2.8192 | 20.0438 | 53.6786 | 53.879 | -8.707e-05 | 3.45e-05 | -0.00081154 | 31.4502 | 16.6115 | 16.693 | 17.0791 | 17.0996 | 16.0974 | 14.6722 | 16.6792 | 17.0492 | 17.3957 | 17.48 | 17.2185 | 16.4096 | 14.7077 | 766.9417 | 522.8417 | 480.8463 | 271.5284 | 237.8674 | 740.9786 | 446.3212 | 25.6219 | 43.5076 | 49.2976 | 83.7901 | 86.5461 | 90.4855 |  |  |  | 638.8146 | 592.6763 | 593.9588 | 617.9283 | 81.5603 | 31.5239 | 937.7351 |  |  | 809.0614 |  |  | 22.7837 | 59.5849 | 610.1052 | 23.9183 | 62.3691 | 873.2191 | 744.7647 | 634.1188 | 924.8681 | 917.5985 | 748.7836 |  | 829.1028 | 944.9086 | 1081.6604 | 612.7382 | 698.4987 | 890.84 |  | 366.4699 |  |  | 467.9948 | 663.9122 | 743.6207 | [6 empty] | 624.757 |  |  | 452.6403 |  |  | 536.8271 | 693.3615 | 698.7511 | 1075.173 | 1133.9751 | 1074.9248 | 556.4803 | 738.1168 | 857.093 | 639.4216 | 720.5036 | 1078.8486 | 1116.6404 | 650.7768 | 835.1052 | 988.1118 | 1099.2839 | 1105.0901 | 561.1575 | 673.0607 | 714.3686 | 579.9701 | 768.262 | 896.9423 | 1047.6276 | 1133.0121 | 621.6065 | 714.8393 | 684.3914 | 870.3222 | 92.1352 | 0.0089666 | 17.7026 | 5.0059 | -40.2136 | 3.1211 | 9655.27 | 0.34 | 2.1184 | -1.8674 | -1.6283 | -2.2379 | 7.2598 | 6.5001 | 8.2134 | 85.9277 | 194.8267 | 52.9205 | 57.0881 | 11.3566 | 90.5975 | 39.799
42810.4537 | 1179 | 17.42 | 17.8454 | 18.0016 | 18.0538 | 17.4095 | 16.0757 | 15.1814 | 16.4538 | 16.917 | 17.0705 | 17.097 | 16.6265 | 15.6612 | 14.4525 | 37.2045 | 55.1087 | 53.8176 | 90.1161 | 74.0177 | 93.041 |  |  |  | 47.8529 | 88.0899 | 541.0155 | 694.0119 | 713.4689 | 700.6882 | 21.6612 | 58.079 | 875.683 | 21.3946 | 56.2444 | 750.7 | 841.0628 | 766.8377 |  | 247.7586 | 876.8636 | 872.0593 | 678.2392 |  | 478.1779 | 727.7565 | 567.0027 | 738.0303 | 948.2663 | 1048.5911 | 1056.6651 | 55.2242 | 409.1541 | 101.4488 | 629.8525 | 14.6723 | 49.4413 | 48.5277 | 51.22 | 73.3438 |  |  | 0.40829 | -1.0822 | -0.19923 | -0.84439 | 7.9552 | 6.2789 | 10.1359 | -3.5072 | 21.1478 | 55.6338 | 49.9898 | -4.435e-05 | -9.857e-05 | -0.00079675 | 31.5408 | 16.6144 | 16.6902 | 17.0789 | 17.0925 | 16.0907 | 14.6684 | 16.668 | 17.0341 | 17.3849 | 17.464 | 17.2106 | 16.4089 | 14.7056 | 745.3959 | 519.8807 | 481.7073 | 282.3954 | 245.5841 | 741.5832 | 447.1409 | 25.7197 | 43.6255 | 49.4105 | 83.8437 | 86.5917 | 90.5341 |  |  |  | 638.611 | 592.2368 | 592.9457 | 618.1045 | 86.243 | 42.6418 | 932.4212 |  |  | 793.1989 |  |  | 22.8298 | 59.661 | 607.2835 | 23.9816 | 62.4372 | 873.5037 | 742.8822 | 632.5362 | 919.057 | 911.0348 | 744.9988 |  | 829.4063 | 939.4116 | 1081.6245 | 611.7991 | 698.7579 | 890.8583 |  | 343.926 |  |  | 467.8874 | 659.5048 | 741.3721 | [6 empty] | 622.9369 |  |  | 451.5807 |  |  | 537.0345 | 693.3766 | 699.3738 | 1071.7004 | 1135.9764 | 1076.3456 | 556.282 | 738.3724 | 857.191 | 639.0437 | 721.5053 | 1082.5769 | 1118.1304 | 650.369 | 832.6338 | 992.4771 | 1100.4885 | 1104.1811 | 561.5324 | 673.1115 | 714.6352 | 579.8943 | 767.0786 | 894.3536 | 1043.9048 | 1134.1594 | 622.0157 | 715.8296 | 684.27 | 867.4955 | 109.7458 | -0.0055411 | 17.7031 | 5.0062 | -40.2269 | 3.1211 | 9648.58 | 0.4 | 1.3896 | -2.2936 | -0.9841 | -2.026 | 7.146 | 6.3487 | 8.0662 | 86.1335 | 194.9582 | 53.0077 | 59.6924 | 11.4214 | 91.9117 | 39.7535
42810.4537 | 1180 | 17.4292 | 17.8475 | 18.0082 | 18.0567 | 17.4105 | 16.0772 | 15.185 | 16.4603 | 16.9242 | 17.0777 | 17.1007 | 16.635 | 15.6712 | 14.4639 | 37.336 | 55.2405 | 53.9376 | 90.078 | 74.2426 | 93.078 |  |  |  | 48.0514 | 88.0994 | 538.6072 | 691.709 | 710.9647 | 698.3035 | 22.0116 | 58.3986 | 877.8053 | 21.3812 | 56.2629 | 751.0573 | 840.1548 | 766.8614 |  | 257.0146 | 882.7781 | 875.2915 | 710.2379 |  | 476.9961 | 727.3556 | 568.953 | 738.6611 | 952.3876 | 1050.0235 | 1057.3602 | 53.7518 | 409.0886 | 99.5121 | 630.5144 | 14.6898 | 49.4959 | 48.5121 | 51.2418 | 73.3991 |  |  | 1.1075 | -0.74377 | 0.024848 | -0.82337 | 8.1136 | 5.7401 | 9.8967 | -2.5268 | 21.0682 | 54.7532 | 41.5125 | -8.378e-05 | -5.914e-05 | -0.00076882 | 31.6263 | 16.6147 | 16.6858 | 17.074 | 17.0825 | 16.0954 | 14.6658 | 16.6675 | 17.0343 | 17.3799 | 17.4639 | 17.2114 | 16.404 | 14.7033 | 727.7962 | 521.7666 | 506.0647 | 304.6233 | 261.5936 | 742.3333 | 448.6935 | 25.8112 | 43.7282 | 49.5119 | 83.8877 | 86.6223 | 90.5993 |  |  |  | 638.7267 | 593.9988 | 593.6834 | 621.5469 | 79.0665 | 32.1551 | 928.243 |  |  | 779.9293 |  |  | 22.8726 | 59.7258 | 604.0767 | 24.0121 | 62.5404 | 877.2892 | 744.2723 | 631.0689 | 909.7608 | 901.7998 | 746.0553 |  | 830.0621 | 930.1832 | 1079.2872 | 609.9065 | 699.0008 | 900.5007 |  | 344.5907 |  |  | 467.7202 | 658.6805 | 740.3591 | [6 empty] | 620.7512 |  |  | 448.3432 |  |  | 537.1044 | 693.7562 | 699.6803 | 1069.6323 | 1134.5942 | 1077.7673 | 557.3075 | 737.7466 | 856.2981 | 638.7631 | 721.4828 | 1085.7839 | 1118.9576 | 651.3435 | 830.9106 | 988.7182 | 1099.4935 | 1102.0844 | 561.0997 | 673.2868 | 714.4983 | 580.5824 | 766.2185 | 893.7096 | 1040.6232 | 1133.0923 | 622.5167 | 716.1138 | 684.1011 | 865.3267 | 118.8496 | 0.0027089 | 17.702 | 5.0059 | -40.2277 | 3.1211 | 9622.03 | 0.28 | 2.2858 | -1.9011 | 0.34747 | -2.0002 | 7.2207 | 6.0734 | 7.9748 | 86.3219 | 193.8349 | 53.1176 | 61.9093 | 9.0196 | 90.7131 | 39.681
42810.4537 | 1181 | 17.4255 | 17.8523 | 18.0083 | 18.0514 | 17.4104 | 16.082 | 15.1918 | 16.4578 | 16.9268 | 17.0742 | 17.1006 | 16.6366 | 15.6676 | 14.4615 | 37.5447 | 55.406 | 54.1226 | 90.0597 | 74.4635 | 93.151 |  |  |  | 48.2726 | 88.1162 | 540.6855 | 692.0057 | 711.7228 | 698.5142 | 21.403 | 58.6224 | 883.8575 | 21.4416 | 56.3409 | 752.4567 | 839.7487 | 768.0739 |  | 242.2764 | 889.5065 | 879.3184 | 679.3099 |  | 478.6489 | 728.3189 | 569.1128 | 739.1983 | 955.3595 | 1050.4902 | 1057.5147 | 53.5721 | 408.9074 | 96.5427 | 630.6905 | 14.7174 | 49.5428 | 48.513 | 51.2713 | 73.4764 |  |  | 1.1962 | -1.1801 | -0.40293 | -1.0777 | 8.36 | 5.7769 | 10.3094 | -3.4428 | 20.1067 | 53.8293 | 39.8839 | -5.421e-05 | -4.93e-06 | -0.00077868 | 31.7173 | 16.6202 | 16.6893 | 17.0768 | 17.0856 | 16.095 | 14.662 | 16.6669 | 17.0411 | 17.3841 | 17.4648 | 17.2075 | 16.4037 | 14.708 | 721.4189 | 512.7841 | 471.7007 | 303.6014 | 263.7163 | 742.9381 | 449.4935 | 25.9088 | 43.8341 | 49.6172 | 83.9553 | 86.6632 | 90.6607 |  |  |  | 638.9188 | 595.4696 | 594.2868 | 623.9728 | 80.6531 | 28.4613 | 921.292 |  |  | 771.5488 |  |  | 22.9086 | 59.7936 | 604.9078 | 24.0564 | 62.6066 | 882.4581 | 750.8017 | 631.1685 | 903.815 | 898.0794 | 753.9543 |  | 831.8703 | 925.5628 | 1077.0361 | 609.44 | 699.2434 | 905.4844 |  | 346.7226 |  |  | 468.5775 | 666.31 | 745.8722 | [6 empty] | 620.5329 |  |  | 447.0516 |  |  | 537.2531 | 693.7003 | 699.4908 | 1066.1676 | 1133.8816 | 1078.4245 | 558.9106 | 739.841 | 860.2418 | 639.2957 | 721.3983 | 1086.7947 | 1119.2444 | 652.3637 | 837.4872 | 995.1875 | 1094.9902 | 1102.5554 | 561.1918 | 673.3293 | 713.9343 | 581.4691 | 766.5589 | 892.7936 | 1035.5226 | 1129.5775 | 623.0522 | 715.5173 | 684.3463 | 868.0483 | 100.7918 | -0.0019983 | 17.7018 | 5.0047 | -40.2665 | 3.1211 | 9597.88 | 0.32 | 2.3759 | -2.3958 | -1.3999 | -2.2894 | 7.3309 | 6.094 | 8.1408 | 86.7047 | 192.6409 | 53.1879 | 62.8288 | 12.995 | 91.4339 | 39.652
42810.4537 | 1182 | 17.4202 | 17.8497 | 18.0034 | 18.0405 | 17.4023 | 16.078 | 15.2093 | 16.449 | 16.9206 | 17.0712 | 17.0904 | 16.6295 | 15.6683 | 14.4598 | 37.6704 | 55.5422 | 54.2394 | 90.0716 | 74.6987 | 93.2042 |  |  |  | 48.4693 | 88.1439 | 541.6809 | 692.6435 | 711.9853 | 699.5765 | 22.2598 | 59.4074 | 897.2904 | 33.9151 | 73.1384 | 764.4314 | 849.299 | 766.6191 |  | 240.1865 | 888.0082 | 883.7556 | 629.5932 |  | 480.9633 | 730.4259 | 567.1243 | 744.9021 | 951.5364 | 1044.5128 | 1056.1307 | 54.1039 | 408.7551 | 92.8644 | 630.5258 | 14.7193 | 49.5623 | 48.5109 | 51.2933 | 73.5448 |  |  | 1.1107 | -1.184 | 0.19504 | -0.88053 | 8.4448 | 6.3519 | 8.9084 | -3.0038 | 19.2137 | 52.0657 | 39.4069 | -8.542e-05 | -3.285e-05 | -0.00080168 | 31.8097 | 16.6315 | 16.6922 | 17.0779 | 17.0923 | 16.095 | 14.6691 | 16.6743 | 17.0406 | 17.3906 | 17.4708 | 17.2124 | 16.4091 | 14.7137 | 718.556 | 506.152 | 461.6735 | 288.5578 | 254.8397 | 742.7649 | 449.8264 | 26.0006 | 43.9429 | 49.7144 | 84.0192 | 86.6977 | 90.7235 |  |  |  | 639.039 | 595.7097 | 594.3085 | 624.489 | 67.8875 | 25.8335 | 918.3515 |  |  | 768.0381 |  |  | 22.9539 | 59.8776 | 606.3953 | 24.1084 | 62.6618 | 882.2556 | 753.2428 | 631.4385 | 900.4875 | 893.4852 | 759.8725 |  | 833.6199 | 922.2873 | 1074.9888 | 609.6827 | 699.5437 | 909.2864 |  | 349.5609 |  |  | 469.4793 | 670.484 | 751.9225 | [6 empty] | 620.6859 |  |  | 446.8561 |  |  | 537.8257 | 694.2394 | 700.0375 | 1061.7227 | 1140.8509 | 1083.6619 | 559.2215 | 741.1552 | 866.5993 | 640.4239 | 722.595 | 1089.8407 | 1121.202 | 652.7217 | 839.3949 | 995.5917 | 1088.8143 | 1101.6853 | 562.6076 | 673.0326 | 713.4989 | 581.7406 | 767.5954 | 893.2458 | 1032.5796 | 1128.9319 | 623.3577 | 715.4492 | 684.4886 | 869.0694 | 98.9868 | 0.0013339 | 17.7021 | 5.0028 | -40.2402 | 3.1211 | 9474.03 | 0.3 | 2.2907 | -2.4023 | 0.97501 | -2.0716 | 7.3513 | 6.3756 | 7.5504 | 87.1256 | 191.5347 | 53.2521 | 63.0865 | 14.1746 | 96.1044 | 39.6616
42810.4537 | 1183 | 17.4206 | 17.8508 | 18.0013 | 18.0476 | 17.4145 | 16.0809 | 15.2087 | 16.4569 | 16.9265 | 17.0673 | 17.0985 | 16.6299 | 15.6774 | 14.4569 | 37.828 | 55.6894 | 54.3911 | 90.0898 | 74.9553 | 93.2319 |  |  |  | 48.6519 | 88.1555 | 541.8374 | 692.5908 | 711.455 | 699.8883 | 27.2065 | 62.7388 | 884.0973 | 24.9171 | 60.1631 | 755.8604 | 847.7261 | 768.7048 |  | 246.1719 | 879.2163 | 871.2161 | 647.6599 |  | 481.644 | 731.0776 | 566.0995 | 746.9536 | 950.1897 | 1042.0109 | 1052.9516 | 54.9206 | 408.6323 | 90.4841 | 630.0938 | 14.7122 | 49.5518 | 48.4993 | 51.3067 | 73.599 |  |  | 1.4669 | -0.48421 | -0.32211 | -1.1532 | 7.2836 | 5.8262 | 9.5301 | -3.2772 | 20.9489 | 56.9779 | 37.4026 | -6.9e-05 | -0.00010021 | -0.00079347 | 31.8966 | 16.6333 | 16.6906 | 17.0756 | 17.0898 | 16.0951 | 14.6716 | 16.6771 | 17.0386 | 17.3878 | 17.4713 | 17.2155 | 16.4129 | 14.7137 | 702.2031 | 499.3394 | 449.2449 | 274.3973 | 247.2088 | 741.8347 | 449.6139 | 26.1152 | 44.0633 | 49.8239 | 84.0789 | 86.7388 | 90.7787 |  |  |  | 639.0552 | 594.6191 | 593.8739 | 622.9942 | 80.8354 | 27.7482 | 914.3709 |  |  | 764.0994 |  |  | 22.9918 | 59.9572 | 606.1978 | 24.162 | 62.7194 | 876.7665 | 752.1948 | 632.2921 | 896.7054 | 889.9796 | 758.4255 |  | 834.4123 | 920.0023 | 1075.2902 | 610.8553 | 700.0699 | 906.8599 |  | 351.2267 |  |  | 470.1405 | 668.016 | 750.6527 | [6 empty] | 621.5334 |  |  | 445.9342 |  |  | 538.4941 | 695.2071 | 701.4983 | 1062.5357 | 1143.3431 | 1088.9807 | 559.6375 | 743.1535 | 868.0098 | 641.066 | 723.3341 | 1090.567 | 1121.8327 | 653.7929 | 843.6569 | 997.0429 | 1085.752 | 1104.5213 | 563.2217 | 673.2032 | 714.4067 | 581.1621 | 767.7642 | 894.348 | 1031.9045 | 1127.0644 | 623.8084 | 717.1125 | 684.3002 | 868.6261 | 88.0136 | 0.00053422 | 17.7017 | 5.001 | -40.1797 | 3.1211 | 9388.25 | 0.35 | 2.6329 | -1.5367 | -1.2534 | -2.3716 | 6.8207 | 6.1003 | 7.802 | 87.4317 | 191.7741 | 53.3441 | 64.5792 | 15.5138 | 95.0554 | 39.7064
42810.4537 | 1184 | 17.4146 | 17.8505 | 18.0033 | 18.0454 | 17.4101 | 16.0804 | 15.2012 | 16.4542 | 16.9242 | 17.0675 | 17.096 | 16.6295 | 15.6718 | 14.4614 | 37.9747 | 55.8205 | 54.5252 | 90.0906 | 75.2344 | 93.2678 |  |  |  | 48.831 | 88.1785 | 542.8724 | 692.4508 | 711.0532 | 699.676 | 23.1365 | 62.293 | 879.8932 | 24.1622 | 59.5108 | 750.3687 | 841.7577 | 769.2384 |  | 234.2977 | 880.0434 | 869.4584 | 640.9384 |  | 481.9341 | 730.6406 | 566.7735 | 746.3708 | 946.3247 | 1041.5936 | 1052.2528 | 55.3533 | 408.4908 | 89.6985 | 630.0856 | 14.6983 | 49.5454 | 48.4968 | 51.3251 | 73.6023 |  |  | 1.2507 | -0.72734 | -0.46273 | -0.58615 | 8.5722 | 6.2507 | 10.8371 | -2.7784 | 20.7919 | 56.248 | 36.9503 | -8.542e-05 | -4.107e-05 | -0.00080989 | 31.9812 | 16.6351 | 16.6918 | 17.0747 | 17.0822 | 16.0934 | 14.6683 | 16.6762 | 17.0409 | 17.3854 | 17.4701 | 17.2059 | 16.4035 | 14.7133 | 714.6219 | 502.4953 | 444.8 | 265.0068 | 240.5515 | 742.1812 | 449.6585 | 26.2395 | 44.1857 | 49.9418 | 84.1316 | 86.7827 | 90.8383 |  |  |  | 639.3301 | 595.7295 | 594.5029 | 626.5369 | 94.906 | 32.2475 | 911.329 |  |  | 764.4001 |  |  | 23.0292 | 60.0305 | 606.6832 | 24.2168 | 62.7974 | 874.3299 | 750.1172 | 632.7139 | 893.7264 | 887.7375 | 755.042 |  | 835.0157 | 925.0296 | 1076.8173 | 612.0723 | 700.5004 | 918.1963 |  | 353.1236 |  |  | 470.5518 | 663.8862 | 748.5094 | [6 empty] | 622.34 |  |  | 446.1103 |  |  | 538.7298 | 695.3913 | 702.4607 | 1063.1848 | 1140.5665 | 1088.2648 | 559.9925 | 744.5465 | 869.8307 | 640.7648 | 723.8274 | 1093.6837 | 1122.0402 | 654.0099 | 847.4083 | 992.3428 | 1082.556 | 1104.5614 | 563.0874 | 673.7991 | 715.4272 | 580.9097 | 767.7966 | 893.6242 | 1029.9527 | 1127.3361 | 624.0571 | 718.8517 | 684.1423 | 868.4734 | 83.1419 | -0.00096006 | 17.7027 | 4.9998 | -40.279 | 3.121 | 9293.28 | 0.45 | 2.4309 | -1.883 | -1.5019 | -1.6904 | 7.3983 | 6.3176 | 8.3185 | 87.7285 | 192.5275 | 53.4123 | 63.3201 | 16.0164 | 93.1853 | 39.663
42810.4538 | 1185 | 17.41 | 17.8427 | 17.9945 | 18.0409 | 17.4015 | 16.0737 | 15.2067 | 16.4522 | 16.9201 | 17.0657 | 17.084 | 16.6267 | 15.6651 | 14.4505 | 38.1268 | 55.9517 | 54.6719 | 90.1013 | 75.5095 | 93.3228 |  |  |  | 49.0198 | 88.1989 | 542.9814 | 691.8565 | 710.3141 | 698.9176 | 21.5043 | 59.1139 | 877.8803 | 23.266 | 60.6679 | 752.9099 | 839.1434 | 768.621 |  | 236.2724 | 885.1812 | 877.1174 | 624.4455 |  | 481.776 | 729.8594 | 567.6728 | 743.1362 | 944.1657 | 1040.9132 | 1051.2814 | 55.3464 | 408.5075 | 88.8467 | 630.3419 | 14.6838 | 49.5739 | 48.5108 | 51.3285 | 73.7 |  |  | 1.1587 | -0.74837 | 0.16547 | -0.6834 | 8.1891 | 6.622 | 9.5938 | -3.2365 | 20.622 | 54.4603 | 43.1971 | -0.00010842 | -5.257e-05 | -0.00075404 | 32.0649 | 16.6417 | 16.691 | 17.0766 | 17.0886 | 16.0923 | 14.674 | 16.6776 | 17.0437 | 17.3862 | 17.4745 | 17.2121 | 16.4066 | 14.7122 | 742.5379 | 510.8366 | 444.3543 | 264.2309 | 231.2104 | 744.1483 | 449.8632 | 26.3254 | 44.2981 | 50.0532 | 84.185 | 86.8133 | 90.9005 |  |  |  | 639.9437 | 599.0379 | 597.0296 | 631.9973 | 93.8219 | 36.3729 | 909.1858 |  |  | 764.6382 |  |  | 23.0704 | 60.1072 | 606.659 | 24.2647 | 62.8688 | 874.2696 | 748.336 | 632.9486 | 894.9236 | 889.4234 | 753.2466 |  | 834.7036 | 923.959 | 1078.6103 | 612.3367 | 700.8109 | 924.0454 |  | 356.9647 |  |  | 470.8017 | 660.5807 | 746.3 | [6 empty] | 622.4821 |  |  | 446.4696 |  |  | 538.8747 | 695.5051 | 703.3516 | 1072.9831 | 1139.4226 | 1084.5542 | 560.1023 | 744.4721 | 870.7238 | 640.5494 | 724.736 | 1096.7918 | 1121.1691 | 653.803 | 845.6077 | 990.3566 | 1083.5445 | 1103.181 | 562.5754 | 674.3545 | 715.5963 | 580.888 | 768.4194 | 892.5898 | 1031.1878 | 1129.5824 | 624.3213 | 718.6456 | 684.245 | 868.356 | 88.4417 | -0.00099511 | 17.7025 | 4.9943 | -40.2357 | 3.121 | 9233.57 | 0.22 | 2.3389 | -1.9093 | 0.8978 | -1.8246 | 7.2293 | 6.5008 | 7.8247 | 87.6735 | 193.6094 | 53.4786 | 60.9052 | 16.1063 | 92.752 | 39.6342
42810.4538 | 1186 | 17.416 | 17.842 | 17.9907 | 18.0452 | 17.4087 | 16.0768 | 15.2101 | 16.4563 | 16.9214 | 17.0703 | 17.0932 | 16.6234 | 15.6647 | 14.4662 | 38.283 | 56.0886 | 54.8036 | 90.1244 | 75.7863 | 93.3442 |  |  |  | 49.2123 | 88.2173 | 543.8566 | 691.8021 | 710.4818 | 698.7703 | 23.446 | 59.8848 | 879.9332 | 22.9025 | 60.6218 | 754.5699 | 839.5577 | 769.2568 |  | 245.7212 | 884.4103 | 878.5792 | 672.6969 |  | 482.0895 | 728.8193 | 566.94 | 741.3014 | 940.2456 | 1040.9931 | 1051.9826 | 54.8737 | 408.4733 | 89.1878 | 630.5443 | 14.6708 | 49.6054 | 48.5417 | 51.3481 | 73.7299 |  |  | 1.3184 | -1.029 | -0.54158 | -0.33184 | 7.9802 | 6.0943 | 10.1517 | -3.3574 | 19.8445 | 54.0145 | 43.6835 | -9.857e-05 | -8.707e-05 | -0.00079839 | 32.1711 | 16.6515 | 16.7028 | 17.0794 | 17.09 | 16.1013 | 14.6758 | 16.6813 | 17.0511 | 17.3884 | 17.4761 | 17.2169 | 16.4097 | 14.7155 | 754.5369 | 520.623 | 463.7926 | 274.567 | 228.1911 | 745.3313 | 450.1658 | 26.4319 | 44.4111 | 50.1585 | 84.2411 | 86.8513 | 90.9574 |  |  |  | 640.4201 | 600.3487 | 598.3436 | 632.2694 | 72.5995 | 26.1132 | 909.0765 |  |  | 766.6795 |  |  | 23.1192 | 60.1858 | 607.3026 | 24.3197 | 62.9367 | 878.2157 | 746.7255 | 633.8519 | 894.0337 | 888.8034 | 751.9011 |  | 833.9912 | 921.6427 | 1078.4956 | 612.4972 | 701.1465 | 929.6572 |  | 358.507 |  |  | 471.0647 | 661.2804 | 744.781 | [6 empty] | 623.1215 |  |  | 446.6461 |  |  | 539.4658 | 695.2548 | 703.9563 | 1079.2123 | 1142.602 | 1081.7326 | 560.5971 | 742.7456 | 869.8788 | 640.3172 | 724.9417 | 1096.7005 | 1121.0021 | 653.4767 | 840.6592 | 989.0862 | 1088.1446 | 1100.3363 | 562.5677 | 674.2775 | 715.1965 | 581.1883 | 768.1835 | 890.3964 | 1028.3576 | 1129.802 | 624.5711 | 717.5975 | 684.2456 | 866.6556 | 91.6653 | -0.0009881 | 17.7033 | 4.9859 | -40.1848 | 3.121 | 9186.78 | 0.39 | 2.4946 | -2.2377 | -1.6234 | -1.2707 | 7.1367 | 6.2366 | 8.0493 | 87.4716 | 193.6064 | 53.5539 | 59.9863 | 14.006 | 91.5526 | 39.7222
42810.4538 | 1187 | 17.408 | 17.8409 | 18.0001 | 18.0472 | 17.4029 | 16.0769 | 15.2231 | 16.4614 | 16.9178 | 17.0703 | 17.0954 | 16.6269 | 15.6684 | 14.4655 | 38.4384 | 56.2332 | 54.936 | 90.13 | 76.0371 | 93.3715 |  |  |  | 49.3969 | 88.2357 | 545.4076 | 692.2776 | 711.3259 | 699.3481 | 24.0705 | 59.4293 | 884.3694 | 21.7514 | 58.6555 | 754.0561 | 837.6537 | 769.1712 |  | 248.3232 | 885.2957 | 875.8586 | 756.851 |  | 483.5888 | 729.2857 | 567.637 | 739.2272 | 938.5353 | 1039.9698 | 1049.6631 | 54.7271 | 408.641 | 90.4026 | 630.9373 | 14.6403 | 49.5772 | 48.5653 | 51.3736 | 73.7919 |  |  | 0.83213 | -1.211 | 0.39284 | -0.23787 | 7.7706 | 6.5017 | 9.718 | -2.9927 | 20.5848 | 55.2557 | 33.3183 | -9.364e-05 | -1.971e-05 | -0.00079347 | 32.2557 | 16.655 | 16.6885 | 17.0693 | 17.0835 | 16.0993 | 14.6716 | 16.6726 | 17.0496 | 17.3863 | 17.4751 | 17.2127 | 16.4051 | 14.7152 | 731.11 | 506.8788 | 437.0946 | 272.6547 | 229.7967 | 745.4399 | 450.0707 | 26.5216 | 44.5085 | 50.2511 | 84.2913 | 86.8881 | 90.9933 |  |  |  | 640.5231 | 599.4785 | 597.9936 | 629.6337 | 95.92 | 38.5227 | 909.2295 |  |  | 767.6451 |  |  | 23.1631 | 60.2517 | 608.6882 | 24.3774 | 63.012 | 883.4694 | 745.3675 | 634.7473 | 896.366 | 893.6409 | 751.0358 |  | 833.2401 | 927.1112 | 1077.4358 | 613.2127 | 701.5454 | 918.6176 |  | 350.6544 |  |  | 471.9459 | 661.8604 | 743.552 | [6 empty] | 623.771 |  |  | 446.6196 |  |  | 539.893 | 694.3969 | 703.5372 | 1085.6139 | 1142.4496 | 1078.6494 | 561.9711 | 741.2095 | 868.1651 | 639.5876 | 723.3447 | 1099.0132 | 1116.8143 | 653.7205 | 836.7232 | 983.3376 | 1083.9044 | 1095.4871 | 562.2689 | 673.8141 | 714.5582 | 581.766 | 767.5268 | 889.0457 | 1024.6279 | 1125.8168 | 624.1769 | 716.4583 | 684.3175 | 866.4085 | 89.4326 | 0.00041493 | 17.7032 | 4.9779 | -40.278 | 3.121 | 9167.18 | 0.23 | 1.9825 | -2.4281 | 1.3829 | -1.0761 | 7.0396 | 6.4392 | 7.8724 | 87.2438 | 192.8322 | 53.6288 | 62.6274 | 16.9537 | 88.5687 | 39.8161
42810.4538 | 1188 | 17.4083 | 17.8378 | 17.9895 | 18.0403 | 17.3944 | 16.07 | 15.2176 | 16.4514 | 16.9148 | 17.0656 | 17.0878 | 16.6258 | 15.6685 | 14.4561 | 38.5962 | 56.3695 | 55.0835 | 90.1212 | 76.3065 | 93.4156 |  |  |  | 49.5855 | 88.2599 | 547.426 | 693.3384 | 712.9403 | 700.691 | 22.1816 | 60.0869 | 885.1287 | 21.6691 | 56.8454 | 752.8855 | 837.1185 | 769.0373 |  | 253.8196 | 881.5856 | 872.5537 | 739.6867 |  | 483.9743 | 729.7086 | 569.3179 | 740.4339 | 938.4172 | 1038.8418 | 1047.8478 | 54.1218 | 408.7771 | 92.206 | 631.4296 | 14.6348 | 49.5497 | 48.5824 | 51.383 | 73.8719 |  |  | 1.8342 | -2.1842 | 0.26601 | -0.6052 | 7.4059 | 6.2704 | 9.9933 | -3.151 | 20.1073 | 55.3235 | 31.2757 | -0.00012814 | -3.614e-05 | -0.00080004 | 32.3395 | 16.6581 | 16.6864 | 17.0723 | 17.0948 | 16.0961 | 14.6795 | 16.6768 | 17.0441 | 17.3907 | 17.4719 | 17.2143 | 16.4091 | 14.7136 | 746.2158 | 504.2147 | 455.4975 | 277.9392 | 234.452 | 746.9859 | 450.8233 | 26.6292 | 44.615 | 50.366 | 84.3493 | 86.9165 | 91.0372 |  |  |  | 640.4731 | 598.7823 | 598.2108 | 627.0216 | 84.8145 | 33.7556 | 911.2325 |  |  | 776.6481 |  |  | 23.1999 | 60.3297 | 610.656 | 24.4255 | 63.1041 | 881.6456 | 744.9279 | 633.5188 | 898.6788 | 895.9319 | 750.7912 |  | 832.7178 | 927.7232 | 1074.599 | 613.3504 | 701.715 | 921.3152 |  | 346.7901 |  |  | 473.5404 | 661.5484 | 743.0437 | [6 empty] | 623.3859 |  |  | 446.3423 |  |  | 540.0738 | 692.8702 | 702.3673 | 1090.5579 | 1140.122 | 1075.7639 | 563.4622 | 741.2403 | 866.3983 | 638.7356 | 721.4745 | 1106.6206 | 1112.8439 | 654.227 | 836.3336 | 979.9842 | 1079.5389 | 1094.5017 | 561.5632 | 673.4578 | 714.182 | 582.317 | 767.4104 | 890.8888 | 1026.1395 | 1122.9324 | 623.4264 | 716.6301 | 684.8658 | 870.7492 | 93.0429 | 3.6099e-05 | 17.7029 | 4.9656 | -40.1969 | 3.121 | 9157.92 | 0.35 | 2.9454 | -3.2616 | 1.1382 | -1.7169 | 6.8694 | 6.3209 | 7.9797 | 87.0757 | 191.1564 | 53.6653 | 61.4922 | 15.0573 | 88.8643 | 39.8786
42810.4538 | 1189 | 17.4248 | 17.8436 | 18.0001 | 18.048 | 17.4087 | 16.0774 | 15.2271 | 16.4625 | 16.9242 | 17.0747 | 17.0971 | 16.6338 | 15.6695 | 14.4659 | 38.7451 | 56.5052 | 55.2275 | 90.1071 | 76.5696 | 93.4548 |  |  |  | 49.7761 | 88.273 | 549.8043 | 694.8898 | 714.5386 | 702.5433 | 21.6312 | 59.198 | 879.6382 | 23.2349 | 57.6313 | 752.5962 | 837.192 | 769.1073 |  | 259.7028 | 875.6979 | 867.5756 | 731.213 |  | 483.8296 | 731.0946 | 571.0626 | 738.729 | 932.211 | 1037.1769 | 1048.6074 | 51.7192 | 408.8917 | 93.7644 | 631.5962 | 14.642 | 49.553 | 48.582 | 51.3873 | 73.9244 |  |  | 1.0023 | -0.82459 | -0.53173 | -1.3077 | 7.1161 | 5.5693 | 10.8495 | -2.697 | 21.824 | 57.9233 | 30.2826 | -4.435e-05 | -4.271e-05 | -0.00078525 | 32.4213 | 16.6558 | 16.6797 | 17.0728 | 17.085 | 16.0894 | 14.668 | 16.6715 | 17.0336 | 17.3838 | 17.4641 | 17.2113 | 16.4037 | 14.7092 | 740.1496 | 507.4129 | 462.9699 | 277.7548 | 233.1139 | 748.1445 | 451.6245 | 26.7349 | 44.7327 | 50.472 | 84.3888 | 86.9595 | 91.086 |  |  |  | 640.63 | 598.9551 | 599.0424 | 629.884 | 104.3854 | 36.6958 | 913.4718 |  |  | 773.7474 |  |  | 23.2346 | 60.3994 | 613.3006 | 24.4769 | 63.1798 | 876.3752 | 744.456 | 631.4906 | 895.3541 | 891.1404 | 749.1449 |  | 832.2755 | 927.1728 | 1072.3442 | 611.8373 | 701.6797 | 922.9857 |  | 347.4309 |  |  | 475.0897 | 661.387 | 742.6475 | [6 empty] | 621.6705 |  |  | 445.8325 |  |  | 540.5893 | 691.2413 | 701.5958 | 1097.5553 | 1137.3338 | 1074.9052 | 564.0965 | 741.7642 | 866.2711 | 638.0462 | 720.498 | 1114.6565 | 1114.6631 | 654.1871 | 837.5612 | 981.0634 | 1077.9977 | 1097.2481 | 561.1304 | 673.7702 | 714.9491 | 582.5901 | 768.0363 | 894.518 | 1027.5574 | 1121.9217 | 622.8687 | 718.1458 | 685.5718 | 874.3445 | 96.4111 | -0.00025152 | 17.7022 | 4.9526 | -40.2033 | 3.121 | 9255.38 | 0.3 | 2.1793 | -2.0054 | -1.6104 | -2.5254 | 6.7294 | 5.9533 | 8.3093 | 86.9736 | 189.8602 | 53.6989 | 62.5744 | 14.3851 | 89.1246 | 39.8306
42810.4538 | 1190 | 17.4018 | 17.8336 | 17.9921 | 18.0411 | 17.3935 | 16.0649 | 15.2235 | 16.4543 | 16.9083 | 17.0595 | 17.077 | 16.6238 | 15.6576 | 14.4595 | 38.9053 | 56.6423 | 55.3614 | 90.0992 | 76.7728 | 93.4959 |  |  |  | 49.9455 | 88.2816 | 551.1457 | 695.8708 | 715.2012 | 703.2759 | 22.6255 | 59.0462 | 876.5057 | 21.9993 | 57.921 | 754.6051 | 838.3894 | 771.6431 |  | 255.5097 | 882.2273 | 872.2744 | 750.1905 |  | 484.8117 | 732.0701 | 571.4219 | 739.5748 | 932.5431 | 1038.0122 | 1053.122 | 50.498 | 409.1933 | 95.7327 | 632.0726 | 14.5993 | 49.5676 | 48.5707 | 51.3851 | 73.9587 |  |  | 1.0017 | -0.75625 | -0.84714 | -1.1559 | 7.7732 | 6.204 | 9.9644 | -2.9335 | 21.7464 | 58.0601 | 30.7873 | -2.628e-05 | -8.707e-05 | -0.00079347 | 32.5104 | 16.6581 | 16.6803 | 17.0721 | 17.0854 | 16.0952 | 14.6749 | 16.6676 | 17.0348 | 17.3847 | 17.4648 | 17.215 | 16.406 | 14.7115 | 751.7694 | 523.8798 | 501.6969 | 291.5523 | 246.237 | 750.3631 | 452.7135 | 26.8364 | 44.8464 | 50.5837 | 84.4341 | 86.9833 | 91.1286 |  |  |  | 641.1017 | 600.4725 | 600.7365 | 632.9934 | 84.5762 | 32.2214 | 909.5989 |  |  | 768.7478 |  |  | 23.285 | 60.4725 | 614.3039 | 24.5373 | 63.2439 | 877.1217 | 745.6721 | 629.8909 | 892.1921 | 889.286 | 749.6173 |  | 832.3056 | 920.162 | 1072.6069 | 609.5513 | 701.6465 | 910.0613 |  | 348.8183 |  |  | 475.4402 | 662.3564 | 743.1 | [6 empty] | 619.8156 |  |  | 445.3645 |  |  | 541.2511 | 690.1804 | 702.3088 | 1102.0104 | 1136.7555 | 1075.5096 | 563.9868 | 741.8668 | 867.0194 | 637.4494 | 719.9884 | 1122.3934 | 1120.0168 | 653.7706 | 837.9122 | 981.7506 | 1078.2642 | 1100.2408 | 561.2238 | 674.6634 | 716.8784 | 582.7196 | 768.4755 | 895.3468 | 1025.1901 | 1124.1664 | 622.5563 | 719.964 | 685.871 | 874.6272 | 93.969 | -0.00024451 | 17.7006 | 4.9399 | -40.2917 | 3.121 | 9345.52 | 0.27 | 2.1795 | -1.9215 | -2.0336 | -2.3755 | 7.0355 | 6.2854 | 7.9656 | 86.9706 | 190.2074 | 53.7545 | 62.0676 | 10.2973 | 89.0031 | 39.839
42810.4538 | 1191 | 17.4159 | 17.8482 | 18.0005 | 18.0408 | 17.4081 | 16.0793 | 15.2406 | 16.4607 | 16.9222 | 17.0737 | 17.1015 | 16.6286 | 15.6712 | 14.4721 | 39.0572 | 56.7777 | 55.5053 | 90.0941 | 76.9815 | 93.5172 |  |  |  | 50.1199 | 88.3015 | 552.9396 | 696.6887 | 716.0494 | 703.6953 | 21.8666 | 59.1973 | 886.5455 | 22.4498 | 57.383 | 756.7217 | 839.2951 | 774.879 |  | 252.488 | 896.3608 | 883.574 | 761.7977 |  | 485.5437 | 732.6858 | 570.6701 | 739.4188 | 930.8669 | 1038.8771 | 1057.0225 | 49.8897 | 409.4052 | 95.1722 | 632.8103 | 14.596 | 49.5833 | 48.5646 | 51.3961 | 74.0144 |  |  | 0.98655 | -1.3516 | -0.17886 | -0.86345 | 7.4979 | 6.7869 | 9.5504 | -2.5715 | 20.4476 | 54.9454 | 32.0007 | -7.064e-05 | -1.64e-06 | -0.00074747 | 32.6016 | 16.6653 | 16.6889 | 17.072 | 17.0931 | 16.0943 | 14.6767 | 16.6739 | 17.0411 | 17.3914 | 17.4672 | 17.2188 | 16.4156 | 14.7176 | 755.5984 | 526.7102 | 505.8477 | 293.4214 | 255.9327 | 752.0464 | 453.5325 | 26.9241 | 44.9423 | 50.6714 | 84.4719 | 87.0082 | 91.1639 |  |  |  | 641.6683 | 602.8396 | 602.7005 | 635.7923 | 104.5469 | 43.5582 | 906.4505 |  |  | 769.7119 |  |  | 23.3193 | 60.5402 | 616.2694 | 24.5852 | 63.3103 | 888.1212 | 744.4254 | 627.6918 | 890.5995 | 887.6479 | 748.5742 |  | 832.2202 | 918.0344 | 1074.9236 | 608.2417 | 701.5498 | 912.9712 |  | 332.9215 |  |  | 475.1577 | 661.3694 | 743.1966 | [6 empty] | 617.8391 |  |  | 445.2257 |  |  | 541.6652 | 689.4443 | 702.8799 | 1103.1588 | 1137.2198 | 1075.2703 | 563.6961 | 741.3782 | 866.051 | 637.3613 | 719.2184 | 1127.5432 | 1121.9806 | 653.3084 | 836.4561 | 982.9546 | 1078.8782 | 1102.9823 | 561.4324 | 675.307 | 717.7656 | 582.9113 | 769.0792 | 894.4509 | 1026.667 | 1127.7696 | 622.4004 | 720.3592 | 685.8318 | 875.5121 | 86.5381 | 0.00077273 | 17.6991 | 4.9249 | -40.304 | 3.121 | 9391.32 | 0.3 | 2.1634 | -2.5695 | -0.93472 | -2.0538 | 6.9121 | 6.5762 | 7.801 | 86.971 | 191.6148 | 53.7679 | 62.2395 | 9.9983 | 88.9882 | 39.8753
42810.4538 | 1192 | 17.4099 | 17.8305 | 17.9964 | 18.041 | 17.4013 | 16.0672 | 15.234 | 16.4633 | 16.9159 | 17.0631 | 17.0955 | 16.6253 | 15.6597 | 14.4599 | 39.2002 | 56.9073 | 55.6385 | 90.091 | 77.1808 | 93.5582 |  |  |  | 50.3007 | 88.3201 | 553.8881 | 697.1662 | 716.3318 | 703.9109 | 21.7896 | 59.0862 | 895.5581 | 22.1496 | 57.5231 | 756.8375 | 838.1747 | 772.6493 |  | 250.7778 | 900.5546 | 886.9189 | 765.5562 |  | 484.7512 | 733.5445 | 572.0204 | 740.9309 | 937.0848 | 1041.6072 | 1056.4223 | 49.1735 | 409.5231 | 93.3479 | 633.4246 | 14.6291 | 49.5965 | 48.5712 | 51.3955 | 74.0666 |  |  | 1.1015 | -0.88702 | 0.016964 | -0.46392 | 7.9348 | 6.4682 | 9.5872 | -3.6544 | 20.5074 | 53.356 | 33.342 | -7.392e-05 | -3.943e-05 | -0.00078854 | 32.6855 | 16.6697 | 16.6758 | 17.0593 | 17.0854 | 16.0864 | 14.6638 | 16.6805 | 17.0382 | 17.3816 | 17.461 | 17.215 | 16.408 | 14.7105 | 765.2316 | 536.0472 | 524.5155 | 317.141 | 274.9048 | 753.9167 | 454.7797 | 27.0357 | 45.0461 | 50.769 | 84.5209 | 87.0507 | 91.208 |  |  |  | 642.1804 | 604.824 | 604.3178 | 635.4872 | 70.7399 | 26.8144 | 906.145 |  |  | 769.1338 |  |  | 23.3572 | 60.6218 | 617.2153 | 24.6211 | 63.3848 | 892.9405 | 740.5447 | 626.3127 | 890.8965 | 889.4746 | 744.9464 |  | 831.6216 | 920.6505 | 1077.6199 | 607.3239 | 701.3556 | 918.01 |  | 311.0593 |  |  | 474.3754 | 657.8214 | 740.4062 | [6 empty] | 616.4436 |  |  | 445.8373 |  |  | 541.7684 | 689.0184 | 702.7596 | 1100.2485 | 1140.1535 | 1072.6622 | 563.3783 | 740.7048 | 865.0003 | 637.7713 | 718.3718 | 1128.8864 | 1121.9684 | 652.5918 | 834.6509 | 981.1955 | 1078.2132 | 1101.432 | 561.0772 | 675.7387 | 717.8809 | 582.8222 | 769.2534 | 894.5672 | 1025.8701 | 1126.4997 | 622.5477 | 720.2259 | 685.3461 | 876.8939 | 84.5552 | -0.00033568 | 17.6983 | 4.9116 | -40.2959 | 3.121 | 9509.14 | 0.28 | 2.2863 | -2.0825 | 0.28799 | -1.506 | 7.118 | 6.4266 | 7.8241 | 86.8719 | 193.1196 | 53.7473 | 61.8353 | 8.1715 | 88.5034 | 39.987
42810.4538 | 1193 | 17.4062 | 17.8332 | 17.9922 | 18.035 | 17.4005 | 16.0646 | 15.2314 | 16.4576 | 16.9154 | 17.067 | 17.0925 | 16.6233 | 15.6618 | 14.4573 | 39.3527 | 57.0279 | 55.7629 | 90.0626 | 77.4444 | 93.5705 |  |  |  | 50.4755 | 88.3254 | 553.3705 | 696.5782 | 714.9863 | 702.9233 | 21.7873 | 59.0738 | 896.0756 | 22.0127 | 57.6442 | 753.9987 | 837.5039 | 769.057 |  | 256.3467 | 900.2204 | 887.8857 | 761.5053 |  | 484.9847 | 732.6379 | 572.844 | 741.3256 | 939.5235 | 1040.2223 | 1054.1527 | 49.405 | 409.7266 | 90.4024 | 633.5614 | 14.6545 | 49.5975 | 48.5896 | 51.3814 | 74.1035 |  |  | 1.1121 | -0.31599 | -0.6349 | -1.3701 | 7.5899 | 4.7814 | 8.3893 | -2.7206 | 20.1816 | 52.0856 | 34.0926 | -4.764e-05 | -5.421e-05 | -0.00076225 | 32.7792 | 16.6829 | 16.6785 | 17.0599 | 17.0777 | 16.0885 | 14.6761 | 16.6699 | 17.0417 | 17.3833 | 17.4669 | 17.2122 | 16.4083 | 14.7141 | 730.0001 | 502.0518 | 464.4682 | 299.7764 | 262.9258 | 752.9331 | 454.7637 | 27.1438 | 45.1701 | 50.8951 | 84.5765 | 87.0791 | 91.2794 |  |  |  | 642.527 | 605.2045 | 605.252 | 635.2165 | 61.6522 | 23.6285 | 908.736 |  |  | 794.5273 |  |  | 23.4103 | 60.686 | 616.8327 | 24.6795 | 63.4575 | 895.4301 | 735.4599 | 625.7805 | 902.5179 | 902.7009 | 739.0756 |  | 830.5157 | 933.3873 | 1078.3321 | 606.8384 | 701.2227 | 919.1262 |  | 312.5647 |  |  | 473.3187 | 653.0325 | 735.4439 | [6 empty] | 615.9234 |  |  | 446.9764 |  |  | 542.2019 | 689.0855 | 702.7218 | 1104.05 | 1139.9466 | 1073.8602 | 563.2366 | 739.3553 | 863.5762 | 638.36 | 718.1747 | 1120.9372 | 1124.5593 | 651.8196 | 831.3681 | 972.2065 | 1075.1394 | 1095.3735 | 560.3848 | 676.5414 | 718.4789 | 582.7135 | 768.1851 | 893.2203 | 1024.0716 | 1122.9753 | 622.5895 | 721.0214 | 684.4579 | 875.2497 | 92.2933 | -0.00086184 | 17.6988 | 4.894 | -40.3055 | 3.121 | 9628.5 | 0.23 | 2.296 | -1.2424 | -1.761 | -2.587 | 6.9579 | 5.5225 | 7.3152 | 86.6666 | 193.184 | 53.7291 | 65.3993 | 14.8403 | 88.3887 | 40.0644
42810.4539 | 1194 | 17.4085 | 17.8406 | 17.9967 | 18.0369 | 17.4001 | 16.0708 | 15.2391 | 16.4573 | 16.9191 | 17.071 | 17.0941 | 16.6258 | 15.6689 | 14.4629 | 39.4952 | 57.168 | 55.8929 | 90.045 | 77.6746 | 93.6163 |  |  |  | 50.65 | 88.3521 | 552.1062 | 695.2297 | 712.8552 | 701.4213 | 22.3573 | 59.1368 | 897.7132 | 22.0731 | 57.6601 | 750.9553 | 836.5253 | 765.3079 |  | 254.8759 | 901.2083 | 889.0489 | 758.0177 |  | 484.1598 | 730.5039 | 571.9669 | 737.8349 | 931.0655 | 1032.8983 | 1049.8374 | 49.4199 | 409.8821 | 86.8752 | 633.7799 | 14.6782 | 49.5961 | 48.6108 | 51.3773 | 74.1515 |  |  | 1.1791 | -0.81934 | -0.36022 | -0.95807 | 8.0045 | 6.0917 | 8.6541 | -3.5933 | 20.2176 | 54.7912 | 36.6008 | -7.064e-05 | -4.93e-06 | -0.00075897 | 32.8771 | 16.6845 | 16.6815 | 17.0652 | 17.0811 | 16.0893 | 14.6729 | 16.6796 | 17.047 | 17.3839 | 17.4693 | 17.2191 | 16.412 | 14.7217 | 697.621 | 486.0054 | 437.9435 | 286.4539 | 252.3262 | 750.7813 | 454.0448 | 27.245 | 45.2702 | 50.9874 | 84.6169 | 87.1024 | 91.3272 |  |  |  | 643.0964 | 607.2795 | 606.8185 | 638.1244 | 64.8316 | 26.7114 | 915.9713 |  |  | 795.0659 |  |  | 23.4484 | 60.7645 | 614.9705 | 24.7445 | 63.5371 | 896.6543 | 732.9227 | 626.7514 | 903.7427 | 906.9464 | 734.7244 |  | 829.442 | 931.2561 | 1080.0166 | 606.9349 | 701.2719 | 913.5025 |  | 314.1273 |  |  | 473.2084 | 651.2813 | 731.6814 | [6 empty] | 616.8436 |  |  | 447.2454 |  |  | 542.7 | 689.3003 | 702.1114 | 1105.823 | 1141.393 | 1073.4382 | 563.7835 | 738.8706 | 862.0144 | 638.5166 | 718.1098 | 1124.7558 | 1124.1538 | 652.5412 | 829.9772 | 971.9237 | 1075.2443 | 1097.0788 | 559.9568 | 677.3063 | 719.0852 | 582.9218 | 766.2914 | 890.9654 | 1022.1507 | 1121.4354 | 622.9556 | 721.8654 | 683.5964 | 872.4651 | 92.9476 | -0.002293 | 17.6978 | 4.8781 | -40.2602 | 3.121 | 9696.18 | 0.35 | 2.3624 | -1.9984 | -1.3251 | -2.161 | 7.1255 | 6.216 | 7.409 | 86.4307 | 194.2349 | 53.7382 | 68.2323 | 17.6448 | 88.1547 | 40.0987
42810.4539 | 1195 | 17.4103 | 17.8399 | 17.9962 | 18.036 | 17.3994 | 16.0678 | 15.2391 | 16.4607 | 16.9115 | 17.0676 | 17.0859 | 16.6296 | 15.6652 | 14.4673 | 39.6708 | 57.3151 | 56.0508 | 90.0403 | 77.9185 | 93.6965 |  |  |  | 50.8577 | 88.3695 | 550.3977 | 693.2612 | 709.9881 | 699.5685 | 23.0614 | 59.3339 | 898.8813 | 22.0297 | 57.5872 | 749.3089 | 835.7295 | 763.4169 |  | 255.2694 | 900.674 | 888.6763 | 748.077 |  | 483.7509 | 728.2236 | 571.6247 | 735.2876 | 921.6876 | 1031.9642 | 1050.2137 | 49.3399 | 409.9515 | 84.2022 | 633.9195 | 14.6945 | 49.5894 | 48.6247 | 51.3824 | 74.19 |  |  | 1.8507 | -1.3371 | 0.12144 | -1.0757 | 7.7101 | 5.9083 | 9.513 | -2.3763 | 20.867 | 54.9668 | 37.3692 | -7.721e-05 | -7.064e-05 | -0.00078032 | 32.9677 | 16.6877 | 16.6728 | 17.0663 | 17.0745 | 16.0887 | 14.6678 | 16.6653 | 17.0375 | 17.3845 | 17.4653 | 17.2103 | 16.3981 | 14.716 | 671.6524 | 479.3646 | 426.3169 | 290.9762 | 249.2499 | 748.911 | 453.4417 | 27.3448 | 45.3835 | 51.0986 | 84.6712 | 87.1408 | 91.3812 |  |  |  | 643.7561 | 610.0465 | 608.6844 | 640.5893 | 91.3348 | 34.8976 | 918.6856 |  |  | 796.6166 |  |  | 23.4894 | 60.8289 | 612.7528 | 24.7957 | 63.5919 | 898.5575 | 732.0686 | 626.0753 | 904.9133 | 905.3308 | 733.8468 |  | 828.9514 | 929.1406 | 1082.1661 | 606.6127 | 701.2616 | 908.7015 |  | 315.0943 |  |  | 473.8639 | 650.7085 | 730.3221 | [6 empty] | 616.5139 |  |  | 447.3385 |  |  | 542.4919 | 689.4864 | 701.6515 | 1109.2779 | 1135.0773 | 1071.4031 | 564.3791 | 738.497 | 861.754 | 638.3412 | 718.2197 | 1130.5764 | 1119.3091 | 652.6579 | 829.5738 | 971.2203 | 1075.2775 | 1096.1922 | 560.151 | 677.756 | 719.2502 | 583.1797 | 765.4231 | 889.4142 | 1023.1168 | 1121.8626 | 623.0948 | 722.2935 | 683.1611 | 872.298 | 92.4172 | 0.0001203 | 17.6974 | 4.8584 | -40.2523 | 3.121 | 9674.2 | 0.34 | 2.9568 | -2.5501 | 0.76852 | -2.2872 | 6.9907 | 6.1196 | 7.7651 | 86.2924 | 195.5641 | 53.7447 | 70.4558 | 18.8171 | 88.1623 | 40.1638
42810.4539 | 1196 | 17.4068 | 17.8421 | 17.9891 | 18.042 | 17.3946 | 16.0685 | 15.247 | 16.4571 | 16.9058 | 17.0645 | 17.0855 | 16.6275 | 15.6664 | 14.4622 | 39.8226 | 57.4449 | 56.1783 | 90.0152 | 78.1857 | 93.7283 |  |  |  | 51.0192 | 88.3776 | 548.1261 | 690.6482 | 706.6218 | 697.3578 | 22.1699 | 59.8411 | 899.1625 | 22.7876 | 57.6183 | 747.9899 | 834.6464 | 761.5584 |  | 262.7347 | 898.814 | 887.2543 | 754.7556 |  | 484.0788 | 727.8161 | 573.5973 | 734.2983 | 920.5005 | 1033.8663 | 1051.4417 | 49.4593 | 409.9437 | 84.2351 | 633.9025 | 14.6758 | 49.6032 | 48.6412 | 51.3919 | 74.2264 |  |  | 1.5096 | -1.2208 | -0.037576 | -1.2886 | 7.5951 | 6.4255 | 10.2982 | -3.2443 | 20.879 | 54.8231 | 38.4982 | -0.00010185 | -9.692e-05 | -0.00079018 | 33.0608 | 16.6981 | 16.6743 | 17.0634 | 17.0826 | 16.0862 | 14.6723 | 16.6697 | 17.0366 | 17.3829 | 17.464 | 17.2071 | 16.4012 | 14.7161 | 691.516 | 493.3162 | 438.5272 | 291.3887 | 244.8226 | 749.1915 | 453.5715 | 27.44 | 45.4853 | 51.1974 | 84.7143 | 87.1715 | 91.4229 |  |  |  | 644.3097 | 611.3371 | 609.6599 | 641.0858 | 96.6088 | 29.6878 | 919.176 |  |  | 791.5269 |  |  | 23.5405 | 60.91 | 609.4887 | 24.8504 | 63.6889 | 898.434 | 733.3181 | 625.6981 | 902.0934 | 901.5735 | 736.0279 |  | 828.9657 | 925.0279 | 1084.3651 | 605.8433 | 701.2401 | 908.7504 |  | 316.2878 |  |  | 474.5788 | 654.0628 | 730.9622 | [6 empty] | 615.8803 |  |  | 446.5964 |  |  | 542.9218 | 690.229 | 701.711 | 1111.7089 | 1137.1116 | 1068.4749 | 564.3461 | 736.4353 | 860.8886 | 639.1208 | 719.3835 | 1132.319 | 1114.1846 | 651.461 | 826.349 | 969.7248 | 1074.6597 | 1096.0403 | 560.9661 | 677.7424 | 719.1927 | 583.7575 | 766.7705 | 887.079 | 1022.4888 | 1123.2487 | 622.9987 | 722.2867 | 683.0932 | 873.7165 | 81.7306 | 0.0010744 | 17.6969 | 4.8435 | -40.2675 | 3.121 | 9604.94 | 0.32 | 2.6675 | -2.4362 | -0.4274 | -2.5029 | 6.9434 | 6.3865 | 8.0852 | 86.2366 | 196.9841 | 53.7609 | 68.3478 | 17.4861 | 87.6123 | 40.2622
42810.4539 | 1197 | 17.4219 | 17.8428 | 17.9936 | 18.0453 | 17.4022 | 16.071 | 15.2427 | 16.4642 | 16.9169 | 17.0729 | 17.0886 | 16.6325 | 15.6605 | 14.4628 | 39.9768 | 57.5754 | 56.3187 | 90.0239 | 78.4142 | 93.7833 |  |  |  | 51.1953 | 88.3936 | 547.5247 | 689.688 | 705.9752 | 696.7095 | 22.0262 | 59.4198 | 900.7334 | 24.0725 | 58.0114 | 748.4276 | 834.4269 | 761.2389 |  | 253.2849 | 900.5326 | 888.9616 | 733.4761 |  | 483.2644 | 727.7922 | 576.926 | 736.9943 | 921.8783 | 1037.3526 | 1051.8523 | 49.8721 | 409.8857 | 85.0444 | 633.9743 | 14.6731 | 49.5837 | 48.6381 | 51.4034 | 74.241 |  |  | 1.3986 | -0.76151 | 0.075448 | -1.2439 | 6.6443 | 4.6933 | 9.5163 | -2.7548 | 20.6714 | 54.304 | 41.6381 | -7.064e-05 | 0 | -0.00076718 | 33.1446 | 16.7019 | 16.6748 | 17.0632 | 17.0799 | 16.0901 | 14.6723 | 16.6718 | 17.0377 | 17.3847 | 17.4633 | 17.2101 | 16.404 | 14.7204 | 720.2036 | 503.0296 | 447.1218 | 286.5428 | 248.7096 | 750.717 | 453.9069 | 27.5608 | 45.596 | 51.3031 | 84.7709 | 87.2129 | 91.4771 |  |  |  | 644.8743 | 611.1358 | 609.7176 | 641.6743 | 95.3392 | 36.3318 | 916.5124 |  |  | 788.9708 |  |  | 23.5823 | 60.9807 | 607.8667 | 24.9004 | 63.7533 | 900.1806 | 732.9604 | 626.3419 | 902.5622 | 903.2315 | 737.6723 |  | 828.3517 | 921.1843 | 1085.0927 | 606.2506 | 701.3121 | 900.8456 |  | 318.0591 |  |  | 475.1459 | 655.4901 | 731.358 | [6 empty] | 616.5955 |  |  | 446.3709 |  |  | 543.2869 | 691.2142 | 701.9764 | 1106.8123 | 1136.9744 | 1063.8571 | 564.0314 | 735.0145 | 859.4764 | 640 | 719.9645 | 1136.8121 | 1114.7439 | 650.5743 | 826.0547 | 969.1356 | 1073.4291 | 1094.8784 | 560.0012 | 677.3077 | 718.9722 | 583.7994 | 768.1579 | 886.1947 | 1023.2955 | 1125.9999 | 623.1126 | 722.5817 | 682.922 | 874.0833 | 83.4742 | -0.00076362 | 17.6968 | 4.8346 | -40.3044 | 3.121 | 9538.41 | 0.27 | 2.5666 | -1.924 | 0.60561 | -2.4591 | 6.5029 | 5.4655 | 7.7825 | 85.9876 | 197.5242 | 53.7667 | 65.7003 | 16.5976 | 88.1296 | 40.3606
42810.4539 | 1198 | 17.4109 | 17.8353 | 17.9968 | 18.0365 | 17.4012 | 16.0765 | 15.253 | 16.4588 | 16.915 | 17.0692 | 17.0911 | 16.6323 | 15.6708 | 14.4789 | 40.1283 | 57.7113 | 56.4507 | 90.0535 | 78.58 | 93.8459 |  |  |  | 51.3597 | 88.4185 | 547.8334 | 689.6221 | 705.8752 | 696.5707 | 22.0776 | 60.0052 | 901.4953 | 22.5413 | 57.9277 | 748.5612 | 834.9593 | 763.8688 |  | 254.3537 | 899.431 | 887.6878 | 752.0276 |  | 482.9284 | 726.6337 | 576.8548 | 735.6449 | 915.8527 | 1034.8446 | 1050.6819 | 50.078 | 409.6039 | 85.6615 | 633.9745 | 14.6854 | 49.5549 | 48.6544 | 51.4221 | 74.28 |  |  | 1.1324 | -0.34753 | 0.21673 | -1.0869 | 7.3539 | 6.2987 | 10.8121 | -2.3724 | 20.9483 | 55.6407 | 41.462 | -0.00013964 | -8.707e-05 | -0.00075404 | 33.2288 | 16.7001 | 16.6686 | 17.0622 | 17.0771 | 16.0839 | 14.6703 | 16.6635 | 17.0293 | 17.3774 | 17.4613 | 17.2102 | 16.3958 | 14.7127 | 756.0109 | 521.229 | 488.5891 | 292.4715 | 255.2853 | 752.6793 | 454.5331 | 27.6742 | 45.7058 | 51.4232 | 84.828 | 87.2531 | 91.534 |  |  |  | 645.4146 | 610.8499 | 610.735 | 641.0906 | 91.3121 | 39.1588 | 917.7785 |  |  | 787.886 |  |  | 23.6211 | 61.0394 | 608.4699 | 24.9594 | 63.8124 | 900.7906 | 732.1362 | 624.618 | 899.5138 | 898.4633 | 737.5669 |  | 827.399 | 917.9273 | 1087.4175 | 606.2648 | 701.0136 | 908.7969 |  | 319.8012 |  |  | 475.7949 | 656.5909 | 730.537 | [6 empty] | 615.6376 |  |  | 447.1589 |  |  | 542.9304 | 691.8092 | 701.7743 | 1101.5158 | 1143.9793 | 1060.66 | 563.9164 | 734.9535 | 859.113 | 640.5067 | 719.5088 | 1133.3219 | 1111.4236 | 650.767 | 825.8609 | 969.6149 | 1074.7526 | 1096.523 | 560.4606 | 677.337 | 719.1076 | 583.2232 | 768.1466 | 886.8687 | 1021.8878 | 1127.4052 | 623.1702 | 723.3609 | 681.9972 | 874.3777 | 93.8642 | -0.00014628 | 17.6968 | 4.8264 | -40.234 | 3.121 | 9484.05 | 0.3 | 2.3094 | -1.299 | 1.0258 | -2.2973 | 6.8349 | 6.3255 | 8.2875 | 85.6757 | 199.0039 | 53.6954 | 62.4188 | 12.1144 | 87.7933 | 40.4867
42810.4539 | 1199 | 17.4093 | 17.834 | 17.9917 | 18.038 | 17.3956 | 16.0693 | 15.2651 | 16.4627 | 16.92 | 17.0722 | 17.0949 | 16.6365 | 15.6683 | 14.4748 | 40.2831 | 57.8415 | 56.5842 | 90.0955 | 78.7237 | 93.8734 |  |  |  | 51.532 | 88.431 | 547.3905 | 688.7574 | 704.8222 | 695.5596 | 22.338 | 60.3617 | 900.3528 | 23.6513 | 58.64 | 746.6505 | 833.736 | 762.6671 |  | 242.3545 | 897.9257 | 885.0113 | 736.4446 |  | 483.1969 | 727.1595 | 577.5207 | 732.5158 | 914.3393 | 1036.0724 | 1051.4135 | 51.1863 | 409.2516 | 86.1514 | 634.0078 | 14.6714 | 49.4974 | 48.6566 | 51.4354 | 74.3096 |  |  | 0.73093 | -0.24305 | -0.37468 | -1.0198 | 6.9873 | 4.7433 | 9.4341 | -2.626 | 21.2246 | 56.8695 | 39.9932 | 2.629e-05 | 0 | -0.00075897 | 33.329 | 16.7235 | 16.6839 | 17.0657 | 17.0901 | 16.0887 | 14.6791 | 16.6785 | 17.0409 | 17.396 | 17.4693 | 17.224 | 16.4135 | 14.7223 | 760.8011 | 532.5199 | 511.4879 | 297.7271 | 262.8606 | 754.189 | 455.4802 | 27.7745 | 45.818 | 51.5177 | 84.8788 | 87.2796 | 91.5839 |  |  |  | 645.7542 | 610.3119 | 611.0652 | 640.2522 | 92.3147 | 39.4688 | 914.6136 |  |  | 788.4111 |  |  | 23.6647 | 61.1186 | 606.7698 | 25.0237 | 63.8928 | 897.9508 | 732.1616 | 623.6292 | 897.5138 | 896.641 | 737.1815 |  | 826.9277 | 917.3415 | 1090.4734 | 606.2248 | 700.5899 | 928.6955 |  | 321.4654 |  |  | 475.8739 | 656.2834 | 729.9703 | [6 empty] | 615.1173 |  |  | 449.4605 |  |  | 542.312 | 691.2163 | 701.3159 | 1090.1123 | 1137.9644 | 1058.552 | 563.8191 | 735.3497 | 857.9588 | 640.2365 | 718.3111 | 1128.4831 | 1109.3153 | 651.0712 | 825.7396 | 965.5226 | 1076.9308 | 1097.4656 | 561.6392 | 678.4545 | 719.7864 | 582.1141 | 766.3203 | 885.0687 | 1025.3674 | 1128.8397 | 623.246 | 724.0864 | 680.3113 | 870.4651 | 103.9239 | -0.0007075 | 17.6965 | 4.8158 | -40.2479 | 3.121 | 9376.89 | 0.32 | 1.8544 | -1.0866 | -1.3492 | -2.2259 | 6.6654 | 5.4918 | 7.745 | 85.5309 | 200.8565 | 53.596 | 62.4247 | 9.7582 | 87.8153 | 40.5791
42810.4539 | 1200 | 17.4124 | 17.8349 | 17.9871 | 18.0412 | 17.3962 | 16.0678 | 15.2645 | 16.4646 | 16.9089 | 17.0723 | 17.0859 | 16.6281 | 15.6635 | 14.467 | 40.4394 | 57.9642 | 56.7173 | 90.1148 | 78.8973 | 93.8756 |  |  |  | 51.701 | 88.4429 | 547.5234 | 688.239 | 704.1441 | 695.0256 | 22.1263 | 59.5726 | 895.5057 | 22.421 | 58.0068 | 742.4435 | 832.1388 | 755.4727 |  | 252.2069 | 894.9569 | 881.7521 | 747.7026 |  | 484.2237 | 728.2867 | 578.4346 | 733.9871 | 913.4333 | 1038.7809 | 1054.4669 | 52.8608 | 408.9811 | 86.9263 | 634.3069 | 14.703 | 49.484 | 48.6539 | 51.4504 | 74.3235 |  |  | 1.4446 | -0.705 | -0.57116 | -1.0297 | 8.0544 | 6.0516 | 10.1537 | -3.862 | 21.2476 | 56.5571 | 42.3135 | -0.00010514 | -8.214e-05 | -0.0007754 | 33.4255 | 16.719 | 16.6921 | 17.0692 | 17.08 | 16.0884 | 14.6813 | 16.6756 | 17.0481 | 17.383 | 17.4636 | 17.2245 | 16.4157 | 14.7185 | 761.9049 | 535.5324 | 489.9688 | 299.8314 | 257.4597 | 755.78 | 456.4648 | 27.8816 | 45.9244 | 51.6225 | 84.9236 | 87.3145 | 91.6183 |  |  |  | 646.2798 | 610.6799 | 611.9338 | 641.5888 | 90.6465 | 36.0287 | 912.8694 |  |  | 785.9907 |  |  | 23.7106 | 61.2067 | 607.3665 | 25.0591 | 63.9934 | 893.592 | 736.4628 | 623.5592 | 893.0325 | 890.8276 | 740.8129 |  | 827.612 | 921.0671 | 1092.5462 | 605.4125 | 700.2896 | 935.1341 |  | 323.5276 |  |  | 475.9288 | 658.8314 | 732.0816 | [6 empty] | 614.8141 |  |  | 450.6143 |  |  | 541.5301 | 689.9375 | 700.5696 | 1085.0026 | 1135.0853 | 1058.5793 | 563.9415 | 736.1246 | 856.3979 | 639.5066 | 716.9958 | 1130.0687 | 1110.8463 | 651.6991 | 826.4772 | 961.9915 | 1080.0917 | 1098.6117 | 562.2382 | 679.6108 | 719.9424 | 581.7678 | 764.1065 | 881.7578 | 1029.144 | 1131.1598 | 623.5379 | 723.8121 | 678.9959 | 865.9981 | 102.3538 | -0.00021643 | 17.697 | 4.8017 | -40.2422 | 3.121 | 9317.22 | 0.28 | 2.6062 | -1.8517 | -1.6667 | -2.2379 | 7.1637 | 6.2095 | 8.0433 | 85.6558 | 202.0054 | 53.5473 | 62.871 | 12.3452 | 86.968 | 40.6492
42810.4539 | 1201 | 17.4052 | 17.8387 | 17.9855 | 18.0418 | 17.3987 | 16.0751 | 15.2725 | 16.4675 | 16.915 | 17.0701 | 17.0881 | 16.6211 | 15.6698 | 14.469 | 40.5959 | 58.1013 | 56.8487 | 90.1358 | 79.0074 | 93.9142 |  |  |  | 51.8774 | 88.4645 | 545.6404 | 686.2366 | 701.4643 | 693.12 | 22.2929 | 59.6465 | 892.6855 | 22.4629 | 57.9339 | 738.2989 | 830.5338 | 751.8285 |  | 250.911 | 891.501 | 879.253 | 728.6276 |  | 485.0414 | 729.016 | 577.6801 | 737.5181 | 918.4147 | 1039.8012 | 1056.9062 | 54.1262 | 408.6793 | 87.2379 | 634.634 | 14.7438 | 49.5317 | 48.6535 | 51.4517 | 74.3381 |  |  | 0.95107 | -1.6197 | -0.26691 | -0.86082 | 7.6976 | 5.7191 | 8.8716 | -3.3298 | 20.9752 | 55.776 | 39.0134 | -0.00014128 | -3.45e-05 | -0.00076554 | 33.5155 | 16.7301 | 16.682 | 17.0652 | 17.0853 | 16.0962 | 14.6789 | 16.6676 | 17.0412 | 17.382 | 17.4653 | 17.2103 | 16.4058 | 14.7129 | 754.0773 | 532.8268 | 494.2857 | 306.9931 | 265.4303 | 756.7372 | 457.3808 | 27.9796 | 46.0196 | 51.7144 | 84.9616 | 87.3348 | 91.658 |  |  |  | 646.7308 | 611.3492 | 612.6598 | 640.8531 | 83.1329 | 31.331 | 908.872 |  |  | 793.3344 |  |  | 23.768 | 61.2728 | 604.9514 | 25.1246 | 64.0526 | 891.1437 | 740.5231 | 622.2518 | 900.6198 | 900.8906 | 747.5265 |  | 828.776 | 925.8464 | 1092.8045 | 603.5035 | 699.8959 | 934.3756 |  | 325.5382 |  |  | 476.6555 | 665.4886 | 736.7465 | [6 empty] | 613.6353 |  |  | 450.4027 |  |  | 540.843 | 689.0591 | 699.7177 | 1084.9309 | 1139.0989 | 1056.8201 | 564.374 | 737.3089 | 855.093 | 639.2724 | 715.9844 | 1131.3976 | 1109.7634 | 652.4011 | 828.6502 | 963.0675 | 1082.089 | 1098.5706 | 562.1993 | 680.2263 | 719.3233 | 582.103 | 762.5983 | 878.8347 | 1029.9293 | 1134.5546 | 623.6972 | 723.496 | 678.4079 | 862.7822 | 106.1234 | 0.0014462 | 17.6963 | 4.7906 | -40.2229 | 3.1209 | 9294.65 | 0.26 | 2.1126 | -2.8077 | -1.1398 | -2.0469 | 7.006 | 6.0388 | 7.5213 | 85.8543 | 202.029 | 53.5071 | 64.0839 | 12.0482 | 86.9628 | 40.7617
42810.4539 | 1202 | 17.4102 | 17.8364 | 17.9914 | 18.0375 | 17.3925 | 16.07 | 15.2703 | 16.4591 | 16.9211 | 17.0689 | 17.0857 | 16.6207 | 15.6673 | 14.4673 | 40.7489 | 58.231 | 56.9883 | 90.161 | 79.1856 | 93.9627 |  |  |  | 52.049 | 88.4743 | 543.5166 | 683.9517 | 699.1239 | 691.1253 | 28.9004 | 60.3386 | 893.2461 | 22.3944 | 58.0702 | 736.2287 | 828.9219 | 750.3204 |  | 246.2035 | 893.5051 | 881.0397 | 677.688 |  | 485.7526 | 728.8264 | 577.3208 | 739.1104 | 914.0731 | 1035.3811 | 1056.9166 | 54.9307 | 408.2928 | 91.3328 | 635.1667 | 14.7615 | 49.628 | 48.6551 | 51.4683 | 74.3374 |  |  | 1.2067 | -1.4436 | 0.055732 | -0.61375 | 8.473 | 6.7199 | 10.2424 | -3.0104 | 20.8413 | 53.4499 | 38.6331 | -0.00011335 | -7.885e-05 | -0.00076718 | 33.602 | 16.7266 | 16.6771 | 17.0583 | 17.0807 | 16.0865 | 14.6732 | 16.6625 | 17.0333 | 17.3761 | 17.4573 | 17.2059 | 16.3992 | 14.7156 | 741.0207 | 518.9724 | 481.1458 | 297.4469 | 265.9466 | 756.6903 | 457.695 | 28.0823 | 46.1366 | 51.8297 | 85.0049 | 87.3677 | 91.7101 |  |  |  | 646.9698 | 611.161 | 612.5362 | 639.2088 | 88.3904 | 31.8555 | 916.4294 |  |  | 799.6909 |  |  | 23.8019 | 61.352 | 601.8909 | 25.1801 | 64.1152 | 893.537 | 746.4723 | 621.3443 | 903.4581 | 902.0487 | 754.9874 |  | 830.0813 | 934.3632 | 1095.3611 | 601.6304 | 699.402 | 940.0952 |  | 327.4159 |  |  | 478.4497 | 673.2605 | 741.637 | [6 empty] | 612.3068 |  |  | 449.7773 |  |  | 540.4381 | 688.6566 | 698.7164 | 1082.6508 | 1145.2069 | 1054.889 | 564.8677 | 739.041 | 855.1283 | 639.4236 | 714.8856 | 1132.7771 | 1107.8054 | 652.5402 | 833.8967 | 964.766 | 1083.6376 | 1100.0521 | 561.9304 | 680.8724 | 718.5302 | 582.6274 | 761.9972 | 877.9519 | 1030.3956 | 1135.7047 | 623.5093 | 723.2988 | 678.2522 | 860.8567 | 100.6807 | -0.00027255 | 17.6931 | 4.7863 | -40.2379 | 3.121 | 9374.88 | 0.33 | 2.3772 | -2.6504 | 0.52077 | -1.7282 | 7.338 | 6.5349 | 8.0679 | 86.0801 | 203.3454 | 53.4423 | 65.5179 | 13.5708 | 87.8426 | 40.8562
42810.454 | 1203 | 17.4218 | 17.8408 | 18.0037 | 18.0399 | 17.3982 | 16.078 | 15.2805 | 16.47 | 16.9238 | 17.0663 | 17.0955 | 16.6376 | 15.6658 | 14.4739 | 40.8932 | 58.3516 | 57.1078 | 90.1915 | 79.4697 | 94.0002 |  |  |  | 52.2086 | 88.4888 | 543.2318 | 683.1943 | 698.8375 | 690.7715 | 24.5164 | 63.2838 | 898.4945 | 24.2947 | 58.1112 | 736.1315 | 828.3408 | 750.6862 |  | 256.0895 | 892.1571 | 879.4316 | 648.961 |  | 486.1264 | 728.7296 | 577.6858 | 739.1024 | 912.6412 | 1036.8387 | 1058.6652 | 54.009 | 408.0978 | 94.4798 | 635.4953 | 14.7865 | 49.7021 | 48.6544 | 51.4882 | 74.2935 |  |  | 1.5418 | -0.77137 | 0.014336 | -0.72217 | 8.1372 | 6.3644 | 10.2463 | -3.4441 | 19.7297 | 52.9951 | 43.5742 | -4.107e-05 | 1.479e-05 | -0.00076061 | 33.7052 | 16.7348 | 16.6817 | 17.0606 | 17.086 | 16.0958 | 14.6791 | 16.6689 | 17.0431 | 17.3836 | 17.4675 | 17.2119 | 16.4085 | 14.7247 | 744.4001 | 514.0431 | 486.3852 | 284.0557 | 256.1252 | 757.4329 | 457.9748 | 28.1951 | 46.2462 | 51.9294 | 85.0309 | 87.4014 | 91.742 |  |  |  | 647.2272 | 611.1158 | 612.352 | 638.5303 | 91.3554 | 37.8431 | 919.6008 |  |  | 817.2776 |  |  | 23.8494 | 61.4215 | 600.7134 | 25.232 | 64.1779 | 891.9688 | 747.8256 | 620.1665 | 910.8668 | 910.9029 | 759.2675 |  | 830.9955 | 941.0225 | 1098.9548 | 599.9701 | 698.7453 | 937.5366 |  | 329.5322 |  |  | 479.5726 | 677.2937 | 745.2288 | [6 empty] | 611.2422 |  |  | 449.4923 |  |  | 540.3822 | 688.0659 | 697.9686 | 1084.4861 | 1145.9401 | 1054.4269 | 564.8815 | 741.6319 | 856.1849 | 639.4141 | 713.8911 | 1136.7624 | 1106.1856 | 651.989 | 836.1447 | 962.6746 | 1082.2123 | 1101.2139 | 561.6515 | 681.7504 | 717.6711 | 582.6569 | 761.2442 | 877.4377 | 1027.3143 | 1133.67 | 623.3259 | 723.2689 | 677.6901 | 858.8921 | 98.5727 | -0.00024451 | 17.6918 | 4.7758 | -40.2805 | 3.1209 | 9435 | 0.24 | 2.6866 | -1.9373 | 0.26411 | -1.8745 | 7.1951 | 6.3632 | 8.0739 | 86.2654 | 205.3575 | 53.3333 | 65.409 | 13.0446 | 88.4482 | 40.9277
42810.454 | 1204 | 17.4124 | 17.8306 | 17.9947 | 18.0306 | 17.4041 | 16.0754 | 15.2779 | 16.4717 | 16.9188 | 17.071 | 17.0861 | 16.6267 | 15.6682 | 14.4765 | 41.054 | 58.4864 | 57.2424 | 90.2378 | 79.6952 | 94.0172 |  |  |  | 52.3708 | 88.5138 | 544.5792 | 683.8256 | 699.8324 | 691.6709 | 23.4411 | 60.4147 | 892.6737 | 26.7972 | 60.2064 | 736.0774 | 827.6632 | 749.4365 |  | 254.1526 | 886.791 | 874.2214 | 649.874 |  | 486.7677 | 728.6791 | 577.3832 | 739.2455 | 914.6377 | 1033.3065 | 1056.4909 | 54.3361 | 407.8882 | 97.4398 | 635.7169 | 14.806 | 49.7671 | 48.6345 | 51.4883 | 74.1764 |  |  | 1.3861 | -0.59263 | -0.32539 | -1.0356 | 8.5683 | 5.5285 | 8.8946 | -3.9402 | 21.1696 | 56.1375 | 41.7813 | -0.00014292 | -8.707e-05 | -0.00074911 | 33.7974 | 16.7428 | 16.6708 | 17.0621 | 17.0826 | 16.0917 | 14.6856 | 16.6708 | 17.0444 | 17.3833 | 17.4662 | 17.2113 | 16.4073 | 14.7217 | 749.3469 | 506.0404 | 472.2463 | 279.4961 | 251.3594 | 758.0378 | 458.4174 | 28.3016 | 46.3579 | 52.0361 | 85.0747 | 87.4324 | 91.7973 |  |  |  | 647.4923 | 610.691 | 612.1918 | 637.6995 | 79.7781 | 22.3288 | 923.7807 |  |  | 809.786 |  |  | 23.8961 | 61.4867 | 602.366 | 25.2954 | 64.2706 | 886.9005 | 747.7393 | 620.4495 | 910.8665 | 912.1929 | 759.3617 |  | 831.7393 | 938.0044 | 1103.1014 | 599.9197 | 698.4239 | 938.3425 |  | 331.6887 |  |  | 479.0082 | 675.1774 | 745.8352 | [6 empty] | 611.27 |  |  | 450.0156 |  |  | 540.1772 | 687.6343 | 697.6714 | 1082.861 | 1152.3563 | 1056.1134 | 564.4047 | 742.403 | 856.4079 | 639.3097 | 713.4969 | 1138.0054 | 1110.6454 | 651.1822 | 834.183 | 959.3962 | 1077.0331 | 1099.2778 | 561.6672 | 682.7013 | 716.7298 | 582.3159 | 759.2994 | 875.3347 | 1023.8123 | 1129.2382 | 623.34 | 723.1296 | 676.652 | 856.1974 | 97.404 | -0.00055315 | 17.6906 | 4.768 | -40.3371 | 3.121 | 9450.45 | 0.28 | 2.5485 | -1.6981 | -1.2583 | -2.2447 | 7.3733 | 5.9227 | 7.5124 | 86.5108 | 207.9969 | 53.2589 | 65.0769 | 14.704 | 88.1988 | 41.0051
42810.454 | 1205 | 17.4106 | 17.8358 | 17.9882 | 18.0309 | 17.3955 | 16.0686 | 15.2722 | 16.4601 | 16.9232 | 17.0755 | 17.0933 | 16.6323 | 15.6667 | 14.4736 | 41.2088 | 58.6106 | 57.3742 | 90.2815 | 79.8332 | 94.0315 |  |  |  | 52.5345 | 88.5305 | 545.5929 | 684.1698 | 700.2069 | 692.0246 | 24.0186 | 60.7531 | 886.5684 | 23.0189 | 60.4062 | 735.6798 | 828.1922 | 752.6492 |  | 254.8017 | 882.0015 | 869.7538 | 692.8123 |  | 487.8494 | 728.7529 | 575.5535 | 736.4317 | 906.0326 | 1024.7448 | 1054.9919 | 55.6544 | 407.8997 | 97.2334 | 635.9814 | 14.8197 | 49.8151 | 48.6148 | 51.5095 | 74.0636 |  |  | 1.5228 | -0.65243 | -0.58758 | -1.054 | 7.7436 | 5.4635 | 9.7482 | -3.2056 | 21.2638 | 55.4699 | 38.6856 | -7.228e-05 | -6.407e-05 | -0.00077211 | 33.8882 | 16.7584 | 16.6824 | 17.072 | 17.0809 | 16.0907 | 14.6868 | 16.6746 | 17.0505 | 17.3855 | 17.4697 | 17.2161 | 16.4155 | 14.7249 | 743.7237 | 488.1144 | 422.7827 | 262.5615 | 234.3204 | 758.1621 | 457.9838 | 28.4048 | 46.4606 | 52.1347 | 85.1265 | 87.4751 | 91.8473 |  |  |  | 647.6349 | 610.3693 | 612.5713 | 637.3146 | 89.782 | 34.3377 | 925.3001 |  |  | 810.4135 |  |  | 23.9452 | 61.5641 | 604.3204 | 25.3545 | 64.3336 | 883.3935 | 747.9752 | 620.8791 | 908.4237 | 906.8229 | 758.9422 |  | 832.3603 | 936.8311 | 1106.4307 | 600.2502 | 698.2251 | 938.0251 |  | 333.6648 |  |  | 477.9573 | 671.922 | 745.7888 | [6 empty] | 611.7584 |  |  | 451.4998 |  |  | 539.6333 | 687.5564 | 697.7461 | 1085.766 | 1157.8313 | 1057.9569 | 563.7957 | 741.2056 | 855.7363 | 639.4969 | 714.0298 | 1140.6997 | 1114.3961 | 650.3911 | 831.6676 | 960.5546 | 1071.9038 | 1099.8077 | 561.3532 | 683.0737 | 715.994 | 581.7213 | 757.3129 | 873.2429 | 1019.2524 | 1123.2273 | 622.9735 | 723.1592 | 675.7829 | 855.5025 | 100.8598 | -0.00027255 | 17.6899 | 4.7604 | -40.2624 | 3.1209 | 9429.47 | 0.36 | 2.6717 | -1.7817 | -1.6909 | -2.2647 | 6.9865 | 5.8684 | 7.8388 | 86.7298 | 210.0974 | 53.2029 | 65.7464 | 20.1133 | 87.1809 | 41.0449
42810.454 | 1206 | 17.4091 | 17.8339 | 17.9861 | 18.0252 | 17.3918 | 16.0635 | 15.2728 | 16.4665 | 16.9131 | 17.0701 | 17.0899 | 16.6191 | 15.6685 | 14.4655 | 41.3585 | 58.7357 | 57.5006 | 90.3065 | 80.0059 | 94.0462 |  |  |  | 52.7055 | 88.5456 | 546.3992 | 684.2873 | 700.4253 | 691.9486 | 22.5909 | 60.4889 | 885.0502 | 26.2463 | 60.9376 | 734.5294 | 827.2328 | 749.0443 |  | 247.8491 | 882.7529 | 870.9401 | 664.4462 |  | 487.5948 | 726.2059 | 573.093 | 735.9429 | 900.4579 | 1018.6161 | 1053.2075 | 56.1088 | 408.0461 | 97.0779 | 636.1547 | 14.8393 | 49.8304 | 48.6108 | 51.5446 | 73.8887 |  |  | 1.5083 | -1.023 | -0.86751 | -1.3445 | 8.2141 | 6.0903 | 9.925 | -3.4862 | 20.4509 | 56.0552 | 37.089 | -6.9e-05 | -9.528e-05 | -0.00077868 | 33.9826 | 16.7621 | 16.6906 | 17.0744 | 17.0822 | 16.0871 | 14.6873 | 16.6812 | 17.0454 | 17.3879 | 17.4722 | 17.2175 | 16.411 | 14.7254 | 754.2033 | 501.7145 | 460.5968 | 278.7935 | 243.0527 | 758.875 | 458.4602 | 28.5023 | 46.5641 | 52.229 | 85.1738 | 87.5097 | 91.8974 |  |  |  | 647.9174 | 610.7911 | 613.2667 | 639.1707 | 73.6188 | 33.6935 | 922.4675 |  |  | 802.5683 |  |  | 23.9838 | 61.6234 | 605.0987 | 25.3811 | 64.3829 | 881.8944 | 748.85 | 620.0621 | 904.8827 | 903.7009 | 759.635 |  | 833.1573 | 932.1146 | 1109.697 | 600.0363 | 697.817 | 933.2246 |  | 335.6123 |  |  | 477.6743 | 669.7876 | 746.2836 | [6 empty] | 611.4257 |  |  | 452.6909 |  |  | 539.0085 | 687.4428 | 698.2235 | 1093.6087 | 1159.5604 | 1060.5627 | 563.2257 | 739.94 | 855.7005 | 639.2617 | 714.837 | 1139.1773 | 1117.0807 | 649.7519 | 829.2715 | 956.0142 | 1066.6847 | 1099.3387 | 560.9232 | 682.9056 | 715.4444 | 581.0253 | 756.9434 | 872.18 | 1014.9669 | 1117.5482 | 622.9403 | 723.0453 | 675.04 | 855.2272 | 98.1451 | 0.0003097 | 17.6889 | 4.7597 | -40.2194 | 3.1209 | 9354.38 | 0.23 | 2.6589 | -2.2283 | -2.0519 | -2.5545 | 7.1786 | 6.1813 | 7.8908 | 86.9772 | 212.2712 | 53.1127 | 64.8388 | 16.0069 | 87.6519 | 41.0513
42810.454 | 1207 | 17.4051 | 17.8301 | 17.9796 | 18.0263 | 17.3852 | 16.069 | 15.2807 | 16.452 | 16.9082 | 17.0643 | 17.0886 | 16.6161 | 15.6568 | 14.4698 | 41.5192 | 58.8718 | 57.6378 | 90.3291 | 80.1574 | 94.0374 |  |  |  | 52.8761 | 88.5627 | 547.2007 | 684.423 | 700.6408 | 691.7816 | 23.4238 | 60.1206 | 886.6267 | 31.2779 | 65.0762 | 736.3996 | 828.6647 | 748.9659 |  | 240.5346 | 885.7526 | 874.5863 | 661.4143 |  | 484.4554 | 722.7624 | 572.4188 | 735.4064 | 899.0517 | 1020.2807 | 1054.3028 | 55.0165 | 408.1109 | 97.2456 | 636.4593 | 14.8451 | 49.8498 | 48.616 | 51.5786 | 73.6192 |  |  | 1.2356 | -1.8398 | -0.32211 | -1.0461 | 7.6424 | 6.6877 | 10.5644 | -3.4145 | 20.3785 | 54.586 | 46.2781 | -7.885e-05 | -5.585e-05 | -0.00076225 | 34.0626 | 16.7581 | 16.6766 | 17.0568 | 17.0789 | 16.0892 | 14.6771 | 16.6722 | 17.0376 | 17.3767 | 17.4641 | 17.2117 | 16.4028 | 14.717 | 727.0496 | 495.0623 | 462.0154 | 289.4576 | 240.4354 | 758.3721 | 458.8342 | 28.6393 | 46.688 | 52.361 | 85.2143 | 87.5554 | 91.964 |  |  |  | 648.0773 | 610.0289 | 612.5992 | 636.6501 | 107.2022 | 35.4626 | 920.8993 |  |  | 801.3192 |  |  | 24.031 | 61.7072 | 606.0777 | 25.4538 | 64.4731 | 883.5501 | 749.2764 | 619.8912 | 905.2068 | 904.5266 | 759.282 |  | 834.1289 | 931.6939 | 1116.7462 | 599.8339 | 697.5408 | 933.1593 |  | 336.4425 |  |  | 476.8282 | 668.6526 | 747.1985 | [6 empty] | 610.9935 |  |  | 453.1144 |  |  | 538.1841 | 687.1827 | 698.5426 | 1094.5837 | 1157.7666 | 1066.181 | 562.8517 | 739.4728 | 855.6177 | 638.6515 | 714.9681 | 1137.3271 | 1125.0407 | 649.6295 | 828.3243 | 952.7548 | 1061.0067 | 1096.8189 | 560.8131 | 682.564 | 714.9191 | 580.6412 | 756.5819 | 870.4084 | 1009.4255 | 1113.4191 | 623.3078 | 722.7991 | 674.3843 | 853.6692 | 94.5265 | -0.00032867 | 17.6879 | 4.7523 | -40.2859 | 3.1209 | 9262.55 | 0.36 | 2.4063 | -2.9831 | -1.2482 | -2.2494 | 6.9287 | 6.4815 | 8.1463 | 87.3127 | 216.7388 | 53.0533 | 67.6747 | 15.9241 | 88.2095 | 41.1541
42810.454 | 1208 | 17.4099 | 17.829 | 17.9882 | 18.0282 | 17.3891 | 16.0663 | 15.284 | 16.4526 | 16.9141 | 17.0656 | 17.0848 | 16.621 | 15.6628 | 14.4701 | 41.6599 | 58.986 | 57.7519 | 90.3345 | 80.2531 | 94.0644 |  |  |  | 53.0336 | 88.554 | 548.1694 | 684.5493 | 700.9014 | 691.7464 | 23.1484 | 60.1295 | 881.4737 | 22.594 | 58.6071 | 729.4895 | 824.3974 | 744.3893 |  | 252.4555 | 878.3864 | 867.0497 | 739.0536 |  | 482.8007 | 721.1888 | 571.7937 | 731.0569 | 903.3876 | 1024.0139 | 1054.5555 | 53.6994 | 408.0877 | 97.1282 | 636.6093 | 14.8128 | 49.8523 | 48.6278 | 51.6061 | 73.1189 |  |  | 1.5668 | -0.51575 | 0.12013 | -0.88382 | 7.6523 | 5.8229 | 10.5092 | -3.0945 | 20.6054 | 55.1894 | 46.9515 | -9.364e-05 | -7.228e-05 | -0.00079675 | 34.1715 | 16.7623 | 16.6792 | 17.059 | 17.0722 | 16.083 | 14.6868 | 16.6703 | 17.04 | 17.3896 | 17.4668 | 17.214 | 16.409 | 14.7211 | 753.7125 | 517.7513 | 483.3822 | 296.9785 | 240.9715 | 760.8035 | 459.6603 | 28.7497 | 46.7945 | 52.4489 | 85.2578 | 87.5905 | 92.0144 |  |  |  | 648.0289 | 608.3057 | 610.9432 | 634.2766 | 97.7468 | 43.1731 | 922.382 |  |  | 801.1475 |  |  | 24.0741 | 61.7705 | 606.7996 | 25.5182 | 64.5418 | 881.8037 | 747.1489 | 620.6337 | 905.9093 | 906.1065 | 755.2855 |  | 834.8704 | 932.4296 | 1121.9155 | 599.5 | 697.5261 | 922.3201 |  | 337.4447 |  |  | 475.9721 | 664.9732 | 745.5574 | [6 empty] | 611.3932 |  |  | 451.8037 |  |  | 537.785 | 687.3244 | 698.221 | 1093.4046 | 1151.4441 | 1072.0124 | 562.6113 | 739.6086 | 856.076 | 638.3639 | 714.5232 | 1137.24 | 1126.4699 | 649.5648 | 828.6562 | 953.7458 | 1056.9943 | 1097.2898 | 561.0512 | 683.068 | 714.7523 | 580.6422 | 755.8507 | 870.8459 | 1005.3624 | 1111.4701 | 623.8466 | 722.9522 | 673.9711 | 853.2546 | 84.9439 | 0.00038689 | 17.6871 | 4.7447 | -40.3579 | 3.1209 | 9156.83 | 0.29 | 2.7096 | -1.5782 | 0.76166 | -2.0659 | 6.9432 | 6.0567 | 8.1367 | 87.6729 | 220.0275 | 53.0591 | 65.5897 | 13.7154 | 84.6473 | 41.2101
42810.454 | 1209 | 17.4108 | 17.8337 | 17.9904 | 18.0284 | 17.3926 | 16.0696 | 15.2869 | 16.4644 | 16.9206 | 17.0721 | 17.0932 | 16.6295 | 15.6637 | 14.4694 | 41.8169 | 59.1078 | 57.8868 | 90.329 | 80.5513 | 94.08 |  |  |  | 53.1791 | 88.57 | 548.9381 | 684.9927 | 701.0309 | 692.3221 | 23.3834 | 60.1446 | 879.5879 | 22.6505 | 58.4516 | 726.9627 | 821.9749 | 741.4102 |  | 253.8125 | 875.0036 | 862.6119 | 737.4444 |  | 484.0336 | 721.665 | 574.8902 | 729.5133 | 907.2987 | 1028.7694 | 1053.2012 | 51.4782 | 408.2542 | 93.313 | 636.687 | 14.8163 | 49.861 | 48.6413 | 51.6464 | 72.3364 |  |  | 1.4518 | -0.50195 | 0.45263 | -0.13668 | 7.852 | 6.413 | 10.9606 | -2.5984 | 21.574 | 57.2467 | 58.377 | -7.064e-05 | -0.00010349 | -0.00074418 | 34.2698 | 16.7754 | 16.6774 | 17.0545 | 17.0745 | 16.0891 | 14.6807 | 16.6813 | 17.0388 | 17.3886 | 17.4691 | 17.2175 | 16.4142 | 14.7338 | 757.6632 | 532.4536 | 501.5517 | 313.8135 | 261.3559 | 762.9385 | 461.1528 | 28.8485 | 46.8977 | 52.5422 | 85.2832 | 87.616 | 92.0559 |  |  |  | 647.9584 | 607.3643 | 609.5103 | 632.6219 | 97.6075 | 45.5461 | 922.487 |  |  | 803.8862 |  |  | 24.1174 | 61.8384 | 607.8249 | 25.5544 | 64.6028 | 878.9305 | 744.0729 | 621.6206 | 907.7929 | 906.8939 | 750.3108 |  | 835.2265 | 928.067 | 1124.442 | 599.5873 | 697.6007 | 918.6615 |  | 338.8032 |  |  | 474.4164 | 662.6585 | 743.174 | [6 empty] | 612.1121 |  |  | 450.1867 |  |  | 537.7049 | 686.8525 | 697.5397 | 1096.4718 | 1144.2789 | 1073.5475 | 562.1227 | 738.8192 | 855.2291 | 637.9097 | 713.5542 | 1136.6156 | 1123.7308 | 648.8647 | 826.8617 | 949.6727 | 1054.8612 | 1096.6268 | 561.5485 | 683.714 | 714.2616 | 580.4586 | 754.4722 | 870.5496 | 1003.0709 | 1112.2166 | 623.8314 | 722.9049 | 673.3111 | 850.702 | 84.4516 | -0.0007075 | 17.6864 | 4.7416 | -40.3145 | 3.1209 | 9112.9 | 0.32 | 2.6091 | -1.5573 | 1.4788 | -0.81262 | 7.0461 | 6.3678 | 8.3248 | 87.9309 | 221.7788 | 53.0743 | 65.9248 | 11.996 | 83.9006 | 41.2416
42810.454 | 1210 | 17.4084 | 17.8278 | 17.983 | 18.0256 | 17.3898 | 16.0639 | 15.2908 | 16.4688 | 16.9143 | 17.0633 | 17.0934 | 16.6288 | 15.6643 | 14.4661 | 41.9622 | 59.2369 | 58.019 | 90.3028 | 80.759 | 94.1247 |  |  |  | 53.34 | 88.569 | 548.2129 | 684.1084 | 699.7603 | 691.4383 | 22.9324 | 60.2472 | 876.3493 | 22.6782 | 58.521 | 726.7462 | 821.0495 | 741.2978 |  | 262.5405 | 871.8587 | 859.5014 | 738.8351 |  | 483.6131 | 723.1836 | 576.8132 | 731.7173 | 907.4488 | 1032.785 | 1052.5418 | 50.147 | 408.4509 | 88.2482 | 636.7339 | 14.8345 | 49.8688 | 48.6537 | 51.6471 | 71.4134 |  |  | 1.3046 | -0.59789 | 0.23513 | -1.2045 | 7.8888 | 6.0411 | 9.5583 | -4.05 | 21.7682 | 57.266 | 70.7411 | -0.00011664 | -3.778e-05 | -0.00079182 | 34.3572 | 16.7747 | 16.6787 | 17.0598 | 17.0709 | 16.084 | 14.6764 | 16.6782 | 17.0385 | 17.3841 | 17.4663 | 17.2155 | 16.4117 | 14.7278 | 769.6328 | 550.1818 | 508.9339 | 310.9834 | 259.3459 | 765.1504 | 462.7817 | 28.9506 | 46.9969 | 52.6476 | 85.3129 | 87.6397 | 92.0861 |  |  |  | 647.9433 | 607.4015 | 609.2181 | 632.1695 | 95.2097 | 35.2653 | 921.828 |  |  | 797.168 |  |  | 24.168 | 61.9034 | 606.8751 | 25.6282 | 64.678 | 874.3093 | 736.7514 | 622.2095 | 901.5556 | 899.8022 | 740.8797 |  | 834.0824 | 923.6069 | 1125.3454 | 599.4992 | 697.5592 | 924.0899 |  | 340.7698 |  |  | 472.8071 | 654.7888 | 736.6133 | [6 empty] | 612.3206 |  |  | 449.5893 |  |  | 537.6091 | 686.0929 | 696.9262 | 1093.0254 | 1134.7569 | 1073.8156 | 562.0345 | 737.2364 | 853.3298 | 636.9907 | 712.8857 | 1138.6388 | 1123.9707 | 648.9932 | 825.9208 | 944.6873 | 1056.3386 | 1097.1001 | 561.9086 | 683.668 | 714.1252 | 580.6143 | 752.9619 | 869.0073 | 1004.2544 | 1115.5316 | 624.2941 | 723.3374 | 672.9642 | 848.438 | 98.3103 | -0.0030436 | 17.685 | 4.7343 | -40.3112 | 3.121 | 9107.92 | 0.31 | 2.4722 | -1.7009 | 1.0666 | -2.4142 | 7.0735 | 6.1899 | 7.7861 | 87.8083 | 222.4877 | 53.0669 | 65.4004 | 11.5035 | 83.561 | 41.2511
42810.4541 | 1211 | 17.4011 | 17.8301 | 17.9782 | 18.0299 | 17.3921 | 16.0628 | 15.2967 | 16.4712 | 16.9173 | 17.0695 | 17.0959 | 16.6297 | 15.67 | 14.4643 | 42.1329 | 59.3738 | 58.1577 | 90.3113 | 80.987 | 94.1862 |  |  |  | 53.4994 | 88.6018 | 547.9685 | 683.1852 | 698.796 | 690.4502 | 22.599 | 60.3112 | 874.7378 | 22.9776 | 58.7177 | 729.7658 | 820.9743 | 745.4122 |  | 271.1327 | 873.7921 | 861.0785 | 745.2419 |  | 483.2844 | 723.1961 | 576.93 | 733.6732 | 907.8956 | 1032.452 | 1051.0069 | 49.9826 | 408.7573 | 85.236 | 636.5229 | 14.829 | 49.8443 | 48.6612 | 51.6608 | 70.4675 |  |  | 1.0089 | 0.021115 | -0.36679 | -1.125 | 7.3664 | 4.8951 | 8.6298 | -3.728 | 22.3362 | 56.8412 | 54.6567 | -5.75e-05 | -5.585e-05 | -0.00078361 | 34.4566 | 16.7779 | 16.6763 | 17.0577 | 17.0709 | 16.0824 | 14.6804 | 16.6747 | 17.0379 | 17.3821 | 17.4635 | 17.218 | 16.4138 | 14.7252 | 755.9283 | 527.477 | 455.5822 | 323.1015 | 260.1167 | 766.7139 | 463.9321 | 29.0561 | 47.0896 | 52.7431 | 85.3445 | 87.6626 | 92.1237 |  |  |  | 647.8472 | 606.9794 | 609.6065 | 630.2759 | 92.1111 | 35.9084 | 916.8539 |  |  | 794.9651 |  |  | 24.2098 | 61.9801 | 605.8715 | 25.686 | 64.775 | 874.613 | 734.9483 | 624.3843 | 896.7417 | 895.36 | 736.6438 |  | 833.4033 | 917.7585 | 1124.0303 | 599.7344 | 697.5982 | 919.2565 |  | 342.6912 |  |  | 472.8659 | 651.811 | 731.7895 | [6 empty] | 614.0407 |  |  | 449.4768 |  |  | 537.5813 | 685.7968 | 696.2524 | 1099.6783 | 1132.3814 | 1072.1185 | 562.6762 | 737.9901 | 854.721 | 637.0414 | 712.7905 | 1139.2928 | 1120.2615 | 649.8803 | 830.5587 | 948.2809 | 1059.0607 | 1097.2229 | 561.637 | 683.535 | 713.7812 | 581.0347 | 753.1783 | 872.3344 | 1005.1555 | 1119.6381 | 624.27 | 722.6369 | 673.378 | 850.9482 | 99.2662 | -0.0025034 | 17.6848 | 4.7335 | -40.3196 | 3.1209 | 9178.74 | 0.27 | 2.1729 | 0.31964 | -1.3322 | -2.3332 | 6.8344 | 5.5712 | 7.3973 | 87.6982 | 221.799 | 53.0696 | 67.4947 | 17.6636 | 83.3586 | 41.284
42810.4541 | 1212 | 17.402 | 17.8314 | 17.9872 | 18.03 | 17.3985 | 16.0711 | 15.3087 | 16.4742 | 16.9132 | 17.0736 | 17.0913 | 16.6147 | 15.6674 | 14.4694 | 42.2741 | 59.4913 | 58.2819 | 90.3294 | 80.9813 | 94.2236 |  |  |  | 53.6632 | 88.6196 | 549.6608 | 683.5903 | 699.5293 | 690.454 | 22.67 | 60.413 | 877.4631 | 22.9526 | 61.7438 | 735.2579 | 822.1205 | 751.6661 |  | 268.7678 | 874.2051 | 861.0037 | 749.5228 |  | 481.7078 | 723.1491 | 575.5996 | 732.3073 | 900.8175 | 1027.6082 | 1050.1503 | 50.24 | 409.0741 | 81.0945 | 636.1001 | 14.8303 | 49.8553 | 48.6685 | 51.6647 | 69.5479 |  |  | 1.1725 | -0.39221 | -0.52384 | -1.4102 | 8.8114 | 5.9156 | 9.99 | -3.4986 | 20.7619 | 54.9039 | 45.8134 | -0.00012649 | -0.00010678 | -0.00078032 | 34.5519 | 16.7825 | 16.6728 | 17.0581 | 17.0692 | 16.0837 | 14.6769 | 16.675 | 17.0339 | 17.3836 | 17.4692 | 17.2139 | 16.4107 | 14.7276 | 747.5536 | 529.9336 | 465.0238 | 320.7464 | 263.1894 | 767.4125 | 464.8791 | 29.1863 | 47.2116 | 52.8512 | 85.3902 | 87.7006 | 92.1841 |  |  |  | 647.624 | 605.361 | 608.8471 | 627.9405 | 72.3272 | 26.0448 | 913.2922 |  |  | 796.9201 |  |  | 24.2602 | 62.0543 | 606.774 | 25.7406 | 64.83 | 876.877 | 740.4115 | 624.8361 | 897.4591 | 896.5429 | 741.7631 |  | 834.1123 | 920.2167 | 1121.9787 | 599.6166 | 697.6712 | 923.5362 |  | 344.5786 |  |  | 473.7246 | 657.9487 | 735.224 | [6 empty] | 614.7513 |  |  | 449.6997 |  |  | 537.6095 | 686.0963 | 696.0327 | 1101.7655 | 1130.5737 | 1072.5494 | 563.0153 | 737.1859 | 859.3958 | 637.1283 | 714.2275 | 1141.0357 | 1122.7136 | 649.2764 | 831.7139 | 951.5076 | 1061.732 | 1097.6827 | 560.9898 | 682.3319 | 713.3503 | 581.2122 | 755.2943 | 875.7765 | 1007.7035 | 1120.7816 | 624.0394 | 721.7829 | 674.289 | 857.6759 | 88.6647 | 8.0602e-06 | 17.6851 | 4.7332 | -40.2946 | 3.1209 | 9203.67 | 0.27 | 2.3425 | -1.3776 | -1.5921 | -2.6121 | 7.4609 | 6.1131 | 7.9442 | 87.7938 | 220.4074 | 53.09 | 68.6812 | 16.8059 | 83.6126 | 41.3031
42810.4541 | 1213 | 17.4027 | 17.8334 | 17.9936 | 18.0403 | 17.3966 | 16.0759 | 15.3057 | 16.4801 | 16.9164 | 17.068 | 17.0928 | 16.6291 | 15.6742 | 14.4736 | 42.4194 | 59.6049 | 58.4008 | 90.3646 | 81.1309 | 94.2163 |  |  |  | 53.8172 | 88.6368 | 551.6948 | 685.1269 | 701.616 | 691.9071 | 22.724 | 60.6505 | 877.937 | 22.8959 | 58.7987 | 736.1731 | 823.3461 | 753.5545 |  | 254.5507 | 877.2604 | 863.2966 | 748.3722 |  | 480.2224 | 721.1693 | 574.3324 | 729.2895 | 895.9573 | 1027.4702 | 1049.9826 | 50.5301 | 409.09 | 79.726 | 635.6602 | 14.8248 | 49.8576 | 48.6517 | 51.6676 | 68.6798 |  |  | 1.277 | -1.096 | -0.3727 | -0.98042 | 7.3875 | 6.6121 | 10.2903 | -3.155 | 20.9933 | 54.3794 | 43.1462 | -7.721e-05 | -0.00010678 | -0.00074582 | 34.6371 | 16.79 | 16.6783 | 17.0589 | 17.0729 | 16.0861 | 14.6892 | 16.6772 | 17.029 | 17.3855 | 17.468 | 17.217 | 16.4061 | 14.734 | 733.7352 | 523.9466 | 452.1099 | 308.8328 | 263.4308 | 766.8881 | 464.8049 | 29.2828 | 47.3164 | 52.9546 | 85.444 | 87.7383 | 92.233 |  |  |  | 647.5027 | 604.0741 | 607.5868 | 628.3362 | 93.3119 | 38.0415 | 914.3585 |  |  | 805.4369 |  |  | 24.3015 | 62.1171 | 608.5778 | 25.8094 | 64.8896 | 879.84 | 742.9262 | 627.0158 | 903.0513 | 901.4302 | 747.7518 |  | 834.3245 | 933.7768 | 1122.2254 | 600.7687 | 698.0292 | 933.2274 |  | 346.5628 |  |  | 475.0791 | 664.9832 | 739.6222 | [6 empty] | 616.62 |  |  | 450.8306 |  |  | 537.383 | 686.5313 | 696.6658 | 1104.3 | 1130.1779 | 1071.8578 | 562.3406 | 736.6424 | 860.8067 | 637.3444 | 715.0317 | 1141.9558 | 1121.3308 | 648.6993 | 830.7622 | 951.6795 | 1064.3502 | 1099.1905 | 560.9033 | 681.2362 | 713.3956 | 581.2229 | 756.6261 | 878.0037 | 1009.0599 | 1120.8598 | 623.9662 | 720.96 | 674.3647 | 858.8535 | 89.5786 | -0.00020241 | 17.6858 | 4.7325 | -40.303 | 3.121 | 9259.44 | 0.29 | 2.4465 | -2.3005 | -1.3416 | -2.1759 | 6.8311 | 6.4627 | 8.0623 | 87.6987 | 220.1896 | 53.1423 | 70.0243 | 18.2258 | 84.0444 | 41.2673
42810.4541 | 1214 | 17.4112 | 17.8348 | 17.9931 | 18.0459 | 17.3996 | 16.071 | 15.3205 | 16.4749 | 16.92 | 17.0731 | 17.0928 | 16.6371 | 15.6694 | 14.4739 | 42.5694 | 59.7222 | 58.5248 | 90.3896 | 81.0816 | 94.2105 |  |  |  | 53.9735 | 88.6608 | 554.7743 | 687.3083 | 704.2394 | 694.2531 | 22.7504 | 60.5471 | 883.0072 | 23.0146 | 58.9513 | 736.1885 | 822.5958 | 752.5705 |  | 256.1141 | 882.2671 | 867.5484 | 747.9341 |  | 480.7157 | 720.4868 | 572.2289 | 729.1544 | 902.5203 | 1032.0256 | 1051.6781 | 50.6249 | 409.1591 | 80.6771 | 635.5855 | 14.7998 | 49.8758 | 48.6387 | 51.6921 | 67.8677 |  |  | 0.80321 | -0.54335 | 0.13262 | -0.59469 | 7.3487 | 5.9044 | 10.3771 | -3.6136 | 21.14 | 56.6013 | 45.0476 | -0.00011992 | -5.421e-05 | -0.0007524 | 34.731 | 16.8062 | 16.683 | 17.0625 | 17.0781 | 16.0923 | 14.6908 | 16.6772 | 17.0352 | 17.3842 | 17.4665 | 17.2193 | 16.4099 | 14.7305 | 756.8355 | 540.7625 | 512.1922 | 322.1211 | 276.5591 | 768.2484 | 465.9255 | 29.3865 | 47.4158 | 53.0444 | 85.4745 | 87.778 | 92.2793 |  |  |  | 647.3709 | 603.5003 | 606.8731 | 629.4219 | 98.2436 | 51.4548 | 919.4638 |  |  | 809.4626 |  |  | 24.342 | 62.1843 | 612.2631 | 25.8636 | 64.9496 | 887.1118 | 741.8911 | 631.3951 | 905.3835 | 902.7699 | 747.3093 |  | 833.8186 | 936.5663 | 1122.1969 | 605.081 | 698.6133 | 930.576 |  | 348.5875 |  |  | 475.6725 | 666.8589 | 739.7747 | [6 empty] | 620.7995 |  |  | 453.358 |  |  | 536.9471 | 686.3206 | 696.3903 | 1100.8191 | 1132.1824 | 1070.8223 | 562.1615 | 736.6272 | 860.8473 | 637.7691 | 714.6535 | 1143.3564 | 1121.5217 | 648.2689 | 830.0689 | 949.665 | 1063.8967 | 1097.5059 | 560.6381 | 680.3218 | 714.015 | 580.7548 | 756.6431 | 877.3098 | 1008.3319 | 1121.9095 | 623.6338 | 721.4757 | 673.8751 | 860.8587 | 97.6345 | -0.00056021 | 17.687 | 4.7317 | -40.3082 | 3.121 | 9361.84 | 0.25 | 1.9426 | -1.6193 | 0.79998 | -1.694 | 6.8251 | 6.1177 | 8.1103 | 87.5412 | 220.0937 | 53.1602 | 67.9566 | 11.7768 | 83.8116 | 41.2101
42810.4541 | 1215 | 17.4019 | 17.8296 | 17.9858 | 18.0271 | 17.389 | 16.0621 | 15.312 | 16.4692 | 16.9129 | 17.0656 | 17.0904 | 16.6281 | 15.6625 | 14.4749 | 42.7201 | 59.8499 | 58.6426 | 90.4063 | 80.9443 | 94.2268 |  |  |  | 54.1181 | 88.6697 | 555.5931 | 687.9062 | 704.4199 | 694.9586 | 22.7911 | 60.5237 | 885.787 | 22.909 | 58.9021 | 735.4854 | 822.2713 | 751.0011 |  | 263.7448 | 883.5939 | 868.8547 | 746.4352 |  | 481.6746 | 721.435 | 571.5897 | 731.5977 | 908.9455 | 1037.1872 | 1054.1062 | 49.4724 | 409.3363 | 83.6821 | 635.8906 | 14.7571 | 49.8767 | 48.6386 | 51.7101 | 67.1144 |  |  | 1.1298 | -0.25356 | 0.11224 | -0.90156 | 8.1267 | 6.1232 | 10.9139 | -3.6399 | 20.9106 | 55.6766 | 50.583 | -5.914e-05 | -0.00012157 | -0.00077375 | 34.8348 | 16.8123 | 16.6765 | 17.0615 | 17.0746 | 16.0862 | 14.6842 | 16.6714 | 17.0443 | 17.3865 | 17.4693 | 17.2238 | 16.4055 | 14.7289 | 784.1177 | 558.6553 | 520.2618 | 325.4827 | 280.0448 | 769.9917 | 467.6196 | 29.4988 | 47.5146 | 53.139 | 85.5081 | 87.819 | 92.3195 |  |  |  | 647.3897 | 604.3702 | 607.3623 | 630.3552 | 95.2129 | 35.8265 | 920.6453 |  |  | 809.3532 |  |  | 24.3866 | 62.245 | 614.1003 | 25.9226 | 65.0247 | 889.4657 | 741.4051 | 634.1393 | 902.3759 | 899.4483 | 746.1185 |  | 833.7608 | 932.5329 | 1119.7249 | 608.7109 | 698.9642 | 933.9806 |  | 350.448 |  |  | 475.707 | 665.4668 | 738.9144 | [6 empty] | 624.2842 |  |  | 457.3188 |  |  | 536.7232 | 685.8776 | 695.7356 | 1104.2913 | 1138.6116 | 1070.7778 | 562.3644 | 736.9706 | 859.4911 | 637.7902 | 714.1625 | 1149.3426 | 1119.336 | 648.5381 | 830.3214 | 945.5904 | 1062.0817 | 1096.3554 | 560.3018 | 679.6074 | 714.5809 | 580.1811 | 756.7176 | 876.3001 | 1005.913 | 1120.4136 | 623.5566 | 722.7011 | 673.5666 | 862.1539 | 96.8703 | -0.00078469 | 17.6872 | 4.7315 | -40.3222 | 3.121 | 9426.29 | 0.31 | 2.3048 | -1.1067 | 0.73632 | -2.0868 | 7.1914 | 6.2423 | 8.3339 | 87.5549 | 218.618 | 53.1422 | 65.5666 | 11.2241 | 83.7475 | 41.1881
42810.4541 | 1216 | 17.3941 | 17.8264 | 17.9738 | 18.0233 | 17.3791 | 16.0506 | 15.3172 | 16.4697 | 16.9046 | 17.0624 | 17.0871 | 16.6221 | 15.6603 | 14.4685 | 42.8698 | 59.9712 | 58.7725 | 90.4027 | 80.9194 | 94.267 |  |  |  | 54.2627 | 88.687 | 554.0762 | 686.5805 | 702.0041 | 693.7823 | 23.1225 | 60.5915 | 887.1503 | 22.9519 | 58.956 | 732.9624 | 821.4302 | 748.2492 |  | 261.4233 | 885.6222 | 870.6405 | 743.8252 |  | 483.3705 | 722.1378 | 571.559 | 734.5323 | 914.3989 | 1038.7854 | 1054.6027 | 46.7792 | 409.5223 | 85.8934 | 636.1918 | 14.8017 | 49.8816 | 48.6568 | 51.7188 | 66.4556 |  |  | 1.3499 | -0.45595 | -0.11906 | -0.6972 | 8.0518 | 5.7099 | 10.1655 | -3.7227 | 20.9343 | 56.8722 | 42.6906 | -0.00010678 | -7.228e-05 | -0.00078525 | 34.9359 | 16.8243 | 16.6755 | 17.0578 | 17.0751 | 16.0914 | 14.6864 | 16.6821 | 17.0468 | 17.3815 | 17.4619 | 17.2232 | 16.4116 | 14.7293 | 774.2227 | 540.804 | 481.6202 | 308.8421 | 269.4065 | 771.1102 | 468.274 | 29.6135 | 47.6329 | 53.2516 | 85.5773 | 87.8638 | 92.3628 |  |  |  | 647.394 | 604.8118 | 607.6687 | 632.6005 | 102.6652 | 31.0824 | 918.6093 |  |  | 808.9904 |  |  | 24.4373 | 62.3211 | 612.221 | 25.9757 | 65.1196 | 891.4961 | 742.4583 | 635.5173 | 900.3689 | 896.7814 | 746.9875 |  | 834.0478 | 930.0037 | 1118.2831 | 609.8863 | 699.1182 | 939.0918 |  | 352.369 |  |  | 475.0502 | 663.5637 | 739.3868 | [6 empty] | 625.8999 |  |  | 459.4915 |  |  | 536.5442 | 685.445 | 695.1174 | 1108.1977 | 1141.0321 | 1071.9301 | 563.0779 | 737.9887 | 859.0275 | 637.4724 | 713.8517 | 1150.3139 | 1114.7223 | 648.9513 | 831.5273 | 942.6923 | 1061.043 | 1096.9479 | 561.024 | 680.6274 | 715.3265 | 579.5664 | 756.6859 | 875.735 | 1006.9425 | 1120.3636 | 623.8894 | 724.8815 | 673.2006 | 861.0118 | 93.7091 | 0.0003939 | 17.6881 | 4.7305 | -40.3385 | 3.121 | 9469.52 | 0.31 | 2.5178 | -1.4846 | -0.75862 | -1.8358 | 7.1626 | 6.0317 | 8.048 | 87.627 | 217.7659 | 53.1459 | 67.0787 | 15.6507 | 83.5461 | 41.1266
42810.4541 | 1217 | 17.3945 | 17.8158 | 17.9773 | 18.0281 | 17.3771 | 16.0633 | 15.3199 | 16.4663 | 16.8987 | 17.0663 | 17.0799 | 16.6239 | 15.656 | 14.4626 | 43.0307 | 60.0945 | 58.9015 | 90.3978 | 80.9696 | 94.311 |  |  |  | 54.4163 | 88.7152 | 552.9192 | 685.3875 | 700.5534 | 692.9648 | 23.0761 | 60.7946 | 889.9144 | 22.9847 | 59.0109 | 732.5473 | 820.8295 | 747.9175 |  | 262.4375 | 887.7872 | 872.7868 | 744.8999 |  | 485.3879 | 723.0352 | 572.9439 | 735.8282 | 914.9912 | 1037.6379 | 1051.7829 | 44.448 | 409.8511 | 85.375 | 636.3171 | 14.8116 | 49.8615 | 48.7174 | 51.7431 | 65.8883 |  |  | 1.3322 | -0.53875 | 0.09122 | -0.94822 | 7.3507 | 5.0107 | 9.4624 | -3.3337 | 21.472 | 56.5709 | 35.0025 | -9.035e-05 | -2.136e-05 | -0.00078032 | 35.0322 | 16.8242 | 16.6809 | 17.0554 | 17.0794 | 16.0913 | 14.693 | 16.6753 | 17.0453 | 17.3852 | 17.4712 | 17.2206 | 16.4108 | 14.7277 | 784.9342 | 526.2061 | 454.6366 | 300.493 | 266.596 | 773.3896 | 468.54 | 29.7249 | 47.7485 | 53.3451 | 85.6147 | 87.9071 | 92.4127 |  |  |  | 647.8069 | 606.1924 | 608.7205 | 637.728 | 95.7249 | 31.5442 | 917.0336 |  |  | 815.0503 |  |  | 24.4837 | 62.3851 | 610.0317 | 26.0317 | 65.1693 | 895.2915 | 742.7553 | 637.1567 | 902.7748 | 899.8603 | 748.2576 |  | 834.2145 | 924.1547 | 1118.891 | 610.8527 | 699.3841 | 930.8128 |  | 354.4933 |  |  | 474.1255 | 662.3466 | 739.9983 | [6 empty] | 627.3807 |  |  | 459.9471 |  |  | 536.6614 | 684.866 | 694.9658 | 1109.514 | 1139.2691 | 1070.1542 | 563.681 | 737.317 | 859.2473 | 637.1821 | 714.5723 | 1150.969 | 1112.4651 | 648.6302 | 829.8147 | 944.1868 | 1063.51 | 1095.7419 | 561.7386 | 682.6968 | 715.7523 | 579.4225 | 756.644 | 876.5138 | 1012.1144 | 1120.3836 | 623.9981 | 725.6307 | 673.1657 | 862.0196 | 98.8596 | -0.00021643 | 17.6892 | 4.7298 | -40.2697 | 3.121 | 9490.24 | 0.2 | 2.5001 | -1.6145 | 0.66433 | -2.1419 | 6.8406 | 5.6478 | 7.7613 | 87.6477 | 218.317 | 53.1819 | 66.7324 | 18.7031 | 83.3211 | 41.0687
42810.4541 | 1218 | 17.4088 | 17.825 | 17.9915 | 18.037 | 17.3953 | 16.0658 | 15.3344 | 16.4751 | 16.9092 | 17.0754 | 17.0912 | 16.6259 | 15.6676 | 14.4848 | 43.179 | 60.2108 | 59.0244 | 90.3784 | 81.0211 | 94.3554 |  |  |  | 54.5657 | 88.7389 | 553.288 | 685.3598 | 700.7444 | 692.9166 | 22.9649 | 62.9107 | 891.7051 | 23.3978 | 59.0895 | 736.0357 | 820.9176 | 750.4464 |  | 266.5057 | 889.3057 | 874.1294 | 749.6483 |  | 487.349 | 724.1931 | 573.2477 | 734.7297 | 907.2567 | 1032.9575 | 1051.021 | 45.2284 | 410.2064 | 82.2536 | 636.0304 | 14.8247 | 49.861 | 48.7879 | 51.7656 | 65.4534 |  |  | 1.3775 | -0.48618 | -0.40688 | -0.91142 | 7.147 | 5.7158 | 9.5609 | -2.3789 | 20.6804 | 55.3726 | 33.4683 | -8.707e-05 | -2.464e-05 | -0.00073925 | 35.1217 | 16.824 | 16.6791 | 17.0519 | 17.0729 | 16.0846 | 14.6922 | 16.6809 | 17.0356 | 17.3885 | 17.4699 | 17.2177 | 16.4092 | 14.7248 | 781.5427 | 511.6287 | 439.9036 | 291.6376 | 251.2501 | 774.4766 | 468.5725 | 29.8435 | 47.8475 | 53.4448 | 85.6663 | 87.9484 | 92.4572 |  |  |  | 648.1033 | 606.7281 | 609.2693 | 637.3593 | 79.5037 | 29.9154 | 916.8803 |  |  | 811.7269 |  |  | 24.5233 | 62.458 | 610.0016 | 26.0934 | 65.2375 | 895.9387 | 744.6576 | 638.2241 | 899.775 | 897.9231 | 751.7386 |  | 834.2859 | 916.6677 | 1120.1366 | 611.3054 | 699.6951 | 916.9239 |  | 356.1321 |  |  | 474.1021 | 665.0093 | 741.2137 | [6 empty] | 628.4553 |  |  | 460.6365 |  |  | 537.1257 | 685.6339 | 695.7741 | 1107.3402 | 1138.019 | 1070.3029 | 564.1942 | 736.2196 | 858.6539 | 637.7527 | 716.7234 | 1156.1019 | 1113.212 | 648.2511 | 827.8134 | 949.6463 | 1066.5832 | 1096.175 | 561.4286 | 682.7117 | 715.9499 | 579.4948 | 756.6128 | 877.6792 | 1015.7808 | 1119.3472 | 623.1731 | 725.246 | 673.4269 | 863.2898 | 96.716 | 0.0001203 | 17.6914 | 4.728 | -40.3004 | 3.121 | 9475.99 | 0.29 | 2.5423 | -1.5346 | -1.4038 | -2.1011 | 6.7331 | 6.0214 | 7.7877 | 87.575 | 219.3226 | 53.2429 | 67.5131 | 20.3467 | 83.2178 | 41.1397
42810.4541 | 1219 | 17.3943 | 17.8295 | 17.9867 | 18.0166 | 17.3856 | 16.0631 | 15.336 | 16.4768 | 16.9164 | 17.0702 | 17.0805 | 16.6266 | 15.6666 | 14.4747 | 43.3217 | 60.3295 | 59.1441 | 90.3526 | 81.1117 | 94.3881 |  |  |  | 54.7165 | 88.7565 | 554.6091 | 686.1217 | 701.5875 | 693.5574 | 23.0528 | 60.9984 | 894.0975 | 24.3125 | 60.4412 | 739.4802 | 821.2379 | 751.5165 |  | 259.3134 | 893.9355 | 878.0028 | 750.1088 |  | 487.6875 | 724.5634 | 571.8466 | 732.2932 | 897.3424 | 1028.0969 | 1050.0563 | 47.903 | 410.4485 | 79.4119 | 635.7345 | 14.8183 | 49.8788 | 48.842 | 51.7792 | 65.1166 |  |  | 1.187 | -0.20559 | 0.44738 | -1.3201 | 7.7265 | 5.0922 | 9.7114 | -3.0978 | 20.9726 | 55.2515 | 36.1414 | -7.064e-05 | -2.136e-05 | -0.00074582 | 35.2148 | 16.833 | 16.6795 | 17.0586 | 17.0799 | 16.0788 | 14.6915 | 16.6796 | 17.0399 | 17.3886 | 17.4729 | 17.2187 | 16.4121 | 14.7271 | 762.6816 | 523.1022 | 449.2399 | 287.7269 | 245.3937 | 773.7898 | 468.1156 | 29.9432 | 47.9545 | 53.5421 | 85.7173 | 87.9878 | 92.4866 |  |  |  | 648.1504 | 605.8789 | 609.066 | 635.0958 | 64.6147 | 24.9505 | 914.5354 |  |  | 809.4377 |  |  | 24.5692 | 62.5266 | 611.0223 | 26.1597 | 65.3033 | 898.7313 | 746.6784 | 638.579 | 900.4964 | 900.1647 | 756.3414 |  | 834.6238 | 915.9547 | 1121.9017 | 611.6176 | 699.9807 | 923.1979 |  | 357.9217 |  |  | 474.9743 | 670.1687 | 743.9453 | [6 empty] | 628.9584 |  |  | 461.6957 |  |  | 537.43 | 687.2492 | 697.0486 | 1108.8058 | 1142.9267 | 1069.4895 | 564.3766 | 735.1019 | 857.2762 | 638.5695 | 718.4421 | 1159.3709 | 1113.876 | 647.8553 | 825.8863 | 953.4591 | 1065.8797 | 1095.8208 | 560.6352 | 681.6855 | 716.2834 | 579.3558 | 756.6257 | 876.6971 | 1016.361 | 1117.0253 | 622.3537 | 724.5404 | 673.775 | 865.7824 | 83.1387 | -5.5071e-05 | 17.6929 | 4.7267 | -40.344 | 3.121 | 9433.55 | 0.28 | 2.3607 | -0.99809 | 1.4723 | -2.5292 | 6.9878 | 5.6728 | 7.8341 | 87.5606 | 220.4762 | 53.3018 | 69.3535 | 19.2163 | 83.3091 | 41.2123
42810.4542 | 1220 | 17.406 | 17.8374 | 17.9901 | 18.0246 | 17.3895 | 16.0735 | 15.3372 | 16.4769 | 16.9206 | 17.0714 | 17.0852 | 16.6318 | 15.6708 | 14.4756 | 43.4697 | 60.4433 | 59.2598 | 90.3211 | 81.1896 | 94.3975 |  |  |  | 54.8632 | 88.766 | 554.3508 | 685.3637 | 700.2294 | 692.7471 | 23.0511 | 60.9714 | 896.9194 | 23.3739 | 59.3394 | 740.0318 | 822.2038 | 752.586 |  | 256.0779 | 896.5323 | 879.6523 | 749.9581 |  | 487.0278 | 725.8353 | 570.8192 | 729.5002 | 896.9644 | 1024.5577 | 1051.2283 | 50.4702 | 410.6834 | 78.9073 | 635.7292 | 14.8085 | 49.9027 | 48.8769 | 51.7985 | 64.8145 |  |  | 1.3559 | -0.95076 | -0.09146 | -0.97056 | 7.7975 | 6.273 | 10.8942 | -4.0119 | 20.6586 | 55.6275 | 38.6959 | -0.00012157 | -8.707e-05 | -0.00074747 | 35.3154 | 16.8427 | 16.6801 | 17.0659 | 17.0819 | 16.0921 | 14.6977 | 16.6818 | 17.0473 | 17.3882 | 17.4806 | 17.2226 | 16.4134 | 14.7368 | 729.8975 | 511.2043 | 424.6356 | 281.9723 | 231.6256 | 772.1732 | 467.0631 | 30.0563 | 48.059 | 53.6432 | 85.7647 | 88.0244 | 92.5228 |  |  |  | 648.0852 | 604.4021 | 608.1623 | 633.0438 | 85.1601 | 29.57 | 916.277 |  |  | 814.8125 |  |  | 24.6085 | 62.5832 | 611.194 | 26.2096 | 65.3824 | 901.0358 | 743.4897 | 638.0861 | 903.0502 | 903.0354 | 754.4567 |  | 834.1656 | 921.433 | 1124.0594 | 611.2724 | 700.2631 | 925.0093 |  | 360.0485 |  |  | 474.9385 | 667.0279 | 742.9911 | [6 empty] | 628.5748 |  |  | 462.38 |  |  | 537.3401 | 687.7517 | 697.6721 | 1108.2034 | 1148.3365 | 1067.6413 | 564.7606 | 734.3372 | 855.0057 | 639.0709 | 718.7481 | 1154.9034 | 1114.1314 | 648.4848 | 824.3699 | 953.2749 | 1064.3966 | 1093.5882 | 560.2223 | 680.5309 | 716.5044 | 579.3049 | 757.2711 | 874.8852 | 1015.7385 | 1115.3193 | 622.1379 | 723.3585 | 673.4676 | 865.1057 | 92.5067 | -0.00095305 | 17.6937 | 4.7278 | -40.2704 | 3.121 | 9332.38 | 0.27 | 2.522 | -2.1477 | -0.66613 | -2.17 | 7.0102 | 6.2877 | 8.2862 | 87.4591 | 221.7157 | 53.3783 | 72.3968 | 21.7361 | 83.6276 | 41.2559
42810.4542 | 1221 | 17.4035 | 17.8384 | 17.9933 | 18.032 | 17.3902 | 16.0796 | 15.3442 | 16.4822 | 16.918 | 17.0662 | 17.0967 | 16.6311 | 15.6792 | 14.4848 | 43.6177 | 60.5664 | 59.383 | 90.2914 | 81.2646 | 94.4224 |  |  |  | 55.0124 | 88.7903 | 552.1529 | 683.1989 | 697.5471 | 690.7958 | 23.1316 | 60.9962 | 898.2098 | 24.1032 | 59.5929 | 738.1655 | 820.4552 | 753.3361 |  | 245.5889 | 898.1875 | 880.1046 | 749.7236 |  | 487.0204 | 726.365 | 571.3303 | 731.4039 | 903.5627 | 1024.1628 | 1050.5303 | 52.0082 | 410.8003 | 79.1417 | 635.7973 | 14.7572 | 49.9335 | 48.8841 | 51.8116 | 64.4709 |  |  | 1.0897 | -1.552 | -0.06912 | -1.5396 | 7.0635 | 5.677 | 9.789 | -4.1393 | 21.7234 | 54.5432 | 39.4271 | -0.00012321 | -5.914e-05 | -0.00074582 | 35.4072 | 16.8371 | 16.6766 | 17.0568 | 17.0723 | 16.089 | 14.6981 | 16.6817 | 17.0359 | 17.3845 | 17.4773 | 17.2278 | 16.4166 | 14.739 | 727.3686 | 506.2718 | 429.5787 | 270.5028 | 221.3132 | 771.6099 | 466.5159 | 30.1755 | 48.1759 | 53.7466 | 85.7899 | 88.0414 | 92.5715 |  |  |  | 648.0853 | 603.6252 | 607.2709 | 634.1338 | 86.2762 | 31.1196 | 918.8038 |  |  | 816.4546 |  |  | 24.663 | 62.6627 | 608.293 | 26.2738 | 65.4519 | 902.387 | 739.3283 | 636.8446 | 904.7317 | 905.9503 | 748.1865 |  | 833.3042 | 923.3051 | 1127.5303 | 610.0235 | 700.3199 | 914.9391 |  | 361.9236 |  |  | 474.8189 | 660.692 | 738.041 | [6 empty] | 627.266 |  |  | 462.0488 |  |  | 536.9061 | 687.5314 | 697.4402 | 1105.1532 | 1146.1616 | 1066.8187 | 565.4705 | 734.9858 | 854.1706 | 638.9806 | 718.4509 | 1150.4847 | 1119.9625 | 649.6973 | 824.9266 | 948.9751 | 1063.9684 | 1093.216 | 560.6051 | 679.6203 | 716.1371 | 579.0415 | 756.7503 | 872.8986 | 1017.928 | 1115.6917 | 622.4648 | 722.4988 | 672.6834 | 863.781 | 109.3419 | -0.00091095 | 17.6953 | 4.7284 | -40.2198 | 3.1209 | 9237.74 | 0.31 | 2.2587 | -2.7448 | -0.57925 | -2.7338 | 6.6711 | 5.9807 | 7.8534 | 87.3444 | 223.9153 | 53.4264 | 72.4694 | 21.0758 | 83.0656 | 41.2256
42810.4542 | 1222 | 17.4024 | 17.8269 | 17.9911 | 18.0293 | 17.3887 | 16.0714 | 15.3501 | 16.4827 | 16.9189 | 17.0715 | 17.0982 | 16.6227 | 15.6751 | 14.4832 | 43.7707 | 60.6784 | 59.5089 | 90.272 | 81.3637 | 94.4592 |  |  |  | 55.1664 | 88.8173 | 550.8656 | 681.9679 | 696.2919 | 689.746 | 23.1434 | 60.9856 | 898.7334 | 23.3517 | 59.6527 | 736.179 | 819.7808 | 748.3172 |  | 254.7312 | 898.9126 | 880.9274 | 748.5867 |  | 486.5026 | 727.8301 | 570.4285 | 732.8189 | 900.0992 | 1025.9601 | 1051.2606 | 53.2083 | 410.725 | 80.646 | 635.9132 | 14.7005 | 49.9667 | 48.8892 | 51.8272 | 64.128 |  |  | 1.3519 | -0.43624 | -0.12169 | -1.4897 | 8.1017 | 7.4841 | 11.0053 | -3.4067 | 20.6278 | 55.0062 | 39.3655 | -9.528e-05 | -8.378e-05 | -0.0007294 | 35.4991 | 16.853 | 16.6734 | 17.0493 | 17.074 | 16.088 | 14.6972 | 16.6804 | 17.0364 | 17.387 | 17.4689 | 17.2222 | 16.4091 | 14.7212 | 732.9253 | 508.9167 | 433.8036 | 259.4231 | 215.2344 | 770.5518 | 465.8851 | 30.2915 | 48.2747 | 53.8417 | 85.8306 | 88.0642 | 92.6074 |  |  |  | 648.155 | 604.4202 | 607.4135 | 634.6116 | 68.5198 | 26.7814 | 921.5943 |  |  | 821.5919 |  |  | 24.7047 | 62.7234 | 606.2641 | 26.3403 | 65.5098 | 903.9989 | 740.7336 | 635.6197 | 913.6757 | 919.1869 | 747.9022 |  | 833.5144 | 929.0962 | 1131.0205 | 608.5671 | 700.2265 | 907.5518 |  | 363.737 |  |  | 474.8703 | 660.4572 | 736.5507 | [6 empty] | 625.599 |  |  | 461.311 |  |  | 536.479 | 687.5647 | 697.4302 | 1106.6008 | 1148.6914 | 1068.9559 | 566.334 | 736.0906 | 854.9678 | 638.6404 | 719.2078 | 1158.5245 | 1122.165 | 650.5663 | 826.8379 | 950.884 | 1065.1212 | 1096.274 | 560.4831 | 679.1994 | 715.8489 | 578.8037 | 755.6686 | 871.9406 | 1020.4746 | 1117.6348 | 622.4889 | 722.883 | 672.318 | 861.8089 | 105.0544 | -0.00051109 | 17.6963 | 4.7271 | -40.4102 | 3.1209 | 9136.33 | 0.31 | 2.5144 | -1.4563 | -0.76914 | -2.6911 | 7.1496 | 6.8716 | 8.3328 | 87.4227 | 226.0348 | 53.4448 | 71.4612 | 20.4785 | 82.8786 | 41.2267
42810.4542 | 1223 | 17.4049 | 17.8304 | 17.9881 | 18.0248 | 17.3841 | 16.0693 | 15.3459 | 16.4833 | 16.9179 | 17.0655 | 17.0878 | 16.6227 | 15.6695 | 14.4795 | 43.9146 | 60.7963 | 59.6226 | 90.2619 | 81.4551 | 94.4715 |  |  |  | 55.3138 | 88.8186 | 551.5008 | 682.217 | 696.9025 | 690.2167 | 23.7141 | 61.0365 | 897.7701 | 23.3128 | 59.444 | 732.7241 | 818.7753 | 745.1146 |  | 259.2411 | 894.4926 | 878.1244 | 744.2645 |  | 486.2513 | 728.2445 | 570.232 | 739.0689 | 905.5978 | 1029.4669 | 1052.3586 | 54.2085 | 410.4988 | 84.0164 | 636.4293 | 14.6231 | 49.9506 | 48.8954 | 51.8384 | 63.7836 |  |  | 1.4084 | 0.10917 | -0.215 | -1.2426 | 8.9935 | 7.8192 | 10.3672 | -3.5269 | 21.1182 | 56.1022 | 34.6889 | -8.871e-05 | -5.585e-05 | -0.00075075 | 35.6076 | 16.8622 | 16.6742 | 17.0542 | 17.0732 | 16.0856 | 14.6978 | 16.6841 | 17.0416 | 17.3873 | 17.4691 | 17.2238 | 16.4089 | 14.7274 | 712.9398 | 504.4608 | 438.901 | 266.6015 | 214.8972 | 768.7975 | 465.0982 | 30.4011 | 48.3808 | 53.9379 | 85.8843 | 88.1024 | 92.6564 |  |  |  | 648.1316 | 605.1594 | 608.0934 | 634.7427 | 86.2041 | 33.815 | 930.4322 |  |  | 834.595 |  |  | 24.7585 | 62.7886 | 606.169 | 26.3983 | 65.5863 | 903.5764 | 745.961 | 635.971 | 921.0669 | 922.8086 | 755.9781 |  | 834.7045 | 937.0581 | 1134.5387 | 608.6865 | 700.2606 | 908.2817 |  | 365.7827 |  |  | 475.8798 | 668.083 | 741.6225 | [6 empty] | 625.7939 |  |  | 461.1296 |  |  | 535.7298 | 688.0878 | 698.1365 | 1106.6488 | 1152.476 | 1070.5454 | 566.557 | 736.9614 | 856.656 | 638.3171 | 720.4177 | 1146.7793 | 1119.8441 | 650.1069 | 829.0718 | 949.3888 | 1067.3911 | 1099.4462 | 560.665 | 679.5376 | 715.5957 | 578.2042 | 754.5455 | 872.5842 | 1019.5681 | 1118.2267 | 622.3541 | 723.0878 | 671.7746 | 860.0933 | 101.3502 | -5.5071e-05 | 17.6972 | 4.7259 | -40.4162 | 3.1209 | 9085.22 | 0.34 | 2.567 | 0.72866 | -1.0226 | -2.4583 | 7.5429 | 7.0333 | 8.0985 | 87.5979 | 228.1288 | 53.4495 | 73.0356 | 19.7528 | 82.6734 | 41.2182
42810.4542 | 1224 | 17.3957 | 17.8245 | 17.9864 | 18.0207 | 17.3825 | 16.067 | 15.3393 | 16.476 | 16.9119 | 17.0642 | 17.0862 | 16.6231 | 15.6676 | 14.4754 | 44.071 | 60.92 | 59.7514 | 90.2682 | 81.5507 | 94.4933 |  |  |  | 55.4599 | 88.8282 | 551.4499 | 681.8152 | 695.9358 | 689.656 | 26.016 | 61.1414 | 897.2532 | 23.2965 | 59.4694 | 729.5415 | 817.4083 | 741.7634 |  | 256.5668 | 894.4723 | 877.6921 | 738.888 |  | 486.4334 | 728.3647 | 571.0977 | 750.0121 | 919.6703 | 1033.3458 | 1051.8012 | 55.5591 | 410.3066 | 84.474 | 636.6683 | 14.5569 | 49.9143 | 48.8995 | 51.838 | 63.4543 |  |  | 1.3736 | -0.44609 | -0.16966 | -1.2755 | 6.7671 | 6.478 | 9.5899 | -2.8468 | 20.9824 | 55.3102 | 34.7937 | -8.05e-05 | -4.93e-06 | -0.0007409 | 35.7101 | 16.8725 | 16.6787 | 17.0608 | 17.0705 | 16.0929 | 14.6971 | 16.6833 | 17.0465 | 17.3898 | 17.4731 | 17.2202 | 16.4166 | 14.733 | 728.9156 | 510.7599 | 452.9402 | 269.0305 | 215.5193 | 768.1064 | 464.8115 | 30.5056 | 48.4801 | 54.0292 | 85.9327 | 88.1418 | 92.7103 |  |  |  | 648.2324 | 606.4127 | 608.9217 | 636.0091 | 78.8275 | 26.2291 | 934.6001 |  |  | 833.2652 |  |  | 24.8111 | 62.8575 | 606.7832 | 26.4626 | 65.6541 | 903.4849 | 748.429 | 636.2319 | 919.1056 | 919.3153 | 761.9135 |  | 835.3011 | 936.8764 | 1139.0901 | 608.8376 | 700.4412 | 922.3816 |  | 367.8569 |  |  | 476.7119 | 677.9631 | 745.4134 | [6 empty] | 626.1818 |  |  | 461.039 |  |  | 535.737 | 689.511 | 698.9068 | 1093.1096 | 1160.1996 | 1069.154 | 566.4723 | 736.8388 | 857.4992 | 638.7687 | 721.4102 | 1133.0248 | 1123.677 | 649.4793 | 829.0096 | 943.5387 | 1067.7802 | 1097.1366 | 560.1489 | 679.2817 | 715.5073 | 577.5955 | 753.2741 | 870.5447 | 1017.4208 | 1120.2231 | 621.5878 | 722.0765 | 671.1753 | 857.0069 | 111.2727 | 2.909e-05 | 17.6991 | 4.7239 | -40.329 | 3.1208 | 9060.32 | 0.34 | 2.5343 | -1.473 | -0.90841 | -2.4907 | 6.5528 | 6.4113 | 7.8006 | 87.6337 | 231.1537 | 53.4881 | 71.0066 | 18.1348 | 82.3819 | 41.2037
42810.4542 | 1225 | 17.3896 | 17.8199 | 17.9784 | 18.0163 | 17.3847 | 16.0522 | 15.343 | 16.4637 | 16.9002 | 17.0551 | 17.0801 | 16.6186 | 15.6637 | 14.4745 | 44.2335 | 61.0384 | 59.8726 | 90.2876 | 81.6276 | 94.4884 |  |  |  | 55.6159 | 88.8642 | 548.6468 | 679.1423 | 692.6766 | 686.8569 | 24.1314 | 63.4705 | 899.303 | 23.7288 | 59.5532 | 728.7888 | 816.1779 | 740.4985 |  | 266.0187 | 894.8594 | 877.905 | 740.5497 |  | 486.8085 | 728.6994 | 571.5921 | 755.285 | 927.2378 | 1034.4006 | 1052.0253 | 56.5407 | 410.2247 | 83.6306 | 636.7576 | 14.4962 | 49.8873 | 48.913 | 51.8486 | 63.26 |  |  | 1.4156 | -1.2898 | -0.41542 | -1.1033 | 7.532 | 5.9379 | 9.6983 | -3.2792 | 20.3168 | 54.5107 | 35.9201 | -0.00012157 | -5.585e-05 | -0.00079347 | 35.8025 | 16.8767 | 16.6764 | 17.0661 | 17.0748 | 16.0888 | 14.6998 | 16.6915 | 17.0477 | 17.3882 | 17.475 | 17.2224 | 16.4136 | 14.7326 | 728.822 | 497.611 | 430.1563 | 267.931 | 209.5199 | 766.5868 | 463.7508 | 30.6143 | 48.5874 | 54.129 | 85.9752 | 88.1672 | 92.7651 |  |  |  | 648.0863 | 605.7858 | 608.7831 | 631.7751 | 69.0818 | 23.123 | 933.4976 |  |  | 831.475 |  |  | 24.8575 | 62.9246 | 603.9823 | 26.5265 | 65.7166 | 905.6379 | 750.4307 | 634.1556 | 916.8592 | 917.3848 | 763.7648 |  | 836.3162 | 932.345 | 1141.2975 | 607.561 | 700.4716 | 914.2247 |  | 369.7125 |  |  | 477.7817 | 681.4122 | 747.1232 | [6 empty] | 624.2972 |  |  | 460.4044 |  |  | 535.8493 | 690.5845 | 699.7558 | 1097.7613 | 1165.1679 | 1074.8097 | 566.825 | 736.0177 | 858.9629 | 638.893 | 722.8408 | 1126.0273 | 1137.9647 | 649.3815 | 828.6591 | 947.2415 | 1068.6616 | 1096.6764 | 560.0481 | 677.1737 | 715.1912 | 577.6071 | 752.2922 | 867.3756 | 1018.7268 | 1121.8298 | 621.1905 | 720.584 | 671.2861 | 854.9062 | 108.7142 | 0.0017128 | 17.7009 | 4.722 | -40.3372 | 3.1209 | 9088.74 | 0.27 | 2.5691 | -2.5052 | -1.4217 | -2.3169 | 6.916 | 6.1406 | 7.8477 | 87.9245 | 232.7544 | 53.5308 | 70.4599 | 20.4521 | 81.9402 | 41.2913
42810.4542 | 1226 | 17.407 | 17.8305 | 17.9889 | 18.0284 | 17.3891 | 16.0618 | 15.3679 | 16.4876 | 16.9194 | 17.0651 | 17.0907 | 16.6321 | 15.6718 | 14.4922 | 44.3777 | 61.1547 | 59.9982 | 90.3049 | 81.722 | 94.5081 |  |  |  | 55.7587 | 88.8698 | 547.6391 | 677.8175 | 691.6126 | 685.6304 | 23.4468 | 61.6206 | 900.5573 | 26.3721 | 60.1683 | 733.2303 | 816.0571 | 744.5647 |  | 261.3555 | 897.2373 | 879.8833 | 750.8614 |  | 486.2179 | 729.3371 | 570.6233 | 762.417 | 932.4133 | 1034.6679 | 1051.3261 | 56.405 | 410.0963 | 84.8691 | 636.9797 | 14.4292 | 49.8587 | 48.9079 | 51.8364 | 63.2098 |  |  | 1.2008 | -1.7991 | 0.14642 | -1.2301 | 8.314 | 7.2186 | 10.3698 | -2.9473 | 21.2176 | 55.8266 | 36.4975 | -6.9e-05 | -0.00013306 | -0.00075075 | 35.9018 | 16.8872 | 16.6837 | 17.0639 | 17.0784 | 16.0919 | 14.7032 | 16.692 | 17.0518 | 17.391 | 17.4797 | 17.2247 | 16.4198 | 14.7368 | 716.3565 | 492.8283 | 419.1564 | 268.7212 | 215.0656 | 764.5353 | 462.4862 | 30.7452 | 48.7031 | 54.2377 | 86.0102 | 88.207 | 92.813 |  |  |  | 647.7146 | 603.4541 | 607.5637 | 627.9972 | 83.733 | 29.1385 | 932.2248 |  |  | 828.364 |  |  | 24.9019 | 62.9922 | 602.0435 | 26.5905 | 65.7896 | 907.2236 | 752.3329 | 631.3711 | 915.2022 | 917.209 | 763.9876 |  | 838.1086 | 927.1719 | 1144.109 | 605.774 | 700.2299 | 919.6644 |  | 371.6403 |  |  | 478.1358 | 677.8205 | 749.437 | [6 empty] | 621.4453 |  |  | 458.6132 |  |  | 535.3376 | 690.5231 | 700.5859 | 1090.9768 | 1167.4928 | 1078.3416 | 567.335 | 734.9827 | 859.6438 | 638.2778 | 723.5887 | 1118.7373 | 1135.8437 | 649.1845 | 827.6578 | 948.1657 | 1072.4439 | 1096.2482 | 560.3545 | 675.8661 | 714.4623 | 578.9524 | 752.051 | 864.2814 | 1015.662 | 1121.2628 | 621.0753 | 719.517 | 672.1305 | 854.8399 | 100.3981 | -0.00075661 | 17.7012 | 4.7205 | -40.1755 | 3.1208 | 9119.87 | 0.29 | 2.3646 | -2.9596 | 0.84431 | -2.4473 | 7.2668 | 6.7712 | 8.1157 | 88.5245 | 234.7859 | 53.5232 | 71.0956 | 21.4193 | 81.615 | 41.3201
42810.4542 | 1227 | 17.3924 | 17.8211 | 17.9771 | 18.0212 | 17.382 | 16.0614 | 15.3617 | 16.4817 | 16.915 | 17.0626 | 17.0926 | 16.629 | 15.6626 | 14.4789 | 44.5081 | 61.2627 | 60.104 | 90.2903 | 81.7934 | 94.5276 |  |  |  | 55.8908 | 88.8843 | 548.4926 | 678.0863 | 692.4914 | 685.921 | 23.393 | 61.3698 | 901.9707 | 23.5824 | 59.8416 | 747.6964 | 818.0551 | 755.1388 |  | 261.2365 | 899.7107 | 882.4052 | 765.1219 |  | 487.2299 | 731.2141 | 570.6177 | 768.1468 | 933.7403 | 1033.8884 | 1053.1835 | 55.1056 | 410.0149 | 89.8116 | 637.4593 | 14.369 | 49.8352 | 48.9212 | 51.8413 | 63.2469 |  |  | 1.3453 | -0.074165 | 0.82587 | -0.45669 | 8.4954 | 7.0721 | 10.1353 | -4.3062 | 20.6547 | 55.6552 | 37.5564 | -9.528e-05 | -8.871e-05 | -0.00075732 | 35.9911 | 16.8886 | 16.6832 | 17.0534 | 17.0776 | 16.0899 | 14.6997 | 16.6917 | 17.0419 | 17.3882 | 17.4749 | 17.2195 | 16.417 | 14.7395 | 705.3468 | 498.3919 | 419.697 | 274.4632 | 222.6818 | 763.1865 | 461.4017 | 30.8578 | 48.8013 | 54.3346 | 86.0496 | 88.2275 | 92.8462 |  |  |  | 647.4942 | 601.9393 | 606.0707 | 628.8514 | 75.7542 | 24.2987 | 931.7258 |  |  | 828.6877 |  |  | 24.9531 | 63.0599 | 602.5218 | 26.6534 | 65.8502 | 910.0612 | 753.6015 | 629.6894 | 913.6727 | 915.5686 | 764.798 |  | 840.2257 | 924.8127 | 1145.126 | 604.122 | 700.1524 | 919.1859 |  | 373.9688 |  |  | 478.6987 | 674.2362 | 751.1432 | [6 empty] | 619.7634 |  |  | 456.4279 |  |  | 534.3184 | 689.6058 | 701.1211 | 1089.4397 | 1167.0324 | 1081.418 | 567.4327 | 735.6961 | 859.2228 | 637.3432 | 722.9908 | 1115.0618 | 1140.5422 | 649.0538 | 830.8786 | 945.7643 | 1072.8384 | 1097.7252 | 560.5246 | 675.121 | 713.6602 | 580.8233 | 751.9457 | 863.9425 | 1014.8962 | 1120.8403 | 620.6218 | 719.3631 | 673.3943 | 856.2528 | 90.8833 | -0.00027956 | 17.7006 | 4.7171 | -40.3351 | 3.1208 | 9148.56 | 0.35 | 2.5033 | -0.60147 | 2.0071 | -1.4925 | 7.3435 | 6.7002 | 8.021 | 89.2217 | 235.5371 | 53.5507 | 71.8279 | 21.141 | 81.8616 | 41.2512
42810.4542 | 1228 | 17.3922 | 17.8189 | 17.9757 | 18.0141 | 17.3806 | 16.05 | 15.3575 | 16.4717 | 16.9019 | 17.0661 | 17.0791 | 16.6243 | 15.6589 | 14.4726 | 44.6507 | 61.3743 | 60.2289 | 90.2741 | 81.8793 | 94.5621 |  |  |  | 56.0285 | 88.9017 | 549.0876 | 678.2144 | 692.7006 | 686.2344 | 23.428 | 61.5319 | 905.0286 | 23.7284 | 59.8232 | 750.2039 | 819.4249 | 759.7784 |  | 254.772 | 903.3884 | 886.1413 | 768.0974 |  | 487.5992 | 732.447 | 571.8904 | 769.3959 | 932.6803 | 1032.0149 | 1054.2229 | 53.3387 | 409.773 | 91.8785 | 637.6981 | 14.3075 | 49.8041 | 48.9249 | 51.8359 | 63.3473 |  |  | 1.3204 | -0.89162 | -0.14469 | -0.47312 | 7.9822 | 6.7264 | 8.7422 | -3.4783 | 20.3777 | 53.7594 | 42.8954 | -0.00014456 | -8.871e-05 | -0.00073597 | 36.0866 | 16.8927 | 16.6688 | 17.0514 | 17.0727 | 16.084 | 14.698 | 16.6839 | 17.0328 | 17.3814 | 17.473 | 17.2219 | 16.4122 | 14.7326 | 693.4732 | 491.268 | 421.5708 | 276.3238 | 218.1586 | 761.2528 | 460.2245 | 30.9678 | 48.8987 | 54.423 | 86.0686 | 88.2525 | 92.8751 |  |  |  | 647.4912 | 601.4656 | 605.4353 | 630.9773 | 70.8641 | 25.1012 | 929.8716 |  |  | 830.67 |  |  | 25.0066 | 63.1326 | 603.2628 | 26.7241 | 65.9137 | 914.2357 | 751.6977 | 628.1966 | 912.5671 | 916.0426 | 762.4305 |  | 840.9422 | 916.6042 | 1145.5977 | 602.2235 | 699.8747 | 910.0036 |  | 375.9303 |  |  | 479.1288 | 670.5659 | 750.3699 | [6 empty] | 617.9024 |  |  | 454.4564 |  |  | 533.2783 | 688.7104 | 701.1114 | 1085.0419 | 1162.7694 | 1086.342 | 567.815 | 736.8373 | 860.3042 | 636.9262 | 722.642 | 1107.7944 | 1144.0545 | 648.935 | 832.869 | 942.4462 | 1072.0777 | 1098.6097 | 560.4846 | 674.9883 | 713.447 | 581.9761 | 751.7684 | 865.7224 | 1015.2145 | 1119.6554 | 620.5734 | 719.8329 | 674.7602 | 856.7153 | 85.1167 | -0.00010418 | 17.7 | 4.7107 | -40.3002 | 3.1209 | 9107.42 | 0.4 | 2.4803 | -2.0867 | -0.84061 | -1.5201 | 7.1131 | 6.5297 | 7.4441 | 89.5318 | 236.0836 | 53.5377 | 72.4456 | 20.6965 | 82.2214 | 41.1916
42810.4543 | 1229 | 17.3966 | 17.8241 | 17.9822 | 18.0215 | 17.3882 | 16.061 | 15.3684 | 16.4751 | 16.9061 | 17.0617 | 17.0823 | 16.6298 | 15.6654 | 14.4747 | 44.7987 | 61.4844 | 60.3376 | 90.2619 | 81.9793 | 94.5702 |  |  |  | 56.1666 | 88.9135 | 548.8519 | 677.9278 | 692.3968 | 685.8803 | 23.4801 | 61.4195 | 908.5246 | 23.5909 | 59.9147 | 756.1343 | 821.0598 | 764.7544 |  | 260.9303 | 905.9428 | 889.4245 | 776.9931 |  | 487.966 | 732.8055 | 573.0626 | 768.9576 | 930.3693 | 1027.2028 | 1050.9835 | 52.5638 | 409.5436 | 89.3304 | 637.5935 | 14.278 | 49.8023 | 48.9294 | 51.8262 | 63.495 |  |  | 1.1607 | -1.117 | 0.2601 | -0.59075 | 8.086 | 6.2612 | 10.3376 | -2.8731 | 21.2817 | 56.6903 | 45.3657 | -2.793e-05 | -0.00011007 | -0.0007754 | 36.1949 | 16.9089 | 16.6735 | 17.0606 | 17.0834 | 16.085 | 14.7046 | 16.6854 | 17.0436 | 17.3909 | 17.476 | 17.2263 | 16.4165 | 14.7405 | 687.5533 | 478.1333 | 400.1396 | 274.4987 | 210.6087 | 759.1701 | 458.9436 | 31.0837 | 49.0011 | 54.5174 | 86.1114 | 88.2873 | 92.9258 |  |  |  | 647.4555 | 600.98 | 606.2443 | 630.1975 | 83.1035 | 27.4456 | 929.1369 |  |  | 829.8555 |  |  | 25.055 | 63.1994 | 602.9105 | 26.7883 | 65.9812 | 917.8038 | 748.7303 | 627.7604 | 912.0077 | 917.5197 | 757.2221 |  | 840.697 | 912.1804 | 1145.3615 | 601.6354 | 699.624 | 908.337 |  | 377.931 |  |  | 478.4491 | 667.1224 | 746.9429 | [6 empty] | 617.1504 |  |  | 454.3044 |  |  | 532.7754 | 689.249 | 701.6629 | 1079.4564 | 1158.7247 | 1086.1569 | 568.2159 | 737.5444 | 860.6763 | 637.423 | 724.4757 | 1098.2594 | 1137.9036 | 648.6089 | 832.0423 | 942.6739 | 1071.5911 | 1098.8916 | 560.7094 | 675.6959 | 713.4894 | 583.4101 | 751.9453 | 864.9807 | 1012.7309 | 1118.9189 | 620.5724 | 720.1163 | 676.2794 | 855.4521 | 107.0679 | 0.001348 | 17.6992 | 4.7056 | -40.3972 | 3.1208 | 9073.05 | 0.23 | 2.3251 | -2.3361 | 1.1273 | -1.6989 | 7.146 | 6.2882 | 8.0799 | 89.5928 | 236.0469 | 53.4947 | 72.3507 | 22.8211 | 82.5044 | 41.2059
42810.4543 | 1230 | 17.3927 | 17.822 | 17.9816 | 18.0257 | 17.3826 | 16.0556 | 15.3714 | 16.4796 | 16.9108 | 17.0687 | 17.0864 | 16.6271 | 15.665 | 14.4785 | 44.9413 | 61.6005 | 60.4541 | 90.2176 | 82.1081 | 94.5715 |  |  |  | 56.3174 | 88.9325 | 549.6608 | 678.3311 | 693.3098 | 685.7729 | 23.6072 | 61.4779 | 909.6867 | 23.6344 | 59.9222 | 763.8633 | 823.6109 | 771.7905 |  | 263.996 | 905.96 | 889.5592 | 781.816 |  | 489.2549 | 733.6183 | 573.7129 | 765.8402 | 925.0337 | 1023.7666 | 1048.3688 | 51.8176 | 409.47 | 86.307 | 637.4682 | 14.2803 | 49.7822 | 48.9297 | 51.8064 | 63.6737 |  |  | 1.3368 | -0.76676 | -0.26428 | -0.59206 | 8.4323 | 6.5832 | 10.6182 | -3.7832 | 20.6874 | 57.6269 | 45.774 | -0.00012485 | -9.199e-05 | -0.00075075 | 36.2909 | 16.893 | 16.6682 | 17.0472 | 17.0691 | 16.0845 | 14.6901 | 16.6812 | 17.0351 | 17.3815 | 17.4707 | 17.2132 | 16.4124 | 14.7317 | 691.5472 | 483.8144 | 420.8567 | 283.6981 | 213.2316 | 757.8102 | 458.1146 | 31.2016 | 49.0998 | 54.6113 | 86.1522 | 88.3304 | 92.9765 |  |  |  | 647.2438 | 601.3523 | 607.6014 | 628.8115 | 70.111 | 31.4482 | 929.09 |  |  | 833.6406 |  |  | 25.0972 | 63.2666 | 603.082 | 26.8444 | 66.0428 | 918.6848 | 749.7909 | 628.5254 | 915.4298 | 924.5829 | 756.2168 |  | 840.8198 | 914.0339 | 1142.968 | 602.1339 | 699.608 | 903.9483 |  | 380.2034 |  |  | 478.228 | 669.3358 | 746.2724 | [6 empty] | 617.8765 |  |  | 455.4013 |  |  | 532.9681 | 691.3848 | 702.7252 | 1076.816 | 1154.8731 | 1082.9866 | 569.1088 | 739.6244 | 860.0886 | 638.2033 | 726.8409 | 1089.4302 | 1136.658 | 649.194 | 834.2661 | 942.6647 | 1071.3695 | 1097.6928 | 560.7871 | 675.7753 | 713.5967 | 584.5712 | 753.1351 | 865.5487 | 1013.5829 | 1118.6785 | 620.6828 | 719.3609 | 677.3525 | 857.3816 | 96.1234 | -0.00060226 | 17.6979 | 4.6997 | -40.2592 | 3.1209 | 9048.5 | 0.34 | 2.4951 | -1.9363 | -1.1367 | -1.7014 | 7.2878 | 6.4393 | 8.178 | 89.6627 | 234.3834 | 53.477 | 71.4172 | 20.3534 | 83.202 | 41.2011
42810.4543 | 1231 | 17.3878 | 17.821 | 17.9712 | 18.0157 | 17.375 | 16.0528 | 15.3737 | 16.4795 | 16.9117 | 17.0621 | 17.0861 | 16.6208 | 15.662 | 14.4778 | 45.0899 | 61.7147 | 60.5727 | 90.1646 | 82.2364 | 94.5983 |  |  |  | 56.4628 | 88.9629 | 550.7568 | 678.977 | 694.0488 | 685.9491 | 25.591 | 61.521 | 910.8377 | 23.6628 | 59.9701 | 763.3504 | 825.1687 | 772.1061 |  | 262.76 | 908.6249 | 891.2231 | 778.2537 |  | 488.7777 | 733.6652 | 573.4767 | 762.4655 | 919.2529 | 1021.917 | 1048.0766 | 50.2074 | 409.5583 | 84.5972 | 637.2049 | 14.3272 | 49.7825 | 48.931 | 51.7821 | 63.8757 |  |  | 1.7153 | -0.42573 | -0.72558 | -1.5107 | 7.9145 | 5.3616 | 9.7482 | -2.8849 | 21.3836 | 56.3987 | 41.6983 | -0.00013471 | -3.45e-05 | -0.0007409 | 36.3869 | 16.9125 | 16.669 | 17.0454 | 17.0629 | 16.0827 | 14.6891 | 16.6718 | 17.0323 | 17.3822 | 17.4661 | 17.2189 | 16.4062 | 14.726 | 691.6262 | 485.5193 | 437.4476 | 288.8488 | 222.0239 | 755.8289 | 457.5785 | 31.3251 | 49.2234 | 54.716 | 86.1983 | 88.3582 | 93.0427 |  |  |  | 646.9033 | 600.7501 | 607.4678 | 627.3536 | 63.9913 | 25.5538 | 933.2566 |  |  | 847.2504 |  |  | 25.1451 | 63.3313 | 604.4355 | 26.9035 | 66.1062 | 921.1586 | 753.4182 | 630.9137 | 921.1922 | 930.0701 | 761.7717 |  | 841.5386 | 914.7593 | 1141.9126 | 603.8356 | 699.9279 | 916.8287 |  | 382.4069 |  |  | 479.0138 | 676.3426 | 749.7889 | [6 empty] | 619.9898 |  |  | 456.9468 |  |  | 532.583 | 693.5217 | 703.3413 | 1077.2069 | 1148.4803 | 1079.6437 | 569.72 | 745.9759 | 860.6588 | 638.8056 | 727.7196 | 1084.7741 | 1137.475 | 650.1841 | 839.8639 | 942.2509 | 1073.5192 | 1099.0912 | 560.6535 | 675.2735 | 713.6637 | 585.8565 | 754.3686 | 869.3517 | 1015.6412 | 1122.039 | 620.81 | 718.3143 | 678.3634 | 860.7641 | 85.2372 | -0.00020241 | 17.6974 | 4.6985 | -40.3077 | 3.1208 | 9041.12 | 0.29 | 2.8266 | -1.4428 | -1.8836 | -2.7179 | 7.0554 | 5.8071 | 7.8303 | 89.7539 | 233.6549 | 53.5055 | 70.6973 | 18.4029 | 83.8113 | 41.1719
42810.4543 | 1232 | 17.3888 | 17.8184 | 17.9689 | 18.0117 | 17.3762 | 16.0587 | 15.3715 | 16.4753 | 16.9156 | 17.0613 | 17.083 | 16.626 | 15.6622 | 14.4802 | 45.2369 | 61.8263 | 60.6926 | 90.106 | 82.3657 | 94.6186 |  |  |  | 56.6033 | 88.994 | 551.6647 | 679.5136 | 695.1949 | 686.6515 | 24.5054 | 61.6003 | 913.6372 | 24.6827 | 60.2508 | 763.3922 | 826.9397 | 773.7525 |  | 261.8665 | 911.0389 | 893.7171 | 780.019 |  | 487.8514 | 734.4397 | 572.8802 | 758.0013 | 917.5029 | 1022.5171 | 1047.0434 | 47.8367 | 409.7696 | 84.6357 | 637.2126 | 14.3916 | 49.7656 | 48.9499 | 51.7708 | 64.0892 |  |  | 1.6634 | -1.3102 | -0.44893 | -1.815 | 8.2568 | 6.8598 | 10.6104 | -2.3973 | 21.1855 | 55.9904 | 41.4771 | -9.528e-05 | -3.285e-05 | -0.00073761 | 36.4877 | 16.9143 | 16.6734 | 17.0503 | 17.0635 | 16.0839 | 14.7046 | 16.6831 | 17.0446 | 17.3817 | 17.4749 | 17.2221 | 16.4122 | 14.7414 | 680.6354 | 474.7763 | 422.9178 | 276.4213 | 220.042 | 753.1957 | 456.6393 | 31.4341 | 49.3233 | 54.8078 | 86.2245 | 88.3834 | 93.0862 |  |  |  | 646.7653 | 601.2694 | 606.6015 | 628.6762 | 68.2487 | 22.4826 | 936.8846 |  |  | 855.962 |  |  | 25.1934 | 63.397 | 604.9404 | 26.9704 | 66.1658 | 924.1299 | 752.7537 | 633.3757 | 925.5895 | 937.0468 | 763.2384 |  | 841.2669 | 910.7701 | 1141.0302 | 605.6021 | 700.3106 | 910.0442 |  | 384.535 |  |  | 479.8807 | 680.6019 | 750.8952 | [6 empty] | 622.2815 |  |  | 457.8521 |  |  | 532.2134 | 694.6389 | 703.747 | 1087.1444 | 1145.0974 | 1077.443 | 570.3591 | 750.8552 | 862.4014 | 640.0875 | 728.4386 | 1090.0876 | 1133.7996 | 650.8194 | 842.1836 | 944.1439 | 1076.8503 | 1101.8983 | 561.2297 | 674.7078 | 713.8437 | 586.9268 | 756.2887 | 875.7318 | 1016.344 | 1125.1605 | 620.7987 | 717.5794 | 679.7474 | 865.193 | 84.5805 | -0.00057423 | 17.6978 | 4.697 | -40.3412 | 3.1208 | 9054.58 | 0.33 | 2.7845 | -2.5321 | -1.4822 | -2.9802 | 7.2081 | 6.5701 | 8.1711 | 89.6203 | 233.1747 | 53.5471 | 70.9778 | 19.8301 | 84.3449 | 41.107
42810.4543 | 1233 | 17.3896 | 17.8229 | 17.9693 | 18.0174 | 17.3809 | 16.068 | 15.3829 | 16.4781 | 16.9042 | 17.061 | 17.0901 | 16.6257 | 15.6648 | 14.4853 | 45.3878 | 61.9412 | 60.8067 | 90.0559 | 82.45 | 94.6293 |  |  |  | 56.7445 | 89.0143 | 555.4007 | 682.2307 | 698.8879 | 689.6561 | 23.6999 | 61.6919 | 914.5238 | 24.015 | 60.182 | 767.7278 | 829.2235 | 778.7712 |  | 273.4732 | 910.039 | 892.1796 | 784.024 |  | 488.3665 | 734.8818 | 572.1937 | 759.6133 | 917.9965 | 1021.4592 | 1043.6352 | 46.0576 | 410.2137 | 85.4819 | 637.1766 | 14.4735 | 49.7394 | 48.9693 | 51.7547 | 64.334 |  |  | 1.4531 | -0.44675 | -0.011292 | -1.4305 | 8.1688 | 5.566 | 10.7602 | -3.385 | 21.1791 | 56.743 | 42.6695 | -5.257e-05 | -9.528e-05 | -0.00073925 | 36.5858 | 16.9231 | 16.6705 | 17.0539 | 17.0677 | 16.0804 | 14.7077 | 16.6793 | 17.0442 | 17.385 | 17.4764 | 17.219 | 16.4128 | 14.7355 | 670.2161 | 466.3954 | 405.0391 | 257.5838 | 212.36 | 750.8165 | 455.5325 | 31.5466 | 49.4234 | 54.8997 | 86.253 | 88.413 | 93.1255 |  |  |  | 646.6281 | 601.8478 | 606.4517 | 628.7528 | 85.5341 | 29.0634 | 942.2915 |  |  | 874.5926 |  |  | 25.2327 | 63.4615 | 607.9596 | 27.031 | 66.2301 | 924.6263 | 749.8568 | 634.4855 | 936.4354 | 947.43 | 760.0573 |  | 840.3936 | 911.3152 | 1140.8585 | 606.5415 | 700.6159 | 897.1342 |  | 386.8448 |  |  | 479.7482 | 679.9076 | 748.6179 | [6 empty] | 623.384 |  |  | 458.6649 |  |  | 532.1197 | 695.7565 | 705.2389 | 1090.6618 | 1148.8313 | 1075.4108 | 570.7613 | 751.6256 | 863.4899 | 640.9604 | 730.0664 | 1085.4729 | 1127.2942 | 650.9043 | 843.5607 | 946.0387 | 1078.1773 | 1105.7528 | 561.7119 | 674.3562 | 713.966 | 587.4582 | 757.6769 | 880.5778 | 1016.1983 | 1126.9542 | 620.6949 | 716.8232 | 680.8579 | 867.665 | 91.4041 | -4.1051e-05 | 17.6976 | 4.6944 | -40.3449 | 3.1209 | 9058.76 | 0.33 | 2.6067 | -1.4789 | -0.23512 | -2.6464 | 7.1666 | 5.9157 | 8.2252 | 89.4106 | 233.0447 | 53.5934 | 71.2897 | 21.5962 | 84.9888 | 41.0768
42810.4543 | 1234 | 17.3938 | 17.8175 | 17.9781 | 18.0137 | 17.3907 | 16.0677 | 15.3864 | 16.4892 | 16.9231 | 17.0708 | 17.0884 | 16.6277 | 15.6714 | 14.4863 | 45.53 | 62.0565 | 60.9277 | 90.0484 | 82.5384 | 94.6485 |  |  |  | 56.8891 | 89.0353 | 559.4528 | 685.2836 | 702.4508 | 692.6225 | 23.7318 | 61.743 | 913.2094 | 23.8549 | 60.4604 | 773.7408 | 832.1052 | 783.0737 |  | 269.9763 | 910.3999 | 892.237 | 792.5483 |  | 488.3915 | 735.7841 | 572.1313 | 763.6855 | 916.0317 | 1021.4025 | 1042.7183 | 45.2262 | 410.6279 | 86.2277 | 637.1478 | 14.5898 | 49.7299 | 48.9896 | 51.7411 | 64.5913 |  |  | 1.1561 | -0.67674 | -0.21434 | -1.5035 | 8.243 | 6.8441 | 10.036 | -1.7244 | 21.5708 | 56.8011 | 42.1531 | -9.199e-05 | 3.29e-06 | -0.00073761 | 36.6942 | 16.9418 | 16.6783 | 17.0577 | 17.0716 | 16.0859 | 14.7036 | 16.6906 | 17.0457 | 17.3937 | 17.4826 | 17.2222 | 16.4183 | 14.7417 | 705.9962 | 484.2441 | 417.6664 | 259.6895 | 217.441 | 750.869 | 454.8334 | 31.6584 | 49.5233 | 54.9918 | 86.2685 | 88.4444 | 93.1745 |  |  |  | 646.3766 | 600.9632 | 606.6521 | 626.5873 | 93.1397 | 33.4684 | 950.2985 |  |  | 873.3654 |  |  | 25.2871 | 63.5243 | 613.292 | 27.1048 | 66.2939 | 925.3566 | 747.1647 | 636.5092 | 940.2137 | 949.496 | 755.5234 |  | 839.6559 | 918.2714 | 1141.2763 | 608.606 | 701.1424 | 889.359 |  | 389.277 |  |  | 479.0292 | 675.1453 | 745.8066 | [6 empty] | 625.4122 |  |  | 460.1014 |  |  | 531.9858 | 696.6967 | 706.9481 | 1083.3851 | 1144.4608 | 1070.0221 | 570.905 | 750.8819 | 863.708 | 640.5844 | 731.0258 | 1076.2632 | 1120.115 | 650.55 | 845.1299 | 947.0196 | 1081.0026 | 1107.3558 | 560.965 | 674.1711 | 714.3306 | 588.7665 | 758.5518 | 881.904 | 1019.2399 | 1129.5447 | 620.6493 | 716.5729 | 683.6595 | 868.0126 | 98.0942 | 0.0017829 | 17.6978 | 4.6864 | -40.3588 | 3.1209 | 9109.31 | 0.26 | 2.3286 | -1.821 | -1.0248 | -2.7142 | 7.199 | 6.5597 | 7.9434 | 89.2852 | 233.1311 | 53.661 | 67.3328 | 20.0543 | 85.7111 | 41.0856
42810.4543 | 1235 | 17.3883 | 17.8109 | 17.9663 | 18.0095 | 17.3819 | 16.047 | 15.386 | 16.4786 | 16.9044 | 17.0493 | 17.0776 | 16.6139 | 15.6493 | 14.4778 | 45.6768 | 62.1765 | 61.0476 | 90.0408 | 82.6121 | 94.6555 |  |  |  | 57.0332 | 89.0618 | 562.0055 | 686.9065 | 704.2246 | 694.0186 | 23.7892 | 61.8067 | 915.5126 | 23.8986 | 60.2658 | 778.5738 | 834.9255 | 785.877 |  | 266.4887 | 914.4242 | 895.7759 | 794.5628 |  | 489.3599 | 736.632 | 570.7328 | 769.2816 | 921.9074 | 1025.2677 | 1044.9139 | 46.1578 | 411.0801 | 85.5225 | 637.0078 | 14.695 | 49.7205 | 49.0172 | 51.717 | 64.767 |  |  | 1.2034 | -0.49866 | -0.048748 | -0.52635 | 8.0998 | 6.4182 | 10.4894 | -2.6253 | 22.6143 | 57.9724 | 42.472 | -6.735e-05 | -1.971e-05 | -0.00076225 | 36.8006 | 16.9395 | 16.6764 | 17.0575 | 17.0694 | 16.0899 | 14.7031 | 16.6963 | 17.05 | 17.3956 | 17.4748 | 17.2287 | 16.4102 | 14.7419 | 740.1957 | 494.144 | 436.325 | 262.7669 | 221.5313 | 751.9227 | 454.5821 | 31.7873 | 49.6458 | 55.1002 | 86.3211 | 88.4924 | 93.2187 |  |  |  | 645.9252 | 599.5019 | 607.2229 | 624.1672 | 93.037 | 31.933 | 952.1552 |  |  | 877.1356 |  |  | 25.3339 | 63.5901 | 616.2264 | 27.1623 | 66.3629 | 928.5221 | 746.0828 | 640.2956 | 944.6787 | 954.0684 | 752.6205 |  | 839.4032 | 917.1434 | 1140.1571 | 612.3252 | 701.8837 | 878.1471 |  | 391.4835 |  |  | 477.3342 | 671.8044 | 743.6288 | [6 empty] | 629.2821 |  |  | 461.93 |  |  | 531.8411 | 696.3742 | 707.7762 | 1087.9814 | 1144.2764 | 1068.551 | 570.718 | 750.6162 | 863.6801 | 639.9012 | 731.086 | 1084.0957 | 1126.0404 | 650.3051 | 847.7072 | 945.5816 | 1084.0899 | 1106.3374 | 560.525 | 674.0863 | 714.9333 | 590.682 | 759.2702 | 885.0193 | 1022.0138 | 1132.1142 | 620.9953 | 717.0274 | 685.7457 | 869.3761 | 101.8881 | 0.0053607 | 17.6972 | 4.6832 | -40.4159 | 3.1209 | 9153.59 | 0.33 | 2.3775 | -1.5638 | -0.48894 | -1.6066 | 7.1468 | 6.3618 | 8.133 | 89.2799 | 232.4139 | 53.7339 | 63.907 | 17.9312 | 86.6004 | 41.0608
42810.4543 | 1236 | 17.3928 | 17.8064 | 17.9719 | 18.01 | 17.3784 | 16.0579 | 15.3983 | 16.4956 | 16.9016 | 17.0579 | 17.0835 | 16.6167 | 15.6662 | 14.4831 | 45.8196 | 62.2704 | 61.1517 | 90.0005 | 82.6888 | 94.6396 |  |  |  | 57.173 | 89.0708 | 563.2685 | 687.5686 | 704.5661 | 694.1529 | 23.8334 | 61.8547 | 916.8006 | 23.9313 | 60.3263 | 781.7423 | 836.5544 | 787.3264 |  | 259.2704 | 914.3033 | 895.6208 | 797.803 |  | 488.9283 | 736.5527 | 569.7143 | 768.8003 | 919.3183 | 1025.275 | 1047.2167 | 48.5839 | 411.2129 | 84.7731 | 637.0487 | 14.7559 | 49.6667 | 49.0525 | 51.7058 | 65.0186 |  |  | 1.321 | -1.508 | 0.15496 | -0.4291 | 9.46 | 8.3219 | 10.2358 | -2.4749 | 21.7586 | 56.1534 | 43.8033 | -9.035e-05 | -0.00015278 | -0.00072775 | 36.8955 | 16.9446 | 16.6723 | 17.0451 | 17.0597 | 16.0719 | 14.6996 | 16.6808 | 17.0373 | 17.3823 | 17.474 | 17.2185 | 16.4145 | 14.7345 | 760.4661 | 508.577 | 465.4142 | 275.2769 | 221.5426 | 753.4165 | 454.6503 | 31.9092 | 49.7408 | 55.1902 | 86.3619 | 88.532 | 93.2779 |  |  |  | 645.6516 | 599.1442 | 606.3126 | 625.154 | 89.5191 | 39.831 | 954.6388 |  |  | 876.1409 |  |  | 25.3885 | 63.6607 | 617.5609 | 27.2259 | 66.4282 | 929.2481 | 747.492 | 644.2814 | 951.2395 | 961.9259 | 753.8417 |  | 839.7222 | 925.4631 | 1140.0425 | 616.4463 | 702.7014 | 869.2084 |  | 393.6187 |  |  | 477.282 | 673.7353 | 744.7607 | [6 empty] | 633.5677 |  |  | 464.5049 |  |  | 531.7041 | 695.6318 | 707.8588 | 1091.1746 | 1149.8708 | 1072.4431 | 570.6452 | 749.8054 | 864.7617 | 639.4578 | 730.0796 | 1084.4164 | 1128.35 | 649.7964 | 852.268 | 943.9712 | 1086.0689 | 1105.9117 | 561.2053 | 674.117 | 715.9135 | 591.7618 | 758.9902 | 885.0346 | 1022.5693 | 1134.7216 | 620.7802 | 717.4975 | 686.4082 | 868.7681 | 115.6363 | 0.0011235 | 17.6973 | 4.6784 | -40.2877 | 3.1209 | 9194.32 | 0.29 | 2.4912 | -2.7193 | 0.87171 | -1.4506 | 7.7236 | 7.2441 | 8.0341 | 89.3545 | 232.1063 | 53.8143 | 62.1864 | 14.7126 | 87.0594 | 40.9776
42810.4544 | 1237 | 17.3907 | 17.8162 | 17.9781 | 18.0265 | 17.3791 | 16.0616 | 15.4012 | 16.4922 | 16.9096 | 17.0676 | 17.0889 | 16.6264 | 15.6731 | 14.4868 | 45.9484 | 62.3779 | 61.2702 | 89.9409 | 82.7672 | 94.6442 |  |  |  | 57.3059 | 89.082 | 563.5543 | 687.4946 | 704.2304 | 693.9836 | 23.8855 | 61.918 | 918.3055 | 23.9801 | 60.3888 | 784.2469 | 838.1037 | 788.4522 |  | 269.1541 | 916.1226 | 897.3526 | 799.9117 |  | 487.3526 | 737.7824 | 568.9489 | 767.6074 | 921.7558 | 1026.6692 | 1048.6191 | 51.4455 | 411.1922 | 83.7222 | 636.9818 | 14.8087 | 49.6338 | 49.0999 | 51.7394 | 65.1816 |  |  | 1.551 | -1.6066 | -0.003408 | -0.73991 | 7.8468 | 6.7685 | 10.6439 | -2.8225 | 21.0022 | 55.6585 | 39.9082 | -8.707e-05 | -4.107e-05 | -0.00073433 | 36.9861 | 16.9499 | 16.6715 | 17.0476 | 17.0604 | 16.0749 | 14.6997 | 16.6859 | 17.0371 | 17.3825 | 17.4691 | 17.2131 | 16.4112 | 14.7386 | 764.3508 | 506.6528 | 477.1958 | 297.2879 | 235.6721 | 754.3098 | 454.8195 | 32.0301 | 49.8417 | 55.2748 | 86.3938 | 88.5695 | 93.3193 |  |  |  | 645.4616 | 599.5639 | 605.2105 | 625.651 | 89.3416 | 27.9398 | 960.418 |  |  | 879.9627 |  |  | 25.4413 | 63.7287 | 617.491 | 27.2916 | 66.4883 | 930.5652 | 749.4953 | 647.6749 | 950.3354 | 958.3423 | 755.5841 |  | 840.28 | 925.304 | 1143.102 | 620.2311 | 703.7154 | 880.0239 |  | 396.0784 |  |  | 476.9017 | 674.0696 | 745.8586 | [6 empty] | 637.0954 |  |  | 466.2605 |  |  | 532.0255 | 695.168 | 707.9263 | 1069.8596 | 1150.1179 | 1071.661 | 571.0663 | 750.2603 | 864.8523 | 639.3468 | 729.6771 | 1073.2418 | 1128.2268 | 650.1184 | 852.5273 | 945.4426 | 1086.7595 | 1105.9619 | 561.0602 | 673.4058 | 715.5844 | 592.815 | 758.1994 | 884.0859 | 1023.3989 | 1135.274 | 620.368 | 716.6651 | 686.9819 | 867.6887 | 121.7973 | -0.00022343 | 17.6969 | 4.6767 | -40.2754 | 3.1208 | 9192.59 | 0.31 | 2.6991 | -2.8085 | -0.12935 | -1.906 | 7.0381 | 6.5366 | 8.1971 | 89.4961 | 234.1604 | 53.9514 | 62.0735 | 13.4372 | 87.525 | 40.9251
42810.4544 | 1238 | 17.3846 | 17.8063 | 17.9735 | 18.0172 | 17.3781 | 16.0511 | 15.3966 | 16.4873 | 16.9044 | 17.0627 | 17.0803 | 16.6183 | 15.6567 | 14.4811 | 46.0895 | 62.4923 | 61.383 | 89.8971 | 82.8699 | 94.6591 |  |  |  | 57.4328 | 89.0974 | 561.7948 | 685.841 | 701.9838 | 692.5101 | 23.9814 | 61.9818 | 919.9692 | 24.0371 | 60.4558 | 784.4429 | 839.4551 | 787.9542 |  | 270.2105 | 917.0604 | 897.8041 | 798.2951 |  | 487.6466 | 738.7 | 569.9025 | 766.0723 | 925.9169 | 1027.6322 | 1049.66 | 53.6277 | 411.2018 | 83.7671 | 636.8296 | 14.85 | 49.6461 | 49.1302 | 51.8054 | 65.1461 |  |  | 1.2862 | -0.59 | -0.029692 | -0.50861 | 8.4375 | 7.2318 | 10.6859 | -2.4282 | 21.6452 | 56.6179 | 43.8444 | -0.00014949 | -7.885e-05 | -0.00074254 | 37.1005 | 16.9701 | 16.6778 | 17.054 | 17.0704 | 16.0796 | 14.7074 | 16.6815 | 17.0419 | 17.3861 | 17.4733 | 17.2246 | 16.4144 | 14.7402 | 768.5307 | 518.6557 | 473.2133 | 293.1086 | 236.5101 | 755.3356 | 454.7875 | 32.1384 | 49.9286 | 55.3597 | 86.4218 | 88.6006 | 93.3653 |  |  |  | 645.2183 | 599.2856 | 604.1909 | 624.9102 | 77.7794 | 42.5048 | 959.3666 |  |  | 875.8446 |  |  | 25.4925 | 63.7967 | 615.82 | 27.3518 | 66.5517 | 932.363 | 752.6814 | 650.6047 | 946.8084 | 954.302 | 762.3611 |  | 841.7908 | 927.7983 | 1143.1785 | 623.078 | 704.506 | 874.3453 |  | 398.2617 |  |  | 478.3502 | 680.0226 | 750.7669 | [6 empty] | 640.5515 |  |  | 467.5504 |  |  | 532.3961 | 695.5609 | 708.0192 | 1074.5901 | 1153.882 | 1076.6611 | 571.9824 | 750.1882 | 864.3774 | 638.8193 | 729.6082 | 1069.6628 | 1136.7505 | 650.7981 | 855.773 | 942.4233 | 1088.5996 | 1106.5129 | 560.4055 | 672.4472 | 715.5542 | 593.9614 | 758.1028 | 882.8084 | 1022.4618 | 1135.205 | 619.7784 | 716.7461 | 688.2918 | 865.6347 | 99.1557 | 0.00024657 | 17.699 | 4.6765 | -40.3905 | 3.1209 | 9196.7 | 0.26 | 2.456 | -1.7028 | -0.38198 | -1.5809 | 7.3009 | 6.7591 | 8.2163 | 89.8238 | 234.1425 | 54.0616 | 61.9758 | 13.8733 | 88.0288 | 40.8962
42810.4544 | 1239 | 17.3908 | 17.8056 | 17.9621 | 18.009 | 17.3729 | 16.0511 | 15.3947 | 16.4865 | 16.8982 | 17.0524 | 17.0762 | 16.6207 | 15.6527 | 14.475 | 46.2393 | 62.5995 | 61.5018 | 89.8461 | 83.0172 | 94.6819 |  |  |  | 57.58 | 89.1125 | 560.1792 | 684.3401 | 700.0592 | 691.0496 | 24.0102 | 62.0778 | 920.6509 | 24.0758 | 60.5126 | 785.0112 | 840.8662 | 790.3191 |  | 274.3295 | 918.7731 | 898.9195 | 802.9715 |  | 488.4676 | 739.9477 | 570.3265 | 765.2015 | 927.5749 | 1028.2631 | 1049.3604 | 56.7973 | 411.5058 | 85.0694 | 636.8706 | 14.8446 | 49.6878 | 49.1365 | 51.8805 | 64.9351 |  |  | 1.4413 | 0.97525 | -0.47062 | -1.2144 | 8.2798 | 6.8717 | 10.8318 | -2.5701 | 22.2381 | 57.5452 | 42.0603 | -9.199e-05 | -8.05e-05 | -0.00072611 | 37.1871 | 16.9687 | 16.6721 | 17.0514 | 17.06 | 16.0754 | 14.7061 | 16.6782 | 17.0326 | 17.3846 | 17.471 | 17.2179 | 16.4073 | 14.7322 | 760.2273 | 538.3386 | 507.5336 | 314.6316 | 255.15 | 755.9043 | 455.3258 | 32.2573 | 50.0334 | 55.4498 | 86.4649 | 88.6459 | 93.4136 |  |  |  | 645.032 | 598.3581 | 603.2402 | 626.0762 | 88.313 | 38.2517 | 957.1689 |  |  | 862.7974 |  |  | 25.542 | 63.8649 | 613.5385 | 27.4118 | 66.6107 | 934.0168 | 753.1557 | 652.4096 | 939.5346 | 948.7061 | 764.2534 |  | 842.848 | 923.9984 | 1142.3293 | 625.1172 | 705.2171 | 875.4567 |  | 400.3921 |  |  | 479.8365 | 678.4373 | 752.7648 | [6 empty] | 642.9116 |  |  | 468.3123 |  |  | 532.9293 | 696.4935 | 708.7829 | 1066.4938 | 1148.2711 | 1092.3473 | 571.4689 | 753.5603 | 868.1178 | 639.1092 | 732.4104 | 1059.7349 | 1144.7804 | 652.351 | 866.4334 | 938.997 | 1090.3426 | 1108.9201 | 560.0892 | 671.9182 | 715.8897 | 597.7542 | 760.985 | 882.2436 | 1027.2769 | 1137.7491 | 619.6487 | 716.4404 | 694.2189 | 871.7363 | 96.6969 | -0.00067245 | 17.6985 | 4.6771 | -40.3219 | 3.1208 | 9211.71 | 0.32 | 2.5979 | 2.1905 | -1.5217 | -2.4444 | 7.2341 | 6.5903 | 8.2742 | 90.1334 | 233.6778 | 54.1756 | 63.102 | 10.1669 | 88.3798 | 40.8259
42810.4544 | 1240 | 17.3979 | 17.8199 | 17.9653 | 18.0172 | 17.3821 | 16.0635 | 15.4068 | 16.4924 | 16.9147 | 17.0634 | 17.0861 | 16.6235 | 15.6632 | 14.4888 | 46.4007 | 62.7271 | 61.6244 | 89.8253 | 83.2003 | 94.7155 |  |  |  | 57.7379 | 89.1351 | 560.4681 | 684.2859 | 700.4404 | 691.0983 | 24.8975 | 62.1594 | 923.8294 | 24.1541 | 60.5884 | 795.6047 | 844.3727 | 800.0125 |  | 280.7028 | 922.9747 | 902.4598 | 815.994 |  | 487.7402 | 739.0312 | 570.1681 | 763.9014 | 929.0294 | 1028.9859 | 1051.8057 | 59.2558 | 411.8044 | 86.3451 | 637.2444 | 14.8707 | 49.754 | 49.1298 | 51.9437 | 64.667 |  |  | 1.5582 | -0.682 | -0.35496 | -0.97713 | 8.1438 | 7.1641 | 11.7485 | -2.8941 | 21.6714 | 56.5646 | 37.6108 | -0.00014621 | -0.00014128 | -0.00074582 | 37.3005 | 16.9817 | 16.6841 | 17.051 | 17.0689 | 16.0815 | 14.7156 | 16.6912 | 17.0472 | 17.3902 | 17.477 | 17.2287 | 16.4177 | 14.7424 | 759.6003 | 539.483 | 500.6401 | 317.6243 | 273.8312 | 756.4431 | 455.9702 | 32.3846 | 50.1602 | 55.5624 | 86.5188 | 88.6883 | 93.4683 |  |  |  | 644.8496 | 597.6145 | 603.6882 | 625.4829 | 80.7118 | 34.2795 | 954.0741 |  |  | 856.1318 |  |  | 25.5917 | 63.9247 | 612.634 | 27.4752 | 66.6659 | 938.7163 | 752.1177 | 653.1962 | 933.7097 | 942.6914 | 760.8865 |  | 843.2098 | 919.9774 | 1142.4863 | 626.0161 | 705.9612 | 878.6611 |  | 402.8448 |  |  | 480.079 | 673.9787 | 751.2282 | [6 empty] | 643.6425 |  |  | 469.6751 |  |  | 532.9222 | 700.3901 | 710.0351 | 1049.1697 | 1144.4077 | 1100.4798 | 571.1145 | 755.6982 | 871.7685 | 639.8469 | 736.584 | 1047.9005 | 1152.7684 | 652.8899 | 868.9785 | 937.6759 | 1096.4534 | 1112.5063 | 561.4772 | 672.1356 | 716.0039 | 602.5286 | 768.4128 | 889.4474 | 1030.3902 | 1139.838 | 619.3703 | 715.9876 | 702.0372 | 886.8999 | 96.9808 | -0.0011916 | 17.6991 | 4.6771 | -40.4761 | 3.1208 | 9230.43 | 0.3 | 2.7013 | -1.831 | -1.321 | -2.1917 | 7.1764 | 6.7309 | 8.6196 | 90.351 | 233.8949 | 54.3295 | 63.3648 | 11.061 | 89.2201 | 40.8053
42810.4544 | 1241 | 17.3917 | 17.8109 | 17.9705 | 18.0134 | 17.3766 | 16.0595 | 15.4068 | 16.495 | 16.9046 | 17.0644 | 17.0894 | 16.6223 | 15.6597 | 14.4904 | 46.5326 | 62.8321 | 61.7256 | 89.8038 | 83.448 | 94.7403 |  |  |  | 57.8697 | 89.1427 | 563.8887 | 687.1359 | 703.9896 | 694.4186 | 24.1636 | 62.1728 | 925.2826 | 24.2026 | 60.6624 | 811.8632 | 849.6583 | 815.3649 |  | 281.0733 | 922.5042 | 901.1807 | 831.8882 |  | 487.2671 | 738.081 | 570.4105 | 763.1659 | 928.3171 | 1031.3575 | 1054.0734 | 61.3335 | 412.059 | 89.2885 | 637.5361 | 14.8998 | 49.8014 | 49.1057 | 51.9922 | 64.4017 |  |  | 1.2967 | -1.0112 | -0.11249 | -0.95085 | 7.741 | 5.9734 | 9.6188 | -3.1247 | 21.558 | 54.2073 | 38.3267 | -6.571e-05 | -6.242e-05 | -0.00074747 | 37.4011 | 16.9898 | 16.6801 | 17.0541 | 17.0705 | 16.0853 | 14.7162 | 16.6936 | 17.0494 | 17.3974 | 17.4804 | 17.2251 | 16.4205 | 14.7557 | 741.6144 | 524.5325 | 486.8915 | 307.0276 | 257.9063 | 756.0471 | 456.346 | 32.5002 | 50.2594 | 55.6506 | 86.5602 | 88.7255 | 93.5049 |  |  |  | 644.5761 | 597.5624 | 604.3229 | 625.5361 | 68.1393 | 30.8405 | 950.3328 |  |  | 850.8665 |  |  | 25.6443 | 63.9942 | 615.1578 | 27.5567 | 66.733 | 939.2928 | 751.8248 | 653.7184 | 927.1035 | 935.1665 | 757.248 |  | 843.492 | 917.2376 | 1143.3554 | 626.152 | 706.4211 | 889.3434 |  | 405.1434 |  |  | 479.7133 | 673.0285 | 750.0747 | [6 empty] | 643.4654 |  |  | 469.5324 |  |  | 532.8578 | 705.5388 | 711.5435 | 1042.3685 | 1140.84 | 1099.7929 | 570.3687 | 754.3474 | 872.7518 | 640.8551 | 739.4913 | 1040.5472 | 1153.7781 | 652.3957 | 864.2855 | 936.8544 | 1100.8071 | 1114.4391 | 562.4017 | 672.2412 | 717.06 | 607.7381 | 779.2451 | 901.6128 | 1027.4278 | 1139.6974 | 619.8784 | 716.0885 | 711.4198 | 908.8255 | 99.1659 | -0.00032867 | 17.6992 | 4.6781 | -40.2999 | 3.1208 | 9240.7 | 0.39 | 2.4685 | -2.2285 | -0.74327 | -2.161 | 7.0031 | 6.1518 | 7.8064 | 90.549 | 234.5548 | 54.4365 | 65.2212 | 12.6634 | 90.6104 | 40.7483
42810.4544 | 1242 | 17.3893 | 17.8125 | 17.9718 | 18.0145 | 17.3847 | 16.0613 | 15.406 | 16.4955 | 16.9088 | 17.0707 | 17.0873 | 16.6283 | 15.6609 | 14.4925 | 46.6769 | 62.9362 | 61.8437 | 89.7858 | 83.6213 | 94.7488 |  |  |  | 58.0057 | 89.157 | 568.7864 | 691.3948 | 708.3068 | 698.7768 | 24.1535 | 62.2381 | 923.5199 | 24.279 | 60.7361 | 825.5813 | 856.2823 | 827.9505 |  | 270.5631 | 920.0585 | 898.1339 | 841.9367 |  | 487.8401 | 736.0186 | 570.3809 | 767.4087 | 929.4914 | 1029.7209 | 1053.4512 | 63.6702 | 412.3144 | 92.9715 | 637.9103 | 14.8663 | 49.8376 | 49.0886 | 52.0615 | 64.1926 |  |  | 1.3447 | -2.0238 | 0.083332 | -1.0218 | 8.0288 | 7.2981 | 10.7562 | -2.9007 | 21.9489 | 57.4913 | 39.8794 | -0.00012649 | -7.557e-05 | -0.00074582 | 37.5008 | 16.989 | 16.6797 | 17.0537 | 17.0583 | 16.0862 | 14.7127 | 16.6945 | 17.0421 | 17.397 | 17.479 | 17.2235 | 16.414 | 14.7483 | 727.3276 | 517.4012 | 470.2307 | 293.5691 | 249.93 | 755.2783 | 456.5193 | 32.6219 | 50.3548 | 55.743 | 86.6097 | 88.7696 | 93.552 |  |  |  | 644.571 | 598.3461 | 605.3513 | 627.9102 | 86.2416 | 39.4917 | 944.9198 |  |  | 847.0914 |  |  | 25.6972 | 64.0627 | 620.1473 | 27.6182 | 66.7911 | 935.3328 | 752.8945 | 655.6373 | 923.0688 | 930.6084 | 756.102 |  | 843.8437 | 919.4247 | 1141.7605 | 627.6743 | 707.0887 | 896.4793 |  | 407.3943 |  |  | 479.5526 | 675.2207 | 750.2714 | [6 empty] | 645.1351 |  |  | 470.5109 |  |  | 532.7911 | 707.3178 | 712.6009 | 1036.3545 | 1137.6924 | 1096.9709 | 569.5594 | 753.854 | 873.8346 | 641.2289 | 739.7395 | 1034.2352 | 1145.9479 | 652.2137 | 864.958 | 932.8719 | 1101.8037 | 1116.4035 | 563.5922 | 673.0805 | 720.382 | 610.5051 | 790.8943 | 912.7763 | 1026.8322 | 1139.3337 | 621.0004 | 717.0238 | 716.8653 | 925.6716 | 103.0194 | -0.00069348 | 17.6973 | 4.6799 | -40.4079 | 3.1208 | 9250.44 | 0.24 | 2.5194 | -3.1495 | 0.63908 | -2.2379 | 7.1276 | 6.7955 | 8.2499 | 90.7017 | 233.4234 | 54.5552 | 66.5333 | 14.5492 | 92.6607 | 40.6813
42810.4544 | 1243 | 17.398 | 17.8193 | 17.9701 | 18.0217 | 17.3839 | 16.0616 | 15.4235 | 16.4906 | 16.9129 | 17.071 | 17.0906 | 16.6317 | 15.6681 | 14.4856 | 46.8182 | 63.0428 | 61.9583 | 89.7655 | 83.7135 | 94.7665 |  |  |  | 58.1339 | 89.1733 | 573.0375 | 694.8022 | 711.9171 | 701.8539 | 24.199 | 62.3234 | 921.7608 | 24.4166 | 60.8441 | 833.2519 | 862.7921 | 833.4486 |  | 259.4856 | 918.5409 | 895.9964 | 842.3044 |  | 487.2896 | 736.0873 | 569.9182 | 770.0538 | 928.5282 | 1029.0078 | 1052.8678 | 65.0664 | 412.6462 | 97.8098 | 638.4738 | 14.8597 | 49.8529 | 49.0775 | 52.1755 | 64.0368 |  |  | 1.415 | -0.9869 | -0.47719 | -1.194 | 7.7397 | 6.1311 | 10.3659 | -2.9868 | 21.5457 | 57.5874 | 40.7433 | -7.721e-05 | -0.00012814 | -0.00076225 | 37.5843 | 16.994 | 16.6697 | 17.0409 | 17.0518 | 16.0771 | 14.6971 | 16.6839 | 17.0359 | 17.3832 | 17.4645 | 17.2126 | 16.4037 | 14.7462 | 751.0054 | 530.2011 | 501.7764 | 305.472 | 259.5639 | 755.6647 | 457.3596 | 32.7421 | 50.4623 | 55.832 | 86.6463 | 88.7991 | 93.6053 |  |  |  | 644.6952 | 600.3887 | 606.9255 | 631.0657 | 87.0573 | 33.8664 | 940.9608 |  |  | 845.869 |  |  | 25.7432 | 64.1346 | 624.7071 | 27.6759 | 66.8505 | 932.7112 | 755.4461 | 658.8562 | 924.4744 | 931.8857 | 757.6278 |  | 844.3597 | 921.7305 | 1138.573 | 630.5525 | 707.9996 | 899.4729 |  | 409.8229 |  |  | 479.8677 | 680.0103 | 751.9844 | [6 empty] | 648.2054 |  |  | 472.5615 |  |  | 532.4316 | 706.5267 | 713.4681 | 1039.3978 | 1134.9315 | 1094.6721 | 569.0539 | 754.7461 | 874.7446 | 641.0658 | 738.525 | 1030.2829 | 1143.7205 | 652.6135 | 864.5712 | 928.7037 | 1102.8242 | 1118.2849 | 564.2702 | 673.8158 | 724.1122 | 612.4863 | 797.9468 | 920.1278 | 1029.7816 | 1138.8912 | 621.5872 | 718.2674 | 721.3204 | 931.5217 | 108.3236 | -4.1051e-05 | 17.6973 | 4.6821 | -40.3544 | 3.1208 | 9290.59 | 0.36 | 2.5885 | -2.1994 | -1.5294 | -2.4191 | 6.9962 | 6.2268 | 8.0966 | 90.8369 | 231.23 | 54.6954 | 64.0408 | 11.2116 | 94.9769 | 40.6189
42810.4544 | 1244 | 17.3948 | 17.8129 | 17.9703 | 18.0092 | 17.3786 | 16.0609 | 15.4188 | 16.4879 | 16.9064 | 17.0606 | 17.0848 | 16.6273 | 15.665 | 14.4883 | 46.9568 | 63.1537 | 62.0672 | 89.7354 | 83.7395 | 94.7744 |  |  |  | 58.2672 | 89.1979 | 577.0855 | 697.3321 | 714.722 | 703.9894 | 24.2544 | 62.3458 | 919.1172 | 24.3548 | 60.861 | 827.3968 | 866.5269 | 828.7728 |  | 267.0982 | 916.8107 | 893.6673 | 835.0231 |  | 485.1798 | 738.09 | 570.3841 | 770.6114 | 930.3856 | 1031.3223 | 1053.4966 | 65.1483 | 413.0885 | 101.4688 | 639.0341 | 14.8721 | 49.8895 | 49.0867 | 52.3635 | 63.9619 |  |  | 1.5753 | -0.56897 | 0.28112 | -1.0645 | 8.6458 | 5.5587 | 9.9066 | -2.6444 | 21.7617 | 58.0414 | 36.3743 | -9.199e-05 | -0.00012485 | -0.00074418 | 37.695 | 17.0042 | 16.6715 | 17.0461 | 17.0556 | 16.0783 | 14.6969 | 16.6893 | 17.0462 | 17.3844 | 17.4741 | 17.2192 | 16.4107 | 14.7382 | 758.9131 | 536.8425 | 508.2631 | 320.0682 | 269.0404 | 756.3229 | 458.0095 | 32.8557 | 50.5581 | 55.9272 | 86.6789 | 88.8395 | 93.6533 |  |  |  | 645.0224 | 602.8523 | 608.2475 | 633.9954 | 86.7082 | 28.9474 | 940.6171 |  |  | 852.4212 |  |  | 25.7952 | 64.2069 | 628.8156 | 27.7418 | 66.9151 | 929.8757 | 759.9701 | 663.3044 | 923.6446 | 931.4803 | 762.0985 |  | 845.4143 | 915.7377 | 1136.6746 | 635.1092 | 709.1673 | 903.8414 |  | 412.4253 |  |  | 480.3394 | 687.8849 | 755.6776 | [6 empty] | 652.7541 |  |  | 476.3983 |  |  | 532.2039 | 705.3623 | 713.7744 | 1048.5632 | 1136.0752 | 1095.7365 | 568.839 | 755.8966 | 875.6141 | 640.8732 | 736.7193 | 1031.6866 | 1143.4997 | 653.0821 | 865.9419 | 927.1874 | 1102.8659 | 1119.9672 | 564.8442 | 674.2846 | 725.7224 | 615.6593 | 804.799 | 927.0138 | 1030.9225 | 1138.6357 | 621.8901 | 718.8634 | 725.848 | 936.2089 | 108.9112 | 0.00056226 | 17.6957 | 4.689 | -40.3025 | 3.1208 | 9353.23 | 0.26 | 2.7342 | -1.6716 | 1.175 | -2.2865 | 7.401 | 5.9343 | 7.9222 | 91.0763 | 230.1348 | 54.8519 | 63.398 | 10.6206 | 96.5306 | 40.604
42810.4544 | 1245 | 17.3858 | 17.8012 | 17.9622 | 18.0109 | 17.3744 | 16.0526 | 15.4211 | 16.4896 | 16.9077 | 17.0548 | 17.0814 | 16.6208 | 15.659 | 14.4826 | 47.0959 | 63.2519 | 62.1743 | 89.7005 | 83.7164 | 94.758 |  |  |  | 58.399 | 89.2104 | 581.4036 | 699.7573 | 717.6329 | 706.2054 | 24.3204 | 62.411 | 915.8996 | 24.3972 | 60.9224 | 824.4081 | 869.7856 | 826.5465 |  | 269.2189 | 912.5118 | 888.5944 | 833.9525 |  | 484.7187 | 740.6739 | 570.4702 | 773.8168 | 934.9592 | 1033.1506 | 1058.0953 | 64.6707 | 413.4422 | 102.8535 | 639.5546 | 14.9117 | 49.9 | 49.1047 | 52.535 | 63.9536 |  |  | 1.3243 | -0.86008 | -0.14797 | -0.76488 | 8.2424 | 5.7618 | 10.3955 | -3.3837 | 22.4625 | 56.6213 | 38.4748 | -6.407e-05 | -8.214e-05 | -0.00079511 | 37.8039 | 17.0193 | 16.6797 | 17.0464 | 17.0628 | 16.0777 | 14.7061 | 16.6941 | 17.0399 | 17.3835 | 17.4694 | 17.2133 | 16.4158 | 14.7416 | 757.8632 | 526.4482 | 487.5164 | 325.7103 | 276.808 | 756.5489 | 458.0208 | 32.9943 | 50.6708 | 56.0252 | 86.7213 | 88.8721 | 93.6978 |  |  |  | 645.2355 | 604.0395 | 608.3663 | 633.7457 | 82.5115 | 29.162 | 940.0942 |  |  | 855.5261 |  |  | 25.8404 | 64.2682 | 632.3937 | 27.8057 | 66.9695 | 925.7019 | 765.6882 | 668.1341 | 917.5891 | 924.6917 | 767.615 |  | 846.8529 | 913.4525 | 1135.2394 | 639.7884 | 710.2668 | 912.7693 |  | 414.934 |  |  | 481.4471 | 697.7587 | 761.2083 | [6 empty] | 658.3198 |  |  | 481.5119 |  |  | 532.1887 | 703.9319 | 713.5295 | 1051.2837 | 1139.9372 | 1096.4203 | 568.3326 | 757.7782 | 877.2316 | 640.4291 | 735.1865 | 1039.0438 | 1144.9997 | 653.9576 | 868.6688 | 928.9856 | 1100.469 | 1120.9993 | 565.3051 | 674.4747 | 726.6365 | 618.639 | 809.546 | 933.3304 | 1029.1604 | 1138.1177 | 621.7796 | 718.8818 | 728.4521 | 937.9124 | 104.8886 | -0.0002375 | 17.6924 | 4.7045 | -40.4167 | 3.1208 | 9382.9 | 0.24 | 2.5098 | -2.0579 | -0.85357 | -1.9406 | 7.2313 | 6.046 | 8.121 | 91.4205 | 229.2477 | 54.9892 | 63.5957 | 12.9281 | 97.7496 | 40.6543
42810.4545 | 1246 | 17.3759 | 17.8043 | 17.9684 | 18.0118 | 17.3731 | 16.0553 | 15.4224 | 16.4898 | 16.906 | 17.0607 | 17.0814 | 16.6226 | 15.6639 | 14.4868 | 47.2451 | 63.3737 | 62.2956 | 89.6924 | 83.7843 | 94.7838 |  |  |  | 58.5413 | 89.2231 | 586.141 | 702.734 | 721.5248 | 709.4863 | 24.3698 | 62.4771 | 911.4579 | 24.4573 | 61.0017 | 822.95 | 873.3057 | 825.5463 |  | 275.9257 | 908.2602 | 883.9362 | 831.7783 |  | 483.6435 | 743.1245 | 570.3801 | 776.0106 | 933.6879 | 1030.6734 | 1061.8449 | 62.5375 | 413.7319 | 103.4403 | 640.102 | 14.9429 | 49.9128 | 49.1243 | 52.6434 | 64.0827 |  |  | 1.1922 | -1.6926 | -0.70981 | -0.9469 | 8.0065 | 6.1659 | 10.3961 | -2.8908 | 21.1324 | 56.9614 | 41.2558 | -8.05e-05 | -2.793e-05 | -0.00072447 | 37.9045 | 17.0197 | 16.6736 | 17.0365 | 17.0606 | 16.0689 | 14.707 | 16.6857 | 17.0334 | 17.3886 | 17.468 | 17.2122 | 16.4068 | 14.7412 | 745.1929 | 519.8154 | 455.3384 | 313.8609 | 269.1658 | 756.5811 | 457.6337 | 33.1003 | 50.7649 | 56.1104 | 86.7755 | 88.8997 | 93.7265 |  |  |  | 645.3684 | 605.4049 | 608.8403 | 634.1884 | 91.521 | 30.9657 | 934.9686 |  |  | 844.8159 |  |  | 25.89 | 64.3264 | 637.1787 | 27.8706 | 67.0244 | 921.01 | 770.3014 | 672.3483 | 909.5264 | 916.0398 | 773.3973 |  | 848.3988 | 909.1017 | 1134.2413 | 643.8867 | 711.426 | 914.2926 |  | 417.5856 |  |  | 483.6656 | 707.3107 | 766.6173 | [6 empty] | 663.0595 |  |  | 485.2573 |  |  | 532.7071 | 702.3253 | 713.0423 | 1039.6608 | 1143.0531 | 1095.2863 | 568.0588 | 759.8492 | 877.3781 | 639.658 | 733.2203 | 1038.255 | 1145.1733 | 655.0506 | 871.0525 | 927.3 | 1097.0548 | 1120.3915 | 564.5439 | 673.8604 | 726.8708 | 620.4632 | 810.8716 | 934.9406 | 1028.6426 | 1137.4291 | 621.2198 | 717.2959 | 729.4379 | 933.9424 | 104.768 | -0.00046198 | 17.6916 | 4.7173 | -40.4917 | 3.1208 | 9437.86 | 0.39 | 2.3853 | -2.8904 | -1.8717 | -2.1618 | 7.1203 | 6.2485 | 8.1136 | 91.7964 | 228.7091 | 55.158 | 65.0151 | 16.4261 | 99.1053 | 40.669
42810.4545 | 1247 | 17.3851 | 17.8138 | 17.9716 | 18.0138 | 17.3779 | 16.0622 | 15.4288 | 16.4971 | 16.9114 | 17.0651 | 17.0938 | 16.6291 | 15.6737 | 14.4934 | 47.3798 | 63.4843 | 62.4065 | 89.692 | 83.8129 | 94.8186 |  |  |  | 58.6678 | 89.2302 | 588.8264 | 704.4981 | 723.424 | 711.2103 | 24.413 | 62.5429 | 909.2181 | 24.5031 | 61.1076 | 819.2961 | 876.3892 | 823.5758 |  | 272.3995 | 908.7847 | 883.7672 | 829.6091 |  | 483.1479 | 743.3622 | 568.7752 | 770.6085 | 932.5041 | 1030.7091 | 1059.8543 | 58.3253 | 413.7896 | 99.8933 | 640.6886 | 14.9863 | 49.9305 | 49.136 | 52.6891 | 64.2111 |  |  | 1.2034 | -1.5652 | -0.27874 | -0.40741 | 8.4973 | 6.9124 | 11.3299 | -3.2772 | 21.7958 | 58.1887 | 37.19 | -6.571e-05 | -6.407e-05 | -0.00075404 | 38.0099 | 17.0328 | 16.673 | 17.0462 | 17.0649 | 16.0815 | 14.7076 | 16.6842 | 17.0405 | 17.3891 | 17.4772 | 17.2166 | 16.4122 | 14.74 | 755.0976 | 521.8537 | 458.5408 | 310.4426 | 276.839 | 757.2579 | 457.4073 | 33.2168 | 50.8665 | 56.1973 | 86.8127 | 88.9343 | 93.7617 |  |  |  | 645.4111 | 605.5539 | 608.7945 | 632.2687 | 80.2513 | 36.1967 | 927.7751 |  |  | 837.4146 |  |  | 25.9426 | 64.3937 | 640.6002 | 27.9388 | 67.0836 | 919.6019 | 772.164 | 674.8282 | 907.9387 | 915.0738 | 776.648 |  | 850.1177 | 907.7004 | 1132.1659 | 646.8543 | 712.7732 | 932.9866 |  | 420.1634 |  |  | 485.9197 | 711.2441 | 769.7838 | [6 empty] | 665.6406 |  |  | 486.5019 |  |  | 533.1921 | 700.4244 | 712.3058 | 1030.0762 | 1142.6808 | 1096.251 | 568.1004 | 762.595 | 876.46 | 638.4165 | 731.0395 | 1031.5784 | 1148.0965 | 656.1654 | 871.8448 | 922.6261 | 1094.9748 | 1118.8201 | 563.784 | 672.7515 | 727.1822 | 622.6921 | 809.9851 | 933.8197 | 1027.2859 | 1137.0084 | 620.9331 | 715.6295 | 731.4497 | 928.5826 | 108.4546 | 0.0046101 | 17.6902 | 4.7306 | -40.3962 | 3.1209 | 9441.84 | 0.34 | 2.3986 | -2.7797 | -1.1731 | -1.4182 | 7.3354 | 6.616 | 8.4702 | 92.3052 | 227.381 | 55.4052 | 64.1575 | 16.0251 | 100.3093 | 40.731
42810.4545 | 1248 | 17.3721 | 17.8044 | 17.9638 | 18.0023 | 17.3744 | 16.0594 | 15.4274 | 16.4968 | 16.8998 | 17.0567 | 17.0772 | 16.6101 | 15.6576 | 14.494 | 47.5191 | 63.5829 | 62.5074 | 89.6746 | 83.8375 | 94.8208 |  |  |  | 58.8102 | 89.2398 | 589.6922 | 704.4075 | 723.0048 | 710.5911 | 24.9669 | 63.4213 | 911.7383 | 25.4076 | 62.204 | 824.1602 | 880.1075 | 827.0913 |  | 267.0978 | 912.3394 | 887.7101 | 721.8837 |  | 483.8223 | 741.9896 | 569.344 | 767.0829 | 929.8202 | 1031.1212 | 1061.3094 | 55.7624 | 413.7333 | 94.9737 | 640.8559 | 15.0089 | 49.9854 | 49.1318 | 52.6783 | 64.3912 |  |  | 1.0943 | -1.1229 | -0.19134 | -0.70771 | 8.2522 | 6.6062 | 10.2614 | -2.7936 | 21.6374 | 57.1368 | 34.7877 | -0.00011828 | -6.735e-05 | -0.00075568 | 38.1104 | 17.0377 | 16.6727 | 17.0436 | 17.0583 | 16.0779 | 14.7077 | 16.6864 | 17.0353 | 17.3846 | 17.4733 | 17.2182 | 16.4097 | 14.7373 | 736.9758 | 519.8576 | 457.9898 | 320.7869 | 269.0957 | 756.8963 | 457.2976 | 33.3426 | 50.9661 | 56.2872 | 86.8768 | 88.9574 | 93.8013 |  |  |  | 645.3695 | 604.969 | 607.8329 | 630.9248 | 86.3437 | 27.9033 | 926.0794 |  |  | 842.0977 |  |  | 25.9964 | 64.4664 | 641.4092 | 28.0025 | 67.1472 | 923.2348 | 771.5748 | 675.2074 | 912.8459 | 919.99 | 775.6362 |  | 851.2142 | 918.7554 | 1130.6117 | 647.1556 | 713.6901 | 946.908 |  | 421.1091 |  |  | 486.2909 | 707.1715 | 770.0582 | [6 empty] | 666.0228 |  |  | 485.9036 |  |  | 533.4825 | 698.0979 | 711.3217 | 1024.4637 | 1139.5857 | 1100.9018 | 568.4128 | 765.2545 | 875.3671 | 637.3028 | 729.9242 | 1035.3252 | 1156.4646 | 657.9602 | 871.8567 | 919.3917 | 1095.8624 | 1119.0968 | 564.1873 | 671.9529 | 726.8846 | 626.4492 | 809.3642 | 933.9268 | 1028.6642 | 1139.643 | 620.9977 | 713.813 | 735.633 | 926.2059 | 105.8129 | -0.0015494 | 17.69 | 4.7477 | -40.4127 | 3.1208 | 9494.46 | 0.31 | 2.2865 | -2.3529 | -0.97125 | -1.8679 | 7.23 | 6.4688 | 8.0622 | 92.7167 | 226.0541 | 55.6219 | 66.0412 | 16.0644 | 104.6921 | 40.7599
42810.4545 | 1249 | 17.3788 | 17.8107 | 17.9624 | 18.0092 | 17.3754 | 16.0562 | 15.4303 | 16.4943 | 16.9 | 17.0622 | 17.0847 | 16.6215 | 15.6663 | 14.4833 | 47.6674 | 63.701 | 62.6278 | 89.6335 | 83.96 | 94.831 |  |  |  | 58.9481 | 89.2589 | 589.8127 | 703.3517 | 721.6014 | 709.3192 | 64.0341 | 119.9901 | 972.9287 | 84.3165 | 133.4957 | 921.8156 | 901.1188 | 876.096 |  | 250.6521 | 976.5375 | 949.5503 | 592.2213 |  | 485.887 | 743.0491 | 569.0666 | 767.0417 | 933.8421 | 1032.4373 | 1064.8769 | 52.833 | 414.032 | 88.4994 | 640.5933 | 15.0348 | 50.0437 | 49.1161 | 52.6309 | 64.5924 |  |  | 1.2586 | -2.2992 | -0.52844 | -0.53226 | 8.2286 | 6.4872 | 10.176 | -1.938 | 20.1285 | 54.1479 | 35.3959 | -7.228e-05 | -0.00010185 | -0.00078689 | 38.2195 | 17.0511 | 16.669 | 17.0488 | 17.0615 | 16.0758 | 14.7047 | 16.6906 | 17.0418 | 17.3867 | 17.4735 | 17.2226 | 16.4082 | 14.7427 | 726.7216 | 516.2528 | 451.5696 | 310.2219 | 250.7413 | 757.1631 | 457.1364 | 33.4681 | 51.0756 | 56.3799 | 86.9343 | 88.9811 | 93.8527 |  |  |  | 645.237 | 604.2623 | 606.7916 | 628.8572 | 86.6581 | 33.7518 | 929.3298 |  |  | 851.7739 |  |  | 26.0471 | 64.5379 | 641.123 | 28.0709 | 67.2059 | 926.9782 | 769.8371 | 674.1828 | 916.4271 | 924.2413 | 772.5948 |  | 852.2534 | 926.1886 | 1129.0546 | 646.2072 | 714.4515 | 959.9174 |  | 422.9418 |  |  | 486.7924 | 700.0893 | 768.7904 | [6 empty] | 664.9682 |  |  | 484.3906 |  |  | 533.68 | 696.4498 | 710.7589 | 1030.392 | 1139.5145 | 1101.6811 | 569.2114 | 767.6333 | 875.6679 | 637.1695 | 729.6428 | 1033.9018 | 1156.3687 | 659.9421 | 874.0644 | 921.1442 | 1099.9438 | 1120.7662 | 565.1268 | 671.3145 | 726.0596 | 630.4418 | 810.2417 | 935.7514 | 1032.783 | 1142.8903 | 621.2429 | 713.0377 | 739.1345 | 926.7426 | 101.4906 | -0.00056021 | 17.6918 | 4.7724 | -40.3212 | 3.1208 | 9519.64 | 0.31 | 2.4506 | -3.3685 | -1.6149 | -1.6208 | 7.2232 | 6.4136 | 8.0326 | 93.1655 | 224.8291 | 55.8356 | 67.2764 | 16.7456 | 116.389 | 40.7903
42810.4545 | 1250 | 17.3807 | 17.8097 | 17.9585 | 18.0013 | 17.3666 | 16.0508 | 15.4358 | 16.4962 | 16.9032 | 17.0622 | 17.0799 | 16.6163 | 15.6591 | 14.4871 | 47.7999 | 63.8018 | 62.7368 | 89.6002 | 83.9455 | 94.835 |  |  |  | 59.0679 | 89.2538 | 589.2317 | 702.235 | 720.0689 | 708.1068 | 102.154 | 134.2706 | 998.4699 | 104.2817 | 141.0676 | 917.5256 | 874.3312 | 925.0348 |  | 231.0476 | 999.2329 | 964.0562 | 604.1273 |  | 486.9671 | 742.324 | 569.051 | 771.2538 | 938.0327 | 1034.0769 | 1065.1201 | 50.3127 | 414.3081 | 83.26 | 639.7951 | 15.0624 | 50.0993 | 49.097 | 52.5638 | 64.838 |  |  | 1.3118 | -0.95865 | 0.11422 | -0.34301 | 7.8875 | 6.6022 | 11.3549 | -2.463 | 19.6258 | 56.1983 | 37.6756 | -0.00010678 | -8.707e-05 | -0.00074418 | 38.3206 | 17.0556 | 16.6714 | 17.0439 | 17.065 | 16.0781 | 14.7141 | 16.6916 | 17.0432 | 17.3888 | 17.4719 | 17.2237 | 16.4165 | 14.7458 | 738.124 | 516.7873 | 445.7069 | 296.1743 | 233.9095 | 757.2833 | 457.1065 | 33.5897 | 51.1751 | 56.4746 | 86.9621 | 89.012 | 93.8876 |  |  |  | 644.8593 | 602.8042 | 606.2057 | 625.553 | 74.9793 | 28.5172 | 933.0747 |  |  | 860.5654 |  |  | 26.1046 | 64.6093 | 640.0809 | 28.1448 | 67.261 | 927.0782 | 767.1095 | 673.6717 | 918.9195 | 927.6176 | 768.1828 |  | 853.0237 | 927.2974 | 1127.4198 | 644.991 | 715.5594 | 956.4 |  | 424.2535 |  |  | 487.3798 | 693.5665 | 766.3961 | [6 empty] | 663.972 |  |  | 482.6019 |  |  | 534.1503 | 698.1018 | 710.5631 | 1036.0679 | 1132.719 | 1098.0207 | 569.7507 | 769.248 | 876.8868 | 638.5415 | 730.3051 | 1033.2963 | 1154.7454 | 661.0137 | 875.8232 | 921.7154 | 1102.8358 | 1123.1717 | 566.0973 | 671.3623 | 725.8889 | 632.3526 | 810.0729 | 935.7588 | 1033.5295 | 1142.9026 | 621.5949 | 713.6167 | 740.2543 | 924.6692 | 95.7043 | -1.3012e-05 | 17.6936 | 4.7935 | -40.3095 | 3.1209 | 9534.27 | 0.31 | 2.5003 | -2.1744 | 0.75052 | -1.3006 | 7.0764 | 6.4742 | 8.4905 | 93.5587 | 223.7325 | 56.1426 | 66.0526 | 17.3911 | 105.8083 | 40.8053
42810.4545 | 1251 | 17.3914 | 17.8072 | 17.9667 | 18.0081 | 17.3793 | 16.0561 | 15.4485 | 16.5024 | 16.908 | 17.0699 | 17.0861 | 16.6237 | 15.6625 | 14.4951 | 47.9373 | 63.9163 | 62.8619 | 89.5742 | 84.0387 | 94.8839 |  |  |  | 59.2077 | 89.2728 | 589.345 | 701.7888 | 719.2849 | 707.8576 | 87.8871 | 131.6214 | 989.2394 | 99.4828 | 135.4055 | 911.218 | 927.2881 | 914.4916 |  | 237.6529 | 1008.9648 | 987.9029 | 571.0745 |  | 486.6537 | 740.1997 | 570.2072 | 768.3457 | 933.5775 | 1032.8054 | 1062.9676 | 49.9203 | 414.4097 | 79.3583 | 639.2061 | 15.093 | 50.1428 | 49.0768 | 52.5104 | 65.0793 |  |  | 1.1239 | -1.0592 | -0.33722 | -0.82008 | 8.8785 | 6.9203 | 10.0367 | -2.3185 | 20.9625 | 55.1653 | 39.5867 | -9.692e-05 | -4.271e-05 | -0.00076718 | 38.4264 | 17.0648 | 16.6666 | 17.0422 | 17.0587 | 16.074 | 14.7144 | 16.6928 | 17.0362 | 17.3901 | 17.4702 | 17.2194 | 16.4204 | 14.7464 | 726.6047 | 514.2211 | 449.2645 | 310.921 | 249.8201 | 756.9351 | 457.0069 | 33.7102 | 51.2788 | 56.563 | 86.9977 | 89.0337 | 93.9258 |  |  |  | 644.6095 | 602.5363 | 605.9509 | 625.4883 | 96.9052 | 38.1525 | 935.8631 |  |  | 864.481 |  |  | 26.1598 | 64.6733 | 639.3184 | 28.2112 | 67.3207 | 925.1472 | 763.8941 | 675.4757 | 918.4105 | 928.2007 | 764.6359 |  | 853.0489 | 922.2854 | 1128.1469 | 646.6804 | 717.0434 | 968.788 |  | 425.7556 |  |  | 485.8748 | 688.2757 | 763.3413 | [6 empty] | 665.5795 |  |  | 481.9207 |  |  | 534.5077 | 700.0717 | 710.9441 | 1037.6537 | 1126.1395 | 1093.9413 | 570.3009 | 769.9705 | 876.9933 | 639.0586 | 731.6215 | 1030.1699 | 1159.7742 | 661.8276 | 876.081 | 924.0815 | 1101.3132 | 1120.4067 | 566.5589 | 672.135 | 726.1629 | 634.7235 | 810.8988 | 935.0488 | 1032.3993 | 1143.7261 | 621.7479 | 715.1996 | 742.4088 | 925.9037 | 110.5156 | -0.00020942 | 17.6948 | 4.8087 | -40.4361 | 3.1209 | 9571.68 | 0.32 | 2.314 | -2.2831 | -1.2883 | -2.009 | 7.5041 | 6.6251 | 7.9786 | 93.6661 | 224.3453 | 56.4629 | 67.2075 | 16.9759 | 127.6397 | 40.7564
42810.4545 | 1252 | 17.39 | 17.8128 | 17.9723 | 18.0102 | 17.3811 | 16.0644 | 15.4584 | 16.5069 | 16.9067 | 17.0686 | 17.0892 | 16.6285 | 15.6615 | 14.5022 | 48.0765 | 64.0119 | 62.9581 | 89.5139 | 84.1289 | 94.8846 |  |  |  | 59.335 | 89.2712 | 589.6392 | 701.1686 | 718.5764 | 707.3783 | 91.5607 | 128.0385 | 988.2998 | 94 | 127.1814 | 907.9248 | 935.9502 | 903.5054 |  | 246.5249 | 992.3064 | 971.1549 | 553.5015 |  | 486.8033 | 739.1509 | 570.1856 | 763.9376 | 931.8532 | 1033.0593 | 1061.2437 | 49.1677 | 414.5369 | 75.6457 | 639.1459 | 15.1127 | 50.1658 | 49.0622 | 52.4447 | 65.3195 |  |  | 1.2139 | -1.3036 | 0.032736 | -0.92916 | 8.2825 | 6.3578 | 10.6458 | -2.9966 | 20.9355 | 56.5791 | 42.6743 | -9.528e-05 | -0.00010514 | -0.00074747 | 38.5227 | 17.0669 | 16.665 | 17.0342 | 17.0592 | 16.0727 | 14.7102 | 16.6929 | 17.0481 | 17.3851 | 17.4747 | 17.2175 | 16.4108 | 14.7389 | 748.798 | 526.783 | 467.4958 | 302.5729 | 255.4554 | 757.8285 | 457.6919 | 33.8306 | 51.3768 | 56.6439 | 87.0207 | 89.0496 | 93.9633 |  |  |  | 644.4398 | 601.7597 | 605.346 | 626.298 | 99.61 | 36.4075 | 935.9838 |  |  | 866.0184 |  |  | 26.2047 | 64.7448 | 639.5775 | 28.273 | 67.3788 | 921.9785 | 761.8356 | 678.6258 | 919.8385 | 931.7865 | 763.1248 |  | 853.0706 | 919.7361 | 1129.2046 | 649.9715 | 718.5164 | 965.9649 |  | 427.3255 |  |  | 484.6285 | 687.3164 | 760.5331 | [6 empty] | 668.9544 |  |  | 483.5158 |  |  | 534.315 | 699.8984 | 711.5739 | 1031.8652 | 1124.3315 | 1092.7863 | 570.6737 | 770.012 | 877.2913 | 638.1306 | 732.3146 | 1031.0355 | 1161.0962 | 662.3895 | 878.9136 | 928.0932 | 1099.3694 | 1121.0759 | 567.1572 | 673.4415 | 726.7739 | 635.8487 | 813.8682 | 937.4855 | 1026.7047 | 1142.6598 | 622.5648 | 716.6606 | 744.376 | 927.3992 | 100.1071 | -0.0021667 | 17.6973 | 4.8184 | -40.3273 | 3.1208 | 9614.65 | 0.35 | 2.4043 | -2.5316 | 0.40118 | -2.1373 | 7.2486 | 6.3508 | 8.2179 | 93.7157 | 225.1063 | 56.7375 | 65.0626 | 15.0869 | 131.8039 | 40.6994
42810.4545 | 1253 | 17.3903 | 17.8097 | 17.9662 | 18.0078 | 17.3796 | 16.0655 | 15.4564 | 16.5072 | 16.9043 | 17.0683 | 17.0852 | 16.6264 | 15.6673 | 14.5028 | 48.2195 | 64.1282 | 63.0736 | 89.4523 | 84.1465 | 94.9112 |  |  |  | 59.4781 | 89.2726 | 593.039 | 703.0598 | 720.3711 | 709.1944 | 121.3388 | 131.9803 | 965.4054 | 96.8697 | 142.8037 | 901.8929 | 962.0682 | 896.7822 |  | 245.833 | 989.9068 | 966.1769 | 571.844 |  | 488.5753 | 738.6459 | 569.0649 | 760.8461 | 929.7021 | 1031.9167 | 1060.4264 | 48.2715 | 414.6813 | 77.3485 | 639.2011 | 15.1419 | 50.1814 | 49.0572 | 52.3869 | 65.5676 |  |  | 1.1094 | -1.0934 | -0.41739 | -1.4292 | 8.2121 | 7.4052 | 11.2386 | -2.7594 | 20.9983 | 56.3504 | 41.3345 | -5.257e-05 | -8.05e-05 | -0.00073433 | 38.6375 | 17.0753 | 16.6686 | 17.0389 | 17.0575 | 16.074 | 14.7107 | 16.6967 | 17.0399 | 17.3953 | 17.4732 | 17.2209 | 16.4054 | 14.7479 | 772.6416 | 545.6458 | 484.3205 | 303.8053 | 245.0099 | 759.5575 | 458.3021 | 33.9504 | 51.4722 | 56.7239 | 87.0526 | 89.0834 | 94.0043 |  |  |  | 644.4726 | 601.772 | 604.9981 | 629.0872 | 78.7006 | 32.6996 | 937.9919 |  |  | 874.3882 |  |  | 26.2551 | 64.8193 | 641.3014 | 28.3287 | 67.4328 | 921.2087 | 759.5863 | 681.2856 | 928.022 | 940.1358 | 762.4427 |  | 853.4974 | 928.2573 | 1130.5688 | 652.9432 | 720.0477 | 953.9644 |  | 429.0077 |  |  | 483.745 | 684.6862 | 759.9314 | [6 empty] | 672.1148 |  |  | 484.9894 |  |  | 533.9228 | 700.5862 | 712.0145 | 1017.6364 | 1124.3292 | 1093.9807 | 571.0483 | 769.8021 | 880.2931 | 638.1216 | 732.645 | 1022.3577 | 1159.0603 | 662.0027 | 882.8434 | 926.7264 | 1093.2471 | 1119.1641 | 567.881 | 674.4999 | 728.6222 | 635.1776 | 814.8357 | 937.5013 | 1022.3154 | 1138.8402 | 622.7472 | 718.3119 | 743.1321 | 925.7627 | 97.9914 | 5.0162e-05 | 17.6993 | 4.8314 | -40.3013 | 3.1208 | 9621.01 | 0.21 | 2.3006 | -2.3179 | -1.4321 | -2.6501 | 7.2146 | 6.851 | 8.4399 | 93.8849 | 225.7621 | 57.0369 | 63.0362 | 13.3394 | 142.8346 | 40.6286
42810.4545 | 1254 | 17.3882 | 17.8011 | 17.9614 | 18.0086 | 17.375 | 16.0648 | 15.458 | 16.4992 | 16.8999 | 17.0633 | 17.0814 | 16.6231 | 15.6681 | 14.4908 | 48.3603 | 64.2447 | 63.1827 | 89.3885 | 84.0592 | 94.9358 |  |  |  | 59.6112 | 89.2961 | 594.9423 | 704.2649 | 721.7928 | 710.4564 | 111.4866 | 150.6142 | 992.1163 | 90.5289 | 125.5936 | 873.8938 | 973.3239 | 881.2955 |  | 246.004 | 977.7383 | 957.6506 | 562.6537 |  | 487.1852 | 738.9943 | 567.2238 | 762.1298 | 928.9682 | 1031.4934 | 1059.2699 | 47.743 | 414.7989 | 77.9628 | 639.0233 | 15.1294 | 50.1929 | 49.0502 | 52.3351 | 65.7722 |  |  | 1.2514 | -0.90016 | -0.13614 | -1.2275 | 7.9408 | 6.7231 | 10.9126 | -2.6227 | 20.1254 | 55.0478 | 43.552 | -0.00010678 | -0.00012321 | -0.00072118 | 38.7395 | 17.0779 | 16.6625 | 17.0339 | 17.0575 | 16.075 | 14.7059 | 16.6931 | 17.04 | 17.3808 | 17.4709 | 17.2183 | 16.4106 | 14.7466 | 755.2692 | 528.7405 | 461.0002 | 300.7155 | 239.636 | 759.22 | 458.4052 | 34.0857 | 51.578 | 56.8239 | 87.0791 | 89.113 | 94.0382 |  |  |  | 644.6453 | 602.3882 | 604.6158 | 631.0067 | 73.3311 | 26.0753 | 944.6772 |  |  | 888.0794 |  |  | 26.3068 | 64.8856 | 643.6076 | 28.3858 | 67.4848 | 922.6007 | 755.678 | 683.056 | 933.4796 | 942.6648 | 756.8591 |  | 853.143 | 933.064 | 1132.7605 | 655.3675 | 721.6438 | 952.6661 |  | 430.7916 |  |  | 483.6207 | 678.8649 | 755.909 | [6 empty] | 673.8066 |  |  | 485.8435 |  |  | 533.5362 | 702.7114 | 712.7049 | 1020.0683 | 1127.3185 | 1100.5835 | 571.1714 | 773.4247 | 882.4459 | 639.0328 | 733.9574 | 1026.6912 | 1161.0541 | 662.1875 | 883.8945 | 925.5763 | 1090.2384 | 1117.4302 | 568.3201 | 674.3854 | 729.1607 | 633.413 | 814.3058 | 940.9103 | 1023.4694 | 1136.739 | 622.4386 | 718.5247 | 741.1627 | 927.7828 | 101.8082 | 5.0162e-05 | 17.7017 | 4.8394 | -40.3119 | 3.1208 | 9597.24 | 0.27 | 2.445 | -2.1035 | -0.81806 | -2.4564 | 7.0932 | 6.5268 | 8.3153 | 93.9153 | 227.0675 | 57.3694 | 64.8447 | 15.9511 | 148.2799 | 40.6104
42810.4546 | 1255 | 17.3888 | 17.8113 | 17.9683 | 18.0176 | 17.3747 | 16.0615 | 15.4665 | 16.5077 | 16.9075 | 17.0601 | 17.0843 | 16.6315 | 15.6658 | 14.5012 | 48.4895 | 64.3467 | 63.2948 | 89.3431 | 84.0305 | 94.9798 |  |  |  | 59.7373 | 89.2906 | 598.2559 | 706.3964 | 724.2251 | 712.988 | 105.6455 | 151.3843 | 1014.4931 | 116.9192 | 151.6523 | 863.2798 | 957.1521 | 868.0318 |  | 243.4676 | 982.6075 | 953.3435 | 576.604 |  | 485.4472 | 736.678 | 566.2413 | 759.2554 | 925.4726 | 1031.8092 | 1058.8619 | 47.2316 | 414.8964 | 77.642 | 638.6549 | 15.1384 | 50.1875 | 49.06 | 52.3069 | 65.8247 |  |  | 1.2113 | -1.1551 | 0.89947 | -0.51583 | 8.0656 | 6.3992 | 10.9442 | -2.3894 | 21.6002 | 54.3408 | 41.0215 | -0.00011007 | -7.557e-05 | -0.00072775 | 38.8401 | 17.0866 | 16.6633 | 17.0368 | 17.0548 | 16.0746 | 14.7068 | 16.6911 | 17.0378 | 17.3729 | 17.4676 | 17.2148 | 16.413 | 14.743 | 740.7577 | 506.614 | 425.3569 | 290.8899 | 246.1001 | 758.4723 | 457.8378 | 34.201 | 51.6815 | 56.9109 | 87.1035 | 89.1433 | 94.074 |  |  |  | 644.4808 | 601.3894 | 603.6314 | 628.6498 | 90.0017 | 33.8294 | 948.3472 |  |  | 886.7672 |  |  | 26.3612 | 64.9536 | 646.4092 | 28.4588 | 67.5334 | 920.2099 | 753.1608 | 684.5571 | 931.638 | 939.43 | 752.9192 |  | 852.9624 | 932.738 | 1134.3167 | 657.2957 | 723.0209 | 966.9373 |  | 432.3094 |  |  | 483.9778 | 675.7089 | 752.3583 | [6 empty] | 675.3069 |  |  | 487.3395 |  |  | 533.4726 | 705.0842 | 713.3001 | 1018.9449 | 1126.468 | 1103.9123 | 570.2507 | 775.1612 | 887.3675 | 640.3649 | 735.5099 | 1021.303 | 1164.3278 | 661.8159 | 885.4506 | 924.4686 | 1089.4488 | 1118.9317 | 568.9115 | 673.8715 | 729.8048 | 632.2138 | 812.7416 | 943.1987 | 1022.925 | 1135.0897 | 622.0397 | 719.1043 | 738.1281 | 928.5327 | 95.4882 | 0.00028166 | 17.7045 | 4.844 | -40.3665 | 3.1208 | 9549.67 | 0.29 | 2.4086 | -2.3802 | 2.1003 | -1.5905 | 7.1496 | 6.3684 | 8.3283 | 93.9612 | 228.1022 | 57.6622 | 66.1877 | 19.7981 | 140.477 | 40.6424
42810.4546 | 1256 | 17.3906 | 17.8014 | 17.9652 | 18.0136 | 17.3749 | 16.0626 | 15.4647 | 16.5084 | 16.9063 | 17.0728 | 17.0877 | 16.6366 | 15.668 | 14.5049 | 48.6197 | 64.4482 | 63.4042 | 89.3092 | 83.9664 | 94.9853 |  |  |  | 59.8685 | 89.3043 | 600.8343 | 707.8601 | 725.2637 | 714.6619 | 96.9508 | 141.2415 | 988.8044 | 116.4124 | 159.2512 | 866.625 | 940.3994 | 860.472 |  | 249.5454 | 984.2324 | 960.5014 | 560.9325 |  | 484.3218 | 735.2501 | 567.8673 | 758.6583 | 925.9183 | 1030.093 | 1056.0393 | 47.5566 | 414.9007 | 77.2354 | 638.1234 | 15.1199 | 50.1864 | 49.0527 | 52.2753 | 65.6461 |  |  | 1.553 | -0.30284 | -0.80772 | -1.1486 | 8.2877 | 6.9032 | 11.2688 | -2.3421 | 21.0534 | 56.085 | 43.4772 | -4.435e-05 | -0.00012321 | -0.00069983 | 38.9426 | 17.096 | 16.662 | 17.0387 | 17.0583 | 16.0673 | 14.7101 | 16.6947 | 17.0375 | 17.382 | 17.4628 | 17.2177 | 16.4131 | 14.748 | 761.333 | 524.7486 | 456.2051 | 296.3251 | 252.1692 | 759.3456 | 457.9815 | 34.322 | 51.7785 | 56.9949 | 87.1372 | 89.169 | 94.1096 |  |  |  | 644.3579 | 600.7313 | 603.0369 | 628.5176 | 101.4123 | 40.1651 | 946.2937 |  |  | 877.0175 |  |  | 26.4204 | 65.0277 | 648.6976 | 28.5322 | 67.5885 | 916.542 | 751.8845 | 686.0233 | 926.4324 | 935.4881 | 750.3467 |  | 853.0656 | 930.459 | 1134.8128 | 659.3928 | 724.4763 | 970.4023 |  | 433.679 |  |  | 484.3032 | 672.5306 | 750.7569 | [6 empty] | 676.7676 |  |  | 489.0131 |  |  | 533.4223 | 706.7518 | 713.7798 | 1014.9897 | 1123.1162 | 1103.9487 | 569.2031 | 774.828 | 890.2215 | 641.3128 | 736.6852 | 1017.2722 | 1160.4703 | 661.5768 | 883.1063 | 924.2939 | 1086.2738 | 1117.571 | 569.7322 | 673.5452 | 729.8232 | 631.242 | 808.809 | 941.8393 | 1021.7268 | 1131.7114 | 622.5367 | 718.4121 | 734.6491 | 923.856 | 105.5359 | -0.00026554 | 17.7073 | 4.8502 | -40.3203 | 3.1208 | 9475.52 | 0.28 | 2.7295 | -1.2178 | -1.9889 | -2.3718 | 7.2426 | 6.6101 | 8.4454 | 94.0689 | 228.4932 | 57.9714 | 64.2163 | 16.3993 | 133.5146 | 40.6211
42810.4546 | 1257 | 17.3903 | 17.8112 | 17.9633 | 18.0181 | 17.3829 | 16.0629 | 15.4693 | 16.5131 | 16.9123 | 17.071 | 17.0988 | 16.6305 | 15.6724 | 14.5034 | 48.7544 | 64.5545 | 63.5092 | 89.2831 | 83.9614 | 95.0186 |  |  |  | 60.0017 | 89.3098 | 599.736 | 706.3243 | 722.7365 | 713.0276 | 108.3376 | 160.7301 | 999.4351 | 119.9754 | 156.13 | 867.7509 | 933.5662 | 856.0952 |  | 231.9326 | 989.3846 | 963.3941 | 550.3684 |  | 482.9394 | 733.8964 | 567.3603 | 756.3833 | 927.1285 | 1029.8943 | 1054.0533 | 48.3619 | 414.9079 | 76.4928 | 637.4281 | 15.1121 | 50.2305 | 49.0531 | 52.2664 | 65.3131 |  |  | 1.5096 | -0.78648 | 0.33632 | -0.76357 | 8.724 | 7.0708 | 11.1058 | -3.2562 | 21.4348 | 56.2571 | 44.3158 | -9.199e-05 | -9.692e-05 | -0.00074747 | 39.0493 | 17.1044 | 16.6689 | 17.037 | 17.057 | 16.0704 | 14.707 | 16.6997 | 17.0428 | 17.3883 | 17.4745 | 17.223 | 16.4115 | 14.7505 | 782.4211 | 543.6463 | 476.2266 | 294.2353 | 252.2287 | 761.3909 | 458.7369 | 34.4422 | 51.8764 | 57.0795 | 87.1735 | 89.1879 | 94.1486 |  |  |  | 644.1864 | 599.6978 | 602.9872 | 627.0745 | 94.1963 | 41.264 | 942.938 |  |  | 874.2725 |  |  | 26.4773 | 65.0979 | 647.7456 | 28.609 | 67.648 | 912.4956 | 752.3859 | 686.9401 | 924.7224 | 934.5963 | 748.8956 |  | 853.3481 | 937.3516 | 1134.998 | 660.6578 | 725.9311 | 965.2006 |  | 435.264 |  |  | 484.4663 | 669.5714 | 749.7665 | [6 empty] | 677.3995 |  |  | 489.7547 |  |  | 533.3908 | 707.8487 | 714.4736 | 1004.2362 | 1123.6208 | 1101.2248 | 569.0146 | 773.93 | 889.2291 | 642.1795 | 737.3539 | 1022.9178 | 1155.3742 | 661.9867 | 882.124 | 922.4199 | 1082.9131 | 1115.4426 | 570.1103 | 673.7503 | 730.1081 | 632.1902 | 806.0162 | 940.694 | 1018.9318 | 1130.3872 | 623.0943 | 718.8456 | 734.4144 | 920.459 | 115.8516 | -0.0014932 | 17.7103 | 4.8539 | -40.3233 | 3.1207 | 9410.12 | 0.27 | 2.6889 | -1.9613 | 1.2825 | -1.9325 | 7.4303 | 6.6893 | 8.3834 | 94.2086 | 228.4242 | 58.305 | 62.6125 | 14.3256 | 130.8718 | 40.6265
42810.4546 | 1258 | 17.3787 | 17.8014 | 17.9548 | 18.0028 | 17.3716 | 16.0642 | 15.4647 | 16.5113 | 16.9031 | 17.0592 | 17.0873 | 16.6241 | 15.6608 | 14.5002 | 48.8885 | 64.6634 | 63.6105 | 89.2635 | 83.9486 | 95.0772 |  |  |  | 60.1221 | 89.313 | 598.7836 | 704.7518 | 720.8303 | 711.1616 | 117.2865 | 150.3836 | 992.0774 | 117.5725 | 156.1588 | 896.3762 | 906.2197 | 889.8769 |  | 227.667 | 1001.9706 | 978.7593 | 525.2498 |  | 484.1664 | 734.0292 | 565.7793 | 753.4325 | 932.093 | 1033.6072 | 1057.4704 | 48.1232 | 414.982 | 77.2385 | 637.0976 | 15.0996 | 50.249 | 49.0559 | 52.258 | 64.9578 |  |  | 1.4754 | -1.0717 | -0.025092 | -0.28322 | 8.4474 | 6.7337 | 10.9041 | -2.9835 | 21.2643 | 56.4969 | 54.3745 | -9.199e-05 | -7.721e-05 | -0.0007294 | 39.1594 | 17.1176 | 16.6758 | 17.0385 | 17.0607 | 16.08 | 14.7199 | 16.6982 | 17.04 | 17.3939 | 17.4774 | 17.2196 | 16.4186 | 14.7565 | 777.4913 | 549.8082 | 477.2048 | 296.3647 | 262.8087 | 762.7309 | 459.6586 | 34.5499 | 51.9694 | 57.171 | 87.1959 | 89.2029 | 94.1796 |  |  |  | 644.1433 | 599.2718 | 603.0007 | 629.1397 | 89.2433 | 33.407 | 943.3297 |  |  | 887.0684 |  |  | 26.522 | 65.1554 | 645.3893 | 28.6785 | 67.707 | 909.7701 | 755.7301 | 687.0482 | 934.103 | 941.2534 | 753.7734 |  | 854.4681 | 944.5023 | 1133.7551 | 660.7907 | 726.938 | 955.0565 |  | 436.4681 |  |  | 485.4113 | 671.7131 | 752.2192 | [6 empty] | 677.382 |  |  | 489.5797 |  |  | 533.2698 | 708.6065 | 714.4163 | 999.1492 | 1129.5394 | 1100.0283 | 568.9469 | 775.1543 | 889.3376 | 642.5191 | 737.7335 | 1021.1079 | 1157.7227 | 663.0216 | 884.5371 | 918.5006 | 1080.7062 | 1113.9448 | 570.6582 | 674.1432 | 730.6442 | 634.3166 | 806.7558 | 943.7663 | 1016.3368 | 1129.8924 | 623.5113 | 718.8844 | 737.391 | 921.7564 | 112.6067 | -0.00010418 | 17.712 | 4.8564 | -40.3756 | 3.1207 | 9353.57 | 0.28 | 2.6558 | -2.2896 | -0.35034 | -1.177 | 7.3219 | 6.5372 | 8.3188 | 94.4679 | 227.4049 | 58.5574 | 63.6463 | 14.4015 | 120.2765 | 40.5603
42810.4546 | 1259 | 17.3805 | 17.8069 | 17.9549 | 18.0033 | 17.374 | 16.0625 | 15.4644 | 16.5132 | 16.9073 | 17.0624 | 17.088 | 16.6253 | 15.6606 | 14.503 | 49.0256 | 64.7671 | 63.7237 | 89.2681 | 83.9365 | 95.1132 |  |  |  | 60.2384 | 89.3193 | 601.0419 | 705.7478 | 722.3172 | 712.063 | 107.4402 | 141.3362 | 977.4909 | 102.6278 | 150.0638 | 874.1549 | 973.3486 | 855.6071 |  | 235.9383 | 988.7939 | 968.2971 | 531.2279 |  | 485.6763 | 734.8078 | 566.3363 | 750.502 | 932.0054 | 1033.8903 | 1056.4513 | 47.8941 | 414.9518 | 77.0602 | 636.7275 | 15.1237 | 50.2431 | 49.0618 | 52.2473 | 64.6533 |  |  | 1.2395 | -0.92973 | 0.61362 | -0.3601 | 8.1188 | 5.198 | 10.7503 | -2.8803 | 21.0106 | 55.1319 | 49.1096 | -5.75e-05 | -8.542e-05 | -0.0007639 | 39.2734 | 17.1262 | 16.6777 | 17.0478 | 17.0615 | 16.0779 | 14.7252 | 16.7062 | 17.0435 | 17.3881 | 17.4747 | 17.2294 | 16.4247 | 14.7467 | 749.3923 | 538.7082 | 476.674 | 291.7412 | 256.2341 | 762.7671 | 460.1495 | 34.6897 | 52.0804 | 57.2663 | 87.23 | 89.224 | 94.2166 |  |  |  | 644.4262 | 600.0709 | 602.754 | 632.543 | 73.1249 | 29.4814 | 948.8442 |  |  | 897.0928 |  |  | 26.5732 | 65.2248 | 647.001 | 28.7471 | 67.7686 | 910.7838 | 758.3233 | 687.3587 | 942.1117 | 948.2164 | 760.1883 |  | 855.6706 | 954.9451 | 1132.7433 | 661.0985 | 727.8209 | 953.1276 |  | 437.5524 |  |  | 486.1578 | 674.4679 | 756.2041 | [6 empty] | 677.7183 |  |  | 489.5742 |  |  | 533.3081 | 709.2072 | 714.708 | 1001.3921 | 1134.6572 | 1100.947 | 568.4761 | 778.5155 | 890.2949 | 642.6739 | 739.022 | 1019.7123 | 1161.1457 | 664.5888 | 889.5566 | 920.6936 | 1081.0502 | 1113.3415 | 570.0726 | 674.3875 | 730.987 | 635.5726 | 807.1505 | 949.2782 | 1018.5589 | 1130.4185 | 623.3779 | 718.6293 | 738.887 | 924.3416 | 112.482 | -9.7173e-05 | 17.7144 | 4.8565 | -40.3566 | 3.1207 | 9295.89 | 0.34 | 2.4354 | -2.1334 | 1.7332 | -1.3277 | 7.1789 | 5.7442 | 8.2608 | 94.7148 | 226.4484 | 58.7739 | 66.7815 | 14.5588 | 149.1644 | 40.5232
42810.4546 | 1260 | 17.3836 | 17.8028 | 17.9605 | 18.0115 | 17.3717 | 16.0627 | 15.4784 | 16.5103 | 16.9055 | 17.0616 | 17.0845 | 16.6224 | 15.6601 | 14.4977 | 49.1624 | 64.8693 | 63.8247 | 89.2772 | 83.9537 | 95.1369 |  |  |  | 60.37 | 89.3269 | 604.0541 | 707.6142 | 724.2294 | 713.8151 | 115.6404 | 136.7687 | 963.0281 | 98.0102 | 138.9168 | 860.8104 | 976.3914 | 843.5947 |  | 238.6924 | 981.8207 | 956.9335 | 557.652 |  | 487.0768 | 736.0921 | 566.2518 | 749.2695 | 928.3777 | 1031.8573 | 1055.4591 | 48.0231 | 415.0187 | 76.4695 | 636.1555 | 15.1433 | 50.2577 | 49.0723 | 52.242 | 64.4643 |  |  | 1.4104 | -0.30087 | -0.80772 | -0.56775 | 8.3843 | 6.1258 | 11.278 | -2.81 | 21.1797 | 55.8314 | 49.0389 | -8.05e-05 | -9.035e-05 | -0.00071625 | 39.3755 | 17.127 | 16.6599 | 17.0387 | 17.0564 | 16.0754 | 14.7202 | 16.6868 | 17.0422 | 17.3882 | 17.4628 | 17.2132 | 16.4094 | 14.7464 | 730.1539 | 522.8279 | 459.8036 | 292.4656 | 261.0835 | 761.9764 | 460.2322 | 34.8164 | 52.1818 | 57.3642 | 87.2643 | 89.271 | 94.2599 |  |  |  | 644.6412 | 600.4391 | 602.9231 | 632.868 | 79.7533 | 32.8639 | 954.4461 |  |  | 901.7435 |  |  | 26.6289 | 65.2973 | 650.0512 | 28.8195 | 67.8239 | 910.1587 | 759.2509 | 688.8254 | 944.1964 | 948.0015 | 763.0526 |  | 856.6642 | 961.0807 | 1132.214 | 663.1783 | 729.0575 | 944.8177 |  | 438.6444 |  |  | 486.8415 | 675.1391 | 757.5128 | [6 empty] | 679.638 |  |  | 491.2162 |  |  | 533.4263 | 710.8003 | 715.565 | 993.3335 | 1137.4085 | 1101.0332 | 568.1676 | 781.4065 | 892.6666 | 643.1022 | 741.5364 | 1022.1933 | 1158.1679 | 665.7538 | 893.1948 | 923.8908 | 1080.8266 | 1110.8358 | 569.9505 | 674.6306 | 731.594 | 634.778 | 804.9744 | 951.3587 | 1019.75 | 1128.8396 | 623.7777 | 718.6315 | 737.6512 | 922.992 | 125.2857 | 0.00042194 | 17.7152 | 4.8557 | -40.4566 | 3.1207 | 9293.36 | 0.27 | 2.6001 | -1.2144 | -1.9897 | -1.6682 | 7.2897 | 6.231 | 8.4545 | 94.9874 | 225.9299 | 59.0323 | 68.6322 | 16.4499 | 149.8564 | 40.5578
42810.4546 | 1261 | 17.3846 | 17.8002 | 17.9583 | 18.0054 | 17.369 | 16.0652 | 15.485 | 16.5146 | 16.9005 | 17.0597 | 17.0809 | 16.6205 | 15.6656 | 14.5019 | 49.293 | 64.9721 | 63.9309 | 89.2816 | 83.9395 | 95.1706 |  |  |  | 60.4905 | 89.3385 | 605.0452 | 707.8636 | 724.4259 | 714.1868 | 116.9155 | 153.5951 | 982.9226 | 94.2283 | 134.8272 | 861.1943 | 968.2407 | 846.3625 |  | 241.9492 | 983.215 | 960.9005 | 543.8036 |  | 488.0766 | 737.092 | 565.9938 | 749.1925 | 925.3477 | 1029.9914 | 1056.4193 | 47.8404 | 415.0069 | 76.1855 | 635.6572 | 15.152 | 50.2832 | 49.0767 | 52.2482 | 64.3702 |  |  | 1.2967 | -0.12148 | 0.12999 | -1.5147 | 8.4375 | 6.365 | 10.9652 | -2.7095 | 21.2875 | 55.3864 | 48.8825 | -0.00010842 | -4.107e-05 | -0.0007294 | 39.4809 | 17.1405 | 16.6736 | 17.0423 | 17.0601 | 16.0752 | 14.7185 | 16.7011 | 17.045 | 17.3853 | 17.4779 | 17.2221 | 16.4198 | 14.7562 | 718.4901 | 512.8804 | 442.9714 | 290.852 | 265.709 | 761.5366 | 460.3248 | 34.9253 | 52.2715 | 57.4377 | 87.2852 | 89.2969 | 94.291 |  |  |  | 644.6172 | 599.7247 | 603.427 | 631.2159 | 93.6197 | 28.8885 | 955.0169 |  |  | 894.7689 |  |  | 26.6789 | 65.3643 | 651.3448 | 28.8829 | 67.8733 | 912.0321 | 761.8079 | 690.5101 | 937.2679 | 940.8184 | 765.9173 |  | 858.2439 | 947.1446 | 1132.1529 | 666.053 | 730.4967 | 945.8921 |  | 439.6257 |  |  | 487.8229 | 676.3599 | 759.2687 | [6 empty] | 682.1106 |  |  | 493.9127 |  |  | 533.7352 | 713.5766 | 716.7377 | 987.3042 | 1139.7337 | 1101.2428 | 568.2701 | 781.6592 | 895.2362 | 643.9226 | 743.9976 | 1023.1255 | 1155.3833 | 665.8625 | 896.138 | 924.9253 | 1081.037 | 1111.7478 | 569.9216 | 675.1961 | 731.9975 | 634.358 | 802.3501 | 949.5094 | 1021.189 | 1128.8582 | 624.8658 | 718.6185 | 736.9835 | 919.6732 | 117.8874 | -0.0001182 | 17.7165 | 4.8528 | -40.3799 | 3.1206 | 9327.45 | 0.26 | 2.4936 | -0.77202 | 0.7986 | -2.7261 | 7.3075 | 6.3469 | 8.3305 | 95.4695 | 226.2769 | 59.3217 | 69.7687 | 18.3387 | 146.4432 | 40.5988
42810.4546 | 1262 | 17.3744 | 17.7987 | 17.9534 | 18.0084 | 17.3676 | 16.0605 | 15.4834 | 16.5119 | 16.9061 | 17.0624 | 17.078 | 16.616 | 15.6621 | 14.5028 | 49.4216 | 65.0741 | 64.0336 | 89.2853 | 83.9327 | 95.1969 |  |  |  | 60.6182 | 89.3417 | 606.3206 | 708.104 | 724.6543 | 714.7266 | 114.0482 | 171.0288 | 1012.0794 | 122.6379 | 147.9951 | 874.3591 | 955.2895 | 866.8414 |  | 243.9831 | 979.5699 | 956.7537 | 550.3273 |  | 486.2817 | 735.5831 | 565.6694 | 747.0479 | 928.409 | 1029.9589 | 1056.1334 | 47.7207 | 414.8437 | 76.6886 | 635.2405 | 15.1501 | 50.282 | 49.0544 | 52.2551 | 64.3719 |  |  | 1.0601 | -1.5546 | 0.078076 | -0.85819 | 8.9645 | 5.7769 | 10.3804 | -3.1123 | 21.0234 | 54.304 | 55.84 | -0.00012485 | -0.00011992 | -0.0007064 | 39.5816 | 17.1516 | 16.6776 | 17.0438 | 17.0651 | 16.073 | 14.7213 | 16.7025 | 17.047 | 17.3906 | 17.472 | 17.2226 | 16.4165 | 14.7552 | 740.8721 | 520.7017 | 446.0276 | 283.4965 | 260.689 | 762.5005 | 460.7434 | 35.0524 | 52.375 | 57.5286 | 87.3143 | 89.3314 | 94.326 |  |  |  | 644.4711 | 598.9687 | 604.6128 | 629.0345 | 96.8858 | 35.8725 | 949.56 |  |  | 880.1729 |  |  | 26.729 | 65.4336 | 652.233 | 28.9537 | 67.9229 | 912.3948 | 764.7209 | 691.3382 | 929.0458 | 937.5427 | 771.4206 |  | 860.2457 | 934.4707 | 1131.9468 | 667.5467 | 731.9096 | 938.3425 |  | 440.4634 |  |  | 489.4829 | 682.0296 | 763.5242 | [6 empty] | 683.4092 |  |  | 495.6649 |  |  | 534.2376 | 716.5726 | 717.7778 | 978.3641 | 1140.9747 | 1101.8124 | 568.4856 | 782.1978 | 896.229 | 645.9566 | 745.2644 | 1024.0401 | 1153.8718 | 665.6287 | 897.2672 | 922.8726 | 1081.3334 | 1112.9803 | 570.9744 | 675.8689 | 732.1335 | 635.0331 | 802.42 | 947.5004 | 1020.8228 | 1128.391 | 625.844 | 718.9914 | 738.259 | 919.9909 | 100.6884 | -0.00049703 | 17.7162 | 4.8501 | -40.3361 | 3.1206 | 9391.84 | 0.32 | 2.2553 | -2.7598 | 0.61846 | -2.0504 | 7.5322 | 6.0465 | 8.1052 | 96.0315 | 226.4935 | 59.6441 | 67.6314 | 18.0832 | 140.3703 | 40.6298
42810.4547 | 1263 | 17.3795 | 17.8005 | 17.9671 | 18.0097 | 17.3695 | 16.0636 | 15.4926 | 16.5113 | 16.9008 | 17.0568 | 17.0823 | 16.6119 | 15.6652 | 14.5021 | 49.552 | 65.1737 | 64.1265 | 89.2786 | 83.9551 | 95.2261 |  |  |  | 60.7466 | 89.3506 | 607.2979 | 708.3595 | 724.713 | 714.9701 | 110.2789 | 134.6569 | 993.6437 | 124.4768 | 161.9276 | 879.8022 | 953.0946 | 873.402 |  | 249.3464 | 979.8082 | 948.0226 | 572.5031 |  | 485.4543 | 734.3226 | 565.0273 | 746.7956 | 933.1608 | 1032.3867 | 1059.3465 | 48.2001 | 414.7097 | 77.6463 | 635.1128 | 15.1546 | 50.2541 | 49.0452 | 52.2668 | 64.439 |  |  | 1.1666 | -1.8188 | 0.51374 | -1.0685 | 8.5203 | 7.5472 | 11.7905 | -2.5031 | 20.6983 | 55.2093 | 64.271 | -7.557e-05 | -7.064e-05 | -0.00068176 | 39.6964 | 17.1574 | 16.6735 | 17.0427 | 17.0614 | 16.076 | 14.7217 | 16.7027 | 17.0416 | 17.3906 | 17.4694 | 17.2227 | 16.4164 | 14.758 | 754.514 | 526.5224 | 467.2847 | 282.6113 | 251.9908 | 763.9012 | 461.639 | 35.1752 | 52.4749 | 57.6131 | 87.3524 | 89.3578 | 94.363 |  |  |  | 644.2863 | 598.9435 | 605.8362 | 628.7622 | 76.9718 | 31.9827 | 946.4817 |  |  | 886.2669 |  |  | 26.7897 | 65.4961 | 652.668 | 29.0151 | 67.9672 | 910.858 | 763.9022 | 690.5777 | 932.0449 | 940.7175 | 771.1633 |  | 861.0106 | 935.5987 | 1132.1115 | 667.5347 | 732.9009 | 933.5157 |  | 441.2513 |  |  | 490.5062 | 682.2425 | 764.1939 | [6 empty] | 682.7245 |  |  | 495.6546 |  |  | 534.5387 | 718.9356 | 718.6213 | 970.6361 | 1140.4842 | 1106.2164 | 569.0448 | 781.8922 | 895.9776 | 648.607 | 746.9906 | 1023.4785 | 1159.906 | 665.7931 | 895.6984 | 916.0659 | 1079.7578 | 1111.3503 | 572.4015 | 676.1268 | 732.341 | 636.5199 | 806.1517 | 948.4935 | 1020.6137 | 1127.2897 | 626.5012 | 719.5758 | 740.4226 | 923.2176 | 114.6176 | 0.0003097 | 17.7167 | 4.8429 | -40.4173 | 3.1207 | 9442.41 | 0.32 | 2.3661 | -2.9832 | 1.5855 | -2.2865 | 7.35 | 6.9176 | 8.6463 | 96.3127 | 226.5703 | 59.9006 | 66.6249 | 15.9012 | 138.773 | 40.5998
42810.4547 | 1264 | 17.3889 | 17.8072 | 17.9678 | 18.0081 | 17.367 | 16.0519 | 15.507 | 16.5175 | 16.9034 | 17.0646 | 17.0876 | 16.63 | 15.6689 | 14.5111 | 49.685 | 65.2828 | 64.2509 | 89.2845 | 83.9945 | 95.2436 |  |  |  | 60.8812 | 89.3721 | 608.9413 | 709.3754 | 725.4243 | 715.847 | 108.9171 | 145.2777 | 985.8911 | 100.659 | 140.8512 | 863.1063 | 912.9529 | 827.9488 |  | 249.707 | 945.4688 | 907.3374 | 585.5153 |  | 486.2687 | 734.2091 | 566.8218 | 746.1188 | 938.1138 | 1034.1111 | 1061.6008 | 49.702 | 414.504 | 77.8203 | 634.7526 | 15.1554 | 50.1933 | 49.0683 | 52.2852 | 64.5735 |  |  | 1.4577 | -1.4581 | -0.59481 | -0.78263 | 8.4973 | 6.8059 | 11.0138 | -3.1635 | 20.4451 | 55.0069 | 63.3435 | -0.00018071 | -0.00010842 | -0.00077047 | 39.798 | 17.1687 | 16.6746 | 17.045 | 17.0589 | 16.0727 | 14.723 | 16.7021 | 17.0375 | 17.3833 | 17.4768 | 17.2211 | 16.4196 | 14.7529 | 734.0604 | 515.5203 | 449.335 | 276.5447 | 242.7741 | 763.7054 | 461.4731 | 35.3114 | 52.5796 | 57.7042 | 87.3872 | 89.3955 | 94.4074 |  |  |  | 644.1867 | 598.7493 | 606.7376 | 627.5537 | 89.0577 | 31.2145 | 947.1033 |  |  | 891.5967 |  |  | 26.8384 | 65.5519 | 653.6877 | 29.0709 | 68.0206 | 908.3782 | 762.6199 | 688.3402 | 935.0014 | 940.6809 | 767.7661 |  | 861.4356 | 936.1225 | 1132.3073 | 665.6651 | 733.428 | 937.1241 |  | 442.0394 |  |  | 492.2003 | 680.5524 | 762.4098 | [6 empty] | 680.5494 |  |  | 495.3305 |  |  | 534.4578 | 721.7973 | 719.4373 | 967.8524 | 1139.5049 | 1110.3871 | 569.7776 | 780.4637 | 897.5601 | 649.8927 | 748.6521 | 1019.3365 | 1159.1261 | 666.5587 | 896.0816 | 915.1412 | 1078.8574 | 1109.8103 | 574.5666 | 676.2194 | 732.4969 | 640.5383 | 808.082 | 947.9845 | 1021.8212 | 1124.1307 | 626.7391 | 719.6677 | 743.91 | 924.0857 | 116.5758 | -0.00048301 | 17.7168 | 4.8388 | -40.3762 | 3.1207 | 9396.51 | 0.33 | 2.6461 | -2.6708 | -1.7059 | -1.9568 | 7.345 | 6.5734 | 8.3621 | 96.5596 | 226.6845 | 60.089 | 68.8263 | 17.8623 | 121.3161 | 40.6132
42810.4547 | 1265 | 17.3854 | 17.808 | 17.9596 | 18.008 | 17.3595 | 16.0561 | 15.5053 | 16.5132 | 16.9041 | 17.056 | 17.083 | 16.627 | 15.6595 | 14.5049 | 49.8179 | 65.3844 | 64.3541 | 89.3033 | 84.0275 | 95.2352 |  |  |  | 60.9932 | 89.3818 | 610.0278 | 709.4393 | 724.7191 | 715.638 | 68.8804 | 106.9508 | 937.0788 | 67.257 | 92.6165 | 829.0064 | 945.1 | 816.3361 |  | 246.2878 | 949.9593 | 898.5479 | 678.1501 |  | 487.3249 | 735.0136 | 570.8093 | 748.4068 | 940.1991 | 1033.3228 | 1062.5849 | 51.4275 | 414.2845 | 76.0089 | 634.3216 | 15.1481 | 50.1189 | 49.0911 | 52.3088 | 64.745 |  |  | 1.4984 | -1.2129 | -0.44039 | -0.68669 | 7.8074 | 5.6343 | 10.9941 | -2.7607 | 21.297 | 53.1279 | 62.0352 | -0.00015114 | -8.707e-05 | -0.00073104 | 39.9062 | 17.1802 | 16.6728 | 17.0436 | 17.0624 | 16.077 | 14.721 | 16.7014 | 17.046 | 17.3878 | 17.4742 | 17.2252 | 16.4172 | 14.7536 | 731.7868 | 533.8036 | 463.6695 | 270.2275 | 240.9909 | 763.7588 | 461.6507 | 35.4149 | 52.6734 | 57.7844 | 87.4036 | 89.4202 | 94.4422 |  |  |  | 643.9365 | 598.0457 | 607.224 | 625.6908 | 79.1271 | 36.2394 | 946.3658 |  |  | 886.2934 |  |  | 26.8724 | 65.6196 | 654.1758 | 29.1434 | 68.0565 | 906.0528 | 763.0457 | 686.6614 | 929.4817 | 934.5726 | 767.3252 |  | 862.4749 | 927.573 | 1133.2043 | 663.5759 | 733.9008 | 936.0224 |  | 442.6545 |  |  | 493.1066 | 679.0696 | 761.8989 | [6 empty] | 678.3521 |  |  | 494.0432 |  |  | 534.0644 | 724.1988 | 719.6755 | 976.7994 | 1138.2821 | 1114.784 | 570.5638 | 780.9777 | 900.9663 | 650.3876 | 749.1609 | 1014.1908 | 1158.8539 | 667.6246 | 898.2827 | 913.6357 | 1077.0948 | 1107.1777 | 575.6127 | 676.7049 | 733.2699 | 645.8547 | 810.6048 | 950.5972 | 1020.9385 | 1120.8143 | 627.4601 | 720.4811 | 749.2012 | 927.2707 | 110.6839 | -0.00036376 | 17.7191 | 4.8361 | -40.3761 | 3.1207 | 9365.42 | 0.38 | 2.6825 | -2.437 | -1.4684 | -1.8336 | 7.0383 | 5.9791 | 8.3521 | 96.9454 | 227.5122 | 60.2696 | 69.0983 | 16.3052 | 132.3056 | 40.6142
42810.4547 | 1266 | 17.3804 | 17.799 | 17.9577 | 18.0026 | 17.367 | 16.0571 | 15.5079 | 16.5205 | 16.8986 | 17.0552 | 17.0794 | 16.6226 | 15.6607 | 14.5012 | 49.9443 | 65.4847 | 64.4669 | 89.3095 | 84.0894 | 95.2402 |  |  |  | 61.1397 | 89.3864 | 610.587 | 709.0772 | 723.6463 | 715.1754 | 26.195 | 64.1083 | 902.7627 | 30.5539 | 67.0126 | 825.3887 | 907.3599 | 809.3819 |  | 265.0392 | 898.0933 | 911.1285 | 695.3777 |  | 486.9332 | 734.249 | 569.2348 | 746.2782 | 934.0192 | 1028.2049 | 1059.1036 | 51.3462 | 414.1206 | 75.4677 | 633.7965 | 15.1441 | 50.0672 | 49.1142 | 52.3288 | 64.938 |  |  | 1.5142 | -0.90673 | -0.42068 | -1.1289 | 9.297 | 6.7297 | 11.6762 | -3.1379 | 21.8855 | 57.8411 | 59.0329 | -0.00014621 | -0.00010349 | -0.00071954 | 40.0151 | 17.1871 | 16.6758 | 17.0482 | 17.0577 | 16.0731 | 14.731 | 16.7051 | 17.0424 | 17.3913 | 17.4766 | 17.2221 | 16.4199 | 14.7548 | 737.4079 | 532.2757 | 493.3491 | 289.4019 | 253.9457 | 763.5097 | 462.2218 | 35.5393 | 52.7698 | 57.8664 | 87.4311 | 89.4528 | 94.4843 |  |  |  | 643.8759 | 598.3175 | 607.6804 | 626.5446 | 83.1911 | 41.0786 | 942.3264 |  |  | 883.6343 |  |  | 26.8762 | 65.6815 | 653.9035 | 29.216 | 68.1173 | 905.6918 | 764.7292 | 687.1845 | 926.9224 | 930.5952 | 769.0509 |  | 863.9454 | 933.1345 | 1133.6035 | 663.0441 | 734.6946 | 936.5292 |  | 443.2045 |  |  | 493.3067 | 681.6554 | 763.4158 | [6 empty] | 678.931 |  |  | 494.2562 |  |  | 533.7279 | 724.6645 | 720.4408 | 973.3958 | 1139.799 | 1117.5518 | 570.8292 | 781.0855 | 904.7549 | 650.0301 | 749.7136 | 1009.8112 | 1162.0175 | 667.781 | 897.2002 | 917.1709 | 1075.0763 | 1107.6309 | 577.1921 | 678.0869 | 735.2034 | 652.7099 | 815.5931 | 954.2305 | 1021.5232 | 1119.6645 | 628.7989 | 722.1896 | 759.3604 | 935.0208 | 111.9289 | 0.00058329 | 17.72 | 4.8295 | -40.3869 | 3.1207 | 9326 | 0.41 | 2.6959 | -2.1062 | -1.4346 | -2.3502 | 7.6654 | 6.5217 | 8.5904 | 97.4278 | 227.6208 | 60.4905 | 68.3831 | 13.1224 | 116.0072 | 40.5782
42810.4547 | 1267 | 17.3797 | 17.7919 | 17.958 | 18.0012 | 17.3638 | 16.0621 | 15.5043 | 16.5163 | 16.8997 | 17.0592 | 17.0817 | 16.6232 | 15.6616 | 14.5039 | 50.1107 | 65.5802 | 64.5551 | 89.2979 | 84.1634 | 95.259 |  |  |  | 61.2569 | 89.3912 | 613.9631 | 711.4412 | 726.8191 | 718.0636 | 84.5994 | 103.7123 | 951.6989 | 77.5409 | 114.4613 | 825.8882 | 912.6314 | 811.9272 |  | 246.0373 | 949.0212 | 960.6221 | 536.3993 |  | 484.8537 | 733.0884 | 568.2135 | 743.7827 | 927.6387 | 1027.8779 | 1057.6772 | 49.7459 | 413.8594 | 76.1145 | 633.2034 | 15.1597 | 50.05 | 49.1398 | 52.3691 | 65.1798 |  |  | 1.7416 | -0.061025 | 0.048504 | -0.97056 | 7.9677 | 5.8301 | 10.3771 | -2.8948 | 21.0151 | 54.5155 | 53.9791 | -0.00012157 | -0.00012649 | -0.0007524 | 40.1267 | 17.1993 | 16.6774 | 17.0405 | 17.0612 | 16.0837 | 14.7267 | 16.7084 | 17.0544 | 17.3916 | 17.4791 | 17.2173 | 16.4177 | 14.7564 | 748.8248 | 546.189 | 518.9703 | 303.3157 | 260.4551 | 763.4431 | 463.17 | 35.651 | 52.86 | 57.9438 | 87.4698 | 89.469 | 94.5278 |  |  |  | 644.0563 | 599.433 | 607.9267 | 629.5189 | 92.2953 | 34.9459 | 939.7056 |  |  | 880.8912 |  |  | 26.9621 | 65.7355 | 656.4276 | 29.2684 | 68.1777 | 906.3468 | 765.8972 | 689.0131 | 930.9645 | 933.019 | 770.1634 |  | 865.0133 | 936.4492 | 1133.9711 | 664.1954 | 735.9563 | 940.9389 |  | 443.7256 |  |  | 493.4076 | 681.8115 | 764.6028 | [6 empty] | 680.7259 |  |  | 495.539 |  |  | 533.4866 | 723.5363 | 722.1683 | 968.8738 | 1140.054 | 1116.5018 | 570.8672 | 781.486 | 906.0846 | 649.2901 | 749.8834 | 1011.3205 | 1169.0242 | 669.1834 | 898.1887 | 918.7432 | 1074.0646 | 1109.9884 | 578.2077 | 679.329 | 736.4341 | 656.6873 | 830.2495 | 959.4758 | 1021.6807 | 1121.229 | 629.734 | 723.0977 | 772.2033 | 960.5001 | 108.9295 | -0.00027255 | 17.7208 | 4.8218 | -40.4495 | 3.1207 | 9255.87 | 0.4 | 2.8955 | -0.5461 | 0.48686 | -2.1779 | 7.0954 | 6.0695 | 8.0974 | 97.7831 | 227.7711 | 60.7871 | 67.0903 | 10.4667 | 122.5499 | 40.5322
42810.4547 | 1268 | 17.3758 | 17.7948 | 17.9527 | 17.9998 | 17.3651 | 16.0596 | 15.5058 | 16.5152 | 16.9033 | 17.0608 | 17.0824 | 16.6246 | 15.66 | 14.5064 | 50.2039 | 65.6754 | 64.6576 | 89.3065 | 84.2232 | 95.2455 |  |  |  | 61.3861 | 89.397 | 618.0832 | 714.3553 | 730.0347 | 721.1422 | 135.2328 | 157.5202 | 986.1563 | 109.7471 | 150.9209 | 807.7973 | 954.6214 | 814.2542 |  | 238.2457 | 983.0105 | 953.9232 | 554.7238 |  | 484.3034 | 734.7554 | 567.1378 | 748.0217 | 931.3467 | 1030.6567 | 1056.7908 | 49.5163 | 413.6892 | 77.4954 | 632.7609 | 15.1692 | 50.0354 | 49.1661 | 52.4089 | 65.4011 |  |  | 2.2022 | -0.81277 | -0.00012 | -0.82665 | 8.4553 | 6.4813 | 10.9429 | -2.8126 | 21.0156 | 55.1162 | 53.1277 | -0.00013635 | -0.00010349 | -0.00073597 | 40.2453 | 17.2055 | 16.6755 | 17.0394 | 17.0636 | 16.0824 | 14.7162 | 16.7059 | 17.0462 | 17.3941 | 17.4782 | 17.2249 | 16.415 | 14.7487 | 758.3031 | 542.1063 | 513.3242 | 302.4581 | 261.9292 | 764.3457 | 463.6787 | 35.7818 | 52.9725 | 58.0327 | 87.4967 | 89.5006 | 94.5895 |  |  |  | 644.327 | 600.645 | 608.2965 | 631.688 | 93.0228 | 33.0455 | 941.5042 |  |  | 891.0599 |  |  | 27.056 | 65.8063 | 660.44 | 29.3381 | 68.2343 | 905.192 | 766.0462 | 689.6 | 940.8352 | 938.3741 | 770.3417 |  | 865.8767 | 946.9317 | 1133.6399 | 665.1173 | 736.887 | 938.9968 |  | 444.2149 |  |  | 493.0893 | 683.1654 | 765.193 | [6 empty] | 681.4791 |  |  | 496.798 |  |  | 533.1301 | 722.6885 | 723.4037 | 978.9243 | 1141.4534 | 1116.1108 | 571.6521 | 785.0498 | 907.4257 | 649.1625 | 750.204 | 1017.9802 | 1166.3587 | 670.1723 | 903.8312 | 917.328 | 1074.9508 | 1110.8579 | 578.6853 | 679.9499 | 736.8393 | 659.3989 | 842.6444 | 964.4186 | 1023.2734 | 1122.2722 | 630.1156 | 724.2854 | 777.7201 | 970.8029 | 126.0815 | -0.0011424 | 17.723 | 4.8192 | -40.3341 | 3.1207 | 9208.94 | 0.29 | 3.261 | -1.9946 | -0.024236 | -2.0116 | 7.3171 | 6.4063 | 8.3241 | 98.0912 | 227.2615 | 61.0045 | 66.3658 | 11.1966 | 139.949 | 40.5268
42810.4547 | 1269 | 17.3763 | 17.7975 | 17.9471 | 17.9977 | 17.3629 | 16.0562 | 15.5169 | 16.523 | 16.8942 | 17.0574 | 17.0784 | 16.6246 | 15.6582 | 14.5035 | 50.341 | 65.7651 | 64.7566 | 89.315 | 84.2099 | 95.2304 |  |  |  | 61.5111 | 89.4189 | 622.022 | 716.7427 | 732.5009 | 723.3552 | 95.9944 | 166.1236 | 1000.1585 | 118.9602 | 133.0685 | 845.3115 | 967.3997 | 844.5832 |  | 244.4808 | 928.2044 | 908.8869 | 620.0121 |  | 483.3066 | 735.3018 | 567.1645 | 749.4423 | 932.9667 | 1030.674 | 1056.7902 | 49.1183 | 413.7789 | 77.6749 | 632.6353 | 15.164 | 50.0364 | 49.1776 | 52.4446 | 65.6641 |  |  | 1.986 | -1.2826 | 0.08596 | -0.83914 | 8.9185 | 6.5937 | 10.7595 | -3.8055 | 21.5381 | 55.9621 | 50.3225 | -0.00014292 | -0.00012814 | -0.0007524 | 40.3408 | 17.2193 | 16.6697 | 17.0382 | 17.0564 | 16.0735 | 14.7214 | 16.7038 | 17.0376 | 17.3863 | 17.4727 | 17.2206 | 16.4148 | 14.7544 | 773.2439 | 533.0335 | 489.8301 | 303.8402 | 270.0727 | 766.1067 | 464.2441 | 35.9096 | 53.0621 | 58.1211 | 87.5221 | 89.5235 | 94.6357 |  |  |  | 644.3851 | 600.8373 | 608.3553 | 630.1494 | 120.1581 | 32.7261 | 947.1831 |  |  | 900.4831 |  |  | 27.1016 | 65.8791 | 664.0881 | 29.4084 | 68.2853 | 904.659 | 768.2214 | 688.9071 | 948.2455 | 939.5341 | 772.5125 |  | 866.831 | 950.5407 | 1133.1378 | 664.5111 | 737.4865 | 939.9309 |  | 444.694 |  |  | 494.2829 | 687.8614 | 765.8353 | [6 empty] | 680.3839 |  |  | 496.4437 |  |  | 532.5402 | 721.5387 | 724.3009 | 978.0478 | 1146.1113 | 1114.5385 | 571.7242 | 787.118 | 907.7827 | 648.6336 | 750.0154 | 1014.9189 | 1167.8681 | 671.4617 | 903.9427 | 915.4133 | 1078.4506 | 1111.4304 | 578.7933 | 680.7331 | 738.5667 | 659.8827 | 843.5009 | 964.4557 | 1022.3847 | 1122.8939 | 630.4614 | 724.7323 | 776.5681 | 966.7145 | 126.8101 | -0.0014441 | 17.7235 | 4.8186 | -40.2854 | 3.1208 | 9175.47 | 0.31 | 3.1003 | -2.5063 | 0.64885 | -2.0273 | 7.5149 | 6.4616 | 8.2542 | 98.3776 | 226.8305 | 61.1782 | 65.3485 | 13.9213 | 143.9384 | 40.5813
42810.4547 | 1270 | 17.3786 | 17.7932 | 17.9543 | 18.0027 | 17.3629 | 16.0548 | 15.5225 | 16.5195 | 16.8983 | 17.0558 | 17.0772 | 16.6201 | 15.6624 | 14.5019 | 50.4539 | 65.8819 | 64.8637 | 89.303 | 84.2004 | 95.2373 |  |  |  | 61.6472 | 89.4263 | 624.5845 | 718.0669 | 734.2672 | 724.939 | 69.6851 | 94.9034 | 932.5888 | 63.0325 | 91.2187 | 853.5602 | 930.7571 | 839.603 |  | 241.4 | 951.7495 | 942.4932 | 581.887 |  | 482.6906 | 736.0025 | 566.0343 | 745.1871 | 928.3663 | 1030.0427 | 1059.1303 | 48.7432 | 413.8572 | 79.0567 | 632.5882 | 15.1487 | 50.0583 | 49.1945 | 52.4799 | 65.9781 |  |  | 2.0465 | -1.416 | 0.34355 | -0.70443 | 8.9527 | 7.0405 | 11.4817 | -1.9262 | 20.772 | 55.6461 | 47.8665 | -0.00016921 | -0.00013471 | -0.00074911 | 40.4522 | 17.2236 | 16.6737 | 17.0378 | 17.0569 | 16.0751 | 14.7237 | 16.7067 | 17.0438 | 17.3857 | 17.4727 | 17.2149 | 16.415 | 14.7549 | 830.4313 | 542.3988 | 484.6118 | 300.0175 | 258.0544 | 770.0874 | 464.5696 | 36.03 | 53.1575 | 58.2001 | 87.5568 | 89.5457 | 94.6781 |  |  |  | 644.26 | 600.1068 | 608.4399 | 627.844 | 95.1349 | 34.0847 | 949.4496 |  |  | 901.3516 |  |  | 27.1564 | 65.9448 | 667.2365 | 29.4761 | 68.3368 | 907.3882 | 771.4327 | 687.9192 | 944.1127 | 936.3298 | 780.2625 |  | 868.7335 | 949.9605 | 1132.2585 | 663.998 | 738.1941 | 947.0315 |  | 445.0339 |  |  | 495.8765 | 694.6257 | 770.0448 | [6 empty] | 679.5155 |  |  | 495.4706 |  |  | 532.6831 | 720.6476 | 725.1293 | 991.7209 | 1138.5634 | 1117.3438 | 571.7238 | 788.6296 | 908.1111 | 648.6264 | 750.5454 | 1011.373 | 1175.6011 | 672.6884 | 905.3248 | 914.1601 | 1078.5703 | 1112.8262 | 578.6539 | 680.7272 | 738.6345 | 661.2049 | 841.4515 | 963.4946 | 1021.8196 | 1124.8428 | 630.6703 | 723.7023 | 778.5046 | 963.5808 | 104.613 | -0.00049703 | 17.7267 | 4.8199 | -40.2815 | 3.1207 | 9176.01 | 0.3 | 3.1496 | -2.6344 | 1.2976 | -1.8581 | 7.5275 | 6.6754 | 8.5246 | 98.856 | 226.268 | 61.378 | 60.4559 | 14.5669 | 128.8027 | 40.62
42810.4547 | 1271 | 17.3872 | 17.8012 | 17.9531 | 17.9961 | 17.3655 | 16.0551 | 15.5237 | 16.5207 | 16.9062 | 17.0667 | 17.0804 | 16.6262 | 15.6688 | 14.5087 | 50.5859 | 65.9777 | 64.9715 | 89.3277 | 84.2352 | 95.2542 |  |  |  | 61.7805 | 89.4483 | 625.3269 | 717.8896 | 733.6803 | 725.1068 | 92.4267 | 134.0739 | 946.2532 | 44.3392 | 76.3256 | 857.4364 | 931.8296 | 849.4458 |  | 261.2428 | 893.4701 | 868.6641 | 849.747 |  | 483.0945 | 737.7518 | 566.5581 | 746.2263 | 925.1872 | 1029.501 | 1057.8558 | 48.3825 | 413.8605 | 79.7383 | 632.6563 | 15.107 | 50.0709 | 49.1962 | 52.4957 | 66.2289 |  |  | 1.6851 | -0.56569 | 0.70299 | -0.16297 | 7.875 | 6.39 | 11.1413 | -2.9289 | 20.7298 | 55.3 | 46.8901 | -0.00015278 | -4.928e-05 | -0.00077704 | 40.5559 | 17.229 | 16.6715 | 17.0328 | 17.0459 | 16.0688 | 14.7197 | 16.7045 | 17.0404 | 17.3792 | 17.4665 | 17.2159 | 16.4137 | 14.7432 | 827.0465 | 542.1019 | 477.3631 | 295.2891 | 256.7152 | 771.9892 | 464.6726 | 36.1505 | 53.2491 | 58.2786 | 87.5941 | 89.5691 | 94.716 |  |  |  | 644.0481 | 599.6428 | 608.7975 | 625.9647 | 87.7335 | 34.2509 | 947.2954 |  |  | 896.5103 |  |  | 27.1984 | 66.0033 | 667.8939 | 29.5348 | 68.3785 | 909.6144 | 771.3812 | 686.9151 | 936.2015 | 933.7119 | 782.1576 |  | 870.0693 | 937.3924 | 1131.325 | 663.4667 | 738.9653 | 954.9707 |  | 443.7157 |  |  | 496.5005 | 692.3341 | 772.0335 | [6 empty] | 678.5664 |  |  | 494.6762 |  |  | 533.3725 | 720.7665 | 725.8867 | 1004.5915 | 1135.3487 | 1119.7906 | 572.0852 | 790.2608 | 909.6684 | 648.9814 | 752.1776 | 1018.7108 | 1177.4262 | 673.2431 | 907.7741 | 908.8449 | 1079.1734 | 1114.6519 | 577.9268 | 680.3936 | 738.4698 | 665.9563 | 843.4624 | 966.8289 | 1021.0348 | 1128.0779 | 630.1166 | 723.3549 | 783.6988 | 966.209 | 94.1251 | 5.0162e-05 | 17.7313 | 4.8219 | -40.3366 | 3.1207 | 9186.85 | 0.32 | 2.8582 | -1.6665 | 1.8578 | -0.89448 | 7.0584 | 6.3582 | 8.3955 | 99.2924 | 226.0041 | 61.5953 | 61.5344 | 15.3931 | 121.817 | 40.6292
42810.4548 | 1272 | 17.3915 | 17.8017 | 17.9548 | 18.0049 | 17.3731 | 16.0611 | 15.5304 | 16.5246 | 16.9053 | 17.0629 | 17.0852 | 16.6233 | 15.6714 | 14.5143 | 50.7092 | 66.0785 | 65.0733 | 89.3403 | 84.2651 | 95.2427 |  |  |  | 61.9084 | 89.4633 | 624.496 | 716.4923 | 731.1951 | 723.7183 | 29.8602 | 65.6241 | 905.8008 | 28.1422 | 63.6402 | 856.2833 | 925.4717 | 853.2453 |  | 246.8465 | 905.281 | 876.4081 | 862.9398 |  | 484.0205 | 740.2361 | 568.9292 | 745.1194 | 923.1666 | 1030.8882 | 1057.9435 | 47.5996 | 413.8847 | 78.3446 | 632.6411 | 15.1056 | 50.0913 | 49.2304 | 52.514 | 66.3716 |  |  | 1.2547 | -1.2892 | 0.030108 | -1.1513 | 7.9388 | 5.4884 | 10.6596 | -2.3448 | 20.5214 | 55.3012 | 48.961 | -0.00015442 | -0.00010185 | -0.0007524 | 40.6589 | 17.2258 | 16.6628 | 17.0266 | 17.0477 | 16.0645 | 14.7185 | 16.7044 | 17.0358 | 17.3826 | 17.4674 | 17.2157 | 16.4179 | 14.7451 | 811.0117 | 552.9269 | 480.9204 | 293.348 | 256.4166 | 773.2187 | 464.7072 | 36.2791 | 53.348 | 58.3714 | 87.6299 | 89.6018 | 94.7726 |  |  |  | 643.9128 | 599.7997 | 609.6618 | 627.4108 | 97.1409 | 40.5298 | 944.3754 |  |  | 889.0039 |  |  | 27.2643 | 66.0676 | 666.0522 | 29.6131 | 68.4382 | 916.2631 | 768.5746 | 686.285 | 931.0018 | 931.3948 | 778.893 |  | 869.8983 | 932.3832 | 1131.1601 | 662.6841 | 739.6371 | 956.6472 |  | 441.9323 |  |  | 496.4107 | 687.6204 | 769.7986 | [6 empty] | 677.9193 |  |  | 494.7123 |  |  | 534.1683 | 722.2095 | 726.7764 | 1004.7727 | 1136.6595 | 1119.2555 | 572.6634 | 790.6014 | 909.7694 | 650.1169 | 755.5112 | 1015.6642 | 1176.297 | 672.6858 | 905.5566 | 908.3757 | 1082.7759 | 1117.1395 | 577.5414 | 680.6322 | 740.4591 | 674.054 | 848.7917 | 969.5321 | 1021.6352 | 1132.1458 | 630.1008 | 724.144 | 791.393 | 969.8433 | 95.3021 | 0.00048511 | 17.7339 | 4.8283 | -40.5444 | 3.1207 | 9200.7 | 0.41 | 2.4646 | -2.5189 | 0.38494 | -2.3804 | 7.0907 | 5.8957 | 8.2164 | 99.3204 | 226.035 | 61.7938 | 63.7715 | 15.0048 | 118.7709 | 40.5616
42810.4548 | 1273 | 17.3785 | 17.7968 | 17.9536 | 17.993 | 17.3631 | 16.0513 | 15.526 | 16.5268 | 16.9023 | 17.0621 | 17.0873 | 16.6161 | 15.6665 | 14.506 | 50.839 | 66.1816 | 65.1788 | 89.3343 | 84.2852 | 95.2269 |  |  |  | 62.0354 | 89.4789 | 623.3437 | 714.7571 | 728.5852 | 721.6904 | 26.7555 | 66.6704 | 913.6862 | 28.0615 | 65.2619 | 869.575 | 929.8773 | 860.1397 |  | 259.3181 | 911.2853 | 890.1955 | 877.2127 |  | 484.2274 | 740.3783 | 568.8097 | 742.2039 | 919.8081 | 1028.6615 | 1055.7912 | 46.6058 | 413.9423 | 77.0711 | 632.7474 | 15.0759 | 50.1243 | 49.2392 | 52.5189 | 66.5991 |  |  | 1.2113 | -1.5001 | 0.49206 | -0.67749 | 8.1944 | 6.3841 | 11.6138 | -2.4019 | 20.5618 | 55.5072 | 49.7744 | -0.00010842 | -0.00013142 | -0.00076718 | 40.7752 | 17.241 | 16.6714 | 17.0289 | 17.0568 | 16.0675 | 14.7239 | 16.6965 | 17.0385 | 17.3884 | 17.469 | 17.2253 | 16.4175 | 14.756 | 809.429 | 565.282 | 495.6678 | 298.8579 | 261.1976 | 774.5934 | 465.127 | 36.4041 | 53.4596 | 58.4582 | 87.6516 | 89.6306 | 94.8074 |  |  |  | 644.5354 | 603.5448 | 612.3656 | 633.874 | 79.5116 | 39.0658 | 942.234 |  |  | 886.9805 |  |  | 27.3221 | 66.1326 | 663.4643 | 29.6738 | 68.4927 | 921.7835 | 765.5309 | 686.657 | 929.7709 | 931.3992 | 773.9684 |  | 869.2697 | 932.9173 | 1131.6651 | 662.3836 | 740.3377 | 947.909 |  | 441.6099 |  |  | 495.6378 | 684.4582 | 766.4282 | [6 empty] | 678.1289 |  |  | 495.8438 |  |  | 535.3054 | 724.5969 | 728.1175 | 999.381 | 1132.1615 | 1117.9321 | 573.1082 | 787.3876 | 908.0656 | 651.0834 | 758.3675 | 1006.6224 | 1170.3597 | 671.3442 | 898.8409 | 910.6748 | 1084.6876 | 1116.9676 | 577.7613 | 681.3829 | 742.1753 | 677.1164 | 851.4761 | 974.0272 | 1018.8484 | 1133.5157 | 630.5135 | 725.1445 | 793.6489 | 970.8292 | 105.5879 | 5.7172e-05 | 17.7379 | 4.8413 | -40.2946 | 3.1206 | 9267.46 | 0.32 | 2.4192 | -2.7174 | 1.5563 | -1.8261 | 7.1978 | 6.3532 | 8.5689 | 99.2269 | 226.3516 | 61.9869 | 64.458 | 13.4512 | 120.2269 | 40.5084
42810.4548 | 1274 | 17.3839 | 17.8016 | 17.9559 | 18.0031 | 17.3723 | 16.0584 | 15.545 | 16.5267 | 16.8994 | 17.0668 | 17.0909 | 16.6228 | 15.6656 | 14.5123 | 50.9593 | 66.2767 | 65.277 | 89.3022 | 84.3225 | 95.2111 |  |  |  | 62.1581 | 89.4904 | 622.7546 | 713.6825 | 726.885 | 720.4729 | 29.1032 | 65.7873 | 913.5373 | 29.6539 | 67.1732 | 876.5978 | 935.0962 | 867.3004 |  | 261.7063 | 904.9123 | 886.8216 | 883.5077 |  | 483.4992 | 738.4723 | 569.8338 | 739.5208 | 920.2625 | 1027.0119 | 1054.5124 | 45.416 | 414.1652 | 76.9184 | 633.0614 | 15.0227 | 50.2034 | 49.2269 | 52.5223 | 66.7702 |  |  | 1.3217 | -1.0566 | 0.40795 | -0.39493 | 8.6656 | 6.137 | 10.9849 | -3.4927 | 20.0874 | 54.6863 | 51.6732 | -0.00011171 | -9.199e-05 | -0.00072447 | 40.8976 | 17.2721 | 16.6883 | 17.0454 | 17.0654 | 16.0798 | 14.7309 | 16.7161 | 17.0461 | 17.3934 | 17.4849 | 17.2305 | 16.4239 | 14.763 | 795.0657 | 576.2989 | 522.0524 | 315.6818 | 261.0536 | 775.0607 | 465.8714 | 36.5168 | 53.5475 | 58.5372 | 87.6914 | 89.6628 | 94.8427 |  |  |  | 645.1222 | 607.2943 | 614.5939 | 637.9448 | 91.8554 | 38.5009 | 942.9749 |  |  | 889.5215 |  |  | 27.3678 | 66.1872 | 662.0099 | 29.7282 | 68.5463 | 923.0185 | 762.5048 | 687.5915 | 928.0434 | 929.4423 | 768.8313 |  | 868.4485 | 926.1971 | 1131.3912 | 663.0707 | 741.0852 | 950.8885 |  | 441.7656 |  |  | 495.1368 | 681.8519 | 763.1994 | [6 empty] | 679.278 |  |  | 498.6845 |  |  | 535.513 | 726.2592 | 729.3575 | 995.1588 | 1128.0935 | 1117.7386 | 573.6289 | 783.9266 | 905.1184 | 650.8423 | 759.5185 | 1006.0239 | 1171.8833 | 670.8259 | 894.0635 | 909.0357 | 1081.7693 | 1115.4883 | 578.3957 | 682.5356 | 743.3245 | 676.8267 | 851.6413 | 977.5088 | 1015.7254 | 1131.5411 | 631.0978 | 726.3898 | 792.6213 | 967.7167 | 117.1684 | 0.00026063 | 17.7423 | 4.8428 | -40.3236 | 3.1206 | 9280.15 | 0.25 | 2.5255 | -2.2784 | 1.4157 | -1.3929 | 7.3971 | 6.2251 | 8.3284 | 99.0694 | 226.3585 | 62.1652 | 66.2279 | 10.6703 | 122.2714 | 40.5146
42810.4548 | 1275 | 17.3836 | 17.8002 | 17.956 | 17.9967 | 17.3733 | 16.0562 | 15.5485 | 16.5251 | 16.9001 | 17.0602 | 17.0839 | 16.624 | 15.6619 | 14.5097 | 51.0746 | 66.3609 | 65.3683 | 89.25 | 84.3332 | 95.2003 |  |  |  | 62.2616 | 89.4883 | 622.0245 | 712.6529 | 725.2219 | 719.226 | 39.6767 | 70.6165 | 911.5851 | 29.1395 | 68.2462 | 878.5514 | 941.9213 | 865.5863 |  | 261.1887 | 903.09 | 889.6656 | 708.331 |  | 483.6475 | 739.189 | 570.4838 | 741.4794 | 918.7466 | 1025.4297 | 1054.5711 | 42.8483 | 414.2776 | 75.5928 | 633.6315 | 15.0443 | 50.2803 | 49.2321 | 52.536 | 67.035 |  |  | 1.2862 | -1.0329 | 0.31004 | -0.067026 | 7.787 | 6.8079 | 11.322 | -2.5977 | 20.39 | 55.0967 | 51.4535 | -0.00014456 | -8.214e-05 | -0.00073433 | 41.0035 | 17.267 | 16.6726 | 17.0359 | 17.0516 | 16.0677 | 14.7275 | 16.7045 | 17.0383 | 17.3896 | 17.4719 | 17.2163 | 16.4157 | 14.7566 | 798.0575 | 582.9271 | 513.8374 | 325.183 | 272.9363 | 776.2385 | 466.457 | 36.6403 | 53.6424 | 58.6214 | 87.7305 | 89.7021 | 94.889 |  |  |  | 645.7733 | 610.1753 | 616.9488 | 641.2385 | 104.4053 | 38.5635 | 941.7263 |  |  | 881.7829 |  |  | 27.4329 | 66.263 | 660.6539 | 29.7982 | 68.6061 | 920.6182 | 761.4229 | 688.8584 | 920.9321 | 924.7616 | 768.0943 |  | 868.2752 | 915.042 | 1131.3458 | 664.1902 | 741.6249 | 956.1011 |  | 441.8717 |  |  | 495.4074 | 682.4798 | 761.6952 | [6 empty] | 680.7014 |  |  | 501.9981 |  |  | 534.9818 | 726.0527 | 730.2404 | 990.7926 | 1129.0749 | 1120.8518 | 574.1279 | 783.5956 | 902.9264 | 650.4171 | 759.2553 | 1009.6859 | 1177.0417 | 671.4935 | 894.6466 | 906.592 | 1081.3454 | 1115.8597 | 578.7082 | 683.6219 | 744.7994 | 675.2823 | 850.2228 | 977.3785 | 1012.6825 | 1131.3361 | 631.8009 | 727.9137 | 789.6391 | 961.9759 | 106.2568 | 8.0602e-06 | 17.7471 | 4.8494 | -40.326 | 3.1206 | 9284.53 | 0.29 | 2.4898 | -2.2535 | 1.2346 | -0.57405 | 7.0079 | 6.5525 | 8.4501 | 99.0266 | 226.6386 | 62.2769 | 66.3345 | 11.7018 | 130.0806 | 40.5556
42810.4548 | 1276 | 17.3738 | 17.7936 | 17.9523 | 17.9952 | 17.3635 | 16.0493 | 15.5463 | 16.5257 | 16.904 | 17.0554 | 17.0804 | 16.6166 | 15.6616 | 14.5067 | 51.1994 | 66.4632 | 65.468 | 89.1983 | 84.3222 | 95.2264 |  |  |  | 62.397 | 89.5047 | 621.3225 | 711.6718 | 723.7258 | 718.122 | 92.1792 | 149.4153 | 993.2191 | 89.9462 | 125.7878 | 859.6811 | 863.2074 | 823.118 |  | 243.969 | 967.8457 | 948.7802 | 583.5894 |  | 484.881 | 739.2143 | 570.3031 | 744.1193 | 923.2647 | 1027.2873 | 1055.7096 | 41.8848 | 414.5215 | 73.8717 | 634.0244 | 15.0958 | 50.3327 | 49.2262 | 52.5422 | 67.3328 |  |  | 1.3513 | -0.55321 | 0.42963 | -0.87659 | 8.9304 | 6.4616 | 10.7378 | -2.9979 | 21.1914 | 56.5074 | 49.5761 | -0.00019713 | -0.00013635 | -0.00076882 | 41.1131 | 17.274 | 16.6718 | 17.0396 | 17.0574 | 16.078 | 14.736 | 16.7055 | 17.046 | 17.3829 | 17.4709 | 17.2312 | 16.4177 | 14.7544 | 836.5086 | 594.1339 | 523.0266 | 327.1144 | 267.7869 | 778.8937 | 467.2058 | 36.7535 | 53.7362 | 58.6971 | 87.765 | 89.7321 | 94.9269 |  |  |  | 646.5175 | 612.3438 | 619.1977 | 644.1595 | 101.8868 | 39.8222 | 937.8997 |  |  | 875.5206 |  |  | 27.4896 | 66.3242 | 659.4671 | 29.8694 | 68.6462 | 918.2806 | 759.773 | 690.16 | 925.4978 | 932.8738 | 768.1472 |  | 868.1538 | 911.9194 | 1131.1854 | 665.3525 | 742.2387 | 954.3413 |  | 442.0752 |  |  | 495.9888 | 683.7388 | 761.0951 | [6 empty] | 681.8397 |  |  | 503.2276 |  |  | 534.8963 | 725.3623 | 730.5267 | 990.0887 | 1131.9037 | 1124.6847 | 573.9842 | 785.5436 | 901.7934 | 650.1996 | 757.9652 | 1006.4062 | 1180.1863 | 672.9256 | 895.7068 | 906.0364 | 1083.8759 | 1115.8313 | 579.4653 | 684.4129 | 745.8099 | 679.3931 | 847.2524 | 973.4096 | 1011.8362 | 1131.9143 | 632.3449 | 728.2005 | 790.8755 | 956.5769 | 119.824 | -5.5071e-05 | 17.7537 | 4.8554 | -40.384 | 3.1206 | 9263.83 | 0.39 | 2.5505 | -1.6492 | 1.4534 | -2.076 | 7.5101 | 6.3883 | 8.2351 | 98.9809 | 226.6201 | 62.4073 | 63.0557 | 10.8328 | 102.3131 | 40.6263
42810.4548 | 1277 | 17.376 | 17.7954 | 17.9588 | 18.0005 | 17.3671 | 16.0554 | 15.5412 | 16.5349 | 16.8973 | 17.0565 | 17.0803 | 16.6243 | 15.6568 | 14.5105 | 51.3216 | 66.5568 | 65.5709 | 89.1586 | 84.3544 | 95.2637 |  |  |  | 62.5357 | 89.5086 | 620.1765 | 710.0595 | 721.6331 | 716.3738 | 124.8324 | 175.2968 | 1026.2934 | 134.1356 | 170.7457 | 840.4134 | 884.3013 | 819.3993 |  | 236.193 | 985.8747 | 962.4283 | 578.2553 |  | 485.8452 | 739.3478 | 571.7938 | 749.2749 | 931.5854 | 1030.4432 | 1058.1523 | 42.2959 | 414.9543 | 71.881 | 634.1169 | 15.1144 | 50.3734 | 49.2175 | 52.5521 | 67.623 |  |  | 1.2882 | -0.61892 | -0.31225 | -1.2249 | 8.661 | 6.5635 | 11.274 | -2.9624 | 20.0028 | 54.2495 | 48.4996 | -0.00010678 | -9.692e-05 | -0.0007179 | 41.2258 | 17.2826 | 16.6684 | 17.0303 | 17.0579 | 16.0721 | 14.7325 | 16.7101 | 17.0379 | 17.3869 | 17.4666 | 17.224 | 16.4173 | 14.7545 | 848.2978 | 587.1207 | 494.8672 | 321.3347 | 264.9208 | 780.5534 | 467.6459 | 36.878 | 53.8406 | 58.7871 | 87.7988 | 89.7629 | 94.9685 |  |  |  | 647.1457 | 613.1443 | 619.8595 | 643.3441 | 72.9881 | 24.6962 | 942.7913 |  |  | 895.7731 |  |  | 27.5449 | 66.3844 | 658.0989 | 29.9368 | 68.6991 | 915.7447 | 759.7723 | 690.7092 | 940.0826 | 943.2123 | 765.8851 |  | 867.7504 | 925.6271 | 1130.8064 | 666.3379 | 743.0478 | 954.3066 |  | 442.3344 |  |  | 496.6252 | 684.8153 | 759.2572 | [6 empty] | 682.3404 |  |  | 503.1831 |  |  | 534.7202 | 725.0123 | 730.3685 | 991.0471 | 1134.1626 | 1126.7424 | 574.4184 | 787.7581 | 902.2377 | 650.1398 | 756.9376 | 1004.0641 | 1180.8085 | 674.9444 | 898.8373 | 908.8002 | 1086.5472 | 1116.1686 | 579.2713 | 684.4769 | 745.4656 | 688.3641 | 852.1891 | 973.4204 | 1014.3629 | 1134.1154 | 632.5994 | 727.0651 | 796.0246 | 965.1467 | 136.574 | -0.0017177 | 17.759 | 4.8687 | -40.4529 | 3.1206 | 9231.87 | 0.28 | 2.4881 | -1.7445 | -1.2391 | -2.4542 | 7.4049 | 6.4462 | 8.4485 | 98.8966 | 225.9908 | 62.5947 | 62.3695 | 14.0511 | 110.2652 | 40.7773
42810.4548 | 1278 | 17.3751 | 17.7908 | 17.9508 | 18.0006 | 17.3651 | 16.0419 | 15.5497 | 16.5291 | 16.9007 | 17.0624 | 17.0814 | 16.62 | 15.6625 | 14.5148 | 51.444 | 66.6561 | 65.6636 | 89.1209 | 84.374 | 95.2747 |  |  |  | 62.6585 | 89.5018 | 620.1568 | 709.4488 | 721.1987 | 716.0644 | 110.5489 | 167.9124 | 1008.7545 | 127.8743 | 172.699 | 816.2868 | 818.444 | 801.2991 |  | 244.2559 | 980.4838 | 970.0278 | 578.957 |  | 485.0564 | 739.4492 | 571.5735 | 747.8502 | 929.3603 | 1029.9684 | 1057.6485 | 42.6441 | 415.0206 | 71.4955 | 633.896 | 15.1584 | 50.409 | 49.2186 | 52.5607 | 67.8547 |  |  | 1.7685 | -0.39221 | 0.018936 | -0.98633 | 8.0544 | 5.3984 | 11.0414 | -1.6909 | 20.9106 | 56.2495 | 44.8513 | -0.00010349 | -0.00010514 | -0.0007409 | 41.3337 | 17.2962 | 16.6749 | 17.0419 | 17.0666 | 16.0738 | 14.7441 | 16.7127 | 17.0425 | 17.3932 | 17.4792 | 17.2295 | 16.426 | 14.7643 | 790.879 | 553.9032 | 453.9234 | 302.3701 | 255.0489 | 779.254 | 467.1168 | 37.0153 | 53.9386 | 58.8666 | 87.8459 | 89.7882 | 94.9882 |  |  |  | 647.528 | 612.6636 | 618.3826 | 640.8576 | 85.2116 | 30.3785 | 951.4354 |  |  | 911.5006 |  |  | 27.5919 | 66.4389 | 656.6982 | 30.0054 | 68.7397 | 911.9428 | 767.4654 | 690.8835 | 949.8914 | 948.4572 | 773.2816 |  | 869.6128 | 935.2673 | 1131.4319 | 666.9787 | 743.767 | 962.2299 |  | 442.5323 |  |  | 497.8187 | 693.9125 | 763.9741 | [6 empty] | 682.4986 |  |  | 502.7801 |  |  | 534.1894 | 725.207 | 729.9843 | 995.0414 | 1139.7458 | 1126.8817 | 575.2297 | 790.7067 | 905.7501 | 651.4854 | 756.3062 | 1005.3833 | 1181.6618 | 676.3538 | 907.5718 | 911.4327 | 1089.0354 | 1118.8694 | 578.29 | 683.7832 | 744.7253 | 690.3478 | 855.6461 | 977.6462 | 1018.8785 | 1137.2922 | 632.4648 | 725.676 | 795.498 | 969.8775 | 119.0453 | -2.0022e-05 | 17.7635 | 4.8824 | -40.3303 | 3.1205 | 9212.57 | 0.35 | 2.9149 | -1.3888 | 0.30516 | -2.2024 | 7.1396 | 5.8451 | 8.3593 | 99.3716 | 226.1333 | 62.7682 | 68.2609 | 18.4929 | 87.1583 | 40.9246
42810.4548 | 1279 | 17.3849 | 17.7955 | 17.9633 | 17.9987 | 17.3666 | 16.0579 | 15.5649 | 16.5476 | 16.9041 | 17.0658 | 17.0854 | 16.6268 | 15.6648 | 14.5168 | 51.582 | 66.7569 | 65.7646 | 89.1331 | 84.3813 | 95.3008 |  |  |  | 62.7864 | 89.511 | 622.7748 | 711.1938 | 723.2356 | 717.9514 | 126.7732 | 168.8985 | 1016.2347 | 119.6012 | 160.2375 | 822.6843 | 806.3069 | 786.1255 |  | 227.7678 | 991.6351 | 968.2442 | 556.7583 |  | 483.5747 | 739.4104 | 570.8418 | 744.9931 | 919.6019 | 1027.9836 | 1054.3591 | 43.5321 | 414.9503 | 72.7316 | 633.8155 | 15.1743 | 50.437 | 49.2306 | 52.5503 | 68.0623 |  |  | 1.6069 | -0.65309 | 0.46643 | -1.4312 | 8.7306 | 6.9308 | 11.4718 | -3.132 | 21.9394 | 57.5308 | 46.0077 | -5.093e-05 | -9.364e-05 | -0.00074582 | 41.4432 | 17.3054 | 16.6742 | 17.0463 | 17.059 | 16.0831 | 14.7463 | 16.7069 | 17.0429 | 17.391 | 17.4726 | 17.227 | 16.4203 | 14.7673 | 776.3968 | 553.6716 | 460.1441 | 295.1535 | 244.3727 | 778.8287 | 466.6963 | 37.1305 | 54.0344 | 58.9503 | 87.8657 | 89.8116 | 95.0261 |  |  |  | 647.6845 | 611.9161 | 617.1184 | 638.7186 | 84.3805 | 32.7361 | 955.7666 |  |  | 909.6068 |  |  | 27.6467 | 66.4969 | 659.0301 | 30.0653 | 68.7815 | 909.8187 | 772.7432 | 691.324 | 945.1967 | 942.6049 | 782.4817 |  | 871.66 | 932.3291 | 1132.5101 | 667.7944 | 744.6835 | 963.3388 |  | 442.5854 |  |  | 498.7066 | 702.8318 | 771.6192 | [6 empty] | 683.0391 |  |  | 502.2485 |  |  | 534.0388 | 726.7481 | 729.8176 | 998.0614 | 1144.4927 | 1125.1666 | 575.5408 | 793.5359 | 909.3011 | 652.8907 | 756.394 | 1006.5236 | 1179.8164 | 677.1995 | 909.8604 | 912.7103 | 1091.4391 | 1120.7898 | 578.2262 | 683.1434 | 745.1395 | 698.3498 | 855.4531 | 978.69 | 1021.5213 | 1138.4685 | 632.4336 | 724.2801 | 798.4463 | 969.4236 | 113.9855 | 0.0010042 | 17.767 | 4.8936 | -40.4942 | 3.1206 | 9198.13 | 0.32 | 2.7811 | -1.7921 | 1.5145 | -2.6529 | 7.4276 | 6.6179 | 8.5142 | 99.8677 | 226.9232 | 62.9899 | 69.7104 | 17.7163 | 83.9166 | 41.0161
42810.4548 | 1280 | 17.3798 | 17.7998 | 17.9589 | 18.0023 | 17.3594 | 16.0537 | 15.5681 | 16.5374 | 16.8997 | 17.0649 | 17.0804 | 16.6218 | 15.6713 | 14.5155 | 51.6881 | 66.8418 | 65.8663 | 89.1673 | 84.4028 | 95.3276 |  |  |  | 62.9029 | 89.5104 | 625.1372 | 712.7452 | 725.2149 | 719.6106 | 127.686 | 149.5626 | 1007.0106 | 86.498 | 141.5757 | 827.3656 | 803.7574 | 800.0959 |  | 227.2763 | 1000.6471 | 982.1408 | 560.2187 |  | 482.5976 | 740.5194 | 571.6674 | 749.1469 | 920.3198 | 1028.215 | 1054.2526 | 44.2058 | 414.8688 | 73.5445 | 633.9489 | 15.1987 | 50.4765 | 49.2477 | 52.5355 | 68.3098 |  |  | 1.4071 | -0.79897 | -0.15717 | -1.0146 | 7.9618 | 5.8814 | 10.3041 | -1.7711 | 19.9759 | 55.3069 | 46.4043 | -0.00016099 | -0.00017742 | -0.00074582 | 41.5547 | 17.3235 | 16.6701 | 17.0444 | 17.0478 | 16.0663 | 14.7337 | 16.7082 | 17.0373 | 17.3831 | 17.4738 | 17.2225 | 16.4146 | 14.7578 | 786.5588 | 551.0468 | 465.0133 | 308.9609 | 255.6711 | 778.5142 | 466.4658 | 37.2576 | 54.1381 | 59.0322 | 87.8907 | 89.8329 | 95.0602 |  |  |  | 647.5685 | 609.9233 | 616.6922 | 634.5842 | 78.4891 | 27.2807 | 952.0032 |  |  | 902.5696 |  |  | 27.7123 | 66.5741 | 661.9869 | 30.1353 | 68.8521 | 911.3482 | 772.8653 | 690.8574 | 941.8379 | 939.4329 | 782.0328 |  | 872.8416 | 934.8542 | 1134.7427 | 668.0761 | 745.5818 | 970.5248 |  | 442.7042 |  |  | 499.0782 | 700.206 | 773.1538 | [6 empty] | 682.7662 |  |  | 501.3338 |  |  | 534.1632 | 728.5491 | 730.6499 | 994.8119 | 1142.6857 | 1125.8601 | 575.7513 | 793.4678 | 910.6129 | 653.8673 | 758.5938 | 1007.9963 | 1175.3581 | 677.1015 | 909.1799 | 912.7415 | 1090.2114 | 1121.083 | 578.8453 | 683.5881 | 745.0923 | 703.1247 | 857.8185 | 980.8238 | 1020.6748 | 1138.5341 | 633.623 | 723.9719 | 799.9238 | 971.0639 | 102.0622 | -0.0020545 | 17.7693 | 4.9154 | -40.4277 | 3.1205 | 9147.52 | 0.36 | 2.6047 | -1.9833 | -0.87964 | -2.2349 | 7.0937 | 6.0969 | 8.07 | 100.3157 | 228.3248 | 63.2222 | 68.4633 | 17.1285 | 83.0249 | 41.1072
42810.4549 | 1281 | 17.3771 | 17.794 | 17.9564 | 17.999 | 17.3537 | 16.0583 | 15.5686 | 16.5357 | 16.8976 | 17.0567 | 17.0816 | 16.6221 | 15.6688 | 14.5162 | 51.8061 | 66.9472 | 65.9601 | 89.1887 | 84.4107 | 95.3342 |  |  |  | 63.0045 | 89.512 | 626.2876 | 713.0298 | 725.1171 | 719.5943 | 118.4673 | 151.7909 | 1004.6496 | 116.5591 | 159.5493 | 828.8272 | 781.898 | 809.8349 |  | 239.1582 | 995.5787 | 982.6441 | 559.1909 |  | 482.818 | 742.1544 | 571.4751 | 750.2 | 921.5739 | 1028.0366 | 1054.7859 | 43.2697 | 414.7521 | 74.2953 | 633.889 | 15.2375 | 50.4966 | 49.268 | 52.5378 | 68.5369 |  |  | 1.8539 | -1.349 | 0.64385 | 0.15968 | 8.521 | 6.6082 | 11.1564 | -2.0017 | 20.938 | 55.0373 | 46.4999 | -0.00017413 | -6.078e-05 | -0.0007524 | 41.6819 | 17.3254 | 16.6813 | 17.0417 | 17.059 | 16.0822 | 14.7432 | 16.7215 | 17.0428 | 17.3874 | 17.4736 | 17.2294 | 16.4266 | 14.7656 | 770.439 | 534.7579 | 448.7043 | 296.3889 | 245.9802 | 777.5162 | 465.6105 | 37.3772 | 54.2265 | 59.1107 | 87.9096 | 89.8539 | 95.0934 |  |  |  | 647.323 | 608.1866 | 616.9729 | 631.4812 | 81.7311 | 29.7567 | 950.4283 |  |  | 900.0775 |  |  | 27.7718 | 66.6261 | 663.3754 | 30.2201 | 68.9136 | 912.7519 | 770.5626 | 691.0201 | 939.8168 | 939.1043 | 777.1148 |  | 873.6119 | 928.4764 | 1136.8991 | 668.1019 | 746.3024 | 975.7694 |  | 442.9254 |  |  | 499.1575 | 694.7297 | 771.8364 | [6 empty] | 682.3006 |  |  | 501.4727 |  |  | 534.2739 | 730.9769 | 731.8603 | 988.0365 | 1142.8342 | 1124.0211 | 575.0672 | 792.8534 | 909.9532 | 653.7884 | 760.4511 | 1010.6597 | 1175.643 | 676.4811 | 905.2724 | 910.1273 | 1089.2388 | 1121.0685 | 580.5494 | 684.8219 | 746.4273 | 712.4144 | 855.7621 | 979.1121 | 1016.644 | 1137.1239 | 634.8407 | 725.1532 | 804.194 | 967.8326 | 102.8193 | -0.00038479 | 17.7729 | 4.9255 | -40.401 | 3.1205 | 9130.65 | 0.34 | 2.9897 | -2.5791 | 1.7818 | 0.88734 | 7.3381 | 6.4621 | 8.3965 | 100.7369 | 229.9298 | 63.4144 | 69.8807 | 18.7672 | 76.4404 | 41.1431
42810.4549 | 1282 | 17.3719 | 17.794 | 17.9498 | 17.9982 | 17.3614 | 16.0575 | 15.5702 | 16.5389 | 16.8959 | 17.0559 | 17.083 | 16.617 | 15.6697 | 14.5156 | 51.9409 | 67.0566 | 66.0682 | 89.232 | 84.4718 | 95.3548 |  |  |  | 63.1528 | 89.5262 | 626.9987 | 712.5719 | 724.9127 | 719.3233 | 124.7542 | 144.7824 | 984.0977 | 101.3202 | 149.5073 | 843.8675 | 744.1365 | 822.655 |  | 242.3215 | 991.9402 | 987.7109 | 564.2394 |  | 484.1708 | 742.8813 | 568.8643 | 749.909 | 915.8022 | 1021.3345 | 1051.7057 | 42.6078 | 414.6786 | 75.0701 | 633.5137 | 15.2525 | 50.4833 | 49.2808 | 52.5348 | 68.6443 |  |  | 1.9328 | -0.50852 | 0.6616 | -0.54146 | 7.1174 | 5.0876 | 10.2365 | -2.8566 | 20.5124 | 54.8183 | 45.1751 | -0.00015935 | -0.00015278 | -0.00072283 | 41.7915 | 17.3334 | 16.6739 | 17.0333 | 17.0558 | 16.0687 | 14.74 | 16.7137 | 17.039 | 17.3966 | 17.4741 | 17.2209 | 16.4143 | 14.7708 | 773.0618 | 543.0667 | 474.6968 | 290.2238 | 236.2099 | 776.9271 | 465.3157 | 37.5059 | 54.3329 | 59.1976 | 87.9204 | 89.8737 | 95.1256 |  |  |  | 647.27 | 608.6566 | 617.6091 | 633.376 | 84.7758 | 37.2565 | 950.4975 |  |  | 903.6547 |  |  | 27.8242 | 66.6914 | 663.5656 | 30.2792 | 68.9584 | 915.5559 | 765.8302 | 693.0305 | 940.5018 | 941.7561 | 770.2508 |  | 873.3915 | 921.7281 | 1137.2396 | 669.9845 | 747.0093 | 976.3344 |  | 443.1124 |  |  | 497.953 | 686.6487 | 767.1814 | [6 empty] | 684.9631 |  |  | 503.0337 |  |  | 534.0511 | 731.5214 | 732.7933 | 984.0619 | 1138.3033 | 1118.6195 | 574.3129 | 790.7497 | 906.8767 | 653.7924 | 760.4573 | 1016.7576 | 1177.8875 | 676.0745 | 899.6268 | 905.4398 | 1086.2887 | 1120.6819 | 583.3741 | 685.698 | 747.225 | 719.6683 | 866.6551 | 979.5601 | 1015.0807 | 1136.1261 | 635.6241 | 725.679 | 815.5607 | 982.8869 | 110.0114 | -0.00026554 | 17.7765 | 4.9314 | -40.3903 | 3.1206 | 9123.79 | 0.33 | 3.0522 | -1.5841 | 1.8068 | -1.6346 | 6.6892 | 5.6555 | 8.0221 | 100.8461 | 230.3433 | 63.5518 | 69.3689 | 15.8195 | 65.7205 | 41.0797
42810.4549 | 1283 | 17.3791 | 17.7973 | 17.9557 | 18.0009 | 17.364 | 16.0597 | 15.5708 | 16.5439 | 16.9013 | 17.0603 | 17.0802 | 16.6187 | 15.6744 | 14.5152 | 52.053 | 67.135 | 66.1606 | 89.2036 | 84.5194 | 95.3512 |  |  |  | 63.2674 | 89.5218 | 627.6131 | 712.6356 | 724.9143 | 719.8873 | 137.7474 | 163.2628 | 1002.241 | 119.7662 | 155.5633 | 816.7301 | 731.0324 | 804.5136 |  | 244.7709 | 983.7358 | 974.9487 | 591.7701 |  | 484.8954 | 743.6726 | 569.3959 | 750.2237 | 910.9497 | 1016.933 | 1049.148 | 42.9726 | 414.6606 | 73.71 | 632.9612 | 15.2474 | 50.4698 | 49.3038 | 52.5401 | 68.7277 |  |  | 1.4557 | 0.42656 | -0.38913 | -0.89433 | 8.132 | 7.1154 | 11.115 | -2.8856 | 20.6393 | 54.984 | 54.2182 | -0.00010842 | -9.692e-05 | -0.00075404 | 41.904 | 17.3409 | 16.6784 | 17.0406 | 17.059 | 16.0759 | 14.7395 | 16.7192 | 17.0483 | 17.3938 | 17.4754 | 17.2224 | 16.4239 | 14.7745 | 785.4069 | 545.9515 | 495.7731 | 300.2862 | 243.9289 | 776.4816 | 465.3597 | 37.629 | 54.4279 | 59.2762 | 87.9468 | 89.9064 | 95.1658 |  |  |  | 647.4712 | 610.2121 | 618.8229 | 636.4404 | 88.8963 | 34.0185 | 951.5617 |  |  | 904.6177 |  |  | 27.8706 | 66.7486 | 663.3054 | 30.3367 | 69.003 | 915.1932 | 764.0283 | 695.0933 | 933.8753 | 936.3837 | 766.1383 |  | 873.2476 | 915.4986 | 1137.3528 | 672.3288 | 747.633 | 967.9369 |  | 443.3469 |  |  | 497.6952 | 684.3279 | 763.316 | [6 empty] | 687.396 |  |  | 507.1916 |  |  | 534.331 | 730.9792 | 733.0028 | 976.0697 | 1138.0922 | 1117.7387 | 574.4974 | 789.8663 | 906.467 | 655.4148 | 759.3197 | 1018.2323 | 1178.9744 | 676.6203 | 899.2765 | 902.7446 | 1081.9431 | 1123.5238 | 583.7404 | 686.4486 | 748.4478 | 726.9508 | 883.6744 | 986.6034 | 1012.9615 | 1135.1196 | 635.7997 | 728.4508 | 829.6543 | 999.5228 | 101.2169 | -0.00046198 | 17.7797 | 4.9416 | -40.4891 | 3.1205 | 9140.81 | 0.35 | 2.6497 | 1.4514 | -1.3862 | -2.1015 | 7.138 | 6.6769 | 8.3451 | 100.9072 | 230.5916 | 63.6543 | 67.8308 | 13.4866 | 61.5229 | 41.0357
42810.4549 | 1284 | 17.3778 | 17.7972 | 17.9526 | 17.9969 | 17.3607 | 16.0543 | 15.574 | 16.5485 | 16.9069 | 17.0576 | 17.0789 | 16.6319 | 15.6708 | 14.5168 | 52.1743 | 67.2274 | 66.2637 | 89.1667 | 84.5696 | 95.3327 |  |  |  | 63.3791 | 89.5353 | 629.9278 | 714.7566 | 727.0469 | 722.2031 | 134.7126 | 180.0046 | 1017.754 | 130.9377 | 154.1262 | 826.3628 | 752.236 | 822.4959 |  | 246.8738 | 979.7911 | 959.7188 | 614.7025 |  | 485.3682 | 742.497 | 569.7347 | 748.8515 | 912.004 | 1018.0587 | 1049.9129 | 43.4616 | 414.7067 | 73.108 | 632.4786 | 15.2647 | 50.4499 | 49.3252 | 52.5605 | 68.8285 |  |  | 1.2251 | -0.39944 | -0.13023 | -1.1217 | 8.6564 | 5.9832 | 11.5211 | -2.8461 | 20.3079 | 55.3566 | 71.8615 | -0.00016756 | -0.00011171 | -0.00073761 | 42.0099 | 17.3527 | 16.6774 | 17.0386 | 17.0523 | 16.0784 | 14.7386 | 16.7174 | 17.0435 | 17.3929 | 17.4754 | 17.2274 | 16.4222 | 14.7633 | 788.3011 | 549.8106 | 507.5031 | 306.4138 | 254.6215 | 776.3087 | 465.3806 | 37.7416 | 54.521 | 59.3554 | 87.9637 | 89.936 | 95.1941 |  |  |  | 648.1018 | 614.0019 | 621.8794 | 643.0684 | 91.2414 | 37.8102 | 947.1656 |  |  | 892.0707 |  |  | 27.937 | 66.8166 | 665.2648 | 30.4074 | 69.0497 | 912.0576 | 764.5115 | 696.0547 | 920.9267 | 924.7493 | 765.203 |  | 873.3932 | 904.9926 | 1139.9385 | 673.102 | 747.9326 | 972.8252 |  | 443.6602 |  |  | 497.5035 | 686.4442 | 763.1913 | [6 empty] | 688.7425 |  |  | 510.7054 |  |  | 534.9375 | 730.0447 | 733.5733 | 964.056 | 1137.5597 | 1119.9774 | 574.2414 | 789.5251 | 907.5159 | 656.9025 | 758.2602 | 1015.5578 | 1174.0263 | 676.7724 | 898.4769 | 899.3606 | 1080.713 | 1121.9922 | 585.1575 | 687.4451 | 750.7655 | 734.5043 | 896.1989 | 993.024 | 1008.4947 | 1133.0333 | 636.1057 | 730.353 | 836.6487 | 1011.8162 | 99.089 | -0.0011074 | 17.782 | 4.9495 | -40.4957 | 3.1206 | 9131.39 | 0.29 | 2.4335 | -1.4037 | -0.80148 | -2.3522 | 7.3677 | 6.1254 | 8.4999 | 100.987 | 232.6054 | 63.7135 | 67.4447 | 12.1875 | 66.5009 | 40.9808
42810.4549 | 1285 | 17.3816 | 17.7998 | 17.9603 | 18.0027 | 17.3663 | 16.0661 | 15.5791 | 16.5485 | 16.9089 | 17.0605 | 17.0856 | 16.6233 | 15.6656 | 14.5253 | 52.2982 | 67.3222 | 66.3657 | 89.1253 | 84.5814 | 95.3354 |  |  |  | 63.5005 | 89.5453 | 633.0735 | 716.6355 | 729.3431 | 724.1812 | 126.8809 | 163.6021 | 1008.2627 | 136.1952 | 176.1953 | 815.1698 | 709.3427 | 830.2008 |  | 261.6557 | 977.3613 | 962.1733 | 603.0442 |  | 484.3165 | 740.5272 | 567.1756 | 744.7709 | 905.7833 | 1017.4851 | 1051.371 | 45.1097 | 414.9117 | 73.2062 | 632.1469 | 15.2498 | 50.4045 | 49.3323 | 52.5842 | 68.7266 |  |  | 1.3696 | -1.0342 | -0.14666 | -1.0389 | 7.6858 | 5.4273 | 10.8397 | -1.5076 | 20.5747 | 55.4277 | 67.2092 | -0.00019056 | -9.692e-05 | -0.00074254 | 42.1197 | 17.3665 | 16.6721 | 17.0387 | 17.0554 | 16.0734 | 14.7419 | 16.714 | 17.0442 | 17.39 | 17.4759 | 17.2235 | 16.4145 | 14.7664 | 783.252 | 549.1956 | 498.8215 | 314.6923 | 260.1859 | 776.4501 | 465.5922 | 37.8692 | 54.6124 | 59.4394 | 88.0016 | 89.9582 | 95.2357 |  |  |  | 648.8426 | 616.9244 | 624.011 | 645.8812 | 73.7957 | 30.8511 | 937.1506 |  |  | 879.4874 |  |  | 27.9931 | 66.8638 | 667.862 | 30.4854 | 69.1001 | 907.8014 | 765.6432 | 697.1723 | 913.9899 | 917.367 | 765.8778 |  | 873.427 | 907.6025 | 1140.3444 | 672.9246 | 748.2273 | 976.1539 |  | 443.7504 |  |  | 497.0777 | 689.5374 | 763.9121 | [6 empty] | 689.5866 |  |  | 512.0684 |  |  | 535.202 | 729.1155 | 735.1817 | 957.9856 | 1136.225 | 1119.8287 | 573.8001 | 789.7129 | 908.4074 | 657.9705 | 758.1056 | 1012.5954 | 1171.1047 | 676.6062 | 899.6645 | 896.9871 | 1079.6717 | 1116.9535 | 586.0645 | 687.931 | 752.5357 | 731.2823 | 898.8377 | 997.5195 | 1003.0967 | 1131.7274 | 635.6258 | 730.7993 | 832.3423 | 1011.8361 | 113.6552 | -0.00084782 | 17.7838 | 4.9544 | -40.4331 | 3.1205 | 9122.79 | 0.3 | 2.5757 | -2.2564 | -0.8497 | -2.2615 | 6.9409 | 5.8326 | 8.2428 | 100.9807 | 232.8041 | 63.7978 | 68.0585 | 13.1949 | 55.7851 | 41.0548
42810.4549 | 1286 | 17.3871 | 17.7992 | 17.9591 | 17.994 | 17.3661 | 16.0642 | 15.5892 | 16.5419 | 16.9008 | 17.0553 | 17.0908 | 16.6306 | 15.6612 | 14.5212 | 52.4181 | 67.4207 | 66.4622 | 89.0432 | 84.6035 | 95.3317 |  |  |  | 63.6036 | 89.5403 | 636.5215 | 718.8008 | 731.5966 | 726.3273 | 128.5359 | 178.9376 | 1013.3034 | 128.3337 | 162.211 | 831.0643 | 698.6669 | 830.8898 |  | 255.517 | 984.5638 | 957.6078 | 594.5955 |  | 483.7436 | 739.7897 | 564.3732 | 740.712 | 899.6608 | 1012.7795 | 1049.4061 | 45.6021 | 414.8784 | 74.997 | 631.9625 | 15.2129 | 50.3392 | 49.3185 | 52.6132 | 68.3713 |  |  | 1.1318 | -0.72143 | 0.37312 | -1.4121 | 8.339 | 6.4018 | 11.3555 | -2.626 | 20.8323 | 55.7657 | 53.936 | -0.00012649 | -0.00017249 | -0.00073761 | 42.2376 | 17.3734 | 16.6719 | 17.0425 | 17.0561 | 16.0749 | 14.7503 | 16.7141 | 17.0423 | 17.3949 | 17.4629 | 17.2249 | 16.4212 | 14.7728 | 765.7221 | 536.1772 | 472.1187 | 311.9648 | 259.2695 | 774.8909 | 465.2399 | 37.9836 | 54.6937 | 59.5158 | 88.0185 | 89.9793 | 95.2742 |  |  |  | 649.3346 | 618.0338 | 624.2961 | 646.3106 | 69.5743 | 26.3177 | 930.8873 |  |  | 882.4267 |  |  | 28.0436 | 66.9312 | 671.6752 | 30.5628 | 69.1503 | 903.7789 | 769.0246 | 697.1582 | 918.2143 | 923.0338 | 769.038 |  | 873.7166 | 918.0786 | 1140.0034 | 672.3752 | 748.5193 | 984.7926 |  | 443.5196 |  |  | 497.7354 | 696.132 | 766.1554 | [6 empty] | 689.185 |  |  | 512.2254 |  |  | 535.3393 | 727.8438 | 736.1192 | 959.876 | 1132.4928 | 1116.5198 | 574.4055 | 791.0186 | 908.3459 | 656.8835 | 757.8178 | 1013.5022 | 1170.6846 | 678.2955 | 901.7223 | 900.0855 | 1077.414 | 1114.9884 | 586.2945 | 687.2015 | 753.9069 | 725.7697 | 892.4666 | 995.4618 | 1000.92 | 1129.0138 | 634.8047 | 730.3391 | 824.8954 | 1000.825 | 146.5561 | -0.0012617 | 17.7844 | 4.9608 | -40.3737 | 3.1205 | 9093.82 | 0.41 | 2.3439 | -1.8839 | 1.3548 | -2.6357 | 7.2166 | 6.3231 | 8.4213 | 101 | 232.2852 | 63.8918 | 69.425 | 16.0906 | 53.4641 | 41.1441
42810.4549 | 1287 | 17.3812 | 17.8002 | 17.9517 | 17.9905 | 17.3576 | 16.0558 | 15.594 | 16.5463 | 16.8997 | 17.0571 | 17.0837 | 16.6258 | 15.6599 | 14.5189 | 52.5336 | 67.5147 | 66.5571 | 88.9951 | 84.6845 | 95.3334 |  |  |  | 63.711 | 89.543 | 636.4783 | 718.3011 | 730.5372 | 725.8223 | 122.5122 | 164.3408 | 999.563 | 136.1251 | 170.9277 | 811.189 | 741.5305 | 814.0856 |  | 245.9409 | 987.9303 | 969.0037 | 585.6923 |  | 482.6674 | 738.7736 | 563.5454 | 739.7372 | 896.1133 | 1011.8526 | 1047.3611 | 45.2658 | 414.6859 | 76.437 | 631.9671 | 15.225 | 50.287 | 49.3131 | 52.6386 | 67.8665 |  |  | 1.2185 | -0.55321 | 0.59457 | -0.78525 | 9.3023 | 6.8993 | 11.5599 | -1.7514 | 21.5446 | 58.3733 | 49.0257 | -0.00012814 | -0.00011171 | -0.0007754 | 42.3566 | 17.3804 | 16.6748 | 17.0396 | 17.0595 | 16.0725 | 14.7495 | 16.7175 | 17.0376 | 17.3916 | 17.4726 | 17.2257 | 16.4162 | 14.7655 | 741.6836 | 533.4883 | 454.9182 | 305.2663 | 247.4424 | 773.3588 | 464.5879 | 38.1172 | 54.8053 | 59.6019 | 88.0727 | 90.0154 | 95.318 |  |  |  | 650.0968 | 619.6948 | 624.91 | 648.8196 | 105.4454 | 40.2532 | 933.8986 |  |  | 899.8499 |  |  | 28.1074 | 66.9921 | 671.557 | 30.636 | 69.2046 | 900.1088 | 776.4847 | 695.7634 | 923.194 | 929.3348 | 778.3337 |  | 875.5476 | 923.4073 | 1139.4796 | 670.8852 | 748.678 | 996.3945 |  | 443.6411 |  |  | 501.265 | 710.4692 | 771.9967 | [6 empty] | 687.467 |  |  | 510.925 |  |  | 535.1184 | 725.77 | 736.7554 | 953.2039 | 1131.3131 | 1113.0705 | 575.4345 | 794.6202 | 909.0186 | 655.4523 | 756.9625 | 1015.9503 | 1170.4077 | 680.6972 | 905.8658 | 904.9234 | 1075.8409 | 1113.2805 | 585.4482 | 686.4168 | 755.0648 | 723.3163 | 886.058 | 991.3912 | 1002.9372 | 1127.2422 | 634.4256 | 730.3731 | 822.6059 | 992.4478 | 121.4482 | 0.00548 | 17.7842 | 4.9664 | -40.3856 | 3.1206 | 9050.74 | 0.33 | 2.4314 | -1.6489 | 1.7094 | -1.9645 | 7.6193 | 6.5618 | 8.4937 | 101.4206 | 231.7877 | 63.976 | 71.5266 | 17.8699 | 64.4324 | 41.2314
42810.4549 | 1288 | 17.385 | 17.8001 | 17.9543 | 17.9983 | 17.3659 | 16.0587 | 15.5996 | 16.5515 | 16.9051 | 17.0607 | 17.0856 | 16.6323 | 15.6688 | 14.5204 | 52.6508 | 67.606 | 66.6458 | 88.9812 | 84.7243 | 95.3456 |  |  |  | 63.8294 | 89.5468 | 635.0937 | 716.4949 | 728.2049 | 723.8979 | 119.0276 | 160.2979 | 988.6113 | 121.015 | 164.4905 | 806.2391 | 751.7485 | 818.5763 |  | 258.0064 | 984.8195 | 975.4729 | 563.5445 |  | 482.5782 | 738.9749 | 564.9643 | 740.9991 | 901.8068 | 1017.9775 | 1052.9209 | 46.3563 | 414.7087 | 76.3974 | 631.9952 | 15.2353 | 50.2323 | 49.2875 | 52.6446 | 67.2571 |  |  | 1.3486 | -0.57752 | 0.070848 | -1.0159 | 8.5269 | 5.6343 | 11.3089 | -2.4919 | 22.3695 | 58.6719 | 51.7616 | -0.00015442 | -0.00013306 | -0.0007179 | 42.4595 | 17.3959 | 16.6781 | 17.037 | 17.0483 | 16.0759 | 14.7457 | 16.7202 | 17.0393 | 17.3844 | 17.4735 | 17.2194 | 16.4092 | 14.7664 | 770.2796 | 547.8302 | 517.0365 | 313.8575 | 254.5071 | 775.2256 | 465.6665 | 38.24 | 54.8978 | 59.6815 | 88.1141 | 90.0281 | 95.3489 |  |  |  | 650.7755 | 620.6167 | 625.4173 | 649.5921 | 129.9665 | 41.3818 | 937.6692 |  |  | 903.1886 |  |  | 28.1587 | 67.0588 | 669.493 | 30.6931 | 69.2568 | 898.7058 | 781.5346 | 694.375 | 928.5427 | 929.7597 | 789.2037 |  | 877.9401 | 932.6263 | 1139.3991 | 669.5475 | 748.8086 | 1005.7171 |  | 443.7794 |  |  | 504.7937 | 721.6113 | 779.2265 | [6 empty] | 685.7984 |  |  | 509.262 |  |  | 535.2771 | 723.2163 | 736.2165 | 962.4692 | 1134.5738 | 1109.3571 | 576.4912 | 797.6147 | 910.0304 | 653.842 | 756.0226 | 1016.37 | 1170.1017 | 682.0495 | 908.3782 | 904.9547 | 1076.1077 | 1112.1705 | 584.8546 | 685.9205 | 755.5887 | 725.5423 | 886.3502 | 989.4357 | 1004.0379 | 1128.2029 | 634.4869 | 731.0673 | 830.5142 | 993.739 | 133.8649 | 0.00019745 | 17.7873 | 4.9848 | -40.4577 | 3.1206 | 9032.97 | 0.33 | 2.5555 | -1.6849 | 0.59013 | -2.2347 | 7.3122 | 5.9439 | 8.4209 | 102.0101 | 231.4778 | 64.0484 | 69.0433 | 11.1861 | 67.7893 | 41.3501
42810.455 | 1289 | 17.379 | 17.7987 | 17.9523 | 17.9988 | 17.3675 | 16.0575 | 15.6086 | 16.551 | 16.9083 | 17.0618 | 17.0873 | 16.6236 | 15.6669 | 14.5261 | 52.7711 | 67.6984 | 66.7457 | 88.9844 | 84.7317 | 95.3796 |  |  |  | 63.943 | 89.5416 | 635.2271 | 716.037 | 727.6731 | 723.3555 | 127.1622 | 157.4604 | 972.6233 | 111.1168 | 157.0928 | 830.5023 | 745.7926 | 831.1495 |  | 260.6267 | 979.95 | 962.7604 | 586.0441 |  | 483.2342 | 740.2645 | 566.5699 | 744.3848 | 911.6251 | 1025.2428 | 1057.6438 | 49.2193 | 415.1458 | 75.7135 | 632.0344 | 15.239 | 50.1856 | 49.2721 | 52.6523 | 66.6688 |  |  | 1.7797 | -0.13659 | -0.77618 | -1.0402 | 7.4177 | 5.6777 | 10.7543 | -1.9603 | 21.8651 | 56.5267 | 57.5915 | -6.242e-05 | -0.00014949 | -0.00073761 | 42.5855 | 17.4038 | 16.6751 | 17.0317 | 17.0463 | 16.081 | 14.7469 | 16.7139 | 17.0445 | 17.383 | 17.4764 | 17.2252 | 16.4174 | 14.7602 | 821.1317 | 570.4604 | 541.0873 | 318.7438 | 254.1427 | 780.1739 | 467.3682 | 38.3496 | 54.986 | 59.755 | 88.1352 | 90.0311 | 95.3715 |  |  |  | 651.3891 | 621.5668 | 625.9126 | 649.7013 | 122.1 | 46.1514 | 939.0308 |  |  | 904.7197 |  |  | 28.2178 | 67.1252 | 668.5667 | 30.767 | 69.3127 | 900.6608 | 782.553 | 692.9648 | 935.6769 | 931.2322 | 793.2879 |  | 879.1331 | 948.2399 | 1138.8715 | 668.3289 | 749.0919 | 1011.1004 |  | 444.1303 |  |  | 506.3307 | 721.4407 | 782.9131 | [6 empty] | 684.1035 |  |  | 507.3612 |  |  | 535.4509 | 721.2363 | 735.7653 | 981.2641 | 1142.7098 | 1110.2368 | 577.4953 | 798.4609 | 911.0023 | 652.7436 | 755.9695 | 1018.367 | 1168.9484 | 682.8085 | 909.6132 | 906.8004 | 1078.9822 | 1114.2815 | 584.1673 | 685.5063 | 755.6829 | 728.3807 | 896.7246 | 993.8638 | 1006.0295 | 1131.6712 | 634.2027 | 730.948 | 840.8744 | 1007.9487 | 122.4878 | -0.00025152 | 17.7903 | 4.9923 | -40.3383 | 3.1205 | 8983.52 | 0.32 | 2.9348 | -0.81993 | -1.9545 | -2.2627 | 6.8392 | 5.9835 | 8.2349 | 102.3431 | 230.6924 | 64.1587 | 65.2452 | 8.8591 | 65.5572 | 41.4739
42810.455 | 1290 | 17.3759 | 17.7945 | 17.955 | 18.0005 | 17.3585 | 16.0571 | 15.6052 | 16.551 | 16.9001 | 17.0548 | 17.0827 | 16.6196 | 15.6627 | 14.5239 | 52.8793 | 67.7866 | 66.8478 | 89.0167 | 84.7192 | 95.3838 |  |  |  | 64.0534 | 89.5386 | 637.7275 | 717.8229 | 729.779 | 725.0816 | 139.1075 | 164.0929 | 982.7055 | 107.8271 | 141.5289 | 836.5248 | 764.7842 | 848.0201 |  | 255.2991 | 986.0807 | 967.6956 | 577.8142 |  | 483.0595 | 737.9205 | 565.4512 | 741.2347 | 910.21 | 1021.0079 | 1057.8158 | 51.5036 | 415.306 | 77.0343 | 632.24 | 15.2204 | 50.1208 | 49.2653 | 52.6565 | 66.0432 |  |  | 1.7987 | -0.45004 | -0.02312 | -0.90879 | 8.3114 | 5.0823 | 11.1347 | -1.8204 | 21.1702 | 55.9482 | 78.6843 | -0.00014128 | -0.00018728 | -0.00074911 | 42.6977 | 17.4071 | 16.6783 | 17.0395 | 17.0528 | 16.073 | 14.7498 | 16.726 | 17.0451 | 17.3846 | 17.4735 | 17.226 | 16.4215 | 14.7638 | 850.2943 | 607.2547 | 559.3053 | 320.6417 | 257.9666 | 784.9465 | 468.8675 | 38.4732 | 55.0705 | 59.8308 | 88.1635 | 90.0539 | 95.3992 |  |  |  | 651.851 | 621.4917 | 625.5428 | 648.4126 | 102.8935 | 42.7905 | 941.8301 |  |  | 914.7035 |  |  | 28.2761 | 67.1876 | 670.33 | 30.8501 | 69.3584 | 899.7807 | 780.0851 | 690.4155 | 949.2481 | 938.8421 | 792.8274 |  | 880.0663 | 965.4297 | 1137.6415 | 666.6501 | 749.4023 | 1010.8798 |  | 444.2813 |  |  | 507.8128 | 715.7892 | 782.1261 | [6 empty] | 681.8438 |  |  | 504.8614 |  |  | 535.6869 | 719.9099 | 735.8536 | 986.277 | 1150.0896 | 1110.2926 | 578.6161 | 798.8385 | 912.0818 | 652.0413 | 756.744 | 1020.5122 | 1162.3291 | 683.3438 | 910.957 | 912.343 | 1081.6863 | 1116.45 | 583.2308 | 685.2586 | 756.5144 | 729.1524 | 903.3783 | 1000.7044 | 1008.6355 | 1134.5826 | 633.8239 | 730.2485 | 843.8551 | 1014.4275 | 120.0291 | -0.00092497 | 17.7924 | 4.9945 | -40.4201 | 3.1205 | 8928.5 | 0.3 | 2.953 | -1.4866 | -0.33694 | -2.1125 | 7.2276 | 5.6519 | 8.3657 | 102.706 | 229.3964 | 64.2892 | 63.8088 | 7.1399 | 70.9991 | 41.6054
42810.455 | 1291 | 17.3753 | 17.7977 | 17.9584 | 17.9964 | 17.3614 | 16.0566 | 15.6073 | 16.5603 | 16.9001 | 17.0541 | 17.0817 | 16.6232 | 15.6602 | 14.5207 | 52.9873 | 67.8753 | 66.9483 | 89.0521 | 84.7342 | 95.3683 |  |  |  | 64.1616 | 89.5363 | 640.7169 | 719.8751 | 731.8445 | 726.8445 | 122.6542 | 186.6437 | 1015.6507 | 134.4428 | 155.4203 | 833.0045 | 775.0345 | 850.6759 |  | 260.3907 | 977.3464 | 956.6249 | 592.8469 |  | 483.3767 | 734.6037 | 564.5757 | 738.3773 | 900.5922 | 1015.693 | 1055.5825 | 50.8478 | 415.3099 | 79.775 | 632.6326 | 15.1819 | 50.0534 | 49.2771 | 52.6623 | 65.4612 |  |  | 1.5122 | -1.2031 | -0.8984 | -0.95676 | 9.4797 | 6.8769 | 11.257 | -2.3868 | 20.4515 | 53.5853 | 80.2127 | -0.00011664 | -0.00010842 | -0.00074911 | 42.809 | 17.426 | 16.6883 | 17.0436 | 17.0556 | 16.0784 | 14.7502 | 16.7322 | 17.0516 | 17.3971 | 17.4835 | 17.2304 | 16.427 | 14.7672 | 854.7391 | 611.5476 | 566.9236 | 327.6151 | 266.2086 | 788.637 | 470.4385 | 38.6005 | 55.1702 | 59.9025 | 88.1656 | 90.0703 | 95.4398 |  |  |  | 652.3227 | 621.0757 | 624.6581 | 648.7486 | 107.4773 | 42.7404 | 946.9661 |  |  | 919.8574 |  |  | 28.3294 | 67.2455 | 673.7022 | 30.9094 | 69.4118 | 897.8204 | 777.1554 | 687.9692 | 945.685 | 937.2584 | 788.6795 |  | 880.8551 | 971.0779 | 1136.566 | 664.0612 | 749.832 | 1013.0993 |  | 444.1784 |  |  | 508.6324 | 710.7078 | 780.1506 | [6 empty] | 679.2267 |  |  | 501.9163 |  |  | 535.8865 | 719.1993 | 736.4557 | 978.2896 | 1151.5676 | 1107.0376 | 579.3664 | 798.7268 | 911.9003 | 651.3906 | 757.6272 | 1016.3935 | 1163.0455 | 683.0048 | 911.5052 | 913.9952 | 1080.9665 | 1116.3462 | 583.3261 | 685.8182 | 757.797 | 726.281 | 900.2285 | 1004.2286 | 1007.4397 | 1133.7955 | 634.2774 | 730.668 | 839.0671 | 1009.3396 | 123.8776 | 0.001355 | 17.7962 | 5.0062 | -40.3644 | 3.1206 | 8894.94 | 0.39 | 2.71 | -2.4266 | -2.0969 | -2.1639 | 7.7031 | 6.5609 | 8.3942 | 103.1178 | 228.5255 | 64.4773 | 64.7217 | 6.614 | 73.5045 | 41.6939
42810.455 | 1292 | 17.3825 | 17.7976 | 17.9473 | 17.9898 | 17.369 | 16.0554 | 15.6086 | 16.557 | 16.9009 | 17.055 | 17.0903 | 16.6298 | 15.6647 | 14.5242 | 53.1084 | 67.9755 | 67.0589 | 89.0794 | 84.7933 | 95.3812 |  |  |  | 64.284 | 89.5451 | 641.3739 | 719.8106 | 731.0517 | 726.6152 | 129.5357 | 166.244 | 1011.9468 | 155.6185 | 187.152 | 798.7159 | 707.3942 | 852.3681 |  | 269.0547 | 974.3014 | 955.9475 | 595.1405 |  | 483.3173 | 731.6998 | 564.7208 | 738.8819 | 901.1947 | 1016.915 | 1056.7614 | 47.8867 | 415.4337 | 83.8733 | 633.0482 | 15.1755 | 50.0402 | 49.2999 | 52.6672 | 64.932 |  |  | 1.1291 | -1.9824 | -0.47127 | -1.8274 | 8.542 | 6.2356 | 10.9369 | -1.2553 | 19.6311 | 52.6987 | 81.2161 | -0.00014128 | -0.00013306 | -0.00076882 | 42.9236 | 17.4357 | 16.6792 | 17.0382 | 17.0562 | 16.0728 | 14.7455 | 16.7246 | 17.0414 | 17.3957 | 17.4785 | 17.2208 | 16.42 | 14.759 | 832.8928 | 593.0664 | 545.9929 | 325.9917 | 262.1893 | 790.2779 | 471.7706 | 38.7382 | 55.2801 | 59.9998 | 88.2198 | 90.0979 | 95.4795 |  |  |  | 652.7802 | 620.9399 | 623.9594 | 648.2555 | 68.4256 | 29.0336 | 945.4916 |  |  | 917.711 |  |  | 28.3927 | 67.3041 | 674.2628 | 30.985 | 69.4615 | 893.2401 | 771.6816 | 685.9446 | 945.8531 | 938.4535 | 783.1232 |  | 880.6475 | 968.1822 | 1136.1732 | 661.9101 | 750.1233 | 1005.1202 |  | 444.1459 |  |  | 508.7132 | 704.1952 | 774.5244 | [6 empty] | 676.9592 |  |  | 500.6478 |  |  | 535.4404 | 719.5339 | 737.0301 | 969.6755 | 1145.0588 | 1107.001 | 586.5249 | 798.097 | 910.5872 | 651.3569 | 758.1572 | 1014.6675 | 1168.1621 | 694.884 | 909.7648 | 913.7546 | 1077.4044 | 1113.3646 | 583.7028 | 687.3866 | 758.9601 | 720.0933 | 892.324 | 1002.4092 | 1005.8914 | 1130.4381 | 635.2353 | 733.2132 | 829.0705 | 997.3697 | 154.8406 | -0.00052511 | 17.8012 | 5.035 | -40.3943 | 3.1206 | 8898.61 | 0.32 | 2.3415 | -3.1104 | -1.5165 | -2.9863 | 7.3156 | 6.2504 | 8.2779 | 103.1941 | 228.3455 | 64.6159 | 67.7779 | 9.2122 | 55.5327 | 41.8027