## Info
Date: | 2017-04-13
Time: | 9:49
Program Version: | MIDAS.exe Ver. 2.124.0.680
File Name: | CLT_Room_Test_1-5
Test Series information: | Furnished room witth 3 layers of type X gypsum on 3 walls and ceiling. Wall 1 is exposed CLT. The compartment had a rough opening in Wall W2 (front) of 1.8 m wide x 2.0 m high.
Hardware Configuration: | NRCC_TallWoodBuildings_PhaseII_20170412.xlsx

## Channels
Index | Legend/ID | Range/Type | Scaled Units | Notes
0 | TC_Ceiling_Center_020 | Thermocouple | °C | At the centre of the ceiling in panel 20 mm from interface
1 | TC_Ceiling_Center_035 | Thermocouple | °C | At the centre of the ceiling in panel 35 mm from interface
2 | TC_Ceiling_Center_050 | Thermocouple | °C | At the centre of the ceiling in panel 50 mm from interface
3 | TC_Ceiling_Center_065 | Thermocouple | °C | At the centre of the ceiling in panel 65 mm from interface
4 | TC_Ceiling_Center_090 | Thermocouple | °C | At the centre of the ceiling in panel 90 mm from interface
5 | TC_Ceiling_Center_115 | Thermocouple | °C | At the centre of the ceiling in panel 115 mm from interface
6 | TC_Ceiling_Center_070 | Thermocouple | °C | At the centre of the ceiling in panel 70 mm from interface
7 | TC_W3_Middle_180_020 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 20 mm from interface
8 | TC_W3_Middle_180_035 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 35 mm from interface
9 | TC_W3_Middle_180_050 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 50 mm from interface
10 | TC_W3_Middle_180_065 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 65 mm from interface
11 | TC_W3_Middle_180_090 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 90 mm from interface
12 | TC_W3_Middle_180_115 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 115 mm from interface
13 | TC_W3_Middle_180_070 | Thermocouple | °C | W3 at the mid length at h=1.8 m in panel 70 mm from interface
14 | TC_W3_Middle_060_CLT | Thermocouple | °C | W3 on the surface of CLT
15 | TC_W3_Middle_120_CLT | Thermocouple | °C | W3 on the surface of CLT
16 | TC_W3_Middle_180_CLT | Thermocouple | °C | W3 on the surface of CLT
17 | TC_W3_Middle_060_1GB | Thermocouple | °C | W3 on the surface of 1st GB
18 | TC_W3_Middle_120_1GB | Thermocouple | °C | W3 on the surface of 1st GB
19 | TC_W3_Middle_180_1GB | Thermocouple | °C | W3 on the surface of 1st GB
20 | TC_W3_Middle_060_2GB | Thermocouple | °C | W3 on the surface of 2nd GB
21 | TC_W3_Middle_120_2GB | Thermocouple | °C | W3 on the surface of 2nd GB
22 | TC_W3_Middle_180_2GB | Thermocouple | °C | W3 on the surface of 2nd GB
23 | TC_Ceiling_Tr4_CLT | Thermocouple | °C | Ceiling above Tr4 on the surface of CLT
24 | TC_Ceiling_Tr4_1GB | Thermocouple | °C | Ceiling above Tr4 on the surface of 1st GB
25 | TC_Ceiling_Tr4_2GB | Thermocouple | °C | Ceiling above Tr4 on the surface of 2nd GB
26 | STE_6 | Thermocouple | °C | 12" below ceiling (see "Drawings")
27 | STE_10 | Thermocouple | °C | 12" below ceiling (see "Drawings")
28 | TC_V_c | Thermocouple | °C | Temperature co-located with V_c
29 | TC_Ceiling_Tr3_CLT | Thermocouple | °C | Ceiling above Tr3 on the surface of CLT
30 | TC_Ceiling_Tr3_1GB | Thermocouple | °C | Ceiling above Tr3 on the surface of 1st GB
31 | TC_Ceiling_Tr3_2GB | Thermocouple | °C | Ceiling above Tr3 on the surface of 2nd GB
32 | TC_Ceiling_Center_CLT | Thermocouple | °C | Ceiling at the centre on the surface of CLT
33 | TC_Ceiling_Center_1GB | Thermocouple | °C | Ceiling at the centre on the surface of 1st GB
34 | TC_Ceiling_Center_2GB | Thermocouple | °C | Ceiling at the centre on the surface of 2nd GB
35 | PT_W3_Middle_180_SPx | Thermocouple | °C | Plate thermometer on W3 at the mid length at h=1.8 m
36 | PT_Ceiling_Center_SPy | Thermocouple | °C | Temperature for plate thermometer at the centre of the ceiling
37 | DFT_Ceiling_Center_Px | Thermocouple | °C | DFT at the centre of the ceiling (Back plate)
38 | PT_Ceiling_Center_SPx | Thermocouple | °C | Plate thermometer at the centre of the ceiling
39 | STE_5 | Thermocouple | °C | 12" below ceiling (see "Drawings")
40 | STE_9 | Thermocouple | °C | 12" below ceiling (see "Drawings")
41 | PT_W3_Middle_180_SPy | Thermocouple | °C | Temperature for plate thermometer on W3 at the mid length at h=1.8 m
42 | DFT_Ceiling_Center_Py | Thermocouple | °C | DFT at the centre of the ceiling (Front plate)
43 | Door_TC_1 | Thermocouple | °C | At the centreline of the opening
44 | Door_TC_2 | Thermocouple | °C | At the centreline of the opening
45 | Door_TC_3 | Thermocouple | °C | At the centreline of the opening
46 | Door_TC_4 | Thermocouple | °C | At the centreline of the opening
47 | Door_TC_5 | Thermocouple | °C | At the centreline of the opening
48 | Door_TC_6 | Thermocouple | °C | At the centreline of the opening
49 | Door_TC_7 | Thermocouple | °C | At the centreline of the opening
50 | PT_Front_a480_SPy | Thermocouple | °C | Facing the centre of the opening (offset 150 from centerline)
51 | PT_Front_a480_SPx | Thermocouple | °C | Facing the centre of the opening (offset 150 from centerline)
52 | PT_Front_a240_SPy | Thermocouple | °C | Facing the centre of the opening (offset 150 from centerline)
53 | PT_Front_a240_SPx | Thermocouple | °C | Facing the centre of the opening (offset 150 from centerline)
54 | TC_Smoke | Thermocouple | °C | Gas temperature at SMOKE2 outflow (for shutoff)
55 | TC_HFGtower | Thermocouple | °C | H2O outflow temperatures of heat flux gages on roof tower
56 | TC_HFGfloor | Thermocouple | °C | H2O outflow temperatures of heat flux gages on floor
57 | TC_HFGw1 | Thermocouple | °C | H2O outflow temperatures of heat flux gages on W1
58 | TC_GoPro | Thermocouple | °C | H2O outflow temperatures of GoPro water bath
59 | TC_TreeSteel | Thermocouple | °C | Temperature of steel behind thermal insulation in Tree 03 at 2.1 m height
60 | TC_TBD | Thermocouple | °C | Extra TC location TBD
61 | dP_c | ±10V default | Pa | 5/8" diameter bidirectional probe on ceiling near STE 6, Direction normal to the opening
62 | dP_o1 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (low, long side)
63 | dP_o2 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (low, middle)
64 | dP_o3 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (low, short side)
65 | dP_o4 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (high, long side)
66 | dP_o5 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (high, middle)
67 | dP_o6 | ±10V default | Pa | 5/8" diameter bidirectional probe at the opening (high, short side)
68 | dP_r | ±10V default | Pa | On smoke sample line near gas analyzer sample line at 2.1m 1/4" SS tube
69 | Gardon_Front_a480 | ±0.2V default | kW/m2 | facing the centre of the opening
70 | Gardon_Front_a240 | ±0.2V default | kW/m2 | facing the centre of the opening
71 | Gardon_Floor_Center | ±0.2V default | kW/m2 | At the center of the floor
72 | SmokeAlarm | ±10V default | V | Smoke detector at the centre of the ceiling
73 | HeatAlarm | ±10V default | V | Heat detector at the centre of the ceiling
74 | SMOKE | ±10V default | V | at the centre of the room, 1.6 m high
75 | TC_W1_Middle_180_020 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 20 mm from interface
76 | TC_W1_Middle_180_035 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 35 mm from interface
77 | TC_W1_Middle_180_050 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 50 mm from interface
78 | TC_W1_Middle_180_065 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 65 mm from interface
79 | TC_W1_Middle_180_090 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 90 mm from interface
80 | TC_W1_Middle_180_115 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 115 mm from interface
81 | TC_W1_Middle_180_140 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 140 mm from interface
82 | TC_W4_Middle_180_020 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 20 mm from interface
83 | TC_W4_Middle_180_035 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 35 mm from interface
84 | TC_W4_Middle_180_050 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 50 mm from interface
85 | TC_W4_Middle_180_065 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 65 mm from interface
86 | TC_W4_Middle_180_090 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 90 mm from interface
87 | TC_W4_Middle_180_115 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 115 mm from interface
88 | TC_W4_Middle_180_070 | Thermocouple | °C | W4 at the mid length at h=1.8 m in panel 70 mm from interface
89 | Roof_TC_350 | Thermocouple | °C | 3.5 m above ground
90 | Roof_TC_450 | Thermocouple | °C | 4.5 m above ground
91 | Roof_TC_550 | Thermocouple | °C | 5.5 m above ground
92 | Roof_TC_650 | Thermocouple | °C | 6.5 m above ground
93 | Roof_TC_750 | Thermocouple | °C | 7.5 m above ground
94 | PT_Front_e350_SPx | Thermocouple | °C | 3.5 m above ground
95 | PT_Front_e550_SPx | Thermocouple | °C | 5.5 m above the top of the opening
96 | TC_W4_Middle_060_CLT | Thermocouple | °C | W4 on the surface of CLT
97 | TC_W4_Middle_120_CLT | Thermocouple | °C | W4 on the surface of CLT
98 | TC_W4_Middle_180_CLT | Thermocouple | °C | W4 on the surface of CLT
99 | TC_W4_Middle_060_1GB | Thermocouple | °C | W4 on the surface of 1st GB
100 | TC_W4_Middle_120_1GB | Thermocouple | °C | W4 on the surface of 1st GB
101 | TC_W4_Middle_180_1GB | Thermocouple | °C | W4 on the surface of 1st GB
102 | TC_W4_Middle_060_2GB | Thermocouple | °C | W4 on the surface of 2nd GB
103 | TC_W4_Middle_120_2GB | Thermocouple | °C | W4 on the surface of 2nd GB
104 | TC_W4_Middle_180_2GB | Thermocouple | °C | W4 on the surface of 2nd GB
105 | PT_W4_Middle_180_SPx | Thermocouple | °C | Plate thermometer on W4 at the mid length at h=1.8 m
106 | STE_7 | Thermocouple | °C | 12" below ceiling (see "Drawings")
107 | STE_8 | Thermocouple | °C | 18" below ceiling (see "Drawings")
108 | PT_W4_Middle_180_SPy | Thermocouple | °C | Temperature for plate thermometer on W4 at the mid length at h=1.8 m
109 | Gardon_Front_e350 | ±0.2V default | kW/m2 | 3.5 m above ground
110 | Gardon_Front_e550 | ±0.2V default | kW/m2 | 5.5 m above ground
111 | TC_W1_Front_180_CLT | Thermocouple | °C | W1 at the front at h=1.8 m on the surface of CLT
112 | TC_W1_Front_180_035 | Thermocouple | °C | W1 at the front at h=1.8 m in panel 35 mm from interface
113 | TC_W1_Front_180_070 | Thermocouple | °C | W1 at the front at h=1.8 m in panel 70 mm from interface
114 | TC_W1_Front_060_CLT | Thermocouple | °C | W1 at the front at h=0.6 m on the surface of CLT
115 | TC_W1_Front_060_035 | Thermocouple | °C | W1 at the front at h=0.6 m in panel 35 mm from interface
116 | TC_W1_Front_060_070 | Thermocouple | °C | W1 at the front at h=0.6 m in panel 70 mm from interface
117 | TC_Ceiling_Tr1_CLT | Thermocouple | °C | ceiling above Tr1 on the surface of CLT
118 | TC_Ceiling_Tr1_1GB | Thermocouple | °C | ceiling above Tr1 on the surface of 1st GB
119 | TC_Ceiling_Tr1_2GB | Thermocouple | °C | ceiling above Tr1 on the surface of 2nd GB
120 | TC_Ceiling_Tr2_CLT | Thermocouple | °C | ceiling above Tr2 on the surface of CLT
121 | TC_Ceiling_Tr2_1GB | Thermocouple | °C | ceiling above Tr2 on the surface of 1st GB
122 | TC_Ceiling_Tr2_2GB | Thermocouple | °C | ceiling above Tr2 on the surface of 2nd GB
123 | STE_1 | Thermocouple | °C | 12" below ceiling (see "Drawings")
124 | STE_2 | Thermocouple | °C | 12" below ceiling (see "Drawings")
125 | STE_3 | Thermocouple | °C | 12" below ceiling (see "Drawings")
126 | STE_4 | Thermocouple | °C | 18" below ceiling (see "Drawings")
127 | PT_W1_Middle_180_SPy | Thermocouple | °C | Temperature for plate thermometer on W1 at the mid length at h=1.8 m
128 | DFT_W1_Middle_180_Px | Thermocouple | °C | DFT on W1 at the mid length at h=1.8 m (Front plate)
129 | PT_W1_Middle_180_SPx | Thermocouple | °C | Plate thermometer on W1 at the mid length at h=1.8 m
130 | PT_W1_Front_180_SPy | Thermocouple | °C | Temperature for plate thermometer on W1 at front
131 | PT_W1_Front_180_SPx | Thermocouple | °C | Plate thermometer on W1 in the front of the compartment at h=1.8 m
132 | PT_W1_Rear_180_SPy | Thermocouple | °C | Temperature for plate thermometer on W1 in the rear of the compartment at h=1.8 m
133 | PT_W1_Rear_180_SPx | Thermocouple | °C | plate thermometer on W1 in the rear of the compartment at h=1.8 m
134 | PT_Ceiling_Bed_SPy | Thermocouple | °C | Temperature for plate thermometer on ceiling above the bed
135 | DFT_Ceiling_Bed_Px | Thermocouple | °C | DFT on the ceiling above the bed (Back plate)
136 | PT_Ceiling_Bed_SPx | Thermocouple | °C | Plate thermometer on the ceiling above the bed
137 | DFT_W1_Middle_180_Py | Thermocouple | °C | DFT on W1 at the mid length at h=1.8 m
138 | DFT_Ceiling_Bed_Py | Thermocouple | °C | DFT on the ceiling above the bed (Front plate)
139 | TC_W1_Middle_060_CLT | Thermocouple | °C | W1 at the mid length at h=0.6 m on the surface of CLT
140 | TC_W1_Middle_120_CLT | Thermocouple | °C | W1 at the mid length at h=1.2 m on the surface of CLT
141 | TC_W1_Middle_180_CLT | Thermocouple | °C | W1 at the mid length at h=1.8 m on the surface of CLT
142 | TC_W1_Middle_060_1GB | Thermocouple | °C | W1 at the mid length at h=0.6 m on the surface of 1st GB
143 | TC_W1_Middle_120_1GB | Thermocouple | °C | W1 at the mid length at h=1.2 m on the surface of 1st GB
144 | TC_W1_Middle_180_1GB | Thermocouple | °C | W1 at the mid length at h=1.8 m on the surface of 1st GB
145 | TC_W1_Middle_060_2GB | Thermocouple | °C | W1 at the mid length at h=0.6 m on the surface of 2nd GB
146 | TC_W1_Middle_120_2GB | Thermocouple | °C | W1 at the mid length at h=1.2 m on the surface of 2nd GB
147 | TC_W1_Middle_180_070 | Thermocouple | °C | W1 at the mid length at h=1.8 m in panel 70 mm from interface
148 | TC_W1_Rear_180_CLT | Thermocouple | °C | W1 at the rear at h=1.8 m on the surface of CLT
149 | TC_W1_Rear_180_035 | Thermocouple | °C | W1 at the rear at h=1.8 m in panel 35 mm from interface
150 | TC_W1_Rear_180_070 | Thermocouple | °C | W1 at the rear at h=1.8 m in panel 70 mm from interface
151 | TC_W1_Rear_060_CLT | Thermocouple | °C | W1 at the rear at h=0.6 m on the surface of CLT
152 | TC_W1_Rear_060_035 | Thermocouple | °C | W1 at the rear at h=0.6 m in panel 35 mm from interface
153 | TC_W1_Rear_060_070 | Thermocouple | °C | W1 at the rear at h=0.6 m in panel 70 mm from interface
154 | TC_Tree_Tr1_060 | Thermocouple | °C | Tree Tr1 at h=0.6 m
155 | TC_Tree_Tr1_160 | Thermocouple | °C | Tree Tr1 at h=1.6 m
156 | TC_Tree_Tr1_260 | Thermocouple | °C | Tree Tr1 at h=2.6 m
157 | TC_Tree_Tr2_060 | Thermocouple | °C | Tree Tr2 at h=0.6 m
158 | TC_Tree_Tr2_160 | Thermocouple | °C | Tree Tr2 at h=1.6 m
159 | TC_Tree_Tr2_260 | Thermocouple | °C | Tree Tr2 at h=2.6 m
160 | TC_Tree_Tr5_060 | Thermocouple | °C | Tree Tr5 at h=0.6 m
161 | TC_Tree_Tr5_160 | Thermocouple | °C | Tree Tr5 at h=1.6 m
162 | TC_Tree_Tr5_260 | Thermocouple | °C | Tree Tr5 at h=2.6 m
163 | TC_Tree_Tr1_110 | Thermocouple | °C | Tree Tr1 at h=1.1 m
164 | TC_Tree_Tr1_210 | Thermocouple | °C | Tree Tr1 at h=2.1 m
165 | TC_Tree_Tr2_110 | Thermocouple | °C | Tree Tr2 at h=1.1 m
166 | TC_Tree_Tr2_210 | Thermocouple | °C | Tree Tr2 at h=2.1 m
167 | TC_Tree_Tr5_110 | Thermocouple | °C | Tree Tr5 at h=1.1 m
168 | TC_Tree_Tr5_210 | Thermocouple | °C | Tree Tr5 at h=2.1 m
169 | TC_Tree_Tr3_060 | Thermocouple | °C | Tree Tr3 at h=0.6 m
170 | TC_Tree_Tr3_160 | Thermocouple | °C | Tree Tr3 at h=1.6 m
171 | TC_Tree_Tr3_260 | Thermocouple | °C | Tree Tr3 at h=2.6 m
172 | TC_Tree_Tr4_060 | Thermocouple | °C | Tree Tr4 at h=0.6 m
173 | TC_Tree_Tr4_160 | Thermocouple | °C | Tree Tr4 at h=1.6 m
174 | TC_Tree_Tr4_260 | Thermocouple | °C | Tree Tr4 at h=2.6 m
175 | TC_Tree_Tr6_060 | Thermocouple | °C | Tree Tr6 at h=0.6 m
176 | TC_Tree_Tr6_160 | Thermocouple | °C | Tree Tr6 at h=1.6 m
177 | TC_Tree_Tr6_260 | Thermocouple | °C | Tree Tr6 at h=2.6 m
178 | TC_Tree_Tr3_110 | Thermocouple | °C | Tree Tr3 at h=1.1 m
179 | TC_Tree_Tr3_210 | Thermocouple | °C | Tree Tr3 at h=2.1 m
180 | TC_Tree_Tr4_110 | Thermocouple | °C | Tree Tr4 at h=1.1 m
181 | TC_Tree_Tr4_210 | Thermocouple | °C | Tree Tr4 at h=2.1 m
182 | TC_Tree_Tr6_110 | Thermocouple | °C | Tree Tr6 at h=1.1 m
183 | TC_Tree_Tr6_210 | Thermocouple | °C | Tree Tr6 at h=2.1 m
184 | Gardon_W1_Middle_180 | ±0.2V default | kW/m2 | W1 at the mid length at h=1.8 m
185 | O2_room | ±10V default | % | At the centre of the room, 2.1 m high
186 | CO2_room | ±10V default | % | At the centre of the room, 2.1 m high
187 | CO_room | ±10V default | % | At the centre of the room, 2.1 m high
188 | DEWpt_rack | ±10V default | °C | Gas rack dew point measurement
189 | VI | ±10V default | V | Internal heartbeat
190 | HRR | N/A | kW | globdata(r,HRR) [!!! updated from "86: HRR (kW)" on BONICHI on 03/07/2018 by MSH]
191 | HRRburner | N/A | kW | globdata(r,HRRburner) [!!! updated from "85: HRRburner (kW)" on BONICHI on 03/07/2018 by MSH]
192 | VelCeiling | N/A | m/s | sign(scaledata(r,dP_c))*1/1.08*(2*abs(scaledata(r,dP_c))*(scaledata(r,TC_V_c)+273.15)/353.06)^(1/2)
193 | VelDoor1 | N/A | m/s | sign(scaledata(r,dP_o1))*1/1.08*(2*abs(scaledata(r,dP_o1))*(scaledata(r,Door_TC_2)+273.15)/353.06)^(1/2)
194 | VelDoor2 | N/A | m/s | sign(scaledata(r,dP_o2))*1/1.08*(2*abs(scaledata(r,dP_o2))*(scaledata(r,Door_TC_2)+273.15)/353.06)^(1/2)
195 | VelDoor3 | N/A | m/s | sign(scaledata(r,dP_o3))*1/1.08*(2*abs(scaledata(r,dP_o3))*(scaledata(r,Door_TC_2)+273.15)/353.06)^(1/2)
196 | VelDoor4 | N/A | m/s | sign(scaledata(r,dP_o4))*1/1.08*(2*abs(scaledata(r,dP_o4))*(scaledata(r,Door_TC_6)+273.15)/353.06)^(1/2)
197 | VelDoor5 | N/A | m/s | sign(scaledata(r,dP_o5))*1/1.08*(2*abs(scaledata(r,dP_o5))*(scaledata(r,Door_TC_6)+273.15)/353.06)^(1/2)
198 | VelDoor6 | N/A | m/s | sign(scaledata(r,dP_o6))*1/1.08*(2*abs(scaledata(r,dP_o6))*(scaledata(r,Door_TC_6)+273.15)/353.06)^(1/2)
199 | HFPT_W1_Mid_180 | N/A | kW/m^2 | globdata(r,HFPT_W1_Mid_180)
200 | HFPT_W1_Front_180 | N/A | kW/m^2 | globdata(r,HFPT_W1_Front_180)
201 | HFPT_W1_Rear_180 | N/A | kW/m^2 | globdata(r,HFPT_W1_Rear_180)
202 | HFPT_Front_e350 | N/A | kW/m^2 | globdata(r,HFPT_Front_e350)
203 | HFPT_Front_e550 | N/A | kW/m^2 | globdata(r,HFPT_Front_e550)
204 | HFPT_W3_Mid_180 | N/A | kW/m^2 | globdata(r,HFPT_W3_Mid_180)
205 | HFPT_W4_Mid_180 | N/A | kW/m^2 | globdata(r,HFPT_W4_Mid_180)

## User Events
Event Count | Time (s) | Time Stamp | Event Description
1 | 0 | 2017-04-13 10:05 | Ignition
2 | 654 | 2017-04-13 10:16 | burner off
3 | 702 | 2017-04-13 10:17 | flashover
4 | 2559 | 2017-04-13 10:48 | room gas sample line fell - approx time
5 | 2945 | 2017-04-13 10:54 | purge gas rack and shut off sample
6 | 8729 | 2017-04-13 12:31 | CLT delamination in progress
7 | 12160 | 2017-04-13 13:28 | start water suppression
8 | 13171 | 2017-04-13 13:45 | Fire Out

## Scaled Data
Time Stamp | Time (s) | 0: TC_Ceiling_Center_020 (°C) | 1: TC_Ceiling_Center_035 (°C) | 2: TC_Ceiling_Center_050 (°C) | 3: TC_Ceiling_Center_065 (°C) | 4: TC_Ceiling_Center_090 (°C) | 5: TC_Ceiling_Center_115 (°C) | 6: TC_Ceiling_Center_070 (°C) | 7: TC_W3_Middle_180_020 (°C) | 8: TC_W3_Middle_180_035 (°C) | 9: TC_W3_Middle_180_050 (°C) | 10: TC_W3_Middle_180_065 (°C) | 11: TC_W3_Middle_180_090 (°C) | 12: TC_W3_Middle_180_115 (°C) | 13: TC_W3_Middle_180_070 (°C) | 14: TC_W3_Middle_060_CLT (°C) | 15: TC_W3_Middle_120_CLT (°C) | 16: TC_W3_Middle_180_CLT (°C) | 17: TC_W3_Middle_060_1GB (°C) | 18: TC_W3_Middle_120_1GB (°C) | 19: TC_W3_Middle_180_1GB (°C) | 20: TC_W3_Middle_060_2GB (°C) | 21: TC_W3_Middle_120_2GB (°C) | 22: TC_W3_Middle_180_2GB (°C) | 23: TC_Ceiling_Tr4_CLT (°C) | 24: TC_Ceiling_Tr4_1GB (°C) | 25: TC_Ceiling_Tr4_2GB (°C) | 26: STE_6 (°C) | 27: STE_10 (°C) | 28: TC_V_c (°C) | 29: TC_Ceiling_Tr3_CLT (°C) | 30: TC_Ceiling_Tr3_1GB (°C) | 31: TC_Ceiling_Tr3_2GB (°C) | 32: TC_Ceiling_Center_CLT (°C) | 33: TC_Ceiling_Center_1GB (°C) | 34: TC_Ceiling_Center_2GB (°C) | 35: PT_W3_Middle_180_SPx (°C) | 36: PT_Ceiling_Center_SPy (°C) | 37: DFT_Ceiling_Center_Px (°C) | 38: PT_Ceiling_Center_SPx (°C) | 39: STE_5 (°C) | 40: STE_9 (°C) | 41: PT_W3_Middle_180_SPy (°C) | 42: DFT_Ceiling_Center_Py (°C) | 43: Door_TC_1 (°C) | 44: Door_TC_2 (°C) | 45: Door_TC_3 (°C) | 46: Door_TC_4 (°C) | 47: Door_TC_5 (°C) | 48: Door_TC_6 (°C) | 49: Door_TC_7 (°C) | 50: PT_Front_a480_SPy (°C) | 51: PT_Front_a480_SPx (°C) | 52: PT_Front_a240_SPy (°C) | 53: PT_Front_a240_SPx (°C) | 54: TC_Smoke (°C) | 55: TC_HFGtower (°C) | 56: TC_HFGfloor (°C) | 57: TC_HFGw1 (°C) | 58: TC_GoPro (°C) | 59: TC_TreeSteel (°C) | 60: TC_TBD (°C) | 61: dP_c (Pa) | 62: dP_o1 (Pa) | 63: dP_o2 (Pa) | 64: dP_o3 (Pa) | 65: dP_o4 (Pa) | 66: dP_o5 (Pa) | 67: dP_o6 (Pa) | 68: dP_r (Pa) | 69: Gardon_Front_a480 (kW/m2) | 70: Gardon_Front_a240 (kW/m2) | 71: Gardon_Floor_Center (kW/m2) | 72: SmokeAlarm (V) | 73: HeatAlarm (V) | 74: SMOKE (V) | 75: TC_W1_Middle_180_020 (°C) | 76: TC_W1_Middle_180_035 (°C) | 77: TC_W1_Middle_180_050 (°C) | 78: TC_W1_Middle_180_065 (°C) | 79: TC_W1_Middle_180_090 (°C) | 80: TC_W1_Middle_180_115 (°C) | 81: TC_W1_Middle_180_140 (°C) | 82: TC_W4_Middle_180_020 (°C) | 83: TC_W4_Middle_180_035 (°C) | 84: TC_W4_Middle_180_050 (°C) | 85: TC_W4_Middle_180_065 (°C) | 86: TC_W4_Middle_180_090 (°C) | 87: TC_W4_Middle_180_115 (°C) | 88: TC_W4_Middle_180_070 (°C) | 89: Roof_TC_350 (°C) | 90: Roof_TC_450 (°C) | 91: Roof_TC_550 (°C) | 92: Roof_TC_650 (°C) | 93: Roof_TC_750 (°C) | 94: PT_Front_e350_SPx (°C) | 95: PT_Front_e550_SPx (°C) | 96: TC_W4_Middle_060_CLT (°C) | 97: TC_W4_Middle_120_CLT (°C) | 98: TC_W4_Middle_180_CLT (°C) | 99: TC_W4_Middle_060_1GB (°C) | 100: TC_W4_Middle_120_1GB (°C) | 101: TC_W4_Middle_180_1GB (°C) | 102: TC_W4_Middle_060_2GB (°C) | 103: TC_W4_Middle_120_2GB (°C) | 104: TC_W4_Middle_180_2GB (°C) | 105: PT_W4_Middle_180_SPx (°C) | 106: STE_7 (°C) | 107: STE_8 (°C) | 108: PT_W4_Middle_180_SPy (°C) | 109: Gardon_Front_e350 (kW/m2) | 110: Gardon_Front_e550 (kW/m2) | 111: TC_W1_Front_180_CLT (°C) | 112: TC_W1_Front_180_035 (°C) | 113: TC_W1_Front_180_070 (°C) | 114: TC_W1_Front_060_CLT (°C) | 115: TC_W1_Front_060_035 (°C) | 116: TC_W1_Front_060_070 (°C) | 117: TC_Ceiling_Tr1_CLT (°C) | 118: TC_Ceiling_Tr1_1GB (°C) | 119: TC_Ceiling_Tr1_2GB (°C) | 120: TC_Ceiling_Tr2_CLT (°C) | 121: TC_Ceiling_Tr2_1GB (°C) | 122: TC_Ceiling_Tr2_2GB (°C) | 123: STE_1 (°C) | 124: STE_2 (°C) | 125: STE_3 (°C) | 126: STE_4 (°C) | 127: PT_W1_Middle_180_SPy (°C) | 128: DFT_W1_Middle_180_Px (°C) | 129: PT_W1_Middle_180_SPx (°C) | 130: PT_W1_Front_180_SPy (°C) | 131: PT_W1_Front_180_SPx (°C) | 132: PT_W1_Rear_180_SPy (°C) | 133: PT_W1_Rear_180_SPx (°C) | 134: PT_Ceiling_Bed_SPy (°C) | 135: DFT_Ceiling_Bed_Px (°C) | 136: PT_Ceiling_Bed_SPx (°C) | 137: DFT_W1_Middle_180_Py (°C) | 138: DFT_Ceiling_Bed_Py (°C) | 139: TC_W1_Middle_060_CLT (°C) | 140: TC_W1_Middle_120_CLT (°C) | 141: TC_W1_Middle_180_CLT (°C) | 142: TC_W1_Middle_060_1GB (°C) | 143: TC_W1_Middle_120_1GB (°C) | 144: TC_W1_Middle_180_1GB (°C) | 145: TC_W1_Middle_060_2GB (°C) | 146: TC_W1_Middle_120_2GB (°C) | 147: TC_W1_Middle_180_070 (°C) | 148: TC_W1_Rear_180_CLT (°C) | 149: TC_W1_Rear_180_035 (°C) | 150: TC_W1_Rear_180_070 (°C) | 151: TC_W1_Rear_060_CLT (°C) | 152: TC_W1_Rear_060_035 (°C) | 153: TC_W1_Rear_060_070 (°C) | 154: TC_Tree_Tr1_060 (°C) | 155: TC_Tree_Tr1_160 (°C) | 156: TC_Tree_Tr1_260 (°C) | 157: TC_Tree_Tr2_060 (°C) | 158: TC_Tree_Tr2_160 (°C) | 159: TC_Tree_Tr2_260 (°C) | 160: TC_Tree_Tr5_060 (°C) | 161: TC_Tree_Tr5_160 (°C) | 162: TC_Tree_Tr5_260 (°C) | 163: TC_Tree_Tr1_110 (°C) | 164: TC_Tree_Tr1_210 (°C) | 165: TC_Tree_Tr2_110 (°C) | 166: TC_Tree_Tr2_210 (°C) | 167: TC_Tree_Tr5_110 (°C) | 168: TC_Tree_Tr5_210 (°C) | 169: TC_Tree_Tr3_060 (°C) | 170: TC_Tree_Tr3_160 (°C) | 171: TC_Tree_Tr3_260 (°C) | 172: TC_Tree_Tr4_060 (°C) | 173: TC_Tree_Tr4_160 (°C) | 174: TC_Tree_Tr4_260 (°C) | 175: TC_Tree_Tr6_060 (°C) | 176: TC_Tree_Tr6_160 (°C) | 177: TC_Tree_Tr6_260 (°C) | 178: TC_Tree_Tr3_110 (°C) | 179: TC_Tree_Tr3_210 (°C) | 180: TC_Tree_Tr4_110 (°C) | 181: TC_Tree_Tr4_210 (°C) | 182: TC_Tree_Tr6_110 (°C) | 183: TC_Tree_Tr6_210 (°C) | 184: Gardon_W1_Middle_180 (kW/m2) | 185: O2_room (%) | 186: CO2_room (%) | 187: CO_room (%) | 188: DEWpt_rack (°C) | 189: VI (V) | 190: HRR (kW) | 191: HRRburner (kW) | 192: VelCeiling (m/s) | 193: VelDoor1 (m/s) | 194: VelDoor2 (m/s) | 195: VelDoor3 (m/s) | 196: VelDoor4 (m/s) | 197: VelDoor5 (m/s) | 198: VelDoor6 (m/s) | 199: HFPT_W1_Mid_180 (kW/m^2) | 200: HFPT_W1_Front_180 (kW/m^2) | 201: HFPT_W1_Rear_180 (kW/m^2) | 202: HFPT_Front_e350 (kW/m^2) | 203: HFPT_Front_e550 (kW/m^2) | 204: HFPT_W3_Mid_180 (kW/m^2) | 205: HFPT_W4_Mid_180 (kW/m^2)
42838.4107 | -831 | 22.9129 | 22.8835 | 22.8817 | 22.8153 | 22.4671 | 21.817 | 22.7654 | 21.8838 | 22.4063 | 22.4274 | 22.4142 | 22.1005 | 21.331 | 22.2748 | 21.6141 | 21.7879 | 21.9303 | 21.1125 | 21.2084 | 21.4382 | 20.5246 | 20.6706 | 20.9596 | 21.9286 | 21.701 | 21.341 | 20.476 | 20.5883 | 20.5035 | 22.0727 | 21.6797 | 21.2107 | 22.0248 | 21.7687 | 21.3826 | 19.9648 | 20.585 |  | 20.5918 | 20.3226 | 20.4155 | 19.1177 |  | 16.8261 | 16.835 | 16.5991 | 16.8147 | 16.844 | 17.2843 | 17.7409 | 15.546 | 16.6732 | 15.8435 | 16.8492 | 17.8962 | 45.4369 | 48.4102 | 44.461 | 21.2901 |  |  | 0.32747 | -0.67624 | -42.7981 | 0.39094 | 0.17887 | -197.8486 | 14.2991 | -0.5392 | -0.22973 | 0.13396 | -0.032346 | 8.829 | 9.0588 | 1.9783 | 21.8313 | 22.0598 | 22.2481 | 22.3258 | 22.1669 | 21.5134 | 20.3481 | 22.2412 | 22.4102 | 22.4437 | 22.3958 | 22.0478 | 21.2943 | 22.3194 | 17.3489 | 16.9814 | 15.9715 | 16.0777 | 16.1584 | 17.1221 | 16.7527 | 22.4055 | 22.1816 | 21.7485 | 22.1008 | 21.8403 | 21.3448 | 21.9768 | 21.5729 | 20.955 | 20.1552 | 20.5426 | 20.0633 | 19.7642 | 0.028912 | 0.12613 | 20.7266 | 22.0973 | 22.4247 | 20.1295 | 21.7298 | 22.1826 | 21.994 | 21.7706 | 21.3388 | 21.8522 | 21.5329 | 21.1231 | 20.6199 | 20.605 | 20.6151 | 20.6514 | 20.059 |  | 20.2501 | 19.8624 | 20.154 | 19.7134 | 20.1178 | 20.3818 |  | 20.4852 |  |  | 20.2233 | 20.3783 | 20.6118 | [5 empty] | 21.9806 | 20.3623 | 21.7264 | 22.1224 | 19.6324 | 21.2851 | 21.932 | 19.2988 | 19.9051 | 21.1742 |  | 19.7944 | 21.0006 | 18.8133 | 19.731 | 20.8812 | 19.3537 | 20.2172 | 19.0663 | 20.304 | 19.2204 | 20.456 | 18.7817 | 20.3185 | 21.0899 | 19.285 | 19.7829 | 21.0695 | 18.9956 | 19.8384 | 20.8941 | 18.9645 | 20.3667 | 19.337 | 20.1158 | 19.0397 | 20.3566 | -0.12961 | 20.9496 | 0.0477 | 0.01452 | -27.0518 | 0.37453 | -1.07 | -0.2 | 0.6834 | -0.9759 | -7.7637 | 0.74201 | 0.50229 | -16.7054 | 4.491 | 0.42548 | 0.42772 | 0.43065 | 0.37733 | 0.48728 | 0.44207 | 0.43049
42838.4107 | -830 | 22.9197 | 22.8814 | 22.8809 | 22.8208 | 22.4635 | 21.818 | 22.7664 | 21.8895 | 22.409 | 22.4295 | 22.4149 | 22.1041 | 21.3327 | 22.2772 | 21.608 | 21.7814 | 21.9224 | 21.1065 | 21.211 | 21.4289 | 20.5134 | 20.6539 | 20.9635 | 21.9333 | 21.6982 | 21.3322 | 20.4789 | 20.5912 | 20.4951 | 22.0716 | 21.6819 | 21.2127 | 22.026 | 21.7705 | 21.3809 | 19.9662 | 20.5781 |  | 20.5913 | 20.32 | 20.412 | 19.1063 |  | 16.8098 | 16.8317 | 16.5752 | 16.7937 | 16.8267 | 17.263 | 17.716 | 15.5505 | 16.6762 | 15.8826 | 16.8516 | 17.8946 | 45.4534 | 48.3892 | 44.4611 | 21.296 |  |  | 0.31499 | -0.63747 | -41.4195 | 0.61699 | 0.28598 | -197.8466 | 14.8123 | -0.39792 | -0.10596 | 0.027595 | 0.076328 | 8.8285 | 9.0583 | 1.9778 | 21.833 | 22.0658 | 22.2672 | 22.3297 | 22.1724 | 21.5243 | 20.3585 | 22.2504 | 22.4122 | 22.459 | 22.4089 | 22.0573 | 21.3049 | 22.3214 | 17.3486 | 16.9988 | 15.9859 | 16.0675 | 16.1597 | 17.1184 | 16.7542 | 22.4063 | 22.1781 | 21.742 | 22.1047 | 21.8338 | 21.3525 | 21.9728 | 21.5705 | 20.9596 | 20.1611 | 20.5424 | 20.0601 | 19.7664 | -0.13761 | -0.057409 | 20.7009 | 22.0859 | 22.412 | 20.1174 | 21.724 | 22.1747 | 21.9802 | 21.7615 | 21.3343 | 21.8476 | 21.5165 | 21.1181 | 20.6226 | 20.5947 | 20.608 | 20.6488 | 20.071 |  | 20.2494 | 19.8501 | 20.1505 | 19.7252 | 20.1173 | 20.3801 |  | 20.4884 |  |  | 20.2098 | 20.3809 | 20.6205 | [5 empty] | 21.9795 | 20.3793 | 21.7367 | 22.1371 | 19.6334 | 21.2865 | 21.9324 | 19.297 | 19.8851 | 21.1731 |  | 19.7887 | 20.9897 | 18.7964 | 19.7256 | 20.879 | 19.3427 | 20.2081 | 19.0579 | 20.3014 | 19.2211 | 20.4528 | 18.7893 | 20.3148 | 21.0957 | 19.2931 | 19.7858 | 21.078 | 19.0015 | 19.8428 | 20.9004 | 18.9687 | 20.3599 | 19.3425 | 20.1116 | 19.0417 | 20.3611 | -0.17914 | 20.95 | 0.047571 | 0.013054 | -26.9562 | 0.39921 | -1.07 | -0.2 | 0.67023 | -0.94751 | -7.6376 | 0.93216 | 0.6351 | -16.7047 | 4.5707 | 0.42512 | 0.42794 | 0.4303 | 0.37694 | 0.48586 | 0.44243 | 0.43062
42838.4107 | -829 | 22.9145 | 22.8806 | 22.8752 | 22.8152 | 22.4615 | 21.8159 | 22.7593 | 21.8784 | 22.406 | 22.4166 | 22.4095 | 22.1064 | 21.3234 | 22.279 | 21.6049 | 21.7851 | 21.9206 | 21.1095 | 21.2145 | 21.4336 | 20.5067 | 20.658 | 20.9587 | 21.9352 | 21.6979 | 21.3369 | 20.4847 | 20.5876 | 20.4985 | 22.0687 | 21.678 | 21.2085 | 22.0162 | 21.763 | 21.3844 | 19.9718 | 20.5772 |  | 20.5868 | 20.3138 | 20.4077 | 19.108 |  | 16.803 | 16.81 | 16.5608 | 16.7761 | 16.8168 | 17.2541 | 17.7096 | 15.5457 | 16.6674 | 15.9224 | 16.8569 | 17.9003 | 45.4662 | 48.3677 | 44.4464 | 21.3014 |  |  | 0.28345 | -0.39105 | -39.8522 | 0.20958 | 0.29846 | -197.8532 | 15.0515 | -0.51226 | -0.075801 | 0.11613 | 0.038483 | 8.8302 | 9.06 | 1.9783 | 21.8385 | 22.0534 | 22.2633 | 22.3263 | 22.1657 | 21.5194 | 20.3484 | 22.2431 | 22.4083 | 22.4507 | 22.4055 | 22.0466 | 21.2878 | 22.308 | 17.3379 | 16.989 | 15.9865 | 16.0395 | 16.1535 | 17.1156 | 16.7449 | 22.4028 | 22.1757 | 21.7417 | 22.1009 | 21.8316 | 21.3526 | 21.9699 | 21.5701 | 20.959 | 20.1561 | 20.537 | 20.0499 | 19.7627 | -0.11421 | -0.16145 | 20.7121 | 22.1023 | 22.4302 | 20.1133 | 21.7211 | 22.183 | 21.9962 | 21.7708 | 21.3382 | 21.8529 | 21.5298 | 21.1209 | 20.6273 | 20.6121 | 20.6318 | 20.6585 | 20.071 |  | 20.2416 | 19.8182 | 20.1388 | 19.7244 | 20.11 | 20.3724 |  | 20.4863 |  |  | 20.1926 | 20.3819 | 20.6174 | [5 empty] | 21.9783 | 20.3696 | 21.7334 | 22.1409 | 19.6278 | 21.2876 | 21.9303 | 19.2969 | 19.8971 | 21.1761 |  | 19.7838 | 20.996 | 18.8032 | 19.7226 | 20.877 | 19.3379 | 20.2123 | 19.067 | 20.3007 | 19.222 | 20.4528 | 18.7823 | 20.3132 | 21.0839 | 19.285 | 19.7736 | 21.0687 | 18.9925 | 19.8289 | 20.892 | 18.96 | 20.3507 | 19.3274 | 20.0976 | 19.0398 | 20.352 | -0.30083 | 20.9496 | 0.047528 | 0.012879 | -26.9855 | 0.42358 | -1.13 | -0.01 | 0.63579 | -0.74208 | -7.4914 | 0.54326 | 0.64881 | -16.7047 | 4.6074 | 0.42486 | 0.42844 | 0.43008 | 0.3778 | 0.48472 | 0.44257 | 0.43056
42838.4107 | -828 | 22.9195 | 22.8876 | 22.8783 | 22.8153 | 22.4607 | 21.8224 | 22.757 | 21.8824 | 22.4068 | 22.4183 | 22.4138 | 22.1008 | 21.324 | 22.2791 | 21.6064 | 21.7875 | 21.9303 | 21.1189 | 21.2128 | 21.4393 | 20.5132 | 20.6687 | 20.9627 | 21.9401 | 21.7043 | 21.3373 | 20.4931 | 20.5907 | 20.5061 | 22.0642 | 21.6716 | 21.2058 | 22.0269 | 21.7715 | 21.3862 | 19.9737 | 20.5753 |  | 20.5863 | 20.3146 | 20.4082 | 19.0931 |  | 16.802 | 16.802 | 16.5526 | 16.7697 | 16.819 | 17.2709 | 17.7458 | 15.567 | 16.6784 | 15.9565 | 16.8615 | 17.8944 | 45.4585 | 48.3434 | 44.4283 | 21.2942 |  |  | 0.33733 | -0.42259 | -38.6537 | 0.43891 | 0.4358 | -197.8841 | 15.5266 | -0.54905 | 0.081242 | -0.074578 | -0.021582 | 8.8292 | 9.059 | 1.9788 | 21.8394 | 22.0525 | 22.2586 | 22.3288 | 22.1621 | 21.5128 | 20.3545 | 22.2385 | 22.4164 | 22.4414 | 22.4054 | 22.0503 | 21.2963 | 22.3148 | 17.3094 | 16.9744 | 15.9909 | 16.0348 | 16.1393 | 17.1131 | 16.7442 | 22.4007 | 22.1823 | 21.748 | 22.1026 | 21.8354 | 21.3562 | 21.9776 | 21.5747 | 20.9572 | 20.1612 | 20.5259 | 20.0461 | 19.7728 | -0.12326 | -0.29174 | 20.6928 | 22.0773 | 22.4154 | 20.1088 | 21.7134 | 22.1695 | 21.986 | 21.7597 | 21.3321 | 21.8375 | 21.5217 | 21.118 | 20.6165 | 20.6105 | 20.6177 | 20.6464 | 20.0702 |  | 20.2439 | 19.8098 | 20.1395 | 19.7216 | 20.119 | 20.3719 |  | 20.4899 |  |  | 20.1753 | 20.3827 | 20.6194 | [5 empty] | 21.9897 | 20.3814 | 21.734 | 22.1414 | 19.6252 | 21.2844 | 21.9323 | 19.2932 | 19.894 | 21.1686 |  | 19.7903 | 20.9916 | 18.8033 | 19.7169 | 20.8721 | 19.3417 | 20.2027 | 19.0641 | 20.2987 | 19.2249 | 20.4488 | 18.7863 | 20.3173 | 21.0853 | 19.2832 | 19.7666 | 21.0693 | 18.999 | 19.8311 | 20.8909 | 18.9649 | 20.3592 | 19.3226 | 20.095 | 19.0391 | 20.3546 | -0.073405 | 20.9497 | 0.047467 | 0.013141 | -26.9877 | 0.44761 | -1.3 | -0.16 | 0.69361 | -0.77142 | -7.3778 | 0.78617 | 0.78402 | -16.7065 | 4.6797 | 0.42496 | 0.42869 | 0.43046 | 0.38068 | 0.48414 | 0.44305 | 0.43045
42838.4107 | -827 | 22.917 | 22.8852 | 22.8729 | 22.8102 | 22.4606 | 21.8184 | 22.7541 | 21.875 | 22.3991 | 22.4236 | 22.4132 | 22.0908 | 21.3203 | 22.2632 | 21.6062 | 21.789 | 21.9289 | 21.1114 | 21.2068 | 21.4362 | 20.5144 | 20.6656 | 20.9642 | 21.9364 | 21.7032 | 21.3353 | 20.4862 | 20.5888 | 20.5048 | 22.066 | 21.6787 | 21.2052 | 22.0295 | 21.7634 | 21.383 | 19.9669 | 20.562 |  | 20.5817 | 20.3102 | 20.4092 | 19.0679 |  | 16.8014 | 16.7817 | 16.5401 | 16.7599 | 16.8153 | 17.2687 | 17.7578 | 15.5449 | 16.6743 | 15.9516 | 16.8614 | 17.9005 | 45.4575 | 48.3115 | 44.4305 | 21.2962 |  |  | 0.38464 | -0.023065 | -38.3501 | 0.068298 | 0.30569 | -197.8355 | 15.3472 | -0.48926 | -0.13165 | -0.015204 | -0.069496 | 8.8299 | 9.0598 | 1.9784 | 21.8356 | 22.0594 | 22.2615 | 22.3246 | 22.1637 | 21.5112 | 20.352 | 22.2383 | 22.4114 | 22.4413 | 22.4022 | 22.047 | 21.2988 | 22.3122 | 17.2527 | 16.9707 | 15.9926 | 16.0324 | 16.1223 | 17.1104 | 16.7437 | 22.4092 | 22.1873 | 21.7536 | 22.1089 | 21.8421 | 21.356 | 21.9868 | 21.5767 | 20.9658 | 20.1665 | 20.5295 | 20.0458 | 19.7963 | 0.079439 | -0.11941 | 20.6808 | 22.0893 | 22.4149 | 20.1147 | 21.7147 | 22.1783 | 21.9858 | 21.7632 | 21.3419 | 21.8427 | 21.5147 | 21.1341 | 20.6128 | 20.6211 | 20.6183 | 20.6529 | 20.0696 |  | 20.2413 | 19.7969 | 20.1359 | 19.7359 | 20.1137 | 20.3752 |  | 20.4777 |  |  | 20.1588 | 20.381 | 20.62 | [5 empty] | 21.988 | 20.3814 | 21.7334 | 22.1399 | 19.6246 | 21.2857 | 21.9327 | 19.2916 | 19.8971 | 21.1692 |  | 19.788 | 20.986 | 18.7981 | 19.7133 | 20.8666 | 19.3443 | 20.1975 | 19.0537 | 20.2922 | 19.2183 | 20.441 | 18.794 | 20.3217 | 21.0895 | 19.2873 | 19.7684 | 21.0706 | 19.0046 | 19.8323 | 20.8986 | 18.9753 | 20.3564 | 19.3289 | 20.0948 | 19.0422 | 20.3539 | -0.19509 | 20.9511 | 0.047381 | 0.0128 | -27.0946 | 0.47158 | -1.27 | -0.12 | 0.74065 | -0.18022 | -7.3485 | 0.31011 | 0.65663 | -16.7044 | 4.6526 | 0.42489 | 0.42893 | 0.42988 | 0.38666 | 0.4839 | 0.44352 | 0.42998
42838.4107 | -826 | 22.9167 | 22.8926 | 22.8811 | 22.8235 | 22.4703 | 21.8176 | 22.7664 | 21.8785 | 22.4164 | 22.4289 | 22.4126 | 22.1046 | 21.3261 | 22.2817 | 21.608 | 21.7853 | 21.925 | 21.1131 | 21.2079 | 21.4362 | 20.5109 | 20.6649 | 20.9607 | 21.9373 | 21.7008 | 21.3311 | 20.4781 | 20.5891 | 20.509 | 22.0673 | 21.6842 | 21.215 | 22.0321 | 21.7635 | 21.3852 | 19.9652 | 20.5633 |  | 20.582 | 20.3166 | 20.4041 | 19.0765 |  | 16.7814 | 16.7725 | 16.535 | 16.7501 | 16.8074 | 17.2667 | 17.7332 | 15.5102 | 16.6767 | 15.925 | 16.8626 | 17.8987 | 45.4358 | 48.2739 | 44.4179 | 21.2942 |  |  | 0.33076 | -0.3076 | -36.455 | -0.005958 | 0.24655 | -197.8611 | 15.6659 | -0.41697 | -0.10655 | 0.055289 | 0.07737 | 8.8288 | 9.0582 | 1.9782 | 21.8358 | 22.0608 | 22.2553 | 22.3258 | 22.1639 | 21.513 | 20.3542 | 22.244 | 22.4078 | 22.4505 | 22.3992 | 22.0479 | 21.2969 | 22.3145 | 17.1901 | 17.0464 | 15.9989 | 16.0518 | 16.1322 | 17.1118 | 16.7545 | 22.4061 | 22.1763 | 21.7421 | 22.1071 | 21.8307 | 21.3509 | 21.9802 | 21.5707 | 20.9659 | 20.1579 | 20.5175 | 20.0348 | 19.7818 | 0.048966 | -0.16906 | 20.6655 | 22.094 | 22.4154 | 20.1093 | 21.716 | 22.1705 | 21.9837 | 21.7537 | 21.3321 | 21.8478 | 21.5232 | 21.1301 | 20.6014 | 20.602 | 20.6142 | 20.6469 | 20.0613 |  | 20.2431 | 19.7847 | 20.1434 | 19.7636 | 20.1201 | 20.3795 |  | 20.485 |  |  | 20.1397 | 20.3686 | 20.6186 | [5 empty] | 21.9767 | 20.3811 | 21.7278 | 22.1274 | 19.6219 | 21.2841 | 21.9351 | 19.2835 | 19.8912 | 21.1632 |  | 19.7806 | 20.9767 | 18.7908 | 19.6963 | 20.8649 | 19.342 | 20.1902 | 19.0462 | 20.2862 | 19.2118 | 20.4363 | 18.7913 | 20.3229 | 21.0835 | 19.2872 | 19.7626 | 21.0645 | 18.997 | 19.8208 | 20.8929 | 18.9721 | 20.3526 | 19.3227 | 20.0866 | 19.0432 | 20.3516 | -0.11681 | 20.9497 | 0.047178 | 0.01235 | -27.0284 | 0.4953 | -1.16 | -0.16 | 0.68682 | -0.65811 | -7.1645 | -0.091592 | 0.5897 | -16.7054 | 4.7006 | 0.42518 | 0.42952 | 0.42933 | 0.39378 | 0.48446 | 0.44323 | 0.43009
42838.4107 | -825 | 22.9148 | 22.884 | 22.8821 | 22.8173 | 22.4634 | 21.8172 | 22.7662 | 21.8856 | 22.4168 | 22.4303 | 22.4114 | 22.1074 | 21.3303 | 22.2762 | 21.6035 | 21.7825 | 21.9257 | 21.1166 | 21.2142 | 21.4372 | 20.5133 | 20.6612 | 20.961 | 21.9333 | 21.7031 | 21.334 | 20.4877 | 20.5907 | 20.5205 | 22.0663 | 21.6777 | 21.2075 | 22.0234 | 21.7677 | 21.3887 | 19.9667 | 20.5729 |  | 20.5904 | 20.3104 | 20.4066 | 19.0767 |  | 16.7745 | 16.773 | 16.5229 | 16.7416 | 16.8045 | 17.2695 | 17.7536 | 15.5401 | 16.6711 | 15.9027 | 16.8645 | 17.8925 | 45.4103 | 48.2402 | 44.4063 | 21.2924 |  |  | 0.48321 | -0.257 | -36.4011 | -0.036186 | 0.25444 | -197.8381 | 15.9583 | -0.52211 | -0.40973 | 0.16438 | -0.07019 | 8.829 | 9.0587 | 1.9787 | 21.8366 | 22.0643 | 22.2531 | 22.3215 | 22.162 | 21.5133 | 20.3578 | 22.2447 | 22.4087 | 22.446 | 22.3955 | 22.0491 | 21.2992 | 22.3151 | 17.1551 | 17.0795 | 15.9773 | 16.0556 | 16.1329 | 17.1144 | 16.7494 | 22.3995 | 22.1766 | 21.7418 | 22.1039 | 21.8331 | 21.3511 | 21.985 | 21.5739 | 20.963 | 20.163 | 20.5098 | 20.0302 | 19.7779 | 0.060762 | -0.11884 | 20.6673 | 22.0866 | 22.4133 | 20.105 | 21.7099 | 22.1741 | 21.9789 | 21.7615 | 21.338 | 21.851 | 21.5208 | 21.1265 | 20.5981 | 20.6129 | 20.6168 | 20.6481 | 20.0301 |  | 20.2443 | 19.76 | 20.1453 | 19.768 | 20.1191 | 20.3871 |  | 20.4878 |  |  | 20.1356 | 20.3668 | 20.6202 | [5 empty] | 21.9771 | 20.3871 | 21.7328 | 22.1301 | 19.6229 | 21.2899 | 21.935 | 19.2906 | 19.8983 | 21.1657 |  | 19.7928 | 20.981 | 18.7937 | 19.6945 | 20.8674 | 19.344 | 20.1912 | 19.046 | 20.2915 | 19.2097 | 20.449 | 18.793 | 20.3205 | 21.0879 | 19.2909 | 19.7689 | 21.067 | 18.9951 | 19.8279 | 20.8932 | 18.9829 | 20.3574 | 19.3171 | 20.0851 | 19.0473 | 20.3505 | -0.19083 | 20.9503 | 0.045783 | 0.012335 | -27.1236 | 0.51868 | -1.18 | -0.16 | 0.83017 | -0.60155 | -7.1592 | -0.22572 | 0.59906 | -16.7046 | 4.7443 | 0.42608 | 0.43027 | 0.42917 | 0.39797 | 0.48627 | 0.44327 | 0.43037
42838.4107 | -824 | 22.9147 | 22.8838 | 22.8759 | 22.8139 | 22.4626 | 21.8171 | 22.7602 | 21.8838 | 22.402 | 22.4334 | 22.4069 | 22.1053 | 21.3224 | 22.2818 | 21.5987 | 21.787 | 21.9328 | 21.1165 | 21.2114 | 21.4372 | 20.5195 | 20.662 | 20.9665 | 21.9346 | 21.7071 | 21.3429 | 20.489 | 20.5933 | 20.5334 | 22.074 | 21.6882 | 21.2164 | 22.02 | 21.771 | 21.3885 | 19.9779 | 20.5841 |  | 20.5922 | 20.3172 | 20.4166 | 19.0866 |  | 16.7602 | 16.7564 | 16.5099 | 16.7276 | 16.7987 | 17.2542 | 17.7663 | 15.5912 | 16.6723 | 15.8959 | 16.8551 | 17.8918 | 45.3836 | 48.2024 | 44.3795 | 21.291 |  |  | 0.27293 | -0.15252 | -35.8189 | 0.18723 | 0.10198 | -197.8394 | 15.5135 | -0.30986 | -0.33987 | -0.014575 | -0.028353 | 8.8291 | 9.059 | 1.9789 | 21.8335 | 22.0618 | 22.2603 | 22.3313 | 22.1678 | 21.5108 | 20.3524 | 22.2484 | 22.4083 | 22.4498 | 22.4069 | 22.0464 | 21.2979 | 22.3119 | 17.1383 | 17.0784 | 15.9546 | 16.0466 | 16.1411 | 17.1171 | 16.7447 | 22.4005 | 22.1828 | 21.7542 | 22.1084 | 21.8403 | 21.3642 | 21.9876 | 21.581 | 20.9685 | 20.165 | 20.5118 | 20.031 | 19.7877 | 0.047 | -0.11637 | 20.6659 | 22.0831 | 22.4103 | 20.1033 | 21.714 | 22.1637 | 21.9765 | 21.7475 | 21.3311 | 21.8455 | 21.5112 | 21.1152 | 20.58 | 20.6068 | 20.6069 | 20.642 | 20.0067 |  | 20.2438 | 19.7531 | 20.1485 | 19.776 | 20.1225 | 20.3797 |  | 20.4883 |  |  | 20.1257 | 20.3541 | 20.6177 | [5 empty] | 21.9863 | 20.3922 | 21.7412 | 22.1392 | 19.6231 | 21.2986 | 21.9435 | 19.284 | 19.9015 | 21.1667 |  | 19.7847 | 20.9804 | 18.791 | 19.6928 | 20.862 | 19.3342 | 20.1853 | 19.0475 | 20.2809 | 19.2068 | 20.4449 | 18.7989 | 20.3154 | 21.0839 | 19.2918 | 19.7678 | 21.0628 | 18.9967 | 19.8289 | 20.891 | 18.9883 | 20.3614 | 19.32 | 20.0886 | 19.0486 | 20.3599 | -0.2372 | 20.9491 | 0.045341 | 0.011856 | -27.0479 | 0.54184 | -1.13 | -0.18 | 0.62393 | -0.4634 | -7.1015 | 0.51344 | 0.37926 | -16.7042 | 4.6776 | 0.42672 | 0.43057 | 0.42906 | 0.40015 | 0.48824 | 0.44337 | 0.43016
42838.4108 | -823 | 22.9132 | 22.8822 | 22.8732 | 22.8115 | 22.461 | 21.8113 | 22.7535 | 21.8843 | 22.3983 | 22.4255 | 22.4057 | 22.1061 | 21.3236 | 22.2754 | 21.617 | 21.7909 | 21.9265 | 21.1228 | 21.2143 | 21.4433 | 20.5202 | 20.6649 | 20.9595 | 21.9442 | 21.7086 | 21.3411 | 20.4904 | 20.6091 | 20.5378 | 22.0673 | 21.6812 | 21.2123 | 22.0225 | 21.7644 | 21.3844 | 19.9742 | 20.5869 |  | 20.5921 | 20.3194 | 20.4079 | 19.0883 |  | 16.7413 | 16.7317 | 16.4929 | 16.7126 | 16.7857 | 17.2417 | 17.7838 | 15.6137 | 16.6705 | 15.8646 | 16.8597 | 17.895 | 45.3473 | 48.1621 | 44.361 | 21.29 |  |  | 0.39056 | 0.063019 | -34.9029 | 0.32194 | 0.32672 | -197.8834 | 16.6299 | -0.28358 | -0.29239 | -0.042268 | -0.097619 | 8.8291 | 9.0588 | 1.9786 | 21.8345 | 22.0606 | 22.258 | 22.331 | 22.1674 | 21.5263 | 20.3592 | 22.2457 | 22.4134 | 22.4516 | 22.4018 | 22.0546 | 21.3 | 22.3203 | 17.1063 | 17.0588 | 15.9447 | 16.028 | 16.158 | 17.1216 | 16.7417 | 22.4016 | 22.1813 | 21.7498 | 22.1048 | 21.8375 | 21.3524 | 21.9772 | 21.578 | 20.9613 | 20.1568 | 20.4979 | 20.0247 | 19.7911 | -0.083739 | -0.19587 | 20.6789 | 22.0944 | 22.4107 | 20.1155 | 21.7131 | 22.1642 | 21.9915 | 21.7529 | 21.329 | 21.8455 | 21.5196 | 21.1219 | 20.5792 | 20.6144 | 20.6108 | 20.6486 | 19.9508 |  | 20.2416 | 19.7414 | 20.1469 | 19.7806 | 20.1151 | 20.3752 |  | 20.4897 |  |  | 20.1105 | 20.3186 | 20.6093 | [5 empty] | 21.9858 | 20.3869 | 21.7348 | 22.1347 | 19.6148 | 21.2855 | 21.9323 | 19.2777 | 19.9111 | 21.1632 |  | 19.7743 | 20.9858 | 18.7878 | 19.6858 | 20.8604 | 19.3314 | 20.1871 | 19.0469 | 20.2814 | 19.2058 | 20.4496 | 18.7923 | 20.3091 | 21.0778 | 19.2864 | 19.758 | 21.0581 | 18.997 | 19.8229 | 20.8855 | 18.9842 | 20.3509 | 19.3161 | 20.0774 | 19.0442 | 20.354 | -0.15224 | 20.9508 | 0.045206 | 0.011972 | -26.9771 | 0.5648 | -1.19 | -0.17 | 0.74637 | 0.29786 | -7.0098 | 0.67323 | 0.67881 | -16.7057 | 4.8429 | 0.4282 | 0.43084 | 0.42869 | 0.40424 | 0.48899 | 0.4432 | 0.42979
42838.4108 | -822 | 22.9127 | 22.8831 | 22.8788 | 22.8168 | 22.4628 | 21.814 | 22.758 | 21.8851 | 22.4048 | 22.4177 | 22.4067 | 22.1017 | 21.3294 | 22.2779 | 21.6159 | 21.785 | 21.9261 | 21.1182 | 21.2169 | 21.4373 | 20.5183 | 20.6647 | 20.9687 | 21.9379 | 21.7057 | 21.3326 | 20.4867 | 20.5963 | 20.5428 | 22.0633 | 21.6803 | 21.2085 | 22.0304 | 21.7697 | 21.3922 | 19.9695 | 20.5928 |  | 20.5952 | 20.3215 | 20.4118 | 19.0807 |  | 16.7367 | 16.7236 | 16.4944 | 16.7034 | 16.7716 | 17.229 | 17.7663 | 15.6067 | 16.6652 | 15.8327 | 16.8522 | 17.8971 | 45.3277 | 48.1317 | 44.3616 | 21.2898 |  |  | 0.51344 | -0.19917 | -34.8818 | -0.09467 | 0.30766 | -197.8466 | 15.9793 | -0.44194 | 0.0074882 | 0.016476 | -0.038074 | 8.8297 | 9.0594 | 1.9782 | 21.8428 | 22.0663 | 22.2552 | 22.3278 | 22.1594 | 21.5208 | 20.3561 | 22.2414 | 22.4151 | 22.4395 | 22.4073 | 22.0461 | 21.3002 | 22.3115 | 17.0889 | 17.0748 | 15.9529 | 16.0281 | 16.1684 | 17.1195 | 16.7386 | 22.4113 | 22.1817 | 21.7579 | 22.1171 | 21.8444 | 21.352 | 21.983 | 21.5858 | 20.9775 | 20.1628 | 20.4997 | 20.0225 | 19.8061 | -0.23335 | -0.10439 | 20.6788 | 22.0909 | 22.4062 | 20.1221 | 21.7137 | 22.1678 | 21.9813 | 21.7555 | 21.3432 | 21.8445 | 21.5246 | 21.1204 | 20.5842 | 20.6045 | 20.6205 | 20.6452 | 19.9508 |  | 20.2407 | 19.7471 | 20.1495 | 19.7968 | 20.1219 | 20.3872 |  | 20.494 |  |  | 20.0904 | 20.29 | 20.5968 | [5 empty] | 21.9881 | 20.3819 | 21.7345 | 22.1334 | 19.6091 | 21.2753 | 21.9296 | 19.2792 | 19.9117 | 21.1702 |  | 19.7722 | 20.9922 | 18.7882 | 19.691 | 20.8726 | 19.3452 | 20.1962 | 19.0516 | 20.2843 | 19.208 | 20.4581 | 18.7891 | 20.3111 | 21.0834 | 19.2856 | 19.7612 | 21.0585 | 18.9978 | 19.8261 | 20.8921 | 18.9828 | 20.3491 | 19.3138 | 20.0775 | 19.0456 | 20.3506 | -0.29471 | 20.9497 | 0.045193 | 0.011769 | -27.0155 | 0.58752 | -1.15 | -0.11 | 0.85577 | -0.52953 | -7.0076 | -0.36507 | 0.6587 | -16.7037 | 4.7471 | 0.42817 | 0.43077 | 0.42847 | 0.40592 | 0.48771 | 0.44325 | 0.42958
42838.4108 | -821 | 22.9178 | 22.8922 | 22.8887 | 22.8249 | 22.4768 | 21.8257 | 22.7663 | 21.8861 | 22.4125 | 22.4303 | 22.4203 | 22.1108 | 21.34 | 22.2836 | 21.609 | 21.7806 | 21.917 | 21.1066 | 21.2133 | 21.4278 | 20.511 | 20.6593 | 20.9561 | 21.9328 | 21.7057 | 21.336 | 20.4807 | 20.5886 | 20.5417 | 22.0675 | 21.6734 | 21.2052 | 22.0239 | 21.7672 | 21.3829 | 19.9671 | 20.5878 |  | 20.5948 | 20.3181 | 20.4132 | 19.0775 |  | 16.7381 | 16.7237 | 16.4966 | 16.7048 | 16.7674 | 17.2201 | 17.7343 | 15.6189 | 16.6686 | 15.8211 | 16.8675 | 17.893 | 45.2772 | 48.1033 | 44.3507 | 21.2931 |  |  | 0.38596 | -0.60198 | -34.4573 | 0.39291 | 0.1585 | -197.8453 | 16.5136 | -0.50897 | -0.14761 | -0.14927 | -0.086162 | 8.8286 | 9.0586 | 1.9787 | 21.8411 | 22.0574 | 22.2551 | 22.3266 | 22.1695 | 21.5163 | 20.3516 | 22.2397 | 22.4074 | 22.4414 | 22.4042 | 22.0478 | 21.2948 | 22.3106 | 17.0807 | 17.0457 | 15.9717 | 16.0205 | 16.1699 | 17.1155 | 16.739 | 22.4084 | 22.1748 | 21.7459 | 22.1154 | 21.8358 | 21.354 | 21.9755 | 21.5768 | 20.9662 | 20.1611 | 20.4866 | 20.0096 | 19.7988 | -0.0060824 | 0.2045 | 20.6879 | 22.0956 | 22.4137 | 20.1198 | 21.7258 | 22.165 | 21.9851 | 21.7494 | 21.3341 | 21.8508 | 21.5247 | 21.1273 | 20.579 | 20.6078 | 20.6216 | 20.6457 | 19.9562 |  | 20.2409 | 19.7738 | 20.146 | 19.7983 | 20.1192 | 20.3902 |  | 20.4885 |  |  | 20.0619 | 20.2799 | 20.5807 | [5 empty] | 21.9807 | 20.3879 | 21.718 | 22.132 | 19.6172 | 21.2834 | 21.9222 | 19.2839 | 19.9213 | 21.1751 |  | 19.7714 | 20.9861 | 18.7929 | 19.6959 | 20.8709 | 19.3452 | 20.1871 | 19.0502 | 20.2809 | 19.2135 | 20.4627 | 18.7927 | 20.3067 | 21.0869 | 19.2959 | 19.7635 | 21.057 | 19.004 | 19.8286 | 20.8906 | 18.9883 | 20.3512 | 19.3188 | 20.075 | 19.0532 | 20.3529 | -0.19083 | 20.9501 | 0.045218 | 0.011282 | -27.0175 | 0.61004 | -0.81 | -0.03 | 0.74196 | -0.92059 | -6.9649 | 0.74373 | 0.47277 | -16.7034 | 4.8257 | 0.42802 | 0.42991 | 0.42833 | 0.40638 | 0.48567 | 0.44326 | 0.42972
42838.4108 | -820 | 22.9197 | 22.889 | 22.8865 | 22.8145 | 22.4709 | 21.8214 | 22.765 | 21.8944 | 22.4059 | 22.4181 | 22.4152 | 22.1083 | 21.3302 | 22.2809 | 21.6153 | 21.79 | 21.9364 | 21.1262 | 21.2231 | 21.4397 | 20.5231 | 20.672 | 20.9696 | 21.9363 | 21.7036 | 21.3474 | 20.4982 | 20.606 | 20.5456 | 22.0666 | 21.6808 | 21.2136 | 22.0307 | 21.7749 | 21.391 | 19.9717 | 20.6021 |  | 20.5881 | 20.3154 | 20.4071 | 19.0844 |  | 16.7313 | 16.7135 | 16.4853 | 16.6912 | 16.7473 | 17.2063 | 17.7018 | 15.6088 | 16.6684 | 15.8255 | 16.8616 | 17.891 | 45.2345 | 48.0643 | 44.338 | 21.2846 |  |  | 0.53249 | -0.18275 | -33.335 | 0.81412 | -0.013668 | -197.8545 | 16.8592 | -0.69362 | 0.01391 | 0.16313 | -0.11411 | 8.8287 | 9.0584 | 1.979 | 21.8373 | 22.0621 | 22.2575 | 22.3215 | 22.1737 | 21.5206 | 20.3524 | 22.2427 | 22.409 | 22.4442 | 22.4025 | 22.0483 | 21.2952 | 22.3102 | 17.0686 | 17.0178 | 15.9705 | 16.0099 | 16.1531 | 17.1127 | 16.7365 | 22.4039 | 22.1714 | 21.7498 | 22.1149 | 21.8356 | 21.357 | 21.9807 | 21.5743 | 20.966 | 20.1604 | 20.491 | 20.0125 | 19.7924 | 0.052898 | -0.03858 | 20.668 | 22.092 | 22.4142 | 20.1136 | 21.7189 | 22.1682 | 21.983 | 21.764 | 21.3257 | 21.8412 | 21.5144 | 21.1252 | 20.5716 | 20.6068 | 20.6144 | 20.6398 | 19.9513 |  | 20.2357 | 19.8059 | 20.1488 | 19.8028 | 20.1239 | 20.3881 |  | 20.492 |  |  | 20.0495 | 20.2737 | 20.58 | [5 empty] | 21.9827 | 20.3844 | 21.7286 | 22.1468 | 19.6277 | 21.2816 | 21.9344 | 19.2895 | 19.9213 | 21.1643 |  | 19.7653 | 20.9781 | 18.7997 | 19.6992 | 20.8701 | 19.3519 | 20.1866 | 19.0395 | 20.276 | 19.2152 | 20.4711 | 18.7939 | 20.2912 | 21.0806 | 19.2892 | 19.7702 | 21.0641 | 19.0002 | 19.824 | 20.8918 | 18.9723 | 20.3449 | 19.311 | 20.0739 | 19.0424 | 20.3621 | -0.17172 | 20.9508 | 0.046005 | 0.011994 | -27.0309 | 0.63222 | -0.71 | -0.14 | 0.87151 | -0.50721 | -6.8504 | 1.0706 | -0.13883 | -16.7034 | 4.8759 | 0.42799 | 0.42911 | 0.42836 | 0.40738 | 0.48551 | 0.44323 | 0.42988
42838.4108 | -819 | 22.9176 | 22.8917 | 22.8795 | 22.8081 | 22.4591 | 21.8092 | 22.762 | 21.8841 | 22.4135 | 22.425 | 22.4062 | 22.0985 | 21.3243 | 22.2778 | 21.6004 | 21.7787 | 21.9208 | 21.1075 | 21.2115 | 21.4305 | 20.5044 | 20.6594 | 20.9543 | 21.9282 | 21.6963 | 21.3254 | 20.484 | 20.5912 | 20.5365 | 22.0639 | 21.6768 | 21.2099 | 22.0314 | 21.7619 | 21.3815 | 19.9686 | 20.5928 |  | 20.5905 | 20.3149 | 20.4098 | 19.0909 |  | 16.7132 | 16.6991 | 16.4634 | 16.6699 | 16.7454 | 17.1953 | 17.6741 | 15.6095 | 16.6667 | 15.8294 | 16.8561 | 17.8993 | 45.2107 | 48.0432 | 44.3231 | 21.2915 |  |  | 0.3301 | -0.4377 | -32.1804 | 0.42379 | 0.09804 | -197.9058 | 17.3133 | -0.70413 | -0.21689 | 0.14991 | 0.045948 | 8.8284 | 9.0583 | 1.9784 | 21.8301 | 22.0556 | 22.2463 | 22.3169 | 22.1649 | 21.5132 | 20.3453 | 22.2346 | 22.4108 | 22.4342 | 22.3955 | 22.047 | 21.2863 | 22.3111 | 17.0695 | 16.9962 | 15.9683 | 15.9998 | 16.1461 | 17.1188 | 16.7412 | 22.4044 | 22.1729 | 21.7473 | 22.1056 | 21.8344 | 21.3458 | 21.9766 | 21.57 | 20.9628 | 20.1545 | 20.4879 | 20.0013 | 19.7692 | 0.088482 | 0.19137 | 20.6666 | 22.0853 | 22.4149 | 20.1188 | 21.7217 | 22.166 | 21.9816 | 21.7573 | 21.3346 | 21.8422 | 21.5149 | 21.1269 | 20.5631 | 20.6015 | 20.6142 | 20.6477 | 19.9704 |  | 20.2392 | 19.8279 | 20.1448 | 19.8047 | 20.1318 | 20.3911 |  | 20.4936 |  |  | 20.0569 | 20.2508 | 20.5577 | [5 empty] | 21.9773 | 20.3874 | 21.7309 | 22.1267 | 19.6161 | 21.2834 | 21.9297 | 19.284 | 19.9117 | 21.1546 |  | 19.754 | 20.9687 | 18.7878 | 19.6842 | 20.8608 | 19.3503 | 20.188 | 19.0258 | 20.2608 | 19.1996 | 20.4577 | 18.7909 | 20.2809 | 21.073 | 19.2919 | 19.7611 | 21.0477 | 18.9944 | 19.8148 | 20.8804 | 18.9551 | 20.3385 | 19.3035 | 20.0697 | 19.048 | 20.3409 | -0.32476 | 20.9502 | 0.04676 | 0.01301 | -27.1518 | 0.65414 | -1.26 | -0.18 | 0.68617 | -0.78495 | -6.7305 | 0.77238 | 0.37181 | -16.7053 | 4.941 | 0.42757 | 0.42837 | 0.42858 | 0.408 | 0.48631 | 0.44294 | 0.43032
42838.4108 | -818 | 22.9147 | 22.8848 | 22.8736 | 22.8039 | 22.4599 | 21.8112 | 22.7553 | 21.8794 | 22.403 | 22.4226 | 22.4042 | 22.0981 | 21.3225 | 22.2703 | 21.6043 | 21.7817 | 21.9236 | 21.1202 | 21.2161 | 21.435 | 20.5199 | 20.6663 | 20.9599 | 21.9352 | 21.6996 | 21.3333 | 20.4817 | 20.5931 | 20.5446 | 22.074 | 21.6774 | 21.2118 | 22.0233 | 21.7614 | 21.382 | 19.9694 | 20.5928 |  | 20.5907 | 20.3074 | 20.4132 | 19.098 |  | 16.7419 | 16.7302 | 16.469 | 16.6946 | 16.7742 | 17.2038 | 17.6721 | 15.6432 | 16.6607 | 15.8444 | 16.8594 | 17.8991 | 45.1875 | 48.0121 | 44.2983 | 21.2947 |  |  | 0.53052 | 0.054475 | -31.2059 | 0.43825 | 0.16047 | -197.8407 | 17.5952 | -0.4886 | -0.39494 | 0.1327 | -0.16168 | 8.8292 | 9.0591 | 1.978 | 21.8278 | 22.0564 | 22.2447 | 22.3142 | 22.1621 | 21.5125 | 20.3423 | 22.235 | 22.4005 | 22.4351 | 22.3876 | 22.0435 | 21.2862 | 22.31 | 17.0563 | 16.9205 | 15.9643 | 15.975 | 16.1289 | 17.1126 | 16.7377 | 22.4093 | 22.1815 | 21.7523 | 22.1149 | 21.8414 | 21.3514 | 21.9837 | 21.5854 | 20.9747 | 20.1591 | 20.4991 | 20.0106 | 19.7605 | -0.080594 | 0.082388 | 20.6683 | 22.0936 | 22.418 | 20.1259 | 21.7146 | 22.174 | 21.9811 | 21.7494 | 21.3385 | 21.8421 | 21.5223 | 21.1229 | 20.5568 | 20.6126 | 20.6187 | 20.6455 | 19.9649 |  | 20.236 | 19.8429 | 20.1435 | 19.7882 | 20.1247 | 20.3919 |  | 20.4873 |  |  | 20.0495 | 20.2438 | 20.5542 | [5 empty] | 21.9823 | 20.3914 | 21.7336 | 22.1306 | 19.6273 | 21.2815 | 21.9352 | 19.2969 | 19.9298 | 21.1694 |  | 19.773 | 20.9829 | 18.7984 | 19.6988 | 20.877 | 19.3595 | 20.191 | 19.0226 | 20.2761 | 19.2205 | 20.474 | 18.8112 | 20.2886 | 21.0812 | 19.3014 | 19.7699 | 21.0672 | 19.0076 | 19.8257 | 20.8815 | 18.9788 | 20.3485 | 19.3108 | 20.0743 | 19.0494 | 20.3572 | -0.19138 | 20.9503 | 0.046693 | 0.01415 | -27.0565 | 0.67585 | -1.3 | -0.14 | 0.86989 | 0.27693 | -6.6282 | 0.78549 | 0.47569 | -16.7028 | 4.9811 | 0.42762 | 0.42791 | 0.4288 | 0.40874 | 0.48634 | 0.44277 | 0.43072
42838.4108 | -817 | 22.9175 | 22.8945 | 22.8804 | 22.8115 | 22.4655 | 21.8107 | 22.7546 | 21.8821 | 22.41 | 22.4257 | 22.4104 | 22.1005 | 21.3279 | 22.2774 | 21.6087 | 21.7869 | 21.9246 | 21.1174 | 21.2181 | 21.4363 | 20.5195 | 20.6626 | 20.9667 | 21.9355 | 21.7016 | 21.3299 | 20.4885 | 20.5933 | 20.5425 | 22.0683 | 21.6817 | 21.2074 | 22.0221 | 21.7724 | 21.3829 | 19.967 | 20.5874 |  | 20.5957 | 20.3157 | 20.4122 | 19.1007 |  | 16.7589 | 16.7605 | 16.4824 | 16.7139 | 16.8073 | 17.2344 | 17.6698 | 15.6667 | 16.6581 | 15.8516 | 16.8544 | 17.895 | 45.1743 | 47.9808 | 44.2863 | 21.2949 |  |  | 0.42013 | -0.058549 | -30.7427 | 0.10509 | 0.3254 | -197.8808 | 17.5959 | -0.32695 | -0.099542 | -0.002826 | -0.03929 | 8.8297 | 9.0595 | 1.9784 | 21.8285 | 22.0549 | 22.2518 | 22.3205 | 22.1654 | 21.5142 | 20.3497 | 22.2307 | 22.4021 | 22.4372 | 22.3963 | 22.0422 | 21.2867 | 22.3115 | 17.0671 | 16.9244 | 15.9982 | 15.9812 | 16.1253 | 17.1123 | 16.7443 | 22.4004 | 22.173 | 21.7493 | 22.1055 | 21.841 | 21.3477 | 21.9803 | 21.5696 | 20.9634 | 20.1593 | 20.4814 | 20.0053 | 19.7432 | -0.028691 | -0.14262 | 20.6775 | 22.0997 | 22.4194 | 20.1261 | 21.7252 | 22.1779 | 21.9888 | 21.7653 | 21.3352 | 21.855 | 21.5287 | 21.1264 | 20.5599 | 20.6138 | 20.6239 | 20.6453 | 19.9738 |  | 20.2457 | 19.8627 | 20.1503 | 19.7859 | 20.1319 | 20.4026 |  | 20.4954 |  |  | 20.0646 | 20.2383 | 20.5633 | [5 empty] | 21.9801 | 20.3805 | 21.7369 | 22.1325 | 19.6233 | 21.2878 | 21.933 | 19.2965 | 19.9357 | 21.167 |  | 19.7718 | 20.9826 | 18.8081 | 19.7078 | 20.8683 | 19.3543 | 20.1903 | 19.0136 | 20.2794 | 19.2126 | 20.4741 | 18.7956 | 20.2839 | 21.0812 | 19.2966 | 19.766 | 21.0544 | 19.0121 | 19.8212 | 20.8795 | 18.9828 | 20.3447 | 19.3087 | 20.0723 | 19.0434 | 20.3506 | -0.25019 | 20.9497 | 0.04727 | 0.01476 | -27.0281 | 0.69724 | -1.32 | -0.04 | 0.77411 | -0.28712 | -6.5791 | 0.38467 | 0.67743 | -16.7053 | 4.9815 | 0.4277 | 0.42759 | 0.4291 | 0.40751 | 0.48335 | 0.44261 | 0.43121
42838.4108 | -816 | 22.9114 | 22.8803 | 22.8761 | 22.8157 | 22.4544 | 21.8115 | 22.7571 | 21.8763 | 22.4072 | 22.4189 | 22.4076 | 22.0961 | 21.3209 | 22.2757 | 21.614 | 21.7899 | 21.9343 | 21.1164 | 21.2124 | 21.4436 | 20.5259 | 20.6717 | 20.9642 | 21.9403 | 21.7021 | 21.336 | 20.4854 | 20.6049 | 20.5443 | 22.0719 | 21.6757 | 21.207 | 22.028 | 21.7665 | 21.3858 | 19.9696 | 20.5941 |  | 20.5891 | 20.3154 | 20.4085 | 19.0847 |  | 16.7526 | 16.756 | 16.4894 | 16.7254 | 16.828 | 17.2585 | 17.6758 | 15.6802 | 16.6613 | 15.8601 | 16.8534 | 17.894 | 45.1559 | 47.9612 | 44.2604 | 21.2974 |  |  | 0.36821 | -0.18931 | -30.7466 | 0.32983 | 0.25838 | -197.8164 | 17.7463 | -0.39726 | -0.23615 | 0.07459 | -0.042588 | 8.8285 | 9.0583 | 1.9787 | 21.8365 | 22.0647 | 22.2532 | 22.3179 | 22.1758 | 21.5219 | 20.3477 | 22.2413 | 22.4161 | 22.4437 | 22.4048 | 22.0511 | 21.2994 | 22.317 | 17.0815 | 16.9161 | 16.0448 | 15.9821 | 16.0993 | 17.1104 | 16.7419 | 22.402 | 22.1767 | 21.7491 | 22.1071 | 21.84 | 21.3524 | 21.9777 | 21.5734 | 20.9616 | 20.1614 | 20.4799 | 20.0065 | 19.7404 | -0.06172 | -0.053035 | 20.6768 | 22.1005 | 22.4188 | 20.1252 | 21.7272 | 22.1779 | 21.9897 | 21.7656 | 21.3364 | 21.851 | 21.5248 | 21.1287 | 20.551 | 20.6118 | 20.6163 | 20.6437 | 19.9705 |  | 20.2331 | 19.8557 | 20.1416 | 19.7742 | 20.1172 | 20.3919 |  | 20.4925 |  |  | 20.0798 | 20.2489 | 20.5616 | [5 empty] | 21.9817 | 20.3886 | 21.7373 | 22.1356 | 19.6241 | 21.286 | 21.929 | 19.3007 | 19.9355 | 21.1689 |  | 19.7655 | 20.9843 | 18.802 | 19.7073 | 20.8666 | 19.3538 | 20.1838 | 19.006 | 20.2752 | 19.2191 | 20.4709 | 18.7881 | 20.2752 | 21.083 | 19.298 | 19.7671 | 21.0504 | 19.0019 | 19.8203 | 20.8712 | 18.9774 | 20.3359 | 19.3012 | 20.0628 | 19.0399 | 20.3443 | -0.092326 | 20.9504 | 0.047098 | 0.01484 | -27.0345 | 0.71819 | -1.39 | -0.02 | 0.72471 | -0.51628 | -6.5795 | 0.68146 | 0.60367 | -16.7033 | 5.0029 | 0.42737 | 0.42749 | 0.42894 | 0.40569 | 0.47789 | 0.44315 | 0.43136
42838.4108 | -815 | 22.9098 | 22.881 | 22.8761 | 22.8076 | 22.4522 | 21.8101 | 22.7568 | 21.88 | 22.4096 | 22.4212 | 22.4056 | 22.0997 | 21.3183 | 22.2744 | 21.6059 | 21.7814 | 21.9259 | 21.1106 | 21.2148 | 21.4343 | 20.5146 | 20.6651 | 20.9646 | 21.9364 | 21.7023 | 21.332 | 20.4748 | 20.5939 | 20.5343 | 22.0657 | 21.677 | 21.2088 | 22.0197 | 21.7638 | 21.3855 | 19.9662 | 20.586 |  | 20.5883 | 20.3085 | 20.4102 | 19.0758 |  | 16.747 | 16.7454 | 16.4831 | 16.7108 | 16.8059 | 17.2363 | 17.6603 | 15.679 | 16.6594 | 15.8625 | 16.8608 | 17.8923 | 45.1411 | 47.9341 | 44.2376 | 21.2737 |  |  | 0.50818 | -0.085489 | -30.4082 | 0.17935 | 0.24326 | -197.8388 | 17.7352 | -0.50043 | -0.27838 | -0.11402 | -0.071232 | 8.8285 | 9.0582 | 1.9785 | 21.8325 | 22.069 | 22.2537 | 22.3258 | 22.171 | 21.5202 | 20.3484 | 22.2419 | 22.412 | 22.4428 | 22.3991 | 22.0476 | 21.2923 | 22.3204 | 17.0929 | 16.9253 | 16.0478 | 15.9818 | 16.0933 | 17.105 | 16.7338 | 22.4021 | 22.1778 | 21.7493 | 22.1075 | 21.8384 | 21.3489 | 21.9824 | 21.5774 | 20.9644 | 20.1621 | 20.4873 | 20.0171 | 19.747 | -0.044813 | -0.17343 | 20.6782 | 22.0921 | 22.4107 | 20.1279 | 21.7143 | 22.1777 | 21.9834 | 21.7588 | 21.3365 | 21.8527 | 21.5213 | 21.1218 | 20.5451 | 20.6046 | 20.6222 | 20.6429 | 19.9878 |  | 20.2373 | 19.8527 | 20.1417 | 19.7756 | 20.1197 | 20.3889 |  | 20.4862 |  |  | 20.0822 | 20.2508 | 20.5507 | [5 empty] | 21.9789 | 20.3899 | 21.7292 | 22.1267 | 19.6194 | 21.2773 | 21.9272 | 19.3004 | 19.9321 | 21.1638 |  | 19.762 | 20.9793 | 18.8025 | 19.7041 | 20.8614 | 19.3531 | 20.1809 | 19.0105 | 20.2662 | 19.2139 | 20.4734 | 18.7911 | 20.2799 | 21.0892 | 19.3049 | 19.7782 | 21.0622 | 19.0044 | 19.8325 | 20.8798 | 18.9797 | 20.3467 | 19.3123 | 20.0762 | 19.0497 | 20.3491 | -0.14798 | 20.9506 | 0.047184 | 0.014179 | -27.0739 | 0.73892 | -1.19 | -0.21 | 0.85137 | -0.34693 | -6.5431 | 0.5025 | 0.58573 | -16.7036 | 5.0012 | 0.42703 | 0.42758 | 0.42898 | 0.40379 | 0.47661 | 0.44328 | 0.43119
42838.4109 | -814 | 22.9215 | 22.8886 | 22.8775 | 22.8111 | 22.4591 | 21.8237 | 22.7672 | 21.8858 | 22.4107 | 22.425 | 22.4091 | 22.1056 | 21.3227 | 22.2812 | 21.6033 | 21.7806 | 21.9258 | 21.1136 | 21.2149 | 21.4365 | 20.5135 | 20.6678 | 20.9645 | 21.9376 | 21.6973 | 21.3362 | 20.4795 | 20.5943 | 20.5352 | 22.066 | 21.6718 | 21.2095 | 22.0203 | 21.7624 | 21.3837 | 19.9673 | 20.5783 |  | 20.5905 | 20.3105 | 20.4088 | 19.0739 |  | 16.7485 | 16.7372 | 16.4856 | 16.7044 | 16.7976 | 17.2304 | 17.6577 | 15.6659 | 16.6644 | 15.8732 | 16.8756 | 17.8934 | 45.1552 | 47.9134 | 44.2269 | 21.2694 |  |  | 0.47204 | -0.080233 | -30.7256 | 0.49937 | 0.050728 | -197.8631 | 17.933 | -0.46823 | 0.073458 | -0.19416 | -0.026617 | 8.8294 | 9.0592 | 1.9781 | 21.8403 | 22.0642 | 22.2668 | 22.3217 | 22.1723 | 21.5248 | 20.3551 | 22.2412 | 22.4186 | 22.445 | 22.4069 | 22.049 | 21.3066 | 22.321 | 17.0867 | 16.9694 | 16.0467 | 15.9852 | 16.094 | 17.1015 | 16.7337 | 22.4045 | 22.1855 | 21.7544 | 22.1073 | 21.8403 | 21.3564 | 21.9866 | 21.578 | 20.9668 | 20.1571 | 20.4899 | 20.0165 | 19.7438 | 0.066463 | -0.074908 | 20.6754 | 22.084 | 22.4112 | 20.128 | 21.717 | 22.1734 | 21.9835 | 21.7562 | 21.3394 | 21.8516 | 21.5238 | 21.1246 | 20.541 | 20.6044 | 20.6182 | 20.64 | 19.9893 |  | 20.2335 | 19.8202 | 20.147 | 19.767 | 20.1207 | 20.3847 |  | 20.4875 |  |  | 20.0831 | 20.2594 | 20.5446 | [5 empty] | 21.977 | 20.3871 | 21.7288 | 22.1315 | 19.6176 | 21.276 | 21.9303 | 19.317 | 19.936 | 21.1731 |  | 19.7567 | 20.9864 | 18.8123 | 19.7172 | 20.8705 | 19.3571 | 20.1894 | 19.0202 | 20.2689 | 19.221 | 20.4811 | 18.7849 | 20.2766 | 21.0963 | 19.3096 | 19.7785 | 21.0652 | 19.0017 | 19.8343 | 20.8826 | 18.9888 | 20.3416 | 19.3092 | 20.0759 | 19.0549 | 20.3498 | -0.024433 | 20.9511 | 0.047731 | 0.013213 | -27.0651 | 0.75956 | -1.25 | -0.11 | 0.82053 | -0.33609 | -6.5771 | 0.83848 | 0.26747 | -16.7045 | 5.0289 | 0.42686 | 0.42865 | 0.42925 | 0.40407 | 0.47672 | 0.44337 | 0.43112
42838.4109 | -813 | 22.9154 | 22.8923 | 22.8768 | 22.8135 | 22.458 | 21.8141 | 22.7582 | 21.8793 | 22.4074 | 22.4256 | 22.4115 | 22.1001 | 21.3269 | 22.2701 | 21.6107 | 21.7819 | 21.9254 | 21.1197 | 21.2146 | 21.4371 | 20.512 | 20.6659 | 20.9578 | 21.9334 | 21.7035 | 21.3335 | 20.4829 | 20.597 | 20.5291 | 22.0745 | 21.6772 | 21.2078 | 22.0189 | 21.7652 | 21.3839 | 19.9717 | 20.5871 |  | 20.5987 | 20.3183 | 20.4108 | 19.0663 |  | 16.7376 | 16.7283 | 16.4676 | 16.6846 | 16.818 | 17.2401 | 17.6838 | 15.5861 | 16.668 | 15.8079 | 16.8684 | 17.8951 | 45.1482 | 47.8902 | 44.193 | 21.2659 |  |  | 0.50424 | -0.18866 | -30.7611 | 0.30749 | 0.10921 | -197.8795 | 18.1301 | -0.64959 | -0.15072 | -0.28396 | -0.010125 | 8.8303 | 9.0601 | 1.978 | 21.8365 | 22.0662 | 22.2584 | 22.3279 | 22.1725 | 21.5214 | 20.3605 | 22.2419 | 22.4234 | 22.447 | 22.4047 | 22.0485 | 21.3033 | 22.3212 | 17.0938 | 16.9768 | 16.0355 | 15.9968 | 16.0931 | 17.1048 | 16.74 | 22.4098 | 22.1846 | 21.7508 | 22.1138 | 21.8402 | 21.3514 | 21.9787 | 21.5747 | 20.9645 | 20.1546 | 20.4907 | 20.0175 | 19.7566 | 0.10991 | -0.15898 | 20.6743 | 22.1021 | 22.418 | 20.1264 | 21.7214 | 22.1794 | 21.9843 | 21.755 | 21.3408 | 21.8533 | 21.5206 | 21.1205 | 20.5398 | 20.6126 | 20.619 | 20.6437 | 20.0055 |  | 20.2353 | 19.7674 | 20.1449 | 19.7777 | 20.128 | 20.3926 |  | 20.4902 |  |  | 20.0874 | 20.2663 | 20.5555 | [5 empty] | 21.9826 | 20.3903 | 21.7335 | 22.1326 | 19.6257 | 21.2804 | 21.9308 | 19.3196 | 19.9365 | 21.169 |  | 19.7429 | 20.9837 | 18.8202 | 19.7229 | 20.8732 | 19.3627 | 20.1929 | 19.0177 | 20.2689 | 19.2239 | 20.4828 | 18.7852 | 20.2709 | 21.0894 | 19.3105 | 19.7717 | 21.0606 | 19.0039 | 19.8247 | 20.8831 | 18.9889 | 20.3284 | 19.3041 | 20.0668 | 19.0443 | 20.344 | -0.13944 | 20.95 | 0.047866 | 0.013874 | -27.0652 | 0.77979 | -1.26 | -0.3 | 0.84805 | -0.51536 | -6.5808 | 0.65794 | 0.39246 | -16.7055 | 5.0566 | 0.42647 | 0.43005 | 0.4292 | 0.40366 | 0.4787 | 0.44372 | 0.43068
42838.4109 | -812 | 22.9195 | 22.8897 | 22.8809 | 22.8177 | 22.4691 | 21.8133 | 22.7567 | 21.8771 | 22.4165 | 22.4185 | 22.4115 | 22.1047 | 21.3261 | 22.273 | 21.609 | 21.7805 | 21.9231 | 21.1173 | 21.2154 | 21.4375 | 20.5111 | 20.6682 | 20.9553 | 21.9353 | 21.7059 | 21.3314 | 20.4853 | 20.5947 | 20.5239 | 22.066 | 21.6735 | 21.2032 | 22.0235 | 21.7597 | 21.3812 | 19.965 | 20.5913 |  | 20.5935 | 20.3128 | 20.4117 | 19.0696 |  | 16.7371 | 16.7257 | 16.4604 | 16.6816 | 16.8352 | 17.2721 | 17.7059 | 15.5095 | 16.6654 | 15.7843 | 16.8664 | 17.8918 | 45.1529 | 47.8725 | 44.1639 | 21.2655 |  |  | 0.34916 | -0.059865 | -30.8576 | 0.26215 | 0.32212 | -197.8598 | 18.0539 | -0.7751 | -0.021313 | -0.16458 | 0.039178 | 8.8295 | 9.059 | 1.9787 | 21.8322 | 22.0603 | 22.2503 | 22.3222 | 22.1655 | 21.5151 | 20.3516 | 22.24 | 22.4109 | 22.444 | 22.3955 | 22.044 | 21.2934 | 22.3121 | 17.0849 | 16.9885 | 16.0277 | 16.0034 | 16.1004 | 17.1073 | 16.7357 | 22.3971 | 22.1801 | 21.7531 | 22.1045 | 21.8409 | 21.347 | 21.9731 | 21.5709 | 20.9592 | 20.1549 | 20.4885 | 20.0165 | 19.7688 | -0.024759 | -0.12379 | 20.6782 | 22.0981 | 22.4094 | 20.1284 | 21.72 | 22.1816 | 21.9865 | 21.7583 | 21.3377 | 21.8549 | 21.5167 | 21.1303 | 20.5423 | 20.6101 | 20.624 | 20.6498 | 19.9833 |  | 20.2243 | 19.7277 | 20.1366 | 19.7792 | 20.1166 | 20.3861 |  | 20.4795 |  |  | 20.0896 | 20.2737 | 20.5535 | [5 empty] | 21.9822 | 20.3883 | 21.7318 | 22.1299 | 19.6291 | 21.2794 | 21.9288 | 19.3256 | 19.9404 | 21.1702 |  | 19.7306 | 20.9816 | 18.825 | 19.7303 | 20.8772 | 19.3649 | 20.183 | 19.0211 | 20.2718 | 19.2249 | 20.4798 | 18.794 | 20.2617 | 21.0951 | 19.3189 | 19.783 | 21.0628 | 19.006 | 19.8284 | 20.8854 | 18.996 | 20.3336 | 19.3038 | 20.0702 | 19.0425 | 20.3366 | -0.10828 | 20.9491 | 0.047756 | 0.014164 | -26.9893 | 0.79974 | -1.27 | -0.1 | 0.70568 | -0.29031 | -6.591 | 0.6075 | 0.67405 | -16.7055 | 5.0462 | 0.42672 | 0.43088 | 0.42878 | 0.40494 | 0.47906 | 0.44341 | 0.43035
42838.4109 | -811 | 22.9207 | 22.8879 | 22.8791 | 22.8156 | 22.4677 | 21.8224 | 22.7638 | 21.8801 | 22.4201 | 22.4197 | 22.4074 | 22.1008 | 21.3179 | 22.2881 | 21.6139 | 21.7815 | 21.919 | 21.1174 | 21.2139 | 21.4338 | 20.5152 | 20.668 | 20.9559 | 21.9327 | 21.7012 | 21.3326 | 20.4803 | 20.5917 | 20.5248 | 22.0743 | 21.682 | 21.2045 | 22.0193 | 21.7727 | 21.3824 | 19.9606 | 20.5896 |  | 20.5952 | 20.309 | 20.4014 | 19.0735 |  | 16.7295 | 16.7308 | 16.4467 | 16.6703 | 16.8638 | 17.3007 | 17.7193 | 15.4582 | 16.6634 | 15.7983 | 16.8576 | 17.9038 | 45.159 | 47.858 | 44.1399 | 21.2717 |  |  | 0.36033 | -0.19457 | -30.1539 | 0.33049 | 0.20646 | -197.819 | 18.6098 | -0.8073 | 0.035705 | -0.19983 | -0.12158 | 8.8277 | 9.057 | 1.9783 | 21.8347 | 22.0604 | 22.2504 | 22.3152 | 22.1709 | 21.516 | 20.3501 | 22.2384 | 22.4078 | 22.4473 | 22.3984 | 22.0425 | 21.2987 | 22.3137 | 17.0648 | 17.0091 | 16.024 | 16.0081 | 16.0867 | 17.1007 | 16.7311 | 22.3916 | 22.1736 | 21.7459 | 22.1034 | 21.8358 | 21.3491 | 21.9769 | 21.5739 | 20.961 | 20.1548 | 20.4902 | 20.0182 | 19.7722 | 0.076293 | -0.1546 | 20.6756 | 22.1001 | 22.4201 | 20.1322 | 21.72 | 22.1835 | 21.9974 | 21.765 | 21.338 | 21.8484 | 21.5179 | 21.1345 | 20.5424 | 20.6228 | 20.6218 | 20.6473 | 19.9796 |  | 20.2216 | 19.7036 | 20.1354 | 19.7824 | 20.1168 | 20.3811 |  | 20.4843 |  |  | 20.0951 | 20.2766 | 20.5528 | [5 empty] | 21.9797 | 20.3873 | 21.7278 | 22.1219 | 19.6287 | 21.279 | 21.9267 | 19.3329 | 19.9477 | 21.17 |  | 19.7235 | 20.9857 | 18.8231 | 19.729 | 20.8721 | 19.3611 | 20.1719 | 19.0263 | 20.2618 | 19.2221 | 20.473 | 18.7904 | 20.2408 | 21.0934 | 19.3175 | 19.7893 | 21.0622 | 19.0105 | 19.8228 | 20.8855 | 19.0017 | 20.3352 | 19.302 | 20.0773 | 19.0482 | 20.3335 | -0.1131 | 20.951 | 0.047676 | 0.014513 | -27.0037 | 0.81944 | -1.29 | 0.03 | 0.71689 | -0.52338 | -6.5155 | 0.68211 | 0.53967 | -16.7046 | 5.1236 | 0.42673 | 0.43151 | 0.42869 | 0.4064 | 0.47895 | 0.44316 | 0.43025
42838.4109 | -810 | 22.9135 | 22.8807 | 22.8782 | 22.8131 | 22.4617 | 21.8204 | 22.7627 | 21.8813 | 22.4089 | 22.422 | 22.4078 | 22.0967 | 21.326 | 22.2826 | 21.6088 | 21.7897 | 21.9211 | 21.1168 | 21.2074 | 21.4305 | 20.5112 | 20.6672 | 20.954 | 21.9323 | 21.7019 | 21.3301 | 20.4765 | 20.5899 | 20.5242 | 22.0721 | 21.6865 | 21.2135 | 22.0246 | 21.7681 | 21.3935 | 19.97 | 20.5885 |  | 20.5977 | 20.3142 | 20.4062 | 19.0763 |  | 16.7388 | 16.7319 | 16.4469 | 16.6742 | 16.8919 | 17.3166 | 17.7252 | 15.4398 | 16.6597 | 15.8087 | 16.8614 | 17.891 | 45.1452 | 47.8268 | 44.1054 | 21.2689 |  |  | 0.3163 | -0.013865 | -29.5428 | 0.35874 | 0.096728 | -197.865 | 18.8385 | -0.73042 | -0.011777 | -0.24745 | -0.036859 | 8.8287 | 9.0581 | 1.9781 | 21.832 | 22.0682 | 22.2589 | 22.3251 | 22.1716 | 21.5134 | 20.3522 | 22.2438 | 22.4195 | 22.4547 | 22.4028 | 22.0493 | 21.2947 | 22.3158 | 17.0629 | 17.0147 | 16.0304 | 16.0229 | 16.1073 | 17.1096 | 16.7322 | 22.3974 | 22.1812 | 21.7514 | 22.1101 | 21.8391 | 21.3614 | 21.9838 | 21.5805 | 20.9662 | 20.1611 | 20.4984 | 20.0268 | 19.7775 | 0.017903 | -0.24552 | 20.6533 | 22.089 | 22.4157 | 20.1229 | 21.7249 | 22.1762 | 21.9935 | 21.7631 | 21.3345 | 21.8418 | 21.5147 | 21.1233 | 20.5273 | 20.6129 | 20.614 | 20.6553 | 19.9785 |  | 20.2246 | 19.6621 | 20.1376 | 19.7884 | 20.1135 | 20.3817 |  | 20.4847 |  |  | 20.1076 | 20.291 | 20.5637 | [5 empty] | 21.9829 | 20.3855 | 21.7326 | 22.1282 | 19.6309 | 21.2803 | 21.9343 | 19.327 | 19.9411 | 21.1601 |  | 19.7107 | 20.9824 | 18.8205 | 19.7259 | 20.8579 | 19.3572 | 20.1732 | 19.0236 | 20.2455 | 19.2179 | 20.4542 | 18.7908 | 20.2257 | 21.091 | 19.3214 | 19.7839 | 21.0586 | 19.0092 | 19.8225 | 20.886 | 19.0014 | 20.3344 | 19.3042 | 20.0863 | 19.0428 | 20.3291 | -0.13388 | 20.9498 | 0.047369 | 0.013591 | -27.03 | 0.83863 | -1.2 | -0.13 | 0.67166 | -0.13971 | -6.4492 | 0.71067 | 0.3694 | -16.707 | 5.1551 | 0.42686 | 0.43273 | 0.42842 | 0.40765 | 0.47836 | 0.44339 | 0.43032
42838.4109 | -809 | 22.9131 | 22.8834 | 22.886 | 22.8157 | 22.458 | 21.8161 | 22.7561 | 21.8836 | 22.4108 | 22.4242 | 22.4092 | 22.098 | 21.3257 | 22.2739 | 21.6047 | 21.7908 | 21.9215 | 21.1107 | 21.2121 | 21.4278 | 20.5144 | 20.6655 | 20.9576 | 21.9353 | 21.6976 | 21.3295 | 20.4781 | 20.5842 | 20.5289 | 22.0632 | 21.6828 | 21.2067 | 22.0242 | 21.7666 | 21.3862 | 19.9669 | 20.5855 |  | 20.5986 | 20.3157 | 20.4064 | 19.0838 |  | 16.7258 | 16.728 | 16.4546 | 16.6964 | 16.9112 | 17.329 | 17.7299 | 15.4301 | 16.6684 | 15.7649 | 16.8608 | 17.8977 | 45.1365 | 47.815 | 44.0944 | 21.2794 |  |  | 0.50489 | -0.2524 | -29.2707 | 0.39554 | 0.13221 | -197.8585 | 19.3858 | -0.78233 | -0.13476 | -0.19353 | -0.019846 | 8.8284 | 9.0581 | 1.978 | 21.8343 | 22.0675 | 22.2573 | 22.3308 | 22.1706 | 21.5214 | 20.3559 | 22.2469 | 22.4189 | 22.4571 | 22.4018 | 22.0532 | 21.3088 | 22.3296 | 17.0748 | 17.0023 | 16.0292 | 16.0408 | 16.1074 | 17.108 | 16.7277 | 22.3967 | 22.1766 | 21.7505 | 22.1086 | 21.8458 | 21.3558 | 21.9818 | 21.5716 | 20.9636 | 20.1567 | 20.4882 | 20.0323 | 19.7867 | -0.026136 | -0.22916 | 20.6273 | 22.0818 | 22.4095 | 20.1104 | 21.7141 | 22.165 | 21.9819 | 21.7537 | 21.3345 | 21.8399 | 21.5137 | 21.1128 | 20.5286 | 20.5935 | 20.6112 | 20.6431 | 20.0033 |  | 20.2289 | 19.6039 | 20.136 | 19.8002 | 20.1185 | 20.3846 |  | 20.483 |  |  | 20.1132 | 20.3032 | 20.5678 | [5 empty] | 21.9801 | 20.3905 | 21.7292 | 22.1347 | 19.6316 | 21.2847 | 21.9382 | 19.3289 | 19.9456 | 21.164 |  | 19.7026 | 20.9846 | 18.8301 | 19.7262 | 20.8652 | 19.3632 | 20.1776 | 19.0278 | 20.2466 | 19.2271 | 20.4488 | 18.7994 | 20.2035 | 21.0919 | 19.3259 | 19.7845 | 21.0473 | 19.0024 | 19.8177 | 20.8795 | 19.0039 | 20.3328 | 19.3052 | 20.0826 | 19.0428 | 20.3306 | -0.054298 | 20.9491 | 0.046386 | 0.013126 | -27.0456 | 0.85751 | -1.17 | 0.07 | 0.8486 | -0.5961 | -6.4194 | 0.74622 | 0.43188 | -16.7071 | 5.2296 | 0.42632 | 0.4343 | 0.42826 | 0.40614 | 0.47797 | 0.44308 | 0.42991
42838.4109 | -808 | 22.9159 | 22.8816 | 22.8739 | 22.8127 | 22.4649 | 21.8161 | 22.7604 | 21.8834 | 22.4057 | 22.4249 | 22.4084 | 22.1027 | 21.3216 | 22.2707 | 21.6113 | 21.7881 | 21.9318 | 21.1101 | 21.2112 | 21.4306 | 20.5205 | 20.663 | 20.9587 | 21.9352 | 21.6953 | 21.3329 | 20.4795 | 20.5843 | 20.5346 | 22.0571 | 21.679 | 21.2048 | 22.0173 | 21.7596 | 21.3815 | 19.9592 | 20.5807 |  | 20.592 | 20.3046 | 20.397 | 19.0787 |  | 16.7216 | 16.7297 | 16.4628 | 16.7194 | 16.9114 | 17.3326 | 17.7125 | 15.4815 | 16.6692 | 15.7137 | 16.858 | 17.8925 | 45.099 | 47.7912 | 44.0756 | 21.2787 |  |  | 0.43064 | -0.090749 | -29.272 | 0.19841 | 0.16047 | -197.8572 | 19.832 | -0.44588 | 0.12094 | -0.19983 | 0.099764 | 8.8301 | 9.0598 | 1.9788 | 21.8295 | 22.0593 | 22.2574 | 22.3279 | 22.1612 | 21.52 | 20.3528 | 22.2327 | 22.4059 | 22.4373 | 22.3991 | 22.0438 | 21.2911 | 22.3075 | 17.092 | 16.9989 | 16.023 | 16.0539 | 16.1146 | 17.1041 | 16.7246 | 22.4021 | 22.1712 | 21.7499 | 22.1151 | 21.8391 | 21.3524 | 21.9749 | 21.5771 | 20.9634 | 20.1616 | 20.4933 | 20.0353 | 19.8028 | -0.15628 | 0.023996 | 20.6305 | 22.0886 | 22.4159 | 20.1116 | 21.7159 | 22.172 | 21.9866 | 21.7571 | 21.3314 | 21.8458 | 21.5165 | 21.1242 | 20.5388 | 20.5958 | 20.6148 | 20.6518 | 20.008 |  | 20.2256 | 19.5483 | 20.1406 | 19.7965 | 20.1263 | 20.3849 |  | 20.4853 |  |  | 20.1263 | 20.3061 | 20.5661 | [5 empty] | 21.979 | 20.3843 | 21.73 | 22.1352 | 19.6215 | 21.2784 | 21.9296 | 19.3306 | 19.9484 | 21.1597 |  | 19.6852 | 20.9882 | 18.8353 | 19.718 | 20.8569 | 19.3584 | 20.1684 | 19.0202 | 20.2215 | 19.2205 | 20.4411 | 18.8 | 20.1918 | 21.0946 | 19.3259 | 19.7785 | 21.0515 | 18.9981 | 19.8184 | 20.8745 | 18.9916 | 20.3229 | 19.3055 | 20.0819 | 19.0377 | 20.3152 | -0.20492 | 20.9527 | 0.046091 | 0.012662 | -27.0173 | 0.87618 | -1.4 | 0.16 | 0.78373 | -0.35743 | -6.4195 | 0.52851 | 0.4758 | -16.7072 | 5.2895 | 0.42608 | 0.43599 | 0.42862 | 0.40378 | 0.47829 | 0.44297 | 0.42963
42838.4109 | -807 | 22.9182 | 22.8846 | 22.8733 | 22.8102 | 22.4586 | 21.8139 | 22.7508 | 21.8789 | 22.4018 | 22.4193 | 22.4062 | 22.0971 | 21.3193 | 22.2727 | 21.6101 | 21.7933 | 21.931 | 21.1227 | 21.2193 | 21.4376 | 20.5238 | 20.6707 | 20.9681 | 21.939 | 21.7034 | 21.3353 | 20.4874 | 20.6011 | 20.5373 | 22.0576 | 21.6802 | 21.2068 | 22.022 | 21.765 | 21.3837 | 19.9554 | 20.5787 |  | 20.5884 | 20.3001 | 20.4019 | 19.078 |  | 16.7174 | 16.7178 | 16.458 | 16.7332 | 16.9183 | 17.314 | 17.6971 | 15.5486 | 16.6677 | 15.6906 | 16.8634 | 17.897 | 45.0603 | 47.7683 | 44.0662 | 21.2738 |  |  | 0.37019 | -0.23991 | -29.5881 | 0.17672 | 0.11644 | -197.7928 | 19.6572 | -0.44851 | -0.048946 | -0.12157 | 0.014526 | 8.8301 | 9.0598 | 1.9785 | 21.8212 | 22.0527 | 22.2487 | 22.3116 | 22.1481 | 21.5094 | 20.3485 | 22.2312 | 22.4051 | 22.4404 | 22.3925 | 22.0449 | 21.2892 | 22.303 | 17.1082 | 16.9611 | 16.0262 | 16.0612 | 16.1215 | 17.1054 | 16.7238 | 22.4038 | 22.1772 | 21.7428 | 22.116 | 21.8462 | 21.3519 | 21.9779 | 21.5721 | 20.9671 | 20.165 | 20.4998 | 20.0371 | 19.8104 | -0.19836 | -0.02926 | 20.6426 | 22.0918 | 22.4134 | 20.1153 | 21.7124 | 22.1631 | 21.9772 | 21.7537 | 21.3281 | 21.8425 | 21.5194 | 21.1166 | 20.5265 | 20.5994 | 20.6191 | 20.6474 | 20.0248 |  | 20.2331 | 19.4982 | 20.1327 | 19.8038 | 20.1246 | 20.392 |  | 20.4916 |  |  | 20.138 | 20.2935 | 20.5588 | [5 empty] | 21.9778 | 20.3822 | 21.7273 | 22.1346 | 19.6196 | 21.281 | 21.929 | 19.335 | 19.9556 | 21.1688 |  | 19.6772 | 20.9851 | 18.8475 | 19.7148 | 20.8595 | 19.369 | 20.1812 | 19.0256 | 20.2176 | 19.2253 | 20.4324 | 18.7925 | 20.1753 | 21.0963 | 19.3311 | 19.7874 | 21.0578 | 19.0053 | 19.8163 | 20.8755 | 18.9797 | 20.3127 | 19.2996 | 20.081 | 19.0368 | 20.3188 | -0.32235 | 20.9456 | 0.047399 | 0.013141 | -26.9869 | 0.89435 | -1.35 | -0.14 | 0.72664 | -0.58116 | -6.4539 | 0.49878 | 0.40529 | -16.7039 | 5.2659 | 0.42586 | 0.43712 | 0.42836 | 0.40213 | 0.47784 | 0.44286 | 0.42953
42838.4109 | -806 | 22.91 | 22.8811 | 22.873 | 22.8181 | 22.4544 | 21.801 | 22.7502 | 21.8786 | 22.3998 | 22.4076 | 22.4028 | 22.0954 | 21.3189 | 22.2705 | 21.6117 | 21.7925 | 21.928 | 21.1218 | 21.2201 | 21.4353 | 20.5198 | 20.6682 | 20.9623 | 21.9376 | 21.7048 | 21.3399 | 20.4864 | 20.5898 | 20.5431 | 22.0703 | 21.6822 | 21.2063 | 22.0219 | 21.7663 | 21.388 | 19.9579 | 20.5843 |  | 20.5903 | 20.3012 | 20.4008 | 19.0773 |  | 16.7001 | 16.7094 | 16.4694 | 16.7419 | 16.9259 | 17.3158 | 17.7025 | 15.5832 | 16.6647 | 15.6807 | 16.852 | 17.8883 | 45.0357 | 47.7266 | 44.0483 | 21.2683 |  |  | 0.38464 | -0.39893 | -29.4646 | 0.21746 | 0.1539 | -197.8453 | 19.8583 | -0.45246 | -0.39767 | -0.25228 | -0.016374 | 8.8287 | 9.0583 | 1.9785 | 21.8219 | 22.0551 | 22.2422 | 22.3152 | 22.1562 | 21.5048 | 20.342 | 22.23 | 22.4095 | 22.4448 | 22.3912 | 22.0419 | 21.2918 | 22.3127 | 17.1292 | 16.9718 | 16.0306 | 16.0603 | 16.1228 | 17.1017 | 16.7211 | 22.4022 | 22.1793 | 21.7513 | 22.1056 | 21.8421 | 21.3563 | 21.9805 | 21.5797 | 20.9688 | 20.1603 | 20.5026 | 20.0447 | 19.8214 | -0.10772 | -0.035536 | 20.6332 | 22.0955 | 22.4125 | 20.1153 | 21.7128 | 22.1663 | 21.9784 | 21.7492 | 21.3297 | 21.8425 | 21.5201 | 21.1221 | 20.5311 | 20.6002 | 20.6226 | 20.6538 | 20.0257 |  | 20.2259 | 19.4452 | 20.1238 | 19.7994 | 20.1197 | 20.3812 |  | 20.4826 |  |  | 20.1532 | 20.3006 | 20.5568 | [5 empty] | 21.976 | 20.3889 | 21.7324 | 22.1318 | 19.6296 | 21.2789 | 21.9245 | 19.3402 | 19.9551 | 21.1727 |  | 19.661 | 20.9871 | 18.854 | 19.7228 | 20.8542 | 19.3722 | 20.1784 | 19.0233 | 20.212 | 19.219 | 20.4251 | 18.794 | 20.1693 | 21.098 | 19.3347 | 19.7858 | 21.0476 | 19.0045 | 19.8076 | 20.8764 | 18.9782 | 20.305 | 19.3006 | 20.0817 | 19.0354 | 20.3122 | -0.061162 | 20.9508 | 0.048419 | 0.014615 | -27.0388 | 0.91179 | -1.27 | -0.12 | 0.7407 | -0.74939 | -6.4404 | 0.55329 | 0.46594 | -16.7062 | 5.2928 | 0.42559 | 0.4383 | 0.42832 | 0.39936 | 0.47704 | 0.44296 | 0.42907
42838.411 | -805 | 22.9147 | 22.8935 | 22.8808 | 22.8186 | 22.4628 | 21.8165 | 22.7568 | 21.8881 | 22.4155 | 22.4243 | 22.4048 | 22.1098 | 21.3318 | 22.2864 | 21.5944 | 21.7731 | 21.9178 | 21.1049 | 21.2041 | 21.4311 | 20.5097 | 20.6583 | 20.9567 | 21.9368 | 21.6887 | 21.327 | 20.4795 | 20.5783 | 20.5339 | 22.063 | 21.6872 | 21.2066 | 22.022 | 21.7692 | 21.3928 | 19.9664 | 20.5886 |  | 20.5949 | 20.3023 | 20.402 | 19.0769 |  | 16.6913 | 16.6981 | 16.4779 | 16.7602 | 16.9328 | 17.3289 | 17.7087 | 15.5868 | 16.6653 | 15.6675 | 16.8455 | 17.894 | 45.0362 | 47.7057 | 44.0427 | 21.2736 |  |  | 0.50292 | -0.18997 | -29.983 | 0.48557 | 0.40426 | -197.8604 | 20.1428 | -0.44392 | -0.22195 | -0.24871 | 0.051156 | 8.8288 | 9.0584 | 1.9774 | 21.8318 | 22.0641 | 22.2543 | 22.3227 | 22.1653 | 21.5144 | 20.3496 | 22.2371 | 22.4158 | 22.45 | 22.4021 | 22.0424 | 21.2981 | 22.3162 | 17.1432 | 16.9822 | 16.0369 | 16.0421 | 16.1259 | 17.0979 | 16.72 | 22.3996 | 22.1753 | 21.7466 | 22.1078 | 21.8386 | 21.352 | 21.9761 | 21.5712 | 20.9585 | 20.1597 | 20.5009 | 20.0449 | 19.8276 | -0.049531 | -0.074337 | 20.6194 | 22.0898 | 22.4143 | 20.1045 | 21.7213 | 22.1703 | 21.9864 | 21.756 | 21.3327 | 21.8482 | 21.5179 | 21.125 | 20.536 | 20.6016 | 20.6238 | 20.6567 | 20.0284 |  | 20.229 | 19.4278 | 20.1224 | 19.801 | 20.1104 | 20.3884 |  | 20.483 |  |  | 20.1575 | 20.3066 | 20.5597 | [5 empty] | 21.9732 | 20.3994 | 21.7226 | 22.1253 | 19.6229 | 21.275 | 21.9251 | 19.3424 | 19.9587 | 21.1778 |  | 19.6658 | 20.9823 | 18.8555 | 19.7187 | 20.8597 | 19.3656 | 20.1812 | 19.029 | 20.2072 | 19.2181 | 20.4205 | 18.8044 | 20.1759 | 21.1074 | 19.3454 | 19.7999 | 21.0528 | 19.0132 | 19.8173 | 20.8784 | 18.9805 | 20.3069 | 19.3011 | 20.1022 | 19.0422 | 20.3236 | -0.10216 | 20.9496 | 0.048585 | 0.014644 | -27.0825 | 0.9689 | -1.36 | -0.19 | 0.84695 | -0.51713 | -6.4967 | 0.82675 | 0.75518 | -16.7072 | 5.3307 | 0.42562 | 0.43873 | 0.42796 | 0.39736 | 0.47622 | 0.44326 | 0.42887
42838.411 | -804 | 22.9059 | 22.8884 | 22.8734 | 22.8063 | 22.45 | 21.8138 | 22.7568 | 21.8731 | 22.4018 | 22.4168 | 22.4051 | 22.0956 | 21.3207 | 22.2801 | 21.6106 | 21.7831 | 21.9222 | 21.1109 | 21.2116 | 21.4417 | 20.5162 | 20.6671 | 20.9574 | 21.9379 | 21.694 | 21.3351 | 20.4865 | 20.5768 | 20.5511 | 22.0699 | 21.6851 | 21.2117 | 22.0281 | 21.764 | 21.3896 | 19.9637 | 20.587 |  | 20.5927 | 20.3031 | 20.4069 | 19.0545 |  | 16.7062 | 16.7147 | 16.4992 | 16.7865 | 16.9617 | 17.3667 | 17.7167 | 15.5879 | 16.6665 | 15.6776 | 16.8496 | 17.886 | 45.0263 | 47.6669 | 44.0206 | 21.2739 |  |  | 0.39253 | -0.19654 | -30.6973 | 0.35545 | 0.063872 | -197.8381 | 19.7374 | -0.49057 | 0.024808 | -0.44152 | 0.0087976 | 8.8279 | 9.0574 | 1.9787 | 21.8294 | 22.0588 | 22.2544 | 22.3232 | 22.1616 | 21.5163 | 20.351 | 22.2405 | 22.4117 | 22.4447 | 22.397 | 22.0407 | 21.2966 | 22.3136 | 17.1445 | 16.985 | 16.0141 | 16.0304 | 16.1242 | 17.0952 | 16.7185 | 22.3969 | 22.1747 | 21.7412 | 22.1088 | 21.8297 | 21.3414 | 21.9784 | 21.5693 | 20.9522 | 20.156 | 20.5004 | 20.0427 | 19.8335 | -0.14469 | -0.11124 | 20.6191 | 22.0892 | 22.4109 | 20.1027 | 21.718 | 22.1717 | 21.9868 | 21.7659 | 21.3324 | 21.8525 | 21.5098 | 21.1196 | 20.5351 | 20.597 | 20.6205 | 20.6539 | 20.0512 |  | 20.2307 | 19.4108 | 20.1358 | 19.8106 | 20.1163 | 20.3967 |  | 20.487 |  |  | 20.1758 | 20.3022 | 20.5672 | [5 empty] | 21.9773 | 20.389 | 21.7214 | 22.1238 | 19.6236 | 21.2704 | 21.9251 | 19.351 | 19.9556 | 21.1743 |  | 19.6479 | 20.9878 | 18.8615 | 19.7195 | 20.8534 | 19.3623 | 20.1809 | 19.0278 | 20.1968 | 19.2114 | 20.4096 | 18.7863 | 20.1492 | 21.0916 | 19.3416 | 19.794 | 21.0584 | 18.9996 | 19.8225 | 20.8763 | 18.9646 | 20.2963 | 19.2969 | 20.0884 | 19.0316 | 20.3129 | -0.14427 | 20.9502 | 0.048038 | 0.014143 | -27.0307 | 1.102 | -1.64 | -0.16 | 0.74827 | -0.52601 | -6.5738 | 0.70739 | 0.3002 | -16.7073 | 5.2771 | 0.42504 | 0.43965 | 0.4279 | 0.39691 | 0.47857 | 0.44379 | 0.42859
42838.411 | -803 | 22.9227 | 22.8991 | 22.8854 | 22.8173 | 22.4654 | 21.8216 | 22.7635 | 21.89 | 22.4167 | 22.4282 | 22.4137 | 22.1033 | 21.33 | 22.2811 | 21.6122 | 21.781 | 21.9254 | 21.1103 | 21.2089 | 21.4413 | 20.5146 | 20.6648 | 20.9638 | 21.9336 | 21.7046 | 21.3345 | 20.4796 | 20.591 | 20.5581 | 22.0739 | 21.6825 | 21.2153 | 22.032 | 21.7678 | 21.3908 | 19.9697 | 20.5714 |  | 20.5893 | 20.3051 | 20.3985 | 19.0546 |  | 16.7063 | 16.7324 | 16.5186 | 16.7987 | 16.9777 | 17.3752 | 17.691 | 15.5447 | 16.6623 | 15.6623 | 16.8528 | 17.8904 | 45.0345 | 47.6376 | 44.0056 | 21.2814 |  |  | 0.50752 | -0.27671 | -30.8898 | 0.3456 | 0.097384 | -197.892 | 19.8885 | -0.51882 | 0.12094 | -0.25857 | 0.074592 | 8.8283 | 9.0579 | 1.9785 | 21.8289 | 22.059 | 22.2536 | 22.3209 | 22.1681 | 21.516 | 20.3475 | 22.2425 | 22.4135 | 22.4481 | 22.4017 | 22.0481 | 21.2909 | 22.3151 | 17.1513 | 16.9715 | 15.9839 | 16.0177 | 16.1068 | 17.0896 | 16.7149 | 22.4086 | 22.1748 | 21.7446 | 22.1071 | 21.8366 | 21.3592 | 21.9873 | 21.5746 | 20.9649 | 20.1616 | 20.5007 | 20.0579 | 19.8515 | -0.053266 | -0.1565 | 20.6197 | 22.0951 | 22.4115 | 20.1003 | 21.7125 | 22.1661 | 21.9863 | 21.7596 | 21.3372 | 21.8423 | 21.5185 | 21.1138 | 20.5303 | 20.5959 | 20.6199 | 20.658 | 20.0547 |  | 20.2265 | 19.4006 | 20.1273 | 19.811 | 20.1193 | 20.3875 |  | 20.4804 |  |  | 20.1841 | 20.3174 | 20.5811 | [5 empty] | 21.9814 | 20.3956 | 21.7304 | 22.1281 | 19.6271 | 21.28 | 21.9254 | 19.3544 | 19.9699 | 21.177 |  | 19.652 | 20.9829 | 18.8694 | 19.72 | 20.8566 | 19.3738 | 20.1805 | 19.0255 | 20.2093 | 19.2155 | 20.4027 | 18.7873 | 20.1538 | 21.1011 | 19.3479 | 19.801 | 21.0564 | 19.0154 | 19.8298 | 20.8901 | 18.9683 | 20.3001 | 19.3077 | 20.095 | 19.0297 | 20.3182 | -0.11681 | 20.9492 | 0.048733 | 0.014172 | -27.0625 | 1.2306 | -1.67 | -0.01 | 0.85085 | -0.62416 | -6.5946 | 0.69753 | 0.37068 | -16.7099 | 5.2974 | 0.42481 | 0.43965 | 0.42799 | 0.39549 | 0.4815 | 0.44398 | 0.42827
42838.411 | -802 | 22.9189 | 22.8911 | 22.8817 | 22.8194 | 22.4698 | 21.8167 | 22.7644 | 21.8912 | 22.4131 | 22.4241 | 22.4123 | 22.0988 | 21.3311 | 22.2832 | 21.6036 | 21.7857 | 21.9307 | 21.1081 | 21.2083 | 21.4375 | 20.51 | 20.6632 | 20.9591 | 21.9349 | 21.6991 | 21.3422 | 20.4809 | 20.5842 | 20.5609 | 22.0621 | 21.6764 | 21.2053 | 22.0143 | 21.7672 | 21.3878 | 19.9622 | 20.5652 |  | 20.5875 | 20.2987 | 20.3934 | 19.0393 |  | 16.707 | 16.7464 | 16.539 | 16.8109 | 16.974 | 17.3885 | 17.6852 | 15.5523 | 16.6689 | 15.6338 | 16.8522 | 17.8896 | 45.0305 | 47.598 | 43.9852 | 21.2738 |  |  | 0.56929 | 0.022935 | -31.3281 | 0.32194 | 0.25115 | -197.8585 | 19.788 | -0.39857 | -0.025205 | -0.47613 | 0.020776 | 8.8273 | 9.057 | 1.9783 | 21.8304 | 22.0584 | 22.2539 | 22.3166 | 22.1716 | 21.5205 | 20.3509 | 22.2423 | 22.412 | 22.4522 | 22.4005 | 22.047 | 21.2898 | 22.3191 | 17.157 | 16.9427 | 15.9639 | 16.0128 | 16.0758 | 17.084 | 16.7113 | 22.3926 | 22.1712 | 21.7383 | 22.105 | 21.8356 | 21.3503 | 21.97 | 21.5749 | 20.9636 | 20.1567 | 20.5007 | 20.0578 | 19.8639 | -0.065062 | -0.11827 | 20.6103 | 22.0935 | 22.4094 | 20.0985 | 21.7181 | 22.1687 | 21.982 | 21.7576 | 21.3361 | 21.8415 | 21.5244 | 21.1124 | 20.5328 | 20.5937 | 20.6214 | 20.6516 | 20.0603 |  | 20.2326 | 19.4227 | 20.1211 | 19.8027 | 20.1177 | 20.3947 |  | 20.4843 |  |  | 20.1878 | 20.3218 | 20.5755 | [5 empty] | 21.9847 | 20.4026 | 21.7369 | 22.1282 | 19.6293 | 21.2826 | 21.9364 | 19.3624 | 19.9647 | 21.1695 |  | 19.6394 | 20.9823 | 18.8694 | 19.7101 | 20.8548 | 19.366 | 20.1773 | 19.0215 | 20.2064 | 19.2109 | 20.3921 | 18.7788 | 20.1476 | 21.1037 | 19.3557 | 19.8017 | 21.0507 | 19.0025 | 19.816 | 20.8804 | 18.9643 | 20.2895 | 19.3019 | 20.0976 | 19.0205 | 20.3123 | -0.20975 | 20.9499 | 0.048512 | 0.013823 | -27.0123 | 1.3506 | -1.34 | -0.02 | 0.90115 | 0.1797 | -6.6413 | 0.67325 | 0.5953 | -16.7088 | 5.2841 | 0.42486 | 0.43883 | 0.42816 | 0.39422 | 0.4833 | 0.44416 | 0.42777
42838.411 | -801 | 22.9079 | 22.8852 | 22.8756 | 22.8127 | 22.4559 | 21.8103 | 22.7637 | 21.8842 | 22.4044 | 22.418 | 22.4071 | 22.0902 | 21.3278 | 22.2809 | 21.5998 | 21.7801 | 21.9164 | 21.1091 | 21.2115 | 21.4362 | 20.5078 | 20.6539 | 20.9556 | 21.9316 | 21.6946 | 21.3328 | 20.481 | 20.5765 | 20.5592 | 22.0555 | 21.6733 | 21.2015 | 22.0131 | 21.7589 | 21.3802 | 19.9603 | 20.558 |  | 20.5844 | 20.2979 | 20.3918 | 19.0338 |  | 16.6905 | 16.738 | 16.5268 | 16.8086 | 16.9665 | 17.3842 | 17.6953 | 15.545 | 16.6529 | 15.5771 | 16.8353 | 17.9028 | 45.0388 | 47.5719 | 43.9652 | 21.2855 |  |  | 0.58572 | -0.142 | -31.8906 | 0.36597 | 0.18347 | -197.8434 | 19.533 | -0.47808 | 0.19975 | -0.36767 | 0.07112 | 8.8284 | 9.0583 | 1.9776 | 21.8185 | 22.0579 | 22.2568 | 22.3187 | 22.1641 | 21.5163 | 20.3524 | 22.2416 | 22.4076 | 22.4466 | 22.3998 | 22.0483 | 21.2879 | 22.3121 | 17.1653 | 16.947 | 15.9451 | 16.016 | 16.0524 | 17.0905 | 16.7156 | 22.3999 | 22.1728 | 21.744 | 22.103 | 21.8398 | 21.3524 | 21.9739 | 21.577 | 20.9608 | 20.1594 | 20.5091 | 20.059 | 19.8811 | -0.059164 | -0.088222 | 20.6109 | 22.0893 | 22.409 | 20.0921 | 21.7166 | 22.1644 | 21.9872 | 21.7549 | 21.3309 | 21.8377 | 21.5145 | 21.1138 | 20.5411 | 20.5954 | 20.6187 | 20.6534 | 20.069 |  | 20.2279 | 19.4177 | 20.119 | 19.8021 | 20.1156 | 20.3871 |  | 20.4822 |  |  | 20.1792 | 20.325 | 20.5757 | [5 empty] | 21.9707 | 20.3854 | 21.7241 | 22.1218 | 19.6237 | 21.2739 | 21.9145 | 19.3658 | 19.9675 | 21.1721 |  | 19.6358 | 20.9829 | 18.8697 | 19.7064 | 20.8515 | 19.3733 | 20.1791 | 19.0306 | 20.2135 | 19.226 | 20.3896 | 18.7712 | 20.1417 | 21.1148 | 19.3561 | 19.8049 | 21.0572 | 18.9994 | 19.8167 | 20.883 | 18.9644 | 20.282 | 19.3042 | 20.1001 | 19.0192 | 20.3101 | -0.23535 | 20.9496 | 0.047639 | 0.012705 | -26.9996 | 1.4653 | -1.15 | -0.1 | 0.91405 | -0.44712 | -6.7006 | 0.7178 | 0.5088 | -16.7081 | 5.2499 | 0.42445 | 0.4389 | 0.42811 | 0.39404 | 0.4859 | 0.44425 | 0.42738
42838.411 | -800 | 22.9124 | 22.8847 | 22.8729 | 22.8095 | 22.4646 | 21.8096 | 22.7591 | 21.8749 | 22.4076 | 22.4201 | 22.4094 | 22.0975 | 21.3236 | 22.2786 | 21.6018 | 21.7809 | 21.9134 | 21.1113 | 21.2125 | 21.4313 | 20.5127 | 20.6569 | 20.9548 | 21.9363 | 21.6973 | 21.3263 | 20.4807 | 20.5726 | 20.5655 | 22.0544 | 21.6675 | 21.198 | 22.017 | 21.7608 | 21.3741 | 19.961 | 20.5479 |  | 20.5925 | 20.3018 | 20.3953 | 19.0293 |  | 16.6952 | 16.7442 | 16.5253 | 16.8153 | 16.9754 | 17.3937 | 17.7002 | 15.541 | 16.6508 | 15.5629 | 16.8382 | 17.8933 | 45.0274 | 47.5243 | 43.9334 | 21.2799 |  |  | 0.4727 | -0.072349 | -31.9156 | 0.33311 | 0.19201 | -197.8144 | 19.7013 | -0.38017 | 0.056333 | -0.51201 | 0.059662 | 8.8278 | 9.0578 | 1.9788 | 21.8356 | 22.0575 | 22.2573 | 22.3308 | 22.1687 | 21.5132 | 20.3497 | 22.2481 | 22.4226 | 22.4524 | 22.4071 | 22.0581 | 21.2986 | 22.321 | 17.1756 | 16.9411 | 15.9168 | 16.0123 | 16.0358 | 17.0949 | 16.7164 | 22.4009 | 22.1767 | 21.7477 | 22.1119 | 21.8392 | 21.3504 | 21.972 | 21.577 | 20.9515 | 20.1612 | 20.504 | 20.0621 | 19.885 | -0.2308 | -0.24666 | 20.6214 | 22.0914 | 22.4079 | 20.0958 | 21.7168 | 22.1641 | 21.9827 | 21.7564 | 21.3332 | 21.8361 | 21.5122 | 21.1194 | 20.5382 | 20.5983 | 20.6132 | 20.6519 | 20.0557 |  | 20.2258 | 19.411 | 20.1201 | 19.809 | 20.1179 | 20.3896 |  | 20.4851 |  |  | 20.1698 | 20.3282 | 20.5699 | [5 empty] | 21.9653 | 20.3832 | 21.7222 | 22.1192 | 19.6289 | 21.2726 | 21.9156 | 19.3747 | 19.9748 | 21.1769 |  | 19.6335 | 20.9805 | 18.8773 | 19.7051 | 20.8443 | 19.38 | 20.1806 | 19.0217 | 20.2162 | 19.2232 | 20.3895 | 18.7726 | 20.1396 | 21.1128 | 19.3597 | 19.8075 | 21.0608 | 19.0054 | 19.8116 | 20.8784 | 18.9681 | 20.2847 | 19.3046 | 20.1088 | 19.0247 | 20.3077 | -0.1118 | 20.9503 | 0.046865 | 0.013061 | -26.9851 | 1.5765 | -1.14 | 0.01 | 0.82115 | -0.31916 | -6.7033 | 0.68483 | 0.52051 | -16.7071 | 5.2725 | 0.42475 | 0.43912 | 0.42799 | 0.39341 | 0.48914 | 0.4444 | 0.42733
42838.411 | -799 | 22.9149 | 22.8854 | 22.883 | 22.8087 | 22.4648 | 21.8167 | 22.7661 | 21.885 | 22.411 | 22.4183 | 22.4126 | 22.1013 | 21.3254 | 22.2762 | 21.6038 | 21.7819 | 21.9156 | 21.1106 | 21.2075 | 21.4275 | 20.5141 | 20.6546 | 20.9511 | 21.9336 | 21.6947 | 21.3248 | 20.4803 | 20.5681 | 20.5632 | 22.0563 | 21.667 | 21.1993 | 22.0127 | 21.7551 | 21.3682 | 19.9587 | 20.529 |  | 20.5949 | 20.2952 | 20.3932 | 19.0178 |  | 16.6967 | 16.741 | 16.5212 | 16.8189 | 16.966 | 17.385 | 17.6997 | 15.5396 | 16.6613 | 15.5781 | 16.8443 | 17.8898 | 45.0274 | 47.4905 | 43.9141 | 21.2794 |  |  | 0.35639 | -0.019777 | -32.1574 | 0.49213 | 0.21238 | -197.8151 | 19.5146 | -0.21458 | 0.044657 | -0.21221 | 0.094035 | 8.8283 | 9.058 | 1.9785 | 21.8296 | 22.0569 | 22.2565 | 22.3295 | 22.1698 | 21.5138 | 20.3477 | 22.2443 | 22.4087 | 22.4424 | 22.4004 | 22.0456 | 21.2984 | 22.3092 | 17.1686 | 16.9181 | 15.897 | 15.9887 | 16.0202 | 17.091 | 16.7127 | 22.3972 | 22.1733 | 21.7429 | 22.1034 | 21.8341 | 21.3472 | 21.9735 | 21.5735 | 20.9459 | 20.1522 | 20.5003 | 20.064 | 19.8861 | -0.18165 | -0.079282 | 20.635 | 22.0901 | 22.411 | 20.0952 | 21.7179 | 22.1707 | 21.9844 | 21.7566 | 21.3325 | 21.8418 | 21.516 | 21.1202 | 20.5428 | 20.596 | 20.6158 | 20.6613 | 20.0603 |  | 20.2204 | 19.4304 | 20.119 | 19.8083 | 20.1106 | 20.3916 |  | 20.4839 |  |  | 20.1683 | 20.3273 | 20.5679 | [5 empty] | 21.9706 | 20.3822 | 21.7204 | 22.1171 | 19.6213 | 21.2696 | 21.9111 | 19.3756 | 19.969 | 21.1719 |  | 19.6217 | 20.9786 | 18.8776 | 19.7065 | 20.8396 | 19.3739 | 20.1774 | 19.011 | 20.2116 | 19.2151 | 20.3773 | 18.7742 | 20.1319 | 21.1093 | 19.3604 | 19.8157 | 21.0592 | 19.0039 | 19.8085 | 20.8777 | 18.9652 | 20.2759 | 19.304 | 20.108 | 19.0277 | 20.3098 | -0.095294 | 20.95 | 0.046883 | 0.011537 | -26.9842 | 1.6849 | -1.01 | -0.21 | 0.713 | -0.16686 | -6.7286 | 0.83239 | 0.54742 | -16.7069 | 5.2474 | 0.42445 | 0.43855 | 0.42777 | 0.39374 | 0.4909 | 0.44464 | 0.427
42838.411 | -798 | 22.91 | 22.8883 | 22.8778 | 22.8129 | 22.4511 | 21.8231 | 22.7619 | 21.8781 | 22.4103 | 22.4223 | 22.4074 | 22.0991 | 21.3226 | 22.2824 | 21.6113 | 21.7818 | 21.9234 | 21.1139 | 21.2129 | 21.435 | 20.5206 | 20.6567 | 20.9585 | 21.9392 | 21.7 | 21.3363 | 20.4844 | 20.5733 | 20.5712 | 22.0581 | 21.6796 | 21.1972 | 22.0193 | 21.7639 | 21.3752 | 19.9571 | 20.528 |  | 20.5955 | 20.3028 | 20.3903 | 19.0334 |  | 16.6808 | 16.7263 | 16.5081 | 16.7948 | 16.9416 | 17.3714 | 17.6956 | 15.5377 | 16.6575 | 15.5877 | 16.8405 | 17.8854 | 45.0222 | 47.4531 | 43.889 | 21.2819 |  |  | 0.3025 | -0.055265 | -32.2507 | 0.48688 | 0.3116 | -197.8565 | 19.719 | -0.27701 | -0.071909 | -0.10164 | 0.044906 | 8.8278 | 9.0574 | 1.9782 | 21.8248 | 22.063 | 22.2564 | 22.3264 | 22.1677 | 21.5141 | 20.3504 | 22.2436 | 22.4081 | 22.4509 | 22.4094 | 22.0463 | 21.3034 | 22.3136 | 17.184 | 16.9025 | 15.8999 | 15.9974 | 16.0246 | 17.0897 | 16.7161 | 22.3911 | 22.167 | 21.7295 | 22.102 | 21.8248 | 21.3457 | 21.9774 | 21.5735 | 20.9586 | 20.1586 | 20.5024 | 20.0731 | 19.8801 | -0.23532 | -0.056839 | 20.6407 | 22.0955 | 22.4136 | 20.0912 | 21.715 | 22.169 | 21.9807 | 21.7572 | 21.3301 | 21.8425 | 21.5132 | 21.1148 | 20.5437 | 20.5938 | 20.6174 | 20.6587 | 20.0588 |  | 20.2162 | 19.4424 | 20.1174 | 19.8111 | 20.1089 | 20.3895 |  | 20.4775 |  |  | 20.1723 | 20.341 | 20.5858 | [5 empty] | 21.9725 | 20.3891 | 21.724 | 22.1213 | 19.6303 | 21.2726 | 21.9193 | 19.3714 | 19.973 | 21.173 |  | 19.6104 | 20.984 | 18.8794 | 19.7077 | 20.8463 | 19.373 | 20.1832 | 19.0159 | 20.2019 | 19.2125 | 20.3699 | 18.7634 | 20.117 | 21.1068 | 19.3589 | 19.8149 | 21.0521 | 19.0012 | 19.8118 | 20.8748 | 18.9599 | 20.2643 | 19.3023 | 20.1042 | 19.0132 | 20.3006 | -0.12405 | 20.9501 | 0.047473 | 0.012008 | -27.0801 | 1.7907 | -0.96 | -0.12 | 0.6569 | -0.27893 | -6.7382 | 0.82791 | 0.66307 | -16.7083 | 5.2747 | 0.42435 | 0.43816 | 0.42763 | 0.39187 | 0.49097 | 0.44415 | 0.42738
42838.4111 | -797 | 22.9054 | 22.8693 | 22.8783 | 22.8061 | 22.4493 | 21.8034 | 22.7463 | 21.8733 | 22.4042 | 22.4101 | 22.3992 | 22.093 | 21.3206 | 22.2751 | 21.6036 | 21.7827 | 21.9218 | 21.111 | 21.2065 | 21.4376 | 20.5229 | 20.6602 | 20.9572 | 21.9374 | 21.7026 | 21.3403 | 20.4842 | 20.574 | 20.5738 | 22.0637 | 21.6736 | 21.2024 | 22.0205 | 21.7556 | 21.3747 | 19.9586 | 20.5105 |  | 20.5907 | 20.2944 | 20.385 | 19.0524 |  | 16.6761 | 16.7288 | 16.4955 | 16.7751 | 16.9333 | 17.3779 | 17.705 | 15.5081 | 16.6617 | 15.602 | 16.837 | 17.8881 | 45.0284 | 47.4326 | 43.8817 | 21.2804 |  |  | 0.42999 | -0.2478 | -31.9761 | 0.44811 | 0.11053 | -197.8486 | 19.6973 | -0.43406 | -0.3066 | 0.037246 | 0.037962 | 8.828 | 9.0578 | 1.9776 | 21.8295 | 22.0688 | 22.2608 | 22.3259 | 22.1724 | 21.5162 | 20.3542 | 22.2435 | 22.4157 | 22.4533 | 22.4106 | 22.0505 | 21.3025 | 22.3189 | 17.1687 | 16.8694 | 15.8844 | 15.987 | 16.0187 | 17.0794 | 16.7044 | 22.3989 | 22.1749 | 21.7418 | 22.1058 | 21.829 | 21.3504 | 21.9732 | 21.5725 | 20.9606 | 20.1556 | 20.5074 | 20.0788 | 19.8684 | -0.11107 | -0.15327 | 20.6501 | 22.0965 | 22.411 | 20.0955 | 21.7162 | 22.1698 | 21.9792 | 21.7526 | 21.3285 | 21.8459 | 21.5176 | 21.1138 | 20.5455 | 20.5851 | 20.6182 | 20.655 | 20.0706 |  | 20.2252 | 19.4888 | 20.1211 | 19.8194 | 20.1141 | 20.3939 |  | 20.4766 |  |  | 20.1837 | 20.3505 | 20.5946 | [5 empty] | 21.9745 | 20.3947 | 21.7283 | 22.1277 | 19.6383 | 21.2802 | 21.9233 | 19.3886 | 19.9798 | 21.1815 |  | 19.6102 | 20.9914 | 18.8937 | 19.7141 | 20.8472 | 19.381 | 20.1894 | 19.0247 | 20.194 | 19.2148 | 20.3789 | 18.76 | 20.1181 | 21.1093 | 19.3601 | 19.8168 | 21.0487 | 19.0057 | 19.814 | 20.8746 | 18.954 | 20.2609 | 19.3046 | 20.1009 | 19.0114 | 20.3 | -0.091027 | 20.949 | 0.047535 | 0.012037 | -27.0644 | 1.8938 | -0.96 | -0.06 | 0.78318 | -0.59064 | -6.7095 | 0.79427 | 0.39491 | -16.7081 | 5.2719 | 0.42432 | 0.43699 | 0.42758 | 0.39238 | 0.49133 | 0.44367 | 0.42761
42838.4111 | -796 | 22.9149 | 22.898 | 22.8803 | 22.8138 | 22.4667 | 21.8141 | 22.7608 | 21.8836 | 22.4099 | 22.4272 | 22.4095 | 22.103 | 21.3274 | 22.2838 | 21.5902 | 21.7756 | 21.9102 | 21.1032 | 21.2039 | 21.4297 | 20.5072 | 20.6562 | 20.9499 | 21.9324 | 21.6957 | 21.3303 | 20.4785 | 20.5593 | 20.5621 | 22.0709 | 21.6801 | 21.2069 | 22.029 | 21.7622 | 21.3838 | 19.9636 | 20.5029 |  | 20.5984 | 20.3048 | 20.402 | 19.073 |  | 16.6716 | 16.718 | 16.4767 | 16.7598 | 16.9373 | 17.3919 | 17.7166 | 15.3773 | 16.6517 | 15.6281 | 16.8297 | 17.8917 | 45.0156 | 47.4046 | 43.8593 | 21.2884 |  |  | 0.46021 | -0.18209 | -32.051 | -0.028298 | 0.12301 | -197.8795 | 19.6073 | -0.3736 | -0.076384 | 0.13753 | 0.06435 | 8.8285 | 9.0584 | 1.9787 | 21.8206 | 22.0527 | 22.2552 | 22.3197 | 22.1626 | 21.5082 | 20.3433 | 22.2341 | 22.4116 | 22.4451 | 22.3967 | 22.0439 | 21.2915 | 22.3104 | 17.1624 | 16.8542 | 15.8822 | 15.9829 | 16.0109 | 17.0917 | 16.71 | 22.4005 | 22.1787 | 21.7464 | 22.1105 | 21.8378 | 21.3491 | 21.9799 | 21.578 | 20.9608 | 20.1572 | 20.5107 | 20.0805 | 19.8678 | -0.15432 | -0.18656 | 20.6577 | 22.0918 | 22.4113 | 20.0944 | 21.7135 | 22.1685 | 21.9814 | 21.7505 | 21.3281 | 21.839 | 21.5218 | 21.1123 | 20.5533 | 20.582 | 20.6216 | 20.6558 | 20.0768 |  | 20.2195 | 19.528 | 20.1201 | 19.818 | 20.1099 | 20.3833 |  | 20.4783 |  |  | 20.1855 | 20.3511 | 20.5907 | [5 empty] | 21.9715 | 20.388 | 21.7237 | 22.1244 | 19.6378 | 21.2785 | 21.9175 | 19.3915 | 19.9814 | 21.1818 |  | 19.6127 | 20.9881 | 18.8962 | 19.7086 | 20.8485 | 19.3873 | 20.1883 | 19.0234 | 20.1926 | 19.2152 | 20.372 | 18.7651 | 20.1214 | 21.1156 | 19.3679 | 19.8205 | 21.052 | 19.0085 | 19.8195 | 20.8857 | 18.9536 | 20.2654 | 19.3093 | 20.1089 | 19.0123 | 20.3002 | -0.06042 | 20.9529 | 0.047086 | 0.01338 | -26.9734 | 1.9944 | -0.92 | 0.02 | 0.81023 | -0.5063 | -6.7172 | -0.19959 | 0.41662 | -16.7098 | 5.2599 | 0.42396 | 0.43587 | 0.42748 | 0.39451 | 0.49223 | 0.44327 | 0.42768
42838.4111 | -795 | 22.9191 | 22.8886 | 22.8807 | 22.8104 | 22.4681 | 21.8146 | 22.7612 | 21.8786 | 22.4132 | 22.4245 | 22.4114 | 22.0958 | 21.3254 | 22.2774 | 21.5995 | 21.781 | 21.9181 | 21.1029 | 21.2165 | 21.4333 | 20.513 | 20.6569 | 20.9531 | 21.9277 | 21.6945 | 21.3315 | 20.4829 | 20.5664 | 20.5601 | 22.0639 | 21.6772 | 21.203 | 22.0189 | 21.7616 | 21.3845 | 19.9584 | 20.4841 |  | 20.5933 | 20.3013 | 20.3894 | 19.0809 |  | 16.668 | 16.723 | 16.4748 | 16.7651 | 16.9421 | 17.417 | 17.7134 | 15.3123 | 16.6548 | 15.657 | 16.8332 | 17.8917 | 45.0021 | 47.3721 | 43.8212 | 21.2913 |  |  | 0.45101 | -0.050005 | -32.0017 | 0.67021 | 0.23209 | -197.865 | 20.0265 | -0.32826 | -0.20268 | -0.091152 | 0.04942 | 8.8302 | 9.06 | 1.9787 | 21.8161 | 22.0533 | 22.2492 | 22.3157 | 22.1612 | 21.5124 | 20.3441 | 22.2406 | 22.4102 | 22.4512 | 22.3999 | 22.0549 | 21.2911 | 22.3203 | 17.1129 | 16.8594 | 15.8684 | 15.9714 | 16.0048 | 17.0815 | 16.7087 | 22.3982 | 22.1799 | 21.7443 | 22.1124 | 21.8424 | 21.3498 | 21.9808 | 21.5823 | 20.963 | 20.1622 | 20.518 | 20.0805 | 19.8679 | 0.011415 | -0.066159 | 20.6614 | 22.0937 | 22.4108 | 20.1034 | 21.7146 | 22.1692 | 21.9808 | 21.7554 | 21.3325 | 21.8421 | 21.5189 | 21.1184 | 20.5592 | 20.5952 | 20.6241 | 20.6538 | 20.0812 |  | 20.2226 | 19.5729 | 20.123 | 19.8256 | 20.1127 | 20.396 |  | 20.4885 |  |  | 20.1864 | 20.349 | 20.585 | [5 empty] | 21.9686 | 20.3763 | 21.7124 | 22.1174 | 19.6399 | 21.2677 | 21.9139 | 19.3845 | 19.9776 | 21.1698 |  | 19.5941 | 20.979 | 18.8759 | 19.7025 | 20.839 | 19.3845 | 20.1816 | 19.0156 | 20.1831 | 19.2167 | 20.358 | 18.7687 | 20.112 | 21.1155 | 19.3732 | 19.8304 | 21.0572 | 19.0078 | 19.8278 | 20.8886 | 18.96 | 20.2639 | 19.3157 | 20.1103 | 19.0103 | 20.2917 | 0.007473 | 20.9514 | 0.04743 | 0.014019 | -27.0719 | 2.0932 | -0.9 | -0.05 | 0.80208 | -0.26532 | -6.7121 | 0.97135 | 0.5723 | -16.7099 | 5.3161 | 0.42394 | 0.43472 | 0.42736 | 0.39883 | 0.49361 | 0.44287 | 0.42784
42838.4111 | -794 | 22.9153 | 22.8896 | 22.8729 | 22.8078 | 22.4575 | 21.8148 | 22.7594 | 21.8808 | 22.414 | 22.4197 | 22.4118 | 22.0962 | 21.3224 | 22.2723 | 21.596 | 21.775 | 21.9064 | 21.1016 | 21.2109 | 21.4251 | 20.508 | 20.6566 | 20.9475 | 21.9262 | 21.6979 | 21.3296 | 20.4755 | 20.559 | 20.55 | 22.0637 | 21.6808 | 21.204 | 22.0197 | 21.7611 | 21.3848 | 19.955 | 20.4753 |  | 20.6024 | 20.3012 | 20.3899 | 19.0928 |  | 16.6723 | 16.7202 | 16.471 | 16.7766 | 16.9357 | 17.4128 | 17.6859 | 15.3274 | 16.6548 | 15.6819 | 16.8399 | 17.8962 | 44.9912 | 47.3476 | 43.807 | 21.2956 |  |  | 0.50358 | 0.087331 | -31.5995 | 0.43234 | 0.29189 | -197.8473 | 19.9319 | -0.3322 | -0.23479 | 0.033889 | 0.10428 | 8.8275 | 9.0571 | 1.9781 | 21.8203 | 22.0531 | 22.2433 | 22.3175 | 22.157 | 21.5063 | 20.333 | 22.2341 | 22.3993 | 22.4446 | 22.3906 | 22.0422 | 21.2863 | 22.3116 | 17.0726 | 16.8763 | 15.877 | 15.9794 | 16.0159 | 17.074 | 16.7081 | 22.3971 | 22.1746 | 21.7467 | 22.1081 | 21.8409 | 21.3518 | 21.9802 | 21.5753 | 20.9633 | 20.1662 | 20.51 | 20.0836 | 19.8664 | 0.017313 | -0.19036 | 20.665 | 22.0839 | 22.412 | 20.0986 | 21.7097 | 22.1665 | 21.9746 | 21.7469 | 21.3313 | 21.8439 | 21.5086 | 21.1172 | 20.5497 | 20.5856 | 20.6137 | 20.6545 | 20.0855 |  | 20.2236 | 19.6036 | 20.1202 | 19.8313 | 20.1154 | 20.4001 |  | 20.4817 |  |  | 20.1896 | 20.3606 | 20.5925 | [5 empty] | 21.9703 | 20.3887 | 21.7172 | 22.1233 | 19.6483 | 21.2719 | 21.9141 | 19.3976 | 19.9834 | 21.1724 |  | 19.5919 | 20.9912 | 18.8728 | 19.7057 | 20.849 | 19.3909 | 20.1871 | 19.0155 | 20.184 | 19.2175 | 20.3548 | 18.7828 | 20.1124 | 21.1262 | 19.3789 | 19.8358 | 21.0687 | 19.0152 | 19.8322 | 20.8858 | 18.9647 | 20.2683 | 19.3204 | 20.1145 | 19.0081 | 20.2921 | -0.20548 | 20.9522 | 0.047086 | 0.013765 | -27.137 | 2.2002 | -1 | -0.14 | 0.84753 | 0.35063 | -6.6697 | 0.78015 | 0.6418 | -16.7091 | 5.3035 | 0.42385 | 0.43378 | 0.42729 | 0.40242 | 0.49259 | 0.44243 | 0.42802
42838.4111 | -793 | 22.9094 | 22.881 | 22.8745 | 22.8094 | 22.45 | 21.8081 | 22.7519 | 21.875 | 22.4045 | 22.4198 | 22.403 | 22.0903 | 21.314 | 22.2696 | 21.5956 | 21.7705 | 21.9143 | 21.1029 | 21.1985 | 21.4285 | 20.5088 | 20.6584 | 20.9513 | 21.9336 | 21.6983 | 21.3322 | 20.4768 | 20.5621 | 20.5555 | 22.0641 | 21.6791 | 21.2052 | 22.0175 | 21.7648 | 21.3814 | 19.9593 | 20.4567 |  | 20.5951 | 20.2966 | 20.3875 | 19.1004 |  | 16.6599 | 16.7195 | 16.4645 | 16.7566 | 16.9131 | 17.3821 | 17.652 | 15.4044 | 16.6487 | 15.7146 | 16.8374 | 17.8851 | 44.9743 | 47.3131 | 43.7914 | 21.2881 |  |  | 0.53907 | -0.036205 | -31.3787 | 0.07881 | 0.1585 | -197.8591 | 19.9483 | -0.36703 | -0.20521 | -0.046255 | 0.0030688 | 8.8298 | 9.0594 | 1.9776 | 21.8323 | 22.0576 | 22.253 | 22.3265 | 22.1595 | 21.515 | 20.3515 | 22.2381 | 22.4166 | 22.4484 | 22.3991 | 22.0477 | 21.2982 | 22.3142 | 17.0298 | 16.8734 | 15.8854 | 15.9888 | 16.0324 | 17.0803 | 16.7021 | 22.399 | 22.1738 | 21.7468 | 22.1128 | 21.8373 | 21.3479 | 21.9798 | 21.5747 | 20.9625 | 20.1631 | 20.5127 | 20.0881 | 19.8561 | -0.11677 | -0.15707 | 20.6691 | 22.0823 | 22.4066 | 20.0984 | 21.7066 | 22.162 | 21.9728 | 21.7476 | 21.3279 | 21.8384 | 21.5057 | 21.1123 | 20.5461 | 20.5762 | 20.6109 | 20.6499 | 20.0758 |  | 20.2258 | 19.6311 | 20.1314 | 19.8271 | 20.1255 | 20.3977 |  | 20.4899 |  |  | 20.2013 | 20.3673 | 20.5992 | [5 empty] | 21.9813 | 20.3976 | 21.73 | 22.1355 | 19.6508 | 21.2801 | 21.9256 | 19.4014 | 19.9926 | 21.184 |  | 19.5951 | 20.9961 | 18.8718 | 19.713 | 20.8561 | 19.3944 | 20.1854 | 19.0229 | 20.1843 | 19.2237 | 20.3571 | 18.7822 | 20.1074 | 21.1263 | 19.3724 | 19.8281 | 21.0585 | 19.0126 | 19.829 | 20.883 | 18.9556 | 20.2621 | 19.3074 | 20.1063 | 19.0066 | 20.2817 | -0.11867 | 20.9493 | 0.046662 | 0.012909 | -26.9805 | 2.3091 | -0.95 | -0.14 | 0.87689 | -0.22576 | -6.6464 | 0.33309 | 0.4729 | -16.7087 | 5.3054 | 0.4242 | 0.43339 | 0.42775 | 0.40791 | 0.49096 | 0.44237 | 0.4282
42838.4111 | -792 | 22.9072 | 22.8817 | 22.8729 | 22.8064 | 22.4543 | 21.8041 | 22.7584 | 21.882 | 22.405 | 22.4188 | 22.4041 | 22.0958 | 21.3241 | 22.2795 | 21.5981 | 21.7735 | 21.917 | 21.1084 | 21.2012 | 21.4304 | 20.5073 | 20.6558 | 20.9549 | 21.938 | 21.6952 | 21.3337 | 20.476 | 20.5661 | 20.5524 | 22.061 | 21.6749 | 21.2096 | 22.0225 | 21.7692 | 21.3805 | 19.9621 | 20.449 |  | 20.5902 | 20.2997 | 20.3896 | 19.1198 |  | 16.6599 | 16.7166 | 16.4554 | 16.7428 | 16.8981 | 17.3565 | 17.6367 | 15.4673 | 16.6538 | 15.7295 | 16.8333 | 17.8799 | 44.9483 | 47.2893 | 43.7611 | 21.2869 |  |  | 0.4451 | -0.13017 | -31.7086 | 0.20498 | 0.24261 | -197.8282 | 20.2677 | -0.54314 | -0.2021 | -0.13626 | -0.0037016 | 8.8282 | 9.058 | 1.9783 | 21.8217 | 22.0574 | 22.2504 | 22.3205 | 22.1637 | 21.513 | 20.341 | 22.2356 | 22.418 | 22.4495 | 22.3987 | 22.0454 | 21.293 | 22.3133 | 16.9645 | 16.8884 | 15.8738 | 16.0184 | 16.0524 | 17.0716 | 16.698 | 22.3957 | 22.1739 | 21.7341 | 22.1022 | 21.8283 | 21.3453 | 21.9739 | 21.5691 | 20.9535 | 20.1562 | 20.5046 | 20.0847 | 19.8547 | -0.18872 | -0.12455 | 20.6821 | 22.0925 | 22.4061 | 20.1142 | 21.7142 | 22.1651 | 21.9824 | 21.7504 | 21.3304 | 21.8391 | 21.5125 | 21.1181 | 20.5528 | 20.5818 | 20.6232 | 20.6573 | 20.0803 |  | 20.2258 | 19.6435 | 20.1262 | 19.8254 | 20.1213 | 20.4032 |  | 20.4816 |  |  | 20.1952 | 20.3507 | 20.5827 | [5 empty] | 21.9648 | 20.3927 | 21.713 | 22.1066 | 19.6377 | 21.2665 | 21.9109 | 19.4036 | 19.9867 | 21.1806 |  | 19.5889 | 20.9982 | 18.8857 | 19.708 | 20.8521 | 19.4001 | 20.1878 | 19.0182 | 20.1726 | 19.2218 | 20.3536 | 18.7844 | 20.106 | 21.1264 | 19.3768 | 19.831 | 21.0653 | 19.0159 | 19.818 | 20.8848 | 18.9599 | 20.2577 | 19.3135 | 20.1076 | 19.0096 | 20.2869 | -0.065985 | 20.9525 | 0.046515 | 0.012865 | -27.1618 | 2.4149 | -0.91 | -0.02 | 0.7968 | -0.42808 | -6.6812 | 0.53718 | 0.58506 | -16.7066 | 5.3475 | 0.42407 | 0.43287 | 0.42765 | 0.41415 | 0.49176 | 0.44192 | 0.42801
42838.4111 | -791 | 22.9205 | 22.8833 | 22.8698 | 22.8045 | 22.4585 | 21.8166 | 22.7543 | 21.8697 | 22.4041 | 22.4187 | 22.4093 | 22.0997 | 21.3303 | 22.2767 | 21.6023 | 21.7775 | 21.9211 | 21.1127 | 21.2059 | 21.4251 | 20.5014 | 20.66 | 20.9495 | 21.9284 | 21.6938 | 21.3336 | 20.4802 | 20.5727 | 20.565 | 22.0674 | 21.6751 | 21.2114 | 22.0257 | 21.7695 | 21.3845 | 19.9617 | 20.4496 |  | 20.5954 | 20.3088 | 20.3849 | 19.1427 |  | 16.6571 | 16.7044 | 16.4469 | 16.722 | 16.8688 | 17.3728 | 17.654 | 15.5215 | 16.6462 | 15.7375 | 16.8279 | 17.8871 | 44.9214 | 47.2695 | 43.748 | 21.2969 |  |  | 0.4221 | -0.10061 | -31.9603 | 0.17606 | -0.048496 | -197.8217 | 20.0738 | -0.54774 | -0.070741 | -0.44026 | -0.15196 | 8.8299 | 9.0597 | 1.9787 | 21.8191 | 22.0501 | 22.2456 | 22.312 | 22.1618 | 21.5046 | 20.3333 | 22.232 | 22.4116 | 22.4415 | 22.395 | 22.0375 | 21.2868 | 22.3089 | 16.8926 | 16.8979 | 15.8738 | 16.0292 | 16.0684 | 17.0746 | 16.6919 | 22.393 | 22.1689 | 21.7361 | 22.1045 | 21.8289 | 21.3422 | 21.9674 | 21.5732 | 20.9524 | 20.1561 | 20.5052 | 20.0864 | 19.8552 | -0.053266 | -0.09564 | 20.6864 | 22.0935 | 22.4115 | 20.1166 | 21.7178 | 22.1716 | 21.9868 | 21.7561 | 21.3292 | 21.8443 | 21.5137 | 21.1206 | 20.5571 | 20.586 | 20.6252 | 20.6663 | 20.0977 |  | 20.2288 | 19.6643 | 20.1272 | 19.8269 | 20.1243 | 20.4029 |  | 20.4882 |  |  | 20.2045 | 20.359 | 20.5865 | [5 empty] | 21.9765 | 20.3904 | 21.7227 | 22.1132 | 19.6388 | 21.2692 | 21.9134 | 19.3944 | 19.9851 | 21.1875 |  | 19.5944 | 21.0011 | 18.8865 | 19.7066 | 20.8513 | 19.3985 | 20.1844 | 19.0142 | 20.1653 | 19.2093 | 20.3406 | 18.7771 | 20.1046 | 21.1248 | 19.3682 | 19.8313 | 21.0625 | 19.009 | 19.8035 | 20.8895 | 18.9544 | 20.2457 | 19.3084 | 20.1045 | 18.9936 | 20.2765 | -0.12479 | 20.9499 | 0.04606 | 0.013097 | -27.0764 | 2.5174 | -0.91 | -0.13 | 0.77596 | -0.37633 | -6.7075 | 0.49784 | -0.26158 | -16.7068 | 5.322 | 0.42369 | 0.43232 | 0.42771 | 0.4225 | 0.49105 | 0.44127 | 0.42799
42838.4111 | -790 | 22.9094 | 22.8695 | 22.8653 | 22.8043 | 22.4559 | 21.8045 | 22.7577 | 21.8738 | 22.3987 | 22.4216 | 22.4051 | 22.0923 | 21.3133 | 22.2759 | 21.6027 | 21.7821 | 21.9242 | 21.1045 | 21.2126 | 21.4321 | 20.5069 | 20.6551 | 20.9561 | 21.931 | 21.6945 | 21.3283 | 20.4782 | 20.5676 | 20.5565 | 22.058 | 21.6731 | 21.199 | 22.0157 | 21.7588 | 21.376 | 19.9539 | 20.4416 |  | 20.5924 | 20.3011 | 20.3785 | 19.1461 |  | 16.6494 | 16.6938 | 16.4303 | 16.7039 | 16.8567 | 17.3824 | 17.667 | 15.5611 | 16.6468 | 15.6901 | 16.8308 | 17.8834 | 44.8748 | 47.2511 | 43.7367 | 21.2972 |  |  | 0.44181 | -0.2524 | -32.783 | 0.27266 | 0.15915 | -197.8263 | 19.7256 | -0.48334 | -0.30718 | -0.35109 | -0.094668 | 8.829 | 9.0587 | 1.9784 | 21.8243 | 22.0538 | 22.2471 | 22.3188 | 22.1575 | 21.5048 | 20.3379 | 22.2396 | 22.4089 | 22.4418 | 22.3996 | 22.0358 | 21.2925 | 22.3122 | 16.8441 | 16.9214 | 15.8842 | 16.0404 | 16.0781 | 17.0733 | 16.6944 | 22.3972 | 22.1773 | 21.7432 | 22.1101 | 21.8313 | 21.3484 | 21.9772 | 21.5704 | 20.9597 | 20.1577 | 20.5087 | 20.0918 | 19.8716 | 0.050342 | -0.10515 | 20.6855 | 22.0956 | 22.4131 | 20.1045 | 21.7138 | 22.163 | 21.9849 | 21.7569 | 21.324 | 21.8411 | 21.512 | 21.1144 | 20.5566 | 20.5766 | 20.6215 | 20.6604 | 20.0808 |  | 20.2181 | 19.651 | 20.1259 | 19.8098 | 20.1125 | 20.3981 |  | 20.4865 |  |  | 20.2093 | 20.3631 | 20.5956 | [5 empty] | 21.969 | 20.4038 | 21.7214 | 22.1196 | 19.6413 | 21.2786 | 21.9172 | 19.4148 | 19.9931 | 21.1851 |  | 19.6001 | 20.9968 | 18.8886 | 19.7076 | 20.8527 | 19.3957 | 20.1871 | 19.0183 | 20.1731 | 19.2122 | 20.3327 | 18.7989 | 20.114 | 21.1379 | 19.3971 | 19.846 | 21.0672 | 19.0271 | 19.8255 | 20.8922 | 18.9721 | 20.2576 | 19.3182 | 20.1204 | 19.0011 | 20.2732 | 0.023983 | 20.9518 | 0.046478 | 0.01338 | -27.0634 | 2.6165 | -1.1 | -0.06 | 0.79386 | -0.59606 | -6.7932 | 0.61952 | 0.47388 | -16.7073 | 5.2757 | 0.4238 | 0.43265 | 0.42779 | 0.42774 | 0.49019 | 0.44092 | 0.42759
42838.4111 | -789 | 22.9029 | 22.8787 | 22.8699 | 22.8126 | 22.4585 | 21.8084 | 22.7551 | 21.8738 | 22.3983 | 22.4143 | 22.4097 | 22.092 | 21.3187 | 22.2739 | 21.5952 | 21.7704 | 21.912 | 21.1018 | 21.2023 | 21.4261 | 20.5034 | 20.6498 | 20.9526 | 21.9241 | 21.6903 | 21.3304 | 20.4798 | 20.5645 | 20.553 | 22.0639 | 21.6742 | 21.2079 | 22.0189 | 21.7593 | 21.3775 | 19.9537 | 20.448 |  | 20.5883 | 20.3004 | 20.3828 | 19.1627 |  | 16.6415 | 16.6973 | 16.419 | 16.694 | 16.8585 | 17.4005 | 17.6833 | 15.6059 | 16.6506 | 15.6891 | 16.8292 | 17.884 | 44.8341 | 47.2304 | 43.7115 | 21.2946 |  |  | 0.49307 | -0.43639 | -33.3389 | 0.38437 | 0.4128 | -197.8572 | 19.8011 | -0.41763 | 0.031813 | -0.031778 | -0.084946 | 8.8289 | 9.0587 | 1.9778 | 21.8184 | 22.0538 | 22.244 | 22.3202 | 22.1599 | 21.5057 | 20.3434 | 22.2372 | 22.4069 | 22.4431 | 22.3995 | 22.0374 | 21.288 | 22.3116 | 16.8262 | 16.9779 | 15.9123 | 16.0499 | 16.1022 | 17.0793 | 16.6999 | 22.3909 | 22.1684 | 21.7462 | 22.1044 | 21.8255 | 21.3437 | 21.969 | 21.5663 | 20.9571 | 20.1591 | 20.5116 | 20.087 | 19.8716 | 0.015347 | -0.12892 | 20.6885 | 22.0929 | 22.4135 | 20.1064 | 21.7112 | 22.161 | 21.9805 | 21.7557 | 21.3287 | 21.8448 | 21.5138 | 21.1168 | 20.5537 | 20.5767 | 20.6199 | 20.6643 | 20.0845 |  | 20.2239 | 19.6496 | 20.1262 | 19.8 | 20.1165 | 20.404 |  | 20.4799 |  |  | 20.2157 | 20.3602 | 20.5935 | [5 empty] | 21.9715 | 20.4006 | 21.7195 | 22.123 | 19.6406 | 21.2688 | 21.9208 | 19.4191 | 20.0023 | 21.1991 |  | 19.6057 | 20.9979 | 18.9049 | 19.7159 | 20.8625 | 19.3963 | 20.1924 | 19.0243 | 20.1761 | 19.2136 | 20.3477 | 18.7814 | 20.091 | 21.1237 | 19.3826 | 19.832 | 21.0606 | 19.0069 | 19.8038 | 20.87 | 18.9584 | 20.2468 | 19.3141 | 20.1105 | 18.9877 | 20.2591 | -0.15465 | 20.9514 | 0.04622 | 0.012364 | -27.0287 | 2.7126 | -0.9 | 0.21 | 0.83864 | -0.78377 | -6.8506 | 0.73557 | 0.76322 | -16.7091 | 5.2859 | 0.42389 | 0.4327 | 0.4282 | 0.43042 | 0.48771 | 0.44045 | 0.42764
42838.4112 | -788 | 22.8995 | 22.8812 | 22.8703 | 22.8113 | 22.4625 | 21.8118 | 22.7524 | 21.8718 | 22.4019 | 22.4175 | 22.4003 | 22.0983 | 21.3222 | 22.2821 | 21.5946 | 21.7773 | 21.9156 | 21.1046 | 21.2071 | 21.4327 | 20.5115 | 20.6573 | 20.9529 | 21.9309 | 21.6943 | 21.3362 | 20.4762 | 20.5658 | 20.5466 | 22.062 | 21.6718 | 21.2028 | 22.0159 | 21.7553 | 21.383 | 19.9542 | 20.457 |  | 20.5916 | 20.2995 | 20.3804 | 19.1681 |  | 16.6294 | 16.6833 | 16.4076 | 16.6732 | 16.834 | 17.4103 | 17.7095 | 15.6049 | 16.6512 | 15.6486 | 16.8329 | 17.8819 | 44.7859 | 47.2046 | 43.6893 | 21.2969 |  |  | 0.43787 | -0.26882 | -32.9348 | 0.39685 | 0.15521 | -197.842 | 19.8833 | -0.38806 | -0.23537 | -0.33305 | -0.12609 | 8.8299 | 9.0592 | 1.9782 | 21.8231 | 22.0544 | 22.2502 | 22.3189 | 22.1639 | 21.509 | 20.341 | 22.2309 | 22.4062 | 22.4455 | 22.3999 | 22.0364 | 21.294 | 22.3146 | 16.811 | 17.0073 | 15.8826 | 16.0466 | 16.1129 | 17.0809 | 16.6955 | 22.3987 | 22.178 | 21.7508 | 22.1112 | 21.8325 | 21.3495 | 21.9785 | 21.5721 | 20.9595 | 20.1592 | 20.5103 | 20.1038 | 19.8671 | -0.009228 | -0.20291 | 20.6931 | 22.0926 | 22.4155 | 20.1121 | 21.7096 | 22.1657 | 21.9816 | 21.7565 | 21.3339 | 21.8464 | 21.5139 | 21.1208 | 20.5519 | 20.5762 | 20.6217 | 20.6633 | 20.0872 |  | 20.2223 | 19.6555 | 20.1225 | 19.7978 | 20.1154 | 20.41 |  | 20.4805 |  |  | 20.2227 | 20.3504 | 20.5953 | [5 empty] | 21.9661 | 20.392 | 21.718 | 22.1225 | 19.6386 | 21.2677 | 21.9167 | 19.4112 | 19.9976 | 21.1875 |  | 19.5937 | 20.9999 | 18.9011 | 19.7074 | 20.8609 | 19.3988 | 20.1904 | 19.0173 | 20.1728 | 19.2057 | 20.3343 | 18.7837 | 20.1063 | 21.1307 | 19.386 | 19.8381 | 21.0691 | 19.0196 | 19.8142 | 20.8868 | 18.9674 | 20.2517 | 19.3213 | 20.1146 | 18.9936 | 20.255 | 0.023426 | 20.9516 | 0.046846 | 0.011791 | -26.9608 | 2.8051 | -0.78 | -0.05 | 0.79029 | -0.61514 | -6.8088 | 0.74741 | 0.468 | -16.7088 | 5.297 | 0.42376 | 0.43241 | 0.42822 | 0.43229 | 0.4905 | 0.44031 | 0.42776
42838.4112 | -787 | 22.9044 | 22.8861 | 22.8644 | 22.8057 | 22.4524 | 21.8095 | 22.7595 | 21.8719 | 22.4058 | 22.4135 | 22.4093 | 22.0956 | 21.3231 | 22.2756 | 21.6018 | 21.7778 | 21.9152 | 21.1062 | 21.1996 | 21.4292 | 20.5034 | 20.6502 | 20.9528 | 21.9277 | 21.6914 | 21.3288 | 20.4717 | 20.5682 | 20.5479 | 22.058 | 21.6689 | 21.1936 | 22.0182 | 21.7523 | 21.3794 | 19.9522 | 20.4601 |  | 20.5913 | 20.2985 | 20.3783 | 19.1673 |  | 16.6231 | 16.6865 | 16.4118 | 16.6637 | 16.8256 | 17.3963 | 17.7162 | 15.5844 | 16.6609 | 15.6187 | 16.8286 | 17.8754 | 44.7427 | 47.1776 | 43.6702 | 21.2928 |  |  | 0.36953 | -0.35031 | -32.3263 | 0.48688 | 0.17361 | -197.8059 | 19.9365 | -0.34075 | -0.17446 | 0.02277 | -0.066718 | 8.8301 | 9.0599 | 1.9789 | 21.8259 | 22.0621 | 22.2511 | 22.3161 | 22.1636 | 21.5161 | 20.3443 | 22.2375 | 22.4071 | 22.4457 | 22.4044 | 22.0466 | 21.2903 | 22.314 | 16.8068 | 17.0248 | 15.8414 | 16.0021 | 16.1301 | 17.0712 | 16.687 | 22.3923 | 22.1741 | 21.7459 | 22.1095 | 21.8396 | 21.3487 | 21.9732 | 21.575 | 20.9594 | 20.1572 | 20.5094 | 20.0977 | 19.8721 | -0.021614 | -0.1915 | 20.6995 | 22.0918 | 22.4136 | 20.1106 | 21.7103 | 22.1708 | 21.9812 | 21.7543 | 21.3318 | 21.8407 | 21.5094 | 21.1165 | 20.5569 | 20.57 | 20.6253 | 20.6618 | 20.0975 |  | 20.2158 | 19.6542 | 20.1155 | 19.7874 | 20.1099 | 20.4079 |  | 20.4782 |  |  | 20.2302 | 20.3543 | 20.5971 | [5 empty] | 21.9715 | 20.3911 | 21.7242 | 22.1261 | 19.6487 | 21.2698 | 21.9142 | 19.4133 | 19.9971 | 21.1873 |  | 19.5904 | 20.993 | 18.9051 | 19.7015 | 20.8479 | 19.3967 | 20.1904 | 19.019 | 20.1767 | 19.208 | 20.3332 | 18.7808 | 20.094 | 21.1292 | 19.3863 | 19.838 | 21.0679 | 19.0155 | 19.7997 | 20.8873 | 18.9644 | 20.2417 | 19.3094 | 20.1107 | 18.9836 | 20.2435 | 0.036226 | 20.9519 | 0.047399 | 0.011566 | -27.2157 | 2.8937 | -0.73 | 0 | 0.72601 | -0.70221 | -6.7456 | 0.82785 | 0.49495 | -16.7068 | 5.3039 | 0.42326 | 0.43221 | 0.42832 | 0.43163 | 0.49408 | 0.44027 | 0.42755
42838.4112 | -786 | 22.9023 | 22.8833 | 22.8713 | 22.8032 | 22.4571 | 21.805 | 22.7574 | 21.873 | 22.4082 | 22.4103 | 22.4021 | 22.0851 | 21.3171 | 22.2706 | 21.5952 | 21.7765 | 21.9156 | 21.1025 | 21.2016 | 21.4218 | 20.5025 | 20.6488 | 20.9484 | 21.9259 | 21.6945 | 21.3253 | 20.4806 | 20.5703 | 20.5469 | 22.065 | 21.6782 | 21.2057 | 22.0244 | 21.7548 | 21.3788 | 19.9585 | 20.4668 |  | 20.5967 | 20.2995 | 20.3859 | 19.1792 |  | 16.6215 | 16.6936 | 16.422 | 16.6632 | 16.805 | 17.3868 | 17.6961 | 15.5807 | 16.6522 | 15.6056 | 16.8313 | 17.8847 | 44.7126 | 47.1761 | 43.6574 | 21.3032 |  |  | 0.41553 | -0.10323 | -32.1725 | 0.51316 | -0.046524 | -197.8558 | 20.0568 | -0.35455 | -0.069379 | 0.068506 | 0.015047 | 8.8298 | 9.0595 | 1.9786 | 21.827 | 22.0596 | 22.2536 | 22.3159 | 22.1644 | 21.5041 | 20.3457 | 22.2392 | 22.4093 | 22.4501 | 22.3957 | 22.0396 | 21.2864 | 22.3104 | 16.8021 | 16.9995 | 15.8304 | 15.9692 | 16.1342 | 17.0759 | 16.6956 | 22.3884 | 22.1633 | 21.7387 | 22.1036 | 21.8267 | 21.3412 | 21.9719 | 21.5709 | 20.9626 | 20.1622 | 20.5099 | 20.0987 | 19.8704 | -0.076072 | -0.20158 | 20.7047 | 22.0943 | 22.4092 | 20.1151 | 21.7091 | 22.1704 | 21.9842 | 21.7498 | 21.3305 | 21.8395 | 21.5092 | 21.1154 | 20.555 | 20.56 | 20.6229 | 20.6605 | 20.1044 |  | 20.2216 | 19.6531 | 20.1239 | 19.7807 | 20.1133 | 20.3987 |  | 20.4754 |  |  | 20.229 | 20.3503 | 20.5953 | [5 empty] | 21.974 | 20.3944 | 21.7273 | 22.1225 | 19.6477 | 21.2659 | 21.9123 | 19.4257 | 20.008 | 21.2007 |  | 19.5984 | 21.0035 | 18.9211 | 19.7188 | 20.8623 | 19.4074 | 20.1993 | 19.0324 | 20.1896 | 19.222 | 20.3485 | 18.7827 | 20.0962 | 21.1348 | 19.3877 | 19.847 | 21.0763 | 19.0201 | 19.8009 | 20.8898 | 18.9698 | 20.2466 | 19.3164 | 20.116 | 18.9913 | 20.2401 | 0.028805 | 20.9511 | 0.04783 | 0.011057 | -26.9604 | 2.9762 | -1.04 | -0.16 | 0.76987 | -0.3812 | -6.7296 | 0.84992 | -0.25622 | -16.7087 | 5.3198 | 0.42326 | 0.43252 | 0.42863 | 0.4327 | 0.49631 | 0.44015 | 0.42777
42838.4112 | -785 | 22.9059 | 22.8755 | 22.8686 | 22.8032 | 22.4613 | 21.8064 | 22.7531 | 21.8715 | 22.407 | 22.4056 | 22.4021 | 22.0924 | 21.3249 | 22.2747 | 21.5951 | 21.7719 | 21.9217 | 21.1013 | 21.2037 | 21.4244 | 20.5019 | 20.6541 | 20.9477 | 21.9299 | 21.6912 | 21.3275 | 20.4816 | 20.5699 | 20.5467 | 22.0668 | 21.6778 | 21.2071 | 22.0187 | 21.7592 | 21.3837 | 19.9596 | 20.4673 |  | 20.599 | 20.3048 | 20.3823 | 19.1902 |  | 16.6289 | 16.703 | 16.4288 | 16.652 | 16.7887 | 17.3737 | 17.672 | 15.5878 | 16.6516 | 15.6399 | 16.8363 | 17.8804 | 44.6706 | 47.1581 | 43.6364 | 21.3002 |  |  | 0.23285 | -0.1788 | -31.5759 | 0.28251 | 0.031016 | -197.8729 | 20.3965 | -0.45246 | -0.11102 | 0.020672 | 0.0035896 | 8.8274 | 9.0573 | 1.9781 | 21.8203 | 22.0527 | 22.244 | 22.3205 | 22.1622 | 21.5047 | 20.3427 | 22.2354 | 22.4041 | 22.4441 | 22.3898 | 22.0442 | 21.2879 | 22.3118 | 16.7472 | 16.9782 | 15.8376 | 15.9767 | 16.1209 | 17.0689 | 16.696 | 22.3936 | 22.1709 | 21.7369 | 22.1006 | 21.8283 | 21.3401 | 21.9737 | 21.5676 | 20.9566 | 20.1598 | 20.5141 | 20.1054 | 19.8755 | -0.23414 | -0.17971 | 20.7098 | 22.0958 | 22.4135 | 20.1225 | 21.712 | 22.1658 | 21.9896 | 21.7549 | 21.3353 | 21.8477 | 21.5179 | 21.1138 | 20.5597 | 20.5575 | 20.6248 | 20.6662 | 20.1032 |  | 20.2228 | 19.6582 | 20.1266 | 19.7795 | 20.1204 | 20.4088 |  | 20.4792 |  |  | 20.2347 | 20.3512 | 20.6015 | [5 empty] | 21.975 | 20.4007 | 21.7223 | 22.1173 | 19.6424 | 21.2677 | 21.9117 | 19.4295 | 20.0094 | 21.1983 |  | 19.5933 | 21.0036 | 18.9151 | 19.7126 | 20.8611 | 19.3998 | 20.1956 | 19.025 | 20.1868 | 19.2154 | 20.3385 | 18.7812 | 20.095 | 21.1423 | 19.3944 | 19.8518 | 21.0738 | 19.0312 | 19.8178 | 20.8967 | 18.9716 | 20.2574 | 19.3273 | 20.1219 | 18.9983 | 20.2418 | -0.072107 | 20.9523 | 0.047744 | 0.011333 | -26.8304 | 3.0386 | -1.22 | -0.01 | 0.57631 | -0.5017 | -6.667 | 0.63063 | 0.20919 | -16.709 | 5.3646 | 0.42334 | 0.43247 | 0.4289 | 0.43799 | 0.49555 | 0.43988 | 0.42755
42838.4112 | -784 | 22.9149 | 22.8751 | 22.8761 | 22.8058 | 22.4551 | 21.8093 | 22.7555 | 21.868 | 22.409 | 22.413 | 22.3937 | 22.0953 | 21.3281 | 22.2753 | 21.5986 | 21.7757 | 21.9234 | 21.0999 | 21.2042 | 21.4348 | 20.5035 | 20.6608 | 20.9554 | 21.9309 | 21.6937 | 21.336 | 20.4799 | 20.578 | 20.5421 | 22.0662 | 21.6777 | 21.2121 | 22.0189 | 21.7697 | 21.3877 | 19.9581 | 20.4824 |  | 20.6053 | 20.3023 | 20.3876 | 19.1946 |  | 16.6299 | 16.6964 | 16.4364 | 16.6674 | 16.777 | 17.3575 | 17.6379 | 15.6141 | 16.6456 | 15.6353 | 16.8268 | 17.8793 | 44.6285 | 47.1405 | 43.6214 | 21.3064 |  |  | 0.31367 | -0.072349 | -31.4766 | 0.59727 | 0.086872 | -197.8893 | 20.3137 | -0.28949 | -0.32898 | 0.038714 | -0.018631 | 8.8289 | 9.0585 | 1.9782 | 21.8153 | 22.0507 | 22.241 | 22.319 | 22.1574 | 21.5027 | 20.3365 | 22.2309 | 22.4035 | 22.4382 | 22.3945 | 22.0474 | 21.2915 | 22.3058 | 16.6435 | 16.9201 | 15.8488 | 15.9682 | 16.1167 | 17.0697 | 16.6881 | 22.3902 | 22.1738 | 21.7425 | 22.0993 | 21.832 | 21.3434 | 21.9751 | 21.5659 | 20.9549 | 20.1518 | 20.511 | 20.1102 | 19.8837 | -0.16218 | -0.084988 | 20.7164 | 22.0881 | 22.4164 | 20.1219 | 21.7162 | 22.171 | 21.988 | 21.7584 | 21.3365 | 21.8457 | 21.5195 | 21.1186 | 20.5595 | 20.5624 | 20.6318 | 20.6736 | 20.1009 |  | 20.2332 | 19.6575 | 20.129 | 19.772 | 20.1286 | 20.4126 |  | 20.4855 |  |  | 20.2314 | 20.3601 | 20.6007 | [5 empty] | 21.9734 | 20.4059 | 21.7206 | 22.12 | 19.6433 | 21.2682 | 21.9107 | 19.4254 | 20.0016 | 21.1867 |  | 19.5829 | 20.995 | 18.8986 | 19.7049 | 20.8475 | 19.3979 | 20.192 | 19.0159 | 20.1843 | 19.206 | 20.329 | 18.7842 | 20.0863 | 21.1386 | 19.3965 | 19.8425 | 21.0665 | 19.016 | 19.813 | 20.8856 | 18.9692 | 20.2427 | 19.3194 | 20.1177 | 18.9928 | 20.235 | -0.089173 | 20.9508 | 0.047916 | 0.011929 | -26.8913 | 3.0594 | -1.19 | 0.05 | 0.66889 | -0.31913 | -6.6565 | 0.91693 | 0.35009 | -16.7092 | 5.3535 | 0.42375 | 0.43257 | 0.42938 | 0.44961 | 0.49339 | 0.43971 | 0.42705
42838.4112 | -783 | 22.9124 | 22.8758 | 22.8735 | 22.8113 | 22.4605 | 21.8159 | 22.7584 | 21.8743 | 22.4019 | 22.4174 | 22.4048 | 22.0973 | 21.3267 | 22.2798 | 21.5961 | 21.7693 | 21.9139 | 21.0959 | 21.2059 | 21.4286 | 20.5048 | 20.6555 | 20.9525 | 21.9235 | 21.6943 | 21.3318 | 20.4691 | 20.5744 | 20.5406 | 22.0549 | 21.6634 | 21.2054 | 22.0137 | 21.7474 | 21.3737 | 19.9503 | 20.4824 |  | 20.5908 | 20.2964 | 20.376 | 19.1979 |  | 16.6417 | 16.722 | 16.4514 | 16.6809 | 16.7937 | 17.3413 | 17.6269 | 15.6624 | 16.6519 | 15.6462 | 16.8268 | 17.8758 | 44.6008 | 47.1221 | 43.6029 | 21.3027 |  |  | 0.26571 | -0.29511 | -30.8951 | 0.2812 | 0.14141 | -197.8552 | 20.4661 | -0.32563 | -0.35972 | 0.21495 | -0.03061 | 8.8281 | 9.0578 | 1.9792 | 21.8195 | 22.0486 | 22.2537 | 22.318 | 22.1534 | 21.5079 | 20.3353 | 22.2344 | 22.4117 | 22.4396 | 22.3995 | 22.0407 | 21.2945 | 22.311 | 16.5922 | 16.8868 | 15.8263 | 15.9639 | 16.1152 | 17.0747 | 16.6838 | 22.4024 | 22.1758 | 21.7437 | 22.1184 | 21.8345 | 21.3528 | 21.9815 | 21.5773 | 20.9619 | 20.1633 | 20.5183 | 20.1206 | 19.8944 | -0.11932 | -0.074908 | 20.7119 | 22.0887 | 22.4085 | 20.1162 | 21.7097 | 22.1611 | 21.9759 | 21.751 | 21.3273 | 21.8386 | 21.5124 | 21.1114 | 20.5472 | 20.5522 | 20.6216 | 20.6604 | 20.0972 |  | 20.2219 | 19.6408 | 20.1239 | 19.7597 | 20.1168 | 20.4147 |  | 20.4773 |  |  | 20.2232 | 20.3655 | 20.6013 | [5 empty] | 21.9752 | 20.4031 | 21.7194 | 22.1217 | 19.6499 | 21.2674 | 21.9102 | 19.4352 | 20.0005 | 21.1956 |  | 19.5896 | 20.9967 | 18.8975 | 19.7206 | 20.8519 | 19.4111 | 20.2002 | 19.026 | 20.1977 | 19.213 | 20.3304 | 18.7854 | 20.0832 | 21.1347 | 19.3989 | 19.8408 | 21.0633 | 19.0065 | 19.8098 | 20.8845 | 18.9641 | 20.2374 | 19.32 | 20.1153 | 18.9877 | 20.2279 | -0.08064 | 20.9514 | 0.047793 | 0.0128 | -27.0133 | 3.0618 | -1.11 | -0.01 | 0.61562 | -0.64456 | -6.595 | 0.62919 | 0.44666 | -16.7073 | 5.3734 | 0.42347 | 0.43287 | 0.42933 | 0.45588 | 0.49539 | 0.43935 | 0.42714
42838.4112 | -782 | 22.8969 | 22.8717 | 22.8626 | 22.7953 | 22.4534 | 21.8052 | 22.7446 | 21.8627 | 22.4011 | 22.4113 | 22.3952 | 22.0907 | 21.316 | 22.2679 | 21.5981 | 21.7724 | 21.9126 | 21.0979 | 21.2026 | 21.43 | 20.5078 | 20.6548 | 20.9477 | 21.9248 | 21.6931 | 21.3324 | 20.4711 | 20.5771 | 20.5417 | 22.0591 | 21.6729 | 21.2075 | 22.0238 | 21.7609 | 21.3856 | 19.9613 | 20.4976 |  | 20.6028 | 20.3057 | 20.3778 | 19.2178 |  | 16.6514 | 16.7239 | 16.4499 | 16.6695 | 16.8078 | 17.3321 | 17.6268 | 15.6775 | 16.651 | 15.6953 | 16.8214 | 17.8781 | 44.5709 | 47.1204 | 43.5955 | 21.3012 |  |  | 0.30447 | -0.35622 | -30.6231 | 0.40277 | 0.13681 | -197.8092 | 20.6179 | -0.20538 | -0.11803 | 0.025497 | 0.016262 | 8.8292 | 9.0591 | 1.9789 | 21.8218 | 22.0499 | 22.2516 | 22.3162 | 22.1541 | 21.5053 | 20.3402 | 22.2364 | 22.4129 | 22.4437 | 22.3989 | 22.0374 | 21.292 | 22.3095 | 16.5591 | 16.8825 | 15.8308 | 15.9498 | 16.1067 | 17.0635 | 16.6837 | 22.3953 | 22.1677 | 21.7486 | 22.1116 | 21.8316 | 21.3509 | 21.9758 | 21.5751 | 20.9482 | 20.1604 | 20.5113 | 20.113 | 19.8852 | -0.020238 | -0.013473 | 20.7134 | 22.0978 | 22.4152 | 20.1226 | 21.7131 | 22.164 | 21.9829 | 21.7554 | 21.3294 | 21.843 | 21.5166 | 21.1149 | 20.5504 | 20.5458 | 20.6208 | 20.6599 | 20.1119 |  | 20.2269 | 19.6475 | 20.1319 | 19.7741 | 20.1199 | 20.422 |  | 20.4847 |  |  | 20.2255 | 20.3681 | 20.6106 | [5 empty] | 21.9708 | 20.405 | 21.7194 | 22.121 | 19.6589 | 21.2668 | 21.9188 | 19.4325 | 19.9965 | 21.1926 |  | 19.5943 | 20.9929 | 18.893 | 19.7172 | 20.8516 | 19.406 | 20.1979 | 19.0312 | 20.2032 | 19.2119 | 20.3218 | 18.7864 | 20.0841 | 21.1407 | 19.4008 | 19.8461 | 21.069 | 19.0049 | 19.8175 | 20.8861 | 18.9647 | 20.2419 | 19.3295 | 20.1174 | 18.9958 | 20.2287 | -0.064687 | 20.9519 | 0.047277 | 0.013322 | -27.0441 | 3.0623 | -1.18 | 0.04 | 0.659 | -0.70816 | -6.5659 | 0.75301 | 0.43933 | -16.7051 | 5.3932 | 0.42323 | 0.43295 | 0.42903 | 0.45826 | 0.49488 | 0.43917 | 0.4273
42838.4112 | -781 | 22.9031 | 22.876 | 22.8689 | 22.8058 | 22.4565 | 21.8023 | 22.749 | 21.8636 | 22.3964 | 22.4148 | 22.3969 | 22.0899 | 21.3222 | 22.2785 | 21.6038 | 21.7813 | 21.9237 | 21.1066 | 21.2088 | 21.4383 | 20.51 | 20.6624 | 20.958 | 21.9315 | 21.6986 | 21.3412 | 20.4777 | 20.5864 | 20.5429 | 22.06 | 21.6635 | 21.1969 | 22.018 | 21.7549 | 21.3734 | 19.9536 | 20.511 |  | 20.5943 | 20.3058 | 20.3798 | 19.2176 |  | 16.6449 | 16.7174 | 16.4388 | 16.6676 | 16.7941 | 17.3134 | 17.6435 | 15.683 | 16.6474 | 15.7604 | 16.8203 | 17.8819 | 44.5432 | 47.1175 | 43.574 | 21.3012 |  |  | 0.47007 | -0.24386 | -30.1414 | 0.22403 | 0.16507 | -197.8729 | 20.8223 | -0.25204 | -0.3496 | 0.1583 | 0.045427 | 8.8287 | 9.0586 | 1.9782 | 21.827 | 22.061 | 22.2501 | 22.3205 | 22.1605 | 21.5026 | 20.3393 | 22.2433 | 22.4133 | 22.4467 | 22.4062 | 22.0397 | 21.2926 | 22.3152 | 16.56 | 16.8984 | 15.8349 | 15.9295 | 16.103 | 17.0638 | 16.682 | 22.3816 | 22.169 | 21.7401 | 22.094 | 21.8289 | 21.3462 | 21.9734 | 21.5663 | 20.9525 | 20.1605 | 20.5034 | 20.1089 | 19.8782 | 0.063907 | 0.10673 | 20.7153 | 22.0998 | 22.4184 | 20.1289 | 21.7201 | 22.1739 | 21.9882 | 21.7593 | 21.335 | 21.8412 | 21.5209 | 21.1196 | 20.5564 | 20.548 | 20.6247 | 20.6661 | 20.1193 |  | 20.2301 | 19.6542 | 20.1314 | 19.7748 | 20.1285 | 20.4201 |  | 20.4817 |  |  | 20.2285 | 20.3699 | 20.6034 | [5 empty] | 21.9663 | 20.4033 | 21.7197 | 22.1155 | 19.6556 | 21.2626 | 21.918 | 19.4213 | 19.9973 | 21.1846 |  | 19.5949 | 20.9931 | 18.8863 | 19.7134 | 20.8472 | 19.4091 | 20.1992 | 19.0319 | 20.2109 | 19.2101 | 20.3222 | 18.7808 | 20.0745 | 21.1336 | 19.3992 | 19.8469 | 21.0685 | 18.9994 | 19.812 | 20.8801 | 18.9713 | 20.2288 | 19.3301 | 20.1087 | 18.9954 | 20.2201 | -0.027957 | 20.9502 | 0.046988 | 0.013809 | -27.0648 | 3.0626 | -1.28 | 0.01 | 0.81883 | -0.58591 | -6.514 | 0.5616 | 0.48255 | -16.7073 | 5.4197 | 0.42313 | 0.43275 | 0.4293 | 0.45819 | 0.49422 | 0.43892 | 0.4275
42838.4112 | -780 | 22.9098 | 22.8749 | 22.8678 | 22.801 | 22.4522 | 21.8044 | 22.7519 | 21.8708 | 22.4006 | 22.4122 | 22.401 | 22.0929 | 21.3154 | 22.282 | 21.595 | 21.7772 | 21.9236 | 21.1139 | 21.2072 | 21.434 | 20.509 | 20.659 | 20.9596 | 21.9271 | 21.7007 | 21.3428 | 20.4726 | 20.5873 | 20.5349 | 22.0544 | 21.665 | 21.1956 | 22.0087 | 21.7494 | 21.3772 | 19.9503 | 20.517 |  | 20.5889 | 20.3066 | 20.3796 | 19.2275 |  | 16.6476 | 16.72 | 16.4379 | 16.6765 | 16.8002 | 17.3159 | 17.6753 | 15.7012 | 16.6444 | 15.7727 | 16.818 | 17.8768 | 44.5258 | 47.1118 | 43.5543 | 21.3043 |  |  | 0.19934 | -0.3076 | -30.0408 | 0.24966 | 0.28729 | -197.819 | 21.0569 | -0.18632 | -0.40409 | 0.014587 | -0.11585 | 8.8289 | 9.0585 | 1.9776 | 21.8244 | 22.0592 | 22.2447 | 22.3216 | 22.1576 | 21.5096 | 20.3473 | 22.2383 | 22.4114 | 22.4439 | 22.4029 | 22.0498 | 21.2984 | 22.3135 | 16.569 | 16.9317 | 15.8392 | 15.9532 | 16.0841 | 17.064 | 16.6835 | 22.3884 | 22.1738 | 21.7389 | 22.1011 | 21.8297 | 21.3498 | 21.9726 | 21.5722 | 20.9534 | 20.1577 | 20.5057 | 20.1076 | 19.8744 | 0.09379 | -0.12892 | 20.7093 | 22.0937 | 22.4129 | 20.1245 | 21.7194 | 22.1703 | 21.9801 | 21.7525 | 21.3299 | 21.8351 | 21.5133 | 21.1168 | 20.549 | 20.5484 | 20.6194 | 20.6532 | 20.1195 |  | 20.2318 | 19.6536 | 20.1262 | 19.7817 | 20.1258 | 20.4163 |  | 20.4746 |  |  | 20.2208 | 20.3703 | 20.6105 | [5 empty] | 21.961 | 20.3996 | 21.7234 | 22.1203 | 19.6598 | 21.2719 | 21.9167 | 19.4307 | 19.9989 | 21.1849 |  | 19.6029 | 20.9949 | 18.8791 | 19.7164 | 20.8572 | 19.4052 | 20.1994 | 19.0298 | 20.2201 | 19.2176 | 20.3294 | 18.7788 | 20.0653 | 21.1348 | 19.402 | 19.8432 | 21.064 | 18.9935 | 19.8082 | 20.8817 | 18.9715 | 20.2334 | 19.3218 | 20.1027 | 18.9849 | 20.2238 | 0.064978 | 20.9509 | 0.047313 | 0.014005 | -26.9937 | 3.0628 | -1.19 | -0.21 | 0.53322 | -0.65805 | -6.5032 | 0.59285 | 0.63661 | -16.7051 | 5.4502 | 0.42319 | 0.43259 | 0.42902 | 0.45721 | 0.49392 | 0.43853 | 0.42751
42838.4113 | -779 | 22.9054 | 22.8766 | 22.8764 | 22.8098 | 22.4537 | 21.8083 | 22.7559 | 21.8766 | 22.4044 | 22.4136 | 22.4074 | 22.0946 | 21.3157 | 22.2817 | 21.5947 | 21.7724 | 21.9153 | 21.1109 | 21.2068 | 21.4283 | 20.5116 | 20.6557 | 20.956 | 21.9275 | 21.6986 | 21.3326 | 20.4694 | 20.5848 | 20.5355 | 22.0508 | 21.674 | 21.2013 | 22.0126 | 21.7532 | 21.3789 | 19.9535 | 20.5276 |  | 20.5915 | 20.3079 | 20.3754 | 19.2326 |  | 16.6302 | 16.7046 | 16.4306 | 16.6567 | 16.7823 | 17.3015 | 17.6907 | 15.6946 | 16.6331 | 15.7978 | 16.8117 | 17.8817 | 44.4992 | 47.1109 | 43.5285 | 21.3011 |  |  | 0.30053 | -0.34045 | -30.6559 | 0.14978 | 0.25706 | -197.8177 | 20.9478 | -0.25795 | -0.5802 | -0.078144 | 0.046469 | 8.8292 | 9.0588 | 1.979 | 21.8115 | 22.0379 | 22.2429 | 22.3135 | 22.1429 | 21.5085 | 20.3367 | 22.2287 | 22.3959 | 22.4271 | 22.3884 | 22.0358 | 21.2853 | 22.3036 | 16.5961 | 16.9733 | 15.904 | 16.0006 | 16.058 | 17.0622 | 16.6757 | 22.3827 | 22.1622 | 21.7385 | 22.1057 | 21.8273 | 21.3384 | 21.9675 | 21.5563 | 20.9503 | 20.152 | 20.5078 | 20.1064 | 19.8733 | 0.11443 | -0.1896 | 20.7071 | 22.0908 | 22.414 | 20.1181 | 21.7213 | 22.1712 | 21.9804 | 21.7541 | 21.3286 | 21.838 | 21.5111 | 21.1144 | 20.5539 | 20.5494 | 20.6274 | 20.645 | 20.1212 |  | 20.2279 | 19.6671 | 20.1302 | 19.7858 | 20.1216 | 20.4271 |  | 20.4864 |  |  | 20.2032 | 20.3611 | 20.6029 | [5 empty] | 21.9606 | 20.3956 | 21.7198 | 22.1146 | 19.6514 | 21.264 | 21.9112 | 19.4324 | 20.0077 | 21.1918 |  | 19.6111 | 21.0027 | 18.8798 | 19.7229 | 20.8638 | 19.4087 | 20.2061 | 19.0296 | 20.2221 | 19.2232 | 20.3345 | 18.7809 | 20.0689 | 21.1376 | 19.4076 | 19.8509 | 21.0664 | 18.9893 | 19.8195 | 20.8809 | 18.9711 | 20.2403 | 19.3215 | 20.1063 | 18.9942 | 20.2299 | -0.086761 | 20.95 | 0.047221 | 0.015246 | -27.0101 | 3.0631 | -1.17 | 0.19 | 0.65472 | -0.69229 | -6.5692 | 0.45918 | 0.60218 | -16.7046 | 5.4359 | 0.42301 | 0.43235 | 0.42876 | 0.454 | 0.48582 | 0.4385 | 0.42735
42838.4113 | -778 | 22.9087 | 22.8802 | 22.8757 | 22.808 | 22.4493 | 21.8092 | 22.7494 | 21.8729 | 22.4043 | 22.4125 | 22.4076 | 22.0953 | 21.3151 | 22.2775 | 21.6052 | 21.772 | 21.9117 | 21.1025 | 21.2007 | 21.4304 | 20.5089 | 20.6553 | 20.9498 | 21.9242 | 21.698 | 21.3337 | 20.4712 | 20.5871 | 20.5317 | 22.0596 | 21.6801 | 21.1977 | 22.0178 | 21.7608 | 21.3821 | 19.9682 | 20.54 |  | 20.5959 | 20.3082 | 20.3887 | 19.2377 |  | 16.6385 | 16.7081 | 16.418 | 16.6519 | 16.7622 | 17.2965 | 17.7176 | 15.7056 | 16.6344 | 15.8522 | 16.815 | 17.8763 | 44.4734 | 47.1035 | 43.5078 | 21.3034 |  |  | 0.3393 | -0.52313 | -30.5843 | 0.52959 | 0.29058 | -197.8466 | 20.863 | -0.23495 | -0.32781 | -0.15472 | -0.06099 | 8.8283 | 9.058 | 1.9787 | 21.8165 | 22.0552 | 22.2515 | 22.3268 | 22.1567 | 21.5086 | 20.3427 | 22.2408 | 22.4013 | 22.4423 | 22.3982 | 22.0443 | 21.2923 | 22.3176 | 16.623 | 17.0063 | 16.0116 | 16.0611 | 16.0795 | 17.0691 | 16.6856 | 22.3878 | 22.1615 | 21.7352 | 22.1023 | 21.8341 | 21.3394 | 21.9693 | 21.5624 | 20.9581 | 20.1532 | 20.5069 | 20.1053 | 19.8671 | 0.21804 | -0.10325 | 20.7059 | 22.0918 | 22.4098 | 20.1098 | 21.7178 | 22.1697 | 21.9772 | 21.7599 | 21.3286 | 21.8398 | 21.5095 | 21.1116 | 20.5521 | 20.5477 | 20.6242 | 20.6443 | 20.128 |  | 20.2231 | 19.6743 | 20.13 | 19.7848 | 20.1182 | 20.4258 |  | 20.4799 |  |  | 20.2138 | 20.3757 | 20.6076 | [5 empty] | 21.9763 | 20.4025 | 21.7243 | 22.1246 | 19.6527 | 21.2756 | 21.9236 | 19.4416 | 20.0157 | 21.1882 |  | 19.6104 | 21.0092 | 18.8831 | 19.7263 | 20.871 | 19.4141 | 20.2097 | 19.0428 | 20.2292 | 19.2277 | 20.3327 | 18.7718 | 20.073 | 21.1347 | 19.4126 | 19.8422 | 21.0683 | 18.9846 | 19.8165 | 20.8889 | 18.9723 | 20.2397 | 19.3286 | 20.1083 | 18.9954 | 20.2325 | -0.08435 | 20.9502 | 0.047393 | 0.015261 | -27.038 | 3.0635 | -1.11 | -0.05 | 0.69566 | -0.85815 | -6.5616 | 0.86343 | 0.64022 | -16.7057 | 5.4249 | 0.42266 | 0.43214 | 0.42867 | 0.45181 | 0.47501 | 0.43885 | 0.42756
42838.4113 | -777 | 22.9173 | 22.8836 | 22.8748 | 22.8073 | 22.4611 | 21.8105 | 22.7563 | 21.8769 | 22.4097 | 22.4243 | 22.4151 | 22.0955 | 21.3126 | 22.2798 | 21.5856 | 21.7709 | 21.9066 | 21.1024 | 21.1979 | 21.4245 | 20.5038 | 20.6453 | 20.9555 | 21.9277 | 21.6883 | 21.3267 | 20.4629 | 20.5841 | 20.5306 | 22.0522 | 21.6729 | 21.1992 | 22.0071 | 21.7543 | 21.3784 | 19.9553 | 20.5319 |  | 20.5939 | 20.3016 | 20.3863 | 19.2311 |  | 16.6247 | 16.6977 | 16.4149 | 16.6449 | 16.7551 | 17.294 | 17.7478 | 15.7475 | 16.6379 | 15.8783 | 16.8142 | 17.8717 | 44.4616 | 47.0934 | 43.4838 | 21.3021 |  |  | 0.4083 | 0.008479 | -30.3438 | 0.45862 | 0.19595 | -197.8112 | 21.0792 | -0.32563 | -0.31496 | -0.087795 | -0.036859 | 8.8282 | 9.058 | 1.978 | 21.8229 | 22.0585 | 22.2509 | 22.3247 | 22.1649 | 21.51 | 20.339 | 22.2349 | 22.4079 | 22.4386 | 22.4034 | 22.0456 | 21.3027 | 22.3214 | 16.6357 | 17.0141 | 16.0314 | 16.0497 | 16.0674 | 17.0654 | 16.6824 | 22.4021 | 22.1742 | 21.7436 | 22.1116 | 21.8416 | 21.3511 | 21.9766 | 21.5752 | 20.9671 | 20.1656 | 20.5153 | 20.1132 | 19.8775 | 0.09438 | -0.14262 | 20.7023 | 22.0862 | 22.407 | 20.0994 | 21.7083 | 22.1607 | 21.9747 | 21.7552 | 21.3297 | 21.8364 | 21.5061 | 21.1075 | 20.5441 | 20.5403 | 20.6095 | 20.6343 | 20.1217 |  | 20.2111 | 19.6781 | 20.1223 | 19.7784 | 20.1107 | 20.4135 |  | 20.4603 |  |  | 20.2083 | 20.3726 | 20.5986 | [5 empty] | 21.977 | 20.4063 | 21.7142 | 22.1183 | 19.6472 | 21.2653 | 21.9102 | 19.4305 | 20.0063 | 21.1836 |  | 19.5948 | 20.9947 | 18.8725 | 19.7175 | 20.8588 | 19.4059 | 20.201 | 19.0322 | 20.2195 | 19.221 | 20.3357 | 18.7648 | 20.0699 | 21.1431 | 19.4133 | 19.8488 | 21.0685 | 18.981 | 19.8213 | 20.8896 | 18.9848 | 20.2381 | 19.3395 | 20.1017 | 18.9982 | 20.2276 | -0.050774 | 20.9499 | 0.047983 | 0.01423 | -27.0648 | 3.064 | -0.9 | -0.18 | 0.76312 | 0.10925 | -6.5356 | 0.80349 | 0.52574 | -16.7041 | 5.4529 | 0.42243 | 0.43178 | 0.4286 | 0.44997 | 0.47244 | 0.4386 | 0.42769
42838.4113 | -776 | 22.9013 | 22.8726 | 22.8667 | 22.8037 | 22.4493 | 21.8026 | 22.7451 | 21.8661 | 22.3941 | 22.4098 | 22.4028 | 22.0924 | 21.3134 | 22.2693 | 21.5937 | 21.7693 | 21.9116 | 21.1028 | 21.1986 | 21.4223 | 20.5075 | 20.6501 | 20.9524 | 21.9322 | 21.6898 | 21.3256 | 20.4661 | 20.5878 | 20.5387 | 22.0576 | 21.6765 | 21.1957 | 22.0191 | 21.7659 | 21.3837 | 19.9617 | 20.5364 |  | 20.5934 | 20.3049 | 20.3825 | 19.2413 |  | 16.6186 | 16.6954 | 16.4086 | 16.6364 | 16.7425 | 17.3004 | 17.771 | 15.763 | 16.6382 | 15.8966 | 16.8072 | 17.877 | 44.4584 | 47.0866 | 43.4553 | 21.3047 |  |  | 0.38596 | -0.24977 | -30.28 | -0.048014 | 0.12433 | -197.825 | 21.3795 | -0.48268 | -0.16162 | 0.11886 | -0.042588 | 8.8287 | 9.0584 | 1.9776 | 21.8175 | 22.0549 | 22.2549 | 22.3202 | 22.1625 | 21.5089 | 20.341 | 22.2402 | 22.4114 | 22.4507 | 22.4031 | 22.0457 | 21.2968 | 22.3217 | 16.6529 | 17.03 | 16.0124 | 15.9845 | 16.0583 | 17.0637 | 16.6773 | 22.3954 | 22.17 | 21.7366 | 22.1049 | 21.8393 | 21.3435 | 21.9752 | 21.5726 | 20.9517 | 20.1598 | 20.5036 | 20.114 | 19.876 | 0.076293 | -0.015375 | 20.6948 | 22.0898 | 22.4068 | 20.0938 | 21.7088 | 22.1663 | 21.979 | 21.7527 | 21.3254 | 21.8333 | 21.51 | 21.1068 | 20.5405 | 20.543 | 20.6133 | 20.6267 | 20.1392 |  | 20.2332 | 19.7144 | 20.1375 | 19.7769 | 20.1222 | 20.4235 |  | 20.4844 |  |  | 20.2039 | 20.3485 | 20.5901 | [5 empty] | 21.9647 | 20.3882 | 21.7119 | 22.1166 | 19.6308 | 21.2591 | 21.8999 | 19.4452 | 20.002 | 21.188 |  | 19.6058 | 21.007 | 18.8783 | 19.7307 | 20.8614 | 19.4116 | 20.2031 | 19.0536 | 20.2279 | 19.2261 | 20.3349 | 18.752 | 20.0729 | 21.145 | 19.4149 | 19.8504 | 21.0723 | 18.9925 | 19.8209 | 20.8809 | 18.9818 | 20.236 | 19.3449 | 20.1042 | 18.9913 | 20.2347 | -0.15521 | 20.9496 | 0.047664 | 0.013547 | -27.0777 | 3.0645 | -1.1 | 0.04 | 0.74196 | -0.59295 | -6.5287 | -0.25998 | 0.41878 | -16.7049 | 5.4916 | 0.42268 | 0.43128 | 0.42903 | 0.44786 | 0.47394 | 0.43853 | 0.42754
42838.4113 | -775 | 22.9056 | 22.8798 | 22.8616 | 22.7999 | 22.4526 | 21.8042 | 22.7465 | 21.8683 | 22.3982 | 22.4206 | 22.3956 | 22.091 | 21.3225 | 22.2723 | 21.5907 | 21.7691 | 21.9065 | 21.0972 | 21.2041 | 21.4266 | 20.506 | 20.661 | 20.9501 | 21.9296 | 21.6972 | 21.3264 | 20.4734 | 20.5869 | 20.5301 | 22.0648 | 21.6812 | 21.2049 | 22.0173 | 21.7671 | 21.3864 | 19.964 | 20.558 |  | 20.6025 | 20.3154 | 20.4012 | 19.2503 |  | 16.6181 | 16.6904 | 16.4028 | 16.6237 | 16.7349 | 17.2985 | 17.7937 | 15.7942 | 16.6399 | 15.921 | 16.8043 | 17.8752 | 44.4428 | 47.0767 | 43.4338 | 21.3136 |  |  | 0.40107 | -0.303 | -30.1164 | 0.29631 | 0.29452 | -197.8795 | 21.4459 | -0.58191 | -0.16357 | -0.038702 | 0.018519 | 8.8293 | 9.059 | 1.9787 | 21.8205 | 22.057 | 22.2486 | 22.3211 | 22.1594 | 21.5085 | 20.3439 | 22.2375 | 22.4054 | 22.4452 | 22.3973 | 22.0431 | 21.2939 | 22.3116 | 16.664 | 17.0358 | 15.991 | 15.9895 | 16.0541 | 17.0754 | 16.6778 | 22.3821 | 22.1749 | 21.7375 | 22.1083 | 21.8335 | 21.3488 | 21.9734 | 21.5724 | 20.9581 | 20.1612 | 20.5052 | 20.1138 | 19.8613 | 0.13331 | -0.016707 | 20.7039 | 22.097 | 22.4115 | 20.0927 | 21.7129 | 22.1653 | 21.9843 | 21.7524 | 21.3276 | 21.8365 | 21.5135 | 21.1152 | 20.542 | 20.5601 | 20.6136 | 20.6215 | 20.1499 |  | 20.2315 | 19.7312 | 20.1359 | 19.7637 | 20.127 | 20.4247 |  | 20.4874 |  |  | 20.2156 | 20.3661 | 20.6009 | [5 empty] | 21.9747 | 20.3922 | 21.7254 | 22.1175 | 19.6345 | 21.2644 | 21.9068 | 19.4369 | 20.0052 | 21.1898 |  | 19.6045 | 21.0047 | 18.8817 | 19.7231 | 20.8674 | 19.4174 | 20.206 | 19.0467 | 20.2333 | 19.2305 | 20.3347 | 18.7556 | 20.0737 | 21.1341 | 19.4072 | 19.8526 | 21.0731 | 18.9848 | 19.8276 | 20.8807 | 18.9685 | 20.2296 | 19.3435 | 20.1012 | 18.9862 | 20.229 | 0.048468 | 20.9505 | 0.047854 | 0.014121 | -27.0591 | 3.0649 | -1.4 | -0.5 | 0.75634 | -0.65308 | -6.511 | 0.64584 | 0.64455 | -16.7071 | 5.5001 | 0.42233 | 0.43075 | 0.42956 | 0.44799 | 0.47639 | 0.43836 | 0.42799
42838.4113 | -774 | 22.9016 | 22.8747 | 22.8669 | 22.8033 | 22.4515 | 21.804 | 22.7465 | 21.8677 | 22.4023 | 22.4106 | 22.3975 | 22.0903 | 21.3164 | 22.2718 | 21.5842 | 21.766 | 21.9123 | 21.103 | 21.1975 | 21.4196 | 20.5022 | 20.6592 | 20.9489 | 21.9208 | 21.6912 | 21.3329 | 20.4663 | 20.5788 | 20.529 | 22.0602 | 21.6675 | 21.2038 | 22.0154 | 21.7619 | 21.379 | 19.9583 | 20.5575 |  | 20.6039 | 20.3224 | 20.3838 | 19.2596 |  | 16.6107 | 16.6738 | 16.397 | 16.6149 | 16.7329 | 17.3037 | 17.8146 | 15.7901 | 16.6339 | 15.9405 | 16.8066 | 17.8751 | 44.4263 | 47.0645 | 43.4152 | 21.3169 |  |  | 0.23022 | -0.13477 | -29.7392 | 0.21089 | 0.18478 | -197.8223 | 21.3526 | -0.64959 | -0.30854 | -0.034506 | -0.099876 | 8.8285 | 9.0582 | 1.9789 | 21.8208 | 22.0546 | 22.2492 | 22.3234 | 22.1594 | 21.5066 | 20.3448 | 22.2412 | 22.4064 | 22.4416 | 22.3983 | 22.0465 | 21.2934 | 22.3075 | 16.6739 | 17.0307 | 15.9874 | 16.0072 | 16.0236 | 17.0649 | 16.6698 | 22.3891 | 22.1656 | 21.7386 | 22.1031 | 21.8326 | 21.346 | 21.9722 | 21.5663 | 20.9585 | 20.1582 | 20.5079 | 20.1098 | 19.8507 | 0.14884 | -0.051133 | 20.7169 | 22.1036 | 22.4193 | 20.1005 | 21.7165 | 22.1674 | 21.9852 | 21.7536 | 21.3325 | 21.8433 | 21.5174 | 21.1221 | 20.5504 | 20.5595 | 20.6106 | 20.6237 | 20.1573 |  | 20.2338 | 19.7482 | 20.1343 | 19.7544 | 20.125 | 20.4334 |  | 20.4802 |  |  | 20.2246 | 20.3782 | 20.6095 | [5 empty] | 21.9683 | 20.3946 | 21.7264 | 22.1171 | 19.6358 | 21.2648 | 21.9095 | 19.4234 | 20.003 | 21.1861 |  | 19.6069 | 21.0086 | 18.8814 | 19.719 | 20.8623 | 19.4216 | 20.203 | 19.0467 | 20.2318 | 19.2311 | 20.34 | 18.7574 | 20.0864 | 21.1551 | 19.4228 | 19.8567 | 21.0754 | 18.9908 | 19.8388 | 20.893 | 18.9821 | 20.2475 | 19.3463 | 20.1109 | 18.9936 | 20.2329 | -0.064687 | 20.9492 | 0.047823 | 0.013315 | -27.0172 | 3.0653 | -1.41 | -0.14 | 0.57303 | -0.43555 | -6.4699 | 0.54483 | 0.51054 | -16.7049 | 5.4882 | 0.4222 | 0.43023 | 0.42975 | 0.44566 | 0.47585 | 0.43791 | 0.42818
42838.4113 | -773 | 22.9059 | 22.8733 | 22.8725 | 22.804 | 22.4508 | 21.8099 | 22.754 | 21.8709 | 22.4046 | 22.4152 | 22.4008 | 22.0928 | 21.3176 | 22.2702 | 21.5883 | 21.7669 | 21.9115 | 21.0964 | 21.1979 | 21.4181 | 20.4996 | 20.6512 | 20.946 | 21.9213 | 21.6909 | 21.3244 | 20.4653 | 20.5763 | 20.5314 | 22.0641 | 21.6702 | 21.2017 | 22.0157 | 21.7617 | 21.3816 | 19.9609 | 20.5611 |  | 20.5976 | 20.3157 | 20.3806 | 19.2733 |  | 16.6104 | 16.6632 | 16.3818 | 16.6126 | 16.7283 | 17.3229 | 17.8384 | 15.796 | 16.6294 | 15.9413 | 16.8099 | 17.8729 | 44.4077 | 47.0497 | 43.4018 | 21.3134 |  |  | 0.47073 | -0.1466 | -30.3523 | 0.15503 | 0.26626 | -197.8026 | 21.2028 | -0.57205 | -0.63294 | -0.15682 | -0.13477 | 8.83 | 9.0597 | 1.9782 | 21.8194 | 22.0504 | 22.2463 | 22.3208 | 22.1606 | 21.5028 | 20.3356 | 22.2332 | 22.3996 | 22.4387 | 22.3982 | 22.0445 | 21.2887 | 22.3052 | 16.6912 | 17.0152 | 16.0125 | 16.0195 | 16.0235 | 17.0668 | 16.6802 | 22.3884 | 22.1632 | 21.7323 | 22.0979 | 21.8329 | 21.3419 | 21.9695 | 21.5633 | 20.9576 | 20.1484 | 20.4985 | 20.1131 | 19.8443 | -0.13171 | -0.059882 | 20.7195 | 22.1027 | 22.4184 | 20.1077 | 21.722 | 22.1729 | 21.9848 | 21.7582 | 21.3324 | 21.8456 | 21.5154 | 21.1194 | 20.5592 | 20.5555 | 20.6145 | 20.6203 | 20.1681 |  | 20.2332 | 19.7628 | 20.1369 | 19.7521 | 20.128 | 20.418 |  | 20.4905 |  |  | 20.2207 | 20.3699 | 20.6067 | [5 empty] | 21.9688 | 20.3838 | 21.723 | 22.1222 | 19.6247 | 21.2623 | 21.9126 | 19.4285 | 20.0027 | 21.1826 |  | 19.6008 | 21.0081 | 18.8788 | 19.723 | 20.8667 | 19.4159 | 20.2001 | 19.0477 | 20.2309 | 19.2234 | 20.3426 | 18.7638 | 20.078 | 21.1507 | 19.4183 | 19.8469 | 21.0666 | 18.9792 | 19.8262 | 20.8883 | 18.9705 | 20.2455 | 19.3453 | 20.0968 | 18.9911 | 20.2322 | 0.10171 | 20.9516 | 0.047178 | 0.014092 | -27.0846 | 3.0658 | -1.42 | -0.22 | 0.81939 | -0.45425 | -6.5361 | 0.46713 | 0.61288 | -16.7046 | 5.4691 | 0.42188 | 0.42991 | 0.42991 | 0.44396 | 0.47429 | 0.43761 | 0.42804
42838.4113 | -772 | 22.9086 | 22.8765 | 22.8723 | 22.7989 | 22.4495 | 21.8066 | 22.7491 | 21.8716 | 22.3989 | 22.4238 | 22.3954 | 22.0969 | 21.3164 | 22.2757 | 21.5896 | 21.7749 | 21.914 | 21.1 | 21.2038 | 21.4238 | 20.5057 | 20.6494 | 20.9408 | 21.9288 | 21.6919 | 21.3299 | 20.4702 | 20.5771 | 20.5346 | 22.0579 | 21.6679 | 21.2006 | 22.0149 | 21.7586 | 21.386 | 19.9633 | 20.5619 |  | 20.5946 | 20.3069 | 20.3722 | 19.2853 |  | 16.6019 | 16.6578 | 16.3738 | 16.6025 | 16.7208 | 17.3187 | 17.8607 | 15.7897 | 16.628 | 15.9435 | 16.8115 | 17.872 | 44.3807 | 47.0393 | 43.3776 | 21.314 |  |  | 0.44115 | -0.36608 | -30.648 | 0.011786 | 0.22224 | -197.8361 | 21.2783 | -0.61805 | -0.16882 | -0.015834 | 0.01227 | 8.8286 | 9.0586 | 1.9777 | 21.8242 | 22.053 | 22.2426 | 22.3164 | 22.1573 | 21.511 | 20.3342 | 22.2355 | 22.413 | 22.4358 | 22.3947 | 22.0382 | 21.2975 | 22.3146 | 16.7094 | 16.9955 | 16.0371 | 16.0369 | 16.034 | 17.0645 | 16.6799 | 22.3943 | 22.164 | 21.7307 | 22.0948 | 21.8311 | 21.3469 | 21.9695 | 21.5659 | 20.9567 | 20.1489 | 20.4999 | 20.1085 | 19.8389 | -0.10635 | -0.14148 | 20.722 | 22.0973 | 22.4134 | 20.1066 | 21.7206 | 22.1708 | 21.9785 | 21.7558 | 21.3298 | 21.8395 | 21.5153 | 21.1144 | 20.5533 | 20.5502 | 20.6016 | 20.6049 | 20.1621 |  | 20.2288 | 19.764 | 20.1316 | 19.7355 | 20.1211 | 20.42 |  | 20.474 |  |  | 20.2204 | 20.3597 | 20.5928 | [5 empty] | 21.9723 | 20.3735 | 21.7253 | 22.1176 | 19.616 | 21.2683 | 21.9129 | 19.422 | 19.9953 | 21.1807 |  | 19.5907 | 20.9955 | 18.8662 | 19.7131 | 20.8598 | 19.4036 | 20.1876 | 19.0306 | 20.229 | 19.2264 | 20.3361 | 18.7598 | 20.0768 | 21.1423 | 19.4225 | 19.8454 | 21.074 | 18.9834 | 19.8323 | 20.8818 | 18.9727 | 20.2478 | 19.3422 | 20.0982 | 18.9975 | 20.2283 | -0.081938 | 20.9504 | 0.047449 | 0.013758 | -27.1239 | 3.0663 | -1.39 | -0.03 | 0.79324 | -0.71781 | -6.5679 | 0.1288 | 0.55992 | -16.7059 | 5.4788 | 0.4219 | 0.4297 | 0.43014 | 0.44167 | 0.47151 | 0.43736 | 0.4282
42838.4114 | -771 | 22.9003 | 22.8771 | 22.8682 | 22.8033 | 22.4529 | 21.8093 | 22.7508 | 21.8703 | 22.4007 | 22.4166 | 22.3977 | 22.0924 | 21.3223 | 22.2709 | 21.5946 | 21.7741 | 21.9157 | 21.1081 | 21.2093 | 21.4226 | 20.5142 | 20.6554 | 20.9529 | 21.9289 | 21.6995 | 21.3359 | 20.4815 | 20.5839 | 20.541 | 22.0495 | 21.6713 | 21.1945 | 22.0131 | 21.75 | 21.3812 | 19.9541 | 20.557 |  | 20.5934 | 20.3013 | 20.3738 | 19.2966 |  | 16.5915 | 16.6496 | 16.3758 | 16.603 | 16.7206 | 17.3181 | 17.8631 | 15.802 | 16.6324 | 15.9742 | 16.8088 | 17.867 | 44.3734 | 47.0303 | 43.3589 | 21.3113 |  |  | 0.43721 | -0.10783 | -31.0541 | 0.094582 | 0.25641 | -197.8243 | 21.2474 | -0.52605 | -0.17972 | -0.16521 | -0.14449 | 8.8289 | 9.0588 | 1.9786 | 21.811 | 22.0406 | 22.2429 | 22.311 | 22.1519 | 21.499 | 20.3281 | 22.2307 | 22.395 | 22.4363 | 22.3903 | 22.0401 | 21.2847 | 22.3063 | 16.7565 | 16.999 | 16.0705 | 16.0685 | 16.0466 | 17.0672 | 16.6814 | 22.3835 | 22.162 | 21.7338 | 22.0972 | 21.8321 | 21.3329 | 21.9646 | 21.5635 | 20.9531 | 20.1529 | 20.4966 | 20.101 | 19.8323 | -0.19266 | -0.040482 | 20.7254 | 22.098 | 22.4238 | 20.1112 | 21.7199 | 22.1728 | 21.9814 | 21.7549 | 21.327 | 21.84 | 21.5177 | 21.1153 | 20.5633 | 20.5502 | 20.6026 | 20.5974 | 20.1661 |  | 20.2285 | 19.7703 | 20.1371 | 19.7528 | 20.1249 | 20.4276 |  | 20.4782 |  |  | 20.2319 | 20.3762 | 20.598 | [5 empty] | 21.9842 | 20.378 | 21.73 | 22.1248 | 19.6259 | 21.2745 | 21.9172 | 19.4277 | 19.9961 | 21.1827 |  | 19.5928 | 20.9977 | 18.8761 | 19.7186 | 20.8659 | 19.4184 | 20.188 | 19.0366 | 20.231 | 19.2339 | 20.3397 | 18.7542 | 20.0693 | 21.1425 | 19.4263 | 19.8409 | 21.0753 | 18.978 | 19.831 | 20.8825 | 18.9712 | 20.2433 | 19.341 | 20.0908 | 18.9956 | 20.221 | 0.091875 | 20.95 | 0.047184 | 0.015115 | -27.0767 | 3.0672 | -1.03 | -0.07 | 0.78969 | -0.38958 | -6.6111 | 0.36485 | 0.60143 | -16.7054 | 5.4748 | 0.42178 | 0.42971 | 0.42979 | 0.43675 | 0.46797 | 0.43674 | 0.42852
42838.4114 | -770 | 22.9035 | 22.882 | 22.8706 | 22.8061 | 22.4505 | 21.807 | 22.7529 | 21.8715 | 22.4085 | 22.4152 | 22.4049 | 22.0926 | 21.3222 | 22.2766 | 21.5988 | 21.7764 | 21.9123 | 21.1068 | 21.2076 | 21.4279 | 20.5078 | 20.6549 | 20.9545 | 21.9266 | 21.6976 | 21.3342 | 20.4793 | 20.5848 | 20.5445 | 22.0549 | 21.6792 | 21.2055 | 22.0229 | 21.7651 | 21.3866 | 19.9599 | 20.5583 |  | 20.6042 | 20.3133 | 20.3821 | 19.3172 |  | 16.5785 | 16.6346 | 16.3632 | 16.582 | 16.709 | 17.3193 | 17.8628 | 15.7802 | 16.6309 | 15.9689 | 16.801 | 17.8691 | 44.364 | 47.0199 | 43.3415 | 21.3071 |  |  | 0.39319 | -0.36082 | -31.8118 | 0.38568 | 0.27415 | -197.8079 | 21.3736 | -0.51817 | -0.15461 | -0.017932 | 0.058621 | 8.8298 | 9.0596 | 1.9791 | 21.8267 | 22.0567 | 22.2478 | 22.3141 | 22.1589 | 21.5054 | 20.3353 | 22.2312 | 22.4119 | 22.4432 | 22.3961 | 22.0472 | 21.2863 | 22.3091 | 16.8051 | 16.9881 | 16.0711 | 16.0783 | 16.0534 | 17.0571 | 16.6756 | 22.3849 | 22.166 | 21.7359 | 22.1024 | 21.8333 | 21.3473 | 21.9682 | 21.5653 | 20.9498 | 20.1552 | 20.4988 | 20.1056 | 19.8288 | -0.25793 | -0.2128 | 20.7258 | 22.0961 | 22.4175 | 20.1082 | 21.7181 | 22.1694 | 21.9793 | 21.7556 | 21.3359 | 21.8383 | 21.5204 | 21.1166 | 20.5631 | 20.5501 | 20.59 | 20.5942 | 20.1788 |  | 20.2333 | 19.7646 | 20.1364 | 19.7634 | 20.1285 | 20.4295 |  | 20.4851 |  |  | 20.227 | 20.374 | 20.5888 | [5 empty] | 21.9734 | 20.3681 | 21.7171 | 22.1182 | 19.6163 | 21.2691 | 21.9111 | 19.4342 | 20.0044 | 21.1832 |  | 19.594 | 21.0013 | 18.8844 | 19.7176 | 20.8735 | 19.4236 | 20.1916 | 19.0481 | 20.2345 | 19.2386 | 20.3461 | 18.7558 | 20.0753 | 21.1456 | 19.4303 | 19.8392 | 21.0717 | 18.9753 | 19.8371 | 20.884 | 18.9778 | 20.247 | 19.3477 | 20.0891 | 18.999 | 20.2196 | -0.20492 | 20.9484 | 0.048118 | 0.015478 | -27.0574 | 3.0679 | -0.95 | -0.06 | 0.74888 | -0.71261 | -6.6911 | 0.73675 | 0.62188 | -16.7047 | 5.4911 | 0.42159 | 0.42985 | 0.42962 | 0.43017 | 0.46723 | 0.43636 | 0.42869
42838.4114 | -769 | 22.9042 | 22.8748 | 22.8732 | 22.8094 | 22.4602 | 21.8067 | 22.753 | 21.8744 | 22.4013 | 22.4166 | 22.4045 | 22.0933 | 21.3204 | 22.2766 | 21.5936 | 21.7706 | 21.9063 | 21.1003 | 21.1999 | 21.4236 | 20.5015 | 20.6494 | 20.9474 | 21.9267 | 21.6897 | 21.3267 | 20.4691 | 20.5718 | 20.543 | 22.0637 | 21.6815 | 21.2083 | 22.0275 | 21.7702 | 21.389 | 19.9665 | 20.5762 |  | 20.6007 | 20.3145 | 20.3855 | 19.3334 |  | 16.5837 | 16.6328 | 16.3553 | 16.5791 | 16.7159 | 17.3469 | 17.8857 | 15.7653 | 16.6327 | 15.9622 | 16.8067 | 17.8804 | 44.3664 | 47.0104 | 43.3356 | 21.3114 |  |  | 0.39516 | -0.099949 | -32.0247 | 0.33377 | 0.28335 | -197.8177 | 20.6758 | -0.66668 | -0.015475 | -0.10982 | -0.07644 | 8.8298 | 9.0597 | 1.9785 | 21.8246 | 22.0515 | 22.2464 | 22.3192 | 22.1605 | 21.5041 | 20.34 | 22.2342 | 22.4126 | 22.4398 | 22.4007 | 22.0428 | 21.2887 | 22.3129 | 16.8443 | 16.9449 | 16.0716 | 16.083 | 16.0665 | 17.0589 | 16.676 | 22.3916 | 22.1692 | 21.7413 | 22.1066 | 21.8321 | 21.3439 | 21.971 | 21.5707 | 20.9494 | 20.1598 | 20.4974 | 20.1089 | 19.8321 | -0.10831 | -0.27557 | 20.7252 | 22.0975 | 22.4092 | 20.107 | 21.7134 | 22.1678 | 21.976 | 21.7524 | 21.3258 | 21.8365 | 21.5159 | 21.1128 | 20.5599 | 20.5376 | 20.5805 | 20.5821 | 20.1856 |  | 20.236 | 19.7515 | 20.14 | 19.7604 | 20.133 | 20.4258 |  | 20.4791 |  |  | 20.2171 | 20.373 | 20.5837 | [5 empty] | 21.9709 | 20.3669 | 21.7183 | 22.119 | 19.6105 | 21.2732 | 21.9069 | 19.4318 | 20.005 | 21.1874 |  | 19.5949 | 21.0028 | 18.8853 | 19.7219 | 20.874 | 19.4182 | 20.198 | 19.0443 | 20.23 | 19.2358 | 20.353 | 18.7546 | 20.0742 | 21.1386 | 19.4271 | 19.8386 | 21.0707 | 18.9794 | 19.8347 | 20.8778 | 18.9807 | 20.2476 | 19.3425 | 20.084 | 19.0003 | 20.218 | -0.11069 | 20.9493 | 0.04818 | 0.016045 | -27.0451 | 3.0686 | -0.9 | 0.06 | 0.75076 | -0.37505 | -6.7134 | 0.68537 | 0.63226 | -16.7059 | 5.4009 | 0.42149 | 0.43033 | 0.42985 | 0.42602 | 0.46723 | 0.43613 | 0.42875
42838.4114 | -768 | 22.9115 | 22.8909 | 22.8783 | 22.8091 | 22.4531 | 21.8101 | 22.7527 | 21.8771 | 22.4011 | 22.4167 | 22.4051 | 22.0889 | 21.3198 | 22.2754 | 21.5942 | 21.7685 | 21.9088 | 21.0993 | 21.1944 | 21.4208 | 20.5079 | 20.6516 | 20.9515 | 21.9303 | 21.6941 | 21.3309 | 20.4677 | 20.5702 | 20.5475 | 22.0656 | 21.6813 | 21.2126 | 22.0282 | 21.7626 | 21.3869 | 19.9733 | 20.5748 |  | 20.6079 | 20.3131 | 20.3786 | 19.348 |  | 16.5815 | 16.6206 | 16.351 | 16.5854 | 16.7242 | 17.3736 | 17.9107 | 15.747 | 16.6323 | 15.959 | 16.801 | 17.8723 | 44.3685 | 47.0012 | 43.3177 | 21.308 |  |  | 0.40961 | -0.071033 | -31.8959 | 0.32589 | 0.34578 | -197.825 | 20.8505 | -0.34929 | -0.33871 | -0.10584 | -0.05231 | 8.8287 | 9.0584 | 1.9779 | 21.8185 | 22.0495 | 22.2478 | 22.3181 | 22.1617 | 21.5044 | 20.3386 | 22.2326 | 22.4062 | 22.4387 | 22.3986 | 22.0412 | 21.289 | 22.304 | 16.8823 | 16.9572 | 16.1017 | 16.0908 | 16.0693 | 17.0622 | 16.6769 | 22.3915 | 22.1663 | 21.7443 | 22.1077 | 21.8336 | 21.3478 | 21.9784 | 21.5751 | 20.9571 | 20.1632 | 20.4963 | 20.108 | 19.8425 | -0.092783 | -0.22726 | 20.7227 | 22.092 | 22.4055 | 20.1126 | 21.7126 | 22.1664 | 21.9783 | 21.7495 | 21.323 | 21.8355 | 21.506 | 21.1158 | 20.5591 | 20.5308 | 20.5747 | 20.5765 | 20.1809 |  | 20.226 | 19.7411 | 20.1281 | 19.7577 | 20.1205 | 20.4175 |  | 20.4666 |  |  | 20.211 | 20.3659 | 20.5825 | [5 empty] | 21.9709 | 20.3716 | 21.719 | 22.1158 | 19.6061 | 21.2722 | 21.9057 | 19.4295 | 19.9974 | 21.187 |  | 19.5943 | 21.0074 | 18.8873 | 19.7266 | 20.8684 | 19.4219 | 20.1945 | 19.0474 | 20.2252 | 19.2367 | 20.3517 | 18.7604 | 20.079 | 21.138 | 19.4298 | 19.8367 | 21.0652 | 18.9819 | 19.8373 | 20.8824 | 18.9821 | 20.2523 | 19.3378 | 20.0793 | 19.0048 | 20.2184 | -0.14 | 20.9483 | 0.048893 | 0.015936 | -26.9817 | 3.0699 | -1 | -0.01 | 0.76437 | -0.31617 | -6.6998 | 0.67722 | 0.69848 | -16.707 | 5.424 | 0.42128 | 0.43022 | 0.42951 | 0.4222 | 0.46399 | 0.43596 | 0.42858
42838.4114 | -767 | 22.9048 | 22.8784 | 22.8654 | 22.7996 | 22.4515 | 21.7981 | 22.7456 | 21.8643 | 22.4048 | 22.4118 | 22.3991 | 22.0949 | 21.3147 | 22.2674 | 21.5978 | 21.774 | 21.9056 | 21.1009 | 21.1997 | 21.4238 | 20.5064 | 20.6505 | 20.9457 | 21.9261 | 21.6921 | 21.3273 | 20.4709 | 20.5751 | 20.5529 | 22.0463 | 21.6715 | 21.2046 | 22.0124 | 21.7563 | 21.3769 | 19.9529 | 20.562 |  | 20.5894 | 20.2908 | 20.3607 | 19.3456 |  | 16.5763 | 16.6191 | 16.3614 | 16.5839 | 16.7307 | 17.3841 | 17.9271 | 15.7363 | 16.6256 | 15.9569 | 16.8017 | 17.8716 | 44.3738 | 47.0034 | 43.305 | 21.3116 |  |  | 0.47664 | 0.016363 | -31.7093 | 0.45205 | 0.26101 | -197.8217 | 20.9872 | -0.37492 | -0.09059 | 0.0047268 | 0.040219 | 8.8287 | 9.0584 | 1.9782 | 21.8127 | 22.0474 | 22.2467 | 22.31 | 22.1478 | 21.4969 | 20.3345 | 22.2322 | 22.399 | 22.4423 | 22.3937 | 22.0358 | 21.2867 | 22.3036 | 16.89 | 16.9958 | 16.1343 | 16.0914 | 16.0739 | 17.0575 | 16.6751 | 22.3901 | 22.1711 | 21.742 | 22.1067 | 21.8331 | 21.3485 | 21.9798 | 21.5747 | 20.96 | 20.1612 | 20.497 | 20.1062 | 19.8313 | -0.034589 | -0.23353 | 20.7245 | 22.0969 | 22.4069 | 20.1084 | 21.7132 | 22.1673 | 21.9746 | 21.7523 | 21.3261 | 21.8381 | 21.5095 | 21.1152 | 20.5577 | 20.5403 | 20.5634 | 20.5745 | 20.1853 |  | 20.2319 | 19.7494 | 20.1367 | 19.7655 | 20.1253 | 20.4234 |  | 20.477 |  |  | 20.2177 | 20.362 | 20.5934 | [5 empty] | 21.9761 | 20.3757 | 21.7191 | 22.1153 | 19.6154 | 21.2705 | 21.9039 | 19.4314 | 19.9982 | 21.1818 |  | 19.5883 | 21.0049 | 18.8825 | 19.7261 | 20.8737 | 19.4265 | 20.192 | 19.0492 | 20.2224 | 19.2403 | 20.3565 | 18.7626 | 20.0813 | 21.1393 | 19.4358 | 19.8335 | 21.0671 | 18.9794 | 19.8471 | 20.8882 | 18.9864 | 20.2583 | 19.3486 | 20.076 | 19.0066 | 20.2172 | 0.033814 | 20.9496 | 0.048764 | 0.016364 | -27.0849 | 3.0718 | -1.01 | -0.12 | 0.82455 | 0.15175 | -6.6801 | 0.7976 | 0.60687 | -16.7072 | 5.4418 | 0.42136 | 0.43028 | 0.42945 | 0.42079 | 0.46016 | 0.43534 | 0.42882
42838.4114 | -766 | 22.8993 | 22.8749 | 22.868 | 22.796 | 22.4445 | 21.7939 | 22.7488 | 21.8615 | 22.397 | 22.4113 | 22.3933 | 22.0858 | 21.3097 | 22.2703 | 21.5896 | 21.7757 | 21.9102 | 21.1013 | 21.1978 | 21.4235 | 20.5132 | 20.6555 | 20.952 | 21.9313 | 21.6944 | 21.325 | 20.4705 | 20.5786 | 20.5571 | 22.0543 | 21.6674 | 21.1968 | 22.0127 | 21.7583 | 21.3857 | 19.959 | 20.5646 |  | 20.5946 | 20.3008 | 20.3624 | 19.3648 |  | 16.5694 | 16.6105 | 16.3555 | 16.5765 | 16.7198 | 17.3893 | 17.9216 | 15.7362 | 16.6236 | 15.9472 | 16.7978 | 17.8691 | 44.3799 | 46.9975 | 43.3016 | 21.3151 |  |  | 0.53184 | 0.021619 | -32.0109 | 0.32851 | 0.17427 | -197.8164 | 20.6961 | -0.4978 | -0.041162 | -0.18451 | -0.077482 | 8.8281 | 9.0579 | 1.9789 | 21.817 | 22.0531 | 22.2433 | 22.3206 | 22.1519 | 21.5095 | 20.3376 | 22.2348 | 22.4058 | 22.4408 | 22.4026 | 22.0446 | 21.2873 | 22.3135 | 16.8941 | 17.0014 | 16.1821 | 16.0933 | 16.0857 | 17.0537 | 16.6742 | 22.3848 | 22.1603 | 21.7397 | 22.1031 | 21.8297 | 21.3486 | 21.9785 | 21.5699 | 20.9579 | 20.154 | 20.4944 | 20.1068 | 19.8305 | 0.061941 | -0.1139 | 20.7279 | 22.095 | 22.4074 | 20.113 | 21.7138 | 22.1653 | 21.9813 | 21.7548 | 21.3216 | 21.8354 | 21.51 | 21.1161 | 20.5598 | 20.5437 | 20.5528 | 20.5624 | 20.1869 |  | 20.2285 | 19.7484 | 20.1391 | 19.7649 | 20.1201 | 20.4208 |  | 20.4741 |  |  | 20.2096 | 20.3679 | 20.5949 | [5 empty] | 21.9647 | 20.3632 | 21.7163 | 22.111 | 19.611 | 21.2627 | 21.9025 | 19.4301 | 19.9967 | 21.1775 |  | 19.5856 | 20.9976 | 18.8739 | 19.7248 | 20.8703 | 19.4241 | 20.1924 | 19.0457 | 20.2145 | 19.241 | 20.3551 | 18.7581 | 20.0866 | 21.1452 | 19.4331 | 19.839 | 21.0667 | 18.9783 | 19.8518 | 20.884 | 18.9918 | 20.2645 | 19.3578 | 20.0758 | 19.0091 | 20.2228 | -0.076929 | 20.9478 | 0.048063 | 0.015573 | -27.0204 | 3.0742 | -1.08 | -0.07 | 0.87099 | 0.17442 | -6.7117 | 0.67993 | 0.49588 | -16.7071 | 5.404 | 0.4212 | 0.43039 | 0.42929 | 0.4199 | 0.45474 | 0.43501 | 0.4286
42838.4114 | -765 | 22.8996 | 22.8732 | 22.8673 | 22.8008 | 22.4441 | 21.7946 | 22.7475 | 21.8597 | 22.3924 | 22.4061 | 22.3938 | 22.0852 | 21.3094 | 22.2706 | 21.5841 | 21.7679 | 21.904 | 21.0969 | 21.1922 | 21.4189 | 20.4991 | 20.6567 | 20.9443 | 21.9151 | 21.6829 | 21.3199 | 20.4721 | 20.5629 | 20.5576 | 22.0526 | 21.6735 | 21.1994 | 22.015 | 21.7594 | 21.3766 | 19.9561 | 20.5772 |  | 20.5936 | 20.2992 | 20.3601 | 19.3732 |  | 16.5797 | 16.6282 | 16.3596 | 16.5875 | 16.7182 | 17.374 | 17.9 | 15.7323 | 16.634 | 15.958 | 16.8074 | 17.8662 | 44.3844 | 46.9896 | 43.3023 | 21.3103 |  |  | 0.30513 | 0.055131 | -32.599 | 0.43825 | 0.065188 | -197.8223 | 20.543 | -0.22378 | -0.49886 | -0.16311 | -0.060469 | 8.8284 | 9.0582 | 1.9782 | 21.8138 | 22.0453 | 22.2389 | 22.3221 | 22.1536 | 21.5036 | 20.3393 | 22.23 | 22.409 | 22.4424 | 22.3953 | 22.0401 | 21.2864 | 22.3083 | 16.9082 | 17.0028 | 16.2406 | 16.1071 | 16.101 | 17.0602 | 16.6725 | 22.3786 | 22.1666 | 21.7313 | 22.0973 | 21.8194 | 21.3391 | 21.9689 | 21.5634 | 20.9508 | 20.1598 | 20.4875 | 20.0936 | 19.8301 | -0.30983 | -0.070533 | 20.7247 | 22.0866 | 22.4079 | 20.1129 | 21.71 | 22.1738 | 21.9768 | 21.7541 | 21.3257 | 21.8299 | 21.5091 | 21.108 | 20.5646 | 20.5317 | 20.5469 | 20.5549 | 20.1877 |  | 20.2276 | 19.7524 | 20.1295 | 19.768 | 20.1201 | 20.4156 |  | 20.4696 |  |  | 20.23 | 20.384 | 20.6066 | [5 empty] | 21.9787 | 20.3853 | 21.7317 | 22.1237 | 19.6298 | 21.2721 | 21.9176 | 19.4326 | 19.9978 | 21.1709 |  | 19.5879 | 20.9973 | 18.8707 | 19.7137 | 20.8617 | 19.4258 | 20.193 | 19.0481 | 20.2077 | 19.2399 | 20.3532 | 18.7601 | 20.0913 | 21.1432 | 19.4358 | 19.8316 | 21.0615 | 18.9788 | 19.8541 | 20.8827 | 18.9862 | 20.2609 | 19.361 | 20.0629 | 19.0099 | 20.2154 | -0.12961 | 20.9487 | 0.047682 | 0.015384 | -27.0828 | 3.0775 | -1.16 | -0.2 | 0.65974 | 0.27855 | -6.7733 | 0.78535 | 0.30328 | -16.7069 | 5.3838 | 0.42115 | 0.42995 | 0.42921 | 0.41908 | 0.44803 | 0.43468 | 0.42881
42838.4114 | -764 | 22.9007 | 22.8739 | 22.8621 | 22.7985 | 22.4453 | 21.8028 | 22.7496 | 21.8614 | 22.397 | 22.4096 | 22.3956 | 22.088 | 21.3119 | 22.2753 | 21.5919 | 21.7656 | 21.9146 | 21.109 | 21.1928 | 21.424 | 20.5124 | 20.6569 | 20.9521 | 21.9254 | 21.6896 | 21.3304 | 20.4706 | 20.5741 | 20.5642 | 22.0518 | 21.6779 | 21.2042 | 22.0164 | 21.7602 | 21.3784 | 19.957 | 20.5877 |  | 20.5994 | 20.3051 | 20.3647 | 19.3784 |  | 16.5741 | 16.6313 | 16.3541 | 16.5794 | 16.7037 | 17.3545 | 17.8566 | 15.7127 | 16.6298 | 15.936 | 16.8043 | 17.8753 | 44.3953 | 46.9993 | 43.3009 | 21.3155 |  |  | 0.29133 | -0.052633 | -32.5004 | 0.2582 | 0.17558 | -197.8946 | 20.6041 | -0.26715 | -0.50781 | -0.3192 | -0.036338 | 8.8295 | 9.0591 | 1.978 | 21.8092 | 22.0484 | 22.231 | 22.3051 | 22.1481 | 21.4926 | 20.3338 | 22.2241 | 22.3964 | 22.4289 | 22.3836 | 22.0359 | 21.281 | 22.3044 | 16.9262 | 16.9848 | 16.2676 | 16.1365 | 16.112 | 17.0606 | 16.6691 | 22.3877 | 22.1705 | 21.7345 | 22.0956 | 21.8326 | 21.3459 | 21.9699 | 21.5659 | 20.951 | 20.1556 | 20.4871 | 20.1008 | 19.8316 | -0.16611 | -0.074337 | 20.7276 | 22.0842 | 22.4094 | 20.1149 | 21.7064 | 22.1613 | 21.9707 | 21.7473 | 21.3261 | 21.8299 | 21.5012 | 21.1102 | 20.5517 | 20.528 | 20.5323 | 20.5417 | 20.1996 |  | 20.2371 | 19.7797 | 20.1376 | 19.7709 | 20.124 | 20.4211 |  | 20.4768 |  |  | 20.2292 | 20.3691 | 20.5977 | [5 empty] | 21.9719 | 20.3773 | 21.7169 | 22.1071 | 19.6102 | 21.2636 | 21.9084 | 19.428 | 20.0011 | 21.1809 |  | 19.5929 | 20.9975 | 18.873 | 19.7217 | 20.8665 | 19.4274 | 20.1932 | 19.0356 | 20.2038 | 19.2328 | 20.3563 | 18.775 | 20.0977 | 21.1434 | 19.4437 | 19.8369 | 21.0636 | 18.9776 | 19.853 | 20.884 | 18.9974 | 20.2691 | 19.3619 | 20.0706 | 19.0106 | 20.2158 | 0.000795 | 20.9484 | 0.047627 | 0.014077 | -27.0213 | 3.0815 | -1.21 | -0.09 | 0.64465 | -0.27216 | -6.7631 | 0.60281 | 0.49772 | -16.7094 | 5.3916 | 0.42114 | 0.42947 | 0.42925 | 0.41712 | 0.44464 | 0.43457 | 0.42863
42838.4114 | -763 | 22.9023 | 22.8812 | 22.8705 | 22.7994 | 22.4542 | 21.8112 | 22.7599 | 21.8757 | 22.4004 | 22.425 | 22.406 | 22.0905 | 21.3205 | 22.2746 | 21.5939 | 21.771 | 21.9186 | 21.104 | 21.202 | 21.4263 | 20.5055 | 20.6524 | 20.9514 | 21.9247 | 21.6952 | 21.3253 | 20.4801 | 20.5699 | 20.564 | 22.0516 | 21.6739 | 21.1965 | 22.0131 | 21.7641 | 21.3824 | 19.9593 | 20.582 |  | 20.5979 | 20.2967 | 20.3596 | 19.367 |  | 16.5676 | 16.6277 | 16.3448 | 16.5599 | 16.6904 | 17.319 | 17.8499 | 15.7313 | 16.625 | 15.9514 | 16.8016 | 17.8724 | 44.3976 | 47.0073 | 43.3046 | 21.3153 |  |  | 0.37281 | -0.054605 | -32.2435 | 0.39488 | 0.059272 | -197.8079 | 20.6225 | -0.28029 | -0.18867 | 0.02214 | -0.051789 | 8.829 | 9.0588 | 1.9779 | 21.8104 | 22.0468 | 22.2365 | 22.316 | 22.1559 | 21.5007 | 20.3304 | 22.2277 | 22.4014 | 22.4341 | 22.392 | 22.0366 | 21.2807 | 22.3031 | 16.971 | 16.9735 | 16.2886 | 16.1533 | 16.1222 | 17.057 | 16.6746 | 22.3855 | 22.165 | 21.7384 | 22.1066 | 21.8338 | 21.3468 | 21.9727 | 21.569 | 20.9523 | 20.1594 | 20.4857 | 20.105 | 19.8181 | -0.2017 | 0.013345 | 20.7295 | 22.0871 | 22.4059 | 20.1178 | 21.7128 | 22.1549 | 21.9737 | 21.7458 | 21.3205 | 21.8318 | 21.5007 | 21.1153 | 20.5564 | 20.5358 | 20.5377 | 20.5362 | 20.1859 |  | 20.2272 | 19.7625 | 20.127 | 19.7638 | 20.1124 | 20.4065 |  | 20.467 |  |  | 20.224 | 20.3706 | 20.6116 | [5 empty] | 21.9661 | 20.3821 | 21.7268 | 22.1192 | 19.6079 | 21.2641 | 21.907 | 19.4379 | 20.0046 | 21.1756 |  | 19.6001 | 20.9983 | 18.8699 | 19.7225 | 20.8657 | 19.4216 | 20.1976 | 19.0415 | 20.2133 | 19.2402 | 20.3628 | 18.7779 | 20.0956 | 21.1477 | 19.4498 | 19.8257 | 21.0656 | 18.9732 | 19.8513 | 20.8802 | 18.9986 | 20.2677 | 19.3568 | 20.0625 | 19.0076 | 20.2161 | -0.18099 | 20.9479 | 0.046994 | 0.013119 | -27.1003 | 3.0855 | -0.94 | -0.23 | 0.72925 | -0.27721 | -6.7363 | 0.74548 | 0.28916 | -16.7047 | 5.3937 | 0.42118 | 0.42959 | 0.42906 | 0.41174 | 0.44295 | 0.43496 | 0.42913
42838.4115 | -762 | 22.9094 | 22.8736 | 22.8704 | 22.7977 | 22.4478 | 21.7996 | 22.7527 | 21.8716 | 22.3975 | 22.4149 | 22.4046 | 22.0879 | 21.3196 | 22.2678 | 21.5846 | 21.7661 | 21.9052 | 21.0955 | 21.1971 | 21.4137 | 20.5077 | 20.6603 | 20.9482 | 21.9227 | 21.6967 | 21.3241 | 20.4789 | 20.5674 | 20.5572 | 22.0556 | 21.6773 | 21.2007 | 22.0117 | 21.7502 | 21.3809 | 19.9567 | 20.581 |  | 20.5991 | 20.2922 | 20.3563 | 19.3697 |  | 16.579 | 16.6412 | 16.3521 | 16.5679 | 16.691 | 17.3242 | 17.8842 | 15.7475 | 16.6179 | 15.9341 | 16.8049 | 17.8756 | 44.3895 | 47.0138 | 43.3002 | 21.3126 |  |  | 0.32419 | -0.2892 | -31.9393 | 0.43562 | 0.046128 | -197.9215 | 20.8722 | -0.31249 | -0.21436 | -0.035345 | -0.045018 | 8.8288 | 9.0585 | 1.979 | 21.8155 | 22.0437 | 22.241 | 22.3166 | 22.1571 | 21.5007 | 20.333 | 22.229 | 22.404 | 22.4402 | 22.3947 | 22.0395 | 21.2884 | 22.3096 | 17.0233 | 16.9927 | 16.3148 | 16.1732 | 16.1228 | 17.0654 | 16.6893 | 22.3802 | 22.1514 | 21.7303 | 22.0935 | 21.8223 | 21.3355 | 21.9659 | 21.5568 | 20.9477 | 20.1509 | 20.4743 | 20.0951 | 19.8093 | -0.0513 | 0.038451 | 20.731 | 22.091 | 22.4069 | 20.1154 | 21.7028 | 22.1585 | 21.9715 | 21.7431 | 21.3169 | 21.8282 | 21.503 | 21.1106 | 20.5586 | 20.528 | 20.5293 | 20.5234 | 20.1892 |  | 20.2281 | 19.7652 | 20.1234 | 19.7721 | 20.1161 | 20.4127 |  | 20.4686 |  |  | 20.2347 | 20.3715 | 20.6191 | [5 empty] | 21.9756 | 20.3836 | 21.721 | 22.1203 | 19.6089 | 21.2639 | 21.9063 | 19.4329 | 19.9983 | 21.1851 |  | 19.5955 | 21.0031 | 18.884 | 19.7273 | 20.8722 | 19.4251 | 20.1965 | 19.0574 | 20.2041 | 19.245 | 20.3622 | 18.7742 | 20.093 | 21.1414 | 19.4479 | 19.8262 | 21.0524 | 18.9692 | 19.8482 | 20.8717 | 18.9867 | 20.2645 | 19.3612 | 20.0565 | 19.0104 | 20.2134 | -0.08806 | 20.9482 | 0.045132 | 0.012161 | -27.005 | 3.0887 | -1.01 | -0.12 | 0.68002 | -0.63798 | -6.7046 | 0.783 | 0.2551 | -16.7096 | 5.4263 | 0.42113 | 0.42939 | 0.42896 | 0.4069 | 0.44175 | 0.43479 | 0.42909
42838.4115 | -761 | 22.8985 | 22.8739 | 22.8719 | 22.8005 | 22.4478 | 21.801 | 22.747 | 21.8663 | 22.398 | 22.4109 | 22.4005 | 22.089 | 21.3092 | 22.2691 | 21.5996 | 21.7784 | 21.9079 | 21.0978 | 21.2 | 21.4255 | 20.5048 | 20.6567 | 20.9469 | 21.9224 | 21.6958 | 21.332 | 20.4789 | 20.5728 | 20.5651 | 22.0612 | 21.6647 | 21.2038 | 22.0129 | 21.7559 | 21.3691 | 19.9617 | 20.5848 |  | 20.5847 | 20.2908 | 20.3495 | 19.3595 |  | 16.575 | 16.6297 | 16.3407 | 16.5608 | 16.6761 | 17.3066 | 17.8917 | 15.7685 | 16.6191 | 15.9528 | 16.7999 | 17.8698 | 44.3707 | 47.0182 | 43.3017 | 21.3067 |  |  | 0.27359 | -0.44296 | -32.1817 | 0.39291 | 0.30175 | -197.8545 | 20.8795 | -0.37032 | -0.50859 | 0.089066 | -0.026617 | 8.829 | 9.0585 | 1.9784 | 21.814 | 22.0499 | 22.2415 | 22.3133 | 22.1651 | 21.5023 | 20.3433 | 22.2315 | 22.4028 | 22.4434 | 22.3969 | 22.0436 | 21.2916 | 22.3202 | 17.0109 | 16.9972 | 16.2837 | 16.1854 | 16.1136 | 17.0531 | 16.6761 | 22.3882 | 22.1688 | 21.7409 | 22.1002 | 21.8352 | 21.3471 | 21.9719 | 21.5663 | 20.9568 | 20.1615 | 20.489 | 20.0938 | 19.8256 | 0.014757 | -0.11314 | 20.7431 | 22.0982 | 22.4106 | 20.1244 | 21.7132 | 22.1718 | 21.9787 | 21.7528 | 21.3271 | 21.8377 | 21.51 | 21.1186 | 20.5631 | 20.5238 | 20.5322 | 20.5279 | 20.1901 |  | 20.2363 | 19.7745 | 20.1346 | 19.7808 | 20.1293 | 20.4127 |  | 20.4728 |  |  | 20.2322 | 20.3548 | 20.5964 | [5 empty] | 21.9748 | 20.369 | 21.7091 | 22.1062 | 19.597 | 21.2556 | 21.9043 | 19.4329 | 19.9934 | 21.1843 |  | 19.6051 | 20.9946 | 18.8717 | 19.7254 | 20.8627 | 19.4262 | 20.1788 | 19.0465 | 20.2061 | 19.2428 | 20.3623 | 18.7719 | 20.0937 | 21.1219 | 19.4479 | 19.8304 | 21.0567 | 18.9629 | 19.837 | 20.8694 | 18.994 | 20.2661 | 19.3536 | 20.051 | 19.0107 | 20.2065 | 0.11321 | 20.9468 | 0.044837 | 0.012495 | -27.0685 | 3.0908 | -1.19 | -0.12 | 0.62471 | -0.78956 | -6.7299 | 0.74361 | 0.65242 | -16.7063 | 5.4271 | 0.42137 | 0.42951 | 0.42916 | 0.40684 | 0.44366 | 0.43525 | 0.42899
42838.4115 | -760 | 22.8944 | 22.8682 | 22.8629 | 22.7943 | 22.4404 | 21.7984 | 22.7458 | 21.869 | 22.3897 | 22.4064 | 22.3962 | 22.09 | 21.3087 | 22.2714 | 21.5993 | 21.7737 | 21.9142 | 21.0962 | 21.2013 | 21.4217 | 20.5025 | 20.6563 | 20.9492 | 21.9217 | 21.6926 | 21.3259 | 20.4881 | 20.5672 | 20.5727 | 22.0555 | 21.6638 | 21.1991 | 22.0149 | 21.7522 | 21.3751 | 19.9574 | 20.5822 |  | 20.5998 | 20.289 | 20.3554 | 19.3468 |  | 16.5769 | 16.6334 | 16.3433 | 16.566 | 16.6742 | 17.3031 | 17.8988 | 15.8008 | 16.6217 | 16.0122 | 16.7987 | 17.8768 | 44.3574 | 47.0318 | 43.3136 | 21.3135 |  |  | 0.16714 | -0.29971 | -32.4341 | 0.39817 | 0.23866 | -197.8834 | 20.9708 | -0.40383 | -0.38872 | 0.086339 | 0.0020272 | 8.8291 | 9.0588 | 1.978 | 21.8115 | 22.0421 | 22.2341 | 22.312 | 22.1599 | 21.5 | 20.3305 | 22.2311 | 22.3968 | 22.4326 | 22.3903 | 22.0389 | 21.2843 | 22.3089 | 17.0092 | 17.0459 | 16.2714 | 16.1949 | 16.1239 | 17.0592 | 16.6796 | 22.3852 | 22.1633 | 21.7424 | 22.1042 | 21.8328 | 21.3414 | 21.967 | 21.575 | 20.9543 | 20.1569 | 20.4837 | 20.0929 | 19.818 | 0.067053 | -0.087461 | 20.733 | 22.0974 | 22.4065 | 20.1186 | 21.7098 | 22.1657 | 21.9796 | 21.7502 | 21.3193 | 21.8377 | 21.5034 | 21.1115 | 20.5595 | 20.5202 | 20.5271 | 20.5222 | 20.1929 |  | 20.2319 | 19.7642 | 20.1322 | 19.7833 | 20.1182 | 20.3987 |  | 20.4781 |  |  | 20.2269 | 20.3676 | 20.6078 | [5 empty] | 21.9712 | 20.3721 | 21.7122 | 22.117 | 19.5962 | 21.2629 | 21.9061 | 19.4326 | 19.9873 | 21.1721 |  | 19.5976 | 20.99 | 18.8714 | 19.7269 | 20.8572 | 19.4278 | 20.1809 | 19.0419 | 20.1943 | 19.2425 | 20.3607 | 18.7729 | 20.1016 | 21.1288 | 19.4486 | 19.8257 | 21.0541 | 18.9578 | 19.844 | 20.8751 | 18.9937 | 20.2727 | 19.358 | 20.046 | 19.0155 | 20.2125 | -0.14427 | 20.9473 | 0.045667 | 0.012393 | -27.008 | 3.092 | -1.36 | -0.53 | 0.48828 | -0.64946 | -6.7562 | 0.74858 | 0.58023 | -16.7074 | 5.4389 | 0.42115 | 0.42972 | 0.42872 | 0.40775 | 0.44544 | 0.43545 | 0.42905
42838.4115 | -759 | 22.8963 | 22.8718 | 22.8561 | 22.788 | 22.4451 | 21.7986 | 22.7441 | 21.8669 | 22.3945 | 22.4042 | 22.3967 | 22.089 | 21.3122 | 22.2626 | 21.5949 | 21.7722 | 21.9191 | 21.1013 | 21.2023 | 21.4259 | 20.5028 | 20.6553 | 20.9493 | 21.9255 | 21.6952 | 21.3332 | 20.4911 | 20.5682 | 20.5718 | 22.0417 | 21.664 | 21.1951 | 22.009 | 21.7507 | 21.3792 | 19.9555 | 20.5878 |  | 20.5907 | 20.2847 | 20.3411 | 19.3335 |  | 16.5776 | 16.6306 | 16.3452 | 16.5618 | 16.6825 | 17.3092 | 17.9254 | 15.8179 | 16.6119 | 16.1549 | 16.7911 | 17.8766 | 44.3413 | 47.0416 | 43.3259 | 21.3111 |  |  | 0.42999 | -0.21363 | -32.9216 | 0.45534 | 0.084244 | -197.8151 | 20.5345 | -0.4886 | -0.28986 | -0.22815 | -0.081474 | 8.8296 | 9.0591 | 1.9778 | 21.8208 | 22.042 | 22.246 | 22.3093 | 22.1539 | 21.5013 | 20.3371 | 22.237 | 22.4015 | 22.4373 | 22.3987 | 22.0388 | 21.2875 | 22.3105 | 17.0109 | 17.0786 | 16.302 | 16.2344 | 16.161 | 17.0577 | 16.6769 | 22.3907 | 22.1616 | 21.7377 | 22.1074 | 21.8295 | 21.3381 | 21.9675 | 21.5691 | 20.9539 | 20.1546 | 20.4838 | 20.0887 | 19.8065 | -0.021614 | -0.060643 | 20.7414 | 22.0978 | 22.4139 | 20.1169 | 21.7088 | 22.1691 | 21.9824 | 21.7517 | 21.3275 | 21.8366 | 21.5082 | 21.1045 | 20.5598 | 20.5246 | 20.5218 | 20.5205 | 20.1887 |  | 20.2337 | 19.7737 | 20.1463 | 19.7921 | 20.1199 | 20.4025 |  | 20.4727 |  |  | 20.2358 | 20.3678 | 20.6065 | [5 empty] | 21.9743 | 20.3759 | 21.7198 | 22.1141 | 19.6096 | 21.2625 | 21.9058 | 19.4401 | 19.9939 | 21.1822 |  | 19.5968 | 20.9985 | 18.8792 | 19.7264 | 20.8619 | 19.4328 | 20.1813 | 19.0546 | 20.1972 | 19.2506 | 20.3689 | 18.7796 | 20.1057 | 21.1343 | 19.4559 | 19.8256 | 21.0606 | 18.9524 | 19.8449 | 20.8735 | 18.9938 | 20.2682 | 19.3674 | 20.038 | 19.0185 | 20.2094 | -0.019425 | 20.9484 | 0.046121 | 0.012517 | -26.9938 | 3.0925 | -1.1 | -0.09 | 0.78318 | -0.54832 | -6.8068 | 0.80051 | 0.34473 | -16.7047 | 5.3821 | 0.42132 | 0.42992 | 0.42853 | 0.40738 | 0.44173 | 0.43576 | 0.42929
42838.4115 | -758 | 22.8985 | 22.8748 | 22.8638 | 22.798 | 22.4453 | 21.801 | 22.7433 | 21.8593 | 22.3945 | 22.4084 | 22.4036 | 22.0917 | 21.3119 | 22.2705 | 21.5929 | 21.7772 | 21.9169 | 21.1043 | 21.2055 | 21.4277 | 20.5071 | 20.6578 | 20.9495 | 21.9301 | 21.6933 | 21.3381 | 20.4832 | 20.5668 | 20.5766 | 22.0476 | 21.6698 | 21.2018 | 22.0117 | 21.7577 | 21.3774 | 19.9566 | 20.5857 |  | 20.5944 | 20.2905 | 20.3558 | 19.3282 |  | 16.5754 | 16.6306 | 16.3489 | 16.5621 | 16.694 | 17.3408 | 17.9657 | 15.8297 | 16.6171 | 16.3044 | 16.7848 | 17.869 | 44.3159 | 47.0528 | 43.3293 | 21.3097 |  |  | 0.38661 | -0.39171 | -32.7948 | 0.41985 | 0.20581 | -197.8696 | 20.8046 | -0.38083 | -0.43406 | -0.15409 | -0.063767 | 8.8299 | 9.0596 | 1.9791 | 21.8157 | 22.0376 | 22.2406 | 22.3123 | 22.1502 | 21.5022 | 20.3265 | 22.233 | 22.3988 | 22.4341 | 22.3937 | 22.036 | 21.2877 | 22.3054 | 17.0108 | 17.132 | 16.3467 | 16.299 | 16.227 | 17.0655 | 16.6848 | 22.3861 | 22.1661 | 21.7349 | 22.1039 | 21.8257 | 21.3471 | 21.9757 | 21.5709 | 20.9535 | 20.1521 | 20.4837 | 20.0879 | 19.8019 | 0.055453 | -0.15403 | 20.746 | 22.0893 | 22.4106 | 20.1201 | 21.7069 | 22.1752 | 21.9858 | 21.757 | 21.3292 | 21.8418 | 21.5139 | 21.1124 | 20.5638 | 20.5252 | 20.528 | 20.5225 | 20.1844 |  | 20.2365 | 19.778 | 20.1442 | 19.7906 | 20.1237 | 20.4047 |  | 20.4743 |  |  | 20.2364 | 20.3713 | 20.6016 | [5 empty] | 21.9612 | 20.3757 | 21.7216 | 22.1138 | 19.6097 | 21.2583 | 21.9017 | 19.4305 | 19.9974 | 21.1826 |  | 19.6099 | 20.9868 | 18.886 | 19.7235 | 20.8689 | 19.4323 | 20.1766 | 19.0594 | 20.1993 | 19.2451 | 20.3679 | 18.7757 | 20.1123 | 21.1319 | 19.4539 | 19.8257 | 21.0592 | 18.9573 | 19.8446 | 20.8707 | 18.999 | 20.2648 | 19.3594 | 20.0239 | 19.0189 | 20.2135 | -0.12405 | 20.948 | 0.046318 | 0.012698 | -27.1155 | 3.0927 | -1.03 | -0.07 | 0.74264 | -0.74247 | -6.7937 | 0.76869 | 0.53885 | -16.7079 | 5.4177 | 0.42154 | 0.42973 | 0.4287 | 0.4083 | 0.43768 | 0.43595 | 0.42933
42838.4115 | -757 | 22.9051 | 22.8802 | 22.8661 | 22.8037 | 22.4499 | 21.8071 | 22.7457 | 21.8644 | 22.4028 | 22.4131 | 22.4116 | 22.0905 | 21.3186 | 22.2743 | 21.59 | 21.7669 | 21.9157 | 21.1009 | 21.2008 | 21.4218 | 20.5032 | 20.6555 | 20.9485 | 21.9271 | 21.6869 | 21.3298 | 20.4772 | 20.5653 | 20.571 | 22.0486 | 21.6678 | 21.1973 | 22.0091 | 21.7547 | 21.376 | 19.9517 | 20.588 |  | 20.5942 | 20.2759 | 20.3488 | 19.3247 |  | 16.5731 | 16.6293 | 16.3506 | 16.5733 | 16.7314 | 17.3706 | 18.0024 | 15.856 | 16.6082 | 16.3706 | 16.7842 | 17.8652 | 44.3116 | 47.0681 | 43.3351 | 21.314 |  |  | 0.21313 | -0.39499 | -33.2909 | 0.63013 | 0.25509 | -197.8407 | 20.4517 | -0.34995 | -0.64948 | 0.096829 | -0.16619 | 8.8297 | 9.0595 | 1.9785 | 21.8118 | 22.0383 | 22.2445 | 22.3065 | 22.1497 | 21.5004 | 20.3209 | 22.2228 | 22.3991 | 22.4383 | 22.3894 | 22.033 | 21.2769 | 22.3002 | 17.0204 | 17.1547 | 16.3267 | 16.3126 | 16.2622 | 17.0617 | 16.6857 | 22.3917 | 22.1677 | 21.7374 | 22.1018 | 21.8306 | 21.3495 | 21.9653 | 21.5738 | 20.9539 | 20.1537 | 20.4851 | 20.0868 | 19.8081 | 0.013971 | -0.1508 | 20.7495 | 22.0923 | 22.4108 | 20.1177 | 21.7126 | 22.168 | 21.987 | 21.7603 | 21.3265 | 21.8375 | 21.5113 | 21.1185 | 20.5633 | 20.5314 | 20.5232 | 20.5203 | 20.172 |  | 20.238 | 19.7961 | 20.1409 | 19.787 | 20.1169 | 20.393 |  | 20.4731 |  |  | 20.2415 | 20.3656 | 20.6052 | [5 empty] | 21.9667 | 20.3751 | 21.7084 | 22.1066 | 19.6101 | 21.2566 | 21.9025 | 19.4309 | 19.9939 | 21.1759 |  | 19.6099 | 20.9926 | 18.8809 | 19.7223 | 20.8689 | 19.4294 | 20.1827 | 19.063 | 20.1982 | 19.2455 | 20.3641 | 18.7745 | 20.1017 | 21.1272 | 19.4481 | 19.8187 | 21.0667 | 18.9568 | 19.8443 | 20.8693 | 19.0059 | 20.2589 | 19.3573 | 20.0297 | 19.0126 | 20.2107 | -0.058008 | 20.9477 | 0.046926 | 0.013025 | -27.0187 | 3.0928 | -1.06 | -0.36 | 0.55139 | -0.74558 | -6.8448 | 0.94171 | 0.59993 | -16.7076 | 5.3718 | 0.42193 | 0.42912 | 0.42857 | 0.40679 | 0.44001 | 0.43588 | 0.42922
42838.4115 | -756 | 22.9012 | 22.8709 | 22.8634 | 22.8008 | 22.447 | 21.8059 | 22.7499 | 21.8666 | 22.4017 | 22.4125 | 22.3993 | 22.0866 | 21.3149 | 22.2707 | 21.5926 | 21.7724 | 21.9207 | 21.1007 | 21.2046 | 21.4321 | 20.507 | 20.6543 | 20.9497 | 21.93 | 21.6951 | 21.3288 | 20.4811 | 20.5667 | 20.571 | 22.0445 | 21.6699 | 21.1965 | 22.0074 | 21.7546 | 21.3743 | 19.9544 | 20.5832 |  | 20.5938 | 20.2761 | 20.3417 | 19.3217 |  | 16.5734 | 16.6327 | 16.3621 | 16.6092 | 16.754 | 17.4029 | 18.0297 | 15.8986 | 16.6126 | 16.4516 | 16.7886 | 17.8696 | 44.3013 | 47.0811 | 43.3384 | 21.3117 |  |  | 0.35507 | -0.31285 | -33.9389 | -0.011214 | 0.2886 | -197.8453 | 20.2184 | -0.32892 | -0.47901 | -0.0097494 | 0.06487 | 8.8302 | 9.0598 | 1.9781 | 21.8175 | 22.0556 | 22.2508 | 22.3195 | 22.1643 | 21.504 | 20.3363 | 22.2366 | 22.4074 | 22.4492 | 22.3962 | 22.0481 | 21.2921 | 22.3193 | 17.0242 | 17.1409 | 16.2865 | 16.2844 | 16.2403 | 17.0619 | 16.6831 | 22.3892 | 22.167 | 21.7278 | 22.0947 | 21.8268 | 21.3371 | 21.9699 | 21.5602 | 20.9544 | 20.1548 | 20.4723 | 20.0674 | 19.7961 | 0.015937 | -0.12512 | 20.7416 | 22.0971 | 22.4148 | 20.1217 | 21.7039 | 22.1668 | 21.9813 | 21.7524 | 21.3249 | 21.8346 | 21.5049 | 21.1142 | 20.5544 | 20.5341 | 20.5162 | 20.516 | 20.1502 |  | 20.2341 | 19.806 | 20.1304 | 19.7949 | 20.1236 | 20.3841 |  | 20.4678 |  |  | 20.2494 | 20.3653 | 20.6099 | [5 empty] | 21.9779 | 20.3744 | 21.7194 | 22.112 | 19.6097 | 21.2637 | 21.9106 | 19.4319 | 19.9948 | 21.1802 |  | 19.6051 | 20.9967 | 18.8876 | 19.7187 | 20.868 | 19.4296 | 20.1854 | 19.0644 | 20.201 | 19.2479 | 20.3604 | 18.7755 | 20.0945 | 21.121 | 19.4518 | 19.816 | 21.0585 | 18.9468 | 19.8479 | 20.8654 | 19.0013 | 20.2549 | 19.3526 | 20.0276 | 19.0058 | 20.2072 | -0.10828 | 20.9476 | 0.046908 | 0.011689 | -27.0973 | 3.0929 | -1.2 | 0.1 | 0.7117 | -0.66355 | -6.9112 | -0.12563 | 0.63816 | -16.7087 | 5.3414 | 0.42241 | 0.4285 | 0.42857 | 0.40639 | 0.44418 | 0.43605 | 0.42959
42838.4115 | -755 | 22.9036 | 22.8737 | 22.8671 | 22.7965 | 22.4528 | 21.8003 | 22.7457 | 21.8681 | 22.3972 | 22.4111 | 22.3971 | 22.0899 | 21.3166 | 22.2687 | 21.5907 | 21.7688 | 21.9108 | 21.0915 | 21.1986 | 21.4293 | 20.5061 | 20.6545 | 20.9474 | 21.9208 | 21.695 | 21.3284 | 20.4769 | 20.5574 | 20.5589 | 22.04 | 21.6645 | 21.199 | 22.0052 | 21.7561 | 21.3721 | 19.9537 | 20.5862 |  | 20.5935 | 20.2783 | 20.3408 | 19.3135 |  | 16.5773 | 16.6369 | 16.3844 | 16.6424 | 16.7862 | 17.4318 | 18.0594 | 15.9183 | 16.6122 | 16.5929 | 16.7916 | 17.8641 | 44.2945 | 47.0888 | 43.3494 | 21.3151 |  |  | 0.21379 | -0.23991 | -35.3195 | 0.43037 | 0.10198 | -197.8361 | 19.6533 | -0.32498 | -0.48602 | -0.26466 | -0.053004 | 8.8286 | 9.0582 | 1.978 | 21.8136 | 22.0475 | 22.2406 | 22.3162 | 22.1535 | 21.504 | 20.3283 | 22.2358 | 22.4019 | 22.4439 | 22.3913 | 22.0383 | 21.2843 | 22.3062 | 17.0388 | 17.1416 | 16.2713 | 16.2801 | 16.2183 | 17.0565 | 16.6811 | 22.3838 | 22.1662 | 21.7398 | 22.0986 | 21.8287 | 21.3372 | 21.9695 | 21.5679 | 20.9584 | 20.1563 | 20.4717 | 20.0756 | 19.7863 | 0.087303 | -0.074908 | 20.7461 | 22.1006 | 22.4109 | 20.1324 | 21.7154 | 22.1685 | 21.9859 | 21.7542 | 21.3304 | 21.8447 | 21.5085 | 21.1125 | 20.5677 | 20.5367 | 20.5216 | 20.5209 | 20.1477 |  | 20.2373 | 19.8158 | 20.1379 | 19.7941 | 20.1198 | 20.3794 |  | 20.4666 |  |  | 20.2446 | 20.3627 | 20.5988 | [5 empty] | 21.9719 | 20.3663 | 21.7215 | 22.106 | 19.6037 | 21.2598 | 21.9066 | 19.4286 | 19.9887 | 21.1803 |  | 19.6132 | 20.9935 | 18.8903 | 19.7212 | 20.8646 | 19.4278 | 20.1819 | 19.0624 | 20.1989 | 19.2564 | 20.3601 | 18.7752 | 20.099 | 21.123 | 19.4584 | 19.82 | 21.0566 | 18.9467 | 19.8503 | 20.8683 | 19.0017 | 20.2622 | 19.3553 | 20.0249 | 19.009 | 20.2153 | -0.1003 | 20.9473 | 0.046711 | 0.010513 | -27.0596 | 3.093 | -1.33 | 0 | 0.55223 | -0.58108 | -7.0504 | 0.77826 | 0.37937 | -16.7091 | 5.2665 | 0.42259 | 0.42847 | 0.42847 | 0.40414 | 0.44563 | 0.43626 | 0.42991
42838.4116 | -754 | 22.9021 | 22.8741 | 22.8681 | 22.7974 | 22.4486 | 21.8053 | 22.7488 | 21.8621 | 22.4021 | 22.4104 | 22.4049 | 22.0926 | 21.3175 | 22.2784 | 21.5915 | 21.7667 | 21.9097 | 21.1007 | 21.1974 | 21.4233 | 20.5021 | 20.652 | 20.953 | 21.9232 | 21.698 | 21.3293 | 20.475 | 20.5583 | 20.5592 | 22.0457 | 21.6613 | 21.1953 | 22.013 | 21.7524 | 21.373 | 19.9548 | 20.5926 |  | 20.591 | 20.2768 | 20.3478 | 19.2964 |  | 16.5786 | 16.6289 | 16.3958 | 16.6611 | 16.801 | 17.4484 | 18.076 | 15.8953 | 16.603 | 16.7009 | 16.7817 | 17.8699 | 44.2792 | 47.1062 | 43.3648 | 21.3098 |  |  | 0.51672 | -0.12097 | -35.3766 | 0.40343 | 0.0481 | -197.8125 | 19.7768 | -0.34338 | -0.37646 | 0.054659 | -0.11133 | 8.8283 | 9.058 | 1.9787 | 21.8154 | 22.044 | 22.2385 | 22.312 | 22.1497 | 21.5041 | 20.3313 | 22.2279 | 22.3957 | 22.4387 | 22.3954 | 22.0407 | 21.281 | 22.306 | 17.0486 | 17.1297 | 16.2728 | 16.2768 | 16.215 | 17.054 | 16.6794 | 22.3914 | 22.171 | 21.7365 | 22.1015 | 21.8337 | 21.3463 | 21.9797 | 21.572 | 20.9595 | 20.1586 | 20.4705 | 20.0742 | 19.7867 | -0.080594 | -0.20348 | 20.7485 | 22.0939 | 22.4062 | 20.131 | 21.711 | 22.1638 | 21.9758 | 21.7492 | 21.3214 | 21.838 | 21.5001 | 21.1039 | 20.5638 | 20.5247 | 20.5134 | 20.5111 | 20.1328 |  | 20.2433 | 19.8264 | 20.1372 | 19.7872 | 20.1229 | 20.3811 |  | 20.4698 |  |  | 20.2465 | 20.3597 | 20.6042 | [5 empty] | 21.9701 | 20.3664 | 21.7153 | 22.1094 | 19.602 | 21.2617 | 21.9022 | 19.424 | 19.9847 | 21.1751 |  | 19.613 | 20.9918 | 18.8889 | 19.7242 | 20.8604 | 19.4263 | 20.1733 | 19.0605 | 20.1977 | 19.2478 | 20.3651 | 18.7761 | 20.1009 | 21.1261 | 19.4614 | 19.8177 | 21.0528 | 18.9547 | 19.8426 | 20.8677 | 19.0021 | 20.2585 | 19.3567 | 20.0162 | 19.0136 | 20.2178 | -0.18229 | 20.9473 | 0.046361 | 0.0115 | -26.9879 | 3.0931 | -1.26 | -0.81 | 0.85853 | -0.41261 | -7.056 | 0.7535 | 0.26055 | -16.7086 | 5.2831 | 0.4232 | 0.42815 | 0.42876 | 0.40276 | 0.44527 | 0.43677 | 0.42998
42838.4116 | -753 | 22.9019 | 22.875 | 22.8587 | 22.7877 | 22.4475 | 21.7972 | 22.7462 | 21.8688 | 22.3952 | 22.4173 | 22.3923 | 22.0826 | 21.3121 | 22.2593 | 21.5919 | 21.7675 | 21.9121 | 21.1032 | 21.2032 | 21.4239 | 20.5063 | 20.6538 | 20.9514 | 21.9255 | 21.6907 | 21.3298 | 20.4781 | 20.5665 | 20.5627 | 22.0429 | 21.665 | 21.1956 | 22.0057 | 21.7565 | 21.3728 | 19.9604 | 20.5904 |  | 20.5947 | 20.2842 | 20.3442 | 19.2693 |  | 16.5826 | 16.641 | 16.4072 | 16.6767 | 16.8148 | 17.4699 | 18.0949 | 15.8961 | 16.6171 | 16.7246 | 16.7834 | 17.8701 | 44.2548 | 47.1161 | 43.3783 | 21.3192 |  |  | 0.39976 | -0.39105 | -35.3352 | -0.015158 | 0.20844 | -197.8604 | 19.7367 | -0.37032 | -0.31749 | 0.070394 | -0.042067 | 8.8281 | 9.058 | 1.9784 | 21.8194 | 22.0489 | 22.2433 | 22.3163 | 22.1463 | 21.4995 | 20.3348 | 22.233 | 22.398 | 22.4385 | 22.3923 | 22.0419 | 21.2871 | 22.3123 | 17.0656 | 17.117 | 16.2904 | 16.2796 | 16.2237 | 17.052 | 16.6838 | 22.39 | 22.1637 | 21.7296 | 22.1036 | 21.8262 | 21.345 | 21.9739 | 21.5635 | 20.9464 | 20.1545 | 20.4553 | 20.0666 | 19.7802 | -0.13033 | -0.20539 | 20.7457 | 22.0943 | 22.4078 | 20.1166 | 21.709 | 22.1623 | 21.9773 | 21.7506 | 21.3206 | 21.8344 | 21.5019 | 21.1003 | 20.5666 | 20.5324 | 20.5117 | 20.5143 | 20.1264 |  | 20.2563 | 19.8527 | 20.1367 | 19.7994 | 20.1237 | 20.3892 |  | 20.4815 |  |  | 20.2513 | 20.3532 | 20.6099 | [5 empty] | 21.9692 | 20.3726 | 21.714 | 22.1133 | 19.6016 | 21.2573 | 21.8992 | 19.4211 | 19.9856 | 21.1666 |  | 19.6136 | 20.9975 | 18.8853 | 19.7229 | 20.8598 | 19.4257 | 20.175 | 19.0614 | 20.1971 | 19.2449 | 20.3713 | 18.7799 | 20.1031 | 21.1308 | 19.4653 | 19.8177 | 21.0551 | 18.9532 | 19.8436 | 20.8727 | 19.0034 | 20.2629 | 19.3653 | 20.0138 | 19.0126 | 20.2218 | -0.27282 | 20.9475 | 0.046551 | 0.011929 | -27.0902 | 3.093 | -1.04 | 0.43 | 0.75514 | -0.74187 | -7.052 | -0.14606 | 0.5424 | -16.7113 | 5.278 | 0.42381 | 0.42741 | 0.42845 | 0.40064 | 0.44382 | 0.43771 | 0.43002
42838.4116 | -752 | 22.9065 | 22.8807 | 22.8664 | 22.8014 | 22.4564 | 21.8076 | 22.7559 | 21.8703 | 22.4036 | 22.4163 | 22.3976 | 22.0918 | 21.3186 | 22.2748 | 21.594 | 21.7651 | 21.9154 | 21.1038 | 21.2036 | 21.4272 | 20.5041 | 20.6536 | 20.9503 | 21.9269 | 21.6918 | 21.3282 | 20.4886 | 20.5641 | 20.5623 | 22.053 | 21.6647 | 21.1977 | 22.0071 | 21.7523 | 21.3803 | 19.9551 | 20.5971 |  | 20.5963 | 20.287 | 20.3455 | 19.2557 |  | 16.5839 | 16.6431 | 16.4084 | 16.6886 | 16.8273 | 17.4794 | 18.1186 | 15.8908 | 16.61 | 16.7577 | 16.786 | 17.8723 | 44.2345 | 47.1288 | 43.3714 | 21.3236 |  |  | 0.45627 | -0.40879 | -35.0914 | 0.67744 | 0.17492 | -197.8473 | 19.6605 | -0.32629 | -0.2451 | 0.028224 | -0.0049168 | 8.8289 | 9.059 | 1.9781 | 21.8132 | 22.0526 | 22.245 | 22.3116 | 22.1529 | 21.5001 | 20.3325 | 22.233 | 22.4047 | 22.442 | 22.3959 | 22.0339 | 21.2826 | 22.3086 | 17.0886 | 17.1121 | 16.3055 | 16.2943 | 16.2223 | 17.0585 | 16.6803 | 22.3778 | 22.1616 | 21.7372 | 22.0991 | 21.8226 | 21.336 | 21.9667 | 21.5562 | 20.9458 | 20.151 | 20.4566 | 20.0522 | 19.7813 | -0.098091 | -0.1508 | 20.7473 | 22.0986 | 22.4171 | 20.1314 | 21.7227 | 22.1732 | 21.9864 | 21.7595 | 21.328 | 21.8442 | 21.5147 | 21.1154 | 20.5676 | 20.5532 | 20.5278 | 20.5192 | 20.1076 |  | 20.2409 | 19.86 | 20.1408 | 19.8019 | 20.1235 | 20.3784 |  | 20.4736 |  |  | 20.2597 | 20.3485 | 20.5954 | [5 empty] | 21.9624 | 20.3687 | 21.7081 | 22.1111 | 19.6038 | 21.2545 | 21.8971 | 19.4252 | 19.9917 | 21.1737 |  | 19.6096 | 20.9949 | 18.8859 | 19.7274 | 20.869 | 19.4195 | 20.1749 | 19.0677 | 20.1967 | 19.2442 | 20.3705 | 18.7713 | 20.1058 | 21.126 | 19.4637 | 19.8121 | 21.0475 | 18.9525 | 19.845 | 20.8765 | 19.0029 | 20.2627 | 19.3585 | 19.999 | 19.0063 | 20.2205 | 0.005618 | 20.9471 | 0.04528 | 0.012212 | -27.1009 | 3.0931 | -1.06 | -0.7 | 0.80675 | -0.75851 | -7.0277 | 0.97644 | 0.49689 | -16.711 | 5.2679 | 0.42382 | 0.42734 | 0.42838 | 0.39884 | 0.44174 | 0.43791 | 0.42987
42838.4116 | -751 | 22.8919 | 22.8703 | 22.8605 | 22.8003 | 22.4462 | 21.796 | 22.7487 | 21.8625 | 22.3971 | 22.4052 | 22.3928 | 22.0819 | 21.3163 | 22.266 | 21.5896 | 21.7664 | 21.9126 | 21.1008 | 21.2017 | 21.4264 | 20.4996 | 20.6477 | 20.9545 | 21.9297 | 21.6871 | 21.3294 | 20.4779 | 20.5601 | 20.559 | 22.0461 | 21.6712 | 21.1995 | 22.0154 | 21.7556 | 21.3792 | 19.9554 | 20.5989 |  | 20.5982 | 20.285 | 20.3439 | 19.2479 |  | 16.5887 | 16.6375 | 16.4166 | 16.701 | 16.8464 | 17.4939 | 18.1433 | 15.8679 | 16.609 | 16.8132 | 16.7942 | 17.8624 | 44.223 | 47.1268 | 43.3664 | 21.3075 |  |  | 0.29002 | -0.18997 | -34.8542 | 0.23126 | 0.27809 | -197.8309 | 19.7387 | -0.24875 | 0.17095 | 0.071233 | -0.065503 | 8.8282 | 9.0578 | 1.978 | 21.8132 | 22.0478 | 22.2423 | 22.3108 | 22.1532 | 21.5036 | 20.3322 | 22.2352 | 22.4059 | 22.4383 | 22.3963 | 22.037 | 21.2855 | 22.3113 | 17.1241 | 17.1059 | 16.323 | 16.3066 | 16.2291 | 17.0657 | 16.6824 | 22.382 | 22.1647 | 21.7368 | 22.1049 | 21.8305 | 21.3408 | 21.9689 | 21.5656 | 20.9549 | 20.1531 | 20.4555 | 20.0601 | 19.7864 | -0.11166 | -0.19283 | 20.7414 | 22.0965 | 22.4139 | 20.1395 | 21.7221 | 22.1727 | 21.9881 | 21.7624 | 21.3377 | 21.8465 | 21.5193 | 21.1144 | 20.569 | 20.5527 | 20.5206 | 20.5219 | 20.1071 |  | 20.2343 | 19.8684 | 20.1331 | 19.7971 | 20.1197 | 20.3773 |  | 20.4636 |  |  | 20.2597 | 20.3494 | 20.6078 | [5 empty] | 21.9676 | 20.3733 | 21.7067 | 22.1123 | 19.6006 | 21.2622 | 21.9018 | 19.424 | 19.9892 | 21.1884 |  | 19.618 | 21.002 | 18.8898 | 19.7325 | 20.8711 | 19.4297 | 20.172 | 19.0713 | 20.2014 | 19.2418 | 20.3671 | 18.7615 | 20.0965 | 21.127 | 19.4665 | 19.8122 | 21.0451 | 18.9557 | 19.8465 | 20.8707 | 18.9951 | 20.2562 | 19.3504 | 20.0027 | 19.0045 | 20.2163 | -0.045766 | 20.946 | 0.045962 | 0.011856 | -27.1753 | 3.0931 | -0.91 | 0.01 | 0.64319 | -0.51707 | -7.0038 | 0.5705 | 0.62653 | -16.7107 | 5.2785 | 0.42361 | 0.42685 | 0.42838 | 0.39573 | 0.44004 | 0.43813 | 0.4298
42838.4116 | -750 | 22.8915 | 22.8702 | 22.8583 | 22.7941 | 22.4374 | 21.7944 | 22.7465 | 21.8645 | 22.3931 | 22.405 | 22.3936 | 22.0821 | 21.3117 | 22.2664 | 21.5957 | 21.7748 | 21.9107 | 21.0965 | 21.1958 | 21.4296 | 20.5059 | 20.6491 | 20.9533 | 21.925 | 21.6884 | 21.324 | 20.4703 | 20.5572 | 20.5585 | 22.04 | 21.6659 | 21.2006 | 22.0092 | 21.7579 | 21.3738 | 19.9527 | 20.6014 |  | 20.5898 | 20.2742 | 20.3424 | 19.2384 |  | 16.5864 | 16.6401 | 16.418 | 16.6873 | 16.8503 | 17.5144 | 18.165 | 15.862 | 16.6014 | 16.8059 | 16.8009 | 17.8615 | 44.2388 | 47.145 | 43.3544 | 21.3096 |  |  | 0.40304 | -0.40879 | -35.1144 | 0.34363 | 0.31949 | -197.8611 | 19.5771 | -0.29212 | -0.23673 | -0.043527 | -0.11238 | 8.8285 | 9.0579 | 1.9784 | 21.8176 | 22.0451 | 22.2475 | 22.3168 | 22.1482 | 21.502 | 20.3243 | 22.2334 | 22.403 | 22.4391 | 22.3966 | 22.0376 | 21.2889 | 22.3071 | 17.1678 | 17.0794 | 16.3203 | 16.2917 | 16.231 | 17.056 | 16.6844 | 22.3858 | 22.1681 | 21.737 | 22.108 | 21.8362 | 21.3435 | 21.9677 | 21.5649 | 20.9574 | 20.1542 | 20.4531 | 20.0519 | 19.7946 | -0.094159 | -0.20786 | 20.7296 | 22.0876 | 22.4004 | 20.1249 | 21.707 | 22.1586 | 21.9796 | 21.7488 | 21.3253 | 21.8317 | 21.508 | 21.1032 | 20.5613 | 20.5465 | 20.51 | 20.5113 | 20.1001 |  | 20.2354 | 19.8793 | 20.1356 | 19.7943 | 20.1175 | 20.3772 |  | 20.4706 |  |  | 20.2615 | 20.353 | 20.6199 | [5 empty] | 21.9727 | 20.3829 | 21.7098 | 22.1204 | 19.6057 | 21.2558 | 21.9098 | 19.4152 | 19.9783 | 21.1836 |  | 19.6221 | 20.9916 | 18.8783 | 19.7284 | 20.8656 | 19.4209 | 20.1666 | 19.0764 | 20.1963 | 19.2368 | 20.3621 | 18.7676 | 20.1038 | 21.1281 | 19.4698 | 19.818 | 21.0512 | 18.9444 | 19.8468 | 20.8748 | 18.9944 | 20.2549 | 19.3538 | 20.0044 | 19.0128 | 20.2194 | -0.12831 | 20.9462 | 0.046816 | 0.012691 | -27.181 | 3.0932 | -0.93 | -0.08 | 0.75823 | -0.75851 | -7.0299 | 0.69543 | 0.67157 | -16.7126 | 5.257 | 0.42384 | 0.42663 | 0.42839 | 0.38975 | 0.44058 | 0.43831 | 0.42961
42838.4116 | -749 | 22.8933 | 22.8694 | 22.863 | 22.7941 | 22.4469 | 21.7977 | 22.7457 | 21.8623 | 22.3913 | 22.401 | 22.39 | 22.0845 | 21.3096 | 22.275 | 21.6008 | 21.772 | 21.9098 | 21.097 | 21.2036 | 21.4312 | 20.5118 | 20.6557 | 20.9554 | 21.9358 | 21.6979 | 21.3321 | 20.4743 | 20.5648 | 20.5633 | 22.0414 | 21.6632 | 21.2 | 22.0091 | 21.7543 | 21.3747 | 19.9535 | 20.6012 |  | 20.5853 | 20.2774 | 20.3416 | 19.2371 |  | 16.5906 | 16.642 | 16.4215 | 16.687 | 16.8605 | 17.5283 | 18.1907 | 15.88 | 16.6 | 16.7167 | 16.802 | 17.8637 | 44.2565 | 47.1469 | 43.3596 | 21.322 |  |  | 0.35705 | -0.29971 | -34.8299 | 0.36991 | 0.3576 | -197.8631 | 19.6684 | -0.29409 | -0.40078 | -0.23633 | -0.12609 | 8.8285 | 9.0581 | 1.9789 | 21.8066 | 22.0377 | 22.243 | 22.3 | 22.1477 | 21.4872 | 20.3284 | 22.2229 | 22.401 | 22.4297 | 22.3876 | 22.0236 | 21.2786 | 22.2952 | 17.213 | 17.0683 | 16.3036 | 16.2982 | 16.2313 | 17.0536 | 16.6767 | 22.3805 | 22.1626 | 21.732 | 22.0965 | 21.8262 | 21.336 | 21.9693 | 21.5667 | 20.9572 | 20.1504 | 20.4458 | 20.0398 | 19.8051 | -0.1498 | -0.080043 | 20.7336 | 22.085 | 22.4045 | 20.1316 | 21.7061 | 22.1652 | 21.9694 | 21.7488 | 21.3279 | 21.834 | 21.5048 | 21.1055 | 20.5659 | 20.5408 | 20.5112 | 20.5065 | 20.0884 |  | 20.2447 | 19.8905 | 20.1438 | 19.7996 | 20.1211 | 20.38 |  | 20.4755 |  |  | 20.2617 | 20.3521 | 20.6035 | [5 empty] | 21.96 | 20.376 | 21.7106 | 22.1062 | 19.5947 | 21.2562 | 21.9019 | 19.4129 | 19.9871 | 21.19 |  | 19.6347 | 20.9933 | 18.8786 | 19.7321 | 20.8691 | 19.4146 | 20.1728 | 19.0842 | 20.2106 | 19.2423 | 20.3695 | 18.7655 | 20.0969 | 21.128 | 19.4629 | 19.8199 | 21.0512 | 18.9515 | 19.8491 | 20.8691 | 18.9949 | 20.2591 | 19.3639 | 20.0018 | 19.0045 | 20.2261 | -0.18471 | 20.9461 | 0.046822 | 0.014665 | -27.0562 | 3.0933 | -1.06 | -0.23 | 0.71366 | -0.64947 | -7.0014 | 0.72154 | 0.71052 | -16.713 | 5.2694 | 0.42448 | 0.4266 | 0.42836 | 0.38445 | 0.44153 | 0.43837 | 0.42919
42838.4116 | -748 | 22.9014 | 22.8762 | 22.8729 | 22.8064 | 22.4481 | 21.8088 | 22.7491 | 21.8713 | 22.3992 | 22.416 | 22.3978 | 22.0927 | 21.3216 | 22.2776 | 21.5874 | 21.7658 | 21.9147 | 21.0911 | 21.1898 | 21.423 | 20.4966 | 20.6419 | 20.9457 | 21.9204 | 21.6958 | 21.3312 | 20.4657 | 20.5545 | 20.547 | 22.0482 | 21.6662 | 21.1925 | 22.0079 | 21.7533 | 21.3737 | 19.9557 | 20.5995 |  | 20.5925 | 20.2789 | 20.339 | 19.2411 |  | 16.5933 | 16.627 | 16.4139 | 16.6999 | 16.8739 | 17.549 | 18.2075 | 15.9324 | 16.5986 | 16.6534 | 16.791 | 17.8658 | 44.3012 | 47.1493 | 43.3613 | 21.3197 |  |  | 0.38596 | -0.12689 | -34.661 | 0.30551 | 0.30766 | -197.8716 | 19.5192 | -0.30789 | -0.10013 | 0.047736 | -0.12383 | 8.8286 | 9.0584 | 1.9784 | 21.8077 | 22.0433 | 22.2338 | 22.3099 | 22.1487 | 21.4995 | 20.3329 | 22.2246 | 22.4011 | 22.428 | 22.3981 | 22.03 | 21.2821 | 22.2944 | 17.2551 | 17.079 | 16.3073 | 16.2885 | 16.2401 | 17.0579 | 16.6774 | 22.384 | 22.1604 | 21.7349 | 22.1024 | 21.8273 | 21.3368 | 21.9691 | 21.5675 | 20.9481 | 20.1489 | 20.4463 | 20.0368 | 19.8072 | -0.13309 | -0.1158 | 20.7369 | 22.0891 | 22.4004 | 20.1238 | 21.7123 | 22.1553 | 21.9832 | 21.7531 | 21.3222 | 21.8383 | 21.5029 | 21.1091 | 20.5604 | 20.5418 | 20.5131 | 20.5114 | 20.0798 |  | 20.2467 | 19.9002 | 20.1417 | 19.7967 | 20.1169 | 20.374 |  | 20.4684 |  |  | 20.2632 | 20.3554 | 20.6104 | [5 empty] | 21.9762 | 20.3828 | 21.7152 | 22.1127 | 19.5943 | 21.2656 | 21.9099 | 19.4173 | 19.9811 | 21.1804 |  | 19.6225 | 20.9974 | 18.8615 | 19.7262 | 20.8741 | 19.4195 | 20.1729 | 19.0779 | 20.206 | 19.2455 | 20.3721 | 18.7726 | 20.1026 | 21.1257 | 19.4579 | 19.8233 | 21.0426 | 18.9583 | 19.848 | 20.8732 | 18.9942 | 20.2608 | 19.3602 | 20.0047 | 19.0032 | 20.2218 | -0.20233 | 20.9451 | 0.046957 | 0.015544 | -27.0281 | 3.0939 | -0.91 | 0.45 | 0.74197 | -0.42258 | -6.9842 | 0.65571 | 0.65906 | -16.714 | 5.2495 | 0.42479 | 0.42626 | 0.4283 | 0.38027 | 0.4412 | 0.43834 | 0.42908
42838.4116 | -747 | 22.8981 | 22.8718 | 22.8676 | 22.8071 | 22.4491 | 21.8067 | 22.7427 | 21.8629 | 22.3996 | 22.4051 | 22.4068 | 22.0898 | 21.3192 | 22.2648 | 21.5716 | 21.7506 | 21.8984 | 21.0875 | 21.1864 | 21.4078 | 20.4878 | 20.6312 | 20.9339 | 21.9142 | 21.684 | 21.3168 | 20.4589 | 20.5443 | 20.5388 | 22.0427 | 21.6605 | 21.1929 | 22.006 | 21.751 | 21.3683 | 19.9446 | 20.5955 |  | 20.588 | 20.2739 | 20.3459 | 19.2331 |  | 16.5968 | 16.6417 | 16.4232 | 16.7231 | 16.9057 | 17.5689 | 18.2217 | 15.9711 | 16.6048 | 16.6075 | 16.7981 | 17.8723 | 44.3418 | 47.1546 | 43.3657 | 21.3236 |  |  | 0.3991 | -0.19588 | -36.0344 | 0.46717 | 0.2137 | -197.8493 | 18.9876 | -0.37163 | -0.52513 | -0.0061828 | 0.0082768 | 8.8289 | 9.0587 | 1.9782 | 21.81 | 22.0398 | 22.2337 | 22.3098 | 22.1528 | 21.4985 | 20.3297 | 22.2275 | 22.4022 | 22.4313 | 22.3885 | 22.037 | 21.2795 | 22.3021 | 17.2851 | 17.0321 | 16.2951 | 16.2708 | 16.2296 | 17.054 | 16.6783 | 22.3796 | 22.161 | 21.7338 | 22.0972 | 21.8278 | 21.3398 | 21.9727 | 21.5654 | 20.9501 | 20.1482 | 20.4378 | 20.0305 | 19.7909 | -0.093569 | -0.041052 | 20.7357 | 22.0928 | 22.4047 | 20.1289 | 21.7067 | 22.1579 | 21.9861 | 21.7515 | 21.3298 | 21.8252 | 21.4999 | 21.1083 | 20.5578 | 20.5492 | 20.5079 | 20.5055 | 20.0812 |  | 20.2417 | 19.9083 | 20.1336 | 19.7981 | 20.1122 | 20.3695 |  | 20.4717 |  |  | 20.2628 | 20.3605 | 20.613 | [5 empty] | 21.9683 | 20.3757 | 21.71 | 22.1175 | 19.5876 | 21.2544 | 21.8936 | 19.4155 | 19.9794 | 21.1835 |  | 19.6326 | 21.0066 | 18.8688 | 19.7308 | 20.8724 | 19.4214 | 20.178 | 19.0827 | 20.2077 | 19.2436 | 20.3686 | 18.7626 | 20.1029 | 21.1281 | 19.4571 | 19.8086 | 21.0499 | 18.9528 | 19.8488 | 20.8756 | 18.9912 | 20.258 | 19.3617 | 19.9927 | 19.003 | 20.2207 | -0.14556 | 20.9467 | 0.047221 | 0.017134 | -27.0983 | 3.0952 | -1.08 | -0.12 | 0.75448 | -0.52506 | -7.1215 | 0.81086 | 0.54929 | -16.7136 | 5.1777 | 0.42458 | 0.42576 | 0.4281 | 0.37648 | 0.44266 | 0.43819 | 0.42951
42838.4116 | -746 | 22.9055 | 22.8835 | 22.8673 | 22.8085 | 22.4539 | 21.8071 | 22.7513 | 21.8653 | 22.4053 | 22.4107 | 22.3934 | 22.0917 | 21.3276 | 22.2768 | 21.5844 | 21.7598 | 21.909 | 21.0993 | 21.1955 | 21.42 | 20.5043 | 20.6417 | 20.9442 | 21.9215 | 21.6926 | 21.3348 | 20.4707 | 20.5595 | 20.5442 | 22.0493 | 21.6673 | 21.1964 | 22.0075 | 21.7555 | 21.3816 | 19.9487 | 20.5981 |  | 20.5907 | 20.2801 | 20.3418 | 19.2276 |  | 16.5974 | 16.639 | 16.4295 | 16.7481 | 16.9321 | 17.5919 | 18.2442 | 15.9803 | 16.6031 | 16.5652 | 16.8009 | 17.8656 | 44.3629 | 47.1522 | 43.3656 | 21.3194 |  |  | 0.56667 | -0.23991 | -36.7415 | 0.47111 | 0.13878 | -197.8112 | 18.6387 | -0.39069 | -0.13807 | 0.0040974 | 0.050635 | 8.829 | 9.0588 | 1.978 | 21.8095 | 22.0425 | 22.24 | 22.3122 | 22.1484 | 21.4998 | 20.3291 | 22.2274 | 22.4106 | 22.4326 | 22.3918 | 22.0374 | 21.2822 | 22.3031 | 17.3088 | 17.0214 | 16.3031 | 16.2711 | 16.2192 | 17.0571 | 16.6827 | 22.3772 | 22.1558 | 21.7335 | 22.0963 | 21.8271 | 21.3394 | 21.9719 | 21.5652 | 20.9542 | 20.152 | 20.4318 | 20.024 | 19.8044 | -0.092783 | -0.041052 | 20.7421 | 22.0933 | 22.4086 | 20.1264 | 21.7086 | 22.1571 | 21.9803 | 21.7576 | 21.3245 | 21.8347 | 21.5127 | 21.1037 | 20.5585 | 20.5476 | 20.5129 | 20.5116 | 20.077 |  | 20.2329 | 19.913 | 20.1381 | 19.7876 | 20.1152 | 20.3622 |  | 20.4624 |  |  | 20.2642 | 20.3541 | 20.6036 | [5 empty] | 21.9625 | 20.3789 | 21.7039 | 22.1068 | 19.583 | 21.2545 | 21.8978 | 19.4142 | 19.9763 | 21.1822 |  | 19.629 | 20.9964 | 18.864 | 19.7351 | 20.8692 | 19.4262 | 20.169 | 19.0696 | 20.2124 | 19.244 | 20.3697 | 18.7551 | 20.0916 | 21.1206 | 19.465 | 19.8059 | 21.0462 | 18.9477 | 19.8545 | 20.8728 | 18.987 | 20.2528 | 19.3556 | 19.9952 | 18.9994 | 20.2268 | -0.1259 | 20.9461 | 0.047713 | 0.016625 | -27.0513 | 3.0961 | -1.17 | -0.15 | 0.89904 | -0.58108 | -7.1909 | 0.81427 | 0.44268 | -16.7127 | 5.1301 | 0.4244 | 0.42578 | 0.4285 | 0.3742 | 0.44229 | 0.43848 | 0.42927
42838.4117 | -745 | 22.8984 | 22.8782 | 22.8645 | 22.7983 | 22.4419 | 21.8068 | 22.748 | 21.8688 | 22.3977 | 22.4119 | 22.3988 | 22.0884 | 21.3137 | 22.2689 | 21.5933 | 21.7712 | 21.912 | 21.1051 | 21.2053 | 21.435 | 20.5071 | 20.6527 | 20.9488 | 21.9262 | 21.7007 | 21.3291 | 20.4747 | 20.5687 | 20.548 | 22.0553 | 21.6692 | 21.1988 | 22.0133 | 21.7482 | 21.3829 | 19.9587 | 20.6048 |  | 20.6016 | 20.2823 | 20.3589 | 19.2125 |  | 16.5918 | 16.6379 | 16.4217 | 16.7592 | 16.9318 | 17.5683 | 18.2385 | 15.9673 | 16.594 | 16.5091 | 16.7942 | 17.8654 | 44.3686 | 47.1488 | 43.3648 | 21.321 |  |  | 0.25979 | -0.23794 | -36.8637 | 0.49477 | 0.15718 | -197.8033 | 18.4724 | -0.34929 | -0.1912 | -0.10227 | -0.074183 | 8.8289 | 9.0586 | 1.9789 | 21.8154 | 22.0447 | 22.246 | 22.3119 | 22.1552 | 21.4995 | 20.3372 | 22.2307 | 22.4063 | 22.4268 | 22.391 | 22.0383 | 21.2813 | 22.308 | 17.3294 | 17.0574 | 16.3021 | 16.2563 | 16.2225 | 17.054 | 16.69 | 22.3861 | 22.1587 | 21.7358 | 22.1016 | 21.8312 | 21.3439 | 21.9753 | 21.5677 | 20.9489 | 20.1569 | 20.4329 | 20.0185 | 19.8119 | -0.1091 | -0.14699 | 20.7505 | 22.0928 | 22.4159 | 20.129 | 21.7215 | 22.1633 | 21.983 | 21.7523 | 21.3354 | 21.8375 | 21.5032 | 21.1076 | 20.5656 | 20.5461 | 20.5069 | 20.5093 | 20.0818 |  | 20.239 | 19.9252 | 20.1392 | 19.7824 | 20.1144 | 20.3644 |  | 20.4671 |  |  | 20.2677 | 20.3578 | 20.6043 | [5 empty] | 21.9617 | 20.3823 | 21.7175 | 22.1125 | 19.5881 | 21.2595 | 21.8984 | 19.4135 | 19.974 | 21.1824 |  | 19.6246 | 20.9935 | 18.8535 | 19.7233 | 20.8641 | 19.4125 | 20.159 | 19.0727 | 20.2133 | 19.2387 | 20.3696 | 18.7538 | 20.0896 | 21.125 | 19.4674 | 19.8079 | 21.0478 | 18.9484 | 19.8498 | 20.8805 | 18.9975 | 20.2545 | 19.3509 | 19.9871 | 18.9921 | 20.2249 | -0.1682 | 20.9448 | 0.048481 | 0.017555 | -26.8667 | 3.0965 | -1.11 | -0.18 | 0.60874 | -0.57868 | -7.2029 | 0.83446 | 0.47109 | -16.7117 | 5.107 | 0.42447 | 0.42548 | 0.42861 | 0.37156 | 0.44324 | 0.43923 | 0.42922
42838.4117 | -744 | 22.899 | 22.8747 | 22.8613 | 22.7971 | 22.4455 | 21.8035 | 22.7494 | 21.8732 | 22.3987 | 22.4136 | 22.4056 | 22.0917 | 21.314 | 22.2705 | 21.59 | 21.7767 | 21.9102 | 21.1058 | 21.2029 | 21.4263 | 20.504 | 20.6541 | 20.9563 | 21.9293 | 21.6913 | 21.3364 | 20.4673 | 20.568 | 20.5444 | 22.0459 | 21.6617 | 21.1898 | 22.0099 | 21.7501 | 21.3707 | 19.9528 | 20.5993 |  | 20.5953 | 20.272 | 20.3465 | 19.2066 |  | 16.6098 | 16.6518 | 16.4367 | 16.7731 | 16.9334 | 17.5597 | 18.2209 | 15.9876 | 16.6056 | 16.4928 | 16.8061 | 17.8671 | 44.3586 | 47.1461 | 43.3849 | 21.3231 |  |  | 0.47138 | -0.12492 | -37.0694 | 0.4146 | 0.16507 | -197.8506 | 18.4757 | -0.40843 | -0.39125 | 0.0040974 | 0.025463 | 8.8286 | 9.0581 | 1.9782 | 21.8127 | 22.0377 | 22.2413 | 22.3048 | 22.1552 | 21.4931 | 20.3274 | 22.2266 | 22.3989 | 22.4358 | 22.3898 | 22.0337 | 21.2806 | 22.3034 | 17.3289 | 17.0813 | 16.3097 | 16.2509 | 16.2098 | 17.0519 | 16.6747 | 22.3822 | 22.1622 | 21.7336 | 22.1006 | 21.8285 | 21.3388 | 21.9742 | 21.5646 | 20.9485 | 20.1514 | 20.4254 | 20.0187 | 19.8092 | 0.021245 | -0.21528 | 20.7488 | 22.0963 | 22.41 | 20.1223 | 21.7153 | 22.1631 | 21.9739 | 21.7482 | 21.3266 | 21.8364 | 21.5102 | 21.1134 | 20.5609 | 20.5489 | 20.5055 | 20.5015 | 20.0792 |  | 20.2378 | 19.9363 | 20.1412 | 19.7898 | 20.1119 | 20.3668 |  | 20.4658 |  |  | 20.2624 | 20.3698 | 20.6146 | [5 empty] | 21.9668 | 20.3778 | 21.7222 | 22.1164 | 19.5932 | 21.257 | 21.9101 | 19.4177 | 19.9721 | 21.1787 |  | 19.6202 | 20.9953 | 18.856 | 19.7324 | 20.8663 | 19.4203 | 20.1663 | 19.0639 | 20.209 | 19.2357 | 20.3662 | 18.7445 | 20.0906 | 21.1215 | 19.4664 | 19.807 | 21.0513 | 18.9408 | 19.8517 | 20.8761 | 18.9965 | 20.2553 | 19.349 | 19.9802 | 18.9932 | 20.2203 | -0.18155 | 20.9469 | 0.048118 | 0.016821 | -26.9704 | 3.0967 | -1.3 | -0.08 | 0.81998 | -0.4193 | -7.2231 | 0.76389 | 0.48276 | -16.7134 | 5.1074 | 0.4245 | 0.42524 | 0.42833 | 0.37137 | 0.44062 | 0.4392 | 0.42911
42838.4117 | -743 | 22.8971 | 22.8728 | 22.8607 | 22.7942 | 22.4429 | 21.7946 | 22.7457 | 21.8638 | 22.3903 | 22.4121 | 22.4015 | 22.0856 | 21.3114 | 22.2637 | 21.5869 | 21.7669 | 21.9088 | 21.0978 | 21.1998 | 21.4203 | 20.5075 | 20.6535 | 20.9484 | 21.9238 | 21.6894 | 21.3273 | 20.4572 | 20.5561 | 20.5302 | 22.0473 | 21.6574 | 21.1897 | 22.0097 | 21.7535 | 21.3667 | 19.947 | 20.5942 |  | 20.5887 | 20.2716 | 20.3426 | 19.1994 |  | 16.604 | 16.6504 | 16.4304 | 16.7531 | 16.918 | 17.5319 | 18.1854 | 16.0222 | 16.5967 | 16.4404 | 16.792 | 17.8678 | 44.3497 | 47.1415 | 43.3958 | 21.3188 |  |  | 0.49767 | -0.33388 | -37.99 | 0.24835 | 0.22158 | -197.8736 | 18.0795 | -0.43143 | -0.24063 | -0.027582 | -0.017416 | 8.8279 | 9.0576 | 1.9779 | 21.8247 | 22.0441 | 22.2497 | 22.3132 | 22.1588 | 21.498 | 20.33 | 22.2346 | 22.4109 | 22.4439 | 22.3979 | 22.0379 | 21.2829 | 22.3076 | 17.3348 | 17.1254 | 16.3222 | 16.2512 | 16.2039 | 17.0602 | 16.6917 | 22.3788 | 22.1685 | 21.735 | 22.1028 | 21.8315 | 21.3379 | 21.9744 | 21.5641 | 20.9508 | 20.1569 | 20.416 | 20.0122 | 19.8055 | -0.01316 | -0.08689 | 20.7409 | 22.089 | 22.398 | 20.1144 | 21.7082 | 22.1526 | 21.9657 | 21.7441 | 21.3205 | 21.8241 | 21.5072 | 21.0983 | 20.5588 | 20.5373 | 20.4929 | 20.4953 | 20.0811 |  | 20.2336 | 19.9468 | 20.1367 | 19.7943 | 20.1185 | 20.3662 |  | 20.4618 |  |  | 20.2555 | 20.3655 | 20.6078 | [5 empty] | 21.9675 | 20.3782 | 21.7096 | 22.1127 | 19.5914 | 21.2595 | 21.9068 | 19.4032 | 19.9705 | 21.1778 |  | 19.6177 | 20.9891 | 18.8536 | 19.7326 | 20.858 | 19.4218 | 20.1575 | 19.0575 | 20.2046 | 19.2247 | 20.3596 | 18.7431 | 20.0931 | 21.1272 | 19.4678 | 19.8099 | 21.0469 | 18.9343 | 19.8572 | 20.8769 | 18.9998 | 20.2549 | 19.3528 | 19.9861 | 18.9898 | 20.219 | 0.008586 | 20.9466 | 0.046963 | 0.015972 | -26.9493 | 3.0967 | -1.26 | 0.3 | 0.84251 | -0.68551 | -7.3122 | 0.59121 | 0.5593 | -16.7136 | 5.0521 | 0.42431 | 0.4248 | 0.42842 | 0.37168 | 0.4412 | 0.4392 | 0.4294
42838.4117 | -742 | 22.9052 | 22.8713 | 22.8643 | 22.7969 | 22.4377 | 21.7922 | 22.7541 | 21.8668 | 22.3941 | 22.4101 | 22.3976 | 22.0857 | 21.3082 | 22.2656 | 21.5944 | 21.7735 | 21.9077 | 21.102 | 21.1953 | 21.4186 | 20.5043 | 20.6555 | 20.9506 | 21.9199 | 21.693 | 21.3257 | 20.4591 | 20.5592 | 20.5272 | 22.0493 | 21.654 | 21.1879 | 22.0082 | 21.7489 | 21.366 | 19.9464 | 20.5853 |  | 20.5879 | 20.2687 | 20.3495 | 19.1937 |  | 16.614 | 16.6675 | 16.435 | 16.7604 | 16.9067 | 17.5251 | 18.1642 | 16.0514 | 16.6078 | 16.4028 | 16.7939 | 17.8752 | 44.3456 | 47.1456 | 43.405 | 21.3302 |  |  | 0.35901 | -0.33322 | -38.8219 | 0.39817 | 0.3162 | -197.8473 | 18.0887 | -0.45246 | -0.19431 | -0.13479 | -0.15022 | 8.8288 | 9.0584 | 1.9776 | 21.815 | 22.0403 | 22.2352 | 22.3152 | 22.1424 | 21.5001 | 20.3264 | 22.2272 | 22.3957 | 22.4328 | 22.3837 | 22.0276 | 21.273 | 22.3035 | 17.2987 | 17.1402 | 16.322 | 16.2491 | 16.2168 | 17.0541 | 16.6858 | 22.3851 | 22.1724 | 21.732 | 22.0964 | 21.8335 | 21.3424 | 21.9692 | 21.5644 | 20.956 | 20.1437 | 20.4153 | 20.0045 | 19.8014 | -0.010604 | -0.10135 | 20.7436 | 22.0902 | 22.4015 | 20.1206 | 21.7046 | 22.1532 | 21.9627 | 21.7394 | 21.3187 | 21.831 | 21.4975 | 21.1029 | 20.5625 | 20.5457 | 20.5053 | 20.4962 | 20.0778 |  | 20.2412 | 19.957 | 20.1341 | 19.7955 | 20.12 | 20.3658 |  | 20.4669 |  |  | 20.253 | 20.3677 | 20.6055 | [5 empty] | 21.971 | 20.3754 | 21.7073 | 22.1068 | 19.5809 | 21.2551 | 21.8972 | 19.4133 | 19.9815 | 21.186 |  | 19.6214 | 21.0009 | 18.8547 | 19.7405 | 20.8662 | 19.4266 | 20.1648 | 19.0526 | 20.2118 | 19.2278 | 20.3611 | 18.7333 | 20.1001 | 21.1297 | 19.4663 | 19.8134 | 21.0514 | 18.9408 | 19.8595 | 20.8826 | 19.0012 | 20.2619 | 19.354 | 19.9828 | 18.9887 | 20.2229 | -0.051887 | 20.9455 | 0.047049 | 0.014302 | -27.0512 | 3.0967 | -1.07 | 0.32 | 0.71558 | -0.68485 | -7.3921 | 0.74862 | 0.66812 | -16.7123 | 5.0533 | 0.42466 | 0.42443 | 0.42844 | 0.37497 | 0.44054 | 0.43934 | 0.42907
42838.4117 | -741 | 22.896 | 22.864 | 22.8604 | 22.7963 | 22.4385 | 21.7853 | 22.7483 | 21.8612 | 22.3947 | 22.4038 | 22.3927 | 22.0807 | 21.3053 | 22.2635 | 21.5971 | 21.7707 | 21.9081 | 21.0942 | 21.193 | 21.4173 | 20.4949 | 20.6505 | 20.9475 | 21.9173 | 21.6867 | 21.3297 | 20.4545 | 20.5581 | 20.5199 | 22.052 | 21.6668 | 21.198 | 22.0158 | 21.7551 | 21.3742 | 19.9551 | 20.589 |  | 20.5965 | 20.2725 | 20.3555 | 19.1811 |  | 16.6141 | 16.6622 | 16.4302 | 16.7555 | 16.9009 | 17.5086 | 18.1361 | 16.0347 | 16.5999 | 16.355 | 16.7947 | 17.8661 | 44.3244 | 47.1376 | 43.3956 | 21.3257 |  |  | 0.39319 | -0.31745 | -40.0796 | 0.40014 | 0.1815 | -197.8079 | 17.7634 | -0.32958 | -0.048946 | 0.10564 | -0.023839 | 8.8297 | 9.0598 | 1.9787 | 21.8047 | 22.0402 | 22.2373 | 22.312 | 22.1476 | 21.4919 | 20.3218 | 22.2205 | 22.3899 | 22.4315 | 22.3895 | 22.0378 | 21.2799 | 22.2981 | 17.2707 | 17.1217 | 16.3372 | 16.2642 | 16.2449 | 17.0516 | 16.6837 | 22.3964 | 22.1685 | 21.7382 | 22.1044 | 21.8349 | 21.3542 | 21.9686 | 21.5665 | 20.9477 | 20.1467 | 20.421 | 19.9974 | 19.7928 | -0.040291 | -0.23734 | 20.7528 | 22.0914 | 22.4033 | 20.1331 | 21.7067 | 22.163 | 21.9712 | 21.7464 | 21.326 | 21.8289 | 21.4994 | 21.1021 | 20.5569 | 20.5479 | 20.5065 | 20.5048 | 20.0806 |  | 20.2387 | 19.9633 | 20.1443 | 19.7939 | 20.1175 | 20.3671 |  | 20.4696 |  |  | 20.2612 | 20.3747 | 20.6111 | [5 empty] | 21.9724 | 20.3783 | 21.7156 | 22.1044 | 19.5744 | 21.2581 | 21.9012 | 19.4203 | 19.9823 | 21.1872 |  | 19.6254 | 21.003 | 18.8458 | 19.7391 | 20.8633 | 19.4309 | 20.1642 | 19.0444 | 20.2169 | 19.2276 | 20.3596 | 18.7138 | 20.1007 | 21.1318 | 19.4701 | 19.8108 | 21.0522 | 18.9361 | 19.8562 | 20.8825 | 19.0017 | 20.2549 | 19.3528 | 19.9852 | 18.9802 | 20.2156 | -0.24407 | 20.9467 | 0.04582 | 0.013591 | -27.0868 | 3.0968 | -0.86 | -0.15 | 0.74885 | -0.66844 | -7.5108 | 0.75046 | 0.50617 | -16.7102 | 5.0075 | 0.4245 | 0.42459 | 0.4284 | 0.37779 | 0.43861 | 0.43998 | 0.42941
42838.4117 | -740 | 22.8894 | 22.8642 | 22.8594 | 22.7906 | 22.4428 | 21.7905 | 22.7367 | 21.8573 | 22.3911 | 22.3998 | 22.3993 | 22.0796 | 21.3095 | 22.2583 | 21.5873 | 21.7685 | 21.9106 | 21.0943 | 21.19 | 21.4203 | 20.4937 | 20.6454 | 20.9444 | 21.9209 | 21.6828 | 21.3281 | 20.4478 | 20.5578 | 20.5098 | 22.0486 | 21.6652 | 21.194 | 22.0143 | 21.7477 | 21.3696 | 19.9534 | 20.5894 |  | 20.5911 | 20.2675 | 20.3511 | 19.1688 |  | 16.6158 | 16.6717 | 16.438 | 16.7505 | 16.9128 | 17.5119 | 18.136 | 16.0028 | 16.6068 | 16.3317 | 16.8034 | 17.8654 | 44.3203 | 47.1347 | 43.3943 | 21.3233 |  |  | 0.33273 | -0.11309 | -40.6368 | 0.15438 | 0.21961 | -197.867 | 17.3954 | -0.21787 | -0.16434 | 0.060743 | 0.037962 | 8.8295 | 9.0595 | 1.9784 | 21.8152 | 22.0468 | 22.2448 | 22.3124 | 22.1574 | 21.5028 | 20.3337 | 22.2339 | 22.3986 | 22.4335 | 22.3883 | 22.0377 | 21.2822 | 22.307 | 17.2584 | 17.1345 | 16.3688 | 16.3082 | 16.2694 | 17.0615 | 16.6971 | 22.3951 | 22.1691 | 21.7434 | 22.103 | 21.832 | 21.3519 | 21.9708 | 21.5659 | 20.9598 | 20.1522 | 20.4181 | 19.9884 | 19.7855 | -0.16533 | -0.071294 | 20.7704 | 22.103 | 22.4132 | 20.1372 | 21.719 | 22.1653 | 21.9911 | 21.7602 | 21.3345 | 21.839 | 21.5124 | 21.1157 | 20.5736 | 20.5604 | 20.5114 | 20.5154 | 20.0701 |  | 20.2326 | 19.9546 | 20.1415 | 19.7886 | 20.1161 | 20.368 |  | 20.468 |  |  | 20.2696 | 20.3807 | 20.6167 | [5 empty] | 21.9735 | 20.382 | 21.712 | 22.1103 | 19.5768 | 21.2603 | 21.9017 | 19.4161 | 19.9846 | 21.1898 |  | 19.6242 | 21.0055 | 18.8438 | 19.7336 | 20.8615 | 19.4356 | 20.1578 | 19.0366 | 20.2084 | 19.218 | 20.3597 | 18.7065 | 20.102 | 21.1288 | 19.4768 | 19.814 | 21.0543 | 18.9366 | 19.8553 | 20.8863 | 19.0019 | 20.2625 | 19.3584 | 19.9842 | 18.9806 | 20.2128 | -0.059307 | 20.9461 | 0.045009 | 0.013664 | -27.0687 | 3.0968 | -0.79 | 0.12 | 0.68887 | -0.39897 | -7.563 | 0.46615 | 0.55678 | -16.7127 | 4.9554 | 0.42458 | 0.42474 | 0.4285 | 0.38033 | 0.43667 | 0.44027 | 0.4298
42838.4117 | -739 | 22.894 | 22.8744 | 22.8647 | 22.7974 | 22.448 | 21.8008 | 22.7461 | 21.8717 | 22.4013 | 22.4073 | 22.398 | 22.088 | 21.3169 | 22.2712 | 21.5822 | 21.767 | 21.9042 | 21.0973 | 21.1905 | 21.4156 | 20.494 | 20.6457 | 20.942 | 21.922 | 21.6857 | 21.3269 | 20.4442 | 20.5593 | 20.5026 | 22.0506 | 21.673 | 21.1998 | 22.0112 | 21.7578 | 21.3732 | 19.9605 | 20.5995 |  | 20.6004 | 20.2749 | 20.3532 | 19.1646 |  | 16.6248 | 16.687 | 16.4388 | 16.7568 | 16.9288 | 17.5149 | 18.1448 | 15.986 | 16.6095 | 16.3302 | 16.8034 | 17.865 | 44.3036 | 47.1361 | 43.4001 | 21.3305 |  |  | 0.43918 | -0.42982 | -41.3676 | -0.083498 | 0.17164 | -197.8098 | 17.2745 | -0.30592 | -0.3823 | 0.11676 | -0.055782 | 8.829 | 9.0587 | 1.9778 | 21.82 | 22.0423 | 22.2421 | 22.3114 | 22.1541 | 21.5027 | 20.3321 | 22.2283 | 22.4032 | 22.435 | 22.3903 | 22.0366 | 21.2797 | 22.3038 | 17.2497 | 17.1386 | 16.364 | 16.3199 | 16.2839 | 17.0552 | 16.6832 | 22.3902 | 22.1663 | 21.7377 | 22.1035 | 21.8301 | 21.3513 | 21.9757 | 21.573 | 20.9561 | 20.1592 | 20.412 | 19.99 | 19.7804 | -0.02358 | -0.016136 | 20.7619 | 22.0987 | 22.4176 | 20.134 | 21.7154 | 22.1671 | 21.9872 | 21.7539 | 21.3333 | 21.8321 | 21.4959 | 21.107 | 20.5715 | 20.5494 | 20.5103 | 20.5069 | 20.0717 |  | 20.2461 | 19.9647 | 20.148 | 19.7909 | 20.1261 | 20.3851 |  | 20.4783 |  |  | 20.2631 | 20.3809 | 20.6125 | [5 empty] | 21.9679 | 20.3785 | 21.7055 | 22.112 | 19.5746 | 21.2538 | 21.9014 | 19.4115 | 19.9805 | 21.1892 |  | 19.6296 | 21.0002 | 18.8391 | 19.7332 | 20.862 | 19.4307 | 20.156 | 19.0262 | 20.2082 | 19.2159 | 20.3592 | 18.6966 | 20.1 | 21.1303 | 19.4737 | 19.8166 | 21.0513 | 18.9376 | 19.8502 | 20.8917 | 19.0038 | 20.266 | 19.3577 | 19.9808 | 18.9772 | 20.2137 | -0.23294 | 20.9471 | 0.04582 | 0.013431 | -27.0199 | 3.0968 | -1.29 | -0.09 | 0.79142 | -0.77784 | -7.6309 | -0.34283 | 0.49224 | -16.7104 | 4.9382 | 0.42499 | 0.42468 | 0.42877 | 0.38056 | 0.43556 | 0.44062 | 0.43017
42838.4117 | -738 | 22.8976 | 22.8708 | 22.8608 | 22.7899 | 22.4491 | 21.7959 | 22.7465 | 21.8603 | 22.401 | 22.4041 | 22.3912 | 22.0875 | 21.3167 | 22.2712 | 21.586 | 21.7676 | 21.9054 | 21.0964 | 21.1942 | 21.4221 | 20.4991 | 20.653 | 20.9464 | 21.9258 | 21.6879 | 21.3259 | 20.442 | 20.566 | 20.4947 | 22.063 | 21.6663 | 21.2024 | 22.016 | 21.7588 | 21.3769 | 19.9571 | 20.593 |  | 20.5985 | 20.2772 | 20.3493 | 19.1427 |  | 16.6249 | 16.6822 | 16.4416 | 16.7548 | 16.9437 | 17.5435 | 18.1239 | 16.0099 | 16.5976 | 16.3004 | 16.803 | 17.8728 | 44.2863 | 47.1412 | 43.4085 | 21.3338 |  |  | 0.38201 | -0.27605 | -41.5824 | 0.18789 | 0.25575 | -197.8532 | 17.1227 | -0.13507 | -0.075801 | -0.069123 | -0.18442 | 8.8287 | 9.0582 | 1.9774 | 21.8168 | 22.0418 | 22.2361 | 22.3075 | 22.1541 | 21.497 | 20.3238 | 22.2233 | 22.404 | 22.4331 | 22.3862 | 22.0333 | 21.283 | 22.3004 | 17.2662 | 17.1251 | 16.3915 | 16.3741 | 16.3107 | 17.0629 | 16.6923 | 22.3868 | 22.1633 | 21.738 | 22.1089 | 21.8293 | 21.3444 | 21.9764 | 21.571 | 20.9452 | 20.151 | 20.4057 | 19.9781 | 19.7867 | 0.015937 | -0.087461 | 20.7709 | 22.0971 | 22.4106 | 20.1346 | 21.7197 | 22.1647 | 21.9854 | 21.7512 | 21.3252 | 21.8379 | 21.5105 | 21.1114 | 20.5725 | 20.5438 | 20.5087 | 20.5039 | 20.0651 |  | 20.2337 | 19.9544 | 20.1261 | 19.7682 | 20.1106 | 20.3693 |  | 20.4637 |  |  | 20.2631 | 20.3868 | 20.6073 | [5 empty] | 21.9654 | 20.3748 | 21.7085 | 22.1055 | 19.5721 | 21.247 | 21.9042 | 19.4076 | 19.9791 | 21.1796 |  | 19.626 | 20.9963 | 18.832 | 19.7212 | 20.8543 | 19.4239 | 20.154 | 19.0207 | 20.2076 | 19.2114 | 20.3493 | 18.6845 | 20.1005 | 21.1256 | 19.473 | 19.8128 | 21.0499 | 18.934 | 19.8558 | 20.885 | 19.0009 | 20.2609 | 19.3535 | 19.982 | 18.9713 | 20.2046 | -0.044652 | 20.9471 | 0.046459 | 0.014389 | -26.9871 | 3.0968 | -1.33 | -0.08 | 0.7381 | -0.62336 | -7.6506 | 0.51427 | 0.60088 | -16.7131 | 4.9167 | 0.42476 | 0.42423 | 0.42888 | 0.37963 | 0.43358 | 0.44111 | 0.42972
42838.4117 | -737 | 22.8969 | 22.8685 | 22.8648 | 22.7923 | 22.4413 | 21.7948 | 22.735 | 21.8529 | 22.3919 | 22.4048 | 22.3956 | 22.082 | 21.3078 | 22.269 | 21.5895 | 21.7639 | 21.9109 | 21.1022 | 21.1986 | 21.4182 | 20.4995 | 20.6497 | 20.942 | 21.9199 | 21.6849 | 21.3226 | 20.445 | 20.5648 | 20.4886 | 22.0487 | 21.6693 | 21.2011 | 22.0131 | 21.7596 | 21.3792 | 19.955 | 20.5894 |  | 20.599 | 20.2747 | 20.3557 | 19.1312 |  | 16.6315 | 16.6932 | 16.451 | 16.7571 | 16.9782 | 17.5836 | 18.1122 | 16.0078 | 16.6044 | 16.2998 | 16.8119 | 17.8693 | 44.2718 | 47.1339 | 43.4084 | 21.3342 |  |  | 0.38136 | -0.31351 | -42.2185 | 0.18066 | 0.20318 | -197.8407 | 17.0682 | -0.17121 | -0.18731 | 0.12221 | -0.19188 | 8.8286 | 9.0581 | 1.9786 | 21.8132 | 22.0472 | 22.2414 | 22.3045 | 22.1437 | 21.4983 | 20.3186 | 22.2256 | 22.4061 | 22.4323 | 22.3872 | 22.0273 | 21.2768 | 22.2979 | 17.2775 | 17.0991 | 16.3945 | 16.363 | 16.3018 | 17.0651 | 16.6873 | 22.3804 | 22.1528 | 21.7264 | 22.0977 | 21.8185 | 21.3341 | 21.9677 | 21.5604 | 20.9438 | 20.1389 | 20.3908 | 19.9653 | 19.7597 | -0.0041164 | -0.11941 | 20.7806 | 22.1008 | 22.4098 | 20.1374 | 21.7172 | 22.1656 | 21.9798 | 21.7494 | 21.325 | 21.8364 | 21.5058 | 21.1066 | 20.5661 | 20.5519 | 20.5137 | 20.508 | 20.083 |  | 20.2333 | 19.9497 | 20.1306 | 19.7667 | 20.1082 | 20.3673 |  | 20.464 |  |  | 20.2582 | 20.391 | 20.6064 | [5 empty] | 21.966 | 20.379 | 21.7178 | 22.1081 | 19.5756 | 21.2508 | 21.8995 | 19.4105 | 19.9851 | 21.1802 |  | 19.6296 | 20.9993 | 18.8366 | 19.7303 | 20.8577 | 19.4269 | 20.1572 | 19.0305 | 20.2106 | 19.2104 | 20.3517 | 18.6861 | 20.1032 | 21.133 | 19.4799 | 19.8181 | 21.0511 | 18.935 | 19.868 | 20.8908 | 19.0061 | 20.2634 | 19.3557 | 19.979 | 18.972 | 20.2129 | -0.099004 | 20.9479 | 0.047559 | 0.016233 | -26.9937 | 3.0969 | -1.28 | 0.13 | 0.73746 | -0.66431 | -7.709 | 0.50429 | 0.53562 | -16.7137 | 4.9092 | 0.42425 | 0.42451 | 0.42884 | 0.37863 | 0.43267 | 0.44137 | 0.43007
42838.4118 | -736 | 22.8907 | 22.8665 | 22.8594 | 22.7935 | 22.4392 | 21.7957 | 22.7417 | 21.8579 | 22.3915 | 22.4055 | 22.3935 | 22.0847 | 21.3096 | 22.2644 | 21.59 | 21.7617 | 21.9148 | 21.0999 | 21.201 | 21.4199 | 20.5072 | 20.6582 | 20.9482 | 21.9242 | 21.6904 | 21.3249 | 20.4397 | 20.5686 | 20.4886 | 22.0412 | 21.6603 | 21.1884 | 22.0115 | 21.7448 | 21.3713 | 19.95 | 20.5782 |  | 20.5899 | 20.269 | 20.3486 | 19.1147 |  | 16.6298 | 16.6884 | 16.4429 | 16.7611 | 16.9923 | 17.6162 | 18.1064 | 15.9873 | 16.5976 | 16.3193 | 16.8135 | 17.8728 | 44.2668 | 47.1349 | 43.3968 | 21.3331 |  |  | 0.3577 | -0.30825 | -42.572 | 0.25426 | 0.23932 | -197.8532 | 16.668 | -0.28752 | -0.015475 | 0.19418 | -0.033561 | 8.8292 | 9.0589 | 1.9786 | 21.8198 | 22.0505 | 22.2477 | 22.3114 | 22.1523 | 21.4959 | 20.3305 | 22.224 | 22.405 | 22.4291 | 22.3913 | 22.0306 | 21.2776 | 22.307 | 17.2875 | 17.1088 | 16.4024 | 16.3571 | 16.2859 | 17.0599 | 16.6922 | 22.3871 | 22.1656 | 21.7329 | 22.1 | 21.8265 | 21.3409 | 21.966 | 21.5637 | 20.9492 | 20.1482 | 20.3942 | 19.9773 | 19.7634 | 0.0354 | -0.14509 | 20.7642 | 22.0907 | 22.3994 | 20.1302 | 21.7042 | 22.1669 | 21.9723 | 21.7444 | 21.3253 | 21.8318 | 21.4973 | 21.1041 | 20.5564 | 20.5489 | 20.4928 | 20.4981 | 20.1122 |  | 20.246 | 19.9509 | 20.1391 | 19.7793 | 20.12 | 20.377 |  | 20.4636 |  |  | 20.2561 | 20.3975 | 20.6111 | [5 empty] | 21.9684 | 20.384 | 21.7174 | 22.1132 | 19.5783 | 21.2549 | 21.9034 | 19.4147 | 19.9855 | 21.1917 |  | 19.6358 | 20.9997 | 18.848 | 19.74 | 20.8717 | 19.4411 | 20.1624 | 19.0454 | 20.215 | 19.2183 | 20.3665 | 18.6797 | 20.1033 | 21.1238 | 19.4701 | 19.8213 | 21.045 | 18.9374 | 19.8622 | 20.8878 | 19.0084 | 20.2629 | 19.3479 | 19.9768 | 18.9653 | 20.2119 | -0.1413 | 20.9512 | 0.047289 | 0.016618 | -27.1323 | 3.0968 | -0.89 | 0.03 | 0.71422 | -0.65872 | -7.7412 | 0.59825 | 0.58134 | -16.7152 | 4.8516 | 0.42386 | 0.42476 | 0.42889 | 0.3769 | 0.43236 | 0.44166 | 0.43028
42838.4118 | -735 | 22.896 | 22.8735 | 22.8623 | 22.8027 | 22.4475 | 21.7971 | 22.7436 | 21.8627 | 22.3987 | 22.406 | 22.3966 | 22.086 | 21.3092 | 22.2693 | 21.5945 | 21.7708 | 21.9146 | 21.1061 | 21.2004 | 21.4147 | 20.4965 | 20.6504 | 20.9462 | 21.916 | 21.6877 | 21.3275 | 20.4451 | 20.5692 | 20.4903 | 22.0485 | 21.6638 | 21.1912 | 22.0136 | 21.7596 | 21.3746 | 19.958 | 20.5865 |  | 20.5965 | 20.277 | 20.3628 | 19.1086 |  | 16.6348 | 16.6902 | 16.45 | 16.7747 | 17.0071 | 17.6469 | 18.144 | 15.9857 | 16.607 | 16.3102 | 16.8098 | 17.8639 | 44.2591 | 47.1442 | 43.4044 | 21.3309 |  |  | 0.58572 | -0.68872 | -43.078 | 0.13401 | 0.17821 | -197.8893 | 16.6759 | -0.33023 | -0.20151 | 0.0019994 | -0.0089096 | 8.8284 | 9.0584 | 1.9782 | 21.8169 | 22.0484 | 22.2492 | 22.3076 | 22.1517 | 21.4946 | 20.3234 | 22.2303 | 22.403 | 22.4313 | 22.3873 | 22.0344 | 21.274 | 22.2954 | 17.2779 | 17.1239 | 16.4028 | 16.3562 | 16.2869 | 17.0624 | 16.6935 | 22.3852 | 22.1602 | 21.7323 | 22.0945 | 21.8269 | 21.3371 | 21.9657 | 21.5594 | 20.9491 | 20.1414 | 20.3948 | 19.9712 | 19.7518 | 0.032255 | -0.057409 | 20.7649 | 22.0909 | 22.4153 | 20.1413 | 21.7014 | 22.162 | 21.9697 | 21.7493 | 21.3228 | 21.8235 | 21.5016 | 21.0978 | 20.5627 | 20.5436 | 20.5009 | 20.4926 | 20.1159 |  | 20.2371 | 19.9315 | 20.1324 | 19.7729 | 20.1137 | 20.3676 |  | 20.4677 |  |  | 20.2611 | 20.3856 | 20.5983 | [5 empty] | 21.963 | 20.3676 | 21.7153 | 22.1076 | 19.5662 | 21.2489 | 21.8949 | 19.4036 | 19.984 | 21.1982 |  | 19.6439 | 21.0115 | 18.8447 | 19.7343 | 20.8677 | 19.4413 | 20.1632 | 19.0438 | 20.2078 | 19.217 | 20.3559 | 18.664 | 20.0981 | 21.1148 | 19.4598 | 19.8083 | 21.0379 | 18.9276 | 19.8519 | 20.8867 | 19.0067 | 20.2506 | 19.3473 | 19.9755 | 18.9594 | 20.2067 | -0.039087 | 20.9478 | 0.047375 | 0.015609 | -26.9883 | 3.0969 | -1.01 | 0.32 | 0.91395 | -0.98462 | -7.7871 | 0.43432 | 0.50168 | -16.7176 | 4.853 | 0.42346 | 0.42508 | 0.42885 | 0.37826 | 0.43246 | 0.44209 | 0.43037
42838.4118 | -734 | 22.9013 | 22.8698 | 22.8664 | 22.7986 | 22.4444 | 21.7926 | 22.74 | 21.8627 | 22.3971 | 22.4102 | 22.3966 | 22.0891 | 21.3103 | 22.2725 | 21.6009 | 21.7759 | 21.9197 | 21.1005 | 21.193 | 21.4236 | 20.5125 | 20.6591 | 20.9496 | 21.9327 | 21.6931 | 21.3317 | 20.4463 | 20.5686 | 20.4854 | 22.0464 | 21.6682 | 21.1869 | 22.014 | 21.7582 | 21.3758 | 19.9577 | 20.5847 |  | 20.5997 | 20.2772 | 20.362 | 19.0948 |  | 16.6486 | 16.6899 | 16.4489 | 16.7848 | 17.0206 | 17.6743 | 18.1762 | 15.973 | 16.6133 | 16.3003 | 16.814 | 17.8772 | 44.2701 | 47.1492 | 43.4126 | 21.3308 |  |  | 0.28147 | -1.0672 | -43.925 | -0.031586 | 0.042188 | -197.8164 | 16.3513 | -0.23561 | -0.23168 | 0.12368 | -0.042067 | 8.8282 | 9.0581 | 1.9777 | 21.8133 | 22.0463 | 22.2498 | 22.3142 | 22.1446 | 21.5024 | 20.3296 | 22.2316 | 22.4062 | 22.4352 | 22.3924 | 22.038 | 21.2847 | 22.2998 | 17.2582 | 17.145 | 16.3834 | 16.3449 | 16.2753 | 17.0585 | 16.69 | 22.3942 | 22.1659 | 21.7392 | 22.1119 | 21.8341 | 21.3406 | 21.9711 | 21.5634 | 20.9473 | 20.1474 | 20.3951 | 19.9759 | 19.7532 | -0.0021504 | -0.10382 | 20.7718 | 22.0875 | 22.4053 | 20.1313 | 21.7028 | 22.1678 | 21.982 | 21.7511 | 21.3178 | 21.8363 | 21.5042 | 21.1064 | 20.5611 | 20.5346 | 20.5056 | 20.5008 | 20.1173 |  | 20.2396 | 19.9263 | 20.1394 | 19.7762 | 20.1257 | 20.3759 |  | 20.4726 |  |  | 20.2631 | 20.3951 | 20.5958 | [5 empty] | 21.961 | 20.3767 | 21.7097 | 22.1033 | 19.571 | 21.2548 | 21.8948 | 19.4089 | 19.9815 | 21.1807 |  | 19.6336 | 20.9995 | 18.8419 | 19.7164 | 20.8622 | 19.4342 | 20.1529 | 19.047 | 20.202 | 19.2031 | 20.357 | 18.671 | 20.1059 | 21.1227 | 19.4719 | 19.8132 | 21.0421 | 18.9347 | 19.855 | 20.886 | 19.0031 | 20.2603 | 19.3507 | 19.9699 | 18.9625 | 20.2037 | -0.14853 | 20.9458 | 0.047178 | 0.014535 | -26.9694 | 3.0969 | -1.22 | -0.13 | 0.63356 | -1.2257 | -7.8633 | -0.21086 | 0.24411 | -16.7153 | 4.8057 | 0.42351 | 0.42546 | 0.42916 | 0.38 | 0.4342 | 0.44247 | 0.43053
42838.4118 | -733 | 22.8972 | 22.873 | 22.8631 | 22.7978 | 22.4406 | 21.8 | 22.7493 | 21.8619 | 22.3933 | 22.4117 | 22.3984 | 22.0873 | 21.3106 | 22.2753 | 21.5892 | 21.7671 | 21.9091 | 21.0896 | 21.1966 | 21.411 | 20.5072 | 20.644 | 20.9431 | 21.9261 | 21.6916 | 21.3201 | 20.4417 | 20.564 | 20.4798 | 22.0514 | 21.6648 | 21.1929 | 22.0105 | 21.7532 | 21.3741 | 19.9539 | 20.5809 |  | 20.598 | 20.275 | 20.3562 | 19.0788 |  | 16.6357 | 16.6861 | 16.4473 | 16.7768 | 17.0385 | 17.7068 | 18.2004 | 15.9301 | 16.6049 | 16.3496 | 16.808 | 17.8681 | 44.2759 | 47.1534 | 43.4219 | 21.3283 |  |  | 0.32616 | -0.43311 | -44.4284 | 0.37714 | 0.23078 | -197.8361 | 16.2455 | -0.3 | -0.27137 | 0.077318 | -0.22574 | 8.8289 | 9.0586 | 1.9783 | 21.8189 | 22.0448 | 22.2447 | 22.3027 | 22.1459 | 21.4943 | 20.3176 | 22.2279 | 22.4005 | 22.4336 | 22.3926 | 22.0292 | 21.2679 | 22.3029 | 17.2482 | 17.1557 | 16.382 | 16.3487 | 16.2862 | 17.0629 | 16.6949 | 22.387 | 22.1623 | 21.7347 | 22.0986 | 21.8216 | 21.3362 | 21.9668 | 21.5608 | 20.9458 | 20.1491 | 20.3856 | 19.9681 | 19.7515 | 0.009449 | -0.063115 | 20.758 | 22.0943 | 22.4072 | 20.1288 | 21.7074 | 22.1634 | 21.963 | 21.7442 | 21.3207 | 21.8191 | 21.5029 | 21.1057 | 20.5464 | 20.5486 | 20.5066 | 20.494 | 20.1079 |  | 20.2506 | 19.9191 | 20.1427 | 19.7841 | 20.1254 | 20.3802 |  | 20.473 |  |  | 20.266 | 20.3952 | 20.6112 | [5 empty] | 21.9711 | 20.3709 | 21.7085 | 22.115 | 19.5827 | 21.2571 | 21.8976 | 19.4185 | 19.983 | 21.1878 |  | 19.6601 | 21.0041 | 18.8491 | 19.7299 | 20.8658 | 19.4416 | 20.165 | 19.0537 | 20.2142 | 19.2116 | 20.3564 | 18.6757 | 20.1035 | 21.1238 | 19.4608 | 19.8127 | 21.0469 | 18.9226 | 19.8524 | 20.8799 | 19.0137 | 20.2637 | 19.3434 | 19.973 | 18.9571 | 20.2067 | -0.021279 | 20.9477 | 0.047123 | 0.015188 | -26.9683 | 3.0968 | -1.01 | -0.11 | 0.68199 | -0.7808 | -7.9081 | 0.72861 | 0.57096 | -16.717 | 4.7904 | 0.42414 | 0.42576 | 0.42893 | 0.38161 | 0.43494 | 0.44278 | 0.43064
42838.4118 | -732 | 22.8955 | 22.8663 | 22.8602 | 22.7997 | 22.4458 | 21.7982 | 22.7387 | 21.8596 | 22.4001 | 22.4036 | 22.3918 | 22.0868 | 21.3077 | 22.275 | 21.5792 | 21.7667 | 21.9036 | 21.0963 | 21.1914 | 21.4138 | 20.499 | 20.6425 | 20.9405 | 21.9178 | 21.6912 | 21.3218 | 20.4308 | 20.567 | 20.4746 | 22.0516 | 21.6667 | 21.1936 | 22.0085 | 21.7431 | 21.3732 | 19.9493 | 20.5872 |  | 20.5956 | 20.2654 | 20.3626 | 19.0633 |  | 16.6331 | 16.6848 | 16.4438 | 16.7703 | 17.0385 | 17.7296 | 18.2237 | 15.911 | 16.6029 | 16.4238 | 16.8011 | 17.8684 | 44.2939 | 47.1643 | 43.4349 | 21.3291 |  |  | 0.3393 | -0.049349 | -43.9921 | 0.23257 | 0.39506 | -197.8368 | 15.9478 | -0.25532 | 0.053608 | 0.078157 | -0.10613 | 8.8284 | 9.0581 | 1.9788 | 21.8173 | 22.0377 | 22.2389 | 22.2974 | 22.1432 | 21.4896 | 20.3222 | 22.2279 | 22.3976 | 22.4247 | 22.3891 | 22.0274 | 21.2703 | 22.3035 | 17.2181 | 17.1621 | 16.3645 | 16.3434 | 16.2781 | 17.062 | 16.692 | 22.384 | 22.1581 | 21.7314 | 22.0896 | 21.8181 | 21.3361 | 21.964 | 21.5584 | 20.9455 | 20.1409 | 20.388 | 19.9616 | 19.7411 | 0.037956 | 0.12233 | 20.7606 | 22.0895 | 22.4107 | 20.131 | 21.7059 | 22.1486 | 21.9734 | 21.7492 | 21.3095 | 21.8234 | 21.5061 | 21.1013 | 20.5416 | 20.5573 | 20.5028 | 20.5024 | 20.1165 |  | 20.2461 | 19.9112 | 20.1403 | 19.7842 | 20.1256 | 20.384 |  | 20.4709 |  |  | 20.2723 | 20.395 | 20.6097 | [5 empty] | 21.9769 | 20.3708 | 21.7154 | 22.1111 | 19.5819 | 21.2583 | 21.9032 | 19.4095 | 19.9769 | 21.1797 |  | 19.6491 | 20.984 | 18.8346 | 19.7211 | 20.8548 | 19.4272 | 20.1463 | 19.0409 | 20.2124 | 19.2008 | 20.3598 | 18.6733 | 20.1001 | 21.1237 | 19.4618 | 19.8106 | 21.0379 | 18.9345 | 19.8567 | 20.8785 | 19.0097 | 20.2647 | 19.3406 | 19.9691 | 18.9628 | 20.1997 | -0.25928 | 20.943 | 0.048217 | 0.015769 | -27.1153 | 3.0969 | -1.3 | -0.4 | 0.69559 | -0.26356 | -7.8692 | 0.57217 | 0.74706 | -16.7177 | 4.7465 | 0.42374 | 0.4259 | 0.42894 | 0.38485 | 0.43654 | 0.44306 | 0.43065
42838.4118 | -731 | 22.9028 | 22.8649 | 22.8615 | 22.799 | 22.4486 | 21.7988 | 22.7435 | 21.8587 | 22.3941 | 22.4086 | 22.39 | 22.0862 | 21.3067 | 22.2678 | 21.5923 | 21.7725 | 21.9153 | 21.1006 | 21.199 | 21.4262 | 20.5096 | 20.6525 | 20.9457 | 21.9301 | 21.6875 | 21.3275 | 20.444 | 20.5756 | 20.4787 | 22.0582 | 21.66 | 21.195 | 22.0147 | 21.7575 | 21.3808 | 19.9566 | 20.5837 |  | 20.5969 | 20.2715 | 20.365 | 19.0424 |  | 16.6425 | 16.688 | 16.4477 | 16.77 | 17.0426 | 17.7511 | 18.2606 | 15.9129 | 16.5995 | 16.5052 | 16.8026 | 17.8668 | 44.3099 | 47.1724 | 43.4289 | 21.3306 |  |  | 0.39187 | -0.058549 | -43.7121 | 0.21417 | 0.46603 | -197.8289 | 16.373 | -0.38937 | 0.075404 | -0.090522 | -0.10786 | 8.8285 | 9.0581 | 1.9783 | 21.8166 | 22.0397 | 22.2397 | 22.3006 | 22.1479 | 21.4885 | 20.3247 | 22.2272 | 22.3982 | 22.4264 | 22.3806 | 22.0301 | 21.2779 | 22.2986 | 17.2089 | 17.165 | 16.3841 | 16.3466 | 16.2776 | 17.0668 | 16.6969 | 22.3873 | 22.1673 | 21.7361 | 22.1002 | 21.824 | 21.3412 | 21.975 | 21.5598 | 20.9468 | 20.1514 | 20.3947 | 19.962 | 19.7509 | 0.0004054 | 0.15181 | 20.7658 | 22.0878 | 22.4001 | 20.1283 | 21.7093 | 22.1624 | 21.9741 | 21.7415 | 21.3214 | 21.8323 | 21.4956 | 21.0947 | 20.5439 | 20.5629 | 20.5047 | 20.4906 | 20.1134 |  | 20.244 | 19.8968 | 20.1332 | 19.778 | 20.1201 | 20.3724 |  | 20.4604 |  |  | 20.2697 | 20.3956 | 20.6194 | [5 empty] | 21.9649 | 20.3738 | 21.7093 | 22.1088 | 19.58 | 21.2577 | 21.894 | 19.4044 | 19.9823 | 21.1868 |  | 19.6576 | 21.0023 | 18.8506 | 19.7188 | 20.8715 | 19.4426 | 20.1577 | 19.0519 | 20.2181 | 19.2025 | 20.3554 | 18.673 | 20.1113 | 21.119 | 19.4619 | 19.8082 | 21.0354 | 18.9306 | 19.8548 | 20.8819 | 19.0081 | 20.2696 | 19.3428 | 19.9771 | 18.9624 | 20.2016 | -0.05671 | 20.9452 | 0.047541 | 0.015899 | -27.0426 | 3.0969 | -1.15 | -0.1 | 0.74754 | -0.28708 | -7.8441 | 0.54907 | 0.81142 | -16.718 | 4.8095 | 0.42376 | 0.42607 | 0.42893 | 0.38644 | 0.43495 | 0.44389 | 0.43073
42838.4118 | -730 | 22.8875 | 22.8751 | 22.8633 | 22.7929 | 22.441 | 21.7987 | 22.7442 | 21.8568 | 22.3897 | 22.4025 | 22.3937 | 22.0823 | 21.3066 | 22.2637 | 21.5928 | 21.7735 | 21.9167 | 21.1088 | 21.2049 | 21.4249 | 20.5063 | 20.6523 | 20.9564 | 21.9248 | 21.6903 | 21.3341 | 20.4451 | 20.5628 | 20.4771 | 22.0422 | 21.6619 | 21.1948 | 22.0028 | 21.7503 | 21.3748 | 19.9583 | 20.5837 |  | 20.5981 | 20.2647 | 20.3596 | 19.0379 |  | 16.654 | 16.6944 | 16.4424 | 16.7744 | 17.0379 | 17.7428 | 18.266 | 15.9189 | 16.6071 | 16.5204 | 16.8014 | 17.8646 | 44.3207 | 47.1804 | 43.428 | 21.3257 |  |  | 0.45233 | -0.20837 | -43.3054 | 0.23783 | 0.33263 | -197.8315 | 16.6424 | -0.28489 | 0.084355 | -0.23906 | -0.11758 | 8.8288 | 9.0587 | 1.9776 | 21.809 | 22.0387 | 22.2353 | 22.3015 | 22.1494 | 21.4937 | 20.3212 | 22.2208 | 22.3946 | 22.4272 | 22.3805 | 22.027 | 21.2729 | 22.295 | 17.1951 | 17.1597 | 16.4195 | 16.3395 | 16.2722 | 17.0602 | 16.6869 | 22.3919 | 22.1633 | 21.7367 | 22.1012 | 21.8294 | 21.3426 | 21.9732 | 21.559 | 20.9521 | 20.148 | 20.3936 | 19.9595 | 19.7491 | -0.0021504 | 0.14553 | 20.7689 | 22.0867 | 22.4108 | 20.1397 | 21.7056 | 22.1505 | 21.9826 | 21.7516 | 21.3294 | 21.8358 | 21.5028 | 21.1038 | 20.5575 | 20.5586 | 20.5086 | 20.4998 | 20.1214 |  | 20.2406 | 19.8886 | 20.134 | 19.7767 | 20.1226 | 20.3732 |  | 20.4662 |  |  | 20.2763 | 20.4004 | 20.6214 | [5 empty] | 21.9711 | 20.3731 | 21.7178 | 22.1151 | 19.5834 | 21.2543 | 21.9026 | 19.4049 | 19.9781 | 21.1837 |  | 19.6719 | 20.9962 | 18.853 | 19.7182 | 20.8591 | 19.4403 | 20.1545 | 19.0572 | 20.2172 | 19.1998 | 20.3516 | 18.6772 | 20.1025 | 21.1132 | 19.4495 | 19.8049 | 21.0291 | 18.9255 | 19.8422 | 20.8739 | 19.0096 | 20.2595 | 19.3367 | 19.9661 | 18.9494 | 20.1992 | -0.096036 | 20.9462 | 0.047215 | 0.016248 | -26.9853 | 3.0968 | -1.02 | -0.31 | 0.80314 | -0.54159 | -7.8077 | 0.57861 | 0.68551 | -16.7179 | 4.8489 | 0.42343 | 0.42632 | 0.42905 | 0.38721 | 0.42984 | 0.44407 | 0.43066
42838.4118 | -729 | 22.8984 | 22.8708 | 22.8641 | 22.8002 | 22.4411 | 21.7977 | 22.7501 | 21.8635 | 22.3931 | 22.4108 | 22.3884 | 22.0877 | 21.3124 | 22.2693 | 21.5843 | 21.7688 | 21.9107 | 21.1026 | 21.1962 | 21.422 | 20.5004 | 20.6463 | 20.9444 | 21.9225 | 21.6933 | 21.3224 | 20.4465 | 20.557 | 20.469 | 22.0484 | 21.6602 | 21.2033 | 22.0096 | 21.7512 | 21.3719 | 19.948 | 20.5801 |  | 20.5972 | 20.2667 | 20.3573 | 19.0288 |  | 16.657 | 16.6918 | 16.4369 | 16.7543 | 17.0273 | 17.7218 | 18.2401 | 15.9231 | 16.6091 | 16.4442 | 16.802 | 17.8656 | 44.3422 | 47.1926 | 43.4362 | 21.3286 |  |  | 0.45627 | -0.25437 | -43.8606 | 0.56179 | 0.14141 | -197.7987 | 16.1594 | -0.13441 | -0.28791 | -0.33788 | -0.080954 | 8.829 | 9.0587 | 1.978 | 21.8109 | 22.049 | 22.243 | 22.305 | 22.1518 | 21.499 | 20.3222 | 22.2243 | 22.3981 | 22.4325 | 22.3877 | 22.0252 | 21.2726 | 22.301 | 17.195 | 17.1608 | 16.4811 | 16.3518 | 16.2645 | 17.0699 | 16.7003 | 22.4004 | 22.1628 | 21.7403 | 22.1048 | 21.8327 | 21.3451 | 21.9738 | 21.5606 | 20.9537 | 20.1516 | 20.3939 | 19.9617 | 19.7526 | -0.13564 | 0.16322 | 20.7686 | 22.0905 | 22.4093 | 20.1332 | 21.7059 | 22.1542 | 21.9714 | 21.7451 | 21.3268 | 21.825 | 21.4982 | 21.0954 | 20.5509 | 20.5538 | 20.4932 | 20.5084 | 20.1261 |  | 20.2422 | 19.8662 | 20.1414 | 19.7773 | 20.1189 | 20.3722 |  | 20.4668 |  |  | 20.2732 | 20.4016 | 20.6185 | [5 empty] | 21.9685 | 20.3763 | 21.7161 | 22.1071 | 19.5861 | 21.2547 | 21.9031 | 19.4064 | 19.9787 | 21.1769 |  | 19.6721 | 20.9986 | 18.8499 | 19.7193 | 20.8569 | 19.4361 | 20.1426 | 19.0508 | 20.2177 | 19.1993 | 20.3438 | 18.6866 | 20.1124 | 21.123 | 19.4591 | 19.8183 | 21.0408 | 18.933 | 19.848 | 20.8828 | 19.0171 | 20.2718 | 19.3386 | 19.965 | 18.9549 | 20.1969 | 0.015449 | 20.9458 | 0.047492 | 0.014433 | -27.0933 | 3.0968 | -1.17 | 0.27 | 0.80662 | -0.59838 | -7.8575 | 0.88927 | 0.44695 | -16.7159 | 4.7778 | 0.42335 | 0.42719 | 0.42891 | 0.38835 | 0.42456 | 0.44397 | 0.43069
42838.4119 | -728 | 22.8994 | 22.8659 | 22.859 | 22.8013 | 22.4446 | 21.7899 | 22.739 | 21.86 | 22.3895 | 22.4065 | 22.3865 | 22.0772 | 21.3007 | 22.2651 | 21.5854 | 21.7729 | 21.9031 | 21.1012 | 21.1909 | 21.4222 | 20.5016 | 20.6525 | 20.9419 | 21.9279 | 21.6921 | 21.3302 | 20.4394 | 20.5643 | 20.4667 | 22.0467 | 21.6639 | 21.1954 | 22.0052 | 21.752 | 21.3746 | 19.9472 | 20.5787 |  | 20.5921 | 20.2602 | 20.3563 | 19.0295 |  | 16.6579 | 16.6864 | 16.4396 | 16.7527 | 17.0122 | 17.7082 | 18.2305 | 15.9356 | 16.6102 | 16.3695 | 16.814 | 17.8663 | 44.3461 | 47.1967 | 43.4446 | 21.3364 |  |  | 0.39516 | -0.23006 | -43.9986 | 0.25229 | 0.27086 | -197.8834 | 16.0851 | -0.3046 | -0.18808 | 0.05382 | -0.072447 | 8.8303 | 9.0599 | 1.9787 | 21.8204 | 22.0484 | 22.2479 | 22.3199 | 22.1658 | 21.4929 | 20.3369 | 22.2391 | 22.4107 | 22.4394 | 22.3958 | 22.034 | 21.2828 | 22.3111 | 17.1954 | 17.125 | 16.4938 | 16.3524 | 16.2657 | 17.0819 | 16.6987 | 22.392 | 22.1685 | 21.7314 | 22.106 | 21.8286 | 21.34 | 21.9742 | 21.564 | 20.9493 | 20.149 | 20.3889 | 19.9567 | 19.7486 | -0.032034 | -0.098873 | 20.7638 | 22.094 | 22.4102 | 20.1401 | 21.7005 | 22.1662 | 21.9773 | 21.7493 | 21.3166 | 21.8318 | 21.504 | 21.1066 | 20.559 | 20.5516 | 20.5044 | 20.504 | 20.1319 |  | 20.253 | 19.8599 | 20.1366 | 19.7771 | 20.1211 | 20.3779 |  | 20.4736 |  |  | 20.2748 | 20.3954 | 20.6315 | [5 empty] | 21.9708 | 20.3785 | 21.7236 | 22.1149 | 19.5795 | 21.2576 | 21.9034 | 19.4051 | 19.977 | 21.1841 |  | 19.6848 | 20.9923 | 18.8532 | 19.7233 | 20.8622 | 19.4391 | 20.1487 | 19.0564 | 20.2076 | 19.1955 | 20.3396 | 18.6875 | 20.1065 | 21.1225 | 19.4617 | 19.8163 | 21.031 | 18.9259 | 19.8482 | 20.8803 | 19.0227 | 20.2636 | 19.3335 | 19.9614 | 18.9526 | 20.1922 | -0.048177 | 20.9486 | 0.046883 | 0.013446 | -26.9991 | 3.0968 | -1.02 | 0.22 | 0.75066 | -0.56906 | -7.8698 | 0.59593 | 0.61856 | -16.7191 | 4.7667 | 0.42355 | 0.42721 | 0.42899 | 0.3897 | 0.42297 | 0.44393 | 0.43071
42838.4119 | -727 | 22.8941 | 22.8683 | 22.8603 | 22.796 | 22.4454 | 21.795 | 22.7425 | 21.8605 | 22.3917 | 22.4065 | 22.3887 | 22.0854 | 21.3089 | 22.2672 | 21.5843 | 21.7693 | 21.9063 | 21.0956 | 21.1956 | 21.4193 | 20.5017 | 20.6534 | 20.9455 | 21.9241 | 21.689 | 21.326 | 20.442 | 20.5576 | 20.4685 | 22.052 | 21.6685 | 21.1943 | 22.0134 | 21.7512 | 21.3787 | 19.9606 | 20.5803 |  | 20.5917 | 20.264 | 20.3677 | 19.0436 |  | 16.6605 | 16.6901 | 16.4383 | 16.7464 | 16.996 | 17.7238 | 18.2439 | 15.9329 | 16.5961 | 16.3234 | 16.8099 | 17.8687 | 44.3673 | 47.2189 | 43.445 | 21.3384 |  |  | 0.45824 | -0.2938 | -44.7471 | 0.41197 | 0.35957 | -197.8742 | 15.8348 | -0.44851 | -0.13671 | -0.080872 | 0.023727 | 8.8297 | 9.0593 | 1.9786 | 21.8177 | 22.0407 | 22.2374 | 22.3111 | 22.141 | 21.4959 | 20.3245 | 22.2204 | 22.3926 | 22.4336 | 22.3906 | 22.0283 | 21.2747 | 22.302 | 17.1794 | 17.0628 | 16.4648 | 16.3462 | 16.2657 | 17.0758 | 16.7002 | 22.3964 | 22.1685 | 21.7321 | 22.1013 | 21.8303 | 21.3425 | 21.9679 | 21.5644 | 20.9494 | 20.145 | 20.3981 | 19.9521 | 19.7507 | 0.05683 | -0.21413 | 20.7653 | 22.0947 | 22.4051 | 20.1328 | 21.7008 | 22.1519 | 21.9778 | 21.7458 | 21.3136 | 21.8327 | 21.4908 | 21.0942 | 20.5428 | 20.5419 | 20.4916 | 20.508 | 20.1274 |  | 20.2478 | 19.8392 | 20.1355 | 19.7747 | 20.1102 | 20.3744 |  | 20.4664 |  |  | 20.2817 | 20.3915 | 20.6298 | [5 empty] | 21.9704 | 20.3734 | 21.7203 | 22.1098 | 19.5757 | 21.251 | 21.9013 | 19.4055 | 19.9749 | 21.184 |  | 19.6782 | 20.9928 | 18.8522 | 19.7163 | 20.8616 | 19.4381 | 20.1483 | 19.061 | 20.201 | 19.1934 | 20.3421 | 18.6883 | 20.1059 | 21.1192 | 19.4591 | 19.8145 | 21.032 | 18.9303 | 19.8391 | 20.8702 | 19.0207 | 20.2651 | 19.3341 | 19.9583 | 18.9449 | 20.1883 | -0.16078 | 20.9476 | 0.046508 | 0.013707 | -27.0607 | 3.0968 | -0.81 | -0.04 | 0.80836 | -0.64309 | -7.9365 | 0.76151 | 0.71271 | -16.7191 | 4.7296 | 0.4235 | 0.42775 | 0.42869 | 0.39076 | 0.42635 | 0.44399 | 0.43052
42838.4119 | -726 | 22.893 | 22.87 | 22.8596 | 22.7971 | 22.4508 | 21.7967 | 22.7481 | 21.8649 | 22.3952 | 22.4106 | 22.394 | 22.0841 | 21.3116 | 22.2699 | 21.5847 | 21.7637 | 21.9072 | 21.0944 | 21.1966 | 21.4163 | 20.4999 | 20.6503 | 20.9452 | 21.9157 | 21.6893 | 21.3308 | 20.4404 | 20.557 | 20.4725 | 22.0458 | 21.659 | 21.1878 | 22.0015 | 21.7437 | 21.3689 | 19.9514 | 20.5782 |  | 20.5895 | 20.2538 | 20.357 | 19.0393 |  | 16.655 | 16.6854 | 16.4304 | 16.7387 | 16.9861 | 17.7043 | 18.2392 | 15.9239 | 16.6006 | 16.2817 | 16.8067 | 17.8705 | 44.379 | 47.234 | 43.4595 | 21.3407 |  |  | 0.33536 | -0.39302 | -44.9587 | 0.51053 | 0.24064 | -197.8197 | 15.6081 | -0.51554 | -0.20988 | -0.018771 | -0.074183 | 8.8286 | 9.0582 | 1.9782 | 21.8109 | 22.0424 | 22.2397 | 22.3066 | 22.1471 | 21.4953 | 20.3168 | 22.2302 | 22.4014 | 22.4304 | 22.3945 | 22.0346 | 21.2784 | 22.3013 | 17.1949 | 17.1017 | 16.4198 | 16.3542 | 16.2613 | 17.0803 | 16.7052 | 22.3923 | 22.1682 | 21.7362 | 22.1104 | 21.825 | 21.345 | 21.9724 | 21.5678 | 20.9532 | 20.1471 | 20.3974 | 19.9539 | 19.7559 | -0.047565 | -0.06749 | 20.7671 | 22.0951 | 22.4153 | 20.1378 | 21.713 | 22.1552 | 21.9732 | 21.7406 | 21.3228 | 21.8291 | 21.5038 | 21.0966 | 20.5475 | 20.5524 | 20.4993 | 20.5096 | 20.1298 |  | 20.2482 | 19.8385 | 20.14 | 19.7711 | 20.1211 | 20.3749 |  | 20.469 |  |  | 20.2804 | 20.3864 | 20.623 | [5 empty] | 21.9649 | 20.3664 | 21.7092 | 22.1058 | 19.5755 | 21.25 | 21.8947 | 19.3996 | 19.9724 | 21.1781 |  | 19.6689 | 20.9888 | 18.8471 | 19.713 | 20.8547 | 19.436 | 20.1402 | 19.057 | 20.1953 | 19.1888 | 20.3352 | 18.692 | 20.1027 | 21.1188 | 19.4603 | 19.8199 | 21.0307 | 18.9305 | 19.8357 | 20.8719 | 19.0196 | 20.2706 | 19.3411 | 19.9624 | 18.9485 | 20.1878 | 0.045315 | 20.9475 | 0.045931 | 0.01505 | -26.9523 | 3.0969 | -0.89 | -0.44 | 0.69154 | -0.74379 | -7.9552 | 0.84773 | 0.58302 | -16.7163 | 4.6955 | 0.42345 | 0.42791 | 0.42915 | 0.38958 | 0.43194 | 0.4438 | 0.43045
42838.4119 | -725 | 22.8941 | 22.8597 | 22.849 | 22.7879 | 22.4354 | 21.7825 | 22.7358 | 21.8586 | 22.3882 | 22.4022 | 22.3892 | 22.0706 | 21.3056 | 22.2593 | 21.585 | 21.7629 | 21.9062 | 21.0979 | 21.1935 | 21.4131 | 20.5049 | 20.6471 | 20.9383 | 21.9213 | 21.6842 | 21.3288 | 20.4369 | 20.5528 | 20.467 | 22.0472 | 21.6567 | 21.1865 | 21.9975 | 21.7424 | 21.3681 | 19.9425 | 20.5649 |  | 20.5928 | 20.2514 | 20.3544 | 19.0238 |  | 16.6599 | 16.6919 | 16.4352 | 16.7333 | 16.9637 | 17.6911 | 18.2123 | 15.9445 | 16.6054 | 16.2666 | 16.8121 | 17.8756 | 44.3797 | 47.2451 | 43.466 | 21.3321 |  |  | 0.42275 | -0.2156 | -45.7827 | 0.57822 | 0.11184 | -197.8854 | 15.5581 | -0.59965 | -0.0039932 | -0.0055534 | -0.034082 | 8.8282 | 9.0579 | 1.9777 | 21.8039 | 22.0376 | 22.2345 | 22.3033 | 22.1464 | 21.4945 | 20.3179 | 22.2272 | 22.3951 | 22.4282 | 22.3814 | 22.025 | 21.2764 | 22.3003 | 17.2139 | 17.155 | 16.3811 | 16.3303 | 16.245 | 17.0665 | 16.6904 | 22.3925 | 22.169 | 21.7323 | 22.0968 | 21.818 | 21.3375 | 21.9701 | 21.5592 | 20.9429 | 20.1376 | 20.395 | 19.9461 | 19.7507 | 0.026946 | -0.074337 | 20.7675 | 22.0995 | 22.4098 | 20.1462 | 21.712 | 22.1525 | 21.9756 | 21.7413 | 21.3282 | 21.8352 | 21.5047 | 21.1051 | 20.545 | 20.5558 | 20.5042 | 20.5031 | 20.1253 |  | 20.2389 | 19.8112 | 20.1347 | 19.7528 | 20.1173 | 20.3766 |  | 20.4639 |  |  | 20.2784 | 20.3845 | 20.6217 | [5 empty] | 21.967 | 20.3638 | 21.7114 | 22.1078 | 19.5742 | 21.2507 | 21.8965 | 19.4056 | 19.9775 | 21.179 |  | 19.6749 | 20.9902 | 18.8561 | 19.7119 | 20.8603 | 19.4398 | 20.1439 | 19.0557 | 20.1978 | 19.1872 | 20.3285 | 18.6862 | 20.1042 | 21.118 | 19.4609 | 19.8152 | 21.027 | 18.9276 | 19.8416 | 20.8701 | 19.0225 | 20.269 | 19.3352 | 19.9633 | 18.9472 | 20.1838 | -0.20047 | 20.9478 | 0.04566 | 0.01513 | -26.9833 | 3.0969 | -0.97 | -0.03 | 0.77643 | -0.5509 | -8.0278 | 0.90218 | 0.39746 | -16.7187 | 4.6878 | 0.42326 | 0.4285 | 0.42953 | 0.38585 | 0.43452 | 0.44393 | 0.43027
42838.4119 | -724 | 22.8964 | 22.8673 | 22.8555 | 22.793 | 22.4404 | 21.7956 | 22.7424 | 21.8623 | 22.3855 | 22.411 | 22.3868 | 22.0843 | 21.3043 | 22.2663 | 21.5847 | 21.7612 | 21.9056 | 21.0951 | 21.1884 | 21.4125 | 20.501 | 20.6446 | 20.9416 | 21.9192 | 21.6861 | 21.3199 | 20.4374 | 20.5502 | 20.4701 | 22.0584 | 21.6603 | 21.1966 | 22.009 | 21.7539 | 21.3801 | 19.9647 | 20.5852 |  | 20.6009 | 20.2602 | 20.3748 | 19.0383 |  | 16.6567 | 16.6869 | 16.4298 | 16.7222 | 16.9617 | 17.6753 | 18.1994 | 15.9558 | 16.6053 | 16.2483 | 16.8111 | 17.8743 | 44.3835 | 47.2589 | 43.4537 | 21.3364 |  |  | 0.61003 | -0.092061 | -46.1987 | 0.51382 | 0.19004 | -197.8539 | 15.361 | -0.51488 | -0.084752 | -0.044996 | -0.046581 | 8.8291 | 9.0587 | 1.9788 | 21.8113 | 22.0437 | 22.2432 | 22.3091 | 22.1455 | 21.4952 | 20.319 | 22.2291 | 22.4012 | 22.4392 | 22.3817 | 22.0345 | 21.276 | 22.3058 | 17.2464 | 17.1828 | 16.3795 | 16.3278 | 16.2487 | 17.0729 | 16.6953 | 22.3909 | 22.1661 | 21.7342 | 22.1026 | 21.8246 | 21.3359 | 21.9616 | 21.5684 | 20.9486 | 20.1506 | 20.3974 | 19.9504 | 19.7613 | -0.15687 | -0.23544 | 20.7716 | 22.0945 | 22.3973 | 20.1518 | 21.6992 | 22.1505 | 21.9753 | 21.7409 | 21.3253 | 21.8284 | 21.4964 | 21.0992 | 20.5324 | 20.5546 | 20.5037 | 20.4979 | 20.1286 |  | 20.2369 | 19.7878 | 20.1396 | 19.7449 | 20.1157 | 20.381 |  | 20.4601 |  |  | 20.275 | 20.3856 | 20.6243 | [5 empty] | 21.9653 | 20.3675 | 21.7152 | 22.1043 | 19.583 | 21.2508 | 21.8964 | 19.4117 | 19.9868 | 21.1898 |  | 19.6803 | 20.9955 | 18.8565 | 19.7156 | 20.8658 | 19.4448 | 20.1491 | 19.0589 | 20.2006 | 19.1913 | 20.3308 | 18.6774 | 20.1015 | 21.1182 | 19.4564 | 19.812 | 21.0234 | 18.9289 | 19.8411 | 20.8675 | 19.0225 | 20.2651 | 19.3312 | 19.9647 | 18.9415 | 20.1811 | -0.067283 | 20.9489 | 0.045249 | 0.014818 | -27.0724 | 3.0969 | -1.1 | 0.03 | 0.93269 | -0.35998 | -8.0641 | 0.85045 | 0.51809 | -16.7169 | 4.6579 | 0.4231 | 0.42931 | 0.4297 | 0.38299 | 0.43526 | 0.44427 | 0.43041
42838.4119 | -723 | 22.8984 | 22.8723 | 22.8627 | 22.7957 | 22.4489 | 21.7967 | 22.7421 | 21.862 | 22.3961 | 22.4064 | 22.396 | 22.0855 | 21.3093 | 22.2639 | 21.5783 | 21.7603 | 21.9003 | 21.0994 | 21.1888 | 21.4158 | 20.4914 | 20.6461 | 20.937 | 21.9137 | 21.6796 | 21.322 | 20.4349 | 20.5474 | 20.4716 | 22.0449 | 21.6608 | 21.1994 | 22.0055 | 21.7499 | 21.3702 | 19.9463 | 20.564 |  | 20.5903 | 20.2489 | 20.3591 | 19.0254 |  | 16.6497 | 16.6791 | 16.4324 | 16.7346 | 16.9607 | 17.678 | 18.2301 | 15.9434 | 16.6024 | 16.2226 | 16.8147 | 17.875 | 44.3964 | 47.2757 | 43.4602 | 21.3412 |  |  | 0.3899 | -0.16697 | -46.9077 | 0.47242 | 0.33658 | -197.8703 | 15.0101 | -0.54905 | -0.16104 | -0.11822 | -0.056302 | 8.83 | 9.0596 | 1.9786 | 21.8125 | 22.045 | 22.2417 | 22.3074 | 22.1512 | 21.4998 | 20.3236 | 22.2327 | 22.3937 | 22.4336 | 22.386 | 22.03 | 21.2786 | 22.3033 | 17.2918 | 17.1743 | 16.3803 | 16.3177 | 16.257 | 17.0703 | 16.6939 | 22.3988 | 22.1654 | 21.7411 | 22.099 | 21.8307 | 21.3384 | 21.9704 | 21.5698 | 20.9532 | 20.1498 | 20.4021 | 19.9568 | 19.7689 | -0.29489 | -0.061213 | 20.7605 | 22.0901 | 22.3965 | 20.1459 | 21.7025 | 22.1551 | 21.9743 | 21.7414 | 21.3148 | 21.8265 | 21.4922 | 21.0945 | 20.5373 | 20.5478 | 20.5013 | 20.502 | 20.1365 |  | 20.2465 | 19.7694 | 20.1383 | 19.7458 | 20.1184 | 20.3806 |  | 20.4691 |  |  | 20.2858 | 20.3705 | 20.6341 | [5 empty] | 21.9657 | 20.3757 | 21.719 | 22.1084 | 19.585 | 21.2492 | 21.9049 | 19.4143 | 20.0027 | 21.1974 |  | 19.6961 | 21.0032 | 18.8537 | 19.7248 | 20.871 | 19.4534 | 20.1493 | 19.0674 | 20.2056 | 19.1927 | 20.3337 | 18.6691 | 20.1018 | 21.1133 | 19.4624 | 19.8226 | 21.0261 | 18.9247 | 19.836 | 20.8677 | 19.0313 | 20.2667 | 19.3326 | 19.9615 | 18.937 | 20.1798 | -0.21531 | 20.9489 | 0.045998 | 0.015079 | -27.0237 | 3.0969 | -0.85 | -0.01 | 0.74565 | -0.4848 | -8.1257 | 0.81546 | 0.68949 | -16.7177 | 4.6044 | 0.4232 | 0.42978 | 0.42977 | 0.37765 | 0.435 | 0.44401 | 0.43018
42838.4119 | -722 | 22.9014 | 22.8692 | 22.8696 | 22.7964 | 22.447 | 21.7943 | 22.7476 | 21.8621 | 22.3942 | 22.4004 | 22.3924 | 22.0803 | 21.3132 | 22.2701 | 21.5935 | 21.771 | 21.913 | 21.1042 | 21.2005 | 21.4261 | 20.5076 | 20.6556 | 20.9503 | 21.925 | 21.692 | 21.3292 | 20.444 | 20.5568 | 20.4863 | 22.0431 | 21.6606 | 21.1964 | 22.0045 | 21.7529 | 21.3769 | 19.9526 | 20.5733 |  | 20.5907 | 20.256 | 20.3596 | 19.0251 |  | 16.6565 | 16.6938 | 16.442 | 16.7505 | 16.9936 | 17.7045 | 18.2492 | 15.909 | 16.6037 | 16.198 | 16.8244 | 17.8759 | 44.4066 | 47.2837 | 43.4664 | 21.3376 |  |  | 0.36887 | -0.18603 | -47.459 | 0.54668 | 0.14404 | -197.8204 | 14.7065 | -0.58256 | -0.23985 | -0.097446 | 0.049941 | 8.83 | 9.0597 | 1.978 | 21.8225 | 22.0436 | 22.2484 | 22.3157 | 22.1505 | 21.4931 | 20.3251 | 22.2328 | 22.3956 | 22.4378 | 22.3883 | 22.0307 | 21.2815 | 22.3071 | 17.3436 | 17.1458 | 16.391 | 16.2945 | 16.2688 | 17.0807 | 16.7027 | 22.3897 | 22.1682 | 21.7325 | 22.1028 | 21.8219 | 21.3327 | 21.9628 | 21.5561 | 20.9458 | 20.1449 | 20.395 | 19.9519 | 19.7717 | -0.099271 | 0.12746 | 20.7655 | 22.0965 | 22.4156 | 20.1481 | 21.7139 | 22.1604 | 21.9842 | 21.7557 | 21.3219 | 21.832 | 21.5066 | 21.1049 | 20.5472 | 20.5502 | 20.5114 | 20.5082 | 20.1337 |  | 20.2524 | 19.7561 | 20.1402 | 19.7482 | 20.1233 | 20.3789 |  | 20.467 |  |  | 20.2874 | 20.3615 | 20.6237 | [5 empty] | 21.9657 | 20.37 | 21.7138 | 22.102 | 19.5782 | 21.2541 | 21.8972 | 19.4113 | 19.9962 | 21.1982 |  | 19.6968 | 21.0006 | 18.8503 | 19.7198 | 20.8687 | 19.453 | 20.1529 | 19.0701 | 20.2013 | 19.1924 | 20.3353 | 18.6733 | 20.1003 | 21.1222 | 19.4682 | 19.8248 | 21.033 | 18.9356 | 19.8379 | 20.8667 | 19.0444 | 20.2776 | 19.3318 | 19.9596 | 18.9422 | 20.178 | -0.11421 | 20.9493 | 0.046767 | 0.016393 | -27.0132 | 3.097 | -0.64 | 0.06 | 0.72529 | -0.51173 | -8.1735 | 0.87723 | 0.45107 | -16.7163 | 4.5578 | 0.42348 | 0.43021 | 0.42986 | 0.37309 | 0.43485 | 0.44423 | 0.42993
42838.4119 | -721 | 22.8995 | 22.8741 | 22.8648 | 22.7986 | 22.4427 | 21.7968 | 22.7403 | 21.8614 | 22.3893 | 22.4055 | 22.3908 | 22.0847 | 21.3102 | 22.2673 | 21.5862 | 21.7624 | 21.9041 | 21.0996 | 21.1944 | 21.4205 | 20.496 | 20.639 | 20.9418 | 21.9091 | 21.6829 | 21.3201 | 20.442 | 20.5508 | 20.4859 | 22.046 | 21.6583 | 21.1953 | 22.0053 | 21.7541 | 21.3734 | 19.9506 | 20.5703 |  | 20.6003 | 20.2552 | 20.3601 | 19.0281 |  | 16.6525 | 16.7076 | 16.4483 | 16.7615 | 17.0232 | 17.7189 | 18.2653 | 15.8806 | 16.6052 | 16.1771 | 16.8184 | 17.8772 | 44.4219 | 47.2974 | 43.4783 | 21.3418 |  |  | 0.47467 | -0.12886 | -47.8336 | 0.40145 | 0.33263 | -197.8223 | 14.6171 | -0.46691 | 0.013326 | 0.037246 | 0.15115 | 8.8289 | 9.0585 | 1.9778 | 21.8141 | 22.0418 | 22.2378 | 22.3097 | 22.1416 | 21.4865 | 20.3188 | 22.2221 | 22.3911 | 22.4277 | 22.3868 | 22.0256 | 21.2691 | 22.2911 | 17.372 | 17.1161 | 16.4037 | 16.2741 | 16.2562 | 17.072 | 16.6961 | 22.3965 | 22.1697 | 21.7429 | 22.1045 | 21.8288 | 21.3402 | 21.9685 | 21.5618 | 20.948 | 20.1488 | 20.3969 | 19.9604 | 19.7847 | 0.028912 | -0.10058 | 20.7534 | 22.1008 | 22.407 | 20.1453 | 21.7039 | 22.1616 | 21.9802 | 21.7478 | 21.3164 | 21.8269 | 21.501 | 21.1001 | 20.5464 | 20.5462 | 20.507 | 20.5078 | 20.1337 |  | 20.2584 | 19.7377 | 20.1423 | 19.744 | 20.1229 | 20.3836 |  | 20.4692 |  |  | 20.2864 | 20.3666 | 20.6199 | [5 empty] | 21.9652 | 20.3684 | 21.707 | 22.1054 | 19.5842 | 21.2513 | 21.8996 | 19.4093 | 19.9917 | 21.2009 |  | 19.6961 | 21.0053 | 18.8532 | 19.7245 | 20.8761 | 19.4513 | 20.1537 | 19.0566 | 20.2063 | 19.1921 | 20.336 | 18.6601 | 20.0994 | 21.1138 | 19.4564 | 19.8218 | 21.0307 | 18.9318 | 19.8363 | 20.876 | 19.0473 | 20.2725 | 19.3263 | 19.9606 | 18.9411 | 20.1739 | -0.08435 | 20.9486 | 0.046625 | 0.016495 | -27.012 | 3.0969 | -0.52 | -0.12 | 0.82275 | -0.42591 | -8.2059 | 0.75176 | 0.68548 | -16.7168 | 4.5441 | 0.42368 | 0.43079 | 0.42996 | 0.36893 | 0.43266 | 0.44408 | 0.4297
42838.4119 | -720 | 22.9007 | 22.8703 | 22.8662 | 22.7944 | 22.4388 | 21.794 | 22.7448 | 21.8561 | 22.3892 | 22.4065 | 22.3916 | 22.0807 | 21.3009 | 22.2611 | 21.582 | 21.7615 | 21.9018 | 21.0907 | 21.186 | 21.4138 | 20.487 | 20.6367 | 20.9409 | 21.9203 | 21.6948 | 21.3159 | 20.4353 | 20.5461 | 20.4873 | 22.0506 | 21.6655 | 21.2018 | 22.0075 | 21.7567 | 21.3736 | 19.9525 | 20.5727 |  | 20.601 | 20.2601 | 20.3603 | 19.0289 |  | 16.6525 | 16.7017 | 16.4559 | 16.7643 | 17.0437 | 17.7364 | 18.2937 | 15.8921 | 16.6096 | 16.1798 | 16.8273 | 17.8751 | 44.445 | 47.3031 | 43.4848 | 21.3345 |  |  | 0.31039 | -0.26357 | -48.8225 | 0.041354 | 0.29452 | -197.8118 | 14.7006 | -0.62134 | -0.018199 | 0.08508 | 0.063655 | 8.8276 | 9.0574 | 1.9788 | 21.8257 | 22.0566 | 22.2458 | 22.3064 | 22.1527 | 21.4998 | 20.3294 | 22.2304 | 22.3987 | 22.4363 | 22.3881 | 22.0316 | 21.2858 | 22.3069 | 17.394 | 17.0937 | 16.4505 | 16.2664 | 16.252 | 17.0722 | 16.689 | 22.3911 | 22.1648 | 21.7351 | 22.0972 | 21.8212 | 21.3346 | 21.9563 | 21.5532 | 20.9429 | 20.1433 | 20.4 | 19.9596 | 19.7826 | 0.012791 | -0.065017 | 20.7451 | 22.0908 | 22.4119 | 20.1519 | 21.7105 | 22.1606 | 21.9742 | 21.7426 | 21.3162 | 21.8177 | 21.4939 | 21.0962 | 20.542 | 20.5406 | 20.5009 | 20.5043 | 20.1272 |  | 20.2477 | 19.7208 | 20.1393 | 19.7367 | 20.1158 | 20.3766 |  | 20.4607 |  |  | 20.2881 | 20.3595 | 20.6082 | [5 empty] | 21.9698 | 20.3618 | 21.7047 | 22.0991 | 19.5814 | 21.2485 | 21.8932 | 19.4018 | 19.9879 | 21.1846 |  | 19.6884 | 20.9916 | 18.8434 | 19.7171 | 20.8653 | 19.4434 | 20.1455 | 19.0464 | 20.1866 | 19.1942 | 20.3201 | 18.663 | 20.111 | 21.1286 | 19.4662 | 19.8198 | 21.0344 | 18.9371 | 19.8374 | 20.8724 | 19.0469 | 20.2808 | 19.3319 | 19.9583 | 18.9404 | 20.1701 | -0.1272 | 20.9487 | 0.04692 | 0.01725 | -27.0642 | 3.097 | -0.63 | -0.38 | 0.66531 | -0.60912 | -8.2902 | 0.24128 | 0.64504 | -16.7169 | 4.5572 | 0.4235 | 0.43116 | 0.42993 | 0.36651 | 0.42663 | 0.44412 | 0.42958
42838.412 | -719 | 22.897 | 22.872 | 22.8583 | 22.7953 | 22.4373 | 21.7945 | 22.7418 | 21.8538 | 22.3894 | 22.3992 | 22.396 | 22.0773 | 21.304 | 22.265 | 21.5952 | 21.7724 | 21.9058 | 21.1019 | 21.1931 | 21.4201 | 20.5075 | 20.6496 | 20.9518 | 21.9277 | 21.6975 | 21.3197 | 20.4398 | 20.5559 | 20.4853 | 22.0502 | 21.6646 | 21.1985 | 22.0073 | 21.7576 | 21.3811 | 19.9497 | 20.573 |  | 20.5995 | 20.2572 | 20.3636 | 19.0297 |  | 16.6524 | 16.6951 | 16.4491 | 16.7731 | 17.0721 | 17.7507 | 18.3013 | 15.8999 | 16.6035 | 16.1796 | 16.8208 | 17.8739 | 44.4618 | 47.308 | 43.4746 | 21.3331 |  |  | 0.4083 | -0.4607 | -49.7261 | 0.28975 | 0.25838 | -197.8328 | 14.2774 | -0.61345 | -0.11939 | 0.09599 | -0.032866 | 8.828 | 9.0575 | 1.979 | 21.8265 | 22.054 | 22.2437 | 22.3107 | 22.1482 | 21.4938 | 20.3292 | 22.2381 | 22.4074 | 22.436 | 22.388 | 22.0344 | 21.2811 | 22.3022 | 17.4066 | 17.1046 | 16.4426 | 16.257 | 16.2514 | 17.0721 | 16.6878 | 22.3854 | 22.1588 | 21.7279 | 22.0949 | 21.8197 | 21.3342 | 21.9569 | 21.555 | 20.937 | 20.1402 | 20.3955 | 19.9544 | 19.7872 | 0.055453 | -0.022413 | 20.7425 | 22.0934 | 22.4142 | 20.149 | 21.7104 | 22.1574 | 21.9739 | 21.743 | 21.3226 | 21.8321 | 21.497 | 21.1048 | 20.5504 | 20.5569 | 20.5046 | 20.5078 | 20.1312 |  | 20.2533 | 19.7064 | 20.1388 | 19.7324 | 20.1178 | 20.3746 |  | 20.4612 |  |  | 20.3051 | 20.3742 | 20.6133 | [5 empty] | 21.9753 | 20.3772 | 21.7193 | 22.1164 | 19.5892 | 21.2548 | 21.9052 | 19.4168 | 19.9978 | 21.2044 |  | 19.7104 | 21.0073 | 18.8492 | 19.7336 | 20.883 | 19.47 | 20.1571 | 19.0595 | 20.2112 | 19.1923 | 20.341 | 18.6773 | 20.1295 | 21.1372 | 19.4631 | 19.8316 | 21.0292 | 18.9453 | 19.8384 | 20.876 | 19.0573 | 20.2821 | 19.3329 | 19.9767 | 18.9428 | 20.1816 | -0.15224 | 20.9488 | 0.047393 | 0.016879 | -26.9828 | 3.097 | -0.89 | -0.03 | 0.76306 | -0.80531 | -8.3665 | 0.63864 | 0.60418 | -16.7182 | 4.4912 | 0.42358 | 0.43154 | 0.43012 | 0.3651 | 0.42737 | 0.44401 | 0.42935
42838.412 | -718 | 22.8937 | 22.8629 | 22.8615 | 22.7976 | 22.4334 | 21.7866 | 22.7309 | 21.8582 | 22.391 | 22.4007 | 22.3864 | 22.0837 | 21.3068 | 22.2655 | 21.5797 | 21.7638 | 21.9061 | 21.0849 | 21.1895 | 21.4191 | 20.4958 | 20.6447 | 20.9454 | 21.9196 | 21.689 | 21.3202 | 20.4351 | 20.5472 | 20.4822 | 22.0458 | 21.6591 | 21.1936 | 22.008 | 21.7534 | 21.3699 | 19.9461 | 20.5654 |  | 20.5958 | 20.25 | 20.3665 | 19.0288 |  | 16.6558 | 16.6953 | 16.4635 | 16.8052 | 17.1184 | 17.7797 | 18.3214 | 15.9198 | 16.6091 | 16.1846 | 16.8185 | 17.8723 | 44.4744 | 47.3141 | 43.4681 | 21.3317 |  |  | 0.44444 | -0.4009 | -49.9712 | 0.41525 | 0.20646 | -197.8263 | 14.125 | -0.56548 | -0.04447 | -0.27997 | -0.033561 | 8.8286 | 9.0585 | 1.9783 | 21.8156 | 22.0442 | 22.2369 | 22.3042 | 22.1449 | 21.4887 | 20.3195 | 22.2272 | 22.3928 | 22.425 | 22.3777 | 22.024 | 21.2669 | 22.2943 | 17.3926 | 17.1334 | 16.3986 | 16.2382 | 16.2581 | 17.0676 | 16.6847 | 22.4003 | 22.1707 | 21.7302 | 22.1034 | 21.8225 | 21.3403 | 21.9662 | 21.5637 | 20.9521 | 20.151 | 20.4103 | 19.9667 | 19.8009 | -0.090227 | -0.10249 | 20.7456 | 22.1047 | 22.42 | 20.152 | 21.7162 | 22.17 | 21.9872 | 21.7465 | 21.3352 | 21.8348 | 21.5049 | 21.1082 | 20.5517 | 20.5543 | 20.5093 | 20.5044 | 20.1326 |  | 20.2466 | 19.7012 | 20.14 | 19.7291 | 20.1165 | 20.3758 |  | 20.4614 |  |  | 20.3037 | 20.3704 | 20.6122 | [5 empty] | 21.9706 | 20.3794 | 21.7181 | 22.1066 | 19.5858 | 21.2533 | 21.9002 | 19.4301 | 20.0066 | 21.2077 |  | 19.7207 | 21.0127 | 18.8453 | 19.7278 | 20.8779 | 19.4688 | 20.1592 | 19.0484 | 20.2043 | 19.1947 | 20.3371 | 18.6726 | 20.1197 | 21.1309 | 19.4619 | 19.8318 | 21.0315 | 18.9414 | 19.8364 | 20.8786 | 19.0571 | 20.2851 | 19.3166 | 19.9675 | 18.9355 | 20.1667 | -0.2372 | 20.9472 | 0.04735 | 0.016364 | -27.0338 | 3.0969 | -0.61 | -0.33 | 0.79612 | -0.75123 | -8.3871 | 0.76455 | 0.54011 | -16.7187 | 4.4674 | 0.42332 | 0.43173 | 0.43016 | 0.36612 | 0.4319 | 0.44391 | 0.42932
42838.412 | -717 | 22.9069 | 22.8717 | 22.8669 | 22.7929 | 22.4465 | 21.8001 | 22.7408 | 21.8669 | 22.4037 | 22.4102 | 22.3958 | 22.0904 | 21.3131 | 22.2736 | 21.5848 | 21.7634 | 21.9039 | 21.0997 | 21.1944 | 21.4191 | 20.494 | 20.6442 | 20.9375 | 21.9223 | 21.6899 | 21.325 | 20.4301 | 20.5529 | 20.475 | 22.0508 | 21.671 | 21.1948 | 22.0147 | 21.7463 | 21.3772 | 19.952 | 20.5661 |  | 20.5928 | 20.2485 | 20.3665 | 19.0353 |  | 16.6574 | 16.6878 | 16.483 | 16.827 | 17.1405 | 17.7986 | 18.3303 | 15.9377 | 16.6033 | 16.1907 | 16.8214 | 17.8805 | 44.4981 | 47.3398 | 43.4737 | 21.3415 |  |  | 0.52855 | -0.28788 | -50.9082 | 0.31471 | 0.0803 | -197.8026 | 13.8194 | -0.53985 | -0.23985 | -0.073319 | -0.042067 | 8.8278 | 9.0575 | 1.9781 | 21.8206 | 22.0472 | 22.2367 | 22.3065 | 22.1483 | 21.4947 | 20.3191 | 22.2253 | 22.3937 | 22.4344 | 22.3799 | 22.0229 | 21.2757 | 22.298 | 17.3576 | 17.0941 | 16.3465 | 16.2286 | 16.2623 | 17.0717 | 16.6892 | 22.3968 | 22.1699 | 21.7391 | 22.1046 | 21.8244 | 21.3376 | 21.9688 | 21.5661 | 20.9513 | 20.1485 | 20.4088 | 19.9673 | 19.7993 | -0.16729 | -0.085559 | 20.7564 | 22.1076 | 22.4259 | 20.1533 | 21.7204 | 22.1677 | 21.9817 | 21.7549 | 21.3358 | 21.8367 | 21.5083 | 21.1079 | 20.5526 | 20.5575 | 20.5145 | 20.519 | 20.1375 |  | 20.2609 | 19.6936 | 20.1399 | 19.7358 | 20.1243 | 20.3791 |  | 20.4696 |  |  | 20.3029 | 20.3802 | 20.6128 | [5 empty] | 21.971 | 20.3777 | 21.7171 | 22.1152 | 19.5966 | 21.2575 | 21.9013 | 19.4119 | 19.9899 | 21.2017 |  | 19.7079 | 20.9939 | 18.8376 | 19.7214 | 20.8595 | 19.4478 | 20.1446 | 19.0235 | 20.187 | 19.1847 | 20.3165 | 18.6646 | 20.1314 | 21.127 | 19.4651 | 19.8307 | 21.0241 | 18.9343 | 19.8433 | 20.8694 | 19.0497 | 20.2892 | 19.3224 | 19.9687 | 18.9358 | 20.1617 | 0.011183 | 20.9478 | 0.04716 | 0.016807 | -27.0573 | 3.097 | -0.66 | -0.01 | 0.86817 | -0.63658 | -8.4652 | 0.66558 | 0.33685 | -16.7183 | 4.419 | 0.42366 | 0.43194 | 0.43024 | 0.37048 | 0.43822 | 0.44393 | 0.42929
42838.412 | -716 | 22.8968 | 22.8634 | 22.8608 | 22.7938 | 22.4418 | 21.7846 | 22.7304 | 21.8571 | 22.3875 | 22.3996 | 22.3828 | 22.0803 | 21.3028 | 22.2647 | 21.5913 | 21.7628 | 21.9043 | 21.1009 | 21.1973 | 21.4249 | 20.4967 | 20.6477 | 20.9428 | 21.9246 | 21.6922 | 21.329 | 20.4354 | 20.5604 | 20.4757 | 22.0475 | 21.6658 | 21.196 | 22.0131 | 21.7478 | 21.372 | 19.9469 | 20.5663 |  | 20.5959 | 20.251 | 20.3643 | 19.0366 |  | 16.6667 | 16.7012 | 16.5118 | 16.8663 | 17.1723 | 17.8211 | 18.3469 | 15.9677 | 16.6091 | 16.1966 | 16.8183 | 17.8761 | 44.5066 | 47.3528 | 43.4648 | 21.3347 |  |  | 0.42539 | -0.057233 | -51.2223 | 0.22732 | 0.22486 | -197.8046 | 13.799 | -0.55562 | -0.11939 | -0.2806 | -0.087898 | 8.8296 | 9.0592 | 1.9783 | 21.8225 | 22.05 | 22.2452 | 22.3081 | 22.1476 | 21.4964 | 20.3188 | 22.2248 | 22.4012 | 22.4379 | 22.3822 | 22.0304 | 21.279 | 22.302 | 17.3336 | 17.0672 | 16.2922 | 16.1973 | 16.2491 | 17.0706 | 16.6903 | 22.3978 | 22.1731 | 21.744 | 22.1093 | 21.828 | 21.3432 | 21.9763 | 21.5645 | 20.9503 | 20.1544 | 20.4144 | 19.9732 | 19.8075 | -0.29744 | -0.060643 | 20.7549 | 22.1 | 22.4255 | 20.1499 | 21.7114 | 22.1665 | 21.9862 | 21.7575 | 21.3313 | 21.8388 | 21.5107 | 21.1068 | 20.5509 | 20.5625 | 20.518 | 20.515 | 20.1214 |  | 20.2529 | 19.6888 | 20.1406 | 19.7304 | 20.1215 | 20.3764 |  | 20.4685 |  |  | 20.3002 | 20.3853 | 20.6146 | [5 empty] | 21.9727 | 20.3669 | 21.7094 | 22.1124 | 19.5931 | 21.2565 | 21.8955 | 19.4189 | 19.9906 | 21.2074 |  | 19.7138 | 21.0056 | 18.8366 | 19.7328 | 20.8822 | 19.4581 | 20.1461 | 19.0173 | 20.1893 | 19.1866 | 20.3183 | 18.6671 | 20.1267 | 21.1349 | 19.4733 | 19.8348 | 21.0366 | 18.9376 | 19.8364 | 20.8786 | 19.0577 | 20.3045 | 19.3305 | 19.9726 | 18.9408 | 20.1638 | -0.20734 | 20.9473 | 0.048419 | 0.015391 | -27.0203 | 3.097 | -0.6 | 0.15 | 0.77885 | -0.28384 | -8.4915 | 0.56568 | 0.5637 | -16.719 | 4.4159 | 0.42384 | 0.43209 | 0.43029 | 0.37303 | 0.44437 | 0.44372 | 0.42926
42838.412 | -715 | 22.8957 | 22.8697 | 22.8606 | 22.7921 | 22.4383 | 21.7869 | 22.7399 | 21.8591 | 22.3939 | 22.4052 | 22.3906 | 22.0749 | 21.3079 | 22.2698 | 21.5929 | 21.765 | 21.912 | 21.1018 | 21.2026 | 21.423 | 20.4961 | 20.6478 | 20.949 | 21.9259 | 21.6936 | 21.3315 | 20.4366 | 20.5635 | 20.4788 | 22.0545 | 21.6681 | 21.1968 | 22.0192 | 21.7547 | 21.3774 | 19.9507 | 20.5641 |  | 20.5908 | 20.255 | 20.3612 | 19.051 |  | 16.6556 | 16.7109 | 16.5411 | 16.892 | 17.1919 | 17.8273 | 18.3544 | 15.9927 | 16.6079 | 16.2324 | 16.8204 | 17.8805 | 44.522 | 47.3671 | 43.4682 | 21.3422 |  |  | 0.40173 | -0.25371 | -51.9031 | 0.62356 | 0.058616 | -197.8348 | 13.3949 | -0.52211 | -0.39572 | -0.023596 | 0.037962 | 8.8289 | 9.0585 | 1.9792 | 21.8173 | 22.0494 | 22.2422 | 22.3124 | 22.1491 | 21.4992 | 20.3221 | 22.2313 | 22.401 | 22.4288 | 22.3877 | 22.0291 | 21.2759 | 22.2951 | 17.3151 | 17.0349 | 16.2725 | 16.1888 | 16.2296 | 17.0671 | 16.6904 | 22.3991 | 22.1679 | 21.733 | 22.0988 | 21.828 | 21.3371 | 21.9709 | 21.5569 | 20.9411 | 20.1452 | 20.4139 | 19.9637 | 19.8127 | -0.0041164 | -0.19911 | 20.7427 | 22.1007 | 22.4138 | 20.1502 | 21.7097 | 22.1623 | 21.9773 | 21.7469 | 21.322 | 21.8245 | 21.5005 | 21.0991 | 20.5411 | 20.5553 | 20.5068 | 20.5053 | 20.1128 |  | 20.2415 | 19.6684 | 20.1344 | 19.7206 | 20.1142 | 20.3712 |  | 20.4619 |  |  | 20.295 | 20.38 | 20.6035 | [5 empty] | 21.9618 | 20.3618 | 21.7103 | 22.0987 | 19.5888 | 21.2492 | 21.8916 | 19.4226 | 19.984 | 21.2077 |  | 19.7105 | 21.0027 | 18.8289 | 19.7225 | 20.8773 | 19.4554 | 20.1415 | 19.0187 | 20.1709 | 19.1769 | 20.3156 | 18.675 | 20.1335 | 21.1348 | 19.4784 | 19.8392 | 21.0373 | 18.9355 | 19.84 | 20.8751 | 19.0594 | 20.2921 | 19.33 | 19.971 | 18.9309 | 20.1511 | -0.085462 | 20.9478 | 0.048622 | 0.014941 | -27.0385 | 3.097 | -0.7 | -0.06 | 0.75689 | -0.59763 | -8.5479 | 0.93692 | 0.28781 | -16.7204 | 4.3508 | 0.4237 | 0.43245 | 0.43032 | 0.37467 | 0.44658 | 0.44345 | 0.4288
42838.412 | -714 | 22.8881 | 22.8608 | 22.86 | 22.789 | 22.4391 | 21.7894 | 22.7314 | 21.8488 | 22.3891 | 22.4106 | 22.3887 | 22.0747 | 21.3009 | 22.2586 | 21.5883 | 21.7681 | 21.9147 | 21.0974 | 21.1925 | 21.4259 | 20.4965 | 20.6452 | 20.9445 | 21.9269 | 21.6893 | 21.3265 | 20.4312 | 20.5655 | 20.4807 | 22.0456 | 21.659 | 21.1891 | 22.0079 | 21.7398 | 21.3711 | 19.9393 | 20.5603 |  | 20.5831 | 20.2491 | 20.3566 | 19.0464 |  | 16.6647 | 16.7391 | 16.5746 | 16.9139 | 17.1936 | 17.8206 | 18.3711 | 16.0014 | 16.6132 | 16.2697 | 16.8186 | 17.8787 | 44.5374 | 47.3878 | 43.4641 | 21.338 |  |  | 0.53644 | -0.15646 | -52.0628 | 0.66956 | 0.13812 | -197.8506 | 13.5276 | -0.55102 | -0.80341 | 0.0028386 | 0.011054 | 8.8285 | 9.0583 | 1.9784 | 21.8138 | 22.0419 | 22.2289 | 22.293 | 22.1334 | 21.4847 | 20.3189 | 22.2144 | 22.3923 | 22.424 | 22.3774 | 22.0179 | 21.2673 | 22.2915 | 17.2856 | 17.0321 | 16.2557 | 16.1681 | 16.2086 | 17.0682 | 16.6902 | 22.395 | 22.1702 | 21.7337 | 22.0991 | 21.821 | 21.3363 | 21.9694 | 21.5575 | 20.9404 | 20.1447 | 20.4185 | 19.9656 | 19.8169 | 0.14353 | -0.042954 | 20.7431 | 22.1032 | 22.4093 | 20.1503 | 21.7129 | 22.166 | 21.9804 | 21.7474 | 21.3246 | 21.8307 | 21.4955 | 21.1078 | 20.5431 | 20.5541 | 20.5041 | 20.5116 | 20.1122 |  | 20.2393 | 19.6661 | 20.1306 | 19.7173 | 20.1158 | 20.3737 |  | 20.4603 |  |  | 20.2925 | 20.39 | 20.6098 | [5 empty] | 21.9705 | 20.3586 | 21.7134 | 22.1057 | 19.5868 | 21.2481 | 21.8944 | 19.4243 | 20 | 21.206 |  | 19.7063 | 21.0097 | 18.8368 | 19.7232 | 20.87 | 19.4609 | 20.1482 | 19.0219 | 20.1804 | 19.1781 | 20.3224 | 18.6671 | 20.1381 | 21.1363 | 19.4744 | 19.8364 | 21.0397 | 18.9242 | 19.8314 | 20.8685 | 19.0643 | 20.2968 | 19.334 | 19.9671 | 18.9314 | 20.1513 | -0.11922 | 20.9471 | 0.048432 | 0.015036 | -27.0677 | 3.097 | -1.2 | -0.06 | 0.87464 | -0.46934 | -8.5614 | 0.97091 | 0.4418 | -16.7209 | 4.3722 | 0.42364 | 0.43239 | 0.43047 | 0.37809 | 0.44842 | 0.4432 | 0.42867
42838.412 | -713 | 22.8975 | 22.8695 | 22.8625 | 22.7953 | 22.4448 | 21.7973 | 22.7424 | 21.861 | 22.3863 | 22.4137 | 22.3977 | 22.0851 | 21.3064 | 22.2632 | 21.5821 | 21.7634 | 21.9076 | 21.0933 | 21.1906 | 21.4175 | 20.4927 | 20.6412 | 20.9399 | 21.919 | 21.6893 | 21.3184 | 20.4299 | 20.554 | 20.4739 | 22.0448 | 21.6697 | 21.1871 | 22.0056 | 21.7422 | 21.368 | 19.9409 | 20.5547 |  | 20.5855 | 20.2426 | 20.3602 | 19.0604 |  | 16.6833 | 16.7676 | 16.5855 | 16.901 | 17.183 | 17.8331 | 18.3431 | 16.0073 | 16.6061 | 16.3654 | 16.8215 | 17.8794 | 44.5507 | 47.4018 | 43.4672 | 21.3373 |  |  | 0.33996 | -0.029637 | -51.288 | 0.44154 | 0.26889 | -197.8558 | 13.7951 | -0.62922 | -0.52649 | -0.14025 | -0.067239 | 8.8288 | 9.0584 | 1.9781 | 21.8223 | 22.0359 | 22.2338 | 22.3013 | 22.1416 | 21.4908 | 20.3141 | 22.2234 | 22.39 | 22.4321 | 22.3832 | 22.0242 | 21.28 | 22.3007 | 17.2667 | 17.0276 | 16.238 | 16.1403 | 16.1877 | 17.0726 | 16.6865 | 22.4051 | 22.1702 | 21.7304 | 22.1038 | 21.8293 | 21.3425 | 21.976 | 21.5721 | 20.9498 | 20.1514 | 20.4209 | 19.9777 | 19.8295 | 0.12092 | -0.089934 | 20.7402 | 22.0997 | 22.416 | 20.1499 | 21.7144 | 22.1666 | 21.9848 | 21.7548 | 21.3277 | 21.837 | 21.5019 | 21.1042 | 20.5494 | 20.5536 | 20.5088 | 20.518 | 20.1272 |  | 20.2466 | 19.6696 | 20.1356 | 19.7243 | 20.1204 | 20.3818 |  | 20.4662 |  |  | 20.2857 | 20.3834 | 20.6095 | [5 empty] | 21.9698 | 20.3619 | 21.7127 | 22.1069 | 19.5768 | 21.2434 | 21.8906 | 19.424 | 20.0078 | 21.2128 |  | 19.7102 | 21.0101 | 18.835 | 19.725 | 20.8763 | 19.4538 | 20.1508 | 19.0267 | 20.1819 | 19.1807 | 20.3192 | 18.6684 | 20.1425 | 21.1445 | 19.4783 | 19.84 | 21.036 | 18.9265 | 19.8377 | 20.8731 | 19.0751 | 20.2959 | 19.3334 | 19.9711 | 18.9312 | 20.1556 | -0.12219 | 20.9495 | 0.048512 | 0.014738 | -27.0377 | 3.097 | -1.13 | 0.05 | 0.69627 | -0.20428 | -8.4979 | 0.78848 | 0.61644 | -16.7215 | 4.4153 | 0.42346 | 0.43246 | 0.43043 | 0.3807 | 0.44996 | 0.44286 | 0.42855
42838.412 | -712 | 22.8976 | 22.8726 | 22.8593 | 22.8018 | 22.4452 | 21.7965 | 22.7387 | 21.8651 | 22.3958 | 22.4113 | 22.3965 | 22.0841 | 21.3099 | 22.2667 | 21.5739 | 21.7619 | 21.9017 | 21.0864 | 21.1899 | 21.4033 | 20.4902 | 20.6361 | 20.935 | 21.9117 | 21.6809 | 21.3134 | 20.4266 | 20.5472 | 20.4658 | 22.0511 | 21.6652 | 21.1865 | 22.0081 | 21.746 | 21.3682 | 19.9442 | 20.5505 |  | 20.5857 | 20.2454 | 20.3625 | 19.0672 |  | 16.6964 | 16.7731 | 16.5818 | 16.912 | 17.1905 | 17.8486 | 18.3117 | 16.0144 | 16.6115 | 16.4218 | 16.8232 | 17.8746 | 44.5512 | 47.4151 | 43.4602 | 21.3381 |  |  | 0.45627 | -0.11374 | -50.9805 | 0.41065 | 0.21238 | -197.819 | 13.7866 | -0.7061 | -0.028318 | -0.14234 | -0.13303 | 8.8287 | 9.0583 | 1.9779 | 21.8211 | 22.0427 | 22.2394 | 22.3075 | 22.1489 | 21.4893 | 20.3175 | 22.2291 | 22.3938 | 22.4328 | 22.3831 | 22.0282 | 21.2702 | 22.2952 | 17.2501 | 17.0707 | 16.2112 | 16.1176 | 16.1628 | 17.0681 | 16.691 | 22.4015 | 22.1703 | 21.7267 | 22.1008 | 21.8232 | 21.3381 | 21.9641 | 21.5562 | 20.9465 | 20.146 | 20.4094 | 19.9692 | 19.8186 | 0.080815 | -0.038009 | 20.7283 | 22.0927 | 22.4082 | 20.141 | 21.7072 | 22.1552 | 21.976 | 21.7425 | 21.3165 | 21.8211 | 21.4936 | 21.0959 | 20.5394 | 20.5432 | 20.4934 | 20.5033 | 20.134 |  | 20.2594 | 19.6819 | 20.147 | 19.7332 | 20.1197 | 20.389 |  | 20.4749 |  |  | 20.2903 | 20.3803 | 20.6168 | [5 empty] | 21.9661 | 20.3586 | 21.7137 | 22.1022 | 19.5795 | 21.2444 | 21.8879 | 19.4212 | 20.0067 | 21.2144 |  | 19.7153 | 21.0115 | 18.8356 | 19.727 | 20.876 | 19.4606 | 20.1499 | 19.0312 | 20.1799 | 19.1827 | 20.3128 | 18.6686 | 20.1505 | 21.1468 | 19.4808 | 19.8423 | 21.0404 | 18.9263 | 19.8405 | 20.872 | 19.0791 | 20.2963 | 19.3356 | 19.9724 | 18.9277 | 20.162 | -0.011448 | 20.9468 | 0.048309 | 0.015529 | -27.0279 | 3.0971 | -0.91 | 0.03 | 0.80662 | -0.4002 | -8.4725 | 0.76041 | 0.54786 | -16.7204 | 4.4141 | 0.4237 | 0.4325 | 0.43016 | 0.38202 | 0.45346 | 0.44278 | 0.42867
42838.412 | -711 | 22.896 | 22.8717 | 22.8588 | 22.7968 | 22.4403 | 21.7977 | 22.75 | 21.8629 | 22.3915 | 22.4095 | 22.3963 | 22.0803 | 21.3068 | 22.2648 | 21.586 | 21.7694 | 21.9071 | 21.0927 | 21.1983 | 21.4161 | 20.5007 | 20.6469 | 20.9435 | 21.9244 | 21.6877 | 21.3229 | 20.4284 | 20.5551 | 20.4748 | 22.0396 | 21.6624 | 21.186 | 21.9996 | 21.7468 | 21.3668 | 19.9394 | 20.5375 |  | 20.5793 | 20.2387 | 20.3575 | 19.075 |  | 16.6893 | 16.7623 | 16.5721 | 16.9213 | 17.2118 | 17.8634 | 18.3035 | 16.0318 | 16.6065 | 16.466 | 16.8227 | 17.8742 | 44.5517 | 47.434 | 43.4606 | 21.3394 |  |  | 0.45955 | -0.26422 | -51.5266 | 0.10707 | 0.20844 | -197.8328 | 13.8608 | -0.6923 | -0.53097 | -0.36494 | -0.03981 | 8.8278 | 9.0576 | 1.9789 | 21.8224 | 22.0419 | 22.2434 | 22.3041 | 22.1535 | 21.4868 | 20.3197 | 22.224 | 22.3983 | 22.4295 | 22.3847 | 22.0247 | 21.2657 | 22.2949 | 17.2365 | 17.1016 | 16.1913 | 16.0919 | 16.1349 | 17.0661 | 16.6857 | 22.3917 | 22.1668 | 21.7349 | 22.1042 | 21.8288 | 21.3312 | 21.968 | 21.5591 | 20.9383 | 20.1448 | 20.4172 | 19.976 | 19.8068 | -0.15884 | -0.064257 | 20.7353 | 22.1074 | 22.4139 | 20.1449 | 21.7126 | 22.1572 | 21.9824 | 21.7506 | 21.3244 | 21.8305 | 21.5003 | 21.0991 | 20.5411 | 20.5476 | 20.5121 | 20.5084 | 20.1404 |  | 20.255 | 19.6762 | 20.1433 | 19.7327 | 20.1204 | 20.3778 |  | 20.4722 |  |  | 20.2914 | 20.3785 | 20.6167 | [5 empty] | 21.9662 | 20.3654 | 21.7127 | 22.1092 | 19.5846 | 21.2476 | 21.8874 | 19.4236 | 20.0069 | 21.2116 |  | 19.7104 | 21.0084 | 18.8319 | 19.7285 | 20.8778 | 19.4645 | 20.1462 | 19.0324 | 20.1752 | 19.1778 | 20.3054 | 18.6775 | 20.151 | 21.1445 | 19.4838 | 19.8403 | 21.0413 | 18.9232 | 19.8353 | 20.8648 | 19.0799 | 20.3002 | 19.3389 | 19.9711 | 18.9249 | 20.1611 | -0.070808 | 20.9467 | 0.048297 | 0.014564 | -27.045 | 3.097 | -0.76 | -0.56 | 0.80953 | -0.60994 | -8.5176 | 0.38826 | 0.54276 | -16.7214 | 4.4261 | 0.42338 | 0.43254 | 0.4302 | 0.38329 | 0.45506 | 0.4424 | 0.42895
42838.4121 | -710 | 22.8912 | 22.868 | 22.8528 | 22.7929 | 22.4427 | 21.7879 | 22.742 | 21.861 | 22.3897 | 22.4073 | 22.3908 | 22.0799 | 21.3024 | 22.254 | 21.5842 | 21.7633 | 21.906 | 21.0874 | 21.1929 | 21.4201 | 20.4996 | 20.641 | 20.9437 | 21.9184 | 21.6847 | 21.3226 | 20.4224 | 20.5547 | 20.4658 | 22.0468 | 21.6605 | 21.1904 | 22.003 | 21.7466 | 21.3693 | 19.9529 | 20.543 |  | 20.5839 | 20.2505 | 20.3607 | 19.0983 |  | 16.7019 | 16.7704 | 16.583 | 16.9455 | 17.2413 | 17.8775 | 18.3256 | 16.0691 | 16.6138 | 16.5787 | 16.8313 | 17.8747 | 44.5558 | 47.4514 | 43.4703 | 21.3431 |  |  | 0.4451 | -0.29117 | -51.4129 | 0.67744 | 0.25706 | -197.8236 | 13.5513 | -0.60688 | -0.4687 | 0.11676 | -0.029568 | 8.8286 | 9.0584 | 1.9784 | 21.8201 | 22.0486 | 22.2414 | 22.3083 | 22.1495 | 21.4887 | 20.3276 | 22.2313 | 22.3973 | 22.4327 | 22.3888 | 22.0275 | 21.2748 | 22.2977 | 17.255 | 17.0914 | 16.1751 | 16.0736 | 16.1086 | 17.0652 | 16.6913 | 22.3985 | 22.1712 | 21.7405 | 22.1045 | 21.8328 | 21.3389 | 21.9696 | 21.5626 | 20.9507 | 20.1491 | 20.4279 | 19.9801 | 19.8141 | 0.056043 | 0.1695 | 20.7365 | 22.103 | 22.4178 | 20.1532 | 21.7189 | 22.1594 | 21.9803 | 21.7516 | 21.3242 | 21.8374 | 21.5024 | 21.1046 | 20.5388 | 20.5623 | 20.5125 | 20.5141 | 20.1341 |  | 20.2519 | 19.6738 | 20.141 | 19.735 | 20.1203 | 20.3774 |  | 20.457 |  |  | 20.2879 | 20.3721 | 20.611 | [5 empty] | 21.9642 | 20.3603 | 21.7112 | 22.1065 | 19.5897 | 21.2456 | 21.8879 | 19.428 | 20.0125 | 21.2191 |  | 19.7216 | 21.0162 | 18.8391 | 19.743 | 20.889 | 19.4606 | 20.1522 | 19.0434 | 20.1727 | 19.1794 | 20.3151 | 18.6789 | 20.1512 | 21.15 | 19.4849 | 19.8419 | 21.0404 | 18.9244 | 19.837 | 20.8716 | 19.0765 | 20.2961 | 19.3427 | 19.9711 | 18.9321 | 20.1568 | 0.003763 | 20.9479 | 0.047516 | 0.013961 | -27.0755 | 3.097 | -0.95 | -0.04 | 0.79668 | -0.64029 | -8.5083 | 0.97666 | 0.60277 | -16.7214 | 4.3765 | 0.42345 | 0.43252 | 0.43013 | 0.38113 | 0.4575 | 0.44221 | 0.4289
42838.4121 | -709 | 22.9025 | 22.8692 | 22.863 | 22.7953 | 22.4471 | 21.7994 | 22.7484 | 21.861 | 22.4015 | 22.4058 | 22.3925 | 22.0862 | 21.3118 | 22.2642 | 21.5913 | 21.7637 | 21.9014 | 21.0933 | 21.1929 | 21.4198 | 20.4949 | 20.6431 | 20.9474 | 21.9138 | 21.6853 | 21.3282 | 20.425 | 20.5575 | 20.4682 | 22.0511 | 21.6581 | 21.1883 | 22.0079 | 21.749 | 21.3646 | 19.9433 | 20.5475 |  | 20.5826 | 20.2463 | 20.3602 | 19.1051 |  | 16.7001 | 16.7691 | 16.5849 | 16.9431 | 17.2316 | 17.8812 | 18.341 | 16.0683 | 16.6123 | 16.6284 | 16.8299 | 17.8781 | 44.5567 | 47.4698 | 43.4863 | 21.3453 |  |  | 0.43393 | -0.11637 | -52.068 | 0.62356 | 0.22224 | -197.8381 | 13.4265 | -0.49911 | -0.53486 | -0.11129 | 0.051677 | 8.8285 | 9.058 | 1.9784 | 21.8224 | 22.048 | 22.2439 | 22.3065 | 22.1457 | 21.4935 | 20.3193 | 22.2306 | 22.3993 | 22.4343 | 22.3897 | 22.0271 | 21.2758 | 22.2997 | 17.2632 | 17.0943 | 16.1626 | 16.0782 | 16.0887 | 17.0723 | 16.6909 | 22.402 | 22.1686 | 21.7336 | 22.1059 | 21.8309 | 21.3371 | 21.9684 | 21.5596 | 20.9491 | 20.1427 | 20.4216 | 19.9854 | 19.8056 | 0.048966 | 0.049673 | 20.7247 | 22.0985 | 22.4108 | 20.1485 | 21.7126 | 22.1532 | 21.9775 | 21.7441 | 21.3184 | 21.8324 | 21.4949 | 21.1049 | 20.5354 | 20.5558 | 20.5163 | 20.5164 | 20.1356 |  | 20.2501 | 19.6799 | 20.1402 | 19.7269 | 20.1137 | 20.3791 |  | 20.4638 |  |  | 20.2901 | 20.3802 | 20.6118 | [5 empty] | 21.9731 | 20.3564 | 21.7156 | 22.105 | 19.5936 | 21.25 | 21.8886 | 19.4244 | 20.0152 | 21.2239 |  | 19.7291 | 21.0151 | 18.842 | 19.7442 | 20.888 | 19.4668 | 20.1565 | 19.0494 | 20.1801 | 19.1833 | 20.3104 | 18.6863 | 20.155 | 21.1539 | 19.4749 | 19.8447 | 21.039 | 18.9224 | 19.8419 | 20.8748 | 19.0789 | 20.2977 | 19.3414 | 19.9714 | 18.9328 | 20.1596 | -0.1541 | 20.9473 | 0.047418 | 0.012916 | -27.0161 | 3.097 | -0.93 | -0.19 | 0.78662 | -0.40479 | -8.5623 | 0.93701 | 0.56046 | -16.7221 | 4.3563 | 0.42335 | 0.43233 | 0.43013 | 0.38105 | 0.45886 | 0.4417 | 0.42892
42838.4121 | -708 | 22.8948 | 22.866 | 22.8539 | 22.7964 | 22.4384 | 21.7903 | 22.7411 | 21.8545 | 22.39 | 22.4038 | 22.3867 | 22.0832 | 21.3028 | 22.2609 | 21.5857 | 21.7637 | 21.9019 | 21.0924 | 21.192 | 21.422 | 20.5004 | 20.6387 | 20.9357 | 21.9177 | 21.6831 | 21.3227 | 20.4243 | 20.554 | 20.4626 | 22.043 | 21.6629 | 21.1943 | 21.9997 | 21.748 | 21.363 | 19.9504 | 20.5298 |  | 20.5881 | 20.2413 | 20.3604 | 19.1113 |  | 16.7044 | 16.7772 | 16.5937 | 16.9483 | 17.2234 | 17.8967 | 18.358 | 16.0149 | 16.61 | 16.6442 | 16.8302 | 17.8779 | 44.5585 | 47.4801 | 43.4927 | 21.3402 |  |  | 0.31105 | -0.069721 | -52.5234 | 0.70504 | 0.18018 | -197.8808 | 13.2037 | -0.49188 | -0.093704 | 0.10648 | 0.044212 | 8.8292 | 9.0589 | 1.9783 | 21.8158 | 22.0368 | 22.2373 | 22.3035 | 22.1415 | 21.4883 | 20.3172 | 22.2235 | 22.3955 | 22.4253 | 22.3783 | 22.0168 | 21.2639 | 22.2934 | 17.2676 | 17.1465 | 16.1628 | 16.095 | 16.0911 | 17.071 | 16.6989 | 22.3984 | 22.1772 | 21.7351 | 22.0966 | 21.8229 | 21.3331 | 21.9627 | 21.5539 | 20.9469 | 20.1459 | 20.4222 | 19.9777 | 19.8136 | 0.065873 | -0.13577 | 20.731 | 22.1043 | 22.4136 | 20.1482 | 21.71 | 22.1639 | 21.9795 | 21.7499 | 21.3208 | 21.8345 | 21.4984 | 21.1038 | 20.5356 | 20.5433 | 20.5156 | 20.5264 | 20.1277 |  | 20.2524 | 19.6905 | 20.1398 | 19.7263 | 20.1168 | 20.3817 |  | 20.4635 |  |  | 20.2881 | 20.3768 | 20.6141 | [5 empty] | 21.9644 | 20.3506 | 21.7058 | 22.1079 | 19.5846 | 21.2508 | 21.8861 | 19.4192 | 20.0211 | 21.2335 |  | 19.7246 | 21.0147 | 18.8334 | 19.7476 | 20.8916 | 19.4689 | 20.1659 | 19.0504 | 20.1767 | 19.186 | 20.3114 | 18.6843 | 20.1575 | 21.1589 | 19.4733 | 19.8435 | 21.0423 | 18.9178 | 19.832 | 20.8704 | 19.076 | 20.2977 | 19.34 | 19.9747 | 18.9303 | 20.1572 | -0.11496 | 20.9473 | 0.045845 | 0.013083 | -27.0151 | 3.097 | -0.56 | -0.63 | 0.66599 | -0.31332 | -8.5998 | 0.99637 | 0.50466 | -16.7244 | 4.3201 | 0.42365 | 0.43202 | 0.43025 | 0.38041 | 0.45975 | 0.44176 | 0.4288
42838.4121 | -707 | 22.8997 | 22.866 | 22.861 | 22.7939 | 22.4358 | 21.7885 | 22.7392 | 21.8509 | 22.3915 | 22.3984 | 22.3845 | 22.0762 | 21.296 | 22.2684 | 21.5815 | 21.7645 | 21.9102 | 21.0929 | 21.1947 | 21.4145 | 20.4966 | 20.6479 | 20.9385 | 21.9228 | 21.6789 | 21.3236 | 20.426 | 20.554 | 20.4687 | 22.046 | 21.6707 | 21.1914 | 22.0072 | 21.7488 | 21.3744 | 19.9453 | 20.5307 |  | 20.5924 | 20.2471 | 20.3646 | 19.1268 |  | 16.7009 | 16.783 | 16.5911 | 16.9415 | 17.2189 | 17.8959 | 18.3625 | 15.9928 | 16.6135 | 16.6001 | 16.8246 | 17.8776 | 44.5813 | 47.5048 | 43.508 | 21.3432 |  |  | 0.51804 | -0.067093 | -52.7784 | 0.58742 | 0.21961 | -197.8282 | 12.9001 | -0.44786 | -0.055368 | -0.098914 | 0.075113 | 8.8291 | 9.0587 | 1.9788 | 21.8223 | 22.0453 | 22.2399 | 22.3076 | 22.1469 | 21.4914 | 20.3191 | 22.2358 | 22.3962 | 22.428 | 22.3802 | 22.0223 | 21.2671 | 22.2935 | 17.2522 | 17.1892 | 16.1462 | 16.0979 | 16.089 | 17.0653 | 16.6899 | 22.4039 | 22.1783 | 21.7393 | 22.1082 | 21.8258 | 21.3408 | 21.9676 | 21.568 | 20.945 | 20.147 | 20.4272 | 19.9788 | 19.8193 | 0.009449 | 0.0051664 | 20.7369 | 22.1 | 22.4145 | 20.1493 | 21.7079 | 22.1652 | 21.9799 | 21.7498 | 21.3289 | 21.8329 | 21.5056 | 21.1031 | 20.5405 | 20.5477 | 20.5159 | 20.5198 | 20.1294 |  | 20.2546 | 19.7025 | 20.1442 | 19.7288 | 20.1229 | 20.3847 |  | 20.4681 |  |  | 20.2897 | 20.3733 | 20.6134 | [5 empty] | 21.9613 | 20.354 | 21.7147 | 22.1051 | 19.5887 | 21.2509 | 21.8935 | 19.4262 | 20.0207 | 21.2318 |  | 19.7267 | 21.0205 | 18.828 | 19.7438 | 20.8854 | 19.4675 | 20.1637 | 19.0439 | 20.1838 | 19.1848 | 20.3135 | 18.6923 | 20.1562 | 21.1629 | 19.484 | 19.8487 | 21.0393 | 18.932 | 19.8357 | 20.8787 | 19.0698 | 20.3034 | 19.3357 | 19.9726 | 18.9326 | 20.1646 | -0.042055 | 20.9464 | 0.045667 | 0.012604 | -26.9768 | 3.0971 | -0.5 | -0.05 | 0.85949 | -0.30737 | -8.6207 | 0.90947 | 0.55715 | -16.7221 | 4.2702 | 0.42367 | 0.43183 | 0.43039 | 0.38145 | 0.46055 | 0.44116 | 0.42868
42838.4121 | -706 | 22.8987 | 22.8675 | 22.863 | 22.7895 | 22.442 | 21.7875 | 22.7345 | 21.8567 | 22.3913 | 22.398 | 22.3884 | 22.0792 | 21.303 | 22.2663 | 21.5809 | 21.7641 | 21.8994 | 21.0979 | 21.1978 | 21.4225 | 20.4932 | 20.6395 | 20.949 | 21.9164 | 21.6855 | 21.3245 | 20.4252 | 20.5576 | 20.4709 | 22.0488 | 21.6642 | 21.1931 | 22.0097 | 21.7499 | 21.3779 | 19.9438 | 20.5318 |  | 20.5833 | 20.2502 | 20.3697 | 19.138 |  | 16.7112 | 16.7873 | 16.5882 | 16.9446 | 17.2108 | 17.8814 | 18.3721 | 15.977 | 16.6216 | 16.6099 | 16.8303 | 17.8723 | 44.5975 | 47.52 | 43.533 | 21.3431 |  |  | 0.28279 | -0.2478 | -53.0596 | 0.40671 | 0.28664 | -197.867 | 13.0966 | -0.53394 | -0.10713 | 0.082982 | 0.010013 | 8.8283 | 9.0582 | 1.9788 | 21.8219 | 22.0533 | 22.2395 | 22.3034 | 22.1472 | 21.4884 | 20.314 | 22.2234 | 22.4035 | 22.4432 | 22.386 | 22.0229 | 21.2681 | 22.2999 | 17.264 | 17.1822 | 16.144 | 16.1022 | 16.0965 | 17.0709 | 16.6928 | 22.4071 | 22.1723 | 21.7339 | 22.1031 | 21.8251 | 21.3401 | 21.9646 | 21.5624 | 20.9394 | 20.1485 | 20.4195 | 19.9819 | 19.8184 | -0.14586 | 0.044157 | 20.7348 | 22.0976 | 22.4136 | 20.1456 | 21.7066 | 22.1603 | 21.9793 | 21.7463 | 21.3233 | 21.8306 | 21.4935 | 21.1034 | 20.5405 | 20.5412 | 20.5105 | 20.5222 | 20.1364 |  | 20.251 | 19.7041 | 20.1419 | 19.7212 | 20.1139 | 20.3782 |  | 20.4564 |  |  | 20.2796 | 20.368 | 20.6115 | [5 empty] | 21.9583 | 20.3457 | 21.7063 | 22.0967 | 19.5723 | 21.2461 | 21.8762 | 19.4279 | 20.0238 | 21.2281 |  | 19.7241 | 21.0219 | 18.8252 | 19.7387 | 20.8867 | 19.4568 | 20.1629 | 19.0432 | 20.1849 | 19.1852 | 20.3041 | 18.6957 | 20.1656 | 21.1722 | 19.4931 | 19.8528 | 21.0432 | 18.9345 | 19.8363 | 20.8872 | 19.072 | 20.3117 | 19.3466 | 19.9712 | 18.937 | 20.165 | -0.083051 | 20.9471 | 0.046662 | 0.013293 | -27.0259 | 3.097 | -0.61 | -0.23 | 0.63503 | -0.5907 | -8.6437 | 0.75677 | 0.63651 | -16.7234 | 4.3025 | 0.42336 | 0.43171 | 0.4303 | 0.38079 | 0.46114 | 0.4408 | 0.42876
42838.4121 | -705 | 22.9005 | 22.8653 | 22.8629 | 22.7862 | 22.4435 | 21.7894 | 22.7365 | 21.8532 | 22.3901 | 22.4016 | 22.3836 | 22.0777 | 21.3009 | 22.2632 | 21.5864 | 21.7569 | 21.9024 | 21.094 | 21.1925 | 21.4239 | 20.4868 | 20.6453 | 20.9385 | 21.9149 | 21.6803 | 21.3281 | 20.4223 | 20.557 | 20.4608 | 22.0511 | 21.6656 | 21.1888 | 22.0119 | 21.7504 | 21.3729 | 19.949 | 20.5256 |  | 20.5877 | 20.2548 | 20.3669 | 19.1499 |  | 16.7055 | 16.7722 | 16.5717 | 16.9271 | 17.183 | 17.8591 | 18.3794 | 15.9756 | 16.6097 | 16.6356 | 16.8215 | 17.877 | 44.6131 | 47.5511 | 43.5456 | 21.3495 |  |  | 0.41159 | -0.27671 | -54.339 | 0.19709 | 0.1631 | -197.8466 | 12.63 | -0.5024 | -0.36692 | 0.09536 | 0.040914 | 8.8289 | 9.0585 | 1.9785 | 21.8143 | 22.0368 | 22.2357 | 22.3024 | 22.1426 | 21.4842 | 20.3089 | 22.2213 | 22.3845 | 22.4238 | 22.3766 | 22.0128 | 21.2558 | 22.2889 | 17.2792 | 17.1487 | 16.1399 | 16.1141 | 16.1056 | 17.0749 | 16.6986 | 22.4032 | 22.1702 | 21.7358 | 22.1068 | 21.8307 | 21.3353 | 21.9645 | 21.5589 | 20.9449 | 20.1501 | 20.4221 | 19.9825 | 19.8239 | 0.080028 | -0.034966 | 20.7373 | 22.1031 | 22.4163 | 20.1472 | 21.7135 | 22.1643 | 21.9802 | 21.7559 | 21.3228 | 21.8336 | 21.4949 | 21.1096 | 20.5366 | 20.5504 | 20.5152 | 20.5252 | 20.1433 |  | 20.25 | 19.7129 | 20.1387 | 19.7189 | 20.1126 | 20.3797 |  | 20.4558 |  |  | 20.2865 | 20.3702 | 20.6181 | [5 empty] | 21.9704 | 20.3538 | 21.707 | 22.1017 | 19.5786 | 21.2469 | 21.8908 | 19.4312 | 20.0203 | 21.2236 |  | 19.7227 | 21.0202 | 18.829 | 19.7458 | 20.8908 | 19.4577 | 20.1588 | 19.0375 | 20.1846 | 19.1811 | 20.3105 | 18.6917 | 20.1695 | 21.1745 | 19.4881 | 19.8547 | 21.0493 | 18.9388 | 19.8367 | 20.884 | 19.0755 | 20.3092 | 19.3468 | 19.9758 | 18.9347 | 20.1553 | -0.034821 | 20.9471 | 0.047799 | 0.014687 | -26.9878 | 3.0971 | -0.69 | 0.04 | 0.7661 | -0.6242 | -8.7471 | 0.52679 | 0.48011 | -16.7219 | 4.225 | 0.42313 | 0.43136 | 0.43032 | 0.37957 | 0.46226 | 0.44064 | 0.42866
42838.4121 | -704 | 22.9047 | 22.8733 | 22.8652 | 22.7916 | 22.4439 | 21.7973 | 22.739 | 21.8521 | 22.3897 | 22.4073 | 22.3848 | 22.0766 | 21.3018 | 22.2639 | 21.5853 | 21.7643 | 21.9023 | 21.0917 | 21.1931 | 21.4272 | 20.5031 | 20.6485 | 20.9496 | 21.9215 | 21.6925 | 21.3222 | 20.4286 | 20.553 | 20.4742 | 22.0407 | 21.6534 | 21.1855 | 22.0003 | 21.7429 | 21.3647 | 19.9424 | 20.5081 |  | 20.5865 | 20.2403 | 20.3636 | 19.1581 |  | 16.71 | 16.7758 | 16.5729 | 16.9266 | 17.1664 | 17.8459 | 18.3729 | 15.9943 | 16.6098 | 16.73 | 16.8236 | 17.8738 | 44.624 | 47.5732 | 43.553 | 21.3425 |  |  | 0.40567 | -0.2984 | -54.5033 | 0.51053 | 0.14864 | -197.8177 | 12.7457 | -0.6877 | -0.27585 | 0.080255 | -0.12279 | 8.8292 | 9.0588 | 1.9781 | 21.8208 | 22.0478 | 22.2413 | 22.3007 | 22.1529 | 21.4957 | 20.3168 | 22.2243 | 22.4047 | 22.4303 | 22.3866 | 22.0285 | 21.2698 | 22.3002 | 17.2765 | 17.1078 | 16.1426 | 16.1178 | 16.1099 | 17.0642 | 16.6986 | 22.4029 | 22.1706 | 21.7345 | 22.1029 | 21.8234 | 21.3329 | 21.9641 | 21.5543 | 20.9409 | 20.1418 | 20.4209 | 19.9782 | 19.8008 | -0.028691 | -0.15574 | 20.7385 | 22.1033 | 22.4126 | 20.1474 | 21.7149 | 22.159 | 21.9702 | 21.7519 | 21.3232 | 21.8382 | 21.4991 | 21.1041 | 20.5394 | 20.5593 | 20.5099 | 20.5226 | 20.1518 |  | 20.2533 | 19.7226 | 20.1366 | 19.7323 | 20.1184 | 20.3818 |  | 20.4629 |  |  | 20.2813 | 20.3719 | 20.6129 | [5 empty] | 21.9555 | 20.35 | 21.7011 | 22.098 | 19.5796 | 21.2374 | 21.8846 | 19.425 | 20.017 | 21.225 |  | 19.7252 | 21.0251 | 18.818 | 19.7417 | 20.8848 | 19.4531 | 20.1714 | 19.0339 | 20.1773 | 19.1731 | 20.3055 | 18.6876 | 20.1577 | 21.1662 | 19.4903 | 19.8451 | 21.0503 | 18.9386 | 19.8356 | 20.8755 | 19.0629 | 20.2988 | 19.3404 | 19.9824 | 18.9299 | 20.1521 | -0.10383 | 20.9477 | 0.048358 | 0.015616 | -27.0881 | 3.0971 | -0.76 | -0.06 | 0.76059 | -0.6482 | -8.7604 | 0.84786 | 0.45833 | -16.7203 | 4.2442 | 0.42301 | 0.43102 | 0.43014 | 0.37862 | 0.46196 | 0.4402 | 0.42902
42838.4121 | -703 | 22.8989 | 22.8737 | 22.8621 | 22.7952 | 22.4407 | 21.7848 | 22.7447 | 21.8503 | 22.3876 | 22.4121 | 22.4017 | 22.0696 | 21.3033 | 22.265 | 21.5907 | 21.7707 | 21.9041 | 21.0918 | 21.1934 | 21.4122 | 20.4958 | 20.6512 | 20.95 | 21.9273 | 21.6884 | 21.3214 | 20.43 | 20.5529 | 20.4778 | 22.0424 | 21.6574 | 21.1919 | 22 | 21.7386 | 21.3622 | 19.9385 | 20.5071 |  | 20.5808 | 20.2394 | 20.3602 | 19.1781 |  | 16.7213 | 16.785 | 16.5765 | 16.926 | 17.1699 | 17.8708 | 18.3769 | 16.0135 | 16.6169 | 16.7512 | 16.833 | 17.8675 | 44.6132 | 47.6004 | 43.5764 | 21.3393 |  |  | 0.51278 | -0.010581 | -55.1492 | 0.20169 | 0.2748 | -197.7888 | 12.8042 | -0.44392 | -0.21747 | -0.0040848 | -0.074704 | 8.8287 | 9.0587 | 1.9776 | 21.8214 | 22.0492 | 22.2386 | 22.3134 | 22.153 | 21.4937 | 20.3226 | 22.2247 | 22.399 | 22.4325 | 22.3823 | 22.0249 | 21.2716 | 22.2982 | 17.2896 | 17.0872 | 16.1149 | 16.1004 | 16.1066 | 17.061 | 16.6906 | 22.407 | 22.1665 | 21.7367 | 22.1001 | 21.8285 | 21.3329 | 21.9652 | 21.549 | 20.9453 | 20.1443 | 20.4211 | 19.9772 | 19.7927 | -0.01316 | -0.14148 | 20.7442 | 22.1017 | 22.4198 | 20.1472 | 21.7169 | 22.1604 | 21.9681 | 21.7575 | 21.3216 | 21.8328 | 21.4982 | 21.0993 | 20.5384 | 20.5472 | 20.5091 | 20.5272 | 20.1355 |  | 20.2484 | 19.724 | 20.1369 | 19.735 | 20.1164 | 20.3838 |  | 20.4574 |  |  | 20.2997 | 20.3761 | 20.6143 | [5 empty] | 21.9673 | 20.3516 | 21.7037 | 22.0975 | 19.5804 | 21.2438 | 21.8784 | 19.4186 | 20.0172 | 21.2212 |  | 19.7198 | 21.0153 | 18.8221 | 19.7313 | 20.8779 | 19.4522 | 20.1659 | 19.0385 | 20.1828 | 19.1816 | 20.3014 | 18.6953 | 20.1453 | 21.1615 | 19.4778 | 19.8507 | 21.0356 | 18.93 | 19.8339 | 20.8636 | 19.0582 | 20.2996 | 19.3382 | 19.982 | 18.9298 | 20.1464 | 0.092432 | 20.948 | 0.048364 | 0.01542 | -27.0334 | 3.0971 | -0.87 | -0.16 | 0.85513 | -0.12206 | -8.8123 | 0.53292 | 0.62322 | -16.7198 | 4.2541 | 0.42329 | 0.43099 | 0.43 | 0.3768 | 0.46411 | 0.43951 | 0.42933
42838.4122 | -702 | 22.9021 | 22.8737 | 22.8686 | 22.7974 | 22.4437 | 21.7917 | 22.7389 | 21.8611 | 22.3964 | 22.4158 | 22.4031 | 22.0855 | 21.3092 | 22.2737 | 21.5932 | 21.7676 | 21.9073 | 21.0959 | 21.1998 | 21.4227 | 20.5004 | 20.6424 | 20.9453 | 21.9188 | 21.6822 | 21.325 | 20.4292 | 20.5564 | 20.4836 | 22.0576 | 21.6722 | 21.1948 | 22.0129 | 21.7567 | 21.3788 | 19.9513 | 20.5036 |  | 20.589 | 20.2534 | 20.3674 | 19.1876 |  | 16.7219 | 16.7794 | 16.5665 | 16.9135 | 17.1686 | 17.8846 | 18.3737 | 16.0161 | 16.6086 | 16.7261 | 16.8237 | 17.8709 | 44.6065 | 47.6343 | 43.5909 | 21.3385 |  |  | 0.49767 | -0.28394 | -55.3234 | 0.003242 | 0.21764 | -197.8985 | 12.8377 | -0.57665 | -0.256 | 0.14236 | -0.094668 | 8.8291 | 9.0586 | 1.9788 | 21.8111 | 22.036 | 22.2304 | 22.3092 | 22.14 | 21.4854 | 20.3149 | 22.221 | 22.3867 | 22.4257 | 22.3806 | 22.0222 | 21.2638 | 22.2865 | 17.3029 | 17.1353 | 16.0817 | 16.0581 | 16.0945 | 17.0633 | 16.6977 | 22.407 | 22.1707 | 21.7394 | 22.1022 | 21.8315 | 21.3416 | 21.9707 | 21.5565 | 20.9488 | 20.1489 | 20.4285 | 19.9911 | 19.7967 | -0.010604 | -0.0035828 | 20.7465 | 22.1016 | 22.4192 | 20.1508 | 21.7198 | 22.1591 | 21.9729 | 21.751 | 21.3227 | 21.8316 | 21.5054 | 21.1014 | 20.5381 | 20.545 | 20.5155 | 20.5301 | 20.1299 |  | 20.256 | 19.7369 | 20.1445 | 19.7342 | 20.1149 | 20.3863 |  | 20.4619 |  |  | 20.2962 | 20.3795 | 20.616 | [5 empty] | 21.9604 | 20.3674 | 21.7047 | 22.0973 | 19.5792 | 21.2401 | 21.8823 | 19.4234 | 20.0297 | 21.2348 |  | 19.7276 | 21.0226 | 18.8244 | 19.7452 | 20.8821 | 19.4512 | 20.1709 | 19.0348 | 20.1819 | 19.1843 | 20.3082 | 18.7007 | 20.151 | 21.1636 | 19.4833 | 19.852 | 21.0438 | 18.9363 | 19.8298 | 20.8758 | 19.0599 | 20.2941 | 19.3391 | 19.9757 | 18.9308 | 20.1541 | -0.18229 | 20.9478 | 0.048198 | 0.014629 | -26.999 | 3.0971 | -1.08 | 0.12 | 0.84244 | -0.63231 | -8.8261 | 0.067565 | 0.55463 | -16.7248 | 4.2597 | 0.42371 | 0.43089 | 0.42997 | 0.3756 | 0.46863 | 0.43967 | 0.42937
42838.4122 | -701 | 22.8963 | 22.8682 | 22.8541 | 22.7916 | 22.4404 | 21.7893 | 22.7386 | 21.8527 | 22.3894 | 22.4085 | 22.3934 | 22.0823 | 21.2998 | 22.2637 | 21.5895 | 21.7662 | 21.9087 | 21.0922 | 21.1923 | 21.4204 | 20.4947 | 20.6449 | 20.9453 | 21.9246 | 21.6871 | 21.3239 | 20.4254 | 20.552 | 20.4821 | 22.0552 | 21.6653 | 21.2 | 22.0167 | 21.7608 | 21.381 | 19.9499 | 20.5037 |  | 20.5886 | 20.26 | 20.374 | 19.1646 |  | 16.7141 | 16.7763 | 16.5617 | 16.9139 | 17.1831 | 17.8876 | 18.3893 | 15.9987 | 16.607 | 16.7401 | 16.8241 | 17.8775 | 44.6045 | 47.6678 | 43.5965 | 21.3492 |  |  | 0.34916 | -0.026349 | -54.9725 | 0.44219 | 0.35694 | -197.8374 | 13.0039 | -0.44523 | -0.062957 | -0.059472 | -0.079912 | 8.8282 | 9.0577 | 1.9784 | 21.814 | 22.0375 | 22.2267 | 22.3053 | 22.1402 | 21.4876 | 20.317 | 22.222 | 22.3884 | 22.429 | 22.3839 | 22.0203 | 21.2633 | 22.2912 | 17.2894 | 17.1115 | 16.0637 | 16.0389 | 16.0676 | 17.0586 | 16.6946 | 22.4041 | 22.1741 | 21.7434 | 22.1063 | 21.827 | 21.3381 | 21.9697 | 21.5683 | 20.9478 | 20.1515 | 20.4281 | 19.9936 | 19.7993 | 0.08455 | 0.072307 | 20.7503 | 22.1051 | 22.4172 | 20.1501 | 21.7206 | 22.166 | 21.9803 | 21.7483 | 21.3266 | 21.834 | 21.5071 | 21.1062 | 20.5409 | 20.5518 | 20.5208 | 20.5283 | 20.1203 |  | 20.2583 | 19.7567 | 20.1495 | 19.7398 | 20.1218 | 20.3874 |  | 20.4739 |  |  | 20.2946 | 20.3854 | 20.6061 | [5 empty] | 21.9604 | 20.3673 | 21.7053 | 22.1058 | 19.5684 | 21.2394 | 21.8867 | 19.415 | 20.0169 | 21.2313 |  | 19.7241 | 21.0142 | 18.8344 | 19.7403 | 20.8867 | 19.4467 | 20.1713 | 19.0318 | 20.1935 | 19.1756 | 20.3043 | 18.7017 | 20.1483 | 21.1624 | 19.4852 | 19.852 | 21.0453 | 18.9379 | 19.8259 | 20.8783 | 19.0714 | 20.3003 | 19.3474 | 19.9857 | 18.9343 | 20.1629 | 0.024539 | 20.948 | 0.04818 | 0.01415 | -27.0456 | 3.0971 | -0.82 | 0.08 | 0.70563 | -0.19262 | -8.798 | 0.78907 | 0.7103 | -16.7223 | 4.2873 | 0.42405 | 0.4305 | 0.43005 | 0.37654 | 0.47028 | 0.44027 | 0.42939
42838.4122 | -700 | 22.9009 | 22.8722 | 22.8591 | 22.7916 | 22.4403 | 21.7899 | 22.7383 | 21.8526 | 22.3908 | 22.4069 | 22.3984 | 22.0774 | 21.2988 | 22.2646 | 21.5883 | 21.7738 | 21.912 | 21.0987 | 21.1949 | 21.421 | 20.5 | 20.6499 | 20.9454 | 21.926 | 21.6919 | 21.3305 | 20.4379 | 20.5616 | 20.4947 | 22.0475 | 21.6594 | 21.1922 | 22.0119 | 21.7501 | 21.3639 | 19.9389 | 20.4906 |  | 20.5871 | 20.2507 | 20.3679 | 19.1472 |  | 16.7204 | 16.7712 | 16.5626 | 16.9107 | 17.1763 | 17.8814 | 18.4071 | 15.9965 | 16.6052 | 16.6786 | 16.8271 | 17.8792 | 44.6002 | 47.7083 | 43.605 | 21.3465 |  |  | 0.36164 | -0.007949 | -54.4619 | 0.49673 | 0.4312 | -197.8532 | 12.6438 | -0.32629 | 0.0004826 | 0.25565 | 0.05619 | 8.8286 | 9.0583 | 1.9781 | 21.8234 | 22.047 | 22.2394 | 22.3076 | 22.1512 | 21.4988 | 20.323 | 22.2285 | 22.3977 | 22.4296 | 22.3917 | 22.0272 | 21.272 | 22.2904 | 17.2724 | 17.0841 | 16.0634 | 16.0381 | 16.0616 | 17.0583 | 16.6985 | 22.4016 | 22.163 | 21.7329 | 22.1043 | 21.8264 | 21.3339 | 21.9549 | 21.5594 | 20.9393 | 20.1407 | 20.4208 | 19.9824 | 19.7767 | -0.010014 | 0.13926 | 20.7535 | 22.1085 | 22.4144 | 20.1515 | 21.7189 | 22.1659 | 21.9792 | 21.745 | 21.3217 | 21.8341 | 21.5054 | 21.1033 | 20.5349 | 20.554 | 20.5206 | 20.5263 | 20.117 |  | 20.2554 | 19.7528 | 20.14 | 19.7335 | 20.1104 | 20.3859 |  | 20.4617 |  |  | 20.2848 | 20.384 | 20.5951 | [5 empty] | 21.963 | 20.36 | 21.7071 | 22.1006 | 19.5663 | 21.2371 | 21.8855 | 19.4194 | 20.0127 | 21.228 |  | 19.7202 | 21.02 | 18.8314 | 19.7461 | 20.8823 | 19.4456 | 20.1712 | 19.035 | 20.191 | 19.1795 | 20.303 | 18.6941 | 20.1431 | 21.1554 | 19.4762 | 19.8467 | 21.0357 | 18.9312 | 19.8247 | 20.8769 | 19.0643 | 20.2985 | 19.3424 | 19.9811 | 18.9276 | 20.1593 | -0.15521 | 20.9472 | 0.047952 | 0.013743 | -26.893 | 3.0971 | -0.82 | -0.06 | 0.71815 | -0.10579 | -8.757 | 0.83631 | 0.78069 | -16.7228 | 4.2274 | 0.42404 | 0.43029 | 0.42984 | 0.37839 | 0.47077 | 0.44038 | 0.42965
42838.4122 | -699 | 22.9168 | 22.887 | 22.8714 | 22.8042 | 22.4542 | 21.799 | 22.7503 | 21.862 | 22.4026 | 22.4227 | 22.3999 | 22.0923 | 21.3173 | 22.2732 | 21.5851 | 21.7678 | 21.9103 | 21.0963 | 21.1886 | 21.4168 | 20.4987 | 20.6497 | 20.9412 | 21.9204 | 21.687 | 21.3277 | 20.43 | 20.5522 | 20.4972 | 22.0524 | 21.66 | 21.1935 | 22.0116 | 21.7418 | 21.37 | 19.941 | 20.4765 |  | 20.5837 | 20.2499 | 20.3721 | 19.1394 |  | 16.7091 | 16.7722 | 16.5509 | 16.9117 | 17.1764 | 17.8638 | 18.3966 | 15.9924 | 16.6045 | 16.6474 | 16.8295 | 17.8815 | 44.6081 | 47.7578 | 43.6049 | 21.3442 |  |  | 0.36624 | -0.11834 | -54.7891 | 0.39291 | 0.22026 | -197.8236 | 12.8521 | -0.12784 | 0.046019 | 0.10858 | 0.041434 | 8.8296 | 9.0593 | 1.9777 | 21.8189 | 22.047 | 22.2435 | 22.3057 | 22.1466 | 21.4901 | 20.3161 | 22.217 | 22.396 | 22.4237 | 22.3827 | 22.0186 | 21.2728 | 22.2936 | 17.275 | 17.0487 | 16.0709 | 16.0512 | 16.064 | 17.0637 | 16.7081 | 22.4098 | 22.1726 | 21.7435 | 22.1052 | 21.8347 | 21.3463 | 21.9646 | 21.5575 | 20.9426 | 20.1504 | 20.4279 | 19.9826 | 19.7773 | -0.12208 | 0.10997 | 20.7573 | 22.1039 | 22.416 | 20.1533 | 21.7145 | 22.1658 | 21.9748 | 21.7446 | 21.3195 | 21.826 | 21.5037 | 21.1001 | 20.5295 | 20.5565 | 20.5191 | 20.5299 | 20.1239 |  | 20.249 | 19.7723 | 20.144 | 19.7247 | 20.1202 | 20.3828 |  | 20.4652 |  |  | 20.2837 | 20.3866 | 20.6043 | [5 empty] | 21.971 | 20.3664 | 21.7138 | 22.1004 | 19.5691 | 21.2463 | 21.8875 | 19.4141 | 20.0162 | 21.228 |  | 19.7238 | 21.0219 | 18.8314 | 19.7476 | 20.8834 | 19.4484 | 20.1669 | 19.0431 | 20.1987 | 19.1796 | 20.3027 | 18.7066 | 20.1463 | 21.1606 | 19.4769 | 19.8528 | 21.0392 | 18.95 | 19.8353 | 20.8821 | 19.08 | 20.3027 | 19.3459 | 19.9901 | 18.9377 | 20.1616 | -0.086205 | 20.9488 | 0.047977 | 0.012183 | -26.9702 | 3.0971 | -0.79 | 0.03 | 0.72271 | -0.40821 | -8.7832 | 0.7438 | 0.55795 | -16.721 | 4.262 | 0.42364 | 0.42989 | 0.43041 | 0.37873 | 0.47105 | 0.44067 | 0.42996
42838.4122 | -698 | 22.9032 | 22.8743 | 22.8614 | 22.796 | 22.438 | 21.7905 | 22.7406 | 21.8531 | 22.3938 | 22.3981 | 22.3892 | 22.0796 | 21.3045 | 22.2613 | 21.5902 | 21.7713 | 21.9077 | 21.0937 | 21.1931 | 21.421 | 20.5042 | 20.6523 | 20.945 | 21.9235 | 21.6867 | 21.3283 | 20.4293 | 20.5554 | 20.4968 | 22.0517 | 21.6599 | 21.1964 | 22.0158 | 21.7506 | 21.3692 | 19.9431 | 20.4747 |  | 20.5861 | 20.2518 | 20.3733 | 19.1358 |  | 16.7182 | 16.771 | 16.5586 | 16.9036 | 17.1578 | 17.833 | 18.3541 | 15.9033 | 16.6069 | 16.6306 | 16.8342 | 17.8777 | 44.6025 | 47.8106 | 43.6141 | 21.3501 |  |  | 0.45167 | -0.34308 | -54.9784 | 0.28515 | 0.16572 | -197.865 | 13.1524 | -0.21195 | -0.066849 | 0.087808 | -0.10335 | 8.8287 | 9.0582 | 1.9785 | 21.8224 | 22.0387 | 22.245 | 22.312 | 22.1481 | 21.4978 | 20.3229 | 22.2198 | 22.3884 | 22.422 | 22.3958 | 22.0208 | 21.2709 | 22.2927 | 17.2863 | 17.0155 | 16.0911 | 16.0684 | 16.0763 | 17.0665 | 16.7064 | 22.4045 | 22.1754 | 21.7358 | 22.0991 | 21.8294 | 21.3403 | 21.9556 | 21.5558 | 20.9375 | 20.1502 | 20.4247 | 19.9832 | 19.7673 | -0.17378 | -0.21413 | 20.7491 | 22.101 | 22.4201 | 20.1462 | 21.7124 | 22.1689 | 21.9788 | 21.7464 | 21.3266 | 21.8258 | 21.4989 | 21.1012 | 20.5307 | 20.5547 | 20.5166 | 20.5319 | 20.1314 |  | 20.256 | 19.7755 | 20.1476 | 19.7282 | 20.1269 | 20.3897 |  | 20.4692 |  |  | 20.2735 | 20.3886 | 20.6021 | [5 empty] | 21.9684 | 20.365 | 21.7132 | 22.102 | 19.5674 | 21.2469 | 21.8871 | 19.416 | 20.0256 | 21.227 |  | 19.7299 | 21.0237 | 18.838 | 19.7532 | 20.8867 | 19.4511 | 20.1723 | 19.0501 | 20.2012 | 19.1841 | 20.3153 | 18.7063 | 20.1402 | 21.1575 | 19.4748 | 19.8528 | 21.0413 | 18.9449 | 19.8332 | 20.8809 | 19.0797 | 20.2935 | 19.3412 | 19.9862 | 18.9374 | 20.1603 | 0.056445 | 20.9487 | 0.046767 | 0.013054 | -27.0088 | 3.0971 | -0.82 | -0.1 | 0.80258 | -0.69503 | -8.7984 | 0.63364 | 0.48394 | -16.7219 | 4.3113 | 0.42366 | 0.42992 | 0.43054 | 0.3778 | 0.4686 | 0.44084 | 0.43023
42838.4122 | -697 | 22.9071 | 22.8767 | 22.863 | 22.8007 | 22.4405 | 21.7946 | 22.7428 | 21.8581 | 22.3961 | 22.408 | 22.3965 | 22.0774 | 21.3081 | 22.2651 | 21.5869 | 21.7699 | 21.9052 | 21.0894 | 21.1956 | 21.416 | 20.5017 | 20.6465 | 20.9427 | 21.9153 | 21.6846 | 21.3249 | 20.427 | 20.5492 | 20.5007 | 22.0499 | 21.6657 | 21.1958 | 22.016 | 21.752 | 21.3673 | 19.9452 | 20.4823 |  | 20.5811 | 20.2479 | 20.3733 | 19.1336 |  | 16.7225 | 16.7705 | 16.5599 | 16.9005 | 17.1528 | 17.8182 | 18.3277 | 15.8189 | 16.6176 | 16.6455 | 16.8342 | 17.875 | 44.5975 | 47.8482 | 43.6208 | 21.3447 |  |  | 0.25651 | -0.28723 | -55.2281 | 0.43562 | 0.20778 | -197.8217 | 12.5426 | -0.45771 | 0.015272 | 0.069765 | -0.065503 | 8.8287 | 9.0583 | 1.9788 | 21.827 | 22.0504 | 22.2391 | 22.3048 | 22.1506 | 21.4903 | 20.3216 | 22.229 | 22.3956 | 22.428 | 22.3818 | 22.025 | 21.2689 | 22.2873 | 17.2983 | 16.9897 | 16.085 | 16.0673 | 16.0824 | 17.058 | 16.6998 | 22.4123 | 22.1818 | 21.7442 | 22.1017 | 21.8351 | 21.3408 | 21.9664 | 21.5601 | 20.9442 | 20.153 | 20.4366 | 19.993 | 19.78 | 0.0043374 | 0.062226 | 20.746 | 22.108 | 22.4231 | 20.1447 | 21.7165 | 22.174 | 21.9798 | 21.7496 | 21.3268 | 21.8349 | 21.4979 | 21.1098 | 20.5353 | 20.5553 | 20.521 | 20.5288 | 20.1344 |  | 20.2659 | 19.7929 | 20.1492 | 19.7336 | 20.1305 | 20.3897 |  | 20.4716 |  |  | 20.2667 | 20.3851 | 20.5985 | [5 empty] | 21.9647 | 20.3627 | 21.7081 | 22.0958 | 19.5629 | 21.2373 | 21.8846 | 19.4103 | 20.0217 | 21.223 |  | 19.7262 | 21.0116 | 18.8362 | 19.747 | 20.8844 | 19.446 | 20.1671 | 19.0383 | 20.1993 | 19.1809 | 20.3142 | 18.7042 | 20.1408 | 21.1592 | 19.466 | 19.8544 | 21.0381 | 18.9415 | 19.8317 | 20.8769 | 19.0851 | 20.2938 | 19.3397 | 19.9867 | 18.9371 | 20.159 | -0.18155 | 20.949 | 0.046754 | 0.012161 | -27.0579 | 3.0972 | -1.15 | 0.06 | 0.60483 | -0.63594 | -8.8183 | 0.78318 | 0.54187 | -16.7196 | 4.21 | 0.42391 | 0.42949 | 0.43051 | 0.37548 | 0.46851 | 0.44097 | 0.42997
42838.4122 | -696 | 22.9047 | 22.8733 | 22.8633 | 22.797 | 22.4399 | 21.7976 | 22.7345 | 21.8571 | 22.3946 | 22.4032 | 22.3974 | 22.0755 | 21.309 | 22.2613 | 21.5841 | 21.7643 | 21.9019 | 21.0813 | 21.1926 | 21.4123 | 20.4934 | 20.6399 | 20.9377 | 21.9112 | 21.6814 | 21.3213 | 20.4173 | 20.5421 | 20.5066 | 22.054 | 21.6572 | 21.1877 | 22.0095 | 21.7479 | 21.3669 | 19.9371 | 20.4713 |  | 20.5771 | 20.2441 | 20.3695 | 19.1246 |  | 16.7355 | 16.7795 | 16.5676 | 16.8962 | 17.1523 | 17.8118 | 18.3234 | 15.7604 | 16.6313 | 16.6381 | 16.8494 | 17.8805 | 44.6052 | 47.9075 | 43.6246 | 21.3404 |  |  | 0.19868 | -0.15383 | -55.7564 | 0.062382 | 0.37206 | -197.8342 | 12.4007 | -0.38017 | -0.26612 | 0.039344 | -0.14796 | 8.8286 | 9.0584 | 1.9785 | 21.8205 | 22.0434 | 22.2417 | 22.3078 | 22.1451 | 21.4862 | 20.3148 | 22.2191 | 22.3929 | 22.4349 | 22.3853 | 22.0238 | 21.2685 | 22.2876 | 17.3195 | 17.0153 | 16.106 | 16.0886 | 16.1121 | 17.0584 | 16.7127 | 22.4109 | 22.1788 | 21.7381 | 22.1031 | 21.83 | 21.3341 | 21.9712 | 21.5578 | 20.9447 | 20.1491 | 20.4296 | 19.9848 | 19.7811 | -0.0021504 | -0.10876 | 20.7484 | 22.1057 | 22.4202 | 20.1499 | 21.7117 | 22.178 | 21.979 | 21.7514 | 21.3233 | 21.8375 | 21.4978 | 21.1081 | 20.5352 | 20.5617 | 20.5205 | 20.5259 | 20.1388 |  | 20.2608 | 19.8078 | 20.144 | 19.7402 | 20.1279 | 20.393 |  | 20.4666 |  |  | 20.2649 | 20.3783 | 20.6038 | [5 empty] | 21.9682 | 20.3709 | 21.7156 | 22.1046 | 19.5663 | 21.2423 | 21.8882 | 19.4021 | 20.0164 | 21.2159 |  | 19.7259 | 21.0086 | 18.8299 | 19.74 | 20.8782 | 19.4446 | 20.161 | 19.0379 | 20.1979 | 19.1786 | 20.3002 | 18.7032 | 20.1426 | 21.1572 | 19.4608 | 19.8538 | 21.0422 | 18.9383 | 19.8294 | 20.8736 | 19.0853 | 20.296 | 19.3324 | 19.9915 | 18.9445 | 20.1666 | -0.08806 | 20.9478 | 0.047707 | 0.011733 | -27.0719 | 3.0972 | -1.29 | 0 | 0.53231 | -0.46541 | -8.8605 | 0.29638 | 0.72509 | -16.72 | 4.1861 | 0.42362 | 0.4289 | 0.43024 | 0.37317 | 0.46768 | 0.44095 | 0.42981
42838.4122 | -695 | 22.9082 | 22.8791 | 22.8681 | 22.8039 | 22.4488 | 21.8077 | 22.7453 | 21.8692 | 22.4045 | 22.4132 | 22.3985 | 22.0869 | 21.3137 | 22.2669 | 21.5911 | 21.7684 | 21.9105 | 21.0921 | 21.1963 | 21.4177 | 20.4994 | 20.6465 | 20.9431 | 21.9217 | 21.6824 | 21.3272 | 20.4294 | 20.5519 | 20.5188 | 22.0487 | 21.6618 | 21.1908 | 22.0093 | 21.7459 | 21.3739 | 19.9445 | 20.4688 |  | 20.5803 | 20.2553 | 20.3675 | 19.139 |  | 16.7351 | 16.7706 | 16.5586 | 16.8887 | 17.1376 | 17.7935 | 18.3443 | 15.7681 | 16.6188 | 16.611 | 16.8445 | 17.8773 | 44.6291 | 47.964 | 43.6498 | 21.3502 |  |  | 0.37807 | -0.119 | -54.8759 | 0.5907 | 0.21172 | -197.8788 | 12.835 | -0.40909 | -0.34065 | 0.30411 | -0.010125 | 8.8278 | 9.0575 | 1.978 | 21.8182 | 22.0491 | 22.2312 | 22.3055 | 22.143 | 21.4902 | 20.3135 | 22.222 | 22.3967 | 22.4306 | 22.3774 | 22.024 | 21.2713 | 22.2904 | 17.34 | 17.038 | 16.1335 | 16.0983 | 16.1164 | 17.0634 | 16.7145 | 22.3995 | 22.174 | 21.7343 | 22.0943 | 21.8255 | 21.3344 | 21.9641 | 21.5582 | 20.9415 | 20.1486 | 20.4259 | 19.983 | 19.7685 | -0.017092 | -0.14833 | 20.7568 | 22.1044 | 22.4202 | 20.1512 | 21.7075 | 22.1785 | 21.9834 | 21.7538 | 21.3298 | 21.8359 | 21.5015 | 21.1018 | 20.5374 | 20.5588 | 20.5216 | 20.5247 | 20.131 |  | 20.2483 | 19.8076 | 20.1458 | 19.7352 | 20.1175 | 20.3803 |  | 20.4561 |  |  | 20.2606 | 20.3765 | 20.603 | [5 empty] | 21.9699 | 20.3722 | 21.7176 | 22.1081 | 19.5625 | 21.249 | 21.887 | 19.4047 | 20.0133 | 21.2237 |  | 19.7275 | 21.0144 | 18.8315 | 19.744 | 20.8723 | 19.4452 | 20.1585 | 19.0429 | 20.1961 | 19.1853 | 20.294 | 18.7025 | 20.1425 | 21.1594 | 19.4526 | 19.8514 | 21.037 | 18.9343 | 19.8269 | 20.8716 | 19.0835 | 20.3041 | 19.3344 | 19.9904 | 18.9412 | 20.1601 | -0.098447 | 20.9484 | 0.048487 | 0.014767 | -26.9814 | 3.0972 | -1.19 | -0.23 | 0.73431 | -0.40934 | -8.7902 | 0.91199 | 0.54696 | -16.7213 | 4.2586 | 0.42342 | 0.42897 | 0.43003 | 0.37148 | 0.46484 | 0.4408 | 0.43014
42838.4122 | -694 | 22.9066 | 22.8713 | 22.8665 | 22.794 | 22.4458 | 21.7894 | 22.7374 | 21.8551 | 22.3885 | 22.4101 | 22.3911 | 22.0807 | 21.3021 | 22.2686 | 21.5968 | 21.7717 | 21.9136 | 21.1036 | 21.1989 | 21.4244 | 20.4955 | 20.6529 | 20.9468 | 21.9206 | 21.6828 | 21.3307 | 20.4374 | 20.556 | 20.5236 | 22.0467 | 21.6589 | 21.1889 | 22.0009 | 21.7438 | 21.3651 | 19.942 | 20.4705 |  | 20.58 | 20.2477 | 20.364 | 19.1365 |  | 16.7418 | 16.7702 | 16.5558 | 16.8715 | 17.1228 | 17.7902 | 18.3691 | 15.7907 | 16.6273 | 16.5614 | 16.8518 | 17.8793 | 44.6416 | 48.0184 | 43.6624 | 21.3458 |  |  | 0.36953 | -0.10849 | -55.211 | 0.61765 | 0.20121 | -197.865 | 12.6537 | -0.24415 | -0.28986 | -0.022128 | 0.076328 | 8.829 | 9.0592 | 1.9779 | 21.822 | 22.0489 | 22.24 | 22.3048 | 22.1486 | 21.491 | 20.3197 | 22.2256 | 22.4017 | 22.4294 | 22.3786 | 22.0221 | 21.2707 | 22.2968 | 17.3375 | 17.0666 | 16.16 | 16.1091 | 16.1204 | 17.0551 | 16.7155 | 22.406 | 22.1691 | 21.7389 | 22.1003 | 21.8266 | 21.3364 | 21.9709 | 21.5607 | 20.9452 | 20.1521 | 20.4262 | 19.9848 | 19.7548 | 0.0082694 | -0.066159 | 20.7581 | 22.1103 | 22.4186 | 20.156 | 21.7143 | 22.1751 | 21.9809 | 21.7551 | 21.3252 | 21.8358 | 21.504 | 21.0983 | 20.5397 | 20.556 | 20.5194 | 20.5205 | 20.1192 |  | 20.2486 | 19.821 | 20.1393 | 19.7299 | 20.1155 | 20.3819 |  | 20.4579 |  |  | 20.254 | 20.372 | 20.601 | [5 empty] | 21.9615 | 20.3693 | 21.7043 | 22.0996 | 19.5535 | 21.2294 | 21.88 | 19.398 | 20.0103 | 21.22 |  | 19.723 | 21.0031 | 18.8282 | 19.728 | 20.8604 | 19.4324 | 20.1535 | 19.0268 | 20.1925 | 19.174 | 20.2869 | 18.711 | 20.1522 | 21.1605 | 19.455 | 19.8553 | 21.044 | 18.9377 | 19.8303 | 20.8732 | 19.0879 | 20.3066 | 19.3416 | 19.9964 | 18.9448 | 20.1591 | -0.14668 | 20.9491 | 0.049212 | 0.015217 | -27.0406 | 3.0972 | -1.29 | 0.02 | 0.72598 | -0.39084 | -8.817 | 0.93256 | 0.5332 | -16.7207 | 4.2284 | 0.42376 | 0.42838 | 0.43011 | 0.37079 | 0.46201 | 0.44078 | 0.43064
42838.4123 | -693 | 22.9047 | 22.877 | 22.873 | 22.7961 | 22.4425 | 21.792 | 22.7432 | 21.8621 | 22.3979 | 22.4075 | 22.3981 | 22.0868 | 21.3083 | 22.2617 | 21.5844 | 21.7635 | 21.9064 | 21.0896 | 21.1866 | 21.4115 | 20.4912 | 20.6388 | 20.9357 | 21.9165 | 21.6766 | 21.3163 | 20.4278 | 20.5466 | 20.5209 | 22.0433 | 21.6628 | 21.1872 | 21.9978 | 21.7438 | 21.3698 | 19.9442 | 20.4659 |  | 20.5784 | 20.2493 | 20.3622 | 19.1361 |  | 16.7429 | 16.7737 | 16.5464 | 16.8619 | 17.0934 | 17.7832 | 18.3958 | 15.7984 | 16.6275 | 16.5284 | 16.8543 | 17.8789 | 44.6566 | 48.0815 | 43.6786 | 21.3453 |  |  | 0.52527 | -0.015837 | -55.4982 | 0.33903 | 0.17492 | -197.8453 | 12.4092 | -0.066728 | -0.15909 | 0.13208 | 0.025463 | 8.8292 | 9.0586 | 1.979 | 21.814 | 22.0431 | 22.241 | 22.3061 | 22.1484 | 21.4887 | 20.317 | 22.2256 | 22.3912 | 22.426 | 22.3847 | 22.0245 | 21.275 | 22.292 | 17.3458 | 17.0841 | 16.1942 | 16.1264 | 16.1295 | 17.0623 | 16.7104 | 22.4057 | 22.1803 | 21.7437 | 22.1073 | 21.8325 | 21.3539 | 21.9629 | 21.5619 | 20.9428 | 20.152 | 20.4427 | 19.9846 | 19.7556 | -0.044223 | 0.0026938 | 20.7534 | 22.1071 | 22.4107 | 20.1511 | 21.712 | 22.1625 | 21.9736 | 21.7462 | 21.3149 | 21.8296 | 21.4949 | 21.0943 | 20.5309 | 20.5522 | 20.5103 | 20.5099 | 20.1306 |  | 20.2667 | 19.8398 | 20.1508 | 19.7434 | 20.1249 | 20.3984 |  | 20.466 |  |  | 20.2638 | 20.3749 | 20.6031 | [5 empty] | 21.9619 | 20.3686 | 21.7154 | 22.1013 | 19.5596 | 21.2412 | 21.8819 | 19.4018 | 20.0181 | 21.2213 |  | 19.7262 | 21.0086 | 18.8312 | 19.7397 | 20.8623 | 19.4335 | 20.1612 | 19.0364 | 20.2051 | 19.1786 | 20.3063 | 18.7162 | 20.1416 | 21.1505 | 19.4348 | 19.851 | 21.0327 | 18.9265 | 19.8238 | 20.8631 | 19.0834 | 20.2888 | 19.3194 | 19.9899 | 18.9382 | 20.151 | -0.13814 | 20.9481 | 0.049015 | 0.014114 | -26.9836 | 3.0971 | -1.05 | 0.07 | 0.86554 | -0.14933 | -8.8399 | 0.69092 | 0.49715 | -16.7196 | 4.1873 | 0.42405 | 0.42824 | 0.43005 | 0.3707 | 0.45761 | 0.44087 | 0.43062
42838.4123 | -692 | 22.9044 | 22.8727 | 22.8666 | 22.7996 | 22.4469 | 21.797 | 22.7367 | 21.8672 | 22.3913 | 22.4046 | 22.3907 | 22.0825 | 21.2986 | 22.2593 | 21.5864 | 21.7615 | 21.9041 | 21.0938 | 21.1925 | 21.4182 | 20.4957 | 20.6396 | 20.942 | 21.9162 | 21.6813 | 21.322 | 20.4381 | 20.5525 | 20.5269 | 22.0435 | 21.6649 | 21.1905 | 22.0079 | 21.7505 | 21.3699 | 19.95 | 20.4646 |  | 20.5827 | 20.253 | 20.3712 | 19.1468 |  | 16.7453 | 16.7718 | 16.5346 | 16.8439 | 17.0872 | 17.7897 | 18.4169 | 15.8242 | 16.6212 | 16.521 | 16.8588 | 17.8824 | 44.6687 | 48.1396 | 43.6839 | 21.3392 |  |  | 0.39056 | -0.12886 | -55.9312 | 0.47702 | 0.26232 | -197.8683 | 12.0925 | -0.20078 | -0.052059 | 0.057387 | -0.086682 | 8.8289 | 9.0585 | 1.9787 | 21.8228 | 22.0466 | 22.2372 | 22.3023 | 22.1468 | 21.4896 | 20.3169 | 22.2272 | 22.3923 | 22.4289 | 22.3826 | 22.0235 | 21.2691 | 22.2958 | 17.3326 | 17.0692 | 16.2163 | 16.151 | 16.1338 | 17.066 | 16.718 | 22.4081 | 22.1839 | 21.7379 | 22.1029 | 21.8309 | 21.3482 | 21.9629 | 21.5538 | 20.9402 | 20.1472 | 20.4357 | 19.9812 | 19.7548 | 0.08455 | 0.12233 | 20.7506 | 22.1043 | 22.4097 | 20.1514 | 21.7084 | 22.1562 | 21.9727 | 21.7442 | 21.3156 | 21.8268 | 21.4921 | 21.0896 | 20.5273 | 20.5489 | 20.5047 | 20.5085 | 20.1158 |  | 20.2504 | 19.8318 | 20.1365 | 19.7137 | 20.1219 | 20.3849 |  | 20.4554 |  |  | 20.2707 | 20.3642 | 20.6024 | [5 empty] | 21.9665 | 20.3617 | 21.7114 | 22.1026 | 19.5557 | 21.241 | 21.875 | 19.4015 | 20.0131 | 21.2228 |  | 19.7302 | 21.0188 | 18.8347 | 19.7461 | 20.8693 | 19.4379 | 20.1632 | 19.0325 | 20.2066 | 19.1784 | 20.3027 | 18.7103 | 20.1354 | 21.1505 | 19.4348 | 19.8416 | 21.0361 | 18.9221 | 19.8304 | 20.862 | 19.0775 | 20.2901 | 19.3246 | 19.9893 | 18.9412 | 20.1541 | 0.025095 | 20.9472 | 0.049421 | 0.014593 | -27.0491 | 3.0972 | -0.88 | 0.03 | 0.74635 | -0.42596 | -8.8743 | 0.81955 | 0.60881 | -16.7208 | 4.1336 | 0.42391 | 0.42798 | 0.43077 | 0.37261 | 0.45605 | 0.44076 | 0.43048
42838.4123 | -691 | 22.9007 | 22.8711 | 22.8714 | 22.7965 | 22.4502 | 21.7939 | 22.7362 | 21.8594 | 22.3871 | 22.401 | 22.3941 | 22.0776 | 21.2964 | 22.2639 | 21.5989 | 21.7639 | 21.9038 | 21.0966 | 21.2014 | 21.4212 | 20.5004 | 20.6499 | 20.9423 | 21.9169 | 21.683 | 21.3232 | 20.4331 | 20.552 | 20.5432 | 22.048 | 21.6606 | 21.192 | 22.0104 | 21.7541 | 21.3756 | 19.9482 | 20.4644 |  | 20.5896 | 20.2516 | 20.3723 | 19.1607 |  | 16.7386 | 16.7736 | 16.5272 | 16.8341 | 17.09 | 17.8098 | 18.4307 | 15.875 | 16.6292 | 16.5064 | 16.855 | 17.8872 | 44.6961 | 48.2144 | 43.7095 | 21.3531 |  |  | 0.4129 | -0.3214 | -55.6119 | 0.26149 | 0.13681 | -197.8644 | 12.2574 | -0.18304 | -0.31419 | -0.19081 | -0.044324 | 8.8281 | 9.0579 | 1.9778 | 21.8109 | 22.0386 | 22.2339 | 22.3065 | 22.1355 | 21.4846 | 20.3069 | 22.2152 | 22.383 | 22.4272 | 22.3834 | 22.0162 | 21.2689 | 22.2937 | 17.3242 | 17.0391 | 16.2206 | 16.1715 | 16.1413 | 17.0549 | 16.7205 | 22.4178 | 22.1806 | 21.7367 | 22.1015 | 21.8318 | 21.3414 | 21.9659 | 21.5643 | 20.9405 | 20.1447 | 20.4351 | 19.9877 | 19.7658 | 0.051521 | -0.014805 | 20.7587 | 22.1073 | 22.416 | 20.1535 | 21.7132 | 22.16 | 21.9708 | 21.7505 | 21.3171 | 21.8285 | 21.4947 | 21.0926 | 20.5312 | 20.5471 | 20.5059 | 20.5088 | 20.1169 |  | 20.2497 | 19.8305 | 20.1419 | 19.7064 | 20.1171 | 20.3847 |  | 20.459 |  |  | 20.2572 | 20.3558 | 20.5992 | [5 empty] | 21.966 | 20.3643 | 21.7018 | 22.0919 | 19.5481 | 21.2386 | 21.8744 | 19.3995 | 20.0128 | 21.2214 |  | 19.7361 | 21.0088 | 18.8387 | 19.7345 | 20.8711 | 19.4335 | 20.1556 | 19.0266 | 20.2072 | 19.1829 | 20.2969 | 18.7103 | 20.1458 | 21.1581 | 19.4362 | 19.8393 | 21.0288 | 18.9209 | 19.8223 | 20.8703 | 19.0744 | 20.2963 | 19.3225 | 19.9892 | 18.9254 | 20.1567 | -0.10642 | 20.9481 | 0.0492 | 0.014288 | -27.0964 | 3.0972 | -0.88 | -0.03 | 0.76742 | -0.67271 | -8.849 | 0.60679 | 0.43969 | -16.7212 | 4.1618 | 0.42386 | 0.4282 | 0.43082 | 0.37225 | 0.45586 | 0.44032 | 0.43009
42838.4123 | -690 | 22.9044 | 22.8694 | 22.8621 | 22.7995 | 22.439 | 21.7901 | 22.7435 | 21.856 | 22.3859 | 22.3936 | 22.388 | 22.0808 | 21.3015 | 22.2607 | 21.5877 | 21.7724 | 21.9054 | 21.0985 | 21.1915 | 21.4105 | 20.4856 | 20.6441 | 20.9289 | 21.9188 | 21.683 | 21.3209 | 20.4332 | 20.5463 | 20.5337 | 22.0572 | 21.6668 | 21.1944 | 22.0154 | 21.7544 | 21.3712 | 19.9427 | 20.4569 |  | 20.59 | 20.2558 | 20.3675 | 19.1728 |  | 16.7434 | 16.7622 | 16.5281 | 16.8297 | 17.0766 | 17.7901 | 18.44 | 15.9245 | 16.6245 | 16.4475 | 16.8615 | 17.8785 | 44.7104 | 48.2785 | 43.7103 | 21.34 |  |  | 0.4129 | -0.16895 | -55.5705 | 0.2306 | 0.20384 | -197.8624 | 12.4224 | -0.33023 | -0.43348 | -0.024226 | -0.037554 | 8.8292 | 9.0589 | 1.9777 | 21.8153 | 22.0514 | 22.2377 | 22.3107 | 22.1435 | 21.4872 | 20.3196 | 22.2223 | 22.3922 | 22.4275 | 22.3836 | 22.0339 | 21.2712 | 22.3006 | 17.3051 | 17.0209 | 16.2175 | 16.1881 | 16.1424 | 17.0581 | 16.7235 | 22.4041 | 22.1656 | 21.727 | 22.1058 | 21.8257 | 21.33 | 21.9589 | 21.5542 | 20.9388 | 20.1446 | 20.431 | 19.9784 | 19.7621 | 0.037956 | -0.08632 | 20.7674 | 22.1083 | 22.4231 | 20.1536 | 21.719 | 22.1654 | 21.9772 | 21.7536 | 21.3225 | 21.8321 | 21.4946 | 21.1013 | 20.5374 | 20.5486 | 20.5076 | 20.5082 | 20.1062 |  | 20.2383 | 19.8199 | 20.1351 | 19.6917 | 20.1106 | 20.3796 |  | 20.4516 |  |  | 20.2711 | 20.3587 | 20.6004 | [5 empty] | 21.9704 | 20.3681 | 21.7057 | 22.1034 | 19.5655 | 21.2356 | 21.8759 | 19.3965 | 20.0099 | 21.2317 |  | 19.7286 | 21.0092 | 18.8449 | 19.7462 | 20.8668 | 19.4275 | 20.1556 | 19.0268 | 20.1991 | 19.1844 | 20.2964 | 18.7106 | 20.1456 | 21.1706 | 19.441 | 19.8493 | 21.0461 | 18.9404 | 19.8253 | 20.8751 | 19.0659 | 20.2964 | 19.3316 | 19.9929 | 18.9418 | 20.1661 | -0.096592 | 20.9494 | 0.048856 | 0.014281 | -27.072 | 3.0972 | -1.13 | -0.06 | 0.76741 | -0.48772 | -8.8455 | 0.56981 | 0.53667 | -16.7205 | 4.1896 | 0.42377 | 0.42827 | 0.43101 | 0.37473 | 0.45655 | 0.4398 | 0.43019
42838.4123 | -689 | 22.8977 | 22.8583 | 22.8488 | 22.7876 | 22.4251 | 21.7806 | 22.7334 | 21.8468 | 22.3811 | 22.3913 | 22.3756 | 22.0689 | 21.2907 | 22.2479 | 21.586 | 21.7593 | 21.902 | 21.0953 | 21.1918 | 21.4142 | 20.4918 | 20.6383 | 20.9412 | 21.9139 | 21.6875 | 21.3205 | 20.4317 | 20.5515 | 20.5436 | 22.0577 | 21.672 | 21.2017 | 22.0158 | 21.7591 | 21.3804 | 19.9523 | 20.4653 |  | 20.5982 | 20.2603 | 20.3801 | 19.1897 |  | 16.7324 | 16.7479 | 16.5105 | 16.823 | 17.0715 | 17.7708 | 18.4041 | 15.9316 | 16.6222 | 16.3967 | 16.8578 | 17.8801 | 44.7171 | 48.3598 | 43.7295 | 21.3433 |  |  | 0.36821 | -0.12032 | -55.4127 | 0.30289 | 0.34249 | -197.8808 | 12.4894 | -0.30395 | -0.2379 | 0.17068 | 0.027026 | 8.829 | 9.0586 | 1.9787 | 21.8297 | 22.049 | 22.2465 | 22.3138 | 22.1539 | 21.4908 | 20.3197 | 22.2268 | 22.4045 | 22.4317 | 22.3883 | 22.0234 | 21.2681 | 22.2998 | 17.3071 | 17.0536 | 16.2121 | 16.2023 | 16.1502 | 17.0589 | 16.7285 | 22.4135 | 22.1724 | 21.7355 | 22.1054 | 21.8282 | 21.3366 | 21.9642 | 21.5526 | 20.95 | 20.1522 | 20.4264 | 19.9823 | 19.7621 | 0.10401 | 0.045299 | 20.7607 | 22.1063 | 22.4207 | 20.1577 | 21.7164 | 22.1598 | 21.9787 | 21.7491 | 21.3223 | 21.831 | 21.4952 | 21.1051 | 20.5398 | 20.5452 | 20.5022 | 20.5113 | 20.1088 |  | 20.2548 | 19.8086 | 20.1414 | 19.7036 | 20.1207 | 20.3879 |  | 20.4595 |  |  | 20.2689 | 20.3527 | 20.5966 | [5 empty] | 21.9627 | 20.37 | 21.7061 | 22.0933 | 19.5544 | 21.2356 | 21.8783 | 19.407 | 20.0266 | 21.2315 |  | 19.7373 | 21.0116 | 18.8497 | 19.7479 | 20.8825 | 19.4355 | 20.1704 | 19.0436 | 20.2047 | 19.1789 | 20.3075 | 18.7005 | 20.1359 | 21.1552 | 19.4239 | 19.8431 | 21.0344 | 18.9196 | 19.8218 | 20.8658 | 19.049 | 20.2842 | 19.3166 | 19.9811 | 18.9406 | 20.1529 | -0.00106 | 20.9484 | 0.047645 | 0.01272 | -27.0407 | 3.0972 | -1.3 | -0.18 | 0.72471 | -0.41158 | -8.8327 | 0.65302 | 0.69563 | -16.7208 | 4.2007 | 0.42425 | 0.42879 | 0.43101 | 0.37461 | 0.45773 | 0.43965 | 0.43044
42838.4123 | -688 | 22.9061 | 22.867 | 22.8576 | 22.7937 | 22.4386 | 21.7916 | 22.7359 | 21.8521 | 22.3929 | 22.4014 | 22.3918 | 22.0804 | 21.3065 | 22.2644 | 21.5886 | 21.765 | 21.8976 | 21.0946 | 21.1933 | 21.4135 | 20.492 | 20.6359 | 20.9464 | 21.9122 | 21.6826 | 21.321 | 20.4351 | 20.5482 | 20.5393 | 22.0481 | 21.6635 | 21.1958 | 22.0112 | 21.7503 | 21.3662 | 19.948 | 20.4592 |  | 20.586 | 20.2492 | 20.3682 | 19.1866 |  | 16.7177 | 16.7412 | 16.4971 | 16.8165 | 17.0668 | 17.7484 | 18.3745 | 15.91 | 16.6162 | 16.3138 | 16.8499 | 17.8876 | 44.7416 | 48.4493 | 43.7465 | 21.352 |  |  | 0.56798 | -0.1972 | -55.7604 | 0.33574 | 0.24918 | -197.8552 | 12.6425 | -0.41237 | -0.19567 | -0.0019868 | -0.050053 | 8.8286 | 9.0585 | 1.979 | 21.8179 | 22.0449 | 22.2414 | 22.3044 | 22.1495 | 21.488 | 20.3113 | 22.2206 | 22.4013 | 22.4241 | 22.3838 | 22.0204 | 21.2681 | 22.2926 | 17.281 | 17.1043 | 16.1995 | 16.1878 | 16.1467 | 17.057 | 16.714 | 22.4095 | 22.1706 | 21.7379 | 22.1045 | 21.822 | 21.3308 | 21.9563 | 21.5547 | 20.9423 | 20.1503 | 20.4196 | 19.9835 | 19.7513 | 0.09497 | -0.10058 | 20.7603 | 22.1111 | 22.4249 | 20.1537 | 21.7135 | 22.1571 | 21.9798 | 21.7451 | 21.3218 | 21.8326 | 21.5034 | 21.1009 | 20.5425 | 20.5407 | 20.5022 | 20.5078 | 20.113 |  | 20.2597 | 19.8011 | 20.1453 | 19.7043 | 20.1227 | 20.3903 |  | 20.466 |  |  | 20.2725 | 20.3467 | 20.6077 | [5 empty] | 21.9676 | 20.3651 | 21.7066 | 22.1041 | 19.5438 | 21.241 | 21.8806 | 19.3935 | 20.0114 | 21.2096 |  | 19.7274 | 21.0059 | 18.8298 | 19.7394 | 20.8661 | 19.4228 | 20.1637 | 19.028 | 20.1937 | 19.1663 | 20.2903 | 18.7108 | 20.1526 | 21.1711 | 19.4272 | 19.852 | 21.0356 | 18.9323 | 19.8317 | 20.8685 | 19.0578 | 20.2909 | 19.3299 | 19.9872 | 18.9471 | 20.164 | -0.17728 | 20.9491 | 0.046717 | 0.012262 | -27.0821 | 3.0972 | -1.36 | 0.03 | 0.90007 | -0.52691 | -8.8603 | 0.68752 | 0.59333 | -16.719 | 4.2262 | 0.4243 | 0.42913 | 0.43106 | 0.37729 | 0.45745 | 0.43959 | 0.43068
42838.4123 | -687 | 22.9086 | 22.8781 | 22.8518 | 22.7917 | 22.4368 | 21.7887 | 22.7413 | 21.8576 | 22.3883 | 22.4018 | 22.3873 | 22.0809 | 21.3032 | 22.2661 | 21.5896 | 21.7682 | 21.9078 | 21.0947 | 21.1912 | 21.4141 | 20.4958 | 20.6483 | 20.9409 | 21.9199 | 21.6861 | 21.324 | 20.4364 | 20.5489 | 20.5503 | 22.0552 | 21.6642 | 21.1949 | 22.0178 | 21.7451 | 21.374 | 19.9473 | 20.4603 |  | 20.5922 | 20.2517 | 20.3682 | 19.2063 |  | 16.7178 | 16.7358 | 16.4894 | 16.8106 | 17.0576 | 17.7298 | 18.3551 | 15.899 | 16.6183 | 16.2054 | 16.8468 | 17.8872 | 44.7388 | 48.5279 | 43.7465 | 21.3525 |  |  | 0.4589 | -0.25897 | -55.4903 | 0.10378 | 0.15784 | -197.821 | 12.4263 | -0.28489 | 0.060809 | -0.41194 | -0.076961 | 8.8288 | 9.0583 | 1.9784 | 21.8278 | 22.0555 | 22.2468 | 22.3181 | 22.1548 | 21.4954 | 20.3229 | 22.2303 | 22.403 | 22.4289 | 22.3945 | 22.0335 | 21.2749 | 22.3019 | 17.2533 | 17.1061 | 16.1987 | 16.1789 | 16.1347 | 17.0595 | 16.7212 | 22.4025 | 22.1739 | 21.7363 | 22.1042 | 21.8212 | 21.3369 | 21.9616 | 21.5574 | 20.9371 | 20.1482 | 20.4173 | 19.9894 | 19.7432 | -0.12326 | -0.088792 | 20.7583 | 22.1066 | 22.4243 | 20.1531 | 21.714 | 22.1634 | 21.9834 | 21.7478 | 21.3219 | 21.8364 | 21.5024 | 21.1064 | 20.5399 | 20.5451 | 20.4963 | 20.5015 | 20.1297 |  | 20.2543 | 19.791 | 20.1471 | 19.7044 | 20.1246 | 20.3838 |  | 20.4637 |  |  | 20.284 | 20.3401 | 20.6109 | [5 empty] | 21.9632 | 20.3702 | 21.7057 | 22.0977 | 19.5507 | 21.2329 | 21.8852 | 19.3939 | 20.0193 | 21.2175 |  | 19.7307 | 21.0066 | 18.834 | 19.74 | 20.87 | 19.4286 | 20.1653 | 19.0246 | 20.2036 | 19.1739 | 20.2887 | 18.7041 | 20.1502 | 21.1672 | 19.4216 | 19.8503 | 21.0373 | 18.9243 | 19.8251 | 20.8642 | 19.0414 | 20.2909 | 19.3232 | 19.9885 | 18.9395 | 20.1583 | -0.07155 | 20.9486 | 0.047916 | 0.011631 | -27.0447 | 3.0972 | -1.13 | -0.35 | 0.80905 | -0.60382 | -8.8387 | 0.38224 | 0.47221 | -16.7171 | 4.1898 | 0.42365 | 0.42947 | 0.43112 | 0.38065 | 0.45836 | 0.43902 | 0.43084
42838.4123 | -686 | 22.8956 | 22.8682 | 22.8607 | 22.7906 | 22.4318 | 21.7895 | 22.7355 | 21.8491 | 22.3969 | 22.4034 | 22.3915 | 22.0802 | 21.307 | 22.2619 | 21.5934 | 21.7675 | 21.9048 | 21.0916 | 21.1959 | 21.4162 | 20.5005 | 20.6492 | 20.9418 | 21.9177 | 21.6813 | 21.3174 | 20.4436 | 20.549 | 20.5524 | 22.0497 | 21.6581 | 21.1808 | 22.0039 | 21.7504 | 21.3691 | 19.9425 | 20.4616 |  | 20.5836 | 20.2434 | 20.3627 | 19.2208 |  | 16.7204 | 16.7347 | 16.4892 | 16.7968 | 17.0539 | 17.7025 | 18.3561 | 15.9045 | 16.6185 | 16.1649 | 16.8467 | 17.8779 | 44.7433 | 48.6135 | 43.745 | 21.3535 |  |  | 0.53381 | -0.37199 | -54.8641 | 0.23389 | 0.24524 | -197.8506 | 12.8377 | -0.43406 | 0.10615 | -0.19626 | -0.0004032 | 8.8297 | 9.0595 | 1.9783 | 21.8198 | 22.0476 | 22.2358 | 22.3077 | 22.1473 | 21.4877 | 20.3134 | 22.2211 | 22.3937 | 22.4319 | 22.3807 | 22.0191 | 21.2653 | 22.2958 | 17.1926 | 17.0895 | 16.1982 | 16.1826 | 16.1349 | 17.056 | 16.725 | 22.4094 | 22.1707 | 21.7325 | 22.0991 | 21.8294 | 21.3384 | 21.9683 | 21.557 | 20.9408 | 20.1464 | 20.4314 | 19.992 | 19.7498 | -0.12326 | -0.25236 | 20.7515 | 22.1052 | 22.4248 | 20.1507 | 21.7125 | 22.1611 | 21.9816 | 21.7515 | 21.3174 | 21.835 | 21.4936 | 21.1057 | 20.5421 | 20.5525 | 20.4945 | 20.5017 | 20.1314 |  | 20.2546 | 19.7798 | 20.1491 | 19.7024 | 20.1185 | 20.3896 |  | 20.4618 |  |  | 20.2791 | 20.3345 | 20.6081 | [5 empty] | 21.9665 | 20.3644 | 21.7038 | 22.0995 | 19.5594 | 21.2351 | 21.8809 | 19.3963 | 20.0236 | 21.2234 |  | 19.7281 | 21.0125 | 18.8405 | 19.7483 | 20.8712 | 19.4289 | 20.1712 | 19.0189 | 20.2086 | 19.1827 | 20.2932 | 18.706 | 20.1433 | 21.1706 | 19.4252 | 19.8426 | 21.0445 | 18.9226 | 19.8319 | 20.8651 | 19.0278 | 20.2887 | 19.3269 | 19.9877 | 18.9424 | 20.1623 | -0.1541 | 20.9487 | 0.048413 | 0.012858 | -27.0714 | 3.0972 | -1.12 | -0.8 | 0.8726 | -0.72368 | -8.7887 | 0.57383 | 0.58857 | -16.7175 | 4.2584 | 0.42362 | 0.42985 | 0.43097 | 0.38699 | 0.45886 | 0.43846 | 0.43059
42838.4123 | -685 | 22.8896 | 22.8639 | 22.8576 | 22.79 | 22.4329 | 21.7886 | 22.7321 | 21.855 | 22.385 | 22.3994 | 22.3854 | 22.067 | 21.3027 | 22.2592 | 21.5933 | 21.7708 | 21.9072 | 21.0918 | 21.193 | 21.4141 | 20.5008 | 20.6472 | 20.9403 | 21.9185 | 21.6842 | 21.3216 | 20.4435 | 20.5548 | 20.5537 | 22.0502 | 21.6659 | 21.1895 | 22.0083 | 21.7537 | 21.3654 | 19.9401 | 20.4611 |  | 20.5746 | 20.2485 | 20.3642 | 19.2309 |  | 16.7096 | 16.7229 | 16.4939 | 16.8031 | 17.0452 | 17.691 | 18.3708 | 15.913 | 16.6158 | 16.175 | 16.8488 | 17.8887 | 44.7517 | 48.6981 | 43.7629 | 21.3606 |  |  | 0.35836 | -0.1926 | -55.1499 | 0.26017 | 0.1953 | -197.8926 | 12.6313 | -0.29212 | 0.24276 | -0.074578 | -0.16324 | 8.8294 | 9.059 | 1.9781 | 21.8154 | 22.0404 | 22.2272 | 22.2992 | 22.1384 | 21.486 | 20.3132 | 22.2171 | 22.3867 | 22.4226 | 22.378 | 22.0181 | 21.2592 | 22.2942 | 17.1147 | 17.1188 | 16.1927 | 16.1869 | 16.1525 | 17.069 | 16.7255 | 22.4061 | 22.171 | 21.7357 | 22.098 | 21.8195 | 21.3356 | 21.9628 | 21.5597 | 20.9391 | 20.147 | 20.4233 | 19.9814 | 19.7388 | 0.093004 | -0.18903 | 20.7592 | 22.113 | 22.4267 | 20.1495 | 21.7128 | 22.1658 | 21.9793 | 21.7548 | 21.3217 | 21.8336 | 21.4971 | 21.1003 | 20.5489 | 20.5462 | 20.502 | 20.5044 | 20.1317 |  | 20.2563 | 19.7635 | 20.1398 | 19.7031 | 20.122 | 20.3847 |  | 20.46 |  |  | 20.2845 | 20.3352 | 20.61 | [5 empty] | 21.9629 | 20.3586 | 21.7089 | 22.0976 | 19.5531 | 21.2285 | 21.8794 | 19.399 | 20.0236 | 21.2256 |  | 19.7238 | 21.0099 | 18.8473 | 19.7484 | 20.8731 | 19.4279 | 20.1707 | 18.9929 | 20.2051 | 19.1731 | 20.3026 | 18.7021 | 20.1468 | 21.1726 | 19.417 | 19.8445 | 21.0397 | 18.9298 | 19.8397 | 20.8763 | 19.0191 | 20.2882 | 19.3282 | 19.9844 | 18.9528 | 20.1634 | -0.16931 | 20.9486 | 0.048764 | 0.014099 | -27.0977 | 3.0973 | -0.92 | 0.06 | 0.71496 | -0.52071 | -8.8114 | 0.60521 | 0.52522 | -16.719 | 4.224 | 0.42367 | 0.42999 | 0.43107 | 0.39716 | 0.45955 | 0.4381 | 0.43092
42838.4124 | -684 | 22.9014 | 22.8727 | 22.862 | 22.7981 | 22.4365 | 21.7854 | 22.7333 | 21.8562 | 22.3937 | 22.4059 | 22.387 | 22.0851 | 21.3069 | 22.262 | 21.5895 | 21.7641 | 21.9051 | 21.0898 | 21.1875 | 21.4164 | 20.4996 | 20.6453 | 20.942 | 21.919 | 21.6852 | 21.3219 | 20.4398 | 20.5505 | 20.5534 | 22.0609 | 21.6709 | 21.1962 | 22.0101 | 21.7543 | 21.3687 | 19.9476 | 20.4731 |  | 20.5806 | 20.254 | 20.3694 | 19.2367 |  | 16.7113 | 16.728 | 16.489 | 16.7957 | 17.0409 | 17.6877 | 18.3742 | 15.9437 | 16.6189 | 16.1784 | 16.8514 | 17.8832 | 44.7556 | 48.7846 | 43.7827 | 21.3606 |  |  | 0.36164 | -0.32928 | -55.2412 | 0.24046 | 0.22092 | -197.8309 | 12.5867 | -0.57534 | 0.040181 | -0.12031 | 0.051677 | 8.8285 | 9.0583 | 1.979 | 21.819 | 22.0427 | 22.2365 | 22.3124 | 22.1431 | 21.489 | 20.3117 | 22.2186 | 22.3925 | 22.4291 | 22.3872 | 22.0276 | 21.2654 | 22.2954 | 17.068 | 17.1437 | 16.1909 | 16.1885 | 16.1585 | 17.0634 | 16.7212 | 22.4038 | 22.1711 | 21.7357 | 22.0957 | 21.8192 | 21.3368 | 21.9629 | 21.5619 | 20.9386 | 20.14 | 20.4259 | 19.9848 | 19.7423 | 0.031468 | -0.15327 | 20.76 | 22.1078 | 22.4227 | 20.1533 | 21.718 | 22.1682 | 21.9781 | 21.7552 | 21.3215 | 21.8277 | 21.4965 | 21.1011 | 20.5479 | 20.5432 | 20.495 | 20.4976 | 20.1442 |  | 20.2665 | 19.761 | 20.1505 | 19.7238 | 20.1315 | 20.3902 |  | 20.4689 |  |  | 20.2894 | 20.3411 | 20.6126 | [5 empty] | 21.9683 | 20.3618 | 21.7113 | 22.0971 | 19.5554 | 21.233 | 21.8796 | 19.3956 | 20.0191 | 21.2203 |  | 19.7193 | 21.0123 | 18.8403 | 19.753 | 20.8686 | 19.4242 | 20.1662 | 18.9631 | 20.1974 | 19.1719 | 20.297 | 18.6959 | 20.1434 | 21.1718 | 19.413 | 19.8456 | 21.0368 | 18.9307 | 19.8447 | 20.8751 | 19.0086 | 20.2786 | 19.3186 | 19.9787 | 18.9464 | 20.1542 | 0.009328 | 20.9491 | 0.049243 | 0.01391 | -27.0118 | 3.0973 | -1.3 | -0.15 | 0.71823 | -0.68086 | -8.8187 | 0.58183 | 0.55862 | -16.7163 | 4.2165 | 0.42366 | 0.43042 | 0.43082 | 0.4017 | 0.45924 | 0.43819 | 0.43059
42838.4124 | -683 | 22.9004 | 22.8667 | 22.8603 | 22.7979 | 22.4354 | 21.7858 | 22.7346 | 21.8527 | 22.388 | 22.4015 | 22.386 | 22.0804 | 21.3043 | 22.2625 | 21.5889 | 21.7631 | 21.9014 | 21.0853 | 21.1905 | 21.415 | 20.4959 | 20.642 | 20.9377 | 21.9151 | 21.6827 | 21.3129 | 20.4389 | 20.5454 | 20.5492 | 22.0542 | 21.667 | 21.1997 | 22.0116 | 21.7511 | 21.3722 | 19.9479 | 20.4797 |  | 20.585 | 20.2569 | 20.3682 | 19.2313 |  | 16.7125 | 16.7292 | 16.4898 | 16.7979 | 17.0517 | 17.6775 | 18.3519 | 15.9828 | 16.6362 | 16.1758 | 16.8598 | 17.8867 | 44.76 | 48.8702 | 43.8044 | 21.3602 |  |  | 0.54629 | -0.25042 | -55.4417 | 0.24375 | 0.080956 | -197.913 | 12.245 | -0.52211 | -0.042524 | -0.46313 | -0.078176 | 8.8287 | 9.0583 | 1.9785 | 21.826 | 22.0501 | 22.2495 | 22.3081 | 22.1482 | 21.4911 | 20.3193 | 22.2275 | 22.3961 | 22.423 | 22.3879 | 22.0269 | 21.2707 | 22.2921 | 17.0693 | 17.1827 | 16.1904 | 16.2012 | 16.1736 | 17.0637 | 16.7257 | 22.4034 | 22.1764 | 21.7418 | 22.1081 | 21.8205 | 21.3345 | 21.9696 | 21.5603 | 20.9407 | 20.1417 | 20.4303 | 19.9916 | 19.7528 | -0.017092 | -0.18522 | 20.7555 | 22.1041 | 22.4239 | 20.1497 | 21.7188 | 22.1639 | 21.9782 | 21.7501 | 21.3185 | 21.8263 | 21.4925 | 21.1007 | 20.5428 | 20.549 | 20.4913 | 20.494 | 20.1524 |  | 20.2699 | 19.7551 | 20.1445 | 19.726 | 20.1226 | 20.3955 |  | 20.4727 |  |  | 20.288 | 20.3509 | 20.6131 | [5 empty] | 21.9659 | 20.3717 | 21.7051 | 22.0967 | 19.5557 | 21.2382 | 21.8871 | 19.3935 | 20.0203 | 21.2189 |  | 19.7141 | 21.0071 | 18.8374 | 19.7526 | 20.8688 | 19.4266 | 20.1638 | 18.9501 | 20.1928 | 19.1742 | 20.2876 | 18.7053 | 20.146 | 21.1818 | 19.4125 | 19.8516 | 21.0373 | 18.9307 | 19.8454 | 20.8761 | 19.0125 | 20.2781 | 19.3193 | 19.9869 | 18.9471 | 20.1609 | -0.1118 | 20.9489 | 0.049132 | 0.01452 | -26.9809 | 3.0973 | -1.29 | 0.26 | 0.88274 | -0.59376 | -8.8347 | 0.58579 | 0.33815 | -16.7194 | 4.1588 | 0.42355 | 0.43038 | 0.43046 | 0.40158 | 0.45982 | 0.43834 | 0.43035
42838.4124 | -682 | 22.8994 | 22.864 | 22.8589 | 22.7956 | 22.4446 | 21.7814 | 22.7381 | 21.8521 | 22.3863 | 22.404 | 22.3776 | 22.0805 | 21.305 | 22.2661 | 21.5883 | 21.7569 | 21.9023 | 21.0857 | 21.1905 | 21.4148 | 20.4974 | 20.6351 | 20.934 | 21.9133 | 21.6799 | 21.3161 | 20.4427 | 20.5498 | 20.5503 | 22.054 | 21.6553 | 21.1975 | 22.0104 | 21.7468 | 21.372 | 19.9507 | 20.4816 |  | 20.5844 | 20.2525 | 20.3641 | 19.2235 |  | 16.7165 | 16.7173 | 16.4875 | 16.789 | 17.0245 | 17.6581 | 18.3436 | 15.9969 | 16.6229 | 16.1074 | 16.8529 | 17.8878 | 44.7787 | 48.9527 | 43.8339 | 21.3583 |  |  | 0.37413 | -0.19786 | -54.9515 | 0.55982 | 0.27086 | -197.8558 | 12.5361 | -0.40712 | -0.0053554 | -0.15682 | -0.047796 | 8.8277 | 9.0571 | 1.978 | 21.8141 | 22.0337 | 22.2409 | 22.297 | 22.1395 | 21.4858 | 20.3062 | 22.2207 | 22.3944 | 22.4248 | 22.3788 | 22.0249 | 21.2584 | 22.2857 | 17.0778 | 17.1806 | 16.1861 | 16.193 | 16.1821 | 17.0663 | 16.7298 | 22.4088 | 22.1792 | 21.7438 | 22.1113 | 21.8284 | 21.3358 | 21.9636 | 21.5601 | 20.945 | 20.1488 | 20.4286 | 19.9974 | 19.764 | -0.16611 | -0.02983 | 20.7589 | 22.1098 | 22.425 | 20.1506 | 21.7157 | 22.162 | 21.9807 | 21.7502 | 21.3202 | 21.8316 | 21.4945 | 21.0996 | 20.5414 | 20.552 | 20.4948 | 20.4994 | 20.1465 |  | 20.2606 | 19.7451 | 20.1366 | 19.7187 | 20.1227 | 20.3863 |  | 20.4638 |  |  | 20.2928 | 20.3547 | 20.6154 | [5 empty] | 21.9599 | 20.3682 | 21.7046 | 22.0974 | 19.5527 | 21.238 | 21.8814 | 19.4013 | 20.021 | 21.2217 |  | 19.7124 | 21.0123 | 18.8403 | 19.7538 | 20.868 | 19.4248 | 20.169 | 18.9415 | 20.1946 | 19.1775 | 20.2912 | 18.7081 | 20.1434 | 21.1805 | 19.4096 | 19.8429 | 21.036 | 18.9222 | 19.8481 | 20.8716 | 19.0092 | 20.2705 | 19.3169 | 19.983 | 18.9442 | 20.1615 | 0.057558 | 20.9484 | 0.049544 | 0.014723 | -27.0194 | 3.0973 | -1.52 | -0.34 | 0.73052 | -0.52777 | -8.7954 | 0.88775 | 0.61851 | -16.7165 | 4.2078 | 0.4234 | 0.43039 | 0.43066 | 0.40094 | 0.46078 | 0.43865 | 0.43028
42838.4124 | -681 | 22.9071 | 22.8714 | 22.861 | 22.7943 | 22.4423 | 21.7913 | 22.7371 | 21.8554 | 22.3894 | 22.4084 | 22.3923 | 22.084 | 21.3055 | 22.2682 | 21.5894 | 21.7576 | 21.9057 | 21.0908 | 21.1934 | 21.4145 | 20.5001 | 20.6431 | 20.9397 | 21.9142 | 21.6801 | 21.32 | 20.4453 | 20.5564 | 20.5522 | 22.0571 | 21.6561 | 21.1931 | 22.0113 | 21.7399 | 21.3681 | 19.9441 | 20.4819 |  | 20.5851 | 20.253 | 20.353 | 19.2134 |  | 16.708 | 16.7182 | 16.4777 | 16.7772 | 17.0059 | 17.6292 | 18.3007 | 15.9938 | 16.6194 | 16.0708 | 16.8518 | 17.8898 | 44.7985 | 49.0385 | 43.8594 | 21.361 |  |  | 0.40107 | -0.41799 | -55.5021 | 0.61436 | 0.14601 | -197.8506 | 12.4664 | -0.42223 | 0.030646 | -0.17822 | -0.099355 | 8.829 | 9.0587 | 1.978 | 21.8196 | 22.0407 | 22.2365 | 22.3053 | 22.144 | 21.4852 | 20.3149 | 22.2244 | 22.3934 | 22.4308 | 22.3877 | 22.0208 | 21.264 | 22.2897 | 17.1009 | 17.1492 | 16.1892 | 16.1885 | 16.179 | 17.063 | 16.7347 | 22.4058 | 22.1687 | 21.7358 | 22.1013 | 21.8176 | 21.3309 | 21.9587 | 21.5506 | 20.9443 | 20.1424 | 20.4247 | 19.9929 | 19.7574 | -0.15058 | 0.054048 | 20.7604 | 22.1146 | 22.4235 | 20.1549 | 21.7164 | 22.1659 | 21.9815 | 21.7502 | 21.3184 | 21.8307 | 21.496 | 21.101 | 20.5476 | 20.5458 | 20.4893 | 20.4974 | 20.155 |  | 20.261 | 19.7327 | 20.1374 | 19.7255 | 20.1227 | 20.3772 |  | 20.4617 |  |  | 20.2991 | 20.3589 | 20.6179 | [5 empty] | 21.9617 | 20.3665 | 21.7105 | 22.0983 | 19.5546 | 21.2363 | 21.8807 | 19.3998 | 20.0228 | 21.2282 |  | 19.7172 | 21.0185 | 18.844 | 19.7544 | 20.8732 | 19.4286 | 20.1787 | 18.9396 | 20.1947 | 19.1755 | 20.2943 | 18.7093 | 20.1455 | 21.1786 | 19.4175 | 19.8426 | 21.0382 | 18.9263 | 19.8455 | 20.8714 | 19.0048 | 20.2763 | 19.3086 | 19.9876 | 18.9468 | 20.1583 | -0.072663 | 20.9483 | 0.049077 | 0.014542 | -27.1267 | 3.0973 | -1.44 | 0.35 | 0.75636 | -0.7671 | -8.8394 | 0.92999 | 0.45409 | -16.7154 | 4.1958 | 0.42317 | 0.43077 | 0.43047 | 0.39799 | 0.46101 | 0.43871 | 0.43025
42838.4124 | -680 | 22.9071 | 22.8772 | 22.8644 | 22.8015 | 22.4413 | 21.7999 | 22.7385 | 21.8623 | 22.3942 | 22.4132 | 22.4013 | 22.0815 | 21.3126 | 22.2708 | 21.5935 | 21.7706 | 21.9069 | 21.0939 | 21.1921 | 21.4214 | 20.4966 | 20.6455 | 20.9493 | 21.9196 | 21.6862 | 21.3247 | 20.4501 | 20.5596 | 20.5589 | 22.0568 | 21.6684 | 21.1982 | 22.017 | 21.7541 | 21.376 | 19.9502 | 20.5031 |  | 20.5879 | 20.2529 | 20.3596 | 19.2112 |  | 16.6993 | 16.7184 | 16.4833 | 16.7703 | 17.0074 | 17.6099 | 18.2586 | 15.9776 | 16.6179 | 16.0678 | 16.8556 | 17.8875 | 44.8291 | 49.1183 | 43.892 | 21.3626 |  |  | 0.57586 | -0.2524 | -55.5705 | 0.60253 | 0.27612 | -197.8775 | 12.5065 | -0.3736 | -0.059843 | 0.062841 | -0.10265 | 8.8281 | 9.0578 | 1.9784 | 21.8256 | 22.0507 | 22.2435 | 22.31 | 22.1491 | 21.4906 | 20.3226 | 22.2327 | 22.4007 | 22.433 | 22.3872 | 22.0308 | 21.2693 | 22.2938 | 17.1202 | 17.1313 | 16.1836 | 16.1864 | 16.1846 | 17.0659 | 16.7361 | 22.4065 | 22.1691 | 21.7396 | 22.0972 | 21.8234 | 21.33 | 21.9674 | 21.5511 | 20.9376 | 20.1447 | 20.4306 | 19.9986 | 19.7678 | -0.27287 | -0.04809 | 20.7532 | 22.1093 | 22.4203 | 20.1486 | 21.7124 | 22.1689 | 21.976 | 21.7438 | 21.3195 | 21.8281 | 21.4973 | 21.0944 | 20.5467 | 20.5333 | 20.4823 | 20.4911 | 20.1563 |  | 20.2643 | 19.7341 | 20.1393 | 19.728 | 20.1248 | 20.3733 |  | 20.4683 |  |  | 20.3035 | 20.3651 | 20.6208 | [5 empty] | 21.9644 | 20.3684 | 21.6982 | 22.099 | 19.5561 | 21.2421 | 21.8758 | 19.398 | 20.0308 | 21.2264 |  | 19.7121 | 21.0146 | 18.8353 | 19.7556 | 20.8708 | 19.4347 | 20.1739 | 18.9256 | 20.1924 | 19.1702 | 20.2964 | 18.715 | 20.1485 | 21.1806 | 19.4186 | 19.8421 | 21.0404 | 18.9262 | 19.8332 | 20.8702 | 19.004 | 20.2735 | 19.3007 | 19.9803 | 18.9411 | 20.1496 | -0.031668 | 20.9487 | 0.049937 | 0.015115 | -27.0365 | 3.0973 | -1.36 | 0 | 0.90633 | -0.59609 | -8.8448 | 0.92099 | 0.62443 | -16.716 | 4.2024 | 0.42325 | 0.43079 | 0.43047 | 0.39619 | 0.46178 | 0.43898 | 0.43004
42838.4124 | -679 | 22.9071 | 22.8753 | 22.8665 | 22.7909 | 22.4334 | 21.7849 | 22.7408 | 21.8608 | 22.3909 | 22.4006 | 22.3932 | 22.0759 | 21.3079 | 22.2586 | 21.584 | 21.7626 | 21.8994 | 21.0851 | 21.1818 | 21.4097 | 20.4872 | 20.6391 | 20.9448 | 21.9097 | 21.6778 | 21.3171 | 20.4434 | 20.5459 | 20.5561 | 22.0545 | 21.6582 | 21.1911 | 22.0081 | 21.7451 | 21.3695 | 19.9536 | 20.5016 |  | 20.588 | 20.2541 | 20.356 | 19.2277 |  | 16.705 | 16.7285 | 16.489 | 16.7837 | 17.0034 | 17.6027 | 18.2253 | 15.9731 | 16.6217 | 16.0728 | 16.858 | 17.8857 | 44.854 | 49.2007 | 43.9196 | 21.3583 |  |  | 0.30645 | -0.15515 | -55.5475 | 0.32326 | 0.17558 | -197.7987 | 12.1635 | -0.42026 | 0.076766 | -0.026953 | -0.15994 | 8.8288 | 9.0586 | 1.9787 | 21.8188 | 22.0452 | 22.2401 | 22.2998 | 22.1449 | 21.4892 | 20.3153 | 22.225 | 22.3902 | 22.4243 | 22.3788 | 22.0209 | 21.2628 | 22.2884 | 17.1353 | 17.103 | 16.1955 | 16.1829 | 16.1819 | 17.0607 | 16.7391 | 22.4037 | 22.172 | 21.7365 | 22.0974 | 21.8295 | 21.3306 | 21.9589 | 21.5572 | 20.9345 | 20.1452 | 20.4304 | 19.9972 | 19.7744 | -0.010604 | -0.15898 | 20.7465 | 22.1063 | 22.4171 | 20.1483 | 21.711 | 22.1622 | 21.975 | 21.7476 | 21.3208 | 21.8267 | 21.497 | 21.1 | 20.5459 | 20.5332 | 20.4804 | 20.4892 | 20.1489 |  | 20.2515 | 19.7243 | 20.143 | 19.7217 | 20.1186 | 20.3731 |  | 20.4594 |  |  | 20.3041 | 20.3703 | 20.6244 | [5 empty] | 21.9631 | 20.3625 | 21.7044 | 22.095 | 19.5599 | 21.2386 | 21.8695 | 19.4008 | 20.0331 | 21.2297 |  | 19.7131 | 21.0129 | 18.8434 | 19.7512 | 20.8759 | 19.4309 | 20.1781 | 18.9227 | 20.1867 | 19.1723 | 20.2947 | 18.7086 | 20.1453 | 21.1723 | 19.4132 | 19.8414 | 21.0305 | 18.9243 | 19.8312 | 20.865 | 19.0008 | 20.2711 | 19.2945 | 19.9816 | 18.9394 | 20.1475 | -0.14668 | 20.9391 | 0.050103 | 0.015239 | -27.0327 | 3.0974 | -1.15 | 0.02 | 0.66115 | -0.46735 | -8.8432 | 0.67461 | 0.49793 | -16.7125 | 4.1444 | 0.42303 | 0.43119 | 0.43044 | 0.39391 | 0.46081 | 0.43863 | 0.42987
42838.4124 | -678 | 22.9038 | 22.8766 | 22.8666 | 22.7935 | 22.439 | 21.7866 | 22.7402 | 21.8545 | 22.3813 | 22.4051 | 22.3833 | 22.0774 | 21.3054 | 22.2608 | 21.5997 | 21.7737 | 21.922 | 21.1044 | 21.2051 | 21.4196 | 20.5083 | 20.6602 | 20.9499 | 21.9242 | 21.6882 | 21.33 | 20.4615 | 20.5623 | 20.5659 | 22.0542 | 21.6611 | 21.1931 | 22 | 21.7462 | 21.369 | 19.9528 | 20.5085 |  | 20.5884 | 20.2542 | 20.3615 | 19.2275 |  | 16.7106 | 16.7207 | 16.486 | 16.7769 | 16.9976 | 17.5903 | 18.1817 | 15.9572 | 16.6194 | 16.0567 | 16.8578 | 17.8917 | 44.8728 | 49.281 | 43.9485 | 21.3581 |  |  | 0.48453 | -0.16237 | -53.996 | 0.43299 | 0.14338 | -197.8729 | 12.8948 | -0.39923 | -0.17193 | -0.24808 | 0.0075824 | 8.8291 | 9.0589 | 1.9787 | 21.8174 | 22.0368 | 22.236 | 22.2937 | 22.1366 | 21.4849 | 20.3047 | 22.218 | 22.3867 | 22.4235 | 22.3734 | 22.0099 | 21.2587 | 22.2844 | 17.148 | 17.0862 | 16.1977 | 16.1883 | 16.1776 | 17.0637 | 16.737 | 22.4113 | 22.1752 | 21.7411 | 22.1016 | 21.8252 | 21.3386 | 21.9655 | 21.5592 | 20.9378 | 20.1568 | 20.4374 | 19.9965 | 19.7854 | 0.010235 | -0.34062 | 20.7438 | 22.0997 | 22.4155 | 20.1425 | 21.7044 | 22.1534 | 21.9744 | 21.7482 | 21.3179 | 21.8219 | 21.4946 | 21.0951 | 20.542 | 20.5344 | 20.4735 | 20.4834 | 20.1487 |  | 20.2545 | 19.7191 | 20.1362 | 19.7289 | 20.1143 | 20.3739 |  | 20.4624 |  |  | 20.3084 | 20.382 | 20.6322 | [5 empty] | 21.9748 | 20.3702 | 21.7142 | 22.1062 | 19.5713 | 21.2387 | 21.8795 | 19.3904 | 20.0312 | 21.2201 |  | 19.7052 | 21.0077 | 18.837 | 19.7427 | 20.8684 | 19.428 | 20.1694 | 18.9231 | 20.1852 | 19.1629 | 20.2821 | 18.7208 | 20.1499 | 21.1738 | 19.4218 | 19.8451 | 21.0363 | 18.9352 | 19.8377 | 20.8728 | 19.0155 | 20.2679 | 19.2954 | 19.9825 | 18.94 | 20.1493 | -0.051887 | 20.9496 | 0.04963 | 0.015203 | -27.117 | 3.0974 | -1.08 | -0.36 | 0.83136 | -0.47811 | -8.7187 | 0.78075 | 0.44996 | -16.7152 | 4.2671 | 0.42313 | 0.4311 | 0.4301 | 0.39285 | 0.46032 | 0.43861 | 0.42995
42838.4124 | -677 | 22.8997 | 22.8718 | 22.8602 | 22.7896 | 22.4377 | 21.781 | 22.7349 | 21.8537 | 22.3806 | 22.3963 | 22.389 | 22.0768 | 21.3002 | 22.2596 | 21.5962 | 21.7686 | 21.9204 | 21.0974 | 21.1954 | 21.4188 | 20.5093 | 20.6481 | 20.9479 | 21.9084 | 21.6847 | 21.3274 | 20.4519 | 20.56 | 20.56 | 22.0551 | 21.664 | 21.1981 | 22.0117 | 21.7549 | 21.3776 | 19.9585 | 20.5151 |  | 20.5886 | 20.2621 | 20.3649 | 19.2473 |  | 16.7161 | 16.7299 | 16.4945 | 16.7968 | 17.0054 | 17.5841 | 18.1443 | 15.9557 | 16.6227 | 16.0223 | 16.8633 | 17.8863 | 44.8948 | 49.3564 | 43.9746 | 21.3655 |  |  | 0.52855 | -0.27737 | -54.2424 | 0.51382 | 0.032988 | -197.8493 | 12.4763 | -0.36834 | -0.38541 | -0.13059 | 0.092299 | 8.8281 | 9.0579 | 1.978 | 21.8114 | 22.0345 | 22.2355 | 22.2974 | 22.1332 | 21.4789 | 20.2985 | 22.2134 | 22.3857 | 22.4244 | 22.373 | 22.0182 | 21.2566 | 22.2782 | 17.1532 | 17.0951 | 16.1711 | 16.1828 | 16.1773 | 17.0605 | 16.7386 | 22.4066 | 22.1776 | 21.7409 | 22.1082 | 21.8298 | 21.3386 | 21.9668 | 21.564 | 20.9413 | 20.1479 | 20.4438 | 19.9997 | 19.7972 | 0.03599 | -0.030401 | 20.743 | 22.1057 | 22.4174 | 20.1444 | 21.7076 | 22.1572 | 21.9784 | 21.7496 | 21.3237 | 21.8189 | 21.4929 | 21.095 | 20.5408 | 20.541 | 20.481 | 20.4795 | 20.153 |  | 20.2612 | 19.7083 | 20.138 | 19.731 | 20.1178 | 20.38 |  | 20.4603 |  |  | 20.305 | 20.3696 | 20.6142 | [5 empty] | 21.9576 | 20.3604 | 21.7053 | 22.0978 | 19.5683 | 21.2388 | 21.8803 | 19.3984 | 20.0385 | 21.2276 |  | 19.7186 | 21.0123 | 18.8492 | 19.7533 | 20.8798 | 19.4315 | 20.1808 | 18.9322 | 20.1926 | 19.1646 | 20.2986 | 18.7128 | 20.1517 | 21.1763 | 19.4179 | 19.8483 | 21.0426 | 18.942 | 19.8426 | 20.8836 | 19.0144 | 20.2735 | 19.2917 | 19.9883 | 18.9509 | 20.1557 | -0.051887 | 20.9495 | 0.049661 | 0.014781 | -27.0283 | 3.0974 | -1.01 | -0.03 | 0.8683 | -0.62489 | -8.7387 | 0.85052 | 0.21582 | -16.7141 | 4.1972 | 0.42324 | 0.43146 | 0.43016 | 0.39189 | 0.46347 | 0.43826 | 0.42933
42838.4125 | -676 | 22.9031 | 22.8672 | 22.8514 | 22.7927 | 22.4308 | 21.7766 | 22.7317 | 21.8486 | 22.3819 | 22.4001 | 22.3875 | 22.078 | 21.2982 | 22.2568 | 21.5931 | 21.7696 | 21.9054 | 21.0973 | 21.1985 | 21.4233 | 20.5073 | 20.6486 | 20.951 | 21.9223 | 21.6897 | 21.3275 | 20.4486 | 20.5588 | 20.5505 | 22.0536 | 21.6642 | 21.1933 | 22.0089 | 21.7579 | 21.3779 | 19.9527 | 20.5146 |  | 20.5858 | 20.257 | 20.3621 | 19.2484 |  | 16.714 | 16.735 | 16.5051 | 16.8138 | 17.0122 | 17.5757 | 18.134 | 15.9412 | 16.6315 | 16.0023 | 16.8691 | 17.893 | 44.916 | 49.4269 | 43.9963 | 21.3618 |  |  | 0.50621 | -0.34571 | -55.1828 | 0.65313 | 0.21632 | -197.8276 | 12.4145 | -0.58848 | -0.24958 | -0.12304 | -0.1714 | 8.8293 | 9.0588 | 1.9777 | 21.8195 | 22.0428 | 22.2383 | 22.3053 | 22.1461 | 21.487 | 20.3141 | 22.2312 | 22.3955 | 22.4288 | 22.3852 | 22.0238 | 21.2748 | 22.2912 | 17.172 | 17.116 | 16.1501 | 16.167 | 16.1752 | 17.0642 | 16.7419 | 22.4125 | 22.1783 | 21.7372 | 22.1055 | 21.8318 | 21.344 | 21.9632 | 21.5623 | 20.9478 | 20.145 | 20.4451 | 20.0091 | 19.7918 | 0.15002 | 0.036549 | 20.7458 | 22.1087 | 22.4207 | 20.1497 | 21.7113 | 22.1638 | 21.9844 | 21.7551 | 21.3214 | 21.825 | 21.4987 | 21.1048 | 20.5414 | 20.5503 | 20.4855 | 20.4889 | 20.1637 |  | 20.2618 | 19.7041 | 20.1385 | 19.7349 | 20.126 | 20.3814 |  | 20.4701 |  |  | 20.3063 | 20.3656 | 20.6168 | [5 empty] | 21.9641 | 20.3596 | 21.6955 | 22.0936 | 19.5684 | 21.2377 | 21.8681 | 19.3976 | 20.0333 | 21.2318 |  | 19.7134 | 21.0115 | 18.8341 | 19.7474 | 20.8796 | 19.4263 | 20.1773 | 18.9238 | 20.1798 | 19.1584 | 20.2912 | 18.7175 | 20.1539 | 21.171 | 19.4079 | 19.8397 | 21.0276 | 18.9312 | 19.8382 | 20.8675 | 19.0106 | 20.2683 | 19.2864 | 19.9784 | 18.9419 | 20.1525 | -0.25686 | 20.9481 | 0.049396 | 0.014796 | -26.9675 | 3.0974 | -1.04 | -0.24 | 0.84974 | -0.69765 | -8.8142 | 0.95891 | 0.55266 | -16.7129 | 4.1867 | 0.42296 | 0.4316 | 0.43033 | 0.39024 | 0.46619 | 0.43803 | 0.42938
42838.4125 | -675 | 22.9025 | 22.8699 | 22.8536 | 22.791 | 22.4371 | 21.7832 | 22.7385 | 21.8496 | 22.3918 | 22.4092 | 22.3947 | 22.0737 | 21.3041 | 22.2632 | 21.5875 | 21.7659 | 21.8995 | 21.0874 | 21.1899 | 21.4141 | 20.4943 | 20.633 | 20.9404 | 21.9165 | 21.6815 | 21.311 | 20.4548 | 20.5438 | 20.5417 | 22.0577 | 21.6697 | 21.196 | 22.0119 | 21.7545 | 21.3798 | 19.9556 | 20.5135 |  | 20.5876 | 20.2613 | 20.3623 | 19.2473 |  | 16.7114 | 16.7245 | 16.511 | 16.8235 | 16.9984 | 17.5754 | 18.1574 | 15.9082 | 16.6335 | 15.9967 | 16.8585 | 17.8818 | 44.9244 | 49.4944 | 44.0023 | 21.3564 |  |  | 0.37741 | -0.057233 | -54.5454 | 0.58545 | 0.30306 | -197.8552 | 12.5847 | -0.37952 | -0.35661 | -0.062829 | -0.082169 | 8.8289 | 9.0587 | 1.9789 | 21.8185 | 22.0516 | 22.244 | 22.3075 | 22.142 | 21.4879 | 20.31 | 22.2268 | 22.3962 | 22.4187 | 22.3834 | 22.0177 | 21.2645 | 22.2924 | 17.2042 | 17.1233 | 16.1473 | 16.1617 | 16.1618 | 17.0622 | 16.7467 | 22.4056 | 22.1719 | 21.7337 | 22.095 | 21.8161 | 21.3293 | 21.9588 | 21.5528 | 20.9328 | 20.1388 | 20.4314 | 20.0019 | 19.7679 | 0.10657 | -0.16963 | 20.7494 | 22.1128 | 22.4219 | 20.1459 | 21.7156 | 22.161 | 21.9846 | 21.7512 | 21.3226 | 21.8244 | 21.4976 | 21.0994 | 20.5397 | 20.5446 | 20.482 | 20.4925 | 20.16 |  | 20.2549 | 19.7059 | 20.1361 | 19.729 | 20.1282 | 20.3805 |  | 20.4596 |  |  | 20.31 | 20.3724 | 20.6129 | [5 empty] | 21.9714 | 20.3709 | 21.7033 | 22.0976 | 19.5586 | 21.2299 | 21.8733 | 19.4093 | 20.0351 | 21.2285 |  | 19.7061 | 21.0123 | 18.8302 | 19.7493 | 20.8763 | 19.425 | 20.1822 | 18.9224 | 20.1758 | 19.1613 | 20.2961 | 18.7167 | 20.1485 | 21.1793 | 19.4022 | 19.8365 | 21.0299 | 18.9312 | 19.8284 | 20.8653 | 19.0107 | 20.2688 | 19.2803 | 19.9738 | 18.9304 | 20.143 | -0.1118 | 20.9482 | 0.048886 | 0.014709 | -26.9748 | 3.0974 | -0.78 | -0.76 | 0.73371 | -0.28385 | -8.763 | 0.90785 | 0.65414 | -16.7141 | 4.2153 | 0.42283 | 0.43147 | 0.43056 | 0.38643 | 0.46705 | 0.43816 | 0.42984
42838.4125 | -674 | 22.8953 | 22.8723 | 22.8513 | 22.7906 | 22.4375 | 21.7888 | 22.7435 | 21.8502 | 22.3882 | 22.403 | 22.3909 | 22.0787 | 21.3016 | 22.2612 | 21.5805 | 21.7629 | 21.8931 | 21.0863 | 21.1826 | 21.4139 | 20.4876 | 20.6313 | 20.9332 | 21.9134 | 21.6741 | 21.3084 | 20.4391 | 20.545 | 20.5394 | 22.057 | 21.6727 | 21.1973 | 22.0165 | 21.751 | 21.377 | 19.9576 | 20.5191 |  | 20.5829 | 20.2621 | 20.3609 | 19.2388 |  | 16.7054 | 16.7213 | 16.4944 | 16.8074 | 16.987 | 17.5546 | 18.1611 | 15.8952 | 16.6166 | 15.9839 | 16.8556 | 17.8824 | 44.9425 | 49.5534 | 44.0297 | 21.3664 |  |  | 0.44313 | -0.27145 | -54.9869 | 0.50659 | 0.15981 | -197.8302 | 12.6957 | -0.30526 | -0.22973 | -0.035345 | -0.23824 | 8.8297 | 9.0594 | 1.9787 | 21.8236 | 22.0512 | 22.2437 | 22.3043 | 22.1568 | 21.4925 | 20.315 | 22.228 | 22.3974 | 22.4302 | 22.387 | 22.0236 | 21.2702 | 22.2997 | 17.2388 | 17.1314 | 16.1748 | 16.1712 | 16.1666 | 17.0625 | 16.7425 | 22.4038 | 22.1716 | 21.7343 | 22.1 | 21.8211 | 21.3359 | 21.9621 | 21.5559 | 20.9394 | 20.1456 | 20.4407 | 20.0133 | 19.7658 | -0.030657 | -0.14452 | 20.7497 | 22.1093 | 22.4215 | 20.1464 | 21.7126 | 22.1629 | 21.9758 | 21.7446 | 21.3246 | 21.8244 | 21.4934 | 21.0966 | 20.5387 | 20.5398 | 20.4888 | 20.4927 | 20.1658 |  | 20.2567 | 19.7166 | 20.1442 | 19.7182 | 20.1271 | 20.38 |  | 20.463 |  |  | 20.3175 | 20.3816 | 20.6255 | [5 empty] | 21.965 | 20.382 | 21.7048 | 22.0974 | 19.5641 | 21.2405 | 21.8781 | 19.3939 | 20.0313 | 21.2154 |  | 19.708 | 21.0087 | 18.8216 | 19.7308 | 20.8602 | 19.4116 | 20.1663 | 18.9241 | 20.1645 | 19.1474 | 20.2929 | 18.713 | 20.1637 | 21.1748 | 19.4173 | 19.83 | 21.0303 | 18.9355 | 19.8238 | 20.8611 | 19.0087 | 20.2698 | 19.2842 | 19.9747 | 18.9334 | 20.1465 | -0.16078 | 20.9494 | 0.048241 | 0.013947 | -26.9918 | 3.0974 | -0.81 | -0.71 | 0.79501 | -0.61818 | -8.7983 | 0.8445 | 0.475 | -16.7124 | 4.2337 | 0.42273 | 0.43144 | 0.43082 | 0.38261 | 0.46352 | 0.43846 | 0.43012
42838.4125 | -673 | 22.9064 | 22.8668 | 22.8601 | 22.7892 | 22.4363 | 21.7904 | 22.7372 | 21.8539 | 22.3919 | 22.4043 | 22.3917 | 22.0758 | 21.3024 | 22.2654 | 21.5847 | 21.7676 | 21.894 | 21.0911 | 21.1937 | 21.4179 | 20.4904 | 20.6369 | 20.9451 | 21.9139 | 21.6754 | 21.3156 | 20.4492 | 20.5439 | 20.5424 | 22.0514 | 21.6573 | 21.1976 | 22.0154 | 21.747 | 21.3696 | 19.9548 | 20.5208 |  | 20.5792 | 20.2582 | 20.3545 | 19.2366 |  | 16.7074 | 16.7274 | 16.497 | 16.8135 | 16.9933 | 17.543 | 18.1833 | 15.9182 | 16.6242 | 16.01 | 16.8561 | 17.8808 | 44.9751 | 49.6196 | 44.0586 | 21.3694 |  |  | 0.46415 | -0.061833 | -55.1394 | 0.55522 | 0.0619 | -197.8006 | 12.0945 | -0.18304 | 0.038235 | 0.007664 | -0.13008 | 8.8291 | 9.0588 | 1.9785 | 21.8163 | 22.0387 | 22.2423 | 22.3048 | 22.1481 | 21.4922 | 20.3141 | 22.2248 | 22.3955 | 22.4251 | 22.3854 | 22.0239 | 21.2663 | 22.2923 | 17.2626 | 17.1444 | 16.204 | 16.1763 | 16.1657 | 17.0655 | 16.748 | 22.4019 | 22.1692 | 21.7363 | 22.1015 | 21.8206 | 21.3368 | 21.9626 | 21.5563 | 20.9418 | 20.1438 | 20.433 | 20.0093 | 19.7685 | -0.10124 | -0.17533 | 20.7443 | 22.1042 | 22.4142 | 20.1428 | 21.7128 | 22.1667 | 21.9758 | 21.7456 | 21.3167 | 21.825 | 21.4916 | 21.0905 | 20.5386 | 20.5427 | 20.4924 | 20.4902 | 20.1607 |  | 20.2564 | 19.7142 | 20.1374 | 19.712 | 20.1211 | 20.3714 |  | 20.4647 |  |  | 20.3167 | 20.3777 | 20.6206 | [5 empty] | 21.9574 | 20.3737 | 21.705 | 22.0933 | 19.5544 | 21.2391 | 21.8806 | 19.3928 | 20.031 | 21.2221 |  | 19.7136 | 21.0068 | 18.8171 | 19.7345 | 20.8622 | 19.4117 | 20.1719 | 18.9276 | 20.173 | 19.148 | 20.2893 | 18.7321 | 20.1554 | 21.1763 | 19.4239 | 19.8356 | 21.0347 | 18.9314 | 19.8218 | 20.8638 | 19.0145 | 20.2739 | 19.2818 | 19.9666 | 18.9397 | 20.1592 | -0.11607 | 20.9494 | 0.046668 | 0.013417 | -27.0622 | 3.0974 | -0.64 | 0.01 | 0.81366 | -0.29504 | -8.8106 | 0.88411 | 0.29562 | -16.7108 | 4.1322 | 0.42286 | 0.43128 | 0.43079 | 0.38032 | 0.46091 | 0.43843 | 0.42998
42838.4125 | -672 | 22.9021 | 22.8659 | 22.8565 | 22.7904 | 22.4368 | 21.7865 | 22.7424 | 21.8583 | 22.3862 | 22.4005 | 22.3967 | 22.0826 | 21.3023 | 22.2558 | 21.5806 | 21.7678 | 21.9001 | 21.0862 | 21.1903 | 21.4176 | 20.4928 | 20.6433 | 20.9363 | 21.9136 | 21.6795 | 21.3139 | 20.4446 | 20.5486 | 20.5441 | 22.0501 | 21.6577 | 21.1899 | 22.0048 | 21.7497 | 21.3616 | 19.941 | 20.5145 |  | 20.5824 | 20.2536 | 20.3479 | 19.2233 |  | 16.7054 | 16.7293 | 16.5013 | 16.8051 | 16.9882 | 17.5524 | 18.1996 | 15.894 | 16.6176 | 16.0611 | 16.8486 | 17.8913 | 44.9979 | 49.6867 | 44.0908 | 21.3672 |  |  | 0.49964 | -0.25502 | -54.797 | 0.41788 | 0.19924 | -197.8414 | 12.4887 | -0.19092 | -0.1515 | 0.082143 | -0.057518 | 8.8288 | 9.0584 | 1.9779 | 21.8168 | 22.0405 | 22.2466 | 22.3042 | 22.1398 | 21.4874 | 20.312 | 22.2216 | 22.3972 | 22.4266 | 22.3773 | 22.0224 | 21.2655 | 22.2911 | 17.2672 | 17.1321 | 16.2148 | 16.187 | 16.1696 | 17.0668 | 16.748 | 22.3993 | 22.1783 | 21.7365 | 22.1015 | 21.8228 | 21.334 | 21.9639 | 21.5555 | 20.9354 | 20.1437 | 20.4419 | 20.0085 | 19.7638 | -0.19069 | -0.24476 | 20.743 | 22.106 | 22.4137 | 20.146 | 21.7132 | 22.1644 | 21.9835 | 21.7481 | 21.3165 | 21.8239 | 21.4933 | 21.0957 | 20.5378 | 20.5503 | 20.4896 | 20.4924 | 20.1554 |  | 20.2574 | 19.7161 | 20.1374 | 19.7198 | 20.1185 | 20.3811 |  | 20.4584 |  |  | 20.3208 | 20.3731 | 20.6253 | [5 empty] | 21.9656 | 20.3688 | 21.707 | 22.095 | 19.554 | 21.2372 | 21.8768 | 19.3895 | 20.0397 | 21.2161 |  | 19.7122 | 21.0065 | 18.8203 | 19.7257 | 20.8613 | 19.4201 | 20.1747 | 18.9261 | 20.1698 | 19.1462 | 20.2888 | 18.7195 | 20.1532 | 21.1637 | 19.4097 | 19.8278 | 21.0301 | 18.933 | 19.8159 | 20.8647 | 19.0104 | 20.272 | 19.2669 | 19.9606 | 18.9301 | 20.1522 | -0.082494 | 20.9486 | 0.046883 | 0.013235 | -27.0332 | 3.0974 | -0.62 | 0.15 | 0.84419 | -0.59919 | -8.7832 | 0.76701 | 0.53037 | -16.7128 | 4.199 | 0.42305 | 0.43123 | 0.43049 | 0.37996 | 0.4597 | 0.43834 | 0.43011
42838.4125 | -671 | 22.9061 | 22.8707 | 22.8643 | 22.7931 | 22.4349 | 21.7924 | 22.7502 | 21.8537 | 22.389 | 22.4073 | 22.3906 | 22.0823 | 21.2981 | 22.2639 | 21.5898 | 21.7707 | 21.9029 | 21.0928 | 21.1899 | 21.419 | 20.4996 | 20.6446 | 20.9394 | 21.9206 | 21.6875 | 21.323 | 20.4547 | 20.5586 | 20.5436 | 22.0544 | 21.6603 | 21.1923 | 22.004 | 21.7456 | 21.3699 | 19.9421 | 20.5184 |  | 20.5849 | 20.2504 | 20.3521 | 19.2164 |  | 16.714 | 16.7258 | 16.4978 | 16.808 | 17.0016 | 17.5886 | 18.1969 | 15.9106 | 16.6231 | 16.087 | 16.8526 | 17.8866 | 45.0114 | 49.7449 | 44.1202 | 21.3726 |  |  | 0.6764 | -0.42522 | -54.2122 | 0.6597 | 0.10987 | -197.8933 | 12.768 | -0.36112 | -0.40915 | 0.068506 | -0.0066528 | 8.8293 | 9.0586 | 1.9777 | 21.824 | 22.0474 | 22.2359 | 22.3041 | 22.1451 | 21.4839 | 20.3087 | 22.2275 | 22.393 | 22.4285 | 22.3851 | 22.0262 | 21.2628 | 22.2962 | 17.2627 | 17.1201 | 16.2168 | 16.1851 | 16.184 | 17.0717 | 16.7552 | 22.4026 | 22.175 | 21.7308 | 22.0996 | 21.8251 | 21.3328 | 21.96 | 21.5556 | 20.9332 | 20.1422 | 20.4469 | 20.0176 | 19.7765 | -0.10006 | -0.31931 | 20.7496 | 22.1036 | 22.4165 | 20.1431 | 21.7046 | 22.1613 | 21.9865 | 21.7437 | 21.3164 | 21.8249 | 21.4875 | 21.0907 | 20.5353 | 20.5424 | 20.4913 | 20.4966 | 20.1452 |  | 20.2597 | 19.7179 | 20.1417 | 19.7233 | 20.1175 | 20.3749 |  | 20.461 |  |  | 20.327 | 20.3709 | 20.6221 | [5 empty] | 21.9705 | 20.371 | 21.703 | 22.0916 | 19.5545 | 21.2364 | 21.8706 | 19.3989 | 20.0413 | 21.2247 |  | 19.723 | 21.0091 | 18.8196 | 19.7314 | 20.8721 | 19.4306 | 20.1793 | 18.935 | 20.1681 | 19.1477 | 20.2953 | 18.7257 | 20.1488 | 21.1588 | 19.4139 | 19.8221 | 21.0268 | 18.9344 | 19.8121 | 20.8573 | 19.0137 | 20.2657 | 19.2633 | 19.966 | 18.9349 | 20.146 | -0.074518 | 20.948 | 0.047172 | 0.012255 | -27.0429 | 3.0975 | -0.71 | -0.6 | 0.98224 | -0.77371 | -8.7362 | 0.96371 | 0.39387 | -16.7161 | 4.246 | 0.4234 | 0.43132 | 0.43036 | 0.38103 | 0.46032 | 0.43856 | 0.42971
42838.4125 | -670 | 22.9043 | 22.8738 | 22.8703 | 22.8007 | 22.4417 | 21.7898 | 22.7501 | 21.8567 | 22.3942 | 22.4058 | 22.3956 | 22.0818 | 21.3039 | 22.2665 | 21.5901 | 21.7635 | 21.8995 | 21.0892 | 21.1865 | 21.4121 | 20.4944 | 20.6413 | 20.9414 | 21.9144 | 21.6858 | 21.3196 | 20.4541 | 20.5573 | 20.5411 | 22.0539 | 21.6706 | 21.1993 | 22.0105 | 21.7585 | 21.3796 | 19.9482 | 20.5337 |  | 20.5873 | 20.2659 | 20.3675 | 19.2148 |  | 16.7056 | 16.7222 | 16.5049 | 16.809 | 17.004 | 17.5953 | 18.1608 | 15.8995 | 16.6291 | 16.1397 | 16.8561 | 17.8932 | 45.0318 | 49.8082 | 44.1802 | 21.3799 |  |  | 0.38333 | -0.14595 | -53.9815 | 0.70767 | 0.1263 | -197.8427 | 12.6504 | -0.37558 | -0.46111 | 0.061583 | 0.040219 | 8.829 | 9.0588 | 1.9789 | 21.8111 | 22.0463 | 22.2305 | 22.2962 | 22.1406 | 21.479 | 20.3098 | 22.2216 | 22.3871 | 22.4197 | 22.3864 | 22.0131 | 21.2574 | 22.2863 | 17.2444 | 17.0771 | 16.2079 | 16.1804 | 16.177 | 17.0678 | 16.7503 | 22.3919 | 22.1725 | 21.7316 | 22.0983 | 21.8219 | 21.3255 | 21.9535 | 21.5544 | 20.9298 | 20.1377 | 20.4349 | 20.01 | 19.782 | -0.043043 | -0.17838 | 20.7422 | 22.0967 | 22.409 | 20.1396 | 21.7021 | 22.157 | 21.9745 | 21.7426 | 21.3155 | 21.8261 | 21.4831 | 21.0859 | 20.531 | 20.5376 | 20.4897 | 20.4873 | 20.1477 |  | 20.2596 | 19.7258 | 20.1357 | 19.727 | 20.116 | 20.3699 |  | 20.4555 |  |  | 20.3218 | 20.3749 | 20.6252 | [5 empty] | 21.9699 | 20.3643 | 21.7072 | 22.0947 | 19.5513 | 21.2252 | 21.8755 | 19.3892 | 20.0335 | 21.2185 |  | 19.717 | 21.0017 | 18.8101 | 19.7228 | 20.8653 | 19.4219 | 20.1766 | 18.9305 | 20.1627 | 19.1438 | 20.2963 | 18.7349 | 20.1512 | 21.1624 | 19.4125 | 19.8255 | 21.0288 | 18.9392 | 19.81 | 20.8624 | 19.0275 | 20.2622 | 19.2694 | 19.9691 | 18.9393 | 20.1545 | -0.08435 | 20.9482 | 0.048057 | 0.014027 | -27.1044 | 3.0974 | -0.97 | 0.04 | 0.73943 | -0.45328 | -8.7175 | 0.99813 | 0.4223 | -16.7141 | 4.2264 | 0.42333 | 0.4309 | 0.43021 | 0.38261 | 0.46075 | 0.43881 | 0.42941
42838.4125 | -669 | 22.9021 | 22.8714 | 22.8651 | 22.7909 | 22.4431 | 21.7837 | 22.7368 | 21.8516 | 22.3899 | 22.4006 | 22.3887 | 22.0689 | 21.2937 | 22.2645 | 21.5943 | 21.7647 | 21.9035 | 21.0907 | 21.1927 | 21.4135 | 20.4979 | 20.6457 | 20.9438 | 21.9183 | 21.6886 | 21.3213 | 20.4518 | 20.5583 | 20.5419 | 22.0465 | 21.6664 | 21.1911 | 22.0048 | 21.7553 | 21.3713 | 19.9464 | 20.5289 |  | 20.5822 | 20.2588 | 20.3593 | 19.2031 |  | 16.6965 | 16.7165 | 16.5033 | 16.8138 | 16.9934 | 17.5642 | 18.1084 | 15.8846 | 16.6196 | 16.1555 | 16.8467 | 17.8881 | 45.0573 | 49.8591 | 44.2171 | 21.3752 |  |  | 0.46153 | -0.037521 | -53.4966 | 0.72344 | 0.1723 | -197.8552 | 12.8784 | -0.43932 | -0.46305 | -0.033247 | -0.022103 | 8.8293 | 9.0589 | 1.9786 | 21.8165 | 22.0415 | 22.23 | 22.304 | 22.1472 | 21.4848 | 20.3122 | 22.2189 | 22.3934 | 22.4207 | 22.3772 | 22.018 | 21.2628 | 22.2924 | 17.2306 | 17.0665 | 16.1878 | 16.1695 | 16.1717 | 17.0657 | 16.7515 | 22.3966 | 22.1743 | 21.7349 | 22.1011 | 21.8224 | 21.3265 | 21.9598 | 21.5535 | 20.9369 | 20.1424 | 20.4363 | 20.0157 | 19.7958 | 0.039922 | -0.16088 | 20.7516 | 22.1017 | 22.4167 | 20.1434 | 21.7093 | 22.1645 | 21.9837 | 21.7456 | 21.3222 | 21.8277 | 21.4914 | 21.0945 | 20.5346 | 20.5462 | 20.4985 | 20.494 | 20.1494 |  | 20.2701 | 19.7444 | 20.1396 | 19.7366 | 20.1235 | 20.3761 |  | 20.461 |  |  | 20.3181 | 20.376 | 20.6344 | [5 empty] | 21.9651 | 20.3573 | 21.7099 | 22.0944 | 19.5607 | 21.2354 | 21.8716 | 19.3823 | 20.0298 | 21.212 |  | 19.7135 | 21.002 | 18.7988 | 19.7198 | 20.861 | 19.4136 | 20.169 | 18.9316 | 20.1638 | 19.1395 | 20.2961 | 18.7342 | 20.1462 | 21.1589 | 19.4146 | 19.8244 | 21.0339 | 18.9425 | 19.8129 | 20.8707 | 19.0266 | 20.2659 | 19.2725 | 19.9678 | 18.9383 | 20.1538 | -0.12405 | 20.9495 | 0.048555 | 0.013889 | -27.0415 | 3.0975 | -1.14 | 0.18 | 0.81136 | -0.22983 | -8.6782 | 1.0092 | 0.49322 | -16.7137 | 4.2641 | 0.42364 | 0.43051 | 0.43019 | 0.38389 | 0.46313 | 0.43908 | 0.42918
42838.4125 | -668 | 22.8945 | 22.8703 | 22.8565 | 22.7867 | 22.4334 | 21.7836 | 22.7351 | 21.8555 | 22.3846 | 22.3952 | 22.3878 | 22.0721 | 21.2941 | 22.2558 | 21.5909 | 21.7689 | 21.9108 | 21.0969 | 21.1946 | 21.4206 | 20.5007 | 20.6436 | 20.9421 | 21.9256 | 21.6954 | 21.3246 | 20.4591 | 20.5657 | 20.5457 | 22.0488 | 21.6646 | 21.1891 | 22.0092 | 21.7524 | 21.3689 | 19.9528 | 20.5314 |  | 20.5723 | 20.2534 | 20.3545 | 19.1943 |  | 16.7057 | 16.7333 | 16.5102 | 16.8119 | 16.9987 | 17.5567 | 18.0657 | 15.8892 | 16.6219 | 16.1472 | 16.8522 | 17.8907 | 45.1033 | 49.9167 | 44.2708 | 21.3802 |  |  | 0.46021 | -0.1512 | -53.4414 | 0.57099 | 0.026416 | -197.8913 | 12.6419 | -0.46428 | -0.17894 | -0.25228 | -0.15022 | 8.8285 | 9.0582 | 1.9777 | 21.8201 | 22.0397 | 22.2326 | 22.2964 | 22.1367 | 21.4791 | 20.3039 | 22.2107 | 22.384 | 22.4261 | 22.3776 | 22.027 | 21.2618 | 22.2828 | 17.2207 | 17.0562 | 16.1728 | 16.1629 | 16.1478 | 17.0685 | 16.7534 | 22.3976 | 22.1685 | 21.7399 | 22.0976 | 21.8283 | 21.3292 | 21.9649 | 21.5539 | 20.9357 | 20.1498 | 20.4444 | 20.0254 | 19.7944 | -0.074696 | -0.034205 | 20.7636 | 22.114 | 22.4269 | 20.1463 | 21.7228 | 22.1709 | 21.9903 | 21.7506 | 21.3272 | 21.8347 | 21.5044 | 21.1087 | 20.5483 | 20.5485 | 20.5059 | 20.5037 | 20.1457 |  | 20.2597 | 19.7581 | 20.1322 | 19.7325 | 20.1251 | 20.3821 |  | 20.4651 |  |  | 20.3158 | 20.3671 | 20.631 | [5 empty] | 21.9555 | 20.3546 | 21.7036 | 22.0908 | 19.559 | 21.2321 | 21.8671 | 19.3771 | 20.0244 | 21.2077 |  | 19.7141 | 20.9982 | 18.791 | 19.7185 | 20.858 | 19.4095 | 20.159 | 18.935 | 20.1642 | 19.135 | 20.2904 | 18.7259 | 20.1372 | 21.1562 | 19.4077 | 19.8158 | 21.0292 | 18.9358 | 19.8161 | 20.8624 | 19.0256 | 20.2635 | 19.2633 | 19.9665 | 18.9378 | 20.1489 | -0.094181 | 20.948 | 0.048751 | 0.014665 | -27.0101 | 3.0975 | -1.17 | -0.03 | 0.8102 | -0.46138 | -8.674 | 0.89659 | 0.19312 | -16.7151 | 4.2247 | 0.42339 | 0.42989 | 0.43036 | 0.38533 | 0.465 | 0.43954 | 0.42947
42838.4126 | -667 | 22.9008 | 22.8715 | 22.8605 | 22.795 | 22.4371 | 21.7908 | 22.7468 | 21.8627 | 22.3935 | 22.4054 | 22.3947 | 22.0798 | 21.3 | 22.2699 | 21.5831 | 21.7563 | 21.8963 | 21.0918 | 21.1926 | 21.411 | 20.4867 | 20.6368 | 20.9383 | 21.9183 | 21.6793 | 21.3168 | 20.447 | 20.5571 | 20.5404 | 22.0551 | 21.6699 | 21.187 | 22.0101 | 21.7502 | 21.3734 | 19.9487 | 20.5313 |  | 20.5759 | 20.26 | 20.3615 | 19.1863 |  | 16.7102 | 16.74 | 16.511 | 16.8089 | 16.991 | 17.5515 | 18.032 | 15.8992 | 16.6228 | 16.0752 | 16.8586 | 17.8868 | 45.141 | 49.9711 | 44.3194 | 21.3746 |  |  | 0.30185 | -0.15317 | -53.4493 | 0.43759 | 0.04876 | -197.8578 | 12.724 | -0.58125 | -0.20151 | -0.20675 | -0.13928 | 8.8294 | 9.0587 | 1.9775 | 21.8094 | 22.041 | 22.2344 | 22.2942 | 22.1347 | 21.4815 | 20.3016 | 22.2112 | 22.3855 | 22.4264 | 22.3767 | 22.0116 | 21.2604 | 22.2926 | 17.197 | 17.0585 | 16.1602 | 16.1613 | 16.1365 | 17.0691 | 16.7551 | 22.4079 | 22.1683 | 21.7367 | 22.0973 | 21.821 | 21.3409 | 21.9669 | 21.5552 | 20.9399 | 20.1444 | 20.4489 | 20.0254 | 19.7952 | -0.033213 | -0.10382 | 20.7571 | 22.1113 | 22.4235 | 20.1385 | 21.7108 | 22.1673 | 21.9875 | 21.7545 | 21.323 | 21.8263 | 21.4958 | 21.0973 | 20.5401 | 20.5353 | 20.4969 | 20.4989 | 20.1427 |  | 20.2511 | 19.7678 | 20.1371 | 19.7172 | 20.1229 | 20.3743 |  | 20.4543 |  |  | 20.3061 | 20.3694 | 20.6336 | [5 empty] | 21.9615 | 20.3608 | 21.7014 | 22.094 | 19.5607 | 21.2258 | 21.8655 | 19.3783 | 20.0235 | 21.2084 |  | 19.7161 | 20.9996 | 18.7959 | 19.7167 | 20.8589 | 19.4052 | 20.1623 | 18.9366 | 20.1672 | 19.1348 | 20.289 | 18.7312 | 20.14 | 21.1568 | 19.406 | 19.826 | 21.0319 | 18.941 | 19.8153 | 20.8621 | 19.0315 | 20.2677 | 19.2619 | 19.9669 | 18.935 | 20.1537 | -0.019425 | 20.9491 | 0.049372 | 0.015616 | -27.1009 | 3.0975 | -1.21 | 0.27 | 0.65615 | -0.46438 | -8.6747 | 0.78491 | 0.26238 | -16.7135 | 4.2384 | 0.42319 | 0.42978 | 0.43071 | 0.38803 | 0.4666 | 0.43962 | 0.42926
42838.4126 | -666 | 22.8929 | 22.8713 | 22.8523 | 22.7861 | 22.4348 | 21.7868 | 22.7322 | 21.8474 | 22.3929 | 22.397 | 22.376 | 22.0725 | 21.2963 | 22.2572 | 21.5877 | 21.7613 | 21.9013 | 21.0899 | 21.193 | 21.4185 | 20.4951 | 20.6428 | 20.9373 | 21.9184 | 21.6777 | 21.3237 | 20.449 | 20.5591 | 20.5415 | 22.0537 | 21.6639 | 21.194 | 22.0075 | 21.7493 | 21.3683 | 19.9447 | 20.5366 |  | 20.5762 | 20.259 | 20.3678 | 19.1868 |  | 16.7116 | 16.7307 | 16.5029 | 16.7938 | 16.9751 | 17.5327 | 18.0298 | 15.906 | 16.6181 | 16.0656 | 16.8554 | 17.8877 | 45.198 | 50.018 | 44.3819 | 21.3811 |  |  | 0.4405 | -0.21494 | -53.8718 | 0.55522 | 0.078328 | -197.8821 | 12.7365 | -0.69953 | -0.47454 | -0.044996 | -0.029568 | 8.8288 | 9.0582 | 1.9778 | 21.8089 | 22.0421 | 22.2334 | 22.2988 | 22.1374 | 21.4877 | 20.3057 | 22.2167 | 22.3833 | 22.426 | 22.3796 | 22.0135 | 21.2607 | 22.2881 | 17.1761 | 17.0749 | 16.1329 | 16.1488 | 16.126 | 17.0677 | 16.7544 | 22.4037 | 22.183 | 21.7428 | 22.1112 | 21.83 | 21.3391 | 21.9651 | 21.5608 | 20.9411 | 20.1491 | 20.4454 | 20.0326 | 19.7893 | 0.12151 | 0.013916 | 20.758 | 22.1124 | 22.4254 | 20.1405 | 21.7106 | 22.1661 | 21.9875 | 21.7472 | 21.3236 | 21.8286 | 21.498 | 21.0973 | 20.5416 | 20.5372 | 20.4973 | 20.4969 | 20.1503 |  | 20.2588 | 19.7829 | 20.1374 | 19.7285 | 20.1179 | 20.3738 |  | 20.4563 |  |  | 20.3082 | 20.3799 | 20.6355 | [5 empty] | 21.9668 | 20.3641 | 21.7036 | 22.0937 | 19.5604 | 21.2314 | 21.8677 | 19.3777 | 20.0244 | 21.2109 |  | 19.723 | 20.9981 | 18.7898 | 19.712 | 20.8579 | 19.4075 | 20.1595 | 18.9424 | 20.1628 | 19.1332 | 20.2867 | 18.7369 | 20.1336 | 21.1598 | 19.412 | 19.8295 | 21.0338 | 18.9479 | 19.8193 | 20.8642 | 19.0281 | 20.2704 | 19.2631 | 19.9704 | 18.9302 | 20.1534 | -0.044652 | 20.9477 | 0.049439 | 0.01595 | -27.0298 | 3.0975 | -1.22 | 0.81 | 0.79266 | -0.55009 | -8.7088 | 0.88411 | 0.33253 | -16.714 | 4.2403 | 0.42323 | 0.42937 | 0.43023 | 0.39019 | 0.46956 | 0.43947 | 0.42959
42838.4126 | -665 | 22.9001 | 22.8746 | 22.8667 | 22.7917 | 22.4387 | 21.7842 | 22.7331 | 21.8492 | 22.3844 | 22.3989 | 22.3864 | 22.0806 | 21.306 | 22.2653 | 21.5808 | 21.7584 | 21.9002 | 21.0842 | 21.1859 | 21.4134 | 20.4891 | 20.6327 | 20.9299 | 21.9096 | 21.6799 | 21.3191 | 20.4506 | 20.5581 | 20.5343 | 22.0594 | 21.6729 | 21.1973 | 22.0151 | 21.7578 | 21.368 | 19.9631 | 20.5408 |  | 20.5834 | 20.2674 | 20.3605 | 19.1859 |  | 16.7163 | 16.742 | 16.512 | 16.7885 | 16.9621 | 17.5199 | 18.05 | 15.895 | 16.6201 | 16.0885 | 16.8558 | 17.8946 | 45.2561 | 50.0717 | 44.4371 | 21.3921 |  |  | 0.4037 | -0.1374 | -53.5104 | 0.56836 | 0.13024 | -197.8723 | 12.6839 | -0.66668 | -0.78551 | 0.037246 | 0.10949 | 8.8288 | 9.0585 | 1.9787 | 21.8148 | 22.0391 | 22.2294 | 22.3018 | 22.1394 | 21.4824 | 20.2995 | 22.2206 | 22.387 | 22.4246 | 22.3812 | 22.0213 | 21.2569 | 22.2835 | 17.1589 | 17.0773 | 16.1105 | 16.1166 | 16.1231 | 17.0736 | 16.7563 | 22.4047 | 22.1772 | 21.7386 | 22.1062 | 21.8284 | 21.3352 | 21.9648 | 21.5567 | 20.9364 | 20.145 | 20.4448 | 20.0322 | 19.7719 | 0.026946 | -0.053035 | 20.7608 | 22.1105 | 22.4221 | 20.1395 | 21.7154 | 22.1641 | 21.9867 | 21.7455 | 21.3221 | 21.8305 | 21.501 | 21.0981 | 20.5384 | 20.545 | 20.4991 | 20.4957 | 20.1482 |  | 20.261 | 19.8025 | 20.1382 | 19.7209 | 20.1198 | 20.3749 |  | 20.4601 |  |  | 20.3086 | 20.3815 | 20.6327 | [5 empty] | 21.9516 | 20.3577 | 21.7036 | 22.0906 | 19.5533 | 21.2298 | 21.8636 | 19.384 | 20.0311 | 21.2163 |  | 19.7361 | 21.0042 | 18.7981 | 19.7239 | 20.8661 | 19.4209 | 20.172 | 18.9608 | 20.1639 | 19.1419 | 20.2978 | 18.7416 | 20.132 | 21.1689 | 19.4175 | 19.8316 | 21.0366 | 18.942 | 19.8138 | 20.8616 | 19.0297 | 20.2717 | 19.2643 | 19.9757 | 18.9263 | 20.1572 | -0.17005 | 20.9465 | 0.047787 | 0.014919 | -27.0647 | 3.0975 | -1.36 | 0.06 | 0.75881 | -0.43983 | -8.6797 | 0.89454 | 0.42878 | -16.7132 | 4.2315 | 0.42337 | 0.42885 | 0.4305 | 0.39279 | 0.47227 | 0.44012 | 0.42993
42838.4126 | -664 | 22.8965 | 22.8634 | 22.8613 | 22.7926 | 22.4323 | 21.7921 | 22.7379 | 21.8493 | 22.3841 | 22.4001 | 22.3891 | 22.0816 | 21.3011 | 22.2635 | 21.5921 | 21.7585 | 21.8965 | 21.0873 | 21.1838 | 21.4114 | 20.4871 | 20.643 | 20.9349 | 21.9127 | 21.6745 | 21.3221 | 20.4433 | 20.5615 | 20.5335 | 22.0567 | 21.6655 | 21.1956 | 22.0142 | 21.753 | 21.3749 | 19.9549 | 20.5481 |  | 20.5894 | 20.2713 | 20.3596 | 19.1612 |  | 16.7168 | 16.7539 | 16.516 | 16.7952 | 16.9729 | 17.5321 | 18.0594 | 15.8846 | 16.622 | 16.1147 | 16.8596 | 17.8867 | 45.3103 | 50.1089 | 44.4754 | 21.3847 |  |  | 0.22628 | -0.2892 | -52.5569 | 0.32589 | 0.15718 | -197.867 | 12.9178 | -0.56417 | -0.4111 | 0.037246 | 0.028241 | 8.8295 | 9.0592 | 1.9782 | 21.8128 | 22.038 | 22.2318 | 22.2994 | 22.1396 | 21.4813 | 20.3029 | 22.2213 | 22.3925 | 22.4188 | 22.3744 | 22.0163 | 21.2592 | 22.2871 | 17.1317 | 17.0723 | 16.0922 | 16.0912 | 16.1056 | 17.0741 | 16.7565 | 22.411 | 22.1755 | 21.7432 | 22.1047 | 21.8285 | 21.3368 | 21.9705 | 21.562 | 20.9395 | 20.1491 | 20.4461 | 20.0362 | 19.78 | 0.13586 | -0.073767 | 20.7599 | 22.1136 | 22.4144 | 20.1302 | 21.7079 | 22.16 | 21.9811 | 21.7439 | 21.3155 | 21.8255 | 21.4958 | 21.0912 | 20.5234 | 20.541 | 20.4981 | 20.4967 | 20.1546 |  | 20.2664 | 19.8256 | 20.1353 | 19.7212 | 20.1244 | 20.3752 |  | 20.4577 |  |  | 20.3157 | 20.3928 | 20.6313 | [5 empty] | 21.9677 | 20.3568 | 21.7128 | 22.0944 | 19.5596 | 21.2369 | 21.8707 | 19.3777 | 20.0331 | 21.216 |  | 19.7361 | 20.9947 | 18.7879 | 19.7172 | 20.8699 | 19.4138 | 20.1639 | 18.9573 | 20.1724 | 19.1328 | 20.3012 | 18.7476 | 20.1346 | 21.1703 | 19.4043 | 19.828 | 21.033 | 18.9441 | 19.8159 | 20.8597 | 19.0303 | 20.2639 | 19.2643 | 19.9771 | 18.9191 | 20.1585 | -0.1669 | 20.9478 | 0.046717 | 0.014368 | -27.0594 | 3.0975 | -1.06 | -0.06 | 0.5681 | -0.6381 | -8.6022 | 0.67737 | 0.47106 | -16.7133 | 4.2704 | 0.42337 | 0.42811 | 0.43065 | 0.39587 | 0.47433 | 0.44053 | 0.42984
42838.4126 | -663 | 22.8926 | 22.8659 | 22.8597 | 22.7818 | 22.4284 | 21.7855 | 22.7341 | 21.8498 | 22.3836 | 22.3987 | 22.3864 | 22.0732 | 21.304 | 22.2583 | 21.5954 | 21.7627 | 21.9099 | 21.0875 | 21.1907 | 21.4179 | 20.4966 | 20.6336 | 20.9437 | 21.9205 | 21.6818 | 21.3198 | 20.4467 | 20.5618 | 20.5294 | 22.0555 | 21.6604 | 21.1942 | 22.0107 | 21.7531 | 21.3686 | 19.9527 | 20.5473 |  | 20.5833 | 20.2602 | 20.3607 | 19.15 |  | 16.7299 | 16.7597 | 16.5115 | 16.7899 | 16.9811 | 17.5431 | 18.0715 | 15.8717 | 16.6087 | 16.1913 | 16.8573 | 17.8913 | 45.3716 | 50.1619 | 44.5193 | 21.3887 |  |  | 0.24139 | -0.32008 | -51.6665 | 0.37583 | 0.27349 | -197.9104 | 13.3049 | -0.57271 | -0.42511 | -0.050451 | 0.0075824 | 8.8288 | 9.0586 | 1.9781 | 21.8071 | 22.0403 | 22.23 | 22.2944 | 22.1371 | 21.4769 | 20.3057 | 22.2174 | 22.3899 | 22.424 | 22.3773 | 22.0144 | 21.2576 | 22.2887 | 17.1086 | 17.0813 | 16.079 | 16.0796 | 16.089 | 17.0638 | 16.7561 | 22.4015 | 22.165 | 21.7402 | 22.1006 | 21.8243 | 21.3319 | 21.9622 | 21.558 | 20.9359 | 20.1436 | 20.4387 | 20.0312 | 19.7802 | 0.21745 | 0.03712 | 20.7598 | 22.1118 | 22.4168 | 20.1287 | 21.7101 | 22.1653 | 21.9854 | 21.7454 | 21.3236 | 21.8271 | 21.4945 | 21.0959 | 20.5284 | 20.5371 | 20.5027 | 20.4981 | 20.1468 |  | 20.2578 | 19.8386 | 20.1427 | 19.7161 | 20.1157 | 20.3728 |  | 20.4541 |  |  | 20.3262 | 20.401 | 20.6438 | [5 empty] | 21.9677 | 20.3695 | 21.7188 | 22.0919 | 19.5681 | 21.2405 | 21.8823 | 19.3748 | 20.0314 | 21.2164 |  | 19.7423 | 21.0097 | 18.7953 | 19.7158 | 20.8594 | 19.416 | 20.1702 | 18.9621 | 20.1689 | 19.1398 | 20.2966 | 18.7473 | 20.1273 | 21.1635 | 19.3989 | 19.8248 | 21.0292 | 18.9427 | 19.8171 | 20.8515 | 19.04 | 20.2602 | 19.2636 | 19.9775 | 18.9141 | 20.1577 | -0.19083 | 20.9475 | 0.048038 | 0.015536 | -27.0317 | 3.0976 | -1.3 | -0.33 | 0.58676 | -0.67132 | -8.5291 | 0.72743 | 0.62138 | -16.7155 | 4.334 | 0.4233 | 0.428 | 0.4305 | 0.39724 | 0.47574 | 0.44077 | 0.42965
42838.4126 | -662 | 22.9025 | 22.871 | 22.8652 | 22.7949 | 22.4323 | 21.7851 | 22.7385 | 21.855 | 22.3856 | 22.4036 | 22.394 | 22.0836 | 21.3032 | 22.2608 | 21.5773 | 21.7568 | 21.8976 | 21.0792 | 21.1844 | 21.4085 | 20.4814 | 20.6367 | 20.929 | 21.9057 | 21.6794 | 21.3147 | 20.4335 | 20.5587 | 20.5202 | 22.0507 | 21.6641 | 21.1908 | 22.0079 | 21.7476 | 21.3747 | 19.95 | 20.5471 |  | 20.5848 | 20.2615 | 20.3604 | 19.1466 |  | 16.7253 | 16.7448 | 16.5018 | 16.784 | 16.9919 | 17.5464 | 18.0771 | 15.8675 | 16.6063 | 16.1926 | 16.8567 | 17.8937 | 45.4483 | 50.2122 | 44.5736 | 21.3938 |  |  | 0.23679 | -0.30168 | -50.3937 | 0.66167 | 0.31818 | -197.869 | 13.4692 | -0.53591 | -0.2706 | -0.21347 | 0.091084 | 8.8295 | 9.0591 | 1.9781 | 21.8154 | 22.0363 | 22.2397 | 22.2972 | 22.1366 | 21.4817 | 20.3092 | 22.2146 | 22.3853 | 22.42 | 22.3804 | 22.0156 | 21.2584 | 22.2888 | 17.0966 | 17.083 | 16.1089 | 16.095 | 16.1138 | 17.0737 | 16.7665 | 22.4149 | 22.1758 | 21.7466 | 22.1081 | 21.8349 | 21.3477 | 21.9719 | 21.5562 | 20.9398 | 20.1546 | 20.4426 | 20.0351 | 19.7978 | 0.028912 | -0.022983 | 20.7725 | 22.113 | 22.4183 | 20.1313 | 21.7195 | 22.1729 | 21.9824 | 21.7482 | 21.3194 | 21.8215 | 21.4964 | 21.1009 | 20.5342 | 20.5489 | 20.5087 | 20.4965 | 20.1652 |  | 20.2644 | 19.8672 | 20.1447 | 19.7261 | 20.1269 | 20.3791 |  | 20.4607 |  |  | 20.3177 | 20.3977 | 20.6284 | [5 empty] | 21.9618 | 20.3536 | 21.7043 | 22.0899 | 19.5598 | 21.2252 | 21.865 | 19.3824 | 20.0288 | 21.2161 |  | 19.739 | 21.0072 | 18.8003 | 19.714 | 20.8629 | 19.4087 | 20.1754 | 18.9665 | 20.1653 | 19.1316 | 20.3012 | 18.7493 | 20.1303 | 21.1596 | 19.3998 | 19.8216 | 21.0217 | 18.9368 | 19.8114 | 20.8524 | 19.0212 | 20.255 | 19.2605 | 19.9663 | 18.9056 | 20.1522 | -0.081938 | 20.9468 | 0.048358 | 0.016821 | -26.9917 | 3.0976 | -1.19 | 0.27 | 0.58114 | -0.65172 | -8.4232 | 0.96518 | 0.67022 | -16.7138 | 4.3607 | 0.42301 | 0.42727 | 0.4306 | 0.39973 | 0.47364 | 0.44077 | 0.42953
42838.4126 | -661 | 22.9031 | 22.8738 | 22.859 | 22.7927 | 22.4383 | 21.7866 | 22.7383 | 21.8539 | 22.3882 | 22.4061 | 22.3961 | 22.0824 | 21.3053 | 22.2607 | 21.588 | 21.7521 | 21.9041 | 21.0886 | 21.1894 | 21.4116 | 20.4924 | 20.637 | 20.9345 | 21.918 | 21.6832 | 21.3154 | 20.4441 | 20.5635 | 20.5247 | 22.0424 | 21.6584 | 21.185 | 22.0042 | 21.7474 | 21.3687 | 19.9436 | 20.5456 |  | 20.5787 | 20.2544 | 20.3497 | 19.1503 |  | 16.7259 | 16.7454 | 16.5052 | 16.7999 | 17.0099 | 17.5573 | 18.0933 | 15.8937 | 16.6158 | 16.1566 | 16.8618 | 17.8912 | 45.5048 | 50.2588 | 44.6145 | 21.3844 |  |  | 0.33339 | -0.3076 | -49.3955 | 0.52368 | 0.4128 | -197.848 | 13.6472 | -0.50897 | -0.23168 | -0.2571 | 0.032754 | 8.8288 | 9.0583 | 1.9784 | 21.8174 | 22.0375 | 22.2337 | 22.308 | 22.1395 | 21.4772 | 20.3109 | 22.2218 | 22.3924 | 22.4228 | 22.3785 | 22.0225 | 21.2663 | 22.2862 | 17.0841 | 17.1093 | 16.1394 | 16.0895 | 16.1077 | 17.0687 | 16.7689 | 22.4059 | 22.1737 | 21.743 | 22.1123 | 21.8291 | 21.3341 | 21.9654 | 21.5528 | 20.9456 | 20.1571 | 20.4499 | 20.0272 | 19.7855 | -0.081773 | 0.13298 | 20.7706 | 22.1044 | 22.4117 | 20.1346 | 21.718 | 22.1656 | 21.9748 | 21.7454 | 21.3065 | 21.8205 | 21.4901 | 21.0896 | 20.5369 | 20.55 | 20.5005 | 20.4919 | 20.1647 |  | 20.2564 | 19.8774 | 20.1354 | 19.7164 | 20.1183 | 20.3788 |  | 20.4575 |  |  | 20.3248 | 20.4 | 20.6346 | [5 empty] | 21.9703 | 20.3412 | 21.7028 | 22.0936 | 19.5672 | 21.2269 | 21.8638 | 19.379 | 20.0367 | 21.2179 |  | 19.7435 | 21.0068 | 18.7959 | 19.7203 | 20.8633 | 19.4128 | 20.1639 | 18.9686 | 20.1737 | 19.121 | 20.2888 | 18.7433 | 20.1366 | 21.1606 | 19.4005 | 19.8218 | 21.031 | 18.9329 | 19.8108 | 20.8494 | 19.0216 | 20.2698 | 19.2628 | 19.963 | 18.9157 | 20.1502 | 0.068688 | 20.9475 | 0.048346 | 0.017569 | -27.0429 | 3.0976 | -1.08 | -0.02 | 0.68957 | -0.65808 | -8.3393 | 0.85866 | 0.76342 | -16.7132 | 4.3895 | 0.42275 | 0.42668 | 0.43058 | 0.40053 | 0.47053 | 0.44045 | 0.42996
42838.4126 | -660 | 22.9017 | 22.8738 | 22.8576 | 22.7881 | 22.4439 | 21.7905 | 22.7413 | 21.8475 | 22.3938 | 22.4078 | 22.3925 | 22.0823 | 21.3059 | 22.2651 | 21.5908 | 21.7627 | 21.8978 | 21.095 | 21.189 | 21.4151 | 20.4939 | 20.6456 | 20.9361 | 21.9204 | 21.687 | 21.3157 | 20.4513 | 20.5633 | 20.532 | 22.0502 | 21.6685 | 21.1891 | 22.0109 | 21.751 | 21.3678 | 19.9522 | 20.5499 |  | 20.5852 | 20.2554 | 20.3561 | 19.1688 |  | 16.7185 | 16.7414 | 16.4939 | 16.7769 | 17.0235 | 17.5495 | 18.0494 | 15.8756 | 16.6081 | 16.1234 | 16.8613 | 17.89 | 45.574 | 50.2997 | 44.6427 | 21.3821 |  |  | 0.41947 | -0.19457 | -49.4507 | 0.49608 | 0.20975 | -197.842 | 13.6775 | -0.41697 | -0.33793 | 0.021511 | -0.041546 | 8.8296 | 9.0592 | 1.9786 | 21.8188 | 22.0468 | 22.2367 | 22.3143 | 22.1417 | 21.4827 | 20.3142 | 22.2264 | 22.4023 | 22.4378 | 22.3851 | 22.0247 | 21.275 | 22.2972 | 17.0748 | 17.1519 | 16.2113 | 16.1052 | 16.1111 | 17.0778 | 16.7704 | 22.4046 | 22.171 | 21.7362 | 22.1041 | 21.823 | 21.3358 | 21.9618 | 21.5541 | 20.9434 | 20.1483 | 20.4483 | 20.0249 | 19.7745 | 0.052898 | -0.022983 | 20.7678 | 22.1033 | 22.4205 | 20.13 | 21.7169 | 22.1707 | 21.98 | 21.7467 | 21.314 | 21.8332 | 21.4921 | 21.095 | 20.5375 | 20.5473 | 20.4999 | 20.4947 | 20.168 |  | 20.254 | 19.8891 | 20.1347 | 19.7145 | 20.1184 | 20.3728 |  | 20.4485 |  |  | 20.3176 | 20.3979 | 20.6472 | [5 empty] | 21.9709 | 20.3406 | 21.7065 | 22.1043 | 19.57 | 21.2308 | 21.8747 | 19.3635 | 20.026 | 21.2158 |  | 19.7475 | 21.0017 | 18.7942 | 19.7123 | 20.8537 | 19.3979 | 20.1546 | 18.9577 | 20.1623 | 19.1149 | 20.2813 | 18.7555 | 20.1374 | 21.1646 | 19.3973 | 19.8188 | 21.0314 | 18.9338 | 19.8115 | 20.8473 | 19.0182 | 20.2591 | 19.2616 | 19.972 | 18.9041 | 20.154 | -0.14742 | 20.9471 | 0.047485 | 0.016836 | -27.0329 | 3.0977 | -1.21 | -0.08 | 0.77349 | -0.52339 | -8.3439 | 0.83572 | 0.54418 | -16.7128 | 4.3943 | 0.42258 | 0.42633 | 0.43064 | 0.40262 | 0.46272 | 0.44023 | 0.42997
42838.4127 | -659 | 22.8913 | 22.8652 | 22.8522 | 22.7822 | 22.4297 | 21.7763 | 22.7307 | 21.8471 | 22.3807 | 22.3949 | 22.3744 | 22.0727 | 21.294 | 22.2607 | 21.5959 | 21.7625 | 21.9028 | 21.0907 | 21.1853 | 21.4123 | 20.493 | 20.6389 | 20.9353 | 21.9133 | 21.6865 | 21.3206 | 20.4496 | 20.5532 | 20.5292 | 22.0575 | 21.6621 | 21.1937 | 22.0134 | 21.7483 | 21.3779 | 19.9515 | 20.5516 |  | 20.5836 | 20.2631 | 20.3594 | 19.1764 |  | 16.7217 | 16.7448 | 16.5022 | 16.7869 | 17.0184 | 17.5489 | 18.0257 | 15.8679 | 16.6132 | 16.1192 | 16.8691 | 17.8899 | 45.6455 | 50.3271 | 44.6521 | 21.3885 |  |  | 0.28147 | -0.39499 | -50.0086 | 0.60319 | 0.18478 | -197.846 | 13.8174 | -0.57534 | -0.17524 | -0.021498 | -0.024881 | 8.8292 | 9.059 | 1.9783 | 21.8182 | 22.0502 | 22.2372 | 22.3104 | 22.146 | 21.4834 | 20.3055 | 22.2292 | 22.3953 | 22.4285 | 22.3864 | 22.0251 | 21.269 | 22.2995 | 17.0566 | 17.1578 | 16.2672 | 16.1227 | 16.1203 | 17.0758 | 16.7654 | 22.4046 | 22.167 | 21.7363 | 22.0966 | 21.8173 | 21.3254 | 21.9634 | 21.5524 | 20.9343 | 20.1436 | 20.4409 | 20.0217 | 19.7662 | 0.10146 | -0.042384 | 20.7797 | 22.1046 | 22.423 | 20.1335 | 21.7126 | 22.1725 | 21.9829 | 21.7506 | 21.3234 | 21.8307 | 21.5003 | 21.0929 | 20.5367 | 20.5451 | 20.4983 | 20.495 | 20.1685 |  | 20.2519 | 19.9131 | 20.1394 | 19.7042 | 20.1203 | 20.3736 |  | 20.4494 |  |  | 20.3197 | 20.4087 | 20.6353 | [5 empty] | 21.9667 | 20.3401 | 21.7118 | 22.102 | 19.5623 | 21.2326 | 21.8669 | 19.366 | 20.0252 | 21.2177 |  | 19.7597 | 20.9964 | 18.7961 | 19.7162 | 20.8573 | 19.4066 | 20.1544 | 18.9683 | 20.1706 | 19.1327 | 20.2899 | 18.7583 | 20.147 | 21.1703 | 19.4073 | 19.8235 | 21.0389 | 18.9352 | 19.82 | 20.8616 | 19.0223 | 20.2722 | 19.2657 | 19.9726 | 18.9193 | 20.1583 | -0.12034 | 20.9468 | 0.046263 | 0.01383 | -27.0506 | 3.0976 | -1.21 | 0.17 | 0.63361 | -0.74573 | -8.3909 | 0.92154 | 0.51076 | -16.7129 | 4.4167 | 0.4225 | 0.42582 | 0.43099 | 0.40441 | 0.45592 | 0.43999 | 0.43004
42838.4127 | -658 | 22.9019 | 22.8613 | 22.8536 | 22.7876 | 22.4284 | 21.7825 | 22.7373 | 21.8436 | 22.3765 | 22.4001 | 22.3836 | 22.0716 | 21.2972 | 22.2539 | 21.5953 | 21.7626 | 21.9024 | 21.0851 | 21.191 | 21.4086 | 20.4932 | 20.6395 | 20.9408 | 21.9143 | 21.6821 | 21.3156 | 20.4452 | 20.5655 | 20.5307 | 22.0463 | 21.6627 | 21.1885 | 22.0089 | 21.7449 | 21.3704 | 19.9492 | 20.5464 |  | 20.578 | 20.2636 | 20.3508 | 19.1779 |  | 16.7205 | 16.7356 | 16.4937 | 16.7783 | 17.0042 | 17.5423 | 18.0052 | 15.8541 | 16.6105 | 16.0976 | 16.858 | 17.8908 | 45.7199 | 50.3583 | 44.6941 | 21.386 |  |  | 0.28607 | -0.60461 | -50.0106 | 0.62816 | 0.34183 | -197.8775 | 13.3384 | -0.5208 | 0.0287 | -0.70419 | 0.029456 | 8.829 | 9.0585 | 1.9781 | 21.8174 | 22.0403 | 22.233 | 22.2955 | 22.1385 | 21.4746 | 20.3076 | 22.2193 | 22.3837 | 22.4165 | 22.3799 | 22.0248 | 21.2623 | 22.2914 | 17.0388 | 17.1301 | 16.3068 | 16.1256 | 16.1317 | 17.0775 | 16.7719 | 22.4011 | 22.1692 | 21.7436 | 22.099 | 21.8246 | 21.3317 | 21.9622 | 21.5561 | 20.9402 | 20.1479 | 20.4343 | 20.0324 | 19.768 | 0.021835 | 0.044157 | 20.7844 | 22.114 | 22.4189 | 20.1358 | 21.713 | 22.162 | 21.9855 | 21.7466 | 21.3178 | 21.8211 | 21.4999 | 21.0943 | 20.5401 | 20.5475 | 20.4987 | 20.499 | 20.1607 |  | 20.2586 | 19.9234 | 20.1437 | 19.7094 | 20.1252 | 20.3765 |  | 20.4651 |  |  | 20.3137 | 20.3931 | 20.6345 | [5 empty] | 21.9573 | 20.3306 | 21.6991 | 22.093 | 19.5566 | 21.2239 | 21.8612 | 19.375 | 20.0378 | 21.2197 |  | 19.7647 | 21.0041 | 18.7962 | 19.72 | 20.8698 | 19.4079 | 20.1615 | 18.9669 | 20.1739 | 19.128 | 20.2977 | 18.7655 | 20.1439 | 21.1849 | 19.4062 | 19.8181 | 21.0395 | 18.9327 | 19.8148 | 20.8581 | 19.0331 | 20.267 | 19.2599 | 19.9754 | 18.9133 | 20.1609 | -0.12906 | 20.9467 | 0.047197 | 0.013003 | -27.0641 | 3.0977 | -1.39 | -0.66 | 0.63877 | -0.92261 | -8.391 | 0.9404 | 0.69469 | -16.7141 | 4.3395 | 0.42293 | 0.42568 | 0.431 | 0.40659 | 0.45228 | 0.43987 | 0.43014
42838.4127 | -657 | 22.8954 | 22.8647 | 22.8525 | 22.7878 | 22.4365 | 21.7791 | 22.7313 | 21.8462 | 22.3869 | 22.3917 | 22.3823 | 22.0741 | 21.3016 | 22.2594 | 21.5933 | 21.7631 | 21.9047 | 21.0935 | 21.1862 | 21.4149 | 20.4938 | 20.636 | 20.9414 | 21.9185 | 21.6871 | 21.323 | 20.4449 | 20.5687 | 20.5341 | 22.0531 | 21.6708 | 21.1905 | 22.0067 | 21.7553 | 21.3766 | 19.9586 | 20.5527 |  | 20.5878 | 20.2555 | 20.3565 | 19.1967 |  | 16.7184 | 16.7347 | 16.4877 | 16.7721 | 16.9947 | 17.5372 | 18.0028 | 15.8416 | 16.6087 | 16.0241 | 16.8678 | 17.8875 | 45.7806 | 50.3782 | 44.7484 | 21.3866 |  |  | 0.27096 | -0.072349 | -49.8299 | 0.61962 | 0.33658 | -197.8821 | 13.3055 | -0.4794 | 0.047965 | -0.41319 | -0.0004032 | 8.829 | 9.0588 | 1.9778 | 21.821 | 22.0406 | 22.2342 | 22.3018 | 22.1429 | 21.4812 | 20.3129 | 22.2205 | 22.3922 | 22.422 | 22.377 | 22.0214 | 21.2646 | 22.2966 | 17.0139 | 17.0748 | 16.3239 | 16.139 | 16.1285 | 17.0763 | 16.7699 | 22.4048 | 22.1786 | 21.7409 | 22.1051 | 21.8275 | 21.3372 | 21.9666 | 21.5522 | 20.9433 | 20.1484 | 20.4495 | 20.0266 | 19.771 | -0.070764 | 0.07478 | 20.7844 | 22.1059 | 22.4144 | 20.1337 | 21.7075 | 22.1599 | 21.9789 | 21.7444 | 21.3201 | 21.8173 | 21.4963 | 21.0937 | 20.5399 | 20.5374 | 20.495 | 20.4963 | 20.1532 |  | 20.254 | 19.942 | 20.1471 | 19.7054 | 20.1214 | 20.3842 |  | 20.4624 |  |  | 20.3145 | 20.3822 | 20.65 | [5 empty] | 21.9566 | 20.3461 | 21.7035 | 22.0891 | 19.5559 | 21.2297 | 21.8638 | 19.377 | 20.031 | 21.2162 |  | 19.7673 | 21.0027 | 18.8022 | 19.7161 | 20.8631 | 19.4063 | 20.1634 | 18.9702 | 20.1742 | 19.1234 | 20.2957 | 18.7648 | 20.1439 | 21.1776 | 19.4075 | 19.8163 | 21.0363 | 18.9222 | 19.8058 | 20.8582 | 19.0247 | 20.2713 | 19.2539 | 19.9716 | 18.9094 | 20.158 | -0.034821 | 20.9469 | 0.048856 | 0.014847 | -27.0841 | 3.0977 | -1.27 | -0.28 | 0.62167 | -0.31915 | -8.3758 | 0.93399 | 0.68932 | -16.7141 | 4.3341 | 0.42299 | 0.42528 | 0.43099 | 0.40921 | 0.45015 | 0.43966 | 0.43007
42838.4127 | -656 | 22.8981 | 22.8572 | 22.8506 | 22.7864 | 22.4312 | 21.7774 | 22.7335 | 21.842 | 22.3811 | 22.3975 | 22.3878 | 22.0755 | 21.3002 | 22.2531 | 21.5835 | 21.7577 | 21.9005 | 21.0888 | 21.1828 | 21.4041 | 20.4936 | 20.6305 | 20.942 | 21.913 | 21.6809 | 21.3174 | 20.4446 | 20.5662 | 20.5303 | 22.0553 | 21.6701 | 21.1969 | 22.0064 | 21.7566 | 21.3723 | 19.9604 | 20.558 |  | 20.5842 | 20.2657 | 20.3638 | 19.1968 |  | 16.716 | 16.7354 | 16.4833 | 16.7596 | 16.9871 | 17.5337 | 17.9847 | 15.8359 | 16.6111 | 15.9796 | 16.8562 | 17.8889 | 45.8609 | 50.3983 | 44.7951 | 21.3845 |  |  | 0.40633 | -0.165 | -49.6452 | 0.6919 | 0.20844 | -197.8473 | 13.3949 | -0.40843 | -0.11239 | 0.0040974 | -0.071753 | 8.8287 | 9.0582 | 1.9785 | 21.8159 | 22.0411 | 22.2413 | 22.3015 | 22.1374 | 21.4855 | 20.3149 | 22.2135 | 22.3929 | 22.4267 | 22.3728 | 22.0221 | 21.2595 | 22.2935 | 16.9888 | 17.0754 | 16.3297 | 16.1722 | 16.1546 | 17.0779 | 16.7713 | 22.3974 | 22.1681 | 21.733 | 22.1019 | 21.8192 | 21.3404 | 21.9603 | 21.5548 | 20.9399 | 20.1423 | 20.4374 | 20.0229 | 19.7644 | -0.0047062 | 0.10103 | 20.7831 | 22.0992 | 22.4129 | 20.137 | 21.7113 | 22.1715 | 21.9735 | 21.7458 | 21.3171 | 21.8236 | 21.4941 | 21.0868 | 20.5409 | 20.5481 | 20.4923 | 20.4891 | 20.1546 |  | 20.2521 | 19.9488 | 20.1417 | 19.6983 | 20.1064 | 20.386 |  | 20.4491 |  |  | 20.3092 | 20.3826 | 20.6425 | [5 empty] | 21.9521 | 20.3419 | 21.6998 | 22.0858 | 19.5443 | 21.2252 | 21.8556 | 19.3795 | 20.0282 | 21.2142 |  | 19.7695 | 21.0004 | 18.8055 | 19.7112 | 20.8611 | 19.4058 | 20.1637 | 18.9697 | 20.1714 | 19.1212 | 20.2988 | 18.7613 | 20.1457 | 21.1721 | 19.408 | 19.8132 | 21.0327 | 18.9225 | 19.8092 | 20.8533 | 19.0191 | 20.2617 | 19.2525 | 19.9668 | 18.905 | 20.1576 | -0.15039 | 20.9462 | 0.048782 | 0.014324 | -27.0497 | 3.0977 | -1.05 | 0.04 | 0.76128 | -0.48197 | -8.3602 | 0.98696 | 0.54245 | -16.7125 | 4.3486 | 0.42289 | 0.42491 | 0.43068 | 0.4122 | 0.44965 | 0.43972 | 0.43005
42838.4127 | -655 | 22.8917 | 22.8559 | 22.8494 | 22.7864 | 22.4351 | 21.7764 | 22.7337 | 21.8452 | 22.3873 | 22.3964 | 22.3884 | 22.0735 | 21.2982 | 22.2565 | 21.5771 | 21.7571 | 21.8953 | 21.0802 | 21.1831 | 21.4074 | 20.4987 | 20.6272 | 20.9357 | 21.9117 | 21.676 | 21.3124 | 20.4407 | 20.5598 | 20.5326 | 22.0535 | 21.6598 | 21.1914 | 22.0019 | 21.7476 | 21.3639 | 19.9556 | 20.5508 |  | 20.5785 | 20.2565 | 20.3549 | 19.1752 |  | 16.7037 | 16.7174 | 16.4758 | 16.7555 | 16.9873 | 17.5217 | 17.9561 | 15.8007 | 16.6074 | 15.952 | 16.857 | 17.8923 | 45.932 | 50.4095 | 44.8444 | 21.3871 |  |  | 0.20262 | -0.1788 | -49.2247 | 0.64459 | -0.11158 | -197.8289 | 13.7215 | -0.48006 | -0.03727 | -0.31438 | -0.17869 | 8.8291 | 9.059 | 1.9787 | 21.813 | 22.0392 | 22.2293 | 22.2881 | 22.133 | 21.473 | 20.3055 | 22.2157 | 22.3824 | 22.4169 | 22.3671 | 22.021 | 21.2562 | 22.2906 | 16.9802 | 17.0784 | 16.3377 | 16.2019 | 16.2062 | 17.0841 | 16.7786 | 22.4074 | 22.1745 | 21.7358 | 22.1081 | 21.8272 | 21.3381 | 21.9659 | 21.5565 | 20.9468 | 20.1558 | 20.4413 | 20.0335 | 19.7691 | -0.068798 | 0.12499 | 20.7803 | 22.1086 | 22.4102 | 20.1301 | 21.7126 | 22.1647 | 21.975 | 21.7444 | 21.3113 | 21.8207 | 21.4932 | 21.0895 | 20.5374 | 20.5428 | 20.4936 | 20.4908 | 20.161 |  | 20.2526 | 19.9614 | 20.1428 | 19.6916 | 20.1216 | 20.3811 |  | 20.4537 |  |  | 20.3019 | 20.3893 | 20.637 | [5 empty] | 21.9515 | 20.3473 | 21.6934 | 22.0877 | 19.5514 | 21.2212 | 21.8598 | 19.3837 | 20.0315 | 21.2275 |  | 19.7765 | 21.0092 | 18.8077 | 19.721 | 20.8757 | 19.4123 | 20.1695 | 18.9806 | 20.1741 | 19.1276 | 20.3017 | 18.7664 | 20.1464 | 21.1683 | 19.4102 | 19.8187 | 21.0293 | 18.9217 | 19.8133 | 20.857 | 19.0226 | 20.266 | 19.2555 | 19.9722 | 18.9062 | 20.1553 | -0.24703 | 20.9485 | 0.049169 | 0.015587 | -26.9831 | 3.0976 | -0.79 | -0.01 | 0.53759 | -0.50171 | -8.3245 | 0.95259 | -0.39688 | -16.7114 | 4.4012 | 0.42273 | 0.42459 | 0.43138 | 0.41387 | 0.44962 | 0.44016 | 0.43037
42838.4127 | -654 | 22.8925 | 22.8574 | 22.8516 | 22.7843 | 22.4271 | 21.7744 | 22.7321 | 21.841 | 22.3796 | 22.3987 | 22.384 | 22.0733 | 21.2936 | 22.257 | 21.5848 | 21.7658 | 21.8949 | 21.09 | 21.1937 | 21.4128 | 20.5071 | 20.6388 | 20.9371 | 21.9181 | 21.6843 | 21.3248 | 20.449 | 20.5739 | 20.5328 | 22.0503 | 21.6606 | 21.1931 | 22 | 21.7466 | 21.3649 | 19.9496 | 20.5455 |  | 20.5793 | 20.2516 | 20.3515 | 19.1557 |  | 16.7112 | 16.722 | 16.4795 | 16.7539 | 16.9819 | 17.5101 | 17.9255 | 15.7836 | 16.6099 | 15.9323 | 16.8542 | 17.8868 | 46.0009 | 50.4209 | 44.8858 | 21.3915 |  |  | 0.42341 | -0.30103 | -49.2273 | 0.7379 | 0.11118 | -197.8328 | 13.8575 | -0.34666 | 0.11335 | -0.43396 | -0.16393 | 8.8283 | 9.058 | 1.9783 | 21.8103 | 22.0352 | 22.2264 | 22.2922 | 22.1319 | 21.4747 | 20.3068 | 22.2126 | 22.3871 | 22.4171 | 22.3672 | 22.0119 | 21.2561 | 22.2784 | 16.9608 | 17.0877 | 16.3382 | 16.2136 | 16.2358 | 17.0803 | 16.7785 | 22.4023 | 22.1752 | 21.7405 | 22.1079 | 21.8261 | 21.3342 | 21.9711 | 21.5612 | 20.9441 | 20.1514 | 20.4407 | 20.0342 | 19.7708 | -0.02417 | 0.20316 | 20.7902 | 22.1102 | 22.4141 | 20.1295 | 21.7172 | 22.1627 | 21.9781 | 21.7449 | 21.3185 | 21.8277 | 21.4895 | 21.0935 | 20.5427 | 20.5389 | 20.498 | 20.4974 | 20.1735 |  | 20.2553 | 19.9773 | 20.1528 | 19.6978 | 20.1192 | 20.3859 |  | 20.4582 |  |  | 20.3075 | 20.403 | 20.6459 | [5 empty] | 21.9639 | 20.3545 | 21.7027 | 22.094 | 19.553 | 21.2215 | 21.8682 | 19.3858 | 20.0287 | 21.2278 |  | 19.7841 | 21.02 | 18.8122 | 19.7247 | 20.8821 | 19.4061 | 20.169 | 18.9853 | 20.1752 | 19.1292 | 20.2996 | 18.7771 | 20.1524 | 21.1751 | 19.4095 | 19.822 | 21.0372 | 18.9262 | 19.8185 | 20.8583 | 19.0268 | 20.2633 | 19.2567 | 19.9682 | 18.9046 | 20.1596 | -0.070808 | 20.9471 | 0.048499 | 0.015747 | -27.142 | 3.0977 | -0.86 | 0.1 | 0.77712 | -0.65099 | -8.3248 | 1.0192 | 0.39617 | -16.7112 | 4.4229 | 0.42247 | 0.42449 | 0.43113 | 0.41559 | 0.44956 | 0.4405 | 0.43018
42838.4127 | -653 | 22.8917 | 22.8634 | 22.8562 | 22.7886 | 22.4301 | 21.7822 | 22.7294 | 21.8462 | 22.3815 | 22.4022 | 22.3873 | 22.0729 | 21.3038 | 22.2589 | 21.5841 | 21.7654 | 21.8997 | 21.0938 | 21.1928 | 21.4122 | 20.4962 | 20.6393 | 20.9395 | 21.9125 | 21.6793 | 21.3234 | 20.4505 | 20.5721 | 20.5271 | 22.0502 | 21.6602 | 21.1977 | 22.0081 | 21.7447 | 21.3729 | 19.9514 | 20.5501 |  | 20.5731 | 20.2494 | 20.3535 | 19.1482 |  | 16.7231 | 16.7395 | 16.4916 | 16.7556 | 16.978 | 17.4981 | 17.899 | 15.7342 | 16.6148 | 15.9583 | 16.8677 | 17.8852 | 46.0494 | 50.4376 | 44.9311 | 21.3868 |  |  | 0.39779 | -0.35031 | -49.3844 | 0.36531 | 0.15258 | -197.8388 | 13.7826 | -0.44588 | 0.20501 | -0.32906 | -0.071753 | 8.8296 | 9.0593 | 1.9778 | 21.816 | 22.0388 | 22.2317 | 22.2957 | 22.1423 | 21.4786 | 20.3086 | 22.2195 | 22.3893 | 22.4274 | 22.376 | 22.021 | 21.2718 | 22.2881 | 16.9546 | 17.0986 | 16.329 | 16.232 | 16.2458 | 17.075 | 16.7859 | 22.3988 | 22.17 | 21.7352 | 22.0964 | 21.821 | 21.3372 | 21.9652 | 21.5526 | 20.9339 | 20.1465 | 20.439 | 20.0263 | 19.7806 | 0.017313 | 0.078584 | 20.7882 | 22.1141 | 22.422 | 20.1404 | 21.7148 | 22.1621 | 21.9755 | 21.7471 | 21.3186 | 21.8309 | 21.4911 | 21.0913 | 20.5426 | 20.5463 | 20.5069 | 20.4997 | 20.1745 |  | 20.2543 | 19.978 | 20.144 | 19.6842 | 20.1146 | 20.3838 |  | 20.4527 |  |  | 20.3059 | 20.4012 | 20.643 | [5 empty] | 21.9624 | 20.3546 | 21.7039 | 22.0897 | 19.5465 | 21.2283 | 21.866 | 19.3778 | 20.0244 | 21.2191 |  | 19.7757 | 21.0104 | 18.8067 | 19.7172 | 20.8677 | 19.398 | 20.1562 | 18.9738 | 20.1703 | 19.1227 | 20.2972 | 18.786 | 20.1617 | 21.1796 | 19.4221 | 19.8226 | 21.0477 | 18.9327 | 19.8228 | 20.8594 | 19.035 | 20.2666 | 19.2605 | 19.9695 | 18.9076 | 20.167 | -0.18285 | 20.9457 | 0.047135 | 0.013983 | -27.1164 | 3.0976 | -0.74 | 0.2 | 0.75323 | -0.70228 | -8.3383 | 0.71716 | 0.46409 | -16.7112 | 4.4108 | 0.42241 | 0.42417 | 0.43135 | 0.41565 | 0.45144 | 0.44077 | 0.42974
42838.4127 | -652 | 22.8957 | 22.8652 | 22.8435 | 22.79 | 22.4359 | 21.7895 | 22.7313 | 21.8521 | 22.3895 | 22.3979 | 22.3902 | 22.0736 | 21.3082 | 22.2548 | 21.5842 | 21.7653 | 21.9008 | 21.0908 | 21.1952 | 21.4169 | 20.4968 | 20.6383 | 20.9435 | 21.9123 | 21.6829 | 21.3231 | 20.4515 | 20.5661 | 20.5281 | 22.0421 | 21.6543 | 21.1812 | 22.0002 | 21.7413 | 21.3654 | 19.9425 | 20.5436 |  | 20.5568 | 20.2508 | 20.3416 | 19.1332 |  | 16.7257 | 16.7489 | 16.4931 | 16.7581 | 16.9698 | 17.4753 | 17.8648 | 15.6337 | 16.6148 | 15.9742 | 16.8614 | 17.8917 | 46.1062 | 50.4561 | 44.9908 | 21.3948 |  |  | 0.47007 | -0.27605 | -49.7754 | 0.74053 | 0.27809 | -197.8453 | 13.6827 | -0.24612 | 0.14604 | -0.57642 | -0.07019 | 8.8289 | 9.0588 | 1.9778 | 21.8231 | 22.0489 | 22.2456 | 22.305 | 22.1443 | 21.4914 | 20.3179 | 22.2284 | 22.3983 | 22.4322 | 22.3856 | 22.0309 | 21.2753 | 22.2985 | 16.952 | 17.1208 | 16.2685 | 16.2289 | 16.248 | 17.082 | 16.7806 | 22.4142 | 22.1772 | 21.7388 | 22.1122 | 21.8284 | 21.3393 | 21.9734 | 21.556 | 20.9435 | 20.1535 | 20.4405 | 20.0309 | 19.7881 | -0.095339 | -0.089363 | 20.7893 | 22.1178 | 22.4222 | 20.1403 | 21.7187 | 22.1636 | 21.9833 | 21.7544 | 21.3246 | 21.8253 | 21.4944 | 21.0922 | 20.548 | 20.554 | 20.5123 | 20.507 | 20.1836 |  | 20.252 | 19.9774 | 20.1403 | 19.6875 | 20.1081 | 20.381 |  | 20.4434 |  |  | 20.3075 | 20.3916 | 20.6269 | [5 empty] | 21.9553 | 20.3568 | 21.6987 | 22.0843 | 19.5445 | 21.2284 | 21.8572 | 19.3722 | 20.021 | 21.2237 |  | 19.7766 | 21.0032 | 18.806 | 19.7192 | 20.8614 | 19.3961 | 20.157 | 18.9741 | 20.1663 | 19.1166 | 20.2967 | 18.79 | 20.1591 | 21.1817 | 19.4242 | 19.8229 | 21.0458 | 18.9373 | 19.8277 | 20.8635 | 19.0348 | 20.266 | 19.2653 | 19.972 | 18.9084 | 20.1659 | -0.27337 | 20.9457 | 0.047406 | 0.014121 | -26.8804 | 3.0977 | -0.87 | 0.1 | 0.81881 | -0.62343 | -8.3714 | 1.0211 | 0.62651 | -16.7108 | 4.3946 | 0.42208 | 0.42407 | 0.43104 | 0.41676 | 0.45754 | 0.44089 | 0.42977
42838.4127 | -651 | 22.8876 | 22.8635 | 22.8533 | 22.785 | 22.4342 | 21.7871 | 22.7272 | 21.8403 | 22.3842 | 22.4013 | 22.387 | 22.0761 | 21.306 | 22.2587 | 21.5763 | 21.7579 | 21.8971 | 21.0788 | 21.185 | 21.406 | 20.4893 | 20.6375 | 20.9341 | 21.9081 | 21.6736 | 21.3131 | 20.4355 | 20.5666 | 20.5228 | 22.038 | 21.6607 | 21.1826 | 21.9943 | 21.7453 | 21.3585 | 19.9425 | 20.5411 |  | 20.5589 | 20.2445 | 20.3457 | 19.1402 |  | 16.7316 | 16.7547 | 16.4881 | 16.7543 | 16.9513 | 17.4537 | 17.8323 | 15.5404 | 16.6083 | 15.9687 | 16.8603 | 17.8794 | 46.1464 | 50.4621 | 45.0479 | 21.3832 |  |  | 0.3991 | -0.43705 | -50.5317 | 0.50593 | 0.005388 | -197.8138 | 13.5073 | -0.16332 | -0.02968 | -0.4348 | 0.029456 | 8.8292 | 9.0588 | 1.9785 | 21.8173 | 22.0413 | 22.238 | 22.3001 | 22.1418 | 21.4837 | 20.312 | 22.2249 | 22.3922 | 22.4239 | 22.3798 | 22.0221 | 21.2682 | 22.2946 | 16.9537 | 17.1088 | 16.1804 | 16.197 | 16.2621 | 17.0782 | 16.7769 | 22.4161 | 22.179 | 21.7433 | 22.111 | 21.83 | 21.3408 | 21.9667 | 21.559 | 20.9493 | 20.1493 | 20.4468 | 20.0313 | 19.7905 | -0.090817 | -0.008528 | 20.7859 | 22.1089 | 22.4166 | 20.1385 | 21.7103 | 22.1552 | 21.9756 | 21.7448 | 21.3161 | 21.8155 | 21.489 | 21.0931 | 20.5379 | 20.5419 | 20.502 | 20.4936 | 20.1904 |  | 20.2533 | 19.9749 | 20.1475 | 19.6985 | 20.1181 | 20.3871 |  | 20.4471 |  |  | 20.3012 | 20.3979 | 20.6305 | [5 empty] | 21.9578 | 20.3605 | 21.7036 | 22.0917 | 19.5474 | 21.2331 | 21.8624 | 19.3789 | 20.0181 | 21.221 |  | 19.7798 | 21.0052 | 18.8127 | 19.712 | 20.8697 | 19.3939 | 20.1517 | 18.9693 | 20.1595 | 19.1087 | 20.2915 | 18.794 | 20.1636 | 21.1833 | 19.4189 | 19.8221 | 21.0425 | 18.9363 | 19.8276 | 20.8639 | 19.0313 | 20.2596 | 19.2587 | 19.9708 | 18.9022 | 20.1593 | -0.2385 | 20.9451 | 0.048678 | 0.01391 | -27.0512 | 3.0977 | -0.78 | -0.12 | 0.75446 | -0.78444 | -8.4348 | 0.844 | 0.087203 | -16.7088 | 4.3662 | 0.42194 | 0.42438 | 0.43107 | 0.41613 | 0.46691 | 0.4407 | 0.42956
42838.4128 | -650 | 22.9095 | 22.8696 | 22.861 | 22.802 | 22.4443 | 21.7878 | 22.7397 | 21.8603 | 22.3927 | 22.405 | 22.3924 | 22.0845 | 21.3109 | 22.2706 | 21.5843 | 21.7607 | 21.8973 | 21.0817 | 21.1831 | 21.4065 | 20.4919 | 20.6352 | 20.9342 | 21.9015 | 21.674 | 21.3159 | 20.4379 | 20.5666 | 20.5249 | 22.0425 | 21.6601 | 21.1878 | 22.0011 | 21.7403 | 21.3649 | 19.9488 | 20.5418 |  | 20.5653 | 20.243 | 20.3368 | 19.1679 |  | 16.7326 | 16.7568 | 16.4957 | 16.7551 | 16.9447 | 17.4596 | 17.8148 | 15.4676 | 16.6207 | 15.9242 | 16.8588 | 17.8907 | 46.2131 | 50.4758 | 45.1206 | 21.3927 |  |  | 0.42013 | -0.36082 | -50.2143 | 0.56113 | 0.21106 | -197.8335 | 13.78 | -0.26452 | -0.16999 | -0.57495 | -0.031304 | 8.8287 | 9.0584 | 1.9787 | 21.8139 | 22.0465 | 22.2418 | 22.308 | 22.1439 | 21.4843 | 20.3062 | 22.2245 | 22.3968 | 22.4251 | 22.3836 | 22.025 | 21.2705 | 22.3 | 16.9409 | 17.0737 | 16.1377 | 16.1457 | 16.2615 | 17.088 | 16.7839 | 22.4079 | 22.1779 | 21.7382 | 22.1063 | 21.8299 | 21.3389 | 21.9696 | 21.5614 | 20.9432 | 20.1513 | 20.4473 | 20.0376 | 19.7967 | -0.090817 | -0.10515 | 20.7838 | 22.1008 | 22.416 | 20.1391 | 21.711 | 22.1544 | 21.9721 | 21.7416 | 21.3169 | 21.8218 | 21.4879 | 21.0849 | 20.5372 | 20.5459 | 20.4914 | 20.4977 | 20.1926 |  | 20.2529 | 19.9687 | 20.1473 | 19.6989 | 20.1177 | 20.3891 |  | 20.4424 |  |  | 20.2891 | 20.4051 | 20.6336 | [5 empty] | 21.9625 | 20.3554 | 21.707 | 22.091 | 19.5447 | 21.2329 | 21.8649 | 19.393 | 20.0367 | 21.2302 |  | 19.7912 | 21.012 | 18.8232 | 19.7228 | 20.8698 | 19.4061 | 20.1641 | 18.9843 | 20.1675 | 19.1237 | 20.298 | 18.794 | 20.176 | 21.1776 | 19.417 | 19.8254 | 21.0497 | 18.9299 | 19.8327 | 20.8674 | 19.0302 | 20.2638 | 19.2586 | 19.9706 | 18.8958 | 20.1654 | -0.17358 | 20.9459 | 0.048665 | 0.01627 | -27.104 | 3.0977 | -0.94 | -0.23 | 0.77409 | -0.71276 | -8.4083 | 0.88885 | 0.54579 | -16.7098 | 4.4101 | 0.42186 | 0.42454 | 0.43104 | 0.41869 | 0.47247 | 0.44014 | 0.42946
42838.4128 | -649 | 22.8982 | 22.8637 | 22.8557 | 22.7922 | 22.4332 | 21.7849 | 22.7366 | 21.8491 | 22.3858 | 22.3985 | 22.3787 | 22.0814 | 21.3024 | 22.2609 | 21.5865 | 21.7566 | 21.8984 | 21.089 | 21.1844 | 21.413 | 20.4942 | 20.6359 | 20.9378 | 21.9111 | 21.6742 | 21.3202 | 20.4463 | 20.5694 | 20.5289 | 22.0435 | 21.6596 | 21.1819 | 22.0014 | 21.7438 | 21.362 | 19.9424 | 20.5426 |  | 20.5748 | 20.2377 | 20.3337 | 19.1778 |  | 16.7271 | 16.7586 | 16.4972 | 16.7508 | 16.9407 | 17.4894 | 17.8433 | 15.4152 | 16.6199 | 15.881 | 16.8631 | 17.8825 | 46.2676 | 50.4787 | 45.1694 | 21.3861 |  |  | 0.26176 | -0.38185 | -49.8765 | 0.14255 | 0.41477 | -197.8223 | 13.6407 | -0.34075 | -0.069379 | -0.21913 | 0.031192 | 8.8285 | 9.0581 | 1.9782 | 21.8148 | 22.0426 | 22.2421 | 22.3024 | 22.1424 | 21.4831 | 20.3152 | 22.2216 | 22.3997 | 22.4285 | 22.3909 | 22.0258 | 21.2643 | 22.2974 | 16.951 | 17.0638 | 16.0777 | 16.0895 | 16.211 | 17.0805 | 16.7768 | 22.4093 | 22.1737 | 21.7394 | 22.1032 | 21.8279 | 21.3376 | 21.9643 | 21.5556 | 20.9365 | 20.1484 | 20.4338 | 20.0316 | 19.7951 | -0.014536 | -0.065588 | 20.7852 | 22.0935 | 22.4126 | 20.1373 | 21.6999 | 22.1556 | 21.9626 | 21.7399 | 21.3095 | 21.8207 | 21.4807 | 21.0862 | 20.5342 | 20.5451 | 20.4858 | 20.4891 | 20.2009 |  | 20.2621 | 19.9695 | 20.1466 | 19.6948 | 20.1255 | 20.3892 |  | 20.4502 |  |  | 20.2866 | 20.403 | 20.638 | [5 empty] | 21.9642 | 20.3532 | 21.7099 | 22.0934 | 19.5489 | 21.2312 | 21.8723 | 19.3901 | 20.0385 | 21.2306 |  | 19.7947 | 21.0138 | 18.8246 | 19.72 | 20.8703 | 19.3979 | 20.1643 | 18.9871 | 20.1673 | 19.1202 | 20.2992 | 18.802 | 20.17 | 21.1857 | 19.4232 | 19.8229 | 21.0468 | 18.9295 | 19.8269 | 20.8589 | 19.0329 | 20.2629 | 19.2602 | 19.9732 | 18.8984 | 20.1743 | -0.15836 | 20.9463 | 0.049095 | 0.016749 | -26.9971 | 3.0977 | -0.73 | 0.49 | 0.61102 | -0.73324 | -8.38 | 0.448 | 0.76515 | -16.7102 | 4.388 | 0.42194 | 0.4245 | 0.43142 | 0.41669 | 0.4783 | 0.43965 | 0.4294
42838.4128 | -648 | 22.9057 | 22.8682 | 22.8549 | 22.7932 | 22.4339 | 21.7798 | 22.7392 | 21.8523 | 22.3924 | 22.4023 | 22.3846 | 22.0853 | 21.3046 | 22.2657 | 21.5981 | 21.7765 | 21.9037 | 21.0977 | 21.1923 | 21.421 | 20.5061 | 20.6467 | 20.9488 | 21.9185 | 21.6893 | 21.3245 | 20.4517 | 20.5751 | 20.5316 | 22.0487 | 21.6631 | 21.1834 | 22.0086 | 21.7422 | 21.3662 | 19.9522 | 20.5441 |  | 20.5754 | 20.2479 | 20.3425 | 19.1849 |  | 16.7278 | 16.7618 | 16.4852 | 16.7489 | 16.9566 | 17.524 | 17.8727 | 15.3824 | 16.6127 | 15.8906 | 16.8632 | 17.8912 | 46.3238 | 50.489 | 45.2426 | 21.3985 |  |  | 0.18882 | -0.33585 | -49.546 | 0.34231 | 0.40492 | -197.823 | 13.6525 | -0.30395 | 0.049911 | -0.35445 | -0.011166 | 8.829 | 9.0586 | 1.9779 | 21.8123 | 22.0344 | 22.2357 | 22.2912 | 22.1403 | 21.4791 | 20.3072 | 22.2246 | 22.3932 | 22.4213 | 22.3854 | 22.0229 | 21.2606 | 22.2828 | 16.9761 | 17.0467 | 16.0462 | 16.0806 | 16.1688 | 17.0822 | 16.777 | 22.4007 | 22.1724 | 21.7345 | 22.0969 | 21.816 | 21.3314 | 21.9602 | 21.5517 | 20.9397 | 20.145 | 20.4314 | 20.0184 | 19.8012 | -0.085705 | -0.12455 | 20.7869 | 22.0989 | 22.4119 | 20.1366 | 21.706 | 22.1598 | 21.9787 | 21.7368 | 21.3098 | 21.8204 | 21.48 | 21.0866 | 20.5554 | 20.5324 | 20.4935 | 20.4858 | 20.2129 |  | 20.2585 | 19.9628 | 20.142 | 19.7045 | 20.1185 | 20.3962 |  | 20.4558 |  |  | 20.2843 | 20.3997 | 20.6411 | [5 empty] | 21.9613 | 20.3581 | 21.7104 | 22.09 | 19.5445 | 21.2289 | 21.8538 | 19.3823 | 20.031 | 21.2279 |  | 19.792 | 21.0095 | 18.8307 | 19.7146 | 20.8675 | 19.389 | 20.1553 | 18.9862 | 20.1672 | 19.1187 | 20.2972 | 18.806 | 20.1704 | 21.1927 | 19.4342 | 19.8281 | 21.0518 | 18.9308 | 19.8352 | 20.8686 | 19.0365 | 20.2699 | 19.2696 | 19.9766 | 18.8968 | 20.1835 | -0.089173 | 20.9464 | 0.048862 | 0.016625 | -27.0414 | 3.0977 | -0.62 | -0.02 | 0.51896 | -0.68766 | -8.3523 | 0.69424 | 0.75605 | -16.7112 | 4.3901 | 0.42148 | 0.42453 | 0.43092 | 0.4141 | 0.48182 | 0.43978 | 0.42912
42838.4128 | -647 | 22.9014 | 22.8723 | 22.8533 | 22.7886 | 22.4392 | 21.7907 | 22.7373 | 21.8528 | 22.3907 | 22.402 | 22.3871 | 22.0778 | 21.3041 | 22.2662 | 21.5789 | 21.7626 | 21.9004 | 21.0788 | 21.1839 | 21.4116 | 20.4909 | 20.6374 | 20.9303 | 21.9168 | 21.6732 | 21.3093 | 20.4478 | 20.5679 | 20.5255 | 22.0475 | 21.6604 | 21.1933 | 22.0064 | 21.7479 | 21.3672 | 19.952 | 20.5443 |  | 20.5745 | 20.2448 | 20.3437 | 19.1987 |  | 16.7299 | 16.7535 | 16.4929 | 16.7515 | 16.9818 | 17.5527 | 17.8796 | 15.3652 | 16.621 | 15.8989 | 16.8631 | 17.878 | 46.3656 | 50.4721 | 45.2928 | 21.39 |  |  | 0.33602 | -0.31876 | -49.3377 | 0.13204 | 0.38389 | -197.8473 | 13.6183 | -0.27898 | -0.1694 | -0.4583 | 0.017998 | 8.829 | 9.059 | 1.9777 | 21.8079 | 22.0354 | 22.2336 | 22.3005 | 22.1328 | 21.4756 | 20.3084 | 22.2212 | 22.3914 | 22.4238 | 22.3791 | 22.0316 | 21.2567 | 22.2848 | 16.996 | 17.0533 | 16.0394 | 16.062 | 16.1461 | 17.0866 | 16.7808 | 22.4057 | 22.1768 | 21.7393 | 22.1029 | 21.829 | 21.3392 | 21.9644 | 21.5622 | 20.9374 | 20.1549 | 20.4481 | 20.04 | 19.8166 | 0.017313 | -0.13767 | 20.7959 | 22.1139 | 22.4144 | 20.138 | 21.7191 | 22.1581 | 21.9831 | 21.7514 | 21.3213 | 21.829 | 21.4864 | 21.0932 | 20.5527 | 20.5501 | 20.5014 | 20.4942 | 20.2122 |  | 20.256 | 19.9411 | 20.1317 | 19.6952 | 20.1124 | 20.3838 |  | 20.4431 |  |  | 20.2825 | 20.4032 | 20.6303 | [5 empty] | 21.9586 | 20.3557 | 21.703 | 22.0905 | 19.5492 | 21.2222 | 21.8618 | 19.3927 | 20.0409 | 21.229 |  | 19.8 | 21.0198 | 18.8293 | 19.7258 | 20.8704 | 19.4036 | 20.1543 | 18.9895 | 20.1668 | 19.1228 | 20.3016 | 18.8056 | 20.1566 | 21.1611 | 19.4163 | 19.8033 | 21.0406 | 18.9253 | 19.829 | 20.857 | 19.023 | 20.2587 | 19.2509 | 19.9631 | 18.8869 | 20.1673 | -0.12163 | 20.9461 | 0.048567 | 0.016001 | -27.057 | 3.0977 | -0.52 | 0.06 | 0.69228 | -0.66993 | -8.3346 | 0.43116 | 0.7362 | -16.7131 | 4.3848 | 0.42142 | 0.42479 | 0.43097 | 0.4124 | 0.48302 | 0.43939 | 0.42902
42838.4128 | -646 | 22.8966 | 22.8675 | 22.853 | 22.7847 | 22.4344 | 21.7836 | 22.7325 | 21.8497 | 22.386 | 22.395 | 22.3846 | 22.0749 | 21.3027 | 22.2605 | 21.5893 | 21.7677 | 21.9053 | 21.0942 | 21.1978 | 21.414 | 20.502 | 20.6515 | 20.9476 | 21.9253 | 21.6891 | 21.328 | 20.4512 | 20.5728 | 20.5251 | 22.05 | 21.6628 | 21.1992 | 22.0099 | 21.7526 | 21.3689 | 19.951 | 20.5452 |  | 20.5763 | 20.2452 | 20.3418 | 19.2035 |  | 16.7315 | 16.7513 | 16.4981 | 16.7655 | 17.0049 | 17.5798 | 17.8673 | 15.3614 | 16.631 | 15.931 | 16.8726 | 17.8847 | 46.4071 | 50.4669 | 45.3479 | 21.4031 |  |  | 0.4773 | -0.34374 | -48.954 | 0.50725 | 0.5462 | -197.7914 | 13.4508 | -0.094328 | -0.064319 | -0.47131 | -0.084426 | 8.8289 | 9.0588 | 1.9785 | 21.8306 | 22.0499 | 22.2435 | 22.3061 | 22.1467 | 21.4889 | 20.3148 | 22.2319 | 22.398 | 22.4325 | 22.389 | 22.0282 | 21.2654 | 22.2959 | 16.9993 | 17.0337 | 16.0269 | 16.0551 | 16.126 | 17.0774 | 16.7739 | 22.4008 | 22.1724 | 21.7336 | 22.1082 | 21.8265 | 21.3339 | 21.9603 | 21.557 | 20.9406 | 20.1549 | 20.4363 | 20.0325 | 19.8168 | 0.048376 | -0.0098594 | 20.791 | 22.1035 | 22.4133 | 20.1426 | 21.7088 | 22.1564 | 21.9635 | 21.746 | 21.3081 | 21.8147 | 21.4829 | 21.0878 | 20.5337 | 20.5375 | 20.4875 | 20.4814 | 20.2261 |  | 20.2581 | 19.9434 | 20.1471 | 19.7047 | 20.1164 | 20.3852 |  | 20.4392 |  |  | 20.2879 | 20.4 | 20.6266 | [5 empty] | 21.9553 | 20.3559 | 21.697 | 22.0918 | 19.5568 | 21.2208 | 21.8571 | 19.3843 | 20.0367 | 21.2354 |  | 19.8034 | 21.0119 | 18.8328 | 19.7258 | 20.8825 | 19.3948 | 20.1651 | 18.9959 | 20.1668 | 19.126 | 20.3087 | 18.8121 | 20.1714 | 21.1856 | 19.4322 | 19.8207 | 21.0547 | 18.9257 | 19.8356 | 20.8659 | 19.0294 | 20.2571 | 19.252 | 19.9762 | 18.8975 | 20.174 | -0.20418 | 20.9461 | 0.048419 | 0.016132 | -27.02 | 3.0977 | -0.56 | -0.16 | 0.82508 | -0.69567 | -8.3021 | 0.84509 | 0.87818 | -16.7115 | 4.358 | 0.4211 | 0.42524 | 0.43084 | 0.41096 | 0.4836 | 0.43922 | 0.42902
42838.4128 | -645 | 22.9002 | 22.8709 | 22.8607 | 22.7903 | 22.4339 | 21.7839 | 22.743 | 21.8501 | 22.3994 | 22.4018 | 22.3937 | 22.087 | 21.307 | 22.2639 | 21.587 | 21.7545 | 21.8894 | 21.0814 | 21.1877 | 21.408 | 20.4885 | 20.6358 | 20.9336 | 21.9075 | 21.6814 | 21.3147 | 20.4468 | 20.5697 | 20.5148 | 22.042 | 21.6656 | 21.1967 | 22.0072 | 21.7485 | 21.3638 | 19.9506 | 20.5393 |  | 20.5779 | 20.245 | 20.3379 | 19.1889 |  | 16.7198 | 16.752 | 16.5009 | 16.7632 | 17.0126 | 17.5829 | 17.8167 | 15.3518 | 16.6198 | 15.9425 | 16.8618 | 17.8843 | 46.449 | 50.4551 | 45.3998 | 21.4019 |  |  | 0.51278 | 0.053159 | -48.8843 | 0.55588 | 0.24064 | -197.8276 | 13.5796 | 0.059436 | 0.12094 | -0.20172 | -0.038074 | 8.8289 | 9.0586 | 1.9785 | 21.8185 | 22.0394 | 22.2405 | 22.3067 | 22.1442 | 21.4848 | 20.3095 | 22.2282 | 22.3913 | 22.4212 | 22.3825 | 22.0229 | 21.269 | 22.2897 | 17.0053 | 17.0407 | 16.0236 | 16.0285 | 16.1014 | 17.0817 | 16.7823 | 22.3941 | 22.1681 | 21.7239 | 22.0954 | 21.8208 | 21.3255 | 21.9588 | 21.5473 | 20.9317 | 20.1358 | 20.4343 | 20.0244 | 19.8119 | 0.020459 | -0.024885 | 20.798 | 22.1114 | 22.4304 | 20.1579 | 21.7166 | 22.1588 | 21.9858 | 21.7419 | 21.3159 | 21.824 | 21.4932 | 21.0994 | 20.5508 | 20.5501 | 20.495 | 20.4875 | 20.2393 |  | 20.2697 | 19.9433 | 20.155 | 19.7138 | 20.1253 | 20.3964 |  | 20.4575 |  |  | 20.2887 | 20.3981 | 20.6209 | [5 empty] | 21.9589 | 20.3541 | 21.6991 | 22.0858 | 19.5558 | 21.2173 | 21.8564 | 19.3788 | 20.0375 | 21.2285 |  | 19.7909 | 21.0126 | 18.8345 | 19.718 | 20.8691 | 19.3907 | 20.152 | 18.9855 | 20.1657 | 19.1143 | 20.304 | 18.8131 | 20.1688 | 21.178 | 19.4286 | 19.8163 | 21.0432 | 18.9297 | 19.8313 | 20.8686 | 19.0294 | 20.2538 | 19.254 | 19.9711 | 18.9022 | 20.1761 | -0.040201 | 20.9466 | 0.048364 | 0.015979 | -27.1274 | 3.0977 | -0.67 | -0.07 | 0.85518 | 0.27358 | -8.2962 | 0.88467 | 0.5829 | -16.7131 | 4.3788 | 0.42113 | 0.42551 | 0.43089 | 0.41079 | 0.48496 | 0.43961 | 0.42851
42838.4128 | -644 | 22.8983 | 22.8679 | 22.8516 | 22.7832 | 22.4301 | 21.7834 | 22.7346 | 21.8431 | 22.3817 | 22.3975 | 22.3932 | 22.0794 | 21.2951 | 22.2613 | 21.589 | 21.7585 | 21.8966 | 21.0852 | 21.188 | 21.4157 | 20.4975 | 20.6391 | 20.9347 | 21.9101 | 21.6861 | 21.3237 | 20.4508 | 20.5719 | 20.516 | 22.0433 | 21.6593 | 21.1879 | 22.0042 | 21.7378 | 21.3598 | 19.94 | 20.5344 |  | 20.5719 | 20.2433 | 20.3378 | 19.1953 |  | 16.7285 | 16.7657 | 16.507 | 16.7745 | 17.0227 | 17.5632 | 17.8092 | 15.3706 | 16.6193 | 15.9643 | 16.8676 | 17.8873 | 46.4894 | 50.4411 | 45.4424 | 21.4079 |  |  | 0.43458 | -0.25634 | -48.7266 | 0.71884 | 0.15521 | -197.8512 | 13.546 | 0.016068 | 0.11588 | -0.18724 | -0.076961 | 8.8286 | 9.0583 | 1.9783 | 21.8203 | 22.0421 | 22.2384 | 22.3038 | 22.14 | 21.4821 | 20.3067 | 22.2186 | 22.393 | 22.4207 | 22.3747 | 22.0153 | 21.2644 | 22.2921 | 17.0113 | 17.0759 | 16.0075 | 16.0152 | 16.0866 | 17.0756 | 16.7759 | 22.3954 | 22.1728 | 21.7282 | 22.0983 | 21.8224 | 21.3292 | 21.9609 | 21.5539 | 20.9357 | 20.1403 | 20.4446 | 20.0265 | 19.8216 | 0.067839 | -0.014234 | 20.8037 | 22.1079 | 22.4156 | 20.1518 | 21.7174 | 22.1608 | 21.9657 | 21.7491 | 21.3166 | 21.8275 | 21.485 | 21.0892 | 20.5386 | 20.5509 | 20.4857 | 20.4821 | 20.2258 |  | 20.2662 | 19.9322 | 20.1528 | 19.7092 | 20.1233 | 20.393 |  | 20.4558 |  |  | 20.2965 | 20.4004 | 20.6287 | [5 empty] | 21.965 | 20.3623 | 21.7042 | 22.0935 | 19.5542 | 21.2231 | 21.8571 | 19.3863 | 20.0416 | 21.2398 |  | 19.8024 | 21.0139 | 18.8319 | 19.7312 | 20.8726 | 19.3853 | 20.1532 | 18.9866 | 20.1657 | 19.123 | 20.3068 | 18.8107 | 20.1626 | 21.1753 | 19.4184 | 19.8146 | 21.0456 | 18.9261 | 19.8395 | 20.8726 | 19.0285 | 20.2447 | 19.251 | 19.977 | 18.8985 | 20.1766 | -0.073961 | 20.9467 | 0.047528 | 0.01542 | -26.9906 | 3.0977 | -0.8 | 0.06 | 0.78728 | -0.60078 | -8.283 | 1.006 | 0.46813 | -16.7136 | 4.3733 | 0.42138 | 0.42574 | 0.43095 | 0.40942 | 0.48599 | 0.43908 | 0.42839
42838.4128 | -643 | 22.8952 | 22.8636 | 22.8508 | 22.7866 | 22.4253 | 21.776 | 22.7283 | 21.8351 | 22.3869 | 22.3923 | 22.3874 | 22.0867 | 21.2981 | 22.2657 | 21.5783 | 21.756 | 21.895 | 21.0811 | 21.1801 | 21.4042 | 20.4846 | 20.6351 | 20.9357 | 21.9073 | 21.682 | 21.311 | 20.4439 | 20.565 | 20.5128 | 22.0346 | 21.6643 | 21.2001 | 22.0051 | 21.7437 | 21.3623 | 19.9438 | 20.5418 |  | 20.5781 | 20.2462 | 20.3407 | 19.206 |  | 16.7375 | 16.7887 | 16.5076 | 16.7658 | 17.0148 | 17.5329 | 17.7679 | 15.3905 | 16.6283 | 15.9863 | 16.8623 | 17.8845 | 46.5257 | 50.4063 | 45.4942 | 21.4082 |  |  | 0.51541 | -0.10652 | -48.7877 | 0.59005 | 0.10133 | -197.8808 | 13.5493 | -0.13376 | 0.067814 | -0.04017 | 0.016262 | 8.8284 | 9.0578 | 1.9782 | 21.8141 | 22.0399 | 22.2326 | 22.3018 | 22.138 | 21.4787 | 20.3067 | 22.2173 | 22.3914 | 22.4262 | 22.3781 | 22.0189 | 21.2628 | 22.2929 | 17.0178 | 17.096 | 16.0174 | 16.023 | 16.0743 | 17.0755 | 16.7743 | 22.3916 | 22.1663 | 21.7367 | 22.1034 | 21.8221 | 21.3284 | 21.9609 | 21.554 | 20.9293 | 20.145 | 20.4416 | 20.0268 | 19.8218 | 0.10087 | -0.12702 | 20.7937 | 22.1124 | 22.4215 | 20.1552 | 21.7142 | 22.158 | 21.9713 | 21.7472 | 21.3152 | 21.8217 | 21.4864 | 21.0921 | 20.5413 | 20.5365 | 20.4774 | 20.4715 | 20.2076 |  | 20.2598 | 19.9234 | 20.1433 | 19.6913 | 20.1215 | 20.3825 |  | 20.449 |  |  | 20.3058 | 20.4001 | 20.6258 | [5 empty] | 21.9598 | 20.3572 | 21.6983 | 22.0858 | 19.5528 | 21.2225 | 21.8516 | 19.3817 | 20.0325 | 21.2318 |  | 19.7988 | 21.0138 | 18.8344 | 19.7177 | 20.8679 | 19.3884 | 20.1474 | 18.9799 | 20.1605 | 19.1175 | 20.3 | 18.8175 | 20.1672 | 21.1792 | 19.431 | 19.8141 | 21.051 | 18.9372 | 19.8476 | 20.8687 | 19.0293 | 20.2564 | 19.2583 | 19.9799 | 18.9009 | 20.1835 | -0.18582 | 20.9453 | 0.046134 | 0.015595 | -27.2217 | 3.0977 | -0.66 | -0.18 | 0.85737 | -0.38728 | -8.2885 | 0.91151 | 0.37822 | -16.7139 | 4.3736 | 0.42167 | 0.42567 | 0.43138 | 0.40869 | 0.48471 | 0.43891 | 0.42855
42838.4128 | -642 | 22.888 | 22.8608 | 22.8516 | 22.7782 | 22.4287 | 21.7619 | 22.7228 | 21.8317 | 22.38 | 22.3977 | 22.3838 | 22.0731 | 21.2938 | 22.2569 | 21.5823 | 21.7662 | 21.8974 | 21.0876 | 21.1878 | 21.4149 | 20.4905 | 20.6449 | 20.9388 | 21.919 | 21.6839 | 21.3161 | 20.4501 | 20.5719 | 20.522 | 22.0476 | 21.6566 | 21.1924 | 21.9989 | 21.7435 | 21.3651 | 19.9415 | 20.5415 |  | 20.5724 | 20.2427 | 20.3327 | 19.1915 |  | 16.7632 | 16.8149 | 16.513 | 16.7682 | 17.0033 | 17.5112 | 17.7422 | 15.4673 | 16.6285 | 16.0079 | 16.8727 | 17.8883 | 46.5661 | 50.3897 | 45.5587 | 21.4125 |  |  | 0.63961 | -0.090749 | -48.4309 | 0.62619 | 0.19727 | -197.8236 | 13.7524 | -0.13901 | 0.055554 | -0.11822 | -0.038595 | 8.8283 | 9.0581 | 1.9774 | 21.8101 | 22.0331 | 22.2321 | 22.3001 | 22.1386 | 21.4843 | 20.3027 | 22.2097 | 22.3877 | 22.4233 | 22.3851 | 22.0166 | 21.2585 | 22.2888 | 17.0112 | 17.083 | 16.033 | 16.0345 | 16.0802 | 17.0776 | 16.7812 | 22.3994 | 22.1739 | 21.7362 | 22.1071 | 21.8252 | 21.3254 | 21.9632 | 21.5523 | 20.9309 | 20.144 | 20.4471 | 20.0324 | 19.8251 | 0.054864 | -0.13634 | 20.7957 | 22.099 | 22.4151 | 20.1586 | 21.6989 | 22.1552 | 21.9712 | 21.737 | 21.3124 | 21.8152 | 21.485 | 21.085 | 20.5423 | 20.5428 | 20.4683 | 20.4675 | 20.2106 |  | 20.2612 | 19.926 | 20.1505 | 19.692 | 20.1145 | 20.3979 |  | 20.4549 |  |  | 20.3077 | 20.4018 | 20.6257 | [5 empty] | 21.9597 | 20.3513 | 21.6936 | 22.0873 | 19.5539 | 21.218 | 21.8487 | 19.3871 | 20.0393 | 21.2333 |  | 19.8108 | 21.0142 | 18.8401 | 19.7283 | 20.8755 | 19.3961 | 20.1567 | 18.9849 | 20.1704 | 19.1289 | 20.3121 | 18.8213 | 20.167 | 21.176 | 19.4274 | 19.8145 | 21.051 | 18.9353 | 19.839 | 20.8708 | 19.0261 | 20.2575 | 19.2619 | 19.9742 | 18.8951 | 20.1859 | 0.038637 | 20.9459 | 0.046939 | 0.014818 | -27.0474 | 3.0977 | -0.56 | -0.17 | 0.95511 | -0.35749 | -8.2585 | 0.93906 | 0.5277 | -16.7109 | 4.4061 | 0.42164 | 0.42583 | 0.43113 | 0.40967 | 0.48378 | 0.43924 | 0.42842
42838.4129 | -641 | 22.8979 | 22.8655 | 22.856 | 22.7866 | 22.4416 | 21.7768 | 22.7292 | 21.8464 | 22.388 | 22.401 | 22.3826 | 22.0789 | 21.298 | 22.2575 | 21.5844 | 21.7677 | 21.899 | 21.0862 | 21.1852 | 21.415 | 20.4937 | 20.6461 | 20.9387 | 21.9184 | 21.6839 | 21.3174 | 20.4489 | 20.5762 | 20.5254 | 22.0626 | 21.6742 | 21.1988 | 22.009 | 21.7521 | 21.3729 | 19.9535 | 20.5503 |  | 20.5887 | 20.2527 | 20.3463 | 19.2012 |  | 16.7749 | 16.8125 | 16.5137 | 16.7602 | 16.9931 | 17.5033 | 17.7249 | 15.5542 | 16.6315 | 16.0323 | 16.8677 | 17.8856 | 46.5966 | 50.3595 | 45.6191 | 21.4136 |  |  | 0.29067 | 0.012419 | -47.5293 | 0.73987 | 0.0389 | -197.8893 | 14.2906 | -0.16727 | 0.28966 | -0.31102 | -0.038074 | 8.8291 | 9.0589 | 1.9787 | 21.8146 | 22.0354 | 22.2283 | 22.2987 | 22.1412 | 21.4855 | 20.3057 | 22.2212 | 22.3903 | 22.4292 | 22.3772 | 22.0175 | 21.2645 | 22.2872 | 17.0056 | 17.0438 | 16.0381 | 16.0403 | 16.0789 | 17.0741 | 16.7775 | 22.4127 | 22.1733 | 21.7471 | 22.1138 | 21.8336 | 21.3408 | 21.9681 | 21.5586 | 20.9401 | 20.1493 | 20.4527 | 20.0398 | 19.8231 | 0.16299 | -0.021081 | 20.7943 | 22.1137 | 22.4182 | 20.1535 | 21.7186 | 22.1651 | 21.9819 | 21.7469 | 21.3094 | 21.8159 | 21.4853 | 21.0887 | 20.5443 | 20.5408 | 20.482 | 20.4642 | 20.2065 |  | 20.265 | 19.9205 | 20.1542 | 19.7068 | 20.1211 | 20.3929 |  | 20.4569 |  |  | 20.3006 | 20.4075 | 20.6337 | [5 empty] | 21.959 | 20.3495 | 21.6979 | 22.09 | 19.5584 | 21.2209 | 21.8531 | 19.3799 | 20.0279 | 21.229 |  | 19.7971 | 21.0153 | 18.8382 | 19.7246 | 20.8725 | 19.3945 | 20.1566 | 18.9798 | 20.1636 | 19.1242 | 20.3153 | 18.8148 | 20.1582 | 21.1674 | 19.421 | 19.8029 | 21.0446 | 18.9302 | 19.8273 | 20.864 | 19.013 | 20.2513 | 19.2508 | 19.9625 | 18.8899 | 20.1786 | -0.24036 | 20.947 | 0.048389 | 0.015355 | -26.9507 | 3.0977 | -0.6 | -0.33 | 0.64388 | 0.13225 | -8.1812 | 1.0207 | 0.23433 | -16.7134 | 4.4914 | 0.42188 | 0.42611 | 0.43094 | 0.40987 | 0.48278 | 0.43937 | 0.42865
42838.4129 | -640 | 22.8949 | 22.8627 | 22.8518 | 22.7775 | 22.4262 | 21.7723 | 22.7273 | 21.838 | 22.3806 | 22.3948 | 22.3797 | 22.0724 | 21.2993 | 22.2567 | 21.5831 | 21.7597 | 21.8987 | 21.0828 | 21.1882 | 21.4084 | 20.4937 | 20.6417 | 20.9401 | 21.9097 | 21.6864 | 21.3143 | 20.4455 | 20.5743 | 20.5222 | 22.0541 | 21.6716 | 21.1979 | 22.013 | 21.7588 | 21.3764 | 19.9584 | 20.5427 |  | 20.5879 | 20.2471 | 20.3453 | 19.1917 |  | 16.7872 | 16.7931 | 16.5156 | 16.7553 | 16.9747 | 17.4818 | 17.7029 | 15.6042 | 16.6324 | 16.096 | 16.875 | 17.8797 | 46.6445 | 50.3238 | 45.6627 | 21.411 |  |  | 0.39976 | -0.097317 | -46.3728 | 0.58873 | 0.12367 | -197.8434 | 14.5074 | -0.0871 | -0.09312 | -0.36347 | -0.15699 | 8.8291 | 9.0586 | 1.9785 | 21.8117 | 22.0348 | 22.2412 | 22.3072 | 22.1417 | 21.4838 | 20.3036 | 22.2199 | 22.3939 | 22.432 | 22.3854 | 22.0253 | 21.2692 | 22.3006 | 17.0022 | 17.0502 | 16.0572 | 16.0358 | 16.0825 | 17.08 | 16.7816 | 22.4065 | 22.1727 | 21.7448 | 22.1063 | 21.8305 | 21.3406 | 21.9686 | 21.563 | 20.9398 | 20.1516 | 20.447 | 20.0394 | 19.8226 | 0.12859 | -0.059882 | 20.7952 | 22.1113 | 22.4232 | 20.1585 | 21.719 | 22.1578 | 21.9757 | 21.7498 | 21.318 | 21.821 | 21.4864 | 21.0884 | 20.5487 | 20.5466 | 20.4716 | 20.4737 | 20.2066 |  | 20.2578 | 19.9254 | 20.1528 | 19.6986 | 20.118 | 20.3928 |  | 20.4556 |  |  | 20.3051 | 20.405 | 20.6312 | [5 empty] | 21.9565 | 20.3506 | 21.7002 | 22.0914 | 19.5657 | 21.223 | 21.8597 | 19.3766 | 20.0245 | 21.2283 |  | 19.7984 | 21.0173 | 18.8374 | 19.7167 | 20.8724 | 19.3829 | 20.1503 | 18.9743 | 20.1584 | 19.1222 | 20.3067 | 18.8108 | 20.1544 | 21.1708 | 19.4188 | 19.8026 | 21.0387 | 18.931 | 19.8283 | 20.8622 | 19.0112 | 20.2502 | 19.2483 | 19.9674 | 18.8914 | 20.1729 | -0.15224 | 20.9455 | 0.048518 | 0.016117 | -27.0263 | 3.0978 | -0.73 | -0.12 | 0.75509 | -0.37018 | -8.0808 | 0.9105 | 0.4178 | -16.7109 | 4.5252 | 0.42163 | 0.42593 | 0.43106 | 0.41094 | 0.48115 | 0.4398 | 0.42874
42838.4129 | -639 | 22.888 | 22.8547 | 22.8474 | 22.7723 | 22.425 | 21.771 | 22.7208 | 21.8358 | 22.3747 | 22.3888 | 22.3833 | 22.0675 | 21.2917 | 22.2485 | 21.5842 | 21.7565 | 21.8983 | 21.0886 | 21.1887 | 21.4131 | 20.4929 | 20.64 | 20.9386 | 21.9112 | 21.6818 | 21.316 | 20.4476 | 20.5796 | 20.5212 | 22.0498 | 21.6627 | 21.1905 | 22.0046 | 21.7477 | 21.3676 | 19.952 | 20.5322 |  | 20.58 | 20.2456 | 20.3368 | 19.1793 |  | 16.7899 | 16.7935 | 16.5173 | 16.7531 | 16.9628 | 17.4573 | 17.6722 | 15.619 | 16.6352 | 16.1057 | 16.8791 | 17.886 | 46.7074 | 50.298 | 45.7236 | 21.4225 |  |  | 0.32945 | -0.30103 | -45.6158 | 0.61502 | 0.015244 | -197.8867 | 14.7039 | -0.11207 | -0.073855 | -0.34144 | -0.26046 | 8.829 | 9.0586 | 1.9783 | 21.8097 | 22.0337 | 22.232 | 22.2969 | 22.1318 | 21.4764 | 20.3096 | 22.2145 | 22.3852 | 22.4248 | 22.3737 | 22.0133 | 21.2635 | 22.2929 | 16.9986 | 17.0731 | 16.0727 | 16.0234 | 16.0761 | 17.082 | 16.7804 | 22.4027 | 22.1755 | 21.745 | 22.1061 | 21.8262 | 21.333 | 21.9575 | 21.5511 | 20.9419 | 20.1492 | 20.4508 | 20.0314 | 19.826 | 0.070395 | -0.078712 | 20.7841 | 22.0992 | 22.4151 | 20.1468 | 21.697 | 22.1524 | 21.9744 | 21.7421 | 21.3102 | 21.8159 | 21.4863 | 21.0821 | 20.5423 | 20.5292 | 20.477 | 20.4684 | 20.2014 |  | 20.2652 | 19.9316 | 20.1566 | 19.7064 | 20.1245 | 20.388 |  | 20.4527 |  |  | 20.3032 | 20.4028 | 20.6304 | [5 empty] | 21.9621 | 20.3479 | 21.6933 | 22.0879 | 19.5625 | 21.2171 | 21.8568 | 19.3792 | 20.0326 | 21.2283 |  | 19.8043 | 21.0162 | 18.8421 | 19.7141 | 20.8724 | 19.3859 | 20.1516 | 18.9773 | 20.1624 | 19.1213 | 20.311 | 18.8166 | 20.1582 | 21.1713 | 19.4177 | 19.8108 | 21.0393 | 18.9349 | 19.8228 | 20.8598 | 19.0066 | 20.2608 | 19.2529 | 19.9708 | 18.8899 | 20.1812 | -0.17914 | 20.9457 | 0.048659 | 0.015602 | -27.0303 | 3.0977 | -0.69 | -0.11 | 0.68547 | -0.65107 | -8.0146 | 0.93061 | 0.14668 | -16.712 | 4.5555 | 0.42203 | 0.42588 | 0.43106 | 0.41158 | 0.47927 | 0.43993 | 0.42857
42838.4129 | -638 | 22.8881 | 22.862 | 22.8491 | 22.7785 | 22.4349 | 21.7788 | 22.7277 | 21.8436 | 22.3843 | 22.3942 | 22.3883 | 22.0705 | 21.295 | 22.2559 | 21.583 | 21.7612 | 21.9042 | 21.0869 | 21.1897 | 21.4149 | 20.4924 | 20.6362 | 20.94 | 21.9102 | 21.6776 | 21.3192 | 20.4499 | 20.574 | 20.5204 | 22.0488 | 21.6606 | 21.1881 | 22.0034 | 21.7475 | 21.3654 | 19.9397 | 20.5334 |  | 20.5759 | 20.2427 | 20.3359 | 19.1669 |  | 16.7778 | 16.7785 | 16.4996 | 16.7417 | 16.9448 | 17.4259 | 17.6407 | 15.6276 | 16.6262 | 16.054 | 16.874 | 17.8855 | 46.7614 | 50.2494 | 45.7801 | 21.4172 |  |  | 0.49373 | -0.29051 | -45.0671 | 0.46125 | 0.20646 | -197.8296 | 14.6382 | -0.16267 | -0.091174 | -0.5267 | -0.11932 | 8.8294 | 9.059 | 1.978 | 21.8173 | 22.0429 | 22.242 | 22.3045 | 22.1453 | 21.4797 | 20.3106 | 22.226 | 22.3905 | 22.4305 | 22.3764 | 22.0253 | 21.2681 | 22.3018 | 16.9897 | 17.0548 | 16.06 | 16.0404 | 16.071 | 17.075 | 16.7841 | 22.3976 | 22.1693 | 21.7315 | 22.1012 | 21.8209 | 21.3311 | 21.963 | 21.5512 | 20.9404 | 20.1487 | 20.448 | 20.0315 | 19.8168 | 0.043264 | -0.21661 | 20.7907 | 22.1021 | 22.4216 | 20.1493 | 21.7141 | 22.1489 | 21.9734 | 21.7379 | 21.3164 | 21.8253 | 21.4855 | 21.0834 | 20.5306 | 20.5351 | 20.4585 | 20.4681 | 20.1988 |  | 20.2689 | 19.9372 | 20.1435 | 19.7186 | 20.122 | 20.3781 |  | 20.4483 |  |  | 20.3013 | 20.3974 | 20.6285 | [5 empty] | 21.9657 | 20.346 | 21.6923 | 22.086 | 19.5627 | 21.219 | 21.8525 | 19.3821 | 20.028 | 21.2237 |  | 19.7966 | 21.0152 | 18.8524 | 19.7106 | 20.8692 | 19.3854 | 20.1504 | 18.98 | 20.167 | 19.1189 | 20.3133 | 18.8111 | 20.1526 | 21.1687 | 19.4178 | 19.8009 | 21.0329 | 18.9286 | 19.8174 | 20.8613 | 18.9996 | 20.2531 | 19.2551 | 19.9633 | 18.8848 | 20.1843 | -0.11681 | 20.9488 | 0.049224 | 0.015536 | -27.0136 | 3.0977 | -0.62 | -0.64 | 0.83915 | -0.63958 | -7.966 | 0.8059 | 0.53978 | -16.7087 | 4.5451 | 0.42222 | 0.42529 | 0.43064 | 0.41176 | 0.48112 | 0.43986 | 0.42881
42838.4129 | -637 | 22.8931 | 22.8611 | 22.8491 | 22.7821 | 22.4295 | 21.7748 | 22.7275 | 21.8407 | 22.3852 | 22.3919 | 22.3876 | 22.0738 | 21.2986 | 22.2569 | 21.5931 | 21.7603 | 21.8982 | 21.0896 | 21.1887 | 21.4114 | 20.4955 | 20.6375 | 20.9382 | 21.9129 | 21.6887 | 21.3299 | 20.4473 | 20.5726 | 20.5233 | 22.0483 | 21.6612 | 21.1886 | 22.0001 | 21.748 | 21.3639 | 19.9381 | 20.5366 |  | 20.5726 | 20.2358 | 20.3288 | 19.17 |  | 16.7658 | 16.778 | 16.489 | 16.7263 | 16.9218 | 17.4071 | 17.5991 | 15.6971 | 16.6278 | 16.0168 | 16.8717 | 17.8833 | 46.8172 | 50.2164 | 45.8359 | 21.4214 |  |  | 0.29265 | -0.21166 | -44.8969 | 0.42248 | 0.11907 | -197.8388 | 14.9266 | -0.14887 | -0.58098 | -0.17276 | 0.072335 | 8.8284 | 9.0584 | 1.9777 | 21.8129 | 22.0371 | 22.2324 | 22.2984 | 22.138 | 21.4776 | 20.3035 | 22.222 | 22.3906 | 22.4283 | 22.3808 | 22.0144 | 21.2651 | 22.2898 | 16.9827 | 17.0397 | 16.0709 | 16.0427 | 16.0815 | 17.0754 | 16.7792 | 22.4021 | 22.1687 | 21.7317 | 22.1034 | 21.8209 | 21.3326 | 21.9643 | 21.5591 | 20.9386 | 20.1516 | 20.4455 | 20.0309 | 19.8038 | 0.005517 | -0.17077 | 20.7818 | 22.1048 | 22.4165 | 20.1497 | 21.716 | 22.1604 | 21.9787 | 21.7462 | 21.3075 | 21.8206 | 21.4839 | 21.0891 | 20.5477 | 20.55 | 20.4724 | 20.4631 | 20.2072 |  | 20.2696 | 19.9449 | 20.1537 | 19.7281 | 20.1238 | 20.3871 |  | 20.4556 |  |  | 20.3037 | 20.3922 | 20.6282 | [5 empty] | 21.9617 | 20.3444 | 21.6996 | 22.0865 | 19.5674 | 21.2252 | 21.861 | 19.3842 | 20.0279 | 21.2226 |  | 19.8031 | 21.0181 | 18.8562 | 19.7137 | 20.8675 | 19.386 | 20.1518 | 18.9839 | 20.1688 | 19.1233 | 20.3128 | 18.8065 | 20.1518 | 21.169 | 19.422 | 19.795 | 21.0317 | 18.9326 | 19.8308 | 20.8664 | 19.0057 | 20.2507 | 19.2583 | 19.9688 | 18.8864 | 20.1913 | -0.10754 | 20.9474 | 0.049089 | 0.016342 | -27.3347 | 3.0978 | -0.51 | -0.24 | 0.64606 | -0.54592 | -7.951 | 0.77129 | 0.4099 | -16.7085 | 4.5895 | 0.42202 | 0.42542 | 0.43044 | 0.41258 | 0.47934 | 0.43972 | 0.42927
42838.4129 | -636 | 22.8933 | 22.8582 | 22.8468 | 22.7784 | 22.4268 | 21.7795 | 22.7342 | 21.84 | 22.3795 | 22.3982 | 22.3888 | 22.0719 | 21.2943 | 22.2633 | 21.5856 | 21.7548 | 21.8988 | 21.0855 | 21.1908 | 21.4095 | 20.4924 | 20.6354 | 20.9388 | 21.9123 | 21.6797 | 21.3203 | 20.4404 | 20.5697 | 20.516 | 22.0398 | 21.6602 | 21.1909 | 21.9971 | 21.7516 | 21.3591 | 19.9435 | 20.532 |  | 20.573 | 20.2402 | 20.3301 | 19.1718 |  | 16.7718 | 16.7706 | 16.4955 | 16.7169 | 16.9157 | 17.3956 | 17.5781 | 15.7459 | 16.6428 | 16.0149 | 16.8797 | 17.8862 | 46.8912 | 50.181 | 45.8802 | 21.4204 |  |  | 0.58835 | 0.007163 | -44.3417 | 0.60582 | 0.03496 | -197.8808 | 14.993 | -0.23364 | -0.077747 | -0.34144 | -0.053525 | 8.8292 | 9.0586 | 1.9786 | 21.8122 | 22.0311 | 22.2255 | 22.2943 | 22.1327 | 21.4737 | 20.3032 | 22.2196 | 22.3835 | 22.4261 | 22.3739 | 22.0116 | 21.2581 | 22.2876 | 16.9768 | 17.0311 | 16.0663 | 16.0558 | 16.0804 | 17.0796 | 16.7778 | 22.4044 | 22.1802 | 21.7417 | 22.105 | 21.8266 | 21.3375 | 21.9617 | 21.5613 | 20.9422 | 20.151 | 20.4554 | 20.037 | 19.8019 | -0.081773 | -0.098112 | 20.7882 | 22.1083 | 22.4182 | 20.147 | 21.71 | 22.1642 | 21.9769 | 21.7488 | 21.3043 | 21.8166 | 21.4823 | 21.0925 | 20.5473 | 20.5615 | 20.4655 | 20.4651 | 20.2025 |  | 20.2626 | 19.9459 | 20.1571 | 19.7264 | 20.1177 | 20.3717 |  | 20.4514 |  |  | 20.3031 | 20.4031 | 20.6224 | [5 empty] | 21.9561 | 20.3476 | 21.6998 | 22.0813 | 19.573 | 21.2234 | 21.8557 | 19.3831 | 20.0228 | 21.2256 |  | 19.8011 | 21.0178 | 18.8552 | 19.7204 | 20.8684 | 19.3831 | 20.1527 | 18.9787 | 20.168 | 19.1207 | 20.3123 | 18.8131 | 20.1583 | 21.1649 | 19.4258 | 19.797 | 21.0346 | 18.9316 | 19.8299 | 20.8622 | 19.0054 | 20.2411 | 19.2549 | 19.9683 | 18.885 | 20.1887 | -0.32717 | 20.9454 | 0.049329 | 0.016357 | -27.1125 | 3.0978 | -0.52 | -0.63 | 0.91603 | 0.10043 | -7.9016 | 0.92359 | 0.22211 | -16.71 | 4.5996 | 0.42191 | 0.4255 | 0.43028 | 0.41372 | 0.47969 | 0.43985 | 0.4293
42838.4129 | -635 | 22.8996 | 22.8708 | 22.859 | 22.7939 | 22.4363 | 21.79 | 22.7345 | 21.8454 | 22.386 | 22.4013 | 22.3943 | 22.0886 | 21.3074 | 22.2615 | 21.5853 | 21.7585 | 21.9012 | 21.0848 | 21.1848 | 21.4163 | 20.4869 | 20.6394 | 20.9435 | 21.9147 | 21.6739 | 21.3138 | 20.4492 | 20.5743 | 20.5226 | 22.0382 | 21.6521 | 21.1871 | 22.0023 | 21.7479 | 21.3631 | 19.9396 | 20.5315 |  | 20.5779 | 20.2369 | 20.3376 | 19.1798 |  | 16.7579 | 16.7667 | 16.4874 | 16.7106 | 16.8989 | 17.3704 | 17.5522 | 15.69 | 16.6429 | 16.0194 | 16.8777 | 17.8777 | 46.9415 | 50.1375 | 45.9112 | 21.4267 |  |  | 0.43984 | -0.22611 | -44.3909 | 0.51251 | 0.0941 | -197.8631 | 14.7735 | -0.30132 | -0.27527 | 0.20655 | -0.070711 | 8.8289 | 9.0585 | 1.9787 | 21.8171 | 22.0421 | 22.2273 | 22.2939 | 22.1366 | 21.4756 | 20.3043 | 22.216 | 22.39 | 22.4272 | 22.3804 | 22.0158 | 21.2627 | 22.2918 | 16.9855 | 17.0314 | 16.0555 | 16.0832 | 16.1112 | 17.0742 | 16.7875 | 22.4082 | 22.1749 | 21.7454 | 22.1016 | 21.8235 | 21.3439 | 21.9679 | 21.5526 | 20.9368 | 20.1476 | 20.4498 | 20.0326 | 19.7951 | -0.17437 | -0.02926 | 20.7973 | 22.1193 | 22.4106 | 20.161 | 21.7201 | 22.1698 | 21.9797 | 21.7473 | 21.3296 | 21.8261 | 21.4899 | 21.091 | 20.5436 | 20.5667 | 20.4764 | 20.4672 | 20.2036 |  | 20.2692 | 19.9274 | 20.166 | 19.7306 | 20.1277 | 20.3787 |  | 20.4549 |  |  | 20.2954 | 20.399 | 20.6214 | [5 empty] | 21.9568 | 20.3467 | 21.697 | 22.0787 | 19.5641 | 21.2104 | 21.8488 | 19.3811 | 20.0195 | 21.2138 |  | 19.7982 | 21.0089 | 18.8516 | 19.7185 | 20.8701 | 19.3764 | 20.146 | 18.9766 | 20.1675 | 19.1231 | 20.3173 | 18.8232 | 20.1648 | 21.164 | 19.4175 | 19.8067 | 21.0397 | 18.9297 | 19.8358 | 20.8614 | 19.014 | 20.248 | 19.2591 | 19.9767 | 18.9017 | 20.2012 | -0.17543 | 20.9462 | 0.05041 | 0.016226 | -26.9798 | 3.0978 | -0.54 | 0.11 | 0.79204 | -0.56424 | -7.9059 | 0.84948 | 0.36438 | -16.7085 | 4.5656 | 0.4221 | 0.42631 | 0.4305 | 0.41212 | 0.48202 | 0.4395 | 0.42938
42838.4129 | -634 | 22.8916 | 22.8631 | 22.8542 | 22.7837 | 22.4266 | 21.7702 | 22.7263 | 21.8363 | 22.3786 | 22.3951 | 22.3928 | 22.0728 | 21.2927 | 22.2573 | 21.5762 | 21.7539 | 21.8857 | 21.0897 | 21.1801 | 21.3973 | 20.4874 | 20.6276 | 20.9378 | 21.91 | 21.6723 | 21.316 | 20.4474 | 20.5709 | 20.5168 | 22.0321 | 21.6568 | 21.1848 | 21.9983 | 21.7416 | 21.3598 | 19.934 | 20.5268 |  | 20.5717 | 20.233 | 20.3259 | 19.1769 |  | 16.7506 | 16.7673 | 16.4772 | 16.7111 | 16.8887 | 17.3448 | 17.5455 | 15.6284 | 16.6454 | 16.0074 | 16.8837 | 17.8732 | 46.996 | 50.0858 | 45.9446 | 21.4166 |  |  | 0.41553 | -0.14923 | -44.3081 | 0.50725 | 0.21698 | -197.8591 | 14.6605 | -0.37426 | -0.14566 | 0.029693 | -0.13755 | 8.8291 | 9.0586 | 1.9782 | 21.8176 | 22.0378 | 22.231 | 22.292 | 22.1405 | 21.4779 | 20.3081 | 22.2222 | 22.3914 | 22.424 | 22.3814 | 22.0255 | 21.266 | 22.2941 | 17.0053 | 17.004 | 16.0392 | 16.0723 | 16.1291 | 17.08 | 16.7739 | 22.4048 | 22.1702 | 21.7443 | 22.1034 | 21.8196 | 21.3304 | 21.9622 | 21.5486 | 20.9345 | 20.1435 | 20.4438 | 20.0294 | 19.7975 | -0.083739 | -0.1158 | 20.7934 | 22.1093 | 22.4103 | 20.1603 | 21.7193 | 22.1635 | 21.9934 | 21.7443 | 21.3084 | 21.8279 | 21.4879 | 21.0919 | 20.5446 | 20.5606 | 20.4617 | 20.4645 | 20.1913 |  | 20.2703 | 19.9171 | 20.1559 | 19.7367 | 20.1291 | 20.3758 |  | 20.4559 |  |  | 20.3134 | 20.4062 | 20.6281 | [5 empty] | 21.9646 | 20.3511 | 21.7033 | 22.0868 | 19.5735 | 21.2236 | 21.8544 | 19.3819 | 20.0171 | 21.2186 |  | 19.7901 | 21.0068 | 18.8532 | 19.716 | 20.8643 | 19.3824 | 20.1531 | 18.9823 | 20.1594 | 19.1235 | 20.3162 | 18.8126 | 20.1581 | 21.1577 | 19.4139 | 19.7952 | 21.0316 | 18.9314 | 19.8313 | 20.8604 | 19.0004 | 20.2366 | 19.249 | 19.9661 | 18.8934 | 20.1955 | -0.26354 | 20.9464 | 0.050509 | 0.016524 | -27.0122 | 3.0978 | -0.81 | -0.26 | 0.76983 | -0.45839 | -7.8985 | 0.84511 | 0.55328 | -16.7076 | 4.5479 | 0.42248 | 0.42626 | 0.43038 | 0.4106 | 0.48223 | 0.43939 | 0.42917
42838.413 | -633 | 22.8933 | 22.8609 | 22.8561 | 22.7892 | 22.4276 | 21.7781 | 22.7242 | 21.8426 | 22.3859 | 22.3926 | 22.3876 | 22.077 | 21.2919 | 22.2569 | 21.5835 | 21.7568 | 21.8974 | 21.0897 | 21.1843 | 21.4065 | 20.4798 | 20.6329 | 20.9268 | 21.9091 | 21.6814 | 21.3142 | 20.4464 | 20.5735 | 20.5102 | 22.0407 | 21.6595 | 21.1938 | 22.0008 | 21.7398 | 21.361 | 19.9418 | 20.5253 |  | 20.5796 | 20.2373 | 20.3253 | 19.1767 |  | 16.7489 | 16.7516 | 16.4701 | 16.6901 | 16.8738 | 17.3483 | 17.5225 | 15.6177 | 16.6429 | 16.0267 | 16.8848 | 17.8748 | 47.0343 | 50.0372 | 45.9687 | 21.4185 |  |  | 0.49833 | -0.257 | -44.067 | 0.68796 | 0.18938 | -197.842 | 14.742 | -0.42092 | -0.088644 | 0.061583 | -0.040331 | 8.8285 | 9.0581 | 1.9777 | 21.8069 | 22.0351 | 22.2257 | 22.2985 | 22.1303 | 21.4766 | 20.3045 | 22.2229 | 22.3916 | 22.4195 | 22.373 | 22.02 | 21.2558 | 22.2901 | 17.0332 | 17.0232 | 16.0533 | 16.085 | 16.1421 | 17.0722 | 16.7769 | 22.4074 | 22.1701 | 21.7334 | 22.0986 | 21.8259 | 21.3281 | 21.9604 | 21.5558 | 20.9395 | 20.1441 | 20.453 | 20.0333 | 19.8037 | -0.076662 | 0.013916 | 20.7954 | 22.1031 | 22.4165 | 20.1556 | 21.7052 | 22.1598 | 21.9727 | 21.7367 | 21.3105 | 21.8244 | 21.4863 | 21.0819 | 20.5429 | 20.5434 | 20.4529 | 20.4547 | 20.1843 |  | 20.2636 | 19.8982 | 20.1578 | 19.7416 | 20.126 | 20.3726 |  | 20.4526 |  |  | 20.3098 | 20.4006 | 20.6407 | [5 empty] | 21.9631 | 20.3546 | 21.7022 | 22.0895 | 19.5812 | 21.219 | 21.8526 | 19.3893 | 20.0262 | 21.2262 |  | 19.8003 | 21.0096 | 18.8556 | 19.7224 | 20.8859 | 19.3816 | 20.1585 | 18.9829 | 20.1696 | 19.1262 | 20.3221 | 18.8141 | 20.1584 | 21.1593 | 19.423 | 19.7949 | 21.0295 | 18.932 | 19.829 | 20.8574 | 18.9989 | 20.2366 | 19.2542 | 19.9644 | 18.8959 | 20.1927 | -0.089173 | 20.9467 | 0.049421 | 0.016908 | -27.1083 | 3.0978 | -0.68 | 0.36 | 0.84304 | -0.60153 | -7.8768 | 0.98418 | 0.5169 | -16.707 | 4.5605 | 0.42245 | 0.42685 | 0.43014 | 0.40659 | 0.48103 | 0.43966 | 0.42902
42838.413 | -632 | 22.894 | 22.8679 | 22.8535 | 22.7902 | 22.4318 | 21.7853 | 22.7339 | 21.8431 | 22.3849 | 22.3993 | 22.3856 | 22.0748 | 21.2999 | 22.2598 | 21.5879 | 21.7645 | 21.9043 | 21.0926 | 21.1866 | 21.408 | 20.4953 | 20.6471 | 20.9425 | 21.9213 | 21.682 | 21.3232 | 20.4489 | 20.5818 | 20.5146 | 22.0453 | 21.6649 | 21.1963 | 22.0077 | 21.7468 | 21.3679 | 19.9481 | 20.5298 |  | 20.5851 | 20.2433 | 20.337 | 19.1911 |  | 16.739 | 16.7512 | 16.4639 | 16.6844 | 16.861 | 17.3387 | 17.5319 | 15.5666 | 16.6413 | 16.0502 | 16.881 | 17.8754 | 47.0512 | 49.9869 | 46.017 | 21.4251 |  |  | 0.25191 | -0.32796 | -43.3428 | 0.64459 | 0.13681 | -197.8289 | 14.9595 | -0.33352 | -0.09312 | -0.031149 | -0.15248 | 8.8285 | 9.0582 | 1.9777 | 21.8262 | 22.042 | 22.236 | 22.3033 | 22.1422 | 21.4894 | 20.3044 | 22.2241 | 22.3926 | 22.437 | 22.3868 | 22.0312 | 21.2585 | 22.3049 | 17.0472 | 17.0621 | 16.063 | 16.0949 | 16.1435 | 17.068 | 16.7725 | 22.4084 | 22.1792 | 21.7472 | 22.097 | 21.8207 | 21.3333 | 21.9674 | 21.5546 | 20.9337 | 20.1452 | 20.4541 | 20.0325 | 19.8097 | -0.014536 | -0.084988 | 20.7895 | 22.116 | 22.4246 | 20.1563 | 21.7118 | 22.1573 | 21.9751 | 21.7486 | 21.3069 | 21.8147 | 21.4923 | 21.0913 | 20.5388 | 20.5404 | 20.4574 | 20.4504 | 20.1948 |  | 20.2685 | 19.8928 | 20.1543 | 19.7434 | 20.1144 | 20.3748 |  | 20.4565 |  |  | 20.3033 | 20.3948 | 20.6439 | [5 empty] | 21.9572 | 20.3535 | 21.7075 | 22.0821 | 19.5749 | 21.219 | 21.8592 | 19.3855 | 20.0275 | 21.2309 |  | 19.8076 | 21.0145 | 18.8559 | 19.7278 | 20.8873 | 19.3912 | 20.1665 | 18.9805 | 20.1707 | 19.1358 | 20.3243 | 18.8073 | 20.1599 | 21.1604 | 19.4138 | 19.7953 | 21.0323 | 18.9294 | 19.8248 | 20.8606 | 19.0035 | 20.2386 | 19.2498 | 19.9697 | 18.9008 | 20.1954 | -0.059307 | 20.9461 | 0.048739 | 0.014694 | -27.0718 | 3.0977 | -0.6 | -0.01 | 0.59939 | -0.67953 | -7.8118 | 0.95265 | 0.43933 | -16.7062 | 4.594 | 0.42232 | 0.42688 | 0.4297 | 0.40455 | 0.47944 | 0.43947 | 0.42889
42838.413 | -631 | 22.8948 | 22.8642 | 22.852 | 22.7915 | 22.4275 | 21.7746 | 22.7338 | 21.8399 | 22.3784 | 22.4004 | 22.3823 | 22.0738 | 21.3002 | 22.2648 | 21.5857 | 21.7526 | 21.8916 | 21.0808 | 21.182 | 21.4023 | 20.4876 | 20.6332 | 20.9333 | 21.9052 | 21.6703 | 21.3123 | 20.4482 | 20.5725 | 20.5041 | 22.0421 | 21.6623 | 21.1871 | 22.0055 | 21.7451 | 21.3672 | 19.9494 | 20.5293 |  | 20.5804 | 20.2386 | 20.3376 | 19.199 |  | 16.722 | 16.7316 | 16.4495 | 16.6803 | 16.8366 | 17.3192 | 17.528 | 15.4987 | 16.6341 | 16.0528 | 16.8706 | 17.8859 | 47.063 | 49.9451 | 46.0413 | 21.4283 |  |  | 0.44838 | 0.040675 | -43.4644 | 0.83778 | 0.055988 | -197.8512 | 15.1185 | -0.26978 | 0.032592 | -0.23025 | -0.082169 | 8.8287 | 9.0584 | 1.9786 | 21.8158 | 22.0371 | 22.2318 | 22.2959 | 22.1359 | 21.4773 | 20.3043 | 22.2238 | 22.3834 | 22.4249 | 22.3817 | 22.0259 | 21.2669 | 22.2886 | 17.0667 | 17.0904 | 16.083 | 16.1003 | 16.1702 | 17.0806 | 16.7842 | 22.408 | 22.1783 | 21.745 | 22.0939 | 21.8199 | 21.3347 | 21.9689 | 21.5529 | 20.938 | 20.1483 | 20.4565 | 20.0369 | 19.7972 | 0.015347 | -0.1546 | 20.7856 | 22.1064 | 22.4101 | 20.1601 | 21.7126 | 22.1547 | 21.9692 | 21.7457 | 21.3127 | 21.8194 | 21.4897 | 21.0897 | 20.5402 | 20.5416 | 20.4482 | 20.4395 | 20.1906 |  | 20.259 | 19.8703 | 20.1472 | 19.7463 | 20.1152 | 20.3745 |  | 20.4461 |  |  | 20.3072 | 20.389 | 20.6384 | [5 empty] | 21.9574 | 20.3591 | 21.6994 | 22.0906 | 19.5793 | 21.2138 | 21.8589 | 19.3806 | 20.0175 | 21.2146 |  | 19.8035 | 21.014 | 18.8563 | 19.7205 | 20.8767 | 19.3889 | 20.1636 | 18.9776 | 20.1702 | 19.1255 | 20.3219 | 18.8 | 20.142 | 21.1451 | 19.4059 | 19.7852 | 21.017 | 18.9254 | 19.824 | 20.8498 | 18.9873 | 20.2354 | 19.2443 | 19.9608 | 18.8907 | 20.1946 | -0.18471 | 20.9447 | 0.04708 | 0.0137 | -26.9301 | 3.0978 | -0.32 | 0.87 | 0.79967 | 0.2393 | -7.8225 | 1.086 | 0.28104 | -16.7065 | 4.6182 | 0.42212 | 0.42727 | 0.42964 | 0.40386 | 0.47857 | 0.43929 | 0.42934
42838.413 | -630 | 22.892 | 22.8637 | 22.8494 | 22.7903 | 22.4345 | 21.7712 | 22.728 | 21.8365 | 22.3847 | 22.3907 | 22.3816 | 22.0771 | 21.2995 | 22.2567 | 21.5895 | 21.7571 | 21.8981 | 21.0887 | 21.1874 | 21.4151 | 20.489 | 20.6368 | 20.94 | 21.909 | 21.6821 | 21.3141 | 20.4472 | 20.5788 | 20.5087 | 22.0389 | 21.6591 | 21.1812 | 21.9981 | 21.7378 | 21.358 | 19.9467 | 20.5167 |  | 20.5772 | 20.2264 | 20.3281 | 19.1835 |  | 16.7311 | 16.735 | 16.4493 | 16.6811 | 16.8393 | 17.3043 | 17.5651 | 15.4737 | 16.646 | 16.0446 | 16.884 | 17.8775 | 47.0819 | 49.8826 | 46.0713 | 21.4243 |  |  | 0.40567 | -0.22217 | -43.1464 | 0.47899 | -0.1648 | -197.8558 | 14.9628 | -0.35389 | -0.071325 | -0.22458 | -0.10908 | 8.828 | 9.058 | 1.9785 | 21.8154 | 22.0392 | 22.2344 | 22.3056 | 22.1405 | 21.4766 | 20.3056 | 22.225 | 22.3956 | 22.4284 | 22.3807 | 22.0178 | 21.2688 | 22.2981 | 17.0711 | 17.0737 | 16.0758 | 16.0985 | 16.1682 | 17.0729 | 16.7754 | 22.4063 | 22.1722 | 21.7347 | 22.0964 | 21.8208 | 21.323 | 21.9662 | 21.5568 | 20.9377 | 20.1439 | 20.451 | 20.0297 | 19.7831 | -0.089048 | -0.1295 | 20.7919 | 22.1126 | 22.4237 | 20.1659 | 21.7124 | 22.1667 | 21.9779 | 21.7427 | 21.3117 | 21.8182 | 21.495 | 21.0907 | 20.546 | 20.5584 | 20.4466 | 20.4436 | 20.1942 |  | 20.2651 | 19.8574 | 20.152 | 19.7501 | 20.1238 | 20.3781 |  | 20.4593 |  |  | 20.3072 | 20.3999 | 20.6435 | [5 empty] | 21.9629 | 20.3629 | 21.7057 | 22.0938 | 19.5788 | 21.2193 | 21.8517 | 19.3706 | 20.0105 | 21.2183 |  | 19.8044 | 21.009 | 18.8504 | 19.718 | 20.8758 | 19.3844 | 20.163 | 18.9767 | 20.163 | 19.1243 | 20.3302 | 18.8008 | 20.1428 | 21.1416 | 19.4055 | 19.7792 | 21.0183 | 18.9305 | 19.8229 | 20.8527 | 18.9828 | 20.2284 | 19.2461 | 19.961 | 18.8987 | 20.191 | -0.13759 | 20.9459 | 0.047707 | 0.013576 | -27.0226 | 3.0978 | -0.35 | 0.22 | 0.76063 | -0.55927 | -7.7938 | 0.82119 | -0.48216 | -16.7063 | 4.5942 | 0.42223 | 0.42779 | 0.42983 | 0.40246 | 0.47835 | 0.43963 | 0.42958
42838.413 | -629 | 22.8919 | 22.8678 | 22.85 | 22.7856 | 22.4275 | 21.7719 | 22.7254 | 21.8403 | 22.3861 | 22.3979 | 22.3765 | 22.0705 | 21.2989 | 22.2567 | 21.5871 | 21.7531 | 21.9018 | 21.0828 | 21.1913 | 21.4194 | 20.4918 | 20.6373 | 20.9402 | 21.9073 | 21.6807 | 21.3126 | 20.4527 | 20.5779 | 20.5187 | 22.0438 | 21.6603 | 21.187 | 22.0068 | 21.7458 | 21.3638 | 19.941 | 20.5244 |  | 20.5732 | 20.2359 | 20.3365 | 19.2059 |  | 16.7298 | 16.725 | 16.4477 | 16.6774 | 16.8314 | 17.2894 | 17.5717 | 15.473 | 16.6482 | 16.0733 | 16.8865 | 17.8813 | 47.0999 | 49.8352 | 46.1141 | 21.4349 |  |  | 0.4819 | -0.26817 | -43.2219 | 0.45599 | 0.13616 | -197.8381 | 14.9247 | -0.2297 | -0.17446 | 0.028224 | 0.0020272 | 8.8295 | 9.0595 | 1.9784 | 21.8099 | 22.0322 | 22.2249 | 22.2933 | 22.1309 | 21.4711 | 20.3021 | 22.2138 | 22.3925 | 22.4247 | 22.3754 | 22.0072 | 21.2588 | 22.2942 | 17.0844 | 17.0919 | 16.0741 | 16.1111 | 16.1642 | 17.0672 | 16.7747 | 22.4026 | 22.1758 | 21.7358 | 22.1005 | 21.8261 | 21.3369 | 21.9655 | 21.5507 | 20.9383 | 20.1485 | 20.454 | 20.0368 | 19.7857 | 0.0049272 | -0.15574 | 20.7923 | 22.1088 | 22.4189 | 20.156 | 21.7143 | 22.1632 | 21.9819 | 21.7471 | 21.3157 | 21.8158 | 21.4878 | 21.0931 | 20.5483 | 20.5648 | 20.4427 | 20.4518 | 20.1784 |  | 20.2592 | 19.8405 | 20.145 | 19.7383 | 20.1174 | 20.3716 |  | 20.4456 |  |  | 20.3076 | 20.4082 | 20.6418 | [5 empty] | 21.9672 | 20.3592 | 21.7083 | 22.0837 | 19.5892 | 21.2201 | 21.8576 | 19.3706 | 20.0018 | 21.2117 |  | 19.8037 | 21.009 | 18.8547 | 19.7199 | 20.8707 | 19.3837 | 20.1567 | 18.9772 | 20.1566 | 19.1256 | 20.3241 | 18.7984 | 20.1403 | 21.1335 | 19.404 | 19.7756 | 21.0149 | 18.9242 | 19.8187 | 20.8413 | 18.9769 | 20.2229 | 19.2462 | 19.958 | 18.8959 | 20.1942 | -0.29471 | 20.9453 | 0.048481 | 0.014948 | -27.0078 | 3.0978 | -0.63 | 0.05 | 0.82904 | -0.61444 | -7.8005 | 0.80122 | 0.43824 | -16.7051 | 4.5883 | 0.42246 | 0.42803 | 0.42994 | 0.40032 | 0.47846 | 0.43882 | 0.42967
42838.413 | -628 | 22.8945 | 22.8591 | 22.852 | 22.7843 | 22.4243 | 21.782 | 22.7311 | 21.8421 | 22.3873 | 22.4016 | 22.3875 | 22.0634 | 21.2978 | 22.2612 | 21.5808 | 21.752 | 21.8902 | 21.0813 | 21.1847 | 21.411 | 20.4893 | 20.6353 | 20.9342 | 21.9087 | 21.6742 | 21.3149 | 20.449 | 20.5761 | 20.5153 | 22.0392 | 21.6598 | 21.1858 | 21.9993 | 21.7424 | 21.3716 | 19.951 | 20.5263 |  | 20.5737 | 20.227 | 20.3349 | 19.207 |  | 16.7206 | 16.7252 | 16.4523 | 16.6736 | 16.827 | 17.2789 | 17.6021 | 15.5281 | 16.6572 | 16.096 | 16.8838 | 17.8794 | 47.111 | 49.7706 | 46.144 | 21.4233 |  |  | 0.41421 | -0.21626 | -42.8894 | 0.9232 | 0.088844 | -197.8486 | 15.02 | -0.17187 | -0.18536 | 0.024238 | -0.054046 | 8.8284 | 9.0582 | 1.9782 | 21.8069 | 22.0319 | 22.2236 | 22.2907 | 22.1313 | 21.4633 | 20.2935 | 22.2137 | 22.3869 | 22.4173 | 22.373 | 22.013 | 21.2538 | 22.2829 | 17.1036 | 17.1044 | 16.0961 | 16.1198 | 16.178 | 17.0727 | 16.7766 | 22.4015 | 22.1706 | 21.7351 | 22.101 | 21.8332 | 21.332 | 21.954 | 21.5471 | 20.9404 | 20.1409 | 20.4541 | 20.0318 | 19.7783 | 0.013971 | -0.051133 | 20.7893 | 22.1097 | 22.4154 | 20.1533 | 21.7094 | 22.1598 | 21.9734 | 21.7408 | 21.3068 | 21.8197 | 21.485 | 21.0816 | 20.5381 | 20.5706 | 20.4425 | 20.4375 | 20.1568 |  | 20.2613 | 19.8292 | 20.1455 | 19.7334 | 20.1158 | 20.3701 |  | 20.4512 |  |  | 20.3073 | 20.4038 | 20.6405 | [5 empty] | 21.9656 | 20.3612 | 21.703 | 22.0887 | 19.5816 | 21.2154 | 21.8487 | 19.3772 | 20.0072 | 21.219 |  | 19.8036 | 21.0073 | 18.8548 | 19.7186 | 20.8777 | 19.3814 | 20.1694 | 18.9787 | 20.1658 | 19.1327 | 20.3272 | 18.7929 | 20.1381 | 21.1345 | 19.4084 | 19.7834 | 21.0224 | 18.9293 | 19.8229 | 20.8419 | 18.9771 | 20.2253 | 19.2409 | 19.9574 | 18.8948 | 20.1938 | -0.092883 | 20.9455 | 0.048094 | 0.014869 | -27.0559 | 3.0978 | -0.7 | -0.52 | 0.76861 | -0.55177 | -7.7705 | 1.14 | 0.354 | -16.7053 | 4.6028 | 0.42314 | 0.42836 | 0.43002 | 0.39883 | 0.47623 | 0.43913 | 0.42962
42838.413 | -627 | 22.8908 | 22.8561 | 22.8498 | 22.7821 | 22.4215 | 21.7751 | 22.7319 | 21.8349 | 22.3807 | 22.3989 | 22.3746 | 22.0703 | 21.2975 | 22.2561 | 21.5851 | 21.7537 | 21.8936 | 21.0812 | 21.1809 | 21.4032 | 20.4865 | 20.63 | 20.9319 | 21.9087 | 21.673 | 21.3133 | 20.4454 | 20.5722 | 20.5095 | 22.0342 | 21.6604 | 21.1818 | 22.0012 | 21.7439 | 21.3615 | 19.9438 | 20.5109 |  | 20.5718 | 20.2238 | 20.336 | 19.1951 |  | 16.7234 | 16.729 | 16.456 | 16.6811 | 16.8256 | 17.2771 | 17.6396 | 15.6423 | 16.6626 | 16.0871 | 16.8961 | 17.8732 | 47.1397 | 49.7038 | 46.1727 | 21.424 |  |  | 0.33339 | -0.14529 | -42.5425 | 0.79835 | 0.19332 | -197.8552 | 15.0962 | -0.28226 | -0.043692 | -0.16102 | -0.013423 | 8.8284 | 9.0581 | 1.9778 | 21.8077 | 22.04 | 22.2378 | 22.2978 | 22.1354 | 21.4738 | 20.2991 | 22.216 | 22.3865 | 22.4215 | 22.3749 | 22.0148 | 21.2597 | 22.2919 | 17.1131 | 17.0827 | 16.1016 | 16.1167 | 16.1705 | 17.07 | 16.7794 | 22.408 | 22.1751 | 21.737 | 22.101 | 21.8296 | 21.3334 | 21.9642 | 21.557 | 20.9373 | 20.1495 | 20.4573 | 20.0276 | 19.7815 | -0.060541 | -0.19283 | 20.7872 | 22.1018 | 22.4145 | 20.1367 | 21.7109 | 22.1596 | 21.9716 | 21.7448 | 21.3125 | 21.8192 | 21.4887 | 21.0859 | 20.5347 | 20.5583 | 20.4348 | 20.4366 | 20.1321 |  | 20.272 | 19.8292 | 20.147 | 19.7322 | 20.1246 | 20.3679 |  | 20.4565 |  |  | 20.3174 | 20.404 | 20.6465 | [5 empty] | 21.9669 | 20.3673 | 21.7053 | 22.0887 | 19.5872 | 21.2227 | 21.8538 | 19.3734 | 20.004 | 21.2131 |  | 19.7961 | 21.0043 | 18.84 | 19.7176 | 20.8745 | 19.3759 | 20.1665 | 18.9816 | 20.1637 | 19.1314 | 20.3324 | 18.7913 | 20.1387 | 21.136 | 19.3985 | 19.7798 | 21.0205 | 18.9362 | 19.8191 | 20.8476 | 18.9722 | 20.2299 | 19.2406 | 19.9616 | 18.8971 | 20.1935 | -0.24518 | 20.9459 | 0.048321 | 0.015609 | -27.0687 | 3.0977 | -0.54 | -0.44 | 0.68955 | -0.45226 | -7.739 | 1.0602 | 0.52219 | -16.7055 | 4.6144 | 0.42418 | 0.42841 | 0.43035 | 0.39746 | 0.47594 | 0.43921 | 0.42982
42838.413 | -626 | 22.8872 | 22.8644 | 22.8503 | 22.779 | 22.4305 | 21.7759 | 22.7281 | 21.8473 | 22.3774 | 22.3911 | 22.379 | 22.0693 | 21.2932 | 22.2567 | 21.5854 | 21.7609 | 21.897 | 21.0825 | 21.1885 | 21.4111 | 20.4892 | 20.6304 | 20.936 | 21.905 | 21.6791 | 21.3198 | 20.4516 | 20.5789 | 20.5099 | 22.0407 | 21.6574 | 21.1872 | 22.0039 | 21.7451 | 21.3624 | 19.9525 | 20.5169 |  | 20.576 | 20.2298 | 20.3381 | 19.1881 |  | 16.7262 | 16.74 | 16.4578 | 16.6828 | 16.813 | 17.2786 | 17.6455 | 15.6911 | 16.6663 | 16.1013 | 16.8939 | 17.8815 | 47.1728 | 49.6429 | 46.2071 | 21.434 |  |  | 0.52132 | -0.044749 | -41.8052 | 0.41065 | 0.10067 | -197.8598 | 15.7645 | -0.25729 | -0.027151 | 0.11466 | 0.010534 | 8.8293 | 9.0589 | 1.9784 | 21.8079 | 22.0302 | 22.2344 | 22.2921 | 22.1316 | 21.4742 | 20.3004 | 22.2161 | 22.3915 | 22.4256 | 22.3748 | 22.0166 | 21.2597 | 22.2942 | 17.1314 | 17.0855 | 16.1019 | 16.1173 | 16.1627 | 17.0689 | 16.773 | 22.4059 | 22.1843 | 21.744 | 22.1035 | 21.8354 | 21.3352 | 21.9641 | 21.5529 | 20.9453 | 20.1492 | 20.4553 | 20.037 | 19.7915 | -0.028102 | -0.037438 | 20.7645 | 22.1061 | 22.4149 | 20.1412 | 21.7078 | 22.1564 | 21.9698 | 21.7465 | 21.3047 | 21.8196 | 21.4824 | 21.0816 | 20.5408 | 20.5625 | 20.4224 | 20.4335 | 20.1185 |  | 20.2647 | 19.8143 | 20.1486 | 19.7325 | 20.1184 | 20.3679 |  | 20.456 |  |  | 20.3146 | 20.4032 | 20.6461 | [5 empty] | 21.9617 | 20.3713 | 21.7021 | 22.0853 | 19.5829 | 21.2119 | 21.8554 | 19.3746 | 20.0005 | 21.2063 |  | 19.7872 | 21.0052 | 18.8452 | 19.724 | 20.8674 | 19.3778 | 20.1665 | 18.9806 | 20.1603 | 19.132 | 20.335 | 18.781 | 20.1379 | 21.1289 | 19.3896 | 19.785 | 21.0228 | 18.9299 | 19.8155 | 20.8463 | 18.9724 | 20.2255 | 19.2374 | 19.9657 | 18.8911 | 20.1954 | -0.029812 | 20.9463 | 0.048192 | 0.01407 | -27.1493 | 3.0978 | -0.57 | -0.36 | 0.86227 | -0.251 | -7.6718 | 0.76036 | 0.37683 | -16.7057 | 4.7155 | 0.42432 | 0.42887 | 0.43013 | 0.3953 | 0.47517 | 0.4397 | 0.42953
42838.413 | -625 | 22.8933 | 22.8612 | 22.8435 | 22.7767 | 22.4272 | 21.7757 | 22.725 | 21.8447 | 22.3791 | 22.3909 | 22.3802 | 22.0686 | 21.2946 | 22.2576 | 21.5815 | 21.7594 | 21.8919 | 21.0803 | 21.1846 | 21.4078 | 20.4879 | 20.6306 | 20.9338 | 21.9011 | 21.6793 | 21.3211 | 20.4482 | 20.5753 | 20.5111 | 22.0393 | 21.6564 | 21.1905 | 22.005 | 21.7431 | 21.3627 | 19.9528 | 20.5159 |  | 20.5767 | 20.2294 | 20.3392 | 19.179 |  | 16.7332 | 16.7518 | 16.4441 | 16.6662 | 16.8051 | 17.2577 | 17.6436 | 15.7261 | 16.6583 | 16.1144 | 16.8808 | 17.8784 | 47.1905 | 49.5726 | 46.2189 | 21.4355 |  |  | 0.28936 | -0.003353 | -41.7231 | 0.21943 | 0.035616 | -197.8755 | 15.1698 | -0.31446 | -0.081639 | -0.11066 | 0.048205 | 8.8297 | 9.0594 | 1.9785 | 21.8178 | 22.0451 | 22.2383 | 22.3002 | 22.1428 | 21.4749 | 20.3074 | 22.2175 | 22.4002 | 22.4273 | 22.3831 | 22.0235 | 21.2665 | 22.3011 | 17.1553 | 17.0935 | 16.1007 | 16.1182 | 16.1681 | 17.0734 | 16.7785 | 22.403 | 22.1719 | 21.739 | 22.1062 | 21.8305 | 21.3381 | 21.9595 | 21.5512 | 20.9438 | 20.146 | 20.455 | 20.0287 | 19.7936 | -0.041667 | 0.14192 | 20.7744 | 22.1044 | 22.4148 | 20.1502 | 21.7131 | 22.1635 | 21.9717 | 21.7473 | 21.3106 | 21.8196 | 21.4855 | 21.0837 | 20.5362 | 20.5596 | 20.4259 | 20.4272 | 20.1031 |  | 20.2654 | 19.7894 | 20.1451 | 19.7364 | 20.1139 | 20.3631 |  | 20.4483 |  |  | 20.3107 | 20.4021 | 20.6448 | [5 empty] | 21.9584 | 20.3674 | 21.6987 | 22.0823 | 19.5807 | 21.2104 | 21.8517 | 19.3695 | 19.9941 | 21.2082 |  | 19.7796 | 21.0015 | 18.8395 | 19.7205 | 20.865 | 19.3702 | 20.1623 | 18.9711 | 20.1574 | 19.1257 | 20.3292 | 18.7713 | 20.1326 | 21.1344 | 19.3875 | 19.7827 | 21.0253 | 18.928 | 19.8158 | 20.8411 | 18.97 | 20.2221 | 19.2363 | 19.9678 | 18.8884 | 20.1905 | -0.19454 | 20.9464 | 0.04668 | 0.011348 | -27.0029 | 3.0978 | -0.69 | 0.11 | 0.64241 | -0.068708 | -7.6644 | 0.55583 | 0.22413 | -16.7058 | 4.6255 | 0.42477 | 0.42945 | 0.42987 | 0.39316 | 0.47595 | 0.43996 | 0.42936
42838.4131 | -624 | 22.8895 | 22.8536 | 22.8456 | 22.7727 | 22.4253 | 21.7711 | 22.7226 | 21.8395 | 22.3779 | 22.3882 | 22.3827 | 22.0694 | 21.2947 | 22.2523 | 21.5838 | 21.7543 | 21.8921 | 21.0847 | 21.1797 | 21.402 | 20.488 | 20.6343 | 20.9296 | 21.9115 | 21.6702 | 21.3178 | 20.4444 | 20.5728 | 20.5067 | 22.0337 | 21.6577 | 21.1874 | 22.0021 | 21.7429 | 21.3564 | 19.9488 | 20.5063 |  | 20.5726 | 20.2244 | 20.3309 | 19.1657 |  | 16.7318 | 16.7454 | 16.4429 | 16.6516 | 16.8015 | 17.2671 | 17.6513 | 15.7645 | 16.6537 | 16.082 | 16.8848 | 17.8828 | 47.1999 | 49.5146 | 46.2185 | 21.4366 |  |  | 0.42735 | -0.35031 | -41.3432 | 0.57559 | 0.2091 | -197.8723 | 15.4129 | -0.3322 | -0.12776 | -0.059472 | 0.050635 | 8.8285 | 9.058 | 1.978 | 21.8141 | 22.0351 | 22.2215 | 22.2927 | 22.1249 | 21.4662 | 20.2991 | 22.2177 | 22.3845 | 22.4252 | 22.3798 | 22.0144 | 21.2625 | 22.2885 | 17.1545 | 17.0949 | 16.108 | 16.1153 | 16.1592 | 17.071 | 16.7718 | 22.3991 | 22.1718 | 21.7323 | 22.1029 | 21.8262 | 21.3218 | 21.9623 | 21.5527 | 20.9366 | 20.1442 | 20.4535 | 20.0225 | 19.7954 | -0.14272 | -0.0022514 | 20.7703 | 22.1046 | 22.4137 | 20.1479 | 21.7087 | 22.1512 | 21.9734 | 21.7419 | 21.3128 | 21.814 | 21.4811 | 21.0801 | 20.529 | 20.5557 | 20.4214 | 20.4124 | 20.095 |  | 20.2622 | 19.7847 | 20.1511 | 19.7353 | 20.1201 | 20.3629 |  | 20.4464 |  |  | 20.3089 | 20.3993 | 20.6336 | [5 empty] | 21.9557 | 20.3605 | 21.6995 | 22.0817 | 19.5754 | 21.214 | 21.8476 | 19.3645 | 20.0004 | 21.2077 |  | 19.7837 | 20.9998 | 18.8333 | 19.72 | 20.8708 | 19.3786 | 20.1662 | 18.9733 | 20.1555 | 19.1259 | 20.3299 | 18.7675 | 20.1321 | 21.1356 | 19.3879 | 19.7819 | 21.0188 | 18.9319 | 19.8152 | 20.8377 | 18.9695 | 20.2191 | 19.2413 | 19.9685 | 18.8896 | 20.1925 | -0.23238 | 20.9459 | 0.047584 | 0.011529 | -26.9741 | 3.0978 | -0.93 | -1.1 | 0.78069 | -0.70228 | -7.6294 | 0.90021 | 0.54306 | -16.7059 | 4.6625 | 0.42488 | 0.42978 | 0.43011 | 0.39297 | 0.47434 | 0.4402 | 0.42925
42838.4131 | -623 | 22.8879 | 22.8567 | 22.8516 | 22.7854 | 22.4247 | 21.7693 | 22.7246 | 21.841 | 22.3865 | 22.3862 | 22.3869 | 22.0724 | 21.3003 | 22.2575 | 21.5885 | 21.7588 | 21.896 | 21.0905 | 21.1843 | 21.4098 | 20.4936 | 20.6394 | 20.9359 | 21.9157 | 21.6802 | 21.3142 | 20.4413 | 20.5745 | 20.5135 | 22.0395 | 21.648 | 21.1891 | 22.0026 | 21.7487 | 21.3611 | 19.9481 | 20.5107 |  | 20.5788 | 20.2229 | 20.3386 | 19.1649 |  | 16.7352 | 16.7508 | 16.4484 | 16.6614 | 16.7986 | 17.2711 | 17.6851 | 15.7506 | 16.6641 | 16.0605 | 16.8932 | 17.8804 | 47.206 | 49.4448 | 46.2155 | 21.4362 |  |  | 0.34325 | -0.165 | -40.8971 | 0.61896 | 0.14995 | -197.9281 | 15.639 | -0.44063 | -0.12523 | -0.068493 | 0.041955 | 8.8284 | 9.0583 | 1.9779 | 21.8122 | 22.0294 | 22.2327 | 22.3046 | 22.1359 | 21.4767 | 20.2934 | 22.2182 | 22.3937 | 22.4259 | 22.3724 | 22.0221 | 21.2612 | 22.2957 | 17.1506 | 17.0778 | 16.1288 | 16.1164 | 16.1612 | 17.0672 | 16.7727 | 22.3916 | 22.1668 | 21.7307 | 22.091 | 21.8166 | 21.3231 | 21.9507 | 21.5473 | 20.9253 | 20.1416 | 20.4467 | 20.0226 | 19.7943 | -0.01316 | -0.21718 | 20.7697 | 22.1099 | 22.4196 | 20.141 | 21.7076 | 22.1575 | 21.9777 | 21.7441 | 21.3166 | 21.8207 | 21.485 | 21.0844 | 20.5379 | 20.5646 | 20.42 | 20.4243 | 20.0852 |  | 20.2606 | 19.7755 | 20.1472 | 19.7408 | 20.1168 | 20.356 |  | 20.4412 |  |  | 20.3087 | 20.3997 | 20.6357 | [5 empty] | 21.9627 | 20.3593 | 21.6977 | 22.0855 | 19.5714 | 21.2136 | 21.8504 | 19.373 | 20.0051 | 21.2121 |  | 19.7818 | 21 | 18.8394 | 19.7245 | 20.868 | 19.3787 | 20.1659 | 18.9846 | 20.1582 | 19.1341 | 20.3311 | 18.7721 | 20.1458 | 21.1372 | 19.393 | 19.7878 | 21.0275 | 18.9406 | 19.8255 | 20.8434 | 18.9702 | 20.2201 | 19.2453 | 19.9781 | 18.8955 | 20.1981 | -0.21772 | 20.9454 | 0.048475 | 0.01211 | -26.9038 | 3.0978 | -0.96 | 0.09 | 0.69967 | -0.48199 | -7.5882 | 0.93352 | 0.45989 | -16.7084 | 4.6966 | 0.4251 | 0.42991 | 0.42985 | 0.39296 | 0.47215 | 0.4402 | 0.42919
42838.4131 | -622 | 22.8925 | 22.858 | 22.8584 | 22.7854 | 22.4292 | 21.7756 | 22.7279 | 21.8487 | 22.3895 | 22.3969 | 22.3805 | 22.0778 | 21.2971 | 22.2667 | 21.5899 | 21.7662 | 21.905 | 21.0909 | 21.1921 | 21.4131 | 20.4985 | 20.6404 | 20.941 | 21.9156 | 21.6825 | 21.3177 | 20.4537 | 20.5827 | 20.5187 | 22.0401 | 21.6473 | 21.1851 | 22.0008 | 21.7458 | 21.3536 | 19.944 | 20.4973 |  | 20.569 | 20.2203 | 20.3422 | 19.1677 |  | 16.7301 | 16.7452 | 16.4415 | 16.6511 | 16.7907 | 17.2585 | 17.7158 | 15.7424 | 16.6572 | 16.0281 | 16.8886 | 17.8791 | 47.2012 | 49.3775 | 46.2024 | 21.4386 |  |  | 0.28673 | -0.14463 | -40.3609 | 0.84829 | 0.19267 | -197.8348 | 15.4333 | -0.4426 | -0.1118 | -0.40145 | 0.051677 | 8.8289 | 9.0587 | 1.9778 | 21.8122 | 22.0299 | 22.2302 | 22.3022 | 22.1348 | 21.4762 | 20.3003 | 22.2188 | 22.3901 | 22.4229 | 22.3711 | 22.0147 | 21.26 | 22.2843 | 17.181 | 17.0433 | 16.1203 | 16.1153 | 16.1656 | 17.0648 | 16.7739 | 22.4018 | 22.1729 | 21.7373 | 22.1008 | 21.8276 | 21.3367 | 21.9576 | 21.5582 | 20.9352 | 20.1448 | 20.4597 | 20.0308 | 19.8015 | 0.079439 | 0.0078292 | 20.7613 | 22.0948 | 22.4188 | 20.1354 | 21.7054 | 22.1513 | 21.9669 | 21.7387 | 21.3148 | 21.7994 | 21.4736 | 21.0805 | 20.5301 | 20.5641 | 20.4023 | 20.4121 | 20.0572 |  | 20.2686 | 19.7622 | 20.1523 | 19.7382 | 20.1195 | 20.3586 |  | 20.4466 |  |  | 20.3113 | 20.4124 | 20.6469 | [5 empty] | 21.9623 | 20.3615 | 21.7042 | 22.0877 | 19.583 | 21.213 | 21.8491 | 19.3712 | 20.0085 | 21.2075 |  | 19.7768 | 20.9946 | 18.842 | 19.7202 | 20.8699 | 19.377 | 20.17 | 18.9863 | 20.159 | 19.1313 | 20.3284 | 18.7607 | 20.1446 | 21.1284 | 19.387 | 19.7884 | 21.0216 | 18.9337 | 19.8168 | 20.8372 | 18.967 | 20.216 | 19.2373 | 19.9753 | 18.8875 | 20.1927 | -0.002915 | 20.9465 | 0.048862 | 0.012393 | -27.1595 | 3.0979 | -0.87 | -0.31 | 0.63949 | -0.45125 | -7.5382 | 1.0929 | 0.52129 | -16.7041 | 4.6655 | 0.42615 | 0.43044 | 0.43001 | 0.38931 | 0.47323 | 0.43998 | 0.4291
42838.4131 | -621 | 22.8988 | 22.8626 | 22.8487 | 22.7832 | 22.4182 | 21.7704 | 22.7207 | 21.8326 | 22.3794 | 22.3992 | 22.378 | 22.0674 | 21.2984 | 22.2593 | 21.5822 | 21.7576 | 21.893 | 21.0807 | 21.1745 | 21.4081 | 20.4921 | 20.6358 | 20.9363 | 21.9039 | 21.6773 | 21.3152 | 20.4516 | 20.5738 | 20.5064 | 22.0348 | 21.6449 | 21.1812 | 21.9939 | 21.7375 | 21.3585 | 19.9456 | 20.4865 |  | 20.5711 | 20.2098 | 20.3307 | 19.1607 |  | 16.7301 | 16.7424 | 16.434 | 16.6481 | 16.7839 | 17.2452 | 17.7212 | 15.7276 | 16.6588 | 15.9936 | 16.8853 | 17.8776 | 47.1799 | 49.3028 | 46.1965 | 21.4387 |  |  | 0.4451 | -0.20114 | -40.2419 | 0.62619 | 0.25115 | -197.7829 | 15.4004 | -0.46231 | -0.075801 | -0.40564 | 0.032234 | 8.8281 | 9.0578 | 1.9784 | 21.8081 | 22.0324 | 22.226 | 22.2926 | 22.134 | 21.47 | 20.2991 | 22.2197 | 22.3825 | 22.4227 | 22.3737 | 22.016 | 21.2595 | 22.2848 | 17.2331 | 17.0174 | 16.1189 | 16.1155 | 16.1648 | 17.0648 | 16.7755 | 22.4 | 22.169 | 21.7293 | 22.0984 | 21.8249 | 21.3327 | 21.9611 | 21.5536 | 20.9366 | 20.1414 | 20.4517 | 20.0303 | 19.7878 | -0.14783 | 0.032175 | 20.7652 | 22.1007 | 22.4065 | 20.1378 | 21.7062 | 22.1485 | 21.9658 | 21.7415 | 21.3099 | 21.8057 | 21.4821 | 21.0803 | 20.5232 | 20.5632 | 20.4054 | 20.4162 | 20.0685 |  | 20.2691 | 19.764 | 20.1537 | 19.7442 | 20.1254 | 20.3708 |  | 20.4566 |  |  | 20.294 | 20.4099 | 20.6447 | [5 empty] | 21.9593 | 20.3603 | 21.6975 | 22.0911 | 19.5819 | 21.2118 | 21.8548 | 19.3628 | 20.0004 | 21.1928 |  | 19.7764 | 20.9909 | 18.8359 | 19.7136 | 20.8652 | 19.3726 | 20.1608 | 18.9728 | 20.1542 | 19.1223 | 20.3156 | 18.7567 | 20.1416 | 21.1264 | 19.3812 | 19.7884 | 21.0156 | 18.9345 | 19.8099 | 20.8345 | 18.9673 | 20.2229 | 19.2305 | 19.9761 | 18.8879 | 20.1908 | -0.13388 | 20.946 | 0.049046 | 0.012422 | -26.9905 | 3.0978 | -1.02 | -0.14 | 0.79674 | -0.53215 | -7.527 | 0.93894 | 0.59515 | -16.7015 | 4.6605 | 0.42585 | 0.43044 | 0.43004 | 0.38352 | 0.47356 | 0.44023 | 0.42937
42838.4131 | -620 | 22.8907 | 22.8604 | 22.8379 | 22.7812 | 22.4185 | 21.7747 | 22.72 | 21.8331 | 22.3737 | 22.3942 | 22.3769 | 22.0634 | 21.2899 | 22.2529 | 21.5812 | 21.7585 | 21.9021 | 21.0837 | 21.1799 | 21.4016 | 20.4828 | 20.6345 | 20.9339 | 21.9088 | 21.6711 | 21.3133 | 20.4444 | 20.5761 | 20.5129 | 22.0267 | 21.6538 | 21.1815 | 22.0001 | 21.7391 | 21.3635 | 19.9434 | 20.4871 |  | 20.5694 | 20.2167 | 20.3358 | 19.1696 |  | 16.7197 | 16.7334 | 16.4242 | 16.6323 | 16.7644 | 17.2378 | 17.748 | 15.7375 | 16.6589 | 15.9808 | 16.8822 | 17.873 | 47.1607 | 49.2296 | 46.1901 | 21.4281 |  |  | 0.24073 | -0.25897 | -39.9541 | 0.50593 | 0.37732 | -197.8933 | 15.6278 | -0.4012 | -0.0014634 | 0.039973 | 0.002548 | 8.8282 | 9.0579 | 1.9787 | 21.8086 | 22.0323 | 22.2293 | 22.2966 | 22.1321 | 21.4738 | 20.3004 | 22.2179 | 22.3895 | 22.429 | 22.3765 | 22.01 | 21.2521 | 22.2878 | 17.2614 | 16.9985 | 16.1485 | 16.1049 | 16.1476 | 17.0657 | 16.7763 | 22.3956 | 22.1672 | 21.7323 | 22.0915 | 21.8221 | 21.3333 | 21.9623 | 21.5546 | 20.9347 | 20.1365 | 20.4445 | 20.0215 | 19.7834 | -0.19069 | -0.0054848 | 20.7617 | 22.0979 | 22.4087 | 20.1459 | 21.7071 | 22.1589 | 21.9712 | 21.7453 | 21.3091 | 21.8075 | 21.4858 | 21.0714 | 20.5314 | 20.5642 | 20.4071 | 20.4133 | 20.0641 |  | 20.2698 | 19.76 | 20.1523 | 19.74 | 20.121 | 20.3551 |  | 20.4554 |  |  | 20.2975 | 20.4068 | 20.643 | [5 empty] | 21.9633 | 20.364 | 21.7021 | 22.0926 | 19.5727 | 21.2197 | 21.8459 | 19.3707 | 20.0136 | 21.2113 |  | 19.7823 | 21.0018 | 18.8463 | 19.7186 | 20.8789 | 19.3837 | 20.1761 | 18.9816 | 20.166 | 19.1306 | 20.3232 | 18.7647 | 20.1464 | 21.1337 | 19.3945 | 19.7901 | 21.0273 | 18.9418 | 19.8173 | 20.8388 | 18.9753 | 20.2294 | 19.2343 | 19.9897 | 18.8934 | 20.1979 | -0.18044 | 20.9457 | 0.047356 | 0.011827 | -27.0601 | 3.0979 | -0.96 | -0.08 | 0.58595 | -0.60381 | -7.5 | 0.84397 | 0.72947 | -16.706 | 4.6947 | 0.426 | 0.43051 | 0.43001 | 0.38048 | 0.47037 | 0.43991 | 0.42933
42838.4131 | -619 | 22.888 | 22.8588 | 22.8462 | 22.7833 | 22.4243 | 21.7701 | 22.7258 | 21.8379 | 22.3737 | 22.3949 | 22.382 | 22.0736 | 21.2977 | 22.2548 | 21.5758 | 21.7643 | 21.8874 | 21.0746 | 21.1741 | 21.3967 | 20.4811 | 20.63 | 20.9353 | 21.9162 | 21.6814 | 21.3119 | 20.4399 | 20.5754 | 20.5166 | 22.0396 | 21.6561 | 21.1835 | 22.0063 | 21.7454 | 21.3621 | 19.9451 | 20.4802 |  | 20.5748 | 20.2183 | 20.3386 | 19.1826 |  | 16.7227 | 16.7388 | 16.4227 | 16.6323 | 16.7648 | 17.2492 | 17.7781 | 15.7814 | 16.6655 | 15.9354 | 16.8798 | 17.8692 | 47.1514 | 49.1554 | 46.1861 | 21.4215 |  |  | 0.40699 | -0.29905 | -40.0159 | 0.22929 | 0.14995 | -197.842 | 15.7474 | -0.49517 | -0.16298 | -0.21221 | -0.018631 | 8.8286 | 9.0583 | 1.9781 | 21.8058 | 22.0387 | 22.2278 | 22.2985 | 22.1391 | 21.4763 | 20.3055 | 22.2223 | 22.3936 | 22.423 | 22.3807 | 22.023 | 21.2613 | 22.2898 | 17.3173 | 16.9776 | 16.1839 | 16.1141 | 16.1373 | 17.0705 | 16.7814 | 22.3973 | 22.169 | 21.7362 | 22.0975 | 21.8175 | 21.3324 | 21.9554 | 21.5541 | 20.9325 | 20.1457 | 20.4517 | 20.0261 | 19.7804 | 0.012791 | -0.042954 | 20.7568 | 22.1089 | 22.4139 | 20.1407 | 21.7105 | 22.1602 | 21.9694 | 21.7418 | 21.3102 | 21.8155 | 21.481 | 21.0764 | 20.5306 | 20.5502 | 20.3978 | 20.4074 | 20.05 |  | 20.2563 | 19.7533 | 20.148 | 19.7468 | 20.1138 | 20.3449 |  | 20.4594 |  |  | 20.2976 | 20.4142 | 20.643 | [5 empty] | 21.9708 | 20.3601 | 21.7043 | 22.0954 | 19.5707 | 21.2175 | 21.8519 | 19.3706 | 20.0082 | 21.2149 |  | 19.7873 | 21.0023 | 18.8479 | 19.7197 | 20.8759 | 19.3847 | 20.1854 | 18.987 | 20.1705 | 19.1338 | 20.3228 | 18.7633 | 20.1545 | 21.1364 | 19.3901 | 19.7962 | 21.0214 | 18.9481 | 19.8098 | 20.8404 | 18.9803 | 20.2297 | 19.2397 | 19.9814 | 18.8982 | 20.1939 | -0.044652 | 20.9464 | 0.046601 | 0.011616 | -27.0827 | 3.0978 | -0.93 | -0.02 | 0.76188 | -0.64887 | -7.5058 | 0.56817 | 0.45988 | -16.7041 | 4.7127 | 0.42593 | 0.43055 | 0.42958 | 0.37483 | 0.46703 | 0.43961 | 0.42972
42838.4131 | -618 | 22.8927 | 22.8612 | 22.8513 | 22.7866 | 22.4322 | 21.7718 | 22.7238 | 21.8432 | 22.3731 | 22.3896 | 22.3849 | 22.0721 | 21.2995 | 22.2554 | 21.5796 | 21.7565 | 21.8918 | 21.0822 | 21.176 | 21.4055 | 20.4866 | 20.6328 | 20.9244 | 21.9078 | 21.6747 | 21.3078 | 20.4516 | 20.5763 | 20.5227 | 22.0439 | 21.6583 | 21.1877 | 22.0077 | 21.7497 | 21.3654 | 19.9482 | 20.4828 |  | 20.5819 | 20.2189 | 20.3474 | 19.1944 |  | 16.7223 | 16.7342 | 16.4149 | 16.6277 | 16.7451 | 17.2676 | 17.7969 | 15.8347 | 16.6662 | 15.8481 | 16.874 | 17.8713 | 47.1298 | 49.0896 | 46.183 | 21.4288 |  |  | 0.44838 | -0.18603 | -39.7077 | 0.20498 | 0.20844 | -197.8466 | 15.8604 | -0.37229 | -0.0020472 | -0.2164 | -0.03061 | 8.8289 | 9.0584 | 1.978 | 21.8051 | 22.0403 | 22.2272 | 22.2925 | 22.136 | 21.4772 | 20.3043 | 22.2207 | 22.3896 | 22.4265 | 22.3778 | 22.0238 | 21.2669 | 22.2971 | 17.3652 | 16.9757 | 16.1871 | 16.109 | 16.1426 | 17.0707 | 16.7883 | 22.4064 | 22.173 | 21.7425 | 22.0981 | 21.8213 | 21.3324 | 21.9549 | 21.5503 | 20.9368 | 20.142 | 20.4583 | 20.0274 | 19.7916 | -0.048155 | -0.12018 | 20.7608 | 22.1061 | 22.4133 | 20.1433 | 21.7116 | 22.156 | 21.9777 | 21.7371 | 21.3158 | 21.8233 | 21.489 | 21.0864 | 20.5342 | 20.5609 | 20.4048 | 20.4129 | 20.044 |  | 20.2549 | 19.7399 | 20.1448 | 19.748 | 20.1099 | 20.3469 |  | 20.4444 |  |  | 20.2993 | 20.4184 | 20.6515 | [5 empty] | 21.9727 | 20.3773 | 21.7119 | 22.0889 | 19.5873 | 21.2261 | 21.8541 | 19.3697 | 20.019 | 21.2188 |  | 19.7922 | 21.0134 | 18.8577 | 19.7296 | 20.8782 | 19.3857 | 20.1857 | 18.9968 | 20.166 | 19.1473 | 20.3422 | 18.7586 | 20.1609 | 21.1255 | 19.3987 | 19.7984 | 21.0215 | 18.9368 | 19.8047 | 20.8382 | 18.9772 | 20.2316 | 19.236 | 19.9857 | 18.8851 | 20.1922 | -0.20492 | 20.9459 | 0.04802 | 0.011965 | -27.0672 | 3.0978 | -0.81 | -0.18 | 0.79969 | -0.51176 | -7.4768 | 0.5372 | 0.54221 | -16.7049 | 4.7297 | 0.42606 | 0.43081 | 0.42942 | 0.36953 | 0.46748 | 0.43938 | 0.42928
42838.4131 | -617 | 22.8993 | 22.8697 | 22.8529 | 22.7879 | 22.4304 | 21.7726 | 22.7272 | 21.8442 | 22.3784 | 22.3916 | 22.3863 | 22.0722 | 21.3017 | 22.2629 | 21.5893 | 21.7484 | 21.8919 | 21.081 | 21.1876 | 21.4102 | 20.4818 | 20.631 | 20.9307 | 21.9089 | 21.6786 | 21.3166 | 20.4484 | 20.577 | 20.519 | 22.0419 | 21.6548 | 21.1885 | 22.0018 | 21.7449 | 21.3618 | 19.9482 | 20.4775 |  | 20.5816 | 20.2285 | 20.3419 | 19.1839 |  | 16.7312 | 16.7373 | 16.4246 | 16.6292 | 16.7574 | 17.296 | 17.8274 | 15.8941 | 16.6736 | 15.838 | 16.8755 | 17.8778 | 47.1293 | 49.025 | 46.1712 | 21.4374 |  |  | 0.33076 | -0.38514 | -39.6696 | 0.26149 | 0.057956 | -197.8486 | 15.7894 | -0.29081 | -0.10013 | -0.20528 | 0.055149 | 8.8282 | 9.0582 | 1.978 | 21.8164 | 22.0393 | 22.2355 | 22.2918 | 22.1317 | 21.4741 | 20.305 | 22.2265 | 22.3924 | 22.4289 | 22.3784 | 22.0225 | 21.2676 | 22.299 | 17.3847 | 16.9841 | 16.1829 | 16.1167 | 16.1386 | 17.0714 | 16.7864 | 22.4063 | 22.1729 | 21.738 | 22.1026 | 21.8205 | 21.3301 | 21.9581 | 21.5562 | 20.9391 | 20.144 | 20.4563 | 20.0301 | 19.8001 | -0.063686 | 0.0040252 | 20.7509 | 22.1025 | 22.4107 | 20.1357 | 21.7093 | 22.1542 | 21.9708 | 21.7339 | 21.3101 | 21.8234 | 21.4841 | 21.0815 | 20.5224 | 20.5675 | 20.4003 | 20.4006 | 20.0525 |  | 20.264 | 19.7507 | 20.1501 | 19.7477 | 20.1179 | 20.3508 |  | 20.45 |  |  | 20.3003 | 20.4084 | 20.6299 | [5 empty] | 21.9637 | 20.3608 | 21.6953 | 22.0817 | 19.5703 | 21.2139 | 21.8469 | 19.3743 | 20.0051 | 21.2161 |  | 19.7863 | 20.9992 | 18.8579 | 19.7312 | 20.8765 | 19.3753 | 20.185 | 18.9957 | 20.1598 | 19.1346 | 20.3259 | 18.7572 | 20.1564 | 21.1362 | 19.3876 | 19.7934 | 21.0173 | 18.9358 | 19.8092 | 20.8357 | 18.9805 | 20.2233 | 19.234 | 19.9867 | 18.8872 | 20.1876 | -0.047621 | 20.9412 | 0.04853 | 0.013497 | -26.9362 | 3.0979 | -0.57 | -0.39 | 0.68683 | -0.73636 | -7.4733 | 0.60675 | 0.28592 | -16.7058 | 4.7194 | 0.42612 | 0.43069 | 0.4297 | 0.36745 | 0.46772 | 0.43967 | 0.42911
42838.4131 | -616 | 22.9 | 22.8599 | 22.8467 | 22.7845 | 22.4268 | 21.7681 | 22.7298 | 21.8381 | 22.3836 | 22.3904 | 22.3783 | 22.0677 | 21.3002 | 22.2652 | 21.5823 | 21.755 | 21.8856 | 21.0828 | 21.1881 | 21.41 | 20.4848 | 20.6342 | 20.9356 | 21.9048 | 21.6698 | 21.315 | 20.4525 | 20.5733 | 20.5233 | 22.0454 | 21.6582 | 21.1891 | 22.0094 | 21.7487 | 21.3647 | 19.9516 | 20.4806 |  | 20.5759 | 20.2297 | 20.3457 | 19.1903 |  | 16.7326 | 16.7383 | 16.4166 | 16.6306 | 16.7766 | 17.3244 | 17.8436 | 15.9312 | 16.6763 | 15.8545 | 16.8792 | 17.8767 | 47.117 | 48.9512 | 46.1523 | 21.4339 |  |  | 0.4819 | -0.35425 | -39.3785 | 0.41065 | 0.15061 | -197.848 | 15.6731 | -0.20538 | -0.091758 | -0.23025 | 0.14091 | 8.8286 | 9.0583 | 1.978 | 21.8162 | 22.0417 | 22.2377 | 22.2981 | 22.1445 | 21.4765 | 20.3047 | 22.2279 | 22.3934 | 22.4342 | 22.3845 | 22.0234 | 21.2644 | 22.3042 | 17.3968 | 16.9878 | 16.1951 | 16.1294 | 16.1392 | 17.074 | 16.7926 | 22.4063 | 22.1776 | 21.7377 | 22.1071 | 21.8278 | 21.3283 | 21.9581 | 21.5534 | 20.9386 | 20.1451 | 20.4592 | 20.0341 | 19.7991 | -0.12463 | 0.063558 | 20.7513 | 22.1038 | 22.4164 | 20.1358 | 21.7023 | 22.155 | 21.9726 | 21.737 | 21.3108 | 21.8114 | 21.4894 | 21.0847 | 20.5227 | 20.57 | 20.3995 | 20.407 | 20.05 |  | 20.2676 | 19.7635 | 20.1498 | 19.7386 | 20.1124 | 20.3646 |  | 20.4534 |  |  | 20.2977 | 20.4059 | 20.6435 | [5 empty] | 21.9522 | 20.3529 | 21.6947 | 22.0877 | 19.5646 | 21.2161 | 21.8407 | 19.3853 | 20.0139 | 21.2287 |  | 19.798 | 21.0111 | 18.858 | 19.7326 | 20.8851 | 19.3952 | 20.2019 | 19.0079 | 20.1716 | 19.1392 | 20.338 | 18.7694 | 20.168 | 21.1373 | 19.3861 | 19.8025 | 21.0267 | 18.9424 | 19.8171 | 20.8453 | 18.9835 | 20.2354 | 19.235 | 19.991 | 18.8866 | 20.1889 | -0.14798 | 20.9455 | 0.047946 | 0.014215 | -27.0432 | 3.0978 | -0.61 | -0.25 | 0.82904 | -0.70621 | -7.4458 | 0.76036 | 0.46095 | -16.7065 | 4.7022 | 0.42631 | 0.43033 | 0.42976 | 0.36641 | 0.4671 | 0.43961 | 0.42918
42838.4132 | -615 | 22.8993 | 22.8636 | 22.8522 | 22.7794 | 22.4316 | 21.7764 | 22.7281 | 21.8398 | 22.3831 | 22.3984 | 22.3831 | 22.0711 | 21.2929 | 22.2659 | 21.578 | 21.755 | 21.8913 | 21.0846 | 21.1836 | 21.4105 | 20.4852 | 20.642 | 20.9349 | 21.9068 | 21.6811 | 21.3161 | 20.4529 | 20.5775 | 20.5425 | 22.0414 | 21.6526 | 21.1868 | 22.0055 | 21.7444 | 21.362 | 19.9477 | 20.4636 |  | 20.5737 | 20.2259 | 20.3394 | 19.1867 |  | 16.7169 | 16.7229 | 16.4094 | 16.6251 | 16.7734 | 17.3407 | 17.8537 | 15.9383 | 16.6743 | 15.8367 | 16.8713 | 17.8771 | 47.0941 | 48.8809 | 46.1163 | 21.4324 |  |  | 0.27228 | -0.013865 | -38.8764 | 0.58282 | 0.2794 | -197.8565 | 15.934 | -0.043072 | -0.15014 | -0.28606 | 0.037442 | 8.8296 | 9.0594 | 1.9788 | 21.816 | 22.0439 | 22.23 | 22.2988 | 22.1405 | 21.4836 | 20.3052 | 22.2251 | 22.3952 | 22.4306 | 22.383 | 22.0188 | 21.2657 | 22.2978 | 17.4176 | 16.9774 | 16.1873 | 16.1367 | 16.1545 | 17.0702 | 16.7891 | 22.3995 | 22.1684 | 21.7323 | 22.098 | 21.817 | 21.3307 | 21.9555 | 21.5501 | 20.9325 | 20.1421 | 20.4563 | 20.0308 | 19.7998 | 0.04641 | -0.23487 | 20.7428 | 22.1053 | 22.4161 | 20.1392 | 21.706 | 22.1624 | 21.9744 | 21.7442 | 21.3099 | 21.8173 | 21.4872 | 21.0853 | 20.5208 | 20.5655 | 20.4037 | 20.402 | 20.0533 |  | 20.2752 | 19.7718 | 20.1509 | 19.7427 | 20.122 | 20.3574 |  | 20.4571 |  |  | 20.3013 | 20.4125 | 20.6403 | [5 empty] | 21.9585 | 20.3603 | 21.7 | 22.0833 | 19.5624 | 21.2149 | 21.8502 | 19.3839 | 20.0176 | 21.2287 |  | 19.8037 | 21.0069 | 18.8561 | 19.7326 | 20.8763 | 19.392 | 20.1889 | 19.0061 | 20.1668 | 19.1402 | 20.3348 | 18.7691 | 20.177 | 21.1465 | 19.3955 | 19.8092 | 21.0272 | 18.9562 | 19.8241 | 20.8491 | 18.9903 | 20.2346 | 19.2407 | 19.9924 | 18.8955 | 20.1955 | -0.1669 | 20.9473 | 0.048708 | 0.013272 | -27.0603 | 3.0979 | -0.48 | 0.33 | 0.62319 | -0.13971 | -7.398 | 0.90581 | 0.62784 | -16.7074 | 4.7413 | 0.42648 | 0.43013 | 0.42997 | 0.36364 | 0.46755 | 0.43958 | 0.42906
42838.4132 | -614 | 22.8963 | 22.8592 | 22.845 | 22.7814 | 22.4299 | 21.7717 | 22.7257 | 21.8379 | 22.3772 | 22.397 | 22.3911 | 22.0689 | 21.3026 | 22.26 | 21.5766 | 21.7524 | 21.8924 | 21.0848 | 21.1819 | 21.4093 | 20.485 | 20.6428 | 20.9385 | 21.9042 | 21.6806 | 21.3117 | 20.4517 | 20.5729 | 20.5409 | 22.0399 | 21.6581 | 21.1909 | 22.0088 | 21.7429 | 21.3647 | 19.949 | 20.4677 |  | 20.5794 | 20.2173 | 20.3496 | 19.1972 |  | 16.7222 | 16.7221 | 16.4144 | 16.6361 | 16.804 | 17.3547 | 17.8512 | 15.9603 | 16.6811 | 15.8435 | 16.8763 | 17.8709 | 47.0644 | 48.8161 | 46.0701 | 21.4348 |  |  | 0.52724 | -0.064461 | -38.8147 | 0.36465 | -0.003156 | -197.8394 | 15.8762 | -0.18764 | 0.045435 | -0.10164 | 0.046469 | 8.8295 | 9.0594 | 1.9784 | 21.8093 | 22.0348 | 22.2284 | 22.2973 | 22.1282 | 21.4758 | 20.2991 | 22.2131 | 22.3882 | 22.4254 | 22.3726 | 22.0112 | 21.2561 | 22.2849 | 17.4028 | 16.9597 | 16.1707 | 16.1386 | 16.1806 | 17.0648 | 16.7816 | 22.4074 | 22.1759 | 21.7323 | 22.0997 | 21.8234 | 21.3344 | 21.9609 | 21.5468 | 20.9339 | 20.1435 | 20.4562 | 20.0381 | 19.8071 | 0.031468 | -0.052464 | 20.7407 | 22.1001 | 22.4108 | 20.1339 | 21.7049 | 22.1501 | 21.9694 | 21.7384 | 21.3168 | 21.817 | 21.4824 | 21.0732 | 20.5234 | 20.5544 | 20.4031 | 20.3926 | 20.0212 |  | 20.2604 | 19.7577 | 20.1398 | 19.7236 | 20.1139 | 20.347 |  | 20.4461 |  |  | 20.2949 | 20.4078 | 20.6365 | [5 empty] | 21.95 | 20.3488 | 21.6973 | 22.0715 | 19.5595 | 21.2081 | 21.8443 | 19.3881 | 20.0214 | 21.2302 |  | 19.805 | 21.0161 | 18.8552 | 19.7323 | 20.888 | 19.4001 | 20.1955 | 19.0116 | 20.1713 | 19.1392 | 20.3339 | 18.7817 | 20.176 | 21.1424 | 19.388 | 19.8097 | 21.0265 | 18.9519 | 19.812 | 20.8437 | 18.9872 | 20.2299 | 19.2312 | 19.9967 | 18.8913 | 20.1919 | -0.074518 | 20.9469 | 0.046343 | 0.012778 | -26.9568 | 3.0979 | -0.63 | -0.26 | 0.86719 | -0.30124 | -7.3921 | 0.71649 | -0.066729 | -16.7071 | 4.7328 | 0.42687 | 0.43015 | 0.43023 | 0.36467 | 0.46852 | 0.43933 | 0.4289
42838.4132 | -613 | 22.8922 | 22.8542 | 22.8399 | 22.7724 | 22.4215 | 21.7711 | 22.7231 | 21.8325 | 22.3764 | 22.3953 | 22.3838 | 22.0721 | 21.3086 | 22.2442 | 21.5734 | 21.748 | 21.8904 | 21.0736 | 21.1783 | 21.4075 | 20.4814 | 20.6235 | 20.9324 | 21.9027 | 21.6712 | 21.3092 | 20.4439 | 20.5667 | 20.5304 | 22.0325 | 21.6541 | 21.1842 | 22.0033 | 21.746 | 21.3632 | 19.9502 | 20.4659 |  | 20.5725 | 20.2262 | 20.3462 | 19.1913 |  | 16.7124 | 16.7215 | 16.4137 | 16.6301 | 16.7859 | 17.3421 | 17.8545 | 15.9655 | 16.677 | 15.8575 | 16.8709 | 17.8707 | 47.0437 | 48.7412 | 46.0392 | 21.4391 |  |  | 0.34456 | -0.15317 | -39.0052 | 0.35349 | -0.012352 | -197.8539 | 15.4458 | -0.1009 | 0.0030124 | -0.13332 | 0.16486 | 8.8289 | 9.0583 | 1.9782 | 21.806 | 22.0379 | 22.2293 | 22.3012 | 22.1352 | 21.4647 | 20.2944 | 22.2192 | 22.3874 | 22.4208 | 22.3766 | 22.0167 | 21.2557 | 22.2878 | 17.3871 | 16.9508 | 16.1453 | 16.1277 | 16.2052 | 17.0661 | 16.7858 | 22.4072 | 22.1765 | 21.7392 | 22.0988 | 21.8229 | 21.3322 | 21.963 | 21.5449 | 20.9403 | 20.1434 | 20.4616 | 20.0398 | 19.8141 | 0.04582 | -0.058741 | 20.7384 | 22.1068 | 22.4106 | 20.1312 | 21.704 | 22.1513 | 21.9727 | 21.7394 | 21.3125 | 21.8129 | 21.4843 | 21.0823 | 20.5181 | 20.5607 | 20.4048 | 20.3935 | 20.0127 |  | 20.2694 | 19.7699 | 20.152 | 19.7297 | 20.124 | 20.3569 |  | 20.4522 |  |  | 20.29 | 20.4202 | 20.6455 | [5 empty] | 21.9648 | 20.3534 | 21.7006 | 22.0827 | 19.5583 | 21.2148 | 21.85 | 19.3925 | 20.021 | 21.2359 |  | 19.8026 | 21.0079 | 18.85 | 19.7243 | 20.8876 | 19.398 | 20.201 | 19.0168 | 20.1687 | 19.1386 | 20.3283 | 18.7897 | 20.1808 | 21.1433 | 19.401 | 19.8121 | 21.0278 | 18.9566 | 19.8169 | 20.8491 | 18.99 | 20.2355 | 19.2311 | 20.0043 | 18.8906 | 20.1946 | -0.091027 | 20.9455 | 0.047234 | 0.013947 | -27.0336 | 3.0979 | -0.98 | -0.29 | 0.70103 | -0.46437 | -7.4102 | 0.70543 | -0.13201 | -16.7073 | 4.6681 | 0.42741 | 0.43022 | 0.4304 | 0.36656 | 0.47184 | 0.43953 | 0.4287
42838.4132 | -612 | 22.8924 | 22.8561 | 22.8466 | 22.7843 | 22.4276 | 21.7736 | 22.7277 | 21.8379 | 22.3865 | 22.3923 | 22.3839 | 22.0752 | 21.2966 | 22.2616 | 21.5732 | 21.7572 | 21.8994 | 21.0739 | 21.1775 | 21.4021 | 20.4856 | 20.6255 | 20.9319 | 21.9079 | 21.6696 | 21.316 | 20.4496 | 20.5756 | 20.5424 | 22.0342 | 21.6556 | 21.1802 | 21.9984 | 21.7355 | 21.3653 | 19.9441 | 20.4625 |  | 20.5667 | 20.2233 | 20.3363 | 19.1839 |  | 16.7177 | 16.7252 | 16.4241 | 16.6377 | 16.7872 | 17.3292 | 17.843 | 15.9221 | 16.6856 | 15.8795 | 16.8772 | 17.8659 | 47.0145 | 48.6677 | 46.0045 | 21.4411 |  |  | 0.38136 | -0.035549 | -38.9014 | 0.65773 | -0.020896 | -197.848 | 15.6035 | -0.17055 | 0.0024286 | -0.23424 | 0.083793 | 8.8277 | 9.0578 | 1.9778 | 21.8056 | 22.0381 | 22.2265 | 22.3029 | 22.1374 | 21.4765 | 20.2966 | 22.225 | 22.3884 | 22.4192 | 22.3812 | 22.0191 | 21.2611 | 22.2923 | 17.3628 | 16.9708 | 16.1244 | 16.1107 | 16.2 | 17.0655 | 16.7867 | 22.407 | 22.169 | 21.7327 | 22.1 | 21.8157 | 21.327 | 21.9654 | 21.5457 | 20.9351 | 20.1473 | 20.4613 | 20.04 | 19.8163 | 0.089269 | -0.15764 | 20.7403 | 22.1036 | 22.4141 | 20.1352 | 21.701 | 22.1554 | 21.9777 | 21.7386 | 21.3074 | 21.8182 | 21.4802 | 21.0792 | 20.5262 | 20.5601 | 20.4039 | 20.3948 | 20.0088 |  | 20.2649 | 19.77 | 20.1421 | 19.7235 | 20.1221 | 20.3523 |  | 20.4517 |  |  | 20.2858 | 20.4245 | 20.6437 | [5 empty] | 21.9636 | 20.3509 | 21.6991 | 22.085 | 19.5643 | 21.2113 | 21.8498 | 19.3837 | 20.0204 | 21.2286 |  | 19.7973 | 21.0021 | 18.8495 | 19.728 | 20.8764 | 19.3978 | 20.2032 | 19.016 | 20.1667 | 19.1349 | 20.3242 | 18.7887 | 20.1787 | 21.144 | 19.3927 | 19.8092 | 21.025 | 18.9506 | 19.8098 | 20.8465 | 18.9862 | 20.2339 | 19.2309 | 20.0019 | 18.8875 | 20.1933 | 0.027692 | 20.9469 | 0.048358 | 0.014027 | -27.1442 | 3.0979 | -0.5 | 0.24 | 0.73753 | -0.22371 | -7.4004 | 0.96227 | -0.17169 | -16.7067 | 4.6918 | 0.42737 | 0.42989 | 0.43051 | 0.36918 | 0.47427 | 0.43954 | 0.42878
42838.4132 | -611 | 22.891 | 22.8591 | 22.8498 | 22.7839 | 22.4325 | 21.7718 | 22.7311 | 21.8362 | 22.3891 | 22.3926 | 22.38 | 22.079 | 21.2992 | 22.262 | 21.5719 | 21.7616 | 21.896 | 21.0799 | 21.1841 | 21.4036 | 20.4869 | 20.628 | 20.931 | 21.9097 | 21.6749 | 21.3161 | 20.4484 | 20.5739 | 20.5433 | 22.0331 | 21.6508 | 21.1808 | 22.0018 | 21.7405 | 21.3636 | 19.9452 | 20.4603 |  | 20.5703 | 20.2221 | 20.339 | 19.1848 |  | 16.7186 | 16.7206 | 16.4215 | 16.6205 | 16.776 | 17.3175 | 17.8163 | 15.8785 | 16.6811 | 15.9113 | 16.8773 | 17.8731 | 47.0002 | 48.5779 | 45.9798 | 21.4357 |  |  | 0.47467 | 0.16356 | -39.1728 | 0.54405 | -0.09778 | -197.844 | 15.4543 | -0.21787 | -0.047584 | 0.23781 | 0.020776 | 8.8289 | 9.0586 | 1.9777 | 21.8068 | 22.0341 | 22.2251 | 22.3019 | 22.1383 | 21.4736 | 20.3019 | 22.2301 | 22.3911 | 22.4244 | 22.3735 | 22.0111 | 21.266 | 22.2978 | 17.3391 | 17.0065 | 16.1244 | 16.0946 | 16.1875 | 17.0705 | 16.7893 | 22.3982 | 22.1664 | 21.7374 | 22.1013 | 21.82 | 21.3273 | 21.9558 | 21.5492 | 20.9319 | 20.1458 | 20.4574 | 20.0385 | 19.8241 | 0.13252 | -0.22231 | 20.736 | 22.107 | 22.4174 | 20.1422 | 21.7065 | 22.165 | 21.9831 | 21.7487 | 21.3066 | 21.8226 | 21.4857 | 21.0841 | 20.5244 | 20.5633 | 20.4098 | 20.4062 | 20.0009 |  | 20.2665 | 19.7718 | 20.147 | 19.7041 | 20.1167 | 20.3485 |  | 20.4484 |  |  | 20.2721 | 20.4196 | 20.6355 | [5 empty] | 21.9535 | 20.352 | 21.6923 | 22.083 | 19.5645 | 21.2081 | 21.8408 | 19.3836 | 20.015 | 21.2278 |  | 19.8015 | 21.0052 | 18.8509 | 19.7388 | 20.8785 | 19.4062 | 20.2 | 19.0133 | 20.1634 | 19.1358 | 20.3284 | 18.7932 | 20.1781 | 21.1366 | 19.391 | 19.7994 | 21.0274 | 18.9502 | 19.8047 | 20.8399 | 18.9922 | 20.2248 | 19.2287 | 19.9994 | 18.8889 | 20.192 | -0.27634 | 20.9454 | 0.048358 | 0.014375 | -27.0231 | 3.098 | -0.44 | -0.53 | 0.82283 | 0.47984 | -7.4261 | 0.87516 | -0.3714 | -16.7062 | 4.6692 | 0.42764 | 0.43 | 0.43087 | 0.37241 | 0.47456 | 0.43955 | 0.42851
42838.4132 | -610 | 22.8921 | 22.8617 | 22.8488 | 22.7815 | 22.4285 | 21.7721 | 22.7335 | 21.841 | 22.3821 | 22.4023 | 22.3852 | 22.0787 | 21.301 | 22.2604 | 21.5739 | 21.7528 | 21.8924 | 21.0824 | 21.1808 | 21.4076 | 20.4869 | 20.6321 | 20.9335 | 21.906 | 21.6761 | 21.3174 | 20.4525 | 20.5709 | 20.5438 | 22.0355 | 21.6506 | 21.1833 | 22.0024 | 21.7422 | 21.3657 | 19.9447 | 20.4595 |  | 20.5789 | 20.221 | 20.3389 | 19.1839 |  | 16.7164 | 16.7188 | 16.4141 | 16.6181 | 16.7675 | 17.296 | 17.7864 | 15.8859 | 16.6777 | 15.9731 | 16.8713 | 17.8692 | 46.9777 | 48.5036 | 45.9561 | 21.4421 |  |  | 0.40304 | 0.039363 | -39.3627 | 0.29434 | 0.10198 | -197.8223 | 15.3847 | -0.21984 | -0.1297 | 0.047736 | -0.028874 | 8.8282 | 9.0578 | 1.9789 | 21.8079 | 22.045 | 22.237 | 22.2924 | 22.1369 | 21.4779 | 20.2951 | 22.2228 | 22.3942 | 22.4305 | 22.3837 | 22.0232 | 21.2572 | 22.2948 | 17.3092 | 17.0143 | 16.1172 | 16.07 | 16.1647 | 17.0611 | 16.7738 | 22.3988 | 22.1724 | 21.7336 | 22.1 | 21.8257 | 21.3323 | 21.9626 | 21.5536 | 20.9381 | 20.1443 | 20.4585 | 20.044 | 19.8347 | 0.11129 | -0.13958 | 20.7292 | 22.1134 | 22.4215 | 20.1431 | 21.7193 | 22.161 | 21.9887 | 21.7452 | 21.3183 | 21.8238 | 21.485 | 21.0856 | 20.523 | 20.573 | 20.4142 | 20.4095 | 20.0054 |  | 20.2666 | 19.7848 | 20.1539 | 19.7062 | 20.1209 | 20.3577 |  | 20.4537 |  |  | 20.2678 | 20.4272 | 20.6387 | [5 empty] | 21.9541 | 20.3553 | 21.6983 | 22.0878 | 19.5707 | 21.2129 | 21.8426 | 19.3869 | 20.0176 | 21.2363 |  | 19.8062 | 21.0107 | 18.8493 | 19.7464 | 20.8845 | 19.4069 | 20.2051 | 19.0138 | 20.1693 | 19.1348 | 20.3295 | 18.7981 | 20.1883 | 21.1357 | 19.396 | 19.8047 | 21.029 | 18.9563 | 19.8063 | 20.843 | 18.9937 | 20.2239 | 19.225 | 20.0039 | 18.8937 | 20.1955 | -0.013303 | 20.9463 | 0.04759 | 0.015384 | -27.0735 | 3.0979 | -0.41 | -0.13 | 0.75821 | 0.2354 | -7.4441 | 0.64372 | 0.37929 | -16.7046 | 4.6585 | 0.42752 | 0.42987 | 0.43095 | 0.37462 | 0.47356 | 0.43955 | 0.42816
42838.4132 | -609 | 22.8923 | 22.8582 | 22.8468 | 22.7763 | 22.4245 | 21.7714 | 22.723 | 21.8445 | 22.3767 | 22.4024 | 22.3865 | 22.0732 | 21.3006 | 22.2574 | 21.5684 | 21.7528 | 21.8857 | 21.0839 | 21.1699 | 21.4014 | 20.4808 | 20.6263 | 20.9319 | 21.9116 | 21.674 | 21.315 | 20.449 | 20.5747 | 20.5412 | 22.0375 | 21.6488 | 21.1824 | 21.9909 | 21.7376 | 21.3579 | 19.9469 | 20.455 |  | 20.5733 | 20.2163 | 20.3427 | 19.1775 |  | 16.7187 | 16.7197 | 16.4194 | 16.6163 | 16.7635 | 17.2838 | 17.8049 | 15.8991 | 16.6903 | 16.044 | 16.8764 | 17.8707 | 46.9519 | 48.4327 | 45.9349 | 21.4408 |  |  | 0.47335 | -0.25831 | -39.1222 | 0.38437 | 0.21435 | -197.9209 | 15.9051 | -0.29935 | 0.092139 | 0.11886 | 0.1357 | 8.8285 | 9.058 | 1.9787 | 21.8101 | 22.0421 | 22.2352 | 22.2947 | 22.1437 | 21.4801 | 20.2959 | 22.221 | 22.3955 | 22.4314 | 22.3829 | 22.0267 | 21.2635 | 22.2946 | 17.3114 | 17.0536 | 16.1316 | 16.0771 | 16.1483 | 17.0707 | 16.7773 | 22.4058 | 22.1751 | 21.7409 | 22.1018 | 21.8198 | 21.3385 | 21.9608 | 21.5526 | 20.9355 | 20.1377 | 20.4645 | 20.0454 | 19.8293 | 0.0023714 | -0.19968 | 20.7255 | 22.1125 | 22.4141 | 20.1405 | 21.7132 | 22.1584 | 21.9816 | 21.7474 | 21.319 | 21.818 | 21.484 | 21.0798 | 20.52 | 20.5723 | 20.4151 | 20.4032 | 20.0049 |  | 20.2597 | 19.7885 | 20.1482 | 19.715 | 20.1141 | 20.3539 |  | 20.4493 |  |  | 20.2655 | 20.4248 | 20.6404 | [5 empty] | 21.9563 | 20.3551 | 21.6949 | 22.0825 | 19.5679 | 21.209 | 21.8426 | 19.3919 | 20.027 | 21.2394 |  | 19.8072 | 21.0121 | 18.8556 | 19.7482 | 20.8927 | 19.4077 | 20.2109 | 19.0256 | 20.1764 | 19.1413 | 20.3267 | 18.7968 | 20.1904 | 21.1411 | 19.3976 | 19.8074 | 21.0322 | 18.9563 | 19.8073 | 20.8493 | 18.9962 | 20.2291 | 19.2283 | 20.0038 | 18.8982 | 20.1942 | -0.078228 | 20.9463 | 0.046263 | 0.013155 | -26.9034 | 3.0979 | -0.54 | -0.93 | 0.82169 | -0.60303 | -7.4213 | 0.7356 | 0.54986 | -16.7085 | 4.7365 | 0.4273 | 0.42958 | 0.43048 | 0.37551 | 0.47238 | 0.43981 | 0.42809
42838.4132 | -608 | 22.8857 | 22.8556 | 22.8441 | 22.7722 | 22.4203 | 21.7646 | 22.7271 | 21.8371 | 22.3729 | 22.3963 | 22.3766 | 22.0712 | 21.2947 | 22.257 | 21.5706 | 21.7594 | 21.8892 | 21.0865 | 21.1791 | 21.4063 | 20.4837 | 20.6249 | 20.9365 | 21.9113 | 21.6806 | 21.3147 | 20.4538 | 20.5832 | 20.5469 | 22.0348 | 21.6547 | 21.1866 | 21.9945 | 21.7444 | 21.3666 | 19.9507 | 20.4633 |  | 20.5753 | 20.2207 | 20.3428 | 19.1788 |  | 16.7186 | 16.7107 | 16.4141 | 16.6141 | 16.7556 | 17.2655 | 17.7925 | 15.9188 | 16.6873 | 16.0951 | 16.8731 | 17.866 | 46.92 | 48.3665 | 45.9173 | 21.4453 |  |  | 0.3899 | 0.12873 | -38.9881 | 0.29697 | 0.11907 | -197.911 | 15.7093 | -0.33746 | -0.086698 | 0.076688 | 0.058621 | 8.8288 | 9.0583 | 1.978 | 21.8063 | 22.0307 | 22.2291 | 22.3001 | 22.1343 | 21.4739 | 20.2968 | 22.216 | 22.39 | 22.4208 | 22.3763 | 22.0178 | 21.2636 | 22.2902 | 17.3214 | 17.0632 | 16.132 | 16.0845 | 16.1391 | 17.0646 | 16.7801 | 22.3995 | 22.1698 | 21.739 | 22.1003 | 21.82 | 21.3338 | 21.9602 | 21.55 | 20.9347 | 20.1471 | 20.4594 | 20.0445 | 19.8427 | -0.011784 | -0.031162 | 20.7204 | 22.1092 | 22.4089 | 20.1421 | 21.7052 | 22.1532 | 21.9726 | 21.7434 | 21.3086 | 21.8165 | 21.4867 | 21.0806 | 20.5202 | 20.5606 | 20.4154 | 20.4011 | 20.0203 |  | 20.2603 | 19.7983 | 20.1473 | 19.7177 | 20.1172 | 20.354 |  | 20.4503 |  |  | 20.2605 | 20.4211 | 20.6356 | [5 empty] | 21.9643 | 20.361 | 21.6973 | 22.0821 | 19.568 | 21.2058 | 21.8443 | 19.3902 | 20.0218 | 21.2355 |  | 19.8096 | 21.0159 | 18.8555 | 19.7481 | 20.8915 | 19.4162 | 20.2133 | 19.0284 | 20.1743 | 19.1392 | 20.3313 | 18.7927 | 20.1808 | 21.1368 | 19.3947 | 19.8001 | 21.0324 | 18.9523 | 19.808 | 20.8422 | 18.9917 | 20.2318 | 19.2287 | 20.0004 | 18.8967 | 20.1897 | -0.18396 | 20.9455 | 0.046834 | 0.013649 | -26.9995 | 3.0979 | -0.67 | 0.09 | 0.74575 | 0.4257 | -7.4085 | 0.64658 | 0.4098 | -16.7075 | 4.7071 | 0.42689 | 0.42927 | 0.43051 | 0.37368 | 0.47265 | 0.4399 | 0.42803
42838.4133 | -607 | 22.8936 | 22.8624 | 22.8427 | 22.7911 | 22.4212 | 21.7728 | 22.7295 | 21.8459 | 22.3755 | 22.3983 | 22.3828 | 22.065 | 21.2948 | 22.2599 | 21.5762 | 21.7528 | 21.8952 | 21.0815 | 21.1699 | 21.4041 | 20.4829 | 20.6322 | 20.9296 | 21.9071 | 21.6758 | 21.3123 | 20.454 | 20.5734 | 20.5449 | 22.0446 | 21.6641 | 21.1942 | 22.0039 | 21.7476 | 21.3743 | 19.9554 | 20.4718 |  | 20.5839 | 20.2203 | 20.353 | 19.1747 |  | 16.7133 | 16.7082 | 16.4046 | 16.596 | 16.7312 | 17.2492 | 17.7808 | 15.9188 | 16.6852 | 16.1453 | 16.8803 | 17.8632 | 46.8793 | 48.3033 | 45.8983 | 21.4428 |  |  | 0.35639 | -0.38777 | -38.4513 | 0.68073 | 0.27415 | -197.8138 | 15.3702 | -0.20735 | -0.15851 | 0.042071 | -0.045539 | 8.8283 | 9.058 | 1.978 | 21.811 | 22.0321 | 22.2319 | 22.3042 | 22.1431 | 21.4805 | 20.2995 | 22.2187 | 22.392 | 22.4329 | 22.3791 | 22.0174 | 21.265 | 22.2984 | 17.3294 | 17.0896 | 16.1324 | 16.0914 | 16.1491 | 17.0699 | 16.7798 | 22.4032 | 22.1778 | 21.7402 | 22.1057 | 21.8316 | 21.3322 | 21.9713 | 21.5535 | 20.9363 | 20.1515 | 20.476 | 20.0576 | 19.8435 | 0.054274 | 0.019622 | 20.723 | 22.1084 | 22.4101 | 20.1427 | 21.7124 | 22.152 | 21.9745 | 21.7333 | 21.3081 | 21.8087 | 21.4786 | 21.0814 | 20.5156 | 20.5514 | 20.4183 | 20.4025 | 20.0377 |  | 20.261 | 19.8097 | 20.1472 | 19.7219 | 20.1217 | 20.3573 |  | 20.452 |  |  | 20.2493 | 20.4135 | 20.6354 | [5 empty] | 21.9601 | 20.3536 | 21.6969 | 22.08 | 19.5635 | 21.2075 | 21.8416 | 19.381 | 20.0147 | 21.2292 |  | 19.802 | 21.0095 | 18.8524 | 19.7411 | 20.8867 | 19.4085 | 20.21 | 19.0273 | 20.169 | 19.1265 | 20.3297 | 18.7856 | 20.1721 | 21.1321 | 19.3926 | 19.7966 | 21.0235 | 18.9517 | 19.7951 | 20.8395 | 18.9905 | 20.2269 | 19.2199 | 19.9967 | 18.8861 | 20.1878 | -0.058008 | 20.9467 | 0.047787 | 0.013315 | -27.1259 | 3.098 | -0.6 | -0.17 | 0.71298 | -0.73883 | -7.3572 | 0.97892 | 0.62181 | -16.7029 | 4.6559 | 0.42644 | 0.42896 | 0.43054 | 0.37341 | 0.47257 | 0.44017 | 0.42816
42838.4133 | -606 | 22.898 | 22.863 | 22.8462 | 22.792 | 22.4245 | 21.7745 | 22.7284 | 21.8411 | 22.3802 | 22.4043 | 22.3866 | 22.0746 | 21.3021 | 22.2666 | 21.5701 | 21.746 | 21.8875 | 21.0835 | 21.1751 | 21.398 | 20.4809 | 20.634 | 20.9325 | 21.9032 | 21.6761 | 21.3078 | 20.4467 | 20.5689 | 20.5482 | 22.0266 | 21.6487 | 21.1759 | 21.9863 | 21.7313 | 21.3581 | 19.9357 | 20.4661 |  | 20.5648 | 20.2099 | 20.3339 | 19.1444 |  | 16.7075 | 16.6948 | 16.4045 | 16.5972 | 16.7324 | 17.2415 | 17.7817 | 15.9484 | 16.689 | 16.1806 | 16.874 | 17.8638 | 46.8571 | 48.2367 | 45.8625 | 21.4425 |  |  | 0.40633 | -0.23926 | -38.0761 | 0.55982 | 0.15981 | -197.8545 | 15.5286 | -0.23824 | -0.033572 | 0.18725 | 0.11973 | 8.8292 | 9.0588 | 1.9774 | 21.8018 | 22.034 | 22.2256 | 22.2937 | 22.1344 | 21.4746 | 20.2959 | 22.2137 | 22.3877 | 22.427 | 22.3768 | 22.013 | 21.2594 | 22.2935 | 17.3362 | 17.1008 | 16.1261 | 16.0915 | 16.1507 | 17.0673 | 16.778 | 22.3963 | 22.1774 | 21.7365 | 22.1045 | 21.8278 | 21.332 | 21.9613 | 21.5642 | 20.9404 | 20.147 | 20.4743 | 20.0678 | 19.8376 | -0.08315 | 0.023996 | 20.7342 | 22.1114 | 22.4084 | 20.1349 | 21.7099 | 22.1538 | 21.9704 | 21.7332 | 21.3077 | 21.8059 | 21.4803 | 21.0812 | 20.5123 | 20.558 | 20.4148 | 20.4044 | 20.0516 |  | 20.267 | 19.8242 | 20.1428 | 19.7222 | 20.1198 | 20.3547 |  | 20.4472 |  |  | 20.2528 | 20.4102 | 20.643 | [5 empty] | 21.9603 | 20.359 | 21.7011 | 22.0926 | 19.5711 | 21.2119 | 21.8515 | 19.3851 | 20.0284 | 21.2363 |  | 19.8064 | 21.0172 | 18.855 | 19.7471 | 20.8878 | 19.4202 | 20.2192 | 19.0395 | 20.1828 | 19.1399 | 20.3301 | 18.7822 | 20.1754 | 21.1323 | 19.3897 | 19.8047 | 21.0298 | 18.9501 | 19.798 | 20.8343 | 18.9927 | 20.2333 | 19.2262 | 19.9995 | 18.8896 | 20.19 | -0.17487 | 20.9451 | 0.048192 | 0.013308 | -27.1109 | 3.098 | -0.71 | -0.13 | 0.7613 | -0.58034 | -7.3211 | 0.88771 | 0.47475 | -16.7044 | 4.6798 | 0.42625 | 0.4284 | 0.43047 | 0.37236 | 0.47307 | 0.44035 | 0.42817
42838.4133 | -605 | 22.894 | 22.8624 | 22.8451 | 22.7822 | 22.4269 | 21.7745 | 22.7286 | 21.8406 | 22.3811 | 22.3957 | 22.3833 | 22.0717 | 21.2952 | 22.2572 | 21.5755 | 21.7622 | 21.905 | 21.0873 | 21.1961 | 21.4136 | 20.4955 | 20.6468 | 20.9411 | 21.9166 | 21.6846 | 21.3283 | 20.465 | 20.5805 | 20.5557 | 22.0289 | 21.6623 | 21.1918 | 21.9942 | 21.7429 | 21.3634 | 19.9467 | 20.4753 |  | 20.573 | 20.221 | 20.3459 | 19.1403 |  | 16.702 | 16.7072 | 16.4099 | 16.5976 | 16.7246 | 17.225 | 17.7519 | 15.9588 | 16.6881 | 16.2046 | 16.8846 | 17.8609 | 46.8478 | 48.1649 | 45.8272 | 21.4479 |  |  | 0.21839 | -0.36279 | -37.8224 | 0.51579 | 0.16244 | -197.8644 | 15.8052 | -0.26781 | -0.26612 | -0.039331 | -0.027832 | 8.8288 | 9.0585 | 1.9786 | 21.7997 | 22.0345 | 22.2327 | 22.2935 | 22.1334 | 21.4757 | 20.3025 | 22.2183 | 22.3876 | 22.4245 | 22.3735 | 22.015 | 21.2644 | 22.2906 | 17.3317 | 17.1249 | 16.1207 | 16.0965 | 16.1476 | 17.0729 | 16.7853 | 22.3991 | 22.1746 | 21.7405 | 22.1065 | 21.8306 | 21.3414 | 21.9611 | 21.553 | 20.9471 | 20.1468 | 20.4701 | 20.0655 | 19.8423 | -0.036555 | -0.031732 | 20.7409 | 22.1093 | 22.4169 | 20.1391 | 21.7117 | 22.1556 | 21.9764 | 21.7449 | 21.3121 | 21.8194 | 21.488 | 21.0825 | 20.5163 | 20.557 | 20.4183 | 20.4132 | 20.0704 |  | 20.2658 | 19.8359 | 20.1396 | 19.7183 | 20.1085 | 20.3504 |  | 20.446 |  |  | 20.2577 | 20.4097 | 20.6479 | [5 empty] | 21.969 | 20.3622 | 21.7012 | 22.0861 | 19.5711 | 21.2117 | 21.8465 | 19.3802 | 20.0113 | 21.2306 |  | 19.808 | 21.0072 | 18.8565 | 19.7392 | 20.8882 | 19.4121 | 20.2103 | 19.0277 | 20.1662 | 19.1399 | 20.3328 | 18.7752 | 20.1741 | 21.137 | 19.3897 | 19.8021 | 21.0196 | 18.9562 | 19.8002 | 20.8463 | 18.9966 | 20.2244 | 19.2256 | 20.0059 | 18.8936 | 20.1944 | -0.092883 | 20.9472 | 0.048223 | 0.014106 | -26.9802 | 3.098 | -0.75 | -0.43 | 0.55814 | -0.71464 | -7.2968 | 0.85211 | 0.47862 | -16.7044 | 4.7211 | 0.42569 | 0.42797 | 0.4302 | 0.37351 | 0.47452 | 0.44084 | 0.42804
42838.4133 | -604 | 22.8937 | 22.8617 | 22.8427 | 22.7795 | 22.4233 | 21.7738 | 22.7276 | 21.8362 | 22.3774 | 22.3976 | 22.385 | 22.0673 | 21.2947 | 22.2536 | 21.5781 | 21.7601 | 21.898 | 21.0811 | 21.1799 | 21.4133 | 20.4832 | 20.6317 | 20.9297 | 21.9172 | 21.6778 | 21.3142 | 20.4596 | 20.5742 | 20.5434 | 22.03 | 21.651 | 21.1809 | 21.9946 | 21.7395 | 21.3593 | 19.9465 | 20.4709 |  | 20.5765 | 20.2195 | 20.34 | 19.1196 |  | 16.7041 | 16.7197 | 16.4231 | 16.5991 | 16.7221 | 17.2171 | 17.7168 | 15.977 | 16.6894 | 16.2193 | 16.89 | 17.8653 | 46.8399 | 48.0971 | 45.7986 | 21.4516 |  |  | 0.43853 | -0.19786 | -37.9887 | 0.51842 | 0.086212 | -197.8296 | 15.8302 | -0.21195 | -0.26495 | -0.017932 | -0.0031808 | 8.8297 | 9.0594 | 1.9783 | 21.8049 | 22.0404 | 22.2306 | 22.2925 | 22.1383 | 21.4814 | 20.2994 | 22.2149 | 22.3926 | 22.4284 | 22.3794 | 22.0246 | 21.265 | 22.2921 | 17.3354 | 17.1234 | 16.1287 | 16.1064 | 16.152 | 17.0695 | 16.7797 | 22.3976 | 22.1684 | 21.7306 | 22.0955 | 21.8249 | 21.3348 | 21.9608 | 21.5497 | 20.9274 | 20.1478 | 20.4648 | 20.0595 | 19.8446 | -0.0015606 | -0.088792 | 20.7502 | 22.1079 | 22.414 | 20.1359 | 21.7034 | 22.1529 | 21.9761 | 21.7458 | 21.3149 | 21.8138 | 21.4845 | 21.0827 | 20.5176 | 20.5597 | 20.4163 | 20.4113 | 20.076 |  | 20.2629 | 19.8538 | 20.144 | 19.734 | 20.112 | 20.35 |  | 20.4496 |  |  | 20.2645 | 20.409 | 20.6495 | [5 empty] | 21.953 | 20.3581 | 21.6965 | 22.0882 | 19.5673 | 21.2093 | 21.8447 | 19.3781 | 20.0198 | 21.2334 |  | 19.8025 | 21.0163 | 18.849 | 19.7526 | 20.8857 | 19.4247 | 20.2124 | 19.0358 | 20.1774 | 19.1394 | 20.3391 | 18.7664 | 20.17 | 21.1292 | 19.3872 | 19.7905 | 21.0086 | 18.952 | 19.8004 | 20.8309 | 18.9962 | 20.2295 | 19.2159 | 19.9978 | 18.8802 | 20.1831 | -0.20919 | 20.9451 | 0.048659 | 0.01431 | -27.008 | 3.098 | -0.48 | 0.82 | 0.79088 | -0.52777 | -7.313 | 0.8543 | 0.34868 | -16.7027 | 4.7248 | 0.42543 | 0.42762 | 0.42988 | 0.3727 | 0.47296 | 0.4414 | 0.42801
42838.4133 | -603 | 22.8889 | 22.8575 | 22.8411 | 22.7716 | 22.4194 | 21.765 | 22.7266 | 21.8282 | 22.365 | 22.396 | 22.3779 | 22.0642 | 21.2969 | 22.2558 | 21.5817 | 21.7552 | 21.8936 | 21.0803 | 21.1786 | 21.402 | 20.4908 | 20.6397 | 20.9309 | 21.9081 | 21.6825 | 21.3145 | 20.4563 | 20.5721 | 20.5491 | 22.0215 | 21.6421 | 21.1795 | 21.993 | 21.7357 | 21.3531 | 19.94 | 20.4711 |  | 20.5705 | 20.2078 | 20.3312 | 19.1122 |  | 16.702 | 16.7117 | 16.4231 | 16.6002 | 16.7191 | 17.1978 | 17.6891 | 15.9898 | 16.6834 | 16.1998 | 16.8876 | 17.8629 | 46.8303 | 48.0297 | 45.751 | 21.4398 |  |  | 0.34456 | -0.15712 | -38.5452 | 0.62487 | 0.1815 | -197.844 | 15.6817 | -0.3414 | -0.28033 | 0.0007406 | 0.011749 | 8.8296 | 9.0594 | 1.9783 | 21.8152 | 22.0457 | 22.2338 | 22.3046 | 22.137 | 21.4694 | 20.2976 | 22.2239 | 22.3952 | 22.4296 | 22.3845 | 22.0185 | 21.2546 | 22.2954 | 17.3452 | 17.0828 | 16.1366 | 16.1402 | 16.1556 | 17.069 | 16.779 | 22.3988 | 22.1717 | 21.7315 | 22.098 | 21.8228 | 21.331 | 21.965 | 21.554 | 20.9285 | 20.1444 | 20.4691 | 20.0621 | 19.8446 | 0.13645 | -0.074337 | 20.7531 | 22.1003 | 22.4136 | 20.1378 | 21.7056 | 22.1642 | 21.9794 | 21.7447 | 21.3155 | 21.8149 | 21.4878 | 21.0841 | 20.5228 | 20.5586 | 20.4159 | 20.4149 | 20.0901 |  | 20.266 | 19.8636 | 20.1488 | 19.7293 | 20.1157 | 20.3612 |  | 20.4514 |  |  | 20.2696 | 20.404 | 20.6512 | [5 empty] | 21.9631 | 20.3731 | 21.6974 | 22.0862 | 19.5747 | 21.2127 | 21.8455 | 19.3838 | 20.02 | 21.2326 |  | 19.8166 | 21.0234 | 18.8563 | 19.75 | 20.895 | 19.4231 | 20.2266 | 19.0403 | 20.1829 | 19.1454 | 20.3402 | 18.7838 | 20.1835 | 21.1409 | 19.3954 | 19.8177 | 21.0289 | 18.9581 | 19.8129 | 20.8559 | 19.0095 | 20.2393 | 19.2401 | 20.0064 | 18.9069 | 20.1967 | -0.11922 | 20.9469 | 0.048886 | 0.013061 | -27.0608 | 3.0979 | -0.57 | -0.2 | 0.70105 | -0.4703 | -7.3663 | 0.9379 | 0.50589 | -16.7027 | 4.7024 | 0.42515 | 0.42751 | 0.43013 | 0.37154 | 0.47201 | 0.44139 | 0.42789
42838.4133 | -602 | 22.892 | 22.8573 | 22.8387 | 22.7745 | 22.4242 | 21.7694 | 22.7251 | 21.8308 | 22.371 | 22.3968 | 22.3705 | 22.0693 | 21.2944 | 22.2603 | 21.576 | 21.7493 | 21.8907 | 21.0834 | 21.179 | 21.4062 | 20.4847 | 20.6373 | 20.9306 | 21.91 | 21.6805 | 21.3121 | 20.4591 | 20.5769 | 20.5396 | 22.0232 | 21.657 | 21.1854 | 21.9968 | 21.7366 | 21.3569 | 19.9491 | 20.4889 |  | 20.5771 | 20.2121 | 20.3369 | 19.1232 |  | 16.7045 | 16.7191 | 16.4157 | 16.59 | 16.7084 | 17.1722 | 17.6824 | 15.9931 | 16.6894 | 16.1725 | 16.8922 | 17.8653 | 46.8233 | 47.9737 | 45.7158 | 21.4469 |  |  | 0.4865 | -0.11966 | -38.0649 | 0.51711 | -0.035352 | -197.819 | 15.8315 | -0.48597 | -0.47395 | 0.11886 | -0.094668 | 8.8291 | 9.0588 | 1.9785 | 21.8126 | 22.0361 | 22.2373 | 22.2939 | 22.1327 | 21.4756 | 20.3003 | 22.2231 | 22.3855 | 22.4313 | 22.3775 | 22.0218 | 21.2697 | 22.2945 | 17.3618 | 17.055 | 16.1478 | 16.1621 | 16.179 | 17.0689 | 16.7799 | 22.4066 | 22.1806 | 21.7377 | 22.1084 | 21.8219 | 21.3303 | 21.9674 | 21.5598 | 20.9366 | 20.1506 | 20.4708 | 20.0686 | 19.8549 | -0.0047062 | 0.0015526 | 20.7544 | 22.1024 | 22.4118 | 20.1309 | 21.7096 | 22.1617 | 21.9773 | 21.745 | 21.3123 | 21.8166 | 21.4834 | 21.0855 | 20.518 | 20.5575 | 20.4165 | 20.4152 | 20.0881 |  | 20.261 | 19.8931 | 20.1453 | 19.7232 | 20.1172 | 20.3508 |  | 20.4492 |  |  | 20.2529 | 20.4024 | 20.6521 | [5 empty] | 21.9643 | 20.3707 | 21.6978 | 22.0861 | 19.5784 | 21.2151 | 21.8506 | 19.3729 | 20.0011 | 21.22 |  | 19.8016 | 21.0088 | 18.8405 | 19.7337 | 20.8865 | 19.4136 | 20.2164 | 19.0289 | 20.1714 | 19.1385 | 20.3235 | 18.7665 | 20.1795 | 21.1339 | 19.382 | 19.7936 | 21.0168 | 18.9504 | 19.805 | 20.8381 | 18.9915 | 20.2273 | 19.2278 | 19.9928 | 18.8867 | 20.1774 | -0.15966 | 20.948 | 0.047707 | 0.01248 | -26.9019 | 3.098 | -0.83 | 0.57 | 0.83301 | -0.41043 | -7.3203 | 0.85321 | -0.22326 | -16.7009 | 4.7246 | 0.42503 | 0.42658 | 0.43035 | 0.36969 | 0.47087 | 0.44139 | 0.42781
42838.4133 | -601 | 22.8944 | 22.8519 | 22.8456 | 22.768 | 22.4208 | 21.7656 | 22.7223 | 21.8294 | 22.3712 | 22.3885 | 22.3777 | 22.0667 | 21.2952 | 22.2636 | 21.5736 | 21.7469 | 21.8838 | 21.0777 | 21.1688 | 21.3976 | 20.483 | 20.6272 | 20.9231 | 21.9041 | 21.6688 | 21.3073 | 20.4508 | 20.5664 | 20.5392 | 22.0212 | 21.6549 | 21.1835 | 21.9939 | 21.738 | 21.3652 | 19.9403 | 20.4879 |  | 20.5781 | 20.2164 | 20.3377 | 19.1291 |  | 16.7075 | 16.7181 | 16.4209 | 16.5905 | 16.6971 | 17.1689 | 17.6822 | 15.9548 | 16.6878 | 16.1477 | 16.8867 | 17.8656 | 46.7864 | 47.9141 | 45.6767 | 21.4427 |  |  | 0.46481 | -0.051321 | -37.8993 | 0.56442 | 0.11184 | -197.846 | 15.6652 | -0.32629 | -0.062957 | -0.079403 | -0.11585 | 8.8291 | 9.0589 | 1.9778 | 21.8026 | 22.0258 | 22.2255 | 22.287 | 22.1285 | 21.4642 | 20.2901 | 22.2116 | 22.3757 | 22.4164 | 22.3768 | 22.0094 | 21.2586 | 22.2846 | 17.3748 | 17.0296 | 16.1592 | 16.1631 | 16.1908 | 17.0635 | 16.773 | 22.4097 | 22.1755 | 21.7472 | 22.107 | 21.8321 | 21.3322 | 21.9661 | 21.554 | 20.9395 | 20.1534 | 20.485 | 20.0722 | 19.8588 | 0.038742 | -0.022983 | 20.7546 | 22.1044 | 22.4087 | 20.1359 | 21.7105 | 22.1566 | 21.9701 | 21.7445 | 21.3123 | 21.8151 | 21.4816 | 21.0841 | 20.5107 | 20.5588 | 20.4182 | 20.4161 | 20.0893 |  | 20.2641 | 19.9037 | 20.1444 | 19.7122 | 20.1143 | 20.3592 |  | 20.4486 |  |  | 20.2411 | 20.4 | 20.6566 | [5 empty] | 21.9654 | 20.3656 | 21.7075 | 22.0956 | 19.5809 | 21.2155 | 21.8424 | 19.3722 | 20.0027 | 21.2278 |  | 19.806 | 21.0018 | 18.857 | 19.744 | 20.8853 | 19.4293 | 20.2247 | 19.0409 | 20.1781 | 19.1367 | 20.3214 | 18.7713 | 20.1813 | 21.1395 | 19.3839 | 19.809 | 21.0312 | 18.9526 | 19.8119 | 20.8421 | 19.0073 | 20.2391 | 19.2355 | 20.0078 | 18.8907 | 20.1885 | -0.22923 | 20.948 | 0.046932 | 0.012705 | -27.048 | 3.098 | -0.8 | -0.12 | 0.81423 | -0.26879 | -7.3044 | 0.89139 | 0.3971 | -16.702 | 4.6997 | 0.42511 | 0.42625 | 0.43056 | 0.36763 | 0.4688 | 0.44093 | 0.4278
42838.4133 | -600 | 22.8901 | 22.8592 | 22.8471 | 22.7733 | 22.4249 | 21.7751 | 22.7245 | 21.8394 | 22.3812 | 22.3894 | 22.3801 | 22.0654 | 21.3004 | 22.2615 | 21.5613 | 21.7438 | 21.8798 | 21.0729 | 21.1708 | 21.394 | 20.4795 | 20.6247 | 20.9218 | 21.8978 | 21.669 | 21.3048 | 20.4414 | 20.57 | 20.5354 | 22.0197 | 21.6471 | 21.1791 | 21.9952 | 21.7308 | 21.3671 | 19.9393 | 20.4961 |  | 20.5745 | 20.214 | 20.3402 | 19.1125 |  | 16.7107 | 16.7181 | 16.4211 | 16.5869 | 16.7002 | 17.1493 | 17.7011 | 15.8674 | 16.6853 | 16.0918 | 16.8872 | 17.8676 | 46.7357 | 47.8601 | 45.6472 | 21.4443 |  |  | 0.48058 | -0.15843 | -37.2363 | 0.42643 | 0.1401 | -197.892 | 15.7848 | -0.34995 | -0.093704 | -0.000728 | -0.035297 | 8.8284 | 9.0581 | 1.9781 | 21.8082 | 22.0289 | 22.2206 | 22.2915 | 22.1306 | 21.4709 | 20.2911 | 22.2121 | 22.3843 | 22.418 | 22.3737 | 22.013 | 21.2563 | 22.2883 | 17.4037 | 17.089 | 16.1632 | 16.1714 | 16.2166 | 17.0706 | 16.7808 | 22.4001 | 22.1789 | 21.7449 | 22.1002 | 21.8305 | 21.3357 | 21.9687 | 21.5576 | 20.9365 | 20.1583 | 20.4829 | 20.0765 | 19.85 | 0.10087 | -0.16468 | 20.7509 | 22.1045 | 22.4108 | 20.1307 | 21.7042 | 22.1546 | 21.9699 | 21.735 | 21.3133 | 21.8101 | 21.4785 | 21.0838 | 20.5115 | 20.55 | 20.4182 | 20.4146 | 20.0972 |  | 20.255 | 19.914 | 20.1349 | 19.7169 | 20.1077 | 20.3519 |  | 20.4421 |  |  | 20.2385 | 20.4069 | 20.659 | [5 empty] | 21.9601 | 20.3613 | 21.6983 | 22.0918 | 19.5818 | 21.2141 | 21.8426 | 19.3771 | 20.0001 | 21.2245 |  | 19.8083 | 21.0048 | 18.8531 | 19.7414 | 20.8824 | 19.4192 | 20.2287 | 19.0369 | 20.1748 | 19.1375 | 20.3283 | 18.7679 | 20.1787 | 21.1273 | 19.3775 | 19.7953 | 21.0279 | 18.9383 | 19.8037 | 20.8403 | 19.0018 | 20.2339 | 19.2297 | 20.0055 | 18.8831 | 20.1843 | 0.005618 | 20.9476 | 0.048837 | 0.012713 | -26.9262 | 3.098 | -0.72 | 0.23 | 0.82793 | -0.47226 | -7.2402 | 0.7748 | 0.44443 | -16.7034 | 4.7175 | 0.42458 | 0.42564 | 0.43021 | 0.36524 | 0.46926 | 0.44136 | 0.42821
42838.4133 | -599 | 22.8967 | 22.8568 | 22.8431 | 22.7803 | 22.4181 | 21.7642 | 22.7268 | 21.8427 | 22.378 | 22.3885 | 22.3769 | 22.069 | 21.2918 | 22.2559 | 21.5671 | 21.7486 | 21.8802 | 21.0772 | 21.1706 | 21.3966 | 20.4807 | 20.6304 | 20.9297 | 21.9049 | 21.6706 | 21.3084 | 20.4499 | 20.5718 | 20.5389 | 22.0362 | 21.6575 | 21.182 | 21.9986 | 21.738 | 21.3641 | 19.942 | 20.4976 |  | 20.5643 | 20.2213 | 20.3295 | 19.0917 |  | 16.7112 | 16.7205 | 16.42 | 16.5867 | 16.6999 | 17.1572 | 17.731 | 15.7728 | 16.6902 | 16.0573 | 16.8827 | 17.8633 | 46.6617 | 47.8141 | 45.6093 | 21.4442 |  |  | 0.65603 | 0.005847 | -36.8433 | 0.55982 | 0.11316 | -197.7816 | 15.7204 | -0.29869 | -0.027151 | -0.1264 | -0.090154 | 8.829 | 9.0585 | 1.9787 | 21.8048 | 22.0239 | 22.217 | 22.2892 | 22.128 | 21.4611 | 20.2918 | 22.2079 | 22.3843 | 22.4175 | 22.3679 | 22.0116 | 21.2506 | 22.2873 | 17.4308 | 17.1332 | 16.1675 | 16.1718 | 16.2245 | 17.0634 | 16.7679 | 22.404 | 22.1834 | 21.7399 | 22.1068 | 21.8266 | 21.3334 | 21.9682 | 21.5589 | 20.9367 | 20.1508 | 20.4795 | 20.0769 | 19.8422 | 0.11954 | 0.049673 | 20.7521 | 22.1055 | 22.4157 | 20.1306 | 21.7076 | 22.1533 | 21.975 | 21.7361 | 21.3108 | 21.8158 | 21.4831 | 21.0818 | 20.5081 | 20.5506 | 20.4224 | 20.4139 | 20.1079 |  | 20.2658 | 19.9301 | 20.1431 | 19.7059 | 20.1087 | 20.3584 |  | 20.4458 |  |  | 20.236 | 20.3997 | 20.6539 | [5 empty] | 21.9617 | 20.3612 | 21.6944 | 22.084 | 19.581 | 21.2109 | 21.8408 | 19.3804 | 20.0048 | 21.2271 |  | 19.817 | 21.0095 | 18.8573 | 19.7358 | 20.8855 | 19.4244 | 20.2189 | 19.0403 | 20.1784 | 19.1375 | 20.3264 | 18.7705 | 20.1817 | 21.1274 | 19.3751 | 19.7933 | 21.0277 | 18.9328 | 19.7981 | 20.8376 | 18.999 | 20.2338 | 19.2345 | 19.9981 | 18.8842 | 20.1845 | -0.28079 | 20.9479 | 0.048026 | 0.014295 | -27.0793 | 3.098 | -0.67 | 0.45 | 0.96733 | 0.090727 | -7.2019 | 0.88775 | 0.39942 | -16.6989 | 4.7079 | 0.42465 | 0.42547 | 0.43055 | 0.36139 | 0.46728 | 0.44203 | 0.42817
42838.4134 | -598 | 22.8751 | 22.8511 | 22.8428 | 22.7752 | 22.4122 | 21.7595 | 22.7177 | 21.8402 | 22.3751 | 22.3872 | 22.3747 | 22.059 | 21.2899 | 22.2505 | 21.5696 | 21.7473 | 21.881 | 21.078 | 21.1752 | 21.3954 | 20.4818 | 20.6284 | 20.9263 | 21.9071 | 21.6665 | 21.3058 | 20.4497 | 20.5711 | 20.5401 | 22.0305 | 21.6508 | 21.1783 | 22.0023 | 21.7367 | 21.3607 | 19.9434 | 20.4938 |  | 20.5684 | 20.2252 | 20.3412 | 19.0841 |  | 16.7107 | 16.7245 | 16.4212 | 16.5825 | 16.6953 | 17.1426 | 17.7084 | 15.7322 | 16.6968 | 16.0442 | 16.8834 | 17.8653 | 46.599 | 47.765 | 45.567 | 21.4461 |  |  | 0.45758 | -0.098633 | -36.1336 | 0.68664 | 0.12893 | -197.8098 | 15.9531 | -0.21852 | 0.14663 | 0.21285 | 0.00602 | 8.8281 | 9.0574 | 1.9788 | 21.8006 | 22.0353 | 22.2243 | 22.2892 | 22.1297 | 21.4676 | 20.3007 | 22.2097 | 22.3911 | 22.415 | 22.3791 | 22.0138 | 21.2502 | 22.2907 | 17.4512 | 17.1592 | 16.1776 | 16.1965 | 16.2302 | 17.0697 | 16.7733 | 22.4023 | 22.1784 | 21.7348 | 22.1026 | 21.8292 | 21.3324 | 21.964 | 21.5549 | 20.9382 | 20.1559 | 20.4829 | 20.0787 | 19.8416 | 0.073541 | 0.030843 | 20.7586 | 22.1028 | 22.4135 | 20.1316 | 21.7119 | 22.1529 | 21.9719 | 21.7407 | 21.3065 | 21.818 | 21.4792 | 21.082 | 20.5108 | 20.5569 | 20.423 | 20.4146 | 20.1159 |  | 20.2682 | 19.9459 | 20.1454 | 19.702 | 20.1113 | 20.3686 |  | 20.4488 |  |  | 20.2413 | 20.4008 | 20.6535 | [5 empty] | 21.9634 | 20.3676 | 21.6989 | 22.0899 | 19.5837 | 21.2162 | 21.8411 | 19.3778 | 19.9971 | 21.2249 |  | 19.8184 | 21.0069 | 18.8567 | 19.7367 | 20.8836 | 19.4255 | 20.2189 | 19.0408 | 20.1827 | 19.1343 | 20.3222 | 18.7766 | 20.1748 | 21.1262 | 19.3676 | 19.7974 | 21.0254 | 18.9298 | 19.7948 | 20.8356 | 19.0054 | 20.2384 | 19.2369 | 19.9911 | 18.8854 | 20.1822 | -0.065985 | 20.9466 | 0.048352 | 0.014607 | -27.0375 | 3.098 | -0.76 | -0.12 | 0.80788 | -0.37263 | -7.1323 | 0.98319 | 0.42634 | -16.6997 | 4.7425 | 0.4245 | 0.42511 | 0.43074 | 0.35986 | 0.4668 | 0.44229 | 0.42836
42838.4134 | -597 | 22.8938 | 22.8576 | 22.8499 | 22.7874 | 22.4264 | 21.774 | 22.7301 | 21.845 | 22.3833 | 22.397 | 22.389 | 22.0683 | 21.2978 | 22.2592 | 21.5756 | 21.7553 | 21.8929 | 21.0839 | 21.1819 | 21.4018 | 20.4854 | 20.6293 | 20.9364 | 21.9118 | 21.6785 | 21.3117 | 20.4528 | 20.5726 | 20.5438 | 22.0307 | 21.6477 | 21.1845 | 22.0006 | 21.7355 | 21.3589 | 19.9399 | 20.5022 |  | 20.568 | 20.2204 | 20.3419 | 19.0807 |  | 16.7214 | 16.7191 | 16.4248 | 16.5924 | 16.6985 | 17.1269 | 17.6797 | 15.6952 | 16.6969 | 16.0777 | 16.8912 | 17.8621 | 46.5437 | 47.719 | 45.5202 | 21.4427 |  |  | 0.59821 | -0.005981 | -35.6119 | 0.76747 | 0.14141 | -197.865 | 16.3125 | -0.24875 | -0.041746 | 0.0040974 | 0.015047 | 8.8292 | 9.0587 | 1.978 | 21.8004 | 22.0371 | 22.2359 | 22.2986 | 22.1379 | 21.4742 | 20.2965 | 22.2196 | 22.3909 | 22.4253 | 22.3843 | 22.0161 | 21.2611 | 22.2924 | 17.4527 | 17.1651 | 16.1887 | 16.2215 | 16.23 | 17.0675 | 16.7739 | 22.3938 | 22.1728 | 21.7294 | 22.0975 | 21.8214 | 21.3257 | 21.959 | 21.5484 | 20.9399 | 20.1528 | 20.473 | 20.0675 | 19.8289 | 0.18953 | 0.024567 | 20.7536 | 22.102 | 22.4047 | 20.125 | 21.7015 | 22.1466 | 21.9657 | 21.732 | 21.2975 | 21.8091 | 21.4735 | 21.073 | 20.5072 | 20.5454 | 20.4127 | 20.4089 | 20.1086 |  | 20.2539 | 19.9497 | 20.1319 | 19.6877 | 20.1037 | 20.3576 |  | 20.4403 |  |  | 20.2441 | 20.3992 | 20.6549 | [5 empty] | 21.9613 | 20.3674 | 21.6982 | 22.0859 | 19.5811 | 21.2098 | 21.8463 | 19.3673 | 19.9881 | 21.2187 |  | 19.8081 | 21.0006 | 18.8516 | 19.7334 | 20.879 | 19.4152 | 20.2197 | 19.0357 | 20.1775 | 19.1319 | 20.3188 | 18.7823 | 20.1756 | 21.1289 | 19.372 | 19.8052 | 21.0296 | 18.9292 | 19.7992 | 20.8327 | 19.0141 | 20.2352 | 19.2374 | 19.9995 | 18.8886 | 20.1887 | -0.27467 | 20.9445 | 0.048462 | 0.015232 | -27.0889 | 3.098 | -0.9 | -0.01 | 0.92372 | -0.09176 | -7.0805 | 1.0394 | 0.44649 | -16.7016 | 4.7955 | 0.42423 | 0.42456 | 0.43089 | 0.35943 | 0.46562 | 0.44226 | 0.42861
42838.4134 | -596 | 22.8915 | 22.8634 | 22.8443 | 22.7863 | 22.4251 | 21.7729 | 22.7267 | 21.8387 | 22.3823 | 22.3948 | 22.3853 | 22.0593 | 21.294 | 22.2603 | 21.5774 | 21.7573 | 21.8923 | 21.0845 | 21.1844 | 21.4063 | 20.4819 | 20.6293 | 20.9421 | 21.9095 | 21.6816 | 21.3116 | 20.4574 | 20.5707 | 20.5412 | 22.0237 | 21.6487 | 21.1821 | 21.9973 | 21.7375 | 21.3602 | 19.9433 | 20.5036 |  | 20.57 | 20.2162 | 20.3369 | 19.0677 |  | 16.7152 | 16.7226 | 16.4279 | 16.5896 | 16.6933 | 17.1253 | 17.6498 | 15.7022 | 16.7026 | 16.0722 | 16.8915 | 17.8679 | 46.4842 | 47.6816 | 45.4751 | 21.4458 |  |  | 0.60806 | -0.11441 | -35.1992 | 0.39751 | 0.11316 | -197.8388 | 16.603 | -0.073956 | 0.042127 | -0.012477 | -0.029568 | 8.8282 | 9.0579 | 1.9781 | 21.806 | 22.0277 | 22.2221 | 22.2932 | 22.1246 | 21.4609 | 20.2839 | 22.2138 | 22.3885 | 22.4108 | 22.3774 | 22.011 | 21.2533 | 22.2919 | 17.4634 | 17.1585 | 16.1942 | 16.2394 | 16.2639 | 17.0742 | 16.7793 | 22.3955 | 22.1602 | 21.7302 | 22.0972 | 21.8177 | 21.3231 | 21.9565 | 21.5419 | 20.9309 | 20.1446 | 20.4769 | 20.0571 | 19.8278 | -0.054643 | 0.071736 | 20.7606 | 22.0968 | 22.4023 | 20.1183 | 21.6989 | 22.1408 | 21.9662 | 21.7319 | 21.296 | 21.8038 | 21.4757 | 21.0761 | 20.5053 | 20.5431 | 20.4077 | 20.411 | 20.1217 |  | 20.2655 | 19.9635 | 20.141 | 19.6953 | 20.1187 | 20.3744 |  | 20.45 |  |  | 20.253 | 20.3886 | 20.6586 | [5 empty] | 21.9587 | 20.3691 | 21.701 | 22.0815 | 19.5763 | 21.204 | 21.8462 | 19.3754 | 19.9947 | 21.2257 |  | 19.8151 | 21.001 | 18.8509 | 19.7398 | 20.8897 | 19.4222 | 20.2213 | 19.0412 | 20.1835 | 19.1416 | 20.322 | 18.7886 | 20.1758 | 21.1328 | 19.3767 | 19.8064 | 21.0313 | 18.9279 | 19.8015 | 20.8378 | 19.0179 | 20.2379 | 19.2397 | 19.9985 | 18.8891 | 20.1882 | -0.059864 | 20.9476 | 0.0492 | 0.015297 | -26.9638 | 3.098 | -0.72 | -0.12 | 0.93129 | -0.40132 | -7.0394 | 0.74807 | 0.3994 | -16.7004 | 4.838 | 0.42425 | 0.42447 | 0.43118 | 0.35903 | 0.46565 | 0.44274 | 0.42836
42838.4134 | -595 | 22.8915 | 22.8565 | 22.849 | 22.7778 | 22.4237 | 21.7725 | 22.7245 | 21.8348 | 22.3789 | 22.3954 | 22.3818 | 22.0649 | 21.2932 | 22.2651 | 21.5698 | 21.7505 | 21.8862 | 21.0833 | 21.1799 | 21.4073 | 20.4886 | 20.6306 | 20.9344 | 21.9047 | 21.6731 | 21.3093 | 20.4541 | 20.5676 | 20.5425 | 22.024 | 21.6441 | 21.1812 | 21.9923 | 21.7354 | 21.3621 | 19.9418 | 20.5046 |  | 20.5721 | 20.2201 | 20.3356 | 19.0692 |  | 16.7184 | 16.7189 | 16.4173 | 16.585 | 16.6861 | 17.1152 | 17.6298 | 15.6532 | 16.6938 | 16.0605 | 16.8894 | 17.8609 | 46.4142 | 47.6354 | 45.4195 | 21.4392 |  |  | 0.46875 | -0.076949 | -35.1348 | 0.69519 | -0.003156 | -197.8322 | 16.6693 | -0.1423 | -0.28733 | -0.16311 | 0.02772 | 8.8287 | 9.0584 | 1.9779 | 21.8063 | 22.029 | 22.2383 | 22.297 | 22.1367 | 21.474 | 20.297 | 22.2208 | 22.3933 | 22.4325 | 22.3713 | 22.0205 | 21.2607 | 22.2921 | 17.4531 | 17.1609 | 16.2008 | 16.2397 | 16.2807 | 17.0728 | 16.7766 | 22.3956 | 22.1737 | 21.7353 | 22.0962 | 21.816 | 21.3298 | 21.9642 | 21.5488 | 20.9344 | 20.1477 | 20.4799 | 20.0724 | 19.8253 | 0.1048 | -0.19283 | 20.7689 | 22.0991 | 22.4073 | 20.124 | 21.7052 | 22.1441 | 21.9637 | 21.7355 | 21.2969 | 21.8065 | 21.4731 | 21.0767 | 20.5103 | 20.5455 | 20.4158 | 20.4175 | 20.1282 |  | 20.2664 | 19.982 | 20.1451 | 19.7064 | 20.1275 | 20.3777 |  | 20.4644 |  |  | 20.263 | 20.3881 | 20.6557 | [5 empty] | 21.961 | 20.3713 | 21.7015 | 22.0842 | 19.578 | 21.2131 | 21.8474 | 19.3794 | 19.9997 | 21.2293 |  | 19.8254 | 21.0065 | 18.8553 | 19.74 | 20.8866 | 19.4358 | 20.2271 | 19.0463 | 20.1851 | 19.1456 | 20.3218 | 18.7862 | 20.1785 | 21.1332 | 19.3726 | 19.7997 | 21.0267 | 18.9224 | 19.7945 | 20.8307 | 19.0147 | 20.234 | 19.2382 | 19.9926 | 18.8869 | 20.1855 | -0.065429 | 20.9474 | 0.049439 | 0.015551 | -26.9959 | 3.098 | -0.69 | -0.31 | 0.81768 | -0.32913 | -7.0329 | 0.98928 | -0.066701 | -16.6999 | 4.8476 | 0.4241 | 0.4241 | 0.43116 | 0.36 | 0.46459 | 0.44264 | 0.42854
42838.4134 | -594 | 22.889 | 22.8554 | 22.8507 | 22.7772 | 22.4211 | 21.7712 | 22.7231 | 21.8323 | 22.3719 | 22.3868 | 22.3745 | 22.0637 | 21.2892 | 22.2583 | 21.5676 | 21.7469 | 21.8876 | 21.0804 | 21.1743 | 21.4008 | 20.4867 | 20.6317 | 20.9286 | 21.9095 | 21.6757 | 21.3111 | 20.4549 | 20.5681 | 20.5366 | 22.0281 | 21.6515 | 21.1749 | 21.9918 | 21.7384 | 21.3675 | 19.9396 | 20.5143 |  | 20.5712 | 20.2258 | 20.3404 | 19.0876 |  | 16.7337 | 16.7265 | 16.4295 | 16.5815 | 16.6855 | 17.1063 | 17.6046 | 15.5917 | 16.6999 | 16.0657 | 16.8979 | 17.8585 | 46.3571 | 47.5918 | 45.3789 | 21.4391 |  |  | 0.56403 | 0.005191 | -34.4264 | 0.41131 | 0.31949 | -197.8296 | 16.6621 | -0.28818 | -0.16882 | -0.15976 | 0.024769 | 8.8288 | 9.0583 | 1.9787 | 21.8052 | 22.0313 | 22.2329 | 22.2972 | 22.133 | 21.4688 | 20.2933 | 22.2143 | 22.3909 | 22.4296 | 22.38 | 22.0142 | 21.2639 | 22.2942 | 17.4273 | 17.1568 | 16.2026 | 16.2508 | 16.2773 | 17.0705 | 16.7747 | 22.3987 | 22.1727 | 21.7338 | 22.097 | 21.8153 | 21.3299 | 21.9567 | 21.5538 | 20.9393 | 20.1501 | 20.4861 | 20.0678 | 19.8261 | 0.17341 | -0.041813 | 20.7723 | 22.1023 | 22.4126 | 20.1303 | 21.7051 | 22.1461 | 21.9615 | 21.7382 | 21.3024 | 21.8126 | 21.4711 | 21.0757 | 20.5089 | 20.5356 | 20.4237 | 20.417 | 20.1094 |  | 20.267 | 19.9833 | 20.1454 | 19.7051 | 20.1231 | 20.3712 |  | 20.4582 |  |  | 20.2633 | 20.3828 | 20.6414 | [5 empty] | 21.9628 | 20.3662 | 21.7015 | 22.0822 | 19.5732 | 21.2129 | 21.8443 | 19.368 | 19.9982 | 21.2284 |  | 19.8261 | 21.0108 | 18.8557 | 19.7444 | 20.8815 | 19.4344 | 20.2342 | 19.0456 | 20.18 | 19.1415 | 20.3212 | 18.7875 | 20.1806 | 21.139 | 19.3714 | 19.7995 | 21.0226 | 18.9217 | 19.7963 | 20.8416 | 19.0053 | 20.2336 | 19.2373 | 19.9928 | 18.8822 | 20.1829 | -0.088616 | 20.9437 | 0.04979 | 0.015522 | -27.0586 | 3.098 | 4.13 | 0.86 | 0.89694 | 0.085487 | -6.9618 | 0.76095 | 0.6711 | -16.6995 | 4.8464 | 0.42464 | 0.42407 | 0.43106 | 0.36261 | 0.46418 | 0.44206 | 0.4286
42838.4134 | -593 | 22.8855 | 22.8549 | 22.8432 | 22.7771 | 22.4186 | 21.7617 | 22.7177 | 21.8332 | 22.3754 | 22.3857 | 22.3742 | 22.0673 | 21.294 | 22.2598 | 21.5726 | 21.7566 | 21.8956 | 21.0839 | 21.1782 | 21.3986 | 20.4922 | 20.639 | 20.9342 | 21.9121 | 21.6842 | 21.3166 | 20.4537 | 20.5739 | 20.543 | 22.028 | 21.6552 | 21.1908 | 21.9884 | 21.7373 | 21.3557 | 19.9396 | 20.5099 |  | 20.5781 | 20.2173 | 20.3375 | 19.0925 |  | 16.7287 | 16.7316 | 16.4318 | 16.5832 | 16.673 | 17.0881 | 17.5674 | 15.5612 | 16.7074 | 16.0785 | 16.8962 | 17.8658 | 46.2888 | 47.5508 | 45.3388 | 21.4394 |  |  | 0.42275 | -0.092061 | -34.3443 | 0.46125 | 0.10461 | -197.8578 | 16.4945 | -0.13836 | 0.053608 | -0.14507 | 0.000812 | 8.8295 | 9.0588 | 1.9783 | 21.8021 | 22.0241 | 22.2264 | 22.2881 | 22.1286 | 21.4625 | 20.2874 | 22.209 | 22.3872 | 22.4155 | 22.3705 | 22.0137 | 21.2541 | 22.2905 | 17.4035 | 17.129 | 16.1989 | 16.2726 | 16.2614 | 17.0703 | 16.7715 | 22.3933 | 22.1765 | 21.7378 | 22.1001 | 21.8225 | 21.3342 | 21.9575 | 21.5518 | 20.9368 | 20.1503 | 20.4815 | 20.0738 | 19.8267 | 0.072361 | 0.012774 | 20.7672 | 22.0983 | 22.4112 | 20.1243 | 21.6999 | 22.1468 | 21.9631 | 21.7305 | 21.3031 | 21.811 | 21.4737 | 21.0727 | 20.5103 | 20.5336 | 20.4186 | 20.4189 | 20.0944 |  | 20.2657 | 19.9762 | 20.1479 | 19.6943 | 20.1224 | 20.3725 |  | 20.4611 |  |  | 20.2727 | 20.3811 | 20.6351 | [5 empty] | 21.964 | 20.3702 | 21.7011 | 22.0852 | 19.5756 | 21.2194 | 21.8433 | 19.3683 | 19.9951 | 21.231 |  | 19.8329 | 21.0049 | 18.8646 | 19.748 | 20.8834 | 19.4387 | 20.2311 | 19.045 | 20.1851 | 19.1455 | 20.3279 | 18.7924 | 20.1772 | 21.1495 | 19.3742 | 19.8034 | 21.031 | 18.9226 | 19.8033 | 20.8457 | 19.0134 | 20.2392 | 19.2434 | 19.9974 | 18.8838 | 20.1812 | -0.022578 | 20.9466 | 0.049833 | 0.015965 | -27.0658 | 3.0981 | -7.91 | -0.23 | 0.77653 | -0.36001 | -6.9535 | 0.80583 | 0.384 | -16.7002 | 4.8219 | 0.42502 | 0.42435 | 0.43133 | 0.36522 | 0.46421 | 0.44193 | 0.42859
42838.4134 | -592 | 22.8893 | 22.8638 | 22.8335 | 22.7821 | 22.4185 | 21.7622 | 22.72 | 21.8326 | 22.3765 | 22.3882 | 22.3727 | 22.0645 | 21.2888 | 22.2552 | 21.574 | 21.7521 | 21.895 | 21.0809 | 21.1776 | 21.4061 | 20.4799 | 20.6351 | 20.9304 | 21.9143 | 21.6743 | 21.3186 | 20.4539 | 20.5763 | 20.5424 | 22.0288 | 21.6488 | 21.1796 | 21.9967 | 21.7414 | 21.3626 | 19.9508 | 20.513 |  | 20.5757 | 20.2183 | 20.3428 | 19.1036 |  | 16.728 | 16.7263 | 16.4262 | 16.5698 | 16.6669 | 17.071 | 17.5358 | 15.5643 | 16.7039 | 16.0657 | 16.8897 | 17.8575 | 46.2241 | 47.5156 | 45.2791 | 21.4296 |  |  | 0.47533 | 0.004535 | -34.0302 | 0.71687 | 0.10921 | -197.8407 | 16.9302 | -0.17581 | -0.10986 | -0.15976 | 0.096813 | 8.8279 | 9.0574 | 1.978 | 21.8023 | 22.0297 | 22.2247 | 22.2869 | 22.1304 | 21.4669 | 20.2885 | 22.2076 | 22.3894 | 22.4221 | 22.3712 | 22.0163 | 21.2617 | 22.2932 | 17.39 | 17.1171 | 16.1915 | 16.2913 | 16.2622 | 17.0658 | 16.7764 | 22.3927 | 22.1674 | 21.7427 | 22.1041 | 21.824 | 21.3283 | 21.9624 | 21.5487 | 20.9394 | 20.1445 | 20.477 | 20.0813 | 19.8116 | 0.030289 | 0.14629 | 20.7645 | 22.1004 | 22.4098 | 20.1222 | 21.6982 | 22.1479 | 21.9679 | 21.7311 | 21.3062 | 21.8137 | 21.4731 | 21.0746 | 20.508 | 20.5395 | 20.4161 | 20.4215 | 20.0926 |  | 20.2714 | 19.977 | 20.15 | 19.6689 | 20.1141 | 20.3829 |  | 20.4543 |  |  | 20.2818 | 20.3911 | 20.6289 | [5 empty] | 21.9648 | 20.3741 | 21.6939 | 22.089 | 19.5707 | 21.2187 | 21.8484 | 19.3765 | 19.9965 | 21.2268 |  | 19.8347 | 21.0106 | 18.873 | 19.743 | 20.8864 | 19.4402 | 20.2384 | 19.0475 | 20.1855 | 19.1518 | 20.3288 | 18.799 | 20.1801 | 21.147 | 19.3775 | 19.8072 | 21.0281 | 18.9229 | 19.8083 | 20.8442 | 19.0053 | 20.2496 | 19.2498 | 19.9921 | 18.885 | 20.1792 | -0.19454 | 20.9464 | 0.049962 | 0.016204 | -27.0798 | 3.0981 | 4.29 | -0.96 | 0.8234 | 0.079903 | -6.9216 | 1.0046 | 0.39234 | -16.699 | 4.885 | 0.42526 | 0.4244 | 0.43176 | 0.3662 | 0.46561 | 0.44199 | 0.42881
42838.4134 | -591 | 22.893 | 22.864 | 22.8458 | 22.7861 | 22.4268 | 21.7685 | 22.7326 | 21.8411 | 22.3699 | 22.4028 | 22.3769 | 22.0716 | 21.3083 | 22.2645 | 21.5739 | 21.7394 | 21.8808 | 21.074 | 21.1658 | 21.3943 | 20.4784 | 20.6256 | 20.9244 | 21.902 | 21.674 | 21.3154 | 20.4521 | 20.5661 | 20.5289 | 22.026 | 21.6472 | 21.1809 | 22.0034 | 21.7378 | 21.3637 | 19.9465 | 20.5185 |  | 20.5803 | 20.2172 | 20.3423 | 19.1188 |  | 16.7262 | 16.719 | 16.4248 | 16.56 | 16.66 | 17.0522 | 17.5126 | 15.5236 | 16.7117 | 16.0387 | 16.8933 | 17.8497 | 46.1679 | 47.4756 | 45.2336 | 21.4352 |  |  | 0.45955 | -0.13477 | -34.0394 | 0.64721 | 0.17164 | -197.8604 | 16.6325 | -0.13704 | 0.088247 | 0.057387 | 0.10949 | 8.8275 | 9.0574 | 1.9781 | 21.8031 | 22.0359 | 22.2354 | 22.2917 | 22.1317 | 21.4737 | 20.2977 | 22.2184 | 22.3934 | 22.4265 | 22.379 | 22.0217 | 21.2706 | 22.2973 | 17.3534 | 17.1129 | 16.198 | 16.3007 | 16.2463 | 17.0722 | 16.7712 | 22.4 | 22.1713 | 21.7446 | 22.1032 | 21.8389 | 21.3381 | 21.9638 | 21.5569 | 20.9392 | 20.1545 | 20.4844 | 20.0829 | 19.816 | 0.11502 | -0.033634 | 20.7636 | 22.097 | 22.4069 | 20.1215 | 21.6968 | 22.1505 | 21.9715 | 21.7329 | 21.303 | 21.8038 | 21.47 | 21.0786 | 20.512 | 20.547 | 20.419 | 20.4233 | 20.0928 |  | 20.2765 | 19.9888 | 20.1472 | 19.6653 | 20.1154 | 20.3814 |  | 20.4583 |  |  | 20.2756 | 20.3765 | 20.6084 | [5 empty] | 21.9485 | 20.3526 | 21.6897 | 22.0777 | 19.5566 | 21.2085 | 21.8312 | 19.3768 | 20.0001 | 21.2335 |  | 19.8322 | 21.0117 | 18.8626 | 19.7489 | 20.8866 | 19.4324 | 20.238 | 19.0485 | 20.1962 | 19.147 | 20.3335 | 18.7927 | 20.1813 | 21.1412 | 19.3699 | 19.7963 | 21.0251 | 18.9205 | 19.7965 | 20.831 | 19.0046 | 20.2392 | 19.2397 | 19.9964 | 18.8809 | 20.1701 | 0.0080295 | 20.9465 | 0.049335 | 0.016444 | -27.0754 | 3.098 | -7.81 | 0.02 | 0.8096 | -0.43558 | -6.9224 | 0.95453 | 0.49184 | -16.6992 | 4.8417 | 0.42542 | 0.42398 | 0.4319 | 0.37101 | 0.46428 | 0.44142 | 0.42902
42838.4134 | -590 | 22.8811 | 22.8592 | 22.8424 | 22.7783 | 22.4106 | 21.7604 | 22.7206 | 21.8335 | 22.372 | 22.3928 | 22.3761 | 22.0594 | 21.2902 | 22.2584 | 21.5566 | 21.7436 | 21.8816 | 21.0784 | 21.1737 | 21.391 | 20.4749 | 20.6292 | 20.9166 | 21.9019 | 21.6695 | 21.3093 | 20.4471 | 20.5659 | 20.5401 | 22.0195 | 21.6397 | 21.183 | 21.9916 | 21.7341 | 21.3493 | 19.9455 | 20.5163 |  | 20.5777 | 20.2131 | 20.3331 | 19.1207 |  | 16.7212 | 16.7352 | 16.4227 | 16.5698 | 16.6509 | 17.0501 | 17.4823 | 15.4736 | 16.7111 | 16.049 | 16.8971 | 17.8622 | 46.1238 | 47.4492 | 45.1758 | 21.4295 |  |  | 0.29133 | -0.11572 | -33.6129 | 0.41263 | 0.13484 | -197.8355 | 16.5839 | 0.031836 | -0.052643 | -0.097446 | -0.098661 | 8.8296 | 9.0591 | 1.9778 | 21.8064 | 22.0358 | 22.2304 | 22.2962 | 22.1302 | 21.4708 | 20.2981 | 22.2244 | 22.3902 | 22.4293 | 22.38 | 22.0215 | 21.2714 | 22.3001 | 17.3233 | 17.1055 | 16.1925 | 16.3022 | 16.2673 | 17.0827 | 16.7739 | 22.4036 | 22.1796 | 21.7386 | 22.1069 | 21.8222 | 21.3382 | 21.9644 | 21.5564 | 20.9371 | 20.1521 | 20.4848 | 20.0868 | 19.8146 | 0.030878 | -0.078712 | 20.7646 | 22.0996 | 22.4098 | 20.1285 | 21.7029 | 22.1549 | 21.9692 | 21.7345 | 21.3034 | 21.8067 | 21.4775 | 21.0814 | 20.5113 | 20.5518 | 20.4202 | 20.4248 | 20.0855 |  | 20.2608 | 19.994 | 20.1488 | 19.664 | 20.1162 | 20.3773 |  | 20.4518 |  |  | 20.303 | 20.3853 | 20.6302 | [5 empty] | 21.9596 | 20.3711 | 21.7109 | 22.0841 | 19.5678 | 21.2135 | 21.8453 | 19.3819 | 20.0024 | 21.2414 |  | 19.8406 | 21.0197 | 18.8721 | 19.7487 | 20.8922 | 19.4433 | 20.2419 | 19.0526 | 20.1953 | 19.159 | 20.3303 | 18.789 | 20.18 | 21.1365 | 19.3776 | 19.7968 | 21.0263 | 18.9193 | 19.7941 | 20.8325 | 19.0133 | 20.2415 | 19.2402 | 19.9927 | 18.8831 | 20.1845 | -0.093439 | 20.9463 | 0.049482 | 0.016168 | -26.9734 | 3.0981 | -14.95 | -0.41 | 0.64463 | -0.40363 | -6.8791 | 0.76218 | 0.43594 | -16.6981 | 4.8346 | 0.4251 | 0.42389 | 0.43196 | 0.37558 | 0.46522 | 0.44134 | 0.42898
42838.4135 | -589 | 22.8887 | 22.8558 | 22.8439 | 22.7748 | 22.4215 | 21.7596 | 22.7106 | 21.8328 | 22.3734 | 22.3935 | 22.3741 | 22.0598 | 21.2891 | 22.2548 | 21.5617 | 21.7433 | 21.8889 | 21.0797 | 21.1791 | 21.4018 | 20.4808 | 20.6344 | 20.9327 | 21.9143 | 21.6746 | 21.3142 | 20.451 | 20.5703 | 20.5333 | 22.0188 | 21.6356 | 21.1777 | 21.9803 | 21.7297 | 21.3538 | 19.9378 | 20.5136 |  | 20.5697 | 20.2089 | 20.3305 | 19.1169 |  | 16.7359 | 16.7356 | 16.4195 | 16.5623 | 16.6448 | 17.0345 | 17.4574 | 15.4617 | 16.7128 | 16.0683 | 16.8947 | 17.8618 | 46.0684 | 47.4231 | 45.132 | 21.4375 |  |  | 0.42933 | -0.19523 | -33.1944 | 0.61239 | 0.0895 | -197.848 | 16.9079 | -0.060816 | -0.11744 | 0.027595 | -0.11411 | 8.8282 | 9.058 | 1.9786 | 21.8047 | 22.0327 | 22.2298 | 22.2949 | 22.1293 | 21.4654 | 20.2896 | 22.2208 | 22.394 | 22.4247 | 22.3812 | 22.0185 | 21.2633 | 22.2979 | 17.2935 | 17.049 | 16.171 | 16.299 | 16.2832 | 17.0736 | 16.7569 | 22.3985 | 22.1713 | 21.7352 | 22.1014 | 21.8246 | 21.3305 | 21.9661 | 21.5531 | 20.9337 | 20.1476 | 20.4823 | 20.0863 | 19.8054 | -0.08256 | -0.011001 | 20.7706 | 22.1014 | 22.4131 | 20.1354 | 21.702 | 22.1575 | 21.969 | 21.7377 | 21.3029 | 21.8123 | 21.4829 | 21.0759 | 20.5057 | 20.5404 | 20.4252 | 20.4303 | 20.0736 |  | 20.2671 | 20.0034 | 20.1418 | 19.6622 | 20.1154 | 20.3766 |  | 20.454 |  |  | 20.2869 | 20.3907 | 20.6245 | [5 empty] | 21.9529 | 20.3577 | 21.6989 | 22.088 | 19.5556 | 21.2109 | 21.8415 | 19.3738 | 19.9859 | 21.2344 |  | 19.8459 | 21.0022 | 18.8702 | 19.7368 | 20.8867 | 19.4355 | 20.2285 | 19.0572 | 20.1981 | 19.1585 | 20.3327 | 18.7922 | 20.1714 | 21.1423 | 19.3695 | 19.795 | 21.0323 | 18.9206 | 19.8065 | 20.8333 | 19.0102 | 20.2327 | 19.2391 | 20.0034 | 18.8825 | 20.1872 | -0.11421 | 20.9455 | 0.048327 | 0.015348 | -26.9814 | 3.0981 | 9.72 | 0.21 | 0.78253 | -0.52427 | -6.8362 | 0.92853 | 0.35515 | -16.6982 | 4.8814 | 0.42564 | 0.42339 | 0.43199 | 0.37783 | 0.46562 | 0.44119 | 0.42909
42838.4135 | -588 | 22.8859 | 22.8559 | 22.8453 | 22.7714 | 22.4188 | 21.7569 | 22.7135 | 21.8375 | 22.3649 | 22.3827 | 22.3723 | 22.0596 | 21.2956 | 22.2602 | 21.5696 | 21.7471 | 21.8838 | 21.0728 | 21.1721 | 21.3977 | 20.4819 | 20.6274 | 20.919 | 21.9015 | 21.6731 | 21.3032 | 20.4467 | 20.5756 | 20.5309 | 22.0185 | 21.641 | 21.1751 | 21.9828 | 21.73 | 21.3541 | 19.9376 | 20.5076 |  | 20.5672 | 20.2094 | 20.3324 | 19.1122 |  | 16.7383 | 16.7218 | 16.4034 | 16.5533 | 16.6267 | 17.0101 | 17.4369 | 15.4735 | 16.7109 | 16.0872 | 16.8944 | 17.8559 | 46.0116 | 47.3852 | 45.0795 | 21.4319 |  |  | 0.48715 | -0.27408 | -32.9512 | 0.54076 | 0.17427 | -197.8355 | 16.8678 | -0.06016 | -0.059843 | -0.13815 | 0.067648 | 8.8279 | 9.0575 | 1.9789 | 21.8057 | 22.0238 | 22.2247 | 22.2901 | 22.1284 | 21.4711 | 20.2853 | 22.2081 | 22.3846 | 22.4093 | 22.3853 | 22.0095 | 21.2487 | 22.2909 | 17.2839 | 17.0829 | 16.146 | 16.3041 | 16.2988 | 17.0801 | 16.7674 | 22.3964 | 22.17 | 21.7336 | 22.0986 | 21.824 | 21.3367 | 21.9637 | 21.5525 | 20.9391 | 20.1478 | 20.4838 | 20.0867 | 19.7878 | 0.025767 | 0.051005 | 20.7695 | 22.0966 | 22.4103 | 20.1281 | 21.6951 | 22.1507 | 21.9645 | 21.7368 | 21.2983 | 21.8063 | 21.4741 | 21.0729 | 20.5029 | 20.5366 | 20.424 | 20.4286 | 20.0633 |  | 20.2716 | 20.0059 | 20.151 | 19.6702 | 20.1182 | 20.3713 |  | 20.454 |  |  | 20.2895 | 20.3958 | 20.6327 | [5 empty] | 21.9585 | 20.3491 | 21.6943 | 22.0875 | 19.5619 | 21.2019 | 21.8443 | 19.3707 | 19.9914 | 21.2295 |  | 19.838 | 21.0106 | 18.8624 | 19.7496 | 20.8907 | 19.4448 | 20.2411 | 19.0597 | 20.2045 | 19.1582 | 20.3416 | 18.7941 | 20.1762 | 21.1377 | 19.368 | 19.7983 | 21.0276 | 18.9201 | 19.8007 | 20.8319 | 19.013 | 20.2285 | 19.2466 | 19.9905 | 18.8834 | 20.1765 | -0.11125 | 20.9459 | 0.04802 | 0.014469 | -27.0131 | 3.0981 | 7.11 | -0.19 | 0.83356 | -0.62117 | -6.8109 | 0.87252 | 0.49556 | -16.697 | 4.8754 | 0.42608 | 0.42363 | 0.43186 | 0.37965 | 0.46962 | 0.44131 | 0.42958
42838.4135 | -587 | 22.8861 | 22.8479 | 22.8377 | 22.7676 | 22.4163 | 21.7608 | 22.7155 | 21.8319 | 22.3691 | 22.3888 | 22.3743 | 22.0601 | 21.2878 | 22.265 | 21.5733 | 21.7458 | 21.8871 | 21.0722 | 21.1846 | 21.3999 | 20.482 | 20.631 | 20.9224 | 21.9037 | 21.6654 | 21.3032 | 20.4509 | 20.57 | 20.5292 | 22.0343 | 21.6547 | 21.1902 | 21.9997 | 21.7506 | 21.3687 | 19.9548 | 20.5205 |  | 20.5839 | 20.2256 | 20.3455 | 19.1185 |  | 16.7482 | 16.7377 | 16.4201 | 16.5484 | 16.6243 | 17.0164 | 17.4174 | 15.5471 | 16.7171 | 16.1087 | 16.9017 | 17.8591 | 45.9471 | 47.3569 | 45.018 | 21.4316 |  |  | 0.6764 | 0.002563 | -32.9749 | 0.21352 | 0.11513 | -197.8545 | 16.8362 | -0.035844 | 0.01897 | -0.11465 | 0.019734 | 8.8301 | 9.0596 | 1.9787 | 21.8026 | 22.032 | 22.2342 | 22.2868 | 22.1321 | 21.4673 | 20.2955 | 22.2143 | 22.3906 | 22.4256 | 22.3701 | 22.0207 | 21.2601 | 22.2931 | 17.264 | 17.0638 | 16.1493 | 16.2834 | 16.2984 | 17.0805 | 16.768 | 22.3974 | 22.1665 | 21.7353 | 22.1051 | 21.8213 | 21.3308 | 21.9638 | 21.5561 | 20.9332 | 20.1497 | 20.4789 | 20.0853 | 19.7703 | 0.032844 | -0.080043 | 20.7726 | 22.1011 | 22.4128 | 20.1261 | 21.6973 | 22.1507 | 21.9637 | 21.7369 | 21.2989 | 21.8065 | 21.4688 | 21.0743 | 20.5057 | 20.5416 | 20.428 | 20.4312 | 20.0694 |  | 20.268 | 20.0078 | 20.1427 | 19.6692 | 20.1165 | 20.3699 |  | 20.4512 |  |  | 20.2883 | 20.4072 | 20.6344 | [5 empty] | 21.9681 | 20.3443 | 21.6966 | 22.0781 | 19.5689 | 21.2102 | 21.8411 | 19.3694 | 19.9925 | 21.2381 |  | 19.8498 | 21.0185 | 18.8778 | 19.7445 | 20.8954 | 19.4466 | 20.2379 | 19.0595 | 20.2121 | 19.1618 | 20.3478 | 18.7985 | 20.1886 | 21.1354 | 19.3666 | 19.8017 | 21.0357 | 18.9229 | 19.8088 | 20.8394 | 19.0064 | 20.2318 | 19.2511 | 19.9999 | 18.8899 | 20.1838 | -0.22811 | 20.9463 | 0.047946 | 0.013867 | -26.9687 | 3.0981 | 16.21 | -0.62 | 0.98221 | 0.06007 | -6.8136 | 0.54828 | 0.40279 | -16.698 | 4.8709 | 0.42579 | 0.4233 | 0.43183 | 0.38192 | 0.46932 | 0.44171 | 0.43013
42838.4135 | -586 | 22.8893 | 22.8528 | 22.8489 | 22.7777 | 22.4257 | 21.7639 | 22.7204 | 21.8347 | 22.3755 | 22.3908 | 22.3828 | 22.0611 | 21.2931 | 22.259 | 21.5678 | 21.7496 | 21.8831 | 21.0761 | 21.1778 | 21.3993 | 20.4823 | 20.6331 | 20.9252 | 21.9003 | 21.673 | 21.3083 | 20.4477 | 20.5726 | 20.5349 | 22.0249 | 21.648 | 21.1772 | 21.9931 | 21.7398 | 21.3603 | 19.9447 | 20.5141 |  | 20.5767 | 20.2153 | 20.337 | 19.1014 |  | 16.7548 | 16.7322 | 16.4176 | 16.5481 | 16.615 | 17.0134 | 17.4061 | 15.6463 | 16.7251 | 16.1167 | 16.8993 | 17.8636 | 45.8914 | 47.3404 | 44.965 | 21.4433 |  |  | 0.54432 | -0.35951 | -33.1529 | 0.16292 | 0.040216 | -197.8565 | 17.0156 | -0.081188 | -0.36108 | -0.22123 | 0.036226 | 8.8279 | 9.0573 | 1.978 | 21.8051 | 22.0307 | 22.2279 | 22.2894 | 22.1348 | 21.4687 | 20.295 | 22.2208 | 22.3859 | 22.4246 | 22.3745 | 22.019 | 21.2629 | 22.2943 | 17.2285 | 17.0359 | 16.1419 | 16.2704 | 16.2909 | 17.0714 | 16.775 | 22.4044 | 22.1685 | 21.7343 | 22.1074 | 21.8264 | 21.3274 | 21.959 | 21.5578 | 20.9352 | 20.1519 | 20.4853 | 20.0864 | 19.7749 | 0.028912 | -0.10192 | 20.7732 | 22.0996 | 22.4099 | 20.1218 | 21.6949 | 22.1508 | 21.9642 | 21.733 | 21.2965 | 21.8052 | 21.4687 | 21.0745 | 20.5074 | 20.5438 | 20.4263 | 20.4314 | 20.0782 |  | 20.268 | 20.0077 | 20.1487 | 19.6785 | 20.1256 | 20.3701 |  | 20.4585 |  |  | 20.2945 | 20.4079 | 20.6421 | [5 empty] | 21.9599 | 20.3461 | 21.6916 | 22.0848 | 19.5643 | 21.2086 | 21.8428 | 19.3793 | 19.9943 | 21.238 |  | 19.8544 | 21.0167 | 18.8776 | 19.749 | 20.89 | 19.4391 | 20.2386 | 19.0643 | 20.2159 | 19.1589 | 20.3543 | 18.7994 | 20.1811 | 21.1357 | 19.3661 | 19.7882 | 21.0336 | 18.9216 | 19.7949 | 20.8363 | 19.0029 | 20.236 | 19.2576 | 19.9917 | 18.8859 | 20.1852 | -0.061162 | 20.9451 | 0.047799 | 0.012879 | -27.0357 | 3.0981 | -12.87 | 0.01 | 0.88112 | -0.71143 | -6.8319 | 0.47893 | 0.23806 | -16.698 | 4.8968 | 0.42554 | 0.4235 | 0.43187 | 0.3848 | 0.47096 | 0.44185 | 0.43008
42838.4135 | -585 | 22.8895 | 22.8608 | 22.8558 | 22.7843 | 22.4247 | 21.7698 | 22.7257 | 21.8364 | 22.3842 | 22.3895 | 22.3778 | 22.066 | 21.2962 | 22.2646 | 21.5651 | 21.7422 | 21.8797 | 21.0736 | 21.1722 | 21.3995 | 20.4822 | 20.6314 | 20.9249 | 21.9001 | 21.6713 | 21.3078 | 20.4397 | 20.5684 | 20.5322 | 22.0179 | 21.645 | 21.167 | 21.9838 | 21.7287 | 21.3528 | 19.9399 | 20.5125 |  | 20.5709 | 20.2137 | 20.3352 | 19.08 |  | 16.7375 | 16.7246 | 16.4145 | 16.5321 | 16.6099 | 16.9943 | 17.4016 | 15.7157 | 16.7181 | 16.1441 | 16.8969 | 17.8605 | 45.8376 | 47.3104 | 44.9143 | 21.4438 |  |  | 0.47204 | -0.051977 | -33.2009 | -0.15447 | 0.046128 | -197.8177 | 16.8908 | -0.26452 | 0.045435 | 0.048995 | -0.078697 | 8.8299 | 9.0596 | 1.9777 | 21.8016 | 22.0362 | 22.2273 | 22.2938 | 22.1343 | 21.4674 | 20.2932 | 22.2229 | 22.3907 | 22.4293 | 22.381 | 22.019 | 21.2597 | 22.2963 | 17.2113 | 17.024 | 16.1577 | 16.2673 | 16.2946 | 17.0806 | 16.7807 | 22.4032 | 22.1727 | 21.7436 | 22.1124 | 21.8285 | 21.3384 | 21.9613 | 21.5601 | 20.937 | 20.1585 | 20.4857 | 20.0792 | 19.7736 | 0.13055 | -0.043715 | 20.7752 | 22.0986 | 22.4065 | 20.1261 | 21.6978 | 22.1475 | 21.968 | 21.7296 | 21.3003 | 21.8024 | 21.4749 | 21.0766 | 20.5083 | 20.5528 | 20.4191 | 20.4314 | 20.0768 |  | 20.2656 | 19.996 | 20.1425 | 19.6814 | 20.1156 | 20.3664 |  | 20.4537 |  |  | 20.2902 | 20.4048 | 20.6492 | [5 empty] | 21.9614 | 20.3451 | 21.687 | 22.0768 | 19.5676 | 21.2104 | 21.8408 | 19.3669 | 19.9907 | 21.2386 |  | 19.8522 | 21.0042 | 18.8744 | 19.7496 | 20.8857 | 19.4383 | 20.2372 | 19.0621 | 20.2194 | 19.1618 | 20.3524 | 18.7991 | 20.1827 | 21.1304 | 19.3717 | 19.7906 | 21.0265 | 18.9229 | 19.7972 | 20.8322 | 19.0049 | 20.2304 | 19.2585 | 19.9936 | 18.8776 | 20.1842 | -0.21272 | 20.9468 | 0.047166 | 0.012008 | -27.0538 | 3.0981 | -4.3 | 0.67 | 0.82053 | -0.27051 | -6.8367 | -0.46632 | 0.25495 | -16.6958 | 4.8786 | 0.4255 | 0.42362 | 0.43146 | 0.38778 | 0.46987 | 0.44228 | 0.43033
42838.4135 | -584 | 22.8816 | 22.8619 | 22.8482 | 22.7879 | 22.4222 | 21.7748 | 22.7216 | 21.8431 | 22.378 | 22.3883 | 22.3691 | 22.068 | 21.2928 | 22.2577 | 21.5786 | 21.7563 | 21.8897 | 21.0804 | 21.1776 | 21.4044 | 20.4913 | 20.638 | 20.9357 | 21.9048 | 21.6751 | 21.3218 | 20.4561 | 20.5741 | 20.5354 | 22.021 | 21.6439 | 21.1716 | 21.9883 | 21.7363 | 21.3526 | 19.9366 | 20.516 |  | 20.5751 | 20.2098 | 20.3364 | 19.0793 |  | 16.7421 | 16.7334 | 16.4182 | 16.536 | 16.6112 | 16.9857 | 17.4204 | 15.7341 | 16.7221 | 16.1746 | 16.9054 | 17.853 | 45.7857 | 47.2897 | 44.8726 | 21.4383 |  |  | 0.35376 | -0.083521 | -33.7214 | 0.31931 | 0.19267 | -197.846 | 16.6536 | -0.18304 | 0.13884 | -0.077515 | 0.094556 | 8.829 | 9.0587 | 1.9782 | 21.8039 | 22.0375 | 22.2283 | 22.2908 | 22.1305 | 21.4696 | 20.297 | 22.2223 | 22.3869 | 22.4285 | 22.3785 | 22.0219 | 21.261 | 22.2984 | 17.1949 | 17.0347 | 16.141 | 16.2587 | 16.2687 | 17.0849 | 16.7823 | 22.3998 | 22.1661 | 21.7382 | 22.1015 | 21.8213 | 21.3264 | 21.9576 | 21.5511 | 20.9281 | 20.1493 | 20.4799 | 20.0758 | 19.766 | 0.13901 | -0.063115 | 20.7753 | 22.0958 | 22.4054 | 20.1256 | 21.6996 | 22.1467 | 21.969 | 21.7345 | 21.3045 | 21.8025 | 21.4808 | 21.0749 | 20.5103 | 20.5497 | 20.4243 | 20.436 | 20.0822 |  | 20.2598 | 20.0049 | 20.1488 | 19.6866 | 20.1158 | 20.3635 |  | 20.4497 |  |  | 20.286 | 20.4076 | 20.641 | [5 empty] | 21.9666 | 20.3531 | 21.6897 | 22.083 | 19.5654 | 21.2107 | 21.8438 | 19.3589 | 19.9774 | 21.2259 |  | 19.8422 | 21.0046 | 18.869 | 19.7463 | 20.8812 | 19.437 | 20.2322 | 19.0549 | 20.2216 | 19.1619 | 20.3503 | 18.7912 | 20.1811 | 21.1321 | 19.3673 | 19.7837 | 21.0234 | 18.9193 | 19.7899 | 20.8387 | 19.0037 | 20.2218 | 19.254 | 19.9899 | 18.8806 | 20.1857 | -0.13202 | 20.9457 | 0.04633 | 0.012502 | -26.9859 | 3.0981 | -2.5 | 0.04 | 0.71033 | -0.34291 | -6.8902 | 0.67048 | 0.52104 | -16.6967 | 4.8442 | 0.42516 | 0.42359 | 0.43132 | 0.3901 | 0.47191 | 0.44219 | 0.43024
42838.4135 | -583 | 22.89 | 22.8593 | 22.8469 | 22.7812 | 22.4231 | 21.7653 | 22.7303 | 21.8349 | 22.3859 | 22.3997 | 22.3771 | 22.0657 | 21.2991 | 22.2628 | 21.5813 | 21.7546 | 21.8883 | 21.0807 | 21.1799 | 21.4084 | 20.4937 | 20.6344 | 20.9356 | 21.9106 | 21.6741 | 21.3208 | 20.4564 | 20.5748 | 20.5376 | 22.0279 | 21.6449 | 21.1801 | 21.9921 | 21.7456 | 21.3651 | 19.9387 | 20.5229 |  | 20.579 | 20.2143 | 20.342 | 19.0813 |  | 16.7557 | 16.7513 | 16.4278 | 16.5558 | 16.6273 | 16.9955 | 17.4312 | 15.704 | 16.7343 | 16.2142 | 16.9165 | 17.8525 | 45.7374 | 47.2745 | 44.8249 | 21.4479 |  |  | 0.59755 | -0.28723 | -33.9343 | 0.32786 | 0.20975 | -197.846 | 16.576 | -0.31052 | -0.019367 | -0.020659 | 0.021991 | 8.8302 | 9.0601 | 1.9791 | 21.8001 | 22.0326 | 22.228 | 22.2991 | 22.131 | 21.4733 | 20.2935 | 22.2174 | 22.3866 | 22.422 | 22.3751 | 22.0165 | 21.2624 | 22.3002 | 17.1753 | 17.034 | 16.156 | 16.2454 | 16.2462 | 17.073 | 16.7689 | 22.388 | 22.156 | 21.7284 | 22.0918 | 21.8227 | 21.3229 | 21.9522 | 21.5383 | 20.9262 | 20.145 | 20.4679 | 20.0642 | 19.7563 | 0.070985 | -0.096971 | 20.7779 | 22.098 | 22.4069 | 20.1241 | 21.6989 | 22.1483 | 21.9669 | 21.7377 | 21.306 | 21.8095 | 21.4854 | 21.0808 | 20.5135 | 20.5409 | 20.4308 | 20.4384 | 20.0707 |  | 20.26 | 20.0011 | 20.1452 | 19.6836 | 20.1142 | 20.3604 |  | 20.4511 |  |  | 20.2887 | 20.4085 | 20.6369 | [5 empty] | 21.96 | 20.3509 | 21.6934 | 22.0789 | 19.5641 | 21.2094 | 21.845 | 19.3641 | 19.9797 | 21.2264 |  | 19.842 | 21.0109 | 18.8696 | 19.7438 | 20.8808 | 19.4441 | 20.2319 | 19.0521 | 20.2238 | 19.1629 | 20.358 | 18.8033 | 20.1818 | 21.1359 | 19.3724 | 19.7838 | 21.0265 | 18.9198 | 19.7926 | 20.842 | 19.0044 | 20.225 | 19.2572 | 19.9913 | 18.8872 | 20.1815 | -0.095294 | 20.9454 | 0.046177 | 0.012386 | -27.1458 | 3.0981 | -2.41 | 0.12 | 0.9232 | -0.63592 | -6.9121 | 0.67941 | 0.54366 | -16.697 | 4.833 | 0.42548 | 0.42357 | 0.43135 | 0.3909 | 0.46868 | 0.44221 | 0.43036
42838.4135 | -582 | 22.8866 | 22.8552 | 22.8405 | 22.7714 | 22.4218 | 21.7589 | 22.7259 | 21.8337 | 22.3816 | 22.387 | 22.3693 | 22.0651 | 21.2896 | 22.2584 | 21.5767 | 21.7554 | 21.893 | 21.0862 | 21.1877 | 21.4097 | 20.4919 | 20.6395 | 20.9358 | 21.9121 | 21.6749 | 21.3228 | 20.4616 | 20.5766 | 20.544 | 22.024 | 21.6458 | 21.1812 | 21.9979 | 21.7451 | 21.3597 | 19.939 | 20.5233 |  | 20.5753 | 20.2155 | 20.3442 | 19.0804 |  | 16.7489 | 16.7389 | 16.4163 | 16.5531 | 16.6253 | 17.0013 | 17.4095 | 15.628 | 16.7299 | 16.2181 | 16.9152 | 17.8612 | 45.6827 | 47.261 | 44.7713 | 21.4441 |  |  | 0.67443 | -0.21297 | -34.2037 | 0.24112 | 0.17755 | -197.8447 | 16.5366 | -0.099584 | -0.17446 | -0.04017 | 0.13917 | 8.8287 | 9.0585 | 1.9786 | 21.8063 | 22.03 | 22.2234 | 22.2901 | 22.1293 | 21.4717 | 20.2962 | 22.2149 | 22.3914 | 22.4203 | 22.3784 | 22.0237 | 21.2613 | 22.292 | 17.1679 | 17.055 | 16.1769 | 16.261 | 16.2538 | 17.0774 | 16.7777 | 22.3976 | 22.1694 | 21.726 | 22.1047 | 21.8244 | 21.3298 | 21.9589 | 21.547 | 20.9262 | 20.1451 | 20.4772 | 20.0663 | 19.7748 | 0.12544 | 0.11301 | 20.7804 | 22.101 | 22.4078 | 20.1215 | 21.7015 | 22.1502 | 21.9728 | 21.739 | 21.3098 | 21.8086 | 21.4868 | 21.0792 | 20.5204 | 20.5415 | 20.4269 | 20.4407 | 20.0868 |  | 20.2693 | 20.0123 | 20.1473 | 19.6971 | 20.1234 | 20.3692 |  | 20.4626 |  |  | 20.2956 | 20.4091 | 20.6377 | [5 empty] | 21.9528 | 20.3514 | 21.6983 | 22.0815 | 19.5654 | 21.2081 | 21.8485 | 19.3611 | 19.9808 | 21.2274 |  | 19.8477 | 21.0126 | 18.8737 | 19.7421 | 20.8765 | 19.4481 | 20.2276 | 19.0518 | 20.2279 | 19.1615 | 20.3539 | 18.807 | 20.1892 | 21.1397 | 19.3702 | 19.7856 | 21.0334 | 18.9238 | 19.7947 | 20.8412 | 19.0133 | 20.2278 | 19.2596 | 19.9935 | 18.8917 | 20.1817 | -0.18396 | 20.9468 | 0.046238 | 0.012582 | -27 | 3.0981 | -4.65 | 0.25 | 0.98081 | -0.54758 | -6.9394 | 0.58264 | 0.5002 | -16.6971 | 4.8273 | 0.42535 | 0.42333 | 0.43129 | 0.39223 | 0.46738 | 0.44224 | 0.42985
42838.4136 | -581 | 22.8895 | 22.8567 | 22.842 | 22.7746 | 22.4176 | 21.7584 | 22.7199 | 21.8368 | 22.3796 | 22.3887 | 22.3773 | 22.063 | 21.2938 | 22.2615 | 21.5753 | 21.7503 | 21.8874 | 21.0835 | 21.1803 | 21.4009 | 20.4859 | 20.635 | 20.9311 | 21.9065 | 21.6715 | 21.3178 | 20.4521 | 20.565 | 20.5435 | 22.0332 | 21.6515 | 21.1844 | 21.9921 | 21.7437 | 21.3602 | 19.9459 | 20.5302 |  | 20.5801 | 20.2214 | 20.3498 | 19.088 |  | 16.7432 | 16.7395 | 16.4153 | 16.5455 | 16.6213 | 16.9916 | 17.402 | 15.6025 | 16.7293 | 16.2233 | 16.9023 | 17.8586 | 45.6267 | 47.244 | 44.7436 | 21.4421 |  |  | 0.3945 | -0.23794 | -34.3666 | 0.20892 | 0.1493 | -197.8269 | 16.143 | -0.29738 | -0.25405 | -0.18451 | 0.070078 | 8.8294 | 9.0589 | 1.9785 | 21.7965 | 22.032 | 22.2318 | 22.2939 | 22.132 | 21.4683 | 20.2935 | 22.2121 | 22.3948 | 22.4226 | 22.3788 | 22.0183 | 21.2611 | 22.2974 | 17.1605 | 17.0809 | 16.1952 | 16.2658 | 16.2619 | 17.0804 | 16.774 | 22.3967 | 22.1695 | 21.7303 | 22.0967 | 21.8188 | 21.3267 | 21.967 | 21.5518 | 20.9393 | 20.1497 | 20.4721 | 20.0687 | 19.7818 | 0.20959 | -0.083847 | 20.7863 | 22.1026 | 22.4042 | 20.1181 | 21.7036 | 22.1485 | 21.9686 | 21.7374 | 21.3075 | 21.8065 | 21.4803 | 21.0808 | 20.523 | 20.544 | 20.4225 | 20.4455 | 20.0887 |  | 20.2611 | 19.9991 | 20.1422 | 19.6839 | 20.1129 | 20.3553 |  | 20.4509 |  |  | 20.2986 | 20.4152 | 20.6442 | [5 empty] | 21.9589 | 20.3588 | 21.702 | 22.0861 | 19.5787 | 21.2122 | 21.8478 | 19.3608 | 19.9774 | 21.2307 |  | 19.847 | 21.0156 | 18.8801 | 19.7416 | 20.8767 | 19.4458 | 20.2286 | 19.0523 | 20.2283 | 19.1711 | 20.3539 | 18.8047 | 20.1854 | 21.1323 | 19.3684 | 19.7796 | 21.0286 | 18.9183 | 19.7861 | 20.8346 | 19.0079 | 20.2189 | 19.2483 | 19.987 | 18.8893 | 20.177 | -0.15781 | 20.9457 | 0.047774 | 0.012139 | -26.8699 | 3.0981 | 6.95 | 0.48 | 0.75013 | -0.57879 | -6.9559 | 0.54234 | 0.45867 | -16.6961 | 4.7694 | 0.42502 | 0.42353 | 0.4313 | 0.39341 | 0.46491 | 0.44226 | 0.42982
42838.4136 | -580 | 22.8891 | 22.8603 | 22.8511 | 22.7793 | 22.4226 | 21.7686 | 22.7202 | 21.8396 | 22.3846 | 22.3963 | 22.3872 | 22.0774 | 21.3044 | 22.2638 | 21.5721 | 21.7443 | 21.8821 | 21.0784 | 21.1791 | 21.3979 | 20.4867 | 20.6199 | 20.9254 | 21.9064 | 21.6698 | 21.3133 | 20.4473 | 20.5649 | 20.5413 | 22.0297 | 21.6486 | 21.1848 | 21.9994 | 21.7382 | 21.3663 | 19.9422 | 20.5302 |  | 20.5827 | 20.2223 | 20.3492 | 19.0992 |  | 16.7418 | 16.7354 | 16.4115 | 16.5408 | 16.6138 | 16.9879 | 17.4247 | 15.6091 | 16.7341 | 16.2132 | 16.9074 | 17.8542 | 45.5574 | 47.2215 | 44.7048 | 21.4387 |  |  | 0.3577 | -0.29314 | -34.0433 | 0.072894 | 0.1631 | -197.8144 | 16.4314 | -0.29935 | -0.099542 | -0.063668 | 0.14091 | 8.8288 | 9.0585 | 1.9783 | 21.7954 | 22.0333 | 22.2254 | 22.2956 | 22.139 | 21.4697 | 20.2958 | 22.2191 | 22.3897 | 22.4254 | 22.3787 | 22.0228 | 21.2688 | 22.2982 | 17.1565 | 17.0992 | 16.2181 | 16.2849 | 16.2626 | 17.0872 | 16.773 | 22.3946 | 22.1718 | 21.7314 | 22.0941 | 21.8177 | 21.3262 | 21.9609 | 21.5464 | 20.9282 | 20.1437 | 20.4724 | 20.0588 | 19.7709 | 0.09438 | -0.051703 | 20.7862 | 22.1007 | 22.4048 | 20.1116 | 21.7057 | 22.1475 | 21.9602 | 21.7349 | 21.3062 | 21.8099 | 21.4754 | 21.0801 | 20.523 | 20.5439 | 20.4193 | 20.445 | 20.0989 |  | 20.2599 | 20.0044 | 20.1392 | 19.6793 | 20.1068 | 20.3503 |  | 20.4442 |  |  | 20.2997 | 20.4153 | 20.6418 | [5 empty] | 21.9646 | 20.3642 | 21.6993 | 22.0845 | 19.5794 | 21.215 | 21.8477 | 19.3639 | 19.9768 | 21.2334 |  | 19.847 | 21.0069 | 18.8793 | 19.742 | 20.8784 | 19.4456 | 20.226 | 19.0467 | 20.2302 | 19.1722 | 20.3563 | 18.8068 | 20.1725 | 21.1258 | 19.3606 | 19.7782 | 21.0221 | 18.9157 | 19.7808 | 20.8297 | 19.0071 | 20.2188 | 19.25 | 19.983 | 18.8937 | 20.1786 | -0.18044 | 20.9459 | 0.048002 | 0.013272 | -27.0619 | 3.098 | 8.87 | 0.94 | 0.71429 | -0.64242 | -6.923 | 0.32035 | 0.47939 | -16.6955 | 4.8118 | 0.4247 | 0.42328 | 0.43122 | 0.39465 | 0.46225 | 0.44182 | 0.42992
42838.4136 | -579 | 22.8877 | 22.8559 | 22.8436 | 22.7743 | 22.42 | 21.7628 | 22.7206 | 21.8321 | 22.381 | 22.3883 | 22.3794 | 22.0723 | 21.2923 | 22.2689 | 21.5692 | 21.7376 | 21.8842 | 21.069 | 21.1769 | 21.3944 | 20.4839 | 20.6253 | 20.9249 | 21.8933 | 21.6756 | 21.3075 | 20.4554 | 20.5731 | 20.5344 | 22.0223 | 21.6424 | 21.176 | 21.9929 | 21.7376 | 21.3592 | 19.9335 | 20.532 |  | 20.5747 | 20.2189 | 20.3462 | 19.0998 |  | 16.7347 | 16.7323 | 16.4072 | 16.5371 | 16.6137 | 16.9845 | 17.4507 | 15.539 | 16.7367 | 16.1819 | 16.9104 | 17.8563 | 45.4878 | 47.2129 | 44.6737 | 21.4427 |  |  | 0.37216 | -0.19588 | -33.9126 | 0.37123 | 0.24918 | -197.8683 | 16.4012 | -0.22575 | -0.16104 | -0.10101 | 0.041955 | 8.8286 | 9.0584 | 1.978 | 21.7994 | 22.0268 | 22.2253 | 22.2913 | 22.1302 | 21.4705 | 20.2954 | 22.2147 | 22.3951 | 22.4282 | 22.3804 | 22.0197 | 21.272 | 22.2986 | 17.1556 | 17.1085 | 16.2307 | 16.2938 | 16.2566 | 17.088 | 16.7697 | 22.3997 | 22.1743 | 21.7372 | 22.1006 | 21.8167 | 21.3331 | 21.9658 | 21.5597 | 20.9362 | 20.1496 | 20.4768 | 20.0638 | 19.7782 | 0.1339 | -0.021652 | 20.7741 | 22.0962 | 22.4035 | 20.0977 | 21.7036 | 22.1503 | 21.9625 | 21.7347 | 21.3057 | 21.8114 | 21.4722 | 21.076 | 20.5155 | 20.5419 | 20.4195 | 20.4435 | 20.1172 |  | 20.27 | 20.0053 | 20.1402 | 19.6741 | 20.1201 | 20.3546 |  | 20.452 |  |  | 20.2928 | 20.4157 | 20.637 | [5 empty] | 21.9636 | 20.3593 | 21.693 | 22.0836 | 19.5757 | 21.2107 | 21.8451 | 19.3653 | 19.984 | 21.2312 |  | 19.8534 | 21.0097 | 18.8755 | 19.7396 | 20.88 | 19.4499 | 20.2244 | 19.052 | 20.2274 | 19.1723 | 20.3584 | 18.8131 | 20.1788 | 21.1282 | 19.3676 | 19.7831 | 21.0249 | 18.9181 | 19.7827 | 20.8313 | 19.0129 | 20.2205 | 19.2543 | 19.9847 | 18.8924 | 20.1844 | -0.065985 | 20.9458 | 0.048174 | 0.014556 | -26.9597 | 3.098 | 8.57 | -0.92 | 0.72857 | -0.52514 | -6.9097 | 0.72293 | 0.59255 | -16.6976 | 4.8073 | 0.42453 | 0.42329 | 0.43181 | 0.39483 | 0.46048 | 0.44152 | 0.42991
42838.4136 | -578 | 22.885 | 22.8537 | 22.8301 | 22.7802 | 22.4145 | 21.7591 | 22.7165 | 21.8292 | 22.3752 | 22.3872 | 22.379 | 22.0567 | 21.2915 | 22.2584 | 21.5619 | 21.7461 | 21.8828 | 21.0733 | 21.1772 | 21.3956 | 20.481 | 20.6291 | 20.9231 | 21.9031 | 21.6787 | 21.3095 | 20.4516 | 20.5619 | 20.5392 | 22.0224 | 21.6407 | 21.1702 | 21.9948 | 21.7276 | 21.364 | 19.9406 | 20.5314 |  | 20.5795 | 20.223 | 20.3494 | 19.1113 |  | 16.7383 | 16.7226 | 16.4025 | 16.5289 | 16.6045 | 16.9882 | 17.4687 | 15.5267 | 16.7371 | 16.1397 | 16.9009 | 17.8584 | 45.4122 | 47.2008 | 44.6335 | 21.4494 |  |  | 0.29002 | -0.090089 | -34.0479 | 0.28251 | 0.20055 | -197.8374 | 16.3118 | -0.21918 | 0.085134 | -0.084228 | 0.14264 | 8.8291 | 9.0588 | 1.9789 | 21.7944 | 22.0197 | 22.2149 | 22.2854 | 22.1284 | 21.4629 | 20.2845 | 22.2074 | 22.3842 | 22.412 | 22.3763 | 22.0122 | 21.2622 | 22.2895 | 17.1645 | 17.1191 | 16.2363 | 16.2846 | 16.2467 | 17.0837 | 16.7733 | 22.3999 | 22.1777 | 21.7437 | 22.1022 | 21.8234 | 21.3318 | 21.9656 | 21.5543 | 20.9372 | 20.1565 | 20.483 | 20.0703 | 19.7811 | 0.11443 | -0.020511 | 20.7748 | 22.0963 | 22.4075 | 20.0933 | 21.6978 | 22.1517 | 21.9702 | 21.7372 | 21.3076 | 21.8112 | 21.4737 | 21.0798 | 20.5109 | 20.5465 | 20.4236 | 20.4507 | 20.1175 |  | 20.2648 | 20.0009 | 20.1369 | 19.6655 | 20.1143 | 20.354 |  | 20.4521 |  |  | 20.2886 | 20.4304 | 20.6435 | [5 empty] | 21.9607 | 20.355 | 21.6976 | 22.0853 | 19.5732 | 21.2139 | 21.8456 | 19.3604 | 19.9785 | 21.2144 |  | 19.8519 | 20.995 | 18.8642 | 19.7349 | 20.8742 | 19.4356 | 20.217 | 19.0472 | 20.2266 | 19.1703 | 20.3484 | 18.8064 | 20.1795 | 21.1279 | 19.3756 | 19.7807 | 21.0268 | 18.9151 | 19.7923 | 20.8326 | 19.0138 | 20.2215 | 19.2464 | 19.9812 | 18.892 | 20.1869 | -0.21587 | 20.9447 | 0.048383 | 0.014237 | -27.1025 | 3.098 | 6.39 | -0.93 | 0.64317 | -0.35613 | -6.9233 | 0.63065 | 0.5316 | -16.6964 | 4.7943 | 0.42434 | 0.4233 | 0.43186 | 0.39334 | 0.46027 | 0.44144 | 0.43006
42838.4136 | -577 | 22.8906 | 22.8631 | 22.8446 | 22.7827 | 22.4255 | 21.7703 | 22.7304 | 21.8412 | 22.3829 | 22.3985 | 22.3901 | 22.0766 | 21.302 | 22.265 | 21.5547 | 21.7517 | 21.889 | 21.0781 | 21.1702 | 21.4048 | 20.4812 | 20.6254 | 20.9244 | 21.9129 | 21.6786 | 21.3036 | 20.4462 | 20.5645 | 20.539 | 22.0345 | 21.6425 | 21.1756 | 22.0004 | 21.7426 | 21.358 | 19.9389 | 20.5321 |  | 20.5755 | 20.2188 | 20.3464 | 19.1437 |  | 16.7398 | 16.7317 | 16.4079 | 16.5412 | 16.6077 | 16.9918 | 17.4965 | 15.5998 | 16.7483 | 16.1282 | 16.9106 | 17.8538 | 45.3353 | 47.1841 | 44.5901 | 21.4489 |  |  | 0.57126 | -0.22874 | -34.2083 | 0.15109 | 0.1769 | -197.8775 | 16.302 | -0.11733 | -0.12581 | -0.067654 | 0.15809 | 8.8298 | 9.0594 | 1.9786 | 21.8008 | 22.028 | 22.2229 | 22.2897 | 22.1274 | 21.4646 | 20.2869 | 22.2106 | 22.3853 | 22.4186 | 22.3767 | 22.0159 | 21.264 | 22.2926 | 17.1687 | 17.1352 | 16.2406 | 16.2766 | 16.2303 | 17.0831 | 16.7715 | 22.3926 | 22.1674 | 21.7346 | 22.0996 | 21.814 | 21.3282 | 21.9624 | 21.5526 | 20.9396 | 20.1473 | 20.4771 | 20.0673 | 19.7759 | -0.070174 | -0.11694 | 20.766 | 22.0927 | 22.4069 | 20.0939 | 21.6934 | 22.1493 | 21.9685 | 21.7344 | 21.3021 | 21.8087 | 21.4716 | 21.0776 | 20.5119 | 20.5451 | 20.4222 | 20.4537 | 20.1179 |  | 20.2629 | 19.9827 | 20.1297 | 19.64 | 20.1099 | 20.3527 |  | 20.4497 |  |  | 20.2806 | 20.4208 | 20.6496 | [5 empty] | 21.9581 | 20.3518 | 21.6938 | 22.0842 | 19.573 | 21.2147 | 21.8414 | 19.3697 | 19.9675 | 21.2302 |  | 19.8493 | 21.0027 | 18.8745 | 19.7376 | 20.8773 | 19.4408 | 20.223 | 19.051 | 20.2326 | 19.1684 | 20.3547 | 18.8146 | 20.1763 | 21.1218 | 19.3755 | 19.7768 | 21.0276 | 18.919 | 19.7929 | 20.8305 | 19.0265 | 20.221 | 19.2492 | 19.9793 | 18.8969 | 20.184 | -0.035934 | 20.9476 | 0.048229 | 0.014905 | -27.0622 | 3.098 | -11.1 | 0.78 | 0.90267 | -0.56748 | -6.9397 | 0.46121 | 0.49927 | -16.6982 | 4.7928 | 0.42427 | 0.42356 | 0.43242 | 0.39281 | 0.45958 | 0.44048 | 0.4299
42838.4136 | -576 | 22.8822 | 22.8535 | 22.8447 | 22.7773 | 22.4179 | 21.7595 | 22.7233 | 21.8336 | 22.371 | 22.3888 | 22.3704 | 22.0622 | 21.2905 | 22.2547 | 21.5716 | 21.7502 | 21.8915 | 21.0859 | 21.1844 | 21.4038 | 20.4907 | 20.633 | 20.9415 | 21.9231 | 21.685 | 21.319 | 20.4622 | 20.5745 | 20.5468 | 22.0197 | 21.637 | 21.1812 | 21.9897 | 21.7424 | 21.3595 | 19.9415 | 20.5313 |  | 20.575 | 20.2107 | 20.3447 | 19.1532 |  | 16.736 | 16.7296 | 16.4111 | 16.551 | 16.6094 | 16.981 | 17.5138 | 15.6807 | 16.7489 | 16.1644 | 16.9052 | 17.8535 | 45.2692 | 47.1668 | 44.5582 | 21.4478 |  |  | 0.37544 | -0.23466 | -34.0131 | 0.39028 | 0.1631 | -197.8749 | 15.8998 | -0.1469 | -0.10207 | -0.080242 | 0.16313 | 8.8277 | 9.0576 | 1.9784 | 21.8058 | 22.029 | 22.2289 | 22.2901 | 22.1234 | 21.4603 | 20.2839 | 22.2091 | 22.3886 | 22.4234 | 22.3758 | 22.0145 | 21.2558 | 22.2944 | 17.1808 | 17.1442 | 16.2487 | 16.2722 | 16.2224 | 17.0806 | 16.7729 | 22.4003 | 22.159 | 21.7357 | 22.1031 | 21.8146 | 21.3264 | 21.9644 | 21.5521 | 20.9346 | 20.1509 | 20.4755 | 20.0606 | 19.7713 | -0.02358 | -0.0041534 | 20.751 | 22.0939 | 22.4087 | 20.0957 | 21.6948 | 22.1449 | 21.9676 | 21.7303 | 21.3004 | 21.8068 | 21.4733 | 21.0759 | 20.5167 | 20.5509 | 20.4243 | 20.4525 | 20.1252 |  | 20.2587 | 19.9607 | 20.1332 | 19.6302 | 20.1055 | 20.3525 |  | 20.452 |  |  | 20.2819 | 20.4183 | 20.6414 | [5 empty] | 21.9532 | 20.3455 | 21.6967 | 22.0764 | 19.5753 | 21.2089 | 21.8464 | 19.3687 | 19.9743 | 21.2315 |  | 19.8509 | 21.0022 | 18.8842 | 19.7371 | 20.8773 | 19.439 | 20.2167 | 19.056 | 20.2321 | 19.1712 | 20.3608 | 18.8233 | 20.1809 | 21.1339 | 19.3744 | 19.77 | 21.0261 | 18.9189 | 19.7885 | 20.83 | 19.024 | 20.2226 | 19.2513 | 19.9783 | 18.894 | 20.1875 | -0.033522 | 20.9472 | 0.048401 | 0.014121 | -27.0992 | 3.098 | -3.74 | -0.1 | 0.73179 | -0.57477 | -6.9199 | 0.74125 | 0.47939 | -16.6978 | 4.7333 | 0.42393 | 0.42429 | 0.43255 | 0.39118 | 0.45885 | 0.4403 | 0.43014
42838.4136 | -575 | 22.8812 | 22.8503 | 22.838 | 22.7705 | 22.4168 | 21.7544 | 22.7174 | 21.8247 | 22.3644 | 22.38 | 22.3702 | 22.052 | 21.2876 | 22.2509 | 21.5656 | 21.7522 | 21.8881 | 21.0721 | 21.1717 | 21.3994 | 20.4913 | 20.6241 | 20.9294 | 21.907 | 21.6654 | 21.3114 | 20.4543 | 20.5649 | 20.5515 | 22.0178 | 21.6402 | 21.177 | 21.9985 | 21.7376 | 21.3628 | 19.9411 | 20.5385 |  | 20.5819 | 20.216 | 20.3435 | 19.1731 |  | 16.7304 | 16.729 | 16.4163 | 16.5524 | 16.6136 | 17.0063 | 17.5292 | 15.7594 | 16.7421 | 16.1873 | 16.8986 | 17.8596 | 45.2354 | 47.1579 | 44.5294 | 21.4522 |  |  | 0.43984 | -0.39368 | -33.9277 | 0.095894 | 0.13878 | -197.8276 | 16.2514 | -0.27504 | 0.11082 | -0.062199 | 0.054628 | 8.8292 | 9.059 | 1.978 | 21.793 | 22.0296 | 22.2283 | 22.2927 | 22.122 | 21.458 | 20.2856 | 22.2201 | 22.3859 | 22.4239 | 22.3798 | 22.022 | 21.2498 | 22.2931 | 17.1846 | 17.1326 | 16.2425 | 16.268 | 16.2056 | 17.0815 | 16.7711 | 22.3862 | 22.1625 | 21.7349 | 22.0966 | 21.8143 | 21.328 | 21.9554 | 21.5453 | 20.929 | 20.1519 | 20.474 | 20.057 | 19.7657 | 0.065283 | -0.093738 | 20.7411 | 22.1006 | 22.4172 | 20.1061 | 21.7045 | 22.1532 | 21.9767 | 21.7364 | 21.3112 | 21.8124 | 21.4799 | 21.0803 | 20.5286 | 20.5538 | 20.4376 | 20.4533 | 20.1306 |  | 20.262 | 19.9585 | 20.1382 | 19.6271 | 20.1192 | 20.3553 |  | 20.4503 |  |  | 20.2938 | 20.3928 | 20.6392 | [5 empty] | 21.9536 | 20.3452 | 21.6973 | 22.0812 | 19.5795 | 21.2047 | 21.8542 | 19.3723 | 19.9788 | 21.2318 |  | 19.8504 | 21.0029 | 18.8863 | 19.7371 | 20.8791 | 19.4394 | 20.2202 | 19.0585 | 20.2333 | 19.177 | 20.3667 | 18.8051 | 20.1818 | 21.1132 | 19.3634 | 19.7637 | 21.0159 | 18.908 | 19.7863 | 20.8262 | 19.0246 | 20.2057 | 19.2475 | 19.9627 | 18.8881 | 20.1815 | -0.19083 | 20.9472 | 0.048868 | 0.014455 | -27.0526 | 3.0981 | -12.68 | -0.36 | 0.79208 | -0.74447 | -6.9112 | 0.36743 | 0.44223 | -16.6965 | 4.7855 | 0.42389 | 0.42452 | 0.43309 | 0.39086 | 0.45931 | 0.43974 | 0.43033
42838.4136 | -574 | 22.8818 | 22.8528 | 22.8421 | 22.7695 | 22.4136 | 21.7623 | 22.7153 | 21.8285 | 22.3735 | 22.3847 | 22.3745 | 22.0543 | 21.2868 | 22.2522 | 21.5606 | 21.737 | 21.8772 | 21.0635 | 21.1654 | 21.3954 | 20.4771 | 20.622 | 20.9213 | 21.89 | 21.6676 | 21.3001 | 20.4551 | 20.5627 | 20.5419 | 22.0199 | 21.6462 | 21.1784 | 21.9973 | 21.7419 | 21.3637 | 19.9404 | 20.5357 |  | 20.5775 | 20.2183 | 20.3452 | 19.19 |  | 16.7358 | 16.7313 | 16.415 | 16.541 | 16.6183 | 17.0225 | 17.5304 | 15.7499 | 16.7441 | 16.1842 | 16.8993 | 17.8578 | 45.1892 | 47.1353 | 44.4837 | 21.4515 |  |  | 0.3945 | -0.2294 | -33.8988 | 0.44942 | 0.040216 | -197.8407 | 16.5248 | -0.33286 | -0.011777 | -0.22186 | -0.099355 | 8.8298 | 9.0594 | 1.9778 | 21.8012 | 22.0272 | 22.2254 | 22.2846 | 22.1289 | 21.4719 | 20.2929 | 22.2179 | 22.394 | 22.4211 | 22.3803 | 22.0233 | 21.2634 | 22.2978 | 17.1865 | 17.1209 | 16.2317 | 16.2485 | 16.196 | 17.0796 | 16.7689 | 22.382 | 22.1606 | 21.7351 | 22.0913 | 21.8118 | 21.327 | 21.9525 | 21.5464 | 20.9288 | 20.1504 | 20.47 | 20.0589 | 19.7697 | -0.079218 | -0.12645 | 20.7281 | 22.099 | 22.4169 | 20.108 | 21.7024 | 22.1589 | 21.975 | 21.7417 | 21.3092 | 21.8091 | 21.4799 | 21.0766 | 20.5238 | 20.5494 | 20.4384 | 20.4493 | 20.1316 |  | 20.2638 | 19.9371 | 20.1299 | 19.6306 | 20.1155 | 20.3519 |  | 20.4475 |  |  | 20.2918 | 20.3903 | 20.6325 | [5 empty] | 21.9616 | 20.3485 | 21.6993 | 22.0852 | 19.5833 | 21.215 | 21.8432 | 19.3758 | 19.9685 | 21.2297 |  | 19.8384 | 21.0049 | 18.8761 | 19.7416 | 20.8695 | 19.4383 | 20.2144 | 19.0502 | 20.2246 | 19.1652 | 20.3599 | 18.8146 | 20.1803 | 21.1168 | 19.3672 | 19.7734 | 21.0237 | 18.9236 | 19.7892 | 20.831 | 19.0332 | 20.2173 | 19.2516 | 19.9711 | 18.8994 | 20.1974 | -0.12405 | 20.9472 | 0.049065 | 0.014237 | -26.9997 | 3.0981 | -9.8 | 0.83 | 0.75013 | -0.56829 | -6.9083 | 0.79543 | 0.23806 | -16.6976 | 4.8257 | 0.42392 | 0.42483 | 0.43287 | 0.39043 | 0.46027 | 0.43924 | 0.43017
42838.4136 | -573 | 22.8906 | 22.8625 | 22.8496 | 22.7731 | 22.4179 | 21.7702 | 22.7174 | 21.8361 | 22.3747 | 22.3945 | 22.3771 | 22.0612 | 21.293 | 22.26 | 21.5548 | 21.7358 | 21.8712 | 21.0663 | 21.1709 | 21.3936 | 20.4772 | 20.6257 | 20.9171 | 21.8953 | 21.6692 | 21.3046 | 20.4602 | 20.5599 | 20.542 | 22.0208 | 21.6443 | 21.1853 | 21.9923 | 21.7381 | 21.3577 | 19.9436 | 20.5322 |  | 20.5764 | 20.217 | 20.3501 | 19.2093 |  | 16.7459 | 16.735 | 16.4235 | 16.5475 | 16.6262 | 17.016 | 17.5434 | 15.7968 | 16.7465 | 16.1697 | 16.9114 | 17.8571 | 45.1559 | 47.1223 | 44.4511 | 21.4491 |  |  | 0.25585 | -0.030949 | -34.2497 | 0.47637 | 0.0619 | -197.8677 | 16.4157 | -0.3644 | 0.11082 | -0.12094 | 0.097507 | 8.8283 | 9.0583 | 1.9786 | 21.7993 | 22.0221 | 22.223 | 22.2903 | 22.1211 | 21.4551 | 20.2899 | 22.2147 | 22.386 | 22.4228 | 22.3748 | 22.0231 | 21.2573 | 22.2994 | 17.188 | 17.101 | 16.2088 | 16.2375 | 16.1865 | 17.0782 | 16.7624 | 22.3898 | 22.165 | 21.7362 | 22.0947 | 21.8177 | 21.3262 | 21.95 | 21.5427 | 20.9265 | 20.154 | 20.4737 | 20.053 | 19.7832 | 0.049752 | -0.10876 | 20.7118 | 22.0877 | 22.4062 | 20.0995 | 21.6923 | 22.145 | 21.9636 | 21.7359 | 21.3016 | 21.8053 | 21.4693 | 21.068 | 20.5147 | 20.5507 | 20.4316 | 20.4464 | 20.117 |  | 20.2649 | 19.9361 | 20.1265 | 19.6309 | 20.1201 | 20.3559 |  | 20.4486 |  |  | 20.3013 | 20.3928 | 20.6426 | [5 empty] | 21.9633 | 20.3575 | 21.6962 | 22.089 | 19.5856 | 21.2152 | 21.8475 | 19.3657 | 19.9664 | 21.2269 |  | 19.8368 | 20.9946 | 18.8726 | 19.7313 | 20.8648 | 19.4331 | 20.2103 | 19.0451 | 20.2147 | 19.164 | 20.3518 | 18.8155 | 20.1787 | 21.1262 | 19.3731 | 19.7634 | 21.0276 | 18.9096 | 19.78 | 20.8256 | 19.0171 | 20.2039 | 19.255 | 19.9708 | 18.8945 | 20.1878 | -0.2398 | 20.9465 | 0.049169 | 0.014658 | -27.0616 | 3.098 | -2.65 | 0.9 | 0.6041 | -0.20874 | -6.944 | 0.81894 | 0.29535 | -16.6985 | 4.8097 | 0.42436 | 0.42475 | 0.43301 | 0.39009 | 0.46206 | 0.43881 | 0.42992
42838.4137 | -572 | 22.8903 | 22.8556 | 22.8478 | 22.7757 | 22.4213 | 21.7715 | 22.7267 | 21.8389 | 22.382 | 22.3975 | 22.3872 | 22.066 | 21.3021 | 22.2661 | 21.562 | 21.7442 | 21.8795 | 21.0713 | 21.174 | 21.3939 | 20.4835 | 20.6339 | 20.9271 | 21.9047 | 21.6714 | 21.3028 | 20.4612 | 20.5714 | 20.5401 | 22.0228 | 21.6463 | 21.1848 | 21.9891 | 21.7324 | 21.356 | 19.945 | 20.538 |  | 20.5714 | 20.2186 | 20.3452 | 19.2294 |  | 16.7468 | 16.7334 | 16.4206 | 16.5551 | 16.6309 | 17.0238 | 17.5732 | 15.7435 | 16.746 | 16.0844 | 16.9056 | 17.8505 | 45.1093 | 47.1071 | 44.4061 | 21.4436 |  |  | 0.60018 | -0.27014 | -34.2477 | 0.43957 | 0.26758 | -197.8762 | 16.2567 | -0.28621 | -0.034156 | -0.12304 | 0.14716 | 8.8286 | 9.0585 | 1.9789 | 21.7962 | 22.0281 | 22.2276 | 22.289 | 22.1265 | 21.469 | 20.2894 | 22.2166 | 22.3826 | 22.4158 | 22.3767 | 22.0152 | 21.2615 | 22.29 | 17.2033 | 17.1109 | 16.1724 | 16.2082 | 16.1989 | 17.09 | 16.7742 | 22.3871 | 22.1641 | 21.7276 | 22.1025 | 21.8221 | 21.3251 | 21.9512 | 21.5522 | 20.9265 | 20.1537 | 20.4705 | 20.0503 | 19.7925 | 0.0029612 | -0.21661 | 20.6993 | 22.0869 | 22.4062 | 20.1036 | 21.6907 | 22.1402 | 21.9542 | 21.7307 | 21.2993 | 21.8023 | 21.4685 | 21.0681 | 20.5191 | 20.5494 | 20.4321 | 20.4544 | 20.1015 |  | 20.2612 | 19.9222 | 20.1283 | 19.6314 | 20.1051 | 20.3494 |  | 20.4471 |  |  | 20.3033 | 20.3877 | 20.6393 | [5 empty] | 21.9682 | 20.3573 | 21.7035 | 22.0868 | 19.5827 | 21.2158 | 21.8398 | 19.368 | 19.9552 | 21.2217 |  | 19.839 | 20.9925 | 18.8698 | 19.7369 | 20.8659 | 19.4318 | 20.2018 | 19.0467 | 20.2179 | 19.1765 | 20.3537 | 18.8118 | 20.1694 | 21.1245 | 19.3698 | 19.7694 | 21.0216 | 18.9204 | 19.7898 | 20.8236 | 19.0252 | 20.2065 | 19.2488 | 19.9676 | 18.8913 | 20.1938 | -0.051331 | 20.9479 | 0.048868 | 0.014331 | -27.0617 | 3.0981 | -0.78 | -0.04 | 0.92523 | -0.6167 | -6.9438 | 0.78667 | 0.61407 | -16.6991 | 4.7864 | 0.42467 | 0.4252 | 0.4325 | 0.38976 | 0.46747 | 0.4383 | 0.42965
42838.4137 | -571 | 22.8884 | 22.8593 | 22.8458 | 22.775 | 22.423 | 21.7686 | 22.7216 | 21.8325 | 22.3869 | 22.3913 | 22.3766 | 22.0637 | 21.3033 | 22.2662 | 21.5672 | 21.7422 | 21.8851 | 21.0742 | 21.1781 | 21.4014 | 20.4869 | 20.637 | 20.9284 | 21.9086 | 21.6739 | 21.3119 | 20.4657 | 20.5694 | 20.5434 | 22.0199 | 21.6441 | 21.179 | 21.9898 | 21.735 | 21.3554 | 19.9414 | 20.5366 |  | 20.5735 | 20.2175 | 20.3564 | 19.2398 |  | 16.7524 | 16.7436 | 16.4225 | 16.5522 | 16.6342 | 17.0619 | 17.6084 | 15.6701 | 16.751 | 16.0337 | 16.9087 | 17.8616 | 45.0832 | 47.1095 | 44.382 | 21.4511 |  |  | 0.38399 | -0.18668 | -33.9527 | 0.42183 | 0.28204 | -197.8388 | 16.3559 | -0.11864 | 0.0088504 | -0.1499 | 0.10081 | 8.8302 | 9.0601 | 1.9783 | 21.7997 | 22.0305 | 22.2306 | 22.2933 | 22.1298 | 21.4643 | 20.292 | 22.2204 | 22.3893 | 22.4247 | 22.3832 | 22.0207 | 21.2612 | 22.2979 | 17.201 | 17.0954 | 16.0845 | 16.1367 | 16.2089 | 17.0823 | 16.7624 | 22.3954 | 22.1682 | 21.7295 | 22.0963 | 21.8167 | 21.3279 | 21.9635 | 21.5553 | 20.9276 | 20.1529 | 20.478 | 20.0529 | 19.8075 | 0.049752 | -0.18085 | 20.6998 | 22.0946 | 22.4076 | 20.1039 | 21.693 | 22.1429 | 21.961 | 21.7359 | 21.3022 | 21.8061 | 21.4739 | 21.0716 | 20.5168 | 20.5416 | 20.4268 | 20.4577 | 20.1028 |  | 20.2582 | 19.9251 | 20.1271 | 19.6431 | 20.1117 | 20.3525 |  | 20.4496 |  |  | 20.3097 | 20.3772 | 20.6297 | [5 empty] | 21.9598 | 20.3533 | 21.7019 | 22.0814 | 19.5783 | 21.2157 | 21.8457 | 19.3762 | 19.962 | 21.2227 |  | 19.8432 | 21.0005 | 18.87 | 19.7344 | 20.8696 | 19.4378 | 20.2188 | 19.0512 | 20.2292 | 19.1806 | 20.3476 | 18.8182 | 20.1781 | 21.1197 | 19.3726 | 19.7684 | 21.0191 | 18.9245 | 19.7872 | 20.8282 | 19.0213 | 20.2085 | 19.2494 | 19.9744 | 18.895 | 20.1965 | -0.10698 | 20.947 | 0.048794 | 0.012582 | -27.0151 | 3.098 | -10.62 | -0.7 | 0.74007 | -0.51267 | -6.9139 | 0.77064 | 0.63049 | -16.6986 | 4.8013 | 0.42453 | 0.42508 | 0.43239 | 0.38913 | 0.47586 | 0.43789 | 0.42921
42838.4137 | -570 | 22.8817 | 22.8483 | 22.8471 | 22.776 | 22.4063 | 21.7614 | 22.7197 | 21.8225 | 22.3744 | 22.3851 | 22.3721 | 22.0582 | 21.2913 | 22.2506 | 21.5686 | 21.7408 | 21.8839 | 21.0703 | 21.1724 | 21.3958 | 20.4783 | 20.6252 | 20.9247 | 21.9023 | 21.6724 | 21.3095 | 20.4565 | 20.5649 | 20.5467 | 22.0257 | 21.6468 | 21.1757 | 21.9928 | 21.7361 | 21.3522 | 19.9495 | 20.5351 |  | 20.5721 | 20.2237 | 20.3522 | 19.2581 |  | 16.7545 | 16.7435 | 16.4191 | 16.5689 | 16.6503 | 17.1113 | 17.6517 | 15.6129 | 16.757 | 16.005 | 16.9185 | 17.8522 | 45.0454 | 47.103 | 44.3585 | 21.4538 |  |  | 0.40304 | -0.13083 | -34.0749 | 0.25032 | 0.25115 | -197.8696 | 16.1541 | -0.16596 | 0.076766 | -0.089264 | 0.0020272 | 8.8289 | 9.0583 | 1.9782 | 21.7972 | 22.0233 | 22.2265 | 22.2926 | 22.1279 | 21.4628 | 20.2946 | 22.2146 | 22.3874 | 22.424 | 22.3793 | 22.02 | 21.2563 | 22.2965 | 17.2179 | 17.0664 | 16.0279 | 16.1246 | 16.2261 | 17.0918 | 16.776 | 22.396 | 22.1737 | 21.7346 | 22.1065 | 21.8188 | 21.3292 | 21.9657 | 21.5528 | 20.9346 | 20.159 | 20.4722 | 20.0603 | 19.8106 | -0.022204 | -0.018609 | 20.7026 | 22.0942 | 22.4071 | 20.1066 | 21.7016 | 22.1451 | 21.9686 | 21.7298 | 21.3009 | 21.81 | 21.4763 | 21.0737 | 20.5123 | 20.5432 | 20.4295 | 20.4558 | 20.1152 |  | 20.269 | 19.9326 | 20.133 | 19.6622 | 20.1221 | 20.3621 |  | 20.4569 |  |  | 20.3 | 20.3633 | 20.6256 | [5 empty] | 21.963 | 20.3476 | 21.6997 | 22.0831 | 19.5765 | 21.2091 | 21.8516 | 19.3749 | 19.9673 | 21.2175 |  | 19.8398 | 21.0017 | 18.872 | 19.7341 | 20.8729 | 19.4317 | 20.2226 | 19.0615 | 20.2243 | 19.1779 | 20.3564 | 18.8178 | 20.1767 | 21.1206 | 19.3704 | 19.7587 | 21.0238 | 18.9157 | 19.7793 | 20.8316 | 19.0191 | 20.2077 | 19.245 | 19.9662 | 18.8928 | 20.1973 | 0.016006 | 20.9472 | 0.047651 | 0.012742 | -26.9912 | 3.0981 | -2.55 | -0.11 | 0.75821 | -0.42919 | -6.9263 | 0.59365 | 0.59501 | -16.7013 | 4.772 | 0.42455 | 0.42507 | 0.43221 | 0.38835 | 0.48374 | 0.43766 | 0.42933
42838.4137 | -569 | 22.8872 | 22.8561 | 22.8378 | 22.7664 | 22.4217 | 21.7572 | 22.7173 | 21.8303 | 22.3723 | 22.3816 | 22.3713 | 22.0645 | 21.2849 | 22.2593 | 21.5666 | 21.7435 | 21.8819 | 21.0722 | 21.172 | 21.3932 | 20.4811 | 20.6256 | 20.9223 | 21.901 | 21.6701 | 21.3128 | 20.4593 | 20.5711 | 20.5459 | 22.025 | 21.6429 | 21.1726 | 21.9875 | 21.7405 | 21.3575 | 19.9405 | 20.5468 |  | 20.572 | 20.2263 | 20.3539 | 19.2663 |  | 16.7437 | 16.7363 | 16.4171 | 16.577 | 16.6625 | 17.1218 | 17.6576 | 15.5711 | 16.7449 | 15.9213 | 16.9189 | 17.8565 | 45.0261 | 47.1108 | 44.3419 | 21.462 |  |  | 0.61201 | -0.13149 | -33.722 | 0.17212 | 0.19398 | -197.8289 | 16.2849 | -0.19815 | 0.12425 | -0.099544 | 0.071641 | 8.8292 | 9.0585 | 1.9782 | 21.7952 | 22.023 | 22.2228 | 22.2924 | 22.1256 | 21.4648 | 20.2852 | 22.2167 | 22.3818 | 22.4229 | 22.3826 | 22.0221 | 21.2597 | 22.2937 | 17.1979 | 17.0256 | 16.0306 | 16.1122 | 16.2382 | 17.0747 | 16.7675 | 22.3841 | 22.1675 | 21.7291 | 22.1032 | 21.822 | 21.3179 | 21.9562 | 21.5472 | 20.931 | 20.1538 | 20.4693 | 20.0592 | 19.8138 | 0.08455 | -0.060643 | 20.6948 | 22.0905 | 22.4052 | 20.1137 | 21.6987 | 22.1468 | 21.9629 | 21.7275 | 21.2983 | 21.8061 | 21.4782 | 21.0731 | 20.5181 | 20.5457 | 20.4259 | 20.4507 | 20.1079 |  | 20.2674 | 19.9362 | 20.1287 | 19.6637 | 20.1207 | 20.3565 |  | 20.4557 |  |  | 20.2959 | 20.3582 | 20.624 | [5 empty] | 21.9674 | 20.3501 | 21.7049 | 22.0847 | 19.5808 | 21.2104 | 21.8533 | 19.3798 | 19.9678 | 21.2222 |  | 19.8453 | 21.011 | 18.8755 | 19.7485 | 20.8822 | 19.4352 | 20.2254 | 19.0683 | 20.2313 | 19.1907 | 20.3666 | 18.8089 | 20.1686 | 21.1182 | 19.3654 | 19.7513 | 21.0119 | 18.9066 | 19.7781 | 20.8221 | 19.0096 | 20.205 | 19.2482 | 19.9589 | 18.8901 | 20.1969 | 0.10838 | 20.9471 | 0.047092 | 0.012858 | -27.038 | 3.098 | -0.62 | 0.07 | 0.93432 | -0.43025 | -6.8903 | 0.49227 | 0.52294 | -16.6999 | 4.7914 | 0.4247 | 0.42482 | 0.43212 | 0.38858 | 0.48245 | 0.43713 | 0.42906
42838.4137 | -568 | 22.8881 | 22.8603 | 22.8426 | 22.7761 | 22.4188 | 21.7683 | 22.7168 | 21.8357 | 22.3745 | 22.3869 | 22.3822 | 22.0641 | 21.2941 | 22.2587 | 21.5652 | 21.7452 | 21.8827 | 21.0771 | 21.1762 | 21.3978 | 20.4854 | 20.6282 | 20.9273 | 21.9041 | 21.6766 | 21.3173 | 20.4624 | 20.5734 | 20.5432 | 22.0243 | 21.6397 | 21.1701 | 21.9876 | 21.7335 | 21.3554 | 19.9373 | 20.5436 |  | 20.5586 | 20.2151 | 20.345 | 19.2655 |  | 16.7448 | 16.7311 | 16.4213 | 16.5811 | 16.6606 | 17.1105 | 17.658 | 15.5413 | 16.752 | 15.8373 | 16.9125 | 17.858 | 44.9973 | 47.1182 | 44.3273 | 21.4581 |  |  | 0.22693 | -0.17354 | -33.2154 | 0.58742 | 0.19792 | -197.8736 | 16.5123 | -0.0917 | 0.047965 | 0.084241 | 0.080842 | 8.8286 | 9.0579 | 1.978 | 21.8006 | 22.029 | 22.2334 | 22.2948 | 22.1343 | 21.4696 | 20.2843 | 22.2269 | 22.3901 | 22.4329 | 22.3893 | 22.0245 | 21.2639 | 22.2968 | 17.1804 | 17.0044 | 16.038 | 16.1143 | 16.234 | 17.0829 | 16.7657 | 22.3912 | 22.1671 | 21.7399 | 22.1037 | 21.8255 | 21.3281 | 21.9643 | 21.5516 | 20.9354 | 20.1567 | 20.4706 | 20.0615 | 19.811 | -0.0001844 | -0.032303 | 20.6969 | 22.0932 | 22.4051 | 20.1126 | 21.6961 | 22.1433 | 21.9673 | 21.728 | 21.3009 | 21.8058 | 21.4731 | 21.0711 | 20.5177 | 20.5488 | 20.4311 | 20.4552 | 20.1156 |  | 20.2717 | 19.9433 | 20.1328 | 19.6729 | 20.1205 | 20.3681 |  | 20.4607 |  |  | 20.292 | 20.3631 | 20.6322 | [5 empty] | 21.9607 | 20.3533 | 21.7018 | 22.0893 | 19.5862 | 21.2119 | 21.8475 | 19.3737 | 19.9536 | 21.2218 |  | 19.8416 | 21.0035 | 18.8806 | 19.7383 | 20.8757 | 19.4365 | 20.2278 | 19.0666 | 20.2282 | 19.1838 | 20.3625 | 18.8117 | 20.1667 | 21.114 | 19.3689 | 19.7523 | 21.0119 | 18.913 | 19.7767 | 20.8265 | 19.0062 | 20.2018 | 19.2456 | 19.9679 | 18.8918 | 20.1982 | -0.0005035 | 20.9471 | 0.047903 | 0.012836 | -27.0578 | 3.0981 | 8.88 | 0.02 | 0.56894 | -0.49429 | -6.8383 | 0.90939 | 0.52821 | -16.7015 | 4.8246 | 0.42463 | 0.42476 | 0.43186 | 0.39148 | 0.48141 | 0.43704 | 0.42924
42838.4137 | -567 | 22.8898 | 22.8643 | 22.8454 | 22.7776 | 22.4239 | 21.7719 | 22.7261 | 21.8395 | 22.381 | 22.3922 | 22.3882 | 22.0667 | 21.3024 | 22.2634 | 21.5625 | 21.7424 | 21.8811 | 21.0745 | 21.172 | 21.3945 | 20.4844 | 20.623 | 20.9263 | 21.9049 | 21.6757 | 21.313 | 20.4563 | 20.5664 | 20.5451 | 22.0207 | 21.6388 | 21.1782 | 21.9916 | 21.7388 | 21.3636 | 19.9411 | 20.5446 |  | 20.5643 | 20.2203 | 20.3512 | 19.2711 |  | 16.7421 | 16.7309 | 16.414 | 16.5782 | 16.6561 | 17.0956 | 17.6398 | 15.5073 | 16.7578 | 15.7773 | 16.9132 | 17.8586 | 44.9638 | 47.1324 | 44.3047 | 21.4676 |  |  | 0.50227 | -0.18143 | -32.6976 | 0.35151 | 0.073072 | -197.8079 | 16.5668 | -0.031904 | -0.031626 | 0.073331 | 0.032234 | 8.8288 | 9.0586 | 1.9788 | 21.8015 | 22.0339 | 22.2377 | 22.2923 | 22.1283 | 21.471 | 20.2938 | 22.2205 | 22.4004 | 22.4301 | 22.3825 | 22.0275 | 21.269 | 22.3069 | 17.178 | 16.9948 | 16.0344 | 16.1188 | 16.2189 | 17.0809 | 16.7621 | 22.3914 | 22.1637 | 21.7342 | 22.0942 | 21.8164 | 21.3259 | 21.9577 | 21.5494 | 20.9329 | 20.1599 | 20.4676 | 20.0587 | 19.8087 | 0.03481 | -0.073006 | 20.7094 | 22.0911 | 22.4104 | 20.1163 | 21.7011 | 22.1477 | 21.9731 | 21.7342 | 21.3057 | 21.81 | 21.4706 | 21.0731 | 20.5208 | 20.5571 | 20.4333 | 20.4634 | 20.1034 |  | 20.2602 | 19.9281 | 20.1239 | 19.6602 | 20.1065 | 20.356 |  | 20.4472 |  |  | 20.2959 | 20.3639 | 20.637 | [5 empty] | 21.9674 | 20.3566 | 21.6996 | 22.0891 | 19.5885 | 21.2131 | 21.8446 | 19.3683 | 19.9469 | 21.2189 |  | 19.8396 | 20.9958 | 18.8812 | 19.7274 | 20.874 | 19.4373 | 20.2267 | 19.0652 | 20.2308 | 19.1695 | 20.3552 | 18.8134 | 20.1671 | 21.1188 | 19.3705 | 19.7545 | 21.0213 | 18.9161 | 19.7762 | 20.8291 | 19.0033 | 20.2078 | 19.2447 | 19.968 | 18.8985 | 20.2004 | -0.21457 | 20.9473 | 0.048204 | 0.01346 | -27.055 | 3.0981 | -2.58 | 0.34 | 0.84641 | -0.50539 | -6.7848 | 0.70347 | 0.32094 | -16.6983 | 4.8325 | 0.42458 | 0.42488 | 0.43175 | 0.39151 | 0.4814 | 0.43701 | 0.42941
42838.4137 | -566 | 22.8823 | 22.8525 | 22.838 | 22.7765 | 22.4214 | 21.7654 | 22.7243 | 21.8376 | 22.3773 | 22.3889 | 22.3806 | 22.0627 | 21.297 | 22.2629 | 21.5632 | 21.7382 | 21.8892 | 21.0783 | 21.1749 | 21.3962 | 20.487 | 20.6285 | 20.9316 | 21.9073 | 21.6764 | 21.3131 | 20.4575 | 20.5688 | 20.5415 | 22.0131 | 21.6297 | 21.1717 | 21.9849 | 21.7325 | 21.3599 | 19.9396 | 20.5364 |  | 20.5622 | 20.2177 | 20.3416 | 19.2658 |  | 16.7485 | 16.7343 | 16.4134 | 16.581 | 16.6567 | 17.0916 | 17.6315 | 15.4959 | 16.7606 | 15.7544 | 16.9117 | 17.8561 | 44.9195 | 47.1485 | 44.2747 | 21.4655 |  |  | 0.40699 | -0.18537 | -32.6148 | 0.50396 | 0.12367 | -197.825 | 16.8651 | -0.008248 | -0.15792 | 0.021511 | -0.069496 | 8.8295 | 9.0593 | 1.9785 | 21.8043 | 22.0337 | 22.2265 | 22.2963 | 22.1308 | 21.4721 | 20.2925 | 22.2216 | 22.3995 | 22.4234 | 22.3865 | 22.0226 | 21.2679 | 22.3003 | 17.1612 | 16.9932 | 16.047 | 16.0979 | 16.1994 | 17.0784 | 16.7616 | 22.392 | 22.1648 | 21.7356 | 22.0925 | 21.818 | 21.3183 | 21.9576 | 21.5493 | 20.9301 | 20.1511 | 20.4674 | 20.0533 | 19.8113 | 0.017903 | -0.12379 | 20.7107 | 22.0901 | 22.4083 | 20.1113 | 21.702 | 22.1478 | 21.9679 | 21.7348 | 21.3036 | 21.807 | 21.4654 | 21.073 | 20.5137 | 20.5527 | 20.4301 | 20.4592 | 20.1083 |  | 20.2712 | 19.9282 | 20.1256 | 19.656 | 20.1167 | 20.3648 |  | 20.4511 |  |  | 20.3062 | 20.3607 | 20.6391 | [5 empty] | 21.9671 | 20.356 | 21.7027 | 22.0821 | 19.5872 | 21.2126 | 21.8508 | 19.3738 | 19.9533 | 21.2237 |  | 19.8392 | 21.0007 | 18.8858 | 19.7306 | 20.8798 | 19.4371 | 20.2276 | 19.0759 | 20.2365 | 19.1706 | 20.3568 | 18.8148 | 20.1657 | 21.1217 | 19.3738 | 19.7522 | 21.0201 | 18.9175 | 19.7766 | 20.8253 | 18.9981 | 20.2065 | 19.2409 | 19.9641 | 18.9098 | 20.2014 | 0.017861 | 20.9474 | 0.0481 | 0.013976 | -27.0334 | 3.0981 | -3.33 | -0.89 | 0.76191 | -0.51086 | -6.7762 | 0.84232 | 0.41752 | -16.6989 | 4.8758 | 0.42482 | 0.42494 | 0.4322 | 0.39309 | 0.47994 | 0.43711 | 0.42904
42838.4137 | -565 | 22.8871 | 22.854 | 22.8492 | 22.7756 | 22.4159 | 21.763 | 22.723 | 21.8347 | 22.3827 | 22.3923 | 22.3812 | 22.0703 | 21.2937 | 22.263 | 21.563 | 21.7395 | 21.8835 | 21.0781 | 21.1702 | 21.3999 | 20.4837 | 20.6325 | 20.9293 | 21.9081 | 21.6681 | 21.312 | 20.4537 | 20.5635 | 20.5348 | 22.0138 | 21.6353 | 21.1761 | 21.9907 | 21.7352 | 21.365 | 19.9388 | 20.546 |  | 20.5706 | 20.2224 | 20.3419 | 19.2783 |  | 16.7482 | 16.735 | 16.4295 | 16.5772 | 16.6648 | 17.1011 | 17.6546 | 15.496 | 16.7642 | 15.7237 | 16.9119 | 17.8669 | 44.8778 | 47.1649 | 44.2442 | 21.5892 |  |  | 0.47401 | -0.28394 | -32.6673 | 0.39094 | 0.14141 | -197.9012 | 16.7219 | -0.099584 | -0.031626 | 0.10019 | -0.075225 | 8.83 | 9.0598 | 1.9783 | 21.7937 | 22.0373 | 22.2283 | 22.2882 | 22.1246 | 21.4737 | 20.2881 | 22.2199 | 22.3884 | 22.4269 | 22.3841 | 22.0154 | 21.2601 | 22.3014 | 17.1481 | 17.0189 | 16.0623 | 16.1038 | 16.1773 | 17.0851 | 16.7645 | 22.385 | 22.1647 | 21.7222 | 22.0954 | 21.8133 | 21.3194 | 21.9579 | 21.5436 | 20.9281 | 20.1426 | 20.4694 | 20.0593 | 19.8174 | -0.046189 | -0.14947 | 20.7116 | 22.0955 | 22.4165 | 20.1114 | 21.6992 | 22.1539 | 21.9736 | 21.7344 | 21.3087 | 21.8087 | 21.4727 | 21.0794 | 20.5202 | 20.5647 | 20.4322 | 20.4611 | 20.1238 |  | 20.2713 | 19.9353 | 20.1284 | 19.6679 | 20.1232 | 20.3616 |  | 20.46 |  |  | 20.3096 | 20.3632 | 20.6365 | [5 empty] | 21.967 | 20.3646 | 21.7077 | 22.0901 | 19.5885 | 21.2141 | 21.8514 | 19.3829 | 19.9537 | 21.2234 |  | 19.8386 | 21.0066 | 18.8899 | 19.7344 | 20.8854 | 19.4424 | 20.2287 | 19.0781 | 20.2414 | 19.1758 | 20.3574 | 18.8201 | 20.1695 | 21.1248 | 19.3769 | 19.754 | 21.0233 | 18.9199 | 19.7826 | 20.8276 | 18.9903 | 20.2077 | 19.244 | 19.9688 | 18.9119 | 20.2021 | -0.20845 | 20.9485 | 0.048383 | 0.014121 | -26.9967 | 3.0981 | -0.87 | 0.34 | 0.82225 | -0.63226 | -6.7817 | 0.74188 | 0.44647 | -16.7024 | 4.8551 | 0.42439 | 0.42484 | 0.43209 | 0.39533 | 0.47858 | 0.43674 | 0.42859
42838.4137 | -564 | 22.8838 | 22.8581 | 22.8529 | 22.7779 | 22.4158 | 21.7619 | 22.7203 | 21.8341 | 22.3763 | 22.3925 | 22.3807 | 22.0654 | 21.2936 | 22.2537 | 21.5547 | 21.7391 | 21.8811 | 21.0707 | 21.1689 | 21.3957 | 20.4725 | 20.6241 | 20.9154 | 21.8984 | 21.6682 | 21.3093 | 20.4442 | 20.5634 | 20.528 | 22.0234 | 21.6489 | 21.1819 | 22.0007 | 21.7448 | 21.3677 | 19.9502 | 20.5553 |  | 20.5795 | 20.2287 | 20.3479 | 19.2955 |  | 16.7518 | 16.7423 | 16.4318 | 16.5915 | 16.6714 | 17.1288 | 17.6851 | 15.4754 | 16.7709 | 15.7061 | 16.9124 | 17.8589 | 44.8328 | 47.1838 | 44.2086 | 21.8278 |  |  | 0.45693 | -0.16172 | -32.7712 | 0.42183 | 0.22618 | -197.9038 | 16.8389 | -0.19947 | 0.0063206 | -0.050451 | -0.023839 | 8.829 | 9.0588 | 1.9779 | 21.7964 | 22.034 | 22.2286 | 22.2927 | 22.1342 | 21.4706 | 20.2912 | 22.2244 | 22.3845 | 22.4299 | 22.3819 | 22.0238 | 21.2688 | 22.3008 | 17.1099 | 17.0347 | 16.0496 | 16.1151 | 16.1655 | 17.0859 | 16.7598 | 22.3841 | 22.1707 | 21.7321 | 22.0958 | 21.814 | 21.3249 | 21.9551 | 21.5512 | 20.9325 | 20.1522 | 20.4677 | 20.0606 | 19.8136 | -0.035769 | -0.04866 | 20.7139 | 22.0982 | 22.407 | 20.1095 | 21.6973 | 22.1497 | 21.9719 | 21.7331 | 21.3074 | 21.8091 | 21.4714 | 21.077 | 20.5226 | 20.5669 | 20.4253 | 20.463 | 20.1214 |  | 20.265 | 19.9391 | 20.1237 | 19.6625 | 20.1141 | 20.3602 |  | 20.4537 |  |  | 20.2986 | 20.3604 | 20.6286 | [5 empty] | 21.9673 | 20.356 | 21.6976 | 22.09 | 19.5906 | 21.2137 | 21.8413 | 19.3816 | 19.9468 | 21.2242 |  | 19.8374 | 21.01 | 18.8865 | 19.732 | 20.8836 | 19.4512 | 20.2274 | 19.0828 | 20.2398 | 19.1677 | 20.3605 | 18.8204 | 20.1654 | 21.1306 | 19.3832 | 19.7576 | 21.0232 | 18.925 | 19.7784 | 20.8361 | 18.9893 | 20.2124 | 19.2447 | 19.9738 | 18.9025 | 20.2 | -0.031668 | 20.9472 | 0.048886 | 0.014237 | -26.9751 | 3.0981 | 2.41 | -0.05 | 0.80728 | -0.47716 | -6.7925 | 0.77064 | 0.56468 | -16.7033 | 4.8723 | 0.42424 | 0.42457 | 0.43193 | 0.39967 | 0.47944 | 0.43664 | 0.42901
42838.4138 | -563 | 22.8857 | 22.8601 | 22.8433 | 22.7799 | 22.4186 | 21.7604 | 22.7299 | 21.8368 | 22.3767 | 22.3967 | 22.3825 | 22.0648 | 21.2941 | 22.2629 | 21.5701 | 21.7465 | 21.8815 | 21.0739 | 21.1711 | 21.3946 | 20.4771 | 20.6249 | 20.9258 | 21.902 | 21.6625 | 21.3098 | 20.4485 | 20.5669 | 20.5315 | 22.0279 | 21.6455 | 21.1779 | 21.9972 | 21.73 | 21.3664 | 19.9509 | 20.5494 |  | 20.5771 | 20.2191 | 20.3376 | 19.2844 |  | 16.766 | 16.7515 | 16.4373 | 16.6024 | 16.6939 | 17.145 | 17.7192 | 15.4602 | 16.7736 | 15.697 | 16.9101 | 17.8539 | 44.7867 | 47.2075 | 44.1911 | 21.8524 |  |  | 0.3301 | -0.34111 | -32.8934 | 0.13927 | 0.23209 | -197.8558 | 16.666 | -0.18238 | -0.012361 | 0.059485 | -0.084426 | 8.8298 | 9.0595 | 1.9778 | 21.7983 | 22.0333 | 22.2345 | 22.2969 | 22.1384 | 21.4695 | 20.2958 | 22.2192 | 22.3943 | 22.4289 | 22.3825 | 22.0234 | 21.2721 | 22.3018 | 17.0911 | 17.0476 | 16.0398 | 16.1265 | 16.194 | 17.0894 | 16.765 | 22.386 | 22.1625 | 21.7273 | 22.0964 | 21.8086 | 21.3331 | 21.9584 | 21.5418 | 20.9315 | 20.1524 | 20.4627 | 20.0586 | 19.8125 | 0.078849 | -0.083086 | 20.7121 | 22.0927 | 22.4037 | 20.1086 | 21.6997 | 22.1442 | 21.9673 | 21.7366 | 21.3017 | 21.8072 | 21.479 | 21.075 | 20.5231 | 20.5559 | 20.4297 | 20.4576 | 20.118 |  | 20.2627 | 19.9381 | 20.126 | 19.6611 | 20.1109 | 20.3642 |  | 20.4546 |  |  | 20.291 | 20.3665 | 20.6344 | [5 empty] | 21.9651 | 20.3657 | 21.6967 | 22.0838 | 19.5833 | 21.2113 | 21.8462 | 19.3759 | 19.9477 | 21.222 |  | 19.8403 | 21.0012 | 18.8824 | 19.7243 | 20.8812 | 19.4375 | 20.2259 | 19.0754 | 20.2354 | 19.1597 | 20.3519 | 18.8235 | 20.1648 | 21.1172 | 19.3828 | 19.7517 | 21.0125 | 18.9171 | 19.7776 | 20.8289 | 18.9697 | 20.204 | 19.2424 | 19.9588 | 18.9029 | 20.1979 | -0.23238 | 20.947 | 0.048499 | 0.015413 | -26.9891 | 3.0981 | 10.38 | 0.52 | 0.68617 | -0.69301 | -6.8053 | 0.44281 | 0.57203 | -16.7017 | 4.8473 | 0.42426 | 0.42468 | 0.43187 | 0.40217 | 0.48113 | 0.43697 | 0.42905
42838.4138 | -562 | 22.8836 | 22.8577 | 22.8424 | 22.7783 | 22.4164 | 21.7567 | 22.7188 | 21.8288 | 22.3758 | 22.3826 | 22.3819 | 22.073 | 21.294 | 22.2511 | 21.569 | 21.7388 | 21.878 | 21.0745 | 21.1757 | 21.4011 | 20.4855 | 20.6264 | 20.924 | 21.9088 | 21.6704 | 21.317 | 20.4566 | 20.5778 | 20.5287 | 22.0253 | 21.6469 | 21.1767 | 21.9944 | 21.7385 | 21.3666 | 19.951 | 20.5456 |  | 20.5759 | 20.23 | 20.3347 | 19.275 |  | 16.7794 | 16.7609 | 16.4495 | 16.6214 | 16.7209 | 17.1848 | 17.7641 | 15.4535 | 16.7708 | 15.7228 | 16.9346 | 17.8587 | 44.7325 | 47.2317 | 44.1631 | 21.9108 |  |  | 0.31499 | -0.21757 | -32.9374 | 0.18066 | 0.14272 | -197.8414 | 16.4019 | -0.23495 | 0.01644 | -0.08297 | -0.051789 | 8.8284 | 9.0581 | 1.9785 | 21.8044 | 22.0351 | 22.2339 | 22.3023 | 22.1368 | 21.4754 | 20.3 | 22.2214 | 22.4031 | 22.4257 | 22.3863 | 22.0273 | 21.2716 | 22.3091 | 17.0844 | 17.0554 | 16.0388 | 16.1189 | 16.2221 | 17.0848 | 16.7631 | 22.3948 | 22.1669 | 21.7313 | 22.0958 | 21.8183 | 21.3276 | 21.9632 | 21.543 | 20.9336 | 20.1491 | 20.4786 | 20.0588 | 19.8253 | 0.0068932 | -0.12455 | 20.7211 | 22.0926 | 22.4121 | 20.1138 | 21.7054 | 22.1508 | 21.9642 | 21.737 | 21.2975 | 21.8081 | 21.4815 | 21.0763 | 20.5237 | 20.5572 | 20.4346 | 20.4594 | 20.1116 |  | 20.267 | 19.9466 | 20.132 | 19.6746 | 20.1175 | 20.3647 |  | 20.4526 |  |  | 20.2903 | 20.375 | 20.6374 | [5 empty] | 21.9621 | 20.3715 | 21.6964 | 22.0825 | 19.581 | 21.2111 | 21.8434 | 19.3799 | 19.9477 | 21.2238 |  | 19.8345 | 20.999 | 18.8746 | 19.726 | 20.8678 | 19.4455 | 20.2266 | 19.0761 | 20.2328 | 19.1617 | 20.3517 | 18.8288 | 20.1629 | 21.1186 | 19.3924 | 19.7587 | 21.0148 | 18.9171 | 19.7855 | 20.8278 | 18.9831 | 20.2132 | 19.2496 | 19.9565 | 18.9091 | 20.1935 | -0.29471 | 20.9473 | 0.048481 | 0.015464 | -27.0414 | 3.098 | 15.95 | -1.12 | 0.67027 | -0.55347 | -6.81 | 0.50435 | 0.44861 | -16.7023 | 4.8091 | 0.42458 | 0.42464 | 0.43171 | 0.40237 | 0.48102 | 0.43723 | 0.42859
42838.4138 | -561 | 22.8861 | 22.8545 | 22.8413 | 22.7729 | 22.4198 | 21.7581 | 22.7229 | 21.829 | 22.3752 | 22.39 | 22.3749 | 22.0641 | 21.2913 | 22.2529 | 21.5638 | 21.7425 | 21.8808 | 21.0766 | 21.1706 | 21.3934 | 20.4833 | 20.6242 | 20.9294 | 21.907 | 21.6734 | 21.3111 | 20.4524 | 20.571 | 20.5264 | 22.0186 | 21.6424 | 21.1821 | 21.9951 | 21.7348 | 21.3575 | 19.9479 | 20.5438 |  | 20.5753 | 20.2254 | 20.3332 | 19.2503 |  | 16.7802 | 16.7493 | 16.4426 | 16.6216 | 16.7317 | 17.1965 | 17.7875 | 15.4245 | 16.7789 | 15.7374 | 16.9241 | 17.8531 | 44.6908 | 47.2555 | 44.1421 | 21.5679 |  |  | 0.3715 | -0.33716 | -32.6273 | 0.23389 | 0.18741 | -197.8755 | 16.967 | -0.28161 | -0.0008796 | 0.062212 | -0.068975 | 8.828 | 9.0575 | 1.9791 | 21.7986 | 22.0303 | 22.2265 | 22.2882 | 22.122 | 21.4683 | 20.2911 | 22.2184 | 22.3931 | 22.4287 | 22.3807 | 22.0219 | 21.2648 | 22.3049 | 17.0786 | 17.083 | 16.0356 | 16.094 | 16.2172 | 17.0828 | 16.7575 | 22.3929 | 22.1662 | 21.7363 | 22.1059 | 21.8185 | 21.3308 | 21.9679 | 21.5512 | 20.9342 | 20.1629 | 20.473 | 20.0613 | 19.8368 | 0.1048 | 0.010302 | 20.7196 | 22.0909 | 22.4032 | 20.1155 | 21.6962 | 22.1491 | 21.9671 | 21.729 | 21.3022 | 21.8132 | 21.4755 | 21.0799 | 20.5126 | 20.5558 | 20.4321 | 20.4522 | 20.1125 |  | 20.2613 | 19.9472 | 20.1177 | 19.6709 | 20.1116 | 20.3602 |  | 20.4544 |  |  | 20.2953 | 20.3851 | 20.6339 | [5 empty] | 21.9643 | 20.3678 | 21.7056 | 22.0859 | 19.5846 | 21.2199 | 21.8492 | 19.3701 | 19.9519 | 21.2202 |  | 19.824 | 20.9967 | 18.8714 | 19.7191 | 20.8723 | 19.4338 | 20.2306 | 19.0749 | 20.2221 | 19.1545 | 20.3523 | 18.8257 | 20.167 | 21.1215 | 19.3881 | 19.7519 | 21.0195 | 18.9196 | 19.782 | 20.824 | 18.9816 | 20.2023 | 19.2455 | 19.9692 | 18.9182 | 20.1993 | -0.4073 | 20.9468 | 0.04845 | 0.015979 | -26.9533 | 3.098 | 5.13 | 0.56 | 0.72792 | -0.68899 | -6.7777 | 0.57385 | 0.51407 | -16.704 | 4.8913 | 0.42437 | 0.42415 | 0.43162 | 0.40279 | 0.48073 | 0.43782 | 0.42873
42838.4138 | -560 | 22.8835 | 22.8546 | 22.846 | 22.773 | 22.4138 | 21.7646 | 22.7194 | 21.8312 | 22.373 | 22.3878 | 22.3742 | 22.067 | 21.2865 | 22.2536 | 21.5572 | 21.7393 | 21.8762 | 21.0786 | 21.1645 | 21.3873 | 20.4745 | 20.6179 | 20.9294 | 21.9002 | 21.6668 | 21.3042 | 20.4453 | 20.5672 | 20.5235 | 22.0211 | 21.6356 | 21.1697 | 21.9898 | 21.7266 | 21.3506 | 19.9421 | 20.5428 |  | 20.5707 | 20.2221 | 20.3244 | 19.2322 |  | 16.7769 | 16.7458 | 16.4391 | 16.6307 | 16.7376 | 17.223 | 17.8115 | 15.4069 | 16.7633 | 15.7783 | 16.9278 | 17.8604 | 44.6602 | 47.2852 | 44.1275 | 21.551 |  |  | 0.4451 | -0.29314 | -32.4814 | 0.5861 | 0.22421 | -197.8499 | 16.5129 | -0.06016 | 0.14604 | -0.026953 | -0.055261 | 8.8284 | 9.0584 | 1.9785 | 21.7973 | 22.0267 | 22.2262 | 22.2878 | 22.1281 | 21.4659 | 20.2899 | 22.2261 | 22.3909 | 22.4215 | 22.3793 | 22.0202 | 21.266 | 22.3032 | 17.0688 | 17.108 | 16.0166 | 16.0646 | 16.2028 | 17.0854 | 16.752 | 22.3959 | 22.1723 | 21.7422 | 22.1007 | 21.8204 | 21.338 | 21.9659 | 21.5556 | 20.9421 | 20.1619 | 20.4762 | 20.0688 | 19.8441 | 0.15592 | -0.059882 | 20.7266 | 22.0912 | 22.4019 | 20.1111 | 21.7038 | 22.1474 | 21.9706 | 21.7303 | 21.3069 | 21.8126 | 21.4789 | 21.076 | 20.5179 | 20.5543 | 20.422 | 20.4535 | 20.1186 |  | 20.2744 | 19.952 | 20.131 | 19.6752 | 20.1151 | 20.3638 |  | 20.4602 |  |  | 20.2973 | 20.3728 | 20.6399 | [5 empty] | 21.9621 | 20.3694 | 21.7005 | 22.0935 | 19.5882 | 21.2153 | 21.8415 | 19.376 | 19.9378 | 21.2221 |  | 19.8372 | 20.9971 | 18.8779 | 19.7237 | 20.8699 | 19.4483 | 20.2253 | 19.0783 | 20.2388 | 19.1515 | 20.3592 | 18.8256 | 20.17 | 21.1242 | 19.3836 | 19.7563 | 21.0257 | 18.9321 | 19.783 | 20.8306 | 18.9747 | 20.2183 | 19.2498 | 19.9636 | 18.9118 | 20.2101 | -0.24518 | 20.9459 | 0.04775 | 0.015355 | -26.9768 | 3.098 | -8.86 | 0.18 | 0.79676 | -0.64243 | -6.7625 | 0.90839 | 0.5623 | -16.7037 | 4.8257 | 0.42464 | 0.42446 | 0.43162 | 0.40418 | 0.4822 | 0.43813 | 0.42849
42838.4138 | -559 | 22.8798 | 22.8468 | 22.845 | 22.7733 | 22.4141 | 21.7616 | 22.7149 | 21.8271 | 22.3773 | 22.3821 | 22.3746 | 22.0686 | 21.2892 | 22.2496 | 21.5554 | 21.7434 | 21.8815 | 21.0797 | 21.1725 | 21.3861 | 20.4806 | 20.6236 | 20.9286 | 21.9023 | 21.6753 | 21.3107 | 20.4513 | 20.5611 | 20.5265 | 22.0211 | 21.6404 | 21.1682 | 21.9858 | 21.7291 | 21.3576 | 19.9431 | 20.5434 |  | 20.5738 | 20.222 | 20.3247 | 19.2221 |  | 16.7788 | 16.7437 | 16.4399 | 16.6295 | 16.7359 | 17.2467 | 17.839 | 15.403 | 16.7712 | 15.8734 | 16.9267 | 17.852 | 44.6347 | 47.3071 | 44.1217 | 21.551 |  |  | 0.48584 | -0.16434 | -32.5274 | 0.54208 | 0.12104 | -197.848 | 16.6417 | -0.098928 | 0.01391 | 0.16103 | 0.020776 | 8.8291 | 9.0588 | 1.9782 | 21.7911 | 22.0361 | 22.2225 | 22.2917 | 22.1307 | 21.4558 | 20.2886 | 22.2336 | 22.3921 | 22.4277 | 22.3735 | 22.0215 | 21.2621 | 22.2988 | 17.0542 | 17.097 | 15.9651 | 16.0527 | 16.1998 | 17.0796 | 16.7531 | 22.3835 | 22.1654 | 21.7264 | 22.0969 | 21.8171 | 21.3284 | 21.9597 | 21.5388 | 20.9286 | 20.1469 | 20.4689 | 20.065 | 19.8401 | -0.039111 | -0.018609 | 20.7307 | 22.0951 | 22.3971 | 20.1161 | 21.7057 | 22.1498 | 21.9671 | 21.7347 | 21.3052 | 21.8153 | 21.48 | 21.077 | 20.5197 | 20.5504 | 20.4263 | 20.455 | 20.1151 |  | 20.2603 | 19.9428 | 20.1195 | 19.6411 | 20.1028 | 20.3544 |  | 20.4447 |  |  | 20.3061 | 20.3845 | 20.6463 | [5 empty] | 21.9619 | 20.3735 | 21.6997 | 22.0874 | 19.5871 | 21.2244 | 21.8483 | 19.3694 | 19.9425 | 21.2154 |  | 19.8296 | 21.0044 | 18.8804 | 19.7221 | 20.8762 | 19.4385 | 20.2292 | 19.0778 | 20.2306 | 19.1481 | 20.3574 | 18.8203 | 20.1587 | 21.1215 | 19.3789 | 19.7439 | 21.0154 | 18.9263 | 19.7841 | 20.8342 | 18.9697 | 20.2122 | 19.2471 | 19.9669 | 18.9048 | 20.1975 | -0.27282 | 20.9476 | 0.047516 | 0.013475 | -27.0056 | 3.098 | 6.18 | -0.12 | 0.83243 | -0.48102 | -6.7672 | 0.87361 | 0.41317 | -16.7043 | 4.8446 | 0.42426 | 0.42433 | 0.43215 | 0.40511 | 0.48804 | 0.43844 | 0.4281
42838.4138 | -558 | 22.881 | 22.8491 | 22.844 | 22.7776 | 22.42 | 21.7579 | 22.7209 | 21.8269 | 22.3755 | 22.3855 | 22.3799 | 22.0674 | 21.2905 | 22.2503 | 21.5501 | 21.7375 | 21.8751 | 21.0696 | 21.1667 | 21.3886 | 20.4756 | 20.6241 | 20.9176 | 21.9057 | 21.6724 | 21.3101 | 20.4513 | 20.5633 | 20.5219 | 22.0237 | 21.6488 | 21.1722 | 21.9941 | 21.7329 | 21.3597 | 19.9508 | 20.5516 |  | 20.5815 | 20.2312 | 20.3376 | 19.2107 |  | 16.7832 | 16.756 | 16.4448 | 16.6274 | 16.7556 | 17.2708 | 17.8722 | 15.4158 | 16.7739 | 15.9254 | 16.961 | 17.8554 | 44.6141 | 47.3323 | 44.119 | 21.6022 |  |  | 0.31762 | -0.45544 | -32.7889 | 0.3226 | 0.61322 | -197.8617 | 16.6338 | -0.062128 | 0.20364 | 0.12725 | -0.1714 | 8.8302 | 9.0599 | 1.9782 | 21.7906 | 22.0242 | 22.2252 | 22.2854 | 22.1352 | 21.4609 | 20.2891 | 22.224 | 22.3909 | 22.4258 | 22.3752 | 22.0262 | 21.2736 | 22.3011 | 17.0385 | 17.0981 | 15.9422 | 16.0728 | 16.2073 | 17.0895 | 16.7554 | 22.3891 | 22.1633 | 21.7261 | 22.0973 | 21.8117 | 21.3258 | 21.9627 | 21.5524 | 20.9346 | 20.1521 | 20.473 | 20.0628 | 19.8463 | -0.02358 | -0.020511 | 20.7407 | 22.099 | 22.4099 | 20.1235 | 21.7061 | 22.1557 | 21.9684 | 21.7393 | 21.3086 | 21.8175 | 21.4847 | 21.0845 | 20.5262 | 20.5557 | 20.4346 | 20.4655 | 20.1143 |  | 20.2669 | 19.9574 | 20.126 | 19.6615 | 20.1233 | 20.3627 |  | 20.4556 |  |  | 20.3072 | 20.3814 | 20.6412 | [5 empty] | 21.9688 | 20.3667 | 21.7069 | 22.0876 | 19.589 | 21.2097 | 21.8433 | 19.3823 | 19.9448 | 21.2138 |  | 19.8241 | 20.9932 | 18.8823 | 19.731 | 20.8773 | 19.4418 | 20.2357 | 19.0792 | 20.2356 | 19.1475 | 20.3582 | 18.8151 | 20.1534 | 21.1188 | 19.3838 | 19.7442 | 21.003 | 18.9205 | 19.7926 | 20.8295 | 18.9755 | 20.203 | 19.2406 | 19.961 | 18.9005 | 20.191 | 0.063123 | 20.9477 | 0.046109 | 0.01264 | -27.0703 | 3.098 | -4.22 | -0.26 | 0.67306 | -0.80078 | -6.7945 | 0.67395 | 0.93001 | -16.7056 | 4.8437 | 0.4245 | 0.42414 | 0.43227 | 0.40802 | 0.49086 | 0.43902 | 0.4281
42838.4138 | -557 | 22.8858 | 22.8503 | 22.8391 | 22.7741 | 22.4208 | 21.766 | 22.7166 | 21.8286 | 22.3729 | 22.3894 | 22.3775 | 22.0697 | 21.2871 | 22.2571 | 21.5558 | 21.7434 | 21.8796 | 21.0749 | 21.1683 | 21.3966 | 20.4752 | 20.6248 | 20.9254 | 21.9009 | 21.667 | 21.3138 | 20.4552 | 20.5627 | 20.5234 | 22.0246 | 21.6443 | 21.1806 | 21.9954 | 21.7389 | 21.3699 | 19.9505 | 20.555 |  | 20.5834 | 20.2271 | 20.34 | 19.19 |  | 16.7688 | 16.7455 | 16.4457 | 16.6369 | 16.7615 | 17.2782 | 17.8876 | 15.449 | 16.7808 | 16.0272 | 16.9296 | 17.8616 | 44.6031 | 47.3589 | 44.1082 | 21.4197 |  |  | 0.40041 | -0.20903 | -31.9051 | 0.36531 | 0.054016 | -197.8263 | 16.9184 | 0.00358 | 0.083188 | -0.20109 | 0.088827 | 8.8288 | 9.0585 | 1.9782 | 21.7955 | 22.0264 | 22.2265 | 22.2948 | 22.1274 | 21.4672 | 20.295 | 22.2177 | 22.3969 | 22.4239 | 22.3805 | 22.0201 | 21.2671 | 22.2939 | 17.0255 | 17.1012 | 15.9262 | 16.0947 | 16.2028 | 17.0795 | 16.7541 | 22.3868 | 22.1691 | 21.73 | 22.099 | 21.817 | 21.3254 | 21.9556 | 21.5461 | 20.9308 | 20.1522 | 20.4658 | 20.0586 | 19.8429 | 0.17852 | 0.021524 | 20.7425 | 22.0915 | 22.4003 | 20.1215 | 21.6977 | 22.1498 | 21.969 | 21.7345 | 21.3061 | 21.8118 | 21.4784 | 21.0794 | 20.5166 | 20.5521 | 20.4321 | 20.4661 | 20.0977 |  | 20.2609 | 19.9478 | 20.1235 | 19.6584 | 20.1051 | 20.3503 |  | 20.4411 |  |  | 20.3008 | 20.3871 | 20.6334 | [5 empty] | 21.9699 | 20.3756 | 21.705 | 22.0869 | 19.5871 | 21.2083 | 21.8519 | 19.3721 | 19.9309 | 21.2145 |  | 19.8229 | 20.9894 | 18.8807 | 19.7202 | 20.8717 | 19.4432 | 20.2295 | 19.0765 | 20.2383 | 19.145 | 20.3514 | 18.815 | 20.1621 | 21.1159 | 19.389 | 19.7496 | 21.015 | 18.9263 | 19.7926 | 20.834 | 18.981 | 20.2091 | 19.2441 | 19.9595 | 18.9016 | 20.1995 | -0.069695 | 20.9475 | 0.045919 | 0.012814 | -27.1022 | 3.098 | -7.42 | -0.18 | 0.75571 | -0.54249 | -6.7022 | 0.71717 | 0.27602 | -16.7043 | 4.885 | 0.42476 | 0.42432 | 0.43175 | 0.4083 | 0.49248 | 0.43958 | 0.4282
42838.4138 | -556 | 22.8795 | 22.8518 | 22.8361 | 22.7666 | 22.4217 | 21.7603 | 22.7194 | 21.8248 | 22.376 | 22.3848 | 22.3711 | 22.0591 | 21.2912 | 22.2462 | 21.5604 | 21.7405 | 21.8788 | 21.074 | 21.1673 | 21.3943 | 20.4794 | 20.6251 | 20.9245 | 21.8988 | 21.6675 | 21.3146 | 20.451 | 20.5649 | 20.5191 | 22.0266 | 21.645 | 21.1776 | 21.9962 | 21.7381 | 21.3625 | 19.949 | 20.548 |  | 20.5731 | 20.2329 | 20.3333 | 19.1614 |  | 16.7629 | 16.737 | 16.4441 | 16.6368 | 16.7721 | 17.3066 | 17.92 | 15.4576 | 16.7799 | 16.0456 | 16.9399 | 17.8528 | 44.601 | 47.3768 | 44.0946 | 21.3946 |  |  | 0.34456 | -0.23597 | -30.4903 | 0.15241 | 0.16375 | -197.8532 | 17.3475 | -0.043072 | -0.1046 | -0.20738 | 0.056885 | 8.8298 | 9.0595 | 1.979 | 21.7929 | 22.0282 | 22.2234 | 22.294 | 22.1235 | 21.4654 | 20.2875 | 22.2086 | 22.3979 | 22.429 | 22.3751 | 22.0203 | 21.2627 | 22.2958 | 17.0277 | 17.0737 | 15.9322 | 16.1172 | 16.2249 | 17.0948 | 16.7548 | 22.3853 | 22.1629 | 21.7281 | 22.1003 | 21.8223 | 21.3181 | 21.9609 | 21.5474 | 20.9312 | 20.1508 | 20.4678 | 20.0654 | 19.8445 | 0.14156 | -0.085559 | 20.7468 | 22.0865 | 22.3991 | 20.1203 | 21.6947 | 22.1531 | 21.9658 | 21.7346 | 21.3024 | 21.8083 | 21.478 | 21.071 | 20.5149 | 20.5549 | 20.4324 | 20.459 | 20.0924 |  | 20.2636 | 19.9598 | 20.1245 | 19.667 | 20.1087 | 20.3603 |  | 20.4465 |  |  | 20.3049 | 20.3862 | 20.6249 | [5 empty] | 21.9621 | 20.3735 | 21.6982 | 22.088 | 19.584 | 21.2042 | 21.8478 | 19.362 | 19.9233 | 21.2098 |  | 19.8324 | 20.9902 | 18.8819 | 19.7158 | 20.8679 | 19.447 | 20.2278 | 19.0726 | 20.2368 | 19.1429 | 20.3452 | 18.8154 | 20.1603 | 21.1154 | 19.3974 | 19.7489 | 21.0138 | 18.9321 | 19.7851 | 20.8308 | 18.9736 | 20.2093 | 19.2518 | 19.9804 | 18.9071 | 20.207 | -0.19806 | 20.9487 | 0.047012 | 0.012792 | -26.9917 | 3.098 | 13.54 | -0.53 | 0.70101 | -0.57638 | -6.5518 | 0.46321 | 0.48062 | -16.7063 | 4.9468 | 0.425 | 0.42402 | 0.43163 | 0.40985 | 0.4919 | 0.44032 | 0.42811
42838.4139 | -555 | 22.8848 | 22.8625 | 22.8385 | 22.7761 | 22.4176 | 21.7608 | 22.7144 | 21.8311 | 22.3761 | 22.3945 | 22.3855 | 22.0612 | 21.2957 | 22.2604 | 21.5648 | 21.7434 | 21.8833 | 21.0734 | 21.1712 | 21.3954 | 20.4806 | 20.6233 | 20.9252 | 21.9041 | 21.6721 | 21.3126 | 20.4543 | 20.565 | 20.5199 | 22.0144 | 21.647 | 21.1726 | 21.9849 | 21.7315 | 21.3527 | 19.9441 | 20.547 |  | 20.5772 | 20.2273 | 20.3172 | 19.1359 |  | 16.7573 | 16.7229 | 16.4194 | 16.6243 | 16.754 | 17.3064 | 17.936 | 15.4465 | 16.7811 | 16.0515 | 16.9366 | 17.8537 | 44.6149 | 47.4038 | 44.0812 | 21.3903 |  |  | 0.46284 | -0.4975 | -30.5192 | 0.14781 | 0.16967 | -197.8374 | 17.4342 | -0.052272 | 0.13125 | -0.25773 | -0.027832 | 8.8279 | 9.0576 | 1.979 | 21.7982 | 22.0317 | 22.2245 | 22.2889 | 22.1284 | 21.4703 | 20.2879 | 22.2179 | 22.3922 | 22.4345 | 22.3818 | 22.0207 | 21.2648 | 22.3003 | 17.006 | 17.0754 | 15.937 | 16.1156 | 16.2374 | 17.0764 | 16.7479 | 22.388 | 22.1638 | 21.7288 | 22.0975 | 21.8193 | 21.3243 | 21.9622 | 21.5506 | 20.9401 | 20.1534 | 20.4738 | 20.0572 | 19.8366 | 0.20507 | -0.12759 | 20.7548 | 22.0962 | 22.4141 | 20.1251 | 21.6989 | 22.1565 | 21.9764 | 21.7413 | 21.309 | 21.8121 | 21.4772 | 21.0815 | 20.5202 | 20.564 | 20.4406 | 20.4711 | 20.096 |  | 20.2667 | 19.9675 | 20.1257 | 19.6773 | 20.1125 | 20.3575 |  | 20.4501 |  |  | 20.306 | 20.3853 | 20.6211 | [5 empty] | 21.9584 | 20.3704 | 21.6996 | 22.0895 | 19.5834 | 21.206 | 21.8416 | 19.363 | 19.9285 | 21.212 |  | 19.8268 | 20.993 | 18.8809 | 19.7138 | 20.8714 | 19.4471 | 20.2288 | 19.0835 | 20.2402 | 19.1475 | 20.3483 | 18.8145 | 20.1568 | 21.1099 | 19.3933 | 19.7511 | 21.0087 | 18.9265 | 19.7864 | 20.8343 | 18.9701 | 20.2133 | 19.2529 | 19.9804 | 18.9074 | 20.2098 | -0.24407 | 20.9463 | 0.048045 | 0.012553 | -27.0454 | 3.0981 | 1.2 | 0.23 | 0.81248 | -0.83689 | -6.5548 | 0.45616 | 0.48922 | -16.7056 | 4.9592 | 0.42501 | 0.42385 | 0.43147 | 0.4101 | 0.49056 | 0.44087 | 0.42842
42838.4139 | -554 | 22.8832 | 22.8563 | 22.8437 | 22.777 | 22.4153 | 21.7651 | 22.719 | 21.8292 | 22.3743 | 22.3916 | 22.3793 | 22.0542 | 21.2874 | 22.2478 | 21.5718 | 21.7482 | 21.8898 | 21.0749 | 21.1753 | 21.4 | 20.4836 | 20.6285 | 20.9341 | 21.909 | 21.6717 | 21.3148 | 20.4623 | 20.5695 | 20.5227 | 22.0168 | 21.6409 | 21.1701 | 21.9844 | 21.7303 | 21.3577 | 19.9438 | 20.5457 |  | 20.5748 | 20.2296 | 20.3248 | 19.1182 |  | 16.7523 | 16.7236 | 16.4228 | 16.6204 | 16.7504 | 17.3033 | 17.959 | 15.4507 | 16.7834 | 16.0655 | 16.9441 | 17.8564 | 44.6165 | 47.4287 | 44.0707 | 21.3948 |  |  | 0.38793 | -0.43113 | -30.5711 | 0.41854 | 0.1447 | -197.8558 | 17.5669 | -0.065416 | 0.2089 | -0.069752 | 0.11799 | 8.829 | 9.0585 | 1.9787 | 21.7973 | 22.0292 | 22.219 | 22.2867 | 22.123 | 21.4597 | 20.2866 | 22.2162 | 22.3859 | 22.427 | 22.3777 | 22.0192 | 21.2692 | 22.2935 | 17.0069 | 17.0832 | 15.983 | 16.1401 | 16.2433 | 17.0875 | 16.756 | 22.3839 | 22.1576 | 21.7231 | 22.0835 | 21.8119 | 21.3297 | 21.9515 | 21.5407 | 20.9275 | 20.1481 | 20.4587 | 20.0574 | 19.8399 | 0.097526 | -0.10325 | 20.7504 | 22.0983 | 22.4018 | 20.1245 | 21.6913 | 22.1493 | 21.9653 | 21.7293 | 21.2986 | 21.8123 | 21.4736 | 21.0788 | 20.5108 | 20.5614 | 20.4368 | 20.4751 | 20.0974 |  | 20.2685 | 19.9772 | 20.1294 | 19.6764 | 20.1184 | 20.3638 |  | 20.4587 |  |  | 20.3047 | 20.3862 | 20.6252 | [5 empty] | 21.9637 | 20.3732 | 21.6987 | 22.0894 | 19.5848 | 21.209 | 21.842 | 19.3623 | 19.9301 | 21.2095 |  | 19.8286 | 20.9963 | 18.882 | 19.7149 | 20.8679 | 19.4508 | 20.227 | 19.0889 | 20.2376 | 19.1473 | 20.3492 | 18.8114 | 20.161 | 21.1131 | 19.3903 | 19.7529 | 21.0078 | 18.9257 | 19.7849 | 20.8333 | 18.9714 | 20.2095 | 19.251 | 19.972 | 18.9013 | 20.2032 | -0.1413 | 20.9464 | 0.047909 | 0.013656 | -27.07 | 3.098 | 4.25 | 0.51 | 0.74383 | -0.77907 | -6.5604 | 0.76761 | 0.45179 | -16.7063 | 4.978 | 0.42503 | 0.42371 | 0.43169 | 0.4113 | 0.48639 | 0.44135 | 0.42814
42838.4139 | -553 | 22.8907 | 22.8649 | 22.8459 | 22.7801 | 22.4186 | 21.765 | 22.7253 | 21.835 | 22.3783 | 22.3943 | 22.3845 | 22.0684 | 21.2979 | 22.2557 | 21.5612 | 21.742 | 21.883 | 21.0735 | 21.1747 | 21.4026 | 20.4794 | 20.6233 | 20.9317 | 21.9053 | 21.6706 | 21.3113 | 20.4532 | 20.5581 | 20.5219 | 22.0254 | 21.6433 | 21.1754 | 21.9949 | 21.7328 | 21.3639 | 19.9468 | 20.5531 |  | 20.5805 | 20.2302 | 20.3226 | 19.1154 |  | 16.7347 | 16.7052 | 16.4062 | 16.6062 | 16.728 | 17.2803 | 17.9324 | 15.4311 | 16.7704 | 16.0727 | 16.9286 | 17.8572 | 44.6123 | 47.4572 | 44.0552 | 21.3943 |  |  | 0.48913 | -0.41405 | -30.4831 | 0.33049 | 0.090156 | -197.8434 | 17.5525 | -0.14296 | 0.21201 | -0.17067 | 0.07737 | 8.8292 | 9.0589 | 1.9785 | 21.7957 | 22.0239 | 22.2277 | 22.2953 | 22.1233 | 21.4641 | 20.2932 | 22.2254 | 22.3931 | 22.4269 | 22.3833 | 22.0259 | 21.2646 | 22.2978 | 16.9931 | 17.0755 | 16.0128 | 16.1705 | 16.275 | 17.0859 | 16.7556 | 22.3874 | 22.1678 | 21.7266 | 22.1013 | 21.8112 | 21.3247 | 21.9588 | 21.552 | 20.928 | 20.1454 | 20.4764 | 20.061 | 19.8502 | -0.042257 | -0.13577 | 20.761 | 22.0968 | 22.4124 | 20.1389 | 21.7052 | 22.1572 | 21.9698 | 21.7463 | 21.3105 | 21.815 | 21.4877 | 21.0798 | 20.522 | 20.5583 | 20.4432 | 20.4748 | 20.0953 |  | 20.2672 | 19.9773 | 20.1247 | 19.6647 | 20.1133 | 20.3592 |  | 20.4532 |  |  | 20.3029 | 20.3907 | 20.6195 | [5 empty] | 21.9584 | 20.3755 | 21.6963 | 22.0835 | 19.5814 | 21.2165 | 21.8482 | 19.361 | 19.9281 | 21.2076 |  | 19.82 | 20.9913 | 18.8828 | 19.7144 | 20.8696 | 19.4519 | 20.2334 | 19.0855 | 20.2419 | 19.1408 | 20.352 | 18.8116 | 20.1647 | 21.1183 | 19.3954 | 19.7608 | 21.0085 | 18.9342 | 19.7841 | 20.8335 | 18.968 | 20.2085 | 19.2494 | 19.9871 | 18.9018 | 20.2012 | -0.089914 | 20.9476 | 0.048008 | 0.013656 | -27.0423 | 3.0981 | 19.31 | -0.52 | 0.83523 | -0.76345 | -6.5507 | 0.68208 | 0.3566 | -16.7051 | 4.9757 | 0.42504 | 0.42355 | 0.43185 | 0.41265 | 0.48304 | 0.44153 | 0.42777
42838.4139 | -552 | 22.8897 | 22.8512 | 22.843 | 22.7684 | 22.4133 | 21.7567 | 22.7217 | 21.8298 | 22.379 | 22.3825 | 22.3773 | 22.0599 | 21.2921 | 22.2507 | 21.5612 | 21.747 | 21.883 | 21.0752 | 21.181 | 21.4026 | 20.4828 | 20.6345 | 20.9299 | 21.9082 | 21.6781 | 21.3192 | 20.452 | 20.5627 | 20.5263 | 22.0238 | 21.6423 | 21.1737 | 21.9899 | 21.7368 | 21.3588 | 19.9449 | 20.5502 |  | 20.5828 | 20.2311 | 20.316 | 19.0881 |  | 16.7312 | 16.6951 | 16.3994 | 16.5938 | 16.7218 | 17.259 | 17.903 | 15.4371 | 16.7771 | 16.0662 | 16.9352 | 17.8577 | 44.6142 | 47.4839 | 44.0402 | 21.3997 |  |  | 0.39844 | -0.29971 | -30.1335 | 0.48491 | 0.27086 | -197.8269 | 17.5926 | -0.18238 | 0.22544 | 0.19564 | 0.032234 | 8.8296 | 9.0593 | 1.9782 | 21.7982 | 22.0225 | 22.2249 | 22.2923 | 22.1225 | 21.4694 | 20.2902 | 22.2146 | 22.3848 | 22.4185 | 22.3731 | 22.0217 | 21.2662 | 22.3054 | 16.9864 | 17.076 | 16.0175 | 16.184 | 16.2891 | 17.0903 | 16.7491 | 22.3882 | 22.1633 | 21.7355 | 22.0936 | 21.819 | 21.3286 | 21.957 | 21.5527 | 20.9338 | 20.151 | 20.4766 | 20.0702 | 19.8601 | 0.10087 | -0.033064 | 20.7623 | 22.0981 | 22.399 | 20.1336 | 21.6995 | 22.1517 | 21.9708 | 21.7396 | 21.3054 | 21.8033 | 21.482 | 21.0707 | 20.5164 | 20.5527 | 20.4354 | 20.4783 | 20.0872 |  | 20.2692 | 19.9726 | 20.1282 | 19.6511 | 20.1077 | 20.3572 |  | 20.4535 |  |  | 20.3037 | 20.3893 | 20.6237 | [5 empty] | 21.9575 | 20.3752 | 21.6943 | 22.0819 | 19.5859 | 21.2145 | 21.8445 | 19.3523 | 19.9254 | 21.2034 |  | 19.8179 | 20.9887 | 18.8859 | 19.7077 | 20.8685 | 19.4513 | 20.2272 | 19.0807 | 20.2434 | 19.1338 | 20.3488 | 18.806 | 20.1603 | 21.1116 | 19.3971 | 19.7665 | 21.0123 | 18.9335 | 19.7832 | 20.8373 | 18.9708 | 20.2087 | 19.2511 | 19.9898 | 18.9066 | 20.2079 | -0.30027 | 20.9482 | 0.047682 | 0.011994 | -27.0093 | 3.0981 | 21.96 | 0.38 | 0.75385 | -0.64953 | -6.5129 | 0.82619 | 0.61808 | -16.7038 | 4.9812 | 0.42533 | 0.42379 | 0.43204 | 0.41391 | 0.48176 | 0.44222 | 0.42768
42838.4139 | -551 | 22.8829 | 22.8497 | 22.8331 | 22.7696 | 22.4061 | 21.7518 | 22.7204 | 21.8212 | 22.3685 | 22.3803 | 22.3676 | 22.0564 | 21.2848 | 22.2554 | 21.5677 | 21.7451 | 21.8797 | 21.0786 | 21.1779 | 21.4005 | 20.481 | 20.6383 | 20.9294 | 21.9157 | 21.6783 | 21.3166 | 20.456 | 20.5656 | 20.525 | 22.0228 | 21.6424 | 21.1712 | 21.9865 | 21.7363 | 21.3575 | 19.9481 | 20.5467 |  | 20.5768 | 20.2254 | 20.3091 | 19.0768 |  | 16.7284 | 16.6954 | 16.3966 | 16.5896 | 16.7155 | 17.2438 | 17.8778 | 15.4545 | 16.7838 | 16.0435 | 16.9369 | 17.857 | 44.6045 | 47.518 | 44.0225 | 21.3974 |  |  | 0.32222 | -0.19063 | -29.8818 | 0.47768 | 0.13024 | -197.8355 | 17.699 | -0.033216 | 0.24665 | 0.093262 | 0.17285 | 8.8285 | 9.0583 | 1.9787 | 21.7866 | 22.0208 | 22.222 | 22.288 | 22.1171 | 21.4658 | 20.2765 | 22.2108 | 22.3874 | 22.4243 | 22.3805 | 22.0155 | 21.2584 | 22.303 | 16.982 | 17.0801 | 16.0092 | 16.2028 | 16.3136 | 17.0868 | 16.7533 | 22.3917 | 22.1639 | 21.7318 | 22.0965 | 21.8213 | 21.3252 | 21.959 | 21.5491 | 20.9368 | 20.1457 | 20.4829 | 20.0694 | 19.8617 | 0.017903 | 0.096082 | 20.757 | 22.0886 | 22.3969 | 20.1299 | 21.6892 | 22.1394 | 21.9631 | 21.725 | 21.2935 | 21.7927 | 21.4691 | 21.0706 | 20.5102 | 20.552 | 20.4301 | 20.4673 | 20.0849 |  | 20.26 | 19.9718 | 20.1259 | 19.649 | 20.1043 | 20.3533 |  | 20.4467 |  |  | 20.3131 | 20.3955 | 20.6257 | [5 empty] | 21.9643 | 20.3719 | 21.6971 | 22.0841 | 19.59 | 21.2103 | 21.8432 | 19.3499 | 19.9277 | 21.2053 |  | 19.8166 | 20.9923 | 18.8807 | 19.7067 | 20.8701 | 19.4548 | 20.2256 | 19.0804 | 20.2469 | 19.1357 | 20.3568 | 18.7947 | 20.1528 | 21.1087 | 19.3929 | 19.7594 | 21.0142 | 18.9266 | 19.782 | 20.8362 | 18.9655 | 20.1976 | 19.2441 | 19.9746 | 18.9012 | 20.2 | -0.045766 | 20.9463 | 0.047571 | 0.011362 | -26.9911 | 3.098 | 17.48 | -0.18 | 0.67792 | -0.51802 | -6.4857 | 0.82001 | 0.42858 | -16.7037 | 4.9961 | 0.42509 | 0.42374 | 0.43198 | 0.41398 | 0.48317 | 0.44265 | 0.42746
42838.4139 | -550 | 22.882 | 22.8519 | 22.8369 | 22.7714 | 22.4095 | 21.7532 | 22.7165 | 21.8224 | 22.3721 | 22.3821 | 22.3746 | 22.0625 | 21.2874 | 22.2582 | 21.568 | 21.7421 | 21.8798 | 21.0758 | 21.1732 | 21.3931 | 20.4752 | 20.6232 | 20.9241 | 21.9065 | 21.6678 | 21.3134 | 20.4489 | 20.5632 | 20.5229 | 22.0107 | 21.6426 | 21.169 | 21.9844 | 21.7276 | 21.3549 | 19.9402 | 20.5343 |  | 20.5735 | 20.2226 | 20.3098 | 19.0678 |  | 16.7188 | 16.6941 | 16.3924 | 16.5809 | 16.7031 | 17.2399 | 17.8556 | 15.4795 | 16.7897 | 16.0199 | 16.9446 | 17.8563 | 44.6037 | 47.5564 | 44.0297 | 21.3999 |  |  | 0.35901 | -0.17946 | -30.5777 | 0.047926 | 0.12498 | -197.8309 | 17.3113 | -0.1147 | -0.018199 | -0.39536 | -0.063246 | 8.8284 | 9.058 | 1.9792 | 21.7885 | 22.0308 | 22.2223 | 22.286 | 22.1299 | 21.4601 | 20.289 | 22.2165 | 22.3868 | 22.4263 | 22.3758 | 22.0228 | 21.2673 | 22.3055 | 16.9687 | 17.0821 | 16.0109 | 16.2161 | 16.3261 | 17.0887 | 16.751 | 22.3823 | 22.1655 | 21.7282 | 22.0954 | 21.8213 | 21.3235 | 21.9556 | 21.5512 | 20.9394 | 20.1446 | 20.4809 | 20.0646 | 19.8534 | 0.0023714 | 0.015818 | 20.7598 | 22.0934 | 22.3972 | 20.1275 | 21.6905 | 22.1464 | 21.9634 | 21.7269 | 21.3055 | 21.806 | 21.4777 | 21.0762 | 20.5168 | 20.5516 | 20.4363 | 20.472 | 20.0839 |  | 20.2657 | 19.9672 | 20.1275 | 19.6448 | 20.1141 | 20.3546 |  | 20.4566 |  |  | 20.3225 | 20.4021 | 20.628 | [5 empty] | 21.9686 | 20.379 | 21.6984 | 22.0845 | 19.5885 | 21.2198 | 21.8513 | 19.3522 | 19.9159 | 21.1968 |  | 19.8117 | 20.9914 | 18.8763 | 19.7022 | 20.8683 | 19.4532 | 20.2313 | 19.0762 | 20.2397 | 19.1359 | 20.3511 | 18.7844 | 20.1448 | 21.0997 | 19.3874 | 19.7547 | 21.0034 | 18.9192 | 19.7774 | 20.8262 | 18.9561 | 20.1942 | 19.2388 | 19.966 | 18.8919 | 20.1885 | -0.18285 | 20.9458 | 0.047479 | 0.011769 | -26.9915 | 3.0981 | 8.77 | 0.09 | 0.71557 | -0.50261 | -6.5607 | 0.25974 | 0.41984 | -16.7034 | 4.9411 | 0.42531 | 0.42392 | 0.43243 | 0.41569 | 0.48271 | 0.44263 | 0.42765
42838.4139 | -549 | 22.8961 | 22.8552 | 22.8507 | 22.7847 | 22.423 | 21.7684 | 22.7235 | 21.8395 | 22.3851 | 22.3916 | 22.3839 | 22.0634 | 21.2977 | 22.2638 | 21.5551 | 21.7382 | 21.8758 | 21.0712 | 21.1638 | 21.388 | 20.4749 | 20.6207 | 20.9209 | 21.8998 | 21.6701 | 21.3022 | 20.4454 | 20.5512 | 20.518 | 22.0123 | 21.6383 | 21.1679 | 21.9812 | 21.7245 | 21.3523 | 19.9387 | 20.5423 |  | 20.5695 | 20.2249 | 20.3116 | 19.0703 |  | 16.7213 | 16.683 | 16.3904 | 16.5763 | 16.7073 | 17.2536 | 17.8617 | 15.5015 | 16.7954 | 15.9997 | 16.95 | 17.8526 | 44.5867 | 47.5803 | 44.0099 | 21.3898 |  |  | 0.28871 | -0.17815 | -30.7827 | 0.095238 | -0.003156 | -197.8105 | 16.8113 | -0.1377 | 0.31593 | 0.031791 | 0.074592 | 8.8279 | 9.0575 | 1.9787 | 21.7979 | 22.0183 | 22.2206 | 22.2877 | 22.1258 | 21.4641 | 20.2862 | 22.2176 | 22.3853 | 22.4249 | 22.3805 | 22.0206 | 21.2617 | 22.2982 | 16.9575 | 17.0571 | 16.0224 | 16.2128 | 16.3199 | 17.0857 | 16.7521 | 22.3903 | 22.1595 | 21.7381 | 22.1032 | 21.8173 | 21.325 | 21.957 | 21.5443 | 20.9352 | 20.1523 | 20.4814 | 20.0675 | 19.86 | 0.18187 | 0.028371 | 20.7615 | 22.0872 | 22.4037 | 20.1257 | 21.6936 | 22.1428 | 21.9585 | 21.7242 | 21.2975 | 21.8035 | 21.4707 | 21.0748 | 20.5099 | 20.5484 | 20.4391 | 20.4707 | 20.0849 |  | 20.2615 | 19.9714 | 20.123 | 19.6385 | 20.1114 | 20.3611 |  | 20.4551 |  |  | 20.3195 | 20.4085 | 20.6226 | [5 empty] | 21.9546 | 20.381 | 21.7016 | 22.0932 | 19.5882 | 21.2164 | 21.8527 | 19.3389 | 19.9093 | 21.1861 |  | 19.7983 | 20.9716 | 18.8752 | 19.6978 | 20.862 | 19.4537 | 20.2248 | 19.0651 | 20.2354 | 19.1313 | 20.3455 | 18.7785 | 20.1321 | 21.0985 | 19.3839 | 19.7548 | 21.005 | 18.9274 | 19.7752 | 20.8238 | 18.9597 | 20.197 | 19.2429 | 19.9726 | 18.8972 | 20.1861 | -0.11551 | 20.9471 | 0.047553 | 0.012444 | -26.9888 | 3.0981 | -0.34 | -0.45 | 0.64169 | -0.50076 | -6.5826 | 0.36614 | -0.066717 | -16.7029 | 4.8693 | 0.42514 | 0.42365 | 0.43251 | 0.41658 | 0.48156 | 0.44251 | 0.42773
42838.4139 | -548 | 22.8919 | 22.8593 | 22.8557 | 22.7777 | 22.4229 | 21.7693 | 22.7225 | 21.839 | 22.3838 | 22.3904 | 22.3834 | 22.0645 | 21.2994 | 22.262 | 21.5654 | 21.7454 | 21.8867 | 21.0752 | 21.1656 | 21.4007 | 20.4832 | 20.6335 | 20.9256 | 21.903 | 21.6762 | 21.3216 | 20.4515 | 20.5669 | 20.5262 | 22.0194 | 21.6439 | 21.1795 | 21.9963 | 21.7334 | 21.3621 | 19.9496 | 20.5394 |  | 20.5733 | 20.2342 | 20.3011 | 19.0776 |  | 16.7279 | 16.6855 | 16.3921 | 16.5748 | 16.703 | 17.2569 | 17.8793 | 15.5264 | 16.7939 | 15.9832 | 16.9499 | 17.8518 | 44.5729 | 47.6049 | 44.0141 | 21.3874 |  |  | 0.40699 | -0.34242 | -31.0384 | 0.18658 | 0.1815 | -197.8558 | 17.0504 | 0.016724 | 0.10362 | 0.073331 | 0.13969 | 8.8292 | 9.0585 | 1.9786 | 21.7981 | 22.0342 | 22.2246 | 22.2946 | 22.1308 | 21.4749 | 20.2903 | 22.2246 | 22.391 | 22.4269 | 22.3875 | 22.0245 | 21.2707 | 22.303 | 16.9653 | 17.051 | 16.0373 | 16.218 | 16.3148 | 17.0972 | 16.7576 | 22.3948 | 22.1662 | 21.7316 | 22.1048 | 21.8243 | 21.3297 | 21.9527 | 21.5548 | 20.9323 | 20.1487 | 20.4771 | 20.0708 | 19.8585 | 0.072951 | -0.14338 | 20.7628 | 22.0972 | 22.4039 | 20.1192 | 21.6977 | 22.1443 | 21.9582 | 21.7346 | 21.3049 | 21.8073 | 21.4778 | 21.0719 | 20.5094 | 20.5537 | 20.4407 | 20.4817 | 20.072 |  | 20.2563 | 19.9621 | 20.1174 | 19.6324 | 20.1058 | 20.3572 |  | 20.4495 |  |  | 20.3102 | 20.4134 | 20.6202 | [5 empty] | 21.9615 | 20.3721 | 21.6983 | 22.0831 | 19.5928 | 21.2166 | 21.8498 | 19.3479 | 19.9094 | 21.1988 |  | 19.8039 | 20.9869 | 18.8895 | 19.7193 | 20.8738 | 19.4551 | 20.2351 | 19.0701 | 20.2534 | 19.1373 | 20.3547 | 18.7745 | 20.1437 | 21.11 | 19.3926 | 19.7614 | 21.0051 | 18.9378 | 19.7831 | 20.8286 | 18.9631 | 20.202 | 19.2426 | 19.9792 | 18.9021 | 20.1999 | -0.043354 | 20.9479 | 0.047289 | 0.01325 | -27.1001 | 3.0981 | 2.38 | -0.09 | 0.76189 | -0.69426 | -6.6099 | 0.51248 | 0.50595 | -16.7049 | 4.9039 | 0.42532 | 0.42372 | 0.43249 | 0.41705 | 0.48055 | 0.44267 | 0.42765
42838.4139 | -547 | 22.8841 | 22.8627 | 22.8472 | 22.7768 | 22.4178 | 21.7691 | 22.7242 | 21.8274 | 22.3823 | 22.4043 | 22.3812 | 22.0696 | 21.2984 | 22.263 | 21.5564 | 21.7291 | 21.8819 | 21.0741 | 21.1708 | 21.3875 | 20.4791 | 20.6229 | 20.9218 | 21.8983 | 21.6644 | 21.3086 | 20.4506 | 20.5566 | 20.5209 | 22.0237 | 21.6447 | 21.1739 | 21.9963 | 21.7303 | 21.3562 | 19.945 | 20.542 |  | 20.5756 | 20.2306 | 20.3032 | 19.0765 |  | 16.7164 | 16.6854 | 16.3872 | 16.5876 | 16.7049 | 17.2334 | 17.8663 | 15.5099 | 16.7988 | 15.9465 | 16.9454 | 17.8542 | 44.5628 | 47.632 | 44.0036 | 21.3864 |  |  | 0.28936 | -0.31023 | -30.8406 | 0.36137 | 0.18215 | -197.8617 | 17.607 | -0.094328 | 0.16589 | 0.11047 | 0.11348 | 8.8281 | 9.058 | 1.9783 | 21.8022 | 22.0376 | 22.2295 | 22.2992 | 22.1311 | 21.4781 | 20.29 | 22.2294 | 22.3998 | 22.4309 | 22.3899 | 22.0243 | 21.2778 | 22.3061 | 16.9463 | 17.0519 | 16.0482 | 16.2091 | 16.2938 | 17.0868 | 16.753 | 22.3934 | 22.1681 | 21.7325 | 22.1043 | 21.8254 | 21.3328 | 21.9671 | 21.5511 | 20.9397 | 20.1598 | 20.49 | 20.0774 | 19.8627 | -0.027512 | -0.044286 | 20.7577 | 22.0964 | 22.3958 | 20.1271 | 21.6962 | 22.147 | 21.9625 | 21.7279 | 21.3043 | 21.8048 | 21.4727 | 21.0667 | 20.5206 | 20.5547 | 20.4406 | 20.4738 | 20.0803 |  | 20.2622 | 19.9586 | 20.1175 | 19.6371 | 20.106 | 20.3616 |  | 20.4488 |  |  | 20.3086 | 20.4167 | 20.6188 | [5 empty] | 21.9597 | 20.3694 | 21.7016 | 22.0951 | 19.5971 | 21.2125 | 21.8525 | 19.3512 | 19.9175 | 21.1969 |  | 19.8014 | 20.9953 | 18.8822 | 19.7154 | 20.8769 | 19.4556 | 20.228 | 19.0736 | 20.2612 | 19.1408 | 20.3654 | 18.7791 | 20.1446 | 21.1066 | 19.3924 | 19.7557 | 21.0036 | 18.9392 | 19.7929 | 20.8317 | 18.9575 | 20.2053 | 19.2408 | 19.9741 | 18.9021 | 20.1971 | -0.18897 | 20.9489 | 0.047068 | 0.013526 | -27.0837 | 3.0981 | 2.84 | -0.04 | 0.64242 | -0.66082 | -6.5888 | 0.71321 | 0.50684 | -16.7045 | 4.9831 | 0.42529 | 0.42383 | 0.43237 | 0.41795 | 0.47881 | 0.44255 | 0.4279
42838.414 | -546 | 22.8844 | 22.8667 | 22.8446 | 22.7778 | 22.4221 | 21.7583 | 22.7187 | 21.8307 | 22.3813 | 22.3908 | 22.3781 | 22.0611 | 21.2895 | 22.2571 | 21.5587 | 21.741 | 21.8814 | 21.0702 | 21.1738 | 21.3892 | 20.4825 | 20.6181 | 20.9267 | 21.9017 | 21.6693 | 21.3067 | 20.4506 | 20.5584 | 20.5109 | 22.0207 | 21.6401 | 21.1641 | 21.9866 | 21.7292 | 21.3635 | 19.9445 | 20.536 |  | 20.5773 | 20.2299 | 20.3036 | 19.0674 |  | 16.7178 | 16.6822 | 16.3899 | 16.5767 | 16.697 | 17.2214 | 17.8273 | 15.5016 | 16.8083 | 15.9162 | 16.9459 | 17.8532 | 44.5501 | 47.6576 | 44.0122 | 21.3922 |  |  | 0.3025 | -0.37068 | -30.7032 | 0.20892 | 0.081612 | -197.8755 | 17.5847 | -0.007588 | 0.049133 | 0.12788 | -0.041546 | 8.8296 | 9.0593 | 1.9781 | 21.802 | 22.0334 | 22.2234 | 22.2968 | 22.1251 | 21.4689 | 20.2872 | 22.2296 | 22.4008 | 22.4326 | 22.3888 | 22.0279 | 21.2765 | 22.3104 | 16.9621 | 17.0763 | 16.0543 | 16.2116 | 16.3038 | 17.0948 | 16.759 | 22.388 | 22.1658 | 21.731 | 22.1021 | 21.8222 | 21.3306 | 21.9636 | 21.5489 | 20.9407 | 20.1512 | 20.4883 | 20.0792 | 19.8661 | -0.027512 | -0.0098594 | 20.7564 | 22.0835 | 22.3906 | 20.1259 | 21.6898 | 22.1415 | 21.9566 | 21.728 | 21.2943 | 21.8015 | 21.4663 | 21.0684 | 20.5121 | 20.5502 | 20.4342 | 20.467 | 20.0742 |  | 20.2641 | 19.9595 | 20.115 | 19.6371 | 20.1085 | 20.3589 |  | 20.446 |  |  | 20.2983 | 20.4202 | 20.6304 | [5 empty] | 21.9622 | 20.3741 | 21.7052 | 22.0933 | 19.6038 | 21.222 | 21.8569 | 19.3496 | 19.9123 | 21.2012 |  | 19.8033 | 20.9805 | 18.8801 | 19.7036 | 20.8751 | 19.4563 | 20.2297 | 19.0669 | 20.256 | 19.1422 | 20.3581 | 18.7811 | 20.133 | 21.0929 | 19.3858 | 19.7594 | 20.9987 | 18.9174 | 19.7775 | 20.8171 | 18.9514 | 20.2007 | 19.2329 | 19.9678 | 18.8926 | 20.1838 | -0.0159 | 20.9456 | 0.047412 | 0.012502 | -27.0666 | 3.0981 | -4.85 | 0.07 | 0.65683 | -0.72233 | -6.574 | 0.54229 | 0.33925 | -16.7047 | 4.9798 | 0.42552 | 0.42372 | 0.43245 | 0.41713 | 0.47883 | 0.44279 | 0.42752
42838.414 | -545 | 22.8841 | 22.8633 | 22.8462 | 22.7808 | 22.4212 | 21.7625 | 22.7182 | 21.832 | 22.3764 | 22.3931 | 22.3794 | 22.0597 | 21.2932 | 22.2596 | 21.5645 | 21.7337 | 21.8877 | 21.0734 | 21.1769 | 21.3997 | 20.4852 | 20.634 | 20.9236 | 21.9062 | 21.6716 | 21.3135 | 20.4502 | 20.5571 | 20.5169 | 22.024 | 21.6412 | 21.1706 | 21.9912 | 21.7296 | 21.3628 | 19.9441 | 20.5368 |  | 20.5785 | 20.2331 | 20.3058 | 19.0609 |  | 16.7135 | 16.6851 | 16.3874 | 16.5786 | 16.6886 | 17.2109 | 17.8088 | 15.5219 | 16.8172 | 15.8888 | 16.9409 | 17.8509 | 44.5497 | 47.6741 | 44.0014 | 21.3895 |  |  | 0.23811 | -0.43508 | -30.2846 | 0.46191 | 0.19858 | -197.7947 | 17.8403 | -0.29606 | 0.10167 | -0.043527 | -0.068454 | 8.8285 | 9.0583 | 1.979 | 21.7949 | 22.0241 | 22.2227 | 22.2884 | 22.126 | 21.46 | 20.2834 | 22.2208 | 22.3866 | 22.427 | 22.3806 | 22.02 | 21.2605 | 22.3036 | 16.9574 | 17.0189 | 16.0575 | 16.2074 | 16.2802 | 17.0892 | 16.7592 | 22.3908 | 22.1661 | 21.7374 | 22.0991 | 21.8261 | 21.3314 | 21.9665 | 21.5558 | 20.9395 | 20.156 | 20.4888 | 20.0905 | 19.8741 | -0.11284 | -0.21604 | 20.7611 | 22.0878 | 22.3886 | 20.1232 | 21.7012 | 22.1482 | 21.9711 | 21.7324 | 21.2959 | 21.8078 | 21.4815 | 21.0714 | 20.5137 | 20.5605 | 20.4338 | 20.4754 | 20.07 |  | 20.2582 | 19.9678 | 20.1223 | 19.6369 | 20.1116 | 20.3612 |  | 20.453 |  |  | 20.2936 | 20.4064 | 20.6232 | [5 empty] | 21.9645 | 20.3678 | 21.7 | 22.0872 | 19.5942 | 21.2092 | 21.8444 | 19.3363 | 19.9087 | 21.1916 |  | 19.7862 | 20.9795 | 18.8762 | 19.6998 | 20.8646 | 19.4575 | 20.2325 | 19.0596 | 20.2521 | 19.1372 | 20.365 | 18.7754 | 20.1384 | 21.0995 | 19.3932 | 19.7516 | 20.9936 | 18.9323 | 19.7794 | 20.8198 | 18.9548 | 20.2015 | 19.2398 | 19.9715 | 18.8923 | 20.1826 | -0.10884 | 20.95 | 0.048014 | 0.012458 | -26.9758 | 3.0981 | 1.52 | -0.15 | 0.58275 | -0.78257 | -6.5291 | 0.80635 | 0.52918 | -16.701 | 5.0158 | 0.42544 | 0.42373 | 0.43256 | 0.41701 | 0.4785 | 0.44295 | 0.42746
42838.414 | -544 | 22.8896 | 22.8596 | 22.8423 | 22.7758 | 22.4194 | 21.7632 | 22.7182 | 21.8313 | 22.3749 | 22.3922 | 22.3786 | 22.0639 | 21.2927 | 22.2606 | 21.5612 | 21.736 | 21.877 | 21.0738 | 21.1678 | 21.3924 | 20.4705 | 20.6251 | 20.9149 | 21.9011 | 21.6659 | 21.3053 | 20.4484 | 20.5564 | 20.5128 | 22.0277 | 21.641 | 21.1772 | 21.9966 | 21.7375 | 21.3667 | 19.9529 | 20.5294 |  | 20.5776 | 20.2397 | 20.2998 | 19.0607 |  | 16.7144 | 16.6792 | 16.3955 | 16.5689 | 16.6827 | 17.2033 | 17.8265 | 15.5318 | 16.8127 | 15.8582 | 16.9403 | 17.8502 | 44.5671 | 47.7045 | 44.0197 | 21.3929 |  |  | 0.38596 | -0.27474 | -30.4187 | 0.38831 | 0.24458 | -197.8801 | 17.6846 | -0.28686 | 0.064506 | -0.049821 | 0.040219 | 8.8282 | 9.0577 | 1.9787 | 21.795 | 22.025 | 22.228 | 22.2911 | 22.1246 | 21.4636 | 20.2898 | 22.2134 | 22.3935 | 22.4325 | 22.3787 | 22.0268 | 21.2681 | 22.309 | 16.961 | 17.0231 | 16.037 | 16.1958 | 16.2817 | 17.09 | 16.7653 | 22.3731 | 22.15 | 21.7185 | 22.0902 | 21.8083 | 21.3189 | 21.9523 | 21.543 | 20.9232 | 20.148 | 20.4759 | 20.0672 | 19.8495 | -0.076072 | -0.21794 | 20.7664 | 22.0909 | 22.4091 | 20.1204 | 21.7059 | 22.1452 | 21.9713 | 21.7373 | 21.3046 | 21.8076 | 21.4754 | 21.0745 | 20.5144 | 20.5605 | 20.4469 | 20.4783 | 20.0773 |  | 20.2657 | 19.9682 | 20.1299 | 19.6373 | 20.1191 | 20.3624 |  | 20.4539 |  |  | 20.2742 | 20.4085 | 20.6271 | [5 empty] | 21.955 | 20.359 | 21.6935 | 22.0819 | 19.5933 | 21.2052 | 21.837 | 19.337 | 19.9034 | 21.1956 |  | 19.7882 | 20.9846 | 18.8695 | 19.705 | 20.8702 | 19.4626 | 20.2344 | 19.0569 | 20.253 | 19.137 | 20.3714 | 18.7845 | 20.1397 | 21.101 | 19.3953 | 19.7584 | 20.9969 | 18.9325 | 19.7761 | 20.826 | 18.9626 | 20.1988 | 19.2445 | 19.9758 | 18.8969 | 20.1876 | -0.11978 | 20.9475 | 0.047387 | 0.012705 | -27.0659 | 3.098 | -6.18 | 0.08 | 0.74193 | -0.62187 | -6.5435 | 0.73931 | 0.58727 | -16.7044 | 4.9938 | 0.42549 | 0.42397 | 0.4328 | 0.41669 | 0.48148 | 0.44325 | 0.42788
42838.414 | -543 | 22.8939 | 22.8587 | 22.846 | 22.7648 | 22.4165 | 21.7686 | 22.7208 | 21.831 | 22.3798 | 22.3918 | 22.3757 | 22.0606 | 21.2906 | 22.2553 | 21.5507 | 21.7281 | 21.8744 | 21.0699 | 21.1716 | 21.3846 | 20.4709 | 20.6219 | 20.9162 | 21.8929 | 21.6624 | 21.3 | 20.4425 | 20.5438 | 20.5017 | 22.0219 | 21.6388 | 21.1678 | 21.9859 | 21.7307 | 21.3619 | 19.9499 | 20.5304 |  | 20.5764 | 20.2341 | 20.2995 | 19.0585 |  | 16.7183 | 16.6809 | 16.3937 | 16.5675 | 16.6748 | 17.203 | 17.8649 | 15.5772 | 16.8183 | 15.8404 | 16.9361 | 17.8549 | 44.5846 | 47.7305 | 44.0129 | 21.4072 |  |  | 0.58572 | -0.188 | -30.3444 | 0.37648 | 0.031672 | -197.8144 | 17.6248 | -0.40974 | -0.33092 | 0.065569 | -0.14796 | 8.8295 | 9.0588 | 1.9788 | 21.7873 | 22.0254 | 22.2234 | 22.2863 | 22.1181 | 21.4689 | 20.287 | 22.2119 | 22.3852 | 22.43 | 22.3794 | 22.0194 | 21.2578 | 22.299 | 16.9298 | 17.0031 | 16.0249 | 16.1842 | 16.2701 | 17.0904 | 16.7515 | 22.389 | 22.1641 | 21.7329 | 22.0945 | 21.8153 | 21.3353 | 21.9643 | 21.5467 | 20.9347 | 20.1472 | 20.4808 | 20.0818 | 19.8563 | 0.044444 | -0.043715 | 20.7629 | 22.0905 | 22.4061 | 20.1196 | 21.6982 | 22.1448 | 21.9683 | 21.7277 | 21.2985 | 21.8132 | 21.474 | 21.0676 | 20.514 | 20.5627 | 20.4445 | 20.4755 | 20.0796 |  | 20.2653 | 19.9545 | 20.132 | 19.6445 | 20.1113 | 20.365 |  | 20.4639 |  |  | 20.281 | 20.419 | 20.6372 | [5 empty] | 21.9653 | 20.374 | 21.7026 | 22.0858 | 19.6008 | 21.2172 | 21.848 | 19.3335 | 19.9042 | 21.1966 |  | 19.7917 | 20.9755 | 18.8681 | 19.698 | 20.8753 | 19.4629 | 20.2281 | 19.0568 | 20.2513 | 19.139 | 20.36 | 18.789 | 20.1441 | 21.1009 | 19.3945 | 19.7633 | 21.0067 | 18.9278 | 19.7749 | 20.8274 | 18.9755 | 20.2104 | 19.2511 | 19.9794 | 18.8995 | 20.1888 | -0.25557 | 20.9436 | 0.047283 | 0.012117 | -27.0733 | 3.098 | 0.08 | 0.12 | 0.91396 | -0.51442 | -6.5355 | 0.72797 | 0.21133 | -16.7016 | 4.9853 | 0.42541 | 0.42443 | 0.43234 | 0.4202 | 0.48122 | 0.44321 | 0.42766
42838.414 | -542 | 22.8942 | 22.8589 | 22.8488 | 22.7726 | 22.4243 | 21.7631 | 22.7214 | 21.8335 | 22.3755 | 22.3979 | 22.3804 | 22.0632 | 21.2929 | 22.2576 | 21.5644 | 21.7404 | 21.8799 | 21.0755 | 21.1751 | 21.3932 | 20.484 | 20.6275 | 20.9295 | 21.8996 | 21.6764 | 21.3137 | 20.4424 | 20.5512 | 20.5172 | 22.0189 | 21.6431 | 21.175 | 21.9768 | 21.7381 | 21.3637 | 19.9419 | 20.5248 |  | 20.5737 | 20.2308 | 20.2998 | 19.0677 |  | 16.7208 | 16.6836 | 16.3796 | 16.5592 | 16.6736 | 17.1987 | 17.8815 | 15.6332 | 16.8253 | 15.8518 | 16.9394 | 17.8467 | 44.5926 | 47.7584 | 43.9949 | 21.3853 |  |  | 0.53907 | -0.17354 | -30.4956 | 0.29566 | 0.25312 | -197.8184 | 17.6208 | -0.35652 | -0.39241 | -0.060101 | 0.039178 | 8.8293 | 9.0589 | 1.9783 | 21.7839 | 22.0237 | 22.2187 | 22.2905 | 22.1243 | 21.4617 | 20.2864 | 22.2195 | 22.3854 | 22.4239 | 22.38 | 22.0175 | 21.2592 | 22.2996 | 16.917 | 17.0273 | 16.0167 | 16.1636 | 16.2503 | 17.0853 | 16.7571 | 22.392 | 22.1668 | 21.7361 | 22.1019 | 21.8202 | 21.3349 | 21.9636 | 21.5544 | 20.9358 | 20.15 | 20.4826 | 20.0772 | 19.857 | 0.16752 | -0.11827 | 20.7541 | 22.0939 | 22.4073 | 20.1248 | 21.7029 | 22.1515 | 21.9733 | 21.7323 | 21.2974 | 21.8067 | 21.4776 | 21.069 | 20.5181 | 20.554 | 20.4493 | 20.4764 | 20.0773 |  | 20.2625 | 19.9258 | 20.1153 | 19.6366 | 20.1012 | 20.3528 |  | 20.4531 |  |  | 20.2764 | 20.4076 | 20.6271 | [5 empty] | 21.9573 | 20.3673 | 21.6944 | 22.0859 | 19.598 | 21.2129 | 21.8434 | 19.3374 | 19.9062 | 21.1957 |  | 19.7981 | 20.9842 | 18.8794 | 19.7067 | 20.871 | 19.4667 | 20.2316 | 19.0642 | 20.2617 | 19.1406 | 20.369 | 18.7889 | 20.135 | 21.0989 | 19.3971 | 19.7621 | 20.9994 | 18.9229 | 19.775 | 20.826 | 18.9637 | 20.2018 | 19.2482 | 19.9722 | 18.8964 | 20.1823 | -0.10271 | 20.9411 | 0.047313 | 0.013816 | -27.0873 | 3.098 | -0.6 | 0.16 | 0.87683 | -0.49425 | -6.5518 | 0.64511 | 0.59743 | -16.7017 | 4.9847 | 0.42538 | 0.42466 | 0.43222 | 0.42103 | 0.48278 | 0.44269 | 0.42773
42838.414 | -541 | 22.8806 | 22.8633 | 22.8416 | 22.7756 | 22.414 | 21.7632 | 22.7242 | 21.8266 | 22.3793 | 22.4011 | 22.382 | 22.0623 | 21.2826 | 22.262 | 21.5571 | 21.7444 | 21.8808 | 21.0707 | 21.1736 | 21.3922 | 20.4841 | 20.6233 | 20.9286 | 21.9053 | 21.6729 | 21.3103 | 20.4437 | 20.5499 | 20.5182 | 22.0094 | 21.6376 | 21.1718 | 21.9827 | 21.7288 | 21.3573 | 19.9403 | 20.5187 |  | 20.5736 | 20.2339 | 20.2965 | 19.076 |  | 16.7127 | 16.678 | 16.3664 | 16.548 | 16.6593 | 17.1826 | 17.8756 | 15.6651 | 16.8185 | 15.8619 | 16.9314 | 17.8529 | 44.6239 | 47.783 | 44.0072 | 21.3939 |  |  | 0.36361 | -0.067093 | -31.1658 | 0.6597 | 0.33986 | -197.8282 | 17.3021 | -0.39069 | -0.34766 | -0.088424 | -0.15473 | 8.8296 | 9.059 | 1.9783 | 21.7965 | 22.0306 | 22.221 | 22.2906 | 22.1311 | 21.4601 | 20.2846 | 22.2179 | 22.3897 | 22.428 | 22.3848 | 22.022 | 21.2616 | 22.3049 | 16.9139 | 17.0665 | 16.0187 | 16.1435 | 16.253 | 17.0899 | 16.7567 | 22.3814 | 22.1608 | 21.7283 | 22.0931 | 21.8176 | 21.3231 | 21.9553 | 21.5449 | 20.9344 | 20.141 | 20.4764 | 20.0738 | 19.8411 | 0.059385 | -0.20539 | 20.7549 | 22.0867 | 22.4047 | 20.1201 | 21.6976 | 22.139 | 21.9611 | 21.731 | 21.3042 | 21.8041 | 21.4671 | 21.0742 | 20.5165 | 20.5404 | 20.4435 | 20.4811 | 20.0703 |  | 20.2668 | 19.9261 | 20.1186 | 19.6416 | 20.1119 | 20.364 |  | 20.4605 |  |  | 20.2651 | 20.4034 | 20.6229 | [5 empty] | 21.9542 | 20.3548 | 21.6867 | 22.0823 | 19.5992 | 21.2076 | 21.8334 | 19.3314 | 19.9081 | 21.1937 |  | 19.7979 | 20.9833 | 18.8758 | 19.7058 | 20.8731 | 19.4592 | 20.2311 | 19.0562 | 20.2585 | 19.1374 | 20.3666 | 18.7914 | 20.1306 | 21.0981 | 19.3985 | 19.7584 | 20.9968 | 18.9208 | 19.7718 | 20.8247 | 18.9602 | 20.2024 | 19.2416 | 19.9663 | 18.8944 | 20.181 | 0.075366 | 20.9571 | 0.047485 | 0.014324 | -27.0209 | 3.0981 | -2.46 | -0.22 | 0.72014 | -0.30731 | -6.6233 | 0.96363 | 0.69225 | -16.7016 | 4.9393 | 0.42572 | 0.42477 | 0.43244 | 0.42192 | 0.4825 | 0.4424 | 0.42788
42838.414 | -540 | 22.8915 | 22.8622 | 22.8553 | 22.7738 | 22.4242 | 21.7677 | 22.7306 | 21.8324 | 22.3829 | 22.3988 | 22.3791 | 22.0616 | 21.2956 | 22.2606 | 21.5554 | 21.746 | 21.8849 | 21.0738 | 21.1737 | 21.392 | 20.4827 | 20.6309 | 20.9347 | 21.9065 | 21.6745 | 21.3178 | 20.4511 | 20.5538 | 20.5132 | 22.0134 | 21.6339 | 21.159 | 21.9782 | 21.7223 | 21.3523 | 19.9398 | 20.516 |  | 20.5675 | 20.2182 | 20.2879 | 19.0647 |  | 16.7055 | 16.6741 | 16.375 | 16.542 | 16.6442 | 17.17 | 17.8766 | 15.6975 | 16.8166 | 15.8802 | 16.933 | 17.8528 | 44.6439 | 47.8029 | 44.0076 | 21.3956 |  |  | 0.38267 | -0.36214 | -31.9399 | 0.4192 | 0.23735 | -197.8223 | 16.9985 | -0.39463 | -0.1118 | 0.17487 | -0.10838 | 8.8291 | 9.0587 | 1.9785 | 21.8036 | 22.038 | 22.2267 | 22.2926 | 22.1317 | 21.4669 | 20.2924 | 22.2216 | 22.3975 | 22.4285 | 22.3853 | 22.0268 | 21.2737 | 22.3149 | 16.9202 | 17.0763 | 16.0142 | 16.1229 | 16.2352 | 17.0916 | 16.7607 | 22.383 | 22.158 | 21.7269 | 22.0845 | 21.8141 | 21.3267 | 21.9628 | 21.5443 | 20.9343 | 20.1462 | 20.4869 | 20.0795 | 19.8474 | 0.091824 | -0.083847 | 20.7491 | 22.0965 | 22.3994 | 20.1201 | 21.6944 | 22.1409 | 21.9664 | 21.7255 | 21.2917 | 21.8049 | 21.4777 | 21.0668 | 20.5099 | 20.5585 | 20.4419 | 20.4761 | 20.0734 |  | 20.2637 | 19.9162 | 20.1194 | 19.6494 | 20.1174 | 20.3681 |  | 20.4579 |  |  | 20.2717 | 20.411 | 20.6343 | [5 empty] | 21.9607 | 20.3634 | 21.6974 | 22.0857 | 19.5966 | 21.2176 | 21.8459 | 19.3285 | 19.8993 | 21.1898 |  | 19.7937 | 20.9821 | 18.8723 | 19.6984 | 20.8755 | 19.4558 | 20.225 | 19.0557 | 20.2548 | 19.1334 | 20.3615 | 18.7931 | 20.1398 | 21.0962 | 19.4079 | 19.7588 | 20.9982 | 18.9207 | 19.7773 | 20.826 | 18.962 | 20.2076 | 19.2467 | 19.9704 | 18.8968 | 20.1817 | -0.16022 | 20.9361 | 0.047608 | 0.013932 | -27.0306 | 3.0981 | 2.86 | -0.41 | 0.73876 | -0.71395 | -6.705 | 0.76815 | 0.5785 | -16.701 | 4.8957 | 0.42553 | 0.42506 | 0.43241 | 0.42141 | 0.48348 | 0.4427 | 0.42787
42838.414 | -539 | 22.8919 | 22.8622 | 22.8493 | 22.7808 | 22.4201 | 21.7677 | 22.7265 | 21.8375 | 22.3787 | 22.3877 | 22.3775 | 22.0679 | 21.2899 | 22.2574 | 21.5584 | 21.7396 | 21.8844 | 21.0762 | 21.169 | 21.3912 | 20.4824 | 20.6355 | 20.9297 | 21.9072 | 21.6712 | 21.3165 | 20.4486 | 20.5525 | 20.5107 | 22.0124 | 21.6382 | 21.1694 | 21.9875 | 21.732 | 21.3558 | 19.9401 | 20.5209 |  | 20.5677 | 20.2271 | 20.2907 | 19.0807 |  | 16.7053 | 16.6717 | 16.3633 | 16.5332 | 16.6393 | 17.1549 | 17.8475 | 15.7255 | 16.8145 | 15.9326 | 16.9374 | 17.8512 | 44.6667 | 47.8214 | 44.0067 | 21.39 |  |  | 0.55024 | -0.31023 | -31.9215 | 0.45731 | 0.095412 | -197.8663 | 17.2318 | -0.36506 | 0.015856 | 0.12096 | 0.024769 | 8.828 | 9.0578 | 1.9792 | 21.8088 | 22.0284 | 22.2218 | 22.292 | 22.1324 | 21.4707 | 20.2885 | 22.2194 | 22.3943 | 22.426 | 22.3832 | 22.0236 | 21.2681 | 22.3085 | 16.9188 | 17.0774 | 16.0226 | 16.1253 | 16.2122 | 17.0947 | 16.7588 | 22.3827 | 22.1637 | 21.7329 | 22.0964 | 21.813 | 21.3274 | 21.9571 | 21.5508 | 20.935 | 20.1475 | 20.4841 | 20.075 | 19.8569 | 0.067839 | -0.1371 | 20.7376 | 22.088 | 22.399 | 20.1199 | 21.6887 | 22.1358 | 21.963 | 21.7242 | 21.2938 | 21.804 | 21.4715 | 21.0783 | 20.5136 | 20.5473 | 20.4498 | 20.4696 | 20.0744 |  | 20.2576 | 19.8984 | 20.1171 | 19.6459 | 20.1092 | 20.3537 |  | 20.4472 |  |  | 20.2686 | 20.4053 | 20.63 | [5 empty] | 21.9624 | 20.3552 | 21.6955 | 22.0806 | 19.5906 | 21.2094 | 21.8402 | 19.331 | 19.8936 | 21.1885 |  | 19.7848 | 20.9717 | 18.8734 | 19.6926 | 20.8713 | 19.449 | 20.2239 | 19.0527 | 20.245 | 19.1305 | 20.357 | 18.7901 | 20.1447 | 21.0969 | 19.4073 | 19.7572 | 20.9968 | 18.9254 | 19.7776 | 20.828 | 18.9594 | 20.1988 | 19.2428 | 19.9644 | 18.8934 | 20.1796 | -0.09956 | 20.9627 | 0.047516 | 0.013242 | -27.1311 | 3.098 | 4.26 | 0.02 | 0.88586 | -0.6608 | -6.7031 | 0.8023 | 0.36677 | -16.7024 | 4.929 | 0.4253 | 0.42548 | 0.43223 | 0.42193 | 0.48232 | 0.44227 | 0.42765
42838.4141 | -538 | 22.8817 | 22.8505 | 22.8359 | 22.7689 | 22.407 | 21.7479 | 22.7197 | 21.8296 | 22.3664 | 22.3865 | 22.3658 | 22.0516 | 21.2871 | 22.2531 | 21.5644 | 21.7398 | 21.8866 | 21.0798 | 21.1712 | 21.3959 | 20.4868 | 20.6371 | 20.9309 | 21.9103 | 21.6763 | 21.3142 | 20.4501 | 20.548 | 20.5152 | 22.0242 | 21.6371 | 21.1734 | 21.9858 | 21.7297 | 21.3619 | 19.9437 | 20.5266 |  | 20.574 | 20.2321 | 20.2932 | 19.0973 |  | 16.6938 | 16.6501 | 16.3523 | 16.52 | 16.6188 | 17.1351 | 17.835 | 15.7219 | 16.8137 | 15.9629 | 16.9308 | 17.8559 | 44.6817 | 47.8562 | 44.0232 | 21.4074 |  |  | 0.50029 | -0.27014 | -31.0988 | 0.33509 | 0.024444 | -197.8414 | 17.6405 | -0.3736 | 0.23517 | -0.085697 | 0.13171 | 8.8277 | 9.0574 | 1.9788 | 21.8057 | 22.0307 | 22.23 | 22.297 | 22.134 | 21.4778 | 20.2981 | 22.2308 | 22.3998 | 22.43 | 22.3938 | 22.0303 | 21.2733 | 22.3134 | 16.917 | 17.08 | 16.073 | 16.1243 | 16.2071 | 17.0891 | 16.7541 | 22.3842 | 22.1672 | 21.7309 | 22.0958 | 21.8198 | 21.3267 | 21.9592 | 21.5543 | 20.9334 | 20.1499 | 20.4896 | 20.0764 | 19.8501 | 0.10146 | -0.14509 | 20.7572 | 22.0978 | 22.4049 | 20.13 | 21.7071 | 22.153 | 21.9738 | 21.7356 | 21.3057 | 21.8094 | 21.4806 | 21.0765 | 20.5191 | 20.5642 | 20.4435 | 20.4946 | 20.0769 |  | 20.2607 | 19.8875 | 20.1186 | 19.6461 | 20.1072 | 20.3587 |  | 20.4537 |  |  | 20.2673 | 20.4016 | 20.6281 | [5 empty] | 21.9608 | 20.3505 | 21.6973 | 22.0817 | 19.5907 | 21.2123 | 21.8429 | 19.3305 | 19.8935 | 21.1871 |  | 19.7849 | 20.9699 | 18.8768 | 19.6963 | 20.8688 | 19.4484 | 20.2216 | 19.05 | 20.2409 | 19.1311 | 20.3622 | 18.7987 | 20.144 | 21.1037 | 19.4122 | 19.7627 | 21.0046 | 18.9264 | 19.7807 | 20.8323 | 18.9597 | 20.206 | 19.2514 | 19.9695 | 18.8997 | 20.1779 | -0.068953 | 20.9582 | 0.047258 | 0.013293 | -27.0729 | 3.098 | 0.32 | -0.02 | 0.84471 | -0.61661 | -6.6159 | 0.68674 | 0.18564 | -16.7008 | 4.987 | 0.42534 | 0.42584 | 0.43216 | 0.42148 | 0.47618 | 0.44193 | 0.42792
42838.4141 | -537 | 22.8809 | 22.854 | 22.8365 | 22.7684 | 22.4079 | 21.7497 | 22.7171 | 21.8281 | 22.3668 | 22.3858 | 22.3634 | 22.0578 | 21.2819 | 22.2454 | 21.5712 | 21.747 | 21.8906 | 21.0794 | 21.1746 | 21.4067 | 20.4879 | 20.6373 | 20.9359 | 21.9119 | 21.6834 | 21.3205 | 20.4524 | 20.5527 | 20.5153 | 22.0193 | 21.6351 | 21.1688 | 21.9817 | 21.7234 | 21.3584 | 19.9375 | 20.5141 |  | 20.5692 | 20.2278 | 20.2931 | 19.1036 |  | 16.7051 | 16.664 | 16.3695 | 16.5456 | 16.6283 | 17.1351 | 17.8141 | 15.6838 | 16.8307 | 16.0229 | 16.9398 | 17.8606 | 44.6937 | 47.8827 | 44.0392 | 21.3964 |  |  | 0.34653 | -0.36279 | -30.8379 | 0.49739 | 0.1907 | -197.8769 | 17.8495 | -0.42617 | -0.057314 | -0.027582 | -0.099355 | 8.8281 | 9.0577 | 1.9787 | 21.8035 | 22.0234 | 22.2385 | 22.2957 | 22.1278 | 21.4608 | 20.2974 | 22.2218 | 22.3935 | 22.4355 | 22.3911 | 22.0239 | 21.2682 | 22.3112 | 16.9374 | 17.0887 | 16.1233 | 16.1468 | 16.2034 | 17.0945 | 16.7611 | 22.3927 | 22.1616 | 21.7267 | 22.0994 | 21.8222 | 21.3338 | 21.9587 | 21.5498 | 20.9368 | 20.1504 | 20.4873 | 20.0791 | 19.8459 | 0.11502 | -0.13254 | 20.7577 | 22.0867 | 22.4042 | 20.1262 | 21.6942 | 22.1506 | 21.9687 | 21.7328 | 21.307 | 21.8154 | 21.48 | 21.0779 | 20.5196 | 20.5638 | 20.4401 | 20.4888 | 20.0793 |  | 20.2528 | 19.883 | 20.1204 | 19.6437 | 20.1037 | 20.3556 |  | 20.4523 |  |  | 20.2681 | 20.3999 | 20.6232 | [5 empty] | 21.9577 | 20.3471 | 21.6954 | 22.0844 | 19.5909 | 21.2127 | 21.8457 | 19.3268 | 19.8992 | 21.1909 |  | 19.7914 | 20.9759 | 18.8809 | 19.7053 | 20.8726 | 19.4596 | 20.2246 | 19.052 | 20.2526 | 19.1315 | 20.3638 | 18.8032 | 20.1392 | 21.1011 | 19.4097 | 19.7617 | 20.9995 | 18.9237 | 19.773 | 20.8278 | 18.9474 | 20.204 | 19.2529 | 19.9661 | 18.8982 | 20.1719 | -0.14668 | 20.937 | 0.046404 | 0.012923 | -27.0662 | 3.098 | 9.55 | -0.04 | 0.70301 | -0.71459 | -6.5882 | 0.83671 | 0.5185 | -16.7023 | 5.0164 | 0.425 | 0.42602 | 0.43211 | 0.41983 | 0.47141 | 0.44155 | 0.42806
42838.4141 | -536 | 22.875 | 22.8528 | 22.8428 | 22.7689 | 22.4107 | 21.7562 | 22.7219 | 21.826 | 22.3641 | 22.3864 | 22.369 | 22.058 | 21.2833 | 22.2513 | 21.5612 | 21.7446 | 21.8797 | 21.0679 | 21.1733 | 21.3892 | 20.4778 | 20.6272 | 20.9196 | 21.8991 | 21.6669 | 21.3096 | 20.4452 | 20.5456 | 20.5056 | 22.0221 | 21.6393 | 21.1734 | 21.9887 | 21.7276 | 21.3571 | 19.9468 | 20.5245 |  | 20.5675 | 20.2331 | 20.2947 | 19.1194 |  | 16.6943 | 16.6548 | 16.3632 | 16.5421 | 16.6243 | 17.1392 | 17.8079 | 15.6576 | 16.8206 | 16.0806 | 16.9423 | 17.8544 | 44.6965 | 47.9057 | 44.0465 | 21.4008 |  |  | 0.31959 | -0.077605 | -31.4017 | 0.41985 | -0.01958 | -197.8204 | 17.7897 | -0.461 | -0.21046 | 0.13753 | -0.11359 | 8.8282 | 9.0578 | 1.9783 | 21.8053 | 22.0266 | 22.2299 | 22.2944 | 22.1313 | 21.4679 | 20.2917 | 22.2229 | 22.3978 | 22.4301 | 22.3859 | 22.027 | 21.271 | 22.3086 | 16.9408 | 17.0948 | 16.1252 | 16.1725 | 16.1966 | 17.0962 | 16.7529 | 22.3911 | 22.166 | 21.7245 | 22.0971 | 21.8232 | 21.3305 | 21.9608 | 21.5553 | 20.9302 | 20.1536 | 20.4946 | 20.0776 | 19.8378 | 0.15847 | -0.1759 | 20.7464 | 22.0923 | 22.405 | 20.1218 | 21.6976 | 22.1397 | 21.969 | 21.7302 | 21.3013 | 21.8161 | 21.4835 | 21.0775 | 20.5259 | 20.5478 | 20.4427 | 20.4943 | 20.0997 |  | 20.251 | 19.8845 | 20.1244 | 19.6461 | 20.1034 | 20.3549 |  | 20.4488 |  |  | 20.2654 | 20.3977 | 20.6229 | [5 empty] | 21.9592 | 20.3493 | 21.6937 | 22.09 | 19.5875 | 21.2141 | 21.8461 | 19.3217 | 19.8954 | 21.1809 |  | 19.7839 | 20.9734 | 18.8727 | 19.6943 | 20.8714 | 19.4605 | 20.2201 | 19.0515 | 20.24 | 19.1266 | 20.3608 | 18.8022 | 20.145 | 21.0966 | 19.4093 | 19.7585 | 20.9991 | 18.9198 | 19.7793 | 20.8282 | 18.9488 | 20.2077 | 19.2547 | 19.9678 | 18.8992 | 20.1683 | -0.24147 | 20.952 | 0.046699 | 0.013003 | -27.0465 | 3.098 | -3.25 | 0.05 | 0.67512 | -0.33049 | -6.6481 | 0.76872 | -0.16615 | -16.7001 | 5.008 | 0.42438 | 0.42611 | 0.43203 | 0.41966 | 0.47024 | 0.44142 | 0.42839
42838.4141 | -535 | 22.8851 | 22.8517 | 22.8488 | 22.7818 | 22.4172 | 21.7538 | 22.7272 | 21.8273 | 22.373 | 22.3886 | 22.3782 | 22.0668 | 21.2849 | 22.2586 | 21.5607 | 21.744 | 21.8795 | 21.0741 | 21.1745 | 21.3941 | 20.4731 | 20.6271 | 20.9223 | 21.8983 | 21.6679 | 21.3083 | 20.4416 | 20.5491 | 20.5005 | 22.0209 | 21.6396 | 21.1712 | 21.9856 | 21.7312 | 21.3589 | 19.9409 | 20.5228 |  | 20.575 | 20.2318 | 20.2923 | 19.1288 |  | 16.7014 | 16.649 | 16.3673 | 16.5394 | 16.6196 | 17.1561 | 17.8412 | 15.6902 | 16.8189 | 16.1548 | 16.9387 | 17.8563 | 44.7078 | 47.9299 | 44.0724 | 21.4011 |  |  | 0.47073 | -0.34308 | -31.545 | 0.23455 | 0.30569 | -197.8131 | 17.4434 | -0.44523 | -0.18419 | 0.013748 | 0.0798 | 8.8294 | 9.0587 | 1.9778 | 21.7993 | 22.0251 | 22.2254 | 22.2941 | 22.1352 | 21.4642 | 20.2917 | 22.2208 | 22.3965 | 22.43 | 22.3871 | 22.0283 | 21.2734 | 22.3064 | 16.9449 | 17.1127 | 16.1257 | 16.1953 | 16.2219 | 17.0961 | 16.762 | 22.393 | 22.1636 | 21.7338 | 22.0996 | 21.8269 | 21.323 | 21.9678 | 21.5524 | 20.9338 | 20.1523 | 20.4943 | 20.0801 | 19.8404 | 0.21863 | -0.084418 | 20.7397 | 22.0922 | 22.3969 | 20.119 | 21.6934 | 22.1418 | 21.957 | 21.7244 | 21.3006 | 21.8006 | 21.472 | 21.0737 | 20.5168 | 20.5476 | 20.4411 | 20.4831 | 20.0995 |  | 20.2545 | 19.8822 | 20.1203 | 19.6587 | 20.1051 | 20.3536 |  | 20.448 |  |  | 20.2698 | 20.4047 | 20.6322 | [5 empty] | 21.9617 | 20.3551 | 21.7018 | 22.0913 | 19.5864 | 21.2151 | 21.8488 | 19.3267 | 19.8966 | 21.1868 |  | 19.784 | 20.9819 | 18.8688 | 19.6994 | 20.8715 | 19.461 | 20.2229 | 19.0529 | 20.2367 | 19.1288 | 20.3532 | 18.8021 | 20.1462 | 21.1012 | 19.4136 | 19.7623 | 21.0167 | 18.9187 | 19.7837 | 20.8331 | 18.9562 | 20.2107 | 19.2585 | 19.9728 | 18.8995 | 20.1687 | -0.054298 | 20.957 | 0.047467 | 0.012988 | -27.0654 | 3.098 | 5.7 | -0.22 | 0.81934 | -0.69489 | -6.6632 | 0.57455 | 0.6565 | -16.7002 | 4.9592 | 0.4245 | 0.42604 | 0.43174 | 0.41919 | 0.47125 | 0.44096 | 0.42827
42838.4141 | -534 | 22.8778 | 22.8485 | 22.8441 | 22.7701 | 22.4191 | 21.7583 | 22.7182 | 21.8275 | 22.3735 | 22.3866 | 22.3749 | 22.0668 | 21.2873 | 22.2604 | 21.5524 | 21.7361 | 21.8833 | 21.0653 | 21.1695 | 21.3867 | 20.4744 | 20.6296 | 20.9228 | 21.9048 | 21.6684 | 21.3061 | 20.4376 | 20.5388 | 20.4956 | 22.0148 | 21.6346 | 21.1717 | 21.9884 | 21.7324 | 21.3575 | 19.9364 | 20.5107 |  | 20.5715 | 20.2282 | 20.2857 | 19.1361 |  | 16.6969 | 16.65 | 16.3627 | 16.545 | 16.6197 | 17.1721 | 17.8827 | 15.714 | 16.822 | 16.1949 | 16.9414 | 17.8492 | 44.7077 | 47.96 | 44.0873 | 21.3919 |  |  | 0.37873 | -0.15843 | -31.6265 | 0.27595 | 0.3852 | -197.8453 | 17.3856 | -0.44392 | -0.21747 | 0.14655 | 0.12945 | 8.8278 | 9.0576 | 1.9787 | 21.7873 | 22.0217 | 22.2257 | 22.2836 | 22.1192 | 21.4565 | 20.2817 | 22.2138 | 22.3903 | 22.4266 | 22.384 | 22.0165 | 21.2621 | 22.2984 | 16.9614 | 17.1502 | 16.1401 | 16.2069 | 16.2223 | 17.0978 | 16.7535 | 22.3942 | 22.1576 | 21.7358 | 22.1035 | 21.8184 | 21.3295 | 21.9567 | 21.5534 | 20.9362 | 20.1472 | 20.4895 | 20.0756 | 19.8314 | 0.068429 | -0.037438 | 20.7337 | 22.085 | 22.3945 | 20.124 | 21.6928 | 22.1582 | 21.9679 | 21.7296 | 21.3011 | 21.8107 | 21.4713 | 21.0723 | 20.5203 | 20.5581 | 20.4455 | 20.4752 | 20.1003 |  | 20.2539 | 19.8765 | 20.1094 | 19.6594 | 20.1021 | 20.3476 |  | 20.4442 |  |  | 20.2748 | 20.4041 | 20.6362 | [5 empty] | 21.9653 | 20.3515 | 21.7001 | 22.0869 | 19.5895 | 21.2165 | 21.856 | 19.3325 | 19.9012 | 21.1914 |  | 19.786 | 20.9762 | 18.8778 | 19.7004 | 20.8725 | 19.4593 | 20.2232 | 19.0497 | 20.2436 | 19.1294 | 20.3534 | 18.8032 | 20.1445 | 21.1064 | 19.4109 | 19.7644 | 21.0083 | 18.9249 | 19.7815 | 20.8379 | 18.9534 | 20.2076 | 19.2592 | 19.9715 | 18.8989 | 20.1795 | -0.074518 | 20.9396 | 0.04794 | 0.012909 | -27.0017 | 3.098 | 3.63 | 0.06 | 0.73493 | -0.47221 | -6.6718 | 0.6232 | 0.73697 | -16.7021 | 4.9511 | 0.42446 | 0.42583 | 0.43162 | 0.41756 | 0.46866 | 0.4406 | 0.42835
42838.4141 | -533 | 22.882 | 22.8503 | 22.8382 | 22.7755 | 22.4118 | 21.7688 | 22.713 | 21.8236 | 22.3774 | 22.3942 | 22.3802 | 22.0561 | 21.2861 | 22.2528 | 21.5691 | 21.7423 | 21.8909 | 21.0751 | 21.1806 | 21.4051 | 20.4906 | 20.6308 | 20.938 | 21.9137 | 21.6768 | 21.3189 | 20.4548 | 20.5435 | 20.5116 | 22.0193 | 21.6412 | 21.1669 | 21.9777 | 21.7352 | 21.3557 | 19.9402 | 20.5165 |  | 20.5724 | 20.2273 | 20.2901 | 19.1552 |  | 16.6913 | 16.653 | 16.3538 | 16.543 | 16.6227 | 17.1845 | 17.8956 | 15.7295 | 16.8148 | 16.2771 | 16.9377 | 17.8654 | 44.7199 | 47.9921 | 44.0986 | 21.4015 |  |  | 0.46021 | -0.42259 | -31.3222 | 0.32063 | 0.43383 | -197.825 | 17.5137 | -0.4564 | -0.1297 | 0.098088 | -0.0031808 | 8.8289 | 9.0585 | 1.9785 | 21.7902 | 22.0253 | 22.2219 | 22.2817 | 22.122 | 21.4582 | 20.2727 | 22.2138 | 22.3882 | 22.4231 | 22.3767 | 22.0158 | 21.2616 | 22.2924 | 16.9737 | 17.1767 | 16.1569 | 16.2087 | 16.2217 | 17.0975 | 16.7579 | 22.3764 | 22.1552 | 21.7205 | 22.0952 | 21.8117 | 21.3165 | 21.9538 | 21.5452 | 20.9224 | 20.143 | 20.4764 | 20.0691 | 19.8205 | 0.10932 | -0.006626 | 20.7418 | 22.0864 | 22.399 | 20.1181 | 21.6978 | 22.1475 | 21.9621 | 21.7285 | 21.3008 | 21.8069 | 21.469 | 21.0683 | 20.5143 | 20.5596 | 20.4501 | 20.4775 | 20.1077 |  | 20.2644 | 19.8904 | 20.118 | 19.6638 | 20.1089 | 20.3499 |  | 20.4524 |  |  | 20.2766 | 20.3977 | 20.638 | [5 empty] | 21.9669 | 20.351 | 21.6961 | 22.0802 | 19.5922 | 21.2166 | 21.857 | 19.3339 | 19.9049 | 21.2048 |  | 19.7943 | 20.9822 | 18.8878 | 19.7064 | 20.8789 | 19.4697 | 20.2277 | 19.048 | 20.2518 | 19.1372 | 20.3643 | 18.8043 | 20.1348 | 21.0962 | 19.412 | 19.7477 | 21.0111 | 18.918 | 19.775 | 20.822 | 18.9566 | 20.202 | 19.2498 | 19.9613 | 18.8947 | 20.1602 | -0.11255 | 20.9456 | 0.047553 | 0.0137 | -27.0457 | 3.098 | -4.49 | -0.07 | 0.81016 | -0.77122 | -6.6396 | 0.67177 | 0.78212 | -16.7016 | 4.9694 | 0.4246 | 0.42574 | 0.43172 | 0.41616 | 0.46731 | 0.4402 | 0.42851
42838.4141 | -532 | 22.8892 | 22.8587 | 22.8495 | 22.7875 | 22.4256 | 21.7711 | 22.7256 | 21.8328 | 22.3765 | 22.3962 | 22.3792 | 22.0668 | 21.2925 | 22.2613 | 21.567 | 21.7469 | 21.882 | 21.0828 | 21.1793 | 21.4016 | 20.4847 | 20.6298 | 20.9314 | 21.9006 | 21.662 | 21.3114 | 20.4452 | 20.5449 | 20.5012 | 22.0153 | 21.6412 | 21.1693 | 21.9943 | 21.7348 | 21.3532 | 19.9407 | 20.5207 |  | 20.5736 | 20.2337 | 20.2886 | 19.1727 |  | 16.7011 | 16.6509 | 16.3617 | 16.5346 | 16.6279 | 17.1914 | 17.9243 | 15.7628 | 16.8165 | 16.4122 | 16.9456 | 17.8557 | 44.7166 | 48.0087 | 44.1048 | 21.394 |  |  | 0.36033 | -0.303 | -30.8977 | 0.36663 | 0.11776 | -197.8105 | 17.6083 | -0.4518 | -0.13807 | 0.073961 | 0.025984 | 8.8287 | 9.0586 | 1.9787 | 21.7957 | 22.0146 | 22.222 | 22.2831 | 22.1209 | 21.4553 | 20.2818 | 22.213 | 22.3871 | 22.4185 | 22.3758 | 22.0174 | 21.2627 | 22.2976 | 16.9846 | 17.1386 | 16.1884 | 16.2086 | 16.2051 | 17.0913 | 16.756 | 22.3878 | 22.16 | 21.7209 | 22.0961 | 21.8193 | 21.3257 | 21.9545 | 21.5482 | 20.9329 | 20.1514 | 20.4826 | 20.0728 | 19.8118 | -0.032623 | -0.19473 | 20.7351 | 22.0761 | 22.4013 | 20.1122 | 21.6907 | 22.1375 | 21.9669 | 21.7334 | 21.2948 | 21.8029 | 21.4714 | 21.0695 | 20.5101 | 20.5552 | 20.4375 | 20.474 | 20.1019 |  | 20.2635 | 19.8823 | 20.1167 | 19.6536 | 20.105 | 20.3453 |  | 20.4452 |  |  | 20.2818 | 20.4017 | 20.6494 | [5 empty] | 21.9788 | 20.3641 | 21.709 | 22.0956 | 19.6024 | 21.2176 | 21.8539 | 19.3281 | 19.9092 | 21.1939 |  | 19.7991 | 20.9829 | 18.881 | 19.7082 | 20.8822 | 19.4639 | 20.2319 | 19.0512 | 20.2564 | 19.1333 | 20.3618 | 18.8195 | 20.1469 | 21.1047 | 19.4246 | 19.7696 | 21.0176 | 18.9279 | 19.7823 | 20.8428 | 18.9776 | 20.2119 | 19.2673 | 19.977 | 18.9 | 20.1796 | -0.08435 | 20.9462 | 0.047774 | 0.015544 | -27.0418 | 3.098 | -19.61 | -0.04 | 0.71686 | -0.65303 | -6.5945 | 0.71834 | 0.40749 | -16.7011 | 4.9829 | 0.42474 | 0.42592 | 0.43188 | 0.41422 | 0.46357 | 0.43973 | 0.42904
42838.4141 | -531 | 22.877 | 22.8554 | 22.8397 | 22.7676 | 22.4134 | 21.7608 | 22.7183 | 21.8265 | 22.3716 | 22.3872 | 22.3656 | 22.0579 | 21.2875 | 22.2509 | 21.5529 | 21.7323 | 21.884 | 21.0779 | 21.1681 | 21.3922 | 20.478 | 20.6229 | 20.9261 | 21.8964 | 21.6718 | 21.3129 | 20.44 | 20.5407 | 20.4977 | 22.017 | 21.6343 | 21.1694 | 21.9906 | 21.7315 | 21.3481 | 19.9352 | 20.5186 |  | 20.5698 | 20.2344 | 20.2878 | 19.1912 |  | 16.6888 | 16.6437 | 16.3452 | 16.5302 | 16.6249 | 17.1974 | 17.9429 | 15.7562 | 16.8116 | 16.4229 | 16.9389 | 17.8529 | 44.7431 | 48.0359 | 44.1008 | 21.3962 |  |  | 0.50884 | -0.24649 | -30.7906 | 0.44088 | 0.27021 | -197.7796 | 17.7306 | -0.59242 | -0.70981 | 0.088437 | -0.000924 | 8.8286 | 9.0582 | 1.9786 | 21.7962 | 22.0161 | 22.222 | 22.2909 | 22.1246 | 21.4621 | 20.2857 | 22.2217 | 22.3923 | 22.4298 | 22.3826 | 22.0222 | 21.2642 | 22.3055 | 16.9957 | 17.1082 | 16.181 | 16.2144 | 16.2008 | 17.0951 | 16.7483 | 22.3915 | 22.1692 | 21.7273 | 22.1009 | 21.8214 | 21.3262 | 21.9641 | 21.5562 | 20.9366 | 20.1575 | 20.496 | 20.0769 | 19.8118 | 0.096936 | -0.04866 | 20.7311 | 22.0807 | 22.3981 | 20.1098 | 21.6962 | 22.1393 | 21.9669 | 21.7348 | 21.3012 | 21.8131 | 21.4748 | 21.0745 | 20.5149 | 20.5614 | 20.4425 | 20.4811 | 20.0924 |  | 20.2649 | 19.8655 | 20.1187 | 19.65 | 20.1054 | 20.3466 |  | 20.4508 |  |  | 20.2805 | 20.3863 | 20.6416 | [5 empty] | 21.9581 | 20.346 | 21.6985 | 22.0879 | 19.5944 | 21.2122 | 21.8468 | 19.3232 | 19.9111 | 21.2003 |  | 19.7948 | 20.9864 | 18.8868 | 19.7054 | 20.8814 | 19.4757 | 20.2267 | 19.0499 | 20.238 | 19.1275 | 20.3511 | 18.8107 | 20.1484 | 21.0982 | 19.4163 | 19.7607 | 21.0195 | 18.9341 | 19.7811 | 20.8473 | 18.9806 | 20.2156 | 19.2597 | 19.97 | 18.9072 | 20.1826 | -0.19936 | 20.948 | 0.047959 | 0.014549 | -27.0456 | 3.098 | -15.84 | -0.24 | 0.85186 | -0.58899 | -6.583 | 0.78772 | 0.61727 | -16.7 | 5.0002 | 0.42505 | 0.42645 | 0.43199 | 0.41343 | 0.4635 | 0.43903 | 0.42924
42838.4141 | -530 | 22.8832 | 22.8485 | 22.8452 | 22.7724 | 22.4117 | 21.7593 | 22.7203 | 21.8337 | 22.3702 | 22.3905 | 22.3753 | 22.0582 | 21.2879 | 22.2514 | 21.5583 | 21.7384 | 21.8795 | 21.067 | 21.1756 | 21.3981 | 20.4759 | 20.6258 | 20.928 | 21.897 | 21.6721 | 21.3136 | 20.4402 | 20.5451 | 20.4971 | 22.0179 | 21.6409 | 21.1745 | 21.9886 | 21.7294 | 21.3486 | 19.9373 | 20.5199 |  | 20.5729 | 20.2299 | 20.2885 | 19.2054 |  | 16.6946 | 16.6439 | 16.3486 | 16.5241 | 16.623 | 17.2122 | 17.9695 | 15.7598 | 16.8041 | 16.4309 | 16.9354 | 17.8618 | 44.7686 | 48.0666 | 44.0876 | 21.4004 |  |  | 0.39516 | -0.10455 | -30.8537 | 0.11101 | 0.1723 | -197.8388 | 17.5242 | -0.68508 | -0.77325 | -0.22123 | -0.014118 | 8.8286 | 9.0583 | 1.9781 | 21.7887 | 22.0119 | 22.2145 | 22.2843 | 22.1147 | 21.4591 | 20.2805 | 22.21 | 22.3882 | 22.4185 | 22.3687 | 22.0164 | 21.2617 | 22.2994 | 17.0141 | 17.112 | 16.1795 | 16.2268 | 16.2567 | 17.0972 | 16.7563 | 22.3862 | 22.1701 | 21.7345 | 22.0961 | 21.8236 | 21.328 | 21.9615 | 21.5565 | 20.9388 | 20.1497 | 20.5007 | 20.074 | 19.8167 | 0.040512 | -0.1565 | 20.735 | 22.0857 | 22.3899 | 20.1079 | 21.6859 | 22.1416 | 21.9686 | 21.7268 | 21.3044 | 21.8116 | 21.4752 | 21.0763 | 20.5102 | 20.551 | 20.4341 | 20.4702 | 20.0866 |  | 20.2571 | 19.8446 | 20.1168 | 19.6567 | 20.1022 | 20.3439 |  | 20.4568 |  |  | 20.2753 | 20.3969 | 20.6448 | [5 empty] | 21.9605 | 20.3472 | 21.6943 | 22.0839 | 19.5878 | 21.2199 | 21.8451 | 19.3388 | 19.9097 | 21.2041 |  | 19.8028 | 20.9869 | 18.8805 | 19.7084 | 20.8756 | 19.4681 | 20.2276 | 19.0424 | 20.2393 | 19.1331 | 20.349 | 18.8139 | 20.1434 | 21.1019 | 19.4276 | 19.7632 | 21.0188 | 18.9308 | 19.7833 | 20.8424 | 18.9781 | 20.205 | 19.2694 | 19.9692 | 18.9109 | 20.1776 | -0.11421 | 20.9499 | 0.048223 | 0.014201 | -27.0341 | 3.098 | 3.43 | 0.02 | 0.7507 | -0.38359 | -6.5897 | 0.39527 | 0.49292 | -16.7029 | 4.9711 | 0.42494 | 0.42697 | 0.4317 | 0.41163 | 0.4646 | 0.43871 | 0.42885
42838.4142 | -529 | 22.8855 | 22.8547 | 22.8476 | 22.7747 | 22.4188 | 21.7647 | 22.7139 | 21.8321 | 22.376 | 22.3888 | 22.3771 | 22.0646 | 21.2852 | 22.2557 | 21.5627 | 21.7413 | 21.8832 | 21.075 | 21.1727 | 21.3984 | 20.4772 | 20.6251 | 20.9271 | 21.9026 | 21.675 | 21.3078 | 20.433 | 20.5387 | 20.507 | 22.0191 | 21.6456 | 21.1726 | 21.988 | 21.7294 | 21.3558 | 19.9422 | 20.5147 |  | 20.5795 | 20.2283 | 20.2898 | 19.2114 |  | 16.6957 | 16.6483 | 16.3497 | 16.5217 | 16.629 | 17.2196 | 17.9807 | 15.7611 | 16.8029 | 16.4163 | 16.9328 | 17.8576 | 44.7993 | 48.0953 | 44.0825 | 21.4003 |  |  | 0.32025 | -0.084833 | -30.7617 | 0.2674 | 0.399 | -197.8401 | 17.6951 | -0.70282 | -0.42452 | -0.12577 | 0.028762 | 8.8288 | 9.0584 | 1.9779 | 21.7861 | 22.0173 | 22.2154 | 22.2908 | 22.1095 | 21.4526 | 20.2758 | 22.2115 | 22.3921 | 22.4261 | 22.3746 | 22.0158 | 21.2584 | 22.3002 | 17.0235 | 17.1372 | 16.1864 | 16.2304 | 16.2993 | 17.0988 | 16.7511 | 22.3822 | 22.1654 | 21.7296 | 22.101 | 21.8191 | 21.3284 | 21.9624 | 21.5534 | 20.9396 | 20.1474 | 20.4895 | 20.0794 | 19.8193 | 0.14943 | -0.112 | 20.7305 | 22.0837 | 22.39 | 20.1001 | 21.6976 | 22.1391 | 21.963 | 21.73 | 21.3028 | 21.8035 | 21.4698 | 21.0692 | 20.5081 | 20.5538 | 20.4407 | 20.4717 | 20.0856 |  | 20.2572 | 19.8251 | 20.1231 | 19.6636 | 20.106 | 20.34 |  | 20.4441 |  |  | 20.2666 | 20.3899 | 20.6295 | [5 empty] | 21.9539 | 20.3386 | 21.6922 | 22.0783 | 19.5785 | 21.2112 | 21.8383 | 19.3458 | 19.9119 | 21.2107 |  | 19.8057 | 21.0013 | 18.8935 | 19.7129 | 20.8773 | 19.4697 | 20.2325 | 19.0543 | 20.2389 | 19.1332 | 20.3434 | 18.8076 | 20.149 | 21.0955 | 19.4305 | 19.7743 | 21.0195 | 18.924 | 19.788 | 20.8496 | 18.9819 | 20.2175 | 19.2724 | 19.968 | 18.9082 | 20.1778 | -0.20233 | 20.9446 | 0.048032 | 0.014622 | -27.0147 | 3.098 | 9.06 | -0.09 | 0.67582 | -0.34554 | -6.5799 | 0.61348 | 0.75012 | -16.7032 | 4.9954 | 0.42498 | 0.42772 | 0.43163 | 0.41077 | 0.46323 | 0.43871 | 0.42869
42838.4142 | -528 | 22.8737 | 22.8583 | 22.8447 | 22.7724 | 22.4167 | 21.7633 | 22.7181 | 21.8293 | 22.375 | 22.384 | 22.3742 | 22.0621 | 21.2812 | 22.2539 | 21.5627 | 21.7404 | 21.8868 | 21.0721 | 21.1762 | 21.3974 | 20.4858 | 20.6288 | 20.9298 | 21.9082 | 21.6751 | 21.318 | 20.4488 | 20.5483 | 20.5055 | 22.0248 | 21.6445 | 21.1728 | 21.9939 | 21.7369 | 21.3561 | 19.9495 | 20.5175 |  | 20.5827 | 20.2342 | 20.2963 | 19.2215 |  | 16.6747 | 16.6319 | 16.3352 | 16.5098 | 16.6174 | 17.2015 | 17.9647 | 15.766 | 16.7941 | 16.3552 | 16.9212 | 17.8556 | 44.8301 | 48.1179 | 44.0756 | 21.3987 |  |  | 0.38727 | -0.15909 | -30.899 | 0.28317 | 0.60796 | -197.8309 | 17.6787 | -0.461 | -0.26495 | -0.32969 | -0.024881 | 8.8288 | 9.0585 | 1.9793 | 21.7921 | 22.0313 | 22.2244 | 22.2928 | 22.1225 | 21.4639 | 20.2828 | 22.2152 | 22.3993 | 22.4279 | 22.3891 | 22.0241 | 21.2687 | 22.3074 | 17.0313 | 17.1913 | 16.2061 | 16.2531 | 16.3132 | 17.0967 | 16.747 | 22.3849 | 22.1542 | 21.7264 | 22.0967 | 21.8196 | 21.3284 | 21.961 | 21.5526 | 20.9321 | 20.1445 | 20.4875 | 20.0822 | 19.8198 | 0.10598 | 0.12746 | 20.7343 | 22.0786 | 22.3942 | 20.0993 | 21.694 | 22.1407 | 21.9596 | 21.7271 | 21.2925 | 21.8005 | 21.4695 | 21.0628 | 20.5114 | 20.549 | 20.437 | 20.4676 | 20.0999 |  | 20.2571 | 19.8016 | 20.1273 | 19.6748 | 20.1067 | 20.3456 |  | 20.446 |  |  | 20.2706 | 20.3794 | 20.6466 | [5 empty] | 21.9589 | 20.343 | 21.6966 | 22.0758 | 19.5879 | 21.2193 | 21.8434 | 19.3423 | 19.9115 | 21.2053 |  | 19.8027 | 21.0056 | 18.8912 | 19.7149 | 20.8796 | 19.4768 | 20.2273 | 19.0594 | 20.2328 | 19.1246 | 20.3489 | 18.8122 | 20.1519 | 21.1042 | 19.433 | 19.7813 | 21.0318 | 18.9338 | 19.7943 | 20.8527 | 18.991 | 20.225 | 19.2741 | 19.9731 | 18.9197 | 20.1851 | -0.15224 | 20.9481 | 0.048223 | 0.015406 | -27.0257 | 3.098 | 2.63 | -0.21 | 0.74318 | -0.47318 | -6.5944 | 0.63129 | 0.92591 | -16.7023 | 4.9929 | 0.42458 | 0.42851 | 0.43135 | 0.40967 | 0.46056 | 0.43867 | 0.42858
42838.4142 | -527 | 22.8741 | 22.8543 | 22.8391 | 22.7725 | 22.4166 | 21.7555 | 22.7178 | 21.8248 | 22.369 | 22.3877 | 22.3746 | 22.0573 | 21.2788 | 22.253 | 21.5578 | 21.742 | 21.8806 | 21.0657 | 21.1716 | 21.3919 | 20.4756 | 20.6261 | 20.9241 | 21.9011 | 21.6693 | 21.3092 | 20.4356 | 20.5386 | 20.4917 | 22.0187 | 21.6433 | 21.1692 | 21.9948 | 21.725 | 21.3599 | 19.9455 | 20.5175 |  | 20.5728 | 20.2345 | 20.2926 | 19.2259 |  | 16.6894 | 16.6417 | 16.347 | 16.5226 | 16.624 | 17.1983 | 17.9936 | 15.7876 | 16.8048 | 16.2594 | 16.9398 | 17.8582 | 44.8593 | 48.1325 | 44.0813 | 21.3956 |  |  | 0.37347 | -0.046065 | -30.6605 | 0.11495 | 0.40557 | -197.8532 | 17.5315 | -0.34929 | -0.17524 | -0.4562 | 0.032234 | 8.8281 | 9.0577 | 1.9789 | 21.7923 | 22.0292 | 22.2332 | 22.2929 | 22.1229 | 21.4537 | 20.2805 | 22.2188 | 22.3906 | 22.4263 | 22.3878 | 22.0167 | 21.2669 | 22.3067 | 17.0372 | 17.2122 | 16.2367 | 16.2524 | 16.319 | 17.0975 | 16.7454 | 22.3765 | 22.155 | 21.7223 | 22.0936 | 21.8113 | 21.3239 | 21.9526 | 21.5467 | 20.9349 | 20.1396 | 20.4807 | 20.0726 | 19.8247 | 0.14097 | 0.028371 | 20.7338 | 22.0765 | 22.3993 | 20.0969 | 21.6968 | 22.1512 | 21.9588 | 21.7363 | 21.3022 | 21.81 | 21.4728 | 21.0749 | 20.5152 | 20.5573 | 20.4371 | 20.4705 | 20.0918 |  | 20.2549 | 19.7946 | 20.1168 | 19.6632 | 20.1024 | 20.3344 |  | 20.4457 |  |  | 20.281 | 20.38 | 20.6463 | [5 empty] | 21.9669 | 20.3486 | 21.7003 | 22.0821 | 19.5885 | 21.2108 | 21.851 | 19.3523 | 19.9212 | 21.2173 |  | 19.8141 | 21.003 | 18.9045 | 19.7224 | 20.8941 | 19.4871 | 20.2443 | 19.0569 | 20.2359 | 19.1396 | 20.3542 | 18.8043 | 20.1423 | 21.1036 | 19.433 | 19.7719 | 21.0251 | 18.9345 | 19.7892 | 20.8526 | 18.9854 | 20.2203 | 19.2676 | 19.9642 | 18.9145 | 20.1796 | -0.072663 | 20.9457 | 0.048401 | 0.016756 | -27.0478 | 3.098 | -10.61 | 0.03 | 0.7298 | -0.25462 | -6.569 | 0.40222 | 0.75624 | -16.7031 | 4.9721 | 0.42473 | 0.42836 | 0.43152 | 0.4091 | 0.45697 | 0.43841 | 0.42828
42838.4142 | -526 | 22.886 | 22.8551 | 22.8386 | 22.7631 | 22.4107 | 21.759 | 22.7214 | 21.8198 | 22.3733 | 22.3776 | 22.3695 | 22.0637 | 21.2815 | 22.2477 | 21.5572 | 21.7357 | 21.8769 | 21.0707 | 21.1665 | 21.3904 | 20.4759 | 20.6237 | 20.9225 | 21.8929 | 21.6718 | 21.3095 | 20.4353 | 20.5372 | 20.4894 | 22.0211 | 21.6366 | 21.1716 | 21.9808 | 21.7236 | 21.3547 | 19.9418 | 20.5076 |  | 20.5734 | 20.2293 | 20.2873 | 19.2329 |  | 16.6816 | 16.6385 | 16.3357 | 16.5076 | 16.6015 | 17.1767 | 17.9613 | 15.7891 | 16.7925 | 16.159 | 16.9267 | 17.8603 | 44.8945 | 48.1637 | 44.0933 | 21.3938 |  |  | 0.42539 | -0.004009 | -30.9063 | 0.37123 | 0.21961 | -197.7855 | 17.8876 | -0.57928 | -0.068795 | -0.39872 | 0.04317 | 8.829 | 9.0587 | 1.9787 | 21.7875 | 22.0208 | 22.2245 | 22.2851 | 22.1201 | 21.4526 | 20.2811 | 22.2133 | 22.3885 | 22.425 | 22.3853 | 22.013 | 21.2627 | 22.2935 | 17.0425 | 17.2137 | 16.2666 | 16.2514 | 16.3208 | 17.1007 | 16.7451 | 22.3824 | 22.1669 | 21.7289 | 22.1011 | 21.8187 | 21.3339 | 21.9626 | 21.548 | 20.9397 | 20.1471 | 20.4892 | 20.0879 | 19.8283 | 0.005517 | 0.06603 | 20.7269 | 22.0818 | 22.3996 | 20.0991 | 21.6883 | 22.1445 | 21.9631 | 21.7379 | 21.2966 | 21.8121 | 21.4698 | 21.0692 | 20.5128 | 20.5553 | 20.4314 | 20.4676 | 20.0832 |  | 20.2577 | 19.7915 | 20.1178 | 19.667 | 20.1066 | 20.3413 |  | 20.4577 |  |  | 20.2816 | 20.3835 | 20.6468 | [5 empty] | 21.9715 | 20.3539 | 21.7025 | 22.0899 | 19.5941 | 21.2136 | 21.8507 | 19.3548 | 19.92 | 21.2216 |  | 19.816 | 21.0059 | 18.9016 | 19.7219 | 20.8879 | 19.4798 | 20.2375 | 19.0533 | 20.2296 | 19.1367 | 20.3529 | 18.8025 | 20.1499 | 21.1052 | 19.4323 | 19.7728 | 21.0265 | 18.9373 | 19.7874 | 20.8573 | 18.9844 | 20.2225 | 19.2715 | 19.9589 | 18.9088 | 20.1736 | -0.12293 | 20.9452 | 0.04885 | 0.016807 | -27.0002 | 3.098 | -1.83 | 0.09 | 0.77887 | -0.075115 | -6.5952 | 0.72281 | 0.55646 | -16.6997 | 5.0221 | 0.42506 | 0.42848 | 0.43156 | 0.40889 | 0.45362 | 0.4381 | 0.42844
42838.4142 | -525 | 22.8703 | 22.8593 | 22.8407 | 22.7688 | 22.4166 | 21.7617 | 22.7146 | 21.8274 | 22.3739 | 22.3908 | 22.3756 | 22.0626 | 21.2859 | 22.2511 | 21.5558 | 21.7363 | 21.8812 | 21.0741 | 21.166 | 21.391 | 20.478 | 20.6225 | 20.9247 | 21.8974 | 21.6727 | 21.3102 | 20.4352 | 20.5382 | 20.4951 | 22.0241 | 21.6431 | 21.178 | 21.9903 | 21.7261 | 21.3669 | 19.9486 | 20.5233 |  | 20.581 | 20.2272 | 20.2999 | 19.2528 |  | 16.6747 | 16.6385 | 16.3354 | 16.5034 | 16.5815 | 17.1442 | 17.9503 | 15.7738 | 16.7936 | 16.1157 | 16.9254 | 17.8603 | 44.9225 | 48.1987 | 44.0907 | 21.3977 |  |  | 0.50687 | -0.042121 | -31.5864 | 0.44285 | 0.1677 | -197.8322 | 17.5558 | -0.59899 | 0.11783 | -0.29864 | 0.02772 | 8.829 | 9.0587 | 1.9785 | 21.7895 | 22.0217 | 22.2196 | 22.2865 | 22.1195 | 21.4608 | 20.289 | 22.2149 | 22.3949 | 22.429 | 22.3833 | 22.0226 | 21.2633 | 22.3018 | 17.0382 | 17.2147 | 16.2863 | 16.2411 | 16.3161 | 17.1067 | 16.7464 | 22.3892 | 22.1653 | 21.7296 | 22.1016 | 21.8198 | 21.3333 | 21.9631 | 21.5475 | 20.9359 | 20.1462 | 20.4913 | 20.0838 | 19.8229 | -0.093569 | 0.05595 | 20.7267 | 22.0804 | 22.4007 | 20.0957 | 21.6911 | 22.1374 | 21.9668 | 21.7366 | 21.2963 | 21.8085 | 21.4731 | 21.0728 | 20.5033 | 20.5545 | 20.4287 | 20.4704 | 20.0632 |  | 20.2565 | 19.8075 | 20.115 | 19.6655 | 20.1048 | 20.3437 |  | 20.4587 |  |  | 20.2797 | 20.3922 | 20.6465 | [5 empty] | 21.9641 | 20.3537 | 21.7023 | 22.0885 | 19.5848 | 21.214 | 21.8468 | 19.3532 | 19.9175 | 21.2134 |  | 19.8124 | 21.0016 | 18.8963 | 19.7215 | 20.8815 | 19.4768 | 20.2255 | 19.0559 | 20.2185 | 19.1298 | 20.3429 | 18.7981 | 20.1538 | 21.1046 | 19.4294 | 19.7715 | 21.0255 | 18.9353 | 19.7829 | 20.8515 | 18.9792 | 20.2166 | 19.2642 | 19.9526 | 18.9105 | 20.1688 | -0.04391 | 20.9486 | 0.048708 | 0.015892 | -26.998 | 3.098 | -8.06 | -0.11 | 0.85021 | -0.24348 | -6.6674 | 0.78947 | 0.48624 | -16.7007 | 4.975 | 0.42558 | 0.42794 | 0.43154 | 0.41006 | 0.45158 | 0.43777 | 0.42855
42838.4142 | -524 | 22.8778 | 22.8542 | 22.839 | 22.7717 | 22.415 | 21.7571 | 22.7151 | 21.8287 | 22.3719 | 22.3847 | 22.3745 | 22.0592 | 21.2825 | 22.2509 | 21.56 | 21.7415 | 21.8871 | 21.0744 | 21.1704 | 21.3908 | 20.4773 | 20.623 | 20.9232 | 21.9026 | 21.6689 | 21.3115 | 20.4385 | 20.541 | 20.501 | 22.0267 | 21.6405 | 21.17 | 21.9979 | 21.7285 | 21.3622 | 19.945 | 20.5208 |  | 20.577 | 20.231 | 20.296 | 19.2677 |  | 16.6826 | 16.63 | 16.3335 | 16.4937 | 16.5858 | 17.1358 | 17.9417 | 15.7462 | 16.7913 | 16.1276 | 16.933 | 17.8639 | 44.9447 | 48.2165 | 44.1 | 21.3993 |  |  | 0.32813 | -0.38974 | -31.5969 | 0.28251 | 0.51137 | -197.8703 | 17.3816 | -0.76722 | 0.029283 | -0.20109 | 0.020255 | 8.8291 | 9.0589 | 1.9779 | 21.7964 | 22.0285 | 22.2221 | 22.294 | 22.1252 | 21.4616 | 20.2872 | 22.2188 | 22.3959 | 22.4304 | 22.3754 | 22.0194 | 21.2665 | 22.3079 | 17.0494 | 17.2132 | 16.3177 | 16.2251 | 16.3006 | 17.1001 | 16.7491 | 22.3856 | 22.1577 | 21.7336 | 22.1005 | 21.8255 | 21.332 | 21.9631 | 21.5562 | 20.9435 | 20.1527 | 20.4947 | 20.086 | 19.8206 | 0.081405 | 0.10369 | 20.725 | 22.082 | 22.3999 | 20.1011 | 21.6989 | 22.141 | 21.9682 | 21.7365 | 21.3041 | 21.8149 | 21.4753 | 21.0783 | 20.5115 | 20.5608 | 20.4362 | 20.4621 | 20.0513 |  | 20.2518 | 19.8137 | 20.1188 | 19.6666 | 20.0984 | 20.3413 |  | 20.4518 |  |  | 20.2751 | 20.3937 | 20.6517 | [5 empty] | 21.9643 | 20.349 | 21.6958 | 22.0868 | 19.5774 | 21.2161 | 21.8457 | 19.3598 | 19.9343 | 21.221 |  | 19.8248 | 21.0173 | 18.9098 | 19.7289 | 20.8946 | 19.4841 | 20.2283 | 19.06 | 20.2281 | 19.1404 | 20.3479 | 18.807 | 20.1589 | 21.108 | 19.4321 | 19.7721 | 21.0254 | 18.9384 | 19.7867 | 20.8562 | 18.9865 | 20.2156 | 19.2698 | 19.9674 | 18.9159 | 20.1701 | -0.23182 | 20.9469 | 0.048985 | 0.016226 | -26.9849 | 3.098 | 7.69 | 0.09 | 0.68408 | -0.74061 | -6.6684 | 0.63055 | 0.84908 | -16.7021 | 4.9502 | 0.42575 | 0.42789 | 0.4313 | 0.40805 | 0.4484 | 0.43724 | 0.42883
42838.4142 | -523 | 22.8772 | 22.8526 | 22.841 | 22.7692 | 22.4112 | 21.7625 | 22.7152 | 21.8282 | 22.3718 | 22.3814 | 22.367 | 22.0577 | 21.2811 | 22.2509 | 21.5634 | 21.741 | 21.8879 | 21.083 | 21.1829 | 21.3978 | 20.4807 | 20.6285 | 20.93 | 21.9079 | 21.6799 | 21.3216 | 20.4442 | 20.5488 | 20.5085 | 22.0249 | 21.6408 | 21.1764 | 21.99 | 21.736 | 21.3571 | 19.9445 | 20.5153 |  | 20.5772 | 20.2339 | 20.2977 | 19.2631 |  | 16.6822 | 16.6251 | 16.3287 | 16.4971 | 16.5905 | 17.1559 | 17.9459 | 15.7279 | 16.7967 | 16.1843 | 16.9328 | 17.8634 | 44.9555 | 48.2344 | 44.1028 | 21.4028 |  |  | 0.48781 | -0.30694 | -31.9209 | 0.52762 | 0.51465 | -197.8006 | 16.9972 | -0.53591 | -0.081639 | -0.12514 | 0.05567 | 8.8281 | 9.0579 | 1.9788 | 21.8045 | 22.0283 | 22.227 | 22.2941 | 22.1291 | 21.4757 | 20.2772 | 22.2286 | 22.3982 | 22.4305 | 22.3885 | 22.0254 | 21.2598 | 22.3105 | 17.0685 | 17.1795 | 16.3714 | 16.2319 | 16.2907 | 17.1113 | 16.7505 | 22.3809 | 22.1583 | 21.7264 | 22.093 | 21.8191 | 21.3204 | 21.9559 | 21.5473 | 20.9346 | 20.1451 | 20.4885 | 20.0802 | 19.8127 | 0.0004054 | 0.019622 | 20.7116 | 22.0691 | 22.3829 | 20.0838 | 21.678 | 22.1278 | 21.9555 | 21.7183 | 21.2953 | 21.7915 | 21.4537 | 21.0606 | 20.4939 | 20.547 | 20.4263 | 20.4486 | 20.0628 |  | 20.2525 | 19.8212 | 20.1145 | 19.6688 | 20.0953 | 20.3391 |  | 20.4482 |  |  | 20.2757 | 20.3895 | 20.6508 | [5 empty] | 21.9634 | 20.3476 | 21.6915 | 22.092 | 19.5767 | 21.2151 | 21.8453 | 19.3586 | 19.928 | 21.2162 |  | 19.8119 | 21.0117 | 18.9054 | 19.7231 | 20.8926 | 19.479 | 20.2266 | 19.0414 | 20.2221 | 19.1311 | 20.3443 | 18.8108 | 20.164 | 21.1089 | 19.438 | 19.7785 | 21.0376 | 18.9455 | 19.7921 | 20.8575 | 18.9824 | 20.2165 | 19.2738 | 19.9753 | 18.9127 | 20.1739 | -0.072663 | 20.9446 | 0.049329 | 0.016712 | -27.0313 | 3.0979 | 1.75 | -0.06 | 0.83409 | -0.65724 | -6.7025 | 0.86171 | 0.85183 | -16.6997 | 4.8954 | 0.42545 | 0.42754 | 0.43113 | 0.40723 | 0.4426 | 0.43735 | 0.4288
42838.4142 | -522 | 22.8801 | 22.8539 | 22.8376 | 22.7686 | 22.4082 | 21.7668 | 22.7118 | 21.823 | 22.3727 | 22.3817 | 22.3698 | 22.0589 | 21.2763 | 22.2479 | 21.5627 | 21.7429 | 21.8911 | 21.082 | 21.1804 | 21.3982 | 20.4806 | 20.6315 | 20.9305 | 21.9152 | 21.6782 | 21.3162 | 20.4455 | 20.5445 | 20.5024 | 22.0218 | 21.6387 | 21.1695 | 21.9829 | 21.7339 | 21.3554 | 19.942 | 20.5115 |  | 20.5704 | 20.2288 | 20.2955 | 19.2397 |  | 16.6665 | 16.6145 | 16.3128 | 16.4768 | 16.5898 | 17.18 | 17.9597 | 15.7021 | 16.7954 | 16.1624 | 16.9254 | 17.8632 | 44.9523 | 48.2495 | 44.108 | 21.4014 |  |  | 0.51212 | -0.20837 | -31.8407 | 0.64393 | 0.15521 | -197.8118 | 17.3271 | -0.48334 | 0.040181 | -0.26256 | -0.1056 | 8.8279 | 9.0577 | 1.9789 | 21.7867 | 22.022 | 22.2133 | 22.2857 | 22.116 | 21.4553 | 20.2794 | 22.2072 | 22.3753 | 22.4253 | 22.3792 | 22.0153 | 21.2507 | 22.2969 | 17.0812 | 17.1436 | 16.3779 | 16.2232 | 16.2686 | 17.1118 | 16.7525 | 22.386 | 22.1662 | 21.7336 | 22.105 | 21.8221 | 21.3258 | 21.9616 | 21.5527 | 20.9328 | 20.1432 | 20.4913 | 20.0856 | 19.817 | -0.070174 | -0.12075 | 20.7191 | 22.0683 | 22.3908 | 20.0973 | 21.6899 | 22.1382 | 21.9572 | 21.7172 | 21.2954 | 21.8083 | 21.4652 | 21.0667 | 20.5015 | 20.5569 | 20.4373 | 20.4634 | 20.0612 |  | 20.2622 | 19.8263 | 20.1135 | 19.6803 | 20.1103 | 20.3441 |  | 20.4539 |  |  | 20.2803 | 20.3891 | 20.6485 | [5 empty] | 21.963 | 20.3465 | 21.7045 | 22.0905 | 19.5836 | 21.2191 | 21.8504 | 19.361 | 19.9273 | 21.2179 |  | 19.8092 | 21.0107 | 18.9022 | 19.7176 | 20.8887 | 19.4806 | 20.2276 | 19.0343 | 20.214 | 19.1315 | 20.3385 | 18.8166 | 20.1687 | 21.1114 | 19.4465 | 19.7876 | 21.0416 | 18.9482 | 19.7969 | 20.8642 | 18.9819 | 20.2243 | 19.2781 | 19.9718 | 18.9218 | 20.1826 | -0.045766 | 20.9458 | 0.049138 | 0.015631 | -27.0484 | 3.0981 | 4.22 | -0.29 | 0.85461 | -0.54151 | -6.6939 | 0.95194 | 0.46782 | -16.7009 | 4.9428 | 0.42582 | 0.42736 | 0.43131 | 0.40587 | 0.4421 | 0.43792 | 0.42862
42838.4142 | -521 | 22.874 | 22.8452 | 22.836 | 22.7613 | 22.4006 | 21.7539 | 22.7057 | 21.8189 | 22.3694 | 22.3751 | 22.3671 | 22.0541 | 21.2737 | 22.2413 | 21.561 | 21.7364 | 21.8854 | 21.0761 | 21.1731 | 21.3943 | 20.4786 | 20.6255 | 20.9244 | 21.9081 | 21.6662 | 21.3043 | 20.4408 | 20.5408 | 20.5011 | 22.0273 | 21.6416 | 21.1716 | 21.9856 | 21.7338 | 21.3623 | 19.9441 | 20.511 |  | 20.576 | 20.2294 | 20.2996 | 19.2231 |  | 16.6674 | 16.6139 | 16.3248 | 16.4989 | 16.5998 | 17.1824 | 17.9303 | 15.6906 | 16.7979 | 16.1326 | 16.933 | 17.8676 | 44.9802 | 48.2756 | 44.1131 | 21.4039 |  |  | 0.50555 | -0.26751 | -31.9333 | 0.61699 | 0.078328 | -197.8158 | 17.358 | -0.56548 | 0.15169 | 0.20865 | -0.11359 | 8.8286 | 9.0583 | 1.9789 | 21.7967 | 22.0297 | 22.2255 | 22.2887 | 22.1258 | 21.4627 | 20.2805 | 22.2203 | 22.3861 | 22.4303 | 22.3824 | 22.0163 | 21.2656 | 22.2964 | 17.1042 | 17.1227 | 16.3693 | 16.2226 | 16.2613 | 17.1104 | 16.7463 | 22.3809 | 22.1611 | 21.7293 | 22.0937 | 21.8131 | 21.3165 | 21.9548 | 21.5423 | 20.92 | 20.1397 | 20.48 | 20.0776 | 19.8005 | -0.070174 | -0.10515 | 20.721 | 22.0797 | 22.3855 | 20.0932 | 21.6848 | 22.1364 | 21.9631 | 21.7274 | 21.2995 | 21.8078 | 21.462 | 21.0653 | 20.5 | 20.5526 | 20.4331 | 20.4481 | 20.0599 |  | 20.2565 | 19.8255 | 20.1152 | 19.6703 | 20.1012 | 20.3502 |  | 20.4479 |  |  | 20.2772 | 20.3828 | 20.6495 | [5 empty] | 21.9617 | 20.345 | 21.7012 | 22.0848 | 19.5724 | 21.215 | 21.8437 | 19.3616 | 19.9222 | 21.2162 |  | 19.8119 | 21.0152 | 18.9049 | 19.7221 | 20.8874 | 19.48 | 20.229 | 19.0364 | 20.2184 | 19.1364 | 20.3399 | 18.8193 | 20.171 | 21.1167 | 19.4498 | 19.7927 | 21.047 | 18.9538 | 19.801 | 20.8678 | 18.9765 | 20.2317 | 19.2788 | 19.9651 | 18.9186 | 20.1783 | -0.24147 | 20.9462 | 0.048512 | 0.016023 | -27.0866 | 3.098 | -12.97 | -0.24 | 0.84912 | -0.61357 | -6.7036 | 0.93181 | 0.33233 | -16.7011 | 4.9473 | 0.42567 | 0.42744 | 0.43128 | 0.40316 | 0.44234 | 0.43845 | 0.42896
42838.4143 | -520 | 22.8931 | 22.8581 | 22.8529 | 22.7769 | 22.425 | 21.7661 | 22.7228 | 21.834 | 22.3778 | 22.3953 | 22.3804 | 22.0622 | 21.2896 | 22.2546 | 21.5662 | 21.7405 | 21.8875 | 21.0785 | 21.1699 | 21.3964 | 20.4844 | 20.6273 | 20.9272 | 21.9018 | 21.6674 | 21.311 | 20.4308 | 20.5386 | 20.5047 | 22.0316 | 21.6486 | 21.1734 | 21.9891 | 21.742 | 21.3592 | 19.9444 | 20.5146 |  | 20.5789 | 20.2313 | 20.2975 | 19.2005 |  | 16.6655 | 16.6218 | 16.335 | 16.525 | 16.6118 | 17.1711 | 17.8949 | 15.6823 | 16.7908 | 16.1375 | 16.9298 | 17.8665 | 45.0106 | 48.2902 | 44.1069 | 21.4 |  |  | 0.47401 | -0.34045 | -30.9188 | 0.34034 | 0.21238 | -197.8453 | 17.6458 | -0.45048 | -0.14119 | -0.07185 | -0.19883 | 8.8285 | 9.0583 | 1.9787 | 21.7946 | 22.027 | 22.2212 | 22.286 | 22.1195 | 21.4585 | 20.2804 | 22.2154 | 22.3853 | 22.4283 | 22.3772 | 22.021 | 21.2655 | 22.3053 | 17.1458 | 17.0833 | 16.3361 | 16.2219 | 16.2715 | 17.1113 | 16.7483 | 22.3907 | 22.1649 | 21.7317 | 22.1083 | 21.8212 | 21.3332 | 21.9716 | 21.551 | 20.9375 | 20.1528 | 20.49 | 20.084 | 19.8254 | -0.16022 | -0.17895 | 20.7212 | 22.0818 | 22.3899 | 20.0884 | 21.6877 | 22.1432 | 21.962 | 21.7311 | 21.3048 | 21.8021 | 21.4675 | 21.07 | 20.498 | 20.5598 | 20.4362 | 20.447 | 20.0484 |  | 20.2516 | 19.8186 | 20.1102 | 19.6741 | 20.0968 | 20.3491 |  | 20.4534 |  |  | 20.2708 | 20.3828 | 20.6433 | [5 empty] | 21.953 | 20.3371 | 21.6979 | 22.0821 | 19.5525 | 21.2057 | 21.8445 | 19.3627 | 19.923 | 21.2194 |  | 19.8026 | 21.0066 | 18.8967 | 19.7171 | 20.8852 | 19.4817 | 20.2317 | 19.0422 | 20.2168 | 19.1363 | 20.3354 | 18.8244 | 20.1726 | 21.112 | 19.4539 | 19.7909 | 21.0398 | 18.9548 | 19.7954 | 20.8566 | 18.9708 | 20.2322 | 19.2831 | 19.9631 | 18.9211 | 20.1827 | -0.13332 | 20.9462 | 0.047971 | 0.015507 | -26.9901 | 3.098 | -8.31 | 0.08 | 0.8222 | -0.69219 | -6.5964 | 0.69207 | 0.54722 | -16.702 | 4.988 | 0.42582 | 0.42747 | 0.43103 | 0.39863 | 0.44627 | 0.43908 | 0.42871
42838.4143 | -519 | 22.89 | 22.8599 | 22.8462 | 22.7735 | 22.4224 | 21.76 | 22.7192 | 21.8256 | 22.3771 | 22.3839 | 22.3673 | 22.0667 | 21.2882 | 22.2524 | 21.56 | 21.7392 | 21.8788 | 21.0645 | 21.1635 | 21.3906 | 20.4767 | 20.628 | 20.9218 | 21.8951 | 21.6715 | 21.3053 | 20.4277 | 20.5294 | 20.4941 | 22.0245 | 21.6426 | 21.1759 | 21.9919 | 21.7306 | 21.3597 | 19.9375 | 20.5133 |  | 20.5686 | 20.2245 | 20.2886 | 19.1935 |  | 16.662 | 16.6321 | 16.3464 | 16.5403 | 16.6154 | 17.1624 | 17.8518 | 15.6973 | 16.7812 | 16.1354 | 16.9273 | 17.8662 | 45.039 | 48.3154 | 44.1134 | 21.4036 |  |  | 0.58375 | -0.29183 | -31.0666 | 0.072894 | 0.20581 | -197.8276 | 17.4894 | -0.52868 | -0.21105 | 0.092633 | -0.10786 | 8.8291 | 9.0584 | 1.9783 | 21.794 | 22.0239 | 22.2182 | 22.2886 | 22.1244 | 21.4622 | 20.2764 | 22.2142 | 22.3887 | 22.4236 | 22.3823 | 22.0199 | 21.2627 | 22.3035 | 17.1789 | 17.0426 | 16.2903 | 16.2278 | 16.2793 | 17.1096 | 16.7518 | 22.3833 | 22.1573 | 21.7233 | 22.0879 | 21.813 | 21.3202 | 21.9557 | 21.5516 | 20.9265 | 20.135 | 20.4826 | 20.0814 | 19.8222 | -0.089048 | -0.03934 | 20.7234 | 22.0847 | 22.392 | 20.0941 | 21.6929 | 22.1411 | 21.9584 | 21.7238 | 21.3034 | 21.8073 | 21.4737 | 21.0721 | 20.4979 | 20.5611 | 20.4273 | 20.4474 | 20.0403 |  | 20.25 | 19.8296 | 20.1132 | 19.681 | 20.0967 | 20.3448 |  | 20.4502 |  |  | 20.263 | 20.3888 | 20.6381 | [5 empty] | 21.95 | 20.3374 | 21.6925 | 22.0804 | 19.5491 | 21.2095 | 21.8437 | 19.3713 | 19.9282 | 21.2157 |  | 19.7932 | 20.9998 | 18.8897 | 19.7169 | 20.8778 | 19.4865 | 20.2269 | 19.0463 | 20.2169 | 19.1284 | 20.3332 | 18.8167 | 20.1765 | 21.1138 | 19.4484 | 19.7822 | 21.0401 | 18.9467 | 19.7825 | 20.854 | 18.9662 | 20.2251 | 19.2806 | 19.9584 | 18.9013 | 20.1783 | -0.12349 | 20.9449 | 0.046558 | 0.014273 | -26.9863 | 3.098 | -5.89 | -0.35 | 0.91241 | -0.64086 | -6.6123 | 0.32029 | 0.53868 | -16.701 | 4.9658 | 0.426 | 0.42726 | 0.43084 | 0.39477 | 0.45176 | 0.43905 | 0.4282
42838.4143 | -518 | 22.881 | 22.8462 | 22.8407 | 22.7686 | 22.4103 | 21.7505 | 22.7133 | 21.8231 | 22.3702 | 22.3884 | 22.3687 | 22.0567 | 21.2826 | 22.247 | 21.5739 | 21.7433 | 21.8861 | 21.0726 | 21.1755 | 21.4047 | 20.4865 | 20.629 | 20.9336 | 21.9065 | 21.6697 | 21.3116 | 20.4407 | 20.5421 | 20.5053 | 22.0167 | 21.6401 | 21.1755 | 21.9808 | 21.7327 | 21.349 | 19.9431 | 20.5204 |  | 20.5665 | 20.2183 | 20.2865 | 19.1887 |  | 16.6664 | 16.6412 | 16.344 | 16.5284 | 16.6116 | 17.1489 | 17.8281 | 15.7358 | 16.7796 | 16.0773 | 16.9224 | 17.8636 | 45.0588 | 48.3329 | 44.0998 | 21.3962 |  |  | 0.59361 | -0.22677 | -31.4589 | 0.32391 | 0.34249 | -197.8604 | 17.3389 | -0.56285 | -0.19626 | -0.48662 | -0.050053 | 8.8281 | 9.058 | 1.9781 | 21.7936 | 22.018 | 22.2096 | 22.2844 | 22.1155 | 21.4563 | 20.2764 | 22.2063 | 22.3784 | 22.4183 | 22.3846 | 22.015 | 21.2563 | 22.2964 | 17.1737 | 17.0264 | 16.2907 | 16.235 | 16.2926 | 17.109 | 16.7524 | 22.3877 | 22.1543 | 21.7231 | 22.0912 | 21.8167 | 21.3273 | 21.9573 | 21.5453 | 20.9238 | 20.1368 | 20.4826 | 20.0829 | 19.8267 | 0.029502 | -0.047329 | 20.7259 | 22.0856 | 22.3987 | 20.096 | 21.6974 | 22.1469 | 21.9678 | 21.7349 | 21.3052 | 21.8056 | 21.4681 | 21.0717 | 20.5001 | 20.5704 | 20.4273 | 20.4517 | 19.9938 |  | 20.2527 | 19.8418 | 20.1154 | 19.6769 | 20.1021 | 20.3532 |  | 20.4435 |  |  | 20.2696 | 20.3949 | 20.6442 | [5 empty] | 21.9663 | 20.3369 | 21.6933 | 22.0802 | 19.5607 | 21.2103 | 21.847 | 19.373 | 19.9334 | 21.2191 |  | 19.8037 | 21.007 | 18.8775 | 19.7157 | 20.876 | 19.4864 | 20.2304 | 19.0415 | 20.2176 | 19.1396 | 20.3448 | 18.8195 | 20.1826 | 21.1094 | 19.4542 | 19.7881 | 21.0514 | 18.9566 | 19.786 | 20.8578 | 18.9659 | 20.2246 | 19.2824 | 19.9626 | 18.9171 | 20.1809 | -0.06784 | 20.9457 | 0.046564 | 0.013925 | -26.9156 | 3.0979 | 9.72 | 0.05 | 0.9201 | -0.56494 | -6.654 | 0.67519 | 0.69488 | -16.702 | 4.9443 | 0.42738 | 0.427 | 0.43113 | 0.39527 | 0.45178 | 0.43937 | 0.42813
42838.4143 | -517 | 22.8796 | 22.848 | 22.8391 | 22.7777 | 22.4137 | 21.7566 | 22.7155 | 21.8181 | 22.3679 | 22.3858 | 22.3721 | 22.0594 | 21.2795 | 22.2493 | 21.5724 | 21.7325 | 21.8839 | 21.0586 | 21.1745 | 21.3959 | 20.4842 | 20.6248 | 20.9195 | 21.9027 | 21.6658 | 21.3122 | 20.4402 | 20.5426 | 20.4985 | 22.0241 | 21.6421 | 21.1739 | 21.9938 | 21.7238 | 21.3508 | 19.9426 | 20.5111 |  | 20.5702 | 20.2184 | 20.2939 | 19.1897 |  | 16.6749 | 16.6359 | 16.3441 | 16.5354 | 16.6083 | 17.1404 | 17.824 | 15.7697 | 16.781 | 16.0448 | 16.9305 | 17.8611 | 45.0637 | 48.3527 | 44.0954 | 21.3959 |  |  | 0.39516 | -0.29577 | -32.4551 | -0.14921 | 0.28598 | -197.8348 | 17.1037 | -0.63251 | -0.076384 | -0.12367 | -0.074183 | 8.8297 | 9.0595 | 1.9788 | 21.7926 | 22.0176 | 22.2072 | 22.2742 | 22.1119 | 21.4568 | 20.2769 | 22.2117 | 22.3845 | 22.4203 | 22.3835 | 22.0157 | 21.2613 | 22.2947 | 17.1582 | 17.0133 | 16.31 | 16.2374 | 16.2794 | 17.1009 | 16.7485 | 22.3885 | 22.1552 | 21.7276 | 22.0987 | 21.8158 | 21.329 | 21.957 | 21.5519 | 20.9349 | 20.1434 | 20.4893 | 20.0791 | 19.8397 | -0.19639 | 0.013916 | 20.7197 | 22.0786 | 22.4032 | 20.0858 | 21.6856 | 22.1483 | 21.9622 | 21.7291 | 21.306 | 21.8119 | 21.4714 | 21.0673 | 20.4993 | 20.5586 | 20.4169 | 20.4471 | 19.9788 |  | 20.2554 | 19.8391 | 20.1206 | 19.6715 | 20.1055 | 20.3461 |  | 20.4473 |  |  | 20.2677 | 20.4001 | 20.6377 | [5 empty] | 21.9571 | 20.3402 | 21.6935 | 22.0844 | 19.5718 | 21.2134 | 21.8452 | 19.3707 | 19.9406 | 21.2323 |  | 19.7875 | 21.0131 | 18.8817 | 19.7278 | 20.8952 | 19.4905 | 20.2354 | 19.0527 | 20.219 | 19.1337 | 20.3338 | 18.8287 | 20.1916 | 21.113 | 19.4654 | 19.7891 | 21.0511 | 18.9606 | 19.796 | 20.8609 | 18.9745 | 20.233 | 19.2863 | 19.9696 | 18.9255 | 20.1856 | -0.18155 | 20.9462 | 0.04778 | 0.014215 | -27.0671 | 3.0979 | 7.75 | -0.06 | 0.7507 | -0.64518 | -6.7584 | -0.45825 | 0.63496 | -16.7007 | 4.9105 | 0.42788 | 0.42725 | 0.4314 | 0.39606 | 0.44919 | 0.43933 | 0.428
42838.4143 | -516 | 22.8881 | 22.8565 | 22.8467 | 22.7759 | 22.4168 | 21.7616 | 22.7215 | 21.8281 | 22.3758 | 22.3896 | 22.3738 | 22.0647 | 21.2881 | 22.2498 | 21.5584 | 21.7347 | 21.8787 | 21.0627 | 21.162 | 21.3889 | 20.4751 | 20.6169 | 20.9149 | 21.8977 | 21.6754 | 21.3033 | 20.4277 | 20.5341 | 20.4972 | 22.0212 | 21.6448 | 21.1698 | 21.9945 | 21.7311 | 21.35 | 19.9413 | 20.5067 |  | 20.5695 | 20.2171 | 20.2949 | 19.1828 |  | 16.6703 | 16.6318 | 16.3442 | 16.5282 | 16.6028 | 17.139 | 17.8288 | 15.7776 | 16.777 | 16.0379 | 16.9272 | 17.8627 | 45.0634 | 48.3733 | 44.0987 | 21.3931 |  |  | 0.50884 | -0.48502 | -32.2336 | 0.40211 | 0.30569 | -197.7993 | 17.1773 | -0.49648 | -0.20716 | -0.20109 | 0.074592 | 8.8285 | 9.0581 | 1.9786 | 21.7886 | 22.0247 | 22.2206 | 22.2835 | 22.1161 | 21.4556 | 20.2844 | 22.2202 | 22.3889 | 22.4262 | 22.3856 | 22.0151 | 21.2583 | 22.2958 | 17.1696 | 16.9951 | 16.2993 | 16.2455 | 16.2798 | 17.1013 | 16.7459 | 22.393 | 22.1589 | 21.7294 | 22.0947 | 21.8211 | 21.3267 | 21.9621 | 21.5516 | 20.9299 | 20.141 | 20.4895 | 20.0754 | 19.8455 | -0.028102 | -0.10135 | 20.7225 | 22.0724 | 22.3965 | 20.0906 | 21.687 | 22.1433 | 21.9619 | 21.7319 | 21.2996 | 21.7995 | 21.469 | 21.0641 | 20.5005 | 20.5547 | 20.4285 | 20.4427 | 19.9879 |  | 20.2533 | 19.841 | 20.125 | 19.6529 | 20.0986 | 20.3398 |  | 20.4388 |  |  | 20.265 | 20.3952 | 20.6427 | [5 empty] | 21.961 | 20.3448 | 21.6995 | 22.0827 | 19.561 | 21.2078 | 21.8449 | 19.377 | 19.94 | 21.232 |  | 19.7888 | 21.0152 | 18.8714 | 19.7316 | 20.8735 | 19.4885 | 20.2239 | 19.0374 | 20.2118 | 19.1354 | 20.3334 | 18.8291 | 20.1993 | 21.1271 | 19.4717 | 19.7952 | 21.0468 | 18.963 | 19.796 | 20.8649 | 18.9861 | 20.233 | 19.2961 | 19.9681 | 18.9206 | 20.1861 | -0.073405 | 20.9457 | 0.047952 | 0.015645 | -26.9698 | 3.0979 | 7.32 | -0.03 | 0.85186 | -0.82619 | -6.7353 | 0.75227 | 0.65648 | -16.6992 | 4.9211 | 0.42756 | 0.42734 | 0.43168 | 0.39483 | 0.45008 | 0.43947 | 0.42775
42838.4143 | -515 | 22.892 | 22.8618 | 22.8508 | 22.7769 | 22.4178 | 21.7682 | 22.7242 | 21.836 | 22.381 | 22.3915 | 22.3745 | 22.0634 | 21.2854 | 22.2571 | 21.568 | 21.738 | 21.8841 | 21.0782 | 21.1755 | 21.4009 | 20.4803 | 20.6243 | 20.9217 | 21.9021 | 21.6669 | 21.3124 | 20.4373 | 20.5406 | 20.5019 | 22.0222 | 21.6501 | 21.1716 | 21.991 | 21.7361 | 21.3574 | 19.9468 | 20.5116 |  | 20.5791 | 20.2235 | 20.3013 | 19.176 |  | 16.6711 | 16.6282 | 16.342 | 16.5327 | 16.6137 | 17.1542 | 17.8582 | 15.7893 | 16.7778 | 16.0397 | 16.9292 | 17.8618 | 45.0719 | 48.3929 | 44.107 | 21.3951 |  |  | 0.55221 | -0.53693 | -32.3736 | 0.3824 | 0.51202 | -197.8322 | 17.471 | -0.25204 | -0.11939 | -0.15409 | 0.051156 | 8.829 | 9.0589 | 1.9786 | 21.7928 | 22.0194 | 22.2262 | 22.2853 | 22.1232 | 21.4492 | 20.2812 | 22.2159 | 22.3925 | 22.4252 | 22.3757 | 22.0162 | 21.2616 | 22.2977 | 17.1986 | 16.9893 | 16.2847 | 16.2677 | 16.2865 | 17.1054 | 16.7496 | 22.3812 | 22.1547 | 21.7274 | 22.0927 | 21.8209 | 21.3218 | 21.9602 | 21.549 | 20.9314 | 20.1451 | 20.4859 | 20.0732 | 19.8401 | 0.037366 | -0.34195 | 20.7256 | 22.0748 | 22.3893 | 20.0877 | 21.688 | 22.1482 | 21.9529 | 21.723 | 21.3011 | 21.8033 | 21.4712 | 21.0633 | 20.5017 | 20.5486 | 20.4187 | 20.4383 | 19.9935 |  | 20.2546 | 19.8407 | 20.1256 | 19.6701 | 20.1053 | 20.3529 |  | 20.4449 |  |  | 20.273 | 20.4086 | 20.6526 | [5 empty] | 21.9646 | 20.3545 | 21.7038 | 22.0874 | 19.5611 | 21.2177 | 21.8591 | 19.3775 | 19.9333 | 21.2297 |  | 19.7937 | 21.0119 | 18.8794 | 19.7163 | 20.8843 | 19.4917 | 20.2297 | 19.043 | 20.2113 | 19.1311 | 20.3349 | 18.8292 | 20.2093 | 21.1223 | 19.4755 | 19.793 | 21.0494 | 18.9675 | 19.7981 | 20.8669 | 18.9839 | 20.2323 | 19.289 | 19.9638 | 18.9177 | 20.1821 | -0.15224 | 20.9447 | 0.048653 | 0.016103 | -26.9756 | 3.0979 | 3.03 | -0.31 | 0.88743 | -0.86928 | -6.7499 | 0.7336 | 0.84965 | -16.701 | 4.9631 | 0.42745 | 0.42737 | 0.43143 | 0.39209 | 0.45213 | 0.43984 | 0.42804
42838.4143 | -514 | 22.8822 | 22.8518 | 22.8454 | 22.7702 | 22.4083 | 21.7615 | 22.7248 | 21.8247 | 22.3684 | 22.3849 | 22.3722 | 22.0555 | 21.2841 | 22.2535 | 21.5704 | 21.7408 | 21.8912 | 21.0809 | 21.1752 | 21.4008 | 20.4884 | 20.6279 | 20.9301 | 21.9042 | 21.6793 | 21.3155 | 20.4356 | 20.5424 | 20.5095 | 22.0306 | 21.649 | 21.1746 | 21.9946 | 21.733 | 21.3649 | 19.9446 | 20.5156 |  | 20.5743 | 20.2241 | 20.3016 | 19.1641 |  | 16.6718 | 16.6333 | 16.3533 | 16.5488 | 16.6454 | 17.2188 | 17.8826 | 15.813 | 16.7844 | 16.0592 | 16.9295 | 17.8627 | 45.0858 | 48.4066 | 44.1122 | 21.3956 |  |  | 0.46744 | -0.28723 | -33.7424 | 0.41328 | 0.33263 | -197.8361 | 16.7383 | -0.46888 | 0.12483 | -0.18808 | -0.022624 | 8.8291 | 9.0591 | 1.9784 | 21.7963 | 22.0314 | 22.2136 | 22.2844 | 22.1163 | 21.4539 | 20.2819 | 22.2164 | 22.3921 | 22.4253 | 22.3843 | 22.0186 | 21.2681 | 22.2985 | 17.2171 | 17.0171 | 16.2585 | 16.2697 | 16.2775 | 17.1011 | 16.7508 | 22.3845 | 22.1595 | 21.7273 | 22.0962 | 21.8195 | 21.3257 | 21.963 | 21.554 | 20.9373 | 20.1412 | 20.4863 | 20.0771 | 19.8453 | 0.055453 | -0.2731 | 20.7176 | 22.0789 | 22.395 | 20.0846 | 21.6917 | 22.1417 | 21.9629 | 21.7287 | 21.3019 | 21.8008 | 21.4674 | 21.0687 | 20.5017 | 20.5646 | 20.4194 | 20.4416 | 20.0039 |  | 20.2573 | 19.8326 | 20.1236 | 19.6602 | 20.1046 | 20.3508 |  | 20.4404 |  |  | 20.2505 | 20.3905 | 20.6397 | [5 empty] | 21.9507 | 20.3411 | 21.6976 | 22.0781 | 19.5541 | 21.2114 | 21.8494 | 19.3848 | 19.9423 | 21.2313 |  | 19.7962 | 21.0154 | 18.8816 | 19.7181 | 20.8895 | 19.4921 | 20.2322 | 19.0474 | 20.215 | 19.1349 | 20.3277 | 18.8392 | 20.2076 | 21.1225 | 19.4737 | 19.7909 | 21.0514 | 18.9643 | 19.7978 | 20.868 | 18.989 | 20.2282 | 19.2864 | 19.9714 | 18.9174 | 20.1857 | -0.27708 | 20.9474 | 0.048751 | 0.014999 | -27.0256 | 3.0979 | -7.12 | -0.2 | 0.81649 | -0.63579 | -6.8911 | 0.76265 | 0.68489 | -16.703 | 4.8585 | 0.42725 | 0.42753 | 0.43168 | 0.38953 | 0.45517 | 0.4401 | 0.42776
42838.4143 | -513 | 22.888 | 22.858 | 22.8396 | 22.775 | 22.4182 | 21.7636 | 22.7241 | 21.8346 | 22.3695 | 22.3882 | 22.3738 | 22.0569 | 21.2937 | 22.2513 | 21.5727 | 21.7481 | 21.8876 | 21.0791 | 21.1728 | 21.4011 | 20.4861 | 20.63 | 20.9281 | 21.9098 | 21.6802 | 21.313 | 20.4357 | 20.5401 | 20.5102 | 22.0332 | 21.639 | 21.174 | 21.9941 | 21.7267 | 21.358 | 19.9397 | 20.5068 |  | 20.5704 | 20.2183 | 20.2967 | 19.1398 |  | 16.6697 | 16.6369 | 16.3663 | 16.5667 | 16.6687 | 17.2617 | 17.8958 | 15.8184 | 16.7797 | 16.0527 | 16.9237 | 17.8709 | 45.1007 | 48.4278 | 44.1347 | 21.3985 |  |  | 0.40041 | -0.26029 | -34.1005 | 0.47439 | 0.2886 | -197.8473 | 16.4985 | -0.44523 | -0.11803 | -0.043527 | -0.055261 | 8.8292 | 9.0589 | 1.9781 | 21.7974 | 22.0264 | 22.2135 | 22.2888 | 22.1203 | 21.4551 | 20.2821 | 22.2141 | 22.3818 | 22.4298 | 22.382 | 22.0163 | 21.2636 | 22.3015 | 17.223 | 17.0598 | 16.2545 | 16.2794 | 16.3031 | 17.0981 | 16.7479 | 22.3803 | 22.1539 | 21.7225 | 22.0943 | 21.8096 | 21.3264 | 21.9593 | 21.5454 | 20.9317 | 20.1415 | 20.4778 | 20.0659 | 19.8458 | 0.052308 | -0.12512 | 20.7285 | 22.079 | 22.3958 | 20.0812 | 21.6936 | 22.1449 | 21.9628 | 21.7335 | 21.3041 | 21.8018 | 21.4736 | 21.0666 | 20.498 | 20.5654 | 20.4259 | 20.4439 | 19.9975 |  | 20.2512 | 19.8114 | 20.1162 | 19.654 | 20.0992 | 20.3362 |  | 20.4376 |  |  | 20.2543 | 20.3941 | 20.6418 | [5 empty] | 21.9609 | 20.35 | 21.7078 | 22.0917 | 19.5601 | 21.2151 | 21.8486 | 19.387 | 19.9359 | 21.2242 |  | 19.7981 | 21.0122 | 18.8751 | 19.7237 | 20.8783 | 19.4933 | 20.2263 | 19.0269 | 20.2109 | 19.1313 | 20.323 | 18.8502 | 20.2098 | 21.1253 | 19.4719 | 19.8019 | 21.0594 | 18.9706 | 19.8063 | 20.8693 | 18.9927 | 20.2309 | 19.2937 | 19.9696 | 18.9275 | 20.1917 | -0.19565 | 20.9456 | 0.048413 | 0.01521 | -27.0847 | 3.0979 | -19.26 | -0.12 | 0.75569 | -0.60524 | -6.9277 | 0.8171 | 0.63801 | -16.7047 | 4.8239 | 0.42722 | 0.42787 | 0.43167 | 0.38853 | 0.45529 | 0.44061 | 0.42776
42838.4144 | -512 | 22.8898 | 22.8561 | 22.8445 | 22.7797 | 22.4183 | 21.7545 | 22.7261 | 21.8316 | 22.3767 | 22.3965 | 22.3723 | 22.0614 | 21.2872 | 22.2476 | 21.571 | 21.7463 | 21.8841 | 21.075 | 21.1781 | 21.4045 | 20.4849 | 20.6297 | 20.9293 | 21.9089 | 21.6757 | 21.3155 | 20.44 | 20.5351 | 20.5081 | 22.0219 | 21.6384 | 21.169 | 21.9887 | 21.7242 | 21.3483 | 19.9386 | 20.5083 |  | 20.5723 | 20.2116 | 20.2919 | 19.1331 |  | 16.6801 | 16.64 | 16.3869 | 16.5939 | 16.6959 | 17.2849 | 17.8764 | 15.7971 | 16.7765 | 16.0575 | 16.919 | 17.8602 | 45.0851 | 48.4366 | 44.1451 | 21.3752 |  |  | 0.34587 | -0.1696 | -34.7445 | 0.46059 | 0.0849 | -197.8066 | 16.344 | -0.37886 | -0.024621 | 0.12998 | -0.016895 | 8.8289 | 9.0588 | 1.9782 | 21.795 | 22.0325 | 22.209 | 22.292 | 22.1286 | 21.4611 | 20.2869 | 22.2112 | 22.3846 | 22.4275 | 22.386 | 22.0144 | 21.2598 | 22.3058 | 17.2338 | 17.0793 | 16.255 | 16.2748 | 16.3173 | 17.1018 | 16.7524 | 22.3829 | 22.1625 | 21.7252 | 22.1034 | 21.8101 | 21.3281 | 21.956 | 21.5534 | 20.9236 | 20.1377 | 20.474 | 20.0644 | 19.8528 | 0.067053 | -0.12018 | 20.728 | 22.0854 | 22.398 | 20.077 | 21.692 | 22.1449 | 21.9646 | 21.7382 | 21.3042 | 21.806 | 21.4732 | 21.0739 | 20.5025 | 20.5803 | 20.4311 | 20.4495 | 20.0147 |  | 20.2597 | 19.797 | 20.1227 | 19.671 | 20.1102 | 20.351 |  | 20.4574 |  |  | 20.2505 | 20.3917 | 20.637 | [5 empty] | 21.959 | 20.3564 | 21.7059 | 22.093 | 19.5692 | 21.2128 | 21.8469 | 19.3955 | 19.9403 | 21.2331 |  | 19.8027 | 21.02 | 18.8813 | 19.7329 | 20.8926 | 19.4958 | 20.2281 | 19.024 | 20.2204 | 19.1369 | 20.3358 | 18.8486 | 20.2123 | 21.1305 | 19.4781 | 19.8048 | 21.0667 | 18.9774 | 19.8021 | 20.8731 | 18.9898 | 20.234 | 19.3022 | 19.9759 | 18.9258 | 20.1967 | -0.1003 | 20.9453 | 0.048512 | 0.014731 | -27.0302 | 3.0979 | 2.25 | -0.12 | 0.70234 | -0.48857 | -6.9928 | 0.80513 | 0.34606 | -16.7037 | 4.8014 | 0.42703 | 0.42849 | 0.43157 | 0.38775 | 0.45575 | 0.44076 | 0.42744
42838.4144 | -511 | 22.8839 | 22.8599 | 22.8473 | 22.7718 | 22.4151 | 21.7576 | 22.7191 | 21.8336 | 22.3684 | 22.389 | 22.3792 | 22.0592 | 21.281 | 22.2494 | 21.5667 | 21.7415 | 21.881 | 21.0695 | 21.172 | 21.3946 | 20.4775 | 20.6258 | 20.9262 | 21.899 | 21.6734 | 21.3114 | 20.4446 | 20.536 | 20.5067 | 22.0157 | 21.6331 | 21.163 | 21.9831 | 21.7225 | 21.3532 | 19.9342 | 20.5031 |  | 20.57 | 20.2063 | 20.2957 | 19.1161 |  | 16.6862 | 16.6588 | 16.4082 | 16.6105 | 16.6995 | 17.2914 | 17.8848 | 15.7607 | 16.786 | 16.1016 | 16.9271 | 17.8633 | 45.0878 | 48.447 | 44.1637 | 21.3613 |  |  | 0.50227 | -0.090089 | -35.056 | 0.32391 | 0.16112 | -197.8572 | 16.1075 | -0.55037 | -0.12134 | 0.038714 | -0.047796 | 8.8284 | 9.0582 | 1.9793 | 21.8011 | 22.0318 | 22.2179 | 22.2865 | 22.1258 | 21.4643 | 20.2838 | 22.2128 | 22.3864 | 22.4303 | 22.3784 | 22.0193 | 21.2581 | 22.3058 | 17.2586 | 17.0962 | 16.2335 | 16.2392 | 16.2916 | 17.1074 | 16.7511 | 22.384 | 22.1597 | 21.7242 | 22.0892 | 21.8217 | 21.3278 | 21.9631 | 21.5457 | 20.9342 | 20.1427 | 20.479 | 20.0721 | 19.858 | -0.089637 | -0.011761 | 20.7302 | 22.0879 | 22.4014 | 20.0802 | 21.6951 | 22.1443 | 21.9711 | 21.7314 | 21.3012 | 21.8054 | 21.4789 | 21.0725 | 20.5012 | 20.572 | 20.4289 | 20.4469 | 20.0341 |  | 20.2667 | 19.8022 | 20.1301 | 19.6733 | 20.111 | 20.3523 |  | 20.4575 |  |  | 20.2429 | 20.383 | 20.6345 | [5 empty] | 21.9612 | 20.3525 | 21.6991 | 22.086 | 19.5656 | 21.2099 | 21.848 | 19.404 | 19.9512 | 21.242 |  | 19.8058 | 21.0311 | 18.8909 | 19.7446 | 20.8982 | 19.5054 | 20.2335 | 19.0316 | 20.2278 | 19.1416 | 20.3405 | 18.852 | 20.2114 | 21.1351 | 19.481 | 19.8045 | 21.0725 | 18.9788 | 19.8061 | 20.878 | 18.9947 | 20.2378 | 19.2981 | 19.9768 | 18.9246 | 20.1978 | -0.20919 | 20.9446 | 0.04786 | 0.015108 | -27.0058 | 3.0979 | 0.79 | -0.04 | 0.84636 | -0.35609 | -7.0243 | 0.67521 | 0.47673 | -16.706 | 4.7666 | 0.42673 | 0.42859 | 0.43153 | 0.38566 | 0.45799 | 0.44109 | 0.42746
42838.4144 | -510 | 22.8808 | 22.8518 | 22.8499 | 22.7716 | 22.413 | 21.7641 | 22.712 | 21.8277 | 22.3707 | 22.3844 | 22.3722 | 22.0536 | 21.2857 | 22.2533 | 21.5616 | 21.7431 | 21.8798 | 21.0684 | 21.1707 | 21.391 | 20.4749 | 20.631 | 20.9283 | 21.9006 | 21.6668 | 21.307 | 20.4384 | 20.5373 | 20.5063 | 22.0124 | 21.6288 | 21.1606 | 21.9778 | 21.7257 | 21.3402 | 19.9331 | 20.5021 |  | 20.5583 | 20.2043 | 20.2889 | 19.1128 |  | 16.6866 | 16.6557 | 16.4001 | 16.6095 | 16.6919 | 17.2918 | 17.9107 | 15.7197 | 16.782 | 16.1655 | 16.9245 | 17.8661 | 45.0913 | 48.4695 | 44.2024 | 21.3513 |  |  | 0.50555 | -0.25962 | -35.008 | 0.44088 | 0.34183 | -197.8887 | 16.2534 | -0.45311 | -0.15851 | 0.031162 | -0.14328 | 8.8284 | 9.0581 | 1.9794 | 21.8011 | 22.0281 | 22.2242 | 22.2868 | 22.1214 | 21.4636 | 20.285 | 22.2191 | 22.3885 | 22.4374 | 22.3847 | 22.0239 | 21.2619 | 22.3093 | 17.2715 | 17.1012 | 16.2151 | 16.2081 | 16.2535 | 17.1052 | 16.7464 | 22.3828 | 22.1626 | 21.7246 | 22.0967 | 21.8123 | 21.3214 | 21.9548 | 21.5522 | 20.9306 | 20.1374 | 20.4857 | 20.0604 | 19.8613 | -0.045599 | 0.023996 | 20.7227 | 22.0818 | 22.392 | 20.0753 | 21.6922 | 22.1416 | 21.9707 | 21.7344 | 21.3016 | 21.8028 | 21.4783 | 21.0743 | 20.5048 | 20.5668 | 20.4238 | 20.4521 | 20.0339 |  | 20.2574 | 19.7987 | 20.1292 | 19.6755 | 20.1064 | 20.3489 |  | 20.4464 |  |  | 20.2412 | 20.3788 | 20.6389 | [5 empty] | 21.9667 | 20.3555 | 21.7044 | 22.0871 | 19.5637 | 21.2128 | 21.8531 | 19.398 | 19.9536 | 21.2429 |  | 19.8034 | 21.0277 | 18.8963 | 19.7482 | 20.8981 | 19.5044 | 20.2353 | 19.0314 | 20.2296 | 19.1369 | 20.342 | 18.8629 | 20.2224 | 21.1403 | 19.4919 | 19.8126 | 21.0709 | 18.9875 | 19.8107 | 20.8855 | 19.0056 | 20.2394 | 19.3029 | 19.9827 | 18.9286 | 20.2034 | -0.13147 | 20.9468 | 0.047092 | 0.012292 | -27.0233 | 3.0978 | 5.57 | -0.38 | 0.84912 | -0.6045 | -7.0195 | 0.78774 | 0.69439 | -16.7073 | 4.7882 | 0.42642 | 0.42866 | 0.43132 | 0.38396 | 0.45949 | 0.44114 | 0.42719
42838.4144 | -509 | 22.8777 | 22.8531 | 22.8489 | 22.7739 | 22.4128 | 21.7553 | 22.7131 | 21.8185 | 22.3716 | 22.385 | 22.3711 | 22.0566 | 21.2827 | 22.2543 | 21.5634 | 21.7451 | 21.8828 | 21.073 | 21.174 | 21.3945 | 20.4799 | 20.6281 | 20.9312 | 21.8994 | 21.6709 | 21.3068 | 20.432 | 20.548 | 20.5137 | 22.0285 | 21.6399 | 21.1671 | 21.9825 | 21.7268 | 21.3548 | 19.9363 | 20.5005 |  | 20.5658 | 20.212 | 20.296 | 19.1212 |  | 16.6788 | 16.6543 | 16.3894 | 16.5987 | 16.6813 | 17.2913 | 17.9178 | 15.7708 | 16.7768 | 16.2558 | 16.9205 | 17.8647 | 45.0896 | 48.4836 | 44.2247 | 21.3356 |  |  | 0.46021 | -0.1834 | -34.2424 | 0.24572 | 0.25641 | -197.842 | 16.574 | -0.1101 | -0.14566 | 0.049834 | -0.035297 | 8.8296 | 9.0591 | 1.9787 | 21.7947 | 22.0271 | 22.2285 | 22.2893 | 22.1164 | 21.4684 | 20.2724 | 22.224 | 22.3906 | 22.4281 | 22.3784 | 22.0135 | 21.2625 | 22.3083 | 17.2989 | 17.0523 | 16.2144 | 16.1708 | 16.2267 | 17.0974 | 16.7376 | 22.3832 | 22.1631 | 21.7261 | 22.09 | 21.8167 | 21.3221 | 21.9529 | 21.5495 | 20.931 | 20.1457 | 20.4717 | 20.0588 | 19.8619 | -0.065652 | -0.12645 | 20.7293 | 22.0825 | 22.3952 | 20.0798 | 21.6916 | 22.1464 | 21.9704 | 21.7301 | 21.3042 | 21.8042 | 21.4772 | 21.0703 | 20.4989 | 20.5669 | 20.4277 | 20.4523 | 20.0371 |  | 20.2502 | 19.7911 | 20.1261 | 19.6683 | 20.1099 | 20.3441 |  | 20.4464 |  |  | 20.2466 | 20.3793 | 20.6355 | [5 empty] | 21.9655 | 20.3606 | 21.7066 | 22.0877 | 19.5615 | 21.2157 | 21.8502 | 19.4004 | 19.9485 | 21.2432 |  | 19.8093 | 21.0258 | 18.8977 | 19.7494 | 20.8999 | 19.5017 | 20.2368 | 19.0209 | 20.2306 | 19.1344 | 20.3372 | 18.8652 | 20.2155 | 21.1437 | 19.4935 | 19.8088 | 21.0703 | 18.9914 | 19.8111 | 20.8828 | 19.0056 | 20.2357 | 19.3078 | 19.9813 | 18.9278 | 20.1999 | -0.14668 | 20.946 | 0.046269 | 0.012843 | -27.0072 | 3.0978 | -2.83 | 0 | 0.81016 | -0.50807 | -6.9423 | 0.58808 | 0.6014 | -16.7053 | 4.8352 | 0.42609 | 0.42876 | 0.43163 | 0.38 | 0.45855 | 0.44101 | 0.42745
42838.4144 | -508 | 22.8783 | 22.8558 | 22.8457 | 22.7751 | 22.415 | 21.76 | 22.718 | 21.8203 | 22.3664 | 22.3864 | 22.3735 | 22.0621 | 21.2853 | 22.2547 | 21.5626 | 21.7396 | 21.8821 | 21.0711 | 21.1662 | 21.3974 | 20.4784 | 20.6209 | 20.9247 | 21.8965 | 21.6731 | 21.3079 | 20.4341 | 20.541 | 20.5062 | 22.0348 | 21.6414 | 21.1774 | 21.9825 | 21.7359 | 21.363 | 19.9408 | 20.5099 |  | 20.5703 | 20.2141 | 20.2976 | 19.1258 |  | 16.6884 | 16.6476 | 16.3899 | 16.5967 | 16.6832 | 17.2946 | 17.9424 | 15.8125 | 16.7748 | 16.3555 | 16.9145 | 17.86 | 45.0731 | 48.4922 | 44.2499 | 21.332 |  |  | 0.49964 | 0.064331 | -34.1005 | 0.13138 | 0.26758 | -197.8526 | 16.2297 | -0.28161 | -0.10655 | 0.18662 | -0.15352 | 8.829 | 9.0588 | 1.9784 | 21.788 | 22.0135 | 22.2138 | 22.2811 | 22.1124 | 21.445 | 20.2756 | 22.2059 | 22.3842 | 22.4244 | 22.3728 | 22.0101 | 21.2579 | 22.2965 | 17.3278 | 17.0549 | 16.2098 | 16.1668 | 16.2116 | 17.1031 | 16.7422 | 22.3801 | 22.1553 | 21.7168 | 22.0846 | 21.8137 | 21.3175 | 21.9475 | 21.5432 | 20.9273 | 20.1402 | 20.468 | 20.0553 | 19.8551 | 0.0017816 | -0.25788 | 20.726 | 22.0785 | 22.3933 | 20.0759 | 21.688 | 22.1457 | 21.9709 | 21.7257 | 21.3038 | 21.8044 | 21.4731 | 21.0669 | 20.489 | 20.561 | 20.4239 | 20.4398 | 20.0477 |  | 20.2625 | 19.8013 | 20.1307 | 19.6811 | 20.1067 | 20.3443 |  | 20.45 |  |  | 20.246 | 20.3719 | 20.6381 | [5 empty] | 21.9572 | 20.3584 | 21.7016 | 22.0853 | 19.5609 | 21.2162 | 21.845 | 19.4082 | 19.9489 | 21.2462 |  | 19.811 | 21.0298 | 18.9051 | 19.7566 | 20.9065 | 19.5014 | 20.2341 | 19.0193 | 20.2298 | 19.1412 | 20.3371 | 18.8712 | 20.2198 | 21.1464 | 19.4982 | 19.8152 | 21.0695 | 18.9957 | 19.8166 | 20.8955 | 19.0146 | 20.2433 | 19.3147 | 19.9877 | 18.9312 | 20.2075 | -0.11867 | 20.9482 | 0.046601 | 0.012669 | -27.0491 | 3.0978 | 1.04 | 0.01 | 0.84414 | 0.3009 | -6.9278 | 0.43001 | 0.61436 | -16.7059 | 4.7847 | 0.42621 | 0.42864 | 0.43117 | 0.37747 | 0.45958 | 0.44104 | 0.42746
42838.4144 | -507 | 22.888 | 22.8553 | 22.8494 | 22.7727 | 22.4158 | 21.7572 | 22.7158 | 21.8294 | 22.3724 | 22.3854 | 22.3801 | 22.0659 | 21.2837 | 22.2449 | 21.5686 | 21.7436 | 21.887 | 21.0816 | 21.1712 | 21.3949 | 20.4819 | 20.6291 | 20.9285 | 21.9024 | 21.6737 | 21.3082 | 20.4467 | 20.5464 | 20.5069 | 22.0364 | 21.642 | 21.1788 | 21.9912 | 21.7311 | 21.3572 | 19.9459 | 20.52 |  | 20.5757 | 20.217 | 20.3059 | 19.1277 |  | 16.6802 | 16.6508 | 16.3836 | 16.6014 | 16.6923 | 17.3143 | 17.9692 | 15.7855 | 16.7801 | 16.3795 | 16.9252 | 17.8709 | 45.0701 | 48.5018 | 44.2715 | 21.3353 |  |  | 0.40896 | -0.35031 | -34.0696 | 0.23652 | 0.80576 | -197.8328 | 16.6693 | -0.15741 | -0.19509 | 0.0047268 | -0.033561 | 8.8288 | 9.0586 | 1.9778 | 21.7938 | 22.0199 | 22.2198 | 22.288 | 22.1248 | 21.4617 | 20.2752 | 22.215 | 22.3932 | 22.4244 | 22.3716 | 22.0263 | 21.2567 | 22.3033 | 17.3585 | 17.1006 | 16.2001 | 16.1598 | 16.2032 | 17.0921 | 16.7449 | 22.3852 | 22.1646 | 21.7241 | 22.0997 | 21.8236 | 21.3285 | 21.9567 | 21.5494 | 20.9349 | 20.1422 | 20.4725 | 20.0598 | 19.8709 | -0.15176 | -0.15841 | 20.7249 | 22.0717 | 22.3949 | 20.0706 | 21.6928 | 22.144 | 21.9683 | 21.7279 | 21.3004 | 21.8069 | 21.4689 | 21.0679 | 20.492 | 20.557 | 20.4182 | 20.4395 | 20.0592 |  | 20.2641 | 19.8131 | 20.133 | 19.6963 | 20.108 | 20.348 |  | 20.4579 |  |  | 20.2443 | 20.3747 | 20.6383 | [5 empty] | 21.9566 | 20.3557 | 21.7011 | 22.083 | 19.5686 | 21.2115 | 21.8492 | 19.4061 | 19.9535 | 21.2469 |  | 19.8102 | 21.0323 | 18.9127 | 19.7576 | 20.9155 | 19.5083 | 20.2342 | 19.027 | 20.2336 | 19.1488 | 20.3317 | 18.881 | 20.2284 | 21.1514 | 19.5038 | 19.825 | 21.0814 | 19.0025 | 19.8217 | 20.8991 | 19.0239 | 20.2471 | 19.3163 | 19.9955 | 18.9281 | 20.213 | -0.1682 | 20.9471 | 0.047528 | 0.012829 | -27.0987 | 3.0978 | -10.52 | -0.21 | 0.76371 | -0.70217 | -6.9247 | 0.57696 | 1.0661 | -16.7056 | 4.8492 | 0.42594 | 0.42838 | 0.43079 | 0.37277 | 0.46098 | 0.44116 | 0.42709
42838.4144 | -506 | 22.8905 | 22.858 | 22.8472 | 22.7761 | 22.4179 | 21.7584 | 22.7166 | 21.8303 | 22.3747 | 22.3854 | 22.3802 | 22.063 | 21.2833 | 22.2471 | 21.5639 | 21.7372 | 21.8826 | 21.0628 | 21.1637 | 21.3912 | 20.4763 | 20.6234 | 20.9245 | 21.9009 | 21.6625 | 21.3018 | 20.4435 | 20.5397 | 20.5003 | 22.0313 | 21.6408 | 21.1724 | 21.9973 | 21.7358 | 21.3528 | 19.9457 | 20.5244 |  | 20.5777 | 20.2193 | 20.3018 | 19.1193 |  | 16.6844 | 16.6471 | 16.3966 | 16.6157 | 16.7033 | 17.3222 | 18.0003 | 15.7989 | 16.7785 | 16.375 | 16.9272 | 17.8722 | 45.0495 | 48.5087 | 44.2813 | 21.3314 |  |  | 0.57061 | -0.23269 | -34.2135 | -0.15315 | 0.64279 | -197.8125 | 16.2567 | -0.22575 | -0.36751 | -0.07185 | 0.045427 | 8.8291 | 9.059 | 1.9784 | 21.7815 | 22.0089 | 22.2126 | 22.2779 | 22.113 | 21.4506 | 20.2697 | 22.2066 | 22.3798 | 22.416 | 22.369 | 22.0198 | 21.2556 | 22.2867 | 17.3636 | 17.1295 | 16.2039 | 16.1738 | 16.2188 | 17.0877 | 16.7352 | 22.389 | 22.161 | 21.7274 | 22.1083 | 21.826 | 21.3325 | 21.9618 | 21.5587 | 20.9367 | 20.1516 | 20.4775 | 20.0655 | 19.8767 | -0.24829 | -0.17705 | 20.7284 | 22.0818 | 22.3965 | 20.0672 | 21.6982 | 22.1394 | 21.9649 | 21.7311 | 21.3038 | 21.8137 | 21.4661 | 21.0684 | 20.4907 | 20.5684 | 20.4244 | 20.449 | 20.0718 |  | 20.2568 | 19.811 | 20.1266 | 19.6896 | 20.1089 | 20.3425 |  | 20.4476 |  |  | 20.2411 | 20.3615 | 20.6324 | [5 empty] | 21.9682 | 20.3558 | 21.6975 | 22.0881 | 19.5647 | 21.2092 | 21.8503 | 19.4098 | 19.9545 | 21.2447 |  | 19.8034 | 21.0375 | 18.9143 | 19.7579 | 20.9137 | 19.509 | 20.2353 | 19.0218 | 20.2364 | 19.1435 | 20.3277 | 18.8776 | 20.2184 | 21.1468 | 19.5068 | 19.8216 | 21.0859 | 18.9902 | 19.8111 | 20.8907 | 19.0089 | 20.246 | 19.3119 | 19.9867 | 18.9228 | 20.2046 | -0.15094 | 20.9464 | 0.048088 | 0.01468 | -27.0259 | 3.0979 | -16.95 | -0.02 | 0.90209 | -0.57227 | -6.9393 | -0.46427 | 0.95226 | -16.705 | 4.7889 | 0.42535 | 0.42823 | 0.43101 | 0.37169 | 0.45943 | 0.44138 | 0.42724
42838.4144 | -505 | 22.8934 | 22.8593 | 22.8483 | 22.7777 | 22.4158 | 21.7648 | 22.7249 | 21.8309 | 22.3794 | 22.3914 | 22.3813 | 22.0657 | 21.2863 | 22.254 | 21.5745 | 21.7499 | 21.8868 | 21.0738 | 21.1743 | 21.399 | 20.489 | 20.6328 | 20.9227 | 21.9029 | 21.6725 | 21.3134 | 20.4466 | 20.5428 | 20.5124 | 22.0376 | 21.6473 | 21.1738 | 22 | 21.7339 | 21.3556 | 19.9448 | 20.5195 |  | 20.5791 | 20.2126 | 20.2957 | 19.1351 |  | 16.6787 | 16.6589 | 16.4195 | 16.6286 | 16.7148 | 17.3304 | 18.0327 | 15.853 | 16.7762 | 16.2824 | 16.9217 | 17.8683 | 45.0302 | 48.5006 | 44.2817 | 21.3262 |  |  | 0.55549 | -0.40222 | -34.0972 | 0.24506 | 0.37074 | -197.8637 | 16.6536 | -0.23101 | -0.098958 | -0.21493 | -0.074183 | 8.8294 | 9.0591 | 1.9789 | 21.7872 | 22.0179 | 22.2182 | 22.2848 | 22.1213 | 21.4533 | 20.2757 | 22.2129 | 22.3833 | 22.4258 | 22.372 | 22.018 | 21.2564 | 22.2922 | 17.3886 | 17.1046 | 16.2086 | 16.1928 | 16.2403 | 17.0942 | 16.7448 | 22.387 | 22.1625 | 21.7256 | 22.0986 | 21.8201 | 21.3286 | 21.9596 | 21.5616 | 20.9354 | 20.1389 | 20.4683 | 20.0609 | 19.8749 | -0.043043 | -0.066159 | 20.732 | 22.084 | 22.3892 | 20.0689 | 21.6896 | 22.1353 | 21.9628 | 21.7288 | 21.2998 | 21.8021 | 21.4621 | 21.0686 | 20.4887 | 20.5588 | 20.4258 | 20.4435 | 20.0896 |  | 20.2613 | 19.815 | 20.127 | 19.7003 | 20.108 | 20.3426 |  | 20.4536 |  |  | 20.2192 | 20.3519 | 20.6309 | [5 empty] | 21.9657 | 20.3499 | 21.6994 | 22.0817 | 19.5684 | 21.2198 | 21.8466 | 19.4118 | 19.9629 | 21.2525 |  | 19.8042 | 21.037 | 18.9168 | 19.7525 | 20.9168 | 19.5125 | 20.2423 | 19.0204 | 20.2357 | 19.1466 | 20.3367 | 18.8862 | 20.2254 | 21.1604 | 19.5182 | 19.8327 | 21.0794 | 18.9956 | 19.8297 | 20.8979 | 19.0141 | 20.2556 | 19.3214 | 20.0004 | 18.9281 | 20.2059 | -0.10754 | 20.9464 | 0.047485 | 0.014658 | -27.0209 | 3.0978 | -0.76 | -0.04 | 0.89008 | -0.75241 | -6.9276 | 0.5873 | 0.72321 | -16.7074 | 4.8471 | 0.425 | 0.42813 | 0.43068 | 0.36967 | 0.46003 | 0.44091 | 0.42687
42838.4144 | -504 | 22.8908 | 22.859 | 22.8546 | 22.7729 | 22.4221 | 21.7669 | 22.727 | 21.8325 | 22.3783 | 22.3972 | 22.3751 | 22.0614 | 21.2883 | 22.2631 | 21.5754 | 21.752 | 21.8922 | 21.0729 | 21.1694 | 21.3934 | 20.4781 | 20.6255 | 20.9323 | 21.9109 | 21.6789 | 21.3113 | 20.446 | 20.5504 | 20.5227 | 22.0273 | 21.6441 | 21.171 | 21.9829 | 21.7379 | 21.3497 | 19.9371 | 20.5081 |  | 20.567 | 20.1988 | 20.3006 | 19.1235 |  | 16.6865 | 16.66 | 16.4144 | 16.6281 | 16.706 | 17.3229 | 18.0568 | 15.9091 | 16.7776 | 16.1775 | 16.9265 | 17.8764 | 45.0222 | 48.5002 | 44.293 | 21.3363 |  |  | 0.49438 | -0.21429 | -33.7989 | 0.3364 | 0.53634 | -197.8801 | 16.6654 | -0.23495 | -0.01995 | -0.17969 | 0.0087976 | 8.8298 | 9.0595 | 1.9787 | 21.7894 | 22.0238 | 22.2186 | 22.2897 | 22.1216 | 21.4524 | 20.2778 | 22.2188 | 22.3861 | 22.4242 | 22.3771 | 22.0126 | 21.2605 | 22.3006 | 17.4204 | 17.0395 | 16.204 | 16.2097 | 16.2795 | 17.092 | 16.7403 | 22.3904 | 22.1655 | 21.7247 | 22.101 | 21.8129 | 21.3234 | 21.9649 | 21.5558 | 20.9356 | 20.1434 | 20.4598 | 20.0587 | 19.8599 | -0.17064 | 0.029702 | 20.7334 | 22.0757 | 22.3861 | 20.0679 | 21.6912 | 22.1381 | 21.9621 | 21.729 | 21.3011 | 21.7988 | 21.468 | 21.0622 | 20.49 | 20.5537 | 20.4243 | 20.4453 | 20.0997 |  | 20.2558 | 19.8277 | 20.1323 | 19.7028 | 20.1072 | 20.338 |  | 20.4522 |  |  | 20.216 | 20.3524 | 20.6363 | [5 empty] | 21.9621 | 20.3445 | 21.6971 | 22.0812 | 19.5767 | 21.2098 | 21.849 | 19.4223 | 19.9649 | 21.2532 |  | 19.8106 | 21.0335 | 18.917 | 19.7606 | 20.9255 | 19.4982 | 20.2325 | 19.013 | 20.2281 | 19.1572 | 20.3355 | 18.8903 | 20.2293 | 21.1602 | 19.524 | 19.8344 | 21.0841 | 19.0076 | 19.8287 | 20.8951 | 19.0092 | 20.2528 | 19.3224 | 19.996 | 18.9326 | 20.2107 | -0.09956 | 20.9462 | 0.047787 | 0.014738 | -26.9903 | 3.0978 | 0.6 | -0.26 | 0.83971 | -0.54919 | -6.8972 | 0.6881 | 0.86984 | -16.7079 | 4.8487 | 0.42454 | 0.42796 | 0.43058 | 0.36588 | 0.46001 | 0.44098 | 0.42743
42838.4145 | -503 | 22.8839 | 22.8555 | 22.8323 | 22.7719 | 22.4124 | 21.7631 | 22.7221 | 21.8253 | 22.3708 | 22.3902 | 22.3715 | 22.054 | 21.2837 | 22.2498 | 21.5675 | 21.7371 | 21.8783 | 21.0653 | 21.167 | 21.3846 | 20.4713 | 20.6214 | 20.9242 | 21.8935 | 21.662 | 21.3019 | 20.4334 | 20.5364 | 20.5007 | 22.0255 | 21.6423 | 21.1721 | 21.9863 | 21.7269 | 21.3496 | 19.9422 | 20.509 |  | 20.5702 | 20.2026 | 20.3033 | 19.1077 |  | 16.6844 | 16.6543 | 16.4083 | 16.6325 | 16.7248 | 17.3408 | 18.0772 | 15.9662 | 16.7755 | 16.1572 | 16.9245 | 17.8697 | 45.0276 | 48.4986 | 44.3001 | 21.3302 |  |  | 0.40896 | -0.30431 | -33.5558 | 0.35349 | 0.15652 | -197.8118 | 16.8993 | -0.41697 | -0.074438 | -0.10374 | 0.028762 | 8.8279 | 9.0578 | 1.9785 | 21.8022 | 22.0254 | 22.2272 | 22.2927 | 22.1218 | 21.4612 | 20.2878 | 22.2212 | 22.3842 | 22.4322 | 22.3862 | 22.0196 | 21.2677 | 22.3073 | 17.4344 | 16.9999 | 16.1838 | 16.2153 | 16.2874 | 17.0895 | 16.7423 | 22.3818 | 22.1555 | 21.7235 | 22.0927 | 21.8131 | 21.3182 | 21.9592 | 21.5519 | 20.9319 | 20.137 | 20.4529 | 20.0565 | 19.8547 | -0.086295 | 0.067362 | 20.7395 | 22.0796 | 22.3949 | 20.0776 | 21.6887 | 22.1489 | 21.9658 | 21.7345 | 21.3064 | 21.8057 | 21.4726 | 21.0716 | 20.4915 | 20.5621 | 20.4255 | 20.45 | 20.1106 |  | 20.2648 | 19.8328 | 20.141 | 19.7072 | 20.1117 | 20.3408 |  | 20.4504 |  |  | 20.2345 | 20.362 | 20.6342 | [5 empty] | 21.9609 | 20.3599 | 21.7071 | 22.0902 | 19.577 | 21.2103 | 21.8447 | 19.4165 | 19.9616 | 21.2586 |  | 19.8023 | 21.0322 | 18.9145 | 19.7626 | 20.9313 | 19.499 | 20.2361 | 19.0116 | 20.2255 | 19.1425 | 20.3353 | 18.8983 | 20.2332 | 21.1624 | 19.5213 | 19.844 | 21.0842 | 19.0118 | 19.8354 | 20.9032 | 18.989 | 20.2493 | 19.3212 | 20.0025 | 18.9308 | 20.213 | -0.077672 | 20.9474 | 0.048057 | 0.016074 | -27.0658 | 3.0978 | 4.64 | -0.01 | 0.7637 | -0.65445 | -6.8723 | 0.70535 | 0.46992 | -16.7055 | 4.8828 | 0.42454 | 0.42811 | 0.43061 | 0.36404 | 0.46249 | 0.44159 | 0.42736
42838.4145 | -502 | 22.8776 | 22.8554 | 22.8395 | 22.7694 | 22.4111 | 21.7584 | 22.7167 | 21.8253 | 22.3719 | 22.3817 | 22.3739 | 22.0584 | 21.2826 | 22.2442 | 21.5636 | 21.7412 | 21.8813 | 21.0683 | 21.1692 | 21.3972 | 20.4812 | 20.6226 | 20.9279 | 21.9014 | 21.6693 | 21.3116 | 20.4416 | 20.5417 | 20.5088 | 22.0291 | 21.6477 | 21.1729 | 21.995 | 21.7287 | 21.3595 | 19.9408 | 20.5108 |  | 20.5747 | 20.2024 | 20.3 | 19.0905 |  | 16.6938 | 16.6569 | 16.4118 | 16.6345 | 16.7575 | 17.3644 | 18.0801 | 15.9957 | 16.7834 | 16.1571 | 16.9228 | 17.8644 | 45.0568 | 48.4865 | 44.3116 | 21.3321 |  |  | 0.31367 | -0.44428 | -33.9461 | 0.11824 | 0.15784 | -197.846 | 16.6384 | -0.32892 | -0.0008796 | -0.15682 | 0.040219 | 8.8282 | 9.058 | 1.9783 | 21.8006 | 22.0207 | 22.2213 | 22.2895 | 22.1294 | 21.4587 | 20.2815 | 22.2185 | 22.3816 | 22.4225 | 22.3784 | 22.015 | 21.2656 | 22.3041 | 17.4619 | 17.0023 | 16.182 | 16.219 | 16.2793 | 17.0953 | 16.7535 | 22.3934 | 22.1542 | 21.7265 | 22.0896 | 21.8155 | 21.322 | 21.9593 | 21.5492 | 20.9326 | 20.1338 | 20.4568 | 20.0568 | 19.8624 | -0.12011 | 0.010302 | 20.7408 | 22.0788 | 22.397 | 20.0847 | 21.6898 | 22.1473 | 21.9653 | 21.7329 | 21.3036 | 21.8026 | 21.469 | 21.0721 | 20.4934 | 20.5547 | 20.424 | 20.446 | 20.1182 |  | 20.2657 | 19.8337 | 20.137 | 19.6955 | 20.108 | 20.3423 |  | 20.4527 |  |  | 20.2279 | 20.3531 | 20.6333 | [5 empty] | 21.9528 | 20.3517 | 21.6902 | 22.084 | 19.5656 | 21.2069 | 21.8428 | 19.4277 | 19.9769 | 21.2616 |  | 19.8073 | 21.0498 | 18.922 | 19.7734 | 20.9418 | 19.5138 | 20.2445 | 19.0115 | 20.2429 | 19.1466 | 20.3348 | 18.8904 | 20.2266 | 21.1733 | 19.5226 | 19.8486 | 21.0912 | 19.0071 | 19.8326 | 20.8998 | 18.9765 | 20.2535 | 19.3185 | 20.0008 | 18.9312 | 20.2077 | -0.16078 | 20.9479 | 0.048155 | 0.015232 | -26.9474 | 3.0977 | -20.78 | -0.2 | 0.66885 | -0.79077 | -6.9122 | 0.40794 | 0.47191 | -16.7076 | 4.8451 | 0.42436 | 0.42794 | 0.43081 | 0.36165 | 0.46401 | 0.44202 | 0.42704
42838.4145 | -501 | 22.8958 | 22.8576 | 22.846 | 22.7788 | 22.4183 | 21.7591 | 22.7229 | 21.8287 | 22.3779 | 22.3889 | 22.3792 | 22.0584 | 21.2833 | 22.2506 | 21.5602 | 21.7394 | 21.8841 | 21.0679 | 21.169 | 21.3865 | 20.4753 | 20.6181 | 20.9227 | 21.9028 | 21.6649 | 21.3064 | 20.4345 | 20.5412 | 20.5108 | 22.0247 | 21.6428 | 21.166 | 21.9891 | 21.7249 | 21.3602 | 19.9389 | 20.5117 |  | 20.5683 | 20.1943 | 20.2991 | 19.0646 |  | 16.6948 | 16.6556 | 16.4103 | 16.6508 | 16.7724 | 17.3916 | 18.0669 | 16.0364 | 16.7831 | 16.1628 | 16.9327 | 17.8695 | 45.0719 | 48.488 | 44.321 | 21.3315 |  |  | 0.50424 | -0.30825 | -34.5322 | 0.27529 | 0.422 | -197.825 | 16.3289 | -0.23955 | 0.14604 | 0.082982 | 0.060357 | 8.8279 | 9.0577 | 1.9782 | 21.7997 | 22.0288 | 22.2192 | 22.2886 | 22.1225 | 21.4611 | 20.2801 | 22.2143 | 22.3868 | 22.4206 | 22.3828 | 22.0182 | 21.2591 | 22.3102 | 17.4608 | 16.9917 | 16.1855 | 16.2168 | 16.2749 | 17.0919 | 16.7599 | 22.3857 | 22.1637 | 21.7234 | 22.0875 | 21.817 | 21.3278 | 21.9564 | 21.5426 | 20.9265 | 20.1423 | 20.4583 | 20.0747 | 19.8564 | -0.027512 | -0.12132 | 20.75 | 22.0787 | 22.4003 | 20.0948 | 21.6957 | 22.1451 | 21.9696 | 21.7359 | 21.3061 | 21.8056 | 21.4726 | 21.0748 | 20.4899 | 20.5504 | 20.4292 | 20.4462 | 20.109 |  | 20.2641 | 19.8305 | 20.1295 | 19.6884 | 20.1129 | 20.3359 |  | 20.4549 |  |  | 20.2239 | 20.3577 | 20.6304 | [5 empty] | 21.9519 | 20.3514 | 21.6921 | 22.0776 | 19.5668 | 21.2023 | 21.8343 | 19.42 | 19.9779 | 21.2696 |  | 19.7946 | 21.0442 | 18.9272 | 19.7669 | 20.9316 | 19.5182 | 20.2386 | 19.0048 | 20.2341 | 19.1447 | 20.3286 | 18.8883 | 20.2293 | 21.1697 | 19.5148 | 19.8475 | 21.0943 | 18.9962 | 19.8302 | 20.895 | 18.9749 | 20.2563 | 19.3234 | 19.9864 | 18.9215 | 20.2045 | -0.014601 | 20.9481 | 0.048149 | 0.016299 | -27.024 | 3.0977 | -23.4 | 0.13 | 0.84802 | -0.65868 | -6.9716 | 0.62246 | 0.77166 | -16.7075 | 4.8001 | 0.42456 | 0.42778 | 0.43117 | 0.36137 | 0.46435 | 0.44267 | 0.42749
42838.4145 | -500 | 22.8913 | 22.856 | 22.8482 | 22.7756 | 22.4181 | 21.7651 | 22.7179 | 21.8278 | 22.3721 | 22.3862 | 22.3763 | 22.0512 | 21.2816 | 22.2478 | 21.575 | 21.7443 | 21.8859 | 21.0737 | 21.1688 | 21.4001 | 20.4789 | 20.6325 | 20.9313 | 21.9054 | 21.666 | 21.309 | 20.4405 | 20.5476 | 20.5053 | 22.0268 | 21.6381 | 21.1621 | 21.9829 | 21.7211 | 21.3516 | 19.9302 | 20.5183 |  | 20.5663 | 20.1939 | 20.2975 | 19.0354 |  | 16.6929 | 16.661 | 16.4128 | 16.6626 | 16.7779 | 17.3879 | 18.0399 | 16.0698 | 16.7948 | 16.1837 | 16.9287 | 17.8752 | 45.0946 | 48.4856 | 44.334 | 21.3306 |  |  | 0.37544 | -0.38382 | -34.7655 | 0.35217 | 0.29649 | -197.8236 | 16.3611 | -0.18238 | -0.10791 | 0.015846 | -0.036859 | 8.8281 | 9.0577 | 1.979 | 21.7883 | 22.027 | 22.2047 | 22.288 | 22.1221 | 21.4503 | 20.2739 | 22.2092 | 22.3858 | 22.4161 | 22.373 | 22.0101 | 21.2559 | 22.2941 | 17.4477 | 16.9902 | 16.1799 | 16.2253 | 16.2918 | 17.0904 | 16.7617 | 22.3836 | 22.1649 | 21.7255 | 22.0889 | 21.8155 | 21.3254 | 21.9543 | 21.5455 | 20.9282 | 20.1387 | 20.4559 | 20.0424 | 19.8668 | -0.11421 | -0.10762 | 20.7526 | 22.084 | 22.3977 | 20.1005 | 21.6895 | 22.1413 | 21.9637 | 21.7339 | 21.3036 | 21.805 | 21.4684 | 21.0695 | 20.493 | 20.5532 | 20.42 | 20.4402 | 20.1067 |  | 20.2687 | 19.8462 | 20.1403 | 19.6969 | 20.1168 | 20.3391 |  | 20.4566 |  |  | 20.2144 | 20.3489 | 20.6378 | [5 empty] | 21.9602 | 20.357 | 21.7036 | 22.0925 | 19.5665 | 21.2136 | 21.8459 | 19.4406 | 19.9676 | 21.2642 |  | 19.7886 | 21.0467 | 18.9223 | 19.757 | 20.9369 | 19.508 | 20.2391 | 18.9968 | 20.2328 | 19.1374 | 20.329 | 18.8893 | 20.239 | 21.1715 | 19.5282 | 19.8568 | 21.0919 | 19.0011 | 19.8448 | 20.9024 | 18.9813 | 20.2635 | 19.3282 | 20.0092 | 18.9329 | 20.2149 | -0.33088 | 20.9475 | 0.048002 | 0.01701 | -27.046 | 3.0977 | -6.51 | 0.05 | 0.73174 | -0.735 | -6.9952 | 0.70405 | 0.64681 | -16.7073 | 4.8048 | 0.42478 | 0.42771 | 0.43107 | 0.36266 | 0.46519 | 0.4432 | 0.42708
42838.4145 | -499 | 22.8835 | 22.8595 | 22.8521 | 22.7736 | 22.4142 | 21.759 | 22.7173 | 21.8285 | 22.3725 | 22.3864 | 22.374 | 22.0566 | 21.2803 | 22.2505 | 21.5738 | 21.7394 | 21.8892 | 21.0688 | 21.1702 | 21.3959 | 20.4759 | 20.6237 | 20.9244 | 21.9027 | 21.6722 | 21.3087 | 20.4415 | 20.5467 | 20.5077 | 22.0349 | 21.6484 | 21.1712 | 21.9895 | 21.7261 | 21.3547 | 19.9396 | 20.5295 |  | 20.5753 | 20.1997 | 20.3013 | 19.0088 |  | 16.6984 | 16.6641 | 16.4152 | 16.6636 | 16.7644 | 17.3738 | 18.0056 | 16.0994 | 16.7911 | 16.1647 | 16.9265 | 17.8656 | 45.1155 | 48.4697 | 44.3278 | 21.3248 |  |  | 0.50621 | -0.19983 | -34.8884 | 0.3502 | 0.38783 | -197.8236 | 16.3138 | -0.23561 | 0.0069044 | -0.17822 | -0.078176 | 8.8279 | 9.0576 | 1.9792 | 21.7931 | 22.0227 | 22.2185 | 22.2936 | 22.1229 | 21.4556 | 20.2774 | 22.2177 | 22.3873 | 22.4299 | 22.3795 | 22.0148 | 21.2653 | 22.2987 | 17.4276 | 17.0026 | 16.1671 | 16.229 | 16.2938 | 17.0882 | 16.7625 | 22.3854 | 22.1569 | 21.7162 | 22.0837 | 21.8108 | 21.3169 | 21.9513 | 21.5407 | 20.9274 | 20.1287 | 20.4483 | 20.0387 | 19.8628 | -0.029281 | 0.067362 | 20.7509 | 22.0831 | 22.3885 | 20.1031 | 21.6918 | 22.141 | 21.961 | 21.7352 | 21.2998 | 21.8041 | 21.4669 | 21.0719 | 20.4911 | 20.5536 | 20.4209 | 20.4423 | 20.1012 |  | 20.2698 | 19.8571 | 20.1415 | 19.7012 | 20.1207 | 20.3479 |  | 20.4572 |  |  | 20.2027 | 20.2777 | 20.632 | [5 empty] | 21.9639 | 20.3556 | 21.6985 | 22.0846 | 19.5603 | 21.2007 | 21.8391 | 19.4277 | 19.9815 | 21.2548 |  | 19.792 | 21.0454 | 18.9065 | 19.7686 | 20.9484 | 19.5168 | 20.2332 | 18.9982 | 20.2312 | 19.1349 | 20.3357 | 18.8898 | 20.2412 | 21.1717 | 19.524 | 19.8596 | 21.0942 | 18.9987 | 19.8335 | 20.9045 | 18.9705 | 20.2664 | 19.3227 | 20.0082 | 18.9245 | 20.208 | -0.21772 | 20.9464 | 0.048051 | 0.018251 | -26.9395 | 3.0977 | -6.69 | -0.13 | 0.84968 | -0.53034 | -7.0076 | 0.70208 | 0.73974 | -16.7069 | 4.7977 | 0.42497 | 0.42745 | 0.43108 | 0.36463 | 0.4667 | 0.44425 | 0.42686
42838.4145 | -498 | 22.8942 | 22.8653 | 22.8567 | 22.7836 | 22.4203 | 21.7658 | 22.7229 | 21.8265 | 22.377 | 22.3899 | 22.3715 | 22.0624 | 21.2837 | 22.2448 | 21.5669 | 21.7382 | 21.8871 | 21.0743 | 21.1661 | 21.3939 | 20.4836 | 20.6269 | 20.9226 | 21.902 | 21.6728 | 21.3057 | 20.4382 | 20.5495 | 20.5112 | 22.0381 | 21.6419 | 21.1682 | 21.9887 | 21.7317 | 21.3623 | 19.9485 | 20.5425 |  | 20.5818 | 20.1984 | 20.305 | 19.0033 |  | 16.705 | 16.6706 | 16.422 | 16.663 | 16.7637 | 17.3586 | 18.0004 | 16.1198 | 16.7908 | 16.1277 | 16.9272 | 17.87 | 45.1429 | 48.457 | 44.328 | 21.3186 |  |  | 0.48255 | -0.18734 | -35.5291 | 0.21615 | 0.24326 | -197.8217 | 15.9577 | -0.33943 | -0.13729 | -0.080242 | -0.067239 | 8.828 | 9.0574 | 1.9786 | 21.7835 | 22.0164 | 22.212 | 22.2824 | 22.1196 | 21.4571 | 20.2804 | 22.2077 | 22.3857 | 22.4252 | 22.3764 | 22.0137 | 21.261 | 22.2958 | 17.4112 | 16.9934 | 16.1655 | 16.2283 | 16.2993 | 17.0845 | 16.7644 | 22.3834 | 22.156 | 21.7216 | 22.0924 | 21.8158 | 21.3194 | 21.9535 | 21.5447 | 20.9241 | 20.1318 | 20.4525 | 20.0383 | 19.8598 | 0.043854 | -0.078141 | 20.7569 | 22.0852 | 22.3937 | 20.1061 | 21.6911 | 22.1446 | 21.9708 | 21.7321 | 21.3045 | 21.8044 | 21.4702 | 21.073 | 20.4896 | 20.5547 | 20.4283 | 20.4479 | 20.0477 |  | 20.2616 | 19.8588 | 20.1314 | 19.6834 | 20.1052 | 20.3414 |  | 20.4502 |  |  | 20.2075 | 20.1826 | 20.5987 | [5 empty] | 21.9599 | 20.3594 | 21.7011 | 22.0817 | 19.5551 | 21.2127 | 21.8441 | 19.4333 | 19.9821 | 21.2805 |  | 19.795 | 21.045 | 18.8997 | 19.7724 | 20.9511 | 19.5157 | 20.2315 | 19.0012 | 20.2413 | 19.1318 | 20.3352 | 18.9056 | 20.2475 | 21.1797 | 19.5227 | 19.8716 | 21.1044 | 19.0035 | 19.8397 | 20.908 | 18.9764 | 20.2677 | 19.3365 | 20.014 | 18.9287 | 20.2063 | -0.21216 | 20.9479 | 0.047744 | 0.017794 | -27.036 | 3.0977 | 8.51 | 0.02 | 0.82959 | -0.51351 | -7.0717 | 0.55158 | 0.58585 | -16.7064 | 4.7449 | 0.42618 | 0.42706 | 0.43106 | 0.36603 | 0.46711 | 0.4447 | 0.42705
42838.4145 | -497 | 22.8823 | 22.8532 | 22.8402 | 22.7686 | 22.4062 | 21.7535 | 22.7152 | 21.8297 | 22.3697 | 22.3807 | 22.3726 | 22.0525 | 21.2758 | 22.2501 | 21.5692 | 21.7464 | 21.8837 | 21.0732 | 21.1659 | 21.397 | 20.4861 | 20.6303 | 20.9239 | 21.9039 | 21.6754 | 21.3094 | 20.4411 | 20.5547 | 20.5162 | 22.0316 | 21.6404 | 21.1728 | 21.989 | 21.736 | 21.3619 | 19.942 | 20.557 |  | 20.5763 | 20.2036 | 20.3041 | 18.9975 |  | 16.6993 | 16.6662 | 16.415 | 16.6477 | 16.7483 | 17.3476 | 18.0304 | 16.1406 | 16.7835 | 16.1191 | 16.9246 | 17.8627 | 45.1701 | 48.45 | 44.3152 | 21.3239 |  |  | 0.31696 | -0.5711 | -36.1639 | 0.43694 | 0.04416 | -197.8493 | 15.7947 | -0.49254 | -0.2309 | -0.097446 | -0.064982 | 8.8293 | 9.0587 | 1.9785 | 21.7936 | 22.0236 | 22.2155 | 22.2821 | 22.119 | 21.4657 | 20.2805 | 22.2141 | 22.3899 | 22.4274 | 22.3777 | 22.0154 | 21.2628 | 22.3003 | 17.3805 | 17.0006 | 16.1621 | 16.2159 | 16.2899 | 17.0863 | 16.7641 | 22.3865 | 22.1598 | 21.7153 | 22.0951 | 21.8117 | 21.3174 | 21.9521 | 21.5448 | 20.9217 | 20.1336 | 20.4442 | 20.0252 | 19.8547 | -0.024759 | -0.024885 | 20.7643 | 22.0865 | 22.3977 | 20.1103 | 21.6918 | 22.1418 | 21.9666 | 21.7299 | 21.304 | 21.809 | 21.4696 | 21.0708 | 20.4855 | 20.5486 | 20.4273 | 20.4459 | 19.9878 |  | 20.2628 | 19.8668 | 20.1319 | 19.6934 | 20.1119 | 20.3454 |  | 20.457 |  |  | 20.2088 | 20.1315 | 20.577 | [5 empty] | 21.9641 | 20.359 | 21.6977 | 22.0866 | 19.5577 | 21.2163 | 21.8454 | 19.4349 | 19.9849 | 21.2835 |  | 19.7986 | 21.0471 | 18.8901 | 19.7788 | 20.9507 | 19.5179 | 20.2371 | 19.0009 | 20.2455 | 19.1298 | 20.3385 | 18.9132 | 20.2421 | 21.1737 | 19.5222 | 19.865 | 21.1007 | 19.0079 | 19.839 | 20.9093 | 18.9706 | 20.2663 | 19.3303 | 20.0044 | 18.9294 | 20.207 | -0.33886 | 20.9484 | 0.047025 | 0.01619 | -27.0267 | 3.0977 | 9.2 | 0.06 | 0.67235 | -0.89657 | -7.1345 | 0.78422 | 0.2496 | -16.7073 | 4.7206 | 0.42788 | 0.42686 | 0.431 | 0.36965 | 0.46745 | 0.44464 | 0.42725
42838.4145 | -496 | 22.8818 | 22.8579 | 22.8401 | 22.765 | 22.4064 | 21.753 | 22.714 | 21.8203 | 22.3684 | 22.3788 | 22.37 | 22.0535 | 21.276 | 22.245 | 21.57 | 21.7444 | 21.8869 | 21.073 | 21.1722 | 21.3948 | 20.4787 | 20.6256 | 20.9203 | 21.8997 | 21.6678 | 21.3054 | 20.4439 | 20.5476 | 20.5087 | 22.035 | 21.6482 | 21.171 | 21.9911 | 21.7324 | 21.3563 | 19.9377 | 20.5706 |  | 20.5715 | 20.1903 | 20.2859 | 18.9858 |  | 16.7001 | 16.6662 | 16.4171 | 16.6563 | 16.7496 | 17.3632 | 18.0521 | 16.1598 | 16.786 | 16.1239 | 16.9206 | 17.8718 | 45.2006 | 48.4381 | 44.3096 | 21.3287 |  |  | 0.52198 | -0.26948 | -36.4037 | 0.38371 | 0.30963 | -197.8637 | 15.5811 | -0.5162 | -0.27196 | -0.13815 | 0.070599 | 8.8288 | 9.0585 | 1.9782 | 21.7927 | 22.0277 | 22.2235 | 22.2863 | 22.1212 | 21.4541 | 20.2787 | 22.2173 | 22.3957 | 22.4207 | 22.3821 | 22.0226 | 21.2538 | 22.2971 | 17.3658 | 17.0265 | 16.1745 | 16.2262 | 16.2909 | 17.0935 | 16.7788 | 22.3777 | 22.1506 | 21.7211 | 22.0881 | 21.8148 | 21.315 | 21.9474 | 21.5435 | 20.9202 | 20.1324 | 20.4396 | 20.0213 | 19.8579 | 0.0023714 | -0.18332 | 20.7656 | 22.0828 | 22.3988 | 20.1173 | 21.6954 | 22.1411 | 21.9628 | 21.7289 | 21.3056 | 21.8073 | 21.4711 | 21.0681 | 20.4782 | 20.5494 | 20.4305 | 20.446 | 19.9515 |  | 20.2634 | 19.8822 | 20.1291 | 19.6929 | 20.1072 | 20.3454 |  | 20.4574 |  |  | 20.2101 | 20.1233 | 20.5617 | [5 empty] | 21.9563 | 20.3568 | 21.6916 | 22.0893 | 19.5587 | 21.2131 | 21.8387 | 19.4344 | 19.9833 | 21.2706 |  | 19.7997 | 21.051 | 18.8944 | 19.78 | 20.9548 | 19.514 | 20.2334 | 18.9914 | 20.2465 | 19.1282 | 20.3434 | 18.92 | 20.248 | 21.1832 | 19.5133 | 19.8573 | 21.0972 | 19.0211 | 19.8435 | 20.915 | 18.9725 | 20.2723 | 19.3258 | 19.9941 | 18.9242 | 20.2114 | -0.17617 | 20.9483 | 0.047 | 0.015965 | -27.0456 | 3.0976 | 5.18 | -0.32 | 0.86281 | -0.61587 | -7.1582 | 0.7349 | 0.66096 | -16.7083 | 4.6887 | 0.42891 | 0.42633 | 0.43086 | 0.37211 | 0.46778 | 0.44482 | 0.42712
42838.4145 | -495 | 22.8794 | 22.8616 | 22.8489 | 22.7714 | 22.4107 | 21.7572 | 22.7164 | 21.8223 | 22.3688 | 22.3854 | 22.3754 | 22.0594 | 21.2758 | 22.2494 | 21.5684 | 21.7368 | 21.8859 | 21.0727 | 21.1723 | 21.3877 | 20.4721 | 20.6237 | 20.915 | 21.896 | 21.6645 | 21.302 | 20.4413 | 20.5447 | 20.5045 | 22.0337 | 21.644 | 21.171 | 21.9976 | 21.7341 | 21.3501 | 19.9312 | 20.5658 |  | 20.5672 | 20.1919 | 20.2885 | 18.9831 |  | 16.704 | 16.6744 | 16.4239 | 16.6602 | 16.7535 | 17.3885 | 18.0707 | 16.2004 | 16.7907 | 16.118 | 16.9322 | 17.8654 | 45.2093 | 48.4354 | 44.3166 | 21.3313 |  |  | 0.51672 | -0.23137 | -37.2704 | 0.35743 | 0.15784 | -197.8972 | 15.4491 | -0.71202 | 0.063338 | -0.13122 | -0.044324 | 8.8288 | 9.0585 | 1.9784 | 21.794 | 22.0234 | 22.2198 | 22.2858 | 22.121 | 21.4546 | 20.2795 | 22.2203 | 22.3901 | 22.4207 | 22.3792 | 22.0188 | 21.2613 | 22.302 | 17.3449 | 17.0407 | 16.1678 | 16.2229 | 16.2844 | 17.0826 | 16.7692 | 22.3836 | 22.1559 | 21.7272 | 22.0858 | 21.8168 | 21.3214 | 21.9535 | 21.5458 | 20.9219 | 20.1331 | 20.4422 | 20.0234 | 19.8655 | 0.023801 | -0.081945 | 20.764 | 22.0809 | 22.4009 | 20.1206 | 21.6977 | 22.1429 | 21.9682 | 21.7373 | 21.3063 | 21.8043 | 21.4716 | 21.0708 | 20.4789 | 20.5593 | 20.4317 | 20.4425 | 19.9163 |  | 20.2649 | 19.8975 | 20.1394 | 19.6956 | 20.1149 | 20.3583 |  | 20.4526 |  |  | 20.2144 | 20.1322 | 20.5582 | [5 empty] | 21.9523 | 20.3608 | 21.6937 | 22.0937 | 19.5636 | 21.2152 | 21.8435 | 19.4418 | 19.9772 | 21.2696 |  | 19.8011 | 21.048 | 18.8977 | 19.7868 | 20.947 | 19.5123 | 20.2286 | 18.9953 | 20.246 | 19.1268 | 20.3429 | 18.9225 | 20.2486 | 21.1927 | 19.5178 | 19.8476 | 21.1042 | 19.027 | 19.8447 | 20.9224 | 18.9742 | 20.274 | 19.3306 | 19.9813 | 18.9221 | 20.2104 | -0.19695 | 20.9484 | 0.046465 | 0.014796 | -27.0152 | 3.0977 | -2.75 | -0.05 | 0.85845 | -0.57067 | -7.243 | 0.7093 | 0.47193 | -16.7105 | 4.669 | 0.42994 | 0.42626 | 0.43104 | 0.37317 | 0.46741 | 0.44468 | 0.42693
42838.4146 | -494 | 22.882 | 22.8544 | 22.8462 | 22.7694 | 22.4108 | 21.7621 | 22.7178 | 21.8157 | 22.3762 | 22.3829 | 22.3742 | 22.056 | 21.2755 | 22.2515 | 21.5758 | 21.7477 | 21.8878 | 21.0738 | 21.1795 | 21.4007 | 20.4841 | 20.6269 | 20.9295 | 21.9028 | 21.6714 | 21.3122 | 20.4439 | 20.5497 | 20.5125 | 22.0316 | 21.6371 | 21.1729 | 21.9925 | 21.7295 | 21.3556 | 19.9364 | 20.5644 |  | 20.5688 | 20.1942 | 20.2842 | 18.9856 |  | 16.6988 | 16.668 | 16.4143 | 16.6546 | 16.7636 | 17.4152 | 18.0997 | 16.2418 | 16.7836 | 16.1468 | 16.9266 | 17.8684 | 45.2307 | 48.4285 | 44.3113 | 21.33 |  |  | 0.54827 | -0.28788 | -37.99 | 0.341 | 0.23275 | -197.8617 | 15.2178 | -0.70216 | 0.13515 | -0.17759 | 0.03449 | 8.8279 | 9.0579 | 1.9792 | 21.7954 | 22.0277 | 22.2266 | 22.2841 | 22.1246 | 21.4545 | 20.2742 | 22.2247 | 22.3917 | 22.4231 | 22.3863 | 22.0211 | 21.2644 | 22.3055 | 17.3287 | 17.0345 | 16.1725 | 16.2199 | 16.3071 | 17.0892 | 16.7725 | 22.3855 | 22.1614 | 21.7256 | 22.1 | 21.818 | 21.3276 | 21.9577 | 21.5558 | 20.9348 | 20.1369 | 20.4423 | 20.0241 | 19.8695 | 0.065283 | -0.062355 | 20.7693 | 22.0853 | 22.4019 | 20.1237 | 21.6962 | 22.1479 | 21.9673 | 21.7438 | 21.3058 | 21.8133 | 21.4732 | 21.0742 | 20.4758 | 20.5571 | 20.4326 | 20.4426 | 19.893 |  | 20.2577 | 19.9047 | 20.1314 | 19.6876 | 20.1073 | 20.3443 |  | 20.4446 |  |  | 20.2237 | 20.1458 | 20.556 | [5 empty] | 21.9624 | 20.3658 | 21.7053 | 22.0931 | 19.5615 | 21.2199 | 21.8494 | 19.4467 | 19.9669 | 21.2679 |  | 19.8076 | 21.0522 | 18.899 | 19.7956 | 20.9507 | 19.5082 | 20.2237 | 18.9984 | 20.2534 | 19.1279 | 20.3496 | 18.9257 | 20.2471 | 21.1846 | 19.5182 | 19.8447 | 21.1075 | 19.0153 | 19.8415 | 20.9167 | 18.971 | 20.2769 | 19.3223 | 19.9749 | 18.9217 | 20.2162 | -0.083051 | 20.9493 | 0.046551 | 0.014477 | -26.9981 | 3.0976 | 10.37 | -0.26 | 0.88427 | -0.63656 | -7.3125 | 0.6928 | 0.57311 | -16.7097 | 4.6341 | 0.43034 | 0.42579 | 0.43101 | 0.37574 | 0.46726 | 0.44479 | 0.42695
42838.4146 | -493 | 22.892 | 22.8594 | 22.8454 | 22.7771 | 22.4206 | 21.761 | 22.7227 | 21.8229 | 22.3753 | 22.3901 | 22.3775 | 22.0599 | 21.2846 | 22.2564 | 21.5674 | 21.7438 | 21.8889 | 21.0801 | 21.1814 | 21.3972 | 20.4836 | 20.6321 | 20.928 | 21.9172 | 21.6789 | 21.321 | 20.4426 | 20.543 | 20.5095 | 22.0255 | 21.6302 | 21.165 | 21.9863 | 21.7196 | 21.345 | 19.9329 | 20.575 |  | 20.5636 | 20.1938 | 20.2804 | 18.9813 |  | 16.6999 | 16.6685 | 16.4137 | 16.6628 | 16.7838 | 17.4261 | 18.1131 | 16.1701 | 16.7764 | 16.1951 | 16.9182 | 17.8702 | 45.2404 | 48.4201 | 44.2966 | 21.323 |  |  | 0.45298 | -0.51985 | -38.9632 | 0.46782 | 0.14667 | -197.823 | 14.5955 | -0.63448 | -0.38599 | -0.16458 | -0.019846 | 8.8293 | 9.059 | 1.9789 | 21.7965 | 22.0288 | 22.2241 | 22.2978 | 22.1303 | 21.467 | 20.2809 | 22.2215 | 22.3931 | 22.4265 | 22.3871 | 22.0196 | 21.2667 | 22.3158 | 17.3069 | 17.0189 | 16.1811 | 16.2154 | 16.3018 | 17.0859 | 16.767 | 22.3869 | 22.1536 | 21.7191 | 22.1043 | 21.8125 | 21.3236 | 21.9501 | 21.5523 | 20.934 | 20.1355 | 20.4365 | 20.0116 | 19.8289 | 0.098312 | 0.087903 | 20.7693 | 22.0883 | 22.4017 | 20.126 | 21.6967 | 22.1494 | 21.97 | 21.7396 | 21.2997 | 21.8098 | 21.4737 | 21.0724 | 20.4751 | 20.5462 | 20.4354 | 20.4462 | 19.9003 |  | 20.2629 | 19.9181 | 20.1422 | 19.6939 | 20.1128 | 20.3546 |  | 20.4556 |  |  | 20.2307 | 20.1467 | 20.5565 | [5 empty] | 21.9651 | 20.3621 | 21.7042 | 22.0854 | 19.5574 | 21.2179 | 21.8516 | 19.4512 | 19.972 | 21.278 |  | 19.8262 | 21.0513 | 18.8965 | 19.8029 | 20.9563 | 19.5078 | 20.2255 | 19.0086 | 20.2589 | 19.138 | 20.3641 | 18.9268 | 20.2542 | 21.185 | 19.5213 | 19.8478 | 21.1115 | 19.0213 | 19.8482 | 20.9243 | 18.9655 | 20.2861 | 19.3279 | 19.9764 | 18.9333 | 20.2212 | -0.16634 | 20.9487 | 0.045943 | 0.013881 | -26.9964 | 3.0977 | 1.84 | -0.04 | 0.80377 | -0.8554 | -7.4055 | 0.81147 | 0.45495 | -16.7084 | 4.5384 | 0.43032 | 0.42578 | 0.43102 | 0.37778 | 0.46567 | 0.44479 | 0.42803
42838.4146 | -492 | 22.8875 | 22.8471 | 22.8369 | 22.7721 | 22.4101 | 21.7547 | 22.7174 | 21.8192 | 22.3705 | 22.3868 | 22.3691 | 22.0507 | 21.2762 | 22.2481 | 21.5639 | 21.7453 | 21.8823 | 21.0723 | 21.1679 | 21.3958 | 20.4771 | 20.6234 | 20.9305 | 21.9069 | 21.673 | 21.3107 | 20.4435 | 20.5375 | 20.5102 | 22.0311 | 21.6448 | 21.1776 | 21.9891 | 21.7269 | 21.3521 | 19.9341 | 20.5832 |  | 20.5658 | 20.204 | 20.2909 | 18.9791 |  | 16.7039 | 16.6816 | 16.4322 | 16.6832 | 16.7913 | 17.439 | 18.1399 | 16.0092 | 16.7787 | 16.2494 | 16.922 | 17.8766 | 45.2557 | 48.4198 | 44.2951 | 21.3268 |  |  | 0.52067 | -0.48173 | -39.4494 | 0.35151 | 0.16572 | -197.8755 | 14.7571 | -0.75802 | -0.27449 | -0.10857 | 0.091778 | 8.8284 | 9.0581 | 1.9785 | 21.784 | 22.0156 | 22.2177 | 22.2828 | 22.1111 | 21.4528 | 20.2718 | 22.2065 | 22.3914 | 22.425 | 22.378 | 22.0141 | 21.2533 | 22.2974 | 17.267 | 17.0257 | 16.1957 | 16.2237 | 16.2936 | 17.0819 | 16.7601 | 22.3875 | 22.1509 | 21.7239 | 22.0959 | 21.8234 | 21.3235 | 21.9529 | 21.5439 | 20.9306 | 20.131 | 20.4432 | 20.004 | 19.7615 | 0.015347 | -0.036678 | 20.7704 | 22.0902 | 22.3941 | 20.1264 | 21.6959 | 22.1435 | 21.9686 | 21.7328 | 21.299 | 21.8054 | 21.4713 | 21.0728 | 20.4833 | 20.5355 | 20.4306 | 20.4464 | 19.9118 |  | 20.2535 | 19.9185 | 20.139 | 19.6672 | 20.1126 | 20.3573 |  | 20.4469 |  |  | 20.2253 | 20.1559 | 20.5491 | [5 empty] | 21.9625 | 20.3495 | 21.6973 | 22.082 | 19.5544 | 21.2103 | 21.8464 | 19.4376 | 19.9745 | 21.2693 |  | 19.8219 | 21.0484 | 18.8956 | 19.804 | 20.9477 | 19.5042 | 20.2223 | 19.0139 | 20.2632 | 19.138 | 20.3635 | 18.9256 | 20.2469 | 21.1741 | 19.5097 | 19.8431 | 21.0972 | 19.0205 | 19.8307 | 20.9178 | 18.946 | 20.2774 | 19.3281 | 19.9703 | 18.9327 | 20.2134 | -0.36093 | 20.9484 | 0.046386 | 0.013105 | -26.9362 | 3.0977 | 0.56 | -0.35 | 0.86173 | -0.82346 | -7.4518 | 0.70341 | 0.48361 | -16.711 | 4.5636 | 0.42968 | 0.42566 | 0.43175 | 0.38175 | 0.46325 | 0.44489 | 0.42975
42838.4146 | -491 | 22.888 | 22.8534 | 22.8391 | 22.7709 | 22.4092 | 21.7589 | 22.7174 | 21.8198 | 22.3715 | 22.3794 | 22.375 | 22.0597 | 21.2783 | 22.2457 | 21.5717 | 21.748 | 21.8897 | 21.0754 | 21.1722 | 21.4048 | 20.4839 | 20.6308 | 20.9263 | 21.9043 | 21.6701 | 21.3103 | 20.4421 | 20.5397 | 20.5191 | 22.0303 | 21.6452 | 21.1775 | 21.9886 | 21.7325 | 21.3564 | 19.937 | 20.5866 |  | 20.5694 | 20.1959 | 20.2943 | 18.9636 |  | 16.7063 | 16.6969 | 16.4407 | 16.6933 | 16.8133 | 17.4486 | 18.1561 | 15.9023 | 16.7862 | 16.3482 | 16.9246 | 17.8622 | 45.2373 | 48.4099 | 44.2967 | 21.3256 |  |  | 0.70597 | -0.20771 | -39.4067 | 0.27923 | 0.22092 | -197.8893 | 14.7867 | -0.57731 | -0.17641 | -0.13059 | 0.15236 | 8.8295 | 9.0591 | 1.978 | 21.7887 | 22.0167 | 22.2169 | 22.2846 | 22.115 | 21.4598 | 20.2753 | 22.2134 | 22.3872 | 22.4202 | 22.3799 | 22.0149 | 21.2506 | 22.3008 | 17.2493 | 17.0719 | 16.2199 | 16.2834 | 16.3119 | 17.0808 | 16.7672 | 22.3881 | 22.1583 | 21.719 | 22.0942 | 21.8139 | 21.3259 | 21.9563 | 21.5463 | 20.9295 | 20.1344 | 20.4409 | 20.0038 | 19.7484 | 0.059385 | -0.020511 | 20.7697 | 22.0903 | 22.3929 | 20.1234 | 21.6972 | 22.1438 | 21.9671 | 21.7295 | 21.3036 | 21.8051 | 21.4689 | 21.0705 | 20.4822 | 20.5135 | 20.4284 | 20.4459 | 19.8979 |  | 20.2593 | 19.9314 | 20.1477 | 19.651 | 20.1143 | 20.3642 |  | 20.4598 |  |  | 20.2352 | 20.1769 | 20.5601 | [5 empty] | 21.9751 | 20.3513 | 21.7009 | 22.0872 | 19.5572 | 21.213 | 21.8417 | 19.4492 | 19.9688 | 21.2817 |  | 19.8232 | 21.0555 | 18.8948 | 19.8037 | 20.9479 | 19.4924 | 20.2258 | 19.0136 | 20.2587 | 19.1427 | 20.3629 | 18.9257 | 20.2381 | 21.1672 | 19.5071 | 19.8342 | 21.0975 | 19.0094 | 19.8322 | 20.911 | 18.941 | 20.2815 | 19.3202 | 19.9626 | 18.9266 | 20.217 | -0.10939 | 20.9491 | 0.045998 | 0.014252 | -27.0026 | 3.0976 | -4.78 | -0.12 | 1.0034 | -0.54073 | -7.4479 | 0.62695 | 0.55839 | -16.7119 | 4.5682 | 0.43026 | 0.42559 | 0.43226 | 0.38359 | 0.46138 | 0.44542 | 0.43023
42838.4146 | -490 | 22.8957 | 22.8642 | 22.8466 | 22.7757 | 22.4216 | 21.7636 | 22.7322 | 21.8262 | 22.3863 | 22.3997 | 22.3814 | 22.0624 | 21.297 | 22.2552 | 21.5672 | 21.7396 | 21.8724 | 21.0704 | 21.1642 | 21.3972 | 20.4829 | 20.6132 | 20.9241 | 21.8968 | 21.6633 | 21.3033 | 20.4408 | 20.5219 | 20.5115 | 22.0267 | 21.6458 | 21.1678 | 21.986 | 21.7304 | 21.356 | 19.9388 | 20.5866 |  | 20.5683 | 20.1953 | 20.2828 | 18.9586 |  | 16.6996 | 16.703 | 16.443 | 16.7092 | 16.8441 | 17.4848 | 18.1725 | 15.9084 | 16.7825 | 16.373 | 16.9155 | 17.8683 | 45.2254 | 48.4113 | 44.301 | 21.3307 |  |  | 0.60872 | -0.27343 | -39.3279 | 0.53682 | 0.28466 | -197.8545 | 14.7795 | -0.40646 | -0.16804 | -0.32823 | 0.10896 | 8.8294 | 9.0593 | 1.9778 | 21.786 | 22.019 | 22.2149 | 22.281 | 22.1148 | 21.4515 | 20.2761 | 22.2111 | 22.386 | 22.4218 | 22.3661 | 22.0151 | 21.2598 | 22.2972 | 17.2505 | 17.1156 | 16.243 | 16.3151 | 16.3245 | 17.0797 | 16.7677 | 22.3917 | 22.1633 | 21.7185 | 22.0968 | 21.8145 | 21.3279 | 21.9623 | 21.5491 | 20.928 | 20.1398 | 20.4335 | 19.9884 | 19.7238 | -0.0513 | -0.21413 | 20.7619 | 22.0865 | 22.3927 | 20.1179 | 21.7004 | 22.1427 | 21.9661 | 21.7336 | 21.3057 | 21.802 | 21.4701 | 21.0644 | 20.4781 | 20.4961 | 20.4243 | 20.4441 | 19.9052 |  | 20.2608 | 19.9523 | 20.146 | 19.6426 | 20.1169 | 20.368 |  | 20.46 |  |  | 20.2395 | 20.2017 | 20.5665 | [5 empty] | 21.9812 | 20.3481 | 21.7058 | 22.0875 | 19.5512 | 21.215 | 21.8462 | 19.4533 | 19.9708 | 21.2719 |  | 19.8393 | 21.0608 | 18.8909 | 19.805 | 20.9461 | 19.4884 | 20.2177 | 19.0157 | 20.2628 | 19.1404 | 20.3689 | 18.9362 | 20.2452 | 21.1795 | 19.5081 | 19.8321 | 21.1031 | 19.0204 | 19.8418 | 20.9198 | 18.9451 | 20.2898 | 19.327 | 19.9704 | 18.9344 | 20.2229 | -0.25686 | 20.9486 | 0.045962 | 0.013388 | -26.9515 | 3.0976 | 5.47 | -0.33 | 0.93175 | -0.6204 | -7.4406 | 0.8693 | 0.63388 | -16.7114 | 4.5674 | 0.43011 | 0.42496 | 0.43258 | 0.38331 | 0.45888 | 0.44562 | 0.43109
42838.4146 | -489 | 22.8872 | 22.8497 | 22.8397 | 22.768 | 22.405 | 21.7548 | 22.7098 | 21.8164 | 22.371 | 22.377 | 22.3719 | 22.0516 | 21.2747 | 22.2393 | 21.5688 | 21.7463 | 21.8775 | 21.0661 | 21.1791 | 21.3892 | 20.4874 | 20.6311 | 20.9302 | 21.898 | 21.6678 | 21.3091 | 20.4419 | 20.5219 | 20.5222 | 22.0299 | 21.6368 | 21.1677 | 21.9913 | 21.7265 | 21.346 | 19.931 | 20.5835 |  | 20.5704 | 20.1933 | 20.2853 | 18.949 |  | 16.7004 | 16.6942 | 16.4759 | 16.7268 | 16.8698 | 17.5016 | 18.1887 | 15.9512 | 16.7772 | 16.3613 | 16.9166 | 17.869 | 45.2044 | 48.412 | 44.2958 | 21.3367 |  |  | 0.54301 | -0.20837 | -39.3896 | 0.36137 | 0.14404 | -197.8289 | 14.6769 | -0.51357 | -0.26612 | -0.26403 | -0.013423 | 8.8289 | 9.0586 | 1.9785 | 21.7898 | 22.0238 | 22.2184 | 22.2834 | 22.1202 | 21.4527 | 20.2797 | 22.2124 | 22.388 | 22.4213 | 22.3706 | 22.0149 | 21.2597 | 22.2937 | 17.267 | 17.1218 | 16.2406 | 16.3242 | 16.3375 | 17.0813 | 16.7715 | 22.3855 | 22.1537 | 21.7222 | 22.0939 | 21.8105 | 21.3259 | 21.9526 | 21.5469 | 20.9276 | 20.1302 | 20.4297 | 19.9739 | 19.6836 | -0.13486 | -0.17457 | 20.7681 | 22.0938 | 22.3994 | 20.1204 | 21.6998 | 22.1505 | 21.9618 | 21.7361 | 21.3087 | 21.8067 | 21.474 | 21.0694 | 20.4795 | 20.4817 | 20.4285 | 20.4472 | 19.9107 |  | 20.2551 | 19.9477 | 20.142 | 19.6181 | 20.1193 | 20.3653 |  | 20.4563 |  |  | 20.2388 | 20.2123 | 20.5667 | [5 empty] | 21.9578 | 20.3416 | 21.6993 | 22.0802 | 19.5295 | 21.2141 | 21.8423 | 19.4377 | 19.9716 | 21.274 |  | 19.8397 | 21.0528 | 18.8957 | 19.8031 | 20.9506 | 19.4865 | 20.2106 | 19.0214 | 20.2663 | 19.1433 | 20.3592 | 18.9393 | 20.237 | 21.1716 | 19.493 | 19.8243 | 21.0985 | 19.009 | 19.8182 | 20.9105 | 18.9394 | 20.2882 | 19.3228 | 19.9627 | 18.9238 | 20.213 | -0.32902 | 20.9488 | 0.046263 | 0.013424 | -26.8995 | 3.0976 | 3.39 | 0.17 | 0.88004 | -0.54159 | -7.4463 | 0.71322 | 0.45092 | -16.7108 | 4.5517 | 0.42977 | 0.42495 | 0.43334 | 0.38167 | 0.45959 | 0.44562 | 0.43189
42838.4146 | -488 | 22.8906 | 22.848 | 22.8397 | 22.7782 | 22.4089 | 21.755 | 22.7157 | 21.8194 | 22.3684 | 22.3819 | 22.3673 | 22.0541 | 21.2792 | 22.2481 | 21.5586 | 21.7321 | 21.8731 | 21.0675 | 21.1618 | 21.3832 | 20.4749 | 20.6191 | 20.9159 | 21.8941 | 21.6634 | 21.3031 | 20.4211 | 20.5069 | 20.5091 | 22.0314 | 21.6365 | 21.1681 | 21.9851 | 21.7266 | 21.3534 | 19.9351 | 20.5844 |  | 20.573 | 20.1957 | 20.2844 | 18.9389 |  | 16.7037 | 16.7186 | 16.501 | 16.7492 | 16.9105 | 17.5287 | 18.1995 | 16.005 | 16.7808 | 16.3584 | 16.9255 | 17.8641 | 45.1635 | 48.393 | 44.2916 | 21.3315 |  |  | 0.56535 | -0.32205 | -39.3844 | 0.56311 | 0.079644 | -197.8506 | 14.8123 | -0.80664 | 0.032592 | -0.020659 | -0.00266 | 8.8296 | 9.0591 | 1.9791 | 21.7908 | 22.0183 | 22.2125 | 22.2832 | 22.1207 | 21.4526 | 20.2775 | 22.2127 | 22.3885 | 22.4241 | 22.3743 | 22.013 | 21.2558 | 22.2923 | 17.2889 | 17.0816 | 16.2332 | 16.3251 | 16.3192 | 17.0836 | 16.77 | 22.3789 | 22.1384 | 21.7132 | 22.0923 | 21.8116 | 21.3204 | 21.9389 | 21.5349 | 20.9174 | 20.1248 | 20.4118 | 19.9602 | 19.6678 | 0.069805 | -0.002822 | 20.7706 | 22.0979 | 22.4024 | 20.1263 | 21.7018 | 22.1531 | 21.9645 | 21.739 | 21.3044 | 21.8046 | 21.4804 | 21.0759 | 20.4803 | 20.4592 | 20.4302 | 20.4508 | 19.9177 |  | 20.2547 | 19.9339 | 20.1392 | 19.5951 | 20.1071 | 20.3511 |  | 20.4537 |  |  | 20.2404 | 20.2283 | 20.5561 | [5 empty] | 21.9602 | 20.3461 | 21.6953 | 22.0784 | 19.5189 | 21.2049 | 21.8334 | 19.44 | 19.9523 | 21.2616 |  | 19.8346 | 21.0432 | 18.9004 | 19.8003 | 20.9325 | 19.4771 | 20.2011 | 19.0241 | 20.2557 | 19.1487 | 20.3508 | 18.9436 | 20.2444 | 21.1759 | 19.5038 | 19.8232 | 21.0992 | 19.0074 | 19.8269 | 20.9137 | 18.9388 | 20.2834 | 19.3284 | 19.9629 | 18.9409 | 20.2193 | -0.31919 | 20.9491 | 0.045581 | 0.012771 | -26.9744 | 3.0977 | -10.42 | -0.13 | 0.89794 | -0.67334 | -7.4461 | 0.89035 | 0.33531 | -16.7125 | 4.5728 | 0.42956 | 0.42524 | 0.43357 | 0.37952 | 0.46023 | 0.44604 | 0.43215
42838.4146 | -487 | 22.8842 | 22.8398 | 22.8407 | 22.7728 | 22.4078 | 21.7508 | 22.7166 | 21.8233 | 22.3644 | 22.388 | 22.3724 | 22.0525 | 21.28 | 22.2452 | 21.5687 | 21.7459 | 21.8857 | 21.0735 | 21.1772 | 21.3967 | 20.4818 | 20.6296 | 20.9201 | 21.9091 | 21.663 | 21.3078 | 20.4396 | 20.5067 | 20.5159 | 22.0312 | 21.644 | 21.1678 | 21.9771 | 21.7302 | 21.3516 | 19.9278 | 20.5872 |  | 20.5736 | 20.2011 | 20.2836 | 18.9412 |  | 16.7324 | 16.7333 | 16.5199 | 16.7823 | 16.9177 | 17.5205 | 18.1746 | 16.0009 | 16.7898 | 16.3615 | 16.9232 | 17.8651 | 45.1424 | 48.3768 | 44.2987 | 21.3216 |  |  | 0.65735 | -0.2294 | -39.3574 | 0.63605 | 0.11776 | -197.8335 | 14.6369 | -0.72647 | -0.15598 | -0.022128 | -0.19084 | 8.8291 | 9.0589 | 1.9786 | 21.7938 | 22.024 | 22.2116 | 22.284 | 22.121 | 21.4508 | 20.2791 | 22.2154 | 22.3846 | 22.4113 | 22.3809 | 22.0222 | 21.2637 | 22.297 | 17.303 | 17.0606 | 16.2327 | 16.3293 | 16.3068 | 17.0795 | 16.7657 | 22.3869 | 22.159 | 21.7187 | 22.0923 | 21.8172 | 21.3254 | 21.9584 | 21.5494 | 20.9266 | 20.1402 | 20.4271 | 19.9661 | 19.6821 | 0.032255 | -0.23296 | 20.7744 | 22.0882 | 22.3993 | 20.1308 | 21.7036 | 22.1506 | 21.9688 | 21.7391 | 21.3035 | 21.8016 | 21.479 | 21.0739 | 20.4783 | 20.4437 | 20.4272 | 20.453 | 19.9358 |  | 20.2574 | 19.9044 | 20.1419 | 19.5822 | 20.1057 | 20.3581 |  | 20.4507 |  |  | 20.2282 | 20.2302 | 20.5589 | [5 empty] | 21.9523 | 20.3452 | 21.6905 | 22.077 | 19.5082 | 21.2104 | 21.8366 | 19.4449 | 19.9545 | 21.2798 |  | 19.8271 | 21.0493 | 18.8916 | 19.8086 | 20.9427 | 19.4802 | 20.1949 | 19.0286 | 20.2551 | 19.146 | 20.3644 | 18.9434 | 20.2605 | 21.1723 | 19.5009 | 19.8264 | 21.1061 | 19.0146 | 19.8321 | 20.92 | 18.9484 | 20.2933 | 19.3299 | 19.9595 | 18.9452 | 20.2235 | -0.33459 | 20.9494 | 0.046724 | 0.012444 | -27.01 | 3.0976 | -0.87 | -0.3 | 0.96826 | -0.56829 | -7.4438 | 0.94629 | 0.40772 | -16.7116 | 4.5456 | 0.42915 | 0.42615 | 0.43388 | 0.37746 | 0.45978 | 0.44573 | 0.43226
42838.4147 | -486 | 22.8845 | 22.849 | 22.8351 | 22.7655 | 22.409 | 21.7543 | 22.7177 | 21.8227 | 22.3721 | 22.3854 | 22.3693 | 22.0492 | 21.2804 | 22.2407 | 21.5727 | 21.7395 | 21.8856 | 21.0771 | 21.1762 | 21.4035 | 20.4904 | 20.6255 | 20.9218 | 21.8977 | 21.6697 | 21.3052 | 20.4452 | 20.4968 | 20.5149 | 22.0348 | 21.6472 | 21.1737 | 21.9808 | 21.7328 | 21.3577 | 19.9331 | 20.5994 |  | 20.5758 | 20.2001 | 20.2831 | 18.9513 |  | 16.7344 | 16.7594 | 16.5397 | 16.7814 | 16.9054 | 17.5024 | 18.1452 | 16.0109 | 16.7823 | 16.355 | 16.917 | 17.8705 | 45.1274 | 48.3686 | 44.3052 | 21.3359 |  |  | 0.41356 | -0.14857 | -39.0808 | 0.61567 | 0.17558 | -197.8079 | 14.5107 | -0.79678 | -0.20268 | 0.059485 | -0.19484 | 8.8288 | 9.0584 | 1.9783 | 21.7921 | 22.0165 | 22.22 | 22.2928 | 22.114 | 21.453 | 20.2679 | 22.2029 | 22.3827 | 22.4158 | 22.3719 | 22.024 | 21.2594 | 22.3017 | 17.3485 | 17.0581 | 16.2531 | 16.3384 | 16.3252 | 17.0836 | 16.7696 | 22.3842 | 22.1566 | 21.7152 | 22.0925 | 21.8153 | 21.3264 | 21.9583 | 21.5458 | 20.9211 | 20.1322 | 20.4183 | 19.9569 | 19.6878 | -0.07332 | -0.12322 | 20.7798 | 22.0933 | 22.4076 | 20.1313 | 21.702 | 22.1514 | 21.9785 | 21.7394 | 21.3122 | 21.8059 | 21.4764 | 21.0768 | 20.4814 | 20.4265 | 20.433 | 20.4504 | 19.9492 |  | 20.2596 | 19.8888 | 20.1445 | 19.5679 | 20.113 | 20.3549 |  | 20.455 |  |  | 20.2263 | 20.2329 | 20.5445 | [5 empty] | 21.9547 | 20.3389 | 21.6931 | 22.0766 | 19.5073 | 21.1988 | 21.8295 | 19.4484 | 19.9563 | 21.2766 |  | 19.831 | 21.0507 | 18.8872 | 19.816 | 20.9408 | 19.4751 | 20.1847 | 19.0265 | 20.2648 | 19.1552 | 20.3591 | 18.9454 | 20.2565 | 21.1765 | 19.5052 | 19.8221 | 21.1044 | 19.0031 | 19.8291 | 20.9194 | 18.9443 | 20.2985 | 19.3328 | 19.9551 | 18.9442 | 20.2185 | -0.27894 | 20.9497 | 0.045863 | 0.012016 | -27.0425 | 3.0976 | 14.23 | -0.06 | 0.768 | -0.45737 | -7.4179 | 0.93105 | 0.49784 | -16.71 | 4.5258 | 0.42885 | 0.42667 | 0.43453 | 0.37289 | 0.45798 | 0.44563 | 0.43184
42838.4147 | -485 | 22.8853 | 22.8473 | 22.8444 | 22.7711 | 22.4131 | 21.7581 | 22.721 | 21.8217 | 22.3778 | 22.3913 | 22.3674 | 22.0531 | 21.2833 | 22.2518 | 21.5748 | 21.7448 | 21.8834 | 21.0743 | 21.1725 | 21.3942 | 20.4827 | 20.622 | 20.9159 | 21.9051 | 21.6736 | 21.3072 | 20.4392 | 20.4862 | 20.5169 | 22.0352 | 21.6426 | 21.1709 | 21.9868 | 21.7336 | 21.3559 | 19.9369 | 20.6169 |  | 20.5773 | 20.1974 | 20.2805 | 18.9691 |  | 16.7479 | 16.7989 | 16.5503 | 16.7713 | 16.9012 | 17.4784 | 18.1336 | 16.0311 | 16.7764 | 16.3592 | 16.9172 | 17.8707 | 45.1084 | 48.3673 | 44.3156 | 21.3345 |  |  | 0.47927 | -0.12886 | -40.577 | 0.60516 | 0.15127 | -197.8328 | 14.0619 | -0.76459 | 0.033175 | -0.12304 | 0.048205 | 8.8278 | 9.0576 | 1.9786 | 21.7863 | 22.0183 | 22.2111 | 22.2886 | 22.1239 | 21.4521 | 20.2759 | 22.2155 | 22.3867 | 22.4244 | 22.3789 | 22.0232 | 21.262 | 22.2956 | 17.3828 | 17.1022 | 16.2604 | 16.3282 | 16.3399 | 17.0881 | 16.7694 | 22.3825 | 22.1576 | 21.7143 | 22.0913 | 21.8142 | 21.3261 | 21.9509 | 21.5485 | 20.9241 | 20.1308 | 20.4131 | 19.9471 | 19.6918 | -0.017092 | -0.12265 | 20.7711 | 22.0962 | 22.4072 | 20.1245 | 21.6991 | 22.1465 | 21.9739 | 21.7397 | 21.3099 | 21.8062 | 21.4714 | 21.0718 | 20.4831 | 20.4008 | 20.4284 | 20.4428 | 19.9607 |  | 20.2543 | 19.8719 | 20.144 | 19.5514 | 20.1186 | 20.359 |  | 20.4534 |  |  | 20.2114 | 20.2414 | 20.5499 | [5 empty] | 21.9723 | 20.3415 | 21.6959 | 22.0827 | 19.5181 | 21.2057 | 21.8433 | 19.4469 | 19.9566 | 21.2647 |  | 19.832 | 21.0464 | 18.8856 | 19.8182 | 20.9561 | 19.47 | 20.175 | 19.0304 | 20.2585 | 19.154 | 20.3579 | 18.9281 | 20.252 | 21.1645 | 19.5028 | 19.8203 | 21.1026 | 19.0041 | 19.8281 | 20.9157 | 18.9361 | 20.2964 | 19.3268 | 19.9544 | 18.9405 | 20.214 | -0.13573 | 20.9506 | 0.04657 | 0.012843 | -27.0009 | 3.0976 | 9.55 | -0.01 | 0.82677 | -0.42598 | -7.5591 | 0.92313 | 0.46207 | -16.7103 | 4.4551 | 0.42835 | 0.42712 | 0.43517 | 0.3696 | 0.45713 | 0.44526 | 0.43168
42838.4147 | -484 | 22.8787 | 22.8441 | 22.8407 | 22.771 | 22.4105 | 21.7516 | 22.7198 | 21.8186 | 22.3765 | 22.3824 | 22.3669 | 22.0485 | 21.2753 | 22.2488 | 21.5794 | 21.7497 | 21.8828 | 21.0802 | 21.177 | 21.398 | 20.4849 | 20.6247 | 20.9235 | 21.9087 | 21.6748 | 21.3101 | 20.4426 | 20.4769 | 20.5203 | 22.0364 | 21.6405 | 21.1761 | 21.9921 | 21.7311 | 21.3561 | 19.9421 | 20.6152 |  | 20.5803 | 20.1944 | 20.2754 | 18.9861 |  | 16.7747 | 16.8075 | 16.5549 | 16.7766 | 16.8924 | 17.4633 | 18.1135 | 16.0284 | 16.7804 | 16.3456 | 16.9222 | 17.8661 | 45.1081 | 48.3624 | 44.3153 | 21.3353 |  |  | 0.7086 | -0.044093 | -41.8315 | 0.52828 | 0.13944 | -197.8558 | 13.9344 | -0.78233 | -0.066849 | -0.32697 | -0.16446 | 8.8292 | 9.0589 | 1.9778 | 21.7855 | 22.0181 | 22.2183 | 22.2905 | 22.1239 | 21.4582 | 20.2718 | 22.2206 | 22.3881 | 22.4286 | 22.3841 | 22.0138 | 21.2587 | 22.2984 | 17.4145 | 17.1307 | 16.2668 | 16.3243 | 16.349 | 17.0845 | 16.7715 | 22.3859 | 22.1594 | 21.7189 | 22.0938 | 21.8094 | 21.3189 | 21.9541 | 21.5443 | 20.9253 | 20.1239 | 20.4082 | 19.9409 | 19.697 | -0.06172 | -0.14452 | 20.7673 | 22.0973 | 22.4058 | 20.1288 | 21.6988 | 22.1463 | 21.9694 | 21.7407 | 21.3045 | 21.8109 | 21.4719 | 21.0717 | 20.483 | 20.3827 | 20.4302 | 20.4443 | 19.9587 |  | 20.2616 | 19.8604 | 20.1486 | 19.5531 | 20.1141 | 20.3641 |  | 20.4529 |  |  | 20.1934 | 20.2169 | 20.5622 | [5 empty] | 21.9637 | 20.3362 | 21.6962 | 22.0858 | 19.5103 | 21.2109 | 21.8403 | 19.4407 | 19.9531 | 21.2651 |  | 19.8288 | 21.0432 | 18.8802 | 19.8153 | 20.9422 | 19.465 | 20.1695 | 19.0304 | 20.2513 | 19.143 | 20.351 | 18.9414 | 20.2586 | 21.1733 | 19.5072 | 19.8245 | 21.1078 | 19.0141 | 19.8296 | 20.9235 | 18.9408 | 20.3095 | 19.3268 | 19.9681 | 18.9463 | 20.2204 | -0.23479 | 20.9492 | 0.046453 | 0.012553 | -27.0222 | 3.0976 | -2.93 | -0.01 | 1.0053 | -0.24918 | -7.6751 | 0.86251 | 0.44363 | -16.7109 | 4.4347 | 0.42865 | 0.4276 | 0.43497 | 0.36565 | 0.45667 | 0.44496 | 0.43131
42838.4147 | -483 | 22.8834 | 22.8457 | 22.8378 | 22.7685 | 22.4199 | 21.7522 | 22.7167 | 21.8177 | 22.3737 | 22.3847 | 22.3783 | 22.0614 | 21.2778 | 22.2526 | 21.57 | 21.7419 | 21.8738 | 21.0756 | 21.1682 | 21.3948 | 20.4812 | 20.6218 | 20.9193 | 21.9012 | 21.6694 | 21.3063 | 20.4407 | 20.4633 | 20.5186 | 22.0425 | 21.6513 | 21.1769 | 21.9864 | 21.7357 | 21.3563 | 19.9357 | 20.6144 |  | 20.5736 | 20.2029 | 20.2742 | 19.0101 |  | 16.7931 | 16.811 | 16.5633 | 16.7824 | 16.8934 | 17.4405 | 18.0719 | 16.0333 | 16.783 | 16.2907 | 16.9236 | 17.8738 | 45.0969 | 48.3731 | 44.3413 | 21.3393 |  |  | 0.31367 | -0.42456 | -42.641 | 0.68796 | 0.17427 | -197.8486 | 14.1125 | -0.59965 | -0.12718 | -0.22815 | -0.090675 | 8.8283 | 9.0579 | 1.9786 | 21.7878 | 22.0199 | 22.2176 | 22.2846 | 22.1163 | 21.456 | 20.2707 | 22.2124 | 22.3802 | 22.4266 | 22.3703 | 22.0114 | 21.2547 | 22.2969 | 17.4244 | 17.1381 | 16.2687 | 16.3095 | 16.3506 | 17.0822 | 16.771 | 22.3835 | 22.152 | 21.7189 | 22.0856 | 21.8094 | 21.3216 | 21.9607 | 21.5435 | 20.9275 | 20.1285 | 20.4093 | 19.9369 | 19.7155 | -0.19777 | 0.014676 | 20.7688 | 22.0947 | 22.4036 | 20.1297 | 21.6964 | 22.145 | 21.9661 | 21.7375 | 21.3024 | 21.8047 | 21.4735 | 21.0742 | 20.4848 | 20.357 | 20.4326 | 20.4441 | 19.9659 |  | 20.2602 | 19.8558 | 20.1428 | 19.5603 | 20.1165 | 20.3707 |  | 20.4625 |  |  | 20.1906 | 20.1756 | 20.5627 | [5 empty] | 21.9594 | 20.3393 | 21.6985 | 22.0826 | 19.5079 | 21.209 | 21.8394 | 19.4431 | 19.9453 | 21.2628 |  | 19.8284 | 21.0411 | 18.8817 | 19.8125 | 20.9376 | 19.4608 | 20.1677 | 19.0335 | 20.2424 | 19.1369 | 20.3464 | 18.9425 | 20.2561 | 21.1731 | 19.5145 | 19.825 | 21.1111 | 19.0019 | 19.829 | 20.9231 | 18.9369 | 20.3096 | 19.333 | 19.967 | 18.94 | 20.2137 | -0.22811 | 20.9504 | 0.046508 | 0.012183 | -26.9994 | 3.0976 | -33.15 | -0.03 | 0.66886 | -0.77323 | -7.7491 | 0.98428 | 0.49593 | -16.7099 | 4.4628 | 0.4284 | 0.42753 | 0.43485 | 0.36429 | 0.4564 | 0.44408 | 0.43095
42838.4147 | -482 | 22.8922 | 22.8518 | 22.8428 | 22.7793 | 22.4142 | 21.7619 | 22.7281 | 21.8218 | 22.3761 | 22.3932 | 22.3778 | 22.0589 | 21.2872 | 22.2498 | 21.574 | 21.7495 | 21.8834 | 21.0783 | 21.172 | 21.4015 | 20.4799 | 20.6314 | 20.9205 | 21.9029 | 21.6722 | 21.3087 | 20.4429 | 20.4612 | 20.523 | 22.0302 | 21.6459 | 21.1737 | 21.9758 | 21.7344 | 21.349 | 19.9254 | 20.5992 |  | 20.57 | 20.1959 | 20.2705 | 19.0177 |  | 16.7995 | 16.8234 | 16.5702 | 16.7863 | 16.9037 | 17.4389 | 18.0224 | 16.0371 | 16.7855 | 16.1666 | 16.9318 | 17.8648 | 45.0951 | 48.3751 | 44.3491 | 21.3339 |  |  | 0.43918 | -0.59476 | -43.2186 | 0.91401 | 0.13944 | -197.9071 | 13.9554 | -0.60425 | 0.16005 | -0.39599 | 0.0070616 | 8.829 | 9.0588 | 1.9791 | 21.7954 | 22.0229 | 22.221 | 22.2829 | 22.1264 | 21.4528 | 20.2766 | 22.2162 | 22.3877 | 22.4262 | 22.3728 | 22.0201 | 21.2586 | 22.301 | 17.43 | 17.1017 | 16.2638 | 16.2909 | 16.3658 | 17.0826 | 16.7633 | 22.3895 | 22.1671 | 21.72 | 22.0885 | 21.8134 | 21.3248 | 21.9532 | 21.5466 | 20.9236 | 20.1334 | 20.4218 | 19.9449 | 19.7237 | 0.039922 | -0.12265 | 20.7711 | 22.0935 | 22.3999 | 20.1259 | 21.6972 | 22.1459 | 21.9634 | 21.7326 | 21.3022 | 21.8048 | 21.4703 | 21.0715 | 20.4926 | 20.3289 | 20.4289 | 20.4473 | 19.9756 |  | 20.2572 | 19.8436 | 20.1476 | 19.5606 | 20.1198 | 20.3678 |  | 20.45 |  |  | 20.1834 | 20.1527 | 20.5573 | [5 empty] | 21.96 | 20.3346 | 21.7016 | 22.0812 | 19.5065 | 21.2082 | 21.8345 | 19.4441 | 19.9478 | 21.259 |  | 19.826 | 21.0433 | 18.8848 | 19.8116 | 20.939 | 19.4524 | 20.1575 | 19.0306 | 20.2359 | 19.1322 | 20.3464 | 18.9339 | 20.2352 | 21.1668 | 19.5061 | 19.8229 | 21.1025 | 18.992 | 19.823 | 20.9165 | 18.9295 | 20.301 | 19.3277 | 19.966 | 18.9362 | 20.2 | -0.18155 | 20.9499 | 0.046281 | 0.011827 | -27.0916 | 3.0976 | -2.01 | 0 | 0.79145 | -0.9152 | -7.8016 | 1.1345 | 0.44361 | -16.7123 | 4.4379 | 0.42803 | 0.42802 | 0.43496 | 0.36372 | 0.45606 | 0.44353 | 0.43088
42838.4147 | -481 | 22.8919 | 22.8558 | 22.8466 | 22.7707 | 22.4119 | 21.7613 | 22.722 | 21.8188 | 22.3729 | 22.3836 | 22.3762 | 22.0581 | 21.2805 | 22.2529 | 21.5748 | 21.7459 | 21.8856 | 21.0777 | 21.1744 | 21.3976 | 20.4828 | 20.632 | 20.9262 | 21.9001 | 21.6713 | 21.3046 | 20.4419 | 20.4471 | 20.5198 | 22.0295 | 21.6418 | 21.1726 | 21.9853 | 21.7328 | 21.3487 | 19.9386 | 20.5919 |  | 20.5825 | 20.1944 | 20.2734 | 19.033 |  | 16.8049 | 16.8131 | 16.5765 | 16.8012 | 16.9096 | 17.4158 | 17.9928 | 16.0255 | 16.7908 | 16.0846 | 16.9196 | 17.8675 | 45.0696 | 48.3722 | 44.363 | 21.3383 |  |  | 0.53315 | -0.27803 | -43.3685 | 0.51251 | 0.12696 | -197.8105 | 13.7189 | -0.51488 | 0.15052 | -0.054017 | -0.15595 | 8.8294 | 9.0589 | 1.9788 | 21.7902 | 22.0218 | 22.2181 | 22.282 | 22.1204 | 21.4578 | 20.2746 | 22.2166 | 22.3898 | 22.4253 | 22.3796 | 22.0221 | 21.2567 | 22.2992 | 17.4617 | 17.0638 | 16.2622 | 16.2954 | 16.3729 | 17.082 | 16.7629 | 22.3819 | 22.1559 | 21.7125 | 22.0887 | 21.8174 | 21.321 | 21.9523 | 21.5454 | 20.9216 | 20.1278 | 20.4109 | 19.9366 | 19.7226 | -0.15825 | -0.098112 | 20.7765 | 22.1036 | 22.4006 | 20.1342 | 21.7001 | 22.1525 | 21.9705 | 21.7397 | 21.3037 | 21.8114 | 21.4772 | 21.0733 | 20.4921 | 20.304 | 20.4279 | 20.4509 | 19.9748 |  | 20.259 | 19.8157 | 20.1513 | 19.5511 | 20.1105 | 20.3644 |  | 20.4515 |  |  | 20.1641 | 20.1492 | 20.5459 | [5 empty] | 21.9546 | 20.3299 | 21.6961 | 22.0825 | 19.5129 | 21.2074 | 21.8386 | 19.4536 | 19.9574 | 21.2668 |  | 19.83 | 21.0471 | 18.8899 | 19.825 | 20.9432 | 19.4541 | 20.1567 | 19.0343 | 20.2448 | 19.1346 | 20.3474 | 18.9367 | 20.2273 | 21.1637 | 19.5074 | 19.8306 | 21.1021 | 18.99 | 19.8233 | 20.9213 | 18.9364 | 20.3015 | 19.3288 | 19.9718 | 18.9411 | 20.1998 | -0.37744 | 20.9498 | 0.046115 | 0.012611 | -27.0328 | 3.0976 | -1.3 | 0.19 | 0.87201 | -0.62572 | -7.8149 | 0.84955 | 0.42327 | -16.7076 | 4.4 | 0.42811 | 0.42893 | 0.43491 | 0.36013 | 0.45617 | 0.44354 | 0.43072
42838.4147 | -480 | 22.8852 | 22.8468 | 22.8375 | 22.7633 | 22.4121 | 21.7577 | 22.717 | 21.8201 | 22.3685 | 22.3837 | 22.3701 | 22.0537 | 21.2764 | 22.2411 | 21.5627 | 21.739 | 21.8802 | 21.071 | 21.164 | 21.3874 | 20.476 | 20.6148 | 20.9209 | 21.8903 | 21.6629 | 21.2992 | 20.4356 | 20.431 | 20.5094 | 22.0299 | 21.6551 | 21.1733 | 21.995 | 21.7376 | 21.3527 | 19.9428 | 20.5961 |  | 20.5869 | 20.202 | 20.2787 | 19.0492 |  | 16.8176 | 16.8296 | 16.5924 | 16.8317 | 16.9231 | 17.4269 | 17.9953 | 15.9561 | 16.7925 | 16.0897 | 16.9225 | 17.8674 | 45.0684 | 48.3647 | 44.3673 | 21.3328 |  |  | 0.36559 | -0.25042 | -43.1957 | 0.21286 | 0.1999 | -197.8644 | 13.5848 | -0.65748 | -0.10986 | -0.20172 | -0.09189 | 8.8288 | 9.0586 | 1.9783 | 21.7886 | 22.0183 | 22.2124 | 22.2801 | 22.1177 | 21.457 | 20.2728 | 22.2145 | 22.3846 | 22.416 | 22.3838 | 22.0148 | 21.2524 | 22.2914 | 17.4687 | 17.045 | 16.272 | 16.3027 | 16.3681 | 17.0781 | 16.7613 | 22.3884 | 22.1575 | 21.7183 | 22.092 | 21.816 | 21.3195 | 21.955 | 21.5496 | 20.9289 | 20.1307 | 20.4144 | 19.9433 | 19.7217 | -0.098681 | -0.004724 | 20.7733 | 22.0967 | 22.3987 | 20.1399 | 21.6981 | 22.1495 | 21.972 | 21.7334 | 21.3063 | 21.8118 | 21.4777 | 21.0722 | 20.4871 | 20.2938 | 20.433 | 20.4439 | 19.9846 |  | 20.2561 | 19.7818 | 20.147 | 19.5461 | 20.1126 | 20.366 |  | 20.4561 |  |  | 20.1474 | 20.144 | 20.5434 | [5 empty] | 21.9586 | 20.3219 | 21.691 | 22.0824 | 19.5185 | 21.2049 | 21.8366 | 19.4529 | 19.9507 | 21.262 |  | 19.8194 | 21.0373 | 18.8882 | 19.8179 | 20.9362 | 19.4476 | 20.154 | 19.0263 | 20.2365 | 19.1285 | 20.3418 | 18.948 | 20.2192 | 21.1652 | 19.5114 | 19.8252 | 21.1017 | 18.9831 | 19.8156 | 20.9211 | 18.9386 | 20.3042 | 19.329 | 19.9777 | 18.9381 | 20.2023 | -0.29174 | 20.95 | 0.046048 | 0.012458 | -27.0423 | 3.0976 | 3.9 | -0.46 | 0.72208 | -0.59387 | -7.7996 | 0.54752 | 0.53113 | -16.7102 | 4.3785 | 0.42775 | 0.42972 | 0.43512 | 0.35889 | 0.45491 | 0.44323 | 0.43084
42838.4147 | -479 | 22.8898 | 22.8565 | 22.84 | 22.7698 | 22.4121 | 21.7587 | 22.7162 | 21.8185 | 22.3705 | 22.3856 | 22.3699 | 22.0573 | 21.2741 | 22.2431 | 21.5688 | 21.748 | 21.8801 | 21.0745 | 21.1662 | 21.3904 | 20.4824 | 20.6196 | 20.9244 | 21.9012 | 21.6659 | 21.3077 | 20.4375 | 20.4293 | 20.5144 | 22.031 | 21.6478 | 21.1749 | 21.9873 | 21.7343 | 21.3542 | 19.9358 | 20.5756 |  | 20.5863 | 20.202 | 20.2759 | 19.0648 |  | 16.8195 | 16.8402 | 16.6031 | 16.8404 | 16.9304 | 17.449 | 17.9961 | 15.9472 | 16.793 | 16.096 | 16.9219 | 17.8657 | 45.0834 | 48.36 | 44.3704 | 21.3317 |  |  | 0.58638 | -0.26225 | -44.3942 | 0.32457 | 0.23472 | -197.8171 | 13.2615 | -0.57468 | -0.11239 | -0.26193 | -0.088939 | 8.828 | 9.0578 | 1.9783 | 21.7833 | 22.0175 | 22.2103 | 22.2833 | 22.1191 | 21.4433 | 20.2697 | 22.21 | 22.383 | 22.4217 | 22.3707 | 22.0108 | 21.2587 | 22.2955 | 17.4672 | 17.0404 | 16.2768 | 16.3021 | 16.3832 | 17.0842 | 16.7591 | 22.3831 | 22.1592 | 21.7153 | 22.0857 | 21.8125 | 21.3191 | 21.9515 | 21.544 | 20.9246 | 20.1306 | 20.4124 | 19.941 | 19.7263 | -0.059164 | -0.063686 | 20.7735 | 22.0902 | 22.3973 | 20.1413 | 21.6991 | 22.1503 | 21.9718 | 21.7336 | 21.3033 | 21.8163 | 21.4756 | 21.0679 | 20.4816 | 20.2996 | 20.4347 | 20.4501 | 19.9893 |  | 20.2536 | 19.75 | 20.1579 | 19.5416 | 20.1196 | 20.3773 |  | 20.4603 |  |  | 20.1558 | 20.146 | 20.5508 | [5 empty] | 21.9661 | 20.3199 | 21.6985 | 22.0859 | 19.5227 | 21.2073 | 21.8358 | 19.452 | 19.9489 | 21.2612 |  | 19.8019 | 21.0379 | 18.8808 | 19.8235 | 20.9376 | 19.4406 | 20.1445 | 19.0293 | 20.235 | 19.1272 | 20.3444 | 18.9539 | 20.2131 | 21.1566 | 19.5132 | 19.8232 | 21.0958 | 18.9678 | 19.8096 | 20.9151 | 18.9333 | 20.2965 | 19.3267 | 19.9727 | 18.9352 | 20.2007 | -0.36946 | 20.9483 | 0.0463 | 0.012451 | -26.9375 | 3.0977 | 6.2 | -0.04 | 0.9145 | -0.60774 | -7.9072 | 0.6761 | 0.57556 | -16.7088 | 4.3262 | 0.42753 | 0.43097 | 0.43548 | 0.35977 | 0.45412 | 0.44257 | 0.43072
42838.4147 | -478 | 22.8904 | 22.8493 | 22.8396 | 22.7686 | 22.4105 | 21.755 | 22.713 | 21.8147 | 22.3699 | 22.3831 | 22.372 | 22.0587 | 21.2749 | 22.2458 | 21.5656 | 21.7475 | 21.8848 | 21.0814 | 21.1737 | 21.3988 | 20.4828 | 20.6298 | 20.9264 | 21.9048 | 21.6722 | 21.3107 | 20.4428 | 20.4263 | 20.5133 | 22.0334 | 21.6433 | 21.1662 | 21.9815 | 21.7254 | 21.3466 | 19.9245 | 20.5556 |  | 20.5752 | 20.1955 | 20.2686 | 19.073 |  | 16.8152 | 16.8477 | 16.6108 | 16.8497 | 16.9395 | 17.4726 | 18.006 | 15.9489 | 16.7817 | 16.0804 | 16.9134 | 17.8769 | 45.0896 | 48.3651 | 44.3769 | 21.3412 |  |  | 0.81243 | -0.37594 | -44.912 | 0.226 | 0.31292 | -197.8572 | 12.8423 | -0.54577 | 0.21143 | -0.056745 | -0.16966 | 8.8282 | 9.058 | 1.978 | 21.7834 | 22.0167 | 22.2216 | 22.2867 | 22.125 | 21.4461 | 20.2713 | 22.2117 | 22.385 | 22.4162 | 22.3755 | 22.0113 | 21.2485 | 22.2907 | 17.46 | 17.0615 | 16.2594 | 16.2995 | 16.3955 | 17.0792 | 16.7668 | 22.3812 | 22.1435 | 21.7156 | 22.0857 | 21.8111 | 21.322 | 21.9561 | 21.5396 | 20.9258 | 20.114 | 20.4102 | 19.9353 | 19.7323 | -0.10065 | -0.041813 | 20.7741 | 22.0895 | 22.403 | 20.1493 | 21.699 | 22.1505 | 21.9742 | 21.737 | 21.3043 | 21.8146 | 21.4692 | 21.0702 | 20.4711 | 20.2983 | 20.4353 | 20.4529 | 19.9912 |  | 20.2517 | 19.7206 | 20.1485 | 19.556 | 20.1178 | 20.3783 |  | 20.4586 |  |  | 20.1573 | 20.1553 | 20.5614 | [5 empty] | 21.9671 | 20.3079 | 21.7046 | 22.0848 | 19.5257 | 21.2075 | 21.831 | 19.4697 | 19.9645 | 21.2706 |  | 19.7983 | 21.0421 | 18.8903 | 19.8365 | 20.9488 | 19.4478 | 20.1544 | 19.0457 | 20.238 | 19.1366 | 20.3538 | 18.9633 | 20.2142 | 21.161 | 19.5187 | 19.8327 | 21.0999 | 18.9706 | 19.819 | 20.9251 | 18.9503 | 20.2993 | 19.3373 | 19.9638 | 18.9511 | 20.2109 | -0.14798 | 20.9491 | 0.046951 | 0.012567 | -26.9826 | 3.0976 | -4.48 | 0.19 | 1.0764 | -0.72765 | -7.9533 | 0.56418 | 0.66458 | -16.7112 | 4.2575 | 0.42742 | 0.43147 | 0.43502 | 0.35999 | 0.45695 | 0.44196 | 0.42999
42838.4148 | -477 | 22.8874 | 22.8512 | 22.8456 | 22.7665 | 22.4108 | 21.758 | 22.718 | 21.8262 | 22.3712 | 22.3829 | 22.375 | 22.0671 | 21.2842 | 22.2538 | 21.5714 | 21.7491 | 21.8858 | 21.08 | 21.1735 | 21.3945 | 20.4751 | 20.6255 | 20.9278 | 21.9017 | 21.6779 | 21.3151 | 20.4362 | 20.4178 | 20.5003 | 22.0315 | 21.6417 | 21.167 | 21.9812 | 21.7278 | 21.3502 | 19.9291 | 20.5477 |  | 20.5742 | 20.2064 | 20.2697 | 19.0879 |  | 16.8364 | 16.8718 | 16.6097 | 16.8591 | 16.9592 | 17.4955 | 17.9872 | 15.9475 | 16.7879 | 16.1113 | 16.9135 | 17.8669 | 45.0754 | 48.3633 | 44.3644 | 21.3289 |  |  | 0.57126 | -0.32205 | -45.7939 | 0.54208 | 0.26692 | -197.8348 | 12.3199 | -0.58979 | -0.15014 | -0.11885 | 0.073377 | 8.8284 | 9.0581 | 1.9791 | 21.7919 | 22.0215 | 22.2124 | 22.2895 | 22.1183 | 21.4516 | 20.2779 | 22.2144 | 22.3823 | 22.4276 | 22.3778 | 22.0182 | 21.2573 | 22.2967 | 17.462 | 17.097 | 16.2596 | 16.3018 | 16.3922 | 17.0809 | 16.7673 | 22.3846 | 22.1468 | 21.7142 | 22.0911 | 21.8123 | 21.3222 | 21.9525 | 21.5366 | 20.9205 | 20.1169 | 20.4119 | 19.9447 | 19.7423 | 0.04641 | -0.081184 | 20.7667 | 22.0946 | 22.4018 | 20.1449 | 21.6981 | 22.1471 | 21.9721 | 21.7336 | 21.3048 | 21.8087 | 21.4679 | 21.0773 | 20.4584 | 20.2893 | 20.4342 | 20.4524 | 19.9992 |  | 20.2536 | 19.686 | 20.1512 | 19.569 | 20.1153 | 20.3685 |  | 20.4609 |  |  | 20.1528 | 20.1486 | 20.5556 | [5 empty] | 21.96 | 20.2903 | 21.7044 | 22.0807 | 19.5294 | 21.2069 | 21.8282 | 19.4749 | 19.9654 | 21.2711 |  | 19.8038 | 21.0462 | 18.8886 | 19.8362 | 20.948 | 19.4507 | 20.1613 | 19.0518 | 20.237 | 19.1448 | 20.3569 | 18.9695 | 20.2166 | 21.1691 | 19.5272 | 19.8399 | 21.1114 | 18.9688 | 19.8189 | 20.9269 | 18.9661 | 20.3066 | 19.3379 | 19.9644 | 18.951 | 20.2125 | -0.29044 | 20.9474 | 0.047018 | 0.013017 | -27.0853 | 3.0976 | 0.69 | -0.49 | 0.90261 | -0.67351 | -8.0313 | 0.8738 | 0.61382 | -16.7109 | 4.1702 | 0.42725 | 0.43253 | 0.43457 | 0.35996 | 0.45698 | 0.4417 | 0.42981
42838.4148 | -476 | 22.8879 | 22.8629 | 22.849 | 22.7801 | 22.4153 | 21.7586 | 22.7158 | 21.8261 | 22.3783 | 22.3891 | 22.3781 | 22.0606 | 21.287 | 22.2563 | 21.5669 | 21.7491 | 21.8839 | 21.0726 | 21.1746 | 21.3928 | 20.4797 | 20.6276 | 20.9245 | 21.9023 | 21.6728 | 21.3026 | 20.4371 | 20.4058 | 20.4997 | 22.0299 | 21.6432 | 21.1686 | 21.9863 | 21.7191 | 21.3451 | 19.9274 | 20.5391 |  | 20.5772 | 20.203 | 20.2725 | 19.0973 |  | 16.833 | 16.8586 | 16.6023 | 16.857 | 16.9559 | 17.4845 | 17.9525 | 15.9585 | 16.7842 | 16.1501 | 16.909 | 17.8701 | 45.0784 | 48.3658 | 44.3633 | 21.3289 |  |  | 0.61201 | -0.34177 | -45.0619 | 0.45074 | 0.1815 | -197.8204 | 12.8929 | -0.41369 | -0.058481 | -0.20319 | -0.035818 | 8.8293 | 9.0589 | 1.9787 | 21.7901 | 22.0199 | 22.2128 | 22.2831 | 22.1117 | 21.449 | 20.2701 | 22.2096 | 22.3795 | 22.4228 | 22.3741 | 22.0132 | 21.2512 | 22.3006 | 17.4793 | 17.0836 | 16.2538 | 16.299 | 16.3935 | 17.0851 | 16.7692 | 22.3891 | 22.1595 | 21.7269 | 22.0961 | 21.818 | 21.3238 | 21.964 | 21.5479 | 20.9266 | 20.1184 | 20.4218 | 19.9477 | 19.7618 | -0.10772 | 0.06603 | 20.7639 | 22.1025 | 22.4032 | 20.1454 | 21.7022 | 22.1498 | 21.9668 | 21.7371 | 21.3044 | 21.8134 | 21.4747 | 21.0734 | 20.4481 | 20.2854 | 20.4306 | 20.4568 | 20.0141 |  | 20.2544 | 19.6578 | 20.1506 | 19.5917 | 20.1266 | 20.3724 |  | 20.4614 |  |  | 20.1396 | 20.1433 | 20.5378 | [5 empty] | 21.9562 | 20.2906 | 21.6939 | 22.0791 | 19.5271 | 21.2035 | 21.8346 | 19.4782 | 19.9698 | 21.2777 |  | 19.8085 | 21.0445 | 18.8967 | 19.8336 | 20.9419 | 19.4541 | 20.167 | 19.0502 | 20.2438 | 19.1455 | 20.3518 | 18.9705 | 20.2117 | 21.1539 | 19.523 | 19.8355 | 21.1 | 18.9678 | 19.81 | 20.9239 | 18.9659 | 20.3023 | 19.3347 | 19.9679 | 18.9564 | 20.2163 | -0.1387 | 20.9486 | 0.04732 | 0.014745 | -27.065 | 3.0976 | -10.45 | 0.15 | 0.93424 | -0.6938 | -7.9667 | 0.79677 | 0.50614 | -16.71 | 4.2659 | 0.42687 | 0.43329 | 0.43432 | 0.35852 | 0.45786 | 0.44138 | 0.42932
42838.4148 | -475 | 22.8865 | 22.856 | 22.8492 | 22.7767 | 22.4182 | 21.7526 | 22.72 | 21.8236 | 22.3766 | 22.3904 | 22.3731 | 22.0704 | 21.2836 | 22.2446 | 21.5668 | 21.7455 | 21.8778 | 21.0726 | 21.1599 | 21.3897 | 20.4801 | 20.6271 | 20.9174 | 21.8984 | 21.6658 | 21.3088 | 20.4309 | 20.3918 | 20.4933 | 22.0289 | 21.6432 | 21.1663 | 21.9887 | 21.7275 | 21.3479 | 19.9348 | 20.5488 |  | 20.5778 | 20.2057 | 20.2706 | 19.1213 |  | 16.8311 | 16.858 | 16.6178 | 16.8696 | 16.9584 | 17.4827 | 17.9243 | 15.9839 | 16.7873 | 16.2069 | 16.9116 | 17.8738 | 45.082 | 48.3684 | 44.3615 | 21.3344 |  |  | 0.53447 | -0.40222 | -44.8181 | 0.36203 | 0.0941 | -197.9091 | 12.9395 | -0.3138 | -0.01995 | -0.27515 | -0.000924 | 8.8296 | 9.0594 | 1.9785 | 21.7957 | 22.0199 | 22.2169 | 22.2851 | 22.1165 | 21.4538 | 20.2765 | 22.2185 | 22.387 | 22.4232 | 22.3779 | 22.0208 | 21.2546 | 22.3005 | 17.5021 | 17.0384 | 16.2575 | 16.2854 | 16.3803 | 17.0793 | 16.7674 | 22.3876 | 22.1536 | 21.7235 | 22.0942 | 21.822 | 21.3287 | 21.958 | 21.5474 | 20.9253 | 20.1256 | 20.4209 | 19.9464 | 19.7773 | -0.10379 | 0.11434 | 20.7599 | 22.1002 | 22.4036 | 20.1499 | 21.7034 | 22.1504 | 21.9688 | 21.7346 | 21.3032 | 21.8127 | 21.4763 | 21.0725 | 20.434 | 20.2699 | 20.4261 | 20.4527 | 20.0254 |  | 20.2472 | 19.6242 | 20.1499 | 19.6086 | 20.1167 | 20.3723 |  | 20.456 |  |  | 20.1466 | 20.165 | 20.5332 | [5 empty] | 21.9647 | 20.2879 | 21.7062 | 22.0854 | 19.5327 | 21.2099 | 21.8404 | 19.4822 | 19.9658 | 21.277 |  | 19.799 | 21.0479 | 18.8885 | 19.8376 | 20.9332 | 19.4481 | 20.1558 | 19.0557 | 20.242 | 19.1468 | 20.3553 | 18.9817 | 20.235 | 21.1705 | 19.53 | 19.8504 | 21.1084 | 18.9687 | 19.82 | 20.9323 | 18.9749 | 20.3042 | 19.3417 | 19.968 | 18.9584 | 20.2247 | -0.27152 | 20.9486 | 0.047406 | 0.015725 | -27.1436 | 3.0976 | -24.69 | -0.17 | 0.87305 | -0.75267 | -7.9451 | 0.71407 | 0.36445 | -16.7137 | 4.2736 | 0.42631 | 0.4342 | 0.43352 | 0.35532 | 0.45724 | 0.44096 | 0.42913
42838.4148 | -474 | 22.885 | 22.851 | 22.8418 | 22.7704 | 22.4159 | 21.7507 | 22.7216 | 21.8166 | 22.3713 | 22.3811 | 22.3724 | 22.0564 | 21.2835 | 22.2444 | 21.5687 | 21.7429 | 21.8774 | 21.0666 | 21.1655 | 21.387 | 20.47 | 20.6253 | 20.9137 | 21.895 | 21.6626 | 21.2942 | 20.4231 | 20.386 | 20.4684 | 22.0402 | 21.6522 | 21.1722 | 21.9981 | 21.7339 | 21.361 | 19.9428 | 20.5489 |  | 20.5856 | 20.2102 | 20.2788 | 19.1446 |  | 16.8343 | 16.8671 | 16.6226 | 16.8727 | 16.9684 | 17.4955 | 17.9197 | 15.9831 | 16.787 | 16.2052 | 16.9139 | 17.87 | 45.0852 | 48.3636 | 44.366 | 21.3354 |  |  | 0.67115 | -0.57833 | -44.615 | 0.48031 | 0.38257 | -197.8637 | 12.6149 | -0.31446 | -0.21552 | -0.29172 | -0.0094304 | 8.8286 | 9.0584 | 1.9785 | 21.7932 | 22.0188 | 22.2176 | 22.2803 | 22.112 | 21.4472 | 20.2698 | 22.2139 | 22.3856 | 22.416 | 22.3751 | 22.0154 | 21.254 | 22.2953 | 17.533 | 16.983 | 16.2241 | 16.2602 | 16.3425 | 17.081 | 16.7662 | 22.3886 | 22.1541 | 21.7277 | 22.0954 | 21.816 | 21.3286 | 21.9645 | 21.5472 | 20.9358 | 20.1276 | 20.4232 | 19.9522 | 19.7837 | -0.24692 | -0.088222 | 20.7453 | 22.0999 | 22.4077 | 20.1431 | 21.6986 | 22.1549 | 21.9672 | 21.7379 | 21.3053 | 21.809 | 21.4795 | 21.0739 | 20.4134 | 20.2544 | 20.4239 | 20.4559 | 20.0213 |  | 20.2426 | 19.5817 | 20.1388 | 19.6268 | 20.1021 | 20.3722 |  | 20.4524 |  |  | 20.1502 | 20.1652 | 20.5378 | [5 empty] | 21.9709 | 20.3006 | 21.7024 | 22.0854 | 19.5378 | 21.2154 | 21.8431 | 19.4913 | 19.9685 | 21.2838 |  | 19.8045 | 21.0646 | 18.9002 | 19.8403 | 20.9458 | 19.4656 | 20.1767 | 19.0673 | 20.2408 | 19.1542 | 20.3579 | 18.9726 | 20.2171 | 21.1758 | 19.5236 | 19.8457 | 21.1037 | 18.9633 | 19.8247 | 20.9286 | 18.9651 | 20.3005 | 19.3449 | 19.9643 | 18.9529 | 20.2285 | -0.38467 | 20.9488 | 0.0477 | 0.0164 | -27.0624 | 3.0976 | -17.85 | -0.09 | 0.97829 | -0.90254 | -7.9272 | 0.8225 | 0.73486 | -16.7121 | 4.2198 | 0.42627 | 0.43501 | 0.43252 | 0.35208 | 0.4608 | 0.44058 | 0.42902
42838.4148 | -473 | 22.8783 | 22.8598 | 22.8396 | 22.7753 | 22.4073 | 21.7534 | 22.7189 | 21.8186 | 22.37 | 22.3899 | 22.3694 | 22.0586 | 21.2791 | 22.2478 | 21.5731 | 21.7496 | 21.8863 | 21.0809 | 21.1749 | 21.3995 | 20.4779 | 20.625 | 20.9249 | 21.9051 | 21.6693 | 21.3028 | 20.419 | 20.3957 | 20.4698 | 22.0198 | 21.6404 | 21.1676 | 21.9872 | 21.7221 | 21.3476 | 19.9289 | 20.5312 |  | 20.5751 | 20.2023 | 20.2686 | 19.1468 |  | 16.8388 | 16.8645 | 16.6193 | 16.8733 | 16.9872 | 17.5254 | 17.915 | 15.966 | 16.7866 | 16.2211 | 16.9162 | 17.8719 | 45.0907 | 48.3615 | 44.3657 | 21.3368 |  |  | 0.69546 | -0.2386 | -43.8239 | 0.38765 | 0.13156 | -197.8131 | 13.3883 | -0.28818 | -0.39631 | -0.17633 | 0.045948 | 8.8294 | 9.059 | 1.9782 | 21.7853 | 22.0164 | 22.2113 | 22.2749 | 22.1145 | 21.4436 | 20.2654 | 22.2047 | 22.3843 | 22.4148 | 22.3648 | 22.0093 | 21.251 | 22.295 | 17.5474 | 16.9777 | 16.1665 | 16.2532 | 16.3074 | 17.0756 | 16.7686 | 22.3802 | 22.1523 | 21.7122 | 22.0911 | 21.8153 | 21.3221 | 21.9469 | 21.5414 | 20.922 | 20.1187 | 20.4177 | 19.9426 | 19.7772 | -0.22175 | -0.098112 | 20.7407 | 22.0961 | 22.4109 | 20.145 | 21.6956 | 22.1578 | 21.9672 | 21.7391 | 21.3086 | 21.8081 | 21.477 | 21.0755 | 20.3995 | 20.2539 | 20.4312 | 20.4535 | 20.0274 |  | 20.2489 | 19.5272 | 20.1471 | 19.6539 | 20.1107 | 20.3774 |  | 20.4545 |  |  | 20.1392 | 20.1681 | 20.5353 | [5 empty] | 21.9534 | 20.2979 | 21.7065 | 22.083 | 19.5336 | 21.202 | 21.8369 | 19.4979 | 19.9615 | 21.2837 |  | 19.7925 | 21.0634 | 18.8993 | 19.8471 | 20.9415 | 19.4526 | 20.1704 | 19.0558 | 20.2445 | 19.1446 | 20.3484 | 18.9635 | 20.2044 | 21.1616 | 19.5112 | 19.845 | 21.1111 | 18.9572 | 19.8206 | 20.9223 | 18.9572 | 20.2974 | 19.341 | 19.9642 | 18.9488 | 20.2256 | -0.29285 | 20.9485 | 0.047547 | 0.016437 | -27.0531 | 3.0976 | -10.04 | -0.37 | 0.99585 | -0.57971 | -7.8566 | 0.73892 | 0.43095 | -16.7109 | 4.3474 | 0.42631 | 0.4368 | 0.43206 | 0.34985 | 0.46747 | 0.44006 | 0.4289
42838.4148 | -472 | 22.8856 | 22.8525 | 22.8447 | 22.7715 | 22.4138 | 21.7572 | 22.7196 | 21.8228 | 22.3694 | 22.3906 | 22.3755 | 22.0583 | 21.2803 | 22.2544 | 21.5742 | 21.7405 | 21.8834 | 21.0794 | 21.1759 | 21.399 | 20.4703 | 20.6197 | 20.9193 | 21.9035 | 21.6727 | 21.3088 | 20.4166 | 20.3903 | 20.4578 | 22.0331 | 21.6507 | 21.1676 | 21.9872 | 21.7274 | 21.3515 | 19.9349 | 20.5343 |  | 20.5757 | 20.2039 | 20.2648 | 19.1535 |  | 16.8304 | 16.8668 | 16.6072 | 16.883 | 17.0169 | 17.545 | 17.8891 | 15.9894 | 16.7888 | 16.2434 | 16.9037 | 17.8765 | 45.0856 | 48.357 | 44.3643 | 21.3389 |  |  | 0.62777 | -0.36477 | -43.6688 | 0.55851 | 0.24326 | -197.8591 | 12.8134 | -0.37229 | -0.23284 | -0.12787 | 0.12424 | 8.8291 | 9.0588 | 1.9785 | 21.7861 | 22.0116 | 22.2044 | 22.2794 | 22.1155 | 21.4443 | 20.2684 | 22.2033 | 22.3834 | 22.418 | 22.3685 | 22.0117 | 21.2581 | 22.2863 | 17.543 | 16.9428 | 16.1262 | 16.2234 | 16.2879 | 17.0816 | 16.7656 | 22.3871 | 22.1575 | 21.7158 | 22.0859 | 21.8137 | 21.318 | 21.9536 | 21.5424 | 20.9303 | 20.1222 | 20.4167 | 19.9553 | 19.782 | -0.041667 | -0.112 | 20.743 | 22.0949 | 22.4098 | 20.149 | 21.6951 | 22.1523 | 21.9631 | 21.7395 | 21.3039 | 21.8125 | 21.4721 | 21.0719 | 20.3837 | 20.2511 | 20.4372 | 20.4493 | 20.036 |  | 20.244 | 19.4782 | 20.146 | 19.6674 | 20.1157 | 20.3729 |  | 20.4562 |  |  | 20.1482 | 20.1799 | 20.5278 | [5 empty] | 21.9552 | 20.291 | 21.6961 | 22.0846 | 19.5351 | 21.2065 | 21.8339 | 19.501 | 19.9742 | 21.2901 |  | 19.7839 | 21.0561 | 18.8993 | 19.8461 | 20.9381 | 19.4548 | 20.1657 | 19.0437 | 20.2438 | 19.1377 | 20.3441 | 18.9667 | 20.2076 | 21.1619 | 19.519 | 19.8487 | 21.1105 | 18.9599 | 19.8234 | 20.925 | 18.951 | 20.301 | 19.3447 | 19.9602 | 18.9549 | 20.2249 | -0.37744 | 20.9482 | 0.04783 | 0.014934 | -26.9422 | 3.0976 | -0.28 | -0.03 | 0.94613 | -0.71678 | -7.8427 | 0.88694 | 0.58604 | -16.7134 | 4.2532 | 0.42591 | 0.43812 | 0.43185 | 0.35105 | 0.47161 | 0.44007 | 0.42888
42838.4148 | -471 | 22.8869 | 22.8498 | 22.8407 | 22.7715 | 22.406 | 21.7585 | 22.7192 | 21.8145 | 22.3727 | 22.3919 | 22.3719 | 22.0553 | 21.2769 | 22.2549 | 21.5686 | 21.7406 | 21.8851 | 21.0744 | 21.1808 | 21.3992 | 20.4782 | 20.6296 | 20.9256 | 21.8995 | 21.6667 | 21.3062 | 20.4193 | 20.3914 | 20.4458 | 22.0313 | 21.648 | 21.1715 | 21.9832 | 21.7323 | 21.3526 | 19.9333 | 20.5453 |  | 20.5783 | 20.2013 | 20.2676 | 19.1647 |  | 16.8347 | 16.8626 | 16.6158 | 16.899 | 17.0116 | 17.5539 | 17.8971 | 16.0164 | 16.7902 | 16.2598 | 16.9099 | 17.8765 | 45.0694 | 48.3448 | 44.3587 | 21.3412 |  |  | 0.64552 | -0.44493 | -43.9724 | 0.38371 | 0.080956 | -197.8138 | 12.9698 | -0.35323 | -0.067433 | -0.13962 | 0.026505 | 8.8283 | 9.0581 | 1.9793 | 21.7843 | 22.027 | 22.2104 | 22.2795 | 22.1068 | 21.4487 | 20.2692 | 22.2073 | 22.3827 | 22.4173 | 22.3758 | 22.0073 | 21.2551 | 22.3019 | 17.5263 | 16.9368 | 16.1161 | 16.2048 | 16.2772 | 17.0786 | 16.7672 | 22.3846 | 22.1592 | 21.7218 | 22.0877 | 21.8117 | 21.3174 | 21.9545 | 21.5411 | 20.927 | 20.1224 | 20.4179 | 19.9465 | 19.7912 | -0.022793 | -0.22155 | 20.7304 | 22.0955 | 22.3986 | 20.1453 | 21.6955 | 22.1466 | 21.9597 | 21.7342 | 21.3013 | 21.8003 | 21.4697 | 21.0695 | 20.363 | 20.2298 | 20.4318 | 20.4459 | 20.0516 |  | 20.2506 | 19.4434 | 20.1468 | 19.6779 | 20.1153 | 20.3781 |  | 20.4526 |  |  | 20.1645 | 20.194 | 20.5308 | [5 empty] | 21.966 | 20.2985 | 21.7022 | 22.0886 | 19.5491 | 21.2094 | 21.8454 | 19.5004 | 19.9759 | 21.2807 |  | 19.7734 | 21.0544 | 18.9037 | 19.8475 | 20.9309 | 19.4542 | 20.1775 | 19.0381 | 20.2442 | 19.1409 | 20.3465 | 18.97 | 20.2063 | 21.1689 | 19.5176 | 19.8503 | 21.104 | 18.9616 | 19.8259 | 20.9264 | 18.9578 | 20.2945 | 19.3428 | 19.9694 | 18.9581 | 20.2355 | -0.2372 | 20.9476 | 0.048456 | 0.014905 | -27.0122 | 3.0976 | -1.69 | -0.07 | 0.95939 | -0.79163 | -7.8698 | 0.73515 | 0.33808 | -16.7117 | 4.2792 | 0.4257 | 0.43912 | 0.43155 | 0.35255 | 0.47292 | 0.43971 | 0.42864
42838.4148 | -470 | 22.8918 | 22.8493 | 22.8439 | 22.7739 | 22.4094 | 21.7542 | 22.7182 | 21.82 | 22.3767 | 22.3913 | 22.3733 | 22.056 | 21.279 | 22.2529 | 21.5689 | 21.7412 | 21.8864 | 21.0812 | 21.1766 | 21.4012 | 20.4826 | 20.6244 | 20.929 | 21.9073 | 21.6714 | 21.3076 | 20.4156 | 20.3937 | 20.4367 | 22.0285 | 21.6443 | 21.1729 | 21.9841 | 21.7345 | 21.3465 | 19.9323 | 20.5323 |  | 20.581 | 20.2085 | 20.2724 | 19.1743 |  | 16.8358 | 16.8641 | 16.6243 | 16.9043 | 17.0068 | 17.555 | 17.8953 | 16.0254 | 16.7878 | 16.2586 | 16.9115 | 17.8774 | 45.0571 | 48.3314 | 44.3628 | 21.3398 |  |  | 0.67443 | -0.20377 | -44.9436 | 0.24177 | 0.054672 | -197.8637 | 12.8107 | -0.62265 | -0.084752 | 0.08571 | 0.073377 | 8.8287 | 9.0584 | 1.9789 | 21.7795 | 22.0126 | 22.2082 | 22.2695 | 22.108 | 21.4387 | 20.2635 | 22.206 | 22.3808 | 22.4133 | 22.3657 | 22.0071 | 21.2383 | 22.2885 | 17.5119 | 16.9495 | 16.107 | 16.1904 | 16.2538 | 17.0756 | 16.7647 | 22.3791 | 22.1538 | 21.7135 | 22.0915 | 21.8123 | 21.3231 | 21.95 | 21.5459 | 20.924 | 20.1199 | 20.4139 | 19.9508 | 19.7895 | -0.045599 | -0.14775 | 20.7246 | 22.0973 | 22.4037 | 20.1474 | 21.6976 | 22.1466 | 21.9654 | 21.738 | 21.3021 | 21.8005 | 21.4615 | 21.0747 | 20.3509 | 20.2101 | 20.4328 | 20.4532 | 20.0531 |  | 20.249 | 19.4114 | 20.1466 | 19.668 | 20.1106 | 20.3733 |  | 20.4504 |  |  | 20.1836 | 20.2157 | 20.5448 | [5 empty] | 21.973 | 20.3093 | 21.7089 | 22.0923 | 19.5559 | 21.2192 | 21.8413 | 19.4972 | 19.9888 | 21.2838 |  | 19.7665 | 21.0533 | 18.9035 | 19.839 | 20.9167 | 19.4481 | 20.1787 | 19.0307 | 20.2416 | 19.1362 | 20.3337 | 18.9681 | 20.1968 | 21.1715 | 19.5113 | 19.8455 | 21.1082 | 18.9631 | 19.8237 | 20.9236 | 18.9394 | 20.2912 | 19.3323 | 19.956 | 18.9648 | 20.225 | -0.17061 | 20.9476 | 0.048837 | 0.01476 | -27.0148 | 3.0976 | -12.54 | -0.1 | 0.98063 | -0.53573 | -7.9563 | 0.58355 | 0.27783 | -16.7138 | 4.2529 | 0.4256 | 0.44 | 0.43166 | 0.3538 | 0.47363 | 0.43941 | 0.4286
42838.4148 | -469 | 22.8903 | 22.8536 | 22.8444 | 22.7704 | 22.4159 | 21.7614 | 22.7144 | 21.8242 | 22.3719 | 22.3959 | 22.3763 | 22.0652 | 21.2827 | 22.2522 | 21.5616 | 21.7395 | 21.8826 | 21.0726 | 21.1662 | 21.3921 | 20.4754 | 20.6209 | 20.9208 | 21.8981 | 21.6658 | 21.3029 | 20.4018 | 20.3873 | 20.4128 | 22.0326 | 21.6525 | 21.171 | 21.9843 | 21.7371 | 21.3566 | 19.9379 | 20.5335 |  | 20.5752 | 20.21 | 20.2737 | 19.189 |  | 16.8367 | 16.8704 | 16.6175 | 16.8886 | 16.9972 | 17.5821 | 17.9162 | 16.0368 | 16.7886 | 16.2335 | 16.9022 | 17.8702 | 45.0403 | 48.3104 | 44.3576 | 21.3423 |  |  | 0.62055 | -0.40945 | -44.5059 | 0.39488 | 0.2045 | -197.8414 | 12.8863 | -0.45048 | -0.11803 | -0.021498 | 0.048899 | 8.83 | 9.0596 | 1.9784 | 21.7824 | 22.0163 | 22.2178 | 22.2809 | 22.1108 | 21.4507 | 20.2673 | 22.2099 | 22.3878 | 22.4212 | 22.3692 | 22.0163 | 21.2562 | 22.2965 | 17.4933 | 16.9535 | 16.1036 | 16.1577 | 16.2334 | 17.0727 | 16.7585 | 22.3755 | 22.1489 | 21.7106 | 22.0888 | 21.8085 | 21.3164 | 21.9454 | 21.5378 | 20.9137 | 20.1235 | 20.4073 | 19.9497 | 19.7981 | -0.08256 | -0.22669 | 20.7195 | 22.0979 | 22.4074 | 20.1479 | 21.6993 | 22.1484 | 21.9659 | 21.7343 | 21.3047 | 21.8042 | 21.4707 | 21.068 | 20.3369 | 20.2023 | 20.4367 | 20.4578 | 20.065 |  | 20.2497 | 19.3803 | 20.1419 | 19.6639 | 20.1115 | 20.3827 |  | 20.4522 |  |  | 20.183 | 20.2217 | 20.5508 | [5 empty] | 21.9697 | 20.3099 | 21.7092 | 22.0893 | 19.557 | 21.2162 | 21.8439 | 19.5094 | 19.9974 | 21.2843 |  | 19.764 | 21.0556 | 18.912 | 19.8342 | 20.9269 | 19.4561 | 20.1748 | 19.0312 | 20.2408 | 19.1304 | 20.3376 | 18.9708 | 20.2074 | 21.1767 | 19.5199 | 19.8594 | 21.108 | 18.9722 | 19.8382 | 20.9318 | 18.9377 | 20.2934 | 19.3294 | 19.9688 | 18.9713 | 20.2303 | -0.2103 | 20.9485 | 0.048204 | 0.014549 | -27.1327 | 3.0976 | 0.27 | 0.36 | 0.9406 | -0.75942 | -7.9175 | 0.74579 | 0.53735 | -16.7137 | 4.2656 | 0.4253 | 0.4407 | 0.43181 | 0.35553 | 0.47329 | 0.43919 | 0.42848
42838.4149 | -468 | 22.8773 | 22.8507 | 22.8349 | 22.7562 | 22.398 | 21.7536 | 22.7122 | 21.8166 | 22.3637 | 22.3712 | 22.3632 | 22.0491 | 21.2781 | 22.2473 | 21.5633 | 21.7411 | 21.8812 | 21.0645 | 21.1643 | 21.3905 | 20.4721 | 20.6236 | 20.915 | 21.8925 | 21.6665 | 21.3013 | 20.3989 | 20.3877 | 20.3938 | 22.0197 | 21.6381 | 21.1579 | 21.9846 | 21.7146 | 21.352 | 19.9281 | 20.5226 |  | 20.5709 | 20.2004 | 20.2752 | 19.1933 |  | 16.8321 | 16.8625 | 16.6137 | 16.8878 | 16.9889 | 17.602 | 17.9335 | 16.0502 | 16.7759 | 16.2114 | 16.9022 | 17.869 | 45.0363 | 48.2931 | 44.3463 | 21.3413 |  |  | 0.66589 | -0.27408 | -44.1629 | 0.58742 | 0.26955 | -197.8473 | 12.7825 | -0.46823 | -0.096234 | 0.0068248 | -0.099876 | 8.8285 | 9.058 | 1.9783 | 21.7857 | 22.0216 | 22.2181 | 22.2841 | 22.1204 | 21.45 | 20.2719 | 22.2145 | 22.3882 | 22.4269 | 22.3717 | 22.0162 | 21.2583 | 22.3052 | 17.4937 | 16.9806 | 16.1383 | 16.1528 | 16.2369 | 17.0694 | 16.7684 | 22.388 | 22.1509 | 21.718 | 22.0946 | 21.8099 | 21.3267 | 21.9617 | 21.5433 | 20.9343 | 20.1286 | 20.4149 | 19.9593 | 19.808 | -0.1266 | -0.25103 | 20.7355 | 22.1068 | 22.4147 | 20.1547 | 21.7138 | 22.1604 | 21.9743 | 21.7397 | 21.3157 | 21.8144 | 21.4835 | 21.0818 | 20.3372 | 20.2114 | 20.4472 | 20.4632 | 20.0646 |  | 20.2471 | 19.3607 | 20.1496 | 19.6744 | 20.1176 | 20.3829 |  | 20.4535 |  |  | 20.1928 | 20.2315 | 20.5537 | [5 empty] | 21.9618 | 20.307 | 21.7044 | 22.0833 | 19.5518 | 21.2079 | 21.8337 | 19.5183 | 20 | 21.2895 |  | 19.7673 | 21.0576 | 18.9121 | 19.8359 | 20.9354 | 19.4638 | 20.1698 | 19.0282 | 20.2408 | 19.1299 | 20.3369 | 18.9755 | 20.2122 | 21.1874 | 19.5294 | 19.8632 | 21.1136 | 18.9785 | 19.8474 | 20.9354 | 18.9303 | 20.2964 | 19.3401 | 19.9687 | 18.9764 | 20.2393 | -0.044652 | 20.9468 | 0.048475 | 0.0155 | -27.0536 | 3.0976 | -5.03 | -0.22 | 0.97433 | -0.62132 | -7.8869 | 0.9096 | 0.61694 | -16.7145 | 4.2485 | 0.42522 | 0.44151 | 0.43172 | 0.35509 | 0.47059 | 0.43874 | 0.42838
42838.4149 | -467 | 22.887 | 22.8559 | 22.8457 | 22.7702 | 22.4195 | 21.7597 | 22.7174 | 21.8264 | 22.3837 | 22.3913 | 22.3742 | 22.0556 | 21.2859 | 22.2448 | 21.567 | 21.7403 | 21.879 | 21.0628 | 21.1693 | 21.3891 | 20.4734 | 20.6267 | 20.9215 | 21.8959 | 21.6647 | 21.3032 | 20.3908 | 20.391 | 20.3906 | 22.0266 | 21.6554 | 21.1726 | 21.9845 | 21.7257 | 21.3493 | 19.9337 | 20.5267 |  | 20.5675 | 20.2118 | 20.2698 | 19.2123 |  | 16.8382 | 16.8611 | 16.613 | 16.8926 | 17.0028 | 17.6385 | 17.9868 | 16.0559 | 16.7823 | 16.1913 | 16.9124 | 17.8732 | 45.0348 | 48.2795 | 44.3368 | 21.3385 |  |  | 0.61529 | -0.19917 | -44.0473 | 0.42905 | 0.22552 | -197.8052 | 13.0539 | -0.484 | 0.13378 | 0.073331 | -0.090154 | 8.8295 | 9.059 | 1.9782 | 21.7855 | 22.0233 | 22.2175 | 22.2821 | 22.1172 | 21.4507 | 20.2762 | 22.2106 | 22.382 | 22.4199 | 22.3709 | 22.016 | 21.2542 | 22.3012 | 17.4804 | 16.9769 | 16.1495 | 16.1711 | 16.2494 | 17.0743 | 16.7697 | 22.382 | 22.1521 | 21.7163 | 22.0897 | 21.8052 | 21.322 | 21.9492 | 21.5391 | 20.9235 | 20.1186 | 20.4172 | 19.9542 | 19.7961 | -0.085705 | -0.20539 | 20.7253 | 22.105 | 22.4077 | 20.1461 | 21.7077 | 22.1555 | 21.975 | 21.7393 | 21.3118 | 21.8065 | 21.4819 | 21.0811 | 20.3225 | 20.1948 | 20.4416 | 20.4636 | 20.0709 |  | 20.2456 | 19.3511 | 20.1418 | 19.6709 | 20.1116 | 20.3807 |  | 20.4475 |  |  | 20.2091 | 20.2347 | 20.5632 | [5 empty] | 21.9597 | 20.3131 | 21.6991 | 22.0865 | 19.5531 | 21.2071 | 21.8305 | 19.5208 | 19.9979 | 21.289 |  | 19.7717 | 21.0586 | 18.9137 | 19.8352 | 20.9314 | 19.4633 | 20.1591 | 19.022 | 20.2323 | 19.13 | 20.3281 | 18.9752 | 20.1956 | 21.1832 | 19.5261 | 19.8562 | 21.1154 | 18.9782 | 19.8435 | 20.9315 | 18.9236 | 20.2876 | 19.3405 | 19.9601 | 18.971 | 20.2399 | -0.10568 | 20.9478 | 0.048419 | 0.015195 | -26.9891 | 3.0976 | -16.51 | 0.04 | 0.93657 | -0.52965 | -7.8765 | 0.77737 | 0.56435 | -16.7138 | 4.2936 | 0.425 | 0.44151 | 0.43162 | 0.35715 | 0.4695 | 0.4384 | 0.42838
42838.4149 | -466 | 22.8833 | 22.8595 | 22.8402 | 22.7808 | 22.4161 | 21.7492 | 22.7092 | 21.8286 | 22.3755 | 22.3835 | 22.3731 | 22.0531 | 21.2723 | 22.2441 | 21.5736 | 21.7448 | 21.8883 | 21.0771 | 21.1702 | 21.3948 | 20.48 | 20.628 | 20.9271 | 21.903 | 21.6679 | 21.3133 | 20.3893 | 20.394 | 20.3956 | 22.0326 | 21.6498 | 21.1742 | 21.9952 | 21.7354 | 21.3597 | 19.9386 | 20.527 |  | 20.5794 | 20.2066 | 20.2777 | 19.2264 |  | 16.8437 | 16.8622 | 16.6136 | 16.8956 | 17.0258 | 17.6672 | 17.999 | 16.0554 | 16.7778 | 16.1797 | 16.9131 | 17.8714 | 45.035 | 48.2772 | 44.3393 | 21.3404 |  |  | 0.60675 | -0.24451 | -44.5342 | 0.23323 | 0.21041 | -197.8887 | 12.8528 | -0.3782 | -0.051476 | -0.044996 | 0.021991 | 8.829 | 9.059 | 1.9792 | 21.7854 | 22.0165 | 22.2137 | 22.2729 | 22.1172 | 21.4435 | 20.2677 | 22.2056 | 22.384 | 22.4121 | 22.3707 | 22.0136 | 21.2507 | 22.2939 | 17.4726 | 16.9595 | 16.1439 | 16.169 | 16.2487 | 17.0783 | 16.7708 | 22.3847 | 22.151 | 21.7157 | 22.0877 | 21.8096 | 21.3224 | 21.9488 | 21.5391 | 20.9246 | 20.1124 | 20.4113 | 19.9493 | 19.8026 | 0.039922 | -0.1915 | 20.7195 | 22.098 | 22.405 | 20.142 | 21.7054 | 22.1553 | 21.9688 | 21.738 | 21.3038 | 21.801 | 21.4728 | 21.0709 | 20.304 | 20.1801 | 20.4395 | 20.4569 | 20.0766 |  | 20.2391 | 19.343 | 20.1358 | 19.6695 | 20.1027 | 20.3784 |  | 20.4472 |  |  | 20.2259 | 20.2402 | 20.5787 | [5 empty] | 21.9711 | 20.3199 | 21.6998 | 22.0896 | 19.566 | 21.214 | 21.837 | 19.5261 | 19.9976 | 21.2869 |  | 19.7658 | 21.0522 | 18.9164 | 19.8278 | 20.9234 | 19.455 | 20.1473 | 19.0204 | 20.2198 | 19.1245 | 20.3205 | 18.9761 | 20.1821 | 21.1727 | 19.5264 | 19.8561 | 21.1088 | 18.9769 | 19.8421 | 20.9221 | 18.917 | 20.2793 | 19.3254 | 19.9518 | 18.9709 | 20.2328 | -0.29601 | 20.9473 | 0.048659 | 0.015348 | -27.058 | 3.0976 | -0.44 | -0.08 | 0.93006 | -0.58685 | -7.9199 | 0.57315 | 0.54514 | -16.7181 | 4.2606 | 0.42462 | 0.44154 | 0.43136 | 0.35848 | 0.47024 | 0.43817 | 0.42798
42838.4149 | -465 | 22.8757 | 22.8546 | 22.8375 | 22.7709 | 22.4082 | 21.7525 | 22.7143 | 21.819 | 22.3608 | 22.3817 | 22.3751 | 22.0507 | 21.2688 | 22.2411 | 21.5721 | 21.7442 | 21.8859 | 21.075 | 21.1722 | 21.3893 | 20.475 | 20.6255 | 20.9248 | 21.8971 | 21.6668 | 21.3112 | 20.3857 | 20.4055 | 20.3911 | 22.0352 | 21.646 | 21.1737 | 21.9872 | 21.7299 | 21.3511 | 19.9292 | 20.5194 |  | 20.5739 | 20.2049 | 20.2682 | 19.2299 |  | 16.8336 | 16.853 | 16.5973 | 16.9002 | 17.0542 | 17.6642 | 17.9684 | 16.0526 | 16.7673 | 16.1662 | 16.8976 | 17.8781 | 45.0189 | 48.2722 | 44.3319 | 21.3457 |  |  | 0.69283 | -0.17354 | -44.6492 | 0.28843 | 0.097384 | -197.8414 | 12.7306 | -0.43472 | -0.38736 | -0.27158 | -0.0094304 | 8.8292 | 9.0591 | 1.979 | 21.7792 | 22.0111 | 22.2069 | 22.2773 | 22.1173 | 21.4473 | 20.2688 | 22.2093 | 22.3813 | 22.4186 | 22.3716 | 22.0116 | 21.2519 | 22.2892 | 17.4502 | 16.969 | 16.137 | 16.169 | 16.2541 | 17.0746 | 16.7641 | 22.3857 | 22.155 | 21.7224 | 22.0971 | 21.8103 | 21.3262 | 21.9603 | 21.5472 | 20.9243 | 20.1283 | 20.4178 | 19.9632 | 19.8116 | -0.007262 | -0.11694 | 20.7211 | 22.1008 | 22.4054 | 20.1428 | 21.7009 | 22.1558 | 21.9604 | 21.7358 | 21.3041 | 21.802 | 21.4771 | 21.0669 | 20.2925 | 20.1655 | 20.4334 | 20.4535 | 20.1017 |  | 20.2529 | 19.3527 | 20.148 | 19.6595 | 20.1123 | 20.3789 |  | 20.4668 |  |  | 20.2327 | 20.248 | 20.5835 | [5 empty] | 21.9705 | 20.3148 | 21.702 | 22.0877 | 19.5704 | 21.2089 | 21.8409 | 19.5286 | 20.0092 | 21.2784 |  | 19.7603 | 21.0552 | 18.9173 | 19.8159 | 20.9196 | 19.4517 | 20.1395 | 19.0159 | 20.2103 | 19.1205 | 20.3137 | 18.9817 | 20.1855 | 21.1726 | 19.5251 | 19.8651 | 21.1049 | 18.9846 | 19.8402 | 20.9274 | 18.9174 | 20.2733 | 19.3262 | 19.9527 | 18.9737 | 20.2393 | -0.094181 | 20.944 | 0.048235 | 0.014818 | -27.049 | 3.0976 | -4.73 | -0.24 | 0.99384 | -0.4944 | -7.93 | 0.63737 | 0.37087 | -16.716 | 4.2403 | 0.42439 | 0.44168 | 0.43196 | 0.36054 | 0.47023 | 0.43776 | 0.42827
42838.4149 | -464 | 22.8805 | 22.8538 | 22.8375 | 22.7713 | 22.4049 | 21.7485 | 22.7183 | 21.8167 | 22.3644 | 22.3827 | 22.3708 | 22.0474 | 21.2746 | 22.2444 | 21.5661 | 21.7321 | 21.8779 | 21.0641 | 21.1686 | 21.383 | 20.4673 | 20.6203 | 20.9145 | 21.8897 | 21.6614 | 21.2985 | 20.3791 | 20.3939 | 20.3689 | 22.0322 | 21.6424 | 21.1723 | 21.9863 | 21.7279 | 21.3552 | 19.9315 | 20.5255 |  | 20.5682 | 20.1994 | 20.2777 | 19.2566 |  | 16.8344 | 16.8554 | 16.6029 | 16.9134 | 17.0596 | 17.662 | 17.9971 | 16.0595 | 16.7836 | 16.1445 | 16.9173 | 17.8738 | 45.01 | 48.2536 | 44.3286 | 21.3452 |  |  | 0.68757 | -0.5527 | -44.6058 | 0.01967 | 0.19924 | -197.8217 | 13.1229 | -0.35718 | -0.53798 | -0.23906 | -0.11185 | 8.8294 | 9.059 | 1.9788 | 21.786 | 21.9979 | 22.2142 | 22.2754 | 22.11 | 21.4526 | 20.2651 | 22.2147 | 22.3869 | 22.4199 | 22.3677 | 22.0074 | 21.2564 | 22.2946 | 17.4191 | 16.9963 | 16.1398 | 16.1707 | 16.2402 | 17.0668 | 16.7602 | 22.3869 | 22.155 | 21.7224 | 22.0956 | 21.8129 | 21.3208 | 21.9566 | 21.5358 | 20.9282 | 20.1254 | 20.4115 | 19.9697 | 19.8182 | 0.09379 | -0.14148 | 20.7345 | 22.1086 | 22.4079 | 20.1489 | 21.7029 | 22.1492 | 21.9723 | 21.7346 | 21.3058 | 21.8108 | 21.4785 | 21.0688 | 20.2847 | 20.165 | 20.4418 | 20.462 | 20.1062 |  | 20.2505 | 19.36 | 20.1445 | 19.6508 | 20.1162 | 20.3812 |  | 20.4645 |  |  | 20.2491 | 20.2577 | 20.5907 | [5 empty] | 21.9697 | 20.3249 | 21.6984 | 22.0851 | 19.5709 | 21.2116 | 21.8363 | 19.5271 | 20.0219 | 21.2748 |  | 19.7637 | 21.0525 | 18.9196 | 19.8186 | 20.9245 | 19.4533 | 20.1338 | 19.0128 | 20.2079 | 19.1193 | 20.2995 | 18.9809 | 20.1831 | 21.1738 | 19.5198 | 19.8628 | 21.0968 | 18.9891 | 19.8504 | 20.9271 | 18.9175 | 20.2677 | 19.3301 | 19.9437 | 18.975 | 20.2435 | -0.04391 | 20.9468 | 0.048653 | 0.015014 | -27.0395 | 3.0976 | -5.44 | -0.2 | 0.99002 | -0.8823 | -7.9262 | 0.16645 | 0.53047 | -16.7151 | 4.3051 | 0.42418 | 0.44136 | 0.43233 | 0.36308 | 0.46947 | 0.43709 | 0.42799
42838.4149 | -463 | 22.8888 | 22.8592 | 22.8464 | 22.777 | 22.4156 | 21.7576 | 22.7248 | 21.8223 | 22.3787 | 22.3896 | 22.3794 | 22.0557 | 21.2816 | 22.2505 | 21.5682 | 21.7428 | 21.8815 | 21.0715 | 21.1758 | 21.3975 | 20.4821 | 20.6289 | 20.9219 | 21.8984 | 21.6644 | 21.301 | 20.3861 | 20.4069 | 20.3669 | 22.0362 | 21.6442 | 21.1801 | 21.9893 | 21.7297 | 21.3518 | 19.9309 | 20.5252 |  | 20.5744 | 20.1949 | 20.2883 | 19.2797 |  | 16.8333 | 16.8483 | 16.6013 | 16.9158 | 17.0713 | 17.6567 | 18.0043 | 16.0725 | 16.7755 | 16.1095 | 16.9179 | 17.8763 | 45.0141 | 48.2448 | 44.3131 | 21.3465 |  |  | 0.37873 | -0.54218 | -44.2392 | 0.005214 | 0.0941 | -197.8434 | 12.8948 | -0.41697 | -0.42589 | -0.30137 | -0.0089096 | 8.829 | 9.0589 | 1.9785 | 21.7848 | 22.0151 | 22.2079 | 22.279 | 22.1183 | 21.457 | 20.2678 | 22.2128 | 22.383 | 22.4198 | 22.3747 | 22.0096 | 21.2573 | 22.2955 | 17.4 | 16.9995 | 16.1566 | 16.1822 | 16.236 | 17.0706 | 16.7629 | 22.3847 | 22.1628 | 21.7271 | 22.0892 | 21.8189 | 21.3248 | 21.959 | 21.5456 | 20.9305 | 20.1279 | 20.4217 | 19.9647 | 19.8141 | 0.027733 | -0.14833 | 20.734 | 22.1082 | 22.405 | 20.1497 | 21.7023 | 22.1556 | 21.974 | 21.7352 | 21.3104 | 21.8034 | 21.4795 | 21.0695 | 20.2773 | 20.1618 | 20.4328 | 20.4565 | 20.1133 |  | 20.246 | 19.3528 | 20.1345 | 19.6502 | 20.1107 | 20.378 |  | 20.4567 |  |  | 20.2543 | 20.2719 | 20.5984 | [5 empty] | 21.9646 | 20.3318 | 21.6978 | 22.0865 | 19.5625 | 21.2092 | 21.8359 | 19.5271 | 20.0275 | 21.2756 |  | 19.7702 | 21.0584 | 18.9204 | 19.824 | 20.9252 | 19.4659 | 20.1371 | 19.0191 | 20.2038 | 19.131 | 20.3101 | 18.9859 | 20.1802 | 21.1845 | 19.5315 | 19.8528 | 21.1048 | 18.9986 | 19.8609 | 20.9321 | 18.923 | 20.2724 | 19.3366 | 19.949 | 18.976 | 20.2456 | -0.11496 | 20.9459 | 0.048542 | 0.015471 | -26.9814 | 3.0976 | -16.1 | -0.08 | 0.73476 | -0.87385 | -7.8935 | 0.085694 | 0.36456 | -16.7159 | 4.2675 | 0.42383 | 0.44122 | 0.43216 | 0.36564 | 0.4679 | 0.43643 | 0.42819
42838.4149 | -462 | 22.8902 | 22.8516 | 22.8438 | 22.7736 | 22.4133 | 21.7602 | 22.7168 | 21.8244 | 22.3722 | 22.3914 | 22.3708 | 22.0541 | 21.2813 | 22.2483 | 21.5665 | 21.7529 | 21.8928 | 21.0776 | 21.1698 | 21.3893 | 20.4872 | 20.6372 | 20.9287 | 21.91 | 21.6778 | 21.3135 | 20.3857 | 20.4093 | 20.3691 | 22.0365 | 21.64 | 21.1835 | 21.992 | 21.7322 | 21.3513 | 19.937 | 20.5271 |  | 20.5756 | 20.1999 | 20.282 | 19.302 |  | 16.8317 | 16.8499 | 16.6099 | 16.9092 | 17.1031 | 17.6831 | 18.0392 | 16.0905 | 16.7831 | 16.1085 | 16.9252 | 17.8735 | 45.0027 | 48.2285 | 44.3051 | 21.3448 |  |  | 0.58046 | -0.46464 | -43.722 | 0.044638 | 0.15258 | -197.848 | 12.973 | -0.51882 | -0.29064 | -0.12367 | 0.10202 | 8.8294 | 9.0593 | 1.9781 | 21.7808 | 22.0095 | 22.2023 | 22.268 | 22.1045 | 21.4347 | 20.2612 | 22.2022 | 22.3736 | 22.4118 | 22.36 | 22.0027 | 21.247 | 22.2894 | 17.3671 | 17.0352 | 16.1695 | 16.1951 | 16.2392 | 17.0651 | 16.7641 | 22.3833 | 22.154 | 21.7174 | 22.0892 | 21.8118 | 21.3198 | 21.9573 | 21.5436 | 20.925 | 20.1217 | 20.4141 | 19.9587 | 19.8087 | -0.06113 | -0.095069 | 20.7263 | 22.0981 | 22.4031 | 20.1387 | 21.6961 | 22.1499 | 21.9632 | 21.7277 | 21.3032 | 21.7995 | 21.4692 | 21.0665 | 20.2523 | 20.1634 | 20.4283 | 20.444 | 20.1261 |  | 20.2457 | 19.3649 | 20.1433 | 19.6579 | 20.1095 | 20.3816 |  | 20.4575 |  |  | 20.2541 | 20.2675 | 20.6048 | [5 empty] | 21.9601 | 20.3236 | 21.7014 | 22.0876 | 19.565 | 21.2007 | 21.8339 | 19.5248 | 20.0253 | 21.2808 |  | 19.7735 | 21.0539 | 18.9145 | 19.819 | 20.9196 | 19.4534 | 20.1185 | 19.0169 | 20.2047 | 19.1105 | 20.3013 | 18.9794 | 20.1789 | 21.1812 | 19.5279 | 19.8577 | 21.0997 | 18.9917 | 19.8573 | 20.9299 | 18.9165 | 20.2632 | 19.3235 | 19.9391 | 18.9689 | 20.247 | -0.11978 | 20.9455 | 0.048856 | 0.014811 | -26.9588 | 3.0976 | 8.23 | -0.14 | 0.90965 | -0.80896 | -7.8472 | 0.25074 | 0.46424 | -16.7169 | 4.2807 | 0.42346 | 0.44118 | 0.43191 | 0.36867 | 0.46662 | 0.43602 | 0.42813
42838.4149 | -461 | 22.8917 | 22.8531 | 22.8371 | 22.7681 | 22.4126 | 21.7594 | 22.7134 | 21.8259 | 22.3715 | 22.3879 | 22.3728 | 22.0623 | 21.2772 | 22.2473 | 21.5627 | 21.7452 | 21.8757 | 21.0667 | 21.1537 | 21.3849 | 20.4683 | 20.6147 | 20.9129 | 21.8907 | 21.6608 | 21.3054 | 20.3696 | 20.3971 | 20.345 | 22.0465 | 21.6494 | 21.1814 | 21.9978 | 21.7344 | 21.3594 | 19.9437 | 20.5274 |  | 20.5782 | 20.2066 | 20.2825 | 19.3227 |  | 16.8301 | 16.8472 | 16.6023 | 16.9267 | 17.1204 | 17.7033 | 18.0542 | 16.0652 | 16.7807 | 16.1697 | 16.917 | 17.8726 | 44.9962 | 48.218 | 44.3007 | 21.3506 |  |  | 0.55681 | -0.42785 | -43.7102 | 0.27792 | 0.17164 | -197.8861 | 12.5735 | -0.34929 | 0.18963 | -0.17696 | 0.23239 | 8.8285 | 9.0583 | 1.9779 | 21.7794 | 22.0149 | 22.2069 | 22.2742 | 22.1124 | 21.4397 | 20.2657 | 22.2113 | 22.3817 | 22.4223 | 22.3687 | 22.0118 | 21.2557 | 22.2981 | 17.3233 | 17.1134 | 16.1991 | 16.2097 | 16.2401 | 17.0675 | 16.768 | 22.3847 | 22.1551 | 21.714 | 22.0884 | 21.8126 | 21.3134 | 21.9501 | 21.5399 | 20.9303 | 20.1198 | 20.4142 | 19.9565 | 19.8066 | 0.14294 | -0.11694 | 20.7328 | 22.1018 | 22.4059 | 20.1389 | 21.6965 | 22.1494 | 21.9661 | 21.7281 | 21.3017 | 21.8 | 21.4685 | 21.0693 | 20.2429 | 20.1645 | 20.4297 | 20.4432 | 20.1287 |  | 20.2448 | 19.37 | 20.1388 | 19.6404 | 20.1074 | 20.3887 |  | 20.4503 |  |  | 20.2669 | 20.27 | 20.606 | [5 empty] | 21.9576 | 20.3232 | 21.6985 | 22.0849 | 19.5624 | 21.2042 | 21.8335 | 19.535 | 20.0261 | 21.2673 |  | 19.7705 | 21.0522 | 18.9213 | 19.81 | 20.9155 | 19.4565 | 20.1066 | 19.0187 | 20.2039 | 19.1173 | 20.2956 | 18.9781 | 20.1738 | 21.1802 | 19.5331 | 19.8582 | 21.0954 | 18.9883 | 19.8645 | 20.9143 | 18.9144 | 20.259 | 19.323 | 19.9396 | 18.9726 | 20.2391 | -0.22069 | 20.9452 | 0.048659 | 0.015936 | -26.9872 | 3.0977 | -5.8 | 0 | 0.89088 | -0.77626 | -7.8461 | 0.62564 | 0.49239 | -16.7191 | 4.2144 | 0.42336 | 0.44089 | 0.43233 | 0.37381 | 0.46379 | 0.43567 | 0.42812
42838.415 | -460 | 22.8838 | 22.8591 | 22.8508 | 22.7648 | 22.4127 | 21.7557 | 22.718 | 21.8226 | 22.3713 | 22.3897 | 22.3677 | 22.0597 | 21.2819 | 22.249 | 21.5714 | 21.7508 | 21.8837 | 21.0796 | 21.1623 | 21.3987 | 20.4768 | 20.6166 | 20.9222 | 21.9067 | 21.6596 | 21.3002 | 20.3788 | 20.4255 | 20.3456 | 22.035 | 21.6421 | 21.1747 | 21.9894 | 21.7235 | 21.3552 | 19.9293 | 20.513 |  | 20.5696 | 20.198 | 20.2754 | 19.3025 |  | 16.8344 | 16.8494 | 16.6067 | 16.9575 | 17.1279 | 17.7041 | 18.0808 | 16.0804 | 16.7858 | 16.198 | 16.9209 | 17.8778 | 44.9999 | 48.2098 | 44.2887 | 21.3528 |  |  | 0.60018 | -0.40813 | -43.4368 | 0.3502 | 0.0665 | -197.8374 | 13.2313 | -0.50897 | 0.084355 | -0.2571 | -0.12956 | 8.8291 | 9.0585 | 1.979 | 21.7822 | 22.0159 | 22.2099 | 22.2804 | 22.1137 | 21.4433 | 20.2672 | 22.2104 | 22.3853 | 22.4255 | 22.3792 | 22.0178 | 21.2572 | 22.2949 | 17.284 | 17.1678 | 16.2002 | 16.269 | 16.257 | 17.0681 | 16.7663 | 22.3829 | 22.1492 | 21.7167 | 22.0876 | 21.8093 | 21.3243 | 21.9507 | 21.5404 | 20.924 | 20.1177 | 20.406 | 19.9535 | 19.8009 | 0.060762 | -0.17895 | 20.735 | 22.1001 | 22.4014 | 20.138 | 21.6958 | 22.1422 | 21.9641 | 21.7318 | 21.2993 | 21.7957 | 21.4668 | 21.072 | 20.229 | 20.1653 | 20.4221 | 20.4375 | 20.127 |  | 20.246 | 19.3821 | 20.1487 | 19.6345 | 20.1051 | 20.3876 |  | 20.4548 |  |  | 20.2745 | 20.2831 | 20.6174 | [5 empty] | 21.9683 | 20.3311 | 21.7038 | 22.0897 | 19.5702 | 21.2091 | 21.829 | 19.535 | 20.0271 | 21.2633 |  | 19.7728 | 21.0406 | 18.9066 | 19.8121 | 20.9113 | 19.4533 | 20.0977 | 19.01 | 20.1989 | 19.1157 | 20.2827 | 18.99 | 20.1659 | 21.1768 | 19.5327 | 19.8646 | 21.1048 | 19.0038 | 19.8582 | 20.9071 | 18.9171 | 20.2578 | 19.3305 | 19.9413 | 18.9816 | 20.2414 | -0.21828 | 20.9464 | 0.048106 | 0.015921 | -27.0194 | 3.0976 | -16.41 | -0.19 | 0.92493 | -0.75817 | -7.8216 | 0.7023 | 0.30649 | -16.717 | 4.3232 | 0.42345 | 0.44088 | 0.43241 | 0.37825 | 0.46347 | 0.43575 | 0.42821
42838.415 | -459 | 22.8935 | 22.8581 | 22.8468 | 22.7822 | 22.415 | 21.7582 | 22.7206 | 21.8247 | 22.3728 | 22.3905 | 22.3779 | 22.0577 | 21.2858 | 22.248 | 21.5663 | 21.7404 | 21.882 | 21.0657 | 21.1661 | 21.3851 | 20.4789 | 20.63 | 20.9228 | 21.9005 | 21.6583 | 21.2985 | 20.3674 | 20.4184 | 20.3446 | 22.0411 | 21.6493 | 21.1752 | 21.9854 | 21.73 | 21.3638 | 19.935 | 20.5277 |  | 20.5631 | 20.1851 | 20.2885 | 19.2942 |  | 16.8196 | 16.8455 | 16.6146 | 16.9718 | 17.126 | 17.694 | 18.0398 | 16.0935 | 16.7785 | 16.2374 | 16.9096 | 17.8733 | 45.0032 | 48.1967 | 44.2726 | 21.3428 |  |  | 0.61989 | -0.30562 | -43.1155 | 0.45402 | 0.19267 | -197.8092 | 13.0558 | -0.33483 | 0.22038 | -0.33179 | -0.026096 | 8.8278 | 9.0577 | 1.9788 | 21.7831 | 22.0158 | 22.2118 | 22.2766 | 22.1179 | 21.4531 | 20.2727 | 22.2068 | 22.3847 | 22.4203 | 22.382 | 22.0194 | 21.2564 | 22.2945 | 17.2613 | 17.2152 | 16.1987 | 16.2871 | 16.2853 | 17.065 | 16.7556 | 22.3819 | 22.1566 | 21.7284 | 22.0992 | 21.8121 | 21.3239 | 21.9558 | 21.5475 | 20.93 | 20.1228 | 20.4078 | 19.9614 | 19.8113 | -0.043633 | -0.083847 | 20.7351 | 22.0959 | 22.4048 | 20.1327 | 21.6919 | 22.1381 | 21.9676 | 21.7288 | 21.2988 | 21.7975 | 21.4612 | 21.0672 | 20.228 | 20.1486 | 20.4156 | 20.4213 | 20.1307 |  | 20.2439 | 19.3912 | 20.1445 | 19.63 | 20.1116 | 20.3844 |  | 20.453 |  |  | 20.2858 | 20.2882 | 20.6254 | [5 empty] | 21.9642 | 20.3369 | 21.7017 | 22.0909 | 19.5732 | 21.2027 | 21.843 | 19.5462 | 20.0259 | 21.2613 |  | 19.7897 | 21.0458 | 18.9341 | 19.8222 | 20.9268 | 19.4591 | 20.1024 | 19.0116 | 20.1976 | 19.1245 | 20.2979 | 18.9902 | 20.1697 | 21.1769 | 19.5321 | 19.8651 | 21.0932 | 19.0004 | 19.8551 | 20.9173 | 18.9114 | 20.249 | 19.3202 | 19.938 | 18.9835 | 20.2439 | -0.34924 | 20.9463 | 0.04826 | 0.016117 | -26.9653 | 3.0977 | -1.06 | -0.02 | 0.93999 | -0.65608 | -7.7925 | 0.79965 | 0.52168 | -16.7155 | 4.2944 | 0.42328 | 0.44049 | 0.43275 | 0.3804 | 0.46238 | 0.43617 | 0.42809
42838.415 | -458 | 22.8875 | 22.8496 | 22.839 | 22.7778 | 22.415 | 21.7605 | 22.7248 | 21.8233 | 22.3725 | 22.3913 | 22.3787 | 22.0563 | 21.2817 | 22.2435 | 21.5752 | 21.7508 | 21.8855 | 21.0696 | 21.1585 | 21.3942 | 20.4783 | 20.6211 | 20.9231 | 21.9036 | 21.6688 | 21.3113 | 20.375 | 20.4283 | 20.3353 | 22.0305 | 21.6471 | 21.1706 | 21.9855 | 21.7316 | 21.3534 | 19.9271 | 20.5192 |  | 20.5691 | 20.1829 | 20.2774 | 19.2711 |  | 16.8187 | 16.8595 | 16.6295 | 16.9851 | 17.1433 | 17.6956 | 18.0225 | 16.0817 | 16.7747 | 16.2768 | 16.9112 | 17.8715 | 45.0107 | 48.1882 | 44.2573 | 21.3445 |  |  | 0.72437 | -0.22151 | -43.1306 | 0.38634 | 0.16047 | -197.8617 | 13.0204 | -0.36375 | -0.17583 | -0.35529 | 0.028241 | 8.8287 | 9.0587 | 1.9788 | 21.7803 | 22.0106 | 22.2108 | 22.2827 | 22.115 | 21.4544 | 20.2675 | 22.2037 | 22.3901 | 22.4192 | 22.3754 | 22.0121 | 21.2531 | 22.2946 | 17.2602 | 17.2233 | 16.2054 | 16.2543 | 16.3156 | 17.0679 | 16.7463 | 22.386 | 22.1552 | 21.7183 | 22.0909 | 21.8148 | 21.331 | 21.9547 | 21.5441 | 20.9236 | 20.1188 | 20.4082 | 19.963 | 19.81 | -0.028691 | 0.063558 | 20.7353 | 22.1072 | 22.4134 | 20.1406 | 21.7057 | 22.1505 | 21.9693 | 21.7342 | 21.3024 | 21.8049 | 21.4735 | 21.0697 | 20.2218 | 20.1515 | 20.4212 | 20.4203 | 20.1377 |  | 20.2451 | 19.4166 | 20.1362 | 19.6343 | 20.1109 | 20.3879 |  | 20.454 |  |  | 20.2845 | 20.2887 | 20.6277 | [5 empty] | 21.9594 | 20.3357 | 21.6978 | 22.0877 | 19.5647 | 21.1966 | 21.8357 | 19.5366 | 20.0217 | 21.2594 |  | 19.7806 | 21.0455 | 18.9313 | 19.8095 | 20.9174 | 19.4584 | 20.0948 | 19.0087 | 20.1987 | 19.1116 | 20.2916 | 18.9841 | 20.1674 | 21.1692 | 19.53 | 19.8599 | 21.0866 | 18.9964 | 19.8581 | 20.9099 | 18.9184 | 20.2369 | 19.3207 | 19.9329 | 18.9853 | 20.2504 | -0.12293 | 20.9466 | 0.047946 | 0.015914 | -27.0708 | 3.0976 | -6.82 | -0.19 | 1.0161 | -0.55856 | -7.7941 | 0.73766 | 0.47609 | -16.7178 | 4.2885 | 0.42312 | 0.43951 | 0.43261 | 0.38086 | 0.46055 | 0.43654 | 0.428
42838.415 | -457 | 22.8925 | 22.8538 | 22.8422 | 22.7687 | 22.4126 | 21.7579 | 22.7174 | 21.8201 | 22.3766 | 22.3878 | 22.3708 | 22.0566 | 21.2809 | 22.2419 | 21.5692 | 21.7513 | 21.8855 | 21.0768 | 21.1702 | 21.3986 | 20.4835 | 20.6267 | 20.9249 | 21.9029 | 21.6692 | 21.3028 | 20.3681 | 20.4273 | 20.3272 | 22.0364 | 21.648 | 21.1723 | 21.9902 | 21.7369 | 21.3494 | 19.9406 | 20.5156 |  | 20.575 | 20.1821 | 20.2826 | 19.2516 |  | 16.8267 | 16.8737 | 16.6514 | 16.9948 | 17.1438 | 17.684 | 18.0288 | 16.0789 | 16.7831 | 16.2647 | 16.9072 | 17.8738 | 45.0177 | 48.1823 | 44.2439 | 21.3598 |  |  | 0.43853 | -0.32928 | -42.9972 | 0.43628 | 0.069128 | -197.8749 | 13.2096 | -0.42486 | -0.15539 | -0.089893 | -0.028353 | 8.829 | 9.0588 | 1.9784 | 21.7786 | 22.0178 | 22.2113 | 22.2764 | 22.1098 | 21.4514 | 20.2574 | 22.2102 | 22.389 | 22.4098 | 22.3729 | 22.013 | 21.249 | 22.2965 | 17.2707 | 17.222 | 16.2191 | 16.2492 | 16.3516 | 17.0748 | 16.7604 | 22.3992 | 22.1689 | 21.7293 | 22.1015 | 21.8224 | 21.3339 | 21.9666 | 21.5521 | 20.9342 | 20.1316 | 20.4139 | 19.9678 | 19.8255 | -0.048745 | 0.0007918 | 20.7335 | 22.0974 | 22.411 | 20.1454 | 21.7009 | 22.1486 | 21.9675 | 21.7308 | 21.3016 | 21.8029 | 21.4708 | 21.0677 | 20.207 | 20.1538 | 20.4193 | 20.4107 | 20.1359 |  | 20.2457 | 19.4364 | 20.1381 | 19.6366 | 20.113 | 20.3894 |  | 20.4572 |  |  | 20.2812 | 20.2918 | 20.6266 | [5 empty] | 21.9616 | 20.3247 | 21.6877 | 22.0739 | 19.5682 | 21.1965 | 21.8225 | 19.5321 | 20.0171 | 21.2533 |  | 19.7729 | 21.0392 | 18.9259 | 19.8019 | 20.909 | 19.4573 | 20.0811 | 19.0125 | 20.1835 | 19.1081 | 20.2849 | 18.9923 | 20.1536 | 21.1746 | 19.5304 | 19.8633 | 21.0976 | 19.0012 | 19.8613 | 20.9076 | 18.9167 | 20.232 | 19.3274 | 19.9405 | 18.9859 | 20.25 | -0.21717 | 20.9448 | 0.04802 | 0.015043 | -27.003 | 3.0976 | -8.16 | -0.16 | 0.79059 | -0.68103 | -7.7822 | 0.78391 | 0.31248 | -16.718 | 4.3195 | 0.42319 | 0.43902 | 0.43262 | 0.38051 | 0.46068 | 0.43754 | 0.42799
42838.415 | -456 | 22.8912 | 22.8573 | 22.8408 | 22.7649 | 22.4072 | 21.7563 | 22.7102 | 21.8195 | 22.3722 | 22.3831 | 22.3641 | 22.0549 | 21.2752 | 22.2423 | 21.5684 | 21.743 | 21.8847 | 21.0731 | 21.1794 | 21.403 | 20.4833 | 20.6261 | 20.928 | 21.9062 | 21.6669 | 21.3033 | 20.3623 | 20.4322 | 20.329 | 22.0364 | 21.6431 | 21.1652 | 21.9878 | 21.7318 | 21.3438 | 19.938 | 20.5075 |  | 20.5728 | 20.1721 | 20.2797 | 19.2294 |  | 16.8323 | 16.893 | 16.6725 | 17.0023 | 17.1561 | 17.6932 | 18.0456 | 16.0621 | 16.7859 | 16.2774 | 16.9109 | 17.8799 | 45.019 | 48.1605 | 44.2277 | 21.3566 |  |  | 0.50292 | -0.30234 | -43.5209 | 0.11232 | 0.25706 | -197.7908 | 12.6221 | -0.45048 | -0.012361 | -0.15892 | 0.091084 | 8.8283 | 9.058 | 1.9782 | 21.7921 | 22.0241 | 22.2087 | 22.2792 | 22.1087 | 21.4403 | 20.2658 | 22.2158 | 22.3863 | 22.4235 | 22.3743 | 22.0113 | 21.2591 | 22.2982 | 17.2803 | 17.1798 | 16.214 | 16.218 | 16.3295 | 17.0659 | 16.7608 | 22.3942 | 22.1613 | 21.727 | 22.0941 | 21.8119 | 21.3272 | 21.9587 | 21.5464 | 20.9321 | 20.1253 | 20.4035 | 19.9643 | 19.8302 | -0.094749 | -0.027358 | 20.7402 | 22.1008 | 22.4117 | 20.1425 | 21.6992 | 22.1473 | 21.9663 | 21.7334 | 21.2959 | 21.8006 | 21.4672 | 21.0714 | 20.1955 | 20.169 | 20.4145 | 20.4007 | 20.1403 |  | 20.2496 | 19.442 | 20.1443 | 19.6595 | 20.1186 | 20.3895 |  | 20.4545 |  |  | 20.2845 | 20.2981 | 20.6177 | [5 empty] | 21.9613 | 20.3334 | 21.6935 | 22.0818 | 19.5703 | 21.1975 | 21.8296 | 19.5327 | 20.0286 | 21.2475 |  | 19.7815 | 21.0399 | 18.932 | 19.8084 | 20.9107 | 19.4666 | 20.0834 | 19.0102 | 20.1794 | 19.1102 | 20.2827 | 18.9969 | 20.1622 | 21.1694 | 19.5327 | 19.8631 | 21.093 | 19.0071 | 19.8636 | 20.9043 | 18.9241 | 20.2321 | 19.3309 | 19.9387 | 18.9873 | 20.2517 | -0.14612 | 20.9459 | 0.047725 | 0.015732 | -26.9426 | 3.0976 | -3.57 | -0.34 | 0.84665 | -0.6526 | -7.8297 | 0.39777 | 0.60258 | -16.7147 | 4.2224 | 0.4232 | 0.43907 | 0.43217 | 0.37841 | 0.46129 | 0.43807 | 0.42765
42838.415 | -455 | 22.8761 | 22.8473 | 22.8383 | 22.7693 | 22.4085 | 21.7478 | 22.7088 | 21.8188 | 22.3625 | 22.3757 | 22.3639 | 22.0485 | 21.2734 | 22.2399 | 21.5673 | 21.7432 | 21.8792 | 21.0732 | 21.169 | 21.3977 | 20.4778 | 20.6277 | 20.9249 | 21.9036 | 21.667 | 21.3068 | 20.3595 | 20.432 | 20.3176 | 22.0336 | 21.6445 | 21.1718 | 21.983 | 21.7302 | 21.3504 | 19.9397 | 20.504 |  | 20.5724 | 20.1656 | 20.2831 | 19.1977 |  | 16.8412 | 16.9009 | 16.6871 | 17.0151 | 17.178 | 17.7102 | 18.0559 | 15.956 | 16.7851 | 16.2655 | 16.9149 | 17.8788 | 45.0078 | 48.144 | 44.2185 | 21.3541 |  |  | 0.23088 | -0.39959 | -44.297 | 0.28251 | 0.16375 | -197.869 | 12.6681 | -0.484 | -0.36108 | -0.15409 | 0.023727 | 8.8289 | 9.0588 | 1.9784 | 21.7772 | 22.0162 | 22.203 | 22.2675 | 22.1019 | 21.4381 | 20.2584 | 22.2045 | 22.3779 | 22.4104 | 22.3592 | 21.9973 | 21.2419 | 22.2881 | 17.2827 | 17.1657 | 16.2183 | 16.2152 | 16.2897 | 17.0634 | 16.7614 | 22.3872 | 22.1632 | 21.7209 | 22.0958 | 21.8146 | 21.3242 | 21.9592 | 21.5511 | 20.927 | 20.123 | 20.3938 | 19.9629 | 19.8362 | -0.026136 | 0.093609 | 20.7409 | 22.105 | 22.4033 | 20.1405 | 21.6974 | 22.1502 | 21.9676 | 21.7383 | 21.3024 | 21.8035 | 21.4697 | 21.0688 | 20.193 | 20.1753 | 20.4061 | 20.3944 | 20.1457 |  | 20.247 | 19.4455 | 20.1422 | 19.6824 | 20.1146 | 20.3857 |  | 20.4617 |  |  | 20.2926 | 20.2993 | 20.6083 | [5 empty] | 21.9613 | 20.3313 | 21.6937 | 22.0789 | 19.5693 | 21.198 | 21.8313 | 19.5409 | 20.0283 | 21.2576 |  | 19.7899 | 21.0437 | 18.935 | 19.8109 | 20.9202 | 19.4677 | 20.0822 | 19.0101 | 20.186 | 19.1153 | 20.2928 | 18.9969 | 20.1603 | 21.1635 | 19.528 | 19.8606 | 21.0859 | 19.0059 | 19.8648 | 20.905 | 18.9257 | 20.2283 | 19.3249 | 19.9348 | 18.9858 | 20.2454 | -0.064687 | 20.946 | 0.047025 | 0.015152 | -27.0298 | 3.0976 | -3.41 | -0.04 | 0.57364 | -0.75026 | -7.8993 | 0.63085 | 0.48095 | -16.7185 | 4.2302 | 0.42297 | 0.4389 | 0.4314 | 0.37784 | 0.46088 | 0.43901 | 0.42741
42838.415 | -454 | 22.8795 | 22.8461 | 22.8415 | 22.7681 | 22.4057 | 21.7566 | 22.7128 | 21.8216 | 22.3699 | 22.3854 | 22.3717 | 22.0526 | 21.2678 | 22.2367 | 21.5709 | 21.7459 | 21.8842 | 21.0765 | 21.1656 | 21.3915 | 20.48 | 20.6189 | 20.9189 | 21.9024 | 21.6661 | 21.3054 | 20.3609 | 20.4335 | 20.3175 | 22.041 | 21.6471 | 21.1802 | 21.9912 | 21.7388 | 21.3529 | 19.9358 | 20.475 |  | 20.5781 | 20.1585 | 20.2798 | 19.1817 |  | 16.8473 | 16.9085 | 16.7105 | 17.0425 | 17.2091 | 17.7299 | 18.072 | 15.9616 | 16.778 | 16.2431 | 16.9143 | 17.871 | 45.0076 | 48.1293 | 44.2007 | 21.3428 |  |  | 0.46087 | -0.40813 | -45.1151 | 0.08801 | 0.11381 | -197.8709 | 12.4874 | -0.48728 | -0.37257 | -0.13752 | -0.03981 | 8.8287 | 9.0582 | 1.979 | 21.7825 | 22.018 | 22.2091 | 22.2801 | 22.113 | 21.4472 | 20.2636 | 22.2128 | 22.3837 | 22.4134 | 22.3759 | 22.0029 | 21.2534 | 22.2929 | 17.3118 | 17.1383 | 16.2542 | 16.2259 | 16.2507 | 17.0674 | 16.7602 | 22.392 | 22.1541 | 21.7172 | 22.0896 | 21.8124 | 21.3197 | 21.9599 | 21.5445 | 20.936 | 20.1226 | 20.4022 | 19.9597 | 19.8442 | -0.058575 | 0.15124 | 20.7379 | 22.1025 | 22.4074 | 20.1452 | 21.7094 | 22.1498 | 21.9723 | 21.7383 | 21.3137 | 21.8025 | 21.4755 | 21.0721 | 20.1949 | 20.1711 | 20.4134 | 20.3966 | 20.1561 |  | 20.253 | 19.4653 | 20.1427 | 19.705 | 20.1184 | 20.3873 |  | 20.4635 |  |  | 20.3036 | 20.2965 | 20.6024 | [5 empty] | 21.9601 | 20.343 | 21.6971 | 22.0836 | 19.5753 | 21.1996 | 21.8283 | 19.5418 | 20.027 | 21.2512 |  | 19.8007 | 21.0433 | 18.9374 | 19.8122 | 20.9278 | 19.4685 | 20.0759 | 19.0098 | 20.1831 | 19.1143 | 20.2821 | 18.9967 | 20.1642 | 21.1652 | 19.5235 | 19.8601 | 21.086 | 19.018 | 19.8707 | 20.9131 | 18.9263 | 20.2225 | 19.3207 | 19.9368 | 18.9833 | 20.2438 | -0.21828 | 20.9464 | 0.047897 | 0.015863 | -27.0085 | 3.0977 | -21 | -0.04 | 0.81047 | -0.75825 | -7.9721 | 0.35211 | 0.40098 | -16.7192 | 4.2001 | 0.42288 | 0.43837 | 0.4309 | 0.37508 | 0.45675 | 0.43932 | 0.42717
42838.415 | -453 | 22.8738 | 22.8437 | 22.836 | 22.7649 | 22.4012 | 21.7502 | 22.7121 | 21.8196 | 22.3664 | 22.3757 | 22.3628 | 22.0475 | 21.2637 | 22.2401 | 21.5649 | 21.736 | 21.881 | 21.0672 | 21.1626 | 21.3872 | 20.4706 | 20.6143 | 20.9132 | 21.8927 | 21.658 | 21.2961 | 20.3443 | 20.433 | 20.3195 | 22.0402 | 21.6543 | 21.179 | 21.9975 | 21.733 | 21.3509 | 19.934 | 20.4629 |  | 20.5792 | 20.1509 | 20.2713 | 19.1943 |  | 16.8596 | 16.9119 | 16.7199 | 17.0582 | 17.2313 | 17.7522 | 18.0876 | 16.0122 | 16.7826 | 16.2253 | 16.9194 | 17.8803 | 45.0189 | 48.1232 | 44.1973 | 21.3555 |  |  | 0.39384 | -0.15712 | -45.6257 | 0.24243 | 0.25115 | -197.8434 | 12.2443 | -0.59374 | -0.26359 | 0.13963 | -0.040331 | 8.8282 | 9.0578 | 1.979 | 21.7899 | 22.0154 | 22.2187 | 22.2807 | 22.1142 | 21.4492 | 20.2713 | 22.2147 | 22.389 | 22.423 | 22.3805 | 22.0124 | 21.2599 | 22.2965 | 17.3485 | 17.0961 | 16.258 | 16.2253 | 16.2402 | 17.0607 | 16.7634 | 22.3899 | 22.1484 | 21.7115 | 22.0894 | 21.8023 | 21.3214 | 21.9491 | 21.5431 | 20.9237 | 20.1071 | 20.393 | 19.9556 | 19.8435 | -0.11873 | -0.04866 | 20.7441 | 22.1071 | 22.4099 | 20.1405 | 21.7029 | 22.1526 | 21.9749 | 21.7466 | 21.3109 | 21.8162 | 21.4782 | 21.0739 | 20.1902 | 20.1768 | 20.4175 | 20.3919 | 20.1565 |  | 20.248 | 19.4698 | 20.1417 | 19.7132 | 20.1154 | 20.3778 |  | 20.4573 |  |  | 20.3114 | 20.3094 | 20.6001 | [5 empty] | 21.9558 | 20.3441 | 21.6986 | 22.0871 | 19.5767 | 21.1997 | 21.8265 | 19.5381 | 20.0265 | 21.2519 |  | 19.7946 | 21.0378 | 18.9362 | 19.808 | 20.9229 | 19.4626 | 20.0733 | 19.0056 | 20.179 | 19.1154 | 20.2769 | 19.0021 | 20.1647 | 21.1689 | 19.5194 | 19.8592 | 21.0905 | 19.0145 | 19.869 | 20.9046 | 18.928 | 20.2185 | 19.3218 | 19.9385 | 18.9873 | 20.2447 | -0.31196 | 20.9469 | 0.047842 | 0.016016 | -27.1315 | 3.0977 | -9.23 | -0.07 | 0.74922 | -0.47046 | -8.0171 | 0.58439 | 0.59567 | -16.7187 | 4.1592 | 0.4227 | 0.43821 | 0.43057 | 0.37021 | 0.4567 | 0.43891 | 0.42667
42838.415 | -452 | 22.8904 | 22.853 | 22.8435 | 22.7667 | 22.4117 | 21.7535 | 22.7095 | 21.8164 | 22.3729 | 22.3812 | 22.3797 | 22.0637 | 21.2782 | 22.2397 | 21.5683 | 21.7387 | 21.881 | 21.0696 | 21.1661 | 21.3905 | 20.4714 | 20.6219 | 20.9234 | 21.8957 | 21.6621 | 21.2955 | 20.3424 | 20.4311 | 20.3316 | 22.0314 | 21.6403 | 21.1715 | 21.9856 | 21.721 | 21.3389 | 19.9322 | 20.4408 |  | 20.569 | 20.1517 | 20.2662 | 19.1766 |  | 16.8582 | 16.9035 | 16.731 | 17.0816 | 17.2448 | 17.7658 | 18.0906 | 16.0416 | 16.7876 | 16.2753 | 16.9121 | 17.8828 | 45.0131 | 48.1286 | 44.2084 | 21.36 |  |  | 0.4819 | -0.23203 | -45.7558 | 0.29566 | 0.41346 | -197.8755 | 12.1116 | -0.56022 | -0.15403 | -0.0408 | -0.11238 | 8.829 | 9.0587 | 1.9788 | 21.7821 | 22.0086 | 22.2105 | 22.2759 | 22.1112 | 21.4479 | 20.2583 | 22.2124 | 22.3857 | 22.4204 | 22.3766 | 22.0087 | 21.2477 | 22.2907 | 17.4034 | 17.0838 | 16.242 | 16.229 | 16.2405 | 17.0709 | 16.7734 | 22.3904 | 22.1528 | 21.7169 | 22.0946 | 21.811 | 21.3249 | 21.9573 | 21.5455 | 20.9244 | 20.1134 | 20.3936 | 19.9578 | 19.8444 | 0.042478 | -0.046188 | 20.7387 | 22.101 | 22.4131 | 20.1458 | 21.7013 | 22.1504 | 21.9636 | 21.7281 | 21.309 | 21.808 | 21.4761 | 21.0664 | 20.1747 | 20.1673 | 20.4083 | 20.3786 | 20.1533 |  | 20.2483 | 19.4818 | 20.1393 | 19.7244 | 20.1148 | 20.382 |  | 20.4574 |  |  | 20.3219 | 20.3181 | 20.6091 | [5 empty] | 21.9582 | 20.3421 | 21.7022 | 22.0882 | 19.5863 | 21.2036 | 21.8279 | 19.5413 | 20.032 | 21.2496 |  | 19.7978 | 21.0345 | 18.9405 | 19.806 | 20.9155 | 19.4652 | 20.0729 | 19.009 | 20.1736 | 19.1103 | 20.2815 | 19.0016 | 20.1556 | 21.1627 | 19.5162 | 19.8521 | 21.089 | 19.0039 | 19.8567 | 20.8885 | 18.9256 | 20.2079 | 19.3159 | 19.9335 | 18.9817 | 20.2384 | -0.17858 | 20.945 | 0.047332 | 0.014273 | -27.0086 | 3.0976 | -9.18 | 0.07 | 0.82877 | -0.57171 | -8.0284 | 0.64536 | 0.7643 | -16.7204 | 4.1367 | 0.4228 | 0.4378 | 0.43024 | 0.36532 | 0.45965 | 0.43934 | 0.42686
42838.4151 | -451 | 22.8885 | 22.8645 | 22.8386 | 22.7784 | 22.4154 | 21.7533 | 22.7184 | 21.8273 | 22.3759 | 22.391 | 22.3788 | 22.0521 | 21.2867 | 22.2427 | 21.5689 | 21.7428 | 21.8844 | 21.0758 | 21.1779 | 21.3912 | 20.4736 | 20.6242 | 20.9217 | 21.9002 | 21.6694 | 21.3037 | 20.3415 | 20.4376 | 20.3291 | 22.0321 | 21.641 | 21.168 | 21.9823 | 21.7293 | 21.3498 | 19.9299 | 20.4239 |  | 20.5668 | 20.145 | 20.2615 | 19.1785 |  | 16.8534 | 16.9054 | 16.7308 | 17.0917 | 17.2603 | 17.7748 | 18.0927 | 16.0864 | 16.7811 | 16.3012 | 16.9083 | 17.8751 | 44.9935 | 48.1136 | 44.2036 | 21.3587 |  |  | 0.56929 | -0.39499 | -45.7387 | 0.56771 | 0.15192 | -197.8407 | 12.2607 | -0.62265 | -0.10013 | -0.12367 | -0.046581 | 8.8298 | 9.0595 | 1.9785 | 21.7843 | 22.0156 | 22.2123 | 22.275 | 22.1142 | 21.4469 | 20.2696 | 22.2153 | 22.3888 | 22.4209 | 22.383 | 22.0187 | 21.251 | 22.2932 | 17.4322 | 17.0741 | 16.2271 | 16.2133 | 16.2325 | 17.0672 | 16.7694 | 22.3909 | 22.1544 | 21.7158 | 22.0919 | 21.8154 | 21.3201 | 21.9544 | 21.5419 | 20.9216 | 20.1183 | 20.3902 | 19.9575 | 19.8376 | -0.1207 | 0.13374 | 20.7412 | 22.0976 | 22.4062 | 20.1331 | 21.7031 | 22.1562 | 21.9662 | 21.739 | 21.3087 | 21.8079 | 21.4729 | 21.0774 | 20.1672 | 20.176 | 20.4089 | 20.3711 | 20.1419 |  | 20.2425 | 19.485 | 20.1387 | 19.7193 | 20.1119 | 20.3782 |  | 20.4589 |  |  | 20.3298 | 20.3214 | 20.6081 | [5 empty] | 21.9591 | 20.3469 | 21.7 | 22.0858 | 19.5879 | 21.1997 | 21.828 | 19.5488 | 20.0374 | 21.2504 |  | 19.8042 | 21.0376 | 18.9404 | 19.8089 | 20.9242 | 19.4723 | 20.0782 | 19.0154 | 20.1693 | 19.1018 | 20.2786 | 19.0083 | 20.1539 | 21.1667 | 19.5174 | 19.8544 | 21.0917 | 19.0096 | 19.8633 | 20.8932 | 18.9248 | 20.2071 | 19.3145 | 19.9407 | 18.9827 | 20.23 | -0.14371 | 20.9443 | 0.046527 | 0.01272 | -26.9184 | 3.0976 | -7.8 | -0.11 | 0.90079 | -0.74594 | -8.0269 | 0.89427 | 0.46331 | -16.7192 | 4.1621 | 0.42292 | 0.43769 | 0.43028 | 0.36168 | 0.46084 | 0.43921 | 0.42721
42838.4151 | -450 | 22.8931 | 22.8617 | 22.8448 | 22.7776 | 22.4143 | 21.7593 | 22.7241 | 21.8269 | 22.3765 | 22.3933 | 22.3766 | 22.0553 | 21.2814 | 22.2516 | 21.5795 | 21.7487 | 21.8871 | 21.0722 | 21.1782 | 21.4026 | 20.4772 | 20.626 | 20.9233 | 21.901 | 21.6694 | 21.3071 | 20.3463 | 20.4489 | 20.3394 | 22.0355 | 21.6458 | 21.1689 | 21.9879 | 21.7304 | 21.3509 | 19.9373 | 20.4201 |  | 20.5762 | 20.1471 | 20.2634 | 19.1787 |  | 16.8537 | 16.917 | 16.7359 | 17.1108 | 17.2689 | 17.7937 | 18.0923 | 16.153 | 16.7822 | 16.2977 | 16.9142 | 17.8739 | 44.9788 | 48.1005 | 44.199 | 21.3562 |  |  | 0.47007 | -0.29511 | -45.4246 | 0.49542 | 0.10001 | -197.8749 | 11.9361 | -0.52145 | -0.10538 | -0.19207 | 0.071641 | 8.8289 | 9.0583 | 1.9784 | 21.7823 | 22.0117 | 22.2127 | 22.2767 | 22.113 | 21.4449 | 20.2633 | 22.2164 | 22.3795 | 22.4206 | 22.3799 | 22.0181 | 21.2539 | 22.3038 | 17.4524 | 17.0581 | 16.2321 | 16.2172 | 16.2254 | 17.0651 | 16.7778 | 22.3841 | 22.1592 | 21.7198 | 22.0869 | 21.816 | 21.321 | 21.9513 | 21.5335 | 20.9206 | 20.116 | 20.3769 | 19.9495 | 19.8416 | -0.10261 | 0.0021232 | 20.7389 | 22.1033 | 22.4089 | 20.1314 | 21.7074 | 22.1559 | 21.9692 | 21.7304 | 21.3015 | 21.8044 | 21.4743 | 21.0715 | 20.1622 | 20.1629 | 20.4167 | 20.3615 | 20.1452 |  | 20.2497 | 19.4907 | 20.1388 | 19.7292 | 20.1136 | 20.3744 |  | 20.4492 |  |  | 20.3303 | 20.3301 | 20.6063 | [5 empty] | 21.9613 | 20.348 | 21.7031 | 22.0823 | 19.581 | 21.1997 | 21.8303 | 19.5555 | 20.0323 | 21.2463 |  | 19.794 | 21.0352 | 18.9357 | 19.8057 | 20.9236 | 19.4704 | 20.0691 | 19.0154 | 20.163 | 19.0976 | 20.2687 | 19.0091 | 20.1572 | 21.1699 | 19.5238 | 19.858 | 21.0868 | 19.0142 | 19.8667 | 20.8961 | 18.9248 | 20.2024 | 19.3196 | 19.9391 | 18.9827 | 20.2259 | -0.24592 | 20.9443 | 0.046232 | 0.012328 | -27.0317 | 3.0977 | 5.79 | 0.06 | 0.81855 | -0.64477 | -7.9995 | 0.83542 | 0.37592 | -16.7212 | 4.1068 | 0.42307 | 0.43754 | 0.43007 | 0.35918 | 0.46127 | 0.43945 | 0.42702
42838.4151 | -449 | 22.8933 | 22.8572 | 22.8457 | 22.7713 | 22.4079 | 21.7563 | 22.7177 | 21.8256 | 22.3722 | 22.3901 | 22.3725 | 22.0553 | 21.2758 | 22.2454 | 21.5683 | 21.7423 | 21.8839 | 21.0669 | 21.1691 | 21.3964 | 20.4725 | 20.6257 | 20.9217 | 21.8941 | 21.6677 | 21.3031 | 20.3393 | 20.4543 | 20.3492 | 22.0387 | 21.6418 | 21.1729 | 21.9915 | 21.7305 | 21.3494 | 19.9396 | 20.4074 |  | 20.5783 | 20.1444 | 20.2664 | 19.1727 |  | 16.8595 | 16.9272 | 16.7528 | 17.1314 | 17.2881 | 17.799 | 18.0761 | 16.1961 | 16.7893 | 16.2782 | 16.9136 | 17.874 | 44.971 | 48.0903 | 44.1931 | 21.3666 |  |  | 0.51015 | -0.2156 | -45.3076 | 0.49082 | 0.22815 | -197.7914 | 11.9525 | -0.61476 | -0.11803 | -0.20801 | -0.14328 | 8.8298 | 9.0597 | 1.9789 | 21.7826 | 22.0114 | 22.2112 | 22.2718 | 22.1098 | 21.4447 | 20.261 | 22.2031 | 22.3833 | 22.4134 | 22.3688 | 22.0018 | 21.2554 | 22.2848 | 17.4795 | 17.0339 | 16.212 | 16.22 | 16.2199 | 17.0644 | 16.7818 | 22.3894 | 22.1568 | 21.7205 | 22.0898 | 21.8145 | 21.3175 | 21.9526 | 21.5434 | 20.9291 | 20.123 | 20.382 | 19.953 | 19.8562 | 0.017903 | 0.21134 | 20.7351 | 22.1086 | 22.4068 | 20.1413 | 21.6971 | 22.1571 | 21.9765 | 21.7328 | 21.3018 | 21.8067 | 21.466 | 21.0732 | 20.1539 | 20.1754 | 20.4069 | 20.3489 | 20.1374 |  | 20.2409 | 19.5002 | 20.1375 | 19.7279 | 20.1013 | 20.372 |  | 20.4409 |  |  | 20.3345 | 20.3409 | 20.6026 | [5 empty] | 21.9633 | 20.3505 | 21.7023 | 22.0807 | 19.579 | 21.1982 | 21.8276 | 19.547 | 20.0306 | 21.2261 |  | 19.7767 | 21.0296 | 18.9151 | 19.7956 | 20.9004 | 19.4645 | 20.0614 | 19.0037 | 20.1529 | 19.0939 | 20.2549 | 19.0143 | 20.1603 | 21.1682 | 19.5299 | 19.8667 | 21.0916 | 19.0144 | 19.8736 | 20.8959 | 18.9337 | 20.207 | 19.3216 | 19.9505 | 18.9887 | 20.2227 | -0.18767 | 20.9439 | 0.047522 | 0.011885 | -26.8694 | 3.0976 | -3.34 | 0 | 0.85275 | -0.55112 | -7.9893 | 0.83155 | 0.56779 | -16.7178 | 4.1097 | 0.42299 | 0.43723 | 0.42969 | 0.35609 | 0.46396 | 0.4397 | 0.42685
42838.4151 | -448 | 22.8923 | 22.8599 | 22.8489 | 22.7771 | 22.4181 | 21.7559 | 22.7177 | 21.8288 | 22.3718 | 22.382 | 22.3709 | 22.0623 | 21.2803 | 22.2438 | 21.5821 | 21.7436 | 21.8885 | 21.0771 | 21.175 | 21.4013 | 20.4809 | 20.6282 | 20.9267 | 21.8993 | 21.6661 | 21.3107 | 20.3468 | 20.4582 | 20.3823 | 22.0378 | 21.6439 | 21.171 | 21.9868 | 21.7305 | 21.3477 | 19.932 | 20.3725 |  | 20.5711 | 20.1446 | 20.2557 | 19.1646 |  | 16.8723 | 16.951 | 16.7728 | 17.1312 | 17.2695 | 17.7646 | 18.0536 | 16.1453 | 16.7897 | 16.2647 | 16.9102 | 17.871 | 44.9504 | 48.0813 | 44.186 | 21.3561 |  |  | 0.38267 | 0.064987 | -45.0395 | 0.38043 | 0.30306 | -197.7993 | 12.3843 | -0.53065 | 0.049133 | -0.43606 | -0.10335 | 8.8279 | 9.0577 | 1.9792 | 21.7926 | 22.0163 | 22.2141 | 22.2836 | 22.1171 | 21.4479 | 20.2658 | 22.2158 | 22.3872 | 22.4149 | 22.377 | 22.0127 | 21.2526 | 22.3015 | 17.4889 | 17.0308 | 16.1944 | 16.2146 | 16.227 | 17.0555 | 16.7832 | 22.3798 | 22.1505 | 21.7135 | 22.0882 | 21.8061 | 21.3257 | 21.9441 | 21.5422 | 20.9206 | 20.1158 | 20.3698 | 19.9453 | 19.8509 | 0.15198 | 0.033506 | 20.739 | 22.1062 | 22.4042 | 20.1352 | 21.6904 | 22.1412 | 21.974 | 21.7376 | 21.3003 | 21.8031 | 21.4682 | 21.0594 | 20.1531 | 20.1783 | 20.411 | 20.3335 | 20.1531 |  | 20.2498 | 19.5325 | 20.1378 | 19.7363 | 20.1203 | 20.3878 |  | 20.4599 |  |  | 20.3381 | 20.349 | 20.5976 | [5 empty] | 21.9686 | 20.3481 | 21.7012 | 22.0806 | 19.5797 | 21.2063 | 21.827 | 19.5494 | 20.0382 | 21.2355 |  | 19.7873 | 21.0284 | 18.9239 | 19.7975 | 20.903 | 19.4616 | 20.0679 | 19.0097 | 20.1488 | 19.0968 | 20.2607 | 19.0139 | 20.1536 | 21.1698 | 19.5359 | 19.866 | 21.0895 | 19.0168 | 19.8698 | 20.9006 | 18.923 | 20.196 | 19.3219 | 19.9481 | 18.9887 | 20.2114 | -0.14983 | 20.9443 | 0.048333 | 0.013438 | -27.1541 | 3.0976 | 4.04 | -0.1 | 0.7386 | 0.30259 | -7.966 | 0.73211 | 0.65436 | -16.7171 | 4.183 | 0.42285 | 0.43634 | 0.43009 | 0.35401 | 0.46608 | 0.43966 | 0.42676
42838.4151 | -447 | 22.8858 | 22.8502 | 22.8475 | 22.7724 | 22.4159 | 21.752 | 22.7184 | 21.8275 | 22.3686 | 22.3815 | 22.3682 | 22.0537 | 21.2733 | 22.2431 | 21.5689 | 21.738 | 21.8751 | 21.0671 | 21.1667 | 21.3865 | 20.4691 | 20.6172 | 20.9124 | 21.8896 | 21.6519 | 21.3025 | 20.3406 | 20.441 | 20.3827 | 22.0425 | 21.6438 | 21.1705 | 21.9921 | 21.7317 | 21.3584 | 19.9401 | 20.3533 |  | 20.5704 | 20.1489 | 20.2619 | 19.1632 |  | 16.8882 | 16.9808 | 16.7805 | 17.139 | 17.2568 | 17.755 | 18.048 | 16.0289 | 16.7857 | 16.2678 | 16.9085 | 17.8777 | 44.9525 | 48.0802 | 44.177 | 21.3698 |  |  | 0.49109 | -0.28394 | -44.638 | 0.59925 | 0.17821 | -197.8217 | 12.333 | -0.53197 | -0.33228 | -0.15766 | 0.033449 | 8.8284 | 9.0581 | 1.9788 | 21.7928 | 22.0177 | 22.2173 | 22.2835 | 22.1144 | 21.4462 | 20.2665 | 22.2146 | 22.3918 | 22.4198 | 22.3781 | 22.0162 | 21.2496 | 22.3038 | 17.5008 | 17.0576 | 16.1995 | 16.2141 | 16.2341 | 17.0642 | 16.7782 | 22.3814 | 22.1533 | 21.7161 | 22.0888 | 21.8067 | 21.3228 | 21.9498 | 21.5379 | 20.924 | 20.1164 | 20.3563 | 19.9477 | 19.8487 | 0.088482 | 0.11491 | 20.743 | 22.1131 | 22.412 | 20.1361 | 21.6966 | 22.1486 | 21.9733 | 21.738 | 21.3017 | 21.8164 | 21.471 | 21.0665 | 20.1593 | 20.1911 | 20.4235 | 20.3318 | 20.1391 |  | 20.2453 | 19.5313 | 20.134 | 19.747 | 20.1173 | 20.3899 |  | 20.4491 |  |  | 20.3431 | 20.3383 | 20.5984 | [5 empty] | 21.9588 | 20.3424 | 21.694 | 22.0751 | 19.5786 | 21.1926 | 21.8216 | 19.547 | 20.0308 | 21.2287 |  | 19.7752 | 21.0201 | 18.9288 | 19.7908 | 20.9016 | 19.4686 | 20.0618 | 19.0087 | 20.138 | 19.0909 | 20.2531 | 19.0181 | 20.1572 | 21.1703 | 19.539 | 19.8673 | 21.0937 | 19.0114 | 19.8667 | 20.896 | 18.9214 | 20.1951 | 19.3315 | 19.9515 | 18.9896 | 20.2071 | -0.11069 | 20.9451 | 0.048819 | 0.014201 | -26.9868 | 3.0976 | -16.1 | 0.07 | 0.83672 | -0.63253 | -7.9308 | 0.9189 | 0.50177 | -16.7178 | 4.1742 | 0.42309 | 0.43625 | 0.42969 | 0.3537 | 0.46494 | 0.43998 | 0.42684
42838.4151 | -446 | 22.8935 | 22.8589 | 22.8405 | 22.7748 | 22.4083 | 21.7544 | 22.7219 | 21.823 | 22.381 | 22.387 | 22.3713 | 22.0537 | 21.274 | 22.2495 | 21.5661 | 21.7397 | 21.8818 | 21.0679 | 21.1666 | 21.3911 | 20.4807 | 20.6211 | 20.9247 | 21.9022 | 21.6671 | 21.311 | 20.3526 | 20.4545 | 20.4081 | 22.0418 | 21.648 | 21.1715 | 21.9919 | 21.7318 | 21.3524 | 19.9358 | 20.3401 |  | 20.5686 | 20.1423 | 20.2609 | 19.1442 |  | 16.8983 | 16.997 | 16.7789 | 17.1262 | 17.2412 | 17.7528 | 18.0656 | 15.9287 | 16.7908 | 16.3006 | 16.9035 | 17.8771 | 44.937 | 48.0704 | 44.1518 | 21.3639 |  |  | 0.53578 | -0.14989 | -44.5454 | 0.58085 | 0.1493 | -197.8407 | 12.2936 | -0.36703 | -0.2451 | 0.10438 | -0.079218 | 8.8278 | 9.0574 | 1.9787 | 21.7892 | 22.0223 | 22.2202 | 22.2835 | 22.1201 | 21.4493 | 20.2677 | 22.2137 | 22.3912 | 22.4234 | 22.379 | 22.0182 | 21.2586 | 22.3049 | 17.5088 | 17.0639 | 16.2148 | 16.2201 | 16.2432 | 17.0726 | 16.8013 | 22.3888 | 22.1601 | 21.72 | 22.0996 | 21.8117 | 21.3236 | 21.9627 | 21.5477 | 20.9257 | 20.1215 | 20.36 | 19.953 | 19.8592 | 0.058796 | 0.21648 | 20.7392 | 22.1061 | 22.4021 | 20.1427 | 21.6987 | 22.1437 | 21.9668 | 21.7358 | 21.3118 | 21.8075 | 21.4676 | 21.0708 | 20.1624 | 20.1748 | 20.418 | 20.3245 | 20.1251 |  | 20.2523 | 19.5471 | 20.1344 | 19.7452 | 20.1197 | 20.3822 |  | 20.4527 |  |  | 20.3306 | 20.3434 | 20.6056 | [5 empty] | 21.9672 | 20.3556 | 21.702 | 22.079 | 19.5871 | 21.1949 | 21.8257 | 19.5553 | 20.0425 | 21.2262 |  | 19.7828 | 21.0256 | 18.9357 | 19.781 | 20.8986 | 19.4656 | 20.0633 | 19.0041 | 20.1346 | 19.0893 | 20.2589 | 19.0082 | 20.1413 | 21.1607 | 19.5299 | 19.8638 | 21.0905 | 19.0039 | 19.8586 | 20.8814 | 18.9023 | 20.175 | 19.3191 | 19.9484 | 18.9764 | 20.1991 | -0.12535 | 20.9468 | 0.048917 | 0.015144 | -27.1292 | 3.0977 | -1.84 | -0.15 | 0.87399 | -0.45958 | -7.9228 | 0.9047 | 0.45927 | -16.7186 | 4.1675 | 0.42371 | 0.43582 | 0.42983 | 0.35379 | 0.46592 | 0.44036 | 0.42672
42838.4151 | -445 | 22.8941 | 22.8617 | 22.8462 | 22.7772 | 22.4098 | 21.7547 | 22.7192 | 21.8266 | 22.3738 | 22.3879 | 22.3771 | 22.0574 | 21.2789 | 22.2391 | 21.5824 | 21.7546 | 21.8918 | 21.0802 | 21.1809 | 21.3992 | 20.483 | 20.6311 | 20.9272 | 21.8995 | 21.671 | 21.308 | 20.3567 | 20.4585 | 20.4397 | 22.0369 | 21.6483 | 21.1644 | 21.9844 | 21.7268 | 21.3483 | 19.9343 | 20.3138 |  | 20.561 | 20.1363 | 20.2561 | 19.1161 |  | 16.8884 | 16.9867 | 16.7772 | 17.1164 | 17.2282 | 17.7315 | 18.0588 | 15.8409 | 16.7864 | 16.3225 | 16.894 | 17.8772 | 44.9315 | 48.0682 | 44.1392 | 21.3661 |  |  | 0.58375 | -0.10192 | -44.1662 | 0.39817 | 0.14338 | -197.8486 | 12.6116 | -0.34798 | 0.031813 | -0.35382 | -0.068975 | 8.8295 | 9.0592 | 1.9786 | 21.7859 | 22.0228 | 22.2164 | 22.2833 | 22.1209 | 21.4504 | 20.2674 | 22.217 | 22.3895 | 22.4223 | 22.3785 | 22.0154 | 21.2566 | 22.3004 | 17.4944 | 17.0669 | 16.201 | 16.2166 | 16.2289 | 17.0656 | 16.7964 | 22.3783 | 22.148 | 21.7102 | 22.0825 | 21.7943 | 21.3145 | 21.9468 | 21.533 | 20.9216 | 20.112 | 20.3464 | 19.9387 | 19.847 | -0.06231 | 0.15695 | 20.7394 | 22.1045 | 22.411 | 20.1341 | 21.7056 | 22.1478 | 21.9726 | 21.7368 | 21.3087 | 21.8033 | 21.4672 | 21.0695 | 20.1658 | 20.1711 | 20.4139 | 20.3206 | 20.1089 |  | 20.2525 | 19.5459 | 20.1391 | 19.7409 | 20.1102 | 20.3797 |  | 20.4549 |  |  | 20.3391 | 20.3561 | 20.6127 | [5 empty] | 21.9636 | 20.3537 | 21.6932 | 22.0829 | 19.5931 | 21.198 | 21.8225 | 19.5577 | 20.048 | 21.2405 |  | 19.782 | 21.0221 | 18.9329 | 19.7919 | 20.9082 | 19.4818 | 20.073 | 19.0102 | 20.1426 | 19.101 | 20.2641 | 19.0044 | 20.1401 | 21.1588 | 19.5269 | 19.8649 | 21.0889 | 19.0036 | 19.8552 | 20.8828 | 18.9086 | 20.1736 | 19.3255 | 19.9616 | 18.974 | 20.1883 | -0.08064 | 20.9462 | 0.048075 | 0.014673 | -27.1667 | 3.0976 | -3.89 | 0.16 | 0.91233 | -0.37896 | -7.8888 | 0.74904 | 0.45007 | -16.7183 | 4.221 | 0.42417 | 0.43601 | 0.42963 | 0.35457 | 0.46689 | 0.44109 | 0.42674
42838.4151 | -444 | 22.8861 | 22.8528 | 22.8436 | 22.7645 | 22.4107 | 21.755 | 22.7277 | 21.8193 | 22.3699 | 22.3834 | 22.3711 | 22.052 | 21.2717 | 22.2319 | 21.5664 | 21.7425 | 21.8809 | 21.0699 | 21.1707 | 21.386 | 20.4712 | 20.6165 | 20.9206 | 21.8921 | 21.6653 | 21.2948 | 20.3508 | 20.4469 | 20.4372 | 22.046 | 21.6467 | 21.1724 | 21.9994 | 21.7335 | 21.3518 | 19.9335 | 20.3085 |  | 20.5668 | 20.1473 | 20.249 | 19.109 |  | 16.9052 | 17.0133 | 16.7817 | 17.1169 | 17.2227 | 17.7098 | 18.0371 | 15.7467 | 16.8027 | 16.3045 | 16.9094 | 17.8737 | 44.9227 | 48.0621 | 44.1215 | 21.3699 |  |  | 0.51015 | -0.14135 | -43.5525 | 0.42314 | 0.24326 | -197.8512 | 12.3251 | -0.4886 | -0.10402 | -0.18241 | -0.03981 | 8.8292 | 9.0588 | 1.9781 | 21.7861 | 22.0216 | 22.2131 | 22.2832 | 22.1146 | 21.4495 | 20.2637 | 22.2098 | 22.386 | 22.4227 | 22.3726 | 22.0148 | 21.2533 | 22.297 | 17.4874 | 17.0762 | 16.2147 | 16.2215 | 16.2258 | 17.0667 | 16.806 | 22.3861 | 22.1561 | 21.7209 | 22.0942 | 21.8103 | 21.3204 | 21.9584 | 21.5451 | 20.9248 | 20.1157 | 20.3498 | 19.948 | 19.8672 | -0.019648 | 0.17578 | 20.7431 | 22.1035 | 22.4062 | 20.1267 | 21.6982 | 22.1481 | 21.9695 | 21.7368 | 21.3085 | 21.7999 | 21.4658 | 21.0651 | 20.1694 | 20.1739 | 20.4146 | 20.3202 | 20.113 |  | 20.2498 | 19.56 | 20.1417 | 19.748 | 20.1191 | 20.393 |  | 20.4575 |  |  | 20.3375 | 20.3643 | 20.6163 | [5 empty] | 21.972 | 20.3518 | 21.7048 | 22.0821 | 19.59 | 21.2005 | 21.8358 | 19.5543 | 20.0301 | 21.2136 |  | 19.7686 | 21.0148 | 18.9104 | 19.7731 | 20.8836 | 19.4637 | 20.0459 | 18.9925 | 20.1163 | 19.0699 | 20.2394 | 19.0133 | 20.1304 | 21.1619 | 19.5253 | 19.8684 | 21.0791 | 19.0017 | 19.8577 | 20.8886 | 18.916 | 20.1621 | 19.3202 | 19.9528 | 18.9611 | 20.1825 | -0.26595 | 20.9444 | 0.047965 | 0.015108 | -26.8894 | 3.0976 | -3.71 | -0.12 | 0.85288 | -0.4463 | -7.8342 | 0.7722 | 0.5862 | -16.7178 | 4.1726 | 0.42397 | 0.43571 | 0.42973 | 0.35548 | 0.46649 | 0.44126 | 0.4263
42838.4152 | -443 | 22.8916 | 22.8571 | 22.8388 | 22.7731 | 22.4133 | 21.7531 | 22.7241 | 21.8141 | 22.3721 | 22.3885 | 22.3687 | 22.0547 | 21.2798 | 22.2418 | 21.5647 | 21.7393 | 21.8791 | 21.0681 | 21.1592 | 21.3852 | 20.4675 | 20.6134 | 20.907 | 21.8907 | 21.6542 | 21.2961 | 20.3481 | 20.4406 | 20.4493 | 22.0379 | 21.6492 | 21.1665 | 21.9926 | 21.7322 | 21.3513 | 19.9368 | 20.3021 |  | 20.5652 | 20.1403 | 20.243 | 19.0905 |  | 16.9058 | 17.0102 | 16.774 | 17.105 | 17.212 | 17.6824 | 17.9873 | 15.6872 | 16.7967 | 16.2776 | 16.9106 | 17.8835 | 44.9203 | 48.0426 | 44.1139 | 21.3682 |  |  | 0.49307 | 0.038703 | -43.2666 | 0.28909 | -0.008412 | -197.8368 | 12.5571 | -0.36178 | -0.14897 | -0.020659 | -0.0076944 | 8.8286 | 9.0583 | 1.9791 | 21.7761 | 22.0065 | 22.2009 | 22.2715 | 22.1031 | 21.4426 | 20.2541 | 22.2055 | 22.3794 | 22.4102 | 22.3688 | 22.0067 | 21.2376 | 22.2925 | 17.4893 | 17.0668 | 16.2113 | 16.2306 | 16.2291 | 17.0686 | 16.8092 | 22.3819 | 22.1549 | 21.7195 | 22.0904 | 21.8129 | 21.3201 | 21.9565 | 21.5366 | 20.9203 | 20.1182 | 20.3422 | 19.9483 | 19.8681 | -0.019648 | 0.14002 | 20.7349 | 22.1012 | 22.3999 | 20.1329 | 21.6908 | 22.1394 | 21.9721 | 21.7269 | 21.2942 | 21.7979 | 21.4594 | 21.059 | 20.1643 | 20.1658 | 20.4012 | 20.3102 | 20.1207 |  | 20.2498 | 19.5584 | 20.1452 | 19.7548 | 20.1217 | 20.3937 |  | 20.4615 |  |  | 20.3449 | 20.3645 | 20.6225 | [5 empty] | 21.9654 | 20.3465 | 21.6941 | 22.0855 | 19.5889 | 21.2011 | 21.8291 | 19.5538 | 20.0409 | 21.211 |  | 19.7756 | 21.0111 | 18.9177 | 19.775 | 20.89 | 19.4713 | 20.0503 | 18.9961 | 20.1154 | 19.0786 | 20.2434 | 19.0111 | 20.1304 | 21.1549 | 19.5209 | 19.8721 | 21.0783 | 18.998 | 19.8538 | 20.8743 | 18.9144 | 20.1638 | 19.3182 | 19.953 | 18.9602 | 20.1783 | -0.24221 | 20.9452 | 0.047307 | 0.013736 | -26.9533 | 3.0977 | -19.55 | -0.07 | 0.83849 | 0.23354 | -7.8084 | 0.63826 | -0.109 | -16.7164 | 4.2115 | 0.42375 | 0.43587 | 0.42963 | 0.35549 | 0.46723 | 0.44189 | 0.42636
42838.4152 | -442 | 22.8926 | 22.8598 | 22.8471 | 22.7716 | 22.4133 | 21.7562 | 22.7198 | 21.82 | 22.3762 | 22.387 | 22.3702 | 22.059 | 21.2816 | 22.2421 | 21.5663 | 21.7456 | 21.8814 | 21.0764 | 21.1634 | 21.3885 | 20.4739 | 20.625 | 20.9205 | 21.8933 | 21.6637 | 21.302 | 20.3615 | 20.4491 | 20.4729 | 22.0426 | 21.6455 | 21.1717 | 21.9905 | 21.727 | 21.3512 | 19.9405 | 20.2935 |  | 20.57 | 20.1399 | 20.2377 | 19.0761 |  | 16.9133 | 17.0066 | 16.7716 | 17.0917 | 17.1876 | 17.6653 | 17.9486 | 15.6642 | 16.7991 | 16.3069 | 16.9084 | 17.8704 | 44.9162 | 48.0321 | 44.0814 | 21.3639 |  |  | 0.57521 | 0.040019 | -43.3783 | 0.45205 | 0.22158 | -197.8355 | 12.7674 | -0.11536 | -0.028318 | 0.10921 | 0.057926 | 8.8295 | 9.0591 | 1.9791 | 21.7802 | 22.009 | 22.2038 | 22.2882 | 22.1073 | 21.4351 | 20.2586 | 22.2031 | 22.389 | 22.4179 | 22.3732 | 22.0093 | 21.2534 | 22.2961 | 17.4839 | 17.0453 | 16.1924 | 16.241 | 16.2307 | 17.0647 | 16.8186 | 22.3852 | 22.1582 | 21.716 | 22.0932 | 21.8073 | 21.3189 | 21.9494 | 21.5387 | 20.9255 | 20.1193 | 20.3345 | 19.9398 | 19.8708 | -0.1958 | 0.052907 | 20.7362 | 22.1093 | 22.4069 | 20.1432 | 21.692 | 22.1514 | 21.9631 | 21.7261 | 21.303 | 21.8049 | 21.4667 | 21.0641 | 20.178 | 20.177 | 20.4114 | 20.3211 | 20.1126 |  | 20.2469 | 19.543 | 20.1489 | 19.7633 | 20.1216 | 20.3941 |  | 20.4567 |  |  | 20.3446 | 20.3564 | 20.6239 | [5 empty] | 21.9632 | 20.3486 | 21.698 | 22.0826 | 19.584 | 21.2046 | 21.8258 | 19.5506 | 20.0392 | 21.2158 |  | 19.7715 | 21.0086 | 18.9112 | 19.7753 | 20.8902 | 19.4741 | 20.042 | 18.9992 | 20.1072 | 19.0742 | 20.2398 | 19.003 | 20.1299 | 21.154 | 19.5238 | 19.8691 | 21.0841 | 19.007 | 19.8469 | 20.875 | 18.9111 | 20.1596 | 19.3225 | 19.9543 | 18.9607 | 20.1748 | -0.2526 | 20.9444 | 0.045771 | 0.013148 | -26.9209 | 3.0977 | -11.49 | -0.25 | 0.90568 | 0.23747 | -7.8184 | 0.79814 | 0.55942 | -16.7158 | 4.2465 | 0.42388 | 0.43642 | 0.42939 | 0.35564 | 0.47042 | 0.44241 | 0.42632
42838.4152 | -441 | 22.8878 | 22.8477 | 22.8405 | 22.7727 | 22.4106 | 21.7569 | 22.7155 | 21.8187 | 22.3722 | 22.3858 | 22.3662 | 22.0473 | 21.2725 | 22.242 | 21.5718 | 21.7477 | 21.8835 | 21.0716 | 21.1663 | 21.3906 | 20.4732 | 20.626 | 20.9204 | 21.9009 | 21.6669 | 21.302 | 20.3622 | 20.4562 | 20.4843 | 22.0359 | 21.649 | 21.177 | 21.9891 | 21.7249 | 21.352 | 19.9332 | 20.285 |  | 20.5718 | 20.1388 | 20.2339 | 19.0561 |  | 16.9191 | 17.0022 | 16.7706 | 17.0983 | 17.1795 | 17.6384 | 17.928 | 15.6617 | 16.7939 | 16.2959 | 16.9111 | 17.8837 | 44.903 | 48.0249 | 44.0755 | 21.367 |  |  | 0.56601 | -0.093377 | -43.2561 | 0.38568 | 0.056644 | -197.8578 | 12.6741 | -0.22772 | 0.06256 | -0.1929 | -0.0094304 | 8.8292 | 9.0591 | 1.979 | 21.7784 | 22.0168 | 22.2085 | 22.2763 | 22.1153 | 21.4453 | 20.2619 | 22.2073 | 22.3821 | 22.4172 | 22.3699 | 22.0066 | 21.2454 | 22.3015 | 17.4618 | 17.0831 | 16.1944 | 16.2597 | 16.2561 | 17.0576 | 16.8134 | 22.3816 | 22.1552 | 21.715 | 22.0895 | 21.8148 | 21.3168 | 21.951 | 21.5437 | 20.9235 | 20.1199 | 20.3301 | 19.941 | 19.8662 | -0.18617 | 0.086001 | 20.7427 | 22.1052 | 22.4096 | 20.1435 | 21.6958 | 22.1485 | 21.9658 | 21.7256 | 21.2954 | 21.8013 | 21.4671 | 21.0555 | 20.1882 | 20.1699 | 20.41 | 20.3181 | 20.1162 |  | 20.2551 | 19.5434 | 20.1502 | 19.7662 | 20.1212 | 20.3965 |  | 20.4553 |  |  | 20.3425 | 20.3543 | 20.624 | [5 empty] | 21.9538 | 20.3475 | 21.6935 | 22.0812 | 19.5792 | 21.1969 | 21.8165 | 19.5508 | 20.0386 | 21.2166 |  | 19.7727 | 21.0155 | 18.9164 | 19.7799 | 20.8831 | 19.4668 | 20.0392 | 19.0019 | 20.1039 | 19.072 | 20.2425 | 18.9922 | 20.1104 | 21.1456 | 19.5172 | 19.8657 | 21.0727 | 18.9934 | 19.8415 | 20.8679 | 18.9108 | 20.1526 | 19.3145 | 19.9502 | 18.9485 | 20.169 | -0.13629 | 20.9448 | 0.045882 | 0.013221 | -26.9287 | 3.0977 | -10.29 | 0.14 | 0.89842 | -0.36274 | -7.8073 | 0.73722 | 0.28283 | -16.716 | 4.2307 | 0.42405 | 0.43645 | 0.42929 | 0.35727 | 0.46961 | 0.44272 | 0.42647
42838.4152 | -440 | 22.8814 | 22.8493 | 22.8442 | 22.7676 | 22.4124 | 21.7544 | 22.7159 | 21.8159 | 22.3722 | 22.382 | 22.3679 | 22.0484 | 21.2747 | 22.2511 | 21.5791 | 21.757 | 21.89 | 21.0763 | 21.1718 | 21.3978 | 20.4837 | 20.6274 | 20.9267 | 21.9002 | 21.6699 | 21.309 | 20.3709 | 20.4629 | 20.498 | 22.0404 | 21.6499 | 21.1743 | 21.9874 | 21.7279 | 21.3569 | 19.9363 | 20.2899 |  | 20.5791 | 20.1397 | 20.2352 | 19.0462 |  | 16.9176 | 16.9972 | 16.7644 | 17.0925 | 17.1694 | 17.6237 | 17.9226 | 15.6373 | 16.8057 | 16.2305 | 16.9035 | 17.8789 | 44.8894 | 48.0159 | 44.0515 | 21.3691 |  |  | 0.58966 | -0.38579 | -43.0485 | 0.11561 | 0.15587 | -197.8657 | 12.724 | -0.24678 | -0.097596 | -0.36494 | 0.0020272 | 8.8283 | 9.0581 | 1.9785 | 21.7957 | 22.0211 | 22.2181 | 22.2836 | 22.1187 | 21.4479 | 20.2679 | 22.2135 | 22.386 | 22.415 | 22.3742 | 22.0094 | 21.2488 | 22.3052 | 17.4299 | 17.0764 | 16.2069 | 16.2799 | 16.2771 | 17.0643 | 16.8161 | 22.3863 | 22.1621 | 21.7209 | 22.0936 | 21.8144 | 21.3234 | 21.9608 | 21.5428 | 20.9345 | 20.1261 | 20.329 | 19.9354 | 19.8689 | -0.19128 | 0.10806 | 20.7344 | 22.1021 | 22.4068 | 20.1434 | 21.6974 | 22.1557 | 21.9696 | 21.7338 | 21.3035 | 21.8022 | 21.4677 | 21.0716 | 20.1866 | 20.1769 | 20.4109 | 20.3131 | 20.1226 |  | 20.2539 | 19.5325 | 20.1422 | 19.7732 | 20.1211 | 20.4029 |  | 20.4614 |  |  | 20.3467 | 20.3731 | 20.6373 | [5 empty] | 21.9611 | 20.3532 | 21.7002 | 22.0804 | 19.5897 | 21.195 | 21.8237 | 19.5507 | 20.0349 | 21.2104 |  | 19.7768 | 21.0067 | 18.913 | 19.7769 | 20.8725 | 19.4615 | 20.0418 | 19.0035 | 20.0989 | 19.0751 | 20.2336 | 18.9966 | 20.1184 | 21.1454 | 19.5183 | 19.876 | 21.087 | 18.9967 | 19.8443 | 20.8706 | 18.9209 | 20.1596 | 19.3179 | 19.9498 | 18.9505 | 20.1589 | -0.26057 | 20.9468 | 0.046637 | 0.014237 | -27.0145 | 3.0977 | -2.21 | -0.26 | 0.91703 | -0.73732 | -7.7885 | 0.40362 | 0.46916 | -16.7159 | 4.2389 | 0.42384 | 0.43649 | 0.4291 | 0.3616 | 0.46853 | 0.4431 | 0.42661
42838.4152 | -439 | 22.8798 | 22.8507 | 22.8391 | 22.7749 | 22.4099 | 21.7508 | 22.7139 | 21.8193 | 22.3653 | 22.3842 | 22.3769 | 22.0471 | 21.2694 | 22.2403 | 21.5735 | 21.7488 | 21.8833 | 21.0742 | 21.1695 | 21.3916 | 20.4812 | 20.6239 | 20.9223 | 21.899 | 21.6649 | 21.3101 | 20.3706 | 20.4581 | 20.503 | 22.037 | 21.6582 | 21.1723 | 21.9878 | 21.7318 | 21.3478 | 19.941 | 20.2868 |  | 20.5726 | 20.1363 | 20.24 | 19.0394 |  | 16.9103 | 16.983 | 16.7588 | 17.0797 | 17.1626 | 17.6054 | 17.8959 | 15.6074 | 16.8114 | 16.1158 | 16.912 | 17.8799 | 44.8791 | 48.01 | 44.0362 | 21.3661 |  |  | 0.49569 | -0.37791 | -42.9946 | 0.25952 | 0.12236 | -197.865 | 12.8206 | -0.24349 | -0.09565 | -0.17696 | 0.010013 | 8.8281 | 9.058 | 1.978 | 21.7835 | 22.0105 | 22.2113 | 22.276 | 22.1121 | 21.4422 | 20.2571 | 22.2117 | 22.3816 | 22.41 | 22.3691 | 21.9997 | 21.2437 | 22.2905 | 17.4027 | 17.0613 | 16.2203 | 16.2745 | 16.2868 | 17.0643 | 16.82 | 22.3783 | 22.1496 | 21.7161 | 22.0896 | 21.8104 | 21.3174 | 21.9484 | 21.5335 | 20.9234 | 20.1125 | 20.3085 | 19.9328 | 19.8523 | -0.13368 | 0.013345 | 20.7362 | 22.1102 | 22.409 | 20.1372 | 21.6972 | 22.1467 | 21.969 | 21.731 | 21.2976 | 21.8075 | 21.4601 | 21.0662 | 20.186 | 20.1811 | 20.3983 | 20.3033 | 20.1185 |  | 20.2539 | 19.5245 | 20.1419 | 19.7719 | 20.1193 | 20.3972 |  | 20.4574 |  |  | 20.3383 | 20.3737 | 20.6359 | [5 empty] | 21.964 | 20.3526 | 21.6978 | 22.0772 | 19.5899 | 21.1962 | 21.8233 | 19.5488 | 20.0356 | 21.2169 |  | 19.7786 | 21.0022 | 18.913 | 19.7746 | 20.8738 | 19.4675 | 20.0503 | 18.9965 | 20.1001 | 19.0785 | 20.2363 | 19.0006 | 20.1203 | 21.1436 | 19.5194 | 19.8781 | 21.0873 | 18.9978 | 19.8433 | 20.8636 | 18.9255 | 20.1531 | 19.3145 | 19.9462 | 18.9491 | 20.1545 | -0.27208 | 20.9453 | 0.047129 | 0.014745 | -26.9961 | 3.0977 | -5.07 | -0.17 | 0.8408 | -0.72972 | -7.7835 | 0.60471 | 0.41567 | -16.7153 | 4.2549 | 0.42395 | 0.4367 | 0.42907 | 0.36462 | 0.4675 | 0.44345 | 0.42661
42838.4152 | -438 | 22.8976 | 22.8553 | 22.8383 | 22.771 | 22.4123 | 21.7594 | 22.7201 | 21.818 | 22.368 | 22.3861 | 22.3706 | 22.0577 | 21.2796 | 22.2483 | 21.5776 | 21.7502 | 21.8805 | 21.0769 | 21.1748 | 21.393 | 20.4827 | 20.624 | 20.9209 | 21.8974 | 21.6631 | 21.3069 | 20.3723 | 20.4548 | 20.4994 | 22.0319 | 21.6511 | 21.1732 | 21.9896 | 21.7286 | 21.3526 | 19.928 | 20.2791 |  | 20.5713 | 20.1426 | 20.2381 | 19.0475 |  | 16.9123 | 16.9822 | 16.7565 | 17.0703 | 17.1554 | 17.5962 | 17.8616 | 15.5728 | 16.8109 | 16.0864 | 16.9106 | 17.8814 | 44.8569 | 48.0034 | 44.033 | 21.3709 |  |  | 0.61003 | -0.25897 | -42.6838 | 0.33246 | -0.07938 | -197.848 | 12.8324 | -0.066072 | 0.027337 | -0.27368 | -0.11133 | 8.8289 | 9.0587 | 1.9788 | 21.788 | 22.0133 | 22.2087 | 22.2724 | 22.1129 | 21.4412 | 20.2618 | 22.2075 | 22.3829 | 22.4118 | 22.3715 | 22.0066 | 21.2447 | 22.2942 | 17.3802 | 17.0492 | 16.239 | 16.2764 | 16.2895 | 17.0624 | 16.8277 | 22.3824 | 22.1555 | 21.7162 | 22.0856 | 21.8142 | 21.3245 | 21.9526 | 21.5455 | 20.9217 | 20.1164 | 20.3128 | 19.9315 | 19.8584 | 0.019279 | 0.0002212 | 20.7484 | 22.1197 | 22.4145 | 20.1418 | 21.7047 | 22.147 | 21.9714 | 21.7312 | 21.31 | 21.8022 | 21.4619 | 21.0703 | 20.2035 | 20.1817 | 20.4084 | 20.3133 | 20.092 |  | 20.2418 | 19.5286 | 20.1422 | 19.7773 | 20.1127 | 20.387 |  | 20.4615 |  |  | 20.3258 | 20.376 | 20.6306 | [5 empty] | 21.9614 | 20.352 | 21.6971 | 22.0791 | 19.5869 | 21.1913 | 21.8232 | 19.5493 | 20.0328 | 21.2151 |  | 19.7741 | 21.0006 | 18.9095 | 19.7686 | 20.8672 | 19.4599 | 20.044 | 18.9996 | 20.0987 | 19.0731 | 20.2264 | 18.9958 | 20.1144 | 21.1452 | 19.5215 | 19.8772 | 21.0807 | 18.9944 | 19.8386 | 20.8643 | 18.926 | 20.1519 | 19.3189 | 19.9445 | 18.9426 | 20.1486 | -0.28858 | 20.9458 | 0.048346 | 0.016938 | -27.1451 | 3.0977 | 4.23 | -0.08 | 0.93274 | -0.60407 | -7.7553 | 0.68444 | -0.3348 | -16.7144 | 4.2568 | 0.42428 | 0.43659 | 0.4287 | 0.36689 | 0.46632 | 0.44279 | 0.42657
42838.4152 | -437 | 22.8943 | 22.8549 | 22.843 | 22.7729 | 22.4077 | 21.7489 | 22.7157 | 21.8227 | 22.3758 | 22.38 | 22.3701 | 22.0569 | 21.2762 | 22.2383 | 21.5713 | 21.7446 | 21.8753 | 21.067 | 21.1721 | 21.3942 | 20.4782 | 20.6187 | 20.9181 | 21.8877 | 21.6539 | 21.2973 | 20.3637 | 20.4418 | 20.4963 | 22.0472 | 21.6376 | 21.1824 | 21.9885 | 21.7321 | 21.3544 | 19.9349 | 20.2743 |  | 20.565 | 20.144 | 20.2258 | 19.0594 |  | 16.9082 | 16.9786 | 16.745 | 17.0637 | 17.135 | 17.5653 | 17.8472 | 15.5316 | 16.8134 | 16.1062 | 16.911 | 17.8876 | 44.8542 | 48.0023 | 44.0268 | 21.3747 |  |  | 0.67115 | -0.55598 | -42.4571 | 0.20958 | 0.12564 | -197.8663 | 13.0223 | 0.03118 | 0.035121 | -0.195 | -0.1707 | 8.8277 | 9.0576 | 1.9793 | 21.7879 | 22.0155 | 22.2073 | 22.2824 | 22.1067 | 21.4443 | 20.2632 | 22.2065 | 22.3842 | 22.4143 | 22.3733 | 22.0026 | 21.2481 | 22.2966 | 17.3689 | 17.0465 | 16.2669 | 16.2832 | 16.2726 | 17.0605 | 16.8264 | 22.3784 | 22.1537 | 21.7175 | 22.0871 | 21.8075 | 21.3213 | 21.948 | 21.545 | 20.925 | 20.116 | 20.3196 | 19.9272 | 19.8598 | 0.10401 | -0.1333 | 20.7393 | 22.1171 | 22.4126 | 20.1494 | 21.6966 | 22.1449 | 21.9678 | 21.7397 | 21.3072 | 21.8077 | 21.4681 | 21.0737 | 20.1958 | 20.1956 | 20.3992 | 20.31 | 20.0931 |  | 20.2487 | 19.5283 | 20.1348 | 19.7842 | 20.1134 | 20.3962 |  | 20.4566 |  |  | 20.3144 | 20.3785 | 20.6401 | [5 empty] | 21.9695 | 20.3563 | 21.6995 | 22.0854 | 19.589 | 21.1917 | 21.8281 | 19.5458 | 20.0399 | 21.2146 |  | 19.7821 | 21.0064 | 18.9128 | 19.7724 | 20.8671 | 19.4577 | 20.0413 | 19.0029 | 20.0935 | 19.0744 | 20.227 | 18.9901 | 20.1178 | 21.1467 | 19.5256 | 19.8836 | 21.0848 | 18.9939 | 19.8415 | 20.869 | 18.9337 | 20.1536 | 19.3198 | 19.9493 | 18.9439 | 20.1454 | -0.14427 | 20.9475 | 0.048825 | 0.016545 | -26.9789 | 3.0977 | 0.66 | -0.15 | 0.97834 | -0.8851 | -7.7346 | 0.54342 | 0.42118 | -16.7143 | 4.2879 | 0.42448 | 0.43636 | 0.42853 | 0.36793 | 0.46306 | 0.44269 | 0.42652
42838.4152 | -436 | 22.8878 | 22.8533 | 22.846 | 22.7719 | 22.4151 | 21.7588 | 22.7201 | 21.825 | 22.3701 | 22.3882 | 22.3694 | 22.0538 | 21.2693 | 22.245 | 21.5675 | 21.7454 | 21.8848 | 21.0748 | 21.1733 | 21.3965 | 20.4778 | 20.6243 | 20.9188 | 21.8952 | 21.6595 | 21.2993 | 20.3753 | 20.4541 | 20.5041 | 22.0369 | 21.6497 | 21.1793 | 21.9916 | 21.7381 | 21.3498 | 19.9396 | 20.2682 |  | 20.5768 | 20.1466 | 20.2299 | 19.0656 |  | 16.9103 | 16.9772 | 16.7468 | 17.0653 | 17.1338 | 17.5497 | 17.846 | 15.5173 | 16.8205 | 16.1285 | 16.9167 | 17.8744 | 44.8497 | 47.9893 | 44.0113 | 21.3663 |  |  | 0.63172 | -0.211 | -42.1022 | 0.095238 | 0.096072 | -197.8539 | 13.0861 | -0.010876 | 0.07482 | -0.16647 | -0.19588 | 8.8288 | 9.0586 | 1.9788 | 21.7869 | 22.0102 | 22.2005 | 22.2756 | 22.1074 | 21.4446 | 20.2553 | 22.2044 | 22.384 | 22.4127 | 22.3721 | 22.0023 | 21.2538 | 22.2959 | 17.3603 | 17.0429 | 16.2473 | 16.2846 | 16.2749 | 17.0624 | 16.8368 | 22.382 | 22.1466 | 21.7172 | 22.0883 | 21.8125 | 21.3138 | 21.9516 | 21.5436 | 20.919 | 20.1142 | 20.3137 | 19.9272 | 19.8572 | 0.041298 | -0.080043 | 20.7491 | 22.116 | 22.4229 | 20.1536 | 21.7069 | 22.1596 | 21.9744 | 21.7423 | 21.3085 | 21.8098 | 21.4752 | 21.0738 | 20.2077 | 20.1953 | 20.4013 | 20.3066 | 20.0821 |  | 20.2484 | 19.5164 | 20.1366 | 19.7782 | 20.1087 | 20.3947 |  | 20.4499 |  |  | 20.3114 | 20.3808 | 20.642 | [5 empty] | 21.9682 | 20.3523 | 21.6986 | 22.081 | 19.5824 | 21.1953 | 21.8204 | 19.5422 | 20.0408 | 21.2113 |  | 19.7856 | 21.0078 | 18.9145 | 19.7727 | 20.8649 | 19.4589 | 20.0486 | 19.0038 | 20.0955 | 19.0749 | 20.2258 | 18.9783 | 20.106 | 21.1362 | 19.5225 | 19.8878 | 21.0791 | 18.9941 | 19.8326 | 20.8639 | 18.9285 | 20.1493 | 19.3163 | 19.9471 | 18.9379 | 20.1353 | -0.15169 | 20.9459 | 0.048671 | 0.016582 | -26.973 | 3.0976 | 4.71 | -0.23 | 0.94918 | -0.54526 | -7.7022 | 0.36632 | 0.36829 | -16.7133 | 4.2983 | 0.42478 | 0.43675 | 0.42854 | 0.3691 | 0.46645 | 0.44267 | 0.42653
42838.4152 | -435 | 22.8774 | 22.8524 | 22.8345 | 22.765 | 22.4045 | 21.7509 | 22.712 | 21.8152 | 22.3614 | 22.3788 | 22.363 | 22.045 | 21.2692 | 22.239 | 21.5646 | 21.7377 | 21.8806 | 21.0674 | 21.1698 | 21.3903 | 20.4638 | 20.6141 | 20.9131 | 21.8891 | 21.6623 | 21.2976 | 20.3683 | 20.4451 | 20.5026 | 22.0392 | 21.6501 | 21.1707 | 21.9924 | 21.7283 | 21.3506 | 19.9321 | 20.2635 |  | 20.5644 | 20.1386 | 20.2258 | 19.0671 |  | 16.9062 | 16.9737 | 16.7353 | 17.0445 | 17.127 | 17.5334 | 17.827 | 15.4846 | 16.8205 | 16.165 | 16.913 | 17.8862 | 44.854 | 47.983 | 44.0042 | 21.3737 |  |  | 0.53907 | -0.33059 | -41.8137 | 0.040042 | 0.34052 | -197.8322 | 13.4508 | -0.075272 | 0.10051 | -0.1029 | 0.055149 | 8.8285 | 9.0584 | 1.9787 | 21.7841 | 22.0056 | 22.2139 | 22.2721 | 22.1113 | 21.44 | 20.2602 | 22.2024 | 22.3827 | 22.412 | 22.3691 | 22.014 | 21.2502 | 22.2918 | 17.3373 | 17.0406 | 16.2268 | 16.2716 | 16.2622 | 17.0682 | 16.8388 | 22.3875 | 22.151 | 21.715 | 22.0822 | 21.8062 | 21.324 | 21.9467 | 21.5396 | 20.9227 | 20.1106 | 20.305 | 19.9223 | 19.8592 | 0.019279 | -0.081945 | 20.7372 | 22.1076 | 22.4096 | 20.1405 | 21.6941 | 22.1469 | 21.9711 | 21.7355 | 21.3098 | 21.8088 | 21.4726 | 21.0686 | 20.2144 | 20.2049 | 20.3924 | 20.2913 | 20.0888 |  | 20.2531 | 19.536 | 20.1382 | 19.7894 | 20.121 | 20.4092 |  | 20.4616 |  |  | 20.3208 | 20.392 | 20.6387 | [5 empty] | 21.9663 | 20.3506 | 21.6962 | 22.0766 | 19.5872 | 21.2021 | 21.8186 | 19.5386 | 20.0415 | 21.2103 |  | 19.7811 | 21.0005 | 18.9101 | 19.7751 | 20.8667 | 19.4628 | 20.0441 | 19.0005 | 20.0835 | 19.074 | 20.2224 | 18.9734 | 20.108 | 21.1333 | 19.521 | 19.8888 | 21.0738 | 18.9982 | 19.8308 | 20.8591 | 18.9366 | 20.1444 | 19.3252 | 19.9392 | 18.9332 | 20.135 | -0.22496 | 20.9456 | 0.048395 | 0.015863 | -26.9748 | 3.0977 | -9.38 | -0.28 | 0.87681 | -0.6825 | -7.6757 | 0.23753 | 0.69334 | -16.7119 | 4.3576 | 0.42475 | 0.43626 | 0.42864 | 0.37233 | 0.46896 | 0.44238 | 0.42635
42838.4153 | -434 | 22.8811 | 22.8565 | 22.8368 | 22.7664 | 22.4088 | 21.7473 | 22.7151 | 21.8184 | 22.3661 | 22.3773 | 22.3661 | 22.0519 | 21.2676 | 22.2394 | 21.565 | 21.7404 | 21.8742 | 21.0624 | 21.1587 | 21.3841 | 20.4647 | 20.6091 | 20.9084 | 21.8887 | 21.6551 | 21.2886 | 20.363 | 20.4332 | 20.5064 | 22.0377 | 21.6462 | 21.1672 | 21.9842 | 21.7293 | 21.3525 | 19.9257 | 20.2623 |  | 20.5681 | 20.1338 | 20.2199 | 19.0685 |  | 16.9031 | 16.9541 | 16.7276 | 17.04 | 17.1084 | 17.517 | 17.8284 | 15.4552 | 16.8217 | 16.1739 | 16.9148 | 17.8826 | 44.8287 | 47.9768 | 43.9911 | 21.3614 |  |  | 0.54958 | -0.57307 | -41.3262 | 0.22666 | 0.23669 | -197.8466 | 13.4659 | 0.09032 | 0.0010664 | -0.1029 | 0.013311 | 8.829 | 9.0586 | 1.9785 | 21.7889 | 22.0257 | 22.212 | 22.2818 | 22.1195 | 21.4489 | 20.2637 | 22.2172 | 22.3876 | 22.4312 | 22.3799 | 22.0154 | 21.251 | 22.2932 | 17.2889 | 17.094 | 16.2086 | 16.2523 | 16.2504 | 17.066 | 16.8357 | 22.3855 | 22.1579 | 21.7137 | 22.0939 | 21.8125 | 21.3233 | 21.9479 | 21.5413 | 20.9246 | 20.114 | 20.3008 | 19.9169 | 19.8668 | -0.0027402 | -0.071294 | 20.7306 | 22.1082 | 22.411 | 20.1414 | 21.6951 | 22.1415 | 21.9662 | 21.732 | 21.2971 | 21.814 | 21.4669 | 21.069 | 20.217 | 20.1898 | 20.3917 | 20.2969 | 20.0962 |  | 20.2484 | 19.5433 | 20.1441 | 19.7864 | 20.1182 | 20.4059 |  | 20.4589 |  |  | 20.3105 | 20.3859 | 20.636 | [5 empty] | 21.9645 | 20.3462 | 21.6929 | 22.0818 | 19.5872 | 21.1971 | 21.8196 | 19.5343 | 20.0452 | 21.2122 |  | 19.786 | 20.9998 | 18.9166 | 19.7826 | 20.871 | 19.4664 | 20.0402 | 19.006 | 20.089 | 19.0755 | 20.2235 | 18.9857 | 20.1118 | 21.1447 | 19.5274 | 19.8936 | 21.0782 | 18.9971 | 19.8337 | 20.8658 | 18.9526 | 20.146 | 19.3312 | 19.9505 | 18.9448 | 20.1391 | -0.15707 | 20.9459 | 0.047602 | 0.015928 | -27.0085 | 3.0977 | -9.46 | -0.11 | 0.88532 | -0.89856 | -7.6306 | 0.56511 | 0.57804 | -16.712 | 4.36 | 0.42439 | 0.43625 | 0.42863 | 0.37746 | 0.47063 | 0.44213 | 0.42625
42838.4153 | -433 | 22.8917 | 22.8638 | 22.839 | 22.7725 | 22.4162 | 21.7472 | 22.7142 | 21.8206 | 22.3698 | 22.3843 | 22.369 | 22.0467 | 21.2718 | 22.2411 | 21.5763 | 21.7532 | 21.8861 | 21.0767 | 21.17 | 21.392 | 20.4833 | 20.6258 | 20.9229 | 21.901 | 21.6722 | 21.3046 | 20.3754 | 20.4442 | 20.5099 | 22.0429 | 21.6465 | 21.1743 | 21.9844 | 21.7272 | 21.3538 | 19.9322 | 20.2602 |  | 20.5618 | 20.1362 | 20.218 | 19.076 |  | 16.8942 | 16.9473 | 16.726 | 17.0332 | 17.1012 | 17.5047 | 17.8451 | 15.4578 | 16.8272 | 16.1578 | 16.9132 | 17.885 | 44.8191 | 47.9712 | 43.983 | 21.3663 |  |  | 0.63369 | -0.43048 | -41.1671 | 0.24966 | 0.12367 | -197.825 | 12.9395 | -0.020732 | 0.11199 | -0.14297 | -0.0066528 | 8.8282 | 9.058 | 1.9782 | 21.7892 | 22.0181 | 22.211 | 22.2806 | 22.1153 | 21.4452 | 20.267 | 22.2121 | 22.3881 | 22.4247 | 22.3693 | 22.0064 | 21.2549 | 22.2985 | 17.253 | 17.1045 | 16.2006 | 16.2323 | 16.2333 | 17.055 | 16.8276 | 22.3809 | 22.1495 | 21.7164 | 22.0887 | 21.8101 | 21.31 | 21.9465 | 21.5407 | 20.9236 | 20.117 | 20.2961 | 19.9152 | 19.8657 | -0.0021504 | -0.22783 | 20.726 | 22.1039 | 22.4181 | 20.138 | 21.6959 | 22.1548 | 21.9712 | 21.735 | 21.3056 | 21.8066 | 21.4656 | 21.0667 | 20.2207 | 20.1911 | 20.3919 | 20.2967 | 20.1088 |  | 20.246 | 19.5515 | 20.1405 | 19.7779 | 20.1152 | 20.3985 |  | 20.4513 |  |  | 20.3064 | 20.3926 | 20.643 | [5 empty] | 21.9621 | 20.3541 | 21.6944 | 22.0836 | 19.5891 | 21.2001 | 21.8164 | 19.5349 | 20.0469 | 21.1996 |  | 19.7863 | 21.0028 | 18.9202 | 19.7836 | 20.8708 | 19.4593 | 20.0499 | 19.0029 | 20.0864 | 19.0767 | 20.2188 | 18.9843 | 20.1063 | 21.1398 | 19.5321 | 19.8978 | 21.0786 | 19.0006 | 19.8399 | 20.8619 | 18.9497 | 20.1396 | 19.3298 | 19.9533 | 18.9421 | 20.144 | -0.24592 | 20.946 | 0.047086 | 0.015754 | -26.9998 | 3.0977 | -13.61 | -0.07 | 0.95067 | -0.77878 | -7.6158 | 0.59308 | 0.41782 | -16.7108 | 4.2738 | 0.42396 | 0.4359 | 0.42877 | 0.38015 | 0.47057 | 0.44214 | 0.42639
42838.4153 | -432 | 22.8839 | 22.8492 | 22.8431 | 22.7745 | 22.4093 | 21.7491 | 22.7194 | 21.8201 | 22.3712 | 22.3866 | 22.3671 | 22.049 | 21.2726 | 22.2457 | 21.575 | 21.7463 | 21.8833 | 21.0764 | 21.1746 | 21.3972 | 20.4814 | 20.6298 | 20.9248 | 21.8988 | 21.6568 | 21.301 | 20.3815 | 20.4265 | 20.516 | 22.0381 | 21.6463 | 21.1693 | 21.9808 | 21.732 | 21.3502 | 19.9335 | 20.2596 |  | 20.5598 | 20.1316 | 20.2155 | 19.0832 |  | 16.893 | 16.9481 | 16.7194 | 17.0257 | 17.1013 | 17.5185 | 17.8696 | 15.4513 | 16.8242 | 16.1696 | 16.9131 | 17.8891 | 44.8205 | 47.9645 | 43.9711 | 21.3718 |  |  | 0.42473 | -0.5803 | -41.1606 | 0.29434 | 0.1217 | -197.8223 | 13.387 | -0.043732 | -0.11297 | -0.33872 | 0.0087976 | 8.8292 | 9.0588 | 1.979 | 21.7839 | 22.0094 | 22.2042 | 22.2723 | 22.1041 | 21.4406 | 20.26 | 22.2007 | 22.3785 | 22.4171 | 22.3728 | 22.0072 | 21.2505 | 22.2895 | 17.2361 | 17.0695 | 16.1962 | 16.2293 | 16.2364 | 17.0622 | 16.8408 | 22.3891 | 22.1569 | 21.7285 | 22.0909 | 21.8183 | 21.3207 | 21.9525 | 21.5439 | 20.9289 | 20.1208 | 20.3015 | 19.9229 | 19.8729 | -0.026136 | -0.21965 | 20.7353 | 22.1024 | 22.4144 | 20.1336 | 21.7012 | 22.1561 | 21.9673 | 21.7463 | 21.3102 | 21.8201 | 21.4761 | 21.0659 | 20.2224 | 20.1991 | 20.3985 | 20.2985 | 20.1355 |  | 20.2569 | 19.5756 | 20.1515 | 19.7941 | 20.1252 | 20.4102 |  | 20.4641 |  |  | 20.3025 | 20.3933 | 20.64 | [5 empty] | 21.9643 | 20.3513 | 21.6992 | 22.0771 | 19.5884 | 21.1931 | 21.8192 | 19.5276 | 20.0474 | 21.2201 |  | 19.7854 | 21.0031 | 18.9271 | 19.7839 | 20.8678 | 19.4643 | 20.0491 | 19.0119 | 20.0874 | 19.0872 | 20.2229 | 18.9832 | 20.1004 | 21.1478 | 19.5315 | 19.9007 | 21.0804 | 18.9996 | 19.8362 | 20.8589 | 18.9548 | 20.1469 | 19.3361 | 19.9452 | 18.9476 | 20.1416 | -0.2244 | 20.9446 | 0.046932 | 0.01484 | -26.961 | 3.0977 | -8.81 | 0.04 | 0.7783 | -0.9042 | -7.6152 | 0.64397 | 0.41448 | -16.711 | 4.3472 | 0.42358 | 0.4356 | 0.42865 | 0.38288 | 0.4726 | 0.44198 | 0.42632
42838.4153 | -431 | 22.8827 | 22.8403 | 22.8265 | 22.767 | 22.4058 | 21.7463 | 22.7147 | 21.81 | 22.3608 | 22.3789 | 22.3606 | 22.0378 | 21.2704 | 22.2421 | 21.5641 | 21.7579 | 21.8839 | 21.0763 | 21.1677 | 21.3931 | 20.4723 | 20.6254 | 20.9216 | 21.9004 | 21.6655 | 21.2954 | 20.3756 | 20.4401 | 20.5082 | 22.0377 | 21.6438 | 21.1708 | 21.9845 | 21.7224 | 21.3539 | 19.9279 | 20.2558 |  | 20.5606 | 20.1388 | 20.2203 | 19.0808 |  | 16.8833 | 16.94 | 16.7105 | 17.0232 | 17.1093 | 17.5571 | 17.9086 | 15.4445 | 16.8308 | 16.1703 | 16.9114 | 17.8798 | 44.8185 | 47.9522 | 43.9567 | 21.3621 |  |  | 0.58178 | -0.41076 | -40.8964 | 0.341 | 0.24261 | -197.8388 | 12.8738 | -0.04636 | 0.06256 | -0.097446 | -0.012382 | 8.829 | 9.0588 | 1.9792 | 21.7867 | 22.0123 | 22.2074 | 22.2727 | 22.1039 | 21.4476 | 20.2622 | 22.2042 | 22.3833 | 22.4162 | 22.3661 | 22.0052 | 21.2505 | 22.291 | 17.2121 | 17.0571 | 16.1929 | 16.2227 | 16.2284 | 17.062 | 16.8294 | 22.3868 | 22.1582 | 21.722 | 22.0848 | 21.8065 | 21.3196 | 21.9559 | 21.5364 | 20.9213 | 20.1186 | 20.2874 | 19.9163 | 19.8598 | 0.071771 | -0.078712 | 20.7307 | 22.1057 | 22.4057 | 20.1247 | 21.6996 | 22.1533 | 21.9715 | 21.7373 | 21.2996 | 21.7999 | 21.4685 | 21.0738 | 20.216 | 20.2032 | 20.3858 | 20.2876 | 20.1362 |  | 20.2503 | 19.5694 | 20.139 | 19.7957 | 20.1172 | 20.4105 |  | 20.4572 |  |  | 20.3027 | 20.3924 | 20.6367 | [5 empty] | 21.9588 | 20.3288 | 21.6808 | 22.0732 | 19.5672 | 21.1971 | 21.8083 | 19.5317 | 20.0411 | 21.2114 |  | 19.7884 | 21.0021 | 18.9211 | 19.7787 | 20.8533 | 19.4604 | 20.0379 | 19.0054 | 20.0918 | 19.0817 | 20.2215 | 18.9833 | 20.0987 | 21.14 | 19.526 | 19.886 | 21.0701 | 18.9925 | 19.826 | 20.8515 | 18.9553 | 20.1391 | 19.3233 | 19.9393 | 18.9299 | 20.1334 | -0.093439 | 20.946 | 0.046435 | 0.013308 | -27.0104 | 3.0977 | -3.86 | 0.03 | 0.91089 | -0.76073 | -7.5906 | 0.69312 | 0.58526 | -16.7129 | 4.2633 | 0.42334 | 0.43535 | 0.42834 | 0.38552 | 0.47164 | 0.44186 | 0.42661
42838.4153 | -430 | 22.8869 | 22.8546 | 22.8446 | 22.7763 | 22.4071 | 21.7543 | 22.7154 | 21.8221 | 22.3738 | 22.3814 | 22.38 | 22.0538 | 21.2712 | 22.2409 | 21.5777 | 21.75 | 21.8848 | 21.0756 | 21.1702 | 21.3921 | 20.4763 | 20.6233 | 20.9208 | 21.8966 | 21.6582 | 21.2954 | 20.3798 | 20.4374 | 20.4964 | 22.0303 | 21.6474 | 21.1693 | 21.9805 | 21.7239 | 21.3529 | 19.9281 | 20.2523 |  | 20.5578 | 20.1267 | 20.2188 | 19.0923 |  | 16.8762 | 16.9368 | 16.7133 | 17.0191 | 17.1055 | 17.5822 | 17.9417 | 15.4792 | 16.8393 | 16.1318 | 16.9183 | 17.8823 | 44.8173 | 47.949 | 43.9449 | 21.3675 |  |  | 0.50161 | -0.50802 | -40.5534 | 0.59267 | 0.43646 | -197.8519 | 13.2628 | 0.027896 | 0.14663 | -0.26403 | 0.04942 | 8.8286 | 9.0585 | 1.979 | 21.8012 | 22.0169 | 22.2092 | 22.2807 | 22.1169 | 21.4474 | 20.2671 | 22.2087 | 22.3928 | 22.4188 | 22.3763 | 22.002 | 21.2528 | 22.2939 | 17.1943 | 17.0343 | 16.1794 | 16.2177 | 16.2428 | 17.064 | 16.8321 | 22.3784 | 22.1595 | 21.7209 | 22.0924 | 21.8111 | 21.3243 | 21.9513 | 21.5442 | 20.9213 | 20.1191 | 20.2859 | 19.9202 | 19.8754 | 0.1624 | -0.17971 | 20.7259 | 22.1071 | 22.4102 | 20.1342 | 21.7001 | 22.148 | 21.9664 | 21.7295 | 21.3046 | 21.7995 | 21.4689 | 21.0587 | 20.2188 | 20.201 | 20.3719 | 20.2835 | 20.1402 |  | 20.2415 | 19.5645 | 20.1358 | 19.7969 | 20.1148 | 20.3987 |  | 20.4504 |  |  | 20.2994 | 20.3954 | 20.6468 | [5 empty] | 21.9624 | 20.3358 | 21.6909 | 22.0847 | 19.5662 | 21.1919 | 21.8214 | 19.5284 | 20.0403 | 21.2111 |  | 19.7848 | 21.005 | 18.9255 | 19.782 | 20.8657 | 19.4616 | 20.0457 | 19.0152 | 20.0963 | 19.0817 | 20.224 | 18.969 | 20.0884 | 21.1391 | 19.5254 | 19.885 | 21.076 | 18.9954 | 19.8248 | 20.8439 | 18.953 | 20.1185 | 19.3178 | 19.932 | 18.9334 | 20.1333 | -0.23052 | 20.9462 | 0.045876 | 0.013293 | -27.027 | 3.0976 | -11.71 | 0.06 | 0.84579 | -0.846 | -7.5587 | 0.91377 | 0.78503 | -16.7141 | 4.3274 | 0.42293 | 0.43539 | 0.42823 | 0.38774 | 0.47345 | 0.44154 | 0.42619
42838.4153 | -429 | 22.8915 | 22.858 | 22.8481 | 22.7727 | 22.4164 | 21.7512 | 22.7201 | 21.8278 | 22.3801 | 22.3866 | 22.3765 | 22.053 | 21.2759 | 22.2412 | 21.5699 | 21.7409 | 21.8802 | 21.071 | 21.1673 | 21.3828 | 20.472 | 20.6146 | 20.9136 | 21.8896 | 21.6526 | 21.2936 | 20.3692 | 20.4279 | 20.4839 | 22.044 | 21.6534 | 21.173 | 21.9883 | 21.7283 | 21.3552 | 19.9373 | 20.2558 |  | 20.5637 | 20.1325 | 20.2224 | 19.1077 |  | 16.8824 | 16.9257 | 16.6999 | 17.0088 | 17.0842 | 17.5784 | 17.957 | 15.5569 | 16.8404 | 16.0898 | 16.9219 | 17.8862 | 44.828 | 47.9485 | 43.9465 | 21.3703 |  |  | 0.63041 | -0.016493 | -40.3405 | 0.44088 | 0.27612 | -197.8158 | 13.4514 | 0.11989 | 0.15694 | -0.2185 | -0.010125 | 8.8289 | 9.0585 | 1.9783 | 21.7942 | 22.0128 | 22.2131 | 22.2757 | 22.1103 | 21.4438 | 20.2623 | 22.2124 | 22.3849 | 22.4125 | 22.3753 | 22.0063 | 21.2459 | 22.2906 | 17.1898 | 17.0398 | 16.1946 | 16.2292 | 16.2561 | 17.0659 | 16.8313 | 22.3827 | 22.1579 | 21.7157 | 22.0944 | 21.8078 | 21.321 | 21.9531 | 21.548 | 20.9238 | 20.1176 | 20.2849 | 19.9174 | 19.8767 | 0.080815 | -0.11447 | 20.7319 | 22.1113 | 22.4121 | 20.1343 | 21.6966 | 22.1529 | 21.97 | 21.7453 | 21.307 | 21.8148 | 21.4774 | 21.0603 | 20.2276 | 20.2033 | 20.3807 | 20.281 | 20.1504 |  | 20.2495 | 19.586 | 20.1429 | 19.7987 | 20.1188 | 20.4014 |  | 20.4554 |  |  | 20.3063 | 20.3979 | 20.6459 | [5 empty] | 21.9662 | 20.3288 | 21.6861 | 22.0712 | 19.5605 | 21.1889 | 21.8124 | 19.5231 | 20.0441 | 21.2056 |  | 19.7801 | 21.0017 | 18.922 | 19.7744 | 20.8604 | 19.4596 | 20.0442 | 19.0194 | 20.0983 | 19.0826 | 20.2145 | 18.9693 | 20.0915 | 21.1335 | 19.5194 | 19.8928 | 21.0742 | 18.9892 | 19.827 | 20.8511 | 18.9657 | 20.1239 | 19.3258 | 19.9449 | 18.9319 | 20.1263 | -0.12108 | 20.9464 | 0.046693 | 0.013569 | -27.0272 | 3.0977 | 6.94 | -0.11 | 0.94816 | -0.15243 | -7.5386 | 0.7881 | 0.6244 | -16.7125 | 4.3581 | 0.42292 | 0.43502 | 0.42831 | 0.38846 | 0.47167 | 0.44142 | 0.4261
42838.4153 | -428 | 22.8894 | 22.8489 | 22.8448 | 22.7679 | 22.41 | 21.7526 | 22.7117 | 21.821 | 22.3746 | 22.382 | 22.3676 | 22.053 | 21.2741 | 22.2391 | 21.5722 | 21.7573 | 21.8878 | 21.0831 | 21.1848 | 21.3961 | 20.4783 | 20.6227 | 20.9238 | 21.8985 | 21.6598 | 21.3061 | 20.3762 | 20.436 | 20.4804 | 22.0416 | 21.654 | 21.1763 | 21.9961 | 21.7324 | 21.3505 | 19.9428 | 20.2477 |  | 20.5646 | 20.1355 | 20.222 | 19.1114 |  | 16.8834 | 16.9177 | 16.7009 | 16.9877 | 17.0687 | 17.5557 | 17.9801 | 15.5517 | 16.8392 | 16.0389 | 16.921 | 17.8848 | 44.8359 | 47.9441 | 43.9449 | 21.3708 |  |  | 0.66326 | -0.10586 | -39.9081 | 0.28317 | 0.15521 | -197.8 | 13.7018 | 0.006868 | 0.1081 | 0.018574 | 0.0048048 | 8.8288 | 9.0583 | 1.9785 | 21.7813 | 22.0121 | 22.209 | 22.2756 | 22.1089 | 21.4394 | 20.2558 | 22.2053 | 22.3792 | 22.4191 | 22.3675 | 22.0063 | 21.2494 | 22.2941 | 17.1817 | 17.0686 | 16.2129 | 16.2276 | 16.2575 | 17.0667 | 16.8305 | 22.3869 | 22.1582 | 21.7236 | 22.0888 | 21.8106 | 21.3138 | 21.9535 | 21.5456 | 20.9285 | 20.1191 | 20.2826 | 19.9153 | 19.8785 | 0.15533 | -0.024885 | 20.7265 | 22.1029 | 22.4106 | 20.1353 | 21.6962 | 22.1525 | 21.9705 | 21.7327 | 21.3031 | 21.8006 | 21.4693 | 21.0641 | 20.214 | 20.1958 | 20.3676 | 20.2689 | 20.1579 |  | 20.2563 | 19.5922 | 20.13 | 19.8014 | 20.1202 | 20.3966 |  | 20.4516 |  |  | 20.3085 | 20.4065 | 20.6376 | [5 empty] | 21.9634 | 20.3428 | 21.6929 | 22.0767 | 19.571 | 21.1888 | 21.818 | 19.5205 | 20.0394 | 21.1971 |  | 19.7742 | 20.9945 | 18.9206 | 19.781 | 20.8542 | 19.4621 | 20.0426 | 19.0046 | 20.0963 | 19.0851 | 20.2139 | 18.967 | 20.0972 | 21.1313 | 19.53 | 19.8949 | 21.0753 | 18.9909 | 19.8345 | 20.8616 | 18.9654 | 20.1237 | 19.3358 | 19.9395 | 18.9395 | 20.13 | -0.15595 | 20.946 | 0.04786 | 0.015043 | -27.0711 | 3.0977 | 2.94 | -0.25 | 0.97255 | -0.38618 | -7.498 | 0.6316 | 0.46812 | -16.7112 | 4.3983 | 0.42294 | 0.43442 | 0.42828 | 0.38945 | 0.46954 | 0.4415 | 0.4261
42838.4153 | -427 | 22.8923 | 22.8587 | 22.851 | 22.778 | 22.4152 | 21.7607 | 22.7238 | 21.8191 | 22.3744 | 22.3881 | 22.3761 | 22.0581 | 21.2747 | 22.2505 | 21.5688 | 21.7558 | 21.8766 | 21.0727 | 21.1701 | 21.3885 | 20.4726 | 20.6204 | 20.9157 | 21.8968 | 21.6574 | 21.3001 | 20.3712 | 20.4232 | 20.4671 | 22.0489 | 21.6532 | 21.1733 | 21.9952 | 21.7379 | 21.3557 | 19.939 | 20.2595 |  | 20.5683 | 20.1378 | 20.2167 | 19.1222 |  | 16.8777 | 16.9164 | 16.6876 | 16.9566 | 17.0583 | 17.5349 | 17.9992 | 15.5366 | 16.8334 | 15.9898 | 16.925 | 17.8853 | 44.8374 | 47.945 | 43.9417 | 21.3726 |  |  | 0.61332 | -0.24846 | -39.7103 | 0.19643 | 0.03036 | -197.8368 | 13.7859 | 0.052864 | -0.091758 | -0.08234 | -0.0083888 | 8.8295 | 9.0594 | 1.9782 | 21.7802 | 21.9986 | 22.1993 | 22.2667 | 22.1045 | 21.4361 | 20.2511 | 22.1952 | 22.372 | 22.4097 | 22.3677 | 22.0005 | 21.2402 | 22.2796 | 17.1597 | 17.0847 | 16.2161 | 16.2092 | 16.2506 | 17.069 | 16.8346 | 22.3896 | 22.1577 | 21.7208 | 22.0864 | 21.8045 | 21.3083 | 21.959 | 21.5386 | 20.9196 | 20.1191 | 20.274 | 19.9092 | 19.881 | 0.059975 | -0.076239 | 20.7252 | 22.1073 | 22.4067 | 20.1317 | 21.6973 | 22.1446 | 21.9627 | 21.7288 | 21.3082 | 21.7972 | 21.4687 | 21.0629 | 20.2118 | 20.2092 | 20.3668 | 20.2649 | 20.17 |  | 20.254 | 19.614 | 20.1392 | 19.812 | 20.1215 | 20.4085 |  | 20.4574 |  |  | 20.3103 | 20.4082 | 20.6317 | [5 empty] | 21.958 | 20.3425 | 21.6888 | 22.0775 | 19.5642 | 21.192 | 21.813 | 19.5188 | 20.0387 | 21.1949 |  | 19.7713 | 20.9892 | 18.9134 | 19.7724 | 20.8528 | 19.4516 | 20.039 | 19.0082 | 20.0803 | 19.0827 | 20.2114 | 18.9559 | 20.092 | 21.1236 | 19.5226 | 19.8878 | 21.0692 | 18.9818 | 19.8277 | 20.8514 | 18.9535 | 20.113 | 19.3287 | 19.9266 | 18.9265 | 20.129 | -0.086205 | 20.9464 | 0.048721 | 0.016458 | -27.071 | 3.0977 | -3.73 | 0.08 | 0.93519 | -0.59162 | -7.4794 | 0.52605 | 0.20703 | -16.7121 | 4.4116 | 0.42252 | 0.43412 | 0.42803 | 0.39216 | 0.46966 | 0.44108 | 0.42603
42838.4153 | -426 | 22.8926 | 22.8538 | 22.8493 | 22.7732 | 22.4075 | 21.7599 | 22.7202 | 21.8211 | 22.3716 | 22.3833 | 22.3759 | 22.0509 | 21.2701 | 22.2425 | 21.5714 | 21.7497 | 21.8762 | 21.0691 | 21.17 | 21.3885 | 20.4713 | 20.6165 | 20.913 | 21.896 | 21.6578 | 21.299 | 20.3641 | 20.4246 | 20.4422 | 22.044 | 21.649 | 21.1745 | 21.9884 | 21.7319 | 21.3545 | 19.9329 | 20.2607 |  | 20.5603 | 20.1305 | 20.2088 | 19.1257 |  | 16.8798 | 16.9099 | 16.6695 | 16.9472 | 17.0337 | 17.5167 | 18.0014 | 15.5227 | 16.8393 | 15.9616 | 16.9247 | 17.8859 | 44.8269 | 47.945 | 43.9433 | 21.3729 |  |  | 0.55615 | -0.17288 | -38.5078 | 0.57822 | 0.24524 | -197.8 | 13.6729 | -0.004304 | 0.2017 | 0.072492 | -0.0089096 | 8.8291 | 9.0586 | 1.9792 | 21.7858 | 22.0155 | 22.2057 | 22.2768 | 22.1031 | 21.4398 | 20.2622 | 22.2073 | 22.3868 | 22.417 | 22.3721 | 22.0056 | 21.2427 | 22.279 | 17.1342 | 17.1076 | 16.2077 | 16.1896 | 16.244 | 17.0683 | 16.8296 | 22.3936 | 22.16 | 21.7169 | 22.0925 | 21.8143 | 21.3165 | 21.9521 | 21.5413 | 20.923 | 20.1274 | 20.2807 | 19.9137 | 19.8753 | 0.044444 | -0.071294 | 20.7369 | 22.1043 | 22.4121 | 20.14 | 21.7039 | 22.154 | 21.9711 | 21.7385 | 21.3123 | 21.808 | 21.4739 | 21.0708 | 20.2162 | 20.2125 | 20.3658 | 20.2733 | 20.1742 |  | 20.2515 | 19.6316 | 20.1368 | 19.8153 | 20.1193 | 20.4091 |  | 20.4517 |  |  | 20.3065 | 20.4106 | 20.6258 | [5 empty] | 21.9598 | 20.3433 | 21.6956 | 22.0747 | 19.5685 | 21.1931 | 21.8138 | 19.515 | 20.0405 | 21.1963 |  | 19.7744 | 20.9896 | 18.9152 | 19.7723 | 20.8533 | 19.4499 | 20.0323 | 19.0116 | 20.0834 | 19.0837 | 20.218 | 18.9488 | 20.0924 | 21.1225 | 19.5194 | 19.8878 | 21.066 | 18.9842 | 19.8251 | 20.8457 | 18.9593 | 20.1099 | 19.3247 | 19.9251 | 18.9237 | 20.1164 | -0.08435 | 20.9458 | 0.048862 | 0.015885 | -27.017 | 3.0976 | -10.49 | -0.2 | 0.8905 | -0.4935 | -7.3652 | 0.90252 | 0.58838 | -16.7101 | 4.3933 | 0.42232 | 0.43355 | 0.42786 | 0.39492 | 0.47001 | 0.44078 | 0.42647
42838.4154 | -425 | 22.8924 | 22.8524 | 22.8484 | 22.7699 | 22.4106 | 21.7587 | 22.7182 | 21.8237 | 22.374 | 22.3834 | 22.3744 | 22.0486 | 21.2691 | 22.2408 | 21.5749 | 21.7457 | 21.8745 | 21.0767 | 21.1728 | 21.3916 | 20.4766 | 20.6212 | 20.9145 | 21.896 | 21.6633 | 21.3024 | 20.3657 | 20.4222 | 20.4314 | 22.0402 | 21.6476 | 21.1771 | 21.9901 | 21.7319 | 21.3498 | 19.9322 | 20.2664 |  | 20.5582 | 20.1285 | 20.206 | 19.135 |  | 16.8785 | 16.912 | 16.6736 | 16.9433 | 17.0277 | 17.5095 | 17.9978 | 15.4871 | 16.8465 | 15.9544 | 16.9306 | 17.8819 | 44.8182 | 47.9383 | 43.9359 | 21.3715 |  |  | 0.62975 | -0.28 | -37.7666 | -0.02567 | 0.25969 | -197.8499 | 14.0763 | -0.012188 | -0.25269 | -0.16248 | -0.0054376 | 8.8286 | 9.0582 | 1.979 | 21.7838 | 22.0186 | 22.2066 | 22.2732 | 22.1085 | 21.4491 | 20.2558 | 22.2061 | 22.38 | 22.4157 | 22.3724 | 22.0049 | 21.2439 | 22.2893 | 17.0979 | 17.1058 | 16.1973 | 16.1791 | 16.246 | 17.0734 | 16.8267 | 22.3943 | 22.1611 | 21.7248 | 22.0957 | 21.8144 | 21.3192 | 21.9577 | 21.5513 | 20.9247 | 20.1265 | 20.2756 | 19.9123 | 19.8593 | 0.054274 | -0.042384 | 20.7365 | 22.1087 | 22.4075 | 20.1343 | 21.6983 | 22.1484 | 21.9637 | 21.7287 | 21.3097 | 21.8073 | 21.4718 | 21.0676 | 20.2104 | 20.2024 | 20.3559 | 20.2564 | 20.1764 |  | 20.2486 | 19.6396 | 20.1283 | 19.8128 | 20.1126 | 20.3992 |  | 20.4498 |  |  | 20.3097 | 20.4071 | 20.6228 | [5 empty] | 21.9616 | 20.3443 | 21.6913 | 22.0736 | 19.5688 | 21.1904 | 21.8105 | 19.5165 | 20.0476 | 21.2003 |  | 19.7828 | 21.0022 | 18.9259 | 19.7837 | 20.8572 | 19.4552 | 20.0403 | 19.0247 | 20.0991 | 19.088 | 20.2274 | 18.9506 | 20.0878 | 21.1188 | 19.5171 | 19.8888 | 21.0557 | 18.9787 | 19.819 | 20.8419 | 18.962 | 20.1106 | 19.3276 | 19.9305 | 18.9204 | 20.1127 | -0.15781 | 20.9466 | 0.04834 | 0.015957 | -27.1301 | 3.0976 | 3.56 | -0.11 | 0.94758 | -0.62804 | -7.294 | -0.19016 | 0.60546 | -16.712 | 4.4576 | 0.42217 | 0.43305 | 0.42771 | 0.39955 | 0.47083 | 0.4405 | 0.42688
42838.4154 | -424 | 22.8881 | 22.8585 | 22.839 | 22.7723 | 22.4153 | 21.7612 | 22.7209 | 21.8209 | 22.3729 | 22.3826 | 22.3696 | 22.0573 | 21.2791 | 22.2446 | 21.5752 | 21.7482 | 21.8771 | 21.0798 | 21.1714 | 21.3903 | 20.4736 | 20.6231 | 20.9208 | 21.8932 | 21.6604 | 21.3054 | 20.3673 | 20.4204 | 20.4363 | 22.0405 | 21.6515 | 21.1784 | 21.9842 | 21.7303 | 21.355 | 19.9358 | 20.2729 |  | 20.5661 | 20.1309 | 20.2104 | 19.151 |  | 16.8576 | 16.8913 | 16.6593 | 16.9222 | 17.0094 | 17.4796 | 18.0279 | 15.4015 | 16.8373 | 15.972 | 16.9317 | 17.8824 | 44.8102 | 47.933 | 43.9431 | 21.3744 |  |  | 0.46218 | -0.23466 | -36.6186 | 0.23126 | 0.22618 | -197.888 | 14.6737 | 0.083092 | -0.13729 | 0.068506 | 0.14212 | 8.829 | 9.0588 | 1.9789 | 21.786 | 22.0145 | 22.2155 | 22.2763 | 22.1129 | 21.4461 | 20.2585 | 22.2041 | 22.3835 | 22.4256 | 22.3734 | 22.0103 | 21.2446 | 22.2918 | 17.0717 | 17.0903 | 16.1845 | 16.1758 | 16.2272 | 17.071 | 16.8273 | 22.3891 | 22.1556 | 21.7194 | 22.087 | 21.8071 | 21.3146 | 21.9482 | 21.5401 | 20.9209 | 20.1205 | 20.2626 | 19.9058 | 19.8623 | 0.065873 | -0.069392 | 20.7294 | 22.1062 | 22.4063 | 20.1336 | 21.6907 | 22.1422 | 21.9649 | 21.7304 | 21.296 | 21.8021 | 21.4657 | 21.0669 | 20.2076 | 20.1951 | 20.3499 | 20.2487 | 20.1943 |  | 20.2457 | 19.6498 | 20.1339 | 19.8145 | 20.126 | 20.4054 |  | 20.4601 |  |  | 20.3217 | 20.4084 | 20.6323 | [5 empty] | 21.9618 | 20.3499 | 21.6895 | 22.0774 | 19.5656 | 21.1886 | 21.8137 | 19.5163 | 20.0466 | 21.1981 |  | 19.7775 | 20.9949 | 18.9304 | 19.784 | 20.853 | 19.4606 | 20.047 | 19.023 | 20.0957 | 19.0897 | 20.2274 | 18.955 | 20.0856 | 21.1157 | 19.5271 | 19.8943 | 21.0621 | 18.9825 | 19.8217 | 20.8466 | 18.967 | 20.1112 | 19.3294 | 19.9304 | 18.9259 | 20.1212 | -0.23052 | 20.9453 | 0.048493 | 0.015406 | -26.9676 | 3.0976 | 15.98 | 0.08 | 0.81179 | -0.57493 | -7.182 | 0.57075 | 0.56502 | -16.7127 | 4.551 | 0.42157 | 0.43295 | 0.42811 | 0.40218 | 0.47233 | 0.44017 | 0.4266
42838.4154 | -423 | 22.893 | 22.8629 | 22.8496 | 22.7829 | 22.4119 | 21.7596 | 22.72 | 21.8176 | 22.3779 | 22.392 | 22.3736 | 22.0542 | 21.2739 | 22.2468 | 21.5766 | 21.7518 | 21.8822 | 21.0729 | 21.1675 | 21.3905 | 20.4737 | 20.6217 | 20.9238 | 21.8948 | 21.6598 | 21.3016 | 20.365 | 20.4196 | 20.4376 | 22.0364 | 21.6486 | 21.1712 | 21.9862 | 21.7285 | 21.3481 | 19.9222 | 20.2759 |  | 20.558 | 20.1223 | 20.1907 | 19.1612 |  | 16.8549 | 16.8843 | 16.6539 | 16.9132 | 17.0006 | 17.4612 | 18.0548 | 15.3562 | 16.8456 | 16.0312 | 16.9283 | 17.8863 | 44.7934 | 47.9247 | 43.9396 | 21.3718 |  |  | 0.53907 | -0.26685 | -36.0567 | 0.44285 | 0.3576 | -197.846 | 14.6875 | 0.1212 | 0.046603 | 0.073961 | 0.1048 | 8.8284 | 9.0582 | 1.9786 | 21.7843 | 22.0128 | 22.2113 | 22.2765 | 22.1111 | 21.4441 | 20.2613 | 22.2074 | 22.3825 | 22.4304 | 22.3762 | 22.0093 | 21.2451 | 22.2901 | 17.0334 | 17.0898 | 16.1722 | 16.1718 | 16.2074 | 17.0698 | 16.8234 | 22.3846 | 22.1457 | 21.7105 | 22.0867 | 21.7998 | 21.3138 | 21.9441 | 21.5342 | 20.9202 | 20.1106 | 20.2607 | 19.9076 | 19.8501 | 0.19484 | -0.11009 | 20.7373 | 22.1021 | 22.4061 | 20.1317 | 21.6914 | 22.1499 | 21.9694 | 21.7254 | 21.301 | 21.7975 | 21.4581 | 21.0638 | 20.2086 | 20.2059 | 20.3387 | 20.2482 | 20.2066 |  | 20.2549 | 19.6543 | 20.1408 | 19.8101 | 20.1264 | 20.401 |  | 20.4645 |  |  | 20.3257 | 20.4069 | 20.6374 | [5 empty] | 21.9587 | 20.3463 | 21.6919 | 22.074 | 19.5566 | 21.1871 | 21.8164 | 19.5136 | 20.0419 | 21.1965 |  | 19.7752 | 20.9951 | 18.9271 | 19.7845 | 20.8568 | 19.4633 | 20.045 | 19.0177 | 20.0965 | 19.0924 | 20.23 | 18.9552 | 20.0863 | 21.1154 | 19.533 | 19.8895 | 21.0622 | 18.9825 | 19.8226 | 20.8477 | 18.9744 | 20.1081 | 19.3312 | 19.9241 | 18.9278 | 20.1217 | -0.090471 | 20.945 | 0.04735 | 0.013961 | -26.919 | 3.0976 | -7 | -0.28 | 0.87671 | -0.61309 | -7.1266 | 0.78981 | 0.71044 | -16.7104 | 4.553 | 0.42154 | 0.43305 | 0.42825 | 0.4063 | 0.47324 | 0.43944 | 0.42661
42838.4154 | -422 | 22.8994 | 22.8573 | 22.8547 | 22.7745 | 22.4164 | 21.7614 | 22.7163 | 21.8232 | 22.3845 | 22.3907 | 22.372 | 22.0528 | 21.2723 | 22.239 | 21.5755 | 21.7469 | 21.8811 | 21.0712 | 21.1674 | 21.3922 | 20.4757 | 20.6155 | 20.9204 | 21.9007 | 21.6574 | 21.2981 | 20.3641 | 20.4121 | 20.4337 | 22.0373 | 21.6439 | 21.1696 | 21.9871 | 21.7263 | 21.3534 | 19.9242 | 20.2872 |  | 20.5488 | 20.1214 | 20.193 | 19.1699 |  | 16.8461 | 16.8727 | 16.6288 | 16.8938 | 16.9775 | 17.4268 | 18.0274 | 15.382 | 16.8371 | 16.0873 | 16.9235 | 17.8862 | 44.7922 | 47.9141 | 43.9401 | 21.3788 |  |  | 0.67049 | -0.13477 | -35.4141 | 0.28055 | 0.26166 | -197.8519 | 14.6329 | -0.10353 | -0.12192 | 0.14781 | -0.027832 | 8.8293 | 9.0589 | 1.9781 | 21.786 | 22.0146 | 22.2153 | 22.2775 | 22.1154 | 21.4433 | 20.2607 | 22.2141 | 22.3864 | 22.4238 | 22.3717 | 22.0102 | 21.2464 | 22.2967 | 17.0254 | 17.0978 | 16.172 | 16.1726 | 16.1966 | 17.0742 | 16.8233 | 22.3793 | 22.1639 | 21.7226 | 22.0877 | 21.8092 | 21.3213 | 21.9436 | 21.54 | 20.9247 | 20.1198 | 20.2642 | 19.9106 | 19.8345 | 0.11247 | -0.02926 | 20.7381 | 22.1072 | 22.4063 | 20.1268 | 21.6995 | 22.1448 | 21.9678 | 21.7324 | 21.3142 | 21.8006 | 21.4668 | 21.0699 | 20.2156 | 20.2092 | 20.3338 | 20.2462 | 20.2085 |  | 20.2491 | 19.675 | 20.1362 | 19.8118 | 20.1222 | 20.3963 |  | 20.4524 |  |  | 20.3238 | 20.4049 | 20.6411 | [5 empty] | 21.9597 | 20.3437 | 21.6928 | 22.0686 | 19.5568 | 21.1933 | 21.8182 | 19.5066 | 20.0339 | 21.1831 |  | 19.7662 | 20.988 | 18.9237 | 19.7778 | 20.8501 | 19.4582 | 20.0323 | 19.0114 | 20.0882 | 19.0847 | 20.2207 | 18.9499 | 20.0885 | 21.1172 | 19.5326 | 19.8899 | 21.0588 | 18.9841 | 19.8223 | 20.8444 | 18.9792 | 20.1071 | 19.3295 | 19.9244 | 18.9299 | 20.1231 | -0.12293 | 20.9456 | 0.046551 | 0.012546 | -26.9762 | 3.0977 | 7.98 | 0.18 | 0.97775 | -0.4357 | -7.0627 | 0.62862 | 0.60767 | -16.7097 | 4.5443 | 0.42129 | 0.43233 | 0.42806 | 0.40769 | 0.47325 | 0.43926 | 0.42735
42838.4154 | -421 | 22.887 | 22.8581 | 22.849 | 22.7759 | 22.4153 | 21.7522 | 22.7123 | 21.8195 | 22.3704 | 22.387 | 22.3703 | 22.0496 | 21.275 | 22.2368 | 21.5824 | 21.7503 | 21.8836 | 21.0722 | 21.1752 | 21.3903 | 20.4796 | 20.6206 | 20.9224 | 21.9048 | 21.6653 | 21.2983 | 20.3718 | 20.41 | 20.4332 | 22.0448 | 21.6494 | 21.1771 | 21.9926 | 21.734 | 21.3577 | 19.93 | 20.3165 |  | 20.5653 | 20.131 | 20.1951 | 19.1817 |  | 16.8439 | 16.8698 | 16.6276 | 16.8892 | 16.9662 | 17.4386 | 18.0244 | 15.3758 | 16.842 | 16.1936 | 16.9254 | 17.8907 | 44.7816 | 47.9028 | 43.9491 | 21.385 |  |  | 0.78877 | -0.211 | -34.7143 | 0.272 | 0.30569 | -197.8217 | 14.4903 | -0.043072 | -0.11803 | 0.24809 | -0.023145 | 8.8281 | 9.0578 | 1.9784 | 21.7962 | 22.0185 | 22.2125 | 22.2761 | 22.1201 | 21.4513 | 20.2717 | 22.2189 | 22.3848 | 22.423 | 22.3804 | 22.0089 | 21.2512 | 22.3054 | 17.0293 | 17.0884 | 16.1763 | 16.1848 | 16.207 | 17.0812 | 16.8287 | 22.3858 | 22.1468 | 21.7186 | 22.0875 | 21.8004 | 21.3126 | 21.9492 | 21.5319 | 20.9197 | 20.118 | 20.2507 | 19.9065 | 19.828 | 0.007483 | 0.049103 | 20.7414 | 22.1042 | 22.4032 | 20.1296 | 21.6959 | 22.1427 | 21.9669 | 21.7328 | 21.3026 | 21.8013 | 21.4649 | 21.066 | 20.2133 | 20.2105 | 20.3251 | 20.2407 | 20.2018 |  | 20.2476 | 19.6805 | 20.1343 | 19.8119 | 20.1195 | 20.3857 |  | 20.4505 |  |  | 20.3247 | 20.4051 | 20.6445 | [5 empty] | 21.9584 | 20.3483 | 21.687 | 22.0694 | 19.5582 | 21.1922 | 21.8127 | 19.5046 | 20.0329 | 21.1829 |  | 19.7658 | 20.9864 | 18.9272 | 19.7794 | 20.8512 | 19.4615 | 20.034 | 19.0128 | 20.0868 | 19.0828 | 20.2253 | 18.9592 | 20.0941 | 21.1184 | 19.532 | 19.8928 | 21.059 | 18.9916 | 19.8215 | 20.8508 | 18.9869 | 20.1052 | 19.3339 | 19.9238 | 18.9346 | 20.1281 | 0.000795 | 20.9468 | 0.047117 | 0.01484 | -27.1096 | 3.0977 | 0.98 | -0.17 | 1.0605 | -0.54516 | -6.9925 | 0.61897 | 0.65682 | -16.7087 | 4.5222 | 0.42143 | 0.43211 | 0.42797 | 0.40808 | 0.47339 | 0.43912 | 0.42747
42838.4154 | -420 | 22.8871 | 22.856 | 22.8485 | 22.7749 | 22.4158 | 21.7543 | 22.7218 | 21.8195 | 22.3793 | 22.3836 | 22.3723 | 22.045 | 21.2778 | 22.2416 | 21.5661 | 21.7376 | 21.8774 | 21.0646 | 21.1643 | 21.3867 | 20.4697 | 20.6173 | 20.9121 | 21.8877 | 21.6438 | 21.2839 | 20.357 | 20.4039 | 20.4145 | 22.0438 | 21.6448 | 21.1768 | 21.9885 | 21.7303 | 21.348 | 19.9301 | 20.3222 |  | 20.5623 | 20.124 | 20.1908 | 19.188 |  | 16.8428 | 16.8579 | 16.6241 | 16.8868 | 16.9551 | 17.4392 | 18.0182 | 15.372 | 16.8479 | 16.2393 | 16.9296 | 17.8912 | 44.7619 | 47.8883 | 43.9538 | 21.3859 |  |  | 0.63697 | -0.44296 | -34.1104 | 0.27529 | 0.17361 | -197.9064 | 14.9595 | -0.13047 | -0.17193 | 0.31523 | 0.068342 | 8.8295 | 9.0589 | 1.979 | 21.794 | 22.0077 | 22.1993 | 22.2645 | 22.1065 | 21.4362 | 20.2569 | 22.2053 | 22.3748 | 22.4103 | 22.3632 | 21.9964 | 21.2452 | 22.2895 | 17.0236 | 17.0984 | 16.1704 | 16.1755 | 16.2107 | 17.0732 | 16.8251 | 22.393 | 22.1561 | 21.7211 | 22.0942 | 21.8085 | 21.3264 | 21.962 | 21.5428 | 20.9268 | 20.1247 | 20.2734 | 19.9059 | 19.8262 | 0.063907 | -0.092596 | 20.7421 | 22.1113 | 22.4073 | 20.1437 | 21.7023 | 22.1433 | 21.9649 | 21.7269 | 21.3128 | 21.8038 | 21.4673 | 21.0662 | 20.2177 | 20.2164 | 20.3309 | 20.2307 | 20.2025 |  | 20.2502 | 19.7022 | 20.1299 | 19.8092 | 20.1112 | 20.3808 |  | 20.4521 |  |  | 20.3203 | 20.3992 | 20.6446 | [5 empty] | 21.9581 | 20.3457 | 21.6923 | 22.0691 | 19.5636 | 21.1902 | 21.8069 | 19.4976 | 20.0283 | 21.1849 |  | 19.7607 | 20.9883 | 18.9185 | 19.7754 | 20.8497 | 19.4539 | 20.0374 | 19.0014 | 20.083 | 19.0849 | 20.2291 | 18.9522 | 20.0854 | 21.1133 | 19.5231 | 19.8773 | 21.0505 | 18.978 | 19.8199 | 20.8479 | 18.9778 | 20.0946 | 19.3242 | 19.9084 | 18.9319 | 20.1291 | -0.21884 | 20.9468 | 0.048014 | 0.015253 | -27.1796 | 3.0976 | -8.51 | -0.24 | 0.95297 | -0.78987 | -6.9313 | 0.62268 | 0.49499 | -16.7123 | 4.5948 | 0.42149 | 0.43136 | 0.42776 | 0.40777 | 0.47364 | 0.43895 | 0.42774
42838.4154 | -419 | 22.8878 | 22.8502 | 22.843 | 22.7741 | 22.411 | 21.7563 | 22.7173 | 21.8182 | 22.3758 | 22.3831 | 22.3702 | 22.053 | 21.2749 | 22.2449 | 21.5641 | 21.7394 | 21.8751 | 21.0607 | 21.1622 | 21.3919 | 20.4697 | 20.613 | 20.908 | 21.8867 | 21.6519 | 21.2822 | 20.3582 | 20.4047 | 20.4152 | 22.0443 | 21.6402 | 21.1718 | 21.986 | 21.7329 | 21.3476 | 19.9312 | 20.3371 |  | 20.5591 | 20.1302 | 20.1912 | 19.1989 |  | 16.8218 | 16.8406 | 16.603 | 16.8709 | 16.9345 | 17.418 | 17.9848 | 15.4329 | 16.8313 | 16.2026 | 16.9228 | 17.8923 | 44.7469 | 47.8734 | 43.9588 | 21.3872 |  |  | 0.60609 | -0.27145 | -33.6504 | 0.3916 | 0.085556 | -197.8368 | 15.3505 | -0.16136 | 0.071706 | 0.082143 | 0.0002912 | 8.8279 | 9.0578 | 1.9787 | 21.7864 | 22.0092 | 22.1978 | 22.272 | 22.1094 | 21.4297 | 20.2463 | 22.2031 | 22.3802 | 22.4134 | 22.3691 | 22.0051 | 21.2429 | 22.2817 | 16.9998 | 17.1121 | 16.1783 | 16.1637 | 16.2089 | 17.0799 | 16.8252 | 22.3872 | 22.1545 | 21.717 | 22.0902 | 21.804 | 21.3189 | 21.9518 | 21.5395 | 20.9223 | 20.1185 | 20.2731 | 19.9034 | 19.809 | 0.12092 | 0.032745 | 20.7349 | 22.1004 | 22.4 | 20.1332 | 21.6999 | 22.1383 | 21.9643 | 21.7207 | 21.3043 | 21.7941 | 21.4623 | 21.0557 | 20.202 | 20.2098 | 20.3143 | 20.2215 | 20.1983 |  | 20.2531 | 19.7173 | 20.1321 | 19.8184 | 20.1134 | 20.38 |  | 20.4459 |  |  | 20.3274 | 20.3998 | 20.651 | [5 empty] | 21.9606 | 20.351 | 21.6967 | 22.0703 | 19.559 | 21.1929 | 21.8133 | 19.502 | 20.0323 | 21.1886 |  | 19.7536 | 20.9842 | 18.9188 | 19.7743 | 20.8543 | 19.4575 | 20.0381 | 19.0025 | 20.0932 | 19.0919 | 20.2354 | 18.9379 | 20.0797 | 21.1072 | 19.514 | 19.8831 | 21.0411 | 18.9695 | 19.823 | 20.8466 | 18.9733 | 20.0908 | 19.3229 | 19.9029 | 18.9305 | 20.1257 | -0.27894 | 20.9476 | 0.048204 | 0.014898 | -27.1455 | 3.0976 | 0.36 | -0.03 | 0.92958 | -0.61831 | -6.8842 | 0.74264 | 0.34747 | -16.7088 | 4.6543 | 0.42171 | 0.43102 | 0.42758 | 0.4112 | 0.47276 | 0.43869 | 0.42801
42838.4154 | -418 | 22.8848 | 22.8532 | 22.8441 | 22.777 | 22.4107 | 21.7545 | 22.7162 | 21.8207 | 22.3602 | 22.3795 | 22.3664 | 22.0517 | 21.2717 | 22.2362 | 21.5799 | 21.7502 | 21.8921 | 21.0784 | 21.1718 | 21.3937 | 20.4759 | 20.6166 | 20.922 | 21.9005 | 21.6614 | 21.2968 | 20.3516 | 20.4021 | 20.413 | 22.0352 | 21.6417 | 21.1718 | 21.9852 | 21.7314 | 21.3446 | 19.9336 | 20.3538 |  | 20.5574 | 20.1204 | 20.1865 | 19.2142 |  | 16.8166 | 16.8242 | 16.5925 | 16.8461 | 16.9193 | 17.4019 | 17.9607 | 15.5542 | 16.8406 | 16.1447 | 16.9257 | 17.8875 | 44.7319 | 47.8512 | 43.94 | 21.3866 |  |  | 0.53052 | -0.017809 | -32.5103 | 0.16621 | 0.1079 | -197.821 | 15.3551 | -0.008248 | -0.24374 | 0.066408 | -0.045539 | 8.8291 | 9.0589 | 1.9785 | 21.7874 | 22.0216 | 22.2049 | 22.2705 | 22.106 | 21.4363 | 20.2593 | 22.2075 | 22.3844 | 22.4091 | 22.3778 | 22.0055 | 21.2462 | 22.295 | 16.9793 | 17.0672 | 16.1411 | 16.1511 | 16.1924 | 17.076 | 16.8193 | 22.3835 | 22.1513 | 21.7166 | 22.0875 | 21.8056 | 21.3182 | 21.9506 | 21.5469 | 20.9196 | 20.1179 | 20.2657 | 19.9022 | 19.7929 | 0.10736 | 0.03712 | 20.7522 | 22.1081 | 22.4135 | 20.1382 | 21.7071 | 22.1424 | 21.9608 | 21.7369 | 21.299 | 21.7988 | 21.471 | 21.0633 | 20.211 | 20.2227 | 20.3098 | 20.2244 | 20.2083 |  | 20.2601 | 19.7455 | 20.1288 | 19.8289 | 20.1245 | 20.3819 |  | 20.4565 |  |  | 20.3283 | 20.3911 | 20.663 | [5 empty] | 21.9662 | 20.348 | 21.6951 | 22.0757 | 19.5555 | 21.1849 | 21.812 | 19.4983 | 20.0367 | 21.1888 |  | 19.7599 | 20.9814 | 18.9167 | 19.7799 | 20.8649 | 19.4584 | 20.0391 | 19.014 | 20.092 | 19.0963 | 20.2383 | 18.9392 | 20.08 | 21.1166 | 19.5281 | 19.8871 | 21.0445 | 18.9813 | 19.8323 | 20.8491 | 18.9798 | 20.0945 | 19.3271 | 19.9137 | 18.9412 | 20.1399 | -0.12219 | 20.9523 | 0.047965 | 0.015261 | -27.1892 | 3.0976 | 5.79 | -0.08 | 0.8697 | -0.15837 | -6.7664 | 0.4838 | 0.3902 | -16.7076 | 4.6548 | 0.42167 | 0.43012 | 0.42766 | 0.41302 | 0.47621 | 0.43834 | 0.42844
42838.4155 | -417 | 22.8818 | 22.8524 | 22.8415 | 22.7711 | 22.4071 | 21.7471 | 22.7116 | 21.8208 | 22.3673 | 22.3851 | 22.3667 | 22.0488 | 21.266 | 22.2317 | 21.5803 | 21.7557 | 21.895 | 21.0814 | 21.1738 | 21.3979 | 20.4801 | 20.6274 | 20.9208 | 21.8974 | 21.6602 | 21.2978 | 20.3512 | 20.3981 | 20.4102 | 22.0355 | 21.6511 | 21.1748 | 21.9839 | 21.7235 | 21.3426 | 19.9375 | 20.358 |  | 20.5578 | 20.1294 | 20.1904 | 19.2356 |  | 16.7959 | 16.8072 | 16.5684 | 16.8118 | 16.882 | 17.3669 | 17.9427 | 15.6269 | 16.8386 | 16.084 | 16.923 | 17.8918 | 44.7241 | 47.8248 | 43.9412 | 21.3822 |  |  | 0.6488 | -0.20508 | -31.8341 | 0.37254 | 0.010644 | -197.8985 | 15.7027 | -0.1423 | 0.029283 | 0.048365 | 0.072856 | 8.8284 | 9.0582 | 1.9787 | 21.7893 | 22.0053 | 22.2078 | 22.278 | 22.1073 | 21.4416 | 20.2563 | 22.2055 | 22.3801 | 22.4089 | 22.3707 | 22.0062 | 21.2435 | 22.2918 | 16.9592 | 17.0312 | 16.0958 | 16.1433 | 16.1744 | 17.0786 | 16.8228 | 22.381 | 22.1534 | 21.7181 | 22.082 | 21.7984 | 21.3092 | 21.9506 | 21.5382 | 20.9173 | 20.1212 | 20.262 | 19.8931 | 19.7797 | 0.047786 | 0.062226 | 20.7468 | 22.1012 | 22.4003 | 20.1274 | 21.6961 | 22.1421 | 21.9598 | 21.7221 | 21.3005 | 21.7953 | 21.4661 | 21.0575 | 20.1974 | 20.2184 | 20.2958 | 20.2108 | 20.2089 |  | 20.2497 | 19.7448 | 20.1316 | 19.8251 | 20.1187 | 20.3701 |  | 20.4517 |  |  | 20.3201 | 20.3904 | 20.6471 | [5 empty] | 21.953 | 20.3441 | 21.6818 | 22.0635 | 19.5422 | 21.1841 | 21.8053 | 19.4907 | 20.0234 | 21.1815 |  | 19.7518 | 20.9719 | 18.9199 | 19.7722 | 20.843 | 19.4528 | 20.0294 | 19.0092 | 20.0813 | 19.097 | 20.2347 | 18.9345 | 20.077 | 21.1012 | 19.525 | 19.8779 | 21.0402 | 18.9815 | 19.8302 | 20.8355 | 18.979 | 20.0881 | 19.3382 | 19.9092 | 18.9431 | 20.1473 | -0.079527 | 20.9505 | 0.047731 | 0.014861 | -27.1001 | 3.0976 | -8.4 | -0.15 | 0.96177 | -0.5374 | -6.6955 | 0.72431 | 0.12255 | -16.7099 | 4.707 | 0.4213 | 0.43023 | 0.42757 | 0.41557 | 0.48166 | 0.43788 | 0.42892
42838.4155 | -416 | 22.888 | 22.8542 | 22.8458 | 22.7738 | 22.4042 | 21.7527 | 22.7137 | 21.8161 | 22.3731 | 22.3775 | 22.3687 | 22.0503 | 21.2764 | 22.2471 | 21.5767 | 21.7504 | 21.8756 | 21.0656 | 21.1687 | 21.3894 | 20.4718 | 20.6185 | 20.91 | 21.8955 | 21.6617 | 21.2953 | 20.3556 | 20.3977 | 20.4046 | 22.0453 | 21.6523 | 21.1775 | 21.9851 | 21.7307 | 21.3479 | 19.9292 | 20.3744 |  | 20.552 | 20.1214 | 20.1925 | 19.2376 |  | 16.7864 | 16.7981 | 16.561 | 16.797 | 16.8606 | 17.3595 | 17.9502 | 15.6541 | 16.8399 | 16.0486 | 16.9291 | 17.8852 | 44.7097 | 47.8099 | 43.9506 | 21.3828 |  |  | 0.52067 | -0.24057 | -31.8335 | 0.25952 | 0.12367 | -197.8709 | 15.2138 | -0.14887 | 0.031813 | -0.22249 | -0.027832 | 8.8287 | 9.0585 | 1.9785 | 21.7952 | 22.0124 | 22.2149 | 22.2745 | 22.1086 | 21.4392 | 20.2633 | 22.2097 | 22.3859 | 22.416 | 22.3694 | 22.0088 | 21.2495 | 22.2908 | 16.9355 | 17.0281 | 16.0858 | 16.1191 | 16.1674 | 17.0789 | 16.8189 | 22.3882 | 22.1541 | 21.7089 | 22.0841 | 21.8032 | 21.3128 | 21.9443 | 21.5305 | 20.918 | 20.1104 | 20.2651 | 19.8902 | 19.7848 | 0.077473 | 0.089235 | 20.7463 | 22.1101 | 22.4081 | 20.1342 | 21.7011 | 22.1474 | 21.9651 | 21.7341 | 21.3021 | 21.8061 | 21.4644 | 21.0687 | 20.1995 | 20.2205 | 20.2955 | 20.2146 | 20.2077 |  | 20.2454 | 19.7582 | 20.1268 | 19.8165 | 20.1142 | 20.3635 |  | 20.444 |  |  | 20.3193 | 20.3849 | 20.6533 | [5 empty] | 21.968 | 20.3578 | 21.6955 | 22.0738 | 19.5601 | 21.1859 | 21.8105 | 19.4812 | 20.0232 | 21.1606 |  | 19.7342 | 20.964 | 18.92 | 19.7669 | 20.8456 | 19.4515 | 20.0235 | 19.0122 | 20.083 | 19.0843 | 20.2293 | 18.9409 | 20.0791 | 21.1005 | 19.5237 | 19.8846 | 21.0428 | 18.9795 | 19.8308 | 20.8385 | 18.9728 | 20.0825 | 19.3239 | 19.9052 | 18.9479 | 20.1393 | -0.08435 | 20.9471 | 0.047049 | 0.013359 | -27.0745 | 3.0976 | 3.48 | 0.15 | 0.86157 | -0.58203 | -6.6953 | 0.60452 | 0.41771 | -16.7085 | 4.633 | 0.42119 | 0.4297 | 0.42766 | 0.41822 | 0.48231 | 0.43754 | 0.42841
42838.4155 | -415 | 22.8919 | 22.8562 | 22.8472 | 22.7726 | 22.4095 | 21.7615 | 22.7131 | 21.8136 | 22.3794 | 22.385 | 22.3653 | 22.0553 | 21.2713 | 22.2406 | 21.5731 | 21.7517 | 21.8775 | 21.0681 | 21.1715 | 21.3856 | 20.4647 | 20.6155 | 20.9167 | 21.8928 | 21.6586 | 21.2956 | 20.3427 | 20.3982 | 20.3997 | 22.0575 | 21.6598 | 21.1882 | 22.0043 | 21.7407 | 21.3636 | 19.9434 | 20.3978 |  | 20.565 | 20.1355 | 20.2022 | 19.2621 |  | 16.7871 | 16.7938 | 16.5432 | 16.778 | 16.8428 | 17.3576 | 17.9423 | 15.6694 | 16.839 | 16.0091 | 16.9333 | 17.8913 | 44.7049 | 47.8018 | 43.9453 | 21.3913 |  |  | 0.59623 | -0.14135 | -31.0016 | 0.19052 | 0.35038 | -197.821 | 16.0273 | -0.21392 | -0.059843 | 0.11739 | -0.11637 | 8.8281 | 9.0579 | 1.9787 | 21.7894 | 22.0143 | 22.2117 | 22.2773 | 22.111 | 21.4396 | 20.2648 | 22.2095 | 22.3914 | 22.4149 | 22.374 | 22.0097 | 21.2445 | 22.2926 | 16.9065 | 17.0193 | 16.0791 | 16.0973 | 16.1581 | 17.0804 | 16.8255 | 22.3883 | 22.1507 | 21.7119 | 22.082 | 21.8039 | 21.3083 | 21.9446 | 21.5374 | 20.9161 | 20.1134 | 20.2696 | 19.8856 | 19.7956 | 0.053487 | -0.0035828 | 20.7517 | 22.1144 | 22.4157 | 20.1343 | 21.6924 | 22.1464 | 21.9674 | 21.7366 | 21.3019 | 21.8039 | 21.4684 | 21.0704 | 20.2013 | 20.237 | 20.304 | 20.2135 | 20.207 |  | 20.2511 | 19.7699 | 20.1268 | 19.8192 | 20.1147 | 20.359 |  | 20.4527 |  |  | 20.3307 | 20.384 | 20.6618 | [5 empty] | 21.9588 | 20.3584 | 21.6937 | 22.0704 | 19.5547 | 21.1946 | 21.8085 | 19.4937 | 20.0172 | 21.1801 |  | 19.7491 | 20.9823 | 18.9274 | 19.7779 | 20.8502 | 19.4605 | 20.031 | 19.0152 | 20.0864 | 19.0996 | 20.2384 | 18.9372 | 20.076 | 21.0968 | 19.5278 | 19.8711 | 21.0319 | 18.9748 | 19.811 | 20.8324 | 18.963 | 20.0824 | 19.3158 | 19.8938 | 18.9436 | 20.1334 | -0.1541 | 20.9468 | 0.046748 | 0.012125 | -27.0092 | 3.0977 | -22.62 | -0.15 | 0.92197 | -0.44613 | -6.6072 | 0.51795 | 0.70309 | -16.7064 | 4.7553 | 0.4214 | 0.42938 | 0.4276 | 0.42162 | 0.48383 | 0.43734 | 0.42821
42838.4155 | -414 | 22.8921 | 22.8575 | 22.8524 | 22.7701 | 22.4123 | 21.7554 | 22.7156 | 21.8248 | 22.3724 | 22.3804 | 22.369 | 22.0522 | 21.2728 | 22.2432 | 21.5725 | 21.7467 | 21.8833 | 21.0703 | 21.1722 | 21.39 | 20.4767 | 20.6184 | 20.9209 | 21.8901 | 21.6631 | 21.2986 | 20.3404 | 20.3936 | 20.4032 | 22.0488 | 21.65 | 21.1767 | 21.9943 | 21.7367 | 21.3537 | 19.929 | 20.4004 |  | 20.5525 | 20.1158 | 20.1905 | 19.2536 |  | 16.768 | 16.7605 | 16.5118 | 16.7548 | 16.8286 | 17.3851 | 17.9436 | 15.6842 | 16.8395 | 15.9698 | 16.9252 | 17.8886 | 44.7078 | 47.7921 | 43.9415 | 21.3904 |  |  | 0.53775 | -0.10455 | -30.4088 | 0.20366 | 0.1631 | -197.8782 | 16.2527 | -0.25466 | -0.067433 | 0.20173 | -0.060469 | 8.83 | 9.0595 | 1.9789 | 21.7795 | 22.0119 | 22.2108 | 22.2704 | 22.1054 | 21.4318 | 20.2556 | 22.2093 | 22.3782 | 22.4086 | 22.3665 | 22.0072 | 21.2424 | 22.2827 | 16.89 | 17.0089 | 16.0775 | 16.1062 | 16.1502 | 17.0829 | 16.8259 | 22.3864 | 22.1485 | 21.714 | 22.0851 | 21.8049 | 21.311 | 21.9468 | 21.5363 | 20.9186 | 20.109 | 20.2723 | 19.888 | 19.7902 | 0.0023714 | 0.19384 | 20.7527 | 22.1143 | 22.4131 | 20.1334 | 21.6921 | 22.144 | 21.9656 | 21.7363 | 21.3056 | 21.8071 | 21.4659 | 21.0586 | 20.2013 | 20.2289 | 20.2952 | 20.2026 | 20.1989 |  | 20.2439 | 19.7939 | 20.1293 | 19.8026 | 20.118 | 20.3577 |  | 20.455 |  |  | 20.3409 | 20.3926 | 20.662 | [5 empty] | 21.9564 | 20.358 | 21.6933 | 22.0759 | 19.5641 | 21.1902 | 21.813 | 19.49 | 20.0233 | 21.1845 |  | 19.747 | 20.9843 | 18.9248 | 19.775 | 20.8425 | 19.4608 | 20.0341 | 19.0223 | 20.1032 | 19.112 | 20.2449 | 18.945 | 20.0772 | 21.0931 | 19.5254 | 19.8774 | 21.0301 | 18.9729 | 19.8259 | 20.8318 | 18.9675 | 20.0887 | 19.3203 | 19.8965 | 18.9501 | 20.1378 | -0.11551 | 20.9473 | 0.048721 | 0.014092 | -27.1052 | 3.0977 | -11.57 | 0.04 | 0.87559 | -0.38366 | -6.5433 | 0.53549 | 0.47972 | -16.7096 | 4.7888 | 0.42138 | 0.42879 | 0.42817 | 0.42375 | 0.48404 | 0.43709 | 0.42822
42838.4155 | -413 | 22.8947 | 22.8596 | 22.8462 | 22.7746 | 22.4143 | 21.7557 | 22.7265 | 21.8203 | 22.375 | 22.3866 | 22.37 | 22.0503 | 21.2791 | 22.2413 | 21.5685 | 21.7498 | 21.8749 | 21.0676 | 21.1721 | 21.3875 | 20.4777 | 20.6223 | 20.9153 | 21.8916 | 21.6548 | 21.2938 | 20.3388 | 20.3879 | 20.3925 | 22.0498 | 21.657 | 21.1794 | 21.9953 | 21.7328 | 21.3498 | 19.9319 | 20.4019 |  | 20.5644 | 20.113 | 20.1948 | 19.2531 |  | 16.762 | 16.7522 | 16.5068 | 16.7386 | 16.8086 | 17.3868 | 17.9606 | 15.7315 | 16.843 | 15.9477 | 16.9214 | 17.8884 | 44.7172 | 47.7738 | 43.9366 | 21.3891 |  |  | 0.56207 | -0.11506 | -30.0468 | 0.013754 | 0.21238 | -197.8407 | 16.2146 | -0.31183 | 0.051662 | -0.071221 | -0.1747 | 8.8295 | 9.0591 | 1.9789 | 21.7898 | 22.0139 | 22.2092 | 22.275 | 22.1034 | 21.4429 | 20.2546 | 22.2034 | 22.3806 | 22.4072 | 22.3663 | 22 | 21.2413 | 22.2918 | 16.8779 | 16.9886 | 16.0232 | 16.1183 | 16.138 | 17.0756 | 16.8275 | 22.3872 | 22.1526 | 21.7228 | 22.0887 | 21.8078 | 21.3228 | 21.9583 | 21.5368 | 20.9196 | 20.1228 | 20.2885 | 19.889 | 19.7873 | 0.037956 | 0.19632 | 20.7483 | 22.1001 | 22.4075 | 20.1284 | 21.6895 | 22.1419 | 21.9639 | 21.7279 | 21.2963 | 21.8033 | 21.4646 | 21.0529 | 20.1966 | 20.2174 | 20.2854 | 20.1928 | 20.1997 |  | 20.2566 | 19.8116 | 20.1338 | 19.8075 | 20.1199 | 20.3546 |  | 20.4585 |  |  | 20.3377 | 20.391 | 20.6547 | [5 empty] | 21.9607 | 20.3607 | 21.6915 | 22.0762 | 19.5703 | 21.1856 | 21.8121 | 19.4822 | 20.0115 | 21.1777 |  | 19.7346 | 20.9588 | 18.9152 | 19.7739 | 20.8374 | 19.451 | 20.0242 | 19.018 | 20.0922 | 19.0959 | 20.2378 | 18.9311 | 20.0728 | 21.092 | 19.5255 | 19.8751 | 21.0263 | 18.9756 | 19.8193 | 20.8242 | 18.9732 | 20.0882 | 19.3066 | 19.8938 | 18.9572 | 20.1345 | -0.029256 | 20.947 | 0.048604 | 0.014731 | -27.0504 | 3.0977 | -1.43 | 0.02 | 0.89515 | -0.40249 | -6.5042 | 0.13916 | 0.54742 | -16.708 | 4.7832 | 0.42179 | 0.42845 | 0.4281 | 0.42424 | 0.49027 | 0.4372 | 0.42876
42838.4155 | -412 | 22.8928 | 22.8525 | 22.8444 | 22.7714 | 22.4135 | 21.7593 | 22.7245 | 21.8181 | 22.3674 | 22.3843 | 22.3649 | 22.0501 | 21.2744 | 22.2361 | 21.5724 | 21.7519 | 21.8834 | 21.0745 | 21.1709 | 21.3953 | 20.4781 | 20.6232 | 20.917 | 21.8941 | 21.6651 | 21.2945 | 20.3456 | 20.3892 | 20.3909 | 22.0434 | 21.6522 | 21.1744 | 21.989 | 21.7318 | 21.3437 | 19.9336 | 20.4133 |  | 20.5586 | 20.1143 | 20.1926 | 19.2491 |  | 16.7442 | 16.7465 | 16.4893 | 16.7239 | 16.7968 | 17.3622 | 17.9801 | 15.8023 | 16.8354 | 15.9465 | 16.9214 | 17.8857 | 44.7346 | 47.764 | 43.9436 | 21.3861 |  |  | 0.62055 | -0.165 | -29.7175 | 0.18395 | 0.35629 | -197.8769 | 16.6976 | -0.43274 | 0.095253 | -0.21221 | -0.08269 | 8.8291 | 9.0587 | 1.9785 | 21.7913 | 22.0165 | 22.2137 | 22.2787 | 22.1105 | 21.4377 | 20.2568 | 22.2112 | 22.3818 | 22.4152 | 22.3714 | 22.0043 | 21.2441 | 22.2939 | 16.8755 | 16.9821 | 15.9867 | 16.1269 | 16.1275 | 17.0711 | 16.8244 | 22.4 | 22.166 | 21.724 | 22.0888 | 21.8128 | 21.3176 | 21.9589 | 21.5532 | 20.9266 | 20.1196 | 20.2902 | 19.8841 | 19.7845 | -0.076072 | -0.052464 | 20.761 | 22.1093 | 22.4037 | 20.1372 | 21.6983 | 22.1434 | 21.9666 | 21.7332 | 21.3025 | 21.8102 | 21.4699 | 21.0577 | 20.206 | 20.2245 | 20.2899 | 20.199 | 20.1852 |  | 20.248 | 19.8266 | 20.1323 | 19.7967 | 20.1231 | 20.3559 |  | 20.4534 |  |  | 20.3273 | 20.3901 | 20.6572 | [5 empty] | 21.9586 | 20.3563 | 21.6839 | 22.0711 | 19.5661 | 21.1849 | 21.808 | 19.4766 | 20.0109 | 21.17 |  | 19.7314 | 20.9626 | 18.9173 | 19.7616 | 20.8329 | 19.461 | 20.0194 | 19.0247 | 20.088 | 19.0952 | 20.2331 | 18.9182 | 20.0662 | 21.0822 | 19.5192 | 19.8576 | 21.0154 | 18.9706 | 19.8103 | 20.8197 | 18.952 | 20.0782 | 19.3009 | 19.8841 | 18.9463 | 20.1259 | -0.23479 | 20.9474 | 0.048057 | 0.015086 | -27.1893 | 3.0977 | -15.78 | 0 | 0.94056 | -0.48198 | -6.4684 | 0.50891 | 0.70901 | -16.7089 | 4.8537 | 0.4219 | 0.42798 | 0.42851 | 0.42399 | 0.49396 | 0.43737 | 0.42873
42838.4155 | -411 | 22.8881 | 22.8506 | 22.842 | 22.7705 | 22.4044 | 21.7584 | 22.7139 | 21.8127 | 22.3661 | 22.3802 | 22.3656 | 22.0476 | 21.2689 | 22.2357 | 21.5702 | 21.743 | 21.8828 | 21.0724 | 21.166 | 21.3928 | 20.4735 | 20.6188 | 20.919 | 21.8913 | 21.6611 | 21.2947 | 20.3337 | 20.3898 | 20.3819 | 22.0417 | 21.649 | 21.1785 | 21.9867 | 21.7366 | 21.3453 | 19.9287 | 20.428 |  | 20.5563 | 20.1203 | 20.1835 | 19.2507 |  | 16.727 | 16.731 | 16.4797 | 16.7069 | 16.7806 | 17.3366 | 18.0009 | 15.8139 | 16.8332 | 15.9328 | 16.9163 | 17.8864 | 44.761 | 47.7569 | 43.9529 | 21.3855 |  |  | 0.3715 | -0.10192 | -29.9554 | 0.15832 | 0.30832 | -197.8131 | 16.7942 | -0.41172 | -0.043108 | -0.3469 | -0.1056 | 8.8289 | 9.0583 | 1.9783 | 21.787 | 22.0121 | 22.2058 | 22.2684 | 22.1037 | 21.4283 | 20.256 | 22.2101 | 22.3856 | 22.4196 | 22.3716 | 22.0088 | 21.2445 | 22.2829 | 16.9036 | 16.9637 | 16.0079 | 16.1417 | 16.1481 | 17.0732 | 16.8207 | 22.3867 | 22.1521 | 21.714 | 22.0897 | 21.8109 | 21.3136 | 21.9554 | 21.5464 | 20.9216 | 20.1179 | 20.2953 | 19.8776 | 19.7808 | -0.070764 | -0.078141 | 20.7615 | 22.1075 | 22.4 | 20.1339 | 21.6969 | 22.1527 | 21.9633 | 21.7325 | 21.3007 | 21.8061 | 21.4698 | 21.0588 | 20.205 | 20.2315 | 20.2854 | 20.1942 | 20.1963 |  | 20.2577 | 19.8444 | 20.1378 | 19.7998 | 20.12 | 20.3558 |  | 20.4528 |  |  | 20.3391 | 20.3966 | 20.662 | [5 empty] | 21.9639 | 20.3598 | 21.6887 | 22.0785 | 19.5718 | 21.1915 | 21.8091 | 19.482 | 20.0167 | 21.1756 |  | 19.7434 | 20.9688 | 18.9227 | 19.7739 | 20.8455 | 19.4589 | 20.0255 | 19.0348 | 20.0904 | 19.1016 | 20.2498 | 18.9171 | 20.0761 | 21.0911 | 19.5321 | 19.8646 | 21.0231 | 18.986 | 19.8212 | 20.8352 | 18.9648 | 20.0808 | 19.3167 | 19.8954 | 18.9622 | 20.1452 | -0.20418 | 20.9471 | 0.048254 | 0.015007 | -27.0111 | 3.0977 | -20.27 | -0.03 | 0.72774 | -0.37879 | -6.494 | 0.47211 | 0.65952 | -16.7054 | 4.8675 | 0.42192 | 0.42768 | 0.42832 | 0.4211 | 0.49118 | 0.43716 | 0.42877
42838.4155 | -410 | 22.8911 | 22.8531 | 22.8429 | 22.7702 | 22.4092 | 21.7454 | 22.7127 | 21.8171 | 22.3631 | 22.3781 | 22.3703 | 22.0425 | 21.2701 | 22.2361 | 21.574 | 21.745 | 21.8817 | 21.0754 | 21.168 | 21.3868 | 20.4776 | 20.6192 | 20.9188 | 21.8884 | 21.6607 | 21.2975 | 20.3332 | 20.3848 | 20.3829 | 22.0404 | 21.6506 | 21.1788 | 21.9922 | 21.7334 | 21.3507 | 19.9251 | 20.4377 |  | 20.5479 | 20.1171 | 20.1881 | 19.25 |  | 16.7269 | 16.7332 | 16.4772 | 16.7001 | 16.7776 | 17.3496 | 18.0228 | 15.7495 | 16.8383 | 15.9315 | 16.9182 | 17.8831 | 44.7722 | 47.7529 | 43.9502 | 21.3736 |  |  | 0.38464 | -0.12426 | -29.8378 | 0.006526 | 0.30109 | -197.8066 | 16.3434 | -0.3092 | -0.09059 | -0.18724 | 0.035185 | 8.8293 | 9.0592 | 1.9783 | 21.7909 | 22.0024 | 22.2078 | 22.2748 | 22.1088 | 21.4426 | 20.2569 | 22.2056 | 22.3843 | 22.4192 | 22.3749 | 22.0096 | 21.2471 | 22.2893 | 16.9509 | 16.9454 | 16.0192 | 16.1526 | 16.1612 | 17.0719 | 16.8258 | 22.3899 | 22.1582 | 21.7224 | 22.0907 | 21.817 | 21.3209 | 21.9529 | 21.5449 | 20.9219 | 20.1219 | 20.3018 | 19.8888 | 19.7886 | -0.19521 | 0.0064978 | 20.7655 | 22.1138 | 22.4113 | 20.1302 | 21.6991 | 22.1532 | 21.9779 | 21.7337 | 21.3056 | 21.8077 | 21.4707 | 21.0665 | 20.2109 | 20.2374 | 20.2853 | 20.1955 | 20.1724 |  | 20.2501 | 19.8524 | 20.1346 | 19.7885 | 20.1171 | 20.3518 |  | 20.452 |  |  | 20.338 | 20.3913 | 20.6557 | [5 empty] | 21.9604 | 20.3551 | 21.6878 | 22.0738 | 19.5746 | 21.1888 | 21.8045 | 19.4776 | 20.0111 | 21.1718 |  | 19.7484 | 20.9649 | 18.921 | 19.7791 | 20.8511 | 19.4534 | 20.0214 | 19.0394 | 20.0957 | 19.1086 | 20.2517 | 18.8986 | 20.0673 | 21.0852 | 19.5231 | 19.8569 | 21.0192 | 18.9753 | 19.8229 | 20.8346 | 18.9602 | 20.0759 | 19.3117 | 19.8871 | 18.9557 | 20.147 | -0.031111 | 20.9467 | 0.047184 | 0.013061 | -26.993 | 3.0977 | -9.64 | -0.09 | 0.7405 | -0.41826 | -6.4813 | 0.095852 | 0.65176 | -16.7055 | 4.8019 | 0.42233 | 0.42735 | 0.42853 | 0.4157 | 0.49052 | 0.43706 | 0.42869
42838.4155 | -409 | 22.8843 | 22.8537 | 22.8401 | 22.7702 | 22.4034 | 21.7507 | 22.7155 | 21.8164 | 22.3653 | 22.3854 | 22.3617 | 22.0431 | 21.2747 | 22.2354 | 21.5767 | 21.7477 | 21.8799 | 21.0724 | 21.1677 | 21.3901 | 20.4805 | 20.6176 | 20.9177 | 21.888 | 21.6543 | 21.2933 | 20.3276 | 20.3778 | 20.3819 | 22.044 | 21.6511 | 21.1751 | 21.9909 | 21.7265 | 21.3587 | 19.9329 | 20.4493 |  | 20.5614 | 20.1126 | 20.1929 | 19.263 |  | 16.7309 | 16.728 | 16.4755 | 16.6925 | 16.7776 | 17.3609 | 18.0495 | 15.6562 | 16.8392 | 15.9477 | 16.9281 | 17.8869 | 44.7805 | 47.7474 | 43.9608 | 21.3749 |  |  | 0.51672 | -0.27211 | -29.3896 | -0.10584 | 0.25115 | -197.8486 | 17.379 | -0.3 | -0.077747 | -0.020659 | 0.014006 | 8.8289 | 9.0587 | 1.9791 | 21.7896 | 22.0101 | 22.2035 | 22.276 | 22.1081 | 21.4398 | 20.2603 | 22.206 | 22.3813 | 22.4154 | 22.3715 | 22.0017 | 21.2428 | 22.2916 | 16.9993 | 16.9355 | 16.0288 | 16.1477 | 16.1766 | 17.0818 | 16.8276 | 22.3899 | 22.1619 | 21.723 | 22.093 | 21.8113 | 21.3224 | 21.9568 | 21.5419 | 20.92 | 20.1207 | 20.3048 | 19.8901 | 19.7907 | -0.20288 | -0.011761 | 20.7676 | 22.1079 | 22.4032 | 20.1118 | 21.6886 | 22.1394 | 21.9616 | 21.7244 | 21.2975 | 21.8041 | 21.4624 | 21.0611 | 20.2071 | 20.229 | 20.2677 | 20.1875 | 20.1652 |  | 20.2567 | 19.8652 | 20.1311 | 19.7891 | 20.1145 | 20.3629 |  | 20.4515 |  |  | 20.3443 | 20.3901 | 20.6597 | [5 empty] | 21.9596 | 20.3577 | 21.6969 | 22.0776 | 19.5733 | 21.1865 | 21.8141 | 19.4732 | 19.9974 | 21.1588 |  | 19.7358 | 20.9642 | 18.9187 | 19.7711 | 20.8446 | 19.4475 | 20.0093 | 19.0399 | 20.0968 | 19.1065 | 20.2421 | 18.8885 | 20.0667 | 21.0829 | 19.5169 | 19.8554 | 21.0211 | 18.9764 | 19.8189 | 20.8336 | 18.9535 | 20.0757 | 19.3085 | 19.8868 | 18.9565 | 20.1433 | -0.22496 | 20.9473 | 0.046312 | 0.012988 | -26.8924 | 3.0977 | 2.45 | -0.19 | 0.85827 | -0.61894 | -6.4324 | -0.38601 | 0.59527 | -16.7076 | 4.9518 | 0.42275 | 0.42687 | 0.42843 | 0.41148 | 0.48966 | 0.43697 | 0.42859
42838.4156 | -408 | 22.8923 | 22.856 | 22.8421 | 22.7769 | 22.4091 | 21.764 | 22.7214 | 21.8146 | 22.3718 | 22.3782 | 22.3727 | 22.0508 | 21.2722 | 22.2388 | 21.5741 | 21.7476 | 21.8839 | 21.0734 | 21.1732 | 21.3922 | 20.4775 | 20.627 | 20.9212 | 21.885 | 21.6578 | 21.298 | 20.3236 | 20.3764 | 20.3888 | 22.0423 | 21.6432 | 21.1806 | 21.9878 | 21.7313 | 21.3437 | 19.9237 | 20.4501 |  | 20.5496 | 20.1043 | 20.1745 | 19.263 |  | 16.7255 | 16.709 | 16.4582 | 16.6793 | 16.7749 | 17.3492 | 18.0586 | 15.5902 | 16.8324 | 15.965 | 16.9183 | 17.8879 | 44.7808 | 47.749 | 43.9784 | 21.3824 |  |  | 0.53644 | -0.19917 | -29.3496 | 0.26215 | 0.43514 | -197.8335 | 17.3691 | -0.085784 | 0.052441 | 0.13208 | -0.066024 | 8.8293 | 9.0591 | 1.9792 | 21.7911 | 22.0131 | 22.2104 | 22.279 | 22.1023 | 21.4385 | 20.2609 | 22.2069 | 22.3812 | 22.4238 | 22.37 | 22.0003 | 21.2414 | 22.2903 | 17.0559 | 16.9159 | 16.0439 | 16.1542 | 16.1816 | 17.0687 | 16.8234 | 22.3885 | 22.1607 | 21.7207 | 22.0907 | 21.8152 | 21.3188 | 21.9555 | 21.537 | 20.9202 | 20.1152 | 20.3055 | 19.8825 | 19.7946 | -0.1842 | -0.093167 | 20.7707 | 22.1021 | 22.3984 | 20.1075 | 21.6871 | 22.1426 | 21.9616 | 21.73 | 21.2935 | 21.8032 | 21.4596 | 21.0595 | 20.2028 | 20.2161 | 20.2705 | 20.1845 | 20.1339 |  | 20.2372 | 19.8692 | 20.1311 | 19.7857 | 20.1139 | 20.3415 |  | 20.4409 |  |  | 20.3524 | 20.3836 | 20.6626 | [5 empty] | 21.9621 | 20.3528 | 21.6972 | 22.0743 | 19.5674 | 21.1847 | 21.8103 | 19.4751 | 19.9972 | 21.1649 |  | 19.7337 | 20.9641 | 18.9218 | 19.7729 | 20.843 | 19.4539 | 20.0131 | 19.0496 | 20.1034 | 19.1098 | 20.2383 | 18.8844 | 20.0707 | 21.0887 | 19.5253 | 19.8597 | 21.015 | 18.9836 | 19.8282 | 20.835 | 18.963 | 20.0814 | 19.3192 | 19.8909 | 18.9684 | 20.1444 | -0.20734 | 20.9481 | 0.047823 | 0.014564 | -27.0154 | 3.0977 | -4.76 | 0 | 0.8745 | -0.52951 | -6.4278 | 0.60748 | 0.78353 | -16.7067 | 4.9503 | 0.42296 | 0.42676 | 0.4285 | 0.40366 | 0.48749 | 0.43666 | 0.4283
42838.4156 | -407 | 22.888 | 22.8562 | 22.8476 | 22.7795 | 22.4139 | 21.7624 | 22.7135 | 21.8144 | 22.3793 | 22.3784 | 22.3642 | 22.0571 | 21.2764 | 22.2324 | 21.5661 | 21.7401 | 21.8758 | 21.0706 | 21.1672 | 21.3836 | 20.4673 | 20.6171 | 20.9138 | 21.8805 | 21.6537 | 21.2893 | 20.3176 | 20.3594 | 20.3855 | 22.0424 | 21.6522 | 21.1693 | 21.9911 | 21.7347 | 21.3497 | 19.9325 | 20.4607 |  | 20.5478 | 20.1104 | 20.1758 | 19.2616 |  | 16.7126 | 16.6935 | 16.4471 | 16.6653 | 16.7739 | 17.3367 | 18.0762 | 15.5673 | 16.8262 | 15.9579 | 16.909 | 17.8879 | 44.7733 | 47.7406 | 43.98 | 21.385 |  |  | 0.59755 | -0.33848 | -28.9343 | 0.2536 | 0.23012 | -197.8302 | 17.7641 | -0.035844 | -0.071325 | -0.13689 | 0.0053256 | 8.8282 | 9.0582 | 1.9789 | 21.7953 | 22.0159 | 22.208 | 22.279 | 22.1072 | 21.442 | 20.2567 | 22.2173 | 22.3893 | 22.4257 | 22.3654 | 22.0104 | 21.2427 | 22.2912 | 17.1216 | 16.9389 | 16.0641 | 16.155 | 16.1858 | 17.0792 | 16.8342 | 22.3923 | 22.1629 | 21.7218 | 22.0955 | 21.8134 | 21.3184 | 21.9572 | 21.5406 | 20.9273 | 20.117 | 20.3113 | 19.8937 | 19.8069 | -0.15511 | -0.19093 | 20.7714 | 22.1085 | 22.407 | 20.1151 | 21.6965 | 22.1546 | 21.9636 | 21.7316 | 21.3042 | 21.8022 | 21.469 | 21.0646 | 20.1997 | 20.2207 | 20.2733 | 20.19 | 20.1289 |  | 20.2472 | 19.8818 | 20.1341 | 19.7879 | 20.1157 | 20.3505 |  | 20.4429 |  |  | 20.3477 | 20.3831 | 20.6677 | [5 empty] | 21.963 | 20.3635 | 21.6989 | 22.082 | 19.5741 | 21.1916 | 21.8043 | 19.468 | 19.9958 | 21.162 |  | 19.736 | 20.9666 | 18.9204 | 19.7731 | 20.846 | 19.4597 | 20.0167 | 19.0497 | 20.1073 | 19.1156 | 20.2456 | 18.8798 | 20.0689 | 21.085 | 19.5203 | 19.8539 | 21.0106 | 18.981 | 19.8272 | 20.835 | 18.9659 | 20.0856 | 19.3274 | 19.8974 | 18.9637 | 20.1463 | -0.16133 | 20.9467 | 0.048493 | 0.016095 | -26.9921 | 3.0977 | -7.74 | 0.02 | 0.92296 | -0.69027 | -6.382 | 0.59748 | 0.56979 | -16.7062 | 5.0061 | 0.42344 | 0.42651 | 0.42851 | 0.3976 | 0.4865 | 0.43699 | 0.42802
42838.4156 | -406 | 22.8897 | 22.8594 | 22.8488 | 22.7735 | 22.4125 | 21.7514 | 22.7145 | 21.8178 | 22.3743 | 22.3868 | 22.3697 | 22.0548 | 21.2705 | 22.2425 | 21.5673 | 21.7467 | 21.8801 | 21.0703 | 21.169 | 21.3852 | 20.4688 | 20.6198 | 20.9167 | 21.8832 | 21.6543 | 21.2892 | 20.3222 | 20.3614 | 20.393 | 22.0391 | 21.6491 | 21.1708 | 21.9876 | 21.7267 | 21.3548 | 19.9283 | 20.4644 |  | 20.5445 | 20.1093 | 20.1707 | 19.2601 |  | 16.7245 | 16.7019 | 16.4551 | 16.672 | 16.7946 | 17.3546 | 18.085 | 15.5787 | 16.8447 | 15.9556 | 16.917 | 17.8865 | 44.7685 | 47.7362 | 43.9906 | 21.3835 |  |  | 0.72043 | -0.55993 | -28.4316 | 0.16423 | 0.17164 | -197.8322 | 17.4901 | -0.00102 | -0.21611 | -0.089264 | -0.1056 | 8.8292 | 9.0589 | 1.9785 | 21.7908 | 22.0084 | 22.2022 | 22.2769 | 22.1058 | 21.4468 | 20.2604 | 22.2083 | 22.3824 | 22.4155 | 22.3686 | 22.0036 | 21.2435 | 22.2873 | 17.1618 | 16.9795 | 16.0723 | 16.1513 | 16.1794 | 17.0689 | 16.8251 | 22.3891 | 22.1572 | 21.7179 | 22.0885 | 21.8101 | 21.3172 | 21.9457 | 21.5393 | 20.9166 | 20.1181 | 20.3068 | 19.8779 | 19.8085 | 0.027733 | -0.071865 | 20.7757 | 22.1083 | 22.4139 | 20.1139 | 21.6987 | 22.1492 | 21.9704 | 21.7368 | 21.3092 | 21.801 | 21.46 | 21.0656 | 20.1934 | 20.2332 | 20.2725 | 20.1934 | 20.1115 |  | 20.249 | 19.8933 | 20.1316 | 19.7869 | 20.119 | 20.3528 |  | 20.4494 |  |  | 20.3359 | 20.3657 | 20.6601 | [5 empty] | 21.9533 | 20.3627 | 21.6952 | 22.0687 | 19.5665 | 21.192 | 21.8007 | 19.4638 | 19.9883 | 21.1484 |  | 19.7341 | 20.9605 | 18.927 | 19.7698 | 20.8439 | 19.4606 | 20.0124 | 19.0484 | 20.095 | 19.1116 | 20.2308 | 18.8762 | 20.0627 | 21.0815 | 19.5158 | 19.8476 | 21.0019 | 18.9749 | 19.8196 | 20.8284 | 18.9566 | 20.0829 | 19.313 | 19.8819 | 18.9641 | 20.1394 | -0.24091 | 20.9472 | 0.047916 | 0.015399 | -27.0349 | 3.0977 | -2.79 | -0.18 | 1.0134 | -0.88781 | -6.3264 | 0.48082 | 0.4921 | -16.7067 | 4.9675 | 0.42398 | 0.42611 | 0.42864 | 0.39193 | 0.48454 | 0.43689 | 0.42801
42838.4156 | -405 | 22.8894 | 22.8595 | 22.8477 | 22.7712 | 22.4156 | 21.7554 | 22.7226 | 21.8201 | 22.3715 | 22.3851 | 22.3661 | 22.0513 | 21.2704 | 22.2464 | 21.5664 | 21.7483 | 21.876 | 21.0687 | 21.1706 | 21.3874 | 20.4721 | 20.6137 | 20.9154 | 21.8927 | 21.6515 | 21.2891 | 20.3189 | 20.363 | 20.3984 | 22.0404 | 21.6518 | 21.1729 | 21.9804 | 21.7268 | 21.3507 | 19.9337 | 20.4668 |  | 20.5491 | 20.1051 | 20.1741 | 19.2625 |  | 16.7232 | 16.7028 | 16.4609 | 16.6912 | 16.8064 | 17.367 | 18.0839 | 15.5775 | 16.8363 | 15.9507 | 16.9268 | 17.8745 | 44.7552 | 47.726 | 43.975 | 21.3831 |  |  | 0.72371 | -0.23663 | -28.6044 | 0.36925 | 0.20055 | -197.8723 | 17.7128 | 0.073236 | -0.2342 | -0.085697 | -0.078697 | 8.8297 | 9.0593 | 1.9782 | 21.7878 | 22.0079 | 22.2135 | 22.2721 | 22.1041 | 21.4384 | 20.2523 | 22.2062 | 22.3781 | 22.4159 | 22.3709 | 22.0042 | 21.2491 | 22.2804 | 17.1904 | 17.015 | 16.1016 | 16.1688 | 16.1957 | 17.0729 | 16.8349 | 22.3903 | 22.1538 | 21.7202 | 22.0913 | 21.8038 | 21.3133 | 21.9486 | 21.5396 | 20.9179 | 20.1169 | 20.3036 | 19.8789 | 19.8131 | -0.044223 | -0.14642 | 20.7791 | 22.1028 | 22.4151 | 20.1139 | 21.698 | 22.1489 | 21.9714 | 21.7359 | 21.3039 | 21.8005 | 21.4688 | 21.0643 | 20.1972 | 20.2414 | 20.2752 | 20.1921 | 20.1133 |  | 20.2518 | 19.9191 | 20.1347 | 19.796 | 20.1284 | 20.3487 |  | 20.4584 |  |  | 20.3211 | 20.3564 | 20.6479 | [5 empty] | 21.9564 | 20.3578 | 21.6909 | 22.0627 | 19.558 | 21.1832 | 21.8001 | 19.473 | 19.9936 | 21.1611 |  | 19.7311 | 20.9607 | 18.923 | 19.7734 | 20.85 | 19.4542 | 20.0214 | 19.0602 | 20.1045 | 19.1173 | 20.2333 | 18.8815 | 20.0654 | 21.0765 | 19.5083 | 19.8394 | 20.9986 | 18.9711 | 19.8231 | 20.8277 | 18.9626 | 20.0804 | 19.317 | 19.8796 | 18.9641 | 20.1325 | -0.11978 | 20.9476 | 0.048813 | 0.015754 | -27.0673 | 3.0977 | -11.77 | -0.02 | 1.0158 | -0.57715 | -6.3456 | 0.72097 | 0.53194 | -16.7088 | 4.9992 | 0.42403 | 0.4255 | 0.42871 | 0.3892 | 0.48243 | 0.437 | 0.42784
42838.4156 | -404 | 22.8849 | 22.8521 | 22.8404 | 22.7715 | 22.4124 | 21.7455 | 22.7186 | 21.8158 | 22.3635 | 22.3757 | 22.3612 | 22.0465 | 21.2671 | 22.2363 | 21.5736 | 21.7426 | 21.8812 | 21.0711 | 21.1754 | 21.3933 | 20.4809 | 20.6154 | 20.9184 | 21.8973 | 21.6616 | 21.2925 | 20.3194 | 20.3737 | 20.405 | 22.0432 | 21.6455 | 21.1724 | 21.9897 | 21.7273 | 21.3496 | 19.9312 | 20.4632 |  | 20.5475 | 20.1045 | 20.1678 | 19.2718 |  | 16.732 | 16.7178 | 16.4723 | 16.7163 | 16.796 | 17.3605 | 18.0585 | 15.5472 | 16.8429 | 15.9764 | 16.9303 | 17.8851 | 44.7286 | 47.7219 | 43.9668 | 21.3842 |  |  | 0.60083 | -0.14726 | -29.0315 | 0.6643 | 0.042844 | -197.8282 | 17.6248 | -0.012848 | -0.22525 | -0.011847 | 0.092299 | 8.8286 | 9.0586 | 1.9786 | 21.7886 | 22.0195 | 22.2111 | 22.2782 | 22.1101 | 21.4333 | 20.2554 | 22.2073 | 22.3834 | 22.4142 | 22.37 | 22.004 | 21.2492 | 22.2818 | 17.2017 | 17.0184 | 16.0942 | 16.1813 | 16.193 | 17.0756 | 16.8346 | 22.391 | 22.1546 | 21.7241 | 22.0893 | 21.8069 | 21.3146 | 21.952 | 21.535 | 20.9195 | 20.1135 | 20.308 | 19.8721 | 19.8107 | -0.18676 | 0.052907 | 20.7866 | 22.1043 | 22.4146 | 20.1139 | 21.6947 | 22.1495 | 21.9677 | 21.7298 | 21.3035 | 21.8044 | 21.4692 | 21.0636 | 20.1944 | 20.2307 | 20.2707 | 20.1879 | 20.1116 |  | 20.2595 | 19.9263 | 20.1332 | 19.7902 | 20.1283 | 20.3515 |  | 20.4486 |  |  | 20.3279 | 20.3665 | 20.6519 | [5 empty] | 21.9544 | 20.3616 | 21.6996 | 22.0779 | 19.5602 | 21.1921 | 21.8107 | 19.4572 | 19.9947 | 21.1489 |  | 19.7219 | 20.9549 | 18.9154 | 19.7684 | 20.8442 | 19.4571 | 20.0212 | 19.0578 | 20.0981 | 19.118 | 20.2349 | 18.8763 | 20.0682 | 21.0743 | 19.5133 | 19.8445 | 20.9953 | 18.9702 | 19.8261 | 20.8277 | 18.9756 | 20.0904 | 19.3207 | 19.8695 | 18.9679 | 20.1326 | -0.2923 | 20.947 | 0.048782 | 0.014811 | -27.011 | 3.0977 | 18.55 | -0.21 | 0.92553 | -0.45531 | -6.393 | 0.96705 | 0.24586 | -16.7068 | 4.9867 | 0.42433 | 0.42525 | 0.42886 | 0.38826 | 0.4832 | 0.43666 | 0.4278
42838.4156 | -403 | 22.8867 | 22.8511 | 22.8478 | 22.7708 | 22.4088 | 21.7537 | 22.7187 | 21.8236 | 22.3727 | 22.384 | 22.3644 | 22.054 | 21.274 | 22.2361 | 21.5629 | 21.7493 | 21.8803 | 21.068 | 21.1637 | 21.3882 | 20.4711 | 20.6168 | 20.9167 | 21.8929 | 21.6582 | 21.2958 | 20.3228 | 20.3696 | 20.4081 | 22.0463 | 21.6485 | 21.1774 | 21.9964 | 21.7294 | 21.3564 | 19.9377 | 20.4648 |  | 20.5548 | 20.107 | 20.1795 | 19.2862 |  | 16.7343 | 16.7154 | 16.4961 | 16.7044 | 16.7932 | 17.3431 | 18.059 | 15.5708 | 16.8409 | 15.9881 | 16.9328 | 17.889 | 44.7121 | 47.723 | 43.964 | 21.3846 |  |  | 0.57915 | 0.006507 | -28.8955 | 0.5815 | 0.11513 | -197.8565 | 17.6156 | -0.22641 | -0.09818 | 0.060114 | -0.10213 | 8.8292 | 9.0589 | 1.9794 | 21.7889 | 22.0159 | 22.213 | 22.2792 | 22.11 | 21.444 | 20.2604 | 22.213 | 22.3856 | 22.4215 | 22.3779 | 22.0119 | 21.2487 | 22.2878 | 17.207 | 17.0089 | 16.1053 | 16.1844 | 16.2068 | 17.0766 | 16.8406 | 22.3902 | 22.1521 | 21.7144 | 22.0847 | 21.805 | 21.3129 | 21.9427 | 21.5271 | 20.9155 | 20.1158 | 20.3071 | 19.8613 | 19.7914 | -0.017092 | 0.067932 | 20.7764 | 22.1061 | 22.4133 | 20.1166 | 21.692 | 22.1438 | 21.9667 | 21.73 | 21.3017 | 21.8004 | 21.4638 | 21.0623 | 20.1902 | 20.2263 | 20.2635 | 20.1828 | 20.1082 |  | 20.2522 | 19.9382 | 20.1333 | 19.788 | 20.12 | 20.3457 |  | 20.4503 |  |  | 20.3272 | 20.3663 | 20.6467 | [5 empty] | 21.9626 | 20.3552 | 21.6936 | 22.0742 | 19.562 | 21.1879 | 21.8116 | 19.4619 | 20.0019 | 21.1673 |  | 19.7269 | 20.9685 | 18.93 | 19.7769 | 20.8456 | 19.4639 | 20.0173 | 19.0603 | 20.1032 | 19.1209 | 20.2368 | 18.8905 | 20.067 | 21.0742 | 19.5193 | 19.8357 | 21.0047 | 18.9765 | 19.8266 | 20.826 | 18.9824 | 20.0837 | 19.3209 | 19.8824 | 18.9694 | 20.1295 | -0.13573 | 20.9474 | 0.048782 | 0.014491 | -27.0523 | 3.0977 | 0.29 | -0.09 | 0.90868 | 0.09571 | -6.3779 | 0.90478 | 0.40302 | -16.7074 | 4.9852 | 0.42418 | 0.42492 | 0.42865 | 0.38779 | 0.48268 | 0.43648 | 0.42841
42838.4156 | -402 | 22.8904 | 22.8591 | 22.8472 | 22.7828 | 22.4184 | 21.7534 | 22.7212 | 21.8222 | 22.375 | 22.3898 | 22.3765 | 22.0474 | 21.2706 | 22.2503 | 21.5673 | 21.748 | 21.8736 | 21.0702 | 21.1658 | 21.3852 | 20.471 | 20.6177 | 20.916 | 21.8852 | 21.6548 | 21.293 | 20.3229 | 20.3654 | 20.403 | 22.0402 | 21.6447 | 21.1742 | 21.985 | 21.7318 | 21.3575 | 19.932 | 20.4618 |  | 20.5553 | 20.0984 | 20.1755 | 19.2889 |  | 16.7233 | 16.7075 | 16.4848 | 16.6864 | 16.773 | 17.3289 | 18.0409 | 15.6402 | 16.8212 | 15.9951 | 16.9223 | 17.8871 | 44.6974 | 47.7139 | 43.9542 | 21.383 |  |  | 0.60938 | -0.071033 | -28.7161 | 0.26872 | 0.25049 | -197.8151 | 18.0466 | -0.13573 | -0.19061 | 0.21285 | -0.11984 | 8.8296 | 9.0593 | 1.979 | 21.7865 | 22.0156 | 22.2068 | 22.2734 | 22.1104 | 21.436 | 20.257 | 22.2124 | 22.3847 | 22.4233 | 22.375 | 22.0042 | 21.2429 | 22.2904 | 17.2043 | 17.0279 | 16.1164 | 16.1838 | 16.2122 | 17.0762 | 16.8524 | 22.3911 | 22.1584 | 21.7122 | 22.0923 | 21.8028 | 21.3198 | 21.9546 | 21.5459 | 20.9257 | 20.1167 | 20.3199 | 19.8735 | 19.7894 | -0.050121 | -0.14262 | 20.7738 | 22.1074 | 22.4055 | 20.1163 | 21.6917 | 22.1409 | 21.9643 | 21.7303 | 21.2985 | 21.7998 | 21.4638 | 21.0619 | 20.1878 | 20.2255 | 20.263 | 20.1851 | 20.1087 |  | 20.2514 | 19.9448 | 20.1273 | 19.7873 | 20.1234 | 20.3432 |  | 20.4477 |  |  | 20.3385 | 20.3833 | 20.6439 | [5 empty] | 21.9573 | 20.3643 | 21.6932 | 22.0696 | 19.5646 | 21.1804 | 21.8077 | 19.4603 | 19.9921 | 21.1559 |  | 19.7234 | 20.9459 | 18.9184 | 19.7766 | 20.8319 | 19.4574 | 20.0097 | 19.0487 | 20.0906 | 19.1116 | 20.2289 | 18.8719 | 20.0633 | 21.0654 | 19.517 | 19.8334 | 20.9928 | 18.9656 | 19.8293 | 20.8257 | 18.9744 | 20.0864 | 19.3226 | 19.8792 | 18.9631 | 20.1333 | 0.061268 | 20.9473 | 0.048407 | 0.013199 | -27.0595 | 3.0977 | -3.94 | -0.02 | 0.93208 | -0.31622 | -6.358 | 0.61505 | 0.59446 | -16.7053 | 5.0457 | 0.42414 | 0.42454 | 0.42878 | 0.38805 | 0.48281 | 0.43621 | 0.4285
42838.4156 | -401 | 22.8896 | 22.8625 | 22.8375 | 22.7736 | 22.4078 | 21.7482 | 22.7131 | 21.8181 | 22.3655 | 22.3786 | 22.363 | 22.0379 | 21.2682 | 22.2285 | 21.5795 | 21.7558 | 21.8749 | 21.0784 | 21.1806 | 21.3923 | 20.4705 | 20.6234 | 20.9111 | 21.8889 | 21.66 | 21.3049 | 20.3212 | 20.3733 | 20.4038 | 22.0374 | 21.6456 | 21.1718 | 21.9936 | 21.7314 | 21.3549 | 19.9302 | 20.464 |  | 20.5581 | 20.0988 | 20.1761 | 19.2882 |  | 16.7403 | 16.718 | 16.4839 | 16.6848 | 16.7636 | 17.3208 | 18.0249 | 15.741 | 16.8326 | 16.0062 | 16.9277 | 17.8827 | 44.6998 | 47.7104 | 43.9481 | 21.3846 |  |  | 0.46875 | 0.051847 | -29.2135 | 0.73198 | 0.14272 | -197.8302 | 17.9868 | -0.19552 | -0.19704 | -0.08234 | -0.000924 | 8.8285 | 9.0583 | 1.9788 | 21.7868 | 22.0119 | 22.2078 | 22.2726 | 22.1042 | 21.4319 | 20.25 | 22.2044 | 22.3821 | 22.4163 | 22.3715 | 22.0059 | 21.2414 | 22.2852 | 17.1934 | 17.0601 | 16.0932 | 16.1964 | 16.1929 | 17.0747 | 16.8393 | 22.3949 | 22.1608 | 21.7128 | 22.0924 | 21.8125 | 21.316 | 21.9569 | 21.5464 | 20.9231 | 20.1213 | 20.3172 | 19.8682 | 19.7851 | 0.039332 | -0.11637 | 20.7693 | 22.1095 | 22.4038 | 20.1151 | 21.6892 | 22.1466 | 21.9657 | 21.7307 | 21.2991 | 21.8001 | 21.464 | 21.0618 | 20.1856 | 20.2247 | 20.2693 | 20.1805 | 20.0923 |  | 20.2454 | 19.9492 | 20.1292 | 19.784 | 20.1097 | 20.3367 |  | 20.4449 |  |  | 20.341 | 20.3862 | 20.6524 | [5 empty] | 21.9557 | 20.3734 | 21.6966 | 22.0779 | 19.5664 | 21.1887 | 21.8122 | 19.4502 | 19.9778 | 21.1439 |  | 19.7245 | 20.9583 | 18.9269 | 19.7664 | 20.8465 | 19.457 | 20.0038 | 19.0568 | 20.0963 | 19.1028 | 20.2302 | 18.8781 | 20.0609 | 21.0714 | 19.5116 | 19.8295 | 20.9929 | 18.9768 | 19.8341 | 20.8353 | 18.985 | 20.0864 | 19.3261 | 19.8863 | 18.969 | 20.1292 | -0.23182 | 20.9465 | 0.046564 | 0.013046 | -27.1034 | 3.0976 | -24.98 | -0.13 | 0.81749 | 0.27016 | -6.413 | 1.0151 | 0.44871 | -16.7057 | 5.0373 | 0.42439 | 0.42448 | 0.42841 | 0.38908 | 0.48387 | 0.43617 | 0.42877
42838.4156 | -400 | 22.8892 | 22.8526 | 22.8451 | 22.7711 | 22.406 | 21.7532 | 22.7157 | 21.8201 | 22.3706 | 22.3802 | 22.3627 | 22.0397 | 21.2646 | 22.2415 | 21.5683 | 21.7434 | 21.871 | 21.0694 | 21.1713 | 21.3917 | 20.4691 | 20.6205 | 20.9087 | 21.893 | 21.6575 | 21.2939 | 20.322 | 20.3662 | 20.4027 | 22.0368 | 21.6514 | 21.1829 | 21.9856 | 21.7338 | 21.3572 | 19.9304 | 20.4679 |  | 20.5518 | 20.0919 | 20.1783 | 19.2764 |  | 16.7431 | 16.7166 | 16.4818 | 16.6728 | 16.7499 | 17.312 | 18.002 | 15.8077 | 16.8483 | 16.0159 | 16.9305 | 17.882 | 44.6986 | 47.7076 | 43.9364 | 21.3854 |  |  | 0.57915 | 0.14844 | -29.7668 | 0.56311 | 0.11973 | -197.8381 | 17.4572 | -0.29015 | -0.041162 | 0.055918 | 0.041434 | 8.8294 | 9.0591 | 1.9785 | 21.7918 | 22.0236 | 22.2125 | 22.2831 | 22.1089 | 21.442 | 20.2569 | 22.2112 | 22.3799 | 22.4226 | 22.3762 | 22.0101 | 21.2471 | 22.2897 | 17.1851 | 17.0885 | 16.073 | 16.2179 | 16.1926 | 17.0771 | 16.8405 | 22.3843 | 22.158 | 21.7151 | 22.0812 | 21.8079 | 21.3083 | 21.9506 | 21.5315 | 20.9148 | 20.1144 | 20.3084 | 19.8626 | 19.7718 | 0.14491 | -0.022983 | 20.7708 | 22.1063 | 22.4089 | 20.12 | 21.6922 | 22.1441 | 21.9701 | 21.7363 | 21.3044 | 21.804 | 21.4693 | 21.0656 | 20.1892 | 20.2249 | 20.2708 | 20.1865 | 20.0812 |  | 20.2456 | 19.9448 | 20.1269 | 19.7825 | 20.1149 | 20.3363 |  | 20.4487 |  |  | 20.3437 | 20.3917 | 20.6591 | [5 empty] | 21.9673 | 20.3711 | 21.6928 | 22.0783 | 19.5753 | 21.189 | 21.8093 | 19.4498 | 19.9859 | 21.1473 |  | 19.7245 | 20.9597 | 18.9287 | 19.7722 | 20.8377 | 19.4579 | 20.0172 | 19.0648 | 20.0982 | 19.1155 | 20.2291 | 18.8792 | 20.0647 | 21.073 | 19.5161 | 19.8363 | 20.9988 | 18.9712 | 19.8333 | 20.8325 | 18.9953 | 20.0906 | 19.327 | 19.8811 | 18.963 | 20.1269 | -0.13518 | 20.9472 | 0.046908 | 0.013453 | -27.1546 | 3.0977 | 6.88 | 0.14 | 0.90867 | 0.45714 | -6.4734 | 0.89035 | 0.41097 | -16.7058 | 4.9625 | 0.42471 | 0.42452 | 0.42863 | 0.3903 | 0.48626 | 0.43651 | 0.42891
42838.4157 | -399 | 22.8856 | 22.8505 | 22.8383 | 22.7696 | 22.4057 | 21.7458 | 22.7079 | 21.8156 | 22.3611 | 22.3768 | 22.3665 | 22.0381 | 21.263 | 22.2294 | 21.562 | 21.7398 | 21.877 | 21.0686 | 21.1615 | 21.3899 | 20.469 | 20.6179 | 20.9061 | 21.8868 | 21.6553 | 21.2849 | 20.323 | 20.3607 | 20.4058 | 22.0391 | 21.6499 | 21.1706 | 21.991 | 21.7277 | 21.35 | 19.9332 | 20.4673 |  | 20.5509 | 20.0976 | 20.1841 | 19.2698 |  | 16.736 | 16.7286 | 16.4613 | 16.6525 | 16.7271 | 17.2684 | 17.9554 | 15.8187 | 16.8287 | 16.0502 | 16.9186 | 17.876 | 44.685 | 47.6967 | 43.9279 | 21.3837 |  |  | 0.58966 | -0.18603 | -30.3582 | 0.76418 | 0.19398 | -197.8453 | 17.8791 | -0.3506 | 0.23186 | -0.094089 | -0.050053 | 8.8283 | 9.058 | 1.9784 | 21.7796 | 22.0169 | 22.2042 | 22.2774 | 22.1097 | 21.4385 | 20.2496 | 22.2061 | 22.3753 | 22.4147 | 22.3772 | 21.9957 | 21.2388 | 22.2859 | 17.1766 | 17.1027 | 16.0197 | 16.224 | 16.2015 | 17.0675 | 16.8369 | 22.3875 | 22.1588 | 21.7163 | 22.0916 | 21.8113 | 21.3141 | 21.9574 | 21.5302 | 20.9191 | 20.1073 | 20.3155 | 19.8678 | 19.7601 | -0.020238 | -0.11067 | 20.7726 | 22.1065 | 22.4072 | 20.1141 | 21.6942 | 22.1496 | 21.9669 | 21.7299 | 21.3055 | 21.8022 | 21.4658 | 21.0679 | 20.1852 | 20.2208 | 20.2632 | 20.1832 | 20.0773 |  | 20.2552 | 19.9601 | 20.1338 | 19.7801 | 20.1182 | 20.3483 |  | 20.4529 |  |  | 20.3331 | 20.3847 | 20.6547 | [5 empty] | 21.959 | 20.3562 | 21.6895 | 22.0697 | 19.5621 | 21.182 | 21.7997 | 19.455 | 19.9804 | 21.1523 |  | 19.7293 | 20.96 | 18.9225 | 19.7746 | 20.8369 | 19.4592 | 20.0099 | 19.0638 | 20.0955 | 19.1127 | 20.2283 | 18.8663 | 20.0621 | 21.067 | 19.5217 | 19.8347 | 20.9931 | 18.9779 | 19.8289 | 20.8292 | 18.9982 | 20.0919 | 19.327 | 19.8831 | 18.9669 | 20.1206 | -0.16133 | 20.947 | 0.047885 | 0.013344 | -26.959 | 3.0976 | 14.92 | -0.15 | 0.91688 | -0.51176 | -6.5375 | 1.0372 | 0.52307 | -16.7048 | 5.0217 | 0.42514 | 0.42433 | 0.42881 | 0.39011 | 0.49176 | 0.43678 | 0.429
42838.4157 | -398 | 22.8852 | 22.8511 | 22.839 | 22.7751 | 22.4068 | 21.7525 | 22.7153 | 21.8166 | 22.3693 | 22.3796 | 22.371 | 22.0465 | 21.2706 | 22.2324 | 21.5694 | 21.7522 | 21.8799 | 21.073 | 21.1656 | 21.3882 | 20.4729 | 20.6187 | 20.9115 | 21.8866 | 21.6575 | 21.2879 | 20.3239 | 20.3692 | 20.4078 | 22.0457 | 21.6523 | 21.1751 | 21.991 | 21.7276 | 21.3527 | 19.9315 | 20.4729 |  | 20.5509 | 20.0975 | 20.18 | 19.2516 |  | 16.7279 | 16.7164 | 16.46 | 16.6503 | 16.7148 | 17.2374 | 17.9059 | 15.8183 | 16.8303 | 16.0982 | 16.921 | 17.8799 | 44.6823 | 47.6981 | 43.9275 | 21.3886 |  |  | 0.71911 | -0.1604 | -30.5895 | 0.22141 | 0.26824 | -197.8775 | 17.3133 | -0.13836 | 0.035705 | 0.048365 | -0.067239 | 8.8287 | 9.0584 | 1.9792 | 21.7835 | 22.0058 | 22.2099 | 22.2754 | 22.1126 | 21.4299 | 20.2594 | 22.2098 | 22.3763 | 22.4143 | 22.3663 | 22.0003 | 21.2493 | 22.2864 | 17.1866 | 17.0991 | 16.0053 | 16.2315 | 16.2097 | 17.0756 | 16.8439 | 22.3876 | 22.1561 | 21.7058 | 22.0928 | 21.8061 | 21.3089 | 21.9439 | 21.532 | 20.9176 | 20.1073 | 20.3058 | 19.8574 | 19.7588 | 0.032255 | 0.013345 | 20.7705 | 22.1054 | 22.4009 | 20.1046 | 21.6893 | 22.1463 | 21.9589 | 21.7264 | 21.2917 | 21.7937 | 21.4577 | 21.0629 | 20.178 | 20.2156 | 20.2572 | 20.1701 | 20.0733 |  | 20.2601 | 19.9725 | 20.1362 | 19.7893 | 20.1247 | 20.3486 |  | 20.4465 |  |  | 20.3296 | 20.387 | 20.6584 | [5 empty] | 21.9529 | 20.3549 | 21.6907 | 22.0668 | 19.5543 | 21.1812 | 21.7987 | 19.4491 | 19.9821 | 21.149 |  | 19.7257 | 20.9533 | 18.9242 | 19.7678 | 20.8317 | 19.4544 | 20.0142 | 19.0515 | 20.0956 | 19.1057 | 20.2171 | 18.8692 | 20.063 | 21.0756 | 19.5152 | 19.8234 | 20.9931 | 18.9843 | 19.8303 | 20.8219 | 18.9962 | 20.0936 | 19.3195 | 19.8853 | 18.9688 | 20.1105 | -0.15521 | 20.9454 | 0.048948 | 0.01505 | -27.0223 | 3.0977 | -0.38 | -0.12 | 1.0125 | -0.47519 | -6.5622 | 0.55829 | 0.61506 | -16.7053 | 4.9414 | 0.42541 | 0.42407 | 0.42877 | 0.38995 | 0.49418 | 0.43723 | 0.42903
42838.4157 | -397 | 22.8864 | 22.8545 | 22.8394 | 22.7751 | 22.4155 | 21.7518 | 22.7183 | 21.8187 | 22.3722 | 22.3791 | 22.3692 | 22.0415 | 21.2658 | 22.2355 | 21.5719 | 21.7471 | 21.8826 | 21.0709 | 21.1667 | 21.3836 | 20.4718 | 20.622 | 20.9156 | 21.8933 | 21.6526 | 21.2953 | 20.325 | 20.3709 | 20.4011 | 22.0471 | 21.6581 | 21.1746 | 21.9951 | 21.7296 | 21.3573 | 19.9312 | 20.474 |  | 20.5577 | 20.0987 | 20.1827 | 19.2349 |  | 16.7251 | 16.7194 | 16.4455 | 16.6363 | 16.7049 | 17.2118 | 17.8616 | 15.8269 | 16.8245 | 16.124 | 16.9225 | 17.8825 | 44.6859 | 47.6853 | 43.9133 | 21.3883 |  |  | 0.61201 | -0.29577 | -30.1493 | 0.39883 | 0.19464 | -197.867 | 17.7601 | -0.051616 | 0.10751 | 0.036616 | -0.086162 | 8.8291 | 9.0588 | 1.9788 | 21.7865 | 22.0116 | 22.2162 | 22.2803 | 22.1044 | 21.4342 | 20.2591 | 22.1944 | 22.38 | 22.4163 | 22.3731 | 21.9962 | 21.2373 | 22.2832 | 17.2113 | 17.0574 | 15.9994 | 16.2454 | 16.2467 | 17.0732 | 16.8424 | 22.3859 | 22.1491 | 21.715 | 22.0943 | 21.8096 | 21.3162 | 21.9464 | 21.5396 | 20.9182 | 20.1106 | 20.305 | 19.8544 | 19.7667 | -0.15628 | 0.070405 | 20.7758 | 22.1084 | 22.4053 | 20.1141 | 21.6926 | 22.1414 | 21.9564 | 21.7294 | 21.2931 | 21.7916 | 21.4596 | 21.061 | 20.1786 | 20.2197 | 20.2583 | 20.1738 | 20.0731 |  | 20.2494 | 19.9674 | 20.1328 | 19.7841 | 20.1189 | 20.3438 |  | 20.4451 |  |  | 20.3312 | 20.3909 | 20.6613 | [5 empty] | 21.9572 | 20.3648 | 21.6841 | 22.0701 | 19.5527 | 21.1832 | 21.8091 | 19.4502 | 19.9827 | 21.1426 |  | 19.7235 | 20.9495 | 18.9181 | 19.7718 | 20.8335 | 19.4613 | 20.0135 | 19.0484 | 20.0917 | 19.1053 | 20.2154 | 18.8752 | 20.066 | 21.0745 | 19.5065 | 19.8277 | 20.9953 | 18.9825 | 19.836 | 20.8192 | 19.0017 | 20.0872 | 19.3247 | 19.8844 | 18.9648 | 20.1201 | -0.085462 | 20.9466 | 0.049925 | 0.015711 | -27.1192 | 3.0976 | 2.37 | -0.07 | 0.93409 | -0.64527 | -6.5149 | 0.74931 | 0.5239 | -16.7041 | 5.0045 | 0.42506 | 0.42409 | 0.42872 | 0.38692 | 0.49466 | 0.43769 | 0.42892
42838.4157 | -396 | 22.8963 | 22.8581 | 22.8455 | 22.7792 | 22.4173 | 21.7535 | 22.7198 | 21.8248 | 22.3721 | 22.3808 | 22.3696 | 22.0454 | 21.2712 | 22.2334 | 21.5757 | 21.7516 | 21.8877 | 21.0749 | 21.1775 | 21.3932 | 20.4735 | 20.6282 | 20.9205 | 21.901 | 21.6583 | 21.3014 | 20.3283 | 20.3743 | 20.4102 | 22.0463 | 21.6521 | 21.1742 | 21.9984 | 21.7282 | 21.3568 | 19.9383 | 20.4706 |  | 20.565 | 20.0991 | 20.1832 | 19.2176 |  | 16.7276 | 16.7145 | 16.44 | 16.6305 | 16.6915 | 17.1908 | 17.8235 | 15.8424 | 16.8245 | 16.1311 | 16.9174 | 17.8788 | 44.6898 | 47.6786 | 43.8995 | 21.377 |  |  | 0.64223 | -0.052633 | -30.4699 | 0.55391 | 0.11644 | -197.8217 | 17.3981 | -0.077244 | -0.018199 | -0.14507 | 0.02147 | 8.8286 | 9.0581 | 1.9785 | 21.7829 | 22.0086 | 22.2065 | 22.2696 | 22.0987 | 21.4349 | 20.2544 | 22.2003 | 22.3792 | 22.4169 | 22.3623 | 22.0031 | 21.238 | 22.2813 | 17.2258 | 17.0625 | 16.017 | 16.269 | 16.2457 | 17.0745 | 16.838 | 22.3805 | 22.1546 | 21.7122 | 22.0877 | 21.8093 | 21.3182 | 21.9498 | 21.5395 | 20.9186 | 20.115 | 20.3038 | 19.8537 | 19.7709 | -0.011784 | 0.011443 | 20.7841 | 22.1131 | 22.4171 | 20.1174 | 21.6954 | 22.1494 | 21.9623 | 21.7307 | 21.3032 | 21.8009 | 21.4663 | 21.0654 | 20.1884 | 20.2207 | 20.2664 | 20.1851 | 20.0731 |  | 20.252 | 19.9673 | 20.1306 | 19.7806 | 20.1191 | 20.3442 |  | 20.4471 |  |  | 20.3263 | 20.3816 | 20.6527 | [5 empty] | 21.9621 | 20.3657 | 21.6848 | 22.0686 | 19.553 | 21.1812 | 21.8094 | 19.446 | 19.9773 | 21.1419 |  | 19.7243 | 20.9559 | 18.9158 | 19.7689 | 20.8321 | 19.4708 | 20.0143 | 19.0528 | 20.0917 | 19.1001 | 20.215 | 18.8734 | 20.0643 | 21.07 | 19.5023 | 19.8284 | 20.9913 | 18.9757 | 19.8384 | 20.8296 | 19.0079 | 20.0952 | 19.3243 | 19.8868 | 18.9705 | 20.1185 | -0.26169 | 20.9463 | 0.049249 | 0.015536 | -27.0256 | 3.0977 | -25.48 | 0.01 | 0.95689 | -0.2722 | -6.5494 | 0.88304 | 0.4052 | -16.7016 | 4.953 | 0.42515 | 0.42402 | 0.42882 | 0.38546 | 0.49218 | 0.43841 | 0.42895
42838.4157 | -395 | 22.8935 | 22.8503 | 22.8371 | 22.7748 | 22.4105 | 21.7443 | 22.719 | 21.8075 | 22.3719 | 22.3749 | 22.3617 | 22.0497 | 21.2648 | 22.2333 | 21.5766 | 21.7484 | 21.8834 | 21.0707 | 21.1702 | 21.3893 | 20.475 | 20.6207 | 20.9182 | 21.89 | 21.6579 | 21.2961 | 20.3234 | 20.3692 | 20.4067 | 22.0451 | 21.6411 | 21.1719 | 21.9875 | 21.7244 | 21.3407 | 19.9422 | 20.4607 |  | 20.5458 | 20.09 | 20.1811 | 19.1921 |  | 16.7237 | 16.7181 | 16.4453 | 16.6327 | 16.6837 | 17.18 | 17.806 | 15.8584 | 16.83 | 16.1479 | 16.9241 | 17.8803 | 44.7084 | 47.6745 | 43.8991 | 21.3822 |  |  | 0.64946 | -0.35097 | -30.1309 | 0.52631 | 0.15981 | -197.8519 | 17.5505 | -0.18041 | -0.010415 | -0.195 | 0.16434 | 8.8278 | 9.0577 | 1.9784 | 21.7802 | 22.0118 | 22.2117 | 22.2704 | 22.1007 | 21.4321 | 20.2445 | 22.2045 | 22.3753 | 22.4125 | 22.3597 | 22.0007 | 21.2395 | 22.279 | 17.2191 | 17.0427 | 16.0264 | 16.2685 | 16.2349 | 17.0652 | 16.8378 | 22.3847 | 22.1512 | 21.7139 | 22.0874 | 21.807 | 21.3121 | 21.9502 | 21.5407 | 20.9168 | 20.1104 | 20.3034 | 19.8487 | 19.7833 | -0.10006 | 0.14553 | 20.7888 | 22.115 | 22.415 | 20.1155 | 21.6967 | 22.152 | 21.967 | 21.7332 | 21.3028 | 21.8016 | 21.4694 | 21.0684 | 20.1922 | 20.226 | 20.2693 | 20.1849 | 20.0736 |  | 20.2501 | 19.9771 | 20.1293 | 19.7863 | 20.1186 | 20.347 |  | 20.4449 |  |  | 20.3248 | 20.3753 | 20.6512 | [5 empty] | 21.9614 | 20.3677 | 21.6888 | 22.0723 | 19.5579 | 21.1827 | 21.81 | 19.4432 | 19.9749 | 21.1466 |  | 19.7258 | 20.9498 | 18.9188 | 19.7597 | 20.8282 | 19.4738 | 20.0115 | 19.0564 | 20.0937 | 19.102 | 20.2162 | 18.8717 | 20.0587 | 21.0553 | 19.5025 | 19.8239 | 20.9908 | 18.9715 | 19.8429 | 20.8248 | 19.0136 | 20.0959 | 19.3223 | 19.8864 | 18.9636 | 20.1177 | -0.13202 | 20.9459 | 0.049015 | 0.014237 | -26.9785 | 3.0976 | -32.29 | -0.2 | 0.96225 | -0.70291 | -6.5129 | 0.86077 | 0.4747 | -16.7026 | 4.9746 | 0.42507 | 0.42371 | 0.42865 | 0.38513 | 0.49111 | 0.43924 | 0.42846
42838.4157 | -394 | 22.8899 | 22.8621 | 22.8491 | 22.7756 | 22.4039 | 21.7507 | 22.7251 | 21.8145 | 22.3784 | 22.3843 | 22.3699 | 22.0479 | 21.274 | 22.2429 | 21.5755 | 21.746 | 21.883 | 21.0726 | 21.1685 | 21.3938 | 20.4769 | 20.6206 | 20.919 | 21.8892 | 21.661 | 21.2971 | 20.3256 | 20.3668 | 20.4049 | 22.0441 | 21.6455 | 21.1701 | 21.9887 | 21.7266 | 21.3405 | 19.9377 | 20.4669 |  | 20.5588 | 20.0934 | 20.1905 | 19.1878 |  | 16.7277 | 16.7223 | 16.4407 | 16.6141 | 16.6776 | 17.1666 | 17.7991 | 15.8667 | 16.8378 | 16.1342 | 16.9191 | 17.8828 | 44.733 | 47.6722 | 43.9 | 21.3877 |  |  | 0.61069 | -0.21297 | -29.8772 | 0.76024 | 0.090156 | -197.8769 | 17.8699 | -0.16596 | -0.084168 | -0.16458 | 0.085355 | 8.829 | 9.0586 | 1.9784 | 21.7841 | 22.0138 | 22.2181 | 22.2738 | 22.1052 | 21.4334 | 20.2518 | 22.2093 | 22.3787 | 22.4115 | 22.3679 | 22.0065 | 21.2426 | 22.2839 | 17.2454 | 17.0439 | 16.0499 | 16.2566 | 16.2385 | 17.079 | 16.8412 | 22.382 | 22.1514 | 21.7147 | 22.0872 | 21.7985 | 21.313 | 21.9466 | 21.5337 | 20.9108 | 20.1049 | 20.2927 | 19.8461 | 19.7954 | -0.13879 | 0.10426 | 20.7907 | 22.1042 | 22.4066 | 20.1135 | 21.6941 | 22.1499 | 21.9665 | 21.7352 | 21.296 | 21.7948 | 21.4649 | 21.0664 | 20.1893 | 20.2205 | 20.2624 | 20.1817 | 20.0697 |  | 20.2451 | 19.9799 | 20.1303 | 19.7825 | 20.1185 | 20.3475 |  | 20.4492 |  |  | 20.329 | 20.3788 | 20.6579 | [5 empty] | 21.9627 | 20.369 | 21.6923 | 22.0708 | 19.5577 | 21.1794 | 21.8119 | 19.4462 | 19.9711 | 21.1478 |  | 19.7367 | 20.9467 | 18.9209 | 19.7601 | 20.8277 | 19.4726 | 20.0119 | 19.0538 | 20.1046 | 19.1037 | 20.2175 | 18.8719 | 20.0609 | 21.0628 | 19.5032 | 19.8276 | 20.9991 | 18.9608 | 19.8394 | 20.8295 | 19.0227 | 20.0992 | 19.334 | 19.8891 | 18.9657 | 20.1247 | -0.065429 | 20.9466 | 0.04939 | 0.01537 | -27.0131 | 3.0976 | 3.45 | -0.1 | 0.93309 | -0.54756 | -6.4855 | 1.0345 | 0.35653 | -16.7032 | 5.0195 | 0.42501 | 0.42366 | 0.42875 | 0.38381 | 0.4889 | 0.43921 | 0.42794
42838.4157 | -393 | 22.8925 | 22.855 | 22.8403 | 22.7694 | 22.4081 | 21.7466 | 22.7165 | 21.815 | 22.3685 | 22.3742 | 22.3635 | 22.0444 | 21.2694 | 22.2323 | 21.5707 | 21.7456 | 21.882 | 21.0733 | 21.1691 | 21.3908 | 20.4685 | 20.6167 | 20.9216 | 21.8909 | 21.6557 | 21.2978 | 20.3257 | 20.3648 | 20.4063 | 22.0456 | 21.6486 | 21.183 | 21.9907 | 21.7343 | 21.3453 | 19.9359 | 20.4677 |  | 20.5557 | 20.0984 | 20.1866 | 19.172 |  | 16.7258 | 16.7223 | 16.4377 | 16.6123 | 16.6686 | 17.1758 | 17.8098 | 15.8533 | 16.827 | 16.0887 | 16.9252 | 17.877 | 44.7477 | 47.6693 | 43.9024 | 21.3793 |  |  | 0.53578 | -0.12557 | -29.78 | 0.55916 | 0.19398 | -197.8374 | 17.5821 | -0.15216 | 0.1799 | -0.21074 | 0.021991 | 8.8291 | 9.0589 | 1.9787 | 21.7833 | 22.0075 | 22.2073 | 22.2721 | 22.101 | 21.4266 | 20.2429 | 22.197 | 22.3775 | 22.4046 | 22.3674 | 21.9988 | 21.2334 | 22.2792 | 17.2526 | 16.9978 | 16.0642 | 16.2307 | 16.2179 | 17.07 | 16.8374 | 22.3873 | 22.1456 | 21.7069 | 22.0839 | 21.8002 | 21.3079 | 21.9509 | 21.5376 | 20.911 | 20.1048 | 20.3006 | 19.8442 | 19.7902 | 0.051521 | 0.063558 | 20.7834 | 22.0977 | 22.4059 | 20.1055 | 21.6919 | 22.1442 | 21.9621 | 21.729 | 21.2905 | 21.7927 | 21.464 | 21.0619 | 20.1874 | 20.2094 | 20.254 | 20.179 | 20.0735 |  | 20.238 | 19.9774 | 20.127 | 19.78 | 20.1172 | 20.3496 |  | 20.4465 |  |  | 20.3266 | 20.3734 | 20.6509 | [5 empty] | 21.9607 | 20.3551 | 21.6944 | 22.0665 | 19.5551 | 21.1818 | 21.8111 | 19.4468 | 19.9728 | 21.1424 |  | 19.742 | 20.9473 | 18.9253 | 19.7648 | 20.8251 | 19.4691 | 20.0102 | 19.0534 | 20.1056 | 19.1064 | 20.2112 | 18.8736 | 20.0592 | 21.0654 | 19.5001 | 19.8246 | 20.9946 | 18.9574 | 19.8413 | 20.83 | 19.0267 | 20.1024 | 19.3342 | 19.8862 | 18.9683 | 20.1195 | -0.29972 | 20.9462 | 0.048708 | 0.013729 | -27.0334 | 3.0976 | 4.57 | 0.06 | 0.87399 | -0.42045 | -6.4749 | 0.88724 | 0.52298 | -16.7018 | 4.979 | 0.42467 | 0.42362 | 0.42877 | 0.38196 | 0.48687 | 0.43959 | 0.42808
42838.4157 | -392 | 22.8978 | 22.8634 | 22.8479 | 22.7808 | 22.4096 | 21.7563 | 22.7181 | 21.8148 | 22.3751 | 22.3817 | 22.3666 | 22.0443 | 21.2717 | 22.2346 | 21.5756 | 21.7532 | 21.8855 | 21.0792 | 21.1755 | 21.3951 | 20.4749 | 20.6267 | 20.9243 | 21.8944 | 21.6612 | 21.3028 | 20.3245 | 20.3673 | 20.4079 | 22.0462 | 21.6503 | 21.1768 | 21.9847 | 21.7265 | 21.3513 | 19.9344 | 20.4736 |  | 20.5604 | 20.0944 | 20.1898 | 19.161 |  | 16.7352 | 16.7344 | 16.4441 | 16.6012 | 16.6556 | 17.1685 | 17.8218 | 15.8835 | 16.8218 | 16.0444 | 16.9254 | 17.876 | 44.7672 | 47.6606 | 43.9001 | 21.381 |  |  | 0.73357 | -0.27474 | -30.238 | 0.65181 | 0.021816 | -197.8578 | 17.3521 | -0.46231 | -0.047584 | -0.36221 | 0.037442 | 8.8292 | 9.0589 | 1.9793 | 21.7804 | 22.0095 | 22.2021 | 22.2747 | 22.1047 | 21.4315 | 20.2492 | 22.2018 | 22.38 | 22.4103 | 22.3713 | 22.0073 | 21.2383 | 22.2865 | 17.2669 | 16.996 | 16.103 | 16.2247 | 16.2026 | 17.0583 | 16.8379 | 22.3821 | 22.1481 | 21.7128 | 22.0845 | 21.8041 | 21.3058 | 21.9384 | 21.5388 | 20.9215 | 20.1131 | 20.2988 | 19.8405 | 19.7895 | -0.027512 | 0.067932 | 20.7765 | 22.1002 | 22.4076 | 20.1021 | 21.693 | 22.141 | 21.9613 | 21.7262 | 21.2941 | 21.7903 | 21.4654 | 21.0622 | 20.1796 | 20.211 | 20.2467 | 20.1796 | 20.0706 |  | 20.2412 | 19.9803 | 20.1269 | 19.7737 | 20.1066 | 20.3454 |  | 20.439 |  |  | 20.3213 | 20.3645 | 20.6429 | [5 empty] | 21.9545 | 20.3547 | 21.6962 | 22.0662 | 19.5559 | 21.1884 | 21.8098 | 19.4443 | 19.9716 | 21.1397 |  | 19.742 | 20.9441 | 18.9251 | 19.757 | 20.8248 | 19.4733 | 20.0097 | 19.052 | 20.0992 | 19.1026 | 20.2114 | 18.8682 | 20.0567 | 21.0584 | 19.4953 | 19.8252 | 20.9937 | 18.9488 | 19.8419 | 20.8198 | 19.0259 | 20.1017 | 19.3359 | 19.88 | 18.9666 | 20.1117 | -0.040942 | 20.946 | 0.047191 | 0.01383 | -27.0689 | 3.0977 | -19.57 | -0.07 | 1.0227 | -0.62193 | -6.5246 | 0.95795 | 0.17538 | -16.7025 | 4.9463 | 0.42486 | 0.42353 | 0.4286 | 0.379 | 0.48261 | 0.43985 | 0.42837
42838.4158 | -391 | 22.8867 | 22.8543 | 22.8505 | 22.7854 | 22.4185 | 21.7484 | 22.72 | 21.8126 | 22.3765 | 22.3802 | 22.3691 | 22.0452 | 21.2694 | 22.2325 | 21.566 | 21.7494 | 21.8831 | 21.0728 | 21.1667 | 21.3922 | 20.4768 | 20.624 | 20.9071 | 21.888 | 21.6548 | 21.2989 | 20.3149 | 20.3679 | 20.4033 | 22.0407 | 21.6476 | 21.1792 | 21.9888 | 21.7228 | 21.3484 | 19.9327 | 20.473 |  | 20.554 | 20.0917 | 20.1929 | 19.1588 |  | 16.7441 | 16.7553 | 16.4457 | 16.6163 | 16.6525 | 17.1595 | 17.8231 | 15.9371 | 16.8308 | 16.0106 | 16.9251 | 17.879 | 44.7826 | 47.6577 | 43.8985 | 21.3867 |  |  | 0.65472 | -0.11637 | -30.8563 | 0.42774 | 0.14207 | -197.8085 | 17.8061 | -0.5116 | -0.10343 | -0.20738 | 0.15584 | 8.8288 | 9.0585 | 1.9791 | 21.7807 | 22.0048 | 22.199 | 22.2696 | 22.1047 | 21.4273 | 20.2472 | 22.1983 | 22.3694 | 22.4093 | 22.3695 | 21.9944 | 21.2332 | 22.2893 | 17.2914 | 17.022 | 16.1208 | 16.2236 | 16.1945 | 17.0743 | 16.8384 | 22.3905 | 22.1503 | 21.7172 | 22.0901 | 21.8072 | 21.3142 | 21.9472 | 21.5406 | 20.921 | 20.1135 | 20.3007 | 19.8447 | 19.7895 | -0.063096 | 0.013345 | 20.7822 | 22.1022 | 22.4082 | 20.1066 | 21.7018 | 22.1469 | 21.9662 | 21.7353 | 21.3008 | 21.7964 | 21.4681 | 21.0605 | 20.1831 | 20.217 | 20.2472 | 20.189 | 20.0693 |  | 20.2466 | 19.9915 | 20.125 | 19.7731 | 20.1116 | 20.3427 |  | 20.4512 |  |  | 20.3144 | 20.3703 | 20.6467 | [5 empty] | 21.9616 | 20.3597 | 21.6965 | 22.0769 | 19.5621 | 21.1875 | 21.8112 | 19.4423 | 19.9542 | 21.1295 |  | 19.7326 | 20.9309 | 18.9217 | 19.7506 | 20.8201 | 19.4655 | 20.0039 | 19.0468 | 20.1027 | 19.0954 | 20.2043 | 18.8721 | 20.0482 | 21.0515 | 19.4855 | 19.8187 | 20.9881 | 18.9453 | 19.831 | 20.8159 | 19.0261 | 20.0948 | 19.3294 | 19.8811 | 18.9619 | 20.1166 | -0.14056 | 20.9461 | 0.047817 | 0.014615 | -27.0537 | 3.0977 | -5.56 | -0.23 | 0.96613 | -0.40478 | -6.5912 | 0.77604 | 0.44755 | -16.7001 | 5.0105 | 0.42507 | 0.42316 | 0.42878 | 0.37815 | 0.4807 | 0.43985 | 0.42839
42838.4158 | -390 | 22.8889 | 22.8466 | 22.8417 | 22.7707 | 22.4107 | 21.7467 | 22.7164 | 21.816 | 22.3701 | 22.3805 | 22.3633 | 22.0453 | 21.2687 | 22.232 | 21.5625 | 21.7419 | 21.8811 | 21.0789 | 21.1748 | 21.3857 | 20.4709 | 20.6138 | 20.9156 | 21.8915 | 21.6502 | 21.2939 | 20.3269 | 20.3702 | 20.3962 | 22.0357 | 21.6431 | 21.1672 | 21.9842 | 21.7241 | 21.3422 | 19.9297 | 20.4659 |  | 20.548 | 20.0876 | 20.1868 | 19.1481 |  | 16.7377 | 16.754 | 16.4406 | 16.611 | 16.6452 | 17.1438 | 17.8053 | 15.9938 | 16.8234 | 15.951 | 16.9088 | 17.882 | 44.7774 | 47.6589 | 43.8881 | 21.3821 |  |  | 0.61529 | -0.12426 | -30.7249 | 0.81741 | 0.0757 | -197.8677 | 17.425 | -0.32826 | 0.022862 | -0.32277 | -0.016895 | 8.8284 | 9.0582 | 1.9789 | 21.7846 | 22.015 | 22.2108 | 22.2739 | 22.1 | 21.4389 | 20.2547 | 22.2043 | 22.3723 | 22.4153 | 22.3659 | 22.0045 | 21.2357 | 22.2886 | 17.3129 | 17.0098 | 16.1242 | 16.2088 | 16.1845 | 17.0697 | 16.8362 | 22.386 | 22.1497 | 21.7111 | 22.0912 | 21.806 | 21.313 | 21.9461 | 21.5414 | 20.9201 | 20.1084 | 20.2982 | 19.8424 | 19.7855 | -0.047565 | -0.09621 | 20.7817 | 22.1097 | 22.4043 | 20.1146 | 21.6978 | 22.1446 | 21.9664 | 21.7343 | 21.2976 | 21.8 | 21.4672 | 21.0567 | 20.1835 | 20.2142 | 20.2531 | 20.1865 | 20.0818 |  | 20.25 | 20.0007 | 20.1361 | 19.7867 | 20.1234 | 20.3535 |  | 20.4535 |  |  | 20.3103 | 20.3794 | 20.6561 | [5 empty] | 21.9646 | 20.3599 | 21.6979 | 22.0712 | 19.5683 | 21.1908 | 21.812 | 19.4498 | 19.9617 | 21.1324 |  | 19.7378 | 20.9397 | 18.9163 | 19.751 | 20.8264 | 19.4701 | 20.0053 | 19.0623 | 20.1064 | 19.1062 | 20.2135 | 18.8873 | 20.0606 | 21.0605 | 19.4907 | 19.8238 | 20.9947 | 18.9507 | 19.8391 | 20.8174 | 19.0345 | 20.1029 | 19.3341 | 19.8877 | 18.9653 | 20.1169 | -0.086761 | 20.9458 | 0.049212 | 0.016654 | -27.0564 | 3.0977 | -13.18 | -0.14 | 0.93658 | -0.41827 | -6.5772 | 1.0728 | 0.32669 | -16.7022 | 4.9565 | 0.42484 | 0.42328 | 0.4288 | 0.37522 | 0.48006 | 0.44005 | 0.42833
42838.4158 | -389 | 22.8946 | 22.8526 | 22.8423 | 22.7696 | 22.4068 | 21.7515 | 22.7264 | 21.8164 | 22.3728 | 22.3885 | 22.3641 | 22.05 | 21.2717 | 22.2342 | 21.5711 | 21.7417 | 21.8804 | 21.069 | 21.1613 | 21.3824 | 20.4656 | 20.6126 | 20.9036 | 21.8807 | 21.6556 | 21.2873 | 20.3274 | 20.366 | 20.3891 | 22.0409 | 21.6461 | 21.1736 | 21.9863 | 21.7306 | 21.3464 | 19.936 | 20.4712 |  | 20.5515 | 20.0942 | 20.1981 | 19.1486 |  | 16.7515 | 16.7607 | 16.4491 | 16.6054 | 16.6603 | 17.1482 | 17.8199 | 16.0166 | 16.8236 | 15.9005 | 16.9095 | 17.8792 | 44.776 | 47.6609 | 43.8793 | 21.3829 |  |  | 0.46941 | -0.2478 | -30.6375 | 0.65904 | 0.15521 | -197.8388 | 17.5827 | -0.40186 | -0.063541 | -0.2785 | 0.046469 | 8.8278 | 9.0577 | 1.9785 | 21.7946 | 22.0159 | 22.2157 | 22.2755 | 22.1015 | 21.4382 | 20.2626 | 22.209 | 22.3821 | 22.4249 | 22.3681 | 22.0126 | 21.2401 | 22.2942 | 17.3464 | 17.0234 | 16.1286 | 16.1964 | 16.2022 | 17.067 | 16.8321 | 22.3808 | 22.1535 | 21.7098 | 22.0851 | 21.807 | 21.3171 | 21.9481 | 21.5419 | 20.912 | 20.1124 | 20.2955 | 19.8492 | 19.7815 | -0.11166 | 0.011443 | 20.7803 | 22.1093 | 22.4057 | 20.1185 | 21.6915 | 22.1399 | 21.9642 | 21.728 | 21.2954 | 21.7999 | 21.461 | 21.0568 | 20.1764 | 20.2105 | 20.2549 | 20.1868 | 20.0802 |  | 20.2484 | 19.9948 | 20.1294 | 19.7787 | 20.1215 | 20.3516 |  | 20.4511 |  |  | 20.3075 | 20.38 | 20.6494 | [5 empty] | 21.9572 | 20.3556 | 21.6967 | 22.0722 | 19.5651 | 21.1902 | 21.8021 | 19.4439 | 19.9617 | 21.1335 |  | 19.7426 | 20.9407 | 18.9181 | 19.7544 | 20.821 | 19.4723 | 20.014 | 19.0674 | 20.1187 | 19.1087 | 20.2194 | 18.8825 | 20.0474 | 21.0458 | 19.4828 | 19.8109 | 20.9847 | 18.9294 | 19.8371 | 20.814 | 19.0382 | 20.0944 | 19.33 | 19.8819 | 18.9535 | 20.114 | -0.11607 | 20.9461 | 0.04936 | 0.016959 | -27.0462 | 3.0977 | -7.05 | -0.12 | 0.81804 | -0.59067 | -6.5679 | 0.96329 | 0.46779 | -16.7011 | 4.9789 | 0.42483 | 0.42322 | 0.42896 | 0.37119 | 0.4791 | 0.44024 | 0.42857
42838.4158 | -388 | 22.8961 | 22.8562 | 22.8441 | 22.777 | 22.4085 | 21.7482 | 22.7166 | 21.8167 | 22.3724 | 22.3881 | 22.3694 | 22.044 | 21.2648 | 22.2355 | 21.5728 | 21.7463 | 21.88 | 21.0745 | 21.1673 | 21.3891 | 20.4755 | 20.6136 | 20.9112 | 21.8952 | 21.6567 | 21.2917 | 20.3224 | 20.3764 | 20.3979 | 22.0523 | 21.6603 | 21.187 | 21.9957 | 21.7358 | 21.3561 | 19.9391 | 20.4792 |  | 20.5635 | 20.1042 | 20.2011 | 19.1517 |  | 16.7488 | 16.758 | 16.4548 | 16.6181 | 16.6528 | 17.1476 | 17.8112 | 16.0187 | 16.8267 | 15.8796 | 16.9146 | 17.8742 | 44.7531 | 47.6509 | 43.8609 | 21.3893 |  |  | 0.63566 | -0.038837 | -30.1302 | 0.6091 | 0.21895 | -197.8315 | 17.6287 | -0.43406 | -0.035518 | -0.043527 | 0.017998 | 8.8289 | 9.0585 | 1.9786 | 21.788 | 22.016 | 22.2073 | 22.2773 | 22.1058 | 21.4338 | 20.2557 | 22.1999 | 22.3808 | 22.4208 | 22.3728 | 22.0053 | 21.2398 | 22.2882 | 17.3746 | 17.0895 | 16.1493 | 16.1829 | 16.2211 | 17.0686 | 16.8317 | 22.3906 | 22.1499 | 21.7084 | 22.0791 | 21.7911 | 21.3173 | 21.9454 | 21.5353 | 20.9168 | 20.1057 | 20.2915 | 19.8353 | 19.7873 | -0.050121 | -0.012332 | 20.7773 | 22.0999 | 22.406 | 20.1182 | 21.6966 | 22.1461 | 21.9655 | 21.7347 | 21.2957 | 21.7952 | 21.4623 | 21.0604 | 20.1769 | 20.2146 | 20.2561 | 20.1927 | 20.0675 |  | 20.2432 | 20.0021 | 20.1269 | 19.768 | 20.1142 | 20.3514 |  | 20.4494 |  |  | 20.2983 | 20.3887 | 20.6446 | [5 empty] | 21.9579 | 20.3408 | 21.6883 | 22.0731 | 19.5622 | 21.1786 | 21.8089 | 19.4462 | 19.9691 | 21.1404 |  | 19.7497 | 20.9503 | 18.929 | 19.764 | 20.8242 | 19.4842 | 20.0109 | 19.0766 | 20.1227 | 19.1113 | 20.2311 | 18.8827 | 20.0546 | 21.0491 | 19.4901 | 19.8121 | 20.9934 | 18.9366 | 19.8413 | 20.814 | 19.0388 | 20.0932 | 19.335 | 19.8817 | 18.9662 | 20.1161 | -0.14909 | 20.9474 | 0.049624 | 0.016001 | -27.1289 | 3.0977 | -2.45 | -0.18 | 0.95196 | -0.23384 | -6.5133 | 0.92607 | 0.5556 | -16.7008 | 4.9854 | 0.42501 | 0.42293 | 0.42901 | 0.36824 | 0.47675 | 0.44026 | 0.42818
42838.4158 | -387 | 22.8892 | 22.8635 | 22.8409 | 22.7701 | 22.412 | 21.7547 | 22.7167 | 21.8122 | 22.3626 | 22.3882 | 22.3585 | 22.0455 | 21.2663 | 22.2265 | 21.5684 | 21.7475 | 21.8751 | 21.0692 | 21.162 | 21.3903 | 20.4702 | 20.6145 | 20.9135 | 21.8887 | 21.6505 | 21.2907 | 20.3182 | 20.3614 | 20.394 | 22.0443 | 21.6451 | 21.1773 | 21.9925 | 21.7315 | 21.3507 | 19.9305 | 20.4778 |  | 20.5561 | 20.0907 | 20.1938 | 19.1454 |  | 16.7599 | 16.7569 | 16.4557 | 16.6187 | 16.6529 | 17.1449 | 17.8252 | 15.9613 | 16.8354 | 15.8933 | 16.9178 | 17.8824 | 44.7525 | 47.6536 | 43.8714 | 21.3871 |  |  | 0.58178 | -0.11966 | -30.1585 | 0.61699 | 0.080956 | -197.8335 | 17.5499 | -0.31118 | -0.18672 | -0.12514 | -0.034082 | 8.829 | 9.0586 | 1.9791 | 21.7844 | 22.015 | 22.2024 | 22.2749 | 22.1082 | 21.4378 | 20.2531 | 22.2046 | 22.3816 | 22.4158 | 22.3725 | 22.004 | 21.2404 | 22.2871 | 17.416 | 17.1549 | 16.1421 | 16.1757 | 16.231 | 17.0734 | 16.836 | 22.3777 | 22.1436 | 21.7087 | 22.0834 | 21.7959 | 21.3091 | 21.9421 | 21.5315 | 20.9145 | 20.1079 | 20.284 | 19.8365 | 19.7893 | -0.16611 | -0.081184 | 20.7748 | 22.105 | 22.4105 | 20.1171 | 21.6926 | 22.1476 | 21.9685 | 21.7365 | 21.2992 | 21.8012 | 21.4638 | 21.0642 | 20.1776 | 20.2231 | 20.2588 | 20.1856 | 20.0727 |  | 20.2508 | 20.0116 | 20.1321 | 19.7661 | 20.1204 | 20.3506 |  | 20.4466 |  |  | 20.2908 | 20.3984 | 20.6439 | [5 empty] | 21.9596 | 20.3466 | 21.6945 | 22.0744 | 19.5692 | 21.1913 | 21.8115 | 19.4268 | 19.9527 | 21.1234 |  | 19.7469 | 20.9425 | 18.9169 | 19.7521 | 20.8141 | 19.4759 | 20.0071 | 19.0668 | 20.12 | 19.1047 | 20.2145 | 18.8765 | 20.0457 | 21.0485 | 19.4812 | 19.8003 | 20.9863 | 18.9243 | 19.8371 | 20.8207 | 19.0332 | 20.0903 | 19.3252 | 19.8837 | 18.948 | 20.1102 | -0.003657 | 20.9467 | 0.049538 | 0.015246 | -27.0408 | 3.0977 | -1.46 | -0.14 | 0.91071 | -0.41046 | -6.5163 | 0.93204 | 0.33784 | -16.7008 | 4.9742 | 0.42512 | 0.42284 | 0.42927 | 0.36419 | 0.47806 | 0.44015 | 0.42821
42838.4158 | -386 | 22.8838 | 22.8542 | 22.8346 | 22.7683 | 22.3993 | 21.7469 | 22.7102 | 21.8132 | 22.3673 | 22.3786 | 22.3609 | 22.0477 | 21.2638 | 22.225 | 21.5673 | 21.7449 | 21.8782 | 21.0683 | 21.1662 | 21.3868 | 20.4756 | 20.613 | 20.9081 | 21.8815 | 21.6473 | 21.2851 | 20.3167 | 20.3702 | 20.3939 | 22.0454 | 21.6474 | 21.1826 | 21.9851 | 21.7241 | 21.3549 | 19.9338 | 20.478 |  | 20.5613 | 20.0962 | 20.2019 | 19.1435 |  | 16.7469 | 16.7507 | 16.443 | 16.6085 | 16.6418 | 17.1469 | 17.8437 | 15.9463 | 16.8229 | 15.9145 | 16.9021 | 17.8736 | 44.7415 | 47.641 | 43.8567 | 21.379 |  |  | 0.57718 | -0.18472 | -30.6645 | 0.43103 | 0.20055 | -197.842 | 17.7154 | -0.21524 | -0.21105 | 0.073331 | -0.015159 | 8.8276 | 9.0574 | 1.9793 | 21.7815 | 22.0146 | 22.2064 | 22.277 | 22.1063 | 21.4394 | 20.2517 | 22.2083 | 22.3775 | 22.4138 | 22.3682 | 22.005 | 21.2399 | 22.2846 | 17.4407 | 17.1211 | 16.145 | 16.1651 | 16.2363 | 17.0705 | 16.8341 | 22.3898 | 22.1486 | 21.7083 | 22.0867 | 21.8029 | 21.3113 | 21.9484 | 21.5334 | 20.9158 | 20.1082 | 20.2887 | 19.84 | 19.7947 | -0.23866 | 0.051005 | 20.7734 | 22.1033 | 22.4145 | 20.1126 | 21.6928 | 22.1441 | 21.971 | 21.7338 | 21.2996 | 21.8073 | 21.4618 | 21.0653 | 20.1758 | 20.2246 | 20.2583 | 20.1873 | 20.0748 |  | 20.2442 | 20.0122 | 20.1303 | 19.7673 | 20.1171 | 20.3538 |  | 20.4478 |  |  | 20.2835 | 20.4032 | 20.6251 | [5 empty] | 21.9606 | 20.3456 | 21.6931 | 22.0756 | 19.5619 | 21.1885 | 21.8059 | 19.4325 | 19.9545 | 21.1297 |  | 19.7439 | 20.9376 | 18.9187 | 19.7444 | 20.8183 | 19.4829 | 20.0038 | 19.0727 | 20.1206 | 19.1174 | 20.2204 | 18.8795 | 20.0406 | 21.0442 | 19.478 | 19.7962 | 20.983 | 18.9195 | 19.8346 | 20.8112 | 19.0338 | 20.0832 | 19.3346 | 19.8797 | 18.9492 | 20.1122 | -0.17543 | 20.9474 | 0.048671 | 0.013126 | -27.0485 | 3.0977 | -15.1 | -0.14 | 0.90711 | -0.50997 | -6.5707 | 0.77901 | 0.53174 | -16.7012 | 4.9976 | 0.42484 | 0.42277 | 0.42913 | 0.36112 | 0.47752 | 0.44031 | 0.42806
42838.4158 | -385 | 22.8941 | 22.8602 | 22.8481 | 22.7755 | 22.4128 | 21.7511 | 22.7216 | 21.8253 | 22.3793 | 22.3849 | 22.369 | 22.0475 | 21.2651 | 22.2371 | 21.5677 | 21.7435 | 21.877 | 21.0691 | 21.1661 | 21.3888 | 20.4718 | 20.6155 | 20.9096 | 21.8812 | 21.652 | 21.285 | 20.3186 | 20.3672 | 20.392 | 22.0429 | 21.6499 | 21.1758 | 21.9898 | 21.7285 | 21.3483 | 19.9323 | 20.4701 |  | 20.5515 | 20.0919 | 20.1998 | 19.1386 |  | 16.7504 | 16.7467 | 16.4456 | 16.6086 | 16.6474 | 17.1722 | 17.8684 | 15.9521 | 16.8254 | 15.9398 | 16.8993 | 17.8766 | 44.7431 | 47.644 | 43.8629 | 21.3923 |  |  | 0.61923 | -0.22874 | -30.8169 | 0.56705 | 0.17427 | -197.8453 | 17.9356 | -0.25861 | -0.1624 | 0.088437 | -0.02436 | 8.8293 | 9.0588 | 1.9788 | 21.792 | 22.0152 | 22.2085 | 22.2769 | 22.1081 | 21.4368 | 20.2496 | 22.2079 | 22.3756 | 22.4156 | 22.3708 | 21.9988 | 21.2442 | 22.2782 | 17.4648 | 17.0641 | 16.1355 | 16.1625 | 16.2383 | 17.0663 | 16.8346 | 22.3941 | 22.161 | 21.7186 | 22.0945 | 21.8061 | 21.3168 | 21.9554 | 21.541 | 20.9225 | 20.1173 | 20.2922 | 19.8484 | 19.803 | -0.084329 | -0.053035 | 20.7743 | 22.1073 | 22.4102 | 20.1148 | 21.697 | 22.1389 | 21.9697 | 21.7322 | 21.2998 | 21.8047 | 21.4617 | 21.0642 | 20.1799 | 20.2169 | 20.2607 | 20.1911 | 20.0826 |  | 20.2498 | 20.0152 | 20.1333 | 19.7564 | 20.1127 | 20.3519 |  | 20.4411 |  |  | 20.284 | 20.3973 | 20.6212 | [5 empty] | 21.96 | 20.3481 | 21.6931 | 22.0698 | 19.5663 | 21.1967 | 21.8051 | 19.426 | 19.9482 | 21.1163 |  | 19.7331 | 20.9291 | 18.9151 | 19.7422 | 20.8073 | 19.4721 | 20.0062 | 19.0653 | 20.1208 | 19.1138 | 20.2134 | 18.8966 | 20.0468 | 21.0484 | 19.4865 | 19.8041 | 20.9936 | 18.9245 | 19.8375 | 20.8218 | 19.0439 | 20.0895 | 19.3393 | 19.887 | 18.9522 | 20.1249 | -0.21958 | 20.9498 | 0.047559 | 0.012792 | -26.9849 | 3.0976 | -6.16 | 0.05 | 0.93957 | -0.56749 | -6.5869 | 0.89351 | 0.4957 | -16.7021 | 5.0288 | 0.42481 | 0.42278 | 0.42928 | 0.35794 | 0.47862 | 0.4404 | 0.42814
42838.4158 | -384 | 22.8896 | 22.8618 | 22.8519 | 22.7761 | 22.4148 | 21.7399 | 22.7204 | 21.8149 | 22.3737 | 22.3777 | 22.369 | 22.0433 | 21.2641 | 22.2337 | 21.5694 | 21.7365 | 21.8729 | 21.0671 | 21.167 | 21.3877 | 20.4692 | 20.6117 | 20.9107 | 21.883 | 21.6484 | 21.2926 | 20.3153 | 20.3636 | 20.381 | 22.0338 | 21.639 | 21.1755 | 21.9863 | 21.7254 | 21.338 | 19.9222 | 20.4687 |  | 20.5447 | 20.0873 | 20.1925 | 19.1365 |  | 16.7554 | 16.754 | 16.4437 | 16.6016 | 16.6823 | 17.2099 | 17.8577 | 15.9748 | 16.8267 | 15.9653 | 16.8989 | 17.8748 | 44.7437 | 47.6379 | 43.8602 | 21.3845 |  |  | 0.42275 | -0.33914 | -30.8622 | 0.3594 | 0.04416 | -197.8289 | 17.471 | -0.32498 | 0.10946 | 0.06431 | 0.096292 | 8.8286 | 9.0582 | 1.9786 | 21.7936 | 22.0154 | 22.2139 | 22.2764 | 22.1109 | 21.4402 | 20.2565 | 22.2119 | 22.382 | 22.4162 | 22.3662 | 22.0037 | 21.2457 | 22.2906 | 17.482 | 17.0435 | 16.1486 | 16.1621 | 16.2435 | 17.0691 | 16.8357 | 22.383 | 22.1551 | 21.71 | 22.0881 | 21.8067 | 21.3124 | 21.954 | 21.536 | 20.917 | 20.1092 | 20.2914 | 19.8308 | 19.8029 | -0.14921 | -0.10058 | 20.7738 | 22.1041 | 22.4024 | 20.1099 | 21.6866 | 22.1358 | 21.9595 | 21.7284 | 21.2987 | 21.7971 | 21.4597 | 21.0604 | 20.1786 | 20.2128 | 20.2537 | 20.1913 | 20.0561 |  | 20.2394 | 20.0065 | 20.1321 | 19.7526 | 20.1119 | 20.3473 |  | 20.4442 |  |  | 20.286 | 20.3823 | 20.6088 | [5 empty] | 21.9552 | 20.3424 | 21.6925 | 22.0648 | 19.5565 | 21.1908 | 21.8027 | 19.4136 | 19.9432 | 21.116 |  | 19.7386 | 20.9234 | 18.915 | 19.7342 | 20.8103 | 19.4751 | 19.9984 | 19.0601 | 20.119 | 19.106 | 20.2188 | 18.8866 | 20.0355 | 21.0403 | 19.4868 | 19.8035 | 20.9823 | 18.9176 | 19.833 | 20.8132 | 19.0367 | 20.0878 | 19.3343 | 19.8786 | 18.9419 | 20.1229 | -0.061718 | 20.9448 | 0.0488 | 0.014186 | -26.9618 | 3.0976 | -5.97 | -0.02 | 0.77631 | -0.69101 | -6.5919 | 0.71135 | 0.24955 | -16.7025 | 4.9636 | 0.4252 | 0.42298 | 0.42936 | 0.35636 | 0.47729 | 0.44012 | 0.42787
42838.4158 | -383 | 22.885 | 22.8542 | 22.8434 | 22.765 | 22.4115 | 21.7386 | 22.7097 | 21.8143 | 22.3589 | 22.3707 | 22.3607 | 22.0412 | 21.2599 | 22.2266 | 21.5696 | 21.7345 | 21.8799 | 21.0653 | 21.162 | 21.3878 | 20.4701 | 20.6163 | 20.9083 | 21.8846 | 21.6491 | 21.2918 | 20.3151 | 20.3662 | 20.3838 | 22.0332 | 21.6482 | 21.1773 | 21.9886 | 21.7173 | 21.3442 | 19.928 | 20.4737 |  | 20.5524 | 20.0894 | 20.1902 | 19.1252 |  | 16.7639 | 16.7581 | 16.4461 | 16.6164 | 16.696 | 17.2324 | 17.858 | 15.9767 | 16.836 | 15.9756 | 16.9067 | 17.8819 | 44.7495 | 47.6347 | 43.8771 | 21.3846 |  |  | 0.44181 | -0.29248 | -31.541 | 0.41788 | 0.11776 | -197.8092 | 17.3067 | -0.53 | -0.10149 | -0.11947 | 0.059142 | 8.8292 | 9.0588 | 1.9786 | 21.7882 | 22.0157 | 22.2051 | 22.2726 | 22.1089 | 21.4378 | 20.2529 | 22.2047 | 22.3809 | 22.4124 | 22.3717 | 22.0094 | 21.2387 | 22.2896 | 17.4865 | 17.0877 | 16.133 | 16.1592 | 16.2261 | 17.0732 | 16.8414 | 22.3833 | 22.161 | 21.7134 | 22.0901 | 21.8084 | 21.3157 | 21.9554 | 21.5379 | 20.9191 | 20.1143 | 20.3016 | 19.8387 | 19.8006 | -0.030657 | -0.11067 | 20.7753 | 22.1005 | 22.3942 | 20.1038 | 21.6904 | 22.14 | 21.9616 | 21.7302 | 21.2895 | 21.7909 | 21.4628 | 21.0606 | 20.1791 | 20.2158 | 20.245 | 20.1898 | 20.0427 |  | 20.2434 | 20.0093 | 20.1288 | 19.7501 | 20.1096 | 20.3393 |  | 20.4377 |  |  | 20.2898 | 20.3782 | 20.6064 | [5 empty] | 21.9576 | 20.3425 | 21.6945 | 22.0739 | 19.5616 | 21.184 | 21.8059 | 19.4185 | 19.9396 | 21.1244 |  | 19.7432 | 20.9283 | 18.9181 | 19.7365 | 20.8184 | 19.4838 | 20.0081 | 19.0615 | 20.1262 | 19.1176 | 20.2226 | 18.8817 | 20.0366 | 21.0382 | 19.4818 | 19.7972 | 20.9818 | 18.9167 | 19.8311 | 20.8128 | 19.0303 | 20.0929 | 19.3381 | 19.8827 | 18.9368 | 20.1205 | -0.27523 | 20.9467 | 0.049151 | 0.015362 | -27.0363 | 3.0976 | 0.43 | -0.13 | 0.79363 | -0.64172 | -6.664 | 0.76705 | 0.40752 | -16.7023 | 4.9404 | 0.42571 | 0.42279 | 0.42935 | 0.35634 | 0.47969 | 0.44063 | 0.42811
42838.4159 | -382 | 22.8891 | 22.8557 | 22.8404 | 22.7756 | 22.4076 | 21.7478 | 22.7126 | 21.8203 | 22.3688 | 22.3741 | 22.3661 | 22.0483 | 21.2665 | 22.2385 | 21.5751 | 21.7404 | 21.8838 | 21.0715 | 21.1675 | 21.3895 | 20.4749 | 20.6146 | 20.9065 | 21.8928 | 21.6535 | 21.2934 | 20.3124 | 20.3689 | 20.3844 | 22.0381 | 21.6477 | 21.1741 | 21.9892 | 21.7236 | 21.3469 | 19.9344 | 20.4798 |  | 20.5535 | 20.0858 | 20.1879 | 19.121 |  | 16.7677 | 16.7587 | 16.4505 | 16.6146 | 16.6905 | 17.2416 | 17.8438 | 15.9673 | 16.8371 | 15.985 | 16.8999 | 17.8748 | 44.7592 | 47.6249 | 43.8805 | 21.3836 |  |  | 0.46284 | -0.20246 | -31.7428 | 0.066326 | 0.067816 | -197.8276 | 17.7207 | -0.43406 | -0.10538 | -0.22396 | 0.043691 | 8.8292 | 9.0589 | 1.9787 | 21.7843 | 22.0089 | 22.1997 | 22.2755 | 22.0999 | 21.4256 | 20.2401 | 22.1955 | 22.375 | 22.4018 | 22.3615 | 22.0019 | 21.2314 | 22.2812 | 17.478 | 17.0736 | 16.1067 | 16.1352 | 16.213 | 17.0666 | 16.834 | 22.3816 | 22.1532 | 21.7215 | 22.0877 | 21.8123 | 21.3145 | 21.9497 | 21.5389 | 20.915 | 20.1122 | 20.2949 | 19.8253 | 19.809 | 0.032255 | -0.16773 | 20.7736 | 22.1042 | 22.396 | 20.1063 | 21.6945 | 22.144 | 21.9697 | 21.7313 | 21.2894 | 21.8044 | 21.4635 | 21.0615 | 20.1809 | 20.2116 | 20.2544 | 20.1876 | 20.0421 |  | 20.2431 | 20.0118 | 20.1398 | 19.7602 | 20.1199 | 20.3523 |  | 20.4465 |  |  | 20.2885 | 20.3572 | 20.6126 | [5 empty] | 21.9504 | 20.3366 | 21.688 | 22.0739 | 19.5527 | 21.1795 | 21.8043 | 19.4227 | 19.9377 | 21.1245 |  | 19.7512 | 20.9333 | 18.9291 | 19.7382 | 20.8215 | 19.4854 | 20.0103 | 19.0711 | 20.1349 | 19.1288 | 20.2241 | 18.8788 | 20.0374 | 21.046 | 19.4783 | 19.7944 | 20.984 | 18.9189 | 19.833 | 20.8077 | 19.0277 | 20.0903 | 19.3287 | 19.8872 | 18.9386 | 20.12 | -0.10327 | 20.9467 | 0.048813 | 0.015275 | -27.0283 | 3.0977 | 3.84 | 0 | 0.81229 | -0.53391 | -6.6853 | 0.30559 | 0.30926 | -16.7033 | 4.9992 | 0.42571 | 0.42309 | 0.42942 | 0.35652 | 0.48176 | 0.44096 | 0.4278
42838.4159 | -381 | 22.8852 | 22.8472 | 22.8374 | 22.7748 | 22.4062 | 21.7501 | 22.7075 | 21.8115 | 22.3674 | 22.3791 | 22.3625 | 22.0507 | 21.2608 | 22.2298 | 21.5722 | 21.7445 | 21.8797 | 21.0668 | 21.1658 | 21.3816 | 20.4745 | 20.6126 | 20.9063 | 21.8893 | 21.6502 | 21.2933 | 20.3042 | 20.3654 | 20.3774 | 22.0436 | 21.6524 | 21.1794 | 21.9885 | 21.7299 | 21.3489 | 19.9302 | 20.484 |  | 20.5558 | 20.0892 | 20.1875 | 19.1185 |  | 16.7656 | 16.7604 | 16.4422 | 16.6125 | 16.691 | 17.2272 | 17.8506 | 15.9155 | 16.8369 | 15.983 | 16.9022 | 17.8803 | 44.7784 | 47.6245 | 43.8829 | 21.3873 |  |  | 0.53644 | -0.37594 | -31.865 | 0.20563 | -0.016952 | -197.8282 | 17.4914 | -0.39003 | 0.2089 | -0.2164 | -0.000924 | 8.8297 | 9.0598 | 1.9788 | 21.7962 | 22.0174 | 22.2074 | 22.2744 | 22.1036 | 21.444 | 20.2529 | 22.1995 | 22.3784 | 22.4167 | 22.3663 | 21.9965 | 21.2387 | 22.2837 | 17.4569 | 17.0599 | 16.0996 | 16.1241 | 16.2089 | 17.07 | 16.8349 | 22.3882 | 22.1493 | 21.7185 | 22.0906 | 21.8009 | 21.3116 | 21.9496 | 21.5324 | 20.9133 | 20.1171 | 20.2896 | 19.8223 | 19.8041 | 0.05683 | -0.074337 | 20.78 | 22.109 | 22.4022 | 20.1115 | 21.69 | 22.1431 | 21.9682 | 21.7333 | 21.297 | 21.8087 | 21.4632 | 21.0627 | 20.1862 | 20.211 | 20.2534 | 20.1918 | 20.0407 |  | 20.2421 | 20.0034 | 20.1251 | 19.7497 | 20.1096 | 20.348 |  | 20.4441 |  |  | 20.287 | 20.3455 | 20.6143 | [5 empty] | 21.953 | 20.3329 | 21.6829 | 22.0668 | 19.5483 | 21.1787 | 21.7982 | 19.4124 | 19.9317 | 21.1165 |  | 19.7487 | 20.9292 | 18.9209 | 19.7345 | 20.8142 | 19.4826 | 20.008 | 19.0684 | 20.1356 | 19.1235 | 20.2245 | 18.8851 | 20.037 | 21.0424 | 19.4787 | 19.8026 | 20.9819 | 18.9167 | 19.8228 | 20.8104 | 19.0272 | 20.0897 | 19.324 | 19.8866 | 18.9388 | 20.1227 | 0.12304 | 20.9459 | 0.048542 | 0.015152 | -27.0969 | 3.0976 | -8.25 | -0.07 | 0.87448 | -0.72754 | -6.6982 | 0.53808 | -0.15462 | -16.7029 | 4.9666 | 0.42572 | 0.42283 | 0.42936 | 0.35926 | 0.48265 | 0.44089 | 0.4281
42838.4159 | -380 | 22.8927 | 22.8524 | 22.846 | 22.7761 | 22.4156 | 21.7631 | 22.7116 | 21.8131 | 22.373 | 22.3855 | 22.3614 | 22.0501 | 21.2625 | 22.2292 | 21.5733 | 21.7465 | 21.8765 | 21.0693 | 21.1591 | 21.3807 | 20.4688 | 20.6101 | 20.9077 | 21.8858 | 21.6543 | 21.2912 | 20.3161 | 20.3611 | 20.3768 | 22.04 | 21.6531 | 21.1784 | 21.9886 | 21.7286 | 21.3544 | 19.94 | 20.4918 |  | 20.5556 | 20.0895 | 20.1888 | 19.11 |  | 16.7714 | 16.7564 | 16.4419 | 16.6115 | 16.6791 | 17.2369 | 17.8741 | 15.8484 | 16.8389 | 15.9698 | 16.902 | 17.8823 | 44.7864 | 47.6143 | 43.8883 | 21.3858 |  |  | 0.65603 | -0.20377 | -32.2902 | 0.33969 | 0.067156 | -197.8604 | 17.2088 | -0.50962 | 0.042711 | 0.14781 | 0.024769 | 8.8284 | 9.0581 | 1.9789 | 21.7889 | 22.0091 | 22.2131 | 22.2711 | 22.1052 | 21.4415 | 20.2495 | 22.2076 | 22.3732 | 22.4114 | 22.3639 | 21.9978 | 21.2417 | 22.2858 | 17.444 | 17.0992 | 16.0848 | 16.1013 | 16.1994 | 17.0697 | 16.8343 | 22.3835 | 22.1514 | 21.7118 | 22.084 | 21.8075 | 21.3126 | 21.9457 | 21.5367 | 20.9147 | 20.111 | 20.2919 | 19.8212 | 19.8063 | 0.087303 | -0.14205 | 20.7813 | 22.1004 | 22.3997 | 20.1133 | 21.683 | 22.139 | 21.9625 | 21.73 | 21.2946 | 21.7946 | 21.4611 | 21.0573 | 20.1884 | 20.2125 | 20.2459 | 20.1943 | 20.0461 |  | 20.2425 | 19.9958 | 20.1285 | 19.7519 | 20.1162 | 20.3428 |  | 20.4373 |  |  | 20.2939 | 20.3433 | 20.6166 | [5 empty] | 21.9549 | 20.3397 | 21.6858 | 22.0682 | 19.5617 | 21.1808 | 21.802 | 19.4048 | 19.9226 | 21.1102 |  | 19.7409 | 20.9228 | 18.9161 | 19.7258 | 20.8174 | 19.4776 | 19.9961 | 19.0677 | 20.1274 | 19.1231 | 20.2234 | 18.8864 | 20.0282 | 21.0325 | 19.4698 | 19.7879 | 20.9721 | 18.9151 | 19.8139 | 20.8017 | 19.0183 | 20.0868 | 19.3187 | 19.8771 | 18.926 | 20.1163 | -0.092326 | 20.9455 | 0.048223 | 0.014397 | -27.0203 | 3.0976 | 2.56 | 0.04 | 0.96706 | -0.53564 | -6.7427 | 0.69157 | 0.30775 | -16.7046 | 4.9264 | 0.42558 | 0.42316 | 0.42952 | 0.36066 | 0.48422 | 0.44145 | 0.42784
42838.4159 | -379 | 22.8904 | 22.8607 | 22.8467 | 22.7749 | 22.4158 | 21.7474 | 22.7192 | 21.817 | 22.369 | 22.3827 | 22.369 | 22.0423 | 21.2658 | 22.2337 | 21.5713 | 21.7465 | 21.8776 | 21.0697 | 21.1684 | 21.392 | 20.4717 | 20.6136 | 20.9152 | 21.8892 | 21.6561 | 21.2968 | 20.3162 | 20.3614 | 20.3782 | 22.0394 | 21.6506 | 21.1696 | 21.9861 | 21.7312 | 21.3417 | 19.9306 | 20.4879 |  | 20.5517 | 20.0871 | 20.1867 | 19.1056 |  | 16.769 | 16.7566 | 16.4459 | 16.6253 | 16.7144 | 17.2769 | 17.8934 | 15.7782 | 16.8417 | 15.9806 | 16.9061 | 17.8813 | 44.7898 | 47.615 | 43.8892 | 21.391 |  |  | 0.4681 | -0.2524 | -32.2553 | 0.54339 | 0.23735 | -197.8473 | 17.5177 | -0.3322 | 0.063338 | 0.0019994 | 0.020255 | 8.8283 | 9.0583 | 1.979 | 21.7841 | 22.0096 | 22.2133 | 22.272 | 22.0998 | 21.4357 | 20.2451 | 22.2052 | 22.3708 | 22.4125 | 22.3647 | 21.9974 | 21.2376 | 22.2844 | 17.4483 | 17.0966 | 16.0699 | 16.1018 | 16.1985 | 17.0728 | 16.8372 | 22.3833 | 22.1609 | 21.7157 | 22.0859 | 21.8014 | 21.3126 | 21.9532 | 21.5353 | 20.9159 | 20.1103 | 20.2885 | 19.822 | 19.7888 | -0.018272 | -0.14015 | 20.7777 | 22.0951 | 22.3958 | 20.1068 | 21.6821 | 22.1358 | 21.9614 | 21.7213 | 21.2921 | 21.7889 | 21.4584 | 21.0557 | 20.1889 | 20.2067 | 20.2516 | 20.1902 | 20.0434 |  | 20.2337 | 19.9787 | 20.1212 | 19.7524 | 20.1066 | 20.3391 |  | 20.4346 |  |  | 20.2872 | 20.3302 | 20.6253 | [5 empty] | 21.9524 | 20.3388 | 21.686 | 22.065 | 19.5599 | 21.1795 | 21.8008 | 19.3994 | 19.923 | 21.1049 |  | 19.7391 | 20.9191 | 18.9129 | 19.7298 | 20.814 | 19.4697 | 19.9885 | 19.0685 | 20.1293 | 19.1267 | 20.218 | 18.8813 | 20.0254 | 21.0319 | 19.4653 | 19.7796 | 20.9726 | 18.9082 | 19.8009 | 20.8015 | 19.0091 | 20.081 | 19.3168 | 19.8751 | 18.9192 | 20.1116 | -0.080083 | 20.9455 | 0.047277 | 0.013707 | -27.051 | 3.0975 | -12.49 | -0.02 | 0.81688 | -0.59613 | -6.739 | 0.87469 | 0.5786 | -16.7052 | 4.9708 | 0.42536 | 0.42339 | 0.42919 | 0.36054 | 0.48621 | 0.44126 | 0.4283
42838.4159 | -378 | 22.8837 | 22.8589 | 22.8384 | 22.7638 | 22.405 | 21.7422 | 22.7135 | 21.8126 | 22.3668 | 22.3745 | 22.366 | 22.0417 | 21.2625 | 22.2303 | 21.5713 | 21.7382 | 21.8772 | 21.0649 | 21.1643 | 21.385 | 20.4672 | 20.6148 | 20.9087 | 21.8861 | 21.6551 | 21.2864 | 20.3065 | 20.3591 | 20.3754 | 22.0389 | 21.6483 | 21.1755 | 21.9922 | 21.7278 | 21.3507 | 19.9361 | 20.4919 |  | 20.5534 | 20.0832 | 20.1904 | 19.1136 |  | 16.7683 | 16.7524 | 16.4445 | 16.6319 | 16.7422 | 17.3165 | 17.921 | 15.7236 | 16.8451 | 16.0024 | 16.9052 | 17.8801 | 44.7841 | 47.6104 | 43.8772 | 21.3952 |  |  | 0.63369 | -0.21429 | -32.3815 | 0.32129 | 0.15192 | -197.8309 | 17.0971 | -0.39529 | 0.33831 | 0.14718 | -0.027832 | 8.8279 | 9.0579 | 1.9784 | 21.7935 | 22.0102 | 22.2126 | 22.2722 | 22.1104 | 21.435 | 20.2409 | 22.2017 | 22.3789 | 22.4181 | 22.3656 | 22.0074 | 21.2411 | 22.2856 | 17.4656 | 17.1076 | 16.0703 | 16.1112 | 16.1875 | 17.0754 | 16.8333 | 22.3864 | 22.1492 | 21.7106 | 22.0866 | 21.7971 | 21.3167 | 21.9427 | 21.5339 | 20.9106 | 20.1105 | 20.2853 | 19.819 | 19.7919 | 0.025767 | -0.092596 | 20.7755 | 22.099 | 22.3975 | 20.1003 | 21.6873 | 22.1384 | 21.9604 | 21.7293 | 21.2939 | 21.7903 | 21.4577 | 21.0532 | 20.1963 | 20.21 | 20.2491 | 20.1914 | 20.0555 |  | 20.2432 | 19.9783 | 20.1291 | 19.7492 | 20.1172 | 20.3424 |  | 20.4496 |  |  | 20.2922 | 20.3271 | 20.6244 | [5 empty] | 21.9534 | 20.3418 | 21.6896 | 22.0671 | 19.5645 | 21.1849 | 21.8053 | 19.4004 | 19.927 | 21.1067 |  | 19.7469 | 20.9195 | 18.9166 | 19.7292 | 20.816 | 19.4824 | 19.9922 | 19.075 | 20.1341 | 19.1333 | 20.2214 | 18.8717 | 20.0201 | 21.0284 | 19.4682 | 19.7719 | 20.9685 | 18.9044 | 19.8013 | 20.7985 | 18.9961 | 20.0773 | 19.3022 | 19.8666 | 18.919 | 20.1133 | -0.11978 | 20.9432 | 0.0459 | 0.014012 | -26.9982 | 3.0976 | -10.75 | -0.11 | 0.95045 | -0.54927 | -6.7521 | 0.67257 | 0.46294 | -16.7056 | 4.9111 | 0.42534 | 0.42366 | 0.42963 | 0.35893 | 0.48571 | 0.44122 | 0.42822
42838.4159 | -377 | 22.892 | 22.8557 | 22.8479 | 22.7716 | 22.4093 | 21.7546 | 22.7131 | 21.8117 | 22.366 | 22.3766 | 22.3703 | 22.0457 | 21.2708 | 22.2334 | 21.5682 | 21.7401 | 21.8759 | 21.0604 | 21.1697 | 21.3859 | 20.4664 | 20.6075 | 20.9021 | 21.8805 | 21.6468 | 21.2816 | 20.3053 | 20.3598 | 20.3757 | 22.0481 | 21.6585 | 21.1824 | 22 | 21.7359 | 21.3543 | 19.9387 | 20.4843 |  | 20.5527 | 20.086 | 20.197 | 19.1237 |  | 16.7604 | 16.7514 | 16.4371 | 16.6478 | 16.7664 | 17.3405 | 17.9399 | 15.6714 | 16.8371 | 16.018 | 16.9013 | 17.8706 | 44.7723 | 47.593 | 43.8576 | 21.388 |  |  | 0.62055 | -0.26225 | -32.4945 | 0.20761 | 0.18675 | -197.8361 | 17.1135 | -0.37952 | 0.15889 | 0.10375 | 0.11122 | 8.8288 | 9.0586 | 1.9784 | 21.7795 | 22.0106 | 22.1993 | 22.2626 | 22.1006 | 21.4264 | 20.2407 | 22.1955 | 22.37 | 22.4061 | 22.3584 | 21.9907 | 21.2326 | 22.2735 | 17.4586 | 17.103 | 16.0967 | 16.1139 | 16.1937 | 17.0719 | 16.8328 | 22.393 | 22.1604 | 21.7185 | 22.0927 | 21.8042 | 21.3157 | 21.9504 | 21.5428 | 20.9212 | 20.1134 | 20.2951 | 19.8278 | 19.7948 | -0.035179 | -0.04809 | 20.776 | 22.105 | 22.4055 | 20.1107 | 21.7006 | 22.1408 | 21.9666 | 21.7343 | 21.3035 | 21.7992 | 21.4617 | 21.0611 | 20.1995 | 20.2198 | 20.2495 | 20.2022 | 20.0646 |  | 20.2493 | 19.982 | 20.1346 | 19.7549 | 20.1198 | 20.3444 |  | 20.4391 |  |  | 20.2919 | 20.3343 | 20.6253 | [5 empty] | 21.959 | 20.3389 | 21.6898 | 22.066 | 19.5644 | 21.1833 | 21.8085 | 19.3934 | 19.925 | 21.111 |  | 19.7524 | 20.9212 | 18.918 | 19.7312 | 20.8243 | 19.487 | 19.9935 | 19.0785 | 20.1456 | 19.138 | 20.2281 | 18.8737 | 20.0152 | 21.026 | 19.4589 | 19.7688 | 20.9687 | 18.9056 | 19.8076 | 20.8056 | 18.9899 | 20.0806 | 19.3 | 19.8716 | 18.9228 | 20.1202 | -0.1387 | 20.9479 | 0.045642 | 0.013504 | -27.0676 | 3.0976 | -1.97 | -0.16 | 0.94054 | -0.60765 | -6.7639 | 0.54064 | 0.51329 | -16.7065 | 4.9136 | 0.42529 | 0.42374 | 0.42956 | 0.3593 | 0.48272 | 0.44103 | 0.42823
42838.4159 | -376 | 22.8899 | 22.8498 | 22.832 | 22.7673 | 22.4084 | 21.7507 | 22.7124 | 21.8114 | 22.3663 | 22.3777 | 22.3645 | 22.0391 | 21.2583 | 22.226 | 21.5618 | 21.746 | 21.8743 | 21.0654 | 21.1664 | 21.3805 | 20.4689 | 20.6138 | 20.9026 | 21.8796 | 21.6498 | 21.2836 | 20.3086 | 20.351 | 20.3692 | 22.0477 | 21.6573 | 21.1861 | 21.9977 | 21.7327 | 21.3538 | 19.9354 | 20.4835 |  | 20.5548 | 20.0871 | 20.197 | 19.1281 |  | 16.7767 | 16.7566 | 16.456 | 16.6796 | 16.8058 | 17.3821 | 17.9479 | 15.652 | 16.8507 | 16.0553 | 16.9088 | 17.8809 | 44.7746 | 47.5943 | 43.8742 | 21.3981 |  |  | 0.63632 | -0.071693 | -32.4157 | 0.48622 | 0.0941 | -197.8486 | 17.2022 | -0.43209 | 0.16258 | -0.21074 | 0.050635 | 8.8291 | 9.059 | 1.9794 | 21.79 | 22.0079 | 22.1998 | 22.2657 | 22.0911 | 21.4265 | 20.2459 | 22.1947 | 22.3719 | 22.408 | 22.3643 | 21.9918 | 21.2368 | 22.2772 | 17.4513 | 17.056 | 16.1116 | 16.0857 | 16.1895 | 17.06 | 16.8288 | 22.3911 | 22.1604 | 21.7155 | 22.0885 | 21.8012 | 21.3146 | 21.9476 | 21.5425 | 20.9177 | 20.1103 | 20.2888 | 19.8209 | 19.793 | -0.21133 | -0.061213 | 20.7847 | 22.1086 | 22.409 | 20.1164 | 21.7023 | 22.1473 | 21.9704 | 21.7314 | 21.3042 | 21.8068 | 21.4723 | 21.0642 | 20.2036 | 20.2206 | 20.2574 | 20.2011 | 20.0816 |  | 20.2446 | 19.9723 | 20.1333 | 19.7476 | 20.1169 | 20.3442 |  | 20.4426 |  |  | 20.2828 | 20.337 | 20.6218 | [5 empty] | 21.952 | 20.3347 | 21.6891 | 22.0601 | 19.5498 | 21.1816 | 21.7967 | 19.3937 | 19.9203 | 21.1079 |  | 19.7569 | 20.9271 | 18.9199 | 19.729 | 20.8287 | 19.4929 | 19.9961 | 19.0855 | 20.1504 | 19.1498 | 20.2319 | 18.8731 | 20.0219 | 21.0237 | 19.4685 | 19.772 | 20.9562 | 18.9014 | 19.7987 | 20.8082 | 18.9935 | 20.0855 | 19.3078 | 19.8762 | 18.9295 | 20.1289 | -0.15836 | 20.9453 | 0.04649 | 0.014404 | -27.0689 | 3.0976 | 8.33 | -0.09 | 0.95241 | -0.31771 | -6.7557 | 0.8274 | 0.36438 | -16.7082 | 4.9267 | 0.42466 | 0.42397 | 0.42966 | 0.35872 | 0.4806 | 0.44079 | 0.42818
42838.4159 | -375 | 22.8824 | 22.8458 | 22.838 | 22.7694 | 22.4099 | 21.7523 | 22.7147 | 21.8133 | 22.3708 | 22.3865 | 22.3635 | 22.0421 | 21.2668 | 22.2276 | 21.576 | 21.7446 | 21.8821 | 21.0731 | 21.1679 | 21.382 | 20.4701 | 20.6151 | 20.9183 | 21.8841 | 21.6469 | 21.2866 | 20.306 | 20.3617 | 20.3672 | 22.0458 | 21.6497 | 21.1801 | 21.9846 | 21.731 | 21.3556 | 19.9326 | 20.4791 |  | 20.5536 | 20.0857 | 20.1913 | 19.1373 |  | 16.7647 | 16.7534 | 16.4636 | 16.703 | 16.8365 | 17.4023 | 17.9557 | 15.6402 | 16.8565 | 16.0525 | 16.9063 | 17.8723 | 44.751 | 47.5842 | 43.8649 | 21.3946 |  |  | 0.62055 | -0.21626 | -32.1988 | 0.15438 | 0.23275 | -197.848 | 16.831 | -0.40843 | 0.096615 | -0.40564 | 0.028241 | 8.8297 | 9.0593 | 1.9794 | 21.7819 | 22.0102 | 22.1971 | 22.2673 | 22.0936 | 21.424 | 20.248 | 22.1988 | 22.3646 | 22.4031 | 22.3594 | 21.9899 | 21.2308 | 22.2762 | 17.4592 | 17.0321 | 16.1175 | 16.0775 | 16.1913 | 17.0609 | 16.8242 | 22.3871 | 22.1481 | 21.7145 | 22.0862 | 21.8012 | 21.3061 | 21.9485 | 21.5299 | 20.908 | 20.1046 | 20.2859 | 19.8141 | 19.7728 | -0.25164 | -0.14205 | 20.7825 | 22.1045 | 22.4018 | 20.1133 | 21.6945 | 22.1415 | 21.9687 | 21.7304 | 21.2971 | 21.8001 | 21.4679 | 21.057 | 20.2078 | 20.2182 | 20.2541 | 20.1988 | 20.0921 |  | 20.2468 | 19.9699 | 20.1328 | 19.7378 | 20.1128 | 20.3437 |  | 20.4458 |  |  | 20.282 | 20.3448 | 20.6217 | [5 empty] | 21.9533 | 20.334 | 21.6787 | 22.0639 | 19.5551 | 21.1864 | 21.7978 | 19.3857 | 19.9184 | 21.1103 |  | 19.7527 | 20.9237 | 18.9252 | 19.7262 | 20.8194 | 19.4853 | 19.993 | 19.0915 | 20.1472 | 19.1529 | 20.2356 | 18.8862 | 20.0342 | 21.0323 | 19.4691 | 19.7747 | 20.9733 | 18.9042 | 19.8099 | 20.8091 | 19.0161 | 20.1034 | 19.3204 | 19.8839 | 18.9328 | 20.1359 | -0.10568 | 20.9451 | 0.046963 | 0.015507 | -26.9966 | 3.0975 | 0 | -0.12 | 0.94053 | -0.5518 | -6.7331 | 0.46622 | 0.57309 | -16.7088 | 4.8734 | 0.42445 | 0.42402 | 0.4298 | 0.35794 | 0.47941 | 0.44045 | 0.42855
42838.4159 | -374 | 22.8834 | 22.8469 | 22.8437 | 22.7718 | 22.4083 | 21.7551 | 22.7158 | 21.8045 | 22.3662 | 22.3756 | 22.3597 | 22.0485 | 21.263 | 22.2252 | 21.5713 | 21.7478 | 21.8802 | 21.0684 | 21.1686 | 21.3917 | 20.4767 | 20.6101 | 20.9166 | 21.8876 | 21.6587 | 21.2909 | 20.311 | 20.3557 | 20.3716 | 22.0363 | 21.6454 | 21.1709 | 21.9832 | 21.7286 | 21.3439 | 19.9326 | 20.4712 |  | 20.5482 | 20.0787 | 20.1845 | 19.1415 |  | 16.7643 | 16.7536 | 16.4622 | 16.7173 | 16.8472 | 17.4016 | 17.9591 | 15.6337 | 16.8476 | 16.0662 | 16.9014 | 17.8696 | 44.7215 | 47.5697 | 43.8637 | 21.3903 |  |  | 0.43853 | -0.19654 | -32.9867 | -0.013842 | 0.29649 | -197.8512 | 16.8619 | -0.31643 | 0.065868 | -0.15074 | -0.065503 | 8.8293 | 9.059 | 1.9789 | 21.795 | 22.0151 | 22.2153 | 22.2831 | 22.1016 | 21.4359 | 20.2537 | 22.2059 | 22.3826 | 22.4166 | 22.3703 | 22.0088 | 21.2453 | 22.2907 | 17.4744 | 17.0264 | 16.1295 | 16.1069 | 16.1945 | 17.0663 | 16.8315 | 22.3825 | 22.1519 | 21.7093 | 22.0778 | 21.7987 | 21.3099 | 21.9441 | 21.5326 | 20.9162 | 20.1022 | 20.2852 | 19.8057 | 19.7631 | -0.13171 | -0.21908 | 20.7753 | 22.0983 | 22.4004 | 20.1028 | 21.6874 | 22.1356 | 21.9652 | 21.7255 | 21.2915 | 21.7972 | 21.4587 | 21.0582 | 20.203 | 20.2173 | 20.2468 | 20.1955 | 20.1122 |  | 20.2483 | 19.9695 | 20.1286 | 19.7289 | 20.1065 | 20.3344 |  | 20.4417 |  |  | 20.281 | 20.3475 | 20.6246 | [5 empty] | 21.9462 | 20.3286 | 21.6843 | 22.066 | 19.5599 | 21.1803 | 21.804 | 19.3781 | 19.9134 | 21.0991 |  | 19.7506 | 20.921 | 18.9202 | 19.726 | 20.8191 | 19.4804 | 19.9856 | 19.0918 | 20.1371 | 19.1485 | 20.2349 | 18.8746 | 20.0147 | 21.0337 | 19.4643 | 19.7677 | 20.9688 | 18.8988 | 19.8067 | 20.8075 | 19.0123 | 20.0874 | 19.3114 | 19.8795 | 18.9378 | 20.1313 | -0.12108 | 20.9464 | 0.047995 | 0.0155 | -27.0568 | 3.0975 | 18.59 | 0.05 | 0.79065 | -0.52605 | -6.815 | -0.1396 | 0.64682 | -16.7089 | 4.8779 | 0.42394 | 0.42389 | 0.42983 | 0.35688 | 0.47892 | 0.44033 | 0.42874
42838.416 | -373 | 22.8894 | 22.8583 | 22.8428 | 22.7706 | 22.4108 | 21.7542 | 22.7194 | 21.8174 | 22.3752 | 22.381 | 22.3613 | 22.0425 | 21.2615 | 22.234 | 21.5707 | 21.747 | 21.8788 | 21.0775 | 21.1672 | 21.3941 | 20.4731 | 20.6236 | 20.9137 | 21.889 | 21.6527 | 21.2973 | 20.3065 | 20.3525 | 20.3668 | 22.0336 | 21.6462 | 21.1744 | 21.9818 | 21.7293 | 21.3468 | 19.9284 | 20.4703 |  | 20.5491 | 20.082 | 20.1853 | 19.1512 |  | 16.7609 | 16.7516 | 16.4676 | 16.7246 | 16.8525 | 17.4082 | 17.9783 | 15.6092 | 16.8609 | 16.088 | 16.9026 | 17.8749 | 44.7227 | 47.5603 | 43.8717 | 21.3983 |  |  | 0.39844 | -0.049349 | -33.1076 | -0.099926 | 0.22421 | -197.7974 | 16.5622 | -0.16332 | 0.2556 | 0.020042 | -0.10439 | 8.8298 | 9.0595 | 1.9788 | 21.7881 | 22.0167 | 22.2121 | 22.274 | 22.1035 | 21.434 | 20.2533 | 22.2119 | 22.3871 | 22.4154 | 22.3697 | 22.0064 | 21.24 | 22.2837 | 17.4605 | 17.0013 | 16.1107 | 16.1227 | 16.1919 | 17.0598 | 16.8249 | 22.3876 | 22.1456 | 21.7145 | 22.0857 | 21.8023 | 21.3154 | 21.9416 | 21.5311 | 20.9124 | 20.1111 | 20.2903 | 19.8124 | 19.7567 | -0.12778 | -0.23658 | 20.7715 | 22.0936 | 22.3974 | 20.0964 | 21.6859 | 22.131 | 21.9546 | 21.717 | 21.2889 | 21.7952 | 21.453 | 21.0587 | 20.1958 | 20.2211 | 20.2457 | 20.1946 | 20.1206 |  | 20.2402 | 19.9582 | 20.1284 | 19.7176 | 20.1093 | 20.3338 |  | 20.4393 |  |  | 20.2755 | 20.3649 | 20.6305 | [5 empty] | 21.9532 | 20.3299 | 21.6894 | 22.0699 | 19.5666 | 21.1923 | 21.7979 | 19.3764 | 19.9206 | 21.1076 |  | 19.7616 | 20.9215 | 18.9166 | 19.7376 | 20.8289 | 19.4919 | 19.9947 | 19.0995 | 20.1556 | 19.163 | 20.2394 | 18.8794 | 20.0309 | 21.0331 | 19.4664 | 19.777 | 20.9713 | 18.8944 | 19.8012 | 20.8069 | 19.015 | 20.1067 | 19.3166 | 19.8778 | 18.932 | 20.1387 | 0.021571 | 20.9458 | 0.048376 | 0.015791 | -27.0209 | 3.0975 | -10.15 | -0.17 | 0.75364 | -0.26359 | -6.8274 | -0.37509 | 0.56248 | -16.7068 | 4.8344 | 0.42344 | 0.4242 | 0.43024 | 0.35767 | 0.48025 | 0.43992 | 0.42922
42838.416 | -372 | 22.8847 | 22.8505 | 22.8472 | 22.7743 | 22.4061 | 21.7478 | 22.7093 | 21.8115 | 22.3686 | 22.3806 | 22.3624 | 22.0415 | 21.2577 | 22.2342 | 21.5819 | 21.7552 | 21.8899 | 21.0777 | 21.1784 | 21.4011 | 20.4768 | 20.6293 | 20.9223 | 21.8943 | 21.6613 | 21.3048 | 20.3191 | 20.3623 | 20.3517 | 22.038 | 21.6542 | 21.1824 | 21.9879 | 21.7274 | 21.356 | 19.9331 | 20.4742 |  | 20.5564 | 20.076 | 20.1926 | 19.1662 |  | 16.7663 | 16.758 | 16.4673 | 16.7272 | 16.8754 | 17.4488 | 17.9865 | 15.5688 | 16.8647 | 16.0992 | 16.9036 | 17.8734 | 44.7159 | 47.5574 | 43.8763 | 21.4013 |  |  | 0.3071 | -0.20114 | -32.3782 | 0.13138 | 0.29189 | -197.8026 | 16.9197 | -0.1469 | 0.13962 | -0.007022 | 0.11869 | 8.829 | 9.0588 | 1.9785 | 21.7879 | 22.0209 | 22.2069 | 22.2661 | 22.1068 | 21.4341 | 20.2535 | 22.2075 | 22.386 | 22.4102 | 22.368 | 22.0011 | 21.2413 | 22.2809 | 17.4555 | 16.996 | 16.1193 | 16.135 | 16.2023 | 17.0609 | 16.8309 | 22.3841 | 22.1489 | 21.7091 | 22.0866 | 21.7996 | 21.308 | 21.944 | 21.5275 | 20.9108 | 20.1157 | 20.284 | 19.8096 | 19.7534 | -0.10065 | -0.14015 | 20.7727 | 22.0975 | 22.3991 | 20.1039 | 21.6885 | 22.1358 | 21.9616 | 21.7222 | 21.2952 | 21.7923 | 21.4572 | 21.0681 | 20.2005 | 20.2278 | 20.2506 | 20.2032 | 20.13 |  | 20.2431 | 19.9658 | 20.123 | 19.71 | 20.1119 | 20.3413 |  | 20.4413 |  |  | 20.2696 | 20.362 | 20.6472 | [5 empty] | 21.9569 | 20.3309 | 21.6905 | 22.0711 | 19.5595 | 21.1798 | 21.8049 | 19.3667 | 19.9104 | 21.1043 |  | 19.7545 | 20.9169 | 18.9217 | 19.7281 | 20.8226 | 19.4874 | 19.9887 | 19.0996 | 20.1541 | 19.1556 | 20.2416 | 18.8781 | 20.0253 | 21.0194 | 19.4645 | 19.7667 | 20.959 | 18.8915 | 19.7943 | 20.8009 | 19.0124 | 20.0944 | 19.3083 | 19.8719 | 18.9362 | 20.1371 | -0.10698 | 20.9425 | 0.048383 | 0.015631 | -27.0418 | 3.0976 | -2.61 | 0.05 | 0.66163 | -0.53217 | -6.7519 | 0.43009 | 0.64184 | -16.7082 | 4.8866 | 0.42327 | 0.42381 | 0.43054 | 0.35835 | 0.47999 | 0.43966 | 0.42946
42838.416 | -371 | 22.884 | 22.8583 | 22.8469 | 22.7712 | 22.4154 | 21.7492 | 22.7072 | 21.8109 | 22.3739 | 22.3777 | 22.3609 | 22.0372 | 21.2577 | 22.2297 | 21.5849 | 21.7542 | 21.89 | 21.0864 | 21.1774 | 21.4026 | 20.4878 | 20.6308 | 20.9217 | 21.8969 | 21.6721 | 21.3032 | 20.3102 | 20.3635 | 20.3462 | 22.0461 | 21.6513 | 21.172 | 21.9866 | 21.7319 | 21.3456 | 19.9261 | 20.4705 |  | 20.5549 | 20.0833 | 20.1904 | 19.1612 |  | 16.7654 | 16.7584 | 16.4763 | 16.7359 | 16.9043 | 17.4868 | 17.9709 | 15.5541 | 16.8674 | 16.1169 | 16.905 | 17.8807 | 44.7178 | 47.5555 | 43.8853 | 21.4064 |  |  | 0.29725 | -0.21231 | -32.39 | 0.44548 | 0.26166 | -197.7901 | 16.7482 | -0.14098 | -0.25405 | 0.1327 | -0.10838 | 8.8287 | 9.0582 | 1.979 | 21.7906 | 22.0185 | 22.2061 | 22.2723 | 22.1029 | 21.4275 | 20.2494 | 22.2016 | 22.3791 | 22.4117 | 22.3658 | 21.9946 | 21.2353 | 22.2843 | 17.472 | 17.0073 | 16.1211 | 16.1505 | 16.2119 | 17.0687 | 16.8426 | 22.3846 | 22.1511 | 21.7121 | 22.0858 | 21.8034 | 21.3127 | 21.9499 | 21.5281 | 20.9134 | 20.1133 | 20.2788 | 19.8104 | 19.755 | 0.0354 | -0.025456 | 20.7726 | 22.0937 | 22.3944 | 20.1041 | 21.6844 | 22.1339 | 21.967 | 21.7231 | 21.2928 | 21.7857 | 21.459 | 21.0637 | 20.2039 | 20.2224 | 20.2518 | 20.2005 | 20.1444 |  | 20.2435 | 19.962 | 20.1337 | 19.7086 | 20.1108 | 20.3372 |  | 20.4451 |  |  | 20.2662 | 20.3476 | 20.6496 | [5 empty] | 21.9638 | 20.3439 | 21.6908 | 22.0713 | 19.5702 | 21.1917 | 21.8054 | 19.3632 | 19.9113 | 21.1038 |  | 19.7467 | 20.913 | 18.9196 | 19.7221 | 20.8223 | 19.4912 | 19.9887 | 19.1016 | 20.1564 | 19.163 | 20.2395 | 18.8701 | 20.0203 | 21.0179 | 19.4616 | 19.7642 | 20.9577 | 18.8903 | 19.7886 | 20.8007 | 19.0069 | 20.0932 | 19.3069 | 19.863 | 18.9291 | 20.1368 | -0.20919 | 20.9453 | 0.04912 | 0.015812 | -27.0464 | 3.0975 | -11.78 | -0.07 | 0.65092 | -0.54675 | -6.7531 | 0.79198 | 0.60774 | -16.7088 | 4.8621 | 0.42288 | 0.42427 | 0.43055 | 0.35742 | 0.48115 | 0.43956 | 0.42934
42838.416 | -370 | 22.8879 | 22.8567 | 22.8419 | 22.7735 | 22.4062 | 21.7489 | 22.7079 | 21.8152 | 22.367 | 22.38 | 22.3712 | 22.0351 | 21.2604 | 22.226 | 21.5736 | 21.7482 | 21.8807 | 21.0797 | 21.1721 | 21.3978 | 20.4805 | 20.6201 | 20.9135 | 21.8895 | 21.6593 | 21.2938 | 20.2995 | 20.3623 | 20.3281 | 22.0397 | 21.6435 | 21.171 | 21.9807 | 21.7243 | 21.337 | 19.9282 | 20.4665 |  | 20.5594 | 20.0736 | 20.1863 | 19.1504 |  | 16.7716 | 16.7666 | 16.4916 | 16.7402 | 16.9074 | 17.5002 | 17.9718 | 15.6241 | 16.8686 | 16.1557 | 16.9062 | 17.8651 | 44.7111 | 47.543 | 43.8844 | 21.3997 |  |  | 0.56207 | -0.44493 | -32.5589 | 0.33574 | 0.12958 | -197.823 | 16.7791 | -0.14624 | -0.24958 | 0.10921 | 0.05619 | 8.8288 | 9.0588 | 1.9792 | 21.7822 | 22.0133 | 22.2057 | 22.2673 | 22.1005 | 21.4297 | 20.2489 | 22.2023 | 22.3756 | 22.4125 | 22.3614 | 21.9974 | 21.2388 | 22.2788 | 17.462 | 16.994 | 16.116 | 16.1541 | 16.2273 | 17.0646 | 16.8338 | 22.3892 | 22.1479 | 21.7145 | 22.08 | 21.8118 | 21.3058 | 21.9511 | 21.5237 | 20.9166 | 20.1088 | 20.2801 | 19.81 | 19.7499 | 0.041298 | -0.22041 | 20.7727 | 22.0902 | 22.3986 | 20.1014 | 21.684 | 22.1345 | 21.9558 | 21.7196 | 21.2874 | 21.7868 | 21.4611 | 21.0605 | 20.2043 | 20.2193 | 20.2558 | 20.1977 | 20.1498 |  | 20.2386 | 19.9591 | 20.1306 | 19.7103 | 20.1151 | 20.3435 |  | 20.4406 |  |  | 20.2619 | 20.3448 | 20.6427 | [5 empty] | 21.9544 | 20.3426 | 21.6924 | 22.07 | 19.5654 | 21.1935 | 21.8084 | 19.3589 | 19.904 | 21.0986 |  | 19.7482 | 20.9159 | 18.923 | 19.7254 | 20.8182 | 19.4922 | 19.9822 | 19.0979 | 20.1534 | 19.1644 | 20.2383 | 18.8691 | 20.0194 | 21.0137 | 19.4628 | 19.7619 | 20.9604 | 18.8929 | 19.7827 | 20.7991 | 19.0088 | 20.0914 | 19.3076 | 19.8718 | 18.931 | 20.1384 | -0.13944 | 20.9466 | 0.048764 | 0.015478 | -27.0293 | 3.0975 | -10.79 | -0.04 | 0.89505 | -0.7915 | -6.7708 | 0.68755 | 0.42769 | -16.7105 | 4.8667 | 0.42257 | 0.42425 | 0.43064 | 0.35806 | 0.4807 | 0.43993 | 0.42933
42838.416 | -369 | 22.8861 | 22.8529 | 22.8394 | 22.7696 | 22.4119 | 21.7447 | 22.7059 | 21.8118 | 22.3611 | 22.3732 | 22.3661 | 22.0395 | 21.2572 | 22.2209 | 21.5763 | 21.7496 | 21.8875 | 21.0801 | 21.1674 | 21.3942 | 20.4756 | 20.619 | 20.9151 | 21.8862 | 21.6626 | 21.2915 | 20.302 | 20.3592 | 20.3171 | 22.0399 | 21.6469 | 21.1813 | 21.9823 | 21.7275 | 21.3449 | 19.9277 | 20.4655 |  | 20.5612 | 20.076 | 20.1864 | 19.1506 |  | 16.7551 | 16.7536 | 16.4686 | 16.7373 | 16.904 | 17.482 | 17.9322 | 15.7004 | 16.8531 | 16.1549 | 16.8956 | 17.8727 | 44.702 | 47.5421 | 43.8938 | 21.404 |  |  | 0.54367 | -0.37594 | -33.2226 | 0.39028 | 0.14995 | -197.846 | 16.3519 | -0.31578 | -0.13476 | 0.24327 | -0.046581 | 8.8282 | 9.0582 | 1.9791 | 21.7863 | 22.0126 | 22.2064 | 22.2692 | 22.1049 | 21.4334 | 20.2435 | 22.2027 | 22.382 | 22.4164 | 22.3704 | 22.0042 | 21.2372 | 22.2776 | 17.4492 | 16.9812 | 16.1171 | 16.1534 | 16.2348 | 17.0615 | 16.8327 | 22.3847 | 22.1537 | 21.7152 | 22.0866 | 21.8048 | 21.3078 | 21.9506 | 21.5349 | 20.9173 | 20.1113 | 20.2879 | 19.8071 | 19.7626 | 0.012005 | -0.17457 | 20.7644 | 22.0876 | 22.3953 | 20.1029 | 21.6847 | 22.1301 | 21.9528 | 21.7209 | 21.2864 | 21.7929 | 21.4654 | 21.0563 | 20.2037 | 20.2189 | 20.25 | 20.1999 | 20.1363 |  | 20.2349 | 19.9591 | 20.1251 | 19.7133 | 20.1055 | 20.3439 |  | 20.4366 |  |  | 20.2497 | 20.3434 | 20.6292 | [5 empty] | 21.9514 | 20.3436 | 21.6792 | 22.0629 | 19.5525 | 21.1818 | 21.8075 | 19.3612 | 19.9144 | 21.1027 |  | 19.7531 | 20.9224 | 18.9216 | 19.7292 | 20.8204 | 19.4984 | 19.9854 | 19.0994 | 20.1606 | 19.1665 | 20.2385 | 18.8719 | 20.0178 | 21.0179 | 19.4537 | 19.7633 | 20.9544 | 18.8962 | 19.7861 | 20.7946 | 19.0139 | 20.0905 | 19.3071 | 19.8729 | 18.9256 | 20.1375 | -0.22143 | 20.9467 | 0.048585 | 0.014498 | -27.0317 | 3.0975 | -15.08 | -0.09 | 0.88026 | -0.72753 | -6.8393 | 0.74128 | 0.46006 | -16.711 | 4.8042 | 0.42282 | 0.42406 | 0.43024 | 0.35913 | 0.48045 | 0.43991 | 0.42906
42838.416 | -368 | 22.8853 | 22.8531 | 22.8408 | 22.7631 | 22.4099 | 21.7402 | 22.708 | 21.8109 | 22.3652 | 22.3752 | 22.3645 | 22.0367 | 21.2592 | 22.222 | 21.5829 | 21.7538 | 21.8921 | 21.0808 | 21.1683 | 21.3903 | 20.4753 | 20.6257 | 20.9185 | 21.8922 | 21.6578 | 21.2936 | 20.2939 | 20.361 | 20.3116 | 22.0351 | 21.6511 | 21.1745 | 21.9831 | 21.7239 | 21.348 | 19.9281 | 20.4561 |  | 20.5454 | 20.0712 | 20.1851 | 19.1532 |  | 16.7618 | 16.7566 | 16.4808 | 16.7527 | 16.9274 | 17.4856 | 17.934 | 15.7731 | 16.8606 | 16.1755 | 16.9039 | 17.8779 | 44.6966 | 47.5478 | 43.9045 | 21.4079 |  |  | 0.51935 | -0.21034 | -32.9315 | 0.39423 | 0.14404 | -197.8368 | 16.484 | -0.24481 | -0.19373 | 0.037246 | -0.0076944 | 8.8289 | 9.0585 | 1.979 | 21.7745 | 22.0127 | 22.2033 | 22.2635 | 22.0997 | 21.4296 | 20.2458 | 22.2048 | 22.3753 | 22.4157 | 22.3711 | 21.9999 | 21.2286 | 22.2843 | 17.4334 | 17.0324 | 16.1118 | 16.1537 | 16.2262 | 17.061 | 16.8276 | 22.3843 | 22.1563 | 21.716 | 22.0886 | 21.8065 | 21.314 | 21.9461 | 21.537 | 20.9132 | 20.11 | 20.2856 | 19.8039 | 19.7696 | 0.071771 | -0.23981 | 20.7611 | 22.0959 | 22.3934 | 20.11 | 21.6907 | 22.1301 | 21.9604 | 21.727 | 21.2938 | 21.7931 | 21.4577 | 21.0576 | 20.2094 | 20.2262 | 20.2488 | 20.2064 | 20.1435 |  | 20.2468 | 19.9629 | 20.1359 | 19.7207 | 20.1084 | 20.3488 |  | 20.4358 |  |  | 20.2498 | 20.3442 | 20.6316 | [5 empty] | 21.9531 | 20.3467 | 21.6836 | 22.0671 | 19.5582 | 21.1778 | 21.8017 | 19.3515 | 19.9078 | 21.0995 |  | 19.7525 | 20.9161 | 18.9176 | 19.7276 | 20.8169 | 19.4915 | 19.9824 | 19.1009 | 20.1585 | 19.1715 | 20.241 | 18.88 | 20.021 | 21.0188 | 19.4641 | 19.7682 | 20.9579 | 18.8949 | 19.7806 | 20.8032 | 19.0198 | 20.1008 | 19.3144 | 19.8702 | 18.9319 | 20.1473 | -0.10513 | 20.9467 | 0.047492 | 0.014106 | -27.1223 | 3.0975 | -4.83 | 0.05 | 0.86035 | -0.5442 | -6.8093 | 0.74502 | 0.4509 | -16.7107 | 4.8236 | 0.42302 | 0.42432 | 0.43013 | 0.36083 | 0.48044 | 0.43986 | 0.42882
42838.416 | -367 | 22.8908 | 22.8602 | 22.8398 | 22.7734 | 22.4078 | 21.7491 | 22.7155 | 21.8104 | 22.3626 | 22.3792 | 22.3644 | 22.0448 | 21.2666 | 22.2284 | 21.5716 | 21.7516 | 21.8862 | 21.0757 | 21.1653 | 21.3962 | 20.4729 | 20.6234 | 20.9103 | 21.8891 | 21.6507 | 21.2935 | 20.2809 | 20.3546 | 20.3027 | 22.0392 | 21.6534 | 21.1789 | 21.9817 | 21.728 | 21.3514 | 19.9307 | 20.4488 |  | 20.5501 | 20.0776 | 20.184 | 19.158 |  | 16.7577 | 16.7556 | 16.4791 | 16.7555 | 16.9183 | 17.4739 | 17.9527 | 15.8297 | 16.8503 | 16.1864 | 16.9054 | 17.8748 | 44.6812 | 47.5531 | 43.9111 | 21.4088 |  |  | 0.52658 | -0.36345 | -33.3028 | 0.41788 | 0.16901 | -197.8558 | 15.7894 | -0.43537 | -0.036102 | -0.19081 | -0.045539 | 8.8287 | 9.0582 | 1.9785 | 21.7872 | 22.0119 | 22.2093 | 22.2833 | 22.1087 | 21.4397 | 20.2544 | 22.2104 | 22.3762 | 22.4225 | 22.3677 | 22.0019 | 21.2394 | 22.2841 | 17.4172 | 17.0987 | 16.1134 | 16.1725 | 16.2418 | 17.0717 | 16.8333 | 22.3905 | 22.157 | 21.718 | 22.0915 | 21.8087 | 21.3146 | 21.9542 | 21.5398 | 20.9182 | 20.1147 | 20.2859 | 19.8134 | 19.7804 | 0.062531 | -0.16906 | 20.7735 | 22.0963 | 22.3984 | 20.1131 | 21.6921 | 22.1358 | 21.9659 | 21.7311 | 21.2987 | 21.7923 | 21.4632 | 21.0637 | 20.209 | 20.2345 | 20.2532 | 20.2036 | 20.1428 |  | 20.2378 | 19.955 | 20.1304 | 19.7294 | 20.1077 | 20.3421 |  | 20.4447 |  |  | 20.2585 | 20.3587 | 20.6451 | [5 empty] | 21.9595 | 20.3492 | 21.693 | 22.0787 | 19.5632 | 21.1867 | 21.8108 | 19.3403 | 19.8949 | 21.0876 |  | 19.7484 | 20.9133 | 18.9196 | 19.7173 | 20.8211 | 19.4881 | 19.9785 | 19.1043 | 20.1592 | 19.1749 | 20.2455 | 18.8825 | 20.0198 | 21.0138 | 19.4626 | 19.7724 | 20.9565 | 18.8999 | 19.7825 | 20.8033 | 19.0172 | 20.0967 | 19.3182 | 19.8793 | 18.9325 | 20.1514 | -0.12108 | 20.9464 | 0.047277 | 0.013163 | -27.0826 | 3.0975 | -8.31 | -0.04 | 0.8663 | -0.71535 | -6.8476 | 0.76705 | 0.48842 | -16.7112 | 4.7208 | 0.42274 | 0.42436 | 0.42986 | 0.36387 | 0.48092 | 0.43981 | 0.42868
42838.416 | -366 | 22.8915 | 22.8608 | 22.8407 | 22.7703 | 22.4113 | 21.752 | 22.7129 | 21.8201 | 22.3662 | 22.3796 | 22.3618 | 22.0463 | 21.2626 | 22.2263 | 21.5687 | 21.7561 | 21.8879 | 21.0775 | 21.1639 | 21.3924 | 20.47 | 20.6151 | 20.9153 | 21.8883 | 21.6511 | 21.2895 | 20.2828 | 20.3523 | 20.2855 | 22.0473 | 21.654 | 21.1881 | 21.9887 | 21.7326 | 21.3523 | 19.9361 | 20.45 |  | 20.561 | 20.0896 | 20.1951 | 19.1669 |  | 16.7607 | 16.7591 | 16.4776 | 16.7629 | 16.9239 | 17.4818 | 17.9435 | 15.8437 | 16.8629 | 16.1912 | 16.9054 | 17.8722 | 44.6655 | 47.5512 | 43.9002 | 21.4057 |  |  | 0.4037 | -0.30037 | -34.4836 | 0.041354 | 0.2748 | -197.8289 | 15.7993 | -0.58454 | 0.0575 | -0.13542 | 0.002548 | 8.8282 | 9.0579 | 1.9784 | 21.7888 | 22.0138 | 22.2101 | 22.2734 | 22.1097 | 21.4345 | 20.2535 | 22.2099 | 22.3812 | 22.4188 | 22.3664 | 22.0016 | 21.2412 | 22.2861 | 17.3809 | 17.1133 | 16.1136 | 16.1783 | 16.2362 | 17.0637 | 16.8244 | 22.3801 | 22.151 | 21.7185 | 22.0823 | 21.8029 | 21.3113 | 21.9504 | 21.5364 | 20.9113 | 20.111 | 20.2826 | 19.8023 | 19.7773 | 0.16555 | -0.1877 | 20.7721 | 22.0942 | 22.4043 | 20.1111 | 21.6893 | 22.1349 | 21.9639 | 21.7233 | 21.2997 | 21.7982 | 21.4582 | 21.0603 | 20.2126 | 20.2371 | 20.2482 | 20.2021 | 20.1295 |  | 20.2365 | 19.9409 | 20.1181 | 19.7259 | 20.0997 | 20.3359 |  | 20.438 |  |  | 20.2639 | 20.357 | 20.645 | [5 empty] | 21.9586 | 20.3413 | 21.6925 | 22.0706 | 19.5622 | 21.1854 | 21.8099 | 19.3375 | 19.8892 | 21.091 |  | 19.7497 | 20.9094 | 18.9168 | 19.72 | 20.8176 | 19.4883 | 19.9754 | 19.1039 | 20.163 | 19.1696 | 20.2476 | 18.8796 | 20.0179 | 21.0089 | 19.4549 | 19.7701 | 20.9484 | 18.8976 | 19.7792 | 20.7977 | 19.0169 | 20.0894 | 19.3178 | 19.8795 | 18.9354 | 20.1508 | -0.17617 | 20.9463 | 0.048647 | 0.0137 | -26.9817 | 3.0976 | 3.01 | -0.24 | 0.75849 | -0.65032 | -6.9679 | 0.2413 | 0.6228 | -16.7103 | 4.7223 | 0.42306 | 0.42434 | 0.42969 | 0.36696 | 0.47986 | 0.43974 | 0.42864
42838.4161 | -365 | 22.8856 | 22.8499 | 22.829 | 22.7661 | 22.4065 | 21.739 | 22.7154 | 21.809 | 22.358 | 22.3708 | 22.3512 | 22.0368 | 21.2576 | 22.2218 | 21.5775 | 21.7584 | 21.8937 | 21.0819 | 21.1668 | 21.3935 | 20.474 | 20.6236 | 20.9197 | 21.8974 | 21.6557 | 21.2919 | 20.2873 | 20.3644 | 20.2619 | 22.0423 | 21.6444 | 21.1732 | 21.9931 | 21.73 | 21.3477 | 19.9246 | 20.4317 |  | 20.558 | 20.0817 | 20.1927 | 19.1681 |  | 16.7596 | 16.7698 | 16.4867 | 16.7647 | 16.9491 | 17.4835 | 17.9228 | 15.8719 | 16.8628 | 16.1703 | 16.9066 | 17.8642 | 44.6509 | 47.5497 | 43.9041 | 21.4012 |  |  | 0.37216 | -0.37331 | -34.0939 | 0.2812 | 0.1263 | -197.8657 | 15.7553 | -0.54182 | -0.035518 | -0.026953 | 0.023033 | 8.8289 | 9.0586 | 1.9794 | 21.7821 | 22.008 | 22.2071 | 22.2722 | 22.1086 | 21.4311 | 20.25 | 22.2087 | 22.3823 | 22.4126 | 22.3665 | 22.0028 | 21.2386 | 22.285 | 17.3572 | 17.1274 | 16.1249 | 16.1955 | 16.2505 | 17.0683 | 16.8301 | 22.378 | 22.1514 | 21.7138 | 22.08 | 21.7965 | 21.3071 | 21.9502 | 21.5317 | 20.9099 | 20.103 | 20.2753 | 19.7991 | 19.7744 | 0.089858 | -0.24228 | 20.7727 | 22.0987 | 22.4024 | 20.1081 | 21.6866 | 22.1389 | 21.9661 | 21.7311 | 21.2989 | 21.7974 | 21.4549 | 21.0577 | 20.2169 | 20.2378 | 20.2585 | 20.2062 | 20.1345 |  | 20.2356 | 19.9374 | 20.124 | 19.7244 | 20.1062 | 20.3439 |  | 20.4426 |  |  | 20.2707 | 20.3636 | 20.6459 | [5 empty] | 21.9579 | 20.3477 | 21.6924 | 22.0723 | 19.5671 | 21.1876 | 21.8102 | 19.3341 | 19.8938 | 21.0909 |  | 19.7499 | 20.9118 | 18.9114 | 19.7185 | 20.815 | 19.4875 | 19.9766 | 19.1059 | 20.1592 | 19.1723 | 20.2482 | 18.8723 | 20.0102 | 21.0073 | 19.4521 | 19.7604 | 20.9402 | 18.8924 | 19.7719 | 20.7952 | 19.0095 | 20.09 | 19.3097 | 19.8702 | 18.9277 | 20.1469 | -0.14668 | 20.9473 | 0.049956 | 0.015442 | -27.0911 | 3.0975 | 5.56 | -0.06 | 0.72823 | -0.725 | -6.9286 | 0.62924 | 0.42222 | -16.7119 | 4.7158 | 0.42289 | 0.42463 | 0.42995 | 0.37014 | 0.47928 | 0.43932 | 0.42846
42838.4161 | -364 | 22.8888 | 22.8592 | 22.8421 | 22.7667 | 22.4041 | 21.748 | 22.7151 | 21.8166 | 22.3641 | 22.3799 | 22.3645 | 22.0403 | 21.2649 | 22.231 | 21.5733 | 21.7508 | 21.8847 | 21.0753 | 21.1663 | 21.392 | 20.4687 | 20.6191 | 20.9105 | 21.8885 | 21.6504 | 21.2956 | 20.2765 | 20.3637 | 20.2367 | 22.0392 | 21.648 | 21.1716 | 21.9901 | 21.7345 | 21.3496 | 19.926 | 20.423 |  | 20.5497 | 20.0721 | 20.1863 | 19.1726 |  | 16.7424 | 16.7547 | 16.476 | 16.7612 | 16.9284 | 17.4585 | 17.8893 | 15.8722 | 16.8597 | 16.1299 | 16.9043 | 17.8727 | 44.6356 | 47.5498 | 43.9025 | 21.4058 |  |  | 0.40239 | -0.24451 | -32.94 | 0.2858 | 0.11776 | -197.7967 | 15.9412 | -0.60688 | 0.018386 | 0.082982 | 0.0035896 | 8.8296 | 9.0593 | 1.9792 | 21.7781 | 22.0089 | 22.206 | 22.2656 | 22.1007 | 21.4242 | 20.249 | 22.2018 | 22.3804 | 22.4085 | 22.3626 | 22.0006 | 21.2366 | 22.2752 | 17.3302 | 17.1452 | 16.1403 | 16.2153 | 16.267 | 17.0648 | 16.8269 | 22.3761 | 22.152 | 21.7107 | 22.082 | 21.7988 | 21.3071 | 21.948 | 21.5306 | 20.9129 | 20.1061 | 20.2758 | 19.8032 | 19.7676 | 0.10795 | -0.077571 | 20.767 | 22.0897 | 22.398 | 20.0947 | 21.6853 | 22.1247 | 21.9549 | 21.7267 | 21.2918 | 21.7861 | 21.4506 | 21.0462 | 20.2123 | 20.2309 | 20.2434 | 20.1967 | 20.1165 |  | 20.2326 | 19.922 | 20.1193 | 19.7234 | 20.1012 | 20.3369 |  | 20.429 |  |  | 20.2716 | 20.3676 | 20.6424 | [5 empty] | 21.9567 | 20.3466 | 21.6889 | 22.0737 | 19.5694 | 21.1928 | 21.8076 | 19.3313 | 19.8918 | 21.0887 |  | 19.7486 | 20.9088 | 18.9048 | 19.7216 | 20.8165 | 19.4899 | 19.9735 | 19.099 | 20.1605 | 19.1768 | 20.2509 | 18.8809 | 20.0242 | 21.0153 | 19.4598 | 19.7676 | 20.9532 | 18.9016 | 19.781 | 20.7981 | 19.0178 | 20.1003 | 19.3202 | 19.8769 | 18.9349 | 20.1558 | -0.10698 | 20.9471 | 0.049839 | 0.01505 | -27.1334 | 3.0975 | 13.04 | -0.15 | 0.7572 | -0.58674 | -6.8102 | 0.63435 | 0.40767 | -16.7082 | 4.7433 | 0.42329 | 0.4249 | 0.42981 | 0.37272 | 0.4772 | 0.43924 | 0.42875
42838.4161 | -363 | 22.9013 | 22.8621 | 22.8521 | 22.7727 | 22.4183 | 21.7512 | 22.7194 | 21.8267 | 22.3716 | 22.387 | 22.3692 | 22.0505 | 21.2688 | 22.2367 | 21.5696 | 21.7447 | 21.8772 | 21.0706 | 21.1708 | 21.3908 | 20.4653 | 20.6009 | 20.9071 | 21.8818 | 21.6529 | 21.2857 | 20.257 | 20.358 | 20.2069 | 22.0373 | 21.6446 | 21.1766 | 21.983 | 21.7243 | 21.3512 | 19.9303 | 20.4186 |  | 20.5534 | 20.0791 | 20.1901 | 19.1796 |  | 16.7413 | 16.7557 | 16.4699 | 16.765 | 16.9243 | 17.4382 | 17.8947 | 15.8627 | 16.8616 | 16.0989 | 16.9049 | 17.8711 | 44.6127 | 47.5394 | 43.891 | 21.4023 |  |  | 0.46021 | -0.13017 | -32.67 | 0.36531 | 0.22224 | -197.7895 | 16.5543 | -0.4932 | -0.18283 | -0.24598 | 0.047163 | 8.8286 | 9.0583 | 1.9785 | 21.7789 | 22.0076 | 22.2045 | 22.2642 | 22.1032 | 21.4266 | 20.2443 | 22.1978 | 22.3759 | 22.4055 | 22.3653 | 21.999 | 21.2304 | 22.2763 | 17.3019 | 17.1653 | 16.1363 | 16.2182 | 16.2774 | 17.0656 | 16.8238 | 22.3825 | 22.1536 | 21.7093 | 22.0928 | 21.8051 | 21.3109 | 21.948 | 21.5379 | 20.9103 | 20.1159 | 20.278 | 19.8093 | 19.7639 | -0.067028 | -0.015375 | 20.7629 | 22.094 | 22.3986 | 20.0992 | 21.6874 | 22.1227 | 21.9622 | 21.7251 | 21.2878 | 21.7865 | 21.4538 | 21.0526 | 20.2099 | 20.2404 | 20.2481 | 20.2053 | 20.1252 |  | 20.2352 | 19.921 | 20.1285 | 19.7284 | 20.1135 | 20.3448 |  | 20.439 |  |  | 20.2682 | 20.3644 | 20.6365 | [5 empty] | 21.9484 | 20.3391 | 21.6837 | 22.0673 | 19.5643 | 21.1831 | 21.8133 | 19.3254 | 19.8845 | 21.0852 |  | 19.7459 | 20.9057 | 18.8922 | 19.7174 | 20.8131 | 19.4852 | 19.9744 | 19.0974 | 20.1576 | 19.1762 | 20.2445 | 18.8853 | 20.0277 | 21.021 | 19.4568 | 19.7696 | 20.9593 | 18.9021 | 19.7854 | 20.8006 | 19.0209 | 20.1035 | 19.3282 | 19.8766 | 18.944 | 20.163 | -0.094181 | 20.948 | 0.049556 | 0.015812 | -27.1463 | 3.0975 | -0.61 | -0.02 | 0.80974 | -0.42811 | -6.7822 | 0.71718 | 0.56003 | -16.7073 | 4.8335 | 0.42314 | 0.42524 | 0.43008 | 0.37597 | 0.47727 | 0.43919 | 0.42918
42838.4161 | -362 | 22.8978 | 22.855 | 22.8399 | 22.7701 | 22.4104 | 21.744 | 22.7113 | 21.8146 | 22.3645 | 22.3804 | 22.3589 | 22.0434 | 21.2605 | 22.2285 | 21.5733 | 21.7503 | 21.8888 | 21.0775 | 21.1753 | 21.3869 | 20.4784 | 20.6088 | 20.919 | 21.8902 | 21.655 | 21.2899 | 20.2633 | 20.3642 | 20.1993 | 22.0385 | 21.6464 | 21.1795 | 21.986 | 21.7272 | 21.3523 | 19.9311 | 20.4082 |  | 20.5453 | 20.0748 | 20.1874 | 19.1854 |  | 16.7256 | 16.7433 | 16.4611 | 16.7464 | 16.9013 | 17.4302 | 17.9046 | 15.8701 | 16.8621 | 16.0655 | 16.9065 | 17.8673 | 44.5916 | 47.5363 | 43.8907 | 21.403 |  |  | 0.42275 | -0.24977 | -31.9951 | 0.27463 | 0.16704 | -197.8716 | 16.4045 | -0.54182 | -0.20521 | -0.065766 | -0.20733 | 8.8281 | 9.0575 | 1.9788 | 21.7838 | 22.0165 | 22.2187 | 22.2779 | 22.1055 | 21.4329 | 20.2496 | 22.2019 | 22.3833 | 22.411 | 22.3766 | 21.9999 | 21.2417 | 22.2842 | 17.2829 | 17.1968 | 16.1362 | 16.2072 | 16.2867 | 17.0617 | 16.8219 | 22.3816 | 22.1548 | 21.7106 | 22.0871 | 21.8051 | 21.3085 | 21.9449 | 21.5377 | 20.9118 | 20.1117 | 20.2719 | 19.807 | 19.7573 | -0.052677 | 0.11681 | 20.7619 | 22.085 | 22.3947 | 20.092 | 21.6834 | 22.1294 | 21.9622 | 21.7222 | 21.2918 | 21.7853 | 21.4564 | 21.0606 | 20.2056 | 20.2401 | 20.2439 | 20.2037 | 20.1306 |  | 20.2417 | 19.9225 | 20.1362 | 19.728 | 20.1122 | 20.3444 |  | 20.4371 |  |  | 20.2586 | 20.3675 | 20.6366 | [5 empty] | 21.952 | 20.3324 | 21.6794 | 22.0582 | 19.5555 | 21.1716 | 21.8084 | 19.3234 | 19.8773 | 21.0797 |  | 19.7472 | 20.9097 | 18.8858 | 19.7117 | 20.8083 | 19.478 | 19.9785 | 19.0984 | 20.1578 | 19.1764 | 20.2435 | 18.8788 | 20.0213 | 21.0069 | 19.4484 | 19.7689 | 20.9572 | 18.8931 | 19.7769 | 20.8018 | 19.0162 | 20.0982 | 19.3163 | 19.8743 | 18.939 | 20.1568 | -0.090471 | 20.9471 | 0.049784 | 0.01635 | -27.064 | 3.0976 | 9.56 | -0.18 | 0.77607 | -0.593 | -6.7116 | 0.62181 | 0.48552 | -16.7106 | 4.8115 | 0.42321 | 0.42545 | 0.43005 | 0.37763 | 0.47707 | 0.43906 | 0.42922
42838.4161 | -361 | 22.8951 | 22.8576 | 22.8476 | 22.7669 | 22.4086 | 21.7433 | 22.7106 | 21.8111 | 22.3623 | 22.3828 | 22.3594 | 22.0384 | 21.2642 | 22.2281 | 21.582 | 21.7523 | 21.8855 | 21.0754 | 21.1719 | 21.3923 | 20.4708 | 20.6227 | 20.9161 | 21.8929 | 21.6503 | 21.2927 | 20.2609 | 20.3643 | 20.1959 | 22.0417 | 21.648 | 21.18 | 21.9909 | 21.7308 | 21.3456 | 19.9289 | 20.3988 |  | 20.5455 | 20.076 | 20.1814 | 19.1862 |  | 16.7243 | 16.734 | 16.4563 | 16.7323 | 16.8864 | 17.4092 | 17.9009 | 15.8725 | 16.86 | 16.0577 | 16.9036 | 17.8676 | 44.5753 | 47.5368 | 43.8858 | 21.4154 |  |  | 0.64946 | -0.13017 | -32.0345 | 0.11561 | 0.18938 | -197.8506 | 16.7672 | -0.32103 | 0.040765 | -0.054017 | -0.13876 | 8.8283 | 9.0584 | 1.9785 | 21.7903 | 22.0176 | 22.211 | 22.2708 | 22.0985 | 21.4273 | 20.2531 | 22.2016 | 22.3773 | 22.4168 | 22.3677 | 22.0011 | 21.227 | 22.2813 | 17.2668 | 17.1943 | 16.1447 | 16.2108 | 16.3025 | 17.0698 | 16.8228 | 22.3823 | 22.152 | 21.7092 | 22.0813 | 21.8077 | 21.312 | 21.9455 | 21.5349 | 20.9093 | 20.1134 | 20.277 | 19.8099 | 19.7502 | -0.0080484 | -0.035536 | 20.7702 | 22.0928 | 22.3993 | 20.0877 | 21.69 | 22.1374 | 21.9669 | 21.7258 | 21.3058 | 21.7975 | 21.4613 | 21.0645 | 20.2096 | 20.2524 | 20.2456 | 20.2181 | 20.1213 |  | 20.2277 | 19.9206 | 20.1265 | 19.7216 | 20.1083 | 20.3512 |  | 20.4373 |  |  | 20.2676 | 20.3709 | 20.6387 | [5 empty] | 21.9536 | 20.3401 | 21.6798 | 22.0656 | 19.5635 | 21.1884 | 21.8059 | 19.3215 | 19.8759 | 21.0778 |  | 19.7496 | 20.903 | 18.8922 | 19.7141 | 20.8102 | 19.4784 | 19.9785 | 19.0974 | 20.1632 | 19.1761 | 20.252 | 18.8908 | 20.0125 | 21.0078 | 19.463 | 19.7673 | 20.9538 | 18.8941 | 19.7725 | 20.7957 | 19.0212 | 20.0976 | 19.316 | 19.8702 | 18.9336 | 20.1547 | -0.20845 | 20.9472 | 0.048659 | 0.014186 | -27.0651 | 3.0976 | 3.47 | -0.09 | 0.96191 | -0.42809 | -6.7157 | 0.40344 | 0.51695 | -16.7091 | 4.8642 | 0.423 | 0.42518 | 0.4301 | 0.38036 | 0.47623 | 0.43896 | 0.42947
42838.4161 | -360 | 22.8848 | 22.8568 | 22.8452 | 22.7689 | 22.4041 | 21.745 | 22.7128 | 21.8093 | 22.3597 | 22.3761 | 22.3619 | 22.0374 | 21.2594 | 22.2228 | 21.5752 | 21.7386 | 21.8775 | 21.0646 | 21.1582 | 21.3789 | 20.4624 | 20.6103 | 20.9013 | 21.8851 | 21.6482 | 21.283 | 20.2549 | 20.3605 | 20.19 | 22.0488 | 21.6515 | 21.1793 | 21.9874 | 21.7327 | 21.3476 | 19.9313 | 20.3951 |  | 20.5524 | 20.0776 | 20.1846 | 19.1906 |  | 16.7244 | 16.7264 | 16.4514 | 16.7247 | 16.8659 | 17.379 | 17.8739 | 15.8752 | 16.8526 | 16.0617 | 16.9004 | 17.8758 | 44.5646 | 47.5252 | 43.8762 | 21.4019 |  |  | 0.37873 | 0.087987 | -32.3276 | 0.39094 | 0.14141 | -197.8197 | 16.3881 | -0.26649 | 0.061392 | -0.15409 | 0.090042 | 8.8291 | 9.0586 | 1.9792 | 21.789 | 22.0146 | 22.2076 | 22.276 | 22.0989 | 21.4304 | 20.2496 | 22.2111 | 22.3764 | 22.414 | 22.3685 | 22.0013 | 21.2331 | 22.2853 | 17.2488 | 17.1659 | 16.1603 | 16.2235 | 16.3145 | 17.07 | 16.8287 | 22.3805 | 22.151 | 21.7089 | 22.0763 | 21.7991 | 21.307 | 21.9471 | 21.5268 | 20.9119 | 20.1088 | 20.2681 | 19.801 | 19.7368 | -0.13309 | 0.046059 | 20.7661 | 22.0908 | 22.4016 | 20.0896 | 21.6857 | 22.1398 | 21.9619 | 21.7306 | 21.3 | 21.7918 | 21.4556 | 21.0571 | 20.2153 | 20.2521 | 20.2455 | 20.2123 | 20.1055 |  | 20.2306 | 19.9135 | 20.1183 | 19.7082 | 20.1007 | 20.3456 |  | 20.4368 |  |  | 20.2802 | 20.3777 | 20.6425 | [5 empty] | 21.9578 | 20.3487 | 21.6913 | 22.071 | 19.5676 | 21.1918 | 21.8109 | 19.3233 | 19.8852 | 21.0928 |  | 19.7548 | 20.8966 | 18.8881 | 19.7148 | 20.8188 | 19.4918 | 19.9804 | 19.0996 | 20.1666 | 19.1864 | 20.2562 | 18.891 | 20.017 | 21.007 | 19.4555 | 19.7641 | 20.9514 | 18.8872 | 19.7735 | 20.7932 | 19.0156 | 20.0964 | 19.316 | 19.8679 | 18.9282 | 20.1515 | -0.20121 | 20.9481 | 0.047707 | 0.01235 | -27.0496 | 3.0976 | 6.59 | -0.01 | 0.73454 | 0.35195 | -6.7462 | 0.74187 | 0.44669 | -16.7069 | 4.8087 | 0.42353 | 0.4251 | 0.43022 | 0.38237 | 0.47517 | 0.43892 | 0.42969
42838.4161 | -359 | 22.8888 | 22.8543 | 22.8416 | 22.7722 | 22.4081 | 21.7489 | 22.7177 | 21.8109 | 22.3621 | 22.3758 | 22.3729 | 22.0405 | 21.26 | 22.2309 | 21.5832 | 21.7442 | 21.8839 | 21.0735 | 21.1646 | 21.3862 | 20.4787 | 20.615 | 20.9156 | 21.8874 | 21.6542 | 21.2867 | 20.2535 | 20.3602 | 20.1954 | 22.0479 | 21.6565 | 21.1765 | 21.9936 | 21.7279 | 21.3513 | 19.9311 | 20.3976 |  | 20.5425 | 20.0747 | 20.1887 | 19.1892 |  | 16.7178 | 16.7264 | 16.4419 | 16.716 | 16.8626 | 17.3559 | 17.8497 | 15.9124 | 16.8489 | 16.0701 | 16.903 | 17.8751 | 44.5533 | 47.5148 | 43.8893 | 21.3695 |  |  | 0.70006 | -0.30037 | -32.5425 | 0.58019 | 0.16178 | -197.821 | 16.4932 | -0.28621 | 0.033759 | -0.32906 | 0.004284 | 8.8292 | 9.0588 | 1.9792 | 21.7834 | 22.013 | 22.202 | 22.2763 | 22.0957 | 21.4256 | 20.2464 | 22.1984 | 22.3688 | 22.4135 | 22.359 | 21.9959 | 21.2321 | 22.2765 | 17.2497 | 17.1198 | 16.1773 | 16.2346 | 16.3122 | 17.0752 | 16.8385 | 22.3873 | 22.1507 | 21.7101 | 22.0821 | 21.8002 | 21.3114 | 21.945 | 21.532 | 20.919 | 20.1092 | 20.2717 | 19.8045 | 19.731 | -0.057788 | 0.11244 | 20.7575 | 22.095 | 22.3989 | 20.0896 | 21.682 | 22.1344 | 21.9641 | 21.7292 | 21.2893 | 21.7937 | 21.4575 | 21.0567 | 20.2053 | 20.2583 | 20.2477 | 20.2048 | 20.1013 |  | 20.2282 | 19.9073 | 20.1197 | 19.6995 | 20.1038 | 20.3397 |  | 20.4359 |  |  | 20.2862 | 20.3914 | 20.6515 | [5 empty] | 21.9558 | 20.3499 | 21.6982 | 22.0679 | 19.5709 | 21.1903 | 21.8075 | 19.32 | 19.8867 | 21.0893 |  | 19.7565 | 20.9064 | 18.8963 | 19.7254 | 20.8212 | 19.4818 | 19.9854 | 19.1036 | 20.1779 | 19.1967 | 20.2551 | 18.8749 | 20.0012 | 20.9946 | 19.4402 | 19.7497 | 20.936 | 18.8842 | 19.7538 | 20.7867 | 19.0145 | 20.0864 | 19.3035 | 19.8607 | 18.914 | 20.1412 | -0.052443 | 20.9482 | 0.049433 | 0.013141 | -27.1051 | 3.0976 | 0.53 | -0.16 | 0.99867 | -0.65028 | -6.7686 | 0.90377 | 0.47776 | -16.7063 | 4.8239 | 0.42357 | 0.42532 | 0.43056 | 0.38288 | 0.47443 | 0.43895 | 0.42987
42838.4161 | -358 | 22.8866 | 22.8607 | 22.8378 | 22.7694 | 22.4045 | 21.7409 | 22.7192 | 21.8105 | 22.3598 | 22.376 | 22.3752 | 22.0401 | 21.2696 | 22.2412 | 21.5754 | 21.7451 | 21.8789 | 21.0701 | 21.1672 | 21.3889 | 20.4716 | 20.6239 | 20.905 | 21.8838 | 21.6496 | 21.2895 | 20.2598 | 20.3643 | 20.1934 | 22.043 | 21.6511 | 21.1754 | 21.9956 | 21.732 | 21.3464 | 19.9275 | 20.389 |  | 20.5389 | 20.0766 | 20.1934 | 19.1869 |  | 16.7114 | 16.7274 | 16.4464 | 16.7103 | 16.8453 | 17.334 | 17.8375 | 15.9068 | 16.8566 | 16.067 | 16.9017 | 17.8769 | 44.5518 | 47.5052 | 43.8803 | 21.3641 |  |  | 0.60543 | -0.25897 | -32.3598 | 0.20432 | 0.090156 | -197.8269 | 16.4236 | -0.4564 | -0.077163 | -0.049821 | -0.058733 | 8.829 | 9.0587 | 1.9791 | 21.7892 | 22.0154 | 22.2107 | 22.2769 | 22.1 | 21.4349 | 20.2483 | 22.2094 | 22.3777 | 22.4152 | 22.3629 | 21.9977 | 21.2367 | 22.2792 | 17.2404 | 17.1006 | 16.1691 | 16.2237 | 16.2939 | 17.0737 | 16.8357 | 22.3846 | 22.1505 | 21.7151 | 22.0868 | 21.8037 | 21.3166 | 21.9467 | 21.5342 | 20.9106 | 20.1074 | 20.2711 | 19.8029 | 19.733 | 0.091824 | 0.038451 | 20.7573 | 22.0922 | 22.3929 | 20.0867 | 21.6861 | 22.1359 | 21.9691 | 21.7318 | 21.2978 | 21.7923 | 21.4599 | 21.052 | 20.2105 | 20.2556 | 20.2529 | 20.2165 | 20.0933 |  | 20.232 | 19.8965 | 20.1202 | 19.686 | 20.0968 | 20.3419 |  | 20.4312 |  |  | 20.2897 | 20.3839 | 20.6522 | [5 empty] | 21.9532 | 20.3453 | 21.694 | 22.0706 | 19.5696 | 21.1854 | 21.8088 | 19.3235 | 19.8898 | 21.0844 |  | 19.7604 | 20.9101 | 18.8884 | 19.7153 | 20.8157 | 19.4807 | 19.9902 | 19.1107 | 20.1768 | 19.1863 | 20.2579 | 18.8934 | 20.0112 | 21.0066 | 19.4401 | 19.7663 | 20.9496 | 18.8946 | 19.775 | 20.7981 | 19.0203 | 20.1046 | 19.3155 | 19.8707 | 18.9293 | 20.1616 | -0.068953 | 20.9468 | 0.050705 | 0.014382 | -27.0729 | 3.0976 | 0.43 | 0.08 | 0.92873 | -0.60381 | -6.7496 | 0.53632 | 0.35664 | -16.7059 | 4.8135 | 0.42392 | 0.42564 | 0.4307 | 0.38375 | 0.47502 | 0.4389 | 0.42975
42838.4161 | -357 | 22.8942 | 22.8612 | 22.8403 | 22.7741 | 22.4048 | 21.7416 | 22.7211 | 21.8119 | 22.3591 | 22.3777 | 22.3614 | 22.0381 | 21.2612 | 22.2252 | 21.5761 | 21.7457 | 21.8777 | 21.0682 | 21.1659 | 21.3809 | 20.4727 | 20.6122 | 20.9092 | 21.8795 | 21.6507 | 21.2924 | 20.2493 | 20.3617 | 20.2064 | 22.0339 | 21.6408 | 21.1734 | 21.9807 | 21.7179 | 21.3463 | 19.9242 | 20.377 |  | 20.525 | 20.062 | 20.1744 | 19.1807 |  | 16.7079 | 16.722 | 16.4374 | 16.6936 | 16.8394 | 17.323 | 17.8484 | 15.9265 | 16.8534 | 16.0822 | 16.8911 | 17.8665 | 44.5386 | 47.4965 | 43.8684 | 21.3618 |  |  | 0.40896 | -0.26357 | -32.9847 | 0.44811 | 0.090812 | -197.846 | 16.166 | -0.53394 | -0.012361 | -0.16731 | 0.011749 | 8.8284 | 9.0582 | 1.9789 | 21.7841 | 22.0127 | 22.2119 | 22.2784 | 22.1007 | 21.4348 | 20.2503 | 22.2118 | 22.379 | 22.4172 | 22.3724 | 22.0005 | 21.2413 | 22.2883 | 17.2198 | 17.0694 | 16.1589 | 16.2069 | 16.2802 | 17.0685 | 16.832 | 22.3933 | 22.1561 | 21.7155 | 22.0895 | 21.8043 | 21.3119 | 21.9516 | 21.5404 | 20.9249 | 20.1136 | 20.2846 | 19.807 | 19.736 | 0.082781 | 0.0040252 | 20.7543 | 22.0931 | 22.3948 | 20.0944 | 21.6911 | 22.1364 | 21.9676 | 21.7266 | 21.2942 | 21.7953 | 21.4623 | 21.0559 | 20.2154 | 20.2505 | 20.2523 | 20.2189 | 20.094 |  | 20.2261 | 19.8962 | 20.1252 | 19.6872 | 20.0967 | 20.3482 |  | 20.4304 |  |  | 20.2913 | 20.3852 | 20.6389 | [5 empty] | 21.9518 | 20.3382 | 21.6841 | 22.0643 | 19.5624 | 21.1852 | 21.8041 | 19.3213 | 19.8881 | 21.0778 |  | 19.7619 | 20.9021 | 18.8905 | 19.7173 | 20.8183 | 19.475 | 19.9798 | 19.1043 | 20.1772 | 19.183 | 20.2561 | 18.8979 | 20.0171 | 21.0076 | 19.4458 | 19.7671 | 20.946 | 18.8998 | 19.7701 | 20.7985 | 19.0304 | 20.1072 | 19.3225 | 19.8747 | 18.931 | 20.1504 | 0.0080295 | 20.9484 | 0.050023 | 0.015101 | -27.0744 | 3.0975 | -13.53 | -0.13 | 0.76332 | -0.60914 | -6.8144 | 0.79426 | 0.35792 | -16.7064 | 4.7755 | 0.4237 | 0.42581 | 0.43067 | 0.38543 | 0.47571 | 0.43896 | 0.42988
42838.4162 | -356 | 22.8905 | 22.8613 | 22.8464 | 22.7705 | 22.4115 | 21.7437 | 22.7203 | 21.816 | 22.3681 | 22.3803 | 22.3658 | 22.0425 | 21.2643 | 22.2318 | 21.5807 | 21.7478 | 21.8796 | 21.0732 | 21.1745 | 21.3915 | 20.4817 | 20.6236 | 20.9132 | 21.8899 | 21.659 | 21.2933 | 20.2614 | 20.3684 | 20.2185 | 22.0393 | 21.6526 | 21.1822 | 21.9904 | 21.7332 | 21.3483 | 19.9264 | 20.3731 |  | 20.5471 | 20.0753 | 20.1883 | 19.1843 |  | 16.7063 | 16.7207 | 16.4294 | 16.6805 | 16.8333 | 17.3202 | 17.8643 | 15.9686 | 16.8504 | 16.0797 | 16.9023 | 17.8719 | 44.5271 | 47.494 | 43.8484 | 21.3652 |  |  | 0.56338 | -0.18866 | -33.2633 | 0.13795 | 0.17558 | -197.8447 | 16.1219 | -0.51948 | -0.050892 | -0.065766 | 0.024769 | 8.8285 | 9.0584 | 1.9785 | 21.7767 | 22.01 | 22.2054 | 22.2702 | 22.0956 | 21.4306 | 20.2499 | 22.205 | 22.3748 | 22.4062 | 22.3654 | 21.9957 | 21.2393 | 22.2757 | 17.2029 | 17.0477 | 16.1474 | 16.1955 | 16.2599 | 17.0662 | 16.8366 | 22.3964 | 22.158 | 21.717 | 22.0954 | 21.8124 | 21.3116 | 21.9489 | 21.5365 | 20.9198 | 20.1136 | 20.274 | 19.8089 | 19.7388 | 0.065873 | -0.12322 | 20.7622 | 22.0901 | 22.3896 | 20.0977 | 21.6884 | 22.1344 | 21.9598 | 21.7263 | 21.2958 | 21.7931 | 21.4635 | 21.0615 | 20.2132 | 20.2616 | 20.2564 | 20.2183 | 20.0988 |  | 20.2277 | 19.8979 | 20.1264 | 19.6847 | 20.0996 | 20.3513 |  | 20.4324 |  |  | 20.2795 | 20.3883 | 20.6359 | [5 empty] | 21.9497 | 20.34 | 21.6856 | 22.0611 | 19.5636 | 21.1844 | 21.8052 | 19.3152 | 19.8866 | 21.0796 |  | 19.7502 | 20.9088 | 18.8888 | 19.7171 | 20.8167 | 19.481 | 19.9821 | 19.0999 | 20.1691 | 19.181 | 20.2551 | 18.8949 | 20.0197 | 21.0084 | 19.4457 | 19.7605 | 20.9533 | 18.899 | 19.7737 | 20.7914 | 19.0315 | 20.0973 | 19.3088 | 19.8764 | 18.9284 | 20.1496 | 0.003763 | 20.9472 | 0.049101 | 0.015159 | -26.9954 | 3.0976 | 9.65 | -0.09 | 0.89593 | -0.51535 | -6.8431 | 0.44069 | 0.49769 | -16.7063 | 4.769 | 0.42362 | 0.42581 | 0.43083 | 0.38703 | 0.47753 | 0.43893 | 0.4298
42838.4162 | -355 | 22.8807 | 22.8553 | 22.8482 | 22.7692 | 22.4078 | 21.7436 | 22.7135 | 21.8102 | 22.3654 | 22.3758 | 22.3572 | 22.0422 | 21.2615 | 22.2292 | 21.5659 | 21.7378 | 21.8773 | 21.071 | 21.167 | 21.3807 | 20.4709 | 20.6153 | 20.9082 | 21.8834 | 21.6476 | 21.2832 | 20.2588 | 20.3566 | 20.219 | 22.0296 | 21.6468 | 21.1778 | 21.9884 | 21.7253 | 21.3439 | 19.923 | 20.3655 |  | 20.5444 | 20.0683 | 20.189 | 19.187 |  | 16.7135 | 16.7124 | 16.4204 | 16.6779 | 16.8548 | 17.3363 | 17.876 | 15.9892 | 16.8466 | 16.0454 | 16.9004 | 17.8746 | 44.5188 | 47.496 | 43.8324 | 21.368 |  |  | 0.4865 | -0.24188 | -33.5886 | 0.60385 | 0.26692 | -197.8657 | 16.1555 | -0.49451 | 0.12289 | 0.082143 | 0.060357 | 8.8291 | 9.0589 | 1.9789 | 21.7798 | 22.0001 | 22.1954 | 22.2618 | 22.0944 | 21.4208 | 20.2378 | 22.1848 | 22.3667 | 22.4058 | 22.3532 | 21.9891 | 21.2193 | 22.2591 | 17.1804 | 17.0427 | 16.141 | 16.1895 | 16.2423 | 17.0684 | 16.8356 | 22.3902 | 22.1517 | 21.7167 | 22.0851 | 21.8035 | 21.3203 | 21.9486 | 21.5347 | 20.9132 | 20.1186 | 20.2799 | 19.7926 | 19.731 | -0.095339 | -0.14015 | 20.7642 | 22.0893 | 22.3977 | 20.0929 | 21.6892 | 22.1341 | 21.9628 | 21.7281 | 21.2904 | 21.7962 | 21.4637 | 21.0616 | 20.2175 | 20.2701 | 20.2552 | 20.2186 | 20.08 |  | 20.2323 | 19.893 | 20.1179 | 19.6825 | 20.1014 | 20.3507 |  | 20.4282 |  |  | 20.2811 | 20.3881 | 20.6351 | [5 empty] | 21.9495 | 20.3413 | 21.6791 | 22.0617 | 19.5638 | 21.1868 | 21.8022 | 19.3218 | 19.8881 | 21.088 |  | 19.7599 | 20.9091 | 18.8888 | 19.7216 | 20.8145 | 19.4799 | 19.9967 | 19.1093 | 20.1771 | 19.1855 | 20.2562 | 18.9055 | 20.0285 | 21.013 | 19.45 | 19.7694 | 20.9591 | 18.9064 | 19.7801 | 20.7949 | 19.0464 | 20.1022 | 19.3232 | 19.8777 | 18.932 | 20.1517 | -0.21643 | 20.9471 | 0.048764 | 0.015268 | -27.0816 | 3.0975 | 0.52 | -0.07 | 0.83256 | -0.58354 | -6.8764 | 0.92199 | 0.61365 | -16.7076 | 4.7741 | 0.4243 | 0.42566 | 0.43095 | 0.38979 | 0.47813 | 0.43874 | 0.43018
42838.4162 | -354 | 22.8789 | 22.8537 | 22.8492 | 22.7704 | 22.4163 | 21.7393 | 22.7112 | 21.8081 | 22.3621 | 22.3692 | 22.3575 | 22.0364 | 21.2599 | 22.2265 | 21.5683 | 21.7427 | 21.8817 | 21.0746 | 21.1698 | 21.3891 | 20.4712 | 20.6104 | 20.9076 | 21.8892 | 21.6521 | 21.2845 | 20.2588 | 20.3559 | 20.2355 | 22.0377 | 21.647 | 21.1699 | 21.9788 | 21.7235 | 21.349 | 19.9215 | 20.3618 |  | 20.5353 | 20.069 | 20.1809 | 19.1758 |  | 16.7082 | 16.7102 | 16.4216 | 16.6785 | 16.8442 | 17.3415 | 17.8964 | 15.9964 | 16.8465 | 16.0423 | 16.8968 | 17.8637 | 44.5021 | 47.4864 | 43.8014 | 21.3557 |  |  | 0.41487 | -0.19983 | -33.7674 | 0.2628 | 0.19595 | -197.8709 | 15.9097 | -0.4242 | -0.039216 | 0.1818 | -0.13303 | 8.8292 | 9.0589 | 1.9792 | 21.7826 | 22.0107 | 22.1993 | 22.2665 | 22.1004 | 21.4305 | 20.2507 | 22.2006 | 22.3784 | 22.4135 | 22.3558 | 21.993 | 21.232 | 22.2737 | 17.1419 | 17.0542 | 16.14 | 16.1759 | 16.2281 | 17.0674 | 16.8358 | 22.3847 | 22.1559 | 21.719 | 22.0857 | 21.8051 | 21.3172 | 21.9529 | 21.5322 | 20.909 | 20.1158 | 20.2757 | 19.8045 | 19.7397 | -0.032034 | 0.049673 | 20.7607 | 22.0945 | 22.3956 | 20.0953 | 21.6907 | 22.1394 | 21.9603 | 21.728 | 21.2991 | 21.7978 | 21.4578 | 21.0656 | 20.2188 | 20.2626 | 20.2571 | 20.2181 | 20.0876 |  | 20.2274 | 19.8987 | 20.1211 | 19.6944 | 20.1028 | 20.3549 |  | 20.4326 |  |  | 20.2804 | 20.3862 | 20.6435 | [5 empty] | 21.9503 | 20.3407 | 21.6849 | 22.0677 | 19.5644 | 21.1857 | 21.8101 | 19.324 | 19.8869 | 21.0901 |  | 19.763 | 20.9125 | 18.8837 | 19.7181 | 20.8217 | 19.4803 | 19.9967 | 19.1113 | 20.1835 | 19.1841 | 20.2577 | 18.9127 | 20.0253 | 21.0164 | 19.453 | 19.7658 | 20.9587 | 18.9054 | 19.7797 | 20.7978 | 19.0509 | 20.103 | 19.3142 | 19.8779 | 18.9346 | 20.1517 | -0.10271 | 20.9474 | 0.048481 | 0.014302 | -27.0373 | 3.0975 | -0.94 | -0.04 | 0.76885 | -0.53038 | -6.8946 | 0.60824 | 0.52579 | -16.708 | 4.7377 | 0.42392 | 0.42561 | 0.43067 | 0.39395 | 0.47826 | 0.43901 | 0.42985
42838.4162 | -353 | 22.8771 | 22.8489 | 22.8396 | 22.7686 | 22.4048 | 21.7403 | 22.7091 | 21.8028 | 22.3555 | 22.374 | 22.3549 | 22.036 | 21.2483 | 22.225 | 21.5685 | 21.7402 | 21.8786 | 21.0697 | 21.1684 | 21.3818 | 20.4699 | 20.612 | 20.9064 | 21.8845 | 21.6529 | 21.2868 | 20.2597 | 20.3576 | 20.2531 | 22.0332 | 21.6454 | 21.168 | 21.9846 | 21.7269 | 21.3478 | 19.9247 | 20.361 |  | 20.5439 | 20.0678 | 20.1789 | 19.1722 |  | 16.7065 | 16.7025 | 16.4211 | 16.6696 | 16.8491 | 17.3736 | 17.9134 | 16.0246 | 16.8511 | 16.0456 | 16.901 | 17.8689 | 44.5103 | 47.4881 | 43.7847 | 21.357 |  |  | 0.29462 | -0.2478 | -34.9285 | 0.10444 | 0.14272 | -197.8328 | 15.6593 | -0.60622 | 0.10946 | 0.30138 | -0.053525 | 8.8282 | 9.0575 | 1.9792 | 21.7873 | 22.0072 | 22.2059 | 22.2692 | 22.0917 | 21.4301 | 20.238 | 22.1985 | 22.3791 | 22.4159 | 22.3531 | 21.9981 | 21.2282 | 22.2819 | 17.1203 | 17.0612 | 16.1294 | 16.1761 | 16.2253 | 17.0621 | 16.8413 | 22.3764 | 22.1554 | 21.7154 | 22.0866 | 21.8042 | 21.3127 | 21.9454 | 21.5327 | 20.9106 | 20.1073 | 20.2657 | 19.7957 | 19.7439 | -0.10261 | -0.12322 | 20.7563 | 22.0887 | 22.382 | 20.0999 | 21.6884 | 22.1324 | 21.958 | 21.7224 | 21.2903 | 21.7881 | 21.4556 | 21.0602 | 20.2243 | 20.2553 | 20.2576 | 20.2228 | 20.0774 |  | 20.2332 | 19.9028 | 20.1257 | 19.7034 | 20.1008 | 20.3496 |  | 20.4366 |  |  | 20.2835 | 20.398 | 20.6477 | [5 empty] | 21.9514 | 20.3475 | 21.6902 | 22.0739 | 19.5696 | 21.1823 | 21.8089 | 19.3238 | 19.8847 | 21.091 |  | 19.7624 | 20.9166 | 18.8767 | 19.7185 | 20.8119 | 19.4883 | 19.9972 | 19.112 | 20.1772 | 19.1832 | 20.2555 | 18.9142 | 20.0176 | 21.0226 | 19.4553 | 19.765 | 20.9584 | 18.8931 | 19.7758 | 20.794 | 19.043 | 20.1074 | 19.3187 | 19.8838 | 18.9317 | 20.1494 | -0.091584 | 20.9474 | 0.047227 | 0.013838 | -27.0021 | 3.0976 | -4.38 | -0.01 | 0.64793 | -0.59061 | -7.0121 | 0.38343 | 0.44875 | -16.7073 | 4.7005 | 0.4244 | 0.42565 | 0.43035 | 0.39573 | 0.48009 | 0.43921 | 0.42945
42838.4162 | -352 | 22.8804 | 22.8408 | 22.8388 | 22.7666 | 22.3941 | 21.741 | 22.7107 | 21.7987 | 22.3587 | 22.3695 | 22.3549 | 22.0325 | 21.249 | 22.2215 | 21.5648 | 21.7385 | 21.8741 | 21.0671 | 21.1646 | 21.3803 | 20.468 | 20.6084 | 20.9095 | 21.8809 | 21.6461 | 21.2881 | 20.2617 | 20.3638 | 20.2652 | 22.0357 | 21.6487 | 21.1682 | 21.9811 | 21.7188 | 21.3405 | 19.9212 | 20.3507 |  | 20.5422 | 20.0635 | 20.1804 | 19.1718 |  | 16.6949 | 16.696 | 16.4236 | 16.6589 | 16.8717 | 17.4027 | 17.941 | 15.9892 | 16.8439 | 16.0692 | 16.9047 | 17.8747 | 44.5075 | 47.4903 | 43.7681 | 21.3564 |  |  | 0.4497 | -0.50867 | -35.6421 | 0.3548 | 0.21106 | -197.8197 | 15.2848 | -0.37558 | -0.097596 | 0.16522 | 0.047684 | 8.829 | 9.0588 | 1.9785 | 21.7838 | 22.0103 | 22.2037 | 22.2726 | 22.0994 | 21.4278 | 20.2445 | 22.2015 | 22.3672 | 22.4099 | 22.3653 | 21.9944 | 21.2276 | 22.2779 | 17.1093 | 17.075 | 16.1232 | 16.1609 | 16.217 | 17.0603 | 16.8388 | 22.385 | 22.1583 | 21.7165 | 22.0972 | 21.8058 | 21.3185 | 21.9525 | 21.5389 | 20.9148 | 20.1174 | 20.2698 | 19.8046 | 19.7512 | 0.076293 | -0.081945 | 20.7601 | 22.0932 | 22.3933 | 20.1037 | 21.6826 | 22.13 | 21.9576 | 21.723 | 21.2847 | 21.7963 | 21.458 | 20.9973 | 20.2049 | 20.2305 | 20.2521 | 20.2164 | 20.0522 |  | 20.226 | 19.8916 | 20.1007 | 19.7166 | 20.0808 | 20.3706 |  | 20.4051 |  |  | 20.2876 | 20.3899 | 20.6473 | [5 empty] | 21.9473 | 20.3411 | 21.6903 | 22.0767 | 19.5739 | 21.1729 | 21.8299 | 19.3324 | 19.8994 | 21.0999 |  | 19.7673 | 20.9518 | 18.8867 | 19.7194 | 20.825 | 19.4966 | 19.9939 | 19.1257 | 20.1782 | 19.194 | 20.2601 | 18.9133 | 20.0095 | 21.0115 | 19.3522 | 19.7681 | 20.9856 | 18.8937 | 19.7564 | 20.8035 | 19.0345 | 20.1086 | 19.3196 | 19.8877 | 18.9288 | 20.143 | -0.21216 | 20.9469 | 0.047664 | 0.012967 | -27.0495 | 3.0975 | -12.25 | -0.01 | 0.80051 | -0.84619 | -7.0832 | 0.70671 | 0.54574 | -16.7076 | 4.6442 | 0.42486 | 0.42512 | 0.42932 | 0.39674 | 0.48048 | 0.43911 | 0.42958
42838.4162 | -351 | 22.8869 | 22.848 | 22.8441 | 22.7664 | 22.4048 | 21.7434 | 22.7157 | 21.8076 | 22.3675 | 22.3722 | 22.3564 | 22.0396 | 21.2537 | 22.2214 | 21.5629 | 21.7373 | 21.874 | 21.0676 | 21.1586 | 21.381 | 20.4661 | 20.6044 | 20.9075 | 21.882 | 21.6425 | 21.2797 | 20.2563 | 20.3565 | 20.2853 | 22.035 | 21.6515 | 21.1714 | 21.9817 | 21.7213 | 21.3492 | 19.9214 | 20.3419 |  | 20.5462 | 20.0691 | 20.191 | 19.1677 |  | 16.6909 | 16.6909 | 16.4276 | 16.6648 | 16.865 | 17.3427 | 18.0112 | 15.9577 | 16.8464 | 16.1097 | 16.9055 | 17.8606 | 44.4919 | 47.4772 | 43.7423 | 21.3424 |  |  | 0.42735 | -0.057893 | -37.0404 | 0.30354 | 0.1723 | -197.8236 | 14.9845 | -0.48991 | -0.045054 | 0.16585 | -0.01811 | 8.8291 | 9.0589 | 1.9785 | 21.781 | 22.0085 | 22.2047 | 22.27 | 22.0971 | 21.4292 | 20.2468 | 22.2022 | 22.369 | 22.4046 | 22.3606 | 21.9951 | 21.2306 | 22.2788 | 17.117 | 17.05 | 16.1139 | 16.1543 | 16.2144 | 17.0675 | 16.8391 | 22.3862 | 22.1506 | 21.7119 | 22.0938 | 21.7996 | 21.3106 | 21.9554 | 21.5316 | 20.912 | 20.1147 | 20.2698 | 19.8021 | 19.7521 | -0.087082 | -0.061213 | 20.7939 | 22.0761 | 22.418 | 20.1129 | 21.6834 | 22.1329 | 21.9528 | 21.7201 | 21.2926 | 21.7973 | 21.4622 | 21.0487 | 20.2165 | 20.2595 | 20.2643 | 20.2283 | 20.052 |  | 20.2305 | 19.8982 | 20.1281 | 19.735 | 20.1086 | 20.3598 |  | 20.4396 |  |  | 20.2904 | 20.3821 | 20.6521 | [5 empty] | 21.9479 | 20.3439 | 21.6855 | 22.0706 | 19.5709 | 21.1732 | 21.8256 | 19.3307 | 19.9027 | 21.0961 |  | 19.7649 | 20.9452 | 18.8852 | 19.7202 | 20.8182 | 19.4909 | 19.9828 | 19.1189 | 20.1747 | 19.1825 | 20.2557 | 18.9217 | 20.0191 | 21.009 | 19.362 | 19.7701 | 20.9843 | 18.9051 | 19.7608 | 20.8094 | 19.031 | 20.1159 | 19.3199 | 19.8908 | 18.9277 | 20.1464 | -0.037233 | 20.9474 | 0.048622 | 0.014426 | -27.0421 | 3.0975 | -5.11 | -0.05 | 0.7804 | -0.28547 | -7.2208 | 0.65367 | 0.49303 | -16.706 | 4.5979 | 0.42502 | 0.42585 | 0.42974 | 0.39673 | 0.48154 | 0.43923 | 0.42947
42838.4162 | -350 | 22.8872 | 22.8571 | 22.8498 | 22.7753 | 22.4111 | 21.7563 | 22.7031 | 21.8067 | 22.3787 | 22.3792 | 22.3568 | 22.0493 | 21.259 | 22.2301 | 21.5633 | 21.7446 | 21.8815 | 21.0683 | 21.1644 | 21.383 | 20.4698 | 20.6075 | 20.9057 | 21.8813 | 21.6452 | 21.2806 | 20.2581 | 20.366 | 20.3078 | 22.0312 | 21.6435 | 21.1711 | 21.987 | 21.7214 | 21.3427 | 19.9257 | 20.3476 |  | 20.5419 | 20.0666 | 20.183 | 19.155 |  | 16.6849 | 16.7057 | 16.4319 | 16.6389 | 16.8727 | 17.3584 | 18.0291 | 15.9322 | 16.8457 | 16.1618 | 16.9087 | 17.8687 | 44.505 | 47.4762 | 43.7263 | 21.3609 |  |  | 0.57455 | -0.142 | -37.8211 | 0.13072 | 0.25509 | -197.8092 | 14.6967 | -0.28621 | -0.35778 | -0.18325 | -0.10265 | 8.8287 | 9.0583 | 1.9783 | 21.7854 | 22.0126 | 22.206 | 22.2751 | 22.1006 | 21.4232 | 20.2453 | 22.2024 | 22.3752 | 22.4119 | 22.3573 | 21.9948 | 21.2278 | 22.2786 | 17.1409 | 17.0142 | 16.1137 | 16.1376 | 16.2149 | 17.0697 | 16.8306 | 22.3881 | 22.1575 | 21.7187 | 22.0977 | 21.8116 | 21.3113 | 21.9525 | 21.5353 | 20.9155 | 20.1208 | 20.2579 | 19.8002 | 19.748 | -0.081773 | -0.080614 | 20.7639 | 22.0962 | 22.3929 | 20.1035 | 21.6788 | 22.1293 | 21.9591 | 21.7188 | 21.2927 | 21.7945 | 21.4624 | 21.0575 | 20.2211 | 20.2583 | 20.2643 | 20.2307 | 20.0525 |  | 20.2318 | 19.8882 | 20.1325 | 19.7329 | 20.1037 | 20.3609 |  | 20.4362 |  |  | 20.2798 | 20.3683 | 20.6384 | [5 empty] | 21.9462 | 20.3399 | 21.6787 | 22.0625 | 19.563 | 21.1798 | 21.8038 | 19.3265 | 19.8977 | 21.1041 |  | 19.761 | 20.9186 | 18.8778 | 19.7147 | 20.8094 | 19.4822 | 19.9797 | 19.1061 | 20.1696 | 19.1664 | 20.2452 | 18.9228 | 20.0148 | 21.0127 | 19.4483 | 19.772 | 20.9522 | 18.8963 | 19.7776 | 20.7931 | 19.0262 | 20.1032 | 19.3127 | 19.8838 | 18.9245 | 20.1405 | -0.15224 | 20.9468 | 0.04904 | 0.014781 | -26.9862 | 3.0975 | 17.55 | -0.15 | 0.90491 | -0.4471 | -7.2967 | 0.42898 | 0.59992 | -16.7059 | 4.5536 | 0.42505 | 0.42628 | 0.42963 | 0.39433 | 0.48058 | 0.43972 | 0.42978
42838.4162 | -349 | 22.893 | 22.8614 | 22.8486 | 22.7714 | 22.4113 | 21.7585 | 22.7234 | 21.818 | 22.3821 | 22.3765 | 22.3658 | 22.0505 | 21.2661 | 22.2366 | 21.5679 | 21.744 | 21.8821 | 21.0718 | 21.1683 | 21.3869 | 20.4748 | 20.613 | 20.9103 | 21.8822 | 21.6471 | 21.293 | 20.273 | 20.3752 | 20.3322 | 22.0351 | 21.6551 | 21.1766 | 21.9833 | 21.7298 | 21.3543 | 19.9313 | 20.3449 |  | 20.5477 | 20.0799 | 20.198 | 19.1446 |  | 16.6929 | 16.6947 | 16.4483 | 16.6748 | 16.895 | 17.4513 | 18.0004 | 15.9587 | 16.8512 | 16.1788 | 16.9071 | 17.8697 | 44.5103 | 47.4791 | 43.6961 | 21.353 |  |  | 0.52987 | 0.068275 | -37.7206 | 0.082094 | 0.067816 | -197.8434 | 15.0226 | -0.29212 | -0.48933 | 0.15893 | -0.065503 | 8.8283 | 9.0578 | 1.9797 | 21.7911 | 22.0113 | 22.2118 | 22.2767 | 22.1035 | 21.4335 | 20.244 | 22.2044 | 22.3803 | 22.4121 | 22.3667 | 21.9967 | 21.2304 | 22.2884 | 17.1807 | 17.05 | 16.1213 | 16.1419 | 16.2097 | 17.0726 | 16.84 | 22.385 | 22.1513 | 21.7126 | 22.0886 | 21.8009 | 21.3084 | 21.9453 | 21.5355 | 20.9115 | 20.1125 | 20.2613 | 19.8 | 19.7292 | 0.090448 | 0.073448 | 20.7534 | 22.084 | 22.3936 | 20.0939 | 21.6822 | 22.1284 | 21.9521 | 21.72 | 21.2842 | 21.7948 | 21.4566 | 21.0466 | 20.2217 | 20.2705 | 20.2566 | 20.2239 | 20.0599 |  | 20.2253 | 19.8725 | 20.1207 | 19.7211 | 20.0933 | 20.3467 |  | 20.4339 |  |  | 20.2814 | 20.3705 | 20.6379 | [5 empty] | 21.9478 | 20.3378 | 21.6863 | 22.0709 | 19.5635 | 21.1856 | 21.8071 | 19.3279 | 19.896 | 21.1037 |  | 19.7616 | 20.917 | 18.8745 | 19.7119 | 20.8228 | 19.4845 | 19.9836 | 19.1121 | 20.1766 | 19.1599 | 20.2503 | 18.9303 | 20.0171 | 21.0293 | 19.4584 | 19.7763 | 20.9612 | 18.8995 | 19.7875 | 20.804 | 19.0274 | 20.1065 | 19.3177 | 19.8846 | 18.9303 | 20.1504 | -0.15039 | 20.9475 | 0.048561 | 0.014803 | -27.0055 | 3.0976 | 4.78 | -0.1 | 0.86904 | 0.31001 | -7.2868 | 0.33994 | 0.30937 | -16.71 | 4.6046 | 0.42462 | 0.42632 | 0.42961 | 0.39025 | 0.48083 | 0.4402 | 0.43003
42838.4163 | -348 | 22.8857 | 22.8631 | 22.8448 | 22.7687 | 22.4024 | 21.7533 | 22.7108 | 21.8072 | 22.371 | 22.3786 | 22.3623 | 22.0356 | 21.2624 | 22.2289 | 21.5782 | 21.7528 | 21.8764 | 21.0724 | 21.173 | 21.3904 | 20.4673 | 20.617 | 20.9129 | 21.8844 | 21.6487 | 21.2906 | 20.2711 | 20.3742 | 20.3458 | 22.0343 | 21.641 | 21.1708 | 21.9857 | 21.7196 | 21.3385 | 19.9181 | 20.3408 |  | 20.5365 | 20.0735 | 20.1906 | 19.1394 |  | 16.7143 | 16.7094 | 16.4499 | 16.6698 | 16.8913 | 17.442 | 18.0188 | 15.9802 | 16.8548 | 16.2076 | 16.9103 | 17.8626 | 44.5046 | 47.4783 | 43.6643 | 21.3414 |  |  | 0.39253 | -0.25568 | -38.3376 | 0.20498 | 0.22289 | -197.8933 | 15.5181 | -0.19355 | -0.28538 | 0.17697 | -0.010646 | 8.8292 | 9.059 | 1.9791 | 21.7853 | 22.0072 | 22.2096 | 22.2805 | 22.1053 | 21.4267 | 20.246 | 22.2093 | 22.3829 | 22.4114 | 22.3606 | 21.9992 | 21.2304 | 22.2773 | 17.219 | 17.0556 | 16.1372 | 16.1488 | 16.2107 | 17.0695 | 16.8411 | 22.3856 | 22.1497 | 21.7147 | 22.0875 | 21.807 | 21.3123 | 21.949 | 21.5362 | 20.9169 | 20.1142 | 20.2628 | 19.8036 | 19.7316 | -0.097305 | -0.10325 | 20.7635 | 22.0809 | 22.3913 | 20.1005 | 21.6837 | 22.1273 | 21.9546 | 21.7197 | 21.29 | 21.7866 | 21.4696 | 21.0506 | 20.2217 | 20.2688 | 20.257 | 20.2334 | 20.0694 |  | 20.2304 | 19.8685 | 20.1218 | 19.7163 | 20.094 | 20.345 |  | 20.4295 |  |  | 20.2815 | 20.3707 | 20.6308 | [5 empty] | 21.9525 | 20.3358 | 21.6865 | 22.0695 | 19.5654 | 21.1885 | 21.8049 | 19.3407 | 19.8994 | 21.1029 |  | 19.7619 | 20.921 | 18.8798 | 19.7255 | 20.8264 | 19.4908 | 19.9903 | 19.1128 | 20.1785 | 19.1687 | 20.2517 | 18.9242 | 20.0056 | 21.0252 | 19.4475 | 19.7755 | 20.9594 | 18.9003 | 19.7811 | 20.7935 | 19.017 | 20.1136 | 19.3141 | 19.8738 | 18.914 | 20.1354 | -0.027401 | 20.9481 | 0.048524 | 0.014215 | -27.0462 | 3.0975 | -4.17 | -0.09 | 0.748 | -0.59995 | -7.3464 | 0.53717 | 0.56086 | -16.7118 | 4.6798 | 0.42453 | 0.42647 | 0.42976 | 0.38563 | 0.4792 | 0.4399 | 0.43002
42838.4163 | -347 | 22.8835 | 22.8528 | 22.8419 | 22.766 | 22.4011 | 21.7411 | 22.7047 | 21.8042 | 22.3581 | 22.3745 | 22.3572 | 22.0286 | 21.2527 | 22.2205 | 21.574 | 21.7441 | 21.884 | 21.0702 | 21.1631 | 21.3845 | 20.4722 | 20.6097 | 20.9077 | 21.8871 | 21.6475 | 21.2874 | 20.2706 | 20.3663 | 20.3674 | 22.0349 | 21.6479 | 21.1686 | 21.9904 | 21.7214 | 21.3407 | 19.9215 | 20.3283 |  | 20.5394 | 20.0749 | 20.1845 | 19.147 |  | 16.7149 | 16.7063 | 16.4393 | 16.6673 | 16.8815 | 17.4352 | 18.0024 | 15.9972 | 16.8452 | 16.2213 | 16.9041 | 17.8769 | 44.5156 | 47.4834 | 43.6612 | 21.3537 |  |  | 0.31236 | -0.22546 | -38.3422 | 0.21812 | 0.22618 | -197.8197 | 14.5981 | -0.21524 | -0.30718 | 0.24054 | 0.046469 | 8.8288 | 9.059 | 1.9791 | 21.7829 | 22.0067 | 22.2022 | 22.2769 | 22.1049 | 21.4326 | 20.2446 | 22.2019 | 22.3812 | 22.4077 | 22.3582 | 22.0037 | 21.2307 | 22.28 | 17.2514 | 17.0789 | 16.1538 | 16.1603 | 16.2329 | 17.0734 | 16.8386 | 22.3824 | 22.147 | 21.7186 | 22.0851 | 21.8046 | 21.3096 | 21.9466 | 21.5293 | 20.9154 | 20.1126 | 20.2601 | 19.8002 | 19.7354 | -0.10006 | -0.016707 | 20.7511 | 22.0709 | 22.3901 | 20.0957 | 21.6791 | 22.1344 | 21.9495 | 21.7187 | 21.2925 | 21.7902 | 21.4562 | 21.0481 | 20.2242 | 20.268 | 20.2511 | 20.2248 | 20.0877 |  | 20.2235 | 19.8695 | 20.1173 | 19.708 | 20.0954 | 20.3469 |  | 20.4309 |  |  | 20.2823 | 20.3602 | 20.6185 | [5 empty] | 21.9511 | 20.3316 | 21.6825 | 22.077 | 19.558 | 21.1831 | 21.8073 | 19.3351 | 19.9038 | 21.1066 |  | 19.7574 | 20.9265 | 18.8787 | 19.7215 | 20.8245 | 19.4895 | 19.9912 | 19.1065 | 20.1736 | 19.1654 | 20.2523 | 18.9206 | 20.0069 | 21.0216 | 19.4458 | 19.7716 | 20.9533 | 18.8981 | 19.7787 | 20.7969 | 19.0118 | 20.1096 | 19.3154 | 19.8799 | 18.9186 | 20.1296 | -0.11607 | 20.9474 | 0.048512 | 0.013707 | -26.971 | 3.0975 | -8.2 | 0 | 0.66729 | -0.56337 | -7.3468 | 0.55412 | 0.56498 | -16.7085 | 4.5389 | 0.42379 | 0.42629 | 0.43004 | 0.38249 | 0.47706 | 0.4398 | 0.42986
42838.4163 | -346 | 22.8857 | 22.8528 | 22.8414 | 22.7696 | 22.4028 | 21.7413 | 22.7165 | 21.8069 | 22.3603 | 22.374 | 22.3556 | 22.0312 | 21.2552 | 22.2218 | 21.5678 | 21.7397 | 21.8797 | 21.0733 | 21.1703 | 21.386 | 20.4711 | 20.6095 | 20.9007 | 21.8861 | 21.6489 | 21.2838 | 20.2685 | 20.3715 | 20.3728 | 22.0405 | 21.6535 | 21.1741 | 21.9901 | 21.7297 | 21.3482 | 19.9231 | 20.3233 |  | 20.539 | 20.072 | 20.187 | 19.1536 |  | 16.7029 | 16.7064 | 16.4441 | 16.6749 | 16.8877 | 17.4263 | 17.9725 | 15.9945 | 16.8457 | 16.2469 | 16.9017 | 17.8717 | 44.5079 | 47.4878 | 43.6468 | 21.3635 |  |  | 0.4773 | -0.15186 | -37.8408 | -0.19783 | 0.12367 | -197.8696 | 15.1126 | -0.31775 | -0.10402 | 0.078157 | 0.051677 | 8.8287 | 9.0585 | 1.979 | 21.7856 | 22.0109 | 22.214 | 22.2767 | 22.1 | 21.4305 | 20.2501 | 22.202 | 22.3764 | 22.4102 | 22.3572 | 21.9954 | 21.2306 | 22.2816 | 17.2769 | 17.0666 | 16.1634 | 16.1762 | 16.2316 | 17.0653 | 16.8335 | 22.3864 | 22.1519 | 21.7077 | 22.089 | 21.8066 | 21.3104 | 21.9507 | 21.529 | 20.9156 | 20.1044 | 20.2668 | 19.7967 | 19.75 | -0.027512 | 0.047771 | 20.7551 | 22.0825 | 22.3888 | 20.0961 | 21.6746 | 22.1282 | 21.9502 | 21.7228 | 21.2848 | 21.7896 | 21.4597 | 21.0599 | 20.2234 | 20.2626 | 20.2616 | 20.2251 | 20.0986 |  | 20.2353 | 19.872 | 20.1216 | 19.7087 | 20.1014 | 20.3597 |  | 20.4375 |  |  | 20.2605 | 20.3578 | 20.6248 | [5 empty] | 21.9445 | 20.3242 | 21.6788 | 22.0677 | 19.558 | 21.1777 | 21.8065 | 19.3395 | 19.8997 | 21.0968 |  | 19.7575 | 20.9202 | 18.8755 | 19.7113 | 20.8048 | 19.4754 | 19.9829 | 19.0827 | 20.1734 | 19.1567 | 20.2489 | 18.9294 | 20.0151 | 21.0295 | 19.4591 | 19.7902 | 20.9684 | 18.9069 | 19.7939 | 20.8157 | 19.023 | 20.1152 | 19.3223 | 19.8954 | 18.9317 | 20.1361 | -0.070808 | 20.9483 | 0.048167 | 0.012321 | -27.2066 | 3.0975 | 7.54 | -0.07 | 0.82486 | -0.46236 | -7.2986 | -0.52773 | 0.41776 | -16.7104 | 4.6181 | 0.42388 | 0.42637 | 0.43023 | 0.37871 | 0.47539 | 0.43967 | 0.42918
42838.4163 | -345 | 22.8918 | 22.8583 | 22.8448 | 22.7724 | 22.4032 | 21.7465 | 22.7161 | 21.8046 | 22.3693 | 22.3782 | 22.3573 | 22.0449 | 21.2616 | 22.2267 | 21.5634 | 21.7431 | 21.8866 | 21.0648 | 21.1565 | 21.3838 | 20.4728 | 20.6176 | 20.9104 | 21.8937 | 21.6509 | 21.2839 | 20.2718 | 20.3738 | 20.3949 | 22.0453 | 21.6559 | 21.1817 | 21.9882 | 21.7274 | 21.3488 | 19.9267 | 20.3282 |  | 20.5471 | 20.076 | 20.1886 | 19.1605 |  | 16.7054 | 16.7063 | 16.4544 | 16.6862 | 16.8845 | 17.4018 | 17.9467 | 15.9768 | 16.8522 | 16.2676 | 16.912 | 17.865 | 44.4945 | 47.4819 | 43.6261 | 21.3472 |  |  | 0.60149 | -0.073005 | -38.3678 | 0.26477 | 0.26561 | -197.8532 | 14.3918 | -0.51094 | -0.15267 | -0.010379 | 0.004284 | 8.8287 | 9.0583 | 1.9785 | 21.7872 | 22.0085 | 22.2012 | 22.2733 | 22.1009 | 21.4323 | 20.2506 | 22.2078 | 22.3765 | 22.4054 | 22.3597 | 21.9918 | 21.2381 | 22.2802 | 17.2861 | 17.0775 | 16.1609 | 16.2015 | 16.2479 | 17.0611 | 16.8388 | 22.3878 | 22.1545 | 21.7077 | 22.0877 | 21.8021 | 21.3126 | 21.9484 | 21.5368 | 20.9114 | 20.1084 | 20.2627 | 19.8 | 19.7556 | -0.045599 | 0.011443 | 20.7509 | 22.0819 | 22.3887 | 20.1022 | 21.6893 | 22.1332 | 21.9563 | 21.7211 | 21.2965 | 21.7953 | 21.465 | 21.0623 | 20.2311 | 20.2655 | 20.2648 | 20.2312 | 20.0881 |  | 20.2274 | 19.8627 | 20.1147 | 19.6946 | 20.0943 | 20.3523 |  | 20.4327 |  |  | 20.2586 | 20.3744 | 20.6321 | [5 empty] | 21.9541 | 20.3207 | 21.689 | 22.0592 | 19.5685 | 21.1753 | 21.81 | 19.3469 | 19.9084 | 21.112 |  | 19.7597 | 20.9187 | 18.8764 | 19.7266 | 20.8113 | 19.481 | 19.9884 | 19.0861 | 20.1693 | 19.1563 | 20.2454 | 18.9268 | 20.0212 | 21.0307 | 19.4483 | 19.7869 | 20.9596 | 18.8991 | 19.788 | 20.8012 | 19.0046 | 20.1034 | 19.3126 | 19.8845 | 18.92 | 20.1331 | -0.13814 | 20.9481 | 0.046908 | 0.011863 | -27.2408 | 3.0975 | -14.76 | -0.1 | 0.92602 | -0.32058 | -7.3492 | 0.61051 | 0.61221 | -16.709 | 4.5065 | 0.42391 | 0.42639 | 0.43038 | 0.3772 | 0.47629 | 0.4396 | 0.42916
42838.4163 | -344 | 22.8905 | 22.8477 | 22.8381 | 22.7669 | 22.3977 | 21.7496 | 22.7079 | 21.8068 | 22.3662 | 22.3711 | 22.3551 | 22.038 | 21.2602 | 22.2253 | 21.5769 | 21.7495 | 21.8895 | 21.0715 | 21.1738 | 21.3936 | 20.4729 | 20.6109 | 20.915 | 21.893 | 21.6467 | 21.2883 | 20.282 | 20.3773 | 20.4145 | 22.0366 | 21.6483 | 21.1782 | 21.976 | 21.7281 | 21.3523 | 19.9272 | 20.3162 |  | 20.5386 | 20.0703 | 20.1807 | 19.1303 |  | 16.7131 | 16.7155 | 16.4729 | 16.6997 | 16.8798 | 17.3739 | 17.9336 | 15.9733 | 16.848 | 16.2586 | 16.9102 | 17.8642 | 44.4804 | 47.474 | 43.6028 | 21.3523 |  |  | 0.67772 | -0.20574 | -39.0361 | 0.43103 | 0.24721 | -197.8374 | 14.9063 | -0.5714 | -0.24569 | -0.083599 | 0.078585 | 8.8292 | 9.059 | 1.9795 | 21.7796 | 22.0077 | 22.2002 | 22.273 | 22.1011 | 21.4249 | 20.2481 | 22.2039 | 22.3714 | 22.4136 | 22.3568 | 21.9852 | 21.2319 | 22.2722 | 17.3053 | 17.0956 | 16.1768 | 16.2191 | 16.2696 | 17.0653 | 16.8478 | 22.3839 | 22.1584 | 21.7141 | 22.0901 | 21.8053 | 21.3123 | 21.9522 | 21.5353 | 20.9161 | 20.1158 | 20.2654 | 19.8025 | 19.7673 | 0.02498 | 0.11738 | 20.7401 | 22.0865 | 22.3949 | 20.0905 | 21.6828 | 22.1326 | 21.957 | 21.7169 | 21.2912 | 21.7896 | 21.4658 | 21.0453 | 20.2279 | 20.2732 | 20.2485 | 20.2233 | 20.1066 |  | 20.2303 | 19.852 | 20.1161 | 19.686 | 20.0987 | 20.3493 |  | 20.432 |  |  | 20.2759 | 20.3882 | 20.6415 | [5 empty] | 21.9568 | 20.3374 | 21.6919 | 22.0794 | 19.5695 | 21.2004 | 21.8155 | 19.3488 | 19.9001 | 21.1058 |  | 19.7532 | 20.9208 | 18.8825 | 19.7254 | 20.8161 | 19.4708 | 19.987 | 19.0868 | 20.17 | 19.1542 | 20.2518 | 18.9318 | 20.0227 | 21.0277 | 19.4524 | 19.7838 | 20.9629 | 18.9093 | 19.7837 | 20.7975 | 19.0089 | 20.1096 | 19.3203 | 19.8846 | 18.9191 | 20.1253 | -0.11922 | 20.947 | 0.047522 | 0.011994 | -27.0452 | 3.0975 | -13 | -0.15 | 0.98298 | -0.53818 | -7.4131 | 0.77896 | 0.59059 | -16.7075 | 4.5861 | 0.42349 | 0.42674 | 0.43077 | 0.37556 | 0.47557 | 0.44046 | 0.42908
42838.4163 | -343 | 22.8951 | 22.8563 | 22.8456 | 22.7775 | 22.4116 | 21.7448 | 22.7102 | 21.8105 | 22.3658 | 22.3829 | 22.3605 | 22.034 | 21.2591 | 22.2289 | 21.5712 | 21.743 | 21.88 | 21.0729 | 21.1683 | 21.3919 | 20.471 | 20.6171 | 20.9053 | 21.8891 | 21.6488 | 21.2908 | 20.2879 | 20.3777 | 20.4213 | 22.0361 | 21.6483 | 21.1742 | 21.978 | 21.724 | 21.3446 | 19.9203 | 20.3015 |  | 20.5311 | 20.064 | 20.1874 | 19.1081 |  | 16.7152 | 16.7245 | 16.4753 | 16.7008 | 16.8727 | 17.3593 | 17.902 | 15.9678 | 16.8454 | 16.2442 | 16.9097 | 17.8737 | 44.4791 | 47.4841 | 43.5879 | 21.3562 |  |  | 0.55155 | 0.015707 | -39.5151 | 0.30617 | 0.11776 | -197.8552 | 14.2308 | -0.66273 | -0.24705 | -0.14444 | -0.05231 | 8.829 | 9.0586 | 1.9792 | 21.7744 | 22.0045 | 22.2036 | 22.2667 | 22.1014 | 21.4268 | 20.2436 | 22.205 | 22.3686 | 22.4132 | 22.3569 | 21.982 | 21.2284 | 22.2771 | 17.3103 | 17.1055 | 16.1687 | 16.2186 | 16.2869 | 17.0661 | 16.8442 | 22.3874 | 22.155 | 21.7164 | 22.0887 | 21.8009 | 21.31 | 21.948 | 21.537 | 20.908 | 20.1124 | 20.2683 | 19.8083 | 19.7772 | -0.065652 | 0.13374 | 20.7534 | 22.0819 | 22.3968 | 20.1042 | 21.6845 | 22.1306 | 21.953 | 21.7309 | 21.2967 | 21.7933 | 21.4608 | 21.0549 | 20.2451 | 20.275 | 20.253 | 20.2267 | 20.1138 |  | 20.2334 | 19.8474 | 20.1174 | 19.6737 | 20.0947 | 20.3455 |  | 20.4356 |  |  | 20.2693 | 20.3865 | 20.6431 | [5 empty] | 21.9508 | 20.3397 | 21.691 | 22.0722 | 19.5628 | 21.1899 | 21.8179 | 19.3378 | 19.9001 | 21.1043 |  | 19.7528 | 20.9164 | 18.8805 | 19.7198 | 20.8108 | 19.4767 | 19.9872 | 19.0781 | 20.1738 | 19.1444 | 20.2455 | 18.9348 | 20.0212 | 21.0346 | 19.4544 | 19.7878 | 20.9602 | 18.9004 | 19.7914 | 20.8008 | 18.9996 | 20.1115 | 19.3164 | 19.8903 | 18.926 | 20.1229 | -0.16393 | 20.9461 | 0.048297 | 0.013105 | -27.015 | 3.0975 | 11.07 | -0.07 | 0.88678 | 0.1487 | -7.4585 | 0.65653 | 0.4076 | -16.7079 | 4.4809 | 0.4234 | 0.42691 | 0.43097 | 0.37509 | 0.47605 | 0.44085 | 0.42869
42838.4163 | -342 | 22.8934 | 22.8579 | 22.8527 | 22.7774 | 22.4187 | 21.7512 | 22.7135 | 21.8213 | 22.3625 | 22.3805 | 22.3553 | 22.0438 | 21.2571 | 22.23 | 21.5689 | 21.7337 | 21.8748 | 21.0656 | 21.1675 | 21.382 | 20.4736 | 20.6123 | 20.9036 | 21.8865 | 21.6524 | 21.2908 | 20.2909 | 20.3699 | 20.4264 | 22.0482 | 21.6626 | 21.1864 | 21.9954 | 21.7311 | 21.3554 | 19.9264 | 20.3161 |  | 20.5458 | 20.072 | 20.2017 | 19.1085 |  | 16.7064 | 16.7305 | 16.4777 | 16.6951 | 16.8602 | 17.3384 | 17.8674 | 15.9548 | 16.8456 | 16.1693 | 16.8931 | 17.8662 | 44.4679 | 47.4856 | 43.5698 | 21.3538 |  |  | 0.26176 | 0.094559 | -39.7353 | 0.18723 | 0.28466 | -197.8427 | 14.4667 | -0.62922 | -0.075801 | -0.46439 | 0.02772 | 8.8288 | 9.0584 | 1.9791 | 21.78 | 22.0046 | 22.2017 | 22.2648 | 22.1028 | 21.426 | 20.2443 | 22.1994 | 22.3712 | 22.413 | 22.3649 | 21.9916 | 21.2298 | 22.2756 | 17.3434 | 17.1115 | 16.2207 | 16.2087 | 16.2933 | 17.0689 | 16.8491 | 22.3888 | 22.1581 | 21.7142 | 22.0914 | 21.8044 | 21.3182 | 21.9546 | 21.5339 | 20.9134 | 20.1084 | 20.2704 | 19.8144 | 19.7822 | 0.080028 | 0.22085 | 20.7501 | 22.0844 | 22.3919 | 20.0978 | 21.6802 | 22.1302 | 21.9614 | 21.7225 | 21.2853 | 21.7892 | 21.4637 | 21.0537 | 20.2328 | 20.273 | 20.262 | 20.2342 | 20.1249 |  | 20.2213 | 19.8376 | 20.1216 | 19.6793 | 20.0947 | 20.3505 |  | 20.4314 |  |  | 20.2693 | 20.3837 | 20.6316 | [5 empty] | 21.9518 | 20.3346 | 21.6882 | 22.0649 | 19.5607 | 21.1864 | 21.8152 | 19.3434 | 19.9016 | 21.1089 |  | 19.7526 | 20.9226 | 18.8729 | 19.7254 | 20.8049 | 19.489 | 19.9942 | 19.0838 | 20.1783 | 19.1509 | 20.2469 | 18.932 | 20.022 | 21.0314 | 19.4525 | 19.7862 | 20.956 | 18.9079 | 19.8024 | 20.8024 | 19.0127 | 20.1103 | 19.3197 | 19.8906 | 18.9258 | 20.1327 | -0.20789 | 20.9473 | 0.049292 | 0.01399 | -27.1869 | 3.0975 | -6.7 | -0.09 | 0.61092 | 0.36486 | -7.4794 | 0.51342 | 0.63372 | -16.7067 | 4.5177 | 0.42268 | 0.42732 | 0.43082 | 0.37175 | 0.47085 | 0.44104 | 0.42842
42838.4163 | -341 | 22.8859 | 22.8525 | 22.8432 | 22.7632 | 22.4038 | 21.7422 | 22.7059 | 21.8094 | 22.3628 | 22.3732 | 22.3538 | 22.0297 | 21.2508 | 22.2219 | 21.5661 | 21.7396 | 21.8723 | 21.0686 | 21.1638 | 21.3821 | 20.4659 | 20.6118 | 20.9036 | 21.8807 | 21.6477 | 21.2838 | 20.2874 | 20.3713 | 20.4222 | 22.0368 | 21.65 | 21.1719 | 21.9795 | 21.7261 | 21.3347 | 19.9181 | 20.3006 |  | 20.5378 | 20.0594 | 20.1883 | 19.0943 |  | 16.7088 | 16.7485 | 16.4829 | 16.7152 | 16.8611 | 17.346 | 17.9003 | 15.9683 | 16.8471 | 16.1073 | 16.9043 | 17.8696 | 44.4576 | 47.4847 | 43.5657 | 21.3575 |  |  | 0.43984 | -0.1604 | -39.705 | 0.18066 | 0.2794 | -197.8637 | 13.9975 | -0.5438 | -0.0001012 | -0.37669 | -0.0094304 | 8.8295 | 9.0593 | 1.9789 | 21.7913 | 22.0094 | 22.204 | 22.2692 | 22.0981 | 21.4299 | 20.2452 | 22.2015 | 22.3703 | 22.4147 | 22.3642 | 21.9895 | 21.2285 | 22.2799 | 17.374 | 17.1733 | 16.2714 | 16.1996 | 16.2959 | 17.0739 | 16.86 | 22.3844 | 22.1536 | 21.7193 | 22.0878 | 21.8077 | 21.3049 | 21.9485 | 21.5316 | 20.9098 | 20.1196 | 20.2659 | 19.8168 | 19.7825 | 0.017903 | 0.17007 | 20.7354 | 22.0785 | 22.3935 | 20.085 | 21.6723 | 22.1204 | 21.953 | 21.7201 | 21.2792 | 21.7874 | 21.4483 | 21.0421 | 20.2228 | 20.2676 | 20.2477 | 20.229 | 20.1325 |  | 20.2302 | 19.8318 | 20.1154 | 19.6822 | 20.0968 | 20.347 |  | 20.4325 |  |  | 20.2593 | 20.3777 | 20.6255 | [5 empty] | 21.952 | 20.3289 | 21.6837 | 22.0602 | 19.5558 | 21.1791 | 21.8058 | 19.3346 | 19.8977 | 21.1006 |  | 19.7444 | 20.9144 | 18.8602 | 19.715 | 20.8022 | 19.4748 | 19.9896 | 19.0764 | 20.1667 | 19.1414 | 20.2312 | 18.9315 | 20.0163 | 21.0281 | 19.448 | 19.7867 | 20.962 | 18.9131 | 19.797 | 20.7974 | 19.0095 | 20.1146 | 19.3165 | 19.8871 | 18.9184 | 20.1265 | -0.0097785 | 20.9466 | 0.048843 | 0.013664 | -27.101 | 3.0975 | 2.08 | -0.09 | 0.7919 | -0.47522 | -7.4767 | 0.50434 | 0.62785 | -16.7078 | 4.4439 | 0.42277 | 0.42728 | 0.43081 | 0.36893 | 0.46648 | 0.44115 | 0.42879
42838.4163 | -340 | 22.8963 | 22.8553 | 22.8386 | 22.7687 | 22.4018 | 21.747 | 22.71 | 21.81 | 22.3636 | 22.3723 | 22.3554 | 22.0294 | 21.2543 | 22.2183 | 21.5674 | 21.7368 | 21.8747 | 21.0682 | 21.1651 | 21.3858 | 20.4722 | 20.6051 | 20.9066 | 21.8813 | 21.6479 | 21.2806 | 20.2869 | 20.3748 | 20.4312 | 22.0469 | 21.6523 | 21.1745 | 21.9859 | 21.7342 | 21.3477 | 19.9281 | 20.3079 |  | 20.5387 | 20.0616 | 20.197 | 19.1052 |  | 16.701 | 16.7436 | 16.4793 | 16.7089 | 16.853 | 17.3391 | 17.9149 | 15.957 | 16.8534 | 16.0463 | 16.9019 | 17.8603 | 44.4481 | 47.4826 | 43.5625 | 21.3488 |  |  | 0.45035 | -0.37265 | -39.7077 | 0.16161 | 0.18741 | -197.8092 | 14.3937 | -0.46297 | -0.016837 | -0.20172 | 0.014006 | 8.829 | 9.059 | 1.9785 | 21.7898 | 22.0149 | 22.2119 | 22.2776 | 22.0975 | 21.4323 | 20.2447 | 22.205 | 22.3754 | 22.4164 | 22.3631 | 21.9986 | 21.2324 | 22.2796 | 17.4019 | 17.1999 | 16.3225 | 16.2224 | 16.2828 | 17.065 | 16.8455 | 22.3828 | 22.1564 | 21.7063 | 22.084 | 21.8018 | 21.3084 | 21.9444 | 21.5286 | 20.9087 | 20.1096 | 20.2688 | 19.8064 | 19.7829 | -0.23591 | 0.14192 | 20.7365 | 22.0789 | 22.394 | 20.0954 | 21.686 | 22.1329 | 21.9689 | 21.7174 | 21.2933 | 21.7977 | 21.4574 | 21.0545 | 20.2385 | 20.2761 | 20.2557 | 20.247 | 20.1265 |  | 20.2282 | 19.8136 | 20.1212 | 19.6826 | 20.0985 | 20.3415 |  | 20.4281 |  |  | 20.2617 | 20.3779 | 20.6248 | [5 empty] | 21.9581 | 20.3389 | 21.6809 | 22.0679 | 19.5574 | 21.1863 | 21.8114 | 19.3367 | 19.8999 | 21.1025 |  | 19.7393 | 20.9178 | 18.8758 | 19.7173 | 20.8026 | 19.4743 | 19.9902 | 19.0793 | 20.1674 | 19.1407 | 20.2294 | 18.9296 | 20.018 | 21.0285 | 19.445 | 19.777 | 20.9571 | 18.9063 | 19.7944 | 20.7941 | 19.0075 | 20.1122 | 19.3072 | 19.8934 | 18.9208 | 20.1174 | -0.019425 | 20.9495 | 0.048843 | 0.01333 | -27.0188 | 3.0976 | 3.22 | 0.02 | 0.80132 | -0.72433 | -7.4769 | 0.477 | 0.51419 | -16.7053 | 4.5063 | 0.42287 | 0.42797 | 0.43086 | 0.36478 | 0.45912 | 0.44119 | 0.42844
42838.4164 | -339 | 22.8907 | 22.8504 | 22.8364 | 22.7721 | 22.4035 | 21.7491 | 22.7156 | 21.8054 | 22.366 | 22.379 | 22.3592 | 22.0405 | 21.2521 | 22.2215 | 21.5666 | 21.7379 | 21.8735 | 21.0677 | 21.166 | 21.3813 | 20.4718 | 20.6057 | 20.9095 | 21.8888 | 21.6481 | 21.2818 | 20.285 | 20.3783 | 20.4368 | 22.0489 | 21.6576 | 21.1771 | 21.9898 | 21.7328 | 21.3539 | 19.9245 | 20.3193 |  | 20.5473 | 20.0693 | 20.1964 | 19.0959 |  | 16.696 | 16.7313 | 16.4778 | 16.6946 | 16.8394 | 17.3116 | 17.9165 | 15.9549 | 16.8488 | 16.0411 | 16.9001 | 17.8699 | 44.4447 | 47.4822 | 43.5602 | 21.3518 |  |  | 0.50029 | -0.40682 | -39.7984 | 0.050554 | 0.082272 | -197.7987 | 14.1026 | -0.44917 | -0.28033 | -0.27515 | -0.1221 | 8.8287 | 9.0585 | 1.9792 | 21.7927 | 22.0188 | 22.207 | 22.2759 | 22.0996 | 21.4262 | 20.2412 | 22.2112 | 22.3835 | 22.4108 | 22.3573 | 21.9986 | 21.2348 | 22.2683 | 17.4122 | 17.1963 | 16.3672 | 16.2543 | 16.2758 | 17.0609 | 16.8491 | 22.3846 | 22.1529 | 21.7082 | 22.0837 | 21.7974 | 21.3152 | 21.9419 | 21.5325 | 20.905 | 20.1135 | 20.267 | 19.8103 | 19.7738 | -0.080594 | 0.064128 | 20.7494 | 22.0945 | 22.3999 | 20.0976 | 21.6925 | 22.1359 | 21.9632 | 21.7275 | 21.3003 | 21.8001 | 21.4651 | 21.0675 | 20.2421 | 20.2885 | 20.266 | 20.2446 | 20.1324 |  | 20.2311 | 19.81 | 20.1181 | 19.6815 | 20.0932 | 20.3373 |  | 20.43 |  |  | 20.2636 | 20.3817 | 20.6396 | [5 empty] | 21.9595 | 20.342 | 21.6899 | 22.0778 | 19.5612 | 21.188 | 21.8121 | 19.3428 | 19.906 | 21.1104 |  | 19.7419 | 20.9221 | 18.8792 | 19.725 | 20.8009 | 19.4762 | 19.996 | 19.083 | 20.1694 | 19.1427 | 20.2314 | 18.9369 | 20.0308 | 21.0401 | 19.4534 | 19.7888 | 20.9625 | 18.9111 | 19.8003 | 20.805 | 19.0102 | 20.1157 | 19.313 | 19.9012 | 18.9267 | 20.1183 | -0.11793 | 20.9477 | 0.048585 | 0.01391 | -27.0132 | 3.0975 | 0.06 | -0.05 | 0.84459 | -0.7568 | -7.4853 | 0.26678 | 0.34067 | -16.7041 | 4.4603 | 0.4228 | 0.42797 | 0.43071 | 0.36316 | 0.45458 | 0.44132 | 0.42883
42838.4164 | -338 | 22.8772 | 22.8555 | 22.838 | 22.7651 | 22.3982 | 21.7504 | 22.7081 | 21.8073 | 22.369 | 22.3766 | 22.3626 | 22.0411 | 21.255 | 22.2171 | 21.5672 | 21.7461 | 21.8793 | 21.0734 | 21.1671 | 21.3836 | 20.4668 | 20.6144 | 20.9085 | 21.8845 | 21.6516 | 21.2822 | 20.2884 | 20.3778 | 20.441 | 22.0404 | 21.6498 | 21.1778 | 21.9874 | 21.7259 | 21.3506 | 19.9262 | 20.332 |  | 20.5448 | 20.0653 | 20.195 | 19.0905 |  | 16.6957 | 16.7241 | 16.4796 | 16.6885 | 16.8307 | 17.2968 | 17.8989 | 15.9589 | 16.8528 | 16.0654 | 16.9066 | 17.8662 | 44.4645 | 47.4848 | 43.5473 | 21.3511 |  |  | 0.6856 | -0.096005 | -40.307 | 0.32129 | 0.19858 | -197.821 | 14.0317 | -0.44786 | 0.0055422 | -0.017932 | -0.020367 | 8.8287 | 9.0587 | 1.9793 | 21.7844 | 22.0139 | 22.2063 | 22.2789 | 22.0974 | 21.4235 | 20.2423 | 22.2025 | 22.3766 | 22.4048 | 22.3624 | 22.0025 | 21.2318 | 22.2732 | 17.4127 | 17.193 | 16.4133 | 16.2796 | 16.2761 | 17.0752 | 16.8627 | 22.3863 | 22.1513 | 21.7142 | 22.0867 | 21.8017 | 21.3105 | 21.947 | 21.5366 | 20.9134 | 20.112 | 20.2771 | 19.8174 | 19.7795 | -0.040291 | 0.093609 | 20.7363 | 22.0848 | 22.3872 | 20.0826 | 21.6849 | 22.1288 | 21.956 | 21.7266 | 21.2884 | 21.7969 | 21.4623 | 21.06 | 20.2427 | 20.2736 | 20.2456 | 20.236 | 20.1379 |  | 20.2233 | 19.8149 | 20.1255 | 19.6895 | 20.1031 | 20.3403 |  | 20.435 |  |  | 20.2704 | 20.3793 | 20.6433 | [5 empty] | 21.954 | 20.3434 | 21.6889 | 22.0667 | 19.5655 | 21.1868 | 21.8118 | 19.3511 | 19.9087 | 21.1131 |  | 19.7459 | 20.9209 | 18.8824 | 19.7288 | 20.8057 | 19.4763 | 19.995 | 19.0795 | 20.1755 | 19.1478 | 20.2407 | 18.9275 | 20.0245 | 21.0325 | 19.4514 | 19.7886 | 20.9589 | 18.9047 | 19.8024 | 20.7994 | 19.0015 | 20.1058 | 19.3074 | 19.8929 | 18.9216 | 20.1144 | -0.21958 | 20.9456 | 0.048598 | 0.013794 | -26.9517 | 3.0975 | 12.18 | -0.04 | 0.98872 | -0.36764 | -7.5329 | 0.67254 | 0.52926 | -16.7046 | 4.4489 | 0.42239 | 0.42808 | 0.43082 | 0.36478 | 0.45104 | 0.44153 | 0.42862
42838.4164 | -337 | 22.8838 | 22.8541 | 22.8414 | 22.7605 | 22.4028 | 21.7469 | 22.7044 | 21.8073 | 22.3654 | 22.3687 | 22.3578 | 22.0364 | 21.2583 | 22.2171 | 21.5668 | 21.7427 | 21.8789 | 21.0708 | 21.1618 | 21.3873 | 20.4661 | 20.6113 | 20.9074 | 21.8812 | 21.6488 | 21.2829 | 20.2883 | 20.3786 | 20.4379 | 22.0341 | 21.6486 | 21.172 | 21.987 | 21.7194 | 21.3456 | 19.9219 | 20.3252 |  | 20.5399 | 20.0632 | 20.1893 | 19.078 |  | 16.6884 | 16.7128 | 16.4702 | 16.6753 | 16.8154 | 17.2785 | 17.8549 | 15.9273 | 16.8434 | 16.071 | 16.8977 | 17.8644 | 44.4714 | 47.4815 | 43.529 | 21.3494 |  |  | 0.50161 | -0.35951 | -40.7091 | 0.48228 | 0.038244 | -197.8716 | 13.6755 | -0.67259 | -0.086698 | -0.13962 | 0.025984 | 8.8289 | 9.0586 | 1.979 | 21.7926 | 22.0114 | 22.2087 | 22.2712 | 22.0977 | 21.4229 | 20.2436 | 22.2052 | 22.3779 | 22.4075 | 22.3622 | 21.9956 | 21.2311 | 22.2771 | 17.3988 | 17.1928 | 16.4268 | 16.2826 | 16.272 | 17.0655 | 16.8575 | 22.3889 | 22.1542 | 21.7163 | 22.0891 | 21.8067 | 21.3121 | 21.9493 | 21.5395 | 20.9171 | 20.1164 | 20.2854 | 19.8189 | 19.7833 | 0.063907 | 0.16436 | 20.7365 | 22.0817 | 22.3816 | 20.0769 | 21.679 | 22.1161 | 21.9508 | 21.7155 | 21.2882 | 21.7929 | 21.4568 | 21.0487 | 20.2275 | 20.274 | 20.2457 | 20.23 | 20.1329 |  | 20.225 | 19.8067 | 20.1228 | 19.6819 | 20.1013 | 20.344 |  | 20.4289 |  |  | 20.271 | 20.3788 | 20.6273 | [5 empty] | 21.9494 | 20.3463 | 21.6867 | 22.065 | 19.5601 | 21.1915 | 21.815 | 19.3463 | 19.9065 | 21.11 |  | 19.7425 | 20.9179 | 18.8867 | 19.73 | 20.8043 | 19.4789 | 19.9907 | 19.0768 | 20.1722 | 19.1454 | 20.2411 | 18.9276 | 20.0223 | 21.0322 | 19.452 | 19.7867 | 20.961 | 18.9079 | 19.7978 | 20.7939 | 18.9929 | 20.1042 | 19.3049 | 19.8911 | 18.9244 | 20.1079 | -0.18767 | 20.9464 | 0.048874 | 0.014244 | -26.983 | 3.0975 | -3.18 | -0.18 | 0.84571 | -0.71141 | -7.5702 | 0.82397 | 0.23226 | -16.7062 | 4.392 | 0.42258 | 0.42822 | 0.43097 | 0.36519 | 0.44893 | 0.44174 | 0.42866
42838.4164 | -336 | 22.8767 | 22.8529 | 22.8345 | 22.7646 | 22.4054 | 21.7387 | 22.7096 | 21.8011 | 22.3619 | 22.3759 | 22.3562 | 22.0338 | 21.2553 | 22.2265 | 21.561 | 21.7382 | 21.8719 | 21.0683 | 21.1621 | 21.3815 | 20.467 | 20.6101 | 20.8992 | 21.8829 | 21.6489 | 21.2807 | 20.2856 | 20.3713 | 20.4214 | 22.0421 | 21.6474 | 21.1794 | 21.9832 | 21.7276 | 21.346 | 19.9216 | 20.332 |  | 20.5381 | 20.0651 | 20.1935 | 19.0818 |  | 16.6876 | 16.7174 | 16.4695 | 16.6698 | 16.8093 | 17.2628 | 17.8193 | 15.9237 | 16.8493 | 16.069 | 16.8981 | 17.8627 | 44.4703 | 47.4876 | 43.4991 | 21.3489 |  |  | 0.55024 | -0.11572 | -40.8491 | 0.54668 | 0.1401 | -197.8552 | 13.8457 | -0.4886 | -0.34318 | -0.063668 | -0.075225 | 8.8283 | 9.0579 | 1.9787 | 21.788 | 22.0065 | 22.21 | 22.266 | 22.0987 | 21.4269 | 20.2465 | 22.2039 | 22.3746 | 22.4051 | 22.3601 | 21.9923 | 21.2318 | 22.2789 | 17.372 | 17.1687 | 16.4485 | 16.289 | 16.2799 | 17.0592 | 16.8607 | 22.3845 | 22.1561 | 21.7088 | 22.0884 | 21.8086 | 21.3163 | 21.9515 | 21.5362 | 20.9219 | 20.1112 | 20.2834 | 19.8233 | 19.7963 | -0.10065 | 0.12309 | 20.7324 | 22.0809 | 22.3944 | 20.0951 | 21.6852 | 22.1335 | 21.9619 | 21.719 | 21.2924 | 21.7947 | 21.4507 | 21.0489 | 20.2384 | 20.2909 | 20.2462 | 20.2314 | 20.1194 |  | 20.2302 | 19.8079 | 20.1239 | 19.6739 | 20.0992 | 20.3549 |  | 20.427 |  |  | 20.2755 | 20.3791 | 20.621 | [5 empty] | 21.9505 | 20.3461 | 21.6882 | 22.0655 | 19.5635 | 21.1857 | 21.8133 | 19.3406 | 19.9018 | 21.1097 |  | 19.7373 | 20.913 | 18.8819 | 19.7155 | 20.7937 | 19.4764 | 19.9836 | 19.0762 | 20.167 | 19.141 | 20.2299 | 18.9219 | 20.0276 | 21.0262 | 19.4563 | 19.7861 | 20.964 | 18.9083 | 19.7985 | 20.7949 | 18.9909 | 20.1057 | 19.2975 | 19.8856 | 18.9224 | 20.1051 | -0.11978 | 20.9472 | 0.048671 | 0.013729 | -27.107 | 3.0975 | -6.42 | -0.11 | 0.88573 | -0.40361 | -7.5833 | 0.87727 | 0.44452 | -16.7051 | 4.4191 | 0.42313 | 0.42822 | 0.43112 | 0.36743 | 0.4469 | 0.44162 | 0.42812
42838.4164 | -335 | 22.8918 | 22.8527 | 22.8428 | 22.7655 | 22.4069 | 21.7409 | 22.7136 | 21.8037 | 22.3627 | 22.3738 | 22.3536 | 22.0311 | 21.2614 | 22.227 | 21.5688 | 21.7389 | 21.8722 | 21.073 | 21.1715 | 21.3841 | 20.4725 | 20.6092 | 20.907 | 21.8858 | 21.6515 | 21.2782 | 20.2833 | 20.3753 | 20.4183 | 22.0368 | 21.6502 | 21.1799 | 21.9859 | 21.7265 | 21.3497 | 19.9238 | 20.3478 |  | 20.5477 | 20.0691 | 20.2002 | 19.0805 |  | 16.6928 | 16.7233 | 16.4719 | 16.6788 | 16.8181 | 17.2545 | 17.7991 | 15.9359 | 16.8515 | 16.0773 | 16.9018 | 17.8692 | 44.4727 | 47.5025 | 43.4996 | 21.3506 |  |  | 0.24928 | -0.27277 | -41.386 | 0.44745 | -0.095808 | -197.848 | 13.6965 | -0.5162 | -0.1733 | -0.042268 | 0.019734 | 8.8288 | 9.0586 | 1.9784 | 21.7874 | 22.0097 | 22.2101 | 22.2693 | 22.1017 | 21.4296 | 20.2383 | 22.2005 | 22.3696 | 22.4059 | 22.3602 | 21.991 | 21.2269 | 22.2751 | 17.3409 | 17.1541 | 16.406 | 16.296 | 16.2927 | 17.0727 | 16.8564 | 22.3791 | 22.1566 | 21.7155 | 22.0889 | 21.7991 | 21.3138 | 21.9454 | 21.529 | 20.912 | 20.1037 | 20.2789 | 19.821 | 19.7906 | 0.045034 | 0.25471 | 20.7254 | 22.0839 | 22.3784 | 20.0886 | 21.6768 | 22.1275 | 21.9503 | 21.7181 | 21.2859 | 21.7888 | 21.4572 | 21.0486 | 20.2374 | 20.2705 | 20.2314 | 20.2237 | 20.1061 |  | 20.2266 | 19.808 | 20.1136 | 19.6597 | 20.1023 | 20.3561 |  | 20.4289 |  |  | 20.2739 | 20.3818 | 20.6169 | [5 empty] | 21.9534 | 20.3478 | 21.6866 | 22.0664 | 19.5628 | 21.1829 | 21.8142 | 19.338 | 19.8979 | 21.1123 |  | 19.7303 | 20.9078 | 18.8843 | 19.7118 | 20.7973 | 19.4745 | 19.9804 | 19.0682 | 20.1677 | 19.1334 | 20.2236 | 18.9272 | 20.0283 | 21.0311 | 19.4631 | 19.7907 | 20.9601 | 18.9106 | 19.8009 | 20.7927 | 18.9974 | 20.1111 | 19.2962 | 19.8863 | 18.9179 | 20.0972 | -0.083793 | 20.9476 | 0.047 | 0.013148 | -27.0781 | 3.0976 | -8.57 | 0.05 | 0.59616 | -0.61968 | -7.633 | 0.79368 | -0.36759 | -16.7045 | 4.3952 | 0.42338 | 0.42787 | 0.43162 | 0.37245 | 0.45111 | 0.44173 | 0.42803
42838.4164 | -334 | 22.8842 | 22.8555 | 22.8411 | 22.7716 | 22.4066 | 21.7418 | 22.7131 | 21.8115 | 22.3646 | 22.3726 | 22.3628 | 22.0332 | 21.257 | 22.2234 | 21.5713 | 21.7468 | 21.8825 | 21.0754 | 21.1715 | 21.3864 | 20.4766 | 20.6135 | 20.9067 | 21.8932 | 21.6498 | 21.2879 | 20.2892 | 20.3738 | 20.419 | 22.0385 | 21.6482 | 21.1729 | 21.9823 | 21.7305 | 21.344 | 19.9227 | 20.3422 |  | 20.5383 | 20.057 | 20.1897 | 19.0713 |  | 16.6981 | 16.7536 | 16.4723 | 16.6763 | 16.8167 | 17.2751 | 17.8179 | 15.9247 | 16.849 | 16.0625 | 16.9017 | 17.8618 | 44.4579 | 47.5023 | 43.4986 | 21.3502 |  |  | 0.58901 | -0.37396 | -41.4471 | 0.35743 | 0.094756 | -197.8841 | 13.7425 | -0.13244 | -0.061011 | -0.19144 | -0.11533 | 8.8292 | 9.0587 | 1.9787 | 21.7813 | 22.0046 | 22.2012 | 22.2683 | 22.0993 | 21.4258 | 20.2309 | 22.1958 | 22.3667 | 22.4038 | 22.3592 | 21.9861 | 21.2231 | 22.2655 | 17.2961 | 17.1632 | 16.3663 | 16.3023 | 16.3062 | 17.076 | 16.8715 | 22.3808 | 22.1546 | 21.716 | 22.0833 | 21.8007 | 21.3117 | 21.9471 | 21.5299 | 20.9075 | 20.1046 | 20.2817 | 19.8237 | 19.7953 | 0.071771 | -0.068061 | 20.7288 | 22.077 | 22.3832 | 20.0734 | 21.6712 | 22.1292 | 21.9585 | 21.713 | 21.2783 | 21.7882 | 21.4544 | 21.0448 | 20.2361 | 20.2602 | 20.2267 | 20.2208 | 20.0814 |  | 20.2185 | 19.8069 | 20.1126 | 19.6634 | 20.0902 | 20.348 |  | 20.4229 |  |  | 20.27 | 20.3786 | 20.6089 | [5 empty] | 21.9465 | 20.3432 | 21.6792 | 22.0628 | 19.552 | 21.1844 | 21.811 | 19.3364 | 19.8934 | 21.1146 |  | 19.7321 | 20.9074 | 18.882 | 19.7138 | 20.8008 | 19.4704 | 19.9832 | 19.0713 | 20.1642 | 19.1391 | 20.2253 | 18.9293 | 20.027 | 21.0299 | 19.4594 | 19.7946 | 20.9663 | 18.9112 | 19.7988 | 20.7916 | 18.9954 | 20.1105 | 19.2993 | 19.8873 | 18.9186 | 20.0982 | -0.23664 | 20.9476 | 0.046576 | 0.013555 | -27.0375 | 3.0975 | 3.09 | -0.14 | 0.91639 | -0.72562 | -7.6391 | 0.70939 | 0.36558 | -16.7067 | 4.4027 | 0.4238 | 0.42787 | 0.43111 | 0.37782 | 0.45728 | 0.44195 | 0.42793
42838.4164 | -333 | 22.8921 | 22.865 | 22.8402 | 22.7695 | 22.4081 | 21.7452 | 22.7095 | 21.8133 | 22.3666 | 22.3805 | 22.3616 | 22.0339 | 21.2543 | 22.2266 | 21.5649 | 21.7485 | 21.88 | 21.0764 | 21.1683 | 21.3879 | 20.4789 | 20.6113 | 20.9078 | 21.8846 | 21.652 | 21.2867 | 20.2912 | 20.3756 | 20.4148 | 22.0404 | 21.6531 | 21.1737 | 21.9932 | 21.7339 | 21.3554 | 19.9287 | 20.3478 |  | 20.5425 | 20.0742 | 20.1951 | 19.0727 |  | 16.7171 | 16.7697 | 16.4723 | 16.6764 | 16.8217 | 17.3054 | 17.8474 | 15.931 | 16.8462 | 16.0013 | 16.8961 | 17.8731 | 44.4469 | 47.5045 | 43.4905 | 21.3559 |  |  | 0.43327 | -0.2248 | -41.9557 | 0.44811 | 0.13418 | -197.8414 | 13.4304 | -0.16596 | -0.067433 | -0.28333 | 0.087786 | 8.8295 | 9.0592 | 1.9791 | 21.7781 | 22.0124 | 22.2035 | 22.2717 | 22.0925 | 21.4217 | 20.2386 | 22.1992 | 22.372 | 22.4086 | 22.3564 | 21.9886 | 21.226 | 22.2695 | 17.2755 | 17.1566 | 16.3494 | 16.301 | 16.3082 | 17.073 | 16.8621 | 22.3821 | 22.1516 | 21.7084 | 22.0835 | 21.8072 | 21.3084 | 21.9475 | 21.5331 | 20.908 | 20.1089 | 20.2712 | 19.8269 | 19.7924 | -0.039701 | -0.02983 | 20.7383 | 22.0836 | 22.3862 | 20.0933 | 21.6804 | 22.1381 | 21.9668 | 21.7145 | 21.2903 | 21.7884 | 21.4591 | 21.0544 | 20.2469 | 20.2711 | 20.2487 | 20.2273 | 20.0615 |  | 20.22 | 19.7944 | 20.1094 | 19.663 | 20.0871 | 20.3491 |  | 20.4263 |  |  | 20.2746 | 20.3708 | 20.6038 | [5 empty] | 21.9474 | 20.3393 | 21.6799 | 22.0657 | 19.5502 | 21.1841 | 21.8067 | 19.3387 | 19.8968 | 21.1151 |  | 19.745 | 20.9152 | 18.8874 | 19.7166 | 20.8052 | 19.474 | 19.9969 | 19.0802 | 20.1727 | 19.148 | 20.2272 | 18.9279 | 20.0345 | 21.0296 | 19.4549 | 19.7892 | 20.958 | 18.9141 | 19.7927 | 20.7896 | 19.0055 | 20.1096 | 19.2962 | 19.8917 | 18.9177 | 20.0958 | -0.1131 | 20.9468 | 0.046914 | 0.012647 | -27.1165 | 3.0976 | -2.61 | -0.14 | 0.78596 | -0.56261 | -7.686 | 0.79432 | 0.43507 | -16.7057 | 4.3526 | 0.4244 | 0.42811 | 0.43102 | 0.37977 | 0.45807 | 0.44211 | 0.42815
42838.4164 | -332 | 22.8874 | 22.8649 | 22.8459 | 22.7708 | 22.4056 | 21.7453 | 22.7137 | 21.8104 | 22.3639 | 22.3734 | 22.361 | 22.0341 | 21.251 | 22.231 | 21.5737 | 21.7446 | 21.8767 | 21.0651 | 21.1707 | 21.3924 | 20.4728 | 20.6149 | 20.907 | 21.8841 | 21.6488 | 21.2837 | 20.2889 | 20.3874 | 20.407 | 22.0471 | 21.6542 | 21.1809 | 21.9894 | 21.7283 | 21.3537 | 19.9256 | 20.3515 |  | 20.5437 | 20.078 | 20.1909 | 19.0648 |  | 16.7197 | 16.7617 | 16.4731 | 16.678 | 16.8243 | 17.316 | 17.8666 | 15.9271 | 16.8395 | 15.9256 | 16.8934 | 17.868 | 44.4338 | 47.5061 | 43.4879 | 21.351 |  |  | 0.62055 | -0.22808 | -42.0082 | 0.19052 | 0.24064 | -197.8381 | 13.2457 | -0.16792 | -0.03727 | -0.25228 | 0.032754 | 8.8292 | 9.059 | 1.979 | 21.7799 | 22.0036 | 22.1962 | 22.2602 | 22.0908 | 21.4195 | 20.2261 | 22.1898 | 22.3712 | 22.4073 | 22.3523 | 21.9874 | 21.218 | 22.2654 | 17.2658 | 17.1836 | 16.3489 | 16.311 | 16.3338 | 17.0744 | 16.8688 | 22.3937 | 22.1554 | 21.7185 | 22.0944 | 21.8119 | 21.3234 | 21.9536 | 21.5344 | 20.9219 | 20.1164 | 20.285 | 19.8264 | 19.7889 | -0.078038 | -0.034205 | 20.7357 | 22.0833 | 22.3832 | 20.091 | 21.6853 | 22.1298 | 21.9569 | 21.7244 | 21.2834 | 21.7843 | 21.4513 | 21.0586 | 20.2466 | 20.275 | 20.234 | 20.2226 | 20.0777 |  | 20.2313 | 19.7843 | 20.1124 | 19.6706 | 20.0996 | 20.3495 |  | 20.4349 |  |  | 20.2713 | 20.3644 | 20.5897 | [5 empty] | 21.9426 | 20.3335 | 21.6884 | 22.0579 | 19.5461 | 21.1803 | 21.8076 | 19.338 | 19.897 | 21.1222 |  | 19.7463 | 20.9214 | 18.8906 | 19.7297 | 20.8064 | 19.4712 | 19.9968 | 19.076 | 20.1658 | 19.1572 | 20.2266 | 18.9255 | 20.0303 | 21.0293 | 19.4494 | 19.7795 | 20.9563 | 18.9108 | 19.7913 | 20.7887 | 18.9956 | 20.1155 | 19.2927 | 19.8863 | 18.9103 | 20.0993 | -0.11793 | 20.9472 | 0.047762 | 0.01272 | -27.1083 | 3.0976 | -15.62 | 0.03 | 0.94059 | -0.56669 | -7.6907 | 0.51793 | 0.58263 | -16.7059 | 4.3227 | 0.42433 | 0.42849 | 0.43122 | 0.38101 | 0.45889 | 0.44223 | 0.4285
42838.4164 | -331 | 22.8826 | 22.8576 | 22.8415 | 22.7647 | 22.3994 | 21.747 | 22.7142 | 21.8069 | 22.3625 | 22.3739 | 22.3533 | 22.0361 | 21.2492 | 22.2243 | 21.5644 | 21.7352 | 21.8783 | 21.067 | 21.1664 | 21.3796 | 20.4699 | 20.6057 | 20.9101 | 21.8779 | 21.6413 | 21.2815 | 20.29 | 20.3809 | 20.3989 | 22.0464 | 21.6564 | 21.1853 | 21.9886 | 21.7282 | 21.3529 | 19.9228 | 20.3592 |  | 20.5364 | 20.0758 | 20.189 | 19.0523 |  | 16.718 | 16.765 | 16.4668 | 16.6799 | 16.8167 | 17.3045 | 17.8692 | 15.9274 | 16.8419 | 15.9154 | 16.8947 | 17.8773 | 44.4402 | 47.5179 | 43.4947 | 21.3607 |  |  | 0.72569 | -0.33979 | -42.2441 | 0.41985 | 0.16901 | -197.8512 | 13.2628 | -0.39266 | 0.17426 | -0.11947 | 0.031713 | 8.829 | 9.0587 | 1.979 | 21.7965 | 22.0056 | 22.2158 | 22.2805 | 22.1016 | 21.4255 | 20.2449 | 22.2078 | 22.3803 | 22.4119 | 22.3659 | 21.9959 | 21.2352 | 22.2798 | 17.2535 | 17.174 | 16.3286 | 16.3123 | 16.3324 | 17.0776 | 16.8557 | 22.389 | 22.1548 | 21.7158 | 22.0861 | 21.8066 | 21.3207 | 21.9551 | 21.5398 | 20.9205 | 20.1213 | 20.2876 | 19.8344 | 19.7894 | 0.009449 | -0.066919 | 20.7407 | 22.0833 | 22.3987 | 20.0976 | 21.6915 | 22.1323 | 21.9611 | 21.7302 | 21.2952 | 21.7984 | 21.4671 | 21.0618 | 20.2475 | 20.2753 | 20.2463 | 20.2309 | 20.0762 |  | 20.2285 | 19.7813 | 20.1236 | 19.6811 | 20.0993 | 20.3477 |  | 20.4343 |  |  | 20.2844 | 20.3737 | 20.6046 | [5 empty] | 21.9538 | 20.3488 | 21.6869 | 22.0681 | 19.5573 | 21.1856 | 21.8176 | 19.337 | 19.8902 | 21.1165 |  | 19.7411 | 20.9143 | 18.8883 | 19.7206 | 20.7993 | 19.4694 | 19.9958 | 19.0662 | 20.161 | 19.147 | 20.2182 | 18.9073 | 20.0255 | 21.0274 | 19.4406 | 19.7882 | 20.9587 | 18.9095 | 19.7891 | 20.7841 | 19.0071 | 20.1053 | 19.2873 | 19.888 | 18.916 | 20.095 | -0.12405 | 20.9473 | 0.047344 | 0.01362 | -27.0231 | 3.0976 | 1.51 | -0.15 | 1.0171 | -0.69169 | -7.7123 | 0.76887 | 0.48828 | -16.7061 | 4.3254 | 0.42428 | 0.42895 | 0.43092 | 0.38275 | 0.45963 | 0.44248 | 0.42865
42838.4165 | -330 | 22.8786 | 22.8453 | 22.8365 | 22.7619 | 22.3901 | 21.7403 | 22.7087 | 21.7984 | 22.3606 | 22.3694 | 22.3494 | 22.0358 | 21.2483 | 22.2222 | 21.572 | 21.7467 | 21.8846 | 21.0721 | 21.1746 | 21.3872 | 20.4697 | 20.6146 | 20.917 | 21.8919 | 21.654 | 21.294 | 20.2889 | 20.3743 | 20.4038 | 22.0404 | 21.6525 | 21.1761 | 21.9808 | 21.7203 | 21.3485 | 19.9168 | 20.3614 |  | 20.5314 | 20.0694 | 20.1909 | 19.0373 |  | 16.7188 | 16.7518 | 16.4638 | 16.6741 | 16.8096 | 17.3015 | 17.8551 | 15.92 | 16.8397 | 15.9324 | 16.8887 | 17.872 | 44.4325 | 47.5232 | 43.5003 | 21.352 |  |  | 0.4313 | -0.1742 | -42.4998 | 0.60319 | 0.063872 | -197.8506 | 13.1288 | -0.47546 | 0.1044 | 0.1541 | -0.12036 | 8.8286 | 9.0583 | 1.9783 | 21.7801 | 22.0147 | 22.205 | 22.2679 | 22.105 | 21.4262 | 20.243 | 22.2051 | 22.3735 | 22.4038 | 22.3672 | 21.9951 | 21.2305 | 22.2758 | 17.2357 | 17.1901 | 16.2866 | 16.3116 | 16.3295 | 17.073 | 16.8582 | 22.3861 | 22.1559 | 21.7115 | 22.0872 | 21.8001 | 21.3162 | 21.9464 | 21.53 | 20.9145 | 20.1116 | 20.2779 | 19.8322 | 19.7896 | -0.024759 | -0.14148 | 20.7266 | 22.0794 | 22.3915 | 20.0917 | 21.6813 | 22.126 | 21.963 | 21.7168 | 21.2901 | 21.7913 | 21.4567 | 21.0582 | 20.2445 | 20.2786 | 20.2354 | 20.218 | 20.0586 |  | 20.2276 | 19.7697 | 20.1188 | 19.6949 | 20.1022 | 20.3529 |  | 20.4405 |  |  | 20.2818 | 20.3749 | 20.6092 | [5 empty] | 21.9469 | 20.3446 | 21.6884 | 22.0608 | 19.5555 | 21.1861 | 21.7995 | 19.3365 | 19.8802 | 21.1114 |  | 19.7438 | 20.9127 | 18.8887 | 19.7198 | 20.7956 | 19.4657 | 19.9954 | 19.0563 | 20.1554 | 19.1458 | 20.2186 | 18.921 | 20.0319 | 21.0283 | 19.4272 | 19.7942 | 20.9555 | 18.9024 | 19.7951 | 20.7851 | 19.0083 | 20.1218 | 19.2881 | 19.8921 | 18.9041 | 20.0874 | -0.051887 | 20.9475 | 0.04692 | 0.015123 | -27.0346 | 3.0975 | -15.79 | -0.01 | 0.78415 | -0.49524 | -7.7355 | 0.92155 | 0.30016 | -16.706 | 4.3034 | 0.42474 | 0.42911 | 0.43063 | 0.38419 | 0.46459 | 0.44269 | 0.42832
42838.4165 | -329 | 22.8861 | 22.8589 | 22.8394 | 22.7718 | 22.3996 | 21.7454 | 22.7104 | 21.813 | 22.3716 | 22.3776 | 22.3594 | 22.0424 | 21.2558 | 22.232 | 21.5719 | 21.741 | 21.8773 | 21.0735 | 21.1676 | 21.3908 | 20.4658 | 20.61 | 20.9055 | 21.8817 | 21.6431 | 21.283 | 20.2883 | 20.3799 | 20.3973 | 22.0299 | 21.6498 | 21.1733 | 21.9819 | 21.7153 | 21.3473 | 19.9133 | 20.3693 |  | 20.5317 | 20.0619 | 20.1907 | 19.029 |  | 16.7154 | 16.7607 | 16.4661 | 16.6802 | 16.808 | 17.2993 | 17.8518 | 15.9205 | 16.8377 | 15.952 | 16.9017 | 17.8698 | 44.4264 | 47.5301 | 43.5032 | 21.3588 |  |  | 0.51738 | -0.068405 | -42.4906 | 0.60845 | 0.21895 | -197.8657 | 13.1248 | -0.51226 | 0.035705 | 0.10984 | 0.03449 | 8.8293 | 9.0593 | 1.9784 | 21.7852 | 22.0129 | 22.2021 | 22.27 | 22.0977 | 21.4302 | 20.244 | 22.2057 | 22.376 | 22.4036 | 22.3623 | 21.9893 | 21.224 | 22.2714 | 17.2406 | 17.1802 | 16.2534 | 16.3398 | 16.3542 | 17.0774 | 16.8649 | 22.3834 | 22.1479 | 21.7107 | 22.0768 | 21.7996 | 21.3064 | 21.9433 | 21.5269 | 20.9191 | 20.1074 | 20.2711 | 19.8277 | 19.791 | -0.0027402 | -0.25674 | 20.7282 | 22.0713 | 22.3955 | 20.0827 | 21.6791 | 22.1214 | 21.9522 | 21.7142 | 21.2866 | 21.7886 | 21.4475 | 21.0488 | 20.2417 | 20.2647 | 20.2233 | 20.217 | 20.0443 |  | 20.2229 | 19.7465 | 20.1152 | 19.6908 | 20.0898 | 20.3411 |  | 20.4364 |  |  | 20.2937 | 20.3764 | 20.6022 | [5 empty] | 21.9547 | 20.3386 | 21.6967 | 22.0665 | 19.5638 | 21.1903 | 21.8198 | 19.3487 | 19.9055 | 21.1279 |  | 19.7496 | 20.9257 | 18.8901 | 19.7322 | 20.8124 | 19.4748 | 19.9915 | 19.067 | 20.1639 | 19.1507 | 20.2258 | 18.9143 | 20.0365 | 21.0264 | 19.4398 | 19.7998 | 20.9576 | 18.9149 | 19.796 | 20.795 | 19.0122 | 20.114 | 19.2933 | 19.881 | 18.9148 | 20.0988 | -0.2513 | 20.946 | 0.047608 | 0.012807 | -26.9897 | 3.0976 | -10.17 | -0.02 | 0.85884 | -0.31034 | -7.7347 | 0.92557 | 0.55575 | -16.7066 | 4.3028 | 0.42497 | 0.42964 | 0.43034 | 0.38415 | 0.46906 | 0.44281 | 0.42814
42838.4165 | -328 | 22.8904 | 22.8526 | 22.8421 | 22.7751 | 22.4057 | 21.7394 | 22.7174 | 21.809 | 22.3649 | 22.3874 | 22.3638 | 22.0439 | 21.2501 | 22.2227 | 21.5752 | 21.7458 | 21.8828 | 21.0726 | 21.1718 | 21.3927 | 20.4719 | 20.6056 | 20.9081 | 21.8884 | 21.6475 | 21.2875 | 20.2867 | 20.3781 | 20.396 | 22.0419 | 21.6503 | 21.1803 | 21.9812 | 21.7316 | 21.3478 | 19.9231 | 20.3803 |  | 20.5345 | 20.0677 | 20.1934 | 19.0237 |  | 16.7204 | 16.7581 | 16.4675 | 16.675 | 16.7928 | 17.292 | 17.8641 | 15.9162 | 16.8404 | 15.9258 | 16.8931 | 17.8724 | 44.4179 | 47.5417 | 43.5156 | 21.3548 |  |  | 0.60675 | -0.15843 | -42.0122 | 0.41985 | 0.1999 | -197.8604 | 13.3732 | -0.2954 | -0.13029 | -0.2978 | 0.015742 | 8.8291 | 9.0589 | 1.9793 | 21.7847 | 22.0181 | 22.1998 | 22.2728 | 22.0983 | 21.4272 | 20.2417 | 22.2022 | 22.376 | 22.4082 | 22.3616 | 21.992 | 21.2253 | 22.2719 | 17.2427 | 17.1607 | 16.2333 | 16.3351 | 16.3669 | 17.0788 | 16.8625 | 22.3787 | 22.1457 | 21.7124 | 22.0775 | 21.8025 | 21.3043 | 21.9456 | 21.5313 | 20.9124 | 20.1032 | 20.2703 | 19.8282 | 19.7818 | -0.0041164 | -0.13577 | 20.7203 | 22.0801 | 22.3759 | 20.0834 | 21.6725 | 22.1165 | 21.9473 | 21.7111 | 21.2839 | 21.785 | 21.4479 | 21.0487 | 20.2413 | 20.2595 | 20.224 | 20.2082 | 20.0481 |  | 20.2224 | 19.7368 | 20.1119 | 19.6898 | 20.0913 | 20.3329 |  | 20.4267 |  |  | 20.2752 | 20.3751 | 20.5989 | [5 empty] | 21.9461 | 20.3245 | 21.683 | 22.0603 | 19.5441 | 21.1784 | 21.811 | 19.3433 | 19.8914 | 21.1203 |  | 19.7467 | 20.9182 | 18.8954 | 19.735 | 20.8091 | 19.4815 | 19.9961 | 19.0619 | 20.1545 | 19.1472 | 20.2246 | 18.8976 | 20.0364 | 21.0271 | 19.4325 | 19.8015 | 20.9615 | 18.9057 | 19.7899 | 20.7922 | 19.0039 | 20.1106 | 19.2925 | 19.8799 | 18.9049 | 20.0891 | -0.069695 | 20.9479 | 0.049734 | 0.013105 | -27.0602 | 3.0976 | 9.09 | -0.05 | 0.93006 | -0.4723 | -7.691 | 0.76886 | 0.53101 | -16.7061 | 4.3432 | 0.42485 | 0.4298 | 0.43042 | 0.38409 | 0.47101 | 0.44328 | 0.42826
42838.4165 | -327 | 22.9024 | 22.8602 | 22.8446 | 22.7815 | 22.4085 | 21.7447 | 22.7199 | 21.8103 | 22.3612 | 22.3839 | 22.36 | 22.0376 | 21.2535 | 22.221 | 21.5781 | 21.7475 | 21.8833 | 21.0787 | 21.1737 | 21.3923 | 20.4729 | 20.6131 | 20.9136 | 21.8903 | 21.6456 | 21.2869 | 20.2947 | 20.3844 | 20.4003 | 22.0327 | 21.6508 | 21.1792 | 21.9865 | 21.7192 | 21.3488 | 19.9201 | 20.3832 |  | 20.5341 | 20.0675 | 20.1902 | 19.0204 |  | 16.7277 | 16.7598 | 16.4682 | 16.6703 | 16.785 | 17.2969 | 17.8563 | 15.8877 | 16.8399 | 15.8794 | 16.8949 | 17.8694 | 44.4204 | 47.5507 | 43.5109 | 21.3456 |  |  | 0.52264 | -0.076289 | -42.2737 | 0.70504 | 0.14536 | -197.8092 | 13.138 | -0.38674 | -0.21883 | 0.025497 | -0.072968 | 8.8296 | 9.0593 | 1.9792 | 21.7732 | 22.0089 | 22.1969 | 22.2729 | 22.0997 | 21.4224 | 20.236 | 22.1937 | 22.3725 | 22.4076 | 22.3617 | 21.9907 | 21.228 | 22.2672 | 17.2622 | 17.2078 | 16.2418 | 16.3148 | 16.3667 | 17.0787 | 16.8695 | 22.3894 | 22.1555 | 21.7163 | 22.0889 | 21.8036 | 21.3157 | 21.9521 | 21.5471 | 20.9112 | 20.1072 | 20.2801 | 19.8379 | 19.7832 | -0.036555 | 0.0278 | 20.716 | 22.0703 | 22.3754 | 20.0892 | 21.671 | 22.1194 | 21.9476 | 21.7103 | 21.2826 | 21.7874 | 21.4524 | 21.045 | 20.2335 | 20.2677 | 20.2126 | 20.2019 | 20.0472 |  | 20.2255 | 19.7353 | 20.122 | 19.6956 | 20.0969 | 20.3377 |  | 20.4353 |  |  | 20.2825 | 20.3746 | 20.5982 | [5 empty] | 21.9443 | 20.3207 | 21.6818 | 22.0675 | 19.5507 | 21.1889 | 21.8135 | 19.3343 | 19.8951 | 21.1132 |  | 19.7421 | 20.9143 | 18.8941 | 19.7336 | 20.8029 | 19.4862 | 19.9927 | 19.0592 | 20.1531 | 19.1407 | 20.2189 | 18.9112 | 20.0575 | 21.0398 | 19.4381 | 19.8097 | 20.9712 | 18.9244 | 19.8001 | 20.791 | 19.0138 | 20.1233 | 19.2956 | 19.8908 | 18.9202 | 20.0981 | -0.073961 | 20.9461 | 0.04818 | 0.015217 | -27.0144 | 3.0976 | 8.08 | -0.02 | 0.86319 | -0.32774 | -7.715 | 0.99634 | 0.45281 | -16.7041 | 4.3049 | 0.42498 | 0.43018 | 0.43044 | 0.3819 | 0.47087 | 0.44327 | 0.42835
42838.4165 | -326 | 22.8968 | 22.8671 | 22.8542 | 22.7833 | 22.4138 | 21.7535 | 22.7222 | 21.8193 | 22.371 | 22.379 | 22.3614 | 22.044 | 21.266 | 22.231 | 21.5776 | 21.747 | 21.8819 | 21.0725 | 21.1756 | 21.3932 | 20.4702 | 20.6175 | 20.9208 | 21.8888 | 21.6533 | 21.2829 | 20.2949 | 20.3883 | 20.3958 | 22.0402 | 21.6502 | 21.1772 | 21.9929 | 21.7304 | 21.3537 | 19.9165 | 20.393 |  | 20.531 | 20.0671 | 20.1857 | 19.0123 |  | 16.7294 | 16.7578 | 16.4738 | 16.6798 | 16.7819 | 17.2991 | 17.8684 | 15.8761 | 16.8432 | 15.8627 | 16.8955 | 17.8641 | 44.4165 | 47.5616 | 43.5129 | 21.3468 |  |  | 0.60741 | -0.14266 | -42.733 | 0.30026 | 0.19727 | -197.8572 | 13.0953 | -0.27766 | -0.11997 | -0.11129 | 0.014526 | 8.8294 | 9.059 | 1.9787 | 21.7908 | 22.0116 | 22.2063 | 22.2714 | 22.1016 | 21.421 | 20.248 | 22.202 | 22.3795 | 22.414 | 22.3555 | 21.9926 | 21.2386 | 22.2796 | 17.2715 | 17.1767 | 16.2287 | 16.3059 | 16.3422 | 17.069 | 16.8589 | 22.3865 | 22.1526 | 21.7126 | 22.0884 | 21.8034 | 21.3104 | 21.9522 | 21.5408 | 20.9195 | 20.1134 | 20.2787 | 19.8362 | 19.7856 | -0.11559 | -0.26111 | 20.7244 | 22.0804 | 22.3866 | 20.097 | 21.6826 | 22.1294 | 21.9609 | 21.7167 | 21.2882 | 21.7954 | 21.4546 | 21.0506 | 20.2338 | 20.2793 | 20.219 | 20.2114 | 20.0354 |  | 20.23 | 19.73 | 20.1125 | 19.702 | 20.0918 | 20.3335 |  | 20.4347 |  |  | 20.2815 | 20.3714 | 20.6004 | [5 empty] | 21.9448 | 20.3201 | 21.6888 | 22.0607 | 19.5505 | 21.1877 | 21.8131 | 19.3474 | 19.9001 | 21.1216 |  | 19.7375 | 20.9113 | 18.8959 | 19.7341 | 20.8037 | 19.4811 | 19.9933 | 19.0566 | 20.1452 | 19.1416 | 20.2182 | 18.9081 | 20.0514 | 21.0377 | 19.4302 | 19.8014 | 20.9689 | 18.9224 | 19.7922 | 20.7886 | 19.015 | 20.1208 | 19.2958 | 19.8863 | 18.914 | 20.1034 | -0.23479 | 20.9465 | 0.049384 | 0.018513 | -27.0817 | 3.0976 | 1.22 | -0.09 | 0.93056 | -0.44818 | -7.7567 | 0.6502 | 0.52751 | -16.7062 | 4.2979 | 0.42546 | 0.43001 | 0.43009 | 0.37974 | 0.4711 | 0.44338 | 0.42849
42838.4165 | -325 | 22.8939 | 22.8619 | 22.8442 | 22.7772 | 22.4102 | 21.753 | 22.7224 | 21.8131 | 22.3732 | 22.3769 | 22.3633 | 22.04 | 21.2626 | 22.2268 | 21.5753 | 21.7513 | 21.8816 | 21.0724 | 21.1716 | 21.3884 | 20.4712 | 20.6094 | 20.9154 | 21.8869 | 21.6548 | 21.2844 | 20.2845 | 20.3854 | 20.3893 | 22.0442 | 21.6484 | 21.178 | 21.9828 | 21.7311 | 21.3534 | 19.9255 | 20.3915 |  | 20.5313 | 20.0735 | 20.1865 | 19.001 |  | 16.7287 | 16.7631 | 16.4888 | 16.6849 | 16.7879 | 17.3076 | 17.8887 | 15.8981 | 16.8443 | 15.8578 | 16.899 | 17.8674 | 44.4034 | 47.5692 | 43.5073 | 21.3501 |  |  | 0.58112 | -0.17026 | -42.7403 | 0.40605 | 0.28466 | -197.8749 | 13.0079 | -0.31972 | -0.68918 | -0.12934 | 0.12198 | 8.8298 | 9.0596 | 1.9787 | 21.7913 | 22.012 | 22.2046 | 22.2719 | 22.105 | 21.4204 | 20.2425 | 22.2056 | 22.3764 | 22.4145 | 22.3619 | 21.9947 | 21.2258 | 22.2809 | 17.2826 | 17.1453 | 16.2238 | 16.3025 | 16.3348 | 17.0689 | 16.8566 | 22.3846 | 22.1523 | 21.7106 | 22.0827 | 21.8082 | 21.3116 | 21.9436 | 21.5347 | 20.9147 | 20.1084 | 20.2837 | 19.8398 | 19.7839 | -0.12129 | -0.11124 | 20.7271 | 22.0704 | 22.3869 | 20.0923 | 21.6823 | 22.1321 | 21.9554 | 21.7232 | 21.2928 | 21.7896 | 21.46 | 21.0518 | 20.2478 | 20.2801 | 20.2258 | 20.2113 | 20.0404 |  | 20.2259 | 19.7115 | 20.11 | 19.7015 | 20.0917 | 20.327 |  | 20.4244 |  |  | 20.2811 | 20.3735 | 20.6101 | [5 empty] | 21.9463 | 20.3226 | 21.6851 | 22.0595 | 19.5497 | 21.1814 | 21.8097 | 19.3521 | 19.9039 | 21.1268 |  | 19.7469 | 20.9203 | 18.9058 | 19.7413 | 20.8092 | 19.479 | 20.0044 | 19.0675 | 20.1513 | 19.144 | 20.2218 | 18.9159 | 20.0502 | 21.0422 | 19.4332 | 19.8038 | 20.9738 | 18.9233 | 19.7939 | 20.7946 | 19.0092 | 20.1227 | 19.2914 | 19.8858 | 18.9083 | 20.1018 | -0.098447 | 20.9477 | 0.050066 | 0.014752 | -27.0636 | 3.0976 | -6.05 | -0.08 | 0.91019 | -0.48961 | -7.7575 | 0.75612 | 0.63369 | -16.7072 | 4.2836 | 0.42518 | 0.43044 | 0.4301 | 0.3785 | 0.47138 | 0.44399 | 0.42837
42838.4165 | -324 | 22.8963 | 22.8523 | 22.8463 | 22.7746 | 22.4074 | 21.7499 | 22.7175 | 21.8048 | 22.367 | 22.3758 | 22.3586 | 22.0324 | 21.2572 | 22.2183 | 21.5719 | 21.7482 | 21.8783 | 21.0698 | 21.1634 | 21.3816 | 20.4726 | 20.6105 | 20.9032 | 21.8936 | 21.6515 | 21.2818 | 20.2826 | 20.3792 | 20.3914 | 22.0371 | 21.6495 | 21.1763 | 21.981 | 21.7277 | 21.3451 | 19.9223 | 20.3899 |  | 20.5273 | 20.0697 | 20.187 | 18.9955 |  | 16.7199 | 16.759 | 16.4892 | 16.692 | 16.7859 | 17.3181 | 17.8883 | 15.9361 | 16.8361 | 15.8704 | 16.8931 | 17.8709 | 44.3951 | 47.5787 | 43.5075 | 21.3497 |  |  | 0.56863 | -0.080889 | -43.1503 | 0.71227 | 0.20712 | -197.8493 | 13.0171 | -0.39003 | -0.32255 | -0.12514 | 0.018519 | 8.8297 | 9.0595 | 1.9784 | 21.7823 | 22.0096 | 22.2091 | 22.2664 | 22.1041 | 21.4258 | 20.2453 | 22.2035 | 22.3728 | 22.4134 | 22.3618 | 21.9922 | 21.2235 | 22.2733 | 17.2995 | 17.1427 | 16.2314 | 16.2922 | 16.3354 | 17.076 | 16.8575 | 22.3811 | 22.1477 | 21.7135 | 22.0846 | 21.8025 | 21.3053 | 21.9424 | 21.5269 | 20.9091 | 20.1069 | 20.279 | 19.837 | 19.7817 | 0.031468 | -0.15213 | 20.7293 | 22.0889 | 22.3958 | 20.1014 | 21.6809 | 22.1407 | 21.9645 | 21.7207 | 21.2911 | 21.7927 | 21.463 | 21.0616 | 20.2449 | 20.2878 | 20.2281 | 20.2158 | 20.0516 |  | 20.2204 | 19.7031 | 20.1152 | 19.6905 | 20.0925 | 20.3235 |  | 20.4317 |  |  | 20.2682 | 20.3702 | 20.6097 | [5 empty] | 21.9456 | 20.3219 | 21.6767 | 22.0581 | 19.5431 | 21.1792 | 21.8031 | 19.3545 | 19.9038 | 21.1267 |  | 19.7478 | 20.9264 | 18.907 | 19.7389 | 20.8131 | 19.4837 | 20.005 | 19.07 | 20.1518 | 19.1436 | 20.2247 | 18.9166 | 20.053 | 21.0455 | 19.4256 | 19.811 | 20.9702 | 18.9267 | 19.7962 | 20.7902 | 19.0072 | 20.128 | 19.2924 | 19.8897 | 18.9016 | 20.1005 | -0.087318 | 20.9465 | 0.048297 | 0.015072 | -27.0734 | 3.0976 | -7.17 | -0.04 | 0.90036 | -0.33748 | -7.7945 | 1.0014 | 0.54054 | -16.7064 | 4.2852 | 0.42469 | 0.43085 | 0.43043 | 0.37744 | 0.47063 | 0.44404 | 0.42838
42838.4165 | -323 | 22.9023 | 22.8487 | 22.8539 | 22.7767 | 22.4083 | 21.7547 | 22.7211 | 21.813 | 22.368 | 22.3819 | 22.3619 | 22.0433 | 21.2632 | 22.224 | 21.5724 | 21.7441 | 21.8801 | 21.069 | 21.1665 | 21.3833 | 20.466 | 20.6123 | 20.9005 | 21.8846 | 21.6586 | 21.2777 | 20.2841 | 20.3765 | 20.3859 | 22.0401 | 21.6481 | 21.1755 | 21.9876 | 21.7275 | 21.3398 | 19.9231 | 20.3922 |  | 20.5271 | 20.0684 | 20.1807 | 18.9957 |  | 16.721 | 16.7648 | 16.4844 | 16.6818 | 16.7716 | 17.3074 | 17.875 | 15.9731 | 16.8283 | 15.8921 | 16.8873 | 17.8699 | 44.3863 | 47.5852 | 43.5066 | 21.3512 |  |  | 0.51541 | -0.28131 | -43.2719 | 0.23849 | 0.13353 | -197.8565 | 13.0742 | -0.49386 | 0.024224 | -0.0076514 | 0.19576 | 8.829 | 9.059 | 1.9795 | 21.7808 | 22.0068 | 22.2019 | 22.2617 | 22.1007 | 21.4249 | 20.2391 | 22.2012 | 22.3735 | 22.409 | 22.358 | 21.9918 | 21.2219 | 22.2753 | 17.3099 | 17.1568 | 16.2209 | 16.2792 | 16.3206 | 17.0671 | 16.8522 | 22.3832 | 22.1537 | 21.7133 | 22.0923 | 21.798 | 21.3133 | 21.9494 | 21.5335 | 20.9157 | 20.1151 | 20.2874 | 19.8349 | 19.7803 | 0.12485 | -0.12379 | 20.7176 | 22.0871 | 22.3832 | 20.0924 | 21.6769 | 22.1236 | 21.9523 | 21.7242 | 21.2889 | 21.7876 | 21.4573 | 21.0553 | 20.2426 | 20.2801 | 20.2181 | 20.2064 | 20.064 |  | 20.2165 | 19.6956 | 20.1123 | 19.6857 | 20.0924 | 20.3226 |  | 20.4294 |  |  | 20.265 | 20.3727 | 20.6091 | [5 empty] | 21.9473 | 20.3251 | 21.6787 | 22.0599 | 19.5411 | 21.1818 | 21.8041 | 19.3515 | 19.9042 | 21.1295 |  | 19.7356 | 20.9199 | 18.901 | 19.7341 | 20.8083 | 19.4848 | 19.9979 | 19.0626 | 20.1464 | 19.1425 | 20.2201 | 18.9229 | 20.0656 | 21.0532 | 19.4319 | 19.8194 | 20.977 | 18.9381 | 19.8028 | 20.7996 | 19.0147 | 20.1302 | 19.3045 | 19.8962 | 18.9133 | 20.1111 | 0.008586 | 20.948 | 0.049409 | 0.015101 | -27.0904 | 3.0976 | -7.66 | -0.19 | 0.85718 | -0.62936 | -7.8056 | 0.57948 | 0.434 | -16.7064 | 4.2945 | 0.42421 | 0.43096 | 0.43056 | 0.37524 | 0.47118 | 0.44406 | 0.4287
42838.4166 | -322 | 22.8875 | 22.8456 | 22.8477 | 22.7646 | 22.394 | 21.7462 | 22.7033 | 21.8049 | 22.3597 | 22.3705 | 22.3533 | 22.0319 | 21.2526 | 22.2209 | 21.5734 | 21.7458 | 21.884 | 21.0758 | 21.1645 | 21.385 | 20.4657 | 20.6157 | 20.9102 | 21.8831 | 21.6548 | 21.2813 | 20.2878 | 20.3811 | 20.3836 | 22.039 | 21.6471 | 21.1735 | 21.9854 | 21.7165 | 21.3399 | 19.9222 | 20.3941 |  | 20.5233 | 20.069 | 20.1772 | 18.9903 |  | 16.7344 | 16.7687 | 16.4956 | 16.6879 | 16.7695 | 17.3105 | 17.8847 | 16.025 | 16.8448 | 15.9607 | 16.8942 | 17.8721 | 44.3817 | 47.5791 | 43.4961 | 21.3479 |  |  | 0.55352 | -0.45544 | -42.8697 | 0.43694 | 0.20055 | -197.8683 | 12.7963 | -0.5346 | 0.046603 | -0.07185 | 0.011749 | 8.8298 | 9.0595 | 1.9788 | 21.7779 | 22.0071 | 22.1925 | 22.265 | 22.09 | 21.4241 | 20.2333 | 22.1961 | 22.3698 | 22.3986 | 22.3522 | 21.9857 | 21.2174 | 22.2651 | 17.3308 | 17.1676 | 16.2102 | 16.2956 | 16.3095 | 17.0758 | 16.8545 | 22.383 | 22.1541 | 21.7153 | 22.0888 | 21.8036 | 21.315 | 21.9467 | 21.534 | 20.9127 | 20.1183 | 20.2792 | 19.8417 | 19.7785 | 0.13449 | -0.068631 | 20.7185 | 22.0794 | 22.3947 | 20.0921 | 21.6786 | 22.1319 | 21.9591 | 21.7204 | 21.2947 | 21.7979 | 21.463 | 21.0623 | 20.2456 | 20.281 | 20.2257 | 20.2142 | 20.0679 |  | 20.2169 | 19.6905 | 20.1075 | 19.6848 | 20.0858 | 20.3245 |  | 20.427 |  |  | 20.2621 | 20.3781 | 20.6159 | [5 empty] | 21.9485 | 20.3327 | 21.6841 | 22.0669 | 19.5466 | 21.1837 | 21.809 | 19.3565 | 19.9091 | 21.1331 |  | 19.7382 | 20.926 | 18.9078 | 19.7431 | 20.8145 | 19.4871 | 20.0015 | 19.0692 | 20.147 | 19.1453 | 20.2186 | 18.9175 | 20.0633 | 21.0569 | 19.426 | 19.8167 | 20.978 | 18.9394 | 19.8015 | 20.7979 | 19.0132 | 20.1336 | 19.3009 | 19.8914 | 18.9219 | 20.1114 | -0.1272 | 20.9473 | 0.049095 | 0.015239 | -27.0886 | 3.0976 | -9.69 | -0.03 | 0.88831 | -0.8008 | -7.7693 | 0.78436 | 0.53189 | -16.707 | 4.2487 | 0.42412 | 0.43094 | 0.43037 | 0.37395 | 0.47264 | 0.44418 | 0.42885
42838.4166 | -321 | 22.8824 | 22.8541 | 22.845 | 22.7748 | 22.4064 | 21.7479 | 22.7104 | 21.8139 | 22.3652 | 22.3751 | 22.3559 | 22.0364 | 21.2606 | 22.2171 | 21.5694 | 21.7524 | 21.8842 | 21.076 | 21.1618 | 21.3867 | 20.4726 | 20.6149 | 20.9118 | 21.8908 | 21.647 | 21.2887 | 20.2875 | 20.3758 | 20.3788 | 22.0401 | 21.6467 | 21.1761 | 21.9882 | 21.7289 | 21.3455 | 19.9201 | 20.396 |  | 20.5268 | 20.0782 | 20.1848 | 19.009 |  | 16.7315 | 16.7686 | 16.483 | 16.681 | 16.7678 | 17.2999 | 17.8757 | 16.0494 | 16.8414 | 15.9654 | 16.8876 | 17.8662 | 44.378 | 47.5784 | 43.4835 | 21.3425 |  |  | 0.59098 | -0.32403 | -42.3447 | 0.43037 | 0.19858 | -197.8401 | 12.7575 | -0.45048 | -0.28033 | -0.12031 | 0.052198 | 8.8286 | 9.0583 | 1.9788 | 21.7837 | 22.007 | 22.1963 | 22.2658 | 22.0982 | 21.4247 | 20.2321 | 22.1989 | 22.3714 | 22.4016 | 22.3582 | 21.9903 | 21.2216 | 22.2665 | 17.3296 | 17.1698 | 16.2142 | 16.2928 | 16.2998 | 17.075 | 16.8501 | 22.3798 | 22.1532 | 21.7126 | 22.0852 | 21.7961 | 21.314 | 21.9506 | 21.5328 | 20.9117 | 20.1158 | 20.2768 | 19.8353 | 19.7679 | 0.059385 | 0.081627 | 20.7234 | 22.0893 | 22.3918 | 20.1055 | 21.695 | 22.1409 | 21.973 | 21.7345 | 21.2954 | 21.8034 | 21.4687 | 21.0657 | 20.2466 | 20.2885 | 20.2232 | 20.2226 | 20.073 |  | 20.2273 | 19.6865 | 20.1076 | 19.7058 | 20.0952 | 20.3233 |  | 20.4259 |  |  | 20.2533 | 20.377 | 20.6229 | [5 empty] | 21.9449 | 20.3368 | 21.687 | 22.0645 | 19.549 | 21.1852 | 21.8082 | 19.3552 | 19.9119 | 21.1315 |  | 19.7419 | 20.927 | 18.9082 | 19.7397 | 20.8131 | 19.4855 | 20.0045 | 19.0733 | 20.146 | 19.1427 | 20.2212 | 18.906 | 20.0589 | 21.0505 | 19.4199 | 19.8147 | 20.976 | 18.9412 | 19.7985 | 20.7963 | 19.0118 | 20.129 | 19.2998 | 19.889 | 18.9195 | 20.1117 | -0.10939 | 20.9474 | 0.049157 | 0.016103 | -26.9576 | 3.0976 | 16.12 | -0.08 | 0.91786 | -0.67545 | -7.7215 | 0.77844 | 0.52926 | -16.7055 | 4.2421 | 0.42432 | 0.43105 | 0.4301 | 0.37399 | 0.47169 | 0.44359 | 0.42906
42838.4166 | -320 | 22.8846 | 22.8543 | 22.8498 | 22.7743 | 22.4055 | 21.7523 | 22.7207 | 21.8042 | 22.363 | 22.3776 | 22.3506 | 22.0379 | 21.2482 | 22.2261 | 21.5745 | 21.7561 | 21.8889 | 21.0724 | 21.168 | 21.3906 | 20.4793 | 20.6196 | 20.9192 | 21.8907 | 21.6609 | 21.2892 | 20.2887 | 20.3796 | 20.382 | 22.0454 | 21.6573 | 21.1834 | 21.9883 | 21.7295 | 21.3507 | 19.9192 | 20.407 |  | 20.5316 | 20.0747 | 20.1951 | 19.0181 |  | 16.7272 | 16.758 | 16.4783 | 16.6812 | 16.764 | 17.2916 | 17.8832 | 16.0414 | 16.8365 | 15.9325 | 16.8813 | 17.8735 | 44.3744 | 47.5755 | 43.4764 | 21.3461 |  |  | 0.60346 | -0.33388 | -43.0899 | 0.64065 | 0.1447 | -197.8348 | 12.8955 | -0.49517 | 0.014494 | -0.14444 | 0.029977 | 8.8298 | 9.0594 | 1.9785 | 21.7844 | 22.0079 | 22.206 | 22.2668 | 22.104 | 21.4321 | 20.2395 | 22.2004 | 22.3736 | 22.4043 | 22.3597 | 21.9875 | 21.2268 | 22.2765 | 17.3236 | 17.1854 | 16.2168 | 16.2851 | 16.2908 | 17.0759 | 16.852 | 22.3782 | 22.1505 | 21.7127 | 22.0878 | 21.7963 | 21.3021 | 21.9434 | 21.527 | 20.908 | 20.1047 | 20.2745 | 19.838 | 19.7604 | 0.081405 | 0.06546 | 20.717 | 22.0889 | 22.3904 | 20.0916 | 21.6819 | 22.1307 | 21.97 | 21.7218 | 21.2941 | 21.804 | 21.4647 | 21.0649 | 20.2471 | 20.2754 | 20.2236 | 20.2085 | 20.0763 |  | 20.2252 | 19.6846 | 20.1092 | 19.7083 | 20.0922 | 20.3215 |  | 20.422 |  |  | 20.2511 | 20.3785 | 20.622 | [5 empty] | 21.9503 | 20.336 | 21.6898 | 22.0619 | 19.5434 | 21.186 | 21.81 | 19.3554 | 19.9135 | 21.1308 |  | 19.7422 | 20.9255 | 18.9107 | 19.7318 | 20.8084 | 19.4816 | 20.0059 | 19.0688 | 20.1407 | 19.1399 | 20.2213 | 18.898 | 20.068 | 21.0577 | 19.431 | 19.82 | 20.9811 | 18.9457 | 19.8091 | 20.8035 | 19.0118 | 20.1429 | 19.2955 | 19.9015 | 18.9245 | 20.1185 | -0.16207 | 20.9466 | 0.048475 | 0.016792 | -27.0299 | 3.0975 | 9.35 | 0 | 0.92751 | -0.68563 | -7.7891 | 0.94974 | 0.45178 | -16.705 | 4.265 | 0.42416 | 0.43116 | 0.42993 | 0.37476 | 0.47162 | 0.44331 | 0.4289
42838.4166 | -319 | 22.8918 | 22.8534 | 22.8415 | 22.776 | 22.3996 | 21.7464 | 22.7109 | 21.81 | 22.3696 | 22.3733 | 22.3603 | 22.0446 | 21.2491 | 22.22 | 21.5693 | 21.7412 | 21.8735 | 21.0644 | 21.1632 | 21.3859 | 20.4586 | 20.6117 | 20.9017 | 21.8815 | 21.6507 | 21.281 | 20.278 | 20.3755 | 20.3706 | 22.0457 | 21.6567 | 21.1853 | 21.9958 | 21.7298 | 21.3452 | 19.9218 | 20.4077 |  | 20.5328 | 20.0809 | 20.1814 | 19.039 |  | 16.7315 | 16.7709 | 16.4865 | 16.7032 | 16.7852 | 17.3062 | 17.9062 | 15.964 | 16.8426 | 15.9452 | 16.8837 | 17.8746 | 44.3568 | 47.5739 | 43.4672 | 21.3454 |  |  | 0.39121 | -0.18275 | -42.8139 | 0.37517 | 0.24326 | -197.8499 | 13.0243 | -0.56942 | -0.092536 | 0.068506 | -0.065503 | 8.8287 | 9.0585 | 1.9781 | 21.7819 | 22.0109 | 22.2081 | 22.2697 | 22.1003 | 21.4272 | 20.2452 | 22.2014 | 22.3721 | 22.4106 | 22.3549 | 21.9916 | 21.2256 | 22.2769 | 17.3162 | 17.2073 | 16.2153 | 16.2882 | 16.3053 | 17.0718 | 16.8418 | 22.3811 | 22.1401 | 21.7088 | 22.0823 | 21.7976 | 21.302 | 21.9439 | 21.5308 | 20.9092 | 20.1073 | 20.274 | 19.8318 | 19.7629 | -0.017092 | 0.0089704 | 20.7064 | 22.0748 | 22.3833 | 20.094 | 21.6744 | 22.1282 | 21.9496 | 21.711 | 21.2845 | 21.7921 | 21.4544 | 21.0486 | 20.2367 | 20.2773 | 20.2196 | 20.2044 | 20.0873 |  | 20.2344 | 19.6846 | 20.1203 | 19.7215 | 20.0928 | 20.3275 |  | 20.4343 |  |  | 20.2496 | 20.3777 | 20.6186 | [5 empty] | 21.9458 | 20.334 | 21.6762 | 22.0601 | 19.5423 | 21.1874 | 21.8079 | 19.3536 | 19.9126 | 21.1289 |  | 19.7362 | 20.9129 | 18.9049 | 19.7272 | 20.8062 | 19.4856 | 20.0105 | 19.0658 | 20.1408 | 19.1441 | 20.2228 | 18.8887 | 20.0591 | 21.0528 | 19.4205 | 19.8157 | 20.9757 | 18.9342 | 19.8053 | 20.7955 | 18.9925 | 20.128 | 19.2934 | 19.892 | 18.9168 | 20.106 | 0.044758 | 20.9471 | 0.048843 | 0.016095 | -26.9705 | 3.0975 | -8.44 | -0.13 | 0.74678 | -0.50726 | -7.7642 | 0.72681 | 0.5858 | -16.7061 | 4.2863 | 0.42416 | 0.43153 | 0.42958 | 0.3751 | 0.47059 | 0.44281 | 0.42892
42838.4166 | -318 | 22.8937 | 22.8615 | 22.8479 | 22.776 | 22.406 | 21.7405 | 22.7176 | 21.8104 | 22.3652 | 22.3806 | 22.3604 | 22.0402 | 21.2559 | 22.2214 | 21.5719 | 21.7442 | 21.8776 | 21.0718 | 21.1684 | 21.3858 | 20.4635 | 20.6157 | 20.9036 | 21.8757 | 21.6511 | 21.2799 | 20.2833 | 20.3698 | 20.3701 | 22.0441 | 21.6526 | 21.1856 | 21.9833 | 21.7293 | 21.3463 | 19.9163 | 20.4047 |  | 20.5302 | 20.0743 | 20.1782 | 19.0524 |  | 16.7297 | 16.7755 | 16.4936 | 16.718 | 16.8094 | 17.3276 | 17.9225 | 15.9274 | 16.8399 | 15.9966 | 16.8899 | 17.8775 | 44.337 | 47.5789 | 43.4688 | 21.3439 |  |  | 0.49044 | -0.10061 | -43.2824 | 0.45665 | 0.27678 | -197.819 | 12.6169 | -0.45377 | -0.13087 | 0.045638 | -0.036338 | 8.8291 | 9.0589 | 1.9792 | 21.7822 | 22.0079 | 22.1985 | 22.2637 | 22.0924 | 21.4185 | 20.2361 | 22.1937 | 22.3707 | 22.4062 | 22.3475 | 21.9876 | 21.2241 | 22.2728 | 17.3058 | 17.2228 | 16.209 | 16.2795 | 16.3169 | 17.0768 | 16.8467 | 22.3847 | 22.15 | 21.7072 | 22.0796 | 21.7989 | 21.307 | 21.9401 | 21.5217 | 20.9093 | 20.1108 | 20.2719 | 19.8345 | 19.7698 | 0.038742 | 0.097984 | 20.705 | 22.0727 | 22.3786 | 20.0937 | 21.6716 | 22.1234 | 21.9526 | 21.7077 | 21.2776 | 21.7914 | 21.4465 | 21.0563 | 20.2349 | 20.2735 | 20.2171 | 20.2026 | 20.0992 |  | 20.2366 | 19.6873 | 20.1198 | 19.7265 | 20.096 | 20.3263 |  | 20.4313 |  |  | 20.2433 | 20.3732 | 20.6217 | [5 empty] | 21.9448 | 20.3335 | 21.6684 | 22.0544 | 19.5355 | 21.1789 | 21.8013 | 19.3516 | 19.9061 | 21.1188 |  | 19.7295 | 20.9181 | 18.9029 | 19.7304 | 20.8034 | 19.4774 | 20.0013 | 19.0613 | 20.1289 | 19.131 | 20.2166 | 18.8789 | 20.0546 | 21.0592 | 19.4211 | 19.8125 | 20.9729 | 18.9333 | 19.8095 | 20.7909 | 18.9896 | 20.1314 | 19.2907 | 19.882 | 18.916 | 20.1155 | -0.054298 | 20.9475 | 0.048942 | 0.016081 | -27.1589 | 3.0975 | 17.76 | -0.03 | 0.83614 | -0.37637 | -7.8067 | 0.80187 | 0.62487 | -16.7054 | 4.2189 | 0.42391 | 0.43144 | 0.42955 | 0.37684 | 0.47186 | 0.44226 | 0.42885
42838.4166 | -317 | 22.889 | 22.8541 | 22.8437 | 22.7623 | 22.4022 | 21.7416 | 22.7063 | 21.8042 | 22.3641 | 22.3746 | 22.35 | 22.0317 | 21.254 | 22.216 | 21.5698 | 21.748 | 21.8838 | 21.0697 | 21.1634 | 21.3863 | 20.4615 | 20.6136 | 20.9112 | 21.8821 | 21.6459 | 21.2838 | 20.2902 | 20.3654 | 20.3824 | 22.0337 | 21.6443 | 21.1821 | 21.9869 | 21.7195 | 21.3442 | 19.9142 | 20.4062 |  | 20.525 | 20.0659 | 20.1748 | 19.0617 |  | 16.7359 | 16.7793 | 16.5011 | 16.7383 | 16.8431 | 17.3563 | 17.9207 | 15.8852 | 16.8375 | 16.102 | 16.8882 | 17.8782 | 44.3236 | 47.5686 | 43.4632 | 21.3453 |  |  | 0.50292 | -0.25437 | -43.8528 | 0.43497 | 0.076356 | -197.8532 | 12.4414 | -0.35915 | -0.28344 | -0.095977 | 0.036226 | 8.8277 | 9.0574 | 1.9792 | 21.7817 | 22.005 | 22.2005 | 22.2694 | 22.0948 | 21.4264 | 20.2425 | 22.2046 | 22.3728 | 22.4077 | 22.3573 | 21.9915 | 21.2263 | 22.2833 | 17.2912 | 17.226 | 16.2104 | 16.2658 | 16.3205 | 17.0728 | 16.8508 | 22.3825 | 22.1529 | 21.7101 | 22.0793 | 21.811 | 21.3049 | 21.9379 | 21.5291 | 20.9118 | 20.1146 | 20.2794 | 19.8343 | 19.777 | 0.05683 | 0.11168 | 20.7088 | 22.0797 | 22.3824 | 20.0936 | 21.6783 | 22.1221 | 21.959 | 21.7081 | 21.2946 | 21.7906 | 21.4525 | 21.052 | 20.2339 | 20.275 | 20.2243 | 20.2073 | 20.1049 |  | 20.2223 | 19.7032 | 20.121 | 19.7208 | 20.0991 | 20.3191 |  | 20.4328 |  |  | 20.2549 | 20.3899 | 20.6313 | [5 empty] | 21.9555 | 20.3473 | 21.6872 | 22.0726 | 19.5477 | 21.1919 | 21.8148 | 19.3552 | 19.9129 | 21.1316 |  | 19.731 | 20.9115 | 18.9072 | 19.7416 | 20.8096 | 19.4885 | 20.0128 | 19.0657 | 20.1307 | 19.1311 | 20.2289 | 18.8763 | 20.0624 | 21.0521 | 19.423 | 19.8153 | 20.9771 | 18.9399 | 19.8104 | 20.8046 | 18.9905 | 20.1387 | 19.2899 | 19.8821 | 18.9248 | 20.1101 | -0.0159 | 20.9477 | 0.048868 | 0.016364 | -27.1069 | 3.0976 | -3.15 | -0.05 | 0.84673 | -0.59847 | -7.858 | 0.7826 | 0.32822 | -16.7077 | 4.1897 | 0.42327 | 0.43104 | 0.42981 | 0.37799 | 0.47219 | 0.44193 | 0.42877
42838.4166 | -316 | 22.8905 | 22.8604 | 22.8487 | 22.7702 | 22.405 | 21.7441 | 22.7087 | 21.8081 | 22.3644 | 22.3775 | 22.3573 | 22.0379 | 21.261 | 22.2188 | 21.5853 | 21.7502 | 21.8776 | 21.0674 | 21.1708 | 21.3888 | 20.4696 | 20.6177 | 20.9082 | 21.8821 | 21.6499 | 21.2876 | 20.2851 | 20.3694 | 20.3746 | 22.037 | 21.6413 | 21.1797 | 21.9824 | 21.7201 | 21.3464 | 19.914 | 20.4124 |  | 20.5263 | 20.0614 | 20.1776 | 19.0735 |  | 16.7234 | 16.7596 | 16.514 | 16.7675 | 16.8375 | 17.3452 | 17.904 | 15.8784 | 16.8351 | 16.1486 | 16.8899 | 17.8785 | 44.3257 | 47.5749 | 43.4698 | 21.3414 |  |  | 0.47007 | -0.23071 | -44.0124 | 0.6551 | 0.028388 | -197.8184 | 12.5696 | -0.41106 | -0.37957 | -0.2827 | -0.087898 | 8.829 | 9.0588 | 1.979 | 21.7735 | 22.0004 | 22.1936 | 22.2633 | 22.0889 | 21.4174 | 20.2369 | 22.1959 | 22.3679 | 22.4025 | 22.3615 | 21.9868 | 21.224 | 22.2699 | 17.2922 | 17.1923 | 16.2135 | 16.2568 | 16.3057 | 17.0696 | 16.861 | 22.3799 | 22.1573 | 21.714 | 22.0896 | 21.8044 | 21.3097 | 21.9473 | 21.5344 | 20.9158 | 20.1177 | 20.2836 | 19.8377 | 19.7739 | -0.13957 | 0.1482 | 20.7152 | 22.0704 | 22.3841 | 20.0897 | 21.6813 | 22.1239 | 21.954 | 21.719 | 21.2917 | 21.7933 | 21.4482 | 21.0492 | 20.2368 | 20.2828 | 20.2287 | 20.2117 | 20.1152 |  | 20.2294 | 19.7199 | 20.1272 | 19.7269 | 20.1039 | 20.3229 |  | 20.4328 |  |  | 20.2359 | 20.3826 | 20.6318 | [5 empty] | 21.9427 | 20.3294 | 21.6832 | 22.0643 | 19.538 | 21.1871 | 21.8063 | 19.3764 | 19.9135 | 21.1448 |  | 19.7334 | 20.9344 | 18.9102 | 19.7335 | 20.8174 | 19.4874 | 20.0194 | 19.0802 | 20.1433 | 19.1355 | 20.2251 | 18.8714 | 20.0471 | 21.0495 | 19.4245 | 19.8177 | 20.971 | 18.934 | 19.8117 | 20.7951 | 18.9764 | 20.1356 | 19.3012 | 19.889 | 18.9214 | 20.1076 | -0.089914 | 20.9474 | 0.048585 | 0.015994 | -27.0432 | 3.0976 | -2.8 | -0.06 | 0.8186 | -0.56995 | -7.872 | 0.9604 | 0.20013 | -16.7059 | 4.2111 | 0.42322 | 0.43078 | 0.42981 | 0.37751 | 0.47303 | 0.44159 | 0.42896
42838.4166 | -315 | 22.8878 | 22.8624 | 22.8499 | 22.7745 | 22.4084 | 21.7434 | 22.7168 | 21.8125 | 22.3689 | 22.3764 | 22.3591 | 22.0342 | 21.2611 | 22.2185 | 21.5766 | 21.7461 | 21.8789 | 21.0674 | 21.1665 | 21.3859 | 20.471 | 20.6157 | 20.9057 | 21.8829 | 21.6528 | 21.2833 | 20.2854 | 20.3664 | 20.3676 | 22.0439 | 21.6529 | 21.1788 | 21.9841 | 21.7256 | 21.3481 | 19.9183 | 20.4103 |  | 20.5338 | 20.0645 | 20.1763 | 19.087 |  | 16.7295 | 16.7698 | 16.5382 | 16.7746 | 16.8291 | 17.3476 | 17.92 | 15.9248 | 16.8405 | 16.1481 | 16.8875 | 17.8803 | 44.3385 | 47.5749 | 43.4616 | 21.3423 |  |  | 0.43853 | -0.11769 | -44.3252 | 0.25755 | 0.29386 | -197.8217 | 12.4874 | -0.43012 | -0.18731 | -0.25228 | -0.079218 | 8.8293 | 9.0592 | 1.9786 | 21.7777 | 22.0167 | 22.1954 | 22.2688 | 22.0979 | 21.4261 | 20.241 | 22.2024 | 22.3721 | 22.4109 | 22.3618 | 21.9904 | 21.2257 | 22.271 | 17.3048 | 17.1696 | 16.2294 | 16.2821 | 16.2938 | 17.0803 | 16.8682 | 22.381 | 22.15 | 21.7127 | 22.0912 | 21.7988 | 21.309 | 21.9535 | 21.534 | 20.9081 | 20.1129 | 20.2843 | 19.8316 | 19.7561 | -0.089048 | 0.11929 | 20.7218 | 22.0776 | 22.3911 | 20.0933 | 21.6774 | 22.1246 | 21.9603 | 21.7196 | 21.2924 | 21.7889 | 21.4536 | 21.05 | 20.2455 | 20.2849 | 20.2225 | 20.2095 | 20.1134 |  | 20.2254 | 19.716 | 20.1172 | 19.7134 | 20.0953 | 20.3188 |  | 20.4336 |  |  | 20.2313 | 20.3844 | 20.6308 | [5 empty] | 21.9512 | 20.3335 | 21.6794 | 22.066 | 19.5401 | 21.1893 | 21.8153 | 19.3594 | 19.9006 | 21.1238 |  | 19.7215 | 20.9202 | 18.8975 | 19.7331 | 20.807 | 19.4896 | 20.0051 | 19.0635 | 20.135 | 19.1244 | 20.2118 | 18.8656 | 20.0606 | 21.0434 | 19.416 | 19.8089 | 20.973 | 18.9231 | 19.812 | 20.7875 | 18.9689 | 20.1271 | 19.2922 | 19.8777 | 18.9215 | 20.1054 | -0.14371 | 20.9474 | 0.048862 | 0.015275 | -26.9751 | 3.0975 | -18.23 | -0.16 | 0.79065 | -0.40707 | -7.9001 | 0.60219 | 0.64389 | -16.7061 | 4.1973 | 0.42314 | 0.43055 | 0.42989 | 0.37737 | 0.47211 | 0.44137 | 0.4293
42838.4166 | -314 | 22.8906 | 22.8601 | 22.8443 | 22.7744 | 22.4059 | 21.749 | 22.7194 | 21.8113 | 22.369 | 22.3746 | 22.3601 | 22.0331 | 21.2526 | 22.2218 | 21.5691 | 21.75 | 21.8836 | 21.0741 | 21.1702 | 21.3818 | 20.472 | 20.6184 | 20.9141 | 21.882 | 21.653 | 21.2926 | 20.2894 | 20.3694 | 20.3692 | 22.0435 | 21.6506 | 21.1779 | 21.9773 | 21.7309 | 21.3488 | 19.9122 | 20.409 |  | 20.5281 | 20.0643 | 20.1704 | 19.0878 |  | 16.7423 | 16.8059 | 16.5421 | 16.7758 | 16.8296 | 17.3412 | 17.9364 | 15.965 | 16.8409 | 16.125 | 16.89 | 17.8777 | 44.3554 | 47.5767 | 43.4656 | 21.342 |  |  | 0.59492 | -0.2616 | -44.776 | 0.38831 | 0.082928 | -197.8775 | 12.0288 | -0.37623 | -0.39884 | -9.86e-05 | -0.081474 | 8.8288 | 9.0585 | 1.9782 | 21.7772 | 22.0124 | 22.2007 | 22.2659 | 22.0926 | 21.425 | 20.2349 | 22.1919 | 22.3673 | 22.4004 | 22.3549 | 21.9883 | 21.2221 | 22.269 | 17.3029 | 17.1798 | 16.2597 | 16.293 | 16.2915 | 17.0786 | 16.8752 | 22.3911 | 22.1523 | 21.7158 | 22.0901 | 21.8112 | 21.3125 | 21.9559 | 21.5393 | 20.913 | 20.118 | 20.2909 | 19.843 | 19.7605 | -0.22627 | -0.018038 | 20.7127 | 22.0691 | 22.3806 | 20.0851 | 21.6688 | 22.116 | 21.9491 | 21.7049 | 21.2783 | 21.7876 | 21.444 | 21.0496 | 20.2424 | 20.267 | 20.2195 | 20.2064 | 20.1156 |  | 20.2257 | 19.7372 | 20.1158 | 19.7253 | 20.1013 | 20.3152 |  | 20.4249 |  |  | 20.2378 | 20.3793 | 20.6319 | [5 empty] | 21.9506 | 20.3369 | 21.684 | 22.0658 | 19.5369 | 21.1931 | 21.8092 | 19.3703 | 19.9076 | 21.132 |  | 19.7335 | 20.9303 | 18.898 | 19.7384 | 20.8107 | 19.4903 | 20.0145 | 19.0723 | 20.1413 | 19.1367 | 20.2219 | 18.8735 | 20.0546 | 21.0518 | 19.416 | 19.8124 | 20.9733 | 18.9231 | 19.8117 | 20.8 | 18.9731 | 20.1345 | 19.2888 | 19.8813 | 18.9256 | 20.107 | -0.024433 | 20.9481 | 0.048954 | 0.016161 | -27.1287 | 3.0976 | -8.43 | -0.09 | 0.92091 | -0.60695 | -7.9406 | 0.73947 | 0.34205 | -16.7083 | 4.1195 | 0.42309 | 0.42992 | 0.42976 | 0.37738 | 0.46955 | 0.44114 | 0.42934
42838.4167 | -313 | 22.8845 | 22.8468 | 22.8454 | 22.7699 | 22.4079 | 21.743 | 22.7151 | 21.8067 | 22.3668 | 22.3703 | 22.3602 | 22.036 | 21.2527 | 22.2225 | 21.5709 | 21.751 | 21.8789 | 21.0717 | 21.1688 | 21.3935 | 20.4739 | 20.6152 | 20.9046 | 21.8866 | 21.6463 | 21.2842 | 20.2781 | 20.3638 | 20.3658 | 22.0508 | 21.66 | 21.1848 | 21.995 | 21.7354 | 21.3577 | 19.9252 | 20.4205 |  | 20.5354 | 20.0667 | 20.1814 | 19.1024 |  | 16.7573 | 16.7934 | 16.5347 | 16.7649 | 16.817 | 17.3306 | 17.9317 | 15.9702 | 16.8399 | 16.0797 | 16.8851 | 17.8722 | 44.3676 | 47.5721 | 43.4691 | 21.3373 |  |  | 0.55418 | -0.37331 | -45.4141 | 0.48228 | 0.31883 | -197.8368 | 11.8941 | -0.34666 | -0.10207 | -0.1285 | 0.0035896 | 8.8274 | 9.0572 | 1.9794 | 21.7825 | 22.0099 | 22.2046 | 22.2694 | 22.0932 | 21.4169 | 20.2379 | 22.1912 | 22.3708 | 22.4014 | 22.3583 | 21.9903 | 21.2219 | 22.2672 | 17.3154 | 17.1773 | 16.3024 | 16.288 | 16.2946 | 17.0803 | 16.8729 | 22.3765 | 22.1404 | 21.7088 | 22.0767 | 21.7974 | 21.3054 | 21.9423 | 21.5315 | 20.9099 | 20.1088 | 20.2763 | 19.8293 | 19.7396 | -0.12129 | 0.11986 | 20.7126 | 22.0687 | 22.3792 | 20.0825 | 21.6781 | 22.1263 | 21.9562 | 21.7117 | 21.2812 | 21.788 | 21.4554 | 21.0482 | 20.238 | 20.2728 | 20.2262 | 20.208 | 20.1281 |  | 20.2232 | 19.7541 | 20.1076 | 19.7303 | 20.0975 | 20.317 |  | 20.4285 |  |  | 20.2352 | 20.3682 | 20.6258 | [5 empty] | 21.9535 | 20.3405 | 21.6866 | 22.0643 | 19.537 | 21.1923 | 21.8149 | 19.3628 | 19.9137 | 21.13 |  | 19.7237 | 20.9184 | 18.8889 | 19.7334 | 20.814 | 19.481 | 20.0177 | 19.0712 | 20.1292 | 19.1294 | 20.2145 | 18.8773 | 20.0552 | 21.0486 | 19.4163 | 19.8118 | 20.9759 | 18.9208 | 19.8097 | 20.8014 | 18.9635 | 20.136 | 19.2833 | 19.8809 | 18.92 | 20.1021 | -0.047621 | 20.9472 | 0.04936 | 0.016487 | -27.0764 | 3.0976 | 19.08 | 0.02 | 0.88881 | -0.72503 | -7.9968 | 0.82409 | 0.67067 | -16.7063 | 4.0963 | 0.42266 | 0.42917 | 0.4295 | 0.37618 | 0.46454 | 0.44116 | 0.42962
42838.4167 | -312 | 22.8832 | 22.8543 | 22.8433 | 22.7649 | 22.4006 | 21.7429 | 22.7053 | 21.8089 | 22.3633 | 22.368 | 22.3594 | 22.0275 | 21.2506 | 22.2225 | 21.565 | 21.7416 | 21.8761 | 21.0748 | 21.1695 | 21.3883 | 20.4677 | 20.6072 | 20.9066 | 21.8889 | 21.6465 | 21.2876 | 20.2802 | 20.3638 | 20.3661 | 22.0389 | 21.6467 | 21.1712 | 21.9832 | 21.7139 | 21.3442 | 19.9113 | 20.411 |  | 20.5273 | 20.0596 | 20.1697 | 19.1032 |  | 16.7607 | 16.8028 | 16.536 | 16.7659 | 16.8155 | 17.3224 | 17.926 | 16.036 | 16.8468 | 16.0601 | 16.8959 | 17.8766 | 44.3883 | 47.5751 | 43.4917 | 21.3426 |  |  | 0.58441 | -0.096005 | -46.0856 | 0.51119 | 0.17558 | -197.8769 | 11.9223 | -0.47546 | 0.13631 | -0.054017 | -0.041546 | 8.8284 | 9.058 | 1.9794 | 21.7851 | 22.0078 | 22.2068 | 22.2657 | 22.0954 | 21.4228 | 20.2378 | 22.1963 | 22.376 | 22.408 | 22.3659 | 21.9912 | 21.2214 | 22.2704 | 17.3317 | 17.2058 | 16.3445 | 16.2809 | 16.2919 | 17.0745 | 16.8757 | 22.38 | 22.1517 | 21.7126 | 22.0853 | 21.8016 | 21.3087 | 21.9485 | 21.5263 | 20.9163 | 20.11 | 20.2949 | 19.8315 | 19.7435 | -0.097305 | -0.15898 | 20.7205 | 22.0804 | 22.3809 | 20.0881 | 21.6814 | 22.1294 | 21.955 | 21.723 | 21.29 | 21.7946 | 21.4608 | 21.0564 | 20.2477 | 20.2789 | 20.2273 | 20.2112 | 20.1375 |  | 20.2231 | 19.7651 | 20.115 | 19.7327 | 20.1004 | 20.327 |  | 20.427 |  |  | 20.2389 | 20.3642 | 20.6193 | [5 empty] | 21.944 | 20.3323 | 21.6789 | 22.0604 | 19.5354 | 21.185 | 21.806 | 19.364 | 19.9103 | 21.1278 |  | 19.7238 | 20.9172 | 18.894 | 19.732 | 20.807 | 19.4877 | 20.015 | 19.0709 | 20.1293 | 19.1204 | 20.2155 | 18.8689 | 20.0497 | 21.0443 | 19.4049 | 19.7995 | 20.9658 | 18.9126 | 19.7955 | 20.7842 | 18.9573 | 20.1277 | 19.2765 | 19.8752 | 18.9047 | 20.0935 | -0.12163 | 20.9473 | 0.049298 | 0.015987 | -27.0694 | 3.0975 | -3.57 | -0.07 | 0.91273 | -0.36769 | -8.0559 | 0.84844 | 0.49769 | -16.7077 | 4.1011 | 0.42239 | 0.42911 | 0.42953 | 0.3737 | 0.4602 | 0.44068 | 0.42955
42838.4167 | -311 | 22.8871 | 22.8547 | 22.8447 | 22.7687 | 22.4077 | 21.7444 | 22.7116 | 21.8095 | 22.3632 | 22.3726 | 22.3565 | 22.0306 | 21.2577 | 22.2179 | 21.5764 | 21.7515 | 21.8867 | 21.0862 | 21.1696 | 21.3959 | 20.471 | 20.6149 | 20.9097 | 21.8997 | 21.6488 | 21.2919 | 20.2941 | 20.3685 | 20.3749 | 22.0468 | 21.6522 | 21.1724 | 21.98 | 21.7227 | 21.3504 | 19.9135 | 20.4171 |  | 20.5271 | 20.061 | 20.174 | 19.1163 |  | 16.7686 | 16.7977 | 16.5382 | 16.7681 | 16.81 | 17.3182 | 17.9302 | 16.125 | 16.8361 | 16.0564 | 16.8784 | 17.8725 | 44.4137 | 47.5665 | 43.4974 | 21.3356 |  |  | 0.47138 | -0.24254 | -46.2677 | 0.48688 | 0.037588 | -197.8302 | 11.8573 | -0.51094 | 0.1799 | -0.098914 | -0.095883 | 8.8299 | 9.0598 | 1.979 | 21.7835 | 22.0011 | 22.1958 | 22.2586 | 22.0923 | 21.4186 | 20.2329 | 22.189 | 22.3787 | 22.4076 | 22.3515 | 21.9858 | 21.2205 | 22.2685 | 17.3433 | 17.2169 | 16.3617 | 16.2748 | 16.2845 | 17.0773 | 16.8767 | 22.3779 | 22.152 | 21.7074 | 22.0839 | 21.7967 | 21.31 | 21.9439 | 21.524 | 20.9082 | 20.1038 | 20.2903 | 19.8359 | 19.7338 | -0.075286 | 0.12176 | 20.7296 | 22.0746 | 22.3751 | 20.0893 | 21.6715 | 22.1193 | 21.9587 | 21.7207 | 21.2874 | 21.7938 | 21.4581 | 21.0531 | 20.2518 | 20.2728 | 20.2276 | 20.2117 | 20.1363 |  | 20.2222 | 19.7933 | 20.1197 | 19.7431 | 20.0958 | 20.3171 |  | 20.4263 |  |  | 20.2443 | 20.3692 | 20.6166 | [5 empty] | 21.9452 | 20.3302 | 21.674 | 22.0602 | 19.5349 | 21.1777 | 21.8029 | 19.3685 | 19.9147 | 21.1276 |  | 19.7297 | 20.9184 | 18.8817 | 19.7315 | 20.807 | 19.4877 | 20.016 | 19.0721 | 20.1246 | 19.1198 | 20.213 | 18.8714 | 20.0583 | 21.0441 | 19.4139 | 19.8079 | 20.9691 | 18.917 | 19.8039 | 20.798 | 18.9549 | 20.1299 | 19.2795 | 19.8784 | 18.9084 | 20.0946 | -0.082494 | 20.9476 | 0.049089 | 0.016596 | -27.0878 | 3.0975 | -4.98 | -0.08 | 0.81974 | -0.58441 | -8.0717 | 0.82801 | 0.23027 | -16.7056 | 4.0899 | 0.4224 | 0.42849 | 0.42908 | 0.37273 | 0.4584 | 0.44039 | 0.42961
42838.4167 | -310 | 22.8845 | 22.854 | 22.8453 | 22.7679 | 22.4071 | 21.7425 | 22.7119 | 21.8041 | 22.3622 | 22.374 | 22.3553 | 22.029 | 21.2588 | 22.217 | 21.578 | 21.7553 | 21.8851 | 21.0823 | 21.1715 | 21.3934 | 20.4737 | 20.6164 | 20.9062 | 21.8911 | 21.6521 | 21.2908 | 20.2892 | 20.3663 | 20.3714 | 22.0459 | 21.652 | 21.1706 | 21.9908 | 21.7338 | 21.3474 | 19.9155 | 20.4139 |  | 20.5241 | 20.064 | 20.1735 | 19.1215 |  | 16.7668 | 16.7928 | 16.5351 | 16.764 | 16.8186 | 17.335 | 17.9394 | 16.1699 | 16.8345 | 16.038 | 16.8796 | 17.8722 | 44.4249 | 47.5653 | 43.5081 | 21.3365 |  |  | 0.4175 | -0.19851 | -46.4418 | 0.49411 | 0.19135 | -197.8355 | 11.8382 | -0.53065 | 0.099923 | -0.11066 | -0.045018 | 8.828 | 9.0578 | 1.9788 | 21.7849 | 22.0097 | 22.2073 | 22.2682 | 22.0988 | 21.4213 | 20.2375 | 22.2017 | 22.3741 | 22.4109 | 22.3621 | 21.9977 | 21.233 | 22.2726 | 17.3633 | 17.1617 | 16.3694 | 16.2862 | 16.2816 | 17.0769 | 16.8719 | 22.38 | 22.1535 | 21.7033 | 22.0806 | 21.7969 | 21.3032 | 21.9415 | 21.5311 | 20.9076 | 20.1062 | 20.294 | 19.8358 | 19.7329 | -0.23787 | 0.043397 | 20.7328 | 22.0728 | 22.3782 | 20.0915 | 21.6725 | 22.1174 | 21.9605 | 21.7219 | 21.2873 | 21.7965 | 21.4623 | 21.0569 | 20.2469 | 20.263 | 20.2243 | 20.2134 | 20.1375 |  | 20.224 | 19.8072 | 20.1154 | 19.7465 | 20.0905 | 20.3114 |  | 20.4316 |  |  | 20.2499 | 20.3766 | 20.6205 | [5 empty] | 21.9454 | 20.3271 | 21.6745 | 22.0623 | 19.541 | 21.1774 | 21.8051 | 19.3733 | 19.9237 | 21.1328 |  | 19.7296 | 20.9227 | 18.8857 | 19.7382 | 20.8165 | 19.4928 | 20.0214 | 19.0729 | 20.1242 | 19.1235 | 20.2155 | 18.8674 | 20.0644 | 21.0427 | 19.4216 | 19.8054 | 20.9737 | 18.9223 | 19.8177 | 20.8005 | 18.9616 | 20.135 | 19.2798 | 19.8766 | 18.9097 | 20.0991 | -0.026288 | 20.9476 | 0.049304 | 0.016669 | -27.0583 | 3.0975 | -0.22 | -0.12 | 0.77146 | -0.52871 | -8.0868 | 0.83413 | 0.51957 | -16.7063 | 4.0867 | 0.42242 | 0.42796 | 0.42881 | 0.37046 | 0.45698 | 0.44031 | 0.42971
42838.4167 | -309 | 22.8863 | 22.8527 | 22.8436 | 22.768 | 22.3994 | 21.7434 | 22.7063 | 21.8017 | 22.364 | 22.3695 | 22.3557 | 22.0284 | 21.2533 | 22.2114 | 21.5827 | 21.752 | 21.8828 | 21.0772 | 21.1789 | 21.3926 | 20.4716 | 20.6142 | 20.9046 | 21.8905 | 21.6519 | 21.2879 | 20.2874 | 20.3611 | 20.3748 | 22.0464 | 21.6494 | 21.1715 | 21.9896 | 21.7289 | 21.3498 | 19.9195 | 20.4143 |  | 20.5176 | 20.063 | 20.1637 | 19.1169 |  | 16.7726 | 16.7973 | 16.5516 | 16.7701 | 16.8271 | 17.3498 | 17.9416 | 16.1865 | 16.8483 | 16.007 | 16.8832 | 17.8784 | 44.4376 | 47.5713 | 43.5151 | 21.3439 |  |  | 0.48715 | -0.10849 | -46.7842 | 0.62159 | 0.16638 | -197.7921 | 11.6122 | -0.47414 | 0.052441 | -0.13269 | -0.000924 | 8.8287 | 9.0585 | 1.9786 | 21.7812 | 22.0052 | 22.1929 | 22.2583 | 22.1021 | 21.4181 | 20.2413 | 22.2013 | 22.3654 | 22.3999 | 22.354 | 21.981 | 21.2283 | 22.2687 | 17.3964 | 17.1794 | 16.4108 | 16.2949 | 16.2794 | 17.0791 | 16.8789 | 22.3808 | 22.1512 | 21.7035 | 22.0909 | 21.8067 | 21.306 | 21.9382 | 21.5323 | 20.9075 | 20.1125 | 20.2906 | 19.8388 | 19.7362 | -0.15176 | 0.20944 | 20.7324 | 22.0741 | 22.3848 | 20.0984 | 21.6772 | 22.1346 | 21.9605 | 21.7333 | 21.2942 | 21.8017 | 21.4609 | 21.0585 | 20.2497 | 20.2803 | 20.2321 | 20.2201 | 20.1372 |  | 20.2156 | 19.8205 | 20.1121 | 19.7479 | 20.0883 | 20.3121 |  | 20.4262 |  |  | 20.2567 | 20.378 | 20.6212 | [5 empty] | 21.95 | 20.3307 | 21.6775 | 22.0708 | 19.551 | 21.1798 | 21.8099 | 19.3735 | 19.9224 | 21.137 |  | 19.7369 | 20.9232 | 18.8898 | 19.7317 | 20.8168 | 19.496 | 20.026 | 19.0799 | 20.1281 | 19.1226 | 20.2217 | 18.8608 | 20.0633 | 21.0459 | 19.4175 | 19.7975 | 20.9713 | 18.919 | 19.8154 | 20.8034 | 18.9685 | 20.1329 | 19.2782 | 19.8719 | 18.9049 | 20.0999 | -0.027401 | 20.9467 | 0.049249 | 0.016996 | -27.0206 | 3.0974 | -6.73 | -0.06 | 0.83334 | -0.39086 | -8.1166 | 0.93557 | 0.4845 | -16.7049 | 4.0476 | 0.42215 | 0.42748 | 0.4287 | 0.36704 | 0.4532 | 0.44057 | 0.42983
42838.4167 | -308 | 22.8886 | 22.8584 | 22.8514 | 22.7762 | 22.4083 | 21.7458 | 22.7113 | 21.8087 | 22.3645 | 22.3755 | 22.3604 | 22.0344 | 21.2508 | 22.2235 | 21.5766 | 21.7454 | 21.8851 | 21.0775 | 21.1777 | 21.3878 | 20.4667 | 20.6109 | 20.9059 | 21.8847 | 21.6433 | 21.2858 | 20.2871 | 20.3658 | 20.3694 | 22.0453 | 21.6554 | 21.1718 | 21.9806 | 21.7273 | 21.3493 | 19.919 | 20.4137 |  | 20.527 | 20.0617 | 20.1717 | 19.1129 |  | 16.7659 | 16.7911 | 16.5326 | 16.7539 | 16.8087 | 17.344 | 17.9528 | 16.1542 | 16.837 | 15.9732 | 16.8808 | 17.8714 | 44.4384 | 47.5649 | 43.5125 | 21.3297 |  |  | 0.39976 | -0.14792 | -47.0575 | 0.44219 | -0.037324 | -197.8092 | 11.7324 | -0.49451 | 0.11646 | -0.051919 | 0.06487 | 8.83 | 9.0597 | 1.9791 | 21.7753 | 22.0038 | 22.2036 | 22.2617 | 22.0931 | 21.414 | 20.2251 | 22.1946 | 22.3658 | 22.4085 | 22.3585 | 21.9805 | 21.214 | 22.2676 | 17.4405 | 17.2007 | 16.435 | 16.2848 | 16.2862 | 17.0783 | 16.8791 | 22.3828 | 22.1544 | 21.7167 | 22.0877 | 21.8137 | 21.308 | 21.9483 | 21.5353 | 20.9128 | 20.1169 | 20.2957 | 19.8452 | 19.7312 | 0.0017816 | 0.17578 | 20.7293 | 22.0749 | 22.3865 | 20.0968 | 21.6787 | 22.1328 | 21.9567 | 21.7289 | 21.2928 | 21.7989 | 21.4606 | 21.0565 | 20.2513 | 20.2834 | 20.2335 | 20.2191 | 20.1286 |  | 20.2146 | 19.8446 | 20.109 | 19.7502 | 20.0927 | 20.3166 |  | 20.4178 |  |  | 20.2512 | 20.3794 | 20.6172 | [5 empty] | 21.9483 | 20.3353 | 21.6819 | 22.0689 | 19.5425 | 21.1837 | 21.8085 | 19.3721 | 19.9156 | 21.1362 |  | 19.7404 | 20.9158 | 18.8841 | 19.7301 | 20.8159 | 19.4903 | 20.0233 | 19.0804 | 20.1346 | 19.1173 | 20.217 | 18.8674 | 20.0665 | 21.0527 | 19.4149 | 19.798 | 20.9709 | 18.9163 | 19.8183 | 20.8052 | 18.9646 | 20.1342 | 19.2763 | 19.8739 | 18.9106 | 20.1016 | -0.072663 | 20.9478 | 0.049464 | 0.017155 | -27.0945 | 3.0975 | -6.38 | -0.12 | 0.75489 | -0.45638 | -8.1402 | 0.78909 | -0.22947 | -16.7055 | 4.0685 | 0.42235 | 0.42671 | 0.42878 | 0.36204 | 0.45053 | 0.44067 | 0.43012
42838.4167 | -307 | 22.8991 | 22.858 | 22.851 | 22.7787 | 22.409 | 21.7438 | 22.7154 | 21.8152 | 22.3753 | 22.3762 | 22.3617 | 22.0321 | 21.2525 | 22.2255 | 21.5785 | 21.7514 | 21.8916 | 21.0776 | 21.1794 | 21.3917 | 20.4709 | 20.6164 | 20.9165 | 21.8897 | 21.6467 | 21.2903 | 20.2901 | 20.371 | 20.372 | 22.0546 | 21.6536 | 21.1727 | 21.9856 | 21.7321 | 21.3537 | 19.9164 | 20.4171 |  | 20.5171 | 20.0546 | 20.1645 | 19.1173 |  | 16.7796 | 16.7882 | 16.5349 | 16.7581 | 16.8081 | 17.3353 | 17.9553 | 16.1079 | 16.8458 | 15.9896 | 16.8892 | 17.8794 | 44.4694 | 47.5704 | 43.5085 | 21.3412 |  |  | 0.50029 | -0.24517 | -46.9629 | 0.73001 | 0.1861 | -197.8578 | 11.3316 | -0.30329 | 0.11588 | -0.012477 | 0.041434 | 8.8289 | 9.0586 | 1.9794 | 21.7833 | 22.0096 | 22.2022 | 22.2635 | 22.0964 | 21.4184 | 20.2294 | 22.1966 | 22.3764 | 22.4059 | 22.3523 | 21.9863 | 21.2187 | 22.2661 | 17.4705 | 17.1397 | 16.4625 | 16.2887 | 16.291 | 17.0719 | 16.8708 | 22.3837 | 22.1475 | 21.708 | 22.0847 | 21.8057 | 21.3081 | 21.9477 | 21.5343 | 20.9126 | 20.1119 | 20.2984 | 19.8384 | 19.7271 | -0.085705 | 0.15619 | 20.732 | 22.0829 | 22.3873 | 20.0962 | 21.6828 | 22.1284 | 21.9565 | 21.7246 | 21.2881 | 21.794 | 21.457 | 21.0534 | 20.2385 | 20.2924 | 20.2322 | 20.2093 | 20.146 |  | 20.2295 | 19.8703 | 20.1201 | 19.766 | 20.1116 | 20.3235 |  | 20.4313 |  |  | 20.2505 | 20.385 | 20.6145 | [5 empty] | 21.9433 | 20.3307 | 21.676 | 22.0613 | 19.5379 | 21.1882 | 21.7986 | 19.3676 | 19.9139 | 21.1343 |  | 19.7353 | 20.9118 | 18.8818 | 19.7301 | 20.8114 | 19.4876 | 20.0169 | 19.069 | 20.1295 | 19.1224 | 20.2081 | 18.8702 | 20.0613 | 21.0453 | 19.4059 | 19.7963 | 20.9692 | 18.9225 | 19.8149 | 20.7983 | 18.9641 | 20.1329 | 19.2773 | 19.876 | 18.9087 | 20.0989 | -0.085462 | 20.9472 | 0.049587 | 0.017119 | -27.1019 | 3.0975 | -3.08 | -0.16 | 0.8445 | -0.58756 | -8.132 | 1.0139 | 0.51239 | -16.7073 | 3.9983 | 0.42237 | 0.42636 | 0.42898 | 0.35796 | 0.44651 | 0.44046 | 0.43007
42838.4167 | -306 | 22.8903 | 22.8544 | 22.8414 | 22.771 | 22.4023 | 21.7525 | 22.7065 | 21.8049 | 22.3666 | 22.3745 | 22.3572 | 22.0332 | 21.2527 | 22.2155 | 21.5779 | 21.7406 | 21.8717 | 21.0599 | 21.1654 | 21.3811 | 20.4649 | 20.5981 | 20.9022 | 21.8797 | 21.646 | 21.2754 | 20.2809 | 20.3635 | 20.3687 | 22.0504 | 21.6518 | 21.1794 | 21.9938 | 21.736 | 21.3557 | 19.9176 | 20.4195 |  | 20.5238 | 20.0512 | 20.1675 | 19.12 |  | 16.7674 | 16.7866 | 16.533 | 16.7444 | 16.7997 | 17.3153 | 17.9376 | 16.0914 | 16.8346 | 16.0052 | 16.8799 | 17.8809 | 44.474 | 47.5627 | 43.5104 | 21.3359 |  |  | 0.54432 | -0.28525 | -47.8217 | 0.76813 | 0.29978 | -197.8723 | 11.3881 | -0.27044 | -0.13982 | -0.085068 | -0.0014448 | 8.8283 | 9.058 | 1.9789 | 21.7859 | 22.0059 | 22.2028 | 22.266 | 22.0927 | 21.4223 | 20.2305 | 22.2026 | 22.3798 | 22.4132 | 22.3598 | 21.9936 | 21.2234 | 22.271 | 17.4984 | 17.175 | 16.4608 | 16.2995 | 16.302 | 17.0763 | 16.8729 | 22.3848 | 22.1516 | 21.7111 | 22.0834 | 21.8074 | 21.3144 | 21.9508 | 21.5361 | 20.9182 | 20.1146 | 20.2981 | 19.842 | 19.7306 | -0.076662 | 0.14629 | 20.7277 | 22.0731 | 22.3821 | 20.0952 | 21.6772 | 22.1273 | 21.9533 | 21.7173 | 21.2849 | 21.7882 | 21.4552 | 21.051 | 20.2398 | 20.2869 | 20.235 | 20.2097 | 20.1379 |  | 20.2321 | 19.8834 | 20.1144 | 19.7604 | 20.1125 | 20.3234 |  | 20.4267 |  |  | 20.2538 | 20.3876 | 20.6178 | [5 empty] | 21.9365 | 20.3297 | 21.6752 | 22.0584 | 19.5425 | 21.1812 | 21.801 | 19.3642 | 19.9078 | 21.1269 |  | 19.7342 | 20.9102 | 18.8791 | 19.7242 | 20.8048 | 19.4845 | 20.0122 | 19.0714 | 20.1237 | 19.1165 | 20.2131 | 18.8639 | 20.0586 | 21.039 | 19.4033 | 19.787 | 20.9632 | 18.9206 | 19.8075 | 20.7993 | 18.9617 | 20.1328 | 19.274 | 19.8766 | 18.9066 | 20.1017 | -0.062275 | 20.9472 | 0.049544 | 0.016335 | -26.988 | 3.0974 | 17.05 | 0 | 0.88087 | -0.63377 | -8.206 | 1.04 | 0.6503 | -16.7073 | 4.0081 | 0.42268 | 0.42581 | 0.42916 | 0.35537 | 0.44695 | 0.44042 | 0.43006
42838.4167 | -305 | 22.895 | 22.8568 | 22.853 | 22.7752 | 22.4102 | 21.7422 | 22.7168 | 21.8096 | 22.368 | 22.3858 | 22.3609 | 22.0325 | 21.2667 | 22.2247 | 21.5722 | 21.7417 | 21.8775 | 21.0651 | 21.1704 | 21.3832 | 20.4659 | 20.6082 | 20.902 | 21.8865 | 21.6472 | 21.2819 | 20.2846 | 20.3778 | 20.3791 | 22.0541 | 21.6613 | 21.1898 | 21.9972 | 21.7357 | 21.3536 | 19.926 | 20.4225 |  | 20.5252 | 20.06 | 20.1751 | 19.1412 |  | 16.7665 | 16.7816 | 16.5163 | 16.7316 | 16.7793 | 17.3026 | 17.9448 | 16.1002 | 16.8314 | 16.0092 | 16.8689 | 17.8829 | 44.4908 | 47.5609 | 43.5274 | 21.3459 |  |  | 0.56535 | -0.38514 | -48.3244 | 0.41065 | 0.26626 | -197.8519 | 10.7034 | -0.23824 | -0.22195 | 0.13963 | 0.079106 | 8.8299 | 9.0596 | 1.9786 | 21.7851 | 22.0103 | 22.2054 | 22.2607 | 22.0922 | 21.4175 | 20.2303 | 22.194 | 22.3722 | 22.4092 | 22.3622 | 21.991 | 21.2227 | 22.274 | 17.5276 | 17.2029 | 16.4864 | 16.3133 | 16.31 | 17.0748 | 16.8719 | 22.378 | 22.1524 | 21.7083 | 22.0833 | 21.8024 | 21.3096 | 21.9502 | 21.5303 | 20.9126 | 20.1122 | 20.2989 | 19.8393 | 19.7382 | 0.047786 | -0.042954 | 20.7329 | 22.0768 | 22.3871 | 20.0977 | 21.6813 | 22.1306 | 21.9555 | 21.7211 | 21.2889 | 21.792 | 21.4561 | 21.0529 | 20.2404 | 20.2804 | 20.239 | 20.2157 | 20.1293 |  | 20.2238 | 19.8955 | 20.117 | 19.7559 | 20.089 | 20.3269 |  | 20.4284 |  |  | 20.2666 | 20.3878 | 20.6322 | [5 empty] | 21.9509 | 20.3457 | 21.6795 | 22.0723 | 19.5514 | 21.1864 | 21.8119 | 19.3608 | 19.9105 | 21.1276 |  | 19.733 | 20.9153 | 18.8857 | 19.7282 | 20.8012 | 19.4885 | 20.0142 | 19.0782 | 20.1245 | 19.1199 | 20.2129 | 18.8703 | 20.0675 | 21.0398 | 19.4096 | 19.8 | 20.9702 | 18.925 | 19.8161 | 20.8005 | 18.9696 | 20.138 | 19.2809 | 19.8825 | 18.907 | 20.11 | -0.098447 | 20.9475 | 0.048813 | 0.015725 | -26.9518 | 3.0974 | -6.55 | -0.08 | 0.89774 | -0.73641 | -8.2489 | 0.76042 | 0.61286 | -16.7061 | 3.8857 | 0.42264 | 0.42556 | 0.4285 | 0.35197 | 0.44398 | 0.44012 | 0.42977
42838.4168 | -304 | 22.9059 | 22.8616 | 22.8509 | 22.7737 | 22.4078 | 21.7412 | 22.7188 | 21.815 | 22.3695 | 22.3814 | 22.3523 | 22.031 | 21.257 | 22.2239 | 21.5799 | 21.7442 | 21.878 | 21.07 | 21.1622 | 21.3858 | 20.4689 | 20.6076 | 20.9023 | 21.8943 | 21.6418 | 21.287 | 20.2895 | 20.3812 | 20.3734 | 22.0451 | 21.6594 | 21.1783 | 21.9879 | 21.7293 | 21.3468 | 19.9149 | 20.4214 |  | 20.5205 | 20.0514 | 20.1635 | 19.1348 |  | 16.7794 | 16.7869 | 16.5246 | 16.7289 | 16.7744 | 17.3208 | 17.9849 | 16.1117 | 16.8372 | 16.0407 | 16.8807 | 17.8802 | 44.4951 | 47.5433 | 43.5248 | 21.3366 |  |  | 0.51607 | -0.45348 | -48.4138 | 0.54668 | 0.36614 | -197.8348 | 11.1436 | -0.34929 | -0.11492 | 0.27432 | -0.066024 | 8.8288 | 9.0587 | 1.9784 | 21.7899 | 22.0192 | 22.2024 | 22.2688 | 22.0945 | 21.4215 | 20.2398 | 22.2039 | 22.3749 | 22.4068 | 22.3631 | 21.993 | 21.2298 | 22.271 | 17.5348 | 17.246 | 16.4743 | 16.3382 | 16.3037 | 17.0768 | 16.8722 | 22.3818 | 22.1547 | 21.7038 | 22.0854 | 21.802 | 21.3149 | 21.9498 | 21.5297 | 20.9112 | 20.1133 | 20.3017 | 19.841 | 19.7512 | 0.039332 | -0.042384 | 20.7323 | 22.0809 | 22.3909 | 20.1003 | 21.6829 | 22.1298 | 21.96 | 21.7201 | 21.2902 | 21.7968 | 21.4619 | 21.0515 | 20.2522 | 20.28 | 20.2366 | 20.2222 | 20.1352 |  | 20.2135 | 19.8828 | 20.1139 | 19.7434 | 20.0913 | 20.3257 |  | 20.4245 |  |  | 20.2656 | 20.3835 | 20.6245 | [5 empty] | 21.9399 | 20.3415 | 21.6764 | 22.0635 | 19.5498 | 21.1805 | 21.8028 | 19.3538 | 19.9118 | 21.1228 |  | 19.7386 | 20.917 | 18.8814 | 19.7337 | 20.7978 | 19.4839 | 20.0156 | 19.0713 | 20.1252 | 19.121 | 20.2047 | 18.8611 | 20.0668 | 21.04 | 19.4124 | 19.7882 | 20.9733 | 18.9227 | 19.8081 | 20.7977 | 18.9741 | 20.1372 | 19.2785 | 19.887 | 18.9048 | 20.1106 | -0.14482 | 20.9473 | 0.048966 | 0.01611 | -27.0492 | 3.0973 | -4.61 | -0.09 | 0.85771 | -0.79909 | -8.2566 | 0.87737 | 0.71869 | -16.7059 | 3.9649 | 0.42213 | 0.42581 | 0.42892 | 0.3514 | 0.44537 | 0.43992 | 0.42944
42838.4168 | -303 | 22.9032 | 22.869 | 22.8506 | 22.776 | 22.4158 | 21.754 | 22.7208 | 21.8157 | 22.3773 | 22.3851 | 22.366 | 22.0374 | 21.2578 | 22.2279 | 21.5747 | 21.7465 | 21.8876 | 21.0644 | 21.165 | 21.3911 | 20.4667 | 20.6136 | 20.9092 | 21.881 | 21.6469 | 21.2891 | 20.283 | 20.376 | 20.3792 | 22.0468 | 21.6607 | 21.1743 | 21.9938 | 21.728 | 21.345 | 19.9226 | 20.4246 |  | 20.526 | 20.0527 | 20.1716 | 19.1431 |  | 16.7671 | 16.7809 | 16.5202 | 16.7269 | 16.7672 | 17.3117 | 17.9769 | 16.1139 | 16.8364 | 16.0552 | 16.8797 | 17.8829 | 44.5088 | 47.5357 | 43.5351 | 21.3414 |  |  | 0.37741 | -0.31285 | -47.9611 | 0.74841 | 0.422 | -197.8164 | 11.0503 | -0.3828 | -0.03221 | -0.045625 | -0.033561 | 8.8292 | 9.059 | 1.9789 | 21.7848 | 22.0081 | 22.2038 | 22.2685 | 22.094 | 21.4175 | 20.2316 | 22.1992 | 22.3665 | 22.4093 | 22.3615 | 21.9896 | 21.2271 | 22.2692 | 17.5337 | 17.2479 | 16.4538 | 16.3676 | 16.3203 | 17.0735 | 16.8681 | 22.3804 | 22.1483 | 21.7078 | 22.0838 | 21.7958 | 21.3107 | 21.9428 | 21.5249 | 20.9068 | 20.1094 | 20.3006 | 19.8353 | 19.7465 | 0.080028 | -0.16963 | 20.7311 | 22.0789 | 22.3833 | 20.0984 | 21.684 | 22.1251 | 21.9564 | 21.7177 | 21.2902 | 21.7951 | 21.4605 | 21.055 | 20.2469 | 20.2941 | 20.2343 | 20.224 | 20.1355 |  | 20.2282 | 19.8814 | 20.1244 | 19.7345 | 20.1011 | 20.3217 |  | 20.4335 |  |  | 20.2776 | 20.3815 | 20.6271 | [5 empty] | 21.9555 | 20.3338 | 21.6903 | 22.0638 | 19.5577 | 21.1925 | 21.8046 | 19.3644 | 19.9132 | 21.1295 |  | 19.7367 | 20.9155 | 18.8844 | 19.7409 | 20.8114 | 19.4922 | 20.0288 | 19.0839 | 20.1312 | 19.1348 | 20.2192 | 18.8573 | 20.0637 | 21.0367 | 19.3989 | 19.7888 | 20.9761 | 18.9204 | 19.8107 | 20.7897 | 18.9765 | 20.1288 | 19.2829 | 19.8853 | 18.9091 | 20.1134 | -0.030554 | 20.9462 | 0.049157 | 0.016197 | -27.0462 | 3.0974 | 3.15 | -0.15 | 0.7335 | -0.66372 | -8.2179 | 1.0266 | 0.77156 | -16.7048 | 3.9482 | 0.42262 | 0.4262 | 0.4295 | 0.35113 | 0.44716 | 0.43995 | 0.42944
42838.4168 | -302 | 22.8979 | 22.8586 | 22.8461 | 22.7772 | 22.4104 | 21.7493 | 22.7195 | 21.8102 | 22.3666 | 22.3736 | 22.362 | 22.0357 | 21.2521 | 22.2214 | 21.5749 | 21.7454 | 21.8766 | 21.0759 | 21.1748 | 21.376 | 20.4651 | 20.6075 | 20.9037 | 21.8823 | 21.6427 | 21.2737 | 20.2779 | 20.3745 | 20.3729 | 22.0532 | 21.6589 | 21.1783 | 21.9911 | 21.731 | 21.3547 | 19.9241 | 20.43 |  | 20.5264 | 20.0647 | 20.1731 | 19.1517 |  | 16.7791 | 16.7827 | 16.518 | 16.7231 | 16.7599 | 17.3086 | 17.9699 | 16.1349 | 16.8392 | 16.1006 | 16.8799 | 17.8859 | 44.5065 | 47.5386 | 43.5295 | 21.3406 |  |  | 0.54169 | -0.28065 | -48.9165 | 0.70439 | 0.21106 | -197.8085 | 10.6541 | -0.53854 | 0.15499 | -0.0013574 | -0.012382 | 8.8289 | 9.0585 | 1.9789 | 21.7869 | 22.0166 | 22.2046 | 22.2745 | 22.1084 | 21.4349 | 20.2431 | 22.2116 | 22.3781 | 22.4216 | 22.36 | 21.9964 | 21.2361 | 22.2816 | 17.5311 | 17.2353 | 16.4265 | 16.3841 | 16.3337 | 17.0758 | 16.8608 | 22.3816 | 22.146 | 21.7071 | 22.0876 | 21.8006 | 21.3139 | 21.9485 | 21.5275 | 20.9113 | 20.1143 | 20.3034 | 19.831 | 19.7594 | 0.012005 | -0.046188 | 20.7279 | 22.0691 | 22.3772 | 20.0904 | 21.6784 | 22.1229 | 21.9536 | 21.7172 | 21.2867 | 21.7804 | 21.452 | 21.0549 | 20.2382 | 20.2936 | 20.2356 | 20.2161 | 20.132 |  | 20.2256 | 19.8742 | 20.1235 | 19.743 | 20.1053 | 20.3319 |  | 20.4317 |  |  | 20.2785 | 20.388 | 20.621 | [5 empty] | 21.9521 | 20.3398 | 21.6848 | 22.0742 | 19.5577 | 21.1804 | 21.8151 | 19.3677 | 19.9175 | 21.1359 |  | 19.7488 | 20.9217 | 18.8916 | 19.7441 | 20.8078 | 19.4948 | 20.0319 | 19.0911 | 20.1394 | 19.1326 | 20.229 | 18.8461 | 20.0486 | 21.0303 | 19.3875 | 19.7782 | 20.9613 | 18.9109 | 19.7939 | 20.783 | 18.9724 | 20.1212 | 19.2757 | 19.8833 | 18.897 | 20.1075 | -0.13017 | 20.9463 | 0.049255 | 0.015638 | -27.1441 | 3.0974 | -0.84 | -0.11 | 0.87875 | -0.62864 | -8.2993 | 0.99591 | 0.54565 | -16.7044 | 3.8767 | 0.42263 | 0.42637 | 0.4294 | 0.35169 | 0.44934 | 0.43976 | 0.42925
42838.4168 | -301 | 22.8949 | 22.8577 | 22.8469 | 22.7754 | 22.4069 | 21.7519 | 22.7094 | 21.8056 | 22.3662 | 22.3694 | 22.3556 | 22.0338 | 21.2524 | 22.2207 | 21.5772 | 21.7531 | 21.8843 | 21.0728 | 21.177 | 21.3895 | 20.4782 | 20.6146 | 20.9117 | 21.8799 | 21.6519 | 21.2813 | 20.2891 | 20.3755 | 20.374 | 22.0534 | 21.6651 | 21.1877 | 21.9867 | 21.7295 | 21.3503 | 19.9217 | 20.4353 |  | 20.5225 | 20.061 | 20.1796 | 19.1598 |  | 16.771 | 16.7796 | 16.5098 | 16.7075 | 16.7522 | 17.2872 | 17.9441 | 16.1296 | 16.8396 | 16.1175 | 16.8785 | 17.8828 | 44.5108 | 47.5271 | 43.5245 | 21.3424 |  |  | 0.39384 | -0.48436 | -49.3548 | 0.67744 | 0.14076 | -197.867 | 10.8072 | -0.6785 | 0.14604 | -0.12787 | 0.057926 | 8.8288 | 9.0586 | 1.9786 | 21.7841 | 22.0092 | 22.1986 | 22.2613 | 22.0924 | 21.4259 | 20.235 | 22.1991 | 22.3716 | 22.4048 | 22.359 | 21.9902 | 21.2305 | 22.2767 | 17.5324 | 17.2459 | 16.4115 | 16.3877 | 16.3558 | 17.0836 | 16.8705 | 22.3879 | 22.1563 | 21.7183 | 22.0912 | 21.8097 | 21.3205 | 21.9557 | 21.5347 | 20.9141 | 20.1182 | 20.3103 | 19.8422 | 19.7676 | 0.099492 | -0.069392 | 20.7233 | 22.0625 | 22.3762 | 20.0952 | 21.6742 | 22.1234 | 21.9525 | 21.7178 | 21.2827 | 21.7768 | 21.4469 | 21.0475 | 20.2384 | 20.2845 | 20.2358 | 20.2128 | 20.1253 |  | 20.219 | 19.8518 | 20.1192 | 19.7328 | 20.0921 | 20.333 |  | 20.4247 |  |  | 20.2724 | 20.3895 | 20.6125 | [5 empty] | 21.9449 | 20.3317 | 21.6834 | 22.0618 | 19.5487 | 21.1891 | 21.8058 | 19.3577 | 19.9035 | 21.1194 |  | 19.7373 | 20.9043 | 18.8908 | 19.7259 | 20.792 | 19.4886 | 20.0317 | 19.0779 | 20.1327 | 19.1296 | 20.2122 | 18.8541 | 20.0638 | 21.0323 | 19.4008 | 19.7881 | 20.9696 | 18.9185 | 19.8012 | 20.7937 | 18.9814 | 20.1365 | 19.2757 | 19.884 | 18.8947 | 20.1152 | 0.04717 | 20.9462 | 0.048426 | 0.016437 | -26.9642 | 3.0974 | -4.86 | -0.11 | 0.74929 | -0.82584 | -8.3364 | 0.97667 | 0.44558 | -16.7063 | 3.9044 | 0.42259 | 0.42685 | 0.42925 | 0.35246 | 0.45214 | 0.43946 | 0.42915
42838.4168 | -300 | 22.8903 | 22.8614 | 22.846 | 22.7694 | 22.4049 | 21.7392 | 22.7116 | 21.8011 | 22.3645 | 22.3702 | 22.3517 | 22.035 | 21.2541 | 22.2204 | 21.582 | 21.7578 | 21.8884 | 21.0777 | 21.1783 | 21.3962 | 20.4763 | 20.6215 | 20.9138 | 21.8857 | 21.6526 | 21.2869 | 20.2948 | 20.3878 | 20.3776 | 22.0436 | 21.666 | 21.1758 | 21.992 | 21.7287 | 21.3476 | 19.914 | 20.4302 |  | 20.5211 | 20.0485 | 20.1671 | 19.166 |  | 16.7745 | 16.7759 | 16.5039 | 16.7095 | 16.7543 | 17.285 | 17.9461 | 16.1191 | 16.8445 | 16.0995 | 16.8761 | 17.8855 | 44.5069 | 47.5203 | 43.5298 | 21.3429 |  |  | 0.47795 | -0.41733 | -49.0624 | 0.83909 | 0.11316 | -197.8545 | 10.6745 | -0.48531 | 0.075404 | -0.015204 | 0.0048048 | 8.8295 | 9.0592 | 1.9785 | 21.7854 | 22.0139 | 22.2069 | 22.2653 | 22.0998 | 21.4228 | 20.2356 | 22.2044 | 22.3777 | 22.4154 | 22.369 | 21.9938 | 21.2335 | 22.2764 | 17.5385 | 17.2629 | 16.3811 | 16.3945 | 16.3767 | 17.0849 | 16.8694 | 22.3854 | 22.1548 | 21.717 | 22.0901 | 21.8071 | 21.3107 | 21.9549 | 21.5352 | 20.9181 | 20.1203 | 20.3177 | 19.8485 | 19.7643 | 0.0068932 | -0.13577 | 20.7278 | 22.0734 | 22.387 | 20.1038 | 21.6788 | 22.1232 | 21.9512 | 21.7195 | 21.2904 | 21.7821 | 21.4565 | 21.0486 | 20.2427 | 20.2962 | 20.2399 | 20.221 | 20.1284 |  | 20.2265 | 19.8489 | 20.1206 | 19.7239 | 20.0989 | 20.3337 |  | 20.4236 |  |  | 20.2839 | 20.3797 | 20.6232 | [5 empty] | 21.9474 | 20.3495 | 21.6809 | 22.0657 | 19.5526 | 21.1875 | 21.8161 | 19.37 | 19.9097 | 21.1438 |  | 19.7489 | 20.9226 | 18.8999 | 19.7364 | 20.8094 | 19.4924 | 20.0387 | 19.0999 | 20.1418 | 19.1395 | 20.2195 | 18.8596 | 20.0569 | 21.0417 | 19.4024 | 19.7813 | 20.9723 | 18.9303 | 19.8064 | 20.7954 | 18.9851 | 20.132 | 19.2827 | 19.8927 | 18.9023 | 20.1245 | -0.089173 | 20.9458 | 0.047559 | 0.015943 | -27.0098 | 3.0973 | -6.97 | -0.12 | 0.82544 | -0.76657 | -8.3116 | 1.087 | 0.39951 | -16.7057 | 3.8803 | 0.42276 | 0.42697 | 0.42972 | 0.35194 | 0.45539 | 0.43903 | 0.42932
42838.4168 | -299 | 22.8933 | 22.8604 | 22.8551 | 22.7678 | 22.408 | 21.7445 | 22.7155 | 21.8071 | 22.3722 | 22.3804 | 22.3605 | 22.032 | 21.2507 | 22.2232 | 21.5782 | 21.7512 | 21.8798 | 21.0705 | 21.1699 | 21.386 | 20.4693 | 20.6135 | 20.9095 | 21.8818 | 21.6507 | 21.2849 | 20.289 | 20.3857 | 20.3844 | 22.0383 | 21.6565 | 21.183 | 21.9921 | 21.7238 | 21.3559 | 19.921 | 20.433 |  | 20.523 | 20.0573 | 20.1717 | 19.1693 |  | 16.7866 | 16.7749 | 16.5118 | 16.7155 | 16.7579 | 17.2866 | 17.9697 | 16.1217 | 16.8483 | 16.0961 | 16.8779 | 17.8826 | 44.5052 | 47.5191 | 43.53 | 21.3352 |  |  | 0.61858 | -0.31285 | -49.3298 | 0.57427 | 0.15258 | -197.8302 | 10.7645 | -0.49714 | 0.013326 | 0.10984 | 0.018519 | 8.8293 | 9.0592 | 1.9782 | 21.7812 | 22.0041 | 22.2051 | 22.267 | 22.0969 | 21.4231 | 20.2325 | 22.1994 | 22.373 | 22.4084 | 22.3624 | 21.9891 | 21.2234 | 22.2704 | 17.5494 | 17.2686 | 16.353 | 16.372 | 16.3905 | 17.0815 | 16.8692 | 22.3822 | 22.1475 | 21.7095 | 22.0883 | 21.8018 | 21.3121 | 21.9437 | 21.5307 | 20.9096 | 20.1185 | 20.3134 | 19.8455 | 19.7476 | -0.10969 | -0.051133 | 20.7245 | 22.0789 | 22.3862 | 20.0988 | 21.6807 | 22.1227 | 21.9543 | 21.7172 | 21.2898 | 21.7888 | 21.4596 | 21.0543 | 20.2431 | 20.2979 | 20.2417 | 20.2216 | 20.135 |  | 20.2219 | 19.8378 | 20.1176 | 19.7194 | 20.0987 | 20.3355 |  | 20.424 |  |  | 20.2737 | 20.3687 | 20.6146 | [5 empty] | 21.9477 | 20.3317 | 21.6769 | 22.0639 | 19.5468 | 21.1734 | 21.8027 | 19.3675 | 19.9138 | 21.1406 |  | 19.749 | 20.9143 | 18.8996 | 19.7356 | 20.8189 | 19.4922 | 20.042 | 19.0942 | 20.1379 | 19.1425 | 20.23 | 18.8523 | 20.0647 | 21.0326 | 19.3957 | 19.784 | 20.9649 | 18.9267 | 19.8131 | 20.7998 | 18.9907 | 20.1323 | 19.2888 | 19.8915 | 18.8974 | 20.1259 | -0.12163 | 20.9476 | 0.047805 | 0.015232 | -27.1375 | 3.0973 | 1.67 | -0.08 | 0.93906 | -0.66371 | -8.3342 | 0.89923 | 0.46392 | -16.7047 | 3.8966 | 0.42242 | 0.42718 | 0.42984 | 0.35033 | 0.45849 | 0.43917 | 0.42972
42838.4168 | -298 | 22.9035 | 22.8603 | 22.8612 | 22.7885 | 22.4215 | 21.7576 | 22.7253 | 21.8209 | 22.3716 | 22.393 | 22.37 | 22.049 | 21.2689 | 22.2333 | 21.5756 | 21.7453 | 21.8826 | 21.0693 | 21.1689 | 21.386 | 20.4745 | 20.6074 | 20.9046 | 21.8816 | 21.653 | 21.2831 | 20.283 | 20.3809 | 20.3817 | 22.0519 | 21.6589 | 21.1815 | 21.993 | 21.73 | 21.3594 | 19.9246 | 20.4287 |  | 20.5324 | 20.0643 | 20.1734 | 19.1513 |  | 16.7838 | 16.7687 | 16.5087 | 16.722 | 16.77 | 17.3057 | 17.9877 | 16.1297 | 16.8511 | 16.1002 | 16.8778 | 17.881 | 44.4893 | 47.5267 | 43.5461 | 21.342 |  |  | 0.50555 | -0.23531 | -49.7799 | 0.50528 | 0.25969 | -197.8637 | 10.0233 | -0.44983 | 0.14021 | -0.041429 | 0.02772 | 8.8288 | 9.0586 | 1.9788 | 21.7821 | 22.0019 | 22.1978 | 22.2675 | 22.091 | 21.4195 | 20.2328 | 22.2006 | 22.366 | 22.4116 | 22.3603 | 21.9858 | 21.2232 | 22.2701 | 17.5769 | 17.294 | 16.3498 | 16.3646 | 16.4042 | 17.0932 | 16.8797 | 22.38 | 22.1482 | 21.7106 | 22.081 | 21.803 | 21.3073 | 21.9457 | 21.528 | 20.908 | 20.1164 | 20.3076 | 19.8388 | 19.7467 | -0.16985 | -0.24799 | 20.7275 | 22.077 | 22.3796 | 20.0914 | 21.6765 | 22.1217 | 21.9508 | 21.7163 | 21.2884 | 21.7859 | 21.4583 | 21.0502 | 20.243 | 20.2884 | 20.2381 | 20.2227 | 20.1464 |  | 20.2254 | 19.8361 | 20.1245 | 19.7267 | 20.1094 | 20.3392 |  | 20.4294 |  |  | 20.2832 | 20.3772 | 20.6124 | [5 empty] | 21.9449 | 20.3318 | 21.6844 | 22.0596 | 19.5331 | 21.1845 | 21.8144 | 19.3611 | 19.9068 | 21.1234 |  | 19.7475 | 20.9083 | 18.8924 | 19.7315 | 20.8098 | 19.492 | 20.0403 | 19.0974 | 20.1359 | 19.1457 | 20.2229 | 18.8567 | 20.062 | 21.0259 | 19.3889 | 19.7753 | 20.9773 | 18.9319 | 19.8124 | 20.7965 | 18.9945 | 20.1288 | 19.2895 | 19.8938 | 18.9046 | 20.1301 | -0.003657 | 20.9453 | 0.047031 | 0.013206 | -27.1224 | 3.0974 | -6.12 | -0.04 | 0.84894 | -0.57561 | -8.3721 | 0.84347 | 0.60525 | -16.7067 | 3.7602 | 0.42222 | 0.42746 | 0.42999 | 0.34863 | 0.46007 | 0.43979 | 0.42967
42838.4168 | -297 | 22.8964 | 22.8673 | 22.8579 | 22.7751 | 22.4145 | 21.7545 | 22.7185 | 21.8088 | 22.3692 | 22.3801 | 22.3637 | 22.0419 | 21.2595 | 22.2292 | 21.5806 | 21.7424 | 21.884 | 21.0743 | 21.1762 | 21.3923 | 20.4743 | 20.6118 | 20.9059 | 21.8853 | 21.6531 | 21.2796 | 20.2868 | 20.3945 | 20.3781 | 22.0647 | 21.6683 | 21.1872 | 22.0018 | 21.7363 | 21.3641 | 19.9295 | 20.4362 |  | 20.5328 | 20.0639 | 20.1778 | 19.1621 |  | 16.7871 | 16.7761 | 16.5125 | 16.7413 | 16.7886 | 17.3281 | 17.9822 | 16.0781 | 16.859 | 16.1072 | 16.8866 | 17.8869 | 44.4765 | 47.541 | 43.557 | 21.341 |  |  | 0.45693 | -0.18734 | -50.2327 | 0.15372 | 0.18675 | -197.8828 | 10.5319 | -0.49977 | -0.0014634 | 0.11403 | 0.042476 | 8.8294 | 9.0592 | 1.9793 | 21.7755 | 22.0023 | 22.191 | 22.2651 | 22.0961 | 21.4165 | 20.2312 | 22.1955 | 22.3649 | 22.4044 | 22.3562 | 21.984 | 21.2189 | 22.2635 | 17.5929 | 17.2511 | 16.3308 | 16.3447 | 16.3899 | 17.0908 | 16.8744 | 22.3826 | 22.1556 | 21.7175 | 22.09 | 21.8087 | 21.319 | 21.9524 | 21.5376 | 20.919 | 20.1214 | 20.3167 | 19.8524 | 19.7604 | -0.12326 | -0.15327 | 20.7321 | 22.0756 | 22.38 | 20.0925 | 21.67 | 22.1189 | 21.9478 | 21.7209 | 21.2905 | 21.782 | 21.4572 | 21.0511 | 20.2421 | 20.2852 | 20.2374 | 20.2166 | 20.1427 |  | 20.221 | 19.8268 | 20.1253 | 19.7111 | 20.1003 | 20.339 |  | 20.4189 |  |  | 20.2857 | 20.3799 | 20.6173 | [5 empty] | 21.9471 | 20.3361 | 21.6851 | 22.059 | 19.5368 | 21.1827 | 21.8126 | 19.3611 | 19.9036 | 21.1221 |  | 19.738 | 20.9002 | 18.8914 | 19.7218 | 20.8108 | 19.4903 | 20.0356 | 19.0873 | 20.1258 | 19.1432 | 20.2238 | 18.8471 | 20.0564 | 21.0246 | 19.3872 | 19.7652 | 20.969 | 18.9239 | 19.8038 | 20.7931 | 18.9951 | 20.1194 | 19.2904 | 19.8901 | 18.9021 | 20.1273 | -0.1387 | 20.9456 | 0.046754 | 0.013337 | -27.0488 | 3.0973 | -5.13 | -0.08 | 0.80708 | -0.51361 | -8.4102 | 0.46524 | 0.51328 | -16.7081 | 3.8546 | 0.42218 | 0.42775 | 0.43012 | 0.34657 | 0.46156 | 0.43965 | 0.42946
42838.4169 | -296 | 22.8916 | 22.8627 | 22.8478 | 22.7747 | 22.4107 | 21.7492 | 22.7093 | 21.8043 | 22.3665 | 22.3766 | 22.3611 | 22.0375 | 21.2571 | 22.2193 | 21.5838 | 21.7474 | 21.8861 | 21.073 | 21.1718 | 21.387 | 20.4706 | 20.6116 | 20.8967 | 21.8871 | 21.6446 | 21.2769 | 20.2857 | 20.3948 | 20.378 | 22.0563 | 21.6584 | 21.1806 | 21.9963 | 21.7273 | 21.3523 | 19.9245 | 20.4344 |  | 20.5175 | 20.0586 | 20.1773 | 19.1517 |  | 16.784 | 16.7769 | 16.5112 | 16.7311 | 16.7853 | 17.3087 | 17.9462 | 15.9254 | 16.8541 | 16.1253 | 16.8794 | 17.8873 | 44.4531 | 47.5431 | 43.5652 | 21.3388 |  |  | 0.35245 | -0.38579 | -50.6789 | 0.45468 | 0.17821 | -197.8631 | 10.1474 | -0.58979 | -0.072687 | -0.06157 | -0.066024 | 8.8296 | 9.0593 | 1.9786 | 21.7787 | 22.0072 | 22.2052 | 22.2648 | 22.0987 | 21.415 | 20.2327 | 22.1888 | 22.3692 | 22.4045 | 22.3562 | 21.9918 | 21.2252 | 22.2631 | 17.5962 | 17.2157 | 16.3136 | 16.3234 | 16.3637 | 17.0837 | 16.8618 | 22.3785 | 22.1489 | 21.7116 | 22.0878 | 21.8016 | 21.3088 | 21.945 | 21.5288 | 20.9081 | 20.116 | 20.3092 | 19.8453 | 19.7481 | 0.064497 | -0.12018 | 20.7274 | 22.0708 | 22.3827 | 20.1016 | 21.672 | 22.1141 | 21.9538 | 21.7179 | 21.2847 | 21.7841 | 21.4517 | 21.0474 | 20.2381 | 20.2874 | 20.2402 | 20.2137 | 20.1241 |  | 20.2127 | 19.8154 | 20.1156 | 19.6866 | 20.0919 | 20.3263 |  | 20.4144 |  |  | 20.2821 | 20.3739 | 20.6295 | [5 empty] | 21.9441 | 20.3404 | 21.6827 | 22.0598 | 19.5392 | 21.1822 | 21.8062 | 19.3605 | 19.9052 | 21.1208 |  | 19.7456 | 20.915 | 18.8932 | 19.7287 | 20.8156 | 19.4923 | 20.0383 | 19.0891 | 20.1253 | 19.1401 | 20.2251 | 18.843 | 20.0519 | 21.0309 | 19.3816 | 19.7611 | 20.964 | 18.9247 | 19.8053 | 20.7996 | 18.9979 | 20.1168 | 19.2906 | 19.8919 | 18.9028 | 20.1305 | -0.15966 | 20.9478 | 0.04684 | 0.01362 | -27.0133 | 3.0974 | -8.58 | -0.02 | 0.70882 | -0.73704 | -8.4474 | 0.80014 | 0.50139 | -16.7067 | 3.7834 | 0.42241 | 0.42774 | 0.43052 | 0.34538 | 0.46201 | 0.43977 | 0.42962
42838.4169 | -295 | 22.8962 | 22.8617 | 22.8452 | 22.7707 | 22.4064 | 21.7439 | 22.7119 | 21.8075 | 22.3635 | 22.3739 | 22.3576 | 22.0307 | 21.2517 | 22.2178 | 21.5847 | 21.7567 | 21.8907 | 21.0774 | 21.1685 | 21.3917 | 20.469 | 20.6148 | 20.9018 | 21.8864 | 21.6534 | 21.2814 | 20.2914 | 20.3954 | 20.3792 | 22.0509 | 21.661 | 21.187 | 22.0001 | 21.7286 | 21.3581 | 19.9219 | 20.4334 |  | 20.5221 | 20.0562 | 20.172 | 19.149 |  | 16.7826 | 16.7834 | 16.4995 | 16.7373 | 16.7794 | 17.2952 | 17.925 | 15.8009 | 16.8608 | 16.1475 | 16.8847 | 17.8855 | 44.4348 | 47.5341 | 43.5557 | 21.3432 |  |  | 0.54367 | -0.52707 | -51.7184 | 0.31931 | 0.056644 | -197.8335 | 9.8333 | -0.49583 | -0.023842 | -0.26403 | -0.045018 | 8.8282 | 9.0581 | 1.9785 | 21.7832 | 22.0018 | 22.2114 | 22.2645 | 22.0941 | 21.4213 | 20.2364 | 22.2074 | 22.3765 | 22.4126 | 22.3651 | 21.9912 | 21.2365 | 22.2714 | 17.6021 | 17.1954 | 16.3036 | 16.3162 | 16.364 | 17.0898 | 16.8639 | 22.3795 | 22.1502 | 21.7033 | 22.0861 | 21.803 | 21.3083 | 21.9452 | 21.531 | 20.9135 | 20.1143 | 20.3162 | 19.8473 | 19.746 | 0.072951 | -0.051703 | 20.7296 | 22.0703 | 22.3763 | 20.1018 | 21.6758 | 22.116 | 21.9549 | 21.7142 | 21.283 | 21.7819 | 21.4508 | 21.0408 | 20.2383 | 20.2935 | 20.2452 | 20.2091 | 20.1192 |  | 20.2172 | 19.8115 | 20.1055 | 19.6873 | 20.0869 | 20.332 |  | 20.421 |  |  | 20.2883 | 20.377 | 20.6295 | [5 empty] | 21.9503 | 20.3405 | 21.6867 | 22.0701 | 19.5428 | 21.1883 | 21.8086 | 19.3589 | 19.9007 | 21.1292 |  | 19.7388 | 20.9137 | 18.896 | 19.7302 | 20.8167 | 19.4878 | 20.0418 | 19.0894 | 20.1283 | 19.1444 | 20.2265 | 18.8471 | 20.0593 | 21.0339 | 19.3833 | 19.7662 | 20.9653 | 18.9282 | 19.8117 | 20.7993 | 19.0028 | 20.1244 | 19.2922 | 19.897 | 18.9014 | 20.139 | -0.050774 | 20.9468 | 0.04716 | 0.013678 | -26.9815 | 3.0973 | 3.63 | 0 | 0.88036 | -0.86149 | -8.5337 | 0.67054 | 0.28267 | -16.7051 | 3.7243 | 0.4227 | 0.42751 | 0.43034 | 0.34544 | 0.46336 | 0.43976 | 0.42962
42838.4169 | -294 | 22.9038 | 22.8614 | 22.8423 | 22.7755 | 22.4079 | 21.7458 | 22.7192 | 21.8114 | 22.368 | 22.3818 | 22.362 | 22.0314 | 21.2596 | 22.218 | 21.5831 | 21.7626 | 21.8852 | 21.0781 | 21.1747 | 21.3925 | 20.4772 | 20.6156 | 20.9098 | 21.8868 | 21.6597 | 21.2883 | 20.2886 | 20.398 | 20.3753 | 22.0446 | 21.6518 | 21.1834 | 21.9903 | 21.7327 | 21.3465 | 19.9165 | 20.4321 |  | 20.5152 | 20.0508 | 20.1665 | 19.1434 |  | 16.7921 | 16.7803 | 16.5025 | 16.7346 | 16.7753 | 17.2987 | 17.9554 | 15.6881 | 16.8672 | 16.1573 | 16.8876 | 17.8854 | 44.4321 | 47.5345 | 43.5574 | 21.346 |  |  | 0.40173 | -0.31745 | -51.9754 | 0.35349 | 0.088844 | -197.8236 | 9.7394 | -0.36638 | 0.14079 | -0.11465 | 0.01904 | 8.8276 | 9.0573 | 1.9784 | 21.7892 | 22.0083 | 22.2029 | 22.2674 | 22.093 | 21.423 | 20.2383 | 22.2051 | 22.3721 | 22.4083 | 22.3649 | 21.9975 | 21.2248 | 22.2773 | 17.6023 | 17.2099 | 16.2962 | 16.312 | 16.3772 | 17.0902 | 16.8622 | 22.3826 | 22.1558 | 21.7096 | 22.0948 | 21.805 | 21.3104 | 21.9439 | 21.5332 | 20.9166 | 20.1151 | 20.3295 | 19.8511 | 19.761 | 0.030289 | -0.12512 | 20.7377 | 22.074 | 22.3797 | 20.1003 | 21.6704 | 22.1191 | 21.9514 | 21.7146 | 21.2808 | 21.7868 | 21.4564 | 21.0434 | 20.2398 | 20.2954 | 20.243 | 20.2082 | 20.1264 |  | 20.2259 | 19.8042 | 20.112 | 19.705 | 20.0912 | 20.3453 |  | 20.4215 |  |  | 20.3014 | 20.389 | 20.6329 | [5 empty] | 21.9491 | 20.3468 | 21.6881 | 22.0784 | 19.5557 | 21.1966 | 21.8138 | 19.3491 | 19.8969 | 21.1176 |  | 19.7341 | 20.913 | 18.89 | 19.7268 | 20.8124 | 19.4871 | 20.041 | 19.0806 | 20.1266 | 19.1417 | 20.2227 | 18.8422 | 20.0521 | 21.0197 | 19.3741 | 19.7605 | 20.9621 | 18.925 | 19.8051 | 20.7943 | 18.9985 | 20.1188 | 19.2893 | 19.8964 | 18.897 | 20.1334 | -0.12906 | 20.9486 | 0.047129 | 0.013337 | -27.0901 | 3.0973 | -9.49 | -0.05 | 0.75676 | -0.66858 | -8.5549 | 0.7055 | 0.35401 | -16.7048 | 3.7065 | 0.42279 | 0.42793 | 0.42999 | 0.34546 | 0.46398 | 0.43974 | 0.42923
42838.4169 | -293 | 22.8996 | 22.8661 | 22.8456 | 22.7779 | 22.3992 | 21.7433 | 22.7174 | 21.8112 | 22.369 | 22.3848 | 22.3645 | 22.035 | 21.2584 | 22.219 | 21.578 | 21.7525 | 21.8812 | 21.0768 | 21.1692 | 21.3861 | 20.4695 | 20.6093 | 20.916 | 21.8851 | 21.6531 | 21.2809 | 20.2927 | 20.3951 | 20.371 | 22.0545 | 21.6553 | 21.1867 | 21.9989 | 21.7325 | 21.3582 | 19.9216 | 20.4375 |  | 20.5258 | 20.0582 | 20.1768 | 19.157 |  | 16.7822 | 16.7728 | 16.5096 | 16.7406 | 16.7888 | 17.3177 | 17.9808 | 15.5911 | 16.8672 | 16.1615 | 16.8739 | 17.8953 | 44.4367 | 47.5371 | 43.5515 | 21.3502 |  |  | 0.29527 | -0.41996 | -52.0115 | 0.59859 | 0.15258 | -197.8795 | 9.4272 | -0.39529 | -0.0020472 | -0.053178 | -0.096404 | 8.8284 | 9.0582 | 1.9785 | 21.7889 | 22.007 | 22.1991 | 22.2708 | 22.0974 | 21.4197 | 20.2396 | 22.2024 | 22.3696 | 22.3993 | 22.3607 | 21.9905 | 21.222 | 22.2708 | 17.6036 | 17.1443 | 16.2824 | 16.3092 | 16.3567 | 17.0873 | 16.8659 | 22.3813 | 22.147 | 21.7148 | 22.0883 | 21.8013 | 21.312 | 21.9531 | 21.5346 | 20.9171 | 20.1195 | 20.3231 | 19.856 | 19.7634 | -0.0027402 | -0.042954 | 20.7428 | 22.0766 | 22.3878 | 20.1013 | 21.6721 | 22.1194 | 21.9553 | 21.7133 | 21.2815 | 21.7919 | 21.4592 | 21.0537 | 20.2413 | 20.2954 | 20.2417 | 20.2154 | 20.1155 |  | 20.2208 | 19.7968 | 20.1129 | 19.7098 | 20.0907 | 20.3457 |  | 20.4223 |  |  | 20.2981 | 20.3869 | 20.6212 | [5 empty] | 21.9454 | 20.3378 | 21.6832 | 22.0673 | 19.5475 | 21.1871 | 21.8117 | 19.3518 | 19.8947 | 21.1156 |  | 19.7384 | 20.9129 | 18.8865 | 19.7214 | 20.8146 | 19.4837 | 20.0455 | 19.0797 | 20.1268 | 19.145 | 20.2245 | 18.8454 | 20.0554 | 21.0207 | 19.3735 | 19.7682 | 20.969 | 18.929 | 19.8126 | 20.8043 | 19.0027 | 20.1222 | 19.2934 | 19.9011 | 18.9025 | 20.1405 | -0.087318 | 20.9466 | 0.048161 | 0.013315 | -27.1465 | 3.0973 | -2.43 | -0.04 | 0.64878 | -0.76898 | -8.5577 | 0.91806 | 0.46395 | -16.7077 | 3.6468 | 0.42293 | 0.42817 | 0.42984 | 0.34497 | 0.46596 | 0.43953 | 0.42931
42838.4169 | -292 | 22.8946 | 22.8594 | 22.8482 | 22.7694 | 22.4052 | 21.7515 | 22.7225 | 21.8151 | 22.3709 | 22.373 | 22.3613 | 22.0386 | 21.2591 | 22.227 | 21.58 | 21.7523 | 21.8835 | 21.0722 | 21.1688 | 21.388 | 20.4703 | 20.6109 | 20.9089 | 21.8801 | 21.6478 | 21.2782 | 20.2875 | 20.3906 | 20.3635 | 22.0536 | 21.6629 | 21.1849 | 21.9902 | 21.7299 | 21.3505 | 19.9201 | 20.4428 |  | 20.5172 | 20.0627 | 20.1762 | 19.1519 |  | 16.7882 | 16.7739 | 16.5068 | 16.7487 | 16.821 | 17.3209 | 18.0091 | 15.5507 | 16.8726 | 16.1786 | 16.89 | 17.8906 | 44.4361 | 47.5351 | 43.5424 | 21.3442 |  |  | 0.42801 | -0.24977 | -51.98 | 0.54471 | 0.15981 | -197.8434 | 9.351 | -0.28752 | -0.067433 | 0.13124 | 0.048899 | 8.8277 | 9.0575 | 1.9793 | 21.7842 | 22.0078 | 22.2074 | 22.2743 | 22.1015 | 21.4215 | 20.2369 | 22.208 | 22.3789 | 22.4073 | 22.3649 | 21.9932 | 21.2245 | 22.2747 | 17.5973 | 17.1429 | 16.2796 | 16.2988 | 16.3544 | 17.0912 | 16.8628 | 22.3766 | 22.1447 | 21.7118 | 22.0873 | 21.801 | 21.3135 | 21.9502 | 21.5362 | 20.9157 | 20.1158 | 20.3189 | 19.8601 | 19.7603 | 0.14097 | 0.051005 | 20.7464 | 22.0762 | 22.3895 | 20.1092 | 21.6815 | 22.1186 | 21.9583 | 21.7205 | 21.2914 | 21.7905 | 21.4618 | 21.0633 | 20.2436 | 20.2963 | 20.2447 | 20.2235 | 20.1051 |  | 20.2166 | 19.7903 | 20.1129 | 19.7059 | 20.087 | 20.3387 |  | 20.4184 |  |  | 20.2969 | 20.3907 | 20.6249 | [5 empty] | 21.9471 | 20.3378 | 21.6822 | 22.0644 | 19.5489 | 21.1901 | 21.8115 | 19.353 | 19.8936 | 21.1216 |  | 19.7409 | 20.9132 | 18.8884 | 19.7213 | 20.8213 | 19.4843 | 20.0427 | 19.0806 | 20.126 | 19.1479 | 20.2243 | 18.846 | 20.0599 | 21.0235 | 19.376 | 19.7729 | 20.9673 | 18.9351 | 19.8139 | 20.8035 | 19.0078 | 20.1218 | 19.2984 | 19.9093 | 18.8994 | 20.1408 | -0.13573 | 20.9471 | 0.049101 | 0.013279 | -27.0775 | 3.0973 | -3.92 | -0.05 | 0.78111 | -0.59303 | -8.5551 | 0.87577 | 0.47481 | -16.7063 | 3.632 | 0.42307 | 0.42835 | 0.42982 | 0.34613 | 0.4659 | 0.43962 | 0.42928
42838.4169 | -291 | 22.9015 | 22.8756 | 22.8646 | 22.7833 | 22.4166 | 21.7519 | 22.7201 | 21.8118 | 22.3707 | 22.3777 | 22.3594 | 22.037 | 21.2654 | 22.2311 | 21.58 | 21.7479 | 21.8781 | 21.0702 | 21.1638 | 21.3897 | 20.4778 | 20.606 | 20.9011 | 21.879 | 21.6494 | 21.2782 | 20.2841 | 20.3844 | 20.3674 | 22.0442 | 21.6566 | 21.1795 | 21.9907 | 21.7233 | 21.3443 | 19.9201 | 20.4332 |  | 20.5239 | 20.0495 | 20.1563 | 19.1679 |  | 16.7766 | 16.7755 | 16.4983 | 16.7475 | 16.8269 | 17.316 | 17.9973 | 15.5684 | 16.8705 | 16.1891 | 16.8831 | 17.8994 | 44.4477 | 47.5528 | 43.5472 | 21.3554 |  |  | 0.3669 | -0.28788 | -51.8709 | 0.10049 | 0.21501 | -197.888 | 9.9063 | -0.19092 | 0.014494 | 0.12431 | 0.039178 | 8.8277 | 9.0574 | 1.9791 | 21.7853 | 22.0076 | 22.2021 | 22.2751 | 22.0992 | 21.4206 | 20.2334 | 22.1995 | 22.3737 | 22.4067 | 22.3613 | 21.9895 | 21.2216 | 22.2699 | 17.5746 | 17.1826 | 16.2581 | 16.2862 | 16.3432 | 17.0902 | 16.8571 | 22.3787 | 22.1494 | 21.713 | 22.0849 | 21.8 | 21.3135 | 21.9479 | 21.5344 | 20.9137 | 20.112 | 20.3203 | 19.858 | 19.7609 | -0.07332 | -0.03858 | 20.7497 | 22.0741 | 22.3828 | 20.1057 | 21.6782 | 22.1205 | 21.9497 | 21.7242 | 21.2932 | 21.7894 | 21.4567 | 21.0595 | 20.2355 | 20.2868 | 20.2385 | 20.2206 | 20.0955 |  | 20.2248 | 19.7737 | 20.1072 | 19.6986 | 20.0922 | 20.336 |  | 20.4183 |  |  | 20.2902 | 20.3885 | 20.6222 | [5 empty] | 21.9487 | 20.3367 | 21.6775 | 22.0657 | 19.5498 | 21.1842 | 21.8151 | 19.3524 | 19.8921 | 21.1216 |  | 19.7348 | 20.9088 | 18.8928 | 19.7239 | 20.8201 | 19.4898 | 20.0412 | 19.0788 | 20.1233 | 19.1432 | 20.2274 | 18.8316 | 20.047 | 21.023 | 19.3625 | 19.7591 | 20.961 | 18.9264 | 19.8053 | 20.7907 | 19.005 | 20.1121 | 19.2905 | 19.9022 | 18.8855 | 20.1326 | -0.11607 | 20.9478 | 0.048708 | 0.013511 | -27.0735 | 3.0973 | -6.46 | -0.04 | 0.7232 | -0.63667 | -8.5462 | 0.37617 | 0.55073 | -16.708 | 3.7383 | 0.42362 | 0.42861 | 0.4302 | 0.34854 | 0.46762 | 0.43917 | 0.42913
42838.4169 | -290 | 22.8914 | 22.8654 | 22.8512 | 22.7709 | 22.4037 | 21.7421 | 22.7144 | 21.8079 | 22.3618 | 22.3722 | 22.3548 | 22.0334 | 21.2511 | 22.2187 | 21.5834 | 21.7442 | 21.876 | 21.0725 | 21.1655 | 21.3814 | 20.4736 | 20.6051 | 20.9028 | 21.875 | 21.6384 | 21.2757 | 20.2847 | 20.3882 | 20.3562 | 22.0589 | 21.67 | 21.1821 | 21.9948 | 21.7405 | 21.3568 | 19.9257 | 20.4408 |  | 20.5155 | 20.0486 | 20.1691 | 19.1761 |  | 16.7782 | 16.7727 | 16.502 | 16.7451 | 16.8272 | 17.3151 | 17.9836 | 15.6527 | 16.8671 | 16.2115 | 16.8812 | 17.8907 | 44.4394 | 47.5472 | 43.5383 | 21.3494 |  |  | 0.47335 | -0.38382 | -51.5883 | -0.37197 | 0.48246 | -197.7829 | 9.445 | -0.17318 | -0.013723 | -0.11129 | -0.074183 | 8.8278 | 9.0575 | 1.9785 | 21.7899 | 22.0096 | 22.2093 | 22.2701 | 22.0975 | 21.4203 | 20.2374 | 22.1988 | 22.3732 | 22.41 | 22.3644 | 21.9921 | 21.2277 | 22.2705 | 17.5476 | 17.1825 | 16.2541 | 16.2563 | 16.3362 | 17.0919 | 16.8615 | 22.3806 | 22.1434 | 21.703 | 22.0789 | 21.7972 | 21.3048 | 21.9452 | 21.5261 | 20.9039 | 20.108 | 20.3195 | 19.8476 | 19.7632 | 0.028323 | 0.015247 | 20.7436 | 22.072 | 22.3783 | 20.0979 | 21.6664 | 22.1201 | 21.9444 | 21.7114 | 21.2807 | 21.7853 | 21.4511 | 21.0495 | 20.2262 | 20.2822 | 20.2346 | 20.2117 | 20.0965 |  | 20.2305 | 19.7706 | 20.12 | 19.6979 | 20.0963 | 20.3411 |  | 20.4203 |  |  | 20.3002 | 20.3884 | 20.6184 | [5 empty] | 21.9492 | 20.3437 | 21.6866 | 22.0636 | 19.5508 | 21.1842 | 21.8205 | 19.353 | 19.898 | 21.124 |  | 19.7363 | 20.9122 | 18.8844 | 19.7232 | 20.8192 | 19.4876 | 20.0435 | 19.0796 | 20.1171 | 19.1468 | 20.2348 | 18.8308 | 20.0502 | 21.0235 | 19.368 | 19.7684 | 20.9659 | 18.9285 | 19.8124 | 20.7962 | 19.0052 | 20.1155 | 19.2859 | 19.9057 | 18.8959 | 20.1353 | -0.063574 | 20.9484 | 0.048917 | 0.013976 | -27.1013 | 3.0973 | 5.87 | -0.02 | 0.82143 | -0.73514 | -8.5228 | -0.72371 | 0.82498 | -16.7035 | 3.6502 | 0.42378 | 0.42913 | 0.43036 | 0.35173 | 0.46858 | 0.43914 | 0.42893
42838.4169 | -289 | 22.8936 | 22.8641 | 22.845 | 22.7707 | 22.4105 | 21.746 | 22.7154 | 21.8106 | 22.3702 | 22.3811 | 22.3579 | 22.0323 | 21.2568 | 22.2198 | 21.5826 | 21.7568 | 21.8934 | 21.0815 | 21.1789 | 21.3928 | 20.4753 | 20.6142 | 20.9064 | 21.8848 | 21.6547 | 21.2829 | 20.2908 | 20.3982 | 20.3713 | 22.0605 | 21.6634 | 21.1908 | 21.9904 | 21.7415 | 21.3533 | 19.9191 | 20.4369 |  | 20.5272 | 20.0568 | 20.1753 | 19.1721 |  | 16.777 | 16.7635 | 16.4973 | 16.7503 | 16.8255 | 17.3022 | 17.942 | 15.707 | 16.8701 | 16.1781 | 16.8865 | 17.8886 | 44.4486 | 47.5515 | 43.5262 | 21.3467 |  |  | 0.4497 | -0.26357 | -51.2663 | 0.22863 | 0.25641 | -197.8979 | 9.8366 | -0.19355 | 0.16395 | 0.14173 | -0.06776 | 8.8279 | 9.0575 | 1.9779 | 21.7821 | 22.0151 | 22.2065 | 22.2753 | 22.0954 | 21.4242 | 20.2393 | 22.2013 | 22.3782 | 22.4152 | 22.3667 | 22.0013 | 21.2277 | 22.2708 | 17.5231 | 17.1398 | 16.2423 | 16.2351 | 16.3313 | 17.0929 | 16.8664 | 22.3838 | 22.1403 | 21.7 | 22.0899 | 21.8075 | 21.3142 | 21.9514 | 21.5316 | 20.9156 | 20.1075 | 20.3296 | 19.8614 | 19.7627 | 0.0009952 | 0.10673 | 20.7424 | 22.0734 | 22.3817 | 20.1048 | 21.6752 | 22.1211 | 21.9506 | 21.7167 | 21.2795 | 21.7925 | 21.4541 | 21.0566 | 20.2317 | 20.2946 | 20.2397 | 20.2146 | 20.0918 |  | 20.2272 | 19.7648 | 20.1206 | 19.6857 | 20.0954 | 20.3372 |  | 20.4248 |  |  | 20.3016 | 20.3805 | 20.6203 | [5 empty] | 21.9399 | 20.3441 | 21.6769 | 22.0671 | 19.543 | 21.1818 | 21.8101 | 19.3499 | 19.8959 | 21.119 |  | 19.7369 | 20.9108 | 18.8698 | 19.7146 | 20.8163 | 19.4772 | 20.0402 | 19.0697 | 20.1152 | 19.1447 | 20.2237 | 18.8262 | 20.0585 | 21.0236 | 19.3661 | 19.7706 | 20.964 | 18.9413 | 19.8173 | 20.8051 | 19.0086 | 20.1222 | 19.2988 | 19.908 | 18.893 | 20.14 | -0.14556 | 20.9471 | 0.04931 | 0.01431 | -27.1315 | 3.0973 | 2.19 | -0.25 | 0.80066 | -0.60918 | -8.4961 | 0.56738 | 0.60141 | -16.708 | 3.725 | 0.4238 | 0.42931 | 0.43066 | 0.35458 | 0.47047 | 0.43903 | 0.42893
42838.4169 | -288 | 22.9023 | 22.8648 | 22.8491 | 22.7815 | 22.4068 | 21.7473 | 22.7158 | 21.8153 | 22.3698 | 22.3848 | 22.3597 | 22.0353 | 21.2523 | 22.2266 | 21.5755 | 21.7573 | 21.8826 | 21.0749 | 21.1747 | 21.3914 | 20.469 | 20.6169 | 20.9014 | 21.8818 | 21.643 | 21.277 | 20.2809 | 20.3859 | 20.3665 | 22.0566 | 21.6583 | 21.1841 | 21.9869 | 21.7287 | 21.356 | 19.9114 | 20.4402 |  | 20.5234 | 20.0564 | 20.1701 | 19.1648 |  | 16.7757 | 16.7602 | 16.4896 | 16.75 | 16.8253 | 17.2825 | 17.8991 | 15.7904 | 16.8662 | 16.1545 | 16.8898 | 17.8924 | 44.4515 | 47.5589 | 43.5212 | 21.3482 |  |  | 0.28673 | -0.29248 | -50.9989 | 0.50922 | -0.007096 | -197.8112 | 9.8268 | -0.11864 | -0.13924 | 0.086339 | -0.08321 | 8.8287 | 9.0584 | 1.9786 | 21.7808 | 22.0036 | 22.1911 | 22.2688 | 22.0901 | 21.417 | 20.2283 | 22.1961 | 22.3725 | 22.4026 | 22.3513 | 21.9862 | 21.2165 | 22.2638 | 17.4828 | 17.1023 | 16.1928 | 16.2214 | 16.3055 | 17.0937 | 16.863 | 22.3807 | 22.144 | 21.7041 | 22.083 | 21.8 | 21.3044 | 21.9481 | 21.5261 | 20.9142 | 20.114 | 20.3256 | 19.8591 | 19.764 | 0.050342 | 0.042826 | 20.738 | 22.0693 | 22.379 | 20.1075 | 21.6752 | 22.1187 | 21.954 | 21.7235 | 21.283 | 21.7927 | 21.4512 | 21.0554 | 20.2335 | 20.2904 | 20.2345 | 20.2163 | 20.0867 |  | 20.2196 | 19.7636 | 20.1161 | 19.6784 | 20.0955 | 20.3416 |  | 20.4294 |  |  | 20.2992 | 20.3827 | 20.6207 | [5 empty] | 21.9434 | 20.3445 | 21.6747 | 22.0629 | 19.5428 | 21.1811 | 21.8067 | 19.3499 | 19.903 | 21.1213 |  | 19.7374 | 20.9147 | 18.8695 | 19.7229 | 20.8211 | 19.4862 | 20.0477 | 19.0686 | 20.1187 | 19.1461 | 20.2193 | 18.8292 | 20.0725 | 21.0386 | 19.3849 | 19.7636 | 20.9734 | 18.9376 | 19.8166 | 20.7999 | 19.0146 | 20.1207 | 19.2971 | 19.9202 | 18.9015 | 20.1402 | -0.066541 | 20.948 | 0.048886 | 0.013881 | -27.0751 | 3.0973 | 12.24 | -0.15 | 0.63933 | -0.64172 | -8.4738 | 0.84674 | -0.10005 | -16.7038 | 3.723 | 0.42369 | 0.4292 | 0.43087 | 0.35914 | 0.47557 | 0.43897 | 0.42911
42838.417 | -287 | 22.9004 | 22.8638 | 22.8527 | 22.7813 | 22.4063 | 21.7496 | 22.7171 | 21.8173 | 22.3689 | 22.3825 | 22.3629 | 22.0373 | 21.2558 | 22.2243 | 21.5748 | 21.7438 | 21.8948 | 21.0684 | 21.1667 | 21.3883 | 20.4638 | 20.5982 | 20.9052 | 21.8838 | 21.6443 | 21.274 | 20.2775 | 20.3822 | 20.3642 | 22.0549 | 21.657 | 21.1796 | 21.9836 | 21.7245 | 21.3489 | 19.9104 | 20.4404 |  | 20.5172 | 20.0545 | 20.1635 | 19.161 |  | 16.7794 | 16.7589 | 16.4923 | 16.7462 | 16.8067 | 17.2623 | 17.853 | 15.8458 | 16.8684 | 16.1025 | 16.8946 | 17.8991 | 44.455 | 47.5667 | 43.5228 | 21.3566 |  |  | 0.37413 | -0.097317 | -50.6769 | 0.71621 | 0.10987 | -197.821 | 10.112 | -0.19487 | -0.13807 | 0.017944 | -0.038595 | 8.8291 | 9.0589 | 1.9794 | 21.7892 | 22.0081 | 22.2043 | 22.2713 | 22.106 | 21.4226 | 20.2382 | 22.2008 | 22.3803 | 22.4052 | 22.3584 | 21.9905 | 21.2239 | 22.2712 | 17.4221 | 17.1032 | 16.1262 | 16.1918 | 16.2793 | 17.0838 | 16.8589 | 22.3808 | 22.1453 | 21.7089 | 22.0869 | 21.8051 | 21.3057 | 21.9452 | 21.5295 | 20.9184 | 20.1157 | 20.3234 | 19.8583 | 19.7718 | 0.04641 | 0.0078292 | 20.7283 | 22.0632 | 22.3767 | 20.1057 | 21.6697 | 22.116 | 21.949 | 21.7202 | 21.2805 | 21.7804 | 21.4495 | 21.0463 | 20.2257 | 20.2813 | 20.2258 | 20.2099 | 20.0839 |  | 20.2271 | 19.757 | 20.116 | 19.6753 | 20.0985 | 20.34 |  | 20.4217 |  |  | 20.2871 | 20.3747 | 20.6127 | [5 empty] | 21.9293 | 20.3417 | 21.6731 | 22.0581 | 19.5346 | 21.1841 | 21.8019 | 19.3537 | 19.907 | 21.1411 |  | 19.7343 | 20.9219 | 18.8761 | 19.7327 | 20.8148 | 19.4852 | 20.056 | 19.0695 | 20.1167 | 19.1492 | 20.2335 | 18.8133 | 20.0603 | 21.0216 | 19.3746 | 19.7653 | 20.9751 | 18.929 | 19.8089 | 20.8067 | 19.0151 | 20.1182 | 19.2934 | 19.9122 | 18.9025 | 20.1444 | -0.2116 | 20.9484 | 0.048911 | 0.013468 | -27.0401 | 3.0973 | 18.62 | -0.03 | 0.73029 | -0.37016 | -8.447 | 1.0042 | 0.39365 | -16.7036 | 3.7765 | 0.42402 | 0.42937 | 0.43106 | 0.36474 | 0.48249 | 0.43904 | 0.42895
42838.417 | -286 | 22.8957 | 22.8624 | 22.8497 | 22.7719 | 22.4044 | 21.7374 | 22.7065 | 21.8093 | 22.3618 | 22.3742 | 22.3528 | 22.025 | 21.2504 | 22.2231 | 21.5873 | 21.7637 | 21.8867 | 21.0783 | 21.1765 | 21.3904 | 20.4816 | 20.6202 | 20.9032 | 21.8816 | 21.6495 | 21.2791 | 20.2838 | 20.3942 | 20.3585 | 22.0569 | 21.6583 | 21.1767 | 21.9894 | 21.733 | 21.3521 | 19.9075 | 20.4447 |  | 20.5194 | 20.054 | 20.1664 | 19.1538 |  | 16.7744 | 16.7585 | 16.4791 | 16.7248 | 16.7847 | 17.2303 | 17.7993 | 15.8877 | 16.8739 | 16.035 | 16.8921 | 17.8946 | 44.4349 | 47.5684 | 43.5257 | 21.3469 |  |  | 0.37019 | 0.059731 | -50.3326 | 0.63341 | -0.11946 | -197.8526 | 9.9707 | -0.089072 | -0.094482 | 0.050463 | 0.099764 | 8.8288 | 9.0584 | 1.9795 | 21.7826 | 22.0113 | 22.2034 | 22.2677 | 22.0984 | 21.4207 | 20.2351 | 22.2041 | 22.3768 | 22.4081 | 22.3586 | 21.9943 | 21.223 | 22.2746 | 17.3816 | 17.0729 | 16.0974 | 16.1799 | 16.2756 | 17.0968 | 16.8672 | 22.3886 | 22.1588 | 21.7152 | 22.0809 | 21.8044 | 21.3107 | 21.949 | 21.5259 | 20.9153 | 20.1192 | 20.3314 | 19.8629 | 19.7823 | 0.12937 | 0.081056 | 20.727 | 22.0605 | 22.3738 | 20.0973 | 21.6694 | 22.1135 | 21.9462 | 21.7102 | 21.2808 | 21.7847 | 21.4514 | 21.0459 | 20.2229 | 20.2836 | 20.2288 | 20.2103 | 20.0867 |  | 20.2276 | 19.7548 | 20.1184 | 19.6785 | 20.101 | 20.3379 |  | 20.4283 |  |  | 20.2999 | 20.3784 | 20.623 | [5 empty] | 21.9474 | 20.352 | 21.6854 | 22.0695 | 19.5442 | 21.1801 | 21.8155 | 19.3586 | 19.9095 | 21.1246 |  | 19.7379 | 20.9184 | 18.8675 | 19.7163 | 20.8129 | 19.4943 | 20.0516 | 19.0668 | 20.1218 | 19.1477 | 20.2232 | 18.8114 | 20.0622 | 21.021 | 19.3663 | 19.7532 | 20.9646 | 18.9153 | 19.8093 | 20.7901 | 19.0173 | 20.1158 | 19.294 | 19.9088 | 18.8939 | 20.1344 | -0.19194 | 20.9472 | 0.04896 | 0.013707 | -27.1506 | 3.0973 | -17.67 | -0.07 | 0.72642 | 0.29 | -8.4183 | 0.94437 | -0.41046 | -16.704 | 3.7498 | 0.42395 | 0.42952 | 0.43105 | 0.37075 | 0.48666 | 0.43914 | 0.42878
42838.417 | -285 | 22.8959 | 22.8645 | 22.8539 | 22.7709 | 22.4059 | 21.7469 | 22.7122 | 21.8119 | 22.3712 | 22.3747 | 22.3577 | 22.0361 | 21.2617 | 22.223 | 21.5908 | 21.762 | 21.896 | 21.0726 | 21.1723 | 21.3927 | 20.4822 | 20.6232 | 20.9131 | 21.8891 | 21.653 | 21.2918 | 20.2958 | 20.3953 | 20.3689 | 22.0584 | 21.6643 | 21.1861 | 21.9916 | 21.736 | 21.3534 | 19.923 | 20.442 |  | 20.5192 | 20.0564 | 20.1633 | 19.1552 |  | 16.7776 | 16.7606 | 16.4797 | 16.7126 | 16.7761 | 17.2135 | 17.7592 | 15.9278 | 16.8699 | 16.0041 | 16.8895 | 17.8943 | 44.4217 | 47.5772 | 43.5232 | 21.3503 |  |  | 0.55878 | -0.23137 | -49.8056 | 0.60253 | 0.029044 | -197.8177 | 10.5936 | -0.24349 | -0.070741 | 0.12305 | 0.000812 | 8.828 | 9.0578 | 1.9788 | 21.7915 | 22.0106 | 22.2017 | 22.2728 | 22.1027 | 21.4223 | 20.2417 | 22.2044 | 22.3742 | 22.4067 | 22.3621 | 21.9943 | 21.2223 | 22.2778 | 17.3198 | 17.0752 | 16.0737 | 16.1582 | 16.2633 | 17.0944 | 16.8631 | 22.3786 | 22.1537 | 21.7159 | 22.0877 | 21.8048 | 21.3124 | 21.9503 | 21.5359 | 20.9058 | 20.1076 | 20.3363 | 19.8557 | 19.7895 | 0.096936 | 0.18262 | 20.7314 | 22.0683 | 22.3759 | 20.0964 | 21.6674 | 22.1196 | 21.9484 | 21.7122 | 21.2852 | 21.7987 | 21.4575 | 21.0471 | 20.2254 | 20.2949 | 20.2363 | 20.2166 | 20.0873 |  | 20.2193 | 19.7555 | 20.1132 | 19.6733 | 20.0931 | 20.3275 |  | 20.4126 |  |  | 20.2913 | 20.3751 | 20.6225 | [5 empty] | 21.9471 | 20.3385 | 21.6767 | 22.0601 | 19.5399 | 21.1797 | 21.8055 | 19.3598 | 19.906 | 21.1384 |  | 19.7424 | 20.922 | 18.8649 | 19.7243 | 20.8175 | 19.4986 | 20.0493 | 19.0671 | 20.1169 | 19.1552 | 20.2282 | 18.8268 | 20.0661 | 21.0347 | 19.3834 | 19.7677 | 20.9754 | 18.9205 | 19.8244 | 20.8061 | 19.0275 | 20.1173 | 19.3009 | 19.923 | 18.9001 | 20.1393 | -0.069695 | 20.9476 | 0.049046 | 0.01346 | -27.0448 | 3.0973 | -5.42 | -0.19 | 0.89249 | -0.57076 | -8.3741 | 0.92106 | 0.20238 | -16.7021 | 3.8651 | 0.42366 | 0.42932 | 0.43093 | 0.37734 | 0.48881 | 0.43963 | 0.42819
42838.417 | -284 | 22.8844 | 22.8493 | 22.8359 | 22.7668 | 22.397 | 21.7404 | 22.7104 | 21.8012 | 22.3635 | 22.3798 | 22.3471 | 22.0247 | 21.2468 | 22.2204 | 21.5906 | 21.7602 | 21.895 | 21.078 | 21.1747 | 21.3857 | 20.4833 | 20.62 | 20.9095 | 21.8872 | 21.659 | 21.2841 | 20.2867 | 20.3938 | 20.3681 | 22.0559 | 21.6504 | 21.185 | 21.9946 | 21.7238 | 21.3437 | 19.9151 | 20.4394 |  | 20.515 | 20.0477 | 20.1574 | 19.1369 |  | 16.7888 | 16.769 | 16.4671 | 16.7006 | 16.7388 | 17.1978 | 17.7376 | 15.9704 | 16.876 | 16.0226 | 16.8902 | 17.8934 | 44.4084 | 47.5771 | 43.5117 | 21.3448 |  |  | 0.42407 | -0.35951 | -49.3929 | 0.56113 | 0.073072 | -197.8164 | 10.9288 | -0.24481 | 0.037651 | 0.079416 | 0.0013328 | 8.8276 | 9.0572 | 1.9784 | 21.7913 | 22.0148 | 22.2074 | 22.2726 | 22.1013 | 21.4241 | 20.2352 | 22.2046 | 22.3789 | 22.4112 | 22.3589 | 21.997 | 21.2263 | 22.2777 | 17.2592 | 17.0331 | 16.051 | 16.1325 | 16.2583 | 17.0856 | 16.8664 | 22.383 | 22.1559 | 21.7138 | 22.0874 | 21.8013 | 21.3132 | 21.9519 | 21.5366 | 20.9149 | 20.1077 | 20.3302 | 19.8627 | 19.8053 | 0.15592 | 0.15314 | 20.7314 | 22.0744 | 22.3804 | 20.1039 | 21.6738 | 22.1265 | 21.9551 | 21.7189 | 21.2885 | 21.7955 | 21.46 | 21.0536 | 20.225 | 20.2992 | 20.2368 | 20.2249 | 20.1022 |  | 20.2205 | 19.7614 | 20.1179 | 19.679 | 20.0906 | 20.332 |  | 20.4279 |  |  | 20.2962 | 20.3793 | 20.6264 | [5 empty] | 21.9506 | 20.3415 | 21.6878 | 22.0616 | 19.5434 | 21.1867 | 21.8157 | 19.3729 | 19.9095 | 21.1416 |  | 19.7389 | 20.9217 | 18.8667 | 19.7277 | 20.811 | 19.4962 | 20.0513 | 19.0658 | 20.1256 | 19.1564 | 20.2294 | 18.8238 | 20.0548 | 21.0271 | 19.3747 | 19.7618 | 20.9701 | 18.9181 | 19.8121 | 20.7957 | 19.0239 | 20.1115 | 19.3048 | 19.929 | 18.8883 | 20.1337 | -0.0159 | 20.9476 | 0.049611 | 0.013337 | -27.0582 | 3.0972 | -7.19 | -0.11 | 0.7775 | -0.71148 | -8.3395 | 0.88887 | 0.321 | -16.7016 | 3.9257 | 0.42329 | 0.42931 | 0.43069 | 0.38304 | 0.49172 | 0.43987 | 0.42775
42838.417 | -283 | 22.8933 | 22.8523 | 22.84 | 22.7689 | 22.3996 | 21.739 | 22.7062 | 21.7946 | 22.3611 | 22.3792 | 22.3517 | 22.0267 | 21.2482 | 22.2181 | 21.5797 | 21.7442 | 21.8846 | 21.071 | 21.1717 | 21.3784 | 20.4717 | 20.6109 | 20.9067 | 21.8778 | 21.6455 | 21.2792 | 20.2793 | 20.3899 | 20.357 | 22.0521 | 21.6479 | 21.1787 | 21.9839 | 21.7282 | 21.3426 | 19.9075 | 20.4313 |  | 20.5121 | 20.0381 | 20.1557 | 19.1311 |  | 16.8036 | 16.7609 | 16.4561 | 16.6759 | 16.7205 | 17.1683 | 17.7219 | 15.9897 | 16.8646 | 16.0602 | 16.8898 | 17.9004 | 44.4111 | 47.5888 | 43.4989 | 21.3506 |  |  | 0.51869 | -0.37265 | -49.5 | 0.48031 | 0.16901 | -197.8243 | 9.9884 | -0.43734 | -0.18341 | -0.12724 | -0.03981 | 8.8284 | 9.0582 | 1.9784 | 21.7851 | 22.0079 | 22.2055 | 22.2645 | 22.097 | 21.4222 | 20.2378 | 22.2 | 22.3713 | 22.4071 | 22.3616 | 21.9882 | 21.2268 | 22.2737 | 17.2116 | 17.0948 | 16.0606 | 16.1239 | 16.2492 | 17.0897 | 16.8708 | 22.3799 | 22.1488 | 21.706 | 22.0894 | 21.7984 | 21.3087 | 21.9471 | 21.5343 | 20.9098 | 20.1092 | 20.3192 | 19.8578 | 19.8039 | 0.1105 | -0.074337 | 20.7304 | 22.0683 | 22.3748 | 20.1027 | 21.6721 | 22.1238 | 21.9574 | 21.7181 | 21.2864 | 21.7862 | 21.4544 | 21.058 | 20.2219 | 20.2942 | 20.2272 | 20.2272 | 20.0992 |  | 20.2214 | 19.7566 | 20.1159 | 19.6901 | 20.1009 | 20.332 |  | 20.4263 |  |  | 20.2963 | 20.377 | 20.6222 | [5 empty] | 21.9448 | 20.3386 | 21.6836 | 22.062 | 19.5371 | 21.185 | 21.8097 | 19.3565 | 19.903 | 21.1347 |  | 19.7366 | 20.9103 | 18.8681 | 19.7214 | 20.8066 | 19.4923 | 20.0429 | 19.0512 | 20.1148 | 19.1463 | 20.22 | 18.8277 | 20.057 | 21.0285 | 19.3809 | 19.7605 | 20.9744 | 18.9232 | 19.8164 | 20.8049 | 19.0349 | 20.116 | 19.3145 | 19.9251 | 18.8944 | 20.1402 | -0.080083 | 20.9472 | 0.050091 | 0.013446 | -27.0661 | 3.0972 | -8.32 | -0.16 | 0.85987 | -0.72435 | -8.3484 | 0.82235 | 0.48816 | -16.7011 | 3.7528 | 0.4234 | 0.42938 | 0.43073 | 0.3888 | 0.49117 | 0.43978 | 0.42784
42838.417 | -282 | 22.899 | 22.8648 | 22.8504 | 22.7754 | 22.4104 | 21.7412 | 22.7152 | 21.813 | 22.3646 | 22.3824 | 22.3564 | 22.031 | 21.2512 | 22.2177 | 21.5807 | 21.7507 | 21.8872 | 21.0773 | 21.167 | 21.3892 | 20.4682 | 20.6133 | 20.9054 | 21.8803 | 21.6489 | 21.2754 | 20.2863 | 20.3879 | 20.3566 | 22.0613 | 21.6636 | 21.187 | 21.988 | 21.7383 | 21.3579 | 19.9178 | 20.4486 |  | 20.5227 | 20.058 | 20.1729 | 19.1281 |  | 16.8182 | 16.7657 | 16.4516 | 16.6673 | 16.7305 | 17.1638 | 17.7467 | 16.0105 | 16.8592 | 16.1636 | 16.8902 | 17.8998 | 44.4099 | 47.5996 | 43.4887 | 21.3545 |  |  | 0.55615 | -0.55927 | -49.893 | 0.29697 | 0.27546 | -197.8453 | 10.3577 | -0.44851 | -0.2021 | -0.24053 | 0.080321 | 8.8282 | 9.0582 | 1.9795 | 21.784 | 22.0073 | 22.1979 | 22.2686 | 22.0909 | 21.4155 | 20.2329 | 22.1922 | 22.3695 | 22.4101 | 22.3574 | 21.9922 | 21.2207 | 22.2673 | 17.1598 | 17.0982 | 16.0854 | 16.1356 | 16.2425 | 17.0961 | 16.8756 | 22.3844 | 22.1465 | 21.7078 | 22.0911 | 21.8035 | 21.309 | 21.9519 | 21.5318 | 20.9114 | 20.1139 | 20.328 | 19.8569 | 19.8086 | 0.2031 | 0.062226 | 20.7349 | 22.0697 | 22.3774 | 20.1012 | 21.6784 | 22.1223 | 21.955 | 21.717 | 21.2831 | 21.7892 | 21.4512 | 21.0589 | 20.2204 | 20.2952 | 20.2269 | 20.2262 | 20.0845 |  | 20.2251 | 19.7621 | 20.1149 | 19.6802 | 20.0985 | 20.3371 |  | 20.423 |  |  | 20.3016 | 20.3732 | 20.6239 | [5 empty] | 21.949 | 20.3468 | 21.6859 | 22.0635 | 19.5371 | 21.1896 | 21.8109 | 19.359 | 19.9099 | 21.1345 |  | 19.7389 | 20.9169 | 18.8741 | 19.7279 | 20.8179 | 19.4964 | 20.0517 | 19.0517 | 20.119 | 19.1531 | 20.2315 | 18.825 | 20.0627 | 21.0285 | 19.3806 | 19.764 | 20.9679 | 18.929 | 19.8213 | 20.8034 | 19.0315 | 20.1112 | 19.3049 | 19.9237 | 18.8949 | 20.1465 | 0.13473 | 20.9468 | 0.049777 | 0.012713 | -27.0866 | 3.0972 | -15.62 | -0.07 | 0.89037 | -0.88739 | -8.3815 | 0.64664 | 0.62321 | -16.7018 | 3.8215 | 0.42393 | 0.42919 | 0.43092 | 0.39531 | 0.48897 | 0.4402 | 0.42787
42838.417 | -281 | 22.8961 | 22.8636 | 22.8515 | 22.773 | 22.4072 | 21.7498 | 22.7156 | 21.8072 | 22.3677 | 22.3767 | 22.3592 | 22.0309 | 21.2538 | 22.2169 | 21.5894 | 21.7527 | 21.8842 | 21.0772 | 21.1703 | 21.3938 | 20.4729 | 20.6109 | 20.9083 | 21.8852 | 21.6519 | 21.2849 | 20.287 | 20.3875 | 20.3538 | 22.0616 | 21.6671 | 21.1832 | 21.9977 | 21.7407 | 21.3551 | 19.9225 | 20.4517 |  | 20.5233 | 20.0582 | 20.1666 | 19.1295 |  | 16.819 | 16.769 | 16.4461 | 16.6655 | 16.7498 | 17.1704 | 17.7784 | 16.0568 | 16.8628 | 16.2679 | 16.8883 | 17.8999 | 44.404 | 47.6081 | 43.4775 | 21.3507 |  |  | 0.36756 | -0.079577 | -50.0185 | 0.13007 | 0.11053 | -197.8177 | 10.5253 | -0.56614 | -0.39047 | -0.2785 | -0.022103 | 8.8299 | 9.0595 | 1.9792 | 21.7859 | 22.007 | 22.2039 | 22.2684 | 22.1013 | 21.4169 | 20.2325 | 22.2001 | 22.3714 | 22.4077 | 22.3554 | 21.9907 | 21.2186 | 22.2638 | 17.1071 | 17.1579 | 16.088 | 16.132 | 16.2337 | 17.0906 | 16.8724 | 22.3897 | 22.1443 | 21.7112 | 22.089 | 21.8011 | 21.3178 | 21.9505 | 21.5291 | 20.9074 | 20.1182 | 20.3262 | 19.8632 | 19.8074 | 0.1339 | -0.012332 | 20.7413 | 22.0728 | 22.3737 | 20.0929 | 21.6749 | 22.1234 | 21.9544 | 21.718 | 21.2769 | 21.7906 | 21.4484 | 21.0549 | 20.2244 | 20.3011 | 20.2314 | 20.2204 | 20.0947 |  | 20.2216 | 19.7731 | 20.1181 | 19.6806 | 20.0872 | 20.3305 |  | 20.4222 |  |  | 20.3028 | 20.3753 | 20.6305 | [5 empty] | 21.9517 | 20.353 | 21.6839 | 22.066 | 19.5357 | 21.1895 | 21.8085 | 19.361 | 19.9111 | 21.1363 |  | 19.7399 | 20.9159 | 18.8703 | 19.7233 | 20.8166 | 19.4974 | 20.0497 | 19.0438 | 20.1166 | 19.1536 | 20.2288 | 18.8253 | 20.0687 | 21.0339 | 19.3838 | 19.7635 | 20.9733 | 18.9261 | 19.8247 | 20.8128 | 19.0328 | 20.1178 | 19.3075 | 19.9226 | 18.897 | 20.1504 | -0.15966 | 20.947 | 0.049231 | 0.013438 | -27.1504 | 3.0972 | -4.73 | -0.02 | 0.72383 | -0.33473 | -8.3921 | 0.42794 | 0.39477 | -16.7008 | 3.8523 | 0.42353 | 0.429 | 0.43053 | 0.40053 | 0.4883 | 0.44032 | 0.42805
42838.417 | -280 | 22.9025 | 22.8651 | 22.854 | 22.7732 | 22.4146 | 21.7534 | 22.718 | 21.8109 | 22.3776 | 22.3804 | 22.3633 | 22.0384 | 21.2579 | 22.2185 | 21.5844 | 21.7463 | 21.8805 | 21.0772 | 21.1744 | 21.3906 | 20.4737 | 20.608 | 20.9064 | 21.8818 | 21.6473 | 21.2852 | 20.28 | 20.3882 | 20.3537 | 22.0616 | 21.6602 | 21.1809 | 21.9921 | 21.7369 | 21.3507 | 19.9148 | 20.4468 |  | 20.5202 | 20.0501 | 20.1632 | 19.1169 |  | 16.8119 | 16.7572 | 16.4393 | 16.6681 | 16.7713 | 17.1958 | 17.8056 | 16.0619 | 16.8693 | 16.267 | 16.889 | 17.8995 | 44.3924 | 47.6161 | 43.4766 | 21.3573 |  |  | 0.46087 | -0.43245 | -49.1761 | 0.21943 | 0.29715 | -197.8105 | 10.5062 | -0.32826 | -0.15014 | -0.16458 | -0.021582 | 8.8285 | 9.0581 | 1.979 | 21.7846 | 22.0098 | 22.2057 | 22.2636 | 22.0989 | 21.4244 | 20.2322 | 22.1982 | 22.3704 | 22.4119 | 22.3613 | 21.992 | 21.2199 | 22.2636 | 17.0793 | 17.1799 | 16.1058 | 16.1388 | 16.2258 | 17.0932 | 16.8702 | 22.3857 | 22.1494 | 21.7053 | 22.086 | 21.8027 | 21.3094 | 21.9455 | 21.529 | 20.9145 | 20.1055 | 20.3182 | 19.8652 | 19.7932 | 0.028323 | 0.07478 | 20.7371 | 22.0746 | 22.371 | 20.0834 | 21.6677 | 22.118 | 21.9577 | 21.7174 | 21.2779 | 21.7879 | 21.4472 | 21.0491 | 20.2222 | 20.3039 | 20.2354 | 20.2184 | 20.0761 |  | 20.2097 | 19.7768 | 20.1057 | 19.673 | 20.0821 | 20.3184 |  | 20.4122 |  |  | 20.3044 | 20.3757 | 20.6279 | [5 empty] | 21.9436 | 20.3506 | 21.6822 | 22.0649 | 19.5327 | 21.1825 | 21.8096 | 19.3622 | 19.9126 | 21.1397 |  | 19.7452 | 20.9145 | 18.874 | 19.7186 | 20.8134 | 19.4935 | 20.0519 | 19.0439 | 20.1149 | 19.1555 | 20.224 | 18.8193 | 20.0739 | 21.0396 | 19.389 | 19.771 | 20.9774 | 18.9246 | 19.8222 | 20.8151 | 19.0348 | 20.12 | 19.3118 | 19.9305 | 18.8993 | 20.1447 | -0.14853 | 20.9483 | 0.049003 | 0.01272 | -27.0493 | 3.0972 | 15.87 | -0.01 | 0.81052 | -0.7803 | -8.321 | 0.55584 | 0.64731 | -16.7013 | 3.849 | 0.42365 | 0.42848 | 0.43057 | 0.40393 | 0.48608 | 0.44042 | 0.42802
42838.417 | -279 | 22.9002 | 22.8651 | 22.8514 | 22.7782 | 22.4147 | 21.7533 | 22.7242 | 21.8144 | 22.3708 | 22.3836 | 22.3607 | 22.0382 | 21.254 | 22.2227 | 21.5889 | 21.7541 | 21.8854 | 21.0764 | 21.1796 | 21.3983 | 20.4751 | 20.618 | 20.9108 | 21.8833 | 21.6459 | 21.2892 | 20.2872 | 20.4002 | 20.3569 | 22.0571 | 21.6592 | 21.1855 | 21.9869 | 21.7347 | 21.3436 | 19.9098 | 20.4388 |  | 20.5186 | 20.0426 | 20.1614 | 19.1144 |  | 16.7925 | 16.7404 | 16.4231 | 16.6555 | 16.7783 | 17.2189 | 17.8185 | 16.0693 | 16.8622 | 16.2678 | 16.8788 | 17.9044 | 44.3767 | 47.6298 | 43.4743 | 21.3579 |  |  | 0.50752 | -0.52247 | -48.3711 | 0.31274 | 0.3668 | -197.8677 | 10.8722 | -0.47874 | -0.09059 | -0.12367 | -0.1273 | 8.8296 | 9.0594 | 1.9786 | 21.7944 | 22.0154 | 22.2067 | 22.2788 | 22.1027 | 21.4245 | 20.2347 | 22.2068 | 22.3722 | 22.4118 | 22.3636 | 21.9991 | 21.2298 | 22.2747 | 17.0513 | 17.1884 | 16.1344 | 16.1463 | 16.2141 | 17.0893 | 16.8577 | 22.3772 | 22.1461 | 21.7017 | 22.082 | 21.7989 | 21.3016 | 21.9413 | 21.5242 | 20.9043 | 20.1059 | 20.3185 | 19.855 | 19.7915 | 0.11699 | -0.056268 | 20.7408 | 22.0731 | 22.3786 | 20.0898 | 21.671 | 22.1162 | 21.9546 | 21.7228 | 21.2801 | 21.7907 | 21.4477 | 21.0525 | 20.2228 | 20.3056 | 20.243 | 20.2231 | 20.0643 |  | 20.2203 | 19.786 | 20.111 | 19.669 | 20.0851 | 20.3199 |  | 20.4154 |  |  | 20.296 | 20.3689 | 20.6236 | [5 empty] | 21.9306 | 20.3391 | 21.6762 | 22.0573 | 19.5324 | 21.1742 | 21.7982 | 19.3687 | 19.9201 | 21.1532 |  | 19.7549 | 20.9172 | 18.877 | 19.7243 | 20.8209 | 19.4955 | 20.0584 | 19.056 | 20.1147 | 19.1585 | 20.2253 | 18.8168 | 20.0707 | 21.0332 | 19.385 | 19.7656 | 20.9714 | 18.9215 | 19.8234 | 20.8083 | 19.0289 | 20.1165 | 19.3017 | 19.9291 | 18.894 | 20.1362 | 0.080189 | 20.9487 | 0.048118 | 0.012538 | -27.0207 | 3.0972 | -2.11 | -0.16 | 0.85056 | -0.85766 | -8.2523 | 0.66356 | 0.71922 | -16.7043 | 3.9156 | 0.42433 | 0.4284 | 0.43078 | 0.40658 | 0.48144 | 0.44032 | 0.42808
42838.4171 | -278 | 22.9015 | 22.861 | 22.855 | 22.7803 | 22.4051 | 21.7432 | 22.7206 | 21.8095 | 22.3669 | 22.3837 | 22.3616 | 22.0411 | 21.2488 | 22.2157 | 21.586 | 21.7499 | 21.8832 | 21.07 | 21.1717 | 21.3864 | 20.4665 | 20.6141 | 20.9088 | 21.8826 | 21.649 | 21.2821 | 20.2778 | 20.3884 | 20.3559 | 22.0675 | 21.6686 | 21.1919 | 22.0019 | 21.7454 | 21.3588 | 19.9228 | 20.4484 |  | 20.5306 | 20.0485 | 20.1735 | 19.1276 |  | 16.7962 | 16.74 | 16.4289 | 16.6594 | 16.8002 | 17.2584 | 17.8511 | 16.0931 | 16.867 | 16.2668 | 16.8964 | 17.9052 | 44.3762 | 47.6395 | 43.4573 | 21.3578 |  |  | 0.42867 | -0.24057 | -48.2699 | 0.36925 | 0.30175 | -197.8414 | 11.2166 | -0.42157 | 0.24665 | -0.20738 | 0.010534 | 8.8285 | 9.0586 | 1.9782 | 21.7849 | 22.012 | 22.2015 | 22.2689 | 22.0933 | 21.4192 | 20.2304 | 22.1997 | 22.3719 | 22.4064 | 22.362 | 21.995 | 21.2277 | 22.2733 | 17.0419 | 17.206 | 16.1655 | 16.1644 | 16.216 | 17.0953 | 16.8633 | 22.3805 | 22.1449 | 21.7037 | 22.0816 | 21.801 | 21.3043 | 21.938 | 21.5232 | 20.9081 | 20.1028 | 20.3147 | 19.8609 | 19.7871 | -0.027512 | -0.014234 | 20.7456 | 22.0701 | 22.3783 | 20.0936 | 21.6752 | 22.1137 | 21.9508 | 21.7153 | 21.2841 | 21.791 | 21.4509 | 21.054 | 20.2232 | 20.3026 | 20.2403 | 20.2177 | 20.0423 |  | 20.2193 | 19.798 | 20.1074 | 19.6731 | 20.0833 | 20.3164 |  | 20.4083 |  |  | 20.2916 | 20.3731 | 20.6271 | [5 empty] | 21.934 | 20.3399 | 21.6695 | 22.0541 | 19.5403 | 21.1791 | 21.8016 | 19.3734 | 19.92 | 21.1552 |  | 19.7587 | 20.9186 | 18.8795 | 19.725 | 20.8239 | 19.4928 | 20.0621 | 19.0503 | 20.1079 | 19.1594 | 20.2279 | 18.8232 | 20.074 | 21.0328 | 19.3897 | 19.7664 | 20.9757 | 18.919 | 19.8252 | 20.8096 | 19.0231 | 20.1213 | 19.3014 | 19.9284 | 18.8919 | 20.1376 | -0.1975 | 20.9489 | 0.048481 | 0.012894 | -27.0428 | 3.0972 | -0.65 | 0.01 | 0.78169 | -0.58197 | -8.2437 | 0.72102 | 0.65237 | -16.7044 | 3.9774 | 0.42491 | 0.42795 | 0.43061 | 0.40831 | 0.47863 | 0.44039 | 0.4281
42838.4171 | -277 | 22.9057 | 22.8613 | 22.8494 | 22.776 | 22.4074 | 21.7447 | 22.7135 | 21.8069 | 22.3645 | 22.3811 | 22.3506 | 22.0287 | 21.253 | 22.2256 | 21.5897 | 21.7585 | 21.8899 | 21.0791 | 21.172 | 21.3884 | 20.4755 | 20.6132 | 20.9139 | 21.8867 | 21.6502 | 21.29 | 20.2805 | 20.3887 | 20.3604 | 22.0595 | 21.665 | 21.1841 | 21.9856 | 21.7373 | 21.3484 | 19.9199 | 20.4363 |  | 20.5137 | 20.0393 | 20.1631 | 19.1194 |  | 16.7941 | 16.7361 | 16.431 | 16.6574 | 16.7856 | 17.2634 | 17.8734 | 16.117 | 16.8661 | 16.2324 | 16.8895 | 17.9011 | 44.3739 | 47.6426 | 43.4352 | 21.3567 |  |  | 0.45035 | -0.33651 | -48.2909 | 0.64065 | 0.18281 | -197.8466 | 10.6758 | -0.42289 | 0.083188 | -0.2571 | -0.11585 | 8.8279 | 9.0578 | 1.9793 | 21.7857 | 22.0123 | 22.2043 | 22.2704 | 22.0913 | 21.4245 | 20.2378 | 22.1932 | 22.3723 | 22.408 | 22.3636 | 21.9926 | 21.225 | 22.2699 | 17.0427 | 17.215 | 16.1795 | 16.1777 | 16.2204 | 17.0956 | 16.872 | 22.3802 | 22.1522 | 21.7119 | 22.0898 | 21.8104 | 21.3063 | 21.9476 | 21.5287 | 20.9155 | 20.1071 | 20.3164 | 19.8706 | 19.7834 | -0.0041164 | -0.012903 | 20.7442 | 22.0706 | 22.3713 | 20.0921 | 21.6732 | 22.1139 | 21.9479 | 21.7103 | 21.286 | 21.787 | 21.453 | 21.0448 | 20.2287 | 20.2966 | 20.2307 | 20.2187 | 20.0398 |  | 20.2206 | 19.8071 | 20.1102 | 19.6719 | 20.0946 | 20.3133 |  | 20.4116 |  |  | 20.2986 | 20.3812 | 20.6285 | [5 empty] | 21.9366 | 20.3414 | 21.6662 | 22.0516 | 19.5516 | 21.1827 | 21.8041 | 19.3736 | 19.9157 | 21.1478 |  | 19.7458 | 20.918 | 18.8711 | 19.7203 | 20.817 | 19.4893 | 20.0533 | 19.0438 | 20.095 | 19.1545 | 20.2174 | 18.8376 | 20.0798 | 21.0412 | 19.4042 | 19.7706 | 20.9883 | 18.9295 | 19.8327 | 20.815 | 19.0236 | 20.1269 | 19.3016 | 19.9319 | 18.8972 | 20.1394 | -0.025546 | 20.9491 | 0.04936 | 0.014571 | -27.1591 | 3.0972 | 1.64 | -0.07 | 0.80123 | -0.6883 | -8.2454 | 0.94971 | 0.50778 | -16.7047 | 3.8804 | 0.42502 | 0.42779 | 0.43102 | 0.40826 | 0.4781 | 0.44052 | 0.42834
42838.4171 | -276 | 22.9059 | 22.8629 | 22.8481 | 22.7781 | 22.4134 | 21.7476 | 22.7211 | 21.8111 | 22.3684 | 22.3772 | 22.3689 | 22.0377 | 21.2553 | 22.2213 | 21.581 | 21.7572 | 21.8833 | 21.0763 | 21.1668 | 21.385 | 20.4728 | 20.6092 | 20.9052 | 21.8781 | 21.6493 | 21.2814 | 20.2827 | 20.3886 | 20.3523 | 22.0587 | 21.6576 | 21.1792 | 21.9863 | 21.738 | 21.3417 | 19.9061 | 20.4367 |  | 20.515 | 20.0408 | 20.1622 | 19.1129 |  | 16.7809 | 16.727 | 16.4265 | 16.6531 | 16.8009 | 17.2813 | 17.8722 | 16.143 | 16.8641 | 16.2274 | 16.8839 | 17.9051 | 44.3659 | 47.6635 | 43.4207 | 21.3532 |  |  | 0.43195 | -0.42916 | -48.0498 | 0.44088 | 0.28532 | -197.8204 | 11.3309 | -0.41763 | 0.015272 | 0.046267 | -0.068454 | 8.8295 | 9.0594 | 1.9791 | 21.7902 | 22.0153 | 22.2041 | 22.2695 | 22.0989 | 21.4273 | 20.2365 | 22.1994 | 22.3755 | 22.4056 | 22.3675 | 21.9944 | 21.2297 | 22.2786 | 17.0602 | 17.2034 | 16.1964 | 16.1801 | 16.2235 | 17.0907 | 16.8606 | 22.3841 | 22.1544 | 21.7038 | 22.0829 | 21.8012 | 21.3021 | 21.9477 | 21.5323 | 20.9096 | 20.1071 | 20.3166 | 19.859 | 19.7775 | 0.087892 | -0.14699 | 20.7411 | 22.0644 | 22.369 | 20.0891 | 21.6723 | 22.1162 | 21.9484 | 21.7107 | 21.2848 | 21.7791 | 21.446 | 21.0451 | 20.2288 | 20.2918 | 20.2283 | 20.214 | 20.0396 |  | 20.2178 | 19.8146 | 20.1179 | 19.6823 | 20.0899 | 20.3105 |  | 20.4148 |  |  | 20.301 | 20.3884 | 20.6336 | [5 empty] | 21.9427 | 20.3501 | 21.6801 | 22.0623 | 19.5577 | 21.1878 | 21.8099 | 19.3738 | 19.9215 | 21.1487 |  | 19.7469 | 20.923 | 18.8732 | 19.7249 | 20.819 | 19.4929 | 20.0536 | 19.0398 | 20.0993 | 19.1515 | 20.2172 | 18.8397 | 20.0865 | 21.0342 | 19.4071 | 19.7684 | 20.9872 | 18.9179 | 19.829 | 20.8192 | 19.0231 | 20.1294 | 19.3047 | 19.9366 | 18.8987 | 20.1422 | 0.032515 | 20.9482 | 0.049335 | 0.015602 | -27.0718 | 3.0972 | -1.93 | -0.06 | 0.78468 | -0.77729 | -8.2247 | 0.78783 | 0.63439 | -16.7041 | 3.9978 | 0.42493 | 0.42784 | 0.43058 | 0.40575 | 0.47489 | 0.44024 | 0.4285
42838.4171 | -275 | 22.9031 | 22.8609 | 22.8494 | 22.7737 | 22.4057 | 21.7545 | 22.7159 | 21.8132 | 22.3653 | 22.372 | 22.3584 | 22.0316 | 21.2479 | 22.2146 | 21.5829 | 21.7609 | 21.8843 | 21.0745 | 21.169 | 21.4023 | 20.4709 | 20.6082 | 20.9117 | 21.8872 | 21.6527 | 21.2754 | 20.2808 | 20.3922 | 20.3556 | 22.0639 | 21.6611 | 21.182 | 21.9928 | 21.7362 | 21.3517 | 19.9171 | 20.4387 |  | 20.5163 | 20.055 | 20.164 | 19.1226 |  | 16.7834 | 16.7292 | 16.4286 | 16.6514 | 16.8159 | 17.3106 | 17.8884 | 16.1255 | 16.8671 | 16.2386 | 16.885 | 17.9031 | 44.3413 | 47.6726 | 43.4074 | 21.3495 |  |  | 0.40041 | -0.22874 | -47.714 | 0.51185 | 0.31752 | -197.8322 | 11.0957 | -0.34732 | -0.065487 | -0.12577 | 0.036747 | 8.83 | 9.0596 | 1.979 | 21.7856 | 22.0135 | 22.2039 | 22.2641 | 22.0926 | 21.4166 | 20.2307 | 22.1973 | 22.3732 | 22.409 | 22.3626 | 21.9857 | 21.2278 | 22.2742 | 17.0863 | 17.1961 | 16.2278 | 16.1883 | 16.2209 | 17.094 | 16.8641 | 22.3788 | 22.1488 | 21.705 | 22.0769 | 21.8002 | 21.3013 | 21.9461 | 21.5225 | 20.9092 | 20.0986 | 20.3204 | 19.8617 | 19.787 | -0.12915 | 0.051575 | 20.7429 | 22.0717 | 22.3794 | 20.0951 | 21.6756 | 22.1215 | 21.9535 | 21.722 | 21.2844 | 21.7863 | 21.4554 | 21.0518 | 20.2326 | 20.2943 | 20.2313 | 20.2257 | 20.0433 |  | 20.2189 | 19.8212 | 20.1174 | 19.6837 | 20.09 | 20.3136 |  | 20.4219 |  |  | 20.2995 | 20.3809 | 20.625 | [5 empty] | 21.9434 | 20.3467 | 21.6785 | 22.0646 | 19.5556 | 21.1808 | 21.806 | 19.3803 | 19.923 | 21.1449 |  | 19.7484 | 20.9277 | 18.8686 | 19.7304 | 20.8189 | 19.4871 | 20.0483 | 19.0338 | 20.0908 | 19.1485 | 20.2108 | 18.8329 | 20.0844 | 21.042 | 19.4017 | 19.7629 | 20.9808 | 18.9214 | 19.8358 | 20.8097 | 19.0157 | 20.1245 | 19.3056 | 19.9272 | 18.9035 | 20.1294 | -0.06042 | 20.9494 | 0.049685 | 0.016749 | -27.1183 | 3.0971 | 12.44 | -0.11 | 0.75549 | -0.56748 | -8.1959 | 0.84888 | 0.66926 | -16.7055 | 3.9563 | 0.42487 | 0.42764 | 0.43054 | 0.40324 | 0.47181 | 0.44034 | 0.42796
42838.4171 | -274 | 22.9013 | 22.8666 | 22.8508 | 22.78 | 22.4115 | 21.7557 | 22.7139 | 21.8094 | 22.3655 | 22.3746 | 22.355 | 22.0361 | 21.2473 | 22.221 | 21.5907 | 21.7609 | 21.8788 | 21.0726 | 21.1763 | 21.397 | 20.4707 | 20.6156 | 20.905 | 21.8812 | 21.6442 | 21.2794 | 20.2823 | 20.3926 | 20.3535 | 22.0667 | 21.6705 | 21.1945 | 22.0001 | 21.7392 | 21.3554 | 19.9226 | 20.4443 |  | 20.5243 | 20.0467 | 20.1668 | 19.1311 |  | 16.7876 | 16.7376 | 16.4355 | 16.6728 | 16.8316 | 17.3347 | 17.9213 | 16.0992 | 16.8613 | 16.2479 | 16.8903 | 17.9078 | 44.3371 | 47.693 | 43.3995 | 21.3575 |  |  | 0.61398 | -0.25897 | -47.8079 | 0.34757 | 0.29058 | -197.8453 | 11.3322 | -0.37098 | -0.34318 | 0.17341 | 0.04317 | 8.8286 | 9.0584 | 1.9786 | 21.7859 | 22.0072 | 22.1988 | 22.258 | 22.0923 | 21.415 | 20.2281 | 22.1958 | 22.3661 | 22.4039 | 22.3605 | 21.9828 | 21.2211 | 22.2694 | 17.1201 | 17.2226 | 16.2586 | 16.2005 | 16.2297 | 17.0974 | 16.8677 | 22.388 | 22.152 | 21.7097 | 22.0859 | 21.8026 | 21.3063 | 21.9474 | 21.5292 | 20.9082 | 20.1119 | 20.313 | 19.8615 | 19.7938 | -0.11421 | -0.033634 | 20.7403 | 22.0716 | 22.3784 | 20.0987 | 21.6702 | 22.1234 | 21.953 | 21.7187 | 21.2834 | 21.7895 | 21.4576 | 21.0531 | 20.229 | 20.2945 | 20.2415 | 20.2277 | 20.0514 |  | 20.2214 | 19.8284 | 20.1143 | 19.6721 | 20.0912 | 20.317 |  | 20.4167 |  |  | 20.2933 | 20.3719 | 20.628 | [5 empty] | 21.9324 | 20.3387 | 21.6757 | 22.0591 | 19.5568 | 21.1796 | 21.7989 | 19.373 | 19.9125 | 21.1439 |  | 19.7533 | 20.9103 | 18.8621 | 19.7204 | 20.8061 | 19.4819 | 20.0344 | 19.0243 | 20.0834 | 19.1454 | 20.2043 | 18.8293 | 20.0795 | 21.0438 | 19.3954 | 19.7624 | 20.9798 | 18.9195 | 19.8349 | 20.8036 | 19.0126 | 20.1183 | 19.3009 | 19.9316 | 18.8944 | 20.1295 | 0.003763 | 20.9485 | 0.049691 | 0.016843 | -27.0469 | 3.0972 | 7.28 | -0.09 | 0.93551 | -0.60382 | -8.2041 | 0.69952 | 0.64026 | -16.7067 | 3.9984 | 0.42473 | 0.42733 | 0.4309 | 0.39988 | 0.4688 | 0.44028 | 0.42821
42838.4171 | -273 | 22.9079 | 22.8637 | 22.8493 | 22.7818 | 22.4102 | 21.7516 | 22.7121 | 21.8107 | 22.3646 | 22.3732 | 22.3604 | 22.034 | 21.2533 | 22.2144 | 21.5943 | 21.7606 | 21.8892 | 21.0803 | 21.1837 | 21.3956 | 20.4816 | 20.6162 | 20.9118 | 21.8829 | 21.6476 | 21.2837 | 20.2832 | 20.3947 | 20.3626 | 22.0659 | 21.6673 | 21.1865 | 21.998 | 21.741 | 21.3552 | 19.9193 | 20.4365 |  | 20.5181 | 20.0546 | 20.166 | 19.1352 |  | 16.7874 | 16.737 | 16.428 | 16.6896 | 16.8496 | 17.362 | 17.9434 | 16.0882 | 16.8637 | 16.2477 | 16.8868 | 17.903 | 44.3295 | 47.7004 | 43.3841 | 21.3517 |  |  | 0.36821 | -0.19983 | -47.254 | 0.28843 | 0.31883 | -197.8598 | 10.9347 | -0.32103 | -0.38288 | -0.034506 | 0.084834 | 8.8295 | 9.0592 | 1.9782 | 21.7869 | 22.0088 | 22.1977 | 22.2703 | 22.092 | 21.4249 | 20.2328 | 22.199 | 22.3693 | 22.4014 | 22.3672 | 21.989 | 21.2318 | 22.2758 | 17.1392 | 17.2258 | 16.2896 | 16.1971 | 16.2271 | 17.0931 | 16.87 | 22.3898 | 22.1499 | 21.71 | 22.0909 | 21.8036 | 21.3105 | 21.9482 | 21.5286 | 20.9083 | 20.106 | 20.3176 | 19.8585 | 19.7921 | -0.12974 | 0.07478 | 20.7442 | 22.0735 | 22.3848 | 20.1011 | 21.6786 | 22.1244 | 21.9569 | 21.713 | 21.2833 | 21.7986 | 21.4582 | 21.0586 | 20.2346 | 20.3019 | 20.2421 | 20.2275 | 20.0533 |  | 20.2262 | 19.8368 | 20.1209 | 19.663 | 20.0944 | 20.3199 |  | 20.4131 |  |  | 20.2945 | 20.3788 | 20.6232 | [5 empty] | 21.9433 | 20.3398 | 21.6794 | 22.0618 | 19.5615 | 21.1828 | 21.7966 | 19.3688 | 19.9119 | 21.1468 |  | 19.7485 | 20.9156 | 18.8633 | 19.7119 | 20.8115 | 19.4678 | 20.0411 | 19.0295 | 20.0891 | 19.1481 | 20.2036 | 18.8256 | 20.0953 | 21.0484 | 19.4041 | 19.7627 | 20.9795 | 18.9248 | 19.8373 | 20.8089 | 19.0122 | 20.1242 | 19.3075 | 19.9275 | 18.8962 | 20.1319 | -0.19806 | 20.9483 | 0.049464 | 0.01521 | -26.9775 | 3.0972 | -9.8 | -0.18 | 0.72449 | -0.53041 | -8.1564 | 0.63724 | 0.6707 | -16.7081 | 3.9278 | 0.42484 | 0.42732 | 0.43126 | 0.39725 | 0.46563 | 0.44006 | 0.42806
42838.4171 | -272 | 22.9022 | 22.8559 | 22.8519 | 22.7824 | 22.4113 | 21.7489 | 22.7184 | 21.8073 | 22.3611 | 22.3738 | 22.356 | 22.0321 | 21.251 | 22.2111 | 21.5954 | 21.7617 | 21.8944 | 21.0813 | 21.1736 | 21.3976 | 20.4751 | 20.6148 | 20.915 | 21.8927 | 21.6441 | 21.284 | 20.2789 | 20.4022 | 20.3639 | 22.0605 | 21.6651 | 21.185 | 21.9991 | 21.7242 | 21.3547 | 19.9185 | 20.427 |  | 20.5157 | 20.0468 | 20.1596 | 19.1271 |  | 16.783 | 16.7335 | 16.427 | 16.6956 | 16.8567 | 17.3846 | 17.9365 | 16.054 | 16.8573 | 16.1979 | 16.8793 | 17.9039 | 44.3264 | 47.7177 | 43.3754 | 21.3461 |  |  | 0.52592 | -0.43902 | -46.6002 | 0.53353 | 0.27349 | -197.8289 | 11.6174 | -0.54051 | -0.18536 | 0.1562 | 0.03397 | 8.8289 | 9.0587 | 1.9794 | 21.7917 | 22.0193 | 22.2029 | 22.2628 | 22.0949 | 21.4238 | 20.233 | 22.204 | 22.3793 | 22.4061 | 22.3683 | 21.9921 | 21.2258 | 22.2734 | 17.1789 | 17.2095 | 16.3053 | 16.2141 | 16.2396 | 17.0979 | 16.874 | 22.3813 | 22.1525 | 21.7126 | 22.0842 | 21.799 | 21.3058 | 21.9551 | 21.5325 | 20.9162 | 20.1086 | 20.3152 | 19.8503 | 19.7849 | -0.039111 | 0.13051 | 20.7419 | 22.0688 | 22.3708 | 20.0941 | 21.6704 | 22.122 | 21.948 | 21.7128 | 21.2812 | 21.7876 | 21.4517 | 21.0487 | 20.2324 | 20.3037 | 20.2316 | 20.2223 | 20.0552 |  | 20.2273 | 19.8432 | 20.1176 | 19.6648 | 20.0997 | 20.32 |  | 20.4209 |  |  | 20.2826 | 20.3756 | 20.622 | [5 empty] | 21.9426 | 20.3445 | 21.6803 | 22.0608 | 19.5478 | 21.178 | 21.8027 | 19.3727 | 19.9192 | 21.1449 |  | 19.7479 | 20.9173 | 18.863 | 19.7221 | 20.8148 | 19.4802 | 20.0482 | 19.0308 | 20.0867 | 19.1417 | 20.2142 | 18.8203 | 20.0908 | 21.0355 | 19.4012 | 19.7622 | 20.9731 | 18.9243 | 19.8295 | 20.8111 | 19.0166 | 20.119 | 19.3015 | 19.9238 | 18.8885 | 20.1297 | -0.022021 | 20.9488 | 0.048155 | 0.012916 | -27.0124 | 3.0971 | -8.75 | -0.08 | 0.86585 | -0.78618 | -8.0998 | 0.86668 | 0.62121 | -16.7075 | 4.0487 | 0.42482 | 0.42703 | 0.43139 | 0.39341 | 0.46436 | 0.44026 | 0.42835
42838.4171 | -271 | 22.901 | 22.8629 | 22.8504 | 22.7737 | 22.414 | 21.7567 | 22.7197 | 21.811 | 22.3685 | 22.3767 | 22.3635 | 22.0345 | 21.2558 | 22.2158 | 21.5929 | 21.7686 | 21.8995 | 21.0792 | 21.178 | 21.396 | 20.4744 | 20.6238 | 20.9086 | 21.8878 | 21.6568 | 21.2846 | 20.2884 | 20.4055 | 20.3613 | 22.0582 | 21.665 | 21.183 | 21.994 | 21.7224 | 21.3508 | 19.9131 | 20.4179 |  | 20.511 | 20.0406 | 20.1535 | 19.1052 |  | 16.7868 | 16.7437 | 16.4417 | 16.7057 | 16.8669 | 17.3886 | 17.9328 | 16.0274 | 16.8638 | 16.1706 | 16.8894 | 17.9119 | 44.3299 | 47.7438 | 43.3638 | 21.3491 |  |  | 0.50949 | -0.072349 | -46.6501 | 0.67416 | 0.35629 | -197.8742 | 11.1233 | -0.53197 | -0.1264 | -0.31228 | 0.050635 | 8.8291 | 9.059 | 1.9794 | 21.7907 | 22.0141 | 22.2173 | 22.2704 | 22.1011 | 21.4297 | 20.2342 | 22.1982 | 22.3767 | 22.4124 | 22.3648 | 21.9905 | 21.2207 | 22.2736 | 17.2107 | 17.2007 | 16.285 | 16.2233 | 16.2445 | 17.0938 | 16.883 | 22.3876 | 22.1488 | 21.7147 | 22.0907 | 21.8049 | 21.3083 | 21.9498 | 21.5371 | 20.9162 | 20.1147 | 20.3175 | 19.8464 | 19.7981 | -0.076662 | -0.16773 | 20.733 | 22.0688 | 22.3726 | 20.0951 | 21.6637 | 22.1145 | 21.9423 | 21.7188 | 21.2833 | 21.781 | 21.449 | 21.0506 | 20.2361 | 20.3103 | 20.2384 | 20.2222 | 20.0512 |  | 20.2174 | 19.8409 | 20.1189 | 19.6651 | 20.0884 | 20.309 |  | 20.4166 |  |  | 20.2748 | 20.3666 | 20.6107 | [5 empty] | 21.9264 | 20.3391 | 21.6717 | 22.0531 | 19.5356 | 21.1724 | 21.7985 | 19.3758 | 19.9173 | 21.1464 |  | 19.75 | 20.9287 | 18.8697 | 19.7226 | 20.8058 | 19.4798 | 20.0558 | 19.0349 | 20.0827 | 19.1492 | 20.2117 | 18.8288 | 20.0931 | 21.0425 | 19.4069 | 19.7698 | 20.981 | 18.9297 | 19.8351 | 20.8144 | 19.0145 | 20.1229 | 19.3137 | 19.9294 | 18.899 | 20.1332 | -0.06784 | 20.9495 | 0.048174 | 0.013206 | -27.0994 | 3.0971 | -6.14 | -0.09 | 0.85221 | -0.31916 | -8.1042 | 0.97424 | 0.70904 | -16.7095 | 3.9617 | 0.4246 | 0.42714 | 0.431 | 0.38939 | 0.46765 | 0.44069 | 0.42819
42838.4172 | -270 | 22.9123 | 22.8835 | 22.8591 | 22.7956 | 22.4219 | 21.755 | 22.7187 | 21.8207 | 22.3732 | 22.3851 | 22.3667 | 22.044 | 21.2553 | 22.2279 | 21.5861 | 21.7575 | 21.8938 | 21.0723 | 21.1728 | 21.388 | 20.4757 | 20.6144 | 20.9021 | 21.8827 | 21.6479 | 21.2828 | 20.2837 | 20.3948 | 20.3613 | 22.0579 | 21.6647 | 21.1787 | 21.9873 | 21.7306 | 21.3536 | 19.9091 | 20.4129 |  | 20.5016 | 20.0393 | 20.1548 | 19.0974 |  | 16.7809 | 16.7415 | 16.4398 | 16.6935 | 16.8492 | 17.388 | 17.9078 | 16.006 | 16.8662 | 16.1551 | 16.8891 | 17.9117 | 44.3281 | 47.7641 | 43.3474 | 21.3508 |  |  | 0.53775 | -0.2708 | -46.729 | 0.58479 | 0.28072 | -197.8361 | 11.3257 | -0.63974 | -0.039994 | -0.22249 | 0.0053256 | 8.8301 | 9.06 | 1.9789 | 21.7808 | 22.0016 | 22.205 | 22.2648 | 22.0888 | 21.4169 | 20.23 | 22.1916 | 22.3748 | 22.412 | 22.3566 | 21.9791 | 21.2172 | 22.2668 | 17.2486 | 17.1837 | 16.2609 | 16.2088 | 16.2308 | 17.0917 | 16.8856 | 22.3965 | 22.1497 | 21.7105 | 22.0892 | 21.8066 | 21.3155 | 21.9521 | 21.5373 | 20.9163 | 20.1109 | 20.3248 | 19.8479 | 19.8006 | -0.079807 | -0.058741 | 20.7385 | 22.0681 | 22.3853 | 20.1038 | 21.6702 | 22.1229 | 21.949 | 21.7243 | 21.2896 | 21.7842 | 21.4503 | 21.0529 | 20.2401 | 20.3161 | 20.2469 | 20.2251 | 20.0551 |  | 20.2193 | 19.8542 | 20.1183 | 19.6825 | 20.0899 | 20.3114 |  | 20.4117 |  |  | 20.2707 | 20.3772 | 20.6283 | [5 empty] | 21.9436 | 20.3456 | 21.682 | 22.062 | 19.5485 | 21.1809 | 21.8124 | 19.3781 | 19.9213 | 21.1504 |  | 19.7504 | 20.924 | 18.8638 | 19.7134 | 20.8006 | 19.4813 | 20.0465 | 19.03 | 20.0847 | 19.1483 | 20.214 | 18.8226 | 20.0963 | 21.0482 | 19.398 | 19.7741 | 20.9796 | 18.9342 | 19.8347 | 20.8126 | 19.0009 | 20.1215 | 19.3061 | 19.929 | 18.9026 | 20.127 | -0.10142 | 20.949 | 0.049501 | 0.01513 | -27.115 | 3.0971 | -7.06 | -0.02 | 0.87553 | -0.61746 | -8.1111 | 0.90737 | 0.62937 | -16.7079 | 3.9976 | 0.42456 | 0.42675 | 0.43057 | 0.38494 | 0.47063 | 0.44077 | 0.42799
42838.4172 | -269 | 22.9114 | 22.8714 | 22.8586 | 22.7813 | 22.4065 | 21.7555 | 22.7247 | 21.8115 | 22.3803 | 22.3844 | 22.3627 | 22.0422 | 21.2603 | 22.2289 | 21.5811 | 21.7584 | 21.8884 | 21.0677 | 21.1685 | 21.389 | 20.4693 | 20.6118 | 20.9061 | 21.8783 | 21.6433 | 21.2775 | 20.2792 | 20.3892 | 20.3575 | 22.0651 | 21.6742 | 21.1925 | 22.0008 | 21.7406 | 21.3569 | 19.9252 | 20.4282 |  | 20.5123 | 20.0463 | 20.1597 | 19.1027 |  | 16.7907 | 16.7464 | 16.4427 | 16.6975 | 16.852 | 17.402 | 17.8821 | 16.02 | 16.8725 | 16.1091 | 16.8952 | 17.9155 | 44.3448 | 47.787 | 43.3431 | 21.3501 |  |  | 0.49109 | -0.45808 | -46.7848 | 0.59662 | 0.12958 | -197.8052 | 11.1725 | -0.48137 | 0.035705 | -0.10982 | 0.020255 | 8.8285 | 9.0583 | 1.9781 | 21.7814 | 22.0017 | 22.1999 | 22.2646 | 22.0873 | 21.411 | 20.234 | 22.1968 | 22.3685 | 22.4012 | 22.3561 | 21.9795 | 21.213 | 22.2677 | 17.2823 | 17.1561 | 16.2359 | 16.1883 | 16.2076 | 17.087 | 16.876 | 22.3893 | 22.1541 | 21.7107 | 22.0903 | 21.8046 | 21.3109 | 21.9524 | 21.5321 | 20.9106 | 20.1065 | 20.3271 | 19.8459 | 19.7845 | -0.044813 | -0.16963 | 20.7357 | 22.0735 | 22.38 | 20.0986 | 21.671 | 22.1284 | 21.9508 | 21.7141 | 21.2775 | 21.7829 | 21.4447 | 21.0495 | 20.2356 | 20.3042 | 20.2412 | 20.2219 | 20.0471 |  | 20.2169 | 19.8531 | 20.1174 | 19.6867 | 20.0862 | 20.3088 |  | 20.4129 |  |  | 20.2645 | 20.3768 | 20.6307 | [5 empty] | 21.9432 | 20.341 | 21.6845 | 22.0593 | 19.5469 | 21.1862 | 21.8025 | 19.3738 | 19.9191 | 21.1404 |  | 19.7584 | 20.9128 | 18.8552 | 19.7086 | 20.7961 | 19.4761 | 20.0362 | 19.0149 | 20.0669 | 19.139 | 20.1953 | 18.8215 | 20.0962 | 21.0468 | 19.413 | 19.777 | 20.9838 | 18.9282 | 19.8327 | 20.8084 | 18.9939 | 20.1138 | 19.3053 | 19.9257 | 18.8984 | 20.1278 | -0.075817 | 20.9488 | 0.04963 | 0.015645 | -27.1379 | 3.0971 | -15.98 | -0.1 | 0.83668 | -0.80308 | -8.116 | 0.91651 | 0.42762 | -16.707 | 3.9706 | 0.4247 | 0.42675 | 0.43033 | 0.38064 | 0.47229 | 0.44116 | 0.42829
42838.4172 | -268 | 22.9006 | 22.8695 | 22.8506 | 22.778 | 22.4189 | 21.7493 | 22.7184 | 21.8177 | 22.3704 | 22.3831 | 22.3581 | 22.0353 | 21.2561 | 22.2214 | 21.5872 | 21.7632 | 21.8891 | 21.0738 | 21.1718 | 21.3928 | 20.4745 | 20.6174 | 20.9095 | 21.8849 | 21.6522 | 21.2866 | 20.284 | 20.397 | 20.3609 | 22.0676 | 21.6628 | 21.1854 | 21.9932 | 21.7394 | 21.3542 | 19.919 | 20.4161 |  | 20.5129 | 20.043 | 20.1626 | 19.1027 |  | 16.7877 | 16.7447 | 16.4348 | 16.6934 | 16.8437 | 17.3902 | 17.872 | 16.0398 | 16.8663 | 16.0329 | 16.8907 | 17.9102 | 44.3676 | 47.8059 | 43.3345 | 21.3497 |  |  | 0.45364 | -0.2386 | -47.484 | 0.52893 | 0.16835 | -197.8617 | 11.0648 | -0.60556 | 0.039597 | -0.018771 | 0.04942 | 8.8297 | 9.0596 | 1.978 | 21.7811 | 22.007 | 22.1997 | 22.2601 | 22.0913 | 21.4134 | 20.2302 | 22.1951 | 22.362 | 22.3968 | 22.355 | 21.9857 | 21.2148 | 22.2598 | 17.3099 | 17.1474 | 16.231 | 16.174 | 16.2085 | 17.0866 | 16.8742 | 22.3832 | 22.1562 | 21.7137 | 22.0897 | 21.805 | 21.3065 | 21.939 | 21.536 | 20.9123 | 20.1069 | 20.3152 | 19.8432 | 19.7802 | -0.10969 | -0.20158 | 20.7324 | 22.0736 | 22.3715 | 20.104 | 21.6747 | 22.1198 | 21.9533 | 21.7157 | 21.2804 | 21.7879 | 21.45 | 21.0551 | 20.2316 | 20.3159 | 20.2452 | 20.2247 | 20.0541 |  | 20.2159 | 19.8609 | 20.1136 | 19.6799 | 20.0821 | 20.3062 |  | 20.4084 |  |  | 20.265 | 20.3757 | 20.6266 | [5 empty] | 21.9371 | 20.3445 | 21.6806 | 22.0586 | 19.5446 | 21.1814 | 21.8022 | 19.3729 | 19.9189 | 21.1444 |  | 19.7621 | 20.9203 | 18.8559 | 19.7132 | 20.7957 | 19.4756 | 20.0351 | 19.0204 | 20.0705 | 19.1393 | 20.1935 | 18.8174 | 20.0935 | 21.0447 | 19.4112 | 19.7695 | 20.9834 | 18.9325 | 19.8428 | 20.8138 | 18.9997 | 20.1208 | 19.3083 | 19.9295 | 18.8963 | 20.1271 | -0.16578 | 20.9474 | 0.04885 | 0.01521 | -27.0019 | 3.097 | -3.11 | 0.01 | 0.80415 | -0.57959 | -8.1764 | 0.86295 | 0.48739 | -16.709 | 3.9513 | 0.42447 | 0.42641 | 0.43038 | 0.37753 | 0.47262 | 0.44095 | 0.42843
42838.4172 | -267 | 22.8974 | 22.8641 | 22.8551 | 22.779 | 22.413 | 21.7466 | 22.7191 | 21.8168 | 22.3643 | 22.3736 | 22.3569 | 22.0315 | 21.2452 | 22.2127 | 21.5901 | 21.7561 | 21.8868 | 21.0772 | 21.1747 | 21.3864 | 20.4733 | 20.6122 | 20.9068 | 21.8862 | 21.6469 | 21.2845 | 20.2775 | 20.3978 | 20.3624 | 22.0691 | 21.6694 | 21.1853 | 21.9971 | 21.7391 | 21.3549 | 19.909 | 20.4125 |  | 20.5079 | 20.0366 | 20.1545 | 19.0989 |  | 16.7889 | 16.7497 | 16.435 | 16.6933 | 16.842 | 17.3848 | 17.8653 | 16.0764 | 16.868 | 16.0046 | 16.8919 | 17.9101 | 44.3866 | 47.8237 | 43.3463 | 21.3482 |  |  | 0.22956 | -0.16697 | -47.6516 | 0.17803 | 0.17952 | -197.8125 | 11.3565 | -0.53985 | 0.28635 | -0.045625 | -0.023839 | 8.8288 | 9.0584 | 1.9788 | 21.7857 | 22.0085 | 22.1997 | 22.2599 | 22.0951 | 21.4163 | 20.2246 | 22.1932 | 22.3687 | 22.4031 | 22.3514 | 21.9814 | 21.2151 | 22.2626 | 17.3361 | 17.1659 | 16.2353 | 16.1656 | 16.2269 | 17.0906 | 16.8731 | 22.3843 | 22.1518 | 21.7079 | 22.0912 | 21.8042 | 21.3082 | 21.9471 | 21.53 | 20.9176 | 20.1133 | 20.3224 | 19.8409 | 19.7893 | 0.078259 | -0.20025 | 20.728 | 22.0703 | 22.3726 | 20.0989 | 21.6704 | 22.1161 | 21.949 | 21.7085 | 21.2767 | 21.7829 | 21.4454 | 21.0476 | 20.2327 | 20.3122 | 20.2328 | 20.2198 | 20.0584 |  | 20.2172 | 19.8706 | 20.1161 | 19.6942 | 20.0829 | 20.3135 |  | 20.4137 |  |  | 20.2664 | 20.3808 | 20.6287 | [5 empty] | 21.9441 | 20.3408 | 21.6842 | 22.0609 | 19.5383 | 21.1829 | 21.8045 | 19.3847 | 19.9279 | 21.155 |  | 19.7671 | 20.9244 | 18.8605 | 19.7152 | 20.8042 | 19.4779 | 20.0482 | 19.0212 | 20.0765 | 19.1414 | 20.1983 | 18.8173 | 20.0996 | 21.0431 | 19.4152 | 19.7735 | 20.9875 | 18.9313 | 19.8469 | 20.8147 | 18.9979 | 20.1237 | 19.3151 | 19.9319 | 18.8979 | 20.1252 | -0.21457 | 20.9491 | 0.046859 | 0.014244 | -27.0646 | 3.097 | 2.59 | -0.12 | 0.57205 | -0.48486 | -8.1909 | 0.50066 | 0.5033 | -16.7068 | 4.003 | 0.42439 | 0.42622 | 0.43001 | 0.37508 | 0.47202 | 0.44072 | 0.42839
42838.4172 | -266 | 22.9018 | 22.8606 | 22.8524 | 22.7789 | 22.4123 | 21.7538 | 22.7238 | 21.818 | 22.375 | 22.3777 | 22.3531 | 22.0336 | 21.2535 | 22.2199 | 21.5949 | 21.7581 | 21.8902 | 21.0769 | 21.1778 | 21.3943 | 20.4766 | 20.6103 | 20.9114 | 21.8911 | 21.65 | 21.2819 | 20.2786 | 20.4 | 20.371 | 22.0665 | 21.675 | 21.1831 | 21.991 | 21.7331 | 21.3457 | 19.9055 | 20.4075 |  | 20.5074 | 20.0335 | 20.1577 | 19.0907 |  | 16.7866 | 16.7422 | 16.4397 | 16.6854 | 16.8327 | 17.3818 | 17.8939 | 16.1116 | 16.8612 | 16.0033 | 16.8939 | 17.9132 | 44.4109 | 47.8432 | 43.3535 | 21.3494 |  |  | 0.49635 | -0.45282 | -47.5628 | 0.49805 | 0.43514 | -197.8769 | 11.0142 | -0.50502 | 0.20364 | -0.16857 | 0.004284 | 8.8282 | 9.058 | 1.9786 | 21.7784 | 22.0114 | 22.1973 | 22.2695 | 22.0937 | 21.4146 | 20.2299 | 22.1958 | 22.3673 | 22.4051 | 22.3573 | 21.9791 | 21.2119 | 22.2646 | 17.3828 | 17.1847 | 16.2307 | 16.1758 | 16.2387 | 17.0891 | 16.8769 | 22.3894 | 22.1526 | 21.7038 | 22.0842 | 21.8005 | 21.3169 | 21.9505 | 21.5288 | 20.9157 | 20.1109 | 20.3155 | 19.8416 | 19.7851 | -0.10969 | -0.11827 | 20.7363 | 22.0686 | 22.372 | 20.0947 | 21.6713 | 22.1161 | 21.948 | 21.7182 | 21.2843 | 21.7873 | 21.4482 | 21.0515 | 20.2364 | 20.3125 | 20.2368 | 20.2208 | 20.0638 |  | 20.2224 | 19.8728 | 20.1156 | 19.693 | 20.0903 | 20.3072 |  | 20.4095 |  |  | 20.2722 | 20.3811 | 20.6332 | [5 empty] | 21.9409 | 20.3398 | 21.6852 | 22.0587 | 19.5435 | 21.1824 | 21.8038 | 19.397 | 19.9351 | 21.1599 |  | 19.7754 | 20.9214 | 18.8618 | 19.7135 | 20.8085 | 19.4829 | 20.0463 | 19.0232 | 20.0794 | 19.1424 | 20.2048 | 18.8248 | 20.1063 | 21.0508 | 19.4261 | 19.7773 | 20.9956 | 18.9356 | 19.8509 | 20.8201 | 19.002 | 20.1277 | 19.3137 | 19.9371 | 18.8992 | 20.126 | -0.050774 | 20.9486 | 0.047787 | 0.015631 | -27.1778 | 3.097 | 6.37 | -0.05 | 0.84117 | -0.79845 | -8.1831 | 0.83738 | 0.78357 | -16.7094 | 3.9422 | 0.42442 | 0.42614 | 0.43029 | 0.36972 | 0.47298 | 0.44083 | 0.42842
42838.4172 | -265 | 22.904 | 22.8705 | 22.8505 | 22.7891 | 22.4175 | 21.7613 | 22.7299 | 21.8143 | 22.3779 | 22.3861 | 22.3631 | 22.0391 | 21.2541 | 22.2264 | 21.5942 | 21.7605 | 21.8905 | 21.0772 | 21.1747 | 21.3962 | 20.4749 | 20.6109 | 20.9081 | 21.8903 | 21.6489 | 21.2863 | 20.2797 | 20.4009 | 20.3722 | 22.0641 | 21.6685 | 21.1833 | 21.9895 | 21.7295 | 21.3463 | 19.9081 | 20.3939 |  | 20.5049 | 20.0345 | 20.1576 | 19.0879 |  | 16.7849 | 16.7515 | 16.4399 | 16.6866 | 16.8331 | 17.4079 | 17.9047 | 16.1553 | 16.8642 | 16.0314 | 16.8888 | 17.9172 | 44.4139 | 47.8609 | 43.3587 | 21.3511 |  |  | 0.29265 | -0.2984 | -47.463 | 0.55785 | 0.57511 | -197.8315 | 11.0674 | -0.41829 | 0.13067 | 0.031162 | -0.086682 | 8.8279 | 9.0579 | 1.9784 | 21.7846 | 22.005 | 22.2058 | 22.2663 | 22.0939 | 21.4106 | 20.2309 | 22.1928 | 22.368 | 22.4042 | 22.3615 | 21.9844 | 21.221 | 22.2689 | 17.4408 | 17.2566 | 16.23 | 16.1923 | 16.2459 | 17.0918 | 16.883 | 22.3833 | 22.1513 | 21.7052 | 22.0878 | 21.8047 | 21.3112 | 21.9488 | 21.5252 | 20.9092 | 20.1063 | 20.3126 | 19.8297 | 19.761 | -0.0007742 | -0.0060554 | 20.7318 | 22.0754 | 22.3823 | 20.1018 | 21.6755 | 22.1203 | 21.9592 | 21.7261 | 21.293 | 21.7971 | 21.4522 | 21.053 | 20.2458 | 20.315 | 20.2476 | 20.2305 | 20.0726 |  | 20.2265 | 19.8825 | 20.1222 | 19.6954 | 20.0983 | 20.3101 |  | 20.4172 |  |  | 20.2679 | 20.3848 | 20.6418 | [5 empty] | 21.9405 | 20.3535 | 21.6903 | 22.0642 | 19.5452 | 21.1845 | 21.8094 | 19.3883 | 19.9308 | 21.1582 |  | 19.7744 | 20.9183 | 18.8595 | 19.7171 | 20.8045 | 19.4802 | 20.0388 | 19.0234 | 20.0725 | 19.1383 | 20.1944 | 18.8273 | 20.1009 | 21.0537 | 19.4275 | 19.7799 | 20.9959 | 18.9419 | 19.8514 | 20.8229 | 18.997 | 20.1286 | 19.3085 | 19.9393 | 18.9037 | 20.128 | -0.19565 | 20.9496 | 0.048211 | 0.016371 | -27.099 | 3.097 | -2.61 | -0.21 | 0.64589 | -0.64817 | -8.1747 | 0.88624 | 0.90086 | -16.7083 | 3.9519 | 0.42431 | 0.42609 | 0.43049 | 0.36359 | 0.47377 | 0.44099 | 0.42894
42838.4172 | -264 | 22.9029 | 22.8718 | 22.8487 | 22.7853 | 22.4149 | 21.7567 | 22.7267 | 21.8113 | 22.3747 | 22.3866 | 22.3668 | 22.0374 | 21.2515 | 22.2238 | 21.5891 | 21.7595 | 21.8909 | 21.0782 | 21.1786 | 21.3853 | 20.4719 | 20.6194 | 20.9071 | 21.8888 | 21.6467 | 21.2778 | 20.2821 | 20.4003 | 20.3689 | 22.0684 | 21.6712 | 21.1845 | 21.9915 | 21.7363 | 21.352 | 19.9156 | 20.395 |  | 20.5134 | 20.0395 | 20.1593 | 19.0913 |  | 16.7753 | 16.7445 | 16.4361 | 16.6773 | 16.8358 | 17.4246 | 17.9253 | 16.1737 | 16.8671 | 16.0696 | 16.8895 | 17.9089 | 44.4179 | 47.8622 | 43.3604 | 21.348 |  |  | 0.53118 | -0.31482 | -48.2522 | 0.49477 | 0.12564 | -197.844 | 10.4661 | -0.27504 | -0.057314 | 0.067037 | -0.048317 | 8.8298 | 9.0595 | 1.9785 | 21.7919 | 22.0045 | 22.2012 | 22.2634 | 22.0964 | 21.426 | 20.2335 | 22.1979 | 22.3723 | 22.3998 | 22.3598 | 21.9875 | 21.2244 | 22.2635 | 17.4839 | 17.2976 | 16.2307 | 16.1965 | 16.2433 | 17.0926 | 16.8719 | 22.3891 | 22.1504 | 21.708 | 22.0836 | 21.7975 | 21.3076 | 21.9415 | 21.5245 | 20.91 | 20.1021 | 20.3146 | 19.8356 | 19.7557 | -0.017682 | -0.013473 | 20.7357 | 22.076 | 22.3837 | 20.1042 | 21.6807 | 22.1221 | 21.9554 | 21.7215 | 21.2873 | 21.7855 | 21.4489 | 21.0529 | 20.2499 | 20.3085 | 20.2474 | 20.2274 | 20.084 |  | 20.2242 | 19.9062 | 20.1207 | 19.6868 | 20.0898 | 20.3105 |  | 20.4212 |  |  | 20.2501 | 20.3786 | 20.6318 | [5 empty] | 21.9398 | 20.3407 | 21.6796 | 22.0618 | 19.5345 | 21.1777 | 21.8037 | 19.3761 | 19.9218 | 21.1471 |  | 19.7666 | 20.9135 | 18.8559 | 19.7096 | 20.8052 | 19.4764 | 20.0289 | 19.0251 | 20.0687 | 19.1368 | 20.1844 | 18.8373 | 20.1058 | 21.0565 | 19.4267 | 19.7836 | 20.9974 | 18.9446 | 19.8548 | 20.8318 | 18.9991 | 20.125 | 19.3148 | 19.9399 | 18.9059 | 20.1316 | -0.039644 | 20.948 | 0.048346 | 0.016727 | -27.0552 | 3.097 | 13 | -0.07 | 0.87017 | -0.66577 | -8.2422 | 0.83462 | 0.42108 | -16.7093 | 3.8432 | 0.42392 | 0.42539 | 0.43045 | 0.35889 | 0.4724 | 0.44116 | 0.42894
42838.4172 | -263 | 22.9116 | 22.8755 | 22.8559 | 22.7818 | 22.4136 | 21.752 | 22.7163 | 21.814 | 22.3777 | 22.3901 | 22.3703 | 22.0381 | 21.2553 | 22.2225 | 21.588 | 21.7566 | 21.8872 | 21.0828 | 21.1706 | 21.3889 | 20.4773 | 20.6144 | 20.9054 | 21.8913 | 21.6495 | 21.2762 | 20.2772 | 20.3997 | 20.3684 | 22.0694 | 21.6641 | 21.1835 | 22.0004 | 21.7361 | 21.357 | 19.9173 | 20.3929 |  | 20.5101 | 20.0426 | 20.1633 | 19.0963 |  | 16.7774 | 16.7448 | 16.4328 | 16.6782 | 16.8279 | 17.4167 | 17.9147 | 16.1707 | 16.8712 | 16.1013 | 16.8902 | 17.9091 | 44.4155 | 47.8765 | 43.3635 | 21.3475 |  |  | 0.4589 | -0.21034 | -48.6694 | 0.47637 | 0.23144 | -197.8355 | 10.7119 | -0.22641 | -0.042524 | 0.08571 | -0.054046 | 8.8289 | 9.0588 | 1.9781 | 21.7895 | 22.009 | 22.2093 | 22.2675 | 22.0974 | 21.4176 | 20.2398 | 22.203 | 22.3718 | 22.4067 | 22.3575 | 21.9882 | 21.2248 | 22.2628 | 17.5169 | 17.299 | 16.2377 | 16.1988 | 16.2358 | 17.092 | 16.8761 | 22.3873 | 22.1544 | 21.7101 | 22.0862 | 21.803 | 21.3043 | 21.9422 | 21.5306 | 20.9121 | 20.1077 | 20.317 | 19.8322 | 19.7519 | -0.093569 | 0.0002212 | 20.7328 | 22.0773 | 22.3799 | 20.1015 | 21.6807 | 22.1137 | 21.9443 | 21.7112 | 21.2804 | 21.7857 | 21.455 | 21.0483 | 20.2528 | 20.313 | 20.2486 | 20.2256 | 20.09 |  | 20.2269 | 19.9042 | 20.122 | 19.6794 | 20.0919 | 20.3142 |  | 20.4202 |  |  | 20.2677 | 20.386 | 20.6342 | [5 empty] | 21.9511 | 20.3492 | 21.6823 | 22.0676 | 19.5401 | 21.1843 | 21.812 | 19.386 | 19.9249 | 21.1488 |  | 19.7689 | 20.9172 | 18.8592 | 19.7089 | 20.807 | 19.4757 | 20.0298 | 19.0255 | 20.0646 | 19.1347 | 20.1834 | 18.8407 | 20.1106 | 21.0603 | 19.4291 | 19.7833 | 20.9933 | 18.957 | 19.8512 | 20.8312 | 18.9908 | 20.1243 | 19.3181 | 19.9409 | 18.9052 | 20.1327 | -0.080083 | 20.9498 | 0.046908 | 0.014164 | -27.0591 | 3.097 | 0.08 | -0.16 | 0.8088 | -0.54419 | -8.2778 | 0.81895 | 0.57149 | -16.7087 | 3.888 | 0.42384 | 0.42549 | 0.43072 | 0.35516 | 0.47211 | 0.44107 | 0.42924
42838.4172 | -262 | 22.8948 | 22.8603 | 22.8492 | 22.7758 | 22.4051 | 21.7435 | 22.7175 | 21.8059 | 22.379 | 22.3769 | 22.351 | 22.0372 | 21.2504 | 22.2171 | 21.5914 | 21.7608 | 21.8968 | 21.0769 | 21.1782 | 21.4023 | 20.4778 | 20.6158 | 20.9068 | 21.8899 | 21.6545 | 21.279 | 20.2818 | 20.4009 | 20.3684 | 22.0746 | 21.6712 | 21.1816 | 21.9982 | 21.7378 | 21.3507 | 19.9188 | 20.3828 |  | 20.5087 | 20.048 | 20.156 | 19.0896 |  | 16.7692 | 16.7389 | 16.4223 | 16.6742 | 16.8169 | 17.3965 | 17.8818 | 16.144 | 16.8612 | 16.1116 | 16.8893 | 17.9102 | 44.4228 | 47.8828 | 43.3733 | 21.3483 |  |  | 0.43261 | -0.31351 | -49.0282 | 0.32523 | 0.083584 | -197.844 | 10.4596 | -0.30592 | -0.35408 | 0.017315 | -0.11012 | 8.8284 | 9.0579 | 1.9792 | 21.7864 | 22.0049 | 22.2027 | 22.2657 | 22.084 | 21.413 | 20.2305 | 22.196 | 22.3623 | 22.4036 | 22.3519 | 21.9815 | 21.2151 | 22.2643 | 17.5244 | 17.2782 | 16.2574 | 16.2046 | 16.2303 | 17.0914 | 16.8709 | 22.3897 | 22.1563 | 21.7217 | 22.101 | 21.8086 | 21.3141 | 21.9525 | 21.5367 | 20.9106 | 20.1137 | 20.3244 | 19.8376 | 19.7659 | 0.013971 | 0.12423 | 20.7395 | 22.0692 | 22.3731 | 20.0967 | 21.6779 | 22.1167 | 21.9422 | 21.7166 | 21.2754 | 21.786 | 21.4539 | 21.0434 | 20.2492 | 20.3121 | 20.2353 | 20.2252 | 20.0882 |  | 20.2203 | 19.9134 | 20.116 | 19.6779 | 20.0922 | 20.3146 |  | 20.4119 |  |  | 20.2611 | 20.3795 | 20.6259 | [5 empty] | 21.9465 | 20.3473 | 21.6819 | 22.0621 | 19.5351 | 21.1794 | 21.808 | 19.3821 | 19.9188 | 21.1474 |  | 19.7697 | 20.9135 | 18.8534 | 19.7114 | 20.8045 | 19.4705 | 20.0356 | 19.0164 | 20.0605 | 19.13 | 20.1821 | 18.8385 | 20.1089 | 21.0545 | 19.4242 | 19.7808 | 20.9932 | 18.9588 | 19.8447 | 20.8218 | 18.9892 | 20.1249 | 19.3194 | 19.9338 | 18.9046 | 20.1251 | -0.14798 | 20.9495 | 0.047719 | 0.013707 | -27.011 | 3.097 | -7.91 | -0.1 | 0.7853 | -0.66437 | -8.3082 | 0.67667 | 0.34343 | -16.7085 | 3.8418 | 0.42367 | 0.42503 | 0.43078 | 0.35426 | 0.46931 | 0.44131 | 0.42905
42838.4173 | -261 | 22.8997 | 22.8698 | 22.851 | 22.7802 | 22.4078 | 21.7466 | 22.7177 | 21.8133 | 22.3757 | 22.3841 | 22.3588 | 22.0294 | 21.2469 | 22.215 | 21.5934 | 21.7615 | 21.8943 | 21.083 | 21.1722 | 21.3963 | 20.4751 | 20.6136 | 20.9079 | 21.885 | 21.6448 | 21.2753 | 20.2841 | 20.4007 | 20.3754 | 22.0748 | 21.6654 | 21.1893 | 21.9912 | 21.7376 | 21.3575 | 19.9197 | 20.3806 |  | 20.5167 | 20.0404 | 20.1537 | 19.0931 |  | 16.7765 | 16.739 | 16.429 | 16.6816 | 16.8272 | 17.3898 | 17.8614 | 16.1431 | 16.8637 | 16.1175 | 16.894 | 17.9129 | 44.4383 | 47.8887 | 43.394 | 21.3555 |  |  | 0.48781 | -0.41536 | -49.0716 | 0.13795 | 0.25444 | -197.8657 | 10.8262 | -0.3184 | -0.15714 | 0.20257 | -0.10092 | 8.8295 | 9.0591 | 1.9792 | 21.7869 | 22.0064 | 22.1994 | 22.2666 | 22.0829 | 21.4165 | 20.2278 | 22.1982 | 22.3644 | 22.4035 | 22.3552 | 21.9833 | 21.2136 | 22.2664 | 17.5204 | 17.2742 | 16.3181 | 16.231 | 16.2423 | 17.0954 | 16.879 | 22.3943 | 22.1512 | 21.713 | 22.0927 | 21.8043 | 21.3041 | 21.952 | 21.5357 | 20.9122 | 20.1039 | 20.3203 | 19.831 | 19.7604 | -0.054643 | 0.14439 | 20.7413 | 22.0705 | 22.3789 | 20.0845 | 21.6766 | 22.1224 | 21.9446 | 21.71 | 21.2852 | 21.7825 | 21.452 | 21.0489 | 20.2541 | 20.3113 | 20.2327 | 20.221 | 20.0891 |  | 20.2221 | 19.9221 | 20.1205 | 19.6854 | 20.0941 | 20.3224 |  | 20.4162 |  |  | 20.255 | 20.3833 | 20.6246 | [5 empty] | 21.9486 | 20.3519 | 21.6767 | 22.057 | 19.5402 | 21.1854 | 21.807 | 19.394 | 19.9383 | 21.1575 |  | 19.7767 | 20.926 | 18.8614 | 19.7235 | 20.8136 | 19.4799 | 20.0483 | 19.0301 | 20.0687 | 19.1313 | 20.1884 | 18.8294 | 20.1086 | 21.0564 | 19.4178 | 19.7837 | 20.9921 | 18.9482 | 19.8496 | 20.815 | 18.9946 | 20.125 | 19.3144 | 19.9383 | 18.9012 | 20.1245 | 0.063123 | 20.9488 | 0.048266 | 0.015464 | -27.0123 | 3.097 | -13.78 | -0.04 | 0.8339 | -0.76471 | -8.3119 | 0.4407 | 0.59918 | -16.7092 | 3.9085 | 0.4237 | 0.42494 | 0.43063 | 0.35516 | 0.46352 | 0.44124 | 0.42888
42838.4173 | -260 | 22.9003 | 22.8653 | 22.8541 | 22.7789 | 22.4065 | 21.7446 | 22.7169 | 21.8043 | 22.3668 | 22.3764 | 22.3561 | 22.0243 | 21.243 | 22.2118 | 21.5893 | 21.765 | 21.8885 | 21.076 | 21.1705 | 21.3976 | 20.471 | 20.6124 | 20.9019 | 21.8832 | 21.6457 | 21.2782 | 20.2848 | 20.4007 | 20.3758 | 22.0696 | 21.6662 | 21.187 | 21.9883 | 21.7306 | 21.3517 | 19.9132 | 20.3751 |  | 20.5009 | 20.0427 | 20.1571 | 19.0846 |  | 16.7799 | 16.7473 | 16.4364 | 16.7015 | 16.8406 | 17.3879 | 17.8594 | 16.1335 | 16.8653 | 16.1336 | 16.8958 | 17.9251 | 44.4473 | 47.8911 | 43.4037 | 21.361 |  |  | 0.39319 | -0.52313 | -49.0479 | 0.15832 | 0.3392 | -197.848 | 10.0699 | -0.25926 | -0.050113 | 0.019413 | -0.069496 | 8.8283 | 9.0579 | 1.9787 | 21.7853 | 22.0061 | 22.197 | 22.2639 | 22.0911 | 21.4113 | 20.2272 | 22.1997 | 22.3616 | 22.3964 | 22.3514 | 21.9798 | 21.2173 | 22.259 | 17.5026 | 17.2591 | 16.3503 | 16.2335 | 16.2398 | 17.0941 | 16.8775 | 22.3875 | 22.1534 | 21.7086 | 22.0919 | 21.8055 | 21.3124 | 21.9472 | 21.5298 | 20.9152 | 20.112 | 20.322 | 19.8338 | 19.7506 | 0.020459 | -0.01043 | 20.7431 | 22.071 | 22.3778 | 20.0846 | 21.6752 | 22.1255 | 21.9542 | 21.717 | 21.2808 | 21.7873 | 21.4537 | 21.0462 | 20.2485 | 20.3152 | 20.2454 | 20.2185 | 20.0955 |  | 20.221 | 19.94 | 20.1191 | 19.6889 | 20.095 | 20.3232 |  | 20.4149 |  |  | 20.2664 | 20.3785 | 20.6292 | [5 empty] | 21.9493 | 20.3481 | 21.6838 | 22.0602 | 19.5517 | 21.183 | 21.8048 | 19.3982 | 19.9381 | 21.1604 |  | 19.7926 | 20.9304 | 18.8609 | 19.7173 | 20.8173 | 19.4761 | 20.0348 | 19.0371 | 20.0737 | 19.1267 | 20.1872 | 18.8345 | 20.1182 | 21.0628 | 19.4277 | 19.7856 | 20.998 | 18.9572 | 19.8602 | 20.8289 | 18.9954 | 20.1339 | 19.309 | 19.9419 | 18.905 | 20.1257 | -0.18656 | 20.9474 | 0.049138 | 0.015631 | -27.0181 | 3.097 | -10.77 | -0.05 | 0.74867 | -0.85821 | -8.31 | 0.47213 | 0.69183 | -16.7084 | 3.7695 | 0.42349 | 0.42439 | 0.43056 | 0.35699 | 0.45976 | 0.44126 | 0.42942
42838.4173 | -259 | 22.906 | 22.8705 | 22.8559 | 22.7881 | 22.4131 | 21.7574 | 22.7238 | 21.8133 | 22.3715 | 22.381 | 22.363 | 22.0341 | 21.2481 | 22.2209 | 21.59 | 21.7629 | 21.8895 | 21.0801 | 21.1829 | 21.4003 | 20.4703 | 20.6205 | 20.9171 | 21.8816 | 21.6493 | 21.2872 | 20.2924 | 20.3932 | 20.3806 | 22.069 | 21.6678 | 21.1859 | 21.9944 | 21.7324 | 21.3513 | 19.914 | 20.374 |  | 20.5032 | 20.0447 | 20.1529 | 19.077 |  | 16.77 | 16.7341 | 16.4365 | 16.7121 | 16.8497 | 17.3711 | 17.8717 | 16.1199 | 16.8581 | 16.119 | 16.8927 | 17.9219 | 44.4431 | 47.897 | 43.4082 | 21.3508 |  |  | 0.19277 | -0.25634 | -49.5296 | 0.18395 | 0.22421 | -197.8434 | 10.5049 | -0.40054 | 0.026754 | -0.051919 | 0.068863 | 8.8294 | 9.0591 | 1.9782 | 21.7936 | 22.0093 | 22.2055 | 22.2678 | 22.0929 | 21.4184 | 20.2323 | 22.2008 | 22.3769 | 22.4036 | 22.3586 | 21.9941 | 21.2175 | 22.2696 | 17.5039 | 17.251 | 16.3371 | 16.2425 | 16.2488 | 17.0942 | 16.8788 | 22.3849 | 22.1489 | 21.7032 | 22.0798 | 21.7995 | 21.304 | 21.9438 | 21.5283 | 20.9018 | 20.1068 | 20.3087 | 19.8302 | 19.7431 | 0.011415 | -0.14452 | 20.7435 | 22.0719 | 22.385 | 20.0958 | 21.6791 | 22.1183 | 21.9552 | 21.7175 | 21.2826 | 21.7955 | 21.4462 | 21.0488 | 20.2527 | 20.3175 | 20.2384 | 20.2203 | 20.0914 |  | 20.2208 | 19.9443 | 20.1186 | 19.6733 | 20.0887 | 20.3224 |  | 20.4094 |  |  | 20.2634 | 20.3706 | 20.6283 | [5 empty] | 21.947 | 20.3471 | 21.6871 | 22.0611 | 19.5478 | 21.182 | 21.8052 | 19.3974 | 19.9387 | 21.1604 |  | 19.7916 | 20.9199 | 18.8612 | 19.7053 | 20.8169 | 19.4788 | 20.0395 | 19.033 | 20.0727 | 19.1288 | 20.1914 | 18.8387 | 20.1166 | 21.0564 | 19.4252 | 19.7834 | 20.9814 | 18.9487 | 19.8525 | 20.8155 | 18.9897 | 20.1242 | 19.3055 | 19.9302 | 18.9021 | 20.1203 | -0.08064 | 20.9469 | 0.048696 | 0.014433 | -27.0592 | 3.097 | 3.37 | -0.09 | 0.52421 | -0.60074 | -8.3505 | 0.5089 | 0.56245 | -16.7077 | 3.8499 | 0.42359 | 0.42426 | 0.43078 | 0.35686 | 0.46138 | 0.4415 | 0.42945
42838.4173 | -258 | 22.9002 | 22.8691 | 22.855 | 22.7863 | 22.4089 | 21.752 | 22.72 | 21.8081 | 22.372 | 22.3795 | 22.3574 | 22.0341 | 21.2498 | 22.2185 | 21.5865 | 21.7594 | 21.8842 | 21.0761 | 21.1702 | 21.3914 | 20.4708 | 20.6175 | 20.9099 | 21.8789 | 21.6481 | 21.285 | 20.2853 | 20.3921 | 20.3655 | 22.0698 | 21.6649 | 21.1836 | 21.991 | 21.7278 | 21.3496 | 19.9067 | 20.3681 |  | 20.5109 | 20.0413 | 20.1499 | 19.0701 |  | 16.7793 | 16.7327 | 16.4375 | 16.7318 | 16.8566 | 17.3625 | 17.8856 | 16.1175 | 16.8637 | 16.1174 | 16.8963 | 17.9172 | 44.4349 | 47.9022 | 43.4209 | 21.35 |  |  | 0.58046 | -0.33782 | -49.0302 | 0.33443 | 0.14601 | -197.867 | 10.2657 | -0.44128 | -0.004577 | 0.012489 | 0.024248 | 8.8299 | 9.0598 | 1.978 | 21.7958 | 22.0057 | 22.2018 | 22.2698 | 22.0848 | 21.4159 | 20.2229 | 22.1999 | 22.381 | 22.4116 | 22.3583 | 21.9819 | 21.2199 | 22.265 | 17.4866 | 17.2542 | 16.3251 | 16.2432 | 16.258 | 17.0931 | 16.8754 | 22.3852 | 22.1517 | 21.7089 | 22.0821 | 21.8022 | 21.3047 | 21.9426 | 21.5272 | 20.9064 | 20.1049 | 20.3153 | 19.829 | 19.7468 | 0.10205 | -0.036678 | 20.7533 | 22.0768 | 22.3792 | 20.0961 | 21.68 | 22.1142 | 21.955 | 21.7199 | 21.2874 | 21.792 | 21.4494 | 21.0537 | 20.2565 | 20.3273 | 20.243 | 20.2239 | 20.0849 |  | 20.211 | 19.9615 | 20.1191 | 19.6688 | 20.0901 | 20.3246 |  | 20.4118 |  |  | 20.2638 | 20.3681 | 20.6224 | [5 empty] | 21.9472 | 20.3448 | 21.6799 | 22.0588 | 19.5492 | 21.1795 | 21.7972 | 19.3787 | 19.9324 | 21.1549 |  | 19.7826 | 20.9217 | 18.8596 | 19.7065 | 20.8139 | 19.4739 | 20.0324 | 19.0351 | 20.0655 | 19.1357 | 20.1736 | 18.8503 | 20.1167 | 21.0636 | 19.4288 | 19.7891 | 20.9915 | 18.9527 | 19.8567 | 20.8206 | 19.0029 | 20.1212 | 19.3106 | 19.9367 | 18.9002 | 20.1261 | -0.11737 | 20.9469 | 0.047688 | 0.013351 | -26.9814 | 3.097 | -3.86 | -0.19 | 0.90964 | -0.68964 | -8.3083 | 0.68617 | 0.45388 | -16.7084 | 3.8058 | 0.42345 | 0.4238 | 0.43096 | 0.35866 | 0.46231 | 0.44145 | 0.42928
42838.4173 | -257 | 22.9014 | 22.8668 | 22.855 | 22.7795 | 22.4068 | 21.7507 | 22.718 | 21.8127 | 22.373 | 22.3784 | 22.3683 | 22.0362 | 21.256 | 22.224 | 21.5935 | 21.7637 | 21.8875 | 21.0803 | 21.1825 | 21.3943 | 20.4754 | 20.6195 | 20.9093 | 21.8859 | 21.6545 | 21.2868 | 20.2893 | 20.3985 | 20.3745 | 22.0663 | 21.6651 | 21.1845 | 21.9912 | 21.7324 | 21.354 | 19.9154 | 20.3696 |  | 20.5061 | 20.0403 | 20.1458 | 19.0639 |  | 16.7748 | 16.7378 | 16.4441 | 16.7423 | 16.872 | 17.3612 | 17.8722 | 16.1389 | 16.8686 | 16.0937 | 16.8954 | 17.9115 | 44.427 | 47.9129 | 43.4318 | 21.349 |  |  | 0.35639 | -0.37265 | -49.366 | 0.20498 | 0.050728 | -197.8355 | 10.57 | -0.53525 | 0.0030124 | -0.045625 | -0.0004032 | 8.8288 | 9.0583 | 1.9789 | 21.791 | 22.0158 | 22.1986 | 22.263 | 22.0944 | 21.4143 | 20.2293 | 22.1998 | 22.3745 | 22.4109 | 22.3524 | 21.9854 | 21.209 | 22.2681 | 17.479 | 17.2645 | 16.3151 | 16.2425 | 16.2667 | 17.085 | 16.8696 | 22.3925 | 22.1519 | 21.7112 | 22.0844 | 21.8027 | 21.3089 | 21.9503 | 21.5275 | 20.9129 | 20.1056 | 20.3225 | 19.8345 | 19.7599 | -0.0080484 | -0.22288 | 20.7491 | 22.0785 | 22.3849 | 20.0932 | 21.672 | 22.1193 | 21.9511 | 21.7152 | 21.2889 | 21.7888 | 21.4588 | 21.0513 | 20.2565 | 20.3146 | 20.2448 | 20.2264 | 20.091 |  | 20.213 | 19.9666 | 20.1234 | 19.6698 | 20.0894 | 20.3264 |  | 20.4082 |  |  | 20.2711 | 20.3502 | 20.6304 | [5 empty] | 21.9444 | 20.3417 | 21.6827 | 22.0584 | 19.547 | 21.1738 | 21.8009 | 19.4002 | 19.929 | 21.1577 |  | 19.7859 | 20.9227 | 18.8691 | 19.7137 | 20.8113 | 19.4689 | 20.0355 | 19.0365 | 20.0636 | 19.1292 | 20.1759 | 18.8542 | 20.1216 | 21.0674 | 19.4404 | 19.7903 | 21.0022 | 18.9652 | 19.8565 | 20.824 | 19.0075 | 20.1175 | 19.3145 | 19.9445 | 18.9093 | 20.1131 | -0.20975 | 20.9472 | 0.048401 | 0.015007 | -27.0979 | 3.097 | 3.98 | -0.09 | 0.71277 | -0.72432 | -8.3367 | 0.5372 | 0.26753 | -16.7071 | 3.8618 | 0.42335 | 0.4238 | 0.43091 | 0.35854 | 0.46275 | 0.44191 | 0.42894
42838.4173 | -256 | 22.9058 | 22.8721 | 22.8534 | 22.7769 | 22.4095 | 21.7471 | 22.7116 | 21.8119 | 22.3697 | 22.3841 | 22.3623 | 22.033 | 21.2579 | 22.2243 | 21.5957 | 21.7572 | 21.8824 | 21.0824 | 21.1772 | 21.3892 | 20.4743 | 20.6193 | 20.91 | 21.8849 | 21.6497 | 21.2791 | 20.2877 | 20.397 | 20.3662 | 22.0779 | 21.6823 | 21.1948 | 22.0037 | 21.7454 | 21.3632 | 19.9217 | 20.3834 |  | 20.517 | 20.0489 | 20.1535 | 19.0775 |  | 16.7765 | 16.7385 | 16.4445 | 16.7576 | 16.8642 | 17.3346 | 17.8554 | 16.1451 | 16.8745 | 16.1138 | 16.8976 | 17.9176 | 44.4356 | 47.9138 | 43.4393 | 21.3511 |  |  | 0.46218 | -0.35294 | -49.3515 | 0.39225 | 0.19332 | -197.8407 | 9.9635 | -0.5576 | -0.21552 | 0.21977 | -0.016374 | 8.8282 | 9.058 | 1.9794 | 21.7884 | 22.0034 | 22.1984 | 22.2658 | 22.0914 | 21.4121 | 20.2233 | 22.1995 | 22.3654 | 22.4014 | 22.35 | 21.9801 | 21.2122 | 22.2675 | 17.4878 | 17.3024 | 16.3074 | 16.2368 | 16.2574 | 17.0935 | 16.8677 | 22.394 | 22.1447 | 21.7105 | 22.0909 | 21.7975 | 21.3049 | 21.9391 | 21.528 | 20.9049 | 20.1079 | 20.3142 | 19.8266 | 19.7509 | -0.0021504 | -0.03858 | 20.7517 | 22.0792 | 22.3865 | 20.0928 | 21.6738 | 22.1162 | 21.9545 | 21.7275 | 21.2882 | 21.7941 | 21.4585 | 21.0537 | 20.2607 | 20.3185 | 20.2446 | 20.2271 | 20.0898 |  | 20.2201 | 19.9759 | 20.1241 | 19.6705 | 20.0876 | 20.3328 |  | 20.4145 |  |  | 20.2724 | 20.3461 | 20.6295 | [5 empty] | 21.9362 | 20.3431 | 21.6753 | 22.0583 | 19.5405 | 21.1754 | 21.8012 | 19.4006 | 19.9321 | 21.1677 |  | 19.7996 | 20.9193 | 18.8718 | 19.7039 | 20.8158 | 19.4688 | 20.0392 | 19.0413 | 20.068 | 19.1332 | 20.1792 | 18.8542 | 20.1196 | 21.0662 | 19.436 | 19.7857 | 20.999 | 18.9615 | 19.8526 | 20.8237 | 19.0066 | 20.1175 | 19.3156 | 19.9231 | 18.9008 | 20.1135 | -0.070251 | 20.9463 | 0.049003 | 0.01574 | -27.0717 | 3.097 | -11.75 | -0.1 | 0.81169 | -0.70491 | -8.3355 | 0.74313 | 0.52224 | -16.7065 | 3.7492 | 0.42362 | 0.42356 | 0.43082 | 0.35857 | 0.46338 | 0.44174 | 0.42927
42838.4173 | -255 | 22.908 | 22.872 | 22.8546 | 22.7831 | 22.411 | 21.7563 | 22.7207 | 21.8072 | 22.3696 | 22.381 | 22.3576 | 22.0382 | 21.2517 | 22.2121 | 21.6003 | 21.7576 | 21.8885 | 21.0802 | 21.1783 | 21.3931 | 20.4755 | 20.6161 | 20.9115 | 21.8856 | 21.65 | 21.2749 | 20.2913 | 20.4019 | 20.3797 | 22.0649 | 21.6741 | 21.1968 | 21.9949 | 21.7417 | 21.3445 | 19.9196 | 20.3769 |  | 20.5114 | 20.0418 | 20.1464 | 19.0739 |  | 16.7714 | 16.7415 | 16.4472 | 16.7537 | 16.868 | 17.3366 | 17.8691 | 16.1322 | 16.8734 | 16.1599 | 16.8999 | 17.9161 | 44.4633 | 47.9301 | 43.4551 | 21.3545 |  |  | 0.35705 | -0.36739 | -49.4047 | 0.50331 | 0.17558 | -197.7947 | 10.4931 | -0.42814 | -0.18478 | -0.024226 | -0.075225 | 8.8282 | 9.0578 | 1.979 | 21.7808 | 22.0052 | 22.2005 | 22.262 | 22.093 | 21.4155 | 20.2298 | 22.1974 | 22.3666 | 22.4034 | 22.3531 | 21.9834 | 21.2198 | 22.2672 | 17.4996 | 17.3094 | 16.3077 | 16.2368 | 16.2704 | 17.0874 | 16.8664 | 22.3874 | 22.1533 | 21.7031 | 22.0856 | 21.801 | 21.3025 | 21.9452 | 21.5343 | 20.9094 | 20.1006 | 20.3159 | 19.8293 | 19.7525 | 0.074917 | -0.085559 | 20.7444 | 22.0725 | 22.3815 | 20.0854 | 21.6728 | 22.1197 | 21.9538 | 21.7183 | 21.2854 | 21.7849 | 21.4529 | 21.0489 | 20.2586 | 20.3249 | 20.2405 | 20.2267 | 20.0889 |  | 20.2231 | 19.9776 | 20.1173 | 19.6666 | 20.0854 | 20.3306 |  | 20.4143 |  |  | 20.2865 | 20.35 | 20.6268 | [5 empty] | 21.9383 | 20.3443 | 21.6806 | 22.0633 | 19.5367 | 21.1782 | 21.7985 | 19.3935 | 19.9289 | 21.1631 |  | 19.7871 | 20.9153 | 18.8707 | 19.7044 | 20.8079 | 19.4629 | 20.0342 | 19.0418 | 20.0572 | 19.1247 | 20.1775 | 18.8582 | 20.1257 | 21.0728 | 19.4368 | 19.7861 | 20.994 | 18.9629 | 19.8506 | 20.8266 | 19.0046 | 20.12 | 19.3161 | 19.9324 | 18.898 | 20.119 | -0.094181 | 20.9458 | 0.049704 | 0.01693 | -27.0237 | 3.097 | -24.61 | -0.02 | 0.71344 | -0.7192 | -8.3401 | 0.84178 | 0.4977 | -16.7047 | 3.8475 | 0.42374 | 0.42329 | 0.43086 | 0.35653 | 0.4632 | 0.44177 | 0.42898
42838.4173 | -254 | 22.894 | 22.8663 | 22.8512 | 22.7788 | 22.4096 | 21.7435 | 22.7231 | 21.8099 | 22.3669 | 22.3783 | 22.3601 | 22.0264 | 21.2496 | 22.212 | 21.6018 | 21.7642 | 21.8927 | 21.0763 | 21.185 | 21.4021 | 20.4782 | 20.6189 | 20.9151 | 21.889 | 21.6472 | 21.28 | 20.2906 | 20.4034 | 20.3847 | 22.0673 | 21.6674 | 21.1899 | 21.996 | 21.732 | 21.3506 | 19.9198 | 20.3809 |  | 20.5124 | 20.0403 | 20.1405 | 19.0651 |  | 16.7687 | 16.7318 | 16.438 | 16.7583 | 16.8677 | 17.3521 | 17.8874 | 16.1058 | 16.8632 | 16.1827 | 16.9057 | 17.9159 | 44.4894 | 47.9385 | 43.4717 | 21.3537 |  |  | 0.50884 | -0.099949 | -49.889 | 0.7287 | 0.15258 | -197.8545 | 10.0246 | -0.44457 | -0.25911 | -0.15976 | -0.13581 | 8.8294 | 9.0591 | 1.9786 | 21.7836 | 22.0061 | 22.2029 | 22.2617 | 22.0944 | 21.4162 | 20.2259 | 22.1937 | 22.3682 | 22.4059 | 22.3589 | 21.9816 | 21.218 | 22.2732 | 17.5136 | 17.2991 | 16.2928 | 16.2353 | 16.2675 | 17.0868 | 16.8681 | 22.3828 | 22.1491 | 21.7045 | 22.0875 | 21.8027 | 21.3027 | 21.9361 | 21.522 | 20.9046 | 20.0944 | 20.3208 | 19.8334 | 19.7531 | -0.060541 | -0.04809 | 20.7535 | 22.0756 | 22.3824 | 20.0942 | 21.679 | 22.1218 | 21.9525 | 21.7177 | 21.2894 | 21.7939 | 21.4543 | 21.0508 | 20.258 | 20.3261 | 20.2306 | 20.2253 | 20.0884 |  | 20.2284 | 20.001 | 20.1239 | 19.6776 | 20.1038 | 20.3431 |  | 20.4224 |  |  | 20.2786 | 20.342 | 20.6203 | [5 empty] | 21.9388 | 20.3456 | 21.6784 | 22.0608 | 19.5319 | 21.1784 | 21.807 | 19.4017 | 19.9359 | 21.1692 |  | 19.795 | 20.9266 | 18.8793 | 19.7166 | 20.8179 | 19.47 | 20.0424 | 19.0473 | 20.0735 | 19.13 | 20.1748 | 18.8496 | 20.1243 | 21.0749 | 19.4411 | 19.7926 | 20.9997 | 18.9606 | 19.8489 | 20.8226 | 19.0096 | 20.1158 | 19.3087 | 19.9318 | 18.9015 | 20.1257 | -0.067283 | 20.9465 | 0.049194 | 0.015399 | -27.1219 | 3.097 | 5.35 | -0.04 | 0.8517 | -0.37512 | -8.3807 | 1.0129 | 0.46398 | -16.7076 | 3.7607 | 0.42393 | 0.42286 | 0.43117 | 0.35491 | 0.46505 | 0.44202 | 0.42876
42838.4173 | -253 | 22.903 | 22.8647 | 22.8543 | 22.7734 | 22.3995 | 21.7473 | 22.7185 | 21.8073 | 22.3657 | 22.3744 | 22.3574 | 22.0319 | 21.2404 | 22.2145 | 21.5888 | 21.7579 | 21.8792 | 21.08 | 21.1729 | 21.3983 | 20.4703 | 20.6106 | 20.9009 | 21.8772 | 21.6395 | 21.2765 | 20.2836 | 20.3948 | 20.3784 | 22.0707 | 21.6728 | 21.1881 | 21.9986 | 21.739 | 21.3515 | 19.9206 | 20.3849 |  | 20.511 | 20.0381 | 20.1478 | 19.0598 |  | 16.7718 | 16.7357 | 16.4564 | 16.7643 | 16.8897 | 17.3873 | 17.8908 | 16.1014 | 16.872 | 16.187 | 16.9003 | 17.9174 | 44.5332 | 47.9546 | 43.4793 | 21.3493 |  |  | 0.38924 | -0.11966 | -49.6203 | 0.7241 | 0.12958 | -197.8506 | 10.1402 | -0.3322 | 0.054387 | 0.15746 | 0.037962 | 8.8292 | 9.0587 | 1.9787 | 21.7963 | 22.0166 | 22.2021 | 22.2699 | 22.0918 | 21.4172 | 20.2308 | 22.199 | 22.3746 | 22.4107 | 22.3659 | 21.9803 | 21.214 | 22.2709 | 17.5221 | 17.25 | 16.2819 | 16.2456 | 16.2758 | 17.0864 | 16.8606 | 22.3938 | 22.1555 | 21.7086 | 22.0926 | 21.8032 | 21.3038 | 21.9471 | 21.526 | 20.913 | 20.1097 | 20.3247 | 19.8403 | 19.7568 | -0.21133 | 0.090376 | 20.7535 | 22.0689 | 22.3777 | 20.0984 | 21.6711 | 22.1217 | 21.957 | 21.7134 | 21.2872 | 21.7914 | 21.4495 | 21.0484 | 20.2547 | 20.3218 | 20.24 | 20.22 | 20.0833 |  | 20.2219 | 20.0002 | 20.1182 | 19.6744 | 20.0891 | 20.3329 |  | 20.4178 |  |  | 20.2806 | 20.3301 | 20.6198 | [5 empty] | 21.9448 | 20.3458 | 21.6779 | 22.0611 | 19.5318 | 21.1828 | 21.8095 | 19.4032 | 19.9448 | 21.1706 |  | 19.7982 | 20.9311 | 18.8867 | 19.7179 | 20.8131 | 19.4655 | 20.0483 | 19.0568 | 20.0728 | 19.1332 | 20.1721 | 18.8501 | 20.1228 | 21.0714 | 19.4402 | 19.7971 | 20.9978 | 18.9653 | 19.8537 | 20.8249 | 19.0087 | 20.1192 | 19.3133 | 19.9346 | 18.8998 | 20.1247 | -0.065429 | 20.9467 | 0.048149 | 0.013126 | -27.0669 | 3.0971 | -16.54 | -0.17 | 0.74491 | -0.41045 | -8.3581 | 1.0097 | 0.42761 | -16.7085 | 3.7826 | 0.42386 | 0.42269 | 0.43076 | 0.35393 | 0.46539 | 0.44219 | 0.42917
42838.4174 | -252 | 22.9045 | 22.8635 | 22.8461 | 22.768 | 22.4049 | 21.744 | 22.7158 | 21.8072 | 22.367 | 22.3727 | 22.358 | 22.0261 | 21.2489 | 22.2097 | 21.584 | 21.755 | 21.8818 | 21.0771 | 21.1696 | 21.3934 | 20.4657 | 20.6095 | 20.8972 | 21.8773 | 21.6403 | 21.2797 | 20.2801 | 20.3909 | 20.3747 | 22.0677 | 21.6695 | 21.186 | 21.9991 | 21.738 | 21.3538 | 19.9214 | 20.3872 |  | 20.5176 | 20.0403 | 20.146 | 19.0487 |  | 16.7756 | 16.7414 | 16.4503 | 16.7541 | 16.897 | 17.3916 | 17.8855 | 16.0951 | 16.8723 | 16.2041 | 16.8954 | 17.9234 | 44.5667 | 47.9629 | 43.5151 | 21.3512 |  |  | 0.29527 | -0.2984 | -50.3878 | 0.59925 | 0.29452 | -197.8539 | 9.9865 | -0.42157 | 0.14468 | 0.086339 | 0.15914 | 8.8297 | 9.0593 | 1.9789 | 21.7852 | 22.0015 | 22.2002 | 22.2589 | 22.0863 | 21.4059 | 20.2236 | 22.1963 | 22.3657 | 22.4072 | 22.3481 | 21.9797 | 21.2053 | 22.2666 | 17.5283 | 17.1916 | 16.2876 | 16.2443 | 16.2848 | 17.0881 | 16.8663 | 22.3912 | 22.148 | 21.7158 | 22.0904 | 21.8013 | 21.3107 | 21.9475 | 21.531 | 20.9078 | 20.1105 | 20.3156 | 19.8485 | 19.7566 | -0.17968 | -0.15841 | 20.7497 | 22.071 | 22.3751 | 20.0907 | 21.6741 | 22.1137 | 21.9461 | 21.7147 | 21.2884 | 21.7945 | 21.4516 | 21.0424 | 20.2637 | 20.3215 | 20.239 | 20.2187 | 20.0785 |  | 20.2218 | 20.0018 | 20.1189 | 19.6687 | 20.0844 | 20.3261 |  | 20.4088 |  |  | 20.2827 | 20.3297 | 20.6119 | [5 empty] | 21.9419 | 20.3374 | 21.6718 | 22.0501 | 19.5301 | 21.1778 | 21.7986 | 19.3944 | 19.9376 | 21.1541 |  | 19.7956 | 20.9187 | 18.879 | 19.7062 | 20.8025 | 19.4561 | 20.0368 | 19.0518 | 20.0673 | 19.1243 | 20.1718 | 18.8546 | 20.1248 | 21.0668 | 19.4368 | 19.7932 | 20.9946 | 18.9656 | 19.8578 | 20.8294 | 19.0112 | 20.116 | 19.3164 | 19.9362 | 18.8985 | 20.1245 | -0.075817 | 20.9483 | 0.047393 | 0.012778 | -27.1326 | 3.097 | -7.79 | -0.14 | 0.64879 | -0.64816 | -8.4226 | 0.91852 | 0.64466 | -16.7087 | 3.7538 | 0.42399 | 0.42267 | 0.43077 | 0.35343 | 0.46542 | 0.44253 | 0.4292
42838.4174 | -251 | 22.9005 | 22.8659 | 22.8552 | 22.7742 | 22.416 | 21.7465 | 22.7159 | 21.8038 | 22.3673 | 22.3803 | 22.3599 | 22.0315 | 21.2446 | 22.2181 | 21.5859 | 21.761 | 21.8919 | 21.072 | 21.1768 | 21.394 | 20.4657 | 20.6165 | 20.9053 | 21.8857 | 21.6455 | 21.2838 | 20.2893 | 20.3926 | 20.3745 | 22.0801 | 21.6743 | 21.1997 | 21.9988 | 21.7417 | 21.3587 | 19.9257 | 20.3968 |  | 20.5166 | 20.0444 | 20.1483 | 19.0395 |  | 16.7684 | 16.7512 | 16.4609 | 16.7542 | 16.8917 | 17.4068 | 17.9023 | 16.0968 | 16.8725 | 16.1453 | 16.9016 | 17.9142 | 44.5829 | 47.9635 | 43.5224 | 21.3541 |  |  | 0.47073 | -0.3871 | -51.6981 | 0.39094 | 0.15652 | -197.8572 | 9.4798 | -0.42092 | 0.036289 | -0.27997 | -0.012902 | 8.8286 | 9.0581 | 1.9793 | 21.7757 | 22.007 | 22.1938 | 22.2535 | 22.0824 | 21.417 | 20.2188 | 22.1977 | 22.3594 | 22.3976 | 22.3482 | 21.9708 | 21.2088 | 22.2608 | 17.524 | 17.2013 | 16.2879 | 16.2514 | 16.2859 | 17.0933 | 16.8719 | 22.3951 | 22.158 | 21.7056 | 22.0874 | 21.8043 | 21.3131 | 21.952 | 21.5297 | 20.9101 | 20.107 | 20.3234 | 19.8432 | 19.763 | -0.039111 | -0.24913 | 20.7706 | 22.0807 | 22.3822 | 20.097 | 21.6758 | 22.1233 | 21.9537 | 21.7174 | 21.2867 | 21.7969 | 21.4534 | 21.0505 | 20.2743 | 20.3168 | 20.2398 | 20.2304 | 20.0754 |  | 20.225 | 20.0145 | 20.1296 | 19.6647 | 20.0936 | 20.3255 |  | 20.4137 |  |  | 20.286 | 20.343 | 20.6216 | [5 empty] | 21.9399 | 20.3348 | 21.6756 | 22.0535 | 19.5335 | 21.1834 | 21.8034 | 19.4034 | 19.9367 | 21.1603 |  | 19.8065 | 20.923 | 18.8804 | 19.7097 | 20.8087 | 19.4591 | 20.0403 | 19.0617 | 20.072 | 19.1269 | 20.1758 | 18.8497 | 20.1169 | 21.0644 | 19.4318 | 19.7878 | 20.9894 | 18.9593 | 19.858 | 20.8168 | 19.0073 | 20.1121 | 19.3128 | 19.9307 | 18.8926 | 20.1183 | -0.074518 | 20.9468 | 0.048696 | 0.013518 | -27.0077 | 3.097 | 12.77 | -0.04 | 0.81917 | -0.73826 | -8.5316 | 0.7419 | 0.46997 | -16.7093 | 3.6575 | 0.42418 | 0.42268 | 0.43119 | 0.35453 | 0.46604 | 0.44293 | 0.42891
42838.4174 | -250 | 22.8988 | 22.8643 | 22.8516 | 22.7791 | 22.4101 | 21.7495 | 22.7171 | 21.8041 | 22.3691 | 22.3783 | 22.3554 | 22.0349 | 21.2471 | 22.2189 | 21.5885 | 21.7646 | 21.8952 | 21.0764 | 21.1767 | 21.3983 | 20.4735 | 20.6165 | 20.9094 | 21.8844 | 21.6536 | 21.2823 | 20.2905 | 20.3991 | 20.3759 | 22.0714 | 21.6744 | 21.1891 | 21.9928 | 21.7329 | 21.3531 | 19.9227 | 20.3937 |  | 20.5122 | 20.0332 | 20.1445 | 19.0258 |  | 16.7698 | 16.7549 | 16.4576 | 16.7496 | 16.9097 | 17.4323 | 17.9156 | 16.1014 | 16.8667 | 16.0895 | 16.9037 | 17.9229 | 44.5922 | 47.9747 | 43.5552 | 21.3529 |  |  | 0.41356 | -0.26094 | -51.3866 | 0.57231 | 0.32212 | -197.8131 | 9.2879 | -0.35783 | -0.02968 | -0.18179 | 0.029456 | 8.8298 | 9.0595 | 1.979 | 21.7887 | 22.0109 | 22.2017 | 22.2643 | 22.0926 | 21.4127 | 20.2282 | 22.202 | 22.3734 | 22.4 | 22.3558 | 21.9814 | 21.2151 | 22.266 | 17.4916 | 17.2468 | 16.2809 | 16.2538 | 16.2783 | 17.0953 | 16.8768 | 22.3927 | 22.1553 | 21.7074 | 22.0879 | 21.8031 | 21.3047 | 21.9442 | 21.5284 | 20.9058 | 20.1105 | 20.3181 | 19.8473 | 19.7672 | 0.0068932 | -0.10952 | 20.7598 | 22.07 | 22.3744 | 20.1011 | 21.6661 | 22.1207 | 21.953 | 21.713 | 21.2794 | 21.7878 | 21.4475 | 21.0435 | 20.2625 | 20.3152 | 20.2333 | 20.2188 | 20.0712 |  | 20.2197 | 20.0167 | 20.1224 | 19.6585 | 20.09 | 20.3287 |  | 20.4126 |  |  | 20.2874 | 20.3511 | 20.6206 | [5 empty] | 21.944 | 20.339 | 21.6797 | 22.0632 | 19.5356 | 21.1827 | 21.8048 | 19.4066 | 19.947 | 21.1712 |  | 19.8103 | 20.9262 | 18.8889 | 19.7152 | 20.8152 | 19.4623 | 20.0453 | 19.0658 | 20.0817 | 19.133 | 20.1817 | 18.8517 | 20.1181 | 21.0633 | 19.4303 | 19.791 | 20.9895 | 18.9571 | 19.8543 | 20.8158 | 19.0086 | 20.1055 | 19.3174 | 19.9332 | 18.8916 | 20.1209 | -0.065985 | 20.9486 | 0.048401 | 0.014339 | -27.0418 | 3.097 | -0.17 | -0.08 | 0.76782 | -0.60613 | -8.5059 | 0.89765 | 0.67423 | -16.7082 | 3.6204 | 0.42412 | 0.42237 | 0.43124 | 0.35835 | 0.4674 | 0.44321 | 0.42891
42838.4174 | -249 | 22.903 | 22.8694 | 22.8503 | 22.78 | 22.4108 | 21.7416 | 22.7197 | 21.807 | 22.3638 | 22.3747 | 22.3555 | 22.0407 | 21.2489 | 22.2155 | 21.584 | 21.7594 | 21.8933 | 21.0768 | 21.1735 | 21.3942 | 20.4782 | 20.6187 | 20.9113 | 21.8879 | 21.6508 | 21.2824 | 20.2869 | 20.402 | 20.3811 | 22.0715 | 21.6714 | 21.1904 | 21.9977 | 21.7379 | 21.3496 | 19.9163 | 20.3985 |  | 20.511 | 20.0383 | 20.1452 | 19.0183 |  | 16.7824 | 16.7511 | 16.4556 | 16.7361 | 16.9075 | 17.4336 | 17.8986 | 16.107 | 16.863 | 16.0482 | 16.9059 | 17.9197 | 44.5825 | 47.9799 | 43.5661 | 21.3657 |  |  | 0.33142 | -0.36674 | -51.9333 | 0.58873 | 0.28532 | -197.8184 | 9.4108 | -0.34206 | 0.23517 | -0.33872 | 0.040219 | 8.8288 | 9.0584 | 1.9789 | 21.7913 | 22.0105 | 22.2039 | 22.2738 | 22.0937 | 21.4177 | 20.2289 | 22.2021 | 22.3806 | 22.4019 | 22.361 | 21.9856 | 21.2194 | 22.2694 | 17.454 | 17.2427 | 16.2772 | 16.2535 | 16.2811 | 17.0945 | 16.87 | 22.3931 | 22.1497 | 21.7079 | 22.0844 | 21.7959 | 21.3052 | 21.9447 | 21.5249 | 20.8983 | 20.1104 | 20.3243 | 19.8442 | 19.7746 | -0.078038 | -0.22345 | 20.7627 | 22.0742 | 22.372 | 20.0882 | 21.6718 | 22.1131 | 21.952 | 21.7215 | 21.2852 | 21.7849 | 21.4481 | 21.0527 | 20.2674 | 20.3227 | 20.2385 | 20.2234 | 20.0775 |  | 20.2267 | 20.0123 | 20.1158 | 19.6647 | 20.0904 | 20.329 |  | 20.4138 |  |  | 20.2842 | 20.3526 | 20.6182 | [5 empty] | 21.9488 | 20.341 | 21.6858 | 22.0626 | 19.5348 | 21.179 | 21.7996 | 19.3938 | 19.9372 | 21.162 |  | 19.7994 | 20.9151 | 18.8822 | 19.7023 | 20.8113 | 19.4515 | 20.0416 | 19.0594 | 20.0744 | 19.1224 | 20.1761 | 18.8563 | 20.1277 | 21.0673 | 19.43 | 19.7917 | 20.9932 | 18.9637 | 19.8596 | 20.8265 | 19.0252 | 20.1137 | 19.3174 | 19.9391 | 18.8937 | 20.1294 | -0.26855 | 20.9472 | 0.0492 | 0.014535 | -27.0668 | 3.0969 | 1.76 | -0.14 | 0.68736 | -0.71857 | -8.551 | 0.91044 | 0.63455 | -16.7084 | 3.6443 | 0.42418 | 0.42227 | 0.43108 | 0.36244 | 0.467 | 0.4432 | 0.4287
42838.4174 | -248 | 22.9089 | 22.8714 | 22.8517 | 22.7855 | 22.4111 | 21.7556 | 22.7301 | 21.8106 | 22.3782 | 22.3836 | 22.3686 | 22.0362 | 21.255 | 22.2174 | 21.5979 | 21.7622 | 21.8956 | 21.0773 | 21.1731 | 21.3945 | 20.4759 | 20.62 | 20.9083 | 21.8874 | 21.6523 | 21.2831 | 20.285 | 20.3956 | 20.3784 | 22.0774 | 21.6698 | 21.1945 | 22.0005 | 21.7421 | 21.3512 | 19.9157 | 20.392 |  | 20.5099 | 20.0471 | 20.1353 | 19.0219 |  | 16.7664 | 16.7438 | 16.4421 | 16.7245 | 16.8832 | 17.4183 | 17.8983 | 16.0844 | 16.8537 | 16.0275 | 16.8948 | 17.9216 | 44.5781 | 47.9863 | 43.5844 | 21.3636 |  |  | 0.4037 | -0.31482 | -51.8223 | 0.56967 | 0.20515 | -197.8466 | 8.9535 | -0.44063 | 0.031813 | 0.017315 | 0.038483 | 8.8278 | 9.0577 | 1.9785 | 21.7827 | 22 | 22.2016 | 22.2642 | 22.0956 | 21.4198 | 20.228 | 22.2 | 22.3776 | 22.4022 | 22.3547 | 21.9808 | 21.2133 | 22.2634 | 17.4243 | 17.2472 | 16.2713 | 16.2507 | 16.2855 | 17.0955 | 16.8719 | 22.3907 | 22.1524 | 21.708 | 22.0892 | 21.8031 | 21.3008 | 21.9436 | 21.5219 | 20.8972 | 20.1045 | 20.3218 | 19.844 | 19.7779 | 0.063907 | -0.093167 | 20.7608 | 22.0732 | 22.3833 | 20.1054 | 21.675 | 22.1205 | 21.9523 | 21.7113 | 21.2886 | 21.7855 | 21.4495 | 21.0494 | 20.2652 | 20.3163 | 20.2333 | 20.2251 | 20.0723 |  | 20.2307 | 20.0005 | 20.1215 | 19.6656 | 20.0914 | 20.3244 |  | 20.4137 |  |  | 20.2735 | 20.3477 | 20.607 | [5 empty] | 21.9415 | 20.3434 | 21.6819 | 22.0547 | 19.5349 | 21.179 | 21.8007 | 19.4011 | 19.9341 | 21.1653 |  | 19.8037 | 20.9231 | 18.8851 | 19.7059 | 20.8164 | 19.4544 | 20.0439 | 19.0641 | 20.0724 | 19.1233 | 20.1782 | 18.8575 | 20.1183 | 21.069 | 19.4393 | 19.7924 | 20.9972 | 18.9613 | 19.8606 | 20.8259 | 19.0269 | 20.1187 | 19.3165 | 19.9383 | 18.8923 | 20.1303 | -0.17172 | 20.9468 | 0.048929 | 0.01383 | -27.0393 | 3.097 | 23.12 | -0.08 | 0.75861 | -0.66577 | -8.5417 | 0.89557 | 0.53806 | -16.7092 | 3.5546 | 0.42446 | 0.42279 | 0.43109 | 0.36586 | 0.46788 | 0.44309 | 0.42841
42838.4174 | -247 | 22.9179 | 22.8707 | 22.8589 | 22.7818 | 22.4171 | 21.7504 | 22.7245 | 21.8168 | 22.3846 | 22.3828 | 22.3691 | 22.0382 | 21.2522 | 22.2215 | 21.5996 | 21.7617 | 21.8991 | 21.0906 | 21.1876 | 21.3962 | 20.4806 | 20.6252 | 20.914 | 21.89 | 21.651 | 21.2851 | 20.2973 | 20.404 | 20.383 | 22.0763 | 21.6732 | 21.1935 | 22.0034 | 21.7408 | 21.3518 | 19.9157 | 20.4066 |  | 20.5154 | 20.04 | 20.1478 | 19.0294 |  | 16.7764 | 16.7506 | 16.4467 | 16.7328 | 16.889 | 17.4191 | 17.8997 | 16.0855 | 16.8698 | 16.022 | 16.9019 | 17.9181 | 44.5823 | 47.9791 | 43.5862 | 21.3554 |  |  | 0.48518 | -0.27408 | -51.7835 | 0.60779 | 0.078984 | -197.8236 | 9.6999 | -0.3506 | 0.20617 | -0.012477 | -0.042588 | 8.8279 | 9.0578 | 1.9785 | 21.7813 | 22.0077 | 22.2038 | 22.265 | 22.095 | 21.4186 | 20.2292 | 22.2032 | 22.3701 | 22.4033 | 22.3571 | 21.9797 | 21.2151 | 22.2669 | 17.3967 | 17.256 | 16.2713 | 16.2548 | 16.288 | 17.0974 | 16.8613 | 22.3899 | 22.1516 | 21.7086 | 22.0845 | 21.8068 | 21.3031 | 21.9407 | 21.5173 | 20.9038 | 20.1039 | 20.321 | 19.8403 | 19.7849 | -0.021024 | -0.15707 | 20.7637 | 22.0646 | 22.379 | 20.0975 | 21.6693 | 22.1191 | 21.9451 | 21.723 | 21.2844 | 21.7848 | 21.4446 | 21.0463 | 20.2705 | 20.3262 | 20.2347 | 20.218 | 20.0719 |  | 20.2298 | 19.9925 | 20.1241 | 19.6691 | 20.0884 | 20.3208 |  | 20.4146 |  |  | 20.2776 | 20.3591 | 20.6068 | [5 empty] | 21.9456 | 20.3494 | 21.6837 | 22.062 | 19.5432 | 21.1856 | 21.8073 | 19.3967 | 19.9311 | 21.1573 |  | 19.8065 | 20.9211 | 18.8891 | 19.7059 | 20.8117 | 19.4534 | 20.0436 | 19.0625 | 20.0751 | 19.1215 | 20.1733 | 18.8523 | 20.1185 | 21.0635 | 19.4325 | 19.7868 | 20.9956 | 18.9546 | 19.8501 | 20.8267 | 19.0165 | 20.108 | 19.3106 | 19.9301 | 18.8877 | 20.1193 | -0.13759 | 20.9465 | 0.047664 | 0.011152 | -26.9346 | 3.0969 | 10.82 | -0.12 | 0.83166 | -0.6212 | -8.5386 | 0.92506 | 0.33386 | -16.7082 | 3.6998 | 0.42444 | 0.4231 | 0.43089 | 0.36915 | 0.46665 | 0.44287 | 0.42819
42838.4174 | -246 | 22.9024 | 22.8666 | 22.8498 | 22.7775 | 22.4081 | 21.7466 | 22.7139 | 21.8035 | 22.3636 | 22.3771 | 22.3565 | 22.0325 | 21.2375 | 22.2123 | 21.5978 | 21.7567 | 21.8961 | 21.0822 | 21.1737 | 21.3959 | 20.4734 | 20.6213 | 20.9111 | 21.8824 | 21.6538 | 21.28 | 20.2959 | 20.3912 | 20.3777 | 22.0777 | 21.6737 | 21.1882 | 21.9984 | 21.7372 | 21.3495 | 19.9147 | 20.3963 |  | 20.5103 | 20.0392 | 20.1408 | 19.0304 |  | 16.777 | 16.7454 | 16.4426 | 16.7356 | 16.8959 | 17.4299 | 17.8734 | 16.0677 | 16.8681 | 16.0047 | 16.8961 | 17.9172 | 44.6059 | 47.9819 | 43.6164 | 21.3661 |  |  | 0.4221 | -0.41076 | -51.6816 | 0.10049 | 0.081612 | -197.8026 | 9.5922 | -0.4426 | 0.06723 | 0.062841 | 0.091778 | 8.8282 | 9.0581 | 1.9794 | 21.792 | 22.0158 | 22.2054 | 22.2694 | 22.0983 | 21.4145 | 20.2284 | 22.2011 | 22.3743 | 22.4101 | 22.3574 | 21.9874 | 21.2252 | 22.2706 | 17.3755 | 17.2553 | 16.2916 | 16.2688 | 16.2876 | 17.0899 | 16.8665 | 22.3892 | 22.1535 | 21.7034 | 22.0897 | 21.8024 | 21.3031 | 21.9456 | 21.5219 | 20.908 | 20.1039 | 20.3241 | 19.8489 | 19.7919 | 0.025767 | -0.13577 | 20.7701 | 22.0772 | 22.3869 | 20.1002 | 21.6689 | 22.1151 | 21.9503 | 21.7215 | 21.2808 | 21.7926 | 21.4464 | 21.0405 | 20.2601 | 20.3229 | 20.2418 | 20.2216 | 20.0518 |  | 20.2218 | 19.9807 | 20.1096 | 19.6761 | 20.0862 | 20.3142 |  | 20.4102 |  |  | 20.2804 | 20.373 | 20.6241 | [5 empty] | 21.9516 | 20.3617 | 21.6876 | 22.0719 | 19.5433 | 21.1834 | 21.8015 | 19.3966 | 19.9364 | 21.1703 |  | 19.8058 | 20.9269 | 18.8906 | 19.7122 | 20.817 | 19.4579 | 20.0457 | 19.0608 | 20.0834 | 19.1252 | 20.1853 | 18.8611 | 20.12 | 21.071 | 19.4319 | 19.7993 | 20.9975 | 18.9584 | 19.8567 | 20.8169 | 19.0186 | 20.113 | 19.3215 | 19.9402 | 18.8964 | 20.1171 | -0.18155 | 20.948 | 0.047424 | 0.011958 | -27.0399 | 3.097 | 19.35 | -0.13 | 0.77571 | -0.76047 | -8.5301 | 0.37615 | 0.33937 | -16.7077 | 3.6792 | 0.42473 | 0.42295 | 0.43062 | 0.37062 | 0.465 | 0.44281 | 0.428
42838.4174 | -245 | 22.902 | 22.8672 | 22.8531 | 22.7775 | 22.4099 | 21.7492 | 22.7152 | 21.8091 | 22.3606 | 22.3825 | 22.3627 | 22.0249 | 21.2474 | 22.2196 | 21.5959 | 21.763 | 21.8901 | 21.0768 | 21.1741 | 21.3937 | 20.475 | 20.6094 | 20.9072 | 21.8792 | 21.6549 | 21.2761 | 20.2827 | 20.4014 | 20.3749 | 22.0692 | 21.6677 | 21.1816 | 21.9953 | 21.7293 | 21.3501 | 19.9078 | 20.3947 |  | 20.5053 | 20.0378 | 20.1372 | 19.0423 |  | 16.7811 | 16.7583 | 16.4667 | 16.7716 | 16.8922 | 17.4332 | 17.8555 | 16.0752 | 16.8749 | 16.0201 | 16.9073 | 17.9156 | 44.6049 | 47.9638 | 43.6311 | 21.3537 |  |  | 0.36624 | -0.37002 | -51.4464 | 0.41263 | 0.26298 | -197.8604 | 9.8071 | -0.31578 | 0.044073 | -0.0076514 | 0.13744 | 8.8297 | 9.0594 | 1.9794 | 21.7933 | 22.0079 | 22.2094 | 22.2665 | 22.0899 | 21.4131 | 20.225 | 22.1994 | 22.3716 | 22.4028 | 22.3576 | 21.9803 | 21.2183 | 22.269 | 17.3623 | 17.2422 | 16.323 | 16.3146 | 16.3374 | 17.0921 | 16.8604 | 22.3931 | 22.1521 | 21.7127 | 22.083 | 21.806 | 21.3086 | 21.9482 | 21.5286 | 20.9081 | 20.1075 | 20.3245 | 19.8549 | 19.7941 | 0.031468 | -0.15841 | 20.7633 | 22.0769 | 22.3823 | 20.1041 | 21.6752 | 22.1247 | 21.9572 | 21.713 | 21.2885 | 21.7882 | 21.4559 | 21.0524 | 20.274 | 20.3276 | 20.2391 | 20.2246 | 20.0485 |  | 20.2213 | 19.9816 | 20.112 | 19.6853 | 20.0914 | 20.3207 |  | 20.4173 |  |  | 20.2576 | 20.3627 | 20.6214 | [5 empty] | 21.9421 | 20.3427 | 21.6796 | 22.0548 | 19.5263 | 21.1773 | 21.7942 | 19.402 | 19.9462 | 21.1704 |  | 19.8039 | 20.9295 | 18.8867 | 19.7163 | 20.8155 | 19.4606 | 20.0453 | 19.0708 | 20.0786 | 19.1268 | 20.1788 | 18.8669 | 20.1213 | 21.0779 | 19.4417 | 19.8039 | 21.0046 | 18.9654 | 19.8564 | 20.8293 | 19.023 | 20.1199 | 19.3197 | 19.93 | 18.9044 | 20.121 | -0.19509 | 20.9476 | 0.04826 | 0.013823 | -26.8922 | 3.0969 | 0.38 | -0.06 | 0.72256 | -0.72179 | -8.5109 | 0.76221 | 0.6092 | -16.7102 | 3.7202 | 0.4248 | 0.423 | 0.43054 | 0.37235 | 0.46079 | 0.44226 | 0.42806
42838.4175 | -244 | 22.9057 | 22.8723 | 22.854 | 22.7814 | 22.4165 | 21.7632 | 22.7245 | 21.8172 | 22.3724 | 22.3863 | 22.3646 | 22.0383 | 21.2552 | 22.2185 | 21.5958 | 21.7728 | 21.8983 | 21.0769 | 21.1745 | 21.3939 | 20.4872 | 20.6163 | 20.9142 | 21.8899 | 21.644 | 21.2819 | 20.2855 | 20.4008 | 20.3717 | 22.0718 | 21.6732 | 21.1916 | 21.9949 | 21.7424 | 21.3527 | 19.9128 | 20.4027 |  | 20.5134 | 20.0388 | 20.1371 | 19.0438 |  | 16.7891 | 16.7456 | 16.4797 | 16.7739 | 16.888 | 17.4324 | 17.8368 | 16.0679 | 16.8721 | 16.0387 | 16.9038 | 17.9229 | 44.6055 | 47.9669 | 43.6563 | 21.3552 |  |  | 0.29265 | -0.26357 | -51.0245 | 0.295 | 0.12958 | -197.8427 | 10.0351 | -0.45771 | -0.050113 | 0.013119 | 0.029977 | 8.8289 | 9.0589 | 1.9787 | 21.7875 | 22.0088 | 22.1959 | 22.2754 | 22.0882 | 21.4111 | 20.2287 | 22.1952 | 22.3717 | 22.4022 | 22.3483 | 21.9785 | 21.216 | 22.265 | 17.3696 | 17.2122 | 16.3159 | 16.3522 | 16.3861 | 17.0999 | 16.8636 | 22.3924 | 22.1556 | 21.7154 | 22.088 | 21.8105 | 21.3073 | 21.9453 | 21.5236 | 20.91 | 20.1056 | 20.3252 | 19.8552 | 19.7893 | -0.038521 | -0.049992 | 20.758 | 22.0725 | 22.3777 | 20.1064 | 21.6714 | 22.1151 | 21.9467 | 21.7137 | 21.2816 | 21.7821 | 21.4525 | 21.0434 | 20.2665 | 20.3133 | 20.2321 | 20.2213 | 20.0584 |  | 20.2348 | 19.9751 | 20.1261 | 19.6878 | 20.095 | 20.3273 |  | 20.4221 |  |  | 20.2765 | 20.3684 | 20.6142 | [5 empty] | 21.9434 | 20.3423 | 21.6729 | 22.0539 | 19.5333 | 21.1835 | 21.8044 | 19.3942 | 19.937 | 21.1663 |  | 19.8044 | 20.9265 | 18.8787 | 19.718 | 20.8123 | 19.4526 | 20.0498 | 19.0765 | 20.084 | 19.1174 | 20.1792 | 18.8578 | 20.127 | 21.0745 | 19.427 | 19.7987 | 20.9965 | 18.9731 | 19.8588 | 20.835 | 19.0277 | 20.1157 | 19.318 | 19.9425 | 18.896 | 20.1106 | -0.27894 | 20.9469 | 0.048579 | 0.014302 | -27.0142 | 3.0969 | -11.23 | -0.06 | 0.64589 | -0.60917 | -8.4757 | 0.64447 | 0.42764 | -16.7094 | 3.7632 | 0.42498 | 0.42365 | 0.43059 | 0.37245 | 0.46197 | 0.44238 | 0.42813
42838.4175 | -243 | 22.9105 | 22.8761 | 22.8611 | 22.7836 | 22.4206 | 21.7619 | 22.7282 | 21.8192 | 22.3743 | 22.3817 | 22.3632 | 22.0393 | 21.2582 | 22.2224 | 21.5987 | 21.7707 | 21.8879 | 21.0812 | 21.1822 | 21.3942 | 20.478 | 20.6136 | 20.905 | 21.8844 | 21.6506 | 21.2774 | 20.2867 | 20.3977 | 20.3752 | 22.0732 | 21.6676 | 21.1902 | 21.9944 | 21.7356 | 21.3504 | 19.913 | 20.3989 |  | 20.5073 | 20.0339 | 20.1307 | 19.0417 |  | 16.7832 | 16.7488 | 16.49 | 16.7877 | 16.889 | 17.4417 | 17.8579 | 16.083 | 16.8758 | 16.0776 | 16.9078 | 17.9194 | 44.607 | 47.9425 | 43.6655 | 21.3658 |  |  | 0.35967 | -0.37922 | -51.6777 | 0.51842 | 0.23275 | -197.8499 | 9.809 | -0.34666 | -0.16298 | -0.000728 | 0.019734 | 8.8279 | 9.0574 | 1.9786 | 21.7784 | 22.0094 | 22.1942 | 22.2599 | 22.0859 | 21.4176 | 20.2267 | 22.1978 | 22.366 | 22.3988 | 22.3539 | 21.9753 | 21.2046 | 22.2632 | 17.3789 | 17.2169 | 16.3051 | 16.3422 | 16.3769 | 17.0929 | 16.8608 | 22.3942 | 22.1587 | 21.7195 | 22.092 | 21.8017 | 21.3055 | 21.9485 | 21.5349 | 20.9151 | 20.1056 | 20.3321 | 19.8558 | 19.7975 | 0.12859 | -0.13197 | 20.7637 | 22.0743 | 22.3851 | 20.1058 | 21.6721 | 22.1155 | 21.9588 | 21.7187 | 21.2815 | 21.7842 | 21.4422 | 21.0469 | 20.2813 | 20.3184 | 20.2412 | 20.2218 | 20.0588 |  | 20.2263 | 19.9634 | 20.1248 | 19.6868 | 20.0889 | 20.3215 |  | 20.4175 |  |  | 20.275 | 20.3573 | 20.6179 | [5 empty] | 21.9341 | 20.35 | 21.6815 | 22.0545 | 19.5453 | 21.1756 | 21.7984 | 19.4068 | 19.9417 | 21.17 |  | 19.8137 | 20.9384 | 18.8851 | 19.719 | 20.8294 | 19.4564 | 20.057 | 19.0817 | 20.0856 | 19.1282 | 20.1809 | 18.8562 | 20.121 | 21.0708 | 19.4236 | 19.7918 | 20.9941 | 18.9565 | 19.8619 | 20.8207 | 19.0119 | 20.105 | 19.3169 | 19.9237 | 18.8849 | 20.1069 | -0.094181 | 20.9474 | 0.048868 | 0.014419 | -27.0722 | 3.0969 | 1.82 | -0.08 | 0.71605 | -0.7307 | -8.5299 | 0.85434 | 0.57313 | -16.71 | 3.7207 | 0.42469 | 0.42394 | 0.43042 | 0.37059 | 0.46284 | 0.44245 | 0.4279
42838.4175 | -242 | 22.9122 | 22.8682 | 22.8592 | 22.781 | 22.415 | 21.7586 | 22.725 | 21.8124 | 22.3742 | 22.3821 | 22.363 | 22.0379 | 21.2548 | 22.2195 | 21.6055 | 21.7694 | 21.8912 | 21.0842 | 21.1813 | 21.3998 | 20.4892 | 20.6229 | 20.9136 | 21.8852 | 21.6449 | 21.2866 | 20.2945 | 20.4001 | 20.3772 | 22.0725 | 21.6716 | 21.1873 | 21.9996 | 21.7343 | 21.354 | 19.9122 | 20.4088 |  | 20.5157 | 20.0388 | 20.1358 | 19.0513 |  | 16.7866 | 16.7561 | 16.4955 | 16.7983 | 16.9194 | 17.4613 | 17.8796 | 16.0891 | 16.8759 | 16.1032 | 16.9036 | 17.9221 | 44.608 | 47.9372 | 43.6766 | 21.3644 |  |  | 0.41421 | -0.36411 | -52.4524 | 0.50331 | 0.21764 | -197.8611 | 9.1151 | -0.47151 | -0.040578 | -0.078144 | 0.11348 | 8.8293 | 9.0591 | 1.9787 | 21.7823 | 22.0035 | 22.201 | 22.2557 | 22.0865 | 21.4174 | 20.2227 | 22.1967 | 22.3656 | 22.3975 | 22.3486 | 21.9814 | 21.2153 | 22.2596 | 17.3845 | 17.2343 | 16.3344 | 16.3466 | 16.3638 | 17.1029 | 16.8688 | 22.3902 | 22.1562 | 21.7135 | 22.0876 | 21.8014 | 21.3052 | 21.9412 | 21.5306 | 20.9022 | 20.1022 | 20.3274 | 19.8593 | 19.7837 | 0.047786 | -0.079282 | 20.7771 | 22.0871 | 22.3901 | 20.1126 | 21.6796 | 22.1328 | 21.9594 | 21.725 | 21.2881 | 21.7938 | 21.4576 | 21.0541 | 20.2861 | 20.3414 | 20.2397 | 20.2382 | 20.0665 |  | 20.2324 | 19.9683 | 20.1289 | 19.7004 | 20.1014 | 20.3295 |  | 20.4213 |  |  | 20.2834 | 20.3622 | 20.6184 | [5 empty] | 21.9357 | 20.3432 | 21.6782 | 22.051 | 19.5414 | 21.1699 | 21.7906 | 19.3984 | 19.9403 | 21.1749 |  | 19.8023 | 20.9333 | 18.8674 | 19.7085 | 20.8309 | 19.4494 | 20.0465 | 19.0704 | 20.0871 | 19.1201 | 20.1754 | 18.8618 | 20.1253 | 21.0702 | 19.4263 | 19.789 | 21.0014 | 18.9708 | 19.8636 | 20.8284 | 19.0172 | 20.113 | 19.3144 | 19.9391 | 18.8982 | 20.1041 | -0.059864 | 20.9473 | 0.047811 | 0.012241 | -26.9469 | 3.0969 | 17.47 | -0.05 | 0.76843 | -0.716 | -8.5937 | 0.84181 | 0.55423 | -16.711 | 3.5868 | 0.42468 | 0.42394 | 0.43046 | 0.37114 | 0.46051 | 0.44215 | 0.42817
42838.4175 | -241 | 22.9009 | 22.8688 | 22.8526 | 22.7856 | 22.4109 | 21.7581 | 22.718 | 21.8096 | 22.3767 | 22.3845 | 22.3617 | 22.0332 | 21.2483 | 22.2176 | 21.6002 | 21.7669 | 21.893 | 21.0778 | 21.1783 | 21.3943 | 20.4793 | 20.6245 | 20.9125 | 21.8871 | 21.648 | 21.2853 | 20.2945 | 20.3992 | 20.3775 | 22.0729 | 21.6706 | 21.1888 | 21.9982 | 21.7457 | 21.3536 | 19.9172 | 20.4133 |  | 20.51 | 20.0368 | 20.1344 | 19.0571 |  | 16.7954 | 16.775 | 16.5019 | 16.8069 | 16.928 | 17.4736 | 17.8777 | 16.0956 | 16.8827 | 16.0933 | 16.9164 | 17.9194 | 44.5978 | 47.9106 | 43.6731 | 21.3547 |  |  | 0.38333 | -0.20903 | -53.1345 | 0.33311 | 0.26166 | -197.823 | 9.401 | -0.40449 | -0.33734 | -0.16102 | 0.13119 | 8.8285 | 9.0582 | 1.9796 | 21.788 | 22.0116 | 22.2037 | 22.2622 | 22.0929 | 21.4173 | 20.2259 | 22.2001 | 22.368 | 22.4048 | 22.3548 | 21.9896 | 21.2213 | 22.262 | 17.3828 | 17.2506 | 16.3385 | 16.3526 | 16.3539 | 17.1006 | 16.8663 | 22.3999 | 22.1523 | 21.7176 | 22.089 | 21.8013 | 21.3118 | 21.9457 | 21.5343 | 20.9076 | 20.1043 | 20.3256 | 19.8609 | 19.7905 | 0.048966 | -0.031732 | 20.7647 | 22.0755 | 22.3778 | 20.0982 | 21.6753 | 22.1186 | 21.9428 | 21.7193 | 21.293 | 21.7859 | 21.4495 | 21.0553 | 20.2724 | 20.3222 | 20.2267 | 20.2272 | 20.0585 |  | 20.2268 | 19.9549 | 20.1242 | 19.6846 | 20.0903 | 20.3176 |  | 20.4132 |  |  | 20.2824 | 20.3677 | 20.6194 | [5 empty] | 21.9375 | 20.3532 | 21.6807 | 22.0564 | 19.5395 | 21.175 | 21.8036 | 19.4031 | 19.9451 | 21.1719 |  | 19.8078 | 20.933 | 18.8869 | 19.7163 | 20.8268 | 19.4542 | 20.0527 | 19.0665 | 20.0899 | 19.1253 | 20.187 | 18.863 | 20.1296 | 21.076 | 19.4292 | 19.7996 | 21.0009 | 18.9721 | 19.8665 | 20.8291 | 19.0096 | 20.1148 | 19.327 | 19.9327 | 18.8912 | 20.1139 | -0.26966 | 20.948 | 0.047406 | 0.011791 | -27.0564 | 3.0969 | 11.77 | -0.14 | 0.73923 | -0.54252 | -8.6496 | 0.68487 | 0.60772 | -16.7098 | 3.6427 | 0.42471 | 0.42415 | 0.43052 | 0.37106 | 0.45976 | 0.44216 | 0.42805
42838.4175 | -240 | 22.9168 | 22.8736 | 22.8662 | 22.788 | 22.4139 | 21.7499 | 22.7217 | 21.8149 | 22.3752 | 22.3961 | 22.363 | 22.032 | 21.2526 | 22.2192 | 21.5941 | 21.7652 | 21.8943 | 21.081 | 21.1763 | 21.3936 | 20.4702 | 20.613 | 20.907 | 21.8904 | 21.6444 | 21.2811 | 20.2883 | 20.3916 | 20.3751 | 22.0741 | 21.6731 | 21.1976 | 22.0012 | 21.7434 | 21.3603 | 19.9233 | 20.4172 |  | 20.5053 | 20.0479 | 20.1331 | 19.0726 |  | 16.7915 | 16.7685 | 16.4976 | 16.8085 | 16.9158 | 17.4526 | 17.8825 | 16.0819 | 16.8731 | 16.0655 | 16.9123 | 17.9167 | 44.604 | 47.8896 | 43.6553 | 21.3561 |  |  | 0.50029 | -0.39105 | -54.09 | 0.7103 | 0.24918 | -197.7895 | 8.7616 | -0.33418 | -0.44827 | 0.040812 | -0.022624 | 8.8292 | 9.0591 | 1.9789 | 21.785 | 22.0066 | 22.1993 | 22.2673 | 22.0844 | 21.4126 | 20.2235 | 22.1956 | 22.3637 | 22.4043 | 22.3511 | 21.9785 | 21.2121 | 22.2586 | 17.3698 | 17.2691 | 16.3477 | 16.3526 | 16.3523 | 17.1068 | 16.8672 | 22.3955 | 22.1564 | 21.7146 | 22.0864 | 21.7994 | 21.3111 | 21.9463 | 21.5331 | 20.9166 | 20.1077 | 20.325 | 19.8589 | 19.776 | 0.074917 | -0.098873 | 20.766 | 22.0819 | 22.383 | 20.1076 | 21.67 | 22.1109 | 21.9441 | 21.7123 | 21.2826 | 21.7924 | 21.4501 | 21.0494 | 20.2731 | 20.3203 | 20.244 | 20.227 | 20.0624 |  | 20.2234 | 19.952 | 20.1218 | 19.6783 | 20.0918 | 20.3193 |  | 20.414 |  |  | 20.2834 | 20.3692 | 20.6213 | [5 empty] | 21.9393 | 20.3564 | 21.6803 | 22.0592 | 19.5362 | 21.1702 | 21.8007 | 19.3966 | 19.9386 | 21.17 |  | 19.7999 | 20.9321 | 18.878 | 19.7141 | 20.8185 | 19.4568 | 20.0429 | 19.0657 | 20.0766 | 19.1188 | 20.1755 | 18.8673 | 20.1324 | 21.0775 | 19.4275 | 19.7995 | 20.9987 | 18.9673 | 19.8624 | 20.824 | 19.0108 | 20.115 | 19.3193 | 19.9397 | 18.8912 | 20.1091 | -0.070251 | 20.9473 | 0.048088 | 0.01354 | -27.0489 | 3.0969 | 4.46 | -0.12 | 0.84451 | -0.74203 | -8.727 | 1.0001 | 0.59303 | -16.7078 | 3.5165 | 0.42449 | 0.42415 | 0.43075 | 0.37323 | 0.45885 | 0.44193 | 0.42857
42838.4175 | -239 | 22.9073 | 22.8687 | 22.8563 | 22.7818 | 22.4113 | 21.7495 | 22.715 | 21.8146 | 22.3677 | 22.3737 | 22.3616 | 22.0284 | 21.2492 | 22.2168 | 21.5861 | 21.7628 | 21.8914 | 21.0758 | 21.1705 | 21.389 | 20.4671 | 20.6044 | 20.9 | 21.8778 | 21.6411 | 21.2751 | 20.2843 | 20.3874 | 20.3695 | 22.0758 | 21.6702 | 21.1856 | 21.9987 | 21.7369 | 21.3516 | 19.9213 | 20.4162 |  | 20.5137 | 20.0389 | 20.1299 | 19.0821 |  | 16.7846 | 16.7657 | 16.5011 | 16.8057 | 16.9125 | 17.4454 | 17.8944 | 16.0772 | 16.8721 | 16.0457 | 16.9117 | 17.9231 | 44.6254 | 47.8643 | 43.6549 | 21.3622 |  |  | 0.21971 | -0.43902 | -54.3627 | 0.7287 | 0.20121 | -197.8683 | 9.056 | -0.37689 | -0.27702 | -0.074578 | 0.052198 | 8.8296 | 9.0593 | 1.9786 | 21.7785 | 22.0065 | 22.1982 | 22.2659 | 22.0854 | 21.4093 | 20.2255 | 22.1913 | 22.3678 | 22.4012 | 22.3567 | 21.9767 | 21.2091 | 22.2568 | 17.3761 | 17.2624 | 16.3446 | 16.3578 | 16.3707 | 17.1031 | 16.87 | 22.3931 | 22.1475 | 21.7118 | 22.0794 | 21.8002 | 21.3107 | 21.9436 | 21.5252 | 20.908 | 20.0957 | 20.3182 | 19.854 | 19.7677 | 0.077473 | -0.034966 | 20.756 | 22.0676 | 22.3724 | 20.1006 | 21.6663 | 22.1092 | 21.9385 | 21.7002 | 21.274 | 21.7871 | 21.4344 | 21.0434 | 20.2748 | 20.3209 | 20.2343 | 20.2276 | 20.0723 |  | 20.2201 | 19.9527 | 20.1239 | 19.6711 | 20.0919 | 20.3228 |  | 20.4139 |  |  | 20.2867 | 20.3707 | 20.62 | [5 empty] | 21.9377 | 20.3493 | 21.6798 | 22.0583 | 19.5436 | 21.1713 | 21.7923 | 19.3858 | 19.9291 | 21.1559 |  | 19.7936 | 20.9209 | 18.87 | 19.7039 | 20.8097 | 19.4494 | 20.04 | 19.0515 | 20.0701 | 19.1172 | 20.1773 | 18.8571 | 20.1215 | 21.0784 | 19.424 | 19.7991 | 20.9948 | 18.9585 | 19.8566 | 20.8232 | 19.0063 | 20.1047 | 19.311 | 19.9351 | 18.886 | 20.112 | -0.17116 | 20.9475 | 0.048358 | 0.014484 | -27.0723 | 3.0969 | -9.27 | -0.06 | 0.55964 | -0.78622 | -8.7489 | 1.0129 | 0.53289 | -16.7109 | 3.575 | 0.4241 | 0.4242 | 0.43095 | 0.37209 | 0.45951 | 0.4416 | 0.4284
42838.4175 | -238 | 22.9075 | 22.8689 | 22.8547 | 22.7776 | 22.4141 | 21.75 | 22.7186 | 21.8065 | 22.3723 | 22.3809 | 22.3571 | 22.0336 | 21.2526 | 22.2128 | 21.5887 | 21.7605 | 21.8913 | 21.0784 | 21.1679 | 21.3951 | 20.4673 | 20.6105 | 20.9002 | 21.8745 | 21.6406 | 21.271 | 20.2924 | 20.3885 | 20.3689 | 22.0821 | 21.6736 | 21.199 | 22.0059 | 21.7437 | 21.3594 | 19.9215 | 20.4211 |  | 20.5184 | 20.0369 | 20.1405 | 19.0935 |  | 16.7932 | 16.7624 | 16.5027 | 16.8061 | 16.9032 | 17.4577 | 17.901 | 16.0797 | 16.8768 | 16.0604 | 16.9103 | 17.9253 | 44.6239 | 47.8392 | 43.6618 | 21.3642 |  |  | 0.4405 | -0.082205 | -54.9574 | 0.58807 | 0.22158 | -197.8144 | 8.5868 | -0.392 | -0.079693 | 0.035987 | 0.08605 | 8.8303 | 9.0598 | 1.9788 | 21.7816 | 22.0058 | 22.1936 | 22.2624 | 22.0832 | 21.4156 | 20.22 | 22.1901 | 22.3709 | 22.3999 | 22.3582 | 21.9761 | 21.2136 | 22.2626 | 17.3729 | 17.2615 | 16.3401 | 16.3506 | 16.3724 | 17.1049 | 16.8571 | 22.3956 | 22.1529 | 21.719 | 22.094 | 21.8031 | 21.3136 | 21.9403 | 21.5306 | 20.9067 | 20.1038 | 20.3185 | 19.856 | 19.7625 | 0.13783 | -0.10382 | 20.7578 | 22.072 | 22.3812 | 20.1045 | 21.6705 | 22.1159 | 21.9523 | 21.7136 | 21.2874 | 21.7826 | 21.4499 | 21.0415 | 20.2773 | 20.3252 | 20.2393 | 20.2325 | 20.0862 |  | 20.2251 | 19.9563 | 20.1261 | 19.6677 | 20.0926 | 20.3238 |  | 20.4133 |  |  | 20.2859 | 20.3741 | 20.6266 | [5 empty] | 21.9353 | 20.3486 | 21.6824 | 22.0557 | 19.5412 | 21.1724 | 21.7962 | 19.3922 | 19.9368 | 21.1689 |  | 19.7959 | 20.9231 | 18.8744 | 19.7015 | 20.8167 | 19.4512 | 20.0494 | 19.055 | 20.0703 | 19.1245 | 20.179 | 18.8498 | 20.123 | 21.0716 | 19.4219 | 19.789 | 20.9875 | 18.9572 | 19.8497 | 20.822 | 19.0025 | 20.1002 | 19.3111 | 19.9194 | 18.8823 | 20.1031 | -0.20975 | 20.9479 | 0.048432 | 0.014317 | -27.0406 | 3.0969 | -12.56 | -0.05 | 0.79242 | -0.34021 | -8.7966 | 0.90995 | 0.55922 | -16.709 | 3.4813 | 0.42388 | 0.42417 | 0.43107 | 0.37266 | 0.45851 | 0.44129 | 0.42881
42838.4175 | -237 | 22.8998 | 22.8644 | 22.8497 | 22.7762 | 22.4132 | 21.7537 | 22.7236 | 21.809 | 22.3759 | 22.3726 | 22.3566 | 22.0292 | 21.2458 | 22.2074 | 21.5947 | 21.7627 | 21.893 | 21.079 | 21.1668 | 21.3959 | 20.4727 | 20.6149 | 20.9006 | 21.8839 | 21.643 | 21.272 | 20.2942 | 20.3937 | 20.3703 | 22.0687 | 21.6647 | 21.1908 | 21.9894 | 21.732 | 21.3528 | 19.9135 | 20.4118 |  | 20.5033 | 20.0359 | 20.1331 | 19.0824 |  | 16.7939 | 16.7575 | 16.4992 | 16.8016 | 16.8986 | 17.4403 | 17.92 | 16.1069 | 16.8755 | 16.0778 | 16.919 | 17.9203 | 44.641 | 47.8007 | 43.6703 | 21.3607 |  |  | 0.38596 | -0.084177 | -55.832 | 0.70241 | 0.24064 | -197.8552 | 8.4297 | -0.37098 | -0.017421 | 0.16732 | 0.19229 | 8.8285 | 9.0585 | 1.9781 | 21.789 | 22.0124 | 22.2003 | 22.2676 | 22.0866 | 21.4083 | 20.2269 | 22.1968 | 22.3725 | 22.4048 | 22.3503 | 21.9836 | 21.2139 | 22.2729 | 17.381 | 17.2705 | 16.3329 | 16.3462 | 16.3554 | 17.1054 | 16.8618 | 22.4014 | 22.1555 | 21.7126 | 22.0862 | 21.7993 | 21.3081 | 21.9456 | 21.5208 | 20.8993 | 20.0993 | 20.3191 | 19.8611 | 19.7656 | 0.052308 | 0.029702 | 20.7679 | 22.0806 | 22.3737 | 20.1022 | 21.6653 | 22.1289 | 21.942 | 21.7161 | 21.2703 | 21.7878 | 21.4469 | 21.0483 | 20.2817 | 20.3208 | 20.2301 | 20.2258 | 20.0711 |  | 20.2213 | 19.9558 | 20.1219 | 19.6698 | 20.0869 | 20.3161 |  | 20.4124 |  |  | 20.2866 | 20.3734 | 20.6353 | [5 empty] | 21.9415 | 20.3537 | 21.6801 | 22.0568 | 19.549 | 21.1762 | 21.8023 | 19.3983 | 19.9443 | 21.1745 |  | 19.7962 | 20.9268 | 18.878 | 19.7122 | 20.8211 | 19.4526 | 20.0498 | 19.0633 | 20.0806 | 19.1325 | 20.1804 | 18.8495 | 20.1128 | 21.0661 | 19.4163 | 19.7856 | 20.9892 | 18.9495 | 19.8506 | 20.8183 | 19.0006 | 20.0962 | 19.3165 | 19.9212 | 18.8837 | 20.0953 | -0.16319 | 20.9512 | 0.047719 | 0.01325 | -27.0411 | 3.0969 | 0.82 | -0.06 | 0.74175 | -0.34427 | -8.8662 | 0.99447 | 0.58276 | -16.7102 | 3.4492 | 0.42418 | 0.42405 | 0.43082 | 0.37182 | 0.45986 | 0.44133 | 0.42858
42838.4175 | -236 | 22.8984 | 22.8677 | 22.8512 | 22.7842 | 22.4163 | 21.7474 | 22.727 | 21.8142 | 22.3761 | 22.3741 | 22.3604 | 22.0309 | 21.2445 | 22.2159 | 21.5975 | 21.765 | 21.8959 | 21.0772 | 21.1714 | 21.3939 | 20.479 | 20.6136 | 20.9074 | 21.8875 | 21.6465 | 21.2783 | 20.2867 | 20.4003 | 20.3708 | 22.0716 | 21.6625 | 21.1859 | 21.9933 | 21.7333 | 21.354 | 19.9177 | 20.4197 |  | 20.503 | 20.0374 | 20.134 | 19.0832 |  | 16.7869 | 16.7478 | 16.4981 | 16.7934 | 16.8912 | 17.4359 | 17.9118 | 16.0993 | 16.8782 | 16.1449 | 16.9183 | 17.9229 | 44.6453 | 47.7655 | 43.6682 | 21.3638 |  |  | 0.47204 | -0.20246 | -56.5338 | 0.65247 | 0.22026 | -197.8085 | 7.8206 | -0.29804 | -0.04953 | 0.059485 | 0.036226 | 8.8291 | 9.0589 | 1.9792 | 21.7931 | 22.0009 | 22.1957 | 22.2594 | 22.0865 | 21.4058 | 20.2195 | 22.1894 | 22.3706 | 22.4011 | 22.3497 | 21.9844 | 21.2077 | 22.2576 | 17.3665 | 17.2462 | 16.3317 | 16.3346 | 16.3547 | 17.1038 | 16.8635 | 22.3981 | 22.1463 | 21.7143 | 22.0848 | 21.8055 | 21.3089 | 21.9467 | 21.5285 | 20.9007 | 20.1059 | 20.3218 | 19.8649 | 19.7734 | 0.0088592 | -0.0003494 | 20.7721 | 22.0785 | 22.3801 | 20.1081 | 21.6766 | 22.1156 | 21.9485 | 21.7147 | 21.2813 | 21.7871 | 21.4522 | 21.0476 | 20.2823 | 20.3374 | 20.2383 | 20.2304 | 20.0686 |  | 20.2262 | 19.9553 | 20.1224 | 19.6736 | 20.0835 | 20.3084 |  | 20.4036 |  |  | 20.2938 | 20.3745 | 20.6353 | [5 empty] | 21.9434 | 20.3561 | 21.6797 | 22.061 | 19.5479 | 21.1823 | 21.8056 | 19.4 | 19.9453 | 21.1697 |  | 19.7928 | 20.9309 | 18.8785 | 19.7134 | 20.8192 | 19.4507 | 20.0452 | 19.0655 | 20.0818 | 19.1326 | 20.1786 | 18.854 | 20.1074 | 21.0639 | 19.421 | 19.7847 | 20.9941 | 18.9505 | 19.8551 | 20.8206 | 19.0078 | 20.1025 | 19.3113 | 19.9259 | 18.8828 | 20.0949 | -0.22867 | 20.9473 | 0.047307 | 0.011312 | -27.0605 | 3.0969 | 1.91 | -0.08 | 0.8203 | -0.5339 | -8.9216 | 0.95845 | 0.55754 | -16.7081 | 3.3222 | 0.42441 | 0.42408 | 0.4306 | 0.37325 | 0.46019 | 0.44145 | 0.42858
42838.4176 | -235 | 22.8977 | 22.8752 | 22.8543 | 22.7816 | 22.4106 | 21.7489 | 22.7202 | 21.8119 | 22.3733 | 22.3793 | 22.3654 | 22.0297 | 21.2533 | 22.2188 | 21.6016 | 21.769 | 21.9059 | 21.0769 | 21.179 | 21.4019 | 20.4833 | 20.6252 | 20.9144 | 21.8902 | 21.6513 | 21.2828 | 20.2941 | 20.4012 | 20.3723 | 22.0773 | 21.6678 | 21.1904 | 21.9966 | 21.7355 | 21.3544 | 19.9191 | 20.4245 |  | 20.5009 | 20.0447 | 20.1374 | 19.0857 |  | 16.7823 | 16.7424 | 16.4915 | 16.7827 | 16.8909 | 17.4416 | 17.9208 | 16.0799 | 16.872 | 16.2387 | 16.9137 | 17.9295 | 44.6684 | 47.7278 | 43.6766 | 21.365 |  |  | 0.51935 | -0.29183 | -56.8978 | 0.37057 | 0.11644 | -197.8164 | 8.0447 | -0.39529 | -0.073855 | 0.012489 | -0.012902 | 8.8285 | 9.0582 | 1.979 | 21.786 | 22.0078 | 22.1952 | 22.2678 | 22.0929 | 21.4152 | 20.2329 | 22.1968 | 22.3694 | 22.4027 | 22.3557 | 21.983 | 21.217 | 22.2672 | 17.3575 | 17.2027 | 16.3333 | 16.3368 | 16.3462 | 17.1039 | 16.8593 | 22.4006 | 22.1542 | 21.7107 | 22.0938 | 21.8017 | 21.3081 | 21.9448 | 21.5285 | 20.9024 | 20.1034 | 20.322 | 19.8591 | 19.7819 | -0.010014 | -0.10572 | 20.7586 | 22.0675 | 22.3793 | 20.0884 | 21.6722 | 22.1118 | 21.9414 | 21.7103 | 21.2802 | 21.782 | 21.444 | 21.0519 | 20.2776 | 20.3349 | 20.2406 | 20.2238 | 20.0847 |  | 20.2295 | 19.9685 | 20.1288 | 19.6978 | 20.0957 | 20.3203 |  | 20.4128 |  |  | 20.2988 | 20.3822 | 20.6263 | [5 empty] | 21.9407 | 20.3533 | 21.675 | 22.0595 | 19.543 | 21.1781 | 21.8029 | 19.3936 | 19.9373 | 21.1638 |  | 19.7883 | 20.9223 | 18.8784 | 19.7068 | 20.813 | 19.4503 | 20.0446 | 19.0514 | 20.0748 | 19.1266 | 20.1807 | 18.8622 | 20.1109 | 21.0635 | 19.4248 | 19.7843 | 20.9948 | 18.9543 | 19.8496 | 20.8213 | 19.0171 | 20.1076 | 19.3101 | 19.9236 | 18.8749 | 20.0946 | -0.070251 | 20.9477 | 0.047977 | 0.012074 | -27.1077 | 3.0968 | -3.76 | -0.04 | 0.86043 | -0.64098 | -8.9502 | 0.7223 | 0.40538 | -16.7086 | 3.3695 | 0.42407 | 0.42393 | 0.43034 | 0.37427 | 0.45953 | 0.44143 | 0.42826
42838.4176 | -234 | 22.902 | 22.8774 | 22.8569 | 22.7872 | 22.4064 | 21.753 | 22.7251 | 21.807 | 22.3751 | 22.3822 | 22.3641 | 22.0338 | 21.2544 | 22.2209 | 21.6007 | 21.7569 | 21.9024 | 21.0855 | 21.1799 | 21.3985 | 20.4789 | 20.6226 | 20.9144 | 21.8846 | 21.6537 | 21.2809 | 20.2943 | 20.4023 | 20.3754 | 22.0729 | 21.6751 | 21.1884 | 21.995 | 21.7443 | 21.3436 | 19.9099 | 20.4224 |  | 20.4981 | 20.0437 | 20.1283 | 19.0969 |  | 16.7853 | 16.7488 | 16.4914 | 16.7935 | 16.913 | 17.4672 | 17.9461 | 16.084 | 16.8762 | 16.2637 | 16.9168 | 17.924 | 44.6872 | 47.6786 | 43.6696 | 21.3651 |  |  | 0.47927 | -0.20837 | -57.4334 | 0.61896 | 0.11578 | -197.7888 | 7.5959 | -0.34075 | 0.10167 | 0.062212 | 0.01279 | 8.8293 | 9.059 | 1.9791 | 21.791 | 22.0125 | 22.2009 | 22.2692 | 22.0939 | 21.4192 | 20.2283 | 22.1903 | 22.3725 | 22.4134 | 22.3541 | 21.9867 | 21.2156 | 22.2717 | 17.3221 | 17.2016 | 16.3225 | 16.3282 | 16.3383 | 17.104 | 16.8611 | 22.3969 | 22.1557 | 21.7148 | 22.0918 | 21.8017 | 21.3094 | 21.9485 | 21.5286 | 20.9123 | 20.1018 | 20.315 | 19.8597 | 19.7847 | 0.098312 | -0.058741 | 20.7708 | 22.0747 | 22.3798 | 20.086 | 21.6748 | 22.1169 | 21.9474 | 21.7127 | 21.2894 | 21.7895 | 21.4533 | 21.0466 | 20.2789 | 20.3309 | 20.2347 | 20.2181 | 20.0678 |  | 20.2332 | 19.9601 | 20.1309 | 19.6959 | 20.0887 | 20.3186 |  | 20.4127 |  |  | 20.2986 | 20.3842 | 20.6237 | [5 empty] | 21.936 | 20.3437 | 21.6776 | 22.0512 | 19.5433 | 21.1688 | 21.7953 | 19.4081 | 19.9457 | 21.1707 |  | 19.799 | 20.9309 | 18.8877 | 19.7133 | 20.8217 | 19.4503 | 20.0525 | 19.0579 | 20.0806 | 19.1431 | 20.1886 | 18.8664 | 20.1074 | 21.0629 | 19.4251 | 19.7799 | 20.9927 | 18.9492 | 19.8395 | 20.815 | 19.0064 | 20.1003 | 19.3055 | 19.9171 | 18.8748 | 20.1007 | -0.069695 | 20.9481 | 0.048936 | 0.013388 | -27.0916 | 3.0968 | -2.52 | 0.03 | 0.82657 | -0.54164 | -8.9923 | 0.93351 | 0.40425 | -16.7082 | 3.2743 | 0.42467 | 0.42423 | 0.43016 | 0.37821 | 0.46093 | 0.44081 | 0.42813
42838.4176 | -233 | 22.9087 | 22.8686 | 22.8586 | 22.7807 | 22.4102 | 21.7473 | 22.7114 | 21.8084 | 22.3739 | 22.3807 | 22.3652 | 22.0337 | 21.247 | 22.21 | 21.5971 | 21.765 | 21.8847 | 21.0807 | 21.1806 | 21.3982 | 20.4765 | 20.6173 | 20.9062 | 21.8826 | 21.6486 | 21.2807 | 20.2914 | 20.4001 | 20.372 | 22.0746 | 21.6596 | 21.1834 | 21.9903 | 21.7294 | 21.3523 | 19.9012 | 20.4165 |  | 20.5043 | 20.0295 | 20.1255 | 19.0937 |  | 16.7766 | 16.7479 | 16.4933 | 16.7982 | 16.9113 | 17.4527 | 17.9491 | 16.076 | 16.863 | 16.2577 | 16.9066 | 17.9149 | 44.7046 | 47.614 | 43.6778 | 21.3562 |  |  | 0.39384 | -0.3076 | -59.2201 | 0.4146 | 0.032988 | -197.8236 | 7.3034 | -0.44326 | -0.14955 | 0.08571 | 0.080842 | 8.8288 | 9.0584 | 1.9785 | 21.787 | 22.007 | 22.197 | 22.2658 | 22.0833 | 21.4144 | 20.2215 | 22.1894 | 22.367 | 22.4069 | 22.3506 | 21.9807 | 21.2061 | 22.2697 | 17.3081 | 17.2363 | 16.3215 | 16.3136 | 16.359 | 17.1055 | 16.8611 | 22.3911 | 22.1519 | 21.7081 | 22.0742 | 21.8038 | 21.3116 | 21.9445 | 21.524 | 20.9059 | 20.1078 | 20.3178 | 19.8508 | 19.7734 | -0.017092 | -0.070533 | 20.7716 | 22.0711 | 22.375 | 20.0793 | 21.6665 | 22.1187 | 21.9524 | 21.7128 | 21.2773 | 21.7757 | 21.4439 | 21.0428 | 20.2765 | 20.3266 | 20.2327 | 20.2244 | 20.0708 |  | 20.2236 | 19.966 | 20.1316 | 19.6965 | 20.0952 | 20.3264 |  | 20.4098 |  |  | 20.3002 | 20.3851 | 20.625 | [5 empty] | 21.941 | 20.344 | 21.6768 | 22.0574 | 19.539 | 21.1755 | 21.7937 | 19.3976 | 19.9381 | 21.1751 |  | 19.7848 | 20.9211 | 18.8788 | 19.7085 | 20.8139 | 19.4354 | 20.0414 | 19.0549 | 20.0749 | 19.1322 | 20.1877 | 18.8671 | 20.1064 | 21.0726 | 19.4236 | 19.7863 | 21.002 | 18.9515 | 19.8393 | 20.8127 | 19.0063 | 20.1015 | 19.3052 | 19.9185 | 18.8739 | 20.0911 | -0.089173 | 20.9473 | 0.049126 | 0.01436 | -27.0761 | 3.0968 | -2.3 | -0.16 | 0.74929 | -0.65808 | -9.1311 | 0.76402 | 0.21577 | -16.7092 | 3.2106 | 0.42426 | 0.42409 | 0.43036 | 0.37993 | 0.46104 | 0.44061 | 0.42864
42838.4176 | -232 | 22.8998 | 22.8734 | 22.8531 | 22.7819 | 22.4078 | 21.7581 | 22.72 | 21.8145 | 22.3729 | 22.3825 | 22.3623 | 22.0306 | 21.2504 | 22.2123 | 21.6026 | 21.7656 | 21.9007 | 21.0859 | 21.185 | 21.3937 | 20.4781 | 20.6188 | 20.9044 | 21.8886 | 21.6481 | 21.2773 | 20.2891 | 20.3978 | 20.3713 | 22.0785 | 21.67 | 21.1897 | 21.9942 | 21.7316 | 21.3521 | 19.9138 | 20.4297 |  | 20.5054 | 20.0369 | 20.1301 | 19.1169 |  | 16.7849 | 16.7508 | 16.5121 | 16.8027 | 16.9001 | 17.4358 | 17.9486 | 16.0888 | 16.8601 | 16.2543 | 16.9116 | 17.9316 | 44.7199 | 47.5579 | 43.6977 | 21.3609 |  |  | 0.41356 | -0.19391 | -59.7149 | 0.50988 | 0.32343 | -197.8059 | 6.9381 | -0.42354 | -0.2451 | 0.14991 | 0.00602 | 8.829 | 9.0583 | 1.9782 | 21.7845 | 22.0129 | 22.1972 | 22.2646 | 22.0816 | 21.4158 | 20.2259 | 22.1915 | 22.3675 | 22.3965 | 22.3546 | 21.9769 | 21.2118 | 22.2665 | 17.2856 | 17.2758 | 16.3329 | 16.3122 | 16.3547 | 17.1061 | 16.8668 | 22.3993 | 22.156 | 21.7126 | 22.0847 | 21.7993 | 21.3095 | 21.9525 | 21.5365 | 20.901 | 20.1104 | 20.3204 | 19.858 | 19.7758 | -0.037145 | 0.045299 | 20.7728 | 22.0682 | 22.3803 | 20.098 | 21.6766 | 22.1251 | 21.9514 | 21.7161 | 21.2886 | 21.7866 | 21.4558 | 21.0559 | 20.288 | 20.3351 | 20.2376 | 20.2364 | 20.0755 |  | 20.2307 | 19.9671 | 20.1266 | 19.6988 | 20.0873 | 20.317 |  | 20.4065 |  |  | 20.3052 | 20.381 | 20.6293 | [5 empty] | 21.9412 | 20.3401 | 21.6789 | 22.0576 | 19.5343 | 21.1804 | 21.7955 | 19.3958 | 19.923 | 21.1673 |  | 19.7839 | 20.9301 | 18.8795 | 19.7033 | 20.8136 | 19.4402 | 20.0423 | 19.0532 | 20.0757 | 19.1325 | 20.1799 | 18.8655 | 20.1121 | 21.0695 | 19.4229 | 19.7877 | 20.9972 | 18.9504 | 19.8386 | 20.8209 | 19.0128 | 20.101 | 19.3032 | 19.9145 | 18.8698 | 20.0841 | -0.095294 | 20.9475 | 0.04987 | 0.013366 | -27.0882 | 3.0968 | 1.47 | -0.02 | 0.76781 | -0.52251 | -9.1692 | 0.84728 | 0.67561 | -16.708 | 3.1291 | 0.42437 | 0.42389 | 0.43003 | 0.3825 | 0.46044 | 0.44038 | 0.42866
42838.4176 | -231 | 22.9092 | 22.8751 | 22.8673 | 22.7853 | 22.4178 | 21.7581 | 22.729 | 21.8133 | 22.3835 | 22.3866 | 22.3627 | 22.0382 | 21.2472 | 22.2165 | 21.608 | 21.7656 | 21.9025 | 21.0834 | 21.1809 | 21.3961 | 20.4777 | 20.6208 | 20.9163 | 21.8912 | 21.6507 | 21.2815 | 20.2863 | 20.4005 | 20.369 | 22.0824 | 21.6705 | 21.189 | 21.9948 | 21.7352 | 21.3552 | 19.9076 | 20.4298 |  | 20.4982 | 20.0359 | 20.1304 | 19.1312 |  | 16.7851 | 16.7633 | 16.5188 | 16.8029 | 16.9012 | 17.4347 | 17.9391 | 16.1171 | 16.8743 | 16.2484 | 16.9052 | 17.9265 | 44.7307 | 47.4965 | 43.7043 | 21.3658 |  |  | 0.51804 | -0.080233 | -60.6112 | 0.32457 | -0.010384 | -197.8282 | 6.6549 | -0.3966 | -0.068795 | 0.23215 | -0.0071736 | 8.8289 | 9.0583 | 1.979 | 21.777 | 22.003 | 22.1855 | 22.2541 | 22.0857 | 21.4111 | 20.2213 | 22.1951 | 22.3579 | 22.3977 | 22.3503 | 21.972 | 21.2101 | 22.2568 | 17.2834 | 17.2944 | 16.3421 | 16.3165 | 16.3511 | 17.1082 | 16.8665 | 22.3963 | 22.1592 | 21.7134 | 22.088 | 21.8025 | 21.3076 | 21.9437 | 21.534 | 20.9056 | 20.1033 | 20.3214 | 19.8596 | 19.7697 | 0.0049272 | 0.04663 | 20.7632 | 22.0771 | 22.3837 | 20.0857 | 21.6823 | 22.1178 | 21.9556 | 21.7297 | 21.2815 | 21.7784 | 21.4542 | 21.0521 | 20.278 | 20.3376 | 20.2426 | 20.2257 | 20.0905 |  | 20.2354 | 19.9785 | 20.1302 | 19.7005 | 20.0919 | 20.3297 |  | 20.4133 |  |  | 20.3061 | 20.3785 | 20.6216 | [5 empty] | 21.933 | 20.3305 | 21.6743 | 22.0561 | 19.5397 | 21.1673 | 21.7926 | 19.4016 | 19.9382 | 21.1672 |  | 19.7936 | 20.9292 | 18.8883 | 19.7139 | 20.8109 | 19.4402 | 20.0447 | 19.0607 | 20.0831 | 19.1375 | 20.1914 | 18.8622 | 20.1178 | 21.0632 | 19.4222 | 19.7809 | 20.9819 | 18.9424 | 19.8391 | 20.8183 | 19.0084 | 20.1022 | 19.2918 | 19.9172 | 18.8625 | 20.0792 | -0.13202 | 20.9472 | 0.04829 | 0.010607 | -27.0308 | 3.0968 | 8.59 | -0.13 | 0.85934 | -0.33611 | -9.238 | 0.67601 | -0.12106 | -16.7089 | 3.0646 | 0.42411 | 0.4237 | 0.43014 | 0.38299 | 0.45938 | 0.43978 | 0.4286
42838.4176 | -230 | 22.9055 | 22.8699 | 22.8629 | 22.7804 | 22.4166 | 21.7541 | 22.7227 | 21.8137 | 22.3793 | 22.3872 | 22.3663 | 22.0398 | 21.25 | 22.2122 | 21.5933 | 21.759 | 21.8924 | 21.0761 | 21.1796 | 21.3944 | 20.4744 | 20.6048 | 20.9073 | 21.8843 | 21.6427 | 21.279 | 20.2839 | 20.3883 | 20.3643 | 22.0814 | 21.6758 | 21.1898 | 22.0028 | 21.7373 | 21.3565 | 19.9159 | 20.434 |  | 20.5056 | 20.0459 | 20.1364 | 19.1385 |  | 16.7862 | 16.7642 | 16.523 | 16.8004 | 16.8977 | 17.4305 | 17.9613 | 16.1238 | 16.8779 | 16.2411 | 16.9148 | 17.9161 | 44.7282 | 47.4125 | 43.6996 | 21.3599 |  |  | 0.33076 | -0.37988 | -60.7249 | 0.42511 | 0.037588 | -197.7974 | 7.0445 | -0.37952 | -0.041162 | 0.22942 | 0.048899 | 8.8286 | 9.0582 | 1.9792 | 21.7778 | 22.0072 | 22.1856 | 22.2651 | 22.0867 | 21.4093 | 20.2161 | 22.1859 | 22.3634 | 22.4012 | 22.3534 | 21.9749 | 21.2094 | 22.26 | 17.2915 | 17.2887 | 16.3343 | 16.3285 | 16.3452 | 17.1047 | 16.8621 | 22.4043 | 22.1617 | 21.719 | 22.0943 | 21.8065 | 21.3073 | 21.9505 | 21.5345 | 20.9121 | 20.1089 | 20.3174 | 19.866 | 19.7679 | -0.12208 | -0.11124 | 20.7675 | 22.0776 | 22.3844 | 20.0893 | 21.6729 | 22.122 | 21.9528 | 21.7188 | 21.2878 | 21.7815 | 21.4495 | 21.0449 | 20.2909 | 20.3361 | 20.2334 | 20.2281 | 20.084 |  | 20.2353 | 19.9802 | 20.1332 | 19.6906 | 20.0866 | 20.3242 |  | 20.4179 |  |  | 20.3187 | 20.3709 | 20.6276 | [5 empty] | 21.9337 | 20.3354 | 21.679 | 22.0542 | 19.5457 | 21.1678 | 21.7916 | 19.3977 | 19.9317 | 21.1661 |  | 19.7862 | 20.9272 | 18.8848 | 19.7128 | 20.815 | 19.4307 | 20.0457 | 19.0506 | 20.0705 | 19.1297 | 20.1768 | 18.856 | 20.1151 | 21.0641 | 19.4313 | 19.7738 | 20.9966 | 18.9592 | 19.8476 | 20.8186 | 19.0216 | 20.1041 | 19.3098 | 19.9064 | 18.8679 | 20.0809 | -0.13629 | 20.9483 | 0.047737 | 0.010302 | -27.0438 | 3.0968 | 4.69 | -0.14 | 0.68665 | -0.73135 | -9.2467 | 0.77366 | 0.23032 | -16.7075 | 3.153 | 0.42429 | 0.42375 | 0.43023 | 0.38169 | 0.45974 | 0.43986 | 0.42883
42838.4176 | -229 | 22.9062 | 22.8708 | 22.8643 | 22.7817 | 22.4136 | 21.7569 | 22.7304 | 21.8155 | 22.3777 | 22.3835 | 22.3664 | 22.0372 | 21.2551 | 22.2146 | 21.6002 | 21.7666 | 21.9037 | 21.0929 | 21.1748 | 21.403 | 20.4743 | 20.6256 | 20.9079 | 21.8899 | 21.6513 | 21.2786 | 20.2858 | 20.4019 | 20.3652 | 22.0791 | 21.6774 | 21.192 | 22.0028 | 21.7431 | 21.3576 | 19.9188 | 20.4392 |  | 20.5065 | 20.043 | 20.1342 | 19.1372 |  | 16.791 | 16.7688 | 16.5209 | 16.7994 | 16.8941 | 17.4378 | 17.9873 | 16.1474 | 16.8755 | 16.2407 | 16.9209 | 17.9255 | 44.7271 | 47.3369 | 43.7006 | 21.3686 |  |  | 0.45561 | -0.28328 | -60.9135 | 0.15963 | 0.093444 | -197.844 | 6.8382 | -0.37558 | -0.023259 | 0.052561 | 0.094556 | 8.8293 | 9.059 | 1.9786 | 21.7871 | 22.0105 | 22.2059 | 22.2683 | 22.0952 | 21.4152 | 20.2206 | 22.1966 | 22.372 | 22.4115 | 22.3619 | 21.9825 | 21.2174 | 22.2655 | 17.2879 | 17.2905 | 16.3487 | 16.3486 | 16.3626 | 17.0993 | 16.859 | 22.3963 | 22.1589 | 21.7118 | 22.0876 | 21.8025 | 21.2999 | 21.9525 | 21.5332 | 20.9065 | 20.1051 | 20.3177 | 19.8593 | 19.7693 | 0.03599 | -0.057409 | 20.7684 | 22.0795 | 22.3889 | 20.0931 | 21.6772 | 22.1209 | 21.9534 | 21.7172 | 21.2882 | 21.7938 | 21.4548 | 21.0432 | 20.287 | 20.3555 | 20.2426 | 20.2346 | 20.0617 |  | 20.2368 | 19.9831 | 20.1338 | 19.6961 | 20.0904 | 20.3211 |  | 20.4153 |  |  | 20.3204 | 20.3586 | 20.633 | [5 empty] | 21.9377 | 20.3426 | 21.6792 | 22.0517 | 19.5416 | 21.1739 | 21.7976 | 19.4036 | 19.9429 | 21.1767 |  | 19.7891 | 20.9297 | 18.8852 | 19.7095 | 20.8124 | 19.4337 | 20.0535 | 19.0518 | 20.0729 | 19.1387 | 20.1807 | 18.8708 | 20.1167 | 21.0791 | 19.43 | 19.7805 | 21.0003 | 18.9548 | 19.8437 | 20.8204 | 19.0169 | 20.102 | 19.317 | 19.9124 | 18.8812 | 20.079 | 0.019716 | 20.9478 | 0.048548 | 0.011834 | -27.0665 | 3.0968 | -1.02 | -0.07 | 0.8059 | -0.63156 | -9.2611 | 0.4741 | 0.36315 | -16.7096 | 3.1065 | 0.42496 | 0.42369 | 0.43021 | 0.38146 | 0.45778 | 0.43999 | 0.42867
42838.4176 | -228 | 22.9043 | 22.8754 | 22.8523 | 22.7758 | 22.4132 | 21.7586 | 22.7211 | 21.8132 | 22.381 | 22.3781 | 22.3619 | 22.0333 | 21.2543 | 22.2138 | 21.5927 | 21.7657 | 21.8872 | 21.0767 | 21.1707 | 21.3885 | 20.4717 | 20.6137 | 20.9022 | 21.8809 | 21.6465 | 21.2654 | 20.2783 | 20.389 | 20.3474 | 22.0778 | 21.6766 | 21.198 | 22.0062 | 21.7445 | 21.3612 | 19.9182 | 20.4359 |  | 20.516 | 20.0448 | 20.1377 | 19.1291 |  | 16.7904 | 16.7716 | 16.5187 | 16.7972 | 16.8906 | 17.457 | 18.0141 | 16.1674 | 16.8712 | 16.2308 | 16.9264 | 17.9258 | 44.7202 | 47.2385 | 43.6986 | 21.3566 |  |  | 0.57915 | -0.41405 | -61.6849 | 0.26083 | 0.063216 | -197.8006 | 6.2902 | -0.31512 | -0.26242 | 0.016476 | 0.024769 | 8.8299 | 9.0596 | 1.9782 | 21.7834 | 22.0033 | 22.1915 | 22.2592 | 22.0836 | 21.4046 | 20.2198 | 22.1947 | 22.3693 | 22.403 | 22.346 | 21.9805 | 21.211 | 22.2607 | 17.2793 | 17.2745 | 16.3553 | 16.3604 | 16.3711 | 17.1004 | 16.8635 | 22.3958 | 22.1512 | 21.7064 | 22.092 | 21.7997 | 21.2987 | 21.948 | 21.5288 | 20.912 | 20.1034 | 20.301 | 19.8525 | 19.7732 | 0.10991 | -0.078712 | 20.7685 | 22.0746 | 22.3888 | 20.0933 | 21.6721 | 22.1214 | 21.9452 | 21.7163 | 21.2889 | 21.7844 | 21.4516 | 21.0472 | 20.2823 | 20.3389 | 20.2243 | 20.2258 | 20.047 |  | 20.226 | 19.9759 | 20.1291 | 19.6947 | 20.0879 | 20.3147 |  | 20.4081 |  |  | 20.3161 | 20.3625 | 20.6402 | [5 empty] | 21.9407 | 20.3397 | 21.6825 | 22.0592 | 19.5428 | 21.1796 | 21.7931 | 19.4002 | 19.9394 | 21.1679 |  | 19.7853 | 20.922 | 18.8841 | 19.7022 | 20.8089 | 19.4389 | 20.0374 | 19.0432 | 20.0742 | 19.1313 | 20.1751 | 18.8639 | 20.1098 | 21.0651 | 19.4083 | 19.7718 | 20.9845 | 18.94 | 19.8343 | 20.8022 | 18.9991 | 20.0924 | 19.2944 | 19.8959 | 18.8608 | 20.0747 | -0.22997 | 20.9478 | 0.048542 | 0.013431 | -27.0744 | 3.0968 | 16.19 | -0.04 | 0.90858 | -0.76354 | -9.3196 | 0.60602 | 0.2987 | -16.7084 | 2.9796 | 0.425 | 0.42373 | 0.43016 | 0.38254 | 0.45757 | 0.44019 | 0.4285
42838.4177 | -227 | 22.9038 | 22.8673 | 22.8452 | 22.7746 | 22.4121 | 21.7485 | 22.7249 | 21.8099 | 22.37 | 22.3829 | 22.3604 | 22.03 | 21.2454 | 22.2185 | 21.5935 | 21.7615 | 21.8934 | 21.0872 | 21.1814 | 21.3905 | 20.476 | 20.622 | 20.9044 | 21.8848 | 21.6458 | 21.2848 | 20.2895 | 20.3939 | 20.3543 | 22.0731 | 21.6668 | 21.1853 | 21.9889 | 21.7377 | 21.3499 | 19.9082 | 20.431 |  | 20.5039 | 20.0382 | 20.1334 | 19.1174 |  | 16.8069 | 16.7774 | 16.5256 | 16.8005 | 16.9138 | 17.4906 | 18.0344 | 16.2088 | 16.8861 | 16.2382 | 16.9278 | 17.926 | 44.7379 | 47.1516 | 43.7002 | 21.3693 |  |  | 0.49701 | -0.32074 | -62.7488 | 0.43168 | 0.12367 | -197.8177 | 6.4407 | -0.27898 | 0.1441 | -0.07248 | 0.052892 | 8.8293 | 9.0589 | 1.9783 | 21.792 | 22.0057 | 22.1998 | 22.2656 | 22.0898 | 21.4108 | 20.2237 | 22.1981 | 22.3684 | 22.4044 | 22.3592 | 21.9817 | 21.2178 | 22.2625 | 17.3074 | 17.2854 | 16.3527 | 16.3498 | 16.3572 | 17.105 | 16.8638 | 22.3973 | 22.1494 | 21.71 | 22.0909 | 21.7962 | 21.3098 | 21.9509 | 21.5327 | 20.9065 | 20.1052 | 20.3049 | 19.85 | 19.7699 | 0.024391 | -0.10819 | 20.7594 | 22.0654 | 22.377 | 20.0829 | 21.6659 | 22.1134 | 21.9379 | 21.7024 | 21.2832 | 21.7781 | 21.4358 | 21.0371 | 20.2739 | 20.3315 | 20.2202 | 20.2225 | 20.048 |  | 20.22 | 19.9719 | 20.115 | 19.705 | 20.0854 | 20.3259 |  | 20.4094 |  |  | 20.3166 | 20.3565 | 20.631 | [5 empty] | 21.9345 | 20.3344 | 21.6801 | 22.0574 | 19.5406 | 21.1687 | 21.7916 | 19.3977 | 19.9301 | 21.1698 |  | 19.7865 | 20.9261 | 18.8955 | 19.7154 | 20.8169 | 19.4304 | 20.0471 | 19.059 | 20.0745 | 19.1374 | 20.1799 | 18.8673 | 20.1219 | 21.0736 | 19.4227 | 19.7772 | 20.9938 | 18.9538 | 19.8453 | 20.8172 | 18.9964 | 20.0965 | 19.3132 | 19.9111 | 18.8674 | 20.081 | -0.099004 | 20.9475 | 0.048727 | 0.014832 | -27.1018 | 3.0967 | 5 | -0.15 | 0.8417 | -0.67203 | -9.3997 | 0.77964 | 0.41781 | -16.71 | 3.0152 | 0.42477 | 0.42337 | 0.42979 | 0.37995 | 0.45789 | 0.44018 | 0.42865
42838.4177 | -226 | 22.9009 | 22.8576 | 22.8529 | 22.7743 | 22.4121 | 21.7487 | 22.7134 | 21.8026 | 22.3685 | 22.3772 | 22.3632 | 22.031 | 21.2474 | 22.2175 | 21.5924 | 21.7585 | 21.8905 | 21.0827 | 21.1773 | 21.388 | 20.4727 | 20.6106 | 20.9051 | 21.8819 | 21.6462 | 21.2766 | 20.2792 | 20.3928 | 20.3609 | 22.0786 | 21.6683 | 21.1846 | 21.9888 | 21.7309 | 21.3493 | 19.9119 | 20.4288 |  | 20.5047 | 20.0346 | 20.1284 | 19.1097 |  | 16.7942 | 16.7707 | 16.5131 | 16.7952 | 16.9024 | 17.4914 | 18.0488 | 16.2147 | 16.8736 | 16.2399 | 16.9291 | 17.9329 | 44.7598 | 47.0559 | 43.7079 | 21.3669 |  |  | 0.47993 | -0.20246 | -62.5287 | 0.2996 | 0.27218 | -197.8427 | 5.9761 | -0.41829 | 0.011964 | 0.12033 | 0.16209 | 8.8289 | 9.0585 | 1.9786 | 21.7871 | 22.0097 | 22.2013 | 22.2659 | 22.0884 | 21.4193 | 20.2221 | 22.1971 | 22.374 | 22.4025 | 22.3583 | 21.9822 | 21.2117 | 22.265 | 17.3444 | 17.275 | 16.3504 | 16.3479 | 16.3433 | 17.1091 | 16.8581 | 22.3987 | 22.1557 | 21.7126 | 22.088 | 21.8079 | 21.3125 | 21.9535 | 21.5269 | 20.9056 | 20.1082 | 20.3066 | 19.8486 | 19.7605 | -0.12719 | -0.025456 | 20.7653 | 22.0755 | 22.3759 | 20.0878 | 21.6764 | 22.1207 | 21.9464 | 21.713 | 21.2829 | 21.783 | 21.4488 | 21.0412 | 20.2824 | 20.3331 | 20.2264 | 20.2295 | 20.0437 |  | 20.2234 | 19.9678 | 20.1252 | 19.7044 | 20.082 | 20.3182 |  | 20.4008 |  |  | 20.3056 | 20.3529 | 20.6335 | [5 empty] | 21.9323 | 20.3325 | 21.6675 | 22.0504 | 19.5295 | 21.1627 | 21.7893 | 19.3916 | 19.9262 | 21.1635 |  | 19.7808 | 20.9251 | 18.898 | 19.7072 | 20.8049 | 19.4332 | 20.0377 | 19.0574 | 20.0727 | 19.1335 | 20.173 | 18.8702 | 20.125 | 21.0768 | 19.4248 | 19.7805 | 20.9927 | 18.9566 | 19.8463 | 20.8199 | 18.9915 | 20.1007 | 19.3109 | 19.9083 | 18.8733 | 20.085 | -0.11607 | 20.9474 | 0.047737 | 0.013671 | -27.0503 | 3.0968 | -6.11 | -0.01 | 0.82712 | -0.53392 | -9.3831 | 0.6495 | 0.61983 | -16.7111 | 2.9044 | 0.42501 | 0.42383 | 0.4297 | 0.37632 | 0.45748 | 0.44052 | 0.42902
42838.4177 | -225 | 22.9056 | 22.8726 | 22.8547 | 22.7813 | 22.4107 | 21.7584 | 22.7215 | 21.8178 | 22.3739 | 22.3848 | 22.3666 | 22.0316 | 21.2506 | 22.2181 | 21.598 | 21.7652 | 21.8972 | 21.0878 | 21.1784 | 21.4003 | 20.4775 | 20.6146 | 20.9103 | 21.8903 | 21.6452 | 21.2823 | 20.2829 | 20.3933 | 20.3606 | 22.0814 | 21.6834 | 21.1971 | 21.9956 | 21.7401 | 21.3581 | 19.9122 | 20.4311 |  | 20.5066 | 20.0446 | 20.1413 | 19.1205 |  | 16.7892 | 16.7609 | 16.5186 | 16.7985 | 16.8995 | 17.4942 | 18.0367 | 16.1907 | 16.8731 | 16.2712 | 16.9244 | 17.9283 | 44.7643 | 46.9343 | 43.7223 | 21.3716 |  |  | 0.51015 | -0.38974 | -63.4006 | 0.45731 | -0.007752 | -197.7967 | 6.1522 | -0.15544 | 0.1114 | -0.015834 | 0.14091 | 8.8282 | 9.0579 | 1.9792 | 21.7909 | 22.014 | 22.2036 | 22.2638 | 22.0983 | 21.4166 | 20.225 | 22.1988 | 22.373 | 22.4065 | 22.3619 | 21.9903 | 21.2147 | 22.2657 | 17.3898 | 17.2761 | 16.3511 | 16.347 | 16.3338 | 17.1121 | 16.858 | 22.4024 | 22.1621 | 21.7141 | 22.0879 | 21.8067 | 21.3076 | 21.9543 | 21.5288 | 20.9103 | 20.1073 | 20.3064 | 19.8561 | 19.7602 | -0.16081 | 0.055379 | 20.7681 | 22.0781 | 22.3817 | 20.099 | 21.6743 | 22.1165 | 21.9554 | 21.7192 | 21.2886 | 21.7799 | 21.4536 | 21.0495 | 20.2873 | 20.341 | 20.2267 | 20.2307 | 20.0488 |  | 20.2171 | 19.9663 | 20.1286 | 19.7046 | 20.0894 | 20.3215 |  | 20.4045 |  |  | 20.3058 | 20.3501 | 20.6263 | [5 empty] | 21.9301 | 20.3352 | 21.6655 | 22.0468 | 19.5325 | 21.1613 | 21.7833 | 19.3998 | 19.9425 | 21.1709 |  | 19.7917 | 20.929 | 18.8998 | 19.7145 | 20.8135 | 19.4415 | 20.0495 | 19.063 | 20.0795 | 19.1386 | 20.1802 | 18.8714 | 20.1222 | 21.0757 | 19.4239 | 19.7757 | 21.001 | 18.9521 | 19.8538 | 20.816 | 18.9941 | 20.1036 | 19.3125 | 19.9196 | 18.8755 | 20.0896 | -0.15354 | 20.9478 | 0.046975 | 0.012437 | -26.9688 | 3.0967 | -0.77 | -0.01 | 0.85277 | -0.74077 | -9.4481 | 0.80243 | -0.10461 | -16.7093 | 2.9469 | 0.42465 | 0.42398 | 0.42994 | 0.37162 | 0.4574 | 0.44023 | 0.42899
42838.4177 | -224 | 22.9101 | 22.8729 | 22.8609 | 22.7818 | 22.4074 | 21.7498 | 22.724 | 21.8102 | 22.3833 | 22.3835 | 22.364 | 22.0259 | 21.2523 | 22.2158 | 21.5987 | 21.7663 | 21.8948 | 21.0831 | 21.1783 | 21.3974 | 20.4752 | 20.6166 | 20.908 | 21.889 | 21.6394 | 21.2806 | 20.2802 | 20.3894 | 20.3564 | 22.072 | 21.6663 | 21.1919 | 21.9856 | 21.7391 | 21.3495 | 19.909 | 20.4252 |  | 20.5023 | 20.0382 | 20.1385 | 19.1127 |  | 16.798 | 16.7635 | 16.5232 | 16.7951 | 16.8964 | 17.4824 | 18.0141 | 16.1349 | 16.8739 | 16.2544 | 16.9241 | 17.9333 | 44.7791 | 46.8203 | 43.7287 | 21.3668 |  |  | 0.32682 | -0.37265 | -63.8028 | 0.36071 | 0.12301 | -197.8394 | 5.9669 | -0.23626 | -0.069963 | 0.024868 | 0.025463 | 8.829 | 9.0588 | 1.9789 | 21.79 | 22.0073 | 22.1993 | 22.2631 | 22.0962 | 21.4147 | 20.225 | 22.1962 | 22.3706 | 22.4044 | 22.3583 | 21.9829 | 21.2139 | 22.2658 | 17.4397 | 17.2723 | 16.3648 | 16.3377 | 16.3349 | 17.1118 | 16.8631 | 22.398 | 22.1591 | 21.7073 | 22.0845 | 21.8017 | 21.3014 | 21.9462 | 21.5278 | 20.9061 | 20.1039 | 20.2999 | 19.8476 | 19.7409 | -0.085705 | 0.093039 | 20.7703 | 22.0807 | 22.3769 | 20.1005 | 21.6744 | 22.1209 | 21.9493 | 21.7148 | 21.281 | 21.7835 | 21.4495 | 21.0414 | 20.2955 | 20.3491 | 20.2341 | 20.2309 | 20.0528 |  | 20.2291 | 19.97 | 20.1359 | 19.7119 | 20.0938 | 20.3284 |  | 20.4113 |  |  | 20.3083 | 20.355 | 20.615 | [5 empty] | 21.9273 | 20.3371 | 21.6699 | 22.046 | 19.5336 | 21.1694 | 21.7822 | 19.4049 | 19.9438 | 21.1791 |  | 19.8002 | 20.9327 | 18.8977 | 19.7105 | 20.8119 | 19.4359 | 20.0485 | 19.0652 | 20.0764 | 19.1422 | 20.1844 | 18.8646 | 20.1202 | 21.0724 | 19.4203 | 19.7758 | 20.9944 | 18.9535 | 19.848 | 20.8194 | 18.9936 | 20.095 | 19.3093 | 19.9122 | 18.8717 | 20.0838 | -0.061162 | 20.9475 | 0.048684 | 0.014063 | -27.0916 | 3.0967 | 25.6 | -0.08 | 0.68254 | -0.72435 | -9.4781 | 0.71266 | 0.41669 | -16.7107 | 2.9021 | 0.42494 | 0.42412 | 0.42988 | 0.36605 | 0.45647 | 0.44034 | 0.42942
42838.4177 | -223 | 22.9018 | 22.868 | 22.8489 | 22.7834 | 22.4034 | 21.7516 | 22.7205 | 21.8121 | 22.37 | 22.3807 | 22.3618 | 22.034 | 21.2534 | 22.2172 | 21.5989 | 21.7708 | 21.9 | 21.0791 | 21.1773 | 21.4002 | 20.4756 | 20.6151 | 20.9048 | 21.8899 | 21.6472 | 21.2807 | 20.2773 | 20.397 | 20.3531 | 22.0741 | 21.6722 | 21.1939 | 21.9953 | 21.7404 | 21.3545 | 19.9133 | 20.4312 |  | 20.5148 | 20.049 | 20.1402 | 19.1319 |  | 16.7974 | 16.7699 | 16.5261 | 16.8003 | 16.9009 | 17.473 | 18.0135 | 16.0969 | 16.8783 | 16.2218 | 16.9366 | 17.9347 | 44.7897 | 46.7115 | 43.7257 | 21.3705 |  |  | 0.4451 | -0.50473 | -64.1333 | 0.62685 | 0.099356 | -197.8302 | 6.191 | -0.30066 | -0.057314 | -0.12031 | 0.12094 | 8.8284 | 9.058 | 1.9787 | 21.7895 | 22.0064 | 22.2015 | 22.2664 | 22.0939 | 21.4149 | 20.2244 | 22.2057 | 22.373 | 22.4041 | 22.3656 | 21.9839 | 21.2171 | 22.2717 | 17.4985 | 17.2634 | 16.3792 | 16.3333 | 16.3319 | 17.1104 | 16.8595 | 22.389 | 22.1516 | 21.7038 | 22.0779 | 21.7975 | 21.3029 | 21.9402 | 21.5202 | 20.9012 | 20.0939 | 20.2931 | 19.8346 | 19.7305 | -0.090817 | 0.023996 | 20.7749 | 22.0882 | 22.3807 | 20.1017 | 21.6813 | 22.1229 | 21.951 | 21.7175 | 21.2927 | 21.7933 | 21.4612 | 21.0528 | 20.3008 | 20.3602 | 20.2253 | 20.2331 | 20.0599 |  | 20.2273 | 19.9644 | 20.1278 | 19.7009 | 20.0907 | 20.3249 |  | 20.4104 |  |  | 20.3096 | 20.3564 | 20.6199 | [5 empty] | 21.9333 | 20.3422 | 21.6651 | 22.051 | 19.5365 | 21.1689 | 21.7867 | 19.403 | 19.9433 | 21.1786 |  | 19.7972 | 20.9315 | 18.9025 | 19.715 | 20.8132 | 19.4359 | 20.0514 | 19.063 | 20.0764 | 19.1503 | 20.1835 | 18.8623 | 20.1261 | 21.0743 | 19.4223 | 19.7749 | 20.9945 | 18.9601 | 19.8504 | 20.8218 | 18.9927 | 20.093 | 19.3097 | 19.9102 | 18.8752 | 20.0855 | -0.1682 | 20.9473 | 0.049015 | 0.014883 | -27.0616 | 3.0968 | 7.67 | -0.15 | 0.79653 | -0.84301 | -9.5027 | 0.93948 | 0.37448 | -16.7101 | 2.956 | 0.42469 | 0.42401 | 0.43008 | 0.35935 | 0.45445 | 0.43995 | 0.42937
42838.4177 | -222 | 22.9025 | 22.8642 | 22.85 | 22.7772 | 22.4032 | 21.7471 | 22.7182 | 21.8069 | 22.3653 | 22.3775 | 22.3551 | 22.0283 | 21.2456 | 22.2164 | 21.5972 | 21.7665 | 21.8947 | 21.0796 | 21.1754 | 21.3909 | 20.4744 | 20.6132 | 20.9002 | 21.8887 | 21.6459 | 21.2814 | 20.278 | 20.3989 | 20.3493 | 22.0849 | 21.6726 | 21.1934 | 22.0044 | 21.7447 | 21.359 | 19.9175 | 20.4299 |  | 20.5128 | 20.0446 | 20.1446 | 19.1381 |  | 16.7984 | 16.7694 | 16.5147 | 16.7949 | 16.8921 | 17.4747 | 18.0384 | 16.0666 | 16.8741 | 16.2123 | 16.9331 | 17.9326 | 44.7868 | 46.5896 | 43.7128 | 21.3789 |  |  | 0.54892 | -0.25502 | -65.1413 | 0.72081 | 0.15981 | -197.8762 | 5.1507 | -0.3552 | 0.039013 | -0.058003 | 0.16313 | 8.8286 | 9.0583 | 1.9781 | 21.7827 | 22.0052 | 22.2019 | 22.2628 | 22.0826 | 21.4109 | 20.2239 | 22.2056 | 22.3666 | 22.3952 | 22.3507 | 21.981 | 21.2137 | 22.2652 | 17.5446 | 17.2714 | 16.4001 | 16.3418 | 16.3348 | 17.1091 | 16.8688 | 22.3933 | 22.1572 | 21.7127 | 22.0814 | 21.7956 | 21.3027 | 21.9427 | 21.5263 | 20.901 | 20.0924 | 20.2991 | 19.8432 | 19.7288 | -0.046779 | -0.033634 | 20.7711 | 22.072 | 22.3742 | 20.0936 | 21.6696 | 22.1204 | 21.9444 | 21.711 | 21.2847 | 21.7822 | 21.4537 | 21.0476 | 20.2948 | 20.3423 | 20.2284 | 20.2263 | 20.0647 |  | 20.222 | 19.9535 | 20.1251 | 19.6979 | 20.0842 | 20.3187 |  | 20.4065 |  |  | 20.3096 | 20.3552 | 20.6217 | [5 empty] | 21.9356 | 20.3376 | 21.6659 | 22.0478 | 19.5342 | 21.1623 | 21.7977 | 19.4019 | 19.9439 | 21.1714 |  | 19.7955 | 20.9262 | 18.9026 | 19.7136 | 20.8141 | 19.4315 | 20.0505 | 19.0636 | 20.0751 | 19.1488 | 20.1826 | 18.8587 | 20.1208 | 21.0685 | 19.4211 | 19.7745 | 20.9897 | 18.9581 | 19.8423 | 20.8166 | 18.9881 | 20.0918 | 19.3071 | 19.9006 | 18.8678 | 20.0792 | -0.066541 | 20.9478 | 0.049575 | 0.015812 | -27.0367 | 3.0968 | -5.04 | -0.09 | 0.88456 | -0.59923 | -9.5771 | 1.0074 | 0.47494 | -16.7121 | 2.6963 | 0.42438 | 0.42422 | 0.42995 | 0.35408 | 0.45321 | 0.43992 | 0.42937
42838.4177 | -221 | 22.899 | 22.8608 | 22.8536 | 22.7761 | 22.4075 | 21.7444 | 22.7197 | 21.8056 | 22.3677 | 22.3712 | 22.3557 | 22.0304 | 21.2482 | 22.2137 | 21.592 | 21.7621 | 21.8964 | 21.0754 | 21.1788 | 21.3858 | 20.4742 | 20.6152 | 20.9064 | 21.8919 | 21.645 | 21.2795 | 20.2812 | 20.3966 | 20.3547 | 22.0836 | 21.6765 | 21.1973 | 22.0032 | 21.75 | 21.3658 | 19.9191 | 20.4366 |  | 20.5139 | 20.0442 | 20.1403 | 19.1403 |  | 16.8067 | 16.7829 | 16.5364 | 16.8014 | 16.899 | 17.4972 | 18.0581 | 16.0518 | 16.8875 | 16.2005 | 16.9357 | 17.9318 | 44.7737 | 46.4572 | 43.7078 | 21.3746 |  |  | 0.39253 | -0.20246 | -65.6204 | 0.37057 | 0.24984 | -197.8532 | 5.3991 | -0.4058 | 0.17426 | 0.17278 | 0.14837 | 8.83 | 9.0594 | 1.9781 | 21.7811 | 22.0057 | 22.2066 | 22.2607 | 22.0925 | 21.412 | 20.2235 | 22.1968 | 22.3708 | 22.4049 | 22.3634 | 21.9804 | 21.2127 | 22.2659 | 17.5879 | 17.249 | 16.3873 | 16.35 | 16.3472 | 17.1093 | 16.8679 | 22.3946 | 22.156 | 21.7089 | 22.09 | 21.8066 | 21.3102 | 21.9471 | 21.5322 | 20.906 | 20.1029 | 20.2973 | 19.8407 | 19.7372 | -0.10379 | -0.033634 | 20.7653 | 22.0671 | 22.3762 | 20.092 | 21.6608 | 22.1253 | 21.9452 | 21.717 | 21.2829 | 21.7787 | 21.4416 | 21.0432 | 20.288 | 20.3351 | 20.2212 | 20.2271 | 20.0671 |  | 20.2243 | 19.9502 | 20.1283 | 19.6869 | 20.0933 | 20.3249 |  | 20.4032 |  |  | 20.31 | 20.3536 | 20.6168 | [5 empty] | 21.9353 | 20.3374 | 21.6713 | 22.0495 | 19.5345 | 21.1689 | 21.791 | 19.3962 | 19.9377 | 21.1701 |  | 19.7965 | 20.9253 | 18.8966 | 19.7121 | 20.8122 | 19.4294 | 20.0477 | 19.0588 | 20.0687 | 19.1445 | 20.181 | 18.8679 | 20.1282 | 21.067 | 19.4228 | 19.7789 | 20.9937 | 18.9617 | 19.8467 | 20.8222 | 18.992 | 20.0966 | 19.3123 | 19.8982 | 18.8687 | 20.0794 | -0.040201 | 20.948 | 0.04885 | 0.015609 | -27.0626 | 3.0968 | -19.07 | -0.09 | 0.74802 | -0.53393 | -9.6125 | 0.72236 | 0.59385 | -16.7117 | 2.7607 | 0.42439 | 0.42442 | 0.43056 | 0.34929 | 0.45452 | 0.43991 | 0.42948
42838.4177 | -220 | 22.9038 | 22.8674 | 22.8522 | 22.7814 | 22.4027 | 21.7417 | 22.7156 | 21.8028 | 22.3751 | 22.3747 | 22.3512 | 22.0304 | 21.2499 | 22.2122 | 21.5943 | 21.7632 | 21.8959 | 21.0784 | 21.1722 | 21.3966 | 20.4755 | 20.6164 | 20.9153 | 21.8883 | 21.6507 | 21.2763 | 20.2867 | 20.3975 | 20.3475 | 22.0806 | 21.6798 | 21.1979 | 22.0009 | 21.7472 | 21.3618 | 19.9214 | 20.429 |  | 20.5091 | 20.0412 | 20.1439 | 19.1578 |  | 16.8051 | 16.7766 | 16.5326 | 16.7905 | 16.8956 | 17.4766 | 18.0302 | 16.0511 | 16.8828 | 16.1809 | 16.9377 | 17.9293 | 44.762 | 46.3305 | 43.6993 | 21.3749 |  |  | 0.38267 | -0.033577 | -66.6087 | 0.36597 | 0.28269 | -197.8552 | 4.9628 | -0.31775 | -0.061789 | -0.12577 | 0.13639 | 8.8287 | 9.0583 | 1.9791 | 21.7834 | 22.0018 | 22.2043 | 22.2637 | 22.0932 | 21.4081 | 20.2225 | 22.1981 | 22.3753 | 22.4 | 22.3546 | 21.9751 | 21.2139 | 22.2627 | 17.6235 | 17.2118 | 16.3701 | 16.3615 | 16.3971 | 17.1106 | 16.866 | 22.3849 | 22.1493 | 21.7015 | 22.0831 | 21.8019 | 21.2976 | 21.9374 | 21.5189 | 20.9015 | 20.0999 | 20.2832 | 19.8368 | 19.7417 | -0.064276 | -0.12645 | 20.7598 | 22.0741 | 22.3707 | 20.0894 | 21.6654 | 22.1199 | 21.9525 | 21.7164 | 21.2743 | 21.7794 | 21.4419 | 21.0404 | 20.2959 | 20.3364 | 20.2132 | 20.2226 | 20.0804 |  | 20.2252 | 19.9409 | 20.1314 | 19.6692 | 20.0826 | 20.313 |  | 20.4117 |  |  | 20.3145 | 20.3581 | 20.6167 | [5 empty] | 21.9398 | 20.3342 | 21.672 | 22.0539 | 19.534 | 21.1758 | 21.7917 | 19.4019 | 19.9431 | 21.1736 |  | 19.8015 | 20.9296 | 18.898 | 19.7172 | 20.8205 | 19.4296 | 20.0516 | 19.0649 | 20.074 | 19.1507 | 20.1778 | 18.8686 | 20.1367 | 21.0678 | 19.424 | 19.7778 | 20.9991 | 18.957 | 19.8552 | 20.8221 | 18.9936 | 20.0979 | 19.3135 | 19.8958 | 18.8729 | 20.0838 | -0.13814 | 20.9471 | 0.04802 | 0.013141 | -27.1179 | 3.0967 | -16.97 | -0.02 | 0.73855 | -0.21744 | -9.6845 | 0.71785 | 0.63167 | -16.7112 | 2.6467 | 0.42405 | 0.42478 | 0.43069 | 0.34548 | 0.45622 | 0.4395 | 0.42926
42838.4177 | -219 | 22.8976 | 22.8664 | 22.8467 | 22.7806 | 22.4034 | 21.7527 | 22.7133 | 21.8071 | 22.3704 | 22.3714 | 22.3533 | 22.0301 | 21.2518 | 22.2152 | 21.6028 | 21.764 | 21.8932 | 21.0802 | 21.1788 | 21.4014 | 20.476 | 20.6166 | 20.9191 | 21.8833 | 21.6484 | 21.2777 | 20.286 | 20.4033 | 20.359 | 22.085 | 21.6706 | 21.1897 | 22.0009 | 21.7423 | 21.3532 | 19.9165 | 20.4298 |  | 20.5021 | 20.0471 | 20.1427 | 19.1679 |  | 16.8076 | 16.776 | 16.5277 | 16.7891 | 16.8973 | 17.4767 | 18.0052 | 16.0721 | 16.8864 | 16.1753 | 16.9363 | 17.9308 | 44.7477 | 46.207 | 43.6956 | 21.3818 |  |  | 0.3393 | 0.001907 | -67.5562 | 0.76878 | 0.22026 | -197.8322 | 4.9221 | -0.38149 | -0.039216 | 0.017315 | 0.13744 | 8.8285 | 9.0584 | 1.9791 | 21.7776 | 22.004 | 22.2004 | 22.2606 | 22.0918 | 21.4093 | 20.2152 | 22.1922 | 22.3737 | 22.3944 | 22.3549 | 21.9818 | 21.2188 | 22.262 | 17.6549 | 17.2082 | 16.3464 | 16.3673 | 16.4511 | 17.1096 | 16.8688 | 22.3904 | 22.1475 | 21.7058 | 22.0837 | 21.7927 | 21.3078 | 21.9323 | 21.5274 | 20.9011 | 20.1005 | 20.2865 | 19.8408 | 19.7398 | -0.0060824 | -0.2109 | 20.7685 | 22.0758 | 22.3822 | 20.0942 | 21.682 | 22.1247 | 21.9601 | 21.7171 | 21.2833 | 21.788 | 21.4494 | 21.0433 | 20.2995 | 20.34 | 20.2287 | 20.2282 | 20.0836 |  | 20.2298 | 19.9439 | 20.1279 | 19.6659 | 20.0873 | 20.3134 |  | 20.4087 |  |  | 20.3182 | 20.3546 | 20.6249 | [5 empty] | 21.9372 | 20.3419 | 21.6712 | 22.0535 | 19.5382 | 21.1763 | 21.7951 | 19.4059 | 19.9459 | 21.177 |  | 19.8033 | 20.9277 | 18.8952 | 19.7077 | 20.8145 | 19.427 | 20.0536 | 19.0724 | 20.0753 | 19.1462 | 20.1796 | 18.8641 | 20.1316 | 21.0713 | 19.4231 | 19.7777 | 21.0014 | 18.9546 | 19.8423 | 20.819 | 18.9952 | 20.0973 | 19.3064 | 19.8928 | 18.8779 | 20.0838 | -0.069695 | 20.9479 | 0.047522 | 0.014019 | -27.0676 | 3.0967 | -5.15 | -0.07 | 0.69546 | 0.051819 | -9.7531 | 1.0404 | 0.55758 | -16.7103 | 2.6358 | 0.42411 | 0.42458 | 0.43094 | 0.34188 | 0.45917 | 0.43905 | 0.42933
42838.4178 | -218 | 22.8983 | 22.8669 | 22.8563 | 22.7814 | 22.4157 | 21.7485 | 22.7255 | 21.813 | 22.3711 | 22.3746 | 22.361 | 22.0362 | 21.2436 | 22.2205 | 21.6044 | 21.7699 | 21.9002 | 21.0878 | 21.1826 | 21.3987 | 20.4814 | 20.624 | 20.9151 | 21.8841 | 21.6554 | 21.2871 | 20.2912 | 20.4054 | 20.3605 | 22.0716 | 21.6704 | 21.1969 | 21.9988 | 21.7368 | 21.3579 | 19.9145 | 20.4251 |  | 20.5085 | 20.0441 | 20.1384 | 19.1767 |  | 16.8103 | 16.7874 | 16.5304 | 16.7853 | 16.8989 | 17.4984 | 18.0225 | 16.0948 | 16.8883 | 16.1597 | 16.9342 | 17.9312 | 44.7259 | 46.0773 | 43.6768 | 21.376 |  |  | 0.37676 | -0.3825 | -68.6812 | 0.53353 | 0.15587 | -197.8466 | 4.5449 | -0.48071 | 0.17737 | 0.13753 | 0.15184 | 8.8286 | 9.0585 | 1.9786 | 21.7778 | 22.0064 | 22.1947 | 22.2611 | 22.0876 | 21.4081 | 20.2201 | 22.1943 | 22.3723 | 22.4026 | 22.3515 | 21.9826 | 21.2161 | 22.2618 | 17.6754 | 17.2059 | 16.3299 | 16.3577 | 16.4721 | 17.1069 | 16.8673 | 22.3895 | 22.1442 | 21.7007 | 22.0823 | 21.7937 | 21.2985 | 21.9389 | 21.5219 | 20.8954 | 20.0946 | 20.2927 | 19.8462 | 19.7347 | -0.020238 | -0.18713 | 20.7658 | 22.0768 | 22.3822 | 20.089 | 21.6724 | 22.1212 | 21.9512 | 21.719 | 21.2838 | 21.78 | 21.4497 | 21.0388 | 20.2958 | 20.3447 | 20.2259 | 20.226 | 20.0871 |  | 20.2305 | 19.9408 | 20.1182 | 19.6575 | 20.0889 | 20.3105 |  | 20.4063 |  |  | 20.322 | 20.3662 | 20.6203 | [5 empty] | 21.9431 | 20.3421 | 21.6765 | 22.0537 | 19.5394 | 21.1797 | 21.7938 | 19.4032 | 19.9396 | 21.1672 |  | 19.8024 | 20.9221 | 18.8938 | 19.7048 | 20.8113 | 19.4322 | 20.0544 | 19.0789 | 20.0767 | 19.1455 | 20.1713 | 18.8695 | 20.1329 | 21.0686 | 19.419 | 19.7761 | 20.995 | 18.9464 | 19.8429 | 20.822 | 18.9926 | 20.0873 | 19.3051 | 19.8942 | 18.8668 | 20.0704 | -0.21958 | 20.9479 | 0.048622 | 0.014847 | -27.0454 | 3.0967 | -14.94 | -0.07 | 0.73284 | -0.7339 | -9.8342 | 0.86676 | 0.46906 | -16.7115 | 2.5329 | 0.42404 | 0.42434 | 0.43123 | 0.33927 | 0.46083 | 0.43874 | 0.42928
42838.4178 | -217 | 22.8978 | 22.8531 | 22.8406 | 22.7757 | 22.4051 | 21.7434 | 22.7117 | 21.806 | 22.367 | 22.3755 | 22.3623 | 22.0241 | 21.2478 | 22.2131 | 21.5967 | 21.7611 | 21.893 | 21.0742 | 21.1766 | 21.3906 | 20.4748 | 20.6078 | 20.8992 | 21.8769 | 21.6445 | 21.2747 | 20.2812 | 20.3958 | 20.3602 | 22.0835 | 21.6779 | 21.2004 | 22.0114 | 21.7429 | 21.3622 | 19.9208 | 20.4397 |  | 20.5173 | 20.0514 | 20.1487 | 19.1805 |  | 16.8201 | 16.7891 | 16.5402 | 16.7895 | 16.9104 | 17.5228 | 18.0464 | 16.0977 | 16.8948 | 16.147 | 16.9397 | 17.9322 | 44.7195 | 45.9342 | 43.6632 | 21.3785 |  |  | 0.46218 | -0.30694 | -69.2766 | 0.3042 | 0.045472 | -197.8585 | 4.581 | -0.37032 | 0.13709 | -0.022757 | 0.12424 | 8.8286 | 9.0582 | 1.9785 | 21.7778 | 21.9965 | 22.1871 | 22.2553 | 22.074 | 21.3997 | 20.2147 | 22.1934 | 22.3618 | 22.3916 | 22.3424 | 21.9715 | 21.2056 | 22.2555 | 17.6803 | 17.2038 | 16.3249 | 16.3525 | 16.4653 | 17.1229 | 16.8775 | 22.388 | 22.1535 | 21.7043 | 22.0856 | 21.7942 | 21.2986 | 21.935 | 21.5201 | 20.8988 | 20.0983 | 20.293 | 19.8416 | 19.7422 | 0.076883 | -0.061213 | 20.7673 | 22.0796 | 22.3841 | 20.0996 | 21.6767 | 22.1233 | 21.9554 | 21.721 | 21.2862 | 21.792 | 21.4543 | 21.052 | 20.3007 | 20.3563 | 20.2259 | 20.2261 | 20.0956 |  | 20.2267 | 19.9377 | 20.1289 | 19.6546 | 20.0834 | 20.3035 |  | 20.4037 |  |  | 20.3323 | 20.3614 | 20.6295 | [5 empty] | 21.9384 | 20.339 | 21.6706 | 22.0537 | 19.5346 | 21.1709 | 21.795 | 19.396 | 19.9309 | 21.175 |  | 19.7943 | 20.9275 | 18.8898 | 19.7033 | 20.8113 | 19.4233 | 20.0539 | 19.0637 | 20.0749 | 19.1385 | 20.1649 | 18.8808 | 20.1347 | 21.0754 | 19.4318 | 19.7771 | 20.9985 | 18.9605 | 19.8544 | 20.8221 | 19.0041 | 20.0985 | 19.3129 | 19.9009 | 18.8749 | 20.0812 | -0.17728 | 20.9479 | 0.049329 | 0.015899 | -27.0748 | 3.0968 | 5.7 | 0.01 | 0.81168 | -0.65742 | -9.8767 | 0.65449 | 0.25336 | -16.7127 | 2.543 | 0.42368 | 0.42479 | 0.43113 | 0.34061 | 0.46258 | 0.43885 | 0.42919
42838.4178 | -216 | 22.9023 | 22.8615 | 22.8531 | 22.7744 | 22.4061 | 21.7464 | 22.7161 | 21.8086 | 22.3681 | 22.3805 | 22.3593 | 22.0302 | 21.2475 | 22.2214 | 21.5914 | 21.7633 | 21.8892 | 21.0749 | 21.1703 | 21.393 | 20.4731 | 20.6168 | 20.9045 | 21.8871 | 21.6465 | 21.2754 | 20.2774 | 20.3943 | 20.351 | 22.0744 | 21.6793 | 21.1937 | 21.9962 | 21.7341 | 21.352 | 19.9151 | 20.4298 |  | 20.5117 | 20.0426 | 20.1363 | 19.1751 |  | 16.8245 | 16.7823 | 16.5359 | 16.7914 | 16.9294 | 17.5459 | 18.0561 | 16.088 | 16.8896 | 16.1635 | 16.9415 | 17.9321 | 44.7195 | 45.7996 | 43.6488 | 21.3789 |  |  | 0.31696 | -0.43968 | -69.8693 | 0.23586 | 0.046788 | -197.8223 | 4.2557 | -0.26912 | -0.066849 | 0.33453 | 0.185 | 8.8292 | 9.0591 | 1.9783 | 21.7731 | 22.0014 | 22.1963 | 22.2619 | 22.0847 | 21.4127 | 20.2225 | 22.2045 | 22.3704 | 22.3967 | 22.3515 | 21.9768 | 21.2073 | 22.2584 | 17.6643 | 17.2091 | 16.3048 | 16.341 | 16.4547 | 17.1147 | 16.8723 | 22.3948 | 22.1539 | 21.7081 | 22.0906 | 21.7971 | 21.3024 | 21.9381 | 21.5261 | 20.9067 | 20.1003 | 20.299 | 19.8362 | 19.7507 | 0.048966 | -0.15764 | 20.77 | 22.0895 | 22.3866 | 20.1044 | 21.6791 | 22.1238 | 21.9596 | 21.7197 | 21.2892 | 21.7972 | 21.4618 | 21.0555 | 20.3082 | 20.3636 | 20.2289 | 20.2294 | 20.1097 |  | 20.2333 | 19.9444 | 20.1345 | 19.6659 | 20.09 | 20.3086 |  | 20.4103 |  |  | 20.3318 | 20.3703 | 20.6241 | [5 empty] | 21.9455 | 20.3379 | 21.6764 | 22.0571 | 19.5353 | 21.1715 | 21.7947 | 19.4014 | 19.9386 | 21.1814 |  | 19.8002 | 20.9301 | 18.8956 | 19.7006 | 20.8123 | 19.4258 | 20.0464 | 19.0676 | 20.0689 | 19.1454 | 20.1792 | 18.8776 | 20.1345 | 21.0698 | 19.43 | 19.7798 | 20.9941 | 18.9537 | 19.8394 | 20.8176 | 18.9983 | 20.0963 | 19.3049 | 19.889 | 18.8666 | 20.0852 | 0.0050615 | 20.9475 | 0.048825 | 0.016183 | -27.1301 | 3.0967 | 0.59 | -0.09 | 0.67216 | -0.78683 | -9.9188 | 0.57629 | 0.25701 | -16.7118 | 2.4512 | 0.4235 | 0.42479 | 0.43103 | 0.34143 | 0.46421 | 0.43881 | 0.42902
42838.4178 | -215 | 22.9063 | 22.8676 | 22.8598 | 22.7823 | 22.4139 | 21.7487 | 22.7256 | 21.8148 | 22.375 | 22.3875 | 22.3627 | 22.033 | 21.2504 | 22.2192 | 21.585 | 21.7458 | 21.8944 | 21.0812 | 21.1636 | 21.3925 | 20.4696 | 20.6136 | 20.9006 | 21.8741 | 21.6371 | 21.2675 | 20.2812 | 20.3838 | 20.3591 | 22.0736 | 21.6833 | 21.1924 | 22.001 | 21.7413 | 21.3563 | 19.9176 | 20.4327 |  | 20.5132 | 20.0481 | 20.1399 | 19.1927 |  | 16.8273 | 16.7937 | 16.5429 | 16.803 | 16.9506 | 17.5625 | 18.0495 | 16.0808 | 16.8933 | 16.251 | 16.9474 | 17.9319 | 44.7125 | 45.657 | 43.6268 | 21.3747 |  |  | 0.42341 | -0.50933 | -69.8916 | 0.52828 | 0.13221 | -197.8381 | 4.399 | -0.19552 | -0.050113 | 0.044169 | 0.1232 | 8.8288 | 9.0586 | 1.979 | 21.7798 | 22.0032 | 22.1979 | 22.2621 | 22.0901 | 21.4113 | 20.2205 | 22.1911 | 22.373 | 22.4003 | 22.3522 | 21.9766 | 21.2108 | 22.2587 | 17.6541 | 17.1963 | 16.2962 | 16.3439 | 16.4477 | 17.1084 | 16.871 | 22.3981 | 22.1505 | 21.7044 | 22.0812 | 21.7997 | 21.3014 | 21.9444 | 21.5213 | 20.9082 | 20.1027 | 20.2944 | 19.8405 | 19.7688 | 0.038742 | 0.062797 | 20.7634 | 22.0812 | 22.3882 | 20.1026 | 21.6745 | 22.1222 | 21.9524 | 21.7112 | 21.2897 | 21.7863 | 21.4539 | 21.0519 | 20.3035 | 20.3584 | 20.228 | 20.2252 | 20.1207 |  | 20.2272 | 19.9459 | 20.1295 | 19.6729 | 20.0883 | 20.3071 |  | 20.4078 |  |  | 20.3215 | 20.3494 | 20.6125 | [5 empty] | 21.9293 | 20.3281 | 21.6627 | 22.0485 | 19.5325 | 21.1596 | 21.7783 | 19.3939 | 19.9451 | 21.172 |  | 19.8022 | 20.9285 | 18.8896 | 19.7069 | 20.803 | 19.4233 | 20.0481 | 19.0507 | 20.0738 | 19.145 | 20.1732 | 18.8819 | 20.1359 | 21.074 | 19.4307 | 19.7748 | 21.0015 | 18.9485 | 19.8363 | 20.8195 | 19.0013 | 20.0977 | 19.3075 | 19.8875 | 18.8688 | 20.0788 | -0.16207 | 20.9483 | 0.046926 | 0.014005 | -27.0376 | 3.0967 | 2.38 | -0.14 | 0.77689 | -0.84688 | -9.9206 | 0.86249 | 0.43205 | -16.713 | 2.4922 | 0.423 | 0.42458 | 0.43078 | 0.34183 | 0.46501 | 0.4384 | 0.4286
42838.4178 | -214 | 22.9018 | 22.864 | 22.86 | 22.7789 | 22.4179 | 21.7422 | 22.7219 | 21.8167 | 22.3736 | 22.3828 | 22.357 | 22.0333 | 21.2504 | 22.222 | 21.6099 | 21.7687 | 21.8882 | 21.084 | 21.1774 | 21.3938 | 20.4852 | 20.6217 | 20.9094 | 21.8848 | 21.653 | 21.2896 | 20.29 | 20.3963 | 20.3754 | 22.0765 | 21.6767 | 21.1913 | 22.002 | 21.7337 | 21.3525 | 19.916 | 20.4227 |  | 20.5103 | 20.0487 | 20.1366 | 19.1926 |  | 16.8331 | 16.7835 | 16.5406 | 16.8074 | 16.9548 | 17.5814 | 18.0567 | 16.0583 | 16.8947 | 16.3119 | 16.9534 | 17.9321 | 44.7022 | 45.52 | 43.6051 | 21.3738 |  |  | 0.35901 | -0.16303 | -69.1997 | 0.58479 | 0.17295 | -197.8447 | 4.9194 | -0.31709 | -0.014891 | 0.32006 | 0.094556 | 8.8283 | 9.0579 | 1.9788 | 21.7798 | 21.9966 | 22.1954 | 22.2537 | 22.0873 | 21.4141 | 20.2145 | 22.1927 | 22.3731 | 22.3965 | 22.3542 | 21.9795 | 21.2028 | 22.2607 | 17.6294 | 17.1859 | 16.2941 | 16.3469 | 16.4383 | 17.1086 | 16.8606 | 22.3937 | 22.1496 | 21.7056 | 22.0847 | 21.7944 | 21.2957 | 21.9371 | 21.5193 | 20.9 | 20.0978 | 20.2988 | 19.8341 | 19.7693 | 0.13508 | 0.025328 | 20.7599 | 22.0735 | 22.3846 | 20.0943 | 21.6693 | 22.121 | 21.9468 | 21.7075 | 21.286 | 21.7868 | 21.4471 | 21.0453 | 20.2981 | 20.3597 | 20.2182 | 20.2205 | 20.1182 |  | 20.2382 | 19.9534 | 20.1369 | 19.6746 | 20.0877 | 20.3136 |  | 20.4096 |  |  | 20.3219 | 20.3558 | 20.6262 | [5 empty] | 21.9285 | 20.3305 | 21.6701 | 22.0487 | 19.5448 | 21.1589 | 21.7849 | 19.3947 | 19.9357 | 21.165 |  | 19.8004 | 20.9196 | 18.8974 | 19.7019 | 20.8014 | 19.4137 | 20.0396 | 19.0415 | 20.0657 | 19.135 | 20.168 | 18.8829 | 20.1272 | 21.0739 | 19.436 | 19.7803 | 20.9965 | 18.9508 | 19.8254 | 20.8092 | 18.9969 | 20.0991 | 19.2967 | 19.8867 | 18.8717 | 20.0745 | -0.085462 | 20.9476 | 0.047854 | 0.013852 | -27.1224 | 3.0967 | 4.41 | -0.03 | 0.71539 | -0.47912 | -9.8712 | 0.90744 | 0.49417 | -16.7138 | 2.6355 | 0.42343 | 0.42462 | 0.43072 | 0.3446 | 0.46404 | 0.43835 | 0.42842
42838.4178 | -213 | 22.9073 | 22.8625 | 22.8554 | 22.7786 | 22.4092 | 21.7478 | 22.7204 | 21.8119 | 22.3659 | 22.3781 | 22.3583 | 22.0271 | 21.25 | 22.2159 | 21.5942 | 21.7662 | 21.8905 | 21.074 | 21.1761 | 21.3877 | 20.4747 | 20.6133 | 20.9097 | 21.8792 | 21.6462 | 21.2822 | 20.2897 | 20.3984 | 20.3726 | 22.0661 | 21.6649 | 21.1819 | 21.9982 | 21.7298 | 21.3479 | 19.9108 | 20.4212 |  | 20.5018 | 20.0408 | 20.1298 | 19.172 |  | 16.8199 | 16.7841 | 16.5303 | 16.7943 | 16.9405 | 17.5683 | 18.0501 | 16.0209 | 16.8835 | 16.3441 | 16.94 | 17.939 | 44.699 | 45.3757 | 43.5906 | 21.3846 |  |  | 0.48058 | -0.19588 | -69.1727 | 0.71227 | 0.1401 | -197.8381 | 4.1848 | -0.2067 | -0.21805 | 0.23089 | 0.24038 | 8.8291 | 9.0587 | 1.9785 | 21.7817 | 22.0008 | 22.2021 | 22.2635 | 22.0874 | 21.4102 | 20.2156 | 22.1927 | 22.3668 | 22.4009 | 22.3506 | 21.9728 | 21.2102 | 22.2629 | 17.6216 | 17.1981 | 16.3011 | 16.3616 | 16.4311 | 17.1181 | 16.863 | 22.3945 | 22.1541 | 21.7148 | 22.0878 | 21.7995 | 21.3076 | 21.9446 | 21.5225 | 20.9086 | 20.0999 | 20.2989 | 19.8416 | 19.7813 | 0.13134 | -0.025456 | 20.7624 | 22.0698 | 22.3691 | 20.0895 | 21.6684 | 22.1079 | 21.9485 | 21.7037 | 21.2812 | 21.779 | 21.4416 | 21.0407 | 20.2891 | 20.3581 | 20.2124 | 20.213 | 20.1114 |  | 20.2342 | 19.9524 | 20.1323 | 19.6704 | 20.084 | 20.3088 |  | 20.4076 |  |  | 20.3298 | 20.3675 | 20.6268 | [5 empty] | 21.9412 | 20.3339 | 21.671 | 22.0497 | 19.5403 | 21.1746 | 21.7941 | 19.4052 | 19.9418 | 21.1744 |  | 19.802 | 20.9249 | 18.8916 | 19.7018 | 20.8165 | 19.4173 | 20.0421 | 19.0442 | 20.0772 | 19.1477 | 20.1735 | 18.8796 | 20.122 | 21.0652 | 19.4366 | 19.7739 | 20.9964 | 18.9375 | 19.8244 | 20.8022 | 18.9969 | 20.0921 | 19.2998 | 19.8819 | 18.8641 | 20.0711 | -0.16078 | 20.9474 | 0.048807 | 0.014702 | -26.9009 | 3.0966 | -5.53 | -0.1 | 0.8277 | -0.52519 | -9.8692 | 1.0015 | 0.44475 | -16.7131 | 2.4307 | 0.42349 | 0.42449 | 0.43071 | 0.34657 | 0.46354 | 0.43875 | 0.42816
42838.4178 | -212 | 22.907 | 22.8652 | 22.8604 | 22.7772 | 22.4116 | 21.7534 | 22.7184 | 21.8039 | 22.3692 | 22.3858 | 22.3597 | 22.033 | 21.2476 | 22.2167 | 21.5948 | 21.7632 | 21.8946 | 21.0708 | 21.176 | 21.3869 | 20.4743 | 20.613 | 20.9088 | 21.8764 | 21.642 | 21.2767 | 20.2895 | 20.3958 | 20.3733 | 22.0721 | 21.6656 | 21.1841 | 21.9994 | 21.732 | 21.3485 | 19.9121 | 20.4158 |  | 20.4995 | 20.0407 | 20.1351 | 19.1646 |  | 16.8294 | 16.8103 | 16.552 | 16.8027 | 16.9482 | 17.5671 | 18.052 | 16.0178 | 16.8984 | 16.3478 | 16.9514 | 17.9393 | 44.7206 | 45.2298 | 43.5769 | 21.376 |  |  | 0.36624 | -0.009265 | -68.9467 | 0.79375 | 0.10987 | -197.8696 | 4.974 | -0.13704 | -0.015475 | 0.25984 | 0.16261 | 8.8289 | 9.0586 | 1.9786 | 21.7804 | 22.0059 | 22.1926 | 22.2618 | 22.0855 | 21.41 | 20.2154 | 22.1896 | 22.3652 | 22.3938 | 22.3557 | 21.9821 | 21.2094 | 22.2603 | 17.6019 | 17.2354 | 16.3017 | 16.3568 | 16.4226 | 17.117 | 16.8774 | 22.3917 | 22.1491 | 21.7114 | 22.0832 | 21.7984 | 21.3074 | 21.9476 | 21.5287 | 20.907 | 20.101 | 20.3029 | 19.8436 | 19.7756 | 0.0354 | 0.044157 | 20.7572 | 22.0674 | 22.367 | 20.0942 | 21.6675 | 22.1063 | 21.9442 | 21.7092 | 21.2741 | 21.7783 | 21.4427 | 21.0393 | 20.294 | 20.3607 | 20.2114 | 20.2085 | 20.1163 |  | 20.2328 | 19.955 | 20.1258 | 19.666 | 20.0858 | 20.3088 |  | 20.4035 |  |  | 20.3321 | 20.3632 | 20.62 | [5 empty] | 21.9351 | 20.3295 | 21.6742 | 22.0531 | 19.531 | 21.1632 | 21.7879 | 19.4017 | 19.9417 | 21.1662 |  | 19.7961 | 20.9153 | 18.8942 | 19.6939 | 20.8052 | 19.4206 | 20.0427 | 19.0281 | 20.0691 | 19.1371 | 20.1656 | 18.8807 | 20.1217 | 21.0679 | 19.4401 | 19.7861 | 21.0037 | 18.9401 | 19.8314 | 20.8106 | 19.0014 | 20.0937 | 19.3058 | 19.8891 | 18.8671 | 20.0706 | -0.20919 | 20.947 | 0.049353 | 0.015979 | -27.0097 | 3.0967 | -2.95 | 0 | 0.72256 | -0.11422 | -9.8536 | 1.0573 | 0.39386 | -16.7144 | 2.65 | 0.42331 | 0.4242 | 0.43089 | 0.34863 | 0.46514 | 0.439 | 0.42836
42838.4178 | -211 | 22.8934 | 22.8628 | 22.8505 | 22.7765 | 22.4091 | 21.7441 | 22.724 | 21.8038 | 22.3685 | 22.3736 | 22.3587 | 22.0289 | 21.2456 | 22.2156 | 21.597 | 21.7618 | 21.8916 | 21.0791 | 21.1802 | 21.3945 | 20.4723 | 20.6153 | 20.9072 | 21.8805 | 21.6457 | 21.2737 | 20.2881 | 20.4008 | 20.3686 | 22.076 | 21.678 | 21.1883 | 21.9977 | 21.7353 | 21.3508 | 19.9191 | 20.419 |  | 20.498 | 20.0436 | 20.1345 | 19.1566 |  | 16.8491 | 16.8157 | 16.5477 | 16.8081 | 16.9348 | 17.5556 | 18.048 | 16.0134 | 16.9071 | 16.4118 | 16.9601 | 17.937 | 44.7446 | 45.0824 | 43.5631 | 21.3818 |  |  | 0.32353 | -0.2294 | -69.6314 | 0.56179 | 0.1539 | -197.7862 | 4.0724 | -0.027304 | -0.043108 | -0.058003 | 0.15914 | 8.8286 | 9.0582 | 1.9778 | 21.7882 | 22.0102 | 22.1983 | 22.2657 | 22.0873 | 21.4171 | 20.2296 | 22.1984 | 22.3753 | 22.4004 | 22.3604 | 21.984 | 21.2158 | 22.2585 | 17.5835 | 17.249 | 16.2949 | 16.3452 | 16.4113 | 17.1126 | 16.8707 | 22.3992 | 22.1572 | 21.7154 | 22.0913 | 21.8072 | 21.3046 | 21.9529 | 21.5361 | 20.9134 | 20.1082 | 20.3019 | 19.8451 | 19.7752 | 0.11837 | -0.016136 | 20.7606 | 22.0741 | 22.3732 | 20.1006 | 21.6699 | 22.1182 | 21.9455 | 21.7141 | 21.2807 | 21.7853 | 21.4469 | 21.0497 | 20.3013 | 20.3662 | 20.2118 | 20.2185 | 20.1248 |  | 20.2277 | 19.9572 | 20.134 | 19.6648 | 20.0836 | 20.3092 |  | 20.4067 |  |  | 20.3354 | 20.3625 | 20.6207 | [5 empty] | 21.939 | 20.3271 | 21.6761 | 22.0458 | 19.5366 | 21.1642 | 21.7856 | 19.3901 | 19.9351 | 21.1676 |  | 19.7907 | 20.9071 | 18.8895 | 19.6782 | 20.7997 | 19.4141 | 20.0458 | 19.0268 | 20.0593 | 19.1295 | 20.1634 | 18.8785 | 20.1228 | 21.0626 | 19.4393 | 19.7814 | 20.9925 | 18.9357 | 19.8279 | 20.8037 | 18.9995 | 20.0983 | 19.303 | 19.8849 | 18.8674 | 20.0664 | -0.02499 | 20.9476 | 0.048395 | 0.015667 | -27.0457 | 3.0967 | 5.75 | -0.03 | 0.67911 | -0.56837 | -9.9025 | 0.88946 | 0.46613 | -16.7106 | 2.3978 | 0.4229 | 0.42442 | 0.43085 | 0.35016 | 0.46512 | 0.43946 | 0.42861
42838.4178 | -210 | 22.8984 | 22.8666 | 22.8522 | 22.7808 | 22.4207 | 21.7475 | 22.729 | 21.8212 | 22.3759 | 22.3818 | 22.357 | 22.0357 | 21.2527 | 22.2199 | 21.5928 | 21.7588 | 21.8944 | 21.0768 | 21.1805 | 21.3908 | 20.4708 | 20.6126 | 20.906 | 21.8838 | 21.6486 | 21.2723 | 20.2851 | 20.4007 | 20.3708 | 22.08 | 21.6687 | 21.1831 | 21.9919 | 21.7348 | 21.3509 | 19.9109 | 20.4078 |  | 20.5068 | 20.0405 | 20.1355 | 19.1403 |  | 16.8587 | 16.8225 | 16.5638 | 16.8137 | 16.9319 | 17.545 | 18.0188 | 16.015 | 16.9162 | 16.4535 | 16.9601 | 17.9372 | 44.7414 | 44.9233 | 43.542 | 21.3796 |  |  | 0.16188 | 0.1169 | -70.5139 | 0.56967 | 0.24524 | -197.8394 | 4.4457 | -0.093016 | -0.0008796 | 0.28754 | 0.0087976 | 8.8284 | 9.058 | 1.9784 | 21.7834 | 22.0059 | 22.1974 | 22.2644 | 22.0902 | 21.4115 | 20.2229 | 22.1977 | 22.3758 | 22.4003 | 22.3555 | 21.9794 | 21.2092 | 22.2596 | 17.5562 | 17.2484 | 16.301 | 16.3309 | 16.3999 | 17.1183 | 16.8736 | 22.3948 | 22.1512 | 21.7105 | 22.0891 | 21.8069 | 21.3019 | 21.9537 | 21.5318 | 20.9092 | 20.0977 | 20.3017 | 19.8405 | 19.7674 | 0.098312 | 0.066601 | 20.7656 | 22.0771 | 22.3688 | 20.1004 | 21.6692 | 22.1242 | 21.9482 | 21.7215 | 21.2811 | 21.7861 | 21.4498 | 21.0522 | 20.3033 | 20.3626 | 20.2153 | 20.2183 | 20.119 |  | 20.2295 | 19.9349 | 20.135 | 19.6551 | 20.0908 | 20.3005 |  | 20.4077 |  |  | 20.3289 | 20.3698 | 20.6185 | [5 empty] | 21.9346 | 20.3224 | 21.6697 | 22.05 | 19.5307 | 21.1661 | 21.7876 | 19.3881 | 19.9387 | 21.1667 |  | 19.7986 | 20.9118 | 18.8905 | 19.68 | 20.7968 | 19.4053 | 20.0412 | 19.0244 | 20.0648 | 19.1286 | 20.161 | 18.8733 | 20.1218 | 21.0612 | 19.4423 | 19.774 | 20.9932 | 18.9394 | 19.8177 | 20.7966 | 18.9947 | 20.0934 | 19.2965 | 19.8817 | 18.8667 | 20.0684 | -0.085462 | 20.9476 | 0.046797 | 0.012909 | -27.0602 | 3.0966 | -15.89 | -0.02 | 0.48038 | 0.40575 | -9.9651 | 0.89569 | 0.58841 | -16.7125 | 2.5053 | 0.42312 | 0.42507 | 0.43136 | 0.35386 | 0.46479 | 0.43964 | 0.42847
42838.4179 | -209 | 22.9014 | 22.8592 | 22.8508 | 22.776 | 22.4087 | 21.7433 | 22.7177 | 21.8043 | 22.3704 | 22.3706 | 22.3509 | 22.0281 | 21.2428 | 22.2106 | 21.5914 | 21.7663 | 21.899 | 21.0814 | 21.1774 | 21.3927 | 20.4762 | 20.6127 | 20.9077 | 21.8841 | 21.6479 | 21.2774 | 20.2884 | 20.3984 | 20.3679 | 22.0621 | 21.6613 | 21.1837 | 21.9906 | 21.733 | 21.3459 | 19.9111 | 20.405 |  | 20.5047 | 20.0346 | 20.1333 | 19.129 |  | 16.8595 | 16.8317 | 16.5685 | 16.8124 | 16.9211 | 17.5326 | 17.9902 | 16.0167 | 16.9104 | 16.4417 | 16.9533 | 17.929 | 44.7249 | 44.7573 | 43.5096 | 21.3836 |  |  | 0.52198 | 0.029503 | -71.1546 | 0.44745 | 0.11316 | -197.8637 | 4.1907 | -0.095644 | 0.02617 | 0.23299 | 0.12771 | 8.8287 | 9.0584 | 1.979 | 21.7778 | 22.0026 | 22.2021 | 22.2676 | 22.0943 | 21.41 | 20.2182 | 22.1994 | 22.3695 | 22.4048 | 22.3584 | 21.9773 | 21.2128 | 22.2673 | 17.5279 | 17.241 | 16.2984 | 16.3219 | 16.3822 | 17.1137 | 16.869 | 22.3839 | 22.1542 | 21.7094 | 22.0804 | 21.7966 | 21.3032 | 21.9428 | 21.5225 | 20.9023 | 20.0946 | 20.2991 | 19.8365 | 19.7639 | 0.22001 | 0.071736 | 20.7631 | 22.0796 | 22.3754 | 20.0939 | 21.6694 | 22.1236 | 21.9505 | 21.7201 | 21.2827 | 21.7921 | 21.4512 | 21.045 | 20.3026 | 20.3616 | 20.2211 | 20.2163 | 20.1229 |  | 20.2278 | 19.9264 | 20.1407 | 19.655 | 20.0824 | 20.3024 |  | 20.4018 |  |  | 20.3303 | 20.3737 | 20.6233 | [5 empty] | 21.9319 | 20.3221 | 21.6665 | 22.0523 | 19.5301 | 21.1679 | 21.7916 | 19.3974 | 19.9407 | 21.1711 |  | 19.7979 | 20.9179 | 18.8976 | 19.6829 | 20.8037 | 19.4083 | 20.0431 | 19.0295 | 20.0693 | 19.14 | 20.1641 | 18.8785 | 20.1248 | 21.0673 | 19.4504 | 19.7769 | 21.0014 | 18.9494 | 19.82 | 20.8066 | 19.003 | 20.1006 | 19.3008 | 19.8865 | 18.871 | 20.0777 | -0.073405 | 20.9477 | 0.048419 | 0.013714 | -27.093 | 3.0967 | -6.06 | -0.15 | 0.86261 | 0.20384 | -10.0105 | 0.79382 | 0.39968 | -16.7132 | 2.4323 | 0.42296 | 0.4255 | 0.43108 | 0.35647 | 0.46453 | 0.43996 | 0.42846
42838.4179 | -208 | 22.898 | 22.8704 | 22.8581 | 22.7781 | 22.4115 | 21.7469 | 22.7205 | 21.8111 | 22.3746 | 22.3756 | 22.362 | 22.0303 | 21.2476 | 22.2173 | 21.5972 | 21.7699 | 21.8954 | 21.0849 | 21.1802 | 21.395 | 20.478 | 20.617 | 20.9082 | 21.8818 | 21.6487 | 21.2825 | 20.2891 | 20.3957 | 20.3669 | 22.0674 | 21.6707 | 21.1884 | 21.9923 | 21.7332 | 21.3538 | 19.9136 | 20.4086 |  | 20.5048 | 20.0419 | 20.1387 | 19.1326 |  | 16.8544 | 16.8194 | 16.5573 | 16.7981 | 16.9136 | 17.5056 | 17.9467 | 16.032 | 16.8906 | 16.4766 | 16.9485 | 17.9358 | 44.6929 | 44.6013 | 43.4931 | 21.3869 |  |  | 0.46021 | -0.23137 | -71.3097 | 0.90875 | 0.12958 | -197.8158 | 3.8155 | -0.24284 | -0.1009 | 0.24663 | 0.24906 | 8.8296 | 9.0592 | 1.9788 | 21.7823 | 22.0024 | 22.2022 | 22.2595 | 22.0979 | 21.4074 | 20.2205 | 22.2014 | 22.3696 | 22.4036 | 22.3611 | 21.9754 | 21.2111 | 22.2687 | 17.4943 | 17.2569 | 16.2874 | 16.3282 | 16.3773 | 17.1157 | 16.8741 | 22.3969 | 22.1521 | 21.7085 | 22.0874 | 21.7996 | 21.3039 | 21.9423 | 21.5207 | 20.9066 | 20.0957 | 20.3005 | 19.8395 | 19.7764 | 0.072361 | -0.004724 | 20.7573 | 22.0785 | 22.3735 | 20.0922 | 21.6694 | 22.1167 | 21.9516 | 21.7195 | 21.278 | 21.7873 | 21.4443 | 21.0511 | 20.2969 | 20.3689 | 20.2168 | 20.2119 | 20.1293 |  | 20.2284 | 19.9307 | 20.1393 | 19.6544 | 20.0908 | 20.3082 |  | 20.4051 |  |  | 20.3284 | 20.377 | 20.6281 | [5 empty] | 21.9395 | 20.3314 | 21.6692 | 22.0468 | 19.5256 | 21.1752 | 21.7878 | 19.3993 | 19.941 | 21.1661 |  | 19.7985 | 20.9189 | 18.898 | 19.6774 | 20.8016 | 19.4058 | 20.0402 | 19.0274 | 20.063 | 19.1363 | 20.159 | 18.8781 | 20.1214 | 21.0638 | 19.4439 | 19.7681 | 20.9944 | 18.9459 | 19.8185 | 20.803 | 19.0031 | 20.0971 | 19.2962 | 19.8776 | 18.86 | 20.0734 | -0.084906 | 20.946 | 0.048911 | 0.014585 | -27.1006 | 3.0967 | -0.34 | -0.14 | 0.80996 | -0.57082 | -10.0211 | 1.1313 | 0.42769 | -16.7104 | 2.3208 | 0.4228 | 0.42533 | 0.43138 | 0.36043 | 0.46635 | 0.43994 | 0.42815
42838.4179 | -207 | 22.9019 | 22.87 | 22.8554 | 22.7836 | 22.4092 | 21.7496 | 22.7233 | 21.8147 | 22.3755 | 22.3799 | 22.3601 | 22.0274 | 21.2526 | 22.2201 | 21.596 | 21.7641 | 21.8878 | 21.0833 | 21.1799 | 21.3972 | 20.4728 | 20.6201 | 20.9046 | 21.8893 | 21.6484 | 21.2829 | 20.291 | 20.3966 | 20.3615 | 22.0681 | 21.6642 | 21.1859 | 21.9913 | 21.7257 | 21.3522 | 19.9086 | 20.4 |  | 20.4979 | 20.0357 | 20.136 | 19.1384 |  | 16.8589 | 16.8161 | 16.5624 | 16.7947 | 16.9125 | 17.4903 | 17.9338 | 16.0824 | 16.9007 | 16.4759 | 16.9595 | 17.9408 | 44.6399 | 44.4501 | 43.4779 | 21.3842 |  |  | 0.40501 | -0.044093 | -72.0857 | 0.72278 | 0.18478 | -197.8289 | 3.7051 | -0.070672 | -0.033572 | 0.27642 | 0.23187 | 8.8279 | 9.0577 | 1.9785 | 21.789 | 22.0049 | 22.2017 | 22.2616 | 22.0939 | 21.4133 | 20.2239 | 22.1938 | 22.3623 | 22.408 | 22.351 | 21.9824 | 21.2216 | 22.2648 | 17.4698 | 17.2613 | 16.2951 | 16.3484 | 16.3895 | 17.1237 | 16.881 | 22.3905 | 22.1413 | 21.7071 | 22.0825 | 21.7978 | 21.3023 | 21.9401 | 21.5199 | 20.9025 | 20.0933 | 20.2928 | 19.8369 | 19.7778 | 0.083371 | 0.16512 | 20.7555 | 22.0697 | 22.3705 | 20.0913 | 21.6702 | 22.1136 | 21.9546 | 21.713 | 21.2771 | 21.7835 | 21.4398 | 21.0405 | 20.2913 | 20.3693 | 20.2135 | 20.2063 | 20.1168 |  | 20.2353 | 19.9134 | 20.1335 | 19.647 | 20.0849 | 20.2992 |  | 20.4072 |  |  | 20.3289 | 20.3759 | 20.6236 | [5 empty] | 21.9427 | 20.3213 | 21.6718 | 22.0504 | 19.5259 | 21.168 | 21.7842 | 19.3971 | 19.9374 | 21.165 |  | 19.7988 | 20.9242 | 18.9009 | 19.6784 | 20.8068 | 19.4007 | 20.0429 | 19.0254 | 20.0694 | 19.1333 | 20.1559 | 18.8724 | 20.1191 | 21.0629 | 19.4318 | 19.768 | 20.9905 | 18.9452 | 19.8193 | 20.8029 | 18.995 | 20.089 | 19.2889 | 19.872 | 18.8557 | 20.0701 | -0.1272 | 20.9465 | 0.049698 | 0.015747 | -26.9627 | 3.0966 | 13.81 | -0.12 | 0.75983 | -0.24919 | -10.0755 | 1.0089 | 0.51071 | -16.7105 | 2.2869 | 0.42338 | 0.42562 | 0.43139 | 0.36409 | 0.4663 | 0.43961 | 0.42803
42838.4179 | -206 | 22.9032 | 22.8672 | 22.8574 | 22.7864 | 22.4158 | 21.7541 | 22.723 | 21.8146 | 22.3739 | 22.3877 | 22.3635 | 22.0334 | 21.2569 | 22.217 | 21.5992 | 21.7617 | 21.8931 | 21.0782 | 21.1744 | 21.3933 | 20.4749 | 20.615 | 20.9077 | 21.8856 | 21.6489 | 21.2782 | 20.2902 | 20.3967 | 20.3592 | 22.0773 | 21.6771 | 21.1915 | 22.0004 | 21.7369 | 21.3569 | 19.9172 | 20.4116 |  | 20.5107 | 20.0415 | 20.1423 | 19.151 |  | 16.8709 | 16.8352 | 16.5681 | 16.8073 | 16.9042 | 17.484 | 17.9102 | 16.1412 | 16.9133 | 16.4942 | 16.9792 | 17.9375 | 44.5779 | 44.2869 | 43.4498 | 21.3814 |  |  | 0.52461 | -0.39171 | -72.4077 | 0.6413 | 0.17821 | -197.8657 | 3.9936 | -0.16004 | -0.11433 | 0.14991 | 0.18952 | 8.8296 | 9.0596 | 1.9785 | 21.7846 | 22.0143 | 22.2076 | 22.2615 | 22.0905 | 21.4072 | 20.2252 | 22.2009 | 22.3648 | 22.3994 | 22.3537 | 21.9816 | 21.2096 | 22.2636 | 17.4368 | 17.2627 | 16.2833 | 16.348 | 16.392 | 17.1217 | 16.8798 | 22.3975 | 22.1487 | 21.709 | 22.0821 | 21.801 | 21.3054 | 21.9453 | 21.5243 | 20.9028 | 20.0964 | 20.2975 | 19.8503 | 19.7889 | 0.13331 | -0.068631 | 20.7557 | 22.0691 | 22.3768 | 20.1018 | 21.6693 | 22.1174 | 21.9518 | 21.7076 | 21.2794 | 21.7878 | 21.4423 | 21.0418 | 20.2926 | 20.3678 | 20.2118 | 20.2061 | 20.1164 |  | 20.2294 | 19.9293 | 20.1378 | 19.6646 | 20.0895 | 20.3054 |  | 20.4068 |  |  | 20.3332 | 20.381 | 20.622 | [5 empty] | 21.9383 | 20.3181 | 21.6804 | 22.0512 | 19.5273 | 21.1748 | 21.7867 | 19.3896 | 19.9336 | 21.1695 |  | 19.7951 | 20.9174 | 18.9016 | 19.6761 | 20.8028 | 19.405 | 20.0377 | 19.0171 | 20.0677 | 19.1307 | 20.1569 | 18.8703 | 20.1135 | 21.0629 | 19.4274 | 19.7685 | 20.9938 | 18.9376 | 19.8224 | 20.803 | 19.0017 | 20.0931 | 19.2959 | 19.874 | 18.8591 | 20.0713 | 0.05459 | 20.9479 | 0.049052 | 0.015464 | -27.0913 | 3.0967 | 9.77 | -0.1 | 0.86476 | -0.74274 | -10.0983 | 0.95036 | 0.50154 | -16.7119 | 2.3742 | 0.42319 | 0.42532 | 0.43105 | 0.36752 | 0.46747 | 0.43955 | 0.42783
42838.4179 | -205 | 22.9075 | 22.8651 | 22.8613 | 22.781 | 22.4087 | 21.7507 | 22.7201 | 21.8129 | 22.3751 | 22.381 | 22.3621 | 22.0426 | 21.2521 | 22.2172 | 21.6037 | 21.7709 | 21.9034 | 21.0812 | 21.1803 | 21.4001 | 20.4846 | 20.6239 | 20.9152 | 21.8898 | 21.6482 | 21.2811 | 20.2932 | 20.4075 | 20.3616 | 22.0694 | 21.6751 | 21.1901 | 21.9941 | 21.7329 | 21.3556 | 19.9143 | 20.4094 |  | 20.5106 | 20.0366 | 20.1362 | 19.1494 |  | 16.8729 | 16.8337 | 16.5626 | 16.7885 | 16.8905 | 17.4669 | 17.8881 | 16.1706 | 16.9098 | 16.6026 | 16.9787 | 17.9259 | 44.5021 | 44.1307 | 43.4084 | 21.3756 |  |  | 0.19802 | -0.26357 | -73.5689 | 0.52105 | 0.031672 | -197.8434 | 3.552 | -0.039132 | -0.35778 | 0.16376 | 0.06435 | 8.8296 | 9.0595 | 1.9781 | 21.7898 | 22.0126 | 22.1991 | 22.2684 | 22.0928 | 21.4165 | 20.2257 | 22.1944 | 22.3824 | 22.406 | 22.3561 | 21.9878 | 21.2159 | 22.2755 | 17.4043 | 17.2635 | 16.2678 | 16.3436 | 16.3787 | 17.1203 | 16.8858 | 22.3976 | 22.1541 | 21.7053 | 22.0843 | 21.8064 | 21.3002 | 21.9404 | 21.5237 | 20.9045 | 20.0941 | 20.3065 | 19.8433 | 19.7904 | 0.14432 | 0.12309 | 20.7505 | 22.0712 | 22.377 | 20.103 | 21.6672 | 22.1123 | 21.9521 | 21.7133 | 21.2831 | 21.7851 | 21.4499 | 21.048 | 20.287 | 20.3758 | 20.2108 | 20.208 | 20.1297 |  | 20.2344 | 19.9242 | 20.1329 | 19.6623 | 20.0855 | 20.3035 |  | 20.4021 |  |  | 20.3375 | 20.3722 | 20.6284 | [5 empty] | 21.931 | 20.3204 | 21.679 | 22.0449 | 19.5262 | 21.1725 | 21.7826 | 19.389 | 19.9373 | 21.1661 |  | 19.808 | 20.9099 | 18.9018 | 19.6716 | 20.8007 | 19.404 | 20.0453 | 19.0259 | 20.0669 | 19.1379 | 20.1663 | 18.8667 | 20.123 | 21.0683 | 19.442 | 19.7719 | 20.9946 | 18.9445 | 19.821 | 20.8035 | 19.0031 | 20.0917 | 19.2997 | 19.8869 | 18.862 | 20.0693 | -0.074518 | 20.9478 | 0.047086 | 0.013664 | -27.0601 | 3.0966 | -2.61 | -0.17 | 0.5313 | -0.60926 | -10.1789 | 0.85663 | 0.21143 | -16.7105 | 2.239 | 0.42299 | 0.42529 | 0.43098 | 0.37098 | 0.4699 | 0.4395 | 0.42771
42838.4179 | -204 | 22.9045 | 22.872 | 22.8594 | 22.7909 | 22.4099 | 21.7514 | 22.7206 | 21.8082 | 22.3695 | 22.3782 | 22.3623 | 22.0347 | 21.2546 | 22.2145 | 21.5893 | 21.7654 | 21.8934 | 21.0739 | 21.1695 | 21.3897 | 20.4755 | 20.6161 | 20.8991 | 21.8894 | 21.6377 | 21.2721 | 20.2862 | 20.405 | 20.3439 | 22.059 | 21.6699 | 21.1855 | 21.9932 | 21.7443 | 21.3537 | 19.9088 | 20.4076 |  | 20.4991 | 20.0442 | 20.1361 | 19.1482 |  | 16.8661 | 16.8217 | 16.5542 | 16.7854 | 16.8895 | 17.4408 | 17.8806 | 16.1758 | 16.9041 | 16.6772 | 16.9668 | 17.9384 | 44.4435 | 43.9737 | 43.3806 | 21.3902 |  |  | 0.38464 | -0.14857 | -74.8075 | 0.37254 | 0.10461 | -197.8401 | 2.496 | -0.10024 | -0.15461 | 0.14991 | 0.22042 | 8.8288 | 9.0585 | 1.979 | 21.7869 | 22.0112 | 22.1951 | 22.2626 | 22.099 | 21.4096 | 20.2207 | 22.1931 | 22.3764 | 22.4085 | 22.3595 | 21.9857 | 21.2094 | 22.2686 | 17.377 | 17.2475 | 16.2688 | 16.3261 | 16.3647 | 17.1205 | 16.8904 | 22.3886 | 22.1522 | 21.7015 | 22.0813 | 21.7948 | 21.2945 | 21.9437 | 21.5276 | 20.8995 | 20.095 | 20.2963 | 19.8475 | 19.7936 | 0.18894 | 0.039783 | 20.7569 | 22.0735 | 22.3746 | 20.1 | 21.6684 | 22.1157 | 21.9514 | 21.7164 | 21.2865 | 21.7853 | 21.4463 | 21.0515 | 20.292 | 20.3756 | 20.215 | 20.2076 | 20.1328 |  | 20.2335 | 19.9242 | 20.1328 | 19.6741 | 20.0914 | 20.3021 |  | 20.4166 |  |  | 20.3384 | 20.3787 | 20.6257 | [5 empty] | 21.9317 | 20.3134 | 21.6718 | 22.0475 | 19.5308 | 21.1697 | 21.7876 | 19.3819 | 19.9386 | 21.158 |  | 19.8034 | 20.9067 | 18.8952 | 19.6666 | 20.7969 | 19.3968 | 20.0417 | 19.0181 | 20.0723 | 19.1294 | 20.1618 | 18.8615 | 20.116 | 21.058 | 19.4391 | 19.767 | 20.9916 | 18.9375 | 19.8145 | 20.7986 | 19.0019 | 20.0838 | 19.2928 | 19.8828 | 18.8581 | 20.0696 | -0.029812 | 20.946 | 0.048315 | 0.014295 | -27.0902 | 3.0966 | 8.47 | -0.09 | 0.74045 | -0.45742 | -10.264 | 0.72432 | 0.38424 | -16.7096 | 1.8768 | 0.42287 | 0.42529 | 0.43085 | 0.37402 | 0.47031 | 0.43934 | 0.42765
42838.4179 | -203 | 22.9073 | 22.8527 | 22.8485 | 22.775 | 22.4052 | 21.7391 | 22.7188 | 21.8059 | 22.3643 | 22.3806 | 22.361 | 22.0245 | 21.2454 | 22.2157 | 21.5972 | 21.7661 | 21.8931 | 21.0728 | 21.1753 | 21.3934 | 20.4722 | 20.6186 | 20.9094 | 21.8792 | 21.6444 | 21.2806 | 20.2833 | 20.4038 | 20.3433 | 22.0713 | 21.6683 | 21.1948 | 22.005 | 21.7363 | 21.353 | 19.9287 | 20.4114 |  | 20.504 | 20.0472 | 20.1461 | 19.1604 |  | 16.8608 | 16.8213 | 16.5613 | 16.7774 | 16.8658 | 17.4321 | 17.8784 | 16.1933 | 16.8952 | 16.6618 | 16.9763 | 17.9374 | 44.3832 | 43.829 | 43.337 | 21.3858 |  |  | 0.3485 | -0.015837 | -74.6807 | 0.59136 | 0.26692 | -197.8394 | 3.2129 | -0.13836 | -0.24627 | 0.31922 | 0.099243 | 8.8291 | 9.0588 | 1.9787 | 21.7757 | 22.0069 | 22.198 | 22.2611 | 22.0934 | 21.3972 | 20.2209 | 22.1932 | 22.3684 | 22.4065 | 22.3533 | 21.9866 | 21.2096 | 22.265 | 17.3694 | 17.2361 | 16.2831 | 16.3247 | 16.3582 | 17.1309 | 16.8969 | 22.3853 | 22.1504 | 21.7027 | 22.0708 | 21.7948 | 21.2966 | 21.9409 | 21.5189 | 20.8896 | 20.0881 | 20.2895 | 19.8429 | 19.7789 | 0.10087 | 0.22903 | 20.755 | 22.0751 | 22.3715 | 20.097 | 21.6674 | 22.1119 | 21.9508 | 21.7141 | 21.2805 | 21.7798 | 21.4414 | 21.0427 | 20.2932 | 20.3655 | 20.2191 | 20.2012 | 20.1391 |  | 20.2366 | 19.9235 | 20.1429 | 19.6735 | 20.0854 | 20.3025 |  | 20.4055 |  |  | 20.3419 | 20.3776 | 20.6167 | [5 empty] | 21.9361 | 20.3186 | 21.671 | 22.0561 | 19.5258 | 21.1588 | 21.7838 | 19.3856 | 19.9356 | 21.1541 |  | 19.8068 | 20.9083 | 18.8861 | 19.6702 | 20.8026 | 19.4041 | 20.0397 | 19.0222 | 20.0733 | 19.1301 | 20.1636 | 18.8522 | 20.1245 | 21.0567 | 19.4389 | 19.7656 | 20.9865 | 18.9385 | 19.8194 | 20.7908 | 19.0015 | 20.09 | 19.2931 | 19.8849 | 18.854 | 20.07 | -0.10698 | 20.9466 | 0.048764 | 0.015892 | -27.0491 | 3.0966 | -7.71 | -0.19 | 0.7048 | -0.14934 | -10.2553 | 0.91258 | 0.61375 | -16.7093 | 2.1294 | 0.4228 | 0.42565 | 0.43067 | 0.37609 | 0.46948 | 0.43967 | 0.42783
42838.4179 | -202 | 22.9027 | 22.8733 | 22.8563 | 22.7859 | 22.4165 | 21.7547 | 22.7236 | 21.8095 | 22.3741 | 22.3897 | 22.3677 | 22.0369 | 21.2543 | 22.2206 | 21.5917 | 21.7542 | 21.8918 | 21.0698 | 21.1675 | 21.3885 | 20.4673 | 20.6055 | 20.9013 | 21.8754 | 21.6354 | 21.2641 | 20.2811 | 20.3879 | 20.3409 | 22.0641 | 21.6738 | 21.1849 | 21.9905 | 21.7224 | 21.3517 | 19.9121 | 20.397 |  | 20.5017 | 20.0288 | 20.1396 | 19.1637 |  | 16.8614 | 16.8132 | 16.5546 | 16.7661 | 16.8547 | 17.4107 | 17.855 | 16.2064 | 16.8985 | 16.6289 | 16.978 | 17.9306 | 44.3301 | 43.6663 | 43.294 | 21.3869 |  |  | 0.4221 | -0.10652 | -75.0776 | 0.57756 | 0.24326 | -197.8512 | 2.8797 | -0.29869 | -0.2739 | 0.12725 | -0.077482 | 8.8289 | 9.0587 | 1.9784 | 21.7823 | 22.0029 | 22.2038 | 22.2636 | 22.0874 | 21.4065 | 20.221 | 22.1956 | 22.3734 | 22.4039 | 22.351 | 21.9819 | 21.2104 | 22.2608 | 17.347 | 17.2232 | 16.2838 | 16.3027 | 16.333 | 17.1236 | 16.8835 | 22.3923 | 22.1562 | 21.7076 | 22.0834 | 21.7986 | 21.3056 | 21.9437 | 21.5223 | 20.8995 | 20.0983 | 20.2928 | 19.8525 | 19.7867 | 0.11443 | -0.091265 | 20.7453 | 22.0712 | 22.3709 | 20.1032 | 21.6697 | 22.1145 | 21.9512 | 21.7095 | 21.2783 | 21.7789 | 21.4415 | 21.0432 | 20.2906 | 20.3535 | 20.2187 | 20.2006 | 20.1421 |  | 20.2325 | 19.9379 | 20.1418 | 19.6792 | 20.0826 | 20.3013 |  | 20.401 |  |  | 20.3457 | 20.3768 | 20.6282 | [5 empty] | 21.9378 | 20.3168 | 21.6682 | 22.0547 | 19.522 | 21.1685 | 21.7856 | 19.3837 | 19.9369 | 21.1579 |  | 19.8104 | 20.922 | 18.8948 | 19.6818 | 20.8079 | 19.407 | 20.0406 | 19.0211 | 20.0709 | 19.1436 | 20.1659 | 18.8608 | 20.1247 | 21.0602 | 19.4363 | 19.7663 | 20.9847 | 18.9387 | 19.8227 | 20.8059 | 19.0134 | 20.0907 | 19.2985 | 19.8819 | 18.8629 | 20.0711 | -0.29174 | 20.9463 | 0.049734 | 0.015631 | -27.0774 | 3.0966 | -2.61 | -0.06 | 0.77566 | -0.3873 | -10.2824 | 0.90186 | 0.5859 | -16.7092 | 2.0159 | 0.42258 | 0.42521 | 0.43042 | 0.37772 | 0.46785 | 0.43903 | 0.42796
42838.418 | -201 | 22.8977 | 22.8682 | 22.8501 | 22.7786 | 22.4045 | 21.7474 | 22.7196 | 21.803 | 22.3704 | 22.3812 | 22.3614 | 22.0234 | 21.2431 | 22.2146 | 21.6034 | 21.7664 | 21.9014 | 21.0802 | 21.1799 | 21.3936 | 20.4825 | 20.6258 | 20.9096 | 21.8905 | 21.6462 | 21.277 | 20.2922 | 20.3945 | 20.3413 | 22.0722 | 21.676 | 21.1912 | 22.0012 | 21.7304 | 21.3587 | 19.9169 | 20.4051 |  | 20.5135 | 20.0377 | 20.1437 | 19.1634 |  | 16.8747 | 16.8247 | 16.5533 | 16.7693 | 16.8498 | 17.4065 | 17.8362 | 16.2201 | 16.9037 | 16.6338 | 16.9788 | 17.9262 | 44.2827 | 43.5224 | 43.2442 | 21.3817 |  |  | 0.3623 | -0.095349 | -75.9174 | 0.32851 | 0.21304 | -197.7928 | 2.4171 | -0.10418 | -0.34766 | 0.1625 | 0.15584 | 8.8287 | 9.0585 | 1.9784 | 21.7833 | 21.9974 | 22.1952 | 22.2492 | 22.0795 | 21.4074 | 20.2121 | 22.1909 | 22.3639 | 22.4001 | 22.3489 | 21.976 | 21.2079 | 22.2635 | 17.3319 | 17.219 | 16.2891 | 16.3183 | 16.3305 | 17.1283 | 16.8924 | 22.3927 | 22.1457 | 21.7097 | 22.0892 | 21.7965 | 21.3025 | 21.9442 | 21.5211 | 20.9012 | 20.092 | 20.2972 | 19.8448 | 19.7792 | 0.19012 | -0.032303 | 20.7555 | 22.08 | 22.3744 | 20.1055 | 21.6737 | 22.1157 | 21.9487 | 21.7135 | 21.2776 | 21.7847 | 21.4484 | 21.045 | 20.2904 | 20.3537 | 20.22 | 20.2033 | 20.1404 |  | 20.2188 | 19.9382 | 20.131 | 19.684 | 20.0768 | 20.2925 |  | 20.3944 |  |  | 20.3517 | 20.3732 | 20.6315 | [5 empty] | 21.9471 | 20.3296 | 21.6783 | 22.0553 | 19.5241 | 21.1772 | 21.7919 | 19.384 | 19.9379 | 21.1505 |  | 19.8041 | 20.9119 | 18.8884 | 19.6733 | 20.8027 | 19.4014 | 20.0417 | 19.0206 | 20.0701 | 19.1388 | 20.1627 | 18.8483 | 20.1206 | 21.0534 | 19.4285 | 19.7633 | 20.9864 | 18.938 | 19.8202 | 20.7907 | 19.0011 | 20.0731 | 19.2859 | 19.8754 | 18.8465 | 20.0608 | -0.023135 | 20.9465 | 0.04912 | 0.016698 | -27.0096 | 3.0966 | 10.52 | 0.05 | 0.71862 | -0.36644 | -10.3399 | 0.68018 | 0.54829 | -16.7066 | 1.8469 | 0.42217 | 0.42484 | 0.43009 | 0.37995 | 0.4683 | 0.4392 | 0.42796
42838.418 | -200 | 22.8914 | 22.8582 | 22.8488 | 22.7759 | 22.3972 | 21.7464 | 22.7148 | 21.802 | 22.3658 | 22.3781 | 22.3593 | 22.0255 | 21.2408 | 22.2111 | 21.6008 | 21.769 | 21.8981 | 21.0808 | 21.1751 | 21.4018 | 20.4778 | 20.6147 | 20.9051 | 21.8904 | 21.6501 | 21.2739 | 20.2892 | 20.4022 | 20.3446 | 22.0713 | 21.6787 | 21.1924 | 21.9982 | 21.7316 | 21.3567 | 19.9169 | 20.406 |  | 20.5085 | 20.0427 | 20.1438 | 19.1701 |  | 16.8569 | 16.8025 | 16.5357 | 16.7475 | 16.8307 | 17.383 | 17.8134 | 16.1989 | 16.8931 | 16.6135 | 16.9685 | 17.9324 | 44.2326 | 43.3901 | 43.2008 | 21.3839 |  |  | 0.38727 | -0.11441 | -75.4935 | 0.32457 | 0.17952 | -197.8913 | 3.2168 | -0.28621 | -0.056535 | 0.38551 | 0.10254 | 8.829 | 9.0587 | 1.9779 | 21.7911 | 22.0091 | 22.1959 | 22.2634 | 22.0774 | 21.4045 | 20.2203 | 22.1984 | 22.367 | 22.4051 | 22.3538 | 21.9741 | 21.2176 | 22.2622 | 17.3136 | 17.2335 | 16.2834 | 16.3266 | 16.3356 | 17.1355 | 16.9006 | 22.3908 | 22.148 | 21.7127 | 22.0761 | 21.7973 | 21.3 | 21.9414 | 21.5234 | 20.9026 | 20.0926 | 20.2944 | 19.8461 | 19.7709 | 0.17007 | 0.15067 | 20.7638 | 22.0842 | 22.3749 | 20.1119 | 21.6758 | 22.1134 | 21.9525 | 21.718 | 21.2764 | 21.7874 | 21.4509 | 21.0472 | 20.2886 | 20.3644 | 20.2243 | 20.2011 | 20.1456 |  | 20.2286 | 19.9367 | 20.1295 | 19.6911 | 20.0756 | 20.2891 |  | 20.3963 |  |  | 20.3333 | 20.376 | 20.6159 | [5 empty] | 21.9385 | 20.3167 | 21.673 | 22.0473 | 19.519 | 21.1522 | 21.7848 | 19.3809 | 19.9356 | 21.1584 |  | 19.806 | 20.9108 | 18.8936 | 19.6856 | 20.7985 | 19.4072 | 20.042 | 19.0341 | 20.0731 | 19.148 | 20.1724 | 18.8457 | 20.1293 | 21.0568 | 19.4313 | 19.772 | 20.9965 | 18.9347 | 19.8249 | 20.8019 | 19.0131 | 20.0821 | 19.2937 | 19.8743 | 18.8506 | 20.0776 | -0.024433 | 20.9455 | 0.048462 | 0.015544 | -27.0087 | 3.0966 | -10.76 | -0.09 | 0.74297 | -0.40138 | -10.3106 | 0.67606 | 0.5033 | -16.7101 | 2.1305 | 0.42235 | 0.42483 | 0.42985 | 0.38281 | 0.46989 | 0.43901 | 0.4282
42838.418 | -199 | 22.8936 | 22.8575 | 22.8466 | 22.7734 | 22.3987 | 21.745 | 22.7158 | 21.7985 | 22.3676 | 22.3712 | 22.35 | 22.022 | 21.2435 | 22.2086 | 21.5976 | 21.7657 | 21.8872 | 21.076 | 21.1771 | 21.3956 | 20.476 | 20.6161 | 20.9055 | 21.884 | 21.6436 | 21.2812 | 20.2845 | 20.4117 | 20.3433 | 22.0653 | 21.6775 | 21.1906 | 21.993 | 21.7391 | 21.3527 | 19.9207 | 20.4065 |  | 20.5038 | 20.0451 | 20.1397 | 19.1746 |  | 16.8539 | 16.805 | 16.53 | 16.7444 | 16.8249 | 17.3713 | 17.8199 | 16.1785 | 16.8944 | 16.6455 | 16.9712 | 17.9384 | 44.1723 | 43.2661 | 43.1461 | 21.3865 |  |  | 0.66852 | -0.38908 | -75.8044 | 0.40605 | 0.2183 | -197.8302 | 2.7477 | -0.25401 | 0.020332 | 0.1327 | 0.17059 | 8.8285 | 9.0583 | 1.978 | 21.7777 | 22.0009 | 22.1948 | 22.2672 | 22.0889 | 21.4063 | 20.2221 | 22.1935 | 22.3653 | 22.4037 | 22.3477 | 21.9776 | 21.2134 | 22.2543 | 17.304 | 17.236 | 16.2876 | 16.3383 | 16.3408 | 17.1405 | 16.9045 | 22.3888 | 22.1538 | 21.7136 | 22.0894 | 21.8084 | 21.3046 | 21.9407 | 21.5376 | 20.9137 | 20.1026 | 20.3066 | 19.8502 | 19.7692 | 0.13193 | 0.084099 | 20.767 | 22.0812 | 22.3731 | 20.1084 | 21.6683 | 22.117 | 21.9556 | 21.7138 | 21.2825 | 21.7852 | 21.4474 | 21.0421 | 20.2945 | 20.3718 | 20.2269 | 20.197 | 20.1512 |  | 20.2292 | 19.9282 | 20.1399 | 19.6977 | 20.0828 | 20.3039 |  | 20.4062 |  |  | 20.3361 | 20.3698 | 20.6137 | [5 empty] | 21.9305 | 20.3203 | 21.6707 | 22.0478 | 19.5221 | 21.1545 | 21.7824 | 19.3786 | 19.929 | 21.1547 |  | 19.8049 | 20.9018 | 18.889 | 19.6702 | 20.7952 | 19.399 | 20.0448 | 19.0226 | 20.0612 | 19.1387 | 20.1647 | 18.8417 | 20.1148 | 21.0521 | 19.4323 | 19.7665 | 20.989 | 18.9173 | 19.81 | 20.785 | 19.0107 | 20.0759 | 19.2972 | 19.8784 | 18.8485 | 20.0737 | -0.031111 | 20.9463 | 0.047295 | 0.013809 | -26.9703 | 3.0965 | 4.32 | 0 | 0.97616 | -0.7402 | -10.3319 | 0.75618 | 0.55498 | -16.7071 | 1.969 | 0.42222 | 0.42542 | 0.42991 | 0.38447 | 0.46987 | 0.43901 | 0.42859
42838.418 | -198 | 22.9027 | 22.8591 | 22.8517 | 22.7825 | 22.4131 | 21.7501 | 22.7164 | 21.805 | 22.3701 | 22.3741 | 22.354 | 22.0273 | 21.2464 | 22.2074 | 21.5931 | 21.7667 | 21.8934 | 21.0817 | 21.1737 | 21.3999 | 20.4793 | 20.6154 | 20.9085 | 21.8831 | 21.6502 | 21.2849 | 20.2834 | 20.4068 | 20.343 | 22.0639 | 21.6722 | 21.1905 | 21.9953 | 21.7407 | 21.353 | 19.9167 | 20.413 |  | 20.5155 | 20.0458 | 20.1408 | 19.1726 |  | 16.8516 | 16.8069 | 16.5283 | 16.7441 | 16.8225 | 17.3804 | 17.8234 | 16.1541 | 16.8938 | 16.7304 | 16.9735 | 17.9418 | 44.1169 | 43.1421 | 43.0891 | 21.3877 |  |  | 0.41487 | -0.44362 | -76.4884 | 0.24177 | 0.15258 | -197.8545 | 2.6714 | -0.38937 | 0.061976 | 0.16585 | 0.14542 | 8.829 | 9.0587 | 1.979 | 21.7823 | 22.0012 | 22.1906 | 22.2485 | 22.0806 | 21.4007 | 20.2139 | 22.1915 | 22.3655 | 22.3994 | 22.3491 | 21.9754 | 21.2063 | 22.26 | 17.2781 | 17.2307 | 16.2947 | 16.3357 | 16.3469 | 17.1385 | 16.909 | 22.3899 | 22.1516 | 21.7019 | 22.0834 | 21.7971 | 21.2978 | 21.9362 | 21.5297 | 20.9014 | 20.0957 | 20.2995 | 19.8478 | 19.765 | 0.079439 | 0.13241 | 20.7655 | 22.0856 | 22.3758 | 20.1087 | 21.6698 | 22.119 | 21.9512 | 21.7157 | 21.2844 | 21.7886 | 21.4474 | 21.0411 | 20.2989 | 20.373 | 20.2223 | 20.1961 | 20.1511 |  | 20.2345 | 19.9127 | 20.1431 | 19.6902 | 20.0892 | 20.3061 |  | 20.4044 |  |  | 20.3429 | 20.3791 | 20.6183 | [5 empty] | 21.9324 | 20.3226 | 21.6675 | 22.0457 | 19.5256 | 21.1642 | 21.7905 | 19.3741 | 19.924 | 21.1544 |  | 19.8056 | 20.911 | 18.8826 | 19.6695 | 20.795 | 19.3986 | 20.0324 | 19.0277 | 20.0627 | 19.1346 | 20.1658 | 18.839 | 20.1138 | 21.0412 | 19.4301 | 19.7623 | 20.9826 | 18.9183 | 19.8086 | 20.7798 | 19.007 | 20.0741 | 19.2897 | 19.8716 | 18.8564 | 20.0732 | -0.070808 | 20.9458 | 0.046521 | 0.012778 | -26.9902 | 3.0965 | -1.85 | 0 | 0.76899 | -0.79038 | -10.3784 | 0.5835 | 0.464 | -16.7084 | 1.9415 | 0.4224 | 0.42596 | 0.43033 | 0.38712 | 0.46961 | 0.43893 | 0.42847
42838.418 | -197 | 22.9047 | 22.8689 | 22.8495 | 22.7828 | 22.4066 | 21.7483 | 22.7156 | 21.8026 | 22.3673 | 22.3829 | 22.3584 | 22.0287 | 21.2459 | 22.2138 | 21.6008 | 21.772 | 21.8999 | 21.0824 | 21.1827 | 21.4069 | 20.481 | 20.6235 | 20.9173 | 21.8864 | 21.6551 | 21.285 | 20.2856 | 20.4096 | 20.345 | 22.0644 | 21.671 | 21.1958 | 21.9938 | 21.7412 | 21.3578 | 19.9227 | 20.4135 |  | 20.5053 | 20.044 | 20.1402 | 19.1547 |  | 16.8623 | 16.8036 | 16.5291 | 16.7376 | 16.8109 | 17.3963 | 17.8424 | 16.137 | 16.899 | 16.7604 | 16.9802 | 17.9363 | 44.0562 | 43.0301 | 43.028 | 21.3895 |  |  | 0.39319 | -0.49882 | -77.0181 | 0.32391 | 0.17952 | -197.8466 | 2.8515 | -0.44983 | -0.086114 | 0.28061 | -0.0014448 | 8.8289 | 9.0587 | 1.9789 | 21.7822 | 22.006 | 22.2006 | 22.2602 | 22.0855 | 21.404 | 20.2196 | 22.1893 | 22.3701 | 22.4079 | 22.3521 | 21.9729 | 21.2098 | 22.2646 | 17.2415 | 17.261 | 16.3081 | 16.3303 | 16.3424 | 17.1325 | 16.9042 | 22.3949 | 22.1529 | 21.7054 | 22.0839 | 21.7978 | 21.306 | 21.9451 | 21.5272 | 20.9018 | 20.0957 | 20.297 | 19.8514 | 19.7674 | 0.12937 | 0.084099 | 20.7651 | 22.0897 | 22.377 | 20.1167 | 21.6755 | 22.1251 | 21.953 | 21.7223 | 21.2835 | 21.787 | 21.4474 | 21.0473 | 20.3019 | 20.3686 | 20.2226 | 20.1958 | 20.1203 |  | 20.2222 | 19.8891 | 20.1208 | 19.6692 | 20.0754 | 20.2931 |  | 20.3948 |  |  | 20.3302 | 20.3722 | 20.6149 | [5 empty] | 21.9313 | 20.3204 | 21.6609 | 22.0405 | 19.5158 | 21.1652 | 21.7758 | 19.3767 | 19.9262 | 21.1489 |  | 19.804 | 20.9102 | 18.8804 | 19.6694 | 20.7951 | 19.4008 | 20.0475 | 19.0358 | 20.0708 | 19.1354 | 20.1719 | 18.8369 | 20.1176 | 21.0426 | 19.4282 | 19.7604 | 20.9825 | 18.9155 | 19.8138 | 20.7794 | 19.0042 | 20.0761 | 19.2907 | 19.876 | 18.8579 | 20.0688 | 0.024539 | 20.946 | 0.047817 | 0.012676 | -27.0585 | 3.0965 | -5.7 | 0.01 | 0.74863 | -0.83811 | -10.4142 | 0.67538 | 0.50331 | -16.7086 | 2.0059 | 0.42284 | 0.42586 | 0.43045 | 0.39048 | 0.46755 | 0.43963 | 0.4284
42838.418 | -196 | 22.8981 | 22.864 | 22.8523 | 22.7815 | 22.4067 | 21.7501 | 22.7216 | 21.8053 | 22.3644 | 22.3784 | 22.3629 | 22.0292 | 21.2475 | 22.2138 | 21.5962 | 21.7729 | 21.8955 | 21.0781 | 21.1817 | 21.3974 | 20.4804 | 20.6135 | 20.9163 | 21.8812 | 21.6497 | 21.2808 | 20.2864 | 20.4027 | 20.3433 | 22.0674 | 21.6628 | 21.1804 | 21.9942 | 21.7362 | 21.3472 | 19.9168 | 20.4085 |  | 20.5112 | 20.045 | 20.1415 | 19.1384 |  | 16.8636 | 16.801 | 16.5228 | 16.7435 | 16.8193 | 17.4099 | 17.8345 | 16.1398 | 16.8883 | 16.748 | 16.9841 | 17.9339 | 43.9833 | 42.915 | 42.9801 | 21.3926 |  |  | 0.43393 | -0.35425 | -77.0621 | 0.70504 | 0.059928 | -197.8526 | 2.6616 | -0.438 | -0.045054 | 0.21977 | 0.1666 | 8.8282 | 9.0581 | 1.9786 | 21.7863 | 22.005 | 22.1951 | 22.2601 | 22.0879 | 21.4031 | 20.2135 | 22.1925 | 22.3631 | 22.4068 | 22.3503 | 21.9787 | 21.2055 | 22.2613 | 17.2252 | 17.2828 | 16.3277 | 16.3268 | 16.3457 | 17.1358 | 16.9064 | 22.3908 | 22.1517 | 21.7064 | 22.0932 | 21.7963 | 21.3023 | 21.9441 | 21.5215 | 20.9039 | 20.0987 | 20.2981 | 19.8484 | 19.7721 | 0.12033 | 0.084099 | 20.7623 | 22.0842 | 22.3761 | 20.1091 | 21.6696 | 22.1198 | 21.9505 | 21.7174 | 21.2771 | 21.783 | 21.443 | 21.0426 | 20.3004 | 20.3614 | 20.2173 | 20.1907 | 20.1126 |  | 20.2331 | 19.8879 | 20.1364 | 19.6808 | 20.0864 | 20.3003 |  | 20.4071 |  |  | 20.3392 | 20.3824 | 20.6289 | [5 empty] | 21.9346 | 20.3272 | 21.6717 | 22.0531 | 19.5145 | 21.1669 | 21.7859 | 19.375 | 19.9292 | 21.1485 |  | 19.8085 | 20.9025 | 18.8712 | 19.6644 | 20.7966 | 19.4082 | 20.0426 | 19.0384 | 20.0748 | 19.1386 | 20.171 | 18.8383 | 20.1208 | 21.0511 | 19.4337 | 19.7616 | 20.9824 | 18.9154 | 19.8159 | 20.7813 | 19.0139 | 20.078 | 19.2927 | 19.8899 | 18.8629 | 20.0774 | -0.032966 | 20.946 | 0.048456 | 0.014578 | -27.0571 | 3.0965 | 1.83 | -0.07 | 0.78646 | -0.70629 | -10.4172 | 0.99641 | 0.2908 | -16.7092 | 1.938 | 0.42342 | 0.42642 | 0.4305 | 0.39268 | 0.46564 | 0.43988 | 0.42837
42838.418 | -195 | 22.8907 | 22.865 | 22.8507 | 22.7716 | 22.4053 | 21.7397 | 22.7153 | 21.8037 | 22.3637 | 22.3754 | 22.3541 | 22.022 | 21.2414 | 22.2163 | 21.5871 | 21.7642 | 21.8949 | 21.0707 | 21.1753 | 21.3895 | 20.4716 | 20.6154 | 20.9068 | 21.8757 | 21.6407 | 21.2747 | 20.2817 | 20.3998 | 20.3368 | 22.06 | 21.6675 | 21.1895 | 21.998 | 21.7317 | 21.3436 | 19.9196 | 20.417 |  | 20.5049 | 20.0409 | 20.1372 | 19.1465 |  | 16.8716 | 16.8023 | 16.5336 | 16.7479 | 16.8231 | 17.4048 | 17.8149 | 16.1295 | 16.8941 | 16.7608 | 16.9909 | 17.9415 | 43.9054 | 42.8143 | 42.9243 | 21.3908 |  |  | 0.4129 | -0.080233 | -77.7889 | 0.88969 | -0.051124 | -197.8328 | 2.5558 | -0.4702 | 0.1871 | 0.040812 | 0.18552 | 8.8292 | 9.0588 | 1.9787 | 21.7798 | 22.0053 | 22.1965 | 22.2562 | 22.0849 | 21.4095 | 20.2133 | 22.1934 | 22.366 | 22.4017 | 22.3543 | 21.9773 | 21.2061 | 22.2639 | 17.2106 | 17.2831 | 16.3339 | 16.3434 | 16.3494 | 17.144 | 16.9084 | 22.392 | 22.154 | 21.7092 | 22.0854 | 21.8042 | 21.3084 | 21.9432 | 21.5233 | 20.9071 | 20.0904 | 20.3017 | 19.8534 | 19.7842 | 0.12682 | 0.1889 | 20.7651 | 22.0836 | 22.3808 | 20.1137 | 21.6744 | 22.1203 | 21.9571 | 21.7131 | 21.2814 | 21.7838 | 21.448 | 21.0414 | 20.2979 | 20.3676 | 20.2159 | 20.1871 | 20.098 |  | 20.2294 | 19.8788 | 20.1359 | 19.6959 | 20.0853 | 20.3057 |  | 20.4066 |  |  | 20.3373 | 20.384 | 20.6258 | [5 empty] | 21.9294 | 20.3247 | 21.6757 | 22.0438 | 19.5224 | 21.1625 | 21.7814 | 19.3719 | 19.9278 | 21.1452 |  | 19.8052 | 20.9024 | 18.8669 | 19.666 | 20.7972 | 19.406 | 20.0383 | 19.0394 | 20.0714 | 19.1382 | 20.176 | 18.832 | 20.122 | 21.0464 | 19.4282 | 19.7627 | 20.979 | 18.9223 | 19.8151 | 20.7831 | 19.0169 | 20.0678 | 19.2945 | 19.884 | 18.8637 | 20.0807 | -0.087318 | 20.9469 | 0.049249 | 0.015979 | -27.1054 | 3.0966 | -7.07 | -0.06 | 0.76715 | -0.33613 | -10.4662 | 1.1193 | -0.26859 | -16.7082 | 1.8991 | 0.4237 | 0.42666 | 0.43004 | 0.39525 | 0.46518 | 0.43975 | 0.42776
42838.418 | -194 | 22.8892 | 22.8607 | 22.8407 | 22.7654 | 22.4016 | 21.7406 | 22.7137 | 21.802 | 22.3692 | 22.3728 | 22.3553 | 22.023 | 21.241 | 22.216 | 21.584 | 21.7549 | 21.8902 | 21.07 | 21.1718 | 21.3841 | 20.4679 | 20.6143 | 20.9014 | 21.8751 | 21.6387 | 21.2689 | 20.277 | 20.3984 | 20.3343 | 22.0688 | 21.672 | 21.1956 | 22.0011 | 21.7365 | 21.3532 | 19.9143 | 20.4218 |  | 20.5043 | 20.037 | 20.1359 | 19.1574 |  | 16.8751 | 16.8151 | 16.5407 | 16.76 | 16.8199 | 17.3848 | 17.7784 | 16.0943 | 16.9056 | 16.7403 | 16.9949 | 17.9389 | 43.8048 | 42.7334 | 42.8453 | 21.3998 |  |  | 0.4773 | -0.3825 | -79.2792 | 0.62356 | 0.019844 | -197.8519 | 2.4119 | -0.61674 | -0.084752 | 0.19355 | 0.17459 | 8.8292 | 9.0591 | 1.9783 | 21.7814 | 22.0021 | 22.2013 | 22.2587 | 22.0835 | 21.4034 | 20.2164 | 22.1928 | 22.3667 | 22.4012 | 22.3552 | 21.9809 | 21.2105 | 22.2683 | 17.191 | 17.2723 | 16.3426 | 16.3401 | 16.3541 | 17.1356 | 16.9064 | 22.3915 | 22.149 | 21.7033 | 22.0837 | 21.7984 | 21.3094 | 21.9484 | 21.5237 | 20.9079 | 20.0954 | 20.3006 | 19.8507 | 19.7806 | 0.13979 | 0.051005 | 20.7724 | 22.0872 | 22.3866 | 20.1197 | 21.682 | 22.1253 | 21.961 | 21.7183 | 21.2841 | 21.7868 | 21.4531 | 21.0454 | 20.2989 | 20.3806 | 20.2234 | 20.1925 | 20.0976 |  | 20.2279 | 19.8681 | 20.1361 | 19.6798 | 20.0909 | 20.3073 |  | 20.4016 |  |  | 20.3372 | 20.3827 | 20.6165 | [5 empty] | 21.9229 | 20.3192 | 21.6723 | 22.0472 | 19.5212 | 21.1619 | 21.7789 | 19.3692 | 19.9198 | 21.1413 |  | 19.8055 | 20.9009 | 18.8659 | 19.6681 | 20.7944 | 19.3977 | 20.0409 | 19.0377 | 20.0693 | 19.1403 | 20.1771 | 18.8255 | 20.1158 | 21.0396 | 19.4278 | 19.7521 | 20.9835 | 18.9167 | 19.8072 | 20.7821 | 19.0131 | 20.0623 | 19.2879 | 19.8831 | 18.8615 | 20.0805 | -0.096036 | 20.9467 | 0.049593 | 0.01701 | -27.1113 | 3.0966 | -3.59 | -0.05 | 0.82481 | -0.73394 | -10.5662 | 0.93708 | 0.16733 | -16.7085 | 1.8448 | 0.42366 | 0.42696 | 0.43068 | 0.39645 | 0.46398 | 0.43927 | 0.42803
42838.418 | -193 | 22.8959 | 22.8676 | 22.8459 | 22.7745 | 22.4089 | 21.743 | 22.717 | 21.8015 | 22.3659 | 22.3685 | 22.3481 | 22.0212 | 21.2444 | 22.2114 | 21.5887 | 21.7597 | 21.8855 | 21.0767 | 21.1748 | 21.3881 | 20.4714 | 20.6096 | 20.9028 | 21.8796 | 21.6443 | 21.2694 | 20.28 | 20.3979 | 20.3315 | 22.0597 | 21.6734 | 21.1833 | 21.9972 | 21.7383 | 21.3536 | 19.9102 | 20.4251 |  | 20.5031 | 20.0382 | 20.1364 | 19.1708 |  | 16.8785 | 16.8175 | 16.5509 | 16.7656 | 16.8218 | 17.3742 | 17.7428 | 16.0656 | 16.9021 | 16.704 | 16.9904 | 17.9372 | 43.6877 | 42.6297 | 42.7584 | 21.3846 |  |  | 0.51015 | -0.23006 | -79.7227 | 0.50068 | 0.096728 | -197.8098 | 1.8152 | -0.553 | 0.098561 | 0.19837 | 0.078585 | 8.8297 | 9.0594 | 1.9783 | 21.7745 | 22.003 | 22.1978 | 22.257 | 22.0795 | 21.4025 | 20.2119 | 22.1915 | 22.3672 | 22.399 | 22.3517 | 21.9811 | 21.2101 | 22.2613 | 17.155 | 17.2838 | 16.3396 | 16.3453 | 16.3767 | 17.1424 | 16.9108 | 22.3839 | 22.1482 | 21.7042 | 22.085 | 21.7972 | 21.2991 | 21.9467 | 21.5201 | 20.9043 | 20.0995 | 20.2952 | 19.8531 | 19.7797 | 0.33266 | 0.054048 | 20.7753 | 22.0787 | 22.383 | 20.1118 | 21.6751 | 22.1231 | 21.9528 | 21.7197 | 21.2791 | 21.7887 | 21.4497 | 21.0441 | 20.2914 | 20.3759 | 20.2253 | 20.1917 | 20.1025 |  | 20.2293 | 19.8544 | 20.1374 | 19.6602 | 20.0846 | 20.3071 |  | 20.3971 |  |  | 20.3369 | 20.3878 | 20.6241 | [5 empty] | 21.9282 | 20.3254 | 21.6726 | 22.0486 | 19.5204 | 21.1655 | 21.7873 | 19.3676 | 19.9206 | 21.145 |  | 19.8102 | 20.9053 | 18.8743 | 19.6694 | 20.7953 | 19.4022 | 20.0434 | 19.0447 | 20.0762 | 19.1445 | 20.1842 | 18.8265 | 20.116 | 21.0419 | 19.43 | 19.7487 | 20.9833 | 18.9154 | 19.8082 | 20.7838 | 19.0156 | 20.0696 | 19.294 | 19.8873 | 18.8639 | 20.0798 | -0.1272 | 20.9442 | 0.050072 | 0.016604 | -27.0881 | 3.0965 | -5 | -0.05 | 0.85272 | -0.56919 | -10.5958 | 0.83969 | 0.36943 | -16.7064 | 1.6004 | 0.42357 | 0.42739 | 0.43101 | 0.40124 | 0.46483 | 0.43877 | 0.42819
42838.4181 | -192 | 22.9047 | 22.8671 | 22.8549 | 22.7841 | 22.4149 | 21.7561 | 22.7183 | 21.8047 | 22.3722 | 22.3749 | 22.3602 | 22.031 | 21.2569 | 22.2176 | 21.5943 | 21.7681 | 21.8935 | 21.0848 | 21.1755 | 21.3973 | 20.477 | 20.6163 | 20.9081 | 21.8872 | 21.6499 | 21.2793 | 20.2867 | 20.4073 | 20.3425 | 22.0606 | 21.6715 | 21.1831 | 22 | 21.7352 | 21.3552 | 19.9133 | 20.4233 |  | 20.5017 | 20.0409 | 20.1334 | 19.1784 |  | 16.8737 | 16.817 | 16.5436 | 16.7553 | 16.8393 | 17.363 | 17.7081 | 16.0607 | 16.8959 | 16.652 | 16.9873 | 17.9387 | 43.5752 | 42.5602 | 42.6769 | 21.3893 |  |  | 0.57783 | -0.11834 | -80.876 | 0.67284 | 0.24458 | -197.8131 | 1.8218 | -0.576 | -0.17641 | -0.015834 | 0.12945 | 8.8291 | 9.0589 | 1.9788 | 21.7764 | 21.9978 | 22.1894 | 22.2649 | 22.0855 | 21.4069 | 20.2208 | 22.1896 | 22.3643 | 22.3977 | 22.3486 | 21.9758 | 21.2038 | 22.2591 | 17.1118 | 17.2854 | 16.3452 | 16.3463 | 16.3826 | 17.1413 | 16.9066 | 22.3863 | 22.1499 | 21.708 | 22.0875 | 21.805 | 21.2996 | 21.945 | 21.5225 | 20.9012 | 20.1009 | 20.2948 | 19.8579 | 19.788 | 0.31005 | 0.049103 | 20.7689 | 22.0758 | 22.3804 | 20.1079 | 21.6675 | 22.1108 | 21.947 | 21.7149 | 21.2781 | 21.7889 | 21.4454 | 21.0414 | 20.2831 | 20.3668 | 20.2243 | 20.1857 | 20.1006 |  | 20.2317 | 19.8413 | 20.1355 | 19.6543 | 20.0828 | 20.3029 |  | 20.3962 |  |  | 20.3337 | 20.3908 | 20.6313 | [5 empty] | 21.9339 | 20.3271 | 21.6661 | 22.0437 | 19.5208 | 21.1643 | 21.7811 | 19.3571 | 19.9098 | 21.1377 |  | 19.805 | 20.8942 | 18.8723 | 19.6601 | 20.7902 | 19.3976 | 20.04 | 19.0409 | 20.0697 | 19.1432 | 20.1795 | 18.8285 | 20.1149 | 21.0402 | 19.432 | 19.7505 | 20.9837 | 18.9128 | 19.8049 | 20.7819 | 19.0204 | 20.0714 | 19.2943 | 19.89 | 18.8714 | 20.0863 | -0.11125 | 20.9436 | 0.05065 | 0.015703 | -27.0622 | 3.0965 | 9.28 | -0.07 | 0.90754 | -0.40824 | -10.6721 | 0.97341 | 0.58744 | -16.7062 | 1.6032 | 0.42371 | 0.42769 | 0.43111 | 0.40592 | 0.46372 | 0.43866 | 0.42801
42838.4181 | -191 | 22.9044 | 22.8618 | 22.8515 | 22.7829 | 22.4052 | 21.7467 | 22.7201 | 21.8029 | 22.3718 | 22.3808 | 22.3626 | 22.0352 | 21.2483 | 22.2111 | 21.5881 | 21.7568 | 21.8895 | 21.0756 | 21.1683 | 21.3889 | 20.4667 | 20.6105 | 20.9018 | 21.8734 | 21.638 | 21.2731 | 20.2727 | 20.4008 | 20.3349 | 22.0618 | 21.6678 | 21.1777 | 21.9904 | 21.7311 | 21.3516 | 19.9154 | 20.4232 |  | 20.5012 | 20.0366 | 20.1282 | 19.1793 |  | 16.885 | 16.8203 | 16.5551 | 16.7667 | 16.8447 | 17.3885 | 17.6933 | 16.0793 | 16.9004 | 16.6239 | 16.9911 | 17.9348 | 43.4563 | 42.4876 | 42.5943 | 21.3866 |  |  | 0.44247 | -0.3825 | -81.1934 | 0.35809 | 0.12696 | -197.8361 | 1.9302 | -0.55891 | -0.057897 | 0.1839 | 0.36728 | 8.8286 | 9.0582 | 1.9787 | 21.777 | 22.0072 | 22.1973 | 22.2552 | 22.0898 | 21.4035 | 20.214 | 22.1983 | 22.3713 | 22.4078 | 22.3499 | 21.9863 | 21.2091 | 22.2622 | 17.0995 | 17.3112 | 16.3619 | 16.349 | 16.3888 | 17.1482 | 16.9129 | 22.3784 | 22.1532 | 21.6999 | 22.0842 | 21.7978 | 21.297 | 21.9423 | 21.5221 | 20.9026 | 20.1036 | 20.3017 | 19.8475 | 19.7859 | 0.17459 | 0.11738 | 20.7715 | 22.0805 | 22.384 | 20.1135 | 21.6685 | 22.1157 | 21.946 | 21.7162 | 21.2782 | 21.786 | 21.4467 | 21.0401 | 20.2897 | 20.3714 | 20.2273 | 20.1879 | 20.1137 |  | 20.2336 | 19.8333 | 20.1437 | 19.656 | 20.0844 | 20.3023 |  | 20.4036 |  |  | 20.3242 | 20.3883 | 20.6196 | [5 empty] | 21.928 | 20.3205 | 21.6597 | 22.0385 | 19.5201 | 21.1599 | 21.774 | 19.3609 | 19.9043 | 21.1337 |  | 19.8008 | 20.8956 | 18.8806 | 19.6685 | 20.7918 | 19.4021 | 20.0408 | 19.0464 | 20.0713 | 19.1473 | 20.1835 | 18.8124 | 20.1073 | 21.026 | 19.4261 | 19.7507 | 20.9737 | 18.902 | 19.8063 | 20.7783 | 19.0121 | 20.0676 | 19.2943 | 19.8865 | 18.8651 | 20.0813 | -0.094737 | 20.9478 | 0.050496 | 0.015282 | -27.0195 | 3.0965 | -13.75 | -0.01 | 0.79415 | -0.73394 | -10.6931 | 0.71013 | 0.42325 | -16.7079 | 1.6503 | 0.42341 | 0.42818 | 0.43112 | 0.40809 | 0.4626 | 0.4387 | 0.42815
42838.4181 | -190 | 22.8904 | 22.8645 | 22.8498 | 22.7725 | 22.4062 | 21.7457 | 22.7191 | 21.8116 | 22.3694 | 22.3859 | 22.3628 | 22.0364 | 21.2448 | 22.2127 | 21.5883 | 21.7604 | 21.8891 | 21.0752 | 21.1702 | 21.3885 | 20.4719 | 20.6141 | 20.9085 | 21.8782 | 21.6401 | 21.2724 | 20.2834 | 20.4022 | 20.3376 | 22.0742 | 21.6741 | 21.1863 | 21.9987 | 21.7433 | 21.3583 | 19.9149 | 20.4338 |  | 20.5042 | 20.0457 | 20.1426 | 19.1839 |  | 16.8841 | 16.8198 | 16.5575 | 16.7671 | 16.8522 | 17.407 | 17.6793 | 16.072 | 16.8972 | 16.6141 | 16.9931 | 17.9376 | 43.3369 | 42.4264 | 42.5026 | 21.3881 |  |  | 0.3301 | -0.31351 | -81.382 | 0.73527 | 0.18872 | -197.8683 | 1.6779 | -0.39134 | 0.11082 | 0.10228 | 0.033449 | 8.8286 | 9.0583 | 1.9786 | 21.7837 | 22.011 | 22.2004 | 22.2604 | 22.094 | 21.4084 | 20.2162 | 22.2029 | 22.375 | 22.4076 | 22.3527 | 21.9861 | 21.2125 | 22.272 | 17.0998 | 17.3253 | 16.3962 | 16.3533 | 16.3969 | 17.1503 | 16.9199 | 22.3958 | 22.1528 | 21.711 | 22.0876 | 21.8007 | 21.3038 | 21.9439 | 21.5251 | 20.8982 | 20.094 | 20.2906 | 19.8507 | 19.7959 | 0.19484 | 0.078013 | 20.7695 | 22.0807 | 22.3839 | 20.1164 | 21.6647 | 22.1195 | 21.9449 | 21.7184 | 21.2792 | 21.7834 | 21.4493 | 21.0477 | 20.2953 | 20.3663 | 20.2235 | 20.1903 | 20.1098 |  | 20.2303 | 19.8148 | 20.143 | 19.665 | 20.0754 | 20.2959 |  | 20.3988 |  |  | 20.3169 | 20.3923 | 20.6215 | [5 empty] | 21.931 | 20.3176 | 21.6648 | 22.0385 | 19.5258 | 21.1602 | 21.7824 | 19.3547 | 19.9068 | 21.1307 |  | 19.8012 | 20.8882 | 18.8717 | 19.6609 | 20.7847 | 19.3998 | 20.042 | 19.0461 | 20.0619 | 19.1445 | 20.1778 | 18.8029 | 20.1007 | 21.0228 | 19.4253 | 19.7412 | 20.9716 | 18.9023 | 19.8034 | 20.7744 | 19.0058 | 20.0634 | 19.2972 | 19.8883 | 18.8658 | 20.0752 | 0.014151 | 20.9451 | 0.049077 | 0.014767 | -27.0207 | 3.0965 | -5.28 | -0.09 | 0.68594 | -0.66446 | -10.7055 | 1.0176 | 0.51606 | -16.7098 | 1.5387 | 0.4234 | 0.42867 | 0.43057 | 0.4083 | 0.45961 | 0.43856 | 0.42756
42838.4181 | -189 | 22.8931 | 22.8686 | 22.8463 | 22.773 | 22.4047 | 21.7438 | 22.7131 | 21.7999 | 22.3584 | 22.3801 | 22.3532 | 22.0245 | 21.242 | 22.2057 | 21.589 | 21.7555 | 21.8878 | 21.0705 | 21.1756 | 21.3882 | 20.4731 | 20.606 | 20.9068 | 21.8763 | 21.6435 | 21.2673 | 20.2767 | 20.4052 | 20.3387 | 22.074 | 21.6765 | 21.1983 | 22.0021 | 21.7389 | 21.3521 | 19.9207 | 20.4381 |  | 20.505 | 20.0504 | 20.1372 | 19.1864 |  | 16.8981 | 16.8327 | 16.5712 | 16.7938 | 16.8799 | 17.4084 | 17.6834 | 16.071 | 16.9036 | 16.5788 | 17.0035 | 17.9423 | 43.2118 | 42.3827 | 42.4253 | 21.387 |  |  | 0.42539 | 0.032135 | -81.9175 | 0.75367 | 0.25378 | -197.844 | 1.5918 | -0.3184 | -0.62574 | 0.026966 | 0.08605 | 8.8289 | 9.0584 | 1.9782 | 21.7776 | 22.0086 | 22.1958 | 22.2609 | 22.0804 | 21.4054 | 20.2133 | 22.1936 | 22.3681 | 22.3987 | 22.3473 | 21.9818 | 21.2007 | 22.2597 | 17.0913 | 17.3195 | 16.4485 | 16.3438 | 16.3846 | 17.1445 | 16.9158 | 22.386 | 22.1437 | 21.7022 | 22.0837 | 21.7886 | 21.2882 | 21.9413 | 21.5212 | 20.8996 | 20.0947 | 20.2901 | 19.8481 | 19.7895 | 0.13645 | 0.24216 | 20.7691 | 22.0772 | 22.3804 | 20.1135 | 21.665 | 22.1183 | 21.9481 | 21.7162 | 21.2766 | 21.7836 | 21.4481 | 21.0504 | 20.2914 | 20.3603 | 20.2199 | 20.192 | 20.1092 |  | 20.228 | 19.8223 | 20.148 | 19.6601 | 20.0826 | 20.2952 |  | 20.4031 |  |  | 20.3218 | 20.3968 | 20.6343 | [5 empty] | 21.9348 | 20.3295 | 21.6699 | 22.0454 | 19.5293 | 21.1628 | 21.7816 | 19.3513 | 19.9035 | 21.1242 |  | 19.7997 | 20.8855 | 18.8719 | 19.6583 | 20.7863 | 19.4015 | 20.0382 | 19.0511 | 20.061 | 19.141 | 20.1796 | 18.8083 | 20.1125 | 21.0301 | 19.4347 | 19.7459 | 20.9832 | 18.908 | 19.8042 | 20.779 | 19.0116 | 20.0684 | 19.3017 | 19.8914 | 18.8738 | 20.0895 | -0.1528 | 20.9453 | 0.048284 | 0.012364 | -27.0953 | 3.0966 | -5.16 | -0.08 | 0.77867 | 0.21274 | -10.7409 | 1.0302 | 0.59843 | -16.7088 | 1.4987 | 0.42334 | 0.42863 | 0.43095 | 0.40857 | 0.45331 | 0.43869 | 0.42776
42838.4181 | -188 | 22.8961 | 22.8652 | 22.848 | 22.781 | 22.4062 | 21.7466 | 22.7146 | 21.808 | 22.3673 | 22.3777 | 22.3598 | 22.0337 | 21.2515 | 22.2128 | 21.5866 | 21.7589 | 21.881 | 21.0784 | 21.178 | 21.3885 | 20.4728 | 20.6074 | 20.9001 | 21.8728 | 21.6397 | 21.2676 | 20.2836 | 20.399 | 20.3418 | 22.0641 | 21.6673 | 21.1932 | 21.998 | 21.74 | 21.3494 | 19.916 | 20.4405 |  | 20.5017 | 20.041 | 20.138 | 19.1789 |  | 16.8945 | 16.836 | 16.5837 | 16.8066 | 16.89 | 17.4053 | 17.6922 | 16.0609 | 16.8986 | 16.5227 | 16.9964 | 17.9397 | 43.0833 | 42.3333 | 42.3249 | 21.3863 |  |  | 0.37479 | -0.055265 | -81.6783 | 0.58216 | 0.27021 | -197.8342 | 1.5675 | -0.3138 | -0.32392 | 0.11676 | -0.023145 | 8.8286 | 9.0585 | 1.9781 | 21.7805 | 22.0079 | 22.2029 | 22.2678 | 22.0887 | 21.4077 | 20.2191 | 22.1954 | 22.373 | 22.4047 | 22.3494 | 21.9835 | 21.2063 | 22.2635 | 17.1213 | 17.2825 | 16.4824 | 16.3471 | 16.394 | 17.1429 | 16.9142 | 22.3864 | 22.149 | 21.7083 | 22.0811 | 21.7934 | 21.2956 | 21.9368 | 21.5259 | 20.9072 | 20.1002 | 20.3017 | 19.8479 | 19.7951 | 0.10342 | 0.28723 | 20.7787 | 22.081 | 22.3798 | 20.12 | 21.6762 | 22.1257 | 21.9534 | 21.7176 | 21.2796 | 21.7925 | 21.4507 | 21.0495 | 20.2907 | 20.3634 | 20.2261 | 20.1945 | 20.108 |  | 20.2284 | 19.8144 | 20.1411 | 19.6658 | 20.0883 | 20.2998 |  | 20.3992 |  |  | 20.3422 | 20.4107 | 20.6411 | [5 empty] | 21.9396 | 20.3425 | 21.6762 | 22.0581 | 19.536 | 21.17 | 21.7843 | 19.3507 | 19.9048 | 21.1305 |  | 19.7997 | 20.8843 | 18.8694 | 19.6596 | 20.7792 | 19.3889 | 20.041 | 19.0545 | 20.0771 | 19.1459 | 20.1884 | 18.7993 | 20.1002 | 21.0274 | 19.428 | 19.746 | 20.9761 | 18.9143 | 19.8092 | 20.7857 | 19.0172 | 20.0774 | 19.3045 | 19.8931 | 18.878 | 20.0968 | -0.031111 | 20.9444 | 0.047338 | 0.012887 | -27.0281 | 3.0965 | -6.56 | -0.05 | 0.7309 | -0.27898 | -10.7253 | 0.90548 | 0.61749 | -16.7083 | 1.4872 | 0.42339 | 0.42862 | 0.43098 | 0.40506 | 0.44936 | 0.43874 | 0.42779
42838.4181 | -187 | 22.9015 | 22.8687 | 22.8544 | 22.7819 | 22.412 | 21.7473 | 22.7191 | 21.8134 | 22.3764 | 22.3888 | 22.3638 | 22.0332 | 21.2487 | 22.212 | 21.5902 | 21.7552 | 21.8843 | 21.0706 | 21.1765 | 21.3935 | 20.4703 | 20.6139 | 20.9073 | 21.8747 | 21.6379 | 21.2736 | 20.2786 | 20.399 | 20.3364 | 22.0726 | 21.6723 | 21.188 | 21.9991 | 21.7392 | 21.3533 | 19.9243 | 20.4424 |  | 20.5023 | 20.0464 | 20.1375 | 19.1987 |  | 16.9027 | 16.8513 | 16.5904 | 16.8118 | 16.8856 | 17.3926 | 17.7038 | 16.0646 | 16.8989 | 16.4859 | 16.9963 | 17.935 | 42.9555 | 42.2947 | 42.2168 | 21.3805 |  |  | 0.49307 | -0.033577 | -82.62 | 0.54208 | 0.085556 | -197.8361 | 1.5451 | -0.26189 | -0.30718 | -0.15682 | 0.13119 | 8.829 | 9.0586 | 1.9779 | 21.7834 | 22.0071 | 22.2015 | 22.2683 | 22.0878 | 21.4076 | 20.2205 | 22.198 | 22.3707 | 22.4132 | 22.3555 | 21.974 | 21.2128 | 22.2653 | 17.1658 | 17.2852 | 16.5132 | 16.3538 | 16.418 | 17.1458 | 16.9169 | 22.3853 | 22.15 | 21.7069 | 22.076 | 21.7985 | 21.2986 | 21.9422 | 21.5196 | 20.9031 | 20.1012 | 20.3031 | 19.8497 | 19.8001 | 0.044444 | 0.046059 | 20.7763 | 22.0796 | 22.3762 | 20.1179 | 21.6739 | 22.1244 | 21.9492 | 21.7107 | 21.2838 | 21.789 | 21.4467 | 21.0458 | 20.2878 | 20.3663 | 20.2286 | 20.1951 | 20.1078 |  | 20.2286 | 19.8012 | 20.144 | 19.6722 | 20.0866 | 20.2992 |  | 20.4 |  |  | 20.3257 | 20.3918 | 20.6371 | [5 empty] | 21.926 | 20.3258 | 21.667 | 22.0424 | 19.5291 | 21.155 | 21.7885 | 19.3464 | 19.9046 | 21.1283 |  | 19.8071 | 20.8949 | 18.8704 | 19.6691 | 20.788 | 19.3997 | 20.0458 | 19.0446 | 20.0784 | 19.1514 | 20.182 | 18.812 | 20.1024 | 21.0302 | 19.4273 | 19.7385 | 20.9783 | 18.9045 | 19.8123 | 20.7893 | 19.0188 | 20.0736 | 19.3073 | 19.9058 | 18.8848 | 20.0958 | -0.058008 | 20.9451 | 0.046902 | 0.012125 | -27.071 | 3.0965 | -1.77 | -0.08 | 0.83833 | -0.21746 | -10.7872 | 0.87377 | 0.34745 | -16.708 | 1.4766 | 0.4234 | 0.42908 | 0.43075 | 0.40045 | 0.44625 | 0.43846 | 0.42768
42838.4181 | -186 | 22.9025 | 22.8708 | 22.8519 | 22.7796 | 22.4085 | 21.7423 | 22.7162 | 21.8118 | 22.376 | 22.3832 | 22.3595 | 22.0313 | 21.2469 | 22.208 | 21.5882 | 21.7651 | 21.894 | 21.0798 | 21.177 | 21.3998 | 20.4785 | 20.6169 | 20.9081 | 21.8861 | 21.6445 | 21.2756 | 20.2815 | 20.4085 | 20.3518 | 22.0716 | 21.6728 | 21.1872 | 22.0014 | 21.7376 | 21.3564 | 19.9248 | 20.4438 |  | 20.5061 | 20.0408 | 20.1388 | 19.2132 |  | 16.9162 | 16.8545 | 16.5886 | 16.8053 | 16.8779 | 17.3781 | 17.6959 | 16.0701 | 16.9026 | 16.4076 | 16.9989 | 17.9465 | 42.8719 | 42.2736 | 42.1278 | 21.3893 |  |  | 0.55089 | -0.16106 | -83.2653 | 0.71621 | 0.087528 | -197.8637 | 1.2915 | -0.26124 | 0.031813 | 0.1604 | -0.031825 | 8.8291 | 9.0588 | 1.9788 | 21.7792 | 22.0051 | 22.1948 | 22.2668 | 22.0907 | 21.4004 | 20.2212 | 22.1929 | 22.3678 | 22.4152 | 22.3535 | 21.9816 | 21.2119 | 22.2575 | 17.1959 | 17.2731 | 16.4928 | 16.3496 | 16.4025 | 17.1497 | 16.9218 | 22.3893 | 22.1499 | 21.7075 | 22.0792 | 21.7987 | 21.304 | 21.9415 | 21.5237 | 20.9 | 20.0992 | 20.2974 | 19.8496 | 19.8007 | -0.050121 | 0.099886 | 20.7731 | 22.0789 | 22.3781 | 20.114 | 21.6747 | 22.1241 | 21.9561 | 21.7148 | 21.2842 | 21.785 | 21.449 | 21.0429 | 20.2951 | 20.3718 | 20.2299 | 20.1972 | 20.0973 |  | 20.2207 | 19.7779 | 20.1258 | 19.6694 | 20.0771 | 20.2913 |  | 20.3987 |  |  | 20.328 | 20.3977 | 20.6378 | [5 empty] | 21.9324 | 20.3244 | 21.6655 | 22.0468 | 19.5317 | 21.1516 | 21.7705 | 19.3486 | 19.904 | 21.1254 |  | 19.8053 | 20.8883 | 18.871 | 19.6712 | 20.7884 | 19.4008 | 20.0405 | 19.055 | 20.0786 | 19.1441 | 20.1789 | 18.8128 | 20.103 | 21.0263 | 19.4311 | 19.7412 | 20.9779 | 18.9069 | 19.8093 | 20.7837 | 19.0161 | 20.0683 | 19.3083 | 19.9156 | 18.8959 | 20.1001 | -0.022578 | 20.9448 | 0.048352 | 0.011914 | -27.0741 | 3.0965 | -17.89 | -0.15 | 0.88615 | -0.47628 | -10.8293 | 1.0044 | 0.35143 | -16.7088 | 1.3499 | 0.42343 | 0.42912 | 0.4305 | 0.39755 | 0.44909 | 0.43807 | 0.4276
42838.4181 | -185 | 22.903 | 22.8657 | 22.8518 | 22.781 | 22.41 | 21.7458 | 22.7205 | 21.8151 | 22.3691 | 22.381 | 22.3594 | 22.031 | 21.2468 | 22.2155 | 21.5988 | 21.7692 | 21.9002 | 21.0906 | 21.1822 | 21.3993 | 20.4835 | 20.622 | 20.9145 | 21.8921 | 21.6538 | 21.2804 | 20.2931 | 20.411 | 20.3588 | 22.0666 | 21.6672 | 21.1867 | 22.0026 | 21.7399 | 21.3552 | 19.9235 | 20.4434 |  | 20.5045 | 20.0371 | 20.1399 | 19.22 |  | 16.9072 | 16.8542 | 16.5933 | 16.808 | 16.8647 | 17.3602 | 17.6754 | 16.0913 | 16.9018 | 16.39 | 16.9924 | 17.9454 | 42.7749 | 42.2556 | 42.0247 | 21.3851 |  |  | 0.46087 | -0.14069 | -84.3028 | 0.51973 | 0.35563 | -197.7868 | 0.89854 | -0.15084 | -0.064903 | 0.071233 | 0.13639 | 8.8288 | 9.0584 | 1.9784 | 21.7858 | 22.0005 | 22.1925 | 22.2595 | 22.085 | 21.4009 | 20.2118 | 22.1926 | 22.3674 | 22.4007 | 22.352 | 21.9763 | 21.2053 | 22.2546 | 17.2238 | 17.2614 | 16.4729 | 16.349 | 16.3974 | 17.1488 | 16.9226 | 22.3932 | 22.1535 | 21.71 | 22.0886 | 21.8044 | 21.3056 | 21.9455 | 21.5274 | 20.9022 | 20.0932 | 20.3011 | 19.849 | 19.8117 | 0.11896 | 0.14116 | 20.7667 | 22.0736 | 22.3732 | 20.1086 | 21.6683 | 22.1174 | 21.9487 | 21.7138 | 21.2779 | 21.7793 | 21.4447 | 21.032 | 20.2886 | 20.3634 | 20.2262 | 20.1929 | 20.1001 |  | 20.2207 | 19.7585 | 20.1263 | 19.666 | 20.0725 | 20.2849 |  | 20.3924 |  |  | 20.3188 | 20.4042 | 20.6354 | [5 empty] | 21.9369 | 20.3295 | 21.674 | 22.0427 | 19.5323 | 21.1605 | 21.78 | 19.3493 | 19.901 | 21.1234 |  | 19.7979 | 20.8882 | 18.8773 | 19.665 | 20.7832 | 19.3975 | 20.046 | 19.0545 | 20.0732 | 19.1558 | 20.1822 | 18.8139 | 20.107 | 21.027 | 19.4256 | 19.747 | 20.9771 | 18.9094 | 19.8092 | 20.7819 | 19.0139 | 20.0681 | 19.3026 | 19.9063 | 18.8823 | 20.0994 | -0.07155 | 20.9439 | 0.048714 | 0.014752 | -27.0834 | 3.0965 | -5.7 | -0.17 | 0.81053 | -0.44514 | -10.8966 | 0.85558 | 0.70835 | -16.705 | 1.1259 | 0.42335 | 0.42968 | 0.43045 | 0.39435 | 0.45139 | 0.43784 | 0.42709
42838.4181 | -184 | 22.9023 | 22.868 | 22.8538 | 22.7765 | 22.4118 | 21.7446 | 22.718 | 21.8082 | 22.3737 | 22.3773 | 22.3627 | 22.0337 | 21.2505 | 22.2167 | 21.5922 | 21.7554 | 21.8897 | 21.0882 | 21.1757 | 21.3898 | 20.4699 | 20.6154 | 20.901 | 21.8833 | 21.6424 | 21.2791 | 20.284 | 20.4054 | 20.3533 | 22.0655 | 21.6703 | 21.1893 | 21.994 | 21.7421 | 21.3506 | 19.92 | 20.4349 |  | 20.5022 | 20.0393 | 20.1394 | 19.2257 |  | 16.906 | 16.8419 | 16.5943 | 16.7992 | 16.8562 | 17.343 | 17.6574 | 16.0967 | 16.8892 | 16.3827 | 16.989 | 17.9481 | 42.6736 | 42.2471 | 41.9348 | 21.3881 |  |  | 0.61201 | -0.28 | -84.7779 | 0.66824 | 0.1907 | -197.8033 | 0.68958 | -0.24941 | 0.0069044 | 0.19145 | 0.10254 | 8.8294 | 9.0592 | 1.9783 | 21.789 | 22.01 | 22.2043 | 22.2702 | 22.0957 | 21.4167 | 20.2199 | 22.2053 | 22.373 | 22.4132 | 22.3622 | 21.9848 | 21.2131 | 22.2716 | 17.2367 | 17.2464 | 16.4927 | 16.3432 | 16.4082 | 17.1448 | 16.9161 | 22.3914 | 22.1493 | 21.7042 | 22.0821 | 21.8017 | 21.2995 | 21.9433 | 21.5255 | 20.8938 | 20.0946 | 20.3029 | 19.8425 | 19.8094 | 0.065283 | 0.30606 | 20.7588 | 22.0663 | 22.3723 | 20.1051 | 21.6585 | 22.1067 | 21.9431 | 21.7046 | 21.276 | 21.7729 | 21.4374 | 21.0279 | 20.2814 | 20.3546 | 20.2285 | 20.1942 | 20.1045 |  | 20.2238 | 19.7542 | 20.1327 | 19.6714 | 20.0747 | 20.2882 |  | 20.3887 |  |  | 20.316 | 20.4029 | 20.6179 | [5 empty] | 21.9213 | 20.3191 | 21.6673 | 22.0376 | 19.5211 | 21.1567 | 21.7759 | 19.3405 | 19.9094 | 21.1342 |  | 19.8027 | 20.8979 | 18.8818 | 19.6676 | 20.7915 | 19.4054 | 20.0551 | 19.0582 | 20.0777 | 19.16 | 20.1903 | 18.8122 | 20.1089 | 21.0254 | 19.4265 | 19.7404 | 20.969 | 18.9091 | 19.8075 | 20.7897 | 19.0217 | 20.0688 | 19.2989 | 19.9128 | 18.8879 | 20.0958 | -0.19194 | 20.945 | 0.048788 | 0.015065 | -27.0639 | 3.0965 | -13.58 | -0.14 | 0.93401 | -0.62797 | -10.927 | 0.97012 | 0.51869 | -16.7052 | 0.98634 | 0.42333 | 0.43001 | 0.43037 | 0.39245 | 0.44845 | 0.43757 | 0.4272
42838.4182 | -183 | 22.9018 | 22.8654 | 22.851 | 22.7773 | 22.4102 | 21.7396 | 22.7148 | 21.8036 | 22.3664 | 22.3826 | 22.3592 | 22.0225 | 21.2435 | 22.2087 | 21.6013 | 21.7687 | 21.8909 | 21.08 | 21.1763 | 21.3946 | 20.4735 | 20.6089 | 20.9064 | 21.8867 | 21.6425 | 21.2759 | 20.2747 | 20.4078 | 20.3564 | 22.0634 | 21.6778 | 21.195 | 21.9964 | 21.7415 | 21.3573 | 19.9261 | 20.4436 |  | 20.5092 | 20.0462 | 20.1393 | 19.2392 |  | 16.9135 | 16.8525 | 16.5989 | 16.8059 | 16.8597 | 17.3409 | 17.6768 | 16.1228 | 16.8941 | 16.3769 | 16.997 | 17.944 | 42.5734 | 42.2446 | 41.832 | 21.3869 |  |  | 0.43393 | -0.13806 | -85.6066 | 0.72213 | 0.18807 | -197.8066 | 0.80194 | -0.41763 | -0.13671 | 0.23425 | 0.11626 | 8.8282 | 9.058 | 1.9783 | 21.7772 | 22.0011 | 22.2004 | 22.2629 | 22.0835 | 21.4062 | 20.2157 | 22.197 | 22.3642 | 22.4067 | 22.3565 | 21.9797 | 21.2108 | 22.267 | 17.2501 | 17.2523 | 16.52 | 16.357 | 16.4273 | 17.1441 | 16.9218 | 22.3999 | 22.1537 | 21.714 | 22.0865 | 21.8067 | 21.3062 | 21.9459 | 21.5298 | 20.9027 | 20.1069 | 20.308 | 19.8498 | 19.82 | 0.16948 | 0.025328 | 20.7664 | 22.0712 | 22.377 | 20.1115 | 21.6714 | 22.1097 | 21.9478 | 21.709 | 21.2774 | 21.7775 | 21.4403 | 21.0393 | 20.2905 | 20.3575 | 20.2394 | 20.1959 | 20.1184 |  | 20.2245 | 19.7492 | 20.1427 | 19.6811 | 20.0895 | 20.2966 |  | 20.4012 |  |  | 20.3189 | 20.4059 | 20.6323 | [5 empty] | 21.9282 | 20.3245 | 21.6617 | 22.0424 | 19.5269 | 21.1604 | 21.7781 | 19.341 | 19.8977 | 21.1267 |  | 19.7996 | 20.8899 | 18.8841 | 19.6635 | 20.7933 | 19.3936 | 20.0534 | 19.0541 | 20.0719 | 19.1497 | 20.1863 | 18.8203 | 20.1118 | 21.0279 | 19.43 | 19.7414 | 20.9752 | 18.9169 | 19.8169 | 20.7875 | 19.0294 | 20.0727 | 19.3081 | 19.9204 | 18.8922 | 20.1033 | -0.022021 | 20.9444 | 0.048555 | 0.015188 | -27.027 | 3.0965 | -9.42 | -0.05 | 0.78647 | -0.44096 | -10.9805 | 1.0085 | 0.5151 | -16.7053 | 1.0637 | 0.42297 | 0.43049 | 0.4306 | 0.39088 | 0.44607 | 0.4374 | 0.42732
42838.4182 | -182 | 22.8927 | 22.8553 | 22.8465 | 22.776 | 22.4041 | 21.7342 | 22.7193 | 21.8028 | 22.3714 | 22.3723 | 22.3512 | 22.0275 | 21.236 | 22.2077 | 21.5979 | 21.7675 | 21.8934 | 21.075 | 21.1717 | 21.3968 | 20.4757 | 20.6145 | 20.9051 | 21.8874 | 21.6491 | 21.2723 | 20.2802 | 20.4076 | 20.3605 | 22.0658 | 21.6803 | 21.1915 | 22.0009 | 21.7392 | 21.3565 | 19.9304 | 20.44 |  | 20.4999 | 20.0388 | 20.1359 | 19.2369 |  | 16.9189 | 16.8601 | 16.6003 | 16.8038 | 16.8619 | 17.3455 | 17.6962 | 16.1297 | 16.8993 | 16.3807 | 17.0025 | 17.9473 | 42.47 | 42.2531 | 41.7358 | 21.3915 |  |  | 0.56535 | -0.16106 | -85.4068 | 0.71227 | 0.19201 | -197.8532 | 0.34853 | -0.58388 | -0.20151 | 0.27012 | 0.13119 | 8.8288 | 9.0585 | 1.9779 | 21.7836 | 22.0106 | 22.2033 | 22.2573 | 22.0934 | 21.4072 | 20.2236 | 22.2035 | 22.3727 | 22.4087 | 22.3586 | 21.9821 | 21.2198 | 22.2693 | 17.2658 | 17.2611 | 16.5172 | 16.361 | 16.4261 | 17.1492 | 16.9286 | 22.3959 | 22.152 | 21.7117 | 22.0838 | 21.7993 | 21.3103 | 21.9461 | 21.5245 | 20.9009 | 20.1079 | 20.3024 | 19.8514 | 19.8164 | 0.14884 | 0.097413 | 20.7631 | 22.0689 | 22.371 | 20.1169 | 21.6704 | 22.1124 | 21.9367 | 21.7038 | 21.2738 | 21.7782 | 21.4361 | 21.0384 | 20.2934 | 20.3616 | 20.2348 | 20.1944 | 20.104 |  | 20.2272 | 19.7424 | 20.1351 | 19.6861 | 20.0879 | 20.2975 |  | 20.3996 |  |  | 20.3117 | 20.4027 | 20.6372 | [5 empty] | 21.9332 | 20.3213 | 21.668 | 22.0419 | 19.5327 | 21.1621 | 21.7818 | 19.3405 | 19.9014 | 21.1241 |  | 19.8048 | 20.8879 | 18.8812 | 19.6627 | 20.7879 | 19.402 | 20.0491 | 19.0644 | 20.0788 | 19.157 | 20.1878 | 18.8146 | 20.1174 | 21.0332 | 19.4377 | 19.7457 | 20.9762 | 18.9206 | 19.8115 | 20.7901 | 19.031 | 20.0738 | 19.3116 | 19.9174 | 18.8952 | 20.1086 | 0.020272 | 20.9449 | 0.049267 | 0.014208 | -27.0112 | 3.0965 | -6.42 | -0.08 | 0.89771 | -0.47628 | -10.9678 | 1.0016 | 0.52047 | -16.7074 | 0.70123 | 0.42346 | 0.43042 | 0.4304 | 0.38973 | 0.44717 | 0.4376 | 0.42745
42838.4182 | -181 | 22.9038 | 22.8604 | 22.8554 | 22.779 | 22.4039 | 21.7445 | 22.7249 | 21.8016 | 22.3696 | 22.3785 | 22.3569 | 22.028 | 21.2489 | 22.2143 | 21.5917 | 21.7635 | 21.8914 | 21.0774 | 21.1767 | 21.3906 | 20.4692 | 20.6136 | 20.9032 | 21.882 | 21.6458 | 21.2722 | 20.2904 | 20.4072 | 20.3591 | 22.0676 | 21.6767 | 21.1887 | 21.9984 | 21.738 | 21.356 | 19.9154 | 20.4356 |  | 20.5001 | 20.0471 | 20.1344 | 19.2433 |  | 16.9211 | 16.8486 | 16.6081 | 16.7997 | 16.8515 | 17.3607 | 17.7092 | 16.1312 | 16.8966 | 16.4026 | 17.0047 | 17.943 | 42.3659 | 42.2687 | 41.6338 | 21.3841 |  |  | 0.4175 | -0.10586 | -86.4082 | 0.2536 | 0.32475 | -197.8631 | 0.62584 | -0.5208 | -0.017421 | 0.033889 | 0.094035 | 8.8296 | 9.0597 | 1.9781 | 21.7802 | 22.0032 | 22.2022 | 22.2576 | 22.0816 | 21.3999 | 20.2122 | 22.1915 | 22.3698 | 22.4049 | 22.3506 | 21.974 | 21.2116 | 22.2672 | 17.2819 | 17.28 | 16.5007 | 16.3673 | 16.4171 | 17.1494 | 16.9357 | 22.3926 | 22.1577 | 21.7131 | 22.0846 | 21.8033 | 21.3025 | 21.9503 | 21.5332 | 20.9082 | 20.1 | 20.3062 | 19.8503 | 19.8152 | 0.13586 | 0.084099 | 20.7569 | 22.0722 | 22.3755 | 20.1143 | 21.6694 | 22.1125 | 21.9379 | 21.7035 | 21.2752 | 21.7793 | 21.4397 | 21.0378 | 20.2911 | 20.3561 | 20.2312 | 20.1959 | 20.0869 |  | 20.2262 | 19.7577 | 20.1381 | 19.7013 | 20.0887 | 20.3045 |  | 20.3949 |  |  | 20.3114 | 20.4022 | 20.6334 | [5 empty] | 21.9321 | 20.3218 | 21.6593 | 22.042 | 19.5268 | 21.1595 | 21.7782 | 19.3364 | 19.9013 | 21.1243 |  | 19.8091 | 20.886 | 18.8803 | 19.6653 | 20.7898 | 19.4015 | 20.0438 | 19.062 | 20.0768 | 19.1528 | 20.1995 | 18.8124 | 20.1166 | 21.0363 | 19.4373 | 19.7444 | 20.9788 | 18.9152 | 19.8116 | 20.7939 | 19.0296 | 20.0748 | 19.3066 | 19.9168 | 18.8959 | 20.1101 | -0.026288 | 20.9466 | 0.049495 | 0.015007 | -27.0188 | 3.0964 | -15.82 | -0.12 | 0.77144 | -0.38613 | -11.0317 | 0.59764 | 0.6769 | -16.7082 | 0.93968 | 0.4239 | 0.43009 | 0.43001 | 0.38797 | 0.44983 | 0.43692 | 0.42722
42838.4182 | -180 | 22.8957 | 22.854 | 22.8485 | 22.7718 | 22.4023 | 21.7405 | 22.7192 | 21.8105 | 22.369 | 22.3709 | 22.3512 | 22.0153 | 21.2357 | 22.2062 | 21.5858 | 21.763 | 21.8849 | 21.0779 | 21.1765 | 21.3902 | 20.4711 | 20.6121 | 20.9059 | 21.8825 | 21.6421 | 21.2731 | 20.2907 | 20.4106 | 20.3611 | 22.0564 | 21.6713 | 21.1847 | 21.9867 | 21.7332 | 21.3438 | 19.9211 | 20.4239 |  | 20.5 | 20.0278 | 20.1277 | 19.2459 |  | 16.9259 | 16.8495 | 16.6106 | 16.7938 | 16.851 | 17.3579 | 17.7006 | 16.1371 | 16.8888 | 16.4032 | 17.0102 | 17.946 | 42.2563 | 42.292 | 41.539 | 21.3832 |  |  | 0.41553 | -0.1604 | -87.5529 | 0.55062 | 0.29649 | -197.8427 | 0.070573 | -0.40646 | 0.13262 | 0.092633 | -0.0089096 | 8.8293 | 9.0591 | 1.9788 | 21.7752 | 22.0052 | 22.2007 | 22.2602 | 22.0872 | 21.4036 | 20.2165 | 22.2006 | 22.3727 | 22.406 | 22.3515 | 21.9776 | 21.2155 | 22.2688 | 17.2893 | 17.2848 | 16.4674 | 16.3672 | 16.4066 | 17.153 | 16.9355 | 22.3858 | 22.1567 | 21.7073 | 22.0865 | 21.8054 | 21.3087 | 21.946 | 21.5317 | 20.901 | 20.1044 | 20.3064 | 19.8529 | 19.8094 | 0.082781 | 0.01772 | 20.7601 | 22.0838 | 22.3832 | 20.1142 | 21.6693 | 22.1123 | 21.9459 | 21.7145 | 21.2788 | 21.7838 | 21.4522 | 21.0428 | 20.2943 | 20.366 | 20.242 | 20.1943 | 20.0999 |  | 20.2283 | 19.7654 | 20.1316 | 19.7059 | 20.0801 | 20.2916 |  | 20.4004 |  |  | 20.3146 | 20.4004 | 20.6337 | [5 empty] | 21.9285 | 20.3167 | 21.6609 | 22.0399 | 19.5288 | 21.1632 | 21.7737 | 19.3369 | 19.8965 | 21.1207 |  | 19.8028 | 20.8813 | 18.8781 | 19.6619 | 20.7861 | 19.3953 | 20.0379 | 19.0588 | 20.0744 | 19.1477 | 20.1845 | 18.8067 | 20.1053 | 21.0226 | 19.4269 | 19.7406 | 20.9721 | 18.9025 | 19.806 | 20.7805 | 19.0223 | 20.0667 | 19.3014 | 19.9075 | 18.8874 | 20.1014 | -0.062831 | 20.9443 | 0.048776 | 0.014527 | -27.0568 | 3.0964 | -23.76 | -0.15 | 0.76962 | -0.4753 | -11.1045 | 0.88062 | 0.64677 | -16.7073 | 0.31555 | 0.42361 | 0.42966 | 0.42959 | 0.38757 | 0.45351 | 0.43705 | 0.42753
42838.4182 | -179 | 22.8953 | 22.8679 | 22.8531 | 22.7771 | 22.4067 | 21.7412 | 22.7233 | 21.8115 | 22.3723 | 22.3781 | 22.359 | 22.0309 | 21.2472 | 22.2224 | 21.5881 | 21.7619 | 21.8894 | 21.0746 | 21.1766 | 21.3946 | 20.4745 | 20.6117 | 20.904 | 21.8849 | 21.6469 | 21.2738 | 20.2908 | 20.4054 | 20.3604 | 22.0604 | 21.6732 | 21.1919 | 21.9925 | 21.7322 | 21.346 | 19.9189 | 20.4178 |  | 20.5066 | 20.0322 | 20.1286 | 19.2476 |  | 16.9286 | 16.865 | 16.6107 | 16.7968 | 16.8523 | 17.3457 | 17.6981 | 16.1439 | 16.9043 | 16.3906 | 17.0085 | 17.9435 | 42.1439 | 42.3276 | 41.4396 | 21.3816 |  |  | 0.49504 | -0.081549 | -87.7612 | 0.29237 | 0.24655 | -197.8572 | 0.11526 | -0.50766 | 0.12094 | 0.13606 | 0.099243 | 8.8295 | 9.0594 | 1.9788 | 21.7861 | 22.0029 | 22.1985 | 22.2654 | 22.0917 | 21.4107 | 20.2194 | 22.2001 | 22.3671 | 22.4022 | 22.3609 | 21.9849 | 21.2252 | 22.2693 | 17.3 | 17.302 | 16.4443 | 16.3691 | 16.4013 | 17.1598 | 16.926 | 22.3845 | 22.1544 | 21.7058 | 22.0827 | 21.7964 | 21.3029 | 21.9375 | 21.5253 | 20.8969 | 20.0987 | 20.3029 | 19.8446 | 19.7926 | 0.11699 | 0.20202 | 20.755 | 22.0884 | 22.3892 | 20.1237 | 21.6781 | 22.1181 | 21.9556 | 21.7182 | 21.2869 | 21.78 | 21.4573 | 21.0483 | 20.293 | 20.3741 | 20.2459 | 20.1994 | 20.1031 |  | 20.2282 | 19.7742 | 20.1283 | 19.7065 | 20.0761 | 20.292 |  | 20.3997 |  |  | 20.3104 | 20.4019 | 20.6385 | [5 empty] | 21.9326 | 20.3231 | 21.6678 | 22.0443 | 19.5317 | 21.1656 | 21.7747 | 19.3339 | 19.8921 | 21.1225 |  | 19.8084 | 20.8724 | 18.8768 | 19.6523 | 20.7908 | 19.3925 | 20.0382 | 19.0503 | 20.0722 | 19.1489 | 20.1821 | 18.8125 | 20.1022 | 21.0184 | 19.4267 | 19.7444 | 20.9725 | 18.9046 | 19.803 | 20.7829 | 19.0214 | 20.0678 | 19.3062 | 19.9065 | 18.8887 | 20.1007 | -0.13443 | 20.9444 | 0.048739 | 0.01362 | -26.9873 | 3.0965 | -5 | 0.05 | 0.84004 | -0.33891 | -11.118 | 0.64172 | 0.58978 | -16.7075 | 0.40325 | 0.42352 | 0.42931 | 0.42944 | 0.38717 | 0.45497 | 0.43692 | 0.42781
42838.4182 | -178 | 22.8951 | 22.8638 | 22.8487 | 22.7773 | 22.4067 | 21.7372 | 22.7141 | 21.8033 | 22.3711 | 22.3696 | 22.3621 | 22.0293 | 21.2503 | 22.2182 | 21.5901 | 21.7587 | 21.8853 | 21.0687 | 21.1742 | 21.3909 | 20.47 | 20.613 | 20.8961 | 21.8815 | 21.645 | 21.2639 | 20.284 | 20.409 | 20.3576 | 22.0649 | 21.6664 | 21.187 | 21.9959 | 21.7316 | 21.3506 | 19.9157 | 20.4117 |  | 20.4997 | 20.029 | 20.1276 | 19.2521 |  | 16.9255 | 16.8519 | 16.6112 | 16.7974 | 16.8477 | 17.326 | 17.6631 | 16.1509 | 16.8971 | 16.3516 | 17.0069 | 17.9497 | 42.0483 | 42.3736 | 41.3362 | 21.389 |  |  | 0.49964 | -0.25306 | -88.101 | 0.61765 | 0.20055 | -197.8834 | -0.20213 | -0.507 | 0.065284 | -0.08234 | -0.087898 | 8.8285 | 9.0584 | 1.9783 | 21.7797 | 21.9993 | 22.1888 | 22.2564 | 22.0856 | 21.4034 | 20.2162 | 22.1972 | 22.3748 | 22.4012 | 22.3581 | 21.9792 | 21.2109 | 22.2671 | 17.3118 | 17.3178 | 16.4356 | 16.3781 | 16.3997 | 17.1601 | 16.9324 | 22.3876 | 22.149 | 21.7062 | 22.0873 | 21.7913 | 21.301 | 21.9439 | 21.5264 | 20.9002 | 20.0951 | 20.3073 | 19.8467 | 19.796 | 0.13704 | 0.22333 | 20.7574 | 22.086 | 22.3819 | 20.1267 | 21.6763 | 22.1193 | 21.9537 | 21.7177 | 21.284 | 21.7805 | 21.4503 | 21.0471 | 20.2921 | 20.3778 | 20.2401 | 20.1964 | 20.0925 |  | 20.2257 | 19.7827 | 20.1276 | 19.7128 | 20.083 | 20.2882 |  | 20.3964 |  |  | 20.3025 | 20.3995 | 20.6389 | [5 empty] | 21.9335 | 20.3255 | 21.6738 | 22.0458 | 19.5287 | 21.1639 | 21.7792 | 19.3325 | 19.8981 | 21.12 |  | 19.81 | 20.8759 | 18.881 | 19.6529 | 20.7925 | 19.395 | 20.0399 | 19.0529 | 20.073 | 19.1541 | 20.1849 | 18.809 | 20.1024 | 21.0174 | 19.4236 | 19.7421 | 20.9662 | 18.9104 | 19.8025 | 20.7865 | 19.0279 | 20.0665 | 19.3054 | 19.9047 | 18.8966 | 20.0955 | 0.017304 | 20.945 | 0.047479 | 0.012872 | -27.0232 | 3.0964 | -9.17 | -0.06 | 0.84393 | -0.597 | -11.1393 | 0.93269 | 0.53191 | -16.7081 | -0.53399 | 0.42373 | 0.42905 | 0.42949 | 0.38589 | 0.45668 | 0.43669 | 0.42759
42838.4182 | -177 | 22.8945 | 22.8588 | 22.8416 | 22.7696 | 22.404 | 21.7362 | 22.7147 | 21.8055 | 22.3645 | 22.3709 | 22.3547 | 22.0257 | 21.2402 | 22.2133 | 21.5889 | 21.7632 | 21.8923 | 21.0754 | 21.1717 | 21.3959 | 20.4691 | 20.6103 | 20.8999 | 21.8764 | 21.6453 | 21.2708 | 20.2819 | 20.4167 | 20.365 | 22.0644 | 21.6649 | 21.1847 | 21.9988 | 21.733 | 21.3469 | 19.9097 | 20.4074 |  | 20.4956 | 20.0239 | 20.1308 | 19.2496 |  | 16.9275 | 16.854 | 16.6081 | 16.7999 | 16.8387 | 17.3164 | 17.6447 | 16.1666 | 16.8903 | 16.2791 | 17.0015 | 17.9455 | 41.9445 | 42.4186 | 41.2365 | 21.3766 |  |  | 0.41684 | -0.13412 | -88.0195 | 0.92452 | 0.031016 | -197.823 | 0.8624 | -0.3736 | -0.045054 | -0.1264 | 0.065391 | 8.8297 | 9.0596 | 1.9784 | 21.7886 | 22.0093 | 22.2006 | 22.2635 | 22.0884 | 21.4092 | 20.2235 | 22.1973 | 22.3709 | 22.4074 | 22.3578 | 21.9861 | 21.2069 | 22.2697 | 17.3069 | 17.2902 | 16.4235 | 16.3837 | 16.3942 | 17.1562 | 16.9223 | 22.3875 | 22.1515 | 21.7106 | 22.0841 | 21.801 | 21.3019 | 21.9469 | 21.5268 | 20.9058 | 20.0897 | 20.3126 | 19.854 | 19.7953 | 0.04641 | 0.17825 | 20.7522 | 22.0768 | 22.3728 | 20.1161 | 21.6611 | 22.1141 | 21.9445 | 21.7107 | 21.2735 | 21.7786 | 21.4428 | 21.0401 | 20.2875 | 20.3685 | 20.2383 | 20.1961 | 20.0888 |  | 20.223 | 19.7934 | 20.1371 | 19.7164 | 20.0828 | 20.2963 |  | 20.4031 |  |  | 20.297 | 20.3852 | 20.6329 | [5 empty] | 21.9327 | 20.3193 | 21.664 | 22.0407 | 19.5307 | 21.1627 | 21.7778 | 19.3339 | 19.9044 | 21.1197 |  | 19.8059 | 20.8806 | 18.8822 | 19.6597 | 20.779 | 19.3936 | 20.04 | 19.052 | 20.0649 | 19.1595 | 20.1834 | 18.8066 | 20.1084 | 21.0192 | 19.4243 | 19.7428 | 20.9716 | 18.9051 | 19.8022 | 20.7786 | 19.0331 | 20.0619 | 19.3112 | 19.9127 | 18.8988 | 20.0985 | 0.095586 | 20.9451 | 0.047338 | 0.013279 | -27.1325 | 3.0965 | -8.15 | -0.16 | 0.77085 | -0.43462 | -11.1342 | 1.1411 | 0.20917 | -16.7053 | 1.103 | 0.42374 | 0.42907 | 0.42939 | 0.38597 | 0.45685 | 0.43656 | 0.42743
42838.4182 | -176 | 22.9016 | 22.8572 | 22.8484 | 22.7668 | 22.4092 | 21.743 | 22.7213 | 21.8094 | 22.365 | 22.3774 | 22.3549 | 22.0318 | 21.246 | 22.2133 | 21.576 | 21.7533 | 21.8914 | 21.0735 | 21.1685 | 21.3854 | 20.4689 | 20.6063 | 20.8985 | 21.8741 | 21.6475 | 21.2703 | 20.2777 | 20.4057 | 20.3673 | 22.0651 | 21.6734 | 21.1931 | 21.999 | 21.7455 | 21.352 | 19.9193 | 20.41 |  | 20.5126 | 20.0383 | 20.135 | 19.2492 |  | 16.9381 | 16.8713 | 16.617 | 16.8006 | 16.8469 | 17.3108 | 17.6374 | 16.171 | 16.8974 | 16.2084 | 17.0046 | 17.9465 | 41.8383 | 42.4743 | 41.1379 | 21.3788 |  |  | 0.33733 | 0.023591 | -88.6188 | 0.6551 | 0.11447 | -197.8355 | -0.23893 | -0.53985 | -0.14819 | -0.14507 | 0.023033 | 8.829 | 9.0588 | 1.9785 | 21.7813 | 22.0061 | 22.1937 | 22.2529 | 22.084 | 21.4005 | 20.2085 | 22.1894 | 22.3667 | 22.4012 | 22.3488 | 21.9851 | 21.2033 | 22.2621 | 17.3296 | 17.2695 | 16.3955 | 16.3887 | 16.4027 | 17.1569 | 16.9262 | 22.3875 | 22.1524 | 21.7107 | 22.0803 | 21.7993 | 21.3054 | 21.9458 | 21.5252 | 20.9092 | 20.1008 | 20.3149 | 19.8476 | 19.7928 | 0.09497 | 0.10046 | 20.7515 | 22.0711 | 22.3728 | 20.1129 | 21.6669 | 22.1072 | 21.9446 | 21.7084 | 21.276 | 21.7699 | 21.4414 | 21.047 | 20.2795 | 20.3644 | 20.2405 | 20.1913 | 20.0782 |  | 20.2269 | 19.8057 | 20.1349 | 19.7065 | 20.09 | 20.2998 |  | 20.3997 |  |  | 20.2925 | 20.367 | 20.6276 | [5 empty] | 21.9248 | 20.3178 | 21.656 | 22.0395 | 19.5292 | 21.1543 | 21.7758 | 19.3446 | 19.9029 | 21.1253 |  | 19.8068 | 20.8846 | 18.888 | 19.6599 | 20.7882 | 19.3887 | 20.0408 | 19.0483 | 20.0717 | 19.1554 | 20.1866 | 18.8018 | 20.1039 | 21.0172 | 19.4263 | 19.7423 | 20.968 | 18.9005 | 19.7956 | 20.7757 | 19.034 | 20.0578 | 19.3088 | 19.9122 | 18.8922 | 20.0987 | -0.061718 | 20.9443 | 0.048641 | 0.014469 | -27.105 | 3.0965 | -4.35 | -0.07 | 0.69344 | 0.18229 | -11.1724 | 0.96059 | 0.40184 | -16.7056 | -0.58056 | 0.42417 | 0.42865 | 0.4299 | 0.38354 | 0.46042 | 0.43689 | 0.42787
42838.4183 | -175 | 22.9129 | 22.8677 | 22.8583 | 22.7831 | 22.4183 | 21.7525 | 22.7226 | 21.814 | 22.3737 | 22.3853 | 22.3677 | 22.0326 | 21.257 | 22.2209 | 21.5908 | 21.762 | 21.8947 | 21.0728 | 21.1723 | 21.3901 | 20.4759 | 20.6224 | 20.912 | 21.8861 | 21.6529 | 21.2842 | 20.2857 | 20.4152 | 20.371 | 22.0685 | 21.6731 | 21.1853 | 22.0009 | 21.7394 | 21.351 | 19.9151 | 20.3997 |  | 20.5033 | 20.0338 | 20.1379 | 19.2479 |  | 16.9469 | 16.8855 | 16.6315 | 16.8055 | 16.8606 | 17.3021 | 17.6469 | 16.1714 | 16.8987 | 16.185 | 16.9965 | 17.9516 | 41.7375 | 42.555 | 41.0419 | 21.3848 |  |  | 0.44247 | -6.5e-05 | -88.6359 | 1.031 | 0.1309 | -197.7954 | -0.19161 | -0.36703 | -0.057897 | 0.089066 | -0.09189 | 8.8286 | 9.0584 | 1.9782 | 21.7876 | 22.0072 | 22.2021 | 22.2664 | 22.0931 | 21.4071 | 20.2126 | 22.1983 | 22.3645 | 22.4048 | 22.3534 | 21.9832 | 21.209 | 22.2672 | 17.3438 | 17.2546 | 16.3876 | 16.3943 | 16.4037 | 17.1555 | 16.9306 | 22.3949 | 22.1595 | 21.7109 | 22.0925 | 21.8001 | 21.3134 | 21.9451 | 21.5278 | 20.9088 | 20.1088 | 20.317 | 19.859 | 19.8051 | 0.082781 | 0.11681 | 20.754 | 22.0732 | 22.3753 | 20.1118 | 21.6723 | 22.11 | 21.9465 | 21.708 | 21.2824 | 21.7775 | 21.4464 | 21.0407 | 20.2874 | 20.3622 | 20.2472 | 20.1828 | 20.0812 |  | 20.232 | 19.8149 | 20.145 | 19.7124 | 20.0858 | 20.2997 |  | 20.4091 |  |  | 20.2968 | 20.372 | 20.6329 | [5 empty] | 21.9306 | 20.3259 | 21.6655 | 22.0527 | 19.5364 | 21.1666 | 21.7782 | 19.3349 | 19.9042 | 21.1165 |  | 19.8075 | 20.8773 | 18.8783 | 19.6588 | 20.7837 | 19.3804 | 20.0369 | 19.0345 | 20.0692 | 19.1447 | 20.1864 | 18.805 | 20.1201 | 21.0179 | 19.4308 | 19.7406 | 20.9744 | 18.9083 | 19.7971 | 20.7909 | 19.033 | 20.072 | 19.3126 | 19.9179 | 18.9008 | 20.1094 | 0.028249 | 20.9451 | 0.048899 | 0.014607 | -27.0475 | 3.0965 | -4.29 | 0.04 | 0.7942 | -0.0095686 | -11.1737 | 1.2051 | 0.4297 | -16.7037 | -0.5199 | 0.42425 | 0.42874 | 0.4296 | 0.3818 | 0.4618 | 0.43679 | 0.4278
42838.4183 | -174 | 22.9014 | 22.8631 | 22.851 | 22.7775 | 22.3978 | 21.7427 | 22.7173 | 21.8041 | 22.3733 | 22.3821 | 22.3575 | 22.0233 | 21.2368 | 22.2276 | 21.5883 | 21.7719 | 21.8928 | 21.0876 | 21.1764 | 21.3963 | 20.4835 | 20.6225 | 20.9109 | 21.8848 | 21.6586 | 21.2841 | 20.2948 | 20.4179 | 20.3799 | 22.073 | 21.6789 | 21.196 | 22.0026 | 21.7405 | 21.3547 | 19.9227 | 20.3986 |  | 20.5065 | 20.0374 | 20.1354 | 19.2421 |  | 16.9597 | 16.8878 | 16.6363 | 16.8155 | 16.8489 | 17.2909 | 17.6445 | 16.1705 | 16.8997 | 16.1809 | 16.9948 | 17.9547 | 41.6351 | 42.6329 | 40.9493 | 21.3882 |  |  | 0.48124 | 0.080759 | -88.9283 | 0.57165 | 0.10396 | -197.8309 | 0.2112 | -0.44392 | 0.24081 | -0.09325 | -0.0071736 | 8.8293 | 9.0593 | 1.9791 | 21.7868 | 22.0089 | 22.2009 | 22.2679 | 22.0877 | 21.409 | 20.2143 | 22.2004 | 22.3694 | 22.4082 | 22.3591 | 21.9793 | 21.2196 | 22.2674 | 17.3546 | 17.2319 | 16.3796 | 16.4073 | 16.4004 | 17.1562 | 16.9403 | 22.3899 | 22.1481 | 21.7088 | 22.085 | 21.7994 | 21.298 | 21.9432 | 21.5222 | 20.8982 | 20.1007 | 20.3124 | 19.8548 | 19.7969 | -0.043633 | 0.1073 | 20.7525 | 22.0765 | 22.3798 | 20.1085 | 21.664 | 22.1112 | 21.9416 | 21.7105 | 21.2749 | 21.783 | 21.4481 | 21.0403 | 20.2856 | 20.3622 | 20.2479 | 20.183 | 20.0594 |  | 20.224 | 19.8168 | 20.1345 | 19.7235 | 20.0792 | 20.2981 |  | 20.4009 |  |  | 20.302 | 20.3759 | 20.6251 | [5 empty] | 21.9302 | 20.3198 | 21.6694 | 22.0478 | 19.5345 | 21.1619 | 21.7747 | 19.3424 | 19.9062 | 21.1191 |  | 19.8108 | 20.8833 | 18.8805 | 19.6558 | 20.7863 | 19.3966 | 20.0406 | 19.0323 | 20.073 | 19.1594 | 20.1849 | 18.8121 | 20.1124 | 21.0283 | 19.4361 | 19.7439 | 20.9645 | 18.9181 | 19.802 | 20.7895 | 19.0366 | 20.0714 | 19.3102 | 19.916 | 18.9103 | 20.1058 | -0.095294 | 20.9441 | 0.048911 | 0.014556 | -26.9857 | 3.0964 | -17.6 | -0.06 | 0.82827 | 0.33728 | -11.1922 | 0.89734 | 0.38293 | -16.7049 | 0.54581 | 0.42459 | 0.42833 | 0.42907 | 0.38067 | 0.46383 | 0.4372 | 0.42775
42838.4183 | -173 | 22.8921 | 22.8601 | 22.841 | 22.7748 | 22.401 | 21.7399 | 22.7091 | 21.8028 | 22.3677 | 22.3729 | 22.3589 | 22.0171 | 21.2333 | 22.2014 | 21.594 | 21.7658 | 21.897 | 21.0854 | 21.178 | 21.3908 | 20.4709 | 20.6169 | 20.9098 | 21.8883 | 21.654 | 21.2806 | 20.2919 | 20.4243 | 20.3801 | 22.0622 | 21.6637 | 21.1788 | 21.9945 | 21.7224 | 21.3467 | 19.9069 | 20.3784 |  | 20.4925 | 20.0266 | 20.1327 | 19.2369 |  | 16.9742 | 16.9169 | 16.6504 | 16.8257 | 16.8459 | 17.2831 | 17.6229 | 16.1719 | 16.9005 | 16.173 | 16.9941 | 17.954 | 41.5229 | 42.723 | 40.8574 | 21.3844 |  |  | 0.42407 | 0.013075 | -89.4323 | 0.90283 | 0.067156 | -197.8453 | -0.18833 | -0.44523 | 0.06256 | -0.21347 | 0.080842 | 8.8289 | 9.0589 | 1.979 | 21.7899 | 22.0129 | 22.2107 | 22.2634 | 22.0949 | 21.4079 | 20.221 | 22.2054 | 22.3724 | 22.4119 | 22.357 | 21.9896 | 21.2235 | 22.2722 | 17.3705 | 17.226 | 16.3645 | 16.4132 | 16.4064 | 17.1612 | 16.9349 | 22.3897 | 22.1546 | 21.7113 | 22.0849 | 21.7987 | 21.3007 | 21.9491 | 21.532 | 20.9034 | 20.093 | 20.3067 | 19.8586 | 19.7932 | 0.14687 | 0.054048 | 20.7587 | 22.0881 | 22.3826 | 20.1174 | 21.6774 | 22.1177 | 21.9536 | 21.7188 | 21.281 | 21.7812 | 21.4526 | 21.0474 | 20.2931 | 20.3715 | 20.253 | 20.1962 | 20.0609 |  | 20.2269 | 19.8314 | 20.1316 | 19.7225 | 20.081 | 20.2877 |  | 20.402 |  |  | 20.2962 | 20.379 | 20.6149 | [5 empty] | 21.9317 | 20.3207 | 21.6644 | 22.0391 | 19.5266 | 21.149 | 21.7762 | 19.3392 | 19.8955 | 21.124 |  | 19.8013 | 20.868 | 18.8795 | 19.6581 | 20.7836 | 19.3871 | 20.0423 | 19.0209 | 20.0732 | 19.1459 | 20.1881 | 18.8041 | 20.1184 | 21.0212 | 19.4372 | 19.7437 | 20.9687 | 18.9131 | 19.7962 | 20.7824 | 19.0396 | 20.0761 | 19.3063 | 19.9219 | 18.9079 | 20.1012 | -0.068396 | 20.9446 | 0.049206 | 0.014513 | -27.0838 | 3.0965 | 1.57 | -0.11 | 0.77752 | 0.13572 | -11.2244 | 1.1278 | 0.30777 | -16.7052 | -0.51541 | 0.42465 | 0.42783 | 0.42916 | 0.3795 | 0.46488 | 0.43682 | 0.4276
42838.4183 | -172 | 22.8881 | 22.8513 | 22.8416 | 22.7673 | 22.4019 | 21.7433 | 22.7119 | 21.8052 | 22.3629 | 22.367 | 22.3506 | 22.0186 | 21.2412 | 22.2005 | 21.5914 | 21.7671 | 21.8928 | 21.0728 | 21.1726 | 21.3981 | 20.4703 | 20.6111 | 20.904 | 21.8875 | 21.6442 | 21.2777 | 20.2973 | 20.4159 | 20.376 | 22.0695 | 21.6702 | 21.1911 | 22.0016 | 21.7368 | 21.3535 | 19.9192 | 20.3868 |  | 20.4928 | 20.0333 | 20.1379 | 19.251 |  | 16.9824 | 16.9358 | 16.6763 | 16.8518 | 16.8562 | 17.2845 | 17.6012 | 16.2072 | 16.9108 | 16.1985 | 17.0024 | 17.9538 | 41.427 | 42.8204 | 40.7755 | 21.3827 |  |  | 0.36624 | -0.034237 | -89.431 | 0.46848 | 0.19267 | -197.825 | 0.099489 | -0.45903 | 0.11257 | -0.12577 | 0.12997 | 8.8284 | 9.0582 | 1.9792 | 21.7837 | 22.0147 | 22.1936 | 22.2624 | 22.089 | 21.4024 | 20.2161 | 22.2029 | 22.3724 | 22.4082 | 22.354 | 21.9834 | 21.2129 | 22.2683 | 17.3824 | 17.1983 | 16.3595 | 16.3883 | 16.4229 | 17.1578 | 16.9382 | 22.3884 | 22.144 | 21.709 | 22.0821 | 21.7964 | 21.3029 | 21.9448 | 21.5236 | 20.9026 | 20.097 | 20.3078 | 19.8611 | 19.7906 | -0.009228 | 0.034647 | 20.7631 | 22.0798 | 22.3813 | 20.1178 | 21.6727 | 22.117 | 21.9539 | 21.7098 | 21.2816 | 21.78 | 21.4484 | 21.0457 | 20.2842 | 20.3742 | 20.2471 | 20.1884 | 20.0632 |  | 20.2244 | 19.8353 | 20.1324 | 19.7185 | 20.0796 | 20.2866 |  | 20.3929 |  |  | 20.2923 | 20.3819 | 20.6183 | [5 empty] | 21.9401 | 20.3369 | 21.6641 | 22.048 | 19.5293 | 21.1557 | 21.7766 | 19.3442 | 19.9142 | 21.1174 |  | 19.807 | 20.8768 | 18.8825 | 19.6601 | 20.7857 | 19.3998 | 20.0461 | 19.0286 | 20.0638 | 19.1546 | 20.1799 | 18.8043 | 20.1109 | 21.0186 | 19.4277 | 19.7442 | 20.9664 | 18.9127 | 19.792 | 20.7698 | 19.0305 | 20.0661 | 19.3083 | 19.9166 | 18.9067 | 20.1125 | -0.014045 | 20.9445 | 0.049489 | 0.014593 | -27.0595 | 3.0965 | -7.66 | -0.2 | 0.72256 | -0.21962 | -11.2247 | 0.81241 | 0.52131 | -16.7044 | 0.37461 | 0.4245 | 0.42775 | 0.42922 | 0.37777 | 0.46581 | 0.43684 | 0.42781
42838.4183 | -171 | 22.9001 | 22.8623 | 22.8513 | 22.7748 | 22.4068 | 21.7421 | 22.7218 | 21.8057 | 22.3689 | 22.3754 | 22.3546 | 22.0256 | 21.2482 | 22.2122 | 21.5982 | 21.761 | 21.8924 | 21.0763 | 21.1772 | 21.3929 | 20.4737 | 20.6221 | 20.9091 | 21.8839 | 21.6477 | 21.2843 | 20.289 | 20.4263 | 20.3739 | 22.0648 | 21.6718 | 21.188 | 22.0011 | 21.7355 | 21.3522 | 19.9244 | 20.3844 |  | 20.4995 | 20.032 | 20.1308 | 19.2538 |  | 16.9872 | 16.9341 | 16.6819 | 16.8583 | 16.85 | 17.2622 | 17.5651 | 16.2058 | 16.896 | 16.2125 | 16.9968 | 17.9529 | 41.3206 | 42.9331 | 40.6892 | 21.3877 |  |  | 0.38464 | -0.18143 | -89.295 | 0.64721 | 0.085556 | -197.8558 | -0.16993 | -0.38017 | 0.10693 | 0.14089 | -0.066024 | 8.8293 | 9.059 | 1.9788 | 21.7898 | 22.0162 | 22.2004 | 22.2687 | 22.0934 | 21.4073 | 20.2292 | 22.2 | 22.3732 | 22.4014 | 22.3677 | 21.9825 | 21.2128 | 22.2709 | 17.4043 | 17.2024 | 16.3582 | 16.36 | 16.4307 | 17.1583 | 16.939 | 22.3777 | 22.1533 | 21.7102 | 22.0853 | 21.8051 | 21.3026 | 21.946 | 21.5248 | 20.9041 | 20.1027 | 20.3087 | 19.856 | 19.7872 | 0.009449 | 0.064699 | 20.7546 | 22.0759 | 22.3751 | 20.1117 | 21.6671 | 22.1152 | 21.9437 | 21.7087 | 21.278 | 21.7807 | 21.4433 | 21.0387 | 20.278 | 20.3674 | 20.2476 | 20.1839 | 20.0697 |  | 20.2329 | 19.8474 | 20.1357 | 19.7147 | 20.0797 | 20.2914 |  | 20.3949 |  |  | 20.2993 | 20.3871 | 20.6245 | [5 empty] | 21.9278 | 20.3337 | 21.6616 | 22.0339 | 19.5311 | 21.1498 | 21.778 | 19.3346 | 19.9033 | 21.1157 |  | 19.8099 | 20.87 | 18.8736 | 19.6652 | 20.7898 | 19.3923 | 20.047 | 19.0254 | 20.0729 | 19.1508 | 20.1864 | 18.8121 | 20.1161 | 21.0168 | 19.4429 | 19.7482 | 20.9679 | 18.9162 | 19.8013 | 20.7866 | 19.042 | 20.0667 | 19.3093 | 19.9141 | 18.908 | 20.1028 | -0.12163 | 20.9452 | 0.0488 | 0.012909 | -27.0384 | 3.0965 | -7.58 | -0.03 | 0.74049 | -0.50557 | -11.2161 | 0.95489 | 0.34738 | -16.7051 | -0.48957 | 0.4246 | 0.42752 | 0.42933 | 0.37541 | 0.46606 | 0.43693 | 0.42809
42838.4183 | -170 | 22.8924 | 22.8523 | 22.8469 | 22.7623 | 22.3995 | 21.7363 | 22.7135 | 21.7992 | 22.3685 | 22.3678 | 22.3469 | 22.0203 | 21.2414 | 22.2094 | 21.593 | 21.7672 | 21.8922 | 21.0718 | 21.1763 | 21.387 | 20.4706 | 20.6069 | 20.9021 | 21.8788 | 21.6407 | 21.2785 | 20.2931 | 20.4146 | 20.3742 | 22.062 | 21.6708 | 21.1804 | 21.9937 | 21.731 | 21.3488 | 19.9182 | 20.3759 |  | 20.5005 | 20.0338 | 20.1263 | 19.2521 |  | 16.9914 | 16.9539 | 16.6941 | 16.8703 | 16.8541 | 17.2572 | 17.5615 | 16.2325 | 16.8975 | 16.1889 | 17.0008 | 17.9585 | 41.2145 | 43.0479 | 40.6061 | 21.3875 |  |  | 0.39319 | -0.14726 | -89.8535 | 0.4054 | 0.33526 | -197.8138 | 0.156 | -0.23298 | 0.10946 | 0.031791 | -0.027138 | 8.829 | 9.059 | 1.9784 | 21.7952 | 22.0132 | 22.2034 | 22.2662 | 22.0904 | 21.4095 | 20.2168 | 22.2025 | 22.3723 | 22.4129 | 22.365 | 21.9855 | 21.216 | 22.2668 | 17.4189 | 17.2247 | 16.3466 | 16.3572 | 16.4187 | 17.1615 | 16.9461 | 22.381 | 22.1484 | 21.6987 | 22.0781 | 21.7951 | 21.2998 | 21.9401 | 21.5197 | 20.8972 | 20.0976 | 20.3082 | 19.8552 | 19.7986 | 0.031468 | 0.015818 | 20.7544 | 22.0703 | 22.3724 | 20.1055 | 21.6627 | 22.1097 | 21.9435 | 21.7128 | 21.2792 | 21.7788 | 21.4348 | 21.0336 | 20.2776 | 20.3669 | 20.2483 | 20.1862 | 20.0647 |  | 20.2347 | 19.8573 | 20.1422 | 19.7138 | 20.1 | 20.3028 |  | 20.4093 |  |  | 20.2954 | 20.3994 | 20.6258 | [5 empty] | 21.9342 | 20.3263 | 21.6641 | 22.0447 | 19.5459 | 21.1624 | 21.7922 | 19.349 | 19.9167 | 21.1236 |  | 19.8208 | 20.8815 | 18.8849 | 19.6738 | 20.8015 | 19.4078 | 20.0587 | 19.0355 | 20.0768 | 19.1633 | 20.2036 | 18.8149 | 20.1107 | 21.0265 | 19.4407 | 19.7565 | 20.9838 | 18.9229 | 19.8067 | 20.7882 | 19.0385 | 20.0702 | 19.3194 | 19.9234 | 18.9144 | 20.1025 | -0.20548 | 20.9467 | 0.047055 | 0.011653 | -27.0673 | 3.0965 | -5.65 | -0.15 | 0.74867 | -0.4555 | -11.2515 | 0.75576 | 0.68764 | -16.7032 | 0.46907 | 0.4248 | 0.42747 | 0.43004 | 0.37416 | 0.46817 | 0.43677 | 0.4276
42838.4183 | -169 | 22.897 | 22.8629 | 22.8476 | 22.7698 | 22.405 | 21.739 | 22.7178 | 21.805 | 22.3692 | 22.3762 | 22.3547 | 22.0213 | 21.2447 | 22.2098 | 21.5946 | 21.7669 | 21.8941 | 21.0767 | 21.1786 | 21.3951 | 20.4766 | 20.616 | 20.9093 | 21.8824 | 21.6547 | 21.2811 | 20.2958 | 20.4206 | 20.3811 | 22.0677 | 21.6732 | 21.1896 | 21.995 | 21.7354 | 21.3527 | 19.9191 | 20.3775 |  | 20.5005 | 20.0315 | 20.132 | 19.2553 |  | 16.9997 | 16.9679 | 16.709 | 16.8809 | 16.8658 | 17.2567 | 17.5859 | 16.2492 | 16.9062 | 16.1003 | 16.9999 | 17.9502 | 41.1113 | 43.1735 | 40.5329 | 21.3828 |  |  | 0.54235 | -0.32271 | -90.1446 | 0.67153 | 0.42594 | -197.8092 | -0.26587 | -0.27044 | -0.041162 | 0.081514 | 0.081362 | 8.8294 | 9.0591 | 1.9782 | 21.7816 | 22.0115 | 22.2039 | 22.2653 | 22.0998 | 21.41 | 20.2176 | 22.2071 | 22.3676 | 22.4153 | 22.3598 | 21.9899 | 21.2144 | 22.2714 | 17.4518 | 17.2386 | 16.3321 | 16.3612 | 16.397 | 17.1666 | 16.9504 | 22.3849 | 22.1545 | 21.7037 | 22.0876 | 21.7973 | 21.2971 | 21.9395 | 21.52 | 20.9001 | 20.1033 | 20.3137 | 19.8581 | 19.8069 | -0.037145 | -0.052464 | 20.7545 | 22.0673 | 22.3772 | 20.1128 | 21.6684 | 22.1077 | 21.9501 | 21.7076 | 21.2809 | 21.78 | 21.4382 | 21.0363 | 20.2731 | 20.3657 | 20.2439 | 20.1892 | 20.0585 |  | 20.2315 | 19.8502 | 20.1376 | 19.7093 | 20.0883 | 20.3011 |  | 20.3944 |  |  | 20.2887 | 20.3846 | 20.6212 | [5 empty] | 21.9259 | 20.3194 | 21.6562 | 22.0361 | 19.5285 | 21.1496 | 21.7752 | 19.3458 | 19.9149 | 21.1284 |  | 19.8219 | 20.8788 | 18.8806 | 19.6661 | 20.7914 | 19.4018 | 20.0519 | 19.0332 | 20.0786 | 19.1605 | 20.1964 | 18.8129 | 20.1124 | 21.0282 | 19.4396 | 19.7488 | 20.9741 | 18.9202 | 19.801 | 20.7785 | 19.0433 | 20.0647 | 19.3154 | 19.9213 | 18.9149 | 20.1035 | -0.068396 | 20.9462 | 0.048303 | 0.011239 | -27.0239 | 3.0965 | -7.54 | -0.06 | 0.87929 | -0.67431 | -11.27 | 0.97272 | 0.77508 | -16.703 | -0.61236 | 0.42487 | 0.42751 | 0.42977 | 0.3711 | 0.47028 | 0.43671 | 0.42756
42838.4183 | -168 | 22.8888 | 22.864 | 22.8446 | 22.7666 | 22.4005 | 21.7363 | 22.7063 | 21.8003 | 22.3616 | 22.372 | 22.3482 | 22.0154 | 21.2409 | 22.1993 | 21.5923 | 21.7626 | 21.89 | 21.0709 | 21.1741 | 21.3991 | 20.4771 | 20.6096 | 20.9063 | 21.8859 | 21.6477 | 21.277 | 20.2939 | 20.4145 | 20.3829 | 22.0652 | 21.6762 | 21.1901 | 21.9991 | 21.7399 | 21.3611 | 19.9187 | 20.3833 |  | 20.4948 | 20.0363 | 20.1333 | 19.2616 |  | 16.9989 | 16.9679 | 16.7023 | 16.8906 | 16.8581 | 17.2412 | 17.613 | 16.1814 | 16.9047 | 16.0289 | 16.995 | 17.9646 | 41.0334 | 43.3179 | 40.4671 | 21.3905 |  |  | 0.38399 | 0.018335 | -90.4265 | 0.81084 | 0.41017 | -197.8598 | -0.32501 | -0.1239 | -0.23868 | -0.12241 | 0.10775 | 8.8277 | 9.0574 | 1.9781 | 21.7823 | 22.0011 | 22.2018 | 22.2582 | 22.0866 | 21.4079 | 20.2175 | 22.2042 | 22.3702 | 22.4111 | 22.3597 | 21.9805 | 21.2104 | 22.2703 | 17.4586 | 17.2321 | 16.3271 | 16.3497 | 16.3716 | 17.1588 | 16.9499 | 22.3895 | 22.1565 | 21.7132 | 22.0884 | 21.8016 | 21.3011 | 21.9463 | 21.5318 | 20.9048 | 20.1048 | 20.3236 | 19.8645 | 19.8073 | 0.039332 | -0.094498 | 20.7572 | 22.0793 | 22.3803 | 20.1249 | 21.675 | 22.1143 | 21.947 | 21.7126 | 21.2771 | 21.7837 | 21.4495 | 21.0464 | 20.2878 | 20.3734 | 20.2524 | 20.1991 | 20.0456 |  | 20.2277 | 19.8399 | 20.1315 | 19.7106 | 20.082 | 20.2974 |  | 20.3899 |  |  | 20.2942 | 20.3912 | 20.631 | [5 empty] | 21.9345 | 20.3346 | 21.6623 | 22.0394 | 19.5341 | 21.1652 | 21.7794 | 19.3432 | 19.9203 | 21.1234 |  | 19.8149 | 20.8826 | 18.8803 | 19.6734 | 20.7955 | 19.4019 | 20.0541 | 19.0378 | 20.0758 | 19.1646 | 20.1915 | 18.814 | 20.1163 | 21.0259 | 19.4377 | 19.7494 | 20.9691 | 18.9171 | 19.7975 | 20.7806 | 19.0424 | 20.0736 | 19.3157 | 19.9285 | 18.9134 | 20.1026 | -0.19621 | 20.9461 | 0.048499 | 0.012691 | -27.0924 | 3.0965 | 14.43 | -0.11 | 0.73987 | 0.16073 | -11.2876 | 1.0689 | 0.76057 | -16.7047 | -0.67703 | 0.4251 | 0.42759 | 0.42952 | 0.36943 | 0.47078 | 0.43653 | 0.4276
42838.4183 | -167 | 22.904 | 22.8706 | 22.8531 | 22.7836 | 22.4179 | 21.7513 | 22.7191 | 21.8107 | 22.3675 | 22.3882 | 22.363 | 22.029 | 21.2492 | 22.2114 | 21.5911 | 21.7609 | 21.8839 | 21.0742 | 21.1775 | 21.3977 | 20.4746 | 20.6145 | 20.9094 | 21.8904 | 21.6505 | 21.2752 | 20.2936 | 20.4168 | 20.3857 | 22.065 | 21.6725 | 21.1896 | 22.0019 | 21.7331 | 21.3578 | 19.9268 | 20.376 |  | 20.4994 | 20.0371 | 20.1353 | 19.259 |  | 17.0062 | 16.9869 | 16.7126 | 16.8968 | 16.8555 | 17.2467 | 17.6371 | 16.0806 | 16.9131 | 16.0471 | 17.0014 | 17.9604 | 40.9437 | 43.4626 | 40.3976 | 21.3935 |  |  | 0.39581 | -0.23531 | -90.4206 | 0.55785 | 0.32606 | -197.8539 | 0.10343 | -0.23824 | -0.31049 | 0.1776 | -0.063246 | 8.8286 | 9.0584 | 1.9788 | 21.7846 | 22.0034 | 22.1997 | 22.2592 | 22.0863 | 21.4075 | 20.2218 | 22.1943 | 22.3722 | 22.4055 | 22.3588 | 21.9832 | 21.2094 | 22.269 | 17.4558 | 17.222 | 16.3196 | 16.3421 | 16.3609 | 17.158 | 16.9437 | 22.3901 | 22.1511 | 21.7118 | 22.0867 | 21.7997 | 21.3026 | 21.949 | 21.531 | 20.9034 | 20.1019 | 20.3309 | 19.8701 | 19.797 | 0.047786 | -0.065588 | 20.764 | 22.086 | 22.3759 | 20.1279 | 21.6786 | 22.1258 | 21.9505 | 21.7249 | 21.2813 | 21.7909 | 21.4496 | 21.0513 | 20.302 | 20.3691 | 20.2607 | 20.2076 | 20.0372 |  | 20.2327 | 19.8365 | 20.136 | 19.7206 | 20.0786 | 20.2925 |  | 20.3926 |  |  | 20.3004 | 20.3982 | 20.6299 | [5 empty] | 21.9367 | 20.3373 | 21.6691 | 22.0439 | 19.5388 | 21.1636 | 21.7828 | 19.3449 | 19.9234 | 21.1311 |  | 19.8164 | 20.8858 | 18.8839 | 19.6691 | 20.7974 | 19.4045 | 20.0505 | 19.0415 | 20.0721 | 19.1644 | 20.1896 | 18.8254 | 20.1162 | 21.0261 | 19.4334 | 19.7498 | 20.9721 | 18.9265 | 19.8008 | 20.7817 | 19.0449 | 20.0756 | 19.3131 | 19.9234 | 18.9131 | 20.1007 | 0.064978 | 20.9461 | 0.048991 | 0.013569 | -27.0359 | 3.0965 | -1.39 | -0.15 | 0.75118 | -0.57583 | -11.2876 | 0.8866 | 0.67813 | -16.7046 | 0.38193 | 0.4255 | 0.42783 | 0.42913 | 0.36964 | 0.47088 | 0.43687 | 0.42779
42838.4184 | -166 | 22.8903 | 22.8679 | 22.8534 | 22.7754 | 22.4128 | 21.7457 | 22.7155 | 21.7926 | 22.3662 | 22.3783 | 22.3621 | 22.0304 | 21.2517 | 22.2107 | 21.5864 | 21.762 | 21.8905 | 21.0756 | 21.1796 | 21.3961 | 20.4769 | 20.6223 | 20.9066 | 21.8881 | 21.6444 | 21.2713 | 20.2939 | 20.4247 | 20.3873 | 22.0669 | 21.6711 | 21.1977 | 22.0022 | 21.7355 | 21.3518 | 19.9261 | 20.3716 |  | 20.498 | 20.0371 | 20.1304 | 19.2498 |  | 17.0144 | 16.986 | 16.7177 | 16.8932 | 16.8669 | 17.2564 | 17.6618 | 15.9868 | 16.9221 | 16.0574 | 17.0068 | 17.9602 | 40.8535 | 43.6174 | 40.3268 | 21.3922 |  |  | 0.29987 | -0.13543 | -90.1052 | 0.63801 | 0.18807 | -197.773 | -0.070047 | -0.18501 | 0.0063206 | -0.047094 | -0.0031808 | 8.829 | 9.0587 | 1.9789 | 21.7832 | 22.0054 | 22.1962 | 22.2649 | 22.0855 | 21.4057 | 20.2174 | 22.1973 | 22.3753 | 22.4108 | 22.3556 | 21.9784 | 21.2153 | 22.2668 | 17.4234 | 17.196 | 16.3187 | 16.3267 | 16.3486 | 17.1544 | 16.9415 | 22.3911 | 22.1499 | 21.7071 | 22.0792 | 21.7941 | 21.3055 | 21.9391 | 21.5253 | 20.9071 | 20.0984 | 20.3198 | 19.8728 | 19.794 | 0.013971 | -0.070533 | 20.7586 | 22.0749 | 22.3775 | 20.1118 | 21.667 | 22.1147 | 21.9433 | 21.7125 | 21.2749 | 21.7811 | 21.4403 | 21.0455 | 20.2921 | 20.3605 | 20.2505 | 20.1995 | 20.0435 |  | 20.2344 | 19.8395 | 20.1358 | 19.72 | 20.0782 | 20.2963 |  | 20.3992 |  |  | 20.2956 | 20.3992 | 20.629 | [5 empty] | 21.9343 | 20.3396 | 21.6682 | 22.0479 | 19.5349 | 21.158 | 21.7769 | 19.3522 | 19.9307 | 21.1417 |  | 19.8218 | 20.8895 | 18.888 | 19.6767 | 20.8033 | 19.4019 | 20.0593 | 19.0518 | 20.0735 | 19.1649 | 20.198 | 18.8378 | 20.1193 | 21.0267 | 19.4382 | 19.7585 | 20.9742 | 18.9262 | 19.8052 | 20.7821 | 19.0486 | 20.0746 | 19.3188 | 19.9271 | 18.9172 | 20.1103 | -0.10142 | 20.9466 | 0.049009 | 0.014876 | -27.0051 | 3.0965 | -6.02 | -0.07 | 0.65383 | -0.43685 | -11.2679 | 0.94816 | 0.51502 | -16.7014 | -0.31431 | 0.42538 | 0.42775 | 0.42914 | 0.37283 | 0.47073 | 0.4371 | 0.42776
42838.4184 | -165 | 22.8882 | 22.8583 | 22.8539 | 22.78 | 22.4064 | 21.741 | 22.7075 | 21.8048 | 22.3716 | 22.3793 | 22.3581 | 22.0248 | 21.247 | 22.2195 | 21.5891 | 21.7666 | 21.8906 | 21.0779 | 21.1798 | 21.3994 | 20.4766 | 20.6256 | 20.9083 | 21.8836 | 21.6395 | 21.2742 | 20.2975 | 20.4294 | 20.3957 | 22.0667 | 21.6655 | 21.1833 | 21.9871 | 21.732 | 21.3485 | 19.9159 | 20.3798 |  | 20.4946 | 20.0221 | 20.1292 | 19.2294 |  | 17.0136 | 16.9899 | 16.7194 | 16.893 | 16.8953 | 17.2804 | 17.6874 | 15.9428 | 16.9166 | 16.0688 | 16.9958 | 17.9577 | 40.764 | 43.7826 | 40.2656 | 21.3873 |  |  | 0.53512 | -0.15186 | -90.071 | 0.50988 | 0.12893 | -197.8493 | -0.057563 | -0.15938 | -0.023259 | -0.096816 | 0.057406 | 8.8288 | 9.0585 | 1.979 | 21.7767 | 22.0077 | 22.195 | 22.2618 | 22.0864 | 21.4103 | 20.2154 | 22.201 | 22.3778 | 22.4051 | 22.3484 | 21.9842 | 21.2155 | 22.2647 | 17.3631 | 17.2011 | 16.3215 | 16.3219 | 16.3386 | 17.1564 | 16.9428 | 22.3822 | 22.1489 | 21.7004 | 22.0807 | 21.7995 | 21.3017 | 21.94 | 21.522 | 20.8971 | 20.0974 | 20.3174 | 19.8625 | 19.7896 | -0.13623 | -0.031162 | 20.7497 | 22.0673 | 22.3826 | 20.1101 | 21.6574 | 22.1147 | 21.9314 | 21.7021 | 21.2688 | 21.7734 | 21.438 | 21.0359 | 20.2774 | 20.3525 | 20.2443 | 20.1943 | 20.0434 |  | 20.2312 | 19.8505 | 20.1398 | 19.7192 | 20.0841 | 20.3045 |  | 20.403 |  |  | 20.2976 | 20.404 | 20.6312 | [5 empty] | 21.9312 | 20.3354 | 21.6644 | 22.046 | 19.538 | 21.152 | 21.78 | 19.3445 | 19.9256 | 21.134 |  | 19.8204 | 20.884 | 18.8822 | 19.6748 | 20.799 | 19.4049 | 20.0596 | 19.0432 | 20.072 | 19.1629 | 20.1954 | 18.8352 | 20.1226 | 21.0325 | 19.4398 | 19.7592 | 20.9794 | 18.9251 | 19.802 | 20.7866 | 19.0456 | 20.0733 | 19.323 | 19.933 | 18.9253 | 20.1069 | -0.11978 | 20.9468 | 0.047664 | 0.014244 | -27.0703 | 3.0965 | -0.81 | -0.12 | 0.87344 | -0.46259 | -11.2658 | 0.84763 | 0.42644 | -16.7053 | -0.28494 | 0.42528 | 0.42757 | 0.42935 | 0.37975 | 0.47057 | 0.43733 | 0.42784
42838.4184 | -164 | 22.8918 | 22.8597 | 22.852 | 22.7853 | 22.4071 | 21.7422 | 22.7174 | 21.8023 | 22.3699 | 22.378 | 22.3508 | 22.0254 | 21.2498 | 22.2157 | 21.5888 | 21.761 | 21.889 | 21.0782 | 21.1738 | 21.3963 | 20.4719 | 20.6151 | 20.9069 | 21.8835 | 21.6458 | 21.2726 | 20.2967 | 20.4203 | 20.3883 | 22.0768 | 21.6716 | 21.1922 | 21.9991 | 21.7407 | 21.3515 | 19.9225 | 20.3841 |  | 20.4982 | 20.0264 | 20.1281 | 19.2215 |  | 17.0129 | 16.9853 | 16.7186 | 16.9096 | 16.8951 | 17.2911 | 17.7062 | 15.9645 | 16.9177 | 16.0664 | 17.0021 | 17.9532 | 40.6696 | 43.9479 | 40.2052 | 21.3854 |  |  | 0.34193 | -0.082861 | -89.9619 | 1.0507 | 0.11841 | -197.8394 | 0.18163 | -0.30855 | -0.090006 | 0.19627 | 0.061919 | 8.8301 | 9.0599 | 1.979 | 21.7876 | 22.0013 | 22.1951 | 22.2584 | 22.0897 | 21.4125 | 20.2141 | 22.1987 | 22.3727 | 22.4079 | 22.3548 | 21.9854 | 21.2101 | 22.2698 | 17.305 | 17.1983 | 16.3331 | 16.3386 | 16.3331 | 17.1603 | 16.9518 | 22.3925 | 22.1507 | 21.7089 | 22.0913 | 21.8037 | 21.3094 | 21.9478 | 21.5293 | 20.9086 | 20.1083 | 20.3218 | 19.8755 | 19.7985 | 0.03599 | -0.008528 | 20.7504 | 22.0789 | 22.3797 | 20.1191 | 21.6642 | 22.1144 | 21.9361 | 21.7053 | 21.2741 | 21.7731 | 21.436 | 21.0345 | 20.2811 | 20.3618 | 20.2527 | 20.1966 | 20.0315 |  | 20.2246 | 19.8442 | 20.1357 | 19.7184 | 20.0812 | 20.3092 |  | 20.4017 |  |  | 20.2946 | 20.4076 | 20.6278 | [5 empty] | 21.9274 | 20.3369 | 21.6641 | 22.0425 | 19.5358 | 21.1569 | 21.7813 | 19.346 | 19.9234 | 21.1301 |  | 19.8179 | 20.8821 | 18.8727 | 19.6721 | 20.7958 | 19.4157 | 20.0569 | 19.0447 | 20.0751 | 19.1615 | 20.1902 | 18.8397 | 20.1194 | 21.0357 | 19.4405 | 19.7563 | 20.976 | 18.9316 | 19.802 | 20.7875 | 19.0477 | 20.075 | 19.3207 | 19.9309 | 18.93 | 20.1046 | -0.077672 | 20.9453 | 0.046613 | 0.013678 | -27.0767 | 3.0965 | -16.66 | -0.19 | 0.69818 | -0.3417 | -11.2589 | 1.2168 | 0.40869 | -16.7052 | 0.50616 | 0.42539 | 0.42761 | 0.42928 | 0.38667 | 0.47034 | 0.43777 | 0.42796
42838.4184 | -163 | 22.8899 | 22.8637 | 22.8527 | 22.7773 | 22.4001 | 21.7411 | 22.7147 | 21.8017 | 22.3658 | 22.3711 | 22.3508 | 22.0189 | 21.2453 | 22.2077 | 21.5903 | 21.7581 | 21.888 | 21.0747 | 21.1772 | 21.3983 | 20.4717 | 20.6153 | 20.9126 | 21.8799 | 21.6477 | 21.2755 | 20.298 | 20.4233 | 20.3927 | 22.0732 | 21.6716 | 21.1894 | 21.9957 | 21.7383 | 21.3496 | 19.9278 | 20.3855 |  | 20.5047 | 20.0254 | 20.1275 | 19.2103 |  | 17.0378 | 17 | 16.7387 | 16.9171 | 16.8979 | 17.2968 | 17.7405 | 16.0146 | 16.9297 | 16.0694 | 17.0021 | 17.9594 | 40.5801 | 44.1275 | 40.1458 | 21.3855 |  |  | 0.29922 | -0.11637 | -90.1788 | 0.6735 | 0.24852 | -197.848 | 0.29137 | -0.28621 | 0.14468 | 0.073961 | 0.065912 | 8.8281 | 9.0578 | 1.9786 | 21.7869 | 22.0059 | 22.1913 | 22.2656 | 22.0862 | 21.4043 | 20.2127 | 22.1965 | 22.365 | 22.4057 | 22.358 | 21.9784 | 21.2108 | 22.2685 | 17.2583 | 17.216 | 16.3257 | 16.3285 | 16.3345 | 17.1628 | 16.9507 | 22.3835 | 22.1427 | 21.7106 | 22.0859 | 21.8036 | 21.3023 | 21.9418 | 21.5244 | 20.903 | 20.1022 | 20.3189 | 19.8828 | 19.7908 | 0.10283 | 0.035979 | 20.7431 | 22.0782 | 22.3732 | 20.1205 | 21.667 | 22.1123 | 21.9368 | 21.715 | 21.2778 | 21.7767 | 21.4423 | 21.043 | 20.2829 | 20.3679 | 20.2616 | 20.1997 | 20.0279 |  | 20.226 | 19.8389 | 20.1282 | 19.7183 | 20.0797 | 20.3078 |  | 20.3897 |  |  | 20.2909 | 20.4038 | 20.6204 | [5 empty] | 21.9279 | 20.3376 | 21.6659 | 22.0403 | 19.5363 | 21.1536 | 21.7743 | 19.3469 | 19.9294 | 21.1365 |  | 19.8211 | 20.8844 | 18.8764 | 19.6808 | 20.7971 | 19.4197 | 20.0604 | 19.0456 | 20.0717 | 19.1621 | 20.192 | 18.8492 | 20.11 | 21.0377 | 19.4347 | 19.7613 | 20.9743 | 18.9401 | 19.8088 | 20.7902 | 19.0477 | 20.0728 | 19.3252 | 19.9305 | 18.9283 | 20.0985 | -0.085462 | 20.9469 | 0.048057 | 0.014193 | -27.052 | 3.0965 | -18.56 | -0.02 | 0.65313 | -0.40495 | -11.2728 | 0.9742 | 0.59208 | -16.7058 | 0.64109 | 0.42553 | 0.42751 | 0.42923 | 0.39215 | 0.47103 | 0.43826 | 0.42797
42838.4184 | -162 | 22.8968 | 22.8574 | 22.8469 | 22.779 | 22.3972 | 21.744 | 22.7185 | 21.8049 | 22.3649 | 22.3724 | 22.35 | 22.021 | 21.2457 | 22.2115 | 21.5962 | 21.7623 | 21.8941 | 21.0734 | 21.1758 | 21.3949 | 20.4736 | 20.6236 | 20.9088 | 21.8827 | 21.6441 | 21.2797 | 20.2975 | 20.4261 | 20.393 | 22.0612 | 21.665 | 21.1814 | 21.9922 | 21.7298 | 21.3461 | 19.9219 | 20.3732 |  | 20.4977 | 20.0238 | 20.1189 | 19.1909 |  | 17.0359 | 17.0027 | 16.7394 | 16.909 | 16.8868 | 17.2985 | 17.7622 | 16.0518 | 16.9255 | 16.0624 | 17.0074 | 17.9586 | 40.501 | 44.3143 | 40.0916 | 21.382 |  |  | 0.56338 | 0.011107 | -90.6249 | 0.85027 | 0.17952 | -197.8059 | -0.095019 | -0.33878 | -0.13087 | 0.26614 | 0.10601 | 8.8292 | 9.0588 | 1.9786 | 21.7847 | 22.008 | 22.1983 | 22.2645 | 22.0931 | 21.4092 | 20.2167 | 22.1936 | 22.3717 | 22.4077 | 22.3569 | 21.9833 | 21.2153 | 22.269 | 17.2372 | 17.2122 | 16.3117 | 16.3003 | 16.3272 | 17.1584 | 16.9522 | 22.3958 | 22.1612 | 21.7107 | 22.0858 | 21.7986 | 21.3058 | 21.9415 | 21.5236 | 20.9024 | 20.1099 | 20.326 | 19.8721 | 19.7867 | -0.050711 | 0.10616 | 20.7417 | 22.0718 | 22.3765 | 20.128 | 21.6747 | 22.1175 | 21.939 | 21.713 | 21.284 | 21.7771 | 21.4488 | 21.041 | 20.2897 | 20.3733 | 20.2653 | 20.2016 | 20.0296 |  | 20.2283 | 19.8376 | 20.1303 | 19.7132 | 20.0804 | 20.3094 |  | 20.3965 |  |  | 20.2946 | 20.3966 | 20.6132 | [5 empty] | 21.9292 | 20.3379 | 21.6624 | 22.0399 | 19.5322 | 21.1596 | 21.7766 | 19.3491 | 19.9264 | 21.1359 |  | 19.8218 | 20.8803 | 18.877 | 19.6744 | 20.7967 | 19.4175 | 20.058 | 19.0439 | 20.0706 | 19.1569 | 20.193 | 18.8577 | 20.1128 | 21.0357 | 19.4312 | 19.7646 | 20.9778 | 18.9408 | 19.8105 | 20.7906 | 19.048 | 20.0692 | 19.3274 | 19.9384 | 18.9248 | 20.1009 | -0.059307 | 20.9448 | 0.048137 | 0.015718 | -27.0443 | 3.0965 | -8.98 | -0.13 | 0.8962 | 0.12511 | -11.3007 | 1.0946 | 0.50323 | -16.704 | -0.36611 | 0.42556 | 0.42761 | 0.4294 | 0.39399 | 0.47276 | 0.4386 | 0.42835
42838.4184 | -161 | 22.8928 | 22.8654 | 22.8582 | 22.7749 | 22.3976 | 21.7375 | 22.7231 | 21.8023 | 22.3663 | 22.3795 | 22.3544 | 22.0199 | 21.2392 | 22.2199 | 21.5897 | 21.7633 | 21.8886 | 21.0717 | 21.1804 | 21.3947 | 20.4701 | 20.6176 | 20.9108 | 21.8899 | 21.6444 | 21.2776 | 20.2974 | 20.4201 | 20.3918 | 22.0635 | 21.6665 | 21.1884 | 21.9924 | 21.731 | 21.3493 | 19.9207 | 20.3784 |  | 20.5013 | 20.0244 | 20.1225 | 19.1727 |  | 17.0269 | 17.0034 | 16.7399 | 16.9209 | 16.8881 | 17.3046 | 17.8019 | 16.1008 | 16.9301 | 16.0817 | 17.0028 | 17.9613 | 40.4291 | 44.5051 | 40.0309 | 21.3809 |  |  | 0.59295 | -0.042121 | -91.445 | 0.58282 | 0.36812 | -197.8519 | 0.059405 | -0.28752 | -0.0028256 | -0.042268 | -0.043282 | 8.8291 | 9.0589 | 1.9786 | 21.7813 | 22.002 | 22.1996 | 22.2644 | 22.0839 | 21.4066 | 20.2128 | 22.1969 | 22.3701 | 22.3972 | 22.3618 | 21.9811 | 21.2168 | 22.2681 | 17.1799 | 17.1984 | 16.2945 | 16.2695 | 16.3063 | 17.153 | 16.9376 | 22.3878 | 22.1454 | 21.7086 | 22.0779 | 21.8028 | 21.3018 | 21.9419 | 21.5292 | 20.9029 | 20.1043 | 20.3188 | 19.8739 | 19.7942 | 0.19209 | 0.042255 | 20.7464 | 22.0741 | 22.3807 | 20.1248 | 21.6721 | 22.1161 | 21.9416 | 21.7093 | 21.2774 | 21.7708 | 21.4397 | 21.0366 | 20.2881 | 20.3643 | 20.256 | 20.1992 | 20.0379 |  | 20.2422 | 19.7949 | 20.1335 | 19.7132 | 20.0908 | 20.3097 |  | 20.3851 |  |  | 20.3024 | 20.4002 | 20.607 | [5 empty] | 21.9285 | 20.3346 | 21.6654 | 22.0303 | 19.5332 | 21.1605 | 21.7723 | 19.359 | 19.9324 | 21.1419 |  | 19.8271 | 20.891 | 18.8828 | 19.6752 | 20.7973 | 19.4125 | 20.0553 | 19.0504 | 20.068 | 19.1659 | 20.2011 | 18.8512 | 20.1056 | 21.03 | 19.4322 | 19.761 | 20.9789 | 18.9467 | 19.8069 | 20.7878 | 19.0492 | 20.065 | 19.3188 | 19.9363 | 18.9261 | 20.0975 | -0.15465 | 20.9472 | 0.048745 | 0.01603 | -27.0741 | 3.0965 | 11.22 | -0.1 | 0.91941 | -0.24363 | -11.3517 | 0.90625 | 0.72061 | -16.7061 | 0.28948 | 0.4258 | 0.42891 | 0.42975 | 0.39972 | 0.47296 | 0.43906 | 0.42795
42838.4184 | -160 | 22.8994 | 22.8706 | 22.8553 | 22.7768 | 22.402 | 21.7447 | 22.7232 | 21.7945 | 22.3662 | 22.3808 | 22.3513 | 22.0279 | 21.2406 | 22.2094 | 21.5954 | 21.7678 | 21.9026 | 21.0809 | 21.1882 | 21.3999 | 20.4815 | 20.6187 | 20.9196 | 21.8909 | 21.6527 | 21.2812 | 20.3055 | 20.4238 | 20.4002 | 22.0595 | 21.6707 | 21.1883 | 21.9922 | 21.7359 | 21.3537 | 19.9216 | 20.3883 |  | 20.4963 | 20.0229 | 20.1256 | 19.1557 |  | 17.0313 | 17.0004 | 16.7553 | 16.9353 | 16.8952 | 17.3063 | 17.8198 | 16.1249 | 16.9207 | 16.0891 | 17.0046 | 17.9639 | 40.3726 | 44.6988 | 39.9821 | 21.3833 |  |  | 0.30973 | -0.063149 | -92.2618 | 0.54076 | 0.33658 | -197.8361 | -0.28755 | -0.4426 | 0.044073 | 0.014587 | -0.078176 | 8.8291 | 9.0587 | 1.9792 | 21.786 | 22.0074 | 22.2026 | 22.2616 | 22.0858 | 21.4085 | 20.2187 | 22.2023 | 22.3741 | 22.4067 | 22.3581 | 21.9839 | 21.2143 | 22.2722 | 17.1292 | 17.2078 | 16.3114 | 16.2661 | 16.2847 | 17.1583 | 16.9446 | 22.3757 | 22.1399 | 21.707 | 22.0768 | 21.7945 | 21.2981 | 21.9344 | 21.5277 | 20.9001 | 20.0986 | 20.3214 | 19.8824 | 19.7998 | 0.087303 | 0.05595 | 20.7461 | 22.0697 | 22.3738 | 20.1165 | 21.6658 | 22.1112 | 21.9446 | 21.7024 | 21.2711 | 21.7772 | 21.4296 | 21.027 | 20.2782 | 20.3688 | 20.2553 | 20.2004 | 20.0472 |  | 20.2277 | 19.9131 | 20.1494 | 19.7098 | 20.088 | 20.3095 |  | 20.4005 |  |  | 20.3144 | 20.4072 | 20.6134 | [5 empty] | 21.9299 | 20.3373 | 21.6643 | 22.0449 | 19.5409 | 21.1605 | 21.7847 | 19.3606 | 19.9413 | 21.1379 |  | 19.8159 | 20.8902 | 18.8776 | 19.6731 | 20.7885 | 19.4071 | 20.0602 | 19.0406 | 20.0683 | 19.1646 | 20.1972 | 18.8558 | 20.0925 | 21.0341 | 19.4399 | 19.7628 | 20.9863 | 18.9345 | 19.798 | 20.7908 | 19.0475 | 20.0708 | 19.3255 | 19.9465 | 18.9216 | 20.0959 | -0.13629 | 20.9437 | 0.047793 | 0.015028 | -27.0877 | 3.0965 | -3.38 | -0.19 | 0.66451 | -0.29831 | -11.4022 | 0.87293 | 0.68905 | -16.7055 | -0.63689 | 0.42505 | 0.42616 | 0.42975 | 0.40596 | 0.4719 | 0.43957 | 0.4276
42838.4184 | -159 | 22.8913 | 22.8679 | 22.8521 | 22.7733 | 22.4115 | 21.7411 | 22.7192 | 21.8044 | 22.3731 | 22.3818 | 22.3579 | 22.0325 | 21.2529 | 22.2119 | 21.5916 | 21.768 | 21.8957 | 21.084 | 21.186 | 21.3915 | 20.4833 | 20.6193 | 20.9128 | 21.886 | 21.6466 | 21.2863 | 20.2985 | 20.4348 | 20.4014 | 22.0601 | 21.6646 | 21.1876 | 21.9958 | 21.7258 | 21.3482 | 19.9212 | 20.3793 |  | 20.498 | 20.0219 | 20.1155 | 19.149 |  | 17.0287 | 17.016 | 16.7521 | 16.936 | 16.9006 | 17.3281 | 17.8193 | 16.1082 | 16.9231 | 16.1187 | 16.9965 | 17.9701 | 40.3224 | 44.9206 | 39.9562 | 21.3835 |  |  | 0.50292 | -0.089433 | -93.0024 | 0.40474 | 0.30438 | -197.8729 | 0.051517 | -0.5254 | 0.076766 | 0.10648 | 0.035185 | 8.8289 | 9.0587 | 1.9792 | 21.7879 | 22.0024 | 22.1999 | 22.2598 | 22.0864 | 21.4023 | 20.2195 | 22.1979 | 22.3756 | 22.411 | 22.3518 | 21.9823 | 21.2163 | 22.2684 | 17.1245 | 17.2165 | 16.3278 | 16.2576 | 16.2771 | 17.1587 | 16.9448 | 22.3862 | 22.1461 | 21.7162 | 22.0866 | 21.8007 | 21.3054 | 21.9427 | 21.5286 | 20.9139 | 20.0984 | 20.3306 | 19.888 | 19.8051 | 0.12092 | 0.11358 | 20.7542 | 22.0649 | 22.3711 | 20.1191 | 21.6578 | 22.1071 | 21.9433 | 21.7106 | 21.2733 | 21.7757 | 21.4351 | 21.0328 | 20.2847 | 20.3636 | 20.2467 | 20.2144 | 20.0476 |  | 20.2264 | 19.9177 | 20.1342 | 19.7129 | 20.0776 | 20.3018 |  | 20.3937 |  |  | 20.2978 | 20.4288 | 20.6115 | [5 empty] | 21.9263 | 20.3419 | 21.6509 | 22.0442 | 19.5342 | 21.1584 | 21.7804 | 19.3636 | 19.9433 | 21.1419 |  | 19.8305 | 20.8894 | 18.8841 | 19.685 | 20.803 | 19.4163 | 20.0625 | 19.0443 | 20.0825 | 19.1673 | 20.1979 | 18.8614 | 20.0925 | 21.0406 | 19.4429 | 19.7801 | 20.9889 | 18.9487 | 19.8018 | 20.7981 | 19.0541 | 20.0672 | 19.3263 | 19.947 | 18.9299 | 20.1034 | -0.055597 | 20.9466 | 0.046459 | 0.014716 | -27.0546 | 3.0964 | -0.48 | 0.01 | 0.84676 | -0.35501 | -11.4482 | 0.75523 | 0.65528 | -16.7077 | 0.26959 | 0.425 | 0.42552 | 0.42931 | 0.40653 | 0.47011 | 0.43974 | 0.42745
42838.4184 | -158 | 22.8978 | 22.8667 | 22.8486 | 22.773 | 22.3984 | 21.7351 | 22.7132 | 21.8027 | 22.37 | 22.3761 | 22.3466 | 22.0293 | 21.248 | 22.2145 | 21.5867 | 21.7564 | 21.8854 | 21.0653 | 21.1735 | 21.3943 | 20.4726 | 20.6049 | 20.9004 | 21.8788 | 21.6403 | 21.2738 | 20.2882 | 20.4216 | 20.3859 | 22.0655 | 21.6631 | 21.1904 | 21.9924 | 21.7317 | 21.3523 | 19.9198 | 20.3866 |  | 20.4991 | 20.0219 | 20.1184 | 19.1353 |  | 17.0506 | 17.04 | 16.7685 | 16.9556 | 16.9405 | 17.3662 | 17.8252 | 16.0937 | 16.9266 | 16.152 | 16.9997 | 17.9553 | 40.2699 | 45.1185 | 39.922 | 21.3809 |  |  | 0.47598 | -0.095349 | -93.4749 | 0.29171 | 0.18807 | -197.8447 | -0.75542 | -0.53065 | 0.061976 | -0.012477 | -0.10838 | 8.8285 | 9.0583 | 1.9788 | 21.7817 | 22.0042 | 22.1878 | 22.2563 | 22.0794 | 21.3954 | 20.2174 | 22.1905 | 22.3648 | 22.4067 | 22.3494 | 21.972 | 21.2043 | 22.2602 | 17.1323 | 17.2012 | 16.3011 | 16.2676 | 16.2803 | 17.1621 | 16.948 | 22.3846 | 22.1471 | 21.7079 | 22.0783 | 21.7958 | 21.3053 | 21.9443 | 21.5269 | 20.9113 | 20.1054 | 20.3214 | 19.877 | 19.807 | 0.10146 | 0.10179 | 20.7468 | 22.0823 | 22.3763 | 20.126 | 21.6649 | 22.1089 | 21.9494 | 21.7089 | 21.2787 | 21.7788 | 21.4392 | 21.0372 | 20.2901 | 20.3546 | 20.2593 | 20.2097 | 20.0552 |  | 20.2227 | 19.8359 | 20.1395 | 19.7095 | 20.0828 | 20.3014 |  | 20.3974 |  |  | 20.2896 | 20.4138 | 20.6048 | [5 empty] | 21.9295 | 20.3318 | 21.6583 | 22.0431 | 19.536 | 21.1585 | 21.7813 | 19.3649 | 19.949 | 21.1461 |  | 19.8328 | 20.8946 | 18.8868 | 19.6868 | 20.8119 | 19.4213 | 20.0718 | 19.0469 | 20.087 | 19.1707 | 20.203 | 18.8677 | 20.0832 | 21.0381 | 19.4315 | 19.7743 | 20.9865 | 18.9553 | 19.8084 | 20.7915 | 19.0438 | 20.0651 | 19.3314 | 19.9492 | 18.9397 | 20.1091 | -0.1988 | 20.9493 | 0.047916 | 0.015529 | -27.0069 | 3.0965 | -22.37 | -0.04 | 0.82375 | -0.36658 | -11.4777 | 0.64119 | 0.51512 | -16.7076 | -1.0324 | 0.42467 | 0.42797 | 0.42958 | 0.40607 | 0.47345 | 0.44007 | 0.42763
42838.4185 | -157 | 22.8971 | 22.8673 | 22.8531 | 22.7747 | 22.3944 | 21.7439 | 22.7131 | 21.8039 | 22.3703 | 22.3754 | 22.3508 | 22.0203 | 21.2399 | 22.2083 | 21.5832 | 21.7594 | 21.8858 | 21.0737 | 21.1764 | 21.3893 | 20.4696 | 20.6037 | 20.9046 | 21.8772 | 21.6459 | 21.2736 | 20.299 | 20.4214 | 20.3813 | 22.0662 | 21.6572 | 21.186 | 21.9945 | 21.7324 | 21.3479 | 19.9208 | 20.3848 |  | 20.4974 | 20.0176 | 20.1161 | 19.1146 |  | 17.0422 | 17.0375 | 16.7848 | 16.9691 | 16.9529 | 17.3791 | 17.7962 | 16.0782 | 16.9258 | 16.1691 | 17.0066 | 17.9656 | 40.2311 | 45.3291 | 39.8969 | 21.3773 |  |  | 0.49109 | -0.099289 | -94.1313 | 0.24703 | 0.20844 | -197.8315 | -0.66342 | -0.48137 | -0.084168 | -0.000728 | 0.052198 | 8.8285 | 9.0589 | 1.9786 | 21.7879 | 22.0141 | 22.1992 | 22.2676 | 22.0897 | 21.4069 | 20.2188 | 22.1983 | 22.3787 | 22.4054 | 22.3556 | 21.9845 | 21.2139 | 22.2686 | 17.1465 | 17.1836 | 16.294 | 16.2632 | 16.2802 | 17.1654 | 16.952 | 22.3944 | 22.1438 | 21.7122 | 22.0902 | 21.8112 | 21.3128 | 21.9496 | 21.5337 | 20.908 | 20.1076 | 20.3291 | 19.8883 | 19.8099 | 0.1339 | 0.24843 | 20.7534 | 22.0705 | 22.3786 | 20.1218 | 21.6613 | 22.11 | 21.9397 | 21.7011 | 21.2656 | 21.772 | 21.4395 | 21.0412 | 20.2886 | 20.3535 | 20.2527 | 20.2083 | 20.0628 |  | 20.2295 | 19.8597 | 20.1352 | 19.7018 | 20.0812 | 20.3072 |  | 20.3934 |  |  | 20.2991 | 20.4186 | 20.6109 | [5 empty] | 21.9275 | 20.3412 | 21.6665 | 22.045 | 19.5343 | 21.1553 | 21.7794 | 19.3722 | 19.9398 | 21.1356 |  | 19.8211 | 20.8921 | 18.8884 | 19.6764 | 20.7991 | 19.4181 | 20.0709 | 19.0288 | 20.08 | 19.1642 | 20.1992 | 18.8665 | 20.0801 | 21.0446 | 19.4332 | 19.7717 | 20.9728 | 18.9539 | 19.8106 | 20.7912 | 19.0308 | 20.0629 | 19.3204 | 19.9383 | 18.9354 | 20.0944 | -0.021279 | 20.9455 | 0.047842 | 0.016712 | -27.0079 | 3.0965 | -8.66 | -0.08 | 0.83671 | -0.37407 | -11.5179 | 0.59004 | 0.54231 | -16.7074 | -0.96751 | 0.42468 | 0.42716 | 0.42974 | 0.40488 | 0.4747 | 0.44068 | 0.42762
42838.4185 | -156 | 22.9001 | 22.8617 | 22.8484 | 22.7729 | 22.4046 | 21.7385 | 22.7157 | 21.8021 | 22.3693 | 22.3766 | 22.3557 | 22.0235 | 21.2401 | 22.2174 | 21.5956 | 21.7655 | 21.8975 | 21.0812 | 21.1818 | 21.4012 | 20.4764 | 20.6166 | 20.9164 | 21.8908 | 21.6502 | 21.2784 | 20.2979 | 20.4256 | 20.39 | 22.0665 | 21.6675 | 21.1866 | 21.9943 | 21.7368 | 21.3489 | 19.9222 | 20.3941 |  | 20.4961 | 20.0232 | 20.1195 | 19.1092 |  | 17.0513 | 17.0394 | 16.7677 | 16.9652 | 16.9441 | 17.3627 | 17.7546 | 16.0441 | 16.9207 | 16.1894 | 17.0061 | 17.9601 | 40.2069 | 45.5597 | 39.8819 | 21.3773 |  |  | 0.45298 | -0.090089 | -94.3166 | 0.2996 | 0.14667 | -197.8808 | -0.40649 | -0.48531 | -0.027734 | 0.16921 | 0.12094 | 8.829 | 9.0588 | 1.9786 | 21.7842 | 22.0101 | 22.2081 | 22.2657 | 22.0922 | 21.4 | 20.2145 | 22.1968 | 22.3769 | 22.4006 | 22.357 | 21.9836 | 21.2116 | 22.2744 | 17.1722 | 17.1868 | 16.3149 | 16.2644 | 16.2904 | 17.1595 | 16.9621 | 22.3874 | 22.1525 | 21.7154 | 22.0891 | 21.7979 | 21.307 | 21.953 | 21.529 | 20.903 | 20.1046 | 20.33 | 19.8865 | 19.8001 | 0.017313 | 0.26346 | 20.7646 | 22.0786 | 22.3861 | 20.1336 | 21.6768 | 22.1121 | 21.9518 | 21.7124 | 21.2835 | 21.7803 | 21.4435 | 21.0432 | 20.3033 | 20.3674 | 20.2719 | 20.2247 | 20.0744 |  | 20.2255 | 19.8561 | 20.1367 | 19.6994 | 20.0796 | 20.3055 |  | 20.3877 |  |  | 20.2919 | 20.4139 | 20.606 | [5 empty] | 21.9132 | 20.3406 | 21.6563 | 22.0288 | 19.5217 | 21.1543 | 21.772 | 19.3656 | 19.9397 | 21.1235 |  | 19.8158 | 20.8958 | 18.8894 | 19.6721 | 20.7978 | 19.4077 | 20.0584 | 19.0375 | 20.0722 | 19.1586 | 20.1926 | 18.8698 | 20.0865 | 21.0419 | 19.449 | 19.7748 | 20.9933 | 18.9618 | 19.815 | 20.8034 | 19.0291 | 20.0715 | 19.3282 | 19.9529 | 18.9447 | 20.1081 | -0.090471 | 20.9462 | 0.048733 | 0.017896 | -27.0553 | 3.0965 | -16.77 | -0.03 | 0.8036 | -0.35632 | -11.5293 | 0.6498 | 0.4549 | -16.709 | -0.75731 | 0.42423 | 0.42731 | 0.42975 | 0.40133 | 0.47356 | 0.44088 | 0.42779
42838.4185 | -155 | 22.8972 | 22.8708 | 22.8505 | 22.7752 | 22.4045 | 21.739 | 22.715 | 21.8023 | 22.3652 | 22.38 | 22.3597 | 22.0267 | 21.2417 | 22.2166 | 21.5867 | 21.7615 | 21.8922 | 21.0772 | 21.17 | 21.3882 | 20.4692 | 20.6102 | 20.9056 | 21.8788 | 21.6434 | 21.27 | 20.3005 | 20.4245 | 20.387 | 22.0649 | 21.6651 | 21.1796 | 21.9904 | 21.734 | 21.3469 | 19.919 | 20.4062 |  | 20.4917 | 20.017 | 20.1112 | 19.0907 |  | 17.0397 | 17.0382 | 16.7654 | 16.9549 | 16.9427 | 17.3494 | 17.7266 | 15.9585 | 16.9274 | 16.1575 | 17.0035 | 17.9617 | 40.1844 | 45.7835 | 39.8671 | 21.3877 |  |  | 0.43918 | -0.1098 | -94.2509 | 0.4192 | 0.19727 | -197.8197 | -0.90524 | -0.346 | -0.11102 | -0.24871 | -0.05231 | 8.8293 | 9.0591 | 1.9783 | 21.7832 | 21.9907 | 22.1911 | 22.2584 | 22.0843 | 21.3935 | 20.2068 | 22.1977 | 22.365 | 22.4001 | 22.3517 | 21.9684 | 21.205 | 22.2632 | 17.2159 | 17.2034 | 16.3044 | 16.2747 | 16.2839 | 17.1671 | 16.9677 | 22.3876 | 22.1498 | 21.7054 | 22.087 | 21.8038 | 21.3069 | 21.9475 | 21.5339 | 20.9042 | 20.103 | 20.3311 | 19.8868 | 19.7924 | -0.041667 | 0.054809 | 20.7596 | 22.0727 | 22.372 | 20.1322 | 21.6755 | 22.1142 | 21.9453 | 21.709 | 21.2732 | 21.7821 | 21.4397 | 21.0373 | 20.2932 | 20.3681 | 20.277 | 20.2173 | 20.075 |  | 20.2255 | 19.8574 | 20.1382 | 19.7077 | 20.0833 | 20.3071 |  | 20.3924 |  |  | 20.2729 | 20.411 | 20.6194 | [5 empty] | 21.9364 | 20.3317 | 21.6544 | 22.0262 | 19.5251 | 21.1559 | 21.7708 | 19.3689 | 19.9472 | 21.138 |  | 19.8128 | 20.8892 | 18.8971 | 19.6797 | 20.808 | 19.4152 | 20.0685 | 19.0478 | 20.0845 | 19.1609 | 20.2007 | 18.8681 | 20.0795 | 21.0425 | 19.4268 | 19.7724 | 20.9844 | 18.9521 | 19.8078 | 20.7882 | 19.0049 | 20.0639 | 19.3216 | 19.9438 | 18.9414 | 20.1025 | -0.10383 | 20.9443 | 0.047547 | 0.016306 | -27.1237 | 3.0965 | -1.06 | -0.07 | 0.79126 | -0.39339 | -11.5252 | 0.76863 | 0.52756 | -16.7061 | -1.1301 | 0.42421 | 0.42733 | 0.42965 | 0.39735 | 0.47538 | 0.44128 | 0.42795
42838.4185 | -154 | 22.9026 | 22.864 | 22.8551 | 22.7753 | 22.4029 | 21.7447 | 22.7216 | 21.8002 | 22.3642 | 22.3772 | 22.3591 | 22.0314 | 21.2439 | 22.2158 | 21.5877 | 21.7644 | 21.8895 | 21.076 | 21.1661 | 21.39 | 20.4686 | 20.603 | 20.9053 | 21.8759 | 21.6433 | 21.2694 | 20.2974 | 20.4251 | 20.382 | 22.0686 | 21.6651 | 21.1866 | 21.9965 | 21.7368 | 21.3518 | 19.9211 | 20.4257 |  | 20.5013 | 20.0315 | 20.1083 | 19.0871 |  | 17.0343 | 17.0248 | 16.7513 | 16.939 | 16.9326 | 17.335 | 17.71 | 15.8615 | 16.9247 | 16.1326 | 16.9904 | 17.971 | 40.1734 | 46.0062 | 39.8662 | 21.3884 |  |  | 0.39976 | 0.081415 | -94.0498 | 0.35677 | 0.18412 | -197.8611 | -0.1029 | -0.24086 | -0.067433 | 0.17823 | 0.044906 | 8.8298 | 9.0597 | 1.9784 | 21.7879 | 22.0106 | 22.2 | 22.263 | 22.0931 | 21.4106 | 20.2162 | 22.2023 | 22.3745 | 22.4092 | 22.3533 | 21.9851 | 21.2277 | 22.275 | 17.254 | 17.1736 | 16.3049 | 16.2763 | 16.288 | 17.1682 | 16.969 | 22.3847 | 22.1513 | 21.7031 | 22.0758 | 21.8028 | 21.2992 | 21.943 | 21.5242 | 20.9085 | 20.104 | 20.3261 | 19.8862 | 19.7902 | -0.0015606 | 0.11624 | 20.7719 | 22.0798 | 22.378 | 20.1411 | 21.676 | 22.1182 | 21.9513 | 21.7228 | 21.2852 | 21.7816 | 21.4483 | 21.0473 | 20.2965 | 20.3701 | 20.2788 | 20.2252 | 20.0797 |  | 20.232 | 19.8653 | 20.1376 | 19.7169 | 20.0849 | 20.3216 |  | 20.4075 |  |  | 20.2753 | 20.4094 | 20.616 | [5 empty] | 21.9289 | 20.3433 | 21.6623 | 22.0402 | 19.5309 | 21.1522 | 21.7788 | 19.3628 | 19.9432 | 21.1372 |  | 19.7929 | 20.8895 | 18.8863 | 19.663 | 20.8 | 19.4151 | 20.0721 | 19.0431 | 20.0789 | 19.1517 | 20.2033 | 18.875 | 20.0721 | 21.0415 | 19.4334 | 19.7764 | 20.9868 | 18.9557 | 19.81 | 20.7923 | 19.0021 | 20.0591 | 19.3278 | 19.9515 | 18.9445 | 20.0994 | -0.061718 | 20.9467 | 0.046545 | 0.014484 | -27.1522 | 3.0965 | -1.83 | -0.13 | 0.75491 | 0.33873 | -11.5127 | 0.70907 | 0.50966 | -16.7074 | -0.38102 | 0.4243 | 0.42709 | 0.42945 | 0.39326 | 0.47548 | 0.44145 | 0.42805
42838.4185 | -153 | 22.9046 | 22.8678 | 22.8503 | 22.7709 | 22.4054 | 21.7468 | 22.717 | 21.8073 | 22.3678 | 22.3755 | 22.3578 | 22.0312 | 21.2516 | 22.2181 | 21.5885 | 21.7601 | 21.8909 | 21.0775 | 21.1749 | 21.3941 | 20.4783 | 20.6106 | 20.9061 | 21.8798 | 21.6442 | 21.2748 | 20.2925 | 20.4245 | 20.3764 | 22.0744 | 21.6593 | 21.1894 | 21.9983 | 21.7353 | 21.3606 | 19.9199 | 20.4441 |  | 20.5058 | 20.0269 | 20.1129 | 19.082 |  | 17.0368 | 17.0146 | 16.7465 | 16.937 | 16.9307 | 17.3194 | 17.7439 | 15.8572 | 16.9283 | 16.1572 | 16.9934 | 17.9779 | 40.1817 | 46.2373 | 39.8701 | 21.3946 |  |  | 0.38201 | -0.41931 | -93.7804 | 0.57296 | 0.3898 | -197.8394 | -0.49455 | -0.38674 | 0.033175 | 0.21432 | -0.0094304 | 8.8287 | 9.0584 | 1.9784 | 21.7851 | 22.0077 | 22.2045 | 22.262 | 22.0858 | 21.4092 | 20.2174 | 22.2005 | 22.3758 | 22.4082 | 22.3611 | 21.9852 | 21.2233 | 22.2675 | 17.2909 | 17.1769 | 16.2978 | 16.2726 | 16.2987 | 17.1638 | 16.9672 | 22.3779 | 22.1416 | 21.7059 | 22.0821 | 21.7961 | 21.3009 | 21.9374 | 21.5257 | 20.898 | 20.0987 | 20.3144 | 19.89 | 19.785 | -0.0080484 | -0.063686 | 20.764 | 22.0769 | 22.375 | 20.1421 | 21.6739 | 22.116 | 21.9422 | 21.7158 | 21.2731 | 21.7741 | 21.4431 | 21.046 | 20.2923 | 20.3629 | 20.2724 | 20.2239 | 20.0566 |  | 20.2297 | 19.8686 | 20.1406 | 19.7148 | 20.0864 | 20.3158 |  | 20.3983 |  |  | 20.2669 | 20.4073 | 20.6136 | [5 empty] | 21.9268 | 20.3409 | 21.6603 | 22.0355 | 19.5263 | 21.1516 | 21.7743 | 19.36 | 19.9427 | 21.1298 |  | 19.7801 | 20.8917 | 18.8943 | 19.6684 | 20.8106 | 19.4175 | 20.0707 | 19.0477 | 20.0811 | 19.1507 | 20.2044 | 18.8777 | 20.0659 | 21.0358 | 19.434 | 19.7863 | 20.9796 | 18.9555 | 19.8073 | 20.7926 | 18.9938 | 20.0617 | 19.3361 | 19.9559 | 18.9378 | 20.1004 | -0.086205 | 20.9465 | 0.048573 | 0.013954 | -27.1003 | 3.0964 | -15.59 | -0.08 | 0.73796 | -0.7687 | -11.496 | 0.89857 | 0.74155 | -16.706 | -0.83526 | 0.42486 | 0.4271 | 0.42956 | 0.38864 | 0.47605 | 0.44156 | 0.42801
42838.4185 | -152 | 22.892 | 22.8637 | 22.8503 | 22.7754 | 22.4117 | 21.7493 | 22.7224 | 21.8041 | 22.3656 | 22.38 | 22.357 | 22.0268 | 21.2499 | 22.2149 | 21.5946 | 21.7628 | 21.8963 | 21.0756 | 21.1825 | 21.3964 | 20.4811 | 20.6131 | 20.9069 | 21.8843 | 21.6516 | 21.2777 | 20.2952 | 20.4259 | 20.3715 | 22.063 | 21.6676 | 21.19 | 21.9965 | 21.7316 | 21.3475 | 19.9174 | 20.4643 |  | 20.5004 | 20.0203 | 20.1078 | 19.0764 |  | 17.0308 | 17.0175 | 16.7469 | 16.9437 | 16.9391 | 17.3541 | 17.7774 | 15.8457 | 16.9344 | 16.2058 | 16.9976 | 17.9759 | 40.1686 | 46.4555 | 39.8756 | 21.3893 |  |  | 0.49241 | -0.44428 | -93.2652 | 0.35283 | 0.24852 | -197.8131 | 0.081089 | -0.35652 | -0.018199 | 0.069135 | 0.065912 | 8.8286 | 9.0589 | 1.9789 | 21.7833 | 22.0013 | 22.2001 | 22.2636 | 22.0836 | 21.4064 | 20.2165 | 22.1999 | 22.3713 | 22.4113 | 22.3545 | 21.9852 | 21.2157 | 22.2681 | 17.3024 | 17.1969 | 16.2814 | 16.2911 | 16.313 | 17.1645 | 16.9636 | 22.3857 | 22.1536 | 21.7078 | 22.0844 | 21.7906 | 21.3065 | 21.9497 | 21.5235 | 20.906 | 20.1052 | 20.3391 | 19.8941 | 19.7936 | -0.12974 | 0.0278 | 20.7661 | 22.074 | 22.3682 | 20.128 | 21.6635 | 22.1057 | 21.9399 | 21.702 | 21.2743 | 21.7658 | 21.4379 | 21.0371 | 20.2745 | 20.361 | 20.2715 | 20.2087 | 20.0505 |  | 20.2295 | 19.8661 | 20.1305 | 19.7121 | 20.0818 | 20.3102 |  | 20.3933 |  |  | 20.2735 | 20.4163 | 20.6158 | [5 empty] | 21.9291 | 20.3409 | 21.6658 | 22.0377 | 19.5398 | 21.1528 | 21.7764 | 19.3631 | 19.9451 | 21.1379 |  | 19.7716 | 20.8917 | 18.8888 | 19.6784 | 20.8136 | 19.42 | 20.0739 | 19.0542 | 20.0782 | 19.153 | 20.208 | 18.8688 | 20.0617 | 21.0298 | 19.4294 | 19.7844 | 20.983 | 18.9549 | 19.8046 | 20.794 | 18.9858 | 20.0637 | 19.3225 | 19.9543 | 18.9336 | 20.0992 | 0.012296 | 20.946 | 0.049071 | 0.015094 | -27.088 | 3.0964 | -17.77 | 0.06 | 0.83782 | -0.79126 | -11.4644 | 0.70513 | 0.59214 | -16.7059 | 0.33824 | 0.42502 | 0.42683 | 0.42948 | 0.38745 | 0.47745 | 0.44163 | 0.428
42838.4185 | -151 | 22.8861 | 22.8513 | 22.8393 | 22.7618 | 22.3938 | 21.736 | 22.707 | 21.7936 | 22.3541 | 22.3716 | 22.3469 | 22.0215 | 21.2332 | 22.1999 | 21.5881 | 21.7592 | 21.8956 | 21.0764 | 21.1816 | 21.3974 | 20.4752 | 20.6131 | 20.9123 | 21.8871 | 21.6513 | 21.2815 | 20.2995 | 20.4226 | 20.3681 | 22.0714 | 21.676 | 21.1845 | 21.993 | 21.7389 | 21.3525 | 19.9271 | 20.4817 |  | 20.51 | 20.0229 | 20.1052 | 19.0613 |  | 17.0242 | 17.0093 | 16.7447 | 16.9439 | 16.979 | 17.409 | 17.791 | 15.8131 | 16.9355 | 16.2447 | 17.0077 | 17.9739 | 40.1687 | 46.6829 | 39.8855 | 21.3894 |  |  | 0.49438 | -0.27014 | -92.8263 | 0.24703 | -0.009724 | -197.8118 | -0.28624 | -0.24875 | -0.11433 | 0.21914 | 0.051677 | 8.8285 | 9.0583 | 1.9792 | 21.7793 | 22.0002 | 22.1943 | 22.2579 | 22.0826 | 21.4045 | 20.2106 | 22.1955 | 22.3652 | 22.4026 | 22.3501 | 21.9798 | 21.2083 | 22.2639 | 17.2976 | 17.2026 | 16.2687 | 16.2835 | 16.3348 | 17.1635 | 16.9654 | 22.3858 | 22.1478 | 21.6994 | 22.0827 | 21.7968 | 21.3069 | 21.9501 | 21.5249 | 20.9045 | 20.119 | 20.329 | 19.894 | 19.771 | 0.066463 | -0.035536 | 20.7625 | 22.0824 | 22.3725 | 20.1407 | 21.6748 | 22.1133 | 21.9387 | 21.7107 | 21.2779 | 21.7775 | 21.4495 | 21.0468 | 20.2981 | 20.372 | 20.2682 | 20.2042 | 20.0633 |  | 20.2286 | 19.8737 | 20.1399 | 19.7174 | 20.0909 | 20.3124 |  | 20.3999 |  |  | 20.2711 | 20.4004 | 20.6103 | [5 empty] | 21.9227 | 20.3377 | 21.6561 | 22.0353 | 19.5285 | 21.1501 | 21.7692 | 19.3601 | 19.9403 | 21.1368 |  | 19.7666 | 20.8866 | 18.8716 | 19.6667 | 20.8038 | 19.4097 | 20.0689 | 19.0497 | 20.0723 | 19.1532 | 20.1994 | 18.8675 | 20.0629 | 21.0332 | 19.4264 | 19.7728 | 20.987 | 18.9552 | 19.8016 | 20.7891 | 18.979 | 20.0582 | 19.3136 | 19.9565 | 18.9437 | 20.0984 | -0.16022 | 20.9447 | 0.048499 | 0.015101 | -27.0613 | 3.0964 | -9.94 | -0.15 | 0.83949 | -0.61699 | -11.4372 | 0.59001 | -0.11714 | -16.7075 | -0.63555 | 0.42464 | 0.42693 | 0.42964 | 0.38786 | 0.47908 | 0.44237 | 0.42908
42838.4185 | -150 | 22.9086 | 22.8694 | 22.8519 | 22.7775 | 22.4058 | 21.7513 | 22.7281 | 21.816 | 22.3732 | 22.3796 | 22.3624 | 22.0281 | 21.2465 | 22.2195 | 21.5882 | 21.7591 | 21.892 | 21.0706 | 21.1788 | 21.3903 | 20.4715 | 20.6141 | 20.9041 | 21.8808 | 21.6437 | 21.2784 | 20.2972 | 20.4211 | 20.3625 | 22.0652 | 21.6656 | 21.1875 | 21.9966 | 21.7359 | 21.3501 | 19.9232 | 20.4925 |  | 20.508 | 20.0269 | 20.1027 | 19.0414 |  | 17.0186 | 17.0061 | 16.7593 | 16.9735 | 17.0021 | 17.4401 | 17.7841 | 15.8649 | 16.9329 | 16.2259 | 16.9984 | 17.9766 | 40.1876 | 46.9183 | 39.9017 | 21.3977 |  |  | 0.43458 | -0.29708 | -93.3572 | 0.75827 | 0.10527 | -197.8276 | -0.035223 | -0.3138 | -0.10655 | 0.11047 | -0.020367 | 8.8285 | 9.0581 | 1.9788 | 21.7803 | 22.0023 | 22.1944 | 22.2561 | 22.0844 | 21.394 | 20.2146 | 22.1964 | 22.3642 | 22.4024 | 22.3445 | 21.9792 | 21.209 | 22.2656 | 17.2931 | 17.2225 | 16.2518 | 16.2598 | 16.3644 | 17.1738 | 16.9682 | 22.3908 | 22.1544 | 21.7108 | 22.0865 | 21.7993 | 21.3115 | 21.9521 | 21.5341 | 20.9061 | 20.1181 | 20.3332 | 19.896 | 19.7532 | -0.068798 | -0.080614 | 20.7645 | 22.0793 | 22.3749 | 20.1385 | 21.6663 | 22.1147 | 21.9383 | 21.7089 | 21.2784 | 21.7749 | 21.4451 | 21.0336 | 20.2813 | 20.3614 | 20.268 | 20.2161 | 20.0728 |  | 20.225 | 19.8586 | 20.1343 | 19.7231 | 20.0894 | 20.3159 |  | 20.3978 |  |  | 20.2622 | 20.3912 | 20.6075 | [5 empty] | 21.92 | 20.3349 | 21.6592 | 22.0362 | 19.5213 | 21.1532 | 21.7673 | 19.3576 | 19.9327 | 21.1296 |  | 19.7722 | 20.881 | 18.874 | 19.6696 | 20.8009 | 19.4087 | 20.0691 | 19.0542 | 20.0765 | 19.1512 | 20.2073 | 18.8666 | 20.0726 | 21.0409 | 19.4248 | 19.77 | 20.9847 | 18.9524 | 19.8066 | 20.789 | 18.9745 | 20.0595 | 19.314 | 19.9583 | 18.9567 | 20.1017 | -0.10828 | 20.9442 | 0.04853 | 0.015551 | -27.164 | 3.0965 | -7.32 | -0.04 | 0.78708 | -0.64702 | -11.4698 | 1.0337 | 0.38545 | -16.709 | -0.22296 | 0.42425 | 0.42716 | 0.42942 | 0.38957 | 0.48129 | 0.44279 | 0.42955
42838.4186 | -149 | 22.9019 | 22.8652 | 22.8468 | 22.771 | 22.3986 | 21.7473 | 22.7197 | 21.802 | 22.3687 | 22.3728 | 22.3525 | 22.0224 | 21.2373 | 22.2138 | 21.5888 | 21.7632 | 21.89 | 21.0652 | 21.1743 | 21.3896 | 20.4716 | 20.6037 | 20.9006 | 21.8833 | 21.6438 | 21.2737 | 20.2858 | 20.4203 | 20.3627 | 22.0692 | 21.6687 | 21.1922 | 22.0005 | 21.7375 | 21.3478 | 19.9244 | 20.5037 |  | 20.499 | 20.0261 | 20.099 | 19.0317 |  | 17.0228 | 17.0126 | 16.7657 | 17.0015 | 16.9968 | 17.4724 | 17.8195 | 15.93 | 16.946 | 16.2022 | 17.0081 | 17.9711 | 40.2021 | 47.1373 | 39.9253 | 21.3831 |  |  | 0.37413 | -0.25634 | -93.26 | 0.72673 | 0.050072 | -197.8486 | 0.11 | -0.27964 | -0.29064 | 0.089066 | 0.044212 | 8.8283 | 9.0582 | 1.9787 | 21.7845 | 22.0175 | 22.2072 | 22.2694 | 22.0909 | 21.4126 | 20.219 | 22.2019 | 22.375 | 22.4149 | 22.3661 | 21.9894 | 21.2232 | 22.2792 | 17.2653 | 17.2432 | 16.2313 | 16.2355 | 16.3694 | 17.1724 | 16.9695 | 22.3879 | 22.1521 | 21.7111 | 22.0849 | 21.7928 | 21.3023 | 21.944 | 21.5316 | 20.901 | 20.0983 | 20.33 | 19.8892 | 19.7172 | 0.020459 | -0.073767 | 20.7634 | 22.0767 | 22.3727 | 20.1246 | 21.6695 | 22.1151 | 21.9414 | 21.7021 | 21.2698 | 21.7723 | 21.4441 | 21.0372 | 20.2913 | 20.367 | 20.2614 | 20.2111 | 20.063 |  | 20.226 | 19.8512 | 20.1401 | 19.7284 | 20.083 | 20.3135 |  | 20.3995 |  |  | 20.2555 | 20.3948 | 20.6134 | [5 empty] | 21.9248 | 20.3358 | 21.6612 | 22.0405 | 19.5325 | 21.1553 | 21.77 | 19.362 | 19.9213 | 21.1325 |  | 19.7791 | 20.8834 | 18.8806 | 19.6834 | 20.7982 | 19.4091 | 20.076 | 19.072 | 20.0772 | 19.1512 | 20.2212 | 18.8628 | 20.0686 | 21.0358 | 19.423 | 19.7631 | 20.9767 | 18.9558 | 19.7968 | 20.7848 | 18.9585 | 20.0544 | 19.3068 | 19.9493 | 18.9455 | 20.0981 | -0.025546 | 20.9502 | 0.047971 | 0.014433 | -27.0557 | 3.0964 | -15.22 | -0.03 | 0.73028 | -0.60103 | -11.464 | 1.012 | 0.26585 | -16.7108 | 0.39403 | 0.42456 | 0.42756 | 0.42906 | 0.39249 | 0.48372 | 0.4431 | 0.42989
42838.4186 | -148 | 22.8911 | 22.8623 | 22.8497 | 22.7729 | 22.4031 | 21.7391 | 22.7122 | 21.7977 | 22.3661 | 22.3706 | 22.3527 | 22.015 | 21.2325 | 22.2108 | 21.5803 | 21.757 | 21.8945 | 21.0731 | 21.1704 | 21.3899 | 20.4705 | 20.6066 | 20.9054 | 21.8833 | 21.6421 | 21.276 | 20.2895 | 20.4191 | 20.3563 | 22.0612 | 21.6744 | 21.1885 | 21.9983 | 21.7323 | 21.3472 | 19.9175 | 20.5086 |  | 20.4999 | 20.0235 | 20.0847 | 19.0121 |  | 17.0272 | 17.0018 | 16.7603 | 16.9992 | 16.9944 | 17.4948 | 17.83 | 15.9898 | 16.9402 | 16.2364 | 17.0056 | 17.9734 | 40.2302 | 47.36 | 39.9584 | 21.3922 |  |  | 0.44575 | -0.37594 | -93.4013 | 0.67153 | 0.31752 | -197.8447 | -0.18964 | -0.22115 | -0.26106 | 0.15075 | 0.12719 | 8.8297 | 9.0595 | 1.9787 | 21.7837 | 22.0084 | 22.1962 | 22.2637 | 22.0803 | 21.4068 | 20.2172 | 22.1942 | 22.3787 | 22.4087 | 22.3588 | 21.9821 | 21.2092 | 22.2728 | 17.2454 | 17.2449 | 16.2305 | 16.2202 | 16.3583 | 17.1663 | 16.9663 | 22.3831 | 22.1542 | 21.7033 | 22.0818 | 21.7973 | 21.3024 | 21.9417 | 21.5256 | 20.9036 | 20.0957 | 20.3236 | 19.8796 | 19.6679 | -0.020238 | -0.024885 | 20.7591 | 22.0703 | 22.3601 | 20.1173 | 21.6637 | 22.1096 | 21.9439 | 21.7152 | 21.2746 | 21.7735 | 21.4383 | 21.0358 | 20.2795 | 20.3588 | 20.2658 | 20.2027 | 20.0219 |  | 20.2329 | 19.8513 | 20.1412 | 19.7248 | 20.0906 | 20.3181 |  | 20.393 |  |  | 20.2579 | 20.3878 | 20.6054 | [5 empty] | 21.9219 | 20.3289 | 21.6538 | 22.0333 | 19.5268 | 21.151 | 21.7702 | 19.3574 | 19.9104 | 21.1274 |  | 19.7681 | 20.878 | 18.8732 | 19.6892 | 20.7975 | 19.4005 | 20.0717 | 19.068 | 20.0716 | 19.1507 | 20.212 | 18.8617 | 20.0667 | 21.0328 | 19.4152 | 19.7632 | 20.9764 | 18.956 | 19.7961 | 20.7834 | 18.9495 | 20.0513 | 19.3092 | 19.9498 | 18.9475 | 20.0962 | -0.03241 | 20.9461 | 0.046306 | 0.013206 | -27.0634 | 3.0964 | -16.18 | -0.15 | 0.79712 | -0.72784 | -11.4724 | 0.97277 | 0.66947 | -16.7113 | -0.51739 | 0.42593 | 0.4276 | 0.42942 | 0.394 | 0.48342 | 0.44342 | 0.43117
42838.4186 | -147 | 22.897 | 22.8626 | 22.8485 | 22.7731 | 22.4048 | 21.7428 | 22.7113 | 21.7967 | 22.3681 | 22.3803 | 22.3576 | 22.0269 | 21.2346 | 22.2092 | 21.5883 | 21.7702 | 21.895 | 21.0805 | 21.177 | 21.3963 | 20.479 | 20.621 | 20.9048 | 21.8826 | 21.6488 | 21.2742 | 20.3013 | 20.4273 | 20.3604 | 22.0618 | 21.6631 | 21.1841 | 21.9966 | 21.7313 | 21.3491 | 19.918 | 20.5085 |  | 20.5048 | 20.0229 | 20.0821 | 18.9982 |  | 17.0317 | 16.9967 | 16.7632 | 16.9892 | 16.9895 | 17.5058 | 17.8433 | 16.0414 | 16.9429 | 16.2223 | 17.0153 | 17.9752 | 40.2721 | 47.5941 | 39.9933 | 21.388 |  |  | 0.44838 | -0.14529 | -93.2238 | 0.64065 | 0.17164 | -197.821 | 0.27034 | -0.20078 | -0.10713 | 0.052561 | 0.16209 | 8.8289 | 9.0589 | 1.9787 | 21.7824 | 21.9993 | 22.1979 | 22.2632 | 22.0836 | 21.4082 | 20.2168 | 22.2051 | 22.3806 | 22.3995 | 22.3662 | 21.9827 | 21.2148 | 22.2671 | 17.2299 | 17.2143 | 16.2153 | 16.1968 | 16.3447 | 17.1684 | 16.9679 | 22.3803 | 22.1495 | 21.7049 | 22.085 | 21.7982 | 21.2979 | 21.9396 | 21.5244 | 20.9045 | 20.0992 | 20.3135 | 19.8712 | 19.6412 | 0.043264 | -0.042384 | 20.7637 | 22.0778 | 22.376 | 20.1232 | 21.664 | 22.1171 | 21.9513 | 21.7089 | 21.2759 | 21.7848 | 21.4445 | 21.0397 | 20.2797 | 20.3572 | 20.2696 | 20.2126 | 19.9642 |  | 20.2194 | 19.8484 | 20.1381 | 19.7171 | 20.0966 | 20.3056 |  | 20.3954 |  |  | 20.26 | 20.3789 | 20.6068 | [5 empty] | 21.9251 | 20.3308 | 21.6575 | 22.0325 | 19.5355 | 21.1515 | 21.7704 | 19.3565 | 19.9032 | 21.1253 |  | 19.7717 | 20.8809 | 18.8743 | 19.6938 | 20.8001 | 19.3959 | 20.0663 | 19.0663 | 20.0691 | 19.1573 | 20.2105 | 18.8669 | 20.0699 | 21.0352 | 19.4202 | 19.7639 | 20.9714 | 18.9573 | 19.8021 | 20.7864 | 18.9457 | 20.0516 | 19.3112 | 19.9573 | 18.9495 | 20.0994 | -0.066541 | 20.9469 | 0.047442 | 0.013409 | -27.0306 | 3.0964 | -16.12 | -0.02 | 0.79947 | -0.45247 | -11.4614 | 0.95013 | 0.49223 | -16.7106 | 0.61775 | 0.42708 | 0.42758 | 0.42983 | 0.39596 | 0.4853 | 0.44382 | 0.43203
42838.4186 | -146 | 22.8984 | 22.8632 | 22.8543 | 22.7772 | 22.4053 | 21.7483 | 22.7157 | 21.8045 | 22.367 | 22.3764 | 22.362 | 22.0319 | 21.2453 | 22.2174 | 21.5926 | 21.7609 | 21.9002 | 21.0838 | 21.1767 | 21.3986 | 20.481 | 20.613 | 20.9152 | 21.8868 | 21.6524 | 21.2732 | 20.2923 | 20.4275 | 20.3558 | 22.0658 | 21.6586 | 21.1869 | 22.0022 | 21.7386 | 21.3478 | 19.9146 | 20.5143 |  | 20.5015 | 20.0309 | 20.0804 | 18.9976 |  | 17.033 | 17.0118 | 16.779 | 16.9999 | 16.9917 | 17.5021 | 17.8344 | 16.0695 | 16.9431 | 16.1679 | 17.014 | 17.9736 | 40.3203 | 47.8075 | 40.0426 | 21.3935 |  |  | 0.36821 | -0.11506 | -93.2869 | 0.76944 | 0.33723 | -197.8683 | -0.071363 | -0.40843 | -0.089228 | 0.19837 | -0.14154 | 8.8281 | 9.0581 | 1.9784 | 21.7854 | 22.0044 | 22.1967 | 22.2618 | 22.0875 | 21.4045 | 20.2191 | 22.2012 | 22.3715 | 22.4054 | 22.3571 | 21.9832 | 21.2202 | 22.2652 | 17.209 | 17.1947 | 16.2003 | 16.1829 | 16.307 | 17.1728 | 16.9716 | 22.3826 | 22.1539 | 21.704 | 22.0833 | 21.805 | 21.3073 | 21.9453 | 21.5312 | 20.9047 | 20.102 | 20.3109 | 19.8632 | 19.6283 | 0.069019 | 0.072878 | 20.7696 | 22.0799 | 22.3782 | 20.1314 | 21.669 | 22.1179 | 21.949 | 21.714 | 21.2798 | 21.7865 | 21.4516 | 21.0444 | 20.2886 | 20.3552 | 20.2628 | 20.2079 | 19.9116 |  | 20.2233 | 19.8294 | 20.1298 | 19.6927 | 20.0718 | 20.3009 |  | 20.3956 |  |  | 20.2613 | 20.3869 | 20.6007 | [5 empty] | 21.9285 | 20.3373 | 21.6574 | 22.0352 | 19.5401 | 21.1574 | 21.7705 | 19.3623 | 19.9042 | 21.1285 |  | 19.7816 | 20.8844 | 18.8831 | 19.6955 | 20.7988 | 19.3884 | 20.0626 | 19.0864 | 20.0702 | 19.1656 | 20.2114 | 18.869 | 20.0696 | 21.031 | 19.4204 | 19.7577 | 20.978 | 18.9533 | 19.7943 | 20.7887 | 18.9434 | 20.0556 | 19.3016 | 19.9554 | 18.9501 | 20.1015 | -0.10513 | 20.9468 | 0.048192 | 0.015377 | -27.0839 | 3.0964 | -3.95 | -0.17 | 0.72448 | -0.40267 | -11.4656 | 1.0413 | 0.68995 | -16.7125 | -0.31739 | 0.42867 | 0.42782 | 0.42968 | 0.39879 | 0.4874 | 0.44372 | 0.43248
42838.4186 | -145 | 22.9017 | 22.868 | 22.8619 | 22.7695 | 22.405 | 21.7429 | 22.7141 | 21.7984 | 22.3718 | 22.3691 | 22.358 | 22.0236 | 21.2487 | 22.2115 | 21.5851 | 21.7691 | 21.9006 | 21.0871 | 21.1765 | 21.4018 | 20.4719 | 20.6195 | 20.906 | 21.8844 | 21.6413 | 21.2835 | 20.2954 | 20.429 | 20.3621 | 22.0742 | 21.6771 | 21.1933 | 22.0044 | 21.7433 | 21.3553 | 19.9189 | 20.5225 |  | 20.5048 | 20.0333 | 20.0832 | 18.9841 |  | 17.0393 | 17.0131 | 16.8072 | 17.0259 | 16.9938 | 17.5149 | 17.8096 | 16.0379 | 16.938 | 16.1736 | 17.0012 | 17.9682 | 40.3788 | 48.0292 | 40.0931 | 21.4089 |  |  | 0.49833 | -0.17617 | -93.2133 | 0.67941 | 0.23866 | -197.8558 | 0.37285 | -0.18764 | -0.29181 | -0.13122 | 0.046469 | 8.8289 | 9.0589 | 1.978 | 21.7805 | 22.0067 | 22.192 | 22.2552 | 22.0799 | 21.3979 | 20.2159 | 22.1952 | 22.3672 | 22.4082 | 22.3493 | 21.9789 | 21.215 | 22.2646 | 17.1839 | 17.2019 | 16.1666 | 16.1637 | 16.2798 | 17.175 | 16.9752 | 22.3896 | 22.1519 | 21.7072 | 22.09 | 21.8029 | 21.3064 | 21.9459 | 21.5322 | 20.9018 | 20.102 | 20.2925 | 19.8351 | 19.624 | 0.066463 | 0.0078292 | 20.7684 | 22.0812 | 22.3737 | 20.1303 | 21.6688 | 22.1084 | 21.9478 | 21.7124 | 21.2805 | 21.7857 | 21.4398 | 21.0416 | 20.2867 | 20.3507 | 20.2688 | 20.1992 | 19.9125 |  | 20.2283 | 19.8223 | 20.1381 | 19.6795 | 20.0832 | 20.3107 |  | 20.4016 |  |  | 20.2644 | 20.3915 | 20.6003 | [5 empty] | 21.9277 | 20.3334 | 21.6591 | 22.0372 | 19.5464 | 21.1602 | 21.7777 | 19.3544 | 19.9117 | 21.1311 |  | 19.7806 | 20.8831 | 18.8863 | 19.7014 | 20.8034 | 19.3921 | 20.0671 | 19.0944 | 20.0708 | 19.1677 | 20.2117 | 18.8684 | 20.0712 | 21.0274 | 19.4214 | 19.7587 | 20.9728 | 18.9453 | 19.7937 | 20.7829 | 18.9344 | 20.0593 | 19.2906 | 19.9531 | 18.9591 | 20.0926 | -0.063574 | 20.9459 | 0.048585 | 0.015841 | -27.0272 | 3.0963 | 6.43 | -0.03 | 0.84282 | -0.49826 | -11.4611 | 0.97849 | 0.58044 | -16.7124 | 0.72549 | 0.42882 | 0.4283 | 0.43043 | 0.40184 | 0.49156 | 0.44424 | 0.4326
42838.4186 | -144 | 22.8961 | 22.8588 | 22.8533 | 22.7784 | 22.4097 | 21.739 | 22.7161 | 21.7976 | 22.3671 | 22.3778 | 22.3545 | 22.0279 | 21.2334 | 22.2094 | 21.5928 | 21.7604 | 21.9026 | 21.0832 | 21.1754 | 21.3963 | 20.4792 | 20.6089 | 20.914 | 21.8868 | 21.6463 | 21.2873 | 20.286 | 20.4274 | 20.368 | 22.0674 | 21.6705 | 21.1946 | 21.9937 | 21.7397 | 21.352 | 19.9211 | 20.5191 |  | 20.5049 | 20.0344 | 20.0773 | 18.9725 |  | 17.0482 | 17.0295 | 16.8304 | 17.0506 | 16.9944 | 17.515 | 17.7939 | 16.0219 | 16.9406 | 16.2643 | 17.0158 | 17.9852 | 40.4564 | 48.2527 | 40.1588 | 21.4131 |  |  | 0.37479 | -0.038837 | -93.789 | 0.95475 | 0.1861 | -197.8447 | -0.17716 | -0.22312 | -0.26164 | 0.019413 | 0.05567 | 8.8273 | 9.0573 | 1.9786 | 21.7781 | 22.0005 | 22.1882 | 22.2557 | 22.074 | 21.3961 | 20.2109 | 22.1923 | 22.3669 | 22.4 | 22.3455 | 21.9779 | 21.2043 | 22.2585 | 17.1733 | 17.2056 | 16.1464 | 16.1741 | 16.2923 | 17.1731 | 16.9682 | 22.3777 | 22.1435 | 21.701 | 22.0776 | 21.802 | 21.3055 | 21.9443 | 21.5235 | 20.8962 | 20.093 | 20.2575 | 19.8038 | 19.6104 | 0.018493 | 0.10673 | 20.747 | 22.0712 | 22.3678 | 20.1211 | 21.6626 | 22.0998 | 21.9454 | 21.692 | 21.2692 | 21.7698 | 21.4347 | 21.0433 | 20.2719 | 20.341 | 20.2496 | 20.1929 | 19.9127 |  | 20.2234 | 19.8065 | 20.1374 | 19.6529 | 20.0857 | 20.3101 |  | 20.3916 |  |  | 20.2703 | 20.3754 | 20.5974 | [5 empty] | 21.931 | 20.3333 | 21.6629 | 22.0451 | 19.546 | 21.1553 | 21.7766 | 19.3561 | 19.9058 | 21.1159 |  | 19.7701 | 20.876 | 18.8765 | 19.699 | 20.789 | 19.3758 | 20.0617 | 19.0913 | 20.0689 | 19.1575 | 20.2165 | 18.8639 | 20.0781 | 21.0306 | 19.4167 | 19.7626 | 20.9776 | 18.9567 | 19.7973 | 20.7808 | 18.9277 | 20.0599 | 19.2949 | 19.9523 | 18.957 | 20.1016 | -0.064687 | 20.9465 | 0.048997 | 0.015587 | -27.0428 | 3.0963 | -9.28 | -0.12 | 0.73093 | -0.23395 | -11.4968 | 1.16 | 0.51254 | -16.7119 | -0.50009 | 0.42865 | 0.42871 | 0.43125 | 0.4028 | 0.49299 | 0.44464 | 0.43268
42838.4186 | -143 | 22.8978 | 22.8622 | 22.8497 | 22.7727 | 22.4024 | 21.7375 | 22.7164 | 21.8016 | 22.3678 | 22.3741 | 22.3534 | 22.0315 | 21.24 | 22.208 | 21.588 | 21.7656 | 21.8943 | 21.0745 | 21.1733 | 21.3854 | 20.4717 | 20.6085 | 20.9063 | 21.8847 | 21.6402 | 21.2784 | 20.2872 | 20.427 | 20.3626 | 22.072 | 21.6759 | 21.19 | 21.9974 | 21.7385 | 21.3563 | 19.9264 | 20.5285 |  | 20.5057 | 20.037 | 20.0763 | 18.981 |  | 17.0514 | 17.0433 | 16.8397 | 17.0491 | 16.9775 | 17.4995 | 17.7923 | 16.0415 | 16.9423 | 16.3373 | 17.0185 | 17.9839 | 40.5257 | 48.4779 | 40.2172 | 21.4061 |  |  | 0.50424 | -0.27145 | -94.2772 | 0.59333 | 0.11381 | -197.8493 | 0.16191 | -0.45443 | -0.047584 | 0.14382 | 0.068342 | 8.8293 | 9.0591 | 1.9786 | 21.7817 | 22.0027 | 22.1939 | 22.2575 | 22.076 | 21.401 | 20.2109 | 22.1931 | 22.3698 | 22.4062 | 22.3536 | 21.9748 | 21.2076 | 22.2643 | 17.1813 | 17.2029 | 16.1345 | 16.1843 | 16.3139 | 17.1811 | 16.9662 | 22.3794 | 22.1329 | 21.7002 | 22.0698 | 21.7861 | 21.2928 | 21.9342 | 21.5169 | 20.8983 | 20.0852 | 20.2373 | 19.7979 | 19.5856 | -0.063686 | -0.021652 | 20.7544 | 22.0812 | 22.3794 | 20.1232 | 21.6668 | 22.1123 | 21.947 | 21.7107 | 21.2782 | 21.785 | 21.4525 | 21.0441 | 20.2749 | 20.3594 | 20.2586 | 20.1959 | 19.9145 |  | 20.2228 | 19.7765 | 20.1367 | 19.6286 | 20.0801 | 20.308 |  | 20.3914 |  |  | 20.2633 | 20.3811 | 20.5967 | [5 empty] | 21.9324 | 20.3244 | 21.6653 | 22.0387 | 19.5393 | 21.1576 | 21.7803 | 19.3435 | 19.8938 | 21.1145 |  | 19.7732 | 20.8799 | 18.874 | 19.7082 | 20.7913 | 19.3782 | 20.056 | 19.0854 | 20.0654 | 19.171 | 20.2098 | 18.8649 | 20.0695 | 21.0257 | 19.4097 | 19.7483 | 20.9531 | 18.9433 | 19.7912 | 20.7802 | 18.9244 | 20.0472 | 19.2954 | 19.9441 | 18.955 | 20.1 | -0.22811 | 20.9465 | 0.049157 | 0.01582 | -27.1301 | 3.0963 | -10.99 | -0.04 | 0.84781 | -0.61853 | -11.5269 | 0.91445 | 0.40082 | -16.7116 | 0.47807 | 0.42858 | 0.42953 | 0.43174 | 0.40283 | 0.49409 | 0.44458 | 0.4331
42838.4186 | -142 | 22.8915 | 22.8576 | 22.8508 | 22.7768 | 22.399 | 21.74 | 22.7151 | 21.7988 | 22.3642 | 22.3731 | 22.3543 | 22.0284 | 21.2402 | 22.2087 | 21.5877 | 21.7605 | 21.8815 | 21.0738 | 21.1714 | 21.389 | 20.4639 | 20.6079 | 20.9012 | 21.8709 | 21.6457 | 21.2701 | 20.2894 | 20.4231 | 20.3541 | 22.0717 | 21.6709 | 21.1855 | 21.9998 | 21.7424 | 21.3501 | 19.9212 | 20.5216 |  | 20.5067 | 20.0308 | 20.0627 | 18.9753 |  | 17.0688 | 17.0576 | 16.8378 | 17.0431 | 16.9704 | 17.4869 | 17.807 | 16.0462 | 16.9416 | 16.4306 | 17.0181 | 17.9778 | 40.5879 | 48.6899 | 40.2761 | 21.4094 |  |  | 0.43787 | -0.063805 | -93.7009 | 0.47571 | 0.17032 | -197.8184 | 0.17834 | -0.53262 | -0.15267 | 0.0007406 | 0.025984 | 8.829 | 9.0586 | 1.9787 | 21.7711 | 21.9997 | 22.1952 | 22.2626 | 22.0807 | 21.4035 | 20.2093 | 22.2005 | 22.3717 | 22.4052 | 22.3527 | 21.9791 | 21.2092 | 22.2654 | 17.2046 | 17.1937 | 16.1248 | 16.1811 | 16.3306 | 17.169 | 16.9682 | 22.3857 | 22.1444 | 21.7072 | 22.0867 | 21.8016 | 21.3031 | 21.9455 | 21.5295 | 20.9033 | 20.0993 | 20.2298 | 19.7937 | 19.575 | 0.12033 | -0.18218 | 20.7449 | 22.0752 | 22.3739 | 20.1193 | 21.6618 | 22.1151 | 21.9358 | 21.7047 | 21.2738 | 21.7789 | 21.4462 | 21.0414 | 20.2646 | 20.368 | 20.2546 | 20.1953 | 19.9259 |  | 20.2265 | 19.7461 | 20.1346 | 19.591 | 20.0833 | 20.3048 |  | 20.3855 |  |  | 20.2543 | 20.3651 | 20.5812 | [5 empty] | 21.9209 | 20.3211 | 21.6567 | 22.0353 | 19.5301 | 21.1487 | 21.7737 | 19.349 | 19.901 | 21.1187 |  | 19.7815 | 20.8834 | 18.8754 | 19.707 | 20.7965 | 19.3794 | 20.0677 | 19.1015 | 20.0728 | 19.1688 | 20.2105 | 18.8705 | 20.0781 | 21.0271 | 19.413 | 19.7561 | 20.9741 | 18.9486 | 19.7945 | 20.7865 | 18.9224 | 20.0536 | 19.2965 | 19.9521 | 18.964 | 20.1011 | -0.14371 | 20.9453 | 0.047756 | 0.014898 | -27.1113 | 3.0963 | 3.1 | -0.1 | 0.79004 | -0.29988 | -11.4919 | 0.81882 | 0.49032 | -16.71 | 0.50173 | 0.42839 | 0.4303 | 0.43289 | 0.39883 | 0.49539 | 0.44456 | 0.43387
42838.4186 | -141 | 22.9 | 22.8634 | 22.854 | 22.7741 | 22.4019 | 21.7508 | 22.7197 | 21.8113 | 22.3716 | 22.3806 | 22.3573 | 22.0324 | 21.2507 | 22.2205 | 21.5933 | 21.7671 | 21.8985 | 21.0787 | 21.1797 | 21.3894 | 20.4722 | 20.6185 | 20.909 | 21.8816 | 21.6479 | 21.2762 | 20.2975 | 20.4294 | 20.3689 | 22.0652 | 21.6658 | 21.1923 | 21.9981 | 21.739 | 21.3521 | 19.915 | 20.5145 |  | 20.4986 | 20.0291 | 20.0609 | 18.9687 |  | 17.0619 | 17.0463 | 16.8175 | 17.0126 | 16.9537 | 17.4754 | 17.8449 | 16.0468 | 16.9383 | 16.5939 | 17.0081 | 17.976 | 40.6728 | 48.9036 | 40.3581 | 21.408 |  |  | 0.35179 | 0.007819 | -93.7167 | 0.43365 | 0.35234 | -197.7921 | 0.45039 | -0.56548 | -0.31419 | 0.041442 | 0.048205 | 8.8287 | 9.0584 | 1.9786 | 21.7771 | 22.0049 | 22.1969 | 22.2571 | 22.0808 | 21.4035 | 20.2089 | 22.1962 | 22.3708 | 22.4019 | 22.3542 | 21.9849 | 21.2093 | 22.2666 | 17.2184 | 17.2106 | 16.1383 | 16.2058 | 16.3292 | 17.1722 | 16.9691 | 22.383 | 22.1397 | 21.7041 | 22.0777 | 21.7975 | 21.3041 | 21.948 | 21.5226 | 20.9035 | 20.0925 | 20.2182 | 19.7859 | 19.57 | -0.10831 | -0.14148 | 20.7377 | 22.0603 | 22.3739 | 20.1171 | 21.6692 | 22.1159 | 21.9431 | 21.709 | 21.2726 | 21.7633 | 21.4388 | 21.0374 | 20.2652 | 20.3574 | 20.2511 | 20.1927 | 19.9325 |  | 20.2192 | 19.7203 | 20.1375 | 19.5688 | 20.0835 | 20.3004 |  | 20.3867 |  |  | 20.2714 | 20.3691 | 20.5852 | [5 empty] | 21.9268 | 20.3193 | 21.662 | 22.0347 | 19.5393 | 21.1607 | 21.7776 | 19.3428 | 19.887 | 21.1107 |  | 19.7807 | 20.8741 | 18.8728 | 19.7077 | 20.79 | 19.3723 | 20.0605 | 19.091 | 20.0772 | 19.1648 | 20.2086 | 18.867 | 20.085 | 21.026 | 19.4139 | 19.7535 | 20.9669 | 18.9474 | 19.7944 | 20.7854 | 18.9208 | 20.0574 | 19.2993 | 19.9536 | 18.9714 | 20.1081 | -0.088616 | 20.9471 | 0.0463 | 0.013954 | -26.9973 | 3.0964 | 2.67 | -0.11 | 0.70815 | 0.10498 | -11.4927 | 0.78178 | 0.70521 | -16.7085 | 0.79731 | 0.42796 | 0.43111 | 0.43351 | 0.39768 | 0.494 | 0.44454 | 0.43378
42838.4187 | -140 | 22.9033 | 22.8663 | 22.8555 | 22.772 | 22.4023 | 21.7463 | 22.7195 | 21.8066 | 22.3678 | 22.3837 | 22.3559 | 22.0237 | 21.2449 | 22.2185 | 21.5941 | 21.7701 | 21.8985 | 21.0834 | 21.1855 | 21.4 | 20.4763 | 20.6204 | 20.9104 | 21.8853 | 21.6485 | 21.2713 | 20.2965 | 20.4327 | 20.3759 | 22.0686 | 21.6605 | 21.1933 | 21.9929 | 21.7387 | 21.3503 | 19.9136 | 20.519 |  | 20.4963 | 20.029 | 20.0608 | 18.9598 |  | 17.0507 | 17.0361 | 16.8073 | 17.0039 | 16.9505 | 17.4752 | 17.8716 | 16.0649 | 16.9387 | 16.709 | 17.0078 | 17.9768 | 40.7621 | 49.1004 | 40.4325 | 21.4109 |  |  | 0.61398 | -0.17486 | -93.7101 | 0.20892 | 0.17427 | -197.8696 | 0.66527 | -0.59242 | -0.059065 | 0.23089 | -0.10213 | 8.829 | 9.059 | 1.9783 | 21.7844 | 21.998 | 22.1933 | 22.2557 | 22.0819 | 21.3966 | 20.2184 | 22.1884 | 22.3656 | 22.3991 | 22.3552 | 21.9802 | 21.21 | 22.2712 | 17.2378 | 17.1973 | 16.1512 | 16.2191 | 16.3269 | 17.1693 | 16.9587 | 22.3763 | 22.1379 | 21.7051 | 22.076 | 21.796 | 21.3055 | 21.9509 | 21.5234 | 20.9022 | 20.0944 | 20.2115 | 19.7789 | 19.576 | -0.07214 | -0.049231 | 20.7399 | 22.0778 | 22.3779 | 20.1283 | 21.6746 | 22.1042 | 21.9464 | 21.7122 | 21.2745 | 21.7827 | 21.4484 | 21.0322 | 20.2667 | 20.3374 | 20.2541 | 20.1872 | 19.9489 |  | 20.2189 | 19.6749 | 20.1393 | 19.5749 | 20.0789 | 20.3075 |  | 20.3853 |  |  | 20.2721 | 20.3671 | 20.5917 | [5 empty] | 21.9352 | 20.3169 | 21.6613 | 22.0402 | 19.5347 | 21.1574 | 21.7761 | 19.3513 | 19.8927 | 21.1193 |  | 19.7892 | 20.8808 | 18.8647 | 19.7157 | 20.7921 | 19.3745 | 20.0652 | 19.095 | 20.0732 | 19.1643 | 20.214 | 18.8674 | 20.0863 | 21.0294 | 19.4223 | 19.7521 | 20.9682 | 18.9426 | 19.7949 | 20.7853 | 18.9257 | 20.0636 | 19.3014 | 19.9555 | 18.9755 | 20.1142 | -0.16319 | 20.9453 | 0.047172 | 0.014244 | -27.0225 | 3.0963 | 12.88 | -0.12 | 0.93555 | -0.49642 | -11.4921 | 0.54262 | 0.49596 | -16.7118 | 0.96902 | 0.42749 | 0.43244 | 0.43319 | 0.39519 | 0.49135 | 0.44474 | 0.43368
42838.4187 | -139 | 22.8978 | 22.855 | 22.8445 | 22.7686 | 22.398 | 21.7445 | 22.7197 | 21.7975 | 22.3618 | 22.3764 | 22.3524 | 22.0176 | 21.23 | 22.2119 | 21.587 | 21.7643 | 21.889 | 21.0752 | 21.1772 | 21.3883 | 20.4739 | 20.6137 | 20.9053 | 21.8757 | 21.6468 | 21.2767 | 20.2912 | 20.4258 | 20.3679 | 22.0659 | 21.6714 | 21.1901 | 21.9951 | 21.7342 | 21.3542 | 19.9187 | 20.5157 |  | 20.4995 | 20.0269 | 20.0568 | 18.9592 |  | 17.0353 | 17.024 | 16.7982 | 16.9955 | 16.9489 | 17.4889 | 17.9047 | 16.0752 | 16.9415 | 16.6966 | 17.0104 | 17.9763 | 40.8536 | 49.2928 | 40.5141 | 21.4086 |  |  | 0.56601 | -0.040149 | -93.3769 | 0.36925 | 0.29518 | -197.8401 | 0.39191 | -0.5714 | 0.099145 | 0.1625 | 0.0093184 | 8.8289 | 9.0589 | 1.9785 | 21.7705 | 21.998 | 22.192 | 22.2534 | 22.0793 | 21.39 | 20.2032 | 22.1944 | 22.3697 | 22.3987 | 22.3508 | 21.9755 | 21.2079 | 22.265 | 17.2616 | 17.1527 | 16.1652 | 16.206 | 16.3186 | 17.1637 | 16.9543 | 22.3846 | 22.1465 | 21.7108 | 22.09 | 21.7992 | 21.3032 | 21.9488 | 21.5314 | 20.9085 | 20.0901 | 20.1967 | 19.7823 | 19.5664 | -0.24377 | -0.19968 | 20.7361 | 22.0695 | 22.3698 | 20.1026 | 21.655 | 22.0999 | 21.9396 | 21.699 | 21.2652 | 21.7672 | 21.4341 | 21.0332 | 20.2563 | 20.3313 | 20.2504 | 20.1889 | 19.9628 |  | 20.221 | 19.6548 | 20.1351 | 19.6058 | 20.0764 | 20.302 |  | 20.3909 |  |  | 20.2708 | 20.3643 | 20.5858 | [5 empty] | 21.9252 | 20.316 | 21.6577 | 22.0367 | 19.5331 | 21.1549 | 21.7697 | 19.3405 | 19.8979 | 21.1134 |  | 19.7896 | 20.8791 | 18.8662 | 19.7088 | 20.7833 | 19.3651 | 20.0638 | 19.0875 | 20.0767 | 19.1644 | 20.207 | 18.8729 | 20.087 | 21.024 | 19.4211 | 19.75 | 20.9653 | 18.9434 | 19.7897 | 20.7829 | 18.9208 | 20.053 | 19.2928 | 19.9574 | 18.9734 | 20.1109 | 0.037338 | 20.9458 | 0.047639 | 0.015587 | -27.0402 | 3.0963 | 1.07 | -0.16 | 0.89824 | -0.23787 | -11.4714 | 0.72137 | 0.64548 | -16.7109 | 0.74376 | 0.42718 | 0.43285 | 0.43224 | 0.3919 | 0.48928 | 0.44493 | 0.4338
42838.4187 | -138 | 22.9002 | 22.8738 | 22.8529 | 22.7777 | 22.4058 | 21.747 | 22.7217 | 21.8107 | 22.3667 | 22.3782 | 22.3568 | 22.0228 | 21.2474 | 22.2132 | 21.59 | 21.7626 | 21.8963 | 21.0802 | 21.1805 | 21.3911 | 20.4748 | 20.6142 | 20.9092 | 21.8801 | 21.6496 | 21.2736 | 20.2946 | 20.4263 | 20.3741 | 22.0688 | 21.6708 | 21.1905 | 22.0084 | 21.7392 | 21.3641 | 19.9174 | 20.5127 |  | 20.5004 | 20.0316 | 20.0581 | 18.9568 |  | 17.0221 | 17.0119 | 16.7871 | 16.9809 | 16.9425 | 17.4991 | 17.9386 | 16.0689 | 16.9432 | 16.5692 | 17.0103 | 17.9817 | 40.9657 | 49.4944 | 40.622 | 21.4173 |  |  | 0.45693 | 0.031475 | -93.4709 | 0.33837 | 0.29912 | -197.8611 | 0.66527 | -0.45377 | 0.22349 | -0.12094 | -0.10387 | 8.8295 | 9.0593 | 1.9786 | 21.77 | 22.0038 | 22.1913 | 22.2564 | 22.0778 | 21.3991 | 20.2073 | 22.1987 | 22.3658 | 22.3937 | 22.3478 | 21.9751 | 21.2051 | 22.2557 | 17.2959 | 17.1165 | 16.1672 | 16.2094 | 16.3085 | 17.1726 | 16.969 | 22.3799 | 22.1439 | 21.7001 | 22.0767 | 21.7941 | 21.2983 | 21.9354 | 21.5211 | 20.8995 | 20.094 | 20.1937 | 19.7623 | 19.5774 | -0.063686 | -0.14775 | 20.7349 | 22.0778 | 22.3839 | 20.1277 | 21.6712 | 22.1116 | 21.9488 | 21.7162 | 21.2822 | 21.79 | 21.4528 | 21.0491 | 20.2716 | 20.3427 | 20.2603 | 20.2047 | 19.9634 |  | 20.2152 | 19.6429 | 20.1318 | 19.6053 | 20.0731 | 20.2945 |  | 20.3879 |  |  | 20.2794 | 20.3724 | 20.5847 | [5 empty] | 21.9217 | 20.3271 | 21.6626 | 22.0361 | 19.544 | 21.1592 | 21.7824 | 19.338 | 19.8844 | 21.1104 |  | 19.7846 | 20.8714 | 18.8548 | 19.7085 | 20.7825 | 19.3669 | 20.0568 | 19.0764 | 20.0741 | 19.1612 | 20.2026 | 18.8669 | 20.0831 | 21.0181 | 19.4171 | 19.7467 | 20.964 | 18.9339 | 19.7898 | 20.7753 | 18.9224 | 20.0478 | 19.2908 | 19.953 | 18.9741 | 20.1089 | -0.15595 | 20.9467 | 0.047823 | 0.015907 | -27.0454 | 3.0963 | -4.67 | -0.09 | 0.80707 | 0.21061 | -11.4769 | 0.69053 | 0.64979 | -16.7121 | 0.96906 | 0.42696 | 0.43307 | 0.43215 | 0.38912 | 0.49077 | 0.44495 | 0.43363
42838.4187 | -137 | 22.9028 | 22.8733 | 22.8569 | 22.7765 | 22.4127 | 21.7508 | 22.7251 | 21.8104 | 22.3668 | 22.3841 | 22.3546 | 22.0249 | 21.2471 | 22.2063 | 21.5886 | 21.7641 | 21.8959 | 21.0776 | 21.1823 | 21.3994 | 20.4758 | 20.6106 | 20.9069 | 21.8804 | 21.6467 | 21.276 | 20.299 | 20.421 | 20.3786 | 22.0768 | 21.6766 | 21.1952 | 22.0039 | 21.7383 | 21.3577 | 19.9245 | 20.5154 |  | 20.5057 | 20.0363 | 20.0631 | 18.9436 |  | 17.0207 | 16.9963 | 16.7758 | 16.9641 | 16.9343 | 17.4997 | 17.9467 | 16.053 | 16.9314 | 16.4204 | 17.0082 | 17.9822 | 41.0714 | 49.6768 | 40.7041 | 21.4078 |  |  | 0.55943 | -0.31154 | -92.8775 | 0.44679 | 0.57511 | -197.8138 | 0.66987 | -0.63316 | 0.097977 | -0.09262 | 0.037442 | 8.8298 | 9.0598 | 1.9784 | 21.7804 | 22.0063 | 22.1964 | 22.2601 | 22.0818 | 21.4025 | 20.2091 | 22.1969 | 22.3675 | 22.4039 | 22.3571 | 21.979 | 21.2124 | 22.267 | 17.3175 | 17.096 | 16.1906 | 16.2154 | 16.3121 | 17.168 | 16.9598 | 22.3801 | 22.1429 | 21.7053 | 22.087 | 21.7951 | 21.3014 | 21.9407 | 21.5218 | 20.9042 | 20.0846 | 20.1903 | 19.768 | 19.5925 | -0.057198 | -0.088222 | 20.7275 | 22.0825 | 22.3774 | 20.1202 | 21.6725 | 22.113 | 21.9492 | 21.7143 | 21.2812 | 21.7833 | 21.4486 | 21.0425 | 20.267 | 20.3315 | 20.2567 | 20.2049 | 19.9554 |  | 20.2143 | 19.6254 | 20.1339 | 19.6162 | 20.0745 | 20.2973 |  | 20.3919 |  |  | 20.2837 | 20.3692 | 20.5868 | [5 empty] | 21.9279 | 20.3235 | 21.666 | 22.0393 | 19.5412 | 21.1578 | 21.783 | 19.333 | 19.8791 | 21.1136 |  | 19.7818 | 20.869 | 18.8548 | 19.7012 | 20.7736 | 19.3597 | 20.0532 | 19.0782 | 20.0672 | 19.1606 | 20.201 | 18.8568 | 20.0825 | 21.0123 | 19.4187 | 19.745 | 20.9596 | 18.9273 | 19.7817 | 20.7768 | 18.929 | 20.0492 | 19.2878 | 19.9534 | 18.9762 | 20.1117 | -0.061718 | 20.946 | 0.048333 | 0.016509 | -27.0358 | 3.0963 | 2.52 | -0.09 | 0.89303 | -0.66257 | -11.4401 | 0.79347 | 0.901 | -16.7101 | 0.9724 | 0.42716 | 0.43363 | 0.4319 | 0.38618 | 0.4871 | 0.44555 | 0.43289
42838.4187 | -136 | 22.9018 | 22.8617 | 22.849 | 22.7734 | 22.3974 | 21.7395 | 22.7194 | 21.795 | 22.369 | 22.3754 | 22.3541 | 22.0217 | 21.2368 | 22.2077 | 21.5906 | 21.7645 | 21.8953 | 21.0798 | 21.1833 | 21.4002 | 20.4783 | 20.6106 | 20.9078 | 21.8833 | 21.6475 | 21.2758 | 20.2993 | 20.4178 | 20.3775 | 22.0735 | 21.6702 | 21.1929 | 22.0013 | 21.7437 | 21.361 | 19.917 | 20.5083 |  | 20.5041 | 20.0331 | 20.0685 | 18.9455 |  | 17.0118 | 16.9901 | 16.7664 | 16.9463 | 16.9158 | 17.4704 | 17.9707 | 16.0499 | 16.9291 | 16.2766 | 17.002 | 17.9833 | 41.1854 | 49.8686 | 40.8123 | 21.4071 |  |  | 0.28542 | -0.49422 | -92.3308 | 0.11495 | 0.32343 | -197.8098 | 1.116 | -0.52474 | -0.018199 | -0.025484 | -0.053525 | 8.8287 | 9.0586 | 1.9785 | 21.7879 | 22.0034 | 22.1979 | 22.2606 | 22.0909 | 21.4103 | 20.2155 | 22.1993 | 22.373 | 22.4112 | 22.3562 | 21.9823 | 21.2171 | 22.2737 | 17.3368 | 17.1169 | 16.2002 | 16.2169 | 16.3264 | 17.1672 | 16.9703 | 22.3837 | 22.1516 | 21.7073 | 22.089 | 21.8046 | 21.3079 | 21.9511 | 21.5291 | 20.9112 | 20.0914 | 20.192 | 19.77 | 19.5831 | -0.22568 | -0.028689 | 20.7298 | 22.0835 | 22.3843 | 20.1208 | 21.6707 | 22.1147 | 21.9494 | 21.7078 | 21.2839 | 21.7825 | 21.4453 | 21.0442 | 20.2713 | 20.3294 | 20.2642 | 20.2051 | 19.9474 |  | 20.2197 | 19.6091 | 20.1351 | 19.6287 | 20.0794 | 20.3033 |  | 20.3937 |  |  | 20.2815 | 20.3739 | 20.5882 | [5 empty] | 21.9278 | 20.3162 | 21.6637 | 22.0395 | 19.5392 | 21.1537 | 21.7751 | 19.33 | 19.8721 | 21.1092 |  | 19.7833 | 20.8684 | 18.852 | 19.704 | 20.7781 | 19.3552 | 20.0527 | 19.0814 | 20.0772 | 19.1539 | 20.1945 | 18.8522 | 20.0856 | 21.01 | 19.4218 | 19.7413 | 20.9597 | 18.9178 | 19.7793 | 20.7759 | 18.9289 | 20.0563 | 19.2829 | 19.9495 | 18.9731 | 20.1147 | -0.081196 | 20.9461 | 0.04759 | 0.015333 | -27.0469 | 3.0963 | -18.59 | -0.11 | 0.63787 | -0.83451 | -11.4063 | 0.40246 | 0.67565 | -16.7091 | 1.2551 | 0.42756 | 0.43412 | 0.43171 | 0.38394 | 0.48726 | 0.44525 | 0.43338
42838.4187 | -135 | 22.9061 | 22.8655 | 22.845 | 22.7792 | 22.407 | 21.7466 | 22.7189 | 21.804 | 22.3642 | 22.3747 | 22.3614 | 22.0248 | 21.2476 | 22.208 | 21.5919 | 21.763 | 21.8966 | 21.0821 | 21.1772 | 21.397 | 20.4719 | 20.6151 | 20.9059 | 21.8819 | 21.6508 | 21.2736 | 20.3016 | 20.4134 | 20.3751 | 22.0607 | 21.6655 | 21.1918 | 21.9987 | 21.7312 | 21.348 | 19.914 | 20.5022 |  | 20.5018 | 20.0318 | 20.0574 | 18.9433 |  | 17.0202 | 17 | 16.7713 | 16.9561 | 16.9367 | 17.4836 | 18.0017 | 16.0551 | 16.9333 | 16.225 | 17.0093 | 17.9809 | 41.3121 | 50.0488 | 40.9103 | 21.4102 |  |  | 0.4543 | -0.22743 | -91.9635 | 0.2996 | 0.468 | -197.844 | 1.4137 | -0.42814 | -0.12328 | -0.14717 | 0.11122 | 8.8291 | 9.0592 | 1.9785 | 21.7784 | 22.0012 | 22.1916 | 22.2559 | 22.0809 | 21.4027 | 20.2115 | 22.1984 | 22.3698 | 22.3971 | 22.3457 | 21.9809 | 21.2151 | 22.2676 | 17.3558 | 17.1187 | 16.1983 | 16.2278 | 16.33 | 17.165 | 16.9624 | 22.382 | 22.1453 | 21.7067 | 22.0821 | 21.8024 | 21.3059 | 21.9462 | 21.5326 | 20.9019 | 20.0882 | 20.1834 | 19.7598 | 19.5696 | -0.15176 | -0.0011102 | 20.7213 | 22.0741 | 22.3786 | 20.1106 | 21.6659 | 22.112 | 21.9404 | 21.7086 | 21.2769 | 21.7692 | 21.4405 | 21.0344 | 20.2623 | 20.3297 | 20.2492 | 20.2072 | 19.951 |  | 20.2315 | 19.6024 | 20.135 | 19.6298 | 20.0793 | 20.3117 |  | 20.3999 |  |  | 20.2849 | 20.3781 | 20.5978 | [5 empty] | 21.9267 | 20.3168 | 21.6593 | 22.0448 | 19.547 | 21.1545 | 21.7839 | 19.3247 | 19.8675 | 21.1031 |  | 19.7761 | 20.8636 | 18.8459 | 19.705 | 20.7755 | 19.3532 | 20.0427 | 19.0768 | 20.0758 | 19.1518 | 20.1871 | 18.8487 | 20.0754 | 21.0032 | 19.4157 | 19.7253 | 20.9489 | 18.9038 | 19.768 | 20.7588 | 18.9177 | 20.0483 | 19.2778 | 19.9458 | 18.9619 | 20.102 | -0.086205 | 20.9462 | 0.046484 | 0.013569 | -27.0928 | 3.0962 | -25.87 | -0.01 | 0.80475 | -0.56611 | -11.3838 | 0.64976 | 0.81276 | -16.711 | 1.4126 | 0.42785 | 0.43431 | 0.43168 | 0.38158 | 0.48656 | 0.44521 | 0.43365
42838.4187 | -134 | 22.8992 | 22.8637 | 22.8487 | 22.7833 | 22.4089 | 21.7428 | 22.7214 | 21.8059 | 22.3651 | 22.3764 | 22.3543 | 22.0279 | 21.2418 | 22.2071 | 21.5887 | 21.7648 | 21.8952 | 21.0846 | 21.1789 | 21.3926 | 20.4692 | 20.6164 | 20.9074 | 21.8836 | 21.647 | 21.2734 | 20.2972 | 20.4039 | 20.3791 | 22.0712 | 21.6675 | 21.1912 | 22.0005 | 21.7316 | 21.3516 | 19.9141 | 20.4954 |  | 20.5022 | 20.0378 | 20.0641 | 18.9562 |  | 17.0167 | 16.999 | 16.7784 | 16.9673 | 16.9648 | 17.5021 | 18.0213 | 16.0513 | 16.9373 | 16.1846 | 17.0161 | 17.9868 | 41.4351 | 50.2203 | 41.0287 | 21.4118 |  |  | 0.52527 | -0.34242 | -91.7322 | 0.66101 | 0.41017 | -197.8512 | 1.258 | -0.51422 | 0.0287 | -0.12304 | -0.078176 | 8.829 | 9.0592 | 1.9789 | 21.7731 | 22.0065 | 22.1999 | 22.2571 | 22.0814 | 21.4029 | 20.2156 | 22.1927 | 22.3693 | 22.4097 | 22.3607 | 21.9858 | 21.2165 | 22.2681 | 17.3773 | 17.1094 | 16.1874 | 16.2349 | 16.3338 | 17.1662 | 16.9565 | 22.3797 | 22.1427 | 21.6975 | 22.0795 | 21.7953 | 21.3024 | 21.9415 | 21.5262 | 20.9007 | 20.0855 | 20.1808 | 19.7486 | 19.5779 | -0.2192 | -0.16963 | 20.6969 | 22.0737 | 22.3783 | 20.1217 | 21.6577 | 22.1029 | 21.9369 | 21.7079 | 21.2774 | 21.7724 | 21.4373 | 21.0332 | 20.2611 | 20.3266 | 20.2478 | 20.1986 | 19.9419 |  | 20.2239 | 19.5941 | 20.1355 | 19.6368 | 20.0801 | 20.316 |  | 20.4006 |  |  | 20.2829 | 20.3756 | 20.6025 | [5 empty] | 21.9238 | 20.3093 | 21.6574 | 22.0472 | 19.5521 | 21.1585 | 21.781 | 19.3221 | 19.8599 | 21.101 |  | 19.7737 | 20.8635 | 18.8465 | 19.7013 | 20.7634 | 19.3479 | 20.0331 | 19.0746 | 20.0724 | 19.1462 | 20.1781 | 18.8446 | 20.0746 | 21.0035 | 19.4162 | 19.7296 | 20.9506 | 18.9042 | 19.7632 | 20.7604 | 18.9244 | 20.0458 | 19.2775 | 19.951 | 18.9605 | 20.1014 | -0.054298 | 20.947 | 0.047418 | 0.013881 | -27.0746 | 3.0962 | -23.49 | -0.12 | 0.86533 | -0.69464 | -11.3694 | 0.96512 | 0.76092 | -16.7118 | 1.3326 | 0.42785 | 0.43455 | 0.43151 | 0.37933 | 0.48708 | 0.44486 | 0.43332
42838.4187 | -133 | 22.895 | 22.8591 | 22.8451 | 22.7806 | 22.4018 | 21.7436 | 22.7121 | 21.7999 | 22.3695 | 22.3802 | 22.3507 | 22.0224 | 21.2346 | 22.2055 | 21.5973 | 21.7685 | 21.8981 | 21.0836 | 21.1801 | 21.3948 | 20.4811 | 20.6175 | 20.9179 | 21.8879 | 21.6465 | 21.2777 | 20.2979 | 20.401 | 20.3794 | 22.0747 | 21.6744 | 21.1911 | 22.0057 | 21.736 | 21.3552 | 19.9153 | 20.4872 |  | 20.5033 | 20.0402 | 20.0592 | 18.9584 |  | 17.0067 | 16.9878 | 16.7716 | 16.9644 | 16.9547 | 17.5121 | 18.0355 | 16.0508 | 16.9307 | 16.1384 | 17.0104 | 17.9924 | 41.5691 | 50.3811 | 41.1428 | 21.4186 |  |  | 0.49241 | -0.20969 | -91.4674 | 0.25426 | 0.31292 | -197.869 | 1.4071 | -0.54511 | -0.16434 | -0.21703 | -0.12036 | 8.8287 | 9.0585 | 1.9789 | 21.7827 | 22.0015 | 22.2014 | 22.2686 | 22.0854 | 21.4018 | 20.2214 | 22.1988 | 22.3734 | 22.4109 | 22.3599 | 21.9909 | 21.2193 | 22.272 | 17.4133 | 17.1299 | 16.2019 | 16.2426 | 16.347 | 17.1657 | 16.9581 | 22.3718 | 22.141 | 21.6974 | 22.0715 | 21.7922 | 21.299 | 21.9396 | 21.5206 | 20.8944 | 20.0829 | 20.1676 | 19.7392 | 19.5938 | -0.13171 | -0.073006 | 20.6884 | 22.0602 | 22.3648 | 20.1015 | 21.6564 | 22.0961 | 21.9324 | 21.7031 | 21.2654 | 21.7648 | 21.4302 | 21.0288 | 20.2511 | 20.3201 | 20.2489 | 20.1915 | 19.9438 |  | 20.2203 | 19.5735 | 20.1214 | 19.6362 | 20.0725 | 20.3002 |  | 20.3893 |  |  | 20.2746 | 20.3736 | 20.6007 | [5 empty] | 21.921 | 20.2988 | 21.6523 | 22.0359 | 19.5407 | 21.1507 | 21.7784 | 19.3187 | 19.8569 | 21.0951 |  | 19.7692 | 20.8571 | 18.8466 | 19.6956 | 20.752 | 19.3491 | 20.0256 | 19.0711 | 20.0718 | 19.1412 | 20.1718 | 18.8501 | 20.0774 | 21.0037 | 19.4173 | 19.7343 | 20.9481 | 18.9062 | 19.765 | 20.7603 | 18.9174 | 20.0461 | 19.2873 | 19.9548 | 18.9612 | 20.1015 | -0.13332 | 20.9472 | 0.048094 | 0.015304 | -27.0969 | 3.0962 | -27.16 | -0.11 | 0.83783 | -0.54357 | -11.3528 | 0.59856 | 0.66463 | -16.7128 | 1.4094 | 0.42768 | 0.43465 | 0.43127 | 0.37526 | 0.48565 | 0.44484 | 0.4328
42838.4187 | -132 | 22.8944 | 22.8605 | 22.8456 | 22.7752 | 22.4025 | 21.7389 | 22.7078 | 21.7968 | 22.3636 | 22.3743 | 22.3514 | 22.0209 | 21.2423 | 22.2039 | 21.5937 | 21.7763 | 21.9081 | 21.0787 | 21.1771 | 21.3967 | 20.4831 | 20.6259 | 20.9126 | 21.895 | 21.647 | 21.2827 | 20.301 | 20.3982 | 20.3755 | 22.0659 | 21.6614 | 21.1866 | 21.9971 | 21.7365 | 21.3481 | 19.9089 | 20.4852 |  | 20.4946 | 20.0394 | 20.0553 | 18.954 |  | 17.0059 | 16.9812 | 16.7633 | 16.959 | 16.9493 | 17.4988 | 18.0443 | 15.9923 | 16.933 | 16.1091 | 17.0036 | 17.9966 | 41.6874 | 50.5313 | 41.2645 | 21.4133 |  |  | 0.54892 | -0.50342 | -90.9167 | 0.13927 | 0.13287 | -197.8788 | 1.4899 | -0.55825 | -0.1118 | 0.10858 | 0.067127 | 8.8294 | 9.0594 | 1.9788 | 21.7772 | 21.9988 | 22.1894 | 22.2534 | 22.0726 | 21.3918 | 20.2117 | 22.1919 | 22.364 | 22.4006 | 22.3621 | 21.981 | 21.2084 | 22.2595 | 17.4348 | 17.1465 | 16.2131 | 16.2368 | 16.3592 | 17.1647 | 16.961 | 22.3692 | 22.142 | 21.6944 | 22.0655 | 21.7913 | 21.291 | 21.941 | 21.5209 | 20.8994 | 20.0785 | 20.1641 | 19.7348 | 19.61 | 0.0063034 | -0.1508 | 20.698 | 22.0746 | 22.3744 | 20.1099 | 21.6674 | 22.1137 | 21.9452 | 21.7131 | 21.2746 | 21.7778 | 21.4353 | 21.031 | 20.2635 | 20.3193 | 20.2575 | 20.2054 | 19.949 |  | 20.2225 | 19.5703 | 20.1325 | 19.6479 | 20.0708 | 20.3056 |  | 20.39 |  |  | 20.2655 | 20.3869 | 20.599 | [5 empty] | 21.9225 | 20.2968 | 21.6589 | 22.0364 | 19.5458 | 21.1575 | 21.7789 | 19.3221 | 19.8476 | 21.1019 |  | 19.7598 | 20.8615 | 18.8471 | 19.6937 | 20.7561 | 19.3541 | 20.0168 | 19.0725 | 20.0659 | 19.1465 | 20.1721 | 18.8479 | 20.0805 | 20.9946 | 19.4169 | 19.7283 | 20.9436 | 18.9025 | 19.7619 | 20.7571 | 18.9135 | 20.0452 | 19.2882 | 19.9496 | 18.9563 | 20.1038 | -0.069695 | 20.9477 | 0.049009 | 0.014767 | -27.0695 | 3.0962 | 2.93 | 0 | 0.8846 | -0.84222 | -11.3184 | 0.44298 | 0.43307 | -16.7129 | 1.4502 | 0.42761 | 0.43511 | 0.43089 | 0.37276 | 0.48475 | 0.44474 | 0.4322
42838.4188 | -131 | 22.8903 | 22.8633 | 22.8491 | 22.7821 | 22.4084 | 21.7413 | 22.7213 | 21.7995 | 22.3609 | 22.3862 | 22.3558 | 22.0253 | 21.246 | 22.2204 | 21.5941 | 21.7663 | 21.8969 | 21.0813 | 21.1819 | 21.3915 | 20.4817 | 20.6219 | 20.9024 | 21.8922 | 21.6505 | 21.2783 | 20.3004 | 20.4004 | 20.3783 | 22.0741 | 21.6641 | 21.1928 | 21.9972 | 21.7395 | 21.3557 | 19.9183 | 20.4739 |  | 20.4957 | 20.0434 | 20.0632 | 18.9544 |  | 17.0024 | 16.9818 | 16.7568 | 16.9575 | 16.9468 | 17.4926 | 18.0526 | 15.9731 | 16.9294 | 16.0903 | 17.0059 | 17.9948 | 41.8212 | 50.6717 | 41.378 | 21.4153 |  |  | 0.56272 | -0.51524 | -90.6013 | 0.54668 | 0.307 | -197.8716 | 1.7166 | -0.68968 | -0.13982 | -0.024226 | 0.023727 | 8.8288 | 9.0584 | 1.9787 | 21.7772 | 22.0029 | 22.189 | 22.2503 | 22.082 | 21.4 | 20.2084 | 22.1916 | 22.3653 | 22.4013 | 22.3587 | 21.978 | 21.206 | 22.269 | 17.4504 | 17.1998 | 16.2256 | 16.2314 | 16.3356 | 17.167 | 16.9564 | 22.3734 | 22.1438 | 21.6975 | 22.0788 | 21.7965 | 21.296 | 21.9433 | 21.525 | 20.9049 | 20.0774 | 20.1723 | 19.74 | 19.6341 | -0.010014 | -0.17077 | 20.7004 | 22.0727 | 22.3647 | 20.1229 | 21.6679 | 22.1089 | 21.9442 | 21.7069 | 21.2743 | 21.7798 | 21.4408 | 21.039 | 20.2682 | 20.32 | 20.2608 | 20.2092 | 19.947 |  | 20.2195 | 19.5708 | 20.1338 | 19.6691 | 20.0796 | 20.3015 |  | 20.4009 |  |  | 20.2654 | 20.3905 | 20.5947 | [5 empty] | 21.9246 | 20.289 | 21.6575 | 22.0383 | 19.5432 | 21.1542 | 21.7766 | 19.3269 | 19.8451 | 21.1015 |  | 19.7534 | 20.8657 | 18.8454 | 19.6892 | 20.7634 | 19.3487 | 20.023 | 19.0694 | 20.0685 | 19.1555 | 20.1624 | 18.8555 | 20.0798 | 20.9989 | 19.4234 | 19.7335 | 20.9566 | 18.9048 | 19.7622 | 20.761 | 18.9191 | 20.0547 | 19.2887 | 19.9675 | 18.9521 | 20.1115 | -0.1413 | 20.9475 | 0.049538 | 0.015486 | -27.044 | 3.0962 | -5.21 | -0.08 | 0.89565 | -0.85206 | -11.2988 | 0.87767 | 0.65829 | -16.7124 | 1.5566 | 0.42756 | 0.43514 | 0.4306 | 0.37129 | 0.48282 | 0.44505 | 0.43149
42838.4188 | -130 | 22.8929 | 22.8654 | 22.8456 | 22.7704 | 22.3991 | 21.7416 | 22.7149 | 21.7941 | 22.3638 | 22.3755 | 22.3497 | 22.0203 | 21.235 | 22.202 | 21.5977 | 21.7656 | 21.908 | 21.0849 | 21.1755 | 21.4004 | 20.4714 | 20.6206 | 20.9014 | 21.8986 | 21.6432 | 21.2764 | 20.3035 | 20.3879 | 20.3705 | 22.0685 | 21.6616 | 21.1905 | 21.9901 | 21.7263 | 21.3448 | 19.9104 | 20.4688 |  | 20.4959 | 20.0409 | 20.0567 | 18.9517 |  | 16.9994 | 16.9645 | 16.753 | 16.963 | 16.9343 | 17.5 | 18.0576 | 15.9905 | 16.9271 | 16.0619 | 17.0037 | 17.9948 | 41.9764 | 50.8035 | 41.4829 | 21.4159 |  |  | 0.4175 | -0.4929 | -90.849 | 0.17475 | 0.04876 | -197.8388 | 1.7784 | -0.77444 | -0.45021 | 0.071863 | 0.036747 | 8.8278 | 9.0576 | 1.9787 | 21.7827 | 22.0084 | 22.1971 | 22.2549 | 22.0902 | 21.4054 | 20.2127 | 22.195 | 22.3704 | 22.4061 | 22.3579 | 21.9892 | 21.2205 | 22.277 | 17.465 | 17.246 | 16.2433 | 16.2269 | 16.3358 | 17.1671 | 16.9578 | 22.379 | 22.1398 | 21.7044 | 22.0766 | 21.7975 | 21.2984 | 21.9378 | 21.5234 | 20.9001 | 20.0772 | 20.1696 | 19.7368 | 19.6538 | -0.065062 | -0.096971 | 20.7088 | 22.0841 | 22.3742 | 20.1279 | 21.6741 | 22.1105 | 21.9525 | 21.7133 | 21.2852 | 21.7792 | 21.4516 | 21.042 | 20.2733 | 20.3228 | 20.2686 | 20.214 | 19.9547 |  | 20.225 | 19.5767 | 20.136 | 19.6845 | 20.0852 | 20.3122 |  | 20.394 |  |  | 20.2596 | 20.3943 | 20.5914 | [5 empty] | 21.9222 | 20.2887 | 21.658 | 22.0376 | 19.5419 | 21.155 | 21.7704 | 19.3302 | 19.838 | 21.0965 |  | 19.7496 | 20.8562 | 18.8528 | 19.6844 | 20.7488 | 19.342 | 20.013 | 19.0621 | 20.0588 | 19.1519 | 20.1574 | 18.8559 | 20.0814 | 20.9949 | 19.429 | 19.7321 | 20.9513 | 18.905 | 19.7556 | 20.7602 | 18.9181 | 20.0609 | 19.2845 | 19.9578 | 18.9486 | 20.1158 | -0.027957 | 20.9482 | 0.049876 | 0.015899 | -27.0326 | 3.0962 | -14.27 | -0.06 | 0.77146 | -0.83336 | -11.3139 | 0.4962 | 0.26235 | -16.7112 | 1.5844 | 0.42753 | 0.43505 | 0.43036 | 0.36969 | 0.48102 | 0.44486 | 0.43094
42838.4188 | -129 | 22.8947 | 22.8666 | 22.8447 | 22.7728 | 22.3983 | 21.7446 | 22.7185 | 21.7946 | 22.3625 | 22.3714 | 22.3525 | 22.0162 | 21.236 | 22.2003 | 21.5843 | 21.7485 | 21.8895 | 21.0722 | 21.1739 | 21.3878 | 20.4754 | 20.6112 | 20.9001 | 21.8791 | 21.6457 | 21.2598 | 20.2932 | 20.3769 | 20.3535 | 22.0807 | 21.6811 | 21.198 | 22.0024 | 21.7422 | 21.3653 | 19.9279 | 20.4807 |  | 20.512 | 20.0447 | 20.0737 | 18.975 |  | 16.9866 | 16.9614 | 16.7481 | 16.956 | 16.9298 | 17.5091 | 18.0771 | 16.0108 | 16.9303 | 16.0634 | 17.0014 | 17.9836 | 42.1333 | 50.9186 | 41.5931 | 21.4149 |  |  | 0.40239 | -0.32994 | -91.2952 | 0.57493 | 0.21698 | -197.8486 | 1.5925 | -0.62725 | -0.02968 | -0.063668 | 0.040219 | 8.8291 | 9.0589 | 1.9786 | 21.7838 | 22.0116 | 22.1975 | 22.2631 | 22.0871 | 21.4048 | 20.2153 | 22.1975 | 22.373 | 22.409 | 22.3564 | 21.9913 | 21.214 | 22.2757 | 17.4871 | 17.2375 | 16.2522 | 16.2336 | 16.3344 | 17.1586 | 16.9503 | 22.3772 | 22.1429 | 21.7025 | 22.0777 | 21.7954 | 21.3043 | 21.9439 | 21.5285 | 20.9036 | 20.0818 | 20.1583 | 19.7304 | 19.6681 | -0.047565 | -0.068631 | 20.7089 | 22.0725 | 22.3764 | 20.1222 | 21.6682 | 22.1156 | 21.952 | 21.7158 | 21.2849 | 21.7798 | 21.4466 | 21.0484 | 20.2812 | 20.3023 | 20.2679 | 20.2152 | 19.9589 |  | 20.2184 | 19.5834 | 20.133 | 19.6791 | 20.0765 | 20.3052 |  | 20.3885 |  |  | 20.2732 | 20.3881 | 20.5926 | [5 empty] | 21.9262 | 20.2932 | 21.6607 | 22.0332 | 19.5454 | 21.1599 | 21.7675 | 19.3276 | 19.8329 | 21.0958 |  | 19.7383 | 20.858 | 18.8483 | 19.6776 | 20.7526 | 19.3508 | 20.0072 | 19.0692 | 20.0648 | 19.1537 | 20.155 | 18.8573 | 20.0894 | 21.0067 | 19.4238 | 19.7362 | 20.9537 | 18.9071 | 19.7496 | 20.7596 | 18.9312 | 20.059 | 19.2885 | 19.9642 | 18.9577 | 20.1197 | -0.030554 | 20.947 | 0.048407 | 0.014665 | -27.0624 | 3.0962 | -14.81 | 0.02 | 0.75735 | -0.68181 | -11.3416 | 0.90003 | 0.55344 | -16.7119 | 1.4993 | 0.42719 | 0.43476 | 0.43021 | 0.36624 | 0.47914 | 0.4448 | 0.4307
42838.4188 | -128 | 22.8933 | 22.8648 | 22.8521 | 22.7697 | 22.4002 | 21.7355 | 22.7084 | 21.7934 | 22.3633 | 22.3664 | 22.3491 | 22.0184 | 21.2324 | 22.2026 | 21.5985 | 21.7651 | 21.8964 | 21.0763 | 21.184 | 21.3921 | 20.4768 | 20.6164 | 20.9106 | 21.8888 | 21.6463 | 21.276 | 20.2829 | 20.3824 | 20.3416 | 22.0768 | 21.6711 | 21.2006 | 21.9986 | 21.741 | 21.3555 | 19.9172 | 20.4692 |  | 20.5038 | 20.0418 | 20.0693 | 18.9712 |  | 16.9925 | 16.9523 | 16.7434 | 16.9556 | 16.9365 | 17.5117 | 18.0992 | 16.0141 | 16.9242 | 16.1091 | 17.0051 | 17.9785 | 42.2901 | 51.0331 | 41.7043 | 21.4058 |  |  | 0.37479 | -0.38119 | -91.675 | 0.50265 | 0.21698 | -197.8388 | 1.7705 | -0.84081 | 0.11199 | -0.20172 | -0.079218 | 8.8293 | 9.0592 | 1.9787 | 21.782 | 22.0096 | 22.1924 | 22.2579 | 22.0817 | 21.4048 | 20.2201 | 22.2 | 22.3775 | 22.4073 | 22.3603 | 21.9819 | 21.2156 | 22.2669 | 17.5052 | 17.2292 | 16.2594 | 16.2449 | 16.334 | 17.1551 | 16.9505 | 22.3814 | 22.1527 | 21.702 | 22.0927 | 21.8047 | 21.31 | 21.9489 | 21.5293 | 20.9055 | 20.0781 | 20.1583 | 19.7373 | 19.6902 | -0.14528 | -0.080614 | 20.7037 | 22.0754 | 22.3759 | 20.1224 | 21.6658 | 22.1027 | 21.9363 | 21.7101 | 21.2742 | 21.7738 | 21.448 | 21.0357 | 20.278 | 20.3024 | 20.2726 | 20.2136 | 19.9707 |  | 20.2227 | 19.5977 | 20.1272 | 19.6765 | 20.0755 | 20.3001 |  | 20.3935 |  |  | 20.2657 | 20.367 | 20.6022 | [5 empty] | 21.9132 | 20.2875 | 21.6559 | 22.0385 | 19.5333 | 21.1502 | 21.7716 | 19.3269 | 19.8315 | 21.0858 |  | 19.7304 | 20.8445 | 18.8408 | 19.6688 | 20.7393 | 19.3364 | 20.0019 | 19.0569 | 20.0564 | 19.1511 | 20.1308 | 18.8535 | 20.0761 | 20.9858 | 19.4216 | 19.7308 | 20.9459 | 18.8908 | 19.7453 | 20.7504 | 18.9165 | 20.0539 | 19.2881 | 19.9554 | 18.9512 | 20.1076 | -0.19379 | 20.9474 | 0.047332 | 0.012814 | -27.1231 | 3.0963 | -25.96 | -0.12 | 0.7309 | -0.73285 | -11.365 | 0.84154 | 0.55344 | -16.7115 | 1.5809 | 0.42701 | 0.43417 | 0.43025 | 0.36382 | 0.47837 | 0.44454 | 0.42996
42838.4188 | -127 | 22.8919 | 22.8619 | 22.8427 | 22.7659 | 22.3994 | 21.731 | 22.7088 | 21.8022 | 22.3602 | 22.37 | 22.3482 | 22.0263 | 21.2354 | 22.2116 | 21.5933 | 21.7631 | 21.8956 | 21.0823 | 21.1835 | 21.3925 | 20.4788 | 20.6196 | 20.9057 | 21.8874 | 21.6445 | 21.2691 | 20.2862 | 20.3779 | 20.3388 | 22.0745 | 21.6745 | 21.1971 | 22 | 21.7326 | 21.3526 | 19.9157 | 20.46 |  | 20.5067 | 20.0471 | 20.0671 | 18.9752 |  | 16.9773 | 16.9423 | 16.7364 | 16.9541 | 16.9225 | 17.5083 | 18.1119 | 16.0099 | 16.9233 | 16.1227 | 16.9968 | 17.992 | 42.4803 | 51.1623 | 41.8433 | 21.4213 |  |  | 0.26373 | -0.33191 | -91.7486 | 0.39225 | 0.29518 | -197.8125 | 1.6496 | -0.74816 | -0.27196 | 0.070394 | -0.22331 | 8.8289 | 9.0587 | 1.9783 | 21.7763 | 21.9987 | 22.1914 | 22.2521 | 22.0834 | 21.3942 | 20.2107 | 22.1991 | 22.3684 | 22.4109 | 22.3517 | 21.9807 | 21.2113 | 22.2686 | 17.5372 | 17.2387 | 16.2599 | 16.2631 | 16.3489 | 17.1613 | 16.9515 | 22.377 | 22.1433 | 21.7017 | 22.0787 | 21.7953 | 21.301 | 21.9428 | 21.5234 | 20.8974 | 20.0786 | 20.1545 | 19.7336 | 19.6919 | -0.16336 | -0.047329 | 20.7063 | 22.0835 | 22.3785 | 20.1247 | 21.6628 | 22.105 | 21.9381 | 21.7077 | 21.273 | 21.7711 | 21.4416 | 21.0362 | 20.2837 | 20.3004 | 20.2675 | 20.2188 | 19.9938 |  | 20.2159 | 19.6126 | 20.1281 | 19.6544 | 20.0647 | 20.2983 |  | 20.3853 |  |  | 20.2738 | 20.3656 | 20.6001 | [5 empty] | 21.9171 | 20.2825 | 21.6577 | 22.0328 | 19.5321 | 21.1552 | 21.7676 | 19.3205 | 19.8354 | 21.0931 |  | 19.7269 | 20.8509 | 18.8442 | 19.6674 | 20.738 | 19.3401 | 20.0122 | 19.0615 | 20.0531 | 19.1468 | 20.1348 | 18.8361 | 20.069 | 20.9859 | 19.4184 | 19.7269 | 20.942 | 18.8948 | 19.7461 | 20.7484 | 18.9109 | 20.059 | 19.2935 | 19.9416 | 18.9487 | 20.103 | -0.18897 | 20.9462 | 0.047221 | 0.013213 | -27.0826 | 3.0963 | -29.09 | -0.14 | 0.61312 | -0.68382 | -11.3693 | 0.74339 | 0.6455 | -16.7103 | 1.526 | 0.42614 | 0.43379 | 0.4305 | 0.36099 | 0.47844 | 0.44438 | 0.42993
42838.4188 | -126 | 22.8999 | 22.8628 | 22.8504 | 22.7774 | 22.4074 | 21.7408 | 22.7155 | 21.8076 | 22.3624 | 22.3801 | 22.3559 | 22.0259 | 21.244 | 22.2181 | 21.5997 | 21.7657 | 21.9018 | 21.0849 | 21.1804 | 21.4064 | 20.478 | 20.6201 | 20.91 | 21.8865 | 21.6528 | 21.2753 | 20.2899 | 20.3862 | 20.3137 | 22.0699 | 21.6698 | 21.1927 | 21.9949 | 21.7338 | 21.3502 | 19.9087 | 20.4583 |  | 20.501 | 20.0426 | 20.0629 | 18.9852 |  | 16.9814 | 16.946 | 16.7341 | 16.9564 | 16.9378 | 17.515 | 18.1456 | 16.0682 | 16.9232 | 16.1302 | 16.9968 | 17.9896 | 42.671 | 51.2651 | 41.9837 | 21.4093 |  |  | 0.50752 | -0.24517 | -92.4261 | 0.43957 | 0.064528 | -197.8361 | 1.5649 | -0.72647 | -0.23168 | -0.04017 | -0.04606 | 8.829 | 9.0589 | 1.9785 | 21.7808 | 21.9959 | 22.1925 | 22.2551 | 22.0835 | 21.4 | 20.2141 | 22.2023 | 22.3687 | 22.4001 | 22.3566 | 21.9724 | 21.2158 | 22.2647 | 17.5527 | 17.235 | 16.2474 | 16.2692 | 16.3409 | 17.1551 | 16.9412 | 22.3855 | 22.147 | 21.7066 | 22.078 | 21.802 | 21.3008 | 21.9482 | 21.5284 | 20.9039 | 20.0837 | 20.1555 | 19.7352 | 19.7119 | -0.19914 | 0.01848 | 20.708 | 22.0775 | 22.3751 | 20.1246 | 21.6709 | 22.1054 | 21.9484 | 21.7155 | 21.2787 | 21.7819 | 21.4427 | 21.0398 | 20.2962 | 20.3127 | 20.2761 | 20.2273 | 20.0019 |  | 20.2152 | 19.6239 | 20.1238 | 19.6423 | 20.0633 | 20.3006 |  | 20.3883 |  |  | 20.2806 | 20.3716 | 20.6066 | [5 empty] | 21.9212 | 20.2872 | 21.6664 | 22.0438 | 19.533 | 21.1534 | 21.7717 | 19.3162 | 19.8242 | 21.0906 |  | 19.7198 | 20.8465 | 18.8483 | 19.6613 | 20.7384 | 19.3381 | 20.0063 | 19.0677 | 20.0499 | 19.144 | 20.1174 | 18.8245 | 20.0783 | 20.9987 | 19.424 | 19.7294 | 20.951 | 18.8958 | 19.753 | 20.7576 | 18.917 | 20.0662 | 19.2933 | 19.9498 | 18.9608 | 20.1143 | -0.042798 | 20.946 | 0.047571 | 0.01309 | -27.113 | 3.0962 | 0.14 | -0.08 | 0.85049 | -0.58772 | -11.4113 | 0.78695 | 0.30181 | -16.7115 | 1.4863 | 0.42589 | 0.43333 | 0.4308 | 0.35853 | 0.47863 | 0.44387 | 0.42955
42838.4188 | -125 | 22.9064 | 22.8696 | 22.856 | 22.7848 | 22.4084 | 21.7505 | 22.719 | 21.8038 | 22.3693 | 22.3813 | 22.3512 | 22.0245 | 21.2438 | 22.2178 | 21.6014 | 21.7656 | 21.9039 | 21.091 | 21.1828 | 21.3987 | 20.4819 | 20.618 | 20.9145 | 21.8898 | 21.6527 | 21.2834 | 20.2839 | 20.3808 | 20.3043 | 22.078 | 21.6768 | 21.1955 | 22.0001 | 21.7427 | 21.3527 | 19.9196 | 20.4706 |  | 20.5052 | 20.046 | 20.0624 | 18.9853 |  | 16.978 | 16.9487 | 16.7281 | 16.9592 | 16.9475 | 17.5273 | 18.1677 | 16.097 | 16.9237 | 16.1129 | 16.9985 | 17.9961 | 42.8687 | 51.3675 | 42.1388 | 21.4167 |  |  | 0.43261 | -0.17486 | -92.6068 | 0.20826 | 0.18478 | -197.8683 | 1.2619 | -0.6923 | -0.25795 | -0.064297 | -0.063246 | 8.8289 | 9.0589 | 1.9783 | 21.7843 | 22.0016 | 22.193 | 22.2648 | 22.0907 | 21.3983 | 20.2113 | 22.1968 | 22.3757 | 22.4084 | 22.3631 | 21.9871 | 21.2162 | 22.2682 | 17.5896 | 17.2415 | 16.2604 | 16.2782 | 16.3397 | 17.1558 | 16.9487 | 22.3873 | 22.1471 | 21.7075 | 22.0884 | 21.8018 | 21.3031 | 21.949 | 21.5273 | 20.9107 | 20.0807 | 20.1522 | 19.7371 | 19.7174 | -0.15373 | 0.13564 | 20.7167 | 22.0798 | 22.3664 | 20.1201 | 21.6697 | 22.112 | 21.9495 | 21.7062 | 21.2783 | 21.7792 | 21.4392 | 21.0409 | 20.3 | 20.2974 | 20.2737 | 20.2259 | 20.0192 |  | 20.2203 | 19.6532 | 20.1311 | 19.6522 | 20.0741 | 20.3017 |  | 20.3951 |  |  | 20.2856 | 20.3667 | 20.6009 | [5 empty] | 21.9249 | 20.2968 | 21.6619 | 22.0456 | 19.5378 | 21.1463 | 21.7712 | 19.3241 | 19.8227 | 21.0902 |  | 19.718 | 20.8454 | 18.8496 | 19.6572 | 20.738 | 19.3363 | 20.0066 | 19.064 | 20.0472 | 19.1461 | 20.1158 | 18.8174 | 20.0823 | 20.9918 | 19.4285 | 19.7314 | 20.9481 | 18.8914 | 19.7534 | 20.752 | 18.912 | 20.0657 | 19.3041 | 19.9473 | 18.9644 | 20.1199 | -0.24221 | 20.9479 | 0.04826 | 0.012974 | -27.0939 | 3.0961 | -6.99 | -0.18 | 0.78521 | -0.49634 | -11.4225 | 0.54168 | 0.51074 | -16.7132 | 1.3347 | 0.42558 | 0.43276 | 0.43088 | 0.35452 | 0.47805 | 0.44423 | 0.42929
42838.4188 | -124 | 22.8964 | 22.864 | 22.8559 | 22.7895 | 22.4022 | 21.7501 | 22.7222 | 21.7972 | 22.3696 | 22.3766 | 22.3509 | 22.025 | 21.24 | 22.2116 | 21.5958 | 21.7684 | 21.8958 | 21.0815 | 21.1793 | 21.3952 | 20.4746 | 20.6154 | 20.9113 | 21.8839 | 21.6439 | 21.2725 | 20.2713 | 20.3742 | 20.2872 | 22.0738 | 21.6724 | 21.1978 | 22.0035 | 21.7387 | 21.3521 | 19.9217 | 20.4719 |  | 20.5041 | 20.0505 | 20.0677 | 18.9797 |  | 16.9768 | 16.9365 | 16.7289 | 16.9533 | 16.9478 | 17.5288 | 18.1792 | 16.1036 | 16.9235 | 16.1013 | 16.995 | 18.0037 | 43.0545 | 51.4596 | 42.2789 | 21.422 |  |  | 0.32747 | -0.27277 | -92.4774 | 0.3502 | 0.41674 | -197.8335 | 1.6799 | -0.63382 | -0.19626 | -0.15136 | -0.099355 | 8.8285 | 9.058 | 1.9786 | 21.782 | 22.0069 | 22.1955 | 22.2631 | 22.0843 | 21.3894 | 20.2118 | 22.197 | 22.3764 | 22.4039 | 22.3549 | 21.9908 | 21.2138 | 22.2675 | 17.6143 | 17.2549 | 16.3047 | 16.2792 | 16.3366 | 17.1713 | 16.9576 | 22.3698 | 22.1374 | 21.6941 | 22.0753 | 21.7997 | 21.2953 | 21.9378 | 21.5239 | 20.9058 | 20.0764 | 20.1464 | 19.7271 | 19.7229 | -0.23021 | -0.087461 | 20.7026 | 22.0738 | 22.3705 | 20.1135 | 21.6577 | 22.1078 | 21.9352 | 21.7052 | 21.2742 | 21.7791 | 21.437 | 21.0344 | 20.292 | 20.2987 | 20.2652 | 20.222 | 20.0267 |  | 20.221 | 19.6755 | 20.1297 | 19.6569 | 20.0763 | 20.3065 |  | 20.3933 |  |  | 20.2821 | 20.3505 | 20.6018 | [5 empty] | 21.9161 | 20.2997 | 21.6513 | 22.0249 | 19.536 | 21.1457 | 21.7656 | 19.322 | 19.8262 | 21.096 |  | 19.7248 | 20.8517 | 18.8476 | 19.6637 | 20.7464 | 19.3357 | 20.0078 | 19.0737 | 20.0509 | 19.1493 | 20.1124 | 18.7928 | 20.077 | 20.9846 | 19.4223 | 19.7222 | 20.9419 | 18.882 | 19.7451 | 20.7458 | 18.8975 | 20.0505 | 19.3019 | 19.9369 | 18.9562 | 20.1067 | -0.026845 | 20.9478 | 0.047713 | 0.014172 | -27.122 | 3.0961 | -3.45 | -0.09 | 0.68315 | -0.61991 | -11.4143 | 0.7024 | 0.76702 | -16.7118 | 1.54 | 0.4254 | 0.43209 | 0.43083 | 0.35358 | 0.47418 | 0.44446 | 0.429
42838.4189 | -123 | 22.9012 | 22.8653 | 22.8525 | 22.7819 | 22.4024 | 21.7312 | 22.7167 | 21.8056 | 22.3643 | 22.378 | 22.3587 | 22.0208 | 21.2304 | 22.2149 | 21.5935 | 21.7653 | 21.8951 | 21.0759 | 21.1816 | 21.393 | 20.4758 | 20.6098 | 20.9052 | 21.8815 | 21.6442 | 21.2726 | 20.2707 | 20.3748 | 20.268 | 22.074 | 21.672 | 21.1979 | 21.9962 | 21.7325 | 21.3557 | 19.9182 | 20.4743 |  | 20.498 | 20.0486 | 20.0667 | 18.979 |  | 16.9666 | 16.9339 | 16.7204 | 16.9478 | 16.9502 | 17.5285 | 18.2003 | 16.1192 | 16.9257 | 16.1144 | 16.9977 | 17.9999 | 43.2356 | 51.5308 | 42.4165 | 21.4203 |  |  | 0.4313 | -0.14397 | -92.0148 | 0.6781 | 0.37929 | -197.8309 | 1.4991 | -0.53657 | 0.13184 | 0.03326 | 0.054628 | 8.828 | 9.0579 | 1.9787 | 21.7829 | 22.0034 | 22.1987 | 22.2607 | 22.0889 | 21.3995 | 20.2122 | 22.2004 | 22.3766 | 22.4083 | 22.3576 | 21.9876 | 21.2173 | 22.2706 | 17.6408 | 17.2494 | 16.3405 | 16.286 | 16.333 | 17.1656 | 16.9567 | 22.3712 | 22.1386 | 21.6949 | 22.0804 | 21.7992 | 21.2977 | 21.9351 | 21.5241 | 20.8982 | 20.0749 | 20.1415 | 19.7305 | 19.7326 | -0.25793 | 0.0015526 | 20.7083 | 22.0719 | 22.3679 | 20.1231 | 21.6605 | 22.1173 | 21.9449 | 21.7144 | 21.2728 | 21.778 | 21.4461 | 21.0345 | 20.2935 | 20.3051 | 20.2689 | 20.2358 | 20.024 |  | 20.2193 | 19.7023 | 20.1281 | 19.6358 | 20.0716 | 20.3031 |  | 20.395 |  |  | 20.276 | 20.3528 | 20.6009 | [5 empty] | 21.9126 | 20.2983 | 21.6506 | 22.0298 | 19.5303 | 21.1527 | 21.7707 | 19.3209 | 19.8326 | 21.0981 |  | 19.7211 | 20.8468 | 18.8515 | 19.6614 | 20.7453 | 19.3406 | 20.0191 | 19.076 | 20.0509 | 19.1529 | 20.1148 | 18.7913 | 20.0795 | 20.9868 | 19.4274 | 19.7216 | 20.9494 | 18.8821 | 19.7442 | 20.7489 | 18.9027 | 20.0642 | 19.2972 | 19.9359 | 18.963 | 20.112 | -0.15781 | 20.9465 | 0.047805 | 0.014186 | -27.0107 | 3.0961 | -2.32 | 0 | 0.78397 | -0.45037 | -11.3856 | 0.97741 | 0.73174 | -16.7117 | 1.4548 | 0.42542 | 0.4313 | 0.43125 | 0.34998 | 0.47008 | 0.44436 | 0.42867
42838.4189 | -122 | 22.8976 | 22.8665 | 22.8546 | 22.7804 | 22.4102 | 21.7434 | 22.7187 | 21.8069 | 22.3715 | 22.3781 | 22.3522 | 22.0189 | 21.2313 | 22.2101 | 21.5944 | 21.7614 | 21.8894 | 21.0721 | 21.1766 | 21.3845 | 20.4682 | 20.6084 | 20.9032 | 21.8787 | 21.638 | 21.2669 | 20.2581 | 20.3711 | 20.2442 | 22.0676 | 21.6645 | 21.1918 | 21.9968 | 21.729 | 21.3524 | 19.9154 | 20.4749 |  | 20.4914 | 20.0361 | 20.0532 | 18.9608 |  | 16.9602 | 16.9291 | 16.7161 | 16.9383 | 16.9435 | 17.5341 | 18.213 | 16.1 | 16.9239 | 16.1448 | 16.9931 | 17.9944 | 43.4077 | 51.5957 | 42.5935 | 21.4179 |  |  | 0.63895 | -0.48765 | -91.9766 | 0.63079 | 0.39046 | -197.8243 | 1.7344 | -0.7291 | -0.093704 | 0.13606 | -0.18511 | 8.8293 | 9.0592 | 1.9787 | 21.7831 | 22.0083 | 22.1988 | 22.2581 | 22.091 | 21.4045 | 20.2158 | 22.2026 | 22.3743 | 22.4043 | 22.3662 | 21.9874 | 21.2262 | 22.2752 | 17.676 | 17.218 | 16.3931 | 16.288 | 16.3251 | 17.1569 | 16.9517 | 22.3722 | 22.1396 | 21.7028 | 22.0858 | 21.7999 | 21.305 | 21.9421 | 21.5253 | 20.9031 | 20.0778 | 20.1439 | 19.7276 | 19.7414 | -0.21468 | 0.055379 | 20.6998 | 22.0619 | 22.3681 | 20.1122 | 21.655 | 22.1031 | 21.9381 | 21.6954 | 21.2723 | 21.7705 | 21.4392 | 21.0335 | 20.2907 | 20.2922 | 20.2636 | 20.2224 | 20.0262 |  | 20.2183 | 19.7216 | 20.1263 | 19.63 | 20.0713 | 20.3036 |  | 20.392 |  |  | 20.2876 | 20.3666 | 20.6027 | [5 empty] | 21.9212 | 20.3067 | 21.6523 | 22.035 | 19.538 | 21.1539 | 21.7711 | 19.3314 | 19.8373 | 21.0995 |  | 19.7284 | 20.8483 | 18.8565 | 19.6669 | 20.749 | 19.3482 | 20.0197 | 19.0665 | 20.0556 | 19.1612 | 20.1076 | 18.7846 | 20.0877 | 20.9893 | 19.4286 | 19.7227 | 20.9506 | 18.8875 | 19.7499 | 20.7542 | 18.9042 | 20.0687 | 19.2989 | 19.9372 | 18.9651 | 20.1022 | -0.21587 | 20.9472 | 0.048235 | 0.013743 | -27.0863 | 3.0961 | -15.4 | -0.13 | 0.95417 | -0.82885 | -11.3832 | 0.94268 | 0.74245 | -16.7116 | 1.5648 | 0.42532 | 0.4307 | 0.43141 | 0.34506 | 0.46366 | 0.44477 | 0.42853
42838.4189 | -121 | 22.8918 | 22.8621 | 22.8568 | 22.7786 | 22.4038 | 21.741 | 22.7163 | 21.7962 | 22.3675 | 22.3863 | 22.358 | 22.0227 | 21.231 | 22.1985 | 21.6009 | 21.764 | 21.8866 | 21.0841 | 21.1775 | 21.3924 | 20.4688 | 20.6151 | 20.9082 | 21.8815 | 21.638 | 21.2719 | 20.2526 | 20.3781 | 20.2374 | 22.072 | 21.6731 | 21.1904 | 21.9986 | 21.7373 | 21.3534 | 19.9208 | 20.469 |  | 20.5021 | 20.0445 | 20.0685 | 18.9671 |  | 16.971 | 16.9345 | 16.7159 | 16.9376 | 16.9487 | 17.536 | 18.2257 | 16.1372 | 16.9188 | 16.1721 | 16.9877 | 17.9997 | 43.5817 | 51.6626 | 42.7713 | 21.4158 |  |  | 0.38924 | -0.35228 | -91.2991 | 0.82924 | 0.4542 | -197.8289 | 1.9578 | -0.63908 | -0.30154 | -0.034506 | 0.00602 | 8.8289 | 9.0588 | 1.9788 | 21.783 | 22.0066 | 22.1966 | 22.2627 | 22.0896 | 21.4069 | 20.2134 | 22.1992 | 22.3756 | 22.4099 | 22.3678 | 21.9929 | 21.2268 | 22.2788 | 17.7165 | 17.1826 | 16.4393 | 16.292 | 16.3234 | 17.1469 | 16.9464 | 22.3836 | 22.1402 | 21.6997 | 22.083 | 21.7949 | 21.2966 | 21.9434 | 21.5315 | 20.8987 | 20.0766 | 20.1489 | 19.7268 | 19.7406 | -0.18813 | -0.16335 | 20.715 | 22.0631 | 22.374 | 20.1074 | 21.6574 | 22.0989 | 21.9322 | 21.6962 | 21.2646 | 21.7709 | 21.4389 | 21.0333 | 20.2905 | 20.2973 | 20.2621 | 20.2181 | 20.0373 |  | 20.2152 | 19.7391 | 20.1329 | 19.6261 | 20.0792 | 20.3079 |  | 20.4017 |  |  | 20.2933 | 20.3692 | 20.6109 | [5 empty] | 21.9241 | 20.3147 | 21.653 | 22.0356 | 19.5439 | 21.1504 | 21.7706 | 19.3391 | 19.8463 | 21.097 |  | 19.7348 | 20.8578 | 18.8602 | 19.6713 | 20.763 | 19.352 | 20.0195 | 19.07 | 20.0607 | 19.165 | 20.1109 | 18.7768 | 20.0937 | 20.9856 | 19.4289 | 19.7224 | 20.9515 | 18.8926 | 19.7555 | 20.7591 | 18.9015 | 20.0645 | 19.2999 | 19.9346 | 18.966 | 20.0887 | -0.27282 | 20.9469 | 0.048315 | 0.012988 | -27.0328 | 3.096 | -28.56 | -0.2 | 0.74473 | -0.70449 | -11.3413 | 1.0809 | 0.80076 | -16.7118 | 1.6625 | 0.42491 | 0.43044 | 0.43178 | 0.33938 | 0.4579 | 0.44478 | 0.42851
42838.4189 | -120 | 22.8937 | 22.8656 | 22.8572 | 22.7746 | 22.3969 | 21.7407 | 22.7151 | 21.7992 | 22.3701 | 22.3806 | 22.355 | 22.023 | 21.2357 | 22.2017 | 21.6065 | 21.7727 | 21.9 | 21.0898 | 21.1811 | 21.4068 | 20.4844 | 20.6177 | 20.9113 | 21.8901 | 21.646 | 21.2783 | 20.2639 | 20.383 | 20.2366 | 22.0718 | 21.6735 | 21.1833 | 21.9977 | 21.7349 | 21.3503 | 19.9177 | 20.477 |  | 20.4999 | 20.0485 | 20.0693 | 18.9656 |  | 16.9711 | 16.9337 | 16.7166 | 16.9374 | 16.9738 | 17.5435 | 18.2411 | 16.1833 | 16.9189 | 16.1918 | 16.9892 | 17.9983 | 43.7349 | 51.7006 | 42.9396 | 21.4051 |  |  | 0.47401 | -0.19786 | -91.1638 | 0.60779 | 0.34643 | -197.8585 | 1.7764 | -0.63251 | -0.22136 | 0.071863 | 0.025463 | 8.8286 | 9.0582 | 1.9786 | 21.7759 | 21.9945 | 22.1912 | 22.2563 | 22.0848 | 21.3972 | 20.2077 | 22.1964 | 22.3675 | 22.4052 | 22.3521 | 21.9739 | 21.2101 | 22.2638 | 17.7702 | 17.2231 | 16.4424 | 16.3266 | 16.3299 | 17.1607 | 16.9517 | 22.3673 | 22.136 | 21.6955 | 22.0828 | 21.7862 | 21.2938 | 21.9419 | 21.5261 | 20.9003 | 20.0769 | 20.1532 | 19.7311 | 19.7397 | -0.19639 | -0.0054848 | 20.7173 | 22.0665 | 22.3756 | 20.108 | 21.6611 | 22.1055 | 21.9349 | 21.7011 | 21.271 | 21.7714 | 21.44 | 21.0339 | 20.2871 | 20.3028 | 20.2719 | 20.2359 | 20.0203 |  | 20.2094 | 19.7511 | 20.1142 | 19.6011 | 20.0731 | 20.3079 |  | 20.3811 |  |  | 20.2946 | 20.3704 | 20.6145 | [5 empty] | 21.9127 | 20.315 | 21.6544 | 22.0364 | 19.5445 | 21.1541 | 21.7718 | 19.3376 | 19.859 | 21.0993 |  | 19.7369 | 20.8578 | 18.8652 | 19.6786 | 20.7635 | 19.3578 | 20.0293 | 19.0783 | 20.066 | 19.1716 | 20.1125 | 18.778 | 20.1035 | 20.9879 | 19.4292 | 19.7217 | 20.9526 | 18.8931 | 19.7626 | 20.7639 | 18.9009 | 20.0705 | 19.2977 | 19.9306 | 18.9685 | 20.0814 | -0.23368 | 20.9475 | 0.048389 | 0.013264 | -27.0821 | 3.0961 | 9.83 | -0.05 | 0.82183 | -0.52796 | -11.3329 | 0.92535 | 0.69935 | -16.7133 | 1.5837 | 0.42519 | 0.42947 | 0.43227 | 0.33503 | 0.45818 | 0.44472 | 0.42854
42838.4189 | -119 | 22.8989 | 22.8679 | 22.8509 | 22.778 | 22.4032 | 21.7469 | 22.718 | 21.8052 | 22.3658 | 22.3747 | 22.3527 | 22.0219 | 21.2394 | 22.2101 | 21.6035 | 21.7733 | 21.9039 | 21.0831 | 21.1871 | 21.3993 | 20.4794 | 20.6145 | 20.9116 | 21.883 | 21.653 | 21.2819 | 20.2557 | 20.3742 | 20.2215 | 22.0774 | 21.6719 | 21.1912 | 22.0088 | 21.7438 | 21.3567 | 19.9245 | 20.4846 |  | 20.5028 | 20.0599 | 20.0827 | 18.9596 |  | 16.9718 | 16.9331 | 16.7251 | 16.95 | 16.9769 | 17.5386 | 18.2239 | 16.2011 | 16.9124 | 16.2249 | 16.9868 | 18.0017 | 43.8858 | 51.7324 | 43.0967 | 21.4089 |  |  | 0.47664 | -0.40353 | -91.0705 | 0.59399 | 0.23078 | -197.8033 | 2.1484 | -0.58454 | -0.2091 | -0.16941 | -0.004396 | 8.829 | 9.0589 | 1.9789 | 21.7746 | 21.9967 | 22.1918 | 22.2545 | 22.081 | 21.3908 | 20.1984 | 22.1901 | 22.3669 | 22.4002 | 22.3557 | 21.9755 | 21.2044 | 22.2632 | 17.8112 | 17.2708 | 16.4458 | 16.3617 | 16.3269 | 17.1526 | 16.9512 | 22.3851 | 22.1459 | 21.7024 | 22.0917 | 21.8015 | 21.3042 | 21.9477 | 21.5284 | 20.9063 | 20.0799 | 20.1572 | 19.7352 | 19.74 | -0.17378 | -0.0003494 | 20.7171 | 22.0787 | 22.378 | 20.1212 | 21.6659 | 22.1146 | 21.9445 | 21.7048 | 21.2832 | 21.7853 | 21.4415 | 21.0437 | 20.2931 | 20.3212 | 20.2815 | 20.2518 | 20.0203 |  | 20.2137 | 19.7653 | 20.124 | 19.6073 | 20.0687 | 20.3054 |  | 20.3807 |  |  | 20.2968 | 20.3814 | 20.6229 | [5 empty] | 21.911 | 20.3132 | 21.6595 | 22.0338 | 19.5566 | 21.1578 | 21.7764 | 19.3339 | 19.8694 | 21.0992 |  | 19.744 | 20.8658 | 18.8716 | 19.6812 | 20.7589 | 19.3614 | 20.0618 | 19.0831 | 20.0686 | 19.1719 | 20.1108 | 18.7779 | 20.1033 | 20.9885 | 19.4423 | 19.7216 | 20.9543 | 18.8827 | 19.7561 | 20.761 | 18.8997 | 20.0753 | 19.303 | 19.9341 | 18.9746 | 20.0781 | -0.14556 | 20.9476 | 0.048622 | 0.013627 | -27.0432 | 3.0961 | -9.14 | -0.06 | 0.82408 | -0.75399 | -11.3271 | 0.91478 | 0.57079 | -16.7108 | 1.7415 | 0.42533 | 0.42941 | 0.43195 | 0.32953 | 0.45774 | 0.44511 | 0.42864
42838.4189 | -118 | 22.902 | 22.8672 | 22.8503 | 22.7777 | 22.3995 | 21.7424 | 22.7177 | 21.7977 | 22.3669 | 22.3748 | 22.3552 | 22.015 | 21.2321 | 22.2111 | 21.5952 | 21.7714 | 21.8968 | 21.0819 | 21.1821 | 21.3924 | 20.4811 | 20.616 | 20.9081 | 21.8854 | 21.6418 | 21.2706 | 20.2467 | 20.37 | 20.2058 | 22.0735 | 21.6667 | 21.1893 | 21.9981 | 21.738 | 21.3502 | 19.9176 | 20.4803 |  | 20.4969 | 20.0426 | 20.0799 | 18.9411 |  | 16.9857 | 16.9384 | 16.7426 | 16.9646 | 16.9839 | 17.5393 | 18.2038 | 16.2151 | 16.9194 | 16.2782 | 16.9953 | 17.9992 | 44.0376 | 51.7709 | 43.2393 | 21.4096 |  |  | 0.51672 | -0.24977 | -91.746 | 0.51776 | 0.25181 | -197.8598 | 1.854 | -0.52934 | -0.22195 | -0.15346 | -0.13824 | 8.8282 | 9.0579 | 1.9789 | 21.7789 | 22.0055 | 22.1986 | 22.2653 | 22.0943 | 21.4067 | 20.2146 | 22.2098 | 22.3805 | 22.4133 | 22.3596 | 21.9857 | 21.2202 | 22.2784 | 17.8434 | 17.2569 | 16.451 | 16.3969 | 16.3415 | 17.1527 | 16.9497 | 22.3795 | 22.1429 | 21.7007 | 22.0871 | 21.8006 | 21.3075 | 21.946 | 21.5319 | 20.9025 | 20.0858 | 20.1531 | 19.7368 | 19.7367 | -0.13957 | 0.15067 | 20.7087 | 22.0741 | 22.3702 | 20.109 | 21.665 | 22.1076 | 21.9395 | 21.7042 | 21.2682 | 21.774 | 21.4388 | 21.0374 | 20.2771 | 20.3002 | 20.2743 | 20.2405 | 20.0357 |  | 20.2162 | 19.7821 | 20.1238 | 19.5979 | 20.0683 | 20.2982 |  | 20.3861 |  |  | 20.3083 | 20.3858 | 20.6241 | [5 empty] | 21.9249 | 20.3168 | 21.6664 | 22.0376 | 19.5608 | 21.1624 | 21.7819 | 19.3331 | 19.8721 | 21.1181 |  | 19.7409 | 20.8672 | 18.8686 | 19.6732 | 20.7499 | 19.3617 | 20.066 | 19.0816 | 20.0615 | 19.1719 | 20.102 | 18.7807 | 20.1039 | 20.9877 | 19.4356 | 19.717 | 20.9495 | 18.8823 | 19.7477 | 20.7646 | 18.9007 | 20.0729 | 19.2962 | 19.9235 | 18.9721 | 20.0777 | -0.24518 | 20.9481 | 0.048499 | 0.013083 | -27.0413 | 3.0961 | -13.98 | -0.11 | 0.85801 | -0.5932 | -11.3691 | 0.85408 | 0.59623 | -16.7132 | 1.6178 | 0.42499 | 0.42894 | 0.43219 | 0.32596 | 0.45698 | 0.44539 | 0.42893
42838.4189 | -117 | 22.8985 | 22.8667 | 22.8544 | 22.7791 | 22.4015 | 21.7447 | 22.7193 | 21.802 | 22.3718 | 22.3751 | 22.3584 | 22.0229 | 21.2425 | 22.209 | 21.6006 | 21.7637 | 21.8877 | 21.0827 | 21.1801 | 21.3971 | 20.4831 | 20.6126 | 20.9054 | 21.8824 | 21.6373 | 21.2736 | 20.2406 | 20.3699 | 20.1947 | 22.0795 | 21.6735 | 21.1921 | 22.003 | 21.7289 | 21.3575 | 19.9164 | 20.4882 |  | 20.4936 | 20.0414 | 20.0787 | 18.9326 |  | 16.981 | 16.9484 | 16.7409 | 16.9761 | 16.9733 | 17.5192 | 18.1882 | 16.1988 | 16.925 | 16.3277 | 16.9984 | 17.9943 | 44.2121 | 51.7931 | 43.3759 | 21.4132 |  |  | 0.45101 | -0.31942 | -91.8485 | 0.50133 | 0.24984 | -197.819 | 1.7199 | -0.58782 | 0.13826 | -0.41131 | 0.00602 | 8.8284 | 9.0583 | 1.9784 | 21.7839 | 22.0078 | 22.2068 | 22.2685 | 22.0961 | 21.4076 | 20.221 | 22.2092 | 22.3825 | 22.4191 | 22.3666 | 21.9958 | 21.2275 | 22.2831 | 17.8748 | 17.222 | 16.4579 | 16.4098 | 16.3308 | 17.1555 | 16.9559 | 22.3827 | 22.1486 | 21.7032 | 22.0898 | 21.8064 | 21.3164 | 21.9496 | 21.5349 | 20.9123 | 20.0852 | 20.1641 | 19.7417 | 19.75 | -0.13486 | -0.1527 | 20.7128 | 22.0638 | 22.3696 | 20.1041 | 21.6615 | 22.1019 | 21.9384 | 21.7024 | 21.2698 | 21.7667 | 21.441 | 21.0318 | 20.2491 | 20.2836 | 20.2808 | 20.2367 | 20.0544 |  | 20.2238 | 19.767 | 20.1303 | 19.5978 | 20.0755 | 20.3093 |  | 20.386 |  |  | 20.3081 | 20.3881 | 20.6235 | [5 empty] | 21.9131 | 20.3653 | 21.6605 | 22.0334 | 19.5538 | 21.153 | 21.7772 | 19.3353 | 19.8641 | 21.1454 |  | 19.7441 | 20.8619 | 18.8833 | 19.6763 | 20.7584 | 19.3366 | 20.083 | 19.0831 | 20.0634 | 19.1655 | 20.099 | 18.7854 | 20.1306 | 21.0048 | 19.4446 | 19.7223 | 20.9571 | 18.9008 | 19.7509 | 20.7639 | 18.9115 | 20.0773 | 19.3106 | 19.9301 | 18.9757 | 20.0765 | -0.25074 | 20.947 | 0.048524 | 0.013141 | -27.0237 | 3.0961 | -24.79 | -0.04 | 0.80158 | -0.67085 | -11.3756 | 0.84043 | 0.59387 | -16.7109 | 1.5582 | 0.42473 | 0.42957 | 0.43244 | 0.32279 | 0.45696 | 0.44559 | 0.42854
42838.4189 | -116 | 22.9069 | 22.8665 | 22.8603 | 22.7846 | 22.4101 | 21.7466 | 22.7219 | 21.808 | 22.3682 | 22.3828 | 22.3676 | 22.0265 | 21.2449 | 22.2131 | 21.604 | 21.7607 | 21.8902 | 21.0743 | 21.1802 | 21.3955 | 20.4711 | 20.6111 | 20.9027 | 21.8788 | 21.6432 | 21.277 | 20.234 | 20.3718 | 20.1904 | 22.0802 | 21.6755 | 21.1947 | 22.0092 | 21.7412 | 21.3536 | 19.9215 | 20.4819 |  | 20.5044 | 20.0486 | 20.0849 | 18.938 |  | 16.9806 | 16.9392 | 16.7474 | 16.9712 | 16.9749 | 17.5226 | 18.1941 | 16.1794 | 16.9174 | 16.3744 | 16.987 | 18.001 | 44.3891 | 51.8198 | 43.5172 | 21.4081 |  |  | 0.55089 | -0.43836 | -92.8401 | 0.3778 | 0.20384 | -197.8039 | 2.1208 | -0.65616 | -0.0090528 | -0.14108 | 0.01904 | 8.8288 | 9.0586 | 1.9786 | 21.7807 | 22.0041 | 22.1962 | 22.2583 | 22.0871 | 21.402 | 20.2103 | 22.1986 | 22.3699 | 22.4124 | 22.3583 | 21.9873 | 21.2165 | 22.2723 | 17.889 | 17.2109 | 16.4358 | 16.3822 | 16.3235 | 17.1521 | 16.951 | 22.3798 | 22.1412 | 21.697 | 22.0853 | 21.8004 | 21.3069 | 21.9511 | 21.5272 | 20.91 | 20.0847 | 20.1732 | 19.7396 | 19.7485 | -0.13879 | -0.28051 | 20.7151 | 22.0729 | 22.3686 | 20.1115 | 21.6726 | 22.106 | 21.9452 | 21.7042 | 21.2795 | 21.771 | 21.4433 | 21.0274 | 20.2852 | 20.3018 | 20.2783 | 20.2429 | 20.0483 |  | 20.2104 | 19.8099 | 20.1299 | 19.5945 | 20.0621 | 20.3034 |  | 20.3896 |  |  | 20.3054 | 20.3849 | 20.6242 | [5 empty] | 21.9155 | 20.3303 | 21.651 | 22.0313 | 19.5559 | 21.152 | 21.7759 | 19.3353 | 19.8697 | 21.191 |  | 19.7417 | 20.8683 | 18.8763 | 19.682 | 20.7626 | 19.3498 | 20.1082 | 19.0753 | 20.0707 | 19.1637 | 20.0982 | 18.7786 | 20.1118 | 20.9999 | 19.4375 | 19.7217 | 20.9535 | 18.8961 | 19.7455 | 20.763 | 18.9052 | 20.0752 | 19.3052 | 19.9233 | 18.9754 | 20.0781 | -0.14241 | 20.9468 | 0.048383 | 0.012916 | -27.0718 | 3.096 | -11.87 | -0.08 | 0.8859 | -0.78587 | -11.4367 | 0.72956 | 0.53643 | -16.7104 | 1.7303 | 0.42445 | 0.42837 | 0.43208 | 0.32082 | 0.45884 | 0.44561 | 0.42856
42838.4189 | -115 | 22.9047 | 22.8663 | 22.8548 | 22.773 | 22.405 | 21.7418 | 22.7194 | 21.8055 | 22.355 | 22.3656 | 22.3574 | 22.0196 | 21.2376 | 22.2048 | 21.5997 | 21.7728 | 21.8966 | 21.0802 | 21.1817 | 21.3891 | 20.4783 | 20.6054 | 20.9031 | 21.8885 | 21.6422 | 21.2747 | 20.2413 | 20.3752 | 20.1915 | 22.0826 | 21.6731 | 21.1963 | 22.0034 | 21.7404 | 21.3493 | 19.9115 | 20.4783 |  | 20.4975 | 20.0538 | 20.0852 | 18.9368 |  | 16.9874 | 16.9401 | 16.7526 | 16.9781 | 16.993 | 17.5571 | 18.214 | 16.194 | 16.9152 | 16.4017 | 16.9923 | 18.0057 | 44.5623 | 51.8267 | 43.6434 | 21.4149 |  |  | 0.40436 | -0.5343 | -93.7331 | 0.6689 | 0.30438 | -197.8112 | 1.3539 | -0.68442 | 0.066452 | -0.064297 | -0.058038 | 8.8284 | 9.0581 | 1.9787 | 21.7844 | 22.0003 | 22.1998 | 22.256 | 22.0834 | 21.4001 | 20.2133 | 22.2016 | 22.3713 | 22.4101 | 22.3508 | 21.9848 | 21.2154 | 22.2722 | 17.8987 | 17.2126 | 16.3929 | 16.3557 | 16.3175 | 17.1486 | 16.948 | 22.3792 | 22.1424 | 21.7016 | 22.085 | 21.798 | 21.3024 | 21.948 | 21.5324 | 20.906 | 20.0762 | 20.2109 | 19.7652 | 19.759 | -0.067618 | -0.3545 | 20.7182 | 22.0716 | 22.368 | 20.117 | 21.6697 | 22.1074 | 21.9409 | 21.7061 | 21.2795 | 21.7752 | 21.44 | 21.0353 | 20.2852 | 20.3139 | 20.2787 | 20.25 | 20.0238 |  | 20.2169 | 19.8183 | 20.128 | 19.6072 | 20.0734 | 20.2992 |  | 20.3921 |  |  | 20.2982 | 20.3821 | 20.6253 | [5 empty] | 21.9141 | 20.3244 | 21.6463 | 22.0291 | 19.5533 | 21.157 | 21.7711 | 19.3409 | 19.8836 | 21.2281 |  | 19.755 | 20.8662 | 18.8889 | 19.6873 | 20.7603 | 19.3514 | 20.1351 | 19.0818 | 20.0664 | 19.1627 | 20.0988 | 18.7901 | 20.1311 | 21.0019 | 19.4544 | 19.7274 | 20.9614 | 18.9005 | 19.7547 | 20.7781 | 18.9089 | 20.0868 | 19.3197 | 19.9188 | 18.9857 | 20.0683 | -0.23294 | 20.9475 | 0.049317 | 0.013322 | -27.0853 | 3.096 | -2.66 | -0.06 | 0.75899 | -0.86761 | -11.4916 | 0.97077 | 0.65554 | -16.7117 | 1.3826 | 0.42534 | 0.42807 | 0.43211 | 0.31933 | 0.46325 | 0.44531 | 0.42798
42838.419 | -114 | 22.9 | 22.8596 | 22.8483 | 22.7753 | 22.4033 | 21.7397 | 22.7141 | 21.7927 | 22.3637 | 22.3705 | 22.3471 | 22.0146 | 21.2326 | 22.2089 | 21.5925 | 21.7662 | 21.8884 | 21.0769 | 21.1733 | 21.392 | 20.4762 | 20.6116 | 20.9016 | 21.8773 | 21.6372 | 21.2655 | 20.2294 | 20.3656 | 20.2057 | 22.0695 | 21.6694 | 21.1944 | 21.9994 | 21.7353 | 21.3551 | 19.913 | 20.4834 |  | 20.4971 | 20.0447 | 20.0791 | 18.9342 |  | 16.9846 | 16.9486 | 16.7718 | 17.0019 | 17.0311 | 17.5818 | 18.2303 | 16.204 | 16.9231 | 16.3935 | 16.9989 | 17.9995 | 44.7198 | 51.8164 | 43.7786 | 21.4139 |  |  | 0.37676 | -0.35885 | -93.8987 | 0.70964 | 0.28072 | -197.8131 | 1.5806 | -0.63185 | -0.34688 | 0.086339 | -0.062031 | 8.8286 | 9.0585 | 1.9782 | 21.7805 | 21.9991 | 22.199 | 22.2616 | 22.0781 | 21.4023 | 20.2151 | 22.2045 | 22.3703 | 22.4098 | 22.3513 | 21.9859 | 21.2192 | 22.2743 | 17.8926 | 17.2096 | 16.3593 | 16.3442 | 16.2984 | 17.1506 | 16.9461 | 22.3715 | 22.1444 | 21.7035 | 22.0774 | 21.7909 | 21.2975 | 21.9403 | 21.5241 | 20.9035 | 20.0748 | 20.2376 | 19.7968 | 19.7623 | -0.1091 | -0.12512 | 20.7244 | 22.0742 | 22.3836 | 20.1304 | 21.6732 | 22.1138 | 21.9527 | 21.7119 | 21.2836 | 21.7843 | 21.4464 | 21.0497 | 20.2927 | 20.3349 | 20.2845 | 20.254 | 20.0154 |  | 20.2132 | 19.8133 | 20.1211 | 19.6099 | 20.0762 | 20.2994 |  | 20.3855 |  |  | 20.3028 | 20.3948 | 20.6192 | [5 empty] | 21.9152 | 20.3345 | 21.6494 | 22.0372 | 19.5554 | 21.1505 | 21.7715 | 19.338 | 19.882 | 21.2854 |  | 19.7492 | 20.8613 | 18.8825 | 19.6887 | 20.764 | 19.3417 | 20.1394 | 19.0835 | 20.0723 | 19.17 | 20.0983 | 18.8062 | 20.1292 | 21.0028 | 19.4465 | 19.7312 | 20.9636 | 18.9082 | 19.7568 | 20.7839 | 18.9034 | 20.0873 | 19.3159 | 19.9208 | 18.9792 | 20.0707 | -0.17432 | 20.947 | 0.048641 | 0.013918 | -27.0327 | 3.096 | -14.93 | -0.04 | 0.73265 | -0.71104 | -11.5019 | 0.99991 | 0.62958 | -16.7125 | 1.4939 | 0.42545 | 0.42798 | 0.43213 | 0.32025 | 0.46677 | 0.44543 | 0.42785
42838.419 | -113 | 22.9011 | 22.8698 | 22.8518 | 22.7721 | 22.4071 | 21.7429 | 22.7164 | 21.7988 | 22.3692 | 22.3769 | 22.3541 | 22.0193 | 21.2426 | 22.2092 | 21.6021 | 21.7644 | 21.8933 | 21.0825 | 21.1791 | 21.3963 | 20.4753 | 20.6208 | 20.9051 | 21.8772 | 21.6429 | 21.2756 | 20.248 | 20.3776 | 20.3182 | 22.0797 | 21.6796 | 21.1946 | 22.001 | 21.7318 | 21.3492 | 19.9138 | 20.4947 |  | 20.4963 | 20.0533 | 20.0843 | 18.9338 |  | 16.9941 | 16.9665 | 16.8063 | 17.0445 | 17.0578 | 17.5962 | 18.2268 | 16.1492 | 16.9281 | 16.3218 | 16.9893 | 18.0052 | 44.8917 | 51.8142 | 43.92 | 21.4112 |  |  | 0.42801 | -0.41602 | -93.8396 | 0.65641 | 0.23341 | -197.8335 | 1.3618 | -0.65945 | 0.0030124 | -0.12514 | -0.084426 | 8.8299 | 9.0597 | 1.9786 | 21.778 | 22.0032 | 22.2001 | 22.2627 | 22.0825 | 21.4005 | 20.2131 | 22.1991 | 22.3707 | 22.4035 | 22.3548 | 21.9888 | 21.209 | 22.2649 | 17.8816 | 17.2332 | 16.3639 | 16.348 | 16.2784 | 17.1488 | 16.9465 | 22.3748 | 22.1412 | 21.7054 | 22.0891 | 21.8002 | 21.2968 | 21.947 | 21.5296 | 20.9019 | 20.0782 | 20.2599 | 19.8204 | 19.7701 | -0.046779 | -0.27176 | 20.7236 | 22.0764 | 22.3744 | 20.1242 | 21.663 | 22.1058 | 21.952 | 21.709 | 21.2746 | 21.7723 | 21.4486 | 21.0396 | 20.2805 | 20.3308 | 20.2842 | 20.2509 | 19.997 |  | 20.2254 | 19.8164 | 20.1374 | 19.6358 | 20.0808 | 20.314 |  | 20.3937 |  |  | 20.3042 | 20.3813 | 20.6261 | [5 empty] | 21.9113 | 20.3285 | 21.6589 | 22.0234 | 19.5437 | 21.1558 | 21.7636 | 19.3406 | 19.8975 | 21.3417 |  | 19.7486 | 20.8599 | 18.8834 | 19.6796 | 20.7598 | 19.3382 | 20.1467 | 19.0851 | 20.0745 | 19.1575 | 20.0886 | 18.8094 | 20.1341 | 21.0025 | 19.457 | 19.7303 | 20.9561 | 18.9098 | 19.7609 | 20.7789 | 18.9059 | 20.0854 | 19.3196 | 19.9258 | 18.9824 | 20.0764 | -0.20233 | 20.9479 | 0.048751 | 0.014781 | -27.1013 | 3.096 | -11.97 | -0.1 | 0.78105 | -0.76562 | -11.4986 | 0.96171 | 0.57409 | -16.7138 | 1.3867 | 0.42637 | 0.42844 | 0.43156 | 0.32126 | 0.4663 | 0.44547 | 0.42775
42838.419 | -112 | 22.9074 | 22.8764 | 22.855 | 22.7799 | 22.406 | 21.7488 | 22.7186 | 21.8061 | 22.3703 | 22.3791 | 22.3581 | 22.0293 | 21.2482 | 22.2124 | 21.5921 | 21.7594 | 21.8958 | 21.0822 | 21.177 | 21.403 | 20.4731 | 20.6125 | 20.903 | 21.8819 | 21.638 | 21.2691 | 20.2678 | 20.3772 | 20.4318 | 22.0739 | 21.6745 | 21.1952 | 21.996 | 21.7366 | 21.3559 | 19.9173 | 20.5044 |  | 20.4927 | 20.0536 | 20.0837 | 18.9386 |  | 16.9919 | 16.9888 | 16.8251 | 17.0544 | 17.0482 | 17.6004 | 18.2261 | 16.0572 | 16.9128 | 16.3254 | 16.988 | 18.004 | 45.0835 | 51.8089 | 44.0528 | 21.4074 |  |  | 0.4129 | -0.1374 | -94.3534 | 0.64196 | 0.21961 | -197.8762 | 1.2264 | -0.44654 | 0.198 | -0.17822 | -0.13703 | 8.8284 | 9.0583 | 1.979 | 21.7769 | 21.9956 | 22.1858 | 22.2504 | 22.0673 | 21.3877 | 20.2062 | 22.1881 | 22.3662 | 22.3986 | 22.3447 | 21.9735 | 21.2048 | 22.2657 | 17.8507 | 17.2891 | 16.3581 | 16.3603 | 16.2828 | 17.1427 | 16.9445 | 22.3807 | 22.1464 | 21.7032 | 22.0916 | 21.8018 | 21.3027 | 21.949 | 21.5343 | 20.9064 | 20.0848 | 20.2697 | 19.8499 | 19.7796 | -0.02358 | -0.32997 | 20.7248 | 22.0773 | 22.3651 | 20.1259 | 21.6648 | 22.1066 | 21.9485 | 21.7113 | 21.2751 | 21.7758 | 21.444 | 21.033 | 20.2829 | 20.342 | 20.2915 | 20.2537 | 19.9706 |  | 20.2172 | 19.8081 | 20.1283 | 19.6356 | 20.0751 | 20.3076 |  | 20.3871 |  |  | 20.3073 | 20.3272 | 20.6169 | [5 empty] | 21.9207 | 20.3296 | 21.6563 | 22.0287 | 19.5522 | 21.1534 | 21.7725 | 19.3414 | 19.9067 | 21.3837 |  | 19.7466 | 20.8653 | 18.8898 | 19.6913 | 20.7685 | 19.3481 | 20.1655 | 19.0893 | 20.0757 | 19.1618 | 20.0988 | 18.8091 | 20.1301 | 20.9974 | 19.4493 | 19.7238 | 20.9534 | 18.9016 | 19.7579 | 20.775 | 18.9102 | 20.0795 | 19.3177 | 19.9266 | 18.9894 | 20.0593 | -0.16504 | 20.9467 | 0.048671 | 0.015326 | -27.164 | 3.096 | -3.77 | -0.06 | 0.76728 | -0.44001 | -11.5305 | 0.95109 | 0.55687 | -16.7157 | 1.316 | 0.42683 | 0.42837 | 0.43137 | 0.32399 | 0.46671 | 0.44545 | 0.4277
42838.419 | -111 | 22.912 | 22.875 | 22.8574 | 22.7806 | 22.4104 | 21.7501 | 22.7234 | 21.8068 | 22.371 | 22.3751 | 22.3596 | 22.0215 | 21.2453 | 22.2123 | 21.5857 | 21.7551 | 21.8875 | 21.0723 | 21.169 | 21.3929 | 20.4614 | 20.6071 | 20.8909 | 21.8742 | 21.6237 | 21.2586 | 20.2724 | 20.3661 | 20.4718 | 22.0696 | 21.668 | 21.1857 | 21.9928 | 21.7353 | 21.3535 | 19.9102 | 20.5104 |  | 20.4897 | 20.0468 | 20.0868 | 18.952 |  | 17.0087 | 17.0208 | 16.831 | 17.0585 | 17.0422 | 17.604 | 18.2549 | 16.0092 | 16.9248 | 16.3695 | 16.9906 | 18.0032 | 45.2577 | 51.7784 | 44.2102 | 21.411 |  |  | 0.46415 | -0.35557 | -95.1328 | 0.47505 | 0.25969 | -197.8033 | 1.3789 | -0.39529 | 0.088247 | -0.078774 | -0.095883 | 8.8291 | 9.0587 | 1.9791 | 21.7752 | 21.998 | 22.1998 | 22.2564 | 22.076 | 21.3953 | 20.2169 | 22.1964 | 22.3752 | 22.4057 | 22.3558 | 21.9852 | 21.216 | 22.2747 | 17.8456 | 17.3291 | 16.3423 | 16.3772 | 16.2844 | 17.1514 | 16.9455 | 22.3729 | 22.1379 | 21.7049 | 22.082 | 21.7952 | 21.2987 | 21.9423 | 21.5234 | 20.9036 | 20.0773 | 20.2687 | 19.8538 | 19.789 | 0.0004054 | -0.27861 | 20.7139 | 22.062 | 22.365 | 20.1198 | 21.6564 | 22.1005 | 21.9422 | 21.705 | 21.2777 | 21.7734 | 21.4395 | 21.0249 | 20.2686 | 20.3583 | 20.2848 | 20.2619 | 19.9539 |  | 20.2056 | 19.803 | 20.1175 | 19.6372 | 20.0726 | 20.2996 |  | 20.3827 |  |  | 20.2928 | 20.2575 | 20.6044 | [5 empty] | 21.9164 | 20.3333 | 21.6507 | 22.0258 | 19.5482 | 21.1414 | 21.7699 | 19.3396 | 19.9044 | 21.3889 |  | 19.7372 | 20.8644 | 18.8777 | 19.6782 | 20.7581 | 19.3475 | 20.1598 | 19.0753 | 20.0677 | 19.1556 | 20.0895 | 18.8102 | 20.1378 | 21 | 19.4548 | 19.7262 | 20.9588 | 18.9112 | 19.7573 | 20.7767 | 18.9152 | 20.0871 | 19.3147 | 19.9197 | 18.9842 | 20.0475 | -0.15595 | 20.9471 | 0.048032 | 0.015558 | -27.1047 | 3.096 | -29.19 | -0.1 | 0.81356 | -0.70787 | -11.5787 | 0.81821 | 0.60556 | -16.7127 | 1.3954 | 0.4269 | 0.42815 | 0.43125 | 0.32557 | 0.46858 | 0.44484 | 0.42719
42838.419 | -110 | 22.9087 | 22.8775 | 22.8542 | 22.7808 | 22.4138 | 21.7434 | 22.7259 | 21.8013 | 22.3697 | 22.377 | 22.3558 | 22.0253 | 21.2474 | 22.2101 | 21.5923 | 21.7657 | 21.8898 | 21.0755 | 21.1774 | 21.4001 | 20.4706 | 20.6132 | 20.9081 | 21.8842 | 21.6363 | 21.2669 | 20.2941 | 20.3873 | 20.5142 | 22.074 | 21.6684 | 21.1861 | 21.9983 | 21.7359 | 21.3533 | 19.9106 | 20.5157 |  | 20.5017 | 20.0417 | 20.0907 | 18.9574 |  | 17.0166 | 17.0238 | 16.8296 | 17.0624 | 17.0586 | 17.6253 | 18.2674 | 15.8952 | 16.9219 | 16.3512 | 16.9876 | 18.0089 | 45.4296 | 51.7581 | 44.3562 | 21.4078 |  |  | 0.60412 | -0.34045 | -95.1538 | 0.81609 | 0.24918 | -197.8736 | 1.1942 | -0.62331 | 0.039597 | -0.20528 | -0.11012 | 8.8286 | 9.0586 | 1.979 | 21.7744 | 21.9962 | 22.1977 | 22.2655 | 22.0862 | 21.3943 | 20.21 | 22.202 | 22.3767 | 22.4084 | 22.359 | 21.99 | 21.2175 | 22.2712 | 17.8233 | 17.331 | 16.3177 | 16.3944 | 16.3068 | 17.1559 | 16.9385 | 22.376 | 22.1445 | 21.7001 | 22.0811 | 21.805 | 21.3012 | 21.9468 | 21.5255 | 20.9083 | 20.0769 | 20.2863 | 19.8704 | 19.7957 | -0.37078 | -0.10192 | 20.7148 | 22.0619 | 22.3687 | 20.1225 | 21.6545 | 22.1082 | 21.9466 | 21.7052 | 21.2761 | 21.7779 | 21.4426 | 21.0334 | 20.2621 | 20.3888 | 20.2875 | 20.266 | 19.9439 |  | 20.2217 | 19.8077 | 20.1323 | 19.6688 | 20.0826 | 20.3145 |  | 20.395 |  |  | 20.2803 | 20.2243 | 20.5875 | [5 empty] | 21.9194 | 20.3341 | 21.646 | 22.0265 | 19.531 | 21.1459 | 21.7629 | 19.3416 | 19.9182 | 21.4012 |  | 19.7388 | 20.8686 | 18.8737 | 19.679 | 20.76 | 19.3568 | 20.1618 | 19.0766 | 20.0701 | 19.156 | 20.0876 | 18.8127 | 20.1256 | 20.9955 | 19.4465 | 19.7274 | 20.9598 | 18.9071 | 19.756 | 20.7744 | 18.9111 | 20.0794 | 19.3162 | 19.9301 | 18.9776 | 20.0451 | -0.3229 | 20.9467 | 0.047449 | 0.015703 | -27.1156 | 3.096 | -21.82 | -0.07 | 0.92823 | -0.69267 | -11.58 | 1.0724 | 0.5932 | -16.7163 | 1.2986 | 0.42772 | 0.42851 | 0.4307 | 0.32857 | 0.47049 | 0.4447 | 0.42699
42838.419 | -109 | 22.9038 | 22.8712 | 22.858 | 22.7817 | 22.4061 | 21.7427 | 22.7254 | 21.808 | 22.3754 | 22.3883 | 22.3609 | 22.0281 | 21.2444 | 22.211 | 21.5883 | 21.7718 | 21.893 | 21.082 | 21.1858 | 21.4054 | 20.4766 | 20.6175 | 20.9143 | 21.8913 | 21.6482 | 21.2761 | 20.3179 | 20.3877 | 20.5466 | 22.0803 | 21.6817 | 21.196 | 22.0086 | 21.7398 | 21.356 | 19.9198 | 20.5278 |  | 20.5063 | 20.0452 | 20.1046 | 18.9697 |  | 17.0176 | 17.0165 | 16.8153 | 17.0711 | 17.0743 | 17.6423 | 18.2558 | 15.7734 | 16.919 | 16.3365 | 16.9866 | 18.0118 | 45.5937 | 51.7346 | 44.4998 | 21.4089 |  |  | 0.44181 | -0.43179 | -95.3582 | 0.41197 | 0.1539 | -197.8512 | 1.3651 | -0.51226 | -0.10538 | -0.057374 | -0.026617 | 8.828 | 9.058 | 1.9791 | 21.7866 | 22.0089 | 22.203 | 22.2641 | 22.0871 | 21.4037 | 20.2115 | 22.2038 | 22.3833 | 22.4105 | 22.3632 | 21.9868 | 21.2201 | 22.2754 | 17.7716 | 17.2575 | 16.3198 | 16.38 | 16.3175 | 17.1505 | 16.9382 | 22.3739 | 22.145 | 21.7009 | 22.0788 | 21.7986 | 21.3018 | 21.943 | 21.5261 | 20.9088 | 20.0838 | 20.2928 | 19.8663 | 19.8025 | -0.28329 | -0.1295 | 20.7077 | 22.0594 | 22.3606 | 20.1179 | 21.6529 | 22.1032 | 21.9394 | 21.6991 | 21.273 | 21.7765 | 21.4365 | 21.0359 | 20.2567 | 20.4045 | 20.2838 | 20.2546 | 19.9199 |  | 20.2081 | 19.7917 | 20.1235 | 19.6764 | 20.0771 | 20.3102 |  | 20.391 |  |  | 20.2697 | 20.1922 | 20.5767 | [5 empty] | 21.9144 | 20.3325 | 21.6493 | 22.0298 | 19.533 | 21.1483 | 21.7656 | 19.3455 | 19.9264 | 21.4064 |  | 19.7401 | 20.8645 | 18.8683 | 19.676 | 20.7673 | 19.3618 | 20.1654 | 19.0788 | 20.0678 | 19.1561 | 20.0906 | 18.8199 | 20.1197 | 20.9956 | 19.4452 | 19.7369 | 20.9665 | 18.8987 | 19.7491 | 20.7695 | 18.9092 | 20.0712 | 19.3176 | 19.9455 | 18.98 | 20.0455 | -0.22143 | 20.9462 | 0.047412 | 0.016074 | -27.1144 | 3.096 | -3.37 | -0.15 | 0.79385 | -0.78006 | -11.5923 | 0.76194 | 0.4662 | -16.7158 | 1.3885 | 0.42794 | 0.42866 | 0.43031 | 0.33368 | 0.47023 | 0.44467 | 0.42703
42838.419 | -108 | 22.9049 | 22.8681 | 22.8553 | 22.7715 | 22.4058 | 21.7479 | 22.7238 | 21.7943 | 22.3788 | 22.3722 | 22.3617 | 22.0199 | 21.2362 | 22.2105 | 21.5941 | 21.7712 | 21.8961 | 21.0855 | 21.191 | 21.4076 | 20.479 | 20.6215 | 20.9181 | 21.8905 | 21.6523 | 21.2844 | 20.33 | 20.3898 | 20.5613 | 22.0829 | 21.6776 | 21.2022 | 22.0131 | 21.7396 | 21.3605 | 19.9161 | 20.5241 |  | 20.5023 | 20.0507 | 20.1088 | 18.9937 |  | 17.0194 | 17.0178 | 16.8331 | 17.0869 | 17.0863 | 17.6298 | 18.2104 | 15.6917 | 16.9307 | 16.3283 | 16.9894 | 18.0031 | 45.7335 | 51.6823 | 44.6327 | 21.4037 |  |  | 0.42999 | -0.099949 | -94.4343 | 0.91597 | 0.17821 | -197.842 | 1.7173 | -0.46428 | 0.056917 | -0.33032 | -0.04606 | 8.8289 | 9.0587 | 1.9791 | 21.7882 | 22.0063 | 22.1948 | 22.2593 | 22.0817 | 21.3993 | 20.2061 | 22.1974 | 22.3751 | 22.4051 | 22.3585 | 21.983 | 21.2147 | 22.2675 | 17.6588 | 17.1922 | 16.3011 | 16.3578 | 16.3123 | 17.1478 | 16.9415 | 22.3701 | 22.1445 | 21.7026 | 22.0809 | 21.8004 | 21.2985 | 21.9441 | 21.5301 | 20.9035 | 20.0795 | 20.3183 | 19.8757 | 19.7904 | -0.12581 | -0.29307 | 20.7061 | 22.0635 | 22.3648 | 20.1112 | 21.6545 | 22.106 | 21.938 | 21.6996 | 21.269 | 21.7759 | 21.4313 | 21.0326 | 20.2552 | 20.4087 | 20.2896 | 20.2511 | 19.9381 |  | 20.2104 | 19.7976 | 20.1195 | 19.7007 | 20.0731 | 20.3111 |  | 20.3917 |  |  | 20.2589 | 20.1669 | 20.563 | [5 empty] | 21.9189 | 20.3401 | 21.6527 | 22.0308 | 19.5351 | 21.1485 | 21.767 | 19.3481 | 19.9267 | 21.4098 |  | 19.7402 | 20.8698 | 18.8649 | 19.6821 | 20.7718 | 19.36 | 20.1629 | 19.0773 | 20.0655 | 19.1617 | 20.1011 | 18.818 | 20.1153 | 20.9899 | 19.4426 | 19.7314 | 20.9788 | 18.8961 | 19.7474 | 20.7666 | 18.8986 | 20.0666 | 19.3119 | 19.9557 | 18.9756 | 20.0353 | -0.22255 | 20.9459 | 0.047369 | 0.015457 | -27.073 | 3.096 | -11.71 | -0.09 | 0.78317 | -0.3753 | -11.536 | 1.1361 | 0.50166 | -16.7151 | 1.5573 | 0.42751 | 0.42836 | 0.4295 | 0.3459 | 0.47269 | 0.44388 | 0.42722
42838.419 | -107 | 22.9045 | 22.8673 | 22.8577 | 22.7729 | 22.4149 | 21.7454 | 22.7257 | 21.8047 | 22.3664 | 22.3764 | 22.3553 | 22.0191 | 21.2429 | 22.2133 | 21.5953 | 21.7689 | 21.8958 | 21.0778 | 21.1831 | 21.3979 | 20.4755 | 20.6163 | 20.9052 | 21.8847 | 21.6487 | 21.2745 | 20.3239 | 20.387 | 20.562 | 22.0787 | 21.6699 | 21.1927 | 22.0034 | 21.7385 | 21.348 | 19.9137 | 20.5255 |  | 20.4969 | 20.0533 | 20.1029 | 19.0156 |  | 17.0197 | 17.0213 | 16.8322 | 17.0802 | 17.0872 | 17.6089 | 18.1717 | 15.641 | 16.9242 | 16.3033 | 16.9879 | 18.0015 | 45.8889 | 51.6361 | 44.7401 | 21.4079 |  |  | 0.45101 | -0.050665 | -93.5228 | 1.0099 | 0.40163 | -197.8046 | 1.4959 | -0.51554 | 0.16901 | -0.57978 | -0.15473 | 8.8286 | 9.0586 | 1.9788 | 21.7795 | 21.9998 | 22.1869 | 22.254 | 22.0754 | 21.3951 | 20.2037 | 22.1958 | 22.3698 | 22.4023 | 22.3541 | 21.9834 | 21.2078 | 22.2678 | 17.5961 | 17.1941 | 16.2918 | 16.3318 | 16.3122 | 17.1465 | 16.9319 | 22.3675 | 22.1346 | 21.697 | 22.0821 | 21.7985 | 21.2996 | 21.9425 | 21.5242 | 20.902 | 20.0808 | 20.3356 | 19.8874 | 19.7764 | -0.19777 | -0.36572 | 20.7039 | 22.0659 | 22.3667 | 20.1158 | 21.6492 | 22.1056 | 21.9378 | 21.6977 | 21.2642 | 21.7677 | 21.4341 | 21.0309 | 20.2431 | 20.4198 | 20.286 | 20.2619 | 19.9568 |  | 20.2078 | 19.7973 | 20.1278 | 19.71 | 20.0704 | 20.3173 |  | 20.3916 |  |  | 20.2378 | 20.1522 | 20.543 | [5 empty] | 21.916 | 20.3388 | 21.6508 | 22.027 | 19.5375 | 21.1457 | 21.7675 | 19.3534 | 19.9309 | 21.4165 |  | 19.7454 | 20.8719 | 18.8729 | 19.6874 | 20.7689 | 19.3693 | 20.1647 | 19.0791 | 20.0727 | 19.1699 | 20.1055 | 18.8122 | 20.1006 | 20.9989 | 19.4454 | 19.7401 | 20.9889 | 18.906 | 19.7467 | 20.762 | 18.8839 | 20.0688 | 19.3113 | 19.9703 | 18.9805 | 20.0378 | -0.15595 | 20.9465 | 0.047436 | 0.015732 | -27.0186 | 3.0959 | -11.38 | -0.12 | 0.80209 | -0.26721 | -11.4803 | 1.193 | 0.75309 | -16.7129 | 1.4534 | 0.4269 | 0.42865 | 0.42915 | 0.35271 | 0.47261 | 0.44319 | 0.42766
42838.4191 | -106 | 22.8985 | 22.865 | 22.8529 | 22.7691 | 22.4063 | 21.7402 | 22.7156 | 21.7984 | 22.3615 | 22.3778 | 22.3515 | 22.0191 | 21.2318 | 22.2058 | 21.5921 | 21.7707 | 21.8915 | 21.0816 | 21.1784 | 21.3941 | 20.4777 | 20.6107 | 20.8983 | 21.8829 | 21.6436 | 21.2757 | 20.3288 | 20.3826 | 20.5567 | 22.0741 | 21.671 | 21.1891 | 21.9978 | 21.7442 | 21.35 | 19.9088 | 20.516 |  | 20.4981 | 20.0438 | 20.0959 | 19.0339 |  | 17.0268 | 17.0442 | 16.8377 | 17.0922 | 17.0956 | 17.5887 | 18.1415 | 15.6004 | 16.9324 | 16.2421 | 16.9803 | 18.0049 | 46.0397 | 51.579 | 44.8406 | 21.4059 |  |  | 0.3485 | -0.026349 | -93.1397 | 1.1591 | 0.16704 | -197.8223 | 2.2831 | -0.54577 | 0.14857 | -0.24682 | -0.27434 | 8.8279 | 9.0577 | 1.9788 | 21.7724 | 22.0034 | 22.1888 | 22.2579 | 22.0754 | 21.3954 | 20.2072 | 22.1974 | 22.369 | 22.4038 | 22.3582 | 21.9822 | 21.2131 | 22.2715 | 17.5588 | 17.1908 | 16.2849 | 16.3198 | 16.3075 | 17.1426 | 16.9324 | 22.3733 | 22.1409 | 21.6958 | 22.0797 | 21.8011 | 21.2972 | 21.9461 | 21.5252 | 20.9031 | 20.0763 | 20.3464 | 19.9101 | 19.7804 | -0.067028 | -0.17705 | 20.6985 | 22.0621 | 22.3642 | 20.1134 | 21.6568 | 22.1008 | 21.9348 | 21.7024 | 21.2675 | 21.763 | 21.4352 | 21.0289 | 20.2265 | 20.437 | 20.2854 | 20.263 | 19.9717 |  | 20.2056 | 19.8024 | 20.1298 | 19.728 | 20.0761 | 20.3231 |  | 20.3874 |  |  | 20.229 | 20.1633 | 20.535 | [5 empty] | 21.9115 | 20.3373 | 21.6507 | 22.0269 | 19.5425 | 21.1462 | 21.7682 | 19.3546 | 19.9397 | 21.4258 |  | 19.7373 | 20.8683 | 18.8686 | 19.6878 | 20.7669 | 19.3694 | 20.1627 | 19.0852 | 20.0724 | 19.1593 | 20.1109 | 18.8067 | 20.0806 | 20.9942 | 19.4415 | 19.7399 | 20.9976 | 18.9007 | 19.7482 | 20.7565 | 18.8671 | 20.0647 | 19.3125 | 19.9855 | 18.9706 | 20.0292 | -0.12163 | 20.9458 | 0.047252 | 0.015834 | -27.0529 | 3.096 | -7.8 | -0.01 | 0.70506 | -0.19271 | -11.4572 | 1.2781 | 0.48566 | -16.7131 | 1.7955 | 0.42641 | 0.42858 | 0.42884 | 0.35641 | 0.47343 | 0.44252 | 0.4274
42838.4191 | -105 | 22.8984 | 22.8648 | 22.8519 | 22.7791 | 22.4103 | 21.7456 | 22.7182 | 21.8008 | 22.3735 | 22.3812 | 22.356 | 22.026 | 21.2412 | 22.2019 | 21.5938 | 21.7659 | 21.8848 | 21.0851 | 21.1826 | 21.3891 | 20.4756 | 20.6151 | 20.902 | 21.8845 | 21.6425 | 21.2698 | 20.3359 | 20.3864 | 20.5533 | 22.0764 | 21.6726 | 21.1833 | 21.9993 | 21.7372 | 21.3502 | 19.9091 | 20.5117 |  | 20.4985 | 20.0486 | 20.1089 | 19.0394 |  | 17.0346 | 17.0544 | 16.8431 | 17.1021 | 17.1132 | 17.5813 | 18.1024 | 15.5553 | 16.9265 | 16.1491 | 16.9747 | 17.9995 | 46.1882 | 51.5112 | 44.9715 | 21.4141 |  |  | 0.33536 | -0.22677 | -93.2022 | 0.66364 | 0.22618 | -197.7875 | 1.5944 | -0.44851 | 0.10498 | -0.26738 | -0.075225 | 8.8287 | 9.0585 | 1.979 | 21.7868 | 22.0096 | 22.1983 | 22.2529 | 22.0805 | 21.4036 | 20.2085 | 22.193 | 22.3739 | 22.4064 | 22.3569 | 21.9855 | 21.2207 | 22.273 | 17.5096 | 17.1764 | 16.2446 | 16.3225 | 16.3102 | 17.1373 | 16.9235 | 22.3674 | 22.1355 | 21.6924 | 22.0776 | 21.7966 | 21.2947 | 21.9392 | 21.5205 | 20.9003 | 20.0786 | 20.3598 | 19.9001 | 19.7718 | -0.1323 | -0.15898 | 20.7065 | 22.0659 | 22.3659 | 20.1179 | 21.6645 | 22.1033 | 21.937 | 21.7013 | 21.2698 | 21.7676 | 21.4364 | 21.0345 | 20.2118 | 20.4629 | 20.2896 | 20.264 | 19.9688 |  | 20.2072 | 19.8212 | 20.1293 | 19.7443 | 20.0837 | 20.3287 |  | 20.3854 |  |  | 20.2318 | 20.1754 | 20.5387 | [5 empty] | 21.9174 | 20.3403 | 21.6509 | 22.0296 | 19.547 | 21.1566 | 21.7713 | 19.3533 | 19.9371 | 21.4386 |  | 19.7252 | 20.8652 | 18.8667 | 19.6891 | 20.7577 | 19.3669 | 20.1538 | 19.0842 | 20.0622 | 19.1508 | 20.1159 | 18.808 | 20.072 | 20.9933 | 19.437 | 19.7422 | 21.0066 | 18.9007 | 19.7458 | 20.7583 | 18.85 | 20.0643 | 19.3149 | 19.9995 | 18.9672 | 20.0326 | -0.42994 | 20.9459 | 0.04727 | 0.0155 | -27.0974 | 3.096 | -2.5 | -0.06 | 0.69163 | -0.56534 | -11.4612 | 0.96713 | 0.56512 | -16.7114 | 1.5004 | 0.42655 | 0.42804 | 0.42864 | 0.36125 | 0.47687 | 0.44238 | 0.42771
42838.4191 | -104 | 22.9128 | 22.874 | 22.8602 | 22.7825 | 22.4132 | 21.7574 | 22.7229 | 21.8068 | 22.3798 | 22.3857 | 22.3655 | 22.0247 | 21.246 | 22.2173 | 21.6017 | 21.7677 | 21.8985 | 21.0821 | 21.181 | 21.3953 | 20.4831 | 20.6256 | 20.9065 | 21.8849 | 21.6523 | 21.2691 | 20.3463 | 20.3914 | 20.5522 | 22.0812 | 21.6809 | 21.1962 | 22.0071 | 21.736 | 21.3555 | 19.915 | 20.5212 |  | 20.5018 | 20.0568 | 20.1125 | 19.0503 |  | 17.0524 | 17.079 | 16.8561 | 17.1067 | 17.1123 | 17.5739 | 18.0547 | 15.5296 | 16.9255 | 16.1211 | 16.9784 | 18.0017 | 46.3202 | 51.4427 | 45.1022 | 21.3981 |  |  | 0.4727 | -0.11046 | -93.3802 | 0.72935 | 0.17032 | -197.8552 | 1.8356 | -0.38543 | 0.16531 | -0.23424 | 0.084834 | 8.8285 | 9.0583 | 1.9786 | 21.7758 | 21.9964 | 22.1919 | 22.2482 | 22.0824 | 21.3979 | 20.2025 | 22.1918 | 22.3718 | 22.4065 | 22.3566 | 21.9803 | 21.2096 | 22.2684 | 17.473 | 17.187 | 16.2413 | 16.3308 | 16.3349 | 17.1386 | 16.9242 | 22.3729 | 22.1413 | 21.6954 | 22.0824 | 21.7928 | 21.3013 | 21.949 | 21.5246 | 20.9033 | 20.0771 | 20.3986 | 19.9028 | 19.7761 | 0.038742 | -0.14205 | 20.7143 | 22.0662 | 22.366 | 20.1269 | 21.6664 | 22.1065 | 21.9381 | 21.7052 | 21.2725 | 21.7745 | 21.4392 | 21.0367 | 20.2042 | 20.4804 | 20.2956 | 20.2697 | 19.9774 |  | 20.208 | 19.824 | 20.127 | 19.7539 | 20.0804 | 20.3216 |  | 20.3954 |  |  | 20.2374 | 20.1731 | 20.5391 | [5 empty] | 21.9191 | 20.3363 | 21.6499 | 22.0294 | 19.5483 | 21.1495 | 21.7674 | 19.352 | 19.9326 | 21.4596 |  | 19.7214 | 20.8629 | 18.8728 | 19.6882 | 20.7574 | 19.373 | 20.157 | 19.0846 | 20.0563 | 19.1602 | 20.1172 | 18.8025 | 20.0671 | 20.99 | 19.4387 | 19.748 | 21.0127 | 18.8993 | 19.7423 | 20.7599 | 18.8421 | 20.0691 | 19.3139 | 20.0198 | 18.9693 | 20.0322 | -0.24407 | 20.9456 | 0.047209 | 0.015246 | -26.9945 | 3.0959 | -8.44 | -0.09 | 0.82113 | -0.39459 | -11.4727 | 1.0139 | 0.49039 | -16.714 | 1.6099 | 0.42633 | 0.42788 | 0.42827 | 0.36546 | 0.47732 | 0.44227 | 0.42754
42838.4191 | -103 | 22.9087 | 22.8739 | 22.8567 | 22.7772 | 22.4067 | 21.7475 | 22.7187 | 21.8041 | 22.3738 | 22.3844 | 22.3589 | 22.0246 | 21.2379 | 22.2188 | 21.6036 | 21.7625 | 21.8934 | 21.0859 | 21.1841 | 21.3941 | 20.4748 | 20.621 | 20.907 | 21.8838 | 21.6457 | 21.2697 | 20.3448 | 20.3839 | 20.5485 | 22.0852 | 21.6763 | 21.196 | 22.0106 | 21.7421 | 21.3584 | 19.9155 | 20.5285 |  | 20.5068 | 20.0599 | 20.1068 | 19.0531 |  | 17.0763 | 17.1128 | 16.8697 | 17.1059 | 17.1015 | 17.5546 | 18.0113 | 15.5167 | 16.9319 | 16.1076 | 16.9829 | 18.0088 | 46.4507 | 51.3661 | 45.2312 | 21.4011 |  |  | 0.53512 | -0.23071 | -93.4361 | 0.43562 | 0.15784 | -197.8184 | 1.3894 | -0.24021 | -0.14955 | -0.15074 | -0.0014448 | 8.8287 | 9.0584 | 1.9789 | 21.7703 | 21.9939 | 22.187 | 22.2493 | 22.0802 | 21.3866 | 20.2085 | 22.1948 | 22.3661 | 22.4054 | 22.3635 | 21.9804 | 21.2048 | 22.275 | 17.4371 | 17.2094 | 16.2559 | 16.335 | 16.3418 | 17.1356 | 16.9245 | 22.3729 | 22.1355 | 21.6967 | 22.0761 | 21.7964 | 21.2968 | 21.9459 | 21.5242 | 20.8952 | 20.0734 | 20.418 | 19.8969 | 19.7816 | -0.059164 | -0.26416 | 20.7267 | 22.0721 | 22.3715 | 20.1344 | 21.6652 | 22.112 | 21.9484 | 21.7127 | 21.2761 | 21.7768 | 21.4403 | 21.0438 | 20.189 | 20.4946 | 20.2985 | 20.2781 | 20.0065 |  | 20.2017 | 19.8129 | 20.1228 | 19.7661 | 20.0801 | 20.3281 |  | 20.3988 |  |  | 20.2475 | 20.1834 | 20.5397 | [5 empty] | 21.9155 | 20.3335 | 21.657 | 22.0301 | 19.5535 | 21.1512 | 21.7716 | 19.3605 | 19.9433 | 21.4915 |  | 19.7207 | 20.8725 | 18.8748 | 19.698 | 20.7645 | 19.3709 | 20.1479 | 19.0838 | 20.046 | 19.1695 | 20.1193 | 18.8123 | 20.0834 | 21.0011 | 19.4555 | 19.7611 | 21.0399 | 18.9109 | 19.7614 | 20.7706 | 18.8434 | 20.0792 | 19.325 | 20.0359 | 18.9799 | 20.0431 | -0.20418 | 20.9469 | 0.047645 | 0.015602 | -27.0209 | 3.096 | -8.33 | -0.08 | 0.87366 | -0.57029 | -11.4768 | 0.78364 | 0.47206 | -16.7119 | 1.4006 | 0.42531 | 0.42805 | 0.42792 | 0.36911 | 0.47573 | 0.44221 | 0.42726
42838.4191 | -102 | 22.9059 | 22.8698 | 22.8518 | 22.7788 | 22.4035 | 21.7399 | 22.7207 | 21.7986 | 22.3728 | 22.3818 | 22.3467 | 22.0167 | 21.2374 | 22.2062 | 21.6019 | 21.7794 | 21.9006 | 21.0856 | 21.1817 | 21.3988 | 20.4798 | 20.6169 | 20.9092 | 21.8897 | 21.65 | 21.2719 | 20.3531 | 20.3895 | 20.5509 | 22.0761 | 21.6716 | 21.1865 | 22.0042 | 21.7348 | 21.3578 | 19.9106 | 20.5211 |  | 20.5006 | 20.0459 | 20.1063 | 19.0514 |  | 17.086 | 17.1184 | 16.8708 | 17.1081 | 17.0951 | 17.5376 | 17.9816 | 15.5357 | 16.9384 | 16.0383 | 16.9836 | 18.0047 | 46.5792 | 51.2799 | 45.3199 | 21.4055 |  |  | 0.38004 | -0.069721 | -93.4295 | 0.64524 | 0.24589 | -197.8079 | 1.942 | -0.20144 | 0.071706 | -0.11129 | -0.023839 | 8.8284 | 9.0584 | 1.9786 | 21.7884 | 22.01 | 22.2022 | 22.2659 | 22.0908 | 21.4018 | 20.2147 | 22.2058 | 22.381 | 22.4112 | 22.3703 | 21.9868 | 21.2176 | 22.2803 | 17.4037 | 17.2417 | 16.272 | 16.3312 | 16.3432 | 17.1412 | 16.9225 | 22.3691 | 22.1326 | 21.6969 | 22.0808 | 21.7904 | 21.2998 | 21.9383 | 21.526 | 20.8984 | 20.0765 | 20.4381 | 19.9056 | 19.7928 | -0.14134 | -0.050562 | 20.7306 | 22.076 | 22.3745 | 20.137 | 21.6613 | 22.1122 | 21.952 | 21.7114 | 21.2759 | 21.7769 | 21.4445 | 21.0439 | 20.1721 | 20.5293 | 20.2976 | 20.2815 | 20.0297 |  | 20.2097 | 19.815 | 20.1275 | 19.7733 | 20.0734 | 20.3222 |  | 20.3856 |  |  | 20.2611 | 20.1848 | 20.5428 | [5 empty] | 21.9187 | 20.3402 | 21.6603 | 22.0359 | 19.5402 | 21.1566 | 21.7649 | 19.3601 | 19.9452 | 21.5322 |  | 19.7076 | 20.8572 | 18.8719 | 19.7128 | 20.7699 | 19.3758 | 20.1431 | 19.0764 | 20.0418 | 19.1616 | 20.1266 | 18.8157 | 20.075 | 20.9984 | 19.4386 | 19.7503 | 21.0439 | 18.9052 | 19.7554 | 20.7667 | 18.8357 | 20.0731 | 19.3163 | 20.0557 | 18.9775 | 20.0464 | -0.12831 | 20.9454 | 0.048106 | 0.015602 | -27.0819 | 3.096 | -18.77 | -0.02 | 0.73627 | -0.31351 | -11.4765 | 0.95374 | 0.58919 | -16.711 | 1.6558 | 0.42494 | 0.42815 | 0.42749 | 0.37347 | 0.47371 | 0.4421 | 0.42706
42838.4191 | -101 | 22.9061 | 22.8708 | 22.8601 | 22.7793 | 22.4035 | 21.7407 | 22.7207 | 21.8009 | 22.3677 | 22.386 | 22.3583 | 22.0202 | 21.2348 | 22.2099 | 21.6028 | 21.7698 | 21.9048 | 21.0824 | 21.1822 | 21.404 | 20.4819 | 20.6191 | 20.9111 | 21.8908 | 21.6468 | 21.2759 | 20.3567 | 20.392 | 20.555 | 22.0812 | 21.677 | 21.1898 | 21.9962 | 21.7421 | 21.3575 | 19.9121 | 20.5227 |  | 20.5035 | 20.0527 | 20.1114 | 19.0558 |  | 17.0956 | 17.1218 | 16.876 | 17.0917 | 17.0793 | 17.5024 | 17.9494 | 15.5306 | 16.9319 | 15.9396 | 16.9863 | 18.0076 | 46.6913 | 51.1953 | 45.4184 | 21.4019 |  |  | 0.54827 | -0.38119 | -93.1075 | 0.86406 | 0.18478 | -197.8296 | 2.7168 | -0.25204 | 0.054387 | -0.36012 | -0.1004 | 8.8286 | 9.0585 | 1.9784 | 21.7751 | 22.0044 | 22.1936 | 22.2546 | 22.0763 | 21.3933 | 20.206 | 22.1941 | 22.3743 | 22.4061 | 22.3568 | 21.9812 | 21.216 | 22.2681 | 17.3758 | 17.246 | 16.2856 | 16.3282 | 16.3444 | 17.1396 | 16.9245 | 22.372 | 22.1374 | 21.6976 | 22.0781 | 21.8034 | 21.3003 | 21.9476 | 21.5349 | 20.9088 | 20.0794 | 20.4398 | 19.9074 | 19.7986 | -0.27995 | -0.16088 | 20.7264 | 22.067 | 22.3726 | 20.1326 | 21.659 | 22.1081 | 21.9423 | 21.7099 | 21.2701 | 21.7731 | 21.4421 | 21.0368 | 20.1516 | 20.5557 | 20.2935 | 20.2728 | 20.0559 |  | 20.2035 | 19.8033 | 20.1245 | 19.7784 | 20.0752 | 20.3268 |  | 20.3779 |  |  | 20.2646 | 20.1971 | 20.5486 | [5 empty] | 21.9211 | 20.3435 | 21.6572 | 22.0348 | 19.5399 | 21.1519 | 21.7746 | 19.3652 | 19.946 | 21.574 |  | 19.7047 | 20.8661 | 18.8812 | 19.7149 | 20.7713 | 19.3675 | 20.1365 | 19.0787 | 20.0376 | 19.1572 | 20.1318 | 18.8 | 20.0668 | 21.0041 | 19.4465 | 19.7583 | 21.057 | 18.8998 | 19.7603 | 20.7637 | 18.8166 | 20.0726 | 19.3155 | 20.0561 | 18.9708 | 20.0415 | -0.002915 | 20.947 | 0.048739 | 0.016045 | -27.0531 | 3.0959 | -6 | -0.13 | 0.88434 | -0.73306 | -11.4568 | 1.1037 | 0.51072 | -16.7109 | 1.9583 | 0.424 | 0.42837 | 0.42741 | 0.37639 | 0.47244 | 0.44202 | 0.42699
42838.4191 | -100 | 22.9049 | 22.8711 | 22.859 | 22.7821 | 22.4036 | 21.7403 | 22.7208 | 21.8005 | 22.3733 | 22.3795 | 22.3585 | 22.0266 | 21.2374 | 22.2108 | 21.602 | 21.772 | 21.9027 | 21.0884 | 21.1944 | 21.4098 | 20.4855 | 20.6194 | 20.9126 | 21.8871 | 21.6469 | 21.285 | 20.3591 | 20.3951 | 20.5538 | 22.0737 | 21.6752 | 21.1954 | 22.0022 | 21.7344 | 21.3483 | 19.9116 | 20.5202 |  | 20.4943 | 20.0494 | 20.1043 | 19.061 |  | 17.097 | 17.1462 | 16.8702 | 17.101 | 17.0734 | 17.5083 | 17.9758 | 15.5288 | 16.9396 | 15.928 | 16.987 | 18.0066 | 46.8025 | 51.1038 | 45.5161 | 21.4023 |  |  | 0.35901 | -0.62367 | -93.5938 | 0.49805 | 0.47128 | -197.8236 | -0.073335 | -0.21918 | 0.078712 | 0.012489 | -0.16897 | 8.8294 | 9.0594 | 1.9784 | 21.7688 | 21.9965 | 22.1929 | 22.2539 | 22.0779 | 21.3965 | 20.2019 | 22.1925 | 22.3727 | 22.4103 | 22.3512 | 21.9865 | 21.2164 | 22.2705 | 17.3569 | 17.2416 | 16.2859 | 16.3243 | 16.3378 | 17.1386 | 16.9222 | 22.3659 | 22.1345 | 21.6913 | 22.0776 | 21.7898 | 21.2984 | 21.9414 | 21.5215 | 20.8983 | 20.0668 | 20.4469 | 19.8913 | 19.8029 | -0.2249 | -0.036678 | 20.7211 | 22.0643 | 22.3676 | 20.1253 | 21.6619 | 22.1049 | 21.9357 | 21.7059 | 21.2705 | 21.7738 | 21.4426 | 21.0376 | 20.1451 | 20.5814 | 20.2955 | 20.2744 | 20.0784 |  | 20.2028 | 19.7985 | 20.1276 | 19.7913 | 20.0801 | 20.336 |  | 20.3941 |  |  | 20.2574 | 20.1951 | 20.5462 | [5 empty] | 21.9118 | 20.3383 | 21.6471 | 22.0219 | 19.5327 | 21.1453 | 21.7632 | 19.3763 | 19.9514 | 21.6328 |  | 19.7079 | 20.8786 | 18.8945 | 19.7263 | 20.795 | 19.3843 | 20.1492 | 19.0839 | 20.0334 | 19.1666 | 20.1572 | 18.8008 | 20.0582 | 21.0011 | 19.4449 | 19.7647 | 21.0763 | 18.8971 | 19.7611 | 20.7593 | 18.816 | 20.0769 | 19.3206 | 20.0612 | 18.9821 | 20.0425 | -0.15521 | 20.9443 | 0.048807 | 0.016379 | -27.0218 | 3.0959 | -12.69 | -0.07 | 0.71561 | -0.9377 | -11.4871 | 0.83796 | 0.81564 | -16.7108 | -0.32175 | 0.42335 | 0.42861 | 0.42722 | 0.37837 | 0.47213 | 0.44186 | 0.42645
42838.4191 | -99 | 22.9161 | 22.871 | 22.8667 | 22.7805 | 22.4128 | 21.7466 | 22.7221 | 21.8029 | 22.3708 | 22.3811 | 22.3667 | 22.0205 | 21.2409 | 22.2118 | 21.6091 | 21.7726 | 21.8974 | 21.0898 | 21.1767 | 21.3987 | 20.474 | 20.6116 | 20.8976 | 21.8847 | 21.652 | 21.2806 | 20.3641 | 20.3895 | 20.5686 | 22.0765 | 21.6735 | 21.1862 | 22.0015 | 21.73 | 21.3536 | 19.9118 | 20.5157 |  | 20.5026 | 20.0514 | 20.1005 | 19.064 |  | 17.1172 | 17.1416 | 16.874 | 17.0894 | 17.0831 | 17.5505 | 18.0102 | 15.5213 | 16.935 | 15.9738 | 16.9906 | 18.004 | 46.9015 | 51.0122 | 45.5889 | 21.397 |  |  | 0.35047 | -0.34834 | -94.1517 | 0.71424 | 0.49757 | -197.823 | 0.92483 | -0.10156 | -0.07833 | -0.013736 | 0.0002912 | 8.8288 | 9.0586 | 1.9786 | 21.7773 | 21.9984 | 22.1939 | 22.2575 | 22.0839 | 21.4009 | 20.2036 | 22.1956 | 22.3753 | 22.4148 | 22.3567 | 21.9846 | 21.2205 | 22.2709 | 17.3311 | 17.2241 | 16.2651 | 16.2853 | 16.3197 | 17.1417 | 16.9206 | 22.3753 | 22.1346 | 21.6961 | 22.0806 | 21.7991 | 21.2989 | 21.9469 | 21.526 | 20.8995 | 20.072 | 20.4543 | 19.8978 | 19.8178 | -0.2652 | 0.010302 | 20.7239 | 22.0714 | 22.367 | 20.1222 | 21.662 | 22.1097 | 21.9423 | 21.7068 | 21.2751 | 21.7752 | 21.4453 | 21.0368 | 20.1361 | 20.5997 | 20.3005 | 20.2802 | 20.0969 |  | 20.2101 | 19.7892 | 20.1322 | 19.797 | 20.0832 | 20.343 |  | 20.3948 |  |  | 20.265 | 20.2182 | 20.5519 | [5 empty] | 21.9188 | 20.3483 | 21.658 | 22.0331 | 19.5571 | 21.1527 | 21.773 | 19.366 | 19.9406 | 21.665 |  | 19.6898 | 20.8536 | 18.8797 | 19.7171 | 20.7859 | 19.3655 | 20.1323 | 19.0662 | 20.0282 | 19.1501 | 20.1419 | 18.7939 | 20.0582 | 21.0044 | 19.4485 | 19.748 | 21.0875 | 18.8939 | 19.7632 | 20.7536 | 18.7995 | 20.0694 | 19.31 | 20.0607 | 18.9755 | 20.0474 | -0.1682 | 20.9464 | 0.048948 | 0.01619 | -27.041 | 3.0959 | -13.43 | -0.18 | 0.70707 | -0.70078 | -11.5212 | 1.0035 | 0.83814 | -16.712 | 1.1427 | 0.42308 | 0.42902 | 0.42716 | 0.38159 | 0.47425 | 0.44179 | 0.42621
42838.4191 | -98 | 22.9065 | 22.8709 | 22.855 | 22.772 | 22.4085 | 21.7442 | 22.72 | 21.8016 | 22.3648 | 22.3793 | 22.3533 | 22.0184 | 21.2332 | 22.2103 | 21.6002 | 21.7688 | 21.8999 | 21.0839 | 21.1763 | 21.3916 | 20.477 | 20.6188 | 20.9067 | 21.8748 | 21.6421 | 21.2727 | 20.3779 | 20.3919 | 20.6217 | 22.0784 | 21.6775 | 21.1947 | 22.0071 | 21.7358 | 21.3543 | 19.9142 | 20.5266 |  | 20.5124 | 20.057 | 20.1088 | 19.0652 |  | 17.1133 | 17.1404 | 16.8871 | 17.0798 | 17.0529 | 17.4888 | 17.93 | 15.5188 | 16.9407 | 16.0096 | 16.987 | 18.0099 | 46.9977 | 50.9202 | 45.6688 | 21.3954 |  |  | 0.4175 | -0.083521 | -94.8817 | 0.52499 | 0.37666 | -197.8466 | 0.81115 | -0.12061 | 0.040765 | -0.066395 | 0.0002912 | 8.8288 | 9.0585 | 1.9783 | 21.7864 | 22.0046 | 22.1962 | 22.2594 | 22.0867 | 21.405 | 20.2185 | 22.2073 | 22.3832 | 22.4111 | 22.3623 | 21.9888 | 21.2192 | 22.2727 | 17.3238 | 17.2337 | 16.2259 | 16.2598 | 16.3262 | 17.1349 | 16.9244 | 22.374 | 22.1349 | 21.7007 | 22.0793 | 21.7947 | 21.2939 | 21.9448 | 21.5312 | 20.9003 | 20.0771 | 20.4612 | 19.8973 | 19.8181 | -0.044223 | -0.26302 | 20.7193 | 22.0744 | 22.3667 | 20.1229 | 21.6618 | 22.1134 | 21.9447 | 21.7089 | 21.2751 | 21.7754 | 21.4464 | 21.0381 | 20.1333 | 20.6097 | 20.3038 | 20.2796 | 20.1119 |  | 20.2094 | 19.7551 | 20.1281 | 19.8003 | 20.0781 | 20.3418 |  | 20.3841 |  |  | 20.2717 | 20.2237 | 20.5668 | [5 empty] | 21.9121 | 20.3514 | 21.6509 | 22.0293 | 19.546 | 21.1535 | 21.7672 | 19.3831 | 19.9577 | 21.6994 |  | 19.7015 | 20.8761 | 18.8905 | 19.7292 | 20.8102 | 19.3806 | 20.1501 | 19.0769 | 20.0394 | 19.1554 | 20.1668 | 18.793 | 20.0531 | 21.0018 | 19.4595 | 19.7524 | 21.1081 | 18.8949 | 19.7637 | 20.7611 | 18.7966 | 20.0662 | 19.311 | 20.0565 | 18.977 | 20.0452 | -0.10271 | 20.9477 | 0.04885 | 0.015529 | -27.0695 | 3.0959 | -14.09 | -0.16 | 0.77179 | -0.34315 | -11.5658 | 0.86032 | 0.72915 | -16.7112 | 1.07 | 0.42264 | 0.42983 | 0.4269 | 0.38161 | 0.47905 | 0.44183 | 0.42637
42838.4192 | -97 | 22.9012 | 22.8609 | 22.8551 | 22.771 | 22.4055 | 21.7381 | 22.7189 | 21.7962 | 22.3643 | 22.3729 | 22.3519 | 22.0218 | 21.2339 | 22.2068 | 21.5997 | 21.7601 | 21.8928 | 21.0814 | 21.1805 | 21.3893 | 20.4744 | 20.6127 | 20.9091 | 21.8759 | 21.6423 | 21.268 | 20.3957 | 20.3892 | 20.6592 | 22.077 | 21.678 | 21.1933 | 21.996 | 21.7394 | 21.3518 | 19.9133 | 20.5277 |  | 20.5054 | 20.0537 | 20.1104 | 19.0659 |  | 17.1172 | 17.1362 | 16.8987 | 17.0713 | 17.0507 | 17.4675 | 17.9247 | 15.5374 | 16.9387 | 16.0345 | 16.9905 | 18.0014 | 47.0762 | 50.7991 | 45.7391 | 21.3911 |  |  | 0.39056 | -0.36082 | -94.1129 | 0.44482 | 0.422 | -197.8453 | -0.85268 | -0.13836 | -0.0073014 | -0.017932 | -0.049011 | 8.8285 | 9.0585 | 1.9786 | 21.7862 | 22.0104 | 22.196 | 22.2551 | 22.0855 | 21.4081 | 20.2148 | 22.1926 | 22.3695 | 22.4069 | 22.3562 | 21.9929 | 21.2232 | 22.2716 | 17.3078 | 17.2068 | 16.2061 | 16.2512 | 16.3133 | 17.1361 | 16.9257 | 22.3644 | 22.1343 | 21.6982 | 22.0755 | 21.7934 | 21.2933 | 21.9391 | 21.5219 | 20.8947 | 20.0674 | 20.4623 | 19.88 | 19.8182 | 0.030878 | -0.054937 | 20.7144 | 22.0718 | 22.3679 | 20.1328 | 21.6653 | 22.1096 | 21.9444 | 21.7139 | 21.2748 | 21.7821 | 21.4493 | 21.0401 | 20.1442 | 20.6224 | 20.3088 | 20.283 | 20.126 |  | 20.2133 | 19.7154 | 20.1242 | 19.7976 | 20.0758 | 20.3415 |  | 20.3886 |  |  | 20.2722 | 20.237 | 20.5669 | [5 empty] | 21.9173 | 20.3385 | 21.6529 | 22.0289 | 19.5533 | 21.1421 | 21.7661 | 19.389 | 19.9546 | 21.7015 |  | 19.6951 | 20.8763 | 18.8975 | 19.7399 | 20.8166 | 19.3855 | 20.1452 | 19.078 | 20.0356 | 19.1627 | 20.1758 | 18.7981 | 20.0532 | 21.0029 | 19.4545 | 19.7605 | 21.1218 | 18.8947 | 19.761 | 20.7627 | 18.8015 | 20.0696 | 19.3023 | 20.0584 | 18.9717 | 20.0466 | -0.09956 | 20.9475 | 0.048493 | 0.015108 | -27.1523 | 3.0959 | 1.81 | -0.2 | 0.74652 | -0.71322 | -11.5187 | 0.79191 | 0.77176 | -16.7106 | -1.097 | 0.42238 | 0.4308 | 0.4269 | 0.38354 | 0.48141 | 0.44178 | 0.42604
42838.4192 | -96 | 22.9014 | 22.8703 | 22.8562 | 22.7728 | 22.4044 | 21.746 | 22.7194 | 21.7979 | 22.3718 | 22.3751 | 22.3578 | 22.0209 | 21.2371 | 22.2034 | 21.5947 | 21.7681 | 21.89 | 21.078 | 21.1765 | 21.3863 | 20.4748 | 20.6065 | 20.8996 | 21.8753 | 21.6424 | 21.2658 | 20.4107 | 20.3971 | 20.6914 | 22.0755 | 21.6815 | 21.1925 | 22.0002 | 21.7378 | 21.3558 | 19.914 | 20.5201 |  | 20.5046 | 20.0546 | 20.1067 | 19.0638 |  | 17.1438 | 17.144 | 16.8897 | 17.0568 | 17.0424 | 17.4732 | 17.949 | 15.6332 | 16.9424 | 16.0766 | 16.9851 | 18.0075 | 47.1538 | 50.7049 | 45.8126 | 21.3921 |  |  | 0.44773 | -0.23663 | -93.5846 | 0.31406 | 0.15981 | -197.8545 | -2.0861 | -0.1791 | -0.10849 | -0.10857 | -0.024881 | 8.8289 | 9.0588 | 1.9787 | 21.7744 | 22.0001 | 22.1885 | 22.2668 | 22.0755 | 21.3988 | 20.207 | 22.197 | 22.3669 | 22.4048 | 22.3611 | 21.9813 | 21.209 | 22.27 | 17.3013 | 17.2043 | 16.1944 | 16.2556 | 16.3096 | 17.1432 | 16.9287 | 22.3644 | 22.1306 | 21.6936 | 22.0773 | 21.7983 | 21.2914 | 21.9388 | 21.5287 | 20.9011 | 20.0677 | 20.45 | 19.8802 | 19.8236 | -0.069584 | -0.25864 | 20.7159 | 22.0708 | 22.3717 | 20.1336 | 21.6629 | 22.1081 | 21.9486 | 21.7149 | 21.2811 | 21.7813 | 21.4468 | 21.0414 | 20.1544 | 20.6282 | 20.3039 | 20.2869 | 20.1411 |  | 20.1992 | 19.7012 | 20.118 | 19.8002 | 20.0706 | 20.3334 |  | 20.3903 |  |  | 20.2798 | 20.2482 | 20.5759 | [5 empty] | 21.9211 | 20.3477 | 21.6506 | 22.0242 | 19.56 | 21.1507 | 21.7671 | 19.4016 | 19.9611 | 21.7233 |  | 19.7058 | 20.8748 | 18.9008 | 19.7475 | 20.8286 | 19.3941 | 20.1453 | 19.077 | 20.037 | 19.1651 | 20.1954 | 18.7935 | 20.0602 | 21.005 | 19.4511 | 19.7532 | 21.1367 | 18.8914 | 19.7709 | 20.7711 | 18.8048 | 20.0719 | 19.2998 | 20.0587 | 18.9724 | 20.0632 | -0.12034 | 20.9453 | 0.049015 | 0.015101 | -27.0601 | 3.0958 | -14.54 | -0.17 | 0.79934 | -0.57759 | -11.4865 | 0.66541 | 0.47494 | -16.7111 | -1.7159 | 0.42149 | 0.43099 | 0.42665 | 0.38508 | 0.48305 | 0.44187 | 0.42591
42838.4192 | -95 | 22.8938 | 22.8598 | 22.8576 | 22.7703 | 22.4008 | 21.7444 | 22.7164 | 21.7935 | 22.3657 | 22.3724 | 22.3481 | 22.0208 | 21.2362 | 22.1995 | 21.5952 | 21.7586 | 21.8894 | 21.082 | 21.1818 | 21.3993 | 20.4734 | 20.6087 | 20.9012 | 21.8754 | 21.6379 | 21.2738 | 20.4178 | 20.3959 | 20.7059 | 22.0716 | 21.6705 | 21.1903 | 22.0015 | 21.7365 | 21.3514 | 19.9162 | 20.5139 |  | 20.5055 | 20.0542 | 20.094 | 19.0578 |  | 17.1359 | 17.1454 | 16.8739 | 17.0454 | 17.0538 | 17.442 | 17.9309 | 15.7056 | 16.9372 | 16.126 | 16.9885 | 18.0073 | 47.2062 | 50.6041 | 45.8743 | 21.3928 |  |  | 0.42275 | -0.19128 | -92.9728 | 0.57822 | 0.24786 | -197.8499 | -2.4981 | -0.34206 | -0.023842 | 0.047736 | 0.015047 | 8.8288 | 9.0586 | 1.9792 | 21.7692 | 21.9975 | 22.1862 | 22.2509 | 22.0744 | 21.3978 | 20.2058 | 22.1929 | 22.366 | 22.4001 | 22.3501 | 21.972 | 21.2066 | 22.2658 | 17.274 | 17.1638 | 16.186 | 16.2563 | 16.2953 | 17.1364 | 16.9183 | 22.3691 | 22.1385 | 21.6945 | 22.0821 | 21.7962 | 21.2991 | 21.9352 | 21.523 | 20.8976 | 20.0773 | 20.4503 | 19.8803 | 19.8247 | -0.011194 | -0.0041534 | 20.7135 | 22.0735 | 22.3709 | 20.1321 | 21.6616 | 22.107 | 21.944 | 21.7108 | 21.2749 | 21.776 | 21.4438 | 21.0362 | 20.1635 | 20.6335 | 20.2998 | 20.2886 | 20.1513 |  | 20.203 | 19.6919 | 20.1242 | 19.7933 | 20.0742 | 20.3356 |  | 20.388 |  |  | 20.2786 | 20.2608 | 20.587 | [5 empty] | 21.9129 | 20.3454 | 21.6458 | 22.0227 | 19.5639 | 21.1489 | 21.7684 | 19.4051 | 19.9659 | 21.7402 |  | 19.7036 | 20.8694 | 18.902 | 19.739 | 20.8387 | 19.395 | 20.1461 | 19.0742 | 20.0373 | 19.1665 | 20.2007 | 18.7919 | 20.0589 | 21.0037 | 19.4549 | 19.7607 | 21.1458 | 18.8866 | 19.7705 | 20.7796 | 18.8135 | 20.0678 | 19.2973 | 20.0682 | 18.9727 | 20.0748 | -0.17784 | 20.9442 | 0.049151 | 0.015558 | -27.1504 | 3.0959 | -21.2 | -0.09 | 0.77674 | -0.51931 | -11.4489 | 0.90289 | 0.59145 | -16.71 | -1.8776 | 0.42133 | 0.43146 | 0.42696 | 0.38732 | 0.48278 | 0.4421 | 0.4262
42838.4192 | -94 | 22.8991 | 22.8532 | 22.8472 | 22.7708 | 22.4013 | 21.734 | 22.7083 | 21.7929 | 22.3576 | 22.3705 | 22.3405 | 22.0138 | 21.2297 | 22.2029 | 21.5978 | 21.7636 | 21.8907 | 21.0792 | 21.1857 | 21.4024 | 20.4736 | 20.6166 | 20.9071 | 21.8854 | 21.6359 | 21.2717 | 20.4257 | 20.4056 | 20.7079 | 22.0728 | 21.6659 | 21.1923 | 21.9927 | 21.7363 | 21.3454 | 19.9098 | 20.5134 |  | 20.5036 | 20.0544 | 20.0878 | 19.0423 |  | 17.1311 | 17.1427 | 16.8648 | 17.0476 | 17.0282 | 17.4352 | 17.9144 | 15.7175 | 16.9398 | 16.1353 | 16.986 | 18.0009 | 47.2666 | 50.5005 | 45.9317 | 21.3915 |  |  | 0.47467 | -0.068405 | -92.0134 | 0.79309 | 0.096728 | -197.8112 | -1.3869 | -0.29672 | -0.14313 | -0.095977 | -0.00266 | 8.8286 | 9.0584 | 1.979 | 21.7732 | 22.0014 | 22.1934 | 22.2536 | 22.0756 | 21.3938 | 20.2057 | 22.1941 | 22.3661 | 22.4049 | 22.3554 | 21.9762 | 21.2074 | 22.2677 | 17.2571 | 17.1254 | 16.1465 | 16.2553 | 16.281 | 17.1281 | 16.913 | 22.3677 | 22.1452 | 21.6957 | 22.0798 | 21.7937 | 21.2981 | 21.9421 | 21.5226 | 20.8979 | 20.0795 | 20.4512 | 19.8702 | 19.8343 | -0.067618 | -0.2925 | 20.7098 | 22.0716 | 22.3669 | 20.1315 | 21.6628 | 22.1065 | 21.9348 | 21.7025 | 21.269 | 21.7737 | 21.4459 | 21.0333 | 20.167 | 20.6394 | 20.3023 | 20.2828 | 20.175 |  | 20.2055 | 19.6787 | 20.1274 | 19.7928 | 20.0803 | 20.3453 |  | 20.3919 |  |  | 20.2899 | 20.2791 | 20.5983 | [5 empty] | 21.9161 | 20.3478 | 21.6477 | 22.0248 | 19.5736 | 21.1535 | 21.7739 | 19.4093 | 19.9672 | 21.7514 |  | 19.7042 | 20.872 | 18.9057 | 19.7409 | 20.8433 | 19.3923 | 20.1418 | 19.074 | 20.0411 | 19.1669 | 20.213 | 18.8049 | 20.0595 | 21.0098 | 19.4574 | 19.7616 | 21.1649 | 18.8909 | 19.773 | 20.7807 | 18.8194 | 20.0704 | 19.2981 | 20.067 | 18.9737 | 20.0822 | -0.14909 | 20.9483 | 0.048764 | 0.014934 | -27.0959 | 3.0959 | 0.19 | -0.09 | 0.82306 | -0.31055 | -11.3897 | 1.0574 | 0.36947 | -16.7082 | -1.399 | 0.42076 | 0.43193 | 0.42718 | 0.38823 | 0.48655 | 0.44232 | 0.426
42838.4192 | -93 | 22.8975 | 22.8563 | 22.8555 | 22.7771 | 22.3973 | 21.7365 | 22.7173 | 21.7923 | 22.3667 | 22.377 | 22.3503 | 22.0198 | 21.2319 | 22.2104 | 21.5955 | 21.7674 | 21.8879 | 21.0757 | 21.1846 | 21.3941 | 20.4737 | 20.6176 | 20.9053 | 21.8906 | 21.6392 | 21.2686 | 20.436 | 20.4105 | 20.7261 | 22.0902 | 21.6774 | 21.2012 | 22.0077 | 21.7461 | 21.3568 | 19.9206 | 20.5393 |  | 20.5151 | 20.065 | 20.1009 | 19.0522 |  | 17.1364 | 17.1403 | 16.8645 | 17.023 | 17.0195 | 17.3994 | 17.8852 | 15.6769 | 16.9479 | 16.1573 | 16.9889 | 18.0142 | 47.3281 | 50.4053 | 45.9692 | 21.4028 |  |  | 0.40567 | -0.054605 | -91.7158 | 0.77667 | 0.4358 | -197.8289 | -4.7001 | -0.33943 | -0.034156 | 0.007664 | 0.053934 | 8.829 | 9.0588 | 1.9787 | 21.7687 | 21.9966 | 22.1919 | 22.2531 | 22.07 | 21.3941 | 20.1979 | 22.1992 | 22.3672 | 22.4049 | 22.3575 | 21.9775 | 21.2136 | 22.2713 | 17.275 | 17.1191 | 16.1429 | 16.262 | 16.3001 | 17.1381 | 16.9246 | 22.3652 | 22.1432 | 21.7 | 22.081 | 21.796 | 21.305 | 21.9397 | 21.5301 | 20.9061 | 20.0757 | 20.4516 | 19.8692 | 19.8381 | 0.022425 | -0.34575 | 20.7105 | 22.0686 | 22.3705 | 20.1303 | 21.6599 | 22.1115 | 21.936 | 21.7003 | 21.2724 | 21.7735 | 21.4438 | 21.0335 | 20.1709 | 20.6425 | 20.2995 | 20.2815 | 20.1869 |  | 20.2069 | 19.6541 | 20.1272 | 19.8098 | 20.0801 | 20.3506 |  | 20.3909 |  |  | 20.2885 | 20.2872 | 20.6037 | [5 empty] | 21.9136 | 20.3459 | 21.6473 | 22.0279 | 19.5746 | 21.1509 | 21.7714 | 19.4112 | 19.966 | 21.7516 |  | 19.7092 | 20.8733 | 18.9063 | 19.7475 | 20.8468 | 19.3909 | 20.1426 | 19.0673 | 20.0341 | 19.1634 | 20.2197 | 18.8078 | 20.0641 | 21.0102 | 19.4569 | 19.7646 | 21.1787 | 18.8926 | 19.7769 | 20.7903 | 18.8386 | 20.0757 | 19.3007 | 20.0806 | 18.9765 | 20.1003 | -0.18841 | 20.9449 | 0.048499 | 0.014905 | -27.1333 | 3.0959 | 3.41 | -0.2 | 0.76091 | -0.27746 | -11.3712 | 1.0464 | 0.78419 | -16.7079 | -2.5753 | 0.42048 | 0.43261 | 0.4267 | 0.38741 | 0.4883 | 0.44241 | 0.42577
42838.4192 | -92 | 22.8958 | 22.8653 | 22.8559 | 22.7788 | 22.4025 | 21.7361 | 22.7112 | 21.7993 | 22.3676 | 22.3783 | 22.3509 | 22.024 | 21.2331 | 22.2163 | 21.5914 | 21.7636 | 21.8864 | 21.0768 | 21.1765 | 21.3844 | 20.4674 | 20.608 | 20.9027 | 21.8774 | 21.6379 | 21.2626 | 20.4452 | 20.411 | 20.7453 | 22.0756 | 21.6737 | 21.1938 | 21.9926 | 21.7344 | 21.3467 | 19.9096 | 20.5565 |  | 20.4974 | 20.0581 | 20.0891 | 19.0448 |  | 17.1365 | 17.1433 | 16.8653 | 17.0239 | 17.0176 | 17.4006 | 17.865 | 15.648 | 16.9461 | 16.1877 | 16.9875 | 18.0044 | 47.3884 | 50.2995 | 46.008 | 21.3854 |  |  | 0.58441 | -0.14332 | -90.9121 | 0.55325 | 0.37666 | -197.8617 | -5.6641 | -0.24152 | 0.13573 | -0.23633 | 0.062614 | 8.8283 | 9.0583 | 1.9787 | 21.7715 | 21.9999 | 22.1889 | 22.2594 | 22.0738 | 21.3914 | 20.2024 | 22.1934 | 22.3721 | 22.4069 | 22.3581 | 21.9806 | 21.2157 | 22.2723 | 17.2736 | 17.1282 | 16.1499 | 16.2668 | 16.3011 | 17.1371 | 16.924 | 22.366 | 22.1327 | 21.6998 | 22.0827 | 21.7942 | 21.3017 | 21.9416 | 21.5314 | 20.9085 | 20.0819 | 20.4526 | 19.8736 | 19.8418 | -0.011194 | -0.28679 | 20.7091 | 22.0684 | 22.3694 | 20.1329 | 21.6525 | 22.108 | 21.9331 | 21.7032 | 21.269 | 21.7688 | 21.4378 | 21.0344 | 20.1704 | 20.6497 | 20.2946 | 20.2796 | 20.1815 |  | 20.2005 | 19.6185 | 20.1156 | 19.7991 | 20.0778 | 20.3382 |  | 20.3839 |  |  | 20.2922 | 20.2967 | 20.6087 | [5 empty] | 21.9112 | 20.3516 | 21.6483 | 22.0267 | 19.5789 | 21.1522 | 21.7736 | 19.4176 | 19.9742 | 21.7791 |  | 19.7118 | 20.8757 | 18.9085 | 19.7478 | 20.8562 | 19.4023 | 20.1434 | 19.0583 | 20.0302 | 19.1663 | 20.217 | 18.8043 | 20.0652 | 21.0115 | 19.4658 | 19.7649 | 21.185 | 18.8881 | 19.7783 | 20.7973 | 18.8502 | 20.0717 | 19.3003 | 20.0874 | 18.9732 | 20.1089 | -0.27764 | 20.9435 | 0.048653 | 0.014607 | -27.078 | 3.0959 | 6.59 | -0.19 | 0.91332 | -0.4495 | -11.3213 | 0.88317 | 0.72904 | -16.7093 | -2.8271 | 0.42041 | 0.43321 | 0.42693 | 0.38745 | 0.48745 | 0.44224 | 0.42588
42838.4192 | -91 | 22.8984 | 22.8617 | 22.8516 | 22.7773 | 22.4038 | 21.7418 | 22.71 | 21.8027 | 22.373 | 22.375 | 22.3535 | 22.0174 | 21.238 | 22.2063 | 21.6015 | 21.7658 | 21.8943 | 21.0777 | 21.1765 | 21.3874 | 20.4798 | 20.6091 | 20.9027 | 21.8772 | 21.6418 | 21.265 | 20.4674 | 20.4209 | 20.7718 | 22.0741 | 21.6718 | 21.1947 | 21.9974 | 21.7403 | 21.3523 | 19.9157 | 20.5935 |  | 20.5042 | 20.0491 | 20.0911 | 19.0583 |  | 17.1313 | 17.1233 | 16.8548 | 17.0083 | 16.9953 | 17.3742 | 17.816 | 15.6197 | 16.9449 | 16.2191 | 16.9804 | 18.0108 | 47.4613 | 50.2055 | 46.0632 | 21.3955 |  |  | 0.42735 | -0.016493 | -89.5348 | 0.68401 | 0.25312 | -197.7895 | -5.6292 | -0.3414 | 0.23828 | 0.09599 | 0.094035 | 8.8288 | 9.0589 | 1.9784 | 21.7796 | 21.9972 | 22.1885 | 22.2609 | 22.0843 | 21.395 | 20.2035 | 22.1924 | 22.3763 | 22.4068 | 22.3567 | 21.9829 | 21.2152 | 22.2697 | 17.2774 | 17.1696 | 16.129 | 16.2707 | 16.3039 | 17.1372 | 16.917 | 22.3688 | 22.1383 | 21.6955 | 22.0827 | 21.789 | 21.3019 | 21.9441 | 21.522 | 20.9116 | 20.0812 | 20.4597 | 19.8698 | 19.8496 | 0.10087 | -0.29364 | 20.7087 | 22.0619 | 22.3653 | 20.1339 | 21.6488 | 22.1032 | 21.9324 | 21.6991 | 21.2682 | 21.7674 | 21.4319 | 21.0318 | 20.1716 | 20.6663 | 20.2899 | 20.2707 | 20.1867 |  | 20.2032 | 19.6052 | 20.117 | 19.7965 | 20.076 | 20.3437 |  | 20.3859 |  |  | 20.3022 | 20.3022 | 20.6168 | [5 empty] | 21.9118 | 20.3539 | 21.6527 | 22.0332 | 19.5889 | 21.1515 | 21.7747 | 19.4133 | 19.97 | 21.8091 |  | 19.7076 | 20.8676 | 18.9014 | 19.7404 | 20.8582 | 19.3956 | 20.1341 | 19.0488 | 20.0339 | 19.158 | 20.2191 | 18.8059 | 20.0654 | 21.0089 | 19.4611 | 19.7687 | 21.196 | 18.8894 | 19.7822 | 20.8034 | 18.8481 | 20.0691 | 19.2963 | 20.0869 | 18.9702 | 20.1226 | -0.082494 | 20.9463 | 0.048776 | 0.015282 | -27.0848 | 3.0959 | -15.57 | -0.01 | 0.78105 | -0.15248 | -11.2348 | 0.98198 | 0.59761 | -16.7055 | -2.8183 | 0.42036 | 0.43363 | 0.42694 | 0.38704 | 0.48896 | 0.44207 | 0.42564
42838.4192 | -90 | 22.9045 | 22.864 | 22.8589 | 22.779 | 22.4094 | 21.7501 | 22.719 | 21.802 | 22.3676 | 22.3755 | 22.3538 | 22.0189 | 21.2434 | 22.2115 | 21.5997 | 21.7691 | 21.898 | 21.0857 | 21.1747 | 21.3909 | 20.477 | 20.6149 | 20.9043 | 21.8777 | 21.6431 | 21.269 | 20.4853 | 20.427 | 20.7917 | 22.0782 | 21.6743 | 21.1914 | 21.9953 | 21.736 | 21.3547 | 19.9172 | 20.6198 |  | 20.5064 | 20.0535 | 20.0946 | 19.0727 |  | 17.1368 | 17.1166 | 16.8408 | 17.0007 | 16.9863 | 17.3597 | 17.7887 | 15.5909 | 16.9476 | 16.2503 | 16.9792 | 18.0115 | 47.5183 | 50.1039 | 46.1098 | 21.4016 |  |  | 0.45955 | 0.10573 | -88.3027 | 0.77009 | 0.15915 | -197.8322 | -5.2238 | -0.28555 | 0.022278 | -0.13752 | 0.03449 | 8.8288 | 9.0585 | 1.9786 | 21.7743 | 22.0043 | 22.1905 | 22.2561 | 22.0856 | 21.4033 | 20.211 | 22.2002 | 22.3751 | 22.4053 | 22.3655 | 21.9806 | 21.2154 | 22.2765 | 17.2833 | 17.2089 | 16.1147 | 16.2767 | 16.3209 | 17.1392 | 16.9084 | 22.3674 | 22.1276 | 21.6899 | 22.0797 | 21.7891 | 21.3071 | 21.9385 | 21.5245 | 20.9012 | 20.0718 | 20.4585 | 19.8673 | 19.8471 | 0.10401 | -0.052464 | 20.7147 | 22.0635 | 22.3684 | 20.1332 | 21.6609 | 22.1018 | 21.9354 | 21.6996 | 21.2742 | 21.7729 | 21.4349 | 21.0331 | 20.1768 | 20.673 | 20.2943 | 20.2778 | 20.1889 |  | 20.2068 | 19.6059 | 20.1233 | 19.7983 | 20.0809 | 20.3479 |  | 20.3961 |  |  | 20.3035 | 20.312 | 20.6147 | [5 empty] | 21.9161 | 20.3519 | 21.6569 | 22.0263 | 19.5768 | 21.145 | 21.765 | 19.4118 | 19.9671 | 21.8221 |  | 19.6997 | 20.8634 | 18.9089 | 19.7405 | 20.8673 | 19.3924 | 20.1361 | 19.0504 | 20.034 | 19.1641 | 20.2113 | 18.8057 | 20.0683 | 21.0061 | 19.4594 | 19.7662 | 21.2056 | 18.8965 | 19.7898 | 20.8169 | 18.8487 | 20.0717 | 19.2998 | 20.0866 | 18.9766 | 20.1404 | -0.23238 | 20.9476 | 0.048745 | 0.015224 | -27.1397 | 3.0959 | -6.92 | -0.06 | 0.80996 | 0.38607 | -11.1571 | 1.0419 | 0.47386 | -16.7069 | -2.7148 | 0.42042 | 0.43382 | 0.42705 | 0.38662 | 0.48954 | 0.44172 | 0.42539
42838.4192 | -89 | 22.9017 | 22.8633 | 22.855 | 22.7733 | 22.4035 | 21.7416 | 22.7178 | 21.7905 | 22.3613 | 22.3751 | 22.3469 | 22.0084 | 21.2341 | 22.1993 | 21.5968 | 21.7724 | 21.9041 | 21.0875 | 21.1802 | 21.396 | 20.4815 | 20.6174 | 20.9073 | 21.8835 | 21.6535 | 21.2772 | 20.4977 | 20.4356 | 20.8102 | 22.0753 | 21.6703 | 21.1912 | 21.9901 | 21.7296 | 21.3489 | 19.9099 | 20.6436 |  | 20.5032 | 20.0525 | 20.0902 | 19.0784 |  | 17.1296 | 17.1115 | 16.8374 | 16.99 | 16.9861 | 17.3449 | 17.7573 | 15.5415 | 16.9508 | 16.2736 | 16.9867 | 18.0103 | 47.5755 | 50.0073 | 46.1492 | 21.4053 |  |  | 0.58901 | 0.072219 | -87.5135 | 0.56507 | 0.15324 | -197.8197 | -5.1509 | -0.37558 | -0.17894 | -0.25165 | 0.15236 | 8.8279 | 9.0576 | 1.9789 | 21.7805 | 22.0015 | 22.1971 | 22.2638 | 22.081 | 21.4034 | 20.2098 | 22.1985 | 22.3692 | 22.4047 | 22.3625 | 21.9804 | 21.2145 | 22.2787 | 17.2795 | 17.2218 | 16.1219 | 16.2754 | 16.321 | 17.1399 | 16.9125 | 22.366 | 22.1378 | 21.6892 | 22.0823 | 21.7947 | 21.3013 | 21.9408 | 21.5241 | 20.9011 | 20.0708 | 20.4556 | 19.8627 | 19.857 | -0.030068 | -0.069963 | 20.7164 | 22.0673 | 22.37 | 20.1345 | 21.6633 | 22.1023 | 21.9395 | 21.7021 | 21.2775 | 21.7783 | 21.4378 | 21.0346 | 20.1791 | 20.6797 | 20.2981 | 20.279 | 20.1824 |  | 20.1959 | 19.591 | 20.1159 | 19.7758 | 20.074 | 20.3368 |  | 20.3842 |  |  | 20.301 | 20.3172 | 20.6165 | [5 empty] | 21.9223 | 20.343 | 21.655 | 22.0283 | 19.5756 | 21.1492 | 21.7708 | 19.4134 | 19.9726 | 21.8706 |  | 19.7008 | 20.8648 | 18.9235 | 19.7421 | 20.8705 | 19.3932 | 20.1381 | 19.058 | 20.0338 | 19.1617 | 20.2107 | 18.8022 | 20.0611 | 21.0059 | 19.4459 | 19.7577 | 21.2118 | 18.8897 | 19.7926 | 20.8244 | 18.8419 | 20.0627 | 19.2916 | 20.0913 | 18.9741 | 20.1395 | -0.25798 | 20.9465 | 0.048161 | 0.015203 | -27.1101 | 3.0958 | -6.05 | -0.13 | 0.917 | 0.31907 | -11.1071 | 0.89251 | 0.46497 | -16.7059 | -2.6957 | 0.42023 | 0.43398 | 0.42744 | 0.38712 | 0.48923 | 0.44132 | 0.42508
42838.4193 | -88 | 22.8928 | 22.8647 | 22.8648 | 22.773 | 22.4067 | 21.7405 | 22.7185 | 21.7881 | 22.3653 | 22.3813 | 22.3494 | 22.0191 | 21.2349 | 22.2067 | 21.5942 | 21.7677 | 21.8976 | 21.0767 | 21.1837 | 21.3902 | 20.4703 | 20.6049 | 20.9077 | 21.8733 | 21.6427 | 21.2695 | 20.5011 | 20.4456 | 20.8353 | 22.0758 | 21.6728 | 21.1947 | 21.9976 | 21.737 | 21.3512 | 19.906 | 20.6768 |  | 20.5054 | 20.0538 | 20.0933 | 19.1004 |  | 17.1241 | 17.0918 | 16.8233 | 16.9712 | 16.9622 | 17.3121 | 17.7132 | 15.4705 | 16.9561 | 16.2501 | 16.9827 | 18.0127 | 47.6079 | 49.9118 | 46.1867 | 21.4057 |  |  | 0.62055 | 0.028191 | -86.723 | 0.81741 | 0.30963 | -197.8328 | -4.7448 | -0.39594 | -0.1624 | -0.39809 | -0.020888 | 8.8292 | 9.0589 | 1.9786 | 21.7716 | 22.0079 | 22.1995 | 22.2506 | 22.0845 | 21.3989 | 20.211 | 22.1989 | 22.3782 | 22.4041 | 22.3577 | 21.9933 | 21.22 | 22.2782 | 17.2637 | 17.2039 | 16.1281 | 16.2671 | 16.3196 | 17.1341 | 16.9136 | 22.3741 | 22.1434 | 21.6967 | 22.0847 | 21.7916 | 21.2954 | 21.9456 | 21.5347 | 20.9028 | 20.086 | 20.4634 | 19.8675 | 19.8578 | -0.057788 | -0.092596 | 20.7176 | 22.0692 | 22.3724 | 20.1324 | 21.6617 | 22.0983 | 21.9405 | 21.7033 | 21.2731 | 21.7779 | 21.4371 | 21.0326 | 20.1807 | 20.6923 | 20.2923 | 20.2774 | 20.1851 |  | 20.2018 | 19.5928 | 20.1186 | 19.763 | 20.0774 | 20.3421 |  | 20.3918 |  |  | 20.3105 | 20.3239 | 20.6307 | [5 empty] | 21.9195 | 20.3436 | 21.657 | 22.0316 | 19.5875 | 21.1482 | 21.7702 | 19.4118 | 19.975 | 21.9014 |  | 19.7064 | 20.8667 | 18.9155 | 19.7438 | 20.8679 | 19.3914 | 20.1407 | 19.0552 | 20.0411 | 19.162 | 20.2064 | 18.7981 | 20.0562 | 21.0044 | 19.4449 | 19.754 | 21.2272 | 18.8909 | 19.7839 | 20.8191 | 18.8336 | 20.0674 | 19.2884 | 20.0981 | 18.9689 | 20.1495 | -0.15966 | 20.9457 | 0.047737 | 0.013838 | -27.0317 | 3.0958 | -11.83 | -0.13 | 0.94128 | 0.19934 | -11.0564 | 1.0734 | 0.6609 | -16.7056 | -2.5871 | 0.42036 | 0.43402 | 0.42791 | 0.3882 | 0.48866 | 0.44058 | 0.42557
42838.4193 | -87 | 22.9012 | 22.8645 | 22.8551 | 22.7771 | 22.3999 | 21.7393 | 22.7136 | 21.801 | 22.3678 | 22.3807 | 22.3512 | 22.0212 | 21.2363 | 22.202 | 21.5992 | 21.7678 | 21.8939 | 21.0847 | 21.1804 | 21.3949 | 20.4872 | 20.6157 | 20.9152 | 21.8865 | 21.6451 | 21.2635 | 20.5119 | 20.4596 | 20.8805 | 22.0773 | 21.6707 | 21.194 | 22.004 | 21.7342 | 21.3471 | 19.9084 | 20.7635 |  | 20.5027 | 20.0511 | 20.0856 | 19.1342 |  | 17.1303 | 17.0753 | 16.8149 | 16.9612 | 16.9425 | 17.2827 | 17.6957 | 15.4066 | 16.9539 | 16.225 | 16.9921 | 18.0226 | 47.6537 | 49.8173 | 46.2233 | 21.4073 |  |  | 0.53118 | -0.12754 | -86.1447 | 0.79638 | 0.1999 | -197.8519 | -4.9248 | -0.36375 | -0.041162 | -0.14234 | 0.020776 | 8.8284 | 9.0584 | 1.9788 | 21.7751 | 22.0011 | 22.192 | 22.2535 | 22.0828 | 21.3964 | 20.2082 | 22.1996 | 22.3732 | 22.4077 | 22.3565 | 21.9919 | 21.2241 | 22.2777 | 17.254 | 17.1848 | 16.1136 | 16.2608 | 16.3417 | 17.1322 | 16.9103 | 22.3667 | 22.1296 | 21.6835 | 22.0807 | 21.7869 | 21.2913 | 21.9439 | 21.5232 | 20.8968 | 20.0774 | 20.4567 | 19.8507 | 19.8436 | -0.048155 | 0.014676 | 20.7229 | 22.0707 | 22.372 | 20.1318 | 21.6604 | 22.0988 | 21.9357 | 21.7091 | 21.267 | 21.7702 | 21.4401 | 21.0306 | 20.1855 | 20.6905 | 20.291 | 20.2757 | 20.1724 |  | 20.1956 | 19.6002 | 20.1121 | 19.7452 | 20.0768 | 20.3405 |  | 20.3859 |  |  | 20.3144 | 20.3234 | 20.6213 | [5 empty] | 21.909 | 20.3461 | 21.6516 | 22.028 | 19.5852 | 21.154 | 21.7755 | 19.4187 | 19.9709 | 21.9309 |  | 19.7106 | 20.8744 | 18.9223 | 19.7444 | 20.8591 | 19.4022 | 20.1455 | 19.0663 | 20.0373 | 19.1697 | 20.2076 | 18.792 | 20.051 | 21.0001 | 19.4303 | 19.7572 | 21.2336 | 18.8774 | 19.7802 | 20.8174 | 18.8303 | 20.0553 | 19.2839 | 20.1029 | 18.9629 | 20.1533 | -0.26299 | 20.9461 | 0.046515 | 0.012611 | -27.0479 | 3.0959 | 5.38 | -0.07 | 0.87093 | -0.424 | -11.0192 | 1.0595 | 0.531 | -16.7055 | -2.6356 | 0.4205 | 0.4336 | 0.42839 | 0.38906 | 0.48988 | 0.43972 | 0.42567
42838.4193 | -86 | 22.9023 | 22.8661 | 22.8496 | 22.7793 | 22.3979 | 21.7444 | 22.7133 | 21.794 | 22.3669 | 22.3685 | 22.3497 | 22.0244 | 21.2296 | 22.2052 | 21.6009 | 21.772 | 21.8963 | 21.0888 | 21.1794 | 21.4012 | 20.4774 | 20.6109 | 20.9098 | 21.8885 | 21.6429 | 21.2803 | 20.5208 | 20.4764 | 20.9033 | 22.0747 | 21.6749 | 21.1987 | 22.0062 | 21.7416 | 21.3542 | 19.9164 | 20.8421 |  | 20.5091 | 20.0511 | 20.0956 | 19.184 |  | 17.1246 | 17.0618 | 16.8026 | 16.9491 | 16.9257 | 17.2638 | 17.6754 | 15.4617 | 16.9615 | 16.1927 | 16.9934 | 18.0178 | 47.7012 | 49.719 | 46.2588 | 21.4056 |  |  | 0.56403 | 0.11099 | -85.1715 | 0.84501 | 0.28992 | -197.846 | -4.6041 | -0.31906 | 0.1838 | -0.19563 | 0.029456 | 8.8282 | 9.0584 | 1.9789 | 21.7801 | 22.0025 | 22.1915 | 22.2634 | 22.0868 | 21.3963 | 20.208 | 22.2009 | 22.375 | 22.411 | 22.3562 | 21.9891 | 21.218 | 22.279 | 17.2258 | 17.1821 | 16.1106 | 16.2373 | 16.3114 | 17.127 | 16.9082 | 22.3632 | 22.1285 | 21.6897 | 22.0759 | 21.7917 | 21.2979 | 21.9492 | 21.5237 | 20.9025 | 20.0773 | 20.4579 | 19.8572 | 19.8446 | 0.10342 | -0.10382 | 20.7257 | 22.0716 | 22.3701 | 20.1342 | 21.6573 | 22.0987 | 21.9415 | 21.7107 | 21.269 | 21.7628 | 21.4434 | 21.0365 | 20.1912 | 20.6911 | 20.2888 | 20.2726 | 20.1786 |  | 20.2085 | 19.6113 | 20.1187 | 19.7332 | 20.0788 | 20.337 |  | 20.3906 |  |  | 20.3121 | 20.334 | 20.618 | [5 empty] | 21.9194 | 20.3538 | 21.6531 | 22.034 | 19.6 | 21.1502 | 21.7719 | 19.4286 | 19.9808 | 21.9603 |  | 19.7185 | 20.8798 | 18.9336 | 19.7366 | 20.8832 | 19.406 | 20.1494 | 19.066 | 20.0485 | 19.178 | 20.1973 | 18.8075 | 20.0567 | 21.009 | 19.4488 | 19.7635 | 21.2618 | 18.8902 | 19.8022 | 20.8457 | 18.8347 | 20.068 | 19.299 | 20.144 | 18.9757 | 20.1747 | -0.066541 | 20.9459 | 0.04566 | 0.013054 | -27.142 | 3.0958 | 9.64 | -0.13 | 0.8975 | 0.39551 | -10.9565 | 1.0913 | 0.63946 | -16.7047 | -2.5483 | 0.42076 | 0.43351 | 0.42879 | 0.39158 | 0.48997 | 0.43861 | 0.42565
42838.4193 | -85 | 22.9104 | 22.8715 | 22.8521 | 22.7798 | 22.4058 | 21.7451 | 22.7234 | 21.8108 | 22.3698 | 22.3792 | 22.3593 | 22.0218 | 21.2362 | 22.2126 | 21.5979 | 21.7747 | 21.9069 | 21.085 | 21.1946 | 21.3972 | 20.4858 | 20.6128 | 20.9151 | 21.88 | 21.6437 | 21.2725 | 20.5308 | 20.4829 | 20.8795 | 22.0891 | 21.6745 | 21.1994 | 22.0035 | 21.7393 | 21.3562 | 19.9173 | 20.9004 |  | 20.52 | 20.0616 | 20.092 | 19.2381 |  | 17.117 | 17.0488 | 16.7816 | 16.9241 | 16.9023 | 17.2383 | 17.633 | 15.5875 | 16.9523 | 16.1835 | 16.9866 | 18.012 | 47.7326 | 49.6272 | 46.2823 | 21.4003 |  |  | 0.43721 | -0.12229 | -83.9664 | 0.73855 | 0.23801 | -197.8052 | -4.4793 | -0.42223 | -0.015475 | -0.20172 | 0.00602 | 8.8284 | 9.0586 | 1.9789 | 21.7757 | 21.9997 | 22.1883 | 22.2559 | 22.084 | 21.3929 | 20.206 | 22.1999 | 22.3693 | 22.4078 | 22.3546 | 21.9844 | 21.2159 | 22.2735 | 17.2074 | 17.2023 | 16.1187 | 16.2327 | 16.2881 | 17.1334 | 16.9104 | 22.3678 | 22.1435 | 21.7028 | 22.0852 | 21.7976 | 21.3073 | 21.9462 | 21.5328 | 20.8984 | 20.0832 | 20.4698 | 19.8642 | 19.8546 | -0.0080484 | -0.027928 | 20.7241 | 22.0658 | 22.3684 | 20.1306 | 21.6582 | 22.0997 | 21.9431 | 21.7102 | 21.2709 | 21.7667 | 21.4414 | 21.0319 | 20.1936 | 20.692 | 20.2843 | 20.2663 | 20.1758 |  | 20.2135 | 19.6102 | 20.1261 | 19.7306 | 20.0845 | 20.3424 |  | 20.395 |  |  | 20.3083 | 20.3311 | 20.6187 | [5 empty] | 21.9176 | 20.3443 | 21.6555 | 22.0313 | 19.601 | 21.1509 | 21.7679 | 19.4281 | 19.9695 | 22.0035 |  | 19.7079 | 20.8726 | 18.9199 | 19.7365 | 20.9013 | 19.4028 | 20.1377 | 19.0501 | 20.046 | 19.1533 | 20.1918 | 18.7967 | 20.0411 | 20.9988 | 19.4385 | 19.7565 | 21.2705 | 18.8814 | 19.7986 | 20.8444 | 18.8355 | 20.0497 | 19.2814 | 20.1393 | 18.9586 | 20.1662 | -0.24147 | 20.9461 | 0.046287 | 0.012328 | -27.1149 | 3.0958 | -4.44 | -0.09 | 0.79015 | -0.41515 | -10.8785 | 1.0202 | 0.57937 | -16.7023 | -2.5134 | 0.42101 | 0.43379 | 0.42905 | 0.39437 | 0.48933 | 0.43713 | 0.42556
42838.4193 | -84 | 22.8989 | 22.8644 | 22.8501 | 22.7796 | 22.4024 | 21.7417 | 22.7182 | 21.7952 | 22.3601 | 22.3766 | 22.3569 | 22.0186 | 21.2433 | 22.206 | 21.6051 | 21.7758 | 21.9067 | 21.082 | 21.1902 | 21.392 | 20.4766 | 20.6135 | 20.9156 | 21.8961 | 21.6451 | 21.2777 | 20.5398 | 20.493 | 20.8842 | 22.083 | 21.6684 | 21.1883 | 21.9992 | 21.7364 | 21.3492 | 19.907 | 20.9526 |  | 20.5105 | 20.0527 | 20.0892 | 19.2842 |  | 17.1153 | 17.0467 | 16.7683 | 16.9187 | 16.898 | 17.2235 | 17.6057 | 15.7138 | 16.9606 | 16.2205 | 16.9795 | 18.0149 | 47.752 | 49.5408 | 46.3075 | 21.405 |  |  | 0.35901 | -0.053949 | -82.7238 | 0.7655 | 0.33329 | -197.8401 | -1.8548 | -0.5438 | -0.030848 | -0.17339 | -0.038074 | 8.8285 | 9.0581 | 1.9787 | 21.7755 | 21.9957 | 22.1864 | 22.2516 | 22.0776 | 21.3935 | 20.2026 | 22.197 | 22.3772 | 22.4069 | 22.3538 | 21.9802 | 21.2149 | 22.276 | 17.1914 | 17.2305 | 16.1278 | 16.2285 | 16.2768 | 17.1404 | 16.9191 | 22.3684 | 22.1397 | 21.7008 | 22.0793 | 21.7916 | 21.3046 | 21.9451 | 21.5279 | 20.9012 | 20.0803 | 20.4742 | 19.8607 | 19.8586 | 0.032844 | 0.066601 | 20.7251 | 22.0683 | 22.3709 | 20.1293 | 21.6622 | 22.1029 | 21.9409 | 21.7082 | 21.2728 | 21.7723 | 21.4358 | 21.0356 | 20.1975 | 20.6933 | 20.2834 | 20.2675 | 20.1585 |  | 20.2158 | 19.6206 | 20.1169 | 19.7271 | 20.0839 | 20.3482 |  | 20.3995 |  |  | 20.3145 | 20.3288 | 20.6233 | [5 empty] | 21.9183 | 20.3518 | 21.6535 | 22.0256 | 19.5985 | 21.1451 | 21.7645 | 19.416 | 19.971 | 22.0268 |  | 19.6957 | 20.8832 | 18.9275 | 19.7294 | 20.9058 | 19.3945 | 20.1334 | 19.0455 | 20.0526 | 19.1627 | 20.1972 | 18.7918 | 20.0446 | 20.9954 | 19.4418 | 19.7555 | 21.2748 | 18.8876 | 19.8089 | 20.8508 | 18.8314 | 20.0609 | 19.2881 | 20.1494 | 18.9586 | 20.1704 | -0.13388 | 20.9467 | 0.048045 | 0.012386 | -27.1551 | 3.0958 | -9.39 | -0.08 | 0.71601 | -0.27574 | -10.7976 | 1.0387 | 0.68558 | -16.7033 | -1.6173 | 0.42157 | 0.43319 | 0.42913 | 0.39696 | 0.48933 | 0.43551 | 0.42536
42838.4193 | -83 | 22.9058 | 22.8628 | 22.8512 | 22.7795 | 22.403 | 21.7405 | 22.7218 | 21.7867 | 22.3612 | 22.3759 | 22.3524 | 22.0218 | 21.2388 | 22.212 | 21.5945 | 21.7679 | 21.891 | 21.0801 | 21.1721 | 21.3832 | 20.4665 | 20.6118 | 20.9013 | 21.8788 | 21.6357 | 21.2683 | 20.5395 | 20.4876 | 20.8785 | 22.0724 | 21.6687 | 21.1896 | 21.9957 | 21.7298 | 21.3456 | 19.9117 | 21.0113 |  | 20.5141 | 20.0547 | 20.0901 | 19.318 |  | 17.147 | 17.0525 | 16.7704 | 16.9048 | 16.8856 | 17.2 | 17.554 | 15.784 | 16.9644 | 16.2712 | 16.9876 | 18.02 | 47.7466 | 49.4582 | 46.3067 | 21.403 |  |  | 0.43918 | -0.2524 | -81.4976 | 0.67153 | 0.20252 | -197.8256 | -1.5407 | -0.39266 | -0.16746 | -0.27724 | 0.015742 | 8.829 | 9.0588 | 1.9788 | 21.7706 | 21.9962 | 22.1892 | 22.257 | 22.0788 | 21.398 | 20.2083 | 22.201 | 22.3771 | 22.4045 | 22.3532 | 21.9823 | 21.2161 | 22.2797 | 17.1791 | 17.2326 | 16.1481 | 16.2262 | 16.265 | 17.141 | 16.914 | 22.3672 | 22.1343 | 21.6951 | 22.0744 | 21.786 | 21.2993 | 21.9405 | 21.5211 | 20.9062 | 20.07 | 20.4759 | 19.8536 | 19.867 | -0.11028 | -0.01043 | 20.7268 | 22.0713 | 22.3744 | 20.1297 | 21.6628 | 22.1074 | 21.944 | 21.712 | 21.2791 | 21.7742 | 21.4391 | 21.0413 | 20.2119 | 20.6939 | 20.2749 | 20.2702 | 20.1375 |  | 20.2045 | 19.6216 | 20.1189 | 19.7206 | 20.0903 | 20.3361 |  | 20.387 |  |  | 20.3125 | 20.3323 | 20.622 | [5 empty] | 21.9131 | 20.344 | 21.65 | 22.0276 | 19.6075 | 21.1447 | 21.7604 | 19.4178 | 19.9766 | 22.0566 |  | 19.6911 | 20.8862 | 18.9238 | 19.7326 | 20.9111 | 19.4006 | 20.137 | 19.0336 | 20.0533 | 19.1613 | 20.1866 | 18.7977 | 20.0398 | 20.9921 | 19.4405 | 19.757 | 21.2825 | 18.8861 | 19.7997 | 20.8672 | 18.8386 | 20.0604 | 19.2859 | 20.1633 | 18.9584 | 20.1873 | -0.18229 | 20.9469 | 0.04794 | 0.013438 | -27.1203 | 3.0958 | -10.29 | -0.07 | 0.79192 | -0.59643 | -10.7174 | 0.97286 | 0.5344 | -16.702 | -1.474 | 0.42177 | 0.43323 | 0.42952 | 0.39841 | 0.48648 | 0.43472 | 0.42478
42838.4193 | -82 | 22.9035 | 22.863 | 22.8504 | 22.7792 | 22.4058 | 21.7422 | 22.7235 | 21.7885 | 22.3689 | 22.3742 | 22.3464 | 22.0161 | 21.2366 | 22.2091 | 21.5967 | 21.7694 | 21.8957 | 21.0845 | 21.1804 | 21.3905 | 20.4811 | 20.6144 | 20.9071 | 21.8825 | 21.6479 | 21.2695 | 20.5499 | 20.5037 | 20.9042 | 22.0727 | 21.6683 | 21.1926 | 21.9924 | 21.7291 | 21.3432 | 19.9131 | 21.0438 |  | 20.5132 | 20.0533 | 20.088 | 19.3519 |  | 17.1275 | 17.0429 | 16.7541 | 16.8847 | 16.8996 | 17.1799 | 17.5689 | 15.7381 | 16.9617 | 16.2952 | 16.9784 | 18.0179 | 47.7377 | 49.3591 | 46.3053 | 21.4028 |  |  | 0.35836 | -0.43113 | -80.0342 | 0.89692 | 0.43054 | -197.798 | -0.69234 | -0.43406 | -0.38035 | -0.44299 | 0.19576 | 8.8286 | 9.0583 | 1.9785 | 21.7768 | 21.9971 | 22.193 | 22.2556 | 22.0787 | 21.402 | 20.2096 | 22.1975 | 22.3676 | 22.4072 | 22.3623 | 21.9863 | 21.215 | 22.2744 | 17.1496 | 17.219 | 16.1586 | 16.222 | 16.2469 | 17.1346 | 16.9157 | 22.3698 | 22.1375 | 21.6967 | 22.0797 | 21.7984 | 21.3035 | 21.9467 | 21.5242 | 20.9071 | 20.0868 | 20.4936 | 19.8653 | 19.8632 | 0.017903 | -0.052464 | 20.7245 | 22.0638 | 22.3685 | 20.1265 | 21.6556 | 22.1018 | 21.9367 | 21.7021 | 21.2704 | 21.7664 | 21.436 | 21.0351 | 20.2192 | 20.6843 | 20.2647 | 20.2551 | 20.1403 |  | 20.2071 | 19.6442 | 20.1292 | 19.7117 | 20.0876 | 20.3383 |  | 20.3866 |  |  | 20.3226 | 20.3299 | 20.6235 | [5 empty] | 21.9202 | 20.3489 | 21.6559 | 22.0386 | 19.6112 | 21.1474 | 21.7714 | 19.4185 | 19.9807 | 22.0805 |  | 19.6952 | 20.9044 | 18.9259 | 19.7322 | 20.9206 | 19.4103 | 20.1383 | 19.0324 | 20.0605 | 19.1615 | 20.1806 | 18.7807 | 20.0362 | 20.9983 | 19.4338 | 19.7517 | 21.2931 | 18.8789 | 19.8026 | 20.8699 | 18.8373 | 20.0556 | 19.2826 | 20.164 | 18.956 | 20.1934 | -0.094181 | 20.9463 | 0.048143 | 0.013308 | -26.9834 | 3.0958 | -15.35 | -0.13 | 0.71538 | -0.7795 | -10.6206 | 1.1243 | 0.77915 | -16.7003 | -0.98803 | 0.42178 | 0.43295 | 0.42968 | 0.40094 | 0.48551 | 0.43383 | 0.42545
42838.4193 | -81 | 22.9063 | 22.873 | 22.86 | 22.7794 | 22.4084 | 21.7514 | 22.7255 | 21.8077 | 22.3737 | 22.3853 | 22.3529 | 22.0264 | 21.2392 | 22.2134 | 21.5991 | 21.7631 | 21.8973 | 21.0912 | 21.1856 | 21.397 | 20.4809 | 20.6137 | 20.9161 | 21.8842 | 21.6427 | 21.2789 | 20.5564 | 20.5111 | 20.9094 | 22.0718 | 21.676 | 21.1903 | 21.9951 | 21.7342 | 21.3459 | 19.9166 | 21.0592 |  | 20.5148 | 20.0546 | 20.0906 | 19.4173 |  | 17.1144 | 17.0614 | 16.7626 | 16.8929 | 16.8719 | 17.1722 | 17.5962 | 15.6478 | 16.9698 | 16.2781 | 16.9844 | 18.0101 | 47.7259 | 49.2609 | 46.3003 | 21.4022 |  |  | 0.45035 | -0.39171 | -78.6838 | 0.62947 | 0.37534 | -197.8296 | -0.486 | -0.32826 | -0.40584 | -0.46502 | -0.011861 | 8.8288 | 9.0587 | 1.9787 | 21.7799 | 22.0013 | 22.1895 | 22.2501 | 22.0779 | 21.3914 | 20.2032 | 22.1984 | 22.3666 | 22.4071 | 22.3504 | 21.9793 | 21.2214 | 22.2734 | 17.1316 | 17.2125 | 16.173 | 16.2443 | 16.2618 | 17.1335 | 16.9152 | 22.366 | 22.14 | 21.7039 | 22.0802 | 21.7959 | 21.3024 | 21.9533 | 21.5321 | 20.9012 | 20.0837 | 20.5114 | 19.864 | 19.8694 | -0.063096 | -0.1546 | 20.7212 | 22.0632 | 22.3658 | 20.1267 | 21.6571 | 22.1077 | 21.937 | 21.697 | 21.2663 | 21.7632 | 21.4356 | 21.0319 | 20.2243 | 20.6935 | 20.2654 | 20.2464 | 20.1366 |  | 20.2173 | 19.6448 | 20.1234 | 19.7063 | 20.0911 | 20.3382 |  | 20.3889 |  |  | 20.3225 | 20.3248 | 20.6168 | [5 empty] | 21.9193 | 20.3391 | 21.6559 | 22.0333 | 19.6119 | 21.1497 | 21.7735 | 19.4168 | 19.9818 | 22.1037 |  | 19.6928 | 20.9051 | 18.9293 | 19.7226 | 20.9305 | 19.4096 | 20.1362 | 19.024 | 20.0516 | 19.1668 | 20.1725 | 18.7827 | 20.0422 | 20.9998 | 19.4352 | 19.7545 | 21.2999 | 18.8781 | 19.8076 | 20.8707 | 18.8453 | 20.0625 | 19.2877 | 20.1731 | 18.9439 | 20.1949 | -0.23294 | 20.9468 | 0.048284 | 0.013925 | -27.0133 | 3.0958 | 3.29 | -0.16 | 0.80198 | -0.74303 | -10.5309 | 0.94192 | 0.72748 | -16.7014 | -0.8278 | 0.42222 | 0.43274 | 0.42995 | 0.40281 | 0.48385 | 0.43213 | 0.42517
42838.4194 | -80 | 22.9013 | 22.8711 | 22.8602 | 22.7757 | 22.404 | 21.7398 | 22.7152 | 21.8002 | 22.3657 | 22.3688 | 22.3609 | 22.0177 | 21.2359 | 22.2009 | 21.5948 | 21.757 | 21.8924 | 21.0798 | 21.1786 | 21.3933 | 20.4676 | 20.6086 | 20.9034 | 21.8732 | 21.6344 | 21.2675 | 20.5529 | 20.515 | 20.9042 | 22.075 | 21.6796 | 21.1886 | 22.0043 | 21.7374 | 21.3563 | 19.9222 | 21.0666 |  | 20.5127 | 20.063 | 20.0986 | 19.4822 |  | 17.1104 | 17.0513 | 16.7619 | 16.8795 | 16.8686 | 17.1707 | 17.5806 | 15.5861 | 16.9693 | 16.2555 | 16.9835 | 18.0072 | 47.7111 | 49.1753 | 46.281 | 21.401 |  |  | 0.43984 | -0.14397 | -77.4892 | 0.48425 | 0.33986 | -197.8506 | -1.105 | -0.26189 | -0.23479 | -0.28207 | 0.0070616 | 8.829 | 9.0589 | 1.9788 | 21.7729 | 21.998 | 22.1943 | 22.2552 | 22.0845 | 21.3914 | 20.2002 | 22.1978 | 22.3727 | 22.4079 | 22.3528 | 21.9815 | 21.2179 | 22.2768 | 17.1258 | 17.2112 | 16.1719 | 16.255 | 16.2778 | 17.128 | 16.9182 | 22.3673 | 22.136 | 21.6973 | 22.0734 | 21.791 | 21.2972 | 21.9496 | 21.522 | 20.8993 | 20.0822 | 20.5264 | 19.8659 | 19.8666 | -0.18361 | -0.080614 | 20.7243 | 22.0619 | 22.3651 | 20.1315 | 21.6578 | 22.1071 | 21.9396 | 21.6955 | 21.2751 | 21.7668 | 21.4402 | 21.0348 | 20.2301 | 20.7179 | 20.2713 | 20.2501 | 20.1262 |  | 20.2075 | 19.6458 | 20.1118 | 19.6903 | 20.0812 | 20.335 |  | 20.3922 |  |  | 20.311 | 20.3277 | 20.6203 | [5 empty] | 21.9158 | 20.3375 | 21.6574 | 22.0306 | 19.6151 | 21.1537 | 21.7741 | 19.4131 | 19.9803 | 22.1185 |  | 19.6858 | 20.8987 | 18.9303 | 19.7225 | 20.9358 | 19.4083 | 20.1323 | 19.0217 | 20.0612 | 19.1615 | 20.1742 | 18.7925 | 20.044 | 20.9977 | 19.4424 | 19.7561 | 21.3134 | 18.8862 | 19.8146 | 20.8793 | 18.8523 | 20.0645 | 19.2919 | 20.1791 | 18.9526 | 20.2072 | -0.12219 | 20.9472 | 0.04837 | 0.013896 | -27.1534 | 3.0958 | -18.96 | -0.02 | 0.79255 | -0.45046 | -10.4505 | 0.82614 | 0.69224 | -16.7022 | -1.2482 | 0.42218 | 0.43232 | 0.43006 | 0.40281 | 0.48433 | 0.43051 | 0.4252
42838.4194 | -79 | 22.8886 | 22.8484 | 22.8448 | 22.7644 | 22.3959 | 21.7347 | 22.7049 | 21.7932 | 22.3547 | 22.3664 | 22.3437 | 22.0048 | 21.2219 | 22.1995 | 21.5954 | 21.7593 | 21.8831 | 21.0715 | 21.1757 | 21.3882 | 20.4637 | 20.6125 | 20.896 | 21.8739 | 21.6339 | 21.267 | 20.5542 | 20.5298 | 20.9091 | 22.0738 | 21.6714 | 21.1911 | 22.0013 | 21.7288 | 21.3523 | 19.9149 | 21.0523 |  | 20.5123 | 20.0571 | 20.1061 | 19.5242 |  | 17.1 | 17.0367 | 16.7465 | 16.8712 | 16.8492 | 17.1508 | 17.5358 | 15.5315 | 16.97 | 16.2292 | 16.9803 | 18.0175 | 47.7049 | 49.0888 | 46.2826 | 21.4116 |  |  | 0.38267 | -0.26554 | -76.9169 | 0.57887 | 0.35432 | -197.8742 | 0.81246 | -0.1515 | 0.0030124 | -0.27368 | -0.019846 | 8.8283 | 9.0582 | 1.9785 | 21.7765 | 21.9995 | 22.1978 | 22.2593 | 22.0835 | 21.3966 | 20.2086 | 22.1994 | 22.3739 | 22.4103 | 22.363 | 21.9831 | 21.215 | 22.2748 | 17.1222 | 17.2018 | 16.1639 | 16.2455 | 16.2708 | 17.131 | 16.915 | 22.3637 | 22.1327 | 21.6869 | 22.0745 | 21.7949 | 21.2966 | 21.9474 | 21.5211 | 20.8944 | 20.0789 | 20.5298 | 19.8744 | 19.8602 | 0.010825 | -0.077571 | 20.7299 | 22.0641 | 22.3682 | 20.1411 | 21.6603 | 22.1083 | 21.9439 | 21.7077 | 21.2764 | 21.7761 | 21.4372 | 21.0366 | 20.247 | 20.7393 | 20.2736 | 20.2568 | 20.1196 |  | 20.2086 | 19.6599 | 20.1174 | 19.7059 | 20.0865 | 20.342 |  | 20.3967 |  |  | 20.3141 | 20.3409 | 20.6253 | [5 empty] | 21.9141 | 20.3385 | 21.6585 | 22.0309 | 19.6225 | 21.1543 | 21.7749 | 19.4239 | 19.9905 | 22.1395 |  | 19.6867 | 20.9041 | 18.9309 | 19.7297 | 20.9566 | 19.4131 | 20.1379 | 19.0228 | 20.0686 | 19.1596 | 20.1731 | 18.7887 | 20.0403 | 20.9961 | 19.4436 | 19.7548 | 21.3282 | 18.8928 | 19.8211 | 20.8886 | 18.8541 | 20.0624 | 19.2909 | 20.1885 | 18.9563 | 20.2156 | -0.19268 | 20.9473 | 0.048426 | 0.015028 | -27.0719 | 3.0958 | -20.12 | -0.13 | 0.73926 | -0.61175 | -10.4116 | 0.90323 | 0.70678 | -16.7027 | 1.0703 | 0.4224 | 0.43212 | 0.42981 | 0.40357 | 0.48484 | 0.42911 | 0.42526
42838.4194 | -78 | 22.8958 | 22.8616 | 22.8522 | 22.7748 | 22.3998 | 21.7345 | 22.712 | 21.7945 | 22.3618 | 22.3716 | 22.3504 | 22.0122 | 21.223 | 22.2032 | 21.6002 | 21.7663 | 21.8868 | 21.0849 | 21.1818 | 21.3867 | 20.477 | 20.613 | 20.8998 | 21.882 | 21.6355 | 21.272 | 20.5649 | 20.538 | 20.9421 | 22.0812 | 21.6722 | 21.1939 | 21.9987 | 21.7339 | 21.3479 | 19.9206 | 21.0293 |  | 20.5085 | 20.067 | 20.1242 | 19.5793 |  | 17.1039 | 17.046 | 16.7429 | 16.9012 | 16.8562 | 17.1658 | 17.476 | 15.5964 | 16.9749 | 16.223 | 16.9782 | 18.0191 | 47.6904 | 49.0053 | 46.2707 | 21.4152 |  |  | 0.32879 | -0.060521 | -75.9982 | 0.62356 | 0.30503 | -197.8434 | 5.6659 | -0.13047 | -0.13418 | -0.18179 | -0.12609 | 8.8288 | 9.0587 | 1.9786 | 21.774 | 21.9928 | 22.1917 | 22.2537 | 22.0795 | 21.3934 | 20.2042 | 22.1976 | 22.3693 | 22.4019 | 22.3589 | 21.986 | 21.2104 | 22.2679 | 17.1315 | 17.218 | 16.1867 | 16.2313 | 16.2886 | 17.1362 | 16.9146 | 22.3651 | 22.1378 | 21.6931 | 22.0798 | 21.7996 | 21.3041 | 21.9441 | 21.528 | 20.9068 | 20.0782 | 20.5361 | 19.8879 | 19.8579 | -0.083739 | -0.36629 | 20.7311 | 22.0711 | 22.3711 | 20.1359 | 21.6696 | 22.1088 | 21.9454 | 21.7073 | 21.2714 | 21.7798 | 21.4377 | 21.0382 | 20.247 | 20.7582 | 20.2606 | 20.2466 | 20.1142 |  | 20.2099 | 19.6535 | 20.1188 | 19.7064 | 20.086 | 20.3392 |  | 20.3955 |  |  | 20.3035 | 20.3405 | 20.6234 | [5 empty] | 21.9101 | 20.3364 | 21.6492 | 22.0292 | 19.616 | 21.1493 | 21.7674 | 19.4211 | 19.9917 | 22.1696 |  | 19.6864 | 20.9187 | 18.9387 | 19.7324 | 20.9753 | 19.4195 | 20.1491 | 19.0248 | 20.0749 | 19.1625 | 20.1731 | 18.7894 | 20.0392 | 20.9957 | 19.4471 | 19.7585 | 21.3423 | 18.8933 | 19.8194 | 20.8982 | 18.8611 | 20.0645 | 19.2942 | 20.2001 | 18.9597 | 20.22 | -0.08435 | 20.9469 | 0.04802 | 0.015384 | -27.062 | 3.0957 | -10.07 | -0.09 | 0.68528 | -0.29206 | -10.3494 | 0.93746 | 0.65581 | -16.7018 | 2.8264 | 0.4226 | 0.43234 | 0.42977 | 0.40313 | 0.48226 | 0.42776 | 0.4253
42838.4194 | -77 | 22.9037 | 22.8645 | 22.8573 | 22.7718 | 22.4009 | 21.7434 | 22.7156 | 21.7958 | 22.3682 | 22.3753 | 22.346 | 22.0172 | 21.2348 | 22.2029 | 21.5994 | 21.7703 | 21.8956 | 21.0831 | 21.184 | 21.3952 | 20.48 | 20.6125 | 20.8991 | 21.88 | 21.6393 | 21.271 | 20.5781 | 20.5456 | 20.9806 | 22.0841 | 21.6727 | 21.195 | 22.0015 | 21.7432 | 21.3597 | 19.9339 | 21.023 |  | 20.5106 | 20.0645 | 20.1318 | 19.6313 |  | 17.0922 | 17.032 | 16.7365 | 16.8253 | 16.8284 | 17.1014 | 17.4621 | 15.6501 | 16.9703 | 16.2075 | 16.9853 | 18.0076 | 47.6541 | 48.9029 | 46.2294 | 21.4035 |  |  | 0.32813 | -0.14857 | -74.9711 | 0.60647 | 0.24129 | -197.8683 | 6.4407 | -0.16332 | 0.0094342 | -0.11822 | -0.1707 | 8.8283 | 9.0582 | 1.9787 | 21.7746 | 21.991 | 22.1928 | 22.25 | 22.0781 | 21.3933 | 20.1987 | 22.1941 | 22.3684 | 22.406 | 22.3565 | 21.9825 | 21.2137 | 22.2681 | 17.1352 | 17.209 | 16.1603 | 16.2305 | 16.2776 | 17.1406 | 16.9156 | 22.3634 | 22.1312 | 21.6883 | 22.0748 | 21.7968 | 21.2991 | 21.9412 | 21.5274 | 20.8983 | 20.0899 | 20.5527 | 19.9037 | 19.8546 | -0.042257 | -0.056839 | 20.7287 | 22.0736 | 22.3703 | 20.1334 | 21.67 | 22.1082 | 21.9443 | 21.7038 | 21.2794 | 21.7842 | 21.4425 | 21.0384 | 20.2527 | 20.7617 | 20.2502 | 20.2408 | 20.1018 |  | 20.2 | 19.6583 | 20.1164 | 19.7058 | 20.0771 | 20.3286 |  | 20.3908 |  |  | 20.2943 | 20.3426 | 20.6176 | [5 empty] | 21.9021 | 20.3323 | 21.6452 | 22.0257 | 19.6144 | 21.1483 | 21.7661 | 19.4141 | 19.9861 | 22.1822 |  | 19.6836 | 20.9209 | 18.928 | 19.7323 | 20.9828 | 19.4232 | 20.1509 | 19.0234 | 20.0775 | 19.1661 | 20.1643 | 18.7832 | 20.0396 | 20.997 | 19.4466 | 19.7561 | 21.3475 | 18.8899 | 19.8187 | 20.9146 | 18.8669 | 20.0632 | 19.2913 | 20.2041 | 18.9592 | 20.221 | -0.29897 | 20.9477 | 0.048333 | 0.014506 | -27.0607 | 3.0957 | -17.59 | -0.21 | 0.68464 | -0.45759 | -10.279 | 0.9245 | 0.58321 | -16.701 | 3.0131 | 0.42261 | 0.43213 | 0.42949 | 0.40324 | 0.48531 | 0.42677 | 0.42579
42838.4194 | -76 | 22.9052 | 22.8656 | 22.8508 | 22.7751 | 22.4016 | 21.7389 | 22.7155 | 21.7984 | 22.3637 | 22.3772 | 22.3455 | 22.0209 | 21.2363 | 22.2056 | 21.5994 | 21.7701 | 21.8956 | 21.0851 | 21.1829 | 21.3961 | 20.478 | 20.6114 | 20.911 | 21.8828 | 21.6466 | 21.2709 | 20.5866 | 20.5571 | 20.9921 | 22.0785 | 21.67 | 21.1878 | 21.9989 | 21.7362 | 21.3514 | 19.9268 | 21.035 |  | 20.5119 | 20.0624 | 20.1423 | 19.6452 |  | 17.0923 | 17.0227 | 16.7381 | 16.8359 | 16.8289 | 17.1045 | 17.4486 | 15.6539 | 16.9772 | 16.1961 | 16.9846 | 18.0089 | 47.6194 | 48.817 | 46.2191 | 21.4081 |  |  | 0.41224 | -0.20114 | -73.9454 | 0.33311 | 0.48311 | -197.8033 | 6.3441 | -0.17318 | 0.11841 | -0.22878 | 0.0093184 | 8.8292 | 9.0592 | 1.9787 | 21.7716 | 21.9896 | 22.1904 | 22.2619 | 22.0813 | 21.3907 | 20.2041 | 22.1936 | 22.3637 | 22.4061 | 22.3467 | 21.9767 | 21.2075 | 22.2699 | 17.1266 | 17.2069 | 16.1359 | 16.2237 | 16.2699 | 17.1365 | 16.9108 | 22.3568 | 22.1236 | 21.6884 | 22.0718 | 21.7855 | 21.2983 | 21.9362 | 21.5176 | 20.8996 | 20.0805 | 20.5554 | 19.9124 | 19.8478 | -0.20484 | -0.1702 | 20.7275 | 22.0768 | 22.3706 | 20.1363 | 21.6654 | 22.1109 | 21.9473 | 21.7056 | 21.28 | 21.785 | 21.4431 | 21.0412 | 20.2692 | 20.7699 | 20.2456 | 20.2418 | 20.0986 |  | 20.1973 | 19.6684 | 20.1174 | 19.7098 | 20.0794 | 20.3279 |  | 20.3893 |  |  | 20.2962 | 20.3493 | 20.6154 | [5 empty] | 21.9089 | 20.3367 | 21.6482 | 22.0299 | 19.6174 | 21.1496 | 21.7602 | 19.4177 | 19.986 | 22.196 |  | 19.6844 | 20.9172 | 18.9203 | 19.7312 | 20.9921 | 19.4278 | 20.1454 | 19.013 | 20.0846 | 19.1599 | 20.1604 | 18.7809 | 20.0342 | 20.998 | 19.4489 | 19.7573 | 21.3533 | 18.8847 | 19.8267 | 20.9227 | 18.8697 | 20.0642 | 19.2909 | 20.2059 | 18.957 | 20.2269 | -0.16319 | 20.9472 | 0.047903 | 0.013714 | -27.0891 | 3.0957 | -2.08 | -0.04 | 0.7674 | -0.53241 | -10.2082 | 0.68516 | 0.82524 | -16.6983 | 2.9905 | 0.42261 | 0.43188 | 0.42946 | 0.40372 | 0.48746 | 0.42614 | 0.42566
42838.4194 | -75 | 22.9056 | 22.8688 | 22.8516 | 22.7795 | 22.408 | 21.7423 | 22.7146 | 21.8058 | 22.3666 | 22.3807 | 22.3548 | 22.0282 | 21.2383 | 22.2037 | 21.593 | 21.7633 | 21.8946 | 21.0804 | 21.177 | 21.3937 | 20.4831 | 20.6052 | 20.9044 | 21.8838 | 21.6374 | 21.267 | 20.5918 | 20.5597 | 20.9987 | 22.0806 | 21.6771 | 21.1867 | 21.9955 | 21.7288 | 21.3511 | 19.9246 | 21.0488 |  | 20.514 | 20.0689 | 20.1585 | 19.6394 |  | 17.0866 | 17.0051 | 16.715 | 16.8236 | 16.7982 | 17.0857 | 17.4214 | 15.5779 | 16.971 | 16.1692 | 16.9826 | 18.0157 | 47.5765 | 48.7355 | 46.2093 | 21.409 |  |  | 0.46547 | -0.023721 | -73.2613 | 0.76353 | 0.33592 | -197.8716 | 6.7094 | -0.30855 | 0.051662 | -0.27221 | -0.049532 | 8.8292 | 9.0592 | 1.979 | 21.7782 | 21.9992 | 22.1959 | 22.2601 | 22.0761 | 21.3909 | 20.207 | 22.2007 | 22.3725 | 22.4091 | 22.3567 | 21.9816 | 21.2146 | 22.2724 | 17.108 | 17.2077 | 16.1362 | 16.2282 | 16.259 | 17.1283 | 16.9053 | 22.3608 | 22.1288 | 21.6893 | 22.0756 | 21.7868 | 21.2981 | 21.9408 | 21.5218 | 20.899 | 20.0804 | 20.5662 | 19.9348 | 19.8564 | -0.17123 | -0.13007 | 20.7272 | 22.0687 | 22.3715 | 20.1331 | 21.6604 | 22.1095 | 21.9424 | 21.7035 | 21.2763 | 21.7773 | 21.4414 | 21.0352 | 20.2782 | 20.7699 | 20.2386 | 20.2453 | 20.1115 |  | 20.2082 | 19.6971 | 20.1183 | 19.7126 | 20.0885 | 20.3316 |  | 20.3911 |  |  | 20.3003 | 20.3514 | 20.6207 | [5 empty] | 21.9129 | 20.3453 | 21.658 | 22.0359 | 19.6252 | 21.1537 | 21.77 | 19.4162 | 19.9943 | 22.202 |  | 19.6928 | 20.9189 | 18.9234 | 19.7384 | 21.0048 | 19.4193 | 20.153 | 19.0148 | 20.0879 | 19.1589 | 20.1592 | 18.7778 | 20.0343 | 20.9991 | 19.4459 | 19.7516 | 21.3654 | 18.8896 | 19.8256 | 20.9389 | 18.8748 | 20.0672 | 19.295 | 20.2056 | 18.9579 | 20.2257 | -0.22811 | 20.9482 | 0.047442 | 0.013497 | -27.127 | 3.0957 | -9.68 | -0.15 | 0.81545 | -0.18283 | -10.1606 | 1.0373 | 0.68811 | -16.7007 | 3.0753 | 0.42262 | 0.43111 | 0.42969 | 0.40482 | 0.4868 | 0.42623 | 0.42542
42838.4194 | -74 | 22.903 | 22.8741 | 22.8563 | 22.7773 | 22.4097 | 21.7446 | 22.7218 | 21.8038 | 22.3699 | 22.3805 | 22.3584 | 22.0278 | 21.2398 | 22.2064 | 21.5993 | 21.7715 | 21.8924 | 21.0859 | 21.1793 | 21.3962 | 20.4766 | 20.6243 | 20.913 | 21.8843 | 21.6401 | 21.2712 | 20.5968 | 20.5723 | 21.0066 | 22.0866 | 21.6807 | 21.1935 | 22.0031 | 21.7373 | 21.3577 | 19.9305 | 21.057 |  | 20.5227 | 20.0743 | 20.1731 | 19.6373 |  | 17.0788 | 16.9893 | 16.7077 | 16.814 | 16.7916 | 17.0717 | 17.397 | 15.5304 | 16.9756 | 16.1547 | 16.9808 | 18.014 | 47.5315 | 48.6564 | 46.1969 | 21.404 |  |  | 0.36361 | -0.080889 | -72.2454 | 0.73264 | 0.27086 | -197.8 | 7.0577 | -0.27504 | 0.024224 | -0.28878 | -0.12678 | 8.8289 | 9.0588 | 1.9788 | 21.7648 | 21.9934 | 22.1888 | 22.251 | 22.0773 | 21.3936 | 20.2027 | 22.1918 | 22.3647 | 22.3983 | 22.3506 | 21.9791 | 21.2097 | 22.2751 | 17.1048 | 17.1964 | 16.1426 | 16.2441 | 16.2679 | 17.1333 | 16.9163 | 22.3622 | 22.1304 | 21.6926 | 22.0728 | 21.7917 | 21.3024 | 21.9443 | 21.5198 | 20.902 | 20.0884 | 20.5739 | 19.9564 | 19.8546 | -0.045599 | -0.14642 | 20.717 | 22.0675 | 22.3693 | 20.1318 | 21.6666 | 22.1068 | 21.9404 | 21.7022 | 21.2701 | 21.7747 | 21.4399 | 21.0342 | 20.2928 | 20.7746 | 20.2359 | 20.2353 | 20.1256 |  | 20.2113 | 19.7249 | 20.1275 | 19.7237 | 20.0961 | 20.3433 |  | 20.401 |  |  | 20.2866 | 20.3412 | 20.6149 | [5 empty] | 21.9073 | 20.3358 | 21.6529 | 22.0237 | 19.6231 | 21.1477 | 21.7686 | 19.4114 | 19.9901 | 22.2075 |  | 19.6924 | 20.9169 | 18.9223 | 19.7286 | 20.9945 | 19.4274 | 20.1484 | 19.0119 | 20.0787 | 19.1527 | 20.1512 | 18.7745 | 20.0333 | 20.9929 | 19.446 | 19.7518 | 21.3613 | 18.8909 | 19.824 | 20.9538 | 18.874 | 20.0545 | 19.2934 | 20.2037 | 18.9557 | 20.2289 | -0.020723 | 20.9471 | 0.046969 | 0.012974 | -27.1143 | 3.0957 | 11.36 | -0.03 | 0.72074 | -0.33761 | -10.0896 | 1.0161 | 0.61788 | -16.6973 | 3.154 | 0.42233 | 0.43065 | 0.42963 | 0.40576 | 0.48736 | 0.42649 | 0.42574
42838.4194 | -73 | 22.9006 | 22.8695 | 22.8513 | 22.7775 | 22.4034 | 21.7381 | 22.7182 | 21.8065 | 22.3658 | 22.3716 | 22.3501 | 22.0187 | 21.239 | 22.2092 | 21.596 | 21.7698 | 21.887 | 21.0791 | 21.1707 | 21.3908 | 20.4753 | 20.611 | 20.9025 | 21.8817 | 21.6379 | 21.2613 | 20.5978 | 20.5701 | 21.0089 | 22.0784 | 21.675 | 21.194 | 22.0013 | 21.739 | 21.3555 | 19.9281 | 21.0539 |  | 20.5162 | 20.0769 | 20.1796 | 19.6138 |  | 17.0736 | 16.9741 | 16.6952 | 16.8098 | 16.7778 | 17.0538 | 17.3623 | 15.4993 | 16.9797 | 16.1498 | 16.9909 | 18.013 | 47.491 | 48.5797 | 46.1785 | 21.4065 |  |  | 0.33339 | -0.21231 | -71.2617 | 0.44022 | 0.21632 | -197.8709 | 7.6333 | -0.28161 | -0.35661 | -0.073319 | -0.078697 | 8.8276 | 9.0575 | 1.9791 | 21.7788 | 21.9948 | 22.1927 | 22.2602 | 22.0816 | 21.3959 | 20.2053 | 22.1931 | 22.3725 | 22.4052 | 22.3586 | 21.9871 | 21.2098 | 22.2713 | 17.0783 | 17.1675 | 16.1212 | 16.2409 | 16.2709 | 17.1307 | 16.9072 | 22.3757 | 22.1372 | 21.6991 | 22.0783 | 21.7956 | 21.3041 | 21.9447 | 21.5288 | 20.9012 | 20.0924 | 20.5855 | 19.9749 | 19.8588 | -0.039111 | -0.46976 | 20.7159 | 22.0628 | 22.3618 | 20.1236 | 21.6541 | 22.104 | 21.9364 | 21.6959 | 21.2617 | 21.7691 | 21.4363 | 21.0308 | 20.2936 | 20.7924 | 20.226 | 20.2278 | 20.1069 |  | 20.2055 | 19.7295 | 20.1128 | 19.7209 | 20.0809 | 20.3414 |  | 20.3963 |  |  | 20.285 | 20.3442 | 20.6121 | [5 empty] | 21.9098 | 20.3481 | 21.6539 | 22.0342 | 19.6308 | 21.1497 | 21.774 | 19.4158 | 19.9923 | 22.2139 |  | 19.6961 | 20.927 | 18.9209 | 19.7307 | 21.0118 | 19.4226 | 20.1435 | 19.0153 | 20.0847 | 19.1599 | 20.1505 | 18.7763 | 20.0189 | 21.0058 | 19.4494 | 19.7553 | 21.3743 | 18.8965 | 19.8222 | 20.9636 | 18.8916 | 20.0567 | 19.2991 | 20.2129 | 18.9567 | 20.2307 | -0.22385 | 20.948 | 0.046429 | 0.011529 | -27.0882 | 3.0957 | -22.84 | -0.12 | 0.69014 | -0.54695 | -10.0204 | 0.78758 | 0.55217 | -16.6997 | 3.28 | 0.42265 | 0.43003 | 0.4292 | 0.40841 | 0.48867 | 0.42706 | 0.42575
42838.4194 | -72 | 22.9092 | 22.8639 | 22.8526 | 22.7828 | 22.4018 | 21.7352 | 22.7218 | 21.8047 | 22.3633 | 22.3749 | 22.3509 | 22.011 | 21.2331 | 22.2133 | 21.5984 | 21.7664 | 21.8931 | 21.0832 | 21.1835 | 21.3991 | 20.4787 | 20.6148 | 20.9006 | 21.8818 | 21.6431 | 21.2685 | 20.6075 | 20.5882 | 21.0229 | 22.0813 | 21.6749 | 21.1943 | 22.0001 | 21.7421 | 21.3545 | 19.9331 | 21.0669 |  | 20.5232 | 20.0868 | 20.1871 | 19.5653 |  | 17.0538 | 16.956 | 16.6859 | 16.8007 | 16.7594 | 17.0321 | 17.3273 | 15.4263 | 16.9791 | 16.13 | 16.9876 | 18.0101 | 47.4517 | 48.4983 | 46.1507 | 21.4114 |  |  | 0.36296 | -0.34899 | -70.4016 | 0.50988 | 0.30832 | -197.8368 | 7.6294 | -0.17384 | -0.11686 | -0.105 | -0.013423 | 8.8286 | 9.0586 | 1.9787 | 21.7745 | 21.9984 | 22.1944 | 22.2642 | 22.0852 | 21.3984 | 20.2142 | 22.2017 | 22.3809 | 22.413 | 22.359 | 21.9829 | 21.2172 | 22.2785 | 17.0787 | 17.1636 | 16.1014 | 16.2499 | 16.293 | 17.1348 | 16.9162 | 22.3641 | 22.1347 | 21.6935 | 22.0802 | 21.7906 | 21.2944 | 21.9391 | 21.5179 | 20.9023 | 20.0857 | 20.5992 | 19.9875 | 19.8634 | 0.038742 | -0.19587 | 20.7209 | 22.0631 | 22.3621 | 20.1186 | 21.6552 | 22.1023 | 21.9409 | 21.7053 | 21.2716 | 21.7766 | 21.4379 | 21.0361 | 20.3061 | 20.8315 | 20.2276 | 20.2344 | 20.1125 |  | 20.2029 | 19.7359 | 20.117 | 19.7217 | 20.0864 | 20.3391 |  | 20.3937 |  |  | 20.2684 | 20.3493 | 20.6067 | [5 empty] | 21.9097 | 20.3444 | 21.6485 | 22.0238 | 19.6266 | 21.1462 | 21.7691 | 19.4091 | 19.9965 | 22.2268 |  | 19.7093 | 20.9353 | 18.9166 | 19.7351 | 21.0238 | 19.438 | 20.1558 | 19.0108 | 20.0913 | 19.1607 | 20.144 | 18.7808 | 20.0219 | 21.0035 | 19.4406 | 19.7489 | 21.3794 | 18.8924 | 19.8168 | 20.9738 | 18.8898 | 20.0561 | 19.2966 | 20.207 | 18.9486 | 20.2266 | -0.13573 | 20.9486 | 0.04641 | 0.011624 | -27.0876 | 3.0957 | -20.64 | -0.09 | 0.72011 | -0.70122 | -9.9595 | 0.84758 | 0.65918 | -16.6977 | 3.279 | 0.42241 | 0.42999 | 0.42936 | 0.40885 | 0.49193 | 0.42857 | 0.4254
42838.4195 | -71 | 22.8918 | 22.8644 | 22.8501 | 22.7778 | 22.3978 | 21.7336 | 22.7101 | 21.7972 | 22.3577 | 22.3703 | 22.3485 | 22.0146 | 21.2271 | 22.1996 | 21.5992 | 21.7586 | 21.8924 | 21.0803 | 21.183 | 21.3877 | 20.4681 | 20.6093 | 20.8993 | 21.8821 | 21.6364 | 21.2703 | 20.6101 | 20.5952 | 21.0406 | 22.0837 | 21.6735 | 21.1925 | 22.0077 | 21.7364 | 21.3529 | 19.9358 | 21.0696 |  | 20.522 | 20.0871 | 20.2105 | 19.5051 |  | 17.0535 | 16.9663 | 16.6795 | 16.7896 | 16.753 | 17.0195 | 17.3233 | 15.4012 | 16.9847 | 16.1167 | 16.9821 | 18.015 | 47.4058 | 48.4265 | 46.1167 | 21.4166 |  |  | 0.42735 | -0.33059 | -69.3029 | 0.25426 | 0.26692 | -197.8486 | 8.1406 | -0.11733 | -0.013723 | -0.18241 | 0.12146 | 8.8294 | 9.0594 | 1.9787 | 21.7674 | 21.9974 | 22.1985 | 22.257 | 22.0804 | 21.397 | 20.2078 | 22.1989 | 22.3719 | 22.4083 | 22.3647 | 21.9801 | 21.2188 | 22.2754 | 17.0837 | 17.1584 | 16.0932 | 16.2391 | 16.2723 | 17.1354 | 16.9116 | 22.3602 | 22.127 | 21.6847 | 22.076 | 21.7826 | 21.3023 | 21.9394 | 21.5147 | 20.8973 | 20.0832 | 20.6134 | 20.0003 | 19.8547 | 0.21234 | -0.1489 | 20.7213 | 22.0636 | 22.3652 | 20.1148 | 21.6584 | 22.1003 | 21.938 | 21.7068 | 21.2712 | 21.7769 | 21.4372 | 21.0364 | 20.3187 | 20.8644 | 20.234 | 20.2401 | 20.1164 |  | 20.2052 | 19.7435 | 20.1168 | 19.7226 | 20.088 | 20.3421 |  | 20.3959 |  |  | 20.2513 | 20.3565 | 20.5997 | [5 empty] | 21.9153 | 20.3484 | 21.654 | 22.0321 | 19.6285 | 21.1366 | 21.7664 | 19.4053 | 19.9911 | 22.2372 |  | 19.7085 | 20.9356 | 18.9133 | 19.7271 | 21.0366 | 19.4256 | 20.1531 | 19.0073 | 20.0889 | 19.158 | 20.1411 | 18.7717 | 20.023 | 21.0079 | 19.4506 | 19.7561 | 21.3886 | 18.891 | 19.8268 | 20.987 | 18.9065 | 20.0776 | 19.2857 | 20.2187 | 18.9468 | 20.2415 | 0.030104 | 20.949 | 0.047092 | 0.01338 | -27.066 | 3.0957 | -11.39 | -0.04 | 0.7814 | -0.6825 | -9.8816 | 0.59854 | 0.61331 | -16.6978 | 3.387 | 0.42238 | 0.42977 | 0.42939 | 0.40835 | 0.49231 | 0.43034 | 0.42556
42838.4195 | -70 | 22.9082 | 22.8696 | 22.8524 | 22.7786 | 22.4042 | 21.7436 | 22.7187 | 21.801 | 22.3701 | 22.3775 | 22.353 | 22.0225 | 21.2333 | 22.2071 | 21.5907 | 21.7563 | 21.8852 | 21.0743 | 21.1747 | 21.3859 | 20.469 | 20.6065 | 20.906 | 21.8708 | 21.6306 | 21.2614 | 20.6114 | 20.5959 | 21.0355 | 22.0705 | 21.6662 | 21.1876 | 21.9873 | 21.7252 | 21.3409 | 19.9243 | 21.0804 |  | 20.5142 | 20.09 | 20.2052 | 19.4474 |  | 17.063 | 16.9728 | 16.6727 | 16.777 | 16.7458 | 17.0172 | 17.3491 | 15.3891 | 16.9817 | 16.0908 | 16.9837 | 18.0146 | 47.3578 | 48.3549 | 46.0767 | 21.4318 |  |  | 0.54367 | -0.35359 | -68.3875 | 0.39751 | 0.3438 | -197.8539 | 8.7478 | -0.11733 | -0.091758 | -0.40082 | 0.010013 | 8.8285 | 9.0581 | 1.9787 | 21.7758 | 22.0049 | 22.2019 | 22.2547 | 22.0819 | 21.3918 | 20.2056 | 22.2018 | 22.3694 | 22.4105 | 22.3631 | 21.9818 | 21.218 | 22.276 | 17.0746 | 17.185 | 16.0924 | 16.2234 | 16.2555 | 17.1347 | 16.9065 | 22.3635 | 22.1321 | 21.6943 | 22.0801 | 21.7855 | 21.3041 | 21.939 | 21.5266 | 20.8985 | 20.0915 | 20.6274 | 20.0034 | 19.8539 | 0.063317 | 0.022094 | 20.7211 | 22.0637 | 22.3643 | 20.1098 | 21.6531 | 22.1058 | 21.946 | 21.7051 | 21.2745 | 21.779 | 21.4374 | 21.0392 | 20.3241 | 20.9012 | 20.2417 | 20.2418 | 20.1151 |  | 20.2053 | 19.7467 | 20.1145 | 19.7354 | 20.0802 | 20.3404 |  | 20.3997 |  |  | 20.2447 | 20.3473 | 20.6036 | [5 empty] | 21.9139 | 20.3523 | 21.6509 | 22.0315 | 19.6277 | 21.1471 | 21.7692 | 19.4081 | 19.989 | 22.277 |  | 19.715 | 20.921 | 18.9078 | 19.725 | 21.0443 | 19.4237 | 20.1584 | 19.0067 | 20.091 | 19.157 | 20.134 | 18.7794 | 20.0393 | 21.0172 | 19.4525 | 19.7611 | 21.4028 | 18.9037 | 19.8297 | 20.9977 | 18.9026 | 20.0855 | 19.2997 | 20.2235 | 18.9589 | 20.2339 | -0.13258 | 20.9482 | 0.047885 | 0.01293 | -26.9964 | 3.0957 | -9.21 | -0.06 | 0.88134 | -0.70585 | -9.8163 | 0.7484 | 0.69606 | -16.698 | 3.5111 | 0.42242 | 0.42961 | 0.42877 | 0.40928 | 0.49179 | 0.43155 | 0.42586
42838.4195 | -69 | 22.9081 | 22.8683 | 22.8517 | 22.7819 | 22.4064 | 21.7449 | 22.723 | 21.8009 | 22.3753 | 22.3725 | 22.3525 | 22.0258 | 21.2348 | 22.2096 | 21.5948 | 21.7606 | 21.8911 | 21.0818 | 21.1816 | 21.3943 | 20.471 | 20.6126 | 20.901 | 21.8692 | 21.6356 | 21.2608 | 20.6251 | 20.6074 | 21.0525 | 22.0755 | 21.6745 | 21.1951 | 22.0031 | 21.7353 | 21.3546 | 19.9349 | 21.1086 |  | 20.5242 | 20.0988 | 20.2205 | 19.4131 |  | 17.0545 | 16.9617 | 16.6569 | 16.7648 | 16.7369 | 17.0467 | 17.3677 | 15.3795 | 16.9793 | 16.064 | 16.974 | 18.0184 | 47.3182 | 48.291 | 46.044 | 21.4348 |  |  | 0.40239 | -0.17683 | -67.2914 | 0.29697 | 0.27218 | -197.8309 | 8.9607 | -0.10878 | 0.19333 | -0.2592 | 0.010013 | 8.8285 | 9.0584 | 1.9785 | 21.7748 | 22.0004 | 22.1899 | 22.2471 | 22.0788 | 21.3904 | 20.2015 | 22.1905 | 22.3695 | 22.4084 | 22.3514 | 21.9764 | 21.2159 | 22.2716 | 17.0637 | 17.1897 | 16.0918 | 16.2173 | 16.2531 | 17.1292 | 16.9065 | 22.368 | 22.1313 | 21.6907 | 22.0783 | 21.7902 | 21.3003 | 21.9432 | 21.5214 | 20.8993 | 20.0856 | 20.6412 | 20.0039 | 19.859 | 0.010825 | -0.1877 | 20.7268 | 22.0682 | 22.3739 | 20.1051 | 21.6539 | 22.1035 | 21.9441 | 21.7073 | 21.2754 | 21.7775 | 21.4412 | 21.0389 | 20.3315 | 20.94 | 20.2477 | 20.2418 | 20.1167 |  | 20.2065 | 19.7508 | 20.1117 | 19.7329 | 20.0852 | 20.3413 |  | 20.3987 |  |  | 20.253 | 20.3414 | 20.6016 | [5 empty] | 21.9198 | 20.3523 | 21.6547 | 22.027 | 19.6379 | 21.1549 | 21.7711 | 19.4056 | 19.9836 | 22.2901 |  | 19.7007 | 20.9293 | 18.9015 | 19.7161 | 21.0588 | 19.4173 | 20.1587 | 19.0008 | 20.0818 | 19.151 | 20.1341 | 18.7811 | 20.0355 | 21.0186 | 19.4522 | 19.7554 | 21.4079 | 18.9026 | 19.8283 | 21.0003 | 18.908 | 20.0859 | 19.2934 | 20.2358 | 18.9641 | 20.2381 | -0.1528 | 20.9485 | 0.049144 | 0.012132 | -27.0614 | 3.0957 | -3.38 | -0.04 | 0.75825 | -0.49914 | -9.7371 | 0.64686 | 0.61935 | -16.6978 | 3.5537 | 0.42241 | 0.4294 | 0.42901 | 0.40986 | 0.49186 | 0.43286 | 0.42552
42838.4195 | -68 | 22.9065 | 22.8659 | 22.8545 | 22.7815 | 22.4087 | 21.7477 | 22.7221 | 21.8038 | 22.3665 | 22.3759 | 22.3597 | 22.0234 | 21.233 | 22.21 | 21.5958 | 21.7664 | 21.8977 | 21.0789 | 21.1801 | 21.3968 | 20.4721 | 20.6044 | 20.8976 | 21.8706 | 21.6352 | 21.2685 | 20.632 | 20.6121 | 21.0552 | 22.072 | 21.6752 | 21.1894 | 21.9989 | 21.7386 | 21.3495 | 19.9336 | 21.1208 |  | 20.5232 | 20.0932 | 20.219 | 19.3967 |  | 17.0448 | 16.9514 | 16.6609 | 16.761 | 16.7472 | 17.0767 | 17.4002 | 15.4011 | 16.98 | 16.0662 | 16.9837 | 18.0156 | 47.2603 | 48.2124 | 46.0072 | 21.4266 |  |  | 0.43195 | -0.31811 | -65.9877 | 0.3042 | 0.30635 | -197.8572 | 9.2538 | -0.15018 | -0.033572 | 0.029693 | 0.051677 | 8.8296 | 9.0593 | 1.9786 | 21.7733 | 21.9969 | 22.1842 | 22.2471 | 22.0716 | 21.3902 | 20.2026 | 22.1879 | 22.3671 | 22.4063 | 22.3555 | 21.9764 | 21.2123 | 22.2675 | 17.0611 | 17.1673 | 16.0928 | 16.2039 | 16.2429 | 17.1385 | 16.9111 | 22.3706 | 22.132 | 21.6915 | 22.0812 | 21.7914 | 21.2902 | 21.9429 | 21.5173 | 20.903 | 20.0877 | 20.6685 | 20.0055 | 19.8556 | 0.0004054 | -0.25731 | 20.7225 | 22.0677 | 22.3702 | 20.1019 | 21.6584 | 22.1 | 21.9374 | 21.7027 | 21.2687 | 21.7681 | 21.4368 | 21.0301 | 20.3442 | 20.9668 | 20.2471 | 20.2469 | 20.1132 |  | 20.2003 | 19.7636 | 20.113 | 19.7329 | 20.0905 | 20.3398 |  | 20.3951 |  |  | 20.2478 | 20.3348 | 20.6034 | [5 empty] | 21.9221 | 20.3488 | 21.6469 | 22.0228 | 19.6339 | 21.1527 | 21.7688 | 19.4156 | 20.0001 | 22.3075 |  | 19.7155 | 20.9356 | 18.904 | 19.7301 | 21.0824 | 19.4303 | 20.1612 | 19.0073 | 20.0889 | 19.1577 | 20.1392 | 18.7808 | 20.0338 | 21.0148 | 19.4524 | 19.7559 | 21.4159 | 18.9052 | 19.8246 | 21.0048 | 18.9076 | 20.0876 | 19.2929 | 20.2241 | 18.9521 | 20.2289 | -0.14241 | 20.9489 | 0.04912 | 0.013743 | -27.1667 | 3.0957 | -25.88 | -0.13 | 0.78562 | -0.66947 | -9.6421 | 0.65467 | 0.65712 | -16.6998 | 3.6116 | 0.4223 | 0.42909 | 0.42919 | 0.41122 | 0.49228 | 0.43327 | 0.42569
42838.4195 | -67 | 22.9 | 22.8709 | 22.8559 | 22.7799 | 22.4088 | 21.7419 | 22.7148 | 21.8052 | 22.3645 | 22.379 | 22.3632 | 22.0225 | 21.2333 | 22.2112 | 21.5977 | 21.7718 | 21.9006 | 21.0881 | 21.1858 | 21.3989 | 20.4849 | 20.6165 | 20.9116 | 21.8833 | 21.655 | 21.271 | 20.6485 | 20.6329 | 21.089 | 22.0741 | 21.6784 | 21.1979 | 21.9957 | 21.7374 | 21.3484 | 19.9386 | 21.1548 |  | 20.5285 | 20.0995 | 20.2178 | 19.3889 |  | 17.0456 | 16.952 | 16.6578 | 16.7637 | 16.753 | 17.1269 | 17.4477 | 15.4432 | 16.9802 | 16.0845 | 16.9887 | 18.0041 | 47.1925 | 48.1403 | 45.945 | 21.4197 |  |  | 0.27491 | -0.43376 | -65.5067 | 0.64065 | 0.22289 | -197.7987 | 9.0566 | -0.24546 | 0.13573 | 0.1134 | 0.14316 | 8.8281 | 9.0578 | 1.9787 | 21.7726 | 22.0036 | 22.1902 | 22.2513 | 22.0789 | 21.4034 | 20.2077 | 22.1988 | 22.3758 | 22.407 | 22.354 | 21.972 | 21.2181 | 22.273 | 17.0556 | 17.1592 | 16.0907 | 16.2019 | 16.235 | 17.1352 | 16.9067 | 22.3662 | 22.1304 | 21.6939 | 22.0747 | 21.7889 | 21.2954 | 21.9404 | 21.5126 | 20.9007 | 20.0883 | 20.6928 | 20.0007 | 19.8476 | 0.026946 | -0.19778 | 20.7186 | 22.0642 | 22.3615 | 20.0952 | 21.6516 | 22.0997 | 21.9327 | 21.6959 | 21.2653 | 21.7648 | 21.4337 | 21.0324 | 20.3629 | 20.9901 | 20.2445 | 20.252 | 20.1186 |  | 20.2059 | 19.778 | 20.1147 | 19.7412 | 20.0833 | 20.3398 |  | 20.3987 |  |  | 20.246 | 20.324 | 20.6084 | [5 empty] | 21.9149 | 20.3521 | 21.649 | 22.0258 | 19.6355 | 21.1456 | 21.771 | 19.4137 | 19.9989 | 22.3092 |  | 19.7206 | 20.9462 | 18.9033 | 19.7337 | 21.0837 | 19.4274 | 20.1623 | 19.0121 | 20.0767 | 19.1585 | 20.1464 | 18.7785 | 20.0333 | 21.0203 | 19.4484 | 19.7567 | 21.4349 | 18.9135 | 19.8319 | 21.0073 | 18.9173 | 20.0933 | 19.3049 | 20.2336 | 18.953 | 20.2357 | 0.027692 | 20.9498 | 0.04947 | 0.014615 | -27.2837 | 3.0957 | -4.93 | -0.15 | 0.62677 | -0.78175 | -9.6069 | 0.95006 | 0.56056 | -16.6988 | 3.5732 | 0.42234 | 0.42875 | 0.42872 | 0.41144 | 0.49201 | 0.43366 | 0.42593
42838.4195 | -66 | 22.9007 | 22.8638 | 22.859 | 22.7747 | 22.3991 | 21.7321 | 22.7089 | 21.801 | 22.3685 | 22.3785 | 22.3536 | 22.0184 | 21.2288 | 22.2046 | 21.592 | 21.7615 | 21.8967 | 21.0815 | 21.1815 | 21.3957 | 20.4804 | 20.6181 | 20.9106 | 21.8832 | 21.65 | 21.2681 | 20.6505 | 20.6382 | 21.0982 | 22.0829 | 21.6791 | 21.2024 | 21.9984 | 21.7389 | 21.3577 | 19.9388 | 21.1785 |  | 20.5344 | 20.105 | 20.2241 | 19.3628 |  | 17.0481 | 16.946 | 16.6451 | 16.7644 | 16.7813 | 17.1771 | 17.4441 | 15.4881 | 16.9907 | 16.106 | 16.9907 | 18.0142 | 47.126 | 48.0699 | 45.8927 | 21.4157 |  |  | 0.27359 | -0.26225 | -64.523 | 0.51645 | 0.35234 | -197.8361 | 9.4956 | -0.25729 | 0.053025 | -0.24808 | 0.014006 | 8.8277 | 9.0577 | 1.9785 | 21.7793 | 22.0033 | 22.1929 | 22.2506 | 22.0764 | 21.3973 | 20.2098 | 22.1944 | 22.3654 | 22.4083 | 22.356 | 21.9817 | 21.2141 | 22.2732 | 17.0367 | 17.1693 | 16.0889 | 16.2002 | 16.2369 | 17.1305 | 16.8998 | 22.3726 | 22.1402 | 21.7 | 22.0771 | 21.7963 | 21.2992 | 21.9462 | 21.5236 | 20.9052 | 20.0968 | 20.7151 | 20.0096 | 19.8647 | 0.13449 | -0.14775 | 20.7214 | 22.0659 | 22.361 | 20.0955 | 21.6488 | 22.0987 | 21.9367 | 21.702 | 21.2694 | 21.772 | 21.433 | 21.0375 | 20.3745 | 20.9905 | 20.2466 | 20.2584 | 20.1074 |  | 20.1976 | 19.7947 | 20.1111 | 19.7373 | 20.0836 | 20.3486 |  | 20.3958 |  |  | 20.2559 | 20.3223 | 20.611 | [5 empty] | 21.9135 | 20.3507 | 21.6567 | 22.0293 | 19.6379 | 21.1433 | 21.7762 | 19.41 | 19.9979 | 22.3234 |  | 19.7274 | 20.9583 | 18.9033 | 19.7335 | 21.102 | 19.4249 | 20.1634 | 19.0195 | 20.0842 | 19.1597 | 20.159 | 18.774 | 20.04 | 21.0259 | 19.4479 | 19.7569 | 21.4392 | 18.9082 | 19.8241 | 21.0036 | 18.9174 | 20.097 | 19.2991 | 20.2365 | 18.9554 | 20.2318 | -0.037789 | 20.9495 | 0.04955 | 0.014346 | -27.0615 | 3.0956 | -2.81 | -0.04 | 0.62528 | -0.60785 | -9.5344 | 0.85301 | 0.70485 | -16.7018 | 3.6591 | 0.42237 | 0.42816 | 0.42884 | 0.413 | 0.4914 | 0.43439 | 0.42574
42838.4195 | -65 | 22.9015 | 22.8643 | 22.8583 | 22.7752 | 22.4046 | 21.743 | 22.7128 | 21.805 | 22.3647 | 22.3763 | 22.3511 | 22.0129 | 21.2312 | 22.2046 | 21.5912 | 21.7656 | 21.8895 | 21.081 | 21.1844 | 21.3949 | 20.4762 | 20.6139 | 20.9066 | 21.8772 | 21.6423 | 21.266 | 20.6546 | 20.6384 | 21.1095 | 22.0747 | 21.6705 | 21.1912 | 21.9938 | 21.7358 | 21.3523 | 19.9292 | 21.1964 |  | 20.5298 | 20.0983 | 20.2161 | 19.3196 |  | 17.0336 | 16.9388 | 16.6395 | 16.7828 | 16.7946 | 17.1871 | 17.4198 | 15.549 | 16.9761 | 16.1223 | 16.9909 | 18.0086 | 47.0668 | 47.9997 | 45.838 | 21.4176 |  |  | 0.31236 | -0.15515 | -63.8547 | 0.26149 | 0.34249 | -197.8591 | 9.5501 | -0.32169 | 0.096615 | -0.079403 | 0.063134 | 8.8281 | 9.0577 | 1.9785 | 21.7675 | 21.9919 | 22.1736 | 22.2448 | 22.0684 | 21.3807 | 20.197 | 22.1834 | 22.363 | 22.4014 | 22.3465 | 21.9731 | 21.1998 | 22.2625 | 17.02 | 17.1204 | 16.0765 | 16.1907 | 16.2411 | 17.1297 | 16.8957 | 22.3679 | 22.1344 | 21.6966 | 22.0748 | 21.7837 | 21.302 | 21.9416 | 21.5249 | 20.901 | 20.0931 | 20.7258 | 20.0014 | 19.8529 | 0.029502 | -0.061784 | 20.7218 | 22.0635 | 22.3628 | 20.0957 | 21.6518 | 22.0957 | 21.933 | 21.7009 | 21.2677 | 21.7649 | 21.4298 | 21.0342 | 20.3812 | 20.9943 | 20.2484 | 20.2654 | 20.1035 |  | 20.207 | 19.8102 | 20.1133 | 19.7457 | 20.0902 | 20.3472 |  | 20.3953 |  |  | 20.2556 | 20.3197 | 20.6095 | [5 empty] | 21.9124 | 20.3516 | 21.6499 | 22.0254 | 19.6342 | 21.1455 | 21.7745 | 19.4103 | 20.0062 | 22.358 |  | 19.7257 | 20.9589 | 18.9109 | 19.7342 | 21.1245 | 19.4245 | 20.1656 | 19.0216 | 20.0842 | 19.1637 | 20.1746 | 18.7715 | 20.0361 | 21.0324 | 19.4553 | 19.7606 | 21.4512 | 18.9062 | 19.8256 | 21.0114 | 18.929 | 20.1082 | 19.3026 | 20.2386 | 18.9629 | 20.2278 | -0.19138 | 20.9488 | 0.049876 | 0.015159 | -27.2134 | 3.0956 | -16.01 | -0.07 | 0.66813 | -0.46752 | -9.4848 | 0.60696 | 0.69493 | -16.7031 | 3.6696 | 0.4228 | 0.42781 | 0.42882 | 0.41477 | 0.4923 | 0.43527 | 0.42594
42838.4195 | -64 | 22.8968 | 22.8616 | 22.8548 | 22.7707 | 22.3956 | 21.7381 | 22.7055 | 21.7977 | 22.362 | 22.3772 | 22.3509 | 22.0173 | 21.2229 | 22.1994 | 21.5904 | 21.7633 | 21.8878 | 21.0799 | 21.1764 | 21.3882 | 20.4735 | 20.6095 | 20.899 | 21.8688 | 21.6444 | 21.2672 | 20.6654 | 20.6444 | 21.1255 | 22.0743 | 21.6694 | 21.194 | 22.0003 | 21.7338 | 21.3451 | 19.9358 | 21.217 |  | 20.5299 | 20.1052 | 20.22 | 19.3033 |  | 17.0277 | 16.9359 | 16.6411 | 16.7953 | 16.7846 | 17.1768 | 17.411 | 15.6116 | 16.9757 | 16.1048 | 16.9878 | 18.0072 | 47.0138 | 47.9326 | 45.786 | 21.4179 |  |  | 0.35047 | -0.33716 | -62.9952 | 0.34231 | 0.24655 | -197.8453 | 10.0081 | -0.23692 | 0.22155 | -0.37732 | 0.084314 | 8.8285 | 9.0584 | 1.979 | 21.765 | 21.9853 | 22.1774 | 22.2482 | 22.0727 | 21.3824 | 20.1989 | 22.1886 | 22.3607 | 22.3967 | 22.3516 | 21.9717 | 21.2019 | 22.269 | 17.018 | 17.1204 | 16.0517 | 16.181 | 16.2545 | 17.1285 | 16.9023 | 22.3699 | 22.1263 | 21.692 | 22.0765 | 21.7896 | 21.2979 | 21.9452 | 21.5246 | 20.9049 | 20.0931 | 20.7407 | 19.9893 | 19.8502 | 0.13979 | -0.069392 | 20.7276 | 22.0626 | 22.3684 | 20.0965 | 21.6551 | 22.1013 | 21.9405 | 21.6974 | 21.2715 | 21.7773 | 21.4344 | 21.0382 | 20.3989 | 21.0205 | 20.2659 | 20.2849 | 20.0982 |  | 20.2077 | 19.8239 | 20.1122 | 19.7597 | 20.0862 | 20.345 |  | 20.4027 |  |  | 20.2604 | 20.3189 | 20.6138 | [5 empty] | 21.9166 | 20.3455 | 21.6501 | 22.029 | 19.6358 | 21.1502 | 21.7664 | 19.412 | 20.008 | 22.3767 |  | 19.7293 | 20.9645 | 18.9097 | 19.7349 | 21.145 | 19.4295 | 20.1616 | 19.0217 | 20.0807 | 19.1614 | 20.1768 | 18.7746 | 20.0386 | 21.0377 | 19.462 | 19.7567 | 21.4537 | 18.9111 | 19.8259 | 21.017 | 18.9307 | 20.1132 | 19.3065 | 20.2374 | 18.9677 | 20.2276 | -0.12163 | 20.9462 | 0.049716 | 0.01574 | -27.0774 | 3.0956 | -10.54 | -0.07 | 0.70774 | -0.68921 | -9.4207 | 0.69445 | 0.58961 | -16.7022 | 3.7565 | 0.42297 | 0.42739 | 0.4283 | 0.41485 | 0.49583 | 0.43594 | 0.42602
42838.4195 | -63 | 22.9004 | 22.8726 | 22.8545 | 22.775 | 22.4072 | 21.7452 | 22.7205 | 21.8031 | 22.3683 | 22.3742 | 22.3577 | 22.0244 | 21.2371 | 22.2129 | 21.5871 | 21.7621 | 21.8888 | 21.0741 | 21.1717 | 21.3865 | 20.471 | 20.6056 | 20.8996 | 21.8729 | 21.6316 | 21.2657 | 20.6767 | 20.6528 | 21.1494 | 22.0716 | 21.6696 | 21.1866 | 21.99 | 21.7326 | 21.3515 | 19.9322 | 21.2325 |  | 20.5285 | 20.1014 | 20.2035 | 19.2731 |  | 17.0214 | 16.9342 | 16.6411 | 16.7982 | 16.7877 | 17.2108 | 17.4073 | 15.678 | 16.9818 | 16.0952 | 16.9791 | 18.007 | 46.9485 | 47.8655 | 45.7286 | 21.422 |  |  | 0.3255 | -0.079577 | -62.273 | 0.30354 | 0.23209 | -197.8512 | 9.9451 | -0.24612 | 0.019748 | 0.056757 | -0.041026 | 8.8285 | 9.0584 | 1.9788 | 21.7725 | 21.9968 | 22.1958 | 22.2533 | 22.0749 | 21.386 | 20.2006 | 22.1949 | 22.3678 | 22.402 | 22.3537 | 21.9734 | 21.2096 | 22.274 | 17.0287 | 17.1909 | 16.0379 | 16.1891 | 16.2556 | 17.1336 | 16.9014 | 22.3625 | 22.1259 | 21.6888 | 22.0726 | 21.7862 | 21.2928 | 21.9425 | 21.5191 | 20.8946 | 20.0878 | 20.7416 | 19.988 | 19.8557 | 0.03481 | -0.093167 | 20.7308 | 22.0649 | 22.366 | 20.1025 | 21.6565 | 22.1055 | 21.9347 | 21.7052 | 21.2727 | 21.7754 | 21.4371 | 21.0418 | 20.4088 | 21.0634 | 20.2765 | 20.2875 | 20.0928 |  | 20.2111 | 19.8346 | 20.1221 | 19.7635 | 20.0903 | 20.3602 |  | 20.4053 |  |  | 20.2654 | 20.3167 | 20.6181 | [5 empty] | 21.9141 | 20.3455 | 21.6496 | 22.0231 | 19.6368 | 21.1511 | 21.7685 | 19.4148 | 20.0023 | 22.385 |  | 19.7299 | 20.9752 | 18.9019 | 19.7299 | 21.1605 | 19.4298 | 20.1622 | 19.0305 | 20.0841 | 19.1604 | 20.1798 | 18.7779 | 20.0397 | 21.0467 | 19.4623 | 19.7632 | 21.4479 | 18.9197 | 19.8327 | 21.0191 | 18.9284 | 20.1074 | 19.3043 | 20.2412 | 18.9687 | 20.2255 | -0.17005 | 20.9478 | 0.049691 | 0.016088 | -27.0463 | 3.0956 | -18.73 | -0.06 | 0.68208 | -0.33483 | -9.3665 | 0.65394 | 0.57209 | -16.7034 | 3.7449 | 0.42323 | 0.42742 | 0.42833 | 0.41425 | 0.49726 | 0.43666 | 0.42569
42838.4196 | -62 | 22.903 | 22.8644 | 22.8467 | 22.7779 | 22.4057 | 21.7395 | 22.7125 | 21.8014 | 22.3633 | 22.3704 | 22.3565 | 22.0214 | 21.2367 | 22.2054 | 21.5874 | 21.7629 | 21.8894 | 21.0743 | 21.1743 | 21.3901 | 20.4674 | 20.6104 | 20.9017 | 21.8754 | 21.635 | 21.266 | 20.6826 | 20.671 | 21.1902 | 22.0802 | 21.6834 | 21.1922 | 21.9957 | 21.7358 | 21.355 | 19.9337 | 21.2227 |  | 20.543 | 20.1094 | 20.2162 | 19.2589 |  | 17.0184 | 16.9342 | 16.6345 | 16.7934 | 16.8018 | 17.2325 | 17.4258 | 15.7051 | 16.9772 | 16.0988 | 16.9884 | 18.0102 | 46.869 | 47.804 | 45.6733 | 21.4229 |  |  | 0.44378 | -0.2202 | -61.5167 | 0.47308 | 0.26824 | -197.8598 | 10.3512 | -0.11667 | -0.043692 | -0.1264 | 0.088827 | 8.8291 | 9.0589 | 1.9789 | 21.7715 | 21.9959 | 22.1924 | 22.2516 | 22.0702 | 21.3856 | 20.1998 | 22.1913 | 22.3667 | 22.3993 | 22.3534 | 21.9738 | 21.2074 | 22.2689 | 17.0205 | 17.2086 | 16.034 | 16.1899 | 16.2513 | 17.1325 | 16.8963 | 22.3647 | 22.1421 | 21.6916 | 22.074 | 21.7931 | 21.3049 | 21.9413 | 21.5207 | 20.8981 | 20.0914 | 20.7626 | 19.9835 | 19.8608 | -0.1032 | -0.11314 | 20.7348 | 22.0622 | 22.3728 | 20.0989 | 21.6618 | 22.1062 | 21.9368 | 21.7095 | 21.2707 | 21.7733 | 21.4449 | 21.0411 | 20.4257 | 21.0865 | 20.2816 | 20.2947 | 20.0895 |  | 20.2026 | 19.8407 | 20.1076 | 19.7635 | 20.0789 | 20.3522 |  | 20.3957 |  |  | 20.2695 | 20.3197 | 20.6165 | [5 empty] | 21.9137 | 20.3504 | 21.6545 | 22.0215 | 19.6444 | 21.1537 | 21.7748 | 19.4102 | 19.9972 | 22.3882 |  | 19.7312 | 20.9738 | 18.907 | 19.7337 | 21.1797 | 19.4261 | 20.1532 | 19.0262 | 20.0875 | 19.1672 | 20.1856 | 18.7767 | 20.0345 | 21.0459 | 19.4631 | 19.7597 | 21.4534 | 18.9193 | 19.8287 | 21.0219 | 18.9263 | 20.1053 | 19.3027 | 20.2421 | 18.97 | 20.2248 | -0.14371 | 20.948 | 0.049728 | 0.016052 | -27.0382 | 3.0956 | 3.51 | 0.05 | 0.79648 | -0.55698 | -9.3095 | 0.81639 | 0.61505 | -16.7044 | 3.8207 | 0.42304 | 0.42677 | 0.42795 | 0.41504 | 0.4971 | 0.4371 | 0.42567
42838.4196 | -61 | 22.9 | 22.8614 | 22.8447 | 22.7755 | 22.4009 | 21.7328 | 22.7041 | 21.7957 | 22.3599 | 22.3697 | 22.3507 | 22.0139 | 21.2335 | 22.1998 | 21.5934 | 21.7724 | 21.8992 | 21.0832 | 21.1863 | 21.4022 | 20.4693 | 20.6182 | 20.9046 | 21.8839 | 21.6459 | 21.2732 | 20.7076 | 20.6915 | 21.2361 | 22.0781 | 21.6795 | 21.1921 | 21.9976 | 21.7455 | 21.355 | 19.9421 | 21.2162 |  | 20.5525 | 20.1182 | 20.215 | 19.2445 |  | 17.0112 | 16.9366 | 16.6377 | 16.8015 | 16.8011 | 17.2463 | 17.4171 | 15.6587 | 16.9833 | 16.094 | 16.9924 | 18.01 | 46.8007 | 47.7495 | 45.6165 | 21.4245 |  |  | 0.24731 | -0.32008 | -60.7742 | 0.53551 | 0.33658 | -197.8046 | 10.685 | -0.24021 | -0.10402 | 0.009762 | -0.034082 | 8.8289 | 9.0587 | 1.979 | 21.7693 | 21.9959 | 22.1901 | 22.2467 | 22.0819 | 21.3993 | 20.2012 | 22.1936 | 22.3664 | 22.3956 | 22.3544 | 21.9702 | 21.2092 | 22.2747 | 17.0322 | 17.187 | 16.0425 | 16.2021 | 16.2484 | 17.1283 | 16.9004 | 22.3597 | 22.1386 | 21.6936 | 22.0755 | 21.7954 | 21.3005 | 21.9399 | 21.5177 | 20.8976 | 20.0917 | 20.7768 | 19.9762 | 19.8689 | -0.28978 | -0.032303 | 20.739 | 22.0683 | 22.3687 | 20.0997 | 21.6587 | 22.0987 | 21.9369 | 21.6929 | 21.2724 | 21.7715 | 21.4416 | 21.0419 | 20.4278 | 21.1026 | 20.2832 | 20.3026 | 20.1084 |  | 20.2066 | 19.8544 | 20.1135 | 19.7689 | 20.0865 | 20.3507 |  | 20.3969 |  |  | 20.2699 | 20.3211 | 20.6193 | [5 empty] | 21.9107 | 20.354 | 21.651 | 22.0299 | 19.6483 | 21.1541 | 21.7751 | 19.4109 | 20.0013 | 22.4102 |  | 19.7366 | 20.986 | 18.9083 | 19.7335 | 21.2049 | 19.4332 | 20.1553 | 19.0302 | 20.0899 | 19.1639 | 20.1943 | 18.7787 | 20.0409 | 21.0536 | 19.4649 | 19.7613 | 21.4569 | 18.9166 | 19.8238 | 21.0278 | 18.9359 | 20.1187 | 19.3075 | 20.2516 | 18.9706 | 20.2226 | -0.028699 | 20.949 | 0.050146 | 0.016734 | -27.1763 | 3.0957 | -9.49 | -0.1 | 0.59462 | -0.67152 | -9.2532 | 0.86859 | 0.68898 | -16.7025 | 3.8819 | 0.42265 | 0.42658 | 0.42806 | 0.41325 | 0.49663 | 0.43778 | 0.42545
42838.4196 | -60 | 22.9046 | 22.865 | 22.8552 | 22.7806 | 22.4059 | 21.7368 | 22.7118 | 21.7997 | 22.3686 | 22.3774 | 22.3558 | 22.0174 | 21.2345 | 22.2037 | 21.6 | 21.7772 | 21.9013 | 21.0871 | 21.1801 | 21.3998 | 20.4773 | 20.6186 | 20.9055 | 21.8849 | 21.6465 | 21.2704 | 20.731 | 20.7 | 21.2826 | 22.0783 | 21.6806 | 21.1965 | 22.0046 | 21.7467 | 21.3567 | 19.9424 | 21.2452 |  | 20.5606 | 20.1357 | 20.2148 | 19.2294 |  | 17.0012 | 16.9225 | 16.6265 | 16.8181 | 16.7986 | 17.2454 | 17.404 | 15.6246 | 16.9837 | 16.0618 | 16.982 | 18.0074 | 46.7191 | 47.6802 | 45.5559 | 21.4159 |  |  | 0.33667 | -0.18012 | -59.8115 | 0.50791 | 0.27415 | -197.8144 | 10.8006 | -0.17975 | -0.092536 | -0.26822 | 0.0070616 | 8.8272 | 9.0573 | 1.9787 | 21.77 | 21.996 | 22.1813 | 22.2435 | 22.0689 | 21.3769 | 20.1879 | 22.1843 | 22.3542 | 22.3963 | 22.3424 | 21.9758 | 21.2077 | 22.2607 | 17.0421 | 17.1502 | 16.0342 | 16.2097 | 16.2625 | 17.1299 | 16.9084 | 22.3687 | 22.1366 | 21.6969 | 22.0787 | 21.7981 | 21.3052 | 21.9513 | 21.5295 | 20.9007 | 20.099 | 20.7953 | 19.9878 | 19.866 | -0.1783 | -0.19721 | 20.7431 | 22.0649 | 22.3683 | 20.1122 | 21.6563 | 22.0999 | 21.9374 | 21.7078 | 21.2728 | 21.7769 | 21.4349 | 21.0394 | 20.4511 | 21.1108 | 20.2936 | 20.3045 | 20.1339 |  | 20.2078 | 19.8973 | 20.1144 | 19.7845 | 20.0969 | 20.359 |  | 20.4125 |  |  | 20.2676 | 20.3138 | 20.6091 | [5 empty] | 21.9041 | 20.353 | 21.6536 | 22.026 | 19.6419 | 21.1467 | 21.7658 | 19.4096 | 20.0033 | 22.4556 |  | 19.7387 | 20.9908 | 18.9039 | 19.7277 | 21.2232 | 19.4377 | 20.1568 | 19.0312 | 20.0943 | 19.1615 | 20.1979 | 18.7744 | 20.036 | 21.06 | 19.4607 | 19.7608 | 21.4625 | 18.9164 | 19.8218 | 21.0312 | 18.9303 | 20.1164 | 19.3042 | 20.2566 | 18.9695 | 20.2179 | -0.17061 | 20.9487 | 0.049151 | 0.014375 | -27.0303 | 3.0956 | -24.29 | -0.05 | 0.69385 | -0.50373 | -9.1794 | 0.84589 | 0.62181 | -16.7029 | 3.9029 | 0.42198 | 0.42542 | 0.42797 | 0.41233 | 0.49848 | 0.43821 | 0.42578
42838.4196 | -59 | 22.908 | 22.8655 | 22.8585 | 22.7781 | 22.4041 | 21.7407 | 22.7178 | 21.7992 | 22.3685 | 22.3759 | 22.3563 | 22.0205 | 21.2351 | 22.2116 | 21.6028 | 21.7735 | 21.9004 | 21.0883 | 21.1841 | 21.4016 | 20.4801 | 20.6184 | 20.9047 | 21.8854 | 21.6498 | 21.2704 | 20.7604 | 20.7074 | 21.3119 | 22.0781 | 21.6759 | 21.1927 | 21.9999 | 21.7401 | 21.3489 | 19.9311 | 21.302 |  | 20.5525 | 20.1394 | 20.2101 | 19.1954 |  | 16.9907 | 16.921 | 16.6165 | 16.8187 | 16.7948 | 17.2333 | 17.4122 | 15.634 | 16.9831 | 16.0219 | 16.9879 | 18.0085 | 46.6517 | 47.6299 | 45.5018 | 21.4226 |  |  | 0.40896 | -0.26357 | -59.4856 | 0.36269 | 0.27612 | -197.8545 | 10.7099 | -0.14821 | -0.085336 | -0.40438 | -0.017416 | 8.8286 | 9.058 | 1.9787 | 21.7788 | 22.0001 | 22.1842 | 22.2436 | 22.0712 | 21.3917 | 20.198 | 22.1925 | 22.3612 | 22.4015 | 22.3573 | 21.9827 | 21.2096 | 22.2706 | 17.0382 | 17.1121 | 16.0341 | 16.1919 | 16.2619 | 17.132 | 16.9047 | 22.3643 | 22.1344 | 21.691 | 22.0686 | 21.7896 | 21.2977 | 21.9461 | 21.5244 | 20.8966 | 20.0833 | 20.7926 | 19.9826 | 19.8643 | 0.076293 | -0.20348 | 20.7415 | 22.0606 | 22.3679 | 20.1096 | 21.6561 | 22.0983 | 21.9416 | 21.7109 | 21.2679 | 21.7726 | 21.4354 | 21.0358 | 20.4667 | 21.1057 | 20.2922 | 20.3024 | 20.1471 |  | 20.1993 | 19.945 | 20.1076 | 19.7788 | 20.0875 | 20.348 |  | 20.3961 |  |  | 20.266 | 20.3191 | 20.6122 | [5 empty] | 21.9061 | 20.3437 | 21.6486 | 22.0224 | 19.6496 | 21.1447 | 21.7633 | 19.4037 | 20.0002 | 22.4797 |  | 19.7307 | 21.0016 | 18.9078 | 19.7241 | 21.2487 | 19.4393 | 20.1482 | 19.0336 | 20.1074 | 19.162 | 20.2055 | 18.7632 | 20.0274 | 21.068 | 19.4683 | 19.7589 | 21.4559 | 18.921 | 19.8316 | 21.031 | 18.9265 | 20.1097 | 19.3103 | 20.2566 | 18.9685 | 20.2246 | 0.041049 | 20.9487 | 0.048081 | 0.013526 | -27.2427 | 3.0956 | 2.09 | -0.09 | 0.76475 | -0.60935 | -9.1543 | 0.7148 | 0.62402 | -16.7042 | 3.8864 | 0.42133 | 0.42387 | 0.42781 | 0.41301 | 0.49806 | 0.43878 | 0.4253
42838.4196 | -58 | 22.9046 | 22.8624 | 22.8518 | 22.7738 | 22.3982 | 21.7359 | 22.7115 | 21.7885 | 22.3621 | 22.3705 | 22.3448 | 22.0065 | 21.2352 | 22.2023 | 21.5909 | 21.7658 | 21.8809 | 21.0775 | 21.1778 | 21.3859 | 20.4705 | 20.6113 | 20.9031 | 21.8732 | 21.6348 | 21.2672 | 20.7612 | 20.705 | 21.3145 | 22.0739 | 21.6766 | 21.1917 | 21.9972 | 21.7356 | 21.344 | 19.9325 | 21.4091 |  | 20.5549 | 20.1501 | 20.208 | 19.1731 |  | 16.9892 | 16.9166 | 16.6009 | 16.7984 | 16.7879 | 17.2164 | 17.4334 | 15.6293 | 16.9849 | 15.9862 | 16.9922 | 18.0138 | 46.5915 | 47.5799 | 45.4365 | 21.421 |  |  | 0.50752 | -0.17486 | -58.8389 | 0.17672 | 0.38192 | -197.8059 | 11.0457 | -0.081844 | 0.035705 | -0.15074 | 0.014526 | 8.8285 | 9.0583 | 1.9787 | 21.7766 | 22.0036 | 22.1887 | 22.2579 | 22.0773 | 21.3945 | 20.2017 | 22.2021 | 22.3701 | 22.4096 | 22.3557 | 21.9889 | 21.2211 | 22.2762 | 17.0513 | 17.112 | 16.0512 | 16.187 | 16.2591 | 17.1274 | 16.9038 | 22.3605 | 22.1212 | 21.6908 | 22.073 | 21.785 | 21.2881 | 21.9375 | 21.5166 | 20.8942 | 20.0911 | 20.7878 | 19.9769 | 19.8735 | -0.1148 | -0.06749 | 20.7505 | 22.0569 | 22.3668 | 20.1079 | 21.6495 | 22.107 | 21.9369 | 21.7035 | 21.2728 | 21.7702 | 21.4421 | 21.0267 | 20.4755 | 21.1048 | 20.2898 | 20.3027 | 20.1533 |  | 20.2067 | 20.0069 | 20.1163 | 19.7805 | 20.0883 | 20.349 |  | 20.4012 |  |  | 20.2701 | 20.3236 | 20.619 | [5 empty] | 21.9145 | 20.349 | 21.6548 | 22.0233 | 19.6611 | 21.1484 | 21.7761 | 19.4014 | 20.0058 | 22.4807 |  | 19.7403 | 21.017 | 18.919 | 19.729 | 21.2692 | 19.437 | 20.1543 | 19.032 | 20.1169 | 19.1763 | 20.2326 | 18.7668 | 20.0431 | 21.0851 | 19.4702 | 19.7641 | 21.4641 | 18.9225 | 19.8344 | 21.0427 | 18.9307 | 20.1237 | 19.3226 | 20.2634 | 18.9737 | 20.2281 | -0.14853 | 20.9487 | 0.048899 | 0.013845 | -27.0579 | 3.0956 | -26.27 | -0.06 | 0.85194 | -0.49631 | -9.1043 | 0.49895 | 0.73388 | -16.7017 | 3.9467 | 0.4214 | 0.42244 | 0.42779 | 0.41102 | 0.49606 | 0.43945 | 0.4253
42838.4196 | -57 | 22.9082 | 22.8726 | 22.8527 | 22.7781 | 22.3999 | 21.7405 | 22.7158 | 21.7943 | 22.3696 | 22.3818 | 22.3579 | 22.0146 | 21.2374 | 22.2007 | 21.5927 | 21.7669 | 21.8984 | 21.0732 | 21.1796 | 21.3901 | 20.479 | 20.6103 | 20.8972 | 21.876 | 21.6321 | 21.2687 | 20.7934 | 20.7183 | 21.3465 | 22.0624 | 21.6635 | 21.1808 | 21.9861 | 21.7265 | 21.3484 | 19.9303 | 21.4825 |  | 20.5468 | 20.1593 | 20.196 | 19.1399 |  | 16.9848 | 16.9126 | 16.5952 | 16.804 | 16.7796 | 17.2069 | 17.4276 | 15.6245 | 16.9961 | 15.9776 | 16.9946 | 18.0131 | 46.5487 | 47.5287 | 45.3733 | 21.4253 |  |  | 0.50161 | -0.063805 | -58.3645 | 0.53616 | 0.25706 | -197.8979 | 11.346 | -0.033872 | 0.12678 | -0.037233 | -0.032346 | 8.8289 | 9.0587 | 1.9784 | 21.774 | 22.0054 | 22.1866 | 22.2564 | 22.0759 | 21.3953 | 20.1968 | 22.1969 | 22.3729 | 22.4062 | 22.3567 | 21.9863 | 21.212 | 22.2759 | 17.0591 | 17.1206 | 16.0754 | 16.1914 | 16.2503 | 17.1246 | 16.897 | 22.3632 | 22.1312 | 21.6899 | 22.0777 | 21.7847 | 21.2911 | 21.9359 | 21.518 | 20.8985 | 20.0975 | 20.7947 | 19.9867 | 19.8844 | -0.087082 | -0.069963 | 20.7673 | 22.0667 | 22.3666 | 20.1047 | 21.6528 | 22.1063 | 21.9403 | 21.7046 | 21.2692 | 21.7747 | 21.4417 | 21.0363 | 20.5016 | 21.1335 | 20.3054 | 20.3161 | 20.1631 |  | 20.2083 | 20.0524 | 20.1137 | 19.7893 | 20.0905 | 20.3558 |  | 20.4009 |  |  | 20.2846 | 20.3377 | 20.6178 | [5 empty] | 21.912 | 20.3615 | 21.6503 | 22.0286 | 19.6539 | 21.1514 | 21.7705 | 19.4071 | 20.0114 | 22.4972 |  | 19.7507 | 21.0189 | 18.9265 | 19.7382 | 21.2871 | 19.4436 | 20.149 | 19.0489 | 20.1265 | 19.1763 | 20.2421 | 18.753 | 20.0354 | 21.0938 | 19.4632 | 19.7589 | 21.4659 | 18.9329 | 19.8269 | 21.0512 | 18.9199 | 20.1104 | 19.3195 | 20.249 | 18.976 | 20.2269 | -0.048919 | 20.9481 | 0.050595 | 0.015478 | -27.0134 | 3.0956 | -33.57 | 0.03 | 0.84701 | -0.29981 | -9.0675 | 0.86908 | 0.60208 | -16.7053 | 4 | 0.42119 | 0.42109 | 0.42762 | 0.40983 | 0.49257 | 0.4403 | 0.42522
42838.4196 | -56 | 22.8968 | 22.8608 | 22.8538 | 22.7747 | 22.3969 | 21.7393 | 22.7177 | 21.7986 | 22.3647 | 22.3702 | 22.348 | 22.0146 | 21.231 | 22.2007 | 21.6022 | 21.7652 | 21.8958 | 21.088 | 21.1818 | 21.3954 | 20.4732 | 20.6122 | 20.9086 | 21.8761 | 21.6372 | 21.2682 | 20.8023 | 20.7315 | 21.3825 | 22.0654 | 21.6599 | 21.1887 | 21.9946 | 21.7375 | 21.3491 | 19.9301 | 21.58 |  | 20.5537 | 20.1681 | 20.2083 | 19.1272 |  | 16.9814 | 16.9072 | 16.5894 | 16.7917 | 16.7659 | 17.1891 | 17.4366 | 15.6363 | 17.0022 | 15.988 | 16.9937 | 18.0063 | 46.4941 | 47.4909 | 45.3151 | 21.4201 |  |  | 0.39384 | -0.35885 | -57.4767 | 0.3088 | 0.37732 | -197.7882 | 11.5195 | 0.048924 | 0.022278 | -0.30053 | 0.029456 | 8.8293 | 9.0592 | 1.9786 | 21.7675 | 21.9987 | 22.1857 | 22.2511 | 22.0744 | 21.3901 | 20.1963 | 22.1956 | 22.3691 | 22.399 | 22.3533 | 21.9798 | 21.2054 | 22.2691 | 17.073 | 17.1273 | 16.0834 | 16.2073 | 16.2366 | 17.1226 | 16.9035 | 22.3628 | 22.1324 | 21.6882 | 22.0748 | 21.786 | 21.2947 | 21.9419 | 21.5128 | 20.8987 | 20.0946 | 20.8061 | 19.9813 | 19.8832 | -0.053266 | -0.068061 | 20.7602 | 22.0533 | 22.3643 | 20.0992 | 21.6469 | 22.0975 | 21.9374 | 21.699 | 21.2654 | 21.7684 | 21.4339 | 21.0341 | 20.5046 | 21.1471 | 20.3041 | 20.321 | 20.1636 |  | 20.214 | 20.0792 | 20.1144 | 19.7957 | 20.0984 | 20.3527 |  | 20.4074 |  |  | 20.2716 | 20.3292 | 20.614 | [5 empty] | 21.9068 | 20.3527 | 21.6455 | 22.027 | 19.64 | 21.1506 | 21.7629 | 19.4027 | 20.0233 | 22.5214 |  | 19.7498 | 21.0471 | 18.9227 | 19.739 | 21.3016 | 19.4567 | 20.1579 | 19.046 | 20.1363 | 19.1819 | 20.2467 | 18.7524 | 20.0295 | 21.0935 | 19.4693 | 19.756 | 21.4702 | 18.9276 | 19.8249 | 21.051 | 18.9218 | 20.1184 | 19.3202 | 20.2534 | 18.9714 | 20.225 | -0.11793 | 20.9484 | 0.050865 | 0.015769 | -27.0028 | 3.0956 | -14.94 | -0.05 | 0.75058 | -0.71099 | -8.9982 | 0.65955 | 0.72941 | -16.7001 | 4.0303 | 0.42136 | 0.42037 | 0.42771 | 0.40804 | 0.49245 | 0.44064 | 0.42515
42838.4196 | -55 | 22.9096 | 22.8672 | 22.8534 | 22.7832 | 22.4125 | 21.7489 | 22.7233 | 21.8014 | 22.3708 | 22.3749 | 22.3577 | 22.0213 | 21.243 | 22.2057 | 21.6063 | 21.7684 | 21.8999 | 21.0893 | 21.1789 | 21.3981 | 20.4811 | 20.6252 | 20.9094 | 21.8827 | 21.643 | 21.2714 | 20.8153 | 20.7438 | 21.3885 | 22.0751 | 21.6725 | 21.1927 | 21.9977 | 21.7415 | 21.3527 | 19.9352 | 21.6655 |  | 20.5482 | 20.183 | 20.2042 | 19.1138 |  | 16.9767 | 16.9006 | 16.5838 | 16.7794 | 16.7681 | 17.177 | 17.4627 | 15.6773 | 16.996 | 16.0066 | 16.9921 | 18.0078 | 46.4391 | 47.4519 | 45.26 | 21.419 |  |  | 0.35441 | -0.11178 | -56.7289 | 0.53288 | 0.31555 | -197.8328 | 11.6062 | 0.027236 | 0.086301 | 0.13124 | 0.026505 | 8.8291 | 9.0592 | 1.9788 | 21.7739 | 21.9938 | 22.1855 | 22.2484 | 22.0708 | 21.3899 | 20.1975 | 22.1983 | 22.3691 | 22.3969 | 22.3553 | 21.9785 | 21.2119 | 22.2677 | 17.0704 | 17.1475 | 16.0811 | 16.2048 | 16.2616 | 17.1266 | 16.9008 | 22.3565 | 22.1284 | 21.6912 | 22.0698 | 21.7856 | 21.2925 | 21.9402 | 21.5083 | 20.8993 | 20.0915 | 20.8229 | 19.9833 | 19.8884 | 0.10795 | -0.083086 | 20.7624 | 22.06 | 22.3671 | 20.1044 | 21.6501 | 22.1011 | 21.9381 | 21.7026 | 21.2649 | 21.77 | 21.4348 | 21.0392 | 20.5163 | 21.1575 | 20.315 | 20.3343 | 20.1751 |  | 20.2108 | 20.1006 | 20.1248 | 19.8019 | 20.0942 | 20.3538 |  | 20.4121 |  |  | 20.2628 | 20.3228 | 20.6123 | [5 empty] | 21.9113 | 20.3494 | 21.6305 | 22.0096 | 19.6413 | 21.1438 | 21.7565 | 19.3925 | 20.0146 | 22.5279 |  | 19.7521 | 21.0713 | 18.9239 | 19.743 | 21.3143 | 19.4577 | 20.1503 | 19.0461 | 20.1534 | 19.181 | 20.2537 | 18.7485 | 20.0331 | 21.106 | 19.473 | 19.7594 | 21.4694 | 18.9313 | 19.8257 | 21.0611 | 18.9343 | 20.115 | 19.3326 | 20.2508 | 18.9694 | 20.24 | -0.12405 | 20.9484 | 0.050208 | 0.015507 | -27.1431 | 3.0956 | -5.81 | -0.05 | 0.71202 | -0.39681 | -8.9394 | 0.8664 | 0.66703 | -16.7017 | 4.0454 | 0.42093 | 0.42012 | 0.42739 | 0.40881 | 0.49239 | 0.44119 | 0.4249
42838.4197 | -54 | 22.8973 | 22.8662 | 22.8477 | 22.7686 | 22.4053 | 21.7341 | 22.7134 | 21.7964 | 22.3662 | 22.3737 | 22.3539 | 22.0184 | 21.234 | 22.1992 | 21.5987 | 21.7598 | 21.8948 | 21.0802 | 21.1849 | 21.4008 | 20.48 | 20.6169 | 20.9065 | 21.8783 | 21.6448 | 21.2697 | 20.8134 | 20.7599 | 21.3543 | 22.0701 | 21.6563 | 21.1929 | 21.9935 | 21.7334 | 21.3453 | 19.936 | 21.7191 |  | 20.5499 | 20.1906 | 20.1937 | 19.1084 |  | 16.9668 | 16.8882 | 16.5797 | 16.7729 | 16.7644 | 17.1944 | 17.4441 | 15.721 | 17.0019 | 16.0043 | 16.9922 | 18.0021 | 46.374 | 47.4225 | 45.2129 | 21.418 |  |  | 0.38464 | 0.021619 | -56.336 | 0.48031 | 0.32803 | -197.8506 | 11.6641 | -0.026644 | 0.12094 | -0.074578 | 0.072856 | 8.8288 | 9.0586 | 1.9787 | 21.7759 | 22.0022 | 22.1907 | 22.2439 | 22.0776 | 21.39 | 20.1997 | 22.1965 | 22.3707 | 22.4117 | 22.3575 | 21.9724 | 21.2123 | 22.2814 | 17.0588 | 17.1528 | 16.0649 | 16.1993 | 16.2671 | 17.129 | 16.9044 | 22.3521 | 22.1269 | 21.6783 | 22.0657 | 21.7789 | 21.2863 | 21.9325 | 21.5168 | 20.8929 | 20.0818 | 20.8333 | 19.971 | 19.8827 | 0.017903 | -0.091265 | 20.7658 | 22.0603 | 22.3534 | 20.0909 | 21.6513 | 22.092 | 21.9291 | 21.6951 | 21.2668 | 21.7697 | 21.4406 | 21.0359 | 20.53 | 21.1836 | 20.314 | 20.3349 | 20.1875 |  | 20.2094 | 20.1259 | 20.1149 | 19.8082 | 20.0938 | 20.3483 |  | 20.4056 |  |  | 20.2627 | 20.3093 | 20.6127 | [5 empty] | 21.9057 | 20.3474 | 21.6469 | 22.0201 | 19.6398 | 21.1448 | 21.7683 | 19.3842 | 20.006 | 22.5362 |  | 19.7445 | 21.075 | 18.927 | 19.7369 | 21.3343 | 19.4483 | 20.1462 | 19.0407 | 20.1589 | 19.1836 | 20.2608 | 18.7463 | 20.0273 | 21.1038 | 19.4768 | 19.7586 | 21.4755 | 18.9315 | 19.8274 | 21.0653 | 18.9281 | 20.1134 | 19.3319 | 20.2449 | 18.9709 | 20.2476 | -0.13258 | 20.9494 | 0.049476 | 0.014687 | -27.1111 | 3.0956 | -7.87 | -0.06 | 0.74172 | 0.17451 | -8.9082 | 0.82253 | 0.68011 | -16.7029 | 4.0555 | 0.42055 | 0.41909 | 0.42721 | 0.41036 | 0.4946 | 0.44136 | 0.42474
42838.4197 | -53 | 22.8962 | 22.8607 | 22.8513 | 22.7722 | 22.399 | 21.732 | 22.7127 | 21.791 | 22.3583 | 22.3729 | 22.3507 | 22.0093 | 21.2258 | 22.1997 | 21.5912 | 21.7614 | 21.8964 | 21.0788 | 21.182 | 21.406 | 20.4741 | 20.617 | 20.9025 | 21.8755 | 21.6448 | 21.2653 | 20.8123 | 20.7618 | 21.3154 | 22.074 | 21.667 | 21.1943 | 22.0014 | 21.7372 | 21.349 | 19.9384 | 21.7477 |  | 20.562 | 20.2014 | 20.2055 | 19.0999 |  | 16.9624 | 16.8821 | 16.5802 | 16.7742 | 16.7554 | 17.2266 | 17.4694 | 15.7668 | 17.0026 | 15.9719 | 16.9894 | 18.0118 | 46.302 | 47.3971 | 45.1805 | 21.426 |  |  | 0.39121 | -0.41865 | -55.7768 | 0.48754 | 0.36812 | -197.848 | 12.1142 | -0.02336 | -0.1515 | -0.24389 | -0.066024 | 8.8286 | 9.0584 | 1.9786 | 21.7744 | 21.9945 | 22.1822 | 22.2523 | 22.0658 | 21.3817 | 20.1985 | 22.1896 | 22.3639 | 22.3989 | 22.3495 | 21.9765 | 21.1989 | 22.2742 | 17.0645 | 17.1582 | 16.0488 | 16.1924 | 16.2756 | 17.1287 | 16.9072 | 22.3582 | 22.1144 | 21.6842 | 22.0689 | 21.7835 | 21.283 | 21.9348 | 21.5129 | 20.8942 | 20.0862 | 20.8421 | 19.9706 | 19.8823 | 0.039332 | -0.052464 | 20.7697 | 22.0583 | 22.3558 | 20.0944 | 21.6605 | 22.0968 | 21.9421 | 21.7035 | 21.2724 | 21.767 | 21.443 | 21.0381 | 20.5467 | 21.195 | 20.3289 | 20.3519 | 20.1978 |  | 20.2076 | 20.1324 | 20.1153 | 19.8088 | 20.0943 | 20.3484 |  | 20.4082 |  |  | 20.2761 | 20.3121 | 20.6229 | [5 empty] | 21.9068 | 20.3612 | 21.6612 | 22.0304 | 19.6439 | 21.1487 | 21.7714 | 19.3804 | 20.0162 | 22.5695 |  | 19.763 | 21.0954 | 18.9376 | 19.7448 | 21.3554 | 19.4578 | 20.1616 | 19.049 | 20.1729 | 19.1895 | 20.2754 | 18.7473 | 20.033 | 21.1181 | 19.4816 | 19.7684 | 21.4856 | 18.9374 | 19.822 | 21.0707 | 18.9326 | 20.1196 | 19.3287 | 20.248 | 18.9693 | 20.252 | -0.28617 | 20.9486 | 0.04778 | 0.012342 | -27.115 | 3.0956 | -4.11 | -0.07 | 0.74798 | -0.76792 | -8.8637 | 0.82869 | 0.72051 | -16.7037 | 4.1333 | 0.4202 | 0.41892 | 0.42721 | 0.40971 | 0.49673 | 0.44168 | 0.42489
42838.4197 | -52 | 22.9023 | 22.866 | 22.8535 | 22.7772 | 22.4037 | 21.7382 | 22.7194 | 21.7973 | 22.364 | 22.3768 | 22.3506 | 22.0124 | 21.2414 | 22.2035 | 21.5933 | 21.76 | 21.8972 | 21.0816 | 21.1775 | 21.3969 | 20.477 | 20.6207 | 20.907 | 21.8744 | 21.6477 | 21.2687 | 20.8144 | 20.7685 | 21.2811 | 22.0752 | 21.6775 | 21.1917 | 21.9987 | 21.7397 | 21.3565 | 19.9349 | 21.7809 |  | 20.5591 | 20.2123 | 20.2125 | 19.0879 |  | 16.9484 | 16.876 | 16.57 | 16.7736 | 16.7518 | 17.2491 | 17.5058 | 15.8074 | 16.9915 | 15.9706 | 16.9831 | 18.0039 | 46.2304 | 47.3677 | 45.1335 | 21.4133 |  |  | 0.33273 | -0.092061 | -55.3516 | 0.54208 | 0.40754 | -197.7842 | 11.8717 | -0.1101 | -0.091758 | -0.050451 | -0.050053 | 8.8291 | 9.0589 | 1.9789 | 21.7716 | 21.999 | 22.1882 | 22.247 | 22.076 | 21.3869 | 20.202 | 22.1956 | 22.3752 | 22.4038 | 22.3555 | 21.9769 | 21.2087 | 22.2729 | 17.0491 | 17.1617 | 16.0145 | 16.1731 | 16.2779 | 17.1253 | 16.8989 | 22.3583 | 22.1154 | 21.687 | 22.0728 | 21.7778 | 21.2879 | 21.9437 | 21.5174 | 20.8847 | 20.0883 | 20.8577 | 19.9629 | 19.8881 | 0.063317 | -0.036678 | 20.783 | 22.0613 | 22.3588 | 20.0923 | 21.6505 | 22.0938 | 21.939 | 21.7025 | 21.2653 | 21.7655 | 21.4306 | 21.0334 | 20.5562 | 21.1968 | 20.3297 | 20.355 | 20.2111 |  | 20.2181 | 20.1488 | 20.122 | 19.817 | 20.1016 | 20.3552 |  | 20.4112 |  |  | 20.2682 | 20.3049 | 20.6234 | [5 empty] | 21.9088 | 20.3602 | 21.6507 | 22.0315 | 19.6416 | 21.1498 | 21.7642 | 19.3812 | 20.0123 | 22.5734 |  | 19.7713 | 21.1136 | 18.9195 | 19.7418 | 21.3618 | 19.461 | 20.1587 | 19.0486 | 20.1798 | 19.1912 | 20.2823 | 18.7473 | 20.0296 | 21.1203 | 19.477 | 19.7617 | 21.4961 | 18.9303 | 19.8214 | 21.0699 | 18.9252 | 20.1234 | 19.333 | 20.2405 | 18.9786 | 20.2625 | -0.14742 | 20.9484 | 0.04834 | 0.01317 | -27.0786 | 3.0955 | 2.34 | 0 | 0.68977 | -0.3601 | -8.8298 | 0.87381 | 0.75814 | -16.7017 | 4.0919 | 0.42018 | 0.41869 | 0.42722 | 0.41102 | 0.49956 | 0.44189 | 0.4248
42838.4197 | -51 | 22.9051 | 22.8678 | 22.8542 | 22.7751 | 22.3908 | 21.7341 | 22.7144 | 21.7937 | 22.3599 | 22.3689 | 22.3501 | 22.0156 | 21.2311 | 22.2031 | 21.5879 | 21.764 | 21.8957 | 21.0818 | 21.1809 | 21.3896 | 20.4695 | 20.614 | 20.8995 | 21.8778 | 21.6448 | 21.2651 | 20.8178 | 20.7743 | 21.2582 | 22.0707 | 21.6689 | 21.1872 | 22.0021 | 21.732 | 21.3481 | 19.9344 | 21.8209 |  | 20.5588 | 20.2118 | 20.2164 | 19.0737 |  | 16.9505 | 16.8772 | 16.5675 | 16.765 | 16.7682 | 17.2695 | 17.543 | 15.8474 | 16.9957 | 15.9818 | 16.9858 | 18.0042 | 46.1653 | 47.3577 | 45.0972 | 21.4277 |  |  | 0.28673 | -0.007949 | -54.8726 | 0.2812 | 0.23735 | -197.8834 | 11.9966 | 0.014096 | -0.076384 | -0.13269 | -0.050747 | 8.8294 | 9.0593 | 1.9786 | 21.7752 | 21.997 | 22.1885 | 22.2442 | 22.0739 | 21.3857 | 20.2001 | 22.1933 | 22.3707 | 22.3937 | 22.3533 | 21.9809 | 21.2109 | 22.2713 | 17.0596 | 17.164 | 16.0021 | 16.1685 | 16.2601 | 17.1279 | 16.9044 | 22.3622 | 22.126 | 21.69 | 22.0754 | 21.7875 | 21.2947 | 21.9428 | 21.5199 | 20.8936 | 20.0896 | 20.8723 | 19.9609 | 19.8811 | -0.028102 | -0.012903 | 20.7959 | 22.0705 | 22.3632 | 20.11 | 21.6467 | 22.1005 | 21.9514 | 21.7094 | 21.2745 | 21.7742 | 21.4397 | 21.0395 | 20.5837 | 21.2175 | 20.3447 | 20.3649 | 20.2151 |  | 20.208 | 20.1513 | 20.1128 | 19.811 | 20.0933 | 20.3543 |  | 20.3974 |  |  | 20.2643 | 20.2926 | 20.6162 | [5 empty] | 21.9107 | 20.3585 | 21.6456 | 22.0235 | 19.6383 | 21.143 | 21.7668 | 19.369 | 20.0125 | 22.5655 |  | 19.7729 | 21.1196 | 18.9187 | 19.7413 | 21.3703 | 19.4517 | 20.1464 | 19.0514 | 20.1922 | 19.1844 | 20.2748 | 18.7516 | 20.0277 | 21.1289 | 19.4777 | 19.7597 | 21.513 | 18.9327 | 19.821 | 21.072 | 18.9318 | 20.1262 | 19.3368 | 20.2451 | 18.9792 | 20.2639 | -0.23664 | 20.949 | 0.049335 | 0.014876 | -27.0912 | 3.0955 | 0.83 | -0.03 | 0.6403 | -0.10581 | -8.7915 | 0.62935 | 0.5786 | -16.7065 | 4.1135 | 0.41973 | 0.41831 | 0.42711 | 0.41016 | 0.50159 | 0.44227 | 0.42504
42838.4197 | -50 | 22.906 | 22.8714 | 22.8572 | 22.7765 | 22.3973 | 21.7417 | 22.7186 | 21.7984 | 22.3651 | 22.3784 | 22.3447 | 22.0106 | 21.2288 | 22.2052 | 21.5883 | 21.7728 | 21.898 | 21.0805 | 21.1802 | 21.3943 | 20.4758 | 20.6143 | 20.9001 | 21.8748 | 21.6397 | 21.268 | 20.8246 | 20.7844 | 21.2452 | 22.0816 | 21.6776 | 21.1957 | 21.9988 | 21.7413 | 21.3573 | 19.9279 | 21.8387 |  | 20.5613 | 20.2252 | 20.2364 | 19.0816 |  | 16.9539 | 16.8761 | 16.5656 | 16.7636 | 16.7703 | 17.2906 | 17.5758 | 15.8905 | 16.9972 | 15.999 | 16.9915 | 18.0014 | 46.0972 | 47.3447 | 45.0498 | 21.4148 |  |  | 0.4267 | -0.097317 | -54.6623 | 0.39028 | 0.307 | -197.8072 | 12.1884 | -0.006932 | -0.16629 | 0.12578 | -0.042067 | 8.8299 | 9.06 | 1.9787 | 21.7761 | 21.9907 | 22.1857 | 22.2419 | 22.0698 | 21.3829 | 20.191 | 22.1959 | 22.363 | 22.3966 | 22.3526 | 21.9754 | 21.2086 | 22.267 | 17.0517 | 17.1548 | 15.9878 | 16.1532 | 16.2449 | 17.1312 | 16.8968 | 22.3607 | 22.1218 | 21.6919 | 22.075 | 21.7903 | 21.2975 | 21.9344 | 21.518 | 20.8952 | 20.0985 | 20.8938 | 19.9646 | 19.8805 | -0.010604 | -0.075669 | 20.7888 | 22.056 | 22.3624 | 20.1003 | 21.6433 | 22.0946 | 21.937 | 21.7022 | 21.2741 | 21.7772 | 21.4374 | 21.0355 | 20.5889 | 21.2342 | 20.3464 | 20.3825 | 20.199 |  | 20.2047 | 20.1561 | 20.1117 | 19.8116 | 20.0893 | 20.3577 |  | 20.4027 |  |  | 20.2649 | 20.287 | 20.6179 | [5 empty] | 21.9114 | 20.3572 | 21.6467 | 22.0172 | 19.638 | 21.1416 | 21.7677 | 19.3794 | 20.0173 | 22.561 |  | 19.7762 | 21.1343 | 18.9223 | 19.7464 | 21.393 | 19.4598 | 20.1482 | 19.0608 | 20.2062 | 19.1858 | 20.2891 | 18.7555 | 20.0268 | 21.1389 | 19.487 | 19.7632 | 21.529 | 18.939 | 19.8222 | 21.084 | 18.9334 | 20.1297 | 19.3421 | 20.2447 | 18.9812 | 20.2729 | -0.063574 | 20.9486 | 0.049568 | 0.014673 | -27.1235 | 3.0955 | 0.29 | -0.07 | 0.78107 | -0.37024 | -8.7746 | 0.74144 | 0.65806 | -16.7039 | 4.1464 | 0.42007 | 0.41814 | 0.42696 | 0.41142 | 0.50229 | 0.44184 | 0.42536
42838.4197 | -49 | 22.9009 | 22.8627 | 22.8575 | 22.7729 | 22.4001 | 21.7314 | 22.7209 | 21.7883 | 22.3635 | 22.3734 | 22.3526 | 22.0246 | 21.2269 | 22.2003 | 21.5847 | 21.7687 | 21.8938 | 21.0836 | 21.1773 | 21.3964 | 20.4787 | 20.6117 | 20.9073 | 21.8722 | 21.6361 | 21.2673 | 20.8208 | 20.7961 | 21.2469 | 22.0854 | 21.6829 | 21.1978 | 21.9979 | 21.747 | 21.3565 | 19.9427 | 21.8487 |  | 20.5654 | 20.2332 | 20.252 | 19.0655 |  | 16.9498 | 16.879 | 16.5682 | 16.7671 | 16.7702 | 17.2965 | 17.5731 | 15.9244 | 16.9935 | 16.0153 | 16.9974 | 18.0188 | 46.0514 | 47.3477 | 45.0124 | 21.428 |  |  | 0.35836 | -0.015837 | -54.6669 | 0.53616 | 0.35432 | -197.8282 | 12.3159 | 0.000296 | -0.0039932 | 0.11739 | -0.023839 | 8.8286 | 9.0585 | 1.9788 | 21.7799 | 21.9981 | 22.1942 | 22.2556 | 22.0769 | 21.3898 | 20.199 | 22.1958 | 22.3726 | 22.4076 | 22.3614 | 21.9783 | 21.2152 | 22.2728 | 17.0516 | 17.1669 | 15.9744 | 16.1297 | 16.2304 | 17.1292 | 16.8958 | 22.3625 | 22.1366 | 21.6906 | 22.0752 | 21.7907 | 21.2932 | 21.9367 | 21.5193 | 20.895 | 20.0936 | 20.9094 | 19.9643 | 19.8831 | 0.16811 | -0.11124 | 20.7944 | 22.0604 | 22.3593 | 20.1078 | 21.6536 | 22.1001 | 21.9484 | 21.6973 | 21.274 | 21.7736 | 21.4388 | 21.0239 | 20.5978 | 21.2504 | 20.3545 | 20.3716 | 20.2011 |  | 20.2049 | 20.1576 | 20.1122 | 19.8224 | 20.0954 | 20.3562 |  | 20.4088 |  |  | 20.256 | 20.2931 | 20.6183 | [5 empty] | 21.9051 | 20.3576 | 21.6424 | 22.0218 | 19.6296 | 21.1417 | 21.7676 | 19.377 | 20.0247 | 22.5578 |  | 19.7771 | 21.1551 | 18.9157 | 19.7481 | 21.4056 | 19.4587 | 20.1576 | 19.0597 | 20.2044 | 19.1884 | 20.2882 | 18.7598 | 20.0233 | 21.1434 | 19.488 | 19.7631 | 21.536 | 18.9376 | 19.8154 | 21.0911 | 18.9338 | 20.1319 | 19.3429 | 20.24 | 18.9734 | 20.281 | -0.12961 | 20.9488 | 0.049919 | 0.015377 | -27.0869 | 3.0955 | -18.49 | -0.01 | 0.7158 | -0.14936 | -8.7751 | 0.86903 | 0.70696 | -16.7049 | 4.1681 | 0.42002 | 0.41812 | 0.42687 | 0.4112 | 0.50366 | 0.44278 | 0.42512
42838.4197 | -48 | 22.9038 | 22.8649 | 22.8637 | 22.7845 | 22.4006 | 21.7415 | 22.7273 | 21.7957 | 22.3689 | 22.3825 | 22.3546 | 22.0261 | 21.2367 | 22.2012 | 21.593 | 21.7647 | 21.8969 | 21.0911 | 21.1848 | 21.4021 | 20.4782 | 20.6148 | 20.9095 | 21.8807 | 21.6392 | 21.2756 | 20.8286 | 20.809 | 21.2842 | 22.0712 | 21.6728 | 21.1932 | 21.9947 | 21.7359 | 21.3552 | 19.9268 | 21.8502 |  | 20.5686 | 20.2283 | 20.2561 | 19.0524 |  | 16.9403 | 16.8682 | 16.5614 | 16.7509 | 16.7479 | 17.2508 | 17.5608 | 15.8217 | 16.9989 | 16.0926 | 16.9893 | 18.0109 | 45.9814 | 47.3468 | 44.9452 | 21.4216 |  |  | 0.30119 | -0.11243 | -54.5263 | 0.46914 | 0.40557 | -197.8585 | 12.1687 | 0.033152 | -0.2342 | 0.2632 | 0.0030688 | 8.8283 | 9.0579 | 1.9784 | 21.772 | 21.9982 | 22.1948 | 22.2568 | 22.0737 | 21.3915 | 20.201 | 22.1958 | 22.3702 | 22.4016 | 22.3584 | 21.981 | 21.2084 | 22.2728 | 17.062 | 17.1698 | 15.9938 | 16.1011 | 16.2155 | 17.1186 | 16.8901 | 22.3678 | 22.1346 | 21.6891 | 22.0754 | 21.7862 | 21.291 | 21.9398 | 21.5224 | 20.8903 | 20.0937 | 20.9073 | 19.9558 | 19.8694 | 0.08455 | -0.074908 | 20.7859 | 22.0536 | 22.3519 | 20.0988 | 21.6409 | 22.0927 | 21.9288 | 21.6878 | 21.2524 | 21.7665 | 21.4302 | 21.0333 | 20.5941 | 21.2637 | 20.3468 | 20.3782 | 20.1972 |  | 20.2075 | 20.1632 | 20.1159 | 19.808 | 20.0933 | 20.3547 |  | 20.4083 |  |  | 20.252 | 20.3031 | 20.6232 | [5 empty] | 21.9102 | 20.3643 | 21.6518 | 22.0269 | 19.6379 | 21.1443 | 21.7718 | 19.3696 | 20.0226 | 22.5548 |  | 19.7714 | 21.1695 | 18.9032 | 19.7453 | 21.4185 | 19.4585 | 20.1591 | 19.0601 | 20.2069 | 19.1816 | 20.2826 | 18.7613 | 20.0219 | 21.1578 | 19.4887 | 19.7654 | 21.546 | 18.9384 | 19.8145 | 21.102 | 18.9319 | 20.1317 | 19.3426 | 20.2415 | 18.9729 | 20.2789 | -0.20418 | 20.9497 | 0.049532 | 0.014179 | -27.0811 | 3.0955 | -18.03 | -0.02 | 0.65627 | -0.39795 | -8.7636 | 0.81289 | 0.75631 | -16.7049 | 4.1427 | 0.42021 | 0.41809 | 0.4272 | 0.4088 | 0.50085 | 0.44261 | 0.4255
42838.4197 | -47 | 22.9042 | 22.8747 | 22.8646 | 22.7822 | 22.403 | 21.7447 | 22.7186 | 21.8033 | 22.3717 | 22.3754 | 22.349 | 22.0251 | 21.2386 | 22.2079 | 21.5921 | 21.7608 | 21.8968 | 21.0805 | 21.1772 | 21.3957 | 20.4763 | 20.6136 | 20.9042 | 21.8821 | 21.6379 | 21.2728 | 20.8332 | 20.8163 | 21.322 | 22.0768 | 21.681 | 21.189 | 21.9984 | 21.7432 | 21.3542 | 19.9285 | 21.8392 |  | 20.5762 | 20.2399 | 20.2729 | 19.0404 |  | 16.9381 | 16.8622 | 16.5559 | 16.7512 | 16.7425 | 17.2355 | 17.5585 | 15.6956 | 17.0019 | 16.1516 | 16.9877 | 18.0013 | 45.92 | 47.3537 | 44.8992 | 21.4237 |  |  | 0.30513 | -0.40616 | -53.8672 | 0.46388 | 0.3162 | -197.8663 | 12.4263 | -0.01876 | -0.0001012 | 0.13543 | 0.044906 | 8.8297 | 9.0595 | 1.9787 | 21.7784 | 21.9937 | 22.1967 | 22.2546 | 22.0722 | 21.3858 | 20.1982 | 22.1954 | 22.3706 | 22.4024 | 22.3526 | 21.9816 | 21.2049 | 22.2709 | 17.056 | 17.2008 | 16.0074 | 16.0952 | 16.1986 | 17.1217 | 16.8929 | 22.3771 | 22.1361 | 21.697 | 22.087 | 21.7953 | 21.3035 | 21.9523 | 21.5277 | 20.9081 | 20.1043 | 20.9331 | 19.9657 | 19.8748 | 0.072951 | -0.084418 | 20.7957 | 22.0675 | 22.3662 | 20.1002 | 21.6594 | 22.1024 | 21.9408 | 21.7 | 21.2641 | 21.7661 | 21.4293 | 21.0329 | 20.6058 | 21.2931 | 20.367 | 20.3977 | 20.2007 |  | 20.2175 | 20.173 | 20.1186 | 19.8054 | 20.0936 | 20.3611 |  | 20.4138 |  |  | 20.2461 | 20.3047 | 20.622 | [5 empty] | 21.9092 | 20.3519 | 21.6568 | 22.0279 | 19.6323 | 21.1428 | 21.7684 | 19.3641 | 20.0097 | 22.5523 |  | 19.7699 | 21.1881 | 18.892 | 19.7403 | 21.4266 | 19.4592 | 20.1484 | 19.0586 | 20.2112 | 19.1789 | 20.2835 | 18.7644 | 20.0288 | 21.171 | 19.4926 | 19.764 | 21.5476 | 18.9428 | 19.8164 | 21.1045 | 18.9317 | 20.1314 | 19.3447 | 20.2406 | 18.9769 | 20.2755 | -0.069695 | 20.9491 | 0.04794 | 0.012691 | -27.0965 | 3.0955 | -5.88 | -0.04 | 0.66059 | -0.75636 | -8.7104 | 0.80831 | 0.66779 | -16.7048 | 4.1863 | 0.42045 | 0.4179 | 0.42728 | 0.40983 | 0.49966 | 0.443 | 0.42571
42838.4197 | -46 | 22.9068 | 22.8712 | 22.8557 | 22.7741 | 22.409 | 21.7467 | 22.7149 | 21.8024 | 22.3703 | 22.3739 | 22.3488 | 22.0244 | 21.2421 | 22.2061 | 21.588 | 21.767 | 21.8989 | 21.0859 | 21.1726 | 21.3911 | 20.4673 | 20.6016 | 20.8986 | 21.8757 | 21.6324 | 21.2588 | 20.8463 | 20.815 | 21.3433 | 22.0674 | 21.6725 | 21.191 | 21.9899 | 21.7314 | 21.3484 | 19.9302 | 21.8234 |  | 20.579 | 20.2383 | 20.2739 | 19.0333 |  | 16.9218 | 16.8487 | 16.5441 | 16.7373 | 16.727 | 17.2025 | 17.5385 | 15.6386 | 16.9927 | 16.1216 | 16.9783 | 18.0025 | 45.8519 | 47.3612 | 44.8516 | 21.4219 |  |  | 0.26176 | 0.091931 | -53.764 | 0.55128 | 0.37929 | -197.8289 | 12.5137 | -0.12653 | -0.098958 | -0.25501 | -0.018631 | 8.8296 | 9.0595 | 1.9789 | 21.7669 | 21.9907 | 22.1834 | 22.2483 | 22.0686 | 21.3816 | 20.191 | 22.1876 | 22.3671 | 22.3952 | 22.3472 | 21.9725 | 21.203 | 22.2643 | 17.0669 | 17.209 | 16.0011 | 16.1144 | 16.2126 | 17.131 | 16.8982 | 22.3721 | 22.1351 | 21.6958 | 22.0846 | 21.7974 | 21.3016 | 21.9468 | 21.5298 | 20.9066 | 20.0994 | 20.9513 | 19.9691 | 19.8656 | 0.052898 | -0.13577 | 20.7961 | 22.0552 | 22.3557 | 20.1048 | 21.6463 | 22.0947 | 21.9402 | 21.7021 | 21.2746 | 21.7744 | 21.4409 | 21.0371 | 20.6082 | 21.2887 | 20.3808 | 20.404 | 20.1864 |  | 20.2147 | 20.1736 | 20.11 | 19.7912 | 20.0932 | 20.3576 |  | 20.4025 |  |  | 20.2383 | 20.2922 | 20.624 | [5 empty] | 21.9142 | 20.3643 | 21.6498 | 22.0237 | 19.6249 | 21.1551 | 21.7724 | 19.37 | 20.0169 | 22.5685 |  | 19.7737 | 21.1888 | 18.8942 | 19.7405 | 21.4432 | 19.4591 | 20.1574 | 19.0632 | 20.2042 | 19.179 | 20.2866 | 18.7636 | 20.0254 | 21.1903 | 19.4895 | 19.7539 | 21.5571 | 18.9384 | 19.8082 | 21.111 | 18.9368 | 20.1255 | 19.3408 | 20.2346 | 18.9713 | 20.2721 | -0.18155 | 20.9491 | 0.048899 | 0.013526 | -27.073 | 3.0955 | -10.39 | 0 | 0.61187 | 0.35983 | -8.7018 | 0.88115 | 0.73133 | -16.7022 | 4.2007 | 0.42075 | 0.4176 | 0.42766 | 0.40971 | 0.50097 | 0.44325 | 0.4258
42838.4198 | -45 | 22.8998 | 22.8618 | 22.8492 | 22.7676 | 22.4024 | 21.7419 | 22.7109 | 21.7982 | 22.3701 | 22.3724 | 22.3437 | 22.0209 | 21.238 | 22.1971 | 21.5886 | 21.7716 | 21.8948 | 21.0774 | 21.1741 | 21.3926 | 20.4678 | 20.6085 | 20.8981 | 21.8745 | 21.6302 | 21.258 | 20.8548 | 20.83 | 21.3496 | 22.063 | 21.6679 | 21.1852 | 21.9895 | 21.7325 | 21.3462 | 19.9274 | 21.8202 |  | 20.5698 | 20.2437 | 20.2791 | 19.0235 |  | 16.9178 | 16.8406 | 16.5295 | 16.7311 | 16.7158 | 17.1834 | 17.5572 | 15.5982 | 17.0009 | 16.074 | 16.9832 | 18.012 | 45.7678 | 47.3751 | 44.8104 | 21.4201 |  |  | 0.35901 | -0.059205 | -53.2443 | 0.46782 | 0.16112 | -197.8171 | 12.676 | -0.077244 | -0.28733 | -0.36347 | 0.016262 | 8.8287 | 9.0585 | 1.9786 | 21.785 | 22.0013 | 22.1973 | 22.2574 | 22.0779 | 21.3996 | 20.205 | 22.198 | 22.367 | 22.4055 | 22.3596 | 21.989 | 21.2084 | 22.2748 | 17.0649 | 17.2046 | 15.9796 | 16.1134 | 16.2136 | 17.1251 | 16.8934 | 22.3659 | 22.1312 | 21.6956 | 22.0769 | 21.7879 | 21.2961 | 21.9429 | 21.5272 | 20.9005 | 20.1001 | 20.9536 | 19.9795 | 19.8478 | -0.0015606 | 0.051005 | 20.8071 | 22.0628 | 22.371 | 20.1118 | 21.6641 | 22.1039 | 21.9447 | 21.7161 | 21.2807 | 21.7917 | 21.4473 | 21.0387 | 20.6266 | 21.3098 | 20.4021 | 20.4275 | 20.1972 |  | 20.2145 | 20.1835 | 20.1202 | 19.7947 | 20.0987 | 20.3656 |  | 20.4115 |  |  | 20.2286 | 20.2848 | 20.6248 | [5 empty] | 21.9119 | 20.3717 | 21.6504 | 22.0251 | 19.6278 | 21.1524 | 21.7719 | 19.3741 | 20.0207 | 22.591 |  | 19.7676 | 21.2079 | 18.9037 | 19.7412 | 21.4558 | 19.4533 | 20.1549 | 19.0655 | 20.2036 | 19.1786 | 20.2875 | 18.7566 | 20.0207 | 21.2137 | 19.4946 | 19.7586 | 21.5691 | 18.9343 | 19.8123 | 21.1218 | 18.9408 | 20.1325 | 19.3432 | 20.2326 | 18.9624 | 20.2622 | -0.083793 | 20.9476 | 0.049513 | 0.015682 | -27.0798 | 3.0955 | -22.98 | -0.07 | 0.71658 | -0.28876 | -8.6596 | 0.81171 | 0.47665 | -16.7012 | 4.2277 | 0.42044 | 0.41767 | 0.42775 | 0.40924 | 0.50279 | 0.44343 | 0.42632
42838.4198 | -44 | 22.8965 | 22.8672 | 22.8562 | 22.7717 | 22.401 | 21.7406 | 22.7102 | 21.7943 | 22.3595 | 22.3657 | 22.3443 | 22.0137 | 21.2307 | 22.1967 | 21.5955 | 21.7687 | 21.8983 | 21.0784 | 21.1823 | 21.3978 | 20.4679 | 20.6062 | 20.9043 | 21.8786 | 21.6341 | 21.2582 | 20.8691 | 20.8398 | 21.3673 | 22.0695 | 21.6745 | 21.1946 | 21.9964 | 21.7339 | 21.3507 | 19.9331 | 21.8698 |  | 20.5783 | 20.2604 | 20.2966 | 19.0331 |  | 16.9171 | 16.8316 | 16.5276 | 16.7142 | 16.7126 | 17.1758 | 17.6064 | 15.6063 | 17.0082 | 16.0585 | 16.9923 | 18.0038 | 45.6763 | 47.3828 | 44.7659 | 21.4241 |  |  | 0.15728 | -0.010581 | -52.4807 | 0.50856 | 0.32015 | -197.8834 | 12.8252 | -0.2297 | -0.013723 | -0.11675 | 0.010013 | 8.8287 | 9.0584 | 1.9785 | 21.7797 | 21.9985 | 22.198 | 22.2575 | 22.074 | 21.3929 | 20.1989 | 22.1992 | 22.3712 | 22.4022 | 22.3551 | 21.9774 | 21.2101 | 22.2728 | 17.0601 | 17.1819 | 15.9813 | 16.1316 | 16.2204 | 17.1234 | 16.8851 | 22.3655 | 22.1213 | 21.6804 | 22.0688 | 21.7861 | 21.2876 | 21.9347 | 21.5185 | 20.8929 | 20.0928 | 20.9719 | 19.9818 | 19.8386 | -0.087082 | -0.084988 | 20.8088 | 22.0695 | 22.3617 | 20.0965 | 21.6524 | 22.1005 | 21.9334 | 21.7006 | 21.2708 | 21.7712 | 21.4333 | 21.0341 | 20.615 | 21.3074 | 20.3913 | 20.4179 | 20.1918 |  | 20.21 | 20.1876 | 20.1098 | 19.7897 | 20.094 | 20.3617 |  | 20.4105 |  |  | 20.2421 | 20.2828 | 20.6303 | [5 empty] | 21.9127 | 20.3661 | 21.6534 | 22.0263 | 19.6411 | 21.1537 | 21.7752 | 19.3773 | 20.0238 | 22.6057 |  | 19.7712 | 21.2263 | 18.9075 | 19.743 | 21.484 | 19.467 | 20.1678 | 19.0647 | 20.2087 | 19.1737 | 20.2886 | 18.7513 | 20.0229 | 21.2177 | 19.4919 | 19.7533 | 21.5698 | 18.9236 | 19.8084 | 21.1493 | 18.9277 | 20.1311 | 19.3461 | 20.2146 | 18.9681 | 20.2448 | -0.10884 | 20.9493 | 0.050226 | 0.015515 | -27.0921 | 3.0956 | -13.83 | -0.08 | 0.47431 | -0.12207 | -8.5971 | 0.8463 | 0.67187 | -16.7038 | 4.2525 | 0.42045 | 0.41721 | 0.42773 | 0.40957 | 0.50164 | 0.44336 | 0.42633
42838.4198 | -43 | 22.9021 | 22.8736 | 22.8669 | 22.7895 | 22.4059 | 21.7458 | 22.7203 | 21.798 | 22.3697 | 22.3787 | 22.3529 | 22.0204 | 21.2354 | 22.2065 | 21.6074 | 21.7831 | 21.9082 | 21.0899 | 21.1753 | 21.4018 | 20.4833 | 20.621 | 20.9076 | 21.8865 | 21.6422 | 21.2642 | 20.8663 | 20.8567 | 21.3807 | 22.0737 | 21.6743 | 21.1931 | 21.9975 | 21.7298 | 21.3539 | 19.9289 | 21.9548 |  | 20.5773 | 20.2693 | 20.3017 | 19.0505 |  | 16.8888 | 16.848 | 16.5301 | 16.7028 | 16.6929 | 17.1379 | 17.5655 | 15.6507 | 16.9987 | 16.0437 | 16.9812 | 18.0072 | 45.5804 | 47.3971 | 44.7025 | 21.4188 |  |  | 0.25125 | 0.11559 | -52.1574 | 0.29369 | 0.28335 | -197.8749 | 13.1051 | -0.047016 | -0.094482 | 0.15075 | 0.11296 | 8.829 | 9.0588 | 1.9788 | 21.7736 | 21.9937 | 22.1886 | 22.2528 | 22.0716 | 21.3803 | 20.1936 | 22.1896 | 22.3653 | 22.4039 | 22.3535 | 21.9703 | 21.2049 | 22.2627 | 17.0465 | 17.1586 | 15.9682 | 16.1543 | 16.2252 | 17.1203 | 16.8803 | 22.371 | 22.1247 | 21.6839 | 22.0744 | 21.7939 | 21.2929 | 21.9406 | 21.522 | 20.8964 | 20.1015 | 20.9871 | 19.9878 | 19.8448 | -0.11225 | -0.011001 | 20.7966 | 22.0551 | 22.3646 | 20.0956 | 21.6541 | 22.09 | 21.9395 | 21.6965 | 21.2609 | 21.7643 | 21.4304 | 21.0273 | 20.6254 | 21.3105 | 20.3956 | 20.4334 | 20.2074 |  | 20.2116 | 20.1931 | 20.115 | 19.7886 | 20.0957 | 20.3669 |  | 20.4142 |  |  | 20.2431 | 20.2839 | 20.6353 | [5 empty] | 21.9092 | 20.3571 | 21.6464 | 22.024 | 19.6406 | 21.1392 | 21.7605 | 19.3735 | 20.0192 | 22.5992 |  | 19.7614 | 21.2302 | 18.9075 | 19.7418 | 21.4822 | 19.4568 | 20.1534 | 19.0718 | 20.2075 | 19.1723 | 20.2831 | 18.7565 | 20.0321 | 21.2429 | 19.4948 | 19.7614 | 21.5924 | 18.932 | 19.809 | 21.1694 | 18.9378 | 20.1378 | 19.3539 | 20.2217 | 18.9693 | 20.2551 | -0.062275 | 20.9499 | 0.05132 | 0.015747 | -27.0563 | 3.0955 | 10.97 | -0.06 | 0.59949 | 0.40348 | -8.5708 | 0.64314 | 0.63204 | -16.7023 | 4.2984 | 0.42007 | 0.41723 | 0.42781 | 0.41073 | 0.50254 | 0.44273 | 0.42645
42838.4198 | -42 | 22.8946 | 22.8648 | 22.848 | 22.7722 | 22.3943 | 21.7291 | 22.7141 | 21.7959 | 22.3609 | 22.3639 | 22.3523 | 22.0096 | 21.2276 | 22.2035 | 21.5862 | 21.7638 | 21.8953 | 21.0794 | 21.1747 | 21.3852 | 20.469 | 20.5993 | 20.8936 | 21.8705 | 21.6299 | 21.2624 | 20.8786 | 20.8571 | 21.3634 | 22.0766 | 21.6728 | 21.1927 | 22.0035 | 21.7362 | 21.3523 | 19.9322 | 22.0249 |  | 20.5794 | 20.2774 | 20.3136 | 19.043 |  | 16.8956 | 16.8503 | 16.5274 | 16.6984 | 16.6832 | 17.1262 | 17.5506 | 15.6531 | 16.9959 | 16.0401 | 16.9885 | 18.0026 | 45.4823 | 47.3992 | 44.6282 | 21.4128 |  |  | 0.33142 | -0.031609 | -51.7106 | 0.57822 | 0.33 | -197.8434 | 13.065 | -0.12521 | -0.47707 | -0.010379 | -0.004396 | 8.8298 | 9.0594 | 1.9791 | 21.7711 | 21.9926 | 22.1861 | 22.2506 | 22.0754 | 21.3784 | 20.1959 | 22.1957 | 22.3668 | 22.3936 | 22.3503 | 21.9743 | 21.2002 | 22.2662 | 17.0484 | 17.1385 | 15.9854 | 16.1741 | 16.2427 | 17.12 | 16.8854 | 22.3613 | 22.1175 | 21.6844 | 22.0702 | 21.788 | 21.2913 | 21.9364 | 21.5188 | 20.8927 | 20.1008 | 20.995 | 19.9768 | 19.8325 | -0.021614 | -0.050562 | 20.7996 | 22.0544 | 22.3541 | 20.0942 | 21.6535 | 22.0875 | 21.9287 | 21.7006 | 21.267 | 21.766 | 21.4208 | 21.0295 | 20.6237 | 21.3288 | 20.4067 | 20.4309 | 20.207 |  | 20.2155 | 20.1716 | 20.1249 | 19.7882 | 20.0956 | 20.3625 |  | 20.411 |  |  | 20.2319 | 20.277 | 20.6232 | [5 empty] | 21.9051 | 20.3573 | 21.6353 | 22.0149 | 19.6237 | 21.1356 | 21.7679 | 19.3825 | 20.0202 | 22.61 |  | 19.7768 | 21.2465 | 18.9106 | 19.7427 | 21.5143 | 19.4631 | 20.1647 | 19.0701 | 20.2093 | 19.1807 | 20.2945 | 18.772 | 20.039 | 21.2632 | 19.5114 | 19.7588 | 21.6069 | 18.9357 | 19.8167 | 21.1806 | 18.9514 | 20.1503 | 19.3526 | 20.2344 | 18.9685 | 20.2552 | -0.19621 | 20.9486 | 0.050423 | 0.015159 | -27.0302 | 3.0955 | -11.74 | -0.08 | 0.68851 | -0.21099 | -8.5341 | 0.90243 | 0.68208 | -16.7007 | 4.2917 | 0.42021 | 0.41815 | 0.42782 | 0.41048 | 0.50122 | 0.44305 | 0.42677
42838.4198 | -41 | 22.9021 | 22.8641 | 22.85 | 22.7682 | 22.4019 | 21.7312 | 22.7193 | 21.786 | 22.3626 | 22.3673 | 22.3478 | 22.0105 | 21.2259 | 22.1954 | 21.5924 | 21.7684 | 21.8937 | 21.0817 | 21.1739 | 21.3953 | 20.4687 | 20.6149 | 20.9032 | 21.8789 | 21.6413 | 21.2712 | 20.8947 | 20.8776 | 21.367 | 22.0803 | 21.6758 | 21.1905 | 22.0024 | 21.743 | 21.3493 | 19.9332 | 22.0395 |  | 20.5781 | 20.292 | 20.3219 | 19.0574 |  | 16.884 | 16.8387 | 16.5143 | 16.6866 | 16.6699 | 17.1082 | 17.5745 | 15.6241 | 16.9876 | 16.0499 | 16.9823 | 18.0054 | 45.3892 | 47.419 | 44.5672 | 21.4158 |  |  | 0.32879 | -0.20377 | -51.0495 | 0.71293 | 0.3898 | -197.8473 | 13.2287 | -0.20735 | -0.34513 | 0.22187 | -0.074704 | 8.8279 | 9.0577 | 1.9789 | 21.7788 | 21.9963 | 22.1907 | 22.2522 | 22.0755 | 21.3826 | 20.1984 | 22.1918 | 22.3651 | 22.4011 | 22.3494 | 21.9778 | 21.2021 | 22.2602 | 17.0355 | 17.1517 | 16.0004 | 16.185 | 16.2782 | 17.1161 | 16.8845 | 22.3722 | 22.1225 | 21.6902 | 22.0765 | 21.7942 | 21.2938 | 21.9361 | 21.5223 | 20.9045 | 20.0987 | 21.0124 | 19.9791 | 19.832 | -0.029281 | -0.10952 | 20.8081 | 22.0573 | 22.3759 | 20.1004 | 21.6664 | 22.0915 | 21.9391 | 21.7077 | 21.2771 | 21.7866 | 21.4426 | 21.0404 | 20.631 | 21.3584 | 20.4191 | 20.4521 | 20.1956 |  | 20.2056 | 20.1369 | 20.1092 | 19.789 | 20.0873 | 20.3563 |  | 20.4074 |  |  | 20.2344 | 20.2646 | 20.6212 | [5 empty] | 21.8992 | 20.3565 | 21.6433 | 22.0206 | 19.6307 | 21.135 | 21.7622 | 19.3843 | 20.0282 | 22.6267 |  | 19.7726 | 21.2588 | 18.9088 | 19.7433 | 21.5242 | 19.4568 | 20.153 | 19.0842 | 20.2148 | 19.1824 | 20.2914 | 18.7736 | 20.0411 | 21.2777 | 19.5174 | 19.7608 | 21.6166 | 18.9396 | 19.8077 | 21.1992 | 18.961 | 20.1555 | 19.3537 | 20.2257 | 18.9626 | 20.2492 | -0.12906 | 20.9486 | 0.049083 | 0.013896 | -27.0494 | 3.0955 | -11.25 | -0.05 | 0.68577 | -0.53571 | -8.4792 | 1.002 | 0.74128 | -16.7003 | 4.3183 | 0.42019 | 0.41859 | 0.42752 | 0.41146 | 0.49945 | 0.44268 | 0.42671
42838.4198 | -40 | 22.9047 | 22.8689 | 22.8571 | 22.7809 | 22.3985 | 21.7361 | 22.7215 | 21.7933 | 22.3656 | 22.3747 | 22.346 | 22.0162 | 21.2319 | 22.2059 | 21.5903 | 21.7645 | 21.8891 | 21.0874 | 21.1833 | 21.3889 | 20.4741 | 20.6095 | 20.9001 | 21.878 | 21.634 | 21.2627 | 20.9095 | 20.8817 | 21.3706 | 22.0759 | 21.6785 | 21.1829 | 22.0004 | 21.7327 | 21.353 | 19.9348 | 22.0368 |  | 20.5844 | 20.3108 | 20.3332 | 19.0529 |  | 16.8896 | 16.8492 | 16.5212 | 16.6909 | 16.676 | 17.1203 | 17.6236 | 15.626 | 17.0009 | 16.0747 | 16.9922 | 18.0046 | 45.3048 | 47.4377 | 44.5015 | 21.4157 |  |  | 0.3025 | -0.059205 | -50.6506 | 0.3824 | 0.24326 | -197.819 | 13.2201 | -0.25269 | -0.18478 | -0.020659 | 0.030498 | 8.8278 | 9.0577 | 1.9788 | 21.7725 | 21.9928 | 22.1883 | 22.2458 | 22.0688 | 21.3815 | 20.1896 | 22.1867 | 22.3659 | 22.3982 | 22.349 | 21.9686 | 21.1999 | 22.2587 | 17.0328 | 17.1717 | 16.0086 | 16.1778 | 16.2867 | 17.1215 | 16.8886 | 22.371 | 22.1351 | 21.7016 | 22.0817 | 21.7983 | 21.2966 | 21.9413 | 21.5328 | 20.9013 | 20.1115 | 21.0357 | 19.9848 | 19.8376 | -0.033213 | -0.12075 | 20.8088 | 22.0632 | 22.3597 | 20.1033 | 21.6643 | 22.0973 | 21.9329 | 21.7011 | 21.2694 | 21.7666 | 21.4341 | 21.0351 | 20.6314 | 21.3772 | 20.4206 | 20.4577 | 20.2048 |  | 20.2106 | 20.1193 | 20.115 | 19.7935 | 20.089 | 20.3557 |  | 20.4063 |  |  | 20.2446 | 20.2685 | 20.6151 | [5 empty] | 21.8977 | 20.3584 | 21.6347 | 22.0187 | 19.6273 | 21.1411 | 21.7644 | 19.3861 | 20.0356 | 22.6443 |  | 19.7758 | 21.2806 | 18.9226 | 19.7447 | 21.5413 | 19.4655 | 20.1493 | 19.0826 | 20.2173 | 19.1822 | 20.2913 | 18.7704 | 20.0409 | 21.2883 | 19.519 | 19.764 | 21.6109 | 18.9335 | 19.8067 | 21.214 | 18.9524 | 20.1574 | 19.3596 | 20.2262 | 18.9624 | 20.2495 | -0.025546 | 20.9495 | 0.050085 | 0.013983 | -27.1066 | 3.0955 | -23.62 | -0.17 | 0.65779 | -0.28877 | -8.4461 | 0.73388 | 0.58561 | -16.6995 | 4.317 | 0.42011 | 0.41928 | 0.42746 | 0.41239 | 0.49902 | 0.44287 | 0.42698
42838.4198 | -39 | 22.905 | 22.8659 | 22.8579 | 22.7839 | 22.403 | 21.7484 | 22.7239 | 21.7974 | 22.3692 | 22.3749 | 22.3466 | 22.0141 | 21.2307 | 22.2047 | 21.582 | 21.7605 | 21.8833 | 21.0763 | 21.1755 | 21.3918 | 20.4695 | 20.6078 | 20.8968 | 21.8775 | 21.6316 | 21.261 | 20.9258 | 20.8838 | 21.3665 | 22.0808 | 21.6681 | 21.1841 | 21.9965 | 21.7297 | 21.3452 | 19.9365 | 22.0126 |  | 20.5839 | 20.3242 | 20.3398 | 19.05 |  | 16.8968 | 16.8473 | 16.5206 | 16.6907 | 16.6779 | 17.1249 | 17.6417 | 15.588 | 17.0028 | 16.0692 | 16.9981 | 18.0061 | 45.2225 | 47.4624 | 44.4444 | 21.4139 |  |  | 0.26965 | -0.085489 | -50.1078 | 0.44285 | 0.51925 | -197.798 | 13.5993 | -0.11733 | -0.0001012 | 0.2011 | -0.058733 | 8.8282 | 9.058 | 1.9791 | 21.7802 | 21.9877 | 22.1898 | 22.2528 | 22.0685 | 21.3752 | 20.1943 | 22.1929 | 22.3615 | 22.3986 | 22.3553 | 21.9691 | 21.2009 | 22.2653 | 17.0267 | 17.1691 | 15.9844 | 16.1369 | 16.2462 | 17.118 | 16.8783 | 22.36 | 22.1197 | 21.6831 | 22.0706 | 21.7775 | 21.2867 | 21.9309 | 21.5146 | 20.8879 | 20.0904 | 21.0292 | 19.9617 | 19.8243 | 0.029502 | 0.01848 | 20.8052 | 22.0583 | 22.3581 | 20.1019 | 21.6574 | 22.1031 | 21.9398 | 21.7075 | 21.272 | 21.7744 | 21.4411 | 21.0359 | 20.6323 | 21.384 | 20.4346 | 20.4654 | 20.2122 |  | 20.2152 | 20.1002 | 20.1182 | 19.802 | 20.0957 | 20.3567 |  | 20.4169 |  |  | 20.261 | 20.2875 | 20.636 | [5 empty] | 21.9128 | 20.3708 | 21.6527 | 22.0306 | 19.6338 | 21.1562 | 21.7712 | 19.3706 | 20.0257 | 22.6543 |  | 19.7722 | 21.2934 | 18.9073 | 19.7412 | 21.5473 | 19.4624 | 20.1377 | 19.0902 | 20.2083 | 19.1717 | 20.2812 | 18.7763 | 20.0539 | 21.3054 | 19.5307 | 19.772 | 21.6306 | 18.9396 | 19.8101 | 21.2222 | 18.9594 | 20.1715 | 19.3593 | 20.2324 | 18.9684 | 20.2529 | -0.15836 | 20.948 | 0.050791 | 0.014331 | -27.0979 | 3.0955 | 3.19 | -0.1 | 0.62104 | -0.34699 | -8.4007 | 0.78976 | 0.85558 | -16.6987 | 4.3785 | 0.42005 | 0.41991 | 0.42744 | 0.41266 | 0.5005 | 0.443 | 0.42665
42838.4198 | -38 | 22.9048 | 22.867 | 22.8537 | 22.7788 | 22.4016 | 21.7416 | 22.716 | 21.7994 | 22.3683 | 22.375 | 22.3471 | 22.0192 | 21.2331 | 22.2052 | 21.5935 | 21.7669 | 21.8936 | 21.0816 | 21.1845 | 21.3902 | 20.4786 | 20.6165 | 20.9114 | 21.8777 | 21.6426 | 21.2679 | 20.9371 | 20.897 | 21.3773 | 22.081 | 21.672 | 21.1897 | 22.0001 | 21.7353 | 21.3466 | 19.9331 | 21.9865 |  | 20.5841 | 20.3356 | 20.3454 | 19.055 |  | 16.8781 | 16.8221 | 16.4999 | 16.6668 | 16.6513 | 17.1015 | 17.6666 | 15.5356 | 16.9959 | 16.05 | 16.9835 | 18.0086 | 45.15 | 47.4744 | 44.3889 | 21.4153 |  |  | 0.15662 | -0.25371 | -49.4422 | 0.74184 | 0.58628 | -197.8388 | 13.4245 | -0.081188 | 0.12678 | 0.17613 | 0.018519 | 8.8283 | 9.0582 | 1.9788 | 21.769 | 21.992 | 22.1835 | 22.2496 | 22.0652 | 21.3734 | 20.1891 | 22.1915 | 22.3599 | 22.3954 | 22.344 | 21.9755 | 21.1982 | 22.262 | 17.0325 | 17.1686 | 15.9838 | 16.1052 | 16.2399 | 17.1236 | 16.8839 | 22.3646 | 22.1279 | 21.6865 | 22.078 | 21.7943 | 21.2929 | 21.9443 | 21.5155 | 20.8999 | 20.0989 | 21.0387 | 19.9683 | 19.8306 | -0.050121 | -0.08689 | 20.8149 | 22.0649 | 22.3589 | 20.0919 | 21.6596 | 22.1094 | 21.9394 | 21.7022 | 21.2651 | 21.7791 | 21.4439 | 21.0323 | 20.6345 | 21.3924 | 20.4321 | 20.4736 | 20.2294 |  | 20.2169 | 20.0895 | 20.114 | 19.797 | 20.0936 | 20.3651 |  | 20.4166 |  |  | 20.2514 | 20.2883 | 20.6327 | [5 empty] | 21.9138 | 20.3744 | 21.6557 | 22.0303 | 19.6273 | 21.1574 | 21.7759 | 19.3752 | 20.027 | 22.6768 |  | 19.7819 | 21.3 | 18.9085 | 19.7442 | 21.5656 | 19.4641 | 20.13 | 19.0818 | 20.2183 | 19.175 | 20.2789 | 18.7824 | 20.058 | 21.3176 | 19.5335 | 19.7719 | 21.6353 | 18.937 | 19.8094 | 21.2338 | 18.9615 | 20.1777 | 19.3628 | 20.2314 | 18.9704 | 20.2512 | -0.12535 | 20.949 | 0.050509 | 0.01558 | -27.1113 | 3.0955 | -6.03 | -0.17 | 0.47332 | -0.59775 | -8.3444 | 1.0221 | 0.90909 | -16.6997 | 4.3501 | 0.41963 | 0.42007 | 0.42751 | 0.41266 | 0.50122 | 0.44275 | 0.42676
42838.4198 | -37 | 22.9013 | 22.8603 | 22.8546 | 22.7787 | 22.4045 | 21.7399 | 22.7256 | 21.8009 | 22.3694 | 22.3768 | 22.3471 | 22.0235 | 21.2328 | 22.2019 | 21.5965 | 21.7703 | 21.8945 | 21.0806 | 21.1901 | 21.3964 | 20.4801 | 20.6194 | 20.9144 | 21.8812 | 21.6488 | 21.2707 | 20.9438 | 20.9069 | 21.3822 | 22.0756 | 21.6742 | 21.1894 | 21.997 | 21.7319 | 21.3514 | 19.9306 | 21.9753 |  | 20.5845 | 20.3475 | 20.3529 | 19.0479 |  | 16.8757 | 16.8168 | 16.4979 | 16.6628 | 16.6427 | 17.0969 | 17.6805 | 15.5113 | 17.0005 | 16.063 | 16.9856 | 18.0132 | 45.0922 | 47.4948 | 44.3231 | 21.4183 |  |  | 0.4359 | -0.119 | -48.793 | 0.2812 | 0.3254 | -197.8328 | 13.596 | -0.0503 | 0.049133 | 0.30348 | -0.0037016 | 8.8285 | 9.0584 | 1.9788 | 21.7664 | 21.9941 | 22.1936 | 22.2479 | 22.0774 | 21.3864 | 20.1954 | 22.1975 | 22.3659 | 22.4042 | 22.3505 | 21.975 | 21.2051 | 22.2675 | 17.0358 | 17.1174 | 15.9749 | 16.0714 | 16.2482 | 17.1172 | 16.8834 | 22.3643 | 22.1335 | 21.6904 | 22.0791 | 21.7894 | 21.3014 | 21.9454 | 21.5218 | 20.9007 | 20.0971 | 21.0487 | 19.9745 | 19.8353 | 0.076293 | -0.049992 | 20.8076 | 22.0583 | 22.3587 | 20.0993 | 21.6577 | 22.0921 | 21.9384 | 21.7038 | 21.264 | 21.7745 | 21.4359 | 21.0344 | 20.6351 | 21.3992 | 20.434 | 20.4854 | 20.228 |  | 20.2134 | 20.0737 | 20.1136 | 19.8065 | 20.0924 | 20.3598 |  | 20.416 |  |  | 20.2512 | 20.2832 | 20.6321 | [5 empty] | 21.9128 | 20.3639 | 21.6522 | 22.0256 | 19.6196 | 21.1482 | 21.768 | 19.38 | 20.0336 | 22.6837 |  | 19.7866 | 21.3245 | 18.9086 | 19.7473 | 21.5772 | 19.4675 | 20.133 | 19.0856 | 20.2202 | 19.1773 | 20.2819 | 18.7869 | 20.0561 | 21.3237 | 19.5396 | 19.7704 | 21.631 | 18.9298 | 19.8078 | 21.245 | 18.9606 | 20.1757 | 19.3594 | 20.2286 | 18.9575 | 20.2436 | -0.081938 | 20.9496 | 0.050509 | 0.01611 | -27.1118 | 3.0955 | -10.87 | -0.08 | 0.78963 | -0.40938 | -8.2893 | 0.62929 | 0.67727 | -16.6994 | 4.3778 | 0.41955 | 0.4205 | 0.42721 | 0.41156 | 0.50216 | 0.44286 | 0.42656
42838.4199 | -36 | 22.9049 | 22.871 | 22.8636 | 22.7845 | 22.409 | 21.7473 | 22.7286 | 21.8081 | 22.3745 | 22.3758 | 22.3603 | 22.0213 | 21.233 | 22.2035 | 21.5899 | 21.7629 | 21.8902 | 21.08 | 21.1794 | 21.394 | 20.4748 | 20.6119 | 20.9039 | 21.8788 | 21.6425 | 21.2686 | 20.9428 | 20.909 | 21.3697 | 22.0863 | 21.6803 | 21.1878 | 22.0002 | 21.7366 | 21.3528 | 19.9335 | 21.9598 |  | 20.589 | 20.3619 | 20.3623 | 19.0557 |  | 16.8743 | 16.8196 | 16.492 | 16.6556 | 16.6383 | 17.1103 | 17.6409 | 15.4897 | 17.001 | 16.0679 | 16.9817 | 18.0054 | 45.0264 | 47.514 | 44.258 | 21.4078 |  |  | 0.27753 | -0.085489 | -48.2009 | 0.25886 | 0.15652 | -197.8716 | 13.9226 | -0.012848 | -0.1912 | 0.10858 | 0.0048048 | 8.828 | 9.0578 | 1.9787 | 21.7694 | 21.9903 | 22.1874 | 22.2456 | 22.0718 | 21.3823 | 20.1977 | 22.1943 | 22.3634 | 22.4009 | 22.3506 | 21.9721 | 21.197 | 22.268 | 17.0497 | 17.1225 | 16.0035 | 16.0721 | 16.2235 | 17.1172 | 16.8802 | 22.3661 | 22.1316 | 21.6919 | 22.0727 | 21.7887 | 21.2954 | 21.943 | 21.5282 | 20.9045 | 20.0992 | 21.0629 | 19.9666 | 19.8457 | -0.067618 | -0.087461 | 20.806 | 22.0603 | 22.3614 | 20.0991 | 21.6567 | 22.0984 | 21.9389 | 21.7043 | 21.2723 | 21.7762 | 21.4428 | 21.0315 | 20.6305 | 21.3997 | 20.4379 | 20.4891 | 20.2239 |  | 20.2101 | 20.0409 | 20.1161 | 19.8117 | 20.0932 | 20.3654 |  | 20.416 |  |  | 20.2602 | 20.2904 | 20.6339 | [5 empty] | 21.9158 | 20.3616 | 21.6522 | 22.0283 | 19.621 | 21.1505 | 21.7721 | 19.3848 | 20.0429 | 22.7091 |  | 19.7896 | 21.3442 | 18.9138 | 19.7501 | 21.5914 | 19.4762 | 20.1416 | 19.0917 | 20.2314 | 19.1884 | 20.29 | 18.7884 | 20.0679 | 21.3446 | 19.5428 | 19.7707 | 21.6357 | 18.928 | 19.8087 | 21.2531 | 18.9646 | 20.1793 | 19.3634 | 20.2257 | 18.9552 | 20.2488 | -0.16875 | 20.9487 | 0.050343 | 0.014302 | -27.0786 | 3.0955 | -3.39 | -0.05 | 0.63006 | -0.34698 | -8.2389 | 0.60377 | 0.46973 | -16.7014 | 4.4302 | 0.41956 | 0.42149 | 0.42709 | 0.41001 | 0.49861 | 0.44274 | 0.42635
42838.4199 | -35 | 22.898 | 22.8702 | 22.8514 | 22.772 | 22.3964 | 21.735 | 22.7122 | 21.7929 | 22.3594 | 22.3741 | 22.3473 | 22.0155 | 21.2334 | 22.1941 | 21.5846 | 21.7641 | 21.8894 | 21.0806 | 21.1774 | 21.3937 | 20.475 | 20.6051 | 20.9024 | 21.8725 | 21.638 | 21.2596 | 20.9397 | 20.9096 | 21.3572 | 22.0806 | 21.6768 | 21.1963 | 22.0094 | 21.737 | 21.3573 | 19.9415 | 21.9544 |  | 20.5921 | 20.3795 | 20.3705 | 19.0673 |  | 16.8801 | 16.8247 | 16.5017 | 16.65 | 16.6373 | 17.0919 | 17.6188 | 15.4732 | 17.0054 | 16.081 | 16.988 | 18.0018 | 44.9781 | 47.5357 | 44.203 | 21.4075 |  |  | 0.25519 | 0.027535 | -48.0044 | 0.13269 | 0.024444 | -197.8729 | 14.0934 | -0.0917 | -0.19373 | 0.17068 | 0.049941 | 8.8288 | 9.059 | 1.9786 | 21.7727 | 21.9886 | 22.1867 | 22.2443 | 22.062 | 21.3779 | 20.1892 | 22.1945 | 22.3573 | 22.3942 | 22.3478 | 21.9751 | 21.1968 | 22.2693 | 17.0529 | 17.1299 | 16.0279 | 16.0924 | 16.2039 | 17.1129 | 16.8683 | 22.3684 | 22.1348 | 21.6927 | 22.0752 | 21.7893 | 21.2936 | 21.9409 | 21.5269 | 20.8971 | 20.0962 | 21.0584 | 19.967 | 19.8386 | 0.054274 | -0.052464 | 20.7976 | 22.0542 | 22.3446 | 20.0899 | 21.6509 | 22.0924 | 21.9252 | 21.6971 | 21.257 | 21.7629 | 21.4245 | 21.0289 | 20.629 | 21.3807 | 20.4356 | 20.4863 | 20.2201 |  | 20.2145 | 20.0244 | 20.1163 | 19.8189 | 20.0985 | 20.372 |  | 20.4201 |  |  | 20.2537 | 20.2895 | 20.634 | [5 empty] | 21.9125 | 20.3581 | 21.647 | 22.0278 | 19.6221 | 21.1429 | 21.7667 | 19.3921 | 20.0447 | 22.7395 |  | 19.7972 | 21.3644 | 18.9169 | 19.7546 | 21.6089 | 19.4894 | 20.1433 | 19.0968 | 20.237 | 19.188 | 20.2912 | 18.7955 | 20.08 | 21.3678 | 19.5497 | 19.78 | 21.6564 | 18.9408 | 19.8202 | 21.2657 | 18.9737 | 20.1875 | 19.3698 | 20.2305 | 18.9646 | 20.2482 | -0.00477 | 20.9481 | 0.049378 | 0.012408 | -27.0679 | 3.0955 | -9.24 | -0.13 | 0.60415 | 0.19692 | -8.2222 | 0.43229 | 0.18562 | -16.7009 | 4.4571 | 0.41981 | 0.42196 | 0.42707 | 0.40915 | 0.49451 | 0.44269 | 0.42644
42838.4199 | -34 | 22.9066 | 22.8624 | 22.8543 | 22.7792 | 22.408 | 21.737 | 22.7198 | 21.8009 | 22.3697 | 22.3758 | 22.3501 | 22.0178 | 21.2338 | 22.2026 | 21.5919 | 21.7662 | 21.8951 | 21.0856 | 21.1762 | 21.4003 | 20.4754 | 20.6104 | 20.9039 | 21.8765 | 21.6401 | 21.2615 | 20.9477 | 20.9195 | 21.3573 | 22.0751 | 21.6715 | 21.191 | 21.9981 | 21.7392 | 21.3527 | 19.9347 | 21.9422 |  | 20.587 | 20.3818 | 20.3749 | 19.0615 |  | 16.8723 | 16.8103 | 16.4947 | 16.6408 | 16.6287 | 17.0698 | 17.6454 | 15.4524 | 16.9941 | 16.0769 | 16.9768 | 18.0129 | 44.9495 | 47.5716 | 44.1649 | 21.4166 |  |  | 0.21379 | -0.048033 | -47.8198 | 0.32391 | 0.31752 | -197.8453 | 14.1539 | -0.1285 | -0.018199 | 0.051093 | 0.089522 | 8.8288 | 9.0587 | 1.9788 | 21.7743 | 21.9915 | 22.1854 | 22.2482 | 22.0673 | 21.3837 | 20.1903 | 22.1912 | 22.3655 | 22.3983 | 22.3496 | 21.9703 | 21.1954 | 22.2625 | 17.0586 | 17.1537 | 16.0347 | 16.1134 | 16.2143 | 17.1166 | 16.8739 | 22.3678 | 22.1261 | 21.6908 | 22.0767 | 21.7872 | 21.288 | 21.9406 | 21.5169 | 20.8985 | 20.1027 | 21.0566 | 19.9598 | 19.8366 | 0.051521 | -0.22859 | 20.7925 | 22.0561 | 22.361 | 20.0903 | 21.6517 | 22.1004 | 21.9381 | 21.6948 | 21.2719 | 21.7697 | 21.4374 | 21.0284 | 20.6323 | 21.3964 | 20.4576 | 20.5047 | 20.2149 |  | 20.2124 | 20.0048 | 20.1086 | 19.818 | 20.0932 | 20.3658 |  | 20.411 |  |  | 20.2485 | 20.2899 | 20.6344 | [5 empty] | 21.9072 | 20.3509 | 21.6438 | 22.0191 | 19.6204 | 21.1423 | 21.7619 | 19.396 | 20.0519 | 22.7532 |  | 19.8063 | 21.3799 | 18.9223 | 19.7655 | 21.6211 | 19.4931 | 20.1372 | 19.097 | 20.2426 | 19.1894 | 20.29 | 18.8021 | 20.0937 | 21.3842 | 19.5519 | 19.7804 | 21.6722 | 18.9437 | 19.8252 | 21.2848 | 18.9806 | 20.189 | 19.3754 | 20.2312 | 18.9592 | 20.2537 | -0.13332 | 20.9485 | 0.050306 | 0.01423 | -27.0503 | 3.0955 | -1.98 | -0.1 | 0.55298 | -0.26008 | -8.2062 | 0.67538 | 0.66898 | -16.6991 | 4.4665 | 0.41988 | 0.42224 | 0.42691 | 0.40895 | 0.49441 | 0.44262 | 0.42672
42838.4199 | -33 | 22.9012 | 22.8674 | 22.8513 | 22.781 | 22.4018 | 21.7399 | 22.7186 | 21.7989 | 22.3719 | 22.3815 | 22.3494 | 22.0163 | 21.2322 | 22.2005 | 21.6035 | 21.7739 | 21.9014 | 21.0917 | 21.1824 | 21.4005 | 20.4757 | 20.6094 | 20.9007 | 21.8784 | 21.645 | 21.2675 | 20.9615 | 20.9255 | 21.363 | 22.0694 | 21.6636 | 21.1884 | 21.99 | 21.7333 | 21.3475 | 19.9265 | 21.91 |  | 20.5886 | 20.3741 | 20.3757 | 19.0592 |  | 16.873 | 16.8157 | 16.5009 | 16.6474 | 16.6182 | 17.075 | 17.7037 | 15.4325 | 17.0009 | 16.0905 | 16.9838 | 18.0103 | 44.9029 | 47.5991 | 44.129 | 21.4202 |  |  | 0.24796 | 0.022935 | -47.7882 | 0.48622 | 0.33526 | -197.8657 | 14.0533 | 0.029868 | -0.089228 | 0.015217 | -0.049011 | 8.8293 | 9.0589 | 1.979 | 21.7763 | 21.9992 | 22.1849 | 22.2556 | 22.0718 | 21.3925 | 20.1961 | 22.1945 | 22.3709 | 22.4078 | 22.3519 | 21.9719 | 21.2039 | 22.2657 | 17.0228 | 17.186 | 16.0156 | 16.1323 | 16.2086 | 17.1169 | 16.8739 | 22.364 | 22.1279 | 21.6845 | 22.0684 | 21.7885 | 21.2925 | 21.9401 | 21.5116 | 20.893 | 20.0943 | 21.0519 | 19.949 | 19.8401 | 0.044444 | -0.016707 | 20.7883 | 22.0515 | 22.3493 | 20.0798 | 21.6447 | 22.0951 | 21.9251 | 21.6955 | 21.2619 | 21.7667 | 21.4339 | 21.0354 | 20.6333 | 21.4057 | 20.4636 | 20.5023 | 20.2275 |  | 20.2266 | 20.005 | 20.1162 | 19.832 | 20.0977 | 20.3732 |  | 20.4118 |  |  | 20.2587 | 20.3034 | 20.6427 | [5 empty] | 21.9128 | 20.354 | 21.6509 | 22.0221 | 19.6224 | 21.1479 | 21.7676 | 19.4044 | 20.0604 | 22.7615 |  | 19.8212 | 21.4004 | 18.9337 | 19.7706 | 21.6358 | 19.4929 | 20.1359 | 19.0976 | 20.2479 | 19.1896 | 20.2969 | 18.8098 | 20.1127 | 21.4043 | 19.5594 | 19.7898 | 21.6871 | 18.946 | 19.8267 | 21.3046 | 18.991 | 20.1948 | 19.3784 | 20.2281 | 18.9617 | 20.2672 | -0.13518 | 20.9487 | 0.051049 | 0.015805 | -27.0907 | 3.0956 | -15.1 | -0.13 | 0.59554 | 0.17972 | -8.2035 | 0.82748 | 0.68742 | -16.7001 | 4.4507 | 0.42001 | 0.42249 | 0.42668 | 0.41296 | 0.49653 | 0.44241 | 0.42634
42838.4199 | -32 | 22.8998 | 22.865 | 22.8508 | 22.784 | 22.4084 | 21.7339 | 22.7105 | 21.7946 | 22.3619 | 22.3713 | 22.3517 | 22.0129 | 21.2278 | 22.1985 | 21.5971 | 21.7623 | 21.9018 | 21.0827 | 21.1779 | 21.3872 | 20.4711 | 20.6076 | 20.8984 | 21.8799 | 21.6372 | 21.2688 | 20.9706 | 20.9339 | 21.3683 | 22.0766 | 21.6748 | 21.1918 | 21.9994 | 21.7311 | 21.3476 | 19.9268 | 21.888 |  | 20.6015 | 20.395 | 20.3854 | 19.0763 |  | 16.8797 | 16.8285 | 16.511 | 16.6474 | 16.6369 | 17.0816 | 17.7365 | 15.4228 | 17.0055 | 16.1082 | 16.9876 | 18.0069 | 44.8554 | 47.6273 | 44.0878 | 21.4151 |  |  | 0.31236 | -0.37331 | -47.9479 | 0.50002 | 0.32606 | -197.8499 | 14.0008 | -0.06936 | 0.16589 | 0.22942 | -0.027138 | 8.8298 | 9.0598 | 1.9786 | 21.782 | 22.0004 | 22.1957 | 22.2531 | 22.0808 | 21.3896 | 20.1916 | 22.2014 | 22.367 | 22.4144 | 22.3574 | 21.98 | 21.2054 | 22.2765 | 16.9895 | 17.213 | 16.0208 | 16.1265 | 16.1988 | 17.1113 | 16.8703 | 22.3654 | 22.1293 | 21.6905 | 22.0731 | 21.7887 | 21.2936 | 21.9363 | 21.5171 | 20.8942 | 20.0992 | 21.0585 | 19.946 | 19.8365 | -0.028691 | 0.0064978 | 20.7807 | 22.0514 | 22.3546 | 20.0798 | 21.6456 | 22.0909 | 21.9321 | 21.6944 | 21.2667 | 21.758 | 21.4294 | 21.0263 | 20.631 | 21.4208 | 20.4694 | 20.5085 | 20.2242 |  | 20.2241 | 19.9908 | 20.1161 | 19.834 | 20.101 | 20.373 |  | 20.4177 |  |  | 20.2631 | 20.3196 | 20.6538 | [5 empty] | 21.918 | 20.3682 | 21.6537 | 22.0395 | 19.6419 | 21.1568 | 21.7791 | 19.4063 | 20.0592 | 22.7642 |  | 19.8171 | 21.4051 | 18.9356 | 19.766 | 21.6466 | 19.4936 | 20.1358 | 19.0897 | 20.2469 | 19.1847 | 20.2869 | 18.8209 | 20.1188 | 21.4172 | 19.5758 | 19.7934 | 21.6981 | 18.9484 | 19.8393 | 21.3174 | 18.9885 | 20.2099 | 19.3819 | 20.2252 | 18.9676 | 20.2779 | -0.10142 | 20.9495 | 0.050822 | 0.014847 | -27.0814 | 3.0955 | -3.83 | 0.68 | 0.66842 | -0.72508 | -8.2174 | 0.83916 | 0.67794 | -16.6996 | 4.4424 | 0.42002 | 0.42288 | 0.42673 | 0.41601 | 0.49553 | 0.44194 | 0.4266
42838.4199 | -31 | 22.9006 | 22.8653 | 22.8542 | 22.772 | 22.4004 | 21.7373 | 22.7068 | 21.7972 | 22.3668 | 22.3671 | 22.3526 | 22.0093 | 21.2252 | 22.1948 | 21.5951 | 21.7675 | 21.8985 | 21.0841 | 21.1788 | 21.3836 | 20.4686 | 20.6096 | 20.8977 | 21.8821 | 21.6418 | 21.2698 | 20.9726 | 20.9372 | 21.3732 | 22.0718 | 21.6758 | 21.1864 | 22.0006 | 21.7385 | 21.3515 | 19.9363 | 21.879 |  | 20.5957 | 20.4057 | 20.3915 | 19.0989 |  | 16.8685 | 16.8187 | 16.4976 | 16.6381 | 16.6232 | 17.0737 | 17.7435 | 15.4016 | 17.0025 | 16.1117 | 16.9763 | 18.0133 | 44.8243 | 47.6543 | 44.0638 | 21.4119 |  |  | 0.24731 | -0.15252 | -47.7705 | 0.50133 | 0.29649 | -197.8263 | 13.822 | -0.026644 | 0.049911 | 0.11949 | -0.023839 | 8.8283 | 9.0583 | 1.9788 | 21.7681 | 21.9995 | 22.1841 | 22.2533 | 22.0685 | 21.3874 | 20.1943 | 22.1903 | 22.3725 | 22.3971 | 22.3426 | 21.9732 | 21.2056 | 22.2593 | 16.9852 | 17.2205 | 16.0365 | 16.1423 | 16.1766 | 17.1241 | 16.8753 | 22.3796 | 22.1351 | 21.698 | 22.0824 | 21.7921 | 21.2987 | 21.946 | 21.5255 | 20.8967 | 20.1059 | 21.0725 | 19.9553 | 19.8244 | 0.12859 | 0.064128 | 20.7811 | 22.0432 | 22.3578 | 20.0797 | 21.642 | 22.0934 | 21.9285 | 21.6966 | 21.2649 | 21.77 | 21.431 | 21.0268 | 20.6369 | 21.4312 | 20.4675 | 20.5108 | 20.2222 |  | 20.2131 | 19.9716 | 20.1166 | 19.8269 | 20.1032 | 20.3672 |  | 20.4215 |  |  | 20.2394 | 20.3163 | 20.6423 | [5 empty] | 21.9038 | 20.3527 | 21.6434 | 22.0215 | 19.624 | 21.1472 | 21.7689 | 19.4109 | 20.0608 | 22.7725 |  | 19.8242 | 21.4158 | 18.9375 | 19.7704 | 21.6592 | 19.4865 | 20.1367 | 19.0844 | 20.2529 | 19.1833 | 20.2939 | 18.831 | 20.1279 | 21.4356 | 19.5773 | 19.7994 | 21.7142 | 18.9523 | 19.8449 | 21.3329 | 18.9967 | 20.2141 | 19.3849 | 20.2264 | 18.9775 | 20.2794 | -0.15836 | 20.947 | 0.051295 | 0.014012 | -27.0728 | 3.0954 | -4.64 | 0.94 | 0.59476 | -0.46345 | -8.202 | 0.84025 | 0.64646 | -16.6984 | 4.4139 | 0.41971 | 0.42343 | 0.427 | 0.41798 | 0.49437 | 0.44163 | 0.42716
42838.4199 | -30 | 22.9025 | 22.8653 | 22.859 | 22.7761 | 22.4015 | 21.7378 | 22.7143 | 21.7935 | 22.3681 | 22.3683 | 22.3528 | 22.016 | 21.2307 | 22.1912 | 21.6014 | 21.7663 | 21.8982 | 21.0935 | 21.1848 | 21.391 | 20.4726 | 20.6132 | 20.9066 | 21.8747 | 21.6463 | 21.2813 | 20.987 | 20.9528 | 21.379 | 22.0792 | 21.674 | 21.1909 | 22.006 | 21.7464 | 21.3566 | 19.9391 | 21.8573 |  | 20.6055 | 20.414 | 20.3958 | 19.1237 |  | 16.8727 | 16.8212 | 16.4898 | 16.6255 | 16.621 | 17.0757 | 17.7471 | 15.3939 | 17.0001 | 16.1235 | 16.9827 | 18.0041 | 44.7784 | 47.6787 | 44.0256 | 21.4118 |  |  | 0.24271 | -0.5021 | -47.3611 | 0.33114 | 0.33789 | -197.823 | 13.8076 | -0.20078 | 0.0575 | -0.031149 | -0.13581 | 8.8279 | 9.0578 | 1.9789 | 21.7801 | 21.9963 | 22.1918 | 22.2515 | 22.0689 | 21.391 | 20.1979 | 22.1919 | 22.3676 | 22.4034 | 22.3515 | 21.9788 | 21.2012 | 22.27 | 16.9787 | 17.187 | 16.055 | 16.1448 | 16.1513 | 17.112 | 16.8657 | 22.3704 | 22.1287 | 21.6837 | 22.0747 | 21.7829 | 21.2909 | 21.9365 | 21.5172 | 20.8916 | 20.0967 | 21.0733 | 19.9316 | 19.8196 | 0.10401 | 0.078584 | 20.7768 | 22.0585 | 22.3532 | 20.0827 | 21.6509 | 22.0945 | 21.9337 | 21.6946 | 21.2697 | 21.7712 | 21.4312 | 21.0282 | 20.6568 | 21.4467 | 20.4801 | 20.5222 | 20.2233 |  | 20.2254 | 19.9467 | 20.1195 | 19.8305 | 20.1052 | 20.3773 |  | 20.4288 |  |  | 20.2354 | 20.3178 | 20.6463 | [5 empty] | 21.9134 | 20.3591 | 21.6502 | 22.0272 | 19.62 | 21.1507 | 21.7755 | 19.4147 | 20.0661 | 22.7855 |  | 19.826 | 21.4228 | 18.9392 | 19.7621 | 21.6679 | 19.4874 | 20.126 | 19.0875 | 20.2417 | 19.178 | 20.2953 | 18.8383 | 20.1381 | 21.4529 | 19.5741 | 19.7981 | 21.7284 | 18.9518 | 19.8449 | 21.3447 | 19.0054 | 20.2141 | 19.3913 | 20.23 | 18.9734 | 20.2841 | -0.076929 | 20.9477 | 0.05081 | 0.014027 | -27.0751 | 3.0955 | -10.5 | 0.84 | 0.58921 | -0.84089 | -8.1669 | 0.68289 | 0.69011 | -16.6983 | 4.4116 | 0.42009 | 0.42422 | 0.42697 | 0.41729 | 0.4912 | 0.44104 | 0.42699
42838.4199 | -29 | 22.8982 | 22.8605 | 22.854 | 22.7778 | 22.3984 | 21.7297 | 22.712 | 21.7869 | 22.3593 | 22.3656 | 22.3472 | 22.0091 | 21.2255 | 22.1925 | 21.5955 | 21.7625 | 21.8914 | 21.0772 | 21.1798 | 21.4015 | 20.477 | 20.6172 | 20.9098 | 21.8712 | 21.6374 | 21.2669 | 20.9826 | 20.9446 | 21.3969 | 22.0743 | 21.6669 | 21.1895 | 21.9922 | 21.7357 | 21.3444 | 19.9303 | 21.8414 |  | 20.5971 | 20.4191 | 20.3913 | 19.1154 |  | 16.8666 | 16.8154 | 16.4843 | 16.6366 | 16.6202 | 17.0982 | 17.7771 | 15.4114 | 17.0068 | 16.1323 | 16.9819 | 17.9974 | 44.7334 | 47.7122 | 43.9928 | 21.4086 |  |  | 0.33405 | -0.18077 | -47.051 | 0.42183 | 0.41083 | -197.8486 | 14.029 | -0.002988 | -0.11355 | -0.15199 | -0.063246 | 8.827 | 9.0569 | 1.9786 | 21.7729 | 21.9926 | 22.1846 | 22.2539 | 22.0662 | 21.3753 | 20.1907 | 22.1816 | 22.3553 | 22.394 | 22.3436 | 21.9685 | 21.195 | 22.2582 | 16.9782 | 17.1408 | 16.0521 | 16.1628 | 16.1786 | 17.1166 | 16.8709 | 22.37 | 22.133 | 21.6926 | 22.0706 | 21.7895 | 21.2895 | 21.9392 | 21.5215 | 20.8949 | 20.097 | 21.0853 | 19.9314 | 19.8143 | 0.048966 | -0.060643 | 20.7642 | 22.0546 | 22.3522 | 20.0769 | 21.6534 | 22.0958 | 21.9334 | 21.6953 | 21.2571 | 21.7682 | 21.4326 | 21.0208 | 20.6668 | 21.4649 | 20.4784 | 20.5275 | 20.2206 |  | 20.2276 | 19.9427 | 20.1201 | 19.8325 | 20.1126 | 20.3758 |  | 20.4318 |  |  | 20.2355 | 20.3233 | 20.654 | [5 empty] | 21.9184 | 20.3627 | 21.6583 | 22.0278 | 19.6189 | 21.1614 | 21.7767 | 19.4137 | 20.0824 | 22.8018 |  | 19.8264 | 21.4418 | 18.9426 | 19.7771 | 21.6863 | 19.4962 | 20.1288 | 19.09 | 20.2547 | 19.1828 | 20.3006 | 18.8264 | 20.1349 | 21.4548 | 19.5712 | 19.7927 | 21.7272 | 18.9418 | 19.8301 | 21.3408 | 18.9959 | 20.2124 | 19.3752 | 20.2213 | 18.961 | 20.2694 | -0.24332 | 20.9469 | 0.049931 | 0.011936 | -27.1081 | 3.0954 | -13.2 | 1.2 | 0.69127 | -0.50455 | -8.14 | 0.77074 | 0.76099 | -16.7001 | 4.447 | 0.42024 | 0.42435 | 0.42716 | 0.41789 | 0.49212 | 0.44098 | 0.42714
42838.42 | -28 | 22.9008 | 22.8667 | 22.855 | 22.7743 | 22.3989 | 21.7324 | 22.7168 | 21.7939 | 22.3585 | 22.3672 | 22.352 | 22.0181 | 21.2316 | 22.1983 | 21.5898 | 21.7766 | 21.9017 | 21.0888 | 21.1812 | 21.3937 | 20.4798 | 20.6207 | 20.9034 | 21.8788 | 21.6389 | 21.2697 | 20.994 | 20.9644 | 21.4157 | 22.0791 | 21.6733 | 21.1919 | 21.9969 | 21.7358 | 21.3535 | 19.9396 | 21.8096 |  | 20.6009 | 20.431 | 20.4082 | 19.1084 |  | 16.8676 | 16.8071 | 16.484 | 16.6314 | 16.6218 | 17.0835 | 17.805 | 15.4938 | 17.0022 | 16.0543 | 16.969 | 17.9997 | 44.6952 | 47.7426 | 43.965 | 21.4144 |  |  | 0.22562 | -0.23926 | -47.1088 | 0.21877 | 0.19267 | -197.8374 | 14.2538 | 0.12843 | -0.22389 | -0.30137 | -0.026096 | 8.8285 | 9.0584 | 1.9788 | 21.7748 | 21.9959 | 22.1847 | 22.2537 | 22.0715 | 21.3818 | 20.1941 | 22.187 | 22.366 | 22.3949 | 22.3486 | 21.9697 | 21.2023 | 22.2692 | 16.9741 | 17.132 | 16.0464 | 16.1626 | 16.1961 | 17.1039 | 16.8678 | 22.3627 | 22.1304 | 21.6899 | 22.0751 | 21.7867 | 21.2883 | 21.939 | 21.5203 | 20.8984 | 20.0989 | 21.0971 | 19.9293 | 19.8327 | -0.074696 | -0.13881 | 20.7819 | 22.068 | 22.3735 | 20.0933 | 21.6545 | 22.0997 | 21.9451 | 21.7035 | 21.2744 | 21.7819 | 21.4384 | 21.0359 | 20.6947 | 21.4859 | 20.5017 | 20.5476 | 20.2118 |  | 20.226 | 19.9309 | 20.1125 | 19.8206 | 20.1056 | 20.3736 |  | 20.4272 |  |  | 20.24 | 20.3244 | 20.6427 | [5 empty] | 21.9071 | 20.3632 | 21.6615 | 22.0259 | 19.6151 | 21.1475 | 21.7752 | 19.4254 | 20.0833 | 22.84 |  | 19.8405 | 21.4591 | 18.9443 | 19.7759 | 21.6865 | 19.5078 | 20.1293 | 19.0891 | 20.2566 | 19.1817 | 20.2929 | 18.8474 | 20.1508 | 21.4847 | 19.5774 | 19.806 | 21.7546 | 18.9532 | 19.8371 | 21.3733 | 19.0203 | 20.2263 | 19.3884 | 20.2257 | 18.9742 | 20.2851 | -0.065429 | 20.9475 | 0.049568 | 0.012364 | -27.033 | 3.0955 | -35.66 | 0.69 | 0.56813 | -0.58045 | -8.1449 | 0.55505 | 0.52113 | -16.6992 | 4.4823 | 0.42043 | 0.42443 | 0.42726 | 0.41685 | 0.49239 | 0.44148 | 0.4267
42838.42 | -27 | 22.8955 | 22.8568 | 22.8532 | 22.7726 | 22.3987 | 21.7354 | 22.7164 | 21.7915 | 22.3635 | 22.3668 | 22.3498 | 22.0135 | 21.2209 | 22.1932 | 21.5894 | 21.7733 | 21.8948 | 21.0789 | 21.182 | 21.3968 | 20.4768 | 20.6091 | 20.9019 | 21.8774 | 21.6363 | 21.2618 | 20.9998 | 20.9672 | 21.4115 | 22.0806 | 21.6713 | 21.1929 | 21.9955 | 21.7388 | 21.3512 | 19.9314 | 21.7735 |  | 20.5984 | 20.4358 | 20.418 | 19.1206 |  | 16.8678 | 16.803 | 16.4788 | 16.6235 | 16.6077 | 17.0732 | 17.8253 | 15.5537 | 17.0052 | 16.0184 | 16.977 | 18.006 | 44.6648 | 47.7795 | 43.9383 | 21.4196 |  |  | 0.32945 | -0.10718 | -46.8091 | 0.24703 | 0.078328 | -197.8125 | 14.2354 | 0.066008 | -0.15014 | 0.017315 | -0.0066528 | 8.8287 | 9.0586 | 1.9788 | 21.7782 | 21.9983 | 22.1809 | 22.2507 | 22.0692 | 21.3844 | 20.1927 | 22.1862 | 22.3625 | 22.3969 | 22.3456 | 21.9726 | 21.1994 | 22.2641 | 16.9919 | 17.1328 | 16.0543 | 16.1517 | 16.1987 | 17.1088 | 16.8634 | 22.3684 | 22.1376 | 21.6932 | 22.0782 | 21.7875 | 21.2924 | 21.9383 | 21.5244 | 20.8967 | 20.1074 | 21.1054 | 19.932 | 19.8375 | -0.007262 | -0.11941 | 20.7759 | 22.0619 | 22.366 | 20.0909 | 21.6513 | 22.1037 | 21.9338 | 21.7049 | 21.2686 | 21.7716 | 21.4381 | 21.0421 | 20.6986 | 21.4704 | 20.4995 | 20.5456 | 20.2041 |  | 20.2163 | 19.9147 | 20.1086 | 19.8168 | 20.1009 | 20.3748 |  | 20.4264 |  |  | 20.2286 | 20.3153 | 20.6398 | [5 empty] | 21.9075 | 20.3497 | 21.6491 | 22.0231 | 19.6203 | 21.1494 | 21.7694 | 19.4215 | 20.0777 | 22.8634 |  | 19.8342 | 21.4701 | 18.9353 | 19.7793 | 21.6921 | 19.5045 | 20.1201 | 19.0842 | 20.2676 | 19.1877 | 20.3016 | 18.8504 | 20.1564 | 21.5053 | 19.5877 | 19.8071 | 21.7476 | 18.9521 | 19.8411 | 21.3659 | 19.0197 | 20.2277 | 19.3892 | 20.2329 | 18.9733 | 20.2895 | -0.08806 | 20.9467 | 0.050933 | 0.013751 | -27.1135 | 3.0954 | -30.84 | 0.84 | 0.68651 | -0.38849 | -8.1189 | 0.5898 | 0.33227 | -16.6978 | 4.4794 | 0.42031 | 0.42475 | 0.4272 | 0.41545 | 0.49099 | 0.44087 | 0.42685
42838.42 | -26 | 22.9038 | 22.8634 | 22.849 | 22.7724 | 22.4049 | 21.7355 | 22.7122 | 21.7951 | 22.3622 | 22.3649 | 22.3457 | 22.0043 | 21.2266 | 22.1956 | 21.5914 | 21.7648 | 21.896 | 21.0901 | 21.1742 | 21.3952 | 20.4711 | 20.611 | 20.9073 | 21.8794 | 21.6334 | 21.2631 | 21.0088 | 20.9756 | 21.4426 | 22.07 | 21.6668 | 21.1842 | 21.9919 | 21.734 | 21.3452 | 19.9279 | 21.7593 |  | 20.6038 | 20.4443 | 20.4212 | 19.1261 |  | 16.8758 | 16.8054 | 16.4879 | 16.6265 | 16.6105 | 17.0668 | 17.8488 | 15.6236 | 17.0162 | 16.0228 | 16.9868 | 18.0066 | 44.643 | 47.8102 | 43.9082 | 21.4163 |  |  | 0.27951 | -0.080889 | -46.6324 | 0.54208 | 0.21961 | -197.8315 | 14.4154 | -0.085128 | -0.012361 | 0.026336 | -0.087203 | 8.8287 | 9.0585 | 1.9785 | 21.7739 | 21.993 | 22.179 | 22.2498 | 22.0647 | 21.3799 | 20.1854 | 22.1841 | 22.3611 | 22.3908 | 22.3438 | 21.968 | 21.199 | 22.2554 | 17.0133 | 17.1277 | 16.0438 | 16.1306 | 16.2042 | 17.1087 | 16.8617 | 22.357 | 22.1329 | 21.6924 | 22.068 | 21.7827 | 21.2962 | 21.9283 | 21.5174 | 20.8808 | 20.1005 | 21.1062 | 19.9149 | 19.8442 | -0.049531 | -0.09564 | 20.7794 | 22.0569 | 22.3642 | 20.0933 | 21.659 | 22.1029 | 21.9386 | 21.7027 | 21.2748 | 21.7728 | 21.4444 | 21.0385 | 20.7156 | 21.4719 | 20.5139 | 20.5455 | 20.1999 |  | 20.2171 | 19.9006 | 20.1036 | 19.821 | 20.0977 | 20.3688 |  | 20.4251 |  |  | 20.2125 | 20.3126 | 20.6396 | [5 empty] | 21.9041 | 20.3456 | 21.6487 | 22.019 | 19.6099 | 21.1449 | 21.7713 | 19.4347 | 20.0939 | 22.8881 |  | 19.8543 | 21.4774 | 18.9396 | 19.7925 | 21.7053 | 19.5083 | 20.1319 | 19.095 | 20.2726 | 19.1914 | 20.3039 | 18.8465 | 20.1704 | 21.5166 | 19.5932 | 19.8133 | 21.7745 | 18.9551 | 19.8503 | 21.3758 | 19.0254 | 20.2329 | 19.3891 | 20.2307 | 18.9833 | 20.296 | -0.10086 | 20.9475 | 0.051461 | 0.01415 | -27.1293 | 3.0954 | -13.95 | 0.98 | 0.63237 | -0.3375 | -8.1036 | 0.8737 | 0.55636 | -16.6984 | 4.5076 | 0.42046 | 0.42497 | 0.42698 | 0.41306 | 0.49198 | 0.4406 | 0.42643
42838.42 | -25 | 22.8973 | 22.8618 | 22.8458 | 22.774 | 22.3997 | 21.7363 | 22.7131 | 21.7946 | 22.359 | 22.3686 | 22.3485 | 22.0042 | 21.222 | 22.1932 | 21.5873 | 21.7564 | 21.8902 | 21.0817 | 21.1761 | 21.393 | 20.4708 | 20.609 | 20.9037 | 21.873 | 21.6323 | 21.26 | 21.022 | 20.9766 | 21.4657 | 22.0731 | 21.6698 | 21.182 | 21.9919 | 21.7267 | 21.3459 | 19.925 | 21.7544 |  | 20.5995 | 20.444 | 20.4261 | 19.1281 |  | 16.8664 | 16.8 | 16.4802 | 16.624 | 16.6052 | 17.06 | 17.8398 | 15.6475 | 17.0061 | 16.0273 | 16.9753 | 18.0017 | 44.6282 | 47.8385 | 43.8778 | 21.4136 |  |  | 0.25651 | -0.16237 | -46.8505 | 0.6137 | 0.13024 | -197.8598 | 14.3228 | -0.13507 | 0.19469 | 0.22124 | -0.12331 | 8.8295 | 9.0592 | 1.9785 | 21.7768 | 21.9951 | 22.1876 | 22.2456 | 22.0636 | 21.3791 | 20.194 | 22.1875 | 22.3608 | 22.3962 | 22.3527 | 21.9686 | 21.2042 | 22.2583 | 17.0521 | 17.144 | 16.0519 | 16.1327 | 16.2052 | 17.1058 | 16.8713 | 22.3699 | 22.134 | 21.6986 | 22.0812 | 21.7944 | 21.2948 | 21.9498 | 21.5221 | 20.903 | 20.103 | 21.1001 | 19.9242 | 19.8491 | -0.056609 | -0.046188 | 20.7716 | 22.0581 | 22.3548 | 20.089 | 21.6572 | 22.0962 | 21.9324 | 21.7014 | 21.2704 | 21.7691 | 21.4332 | 21.0333 | 20.7133 | 21.4622 | 20.5066 | 20.5591 | 20.2063 |  | 20.2198 | 19.9007 | 20.1159 | 19.8226 | 20.0991 | 20.3718 |  | 20.4213 |  |  | 20.2207 | 20.3185 | 20.6471 | [5 empty] | 21.9058 | 20.3545 | 21.6555 | 22.0285 | 19.6139 | 21.1562 | 21.7737 | 19.4301 | 20.0894 | 22.9016 |  | 19.8454 | 21.479 | 18.9329 | 19.7876 | 21.6896 | 19.5035 | 20.1213 | 19.0868 | 20.2595 | 19.1911 | 20.2895 | 18.8645 | 20.1765 | 21.5374 | 19.6025 | 19.8221 | 21.798 | 18.9687 | 19.8537 | 21.3873 | 19.0431 | 20.2489 | 19.395 | 20.2439 | 18.988 | 20.2914 | -0.034821 | 20.9466 | 0.051572 | 0.015885 | -27.1734 | 3.0954 | -10.01 | 0.49 | 0.60582 | -0.47817 | -8.1224 | 0.92962 | 0.42845 | -16.6994 | 4.493 | 0.42037 | 0.42538 | 0.42698 | 0.40841 | 0.49219 | 0.44044 | 0.42638
42838.42 | -24 | 22.8969 | 22.8624 | 22.8484 | 22.7779 | 22.4008 | 21.7292 | 22.712 | 21.7977 | 22.3593 | 22.3715 | 22.3504 | 22.0105 | 21.2246 | 22.1944 | 21.5916 | 21.7651 | 21.8992 | 21.0794 | 21.176 | 21.3966 | 20.4741 | 20.6133 | 20.9028 | 21.8786 | 21.6381 | 21.2639 | 21.0308 | 20.9836 | 21.4822 | 22.0801 | 21.6692 | 21.1876 | 21.9963 | 21.7375 | 21.3485 | 19.9343 | 21.7616 |  | 20.607 | 20.4457 | 20.4327 | 19.1409 |  | 16.8614 | 16.7912 | 16.4845 | 16.6225 | 16.5919 | 17.0682 | 17.8531 | 15.6564 | 17.0053 | 16.0277 | 16.9816 | 18.0053 | 44.6266 | 47.8675 | 43.855 | 21.416 |  |  | 0.37544 | -0.29511 | -46.2585 | 0.55719 | 0.353 | -197.8374 | 14.4161 | -0.20472 | 0.01897 | 0.020672 | -0.07644 | 8.8294 | 9.0593 | 1.9786 | 21.769 | 21.9999 | 22.1885 | 22.2513 | 22.0707 | 21.3748 | 20.1978 | 22.1891 | 22.3669 | 22.3931 | 22.3514 | 21.9763 | 21.1984 | 22.2622 | 17.0838 | 17.1399 | 16.0492 | 16.1302 | 16.2198 | 17.1032 | 16.8648 | 22.3738 | 22.1313 | 21.6959 | 22.0743 | 21.7937 | 21.2969 | 21.9436 | 21.525 | 20.9018 | 20.1012 | 21.0878 | 19.9167 | 19.8497 | -0.033803 | -0.1934 | 20.7705 | 22.0596 | 22.3572 | 20.0842 | 21.6531 | 22.099 | 21.9351 | 21.7 | 21.2633 | 21.773 | 21.4366 | 21.0355 | 20.7227 | 21.455 | 20.5201 | 20.5656 | 20.2019 |  | 20.2221 | 19.9056 | 20.1124 | 19.8235 | 20.0973 | 20.3749 |  | 20.4225 |  |  | 20.2166 | 20.3149 | 20.6437 | [5 empty] | 21.9111 | 20.3434 | 21.6499 | 22.0252 | 19.6068 | 21.155 | 21.7609 | 19.4359 | 20.0936 | 22.9102 |  | 19.8477 | 21.4962 | 18.9444 | 19.7881 | 21.7003 | 19.5035 | 20.1176 | 19.0851 | 20.2603 | 19.1802 | 20.2898 | 18.8612 | 20.1716 | 21.5388 | 19.5956 | 19.8205 | 21.808 | 18.9572 | 19.8506 | 21.394 | 19.039 | 20.2471 | 19.3919 | 20.2391 | 18.9818 | 20.2815 | -0.20659 | 20.9474 | 0.051449 | 0.016429 | -27.0733 | 3.0954 | -3.18 | 0.32 | 0.73296 | -0.64463 | -8.0708 | 0.88578 | 0.70537 | -16.6987 | 4.5077 | 0.42057 | 0.42513 | 0.4269 | 0.40458 | 0.49173 | 0.4404 | 0.4263
42838.42 | -23 | 22.8975 | 22.8658 | 22.851 | 22.7803 | 22.4012 | 21.7276 | 22.7167 | 21.7982 | 22.3686 | 22.3708 | 22.3499 | 22.012 | 21.2261 | 22.1986 | 21.5997 | 21.7718 | 21.9063 | 21.0844 | 21.1863 | 21.4002 | 20.4775 | 20.6172 | 20.9054 | 21.8749 | 21.6472 | 21.2686 | 21.0435 | 20.9967 | 21.4984 | 22.0786 | 21.6743 | 21.1888 | 21.9997 | 21.7362 | 21.3541 | 19.9348 | 21.7611 |  | 20.614 | 20.4519 | 20.4371 | 19.1479 |  | 16.8643 | 16.7928 | 16.478 | 16.6253 | 16.5896 | 17.0664 | 17.869 | 15.6689 | 17.0061 | 16.0158 | 16.9833 | 18.0122 | 44.6273 | 47.9078 | 43.841 | 21.4236 |  |  | 0.36821 | -0.22086 | -46.4122 | 0.18263 | 0.1079 | -197.8243 | 14.1986 | -0.1653 | 0.10304 | 0.082982 | -0.018631 | 8.8287 | 9.0586 | 1.9785 | 21.7788 | 21.9949 | 22.1882 | 22.2475 | 22.0663 | 21.38 | 20.1971 | 22.1928 | 22.3684 | 22.401 | 22.3518 | 21.9738 | 21.1943 | 22.2636 | 17.1093 | 17.1364 | 16.0594 | 16.1317 | 16.2224 | 17.1119 | 16.8679 | 22.371 | 22.1216 | 21.6867 | 22.0673 | 21.7852 | 21.2982 | 21.9399 | 21.518 | 20.8947 | 20.0987 | 21.082 | 19.9117 | 19.8412 | 0.15651 | -0.0003494 | 20.7739 | 22.0531 | 22.3571 | 20.0808 | 21.6497 | 22.0961 | 21.93 | 21.6997 | 21.2621 | 21.7729 | 21.4378 | 21.031 | 20.7386 | 21.4471 | 20.5228 | 20.577 | 20.223 |  | 20.236 | 19.9399 | 20.1307 | 19.8411 | 20.1102 | 20.3846 |  | 20.4304 |  |  | 20.2146 | 20.3077 | 20.6431 | [5 empty] | 21.9088 | 20.3526 | 21.6522 | 22.0215 | 19.6113 | 21.1477 | 21.7681 | 19.4332 | 20.0919 | 22.9142 |  | 19.8477 | 21.4971 | 18.9405 | 19.7866 | 21.7046 | 19.5024 | 20.1222 | 19.0806 | 20.2643 | 19.1807 | 20.2888 | 18.8681 | 20.1867 | 21.5619 | 19.6008 | 19.8228 | 21.8247 | 18.9647 | 19.8588 | 21.4099 | 19.043 | 20.2563 | 19.3971 | 20.2403 | 18.9932 | 20.2921 | -0.092326 | 20.9476 | 0.049648 | 0.015892 | -27.0579 | 3.0954 | -9.31 | 0.54 | 0.72589 | -0.55767 | -8.0842 | 0.50712 | 0.38998 | -16.6981 | 4.4735 | 0.42045 | 0.42479 | 0.42684 | 0.40277 | 0.49096 | 0.44022 | 0.42645
42838.42 | -22 | 22.8963 | 22.8596 | 22.8524 | 22.7765 | 22.3932 | 21.7327 | 22.7225 | 21.794 | 22.3645 | 22.3722 | 22.3526 | 22.0083 | 21.2224 | 22.1921 | 21.593 | 21.7692 | 21.9032 | 21.0834 | 21.1847 | 21.3949 | 20.4762 | 20.6138 | 20.9079 | 21.8784 | 21.6399 | 21.2606 | 21.0463 | 21.0102 | 21.4769 | 22.0807 | 21.6768 | 21.1914 | 21.9988 | 21.7326 | 21.3547 | 19.9352 | 21.7587 |  | 20.6106 | 20.4551 | 20.4518 | 19.1421 |  | 16.8622 | 16.8015 | 16.484 | 16.6269 | 16.5922 | 17.0591 | 17.8869 | 15.616 | 17.01 | 16.0115 | 16.9836 | 17.9998 | 44.6061 | 47.9314 | 43.8175 | 21.4147 |  |  | 0.32616 | -0.33914 | -46.6133 | 0.22995 | 0.13484 | -197.8545 | 14.1158 | -0.21064 | -0.21436 | -0.18032 | 0.13466 | 8.8289 | 9.0589 | 1.9787 | 21.7731 | 21.9929 | 22.1881 | 22.249 | 22.0762 | 21.3835 | 20.1965 | 22.1926 | 22.3636 | 22.403 | 22.3443 | 21.961 | 21.2015 | 22.2586 | 17.1183 | 17.1305 | 16.0571 | 16.1288 | 16.2124 | 17.1071 | 16.8603 | 22.3752 | 22.1299 | 21.6918 | 22.0792 | 21.795 | 21.3067 | 21.9509 | 21.5221 | 20.9005 | 20.1011 | 21.0915 | 19.9157 | 19.8456 | 0.14805 | 0.011443 | 20.7746 | 22.0561 | 22.3615 | 20.0921 | 21.6516 | 22.1025 | 21.9426 | 21.698 | 21.2694 | 21.766 | 21.4327 | 21.0417 | 20.7578 | 21.4466 | 20.5373 | 20.5816 | 20.2215 |  | 20.2314 | 19.9496 | 20.1222 | 19.8355 | 20.1033 | 20.3761 |  | 20.4302 |  |  | 20.2169 | 20.2985 | 20.6423 | [5 empty] | 21.9041 | 20.3466 | 21.6488 | 22.0173 | 19.6127 | 21.1464 | 21.7684 | 19.4429 | 20.1002 | 22.9421 |  | 19.8594 | 21.5114 | 18.9475 | 19.7945 | 21.7123 | 19.5073 | 20.1225 | 19.0916 | 20.2744 | 19.1875 | 20.302 | 18.8729 | 20.191 | 21.5735 | 19.6086 | 19.8302 | 21.8457 | 18.9712 | 19.8604 | 21.4231 | 19.0553 | 20.2678 | 19.4009 | 20.2394 | 18.9974 | 20.2978 | -0.086205 | 20.9471 | 0.048211 | 0.01391 | -27.076 | 3.0954 | -11.48 | 0.66 | 0.68315 | -0.69106 | -8.1019 | 0.56904 | 0.43595 | -16.6992 | 4.4604 | 0.42034 | 0.42423 | 0.42677 | 0.40122 | 0.49033 | 0.4404 | 0.42641
42838.42 | -21 | 22.8999 | 22.868 | 22.858 | 22.7792 | 22.4046 | 21.7354 | 22.7224 | 21.795 | 22.366 | 22.3741 | 22.3586 | 22.0172 | 21.2271 | 22.2005 | 21.5906 | 21.7664 | 21.8938 | 21.0826 | 21.1843 | 21.3951 | 20.476 | 20.6096 | 20.9035 | 21.8797 | 21.6379 | 21.261 | 21.0438 | 21.0184 | 21.487 | 22.0764 | 21.6805 | 21.1974 | 21.9987 | 21.741 | 21.3481 | 19.9407 | 21.7552 |  | 20.6097 | 20.4581 | 20.4619 | 19.1315 |  | 16.8632 | 16.7979 | 16.4873 | 16.6229 | 16.5919 | 17.0461 | 17.9151 | 15.6367 | 17.0109 | 16.0021 | 16.9732 | 18.0036 | 44.5843 | 47.9515 | 43.7986 | 21.4095 |  |  | 0.4175 | -0.40945 | -46.66 | 0.39423 | 0.18281 | -197.8434 | 14.0192 | -0.25138 | -0.10402 | -0.022128 | 0.061919 | 8.8287 | 9.0584 | 1.9788 | 21.7775 | 21.9953 | 22.1843 | 22.2469 | 22.0752 | 21.3825 | 20.1895 | 22.1893 | 22.3649 | 22.4019 | 22.3485 | 21.9674 | 21.2009 | 22.2606 | 17.1218 | 17.1416 | 16.0607 | 16.1417 | 16.2013 | 17.1043 | 16.8569 | 22.3746 | 22.1355 | 21.6977 | 22.0766 | 21.7995 | 21.3012 | 21.943 | 21.5202 | 20.9028 | 20.1043 | 21.1042 | 19.9099 | 19.8514 | 0.12544 | -0.079282 | 20.7613 | 22.0533 | 22.3647 | 20.0811 | 21.6491 | 22.0914 | 21.9339 | 21.6956 | 21.265 | 21.7638 | 21.4312 | 21.0367 | 20.7747 | 21.437 | 20.5353 | 20.5863 | 20.2229 |  | 20.2244 | 19.9666 | 20.1205 | 19.8281 | 20.1065 | 20.3784 |  | 20.4356 |  |  | 20.2246 | 20.2948 | 20.6426 | [5 empty] | 21.9075 | 20.3404 | 21.6455 | 22.0195 | 19.6054 | 21.147 | 21.7651 | 19.4502 | 20.1016 | 22.9537 |  | 19.8619 | 21.5228 | 18.9469 | 19.8035 | 21.7158 | 19.5103 | 20.1254 | 19.1026 | 20.2781 | 19.1919 | 20.2998 | 18.8683 | 20.1994 | 21.5752 | 19.606 | 19.8292 | 21.8542 | 18.9774 | 19.8667 | 21.4342 | 19.0612 | 20.2683 | 19.4031 | 20.2395 | 18.9943 | 20.3021 | -0.24518 | 20.9475 | 0.049169 | 0.013743 | -27.0418 | 3.0954 | -11.53 | 0.81 | 0.77293 | -0.75932 | -8.1059 | 0.74507 | 0.50759 | -16.6983 | 4.445 | 0.42006 | 0.4237 | 0.42708 | 0.40049 | 0.48953 | 0.44088 | 0.42636
42838.42 | -20 | 22.901 | 22.8703 | 22.8566 | 22.7741 | 22.4017 | 21.7375 | 22.7192 | 21.7923 | 22.3653 | 22.3784 | 22.3542 | 22.016 | 21.229 | 22.202 | 21.6039 | 21.7775 | 21.9023 | 21.0907 | 21.1902 | 21.4029 | 20.4845 | 20.6165 | 20.9071 | 21.8787 | 21.6512 | 21.2715 | 21.0546 | 21.0287 | 21.5198 | 22.0778 | 21.6718 | 21.1961 | 22.0028 | 21.7391 | 21.3458 | 19.9389 | 21.7351 |  | 20.6124 | 20.4565 | 20.4741 | 19.1099 |  | 16.8636 | 16.8037 | 16.4927 | 16.6218 | 16.5853 | 17.0772 | 17.9401 | 15.6691 | 17.009 | 16.0069 | 16.9807 | 18.0067 | 44.5695 | 47.9797 | 43.7955 | 21.4146 |  |  | 0.44313 | -0.37725 | -46.5371 | 0.53485 | 0.31752 | -197.7947 | 14.1289 | -0.3552 | -0.24569 | 0.1604 | 0.020255 | 8.8287 | 9.0585 | 1.9785 | 21.7749 | 21.9951 | 22.1828 | 22.251 | 22.0732 | 21.3814 | 20.1886 | 22.1918 | 22.3632 | 22.402 | 22.3465 | 21.9691 | 21.1959 | 22.2572 | 17.121 | 17.1512 | 16.0655 | 16.1443 | 16.1903 | 17.1024 | 16.8523 | 22.3735 | 22.1337 | 21.6844 | 22.071 | 21.7857 | 21.2975 | 21.9441 | 21.5204 | 20.8921 | 20.0991 | 21.1045 | 19.8991 | 19.8572 | 0.11247 | -0.0035828 | 20.7749 | 22.0598 | 22.364 | 20.0788 | 21.6553 | 22.0996 | 21.9417 | 21.7099 | 21.2708 | 21.7657 | 21.4349 | 21.0405 | 20.7929 | 21.4374 | 20.5511 | 20.6012 | 20.2187 |  | 20.233 | 19.9713 | 20.1195 | 19.8099 | 20.1047 | 20.3792 |  | 20.4372 |  |  | 20.227 | 20.3027 | 20.6444 | [5 empty] | 21.9019 | 20.3334 | 21.6407 | 22.0207 | 19.6056 | 21.1481 | 21.7665 | 19.4586 | 20.1139 | 22.9617 |  | 19.8731 | 21.538 | 18.9509 | 19.8113 | 21.7191 | 19.5163 | 20.1299 | 19.1106 | 20.2848 | 19.1947 | 20.3025 | 18.8795 | 20.2099 | 21.5895 | 19.6118 | 19.8362 | 21.8741 | 18.9836 | 19.8778 | 21.4509 | 19.0662 | 20.2802 | 19.4121 | 20.2367 | 18.9964 | 20.3156 | -0.21401 | 20.9463 | 0.0499 | 0.01513 | -26.9837 | 3.0954 | -7.14 | 0.51 | 0.79634 | -0.72886 | -8.0953 | 0.86786 | 0.66899 | -16.6972 | 4.4626 | 0.42047 | 0.42354 | 0.42752 | 0.40036 | 0.48847 | 0.44142 | 0.42602
42838.4201 | -19 | 22.8994 | 22.8722 | 22.856 | 22.7766 | 22.4047 | 21.7335 | 22.7191 | 21.794 | 22.3648 | 22.3689 | 22.3529 | 22.0086 | 21.2215 | 22.2046 | 21.5974 | 21.7724 | 21.8992 | 21.0828 | 21.1815 | 21.3974 | 20.4768 | 20.6126 | 20.8995 | 21.8783 | 21.6354 | 21.2632 | 21.0589 | 21.0317 | 21.5211 | 22.0798 | 21.6701 | 21.1898 | 21.9901 | 21.7286 | 21.3499 | 19.9405 | 21.7067 |  | 20.6161 | 20.4647 | 20.4745 | 19.0992 |  | 16.8636 | 16.8068 | 16.4847 | 16.6284 | 16.5935 | 17.1132 | 17.9453 | 15.6776 | 17.0157 | 16.0409 | 16.9839 | 18.0084 | 44.5668 | 48.0138 | 43.7964 | 21.4253 |  |  | 0.36033 | -0.36937 | -45.8103 | 0.34231 | 0.23669 | -197.8243 | 14.4082 | -0.26452 | -0.069379 | 0.02214 | -0.090154 | 8.8292 | 9.059 | 1.9788 | 21.7797 | 21.9988 | 22.185 | 22.2505 | 22.0738 | 21.3859 | 20.1955 | 22.197 | 22.3652 | 22.4012 | 22.3472 | 21.9763 | 21.2046 | 22.2623 | 17.1215 | 17.1713 | 16.0795 | 16.1479 | 16.191 | 17.1056 | 16.8509 | 22.3767 | 22.1288 | 21.6924 | 22.0701 | 21.7892 | 21.2927 | 21.9413 | 21.5195 | 20.896 | 20.1023 | 21.1095 | 19.8987 | 19.8575 | 0.007483 | 0.021524 | 20.7721 | 22.0674 | 22.3613 | 20.0802 | 21.6535 | 22.0972 | 21.9372 | 21.7066 | 21.2669 | 21.7645 | 21.4326 | 21.0336 | 20.8038 | 21.4244 | 20.557 | 20.6076 | 20.2169 |  | 20.22 | 19.9768 | 20.1197 | 19.8049 | 20.1024 | 20.3781 |  | 20.4369 |  |  | 20.2262 | 20.3076 | 20.648 | [5 empty] | 21.9063 | 20.3418 | 21.6517 | 22.03 | 19.617 | 21.1473 | 21.7713 | 19.4652 | 20.1209 | 22.9562 |  | 19.886 | 21.5503 | 18.9466 | 19.81 | 21.723 | 19.5168 | 20.1227 | 19.1068 | 20.283 | 19.1882 | 20.3017 | 18.8793 | 20.2117 | 21.5974 | 19.6121 | 19.8387 | 21.8837 | 18.9818 | 19.8729 | 21.4625 | 19.0594 | 20.2849 | 19.412 | 20.2367 | 18.9957 | 20.3157 | -0.18656 | 20.9466 | 0.049691 | 0.015914 | -27.0419 | 3.0954 | -5.74 | 0.96 | 0.7181 | -0.72121 | -8.0318 | 0.6943 | 0.57764 | -16.6995 | 4.5068 | 0.42008 | 0.42339 | 0.42759 | 0.40068 | 0.48675 | 0.44177 | 0.42612
42838.4201 | -18 | 22.8984 | 22.8752 | 22.8544 | 22.7797 | 22.4034 | 21.7325 | 22.719 | 21.7917 | 22.367 | 22.369 | 22.3507 | 22.0087 | 21.2315 | 22.1965 | 21.5861 | 21.7641 | 21.8936 | 21.0798 | 21.1767 | 21.3948 | 20.474 | 20.6033 | 20.8997 | 21.8748 | 21.6286 | 21.2553 | 21.0712 | 21.0335 | 21.5301 | 22.0822 | 21.68 | 21.1948 | 21.9966 | 21.7387 | 21.3524 | 19.9404 | 21.6963 |  | 20.6183 | 20.4689 | 20.4926 | 19.1035 |  | 16.8621 | 16.7966 | 16.4751 | 16.6211 | 16.5927 | 17.1512 | 17.9638 | 15.692 | 17.0059 | 16.1056 | 16.9771 | 18.0072 | 44.5543 | 48.0436 | 43.7912 | 21.4269 |  |  | 0.4359 | -0.35951 | -45.1795 | 0.42971 | 0.31358 | -197.821 | 14.6323 | -0.16924 | -0.0098312 | 0.10228 | -0.040331 | 8.8293 | 9.0591 | 1.9786 | 21.7794 | 22.0003 | 22.1864 | 22.2565 | 22.076 | 21.3866 | 20.1997 | 22.1879 | 22.3681 | 22.4014 | 22.3473 | 21.9696 | 21.2033 | 22.263 | 17.1289 | 17.22 | 16.0731 | 16.1587 | 16.194 | 17.1021 | 16.8497 | 22.3801 | 22.1306 | 21.692 | 22.0735 | 21.7882 | 21.2884 | 21.9409 | 21.5199 | 20.8998 | 20.1065 | 21.1123 | 19.8922 | 19.86 | -0.11618 | 0.010302 | 20.7778 | 22.0587 | 22.3587 | 20.077 | 21.649 | 22.0978 | 21.9274 | 21.6997 | 21.2672 | 21.7629 | 21.43 | 21.0274 | 20.8171 | 21.433 | 20.5649 | 20.6163 | 20.225 |  | 20.2273 | 19.9776 | 20.1218 | 19.8019 | 20.1098 | 20.3823 |  | 20.4376 |  |  | 20.2289 | 20.3065 | 20.6469 | [5 empty] | 21.9133 | 20.3446 | 21.6527 | 22.0334 | 19.6222 | 21.1538 | 21.7718 | 19.4641 | 20.1234 | 22.9485 |  | 19.8892 | 21.5629 | 18.9395 | 19.8137 | 21.7255 | 19.5182 | 20.1227 | 19.1128 | 20.2807 | 19.1936 | 20.3031 | 18.8789 | 20.2154 | 21.6145 | 19.6263 | 19.8517 | 21.8979 | 18.9849 | 19.8744 | 21.4766 | 19.0676 | 20.2959 | 19.4184 | 20.2461 | 19.0026 | 20.3277 | -0.053742 | 20.946 | 0.049833 | 0.016153 | -27.093 | 3.0954 | -4.02 | 0.86 | 0.78983 | -0.71151 | -7.9762 | 0.77788 | 0.66491 | -16.7004 | 4.542 | 0.4201 | 0.42344 | 0.42792 | 0.39944 | 0.48731 | 0.44165 | 0.42619
42838.4201 | -17 | 22.8961 | 22.8689 | 22.852 | 22.7783 | 22.401 | 21.7424 | 22.7265 | 21.7881 | 22.3654 | 22.3692 | 22.3449 | 22.01 | 21.2314 | 22.2028 | 21.5767 | 21.7613 | 21.8897 | 21.0807 | 21.1786 | 21.3964 | 20.474 | 20.612 | 20.8956 | 21.875 | 21.6279 | 21.2631 | 21.0637 | 21.0394 | 21.5616 | 22.0836 | 21.6783 | 21.1973 | 22.006 | 21.7405 | 21.3573 | 19.9459 | 21.6913 |  | 20.6214 | 20.4775 | 20.5056 | 19.1071 |  | 16.8546 | 16.8005 | 16.4801 | 16.6226 | 16.604 | 17.1813 | 17.9702 | 15.7302 | 17.0056 | 16.1116 | 16.9826 | 18.0109 | 44.5562 | 48.0575 | 43.7866 | 21.4265 |  |  | 0.44181 | -0.38316 | -44.981 | 0.37385 | 0.34118 | -197.8217 | 14.1736 | -0.28949 | -0.22584 | 0.071233 | -0.03929 | 8.828 | 9.058 | 1.9783 | 21.7726 | 21.9943 | 22.181 | 22.2467 | 22.0673 | 21.3804 | 20.1961 | 22.1871 | 22.3665 | 22.3982 | 22.3422 | 21.9672 | 21.1962 | 22.2658 | 17.1411 | 17.239 | 16.0845 | 16.1649 | 16.2032 | 17.103 | 16.8562 | 22.3686 | 22.1259 | 21.6935 | 22.0749 | 21.7832 | 21.2938 | 21.9343 | 21.5183 | 20.8925 | 20.1025 | 21.1129 | 19.8846 | 19.8541 | -0.11755 | -0.12702 | 20.7762 | 22.0601 | 22.363 | 20.0886 | 21.6536 | 22.104 | 21.9363 | 21.7098 | 21.2699 | 21.7722 | 21.4393 | 21.0337 | 20.8339 | 21.4469 | 20.5757 | 20.6394 | 20.2299 |  | 20.2315 | 19.9901 | 20.1181 | 19.8065 | 20.1069 | 20.3825 |  | 20.4379 |  |  | 20.2165 | 20.3049 | 20.6467 | [5 empty] | 21.9075 | 20.3481 | 21.6506 | 22.0288 | 19.6283 | 21.1541 | 21.7736 | 19.475 | 20.1247 | 22.9483 |  | 19.9 | 21.573 | 18.944 | 19.8238 | 21.7391 | 19.5256 | 20.1219 | 19.1195 | 20.2884 | 19.2044 | 20.313 | 18.8825 | 20.2187 | 21.6215 | 19.6327 | 19.8584 | 21.9103 | 18.9882 | 19.8755 | 21.4784 | 19.0693 | 20.2981 | 19.421 | 20.2457 | 19.0097 | 20.3398 | -0.24592 | 20.9461 | 0.049304 | 0.015761 | -27.1036 | 3.0954 | -6.54 | 0.59 | 0.79522 | -0.73455 | -7.9587 | 0.72557 | 0.69359 | -16.7013 | 4.4705 | 0.4201 | 0.42297 | 0.42769 | 0.39819 | 0.48681 | 0.44173 | 0.42622
42838.4201 | -16 | 22.8982 | 22.874 | 22.8557 | 22.7759 | 22.4076 | 21.7385 | 22.7183 | 21.7935 | 22.3678 | 22.3759 | 22.349 | 22.0149 | 21.2275 | 22.2018 | 21.5869 | 21.7634 | 21.8919 | 21.0843 | 21.1748 | 21.3879 | 20.4654 | 20.6098 | 20.8963 | 21.8688 | 21.6368 | 21.2583 | 21.0793 | 21.0499 | 21.5928 | 22.0763 | 21.6751 | 21.1934 | 21.9902 | 21.7406 | 21.3546 | 19.9512 | 21.674 |  | 20.6224 | 20.4799 | 20.508 | 19.0997 |  | 16.8542 | 16.7999 | 16.4829 | 16.6331 | 16.6224 | 17.2102 | 17.9764 | 15.7736 | 17.0107 | 16.1234 | 16.9838 | 18.0101 | 44.5545 | 48.0732 | 43.7872 | 21.4219 |  |  | 0.30645 | -0.33059 | -44.9271 | 0.34691 | 0.37797 | -197.8263 | 14.5284 | -0.15872 | 0.049911 | 0.10375 | 0.018519 | 8.8276 | 9.0575 | 1.9786 | 21.7698 | 21.9903 | 22.1859 | 22.239 | 22.0679 | 21.3807 | 20.1915 | 22.1916 | 22.3604 | 22.3982 | 22.3515 | 21.9712 | 21.2005 | 22.2592 | 17.1463 | 17.2119 | 16.0754 | 16.1678 | 16.1961 | 17.1037 | 16.8468 | 22.3735 | 22.1341 | 21.7004 | 22.0768 | 21.783 | 21.2948 | 21.9307 | 21.5183 | 20.8924 | 20.1015 | 21.1221 | 19.8901 | 19.8539 | -0.024759 | -0.16392 | 20.7742 | 22.0569 | 22.359 | 20.0846 | 21.6566 | 22.1032 | 21.94 | 21.7073 | 21.2708 | 21.7772 | 21.4362 | 21.0344 | 20.8431 | 21.4545 | 20.5884 | 20.6424 | 20.2481 |  | 20.2305 | 19.9902 | 20.1265 | 19.8029 | 20.1091 | 20.389 |  | 20.4384 |  |  | 20.2013 | 20.3098 | 20.6399 | [5 empty] | 21.9046 | 20.3466 | 21.6534 | 22.0289 | 19.6221 | 21.1485 | 21.77 | 19.4853 | 20.1371 | 22.9478 |  | 19.9057 | 21.5911 | 18.9451 | 19.8363 | 21.7484 | 19.5405 | 20.1347 | 19.1326 | 20.3008 | 19.2077 | 20.3195 | 18.8878 | 20.2259 | 21.6366 | 19.6449 | 19.8657 | 21.9327 | 19.0078 | 19.901 | 21.5006 | 19.0799 | 20.3149 | 19.4357 | 20.2499 | 19.0152 | 20.3459 | -0.093439 | 20.9453 | 0.048266 | 0.012778 | -27.0927 | 3.0954 | 0.51 | -0.1 | 0.66232 | -0.6823 | -7.954 | 0.69894 | 0.73007 | -16.7023 | 4.5263 | 0.41957 | 0.42325 | 0.42787 | 0.3977 | 0.48673 | 0.44211 | 0.4262
42838.4201 | -15 | 22.9049 | 22.872 | 22.8637 | 22.7832 | 22.4045 | 21.7417 | 22.7179 | 21.7903 | 22.369 | 22.3762 | 22.348 | 22.019 | 21.2272 | 22.1953 | 21.5942 | 21.7724 | 21.9023 | 21.0893 | 21.1826 | 21.4039 | 20.4775 | 20.6149 | 20.9094 | 21.8812 | 21.6448 | 21.2706 | 21.0987 | 21.0657 | 21.6343 | 22.077 | 21.677 | 21.1846 | 21.9903 | 21.7381 | 21.3479 | 19.9413 | 21.6466 |  | 20.6198 | 20.4861 | 20.5147 | 19.095 |  | 16.867 | 16.7921 | 16.4835 | 16.6386 | 16.6404 | 17.2466 | 17.9991 | 15.7934 | 17.012 | 16.2749 | 16.9847 | 18.006 | 44.5527 | 48.0943 | 43.799 | 21.4277 |  |  | 0.3531 | -0.13412 | -44.9147 | 0.77601 | 0.284 | -197.8526 | 14.698 | -0.23955 | -0.11044 | 0.02214 | -0.03061 | 8.828 | 9.0578 | 1.9787 | 21.7716 | 21.995 | 22.1846 | 22.2444 | 22.0672 | 21.3792 | 20.1883 | 22.1916 | 22.3567 | 22.396 | 22.3431 | 21.9759 | 21.1911 | 22.2635 | 17.1661 | 17.2074 | 16.0865 | 16.1842 | 16.2005 | 17.1039 | 16.8445 | 22.3898 | 22.1384 | 21.6959 | 22.0785 | 21.7935 | 21.2948 | 21.9401 | 21.5173 | 20.8983 | 20.1057 | 21.1208 | 19.8896 | 19.8602 | 0.015347 | -0.19397 | 20.775 | 22.057 | 22.3565 | 20.0794 | 21.6505 | 22.0973 | 21.9375 | 21.703 | 21.2673 | 21.7743 | 21.4326 | 21.0308 | 20.8416 | 21.4529 | 20.5981 | 20.6431 | 20.254 |  | 20.2325 | 19.9947 | 20.1305 | 19.8038 | 20.1143 | 20.3859 |  | 20.4373 |  |  | 20.2036 | 20.2964 | 20.6431 | [5 empty] | 21.909 | 20.3447 | 21.6519 | 22.0282 | 19.634 | 21.1534 | 21.7737 | 19.4822 | 20.1288 | 22.9441 |  | 19.9092 | 21.5935 | 18.9419 | 19.8363 | 21.7421 | 19.5299 | 20.16 | 19.1279 | 20.2987 | 19.1988 | 20.312 | 18.8786 | 20.2293 | 21.6296 | 19.6351 | 19.8605 | 21.9272 | 18.9953 | 19.8888 | 21.4958 | 19.0738 | 20.3101 | 19.4213 | 20.2462 | 19.0073 | 20.3501 | -0.18285 | 20.9464 | 0.048124 | 0.012444 | -27.1521 | 3.0954 | -16.1 | -0.09 | 0.711 | -0.43457 | -7.9527 | 1.0453 | 0.63289 | -16.7045 | 4.5529 | 0.41947 | 0.42326 | 0.42802 | 0.39552 | 0.48522 | 0.44191 | 0.42616
42838.4201 | -14 | 22.9089 | 22.8779 | 22.8719 | 22.7793 | 22.409 | 21.7409 | 22.7243 | 21.7931 | 22.3738 | 22.3756 | 22.3571 | 22.0215 | 21.2316 | 22.2034 | 21.594 | 21.769 | 21.8948 | 21.0806 | 21.1802 | 21.3984 | 20.4814 | 20.6169 | 20.8987 | 21.8794 | 21.6378 | 21.2617 | 21.1055 | 21.0822 | 21.67 | 22.0885 | 21.68 | 21.1865 | 21.9961 | 21.7381 | 21.3526 | 19.9449 | 21.6344 |  | 20.6222 | 20.4911 | 20.534 | 19.1034 |  | 16.8598 | 16.7934 | 16.4872 | 16.6295 | 16.6351 | 17.2509 | 18.0151 | 15.8249 | 17.0102 | 16.3457 | 16.9843 | 18.0051 | 44.554 | 48.1104 | 43.7988 | 21.4225 |  |  | 0.22496 | -0.41865 | -45.1578 | 0.47637 | 0.38783 | -197.8999 | 14.0967 | -0.21261 | -0.022675 | 0.016476 | 0.026505 | 8.8282 | 9.0585 | 1.9786 | 21.774 | 21.9979 | 22.1849 | 22.244 | 22.0669 | 21.3816 | 20.1906 | 22.1836 | 22.3637 | 22.394 | 22.352 | 21.9738 | 21.1943 | 22.2687 | 17.1784 | 17.2017 | 16.0614 | 16.181 | 16.2032 | 17.093 | 16.8472 | 22.381 | 22.1359 | 21.6942 | 22.0818 | 21.7886 | 21.2943 | 21.9425 | 21.5141 | 20.8982 | 20.1015 | 21.1251 | 19.8876 | 19.8529 | 0.11129 | -0.16202 | 20.7684 | 22.0509 | 22.3503 | 20.0748 | 21.6455 | 22.0879 | 21.9304 | 21.7015 | 21.2681 | 21.7732 | 21.432 | 21.0268 | 20.8446 | 21.4578 | 20.6035 | 20.6473 | 20.2566 |  | 20.2294 | 19.9905 | 20.1258 | 19.8061 | 20.1061 | 20.3826 |  | 20.4343 |  |  | 20.1931 | 20.2949 | 20.6413 | [5 empty] | 21.9124 | 20.3451 | 21.6426 | 22.0215 | 19.6254 | 21.1439 | 21.7637 | 19.4815 | 20.1371 | 22.9565 |  | 19.923 | 21.5995 | 18.9421 | 19.8466 | 21.7481 | 19.5385 | 20.1953 | 19.1338 | 20.3023 | 19.2006 | 20.3227 | 18.8715 | 20.2235 | 21.6319 | 19.6396 | 19.8603 | 21.9451 | 18.9919 | 19.8874 | 21.5074 | 19.0688 | 20.3129 | 19.4222 | 20.248 | 19.0154 | 20.3563 | -0.15169 | 20.9458 | 0.049396 | 0.013148 | -27.0568 | 3.0954 | -13.68 | -0.13 | 0.56754 | -0.7678 | -7.9743 | 0.81902 | 0.73958 | -16.7066 | 4.4589 | 0.4193 | 0.42322 | 0.42768 | 0.39289 | 0.48833 | 0.4418 | 0.42622
42838.4201 | -13 | 22.9093 | 22.8736 | 22.8539 | 22.79 | 22.407 | 21.7446 | 22.7287 | 21.8062 | 22.3734 | 22.3773 | 22.3591 | 22.0173 | 21.2398 | 22.2041 | 21.5941 | 21.7686 | 21.8997 | 21.0854 | 21.1863 | 21.3948 | 20.4764 | 20.618 | 20.9081 | 21.8798 | 21.6365 | 21.2618 | 21.1086 | 21.0964 | 21.7088 | 22.0885 | 21.682 | 21.1921 | 21.9946 | 21.7399 | 21.3583 | 19.9398 | 21.6562 |  | 20.6275 | 20.4946 | 20.5477 | 19.0938 |  | 16.8578 | 16.7975 | 16.4894 | 16.6302 | 16.6386 | 17.248 | 18.0325 | 15.8616 | 17.0086 | 16.3558 | 16.9881 | 18.0003 | 44.5419 | 48.1216 | 43.7915 | 21.4179 |  |  | 0.44575 | -0.34899 | -45.0093 | 0.56245 | 0.54094 | -197.8598 | 14.4167 | -0.33483 | 0.12172 | 0.14445 | -0.043803 | 8.8294 | 9.0592 | 1.9783 | 21.7698 | 21.9913 | 22.1823 | 22.242 | 22.0667 | 21.3835 | 20.1921 | 22.1852 | 22.364 | 22.3978 | 22.3551 | 21.9698 | 21.1943 | 22.262 | 17.1828 | 17.1757 | 16.0525 | 16.1646 | 16.2013 | 17.0969 | 16.8523 | 22.373 | 22.1303 | 21.6905 | 22.0727 | 21.7814 | 21.2899 | 21.9322 | 21.5108 | 20.8961 | 20.0986 | 21.1258 | 19.8811 | 19.8416 | -0.033803 | -0.052464 | 20.7723 | 22.0525 | 22.3588 | 20.0785 | 21.6522 | 22.0946 | 21.9313 | 21.6995 | 21.2715 | 21.7734 | 21.4343 | 21.0298 | 20.8591 | 21.4708 | 20.6146 | 20.6578 | 20.2555 |  | 20.2319 | 19.9857 | 20.128 | 19.8026 | 20.1065 | 20.3844 |  | 20.4332 |  |  | 20.2047 | 20.3109 | 20.6436 | [5 empty] | 21.9094 | 20.3462 | 21.6513 | 22.0294 | 19.6349 | 21.1498 | 21.7625 | 19.4887 | 20.1407 | 22.9666 |  | 19.9092 | 21.6084 | 18.9405 | 19.8409 | 21.7497 | 19.54 | 20.2045 | 19.1257 | 20.3056 | 19.2053 | 20.325 | 18.8671 | 20.2347 | 21.6359 | 19.6343 | 19.867 | 21.9419 | 19.0015 | 19.8849 | 21.5121 | 19.0781 | 20.3146 | 19.4211 | 20.2568 | 19.0079 | 20.3565 | -0.062275 | 20.9458 | 0.049802 | 0.014048 | -26.9986 | 3.0954 | -12.66 | -0.14 | 0.79895 | -0.70103 | -7.9612 | 0.88995 | 0.87345 | -16.7048 | 4.5092 | 0.41941 | 0.42342 | 0.42779 | 0.39285 | 0.4899 | 0.4419 | 0.42644
42838.4201 | -12 | 22.9038 | 22.8648 | 22.8518 | 22.7761 | 22.3939 | 21.7358 | 22.7143 | 21.7869 | 22.3582 | 22.3669 | 22.3428 | 22.0059 | 21.2226 | 22.195 | 21.5944 | 21.7709 | 21.8977 | 21.0831 | 21.1834 | 21.4015 | 20.4778 | 20.6071 | 20.9061 | 21.882 | 21.6357 | 21.26 | 21.1273 | 21.1099 | 21.7367 | 22.0847 | 21.669 | 21.1872 | 21.9951 | 21.7365 | 21.3469 | 19.9477 | 21.662 |  | 20.6281 | 20.4996 | 20.5593 | 19.0859 |  | 16.8734 | 16.8094 | 16.4981 | 16.6384 | 16.6422 | 17.2487 | 18.0589 | 15.8865 | 17.0185 | 16.3653 | 16.993 | 18.0086 | 44.5388 | 48.1513 | 43.8067 | 21.4292 |  |  | 0.45955 | -0.082205 | -45.05 | 0.49411 | 0.43383 | -197.842 | 14.3188 | -0.36112 | -0.018783 | 0.063471 | -0.11463 | 8.8294 | 9.0589 | 1.9788 | 21.7718 | 21.9901 | 22.1887 | 22.2416 | 22.0665 | 21.3797 | 20.1914 | 22.1901 | 22.3658 | 22.401 | 22.356 | 21.9697 | 21.199 | 22.2628 | 17.1813 | 17.1537 | 16.0434 | 16.1476 | 16.1966 | 17.0929 | 16.8518 | 22.3739 | 22.1322 | 21.6884 | 22.0738 | 21.7862 | 21.2964 | 21.9347 | 21.5179 | 20.8926 | 20.0976 | 21.134 | 19.8753 | 19.833 | 0.10795 | -0.10192 | 20.7708 | 22.0601 | 22.3625 | 20.0844 | 21.6578 | 22.0993 | 21.9378 | 21.6993 | 21.2678 | 21.7765 | 21.436 | 21.0296 | 20.8748 | 21.4683 | 20.6243 | 20.676 | 20.2816 |  | 20.2346 | 19.9839 | 20.1303 | 19.8079 | 20.1064 | 20.3855 |  | 20.4424 |  |  | 20.2074 | 20.3089 | 20.6369 | [5 empty] | 21.9046 | 20.3511 | 21.6403 | 22.0238 | 19.6202 | 21.1438 | 21.7645 | 19.4923 | 20.1409 | 22.9805 |  | 19.9249 | 21.6234 | 18.9392 | 19.8409 | 21.7556 | 19.5387 | 20.2022 | 19.1378 | 20.3113 | 19.1974 | 20.3306 | 18.8849 | 20.2415 | 21.6485 | 19.641 | 19.8711 | 21.9661 | 19.0007 | 19.9049 | 21.5264 | 19.0858 | 20.3347 | 19.435 | 20.2699 | 19.012 | 20.371 | -0.20307 | 20.946 | 0.050373 | 0.014469 | -27.0539 | 3.0954 | -2.75 | -0.14 | 0.81127 | -0.34024 | -7.965 | 0.83415 | 0.78221 | -16.7041 | 4.4938 | 0.41877 | 0.42355 | 0.42764 | 0.39256 | 0.49087 | 0.44238 | 0.42664
42838.4202 | -11 | 22.9005 | 22.8626 | 22.8513 | 22.7738 | 22.4 | 21.7305 | 22.7082 | 21.7906 | 22.361 | 22.3726 | 22.3509 | 22.0125 | 21.2261 | 22.1923 | 21.5987 | 21.7661 | 21.8991 | 21.0908 | 21.1796 | 21.4035 | 20.4832 | 20.6144 | 20.9052 | 21.8834 | 21.6339 | 21.268 | 21.1291 | 21.1151 | 21.7532 | 22.085 | 21.6854 | 21.2026 | 22.0079 | 21.7445 | 21.3533 | 19.9492 | 21.6773 |  | 20.6362 | 20.519 | 20.5801 | 19.089 |  | 16.8616 | 16.8074 | 16.4858 | 16.6342 | 16.6276 | 17.2357 | 18.0413 | 15.8794 | 17.0065 | 16.3316 | 16.9914 | 18.0082 | 44.5297 | 48.1599 | 43.82 | 21.4335 |  |  | 0.48847 | -0.12294 | -44.8391 | 0.3824 | 0.19332 | -197.8644 | 14.2906 | -0.34338 | -0.28286 | -0.000728 | 0.039698 | 8.8292 | 9.0589 | 1.9787 | 21.7772 | 21.9921 | 22.1877 | 22.2471 | 22.0661 | 21.3817 | 20.1967 | 22.1954 | 22.3649 | 22.3993 | 22.3505 | 21.9744 | 21.2037 | 22.2578 | 17.1782 | 17.1482 | 16.0513 | 16.1421 | 16.1787 | 17.0907 | 16.8467 | 22.3786 | 22.1299 | 21.6858 | 22.0736 | 21.7896 | 21.2896 | 21.9428 | 21.5162 | 20.8958 | 20.1048 | 21.1514 | 19.8785 | 19.8277 | 0.089269 | -0.14775 | 20.7749 | 22.0642 | 22.3656 | 20.0906 | 21.6552 | 22.0974 | 21.9404 | 21.701 | 21.2676 | 21.7729 | 21.4367 | 21.0319 | 20.8833 | 21.4642 | 20.6268 | 20.6748 | 20.2898 |  | 20.2354 | 19.9767 | 20.1278 | 19.8037 | 20.1054 | 20.3844 |  | 20.4451 |  |  | 20.2064 | 20.3213 | 20.6379 | [5 empty] | 21.91 | 20.3564 | 21.6501 | 22.0244 | 19.6289 | 21.1517 | 21.7746 | 19.4946 | 20.1389 | 23.011 |  | 19.928 | 21.6228 | 18.9429 | 19.8435 | 21.76 | 19.5387 | 20.2018 | 19.1381 | 20.3164 | 19.2031 | 20.3367 | 18.8911 | 20.2477 | 21.6618 | 19.6407 | 19.8816 | 21.9876 | 19.0092 | 19.9129 | 21.537 | 19.0802 | 20.3404 | 19.4283 | 20.2771 | 19.0135 | 20.3661 | -0.035934 | 20.9456 | 0.050048 | 0.015086 | -27.089 | 3.0954 | -5.03 | -0.19 | 0.83642 | -0.41609 | -7.9463 | 0.73382 | 0.52215 | -16.7047 | 4.4893 | 0.41857 | 0.42367 | 0.42772 | 0.39263 | 0.48939 | 0.44234 | 0.42704
42838.4202 | -10 | 22.904 | 22.8719 | 22.8561 | 22.7803 | 22.4017 | 21.7327 | 22.7155 | 21.7962 | 22.3691 | 22.3784 | 22.3455 | 22.0125 | 21.2316 | 22.1983 | 21.6018 | 21.765 | 21.8948 | 21.0814 | 21.1787 | 21.3981 | 20.4697 | 20.6104 | 20.8989 | 21.8774 | 21.6347 | 21.2642 | 21.1368 | 21.1226 | 21.757 | 22.0768 | 21.6749 | 21.1948 | 21.9986 | 21.7314 | 21.3517 | 19.9405 | 21.6737 |  | 20.6259 | 20.5122 | 20.5857 | 19.0815 |  | 16.8595 | 16.8027 | 16.4852 | 16.6322 | 16.6261 | 17.2207 | 18.0425 | 15.8874 | 17.0006 | 16.2842 | 16.9906 | 17.9972 | 44.5225 | 48.1824 | 43.8283 | 21.4321 |  |  | 0.45627 | -0.2202 | -44.659 | 0.34166 | 0.18741 | -197.8066 | 14.2787 | -0.323 | -0.12192 | -0.046255 | -0.020367 | 8.829 | 9.0587 | 1.9788 | 21.7726 | 21.9861 | 22.1778 | 22.2464 | 22.0655 | 21.384 | 20.1892 | 22.1873 | 22.3587 | 22.3929 | 22.3425 | 21.9581 | 21.1943 | 22.2594 | 17.1688 | 17.1687 | 16.1144 | 16.1565 | 16.1845 | 17.0923 | 16.8382 | 22.3814 | 22.1331 | 21.69 | 22.0758 | 21.7907 | 21.295 | 21.9375 | 21.5239 | 20.8964 | 20.101 | 21.1715 | 19.8794 | 19.8346 | -0.090817 | -0.091836 | 20.772 | 22.0587 | 22.356 | 20.0915 | 21.6508 | 22.1005 | 21.9337 | 21.7034 | 21.2696 | 21.7731 | 21.4382 | 21.0353 | 20.8919 | 21.4656 | 20.6338 | 20.6791 | 20.3013 |  | 20.236 | 19.9857 | 20.1373 | 19.8067 | 20.1095 | 20.3814 |  | 20.4494 |  |  | 20.2192 | 20.3264 | 20.6413 | [5 empty] | 21.9087 | 20.3518 | 21.6506 | 22.0208 | 19.6348 | 21.1423 | 21.7711 | 19.5009 | 20.1427 | 23.0559 |  | 19.9354 | 21.6347 | 18.9492 | 19.8523 | 21.7521 | 19.5455 | 20.2054 | 19.1317 | 20.316 | 19.1995 | 20.3384 | 18.898 | 20.2519 | 21.6733 | 19.6539 | 19.893 | 22.0076 | 19.0056 | 19.9135 | 21.5478 | 19.0926 | 20.3462 | 19.4348 | 20.2874 | 19.0164 | 20.3748 | -0.12646 | 20.9456 | 0.049986 | 0.014658 | -27.0756 | 3.0955 | -13.08 | 1.81 | 0.80839 | -0.55685 | -7.9302 | 0.69363 | 0.51409 | -16.7018 | 4.4873 | 0.41827 | 0.42373 | 0.42777 | 0.39387 | 0.48139 | 0.44226 | 0.42672
42838.4202 | -9 | 22.9068 | 22.8739 | 22.8558 | 22.7797 | 22.4002 | 21.7355 | 22.7212 | 21.7943 | 22.3676 | 22.3771 | 22.3542 | 22.0164 | 21.2312 | 22.1942 | 21.5994 | 21.7695 | 21.8974 | 21.0807 | 21.1821 | 21.3983 | 20.4676 | 20.6112 | 20.8967 | 21.8778 | 21.6319 | 21.2613 | 21.1486 | 21.1338 | 21.7583 | 22.0825 | 21.6738 | 21.1905 | 22.001 | 21.7328 | 21.3513 | 19.9346 | 21.6671 |  | 20.6273 | 20.5187 | 20.6008 | 19.0742 |  | 16.8501 | 16.8002 | 16.4803 | 16.6256 | 16.6248 | 17.208 | 18.0326 | 15.9071 | 17.0047 | 16.2535 | 16.983 | 18.0079 | 44.5394 | 48.2032 | 43.8497 | 21.4348 |  |  | 0.30645 | -0.43902 | -44.6722 | 0.79375 | 0.15981 | -197.865 | 14.5383 | -0.30724 | -0.33423 | -0.022757 | -0.034602 | 8.8279 | 9.0579 | 1.9789 | 21.7694 | 21.9892 | 22.1894 | 22.2437 | 22.0638 | 21.3807 | 20.1903 | 22.1879 | 22.3599 | 22.3991 | 22.3508 | 21.9741 | 21.2002 | 22.2574 | 17.16 | 17.1934 | 16.2091 | 16.1703 | 16.2034 | 17.0922 | 16.8432 | 22.3798 | 22.1298 | 21.6867 | 22.0783 | 21.7887 | 21.2964 | 21.9413 | 21.5202 | 20.8928 | 20.1039 | 21.1828 | 19.8737 | 19.8309 | 0.1048 | -0.030401 | 20.7717 | 22.0556 | 22.3523 | 20.1008 | 21.652 | 22.0992 | 21.9347 | 21.703 | 21.2722 | 21.7783 | 21.436 | 21.0377 | 20.9058 | 21.4711 | 20.637 | 20.6913 | 20.3058 |  | 20.2423 | 19.9889 | 20.1394 | 19.8116 | 20.1118 | 20.3891 |  | 20.4482 |  |  | 20.2221 | 20.313 | 20.64 | [5 empty] | 21.9001 | 20.3456 | 21.648 | 22.0182 | 19.6324 | 21.1408 | 21.7707 | 19.5132 | 20.1541 | 23.0839 |  | 19.9442 | 21.648 | 18.9534 | 19.8575 | 21.7549 | 19.5513 | 20.2101 | 19.1412 | 20.3296 | 19.2046 | 20.3435 | 18.9013 | 20.2521 | 21.6735 | 19.6517 | 19.8867 | 22.0107 | 19.0031 | 19.9135 | 21.5532 | 19.097 | 20.3507 | 19.4399 | 20.292 | 19.0141 | 20.3777 | -0.12535 | 20.9457 | 0.049101 | 0.012248 | -27.0764 | 3.0954 | -22.76 | 4.46 | 0.6625 | -0.78627 | -7.9314 | 1.0572 | 0.47472 | -16.7039 | 4.5278 | 0.41836 | 0.42372 | 0.42772 | 0.39484 | 0.47145 | 0.44227 | 0.42692
42838.4202 | -8 | 22.9065 | 22.8681 | 22.8594 | 22.7788 | 22.4006 | 21.741 | 22.7192 | 21.794 | 22.3669 | 22.374 | 22.3576 | 22.0164 | 21.2322 | 22.1972 | 21.599 | 21.7688 | 21.8961 | 21.0841 | 21.1817 | 21.398 | 20.4722 | 20.6072 | 20.8998 | 21.8818 | 21.6329 | 21.263 | 21.1564 | 21.149 | 21.7784 | 22.0879 | 21.6751 | 21.1936 | 21.9987 | 21.7361 | 21.351 | 19.9432 | 21.6639 |  | 20.6269 | 20.5302 | 20.6124 | 19.0692 |  | 16.8661 | 16.8063 | 16.487 | 16.6244 | 16.624 | 17.2181 | 18.0407 | 15.9585 | 17.011 | 16.2352 | 16.994 | 18.012 | 44.5568 | 48.2305 | 43.8492 | 21.4305 |  |  | 0.46087 | -0.031609 | -44.3587 | 0.56179 | 0.23472 | -197.8361 | 14.6296 | -0.19355 | -0.26884 | 0.18515 | -0.12852 | 8.8276 | 9.0575 | 1.9785 | 21.7746 | 21.9926 | 22.1858 | 22.2507 | 22.0686 | 21.381 | 20.1887 | 22.1965 | 22.3639 | 22.3931 | 22.3495 | 21.9689 | 21.1992 | 22.2632 | 17.1504 | 17.2436 | 16.2971 | 16.1797 | 16.215 | 17.0959 | 16.8514 | 22.3798 | 22.1298 | 21.6871 | 22.0821 | 21.7892 | 21.2885 | 21.9453 | 21.5207 | 20.8934 | 20.1013 | 21.1908 | 19.874 | 19.8287 | 0.091038 | -0.055507 | 20.7716 | 22.0515 | 22.3512 | 20.0946 | 21.6447 | 22.0915 | 21.9302 | 21.6982 | 21.2645 | 21.7691 | 21.432 | 21.0304 | 20.9091 | 21.4652 | 20.6354 | 20.6926 | 20.3135 |  | 20.2465 | 19.9926 | 20.1408 | 19.8033 | 20.1142 | 20.3895 |  | 20.4481 |  |  | 20.2367 | 20.3211 | 20.6505 | [5 empty] | 21.9101 | 20.3539 | 21.6542 | 22.0271 | 19.6431 | 21.1558 | 21.7801 | 19.5138 | 20.1485 | 23.1197 |  | 19.9388 | 21.6477 | 18.9531 | 19.8513 | 21.7461 | 19.5484 | 20.2121 | 19.1368 | 20.3293 | 19.1968 | 20.3436 | 18.9041 | 20.2567 | 21.6801 | 19.6556 | 19.8893 | 22.0206 | 19.0019 | 19.9134 | 21.5577 | 19.0948 | 20.358 | 19.4373 | 20.2916 | 19.0134 | 20.3791 | -0.30639 | 20.9464 | 0.048469 | 0.012016 | -27.1114 | 3.0954 | -23.6 | 3.06 | 0.81248 | -0.21098 | -7.9036 | 0.88945 | 0.57533 | -16.703 | 4.5421 | 0.41829 | 0.42366 | 0.42803 | 0.39633 | 0.46263 | 0.44269 | 0.42689
42838.4202 | -7 | 22.9068 | 22.8732 | 22.858 | 22.7832 | 22.4076 | 21.7359 | 22.7187 | 21.8022 | 22.369 | 22.3751 | 22.3593 | 22.0161 | 21.2338 | 22.1991 | 21.595 | 21.7686 | 21.9013 | 21.0818 | 21.1768 | 21.398 | 20.4811 | 20.6102 | 20.9072 | 21.8831 | 21.6405 | 21.2634 | 21.1645 | 21.1543 | 21.8187 | 22.0783 | 21.6767 | 21.1825 | 21.9976 | 21.7399 | 21.3431 | 19.9369 | 21.6622 |  | 20.6274 | 20.5298 | 20.6242 | 19.0747 |  | 16.8634 | 16.8007 | 16.489 | 16.6278 | 16.6481 | 17.2318 | 18.0745 | 15.9931 | 17.0072 | 16.2324 | 16.9893 | 18.0068 | 44.5738 | 48.2481 | 43.8534 | 21.4335 |  |  | 0.45495 | -0.36937 | -43.8271 | 0.34954 | 0.22552 | -197.8539 | 14.6684 | -0.2251 | -0.1155 | 0.26887 | -0.051789 | 8.8289 | 9.0588 | 1.9788 | 21.7767 | 21.9946 | 22.1829 | 22.2484 | 22.0708 | 21.3827 | 20.1869 | 22.1866 | 22.3638 | 22.3913 | 22.3446 | 21.9702 | 21.1973 | 22.2573 | 17.1263 | 17.2823 | 16.3453 | 16.2291 | 16.2004 | 17.0959 | 16.8475 | 22.3745 | 22.1401 | 21.693 | 22.0842 | 21.7913 | 21.2931 | 21.9448 | 21.5236 | 20.8972 | 20.1051 | 21.1957 | 19.8788 | 19.8202 | 0.1223 | -0.084418 | 20.7719 | 22.0544 | 22.3554 | 20.0918 | 21.6425 | 22.0933 | 21.9381 | 21.6958 | 21.2612 | 21.7648 | 21.4312 | 21.0255 | 20.9118 | 21.4727 | 20.6437 | 20.6947 | 20.3138 |  | 20.2426 | 19.9941 | 20.1346 | 19.7919 | 20.122 | 20.392 |  | 20.441 |  |  | 20.2433 | 20.3232 | 20.6564 | [5 empty] | 21.911 | 20.3552 | 21.6513 | 22.0268 | 19.6387 | 21.1543 | 21.7727 | 19.5166 | 20.1485 | 23.1479 |  | 19.9436 | 21.6568 | 18.9531 | 19.8545 | 21.7392 | 19.5493 | 20.2213 | 19.1371 | 20.3283 | 19.1976 | 20.3454 | 18.9094 | 20.263 | 21.6781 | 19.659 | 19.8906 | 22.0335 | 18.9999 | 19.9156 | 21.5652 | 19.0937 | 20.3666 | 19.4347 | 20.2953 | 19.0084 | 20.3696 | -0.26484 | 20.9459 | 0.048327 | 0.011958 | -27.1032 | 3.0954 | -21.19 | 2.02 | 0.80731 | -0.7212 | -7.856 | 0.70158 | 0.56396 | -16.7041 | 4.5482 | 0.41815 | 0.42341 | 0.42861 | 0.39902 | 0.45681 | 0.44233 | 0.42725
42838.4202 | -6 | 22.9014 | 22.8627 | 22.8569 | 22.7754 | 22.4036 | 21.729 | 22.714 | 21.7886 | 22.3632 | 22.3709 | 22.3465 | 22.0068 | 21.2256 | 22.1976 | 21.5883 | 21.7647 | 21.8984 | 21.0823 | 21.1758 | 21.3889 | 20.4775 | 20.6103 | 20.8978 | 21.8766 | 21.6353 | 21.2598 | 21.1704 | 21.1541 | 21.827 | 22.0805 | 21.6749 | 21.1849 | 21.9991 | 21.7387 | 21.3468 | 19.9375 | 21.6468 |  | 20.6295 | 20.5387 | 20.6466 | 19.0801 |  | 16.8552 | 16.7925 | 16.4852 | 16.6388 | 16.6568 | 17.2483 | 18.1019 | 15.9886 | 17.0028 | 16.2527 | 16.9851 | 18.0077 | 44.5736 | 48.2537 | 43.8566 | 21.4294 |  |  | 0.39187 | -0.53233 | -43.6983 | 0.29106 | 0.16047 | -197.8223 | 14.8057 | -0.27635 | -0.092536 | 0.079416 | -0.11984 | 8.8293 | 9.059 | 1.9786 | 21.7814 | 21.9935 | 22.1873 | 22.2522 | 22.0766 | 21.3868 | 20.1887 | 22.193 | 22.3655 | 22.394 | 22.3441 | 21.9739 | 21.1953 | 22.2662 | 17.1166 | 17.303 | 16.4007 | 16.2814 | 16.2098 | 17.0968 | 16.8499 | 22.3813 | 22.1469 | 21.6918 | 22.0777 | 21.7967 | 21.291 | 21.9423 | 21.5265 | 20.9002 | 20.1188 | 21.2175 | 19.8825 | 19.8205 | 0.028323 | -0.16525 | 20.7761 | 22.0645 | 22.3589 | 20.0942 | 21.655 | 22.1039 | 21.9431 | 21.7057 | 21.2696 | 21.7767 | 21.4391 | 21.0421 | 20.9362 | 21.4806 | 20.6559 | 20.7045 | 20.3259 |  | 20.2447 | 19.98 | 20.1374 | 19.7845 | 20.1227 | 20.4026 |  | 20.4394 |  |  | 20.2488 | 20.3178 | 20.6594 | [5 empty] | 21.9061 | 20.3566 | 21.6516 | 22.0265 | 19.6356 | 21.1492 | 21.7697 | 19.5214 | 20.1495 | 23.1551 |  | 19.9523 | 21.6625 | 18.9584 | 19.8569 | 21.735 | 19.5548 | 20.2256 | 19.141 | 20.3327 | 19.1998 | 20.3469 | 18.9221 | 20.2593 | 21.685 | 19.6649 | 19.8966 | 22.0515 | 18.9919 | 19.9146 | 21.5724 | 19.0979 | 20.3727 | 19.4378 | 20.3048 | 19.0064 | 20.3687 | -0.073405 | 20.9441 | 0.048536 | 0.012371 | -27.0403 | 3.0954 | -19.01 | 2.3 | 0.74926 | -0.86579 | -7.8443 | 0.6402 | 0.47573 | -16.7033 | 4.5696 | 0.41788 | 0.4239 | 0.42883 | 0.40019 | 0.45094 | 0.4422 | 0.4277
42838.4202 | -5 | 22.9126 | 22.8704 | 22.8642 | 22.7822 | 22.4113 | 21.739 | 22.7206 | 21.808 | 22.3718 | 22.3789 | 22.3597 | 22.0213 | 21.2393 | 22.203 | 21.5853 | 21.7588 | 21.8907 | 21.0784 | 21.1728 | 21.3857 | 20.4679 | 20.6095 | 20.8911 | 21.869 | 21.629 | 21.2537 | 21.1776 | 21.1591 | 21.8183 | 22.0774 | 21.6728 | 21.1849 | 21.9908 | 21.7244 | 21.3409 | 19.9347 | 21.6134 |  | 20.6306 | 20.5481 | 20.6416 | 19.0652 |  | 16.853 | 16.7943 | 16.4844 | 16.6417 | 16.6741 | 17.2734 | 18.125 | 15.9925 | 16.9928 | 16.3113 | 16.9824 | 18.0048 | 44.5859 | 48.2693 | 43.8686 | 21.4346 |  |  | 0.3945 | -0.29051 | -43.5544 | 0.56113 | 0.37797 | -197.821 | 14.5087 | -0.37098 | -0.16882 | 0.16921 | -0.044324 | 8.8294 | 9.0592 | 1.9786 | 21.7808 | 21.9996 | 22.1923 | 22.2515 | 22.0757 | 21.3829 | 20.192 | 22.1875 | 22.3628 | 22.3987 | 22.3451 | 21.97 | 21.1992 | 22.262 | 17.1158 | 17.3071 | 16.3917 | 16.3274 | 16.216 | 17.0969 | 16.8443 | 22.3787 | 22.1415 | 21.6931 | 22.0831 | 21.7968 | 21.2988 | 21.942 | 21.5256 | 20.8965 | 20.1076 | 21.2249 | 19.8811 | 19.8035 | -0.0060824 | -0.12132 | 20.7769 | 22.0612 | 22.3506 | 20.0904 | 21.6513 | 22.1012 | 21.9371 | 21.6947 | 21.2634 | 21.7678 | 21.4311 | 21.036 | 20.946 | 21.4728 | 20.6538 | 20.7115 | 20.3217 |  | 20.2426 | 19.9707 | 20.1415 | 19.781 | 20.1157 | 20.3999 |  | 20.4451 |  |  | 20.2531 | 20.3056 | 20.6607 | [5 empty] | 21.9006 | 20.3521 | 21.6506 | 22.0257 | 19.628 | 21.1504 | 21.7655 | 19.5242 | 20.1533 | 23.1686 |  | 19.9531 | 21.6665 | 18.9597 | 19.8578 | 21.7384 | 19.554 | 20.2278 | 19.1443 | 20.3408 | 19.2006 | 20.3505 | 18.9278 | 20.2649 | 21.6976 | 19.6644 | 19.8988 | 22.0624 | 18.9942 | 19.9135 | 21.586 | 19.0978 | 20.3837 | 19.4449 | 20.3054 | 19.0125 | 20.3799 | -0.28005 | 20.945 | 0.048837 | 0.013823 | -27.0108 | 3.0954 | -2.34 | 10.93 | 0.75176 | -0.63959 | -7.8314 | 0.88891 | 0.73015 | -16.7039 | 4.5237 | 0.41793 | 0.42429 | 0.4287 | 0.40029 | 0.45128 | 0.44252 | 0.4278
42838.4202 | -4 | 22.8957 | 22.8712 | 22.8516 | 22.7865 | 22.3987 | 21.7407 | 22.7148 | 21.7961 | 22.3719 | 22.3762 | 22.3506 | 22.0157 | 21.2343 | 22.1975 | 21.5869 | 21.7573 | 21.8945 | 21.0797 | 21.1775 | 21.39 | 20.4752 | 20.6088 | 20.8978 | 21.8705 | 21.6273 | 21.2608 | 21.1834 | 21.1719 | 21.8218 | 22.0767 | 21.6777 | 21.2001 | 21.9994 | 21.7338 | 21.3509 | 19.945 | 21.6091 |  | 20.6312 | 20.552 | 20.6624 | 19.0887 |  | 16.8663 | 16.8008 | 16.4955 | 16.6441 | 16.7031 | 17.3085 | 18.1473 | 16.0089 | 16.9996 | 16.3485 | 16.992 | 18.0123 | 44.5953 | 48.3034 | 43.8772 | 21.4411 |  |  | 0.50292 | -0.35491 | -44.0519 | 0.42511 | 0.13484 | -197.8401 | 14.4194 | -0.32826 | -0.31691 | 0.25355 | 0.048899 | 8.8294 | 9.0592 | 1.9789 | 21.7818 | 21.9968 | 22.1828 | 22.2486 | 22.0723 | 21.3752 | 20.1907 | 22.1833 | 22.3587 | 22.3931 | 22.3453 | 21.9615 | 21.1986 | 22.2569 | 17.1231 | 17.3206 | 16.3781 | 16.3441 | 16.2256 | 17.0914 | 16.8483 | 22.382 | 22.1425 | 21.6857 | 22.0785 | 21.7986 | 21.2936 | 21.9443 | 21.5174 | 20.8916 | 20.106 | 21.2335 | 19.8733 | 19.7985 | -0.024759 | -0.042954 | 20.773 | 22.05 | 22.3502 | 20.0872 | 21.6517 | 22.0958 | 21.9318 | 21.6959 | 21.2637 | 21.7638 | 21.4288 | 21.0291 | 20.9503 | 21.4805 | 20.6535 | 20.7169 | 20.333 |  | 20.2462 | 19.9701 | 20.1481 | 19.7766 | 20.1182 | 20.3991 |  | 20.4474 |  |  | 20.2459 | 20.2983 | 20.6629 | [5 empty] | 21.9023 | 20.3486 | 21.6456 | 22.0192 | 19.6282 | 21.1416 | 21.7633 | 19.5301 | 20.1646 | 23.1868 |  | 19.9608 | 21.6755 | 18.9612 | 19.8645 | 21.7452 | 19.563 | 20.233 | 19.1458 | 20.3549 | 19.2026 | 20.3608 | 18.9332 | 20.2677 | 21.7004 | 19.666 | 19.9046 | 22.0717 | 18.9954 | 19.9074 | 21.5923 | 19.0928 | 20.3858 | 19.4514 | 20.3036 | 19.0015 | 20.382 | -0.18341 | 20.9445 | 0.048573 | 0.013504 | -27.07 | 3.0953 | -7.51 | 23.56 | 0.8488 | -0.70695 | -7.8761 | 0.77371 | 0.43613 | -16.7058 | 4.5101 | 0.41774 | 0.42453 | 0.4289 | 0.39884 | 0.45326 | 0.44221 | 0.42789
42838.4202 | -3 | 22.896 | 22.862 | 22.8515 | 22.7741 | 22.4049 | 21.7361 | 22.7171 | 21.7943 | 22.3592 | 22.3731 | 22.3426 | 22.0051 | 21.2225 | 22.1951 | 21.5931 | 21.7615 | 21.9005 | 21.0811 | 21.1743 | 21.3922 | 20.4743 | 20.6082 | 20.8991 | 21.8735 | 21.6312 | 21.2698 | 21.1988 | 21.1714 | 21.8118 | 22.0789 | 21.6746 | 21.1934 | 21.9952 | 21.7399 | 21.3551 | 19.9392 | 21.5963 |  | 20.6307 | 20.5564 | 20.6764 | 19.1047 |  | 16.8488 | 16.7901 | 16.492 | 16.6463 | 16.7132 | 17.3315 | 18.1524 | 16.0118 | 16.981 | 16.4395 | 16.9784 | 18.007 | 44.5951 | 48.3158 | 43.8736 | 21.4354 |  |  | 0.30579 | -0.25042 | -44.2884 | 0.64721 | 0.17427 | -197.8033 | 14.1026 | -0.44851 | 0.01138 | 0.055918 | -0.1221 | 8.8282 | 9.0579 | 1.9788 | 21.7858 | 21.9947 | 22.1855 | 22.2521 | 22.0721 | 21.3839 | 20.1945 | 22.191 | 22.3624 | 22.3942 | 22.342 | 21.9651 | 21.1908 | 22.2636 | 17.1243 | 17.3049 | 16.3937 | 16.3147 | 16.2781 | 17.0907 | 16.8413 | 22.3804 | 22.1412 | 21.6913 | 22.0786 | 21.8016 | 21.2963 | 21.9397 | 21.5205 | 20.899 | 20.1056 | 21.2454 | 19.8776 | 19.816 | 0.065283 | -0.036678 | 20.7728 | 22.0473 | 22.357 | 20.0895 | 21.6482 | 22.0973 | 21.9348 | 21.7002 | 21.2697 | 21.7706 | 21.4287 | 21.0261 | 20.9622 | 21.4954 | 20.657 | 20.7231 | 20.3421 |  | 20.2454 | 19.9647 | 20.1485 | 19.7784 | 20.1075 | 20.3976 |  | 20.4378 |  |  | 20.25 | 20.3024 | 20.6707 | [5 empty] | 21.9029 | 20.3555 | 21.6446 | 22.0267 | 19.6238 | 21.1465 | 21.7688 | 19.5388 | 20.166 | 23.203 |  | 19.9671 | 21.6848 | 18.9633 | 19.8633 | 21.7388 | 19.5667 | 20.2385 | 19.1453 | 20.356 | 19.2014 | 20.3612 | 18.9366 | 20.2729 | 21.7088 | 19.6781 | 19.9063 | 22.0853 | 18.9973 | 19.915 | 21.5939 | 19.0934 | 20.3986 | 19.4546 | 20.3069 | 19.0067 | 20.3845 | -0.16634 | 20.9446 | 0.048776 | 0.012749 | -27.0588 | 3.0954 | -9.92 | 28.79 | 0.66185 | -0.59383 | -7.8971 | 0.95465 | 0.49583 | -16.7049 | 4.4604 | 0.41746 | 0.42469 | 0.42849 | 0.39863 | 0.45072 | 0.44157 | 0.42739
42838.4203 | -2 | 22.8999 | 22.8653 | 22.8555 | 22.7796 | 22.4035 | 21.7341 | 22.7213 | 21.7911 | 22.3608 | 22.3746 | 22.3488 | 22.0054 | 21.2265 | 22.1971 | 21.5917 | 21.7677 | 21.9018 | 21.0868 | 21.1833 | 21.3979 | 20.4685 | 20.607 | 20.9029 | 21.8739 | 21.6363 | 21.2589 | 21.2021 | 21.181 | 21.7898 | 22.0837 | 21.6779 | 21.1937 | 21.9986 | 21.742 | 21.359 | 19.9454 | 21.5967 |  | 20.6347 | 20.5646 | 20.692 | 19.1359 |  | 16.8519 | 16.794 | 16.4959 | 16.6762 | 16.7287 | 17.364 | 18.1724 | 16.0328 | 16.9852 | 16.4827 | 16.9809 | 18.0068 | 44.6076 | 48.3388 | 43.8856 | 21.4347 |  |  | 0.41224 | -0.48962 | -44.4783 | 0.45862 | 0.24195 | -197.8486 | 14.0395 | -0.29344 | -0.026372 | 0.078786 | 0.014006 | 8.8283 | 9.0584 | 1.9784 | 21.7789 | 21.9923 | 22.1899 | 22.2492 | 22.0675 | 21.3798 | 20.1863 | 22.1895 | 22.3674 | 22.3893 | 22.3439 | 21.9644 | 21.193 | 22.2558 | 17.1255 | 17.2883 | 16.4252 | 16.3122 | 16.3067 | 17.0924 | 16.8426 | 22.3852 | 22.1405 | 21.6884 | 22.0755 | 21.7911 | 21.2965 | 21.9354 | 21.5191 | 20.8991 | 20.0996 | 21.2517 | 19.8688 | 19.817 | 0.10283 | -0.093738 | 20.7798 | 22.059 | 22.3611 | 20.0968 | 21.6491 | 22.0968 | 21.94 | 21.7031 | 21.2718 | 21.7768 | 21.4359 | 21.0356 | 20.975 | 21.5204 | 20.663 | 20.7359 | 20.3422 |  | 20.251 | 19.9743 | 20.1503 | 19.7882 | 20.1153 | 20.3951 |  | 20.4528 |  |  | 20.2568 | 20.2953 | 20.6719 | [5 empty] | 21.9067 | 20.3574 | 21.6414 | 22.0293 | 19.6193 | 21.1439 | 21.7679 | 19.5354 | 20.1652 | 23.1997 |  | 19.9728 | 21.6902 | 18.9641 | 19.8691 | 21.7403 | 19.5739 | 20.2417 | 19.1427 | 20.36 | 19.2019 | 20.3684 | 18.9252 | 20.2726 | 21.7069 | 19.6627 | 19.9032 | 22.0853 | 18.9856 | 19.9132 | 21.5933 | 19.0927 | 20.398 | 19.4482 | 20.2999 | 19.0069 | 20.3839 | -0.21587 | 20.945 | 0.049439 | 0.013373 | -27.0164 | 3.0954 | -0.36 | 58.89 | 0.76844 | -0.83033 | -7.914 | 0.80362 | 0.58427 | -16.7077 | 4.4507 | 0.41764 | 0.42448 | 0.42848 | 0.39869 | 0.44736 | 0.44091 | 0.42716
42838.4203 | -1 | 22.9033 | 22.8701 | 22.8595 | 22.7865 | 22.4088 | 21.7402 | 22.7147 | 21.7957 | 22.3655 | 22.3745 | 22.359 | 22.0106 | 21.2337 | 22.2075 | 21.5902 | 21.7601 | 21.8912 | 21.0844 | 21.1766 | 21.3918 | 20.4673 | 20.5985 | 20.886 | 21.8765 | 21.6381 | 21.2565 | 21.1949 | 21.1791 | 21.7701 | 22.074 | 21.6719 | 21.1859 | 21.9956 | 21.7357 | 21.3526 | 19.9427 | 21.589 |  | 20.6384 | 20.5704 | 20.696 | 19.1534 |  | 16.8482 | 16.7876 | 16.5041 | 16.6819 | 16.7512 | 17.3879 | 18.1887 | 16.0299 | 16.9885 | 16.5391 | 16.9839 | 18.0045 | 44.6346 | 48.3538 | 43.8868 | 21.4362 |  |  | 0.43195 | -0.26817 | -44.82 | 0.57099 | 0.22946 | -197.8834 | 13.8286 | -0.35849 | 0.17679 | -0.002826 | -0.015159 | 8.8295 | 9.0592 | 1.9786 | 21.7811 | 21.9906 | 22.1875 | 22.246 | 22.065 | 21.3775 | 20.1843 | 22.1851 | 22.3567 | 22.4016 | 22.3467 | 21.9573 | 21.1946 | 22.2601 | 17.1353 | 17.2596 | 16.4498 | 16.3031 | 16.329 | 17.0881 | 16.8359 | 22.3932 | 22.1381 | 21.7015 | 22.0911 | 21.7923 | 21.2974 | 21.9437 | 21.5242 | 20.8931 | 20.1098 | 21.2687 | 19.8741 | 19.8162 | -0.010604 | -0.13881 | 20.7879 | 22.0618 | 22.3594 | 20.0964 | 21.6562 | 22.1045 | 21.943 | 21.7081 | 21.2738 | 21.776 | 21.4411 | 21.0405 | 20.9928 | 21.5496 | 20.6721 | 20.7487 | 20.356 |  | 20.2538 | 19.9717 | 20.1496 | 19.786 | 20.1217 | 20.3967 |  | 20.4544 |  |  | 20.2517 | 20.3036 | 20.6695 | [5 empty] | 21.9079 | 20.358 | 21.6443 | 22.0279 | 19.6412 | 21.1501 | 21.7679 | 19.5469 | 20.1731 | 23.206 |  | 19.9796 | 21.6995 | 18.9696 | 19.8701 | 21.7435 | 19.5817 | 20.2532 | 19.143 | 20.3697 | 19.2076 | 20.3736 | 18.9384 | 20.2844 | 21.7247 | 19.6782 | 19.9123 | 22.1141 | 19.0023 | 19.9231 | 21.6136 | 19.0943 | 20.4211 | 19.4626 | 20.3149 | 19.0118 | 20.4004 | -0.026845 | 20.9452 | 0.049679 | 0.014593 | -27.0461 | 3.0953 | -10.1 | 58.39 | 0.78657 | -0.6145 | -7.9443 | 0.89667 | 0.56902 | -16.7099 | 4.4173 | 0.41735 | 0.42454 | 0.42876 | 0.3971 | 0.44385 | 0.44033 | 0.42752
42838.4203 | 0 | 22.892 | 22.8673 | 22.8488 | 22.7799 | 22.4019 | 21.7325 | 22.7138 | 21.7915 | 22.3604 | 22.3686 | 22.3462 | 22.0092 | 21.2266 | 22.1957 | 21.5876 | 21.7681 | 21.8933 | 21.0838 | 21.1811 | 21.3944 | 20.4772 | 20.6075 | 20.9003 | 21.8796 | 21.6333 | 21.2628 | 21.2109 | 21.1995 | 21.788 | 22.0792 | 21.6767 | 21.1917 | 21.9991 | 21.7327 | 21.3582 | 19.9405 | 21.5761 |  | 20.6409 | 20.5725 | 20.7064 | 19.1641 |  | 16.8535 | 16.7971 | 16.5075 | 16.7012 | 16.783 | 17.4209 | 18.2131 | 16.0048 | 17.002 | 16.5647 | 16.9898 | 18.0013 | 44.655 | 48.3608 | 43.8908 | 21.4368 |  |  | 0.43655 | -0.3076 | -44.3785 | 0.77929 | 0.38389 | -197.848 | 14.0198 | -0.25072 | 0.085134 | 0.005566 | -0.071232 | 8.8283 | 9.0581 | 1.9787 | 21.7809 | 21.996 | 22.1871 | 22.2499 | 22.0655 | 21.3762 | 20.1894 | 22.1847 | 22.3561 | 22.3896 | 22.3435 | 21.9699 | 21.1901 | 22.2572 | 17.162 | 17.2617 | 16.4341 | 16.2754 | 16.3384 | 17.096 | 16.8423 | 22.3899 | 22.1384 | 21.7024 | 22.0821 | 21.8002 | 21.2953 | 21.9445 | 21.5165 | 20.9002 | 20.1068 | 21.2889 | 19.8859 | 19.8257 | -0.02358 | 0.1657 | 20.7793 | 22.0475 | 22.3498 | 20.093 | 21.6511 | 22.0969 | 21.935 | 21.7013 | 21.2685 | 21.7696 | 21.4332 | 21.028 | 21.0004 | 21.5673 | 20.6745 | 20.7468 | 20.3574 |  | 20.2535 | 19.9703 | 20.1438 | 19.7972 | 20.1184 | 20.3946 |  | 20.4438 |  |  | 20.2445 | 20.3035 | 20.6718 | [5 empty] | 21.8935 | 20.3437 | 21.6332 | 22.0156 | 19.6325 | 21.1457 | 21.7518 | 19.5454 | 20.1822 | 23.2165 |  | 19.9872 | 21.6996 | 18.9775 | 19.8893 | 21.7486 | 19.5763 | 20.2649 | 19.1479 | 20.3728 | 19.2092 | 20.3825 | 18.9418 | 20.286 | 21.7309 | 19.6785 | 19.9195 | 22.1243 | 18.9917 | 19.927 | 21.6218 | 19.0916 | 20.4215 | 19.4696 | 20.325 | 19.0188 | 20.4021 | -0.20975 | 20.9441 | 0.049525 | 0.014578 | -27.0535 | 3.0954 | 5.45 | 62.53 | 0.79077 | -0.65814 | -7.9052 | 1.0476 | 0.73603 | -16.7093 | 4.448 | 0.4173 | 0.42438 | 0.42834 | 0.39506 | 0.44634 | 0.43997 | 0.42716
42838.4203 | 1 | 22.8962 | 22.8663 | 22.8468 | 22.7683 | 22.3974 | 21.7255 | 22.7126 | 21.789 | 22.357 | 22.3639 | 22.3422 | 21.9994 | 21.2236 | 22.191 | 21.5781 | 21.7468 | 21.8847 | 21.07 | 21.1622 | 21.3829 | 20.4518 | 20.6035 | 20.8889 | 21.8696 | 21.6198 | 21.2552 | 21.2085 | 21.1942 | 21.8053 | 22.0761 | 21.6712 | 21.1932 | 21.9978 | 21.7326 | 21.3474 | 19.9414 | 21.5545 |  | 20.6328 | 20.5684 | 20.7053 | 19.1874 |  | 16.8372 | 16.7908 | 16.5118 | 16.7049 | 16.7858 | 17.424 | 18.2146 | 16.0273 | 16.9917 | 16.563 | 16.9821 | 18.0055 | 44.6782 | 48.3654 | 43.8934 | 21.4296 |  |  | 0.42013 | -0.30365 | -44.32 | 0.38568 | 0.36352 | -197.8388 | 13.9285 | -0.27635 | 0.07735 | -0.25291 | 0.053934 | 8.8284 | 9.0583 | 1.9788 | 21.7839 | 21.9991 | 22.1855 | 22.2486 | 22.0686 | 21.3739 | 20.1888 | 22.1878 | 22.3587 | 22.3988 | 22.3403 | 21.9664 | 21.1942 | 22.2507 | 17.1989 | 17.2748 | 16.413 | 16.2537 | 16.3193 | 17.0906 | 16.8339 | 22.3848 | 22.1441 | 21.6949 | 22.0823 | 21.7952 | 21.2924 | 21.9448 | 21.5203 | 20.8941 | 20.1064 | 21.3025 | 19.8976 | 19.822 | 0.020459 | -0.051133 | 20.7828 | 22.0482 | 22.3561 | 20.0933 | 21.6463 | 22.0926 | 21.9319 | 21.7031 | 21.2676 | 21.7713 | 21.4305 | 21.0281 | 21.004 | 21.5731 | 20.6854 | 20.7499 | 20.3615 |  | 20.2473 | 19.9764 | 20.1425 | 19.8097 | 20.1144 | 20.3969 |  | 20.4445 |  |  | 20.2579 | 20.3167 | 20.6697 | [5 empty] | 21.8999 | 20.3538 | 21.6464 | 22.0274 | 19.6638 | 21.1473 | 21.7584 | 19.5534 | 20.1923 | 23.2384 |  | 20.0035 | 21.7157 | 18.9843 | 19.8949 | 21.7627 | 19.5938 | 20.2816 | 19.1469 | 20.3866 | 19.216 | 20.3836 | 18.9377 | 20.2789 | 21.7246 | 19.6734 | 19.9122 | 22.123 | 18.9861 | 19.9244 | 21.6183 | 19.0759 | 20.415 | 19.4557 | 20.315 | 19.0056 | 20.3972 | 0.014708 | 20.9442 | 0.049501 | 0.013889 | -27.0623 | 3.0954 | -2.9 | 61.94 | 0.77577 | -0.6539 | -7.8999 | 0.73695 | 0.71624 | -16.709 | 4.4335 | 0.41698 | 0.42417 | 0.42786 | 0.39032 | 0.44771 | 0.43935 | 0.42725
42838.4203 | 2 | 22.8978 | 22.8552 | 22.8556 | 22.7757 | 22.391 | 21.7314 | 22.709 | 21.7959 | 22.3575 | 22.3614 | 22.3496 | 22.0086 | 21.2293 | 22.1979 | 21.5933 | 21.7673 | 21.8964 | 21.0843 | 21.1754 | 21.3946 | 20.4645 | 20.6109 | 20.905 | 21.8753 | 21.634 | 21.2595 | 21.2291 | 21.2128 | 21.8247 | 22.0865 | 21.6783 | 21.1966 | 22.0059 | 21.7374 | 21.3594 | 19.9427 | 21.5573 |  | 20.6435 | 20.5772 | 20.7235 | 19.2007 |  | 16.8534 | 16.806 | 16.5205 | 16.7095 | 16.7864 | 17.413 | 18.2107 | 16.0735 | 17.0003 | 16.5315 | 16.9864 | 18.0077 | 44.7104 | 48.3773 | 43.913 | 21.4394 |  |  | 0.41815 | -0.33651 | -44.0433 | 0.71621 | 0.25378 | -197.8552 | 14.1375 | -0.11667 | -0.13729 | -0.34417 | -0.1181 | 8.8291 | 9.0588 | 1.9787 | 21.7907 | 22.0052 | 22.1927 | 22.2475 | 22.0705 | 21.3842 | 20.1886 | 22.1918 | 22.3675 | 22.398 | 22.3451 | 21.9695 | 21.1991 | 22.2642 | 17.2403 | 17.3135 | 16.398 | 16.2469 | 16.3154 | 17.0957 | 16.8394 | 22.393 | 22.1519 | 21.699 | 22.0833 | 21.7917 | 21.3002 | 21.9486 | 21.5155 | 20.8976 | 20.1053 | 21.3535 | 19.9253 | 19.8351 | 0.11129 | 0.031604 | 20.795 | 22.0565 | 22.3597 | 20.0947 | 21.6487 | 22.0961 | 21.9319 | 21.7021 | 21.2692 | 21.7783 | 21.4325 | 21.0376 | 21.0126 | 21.5854 | 20.6937 | 20.7621 | 20.3748 |  | 20.2559 | 20.0019 | 20.1452 | 19.8122 | 20.1162 | 20.3989 |  | 20.4546 |  |  | 20.2664 | 20.326 | 20.6831 | [5 empty] | 21.9163 | 20.357 | 21.6493 | 22.029 | 19.6883 | 21.1518 | 21.7701 | 19.5458 | 20.1902 | 23.271 |  | 19.9978 | 21.7156 | 18.9697 | 19.8809 | 21.7592 | 19.5855 | 20.2814 | 19.1377 | 20.3712 | 19.2052 | 20.3731 | 18.9413 | 20.2904 | 21.7335 | 19.6826 | 19.9164 | 22.1281 | 18.9924 | 19.9325 | 21.6256 | 19.0812 | 20.4293 | 19.4636 | 20.333 | 19.007 | 20.4016 | -0.25631 | 20.9439 | 0.049747 | 0.014048 | -27.0735 | 3.0954 | -0.56 | 63.09 | 0.77398 | -0.68838 | -7.8754 | 1.0043 | 0.59843 | -16.7094 | 4.4666 | 0.4169 | 0.42355 | 0.42785 | 0.38631 | 0.45001 | 0.43902 | 0.42684
42838.4203 | 3 | 22.9089 | 22.8728 | 22.8675 | 22.7775 | 22.4031 | 21.7435 | 22.721 | 21.7906 | 22.3688 | 22.3772 | 22.354 | 22.0062 | 21.2348 | 22.2019 | 21.5905 | 21.7743 | 21.8934 | 21.0897 | 21.1824 | 21.3992 | 20.4748 | 20.6133 | 20.9067 | 21.8822 | 21.6367 | 21.2634 | 21.2457 | 21.2285 | 21.9485 | 22.0748 | 21.6793 | 21.1884 | 21.9964 | 21.7396 | 21.3566 | 19.9425 | 21.5542 |  | 20.636 | 20.5794 | 20.7264 | 19.1933 |  | 16.8517 | 16.8011 | 16.5224 | 16.7045 | 16.7811 | 17.3982 | 18.1929 | 16.1011 | 16.9902 | 16.5084 | 16.9803 | 18.0023 | 44.7385 | 48.378 | 43.9179 | 21.4268 |  |  | 0.45233 | -0.051977 | -43.4204 | 0.83778 | 0.25706 | -197.825 | 14.238 | -0.30526 | 0.11705 | -0.18325 | -0.11585 | 8.8287 | 9.0588 | 1.979 | 21.7839 | 21.9992 | 22.1899 | 22.2528 | 22.0675 | 21.3765 | 20.1905 | 22.1831 | 22.3696 | 22.3964 | 22.3486 | 21.9714 | 21.1964 | 22.2571 | 17.2539 | 17.3021 | 16.3942 | 16.2345 | 16.3108 | 17.0982 | 16.8356 | 22.3938 | 22.1486 | 21.6985 | 22.0851 | 21.791 | 21.3015 | 21.9412 | 21.5125 | 20.8934 | 20.1082 | 21.5529 | 19.9579 | 19.8482 | 0.10991 | 0.056711 | 20.8043 | 22.063 | 22.3573 | 20.0944 | 21.6523 | 22.0984 | 21.932 | 21.702 | 21.2665 | 21.7735 | 21.4334 | 21.0366 | 21.0267 | 21.6972 | 20.6927 | 20.7685 | 20.3846 |  | 20.254 | 20.022 | 20.1596 | 19.8152 | 20.1301 | 20.4067 |  | 20.4587 |  |  | 20.2514 | 20.3272 | 20.6877 | [5 empty] | 21.9098 | 20.3666 | 21.6439 | 22.0182 | 19.7248 | 21.1457 | 21.7752 | 19.5581 | 20.1972 | 23.6175 |  | 19.9964 | 21.7269 | 18.9826 | 19.8919 | 21.7733 | 19.5952 | 20.3093 | 19.1327 | 20.3895 | 19.2141 | 20.3916 | 18.9506 | 20.2929 | 21.7346 | 19.6813 | 19.9282 | 22.1411 | 18.9968 | 19.9416 | 21.6213 | 19.0786 | 20.4336 | 19.4711 | 20.3444 | 19.0117 | 20.412 | -0.088616 | 20.9449 | 0.049796 | 0.014215 | -27.051 | 3.0954 | 6.57 | 61.71 | 0.80515 | -0.27054 | -7.8195 | 1.0862 | 0.60228 | -16.7077 | 4.4823 | 0.41656 | 0.42347 | 0.42823 | 0.3851 | 0.44999 | 0.43922 | 0.42658
42838.4203 | 4 | 22.9056 | 22.8647 | 22.8581 | 22.7769 | 22.3988 | 21.7373 | 22.7113 | 21.7911 | 22.3629 | 22.3726 | 22.3505 | 22.0083 | 21.2293 | 22.1996 | 21.5914 | 21.7624 | 21.8946 | 21.0821 | 21.1808 | 21.3962 | 20.4748 | 20.6055 | 20.8983 | 21.8729 | 21.6419 | 21.2574 | 21.3619 | 21.2382 | 22.8045 | 22.0765 | 21.6724 | 21.1885 | 21.9987 | 21.735 | 21.3433 | 19.9363 | 21.5604 |  | 20.6394 | 20.5837 | 20.7387 | 19.1847 |  | 16.8618 | 16.811 | 16.524 | 16.7053 | 16.7858 | 17.3828 | 18.1583 | 16.1105 | 16.995 | 16.4427 | 16.9833 | 18.0058 | 44.7673 | 48.3839 | 43.9454 | 21.4323 |  |  | 0.49175 | -0.013865 | -43.4132 | 0.57165 | 0.18938 | -197.8657 | 14.3845 | -0.20604 | 0.13826 | -0.045625 | 0.085355 | 8.8294 | 9.0591 | 1.9788 | 21.7834 | 21.9944 | 22.1946 | 22.2609 | 22.0738 | 21.3784 | 20.1887 | 22.1919 | 22.3643 | 22.3932 | 22.3517 | 21.9689 | 21.1984 | 22.2532 | 17.2712 | 17.2806 | 16.3769 | 16.2287 | 16.3004 | 17.0834 | 16.8323 | 22.3777 | 22.1355 | 21.688 | 22.0752 | 21.7841 | 21.2863 | 21.9337 | 21.5077 | 20.8846 | 20.1003 | 21.8308 | 20.01 | 19.8712 | 0.016723 | -0.036678 | 20.8136 | 22.0596 | 22.3579 | 20.0945 | 21.6575 | 22.0995 | 21.9399 | 21.7056 | 21.27 | 21.7738 | 21.4361 | 21.0328 | 21.0401 | 22.0043 | 20.6947 | 20.7723 | 20.3914 |  | 20.2597 | 20.0448 | 20.153 | 19.812 | 20.1233 | 20.4 |  | 20.4514 |  |  | 20.2662 | 20.3352 | 20.692 | [5 empty] | 21.9072 | 20.3778 | 21.6509 | 22.0215 | 19.7791 | 21.1476 | 21.7711 | 19.5639 | 20.2121 | 24.4319 |  | 20.0081 | 21.7262 | 18.9765 | 19.8961 | 21.7781 | 19.6058 | 20.3334 | 19.1256 | 20.3885 | 19.2093 | 20.3933 | 18.9568 | 20.3069 | 21.7514 | 19.698 | 19.9403 | 22.16 | 19.0029 | 19.9573 | 21.6414 | 19.086 | 20.449 | 19.4879 | 20.3779 | 19.0262 | 20.4273 | -0.11255 | 20.9451 | 0.049581 | 0.014462 | -27.0898 | 3.0954 | -4.99 | 63.01 | 0.84072 | -0.13973 | -7.8189 | 0.89722 | 0.51693 | -16.709 | 4.5052 | 0.41656 | 0.42262 | 0.42809 | 0.38145 | 0.45153 | 0.43925 | 0.42568
42838.4203 | 5 | 22.8899 | 22.8579 | 22.8474 | 22.7746 | 22.3984 | 21.7326 | 22.7119 | 21.7947 | 22.3621 | 22.3673 | 22.3475 | 22.0052 | 21.2236 | 22.1912 | 21.5947 | 21.7674 | 21.8985 | 21.0866 | 21.1833 | 21.4042 | 20.4782 | 20.6036 | 20.8978 | 21.8733 | 21.6412 | 21.2586 | 21.6133 | 21.2538 | 24.1559 | 22.083 | 21.6831 | 21.1943 | 22.0017 | 21.7467 | 21.3521 | 19.9518 | 21.6019 |  | 20.6475 | 20.5923 | 20.7551 | 19.1903 |  | 16.862 | 16.81 | 16.5337 | 16.7272 | 16.781 | 17.3695 | 18.1167 | 16.0919 | 16.9839 | 16.3821 | 16.9787 | 18.0069 | 44.8049 | 48.3919 | 43.9919 | 21.4455 |  |  | 0.62581 | -0.057893 | -43.5571 | 0.49739 | 0.0435 | -197.8552 | 14.2084 | -0.50108 | -0.071325 | -0.066395 | -0.012382 | 8.829 | 9.0585 | 1.9783 | 21.7843 | 21.9899 | 22.1959 | 22.2514 | 22.0675 | 21.3774 | 20.1859 | 22.1777 | 22.3643 | 22.3849 | 22.3405 | 21.9675 | 21.2046 | 22.2559 | 17.2782 | 17.2855 | 16.3743 | 16.2502 | 16.2929 | 17.095 | 16.8317 | 22.3833 | 22.1419 | 21.6922 | 22.0731 | 21.7946 | 21.2967 | 21.9388 | 21.5173 | 20.8914 | 20.1081 | 22.0831 | 20.0948 | 19.9183 | -0.07214 | 0.13926 | 20.8256 | 22.0608 | 22.3641 | 20.0977 | 21.6596 | 22.1018 | 21.9392 | 21.7065 | 21.2705 | 21.7775 | 21.4398 | 21.0371 | 21.0544 | 22.438 | 20.7001 | 20.7783 | 20.4041 |  | 20.2602 | 20.0725 | 20.1591 | 19.8241 | 20.1319 | 20.4017 |  | 20.4559 |  |  | 20.2749 | 20.3399 | 20.7048 | [5 empty] | 21.9162 | 20.3993 | 21.6569 | 22.0357 | 19.8643 | 21.1529 | 21.7718 | 19.567 | 20.2452 | 25.5692 |  | 20.0147 | 21.7275 | 18.9709 | 19.9057 | 21.7959 | 19.6258 | 20.3649 | 19.1233 | 20.3924 | 19.2093 | 20.3966 | 18.9593 | 20.3185 | 21.7522 | 19.7082 | 19.9484 | 22.3086 | 19.0112 | 19.9567 | 21.6436 | 19.0898 | 20.4567 | 19.4945 | 20.479 | 19.029 | 20.4321 | -0.26113 | 20.9433 | 0.049999 | 0.015188 | -27.0258 | 3.0954 | -21.55 | 62.31 | 0.95058 | -0.28553 | -7.8319 | 0.83692 | 0.24774 | -16.7081 | 4.4774 | 0.41623 | 0.42205 | 0.42804 | 0.38203 | 0.45174 | 0.43962 | 0.42463
42838.4203 | 6 | 22.8916 | 22.8595 | 22.8491 | 22.7753 | 22.4033 | 21.7264 | 22.7139 | 21.7987 | 22.3594 | 22.366 | 22.3532 | 22.0018 | 21.2189 | 22.1916 | 21.5955 | 21.7698 | 21.8977 | 21.0891 | 21.1846 | 21.4005 | 20.476 | 20.6139 | 20.9038 | 21.876 | 21.6397 | 21.2565 | 21.8566 | 21.2723 | 25.5335 | 22.0856 | 21.6799 | 21.2015 | 22.0012 | 21.747 | 21.3526 | 19.9545 | 21.6834 |  | 20.6495 | 20.5997 | 20.7683 | 19.2003 |  | 16.8761 | 16.8185 | 16.5467 | 16.7371 | 16.7823 | 17.3491 | 18.0967 | 16.0941 | 16.9866 | 16.3355 | 16.9719 | 18.0061 | 44.8135 | 48.388 | 44.0133 | 21.4394 |  |  | 0.33865 | -0.092061 | -43.7549 | 0.6873 | 0.14404 | -197.8572 | 14.0862 | -0.22575 | -0.22525 | -0.26675 | -0.10439 | 8.8286 | 9.0585 | 1.9785 | 21.7932 | 22.0071 | 22.192 | 22.2508 | 22.076 | 21.3822 | 20.192 | 22.1905 | 22.3599 | 22.3958 | 22.3439 | 21.9693 | 21.1947 | 22.2575 | 17.2676 | 17.2788 | 16.3467 | 16.264 | 16.3043 | 17.0913 | 16.8399 | 22.3852 | 22.1434 | 21.6952 | 22.0756 | 21.7919 | 21.2894 | 21.9391 | 21.5168 | 20.8894 | 20.1087 | 22.2174 | 20.1478 | 19.9684 | 0.0082694 | -0.06749 | 20.8307 | 22.057 | 22.3578 | 20.0938 | 21.6544 | 22.1012 | 21.9328 | 21.7078 | 21.2661 | 21.7754 | 21.4403 | 21.0365 | 21.063 | 22.904 | 20.7093 | 20.7844 | 20.4164 |  | 20.2604 | 20.0991 | 20.1549 | 19.8368 | 20.1444 | 20.4066 |  | 20.4521 |  |  | 20.2732 | 20.3427 | 20.7066 | [5 empty] | 21.9119 | 20.4252 | 21.6453 | 22.0224 | 19.9391 | 21.1469 | 21.7675 | 19.5807 | 20.274 | 26.8058 |  | 20.0221 | 21.7275 | 18.9666 | 19.9016 | 21.8302 | 19.6538 | 20.3927 | 19.1208 | 20.405 | 19.2144 | 20.4052 | 18.9527 | 20.3163 | 21.7525 | 19.708 | 19.9618 | 22.815 | 19.0012 | 19.957 | 21.6502 | 19.0775 | 20.4506 | 19.4913 | 20.63 | 19.0262 | 20.4331 | -0.10216 | 20.9452 | 0.049507 | 0.014273 | -27.0718 | 3.0954 | -13.94 | 62.79 | 0.70088 | -0.36006 | -7.8497 | 0.98382 | 0.4508 | -16.7076 | 4.458 | 0.41589 | 0.42118 | 0.42811 | 0.38277 | 0.45577 | 0.43943 | 0.42326
42838.4204 | 7 | 22.9088 | 22.8691 | 22.8545 | 22.7792 | 22.4058 | 21.7354 | 22.7162 | 21.7968 | 22.3645 | 22.3762 | 22.3601 | 22.0125 | 21.2275 | 22.2009 | 21.5946 | 21.7703 | 21.9009 | 21.0865 | 21.1858 | 21.3932 | 20.4755 | 20.6157 | 20.904 | 21.878 | 21.6399 | 21.2616 | 22.1893 | 21.2911 | 27.0851 | 22.0776 | 21.6646 | 21.1911 | 21.9969 | 21.7287 | 21.3491 | 19.9411 | 21.7596 |  | 20.6453 | 20.5972 | 20.769 | 19.2121 |  | 16.8845 | 16.8322 | 16.5692 | 16.7646 | 16.7963 | 17.3397 | 18.0787 | 16.1194 | 16.9833 | 16.2965 | 16.9773 | 17.9979 | 44.8262 | 48.3956 | 44.0357 | 21.4306 |  |  | 0.3945 | -0.063805 | -43.8639 | 0.40343 | 0.36483 | -197.8867 | 14.1079 | -0.50568 | -0.055368 | -0.18032 | -0.056997 | 8.8288 | 9.0586 | 1.9787 | 21.7956 | 22.0037 | 22.1963 | 22.255 | 22.0707 | 21.385 | 20.1882 | 22.1942 | 22.3631 | 22.3968 | 22.3442 | 21.9702 | 21.2015 | 22.2576 | 17.2797 | 17.2762 | 16.3394 | 16.272 | 16.3179 | 17.097 | 16.833 | 22.3987 | 22.1526 | 21.6963 | 22.0881 | 21.7943 | 21.3029 | 21.9508 | 21.5285 | 20.8968 | 20.1236 | 22.8732 | 20.2065 | 20.0226 | -0.098681 | -0.1314 | 20.8419 | 22.0581 | 22.358 | 20.0994 | 21.6586 | 22.1086 | 21.9403 | 21.7108 | 21.2732 | 21.7768 | 21.4378 | 21.0339 | 21.076 | 23.3037 | 20.7173 | 20.7942 | 20.4147 |  | 20.2644 | 20.1187 | 20.16 | 19.8398 | 20.1498 | 20.4165 |  | 20.45 |  |  | 20.2878 | 20.3491 | 20.7202 | [5 empty] | 21.9121 | 20.4573 | 21.6438 | 22.0242 | 20.0195 | 21.1483 | 21.7716 | 19.5984 | 20.3145 | 28.4992 |  | 20.0297 | 21.7329 | 18.9741 | 19.9093 | 22.0058 | 19.6808 | 20.4286 | 19.1209 | 20.4103 | 19.2196 | 20.4337 | 18.9576 | 20.32 | 21.7592 | 19.7268 | 19.9825 | 23.5435 | 19.0038 | 19.9744 | 21.6756 | 19.0815 | 20.4595 | 19.5094 | 20.6875 | 19.0355 | 20.4557 | -0.14427 | 20.9458 | 0.048579 | 0.012843 | -27.1153 | 3.0955 | -6.47 | 61.87 | 0.75844 | -0.29976 | -7.8597 | 0.75376 | 0.71743 | -16.7086 | 4.4613 | 0.41608 | 0.4208 | 0.4282 | 0.3821 | 0.45577 | 0.43865 | 0.42225
42838.4204 | 8 | 22.9109 | 22.8637 | 22.8532 | 22.773 | 22.3997 | 21.7346 | 22.7174 | 21.7904 | 22.3684 | 22.3698 | 22.347 | 22.0091 | 21.2235 | 22.2018 | 21.5907 | 21.764 | 21.8899 | 21.0795 | 21.181 | 21.3928 | 20.4712 | 20.6104 | 20.9026 | 21.8735 | 21.6432 | 21.2664 | 22.6065 | 21.3009 | 28.4534 | 22.0763 | 21.6576 | 21.1932 | 21.9941 | 21.7298 | 21.3448 | 19.9393 | 22.6066 |  | 20.6612 | 20.6045 | 20.7697 | 19.2431 |  | 16.9072 | 16.8471 | 16.5804 | 16.7659 | 16.7879 | 17.3473 | 18.0763 | 16.1403 | 16.9891 | 16.2979 | 16.9851 | 17.9984 | 44.8545 | 48.3921 | 44.0525 | 21.4346 |  |  | 0.42473 | -0.23137 | -43.8929 | 0.27397 | 0.20055 | -197.8052 | 13.8483 | -0.41566 | -0.041746 | -0.16647 | -0.26115 | 8.8287 | 9.0584 | 1.9782 | 21.7914 | 22.0003 | 22.1973 | 22.2459 | 22.0675 | 21.3803 | 20.185 | 22.1892 | 22.366 | 22.3954 | 22.3421 | 21.9702 | 21.1897 | 22.2547 | 17.2886 | 17.3168 | 16.3227 | 16.2678 | 16.3024 | 17.0833 | 16.8237 | 22.3868 | 22.1345 | 21.694 | 22.0701 | 21.7891 | 21.292 | 21.9421 | 21.5103 | 20.887 | 20.1151 | 23.6032 | 20.2235 | 20.0639 | 0.072951 | -0.095069 | 20.8474 | 22.0584 | 22.3622 | 20.1001 | 21.6574 | 22.1009 | 21.9438 | 21.705 | 21.2748 | 21.7731 | 21.4376 | 21.0315 | 21.0803 | 23.6883 | 20.7201 | 20.8019 | 20.4275 |  | 20.2702 | 20.1438 | 20.163 | 19.8458 | 20.1541 | 20.4203 |  | 20.4619 |  |  | 20.3 | 20.3576 | 20.7317 | [5 empty] | 21.9114 | 20.4821 | 21.6491 | 22.0274 | 20.0997 | 21.1444 | 21.7712 | 19.61 | 20.3487 | 30.2548 |  | 20.039 | 21.7402 | 18.9748 | 19.9229 | 22.3758 | 19.7086 | 20.4622 | 19.1205 | 20.4193 | 19.2223 | 20.485 | 18.9611 | 20.3285 | 21.7622 | 19.7344 | 19.9955 | 24.3157 | 19.0096 | 19.9778 | 21.8014 | 19.0827 | 20.4691 | 19.5178 | 20.7164 | 19.037 | 20.4851 | -0.11551 | 20.9456 | 0.048223 | 0.012734 | -27.0947 | 3.0954 | -10.46 | 62.92 | 0.78875 | -0.57084 | -7.8625 | 0.62118 | 0.53193 | -16.7054 | 4.4201 | 0.41592 | 0.4202 | 0.42818 | 0.37952 | 0.45654 | 0.43773 | 0.42082
42838.4204 | 9 | 22.9081 | 22.8711 | 22.8515 | 22.7713 | 22.3997 | 21.736 | 22.715 | 21.796 | 22.3671 | 22.3663 | 22.3499 | 22.0137 | 21.2286 | 22.1888 | 21.5927 | 21.7672 | 21.8883 | 21.0829 | 21.1801 | 21.3962 | 20.4737 | 20.6088 | 20.9023 | 21.8747 | 21.6389 | 21.26 | 23.0287 | 21.4486 | 29.7923 | 22.0769 | 21.6727 | 21.197 | 21.9961 | 21.7379 | 21.3554 | 19.9504 | 23.4191 |  | 20.6912 | 20.6143 | 20.7822 | 19.2801 |  | 16.9097 | 16.8564 | 16.5877 | 16.7636 | 16.7881 | 17.3555 | 18.0994 | 16.1385 | 16.9881 | 16.2942 | 16.9853 | 18.005 | 44.8844 | 48.3977 | 44.0678 | 21.4405 |  |  | 0.45561 | -0.48107 | -43.6845 | 0.44154 | 0.068472 | -197.8355 | 14.0494 | -0.31972 | -0.087282 | 0.011021 | -0.13182 | 8.8283 | 9.0581 | 1.9786 | 21.7913 | 22.0045 | 22.1904 | 22.2457 | 22.0665 | 21.3777 | 20.1883 | 22.1844 | 22.3595 | 22.3879 | 22.344 | 21.9625 | 21.1851 | 22.252 | 17.3099 | 17.3458 | 16.3172 | 16.2554 | 16.2936 | 17.0875 | 16.8252 | 22.3818 | 22.1356 | 21.6926 | 22.068 | 21.7879 | 21.2859 | 21.9301 | 21.5048 | 20.8821 | 20.1173 | 24.2624 | 20.2471 | 20.1144 | 0.041298 | -0.075669 | 20.8512 | 22.0627 | 22.3537 | 20.0963 | 21.6514 | 22.0928 | 21.9345 | 21.7008 | 21.2655 | 21.7702 | 21.4378 | 21.0319 | 21.0839 | 24.1126 | 20.7227 | 20.802 | 20.4484 |  | 20.2655 | 20.1598 | 20.1545 | 19.8564 | 20.1677 | 20.4256 |  | 20.4572 |  |  | 20.2974 | 20.3576 | 20.7401 | [5 empty] | 21.905 | 20.5077 | 21.6513 | 22.0217 | 20.1819 | 21.1411 | 21.7652 | 19.6236 | 20.3891 | 32.1727 |  | 20.0443 | 21.7489 | 18.9737 | 19.9335 | 22.769 | 19.7384 | 20.4982 | 19.1248 | 20.4345 | 19.2245 | 20.5747 | 18.9666 | 20.3365 | 21.7659 | 19.7437 | 20.0091 | 25.1995 | 19.012 | 19.9927 | 22.1616 | 19.0874 | 20.4723 | 19.5277 | 20.744 | 19.0393 | 20.6075 | -0.13443 | 20.9459 | 0.048493 | 0.013743 | -27.0601 | 3.0954 | -27.24 | 61.9 | 0.81874 | -0.82314 | -7.8439 | 0.7886 | 0.31081 | -16.7069 | 4.4522 | 0.41518 | 0.41947 | 0.42834 | 0.37764 | 0.45734 | 0.43708 | 0.41949
42838.4204 | 10 | 22.8942 | 22.8654 | 22.8498 | 22.7749 | 22.3955 | 21.7381 | 22.7167 | 21.7917 | 22.3657 | 22.3682 | 22.3368 | 22.0037 | 21.221 | 22.1945 | 21.5945 | 21.7683 | 21.8923 | 21.082 | 21.1798 | 21.3931 | 20.4734 | 20.6075 | 20.9037 | 21.8727 | 21.6309 | 21.2601 | 23.5029 | 21.7778 | 31.5066 | 22.0748 | 21.6758 | 21.1942 | 22.0043 | 21.7379 | 21.3529 | 19.9603 | 26.0094 |  | 20.7259 | 20.636 | 20.7977 | 19.3347 |  | 16.9093 | 16.849 | 16.5821 | 16.7666 | 16.7863 | 17.3628 | 18.1152 | 16.1301 | 16.9928 | 16.2932 | 16.9893 | 18.0041 | 44.8982 | 48.3959 | 44.084 | 21.4427 |  |  | 0.3577 | 0.013735 | -42.9256 | 0.24835 | 0.25181 | -197.842 | 14.3806 | -0.027304 | -0.16687 | 0.033889 | -0.17591 | 8.8288 | 9.0586 | 1.9787 | 21.7908 | 22.0027 | 22.1942 | 22.2508 | 22.0721 | 21.3858 | 20.1881 | 22.1884 | 22.3635 | 22.3956 | 22.3455 | 21.9678 | 21.1869 | 22.255 | 17.3352 | 17.3465 | 16.3306 | 16.2527 | 16.3325 | 17.0918 | 16.8299 | 22.3984 | 22.1446 | 21.7022 | 22.0811 | 21.7971 | 21.2955 | 21.9405 | 21.5154 | 20.8969 | 20.1326 | 24.7546 | 20.2764 | 20.1861 | -0.035179 | -0.078712 | 20.8582 | 22.0616 | 22.3584 | 20.1003 | 21.6516 | 22.0957 | 21.9276 | 21.6981 | 21.2698 | 21.767 | 21.4342 | 21.0292 | 21.2099 | 24.4591 | 20.7292 | 20.7995 | 20.4482 |  | 20.2686 | 20.1832 | 20.1647 | 19.883 | 20.1714 | 20.4282 |  | 20.4647 |  |  | 20.2998 | 20.367 | 20.7487 | [5 empty] | 21.8971 | 20.5386 | 21.6513 | 22.0185 | 20.2684 | 21.146 | 21.7635 | 19.6393 | 20.4303 | 33.7944 |  | 20.0526 | 21.7532 | 18.9762 | 19.9409 | 23.1932 | 19.7692 | 20.5399 | 19.1284 | 20.4467 | 19.2235 | 20.6209 | 18.9634 | 20.335 | 21.7695 | 19.7534 | 20.0238 | 26.075 | 19.0171 | 20.0099 | 22.8608 | 19.0914 | 20.4816 | 19.5434 | 20.7558 | 19.0427 | 20.7869 | -0.1682 | 20.9432 | 0.04818 | 0.013199 | -27.0614 | 3.0954 | -14.82 | 63.35 | 0.7275 | 0.13908 | -7.7754 | 0.59142 | 0.59605 | -16.7074 | 4.5044 | 0.41529 | 0.41917 | 0.42773 | 0.37532 | 0.45639 | 0.43589 | 0.41801
42838.4204 | 11 | 22.9047 | 22.8701 | 22.8622 | 22.775 | 22.3985 | 21.7376 | 22.7129 | 21.7969 | 22.3659 | 22.3744 | 22.348 | 22.0097 | 21.2283 | 22.1995 | 21.5883 | 21.7647 | 21.8876 | 21.0809 | 21.1829 | 21.3882 | 20.468 | 20.6038 | 20.8928 | 21.87 | 21.6303 | 21.2568 | 24.0868 | 22.2143 | 33.287 | 22.0776 | 21.6747 | 21.197 | 22.001 | 21.7338 | 21.3527 | 19.9565 | 29.3677 |  | 20.7885 | 20.6385 | 20.8105 | 19.4435 |  | 16.9109 | 16.8541 | 16.5826 | 16.7632 | 16.7865 | 17.3478 | 18.1319 | 16.1328 | 16.9846 | 16.2953 | 16.9806 | 18.0054 | 44.9076 | 48.3957 | 44.1041 | 21.4407 |  |  | 0.27688 | -0.19588 | -42.9486 | 0.78324 | 0.4818 | -197.8545 | 14.4562 | -0.27372 | -0.08086 | -0.13479 | -0.012902 | 8.8288 | 9.0589 | 1.9785 | 21.7916 | 22.0011 | 22.1965 | 22.2561 | 22.0734 | 21.377 | 20.1863 | 22.1859 | 22.361 | 22.3982 | 22.345 | 21.9712 | 21.19 | 22.2548 | 17.3531 | 17.3493 | 16.3221 | 16.2582 | 16.3278 | 17.0966 | 16.831 | 22.4022 | 22.148 | 21.6948 | 22.0799 | 21.7949 | 21.2896 | 21.9412 | 21.5134 | 20.894 | 20.1367 | 25.2172 | 20.2937 | 20.2477 | -0.097305 | -0.035536 | 20.8632 | 22.0618 | 22.3593 | 20.0955 | 21.6504 | 22.0968 | 21.9316 | 21.6928 | 21.2738 | 21.7683 | 21.4276 | 21.0262 | 21.4684 | 24.7419 | 20.7361 | 20.8088 | 20.4463 |  | 20.2872 | 20.2154 | 20.1773 | 19.9068 | 20.1955 | 20.44 |  | 20.4697 |  |  | 20.3054 | 20.3791 | 20.7597 | [5 empty] | 21.9057 | 20.574 | 21.6547 | 22.0193 | 20.3609 | 21.1431 | 21.766 | 19.6444 | 20.4665 | 35.388 |  | 20.0657 | 21.8032 | 18.9755 | 19.9479 | 23.7713 | 19.8102 | 20.5773 | 19.126 | 20.455 | 19.225 | 20.6304 | 18.9601 | 20.3508 | 21.7799 | 19.7735 | 20.0461 | 26.9704 | 19.0282 | 20.0345 | 23.6642 | 19.0921 | 20.4907 | 19.5673 | 20.7818 | 19.0564 | 20.8706 | -0.19138 | 20.9424 | 0.048389 | 0.013076 | -27.0658 | 3.0955 | -26.98 | 62.32 | 0.64192 | -0.52525 | -7.7776 | 1.0503 | 0.82446 | -16.7075 | 4.5161 | 0.41596 | 0.41869 | 0.42787 | 0.3739 | 0.45746 | 0.43274 | 0.41644
42838.4204 | 12 | 22.9088 | 22.8726 | 22.8629 | 22.7812 | 22.4092 | 21.7361 | 22.7152 | 21.7915 | 22.3694 | 22.3773 | 22.3526 | 22.0156 | 21.227 | 22.1989 | 21.5924 | 21.7658 | 21.8847 | 21.0767 | 21.1849 | 21.3872 | 20.467 | 20.6058 | 20.8913 | 21.8761 | 21.6351 | 21.2523 | 24.4422 | 22.7236 | 33.0898 | 22.0826 | 21.6734 | 21.1951 | 21.9953 | 21.7343 | 21.3486 | 19.9637 | 31.5312 |  | 20.8515 | 20.6618 | 20.8798 | 19.649 |  | 16.919 | 16.8624 | 16.5904 | 16.7709 | 16.7887 | 17.367 | 18.1505 | 16.0823 | 16.9888 | 16.3076 | 16.9777 | 18.0061 | 44.9198 | 48.3963 | 44.12 | 21.4381 |  |  | 0.42999 | -0.20114 | -43.3783 | 0.46717 | 0.31292 | -197.8401 | 14.2045 | -0.25269 | -0.029097 | 0.026336 | -0.0004032 | 8.8286 | 9.0585 | 1.9786 | 21.7938 | 22.0047 | 22.1913 | 22.254 | 22.071 | 21.3747 | 20.1904 | 22.1827 | 22.3619 | 22.392 | 22.3471 | 21.9628 | 21.1873 | 22.2497 | 17.3646 | 17.3045 | 16.3327 | 16.253 | 16.3036 | 17.0953 | 16.8303 | 22.3908 | 22.1395 | 21.6991 | 22.0818 | 21.796 | 21.2993 | 21.9418 | 21.5048 | 20.8892 | 20.141 | 25.8757 | 20.3144 | 20.2961 | -0.14724 | -0.21908 | 20.8808 | 22.062 | 22.3531 | 20.1 | 21.652 | 22.0992 | 21.935 | 21.6969 | 21.2709 | 21.7689 | 21.4314 | 21.0335 | 21.7259 | 25.2297 | 20.745 | 20.8176 | 20.4042 |  | 20.2752 | 20.2218 | 20.1752 | 19.9076 | 20.1986 | 20.4361 |  | 20.4659 |  |  | 20.296 | 20.3854 | 20.762 | [5 empty] | 21.9114 | 20.6036 | 21.6516 | 22.0213 | 20.437 | 21.1471 | 21.7609 | 19.6681 | 20.5128 | 36.7307 |  | 20.0844 | 21.9893 | 18.9726 | 19.9539 | 24.3728 | 19.8436 | 20.6038 | 19.1258 | 20.4717 | 19.2274 | 20.6417 | 18.9785 | 20.3659 | 21.7935 | 19.791 | 20.077 | 28.064 | 19.0393 | 20.0637 | 24.3677 | 19.1064 | 20.5079 | 19.5847 | 20.8101 | 19.0708 | 20.8921 | -0.22867 | 20.9423 | 0.047793 | 0.010317 | -27.0673 | 3.0955 | -23.18 | 62.74 | 0.7997 | -0.53226 | -7.8165 | 0.81117 | 0.66446 | -16.7074 | 4.4768 | 0.41673 | 0.41845 | 0.42796 | 0.37246 | 0.45621 | 0.42727 | 0.41523
42838.4204 | 13 | 22.9072 | 22.871 | 22.8598 | 22.7765 | 22.4066 | 21.7352 | 22.7144 | 21.7939 | 22.3662 | 22.3691 | 22.3481 | 22.0134 | 21.2266 | 22.192 | 21.5955 | 21.7722 | 21.8924 | 21.0856 | 21.1881 | 21.3918 | 20.4742 | 20.6075 | 20.9013 | 21.8801 | 21.6409 | 21.26 | 24.5574 | 23.2155 | 32.8846 | 22.0819 | 21.6781 | 21.1956 | 21.9945 | 21.7327 | 21.3566 | 19.9768 | 32.9408 |  | 20.916 | 20.7512 | 21.1358 | 20.3026 |  | 16.9209 | 16.8606 | 16.5953 | 16.7713 | 16.7881 | 17.3941 | 18.1796 | 16.0039 | 16.9835 | 16.2623 | 16.9881 | 17.9972 | 44.9365 | 48.3894 | 44.1251 | 21.4392 |  |  | 0.83411 | -0.13214 | -43.4 | 0.44351 | 0.25509 | -197.8788 | 13.9949 | -0.094984 | -0.036686 | -0.25501 | -0.014118 | 8.8286 | 9.0586 | 1.9788 | 21.7904 | 22.0034 | 22.196 | 22.2461 | 22.0753 | 21.3881 | 20.186 | 22.1877 | 22.3568 | 22.3961 | 22.3465 | 21.9706 | 21.1865 | 22.2515 | 17.3664 | 17.2698 | 16.3141 | 16.2845 | 16.3223 | 17.0902 | 16.8328 | 22.4058 | 22.1491 | 21.7065 | 22.086 | 21.8019 | 21.2959 | 21.9517 | 21.5184 | 20.8943 | 20.155 | 26.2587 | 20.3604 | 20.3579 | -0.078038 | -0.24285 | 20.9016 | 22.0584 | 22.3523 | 20.103 | 21.6533 | 22.1008 | 21.9363 | 21.7062 | 21.2677 | 21.7731 | 21.4352 | 21.0382 | 21.9134 | 25.809 | 20.7571 | 20.8287 | 20.374 |  | 20.2852 | 20.2489 | 20.1758 | 19.9174 | 20.2133 | 20.4421 |  | 20.4864 |  |  | 20.3003 | 20.3834 | 20.7756 | [5 empty] | 21.9158 | 20.6451 | 21.6513 | 22.0242 | 20.524 | 21.153 | 21.7589 | 19.6674 | 20.5461 | 37.6494 |  | 20.1198 | 22.2652 | 18.9698 | 19.9566 | 24.882 | 19.8747 | 20.6487 | 19.1238 | 20.4961 | 19.2266 | 20.6426 | 18.9877 | 20.3697 | 21.7951 | 19.8142 | 20.0996 | 28.9364 | 19.0316 | 20.0737 | 25.0148 | 19.1086 | 20.5194 | 19.5976 | 20.8609 | 19.0852 | 20.9147 | -0.10828 | 20.9434 | 0.047645 | 0.012495 | -27.0584 | 3.0955 | -11.75 | 62.27 | 1.1134 | -0.43142 | -7.8184 | 0.79036 | 0.59996 | -16.7099 | 4.4438 | 0.4179 | 0.41771 | 0.42818 | 0.37167 | 0.45857 | 0.40956 | 0.41399
42838.4204 | 14 | 22.8992 | 22.8628 | 22.8573 | 22.7712 | 22.3937 | 21.7316 | 22.7176 | 21.7918 | 22.3605 | 22.3639 | 22.3474 | 22.0081 | 21.2226 | 22.1911 | 21.5927 | 21.7685 | 21.8978 | 21.0906 | 21.1734 | 21.3898 | 20.4766 | 20.6086 | 20.9014 | 21.878 | 21.6446 | 21.2595 | 25.0706 | 23.7122 | 34.3987 | 22.0777 | 21.6794 | 21.1937 | 21.9941 | 21.7365 | 21.3485 | 19.9883 | 34.3482 |  | 20.9903 | 20.8819 | 21.5546 | 21.2499 |  | 16.9117 | 16.8571 | 16.5866 | 16.759 | 16.7972 | 17.3959 | 18.1894 | 15.8947 | 16.9785 | 16.1038 | 16.99 | 18.0055 | 44.9569 | 48.3935 | 44.1548 | 21.4402 |  |  | 0.63106 | -0.24188 | -42.0733 | 0.31209 | 0.25049 | -197.7691 | 14.4995 | -0.3782 | -0.19509 | -0.11675 | 0.093514 | 8.828 | 9.0582 | 1.9785 | 21.7937 | 21.9998 | 22.1892 | 22.244 | 22.0639 | 21.3745 | 20.1848 | 22.1855 | 22.3607 | 22.3943 | 22.34 | 21.9616 | 21.1901 | 22.2476 | 17.3755 | 17.2481 | 16.314 | 16.3069 | 16.3259 | 17.0934 | 16.8213 | 22.3902 | 22.1375 | 21.6919 | 22.077 | 21.7891 | 21.2908 | 21.9358 | 21.5134 | 20.8895 | 20.1437 | 26.4636 | 20.4744 | 20.3681 | -0.046779 | -0.25617 | 20.9134 | 22.064 | 22.3587 | 20.1064 | 21.6571 | 22.1038 | 21.9423 | 21.7073 | 21.2719 | 21.7755 | 21.4376 | 21.0373 | 22.0324 | 26.3541 | 20.7701 | 20.8456 | 20.335 |  | 20.2951 | 20.2863 | 20.1822 | 19.9257 | 20.2209 | 20.438 |  | 20.4949 |  |  | 20.2939 | 20.3741 | 20.7728 | [5 empty] | 21.903 | 20.6643 | 21.645 | 22.0095 | 20.5981 | 21.1376 | 21.7625 | 19.6729 | 20.5734 | 39.1824 |  | 20.1251 | 22.5037 | 18.9667 | 19.9433 | 25.3894 | 19.8903 | 20.6749 | 19.1169 | 20.5615 | 19.2197 | 20.648 | 18.9688 | 20.3744 | 21.7995 | 19.8121 | 20.1162 | 29.5119 | 19.0251 | 20.0901 | 25.7755 | 19.1114 | 20.5222 | 19.5913 | 21.0591 | 19.0797 | 20.9283 | -0.25686 | 20.9441 | 0.046041 | 0.010077 | -27.0877 | 3.0955 | -21.91 | 62.56 | 0.97087 | -0.58368 | -7.6979 | 0.66299 | 0.59453 | -16.7053 | 4.5233 | 0.41932 | 0.41689 | 0.4282 | 0.37103 | 0.45724 | 0.38363 | 0.41333
42838.4205 | 15 | 22.9009 | 22.8603 | 22.8467 | 22.7718 | 22.3997 | 21.7283 | 22.7161 | 21.7912 | 22.3613 | 22.3612 | 22.3441 | 22.0014 | 21.2234 | 22.188 | 21.5876 | 21.7696 | 21.8988 | 21.0809 | 21.1732 | 21.391 | 20.4745 | 20.6086 | 20.8993 | 21.8754 | 21.6373 | 21.2583 | 25.6328 | 24.2511 | 35.0704 | 22.0757 | 21.6723 | 21.1881 | 21.9947 | 21.7333 | 21.3479 | 20.0051 | 35.9981 |  | 21.0543 | 21.01 | 22.0554 | 21.7211 |  | 16.9188 | 16.861 | 16.5964 | 16.7703 | 16.7963 | 17.4101 | 18.2284 | 15.7998 | 16.986 | 15.989 | 16.9878 | 18.0012 | 44.9836 | 48.386 | 44.1724 | 21.4375 |  |  | 0.32485 | -0.14397 | -41.0705 | 0.44482 | 0.40754 | -197.8164 | 14.9792 | -0.10747 | -0.073271 | -0.24682 | 0.01279 | 8.8282 | 9.0582 | 1.9785 | 21.7978 | 22.0083 | 22.1888 | 22.2488 | 22.0712 | 21.3802 | 20.1849 | 22.1881 | 22.3615 | 22.3928 | 22.3412 | 21.96 | 21.1888 | 22.2538 | 17.3783 | 17.262 | 16.313 | 16.325 | 16.3328 | 17.0942 | 16.8217 | 22.3943 | 22.1444 | 21.6951 | 22.0796 | 21.786 | 21.2882 | 21.9399 | 21.5159 | 20.8896 | 20.1507 | 26.864 | 20.7124 | 20.3686 | -0.068208 | -0.058741 | 20.9234 | 22.0685 | 22.3654 | 20.1081 | 21.6582 | 22.1028 | 21.9441 | 21.7082 | 21.2738 | 21.773 | 21.4441 | 21.0383 | 22.1179 | 27.0083 | 20.7782 | 20.8594 | 20.3047 |  | 20.2898 | 20.3159 | 20.1765 | 19.9276 | 20.2263 | 20.4446 |  | 20.5003 |  |  | 20.3009 | 20.3796 | 20.7895 | [5 empty] | 21.9139 | 20.6947 | 21.6491 | 22.0266 | 20.6786 | 21.1509 | 21.7707 | 19.6792 | 20.6188 | 40.4711 |  | 20.1457 | 22.8864 | 18.9645 | 19.9459 | 25.9438 | 19.9259 | 20.7262 | 19.1211 | 20.5971 | 19.2181 | 20.6677 | 18.9717 | 20.3898 | 21.9625 | 19.8153 | 20.1296 | 30.2825 | 19.0262 | 20.109 | 26.3785 | 19.1079 | 20.5449 | 19.5998 | 21.1939 | 19.0785 | 21.0235 | -0.14427 | 20.9431 | 0.046859 | 0.011384 | -27.0731 | 3.0955 | -12.97 | 63 | 0.69733 | -0.45031 | -7.6057 | 0.79153 | 0.75835 | -16.7077 | 4.5976 | 0.41998 | 0.41588 | 0.42833 | 0.37081 | 0.4574 | 0.3711 | 0.41355
42838.4205 | 16 | 22.9083 | 22.867 | 22.8592 | 22.7774 | 22.4059 | 21.7454 | 22.7159 | 21.7988 | 22.3703 | 22.3748 | 22.3531 | 22.0111 | 21.2328 | 22.1971 | 21.5971 | 21.7681 | 21.9049 | 21.0898 | 21.1884 | 21.3965 | 20.4792 | 20.6167 | 20.8993 | 21.8786 | 21.6366 | 21.2655 | 25.8601 | 24.761 | 34.8963 | 22.0807 | 21.6735 | 21.1925 | 21.9886 | 21.7284 | 21.3433 | 20.0085 | 38.1067 |  | 21.1319 | 21.1294 | 22.6103 | 21.7282 |  | 16.92 | 16.8657 | 16.5973 | 16.7677 | 16.7936 | 17.415 | 18.265 | 15.7513 | 16.9831 | 16.0138 | 16.9934 | 18.0019 | 45.0089 | 48.3897 | 44.1719 | 21.4365 |  |  | 0.45101 | -0.17026 | -41.156 | 0.3226 | 0.33986 | -197.8355 | 14.8504 | 0.01278 | -0.023259 | -0.089893 | 0.08657 | 8.8289 | 9.0586 | 1.9789 | 21.802 | 21.9968 | 22.1855 | 22.2469 | 22.0664 | 21.3795 | 20.1904 | 22.1857 | 22.3553 | 22.3922 | 22.3382 | 21.958 | 21.1889 | 22.2505 | 17.3773 | 17.2558 | 16.3174 | 16.3431 | 16.3421 | 17.0923 | 16.8256 | 22.3956 | 22.1471 | 21.6996 | 22.0815 | 21.7885 | 21.2963 | 21.939 | 21.5149 | 20.8866 | 20.1678 | 27.3909 | 20.9345 | 20.3993 | -0.13427 | -0.071865 | 20.9286 | 22.0651 | 22.3656 | 20.1097 | 21.6582 | 22.1022 | 21.9438 | 21.7088 | 21.2717 | 21.7771 | 21.4447 | 21.0415 | 22.28 | 27.4995 | 20.7874 | 20.8669 | 20.3012 |  | 20.2961 | 20.3371 | 20.1772 | 19.9323 | 20.2422 | 20.4608 |  | 20.5434 |  |  | 20.298 | 20.37 | 20.795 | [5 empty] | 21.9118 | 20.7126 | 21.6468 | 22.0151 | 20.7404 | 21.1404 | 21.7573 | 19.6936 | 20.6581 | 41.8986 |  | 20.1791 | 23.2299 | 18.9725 | 19.9492 | 26.7478 | 19.9599 | 20.7648 | 19.1208 | 20.6041 | 19.2206 | 20.6917 | 18.9823 | 20.4245 | 22.325 | 19.8422 | 20.1597 | 31.3936 | 19.0494 | 20.1468 | 26.8273 | 19.1266 | 20.5929 | 19.6259 | 21.3836 | 19.0961 | 21.2171 | -0.1528 | 20.9437 | 0.048598 | 0.012524 | -27.0738 | 3.0955 | -1.62 | 62.22 | 0.82143 | -0.4897 | -7.6137 | 0.67408 | 0.69253 | -16.7086 | 4.5778 | 0.42029 | 0.41531 | 0.42873 | 0.3707 | 0.45736 | 0.37102 | 0.41327
42838.4205 | 17 | 22.9069 | 22.8717 | 22.8534 | 22.7775 | 22.4087 | 21.7436 | 22.7146 | 21.795 | 22.3603 | 22.3724 | 22.3526 | 22.0083 | 21.2255 | 22.1955 | 21.5938 | 21.7628 | 21.9032 | 21.0842 | 21.1801 | 21.3945 | 20.4699 | 20.6098 | 20.8994 | 21.8761 | 21.6338 | 21.2604 | 26.1034 | 25.2681 | 35.1479 | 22.087 | 21.6796 | 21.1972 | 22.0045 | 21.7381 | 21.353 | 20.0414 | 39.5215 |  | 21.222 | 21.1914 | 23.0662 | 21.6148 |  | 16.9271 | 16.8749 | 16.6044 | 16.7718 | 16.8149 | 17.4559 | 18.3289 | 15.6978 | 16.9896 | 16.0408 | 16.989 | 18.0045 | 45.0156 | 48.4011 | 44.1815 | 21.4346 |  |  | 0.42407 | -0.052633 | -40.949 | 0.42577 | 0.50414 | -197.8158 | 14.7939 | -0.006276 | -0.13613 | -0.37102 | 0.15184 | 8.828 | 9.0579 | 1.9783 | 21.7999 | 22.0012 | 22.1842 | 22.2517 | 22.0714 | 21.382 | 20.186 | 22.1876 | 22.3595 | 22.3897 | 22.3422 | 21.9633 | 21.186 | 22.2504 | 17.3898 | 17.2494 | 16.3272 | 16.3407 | 16.3517 | 17.0907 | 16.8198 | 22.4017 | 22.1563 | 21.705 | 22.0915 | 21.7979 | 21.2988 | 21.9506 | 21.5145 | 20.8939 | 20.1833 | 28.1035 | 21.1591 | 20.4558 | -0.27483 | -0.20215 | 20.9318 | 22.06 | 22.3594 | 20.1074 | 21.6566 | 22.1022 | 21.936 | 21.6996 | 21.2709 | 21.7729 | 21.4372 | 21.0301 | 22.6283 | 28.0431 | 20.8302 | 20.901 | 20.3172 |  | 20.3035 | 20.3782 | 20.1928 | 19.9632 | 20.2596 | 20.5262 |  | 20.5863 |  |  | 20.3198 | 20.379 | 20.8123 | [5 empty] | 21.9138 | 20.7528 | 21.6481 | 22.0319 | 20.8131 | 21.1502 | 21.7685 | 19.7034 | 20.6984 | 43.3778 |  | 20.2009 | 23.6134 | 18.9738 | 19.9603 | 27.4331 | 19.9994 | 20.8261 | 19.1253 | 20.6209 | 19.2276 | 20.7121 | 18.9823 | 20.4454 | 22.7942 | 19.8445 | 20.1783 | 32.2077 | 19.0437 | 20.1758 | 27.5128 | 19.1391 | 20.681 | 19.6282 | 21.4848 | 19.1025 | 21.3453 | -0.10995 | 20.9435 | 0.048979 | 0.013213 | -27.0673 | 3.0955 | -9.89 | 62.87 | 0.79684 | -0.27228 | -7.5946 | 0.77441 | 0.84352 | -16.709 | 4.5694 | 0.42009 | 0.41469 | 0.42846 | 0.36913 | 0.45559 | 0.37527 | 0.41222
42838.4205 | 18 | 22.9034 | 22.8728 | 22.8523 | 22.779 | 22.3995 | 21.7376 | 22.7136 | 21.7974 | 22.3668 | 22.3656 | 22.3429 | 22.0088 | 21.2327 | 22.1938 | 21.6025 | 21.7704 | 21.8986 | 21.0816 | 21.1783 | 21.3958 | 20.4727 | 20.6037 | 20.9019 | 21.877 | 21.6449 | 21.2621 | 26.494 | 25.8553 | 36.999 | 22.0758 | 21.6759 | 21.1901 | 22.0007 | 21.7354 | 21.3459 | 20.046 | 41.0453 |  | 21.3134 | 21.327 | 23.2623 | 21.4843 |  | 16.9234 | 16.8691 | 16.6043 | 16.7736 | 16.8419 | 17.4936 | 18.3737 | 15.6667 | 16.9864 | 16.0436 | 16.9866 | 18.0052 | 45.0103 | 48.3964 | 44.1787 | 21.4413 |  |  | 0.37019 | -0.42916 | -40.853 | 0.099838 | 0.3898 | -197.7895 | 14.8386 | -0.10484 | 0.15811 | 0.01165 | -0.050053 | 8.8291 | 9.0592 | 1.9786 | 21.7951 | 22.0059 | 22.1988 | 22.2467 | 22.0686 | 21.3844 | 20.1843 | 22.1866 | 22.3598 | 22.3877 | 22.3447 | 21.9661 | 21.1867 | 22.254 | 17.3811 | 17.2646 | 16.3092 | 16.3439 | 16.3514 | 17.0967 | 16.8138 | 22.4059 | 22.1499 | 21.7027 | 22.078 | 21.7925 | 21.2941 | 21.9416 | 21.5161 | 20.8935 | 20.175 | 28.7713 | 21.3042 | 20.4827 | -0.055232 | -0.18275 | 20.9502 | 22.0641 | 22.365 | 20.1089 | 21.66 | 22.108 | 21.9389 | 21.7079 | 21.2759 | 21.7736 | 21.4407 | 21.0306 | 22.9542 | 28.7157 | 20.9489 | 21.0292 | 20.3501 |  | 20.3046 | 20.4062 | 20.2006 | 19.9843 | 20.2644 | 20.6087 |  | 20.6335 |  |  | 20.3287 | 20.3611 | 20.8217 | [5 empty] | 21.9124 | 20.7726 | 21.6485 | 22.0243 | 20.8669 | 21.1419 | 21.7659 | 19.719 | 20.7458 | 44.8148 |  | 20.2159 | 24.1027 | 18.9885 | 19.9709 | 28.0373 | 20.0203 | 20.924 | 19.1245 | 20.6291 | 19.2356 | 20.7685 | 18.9911 | 20.479 | 23.3429 | 19.8554 | 20.201 | 32.8932 | 19.0498 | 20.2056 | 28.0305 | 19.153 | 20.7831 | 19.6463 | 21.4962 | 19.11 | 21.4519 | -0.11366 | 20.9425 | 0.050158 | 0.014143 | -27.097 | 3.0955 | -21.54 | 62.04 | 0.74673 | -0.77748 | -7.5856 | 0.375 | 0.74177 | -16.7089 | 4.5766 | 0.41922 | 0.41417 | 0.42803 | 0.3708 | 0.4569 | 0.37905 | 0.41119
42838.4205 | 19 | 22.9111 | 22.8691 | 22.8548 | 22.776 | 22.403 | 21.737 | 22.7214 | 21.7896 | 22.3683 | 22.3709 | 22.342 | 22.0063 | 21.2261 | 22.1957 | 21.5937 | 21.766 | 21.9012 | 21.0879 | 21.1911 | 21.3943 | 20.4733 | 20.609 | 20.9066 | 21.8788 | 21.6417 | 21.2615 | 27.0429 | 26.4316 | 39.1519 | 22.0714 | 21.6804 | 21.1994 | 22.0018 | 21.7373 | 21.3546 | 20.0489 | 42.1712 |  | 21.4024 | 21.6146 | 23.4648 | 21.3919 |  | 16.9292 | 16.8797 | 16.6128 | 16.7891 | 16.8666 | 17.5562 | 18.479 | 15.6488 | 16.9972 | 16.0625 | 16.9908 | 18.0116 | 45.0079 | 48.3914 | 44.2004 | 21.4461 |  |  | 0.62777 | -0.36739 | -41.1343 | 0.43168 | 0.56262 | -197.892 | 14.6316 | -0.027304 | 0.094085 | 0.062212 | -0.090154 | 8.8287 | 9.0585 | 1.9786 | 21.7963 | 22.0132 | 22.2012 | 22.2543 | 22.0717 | 21.3796 | 20.1873 | 22.1865 | 22.3609 | 22.398 | 22.3452 | 21.9626 | 21.1901 | 22.255 | 17.3805 | 17.2683 | 16.3105 | 16.3576 | 16.3726 | 17.0963 | 16.8232 | 22.4031 | 22.1499 | 21.6994 | 22.0811 | 21.792 | 21.2921 | 21.9328 | 21.5144 | 20.8907 | 20.1807 | 29.4078 | 21.3803 | 20.5239 | -0.032623 | -0.24171 | 20.9616 | 22.0671 | 22.3669 | 20.1176 | 21.6601 | 22.1082 | 21.9456 | 21.715 | 21.2808 | 21.7724 | 21.4426 | 21.0354 | 23.142 | 29.4171 | 21.1095 | 21.2119 | 20.3952 |  | 20.3066 | 20.4686 | 20.1983 | 20.0169 | 20.2828 | 20.6858 |  | 20.6733 |  |  | 20.3282 | 20.3748 | 20.8307 | [5 empty] | 21.9176 | 20.805 | 21.6489 | 22.0193 | 20.931 | 21.1461 | 21.7651 | 19.7301 | 20.7905 | 46.2656 |  | 20.2205 | 24.713 | 18.9912 | 19.9887 | 28.6229 | 20.0436 | 21.0545 | 19.1317 | 20.6356 | 19.2305 | 20.9463 | 18.9935 | 20.4984 | 23.8959 | 19.8635 | 20.2163 | 34.0284 | 19.047 | 20.223 | 28.511 | 19.1571 | 20.8944 | 19.6569 | 21.4891 | 19.1072 | 21.5028 | -0.12776 | 20.9441 | 0.050545 | 0.014825 | -27.108 | 3.0955 | -6.19 | 62.93 | 0.97579 | -0.71937 | -7.6118 | 0.77978 | 0.89126 | -16.7151 | 4.5451 | 0.41803 | 0.41236 | 0.42774 | 0.37081 | 0.45785 | 0.38171 | 0.41024
42838.4205 | 20 | 22.9049 | 22.8705 | 22.8568 | 22.7743 | 22.4011 | 21.7391 | 22.7234 | 21.7925 | 22.3702 | 22.3722 | 22.3494 | 22.003 | 21.2323 | 22.186 | 21.5851 | 21.764 | 21.9015 | 21.0823 | 21.1808 | 21.3919 | 20.4711 | 20.6049 | 20.9001 | 21.872 | 21.6303 | 21.2534 | 27.5917 | 26.9637 | 41.0062 | 22.0757 | 21.6787 | 21.1943 | 21.9964 | 21.7364 | 21.3489 | 20.0563 | 42.9138 |  | 21.4939 | 21.9427 | 23.8821 | 21.2814 |  | 16.9345 | 16.8872 | 16.6049 | 16.7898 | 16.8769 | 17.7117 | 18.67 | 15.6456 | 17.0047 | 16.0763 | 16.9968 | 18.0074 | 45.0094 | 48.3896 | 44.2141 | 21.4478 |  |  | 0.70203 | -0.36805 | -40.5166 | 0.59136 | 0.56 | -197.8572 | 15.1014 | 0.031836 | 0.10693 | -0.085068 | 0.11521 | 8.8286 | 9.0588 | 1.9785 | 21.792 | 22.0086 | 22.1884 | 22.2531 | 22.0602 | 21.3716 | 20.1851 | 22.185 | 22.3559 | 22.3988 | 22.3425 | 21.9517 | 21.1849 | 22.2439 | 17.3657 | 17.2454 | 16.2818 | 16.3425 | 16.3645 | 17.0813 | 16.8126 | 22.4002 | 22.1514 | 21.7046 | 22.0862 | 21.7895 | 21.3031 | 21.938 | 21.5173 | 20.8894 | 20.1959 | 29.7896 | 21.4311 | 20.5905 | -0.096125 | -0.20976 | 20.9699 | 22.0654 | 22.362 | 20.1189 | 21.657 | 22.1075 | 21.9516 | 21.7089 | 21.2769 | 21.7763 | 21.4395 | 21.0305 | 23.3827 | 30.0424 | 21.2708 | 21.378 | 20.4626 |  | 20.3181 | 20.527 | 20.2074 | 20.0471 | 20.3047 | 20.9791 |  | 20.7411 |  |  | 20.3229 | 20.3836 | 20.8414 | [5 empty] | 21.9148 | 20.8343 | 21.6464 | 22.0194 | 20.9952 | 21.1439 | 21.7587 | 19.7459 | 20.839 | 47.4949 |  | 20.237 | 25.1954 | 18.9952 | 20.008 | 29.2835 | 20.0798 | 21.1516 | 19.1378 | 20.6641 | 19.233 | 21.1713 | 18.9927 | 20.5185 | 24.4521 | 19.8818 | 20.2386 | 34.9749 | 19.0531 | 20.2387 | 29.027 | 19.1666 | 21.0042 | 19.6662 | 21.4927 | 19.1078 | 21.5102 | -0.12535 | 20.9443 | 0.051129 | 0.01632 | -27.1108 | 3.0955 | -15.16 | 62.18 | 1.0349 | -0.72002 | -7.5546 | 0.91268 | 0.88941 | -16.7181 | 4.6187 | 0.41654 | 0.41105 | 0.42764 | 0.37071 | 0.4598 | 0.38503 | 0.4089
42838.4205 | 21 | 22.9003 | 22.8635 | 22.8627 | 22.7749 | 22.4014 | 21.7329 | 22.7205 | 21.7944 | 22.369 | 22.37 | 22.3468 | 22.0066 | 21.2314 | 22.1908 | 21.5835 | 21.7624 | 21.896 | 21.0761 | 21.1688 | 21.385 | 20.4684 | 20.6041 | 20.8945 | 21.8687 | 21.6321 | 21.2555 | 28.4065 | 27.5421 | 43.2118 | 22.0811 | 21.6723 | 21.1934 | 21.9965 | 21.7347 | 21.3459 | 20.0579 | 44.2753 |  | 21.5933 | 22.3355 | 24.402 | 21.1793 |  | 16.9244 | 16.8787 | 16.6015 | 16.7769 | 16.8729 | 17.7659 | 18.9651 | 15.6419 | 17.0049 | 16.1014 | 17.0006 | 18.0082 | 45.0071 | 48.3878 | 44.2275 | 21.4476 |  |  | 0.57981 | -0.42851 | -40.1716 | 0.47242 | 0.43317 | -197.8493 | 14.6605 | 0.1856 | 0.033759 | 0.04291 | 0.016783 | 8.829 | 9.0592 | 1.9785 | 21.8034 | 22.0064 | 22.1901 | 22.2531 | 22.0622 | 21.3746 | 20.1804 | 22.1926 | 22.3545 | 22.3913 | 22.3382 | 21.961 | 21.189 | 22.2585 | 17.339 | 17.2381 | 16.2631 | 16.323 | 16.3593 | 17.0838 | 16.8125 | 22.4059 | 22.1456 | 21.7034 | 22.0845 | 21.7984 | 21.2988 | 21.9451 | 21.5176 | 20.8938 | 20.2008 | 30.3033 | 21.527 | 20.6616 | 0.0043374 | -0.112 | 20.9795 | 22.0592 | 22.3632 | 20.1115 | 21.648 | 22.1007 | 21.9399 | 21.7018 | 21.2741 | 21.7757 | 21.4379 | 21.0315 | 23.767 | 30.8428 | 21.4628 | 21.5505 | 20.5932 |  | 20.3201 | 20.5587 | 20.2059 | 20.0687 | 20.3203 | 21.315 |  | 20.7951 |  |  | 20.3185 | 20.394 | 20.8524 | [5 empty] | 21.9113 | 20.8623 | 21.645 | 22.0193 | 21.0645 | 21.1448 | 21.7612 | 19.7532 | 20.8832 | 48.8306 |  | 20.2602 | 25.6017 | 18.9902 | 20.0247 | 30.0269 | 20.1154 | 21.2065 | 19.146 | 20.7431 | 19.2456 | 21.3776 | 18.9919 | 20.5365 | 25.0132 | 19.8883 | 20.2558 | 35.7907 | 19.0604 | 20.2507 | 29.5658 | 19.1713 | 21.0571 | 19.6801 | 21.4947 | 19.1065 | 21.5074 | -0.11978 | 20.9453 | 0.050883 | 0.015957 | -27.0889 | 3.0955 | -21.15 | 60.63 | 0.94384 | -0.7769 | -7.5222 | 0.81574 | 0.78231 | -16.7193 | 4.5512 | 0.41298 | 0.41012 | 0.42756 | 0.37397 | 0.46187 | 0.38792 | 0.40709
42838.4205 | 22 | 22.8976 | 22.8653 | 22.8549 | 22.7768 | 22.4051 | 21.7303 | 22.7163 | 21.7862 | 22.3634 | 22.3656 | 22.3398 | 22.0053 | 21.2188 | 22.191 | 21.5944 | 21.7694 | 21.8898 | 21.0837 | 21.1772 | 21.3854 | 20.4742 | 20.6042 | 20.8984 | 21.8727 | 21.6371 | 21.2582 | 29.2823 | 28.0797 | 45.0235 | 22.0815 | 21.6799 | 21.1878 | 22.0044 | 21.734 | 21.3467 | 20.0675 | 46.2195 |  | 21.7036 | 22.7509 | 24.9352 | 21.1146 |  | 16.9254 | 16.8849 | 16.5976 | 16.7691 | 16.9009 | 17.9571 | 19.3637 | 15.6481 | 17.0106 | 16.1559 | 17.0043 | 18.0021 | 45.002 | 48.3873 | 44.2448 | 21.4491 |  |  | 0.60215 | -0.55993 | -40.4759 | 0.42379 | 0.3484 | -197.8118 | 14.3996 | 0.19414 | -0.079109 | -0.026953 | -0.078697 | 8.829 | 9.0586 | 1.9789 | 21.7968 | 22.0011 | 22.1897 | 22.2532 | 22.0676 | 21.3729 | 20.1816 | 22.1817 | 22.3537 | 22.3909 | 22.3374 | 21.9587 | 21.1852 | 22.2487 | 17.3248 | 17.223 | 16.249 | 16.3032 | 16.3729 | 17.0878 | 16.8089 | 22.4042 | 22.1427 | 21.6932 | 22.0783 | 21.7903 | 21.2918 | 21.9369 | 21.5201 | 20.885 | 20.2046 | 31.0531 | 21.6976 | 20.7279 | 0.063317 | -0.22669 | 20.9923 | 22.0632 | 22.3627 | 20.1161 | 21.6463 | 22.1013 | 21.9335 | 21.701 | 21.273 | 21.7754 | 21.4409 | 21.0342 | 24.2231 | 31.8113 | 21.758 | 21.8108 | 20.7196 |  | 20.3282 | 20.5482 | 20.2051 | 20.0876 | 20.3364 | 21.3231 |  | 20.842 |  |  | 20.3155 | 20.3969 | 20.8746 | [5 empty] | 21.9129 | 20.8903 | 21.6465 | 22.0279 | 21.1337 | 21.1469 | 21.7648 | 19.7537 | 20.9271 | 50.2622 |  | 20.2673 | 26.1095 | 18.9821 | 20.0369 | 30.656 | 20.1486 | 21.2439 | 19.1498 | 20.8571 | 19.2441 | 21.4564 | 19.001 | 20.5545 | 25.5579 | 19.9162 | 20.2821 | 36.6013 | 19.0699 | 20.2644 | 30.1754 | 19.1762 | 21.0785 | 19.7028 | 21.5107 | 19.1203 | 21.5153 | 0.028805 | 20.945 | 0.050337 | 0.01423 | -27.1472 | 3.0955 | -18.39 | 58.77 | 0.96461 | -0.88809 | -7.5508 | 0.77263 | 0.70183 | -16.7232 | 4.512 | 0.40974 | 0.41038 | 0.42757 | 0.37601 | 0.46301 | 0.39004 | 0.40537
42838.4205 | 23 | 22.9092 | 22.8707 | 22.8605 | 22.7854 | 22.4087 | 21.7329 | 22.7156 | 21.7929 | 22.3594 | 22.3761 | 22.3504 | 22.0075 | 21.2264 | 22.1925 | 21.598 | 21.7693 | 21.8926 | 21.0891 | 21.176 | 21.3948 | 20.4692 | 20.6053 | 20.9002 | 21.8684 | 21.6367 | 21.2558 | 30.0731 | 28.5849 | 46.5022 | 22.0745 | 21.6735 | 21.1901 | 21.9961 | 21.7347 | 21.3453 | 20.0719 | 47.5995 |  | 21.7952 | 23.1261 | 25.4812 | 21.0423 |  | 16.9303 | 16.875 | 16.5912 | 16.7664 | 16.9264 | 18.076 | 19.7169 | 15.6433 | 17.0031 | 16.1654 | 17.0044 | 18.0077 | 45.0058 | 48.3833 | 44.2616 | 21.4532 |  |  | 0.57652 | -0.19917 | -40.0165 | 0.27726 | 0.47194 | -197.9084 | 14.468 | -0.047016 | 0.0575 | -0.14507 | 0.051156 | 8.8283 | 9.0581 | 1.9787 | 21.8041 | 22.0042 | 22.198 | 22.2589 | 22.0711 | 21.3834 | 20.1885 | 22.1907 | 22.3596 | 22.3963 | 22.3462 | 21.9659 | 21.1954 | 22.2563 | 17.2934 | 17.2148 | 16.2202 | 16.2754 | 16.3614 | 17.0977 | 16.811 | 22.4078 | 22.1496 | 21.7007 | 22.0849 | 21.7838 | 21.2946 | 21.9303 | 21.5071 | 20.882 | 20.2154 | 31.8677 | 21.7375 | 20.7781 | 0.0049272 | -0.092596 | 21.0195 | 22.0671 | 22.3664 | 20.1208 | 21.6538 | 22.1108 | 21.9451 | 21.7071 | 21.2726 | 21.7797 | 21.44 | 21.0419 | 24.7485 | 32.6987 | 22.1154 | 22.1636 | 20.8392 |  | 20.3377 | 20.5551 | 20.2129 | 20.1397 | 20.344 | 21.4566 |  | 20.8952 |  |  | 20.3203 | 20.4022 | 20.8934 | [5 empty] | 21.9154 | 20.925 | 21.6517 | 22.0281 | 21.2015 | 21.1484 | 21.7637 | 19.7593 | 20.9739 | 51.7733 |  | 20.2842 | 26.6448 | 18.9866 | 20.0564 | 31.1335 | 20.186 | 21.2905 | 19.1626 | 20.9977 | 19.2465 | 21.4601 | 19.008 | 20.5666 | 26.0684 | 19.9403 | 20.3082 | 37.4126 | 19.0715 | 20.273 | 30.7551 | 19.1815 | 21.0923 | 19.7177 | 21.5297 | 19.1332 | 21.5302 | -0.11607 | 20.9446 | 0.050171 | 0.013489 | -27.1206 | 3.0955 | -18.58 | 58.43 | 0.94605 | -0.52966 | -7.5077 | 0.62492 | 0.81701 | -16.7307 | 4.5236 | 0.40674 | 0.41045 | 0.42638 | 0.38066 | 0.46645 | 0.39219 | 0.40434
42838.4206 | 24 | 22.9117 | 22.8623 | 22.8585 | 22.7851 | 22.401 | 21.7309 | 22.7188 | 21.7895 | 22.3644 | 22.378 | 22.3462 | 22.0127 | 21.2261 | 22.1935 | 21.5959 | 21.7672 | 21.8934 | 21.0843 | 21.1831 | 21.4003 | 20.4667 | 20.6067 | 20.8961 | 21.8801 | 21.6402 | 21.2587 | 30.8355 | 29.0726 | 47.6238 | 22.0803 | 21.6752 | 21.1956 | 21.9931 | 21.736 | 21.3454 | 20.0787 | 48.7384 |  | 21.9024 | 23.5332 | 26.0252 | 20.9947 |  | 16.9417 | 16.8787 | 16.5983 | 16.7659 | 16.9373 | 18.1502 | 19.9799 | 15.6671 | 17.0097 | 16.2001 | 17.0168 | 18.0024 | 45.0162 | 48.3892 | 44.2656 | 21.452 |  |  | 0.50292 | -0.40025 | -39.958 | 0.29894 | 0.19727 | -197.8847 | 14.8892 | 0.006868 | 0.046019 | 0.054659 | 0.052198 | 8.8288 | 9.0586 | 1.9787 | 21.7997 | 22.0032 | 22.1963 | 22.2523 | 22.0694 | 21.378 | 20.1922 | 22.1864 | 22.3576 | 22.3953 | 22.3422 | 21.9626 | 21.187 | 22.2485 | 17.2558 | 17.168 | 16.1936 | 16.2427 | 16.3366 | 17.0877 | 16.8042 | 22.4031 | 22.1509 | 21.6982 | 22.0795 | 21.791 | 21.294 | 21.9294 | 21.5142 | 20.8884 | 20.2249 | 32.354 | 21.768 | 20.8358 | -0.056019 | -0.20348 | 21.0371 | 22.0664 | 22.3601 | 20.1166 | 21.6522 | 22.1049 | 21.9418 | 21.7004 | 21.2734 | 21.7729 | 21.4365 | 21.0375 | 25.2585 | 33.6109 | 22.4404 | 22.472 | 20.9513 |  | 20.3433 | 20.5797 | 20.2262 | 20.1919 | 20.3605 | 21.9514 |  | 20.9769 |  |  | 20.322 | 20.4015 | 20.9084 | [5 empty] | 21.9142 | 20.9493 | 21.6515 | 22.0228 | 21.2501 | 21.1477 | 21.764 | 19.7712 | 21.0175 | 52.9127 |  | 20.3001 | 27.1012 | 18.9944 | 20.0741 | 31.5688 | 20.2229 | 21.3289 | 19.1788 | 21.1325 | 19.2561 | 21.4837 | 18.9986 | 20.5689 | 26.536 | 19.9495 | 20.3249 | 37.9628 | 19.0712 | 20.279 | 31.3587 | 19.1776 | 21.0921 | 19.7295 | 21.5323 | 19.133 | 21.5316 | -0.28321 | 20.9449 | 0.050349 | 0.014215 | -27.0827 | 3.0955 | -13.8 | 55.47 | 0.88515 | -0.75085 | -7.5022 | 0.6489 | 0.52828 | -16.7318 | 4.5896 | 0.40381 | 0.41021 | 0.42549 | 0.38367 | 0.46862 | 0.39374 | 0.40306
42838.4206 | 25 | 22.9061 | 22.8631 | 22.8469 | 22.7721 | 22.391 | 21.7303 | 22.7112 | 21.7871 | 22.361 | 22.369 | 22.3425 | 22.006 | 21.2282 | 22.1844 | 21.589 | 21.7632 | 21.8953 | 21.0838 | 21.1845 | 21.3952 | 20.4696 | 20.6062 | 20.8986 | 21.8708 | 21.6311 | 21.2541 | 31.4719 | 29.571 | 48.0577 | 22.0827 | 21.6822 | 21.1903 | 21.9966 | 21.7426 | 21.3506 | 20.0855 | 49.845 |  | 22.0234 | 23.8928 | 26.3402 | 20.9635 |  | 16.9235 | 16.8637 | 16.5809 | 16.7493 | 16.9228 | 18.2199 | 20.1746 | 15.7045 | 17.0086 | 16.2239 | 17.0089 | 18.0071 | 45.0188 | 48.3857 | 44.2854 | 21.4514 |  |  | 0.47598 | -0.29642 | -40.0487 | 0.47242 | 0.38454 | -197.8171 | 14.5672 | -0.18172 | 0.029283 | -0.11402 | -0.0089096 | 8.8287 | 9.0585 | 1.978 | 21.8003 | 21.9984 | 22.1877 | 22.2484 | 22.0685 | 21.3734 | 20.1874 | 22.1826 | 22.3585 | 22.384 | 22.34 | 21.9624 | 21.1874 | 22.2515 | 17.23 | 17.1553 | 16.1717 | 16.2505 | 16.3084 | 17.0877 | 16.8069 | 22.4056 | 22.1499 | 21.7045 | 22.0881 | 21.7948 | 21.2929 | 21.9389 | 21.5202 | 20.893 | 20.2395 | 32.7448 | 21.8014 | 20.8928 | -0.02358 | -0.072435 | 21.0903 | 22.0622 | 22.3568 | 20.1123 | 21.6492 | 22.1035 | 21.9352 | 21.6979 | 21.2689 | 21.7749 | 21.4406 | 21.0301 | 25.7475 | 34.3507 | 22.7406 | 22.7649 | 21.0183 |  | 20.3518 | 20.6573 | 20.2341 | 20.2295 | 20.3753 | 21.9025 |  | 21.0309 |  |  | 20.3216 | 20.4051 | 20.9298 | [5 empty] | 21.9111 | 20.982 | 21.6542 | 22.0213 | 21.3049 | 21.1452 | 21.7579 | 19.7776 | 21.0602 | 53.6412 |  | 20.3201 | 27.5612 | 18.9867 | 20.0803 | 32.1055 | 20.2516 | 21.3667 | 19.1865 | 21.2405 | 19.2653 | 21.5367 | 18.9936 | 20.5814 | 27.0286 | 19.9556 | 20.3419 | 38.7105 | 19.0748 | 20.2882 | 31.9997 | 19.1729 | 21.1035 | 19.7382 | 21.5375 | 19.1349 | 21.5421 | -0.15966 | 20.9437 | 0.050251 | 0.014593 | -27.0245 | 3.0955 | -35.85 | 55.03 | 0.8617 | -0.64615 | -7.5105 | 0.81572 | 0.73767 | -16.731 | 4.5402 | 0.40224 | 0.40832 | 0.42494 | 0.38653 | 0.47137 | 0.39484 | 0.40196
42838.4206 | 26 | 22.8954 | 22.869 | 22.8552 | 22.775 | 22.4014 | 21.7331 | 22.7071 | 21.7875 | 22.3579 | 22.3713 | 22.3446 | 22.01 | 21.2254 | 22.196 | 21.5856 | 21.7623 | 21.8905 | 21.0801 | 21.177 | 21.3917 | 20.4599 | 20.6021 | 20.8963 | 21.865 | 21.6328 | 21.2494 | 31.9588 | 30.0189 | 48.1767 | 22.0814 | 21.683 | 21.1937 | 22.0007 | 21.7443 | 21.3442 | 20.0954 | 51.3779 |  | 22.1444 | 24.2888 | 26.8148 | 20.9265 |  | 16.9169 | 16.8569 | 16.58 | 16.749 | 16.9213 | 18.263 | 20.3152 | 15.7194 | 17.0087 | 16.269 | 17.0092 | 18.0065 | 45.0287 | 48.3801 | 44.3027 | 21.4547 |  |  | 0.63435 | -0.38842 | -39.684 | 0.31471 | 0.4312 | -197.8184 | 14.7696 | -0.008248 | -0.091174 | 0.15201 | -0.019152 | 8.8288 | 9.0587 | 1.9769 | 21.7994 | 22.0006 | 22.1885 | 22.2457 | 22.067 | 21.3702 | 20.1893 | 22.1792 | 22.3556 | 22.3826 | 22.3358 | 21.9552 | 21.1908 | 22.2482 | 17.2645 | 17.1664 | 16.1724 | 16.305 | 16.3247 | 17.0926 | 16.8104 | 22.399 | 22.1503 | 21.6999 | 22.0832 | 21.7934 | 21.2845 | 21.9306 | 21.5124 | 20.8778 | 20.2363 | 33.28 | 22.0996 | 20.9421 | -0.019058 | -0.16202 | 21.2625 | 22.0629 | 22.3684 | 20.1072 | 21.6514 | 22.1126 | 21.9373 | 21.7022 | 21.2695 | 21.7772 | 21.4431 | 21.0342 | 26.189 | 34.9544 | 23.0382 | 23.0503 | 21.0512 |  | 20.3454 | 20.9189 | 20.2465 | 20.2701 | 20.3901 | 21.8842 |  | 21.0839 |  |  | 20.3209 | 20.4019 | 20.9473 | [5 empty] | 21.9113 | 21.0015 | 21.6509 | 22.0202 | 21.3508 | 21.1452 | 21.7568 | 19.7896 | 21.1041 | 54.4604 |  | 20.3388 | 28.0278 | 18.9852 | 20.0969 | 32.8121 | 20.2843 | 21.4091 | 19.2 | 21.3341 | 19.2779 | 21.5738 | 18.9975 | 20.61 | 27.6007 | 19.9705 | 20.3598 | 39.5745 | 19.0807 | 20.3007 | 32.7237 | 19.1691 | 21.146 | 19.7618 | 21.5567 | 19.1362 | 21.5508 | -0.13629 | 20.9448 | 0.049962 | 0.014302 | -27.1114 | 3.0955 | -8.77 | 53.39 | 0.99496 | -0.73964 | -7.4762 | 0.66578 | 0.7812 | -16.7323 | 4.572 | 0.40111 | 0.40147 | 0.42431 | 0.38328 | 0.47171 | 0.3962 | 0.40048
42838.4206 | 27 | 22.9053 | 22.8723 | 22.8629 | 22.7804 | 22.4065 | 21.743 | 22.7215 | 21.7927 | 22.3694 | 22.3714 | 22.3477 | 22.0153 | 21.2288 | 22.2027 | 21.5923 | 21.7641 | 21.8974 | 21.0815 | 21.1773 | 21.3946 | 20.4685 | 20.6087 | 20.9051 | 21.8735 | 21.6353 | 21.2576 | 32.4954 | 30.4513 | 48.7993 | 22.0776 | 21.6735 | 21.1855 | 22.001 | 21.7346 | 21.3417 | 20.0911 | 52.5028 |  | 22.2657 | 24.799 | 27.4135 | 20.8881 |  | 16.9206 | 16.8676 | 16.5784 | 16.7576 | 16.9261 | 18.2543 | 20.4112 | 15.8 | 17.019 | 16.2997 | 17.0242 | 18.0068 | 45.0304 | 48.3679 | 44.3086 | 21.4605 |  |  | 0.46218 | -0.27934 | -39.3298 | 0.5907 | 0.16572 | -197.8617 | 14.9312 | -0.034532 | -0.16629 | -0.15409 | 0.0053256 | 8.8284 | 9.0581 | 1.9767 | 21.7949 | 21.9999 | 22.1852 | 22.2463 | 22.0648 | 21.3713 | 20.1863 | 22.1858 | 22.3585 | 22.3793 | 22.3333 | 21.9519 | 21.1848 | 22.2425 | 17.4605 | 17.1789 | 16.2223 | 16.3608 | 16.362 | 17.1092 | 16.8127 | 22.4162 | 22.1514 | 21.6931 | 22.0848 | 21.7952 | 21.2925 | 21.9433 | 21.5167 | 20.8893 | 20.2522 | 33.9781 | 22.2653 | 20.9882 | -0.11284 | -0.19968 | 21.421 | 22.0567 | 22.3553 | 20.1067 | 21.6482 | 22.1086 | 21.9311 | 21.703 | 21.262 | 21.7687 | 21.4324 | 21.0233 | 26.505 | 35.6288 | 23.3248 | 23.3125 | 21.1032 |  | 20.3668 | 21.6588 | 20.2873 | 20.3434 | 20.41 | 21.9323 |  | 21.1619 |  |  | 20.3305 | 20.4138 | 20.9503 | [5 empty] | 21.9152 | 21.0295 | 21.6546 | 22.0235 | 21.3998 | 21.1416 | 21.7619 | 19.794 | 21.1381 | 55.0904 |  | 20.374 | 28.5178 | 18.9854 | 20.0876 | 33.3664 | 20.3183 | 21.4393 | 19.2039 | 21.4138 | 19.2769 | 21.5793 | 18.9966 | 20.6329 | 28.092 | 19.9861 | 20.3764 | 40.1263 | 19.0773 | 20.3033 | 33.4289 | 19.1853 | 21.2386 | 19.7736 | 21.5789 | 19.1441 | 21.5614 | -0.038531 | 20.9452 | 0.049304 | 0.013961 | -27.1235 | 3.0955 | -15.86 | 51.44 | 0.85009 | -0.62726 | -7.4429 | 0.91214 | 0.48429 | -16.7339 | 4.5969 | 0.40038 | 0.38228 | 0.42294 | 0.36343 | 0.46642 | 0.39712 | 0.39973
42838.4206 | 28 | 22.9097 | 22.8681 | 22.8576 | 22.7823 | 22.4065 | 21.7379 | 22.7195 | 21.7958 | 22.3632 | 22.3712 | 22.3468 | 22.0152 | 21.2244 | 22.1967 | 21.5856 | 21.7634 | 21.8895 | 21.0778 | 21.1732 | 21.391 | 20.4728 | 20.6107 | 20.9045 | 21.8755 | 21.6267 | 21.25 | 33.2267 | 30.9678 | 49.8851 | 22.0777 | 21.6806 | 21.1874 | 22.0081 | 21.7332 | 21.3421 | 20.0994 | 53.1925 |  | 22.401 | 25.4073 | 27.9027 | 20.8419 |  | 16.9098 | 16.86 | 16.5691 | 16.7483 | 16.9105 | 18.205 | 20.4099 | 15.885 | 17.0095 | 16.2781 | 17.0183 | 18.007 | 45.0422 | 48.3605 | 44.3137 | 21.4556 |  |  | 0.51147 | -0.37791 | -38.973 | 0.29697 | 0.13287 | -197.8348 | 14.7229 | -0.12127 | 0.0074882 | -0.29298 | -0.024881 | 8.8288 | 9.0586 | 1.9774 | 21.8029 | 22.0098 | 22.1931 | 22.2519 | 22.0683 | 21.3849 | 20.1856 | 22.1906 | 22.3715 | 22.3988 | 22.3458 | 21.9533 | 21.1878 | 22.2497 | 17.663 | 17.2458 | 16.2694 | 16.4056 | 16.4028 | 17.1137 | 16.8133 | 22.4058 | 22.1532 | 21.6925 | 22.0896 | 21.7921 | 21.2984 | 21.9425 | 21.5167 | 20.8894 | 20.2583 | 34.46 | 22.2953 | 21.031 | -0.087671 | -0.12759 | 21.5762 | 22.0651 | 22.357 | 20.1105 | 21.6536 | 22.1026 | 21.9376 | 21.7038 | 21.2743 | 21.7755 | 21.4298 | 21.0262 | 26.9446 | 36.456 | 23.6218 | 23.6001 | 21.1245 |  | 20.3648 | 22.5007 | 20.309 | 20.3706 | 20.4251 | 21.9388 |  | 21.224 |  |  | 20.3437 | 20.4319 | 20.9582 | [5 empty] | 21.9081 | 21.0542 | 21.6529 | 22.0273 | 21.4348 | 21.1427 | 21.7598 | 19.8097 | 21.1883 | 55.8192 |  | 20.4555 | 29.019 | 18.9975 | 20.1012 | 34.0115 | 20.36 | 21.4814 | 19.23 | 21.53 | 19.2899 | 21.6181 | 18.9903 | 20.6578 | 28.6246 | 19.994 | 20.3991 | 40.6315 | 19.0738 | 20.3095 | 33.9916 | 19.1859 | 21.5058 | 19.78 | 21.9137 | 19.149 | 21.5738 | -0.070808 | 20.9447 | 0.050023 | 0.013475 | -27.0776 | 3.0956 | -15.11 | 52.21 | 0.89578 | -0.72957 | -7.4089 | 0.64674 | 0.4336 | -16.7313 | 4.5643 | 0.39972 | 0.35963 | 0.42269 | 0.34145 | 0.46125 | 0.39868 | 0.39875
42838.4206 | 29 | 22.9055 | 22.8708 | 22.8517 | 22.7748 | 22.4074 | 21.742 | 22.718 | 21.7912 | 22.3666 | 22.3651 | 22.345 | 22.0143 | 21.221 | 22.1928 | 21.5947 | 21.7629 | 21.8961 | 21.0771 | 21.1802 | 21.3976 | 20.4755 | 20.609 | 20.8991 | 21.8716 | 21.6335 | 21.2604 | 33.7794 | 31.4987 | 50.7407 | 22.0804 | 21.6789 | 21.1887 | 22.0004 | 21.7346 | 21.3492 | 20.1103 | 53.8663 |  | 22.5306 | 25.978 | 28.3663 | 20.7884 |  | 16.9071 | 16.85 | 16.5655 | 16.7432 | 16.8951 | 18.1745 | 20.4198 | 16.001 | 17.0153 | 16.2714 | 17.0154 | 18.0083 | 45.0489 | 48.3584 | 44.2969 | 21.4589 |  |  | 0.4313 | -0.42719 | -38.3612 | 0.6459 | 0.33789 | -197.8545 | 14.8945 | 0.023296 | 0.18633 | -0.10227 | 0.0002912 | 8.8285 | 9.0584 | 1.9778 | 21.7949 | 22.0092 | 22.1837 | 22.2544 | 22.0636 | 21.3792 | 20.1792 | 22.1861 | 22.3547 | 22.3896 | 22.3399 | 21.9563 | 21.186 | 22.2408 | 17.7864 | 17.3753 | 16.3289 | 16.4334 | 16.4418 | 17.1123 | 16.8074 | 22.407 | 22.1488 | 21.6962 | 22.0852 | 21.7926 | 21.2958 | 21.9387 | 21.5133 | 20.8902 | 20.2658 | 34.7518 | 22.3093 | 21.085 | 0.034024 | -0.1508 | 21.7317 | 22.0698 | 22.3641 | 20.1159 | 21.6569 | 22.1032 | 21.9384 | 21.7057 | 21.2743 | 21.7781 | 21.426 | 21.0287 | 27.5085 | 37.1808 | 23.9191 | 23.8688 | 21.1485 |  | 20.3745 | 23.3557 | 20.3356 | 20.3999 | 20.4408 | 21.9297 |  | 21.2785 |  |  | 20.3402 | 20.4341 | 20.9707 | [5 empty] | 21.9074 | 21.0715 | 21.6494 | 22.0311 | 21.4844 | 21.1416 | 21.7595 | 19.822 | 21.242 | 56.9205 |  | 20.5438 | 29.4277 | 18.9974 | 20.1048 | 34.6957 | 20.3965 | 21.527 | 19.2466 | 21.6851 | 19.2989 | 21.6377 | 19.0019 | 20.7442 | 29.1167 | 20.0042 | 20.4095 | 41.1275 | 19.0674 | 20.3256 | 34.4536 | 19.2038 | 21.9087 | 19.7984 | 22.4403 | 19.138 | 21.5887 | -0.06784 | 20.945 | 0.049999 | 0.014121 | -27.1232 | 3.0955 | -6.73 | 51.78 | 0.82367 | -0.77567 | -7.3504 | 0.95378 | 0.69142 | -16.7313 | 4.5906 | 0.39938 | 0.33677 | 0.4224 | 0.32758 | 0.45395 | 0.40053 | 0.39751
42838.4206 | 30 | 22.9097 | 22.8659 | 22.8608 | 22.7776 | 22.4009 | 21.7397 | 22.7159 | 21.7966 | 22.3743 | 22.374 | 22.3483 | 22.0115 | 21.2264 | 22.2044 | 21.5866 | 21.7575 | 21.884 | 21.0722 | 21.1707 | 21.3856 | 20.4647 | 20.5966 | 20.8933 | 21.8755 | 21.6316 | 21.2467 | 34.239 | 32.0002 | 51.6075 | 22.0821 | 21.6791 | 21.1906 | 21.9959 | 21.731 | 21.3443 | 20.1103 | 54.5326 |  | 22.6573 | 26.4166 | 28.9956 | 20.7473 |  | 16.8866 | 16.8371 | 16.5508 | 16.7196 | 16.8841 | 18.131 | 20.4837 | 16.0499 | 17.0076 | 16.2352 | 17.0178 | 18.0061 | 45.0586 | 48.3555 | 44.2954 | 21.4565 |  |  | 0.44444 | -0.37528 | -38.9717 | 0.49739 | 0.17032 | -197.8703 | 14.8327 | -0.31906 | 0.1511 | -0.23424 | -0.083905 | 8.8289 | 9.0588 | 1.978 | 21.791 | 22.0056 | 22.1826 | 22.2468 | 22.0567 | 21.3712 | 20.1719 | 22.1763 | 22.3493 | 22.3777 | 22.3316 | 21.9556 | 21.1781 | 22.2356 | 17.9512 | 17.3951 | 16.4279 | 16.4584 | 16.4492 | 17.1151 | 16.8116 | 22.404 | 22.1565 | 21.6948 | 22.0834 | 21.7969 | 21.3011 | 21.9386 | 21.5208 | 20.8924 | 20.2715 | 35.1635 | 22.3398 | 21.1352 | -0.15511 | -0.24362 | 21.8474 | 22.0621 | 22.3625 | 20.1187 | 21.659 | 22.0993 | 21.9381 | 21.711 | 21.2693 | 21.7766 | 21.4365 | 21.0335 | 27.975 | 37.6333 | 24.2255 | 24.1483 | 21.152 |  | 20.3752 | 24.1984 | 20.3375 | 20.4181 | 20.4511 | 22.0027 |  | 21.3484 |  |  | 20.3581 | 20.4479 | 20.9733 | [5 empty] | 21.9141 | 21.0931 | 21.6469 | 22.0215 | 21.5356 | 21.1374 | 21.7525 | 19.8444 | 21.2801 | 57.5543 |  | 20.6318 | 29.7591 | 19.0133 | 20.125 | 35.4067 | 20.4429 | 21.5859 | 19.2591 | 21.8959 | 19.3144 | 21.6486 | 19.0044 | 20.9875 | 29.7337 | 20.0239 | 20.444 | 41.8411 | 19.0848 | 20.3476 | 34.9737 | 19.2208 | 22.2743 | 19.8225 | 22.6048 | 19.1484 | 21.6114 | -0.12108 | 20.9434 | 0.050435 | 0.014179 | -27.0576 | 3.0955 | -14.25 | 51.37 | 0.83725 | -0.727 | -7.4085 | 0.83696 | 0.49086 | -16.7307 | 4.5807 | 0.39931 | 0.31342 | 0.42224 | 0.30959 | 0.44344 | 0.40168 | 0.3963
42838.4206 | 31 | 22.9023 | 22.8733 | 22.8603 | 22.78 | 22.4075 | 21.746 | 22.7213 | 21.7923 | 22.3623 | 22.3655 | 22.3501 | 22.0165 | 21.223 | 22.1927 | 21.5872 | 21.758 | 21.8916 | 21.0781 | 21.1708 | 21.3873 | 20.4658 | 20.6021 | 20.8964 | 21.873 | 21.6276 | 21.2485 | 34.8108 | 32.4855 | 52.5846 | 22.0817 | 21.6822 | 21.1853 | 21.9968 | 21.7358 | 21.3493 | 20.1181 | 54.7709 |  | 22.7727 | 26.7584 | 29.6633 | 20.7535 |  | 16.8911 | 16.8361 | 16.5508 | 16.7203 | 16.8851 | 18.0921 | 20.5501 | 16.0382 | 17.0152 | 16.1855 | 17.0253 | 18.0094 | 45.0705 | 48.3536 | 44.2924 | 21.4574 |  |  | 0.33733 | -0.24057 | -39.1222 | 0.41788 | 0.20055 | -197.8269 | 14.8531 | -0.34075 | -0.16493 | -0.35592 | -0.043282 | 8.8287 | 9.0586 | 1.9781 | 21.8002 | 22.0135 | 22.1965 | 22.2582 | 22.0644 | 21.3795 | 20.1842 | 22.1889 | 22.3601 | 22.3917 | 22.3427 | 21.9623 | 21.1907 | 22.2484 | 18.1809 | 17.3777 | 16.4594 | 16.4786 | 16.4754 | 17.1293 | 16.8129 | 22.4156 | 22.1608 | 21.6956 | 22.0879 | 21.7944 | 21.296 | 21.9388 | 21.5179 | 20.8932 | 20.2832 | 36.0844 | 22.5128 | 21.175 | -0.14665 | -0.26359 | 21.9614 | 22.0738 | 22.3673 | 20.1195 | 21.6574 | 22.0971 | 21.9385 | 21.7146 | 21.2753 | 21.7779 | 21.442 | 21.0349 | 28.4328 | 37.9688 | 24.5214 | 24.4545 | 21.198 |  | 20.3846 | 24.6842 | 20.3576 | 20.4278 | 20.4691 | 22.1435 |  | 21.4151 |  |  | 20.373 | 20.4633 | 20.9955 | [5 empty] | 21.9169 | 21.1113 | 21.651 | 22.0184 | 21.5794 | 21.1473 | 21.7598 | 19.8463 | 21.3205 | 58.9335 |  | 20.6765 | 30.09 | 19.0026 | 20.1202 | 35.8364 | 20.4561 | 21.6247 | 19.2634 | 22.0982 | 19.3122 | 21.6573 | 19.0096 | 21.1926 | 30.2736 | 20.0374 | 20.4567 | 42.4627 | 19.0902 | 20.3522 | 35.4167 | 19.2433 | 22.5133 | 19.8337 | 22.5874 | 19.1634 | 21.6309 | -0.16634 | 20.9449 | 0.050324 | 0.013489 | -26.99 | 3.0955 | 4.01 | 53.1 | 0.73051 | -0.58207 | -7.4228 | 0.76715 | 0.53261 | -16.7277 | 4.5835 | 0.39835 | 0.3006 | 0.42257 | 0.28573 | 0.4401 | 0.40176 | 0.39559
42838.4206 | 32 | 22.9073 | 22.8735 | 22.8619 | 22.7793 | 22.4021 | 21.7348 | 22.7185 | 21.8 | 22.3734 | 22.3712 | 22.3494 | 22.0163 | 21.22 | 22.1968 | 21.5929 | 21.7676 | 21.8923 | 21.0849 | 21.1813 | 21.3838 | 20.4683 | 20.6091 | 20.9014 | 21.8788 | 21.6323 | 21.2511 | 35.2763 | 32.9544 | 52.8223 | 22.0777 | 21.6702 | 21.1872 | 21.996 | 21.7261 | 21.3426 | 20.1232 | 54.4204 |  | 22.8886 | 27.0285 | 30.2058 | 20.782 |  | 16.8881 | 16.8333 | 16.5262 | 16.7062 | 16.8623 | 18.0531 | 20.6331 | 15.9634 | 17.0143 | 16.1462 | 17.0256 | 18.0099 | 45.0576 | 48.3553 | 44.2932 | 21.4576 |  |  | 0.46481 | -0.30891 | -38.8764 | 0.37451 | 0.29452 | -197.7763 | 15.0055 | -0.35718 | 0.051662 | -0.29927 | 0.12198 | 8.8283 | 9.0585 | 1.978 | 21.8028 | 22.0115 | 22.1971 | 22.2459 | 22.0643 | 21.3743 | 20.1795 | 22.1836 | 22.3589 | 22.3934 | 22.3429 | 21.9516 | 21.1842 | 22.2439 | 18.3541 | 17.4094 | 16.4681 | 16.4911 | 16.4939 | 17.145 | 16.8205 | 22.4078 | 22.1512 | 21.7062 | 22.0808 | 21.7913 | 21.2926 | 21.9346 | 21.5135 | 20.8799 | 20.2878 | 37.0481 | 22.6715 | 21.223 | -0.15511 | -0.26244 | 22.0469 | 22.0687 | 22.361 | 20.1167 | 21.6626 | 22.1028 | 21.9361 | 21.7084 | 21.2766 | 21.7759 | 21.4338 | 21.0323 | 28.8813 | 38.3546 | 24.7934 | 24.7523 | 21.3078 |  | 20.3926 | 24.5911 | 20.3826 | 20.4427 | 20.4897 | 22.1474 |  | 21.4778 |  |  | 20.3929 | 20.4911 | 21.0197 | [5 empty] | 21.9202 | 21.1469 | 21.6501 | 22.0325 | 21.6411 | 21.1543 | 21.7653 | 19.8533 | 21.3643 | 59.4753 |  | 20.7129 | 30.489 | 19.0151 | 20.1427 | 36.1314 | 20.5073 | 21.6867 | 19.2715 | 22.2677 | 19.3277 | 21.7359 | 19.0085 | 21.275 | 30.7252 | 20.0449 | 20.4894 | 42.7966 | 19.1002 | 20.3688 | 35.8586 | 19.2546 | 22.7079 | 19.8516 | 22.6402 | 19.1674 | 21.6648 | -0.032966 | 20.9458 | 0.050509 | 0.012916 | -27.0784 | 3.0956 | -0.87 | 51.02 | 0.85782 | -0.65958 | -7.3994 | 0.72625 | 0.64539 | -16.7245 | 4.6067 | 0.39556 | 0.30402 | 0.42285 | 0.26831 | 0.44003 | 0.40114 | 0.39441
42838.4207 | 33 | 22.8968 | 22.868 | 22.8519 | 22.774 | 22.3952 | 21.7269 | 22.7124 | 21.7875 | 22.3638 | 22.367 | 22.3404 | 22.0023 | 21.2203 | 22.1865 | 21.6023 | 21.7743 | 21.8982 | 21.0791 | 21.1842 | 21.3971 | 20.4712 | 20.6153 | 20.9047 | 21.8743 | 21.6398 | 21.2577 | 35.7294 | 33.3927 | 53.2773 | 22.0873 | 21.6838 | 21.1956 | 21.9998 | 21.7447 | 21.3517 | 20.1428 | 53.6702 |  | 23.0154 | 27.2605 | 30.5986 | 20.8874 |  | 16.8787 | 16.8238 | 16.5214 | 16.702 | 16.8437 | 18.0392 | 20.9094 | 15.8963 | 17.0207 | 16.1093 | 17.0276 | 18.0075 | 45.0364 | 48.3494 | 44.2938 | 21.4591 |  |  | 0.51015 | -0.36542 | -38.4887 | 0.42379 | 0.61716 | -197.8427 | 15.0883 | -0.18107 | 0.042127 | -0.25501 | 0.13518 | 8.8289 | 9.0587 | 1.9784 | 21.8053 | 22.0075 | 22.1956 | 22.2508 | 22.0734 | 21.3796 | 20.1866 | 22.1868 | 22.3629 | 22.3968 | 22.3505 | 21.9587 | 21.1855 | 22.2459 | 18.5774 | 17.4171 | 16.4653 | 16.4907 | 16.5115 | 17.1648 | 16.8219 | 22.414 | 22.1548 | 21.707 | 22.088 | 21.7914 | 21.2959 | 21.9396 | 21.5188 | 20.8881 | 20.2994 | 37.7117 | 22.8374 | 21.2566 | 0.0017816 | -0.19778 | 22.0903 | 22.0585 | 22.3625 | 20.112 | 21.66 | 22.0966 | 21.9369 | 21.6968 | 21.2704 | 21.7675 | 21.431 | 21.0295 | 29.3213 | 38.7087 | 25.0559 | 25.0403 | 21.5839 |  | 20.4074 | 24.2923 | 20.3884 | 20.4647 | 20.5085 | 22.2339 |  | 21.5237 |  |  | 20.4005 | 20.5081 | 21.0845 | [5 empty] | 21.915 | 21.164 | 21.6557 | 22.025 | 21.6869 | 21.1467 | 21.762 | 19.8674 | 21.41 | 60.247 |  | 20.7304 | 30.9139 | 19.0135 | 20.1693 | 36.4337 | 20.5413 | 21.7362 | 19.2763 | 22.4713 | 19.3386 | 21.9769 | 18.9967 | 21.3195 | 31.0611 | 20.0558 | 20.501 | 43.0415 | 19.0994 | 20.38 | 36.3562 | 19.2605 | 22.875 | 19.8618 | 22.9207 | 19.1698 | 21.7641 | -0.16078 | 20.9457 | 0.051387 | 0.012865 | -27.1147 | 3.0956 | -25.14 | 52.47 | 0.89931 | -0.71737 | -7.3623 | 0.77255 | 0.93423 | -16.7269 | 4.6193 | 0.38839 | 0.31252 | 0.42287 | 0.24582 | 0.4405 | 0.39887 | 0.39386
42838.4207 | 34 | 22.9048 | 22.8732 | 22.8532 | 22.7782 | 22.3963 | 21.7338 | 22.7141 | 21.7919 | 22.3647 | 22.3688 | 22.3458 | 22.0093 | 21.2268 | 22.1904 | 21.5986 | 21.7637 | 21.8931 | 21.0796 | 21.1788 | 21.3906 | 20.4704 | 20.6129 | 20.894 | 21.8742 | 21.6358 | 21.2559 | 36.375 | 33.8436 | 53.9124 | 22.0815 | 21.6773 | 21.1906 | 21.9936 | 21.7324 | 21.3479 | 20.1522 | 53.2627 |  | 23.108 | 27.4212 | 30.9361 | 21.3451 |  | 16.8797 | 16.815 | 16.5132 | 16.6807 | 16.8374 | 18.0435 | 21.1979 | 15.8673 | 17.0157 | 16.06 | 17.0327 | 18.0047 | 45.0408 | 48.3486 | 44.2988 | 21.4542 |  |  | 0.60543 | -0.1742 | -37.8172 | 0.26937 | 0.63294 | -197.8388 | 14.9904 | 0.037752 | -0.15909 | -0.23298 | 0.08605 | 8.8283 | 9.0582 | 1.9785 | 21.804 | 22.0052 | 22.1924 | 22.2478 | 22.0639 | 21.3804 | 20.1811 | 22.1887 | 22.3593 | 22.3856 | 22.3367 | 21.9564 | 21.1791 | 22.2439 | 18.7857 | 17.4201 | 16.4797 | 16.5224 | 16.544 | 17.178 | 16.8206 | 22.4116 | 22.1552 | 21.7058 | 22.0918 | 21.7932 | 21.2978 | 21.9364 | 21.5191 | 20.8865 | 20.3155 | 38.2083 | 22.9353 | 21.2937 | -0.049531 | -0.15707 | 22.1403 | 22.0773 | 22.3667 | 20.1258 | 21.6629 | 22.0968 | 21.9477 | 21.7116 | 21.278 | 21.7786 | 21.4399 | 21.0311 | 29.7918 | 39.2758 | 25.3786 | 25.3572 | 22.0328 |  | 20.4254 | 24.0297 | 20.4085 | 20.4799 | 20.5202 | 22.3581 |  | 21.5911 |  |  | 20.4127 | 20.5184 | 21.1625 | [5 empty] | 21.9152 | 21.1902 | 21.6608 | 22.0303 | 21.7281 | 21.1446 | 21.7567 | 19.8712 | 21.4571 | 60.6686 |  | 20.7333 | 31.3514 | 19.0161 | 20.2317 | 36.7648 | 20.5691 | 21.7836 | 19.2791 | 22.6876 | 19.3424 | 22.2816 | 18.9929 | 21.3559 | 31.3313 | 20.0637 | 20.5161 | 43.3834 | 19.0924 | 20.4125 | 36.8605 | 19.2595 | 23.0857 | 19.8754 | 23.024 | 19.1783 | 22.1172 | -0.089173 | 20.945 | 0.051744 | 0.013141 | -27.0143 | 3.0955 | 1.47 | 51.64 | 0.98065 | -0.4953 | -7.2977 | 0.61591 | 0.9461 | -16.7268 | 4.6043 | 0.37652 | 0.32049 | 0.42284 | 0.22421 | 0.43875 | 0.38647 | 0.39337
42838.4207 | 35 | 22.9048 | 22.8648 | 22.8526 | 22.7753 | 22.3943 | 21.73 | 22.7119 | 21.7899 | 22.3606 | 22.3683 | 22.3463 | 22.0071 | 21.217 | 22.1926 | 21.6024 | 21.7705 | 21.8973 | 21.0885 | 21.1858 | 21.3978 | 20.4734 | 20.6184 | 20.9039 | 21.8791 | 21.6371 | 21.2595 | 37.1024 | 34.2567 | 54.6753 | 22.0844 | 21.6801 | 21.1989 | 22.0016 | 21.7347 | 21.3501 | 20.1739 | 53.2295 |  | 23.2009 | 27.6108 | 31.2843 | 22.0463 |  | 16.8803 | 16.8173 | 16.5151 | 16.6799 | 16.8312 | 18.0506 | 21.4207 | 15.774 | 17.0198 | 16.0291 | 17.031 | 18.0122 | 45.0374 | 48.3497 | 44.3076 | 21.4587 |  |  | 0.39253 | -0.16763 | -37.3348 | 0.089322 | 0.17427 | -197.8466 | 15.1113 | 0.010812 | 0.047187 | -0.2848 | 0.082578 | 8.829 | 9.0589 | 1.9784 | 21.8142 | 22.0036 | 22.1888 | 22.2523 | 22.0715 | 21.3771 | 20.1812 | 22.1844 | 22.3598 | 22.3953 | 22.335 | 21.9549 | 21.1817 | 22.2561 | 18.8803 | 17.4044 | 16.4978 | 16.5563 | 16.5699 | 17.1853 | 16.8153 | 22.4225 | 22.1609 | 21.7072 | 22.0865 | 21.7951 | 21.2895 | 21.9381 | 21.5179 | 20.889 | 20.3242 | 38.4998 | 22.9817 | 21.336 | -0.034589 | -0.17533 | 22.1961 | 22.0749 | 22.3686 | 20.1198 | 21.6608 | 22.1058 | 21.9454 | 21.7112 | 21.2732 | 21.7771 | 21.4453 | 21.0282 | 30.2698 | 39.7119 | 25.7025 | 25.6984 | 22.4586 |  | 20.4449 | 24.2682 | 20.4295 | 20.4885 | 20.5249 | 22.5581 |  | 21.6332 |  |  | 20.4135 | 20.5296 | 21.2366 | [5 empty] | 21.9079 | 21.1996 | 21.6558 | 22.0235 | 21.7514 | 21.1459 | 21.7573 | 19.8822 | 21.5107 | 61.4104 |  | 20.7395 | 31.7435 | 19.0264 | 20.3365 | 37.2127 | 20.6044 | 21.8265 | 19.2741 | 22.9015 | 19.3497 | 22.5464 | 19.0019 | 21.3943 | 31.6468 | 20.0792 | 20.5456 | 43.9608 | 19.0973 | 20.5264 | 37.3018 | 19.2605 | 23.3805 | 19.8864 | 23.0385 | 19.1823 | 22.5903 | -0.21105 | 20.9466 | 0.051953 | 0.012807 | -27.0392 | 3.0955 | -1.32 | 51.86 | 0.79054 | -0.48587 | -7.251 | 0.35467 | 0.49645 | -16.7274 | 4.6229 | 0.36535 | 0.31457 | 0.42276 | 0.21455 | 0.43612 | 0.36772 | 0.39249
42838.4207 | 36 | 22.9105 | 22.8733 | 22.8563 | 22.7737 | 22.3998 | 21.7349 | 22.7141 | 21.7945 | 22.3689 | 22.3702 | 22.3445 | 22.0047 | 21.2216 | 22.1935 | 21.5977 | 21.7647 | 21.8966 | 21.0882 | 21.1865 | 21.3976 | 20.4718 | 20.6139 | 20.9026 | 21.8745 | 21.6368 | 21.2565 | 37.7137 | 34.6149 | 55.0139 | 22.0828 | 21.6823 | 21.2028 | 22.0039 | 21.7366 | 21.3528 | 20.1944 | 53.0069 |  | 23.2936 | 27.8666 | 31.6691 | 22.5051 |  | 16.8797 | 16.8147 | 16.515 | 16.6836 | 16.8314 | 18.0302 | 21.3914 | 15.7162 | 17.0248 | 16.0133 | 17.0327 | 18.0062 | 45.0403 | 48.3341 | 44.3171 | 21.4595 |  |  | 0.62515 | -0.10389 | -36.9117 | 0.48885 | 0.014588 | -197.8414 | 15.106 | -0.0687 | -0.28869 | -0.39452 | 0.025984 | 8.8281 | 9.058 | 1.9788 | 21.8006 | 22.0052 | 22.19 | 22.2393 | 22.0645 | 21.3775 | 20.1836 | 22.1802 | 22.3524 | 22.3874 | 22.3313 | 21.9494 | 21.1841 | 22.245 | 18.8709 | 17.3726 | 16.5162 | 16.5997 | 16.5815 | 17.1919 | 16.81 | 22.4183 | 22.1562 | 21.7009 | 22.0859 | 21.7986 | 21.2974 | 21.9377 | 21.5113 | 20.8883 | 20.3396 | 38.7923 | 23.0735 | 21.362 | -0.056019 | -0.026787 | 22.336 | 22.0749 | 22.3723 | 20.1186 | 21.6647 | 22.1042 | 21.948 | 21.7056 | 21.2829 | 21.7807 | 21.4414 | 21.0324 | 30.74 | 40.329 | 26.0561 | 26.041 | 22.7368 |  | 20.4657 | 24.9925 | 20.453 | 20.4969 | 20.5496 | 22.6819 |  | 21.6929 |  |  | 20.4206 | 20.536 | 21.3275 | [5 empty] | 21.9029 | 21.2126 | 21.6512 | 22.0197 | 21.7796 | 21.1401 | 21.7522 | 19.9002 | 21.5714 | 61.7929 |  | 20.7504 | 32.1282 | 19.0335 | 20.4233 | 37.5758 | 20.6346 | 21.8734 | 19.275 | 23.1117 | 19.3672 | 22.8438 | 18.9904 | 21.4142 | 32.0172 | 20.0891 | 20.5727 | 44.8705 | 19.1049 | 20.7287 | 37.7197 | 19.2574 | 23.6975 | 19.9048 | 23.0598 | 19.2007 | 22.9114 | -0.053185 | 20.9472 | 0.052032 | 0.012146 | -27.086 | 3.0955 | -2.53 | 52.52 | 0.99817 | -0.38249 | -7.2098 | 0.82971 | 0.14363 | -16.7266 | 4.6219 | 0.35832 | 0.29524 | 0.42335 | 0.21637 | 0.43345 | 0.35567 | 0.39228
42838.4207 | 37 | 22.9104 | 22.8714 | 22.858 | 22.7784 | 22.4026 | 21.7428 | 22.7141 | 21.796 | 22.3639 | 22.3657 | 22.343 | 22.0082 | 21.2181 | 22.1917 | 21.5849 | 21.7639 | 21.8954 | 21.0788 | 21.1726 | 21.3886 | 20.4629 | 20.6035 | 20.8961 | 21.869 | 21.629 | 21.2498 | 38.3629 | 34.9529 | 55.6801 | 22.082 | 21.6814 | 21.189 | 21.9977 | 21.7312 | 21.3425 | 20.2037 | 52.9318 |  | 23.3865 | 28.1417 | 32.0616 | 22.7255 |  | 16.8772 | 16.8188 | 16.5128 | 16.6775 | 16.8158 | 18 | 21.312 | 15.6594 | 17.0252 | 15.9022 | 17.0262 | 18.0076 | 45.0432 | 48.3284 | 44.3165 | 21.4588 |  |  | 0.36164 | 0.20101 | -36.9938 | 0.62619 | 0.13616 | -197.8374 | 15.3301 | 0.06798 | -0.072687 | -0.18179 | 0.10028 | 8.8284 | 9.0581 | 1.9787 | 21.7999 | 22.0089 | 22.1957 | 22.2457 | 22.0708 | 21.3798 | 20.1835 | 22.1974 | 22.357 | 22.3899 | 22.3404 | 21.9545 | 21.1855 | 22.2473 | 18.8276 | 17.3472 | 16.514 | 16.6327 | 16.5897 | 17.1952 | 16.8191 | 22.429 | 22.1583 | 21.7094 | 22.0849 | 21.7987 | 21.2939 | 21.9467 | 21.5155 | 20.8879 | 20.3438 | 39.2145 | 23.3789 | 21.3976 | 0.1105 | -0.08689 | 22.4932 | 22.0742 | 22.3625 | 20.1097 | 21.6573 | 22.1045 | 21.9493 | 21.6946 | 21.2814 | 21.7771 | 21.4302 | 21.0345 | 31.1018 | 41.1027 | 26.3962 | 26.3744 | 22.8246 |  | 20.4876 | 25.889 | 20.4825 | 20.5049 | 20.5606 | 22.6552 |  | 21.7646 |  |  | 20.4324 | 20.5419 | 21.4028 | [5 empty] | 21.9137 | 21.2291 | 21.6478 | 22.0225 | 21.8202 | 21.1358 | 21.7525 | 19.9081 | 21.6257 | 62.1002 |  | 20.7574 | 32.4868 | 19.0409 | 20.4644 | 37.889 | 20.6664 | 21.9725 | 19.2741 | 23.3149 | 19.3767 | 23.2427 | 18.9884 | 21.4169 | 32.4018 | 20.0974 | 20.5922 | 45.5649 | 19.113 | 20.8742 | 38.1357 | 19.2507 | 23.9849 | 19.9219 | 23.0518 | 19.2174 | 23.1309 | 0.061268 | 20.9463 | 0.053372 | 0.012495 | -27.0012 | 3.0955 | 3.23 | 51.32 | 0.75996 | 0.53205 | -7.2178 | 0.93906 | 0.43878 | -16.7255 | 4.6558 | 0.35661 | 0.27132 | 0.4235 | 0.22156 | 0.43476 | 0.34985 | 0.39143
42838.4207 | 38 | 22.904 | 22.8746 | 22.8552 | 22.7763 | 22.4048 | 21.7334 | 22.7105 | 21.796 | 22.3634 | 22.3721 | 22.3501 | 22.0121 | 21.2207 | 22.191 | 21.5904 | 21.7659 | 21.8996 | 21.0796 | 21.1739 | 21.3891 | 20.4663 | 20.6044 | 20.9032 | 21.8685 | 21.6321 | 21.2553 | 39.0967 | 35.3743 | 56.5978 | 22.0831 | 21.6822 | 21.1977 | 21.993 | 21.7369 | 21.3499 | 20.2195 | 53.0316 |  | 23.487 | 28.482 | 32.4735 | 22.8898 |  | 16.8785 | 16.8215 | 16.5121 | 16.6808 | 16.8136 | 17.9956 | 21.2518 | 15.5897 | 17.0308 | 15.8728 | 17.0287 | 18.0039 | 45.0522 | 48.3298 | 44.3262 | 21.4638 |  |  | 0.19277 | -0.29248 | -36.9425 | 0.78981 | 0.17098 | -197.89 | 15.4813 | 0.12252 | -0.073855 | -0.10773 | 0.020776 | 8.8281 | 9.0581 | 1.9778 | 21.8098 | 22.0167 | 22.1938 | 22.2573 | 22.0675 | 21.3784 | 20.185 | 22.1903 | 22.3573 | 22.3899 | 22.3456 | 21.9542 | 21.1848 | 22.2461 | 18.7673 | 17.3347 | 16.5187 | 16.6149 | 16.6029 | 17.1984 | 16.8252 | 22.4324 | 22.163 | 21.7069 | 22.0957 | 21.8009 | 21.3026 | 21.948 | 21.5205 | 20.895 | 20.3539 | 39.6525 | 23.6585 | 21.4485 | -0.1266 | -0.1546 | 22.7022 | 22.0755 | 22.3653 | 20.1055 | 21.6589 | 22.1043 | 21.9458 | 21.7062 | 21.2769 | 21.7679 | 21.4414 | 21.0381 | 31.4935 | 41.9115 | 26.7541 | 26.7297 | 22.7396 |  | 20.4996 | 26.6221 | 20.5132 | 20.5166 | 20.5806 | 22.7603 |  | 21.8268 |  |  | 20.4354 | 20.5511 | 21.4449 | [5 empty] | 21.907 | 21.2388 | 21.6403 | 22.0142 | 21.8615 | 21.1307 | 21.7519 | 19.9202 | 21.6696 | 62.7785 |  | 20.7743 | 32.8119 | 19.0444 | 20.4752 | 38.2142 | 20.7112 | 22.2973 | 19.2738 | 23.5351 | 19.3853 | 23.5829 | 18.9944 | 21.4207 | 32.7712 | 20.115 | 20.6203 | 45.9045 | 19.1243 | 20.9712 | 38.511 | 19.2601 | 24.2481 | 19.9413 | 23.2407 | 19.2286 | 23.3244 | -0.010892 | 20.9469 | 0.053827 | 0.013438 | -27.0735 | 3.0955 | -3.74 | 52.43 | 0.55561 | -0.64179 | -7.2129 | 1.0546 | 0.49169 | -16.7276 | 4.6787 | 0.35938 | 0.25199 | 0.42384 | 0.22864 | 0.43494 | 0.34582 | 0.39036
42838.4207 | 39 | 22.9112 | 22.8671 | 22.851 | 22.7695 | 22.402 | 21.7375 | 22.7092 | 21.7912 | 22.3648 | 22.3665 | 22.3522 | 22.0077 | 21.2188 | 22.1875 | 21.5933 | 21.7654 | 21.8925 | 21.0883 | 21.1777 | 21.3905 | 20.4726 | 20.6015 | 20.9002 | 21.8687 | 21.6366 | 21.2544 | 39.8064 | 35.8028 | 57.4692 | 22.0803 | 21.6741 | 21.1942 | 21.9966 | 21.7356 | 21.3503 | 20.241 | 53.2466 |  | 23.5899 | 28.8668 | 32.926 | 23.0591 |  | 16.8837 | 16.8217 | 16.5154 | 16.6846 | 16.8131 | 17.9853 | 21.2085 | 15.587 | 17.0282 | 15.8718 | 17.0243 | 18.0092 | 45.0572 | 48.3215 | 44.3307 | 21.4632 |  |  | 0.24796 | -0.47976 | -37.1377 | 0.71293 | 0.024444 | -197.8552 | 15.1402 | 0.025924 | -0.21163 | -0.20738 | -0.085467 | 8.8284 | 9.0583 | 1.9746 | 21.8079 | 22.0096 | 22.1969 | 22.2531 | 22.0727 | 21.376 | 20.1785 | 22.1843 | 22.3551 | 22.3914 | 22.3387 | 21.9505 | 21.1838 | 22.243 | 18.6747 | 17.3052 | 16.5317 | 16.6046 | 16.602 | 17.2004 | 16.8174 | 22.4218 | 22.1547 | 21.7009 | 22.0846 | 21.7931 | 21.3013 | 21.9466 | 21.5115 | 20.8864 | 20.3547 | 40.3874 | 23.859 | 21.4645 | 0.017313 | -0.063686 | 22.8588 | 22.0724 | 22.3569 | 20.0959 | 21.6507 | 22.0968 | 21.938 | 21.709 | 21.2661 | 21.7626 | 21.4333 | 21.0299 | 31.8616 | 42.6137 | 27.0794 | 27.0405 | 22.6072 |  | 20.5192 | 27.0543 | 20.5446 | 20.5199 | 20.599 | 23.0685 |  | 21.8894 |  |  | 20.449 | 20.5724 | 21.4668 | [5 empty] | 21.9026 | 21.2607 | 21.6387 | 22.0136 | 21.9026 | 21.1251 | 21.7534 | 19.9349 | 21.7136 | 63.2755 |  | 20.7941 | 33.0958 | 19.0534 | 20.47 | 38.4708 | 20.7512 | 22.6985 | 19.2689 | 23.7623 | 19.3956 | 23.9013 | 18.9861 | 21.422 | 33.1394 | 20.1201 | 20.6434 | 46.2905 | 19.1284 | 21.0139 | 38.8208 | 19.2599 | 24.4932 | 19.9507 | 23.7656 | 19.2338 | 23.5404 | -0.041499 | 20.9466 | 0.054539 | 0.014767 | -27.0784 | 3.0955 | -4.05 | 51.56 | 0.63099 | -0.82197 | -7.2319 | 1.002 | 0.18591 | -16.7258 | 4.6268 | 0.36371 | 0.24104 | 0.42437 | 0.23916 | 0.4326 | 0.34184 | 0.38994
42838.4207 | 40 | 22.9012 | 22.8609 | 22.8513 | 22.7711 | 22.4033 | 21.7263 | 22.7099 | 21.7905 | 22.364 | 22.3639 | 22.3432 | 22.0011 | 21.2204 | 22.1937 | 21.591 | 21.7624 | 21.8903 | 21.0822 | 21.1717 | 21.3925 | 20.4692 | 20.6052 | 20.8976 | 21.8751 | 21.6313 | 21.2501 | 40.2718 | 36.2143 | 57.5991 | 22.081 | 21.6779 | 21.1938 | 22.0028 | 21.7332 | 21.3461 | 20.2557 | 53.1378 |  | 23.6846 | 29.2255 | 33.3423 | 23.1084 |  | 16.8729 | 16.8305 | 16.5126 | 16.6827 | 16.8066 | 17.9659 | 21.1695 | 15.6456 | 17.0188 | 15.9062 | 17.0294 | 18.0126 | 45.0875 | 48.3188 | 44.3338 | 21.4679 |  |  | 0.3485 | -0.38777 | -37.0687 | 0.54471 | 0.051388 | -197.8729 | 15.0338 | 0.18823 | -0.16882 | -0.07185 | 0.004284 | 8.8288 | 9.0588 | 1.9707 | 21.8013 | 22.0051 | 22.1915 | 22.2481 | 22.066 | 21.3755 | 20.1779 | 22.1834 | 22.353 | 22.3853 | 22.3277 | 21.9522 | 21.182 | 22.2393 | 18.6371 | 17.3194 | 16.5518 | 16.6147 | 16.5975 | 17.2068 | 16.8211 | 22.4128 | 22.1479 | 21.7072 | 22.0794 | 21.7983 | 21.2979 | 21.9442 | 21.5119 | 20.8847 | 20.3732 | 41.4402 | 24.2409 | 21.4901 | -0.15963 | -0.17077 | 23.048 | 22.0634 | 22.3608 | 20.0917 | 21.6457 | 22.0962 | 21.9371 | 21.6974 | 21.2686 | 21.769 | 21.4316 | 21.03 | 32.2303 | 43.3994 | 27.3969 | 27.3579 | 22.445 |  | 20.5183 | 26.9681 | 20.5674 | 20.5307 | 20.6155 | 23.3087 |  | 21.9455 |  |  | 20.4665 | 20.5901 | 21.5039 | [5 empty] | 21.9105 | 21.2838 | 21.6433 | 22.0156 | 21.9556 | 21.1403 | 21.7491 | 19.9505 | 21.7697 | 63.4154 |  | 20.8281 | 33.4227 | 19.0566 | 20.482 | 38.7177 | 20.7923 | 23.1566 | 19.2747 | 24.0126 | 19.4058 | 24.2213 | 18.9749 | 21.4172 | 33.4822 | 20.1269 | 20.6914 | 46.9209 | 19.1335 | 21.0388 | 39.0103 | 19.2593 | 24.7221 | 19.9578 | 24.399 | 19.2424 | 23.7407 | -0.31493 | 20.9467 | 0.056094 | 0.015703 | -27.1381 | 3.0956 | 6.2 | 51.88 | 0.7482 | -0.73899 | -7.2253 | 0.87586 | 0.26954 | -16.726 | 4.6103 | 0.36819 | 0.24419 | 0.42462 | 0.24408 | 0.43079 | 0.34096 | 0.38985
42838.4208 | 41 | 22.898 | 22.8707 | 22.848 | 22.7745 | 22.3938 | 21.7272 | 22.7132 | 21.7859 | 22.3643 | 22.3667 | 22.3435 | 22.0028 | 21.2152 | 22.1825 | 21.5966 | 21.7708 | 21.8938 | 21.0814 | 21.1835 | 21.3919 | 20.473 | 20.6042 | 20.8987 | 21.8759 | 21.6388 | 21.2542 | 40.6391 | 36.616 | 57.2523 | 22.0866 | 21.6855 | 21.198 | 22.0026 | 21.7422 | 21.3578 | 20.2738 | 53.1045 |  | 23.7853 | 29.5789 | 33.7418 | 23.1356 |  | 16.8846 | 16.831 | 16.5235 | 16.6855 | 16.8153 | 17.9738 | 21.178 | 15.6571 | 17.0327 | 15.9521 | 17.0452 | 18.0088 | 45.1139 | 48.3093 | 44.3233 | 21.4636 |  |  | 0.39187 | -0.24123 | -36.9754 | 0.54339 | 0.02116 | -197.8046 | 15.294 | 0.041696 | 0.092723 | -0.21766 | -0.029568 | 8.8288 | 9.0587 | 1.9676 | 21.8063 | 22.0053 | 22.1834 | 22.2465 | 22.0611 | 21.3725 | 20.1748 | 22.1734 | 22.3567 | 22.388 | 22.3376 | 21.9519 | 21.1835 | 22.2455 | 18.6993 | 17.3524 | 16.5303 | 16.6152 | 16.6085 | 17.2207 | 16.8315 | 22.4181 | 22.1625 | 21.7072 | 22.0804 | 21.7955 | 21.2938 | 21.9371 | 21.514 | 20.8852 | 20.3818 | 42.2635 | 24.4936 | 21.5384 | -0.021614 | 0.053477 | 23.151 | 22.0634 | 22.3702 | 20.0986 | 21.6573 | 22.1029 | 21.9423 | 21.7047 | 21.2814 | 21.7728 | 21.442 | 21.0351 | 32.6038 | 43.9971 | 27.7076 | 27.6383 | 22.3113 |  | 20.5453 | 27.174 | 20.6061 | 20.5787 | 20.6325 | 23.3409 |  | 22.006 |  |  | 20.4793 | 20.6078 | 21.7628 | [5 empty] | 21.9152 | 21.3197 | 21.6481 | 22.0276 | 22.0048 | 21.1446 | 21.7553 | 19.9652 | 21.8267 | 63.7311 |  | 20.8514 | 33.7751 | 19.0549 | 20.4922 | 38.9737 | 20.8388 | 23.5171 | 19.2788 | 24.2403 | 19.4107 | 24.5184 | 18.9778 | 21.4239 | 33.8464 | 20.1368 | 20.8451 | 47.4794 | 19.1396 | 21.0592 | 39.2357 | 19.2551 | 24.9533 | 19.9726 | 24.7737 | 19.2529 | 23.9996 | 0.080931 | 20.9467 | 0.05661 | 0.014629 | -27.0712 | 3.0956 | 5.86 | 52.27 | 0.79298 | -0.58286 | -7.2162 | 0.8748 | 0.17297 | -16.7234 | 4.6501 | 0.37281 | 0.23977 | 0.42386 | 0.2388 | 0.43439 | 0.34081 | 0.3888
42838.4208 | 42 | 22.9031 | 22.8687 | 22.8488 | 22.7751 | 22.3959 | 21.7285 | 22.7112 | 21.7808 | 22.3596 | 22.3633 | 22.3418 | 22.0054 | 21.2192 | 22.1788 | 21.5941 | 21.7627 | 21.8846 | 21.078 | 21.1695 | 21.3858 | 20.4709 | 20.6045 | 20.8972 | 21.8759 | 21.631 | 21.2482 | 41.0896 | 37.0893 | 57.8577 | 22.0884 | 21.6881 | 21.1977 | 22.0031 | 21.7398 | 21.3579 | 20.2978 | 53.1889 |  | 23.8902 | 29.941 | 34.1378 | 23.253 |  | 16.8834 | 16.8492 | 16.5276 | 16.6896 | 16.805 | 17.9556 | 21.1441 | 15.6372 | 17.026 | 16.0082 | 17.0439 | 18.0165 | 45.1303 | 48.3015 | 44.3193 | 21.4719 |  |  | 0.47073 | -0.26291 | -36.7093 | 0.45928 | 0.1447 | -197.844 | 15.0627 | 0.078492 | -0.079109 | 0.025497 | -0.011166 | 8.8287 | 9.0586 | 1.9662 | 21.8037 | 22.0115 | 22.1911 | 22.2504 | 22.0731 | 21.3778 | 20.1834 | 22.1842 | 22.3598 | 22.3953 | 22.3392 | 21.9557 | 21.1782 | 22.2465 | 18.809 | 17.3751 | 16.5058 | 16.6151 | 16.6013 | 17.2264 | 16.8247 | 22.4121 | 22.1541 | 21.701 | 22.0862 | 21.7969 | 21.2993 | 21.9425 | 21.512 | 20.8836 | 20.3957 | 42.9138 | 25.0086 | 21.6074 | -0.1266 | -0.021081 | 23.2846 | 22.0746 | 22.3741 | 20.1012 | 21.6642 | 22.1099 | 21.9513 | 21.7184 | 21.2966 | 21.7787 | 21.4525 | 21.0415 | 32.9264 | 44.7228 | 27.9733 | 27.8871 | 22.2047 |  | 20.5658 | 27.9134 | 20.6477 | 20.6238 | 20.656 | 23.4343 |  | 22.061 |  |  | 20.4795 | 20.6093 | 21.8901 | [5 empty] | 21.9065 | 21.333 | 21.6468 | 22.025 | 22.0407 | 21.1342 | 21.751 | 19.9805 | 21.8816 | 64.0908 |  | 20.8636 | 34.0658 | 19.0577 | 20.5033 | 39.2299 | 20.8992 | 23.8807 | 19.2814 | 24.4339 | 19.4233 | 24.7549 | 18.9779 | 21.4213 | 34.1984 | 20.16 | 21.0074 | 47.7426 | 19.1482 | 21.0757 | 39.4543 | 19.2646 | 25.2018 | 19.9901 | 24.8947 | 19.2648 | 24.2136 | -0.073405 | 20.9451 | 0.058257 | 0.012553 | -27.029 | 3.0956 | -11.08 | 51.15 | 0.8699 | -0.60852 | -7.1904 | 0.80428 | 0.45229 | -16.7245 | 4.6147 | 0.37645 | 0.22063 | 0.42339 | 0.22726 | 0.43633 | 0.33835 | 0.38735
42838.4208 | 43 | 22.9075 | 22.8654 | 22.8581 | 22.7813 | 22.4044 | 21.7365 | 22.7121 | 21.7908 | 22.3672 | 22.368 | 22.3451 | 22.0126 | 21.2247 | 22.1881 | 21.5924 | 21.761 | 21.8927 | 21.0762 | 21.1722 | 21.3895 | 20.4646 | 20.5943 | 20.8945 | 21.8739 | 21.6228 | 21.2423 | 41.5811 | 37.662 | 58.4582 | 22.0821 | 21.6821 | 21.1897 | 21.9995 | 21.7339 | 21.3481 | 20.3075 | 53.1287 |  | 23.9811 | 30.2846 | 34.4941 | 23.3703 |  | 16.8924 | 16.8609 | 16.53 | 16.6919 | 16.7993 | 17.947 | 21.1168 | 15.6706 | 17.0285 | 16.0458 | 17.0428 | 18.0222 | 45.1546 | 48.3055 | 44.3181 | 21.4723 |  |  | 0.42407 | -0.26029 | -36.7723 | 0.38174 | 0.056644 | -197.8401 | 15.2362 | 0.011468 | -0.10655 | -0.17151 | -0.1622 | 8.8293 | 9.0591 | 1.9656 | 21.8052 | 22.0083 | 22.1873 | 22.2503 | 22.066 | 21.3759 | 20.1806 | 22.1781 | 22.3575 | 22.3878 | 22.3367 | 21.9605 | 21.1776 | 22.242 | 19.0588 | 17.465 | 16.634 | 16.6112 | 16.601 | 17.2383 | 16.8241 | 22.4153 | 22.1557 | 21.7057 | 22.086 | 21.7935 | 21.2975 | 21.9439 | 21.5114 | 20.887 | 20.4044 | 43.6312 | 25.7173 | 21.6623 | -0.12974 | 0.054048 | 23.4031 | 22.0735 | 22.3623 | 20.0973 | 21.6575 | 22.1072 | 21.9428 | 21.7112 | 21.2727 | 21.7774 | 21.4445 | 21.0376 | 33.278 | 45.5046 | 28.1853 | 28.0928 | 22.0992 |  | 20.5802 | 28.5979 | 20.6805 | 20.6729 | 20.665 | 23.4858 |  | 22.0994 |  |  | 20.4954 | 20.6166 | 21.9791 | [5 empty] | 21.91 | 21.353 | 21.643 | 22.0152 | 22.0699 | 21.14 | 21.7563 | 19.9981 | 21.9459 | 65.1753 |  | 20.8678 | 34.3351 | 19.0673 | 20.5113 | 39.5064 | 20.9604 | 24.2478 | 19.2878 | 24.6753 | 19.426 | 25.0304 | 18.9723 | 21.4279 | 34.5518 | 20.1776 | 21.1501 | 47.9004 | 19.1601 | 21.0913 | 39.6669 | 19.2703 | 25.4679 | 19.9981 | 25.0414 | 19.274 | 24.4042 | -0.072107 | 20.9467 | 0.059394 | 0.01235 | -27.0933 | 3.0956 | -18.61 | 52.71 | 0.82642 | -0.60548 | -7.1967 | 0.73326 | 0.28298 | -16.7241 | 4.6411 | 0.37987 | 0.20271 | 0.42233 | 0.20091 | 0.42201 | 0.33542 | 0.38611
42838.4208 | 44 | 22.9017 | 22.862 | 22.8566 | 22.775 | 22.3991 | 21.7367 | 22.713 | 21.7886 | 22.3622 | 22.3635 | 22.345 | 22.0094 | 21.2258 | 22.1862 | 21.597 | 21.772 | 21.8955 | 21.0897 | 21.175 | 21.3987 | 20.482 | 20.6131 | 20.9051 | 21.8749 | 21.6382 | 21.2578 | 42.1466 | 38.0136 | 59.3426 | 22.0796 | 21.6714 | 21.1901 | 21.9921 | 21.7335 | 21.3417 | 20.3146 | 52.7434 |  | 24.0719 | 30.6149 | 34.8637 | 23.4391 |  | 16.8973 | 16.8619 | 16.5268 | 16.6928 | 16.7943 | 17.9408 | 21.1041 | 15.6872 | 17.0295 | 16.0778 | 17.0407 | 18.0168 | 45.1585 | 48.2995 | 44.3058 | 21.4637 |  |  | 0.49898 | -0.59344 | -36.8243 | 0.26017 | 0.27612 | -197.8723 | 15.1954 | 0.14618 | -0.16045 | -0.10919 | -0.079912 | 8.8282 | 9.0583 | 1.9659 | 21.7968 | 22.0042 | 22.1816 | 22.2469 | 22.0605 | 21.3695 | 20.1786 | 22.182 | 22.3538 | 22.3775 | 22.33 | 21.9558 | 21.1757 | 22.2376 | 19.5439 | 17.6061 | 16.7106 | 16.5894 | 16.6095 | 17.2586 | 16.8275 | 22.4204 | 22.1573 | 21.7072 | 22.0855 | 21.7974 | 21.2983 | 21.9441 | 21.5141 | 20.8862 | 20.4217 | 44.1458 | 26.2545 | 21.8672 | -0.078628 | 0.15752 | 23.6622 | 22.068 | 22.356 | 20.0986 | 21.6564 | 22.1023 | 21.9377 | 21.7044 | 21.2738 | 21.7824 | 21.4316 | 21.0309 | 33.7603 | 46.2598 | 28.3923 | 28.307 | 22.0085 |  | 20.5949 | 29.0856 | 20.7178 | 20.7279 | 20.689 | 23.5273 |  | 22.1615 |  |  | 20.505 | 20.6307 | 22.0294 | [5 empty] | 21.9174 | 21.3839 | 21.6522 | 22.0272 | 22.1154 | 21.1439 | 21.756 | 20.006 | 21.9868 | 66.598 |  | 20.8572 | 34.6161 | 19.0572 | 20.499 | 39.9096 | 20.9907 | 24.6186 | 19.2773 | 24.9104 | 19.427 | 25.3589 | 18.9769 | 21.447 | 34.9259 | 20.1912 | 21.2572 | 48.589 | 19.1508 | 21.1054 | 39.9071 | 19.2671 | 25.7363 | 20.0152 | 25.6789 | 19.2775 | 24.5861 | -0.059864 | 20.948 | 0.060617 | 0.01187 | -27.0514 | 3.0956 | -11.92 | 51.31 | 0.89764 | -0.91425 | -7.2018 | 0.60535 | 0.62478 | -16.7253 | 4.6349 | 0.38288 | 0.19041 | 0.42161 | 0.14938 | 0.41389 | 0.33375 | 0.381
42838.4208 | 45 | 22.9066 | 22.8629 | 22.8514 | 22.7708 | 22.407 | 21.74 | 22.7066 | 21.7935 | 22.3575 | 22.368 | 22.3436 | 22.0109 | 21.23 | 22.1852 | 21.5908 | 21.7697 | 21.8933 | 21.0801 | 21.1721 | 21.3859 | 20.4701 | 20.5968 | 20.895 | 21.8691 | 21.6296 | 21.26 | 42.6384 | 38.3678 | 60.2434 | 22.0797 | 21.6744 | 21.1845 | 21.986 | 21.7299 | 21.3444 | 20.3332 | 52.6013 |  | 24.1692 | 30.9722 | 35.2485 | 23.4478 |  | 16.8982 | 16.8538 | 16.5254 | 16.6805 | 16.7986 | 17.94 | 21.102 | 15.6985 | 17.0306 | 16.0645 | 17.0436 | 18.0099 | 45.16 | 48.2931 | 44.291 | 21.4713 |  |  | 0.49833 | -0.58293 | -37.3217 | 0.59399 | 0.30109 | -197.8138 | 14.7433 | 0.043664 | -0.19567 | -0.13752 | -0.1181 | 8.8295 | 9.0594 | 1.9662 | 21.8007 | 22.0012 | 22.179 | 22.2478 | 22.0646 | 21.3719 | 20.1766 | 22.184 | 22.3552 | 22.3841 | 22.3351 | 21.9523 | 21.1774 | 22.2408 | 19.8514 | 17.6135 | 16.6584 | 16.5461 | 16.6003 | 17.279 | 16.8283 | 22.4258 | 22.1639 | 21.7138 | 22.0956 | 21.7987 | 21.3012 | 21.9519 | 21.5173 | 20.8953 | 20.4457 | 44.9243 | 26.5267 | 22.1737 | 0.027733 | 0.12062 | 23.9493 | 22.0632 | 22.3669 | 20.0978 | 21.6526 | 22.1033 | 21.9391 | 21.7101 | 21.2844 | 21.7722 | 21.4452 | 21.0326 | 34.2497 | 47.1541 | 28.5926 | 28.5574 | 21.9474 |  | 20.6174 | 29.4061 | 20.7497 | 20.7685 | 20.6948 | 23.7005 |  | 22.2178 |  |  | 20.5221 | 20.6354 | 22.0439 | [5 empty] | 21.9125 | 21.4108 | 21.6598 | 22.0267 | 22.1568 | 21.1379 | 21.7529 | 20.0266 | 22.0522 | 67.5201 |  | 20.8596 | 34.9264 | 19.0694 | 20.5194 | 40.2355 | 21.037 | 25.0511 | 19.287 | 25.1773 | 19.4455 | 25.6713 | 18.9779 | 21.4637 | 35.2142 | 20.1991 | 21.2942 | 49.3202 | 19.1625 | 21.1297 | 40.2173 | 19.278 | 26.009 | 20.0329 | 26.055 | 19.2817 | 24.8145 | -0.035378 | 20.9481 | 0.061759 | 0.012052 | -27.1271 | 3.0956 | 0.89 | 51.8 | 0.89826 | -0.9061 | -7.2502 | 0.91466 | 0.65242 | -16.7228 | 4.5654 | 0.38533 | 0.18258 | 0.42068 | 0.11759 | 0.41979 | 0.33413 | 0.37329
42838.4208 | 46 | 22.9064 | 22.8659 | 22.8565 | 22.7805 | 22.4028 | 21.7365 | 22.7146 | 21.7939 | 22.3715 | 22.3678 | 22.3391 | 22.0111 | 21.219 | 22.1797 | 21.5953 | 21.7741 | 21.8911 | 21.0805 | 21.1784 | 21.3992 | 20.4769 | 20.6058 | 20.8958 | 21.8757 | 21.6308 | 21.2622 | 43.248 | 38.7448 | 61.6535 | 22.0823 | 21.6816 | 21.1954 | 22.0039 | 21.7368 | 21.347 | 20.3517 | 52.6721 |  | 24.2715 | 31.3224 | 35.6974 | 23.7481 |  | 16.8942 | 16.8591 | 16.5254 | 16.677 | 16.7956 | 17.9371 | 21.0871 | 15.769 | 17.027 | 16.0773 | 17.0446 | 18.0095 | 45.159 | 48.2958 | 44.2906 | 21.4623 |  |  | 0.28673 | -0.50342 | -37.6075 | 0.30223 | 0.29518 | -197.8414 | 14.7571 | -0.065416 | -0.071909 | 0.10082 | -0.072447 | 8.829 | 9.0591 | 1.9672 | 21.8026 | 22.0089 | 22.1868 | 22.2495 | 22.0693 | 21.3745 | 20.1828 | 22.1833 | 22.3561 | 22.3897 | 22.3349 | 21.9569 | 21.182 | 22.2447 | 20.1441 | 17.6442 | 16.6143 | 16.5194 | 16.5683 | 17.3089 | 16.8339 | 22.4178 | 22.1612 | 21.7027 | 22.0863 | 21.7987 | 21.2894 | 21.9344 | 21.5112 | 20.8877 | 20.4686 | 45.7295 | 26.81 | 22.3993 | -0.070764 | 0.058422 | 24.0655 | 22.0748 | 22.3694 | 20.1027 | 21.6498 | 22.1106 | 21.9431 | 21.7103 | 21.2817 | 21.7757 | 21.4344 | 21.037 | 34.6122 | 48.0093 | 28.8007 | 28.7869 | 21.8693 |  | 20.6306 | 29.1746 | 20.7727 | 20.811 | 20.7141 | 23.6712 |  | 22.2521 |  |  | 20.5197 | 20.6365 | 22.0529 | [5 empty] | 21.8995 | 21.4197 | 21.6414 | 22.0078 | 22.1896 | 21.1298 | 21.7382 | 20.0525 | 22.1044 | 68.2597 |  | 20.8589 | 35.2244 | 19.0777 | 20.5126 | 40.767 | 21.0753 | 25.5336 | 19.2913 | 25.41 | 19.4578 | 25.9697 | 18.9714 | 21.4682 | 35.4629 | 20.211 | 21.3057 | 50.0235 | 19.1727 | 21.1412 | 40.7271 | 19.2772 | 26.2621 | 20.0524 | 26.2823 | 19.2859 | 25.1034 | 0.0583 | 20.9478 | 0.062755 | 0.011994 | -27.1253 | 3.0956 | -8.25 | 52.09 | 0.68281 | -0.84205 | -7.278 | 0.65244 | 0.64598 | -16.7239 | 4.5675 | 0.38795 | 0.18978 | 0.42014 | 0.088549 | 0.42534 | 0.32641 | 0.36779
42838.4208 | 47 | 22.9037 | 22.8714 | 22.8575 | 22.7784 | 22.3967 | 21.7362 | 22.7143 | 21.7834 | 22.3678 | 22.3694 | 22.3457 | 22.0043 | 21.2165 | 22.1914 | 21.598 | 21.7687 | 21.8988 | 21.0796 | 21.1791 | 21.391 | 20.47 | 20.6089 | 20.8971 | 21.8809 | 21.6331 | 21.2624 | 43.9433 | 39.1291 | 63.1699 | 22.0808 | 21.6872 | 21.1967 | 22.0067 | 21.7361 | 21.3475 | 20.3968 | 52.9322 |  | 24.4083 | 31.6268 | 36.13 | 25.9521 |  | 16.8907 | 16.8566 | 16.5187 | 16.6823 | 16.8036 | 17.9236 | 21.0591 | 15.852 | 17.0257 | 16.095 | 17.0545 | 18.0047 | 45.1568 | 48.3154 | 44.2888 | 21.4676 |  |  | 0.42735 | -0.44559 | -37.1765 | 0.35874 | 0.28598 | -197.8578 | 15.0489 | -0.11141 | -0.27137 | -0.13332 | -0.011861 | 8.8287 | 9.0586 | 1.9687 | 21.8015 | 22.0139 | 22.1943 | 22.2481 | 22.0708 | 21.3749 | 20.1785 | 22.1899 | 22.3549 | 22.3906 | 22.3364 | 21.9596 | 21.1831 | 22.2513 | 20.4249 | 17.6111 | 16.5934 | 16.4776 | 16.5427 | 17.341 | 16.8324 | 22.4179 | 22.1609 | 21.7098 | 22.0888 | 21.7991 | 21.297 | 21.944 | 21.5153 | 20.8867 | 20.4936 | 46.603 | 27.0368 | 22.5387 | 0.037366 | -0.02926 | 24.1104 | 22.0739 | 22.3642 | 20.0951 | 21.6513 | 22.1022 | 21.9391 | 21.704 | 21.2673 | 21.7791 | 21.4341 | 21.0253 | 34.9463 | 48.6676 | 28.9952 | 29.0035 | 21.7874 |  | 20.6472 | 28.5766 | 20.7994 | 20.8872 | 20.738 | 23.7783 |  | 22.3068 |  |  | 20.5348 | 20.6674 | 22.1088 | [5 empty] | 21.9131 | 21.4686 | 21.6562 | 22.0275 | 22.2475 | 21.1364 | 21.7584 | 20.0661 | 22.1576 | 69.2683 |  | 20.8542 | 35.507 | 19.0765 | 20.5198 | 41.2803 | 21.1206 | 25.9414 | 19.2966 | 25.6607 | 19.4629 | 26.2477 | 18.9752 | 21.4822 | 35.707 | 20.2223 | 21.3145 | 50.7886 | 19.173 | 21.1486 | 41.2037 | 19.2777 | 26.4678 | 20.0676 | 26.6379 | 19.2915 | 25.3343 | -0.1387 | 20.9476 | 0.063861 | 0.012364 | -27.0794 | 3.0955 | -11.71 | 51.61 | 0.83548 | -0.79221 | -7.2361 | 0.71082 | 0.63582 | -16.7242 | 4.6123 | 0.39078 | 0.20729 | 0.41883 | 0.061085 | 0.42749 | 0.2667 | 0.36476
42838.4208 | 48 | 22.9059 | 22.8633 | 22.8495 | 22.7804 | 22.3953 | 21.7368 | 22.7195 | 21.7884 | 22.3684 | 22.3691 | 22.3492 | 22.0066 | 21.2176 | 22.191 | 21.5993 | 21.7673 | 21.8943 | 21.0816 | 21.1799 | 21.3984 | 20.467 | 20.6046 | 20.9024 | 21.8815 | 21.6314 | 21.2588 | 44.715 | 39.5525 | 64.232 | 22.0867 | 21.68 | 21.1985 | 22.0019 | 21.7325 | 21.353 | 20.4304 | 52.9415 |  | 24.5282 | 31.8876 | 36.55 | 27.5647 |  | 16.8945 | 16.8531 | 16.5179 | 16.6802 | 16.803 | 17.9203 | 21.0005 | 15.9034 | 17.0248 | 16.1099 | 17.056 | 18.0023 | 45.1382 | 48.3153 | 44.2775 | 21.4634 |  |  | 0.52527 | -0.2708 | -37.7429 | 0.46782 | -0.036008 | -197.8466 | 14.7321 | -0.22181 | -0.15014 | -0.18598 | 0.030498 | 8.829 | 9.0589 | 1.9699 | 21.806 | 22.0165 | 22.2017 | 22.2487 | 22.0756 | 21.375 | 20.1928 | 22.1913 | 22.3587 | 22.3937 | 22.3378 | 21.964 | 21.1861 | 22.2509 | 20.7112 | 17.5492 | 16.5393 | 16.4563 | 16.5052 | 17.363 | 16.8363 | 22.4207 | 22.1505 | 21.7101 | 22.0922 | 21.7965 | 21.2924 | 21.9428 | 21.5151 | 20.8861 | 20.5099 | 47.1786 | 27.2115 | 22.658 | -0.011784 | 0.0045958 | 24.2637 | 22.0568 | 22.359 | 20.0938 | 21.64 | 22.0924 | 21.9266 | 21.7029 | 21.2751 | 21.7622 | 21.4328 | 21.0271 | 35.4483 | 49.4833 | 29.2027 | 29.2536 | 21.6978 |  | 20.6603 | 28.0582 | 20.8193 | 20.9531 | 20.7577 | 23.9006 |  | 22.3566 |  |  | 20.5306 | 20.6667 | 22.1002 | [5 empty] | 21.9134 | 21.4927 | 21.6502 | 22.0213 | 22.2925 | 21.1351 | 21.7508 | 20.0697 | 22.2046 | 70.3538 |  | 20.8499 | 35.7441 | 19.066 | 20.5309 | 41.7965 | 21.161 | 26.286 | 19.2964 | 25.9368 | 19.4588 | 26.4863 | 18.9712 | 21.4959 | 35.9591 | 20.2382 | 21.3399 | 51.6817 | 19.1764 | 21.1688 | 41.7943 | 19.2777 | 26.6604 | 20.0869 | 27.0699 | 19.2984 | 25.5899 | 0.010441 | 20.9494 | 0.064518 | 0.013097 | -27.0868 | 3.0955 | -12.8 | 52.4 | 0.92772 | -0.61758 | -7.291 | 0.81172 | -0.22561 | -16.7236 | 4.5635 | 0.3937 | 0.22236 | 0.41766 | 0.031842 | 0.43395 | 0.22303 | 0.36199
42838.4208 | 49 | 22.9064 | 22.8659 | 22.8568 | 22.7718 | 22.402 | 21.735 | 22.7237 | 21.793 | 22.3676 | 22.3691 | 22.3464 | 22.0163 | 21.2172 | 22.1971 | 21.5995 | 21.7682 | 21.8949 | 21.0859 | 21.1827 | 21.3969 | 20.4686 | 20.6131 | 20.9026 | 21.8763 | 21.6357 | 21.2603 | 45.6223 | 40.0544 | 65.446 | 22.0801 | 21.6764 | 21.1939 | 21.9996 | 21.7346 | 21.3483 | 20.4748 | 54.3312 |  | 24.6346 | 32.1439 | 37.0194 | 28.141 |  | 16.8956 | 16.8436 | 16.5138 | 16.6811 | 16.8028 | 17.9048 | 20.9594 | 15.9404 | 17.0278 | 16.0964 | 17.0597 | 18.0143 | 45.1367 | 48.3217 | 44.2781 | 21.4634 |  |  | 0.27885 | -0.21823 | -38.3389 | 0.38765 | 0.16112 | -197.8434 | 14.4299 | -0.002332 | 0.14351 | -0.031778 | 0.079106 | 8.8278 | 9.0576 | 1.9727 | 21.8031 | 22.0103 | 22.1897 | 22.2458 | 22.069 | 21.3728 | 20.1773 | 22.1781 | 22.3533 | 22.3896 | 22.3286 | 21.9554 | 21.1758 | 22.2357 | 21.1839 | 17.4517 | 16.4938 | 16.4344 | 16.4641 | 17.3849 | 16.8433 | 22.4158 | 22.1442 | 21.7026 | 22.0838 | 21.7908 | 21.289 | 21.9367 | 21.5114 | 20.8865 | 20.53 | 47.5971 | 27.3105 | 22.7056 | 0.026357 | 0.091137 | 24.4019 | 22.0753 | 22.3668 | 20.0968 | 21.6577 | 22.1093 | 21.9389 | 21.7034 | 21.2731 | 21.7757 | 21.4449 | 21.0305 | 35.9717 | 50.4272 | 29.4406 | 29.5027 | 21.6267 |  | 20.6788 | 28.1557 | 20.8421 | 21.0017 | 20.7876 | 23.8186 |  | 22.4163 |  |  | 20.5128 | 20.6555 | 22.03 | [5 empty] | 21.9069 | 21.5163 | 21.6436 | 22.0178 | 22.3394 | 21.135 | 21.7447 | 20.0892 | 22.2624 | 71.1731 |  | 20.8647 | 36.0031 | 19.0662 | 20.5508 | 42.4582 | 21.2107 | 26.634 | 19.3071 | 26.2727 | 19.4696 | 26.7277 | 18.9695 | 21.5118 | 36.2393 | 20.2477 | 21.3778 | 52.4912 | 19.1818 | 21.1877 | 42.4172 | 19.2782 | 26.9194 | 20.1106 | 27.4654 | 19.3094 | 25.8625 | -0.073961 | 20.9486 | 0.065428 | 0.013794 | -27.1523 | 3.0956 | 8.04 | 51.45 | 0.67716 | -0.55439 | -7.3482 | 0.7389 | 0.47724 | -16.723 | 4.5163 | 0.3963 | 0.22041 | 0.41731 | -0.018119 | 0.43983 | 0.20851 | 0.36134
42838.4209 | 50 | 22.9001 | 22.8664 | 22.8566 | 22.7784 | 22.4046 | 21.7372 | 22.7159 | 21.7913 | 22.3616 | 22.3709 | 22.3393 | 22.008 | 21.2211 | 22.1925 | 21.5959 | 21.7612 | 21.8905 | 21.0819 | 21.1733 | 21.3882 | 20.4621 | 20.6047 | 20.8948 | 21.8676 | 21.6233 | 21.2465 | 46.4779 | 40.5582 | 67.0544 | 22.0838 | 21.6752 | 21.1909 | 21.9988 | 21.7311 | 21.3475 | 20.5152 | 55.6906 |  | 24.7523 | 32.3957 | 37.53 | 28.0724 |  | 16.8802 | 16.8265 | 16.4998 | 16.6687 | 16.7845 | 17.8653 | 20.8918 | 15.9346 | 17.0171 | 16.0504 | 17.0423 | 18.0069 | 45.1418 | 48.3268 | 44.2674 | 21.4678 |  |  | 0.36427 | -0.16237 | -38.588 | 0.60779 | 0.10593 | -197.8985 | 14.4318 | -0.2251 | -0.20268 | -0.38781 | -0.012902 | 8.8288 | 9.0587 | 1.9753 | 21.8021 | 22.018 | 22.1998 | 22.2552 | 22.0719 | 21.3769 | 20.1821 | 22.1977 | 22.3566 | 22.388 | 22.3446 | 21.9603 | 21.1846 | 22.2443 | 21.4625 | 17.3888 | 16.4625 | 16.4229 | 16.4438 | 17.4089 | 16.8357 | 22.4273 | 22.1662 | 21.708 | 22.0939 | 21.796 | 21.2999 | 21.9458 | 21.5141 | 20.892 | 20.5586 | 48.0784 | 27.499 | 22.7794 | -0.06172 | 0.12689 | 24.4897 | 22.0733 | 22.375 | 20.1029 | 21.6582 | 22.1034 | 21.9429 | 21.7086 | 21.2771 | 21.7751 | 21.4393 | 21.034 | 36.4484 | 51.4676 | 29.6987 | 29.7959 | 21.5806 |  | 20.6845 | 29.1461 | 20.8724 | 21.016 | 20.797 | 23.7756 |  | 22.4724 |  |  | 20.5289 | 20.6521 | 21.9847 | [5 empty] | 21.9112 | 21.5474 | 21.6479 | 22.0206 | 22.3832 | 21.1349 | 21.7462 | 20.1162 | 22.3254 | 71.9062 |  | 20.8857 | 36.3286 | 19.0806 | 20.5693 | 43.0671 | 21.2677 | 26.9736 | 19.3236 | 26.6771 | 19.4815 | 27.0603 | 18.9657 | 21.5263 | 36.5374 | 20.2634 | 21.4068 | 53.0328 | 19.1934 | 21.21 | 42.9894 | 19.2775 | 27.1734 | 20.1313 | 27.7623 | 19.3167 | 26.1589 | 0.069801 | 20.9483 | 0.06595 | 0.013584 | -27.0667 | 3.0956 | -1.98 | 52.39 | 0.7758 | -0.4782 | -7.3718 | 0.92518 | 0.38693 | -16.7242 | 4.5163 | 0.39777 | 0.19392 | 0.41723 | -0.046273 | 0.44242 | 0.21177 | 0.36025
42838.4209 | 51 | 22.9032 | 22.865 | 22.8587 | 22.7808 | 22.4114 | 21.7403 | 22.7167 | 21.7879 | 22.3653 | 22.3705 | 22.3382 | 22.0068 | 21.2185 | 22.1928 | 21.594 | 21.7642 | 21.8934 | 21.0844 | 21.1725 | 21.386 | 20.4704 | 20.6043 | 20.8998 | 21.8702 | 21.6263 | 21.2493 | 47.0306 | 41.0402 | 67.7502 | 22.0852 | 21.6764 | 21.1919 | 21.9992 | 21.7339 | 21.3467 | 20.554 | 56.9809 |  | 24.8914 | 32.6724 | 38.0607 | 27.7941 |  | 16.8781 | 16.8264 | 16.5063 | 16.6645 | 16.7832 | 17.8579 | 20.9718 | 15.9517 | 17.0235 | 16.0375 | 17.058 | 18.0092 | 45.1346 | 48.3391 | 44.2435 | 21.4655 |  |  | 0.4083 | -0.35359 | -38.7917 | 0.57427 | 0.26364 | -197.8453 | 14.3701 | -0.12521 | 0.0024286 | -0.23088 | 0.11053 | 8.8284 | 9.0583 | 1.9764 | 21.8056 | 22.0052 | 22.1817 | 22.248 | 22.0618 | 21.3688 | 20.1779 | 22.1824 | 22.353 | 22.3856 | 22.3283 | 21.9495 | 21.1787 | 22.2401 | 21.5276 | 17.3513 | 16.4737 | 16.4298 | 16.4417 | 17.4301 | 16.8465 | 22.4199 | 22.1559 | 21.7098 | 22.086 | 21.7953 | 21.3 | 21.9357 | 21.5211 | 20.8892 | 20.5844 | 48.5017 | 27.6783 | 22.8342 | -0.10065 | 0.063558 | 24.6134 | 22.076 | 22.363 | 20.1041 | 21.6576 | 22.1011 | 21.9447 | 21.7093 | 21.27 | 21.7707 | 21.4413 | 21.0328 | 36.8722 | 52.3086 | 29.9937 | 30.1034 | 21.6245 |  | 20.7004 | 30.5223 | 20.9006 | 21.0312 | 20.8213 | 23.7712 |  | 22.5238 |  |  | 20.5342 | 20.6508 | 22.0828 | [5 empty] | 21.9065 | 21.5701 | 21.6451 | 22.0126 | 22.4195 | 21.1289 | 21.7436 | 20.1324 | 22.3806 | 72.2196 |  | 20.8939 | 36.674 | 19.0777 | 20.5653 | 43.666 | 21.3082 | 27.3621 | 19.3293 | 27.0152 | 19.4897 | 27.423 | 18.9649 | 21.5393 | 36.8516 | 20.2757 | 21.4425 | 53.6218 | 19.2003 | 21.2335 | 43.5137 | 19.2744 | 27.4067 | 20.1556 | 28.0465 | 19.3246 | 26.4753 | 0.009328 | 20.9439 | 0.066466 | 0.013221 | -27.0437 | 3.0955 | -5.26 | 52.09 | 0.82218 | -0.70567 | -7.3912 | 0.89931 | 0.61041 | -16.7218 | 4.5066 | 0.39709 | 0.15664 | 0.41762 | -0.051025 | 0.44243 | 0.2208 | 0.35959
42838.4209 | 52 | 22.9057 | 22.8647 | 22.8558 | 22.7841 | 22.4086 | 21.7356 | 22.7181 | 21.7872 | 22.3681 | 22.368 | 22.3451 | 22.0006 | 21.216 | 22.1868 | 21.5957 | 21.7679 | 21.894 | 21.0879 | 21.1786 | 21.3914 | 20.4761 | 20.6064 | 20.9044 | 21.876 | 21.6328 | 21.2603 | 47.5756 | 41.4562 | 67.6015 | 22.0736 | 21.6722 | 21.189 | 21.9932 | 21.7319 | 21.3466 | 20.5809 | 57.9512 |  | 25.0306 | 32.989 | 38.5483 | 27.3876 |  | 16.8665 | 16.813 | 16.4936 | 16.6644 | 16.774 | 17.8428 | 21.2852 | 15.9851 | 17.0223 | 16.0385 | 17.0538 | 18.0116 | 45.1355 | 48.3427 | 44.2312 | 21.472 |  |  | 0.54827 | -0.12229 | -39.4652 | 0.43759 | 0.087528 | -197.8644 | 14.0435 | -0.13573 | 0.10498 | 0.069135 | 0.046469 | 8.829 | 9.0588 | 1.9764 | 21.8065 | 22.008 | 22.1944 | 22.2522 | 22.0625 | 21.3666 | 20.1747 | 22.1747 | 22.3588 | 22.3921 | 22.3318 | 21.9563 | 21.181 | 22.2478 | 21.5121 | 17.3103 | 16.4707 | 16.4442 | 16.4358 | 17.4351 | 16.8456 | 22.4167 | 22.1568 | 21.702 | 22.0888 | 21.794 | 21.2889 | 21.945 | 21.5168 | 20.8844 | 20.5948 | 48.7883 | 27.9059 | 22.8932 | -0.011194 | 0.066601 | 24.814 | 22.0641 | 22.3609 | 20.0833 | 21.6376 | 22.0911 | 21.935 | 21.7012 | 21.2719 | 21.7682 | 21.4287 | 21.0244 | 37.4165 | 53.1637 | 30.2846 | 30.4133 | 22.0055 |  | 20.7257 | 31.6186 | 20.9406 | 21.0673 | 20.8457 | 23.8006 |  | 22.5972 |  |  | 20.5432 | 20.6554 | 22.2941 | [5 empty] | 21.9017 | 21.631 | 21.6408 | 22.0178 | 22.4559 | 21.1362 | 21.7477 | 20.1522 | 22.4389 | 72.6996 |  | 20.9037 | 37.1531 | 19.0772 | 20.5702 | 44.3353 | 21.3599 | 27.7304 | 19.3411 | 27.2764 | 19.495 | 27.7673 | 18.9639 | 21.5484 | 37.2308 | 20.2885 | 21.4851 | 54.2851 | 19.2061 | 21.2532 | 44.0873 | 19.281 | 27.6292 | 20.1753 | 28.29 | 19.3405 | 26.816 | 0.06739 | 20.9406 | 0.067904 | 0.013598 | -27.0301 | 3.0955 | 10.54 | 51.37 | 0.95254 | -0.41498 | -7.455 | 0.78501 | 0.35171 | -16.7221 | 4.455 | 0.38735 | 0.12753 | 0.41744 | -0.048724 | 0.44266 | 0.23299 | 0.3583
42838.4209 | 53 | 22.9008 | 22.8612 | 22.8612 | 22.7838 | 22.404 | 21.7372 | 22.7232 | 21.7916 | 22.355 | 22.3712 | 22.3457 | 21.995 | 21.2201 | 22.1875 | 21.6034 | 21.7696 | 21.895 | 21.0845 | 21.1721 | 21.4014 | 20.4801 | 20.6151 | 20.8991 | 21.8716 | 21.6345 | 21.2634 | 48.2119 | 41.8736 | 67.7687 | 22.0833 | 21.6697 | 21.1904 | 21.9868 | 21.7282 | 21.3515 | 20.602 | 59.3874 |  | 25.1704 | 33.4457 | 38.979 | 26.9697 |  | 16.8549 | 16.8089 | 16.4846 | 16.6533 | 16.7595 | 17.8434 | 21.6726 | 15.9403 | 17.0131 | 16.027 | 17.042 | 18.0056 | 45.1157 | 48.3463 | 44.2234 | 21.4654 |  |  | 0.47401 | -0.20706 | -39.9856 | 0.59267 | 0.082272 | -197.8493 | 13.7478 | -0.16398 | -0.13418 | 0.10438 | -0.0094304 | 8.8289 | 9.0585 | 1.9749 | 21.8071 | 22.009 | 22.1869 | 22.2476 | 22.063 | 21.3701 | 20.1757 | 22.1747 | 22.356 | 22.3883 | 22.3316 | 21.9574 | 21.1806 | 22.244 | 21.3539 | 17.2999 | 16.5055 | 16.4599 | 16.421 | 17.4487 | 16.8571 | 22.4192 | 22.159 | 21.6992 | 22.0844 | 21.7946 | 21.298 | 21.9408 | 21.5177 | 20.8896 | 20.6207 | 49.2778 | 28.2537 | 22.9214 | 0.0009952 | -0.11827 | 25.1009 | 22.0661 | 22.3531 | 20.087 | 21.642 | 22.0976 | 21.9366 | 21.6912 | 21.274 | 21.7663 | 21.432 | 21.025 | 38.2275 | 54.0119 | 30.5569 | 30.7202 | 22.2363 |  | 20.7466 | 32.3323 | 20.9832 | 21.1335 | 20.8626 | 23.7905 |  | 22.6823 |  |  | 20.5533 | 20.6708 | 22.4894 | [5 empty] | 21.9038 | 21.7318 | 21.6442 | 22.0213 | 22.5017 | 21.1397 | 21.753 | 20.1652 | 22.4992 | 73.359 |  | 20.9176 | 37.7412 | 19.084 | 20.5735 | 44.9038 | 21.414 | 28.0411 | 19.3471 | 27.4773 | 19.5074 | 28.1314 | 18.9622 | 21.5541 | 37.6053 | 20.3079 | 21.5209 | 55.0318 | 19.2191 | 21.2642 | 44.6462 | 19.2928 | 27.8576 | 20.196 | 28.4813 | 19.3524 | 27.1892 | 0.025837 | 20.9382 | 0.068506 | 0.013983 | -27.0275 | 3.0956 | -5.17 | 52.68 | 0.8859 | -0.53998 | -7.5039 | 0.91357 | 0.34098 | -16.7215 | 4.4078 | 0.38164 | 0.10913 | 0.41616 | -0.029554 | 0.44014 | 0.24531 | 0.35839
42838.4209 | 54 | 22.9094 | 22.8643 | 22.8638 | 22.7798 | 22.4 | 21.7302 | 22.7131 | 21.7911 | 22.3613 | 22.3713 | 22.3478 | 22.012 | 21.2217 | 22.1908 | 21.5993 | 21.7655 | 21.8962 | 21.0842 | 21.1705 | 21.3948 | 20.4704 | 20.6111 | 20.8981 | 21.8652 | 21.6307 | 21.2568 | 48.8053 | 42.3395 | 67.7288 | 22.0858 | 21.6804 | 21.1874 | 21.9978 | 21.7287 | 21.3538 | 20.6292 | 60.0785 |  | 25.3114 | 33.949 | 39.5188 | 26.6921 |  | 16.8534 | 16.8122 | 16.4908 | 16.6549 | 16.7611 | 17.8505 | 21.9271 | 15.9424 | 17.015 | 16.0304 | 17.0569 | 18.0008 | 45.0915 | 48.3464 | 44.2104 | 21.4599 |  |  | 0.4635 | -0.33191 | -39.9968 | 0.53222 | 0.17755 | -197.8164 | 13.8687 | -0.33549 | -0.15598 | 0.035148 | 0.057406 | 8.828 | 9.0584 | 1.9736 | 21.8046 | 22.0065 | 22.187 | 22.2471 | 22.0639 | 21.3697 | 20.1749 | 22.1795 | 22.3505 | 22.385 | 22.3292 | 21.9568 | 21.183 | 22.2412 | 21.1222 | 17.3044 | 16.4856 | 16.4512 | 16.4127 | 17.451 | 16.8466 | 22.4163 | 22.1581 | 21.699 | 22.0821 | 21.7949 | 21.2926 | 21.9365 | 21.5097 | 20.8932 | 20.6423 | 49.8866 | 28.6742 | 22.9821 | -0.12267 | -0.17153 | 25.3472 | 22.0712 | 22.3681 | 20.1084 | 21.6598 | 22.1023 | 21.9514 | 21.7165 | 21.2883 | 21.7744 | 21.4367 | 21.0391 | 39.038 | 54.7881 | 30.8639 | 31.0364 | 22.2178 |  | 20.7744 | 32.959 | 21.0291 | 21.2331 | 20.8902 | 23.9422 |  | 22.785 |  |  | 20.5472 | 20.6792 | 22.5342 | [5 empty] | 21.9088 | 21.8146 | 21.6432 | 22.0156 | 22.5317 | 21.1361 | 21.743 | 20.1773 | 22.5696 | 74.232 |  | 20.9461 | 38.3918 | 19.0811 | 20.5752 | 45.4081 | 21.4598 | 28.3418 | 19.3433 | 27.6845 | 19.5146 | 28.487 | 18.968 | 21.5678 | 37.999 | 20.3328 | 21.5602 | 55.7155 | 19.2314 | 21.2662 | 45.1852 | 19.2971 | 28.088 | 20.2235 | 28.6702 | 19.3646 | 27.5305 | 5.3e-05 | 20.9366 | 0.069588 | 0.013083 | -27.0881 | 3.0956 | -3.41 | 51.8 | 0.87597 | -0.68367 | -7.505 | 0.86573 | 0.50093 | -16.7203 | 4.4272 | 0.38308 | 0.093265 | 0.41432 | -0.0035483 | 0.44112 | 0.25393 | 0.35742
42838.4209 | 55 | 22.9055 | 22.8643 | 22.859 | 22.775 | 22.3975 | 21.7297 | 22.7177 | 21.7886 | 22.3593 | 22.3661 | 22.3394 | 22.0042 | 21.2203 | 22.1863 | 21.5885 | 21.767 | 21.895 | 21.0829 | 21.1701 | 21.3921 | 20.4745 | 20.6041 | 20.8956 | 21.863 | 21.625 | 21.2628 | 49.3782 | 42.7971 | 68.1993 | 22.0706 | 21.6703 | 21.183 | 21.9876 | 21.7284 | 21.3454 | 20.6564 | 60.8392 |  | 25.4455 | 34.3568 | 40.0479 | 26.8015 |  | 16.853 | 16.8122 | 16.4904 | 16.6608 | 16.77 | 17.842 | 22.0839 | 15.9881 | 17.0169 | 16.035 | 17.0611 | 18.0105 | 45.0703 | 48.3541 | 44.2107 | 21.4645 |  |  | 0.23876 | -0.29971 | -40.1249 | 0.36203 | 0.25641 | -197.8506 | 13.9397 | -0.20867 | 0.024808 | 0.23635 | 0.045948 | 8.8294 | 9.0593 | 1.9741 | 21.8015 | 22.0112 | 22.1902 | 22.246 | 22.0603 | 21.3617 | 20.1702 | 22.1748 | 22.3492 | 22.3885 | 22.3351 | 21.952 | 21.1774 | 22.2382 | 20.863 | 17.2977 | 16.4561 | 16.4475 | 16.4192 | 17.4567 | 16.8482 | 22.4136 | 22.1556 | 21.7066 | 22.0842 | 21.793 | 21.2984 | 21.9378 | 21.5111 | 20.8866 | 20.6686 | 50.4613 | 29.0015 | 23.1163 | -0.048155 | 0.076111 | 25.3894 | 22.0662 | 22.364 | 20.0954 | 21.6581 | 22.1048 | 21.9477 | 21.71 | 21.2824 | 21.7794 | 21.4375 | 21.0236 | 39.9066 | 55.3768 | 31.1565 | 31.3327 | 22.1326 |  | 20.7957 | 33.1806 | 21.0818 | 21.4004 | 20.929 | 23.977 |  | 22.9028 |  |  | 20.5491 | 20.6941 | 22.5663 | [5 empty] | 21.9182 | 21.911 | 21.6512 | 22.0299 | 22.5625 | 21.14 | 21.7501 | 20.1949 | 22.6305 | 74.9098 |  | 20.9645 | 39.1355 | 19.0821 | 20.5751 | 45.8958 | 21.4983 | 28.6586 | 19.3431 | 27.9622 | 19.5146 | 28.8399 | 18.9511 | 21.5922 | 38.4303 | 20.3412 | 21.5855 | 56.4032 | 19.2264 | 21.2579 | 45.6863 | 19.2936 | 28.3584 | 20.2381 | 28.8746 | 19.3704 | 27.8399 | 0.15309 | 20.9356 | 0.070878 | 0.014237 | -27.0663 | 3.0955 | 5.98 | 52.21 | 0.62914 | -0.64966 | -7.517 | 0.71402 | 0.60197 | -16.7215 | 4.4385 | 0.38617 | 0.088877 | 0.41098 | 0.02592 | 0.44459 | 0.2518 | 0.35458
42838.4209 | 56 | 22.9027 | 22.8575 | 22.8534 | 22.7784 | 22.3959 | 21.7237 | 22.7067 | 21.7831 | 22.3524 | 22.3639 | 22.3349 | 22.0005 | 21.223 | 22.177 | 21.5846 | 21.7603 | 21.8956 | 21.082 | 21.1662 | 21.3854 | 20.4716 | 20.5985 | 20.902 | 21.8643 | 21.6219 | 21.2595 | 49.9655 | 43.2998 | 68.8228 | 22.0768 | 21.6676 | 21.1876 | 21.9946 | 21.7297 | 21.3495 | 20.69 | 61.54 |  | 25.5761 | 34.7863 | 40.5658 | 27.2474 |  | 16.8648 | 16.8147 | 16.4979 | 16.6725 | 16.7767 | 17.8485 | 22.2182 | 16.0353 | 17.0237 | 16.0513 | 17.0626 | 18.0067 | 45.0374 | 48.3465 | 44.2038 | 21.4668 |  |  | 0.47467 | -0.33914 | -41.1514 | 0.42183 | 0.22881 | -197.8256 | 13.8687 | -0.32629 | -0.021313 | 0.03242 | 0.020255 | 8.8293 | 9.0592 | 1.9743 | 21.8098 | 22.0091 | 22.1947 | 22.2437 | 22.071 | 21.3732 | 20.1799 | 22.189 | 22.3621 | 22.3912 | 22.341 | 21.9588 | 21.1833 | 22.2449 | 20.5778 | 17.2351 | 16.4012 | 16.4106 | 16.4397 | 17.4559 | 16.8396 | 22.4164 | 22.1592 | 21.7058 | 22.0817 | 21.7861 | 21.2932 | 21.9382 | 21.5129 | 20.8862 | 20.6973 | 51.1284 | 29.2226 | 23.3252 | 0.028323 | 0.021524 | 25.4367 | 22.0672 | 22.3648 | 20.094 | 21.6562 | 22.0949 | 21.9348 | 21.6948 | 21.2793 | 21.7623 | 21.427 | 21.0331 | 40.6382 | 56.1249 | 31.5475 | 31.6532 | 21.9922 |  | 20.813 | 32.9566 | 21.1158 | 21.5144 | 20.9523 | 24.0334 |  | 23.0218 |  |  | 20.5551 | 20.7082 | 22.7509 | [5 empty] | 21.9117 | 22.0071 | 21.6539 | 22.0232 | 22.5721 | 21.1402 | 21.7471 | 20.2164 | 22.7248 | 75.5737 |  | 21.0016 | 39.7621 | 19.0854 | 20.5864 | 46.4274 | 21.5554 | 29.0019 | 19.3527 | 28.2567 | 19.5351 | 29.1684 | 18.954 | 21.6491 | 38.8153 | 20.3557 | 21.6205 | 57.1136 | 19.2341 | 21.2758 | 46.1098 | 19.3068 | 28.6559 | 20.2625 | 29.1078 | 19.3867 | 28.1544 | -0.0159 | 20.9353 | 0.073238 | 0.014404 | -27.0432 | 3.0956 | 0.78 | 52.22 | 0.88789 | -0.69108 | -7.6126 | 0.77074 | 0.56865 | -16.7207 | 4.4272 | 0.39065 | 0.096238 | 0.40859 | 0.057506 | 0.44968 | 0.24055 | 0.34974
42838.4209 | 57 | 22.9012 | 22.8618 | 22.8503 | 22.78 | 22.3999 | 21.7314 | 22.7143 | 21.7895 | 22.3553 | 22.3667 | 22.3449 | 22.0078 | 21.2196 | 22.1822 | 21.5895 | 21.7672 | 21.8999 | 21.0888 | 21.1772 | 21.3917 | 20.4666 | 20.6011 | 20.8966 | 21.8636 | 21.6295 | 21.2535 | 50.4859 | 43.9429 | 69.3439 | 22.0861 | 21.6716 | 21.1953 | 21.9982 | 21.7325 | 21.3503 | 20.7233 | 61.9517 |  | 25.6993 | 35.1445 | 41.059 | 27.7347 |  | 16.8678 | 16.8228 | 16.4987 | 16.6676 | 16.7768 | 17.8411 | 22.446 | 16.0801 | 17.0113 | 16.0551 | 17.0677 | 18.0039 | 45.0325 | 48.3498 | 44.1919 | 21.4665 |  |  | 0.3439 | -0.39762 | -41.2696 | 0.41263 | 0.10593 | -197.8762 | 13.6256 | -0.21655 | 0.16589 | 0.15348 | -0.065503 | 8.8291 | 9.059 | 1.9741 | 21.7955 | 22.0036 | 22.1863 | 22.2426 | 22.0643 | 21.3702 | 20.1799 | 22.185 | 22.351 | 22.3846 | 22.333 | 21.9581 | 21.1801 | 22.2445 | 20.338 | 17.215 | 16.3893 | 16.394 | 16.4439 | 17.4604 | 16.8571 | 22.4161 | 22.1535 | 21.7078 | 22.0802 | 21.7906 | 21.2903 | 21.9335 | 21.5179 | 20.8886 | 20.7263 | 51.716 | 29.3983 | 23.5528 | 0.15651 | -0.12265 | 25.5815 | 22.07 | 22.363 | 20.0988 | 21.6615 | 22.0944 | 21.9409 | 21.7127 | 21.2939 | 21.7763 | 21.4257 | 21.0336 | 41.375 | 56.8798 | 31.9035 | 32.0416 | 21.9693 |  | 20.8306 | 32.7809 | 21.172 | 21.5932 | 20.9849 | 24.1731 |  | 23.1532 |  |  | 20.5563 | 20.7274 | 22.9143 | [5 empty] | 21.9023 | 22.1039 | 21.644 | 22.0206 | 22.601 | 21.1414 | 21.7525 | 20.2176 | 22.8452 | 76.0933 |  | 21.0166 | 40.2853 | 19.0801 | 20.5917 | 46.8993 | 21.6012 | 29.3483 | 19.3573 | 28.4691 | 19.5459 | 29.4616 | 18.9491 | 21.68 | 39.2003 | 20.3725 | 21.6494 | 57.7877 | 19.2426 | 21.2821 | 46.5705 | 19.3031 | 28.9763 | 20.2975 | 29.362 | 19.3816 | 28.4502 | 0.14938 | 20.9308 | 0.076292 | 0.01611 | -27.0341 | 3.0956 | -3.84 | 51.28 | 0.75633 | -0.74831 | -7.6236 | 0.7623 | 0.38691 | -16.7226 | 4.3882 | 0.39187 | 0.103 | 0.4075 | 0.084675 | 0.45305 | 0.22812 | 0.34439
42838.4209 | 58 | 22.904 | 22.8694 | 22.8601 | 22.7783 | 22.4019 | 21.736 | 22.7198 | 21.7954 | 22.3629 | 22.3725 | 22.3478 | 22.0038 | 21.2198 | 22.1918 | 21.5849 | 21.7583 | 21.8847 | 21.0758 | 21.1726 | 21.3782 | 20.4681 | 20.6007 | 20.8917 | 21.8666 | 21.6179 | 21.2522 | 50.9317 | 44.5723 | 69.8477 | 22.0836 | 21.6789 | 21.1892 | 21.9968 | 21.7296 | 21.3547 | 20.759 | 62.6584 |  | 25.8112 | 35.495 | 41.5049 | 28.3351 |  | 16.869 | 16.8375 | 16.511 | 16.6798 | 16.7905 | 17.8302 | 22.5889 | 16.1181 | 17.0209 | 16.0659 | 17.0784 | 18.0146 | 45.033 | 48.3566 | 44.1827 | 21.4653 |  |  | 0.3623 | -0.62695 | -42.0319 | 0.082754 | 0.13944 | -197.8552 | 13.1452 | -0.47283 | -0.10596 | -0.046255 | -0.1181 | 8.8285 | 9.0583 | 1.9737 | 21.7949 | 22.004 | 22.1899 | 22.2474 | 22.0661 | 21.3719 | 20.1765 | 22.1781 | 22.3593 | 22.3845 | 22.3344 | 21.9507 | 21.1734 | 22.2418 | 20.0856 | 17.2196 | 16.3485 | 16.3724 | 16.4024 | 17.4569 | 16.8464 | 22.4161 | 22.1599 | 21.7067 | 22.089 | 21.7995 | 21.3006 | 21.9422 | 21.5224 | 20.8914 | 20.7715 | 52.1853 | 29.5759 | 23.7364 | 0.11699 | -0.13254 | 25.5548 | 22.0652 | 22.3601 | 20.1102 | 21.6542 | 22.1006 | 21.9327 | 21.6937 | 21.2938 | 21.7789 | 21.4373 | 21.0252 | 42.0025 | 57.7053 | 32.3006 | 32.3665 | 22.0408 |  | 20.8572 | 32.2175 | 21.2153 | 21.7156 | 21.0223 | 24.3103 |  | 23.2686 |  |  | 20.5585 | 20.7381 | 23.0639 | [5 empty] | 21.9034 | 22.1739 | 21.6504 | 22.0283 | 22.6491 | 21.1335 | 21.7585 | 20.2514 | 22.985 | 76.5588 |  | 21.0406 | 40.8363 | 19.0862 | 20.6073 | 47.3381 | 21.6637 | 29.7337 | 19.3701 | 28.7082 | 19.548 | 29.7872 | 18.9486 | 21.7124 | 39.6345 | 20.3846 | 21.6887 | 58.3966 | 19.2497 | 21.3138 | 46.8813 | 19.3154 | 29.2103 | 20.3226 | 29.6055 | 19.4033 | 28.7335 | -0.042798 | 20.9318 | 0.080365 | 0.016458 | -26.9519 | 3.0955 | -2.39 | 52.96 | 0.77687 | -0.93967 | -7.6939 | 0.34139 | 0.44391 | -16.7214 | 4.3101 | 0.39078 | 0.12011 | 0.40535 | 0.11232 | 0.45634 | 0.21264 | 0.34081
42838.421 | 59 | 22.9025 | 22.8663 | 22.8574 | 22.776 | 22.3948 | 21.7298 | 22.7089 | 21.7931 | 22.3598 | 22.3667 | 22.3451 | 22.0016 | 21.2156 | 22.1909 | 21.5904 | 21.7636 | 21.889 | 21.0781 | 21.1721 | 21.3909 | 20.4743 | 20.6123 | 20.8983 | 21.8664 | 21.6272 | 21.2568 | 51.5017 | 45.1547 | 70.0145 | 22.0752 | 21.6752 | 21.1843 | 21.9956 | 21.7271 | 21.3487 | 20.7888 | 62.9203 |  | 25.9175 | 35.868 | 41.9294 | 29.0474 |  | 16.8616 | 16.8262 | 16.5081 | 16.6732 | 16.779 | 17.8123 | 22.814 | 16.1129 | 17.0165 | 16.0826 | 17.0625 | 18.0141 | 45.0337 | 48.3621 | 44.1826 | 21.4654 |  |  | 0.47927 | -0.32074 | -43.0163 | 0.15832 | 0.22092 | -197.8657 | 13.0894 | -0.60228 | 0.0074882 | -0.083599 | 0.15636 | 8.83 | 9.0601 | 1.9742 | 21.8051 | 22.0053 | 22.1941 | 22.2539 | 22.0703 | 21.368 | 20.1795 | 22.1797 | 22.3577 | 22.3937 | 22.3354 | 21.9561 | 21.184 | 22.2513 | 19.854 | 17.241 | 16.3345 | 16.3724 | 16.3739 | 17.4561 | 16.8532 | 22.4183 | 22.1488 | 21.6992 | 22.0762 | 21.7914 | 21.2888 | 21.9258 | 21.5103 | 20.8791 | 20.7851 | 52.5931 | 29.7539 | 23.7697 | -0.037145 | -0.03934 | 25.6353 | 22.065 | 22.3544 | 20.1187 | 21.6559 | 22.0935 | 21.9368 | 21.7027 | 21.2898 | 21.7731 | 21.4346 | 21.0275 | 42.6586 | 58.5862 | 32.7233 | 32.7375 | 22.1764 |  | 20.875 | 31.6937 | 21.245 | 21.8973 | 21.0531 | 24.4565 |  | 23.3752 |  |  | 20.5514 | 20.7503 | 23.3413 | [5 empty] | 21.9162 | 22.2557 | 21.6478 | 22.0247 | 22.711 | 21.1406 | 21.755 | 20.2465 | 23.1083 | 76.6952 |  | 21.0488 | 41.3187 | 19.0947 | 20.6376 | 47.7503 | 21.725 | 30.1286 | 19.3757 | 28.9883 | 19.5559 | 30.1313 | 18.9496 | 21.7247 | 40.2164 | 20.4138 | 21.7145 | 59.1294 | 19.2589 | 21.3846 | 47.3035 | 19.3207 | 29.417 | 20.3473 | 29.8249 | 19.4135 | 29.1181 | 0.025095 | 20.9274 | 0.084335 | 0.015667 | -27.0668 | 3.0955 | 4.68 | 51.59 | 0.89373 | -0.67208 | -7.7833 | 0.47219 | 0.55874 | -16.7213 | 4.3008 | 0.38761 | 0.13565 | 0.40134 | 0.13795 | 0.45868 | 0.19386 | 0.34033
42838.421 | 60 | 22.9042 | 22.8639 | 22.8543 | 22.7758 | 22.3984 | 21.7267 | 22.7138 | 21.7887 | 22.3571 | 22.3628 | 22.3412 | 22.0062 | 21.2113 | 22.1865 | 21.6029 | 21.7687 | 21.8968 | 21.0749 | 21.1861 | 21.3977 | 20.4751 | 20.6126 | 20.9011 | 21.8721 | 21.6363 | 21.263 | 52.1033 | 45.6766 | 70.2655 | 22.0782 | 21.6719 | 21.1905 | 21.997 | 21.7282 | 21.3523 | 20.8267 | 63.2823 |  | 26.049 | 36.2935 | 42.4247 | 29.7878 |  | 16.8677 | 16.8321 | 16.5098 | 16.6823 | 16.7928 | 17.8117 | 23.2921 | 16.0632 | 17.0146 | 16.1087 | 17.0632 | 18.0124 | 45.0442 | 48.3659 | 44.1668 | 21.4628 |  |  | 0.53578 | -0.24911 | -43.2226 | -0.077582 | -0.013012 | -197.8815 | 13.1715 | -0.46166 | 0.029867 | -0.065766 | 0.12667 | 8.829 | 9.0588 | 1.9745 | 21.8051 | 22.0035 | 22.1884 | 22.2494 | 22.0612 | 21.3666 | 20.1768 | 22.1806 | 22.3542 | 22.384 | 22.3349 | 21.957 | 21.1794 | 22.2463 | 19.6261 | 17.2217 | 16.3394 | 16.3715 | 16.3646 | 17.4603 | 16.8505 | 22.4149 | 22.1571 | 21.7051 | 22.0774 | 21.789 | 21.2895 | 21.9287 | 21.5122 | 20.8845 | 20.8194 | 53.2286 | 29.9773 | 23.8188 | 0.032255 | 0.0007918 | 25.6717 | 22.0688 | 22.3652 | 20.1196 | 21.6494 | 22.0933 | 21.9462 | 21.699 | 21.2899 | 21.7696 | 21.4319 | 21.024 | 43.3741 | 59.4303 | 33.1319 | 33.1803 | 22.4418 |  | 20.9099 | 31.6119 | 21.2803 | 22.0651 | 21.0981 | 24.3816 |  | 23.49 |  |  | 20.5488 | 20.7491 | 23.4672 | [5 empty] | 21.9061 | 22.3453 | 21.6531 | 22.0165 | 22.7594 | 21.1374 | 21.7481 | 20.274 | 23.2586 | 77.5173 |  | 21.0693 | 41.7549 | 19.0998 | 20.676 | 48.2525 | 21.7795 | 30.5296 | 19.3904 | 29.221 | 19.5702 | 30.4636 | 18.947 | 21.7338 | 40.7679 | 20.4348 | 21.767 | 59.7436 | 19.2681 | 21.3994 | 47.7557 | 19.3191 | 29.6485 | 20.3815 | 30.0852 | 19.4227 | 29.5168 | -0.001802 | 20.9257 | 0.089109 | 0.01574 | -27.0289 | 3.0955 | 2.37 | 52.86 | 0.9453 | -0.59231 | -7.802 | -0.33055 | -0.1356 | -16.722 | 4.3142 | 0.38141 | 0.13911 | 0.39818 | 0.16377 | 0.45782 | 0.17456 | 0.34012
42838.421 | 61 | 22.911 | 22.8697 | 22.8534 | 22.7784 | 22.4082 | 21.729 | 22.7162 | 21.7894 | 22.3606 | 22.3682 | 22.344 | 22.0024 | 21.2172 | 22.1819 | 21.5925 | 21.763 | 21.8864 | 21.0715 | 21.1728 | 21.3841 | 20.4729 | 20.5994 | 20.888 | 21.8706 | 21.6245 | 21.2608 | 52.6222 | 46.1469 | 70.9339 | 22.0768 | 21.683 | 21.1962 | 22.0028 | 21.73 | 21.3476 | 20.8839 | 63.6343 |  | 26.2236 | 36.8259 | 43.0083 | 30.4821 |  | 16.8793 | 16.8421 | 16.5225 | 16.6968 | 16.82 | 17.8613 | 23.9063 | 16.0206 | 17.0223 | 16.1519 | 17.0709 | 18.0094 | 45.0485 | 48.3583 | 44.1576 | 21.4601 |  |  | 0.50621 | -0.53693 | -43.9145 | 0.10444 | 0.2045 | -197.823 | 12.9987 | -0.46626 | 0.085134 | -0.24263 | 0.031192 | 8.8284 | 9.0583 | 1.975 | 21.8037 | 22.0047 | 22.1939 | 22.2535 | 22.0601 | 21.3711 | 20.1786 | 22.1822 | 22.353 | 22.3933 | 22.331 | 21.9574 | 21.1817 | 22.2445 | 19.4266 | 17.2228 | 16.3467 | 16.36 | 16.3631 | 17.4688 | 16.8477 | 22.4196 | 22.1645 | 21.6979 | 22.0879 | 21.7984 | 21.2939 | 21.9427 | 21.5173 | 20.8884 | 20.8535 | 53.7694 | 30.2471 | 23.943 | 0.0082694 | -0.16773 | 25.7063 | 22.0642 | 22.3591 | 20.1225 | 21.6436 | 22.0985 | 21.9299 | 21.6961 | 21.2906 | 21.7629 | 21.425 | 21.027 | 43.9303 | 60.4668 | 33.4927 | 33.587 | 22.5781 |  | 20.9528 | 31.476 | 21.3361 | 22.2835 | 21.1376 | 24.6565 |  | 23.6176 |  |  | 20.5488 | 20.7661 | 23.6504 | [5 empty] | 21.9098 | 22.429 | 21.6512 | 22.0212 | 22.8181 | 21.1438 | 21.7476 | 20.286 | 23.4103 | 78.3691 |  | 21.0911 | 42.0899 | 19.0961 | 20.6846 | 48.709 | 21.8189 | 30.8534 | 19.3847 | 29.494 | 19.58 | 30.7973 | 18.9416 | 21.7449 | 41.1933 | 20.4481 | 21.8691 | 60.1701 | 19.2742 | 21.4012 | 48.2246 | 19.3277 | 29.9246 | 20.4172 | 30.3114 | 19.431 | 29.907 | 0.092989 | 20.9266 | 0.093847 | 0.016103 | -27.0478 | 3.0955 | 5.6 | 51.77 | 0.91974 | -0.8696 | -7.8644 | 0.38352 | 0.53761 | -16.7209 | 4.2862 | 0.37906 | 0.14476 | 0.39345 | 0.18693 | 0.45668 | 0.1572 | 0.33782
42838.421 | 62 | 22.9022 | 22.8677 | 22.8523 | 22.7755 | 22.3981 | 21.7278 | 22.708 | 21.7879 | 22.3612 | 22.3674 | 22.3411 | 22.0051 | 21.2182 | 22.1786 | 21.5943 | 21.7691 | 21.8944 | 21.0823 | 21.1752 | 21.3946 | 20.4686 | 20.6019 | 20.9014 | 21.8713 | 21.6349 | 21.264 | 53.0867 | 46.6483 | 71.4253 | 22.0864 | 21.6793 | 21.1963 | 22.0012 | 21.7308 | 21.3577 | 20.9207 | 64.2584 |  | 26.3641 | 37.343 | 43.5346 | 30.831 |  | 16.8711 | 16.8337 | 16.5387 | 16.7189 | 16.8522 | 17.8952 | 24.5166 | 15.9918 | 17.0159 | 16.1754 | 17.0612 | 18.0081 | 45.066 | 48.3559 | 44.155 | 21.4618 |  |  | 0.72503 | -0.27671 | -44.8128 | 0.45534 | 0.063872 | -197.8 | 12.6057 | -0.59571 | -0.008469 | -0.22458 | 0.051677 | 8.8283 | 9.0583 | 1.9746 | 21.8085 | 22.0113 | 22.1929 | 22.2543 | 22.0659 | 21.3771 | 20.1795 | 22.1855 | 22.3555 | 22.3915 | 22.3321 | 21.9575 | 21.1851 | 22.2491 | 19.2529 | 17.2408 | 16.3613 | 16.3523 | 16.3648 | 17.4717 | 16.8524 | 22.4136 | 22.1574 | 21.6974 | 22.0776 | 21.7936 | 21.2879 | 21.9359 | 21.5074 | 20.8814 | 20.8799 | 54.343 | 30.5838 | 24.3578 | -0.039111 | -0.10135 | 25.7836 | 22.0714 | 22.3598 | 20.1178 | 21.6466 | 22.0984 | 21.9314 | 21.702 | 21.2954 | 21.7772 | 21.4274 | 21.0347 | 44.4948 | 61.1896 | 33.8813 | 33.9572 | 22.7015 |  | 20.9674 | 31.1754 | 21.3619 | 22.6001 | 21.1697 | 24.8609 |  | 23.698 |  |  | 20.5537 | 20.7729 | 23.8722 | [5 empty] | 21.9041 | 22.5254 | 21.6466 | 22.0184 | 22.8568 | 21.1415 | 21.7501 | 20.3156 | 23.5748 | 79.5195 |  | 21.133 | 42.42 | 19.1023 | 20.7179 | 49.1217 | 21.8782 | 31.1875 | 19.3856 | 29.9173 | 19.5857 | 31.1254 | 18.9468 | 21.7673 | 41.5968 | 20.4737 | 22.0108 | 60.7318 | 19.288 | 21.4207 | 48.7744 | 19.3403 | 30.1891 | 20.4527 | 30.5801 | 19.4535 | 30.2616 | 0.033814 | 20.9148 | 0.098578 | 0.017351 | -27.0174 | 3.0955 | 9.88 | 51.62 | 1.1015 | -0.62426 | -7.9443 | 0.80079 | 0.30047 | -16.7209 | 4.2212 | 0.37613 | 0.15398 | 0.38573 | 0.20657 | 0.45561 | 0.14874 | 0.32718
42838.421 | 63 | 22.903 | 22.8685 | 22.8488 | 22.7707 | 22.4004 | 21.7321 | 22.7135 | 21.787 | 22.357 | 22.363 | 22.3363 | 22.0017 | 21.2094 | 22.1836 | 21.5877 | 21.7583 | 21.889 | 21.0784 | 21.1658 | 21.3906 | 20.4654 | 20.5954 | 20.8981 | 21.8726 | 21.6268 | 21.2564 | 53.5769 | 47.0986 | 72.2199 | 22.0893 | 21.6802 | 21.2093 | 22.0025 | 21.7337 | 21.3612 | 20.9766 | 65.1379 |  | 26.5113 | 37.8444 | 44.0339 | 30.0865 |  | 16.8786 | 16.8505 | 16.5531 | 16.7422 | 16.8819 | 17.9109 | 24.832 | 15.971 | 17.0216 | 16.2055 | 17.0776 | 18.0135 | 45.0761 | 48.3646 | 44.14 | 21.4601 |  |  | 0.42999 | -0.31614 | -44.3233 | 0.82858 | 0.19661 | -197.8749 | 12.68 | -0.43997 | -0.13165 | -0.17067 | 0.032234 | 8.8281 | 9.0582 | 1.9735 | 21.7978 | 21.9991 | 22.1838 | 22.2502 | 22.0624 | 21.3643 | 20.1729 | 22.1808 | 22.3548 | 22.3784 | 22.3315 | 21.9525 | 21.1745 | 22.2405 | 19.1057 | 17.2703 | 16.3726 | 16.3253 | 16.3845 | 17.4668 | 16.8482 | 22.4155 | 22.1559 | 21.7049 | 22.0772 | 21.7969 | 21.2878 | 21.9288 | 21.5091 | 20.8818 | 20.9236 | 54.9342 | 30.9604 | 25.0847 | -0.055232 | -0.21356 | 25.8968 | 22.0731 | 22.3646 | 20.1241 | 21.653 | 22.0949 | 21.9419 | 21.7095 | 21.3092 | 21.7779 | 21.4328 | 21.0298 | 45.1864 | 62.2711 | 34.2572 | 34.3206 | 23.0522 |  | 20.9955 | 30.9701 | 21.3991 | 23.0046 | 21.2071 | 24.9948 |  | 23.7827 |  |  | 20.5577 | 20.7836 | 23.8684 | [5 empty] | 21.9029 | 22.6079 | 21.6448 | 22.0207 | 22.901 | 21.1381 | 21.7496 | 20.3348 | 23.7192 | 80.4138 |  | 21.1657 | 42.7663 | 19.1138 | 20.7654 | 49.5176 | 21.9479 | 31.5541 | 19.3921 | 30.24 | 19.5975 | 31.4286 | 18.9417 | 21.786 | 41.9941 | 20.4921 | 22.1281 | 61.4027 | 19.2967 | 21.4325 | 49.2813 | 19.3407 | 30.4677 | 20.4817 | 30.8753 | 19.4622 | 30.5514 | 0.14011 | 20.9129 | 0.10311 | 0.017874 | -27.0138 | 3.0956 | 0.49 | 52.72 | 0.84925 | -0.66727 | -7.901 | 1.0803 | 0.52718 | -16.7245 | 4.2337 | 0.36732 | 0.16093 | 0.37575 | 0.22235 | 0.45387 | 0.17129 | 0.30845
42838.421 | 64 | 22.9109 | 22.875 | 22.8514 | 22.7805 | 22.4045 | 21.7413 | 22.7109 | 21.789 | 22.3631 | 22.3655 | 22.3383 | 22.0026 | 21.2143 | 22.1876 | 21.5891 | 21.7568 | 21.8891 | 21.0728 | 21.1684 | 21.3838 | 20.4649 | 20.6023 | 20.8975 | 21.8647 | 21.6245 | 21.2579 | 54.262 | 47.5982 | 73.6252 | 22.0823 | 21.6758 | 21.2042 | 21.9989 | 21.735 | 21.3612 | 21.0122 | 65.9082 |  | 26.6534 | 38.2967 | 44.5069 | 29.1987 |  | 16.8812 | 16.8613 | 16.5605 | 16.7586 | 16.8915 | 17.9203 | 25.2302 | 15.974 | 17.0252 | 16.2195 | 17.0818 | 18.0132 | 45.105 | 48.3709 | 44.135 | 21.4567 |  |  | 0.48058 | -0.22611 | -45.4134 | 0.69256 | 0.21961 | -197.8736 | 12.31 | -0.30066 | -0.17446 | -0.13626 | -0.064982 | 8.8279 | 9.0581 | 1.9727 | 21.793 | 22.0038 | 22.1856 | 22.2449 | 22.0553 | 21.3712 | 20.1736 | 22.1815 | 22.3505 | 22.3822 | 22.3347 | 21.9547 | 21.1703 | 22.2427 | 18.9458 | 17.2797 | 16.4069 | 16.3177 | 16.4026 | 17.4677 | 16.8431 | 22.4209 | 22.1654 | 21.7056 | 22.0855 | 21.7936 | 21.2966 | 21.9367 | 21.5135 | 20.8892 | 20.9723 | 55.7976 | 31.6384 | 25.9425 | -0.090817 | -0.24038 | 26.0354 | 22.0744 | 22.3611 | 20.122 | 21.6569 | 22.1038 | 21.9406 | 21.6998 | 21.3098 | 21.7668 | 21.4411 | 21.031 | 45.7726 | 62.9645 | 34.658 | 34.7352 | 23.337 |  | 21.0349 | 31.8144 | 21.462 | 23.6765 | 21.2486 | 25.0284 |  | 23.8813 |  |  | 20.5546 | 20.7868 | 23.7866 | [5 empty] | 21.9049 | 22.682 | 21.6492 | 22.0177 | 22.9247 | 21.1374 | 21.7486 | 20.3457 | 23.8475 | 81.2308 |  | 21.182 | 43.1115 | 19.1244 | 20.8369 | 49.8362 | 22.0201 | 31.9392 | 19.391 | 30.5259 | 19.6139 | 31.7161 | 18.9386 | 21.818 | 42.3959 | 20.5175 | 22.2499 | 61.9691 | 19.307 | 21.4613 | 49.7452 | 19.3379 | 30.7358 | 20.5048 | 31.1449 | 19.4699 | 30.8299 | 0.10783 | 20.908 | 0.1084 | 0.01815 | -26.9929 | 3.0955 | -8.69 | 51.28 | 0.89965 | -0.56434 | -7.9977 | 0.98765 | 0.55717 | -16.7248 | 4.1715 | 0.36074 | 0.13959 | 0.35847 | 0.24022 | 0.44946 | 0.19715 | 0.28626
42838.421 | 65 | 22.9166 | 22.8834 | 22.8586 | 22.7836 | 22.4082 | 21.7438 | 22.7226 | 21.7948 | 22.3661 | 22.3718 | 22.345 | 22.0092 | 21.2272 | 22.1951 | 21.5911 | 21.758 | 21.8953 | 21.0759 | 21.1761 | 21.3858 | 20.4615 | 20.605 | 20.8951 | 21.8675 | 21.6298 | 21.2662 | 54.9146 | 48.1606 | 74.3175 | 22.0784 | 21.673 | 21.1942 | 21.9967 | 21.7308 | 21.3538 | 21.0477 | 66.9012 |  | 26.8069 | 38.7423 | 44.9888 | 28.8902 |  | 16.8952 | 16.8891 | 16.6004 | 16.7958 | 16.9121 | 17.9572 | 25.6055 | 16.0462 | 17.0224 | 16.2277 | 17.0755 | 18.0079 | 45.1113 | 48.3693 | 44.1187 | 21.4514 |  |  | 0.62252 | 0.12347 | -46.3498 | 0.57953 | 0.10921 | -197.8729 | 12.0958 | -0.54248 | -0.023259 | 0.020672 | -0.0076944 | 8.8287 | 9.0584 | 1.9719 | 21.8041 | 22.0144 | 22.1917 | 22.2539 | 22.0591 | 21.3732 | 20.1915 | 22.1852 | 22.362 | 22.394 | 22.3402 | 21.9629 | 21.1843 | 22.2459 | 18.811 | 17.2821 | 16.3982 | 16.3451 | 16.4058 | 17.4701 | 16.8437 | 22.4197 | 22.1652 | 21.711 | 22.0865 | 21.7932 | 21.2996 | 21.9429 | 21.5174 | 20.8925 | 21.0183 | 56.5822 | 32.1812 | 26.3998 | -0.30845 | -0.031162 | 26.2301 | 22.0665 | 22.3494 | 20.118 | 21.6452 | 22.0922 | 21.9363 | 21.7014 | 21.2981 | 21.7652 | 21.4322 | 21.03 | 46.274 | 63.5686 | 34.9871 | 35.051 | 23.4464 |  | 21.0711 | 33.2453 | 21.5124 | 24.3405 | 21.291 | 24.997 |  | 23.997 |  |  | 20.556 | 20.7851 | 23.8243 | [5 empty] | 21.9167 | 22.7752 | 21.6548 | 22.0238 | 22.9704 | 21.1421 | 21.7591 | 20.3591 | 23.9392 | 81.9944 |  | 21.1967 | 43.4526 | 19.122 | 20.9008 | 50.1606 | 22.0849 | 32.312 | 19.391 | 30.8454 | 19.6232 | 31.9846 | 18.9392 | 21.8427 | 42.7661 | 20.5419 | 22.3437 | 62.6475 | 19.3071 | 21.5116 | 50.3041 | 19.3453 | 31.0017 | 20.5401 | 31.3926 | 19.4852 | 31.1049 | 0.008586 | 20.8993 | 0.11337 | 0.018527 | -27.0783 | 3.0956 | 4.47 | 52.77 | 1.0249 | 0.41704 | -8.0801 | 0.90351 | 0.39294 | -16.7258 | 4.1353 | 0.35891 | 0.10153 | 0.34146 | 0.25549 | 0.45049 | 0.20691 | 0.2751
42838.421 | 66 | 22.8999 | 22.8645 | 22.8511 | 22.7758 | 22.3974 | 21.7331 | 22.7146 | 21.789 | 22.36 | 22.3656 | 22.3392 | 22.0032 | 21.2126 | 22.1832 | 21.5964 | 21.7704 | 21.8968 | 21.0794 | 21.1838 | 21.3947 | 20.4739 | 20.6097 | 20.8989 | 21.8766 | 21.63 | 21.2734 | 55.6688 | 48.6941 | 75.0078 | 22.0859 | 21.6745 | 21.1957 | 21.9985 | 21.7309 | 21.3594 | 21.085 | 67.6401 |  | 26.9571 | 39.1724 | 45.4345 | 29.35 |  | 16.8942 | 16.9052 | 16.61 | 16.7995 | 16.9278 | 17.9918 | 25.8999 | 16.0963 | 17.0173 | 16.2808 | 17.0784 | 18.0125 | 45.1319 | 48.3784 | 44.1211 | 21.4605 |  |  | 0.6442 | -0.29774 | -47.091 | 0.33706 | 0.0665 | -197.8197 | 12.0945 | -0.24678 | 0.16336 | -0.087795 | 0.01227 | 8.8282 | 9.0582 | 1.9718 | 21.8047 | 22.013 | 22.1905 | 22.2457 | 22.067 | 21.3792 | 20.1812 | 22.1864 | 22.3643 | 22.3925 | 22.3384 | 21.9592 | 21.1845 | 22.2519 | 18.6996 | 17.2653 | 16.4477 | 16.4169 | 16.4597 | 17.4741 | 16.8445 | 22.4148 | 22.1588 | 21.7049 | 22.0874 | 21.7944 | 21.297 | 21.9375 | 21.515 | 20.889 | 21.0575 | 57.1005 | 32.4912 | 26.6959 | -0.02358 | -0.15327 | 26.4702 | 22.0593 | 22.3628 | 20.1269 | 21.6509 | 22.0947 | 21.9316 | 21.7008 | 21.3066 | 21.7706 | 21.4358 | 21.0347 | 46.9391 | 64.0862 | 35.2905 | 35.3779 | 23.5076 |  | 21.1098 | 34.3239 | 21.5682 | 24.8738 | 21.3344 | 25.1861 |  | 24.0948 |  |  | 20.5522 | 20.7818 | 23.9702 | [5 empty] | 21.9139 | 22.8729 | 21.6506 | 22.0225 | 23 | 21.1405 | 21.7542 | 20.3737 | 24.009 | 82.9088 |  | 21.2166 | 43.8806 | 19.1255 | 20.975 | 50.6087 | 22.1436 | 32.6828 | 19.4009 | 31.2158 | 19.6281 | 32.2484 | 18.9446 | 21.8561 | 43.1782 | 20.5622 | 22.424 | 63.3329 | 19.314 | 21.5229 | 50.9471 | 19.3546 | 31.2857 | 20.5773 | 31.643 | 19.4984 | 31.434 | 0.1683 | 20.8783 | 0.11893 | 0.019384 | -27.0317 | 3.0956 | -9.96 | 51.64 | 1.0437 | -0.64763 | -8.1447 | 0.68906 | 0.30664 | -16.7245 | 4.1354 | 0.35851 | 0.073446 | 0.3281 | 0.26833 | 0.44508 | 0.19539 | 0.26819
42838.4211 | 67 | 22.9092 | 22.8626 | 22.8525 | 22.776 | 22.3963 | 21.7368 | 22.7131 | 21.7882 | 22.3539 | 22.3603 | 22.3424 | 22.0055 | 21.214 | 22.1853 | 21.5977 | 21.7659 | 21.8919 | 21.0766 | 21.1738 | 21.3912 | 20.4778 | 20.6055 | 20.897 | 21.8704 | 21.6231 | 21.2655 | 56.4327 | 49.2551 | 75.9665 | 22.077 | 21.6701 | 21.193 | 21.989 | 21.7241 | 21.3522 | 21.1254 | 67.9169 |  | 27.081 | 39.5576 | 45.8815 | 30.0746 |  | 16.9044 | 16.9145 | 16.6209 | 16.8315 | 16.9835 | 18.0258 | 26.4177 | 16.093 | 17.02 | 16.328 | 17.0804 | 18.0059 | 45.141 | 48.3799 | 44.1066 | 21.4572 |  |  | 0.4129 | -0.19063 | -48.5045 | 0.20235 | 0.50808 | -197.8204 | 11.5451 | -0.3828 | -0.072687 | -0.032408 | 0.066606 | 8.8281 | 9.0583 | 1.9723 | 21.8094 | 22.0146 | 22.1931 | 22.2497 | 22.0658 | 21.3684 | 20.1744 | 22.184 | 22.3566 | 22.3892 | 22.3363 | 21.9549 | 21.1813 | 22.2444 | 18.5942 | 17.2561 | 16.5844 | 16.456 | 16.4786 | 17.4695 | 16.8466 | 22.4114 | 22.1576 | 21.7062 | 22.0867 | 21.7952 | 21.288 | 21.9347 | 21.5091 | 20.8867 | 21.0926 | 57.6173 | 32.7927 | 26.6557 | -0.090817 | -0.097542 | 26.702 | 22.06 | 22.3645 | 20.1247 | 21.6482 | 22.0947 | 21.9293 | 21.7015 | 21.3079 | 21.7645 | 21.421 | 21.0336 | 47.5604 | 64.7293 | 35.6086 | 35.6555 | 23.5497 |  | 21.1625 | 35.0669 | 21.6284 | 25.2488 | 21.3744 | 25.4191 |  | 24.18 |  |  | 20.5516 | 20.7772 | 24.1362 | [5 empty] | 21.9029 | 22.9619 | 21.6441 | 22.0191 | 23.0193 | 21.1339 | 21.7406 | 20.3914 | 24.0962 | 83.8127 |  | 21.2378 | 44.3524 | 19.1349 | 21.0481 | 51.1684 | 22.2154 | 33.0369 | 19.4108 | 31.5926 | 19.635 | 32.5299 | 18.9445 | 21.859 | 43.6788 | 20.5883 | 22.5031 | 64.0408 | 19.3295 | 21.5288 | 51.4047 | 19.3617 | 31.5824 | 20.6098 | 31.9002 | 19.5075 | 31.7825 | 0.16162 | 20.8591 | 0.12481 | 0.019014 | -26.9998 | 3.0955 | 9.41 | 52.37 | 0.83671 | -0.51821 | -8.2662 | 0.5339 | 0.84764 | -16.7255 | 4.0406 | 0.35911 | 0.054828 | 0.31902 | 0.27949 | 0.43014 | 0.17662 | 0.27049
42838.4211 | 68 | 22.902 | 22.8623 | 22.8503 | 22.7769 | 22.3994 | 21.7302 | 22.7082 | 21.7808 | 22.3616 | 22.3672 | 22.3427 | 22.0018 | 21.2139 | 22.1856 | 21.6024 | 21.7728 | 21.8929 | 21.0848 | 21.181 | 21.3966 | 20.4739 | 20.6087 | 20.8982 | 21.8724 | 21.6274 | 21.2751 | 56.9266 | 49.8207 | 76.2806 | 22.0773 | 21.6814 | 21.205 | 21.9994 | 21.7306 | 21.367 | 21.1815 | 68.1772 |  | 27.2303 | 40.0127 | 46.4252 | 30.4064 |  | 16.9118 | 16.9211 | 16.6277 | 16.8692 | 17.0373 | 18.0607 | 26.7979 | 16.0948 | 17.0224 | 16.328 | 17.0921 | 18.0136 | 45.1508 | 48.3808 | 44.0974 | 21.4609 |  |  | 0.53052 | -0.12426 | -48.6885 | 0.18329 | 0.13287 | -197.8401 | 11.3368 | -0.15741 | 0.14215 | -0.051919 | 0.080321 | 8.8296 | 9.0599 | 1.9724 | 21.8084 | 22.0019 | 22.1938 | 22.2487 | 22.0629 | 21.3734 | 20.178 | 22.1842 | 22.3528 | 22.3882 | 22.3385 | 21.9553 | 21.1759 | 22.2414 | 18.5059 | 17.363 | 16.8607 | 16.5312 | 16.525 | 17.4758 | 16.8684 | 22.4219 | 22.1545 | 21.707 | 22.0846 | 21.8017 | 21.2971 | 21.9406 | 21.5155 | 20.8874 | 21.1532 | 58.2835 | 33.0851 | 26.9888 | 0.012005 | -0.28051 | 26.968 | 22.0649 | 22.3639 | 20.1197 | 21.6523 | 22.0929 | 21.9418 | 21.7038 | 21.3116 | 21.7652 | 21.4252 | 21.0312 | 48.1758 | 65.3983 | 35.8639 | 35.9872 | 23.5577 |  | 21.2078 | 36.0096 | 21.6911 | 25.3136 | 21.4218 | 25.3449 |  | 24.2999 |  |  | 20.5543 | 20.7752 | 24.3267 | [5 empty] | 21.9019 | 23.0639 | 21.6484 | 22.0133 | 23.0624 | 21.1358 | 21.7377 | 20.4083 | 24.1796 | 84.3146 |  | 21.2598 | 44.7627 | 19.1385 | 21.1115 | 51.6634 | 22.2736 | 33.4093 | 19.4212 | 31.9092 | 19.6495 | 32.8057 | 18.9464 | 21.8622 | 44.1781 | 20.613 | 22.587 | 64.7719 | 19.3412 | 21.5367 | 51.7879 | 19.3688 | 31.8679 | 20.6312 | 32.1566 | 19.5166 | 32.1152 | 0.31336 | 20.8431 | 0.13025 | 0.018542 | -27.0858 | 3.0955 | 10.3 | 52.63 | 0.94885 | -0.4184 | -8.2819 | 0.50815 | 0.43349 | -16.7274 | 4.0042 | 0.36041 | 0.030748 | 0.31881 | 0.29004 | 0.40199 | 0.16928 | 0.26327
42838.4211 | 69 | 22.9017 | 22.8611 | 22.849 | 22.7767 | 22.3983 | 21.7283 | 22.7088 | 21.7889 | 22.3573 | 22.3607 | 22.3422 | 21.9996 | 21.21 | 22.1804 | 21.5955 | 21.7693 | 21.891 | 21.0819 | 21.1759 | 21.3968 | 20.4673 | 20.6082 | 20.9041 | 21.867 | 21.6209 | 21.2729 | 57.3077 | 50.3854 | 76.4293 | 22.087 | 21.6779 | 21.2001 | 22.0027 | 21.7352 | 21.3618 | 21.2273 | 68.2769 |  | 27.4133 | 40.5649 | 46.9953 | 30.7464 |  | 16.9168 | 16.9234 | 16.6329 | 16.913 | 17.0835 | 18.0805 | 26.947 | 16.1133 | 17.0189 | 16.3142 | 17.0945 | 18.0132 | 45.1492 | 48.3819 | 44.0853 | 21.4603 |  |  | 0.56009 | -0.16829 | -48.3553 | 0.63276 | 0.18807 | -197.844 | 11.2034 | -0.30132 | 0.13573 | 0.18515 | -0.038074 | 8.8284 | 9.0585 | 1.9722 | 21.803 | 21.998 | 22.1915 | 22.2512 | 22.0645 | 21.3699 | 20.1798 | 22.1808 | 22.3502 | 22.3901 | 22.3351 | 21.9536 | 21.18 | 22.2416 | 18.4206 | 17.4091 | 16.9508 | 16.5259 | 16.5682 | 17.4645 | 16.8626 | 22.4231 | 22.166 | 21.7103 | 22.0921 | 21.8 | 21.3018 | 21.9492 | 21.5144 | 20.8964 | 21.2174 | 58.7594 | 33.4057 | 27.2796 | -0.074106 | -0.21223 | 27.2723 | 22.0612 | 22.3597 | 20.1239 | 21.654 | 22.093 | 21.94 | 21.703 | 21.3196 | 21.7732 | 21.4327 | 21.0289 | 48.7538 | 66.0999 | 36.1684 | 36.2912 | 23.6174 |  | 21.2513 | 37.3885 | 21.7483 | 25.4665 | 21.4643 | 25.4 |  | 24.4063 |  |  | 20.5496 | 20.7716 | 24.5114 | [5 empty] | 21.9072 | 23.1546 | 21.652 | 22.0087 | 23.1017 | 21.1355 | 21.7454 | 20.4332 | 24.2816 | 84.9344 |  | 21.2919 | 45.1563 | 19.1506 | 21.1983 | 52.2331 | 22.3306 | 33.7235 | 19.4446 | 32.1948 | 19.6664 | 33.0582 | 18.936 | 21.8675 | 44.6138 | 20.6218 | 22.6545 | 65.5347 | 19.3332 | 21.6032 | 52.2871 | 19.3735 | 32.1223 | 20.6518 | 32.4463 | 19.5323 | 32.4705 | 0.13528 | 20.8337 | 0.1358 | 0.017722 | -27.1014 | 3.0955 | 8.81 | 51.95 | 0.97515 | -0.48691 | -8.2536 | 0.94415 | 0.51575 | -16.7281 | 3.9807 | 0.36021 | -0.0056335 | 0.31599 | 0.29821 | 0.3913 | 0.16138 | 0.25734
42838.4211 | 70 | 22.9092 | 22.8612 | 22.8584 | 22.7798 | 22.3925 | 21.7312 | 22.7146 | 21.7881 | 22.365 | 22.3689 | 22.3414 | 22.0001 | 21.2139 | 22.1831 | 21.5932 | 21.7688 | 21.8918 | 21.0717 | 21.1831 | 21.3929 | 20.4732 | 20.6082 | 20.897 | 21.8686 | 21.6253 | 21.2684 | 57.857 | 51.0125 | 76.7129 | 22.0829 | 21.6763 | 21.1983 | 21.996 | 21.7307 | 21.3604 | 21.2699 | 69.3607 |  | 27.5829 | 41.0842 | 47.5014 | 31.0261 |  | 16.921 | 16.9299 | 16.6286 | 16.9101 | 17.0892 | 18.0954 | 27.4217 | 16.1763 | 17.0245 | 16.2947 | 17.0931 | 18.0143 | 45.1511 | 48.3827 | 44.0892 | 21.4567 |  |  | 0.51475 | -0.42259 | -48.8061 | 0.3456 | 0.14076 | -197.8355 | 11.0753 | -0.17581 | 0.07735 | -0.16311 | -0.06776 | 8.8283 | 9.0581 | 1.9725 | 21.8028 | 22.0075 | 22.1858 | 22.2486 | 22.062 | 21.3651 | 20.1756 | 22.1804 | 22.3501 | 22.3876 | 22.3317 | 21.9556 | 21.178 | 22.2418 | 18.3425 | 17.408 | 16.9177 | 16.519 | 16.5831 | 17.467 | 16.8598 | 22.4139 | 22.1534 | 21.7062 | 22.0809 | 21.7911 | 21.2928 | 21.9406 | 21.5166 | 20.8867 | 21.2505 | 59.2507 | 33.7159 | 27.1506 | -0.037145 | -0.08689 | 27.4559 | 22.0743 | 22.3686 | 20.1222 | 21.6542 | 22.1083 | 21.9458 | 21.7123 | 21.3244 | 21.7731 | 21.4327 | 21.0361 | 49.3111 | 66.6406 | 36.5134 | 36.6459 | 23.8767 |  | 21.2986 | 38.1347 | 21.8119 | 25.6339 | 21.4988 | 25.4769 |  | 24.5075 |  |  | 20.556 | 20.7762 | 24.5938 | [5 empty] | 21.9103 | 23.2343 | 21.6379 | 22.0052 | 23.1372 | 21.1338 | 21.737 | 20.4504 | 24.4473 | 85.3833 |  | 21.3105 | 45.5935 | 19.164 | 21.2746 | 52.6943 | 22.3888 | 34.0781 | 19.453 | 32.4765 | 19.6759 | 33.3226 | 18.9439 | 21.9624 | 44.9891 | 20.6442 | 22.75 | 66.1663 | 19.352 | 21.7797 | 52.8386 | 19.3787 | 32.3791 | 20.6839 | 32.726 | 19.5552 | 32.7618 | 0.23749 | 20.824 | 0.14157 | 0.016996 | -27.0862 | 3.0955 | 8.53 | 52.94 | 0.93522 | -0.77159 | -8.2921 | 0.69777 | 0.4462 | -16.7282 | 3.958 | 0.35459 | -0.024225 | 0.3125 | 0.30718 | 0.39466 | 0.15504 | 0.26204
42838.4211 | 71 | 22.9061 | 22.8637 | 22.8589 | 22.7804 | 22.3982 | 21.7343 | 22.709 | 21.7871 | 22.3591 | 22.3689 | 22.3418 | 22.0004 | 21.2157 | 22.1866 | 21.5961 | 21.7685 | 21.895 | 21.0822 | 21.1792 | 21.39 | 20.4664 | 20.6011 | 20.8956 | 21.8676 | 21.6267 | 21.2741 | 58.4105 | 51.6673 | 76.9073 | 22.09 | 21.6805 | 21.2007 | 21.9958 | 21.7321 | 21.3671 | 21.322 | 70.6423 |  | 27.756 | 41.5714 | 47.9575 | 31.1505 |  | 16.9345 | 16.9446 | 16.6403 | 16.9186 | 17.1074 | 18.1122 | 27.5197 | 16.1921 | 17.0246 | 16.314 | 17.0966 | 18.0135 | 45.1436 | 48.3825 | 44.0893 | 21.4576 |  |  | 0.41421 | -0.30365 | -48.72 | 0.11232 | 0.17361 | -197.8381 | 11.2047 | -0.0825 | 0.054387 | 0.17005 | -0.031825 | 8.8296 | 9.0593 | 1.9719 | 21.8007 | 22.011 | 22.1963 | 22.2543 | 22.0682 | 21.3731 | 20.1862 | 22.191 | 22.3581 | 22.3896 | 22.3385 | 21.9549 | 21.1826 | 22.2494 | 18.2684 | 17.3703 | 16.9004 | 16.504 | 16.5423 | 17.4596 | 16.8576 | 22.4127 | 22.1587 | 21.7069 | 22.0826 | 21.7948 | 21.2935 | 21.9352 | 21.5142 | 20.8886 | 21.3048 | 59.4316 | 33.9382 | 27.3059 | -0.022793 | -0.16088 | 27.5306 | 22.0648 | 22.3616 | 20.1204 | 21.6467 | 22.0998 | 21.9339 | 21.7063 | 21.3309 | 21.7729 | 21.429 | 21.0342 | 49.9093 | 67.2465 | 36.8529 | 37.0032 | 24.6326 |  | 21.3627 | 37.4393 | 21.8698 | 25.713 | 21.5494 | 25.721 |  | 24.627 |  |  | 20.5668 | 20.79 | 24.8063 | [5 empty] | 21.9031 | 23.3237 | 21.6409 | 22.0168 | 23.1778 | 21.1295 | 21.7397 | 20.4645 | 24.6455 | 85.7904 |  | 21.3429 | 45.9665 | 19.1674 | 21.3637 | 53.026 | 22.437 | 34.4008 | 19.4702 | 32.753 | 19.6891 | 33.5987 | 18.9429 | 22.1555 | 45.3823 | 20.6592 | 22.8264 | 66.728 | 19.3582 | 21.9091 | 53.4211 | 19.3886 | 32.6262 | 20.7054 | 32.9711 | 19.5639 | 33.0986 | 0.13157 | 20.814 | 0.14814 | 0.017693 | -27.0418 | 3.0955 | -8.4 | 51.59 | 0.83917 | -0.65407 | -8.285 | 0.3978 | 0.49556 | -16.7288 | 3.9812 | 0.33575 | -0.0029602 | 0.312 | 0.31454 | 0.39632 | 0.15333 | 0.25954
42838.4211 | 72 | 22.9104 | 22.8712 | 22.8536 | 22.7834 | 22.4068 | 21.74 | 22.7165 | 21.7906 | 22.3655 | 22.3769 | 22.3476 | 22.0083 | 21.2148 | 22.1909 | 21.5928 | 21.7658 | 21.8942 | 21.0824 | 21.181 | 21.3921 | 20.4703 | 20.6049 | 20.8937 | 21.8644 | 21.628 | 21.2743 | 58.7944 | 52.2367 | 76.5232 | 22.0815 | 21.6745 | 21.2044 | 21.9986 | 21.729 | 21.3638 | 21.3708 | 72.0502 |  | 27.9251 | 41.9833 | 48.4257 | 31.3657 |  | 16.9352 | 16.9601 | 16.641 | 16.9204 | 17.1098 | 18.112 | 27.7617 | 16.2032 | 17.0204 | 16.3205 | 17.0966 | 18.0128 | 45.1369 | 48.385 | 44.0957 | 21.4558 |  |  | 0.61069 | -0.38054 | -49.4113 | 0.20366 | 0.25312 | -197.8144 | 10.9288 | -0.1561 | 0.024224 | 0.092004 | -0.058733 | 8.8292 | 9.0591 | 1.9713 | 21.8041 | 22.0166 | 22.194 | 22.2563 | 22.0659 | 21.3696 | 20.1771 | 22.1849 | 22.3606 | 22.3865 | 22.3381 | 21.9585 | 21.1825 | 22.2487 | 18.2116 | 17.3595 | 16.8613 | 16.4923 | 16.4977 | 17.46 | 16.861 | 22.4172 | 22.1611 | 21.7077 | 22.0903 | 21.7978 | 21.2924 | 21.9385 | 21.5167 | 20.8965 | 21.3649 | 59.6571 | 34.1739 | 27.8331 | -0.018272 | -0.30619 | 27.6226 | 22.0656 | 22.3546 | 20.1237 | 21.6457 | 22.0978 | 21.9332 | 21.7073 | 21.3283 | 21.7711 | 21.435 | 21.0323 | 50.3991 | 67.7707 | 37.2536 | 37.3892 | 25.3025 |  | 21.3998 | 36.1864 | 21.8963 | 25.8088 | 21.5878 | 25.9775 |  | 24.716 |  |  | 20.5819 | 20.8073 | 24.9869 | [5 empty] | 21.9064 | 23.4059 | 21.6429 | 22.0116 | 23.2133 | 21.1336 | 21.743 | 20.4769 | 24.805 | 85.9544 |  | 21.3584 | 46.3768 | 19.1816 | 21.4568 | 53.4237 | 22.5026 | 34.7139 | 19.4839 | 33.0271 | 19.6981 | 33.89 | 18.9572 | 22.2298 | 45.8 | 20.6878 | 22.9293 | 67.4202 | 19.3657 | 21.956 | 53.9591 | 19.4018 | 32.9373 | 20.7286 | 33.2734 | 19.591 | 33.4713 | -0.0060685 | 20.8032 | 0.15462 | 0.018738 | -27.0581 | 3.0955 | -5.07 | 53.27 | 1.0184 | -0.73223 | -8.3438 | 0.53568 | 0.59837 | -16.7278 | 3.9318 | 0.31838 | 0.03273 | 0.31063 | 0.3209 | 0.40106 | 0.14899 | 0.24692
42838.4211 | 73 | 22.9098 | 22.8709 | 22.8509 | 22.7771 | 22.4011 | 21.7282 | 22.7151 | 21.783 | 22.3625 | 22.3694 | 22.3408 | 22.0022 | 21.2113 | 22.1888 | 21.5929 | 21.7655 | 21.8949 | 21.0796 | 21.176 | 21.3913 | 20.4744 | 20.6027 | 20.8991 | 21.8647 | 21.6264 | 21.275 | 59.1627 | 52.7031 | 76.2055 | 22.0807 | 21.6748 | 21.2064 | 22.0003 | 21.7286 | 21.3639 | 21.4217 | 72.5669 |  | 28.0903 | 42.3765 | 48.9364 | 31.7149 |  | 16.9343 | 16.9563 | 16.6443 | 16.9202 | 17.1053 | 18.1052 | 28.2405 | 16.2286 | 17.0194 | 16.3283 | 17.1012 | 18.0159 | 45.152 | 48.3849 | 44.1115 | 21.4551 |  |  | 0.65012 | -0.2938 | -50.1913 | 0.27726 | 0.42923 | -197.7783 | 10.5259 | -0.051616 | -0.021313 | -0.077515 | 0.060357 | 8.8289 | 9.0586 | 1.9722 | 21.7989 | 22.007 | 22.1931 | 22.2479 | 22.0687 | 21.363 | 20.1759 | 22.1848 | 22.3596 | 22.3833 | 22.3393 | 21.9546 | 21.1782 | 22.246 | 18.1499 | 17.3773 | 16.835 | 16.4806 | 16.4865 | 17.4632 | 16.8722 | 22.4138 | 22.1659 | 21.7074 | 22.0875 | 21.7932 | 21.291 | 21.9386 | 21.5168 | 20.894 | 21.4114 | 60.2257 | 34.4509 | 28.0958 | 0.031468 | -0.27367 | 27.5878 | 22.071 | 22.363 | 20.1324 | 21.6585 | 22.1004 | 21.9381 | 21.7084 | 21.3389 | 21.7742 | 21.4362 | 21.0434 | 50.9078 | 68.3959 | 37.67 | 37.8125 | 25.1441 |  | 21.4358 | 36.1744 | 21.9344 | 25.9096 | 21.6444 | 26.1339 |  | 24.824 |  |  | 20.5873 | 20.8188 | 25.0438 | [5 empty] | 21.901 | 23.4989 | 21.6468 | 22.0099 | 23.2506 | 21.1344 | 21.7532 | 20.4952 | 24.9161 | 86.2751 |  | 21.3895 | 46.7893 | 19.1848 | 21.55 | 53.9609 | 22.5365 | 35.1557 | 19.4965 | 33.3539 | 19.7088 | 34.2667 | 18.9499 | 22.2207 | 46.2929 | 20.7133 | 23.0593 | 68.0375 | 19.3753 | 22.0271 | 54.4773 | 19.3907 | 33.327 | 20.7517 | 33.5298 | 19.6004 | 33.8557 | 0.075366 | 20.7936 | 0.16143 | 0.018469 | -27.0657 | 3.0955 | 7.83 | 55.65 | 1.0503 | -0.64338 | -8.4093 | 0.62501 | 0.7792 | -16.726 | 3.8586 | 0.32399 | 0.034346 | 0.30973 | 0.32814 | 0.40528 | 0.141 | 0.24118
42838.4211 | 74 | 22.9133 | 22.8702 | 22.861 | 22.787 | 22.4018 | 21.7366 | 22.724 | 21.7937 | 22.3642 | 22.3712 | 22.3472 | 22.0068 | 21.2135 | 22.189 | 21.601 | 21.7659 | 21.8918 | 21.0784 | 21.1727 | 21.3907 | 20.4677 | 20.6029 | 20.8943 | 21.8676 | 21.6258 | 21.2831 | 59.7561 | 53.2472 | 76.4734 | 22.0868 | 21.6809 | 21.2022 | 22.0003 | 21.7309 | 21.3765 | 21.4731 | 72.4146 |  | 28.2527 | 42.7472 | 49.4856 | 31.8177 |  | 16.9345 | 16.9582 | 16.6431 | 16.9223 | 17.1011 | 18.1 | 28.4884 | 16.2561 | 17.0183 | 16.3298 | 17.1032 | 18.0132 | 45.1559 | 48.3788 | 44.1183 | 21.4485 |  |  | 0.59032 | -0.14792 | -50.8819 | 0.3364 | 0.2978 | -197.8769 | 10.409 | 0.025924 | -0.0098312 | -0.025484 | -0.042067 | 8.8278 | 9.0577 | 1.9721 | 21.8008 | 22.0141 | 22.196 | 22.2558 | 22.0641 | 21.3765 | 20.1851 | 22.1817 | 22.3651 | 22.3927 | 22.3382 | 21.9671 | 21.1856 | 22.2502 | 18.0938 | 17.3881 | 16.7459 | 16.4625 | 16.487 | 17.4666 | 16.8728 | 22.411 | 22.1485 | 21.7057 | 22.084 | 21.7932 | 21.2951 | 21.9365 | 21.5107 | 20.8852 | 21.4719 | 60.8684 | 34.7562 | 28.5688 | 0.067839 | -0.22726 | 27.8577 | 22.0647 | 22.3553 | 20.1299 | 21.6506 | 22.0959 | 21.9364 | 21.7048 | 21.3311 | 21.7612 | 21.4231 | 21.0252 | 51.5107 | 69.0734 | 38.0659 | 38.2273 | 24.8895 |  | 21.4756 | 36.8485 | 21.9835 | 26.1396 | 21.7053 | 26.3381 |  | 24.9549 |  |  | 20.6 | 20.8318 | 25.3016 | [5 empty] | 21.9095 | 23.6114 | 21.6481 | 22.0174 | 23.2908 | 21.1369 | 21.744 | 20.5035 | 24.9957 | 86.2693 |  | 21.4052 | 47.1995 | 19.1794 | 21.6107 | 54.4389 | 22.5838 | 35.4723 | 19.5047 | 33.723 | 19.7138 | 34.6198 | 18.9438 | 22.2188 | 46.6529 | 20.7223 | 23.1971 | 68.577 | 19.3805 | 22.0999 | 54.874 | 19.3928 | 33.6488 | 20.7662 | 33.7584 | 19.6087 | 34.1998 | 0.16645 | 20.7847 | 0.16764 | 0.017649 | -27.0614 | 3.0955 | 7.77 | 54.92 | 1.0012 | -0.45652 | -8.467 | 0.68845 | 0.64903 | -16.7301 | 3.8371 | 0.3324 | 0.017272 | 0.30539 | 0.33476 | 0.41526 | 0.13987 | 0.23007
42838.4211 | 75 | 22.9078 | 22.87 | 22.8598 | 22.7763 | 22.4052 | 21.7375 | 22.7171 | 21.7827 | 22.3582 | 22.3653 | 22.34 | 22.0044 | 21.2162 | 22.1825 | 21.6026 | 21.7747 | 21.8976 | 21.0849 | 21.1801 | 21.4047 | 20.481 | 20.6101 | 20.9003 | 21.865 | 21.6343 | 21.2914 | 60.4209 | 53.6952 | 77.3149 | 22.0903 | 21.674 | 21.2037 | 21.9907 | 21.7398 | 21.369 | 21.5207 | 71.9928 |  | 28.3996 | 43.0907 | 50.065 | 31.8203 |  | 16.9386 | 16.9523 | 16.6378 | 16.9121 | 17.0965 | 18.0636 | 28.3874 | 16.2651 | 17.0215 | 16.3003 | 17.1092 | 18.0097 | 45.1655 | 48.3656 | 44.1215 | 21.4508 |  |  | 0.46481 | -0.52444 | -51.6961 | 0.24769 | 0.22486 | -197.8499 | 10.2289 | 0.08572 | -0.11686 | 0.0028386 | -0.045539 | 8.83 | 9.06 | 1.9696 | 21.8021 | 22.0062 | 22.192 | 22.2442 | 22.0609 | 21.3682 | 20.1807 | 22.1754 | 22.3593 | 22.3905 | 22.3341 | 21.9573 | 21.1784 | 22.2457 | 18.0354 | 17.4007 | 16.7243 | 16.437 | 16.4973 | 17.4692 | 16.8732 | 22.4173 | 22.1484 | 21.7045 | 22.0823 | 21.7871 | 21.285 | 21.9331 | 21.5051 | 20.8848 | 21.5116 | 61.1237 | 35.1396 | 28.7395 | -0.015716 | -0.12132 | 28.2778 | 22.0693 | 22.3555 | 20.1295 | 21.6534 | 22.0922 | 21.935 | 21.7013 | 21.3473 | 21.7714 | 21.4273 | 21.0325 | 52.0329 | 69.721 | 38.4298 | 38.6155 | 24.7506 |  | 21.5169 | 37.7983 | 22.0515 | 26.5455 | 21.7471 | 26.3345 |  | 25.0632 |  |  | 20.6108 | 20.8449 | 25.584 | [5 empty] | 21.9059 | 23.7617 | 21.6402 | 22.0135 | 23.3122 | 21.1265 | 21.7361 | 20.5105 | 25.089 | 86.7149 |  | 21.4304 | 47.5662 | 19.1895 | 21.6579 | 54.838 | 22.6263 | 35.8292 | 19.5095 | 34.0262 | 19.7239 | 34.9479 | 18.9448 | 22.2351 | 47.0232 | 20.7543 | 23.3529 | 69.3629 | 19.386 | 22.1791 | 55.3327 | 19.3756 | 33.9869 | 20.7931 | 34.0085 | 19.625 | 34.5969 | 0.32134 | 20.773 | 0.17361 | 0.017758 | -27.081 | 3.0955 | 13.93 | 52.83 | 0.88946 | -0.85959 | -8.5344 | 0.59074 | 0.56394 | -16.7279 | 3.8035 | 0.33765 | -0.0068276 | 0.29552 | 0.34155 | 0.41771 | 0.1414 | 0.22667
42838.4212 | 76 | 22.899 | 22.8597 | 22.8542 | 22.7722 | 22.4002 | 21.7232 | 22.7147 | 21.7781 | 22.3598 | 22.367 | 22.3408 | 21.9903 | 21.2076 | 22.1816 | 21.593 | 21.7621 | 21.8901 | 21.0702 | 21.1765 | 21.3919 | 20.4717 | 20.5992 | 20.9005 | 21.8661 | 21.6276 | 21.2808 | 60.8392 | 54.1401 | 76.9693 | 22.0756 | 21.6655 | 21.2031 | 21.9923 | 21.7394 | 21.3712 | 21.5715 | 71.2712 |  | 28.5684 | 43.466 | 50.6416 | 31.5017 |  | 16.9422 | 16.9604 | 16.642 | 16.9156 | 17.0996 | 18.0586 | 28.2074 | 16.2611 | 17.0206 | 16.3403 | 17.1152 | 18.0206 | 45.1676 | 48.3589 | 44.1315 | 21.4509 |  |  | 0.58441 | -0.45216 | -52.6128 | 0.65904 | 0.073072 | -197.8841 | 10.0686 | 0.1534 | -0.10266 | 0.11823 | -0.023145 | 8.8284 | 9.0583 | 1.9664 | 21.802 | 22.0067 | 22.1869 | 22.2454 | 22.0586 | 21.3707 | 20.1779 | 22.1841 | 22.3517 | 22.3892 | 22.3329 | 21.9574 | 21.1789 | 22.2433 | 17.9663 | 17.4059 | 16.7461 | 16.4406 | 16.4844 | 17.467 | 16.8671 | 22.4147 | 22.1543 | 21.7022 | 22.0875 | 21.792 | 21.2858 | 21.9308 | 21.51 | 20.8854 | 21.5573 | 61.6366 | 35.6696 | 28.797 | -0.0015606 | -0.11751 | 28.5434 | 22.0643 | 22.3574 | 20.1242 | 21.6412 | 22.0913 | 21.9369 | 21.7018 | 21.343 | 21.7659 | 21.4241 | 21.0384 | 52.5341 | 70.3855 | 38.8125 | 38.9765 | 25.0191 |  | 21.5568 | 38.7518 | 22.1161 | 26.6705 | 21.8002 | 26.2276 |  | 25.1564 |  |  | 20.614 | 20.8583 | 25.7252 | [5 empty] | 21.9014 | 23.8594 | 21.6386 | 22.0121 | 23.3442 | 21.1319 | 21.7384 | 20.5312 | 25.2065 | 86.7916 |  | 21.4674 | 47.9261 | 19.2076 | 21.7605 | 55.2089 | 22.6787 | 36.2271 | 19.5332 | 34.341 | 19.7366 | 35.282 | 18.9419 | 22.2557 | 47.4409 | 20.7737 | 23.5016 | 70.0068 | 19.3841 | 22.2464 | 55.8284 | 19.3717 | 34.3595 | 20.807 | 34.2967 | 19.6302 | 34.9481 | 0.11024 | 20.7604 | 0.17991 | 0.016662 | -27.0365 | 3.0955 | 5.82 | 51.61 | 0.99686 | -0.79817 | -8.6098 | 0.96362 | 0.32147 | -16.7292 | 3.7736 | 0.33153 | -0.031141 | 0.29383 | 0.34898 | 0.41458 | 0.15195 | 0.2266
42838.4212 | 77 | 22.8998 | 22.8668 | 22.861 | 22.7786 | 22.3965 | 21.7313 | 22.7166 | 21.7884 | 22.3611 | 22.3668 | 22.3491 | 21.9966 | 21.2169 | 22.1844 | 21.5979 | 21.7684 | 21.8963 | 21.0824 | 21.1812 | 21.3891 | 20.4697 | 20.6081 | 20.9031 | 21.8686 | 21.6291 | 21.2888 | 61.2393 | 54.7108 | 76.9944 | 22.0758 | 21.6725 | 21.2009 | 21.9933 | 21.7325 | 21.368 | 21.6175 | 70.9875 |  | 28.7093 | 43.8057 | 51.1559 | 31.2655 |  | 16.9472 | 16.9719 | 16.6488 | 16.9149 | 17.0965 | 18.0567 | 28.2133 | 16.2416 | 17.0198 | 16.3935 | 17.1103 | 18.0136 | 45.1693 | 48.3445 | 44.1317 | 21.4436 |  |  | 0.88865 | -0.28525 | -53.4933 | 0.37517 | 0.015904 | -197.8749 | 9.8636 | 0.02198 | 0.12872 | -0.053178 | -0.090675 | 8.8292 | 9.0589 | 1.9647 | 21.8044 | 22.0078 | 22.1978 | 22.2513 | 22.0626 | 21.367 | 20.1788 | 22.1888 | 22.354 | 22.3915 | 22.3376 | 21.9591 | 21.1867 | 22.2478 | 17.9242 | 17.3976 | 16.7805 | 16.4544 | 16.46 | 17.4668 | 16.8728 | 22.4205 | 22.1602 | 21.7084 | 22.0879 | 21.7949 | 21.293 | 21.934 | 21.5071 | 20.8884 | 21.6122 | 61.9745 | 35.9567 | 28.8712 | -0.088261 | -0.20462 | 28.69 | 22.066 | 22.3503 | 20.1227 | 21.6409 | 22.0924 | 21.9353 | 21.6984 | 21.3507 | 21.7592 | 21.4294 | 21.0309 | 53.0282 | 71.0331 | 39.2153 | 39.359 | 25.7031 |  | 21.6042 | 39.9487 | 22.1763 | 26.5609 | 21.8645 | 26.3459 |  | 25.2798 |  |  | 20.6088 | 20.8685 | 25.8643 | [5 empty] | 21.9048 | 23.9593 | 21.6444 | 22.0194 | 23.3677 | 21.1291 | 21.7437 | 20.5399 | 25.3452 | 87.0318 |  | 21.5122 | 48.3059 | 19.1949 | 21.9174 | 55.6033 | 22.7142 | 36.6 | 19.554 | 34.6432 | 19.7451 | 35.6071 | 18.9474 | 22.2873 | 47.8588 | 20.7979 | 23.6503 | 70.4108 | 19.3889 | 22.307 | 56.2516 | 19.3761 | 34.7526 | 20.8272 | 34.7378 | 19.6507 | 35.3253 | 0.094843 | 20.7507 | 0.18617 | 0.0164 | -27.0531 | 3.0955 | 3.06 | 53.91 | 1.2293 | -0.63398 | -8.6817 | 0.72706 | 0.14998 | -16.7287 | 3.735 | 0.31412 | -0.062368 | 0.29904 | 0.35363 | 0.41141 | 0.16006 | 0.22639
42838.4212 | 78 | 22.9076 | 22.8665 | 22.8578 | 22.777 | 22.394 | 21.7293 | 22.7106 | 21.783 | 22.3613 | 22.3698 | 22.3383 | 21.9975 | 21.2178 | 22.1844 | 21.5965 | 21.7709 | 21.8916 | 21.0801 | 21.1785 | 21.3859 | 20.4692 | 20.6049 | 20.9026 | 21.8677 | 21.6276 | 21.2909 | 61.9683 | 55.215 | 77.7937 | 22.0856 | 21.6861 | 21.2165 | 22.0024 | 21.7433 | 21.3805 | 21.6599 | 70.7068 |  | 28.8576 | 44.1496 | 51.688 | 30.8976 |  | 16.9445 | 16.9554 | 16.6419 | 16.907 | 17.0899 | 18.0337 | 28.3154 | 16.2088 | 17.0199 | 16.3309 | 17.1097 | 18.0183 | 45.1818 | 48.3399 | 44.1227 | 21.4492 |  |  | 0.55681 | -0.37199 | -53.9329 | 0.72738 | 0.31358 | -197.8407 | 9.3215 | 0.1948 | 0.031229 | -0.14297 | -0.062726 | 8.828 | 9.0577 | 1.9643 | 21.7934 | 22.0015 | 22.1861 | 22.2475 | 22.0614 | 21.3673 | 20.1694 | 22.1746 | 22.3525 | 22.3889 | 22.3318 | 21.9463 | 21.1697 | 22.2403 | 17.9024 | 17.5274 | 16.7888 | 16.48 | 16.4748 | 17.4675 | 16.8727 | 22.406 | 22.1521 | 21.7074 | 22.0734 | 21.7877 | 21.2905 | 21.9422 | 21.5062 | 20.8866 | 21.671 | 62.2414 | 36.2362 | 29.0228 | -0.041077 | -0.25674 | 28.8487 | 22.0752 | 22.3691 | 20.1449 | 21.6508 | 22.0992 | 21.9421 | 21.6984 | 21.3583 | 21.7747 | 21.4351 | 21.0464 | 53.4914 | 71.571 | 39.6163 | 39.7537 | 26.2996 |  | 21.6504 | 41.0401 | 22.2275 | 26.7937 | 21.9077 | 26.9273 |  | 25.3952 |  |  | 20.5928 | 20.8951 | 26.0319 | [5 empty] | 21.9044 | 24.0501 | 21.6422 | 22.0224 | 23.4022 | 21.1298 | 21.7443 | 20.557 | 25.4677 | 87.4656 |  | 21.5593 | 48.7302 | 19.2004 | 22.0627 | 56.0211 | 22.7565 | 36.9268 | 19.5628 | 34.9778 | 19.7569 | 35.8933 | 18.9493 | 22.3007 | 48.2599 | 20.8129 | 23.7728 | 70.8599 | 19.3981 | 22.369 | 56.6615 | 19.3807 | 35.1271 | 20.8457 | 35.0994 | 19.6624 | 35.6826 | 0.22525 | 20.7407 | 0.19213 | 0.016691 | -27.0699 | 3.0955 | -0.13 | 55.51 | 0.97418 | -0.72396 | -8.7171 | 1.0123 | 0.66592 | -16.7266 | 3.6307 | 0.2991 | -0.090963 | 0.29402 | 0.35614 | 0.41047 | 0.1717 | 0.22415
42838.4212 | 79 | 22.9064 | 22.8642 | 22.8573 | 22.7761 | 22.3965 | 21.7301 | 22.7124 | 21.7813 | 22.36 | 22.3686 | 22.3378 | 22.0003 | 21.2149 | 22.1883 | 21.5936 | 21.7644 | 21.89 | 21.0802 | 21.176 | 21.3858 | 20.4665 | 20.6053 | 20.8972 | 21.8673 | 21.6255 | 21.286 | 62.6216 | 55.641 | 78.3133 | 22.0847 | 21.6799 | 21.2112 | 22.0001 | 21.7371 | 21.3784 | 21.6992 | 70.6167 |  | 28.9807 | 44.5092 | 52.1699 | 30.532 |  | 16.9508 | 16.9503 | 16.632 | 16.9075 | 17.0905 | 18.0333 | 28.7666 | 16.2029 | 17.0254 | 16.2995 | 17.1099 | 18.0203 | 45.1787 | 48.3302 | 44.1175 | 21.4525 |  |  | 0.33076 | -0.31548 | -54.5887 | 0.57625 | 0.24786 | -197.8355 | 9.1756 | 0.080464 | 0.031229 | 0.07459 | 0.085355 | 8.828 | 9.0579 | 1.9647 | 21.8011 | 22.014 | 22.1941 | 22.2557 | 22.0636 | 21.3649 | 20.1809 | 22.1858 | 22.3571 | 22.384 | 22.3381 | 21.9561 | 21.1826 | 22.2382 | 18.3158 | 17.8122 | 16.8265 | 16.5134 | 16.5197 | 17.4847 | 16.8754 | 22.4121 | 22.1569 | 21.7061 | 22.0899 | 21.8075 | 21.3008 | 21.9419 | 21.5196 | 20.8906 | 21.7566 | 62.2982 | 36.5065 | 29.4376 | 0.012005 | -0.31247 | 29.018 | 22.0641 | 22.3553 | 20.1291 | 21.6427 | 22.0862 | 21.9281 | 21.6919 | 21.3496 | 21.7627 | 21.4198 | 21.031 | 54.0145 | 72.1286 | 39.9353 | 40.1126 | 26.3127 |  | 21.6953 | 41.3622 | 22.3027 | 27.2424 | 21.9591 | 26.8456 |  | 25.5164 |  |  | 20.5936 | 20.9197 | 26.179 | [5 empty] | 21.907 | 24.1222 | 21.6433 | 22.0206 | 23.4295 | 21.1298 | 21.748 | 20.5666 | 25.5878 | 87.7029 |  | 21.6081 | 49.1841 | 19.2024 | 22.1609 | 56.4768 | 22.8017 | 37.2809 | 19.5799 | 35.338 | 19.7667 | 36.2349 | 18.9475 | 22.2925 | 48.6799 | 20.8155 | 23.8689 | 71.2018 | 19.3979 | 22.4065 | 57.0423 | 19.3751 | 35.3666 | 20.8544 | 35.3638 | 19.6699 | 35.9692 | 0.15365 | 20.7334 | 0.198 | 0.016575 | -27.0202 | 3.0955 | 2.37 | 55.37 | 0.75138 | -0.6667 | -8.7699 | 0.90104 | 0.59205 | -16.7264 | 3.6022 | 0.30025 | -0.097381 | 0.28329 | 0.31221 | 0.40661 | 0.18318 | 0.21551
42838.4212 | 80 | 22.9046 | 22.8606 | 22.8476 | 22.776 | 22.3934 | 21.7248 | 22.7092 | 21.7848 | 22.3533 | 22.3638 | 22.3376 | 21.9962 | 21.212 | 22.1816 | 21.5958 | 21.7657 | 21.8939 | 21.0796 | 21.1736 | 21.3882 | 20.4743 | 20.6076 | 20.8943 | 21.8671 | 21.6234 | 21.2909 | 63.0295 | 55.988 | 78.5587 | 22.0858 | 21.6772 | 21.2107 | 21.9937 | 21.7309 | 21.3729 | 21.7422 | 70.3656 |  | 29.1045 | 44.9019 | 52.6005 | 30.5868 |  | 16.9505 | 16.9538 | 16.632 | 16.9063 | 17.0803 | 18.0489 | 28.9491 | 16.1804 | 17.0184 | 16.3028 | 17.1104 | 18.024 | 45.1726 | 48.316 | 44.0918 | 21.4425 |  |  | 0.50621 | -0.25174 | -55.1289 | 0.20498 | 0.20121 | -197.8184 | 8.9692 | 0.002268 | -0.0078852 | 0.12159 | 0.16087 | 8.8284 | 9.0583 | 1.9651 | 21.7996 | 22.0045 | 22.1854 | 22.2473 | 22.0633 | 21.3681 | 20.1747 | 22.1752 | 22.3482 | 22.3855 | 22.3366 | 21.9505 | 21.1748 | 22.2349 | 19.2896 | 17.9047 | 16.7551 | 16.5165 | 16.53 | 17.5113 | 16.8724 | 22.4109 | 22.1573 | 21.7008 | 22.0875 | 21.7951 | 21.2995 | 21.9327 | 21.5122 | 20.8886 | 21.8037 | 62.499 | 36.7373 | 29.5783 | 0.037366 | -0.18656 | 29.0739 | 22.0629 | 22.3599 | 20.124 | 21.6442 | 22.0946 | 21.9329 | 21.6941 | 21.3604 | 21.7695 | 21.4248 | 21.0333 | 54.5789 | 72.7487 | 40.2592 | 40.5016 | 26.3646 |  | 21.7343 | 41.4506 | 22.3699 | 27.7732 | 21.9987 | 27.1707 |  | 25.6334 |  |  | 20.6041 | 20.9386 | 26.3675 | [5 empty] | 21.9072 | 24.2126 | 21.647 | 22.0206 | 23.4459 | 21.128 | 21.7493 | 20.5713 | 25.6969 | 87.925 |  | 21.6665 | 49.5522 | 19.2004 | 22.1966 | 56.9293 | 22.8463 | 37.6927 | 19.592 | 35.6631 | 19.7731 | 36.6385 | 18.949 | 22.358 | 49.1025 | 20.8432 | 23.9949 | 71.5023 | 19.4009 | 22.475 | 57.4022 | 19.3837 | 35.6037 | 20.8792 | 35.6782 | 19.6861 | 36.2412 | 0.17312 | 20.7242 | 0.20404 | 0.015645 | -26.9969 | 3.0955 | 4.07 | 53.1 | 0.92987 | -0.59555 | -8.8132 | 0.5374 | 0.53344 | -16.7261 | 3.5616 | 0.30012 | -0.097575 | 0.26987 | 0.20711 | 0.41418 | 0.1831 | 0.21318
42838.4212 | 81 | 22.9133 | 22.8724 | 22.8662 | 22.7784 | 22.3945 | 21.7319 | 22.7111 | 21.7946 | 22.3596 | 22.366 | 22.3412 | 21.9982 | 21.2128 | 22.1818 | 21.6017 | 21.7718 | 21.8934 | 21.0766 | 21.182 | 21.395 | 20.474 | 20.6119 | 20.9006 | 21.872 | 21.6309 | 21.2939 | 63.4774 | 56.304 | 78.971 | 22.0786 | 21.6672 | 21.2126 | 21.9913 | 21.7274 | 21.379 | 21.7871 | 70.1708 |  | 29.2374 | 45.2687 | 53.0119 | 31.164 |  | 16.9522 | 16.9649 | 16.6387 | 16.9108 | 17.0756 | 18.0415 | 28.9908 | 16.1698 | 17.0295 | 16.3065 | 17.1115 | 18.0292 | 45.1737 | 48.3111 | 44.0908 | 21.4467 |  |  | 0.57981 | -0.48436 | -54.8713 | 0.38108 | 0.006704 | -197.8335 | 9.0862 | 0.22306 | 0.038235 | 0.013119 | -0.004396 | 8.8288 | 9.0587 | 1.966 | 21.8059 | 22.014 | 22.1964 | 22.2502 | 22.0706 | 21.3697 | 20.1814 | 22.1814 | 22.3561 | 22.3854 | 22.3432 | 21.9558 | 21.1823 | 22.2508 | 19.6079 | 18.0545 | 16.9804 | 16.5435 | 16.5316 | 17.5339 | 16.8835 | 22.4134 | 22.158 | 21.7072 | 22.0897 | 21.7931 | 21.2925 | 21.936 | 21.5104 | 20.8892 | 21.8551 | 62.8788 | 36.9911 | 29.5623 | -0.11284 | -0.016136 | 29.0593 | 22.0703 | 22.3615 | 20.1334 | 21.6485 | 22.0966 | 21.9363 | 21.6997 | 21.3785 | 21.763 | 21.4257 | 21.0384 | 55.1664 | 73.3524 | 40.5941 | 40.9007 | 26.7401 |  | 21.7909 | 41.5839 | 22.4313 | 28.2961 | 22.0609 | 27.3738 |  | 25.767 |  |  | 20.625 | 20.9559 | 26.5571 | [5 empty] | 21.9015 | 24.3256 | 21.647 | 22.0184 | 23.4584 | 21.1301 | 21.7514 | 20.5835 | 25.8218 | 88.1568 |  | 21.7576 | 49.8865 | 19.1943 | 22.2161 | 57.3053 | 22.8964 | 38.1241 | 19.6168 | 35.9496 | 19.7929 | 37.0322 | 18.9465 | 22.5704 | 49.549 | 20.8656 | 24.1167 | 71.7998 | 19.4065 | 22.5861 | 57.8245 | 19.3924 | 35.8728 | 20.9001 | 36.2227 | 19.6971 | 36.5543 | 0.14437 | 20.7127 | 0.2106 | 0.015791 | -26.9727 | 3.0955 | 13.59 | 51.24 | 0.99576 | -0.82611 | -8.7927 | 0.73276 | 0.09737 | -16.7265 | 3.5847 | 0.29159 | -0.099214 | 0.25744 | 0.17438 | 0.39045 | 0.16857 | 0.21535
42838.4212 | 82 | 22.9103 | 22.8663 | 22.8587 | 22.7758 | 22.403 | 21.7289 | 22.713 | 21.7856 | 22.3661 | 22.3594 | 22.3424 | 22.0063 | 21.2139 | 22.177 | 21.5947 | 21.767 | 21.8928 | 21.0712 | 21.175 | 21.389 | 20.4666 | 20.6068 | 20.8958 | 21.8654 | 21.6266 | 21.2952 | 64.0435 | 56.6038 | 79.5341 | 22.0843 | 21.6775 | 21.2157 | 22.0012 | 21.7316 | 21.3824 | 21.862 | 70.3207 |  | 29.3875 | 45.5987 | 53.4267 | 31.8413 |  | 16.9593 | 16.972 | 16.6473 | 16.9127 | 17.0763 | 18.0394 | 28.9014 | 16.1803 | 17.0374 | 16.3141 | 17.1234 | 18.0266 | 45.1712 | 48.3078 | 44.0832 | 21.4497 |  |  | 0.61923 | -0.41405 | -55.1341 | 0.53222 | 0.18215 | -197.8282 | 9.3274 | 0.36434 | 0.050495 | -0.024226 | 0.16157 | 8.8274 | 9.0576 | 1.9656 | 21.8084 | 22.0159 | 22.1997 | 22.254 | 22.074 | 21.3768 | 20.1846 | 22.1904 | 22.3621 | 22.3905 | 22.3449 | 21.9575 | 21.1843 | 22.2557 | 19.6537 | 18.0101 | 17.9021 | 16.5329 | 16.5369 | 17.5438 | 16.886 | 22.4123 | 22.1653 | 21.7085 | 22.0838 | 21.7981 | 21.294 | 21.9385 | 21.5136 | 20.8853 | 21.9112 | 63.3875 | 37.4321 | 29.595 | -0.18479 | -0.20348 | 29.1614 | 22.0641 | 22.3567 | 20.1263 | 21.6457 | 22.0923 | 21.9252 | 21.6979 | 21.3745 | 21.7583 | 21.4288 | 21.039 | 55.7588 | 74.0932 | 40.9244 | 41.2445 | 26.9355 |  | 21.8335 | 42.4212 | 22.4992 | 28.5022 | 22.1189 | 27.428 |  | 25.8807 |  |  | 20.6424 | 20.9573 | 26.5891 | [5 empty] | 21.9107 | 24.4133 | 21.6474 | 22.0169 | 23.4859 | 21.1347 | 21.7525 | 20.6024 | 25.975 | 88.3628 |  | 21.8459 | 50.2341 | 19.1943 | 22.2579 | 57.7445 | 22.9446 | 38.5928 | 19.6445 | 36.3025 | 19.8082 | 37.3899 | 18.9439 | 22.8118 | 49.9656 | 20.8782 | 24.2311 | 72.3175 | 19.4156 | 22.6968 | 58.2513 | 19.405 | 36.1548 | 20.9217 | 36.7428 | 19.716 | 36.9093 | 0.11265 | 20.7037 | 0.21642 | 0.01537 | -27.0453 | 3.0954 | -9.71 | 54.38 | 1.0299 | -0.76381 | -8.8139 | 0.86597 | 0.50754 | -16.7263 | 3.6319 | 0.28759 | -0.12019 | 0.25366 | 0.17045 | 0.28832 | 0.15228 | 0.21633
42838.4212 | 83 | 22.904 | 22.8676 | 22.8566 | 22.7762 | 22.4011 | 21.7382 | 22.71 | 21.7876 | 22.3619 | 22.3713 | 22.3422 | 22.0113 | 21.2185 | 22.1875 | 21.5879 | 21.7658 | 21.893 | 21.0766 | 21.1751 | 21.3923 | 20.4657 | 20.5972 | 20.8892 | 21.8592 | 21.6254 | 21.2999 | 64.5478 | 56.9095 | 79.386 | 22.0922 | 21.6838 | 21.2183 | 22.0075 | 21.7331 | 21.3821 | 21.9497 | 70.2908 |  | 29.5506 | 45.9525 | 53.8611 | 32.4807 |  | 16.9499 | 16.9645 | 16.6443 | 16.9126 | 17.0611 | 18.0388 | 28.9331 | 16.1415 | 17.0339 | 16.3045 | 17.1193 | 18.0259 | 45.1669 | 48.3073 | 44.0776 | 21.4558 |  |  | 0.4405 | -0.48305 | -55.3444 | 0.44679 | 0.1539 | -197.8361 | 9.1204 | 0.18298 | 0.27545 | -0.035345 | 0.036226 | 8.8285 | 9.0584 | 1.9646 | 21.8051 | 22.0117 | 22.1868 | 22.2426 | 22.0659 | 21.3742 | 20.1869 | 22.1861 | 22.3565 | 22.3948 | 22.3385 | 21.954 | 21.1809 | 22.2462 | 19.7048 | 17.8592 | 17.7788 | 16.5403 | 16.5443 | 17.5539 | 16.8903 | 22.4119 | 22.1618 | 21.7054 | 22.0848 | 21.7889 | 21.2938 | 21.9323 | 21.5075 | 20.8896 | 21.9544 | 64.0634 | 38.0582 | 29.4911 | -0.048155 | -0.16202 | 29.3611 | 22.0605 | 22.3537 | 20.1263 | 21.644 | 22.0941 | 21.9381 | 21.6928 | 21.3764 | 21.7605 | 21.4274 | 21.0469 | 56.3202 | 74.7713 | 41.2961 | 41.5927 | 26.8973 |  | 21.8681 | 43.6763 | 22.5661 | 28.5991 | 22.1708 | 27.3605 |  | 25.9751 |  |  | 20.6524 | 20.9631 | 26.5791 | [5 empty] | 21.9129 | 24.4772 | 21.6463 | 22.0195 | 23.5079 | 21.1352 | 21.7509 | 20.6197 | 26.1373 | 88.7349 |  | 21.9124 | 50.6004 | 19.1937 | 22.3284 | 58.1532 | 22.9979 | 39.1376 | 19.6631 | 36.7079 | 19.8155 | 37.6805 | 18.9447 | 22.9407 | 50.3701 | 20.8916 | 24.3333 | 72.81 | 19.4193 | 22.7801 | 58.653 | 19.4158 | 36.4476 | 20.9521 | 37.11 | 19.7252 | 37.2249 | 0.099852 | 20.6927 | 0.2228 | 0.015602 | -27.0558 | 3.0955 | 4.99 | 55.17 | 0.86844 | -0.82498 | -8.8306 | 0.79342 | 0.46652 | -16.7266 | 3.5914 | 0.28982 | -0.1528 | 0.25272 | 0.16595 | 0.30253 | 0.13746 | 0.22067
42838.4212 | 84 | 22.9004 | 22.8694 | 22.8502 | 22.778 | 22.4037 | 21.737 | 22.7186 | 21.7893 | 22.3681 | 22.3665 | 22.3413 | 22.0076 | 21.2193 | 22.1839 | 21.5883 | 21.7676 | 21.8965 | 21.0754 | 21.163 | 21.3872 | 20.4631 | 20.5992 | 20.8969 | 21.861 | 21.6264 | 21.2999 | 64.9928 | 57.2727 | 79.5088 | 22.0911 | 21.6831 | 21.219 | 21.9997 | 21.7376 | 21.3983 | 22.0148 | 71.2919 |  | 29.7029 | 46.28 | 54.2933 | 33.1563 |  | 16.9626 | 16.9669 | 16.6503 | 16.9274 | 17.0775 | 18.0634 | 28.943 | 16.1059 | 17.0286 | 16.2805 | 17.1166 | 18.031 | 45.1601 | 48.3057 | 44.0684 | 21.4429 |  |  | 0.51147 | -0.4009 | -55.4272 | 0.36071 | 0.032332 | -197.8841 | 9.146 | 0.34002 | 0.22427 | 0.1155 | 0.15184 | 8.8289 | 9.0588 | 1.9633 | 21.799 | 22.0066 | 22.1909 | 22.244 | 22.0631 | 21.3723 | 20.1782 | 22.1802 | 22.3559 | 22.3952 | 22.334 | 21.9558 | 21.1802 | 22.2438 | 20.0872 | 17.6877 | 17.4455 | 16.5589 | 16.5537 | 17.568 | 16.8952 | 22.4063 | 22.1544 | 21.699 | 22.0823 | 21.7912 | 21.2913 | 21.9329 | 21.5133 | 20.887 | 22.0025 | 64.9218 | 38.5474 | 29.5185 | 0.12682 | -0.13254 | 29.5727 | 22.0698 | 22.3635 | 20.1428 | 21.6479 | 22.0985 | 21.9405 | 21.7037 | 21.3886 | 21.7662 | 21.4356 | 21.0512 | 56.8587 | 75.3378 | 41.6544 | 41.9642 | 26.9021 |  | 21.9075 | 44.7427 | 22.6387 | 28.7622 | 22.2194 | 27.3663 |  | 26.078 |  |  | 20.6512 | 20.9688 | 26.604 | [5 empty] | 21.9041 | 24.574 | 21.6453 | 22.0124 | 23.5388 | 21.1306 | 21.7402 | 20.631 | 26.2738 | 89.0196 |  | 21.9639 | 51.0176 | 19.1854 | 22.4324 | 58.4103 | 23.0303 | 39.596 | 19.6765 | 37.0375 | 19.8257 | 37.9805 | 18.9488 | 23.0283 | 50.7282 | 20.912 | 24.4288 | 73.0425 | 19.4272 | 22.8645 | 58.9598 | 19.4277 | 36.7544 | 20.9685 | 37.3789 | 19.7339 | 37.5535 | 0.26198 | 20.682 | 0.22883 | 0.015493 | -27.0486 | 3.0954 | 4.73 | 54.9 | 0.93595 | -0.75158 | -8.8372 | 0.71291 | 0.21384 | -16.7293 | 3.5966 | 0.291 | -0.17998 | 0.24982 | 0.1251 | 0.34014 | 0.12088 | 0.22152
42838.4213 | 85 | 22.9015 | 22.8673 | 22.8558 | 22.7696 | 22.3907 | 21.7325 | 22.7126 | 21.7852 | 22.3695 | 22.3583 | 22.3402 | 22.0047 | 21.2145 | 22.1774 | 21.5981 | 21.7702 | 21.9005 | 21.0872 | 21.186 | 21.3919 | 20.4691 | 20.6145 | 20.9055 | 21.8758 | 21.6368 | 21.3126 | 65.4244 | 57.6563 | 79.6627 | 22.0907 | 21.6774 | 21.2173 | 22.0034 | 21.7299 | 21.3941 | 22.0755 | 71.3085 |  | 29.8357 | 46.5834 | 54.6566 | 33.4846 |  | 16.967 | 16.9811 | 16.6602 | 16.948 | 17.0797 | 18.1114 | 28.7897 | 16.0935 | 17.0342 | 16.2278 | 17.1219 | 18.0282 | 45.1538 | 48.308 | 44.0565 | 21.4446 |  |  | 0.60806 | -0.32468 | -55.9923 | 0.45074 | 0.24655 | -197.8887 | 9.194 | 0.14749 | 0.13067 | 0.093892 | 0.029456 | 8.8287 | 9.0586 | 1.9624 | 21.8002 | 22.0093 | 22.1917 | 22.2453 | 22.0663 | 21.3668 | 20.1742 | 22.1794 | 22.3531 | 22.3849 | 22.3389 | 21.9544 | 21.1801 | 22.2439 | 21.0065 | 17.6803 | 17.2857 | 16.5151 | 16.5483 | 17.5979 | 16.8975 | 22.4124 | 22.164 | 21.7126 | 22.0862 | 21.8013 | 21.3014 | 21.9427 | 21.521 | 20.9009 | 22.063 | 65.456 | 38.8786 | 29.5212 | 0.024391 | -0.22973 | 29.6801 | 22.0637 | 22.3586 | 20.1381 | 21.646 | 22.0915 | 21.9383 | 21.7008 | 21.3908 | 21.7616 | 21.4293 | 21.0433 | 57.3484 | 75.8758 | 41.9871 | 42.3076 | 26.8344 |  | 21.9617 | 45.3089 | 22.7274 | 29.0069 | 22.3019 | 27.4606 |  | 26.1899 |  |  | 20.6617 | 20.9854 | 26.7475 | [5 empty] | 21.8967 | 24.6879 | 21.6415 | 22.0067 | 23.5799 | 21.1312 | 21.7426 | 20.6427 | 26.3611 | 89.2261 |  | 22.0313 | 51.4802 | 19.1879 | 22.5424 | 58.7735 | 23.0706 | 40.0583 | 19.6944 | 37.3296 | 19.8469 | 38.372 | 18.9377 | 23.0735 | 51.0303 | 20.9164 | 24.5448 | 73.4292 | 19.4261 | 22.9571 | 59.3127 | 19.4397 | 37.0811 | 20.983 | 37.6693 | 19.7332 | 37.8549 | 0.077777 | 20.6718 | 0.23466 | 0.015275 | -27.0537 | 3.0954 | -2.64 | 52.31 | 1.0207 | -0.67638 | -8.8824 | 0.79694 | 0.59055 | -16.7309 | 3.6063 | 0.29471 | -0.19272 | 0.24579 | 0.02645 | 0.35816 | 0.1138 | 0.22348
42838.4213 | 86 | 22.9039 | 22.8687 | 22.858 | 22.778 | 22.402 | 21.7336 | 22.7121 | 21.7842 | 22.3661 | 22.3642 | 22.3443 | 22.0079 | 21.2101 | 22.1818 | 21.6035 | 21.7742 | 21.9021 | 21.0866 | 21.1896 | 21.3985 | 20.4657 | 20.619 | 20.9127 | 21.8766 | 21.6299 | 21.317 | 66.0707 | 58.0223 | 80.938 | 22.0946 | 21.684 | 21.2237 | 22.0066 | 21.7326 | 21.3993 | 22.1339 | 71.306 |  | 29.9819 | 46.9461 | 54.9644 | 33.2593 |  | 16.973 | 16.9862 | 16.6686 | 16.9753 | 17.1187 | 18.1476 | 28.7429 | 16.075 | 17.0441 | 16.1648 | 17.1225 | 18.0346 | 45.1708 | 48.3156 | 44.0597 | 21.4541 |  |  | 0.46087 | -0.53365 | -56.2571 | 0.49411 | 0.12104 | -197.8322 | 8.8654 | 0.10084 | 0.0069044 | -0.12996 | 0.020776 | 8.8282 | 9.0582 | 1.9625 | 21.8041 | 22.0161 | 22.1982 | 22.2526 | 22.0636 | 21.3651 | 20.1848 | 22.1842 | 22.3599 | 22.3917 | 22.3339 | 21.9551 | 21.1863 | 22.245 | 22.1008 | 17.8629 | 17.5607 | 16.4796 | 16.5342 | 17.6391 | 16.9059 | 22.4132 | 22.1616 | 21.7124 | 22.0867 | 21.8016 | 21.2997 | 21.9419 | 21.5214 | 20.9023 | 22.1163 | 65.8059 | 39.1759 | 29.5812 | 0.088482 | -0.1527 | 29.8064 | 22.0674 | 22.3556 | 20.1312 | 21.6473 | 22.0856 | 21.9358 | 21.7009 | 21.4004 | 21.7681 | 21.4269 | 21.042 | 57.9121 | 76.4571 | 42.3041 | 42.6594 | 26.8124 |  | 21.9943 | 44.9825 | 22.7985 | 29.2163 | 22.3552 | 27.5344 |  | 26.2866 |  |  | 20.6648 | 20.988 | 26.8739 | [5 empty] | 21.8892 | 24.7973 | 21.6437 | 22.0087 | 23.5838 | 21.1251 | 21.7255 | 20.6428 | 26.4189 | 89.7791 |  | 22.0686 | 51.8931 | 19.1867 | 22.6198 | 59.0893 | 23.1062 | 40.4914 | 19.6992 | 37.7331 | 19.845 | 38.7615 | 18.9452 | 23.149 | 51.3253 | 20.9402 | 24.6426 | 73.9181 | 19.4351 | 23.0407 | 59.6795 | 19.4633 | 37.4729 | 21.0048 | 37.9488 | 19.7405 | 38.1454 | 0.30594 | 20.6624 | 0.23951 | 0.016168 | -27.0754 | 3.0954 | -0.89 | 51.71 | 0.89025 | -0.86715 | -8.9034 | 0.83441 | 0.41381 | -16.7295 | 3.5415 | 0.29642 | -0.18126 | 0.24177 | -0.090341 | 0.32858 | 0.12203 | 0.22361
42838.4213 | 87 | 22.9083 | 22.8719 | 22.8583 | 22.778 | 22.4043 | 21.7336 | 22.7181 | 21.7895 | 22.3673 | 22.3708 | 22.3467 | 22.0104 | 21.2147 | 22.1841 | 21.6003 | 21.7768 | 21.902 | 21.0924 | 21.1836 | 21.3991 | 20.4731 | 20.6076 | 20.9044 | 21.8695 | 21.624 | 21.3181 | 66.5508 | 58.3938 | 81.0335 | 22.0888 | 21.6807 | 21.2221 | 21.9999 | 21.7246 | 21.3921 | 22.1868 | 71.7619 |  | 30.1293 | 47.3027 | 55.2296 | 33.3969 |  | 16.9758 | 16.9886 | 16.6665 | 16.9776 | 17.156 | 18.1835 | 28.7358 | 16.0421 | 17.0373 | 16.0849 | 17.1264 | 18.0338 | 45.1916 | 48.3191 | 44.0659 | 21.4565 |  |  | 0.51212 | -0.25437 | -56.1967 | 0.41197 | 0.036932 | -197.8177 | 9.1559 | 0.21386 | 0.10887 | -0.089893 | 0.22389 | 8.8283 | 9.0582 | 1.9632 | 21.8015 | 22.0115 | 22.1939 | 22.2549 | 22.069 | 21.3792 | 20.185 | 22.1886 | 22.3583 | 22.3884 | 22.3364 | 21.9632 | 21.1836 | 22.2421 | 23.5044 | 18.3277 | 17.9248 | 16.6846 | 16.533 | 17.6844 | 16.9203 | 22.4103 | 22.1521 | 21.7001 | 22.0861 | 21.7945 | 21.2932 | 21.944 | 21.5163 | 20.8976 | 22.1568 | 66.4579 | 39.4981 | 29.8563 | 0.1105 | -0.24799 | 29.9265 | 22.0694 | 22.3573 | 20.1334 | 21.6465 | 22.0906 | 21.9318 | 21.6958 | 21.4101 | 21.7689 | 21.4278 | 21.045 | 58.5024 | 77.0218 | 42.6171 | 42.9841 | 26.9352 |  | 22.0504 | 44.3289 | 22.8868 | 29.2626 | 22.418 | 27.5808 |  | 26.4191 |  |  | 20.6781 | 21.0145 | 27.124 | [5 empty] | 21.8994 | 24.8652 | 21.6396 | 22.0036 | 23.6011 | 21.1233 | 21.7359 | 20.6608 | 26.5024 | 90.3597 |  | 22.1388 | 52.3849 | 19.2008 | 22.7107 | 59.329 | 23.1437 | 40.84 | 19.7163 | 38.0775 | 19.8561 | 39.1327 | 18.9468 | 23.2474 | 51.7212 | 20.9515 | 24.7547 | 74.4947 | 19.4333 | 23.1452 | 60.1066 | 19.4766 | 37.8018 | 21.0207 | 38.3389 | 19.7502 | 38.4963 | 0.25215 | 20.6532 | 0.24444 | 0.016023 | -27.0538 | 3.0954 | 13.21 | 55.29 | 0.93857 | -0.59869 | -8.8987 | 0.7619 | 0.22859 | -16.73 | 3.5992 | 0.29489 | -0.16014 | 0.2426 | -0.241 | 0.28981 | 0.11998 | 0.21733
42838.4213 | 88 | 22.9017 | 22.8606 | 22.8583 | 22.7755 | 22.396 | 21.7308 | 22.7128 | 21.7855 | 22.3625 | 22.3642 | 22.3379 | 22.0037 | 21.2121 | 22.1846 | 21.5963 | 21.7668 | 21.895 | 21.0789 | 21.1792 | 21.3889 | 20.4701 | 20.6073 | 20.8936 | 21.8604 | 21.6226 | 21.3199 | 66.9988 | 58.7838 | 81.0563 | 22.0902 | 21.6742 | 21.22 | 21.9902 | 21.7247 | 21.3894 | 22.2526 | 72.3111 |  | 30.277 | 47.6876 | 55.4854 | 33.7109 |  | 16.9763 | 16.9863 | 16.6709 | 16.9891 | 17.1794 | 18.222 | 28.7725 | 16.0072 | 17.0368 | 15.9956 | 17.1293 | 18.0258 | 45.1897 | 48.3139 | 44.0612 | 21.4459 |  |  | 0.57915 | -0.38316 | -56.5903 | 0.53879 | 0.27086 | -197.8447 | 9.0014 | 0.42611 | 0.11393 | 0.076059 | 0.091778 | 8.829 | 9.0589 | 1.9634 | 21.8021 | 22.0081 | 22.1942 | 22.2522 | 22.0672 | 21.371 | 20.1824 | 22.1895 | 22.3586 | 22.383 | 22.3426 | 21.9619 | 21.1799 | 22.249 | 25.2684 | 19.0168 | 18.1528 | 17.0134 | 16.7939 | 17.7421 | 16.9266 | 22.4078 | 22.1589 | 21.7051 | 22.0757 | 21.7908 | 21.29 | 21.9355 | 21.5161 | 20.8925 | 22.2082 | 67.2341 | 39.8472 | 30.2615 | -0.0066722 | 0.011443 | 29.8959 | 22.0666 | 22.3658 | 20.1318 | 21.6485 | 22.0904 | 21.9295 | 21.7 | 21.4176 | 21.7635 | 21.4304 | 21.0494 | 58.9924 | 77.5693 | 42.9239 | 43.3033 | 27.2944 |  | 22.1082 | 44.6488 | 22.9505 | 29.5108 | 22.4678 | 27.7872 |  | 26.549 |  |  | 20.6866 | 21.0196 | 27.2523 | [5 empty] | 21.8968 | 24.8943 | 21.6376 | 22.0111 | 23.6224 | 21.1351 | 21.7382 | 20.6758 | 26.6113 | 90.8091 |  | 22.2025 | 52.9328 | 19.2112 | 22.9029 | 59.6303 | 23.1987 | 41.253 | 19.7427 | 38.5419 | 19.8731 | 39.4967 | 18.9472 | 23.3371 | 52.1021 | 20.9647 | 24.8726 | 75.0529 | 19.4516 | 23.2452 | 60.3884 | 19.4775 | 38.0782 | 21.0443 | 38.7325 | 19.7519 | 38.8807 | 0.17071 | 20.6463 | 0.25004 | 0.015979 | -27.0267 | 3.0954 | 19.15 | 55.11 | 0.99814 | -0.73479 | -8.9297 | 0.87132 | 0.61911 | -16.7322 | 3.569 | 0.28685 | -0.16688 | 0.23738 | -0.43027 | 0.2652 | 0.11347 | 0.2078
42838.4213 | 89 | 22.9026 | 22.8665 | 22.8632 | 22.7804 | 22.4041 | 21.7417 | 22.7177 | 21.7839 | 22.3726 | 22.3629 | 22.3411 | 22.0018 | 21.209 | 22.1882 | 21.5987 | 21.7683 | 21.8968 | 21.085 | 21.1776 | 21.3928 | 20.4643 | 20.6061 | 20.9 | 21.8682 | 21.6252 | 21.3244 | 67.4987 | 59.1757 | 81.2829 | 22.0804 | 21.6666 | 21.2143 | 21.9851 | 21.7193 | 21.3882 | 22.3033 | 71.8616 |  | 30.4215 | 48.0751 | 55.7402 | 33.9984 |  | 16.9788 | 16.9878 | 16.6742 | 17.0129 | 17.2015 | 18.2533 | 28.8733 | 15.9835 | 17.0434 | 15.9859 | 17.1246 | 18.0251 | 45.1984 | 48.3227 | 44.0555 | 21.4511 |  |  | 0.62055 | -0.63944 | -56.2368 | 0.34626 | 0.1861 | -197.8999 | 8.7412 | 0.29206 | 0.18963 | -0.055276 | -0.071753 | 8.8287 | 9.0588 | 1.9639 | 21.8013 | 22.0062 | 22.1975 | 22.2493 | 22.0666 | 21.3743 | 20.1742 | 22.1823 | 22.3598 | 22.3931 | 22.3411 | 21.9548 | 21.1793 | 22.2461 | 26.2913 | 19.891 | 17.8533 | 17.0567 | 17.1669 | 17.8092 | 16.9405 | 22.4068 | 22.1555 | 21.7015 | 22.0866 | 21.7893 | 21.287 | 21.938 | 21.5105 | 20.8887 | 22.27 | 68.056 | 40.27 | 30.8749 | 0.11699 | 0.041495 | 30.0245 | 22.0666 | 22.3558 | 20.1299 | 21.6462 | 22.0877 | 21.9265 | 21.7031 | 21.4171 | 21.7626 | 21.4293 | 21.0463 | 59.4083 | 78.1154 | 43.2167 | 43.6324 | 27.8284 |  | 22.176 | 44.9934 | 23.0207 | 29.7952 | 22.5219 | 27.7043 |  | 26.6693 |  |  | 20.6804 | 21.0435 | 27.4135 | [5 empty] | 21.898 | 24.9647 | 21.6422 | 22.0146 | 23.6409 | 21.1322 | 21.7448 | 20.6805 | 26.734 | 91.5356 |  | 22.2526 | 53.3383 | 19.2154 | 23.1325 | 59.9124 | 23.2481 | 41.6152 | 19.7585 | 38.963 | 19.8935 | 39.7911 | 18.938 | 23.3501 | 52.4494 | 20.9869 | 24.9437 | 75.5808 | 19.4507 | 23.3426 | 60.8251 | 19.4892 | 38.3516 | 21.0677 | 39.0914 | 19.7571 | 39.2216 | 0.27775 | 20.6348 | 0.25478 | 0.015682 | -27.0338 | 3.0954 | 35.96 | 54.93 | 1.0335 | -0.94923 | -8.9018 | 0.6985 | 0.5132 | -16.7354 | 3.5172 | 0.2743 | -0.17409 | 0.2313 | -0.53609 | 0.30011 | 0.10719 | 0.19284
42838.4213 | 90 | 22.9042 | 22.8665 | 22.8653 | 22.7847 | 22.3948 | 21.7321 | 22.7101 | 21.7889 | 22.3611 | 22.3698 | 22.3419 | 21.9991 | 21.2054 | 22.1903 | 21.5911 | 21.7662 | 21.8934 | 21.0793 | 21.1716 | 21.3913 | 20.4674 | 20.6032 | 20.9029 | 21.8635 | 21.6265 | 21.3244 | 68.0861 | 59.6022 | 81.372 | 22.0853 | 21.6809 | 21.223 | 21.9992 | 21.7377 | 21.4101 | 22.3912 | 71.4648 |  | 30.5686 | 48.4303 | 56.0496 | 34.7599 |  | 16.9818 | 17.0016 | 16.6806 | 17.0187 | 17.2218 | 18.2911 | 28.9291 | 15.9326 | 17.042 | 15.9779 | 17.1281 | 18.0357 | 45.2011 | 48.3301 | 44.0515 | 21.4529 |  |  | 0.56798 | -0.43113 | -56.0002 | 0.33443 | 0.11513 | -197.8059 | 9.2866 | 0.43859 | 0.11393 | -0.039331 | -0.18789 | 8.829 | 9.0586 | 1.9647 | 21.7972 | 22.0047 | 22.1981 | 22.2545 | 22.0649 | 21.3691 | 20.179 | 22.1831 | 22.3587 | 22.3843 | 22.3356 | 21.9496 | 21.1742 | 22.2431 | 27.1393 | 20.172 | 18.1941 | 17.099 | 17.3751 | 17.8573 | 16.9466 | 22.4098 | 22.1602 | 21.7076 | 22.0937 | 21.7975 | 21.2917 | 21.941 | 21.5189 | 20.8986 | 22.339 | 68.8376 | 40.7415 | 31.2308 | 0.013971 | -0.26302 | 30.3121 | 22.0671 | 22.3594 | 20.1259 | 21.6491 | 22.0989 | 21.9389 | 21.7059 | 21.4275 | 21.7686 | 21.4319 | 21.048 | 59.8129 | 78.6983 | 43.5066 | 43.9467 | 28.1556 |  | 22.2476 | 45.2332 | 23.0973 | 30.0988 | 22.5794 | 27.767 |  | 26.7854 |  |  | 20.671 | 21.0584 | 27.4826 | [5 empty] | 21.9021 | 25.0643 | 21.6467 | 22.0151 | 23.6524 | 21.1351 | 21.7517 | 20.6836 | 26.8873 | 92.0778 |  | 22.3211 | 53.6482 | 19.217 | 23.3723 | 60.1023 | 23.3132 | 41.9759 | 19.7658 | 39.3524 | 19.904 | 40.1357 | 18.9386 | 23.3693 | 52.7094 | 20.9953 | 25.0249 | 75.9532 | 19.4506 | 23.4569 | 61.3948 | 19.488 | 38.6013 | 21.0801 | 39.3904 | 19.7656 | 39.6138 | 0.090577 | 20.6297 | 0.25983 | 0.015624 | -27.0144 | 3.0954 | 54.04 | 52.33 | 0.9889 | -0.77944 | -8.8833 | 0.68649 | 0.40368 | -16.7325 | 3.6255 | 0.26762 | -0.17817 | 0.2248 | -0.62471 | 0.26295 | 0.088995 | 0.18527
42838.4213 | 91 | 22.9035 | 22.8652 | 22.8572 | 22.7775 | 22.3912 | 21.7246 | 22.7138 | 21.7798 | 22.3538 | 22.3644 | 22.3407 | 21.9921 | 21.2109 | 22.1842 | 21.5959 | 21.7684 | 21.9001 | 21.0783 | 21.1824 | 21.3924 | 20.4745 | 20.6066 | 20.9096 | 21.8686 | 21.6323 | 21.3329 | 68.5814 | 59.9757 | 81.89 | 22.0881 | 21.6758 | 21.2189 | 21.9931 | 21.7377 | 21.4045 | 22.4604 | 72.2193 |  | 30.7003 | 48.7479 | 56.3453 | 35.5956 |  | 16.9924 | 17.0017 | 16.6799 | 17.018 | 17.2409 | 18.3119 | 28.9274 | 15.9053 | 17.0424 | 15.9877 | 17.1407 | 18.0367 | 45.1973 | 48.3312 | 44.0347 | 21.4613 |  |  | 0.57652 | -0.41011 | -55.7025 | 0.69124 | 0.23275 | -197.8105 | 9.1585 | 0.43596 | 0.060809 | -0.021498 | 0.051677 | 8.8284 | 9.0583 | 1.9629 | 21.7998 | 22.0022 | 22.1915 | 22.2434 | 22.0587 | 21.3649 | 20.1676 | 22.1792 | 22.3476 | 22.3802 | 22.3277 | 21.9452 | 21.1697 | 22.238 | 28.1016 | 20.8067 | 19.1299 | 17.302 | 17.3833 | 17.9257 | 16.9669 | 22.4087 | 22.1649 | 21.7101 | 22.089 | 21.8027 | 21.2956 | 21.9456 | 21.5214 | 20.893 | 22.4044 | 69.4273 | 41.2338 | 31.3683 | -0.099271 | -0.38018 | 30.3662 | 22.0693 | 22.3605 | 20.1277 | 21.6477 | 22.096 | 21.9368 | 21.7048 | 21.4331 | 21.7678 | 21.4295 | 21.0572 | 60.2009 | 79.2408 | 43.7683 | 44.2326 | 28.1694 |  | 22.318 | 45.0948 | 23.1722 | 30.3102 | 22.6441 | 28.3663 |  | 26.9084 |  |  | 20.6625 | 21.0747 | 27.5398 | [5 empty] | 21.9009 | 25.191 | 21.6438 | 22.0131 | 23.6814 | 21.1357 | 21.7487 | 20.6984 | 27.0618 | 92.4805 |  | 22.3959 | 53.9434 | 19.2213 | 23.5113 | 60.3984 | 23.3775 | 42.3319 | 19.7778 | 39.6766 | 19.9174 | 40.5018 | 18.9341 | 23.4223 | 52.9225 | 21.0153 | 25.16 | 76.2631 | 19.4657 | 23.5965 | 61.8718 | 19.4952 | 38.8618 | 21.1176 | 39.7223 | 19.764 | 40.2497 | 0.25938 | 20.6192 | 0.26437 | 0.015928 | -26.9968 | 3.0954 | 30.94 | 51.78 | 0.99704 | -0.7602 | -8.8597 | 0.98695 | 0.57399 | -16.7333 | 3.6006 | 0.2696 | -0.1718 | 0.2211 | -0.72365 | 0.16133 | 0.068106 | 0.18365
42838.4213 | 92 | 22.9008 | 22.8595 | 22.8533 | 22.7753 | 22.3901 | 21.7218 | 22.7075 | 21.7794 | 22.3501 | 22.36 | 22.3352 | 21.9909 | 21.2115 | 22.1754 | 21.6008 | 21.7735 | 21.8977 | 21.0856 | 21.1828 | 21.3932 | 20.4671 | 20.6108 | 20.9053 | 21.8692 | 21.6284 | 21.3368 | 69.0098 | 60.3613 | 82.1825 | 22.0853 | 21.675 | 21.2267 | 22.0013 | 21.7335 | 21.4096 | 22.5233 | 73.2005 |  | 30.8593 | 49.1333 | 56.6849 | 36.0659 |  | 16.9984 | 17.0181 | 16.6864 | 17.0336 | 17.2577 | 18.3654 | 28.9879 | 15.8774 | 17.0528 | 15.9807 | 17.1516 | 18.028 | 45.169 | 48.3138 | 44.0175 | 21.452 |  |  | 0.70071 | -0.21231 | -55.6861 | 0.56902 | 0.16047 | -197.8841 | 9.3477 | 0.23489 | -0.064903 | 0.13606 | -0.064462 | 8.8278 | 9.0577 | 1.9583 | 21.7976 | 22.0005 | 22.1921 | 22.2446 | 22.0605 | 21.3699 | 20.1665 | 22.1784 | 22.3498 | 22.3739 | 22.3232 | 21.9523 | 21.1764 | 22.2447 | 27.6703 | 20.7644 | 19.5242 | 17.6785 | 17.4166 | 17.9757 | 16.988 | 22.413 | 22.1663 | 21.7046 | 22.0792 | 21.7988 | 21.2983 | 21.9486 | 21.5157 | 20.8941 | 22.4741 | 69.9024 | 41.808 | 31.7067 | 0.0017816 | -0.30182 | 30.3204 | 22.0588 | 22.3503 | 20.1314 | 21.6438 | 22.0841 | 21.9347 | 21.6954 | 21.4353 | 21.7585 | 21.4199 | 21.0576 | 60.6174 | 79.7253 | 44.0566 | 44.5116 | 28.4468 |  | 22.3702 | 45.2404 | 23.2354 | 30.1939 | 22.7084 | 28.8053 |  | 27.0235 |  |  | 20.6738 | 21.0908 | 27.5652 | [5 empty] | 21.9047 | 25.3159 | 21.6483 | 22.0197 | 23.6921 | 21.1369 | 21.7526 | 20.7084 | 27.2108 | 93.1933 |  | 22.4811 | 54.3085 | 19.2371 | 23.5909 | 60.7804 | 23.4317 | 42.7213 | 19.7971 | 39.9801 | 19.9362 | 40.9018 | 18.9413 | 23.5005 | 53.2014 | 21.035 | 25.2875 | 76.6093 | 19.4682 | 23.7454 | 62.2588 | 19.5019 | 39.1288 | 21.1422 | 40.0602 | 19.7722 | 40.7959 | 0.12304 | 20.6117 | 0.26905 | 0.014542 | -27.0742 | 3.0954 | 37.86 | 55.36 | 1.0997 | -0.54699 | -8.8586 | 0.89548 | 0.47664 | -16.738 | 3.6379 | 0.26365 | -0.17372 | 0.2265 | -0.66988 | 0.11999 | 0.057161 | 0.17659
42838.4214 | 93 | 22.9065 | 22.862 | 22.8533 | 22.7759 | 22.3926 | 21.7267 | 22.7106 | 21.7836 | 22.3548 | 22.3655 | 22.3412 | 21.9931 | 21.2092 | 22.1817 | 21.6065 | 21.7786 | 21.8975 | 21.086 | 21.1844 | 21.3974 | 20.4727 | 20.6075 | 20.9121 | 21.8703 | 21.632 | 21.3406 | 69.5254 | 60.7225 | 82.8817 | 22.0843 | 21.681 | 21.2325 | 21.9983 | 21.7364 | 21.4189 | 22.5948 | 73.7322 |  | 31.017 | 49.5789 | 57.1127 | 36.146 |  | 16.9998 | 17.0154 | 16.6807 | 17.0319 | 17.2641 | 18.3951 | 29.4952 | 15.8695 | 17.05 | 15.9651 | 17.1511 | 18.0386 | 45.1487 | 48.3151 | 44.008 | 21.4607 |  |  | 0.49241 | -0.33914 | -55.5501 | 0.51053 | 0.027732 | -197.8177 | 9.1164 | 0.39522 | -0.025205 | 0.013748 | -0.056997 | 8.8284 | 9.0581 | 1.9565 | 21.8009 | 22.0107 | 22.1948 | 22.2533 | 22.0704 | 21.3735 | 20.1831 | 22.1921 | 22.3627 | 22.3938 | 22.344 | 21.946 | 21.1756 | 22.2534 | 28.3108 | 20.5657 | 19.8127 | 17.9562 | 17.6221 | 18.032 | 16.9991 | 22.4055 | 22.1533 | 21.7008 | 22.0832 | 21.7922 | 21.2934 | 21.9368 | 21.5031 | 20.891 | 22.5458 | 70.127 | 42.1712 | 32.2828 | -0.019058 | -0.35945 | 30.4093 | 22.0659 | 22.3537 | 20.1323 | 21.6504 | 22.0849 | 21.9361 | 21.6972 | 21.4517 | 21.7663 | 21.4273 | 21.0575 | 61.1053 | 80.1607 | 44.3959 | 44.8271 | 28.7407 |  | 22.4271 | 45.7658 | 23.314 | 30.1555 | 22.7758 | 28.8656 |  | 27.1479 |  |  | 20.6658 | 21.0935 | 27.4619 | [5 empty] | 21.9038 | 25.4316 | 21.644 | 22.0212 | 23.6906 | 21.1323 | 21.7483 | 20.7228 | 27.3305 | 94.2579 |  | 22.5594 | 54.6619 | 19.2527 | 23.6824 | 61.1647 | 23.4861 | 43.1007 | 19.8102 | 40.3051 | 19.9475 | 41.2763 | 18.9343 | 23.5822 | 53.5253 | 21.0608 | 25.3864 | 77.1124 | 19.4733 | 23.8891 | 62.5958 | 19.5062 | 39.3779 | 21.1679 | 40.3084 | 19.7809 | 41.1625 | 0.28943 | 20.6028 | 0.27317 | 0.015311 | -27.0195 | 3.0954 | 34.92 | 54.94 | 0.92273 | -0.69132 | -8.8477 | 0.84821 | 0.19816 | -16.736 | 3.5928 | 0.2574 | -0.18566 | 0.22983 | -0.73448 | 0.08923 | 0.057342 | 0.163
42838.4214 | 94 | 22.9078 | 22.8649 | 22.8533 | 22.7796 | 22.4023 | 21.7337 | 22.7211 | 21.783 | 22.358 | 22.3731 | 22.3443 | 22.0016 | 21.2167 | 22.1872 | 21.6062 | 21.769 | 21.8952 | 21.0793 | 21.1813 | 21.3933 | 20.4698 | 20.608 | 20.914 | 21.8698 | 21.6342 | 21.3433 | 70.055 | 61.0718 | 83.6123 | 22.0871 | 21.6802 | 21.2369 | 22.002 | 21.7381 | 21.4205 | 22.6646 | 74.7688 |  | 31.2011 | 49.9896 | 57.568 | 35.8891 |  | 17.0051 | 17.0158 | 16.6837 | 17.0252 | 17.2581 | 18.4141 | 29.9312 | 15.9086 | 17.0478 | 15.9478 | 17.1482 | 18.037 | 45.1235 | 48.3175 | 43.9984 | 21.4707 |  |  | 0.43064 | -0.29905 | -55.876 | 0.60319 | 0.013272 | -197.8342 | 9.1618 | 0.27431 | -0.043108 | 0.14865 | -0.000924 | 8.8285 | 9.0584 | 1.9569 | 21.7956 | 22.005 | 22.1897 | 22.2504 | 22.063 | 21.3727 | 20.1722 | 22.1821 | 22.3518 | 22.3873 | 22.3422 | 21.9547 | 21.1775 | 22.2402 | 29.7685 | 20.9889 | 19.6538 | 18.1984 | 17.9073 | 18.116 | 17.0103 | 22.4013 | 22.1531 | 21.6921 | 22.0806 | 21.796 | 21.2907 | 21.9329 | 21.5091 | 20.8968 | 22.6072 | 70.238 | 42.501 | 32.8365 | 0.15257 | -0.21413 | 30.5473 | 22.0676 | 22.3612 | 20.1337 | 21.6486 | 22.0911 | 21.9422 | 21.7 | 21.4594 | 21.7674 | 21.4345 | 21.0586 | 61.5581 | 80.6377 | 44.7587 | 45.1603 | 29.0314 |  | 22.4856 | 46.5294 | 23.4163 | 30.3935 | 22.8395 | 28.8701 |  | 27.2787 |  |  | 20.6649 | 21.0918 | 27.5106 | [5 empty] | 21.8988 | 25.4922 | 21.6406 | 22.0144 | 23.6952 | 21.1269 | 21.7382 | 20.7353 | 27.4336 | 94.8487 |  | 22.6461 | 54.9836 | 19.2622 | 23.8272 | 61.5831 | 23.5418 | 43.4366 | 19.8311 | 40.6583 | 19.9679 | 41.6624 | 18.9181 | 23.6641 | 53.8408 | 21.0777 | 25.4341 | 77.5407 | 19.4742 | 24.0104 | 62.9826 | 19.504 | 39.6049 | 21.1894 | 40.5572 | 19.794 | 41.5112 | 0.046057 | 20.5936 | 0.27796 | 0.015108 | -27.1424 | 3.0954 | 27.06 | 54.88 | 0.8638 | -0.64918 | -8.8737 | 0.92197 | 0.13709 | -16.7373 | 3.6018 | 0.25129 | -0.20343 | 0.22537 | -0.88665 | 0.1082 | 0.066825 | 0.14969
42838.4214 | 95 | 22.9135 | 22.8791 | 22.8601 | 22.7791 | 22.4063 | 21.7386 | 22.7231 | 21.7887 | 22.3619 | 22.375 | 22.3435 | 22.0079 | 21.2186 | 22.1901 | 21.6014 | 21.7669 | 21.8903 | 21.0813 | 21.1791 | 21.3878 | 20.4661 | 20.6056 | 20.9042 | 21.8703 | 21.6274 | 21.348 | 70.4339 | 61.4731 | 84.2328 | 22.0863 | 21.6863 | 21.2402 | 22.0071 | 21.741 | 21.4224 | 22.7217 | 75.938 |  | 31.3808 | 50.3457 | 58.0188 | 35.8481 |  | 16.9966 | 17.0277 | 16.6858 | 17.041 | 17.2549 | 18.4155 | 30.1124 | 15.8046 | 17.0533 | 15.909 | 17.152 | 18.0514 | 45.0954 | 48.315 | 43.9915 | 21.474 |  |  | 0.50818 | -0.41733 | -55.6651 | 0.43628 | 0.12301 | -197.8322 | 9.2216 | 0.58184 | -0.4002 | 0.093262 | 0.17059 | 8.8287 | 9.0586 | 1.9592 | 21.7917 | 22.0051 | 22.1887 | 22.2431 | 22.0575 | 21.3641 | 20.1698 | 22.1761 | 22.3524 | 22.3826 | 22.3347 | 21.9459 | 21.175 | 22.2376 | 30.7692 | 21.5513 | 19.6993 | 17.9918 | 18.0518 | 18.205 | 17.0301 | 22.4078 | 22.156 | 21.7039 | 22.0872 | 21.7927 | 21.2981 | 21.9332 | 21.5126 | 20.8984 | 22.6736 | 70.6103 | 42.9377 | 33.013 | 0.12485 | -0.18656 | 30.7309 | 22.0631 | 22.36 | 20.1344 | 21.6436 | 22.0871 | 21.9386 | 21.6946 | 21.4637 | 21.7606 | 21.4286 | 21.055 | 61.9795 | 81.1444 | 45.1155 | 45.5117 | 29.3847 |  | 22.5372 | 47.137 | 23.4932 | 30.5685 | 22.8944 | 28.7525 |  | 27.3917 |  |  | 20.6666 | 21.1011 | 27.8017 | [5 empty] | 21.8987 | 25.5667 | 21.6337 | 22.0065 | 23.7075 | 21.1253 | 21.7364 | 20.7441 | 27.5172 | 95.1186 |  | 22.7425 | 55.3738 | 19.2653 | 24.0062 | 62.0005 | 23.6059 | 43.7041 | 19.8518 | 40.9925 | 19.9859 | 42.0378 | 18.9088 | 23.7586 | 54.1073 | 21.0931 | 25.4546 | 77.9491 | 19.4862 | 24.1277 | 63.4949 | 19.5108 | 39.8536 | 21.2181 | 40.799 | 19.8084 | 41.7984 | 0.20188 | 20.5866 | 0.28324 | 0.016095 | -27.0784 | 3.0954 | 33.87 | 51.8 | 0.93917 | -0.7669 | -8.8571 | 0.78412 | 0.41736 | -16.7372 | 3.6136 | 0.24322 | -0.21772 | 0.22236 | -0.98745 | 0.10545 | 0.069885 | 0.14702
42838.4214 | 96 | 22.9135 | 22.8765 | 22.8595 | 22.7815 | 22.4002 | 21.7346 | 22.7166 | 21.7975 | 22.3604 | 22.3667 | 22.3419 | 22.0043 | 21.2151 | 22.181 | 21.5962 | 21.7643 | 21.8948 | 21.0782 | 21.1706 | 21.3878 | 20.4645 | 20.6061 | 20.9059 | 21.8659 | 21.63 | 21.3483 | 70.8106 | 61.8987 | 84.7811 | 22.0783 | 21.6842 | 21.2403 | 22.0001 | 21.7367 | 21.4234 | 22.7886 | 76.8817 |  | 31.5493 | 50.7195 | 58.438 | 36.3729 |  | 17.0154 | 17.027 | 16.6998 | 17.0576 | 17.2879 | 18.4532 | 30.1938 | 15.6945 | 17.0529 | 15.8562 | 17.1652 | 18.0346 | 45.0632 | 48.2988 | 43.9587 | 21.4583 |  |  | 0.70269 | -0.50276 | -55.7282 | 0.44219 | 0.085556 | -197.8519 | 9.1657 | 0.48328 | 0.011964 | 0.21914 | 0.14143 | 8.8284 | 9.0581 | 1.959 | 21.7921 | 22.0114 | 22.1924 | 22.2486 | 22.0593 | 21.3638 | 20.181 | 22.1819 | 22.3502 | 22.3824 | 22.3407 | 21.9564 | 21.1775 | 22.2478 | 31.2871 | 22.6181 | 21.3058 | 17.7525 | 17.9421 | 18.2906 | 17.0632 | 22.4124 | 22.1531 | 21.6937 | 22.0866 | 21.7929 | 21.2997 | 21.9354 | 21.5118 | 20.8982 | 22.7306 | 71.1045 | 43.3042 | 33.2598 | 0.010235 | -0.13254 | 30.9742 | 22.0641 | 22.3528 | 20.1319 | 21.6439 | 22.0786 | 21.9328 | 21.6887 | 21.4703 | 21.758 | 21.4273 | 21.0602 | 62.343 | 81.6143 | 45.4294 | 45.8787 | 29.4532 |  | 22.5897 | 47.0764 | 23.5755 | 30.83 | 22.944 | 28.6491 |  | 27.5031 |  |  | 20.6791 | 21.1135 | 27.8397 | [5 empty] | 21.9025 | 25.6723 | 21.6336 | 22.005 | 23.7278 | 21.1213 | 21.7374 | 20.7555 | 27.6401 | 95.4286 |  | 22.8592 | 55.7883 | 19.2791 | 24.153 | 62.3375 | 23.6607 | 43.971 | 19.8734 | 41.2484 | 20.0035 | 42.3843 | 18.8988 | 23.8047 | 54.3536 | 21.1121 | 25.4951 | 78.4242 | 19.4946 | 24.2018 | 63.9909 | 19.511 | 40.0973 | 21.249 | 41.089 | 19.8243 | 42.1052 | 0.12007 | 20.5774 | 0.28864 | 0.017438 | -26.9123 | 3.0954 | 26.54 | 51.83 | 1.1052 | -0.84174 | -8.8621 | 0.78941 | 0.34809 | -16.7391 | 3.6029 | 0.24308 | -0.21326 | 0.21676 | -1.035 | -0.069191 | 0.057557 | 0.14208
42838.4214 | 97 | 22.9103 | 22.866 | 22.8558 | 22.7764 | 22.3909 | 21.7315 | 22.7089 | 21.7919 | 22.3605 | 22.3666 | 22.3378 | 22.0088 | 21.207 | 22.1816 | 21.5869 | 21.7594 | 21.8814 | 21.0724 | 21.1649 | 21.3857 | 20.4636 | 20.6019 | 20.9072 | 21.8557 | 21.6225 | 21.3536 | 71.1638 | 62.2831 | 84.9624 | 22.0784 | 21.6773 | 21.2299 | 21.9888 | 21.7389 | 21.4243 | 22.8571 | 77.6392 |  | 31.6893 | 51.1019 | 58.8309 | 36.6647 |  | 17.0181 | 17.0396 | 16.7023 | 17.0847 | 17.3227 | 18.4813 | 30.2468 | 15.5542 | 17.05 | 15.8224 | 17.1572 | 18.0377 | 45.0396 | 48.2869 | 43.93 | 21.4623 |  |  | 0.67443 | -0.22349 | -55.8294 | 0.47768 | 0.023788 | -197.8184 | 8.9541 | 0.75598 | -0.035518 | 0.038714 | 0.036747 | 8.829 | 9.059 | 1.9569 | 21.799 | 22.0128 | 22.1908 | 22.2535 | 22.0647 | 21.3742 | 20.1755 | 22.1839 | 22.3606 | 22.3877 | 22.3352 | 21.9543 | 21.1782 | 22.2487 | 32.1356 | 23.0096 | 23.3866 | 18.4425 | 17.7501 | 18.3784 | 17.1111 | 22.4083 | 22.1538 | 21.7065 | 22.0924 | 21.7962 | 21.2948 | 21.9409 | 21.5172 | 20.9058 | 22.8262 | 71.5853 | 43.5994 | 33.9812 | 0.16555 | -0.34195 | 31.0296 | 22.0658 | 22.3534 | 20.1317 | 21.6459 | 22.0824 | 21.9309 | 21.6938 | 21.4807 | 21.761 | 21.4271 | 21.0605 | 62.6998 | 82.0604 | 45.7288 | 46.2213 | 29.3417 |  | 22.6506 | 46.9045 | 23.6609 | 31.1239 | 23.0032 | 28.6542 |  | 27.6415 |  |  | 20.6951 | 21.1246 | 27.8073 | [5 empty] | 21.9093 | 25.7885 | 21.6386 | 22.0087 | 23.7655 | 21.1338 | 21.7375 | 20.7567 | 27.7728 | 95.5482 |  | 22.9714 | 56.0866 | 19.2868 | 24.2415 | 62.628 | 23.6981 | 44.299 | 19.8849 | 41.442 | 20.0103 | 42.6887 | 18.9005 | 23.8304 | 54.6184 | 21.1316 | 25.6202 | 79.0317 | 19.5068 | 24.2456 | 64.4076 | 19.5146 | 40.3212 | 21.2812 | 41.4507 | 19.8451 | 42.4234 | 0.13844 | 20.5715 | 0.29386 | 0.018999 | -26.9621 | 3.0955 | 29.44 | 55.7 | 1.083 | -0.56122 | -8.8703 | 0.82049 | 0.18355 | -16.7385 | 3.5612 | 0.24823 | -0.2056 | 0.21059 | -1.119 | -0.2948 | 0.051758 | 0.12526
42838.4214 | 98 | 22.9072 | 22.8666 | 22.8632 | 22.7778 | 22.3966 | 21.7373 | 22.7121 | 21.7903 | 22.3576 | 22.3716 | 22.3395 | 21.9993 | 21.2098 | 22.1827 | 21.5978 | 21.7694 | 21.8968 | 21.0869 | 21.1776 | 21.3927 | 20.4728 | 20.6112 | 20.9134 | 21.8664 | 21.6358 | 21.3611 | 71.5001 | 62.7224 | 84.9487 | 22.084 | 21.6784 | 21.2338 | 22.0055 | 21.7358 | 21.4329 | 22.9329 | 78.0149 |  | 31.864 | 51.5636 | 59.191 | 36.4153 |  | 17.0236 | 17.0364 | 16.7092 | 17.1065 | 17.3349 | 18.4901 | 30.8759 | 15.483 | 17.047 | 15.7858 | 17.1704 | 18.0439 | 45.0243 | 48.2763 | 43.9155 | 21.4715 |  |  | 0.40239 | -0.30365 | -55.8589 | 0.71818 | 0.11907 | -197.848 | 8.916 | 0.69552 | -0.064319 | 0.023399 | 0.028762 | 8.8285 | 9.0582 | 1.9544 | 21.793 | 22.0087 | 22.1884 | 22.2516 | 22.0589 | 21.3678 | 20.1708 | 22.18 | 22.3596 | 22.3859 | 22.3344 | 21.9516 | 21.1778 | 22.2438 | 33.4901 | 23.9383 | 24.7585 | 19.3358 | 17.6028 | 18.4896 | 17.1751 | 22.3889 | 22.156 | 21.6965 | 22.078 | 21.7837 | 21.2821 | 21.9295 | 21.511 | 20.894 | 22.9016 | 71.9541 | 44.0284 | 34.4506 | 0.098312 | -0.16012 | 31.1264 | 22.0652 | 22.3616 | 20.1354 | 21.6496 | 22.0881 | 21.9295 | 21.6998 | 21.4933 | 21.7638 | 21.4311 | 21.0639 | 62.9725 | 82.4748 | 46.0192 | 46.5347 | 29.354 |  | 22.7243 | 47.2809 | 23.7309 | 31.4941 | 23.0746 | 28.9287 |  | 27.7719 |  |  | 20.6949 | 21.1201 | 27.9136 | [5 empty] | 21.8954 | 25.8764 | 21.6356 | 22.0064 | 23.7973 | 21.1348 | 21.736 | 20.7687 | 27.8875 | 95.6407 |  | 23.0763 | 56.4292 | 19.2933 | 24.2318 | 62.9006 | 23.7384 | 44.6889 | 19.8894 | 41.6431 | 20.0265 | 42.9839 | 18.8781 | 23.9096 | 54.9184 | 21.1421 | 25.7706 | 79.4689 | 19.4993 | 24.2966 | 64.7558 | 19.5086 | 40.527 | 21.3023 | 41.7799 | 19.8619 | 42.6354 | 0.18722 | 20.5669 | 0.29811 | 0.018731 | -27.006 | 3.0954 | 27.95 | 55.18 | 0.83655 | -0.65418 | -8.8726 | 1.0061 | 0.41067 | -16.74 | 3.5537 | 0.25036 | -0.2137 | 0.20271 | -1.2565 | -0.43976 | 0.06124 | 0.11476
42838.4214 | 99 | 22.9083 | 22.8682 | 22.8571 | 22.7688 | 22.4036 | 21.7336 | 22.7083 | 21.7886 | 22.3667 | 22.3689 | 22.3399 | 21.9972 | 21.2112 | 22.1821 | 21.5947 | 21.7607 | 21.8909 | 21.0769 | 21.1727 | 21.3843 | 20.4612 | 20.6062 | 20.9022 | 21.8677 | 21.6212 | 21.3559 | 71.821 | 63.1269 | 85.122 | 22.0917 | 21.6827 | 21.2458 | 22.0028 | 21.7404 | 21.4381 | 22.9958 | 77.9052 |  | 32.0294 | 51.9991 | 59.5099 | 36.1283 |  | 17.0205 | 17.0377 | 16.7056 | 17.1055 | 17.3438 | 18.5086 | 31.5013 | 15.4427 | 17.0544 | 15.7311 | 17.1769 | 18.0495 | 45.0186 | 48.2524 | 43.8986 | 21.4795 |  |  | 0.58966 | -0.23597 | -55.3904 | 0.78718 | 0.11644 | -197.8512 | 9.1624 | 0.55687 | 0.16589 | 0.139 | -0.037554 | 8.8285 | 9.0586 | 1.9522 | 21.7884 | 21.9997 | 22.1829 | 22.2421 | 22.0569 | 21.3628 | 20.1621 | 22.1744 | 22.3429 | 22.3815 | 22.332 | 21.9448 | 21.1774 | 22.2352 | 34.314 | 24.4775 | 26.0706 | 19.9862 | 18.1172 | 18.5974 | 17.2261 | 22.3985 | 22.1597 | 21.6992 | 22.0814 | 21.7878 | 21.2879 | 21.9328 | 21.5177 | 20.902 | 22.9753 | 72.3238 | 44.4656 | 34.4558 | 0.0004054 | -0.14072 | 31.2574 | 22.0629 | 22.3621 | 20.1353 | 21.649 | 22.0895 | 21.927 | 21.6988 | 21.5016 | 21.7595 | 21.4299 | 21.0658 | 63.2091 | 82.9125 | 46.252 | 46.8202 | 29.6525 |  | 22.7726 | 47.9104 | 23.8033 | 31.8705 | 23.1273 | 29.0797 |  | 27.8726 |  |  | 20.712 | 21.1318 | 28.1059 | [5 empty] | 21.8981 | 25.9759 | 21.6359 | 22.0048 | 23.8293 | 21.1255 | 21.745 | 20.7865 | 28.0286 | 95.7244 |  | 23.1726 | 56.7492 | 19.307 | 24.31 | 63.305 | 23.7775 | 45.0272 | 19.9063 | 41.9356 | 20.0435 | 43.2338 | 18.8733 | 24.0175 | 55.2236 | 21.1495 | 25.8807 | 79.8586 | 19.5028 | 24.385 | 65.0871 | 19.5147 | 40.7733 | 21.3263 | 42.0342 | 19.8789 | 42.8833 | 0.083899 | 20.5602 | 0.30343 | 0.01828 | -26.9992 | 3.0955 | 37.98 | 53.91 | 1.0129 | -0.57668 | -8.8354 | 1.0533 | 0.40612 | -16.7407 | 3.6025 | 0.2437 | -0.22875 | 0.19403 | -1.3355 | -0.57961 | 0.071328 | 0.1171
42838.4214 | 100 | 22.9063 | 22.8751 | 22.8617 | 22.7747 | 22.4038 | 21.7276 | 22.7141 | 21.7822 | 22.3691 | 22.3669 | 22.3435 | 22.0057 | 21.2079 | 22.1865 | 21.5975 | 21.7681 | 21.8936 | 21.0767 | 21.1816 | 21.397 | 20.4645 | 20.6137 | 20.9069 | 21.8641 | 21.628 | 21.3619 | 72.1984 | 63.5291 | 84.9854 | 22.0823 | 21.6801 | 21.2424 | 21.9932 | 21.7322 | 21.4333 | 23.0527 | 77.9563 |  | 32.1914 | 52.4129 | 59.7602 | 35.7056 |  | 17.0197 | 17.0294 | 16.6989 | 17.0855 | 17.3325 | 18.5014 | 32.1463 | 15.442 | 17.0538 | 15.7429 | 17.1664 | 18.0504 | 45.0305 | 48.2401 | 43.8872 | 21.4869 |  |  | 0.62252 | -0.165 | -54.8233 | 0.70964 | 0.27415 | -197.8355 | 9.3885 | 0.5503 | 0.092723 | -0.0194 | 0.038483 | 8.8289 | 9.0588 | 1.9525 | 21.7968 | 21.9972 | 22.1933 | 22.2353 | 22.0619 | 21.3585 | 20.1706 | 22.1789 | 22.3508 | 22.388 | 22.3348 | 21.9519 | 21.171 | 22.2463 | 34.7647 | 24.5719 | 25.957 | 20.7226 | 18.7163 | 18.6847 | 17.2806 | 22.3999 | 22.1577 | 21.6941 | 22.0839 | 21.7957 | 21.2955 | 21.935 | 21.5205 | 20.9073 | 23.0344 | 72.8683 | 44.9126 | 34.4935 | -0.15235 | -0.23296 | 31.3772 | 22.0595 | 22.3549 | 20.1376 | 21.6463 | 22.0887 | 21.9281 | 21.6905 | 21.5044 | 21.7589 | 21.4242 | 21.0592 | 63.6069 | 83.3084 | 46.4978 | 47.0797 | 29.9617 |  | 22.8291 | 48.5378 | 23.8775 | 32.4168 | 23.1965 | 28.972 |  | 27.9802 |  |  | 20.7185 | 21.1471 | 28.2503 | [5 empty] | 21.8957 | 26.1083 | 21.6371 | 22.0115 | 23.8425 | 21.1319 | 21.739 | 20.8033 | 28.1948 | 96.1679 |  | 23.2916 | 57.1665 | 19.3157 | 24.4865 | 63.7048 | 23.7947 | 45.3919 | 19.922 | 42.1885 | 20.0662 | 43.4907 | 18.8681 | 24.0958 | 55.5201 | 21.1709 | 25.9581 | 80.2364 | 19.5191 | 24.4941 | 65.4148 | 19.5304 | 41.0013 | 21.3611 | 42.2969 | 19.8937 | 43.1564 | 0.20076 | 20.5516 | 0.30737 | 0.01778 | -26.99 | 3.0955 | 33.05 | 51.83 | 1.0406 | -0.48222 | -8.7899 | 1 | 0.62315 | -16.7398 | 3.6467 | 0.23701 | -0.24367 | 0.18118 | -1.3754 | -0.56063 | 0.084988 | 0.11804
42838.4214 | 101 | 22.8988 | 22.8611 | 22.858 | 22.7699 | 22.3968 | 21.7259 | 22.7124 | 21.7804 | 22.3574 | 22.3579 | 22.3373 | 21.9999 | 21.2082 | 22.176 | 21.5899 | 21.7618 | 21.8927 | 21.0709 | 21.1678 | 21.386 | 20.4597 | 20.6052 | 20.9061 | 21.8526 | 21.6242 | 21.3696 | 72.6197 | 63.9609 | 85.4052 | 22.0797 | 21.6809 | 21.2461 | 21.9948 | 21.7326 | 21.4396 | 23.1086 | 77.999 |  | 32.3732 | 52.7654 | 60.0047 | 35.4567 |  | 17.0209 | 17.0319 | 16.6949 | 17.0802 | 17.3194 | 18.4755 | 32.8726 | 15.4381 | 17.049 | 15.7702 | 17.1727 | 18.0461 | 45.0469 | 48.2151 | 43.8615 | 21.4684 |  |  | 0.55024 | -0.11637 | -54.3285 | 0.41197 | 0.21106 | -197.8144 | 9.5022 | 0.67844 | -0.043108 | 0.037246 | -0.050747 | 8.8282 | 9.0581 | 1.9568 | 21.8031 | 22.0169 | 22.1901 | 22.2573 | 22.0706 | 21.3727 | 20.1826 | 22.1911 | 22.359 | 22.3929 | 22.3442 | 21.9665 | 21.187 | 22.2544 | 34.1868 | 23.6976 | 25.1119 | 21.0539 | 19.3333 | 18.751 | 17.311 | 22.4097 | 22.1625 | 21.7007 | 22.0876 | 21.8049 | 21.2939 | 21.9415 | 21.5238 | 20.9062 | 23.1009 | 73.4475 | 45.3971 | 34.2881 | -0.12856 | -0.16278 | 31.4289 | 22.0592 | 22.3459 | 20.1398 | 21.6411 | 22.079 | 21.9254 | 21.6852 | 21.508 | 21.754 | 21.4182 | 21.0595 | 64.0953 | 83.67 | 46.82 | 47.3424 | 29.8796 |  | 22.8662 | 48.9857 | 23.9491 | 32.9109 | 23.2696 | 29.2115 |  | 28.0831 |  |  | 20.7358 | 21.1666 | 28.2133 | [5 empty] | 21.8982 | 26.1827 | 21.6396 | 22.0132 | 23.878 | 21.1249 | 21.7397 | 20.8016 | 28.3552 | 96.5147 |  | 23.4274 | 57.549 | 19.3219 | 24.662 | 64.026 | 23.824 | 45.7835 | 19.9259 | 42.404 | 20.0717 | 43.7885 | 18.8563 | 24.1343 | 55.881 | 21.1722 | 26.0801 | 80.5281 | 19.5287 | 24.6165 | 65.7227 | 19.5358 | 41.088 | 21.3856 | 42.6794 | 19.9019 | 43.4352 | 0.066833 | 20.5456 | 0.31318 | 0.016604 | -26.9977 | 3.0955 | 30 | 52.43 | 0.97886 | -0.40498 | -8.7502 | 0.76196 | 0.54675 | -16.7382 | 3.6685 | 0.24054 | -0.2537 | 0.16992 | -1.3034 | -0.46319 | 0.093782 | 0.12598
42838.4215 | 102 | 22.906 | 22.866 | 22.8559 | 22.7768 | 22.3997 | 21.7354 | 22.7104 | 21.7914 | 22.3591 | 22.3629 | 22.3384 | 22.003 | 21.2119 | 22.1783 | 21.5966 | 21.7643 | 21.8945 | 21.0842 | 21.1829 | 21.385 | 20.4649 | 20.6021 | 20.9043 | 21.8745 | 21.6235 | 21.3763 | 73.0792 | 64.3227 | 85.7768 | 22.0904 | 21.686 | 21.2518 | 22.0008 | 21.7348 | 21.4486 | 23.1774 | 78.1001 |  | 32.5521 | 53.109 | 60.3635 | 35.8046 |  | 17.0187 | 17.0324 | 16.6909 | 17.0575 | 17.2918 | 18.4591 | 33.4132 | 15.4466 | 17.0532 | 15.7775 | 17.1832 | 18.0504 | 45.0702 | 48.1857 | 43.8605 | 21.4788 |  |  | 0.70663 | -0.20574 | -54.0013 | 0.59859 | 0.20252 | -197.848 | 9.5961 | 0.57462 | -0.062373 | 0.2032 | 0.084834 | 8.8291 | 9.0589 | 1.9588 | 21.7911 | 21.9969 | 22.1932 | 22.2446 | 22.0595 | 21.3666 | 20.1696 | 22.1823 | 22.3522 | 22.3855 | 22.3362 | 21.9496 | 21.1733 | 22.2441 | 33.7082 | 22.5742 | 23.9523 | 20.792 | 19.3263 | 18.8147 | 17.3315 | 22.4014 | 22.1573 | 21.7051 | 22.0864 | 21.7898 | 21.2886 | 21.9354 | 21.5177 | 20.9019 | 23.1805 | 73.6543 | 45.7397 | 34.3663 | -0.16277 | -0.12512 | 31.5864 | 22.0626 | 22.352 | 20.1426 | 21.6451 | 22.0797 | 21.9305 | 21.6959 | 21.5217 | 21.7621 | 21.4264 | 21.0657 | 64.4895 | 84.0271 | 47.1495 | 47.6192 | 29.803 |  | 22.9136 | 49.1663 | 24.0128 | 33.2618 | 23.3431 | 29.3781 |  | 28.1964 |  |  | 20.7506 | 21.1832 | 28.4466 | [5 empty] | 21.8918 | 26.2643 | 21.6333 | 22.0018 | 23.9035 | 21.1256 | 21.731 | 20.8177 | 28.4851 | 97.1024 |  | 23.5045 | 57.9985 | 19.3382 | 24.7608 | 64.4453 | 23.8609 | 46.1263 | 19.9556 | 42.6465 | 20.0861 | 44.0627 | 18.8741 | 24.1763 | 56.324 | 21.2098 | 26.2163 | 80.9429 | 19.5528 | 24.7387 | 65.9837 | 19.5477 | 41.2181 | 21.4204 | 42.9955 | 19.9255 | 43.7517 | 0.1542 | 20.5361 | 0.31606 | 0.01529 | -27.0426 | 3.0955 | 38.88 | 55.59 | 1.1099 | -0.53847 | -8.7238 | 0.91847 | 0.53556 | -16.7391 | 3.6865 | 0.24426 | -0.25657 | 0.16265 | -1.2428 | -0.33194 | 0.086434 | 0.12649
42838.4215 | 103 | 22.9055 | 22.8648 | 22.8513 | 22.7787 | 22.3978 | 21.7272 | 22.7042 | 21.7828 | 22.3567 | 22.3664 | 22.3428 | 21.9969 | 21.2128 | 22.1776 | 21.6045 | 21.7719 | 21.8932 | 21.0847 | 21.1772 | 21.3952 | 20.472 | 20.6075 | 20.9123 | 21.8752 | 21.6256 | 21.3861 | 73.4392 | 64.6216 | 85.5333 | 22.0916 | 21.6892 | 21.2585 | 21.9998 | 21.736 | 21.4488 | 23.2519 | 78.5338 |  | 32.7107 | 53.4303 | 60.7236 | 36.5721 |  | 17.0272 | 17.0344 | 16.6982 | 17.0482 | 17.2723 | 18.4636 | 34.1072 | 15.4256 | 17.0424 | 15.8561 | 17.1812 | 18.0556 | 45.093 | 48.1643 | 43.8686 | 21.4812 |  |  | 0.56667 | -0.10652 | -53.1746 | 0.92255 | 0.21304 | -197.8151 | 10.0936 | 0.60484 | -0.039216 | 0.16921 | 0.10896 | 8.8285 | 9.0586 | 1.959 | 21.7923 | 22.0022 | 22.19 | 22.2396 | 22.0598 | 21.3682 | 20.171 | 22.1802 | 22.3569 | 22.386 | 22.3316 | 21.9521 | 21.1723 | 22.2419 | 33.4358 | 22.3229 | 23.579 | 20.5121 | 19.2297 | 18.8873 | 17.3663 | 22.3979 | 22.1504 | 21.6949 | 22.0728 | 21.7921 | 21.2898 | 21.9394 | 21.5098 | 20.9051 | 23.2375 | 73.8371 | 45.9771 | 34.5612 | -0.042257 | -0.21965 | 31.7481 | 22.0688 | 22.3556 | 20.1495 | 21.6471 | 22.0883 | 21.9363 | 21.7009 | 21.5332 | 21.7677 | 21.4361 | 21.0743 | 64.8782 | 84.4892 | 47.416 | 47.873 | 29.9402 |  | 22.9833 | 49.203 | 24.076 | 33.2551 | 23.4005 | 29.3735 |  | 28.319 |  |  | 20.7696 | 21.202 | 28.666 | [5 empty] | 21.898 | 26.335 | 21.6436 | 22.0104 | 23.9583 | 21.1297 | 21.7472 | 20.8311 | 28.5931 | 97.4744 |  | 23.5542 | 58.4109 | 19.3482 | 24.7991 | 64.7094 | 23.9043 | 46.502 | 19.9703 | 42.9276 | 20.1066 | 44.375 | 18.8744 | 24.219 | 56.7503 | 21.2163 | 26.3147 | 81.3821 | 19.556 | 24.8066 | 66.2163 | 19.5657 | 41.3522 | 21.4478 | 43.2705 | 19.9549 | 44.2418 | 0.25215 | 20.5272 | 0.32151 | 0.014941 | -26.978 | 3.0955 | 33.23 | 55.06 | 0.99354 | -0.38745 | -8.6568 | 1.1402 | 0.54928 | -16.7379 | 3.7809 | 0.2428 | -0.25545 | 0.16477 | -1.2041 | -0.28641 | 0.067626 | 0.123
42838.4215 | 104 | 22.9034 | 22.8623 | 22.86 | 22.7726 | 22.3943 | 21.7293 | 22.7007 | 21.7839 | 22.3576 | 22.3663 | 22.3406 | 21.9996 | 21.2086 | 22.1816 | 21.6034 | 21.77 | 21.8924 | 21.079 | 21.1789 | 21.386 | 20.47 | 20.607 | 20.9091 | 21.8687 | 21.6271 | 21.3918 | 73.7874 | 64.9218 | 85.6372 | 22.0818 | 21.6825 | 21.2601 | 21.9971 | 21.7334 | 21.4499 | 23.3157 | 78.3345 |  | 32.8728 | 53.7435 | 61.0078 | 37.0969 |  | 17.024 | 17.0343 | 16.68 | 17.0388 | 17.2574 | 18.5019 | 34.8668 | 15.4002 | 17.0351 | 15.8842 | 17.1786 | 18.05 | 45.0905 | 48.1298 | 43.8625 | 21.4775 |  |  | 0.72503 | -0.29511 | -52.4899 | 0.65247 | 0.036272 | -197.8098 | 10.1704 | 0.49905 | -0.069963 | 0.00137 | -0.026617 | 8.8293 | 9.0592 | 1.9586 | 21.7844 | 22.0077 | 22.1878 | 22.2422 | 22.0622 | 21.364 | 20.1725 | 22.1823 | 22.3578 | 22.3866 | 22.3314 | 21.9585 | 21.1761 | 22.2522 | 33.6177 | 22.1822 | 24.5475 | 20.5536 | 19.4142 | 18.9685 | 17.4104 | 22.3946 | 22.1467 | 21.6952 | 22.0827 | 21.7894 | 21.2942 | 21.9328 | 21.5094 | 20.9006 | 23.301 | 73.9937 | 46.2381 | 34.615 | 0.23554 | -0.11941 | 31.8904 | 22.0632 | 22.3584 | 20.1491 | 21.6434 | 22.0939 | 21.9378 | 21.6975 | 21.5432 | 21.7662 | 21.4307 | 21.0787 | 65.329 | 85.0476 | 47.6329 | 48.0942 | 30.2773 |  | 23.0513 | 48.5027 | 24.1452 | 32.934 | 23.4745 | 29.4211 |  | 28.465 |  |  | 20.7683 | 21.2042 | 28.7361 | [5 empty] | 21.8976 | 26.4048 | 21.6409 | 22.0097 | 23.9782 | 21.1352 | 21.7432 | 20.8492 | 28.7343 | 97.8342 |  | 23.6064 | 58.817 | 19.3599 | 24.8508 | 65.1383 | 23.9715 | 46.8255 | 19.9911 | 43.2712 | 20.1211 | 44.7225 | 18.8671 | 24.2742 | 57.1194 | 21.2376 | 26.3906 | 81.825 | 19.5754 | 24.8682 | 66.6501 | 19.5708 | 41.5363 | 21.4742 | 43.5013 | 19.9697 | 44.6386 | 0.16274 | 20.5194 | 0.3287 | 0.016197 | -26.9802 | 3.0955 | 58.19 | 54.55 | 1.124 | -0.6449 | -8.6009 | 0.95893 | 0.22667 | -16.7388 | 3.7955 | 0.23572 | -0.23367 | 0.17618 | -1.2148 | -0.38887 | 0.055195 | 0.12364
42838.4215 | 105 | 22.9071 | 22.8687 | 22.8552 | 22.781 | 22.3942 | 21.7375 | 22.714 | 21.7891 | 22.36 | 22.3676 | 22.3406 | 22.009 | 21.217 | 22.1805 | 21.596 | 21.775 | 21.8969 | 21.0873 | 21.1787 | 21.3885 | 20.474 | 20.6091 | 20.9119 | 21.8686 | 21.6267 | 21.3996 | 74.1999 | 65.2982 | 86.1117 | 22.0789 | 21.685 | 21.264 | 21.9975 | 21.7355 | 21.4608 | 23.397 | 78.7792 |  | 33.0475 | 54.0272 | 61.3581 | 37.1974 |  | 17.0233 | 17.0372 | 16.6681 | 17.0268 | 17.2366 | 18.5296 | 35.3478 | 15.4024 | 17.0376 | 15.8431 | 17.1787 | 18.0499 | 45.1055 | 48.1016 | 43.8675 | 21.4829 |  |  | 0.64026 | -0.26422 | -51.8584 | 0.61962 | 0.088844 | -197.8782 | 10.2769 | 0.64164 | 0.092723 | 0.090535 | 0.02147 | 8.8282 | 9.058 | 1.9572 | 21.7913 | 22.0104 | 22.1849 | 22.2484 | 22.0647 | 21.3661 | 20.17 | 22.1855 | 22.3562 | 22.3861 | 22.3391 | 21.9605 | 21.1753 | 22.2482 | 34.6546 | 23.4631 | 24.965 | 21.1214 | 19.6089 | 19.0706 | 17.452 | 22.4063 | 22.1625 | 21.7047 | 22.0902 | 21.7999 | 21.2956 | 21.9426 | 21.5223 | 20.9129 | 23.368 | 74.3257 | 46.6021 | 34.6228 | 0.25756 | -0.22479 | 31.9587 | 22.0627 | 22.3623 | 20.1515 | 21.649 | 22.0914 | 21.9387 | 21.6997 | 21.5552 | 21.7693 | 21.4287 | 21.084 | 65.791 | 85.5228 | 47.8759 | 48.3204 | 30.3541 |  | 23.1048 | 48.3251 | 24.2157 | 33.106 | 23.539 | 29.4737 |  | 28.6014 |  |  | 20.7865 | 21.2231 | 28.8262 | [5 empty] | 21.9101 | 26.4779 | 21.6471 | 22.016 | 24.0137 | 21.136 | 21.753 | 20.8616 | 28.8981 | 98.0473 |  | 23.6934 | 59.2045 | 19.3727 | 24.9628 | 65.6189 | 24.0174 | 47.1699 | 20.0026 | 43.6733 | 20.134 | 45.0641 | 18.8708 | 24.3725 | 57.413 | 21.2644 | 26.4827 | 82.1716 | 19.5852 | 24.9326 | 67.0212 | 19.5884 | 41.6631 | 21.5042 | 43.8835 | 19.9824 | 44.9408 | 0.014708 | 20.5098 | 0.33487 | 0.017206 | -27.0242 | 3.0955 | 69.71 | 51.19 | 1.0569 | -0.61023 | -8.549 | 0.93448 | 0.35476 | -16.7424 | 3.8155 | 0.23539 | -0.22635 | 0.17358 | -1.3181 | -0.43041 | 0.055143 | 0.12568
42838.4215 | 106 | 22.9136 | 22.8747 | 22.8615 | 22.7781 | 22.3993 | 21.7364 | 22.7115 | 21.7883 | 22.3676 | 22.3692 | 22.342 | 22.0053 | 21.2157 | 22.1879 | 21.59 | 21.7711 | 21.8896 | 21.0811 | 21.1714 | 21.3896 | 20.4651 | 20.6074 | 20.9133 | 21.8676 | 21.6235 | 21.3985 | 74.562 | 65.6811 | 86.4381 | 22.0966 | 21.6854 | 21.265 | 22.0026 | 21.7422 | 21.4692 | 23.4746 | 80.2147 |  | 33.2128 | 54.3177 | 61.6775 | 37.2017 |  | 17.0136 | 17.0371 | 16.6614 | 17.0142 | 17.2232 | 18.5562 | 35.7062 | 15.4163 | 17.0224 | 15.8154 | 17.1838 | 18.051 | 45.1142 | 48.0648 | 43.8745 | 21.4821 |  |  | 0.59229 | -0.33585 | -51.5404 | 0.74315 | 0.084244 | -197.848 | 10.361 | 0.48459 | 0.065284 | 0.087808 | -0.047796 | 8.8286 | 9.0585 | 1.9544 | 21.8029 | 22.0147 | 22.1908 | 22.2556 | 22.0596 | 21.3672 | 20.17 | 22.1883 | 22.3554 | 22.3891 | 22.3415 | 21.961 | 21.184 | 22.2533 | 34.9974 | 23.1151 | 25.0677 | 21.4979 | 20.0138 | 19.1759 | 17.5032 | 22.3998 | 22.1624 | 21.6959 | 22.0796 | 21.7942 | 21.2852 | 21.9392 | 21.5184 | 20.9045 | 23.4313 | 74.7552 | 46.9887 | 34.8611 | 0.2375 | -0.32806 | 31.9067 | 22.0669 | 22.358 | 20.1575 | 21.6481 | 22.0925 | 21.9337 | 21.7072 | 21.5682 | 21.7635 | 21.4306 | 21.0864 | 66.1951 | 86.0164 | 48.1822 | 48.6007 | 30.2967 |  | 23.1562 | 48.5714 | 24.282 | 33.3599 | 23.5986 | 29.5003 |  | 28.7304 |  |  | 20.7915 | 21.2378 | 28.9503 | [5 empty] | 21.9068 | 26.5487 | 21.6414 | 22.0128 | 24.0373 | 21.1348 | 21.7482 | 20.8745 | 29.0394 | 98.352 |  | 23.7901 | 59.5864 | 19.3844 | 25.0668 | 66.0549 | 24.0508 | 47.4493 | 20.024 | 43.9481 | 20.1484 | 45.422 | 18.8649 | 24.5002 | 57.7571 | 21.2815 | 26.5842 | 82.4198 | 19.589 | 25.0248 | 67.4022 | 19.5982 | 41.8376 | 21.5253 | 44.2007 | 19.9942 | 45.2292 | 0.05459 | 20.5027 | 0.34126 | 0.017134 | -27.0205 | 3.0955 | 50.89 | 52.23 | 1.017 | -0.68799 | -8.5228 | 1.0234 | 0.34547 | -16.7419 | 3.8313 | 0.23872 | -0.23096 | 0.16853 | -1.3439 | -0.43585 | 0.057639 | 0.12119
42838.4215 | 107 | 22.907 | 22.8669 | 22.8587 | 22.773 | 22.3964 | 21.7255 | 22.7131 | 21.7876 | 22.3614 | 22.3634 | 22.3395 | 22.0002 | 21.2138 | 22.1807 | 21.5917 | 21.7652 | 21.8877 | 21.0792 | 21.1718 | 21.392 | 20.468 | 20.6116 | 20.909 | 21.8685 | 21.6265 | 21.4089 | 74.8637 | 66.1252 | 86.3482 | 22.088 | 21.6781 | 21.2674 | 21.999 | 21.7364 | 21.4679 | 23.5513 | 81.1813 |  | 33.3519 | 54.6512 | 61.9596 | 38.1588 |  | 17.0205 | 17.0552 | 16.6766 | 17.0214 | 17.238 | 18.5913 | 36.2607 | 15.5027 | 17.0292 | 15.8626 | 17.1943 | 18.0493 | 45.1192 | 48.0236 | 43.8898 | 21.4845 |  |  | 0.68232 | -0.19457 | -50.9542 | 0.56245 | 0.25772 | -197.8828 | 10.4405 | 0.64361 | 0.20112 | 0.14865 | 0.081362 | 8.8286 | 9.0584 | 1.9518 | 21.7956 | 21.9995 | 22.1856 | 22.2473 | 22.0692 | 21.3639 | 20.1656 | 22.1829 | 22.3497 | 22.3777 | 22.3378 | 21.9534 | 21.1803 | 22.2464 | 35.4391 | 23.3313 | 24.7398 | 21.5055 | 20.0038 | 19.278 | 17.5289 | 22.3904 | 22.157 | 21.7036 | 22.0765 | 21.7882 | 21.2861 | 21.9281 | 21.5141 | 20.9015 | 23.5143 | 75.2508 | 47.3778 | 35.0671 | 0.26916 | -0.13197 | 31.9614 | 22.065 | 22.359 | 20.1688 | 21.65 | 22.0957 | 21.933 | 21.7089 | 21.5839 | 21.7614 | 21.4365 | 21.0878 | 66.628 | 86.5295 | 48.5544 | 48.9351 | 30.0768 |  | 23.2037 | 48.7076 | 24.3445 | 33.789 | 23.6695 | 29.4763 |  | 28.8639 |  |  | 20.7978 | 21.2414 | 28.8659 | [5 empty] | 21.8984 | 26.5949 | 21.6364 | 22.0064 | 24.0489 | 21.1297 | 21.7397 | 20.8817 | 29.1167 | 98.4425 |  | 23.8893 | 59.9771 | 19.3838 | 25.1621 | 66.342 | 24.0829 | 47.7598 | 20.0413 | 44.1057 | 20.1538 | 45.759 | 18.8581 | 24.6571 | 58.1113 | 21.2963 | 26.6689 | 82.8768 | 19.5897 | 25.1743 | 67.6941 | 19.6074 | 42.0851 | 21.5472 | 44.5681 | 20.0156 | 45.5052 | 0.18481 | 20.494 | 0.34647 | 0.017467 | -27.0085 | 3.0955 | 63.46 | 52.12 | 1.0915 | -0.52367 | -8.4744 | 0.89035 | 0.60428 | -16.7444 | 3.8462 | 0.24643 | -0.23263 | 0.159 | -1.3811 | -0.39641 | 0.033637 | 0.11827
42838.4215 | 108 | 22.9094 | 22.8777 | 22.8628 | 22.7752 | 22.4001 | 21.7289 | 22.7104 | 21.786 | 22.3672 | 22.3688 | 22.3445 | 22.007 | 21.2096 | 22.1836 | 21.5945 | 21.7704 | 21.8958 | 21.0817 | 21.1844 | 21.3932 | 20.4723 | 20.6122 | 20.908 | 21.8683 | 21.6344 | 21.4158 | 75.1302 | 66.5764 | 86.4957 | 22.0874 | 21.6854 | 21.274 | 22.0023 | 21.7419 | 21.4771 | 23.6363 | 81.3984 |  | 33.5093 | 55.0084 | 62.2396 | 38.4537 |  | 17.0186 | 17.0579 | 16.676 | 17.0191 | 17.2249 | 18.6088 | 36.4494 | 15.5775 | 17.0402 | 15.8989 | 17.2028 | 18.0524 | 45.1255 | 47.9867 | 43.8972 | 21.4841 |  |  | 0.56272 | -0.17157 | -50.7742 | 0.57953 | 0.1309 | -197.8434 | 10.5785 | 0.52665 | 0.01138 | 0.19271 | -0.00266 | 8.8279 | 9.0577 | 1.9491 | 21.8034 | 22.004 | 22.1901 | 22.2441 | 22.0675 | 21.3664 | 20.1774 | 22.1858 | 22.3549 | 22.3789 | 22.3431 | 21.9536 | 21.1835 | 22.2466 | 36.0398 | 23.9785 | 24.6066 | 21.3372 | 19.8265 | 19.3938 | 17.5581 | 22.3957 | 22.1475 | 21.7021 | 22.0784 | 21.7868 | 21.2811 | 21.9307 | 21.5119 | 20.9111 | 23.5842 | 75.8776 | 47.7258 | 35.0287 | 0.31909 | -0.056839 | 31.9824 | 22.059 | 22.358 | 20.1702 | 21.6485 | 22.0928 | 21.934 | 21.6983 | 21.5909 | 21.7639 | 21.4331 | 21.0938 | 67.0988 | 86.8047 | 48.8911 | 49.2956 | 29.9049 |  | 23.2503 | 48.4327 | 24.4165 | 34.2381 | 23.7421 | 29.6597 |  | 29.0075 |  |  | 20.8066 | 21.2512 | 28.7696 | [5 empty] | 21.8929 | 26.6697 | 21.6314 | 22.0068 | 24.0566 | 21.1251 | 21.738 | 20.8957 | 29.2083 | 98.385 |  | 23.9844 | 60.2941 | 19.3978 | 25.2838 | 66.6157 | 24.1191 | 48.1561 | 20.0568 | 44.2593 | 20.1683 | 46.0953 | 18.8586 | 24.7753 | 58.4531 | 21.3152 | 26.7354 | 83.0888 | 19.5921 | 25.2997 | 67.9379 | 19.6194 | 42.3988 | 21.5686 | 44.8508 | 20.0349 | 45.7519 | 0.20985 | 20.4869 | 0.35256 | 0.017046 | -27.0526 | 3.0955 | 52.91 | 51.54 | 0.99141 | -0.49175 | -8.4595 | 0.90378 | 0.43067 | -16.7432 | 3.8716 | 0.25277 | -0.22257 | 0.14897 | -1.4343 | -0.37821 | 0.028309 | 0.12169
42838.4215 | 109 | 22.9044 | 22.8725 | 22.8546 | 22.7768 | 22.3989 | 21.7355 | 22.7149 | 21.7815 | 22.3645 | 22.3645 | 22.3408 | 22.0047 | 21.2087 | 22.1796 | 21.5932 | 21.7727 | 21.8973 | 21.0763 | 21.1809 | 21.3923 | 20.467 | 20.6107 | 20.9081 | 21.8666 | 21.6279 | 21.4155 | 75.464 | 66.9682 | 86.6044 | 22.0868 | 21.6827 | 21.2757 | 22.0037 | 21.7356 | 21.4809 | 23.7134 | 80.8019 |  | 33.6616 | 55.3592 | 62.5172 | 37.957 |  | 17.0111 | 17.0493 | 16.6758 | 17.0137 | 17.2232 | 18.5657 | 36.8489 | 15.6416 | 17.0376 | 15.9107 | 17.2019 | 18.0512 | 45.1478 | 47.9534 | 43.9007 | 21.487 |  |  | 0.76643 | -0.18012 | -50.8504 | 0.6597 | 0.15258 | -197.8637 | 10.5187 | 0.61404 | 0.056917 | 0.069135 | 0.028241 | 8.8286 | 9.0585 | 1.9486 | 21.7952 | 22.002 | 22.1919 | 22.245 | 22.0605 | 21.3676 | 20.1696 | 22.1877 | 22.3601 | 22.3921 | 22.3367 | 21.9468 | 21.1736 | 22.2534 | 36.9336 | 24.9874 | 25.1426 | 21.3273 | 19.5459 | 19.5212 | 17.616 | 22.3971 | 22.1538 | 21.7047 | 22.0848 | 21.7916 | 21.2856 | 21.9295 | 21.5118 | 20.9056 | 23.6538 | 76.2211 | 47.9987 | 34.8782 | 0.2149 | -0.25294 | 32.0548 | 22.0592 | 22.3582 | 20.1692 | 21.6494 | 22.0897 | 21.9356 | 21.6983 | 21.5981 | 21.7682 | 21.4328 | 21.0986 | 67.5638 | 87.0906 | 49.2111 | 49.6365 | 29.8627 |  | 23.3153 | 48.6918 | 24.4851 | 34.7015 | 23.8044 | 29.9274 |  | 29.1397 |  |  | 20.8232 | 21.2603 | 28.8246 | [5 empty] | 21.8942 | 26.7665 | 21.6289 | 22.0056 | 24.0739 | 21.1248 | 21.7364 | 20.9109 | 29.3556 | 98.3732 |  | 24.0758 | 60.5879 | 19.411 | 25.4099 | 66.8879 | 24.1498 | 48.5142 | 20.0805 | 44.4752 | 20.1811 | 46.3867 | 18.8553 | 24.8434 | 58.7646 | 21.328 | 26.8133 | 83.2744 | 19.5919 | 25.3992 | 68.1672 | 19.6239 | 42.6455 | 21.5876 | 45.0357 | 20.0475 | 45.9885 | 0.33284 | 20.4773 | 0.35823 | 0.016081 | -27.0665 | 3.0955 | 39.1 | 52.8 | 1.1572 | -0.50384 | -8.4657 | 0.96425 | 0.46494 | -16.7429 | 3.8604 | 0.25613 | -0.22745 | 0.13821 | -1.5187 | -0.431 | 0.044705 | 0.12822
42838.4216 | 110 | 22.9011 | 22.8712 | 22.8514 | 22.7767 | 22.3961 | 21.731 | 22.7135 | 21.7815 | 22.366 | 22.3639 | 22.336 | 22.0038 | 21.2136 | 22.1837 | 21.5977 | 21.773 | 21.8916 | 21.081 | 21.1763 | 21.3905 | 20.4678 | 20.6131 | 20.914 | 21.8655 | 21.6242 | 21.429 | 75.8213 | 67.2916 | 86.4716 | 22.0795 | 21.6741 | 21.2788 | 21.9988 | 21.7351 | 21.4744 | 23.7703 | 80.2475 |  | 33.8131 | 55.7735 | 62.8434 | 37.4229 |  | 16.9993 | 17.0455 | 16.673 | 17.0117 | 17.2124 | 18.5554 | 36.8997 | 15.6602 | 17.0398 | 16.0419 | 17.1987 | 18.0528 | 45.1749 | 47.9342 | 43.9228 | 21.493 |  |  | 0.68166 | -0.23531 | -50.5409 | 0.52105 | 0.284 | -197.8499 | 10.9228 | 0.54899 | 0.061392 | 0.19627 | 0.084314 | 5.1201 | 8.9829 | 1.9502 | 21.788 | 22.0042 | 22.1936 | 22.242 | 22.0587 | 21.3616 | 20.1726 | 22.1883 | 22.3518 | 22.3918 | 22.3348 | 21.9493 | 21.1847 | 22.2502 | 38.2121 | 26.4708 | 25.122 | 21.221 | 19.1314 | 19.655 | 17.6601 | 22.3955 | 22.1638 | 21.7024 | 22.0914 | 21.7991 | 21.2896 | 21.9401 | 21.5079 | 20.9142 | 23.722 | 76.3459 | 48.2464 | 34.7311 | 0.18757 | -0.19283 | 32.1999 | 22.0596 | 22.3556 | 20.1649 | 21.6445 | 22.0833 | 21.9312 | 21.6931 | 21.6021 | 21.765 | 21.4248 | 21.0944 | 68.0235 | 87.3305 | 49.5679 | 50.0029 | 30.1881 |  | 23.3782 | 49.6724 | 24.5652 | 35.048 | 23.8682 | 29.7663 |  | 29.2554 |  |  | 20.8425 | 21.273 | 28.8587 | [5 empty] | 21.897 | 26.8297 | 21.6358 | 22.0054 | 24.105 | 21.1308 | 21.7429 | 20.9283 | 29.491 | 98.3516 |  | 24.1735 | 60.8597 | 19.4183 | 25.5746 | 67.2234 | 24.183 | 48.8702 | 20.0996 | 44.7824 | 20.1932 | 46.6624 | 18.8516 | 24.9763 | 59.0977 | 21.339 | 26.9047 | 83.5864 | 19.5926 | 25.5136 | 68.4305 | 19.6343 | 42.8185 | 21.6198 | 45.2827 | 20.0626 | 46.2353 | 0.1121 | 20.4685 | 0.36407 | 0.01619 | -27.0879 | 3.0955 | 54.48 | 51.46 | 1.0911 | -0.57588 | -8.4398 | 0.85694 | 0.63431 | -16.742 | 3.9338 | 0.24921 | -0.25199 | 0.13073 | -1.6451 | -0.42357 | 0.061462 | 0.13461
42838.4216 | 111 | 22.9106 | 22.8745 | 22.8615 | 22.7804 | 22.4019 | 21.7284 | 22.7237 | 21.7892 | 22.3691 | 22.3702 | 22.3447 | 22.0043 | 21.2165 | 22.1865 | 21.6019 | 21.7785 | 21.9007 | 21.0898 | 21.1836 | 21.4006 | 20.4805 | 20.6161 | 20.9216 | 21.8712 | 21.628 | 21.4393 | 76.2788 | 67.5777 | 87.1261 | 22.0896 | 21.6753 | 21.2783 | 22.0009 | 21.731 | 21.4795 | 23.821 | 79.3991 |  | 33.9554 | 56.1935 | 63.1981 | 37.779 |  | 16.9962 | 17.04 | 16.6687 | 17.0185 | 17.2066 | 18.5859 | 36.7991 | 15.648 | 17.0366 | 16.0743 | 17.2021 | 18.0551 | 45.1782 | 47.905 | 43.9293 | 21.4913 |  |  | 0.61003 | -0.013865 | -49.7044 | 0.63013 | 0.25575 | -197.8401 | 11.1062 | 0.53782 | -0.015475 | 0.068506 | -0.049532 | 0.00026449 | 8.8806 | 1.9499 | 21.7919 | 22.0057 | 22.192 | 22.2505 | 22.0621 | 21.3696 | 20.1754 | 22.1868 | 22.3568 | 22.3918 | 22.3319 | 21.9593 | 21.1875 | 22.2501 | 39.2705 | 26.9082 | 26.5804 | 21.4208 | 18.7423 | 19.7973 | 17.7209 | 22.3934 | 22.1591 | 21.7039 | 22.0778 | 21.796 | 21.2905 | 21.9373 | 21.5128 | 20.9142 | 23.7755 | 76.5978 | 48.4634 | 34.8338 | 0.21745 | -0.30372 | 32.347 | 22.0549 | 22.3504 | 20.1686 | 21.6398 | 22.083 | 21.9254 | 21.6888 | 21.615 | 21.7627 | 21.4212 | 21.0922 | 68.4252 | 87.5259 | 49.8971 | 50.3483 | 30.657 |  | 23.4281 | 50.3549 | 24.656 | 35.3105 | 23.9304 | 29.716 |  | 29.382 |  |  | 20.8517 | 21.292 | 28.8381 | [5 empty] | 21.9033 | 26.9184 | 21.643 | 22.0119 | 24.1382 | 21.1332 | 21.7456 | 20.9384 | 29.5862 | 98.8285 |  | 24.2855 | 61.2157 | 19.4222 | 25.7704 | 67.5614 | 24.2158 | 49.2366 | 20.1064 | 45.1552 | 20.2086 | 46.8927 | 18.8453 | 25.1583 | 59.4399 | 21.3501 | 26.9856 | 83.8395 | 19.5976 | 25.5949 | 68.7103 | 19.6442 | 43.0348 | 21.651 | 45.5799 | 20.0699 | 46.5158 | 0.27849 | 20.4593 | 0.3702 | 0.015667 | -27.0326 | 3.0955 | 41.19 | 52.29 | 1.0331 | -0.13979 | -8.3696 | 0.94237 | 0.60196 | -16.7424 | 3.9668 | 0.23787 | -0.26788 | 0.12554 | -1.7461 | -0.57853 | 0.053279 | 0.13356
42838.4216 | 112 | 22.9135 | 22.8734 | 22.8653 | 22.7869 | 22.4016 | 21.733 | 22.7249 | 21.791 | 22.3612 | 22.3725 | 22.343 | 22.0003 | 21.2138 | 22.1847 | 21.6016 | 21.7714 | 21.9017 | 21.0882 | 21.1711 | 21.3994 | 20.476 | 20.6116 | 20.9264 | 21.8699 | 21.6307 | 21.4403 | 76.6562 | 67.8461 | 87.4305 | 22.0873 | 21.6742 | 21.2786 | 22.0071 | 21.7308 | 21.4917 | 23.8939 | 79.8648 |  | 34.1029 | 56.5977 | 63.5384 | 38.2778 |  | 16.9988 | 17.0425 | 16.6728 | 17.0165 | 17.204 | 18.5743 | 36.7823 | 15.6496 | 17.0353 | 16.0778 | 17.1983 | 18.0536 | 45.1833 | 47.8722 | 43.9566 | 21.4962 |  |  | 0.62909 | -0.18997 | -49.3075 | 0.48097 | 0.076356 | -197.8388 | 11.0332 | 0.66464 | 0.056333 | -0.051919 | 0.087786 | 0.00030885 | 8.8811 | 1.9503 | 21.7934 | 22.0054 | 22.1894 | 22.2463 | 22.0601 | 21.365 | 20.1792 | 22.1784 | 22.3558 | 22.382 | 22.3367 | 21.9573 | 21.1827 | 22.2503 | 40.0314 | 27.5366 | 26.2374 | 21.7476 | 19.3684 | 19.9411 | 17.7711 | 22.3929 | 22.1526 | 21.7009 | 22.081 | 21.7968 | 21.3033 | 21.9422 | 21.5147 | 20.9225 | 23.8557 | 76.7881 | 48.7047 | 34.8133 | 0.19484 | -0.1352 | 32.5016 | 22.0532 | 22.3494 | 20.1777 | 21.6455 | 22.0854 | 21.9301 | 21.697 | 21.6321 | 21.7658 | 21.4269 | 21.0985 | 68.7865 | 87.8536 | 50.2176 | 50.6887 | 30.9395 |  | 23.5017 | 50.692 | 24.749 | 35.5191 | 24.0087 | 29.8249 |  | 29.516 |  |  | 20.8646 | 21.2992 | 28.812 | [5 empty] | 21.8985 | 27.004 | 21.6404 | 22.0187 | 24.1557 | 21.1319 | 21.7499 | 20.956 | 29.7156 | 99.1349 |  | 24.4834 | 61.6258 | 19.4275 | 25.9178 | 67.8856 | 24.2556 | 49.5134 | 20.1237 | 45.5423 | 20.2293 | 47.142 | 18.8343 | 25.2871 | 59.7478 | 21.3564 | 27.0418 | 84.081 | 19.5965 | 25.6508 | 68.9125 | 19.6515 | 43.3174 | 21.6633 | 45.8496 | 20.0846 | 46.8617 | 0.014151 | 20.4505 | 0.37477 | 0.015311 | -26.9954 | 3.0955 | 41.57 | 52.16 | 1.0496 | -0.51744 | -8.3362 | 0.82332 | 0.32891 | -16.7421 | 3.9537 | 0.2325 | -0.2741 | 0.12239 | -1.8139 | -0.53454 | 0.041881 | 0.13683
42838.4216 | 113 | 22.9173 | 22.8787 | 22.8707 | 22.7804 | 22.4041 | 21.7281 | 22.725 | 21.7788 | 22.3612 | 22.3802 | 22.3381 | 21.9999 | 21.2214 | 22.1775 | 21.6014 | 21.7669 | 21.8963 | 21.0861 | 21.1761 | 21.3955 | 20.4657 | 20.6139 | 20.9224 | 21.8698 | 21.6315 | 21.4361 | 76.8649 | 68.1709 | 87.1 | 22.0742 | 21.6807 | 21.2888 | 21.9985 | 21.7222 | 21.4907 | 23.9467 | 79.9231 |  | 34.2559 | 56.9025 | 63.8491 | 38.7123 |  | 16.9983 | 17.04 | 16.658 | 17.0153 | 17.2067 | 18.5901 | 36.8389 | 15.611 | 17.0368 | 16.0396 | 17.2139 | 18.0597 | 45.1835 | 47.8395 | 43.9708 | 21.4981 |  |  | 0.56075 | -0.1788 | -49.1649 | 0.6551 | 0.2045 | -197.8315 | 11.0602 | 0.60353 | 0.014494 | 0.082143 | 0.046469 | 0.00026778 | 8.881 | 1.9525 | 21.7904 | 22.0032 | 22.1881 | 22.2462 | 22.0606 | 21.3629 | 20.1757 | 22.1899 | 22.3524 | 22.3851 | 22.3408 | 21.9573 | 21.1838 | 22.249 | 40.3005 | 27.3777 | 25.9157 | 21.3056 | 19.6908 | 20.0721 | 17.8051 | 22.3933 | 22.1546 | 21.698 | 22.0874 | 21.7911 | 21.2872 | 21.9354 | 21.5143 | 20.9143 | 23.91 | 77.135 | 48.9492 | 34.9645 | 0.31261 | -0.15707 | 32.5882 | 22.0582 | 22.3535 | 20.1784 | 21.6437 | 22.0873 | 21.933 | 21.6942 | 21.6418 | 21.7679 | 21.4269 | 21.1063 | 69.1615 | 88.2865 | 50.4848 | 51.0122 | 31.2043 |  | 23.5589 | 50.4585 | 24.8187 | 35.6689 | 24.0728 | 29.8584 |  | 29.6458 |  |  | 20.8693 | 21.2948 | 29.0054 | [5 empty] | 21.9003 | 27.098 | 21.635 | 22.0125 | 24.1691 | 21.1326 | 21.7522 | 20.9812 | 29.8938 | 99.4084 |  | 24.6771 | 61.9866 | 19.437 | 26.0321 | 68.1019 | 24.2958 | 49.9298 | 20.1453 | 46.0014 | 20.2482 | 47.452 | 18.8312 | 25.4253 | 60.0553 | 21.3696 | 27.0961 | 84.3947 | 19.6083 | 25.7568 | 69.1648 | 19.6536 | 43.6223 | 21.6704 | 46.1027 | 20.092 | 47.1671 | 0.15921 | 20.4416 | 0.37957 | 0.014876 | -27.0854 | 3.0955 | 41.69 | 51.23 | 0.9905 | -0.50199 | -8.3241 | 0.96087 | 0.53828 | -16.7422 | 3.9586 | 0.22707 | -0.26526 | 0.12038 | -1.8284 | -0.49483 | 0.031591 | 0.13446
42838.4216 | 114 | 22.9085 | 22.8751 | 22.867 | 22.7757 | 22.4089 | 21.7328 | 22.7238 | 21.7874 | 22.3645 | 22.3734 | 22.3453 | 22.0069 | 21.2095 | 22.1839 | 21.5898 | 21.7725 | 21.8886 | 21.0803 | 21.1772 | 21.3916 | 20.4636 | 20.6056 | 20.9214 | 21.8609 | 21.6228 | 21.4513 | 77.054 | 68.4816 | 87.321 | 22.0868 | 21.6872 | 21.2904 | 22.0015 | 21.7341 | 21.5039 | 24.0179 | 80.1973 |  | 34.4376 | 57.1909 | 64.1386 | 38.7521 |  | 16.9929 | 17.0478 | 16.6544 | 17.0108 | 17.2024 | 18.6029 | 36.9983 | 15.5583 | 17.0401 | 15.9959 | 17.223 | 18.059 | 45.165 | 47.8111 | 43.9767 | 21.4993 |  |  | 0.56141 | -0.34834 | -48.7614 | 0.49411 | 0.39046 | -197.8368 | 10.9314 | 0.59302 | -0.029097 | 0.11403 | 0.075634 | 0.0002727 | 8.8812 | 1.9535 | 21.7825 | 22.0019 | 22.1903 | 22.2451 | 22.0621 | 21.3612 | 20.172 | 22.1834 | 22.3547 | 22.3801 | 22.3354 | 21.956 | 21.1819 | 22.2397 | 40.7268 | 27.0612 | 25.438 | 20.7636 | 19.5781 | 20.2166 | 17.8521 | 22.4067 | 22.1591 | 21.7055 | 22.0891 | 21.7937 | 21.293 | 21.943 | 21.5212 | 20.9241 | 23.9774 | 77.2822 | 49.1992 | 34.958 | 0.30415 | -0.12816 | 32.5954 | 22.067 | 22.3593 | 20.1815 | 21.6454 | 22.0947 | 21.9322 | 21.6981 | 21.6556 | 21.767 | 21.4291 | 21.1164 | 69.4977 | 88.7428 | 50.7146 | 51.2709 | 31.2306 |  | 23.6225 | 50.0777 | 24.8839 | 35.944 | 24.1384 | 29.8359 |  | 29.7815 |  |  | 20.8739 | 21.2976 | 29.352 | [5 empty] | 21.8971 | 27.1767 | 21.637 | 22.0096 | 24.1794 | 21.1281 | 21.7374 | 20.9753 | 30.0911 | 99.7021 |  | 24.7438 | 62.2868 | 19.4272 | 26.1755 | 68.265 | 24.3067 | 50.3048 | 20.1598 | 46.4413 | 20.2499 | 47.7437 | 18.8208 | 25.6076 | 60.2953 | 21.3873 | 27.1709 | 84.545 | 19.6077 | 25.8887 | 69.4962 | 19.6652 | 43.8725 | 21.7001 | 46.3911 | 20.1116 | 47.4776 | 0.17925 | 20.4328 | 0.38545 | 0.014665 | -27.0647 | 3.0955 | 39.49 | 52.55 | 0.99138 | -0.70067 | -8.29 | 0.8345 | 0.74381 | -16.7428 | 3.9356 | 0.22849 | -0.25248 | 0.11496 | -1.8589 | -0.43628 | 0.032887 | 0.13691
42838.4216 | 115 | 22.907 | 22.8653 | 22.8542 | 22.7704 | 22.3984 | 21.7267 | 22.7137 | 21.7816 | 22.3644 | 22.3602 | 22.3504 | 21.9984 | 21.2088 | 22.1818 | 21.5905 | 21.7689 | 21.8916 | 21.0762 | 21.178 | 21.3881 | 20.476 | 20.6017 | 20.9173 | 21.8631 | 21.6274 | 21.4572 | 77.5424 | 68.7711 | 88.1664 | 22.0871 | 21.6802 | 21.2974 | 22.0043 | 21.7314 | 21.508 | 24.079 | 80.313 |  | 34.6207 | 57.4895 | 64.4156 | 38.9155 |  | 16.9897 | 17.047 | 16.6556 | 16.9982 | 17.2055 | 18.5843 | 37.101 | 15.5142 | 17.0384 | 15.9647 | 17.2113 | 18.0544 | 45.1499 | 47.7787 | 43.9774 | 21.4954 |  |  | 0.60215 | -0.20311 | -48.0471 | 0.3824 | 0.087528 | -197.8243 | 11.3257 | 0.64033 | -0.054589 | 0.079416 | 0.21417 | 0.00027599 | 8.8809 | 1.9523 | 21.7911 | 22.0069 | 22.191 | 22.245 | 22.0532 | 21.3641 | 20.1732 | 22.1817 | 22.3568 | 22.3938 | 22.3439 | 21.9553 | 21.1816 | 22.2505 | 41.2715 | 27.546 | 26.2604 | 20.1126 | 19.466 | 20.3516 | 17.9115 | 22.3898 | 22.1536 | 21.6946 | 22.0857 | 21.7971 | 21.2885 | 21.9372 | 21.5136 | 20.9192 | 24.0254 | 77.5037 | 49.3755 | 35.1402 | 0.32696 | -0.034966 | 32.6032 | 22.067 | 22.3581 | 20.1821 | 21.6442 | 22.0944 | 21.9261 | 21.6977 | 21.6623 | 21.7663 | 21.4323 | 21.1175 | 69.7527 | 89.0931 | 50.954 | 51.5211 | 31.56 |  | 23.692 | 50.2056 | 24.9688 | 36.2546 | 24.2006 | 30.0184 |  | 29.902 |  |  | 20.8734 | 21.3123 | 29.4561 | [5 empty] | 21.8974 | 27.2784 | 21.6341 | 22.0014 | 24.1974 | 21.1256 | 21.7453 | 20.9754 | 30.2739 | 100.0058 |  | 24.7485 | 62.4959 | 19.4271 | 26.3523 | 68.4533 | 24.3429 | 50.6118 | 20.1808 | 46.8295 | 20.2658 | 48.0805 | 18.8241 | 25.8217 | 60.5077 | 21.4114 | 27.3025 | 84.7368 | 19.6242 | 26.0132 | 69.7733 | 19.6762 | 44.0896 | 21.7207 | 46.8374 | 20.1315 | 47.7458 | 0.14011 | 20.4265 | 0.39207 | 0.015449 | -27.0419 | 3.0955 | 32.39 | 51.48 | 1.0279 | -0.53504 | -8.229 | 0.73413 | 0.35216 | -16.7417 | 4.0058 | 0.22168 | -0.25316 | 0.10843 | -1.9037 | -0.52072 | 0.03041 | 0.13347
42838.4216 | 116 | 22.9118 | 22.8698 | 22.8594 | 22.7767 | 22.4047 | 21.7294 | 22.7127 | 21.7945 | 22.3663 | 22.3694 | 22.3475 | 22.0018 | 21.2183 | 22.1848 | 21.5911 | 21.7638 | 21.8962 | 21.0761 | 21.1724 | 21.3839 | 20.4769 | 20.6098 | 20.9178 | 21.862 | 21.6222 | 21.46 | 77.8815 | 69.0481 | 88.0672 | 22.0784 | 21.679 | 21.2944 | 21.9957 | 21.7299 | 21.5052 | 24.1396 | 80.3215 |  | 34.7878 | 57.7882 | 64.6686 | 39.3554 |  | 16.9934 | 17.0489 | 16.647 | 16.9988 | 17.2085 | 18.5713 | 36.9452 | 15.5 | 17.0268 | 15.9732 | 17.226 | 18.0624 | 45.1395 | 47.7497 | 44.0012 | 21.4968 |  |  | 0.39056 | -0.094689 | -47.4242 | 0.73527 | 0.0435 | -197.8407 | 11.5445 | 0.64558 | 0.0049584 | 0.11466 | 0.14438 | 0.00029242 | 8.8811 | 1.9478 | 21.7928 | 22.0158 | 22.204 | 22.2515 | 22.071 | 21.3761 | 20.1935 | 22.1851 | 22.3678 | 22.4034 | 22.3449 | 21.964 | 21.1885 | 22.2586 | 42.5329 | 28.4968 | 27.2704 | 20.6308 | 19.4961 | 20.5212 | 17.9856 | 22.3942 | 22.1537 | 21.6997 | 22.0847 | 21.8001 | 21.2939 | 21.9434 | 21.5184 | 20.9233 | 24.1045 | 78.1372 | 49.592 | 35.5996 | 0.39164 | 0.12937 | 32.7822 | 22.0615 | 22.3533 | 20.1781 | 21.6411 | 22.0874 | 21.9247 | 21.6961 | 21.6757 | 21.7618 | 21.4299 | 21.1097 | 70.0921 | 89.3845 | 51.1909 | 51.7732 | 31.8294 |  | 23.7565 | 51.1556 | 25.0494 | 36.4827 | 24.2644 | 30.4885 |  | 30.0246 |  |  | 20.8774 | 21.3228 | 29.7092 | [5 empty] | 21.8954 | 27.3401 | 21.6444 | 22.0151 | 24.2244 | 21.1278 | 21.7495 | 21.0058 | 30.4169 | 100.4677 |  | 24.7811 | 62.8468 | 19.4441 | 26.4997 | 68.7705 | 24.3843 | 50.9373 | 20.1995 | 47.1041 | 20.2807 | 48.3876 | 18.8204 | 26.0074 | 60.7149 | 21.4363 | 27.4005 | 85.2702 | 19.6327 | 26.1002 | 70.1375 | 19.679 | 44.4075 | 21.7427 | 47.2872 | 20.1601 | 48.002 | 0.1696 | 20.4189 | 0.39754 | 0.017068 | -27.0806 | 3.0955 | 44.35 | 51.95 | 0.82774 | -0.36531 | -8.1755 | 1.018 | 0.24825 | -16.7421 | 4.0443 | 0.21637 | -0.27683 | 0.10424 | -2.024 | -0.62429 | 0.020235 | 0.12338
42838.4216 | 117 | 22.9153 | 22.8724 | 22.8565 | 22.7841 | 22.402 | 21.7337 | 22.7186 | 21.7998 | 22.3636 | 22.373 | 22.3441 | 22.0016 | 21.2194 | 22.1857 | 21.6001 | 21.7655 | 21.8913 | 21.0874 | 21.1776 | 21.3827 | 20.4661 | 20.6079 | 20.9203 | 21.8684 | 21.6231 | 21.4697 | 78.205 | 69.285 | 88.4625 | 22.0878 | 21.6822 | 21.2991 | 21.9957 | 21.731 | 21.5136 | 24.205 | 79.9484 |  | 34.9594 | 58.0942 | 64.9316 | 40.1783 |  | 16.9981 | 17.0553 | 16.6526 | 17.0054 | 17.2081 | 18.5697 | 36.898 | 15.503 | 17.0318 | 15.9764 | 17.2337 | 18.0619 | 45.1299 | 47.7172 | 44.0201 | 21.5029 |  |  | 0.64092 | -0.19326 | -46.8775 | 0.79244 | 0.29518 | -197.8519 | 11.6292 | 0.78226 | 0.056333 | 0.25921 | -0.11307 | 0.00027599 | 8.881 | 1.9457 | 21.7916 | 21.9981 | 22.1878 | 22.244 | 22.0613 | 21.3586 | 20.1817 | 22.1825 | 22.3571 | 22.3913 | 22.3406 | 21.9571 | 21.1792 | 22.2521 | 43.8115 | 29.5967 | 30.0195 | 21.0719 | 19.1533 | 20.6889 | 18.0858 | 22.3942 | 22.1534 | 21.7055 | 22.0883 | 21.7957 | 21.2957 | 21.9434 | 21.518 | 20.9324 | 24.1809 | 78.6263 | 49.8281 | 36.1273 | 0.32106 | 0.039022 | 32.9016 | 22.0623 | 22.3578 | 20.1799 | 21.6446 | 22.0881 | 21.9284 | 21.7005 | 21.6907 | 21.7596 | 21.4311 | 21.1126 | 70.4934 | 89.7207 | 51.4369 | 52.0634 | 31.8114 |  | 23.8244 | 52.0817 | 25.142 | 36.4218 | 24.3364 | 30.5276 |  | 30.1523 |  |  | 20.8966 | 21.3494 | 29.7935 | [5 empty] | 21.8923 | 27.3753 | 21.645 | 22.0148 | 24.2618 | 21.1293 | 21.7561 | 21.0192 | 30.524 | 100.7308 |  | 24.8646 | 63.1801 | 19.4605 | 26.5944 | 69.0663 | 24.4237 | 51.2458 | 20.2367 | 47.206 | 20.31 | 48.6642 | 18.8128 | 26.1685 | 60.95 | 21.4411 | 27.4678 | 85.6358 | 19.642 | 26.1459 | 70.3598 | 19.6747 | 44.682 | 21.7531 | 47.5275 | 20.1742 | 48.1898 | 0.16589 | 20.4156 | 0.40388 | 0.017163 | -27.0613 | 3.0956 | 35.8 | 52.4 | 1.0609 | -0.5219 | -8.1283 | 1.0568 | 0.64668 | -16.7425 | 4.0591 | 0.21916 | -0.29943 | 0.10836 | -2.1465 | -0.91806 | -0.00041538 | 0.1113
42838.4216 | 118 | 22.908 | 22.8682 | 22.8586 | 22.7802 | 22.3964 | 21.7281 | 22.7121 | 21.7838 | 22.3593 | 22.3747 | 22.337 | 21.993 | 21.2086 | 22.1818 | 21.5982 | 21.7678 | 21.8949 | 21.093 | 21.1821 | 21.3889 | 20.4751 | 20.6119 | 20.9315 | 21.8716 | 21.6297 | 21.4783 | 78.4624 | 69.5219 | 88.5322 | 22.0838 | 21.6688 | 21.3001 | 21.9908 | 21.7274 | 21.5248 | 24.2769 | 79.7633 |  | 35.123 | 58.3945 | 65.1786 | 40.7254 |  | 16.9943 | 17.0575 | 16.6596 | 17.0046 | 17.2124 | 18.5612 | 37.369 | 15.5026 | 17.0345 | 15.9811 | 17.2402 | 18.0633 | 45.1118 | 47.6782 | 44.0295 | 21.502 |  |  | 0.70006 | -0.23203 | -46.4641 | 0.87918 | 0.16967 | -197.8709 | 11.7383 | 0.60484 | -0.031626 | 0.089906 | 0.15184 | 0.00025956 | 8.8812 | 1.9478 | 21.7815 | 22.0009 | 22.1803 | 22.2389 | 22.0571 | 21.3607 | 20.1786 | 22.1781 | 22.3567 | 22.3875 | 22.3329 | 21.9554 | 21.1784 | 22.2466 | 44.4679 | 29.9622 | 31.8327 | 21.8511 | 19.3731 | 20.8515 | 18.1862 | 22.3921 | 22.153 | 21.7081 | 22.0934 | 21.7921 | 21.2971 | 21.9473 | 21.5156 | 20.9311 | 24.2501 | 79.0235 | 50.0785 | 36.5465 | 0.36903 | -0.10572 | 33.0103 | 22.0582 | 22.3583 | 20.1751 | 21.6447 | 22.091 | 21.9348 | 21.6982 | 21.7 | 21.7635 | 21.4306 | 21.1172 | 70.8236 | 89.9766 | 51.659 | 52.3468 | 31.6616 |  | 23.8773 | 52.5638 | 25.2331 | 36.4189 | 24.4004 | 30.7988 |  | 30.2842 |  |  | 20.8898 | 21.3519 | 29.8557 | [5 empty] | 21.8933 | 27.4274 | 21.6484 | 22.0107 | 24.2862 | 21.1361 | 21.7438 | 21.029 | 30.6794 | 101.0428 |  | 24.9668 | 63.4436 | 19.4635 | 26.6594 | 69.3871 | 24.4763 | 51.4662 | 20.2561 | 47.3109 | 20.3229 | 48.8956 | 18.8155 | 26.2448 | 61.1661 | 21.4572 | 27.5601 | 86.0073 | 19.6508 | 26.2533 | 70.4912 | 19.6876 | 44.9143 | 21.7792 | 47.7293 | 20.1863 | 48.4079 | 0.22469 | 20.4035 | 0.40955 | 0.016524 | -26.9396 | 3.0955 | 46.93 | 51.64 | 1.1089 | -0.57186 | -8.0925 | 1.1132 | 0.49028 | -16.743 | 4.078 | 0.2251 | -0.30974 | 0.11061 | -2.2004 | -1.1078 | -0.013188 | 0.10199
42838.4217 | 119 | 22.9145 | 22.873 | 22.8684 | 22.7869 | 22.4058 | 21.739 | 22.7212 | 21.7888 | 22.3641 | 22.3775 | 22.3459 | 22.002 | 21.2154 | 22.1802 | 21.5963 | 21.7714 | 21.8971 | 21.0874 | 21.1745 | 21.3928 | 20.4739 | 20.6125 | 20.9293 | 21.8636 | 21.6255 | 21.4835 | 78.6689 | 69.8136 | 88.4854 | 22.0921 | 21.687 | 21.3131 | 22.0081 | 21.7459 | 21.5341 | 24.3714 | 79.342 |  | 35.2875 | 58.7073 | 65.4258 | 40.7531 |  | 16.9917 | 17.0554 | 16.659 | 16.9952 | 17.204 | 18.549 | 37.5336 | 15.5303 | 17.0376 | 15.9681 | 17.2419 | 18.0671 | 45.1066 | 47.6445 | 44.0354 | 21.5078 |  |  | 0.58309 | -0.2892 | -45.9345 | 0.63079 | 0.12236 | -197.823 | 12.0662 | 0.59762 | 0.24412 | -0.081501 | 0.091778 | 0.00030885 | 8.881 | 1.9477 | 21.7862 | 22.0019 | 22.1851 | 22.2466 | 22.0541 | 21.3604 | 20.1691 | 22.184 | 22.3543 | 22.3856 | 22.3278 | 21.9558 | 21.1789 | 22.243 | 44.5193 | 29.8176 | 32.2879 | 22.8691 | 20.4646 | 20.9925 | 18.2706 | 22.3972 | 22.1535 | 21.7039 | 22.0936 | 21.797 | 21.296 | 21.9442 | 21.5222 | 20.9347 | 24.3078 | 79.3514 | 50.2819 | 36.8966 | -0.014536 | -0.07681 | 33.0189 | 22.0532 | 22.347 | 20.1688 | 21.6449 | 22.0811 | 21.9309 | 21.6937 | 21.7101 | 21.7649 | 21.423 | 21.1169 | 71.1139 | 90.1275 | 51.8786 | 52.6225 | 31.6768 |  | 23.9361 | 52.5993 | 25.3099 | 36.5453 | 24.468 | 31.069 |  | 30.3968 |  |  | 20.8888 | 21.352 | 30.0206 | [5 empty] | 21.9012 | 27.5014 | 21.6362 | 22.0087 | 24.3016 | 21.1377 | 21.7484 | 21.0373 | 30.8552 | 101.3367 |  | 25.0746 | 63.6122 | 19.469 | 26.6999 | 69.5866 | 24.5143 | 51.672 | 20.269 | 47.4857 | 20.3396 | 49.1168 | 18.8162 | 26.2603 | 61.334 | 21.4724 | 27.706 | 86.3967 | 19.6574 | 26.4313 | 70.6582 | 19.6883 | 45.127 | 21.8074 | 47.9705 | 20.1975 | 48.6398 | 0.17387 | 20.3884 | 0.41503 | 0.015536 | -27.0137 | 3.0955 | 46.23 | 52.94 | 1.012 | -0.63843 | -8.0462 | 0.94289 | 0.41634 | -16.7407 | 4.1345 | 0.22667 | -0.30813 | 0.10938 | -2.1896 | -1.1485 | -0.010769 | 0.09421
42838.4217 | 120 | 22.9099 | 22.8739 | 22.8618 | 22.7783 | 22.4002 | 21.737 | 22.7147 | 21.786 | 22.3619 | 22.3729 | 22.3393 | 22.0052 | 21.219 | 22.1771 | 21.6044 | 21.7745 | 21.9014 | 21.0889 | 21.183 | 21.3982 | 20.4785 | 20.6149 | 20.9365 | 21.8703 | 21.6365 | 21.5053 | 78.9379 | 70.1332 | 88.9491 | 22.0888 | 21.6841 | 21.3116 | 22.0011 | 21.7337 | 21.5339 | 24.4447 | 78.6895 |  | 35.4574 | 58.9856 | 65.7056 | 40.5087 |  | 16.9806 | 17.0497 | 16.6577 | 16.9889 | 17.1891 | 18.5432 | 37.6113 | 15.5361 | 17.023 | 15.9146 | 17.2379 | 18.0592 | 45.0879 | 47.6043 | 44.0432 | 21.5102 |  |  | 0.92216 | -0.048033 | -45.0783 | 0.66561 | -0.003812 | -197.8098 | 12.3652 | 0.62127 | 0.063922 | 0.10438 | 0.065912 | 0.0002842 | 8.8812 | 1.9445 | 21.7861 | 22.0087 | 22.1906 | 22.2525 | 22.0573 | 21.3637 | 20.1731 | 22.1902 | 22.3559 | 22.3874 | 22.339 | 21.9575 | 21.1926 | 22.2455 | 43.7758 | 28.7661 | 32.6744 | 23.1676 | 20.8133 | 21.1036 | 18.3667 | 22.4009 | 22.1567 | 21.707 | 22.0902 | 21.802 | 21.3011 | 21.9448 | 21.5192 | 20.9431 | 24.3678 | 79.514 | 50.4746 | 37.0387 | 0.20644 | -0.13387 | 32.97 | 22.0583 | 22.3454 | 20.165 | 21.6412 | 22.0757 | 21.9252 | 21.694 | 21.7202 | 21.7667 | 21.4278 | 21.1241 | 71.4289 | 90.3239 | 52.1137 | 52.923 | 32.0207 |  | 24.0083 | 51.9769 | 25.3916 | 36.7263 | 24.5458 | 30.9943 |  | 30.5077 |  |  | 20.8851 | 21.3429 | 30.2294 | [5 empty] | 21.8995 | 27.6191 | 21.6388 | 22.0109 | 24.3263 | 21.1404 | 21.749 | 21.048 | 31.0279 | 101.4125 |  | 25.1661 | 63.8355 | 19.4728 | 26.7747 | 69.7953 | 24.5456 | 51.9097 | 20.286 | 47.6475 | 20.3478 | 49.4294 | 18.8172 | 26.3406 | 61.5765 | 21.4845 | 27.8565 | 86.6243 | 19.6667 | 26.5965 | 70.9178 | 19.7012 | 45.4034 | 21.8316 | 48.221 | 20.2231 | 48.9524 | 0.27292 | 20.3936 | 0.4202 | 0.015827 | -27.0874 | 3.0956 | 36.19 | 51.66 | 1.2735 | -0.26019 | -7.9707 | 0.96856 | -0.073486 | -16.7399 | 4.1853 | 0.21955 | -0.28808 | 0.10697 | -2.0941 | -1.1803 | -0.0015036 | 0.092289
42838.4217 | 121 | 22.9141 | 22.8737 | 22.8587 | 22.7833 | 22.4002 | 21.7355 | 22.7175 | 21.788 | 22.3615 | 22.3707 | 22.3434 | 22.004 | 21.2127 | 22.1836 | 21.6009 | 21.7745 | 21.8927 | 21.0854 | 21.178 | 21.3908 | 20.4698 | 20.6087 | 20.9331 | 21.8704 | 21.6291 | 21.5031 | 79.3499 | 70.4574 | 89.6048 | 22.0888 | 21.6862 | 21.3201 | 22.0022 | 21.7359 | 21.5337 | 24.5088 | 79.2716 |  | 35.6172 | 59.2336 | 65.9315 | 40.4376 |  | 16.9888 | 17.0601 | 16.6585 | 16.9953 | 17.1926 | 18.5355 | 37.7605 | 15.5581 | 17.0341 | 15.9014 | 17.2507 | 18.0659 | 45.0775 | 47.5789 | 44.0642 | 21.5128 |  |  | 0.71386 | -0.16566 | -44.3003 | 0.49608 | 0.33658 | -197.8453 | 12.4697 | 0.5319 | 0.22096 | 0.028224 | 0.11921 | 0.00029406 | 8.8812 | 1.9388 | 21.7946 | 22.009 | 22.1943 | 22.2486 | 22.0674 | 21.3642 | 20.1788 | 22.19 | 22.3568 | 22.3881 | 22.341 | 21.9665 | 21.1908 | 22.2522 | 43.5968 | 27.8407 | 32.7645 | 23.1111 | 21.0608 | 21.2169 | 18.4415 | 22.385 | 22.1505 | 21.6966 | 22.088 | 21.7855 | 21.2906 | 21.931 | 21.5159 | 20.9306 | 24.4327 | 79.6809 | 50.6773 | 37.1179 | 0.23102 | -0.024315 | 32.9735 | 22.0615 | 22.3534 | 20.1714 | 21.6497 | 22.0811 | 21.9269 | 21.702 | 21.7384 | 21.7656 | 21.4312 | 21.1361 | 71.7555 | 90.4896 | 52.3529 | 53.2111 | 32.5706 |  | 24.1001 | 52.4464 | 25.481 | 36.8759 | 24.6201 | 30.7898 |  | 30.6556 |  |  | 20.8614 | 21.3446 | 30.3462 | [5 empty] | 21.8942 | 27.7501 | 21.6362 | 22.0096 | 24.3537 | 21.1318 | 21.7439 | 21.0557 | 31.1939 | 101.9193 |  | 25.248 | 64.1041 | 19.4885 | 26.8549 | 70.0288 | 24.5866 | 52.1694 | 20.3116 | 47.868 | 20.3669 | 49.7351 | 18.807 | 26.4918 | 61.8523 | 21.5044 | 27.959 | 86.9267 | 19.6666 | 26.6914 | 71.2736 | 19.7076 | 45.6726 | 21.8477 | 48.4649 | 20.237 | 49.2876 | 0.014708 | 20.3731 | 0.42543 | 0.016095 | -27.0836 | 3.0956 | 38.47 | 52.21 | 1.1214 | -0.4832 | -7.9018 | 0.83618 | 0.6905 | -16.7412 | 4.2029 | 0.20737 | -0.2981 | 0.10533 | -2.0609 | -1.1815 | 0.0026359 | 0.092276
42838.4217 | 122 | 22.911 | 22.8699 | 22.8495 | 22.7754 | 22.396 | 21.7276 | 22.7081 | 21.782 | 22.3512 | 22.365 | 22.3419 | 21.9919 | 21.2118 | 22.1719 | 21.6013 | 21.774 | 21.8898 | 21.0843 | 21.1784 | 21.3948 | 20.4689 | 20.6144 | 20.9345 | 21.8667 | 21.6249 | 21.505 | 79.7828 | 70.7672 | 89.9088 | 22.0857 | 21.6825 | 21.3236 | 21.9994 | 21.7347 | 21.5467 | 24.5796 | 79.8698 |  | 35.7964 | 59.4813 | 66.213 | 40.4837 |  | 16.9856 | 17.0544 | 16.6567 | 16.9808 | 17.1898 | 18.5176 | 37.6858 | 15.577 | 17.0306 | 15.871 | 17.2497 | 18.0651 | 45.0689 | 47.5499 | 44.0578 | 21.5147 |  |  | 0.57981 | -0.32994 | -43.7135 | 0.86078 | 0.095412 | -197.844 | 12.4855 | 0.40968 | 0.027337 | 0.14508 | 0.13119 | 0.00027928 | 8.8811 | 1.9363 | 21.7902 | 22.004 | 22.1892 | 22.246 | 22.0619 | 21.3708 | 20.1709 | 22.1808 | 22.3604 | 22.3884 | 22.3364 | 21.9557 | 21.1902 | 22.2524 | 43.3276 | 27.0325 | 33.0834 | 23.6095 | 21.1235 | 21.3337 | 18.5224 | 22.3847 | 22.1475 | 21.6934 | 22.0756 | 21.7856 | 21.2886 | 21.9378 | 21.5167 | 20.9316 | 24.503 | 80.1382 | 50.9154 | 37.3163 | 0.18383 | -0.10515 | 33.1444 | 22.055 | 22.355 | 20.1667 | 21.6482 | 22.0829 | 21.9258 | 21.7035 | 21.7513 | 21.7706 | 21.4295 | 21.1398 | 72.0465 | 90.6821 | 52.5899 | 53.4479 | 32.6991 |  | 24.1784 | 52.97 | 25.5698 | 36.9355 | 24.6893 | 30.5706 |  | 30.7842 |  |  | 20.8489 | 21.349 | 30.4572 | [5 empty] | 21.8894 | 27.8624 | 21.6344 | 22.0065 | 24.3842 | 21.1273 | 21.749 | 21.0657 | 31.3479 | 102.1875 |  | 25.3342 | 64.4804 | 19.4989 | 26.9201 | 70.2425 | 24.6327 | 52.457 | 20.3211 | 48.1127 | 20.3753 | 50.0093 | 18.7926 | 26.6633 | 62.1294 | 21.5176 | 28.0085 | 87.2499 | 19.6686 | 26.7256 | 71.6529 | 19.7012 | 45.8844 | 21.8545 | 48.6634 | 20.2514 | 49.5857 | 0.089464 | 20.3722 | 0.43057 | 0.016103 | -27.0119 | 3.0956 | 30.63 | 52.21 | 1.0111 | -0.68192 | -7.8492 | 1.1014 | 0.36763 | -16.7407 | 4.2055 | 0.20644 | -0.30964 | 0.10601 | -2.0174 | -1.2075 | 0.0037451 | 0.089139
42838.4217 | 123 | 22.9084 | 22.8718 | 22.8616 | 22.7711 | 22.4054 | 21.7298 | 22.7127 | 21.7867 | 22.3611 | 22.358 | 22.3424 | 21.9994 | 21.2123 | 22.1757 | 21.6051 | 21.7755 | 21.899 | 21.0879 | 21.1835 | 21.4011 | 20.4744 | 20.6152 | 20.9375 | 21.8705 | 21.6305 | 21.5222 | 79.9751 | 71.0365 | 89.3904 | 22.0928 | 21.676 | 21.3226 | 21.9918 | 21.7361 | 21.554 | 24.6518 | 79.9618 |  | 35.9625 | 59.7429 | 66.4862 | 40.4493 |  | 16.9819 | 17.0509 | 16.6557 | 16.9828 | 17.1882 | 18.4962 | 37.7678 | 15.5965 | 17.0401 | 15.8367 | 17.2567 | 18.0643 | 45.0616 | 47.5161 | 44.0484 | 21.5136 |  |  | 0.76643 | -0.36871 | -43.1483 | 0.61305 | 0.27744 | -197.8256 | 12.6438 | 0.65478 | 0.099923 | 0.091164 | 0.029977 | 0.00024806 | 8.8808 | 1.9359 | 21.7972 | 22.004 | 22.2033 | 22.2663 | 22.0698 | 21.3783 | 20.1876 | 22.1942 | 22.3738 | 22.4064 | 22.347 | 21.977 | 21.2 | 22.2657 | 42.6029 | 26.2176 | 32.5418 | 23.8396 | 21.2924 | 21.4504 | 18.6003 | 22.39 | 22.1512 | 21.6954 | 22.0881 | 21.7966 | 21.2913 | 21.9414 | 21.5225 | 20.9402 | 24.5774 | 80.5058 | 51.1319 | 37.4501 | 0.32165 | 0.015818 | 33.3695 | 22.0592 | 22.3497 | 20.1651 | 21.6512 | 22.084 | 21.9375 | 21.6974 | 21.7692 | 21.7698 | 21.4305 | 21.1407 | 72.3356 | 90.9088 | 52.806 | 53.6583 | 32.6101 |  | 24.2425 | 53.1662 | 25.6598 | 36.8876 | 24.7511 | 30.6714 |  | 30.9091 |  |  | 20.8518 | 21.3739 | 30.4947 | [5 empty] | 21.8917 | 27.959 | 21.6436 | 22.008 | 24.4045 | 21.1366 | 21.7553 | 21.0726 | 31.5063 | 102.0674 |  | 25.4266 | 64.834 | 19.5144 | 27.0088 | 70.457 | 24.667 | 52.8 | 20.3372 | 48.3285 | 20.39 | 50.26 | 18.7808 | 26.7724 | 62.3076 | 21.5319 | 28.0876 | 87.4412 | 19.681 | 26.7981 | 72.0018 | 19.7048 | 46.062 | 21.8751 | 48.9142 | 20.2646 | 49.8517 | 0.13528 | 20.3595 | 0.43586 | 0.014658 | -27.1243 | 3.0956 | 42.82 | 51.06 | 1.1617 | -0.72087 | -7.7983 | 0.92953 | 0.62687 | -16.7393 | 4.2319 | 0.21107 | -0.31204 | 0.10943 | -1.9232 | -1.1383 | 0.0071383 | 0.087936
42838.4217 | 124 | 22.9065 | 22.8677 | 22.859 | 22.7691 | 22.4048 | 21.7318 | 22.7171 | 21.7882 | 22.3643 | 22.3651 | 22.3429 | 22.0031 | 21.2114 | 22.1786 | 21.6063 | 21.7796 | 21.9041 | 21.0841 | 21.1852 | 21.4027 | 20.48 | 20.624 | 20.9458 | 21.8761 | 21.6326 | 21.5381 | 80.2027 | 71.3084 | 89.3198 | 22.0861 | 21.6792 | 21.3328 | 21.9988 | 21.7404 | 21.5603 | 24.7226 | 79.8586 |  | 36.1185 | 60.021 | 66.7676 | 40.5107 |  | 16.9865 | 17.0534 | 16.6529 | 16.9792 | 17.1831 | 18.5292 | 37.8348 | 15.6094 | 17.0349 | 15.8357 | 17.2594 | 18.0725 | 45.0534 | 47.4905 | 44.0573 | 21.517 |  |  | 0.74737 | -0.21823 | -42.3959 | 0.53682 | 0.3208 | -197.8532 | 12.9875 | 0.73232 | 0.16064 | 0.083612 | 0.13813 | 0.0003072 | 8.881 | 1.9351 | 21.7937 | 22.009 | 22.1948 | 22.2471 | 22.0663 | 21.3681 | 20.1836 | 22.1823 | 22.3599 | 22.3905 | 22.3363 | 21.9632 | 21.1828 | 22.2632 | 42.242 | 26.2435 | 31.0568 | 23.92 | 21.2203 | 21.5598 | 18.6547 | 22.3904 | 22.1516 | 21.6993 | 22.0848 | 21.8032 | 21.2957 | 21.9441 | 21.5261 | 20.9439 | 24.646 | 80.7584 | 51.4066 | 37.4944 | 0.19091 | -0.18085 | 33.7388 | 22.061 | 22.3546 | 20.1724 | 21.6539 | 22.0827 | 21.9406 | 21.6959 | 21.781 | 21.7642 | 21.4344 | 21.1485 | 72.677 | 91.1126 | 53.0236 | 53.8692 | 32.5375 |  | 24.319 | 53.4966 | 25.7636 | 36.7405 | 24.8321 | 30.7576 |  | 31.0254 |  |  | 20.8508 | 21.3923 | 30.5547 | [5 empty] | 21.893 | 27.995 | 21.6403 | 22.0113 | 24.4092 | 21.1394 | 21.7548 | 21.0735 | 31.6529 | 102.2545 |  | 25.5161 | 65.1165 | 19.5295 | 27.1316 | 70.7112 | 24.6943 | 53.0903 | 20.3586 | 48.4923 | 20.4088 | 50.4917 | 18.7768 | 26.8533 | 62.4813 | 21.5562 | 28.2197 | 87.5867 | 19.6877 | 26.9096 | 72.341 | 19.7191 | 46.3065 | 21.9099 | 49.1945 | 20.284 | 50.116 | 0.29611 | 20.3547 | 0.44064 | 0.015108 | -27.017 | 3.0955 | 59.43 | 52.46 | 1.147 | -0.55459 | -7.73 | 0.86982 | 0.67412 | -16.7414 | 4.2893 | 0.21567 | -0.31771 | 0.11625 | -1.8703 | -0.9669 | 0.0078205 | 0.089022
42838.4217 | 125 | 22.9119 | 22.8672 | 22.8567 | 22.7722 | 22.3969 | 21.7315 | 22.717 | 21.7832 | 22.3664 | 22.367 | 22.3378 | 22.0054 | 21.2095 | 22.1774 | 21.6025 | 21.7828 | 21.8978 | 21.083 | 21.1884 | 21.4026 | 20.4775 | 20.6225 | 20.9472 | 21.8701 | 21.6362 | 21.5389 | 80.5746 | 71.5664 | 89.6815 | 22.0849 | 21.6855 | 21.3379 | 22.0058 | 21.7361 | 21.5591 | 24.7852 | 79.8792 |  | 36.2602 | 60.2471 | 67.0362 | 41.2283 |  | 16.9853 | 17.0564 | 16.6577 | 16.9882 | 17.1781 | 18.5409 | 37.7826 | 15.6461 | 17.0362 | 15.9061 | 17.2738 | 18.072 | 45.0401 | 47.4561 | 44.0535 | 21.5155 |  |  | 0.7132 | -0.053293 | -41.9333 | 0.75564 | 0.20712 | -197.8545 | 13.1478 | 0.57987 | 0.068398 | 0.13606 | 0.060878 | 0.00027763 | 8.8809 | 1.9359 | 21.7931 | 22.0072 | 22.1952 | 22.2575 | 22.0643 | 21.3714 | 20.1728 | 22.1835 | 22.3641 | 22.3945 | 22.3441 | 21.9624 | 21.1846 | 22.2567 | 41.3173 | 26.5196 | 30.4262 | 24.0092 | 21.3961 | 21.6664 | 18.726 | 22.3909 | 22.1454 | 21.7003 | 22.0877 | 21.7928 | 21.2965 | 21.9464 | 21.5196 | 20.9524 | 24.7104 | 81.4146 | 51.6499 | 37.2952 | 0.077473 | -0.24723 | 33.7892 | 22.0556 | 22.3463 | 20.1681 | 21.6458 | 22.0854 | 21.9293 | 21.6971 | 21.7881 | 21.7655 | 21.4279 | 21.1527 | 72.9557 | 91.2677 | 53.2392 | 54.0756 | 32.7789 |  | 24.4083 | 53.8249 | 25.8523 | 36.8355 | 24.9042 | 31.0985 |  | 31.1468 |  |  | 20.8572 | 21.4069 | 30.6473 | [5 empty] | 21.8984 | 28.1133 | 21.6399 | 22.0138 | 24.4234 | 21.1349 | 21.7487 | 21.0848 | 31.7579 | 102.5703 |  | 25.5891 | 65.3731 | 19.5381 | 27.2767 | 71.0658 | 24.7318 | 53.2978 | 20.3753 | 48.6813 | 20.4285 | 50.7356 | 18.7693 | 26.9779 | 62.6275 | 21.5749 | 28.3607 | 87.8743 | 19.6984 | 27.0034 | 72.6981 | 19.7251 | 46.6062 | 21.9318 | 49.4685 | 20.2985 | 50.4018 | 0.2668 | 20.3506 | 0.44406 | 0.016153 | -27.0666 | 3.0956 | 53.09 | 51.51 | 1.1211 | -0.27407 | -7.6878 | 1.032 | 0.54168 | -16.7418 | 4.3157 | 0.21198 | -0.32383 | 0.11605 | -1.7551 | -0.88852 | -0.0099975 | 0.096731
42838.4217 | 126 | 22.9128 | 22.8701 | 22.8599 | 22.7812 | 22.3952 | 21.7306 | 22.7255 | 21.7833 | 22.3653 | 22.3698 | 22.3378 | 21.9963 | 21.2143 | 22.175 | 21.6056 | 21.7794 | 21.8953 | 21.0878 | 21.1836 | 21.4023 | 20.4732 | 20.6188 | 20.9449 | 21.8684 | 21.6331 | 21.5391 | 80.8952 | 71.827 | 89.7786 | 22.0853 | 21.6876 | 21.3413 | 21.9982 | 21.7254 | 21.568 | 24.8623 | 79.8668 |  | 36.4066 | 60.5003 | 67.2478 | 41.7139 |  | 16.9832 | 17.0564 | 16.6533 | 16.9742 | 17.1722 | 18.518 | 37.5883 | 15.6238 | 17.0335 | 15.9379 | 17.2751 | 18.0745 | 45.0229 | 47.4213 | 44.0542 | 21.5226 |  |  | 0.83543 | -0.22283 | -41.5069 | 0.55916 | 0.27415 | -197.8795 | 12.9796 | 0.26314 | 0.15247 | 0.08508 | 0.11001 | 0.00026613 | 8.8811 | 1.9422 | 21.7844 | 22.003 | 22.1944 | 22.2506 | 22.0595 | 21.3638 | 20.1695 | 22.1829 | 22.3575 | 22.3934 | 22.3355 | 21.9547 | 21.1851 | 22.2553 | 40.5395 | 25.9924 | 29.5678 | 23.6255 | 21.2697 | 21.753 | 18.7767 | 22.3835 | 22.1386 | 21.6944 | 22.0735 | 21.7809 | 21.2833 | 21.9265 | 21.5147 | 20.9377 | 24.7715 | 81.8255 | 51.952 | 37.2579 | 0.060762 | -0.092596 | 33.7065 | 22.0569 | 22.3561 | 20.1667 | 21.6425 | 22.0938 | 21.9302 | 21.702 | 21.8056 | 21.7685 | 21.4283 | 21.1595 | 73.1328 | 91.5668 | 53.4404 | 54.2927 | 33.3044 |  | 24.4834 | 54.2454 | 25.9138 | 37.0156 | 24.9573 | 31.6125 |  | 31.2671 |  |  | 20.8582 | 21.4216 | 30.817 | [5 empty] | 21.9006 | 28.2339 | 21.6421 | 22.0194 | 24.4513 | 21.1406 | 21.7505 | 21.0924 | 31.8102 | 102.634 |  | 25.6311 | 65.5722 | 19.5441 | 27.3876 | 71.4243 | 24.7758 | 53.5714 | 20.3864 | 48.896 | 20.4325 | 50.9733 | 18.7517 | 27.1767 | 62.8599 | 21.5845 | 28.4765 | 88.3257 | 19.7027 | 27.1157 | 72.9667 | 19.7229 | 46.8589 | 21.9462 | 49.7142 | 20.3104 | 50.6958 | 0.15791 | 20.3423 | 0.44995 | 0.016458 | -26.978 | 3.0956 | 42.29 | 52.26 | 1.2135 | -0.56041 | -7.6486 | 0.88775 | 0.62317 | -16.7422 | 4.2879 | 0.19992 | -0.33342 | 0.11284 | -1.6585 | -0.78722 | -0.020882 | 0.099828
42838.4217 | 127 | 22.91 | 22.8831 | 22.8598 | 22.778 | 22.4002 | 21.7303 | 22.7265 | 21.7955 | 22.3683 | 22.3747 | 22.3491 | 22.0014 | 21.2132 | 22.1849 | 21.6052 | 21.7722 | 21.9052 | 21.0796 | 21.1837 | 21.397 | 20.4729 | 20.6191 | 20.9508 | 21.8718 | 21.6268 | 21.5462 | 81.0488 | 72.1516 | 89.6102 | 22.0958 | 21.6893 | 21.3493 | 22.0103 | 21.7354 | 21.5797 | 24.941 | 79.9181 |  | 36.5873 | 60.719 | 67.5065 | 41.9675 |  | 16.981 | 17.0558 | 16.6487 | 16.9571 | 17.1617 | 18.5071 | 37.2824 | 15.5977 | 17.0279 | 15.9476 | 17.2637 | 18.062 | 45.0058 | 47.3987 | 44.0468 | 21.5172 |  |  | 0.58769 | -0.1834 | -40.6631 | 0.58545 | 0.092784 | -197.8269 | 13.4948 | 0.65544 | 0.01644 | 0.23005 | 0.16261 | 0.00030063 | 8.881 | 1.944 | 21.7854 | 22.0023 | 22.1886 | 22.2462 | 22.0651 | 21.3641 | 20.1745 | 22.1812 | 22.3555 | 22.3887 | 22.3356 | 21.9549 | 21.1832 | 22.2545 | 39.5658 | 25.1647 | 28.5637 | 23.0549 | 21.1327 | 21.833 | 18.8135 | 22.3882 | 22.1478 | 21.701 | 22.0865 | 21.7896 | 21.2951 | 21.9373 | 21.5228 | 20.9487 | 24.8463 | 82.0311 | 52.2912 | 37.0806 | 0.174 | -0.14452 | 33.8548 | 22.06 | 22.3602 | 20.1664 | 21.647 | 22.0885 | 21.938 | 21.703 | 21.8257 | 21.7637 | 21.4315 | 21.1574 | 73.3114 | 91.9501 | 53.6271 | 54.5219 | 33.4792 |  | 24.5756 | 54.5427 | 25.9999 | 37.1535 | 25.0423 | 31.9968 |  | 31.4077 |  |  | 20.8656 | 21.4248 | 30.7294 | [5 empty] | 21.901 | 28.3179 | 21.6422 | 22.0261 | 24.4671 | 21.1399 | 21.7555 | 21.1065 | 31.944 | 102.701 |  | 25.698 | 65.7729 | 19.5573 | 27.4768 | 71.7313 | 24.8244 | 53.8523 | 20.4084 | 49.1819 | 20.4476 | 51.12 | 18.7358 | 27.3362 | 63.1341 | 21.6011 | 28.5438 | 88.67 | 19.7065 | 27.2347 | 73.1599 | 19.7298 | 47.1352 | 21.968 | 49.8512 | 20.3238 | 50.993 | 0.14808 | 20.3311 | 0.45479 | 0.017068 | -27.0543 | 3.0956 | 34 | 51.33 | 1.0175 | -0.50842 | -7.5704 | 0.90837 | 0.36253 | -16.7396 | 4.3721 | 0.19818 | -0.33877 | 0.11188 | -1.541 | -0.67135 | -0.025267 | 0.10728
42838.4218 | 128 | 22.9085 | 22.8733 | 22.8519 | 22.7803 | 22.3985 | 21.7224 | 22.7175 | 21.783 | 22.3602 | 22.3637 | 22.3352 | 22.0008 | 21.2069 | 22.1745 | 21.5969 | 21.7749 | 21.8952 | 21.0808 | 21.1809 | 21.3898 | 20.4665 | 20.6112 | 20.9462 | 21.8752 | 21.6237 | 21.5528 | 81.262 | 72.4652 | 90.0603 | 22.0856 | 21.6816 | 21.3479 | 22.004 | 21.7293 | 21.5807 | 25.0108 | 79.8735 |  | 36.7349 | 60.9933 | 67.7935 | 41.6406 |  | 16.9831 | 17.056 | 16.6489 | 16.9656 | 17.1448 | 18.4945 | 37.1075 | 15.6116 | 17.0291 | 15.9726 | 17.2675 | 18.0652 | 44.9813 | 47.3719 | 44.0423 | 21.5199 |  |  | 0.66129 | -0.24057 | -40.3911 | 0.46059 | 0.038244 | -197.8197 | 13.5316 | 0.77044 | -0.066265 | 0.19837 | 0.15063 | 0.00030227 | 8.8811 | 1.9431 | 21.7871 | 21.996 | 22.1911 | 22.2483 | 22.0637 | 21.3619 | 20.1725 | 22.1772 | 22.3588 | 22.3833 | 22.3341 | 21.9542 | 21.1828 | 22.2507 | 38.8553 | 25.4293 | 27.651 | 22.6547 | 20.901 | 21.9234 | 18.8532 | 22.3978 | 22.1542 | 21.7023 | 22.0915 | 21.7979 | 21.2951 | 21.9415 | 21.5209 | 20.9573 | 24.9214 | 82.3392 | 52.5881 | 37.1266 | 0.20841 | -0.13634 | 33.9217 | 22.0539 | 22.3577 | 20.169 | 21.6423 | 22.0832 | 21.9351 | 21.6957 | 21.8329 | 21.7588 | 21.4284 | 21.1559 | 73.5508 | 92.3987 | 53.8144 | 54.7336 | 33.7 |  | 24.6618 | 54.8 | 26.098 | 37.2014 | 25.1195 | 31.8348 |  | 31.5364 |  |  | 20.8597 | 21.4367 | 30.6888 | [5 empty] | 21.9015 | 28.3898 | 21.6375 | 22.0192 | 24.4833 | 21.1462 | 21.7506 | 21.1084 | 32.1596 | 103.0228 |  | 25.7928 | 65.9701 | 19.5718 | 27.5459 | 71.9312 | 24.8568 | 54.1242 | 20.4309 | 49.5306 | 20.4587 | 51.2408 | 18.736 | 27.4083 | 63.3922 | 21.6226 | 28.6292 | 88.8901 | 19.7199 | 27.3674 | 73.4705 | 19.7371 | 47.4375 | 21.999 | 49.9963 | 20.3348 | 51.2452 | 0.16107 | 20.3253 | 0.46021 | 0.016691 | -27.0079 | 3.0956 | 23.22 | 51.52 | 1.08 | -0.58229 | -7.5451 | 0.80571 | 0.23274 | -16.739 | 4.3779 | 0.19496 | -0.34259 | 0.11316 | -1.4515 | -0.56531 | -0.013829 | 0.10854
42838.4218 | 129 | 22.9058 | 22.8746 | 22.8536 | 22.7719 | 22.3978 | 21.732 | 22.7094 | 21.7899 | 22.361 | 22.3612 | 22.3408 | 22.0035 | 21.2086 | 22.178 | 21.6023 | 21.7714 | 21.9046 | 21.0887 | 21.1843 | 21.3907 | 20.4691 | 20.6177 | 20.9503 | 21.8674 | 21.627 | 21.5643 | 81.4605 | 72.7537 | 90.2537 | 22.0831 | 21.6807 | 21.3597 | 21.9974 | 21.7389 | 21.5869 | 25.0717 | 80.2209 |  | 36.8817 | 61.279 | 68.1197 | 41.3933 |  | 16.9767 | 17.059 | 16.6513 | 16.9649 | 17.1424 | 18.4704 | 36.9823 | 15.602 | 17.0427 | 15.9742 | 17.2748 | 18.0652 | 44.9665 | 47.3464 | 44.0254 | 21.5251 |  |  | 0.79074 | -0.50604 | -40.0566 | 0.59859 | 0.23538 | -197.8374 | 13.5276 | 0.64493 | 0.034538 | 0.16438 | 0.072335 | 0.00027106 | 8.881 | 1.9441 | 21.792 | 21.9937 | 22.194 | 22.2437 | 22.0587 | 21.3558 | 20.1781 | 22.1849 | 22.358 | 22.385 | 22.3329 | 21.9648 | 21.1911 | 22.2533 | 38.3317 | 25.4956 | 27.8126 | 22.4656 | 20.8339 | 22.0059 | 18.8958 | 22.3913 | 22.1438 | 21.6996 | 22.0787 | 21.7909 | 21.2935 | 21.9363 | 21.5171 | 20.952 | 25.001 | 82.4371 | 52.8005 | 37.3705 | 0.32755 | -0.11694 | 33.8926 | 22.0548 | 22.3536 | 20.1631 | 21.6352 | 22.0853 | 21.9322 | 21.696 | 21.8432 | 21.7655 | 21.4314 | 21.16 | 73.7714 | 92.9074 | 54.0047 | 54.955 | 33.4609 |  | 24.7222 | 54.7785 | 26.1713 | 37.258 | 25.1879 | 31.6945 |  | 31.6393 |  |  | 20.8571 | 21.4542 | 30.8609 | [5 empty] | 21.8982 | 28.464 | 21.64 | 22.0114 | 24.5119 | 21.1388 | 21.756 | 21.1301 | 32.3639 | 103.1822 |  | 26.0057 | 66.1735 | 19.5881 | 27.6052 | 71.964 | 24.9052 | 54.4383 | 20.4584 | 49.8132 | 20.4833 | 51.3872 | 18.7296 | 27.449 | 63.7057 | 21.6409 | 28.7316 | 89.1687 | 19.7228 | 27.4894 | 73.7824 | 19.7421 | 47.7392 | 22.0211 | 50.491 | 20.3422 | 51.5661 | 0.25029 | 20.3188 | 0.46519 | 0.016531 | -27.0066 | 3.0956 | 25.87 | 52.28 | 1.1814 | -0.84453 | -7.5138 | 0.91852 | 0.57738 | -16.739 | 4.3771 | 0.20364 | -0.33952 | 0.1139 | -1.3837 | -0.57829 | -0.0049021 | 0.10445
42838.4218 | 130 | 22.9085 | 22.8787 | 22.8625 | 22.7814 | 22.4032 | 21.736 | 22.7246 | 21.7909 | 22.3709 | 22.376 | 22.3464 | 22.0032 | 21.213 | 22.1833 | 21.6018 | 21.7785 | 21.9007 | 21.0799 | 21.1806 | 21.395 | 20.4738 | 20.6179 | 20.9491 | 21.8701 | 21.6251 | 21.5831 | 81.6072 | 73.0338 | 90.3805 | 22.0831 | 21.6766 | 21.3636 | 21.996 | 21.7378 | 21.5953 | 25.1458 | 80.5384 |  | 37.012 | 61.5559 | 68.476 | 41.8204 |  | 16.9719 | 17.05 | 16.6384 | 16.9554 | 17.1319 | 18.4442 | 36.901 | 15.5532 | 17.0369 | 15.9449 | 17.2793 | 18.0687 | 44.9568 | 47.321 | 44.0219 | 21.5238 |  |  | 0.81374 | -0.27474 | -39.6945 | 0.45665 | 0.24524 | -197.7914 | 13.592 | 0.55096 | 0.061976 | 0.00137 | 0.093514 | 0.00027435 | 8.8809 | 1.9416 | 21.7862 | 21.9996 | 22.1909 | 22.2378 | 22.0592 | 21.3557 | 20.1681 | 22.1841 | 22.3579 | 22.392 | 22.3246 | 21.957 | 21.1901 | 22.2576 | 37.934 | 24.7512 | 27.6644 | 22.2525 | 20.7316 | 22.0927 | 18.9443 | 22.385 | 22.1372 | 21.6931 | 22.0773 | 21.7937 | 21.2885 | 21.9329 | 21.5182 | 20.9481 | 25.0645 | 82.6367 | 53.0141 | 37.2642 | -0.052087 | -0.10515 | 33.9938 | 22.0561 | 22.3521 | 20.1656 | 21.6433 | 22.0843 | 21.9367 | 21.7 | 21.8627 | 21.7658 | 21.4306 | 21.1702 | 73.9689 | 93.2448 | 54.2171 | 55.1782 | 33.2214 |  | 24.7878 | 55.1956 | 26.2499 | 37.5339 | 25.2516 | 31.8707 |  | 31.7433 |  |  | 20.8601 | 21.4595 | 30.9995 | [5 empty] | 21.8872 | 28.5005 | 21.641 | 22.0113 | 24.5438 | 21.1318 | 21.7524 | 21.1322 | 32.5138 | 103.7965 |  | 26.2049 | 66.3768 | 19.5761 | 27.7402 | 72.0527 | 24.9056 | 54.7252 | 20.457 | 50.0307 | 20.4749 | 51.5883 | 18.7309 | 27.6098 | 64.0221 | 21.6503 | 28.845 | 89.6223 | 19.7341 | 27.6021 | 74.0107 | 19.7732 | 47.9921 | 22.0483 | 51.0266 | 20.373 | 51.8306 | 0.062566 | 20.3103 | 0.47024 | 0.0173 | -27.047 | 3.0957 | 34.7 | 51.69 | 1.1986 | -0.62227 | -7.4796 | 0.80225 | 0.58932 | -16.7363 | 4.3873 | 0.2125 | -0.34844 | 0.10839 | -1.3293 | -0.55615 | -0.014262 | 0.10955
42838.4218 | 131 | 22.904 | 22.8706 | 22.8598 | 22.7843 | 22.394 | 21.7313 | 22.7208 | 21.782 | 22.3683 | 22.3673 | 22.342 | 22.0002 | 21.2077 | 22.183 | 21.6063 | 21.7816 | 21.8982 | 21.0834 | 21.1746 | 21.392 | 20.4721 | 20.6199 | 20.9561 | 21.8632 | 21.6238 | 21.5839 | 81.9592 | 73.2923 | 90.2235 | 22.0869 | 21.6796 | 21.3618 | 22.0029 | 21.7293 | 21.5987 | 25.2389 | 80.9262 |  | 37.1568 | 61.7698 | 68.7997 | 42.327 |  | 16.9799 | 17.0544 | 16.639 | 16.9626 | 17.1369 | 18.4398 | 36.7175 | 15.5491 | 17.0438 | 15.9266 | 17.2849 | 18.0722 | 44.9491 | 47.3001 | 44.0213 | 21.5255 |  |  | 0.66852 | -0.2708 | -39.3752 | 0.66101 | 0.1309 | -197.8098 | 13.5999 | 0.56016 | 0.40233 | 0.20655 | 0.2376 | 0.0002957 | 8.881 | 1.9351 | 21.789 | 21.9959 | 22.1897 | 22.2505 | 22.057 | 21.3627 | 20.1786 | 22.1742 | 22.3594 | 22.3885 | 22.3235 | 21.9573 | 21.1876 | 22.2505 | 36.7679 | 23.4908 | 26.5651 | 22.0845 | 20.5896 | 22.1519 | 18.9808 | 22.3886 | 22.1544 | 21.7031 | 22.0812 | 21.795 | 21.2961 | 21.9399 | 21.5213 | 20.9602 | 25.145 | 82.7129 | 53.2391 | 37.485 | 0.073541 | 0.080486 | 34.0667 | 22.0496 | 22.3494 | 20.1609 | 21.6409 | 22.0862 | 21.9343 | 21.6949 | 21.8774 | 21.7649 | 21.4242 | 21.1805 | 74.1742 | 93.4037 | 54.4615 | 55.4094 | 33.2017 |  | 24.8545 | 55.3338 | 26.3507 | 38.043 | 25.3329 | 32.2355 |  | 31.8534 |  |  | 20.8561 | 21.4598 | 31.0965 | [5 empty] | 21.8974 | 28.4641 | 21.6418 | 22.018 | 24.589 | 21.1358 | 21.7499 | 21.141 | 32.6203 | 103.8682 |  | 26.3317 | 66.5639 | 19.5899 | 27.9259 | 72.2869 | 24.944 | 55.0614 | 20.4721 | 50.3186 | 20.4972 | 51.8408 | 18.7282 | 27.722 | 64.2465 | 21.6765 | 28.9216 | 89.9605 | 19.7305 | 27.7124 | 74.2133 | 19.776 | 48.2777 | 22.057 | 51.3419 | 20.3832 | 52.074 | 0.15847 | 20.304 | 0.47501 | 0.017112 | -27.0206 | 3.0956 | 15.62 | 52.33 | 1.0862 | -0.61779 | -7.4496 | 0.96522 | 0.43054 | -16.737 | 4.3886 | 0.21531 | -0.34887 | 0.096993 | -1.1928 | -0.42976 | -0.025185 | 0.10614
42838.4218 | 132 | 22.9086 | 22.8717 | 22.8638 | 22.7816 | 22.3966 | 21.7321 | 22.722 | 21.788 | 22.3652 | 22.3674 | 22.3397 | 22.0041 | 21.2108 | 22.19 | 21.6077 | 21.7789 | 21.9075 | 21.0872 | 21.1879 | 21.3952 | 20.4721 | 20.6212 | 20.9588 | 21.8731 | 21.6316 | 21.5981 | 82.395 | 73.5593 | 91.0653 | 22.0867 | 21.6824 | 21.3717 | 22.0007 | 21.7278 | 21.6079 | 25.3176 | 81.5788 |  | 37.2979 | 61.9472 | 69.0688 | 42.2604 |  | 16.9867 | 17.066 | 16.6414 | 16.9631 | 17.1359 | 18.4214 | 36.8431 | 15.5626 | 17.05 | 15.8766 | 17.2957 | 18.0774 | 44.9362 | 47.2824 | 44.0191 | 21.5275 |  |  | 0.88077 | -0.38974 | -39.0184 | 0.77273 | 0.10987 | -197.8683 | 13.6256 | 0.6009 | 0.070344 | 0.16648 | 0.28378 | 0.00029735 | 8.8808 | 1.9316 | 21.7845 | 22.001 | 22.1894 | 22.2425 | 22.063 | 21.3601 | 20.1754 | 22.1771 | 22.3608 | 22.39 | 22.3381 | 21.952 | 21.185 | 22.2483 | 35.5386 | 22.8527 | 25.2437 | 21.7827 | 20.5234 | 22.2044 | 18.9985 | 22.4 | 22.1531 | 21.7079 | 22.0874 | 21.7948 | 21.2969 | 21.9464 | 21.5253 | 20.9654 | 25.2216 | 82.7379 | 53.4233 | 37.7759 | 0.23239 | -0.069392 | 34.2177 | 22.0499 | 22.3511 | 20.1617 | 21.6509 | 22.0827 | 21.9289 | 21.6893 | 21.8843 | 21.7651 | 21.4322 | 21.1761 | 74.456 | 93.6375 | 54.6984 | 55.6496 | 33.4296 |  | 24.9255 | 55.0736 | 26.4456 | 38.2476 | 25.4005 | 32.056 |  | 31.9582 |  |  | 20.8629 | 21.454 | 31.0657 | [5 empty] | 21.8992 | 28.5117 | 21.6367 | 22.0159 | 24.63 | 21.1365 | 21.7619 | 21.1651 | 32.6962 | 104.2494 |  | 26.413 | 66.8058 | 19.6068 | 28.0412 | 72.4804 | 24.9847 | 55.2315 | 20.4966 | 50.583 | 20.5093 | 52.1507 | 18.7223 | 27.7687 | 64.4664 | 21.6827 | 29.0031 | 90.186 | 19.7301 | 27.8097 | 74.459 | 19.7978 | 48.477 | 22.0768 | 51.5253 | 20.3937 | 52.3443 | 0.20559 | 20.2973 | 0.47991 | 0.016175 | -27.0424 | 3.0956 | 26.11 | 51.79 | 1.2482 | -0.74116 | -7.4159 | 1.0436 | 0.39443 | -16.7389 | 4.3925 | 0.21137 | -0.33842 | 0.093593 | -1.0501 | -0.28087 | -0.020674 | 0.10065
42838.4218 | 133 | 22.9094 | 22.8791 | 22.8615 | 22.7762 | 22.4052 | 21.7364 | 22.7224 | 21.7858 | 22.3688 | 22.3715 | 22.3472 | 22.0031 | 21.2098 | 22.1767 | 21.5979 | 21.7712 | 21.9029 | 21.085 | 21.1836 | 21.3931 | 20.4664 | 20.6142 | 20.9485 | 21.8694 | 21.6267 | 21.5963 | 82.828 | 73.8287 | 91.3124 | 22.0925 | 21.6928 | 21.3789 | 22.0028 | 21.7385 | 21.6162 | 25.3978 | 81.7357 |  | 37.4506 | 62.1433 | 69.3166 | 42.1309 |  | 16.9859 | 17.0523 | 16.6409 | 16.9607 | 17.1301 | 18.3991 | 37.0346 | 15.5778 | 17.05 | 15.8048 | 17.3079 | 18.0743 | 44.9182 | 47.2582 | 44.0093 | 21.5217 |  |  | 0.72043 | -0.32271 | -38.4736 | 0.51119 | 0.1355 | -197.8552 | 13.8779 | 0.72444 | 0.12289 | 0.15956 | 0.17406 | 0.00032199 | 8.8811 | 1.9357 | 21.791 | 22.0028 | 22.1942 | 22.2499 | 22.0582 | 21.3641 | 20.1735 | 22.1824 | 22.3615 | 22.3905 | 22.3402 | 21.9577 | 21.188 | 22.2554 | 35.7217 | 22.4562 | 24.8958 | 21.4249 | 20.1947 | 22.272 | 19.0264 | 22.3954 | 22.1487 | 21.7061 | 22.0869 | 21.7959 | 21.295 | 21.9422 | 21.5276 | 20.9677 | 25.2907 | 82.8954 | 53.6134 | 37.883 | 0.30946 | -0.040482 | 34.3835 | 22.0494 | 22.3425 | 20.1674 | 21.6395 | 22.0821 | 21.9244 | 21.6922 | 21.8967 | 21.7634 | 21.4305 | 21.1751 | 74.6982 | 93.8803 | 54.9274 | 55.8417 | 33.6628 |  | 24.9732 | 55.8546 | 26.5421 | 38.3764 | 25.4653 | 31.98 |  | 32.0531 |  |  | 20.8651 | 21.4543 | 31.1768 | [5 empty] | 21.9099 | 28.579 | 21.65 | 22.0229 | 24.6732 | 21.1531 | 21.7609 | 21.1799 | 32.789 | 104.1978 |  | 26.4653 | 67.1082 | 19.6215 | 28.0735 | 72.7303 | 25.0376 | 55.3949 | 20.5196 | 50.8273 | 20.5232 | 52.4979 | 18.7222 | 27.833 | 64.7282 | 21.6997 | 29.1592 | 90.7645 | 19.7316 | 27.9173 | 74.7816 | 19.8017 | 48.6933 | 22.0811 | 51.7177 | 20.4132 | 52.5604 | 0.1414 | 20.2892 | 0.48498 | 0.016291 | -27.096 | 3.0957 | 33.7 | 51.14 | 1.1292 | -0.67441 | -7.3637 | 0.84881 | 0.43801 | -16.7377 | 4.4329 | 0.20651 | -0.35685 | 0.092208 | -1.0625 | -0.23895 | -0.014368 | 0.10001
42838.4218 | 134 | 22.9123 | 22.8749 | 22.8649 | 22.7788 | 22.4051 | 21.729 | 22.7141 | 21.7868 | 22.3664 | 22.369 | 22.3483 | 22.0057 | 21.2171 | 22.1813 | 21.5996 | 21.7746 | 21.906 | 21.0877 | 21.1805 | 21.3936 | 20.4726 | 20.6175 | 20.9584 | 21.8658 | 21.6282 | 21.6111 | 83.0953 | 74.1394 | 91.1224 | 22.0973 | 21.6826 | 21.385 | 21.9994 | 21.7393 | 21.6169 | 25.4744 | 81.9159 |  | 37.6276 | 62.348 | 69.5801 | 41.9371 |  | 16.9812 | 17.0458 | 16.6421 | 16.9629 | 17.1366 | 18.3764 | 37.0402 | 15.5684 | 17.0507 | 15.7451 | 17.3069 | 18.072 | 44.9112 | 47.2403 | 43.9873 | 21.5208 |  |  | 0.73883 | -0.079577 | -37.9801 | 0.66561 | 0.22421 | -197.8 | 14.1145 | 0.65873 | 0.14527 | 0.034518 | 0.041434 | 0.0002727 | 8.881 | 1.9342 | 21.7894 | 21.9982 | 22.196 | 22.2535 | 22.058 | 21.3668 | 20.177 | 22.1839 | 22.3622 | 22.394 | 22.3411 | 21.9663 | 21.1869 | 22.2596 | 36.4538 | 22.3103 | 24.1783 | 21.3195 | 20.071 | 22.3683 | 19.0423 | 22.3942 | 22.1459 | 21.7032 | 22.0869 | 21.7934 | 21.2947 | 21.9348 | 21.5223 | 20.9699 | 25.377 | 83.2059 | 53.8037 | 37.8825 | 0.45003 | 0.051005 | 34.5075 | 22.0491 | 22.3412 | 20.1605 | 21.6342 | 22.0813 | 21.9244 | 21.6927 | 21.9151 | 21.7682 | 21.4279 | 21.1835 | 74.9259 | 94.1184 | 55.1529 | 56.0507 | 33.6909 |  | 25.0493 | 56.21 | 26.6597 | 38.4664 | 25.5512 | 31.9441 |  | 32.1821 |  |  | 20.8625 | 21.4483 | 31.378 | [5 empty] | 21.8971 | 28.6842 | 21.6462 | 22.0196 | 24.697 | 21.1486 | 21.7604 | 21.1967 | 32.9471 | 104.2417 |  | 26.532 | 67.3661 | 19.6277 | 28.0926 | 72.9871 | 25.074 | 55.6205 | 20.5418 | 51.0431 | 20.536 | 52.7981 | 18.7191 | 27.9269 | 65.023 | 21.721 | 29.3167 | 91.1546 | 19.74 | 27.9988 | 75.0225 | 19.8286 | 48.9085 | 22.107 | 51.9386 | 20.4308 | 52.7944 | 0.088722 | 20.2823 | 0.49048 | 0.017235 | -27.1063 | 3.0956 | 44.09 | 52.38 | 1.1433 | -0.33489 | -7.3163 | 0.96855 | 0.56342 | -16.7347 | 4.4703 | 0.2083 | -0.36274 | 0.092612 | -1.1326 | -0.15737 | -0.0063942 | 0.10294
42838.4218 | 135 | 22.9027 | 22.872 | 22.8561 | 22.7796 | 22.4 | 21.7256 | 22.7231 | 21.7828 | 22.3631 | 22.3678 | 22.3385 | 21.9968 | 21.2161 | 22.1789 | 21.6016 | 21.77 | 21.9018 | 21.0836 | 21.1754 | 21.3923 | 20.4676 | 20.6171 | 20.9568 | 21.8617 | 21.6284 | 21.6179 | 83.2446 | 74.4682 | 91.4176 | 22.0885 | 21.6785 | 21.3853 | 21.9948 | 21.7369 | 21.6254 | 25.562 | 81.933 |  | 37.7828 | 62.6033 | 69.7788 | 42.4598 |  | 16.9724 | 17.0468 | 16.6284 | 16.9496 | 17.1379 | 18.3573 | 37.0125 | 15.5394 | 17.0437 | 15.7019 | 17.3118 | 18.0709 | 44.8971 | 47.2222 | 43.9762 | 21.5184 |  |  | 0.68757 | -0.13477 | -37.4393 | 0.53419 | 0.20975 | -197.8276 | 14.0487 | 0.52665 | 0.024224 | -0.011008 | 0.14785 | 0.0002727 | 8.881 | 1.9117 | 21.7799 | 21.9942 | 22.189 | 22.2421 | 22.052 | 21.3599 | 20.1761 | 22.1789 | 22.3572 | 22.3906 | 22.3435 | 21.9521 | 21.1862 | 22.2508 | 37.8033 | 23.316 | 24.284 | 21.0367 | 20.0441 | 22.4717 | 19.0606 | 22.3823 | 22.1373 | 21.6883 | 22.0856 | 21.7886 | 21.2849 | 21.9331 | 21.5172 | 20.9646 | 25.4606 | 83.5084 | 54.0256 | 37.4513 | 0.33404 | -0.044856 | 34.5301 | 22.0473 | 22.3466 | 20.1577 | 21.6425 | 22.0869 | 21.9243 | 21.6923 | 21.9413 | 21.7642 | 21.4334 | 21.189 | 75.2139 | 94.4083 | 55.3854 | 56.2662 | 33.7723 |  | 25.1211 | 56.075 | 26.7467 | 38.7618 | 25.6259 | 32.206 |  | 32.3031 |  |  | 20.8506 | 21.4602 | 31.3215 | [5 empty] | 21.8946 | 28.7651 | 21.6393 | 22.0245 | 24.7291 | 21.1362 | 21.7646 | 21.199 | 33.1295 | 104.4647 |  | 26.6216 | 67.6747 | 19.6347 | 28.1409 | 73.3112 | 25.112 | 55.8095 | 20.552 | 51.2164 | 20.5447 | 53.0162 | 18.7123 | 28.1059 | 65.3172 | 21.7312 | 29.4311 | 91.253 | 19.735 | 28.104 | 75.2737 | 19.85 | 49.0923 | 22.1297 | 52.2123 | 20.445 | 53.0206 | 0.1236 | 20.2794 | 0.49574 | 0.017961 | -27.1178 | 3.0957 | 34.79 | 51.62 | 1.1034 | -0.43583 | -7.264 | 0.86768 | 0.54494 | -16.7354 | 4.4597 | 0.20846 | -0.35604 | 0.086934 | -1.2705 | -0.16698 | -0.01795 | 0.11775
42838.4219 | 136 | 22.9095 | 22.8702 | 22.8625 | 22.7806 | 22.4061 | 21.7297 | 22.7211 | 21.7865 | 22.3619 | 22.3732 | 22.3459 | 21.997 | 21.2103 | 22.1839 | 21.6005 | 21.7683 | 21.8989 | 21.0844 | 21.1769 | 21.388 | 20.4742 | 20.6129 | 20.9577 | 21.8634 | 21.6243 | 21.6224 | 83.5143 | 74.7554 | 91.9562 | 22.087 | 21.677 | 21.3904 | 21.9933 | 21.7291 | 21.6311 | 25.6406 | 81.4942 |  | 37.9065 | 62.8218 | 69.9767 | 42.525 |  | 16.9709 | 17.0425 | 16.6271 | 16.947 | 17.1336 | 18.3467 | 37.0494 | 15.5241 | 17.0444 | 15.6847 | 17.3196 | 18.0776 | 44.8886 | 47.2131 | 43.9648 | 21.5297 |  |  | 0.71846 | -0.31285 | -36.9307 | 0.55588 | 0.10724 | -197.8125 | 14.1795 | 0.63376 | 0.083188 | 0.199 | 0.16486 | 0.00028092 | 8.8813 | 1.9111 | 21.7884 | 22.0003 | 22.1902 | 22.2495 | 22.0585 | 21.3585 | 20.1729 | 22.1924 | 22.3636 | 22.3897 | 22.3449 | 21.9559 | 21.1901 | 22.258 | 39.0211 | 23.9191 | 25.2021 | 20.7064 | 19.6879 | 22.5917 | 19.1048 | 22.3811 | 22.1444 | 21.6986 | 22.0823 | 21.7873 | 21.2896 | 21.9337 | 21.5162 | 20.9688 | 25.5375 | 83.8618 | 54.2811 | 37.5795 | 0.13704 | -0.08689 | 34.4722 | 22.045 | 22.3431 | 20.1604 | 21.6411 | 22.084 | 21.935 | 21.6939 | 21.9479 | 21.762 | 21.4347 | 21.1995 | 75.5749 | 94.6978 | 55.6082 | 56.5033 | 33.5691 |  | 25.1812 | 55.9322 | 26.8214 | 39.1338 | 25.7 | 32.2175 |  | 32.4236 |  |  | 20.8332 | 21.4786 | 31.1561 | [5 empty] | 21.8887 | 28.8636 | 21.6388 | 22.0159 | 24.7543 | 21.1341 | 21.7603 | 21.2071 | 33.2956 | 104.7014 |  | 26.7573 | 67.9579 | 19.6472 | 28.2666 | 73.6392 | 25.156 | 56.0608 | 20.5767 | 51.3668 | 20.5595 | 53.2373 | 18.7243 | 28.3445 | 65.5965 | 21.7522 | 29.5076 | 91.4118 | 19.7396 | 28.2236 | 75.5476 | 19.8644 | 49.2847 | 22.1592 | 52.5583 | 20.4635 | 53.2761 | 0.19093 | 20.271 | 0.50128 | 0.017881 | -27.1323 | 3.0956 | 42.06 | 52.69 | 1.1287 | -0.66402 | -7.2145 | 0.88512 | 0.38964 | -16.7344 | 4.4804 | 0.21614 | -0.34954 | 0.079109 | -1.3917 | -0.26383 | -0.017103 | 0.11679
42838.4219 | 137 | 22.9144 | 22.8747 | 22.8577 | 22.7816 | 22.4073 | 21.73 | 22.7187 | 21.7823 | 22.3596 | 22.3726 | 22.3465 | 22.0025 | 21.2118 | 22.1808 | 21.6051 | 21.7685 | 21.8992 | 21.0896 | 21.1789 | 21.3904 | 20.4756 | 20.6109 | 20.961 | 21.8685 | 21.6205 | 21.6308 | 83.7863 | 74.9887 | 92.3269 | 22.0879 | 21.677 | 21.3965 | 21.9962 | 21.7318 | 21.6412 | 25.7192 | 80.3435 |  | 38.0451 | 63.0627 | 70.1433 | 42.1481 |  | 16.971 | 17.0493 | 16.635 | 16.9417 | 17.1364 | 18.3347 | 36.9404 | 15.5255 | 17.0431 | 15.7072 | 17.3183 | 18.0818 | 44.8769 | 47.1991 | 43.9536 | 21.5302 |  |  | 0.89391 | -0.3168 | -36.2151 | 0.65379 | 0.21304 | -197.8526 | 14.2255 | 0.51285 | 0.1114 | 0.16585 | -0.062031 | 0.00028092 | 8.881 | 1.9087 | 21.7889 | 21.9987 | 22.1916 | 22.2434 | 22.0586 | 21.3637 | 20.1741 | 22.1812 | 22.3569 | 22.3917 | 22.3409 | 21.9592 | 21.1846 | 22.2571 | 38.9767 | 23.8979 | 26.162 | 20.7795 | 19.5407 | 22.6826 | 19.1383 | 22.3843 | 22.1466 | 21.7066 | 22.0873 | 21.7953 | 21.2933 | 21.9402 | 21.5214 | 20.981 | 25.6125 | 84.1089 | 54.5063 | 37.7722 | 0.31202 | -0.081945 | 34.4861 | 22.0483 | 22.3468 | 20.1614 | 21.6408 | 22.0754 | 21.9311 | 21.6981 | 21.9614 | 21.763 | 21.4286 | 21.1969 | 75.8808 | 94.8422 | 55.8356 | 56.7257 | 33.43 |  | 25.2457 | 55.5869 | 26.9036 | 39.5083 | 25.7857 | 32.5215 |  | 32.5633 |  |  | 20.8289 | 21.4963 | 31.0669 | [5 empty] | 21.8924 | 29.0166 | 21.6434 | 22.0127 | 24.7812 | 21.1441 | 21.7618 | 21.2189 | 33.4343 | 104.7121 |  | 26.87 | 68.175 | 19.6579 | 28.4165 | 73.886 | 25.191 | 56.3907 | 20.5944 | 51.5278 | 20.5686 | 53.4417 | 18.7266 | 28.5507 | 65.8259 | 21.7781 | 29.5609 | 91.6785 | 19.7465 | 28.3198 | 75.8755 | 19.8694 | 49.4871 | 22.1832 | 52.88 | 20.4827 | 53.5279 | 0.10356 | 20.2593 | 0.50693 | 0.018825 | -27.041 | 3.0956 | 37.58 | 51.79 | 1.2596 | -0.6682 | -7.1443 | 0.95992 | 0.54916 | -16.7358 | 4.4875 | 0.22218 | -0.33716 | 0.071606 | -1.3762 | -0.36657 | -0.003974 | 0.11397
42838.4219 | 138 | 22.9082 | 22.8735 | 22.8521 | 22.778 | 22.3956 | 21.7343 | 22.7174 | 21.7872 | 22.3647 | 22.3718 | 22.3446 | 22.0045 | 21.2055 | 22.1833 | 21.6011 | 21.7696 | 21.8958 | 21.0836 | 21.1777 | 21.3906 | 20.4733 | 20.6157 | 20.9624 | 21.869 | 21.6203 | 21.6438 | 84.0198 | 75.1905 | 92.3612 | 22.0899 | 21.6813 | 21.4019 | 22.0006 | 21.7325 | 21.6533 | 25.7972 | 79.933 |  | 38.1822 | 63.3 | 70.2974 | 43.2407 |  | 16.9758 | 17.0475 | 16.6315 | 16.9403 | 17.1321 | 18.3193 | 36.9993 | 15.5453 | 17.047 | 15.691 | 17.3234 | 18.0802 | 44.8506 | 47.1838 | 43.9282 | 21.5357 |  |  | 0.54432 | -0.32599 | -35.6736 | 0.6137 | 0.12827 | -197.8493 | 14.4069 | 0.55622 | 0.030646 | 0.11613 | 0.057926 | 0.00024806 | 8.8811 | 1.9054 | 21.7908 | 22.014 | 22.194 | 22.2517 | 22.0639 | 21.373 | 20.1934 | 22.1895 | 22.3612 | 22.3957 | 22.3373 | 21.9592 | 21.1949 | 22.2577 | 39.2834 | 24.5755 | 27.1003 | 20.5961 | 19.7629 | 22.7866 | 19.184 | 22.3864 | 22.1453 | 21.7041 | 22.0816 | 21.7978 | 21.2953 | 21.9382 | 21.5254 | 20.9862 | 25.6771 | 84.4737 | 54.7054 | 37.9801 | 0.24399 | -0.022413 | 34.7777 | 22.0476 | 22.3403 | 20.1598 | 21.6321 | 22.0746 | 21.9201 | 21.6949 | 21.9755 | 21.7558 | 21.4153 | 21.2038 | 76.1625 | 94.8879 | 56.0717 | 56.9551 | 33.3507 |  | 25.3051 | 55.8269 | 26.9913 | 39.5399 | 25.8709 | 32.4923 |  | 32.6816 |  |  | 20.835 | 21.5147 | 30.9948 | [5 empty] | 21.8965 | 29.2307 | 21.644 | 22.0135 | 24.8 | 21.1494 | 21.761 | 21.2366 | 33.5734 | 104.5445 |  | 26.9723 | 68.3609 | 19.6655 | 28.5243 | 74.0673 | 25.2198 | 56.7579 | 20.6174 | 51.7068 | 20.5817 | 53.6208 | 18.7085 | 28.6694 | 65.9958 | 21.7875 | 29.6441 | 91.8115 | 19.7429 | 28.3863 | 76.2691 | 19.87 | 49.6961 | 22.1877 | 53.0912 | 20.4951 | 53.7744 | 0.11636 | 20.2508 | 0.51316 | 0.020328 | -27.0468 | 3.0956 | 44.15 | 51.66 | 0.98298 | -0.67783 | -7.0907 | 0.93002 | 0.42611 | -16.7352 | 4.5159 | 0.22639 | -0.34085 | 0.073608 | -1.3981 | -0.46549 | -0.031684 | 0.11038
42838.4219 | 139 | 22.9109 | 22.8739 | 22.8633 | 22.7816 | 22.3952 | 21.7351 | 22.7252 | 21.7947 | 22.3685 | 22.3769 | 22.343 | 22.0037 | 21.2078 | 22.1818 | 21.6056 | 21.7694 | 21.8911 | 21.0787 | 21.1783 | 21.3934 | 20.476 | 20.6197 | 20.9678 | 21.866 | 21.6225 | 21.6541 | 84.2805 | 75.3937 | 92.5835 | 22.0947 | 21.6901 | 21.4048 | 21.9995 | 21.7356 | 21.6608 | 25.8861 | 80.8819 |  | 38.3164 | 63.5366 | 70.4959 | 44.7208 |  | 16.9717 | 17.0423 | 16.6263 | 16.9407 | 17.1354 | 18.3045 | 37.4036 | 15.5665 | 17.0458 | 15.6582 | 17.3242 | 18.076 | 44.8235 | 47.1621 | 43.8992 | 21.53 |  |  | 0.73357 | -0.31023 | -35.1834 | 0.63801 | 0.25444 | -197.8256 | 14.7985 | 0.61207 | 0.063338 | -0.058003 | 0.037442 | 0.00026613 | 8.881 | 1.9134 | 21.7869 | 22.0013 | 22.1908 | 22.2447 | 22.057 | 21.369 | 20.1795 | 22.1812 | 22.3551 | 22.395 | 22.343 | 21.9577 | 21.1936 | 22.2531 | 39.8993 | 26.0233 | 29.2941 | 21.2446 | 19.7648 | 22.8888 | 19.2507 | 22.3785 | 22.1341 | 21.6941 | 22.0787 | 21.7911 | 21.2904 | 21.9389 | 21.517 | 20.9809 | 25.7498 | 84.9151 | 54.8872 | 37.8879 | 0.36844 | 0.074209 | 34.9164 | 22.0386 | 22.3399 | 20.1627 | 21.6338 | 22.0784 | 21.9272 | 21.6825 | 21.9792 | 21.754 | 21.4209 | 21.1963 | 76.4075 | 95.1357 | 56.329 | 57.2248 | 33.4442 |  | 25.3711 | 56.3117 | 27.0826 | 39.0877 | 25.9443 | 32.4843 |  | 32.7982 |  |  | 20.8392 | 21.5215 | 30.9772 | [5 empty] | 21.8971 | 29.3995 | 21.6388 | 22.0124 | 24.8281 | 21.1436 | 21.7584 | 21.2476 | 33.7242 | 104.662 |  | 27.0792 | 68.5542 | 19.6772 | 28.599 | 74.2411 | 25.2531 | 57.1039 | 20.6446 | 51.9082 | 20.6 | 53.7948 | 18.6977 | 28.7774 | 66.192 | 21.8094 | 29.7872 | 91.9094 | 19.7528 | 28.4715 | 76.623 | 19.8699 | 49.8639 | 22.2035 | 53.2478 | 20.512 | 54.0117 | 0.10468 | 20.242 | 0.51895 | 0.019994 | -27.0562 | 3.0956 | 38.24 | 52.66 | 1.1415 | -0.66122 | -7.0417 | 0.94825 | 0.60012 | -16.7338 | 4.5768 | 0.22603 | -0.35122 | 0.088657 | -1.4546 | -0.70146 | -0.06979 | 0.1154
42838.4219 | 140 | 22.9054 | 22.8759 | 22.8619 | 22.7885 | 22.4038 | 21.7283 | 22.7278 | 21.7949 | 22.3719 | 22.3759 | 22.3507 | 22.0044 | 21.2119 | 22.1872 | 21.6032 | 21.7715 | 21.8991 | 21.0791 | 21.1807 | 21.3971 | 20.4781 | 20.611 | 20.974 | 21.8634 | 21.6283 | 21.6691 | 84.5881 | 75.6152 | 93.0222 | 22.0892 | 21.6833 | 21.4047 | 21.9953 | 21.7393 | 21.6656 | 25.9661 | 82.1949 |  | 38.4624 | 63.7385 | 70.7093 | 44.8842 |  | 16.9683 | 17.0441 | 16.6238 | 16.9495 | 17.138 | 18.2984 | 37.3873 | 15.5954 | 17.0434 | 15.624 | 17.3371 | 18.0853 | 44.8039 | 47.1541 | 43.8736 | 21.5338 |  |  | 0.82754 | -0.52182 | -34.7064 | 0.51645 | 0.12433 | -197.8223 | 14.6263 | 0.51219 | -0.022675 | -0.017932 | 0.032754 | 0.00028092 | 8.8812 | 1.9078 | 21.7937 | 22.0063 | 22.1923 | 22.2504 | 22.0681 | 21.3672 | 20.1769 | 22.1866 | 22.3599 | 22.4014 | 22.3423 | 21.9661 | 21.1918 | 22.262 | 40.3629 | 27.0486 | 30.4995 | 22.2224 | 20.5664 | 23.0067 | 19.3214 | 22.392 | 22.1427 | 21.6976 | 22.0809 | 21.7922 | 21.2938 | 21.9386 | 21.5261 | 20.9854 | 25.8311 | 84.98 | 55.0981 | 37.7963 | 0.20389 | 0.01848 | 34.9313 | 22.0492 | 22.3369 | 20.1589 | 21.6308 | 22.076 | 21.9269 | 21.69 | 22.0016 | 21.7562 | 21.4341 | 21.2168 | 76.6409 | 95.5442 | 56.5998 | 57.4767 | 33.4506 |  | 25.4347 | 56.4005 | 27.1521 | 38.8489 | 26.0076 | 32.5296 |  | 32.9215 |  |  | 20.8429 | 21.5192 | 31.2017 | [5 empty] | 21.9044 | 29.4893 | 21.643 | 22.0191 | 24.8534 | 21.141 | 21.7608 | 21.2522 | 33.8328 | 104.6487 |  | 27.1588 | 68.7515 | 19.6826 | 28.7031 | 74.3811 | 25.2926 | 57.3576 | 20.656 | 52.0811 | 20.6041 | 53.9604 | 18.6802 | 28.9976 | 66.3817 | 21.8319 | 29.9391 | 91.9617 | 19.7631 | 28.5834 | 76.8389 | 19.8667 | 50.0096 | 22.2244 | 53.4553 | 20.5293 | 54.2468 | 0.26124 | 20.2323 | 0.52414 | 0.019761 | -27.0478 | 3.0956 | 43.78 | 51.43 | 1.2131 | -0.85757 | -6.9938 | 0.85315 | 0.4195 | -16.7334 | 4.55 | 0.228 | -0.35133 | 0.097429 | -1.4923 | -0.82714 | -0.071624 | 0.1207
42838.4219 | 141 | 22.9039 | 22.8707 | 22.8618 | 22.7801 | 22.3986 | 21.7349 | 22.7122 | 21.7861 | 22.3611 | 22.3743 | 22.346 | 21.9958 | 21.2144 | 22.1791 | 21.5951 | 21.7645 | 21.8874 | 21.0742 | 21.1778 | 21.3901 | 20.4672 | 20.6095 | 20.9642 | 21.8626 | 21.6187 | 21.6641 | 84.7957 | 75.7961 | 92.7923 | 22.0988 | 21.686 | 21.4166 | 21.9987 | 21.7383 | 21.6817 | 26.0357 | 82.9778 |  | 38.6217 | 63.9791 | 70.9539 | 44.4112 |  | 16.9635 | 17.0364 | 16.6145 | 16.9381 | 17.1292 | 18.2835 | 37.2592 | 15.5699 | 17.0455 | 15.5933 | 17.3255 | 18.085 | 44.7936 | 47.1419 | 43.8551 | 21.5347 |  |  | 0.58375 | -0.58556 | -34.088 | 0.72804 | 0.22684 | -197.825 | 14.7473 | 0.35185 | 0.018386 | 0.29026 | 0.12945 | 0.00029406 | 8.8811 | 1.9101 | 21.7962 | 22.0073 | 22.1969 | 22.2534 | 22.0643 | 21.3653 | 20.1843 | 22.1932 | 22.3697 | 22.406 | 22.3508 | 21.9652 | 21.1923 | 22.2644 | 40.1026 | 26.9309 | 31.4779 | 22.4861 | 21.0024 | 23.0895 | 19.3896 | 22.3843 | 22.1455 | 21.6974 | 22.0795 | 21.7939 | 21.2897 | 21.9384 | 21.5237 | 20.9844 | 25.9018 | 85.1768 | 55.4062 | 37.7924 | 0.053487 | 0.011443 | 34.7841 | 22.0472 | 22.3541 | 20.1739 | 21.6405 | 22.095 | 21.9378 | 21.7088 | 22.038 | 21.7684 | 21.4309 | 21.2168 | 76.8647 | 95.8902 | 56.843 | 57.7466 | 33.7109 |  | 25.5172 | 55.9292 | 27.2319 | 39.1633 | 26.0942 | 32.467 |  | 33.0501 |  |  | 20.8445 | 21.5297 | 31.3903 | [5 empty] | 21.9024 | 29.5417 | 21.6432 | 22.0189 | 24.8765 | 21.1388 | 21.7593 | 21.2607 | 33.8975 | 104.6288 |  | 27.2289 | 68.9886 | 19.6864 | 28.8903 | 74.5661 | 25.3365 | 57.569 | 20.6791 | 52.2647 | 20.6179 | 54.1198 | 18.6707 | 29.2595 | 66.5729 | 21.8365 | 30.0767 | 92.188 | 19.7691 | 28.696 | 77.1039 | 19.8571 | 50.1419 | 22.2424 | 53.6879 | 20.5404 | 54.5332 | 0.34879 | 20.2249 | 0.52869 | 0.019682 | -27.0701 | 3.0956 | 42.75 | 52.71 | 1.0186 | -0.90843 | -6.9312 | 1.0129 | 0.56662 | -16.7331 | 4.5687 | 0.22356 | -0.33553 | 0.091628 | -1.4537 | -0.92788 | -0.056128 | 0.1232
42838.4219 | 142 | 22.9112 | 22.8697 | 22.8594 | 22.7786 | 22.393 | 21.7377 | 22.724 | 21.7912 | 22.3683 | 22.3622 | 22.3381 | 22.0054 | 21.215 | 22.1816 | 21.5972 | 21.7643 | 21.8898 | 21.0808 | 21.1822 | 21.3862 | 20.4708 | 20.6149 | 20.9697 | 21.8672 | 21.6216 | 21.6705 | 85.0169 | 75.9372 | 93.5378 | 22.0964 | 21.6839 | 21.4324 | 22.0014 | 21.7411 | 21.6847 | 26.114 | 83.4499 |  | 38.7783 | 64.2774 | 71.2412 | 43.7409 |  | 16.9651 | 17.0284 | 16.6099 | 16.9369 | 17.1212 | 18.3424 | 37.4279 | 15.5449 | 17.0517 | 15.5903 | 17.3281 | 18.0766 | 44.7456 | 47.1194 | 43.8345 | 21.53 |  |  | 0.54892 | -0.46727 | -33.1845 | 0.62422 | 0.32343 | -197.8473 | 15.177 | 0.47014 | 0.14663 | 0.2397 | 0.099243 | 0.00030063 | 8.881 | 1.9267 | 21.788 | 22 | 22.1885 | 22.247 | 22.0573 | 21.3593 | 20.1737 | 22.1853 | 22.3598 | 22.3966 | 22.3409 | 21.9584 | 21.1881 | 22.2578 | 39.1114 | 26.0666 | 30.9802 | 23.1587 | 21.2819 | 23.1587 | 19.4479 | 22.3849 | 22.1476 | 21.6965 | 22.0841 | 21.7909 | 21.2965 | 21.945 | 21.5267 | 20.9954 | 25.9729 | 85.458 | 55.8302 | 37.8921 | 0.1048 | -0.13197 | 34.861 | 22.0439 | 22.3481 | 20.1762 | 21.6489 | 22.0766 | 21.9311 | 21.7002 | 22.0423 | 21.7664 | 21.4357 | 21.2217 | 77.0527 | 96.042 | 57.0458 | 57.9808 | 34.0832 |  | 25.5883 | 55.4835 | 27.3013 | 39.5891 | 26.173 | 32.5538 |  | 33.1951 |  |  | 20.8506 | 21.5417 | 31.5913 | [5 empty] | 21.9052 | 29.5689 | 21.6441 | 22.0193 | 24.9144 | 21.1464 | 21.7618 | 21.2708 | 33.9696 | 105.3534 |  | 27.264 | 69.2952 | 19.6945 | 29.0574 | 74.8076 | 25.3721 | 57.7348 | 20.6932 | 52.4495 | 20.6265 | 54.2828 | 18.6614 | 29.4934 | 66.8525 | 21.8528 | 30.1462 | 92.5575 | 19.7767 | 28.8232 | 77.3229 | 19.8582 | 50.3158 | 22.2565 | 53.8188 | 20.557 | 54.9502 | 0.13714 | 20.217 | 0.53337 | 0.019253 | -27.0769 | 3.0956 | 49.8 | 51.27 | 0.98871 | -0.81149 | -6.8386 | 0.93792 | 0.67666 | -16.7358 | 4.6353 | 0.21562 | -0.3208 | 0.082471 | -1.3354 | -0.86577 | -0.034855 | 0.12283
42838.4219 | 143 | 22.9081 | 22.8794 | 22.8677 | 22.7948 | 22.4004 | 21.7366 | 22.7234 | 21.793 | 22.3714 | 22.3804 | 22.3462 | 22.0104 | 21.2159 | 22.1877 | 21.6049 | 21.776 | 21.9029 | 21.0878 | 21.1883 | 21.3979 | 20.4756 | 20.6243 | 20.9789 | 21.8798 | 21.6243 | 21.697 | 85.21 | 76.0938 | 94.0467 | 22.0968 | 21.6859 | 21.4386 | 22.0069 | 21.7408 | 21.6984 | 26.1733 | 83.0536 |  | 38.9179 | 64.5239 | 71.4737 | 43.1639 |  | 16.9694 | 17.0284 | 16.6052 | 16.929 | 17.1169 | 18.3711 | 37.7568 | 15.5483 | 17.0537 | 15.5884 | 17.3367 | 18.0791 | 44.7056 | 47.1081 | 43.8198 | 21.5448 |  |  | 0.40896 | -0.165 | -32.6365 | 0.29566 | 0.21106 | -197.848 | 15.1113 | 0.42874 | -0.0078852 | 0.051093 | 0.12997 | 0.0002957 | 8.8811 | 1.9305 | 21.7873 | 21.9993 | 22.1888 | 22.2447 | 22.0615 | 21.3541 | 20.1723 | 22.186 | 22.3513 | 22.3926 | 22.337 | 21.9548 | 21.188 | 22.2514 | 38.6824 | 25.2477 | 29.6739 | 22.7768 | 21.6199 | 23.2305 | 19.4871 | 22.3818 | 22.1448 | 21.6955 | 22.0873 | 21.7908 | 21.2905 | 21.9432 | 21.5228 | 20.9967 | 26.0413 | 85.69 | 56.1262 | 37.8109 | 0.014757 | -0.062355 | 35.2065 | 22.0445 | 22.3384 | 20.1736 | 21.6391 | 22.0817 | 21.9168 | 21.702 | 22.058 | 21.7606 | 21.4288 | 21.2234 | 77.2319 | 96.2076 | 57.2157 | 58.1764 | 34.4289 |  | 25.6797 | 55.4572 | 27.377 | 39.8895 | 26.2523 | 33.1265 |  | 33.3487 |  |  | 20.8581 | 21.5726 | 31.6935 | [5 empty] | 21.9027 | 29.5983 | 21.6477 | 22.0243 | 24.9406 | 21.1536 | 21.7694 | 21.2777 | 34.0837 | 105.6778 |  | 27.3093 | 69.5226 | 19.7059 | 29.1812 | 74.9863 | 25.4188 | 57.9122 | 20.7136 | 52.732 | 20.6399 | 54.4505 | 18.658 | 29.6977 | 67.1339 | 21.8759 | 30.1517 | 92.7944 | 19.7819 | 28.9483 | 77.4334 | 19.8638 | 50.532 | 22.2787 | 53.936 | 20.5833 | 55.5056 | 0.20744 | 20.2099 | 0.53782 | 0.019086 | -27.0283 | 3.0956 | 41.81 | 52.04 | 0.854 | -0.48222 | -6.7819 | 0.6455 | 0.54665 | -16.7366 | 4.6254 | 0.20911 | -0.3175 | 0.076809 | -1.2794 | -0.71605 | -0.016821 | 0.1274
42838.4219 | 144 | 22.9082 | 22.8718 | 22.8586 | 22.7821 | 22.4007 | 21.7335 | 22.7194 | 21.794 | 22.3642 | 22.3669 | 22.3479 | 22.0004 | 21.2131 | 22.184 | 21.6001 | 21.772 | 21.9001 | 21.0857 | 21.1823 | 21.3888 | 20.4788 | 20.628 | 20.9845 | 21.8634 | 21.6291 | 21.7057 | 85.3224 | 76.3284 | 94.3478 | 22.0929 | 21.6895 | 21.4404 | 22.0028 | 21.7406 | 21.7062 | 26.2389 | 82.8966 |  | 39.0745 | 64.751 | 71.6613 | 42.7164 |  | 16.9559 | 17.022 | 16.5985 | 16.926 | 17.1073 | 18.3805 | 38.122 | 15.5909 | 17.0429 | 15.5916 | 17.3363 | 18.0767 | 44.6535 | 47.0793 | 43.7901 | 21.5346 |  |  | 0.53512 | -0.17026 | -32.3381 | 0.35611 | 0.1493 | -197.8328 | 15.3433 | 0.46948 | -0.028318 | 0.25292 | 0.080842 | 0.00031542 | 8.8811 | 1.9238 | 21.7916 | 22.0077 | 22.2011 | 22.2554 | 22.0726 | 21.3715 | 20.1809 | 22.1934 | 22.3739 | 22.3982 | 22.3474 | 21.9693 | 21.2014 | 22.2695 | 38.3244 | 25.0314 | 29.5652 | 21.8962 | 21.2663 | 23.2887 | 19.5259 | 22.3818 | 22.1414 | 21.6964 | 22.0864 | 21.7964 | 21.2915 | 21.9387 | 21.5306 | 20.9987 | 26.1074 | 86.0909 | 56.4949 | 37.678 | 0.09556 | -0.014234 | 35.3305 | 22.0511 | 22.3452 | 20.1773 | 21.6431 | 22.0803 | 21.9339 | 21.6968 | 22.0827 | 21.7635 | 21.4284 | 21.2367 | 77.4165 | 96.5624 | 57.4201 | 58.4065 | 34.5264 |  | 25.7568 | 55.7273 | 27.4461 | 39.9488 | 26.3359 | 33.3918 |  | 33.486 |  |  | 20.8514 | 21.5755 | 31.594 | [5 empty] | 21.8947 | 29.6379 | 21.6444 | 22.0124 | 24.9497 | 21.1465 | 21.7692 | 21.2993 | 34.2713 | 106.1593 |  | 27.3843 | 69.6185 | 19.722 | 29.2164 | 75.1544 | 25.4575 | 58.1621 | 20.7442 | 53.045 | 20.6638 | 54.6553 | 18.6649 | 29.8268 | 67.3361 | 21.8966 | 30.1763 | 92.9707 | 19.7823 | 29.0471 | 77.5991 | 19.8674 | 50.6831 | 22.3032 | 54.1034 | 20.6039 | 55.8205 | 0.075923 | 20.2027 | 0.54257 | 0.01958 | -27.0374 | 3.0956 | 43.81 | 52.08 | 0.97728 | -0.48983 | -6.7508 | 0.70842 | 0.45976 | -16.7363 | 4.6609 | 0.20901 | -0.32266 | 0.077993 | -1.2328 | -0.69944 | -0.0021707 | 0.13334
42838.422 | 145 | 22.9142 | 22.8801 | 22.8612 | 22.7828 | 22.3989 | 21.7346 | 22.7233 | 21.7899 | 22.3677 | 22.3738 | 22.3486 | 22.0045 | 21.2179 | 22.1895 | 21.6052 | 21.7811 | 21.9003 | 21.0825 | 21.1838 | 21.3995 | 20.4673 | 20.6259 | 20.987 | 21.8687 | 21.622 | 21.7162 | 85.5501 | 76.4934 | 94.7636 | 22.0909 | 21.6862 | 21.4436 | 22.0076 | 21.7322 | 21.713 | 26.3147 | 83.1029 |  | 39.231 | 64.9545 | 71.839 | 42.5679 |  | 16.9534 | 17.0329 | 16.5976 | 16.9169 | 17.1093 | 18.4612 | 38.5729 | 15.6409 | 17.0468 | 15.6085 | 17.3338 | 18.0754 | 44.6303 | 47.0584 | 43.7721 | 21.5365 |  |  | 0.68297 | -0.32665 | -31.982 | 0.52828 | 0.17755 | -197.8289 | 15.5654 | 0.40179 | 0.1332 | 0.10921 | 0.11921 | 0.00026778 | 8.8813 | 1.9214 | 21.7769 | 21.998 | 22.1902 | 22.2406 | 22.0631 | 21.3639 | 20.171 | 22.1825 | 22.3605 | 22.3944 | 22.3381 | 21.9578 | 21.1911 | 22.2577 | 38.703 | 24.2396 | 28.5644 | 21.8152 | 20.6892 | 23.3746 | 19.5765 | 22.3773 | 22.1425 | 21.697 | 22.0768 | 21.7941 | 21.2861 | 21.9407 | 21.5238 | 21.0036 | 26.1808 | 86.4583 | 56.8626 | 37.4532 | 0.063317 | -0.035536 | 35.3672 | 22.0466 | 22.3455 | 20.1683 | 21.6437 | 22.0811 | 21.9308 | 21.7015 | 22.0962 | 21.7609 | 21.4324 | 21.2375 | 77.6269 | 96.8179 | 57.6135 | 58.6344 | 34.3606 |  | 25.8338 | 56.5009 | 27.5348 | 39.9646 | 26.4102 | 34.1468 |  | 33.6292 |  |  | 20.8323 | 21.5872 | 31.5305 | [5 empty] | 21.8884 | 29.6365 | 21.6355 | 22.0091 | 24.9428 | 21.1379 | 21.7559 | 21.3137 | 34.5085 | 106.5442 |  | 27.5098 | 69.8686 | 19.7171 | 29.2273 | 75.2195 | 25.4904 | 58.4207 | 20.7559 | 53.3204 | 20.6782 | 54.8723 | 18.6569 | 29.9221 | 67.4708 | 21.9154 | 30.2918 | 93.1561 | 19.802 | 29.2151 | 77.9834 | 19.8872 | 50.8164 | 22.3295 | 54.2987 | 20.6292 | 56.0452 | 0.39164 | 20.1944 | 0.54775 | 0.019674 | -27.0421 | 3.0956 | 57.89 | 51.49 | 1.1047 | -0.67849 | -6.7136 | 0.86285 | 0.50145 | -16.7384 | 4.6951 | 0.21622 | -0.34114 | 0.080072 | -1.2648 | -0.58233 | 0.0045232 | 0.14206
42838.422 | 146 | 22.9155 | 22.8798 | 22.8681 | 22.7842 | 22.3999 | 21.7382 | 22.7237 | 21.7904 | 22.3704 | 22.3707 | 22.3481 | 22.0079 | 21.2142 | 22.1887 | 21.609 | 21.7802 | 21.9054 | 21.0884 | 21.1869 | 21.3979 | 20.4663 | 20.6193 | 20.9885 | 21.8733 | 21.6299 | 21.7262 | 85.8133 | 76.6243 | 94.6386 | 22.0956 | 21.6857 | 21.4484 | 22.0002 | 21.7349 | 21.7173 | 26.3857 | 82.9126 |  | 39.3829 | 65.1248 | 72.0222 | 42.6465 |  | 16.9561 | 17.0338 | 16.6022 | 16.9212 | 17.1069 | 18.5464 | 38.7275 | 15.6978 | 17.0479 | 15.6027 | 17.3421 | 18.0853 | 44.606 | 47.0438 | 43.7576 | 21.5384 |  |  | 0.65209 | -0.40945 | -31.7947 | 0.51842 | 0.006044 | -197.8499 | 15.2454 | 0.58973 | 0.031229 | 0.063471 | 0.16556 | 0.00029406 | 8.8811 | 1.9242 | 21.786 | 21.9971 | 22.193 | 22.2413 | 22.0582 | 21.3562 | 20.1678 | 22.1884 | 22.3627 | 22.3883 | 22.3364 | 21.9575 | 21.1937 | 22.2586 | 38.7071 | 23.9867 | 27.4728 | 21.5393 | 20.2003 | 23.4391 | 19.6017 | 22.3858 | 22.1477 | 21.6951 | 22.0864 | 21.7994 | 21.2975 | 21.9422 | 21.5312 | 21.0006 | 26.2605 | 86.3683 | 57.0671 | 37.7007 | 0.22394 | -0.14338 | 35.1316 | 22.0441 | 22.3454 | 20.1683 | 21.647 | 22.0892 | 21.9336 | 21.6968 | 22.1129 | 21.7641 | 21.4404 | 21.2511 | 77.8244 | 96.9534 | 57.846 | 58.8612 | 34.487 |  | 25.9189 | 56.7563 | 27.6291 | 40.2581 | 26.4806 | 34.3789 |  | 33.7293 |  |  | 20.8554 | 21.608 | 31.5682 | [5 empty] | 21.8972 | 29.7071 | 21.6452 | 22.0138 | 24.9872 | 21.1403 | 21.7613 | 21.3173 | 34.7049 | 106.6527 |  | 27.6428 | 70.1025 | 19.7214 | 29.252 | 75.336 | 25.5266 | 58.5852 | 20.7699 | 53.539 | 20.6813 | 55.1221 | 18.6692 | 29.9625 | 67.6839 | 21.9422 | 30.4624 | 93.2255 | 19.8149 | 29.2946 | 78.2633 | 19.8977 | 50.9436 | 22.35 | 54.4252 | 20.6365 | 56.2713 | 0.25827 | 20.1896 | 0.55219 | 0.019043 | -27.0634 | 3.0956 | 39.35 | 52.61 | 1.0792 | -0.75963 | -6.6939 | 0.85476 | 0.092533 | -16.7417 | 4.6473 | 0.21559 | -0.34503 | 0.074304 | -1.2577 | -0.4581 | 0.0047439 | 0.13789
42838.422 | 147 | 22.9081 | 22.8715 | 22.8645 | 22.7755 | 22.3961 | 21.7311 | 22.7054 | 21.7874 | 22.3618 | 22.3708 | 22.3425 | 22.0039 | 21.2106 | 22.179 | 21.5943 | 21.7685 | 21.8998 | 21.0809 | 21.1724 | 21.391 | 20.4661 | 20.6201 | 20.9797 | 21.864 | 21.6235 | 21.7245 | 85.99 | 76.8187 | 94.3341 | 22.091 | 21.6802 | 21.4518 | 21.9997 | 21.7341 | 21.7219 | 26.4585 | 82.9696 |  | 39.5484 | 65.3242 | 72.2091 | 42.7606 |  | 16.9599 | 17.0378 | 16.6146 | 16.9292 | 17.109 | 18.6318 | 38.7633 | 15.7277 | 17.0496 | 15.6047 | 17.3535 | 18.0845 | 44.5779 | 47.0165 | 43.7518 | 21.5364 |  |  | 0.71714 | -0.32205 | -31.4484 | 0.45665 | 0.040872 | -197.8342 | 15.6344 | 0.79015 | 0.14857 | 0.05382 | 0.24837 | 0.00031542 | 8.881 | 1.9109 | 21.7858 | 21.997 | 22.1958 | 22.2403 | 22.0628 | 21.3723 | 20.1758 | 22.1891 | 22.3673 | 22.3937 | 22.3462 | 21.9715 | 21.1966 | 22.2593 | 39.1754 | 24.4321 | 26.9551 | 21.2228 | 19.695 | 23.5193 | 19.6215 | 22.3789 | 22.1402 | 21.6947 | 22.0801 | 21.7906 | 21.2909 | 21.9348 | 21.5248 | 21.0038 | 26.3269 | 86.3161 | 57.2414 | 38.0307 | 0.44217 | -0.17457 | 35.0325 | 22.0418 | 22.3522 | 20.1675 | 21.6493 | 22.0851 | 21.9323 | 21.7057 | 22.1363 | 21.7706 | 21.4284 | 21.2533 | 77.9706 | 97.045 | 58.0552 | 59.0878 | 35.0163 |  | 26.0037 | 56.6062 | 27.7178 | 40.4032 | 26.5561 | 34.2099 |  | 33.843 |  |  | 20.8564 | 21.6166 | 31.7496 | [5 empty] | 21.895 | 29.7621 | 21.6301 | 22.0093 | 24.9965 | 21.1373 | 21.7585 | 21.3347 | 34.8716 | 107.1039 |  | 27.7666 | 70.2771 | 19.7328 | 29.3454 | 75.639 | 25.5754 | 58.8382 | 20.7936 | 53.718 | 20.7097 | 55.3483 | 18.6731 | 30.0104 | 67.9508 | 21.9663 | 30.6307 | 93.3919 | 19.8144 | 29.295 | 78.4864 | 19.9061 | 51.1066 | 22.3646 | 54.6586 | 20.6566 | 56.5427 | 0.3219 | 20.1822 | 0.55646 | 0.019304 | -27.0446 | 3.0956 | 48.79 | 51.72 | 1.1313 | -0.67371 | -6.6574 | 0.80223 | 0.24066 | -16.7435 | 4.7069 | 0.20376 | -0.33785 | 0.072834 | -1.3004 | -0.39826 | 0.0040396 | 0.13097
42838.422 | 148 | 22.9128 | 22.8738 | 22.858 | 22.7744 | 22.3964 | 21.7309 | 22.7161 | 21.7965 | 22.3695 | 22.3716 | 22.3458 | 22.0063 | 21.2124 | 22.1802 | 21.592 | 21.7736 | 21.9 | 21.0794 | 21.1729 | 21.3872 | 20.4724 | 20.6277 | 20.9937 | 21.868 | 21.6273 | 21.7465 | 86.225 | 76.979 | 94.5763 | 22.0965 | 21.6943 | 21.4713 | 22.002 | 21.7414 | 21.7456 | 26.5436 | 83.8304 |  | 39.7459 | 65.549 | 72.352 | 42.7448 |  | 16.9564 | 17.0392 | 16.6076 | 16.9232 | 17.1329 | 18.6622 | 39.0163 | 15.7146 | 17.0373 | 15.595 | 17.3416 | 18.0852 | 44.5622 | 47.0071 | 43.7477 | 21.5408 |  |  | 0.75 | -0.11309 | -31.2276 | 0.44482 | 0.11184 | -197.8631 | 15.2749 | 0.5779 | 0.037651 | 0.098717 | 0.17059 | 0.00032527 | 8.8809 | 1.903 | 21.7837 | 22.0007 | 22.1953 | 22.2503 | 22.0628 | 21.3713 | 20.175 | 22.1871 | 22.3663 | 22.3979 | 22.3421 | 21.9686 | 21.1978 | 22.2689 | 40.4838 | 25.1557 | 28.8367 | 21.3543 | 19.7538 | 23.6278 | 19.6653 | 22.3746 | 22.1413 | 21.6942 | 22.0822 | 21.7965 | 21.2935 | 21.9324 | 21.5212 | 21.0192 | 26.4107 | 86.3013 | 57.4027 | 38.5518 | 0.35409 | -0.066159 | 35.1277 | 22.0359 | 22.3399 | 20.1603 | 21.6459 | 22.0817 | 21.9248 | 21.6984 | 22.143 | 21.7644 | 21.4374 | 21.2549 | 78.191 | 97.1351 | 58.2189 | 59.2857 | 35.0531 |  | 26.0922 | 56.2655 | 27.8025 | 40.4918 | 26.6491 | 33.8644 |  | 33.9684 |  |  | 20.8577 | 21.6254 | 31.8217 | [5 empty] | 21.8991 | 29.8277 | 21.6416 | 22.0255 | 25.0356 | 21.1584 | 21.7699 | 21.3358 | 35.012 | 107.326 |  | 27.868 | 70.6061 | 19.7444 | 29.4844 | 75.833 | 25.6071 | 59.0739 | 20.8077 | 53.8423 | 20.7146 | 55.4585 | 18.6791 | 30.092 | 68.2512 | 21.983 | 30.735 | 93.7426 | 19.8195 | 29.3079 | 78.7495 | 19.923 | 51.3096 | 22.4019 | 54.847 | 20.6775 | 56.8049 | 0.034927 | 20.1759 | 0.56088 | 0.019333 | -27.1424 | 3.0956 | 23.8 | 51.84 | 1.1573 | -0.39923 | -6.634 | 0.79177 | 0.39812 | -16.7456 | 4.6527 | 0.20573 | -0.32551 | 0.073522 | -1.433 | -0.60221 | 0.0073626 | 0.11933
42838.422 | 149 | 22.9015 | 22.8755 | 22.8611 | 22.7822 | 22.404 | 21.7372 | 22.7151 | 21.7807 | 22.3663 | 22.37 | 22.3437 | 21.9906 | 21.2081 | 22.182 | 21.6009 | 21.7803 | 21.9023 | 21.0907 | 21.1802 | 21.3967 | 20.4723 | 20.6278 | 20.9987 | 21.8724 | 21.6299 | 21.762 | 86.4193 | 77.1344 | 94.7396 | 22.1019 | 21.6988 | 21.475 | 22.0045 | 21.7447 | 21.752 | 26.6293 | 85.2614 |  | 39.9484 | 65.7765 | 72.4778 | 42.7071 |  | 16.9642 | 17.0373 | 16.6241 | 16.9301 | 17.1508 | 18.6809 | 39.0259 | 15.7095 | 17.0449 | 15.6241 | 17.354 | 18.0834 | 44.5383 | 46.9864 | 43.7332 | 21.5383 |  |  | 0.76709 | -0.2064 | -31.3341 | 0.74775 | 0.19792 | -197.7849 | 15.9097 | 0.4813 | 0.073458 | 0.1604 | 0.16035 | 0.00027928 | 8.8811 | 1.9035 | 21.7817 | 21.9972 | 22.1927 | 22.2516 | 22.0615 | 21.3629 | 20.1765 | 22.1849 | 22.3595 | 22.3997 | 22.3365 | 21.9662 | 21.1927 | 22.2651 | 41.6224 | 26.1785 | 29.1734 | 21.3015 | 20.2553 | 23.7539 | 19.709 | 22.3834 | 22.1377 | 21.6906 | 22.0873 | 21.7987 | 21.2879 | 21.9437 | 21.5272 | 21.0131 | 26.5058 | 86.4431 | 57.6277 | 38.9754 | 0.38004 | 0.11434 | 35.1235 | 22.0524 | 22.3446 | 20.175 | 21.6439 | 22.0905 | 21.9401 | 21.7072 | 22.1699 | 21.7774 | 21.4373 | 21.2656 | 78.4261 | 97.3512 | 58.4026 | 59.4528 | 34.723 |  | 26.1586 | 56.4078 | 27.8931 | 40.1314 | 26.7229 | 33.6517 |  | 34.0828 |  |  | 20.8555 | 21.6309 | 31.9428 | [5 empty] | 21.8933 | 29.893 | 21.6395 | 22.0139 | 25.0429 | 21.1491 | 21.7672 | 21.3436 | 35.0793 | 107.4973 |  | 27.9333 | 70.8681 | 19.7481 | 29.6006 | 76.0003 | 25.6343 | 59.3408 | 20.8127 | 54.1224 | 20.7223 | 55.6794 | 18.6747 | 30.2079 | 68.4973 | 21.998 | 30.8191 | 93.9962 | 19.8337 | 29.3938 | 79.0469 | 19.9284 | 51.5757 | 22.4278 | 55.0636 | 20.6959 | 57.0118 | 0.16533 | 20.1694 | 0.56526 | 0.018121 | -27.119 | 3.0956 | 48.12 | 52.37 | 1.1707 | -0.53934 | -6.6453 | 1.0266 | 0.52964 | -16.7428 | 4.7486 | 0.21715 | -0.32639 | 0.086035 | -1.5448 | -0.63453 | 0.011314 | 0.11079
42838.422 | 150 | 22.9058 | 22.8696 | 22.8598 | 22.7743 | 22.4006 | 21.7263 | 22.7108 | 21.785 | 22.3653 | 22.3624 | 22.3441 | 21.9997 | 21.2065 | 22.1796 | 21.6082 | 21.7789 | 21.9067 | 21.0911 | 21.1876 | 21.3947 | 20.4727 | 20.6267 | 21.0039 | 21.8713 | 21.6301 | 21.7754 | 86.6913 | 77.3509 | 95.4958 | 22.0928 | 21.6906 | 21.4789 | 21.9993 | 21.7434 | 21.7512 | 26.7044 | 86.0893 |  | 40.1278 | 66.0308 | 72.5868 | 42.6594 |  | 16.9601 | 17.0441 | 16.6191 | 16.9334 | 17.165 | 18.6841 | 38.9104 | 15.7607 | 17.0431 | 15.6891 | 17.3577 | 18.0917 | 44.5208 | 46.9779 | 43.7127 | 21.539 |  |  | 0.71649 | -0.26882 | -30.8044 | 0.52696 | 0.12038 | -197.8755 | 15.7375 | 0.6975 | -0.004577 | -0.011847 | -0.069496 | 0.00036634 | 1.0217 | 1.9018 | 21.7822 | 22.0007 | 22.1956 | 22.2504 | 22.0634 | 21.3617 | 20.1745 | 22.186 | 22.3585 | 22.4013 | 22.339 | 21.9677 | 21.1897 | 22.2595 | 42.7231 | 27.8612 | 31.4382 | 21.572 | 20.1746 | 23.881 | 19.7778 | 22.3825 | 22.1418 | 21.695 | 22.0827 | 21.7886 | 21.2902 | 21.9385 | 21.5328 | 21.0134 | 26.5868 | 86.8283 | 58.1308 | 39.0904 | 0.29648 | 0.0078292 | 35.4572 | 22.0346 | 22.3268 | 20.167 | 21.6273 | 22.0712 | 21.9246 | 21.6833 | 22.1725 | 21.7563 | 21.4272 | 21.2621 | 78.588 | 97.6802 | 58.6351 | 59.6096 | 34.7663 |  | 26.2224 | 56.6433 | 27.9922 | 39.6893 | 26.7921 | 33.6532 |  | 34.2033 |  |  | 20.8569 | 21.633 | 32.3132 | [5 empty] | 21.8882 | 29.9201 | 21.6367 | 22.0163 | 25.0589 | 21.1414 | 21.7647 | 21.3633 | 35.1364 | 107.6997 |  | 28.0327 | 71.1718 | 19.7615 | 29.6711 | 76.3273 | 25.671 | 59.5361 | 20.8333 | 54.3819 | 20.7369 | 55.9601 | 18.6827 | 30.3567 | 68.6649 | 22.0164 | 30.9384 | 94.1236 | 19.8462 | 29.5268 | 79.2383 | 19.9333 | 51.847 | 22.4486 | 55.293 | 20.7123 | 57.2414 | 0.27775 | 20.1623 | 0.5696 | 0.017736 | -27.0539 | 3.0956 | 55.9 | 51.36 | 1.1326 | -0.61553 | -6.589 | 0.86179 | 0.41307 | -16.7468 | 4.7228 | 0.21811 | -0.32956 | 0.10066 | -1.6522 | -0.87812 | 0.015185 | 0.11034
42838.422 | 151 | 22.9114 | 22.8662 | 22.8603 | 22.7786 | 22.3945 | 21.7306 | 22.7122 | 21.7881 | 22.3667 | 22.3697 | 22.342 | 22.006 | 21.2072 | 22.1747 | 21.5994 | 21.7733 | 21.9013 | 21.0834 | 21.1811 | 21.3877 | 20.4701 | 20.6183 | 21.0062 | 21.8638 | 21.6274 | 21.7793 | 86.9504 | 77.5467 | 95.7616 | 22.0898 | 21.6868 | 21.4811 | 21.9936 | 21.7378 | 21.7564 | 26.7924 | 86.4493 |  | 40.2827 | 66.2881 | 72.7573 | 43.0136 |  | 16.9645 | 17.0544 | 16.6249 | 16.9313 | 17.1631 | 18.6558 | 38.9077 | 15.7954 | 17.0405 | 15.7357 | 17.3576 | 18.0864 | 44.4885 | 46.9557 | 43.6879 | 21.5404 |  |  | 0.55681 | -0.094033 | -30.2938 | 0.67284 | 0.14404 | -197.8263 | 15.7862 | 0.41165 | -0.10655 | 0.14655 | -0.012382 | 0.00037127 | 0.0003187 | 1.908 | 21.7823 | 22.0021 | 22.19 | 22.2487 | 22.0574 | 21.3643 | 20.1739 | 22.1823 | 22.3609 | 22.4027 | 22.3417 | 21.9687 | 21.1875 | 22.2608 | 42.8742 | 28.4137 | 33.0206 | 22.1412 | 20.5343 | 23.9858 | 19.8418 | 22.3799 | 22.1445 | 21.7018 | 22.0819 | 21.7886 | 21.2933 | 21.9401 | 21.5296 | 21.0223 | 26.6669 | 86.9781 | 58.4404 | 39.0754 | 0.41897 | 0.0059272 | 35.6077 | 22.04 | 22.3378 | 20.1671 | 21.6366 | 22.0857 | 21.9286 | 21.695 | 22.1922 | 21.7652 | 21.4356 | 21.2805 | 78.8401 | 97.8068 | 58.8947 | 59.7657 | 35.1041 |  | 26.3155 | 56.6815 | 28.1126 | 39.6552 | 26.875 | 33.8047 |  | 34.3453 |  |  | 20.863 | 21.6428 | 32.3535 | [5 empty] | 21.8929 | 29.9607 | 21.6419 | 22.0198 | 25.0936 | 21.1389 | 21.7655 | 21.3621 | 35.2154 | 107.8618 |  | 28.2095 | 71.4318 | 19.7687 | 29.7078 | 76.5373 | 25.6955 | 59.7025 | 20.8389 | 54.5812 | 20.749 | 56.1916 | 18.6873 | 30.4232 | 68.7517 | 22.0347 | 31.0848 | 94.3121 | 19.8543 | 29.6438 | 79.316 | 19.936 | 52.101 | 22.4685 | 55.4901 | 20.7253 | 57.4485 | 0.43134 | 20.1562 | 0.57406 | 0.018019 | -27.0784 | 3.0956 | 40.67 | 52.29 | 0.9988 | -0.36405 | -6.5343 | 0.97381 | 0.45181 | -16.7439 | 4.7299 | 0.21188 | -0.32653 | 0.10442 | -1.6567 | -1.0465 | 0.0083286 | 0.11347
42838.422 | 152 | 22.9074 | 22.8697 | 22.864 | 22.7794 | 22.4009 | 21.7277 | 22.7151 | 21.7892 | 22.3616 | 22.3704 | 22.3425 | 21.9986 | 21.2131 | 22.1785 | 21.5918 | 21.7676 | 21.8964 | 21.0843 | 21.1861 | 21.3929 | 20.4711 | 20.6194 | 21.0057 | 21.8636 | 21.6265 | 21.789 | 87.1614 | 77.7223 | 95.6606 | 22.0926 | 21.6892 | 21.4946 | 21.9974 | 21.7377 | 21.7711 | 26.898 | 86.4979 |  | 40.4454 | 66.5648 | 72.9624 | 43.2483 |  | 16.9617 | 17.0575 | 16.6243 | 16.9311 | 17.149 | 18.6207 | 38.7176 | 15.753 | 17.0448 | 15.7488 | 17.3583 | 18.0915 | 44.4597 | 46.9469 | 43.6823 | 21.5492 |  |  | 0.6902 | -0.27343 | -30.0106 | 0.82529 | 0.004732 | -197.8204 | 16.2415 | 0.49773 | -0.041746 | 0.11613 | 0.004284 | 0.00038277 | 0.00035156 | 1.9063 | 21.7871 | 22.0003 | 22.1976 | 22.2488 | 22.063 | 21.3669 | 20.1707 | 22.1975 | 22.3605 | 22.3939 | 22.3421 | 21.973 | 21.1934 | 22.2594 | 43.5389 | 29.3193 | 34.0778 | 22.023 | 20.9055 | 24.1049 | 19.9133 | 22.38 | 22.1474 | 21.6946 | 22.0858 | 21.7913 | 21.287 | 21.9374 | 21.5305 | 21.0279 | 26.7452 | 87.1215 | 58.7581 | 39.0402 | 0.37866 | 0.16512 | 35.5594 | 22.0376 | 22.3401 | 20.1697 | 21.6413 | 22.0852 | 21.9312 | 21.7025 | 22.2122 | 21.7653 | 21.4309 | 21.2866 | 79.0153 | 97.8966 | 59.1363 | 59.9681 | 35.3874 |  | 26.3805 | 56.6778 | 28.1867 | 39.8965 | 26.937 | 33.8009 |  | 34.4662 |  |  | 20.8751 | 21.6577 | 32.2936 | [5 empty] | 21.8945 | 30.0173 | 21.6499 | 22.0197 | 25.1136 | 21.144 | 21.7685 | 21.3593 | 35.3152 | 108.0868 |  | 28.4456 | 71.6365 | 19.7821 | 29.784 | 76.6782 | 25.7153 | 59.9072 | 20.8448 | 54.7529 | 20.7657 | 56.3976 | 18.6796 | 30.4848 | 68.9164 | 22.0516 | 31.2046 | 94.5878 | 19.8629 | 29.7414 | 79.3568 | 19.9459 | 52.3463 | 22.4922 | 55.6622 | 20.7338 | 57.6926 | 0.254 | 20.1506 | 0.57791 | 0.019101 | -27.0049 | 3.0956 | 51.28 | 51.5 | 1.1119 | -0.62078 | -6.5037 | 1.0785 | 0.081886 | -16.7426 | 4.7974 | 0.20621 | -0.32391 | 0.099819 | -1.7166 | -1.1556 | 0.00539 | 0.1171
42838.422 | 153 | 22.9054 | 22.8716 | 22.8566 | 22.7738 | 22.3953 | 21.7273 | 22.7123 | 21.7878 | 22.3663 | 22.3703 | 22.3409 | 22.0047 | 21.2175 | 22.1784 | 21.5997 | 21.774 | 21.9037 | 21.0867 | 21.1832 | 21.3968 | 20.4757 | 20.6274 | 21.0022 | 21.8745 | 21.6303 | 21.7968 | 87.328 | 77.9269 | 95.4757 | 22.0969 | 21.69 | 21.4983 | 22.0027 | 21.7379 | 21.7826 | 27.001 | 86.0327 |  | 40.6082 | 66.9025 | 73.1957 | 43.9183 |  | 16.9676 | 17.0544 | 16.6189 | 16.9326 | 17.1402 | 18.5842 | 39.25 | 15.7543 | 17.044 | 15.7192 | 17.3604 | 18.0892 | 44.4174 | 46.9358 | 43.6564 | 21.5406 |  |  | 0.66326 | -0.211 | -30.0822 | 0.51973 | 0.14732 | -197.8184 | 15.8072 | 0.38537 | 0.082604 | 0.14928 | 0.070078 | 0.00036306 | 0.0003302 | 1.9128 | 21.7804 | 21.9917 | 22.1931 | 22.2482 | 22.0536 | 21.3589 | 20.1697 | 22.1869 | 22.3604 | 22.3923 | 22.3366 | 21.9585 | 21.1802 | 22.2631 | 43.2465 | 29.7267 | 34.9548 | 23.2536 | 21.4068 | 24.2154 | 20.0038 | 22.3799 | 22.1464 | 21.7083 | 22.0868 | 21.7964 | 21.2872 | 21.9471 | 21.5311 | 21.0315 | 26.8173 | 87.2142 | 58.9859 | 38.8846 | 0.38122 | -0.053035 | 35.7715 | 22.0345 | 22.3401 | 20.1696 | 21.6493 | 22.0775 | 21.9266 | 21.7001 | 22.2323 | 21.7625 | 21.4286 | 21.2822 | 79.18 | 98.0516 | 59.3586 | 60.1547 | 35.5302 |  | 26.4698 | 56.6952 | 28.2779 | 39.9821 | 27.0091 | 33.864 |  | 34.586 |  |  | 20.8905 | 21.6638 | 32.2387 | [5 empty] | 21.8998 | 30.0839 | 21.6465 | 22.0204 | 25.1263 | 21.1481 | 21.7695 | 21.3633 | 35.4226 | 108.4065 |  | 28.6413 | 71.8188 | 19.7887 | 30.0011 | 76.7798 | 25.7358 | 60.1188 | 20.8536 | 54.8907 | 20.7806 | 56.6455 | 18.6729 | 30.6845 | 69.165 | 22.0632 | 31.2929 | 94.8954 | 19.8749 | 29.8115 | 79.456 | 19.9634 | 52.5449 | 22.5161 | 55.8066 | 20.7541 | 57.9266 | 0.18982 | 20.1441 | 0.58251 | 0.021133 | -27.0285 | 3.0957 | 65.94 | 52.45 | 1.0897 | -0.54533 | -6.5114 | 0.85587 | 0.45688 | -16.7415 | 4.7325 | 0.20527 | -0.32129 | 0.099884 | -1.6712 | -1.2425 | -0.0097298 | 0.12387
42838.4221 | 154 | 22.9018 | 22.8714 | 22.8522 | 22.7818 | 22.3929 | 21.7331 | 22.7175 | 21.7812 | 22.3639 | 22.3743 | 22.3465 | 22.0024 | 21.2115 | 22.1837 | 21.5991 | 21.771 | 21.8918 | 21.0825 | 21.1741 | 21.3865 | 20.4683 | 20.6236 | 20.9957 | 21.8658 | 21.6239 | 21.8076 | 87.4645 | 78.1643 | 95.3826 | 22.0878 | 21.6867 | 21.5002 | 21.9981 | 21.7345 | 21.7922 | 27.0874 | 85.1965 |  | 40.7509 | 67.1849 | 73.4232 | 44.6676 |  | 16.9751 | 17.0706 | 16.6415 | 16.9566 | 17.1612 | 18.6005 | 40.0993 | 15.7586 | 17.0535 | 15.7146 | 17.3656 | 18.0813 | 44.3802 | 46.9103 | 43.6382 | 21.5441 |  |  | 0.75 | -0.58096 | -30.2511 | 0.64656 | 0.099356 | -197.8296 | 15.7158 | 0.43728 | -0.10908 | -0.044157 | 0.080842 | 0.00036306 | 0.00035156 | 1.9199 | 21.7819 | 21.998 | 22.1892 | 22.25 | 22.0587 | 21.3656 | 20.1701 | 22.1939 | 22.3618 | 22.396 | 22.3358 | 21.9605 | 21.1871 | 22.2611 | 42.7534 | 28.7427 | 33.2785 | 23.6999 | 21.8563 | 24.3314 | 20.0576 | 22.3765 | 22.1413 | 21.6944 | 22.0809 | 21.7887 | 21.2884 | 21.9368 | 21.5276 | 21.0335 | 26.9007 | 87.4289 | 59.179 | 38.7219 | 0.39361 | -0.098873 | 36.0017 | 22.0449 | 22.3422 | 20.1764 | 21.6303 | 22.0843 | 21.9278 | 21.7005 | 22.2472 | 21.7666 | 21.435 | 21.3012 | 79.4038 | 98.115 | 59.5469 | 60.3585 | 35.7335 |  | 26.5522 | 57.2421 | 28.3812 | 39.8902 | 27.1028 | 33.7308 |  | 34.7247 |  |  | 20.9022 | 21.673 | 32.2314 | [5 empty] | 21.9 | 30.1548 | 21.6455 | 22.0168 | 25.1621 | 21.1545 | 21.7701 | 21.3643 | 35.5125 | 108.5568 |  | 28.7425 | 71.9852 | 19.7786 | 30.3361 | 76.9703 | 25.7628 | 60.2995 | 20.8597 | 55.0988 | 20.7841 | 56.885 | 18.6692 | 30.8971 | 69.386 | 22.0784 | 31.3401 | 95.2103 | 19.8852 | 29.8432 | 79.6164 | 19.9716 | 52.7657 | 22.5347 | 55.9628 | 20.7754 | 58.0673 | 0.26495 | 20.139 | 0.5875 | 0.02048 | -27.0434 | 3.0956 | 37.59 | 51.83 | 1.1586 | -0.90491 | -6.5298 | 0.95463 | 0.37521 | -16.7424 | 4.7189 | 0.20241 | -0.33297 | 0.10561 | -1.6028 | -1.0499 | -0.027612 | 0.13121
42838.4221 | 155 | 22.9084 | 22.8722 | 22.8707 | 22.788 | 22.4048 | 21.7303 | 22.7292 | 21.7936 | 22.3673 | 22.3727 | 22.3443 | 22.0066 | 21.2163 | 22.1844 | 21.5959 | 21.7755 | 21.8924 | 21.083 | 21.1743 | 21.3942 | 20.4673 | 20.6245 | 21.0089 | 21.868 | 21.6241 | 21.8178 | 87.6658 | 78.4311 | 95.5116 | 22.094 | 21.6937 | 21.5096 | 22.0101 | 21.7441 | 21.8045 | 27.1697 | 84.3012 |  | 40.9196 | 67.3857 | 73.6202 | 44.8153 |  | 16.9721 | 17.07 | 16.6494 | 16.9704 | 17.1627 | 18.6573 | 40.5276 | 15.675 | 17.0453 | 15.6946 | 17.3767 | 18.0872 | 44.3809 | 46.9185 | 43.6201 | 21.5483 |  |  | 0.66655 | -0.42785 | -30.2945 | 0.98891 | 0.15784 | -197.8381 | 15.9885 | 0.58973 | -0.31166 | 0.049834 | -0.0071736 | 0.0003417 | 0.00032692 | 1.9171 | 21.7919 | 22.0018 | 22.1939 | 22.2482 | 22.0639 | 21.3639 | 20.1778 | 22.1886 | 22.3638 | 22.4008 | 22.3405 | 21.97 | 21.1966 | 22.2649 | 43.0157 | 28.6958 | 30.9787 | 23.4233 | 21.8965 | 24.4442 | 20.0952 | 22.366 | 22.1396 | 21.6858 | 22.0848 | 21.7897 | 21.2878 | 21.937 | 21.5274 | 21.0416 | 26.967 | 87.5533 | 59.3263 | 38.6313 | 0.33659 | 0.029132 | 36.169 | 22.0368 | 22.3477 | 20.1756 | 21.6425 | 22.0883 | 21.9381 | 21.7018 | 22.2685 | 21.7792 | 21.4385 | 21.2993 | 79.595 | 98.1749 | 59.7504 | 60.5677 | 35.7382 |  | 26.639 | 57.4256 | 28.4511 | 39.8283 | 27.1864 | 33.6045 |  | 34.8656 |  |  | 20.9203 | 21.6903 | 32.2653 | [5 empty] | 21.8971 | 30.188 | 21.6416 | 22.0082 | 25.2058 | 21.1499 | 21.764 | 21.3833 | 35.6616 | 108.8541 |  | 28.8398 | 72.1841 | 19.7873 | 30.5295 | 77.2397 | 25.7956 | 60.5251 | 20.8789 | 55.4345 | 20.7923 | 57.117 | 18.6633 | 31.015 | 69.6131 | 22.0961 | 31.3854 | 95.4784 | 19.9033 | 29.9192 | 79.7982 | 19.98 | 52.9959 | 22.5584 | 56.1059 | 20.7942 | 58.2497 | 0.23749 | 20.135 | 0.59181 | 0.020596 | -27.0413 | 3.0956 | 51.97 | 51.27 | 1.0924 | -0.77656 | -6.5345 | 1.1806 | 0.47296 | -16.7444 | 4.7601 | 0.20522 | -0.33569 | 0.11017 | -1.6188 | -0.78999 | -0.028922 | 0.13598
42838.4221 | 156 | 22.9106 | 22.8669 | 22.858 | 22.7761 | 22.4032 | 21.7341 | 22.7173 | 21.7806 | 22.3728 | 22.3733 | 22.3431 | 21.9972 | 21.216 | 22.1763 | 21.5911 | 21.7716 | 21.8961 | 21.0803 | 21.1744 | 21.3925 | 20.4634 | 20.621 | 21.0096 | 21.8657 | 21.6201 | 21.8258 | 87.9549 | 78.7234 | 95.9033 | 22.0947 | 21.691 | 21.5179 | 22.0083 | 21.7359 | 21.8109 | 27.2465 | 84.0708 |  | 41.0794 | 67.5255 | 73.8573 | 44.6742 |  | 16.9696 | 17.0791 | 16.6503 | 16.9772 | 17.1658 | 18.6863 | 40.7006 | 15.6184 | 17.0486 | 15.65 | 17.3868 | 18.0848 | 44.3782 | 46.8943 | 43.5982 | 21.546 |  |  | 0.7408 | -0.44756 | -30.1867 | 0.84172 | 0.12038 | -197.844 | 15.7454 | 0.73035 | 0.0575 | 0.035987 | 0.074071 | 0.00033842 | 0.00036141 | 1.9178 | 21.7819 | 21.997 | 22.1924 | 22.2447 | 22.0628 | 21.3615 | 20.1751 | 22.189 | 22.3617 | 22.3993 | 22.345 | 21.9622 | 21.1994 | 22.2593 | 43.1378 | 28.8285 | 31.4084 | 23.1775 | 21.5788 | 24.548 | 20.161 | 22.3713 | 22.1412 | 21.6996 | 22.0866 | 21.7948 | 21.2904 | 21.9423 | 21.5311 | 21.0515 | 27.0392 | 87.543 | 59.4807 | 38.7432 | 0.19936 | -0.018609 | 36.1204 | 22.0309 | 22.3323 | 20.1622 | 21.6348 | 22.0836 | 21.9208 | 21.6896 | 22.2798 | 21.7674 | 21.4332 | 21.3027 | 79.7755 | 98.1631 | 59.9878 | 60.7886 | 35.6344 |  | 26.718 | 57.4264 | 28.5125 | 39.7926 | 27.2648 | 33.7005 |  | 34.9851 |  |  | 20.9333 | 21.7104 | 32.4808 | [5 empty] | 21.8979 | 30.2223 | 21.6463 | 22.0184 | 25.2255 | 21.1525 | 21.773 | 21.3896 | 35.8385 | 109.2238 |  | 28.9158 | 72.3486 | 19.7872 | 30.4953 | 77.4633 | 25.8258 | 60.7191 | 20.8807 | 55.675 | 20.8046 | 57.3419 | 18.6694 | 31.0133 | 69.8602 | 22.1085 | 31.4617 | 95.7183 | 19.9173 | 30.0291 | 80.1321 | 19.995 | 53.1738 | 22.5842 | 56.3066 | 20.8144 | 58.528 | 0.45212 | 20.1281 | 0.59606 | 0.018977 | -27.0361 | 3.0956 | 38.34 | 52.43 | 1.1523 | -0.79426 | -6.523 | 1.0892 | 0.41307 | -16.7455 | 4.724 | 0.21078 | -0.33363 | 0.11382 | -1.6202 | -0.83006 | -0.022402 | 0.13532
42838.4221 | 157 | 22.9075 | 22.876 | 22.8594 | 22.7815 | 22.4023 | 21.7382 | 22.7217 | 21.7868 | 22.3711 | 22.3696 | 22.3459 | 21.9999 | 21.2146 | 22.185 | 21.5984 | 21.7768 | 21.8979 | 21.0877 | 21.1818 | 21.3945 | 20.4767 | 20.622 | 21.0177 | 21.8679 | 21.6276 | 21.8457 | 88.1945 | 78.9781 | 96.4339 | 22.0905 | 21.6791 | 21.5184 | 21.9996 | 21.7311 | 21.8078 | 27.3071 | 83.3085 |  | 41.2083 | 67.6763 | 74.0614 | 45.004 |  | 16.9769 | 17.0803 | 16.6526 | 16.967 | 17.1609 | 18.668 | 40.9173 | 15.5694 | 17.055 | 15.6086 | 17.3843 | 18.0916 | 44.3757 | 46.8851 | 43.59 | 21.5472 |  |  | 0.73094 | -0.2386 | -29.9265 | 0.7057 | 0.10527 | -197.8749 | 16.58 | 0.42151 | 0.070928 | 0.015846 | -0.017416 | 0.00035813 | 0.00035977 | 1.9149 | 21.7742 | 21.9895 | 22.1878 | 22.2378 | 22.057 | 21.3568 | 20.1722 | 22.1857 | 22.3555 | 22.393 | 22.3467 | 21.9569 | 21.195 | 22.2525 | 43.1654 | 28.1064 | 32.525 | 23.6898 | 21.856 | 24.6589 | 20.2311 | 22.3682 | 22.1349 | 21.6946 | 22.0765 | 21.7928 | 21.287 | 21.9402 | 21.5271 | 21.0417 | 27.1037 | 87.585 | 59.6582 | 39.1862 | 0.41307 | -0.05798 | 36.2165 | 22.0233 | 22.3387 | 20.1676 | 21.6365 | 22.0762 | 21.9086 | 21.6937 | 22.3027 | 21.7524 | 21.4288 | 21.3005 | 79.9109 | 98.4712 | 60.2032 | 61.0143 | 35.7042 |  | 26.7876 | 56.9932 | 28.5818 | 39.7508 | 27.3335 | 33.6278 |  | 35.1192 |  |  | 20.9447 | 21.712 | 32.6378 | [5 empty] | 21.8964 | 30.2229 | 21.6416 | 22.0215 | 25.2456 | 21.149 | 21.7751 | 21.408 | 35.9758 | 109.3331 |  | 29.0139 | 72.6067 | 19.7896 | 30.4721 | 77.7396 | 25.8755 | 60.9176 | 20.9051 | 55.939 | 20.8161 | 57.5763 | 18.6634 | 31.0165 | 70.0445 | 22.1159 | 31.5806 | 95.7841 | 19.9236 | 30.0939 | 80.5117 | 20.0096 | 53.277 | 22.6047 | 56.5226 | 20.8256 | 58.7246 | 0.04346 | 20.1227 | 0.59987 | 0.018026 | -27.0419 | 3.0956 | 45.98 | 51.34 | 1.1454 | -0.57992 | -6.4948 | 0.99735 | 0.38626 | -16.7463 | 4.8475 | 0.21121 | -0.31924 | 0.11731 | -1.6103 | -0.94593 | -0.029506 | 0.1252
42838.4221 | 158 | 22.9123 | 22.8704 | 22.8573 | 22.7787 | 22.4001 | 21.7351 | 22.7174 | 21.7825 | 22.3656 | 22.3661 | 22.341 | 21.999 | 21.2077 | 22.1842 | 21.6001 | 21.7743 | 21.9024 | 21.0868 | 21.18 | 21.3925 | 20.4773 | 20.6255 | 21.0207 | 21.8698 | 21.6292 | 21.8568 | 88.3876 | 79.2228 | 96.2936 | 22.0996 | 21.6874 | 21.5389 | 22.0054 | 21.7388 | 21.831 | 27.3957 | 83.4839 |  | 41.3623 | 67.8523 | 74.2298 | 45.0865 |  | 16.9734 | 17.0834 | 16.6379 | 16.9699 | 17.1657 | 18.6559 | 41.2502 | 15.496 | 17.049 | 15.5523 | 17.3985 | 18.0882 | 44.3729 | 46.8762 | 43.5752 | 21.5538 |  |  | 0.71649 | -0.47056 | -29.7379 | 0.61107 | 0.079644 | -197.8611 | 16.2422 | 0.59367 | 0.11977 | 0.098717 | 0.066606 | 0.00036306 | 0.00032527 | 1.915 | 21.773 | 21.9896 | 22.185 | 22.2351 | 22.052 | 21.3623 | 20.1675 | 22.1771 | 22.3543 | 22.3904 | 22.3391 | 21.9601 | 21.1939 | 22.2525 | 44.0225 | 29.0591 | 32.3695 | 24.1304 | 22.382 | 24.7648 | 20.2873 | 22.3729 | 22.1387 | 21.6903 | 22.0754 | 21.7855 | 21.2838 | 21.9321 | 21.5237 | 21.0428 | 27.1698 | 87.7887 | 59.8313 | 39.4153 | 0.19209 | 0.032175 | 36.2332 | 22.0236 | 22.3382 | 20.166 | 21.6379 | 22.0756 | 21.9333 | 21.6982 | 22.3192 | 21.774 | 21.4425 | 21.3104 | 80.1378 | 98.4982 | 60.4469 | 61.21 | 35.8875 |  | 26.8903 | 56.9708 | 28.6672 | 39.9975 | 27.4196 | 33.5186 |  | 35.2767 |  |  | 20.9423 | 21.7256 | 32.716 | [5 empty] | 21.9012 | 30.3614 | 21.6477 | 22.027 | 25.2797 | 21.1565 | 21.7808 | 21.4219 | 36.0744 | 109.4164 |  | 29.0755 | 72.7261 | 19.8064 | 30.612 | 77.8864 | 25.9138 | 61.1583 | 20.9264 | 56.234 | 20.8347 | 57.817 | 18.6652 | 31.1187 | 70.1639 | 22.1345 | 31.6815 | 95.8644 | 19.9414 | 30.1059 | 80.7319 | 20.0241 | 53.4019 | 22.6053 | 56.6974 | 20.8418 | 58.923 | 0.24788 | 20.1166 | 0.6039 | 0.018861 | -27.0375 | 3.0956 | 52.99 | 52.73 | 1.1338 | -0.81442 | -6.4743 | 0.92808 | 0.33596 | -16.7454 | 4.7977 | 0.20959 | -0.31571 | 0.11338 | -1.6931 | -0.92208 | -0.02879 | 0.12108
42838.4221 | 159 | 22.9031 | 22.8716 | 22.8535 | 22.7723 | 22.3907 | 21.725 | 22.7112 | 21.7815 | 22.3606 | 22.3607 | 22.3375 | 21.9988 | 21.207 | 22.1759 | 21.6008 | 21.769 | 21.8993 | 21.081 | 21.1792 | 21.3804 | 20.4702 | 20.6169 | 21.0256 | 21.8625 | 21.6267 | 21.869 | 88.6768 | 79.4033 | 97.0756 | 22.096 | 21.6898 | 21.5371 | 21.9992 | 21.7394 | 21.8402 | 27.4781 | 83.2667 |  | 41.494 | 68.0527 | 74.4296 | 45.1688 |  | 16.9786 | 17.0799 | 16.6476 | 16.9669 | 17.1678 | 18.6691 | 41.8691 | 15.4696 | 17.043 | 15.5105 | 17.4064 | 18.0869 | 44.3836 | 46.8749 | 43.5583 | 21.547 |  |  | 0.66589 | -0.23663 | -29.7294 | 0.5907 | 0.16112 | -197.8709 | 15.7947 | 0.52008 | -0.012945 | -0.055276 | 0.22215 | 0.00035484 | 0.00036799 | 1.9097 | 21.7897 | 22.0009 | 22.192 | 22.248 | 22.061 | 21.3642 | 20.1755 | 22.1915 | 22.37 | 22.3951 | 22.3402 | 21.9662 | 21.1992 | 22.2629 | 43.7883 | 28.9245 | 33.1291 | 24.004 | 22.3713 | 24.8723 | 20.355 | 22.3824 | 22.1406 | 21.6973 | 22.0875 | 21.7939 | 21.2854 | 21.9436 | 21.5369 | 21.0624 | 27.2543 | 88.1567 | 60.0279 | 39.4862 | 0.087303 | -0.17533 | 36.2761 | 22.0269 | 22.3307 | 20.1585 | 21.6315 | 22.0722 | 21.9121 | 21.6884 | 22.3261 | 21.7566 | 21.4254 | 21.3167 | 80.3269 | 98.5111 | 60.6617 | 61.3894 | 35.9745 |  | 26.9522 | 57.5281 | 28.7378 | 40.4321 | 27.4923 | 33.5959 |  | 35.3991 |  |  | 20.9779 | 21.7369 | 32.8432 | [5 empty] | 21.9071 | 30.4395 | 21.6585 | 22.0275 | 25.3115 | 21.1747 | 21.7883 | 21.4364 | 36.1372 | 109.6564 |  | 29.1311 | 72.9445 | 19.8167 | 30.7623 | 78.0648 | 25.9475 | 61.3562 | 20.9472 | 56.365 | 20.8603 | 58.0256 | 18.6587 | 31.2686 | 70.3142 | 22.1456 | 31.8084 | 95.8879 | 19.9536 | 30.125 | 80.7898 | 20.0334 | 53.5145 | 22.619 | 56.8982 | 20.858 | 59.1272 | 0.17387 | 20.1109 | 0.6079 | 0.019253 | -27.0339 | 3.0956 | 52.2 | 51.7 | 1.0942 | -0.57753 | -6.4734 | 0.91248 | 0.47786 | -16.7461 | 4.7313 | 0.20928 | -0.32879 | 0.10378 | -1.6545 | -0.99858 | -0.028278 | 0.12198
42838.4221 | 160 | 22.908 | 22.8738 | 22.8562 | 22.7817 | 22.399 | 21.725 | 22.7147 | 21.7827 | 22.3643 | 22.3693 | 22.3428 | 22.0022 | 21.2125 | 22.1792 | 21.6019 | 21.7721 | 21.9029 | 21.0855 | 21.1845 | 21.3951 | 20.4813 | 20.6325 | 21.0295 | 21.8729 | 21.6337 | 21.883 | 88.8411 | 79.5713 | 96.5289 | 22.0977 | 21.6952 | 21.553 | 22.0088 | 21.7424 | 21.8485 | 27.5631 | 83.2918 |  | 41.6529 | 68.234 | 74.6198 | 45.6305 |  | 16.9642 | 17.0743 | 16.6438 | 16.9642 | 17.1618 | 18.6493 | 42.6536 | 15.4606 | 17.0397 | 15.4586 | 17.4008 | 18.0866 | 44.39 | 46.8741 | 43.54 | 21.5513 |  |  | 0.64092 | -0.24254 | -29.0236 | 0.76878 | 0.084244 | -197.8 | 16.7179 | 0.61864 | -0.11355 | 0.19627 | 0.068342 | 0.00033513 | 0.00034334 | 1.9068 | 21.7932 | 22.0016 | 22.1936 | 22.2507 | 22.0634 | 21.3671 | 20.176 | 22.1853 | 22.3626 | 22.4026 | 22.3431 | 21.9659 | 21.2047 | 22.2703 | 43.1524 | 28.6303 | 31.9265 | 23.8441 | 22.2737 | 24.9621 | 20.4091 | 22.3722 | 22.137 | 21.6906 | 22.0841 | 21.7875 | 21.2836 | 21.9354 | 21.5249 | 21.0609 | 27.3103 | 88.3387 | 60.2038 | 39.3055 | 0.20054 | 0.059183 | 36.4704 | 22.0254 | 22.3396 | 20.1623 | 21.6394 | 22.0774 | 21.9302 | 21.6921 | 22.3498 | 21.7638 | 21.4361 | 21.323 | 80.502 | 98.756 | 60.8324 | 61.5758 | 36.2459 |  | 27.0245 | 57.7312 | 28.8029 | 40.795 | 27.5678 | 33.9568 |  | 35.5117 |  |  | 20.9664 | 21.7418 | 32.6928 | [5 empty] | 21.8964 | 30.5594 | 21.647 | 22.0178 | 25.3296 | 21.1522 | 21.7807 | 21.4424 | 36.2017 | 109.9928 |  | 29.2281 | 73.1938 | 19.8136 | 30.8876 | 78.2603 | 25.9954 | 61.531 | 20.9644 | 56.4236 | 20.8629 | 58.1638 | 18.6652 | 31.3872 | 70.5349 | 22.175 | 31.9671 | 95.9455 | 19.9612 | 30.2252 | 80.9713 | 20.0427 | 53.586 | 22.6384 | 57.1757 | 20.8761 | 59.4489 | 0.30353 | 20.1042 | 0.61161 | 0.018854 | -27.0053 | 3.0956 | 35.21 | 51.84 | 1.0727 | -0.58469 | -6.396 | 1.041 | 0.34552 | -16.7426 | 4.8674 | 0.20419 | -0.33222 | 0.096259 | -1.5733 | -0.85862 | -0.038219 | 0.1289
42838.4221 | 161 | 22.9069 | 22.8679 | 22.8552 | 22.7785 | 22.4015 | 21.7259 | 22.7174 | 21.78 | 22.3674 | 22.3672 | 22.3407 | 21.9999 | 21.2094 | 22.1809 | 21.6033 | 21.7642 | 21.8928 | 21.0843 | 21.1798 | 21.3934 | 20.4713 | 20.6241 | 21.0273 | 21.8707 | 21.629 | 21.888 | 89.0367 | 79.7307 | 96.7843 | 22.0967 | 21.6919 | 21.5611 | 22.0114 | 21.7396 | 21.8624 | 27.6392 | 83.0291 |  | 41.7889 | 68.4303 | 74.7728 | 46.0042 |  | 16.9615 | 17.0812 | 16.6451 | 16.9753 | 17.1531 | 18.6321 | 43.3842 | 15.4764 | 17.0428 | 15.4486 | 17.4097 | 18.0903 | 44.4006 | 46.8593 | 43.5322 | 21.549 |  |  | 0.6672 | -0.061177 | -28.1326 | 0.61699 | 0.22618 | -197.8361 | 16.3762 | 0.52336 | 0.17679 | 0.067037 | 0.17129 | 0.00036141 | 0.00032363 | 1.9079 | 21.7829 | 22.0047 | 22.1884 | 22.2486 | 22.067 | 21.3602 | 20.1758 | 22.1915 | 22.3595 | 22.3912 | 22.339 | 21.9658 | 21.1985 | 22.2647 | 41.9637 | 27.8883 | 31.3415 | 23.7969 | 22.2343 | 25.0279 | 20.4605 | 22.3704 | 22.1392 | 21.6922 | 22.081 | 21.786 | 21.293 | 21.9365 | 21.5274 | 21.0692 | 27.3815 | 88.434 | 60.3434 | 39.4071 | 0.21155 | -0.032303 | 36.4481 | 22.0282 | 22.3358 | 20.1564 | 21.6338 | 22.0747 | 21.922 | 21.6918 | 22.3793 | 21.7701 | 21.4378 | 21.3385 | 80.6779 | 99.0363 | 61.0015 | 61.7951 | 36.4133 |  | 27.0991 | 57.8614 | 28.8751 | 40.96 | 27.6341 | 34.1242 |  | 35.6336 |  |  | 20.965 | 21.75 | 32.7074 | [5 empty] | 21.8917 | 30.6099 | 21.6448 | 22.0292 | 25.358 | 21.151 | 21.7734 | 21.4637 | 36.2873 | 110.0769 |  | 29.3134 | 73.4521 | 19.8167 | 30.9815 | 78.5353 | 26.063 | 61.6921 | 20.9746 | 56.5412 | 20.8809 | 58.3649 | 18.6648 | 31.4337 | 70.7121 | 22.1875 | 32.1 | 96.2163 | 19.9733 | 30.4036 | 81.2147 | 20.0452 | 53.7529 | 22.6636 | 57.6117 | 20.8939 | 59.6808 | 0.072955 | 20.0953 | 0.61505 | 0.018099 | -27.0253 | 3.0956 | 44.9 | 52.13 | 1.0949 | -0.29365 | -6.2971 | 0.93256 | 0.56614 | -16.7436 | 4.8173 | 0.20207 | -0.33338 | 0.093926 | -1.4335 | -0.78762 | -0.046016 | 0.12849
42838.4222 | 162 | 22.92 | 22.8795 | 22.8626 | 22.7874 | 22.3986 | 21.7354 | 22.7204 | 21.7905 | 22.378 | 22.3765 | 22.3491 | 22.0066 | 21.2189 | 22.1892 | 21.595 | 21.7724 | 21.8972 | 21.0805 | 21.1791 | 21.3967 | 20.4728 | 20.6273 | 21.0291 | 21.8714 | 21.6256 | 21.8997 | 89.2744 | 79.8428 | 96.7935 | 22.1037 | 21.6968 | 21.5669 | 22.0135 | 21.7447 | 21.8746 | 27.7117 | 82.799 |  | 41.9232 | 68.6343 | 74.9255 | 46.297 |  | 16.9748 | 17.0862 | 16.652 | 16.9774 | 17.1661 | 18.6086 | 44.0197 | 15.4976 | 17.0474 | 15.4677 | 17.4127 | 18.0925 | 44.4131 | 46.848 | 43.5196 | 21.552 |  |  | 0.56207 | -0.30825 | -27.3467 | 0.7011 | 0.010644 | -197.7967 | 17.3034 | 0.82958 | 0.14663 | 0.20047 | 0.11001 | 0.00033842 | 0.0002957 | 1.9035 | 21.7828 | 21.999 | 22.1973 | 22.2469 | 22.0552 | 21.3627 | 20.1796 | 22.1907 | 22.361 | 22.3999 | 22.3465 | 21.9649 | 21.1987 | 22.2697 | 41.2262 | 28.0195 | 31.4773 | 24.0017 | 22.176 | 25.1134 | 20.5179 | 22.3723 | 22.1349 | 21.6996 | 22.0798 | 21.7878 | 21.2879 | 21.9437 | 21.5298 | 21.0751 | 27.4526 | 88.4386 | 60.4929 | 39.6154 | 0.36313 | -0.074908 | 36.2932 | 22.0338 | 22.3322 | 20.1652 | 21.6357 | 22.0799 | 21.93 | 21.6959 | 22.3941 | 21.7691 | 21.4387 | 21.34 | 80.8694 | 99.2338 | 61.1835 | 62.0046 | 36.3738 |  | 27.1798 | 57.5795 | 28.9647 | 41.1917 | 27.7253 | 34.1271 |  | 35.7626 |  |  | 20.9636 | 21.7548 | 32.7244 | [5 empty] | 21.893 | 30.6953 | 21.6393 | 22.0158 | 25.3948 | 21.154 | 21.7744 | 21.4663 | 36.4119 | 109.821 |  | 29.3947 | 73.7208 | 19.818 | 31.0213 | 78.7366 | 26.098 | 61.8483 | 20.9907 | 56.5919 | 20.8879 | 58.539 | 18.6433 | 31.4384 | 70.8862 | 22.195 | 32.2042 | 96.5245 | 19.9746 | 30.5374 | 81.3975 | 20.0401 | 53.9596 | 22.6807 | 57.807 | 20.9099 | 59.8326 | 0.30594 | 20.0937 | 0.6185 | 0.017693 | -27.0196 | 3.0956 | 45.01 | 51.73 | 1.0049 | -0.65917 | -6.2086 | 0.9941 | 0.12281 | -16.7413 | 4.9516 | 0.2059 | -0.3225 | 0.090586 | -1.3416 | -0.79601 | -0.05169 | 0.12511
42838.4222 | 163 | 22.9105 | 22.8771 | 22.8634 | 22.7798 | 22.3968 | 21.7372 | 22.7211 | 21.7842 | 22.3616 | 22.3707 | 22.347 | 22.0017 | 21.217 | 22.1846 | 21.5993 | 21.773 | 21.9046 | 21.0865 | 21.1887 | 21.399 | 20.4706 | 20.629 | 21.039 | 21.8716 | 21.6285 | 21.9204 | 89.4322 | 80.0249 | 96.6788 | 22.0942 | 21.6948 | 21.5691 | 21.9993 | 21.7481 | 21.8725 | 27.7885 | 82.7587 |  | 42.0615 | 68.814 | 75.135 | 46.7176 |  | 16.9677 | 17.0779 | 16.6492 | 16.974 | 17.1681 | 18.606 | 44.1208 | 15.5551 | 17.0428 | 15.4522 | 17.4167 | 18.09 | 44.4186 | 46.8356 | 43.5028 | 21.5523 |  |  | 0.60149 | -0.27408 | -27.5412 | 0.64787 | 0.20844 | -197.8591 | 16.9887 | 0.5503 | -0.0039932 | 0.00137 | 0.035185 | 0.0003532 | 0.00030885 | 1.8938 | 21.7749 | 22.0025 | 22.1911 | 22.2406 | 22.0589 | 21.3585 | 20.1751 | 22.1875 | 22.3566 | 22.3968 | 22.3448 | 21.9617 | 21.1964 | 22.2652 | 41.334 | 28.5899 | 32.6562 | 24.494 | 22.2687 | 25.2107 | 20.5739 | 22.3704 | 22.139 | 21.6971 | 22.0831 | 21.7856 | 21.2885 | 21.9457 | 21.5416 | 21.0848 | 27.5261 | 88.9096 | 61.1229 | 39.6705 | 0.39223 | -0.068061 | 36.4904 | 22.0345 | 22.3411 | 20.1543 | 21.6338 | 22.0706 | 21.9272 | 21.6902 | 22.4168 | 21.7695 | 21.4304 | 21.3489 | 81.0453 | 99.6992 | 61.3524 | 62.1917 | 36.3104 |  | 27.2468 | 57.4296 | 29.0289 | 41.3357 | 27.7973 | 34.5421 |  | 35.8759 |  |  | 20.9749 | 21.775 | 32.7133 | [5 empty] | 21.8933 | 30.8112 | 21.6477 | 22.0301 | 25.4055 | 21.1568 | 21.7774 | 21.4646 | 36.5387 | 109.7454 |  | 29.4492 | 73.9222 | 19.8074 | 31.0979 | 78.8793 | 26.1476 | 61.9883 | 20.9998 | 56.7108 | 20.8969 | 58.644 | 18.6415 | 31.5473 | 71.0818 | 22.2106 | 32.2364 | 96.6807 | 20.0019 | 30.6755 | 81.5683 | 20.0689 | 54.1572 | 22.6998 | 57.9817 | 20.9358 | 59.9634 | 0.18722 | 20.0859 | 0.62082 | 0.016618 | -27.0444 | 3.0956 | 31.59 | 52.83 | 1.0394 | -0.62155 | -6.2306 | 0.95561 | 0.54345 | -16.7438 | 4.9063 | 0.20994 | -0.31615 | 0.089033 | -1.3422 | -0.92045 | -0.060764 | 0.12608
42838.4222 | 164 | 22.9141 | 22.8811 | 22.8669 | 22.7704 | 22.3982 | 21.736 | 22.7234 | 21.7911 | 22.3632 | 22.3727 | 22.3528 | 22.0095 | 21.2129 | 22.1791 | 21.6003 | 21.7749 | 21.9008 | 21.086 | 21.1768 | 21.3957 | 20.4722 | 20.63 | 21.0436 | 21.8732 | 21.6302 | 21.9313 | 89.5381 | 80.2668 | 96.2894 | 22.1022 | 21.6933 | 21.5786 | 22.0011 | 21.7373 | 21.8835 | 27.8727 | 83.2524 |  | 42.201 | 68.9862 | 75.3375 | 46.9714 |  | 16.9698 | 17.0834 | 16.6467 | 16.973 | 17.1865 | 18.6284 | 44.0933 | 15.5483 | 17.0389 | 15.4827 | 17.4167 | 18.0997 | 44.4159 | 46.8278 | 43.4883 | 21.5543 |  |  | 0.79863 | -0.28 | -27.2277 | 0.3732 | 0.1953 | -197.8512 | 17.2601 | 0.44122 | 0.070344 | 0.086339 | 0.19004 | 0.00035813 | 0.00034992 | 1.8929 | 21.7734 | 22.0007 | 22.1883 | 22.2423 | 22.0588 | 21.3581 | 20.1706 | 22.1814 | 22.3578 | 22.3938 | 22.3442 | 21.9602 | 21.1953 | 22.2631 | 41.2025 | 28.2541 | 31.5607 | 24.6868 | 22.6252 | 25.3056 | 20.627 | 22.3797 | 22.1412 | 21.6975 | 22.0896 | 21.7964 | 21.3018 | 21.9498 | 21.5499 | 21.09 | 27.612 | 89.3455 | 61.4967 | 39.7415 | 0.12603 | -0.20596 | 36.4314 | 22.0168 | 22.3304 | 20.1477 | 21.6234 | 22.0635 | 21.9199 | 21.6925 | 22.433 | 21.7581 | 21.4301 | 21.3439 | 81.2985 | 100.1308 | 61.5016 | 62.331 | 36.3147 |  | 27.3171 | 57.4878 | 29.1018 | 41.5085 | 27.8833 | 34.6434 |  | 35.9971 |  |  | 20.9838 | 21.7789 | 32.7926 | [5 empty] | 21.8918 | 30.8786 | 21.648 | 22.0205 | 25.4365 | 21.1557 | 21.7768 | 21.4793 | 36.6715 | 109.5905 |  | 29.496 | 74.0964 | 19.8154 | 31.2724 | 79.0538 | 26.2075 | 62.1689 | 21.0147 | 56.8871 | 20.912 | 58.7729 | 18.6346 | 31.7686 | 71.2688 | 22.2242 | 32.2691 | 96.8055 | 20.0078 | 30.8047 | 81.7167 | 20.0725 | 54.3428 | 22.7151 | 58.3619 | 20.9475 | 60.097 | 0.18296 | 20.0805 | 0.62331 | 0.016858 | -27.1296 | 3.0956 | 32.47 | 51.8 | 1.197 | -0.62823 | -6.1951 | 0.72529 | 0.52607 | -16.7441 | 4.9456 | 0.2122 | -0.31528 | 0.087153 | -1.3164 | -0.79252 | -0.064955 | 0.12703
42838.4222 | 165 | 22.9078 | 22.8747 | 22.855 | 22.772 | 22.4 | 21.7314 | 22.7152 | 21.7803 | 22.3632 | 22.3597 | 22.3403 | 21.9917 | 21.2152 | 22.1757 | 21.6095 | 21.7752 | 21.9017 | 21.0895 | 21.184 | 21.3925 | 20.4787 | 20.6328 | 21.0474 | 21.8744 | 21.628 | 21.9422 | 89.6466 | 80.4771 | 96.0794 | 22.105 | 21.6889 | 21.592 | 22.0094 | 21.7467 | 21.9016 | 27.9537 | 83.2424 |  | 42.3367 | 69.1023 | 75.5506 | 46.9382 |  | 16.9659 | 17.0869 | 16.6507 | 16.9812 | 17.2236 | 18.6593 | 44.4004 | 15.4743 | 17.0339 | 15.5649 | 17.4218 | 18.0973 | 44.3937 | 46.8157 | 43.4719 | 21.5528 |  |  | 0.83083 | -0.18012 | -27.2396 | 0.52762 | 0.0849 | -197.8434 | 17.4533 | 0.56082 | -0.10655 | 0.1155 | 0.053934 | 0.00032856 | 0.00034006 | 1.8945 | 21.7791 | 21.9939 | 22.1904 | 22.2459 | 22.0614 | 21.3591 | 20.1731 | 22.1777 | 22.3527 | 22.3972 | 22.3359 | 21.9588 | 21.1898 | 22.2605 | 39.7606 | 26.645 | 29.6497 | 24.2132 | 22.4274 | 25.3727 | 20.6526 | 22.3712 | 22.1371 | 21.6906 | 22.0827 | 21.7914 | 21.2907 | 21.9426 | 21.533 | 21.0817 | 27.6751 | 89.5332 | 61.6528 | 40.1272 | -0.077252 | 0.0026938 | 36.4634 | 22.0252 | 22.3271 | 20.1575 | 21.6295 | 22.0667 | 21.9167 | 21.6925 | 22.4451 | 21.76 | 21.4258 | 21.3577 | 81.4599 | 100.3244 | 61.6503 | 62.4804 | 36.2952 |  | 27.3759 | 57.8127 | 29.1875 | 41.6462 | 27.9873 | 34.5008 |  | 36.1378 |  |  | 20.9848 | 21.7748 | 32.7624 | [5 empty] | 21.8962 | 30.9458 | 21.6532 | 22.0247 | 25.4668 | 21.1617 | 21.7817 | 21.4817 | 36.7846 | 109.8831 |  | 29.6214 | 74.303 | 19.8094 | 31.415 | 79.2003 | 26.2302 | 62.325 | 21.0263 | 57.0816 | 20.9202 | 58.9915 | 18.626 | 31.9516 | 71.3962 | 22.2371 | 32.3866 | 96.99 | 19.9992 | 30.9106 | 81.8727 | 20.0634 | 54.511 | 22.727 | 58.7346 | 20.9562 | 60.2438 | 0.33358 | 20.0767 | 0.62603 | 0.017104 | -27.1352 | 3.0956 | 37.28 | 51.71 | 1.2206 | -0.50387 | -6.1965 | 0.86239 | 0.34687 | -16.7447 | 4.9734 | 0.21474 | -0.32139 | 0.086861 | -1.1484 | -0.57719 | -0.061281 | 0.11845
42838.4222 | 166 | 22.9052 | 22.875 | 22.8524 | 22.7713 | 22.3991 | 21.7322 | 22.7119 | 21.7782 | 22.3695 | 22.3669 | 22.3413 | 21.9963 | 21.2165 | 22.1816 | 21.6057 | 21.775 | 21.9003 | 21.0875 | 21.1906 | 21.3931 | 20.4726 | 20.6318 | 21.0484 | 21.8747 | 21.6273 | 21.9518 | 89.8696 | 80.6254 | 96.806 | 22.1005 | 21.6877 | 21.588 | 22.011 | 21.739 | 21.9158 | 28.0174 | 82.7899 |  | 42.4698 | 69.2421 | 75.7503 | 46.839 |  | 16.9724 | 17.0932 | 16.6606 | 16.9972 | 17.2747 | 18.6823 | 43.9839 | 15.4837 | 17.0374 | 15.629 | 17.4299 | 18.0939 | 44.3685 | 46.8136 | 43.4568 | 21.5531 |  |  | 0.75329 | -0.38448 | -27.5103 | 0.31603 | 0.1861 | -197.8309 | 17.3396 | 0.75664 | 0.078128 | -0.058843 | 0.091778 | 0.00035977 | 0.00036963 | 1.8924 | 21.7884 | 21.9899 | 22.1941 | 22.2438 | 22.0575 | 21.3573 | 20.1807 | 22.1829 | 22.3612 | 22.3917 | 22.3399 | 21.9576 | 21.1886 | 22.2596 | 38.641 | 25.0579 | 28.0794 | 23.4407 | 22.0053 | 25.4258 | 20.6806 | 22.3725 | 22.129 | 21.6901 | 22.0821 | 21.7897 | 21.2881 | 21.9476 | 21.5313 | 21.0902 | 27.7554 | 89.5534 | 61.7942 | 40.9258 | 0.1164 | -0.10249 | 36.4932 | 22.0348 | 22.3328 | 20.1607 | 21.632 | 22.0707 | 21.9277 | 21.6914 | 22.4693 | 21.7662 | 21.4312 | 21.3731 | 81.6914 | 100.4984 | 61.8258 | 62.6535 | 36.0693 |  | 27.4458 | 57.8451 | 29.2818 | 41.5171 | 28.0782 | 34.5686 |  | 36.263 |  |  | 20.9954 | 21.7818 | 32.8378 | [5 empty] | 21.9007 | 31.034 | 21.6595 | 22.0331 | 25.4807 | 21.1654 | 21.7819 | 21.5024 | 36.9015 | 110.3643 |  | 29.9289 | 74.5182 | 19.8184 | 31.4964 | 79.2931 | 26.2516 | 62.4538 | 21.0445 | 57.2622 | 20.9418 | 59.3066 | 18.6133 | 32.0825 | 71.5516 | 22.2547 | 32.5623 | 97.1927 | 20.0016 | 31.0451 | 82.0688 | 20.0568 | 54.6483 | 22.7484 | 58.9684 | 20.9667 | 60.4222 | 0.2106 | 20.0727 | 0.62919 | 0.018339 | -27.1111 | 3.0956 | 27.78 | 52.36 | 1.1634 | -0.73618 | -6.2272 | 0.66744 | 0.51357 | -16.7448 | 4.9574 | 0.22339 | -0.31908 | 0.093535 | -1.0177 | -0.39944 | -0.056362 | 0.098994
42838.4222 | 167 | 22.9004 | 22.8705 | 22.8526 | 22.7787 | 22.4018 | 21.7305 | 22.7206 | 21.7857 | 22.3684 | 22.371 | 22.3405 | 21.9963 | 21.2121 | 22.1798 | 21.6023 | 21.7749 | 21.9049 | 21.0834 | 21.1856 | 21.3976 | 20.4766 | 20.6321 | 21.0524 | 21.8728 | 21.6283 | 21.9614 | 90.0748 | 80.7968 | 97.2269 | 22.0965 | 21.689 | 21.5975 | 22.0066 | 21.7346 | 21.9218 | 28.0924 | 83.3216 |  | 42.6102 | 69.3756 | 75.9116 | 46.3993 |  | 16.9739 | 17.0974 | 16.6538 | 16.9888 | 17.2753 | 18.6763 | 43.5298 | 15.5325 | 17.0373 | 15.6591 | 17.4381 | 18.0898 | 44.3459 | 46.8054 | 43.4572 | 21.5534 |  |  | 0.59952 | -0.28591 | -27.4788 | 0.30026 | 0.30963 | -197.8066 | 17.4105 | 0.62981 | 0.06723 | -0.084228 | 0.093514 | 0.00036141 | 0.00035156 | 1.8943 | 21.7786 | 21.9936 | 22.1804 | 22.2394 | 22.0565 | 21.3585 | 20.1824 | 22.1818 | 22.3567 | 22.4026 | 22.3368 | 21.9596 | 21.1879 | 22.2537 | 38.3543 | 23.9323 | 26.8009 | 22.991 | 21.3869 | 25.4762 | 20.6893 | 22.363 | 22.1245 | 21.6789 | 22.0733 | 21.783 | 21.2897 | 21.9421 | 21.5304 | 21.0893 | 27.8442 | 89.7575 | 61.9763 | 41.763 | 0.24065 | -0.053605 | 36.5957 | 22.033 | 22.3405 | 20.1622 | 21.6351 | 22.0713 | 21.9304 | 21.6962 | 22.4948 | 21.7662 | 21.4374 | 21.3823 | 81.9763 | 100.6881 | 61.9641 | 62.8155 | 35.9976 |  | 27.5055 | 57.4355 | 29.3611 | 41.2764 | 28.1543 | 34.6426 |  | 36.3849 |  |  | 21.0004 | 21.7989 | 32.9059 | [5 empty] | 21.9008 | 31.065 | 21.6528 | 22.0309 | 25.4991 | 21.1605 | 21.7824 | 21.5074 | 37.0459 | 110.4006 |  | 30.163 | 74.702 | 19.8256 | 31.5127 | 79.412 | 26.2875 | 62.5968 | 21.056 | 57.4992 | 20.9535 | 59.6188 | 18.6145 | 32.1735 | 71.7778 | 22.2756 | 32.6987 | 97.4984 | 20.0106 | 31.2189 | 82.2912 | 20.0568 | 54.8316 | 22.7752 | 59.0845 | 20.9886 | 60.6543 | 0.33173 | 20.0664 | 0.63255 | 0.019079 | -27.053 | 3.0956 | 27.37 | 51.61 | 1.0385 | -0.63484 | -6.2237 | 0.65058 | 0.66245 | -16.7436 | 4.9675 | 0.22741 | -0.305 | 0.10281 | -0.97998 | -0.25638 | -0.041599 | 0.078755
42838.4222 | 168 | 22.906 | 22.8709 | 22.8585 | 22.7778 | 22.4013 | 21.7248 | 22.7162 | 21.789 | 22.3628 | 22.3725 | 22.3449 | 21.9946 | 21.2144 | 22.1771 | 21.6079 | 21.7741 | 21.8988 | 21.0833 | 21.1873 | 21.3966 | 20.4728 | 20.6299 | 21.0589 | 21.867 | 21.6212 | 21.9758 | 90.1322 | 80.9505 | 96.9117 | 22.0945 | 21.6861 | 21.611 | 22.0071 | 21.735 | 21.9284 | 28.1662 | 83.1419 |  | 42.7527 | 69.4744 | 76.0225 | 46.0168 |  | 16.9759 | 17.0983 | 16.6541 | 16.9841 | 17.2716 | 18.6522 | 43.7767 | 15.6061 | 17.0459 | 15.6214 | 17.4378 | 18.094 | 44.3161 | 46.7948 | 43.4393 | 21.5495 |  |  | 0.72437 | -0.28591 | -27.2107 | 0.13007 | 0.31752 | -197.8197 | 17.6307 | 0.67121 | -0.090006 | 0.13963 | 0.15688 | 0.00033184 | 0.00034827 | 1.898 | 21.7853 | 22.0059 | 22.1888 | 22.2445 | 22.061 | 21.3639 | 20.1838 | 22.1856 | 22.368 | 22.4002 | 22.3487 | 21.9754 | 21.1968 | 22.2679 | 38.0471 | 23.3526 | 25.2235 | 22.6527 | 21.2046 | 25.5379 | 20.7057 | 22.3602 | 22.1327 | 21.6813 | 22.0717 | 21.791 | 21.2865 | 21.941 | 21.5297 | 21.091 | 27.9293 | 90.1401 | 62.1621 | 41.8055 | -0.059164 | -0.062355 | 36.6478 | 22.0178 | 22.3193 | 20.1562 | 21.6218 | 22.0689 | 21.9185 | 21.6928 | 22.5059 | 21.7521 | 21.4271 | 21.3824 | 82.1744 | 100.816 | 62.0804 | 62.9509 | 36.2292 |  | 27.5774 | 57.488 | 29.465 | 41.1269 | 28.2519 | 34.6631 |  | 36.5402 |  |  | 21.003 | 21.8013 | 32.9937 | [5 empty] | 21.8979 | 31.0509 | 21.6478 | 22.0208 | 25.5042 | 21.1555 | 21.7779 | 21.5073 | 37.2219 | 110.2795 |  | 30.2586 | 75.0125 | 19.835 | 31.5563 | 79.5407 | 26.3175 | 62.7379 | 21.0658 | 57.6908 | 20.9645 | 59.8832 | 18.6119 | 32.2583 | 71.9628 | 22.2785 | 32.7636 | 97.7634 | 20.0058 | 31.389 | 82.4614 | 20.057 | 55.0482 | 22.7867 | 59.2041 | 21.003 | 60.8257 | 0.30168 | 20.0619 | 0.63636 | 0.019282 | -26.9942 | 3.0956 | 25.13 | 52.83 | 1.141 | -0.63484 | -6.1933 | 0.42819 | 0.67081 | -16.7435 | 4.9986 | 0.22342 | -0.30292 | 0.11028 | -0.93862 | -0.079188 | -0.028467 | 0.080465
42838.4222 | 169 | 22.9187 | 22.8748 | 22.8669 | 22.7824 | 22.4008 | 21.7289 | 22.7227 | 21.7906 | 22.364 | 22.3758 | 22.3484 | 21.9974 | 21.2225 | 22.1809 | 21.6075 | 21.7781 | 21.9009 | 21.0863 | 21.1909 | 21.3928 | 20.4727 | 20.6262 | 21.0647 | 21.8692 | 21.6295 | 21.9952 | 90.2988 | 81.0851 | 97.21 | 22.1027 | 21.6878 | 21.6239 | 22.0094 | 21.7411 | 21.9447 | 28.2464 | 82.8471 |  | 42.9019 | 69.5642 | 76.1383 | 46.29 |  | 16.9701 | 17.0901 | 16.645 | 16.971 | 17.2589 | 18.6181 | 44.1436 | 15.6328 | 17.0364 | 15.5885 | 17.4383 | 18.0974 | 44.2736 | 46.7891 | 43.4237 | 21.5505 |  |  | 0.85119 | -0.38185 | -27.2028 | 0.36663 | 0.19135 | -197.8394 | 17.7312 | 0.6561 | 0.23634 | -0.017302 | 0.05619 | 0.00032199 | 0.00035813 | 1.9021 | 21.7785 | 21.9938 | 22.1857 | 22.2386 | 22.0641 | 21.362 | 20.1727 | 22.1853 | 22.3625 | 22.3963 | 22.3449 | 21.9668 | 21.1965 | 22.2667 | 37.222 | 23.1589 | 23.9711 | 22.0801 | 21.022 | 25.5789 | 20.715 | 22.3687 | 22.1352 | 21.6904 | 22.0842 | 21.7855 | 21.2886 | 21.9418 | 21.5374 | 21.1038 | 28.0183 | 90.3482 | 62.395 | 41.5122 | 0.088482 | -0.037438 | 36.7778 | 22.0162 | 22.3343 | 20.1609 | 21.6245 | 22.0662 | 21.9228 | 21.6893 | 22.5283 | 21.7518 | 21.4292 | 21.3878 | 82.352 | 101.0609 | 62.2451 | 63.1282 | 36.852 |  | 27.638 | 57.6308 | 29.5376 | 41.1599 | 28.329 | 34.6955 |  | 36.67 |  |  | 21.0125 | 21.8012 | 33.1478 | [5 empty] | 21.8921 | 31.0514 | 21.6487 | 22.0157 | 25.5151 | 21.1578 | 21.7784 | 21.5063 | 37.387 | 110.3155 |  | 30.3 | 75.2713 | 19.8443 | 31.6536 | 79.6408 | 26.3532 | 62.8912 | 21.0695 | 57.8401 | 20.9822 | 60.1534 | 18.602 | 32.37 | 72.1385 | 22.302 | 32.8111 | 97.9495 | 20.0061 | 31.5255 | 82.548 | 20.0492 | 55.2452 | 22.8052 | 59.4636 | 21.0147 | 60.9826 | 0.28758 | 20.0577 | 0.63983 | 0.019362 | -27.0453 | 3.0956 | 31.49 | 51.44 | 1.2374 | -0.73365 | -6.1923 | 0.71888 | 0.52072 | -16.7433 | 5.0125 | 0.20817 | -0.30442 | 0.11198 | -0.84213 | 0.061054 | -0.033331 | 0.091634
42838.4222 | 170 | 22.9093 | 22.8729 | 22.864 | 22.7769 | 22.3949 | 21.7328 | 22.7161 | 21.7866 | 22.3607 | 22.374 | 22.3431 | 22.003 | 21.2121 | 22.1756 | 21.6106 | 21.7726 | 21.9069 | 21.093 | 21.1823 | 21.4012 | 20.4723 | 20.6344 | 21.0627 | 21.867 | 21.6383 | 22.0075 | 90.5192 | 81.2275 | 97.2461 | 22.114 | 21.6942 | 21.6386 | 22.0104 | 21.7496 | 21.9624 | 28.3571 | 83.4959 |  | 43.038 | 69.6687 | 76.3158 | 46.7837 |  | 16.9698 | 17.0934 | 16.6382 | 16.9734 | 17.2523 | 18.6075 | 44.9016 | 15.6532 | 17.0397 | 15.5953 | 17.4361 | 18.0989 | 44.2409 | 46.7846 | 43.4177 | 21.5551 |  |  | 0.76117 | -0.33716 | -27.0194 | 0.27595 | 0.19004 | -197.7914 | 17.8994 | 0.52993 | 0.28051 | 0.11466 | 0.13744 | 0.00038606 | 0.00032199 | 1.9037 | 21.7758 | 21.995 | 22.1861 | 22.2407 | 22.059 | 21.3528 | 20.171 | 22.1847 | 22.354 | 22.3961 | 22.3455 | 21.9643 | 21.1954 | 22.2594 | 36.9469 | 22.4929 | 22.8367 | 21.457 | 20.5532 | 25.6328 | 20.7108 | 22.3788 | 22.1409 | 21.6952 | 22.0869 | 21.7924 | 21.2932 | 21.9466 | 21.5382 | 21.112 | 28.098 | 90.5722 | 62.5301 | 41.3879 | 0.31791 | 0.096653 | 36.7655 | 22.022 | 22.331 | 20.159 | 21.6296 | 22.068 | 21.9217 | 21.6982 | 22.5429 | 21.7634 | 21.4276 | 21.3898 | 82.5365 | 101.201 | 62.3809 | 63.2999 | 37.1221 |  | 27.7031 | 57.4737 | 29.6045 | 41.2744 | 28.395 | 34.685 |  | 36.779 |  |  | 21.0321 | 21.822 | 33.1356 | [5 empty] | 21.9025 | 31.0639 | 21.6522 | 22.0276 | 25.5407 | 21.1608 | 21.7888 | 21.5148 | 37.5296 | 110.3814 |  | 30.3741 | 75.4832 | 19.8532 | 31.7773 | 79.796 | 26.3892 | 63.0279 | 21.0837 | 58.0493 | 20.9903 | 60.3448 | 18.6063 | 32.498 | 72.3595 | 22.3393 | 32.9409 | 98.097 | 20.0129 | 31.6652 | 82.6746 | 20.0618 | 55.426 | 22.8336 | 59.7052 | 21.0416 | 61.0866 | 0.13769 | 20.0541 | 0.64424 | 0.019943 | -27.0404 | 3.0956 | 43.45 | 52.13 | 1.1701 | -0.6894 | -6.1714 | 0.62368 | 0.51892 | -16.741 | 5.0361 | 0.20288 | -0.29777 | 0.11104 | -0.80525 | 0.1866 | -0.043281 | 0.097798
42838.4223 | 171 | 22.9167 | 22.8787 | 22.871 | 22.7921 | 22.4108 | 21.7429 | 22.7301 | 21.798 | 22.3756 | 22.3781 | 22.3539 | 22.0068 | 21.2175 | 22.1928 | 21.6079 | 21.7779 | 21.9078 | 21.0949 | 21.1832 | 21.4001 | 20.4782 | 20.6356 | 21.0667 | 21.8656 | 21.6308 | 22.0227 | 90.6195 | 81.3954 | 97.2484 | 22.0933 | 21.6916 | 21.6392 | 22.0042 | 21.7412 | 21.9554 | 28.4339 | 84.1788 |  | 43.1561 | 69.7468 | 76.4511 | 46.9655 |  | 16.9704 | 17.0925 | 16.6328 | 16.966 | 17.2411 | 18.5836 | 45.5307 | 15.6967 | 17.0361 | 15.617 | 17.4377 | 18.1032 | 44.2031 | 46.7891 | 43.4084 | 21.5499 |  |  | 0.78023 | -0.21494 | -27.3013 | 0.49148 | 0.12827 | -197.8486 | 17.747 | 0.59893 | -0.14119 | -0.02968 | 0.096813 | 0.00033513 | 0.00033184 | 1.8989 | 21.78 | 21.9954 | 22.1914 | 22.246 | 22.0641 | 21.3606 | 20.1759 | 22.1846 | 22.3569 | 22.3983 | 22.3508 | 21.974 | 21.1943 | 22.2649 | 37.5022 | 23.1165 | 22.6726 | 20.8908 | 20.088 | 25.6974 | 20.7133 | 22.373 | 22.1402 | 21.6969 | 22.0856 | 21.7874 | 21.2978 | 21.9456 | 21.5387 | 21.1231 | 28.1845 | 90.8074 | 62.6529 | 41.4548 | 0.42152 | -0.037438 | 36.6823 | 22.0239 | 22.3334 | 20.171 | 21.6327 | 22.0765 | 21.9308 | 21.7042 | 22.5686 | 21.7679 | 21.435 | 21.4062 | 82.7581 | 101.3877 | 62.5021 | 63.4675 | 37.2091 |  | 27.7855 | 56.9129 | 29.7101 | 41.354 | 28.4924 | 35.002 |  | 36.899 |  |  | 21.0358 | 21.8307 | 33.1083 | [5 empty] | 21.8988 | 31.0445 | 21.6462 | 22.0225 | 25.5697 | 21.1517 | 21.7855 | 21.5284 | 37.6662 | 110.6562 |  | 30.4546 | 75.7518 | 19.8695 | 31.8536 | 79.9725 | 26.4127 | 63.1668 | 21.0953 | 58.2652 | 21.0017 | 60.4506 | 18.608 | 32.6133 | 72.5202 | 22.3432 | 33.0825 | 98.151 | 20.0267 | 31.8014 | 82.8167 | 20.0749 | 55.5712 | 22.8682 | 59.8766 | 21.0561 | 61.2274 | 0.27775 | 20.0505 | 0.64837 | 0.021235 | -27.0942 | 3.0956 | 22.43 | 52.01 | 1.1847 | -0.55044 | -6.2035 | 0.83234 | 0.4263 | -16.7427 | 5.0144 | 0.20326 | -0.2786 | 0.11214 | -0.85939 | 0.20513 | -0.045718 | 0.098878
42838.4223 | 172 | 22.9127 | 22.878 | 22.8623 | 22.7877 | 22.4046 | 21.7343 | 22.7274 | 21.7905 | 22.3695 | 22.3712 | 22.348 | 22.0021 | 21.2146 | 22.1795 | 21.6129 | 21.7837 | 21.9045 | 21.0865 | 21.1885 | 21.4094 | 20.4795 | 20.6416 | 21.0829 | 21.8788 | 21.6368 | 22.0371 | 90.7023 | 81.551 | 97.165 | 22.0972 | 21.6935 | 21.6411 | 22.0016 | 21.7419 | 21.971 | 28.5125 | 85.5275 |  | 43.2905 | 69.8732 | 76.52 | 46.324 |  | 16.9717 | 17.0854 | 16.6368 | 16.9688 | 17.2264 | 18.55 | 45.6626 | 15.7075 | 17.0299 | 15.6329 | 17.441 | 18.1002 | 44.1725 | 46.7859 | 43.3957 | 21.5524 |  |  | 0.90771 | -0.24846 | -27.0759 | 0.3456 | 0.21764 | -197.8335 | 18.1399 | 0.32688 | 0.0035962 | 0.039973 | -0.02436 | 0.00032856 | 0.00033184 | 1.8943 | 21.78 | 21.9968 | 22.1898 | 22.2417 | 22.0615 | 21.3644 | 20.1748 | 22.1875 | 22.3625 | 22.397 | 22.3427 | 21.9674 | 21.1968 | 22.2707 | 39.0435 | 24.7901 | 24.7204 | 20.8313 | 19.725 | 25.7923 | 20.744 | 22.3665 | 22.1325 | 21.6919 | 22.0823 | 21.7893 | 21.2895 | 21.9478 | 21.5352 | 21.1212 | 28.2589 | 90.9924 | 62.8132 | 41.4651 | 0.34819 | -0.27043 | 36.7964 | 22.0211 | 22.3274 | 20.1596 | 21.6318 | 22.0664 | 21.923 | 21.701 | 22.5855 | 21.7603 | 21.4367 | 21.4089 | 82.9564 | 101.6067 | 62.6338 | 63.6873 | 36.9985 |  | 27.853 | 57.3741 | 29.7891 | 41.6641 | 28.567 | 35.0549 |  | 37.027 |  |  | 21.0361 | 21.8284 | 33.2746 | [5 empty] | 21.8927 | 31.0347 | 21.6432 | 22.0231 | 25.609 | 21.1554 | 21.781 | 21.5373 | 37.7799 | 110.8632 |  | 30.5131 | 76.0066 | 19.8907 | 31.9785 | 80.1259 | 26.4563 | 63.3073 | 21.097 | 58.4038 | 21.0272 | 60.5651 | 18.6073 | 32.6678 | 72.6647 | 22.3586 | 33.1797 | 98.1799 | 20.0349 | 31.9203 | 82.945 | 20.0875 | 55.6469 | 22.8995 | 60.0084 | 21.0729 | 61.4404 | 0.05997 | 20.0474 | 0.65195 | 0.022048 | -27.0008 | 3.0956 | 34.38 | 51.49 | 1.2777 | -0.59179 | -6.1778 | 0.69796 | 0.55527 | -16.7411 | 5.0694 | 0.2114 | -0.28871 | 0.10607 | -1.0195 | -0.018819 | -0.025227 | 0.10112
42838.4223 | 173 | 22.9062 | 22.8734 | 22.8591 | 22.7773 | 22.3968 | 21.7305 | 22.7167 | 21.7879 | 22.3588 | 22.3649 | 22.34 | 21.9982 | 21.2058 | 22.1799 | 21.6038 | 21.7744 | 21.9046 | 21.0812 | 21.1812 | 21.3999 | 20.4694 | 20.6402 | 21.0808 | 21.8681 | 21.6336 | 22.0451 | 90.9127 | 81.7038 | 97.2997 | 22.1057 | 21.69 | 21.6532 | 22.0054 | 21.7392 | 21.9812 | 28.5757 | 86.0464 |  | 43.4226 | 70.0696 | 76.6233 | 46.0655 |  | 16.9616 | 17.0824 | 16.6323 | 16.9625 | 17.214 | 18.5203 | 45.0494 | 15.7076 | 17.0305 | 15.6225 | 17.4357 | 18.1 | 44.1409 | 46.7767 | 43.3804 | 21.5623 |  |  | 0.61792 | -0.19851 | -27.1187 | 0.39488 | 0.031672 | -197.8388 | 17.8679 | 0.54307 | 0.17874 | 0.13753 | 0.29819 | 0.00033349 | 0.00032035 | 1.8832 | 21.7918 | 22.0062 | 22.193 | 22.255 | 22.0711 | 21.3653 | 20.1798 | 22.1958 | 22.3712 | 22.4022 | 22.3546 | 21.9718 | 21.2055 | 22.2829 | 39.1447 | 25.4397 | 26.7308 | 21.5205 | 19.4401 | 25.8743 | 20.7839 | 22.362 | 22.1227 | 21.6793 | 22.075 | 21.7855 | 21.2887 | 21.9356 | 21.5245 | 21.125 | 28.3455 | 91.166 | 63.0869 | 41.4083 | 0.03481 | -0.14338 | 36.8256 | 22.0134 | 22.3103 | 20.1606 | 21.625 | 22.065 | 21.9209 | 21.6937 | 22.5988 | 21.7601 | 21.4259 | 21.41 | 83.1291 | 101.7096 | 62.8079 | 63.8616 | 36.8612 |  | 27.9319 | 57.6169 | 29.8728 | 41.8159 | 28.6504 | 35.1453 |  | 37.1459 |  |  | 21.059 | 21.8469 | 33.3922 | [5 empty] | 21.8911 | 31.055 | 21.6493 | 22.0205 | 25.6244 | 21.1615 | 21.7928 | 21.5334 | 37.8598 | 110.875 |  | 30.5359 | 76.1843 | 19.8909 | 32.153 | 80.279 | 26.4923 | 63.4112 | 21.1078 | 58.6215 | 21.0357 | 60.732 | 18.6167 | 32.6663 | 72.762 | 22.3759 | 33.2519 | 98.2177 | 20.032 | 32.0241 | 83.0344 | 20.0935 | 55.7592 | 22.9049 | 60.0764 | 21.0754 | 61.723 | 0.41854 | 20.0447 | 0.65555 | 0.022941 | -27.0649 | 3.0956 | 44.54 | 52.69 | 1.0544 | -0.52897 | -6.1826 | 0.74606 | 0.21181 | -16.7405 | 5.0309 | 0.2179 | -0.29261 | 0.10469 | -1.0212 | -0.23753 | -0.015898 | 0.10564
42838.4223 | 174 | 22.9071 | 22.874 | 22.8596 | 22.779 | 22.3963 | 21.7278 | 22.719 | 21.7835 | 22.3611 | 22.3687 | 22.3408 | 22.0034 | 21.2009 | 22.1782 | 21.6016 | 21.7741 | 21.8994 | 21.0914 | 21.1793 | 21.3949 | 20.4776 | 20.6313 | 21.0876 | 21.8724 | 21.6279 | 22.0572 | 91.0932 | 81.8526 | 97.3202 | 22.1062 | 21.6976 | 21.6625 | 22.0078 | 21.7436 | 21.9969 | 28.6561 | 85.9734 |  | 43.5588 | 70.3102 | 76.7477 | 46.5896 |  | 16.9666 | 17.0855 | 16.6291 | 16.9587 | 17.2159 | 18.5146 | 44.8085 | 15.7415 | 17.0307 | 15.6137 | 17.4504 | 18.1047 | 44.0879 | 46.7805 | 43.364 | 21.5584 |  |  | 0.73686 | -0.21691 | -27.3881 | 0.28251 | 0.16178 | -197.842 | 17.8383 | 0.49445 | 0.045435 | 0.090535 | -0.046581 | 0.00033842 | 0.00035484 | 1.8588 | 21.7889 | 22.004 | 22.1912 | 22.2507 | 22.0687 | 21.3681 | 20.1776 | 22.1956 | 22.3655 | 22.4086 | 22.3525 | 21.9682 | 21.2046 | 22.2726 | 37.7733 | 25.452 | 27.1802 | 21.813 | 19.8494 | 25.918 | 20.8215 | 22.3693 | 22.1327 | 21.6927 | 22.08 | 21.7942 | 21.2953 | 21.9424 | 21.5409 | 21.1379 | 28.4274 | 91.3617 | 63.2619 | 41.4419 | 0.17852 | -0.092596 | 36.8587 | 22.0124 | 22.3195 | 20.1572 | 21.6228 | 22.0704 | 21.9226 | 21.6926 | 22.6275 | 21.7646 | 21.4261 | 21.4198 | 83.3809 | 101.7768 | 62.9995 | 64.0757 | 36.9358 |  | 28.008 | 57.2393 | 29.9537 | 41.9744 | 28.7275 | 35.1551 |  | 37.2595 |  |  | 21.0727 | 21.838 | 33.3912 | [5 empty] | 21.8993 | 31.0492 | 21.6488 | 22.0326 | 25.6415 | 21.161 | 21.7932 | 21.5544 | 37.9213 | 110.8286 |  | 30.5758 | 76.4392 | 19.9052 | 32.3152 | 80.3961 | 26.5197 | 63.5794 | 21.1198 | 58.9114 | 21.049 | 60.8774 | 18.6021 | 32.7103 | 72.8431 | 22.3807 | 33.311 | 98.3194 | 20.0388 | 32.1176 | 83.0678 | 20.108 | 55.8877 | 22.9476 | 60.1196 | 21.0938 | 61.9123 | 0.21542 | 20.0405 | 0.65919 | 0.022614 | -27.0736 | 3.0955 | 41.76 | 51.66 | 1.1514 | -0.55295 | -6.2133 | 0.63105 | 0.47871 | -16.7405 | 5.0267 | 0.21841 | -0.27936 | 0.10291 | -0.86367 | -0.28307 | -0.027721 | 0.10749
42838.4223 | 175 | 22.9065 | 22.874 | 22.8618 | 22.7806 | 22.4003 | 21.7261 | 22.7185 | 21.7856 | 22.3661 | 22.3724 | 22.3413 | 22.0021 | 21.2084 | 22.1763 | 21.5991 | 21.7743 | 21.9058 | 21.0854 | 21.1834 | 21.3956 | 20.4712 | 20.6277 | 21.0936 | 21.8735 | 21.6257 | 22.0678 | 91.1601 | 82.0088 | 96.9631 | 22.1025 | 21.6917 | 21.6693 | 22.0069 | 21.7382 | 22.0062 | 28.7357 | 86.3536 |  | 43.6836 | 70.551 | 76.8882 | 47.1569 |  | 16.9696 | 17.077 | 16.6296 | 16.9681 | 17.2108 | 18.5413 | 44.9453 | 15.7734 | 17.0356 | 15.6189 | 17.4528 | 18.1039 | 44.0423 | 46.7717 | 43.3393 | 21.5548 |  |  | 0.7178 | -0.1696 | -27.3105 | 0.32523 | 0.18347 | -197.8591 | 17.8955 | 0.56476 | 0.073458 | 0.072492 | 0.039178 | 0.00032363 | 0.00033349 | 1.8623 | 21.7735 | 21.9934 | 22.1891 | 22.2411 | 22.0545 | 21.3508 | 20.1603 | 22.1777 | 22.3595 | 22.3903 | 22.3385 | 21.9647 | 21.1932 | 22.2619 | 37.4215 | 24.6555 | 26.7176 | 21.9324 | 19.9902 | 25.9723 | 20.8392 | 22.3692 | 22.1375 | 21.6908 | 22.0761 | 21.7954 | 21.2928 | 21.9423 | 21.5446 | 21.1341 | 28.5025 | 91.5855 | 63.4224 | 41.5254 | 0.23436 | -0.174 | 37.0556 | 22.0226 | 22.3305 | 20.1593 | 21.6279 | 22.0707 | 21.923 | 21.6994 | 22.6474 | 21.7668 | 21.4345 | 21.4288 | 83.6501 | 101.8466 | 63.1871 | 64.266 | 36.7468 |  | 28.0861 | 57.1397 | 30.0238 | 42.1657 | 28.8112 | 35.1831 |  | 37.373 |  |  | 21.0744 | 21.8519 | 33.524 | [5 empty] | 21.8969 | 31.0759 | 21.6438 | 22.0242 | 25.6619 | 21.1568 | 21.7857 | 21.5627 | 37.9699 | 110.9581 |  | 30.6409 | 76.664 | 19.9065 | 32.4248 | 80.494 | 26.538 | 63.7074 | 21.1316 | 58.9947 | 21.0595 | 61.1551 | 18.6245 | 32.7721 | 72.9746 | 22.398 | 33.3629 | 98.7227 | 20.0574 | 32.2205 | 83.2466 | 20.1373 | 55.9979 | 22.9822 | 60.3579 | 21.119 | 62.0289 | 0.38422 | 20.0353 | 0.66241 | 0.022825 | -27.1072 | 3.0956 | 47.14 | 52.31 | 1.1359 | -0.48893 | -6.2044 | 0.67707 | 0.50981 | -16.742 | 5.035 | 0.22631 | -0.27421 | 0.10044 | -0.81821 | -0.22961 | -0.040773 | 0.10773
42838.4223 | 176 | 22.9109 | 22.8678 | 22.8606 | 22.7764 | 22.398 | 21.7276 | 22.7154 | 21.7887 | 22.3563 | 22.3692 | 22.3406 | 21.995 | 21.2061 | 22.171 | 21.6018 | 21.778 | 21.9022 | 21.0909 | 21.1824 | 21.3963 | 20.4749 | 20.6326 | 21.0947 | 21.8719 | 21.6345 | 22.0852 | 91.2074 | 82.1771 | 96.4599 | 22.1009 | 21.6901 | 21.6752 | 22.0067 | 21.7406 | 22.017 | 28.8211 | 86.9391 |  | 43.8115 | 70.7588 | 77.0498 | 47.3221 |  | 16.9731 | 17.0796 | 16.6365 | 16.9732 | 17.2187 | 18.6327 | 45.2907 | 15.8016 | 17.0376 | 15.6571 | 17.4642 | 18.1018 | 44.0038 | 46.7685 | 43.3387 | 21.5529 |  |  | 0.67837 | -0.24188 | -27.3243 | 0.32983 | 0.2748 | -197.8328 | 17.9093 | 0.58447 | 0.047187 | 0.1583 | 0.10949 | 0.00034992 | 0.0003532 | 1.8773 | 21.7844 | 21.9966 | 22.1989 | 22.2462 | 22.0585 | 21.3617 | 20.1755 | 22.1877 | 22.3669 | 22.3943 | 22.3531 | 21.9689 | 21.2037 | 22.2776 | 37.3249 | 24.9524 | 26.1803 | 21.6488 | 19.9883 | 26.025 | 20.8685 | 22.3697 | 22.1424 | 21.6895 | 22.0845 | 21.7941 | 21.2878 | 21.9408 | 21.5393 | 21.1413 | 28.5788 | 91.6195 | 63.5723 | 41.3227 | 0.073541 | -0.091265 | 36.9727 | 22.0209 | 22.3331 | 20.1665 | 21.6352 | 22.0767 | 21.9235 | 21.6974 | 22.6766 | 21.7721 | 21.4417 | 21.4426 | 83.8585 | 101.9577 | 63.3554 | 64.4302 | 36.7399 |  | 28.1572 | 57.3101 | 30.1213 | 42.2818 | 28.8901 | 35.2878 |  | 37.4765 |  |  | 21.0764 | 21.8589 | 33.6705 | [5 empty] | 21.895 | 31.149 | 21.6458 | 22.0287 | 25.6913 | 21.1609 | 21.7835 | 21.5623 | 38.0474 | 111.2473 |  | 30.7115 | 76.832 | 19.9101 | 32.5257 | 80.5774 | 26.5803 | 63.8083 | 21.1344 | 59.0351 | 21.0661 | 61.49 | 18.625 | 32.8094 | 73.0952 | 22.4153 | 33.4098 | 98.9653 | 20.0485 | 32.3146 | 83.4889 | 20.1356 | 56.1668 | 22.9915 | 60.4708 | 21.125 | 62.1337 | 0.33043 | 20.0322 | 0.66526 | 0.022331 | -27.1121 | 3.0956 | 37.1 | 51.87 | 1.1035 | -0.58391 | -6.206 | 0.68184 | 0.62403 | -16.7435 | 5.0377 | 0.22892 | -0.27561 | 0.0999 | -0.80131 | -0.16647 | -0.042457 | 0.11595
42838.4223 | 177 | 22.9142 | 22.8764 | 22.8653 | 22.7815 | 22.4035 | 21.7341 | 22.7179 | 21.7914 | 22.3578 | 22.368 | 22.3467 | 22.0022 | 21.2164 | 22.1823 | 21.6043 | 21.7711 | 21.8967 | 21.0842 | 21.1871 | 21.394 | 20.4723 | 20.6268 | 21.0946 | 21.8663 | 21.6333 | 22.0924 | 91.1896 | 82.4339 | 95.7958 | 22.1118 | 21.6948 | 21.6897 | 22.0194 | 21.7499 | 22.0341 | 28.9063 | 86.8914 |  | 43.9261 | 70.9337 | 77.2156 | 47.1578 |  | 16.9646 | 17.0705 | 16.6287 | 16.9607 | 17.269 | 18.7133 | 45.7488 | 15.7807 | 17.0303 | 15.7182 | 17.4569 | 18.107 | 43.9712 | 46.7743 | 43.3343 | 21.5597 |  |  | 0.65077 | -0.45611 | -27.4268 | 0.56836 | 0.22749 | -197.8151 | 17.8541 | 0.60156 | 0.12094 | -0.15472 | 0.049941 | 0.00034663 | 0.00035484 | 1.8832 | 21.7833 | 21.9991 | 22.1909 | 22.2413 | 22.0613 | 21.3606 | 20.1702 | 22.1898 | 22.3668 | 22.3967 | 22.3472 | 21.9653 | 21.1964 | 22.2699 | 36.8968 | 24.6297 | 26.4458 | 21.3373 | 19.9006 | 26.0648 | 20.9037 | 22.3658 | 22.1378 | 21.6839 | 22.0792 | 21.7917 | 21.2861 | 21.9464 | 21.536 | 21.1466 | 28.6532 | 91.8867 | 63.8074 | 41.228 | 0.047786 | -0.057409 | 37.0262 | 22.0151 | 22.3322 | 20.1632 | 21.6318 | 22.0727 | 21.9224 | 21.6902 | 22.6947 | 21.7656 | 21.4341 | 21.4485 | 83.976 | 102.0401 | 63.5094 | 64.5652 | 37.2508 |  | 28.242 | 57.7781 | 30.2228 | 42.2857 | 28.9688 | 35.1755 |  | 37.577 |  |  | 21.079 | 21.874 | 33.7558 | [5 empty] | 21.8997 | 31.2357 | 21.6507 | 22.029 | 25.724 | 21.1588 | 21.7936 | 21.5803 | 38.1882 | 111.3302 |  | 30.8187 | 77.0505 | 19.9234 | 32.5874 | 80.7358 | 26.6381 | 63.964 | 21.1383 | 59.1409 | 21.0856 | 61.736 | 18.6305 | 32.7993 | 73.2634 | 22.4269 | 33.5367 | 99.0787 | 20.058 | 32.4192 | 83.6494 | 20.139 | 56.3153 | 23.0209 | 60.5853 | 21.1433 | 62.2714 | 0.27163 | 20.026 | 0.66829 | 0.021983 | -27.1366 | 3.0955 | 56.14 | 51.9 | 1.0798 | -0.8018 | -6.2175 | 0.89504 | 0.56786 | -16.745 | 5.0307 | 0.21761 | -0.28515 | 0.10247 | -0.74907 | -0.19186 | -0.034994 | 0.12111
42838.4223 | 178 | 22.9154 | 22.8756 | 22.848 | 22.7752 | 22.3889 | 21.7298 | 22.7189 | 21.7796 | 22.3573 | 22.3695 | 22.3339 | 21.9911 | 21.2075 | 22.1736 | 21.6107 | 21.7703 | 21.9008 | 21.0854 | 21.1879 | 21.3895 | 20.4747 | 20.6333 | 21.1044 | 21.8762 | 21.6304 | 22.1054 | 91.2986 | 82.64 | 96.0758 | 22.1063 | 21.6982 | 21.7013 | 22.0158 | 21.7426 | 22.0477 | 28.9865 | 86.6067 |  | 44.0341 | 71.0889 | 77.388 | 46.7377 |  | 16.9614 | 17.0787 | 16.6302 | 16.9829 | 17.3248 | 18.8293 | 45.9372 | 15.7111 | 17.0406 | 15.7503 | 17.46 | 18.1035 | 43.9482 | 46.7801 | 43.3156 | 21.5553 |  |  | 0.78811 | -0.35097 | -27.8829 | 0.34429 | 0.041528 | -197.8545 | 17.7457 | 0.59762 | -0.03727 | -0.094089 | 0.15341 | 0.00034334 | 0.00032692 | 1.8904 | 21.7806 | 21.9929 | 22.1862 | 22.2419 | 22.0572 | 21.3629 | 20.1698 | 22.1846 | 22.3593 | 22.3934 | 22.3432 | 21.9662 | 21.1974 | 22.2652 | 36.0854 | 24.8898 | 26.1512 | 21.3806 | 19.7287 | 26.0983 | 20.9338 | 22.3597 | 22.1297 | 21.684 | 22.0845 | 21.7849 | 21.2921 | 21.9411 | 21.5405 | 21.1495 | 28.7432 | 91.9993 | 63.9891 | 41.1472 | 0.18501 | -0.18598 | 37.027 | 22.0078 | 22.3255 | 20.152 | 21.6263 | 22.0678 | 21.917 | 21.691 | 22.7116 | 21.756 | 21.4332 | 21.4526 | 84.0759 | 102.1008 | 63.6279 | 64.7024 | 37.3509 |  | 28.3443 | 58.1577 | 30.3433 | 42.4869 | 29.0596 | 35.1926 |  | 37.6971 |  |  | 21.0855 | 21.8742 | 33.822 | [5 empty] | 21.9036 | 31.3709 | 21.6542 | 22.024 | 25.738 | 21.1606 | 21.7943 | 21.5845 | 38.3483 | 111.2784 |  | 30.9442 | 77.2125 | 19.932 | 32.6599 | 80.9509 | 26.6596 | 64.1351 | 21.129 | 59.2364 | 21.1055 | 61.8612 | 18.6262 | 32.8299 | 73.499 | 22.4401 | 33.7083 | 99.1549 | 20.0724 | 32.5288 | 83.6613 | 20.1455 | 56.4565 | 23.0347 | 60.7837 | 21.1549 | 62.3938 | 0.25586 | 20.0217 | 0.67055 | 0.021787 | -27.106 | 3.0955 | 58.7 | 52.68 | 1.1888 | -0.70335 | -6.2691 | 0.69662 | 0.24267 | -16.75 | 5.0164 | 0.2183 | -0.29158 | 0.09997 | -0.65498 | -0.15561 | -0.020596 | 0.12642
42838.4223 | 179 | 22.9132 | 22.8736 | 22.8609 | 22.7838 | 22.3965 | 21.7341 | 22.723 | 21.798 | 22.3668 | 22.3682 | 22.3454 | 21.9988 | 21.2153 | 22.1755 | 21.6105 | 21.7842 | 21.897 | 21.089 | 21.1796 | 21.3941 | 20.4694 | 20.6382 | 21.1042 | 21.8695 | 21.633 | 22.1188 | 91.546 | 82.8017 | 96.719 | 22.1025 | 21.699 | 21.7048 | 22.01 | 21.7459 | 22.0488 | 29.0623 | 85.8897 |  | 44.1509 | 71.2775 | 77.5284 | 46.6559 |  | 16.9657 | 17.0812 | 16.6317 | 17.0167 | 17.3808 | 18.8969 | 45.9258 | 15.6759 | 17.036 | 15.7147 | 17.4633 | 18.1136 | 43.9419 | 46.7828 | 43.3055 | 21.552 |  |  | 0.8052 | -0.22283 | -27.8014 | 0.57362 | 0.26166 | -197.8374 | 17.7647 | 0.66201 | -0.12387 | 0.066408 | 0.15914 | 0.00036963 | 0.00031213 | 1.8961 | 21.7792 | 21.9994 | 22.1882 | 22.2388 | 22.0616 | 21.3611 | 20.1771 | 22.1911 | 22.3645 | 22.3993 | 22.3482 | 21.9713 | 21.2024 | 22.2673 | 36.0677 | 25.2384 | 25.7802 | 21.4054 | 19.9306 | 26.13 | 20.9435 | 22.3611 | 22.1331 | 21.6867 | 22.0751 | 21.7856 | 21.2862 | 21.9363 | 21.5364 | 21.1575 | 28.8172 | 92.1376 | 64.3032 | 40.9496 | 0.08396 | 0.059183 | 37.1076 | 22.0227 | 22.331 | 20.1701 | 21.6322 | 22.08 | 21.9274 | 21.7026 | 22.7413 | 21.766 | 21.4395 | 21.4703 | 84.2299 | 102.2087 | 63.7741 | 64.8299 | 37.2671 |  | 28.4235 | 59.0774 | 30.4357 | 42.8927 | 29.1502 | 35.1704 |  | 37.8163 |  |  | 21.0865 | 21.8557 | 33.8531 | [5 empty] | 21.8992 | 31.4464 | 21.6488 | 22.0232 | 25.7507 | 21.16 | 21.7886 | 21.5881 | 38.4798 | 111.0496 |  | 31.0607 | 77.3755 | 19.9416 | 32.7539 | 81.1175 | 26.67 | 64.3067 | 21.131 | 59.3393 | 21.1213 | 61.9683 | 18.6095 | 33.0034 | 73.6696 | 22.4525 | 33.8634 | 99.2697 | 20.0786 | 32.6124 | 83.7515 | 20.1468 | 56.6079 | 23.0553 | 61.0112 | 21.1668 | 62.5357 | 0.29871 | 20.0195 | 0.67339 | 0.02093 | -27.0875 | 3.0955 | 70.84 | 51.55 | 1.2027 | -0.56043 | -6.26 | 0.89919 | 0.60921 | -16.7513 | 5.0196 | 0.22332 | -0.31398 | 0.091779 | -0.64932 | -0.11326 | -0.015743 | 0.13442
42838.4224 | 180 | 22.9118 | 22.8758 | 22.8667 | 22.7826 | 22.4007 | 21.7363 | 22.7238 | 21.7909 | 22.3739 | 22.3786 | 22.347 | 21.9999 | 21.2097 | 22.182 | 21.6082 | 21.7851 | 21.9051 | 21.0916 | 21.1855 | 21.4002 | 20.4733 | 20.6435 | 21.114 | 21.8694 | 21.6326 | 22.1431 | 91.7667 | 82.9172 | 96.8185 | 22.0966 | 21.6918 | 21.7005 | 22.0038 | 21.7376 | 22.0571 | 29.1382 | 85.2773 |  | 44.257 | 71.451 | 77.6297 | 47.2208 |  | 16.966 | 17.0892 | 16.6317 | 17.048 | 17.422 | 18.948 | 45.721 | 15.6595 | 17.0445 | 15.6505 | 17.4648 | 18.1045 | 43.9418 | 46.7828 | 43.304 | 21.5547 |  |  | 0.819 | -0.16106 | -27.1574 | 0.59596 | 0.1079 | -197.821 | 18.2168 | 0.5503 | 0.068982 | 0.1604 | 0.14264 | 0.00033677 | 0.00031542 | 1.8929 | 21.7827 | 22.002 | 22.1967 | 22.2473 | 22.0652 | 21.3638 | 20.1784 | 22.1968 | 22.3697 | 22.4074 | 22.3534 | 21.9766 | 21.2033 | 22.2684 | 36.4122 | 26.5889 | 27.0524 | 21.3644 | 20.1365 | 26.1913 | 20.9842 | 22.3637 | 22.1344 | 21.6914 | 22.0771 | 21.7911 | 21.2899 | 21.9489 | 21.5379 | 21.1609 | 28.8966 | 92.2219 | 64.5734 | 40.6742 | 0.30219 | -0.04809 | 37.1827 | 22.0195 | 22.3248 | 20.1725 | 21.6291 | 22.0769 | 21.9238 | 21.7019 | 22.7598 | 21.7679 | 21.4351 | 21.4734 | 84.3531 | 102.3822 | 63.948 | 64.976 | 37.198 |  | 28.4937 | 59.8727 | 30.519 | 42.9764 | 29.2301 | 35.4196 |  | 37.9205 |  |  | 21.0899 | 21.8623 | 33.9785 | [5 empty] | 21.8939 | 31.4829 | 21.6478 | 22.0224 | 25.7664 | 21.1631 | 21.7909 | 21.5919 | 38.5351 | 111.1852 |  | 31.1449 | 77.5194 | 19.9473 | 32.891 | 81.2179 | 26.6885 | 64.4647 | 21.1328 | 59.485 | 21.1331 | 62.0976 | 18.6023 | 33.2137 | 73.7704 | 22.4666 | 33.9805 | 99.3628 | 20.0893 | 32.742 | 83.9626 | 20.1535 | 56.781 | 23.0779 | 61.283 | 21.1847 | 62.6992 | 0.38126 | 20.0141 | 0.67635 | 0.020952 | -27.0657 | 3.0955 | 51.05 | 52.59 | 1.2131 | -0.47647 | -6.1871 | 0.91655 | 0.39124 | -16.752 | 5.0836 | 0.22763 | -0.33323 | 0.092177 | -0.6804 | -0.24986 | -0.028851 | 0.14478
42838.4224 | 181 | 22.9145 | 22.8695 | 22.8635 | 22.7758 | 22.4006 | 21.7339 | 22.7216 | 21.7944 | 22.3699 | 22.3776 | 22.3454 | 21.9986 | 21.2112 | 22.1774 | 21.6121 | 21.7852 | 21.9101 | 21.0971 | 21.1889 | 21.4077 | 20.477 | 20.6494 | 21.1232 | 21.8786 | 21.636 | 22.155 | 91.9007 | 83.0326 | 96.6974 | 22.1048 | 21.7028 | 21.7175 | 22.0084 | 21.7439 | 22.0745 | 29.2304 | 85.098 |  | 44.3906 | 71.6421 | 77.7067 | 47.3895 |  | 16.9652 | 17.0906 | 16.6263 | 17.0564 | 17.4391 | 18.9841 | 45.4569 | 15.6983 | 17.0497 | 15.6045 | 17.474 | 18.1082 | 43.9498 | 46.7785 | 43.2891 | 21.5507 |  |  | 0.79337 | -0.40025 | -27.1574 | 0.29106 | 0.10264 | -197.8696 | 18.0841 | 0.51679 | -0.11939 | 0.19082 | 0.17354 | 0.00034006 | 0.00034334 | 1.8799 | 21.7833 | 21.9891 | 22.192 | 22.2435 | 22.0592 | 21.3579 | 20.1733 | 22.1936 | 22.3578 | 22.4017 | 22.3521 | 21.9665 | 21.1938 | 22.27 | 37.0379 | 27.9364 | 27.4323 | 21.8004 | 20.3767 | 26.2574 | 21.0198 | 22.3765 | 22.1346 | 21.6972 | 22.0903 | 21.7905 | 21.3008 | 21.9547 | 21.5519 | 21.1834 | 28.9788 | 92.3812 | 64.7791 | 40.7014 | 0.31654 | -0.052464 | 37.319 | 22.013 | 22.3228 | 20.1625 | 21.6281 | 22.0665 | 21.9268 | 21.699 | 22.7837 | 21.7668 | 21.44 | 21.4785 | 84.5319 | 102.5135 | 64.145 | 65.1701 | 37.3249 |  | 28.5672 | 60.5256 | 30.5952 | 42.7869 | 29.3007 | 35.5295 |  | 38.0337 |  |  | 21.0879 | 21.8855 | 34.0539 | [5 empty] | 21.895 | 31.5432 | 21.6562 | 22.027 | 25.779 | 21.1676 | 21.796 | 21.5964 | 38.5422 | 111.5582 |  | 31.2219 | 77.7516 | 19.9524 | 33.023 | 81.3202 | 26.7187 | 64.5985 | 21.1314 | 59.5853 | 21.147 | 62.2642 | 18.6 | 33.4329 | 73.841 | 22.4775 | 34.063 | 99.4131 | 20.1037 | 32.8855 | 84.2146 | 20.1617 | 56.9549 | 23.1085 | 61.6656 | 21.2057 | 62.8676 | 0.21857 | 20.0108 | 0.67971 | 0.021133 | -27.0545 | 3.0955 | 49.11 | 51.74 | 1.1938 | -0.75112 | -6.1871 | 0.64052 | 0.38161 | -16.7551 | 5.0653 | 0.22661 | -0.34876 | 0.099845 | -0.74218 | -0.28791 | -0.030396 | 0.14682
42838.4224 | 182 | 22.9082 | 22.8673 | 22.8572 | 22.7794 | 22.4016 | 21.7328 | 22.7208 | 21.7835 | 22.3642 | 22.3742 | 22.3394 | 21.9951 | 21.2069 | 22.1771 | 21.6089 | 21.7823 | 21.9048 | 21.0938 | 21.189 | 21.4018 | 20.4751 | 20.6455 | 21.1267 | 21.8727 | 21.635 | 22.1678 | 91.9477 | 83.1313 | 96.3981 | 22.1064 | 21.6993 | 21.7346 | 22.0086 | 21.7496 | 22.0939 | 29.3145 | 85.352 |  | 44.5189 | 71.8289 | 77.7682 | 47.3892 |  | 16.9669 | 17.091 | 16.6243 | 17.0564 | 17.4588 | 18.9874 | 45.1312 | 15.7365 | 17.0519 | 15.5661 | 17.4795 | 18.1137 | 43.9753 | 46.783 | 43.2807 | 21.5573 |  |  | 0.67903 | -0.2248 | -27.3795 | 0.3686 | 0.25444 | -197.8309 | 18.2674 | 0.48853 | 0.10109 | 0.020672 | 0.075113 | 0.00034992 | 0.00028913 | 1.8705 | 21.7724 | 21.99 | 22.1794 | 22.2353 | 22.0633 | 21.361 | 20.1673 | 22.1862 | 22.3615 | 22.3957 | 22.3427 | 21.9663 | 21.1934 | 22.2683 | 37.1572 | 28.5162 | 27.6565 | 21.5456 | 20.6047 | 26.3361 | 21.0599 | 22.3658 | 22.1439 | 21.6908 | 22.0775 | 21.7907 | 21.2949 | 21.9437 | 21.5506 | 21.1816 | 29.0524 | 92.4597 | 64.9356 | 40.7062 | 0.3995 | -0.10876 | 37.3977 | 22.0121 | 22.3185 | 20.1637 | 21.6268 | 22.0621 | 21.9179 | 21.699 | 22.7946 | 21.7657 | 21.4384 | 21.4803 | 84.7042 | 102.5977 | 64.3297 | 65.3841 | 37.3196 |  | 28.6456 | 60.7643 | 30.7204 | 42.9707 | 29.3981 | 36.1685 |  | 38.1593 |  |  | 21.0959 | 21.904 | 34.2586 | [5 empty] | 21.8982 | 31.6981 | 21.657 | 22.0348 | 25.8012 | 21.1764 | 21.796 | 21.5996 | 38.6038 | 111.7087 |  | 31.2966 | 77.9566 | 19.9603 | 33.0857 | 81.4811 | 26.7482 | 64.7211 | 21.135 | 59.6625 | 21.1586 | 62.4266 | 18.5907 | 33.6246 | 73.974 | 22.4889 | 34.1202 | 99.4617 | 20.119 | 32.9475 | 84.3438 | 20.1702 | 57.1023 | 23.1338 | 62.1132 | 21.2157 | 63.0815 | 0.26921 | 20.0091 | 0.68289 | 0.020865 | -27.0774 | 3.0955 | 47.47 | 51.34 | 1.1039 | -0.56292 | -6.2124 | 0.72081 | 0.60083 | -16.7536 | 5.091 | 0.22942 | -0.35112 | 0.098058 | -0.74621 | -0.30812 | -0.027524 | 0.14919
42838.4224 | 183 | 22.9171 | 22.8759 | 22.8662 | 22.7816 | 22.4045 | 21.7292 | 22.7173 | 21.786 | 22.3608 | 22.3756 | 22.339 | 22.0031 | 21.2127 | 22.1822 | 21.6065 | 21.7763 | 21.9077 | 21.0922 | 21.1926 | 21.3982 | 20.4753 | 20.6404 | 21.1228 | 21.871 | 21.6321 | 22.1828 | 91.9689 | 83.2666 | 96.3508 | 22.106 | 21.6981 | 21.7411 | 22.0101 | 21.7443 | 22.1011 | 29.3968 | 84.8592 |  | 44.6371 | 72.0329 | 77.825 | 47.3493 |  | 16.9686 | 17.0928 | 16.6266 | 17.0532 | 17.4561 | 18.9964 | 44.8264 | 15.7568 | 17.0381 | 15.5458 | 17.4692 | 18.1105 | 44.0062 | 46.7752 | 43.2655 | 21.5506 |  |  | 0.84725 | -0.24714 | -27.2179 | 0.25952 | 0.096072 | -197.8539 | 18.1104 | 0.48525 | -0.095066 | -0.012477 | 0.11626 | 0.00033184 | 0.0002727 | 1.8631 | 21.771 | 21.9941 | 22.1872 | 22.2441 | 22.0578 | 21.3571 | 20.1695 | 22.1831 | 22.3575 | 22.3968 | 22.3475 | 21.9704 | 21.1971 | 22.2649 | 38.4044 | 28.1652 | 27.5623 | 21.7633 | 20.6975 | 26.424 | 21.0947 | 22.361 | 22.1335 | 21.6925 | 22.0795 | 21.792 | 21.2979 | 21.9428 | 21.5458 | 21.185 | 29.1378 | 92.8156 | 65.1199 | 40.6099 | 0.4577 | -0.0060554 | 37.4411 | 22.0136 | 22.3207 | 20.1568 | 21.6336 | 22.0701 | 21.9221 | 21.6956 | 22.8137 | 21.7659 | 21.4375 | 21.4923 | 84.9137 | 102.6604 | 64.4508 | 65.5617 | 37.0801 |  | 28.7134 | 60.6982 | 30.828 | 42.9545 | 29.4767 | 36.0525 |  | 38.2658 |  |  | 21.0966 | 21.9194 | 34.3649 | [5 empty] | 21.8916 | 31.8935 | 21.6469 | 22.029 | 25.8179 | 21.1699 | 21.8009 | 21.5989 | 38.7315 | 111.6664 |  | 31.3737 | 78.0595 | 19.9516 | 33.0988 | 81.6374 | 26.7747 | 64.8448 | 21.1403 | 59.7769 | 21.1677 | 62.5687 | 18.5819 | 33.7743 | 74.1296 | 22.4952 | 34.1836 | 99.5836 | 20.1131 | 32.9724 | 84.4963 | 20.1804 | 57.1864 | 23.1491 | 62.4641 | 21.2236 | 63.2652 | 0.11506 | 20.0059 | 0.6863 | 0.02085 | -27.0489 | 3.0955 | 65.75 | 52.57 | 1.2331 | -0.59023 | -6.1941 | 0.60483 | 0.3692 | -16.7548 | 5.0691 | 0.23838 | -0.34561 | 0.10118 | -0.87449 | -0.29359 | -0.023617 | 0.15477
42838.4224 | 184 | 22.9094 | 22.8742 | 22.8701 | 22.7812 | 22.4019 | 21.7396 | 22.7165 | 21.7815 | 22.3569 | 22.3758 | 22.3491 | 22.0025 | 21.2059 | 22.1813 | 21.6062 | 21.7868 | 21.9036 | 21.0883 | 21.183 | 21.3994 | 20.4782 | 20.6424 | 21.1333 | 21.8759 | 21.6277 | 22.1913 | 92.0775 | 83.411 | 96.4796 | 22.1052 | 21.696 | 21.7553 | 22.0135 | 21.7442 | 22.1125 | 29.4715 | 84.3899 |  | 44.771 | 72.2148 | 77.8825 | 47.5163 |  | 16.9593 | 17.0913 | 16.6304 | 17.0491 | 17.4489 | 19.0155 | 44.5709 | 15.8043 | 17.0452 | 15.5475 | 17.4736 | 18.1178 | 44.032 | 46.7792 | 43.2545 | 21.5585 |  |  | 0.7638 | -0.1926 | -27.7094 | 0.42183 | 0.12761 | -197.8795 | 18.0079 | 0.44516 | 0.16064 | 0.10165 | 0.14837 | 0.00032363 | 0.00029242 | 1.835 | 21.7819 | 22.0005 | 22.1929 | 22.2548 | 22.0595 | 21.3618 | 20.1757 | 22.1885 | 22.3684 | 22.3959 | 22.3472 | 21.9753 | 21.1986 | 22.2686 | 40.5949 | 29.2539 | 27.7904 | 22.2108 | 21.2615 | 26.5171 | 21.1316 | 22.3611 | 22.1305 | 21.6926 | 22.0758 | 21.7944 | 21.2893 | 21.9436 | 21.541 | 21.1877 | 29.2047 | 92.8654 | 65.3095 | 40.6954 | 0.4111 | 0.081627 | 37.4565 | 22.0119 | 22.3197 | 20.1544 | 21.6306 | 22.0667 | 21.9289 | 21.6989 | 22.8392 | 21.7593 | 21.4337 | 21.5028 | 85.0901 | 102.8067 | 64.5493 | 65.7067 | 36.9507 |  | 28.7842 | 60.4162 | 30.9171 | 42.7754 | 29.5509 | 35.9767 |  | 38.3863 |  |  | 21.0907 | 21.9293 | 34.4078 | [5 empty] | 21.8885 | 31.9346 | 21.6457 | 22.0251 | 25.8285 | 21.1626 | 21.7866 | 21.6072 | 38.8826 | 111.4665 |  | 31.4145 | 78.2112 | 19.9542 | 33.1479 | 81.7571 | 26.8117 | 64.9871 | 21.1502 | 59.9266 | 21.1739 | 62.7301 | 18.5787 | 33.8585 | 74.2539 | 22.5002 | 34.2658 | 99.6196 | 20.1164 | 33.0454 | 84.6726 | 20.1888 | 57.2838 | 23.1647 | 62.6798 | 21.2328 | 63.3918 | 0.30724 | 20.0003 | 0.6894 | 0.020756 | -27.1058 | 3.0955 | 67.54 | 51.37 | 1.171 | -0.52105 | -6.2497 | 0.7711 | 0.42553 | -16.7564 | 5.0549 | 0.24438 | -0.33473 | 0.10869 | -1.107 | -0.31462 | -0.025711 | 0.15467
42838.4224 | 185 | 22.9128 | 22.8781 | 22.87 | 22.7898 | 22.4068 | 21.7408 | 22.7268 | 21.7928 | 22.3711 | 22.3717 | 22.3545 | 22.0005 | 21.2157 | 22.1901 | 21.6121 | 21.7919 | 21.9077 | 21.095 | 21.1972 | 21.4092 | 20.4866 | 20.6447 | 21.1444 | 21.8802 | 21.6423 | 22.2024 | 92.2024 | 83.5472 | 96.3303 | 22.1099 | 21.6994 | 21.7646 | 22.0205 | 21.7484 | 22.1222 | 29.5579 | 84.5832 |  | 44.9193 | 72.3655 | 77.9707 | 47.7624 |  | 16.9719 | 17.0903 | 16.6378 | 17.0544 | 17.441 | 19.0224 | 44.4316 | 15.8052 | 17.043 | 15.5767 | 17.4739 | 18.1176 | 44.0456 | 46.7758 | 43.2365 | 21.5629 |  |  | 0.66129 | -0.2156 | -27.5359 | 0.61699 | 0.055988 | -197.8486 | 18.2911 | 0.50628 | 0.067814 | 0.15138 | 0.15514 | 0.0003302 | 0.00032527 | 1.8297 | 21.7826 | 21.9972 | 22.1897 | 22.2439 | 22.0593 | 21.3575 | 20.177 | 22.1856 | 22.3579 | 22.3973 | 22.3442 | 21.9705 | 21.1986 | 22.274 | 41.0553 | 31.1079 | 30.0377 | 22.945 | 21.4543 | 26.6107 | 21.2007 | 22.3673 | 22.1318 | 21.6934 | 22.079 | 21.8008 | 21.298 | 21.9445 | 21.5482 | 21.2035 | 29.2791 | 92.8403 | 65.4393 | 41.019 | 0.40206 | -0.044286 | 37.602 | 22.0179 | 22.3216 | 20.1661 | 21.6307 | 22.0709 | 21.932 | 21.7051 | 22.8616 | 21.769 | 21.4425 | 21.5158 | 85.2123 | 103.0634 | 64.6696 | 65.8353 | 37.0438 |  | 28.8588 | 60.2938 | 31.0041 | 42.7786 | 29.6339 | 35.845 |  | 38.5121 |  |  | 21.0954 | 21.9457 | 34.3182 | [5 empty] | 21.901 | 31.8355 | 21.6537 | 22.0382 | 25.8493 | 21.1679 | 21.799 | 21.6271 | 38.9917 | 111.2825 |  | 31.4895 | 78.4145 | 19.9735 | 33.2122 | 81.9639 | 26.8435 | 65.1623 | 21.1609 | 60.1903 | 21.1955 | 62.9001 | 18.5835 | 33.9472 | 74.3562 | 22.5144 | 34.2901 | 99.5915 | 20.1223 | 33.1539 | 84.7824 | 20.1896 | 57.4181 | 23.1835 | 62.8113 | 21.2471 | 63.4785 | 0.2937 | 19.9959 | 0.69247 | 0.019718 | -27.1066 | 3.0955 | 70.6 | 52.3 | 1.0893 | -0.55128 | -6.2301 | 0.93257 | 0.28186 | -16.7553 | 5.0946 | 0.24434 | -0.32836 | 0.11143 | -1.1472 | -0.55625 | -0.029604 | 0.14822
42838.4224 | 186 | 22.9158 | 22.8699 | 22.8595 | 22.7781 | 22.4041 | 21.7314 | 22.7193 | 21.7881 | 22.3738 | 22.3723 | 22.348 | 22.0021 | 21.2106 | 22.1829 | 21.6163 | 21.7768 | 21.8989 | 21.0926 | 21.1909 | 21.3983 | 20.4745 | 20.6439 | 21.1442 | 21.8694 | 21.6272 | 22.2212 | 92.3288 | 83.6807 | 96.4754 | 22.1088 | 21.7022 | 21.7768 | 22.0161 | 21.754 | 22.1351 | 29.6403 | 85.7805 |  | 45.0749 | 72.5231 | 78.1175 | 47.5116 |  | 16.9638 | 17.0933 | 16.6309 | 17.0469 | 17.4298 | 19.0159 | 44.4463 | 15.775 | 17.0435 | 15.623 | 17.4753 | 18.1155 | 44.0631 | 46.7662 | 43.2162 | 21.5623 |  |  | 0.76446 | -0.28065 | -27.509 | 0.23652 | -0.005784 | -197.8854 | 17.7003 | 0.47802 | -0.0098312 | 0.033889 | 0.21746 | 0.00033677 | 0.00031542 | 1.8467 | 21.7735 | 21.9873 | 22.1855 | 22.2361 | 22.0513 | 21.3543 | 20.168 | 22.1864 | 22.3579 | 22.3965 | 22.3401 | 21.9657 | 21.1991 | 22.2653 | 40.948 | 31.1523 | 30.0042 | 23.2174 | 21.5154 | 26.7103 | 21.2581 | 22.3688 | 22.1397 | 21.6961 | 22.0881 | 21.7945 | 21.3043 | 21.9436 | 21.5546 | 21.2119 | 29.3499 | 92.7814 | 65.5451 | 41.2873 | 0.40265 | -0.036678 | 37.8315 | 22.0052 | 22.3181 | 20.1679 | 21.6192 | 22.0595 | 21.9229 | 21.7032 | 22.8831 | 21.7614 | 21.4316 | 21.5181 | 85.2968 | 103.0537 | 64.8015 | 65.973 | 37.3295 |  | 28.9342 | 60.2474 | 31.0947 | 43.2959 | 29.7027 | 36.2283 |  | 38.6226 |  |  | 21.0976 | 21.9404 | 34.619 | [5 empty] | 21.8995 | 31.7476 | 21.6429 | 22.0329 | 25.8674 | 21.1657 | 21.7948 | 21.6288 | 39.0541 | 111.2951 |  | 31.6427 | 78.5641 | 19.9766 | 33.2446 | 82.1521 | 26.8661 | 65.3387 | 21.1705 | 60.4171 | 21.2045 | 63.0742 | 18.5941 | 34.0236 | 74.474 | 22.5242 | 34.3713 | 99.6891 | 20.1304 | 33.2223 | 84.73 | 20.1978 | 57.6098 | 23.2103 | 62.9846 | 21.2639 | 63.5899 | 0.37087 | 19.9904 | 0.69439 | 0.020691 | -27.0531 | 3.0955 | 59.13 | 51.63 | 1.1715 | -0.62897 | -6.2271 | 0.5774 | -0.090593 | -16.7567 | 5.0116 | 0.23897 | -0.32398 | 0.0994 | -1.1236 | -0.54581 | -0.019827 | 0.14318
42838.4224 | 187 | 22.9157 | 22.8776 | 22.866 | 22.7826 | 22.4034 | 21.7403 | 22.7208 | 21.7917 | 22.3663 | 22.3743 | 22.3464 | 22.0036 | 21.2125 | 22.1785 | 21.606 | 21.7833 | 21.8998 | 21.0808 | 21.1867 | 21.4012 | 20.4747 | 20.6469 | 21.1419 | 21.8727 | 21.6298 | 22.231 | 92.4987 | 83.8148 | 96.5883 | 22.0963 | 21.686 | 21.7737 | 22.005 | 21.7473 | 22.1461 | 29.7048 | 85.861 |  | 45.1864 | 72.6161 | 78.2157 | 47.3118 |  | 16.963 | 17.0908 | 16.625 | 17.0502 | 17.43 | 19.0139 | 44.387 | 15.7352 | 17.0417 | 15.6605 | 17.4777 | 18.1211 | 44.0718 | 46.7734 | 43.2092 | 21.5724 |  |  | 0.76446 | -0.38908 | -27.484 | 0.37845 | 0.18478 | -197.8939 | 18.0847 | 0.34791 | 0.10304 | 0.10564 | 0.011749 | 0.00031377 | 0.0003187 | 1.8661 | 21.7686 | 21.991 | 22.1844 | 22.2462 | 22.0493 | 21.3563 | 20.1711 | 22.1855 | 22.366 | 22.3996 | 22.3407 | 21.9614 | 21.2008 | 22.2704 | 42.2729 | 31.496 | 29.2298 | 23.3038 | 21.721 | 26.8072 | 21.2914 | 22.3594 | 22.1325 | 21.6811 | 22.0743 | 21.7874 | 21.2916 | 21.9435 | 21.5467 | 21.2069 | 29.4361 | 92.7056 | 65.7418 | 41.5413 | 0.13508 | -0.014234 | 37.9474 | 22.0003 | 22.3192 | 20.1663 | 21.6217 | 22.0629 | 21.9165 | 21.6939 | 22.896 | 21.7573 | 21.4284 | 21.526 | 85.4021 | 103.117 | 64.9425 | 66.1267 | 37.8836 |  | 29.0044 | 60.2472 | 31.1701 | 43.7496 | 29.7759 | 36.403 |  | 38.7249 |  |  | 21.1143 | 21.9483 | 34.9371 | [5 empty] | 21.8914 | 31.7063 | 21.6538 | 22.0335 | 25.9014 | 21.162 | 21.8039 | 21.6353 | 39.0827 | 111.2428 |  | 31.9305 | 78.587 | 19.9826 | 33.2808 | 82.2413 | 26.873 | 65.5378 | 21.1771 | 60.6397 | 21.2089 | 63.2322 | 18.5944 | 34.1077 | 74.6235 | 22.5418 | 34.5208 | 99.69 | 20.1301 | 33.2346 | 84.8654 | 20.2003 | 57.8305 | 23.2371 | 63.1505 | 21.2659 | 63.764 | 0.19223 | 19.9862 | 0.697 | 0.020814 | -27.0284 | 3.0955 | 78.11 | 51.54 | 1.1716 | -0.74057 | -6.2242 | 0.73039 | 0.51204 | -16.757 | 5.0657 | 0.22596 | -0.3214 | 0.089294 | -1.2594 | -0.45588 | -0.012082 | 0.13906
42838.4225 | 188 | 22.9111 | 22.8748 | 22.868 | 22.7849 | 22.3961 | 21.7326 | 22.7165 | 21.7861 | 22.3596 | 22.3737 | 22.3427 | 22.0061 | 21.2124 | 22.1759 | 21.616 | 21.7865 | 21.9062 | 21.0878 | 21.1851 | 21.4027 | 20.485 | 20.6463 | 21.1561 | 21.8722 | 21.6364 | 22.2509 | 92.5382 | 84.0178 | 96.4085 | 22.1023 | 21.6949 | 21.7872 | 22.0102 | 21.7453 | 22.1627 | 29.7788 | 85.3625 |  | 45.3309 | 72.7399 | 78.3131 | 47.2509 |  | 16.9739 | 17.0986 | 16.6249 | 17.0493 | 17.4202 | 19.0453 | 44.1137 | 15.7151 | 17.0426 | 15.7364 | 17.4891 | 18.1161 | 44.0709 | 46.7611 | 43.2023 | 21.5665 |  |  | 0.77234 | -0.35622 | -27.1081 | 0.39883 | 0.34052 | -197.8269 | 18.2346 | 0.41428 | 0.0010664 | 0.2053 | 0.018519 | 0.00033842 | 0.00034006 | 1.8824 | 21.777 | 21.9935 | 22.1888 | 22.247 | 22.047 | 21.3533 | 20.1689 | 22.1904 | 22.3665 | 22.3933 | 22.3519 | 21.9726 | 21.202 | 22.2746 | 42.2599 | 30.8 | 29.5804 | 23.4776 | 21.6198 | 26.8773 | 21.331 | 22.3635 | 22.1245 | 21.6948 | 22.0756 | 21.7869 | 21.2917 | 21.9402 | 21.5493 | 21.2179 | 29.506 | 92.8594 | 65.968 | 41.8301 | 0.012005 | -0.008528 | 38.0679 | 22.0119 | 22.3227 | 20.1685 | 21.6339 | 22.0683 | 21.9269 | 21.7077 | 22.925 | 21.7652 | 21.4454 | 21.541 | 85.5504 | 103.199 | 65.0815 | 66.2672 | 38.1627 |  | 29.0768 | 60.6237 | 31.2603 | 43.8827 | 29.8542 | 36.3445 |  | 38.8502 |  |  | 21.1062 | 21.965 | 34.8395 | [5 empty] | 21.8906 | 31.7447 | 21.6424 | 22.0299 | 25.9139 | 21.1624 | 21.7959 | 21.6393 | 39.1526 | 111.2957 |  | 32.1166 | 78.6898 | 19.9829 | 33.3261 | 82.4325 | 26.9251 | 65.724 | 21.1826 | 60.7756 | 21.2132 | 63.3738 | 18.6002 | 34.2479 | 74.79 | 22.5616 | 34.6486 | 99.6879 | 20.1385 | 33.2313 | 85.1042 | 20.2178 | 58.0182 | 23.2457 | 63.4165 | 21.2799 | 63.9097 | 0.25697 | 19.9806 | 0.69988 | 0.020335 | -27.0546 | 3.0955 | 69.34 | 52.37 | 1.1774 | -0.70862 | -6.1816 | 0.7498 | 0.69514 | -16.7551 | 5.0869 | 0.22067 | -0.32877 | 0.088264 | -1.2497 | -0.49021 | -0.0078664 | 0.13342
42838.4225 | 189 | 22.9099 | 22.8758 | 22.8686 | 22.7834 | 22.4002 | 21.7357 | 22.7154 | 21.786 | 22.3605 | 22.3733 | 22.3449 | 22.0049 | 21.2097 | 22.1787 | 21.6075 | 21.7788 | 21.9022 | 21.0867 | 21.1821 | 21.3987 | 20.4826 | 20.6473 | 21.1647 | 21.8777 | 21.6279 | 22.2677 | 92.5863 | 84.155 | 96.3145 | 22.1021 | 21.6984 | 21.8028 | 22.0051 | 21.7431 | 22.1737 | 29.8582 | 85.0245 |  | 45.4901 | 72.89 | 78.4304 | 47.2197 |  | 16.9719 | 17.0902 | 16.6249 | 17.0454 | 17.4061 | 19.0333 | 43.7173 | 15.6863 | 17.0427 | 15.7308 | 17.4828 | 18.1098 | 44.0692 | 46.7622 | 43.198 | 21.5651 |  |  | 0.90705 | -0.19654 | -26.9793 | 0.36071 | 0.30438 | -197.8532 | 18.1163 | 0.48788 | -0.0098312 | -0.12724 | 0.17059 | 0.00036141 | 0.00033677 | 1.8805 | 21.7692 | 21.9927 | 22.1852 | 22.2302 | 22.0488 | 21.3455 | 20.1699 | 22.1867 | 22.3547 | 22.3902 | 22.3465 | 21.9611 | 21.1935 | 22.272 | 41.0748 | 28.3708 | 28.7083 | 23.2535 | 21.7455 | 26.9268 | 21.3613 | 22.3593 | 22.1295 | 21.6913 | 22.0745 | 21.7866 | 21.291 | 21.944 | 21.5402 | 21.228 | 29.57 | 93.1012 | 66.2004 | 42.037 | 0.099492 | -0.09564 | 38.0413 | 22.0101 | 22.3308 | 20.17 | 21.63 | 22.0707 | 21.9251 | 21.7036 | 22.9434 | 21.7675 | 21.4423 | 21.5475 | 85.7114 | 103.2669 | 65.2163 | 66.4011 | 38.1525 |  | 29.1563 | 61.2237 | 31.332 | 43.8097 | 29.941 | 36.3929 |  | 38.9641 |  |  | 21.1076 | 21.9848 | 34.6616 | [5 empty] | 21.8997 | 31.8649 | 21.6611 | 22.0346 | 25.9439 | 21.1721 | 21.806 | 21.6448 | 39.2706 | 111.1279 |  | 32.2133 | 78.8965 | 19.9959 | 33.4127 | 82.6962 | 26.976 | 65.8939 | 21.1957 | 60.9222 | 21.2247 | 63.4467 | 18.5915 | 34.3642 | 74.9222 | 22.565 | 34.7096 | 99.7877 | 20.1255 | 33.2815 | 85.2079 | 20.2138 | 58.1486 | 23.2496 | 63.6122 | 21.2926 | 64.2372 | 0.11636 | 19.9768 | 0.70362 | 0.020814 | -27.0781 | 3.0955 | 60.45 | 51.75 | 1.2758 | -0.52635 | -6.1668 | 0.71306 | 0.6572 | -16.7558 | 5.0702 | 0.22366 | -0.34299 | 0.09325 | -1.1123 | -0.38977 | -0.0042936 | 0.12985
42838.4225 | 190 | 22.9124 | 22.8764 | 22.8615 | 22.7835 | 22.4001 | 21.7356 | 22.7227 | 21.7858 | 22.3635 | 22.3716 | 22.3465 | 22.0055 | 21.2143 | 22.1819 | 21.6083 | 21.7834 | 21.9104 | 21.0888 | 21.1893 | 21.399 | 20.4772 | 20.6472 | 21.1608 | 21.8799 | 21.6352 | 22.2777 | 92.7042 | 84.237 | 96.3915 | 22.1094 | 21.6973 | 21.8098 | 22.0105 | 21.7479 | 22.1789 | 29.9319 | 85.3531 |  | 45.6382 | 73.0622 | 78.5467 | 47.0284 |  | 16.9769 | 17.094 | 16.6291 | 17.0433 | 17.3981 | 18.9998 | 43.9739 | 15.6734 | 17.0398 | 15.6779 | 17.49 | 18.117 | 44.082 | 46.7673 | 43.1878 | 21.5639 |  |  | 0.74934 | -0.060521 | -26.4891 | 0.4054 | 0.037588 | -197.821 | 18.0519 | 0.30914 | 0.091555 | 0.028224 | 0.078064 | 0.00035649 | 0.00031213 | 1.8601 | 21.7725 | 21.9914 | 22.1846 | 22.2392 | 22.0581 | 21.3537 | 20.1745 | 22.1846 | 22.3674 | 22.4066 | 22.3456 | 21.972 | 21.2042 | 22.2722 | 40.0248 | 26.6278 | 27.7187 | 22.5578 | 21.5958 | 26.9756 | 21.3926 | 22.3554 | 22.1279 | 21.6858 | 22.0739 | 21.7865 | 21.2941 | 21.9388 | 21.5392 | 21.2169 | 29.6316 | 93.1871 | 66.4788 | 42.1439 | 0.050932 | -0.11067 | 38.0092 | 22.0085 | 22.33 | 20.1638 | 21.6299 | 22.0723 | 21.922 | 21.7048 | 22.9673 | 21.7702 | 21.4365 | 21.5532 | 85.812 | 103.364 | 65.3956 | 66.5772 | 38.1518 |  | 29.2248 | 61.5035 | 31.3959 | 43.9612 | 30.0149 | 36.3216 |  | 39.089 |  |  | 21.1146 | 21.9948 | 34.6056 | [5 empty] | 21.8987 | 31.9953 | 21.6508 | 22.0324 | 25.9716 | 21.1775 | 21.8035 | 21.6648 | 39.3978 | 110.9721 |  | 32.2559 | 79.105 | 20.0035 | 33.5861 | 82.8651 | 26.9824 | 66.066 | 21.196 | 61.1 | 21.2399 | 63.5583 | 18.5993 | 34.427 | 75.0343 | 22.5752 | 34.7506 | 99.8433 | 20.1418 | 33.3615 | 85.2365 | 20.2155 | 58.3969 | 23.2623 | 63.6884 | 21.3009 | 64.6412 | 0.26012 | 19.9738 | 0.7072 | 0.021329 | -27.0639 | 3.0955 | 38.6 | 52.54 | 1.1597 | -0.29208 | -6.1106 | 0.75594 | 0.23094 | -16.7535 | 5.0609 | 0.22601 | -0.34858 | 0.09156 | -0.98987 | -0.27616 | 0.0035335 | 0.12898
42838.4225 | 191 | 22.9151 | 22.878 | 22.856 | 22.7766 | 22.3974 | 21.729 | 22.7177 | 21.7816 | 22.357 | 22.3714 | 22.3432 | 21.9972 | 21.2072 | 22.1746 | 21.61 | 21.788 | 21.9074 | 21.0932 | 21.1895 | 21.4028 | 20.4833 | 20.6415 | 21.1707 | 21.8717 | 21.631 | 22.294 | 92.9613 | 84.2448 | 97.3102 | 22.1156 | 21.7026 | 21.8247 | 22.0107 | 21.7502 | 22.1914 | 30.0278 | 85.578 |  | 45.753 | 73.2306 | 78.64 | 47.2014 |  | 16.9728 | 17.0893 | 16.6326 | 17.0365 | 17.3886 | 18.9667 | 44.409 | 15.7217 | 17.0346 | 15.6449 | 17.4933 | 18.1233 | 44.0863 | 46.7752 | 43.191 | 21.5721 |  |  | 0.7592 | -0.23006 | -25.5271 | 0.36269 | 0.15127 | -197.8388 | 19.0796 | 0.25657 | 0.063338 | -0.033876 | 0.080842 | 0.0003647 | 0.00034334 | 1.8532 | 21.7779 | 21.9916 | 22.1848 | 22.2349 | 22.0559 | 21.3585 | 20.1755 | 22.1885 | 22.3647 | 22.3985 | 22.3475 | 21.9752 | 21.2046 | 22.2735 | 39.6728 | 26.3235 | 26.6514 | 22.3313 | 21.0711 | 27.0325 | 21.4058 | 22.3521 | 22.1262 | 21.68 | 22.0729 | 21.7912 | 21.2881 | 21.9354 | 21.5424 | 21.2264 | 29.7049 | 93.5305 | 66.9639 | 42.346 | 0.19347 | -0.035536 | 38.0259 | 22.0111 | 22.3258 | 20.1604 | 21.6259 | 22.0621 | 21.9283 | 21.7038 | 22.9868 | 21.7698 | 21.4349 | 21.5623 | 85.9107 | 103.44 | 65.5701 | 66.7556 | 38.654 |  | 29.3043 | 61.3854 | 31.4769 | 44.2377 | 30.1167 | 36.6527 |  | 39.2164 |  |  | 21.1036 | 21.9916 | 34.4746 | [5 empty] | 21.8978 | 32.1339 | 21.6467 | 22.0316 | 25.9732 | 21.1752 | 21.8043 | 21.6776 | 39.5162 | 110.9885 |  | 32.3603 | 79.2994 | 20.0215 | 33.6891 | 83.0375 | 27 | 66.2171 | 21.21 | 61.2235 | 21.2467 | 63.7293 | 18.6128 | 34.4677 | 75.0805 | 22.6062 | 34.8598 | 99.8707 | 20.1516 | 33.4378 | 85.3181 | 20.2268 | 58.5867 | 23.2797 | 63.8595 | 21.3245 | 64.8718 | 0.21727 | 19.9712 | 0.71114 | 0.021496 | -27.1144 | 3.0955 | 35.05 | 51.56 | 1.1687 | -0.56946 | -5.9985 | 0.71501 | 0.46325 | -16.7533 | 5.2027 | 0.21477 | -0.34253 | 0.087354 | -0.94409 | -0.15602 | 0.0019971 | 0.12586
42838.4225 | 192 | 22.9129 | 22.8804 | 22.8635 | 22.7887 | 22.4048 | 21.7383 | 22.7257 | 21.7846 | 22.3699 | 22.3791 | 22.3474 | 22.0067 | 21.2114 | 22.1785 | 21.6128 | 21.7871 | 21.9051 | 21.0927 | 21.1815 | 21.406 | 20.482 | 20.6443 | 21.1713 | 21.8712 | 21.638 | 22.3112 | 93.1173 | 84.2734 | 97.1894 | 22.1103 | 21.6913 | 21.823 | 22.0071 | 21.7476 | 22.2115 | 30.1132 | 85.7214 |  | 45.8536 | 73.3719 | 78.7608 | 47.7494 |  | 16.9715 | 17.0889 | 16.6226 | 17.0367 | 17.3775 | 18.9201 | 44.3862 | 15.7697 | 17.0384 | 15.6099 | 17.495 | 18.1244 | 44.0941 | 46.7826 | 43.1879 | 21.5704 |  |  | 0.76709 | -0.4929 | -25.7519 | 0.52368 | 0.47391 | -197.8473 | 19.2906 | 0.7067 | 0.23069 | -0.0019868 | 0.10827 | 0.00035484 | 0.00036141 | 1.8537 | 21.779 | 21.9932 | 22.1952 | 22.2418 | 22.0618 | 21.3629 | 20.1778 | 22.1956 | 22.3592 | 22.4009 | 22.3452 | 21.9789 | 21.1997 | 22.2785 | 39.6485 | 25.9339 | 26.3021 | 22.1518 | 20.9858 | 27.0808 | 21.4133 | 22.3598 | 22.1302 | 21.6842 | 22.0675 | 21.7931 | 21.2912 | 21.9436 | 21.5416 | 21.2408 | 29.7863 | 93.6437 | 67.3114 | 42.0648 | 0.023801 | -0.12512 | 37.9121 | 22.0044 | 22.3176 | 20.1608 | 21.625 | 22.0635 | 21.9241 | 21.7058 | 23.0071 | 21.7646 | 21.4293 | 21.5689 | 86.0312 | 103.553 | 65.7137 | 66.8724 | 38.9492 |  | 29.3803 | 61.2869 | 31.536 | 44.1715 | 30.1936 | 36.8703 |  | 39.3297 |  |  | 21.097 | 22.001 | 34.2739 | [5 empty] | 21.895 | 32.2441 | 21.6502 | 22.0281 | 25.9941 | 21.172 | 21.8074 | 21.6926 | 39.6059 | 110.9746 |  | 32.5569 | 79.4336 | 20.0358 | 33.7289 | 83.0757 | 27.0426 | 66.3533 | 21.2258 | 61.4256 | 21.252 | 63.8803 | 18.6074 | 34.5099 | 75.0555 | 22.6185 | 34.9855 | 99.9478 | 20.1563 | 33.4663 | 85.4613 | 20.2331 | 58.7266 | 23.2961 | 64.0868 | 21.3353 | 65.0111 | 0.38051 | 19.9675 | 0.71497 | 0.021758 | -27.0908 | 3.0955 | 44.37 | 52.44 | 1.1746 | -0.83354 | -6.0249 | 0.85917 | 0.8199 | -16.7523 | 5.231 | 0.20916 | -0.33777 | 0.091817 | -0.93572 | -0.11632 | -0.010315 | 0.13645
42838.4225 | 193 | 22.9095 | 22.881 | 22.8677 | 22.788 | 22.3979 | 21.7372 | 22.7138 | 21.7927 | 22.3642 | 22.3712 | 22.3441 | 22.0028 | 21.2209 | 22.1808 | 21.6068 | 21.7824 | 21.9035 | 21.0865 | 21.1797 | 21.403 | 20.4799 | 20.6438 | 21.1742 | 21.8674 | 21.6339 | 22.3262 | 93.2321 | 84.3119 | 97.2604 | 22.1104 | 21.7086 | 21.8389 | 22.0121 | 21.7526 | 22.2286 | 30.2049 | 85.9541 |  | 45.9844 | 73.5285 | 78.8921 | 48.2639 |  | 16.9673 | 17.0868 | 16.6275 | 17.0314 | 17.3652 | 18.8909 | 44.5274 | 15.7835 | 17.0434 | 15.5669 | 17.5089 | 18.1224 | 44.0882 | 46.7811 | 43.1816 | 21.5709 |  |  | 0.78548 | -0.36411 | -25.6355 | 0.45731 | 0.30306 | -197.8545 | 19.3247 | 0.44254 | 0.047965 | 0.011021 | 0.11452 | 0.00034006 | 0.00031706 | 1.8699 | 21.7787 | 21.9955 | 22.1928 | 22.2372 | 22.0606 | 21.3625 | 20.1756 | 22.1951 | 22.3594 | 22.4078 | 22.3471 | 21.9775 | 21.2024 | 22.2765 | 38.8632 | 25.1189 | 26.1611 | 22.0862 | 20.9312 | 27.1251 | 21.4488 | 22.3544 | 22.1255 | 21.6822 | 22.0807 | 21.7872 | 21.2887 | 21.9412 | 21.543 | 21.2453 | 29.8571 | 93.8087 | 67.4656 | 41.7007 | -0.076662 | -0.1759 | 37.8613 | 22.0045 | 22.3189 | 20.1671 | 21.6307 | 22.0723 | 21.9223 | 21.7018 | 23.0383 | 21.7667 | 21.4401 | 21.581 | 86.139 | 103.7059 | 65.8494 | 66.9788 | 38.9907 |  | 29.4472 | 61.289 | 31.5909 | 43.9868 | 30.2653 | 36.8019 |  | 39.4516 |  |  | 21.0961 | 22.0135 | 34.2145 | [5 empty] | 21.8875 | 32.3443 | 21.6436 | 22.0239 | 26.0178 | 21.1653 | 21.803 | 21.6903 | 39.6706 | 111.1654 |  | 32.7431 | 79.4749 | 20.035 | 33.766 | 83.2236 | 27.0778 | 66.4622 | 21.2287 | 61.6674 | 21.2538 | 64.0101 | 18.6147 | 34.5675 | 75.1199 | 22.6347 | 35.0855 | 100.0882 | 20.1753 | 33.5527 | 85.6166 | 20.2457 | 58.8585 | 23.3165 | 64.3069 | 21.3542 | 65.1655 | 0.16274 | 19.9607 | 0.71836 | 0.021525 | -27.0743 | 3.0955 | 51.28 | 52.5 | 1.1887 | -0.71641 | -6.0112 | 0.80288 | 0.65562 | -16.7518 | 5.2353 | 0.21029 | -0.33595 | 0.099389 | -0.84327 | -0.096512 | -0.021479 | 0.14897
42838.4225 | 194 | 22.9147 | 22.8731 | 22.8584 | 22.7858 | 22.4008 | 21.7349 | 22.7282 | 21.7961 | 22.3726 | 22.3686 | 22.3466 | 22.0014 | 21.2155 | 22.1777 | 21.6069 | 21.7749 | 21.8999 | 21.0848 | 21.1914 | 21.3969 | 20.4736 | 20.6412 | 21.1784 | 21.8659 | 21.6276 | 22.3335 | 93.3892 | 84.3562 | 97.5991 | 22.1177 | 21.7109 | 21.8443 | 22.0112 | 21.7626 | 22.2395 | 30.2858 | 85.8845 |  | 46.1154 | 73.6311 | 79.023 | 48.3492 |  | 16.9627 | 17.0781 | 16.628 | 17.0205 | 17.3596 | 18.8654 | 45.1711 | 15.8133 | 17.0428 | 15.5333 | 17.5021 | 18.1271 | 44.0824 | 46.791 | 43.1865 | 21.572 |  |  | 0.77103 | -0.13412 | -25.512 | 0.48688 | 0.14207 | -197.7921 | 19.491 | 0.61273 | 0.18438 | 0.090535 | 0.13344 | 0.00035813 | 0.00031542 | 1.8835 | 21.7811 | 21.9942 | 22.1882 | 22.2445 | 22.0586 | 21.3599 | 20.1736 | 22.1897 | 22.3644 | 22.4108 | 22.3504 | 21.9737 | 21.2021 | 22.2764 | 37.9366 | 24.2067 | 25.498 | 22.0093 | 20.9837 | 27.1481 | 21.4626 | 22.3496 | 22.1194 | 21.6808 | 22.0721 | 21.7856 | 21.2841 | 21.9336 | 21.5446 | 21.251 | 29.9244 | 93.8573 | 67.5651 | 41.4139 | 0.19484 | -0.082516 | 37.9152 | 22 | 22.3153 | 20.1685 | 21.6247 | 22.07 | 21.9219 | 21.6986 | 23.0541 | 21.7659 | 21.4411 | 21.5862 | 86.2022 | 103.7559 | 65.9578 | 67.0604 | 38.9288 |  | 29.5263 | 61.547 | 31.6443 | 44.0351 | 30.3458 | 36.6728 |  | 39.5644 |  |  | 21.1002 | 22.0309 | 34.2625 | [5 empty] | 21.8938 | 32.4476 | 21.6517 | 22.0339 | 26.0367 | 21.1727 | 21.803 | 21.7046 | 39.7493 | 111.2001 |  | 32.8284 | 79.5294 | 20.05 | 33.8868 | 83.384 | 27.121 | 66.543 | 21.2361 | 61.9092 | 21.2719 | 64.1119 | 18.6052 | 34.6056 | 75.2129 | 22.6455 | 35.1629 | 100.1795 | 20.1786 | 33.6715 | 85.7204 | 20.2486 | 59.0297 | 23.3327 | 64.5344 | 21.3671 | 65.3507 | 0.25159 | 19.9555 | 0.72183 | 0.021337 | -27.043 | 3.0955 | 58.65 | 51.44 | 1.1783 | -0.43479 | -5.9967 | 0.82841 | 0.44887 | -16.7484 | 5.2576 | 0.2147 | -0.34129 | 0.10079 | -0.73762 | -0.02121 | -0.021087 | 0.15924
42838.4225 | 195 | 22.9083 | 22.8721 | 22.8537 | 22.7835 | 22.4006 | 21.7295 | 22.7236 | 21.7875 | 22.3665 | 22.368 | 22.3405 | 21.9931 | 21.2111 | 22.1775 | 21.609 | 21.7794 | 21.9058 | 21.0879 | 21.1949 | 21.3955 | 20.4736 | 20.6442 | 21.1833 | 21.8645 | 21.6311 | 22.3488 | 93.5801 | 84.4613 | 98.1963 | 22.1183 | 21.7085 | 21.8634 | 22.0245 | 21.7589 | 22.2492 | 30.3632 | 86.3638 |  | 46.2572 | 73.7211 | 79.1443 | 48.4629 |  | 16.955 | 17.0832 | 16.6198 | 17.0215 | 17.3421 | 18.8178 | 45.7394 | 15.8392 | 17.0457 | 15.5185 | 17.5011 | 18.1242 | 44.0731 | 46.7909 | 43.1797 | 21.5682 |  |  | 0.80257 | -0.33322 | -25.2084 | 0.50002 | 0.084244 | -197.8953 | 19.6894 | 0.45108 | 0.23128 | 0.048995 | 0.12997 | 0.00037784 | 0.00032035 | 1.8887 | 21.7749 | 21.9787 | 22.1884 | 22.2472 | 22.054 | 21.3542 | 20.1667 | 22.191 | 22.3622 | 22.4029 | 22.353 | 21.9728 | 21.2034 | 22.2772 | 37.6679 | 24.0856 | 24.9596 | 21.6536 | 20.9011 | 27.1679 | 21.4674 | 22.353 | 22.1264 | 21.6769 | 22.0684 | 21.784 | 21.2842 | 21.9407 | 21.5418 | 21.258 | 30.0052 | 93.9899 | 67.6723 | 41.3217 | 0.15533 | -0.13083 | 37.8674 | 22.0057 | 22.3119 | 20.1663 | 21.6247 | 22.0656 | 21.9185 | 21.7032 | 23.0719 | 21.766 | 21.4403 | 21.5911 | 86.3233 | 103.7963 | 66.0463 | 67.1271 | 38.8394 |  | 29.5979 | 62.1098 | 31.7152 | 44.3834 | 30.4309 | 36.7817 |  | 39.6931 |  |  | 21.1019 | 22.0378 | 34.252 | [5 empty] | 21.8977 | 32.4883 | 21.6543 | 22.0425 | 26.0493 | 21.1797 | 21.81 | 21.712 | 39.8619 | 111.4577 |  | 32.8197 | 79.675 | 20.0594 | 34.0718 | 83.4992 | 27.1634 | 66.6583 | 21.2448 | 62.0998 | 21.2855 | 64.1762 | 18.6021 | 34.6645 | 75.2577 | 22.6533 | 35.2606 | 100.2139 | 20.1857 | 33.7233 | 85.7989 | 20.2574 | 59.2158 | 23.3542 | 64.8106 | 21.3807 | 65.5707 | 0.21598 | 19.9485 | 0.72491 | 0.022491 | -27.0758 | 3.0955 | 55.66 | 52.93 | 1.2031 | -0.68535 | -5.9609 | 0.83953 | 0.34562 | -16.7514 | 5.2839 | 0.21962 | -0.3545 | 0.094024 | -0.70544 | 0.039167 | -0.021607 | 0.16455
42838.4225 | 196 | 22.9113 | 22.878 | 22.8626 | 22.7814 | 22.4024 | 21.7328 | 22.7219 | 21.789 | 22.3659 | 22.3722 | 22.3417 | 21.9963 | 21.2098 | 22.1833 | 21.6077 | 21.7832 | 21.9129 | 21.0918 | 21.1876 | 21.3945 | 20.4872 | 20.6482 | 21.1903 | 21.8689 | 21.6334 | 22.3632 | 93.7919 | 84.6173 | 98.5465 | 22.1112 | 21.6968 | 21.8696 | 22.0121 | 21.7499 | 22.2499 | 30.4267 | 86.5327 |  | 46.3782 | 73.8188 | 79.232 | 48.7088 |  | 16.9592 | 17.0778 | 16.6097 | 17.0098 | 17.3285 | 18.7978 | 45.8763 | 15.8932 | 17.0383 | 15.5641 | 17.4996 | 18.1268 | 44.072 | 46.7951 | 43.177 | 21.5689 |  |  | 0.7362 | -0.43968 | -25.5777 | 0.42379 | 0.19858 | -197.8342 | 19.4266 | 0.36697 | 0.02617 | 0.17005 | 0.17181 | 0.00037127 | 0.00032199 | 1.8848 | 21.7649 | 21.981 | 22.1817 | 22.2397 | 22.061 | 21.3457 | 20.1657 | 22.1801 | 22.3613 | 22.3974 | 22.3529 | 21.9694 | 21.1984 | 22.2729 | 37.1277 | 24.1741 | 25.33 | 21.6458 | 20.7076 | 27.2018 | 21.4785 | 22.3514 | 22.1241 | 21.674 | 22.0686 | 21.7784 | 21.288 | 21.9374 | 21.5409 | 21.2592 | 30.0681 | 94.1586 | 67.8907 | 41.5763 | 0.17597 | -0.25541 | 37.9022 | 22.0037 | 22.3105 | 20.1645 | 21.62 | 22.0621 | 21.9184 | 21.7018 | 23.093 | 21.7696 | 21.4392 | 21.5993 | 86.444 | 103.7981 | 66.1179 | 67.1843 | 38.8343 |  | 29.6727 | 61.9999 | 31.7899 | 44.5171 | 30.5142 | 36.8749 |  | 39.8076 |  |  | 21.1063 | 22.0373 | 34.3645 | [5 empty] | 21.9003 | 32.4783 | 21.6569 | 22.0382 | 26.063 | 21.1792 | 21.8154 | 21.7146 | 39.9922 | 111.7806 |  | 32.808 | 79.7724 | 20.0689 | 34.2004 | 83.5985 | 27.1971 | 66.7964 | 21.2574 | 62.2194 | 21.3 | 64.305 | 18.6071 | 34.7775 | 75.3573 | 22.6681 | 35.3946 | 100.181 | 20.1933 | 33.6958 | 85.9075 | 20.26 | 59.3557 | 23.3732 | 65.0111 | 21.4011 | 65.7108 | 0.32672 | 19.9424 | 0.72874 | 0.02175 | -27.1106 | 3.0954 | 25.75 | 51.76 | 1.1528 | -0.78723 | -6.0044 | 0.77288 | 0.53062 | -16.7483 | 5.2483 | 0.22231 | -0.34889 | 0.093151 | -0.64145 | -0.00069638 | -0.026271 | 0.15962
42838.4226 | 197 | 22.9176 | 22.881 | 22.8718 | 22.7824 | 22.396 | 21.7384 | 22.7244 | 21.7884 | 22.3669 | 22.3705 | 22.3413 | 22.0052 | 21.2131 | 22.1811 | 21.6047 | 21.7806 | 21.9 | 21.0899 | 21.1823 | 21.3977 | 20.4863 | 20.6464 | 21.1944 | 21.8701 | 21.635 | 22.3755 | 93.8877 | 84.7584 | 98.3438 | 22.1043 | 21.6994 | 21.876 | 22.0067 | 21.7495 | 22.2627 | 30.5046 | 86.3519 |  | 46.4964 | 73.935 | 79.34 | 48.8805 |  | 16.9644 | 17.0704 | 16.6035 | 17.0119 | 17.3208 | 18.7842 | 46.4576 | 15.9079 | 17.0406 | 15.6239 | 17.5003 | 18.1288 | 44.0777 | 46.8085 | 43.1938 | 21.5748 |  |  | 0.81308 | -0.2938 | -26.0607 | 0.64721 | 0.23538 | -197.8591 | 19.6894 | 0.40574 | 0.25229 | 0.21222 | 0.12494 | 0.00034663 | 0.0002957 | 1.8764 | 21.7683 | 21.9905 | 22.1891 | 22.2398 | 22.0585 | 21.3596 | 20.1669 | 22.1879 | 22.3553 | 22.4009 | 22.3417 | 21.9751 | 21.2029 | 22.2738 | 36.831 | 24.1432 | 24.9049 | 21.7741 | 20.5943 | 27.2513 | 21.4945 | 22.3548 | 22.1259 | 21.6819 | 22.0784 | 21.7871 | 21.2894 | 21.9403 | 21.5423 | 21.2738 | 30.1509 | 94.3387 | 68.2799 | 42.0034 | 0.4921 | -0.019179 | 38.0041 | 22.0058 | 22.3144 | 20.1673 | 21.6203 | 22.0642 | 21.9223 | 21.7079 | 23.1235 | 21.7711 | 21.4416 | 21.6123 | 86.521 | 103.8013 | 66.225 | 67.2897 | 38.9526 |  | 29.7487 | 61.5957 | 31.8469 | 44.4558 | 30.5898 | 36.8591 |  | 39.9229 |  |  | 21.106 | 22.0359 | 34.5104 | [5 empty] | 21.8993 | 32.5273 | 21.6548 | 22.0282 | 26.0826 | 21.1763 | 21.8161 | 21.7157 | 40.1233 | 112.0547 |  | 32.8334 | 79.8353 | 20.0821 | 34.2423 | 83.6621 | 27.2314 | 66.9623 | 21.2808 | 62.369 | 21.3103 | 64.4868 | 18.6061 | 34.8811 | 75.532 | 22.6852 | 35.5058 | 100.1303 | 20.205 | 33.7396 | 85.9641 | 20.2587 | 59.4558 | 23.39 | 65.2453 | 21.4048 | 65.8374 | 0.26736 | 19.9366 | 0.73193 | 0.01995 | -27.0615 | 3.0955 | 43.91 | 52.03 | 1.2112 | -0.64351 | -6.0607 | 0.95511 | 0.57769 | -16.7489 | 5.2836 | 0.22161 | -0.33571 | 0.097439 | -0.60268 | 0.048409 | -0.028383 | 0.15058
42838.4226 | 198 | 22.916 | 22.8778 | 22.8643 | 22.7844 | 22.4005 | 21.7308 | 22.7202 | 21.7858 | 22.3619 | 22.3688 | 22.3451 | 22.0004 | 21.2131 | 22.1782 | 21.6092 | 21.7762 | 21.8975 | 21.0858 | 21.1847 | 21.4001 | 20.4836 | 20.641 | 21.2014 | 21.8706 | 21.6342 | 22.3933 | 93.9302 | 84.8556 | 98.4669 | 22.1068 | 21.7066 | 21.886 | 22.01 | 21.7522 | 22.2781 | 30.5866 | 85.9101 |  | 46.6204 | 74.0776 | 79.4279 | 49.0403 |  | 16.9648 | 17.0687 | 16.6134 | 17.0118 | 17.3234 | 18.7807 | 46.6354 | 15.8877 | 17.0508 | 15.6849 | 17.5072 | 18.1338 | 44.0866 | 46.8188 | 43.2058 | 21.5739 |  |  | 0.60872 | -0.28525 | -26.3912 | 0.57165 | 0.19201 | -197.8558 | 19.2511 | 0.29337 | 0.033175 | 0.057387 | 0.073377 | 0.00034992 | 0.0003302 | 1.8791 | 21.7709 | 21.994 | 22.1872 | 22.2363 | 22.0546 | 21.3516 | 20.1607 | 22.1818 | 22.3632 | 22.3949 | 22.3443 | 21.9681 | 21.1981 | 22.2677 | 37.8357 | 25.0885 | 24.7924 | 21.7965 | 20.5246 | 27.3322 | 21.5144 | 22.3588 | 22.1313 | 21.69 | 22.0815 | 21.7971 | 21.2941 | 21.9481 | 21.5489 | 21.2792 | 30.2258 | 94.5884 | 68.5328 | 42.3115 | 0.41503 | -0.18028 | 37.9821 | 22.0014 | 22.313 | 20.1616 | 21.619 | 22.0647 | 21.9184 | 21.7034 | 23.1414 | 21.7704 | 21.438 | 21.6187 | 86.6147 | 104.0034 | 66.3459 | 67.4197 | 38.7072 |  | 29.8199 | 62.0753 | 31.9168 | 44.4453 | 30.6766 | 36.959 |  | 40.07 |  |  | 21.1117 | 22.0401 | 34.6623 | [5 empty] | 21.8999 | 32.5616 | 21.648 | 22.0293 | 26.0804 | 21.1791 | 21.8097 | 21.7263 | 40.2187 | 112.2183 |  | 32.9209 | 79.9013 | 20.0926 | 34.2625 | 83.7195 | 27.2722 | 67.1593 | 21.2926 | 62.5118 | 21.3171 | 64.6268 | 18.6112 | 34.9561 | 75.6572 | 22.7124 | 35.58 | 100.1534 | 20.2321 | 33.8477 | 86.0375 | 20.2781 | 59.5667 | 23.416 | 65.4706 | 21.4301 | 65.9703 | 0.23564 | 19.9316 | 0.734 | 0.02072 | -27.1443 | 3.0955 | 35.13 | 51.76 | 1.0481 | -0.63408 | -6.099 | 0.89762 | 0.52175 | -16.7487 | 5.2244 | 0.23086 | -0.34664 | 0.10069 | -0.70482 | 0.063238 | -0.030022 | 0.14458
42838.4226 | 199 | 22.9097 | 22.8775 | 22.8658 | 22.7815 | 22.4059 | 21.7293 | 22.7208 | 21.7887 | 22.3623 | 22.3724 | 22.3436 | 21.9918 | 21.2117 | 22.1769 | 21.6134 | 21.7733 | 21.9055 | 21.083 | 21.183 | 21.3981 | 20.4737 | 20.6431 | 21.2088 | 21.8626 | 21.6342 | 22.4102 | 94.0788 | 84.9017 | 98.7022 | 22.1149 | 21.7033 | 21.8959 | 22.0165 | 21.7511 | 22.2933 | 30.6781 | 86.3177 |  | 46.745 | 74.1974 | 79.5279 | 48.7883 |  | 16.9585 | 17.0834 | 16.6102 | 17.0057 | 17.323 | 18.7707 | 46.8599 | 15.9249 | 17.0494 | 15.723 | 17.511 | 18.1324 | 44.0931 | 46.8389 | 43.2258 | 21.58 |  |  | 0.70269 | -0.33388 | -26.0528 | 0.50265 | 0.19332 | -197.8381 | 19.3339 | 0.42019 | 0.15052 | 0.045638 | 0.12494 | 0.00032856 | 0.00031049 | 1.8749 | 21.7779 | 21.9878 | 22.1888 | 22.2421 | 22.0531 | 21.3507 | 20.1691 | 22.1915 | 22.365 | 22.3913 | 22.3459 | 21.9709 | 21.1984 | 22.2653 | 39.0448 | 26.1155 | 25.5983 | 21.7042 | 20.8588 | 27.4152 | 21.5321 | 22.3621 | 22.128 | 21.6824 | 22.0735 | 21.7924 | 21.2947 | 21.9479 | 21.5396 | 21.2816 | 30.2981 | 94.956 | 68.7598 | 42.3993 | 0.45514 | 0.12556 | 38.0341 | 22.0071 | 22.3191 | 20.1617 | 21.624 | 22.0665 | 21.9247 | 21.7071 | 23.1634 | 21.7703 | 21.4409 | 21.6341 | 86.8024 | 104.1666 | 66.4872 | 67.5632 | 38.7675 |  | 29.8911 | 62.7823 | 31.9934 | 44.5163 | 30.7494 | 36.8356 |  | 40.185 |  |  | 21.116 | 22.0534 | 34.8043 | [5 empty] | 21.9001 | 32.5762 | 21.6535 | 22.0377 | 26.1111 | 21.1841 | 21.8165 | 21.7278 | 40.3056 | 112.2494 |  | 33.0077 | 79.9477 | 20.0936 | 34.3935 | 83.7841 | 27.3073 | 67.3256 | 21.304 | 62.6106 | 21.3235 | 64.6807 | 18.612 | 35.053 | 75.7406 | 22.7223 | 35.6471 | 100.1957 | 20.2423 | 33.9367 | 86.1314 | 20.3031 | 59.6779 | 23.4334 | 65.6727 | 21.4422 | 66.0909 | 0.22711 | 19.9274 | 0.73651 | 0.019711 | -27.0883 | 3.0955 | 45.5 | 51.42 | 1.1265 | -0.68602 | -6.0599 | 0.84173 | 0.52353 | -16.7477 | 5.2355 | 0.23161 | -0.36366 | 0.1012 | -0.82944 | -0.024245 | -0.019898 | 0.14461
42838.4226 | 200 | 22.9095 | 22.866 | 22.8621 | 22.7821 | 22.4046 | 21.7381 | 22.7181 | 21.7785 | 22.3689 | 22.3757 | 22.3449 | 22.0039 | 21.2085 | 22.1768 | 21.6042 | 21.7765 | 21.909 | 21.0903 | 21.1827 | 21.4002 | 20.4774 | 20.6471 | 21.2127 | 21.8736 | 21.6371 | 22.4239 | 94.2032 | 84.9233 | 98.8894 | 22.1058 | 21.6985 | 21.9075 | 22.0051 | 21.7455 | 22.2999 | 30.7597 | 86.4176 |  | 46.8687 | 74.2891 | 79.6543 | 48.7888 |  | 16.9606 | 17.0827 | 16.6109 | 16.9935 | 17.3106 | 18.777 | 47.3921 | 15.9745 | 17.0468 | 15.7391 | 17.5123 | 18.1317 | 44.077 | 46.8486 | 43.2449 | 21.5807 |  |  | 0.819 | -0.21363 | -25.5061 | 0.62159 | 0.12498 | -197.8342 | 19.6316 | 0.24146 | 0.070928 | 0.10082 | 0.26382 | 0.00033513 | 0.00031542 | 1.8638 | 21.7872 | 21.9933 | 22.1953 | 22.2474 | 22.0632 | 21.3646 | 20.1792 | 22.197 | 22.3675 | 22.4036 | 22.3578 | 21.9747 | 21.2063 | 22.2767 | 40.3166 | 27.1058 | 26.9572 | 21.8542 | 20.8198 | 27.5114 | 21.5732 | 22.3577 | 22.1226 | 21.6831 | 22.0701 | 21.7896 | 21.2876 | 21.9446 | 21.5407 | 21.2887 | 30.3723 | 95.1981 | 69.0464 | 42.3061 | 0.62559 | 0.070976 | 38.1788 | 22.0062 | 22.3143 | 20.1608 | 21.6226 | 22.0646 | 21.9243 | 21.7055 | 23.1825 | 21.7631 | 21.4365 | 21.6409 | 86.9676 | 104.2277 | 66.6331 | 67.707 | 38.8016 |  | 29.9536 | 63.3757 | 32.0813 | 44.4818 | 30.8183 | 37.2429 |  | 40.2929 |  |  | 21.1078 | 22.0572 | 34.7649 | [5 empty] | 21.8994 | 32.5799 | 21.6557 | 22.0297 | 26.1258 | 21.1776 | 21.8093 | 21.7502 | 40.4222 | 112.5469 |  | 33.1026 | 80.137 | 20.12 | 34.6597 | 83.8315 | 27.3464 | 67.4772 | 21.326 | 62.6619 | 21.3448 | 64.7893 | 18.6114 | 35.1664 | 75.8657 | 22.7362 | 35.7339 | 100.2455 | 20.2531 | 34.0321 | 86.1405 | 20.3096 | 59.8177 | 23.4535 | 66.0599 | 21.4588 | 66.2545 | 0.25586 | 19.9235 | 0.741 | 0.019972 | -27.0462 | 3.0955 | 45.86 | 52.65 | 1.2165 | -0.54874 | -5.996 | 0.93603 | 0.42095 | -16.7477 | 5.2757 | 0.2328 | -0.37714 | 0.10452 | -0.95946 | -0.17043 | -0.017124 | 0.14973
42838.4226 | 201 | 22.9185 | 22.8712 | 22.8675 | 22.7827 | 22.4045 | 21.7385 | 22.7231 | 21.791 | 22.3719 | 22.3705 | 22.3465 | 22.0069 | 21.2104 | 22.1797 | 21.6065 | 21.7798 | 21.906 | 21.0935 | 21.1848 | 21.3903 | 20.4747 | 20.6513 | 21.2209 | 21.871 | 21.6417 | 22.4361 | 94.2946 | 84.9996 | 98.9549 | 22.1127 | 21.7019 | 21.9176 | 22.0042 | 21.7551 | 22.3219 | 30.8539 | 85.7766 |  | 46.9978 | 74.3859 | 79.719 | 49.1161 |  | 16.9544 | 17.0813 | 16.6097 | 16.9997 | 17.3111 | 18.8198 | 47.8294 | 15.9893 | 17.0527 | 15.7567 | 17.5214 | 18.1201 | 44.0785 | 46.8565 | 43.2645 | 21.5753 |  |  | 0.78614 | -0.33256 | -25.4713 | 0.54339 | 0.11973 | -197.8315 | 19.6986 | 0.36434 | 0.15169 | 0.16376 | 0.11799 | 0.0003762 | 0.00032692 | 1.8566 | 21.7792 | 21.9917 | 22.1954 | 22.2423 | 22.0587 | 21.3583 | 20.1748 | 22.188 | 22.3604 | 22.4038 | 22.3486 | 21.974 | 21.1989 | 22.2781 | 42.2188 | 28.8221 | 29.144 | 22.37 | 20.8518 | 27.6197 | 21.6204 | 22.3573 | 22.1282 | 21.6851 | 22.0759 | 21.7906 | 21.2898 | 21.946 | 21.5429 | 21.297 | 30.4526 | 95.3607 | 69.4191 | 42.2996 | 0.38712 | 0.020953 | 38.2505 | 21.9974 | 22.3104 | 20.1561 | 21.6162 | 22.0612 | 21.9115 | 21.6931 | 23.2006 | 21.754 | 21.4317 | 21.6424 | 87.0786 | 104.33 | 66.7553 | 67.8227 | 38.9574 |  | 30.0291 | 63.3668 | 32.1774 | 44.4477 | 30.8971 | 37.4749 |  | 40.4014 |  |  | 21.1113 | 22.0622 | 34.659 | [5 empty] | 21.8917 | 32.579 | 21.6477 | 22.0357 | 26.1447 | 21.1789 | 21.8099 | 21.7513 | 40.5572 | 112.8225 |  | 33.2186 | 80.3299 | 20.1149 | 34.8897 | 83.8381 | 27.3622 | 67.6178 | 21.3375 | 62.7371 | 21.3394 | 64.9401 | 18.6179 | 35.2489 | 76.0036 | 22.752 | 35.8272 | 100.4954 | 20.2676 | 34.0789 | 86.1603 | 20.3237 | 59.9812 | 23.482 | 66.2723 | 21.4684 | 66.5149 | 0.29555 | 19.9176 | 0.74397 | 0.021039 | -27.0533 | 3.0955 | 60.7 | 51.64 | 1.1919 | -0.68466 | -5.9919 | 0.87517 | 0.41203 | -16.7488 | 5.2851 | 0.23104 | -0.3736 | 0.10815 | -1.1581 | -0.40788 | -0.023002 | 0.15265
42838.4226 | 202 | 22.9013 | 22.8776 | 22.8569 | 22.7821 | 22.4008 | 21.7249 | 22.7184 | 21.7869 | 22.357 | 22.3707 | 22.3386 | 21.9967 | 21.2076 | 22.1752 | 21.605 | 21.7733 | 21.8919 | 21.0846 | 21.1836 | 21.4076 | 20.4787 | 20.65 | 21.2284 | 21.8774 | 21.6303 | 22.4575 | 94.3184 | 85.0853 | 98.4312 | 22.1124 | 21.6947 | 21.9259 | 22.0055 | 21.7478 | 22.3281 | 30.9408 | 86.2847 |  | 47.1251 | 74.5286 | 79.7876 | 49.5071 |  | 16.9627 | 17.0837 | 16.6209 | 16.9996 | 17.3074 | 18.9272 | 47.8955 | 15.9906 | 17.0581 | 15.7871 | 17.523 | 18.1309 | 44.0849 | 46.8724 | 43.2805 | 21.5771 |  |  | 1.0457 | -0.25634 | -25.4351 | 0.6321 | 0.25444 | -197.8348 | 19.5659 | 0.2546 | 0.12347 | 0.098717 | 0.083098 | 0.00033513 | 0.0003072 | 1.8456 | 21.7735 | 21.9904 | 22.1874 | 22.237 | 22.0526 | 21.3511 | 20.1714 | 22.1792 | 22.3639 | 22.399 | 22.3454 | 21.9671 | 21.2012 | 22.2663 | 43.2051 | 29.9792 | 30.8446 | 23.3801 | 21.2103 | 27.7333 | 21.684 | 22.3615 | 22.1294 | 21.6839 | 22.0832 | 21.7908 | 21.299 | 21.9467 | 21.5538 | 21.3074 | 30.5285 | 95.4052 | 69.6837 | 42.3543 | 0.4345 | 0.02723 | 38.3075 | 22.0032 | 22.3159 | 20.1625 | 21.6207 | 22.0572 | 21.9167 | 21.699 | 23.2337 | 21.7587 | 21.4439 | 21.6606 | 87.1932 | 104.3933 | 66.8753 | 67.9138 | 39.1676 |  | 30.1096 | 62.2043 | 32.2642 | 44.4924 | 30.9802 | 37.5105 |  | 40.5244 |  |  | 21.1285 | 22.0816 | 34.7899 | [5 empty] | 21.8956 | 32.5799 | 21.6522 | 22.0415 | 26.1853 | 21.1871 | 21.8148 | 21.7577 | 40.7019 | 112.9249 |  | 33.3009 | 80.4305 | 20.1265 | 35.0086 | 83.87 | 27.3563 | 67.7809 | 21.3187 | 62.789 | 21.3524 | 65.0826 | 18.6137 | 35.2785 | 76.1002 | 22.7537 | 35.949 | 100.8098 | 20.2822 | 34.1308 | 86.345 | 20.3352 | 60.1649 | 23.4881 | 66.425 | 21.4794 | 66.7088 | 0.24287 | 19.9152 | 0.74794 | 0.021634 | -27.0225 | 3.0954 | 61.09 | 52.55 | 1.3737 | -0.6011 | -5.9877 | 0.94392 | 0.60077 | -16.752 | 5.2682 | 0.22795 | -0.33834 | 0.10975 | -1.2544 | -0.5894 | -0.030894 | 0.15372
42838.4226 | 203 | 22.9019 | 22.875 | 22.8536 | 22.7756 | 22.3955 | 21.7239 | 22.7148 | 21.7808 | 22.3566 | 22.3662 | 22.3405 | 21.996 | 21.2024 | 22.1746 | 21.6064 | 21.771 | 21.9048 | 21.0854 | 21.1869 | 21.4036 | 20.4724 | 20.6496 | 21.2253 | 21.8641 | 21.6284 | 22.4636 | 94.4562 | 85.2039 | 98.8179 | 22.107 | 21.7029 | 21.9344 | 22.0103 | 21.7533 | 22.342 | 31.0144 | 86.6201 |  | 47.2468 | 74.6969 | 79.8768 | 49.5604 |  | 16.9577 | 17.0825 | 16.615 | 17.0002 | 17.2999 | 19.0371 | 48.639 | 16.0062 | 17.0539 | 15.8149 | 17.5378 | 18.1384 | 44.0873 | 46.8736 | 43.2953 | 21.5801 |  |  | 0.6534 | -0.17486 | -25.098 | 0.36991 | 0.14404 | -197.8434 | 19.6921 | 0.35974 | -0.012361 | 0.29572 | -0.010646 | 0.00033513 | 0.0003187 | 1.854 | 21.7668 | 21.9799 | 22.1773 | 22.2341 | 22.0462 | 21.3411 | 20.1549 | 22.1732 | 22.3518 | 22.3863 | 22.3361 | 21.9596 | 21.195 | 22.2497 | 43.8713 | 30.5857 | 32.3454 | 24.1683 | 21.7372 | 27.8372 | 21.7454 | 22.3457 | 22.1213 | 21.6828 | 22.0763 | 21.78 | 21.2904 | 21.9407 | 21.5471 | 21.3141 | 30.6 | 95.3182 | 69.7895 | 42.4143 | 0.54381 | 0.086762 | 38.2696 | 22.0081 | 22.3211 | 20.1674 | 21.6223 | 22.0604 | 21.9283 | 21.7033 | 23.2577 | 21.7639 | 21.4467 | 21.6718 | 87.2975 | 104.3933 | 66.9699 | 67.9989 | 39.1016 |  | 30.1801 | 61.6258 | 32.3358 | 44.377 | 31.0515 | 37.4107 |  | 40.625 |  |  | 21.1288 | 22.081 | 35.0082 | [5 empty] | 21.8917 | 32.581 | 21.6535 | 22.0281 | 26.1948 | 21.1714 | 21.8082 | 21.7595 | 40.7729 | 112.9706 |  | 33.3219 | 80.5164 | 20.1299 | 34.9957 | 84.005 | 27.3585 | 67.895 | 21.3232 | 62.9202 | 21.3556 | 65.3413 | 18.6204 | 35.3484 | 76.2004 | 22.7632 | 36.0526 | 101.0041 | 20.2878 | 34.2535 | 86.4802 | 20.3432 | 60.352 | 23.4943 | 66.728 | 21.4942 | 66.8406 | 0.30297 | 19.9075 | 0.75138 | 0.022382 | -27.1015 | 3.0955 | 54.51 | 51.67 | 1.0865 | -0.49646 | -5.9478 | 0.72209 | 0.4521 | -16.7555 | 5.2862 | 0.23218 | -0.31982 | 0.11539 | -1.3162 | -0.74897 | -0.029861 | 0.15449
42838.4226 | 204 | 22.9029 | 22.8745 | 22.8631 | 22.7769 | 22.3924 | 21.7282 | 22.7145 | 21.7866 | 22.3638 | 22.3744 | 22.345 | 21.9974 | 21.2037 | 22.1795 | 21.6121 | 21.7877 | 21.912 | 21.0947 | 21.1896 | 21.4061 | 20.4755 | 20.6579 | 21.2453 | 21.8684 | 21.6391 | 22.4781 | 94.6801 | 85.3704 | 99.0509 | 22.1047 | 21.6997 | 21.9403 | 22.0072 | 21.7516 | 22.3582 | 31.084 | 86.3248 |  | 47.3564 | 74.8517 | 79.9618 | 49.2225 |  | 16.9633 | 17.0844 | 16.6072 | 16.9996 | 17.2958 | 19.0869 | 48.9023 | 16.0143 | 17.053 | 15.8067 | 17.5359 | 18.1347 | 44.0647 | 46.8855 | 43.3344 | 21.5785 |  |  | 0.77694 | -0.20574 | -24.9613 | 0.50725 | 0.21501 | -197.798 | 20.292 | 0.45239 | 0.0055422 | 0.21222 | 0.092299 | 0.00034499 | 0.00033184 | 1.8474 | 21.7681 | 21.9826 | 22.1824 | 22.2429 | 22.0575 | 21.3591 | 20.1682 | 22.1858 | 22.3616 | 22.4013 | 22.3459 | 21.973 | 21.1986 | 22.2706 | 44.7863 | 30.8636 | 32.3006 | 24.4181 | 22.3685 | 27.9517 | 21.7991 | 22.3495 | 22.1126 | 21.6854 | 22.0725 | 21.7807 | 21.2823 | 21.9415 | 21.5423 | 21.3149 | 30.6713 | 95.1011 | 69.8501 | 42.6439 | 0.4746 | 0.056711 | 38.1099 | 22.0009 | 22.3162 | 20.1638 | 21.6199 | 22.0632 | 21.9243 | 21.7044 | 23.273 | 21.7663 | 21.4422 | 21.6773 | 87.3857 | 104.4231 | 67.0389 | 68.0842 | 39.1667 |  | 30.2558 | 61.3872 | 32.4302 | 44.3325 | 31.1293 | 37.4989 |  | 40.7378 |  |  | 21.1357 | 22.0719 | 34.9651 | [5 empty] | 21.8905 | 32.595 | 21.6554 | 22.0269 | 26.2319 | 21.1726 | 21.8024 | 21.7746 | 40.8172 | 112.9073 |  | 33.4105 | 80.6405 | 20.1483 | 35.1002 | 84.0751 | 27.393 | 68.0301 | 21.3395 | 63.0303 | 21.3729 | 65.4487 | 18.6125 | 35.4084 | 76.322 | 22.7799 | 36.1104 | 101.1134 | 20.3021 | 34.3681 | 86.6512 | 20.3675 | 60.4015 | 23.5292 | 66.9165 | 21.5257 | 66.952 | 0.23007 | 19.9031 | 0.75416 | 0.021663 | -27.104 | 3.0954 | 52.31 | 51.95 | 1.1851 | -0.53852 | -5.9316 | 0.84558 | 0.55241 | -16.755 | 5.3666 | 0.23296 | -0.30996 | 0.11928 | -1.4045 | -0.73772 | -0.018095 | 0.15055
42838.4227 | 205 | 22.9141 | 22.8743 | 22.8695 | 22.7903 | 22.3957 | 21.7326 | 22.7203 | 21.7901 | 22.3715 | 22.379 | 22.3555 | 21.9994 | 21.2198 | 22.1834 | 21.6094 | 21.7828 | 21.9113 | 21.0899 | 21.1894 | 21.4053 | 20.4771 | 20.6589 | 21.2527 | 21.8689 | 21.646 | 22.492 | 94.7355 | 85.4809 | 98.4687 | 22.1056 | 21.7022 | 21.9548 | 22.0067 | 21.7491 | 22.3745 | 31.1594 | 86.2771 |  | 47.4659 | 74.9977 | 80.045 | 48.9492 |  | 16.9693 | 17.0977 | 16.6096 | 16.9887 | 17.2939 | 19.128 | 48.9253 | 16.0135 | 17.0554 | 15.7939 | 17.5402 | 18.1358 | 44.0519 | 46.8869 | 43.3617 | 21.5765 |  |  | 0.83937 | -0.073005 | -25.4752 | 0.63473 | 0.13024 | -197.7934 | 19.8958 | 0.45765 | 0.028116 | 0.13543 | 0.15584 | 0.00034006 | 0.00032692 | 1.8263 | 21.7823 | 21.9929 | 22.1949 | 22.2493 | 22.0686 | 21.3607 | 20.1757 | 22.1995 | 22.3718 | 22.4118 | 22.3595 | 21.9728 | 21.2096 | 22.2881 | 45.4666 | 31.7829 | 32.7712 | 24.7874 | 22.5185 | 28.0813 | 21.8724 | 22.3477 | 22.1237 | 21.6846 | 22.0785 | 21.7813 | 21.2902 | 21.9453 | 21.5582 | 21.3253 | 30.7424 | 95.1984 | 70.2542 | 42.9968 | 0.54204 | 0.16379 | 38.1119 | 21.9969 | 22.3124 | 20.1625 | 21.6217 | 22.0589 | 21.9266 | 21.7051 | 23.2951 | 21.7666 | 21.4412 | 21.6818 | 87.4882 | 104.6066 | 67.1311 | 68.1816 | 39.3998 |  | 30.3337 | 61.7694 | 32.5161 | 44.6467 | 31.2028 | 37.7964 |  | 40.8473 |  |  | 21.1535 | 22.0985 | 34.8593 | [5 empty] | 21.8985 | 32.5836 | 21.6665 | 22.0309 | 26.2572 | 21.1819 | 21.8129 | 21.7753 | 40.9026 | 112.7754 |  | 33.5518 | 80.7539 | 20.1503 | 35.3012 | 84.1182 | 27.4225 | 68.2137 | 21.3444 | 63.1323 | 21.3876 | 65.5239 | 18.611 | 35.4596 | 76.4284 | 22.7966 | 36.1546 | 101.1924 | 20.3067 | 34.4571 | 86.719 | 20.3862 | 60.4507 | 23.5498 | 67.1203 | 21.5358 | 67.0223 | 0.37198 | 19.9042 | 0.75666 | 0.021598 | -27.1128 | 3.0954 | 58.24 | 52.8 | 1.2308 | -0.3208 | -5.9925 | 0.9459 | 0.42997 | -16.756 | 5.3143 | 0.22914 | -0.31763 | 0.11307 | -1.4649 | -0.78144 | -0.0079288 | 0.14317
42838.4227 | 206 | 22.9155 | 22.8751 | 22.8629 | 22.7793 | 22.3987 | 21.7318 | 22.7166 | 21.7828 | 22.368 | 22.3739 | 22.3471 | 21.9948 | 21.211 | 22.1749 | 21.6071 | 21.7779 | 21.9072 | 21.0895 | 21.1877 | 21.4054 | 20.473 | 20.657 | 21.2469 | 21.8703 | 21.6353 | 22.5178 | 94.7174 | 85.573 | 98.0243 | 22.1094 | 21.7074 | 21.9585 | 22.0119 | 21.7533 | 22.3863 | 31.2453 | 86.7603 |  | 47.5953 | 75.1232 | 80.1287 | 48.8263 |  | 16.9689 | 17.0984 | 16.5934 | 16.981 | 17.2918 | 19.1403 | 48.8786 | 16.0007 | 17.05 | 15.7373 | 17.5388 | 18.14 | 44.0304 | 46.8863 | 43.3783 | 21.5771 |  |  | 0.73226 | -0.32731 | -25.4588 | 0.61173 | 0.009988 | -197.8539 | 19.9214 | 0.22503 | 0.13125 | -0.23088 | 0.14316 | 0.00034499 | 0.0003302 | 1.8285 | 21.7774 | 21.9941 | 22.1904 | 22.2414 | 22.0632 | 21.3609 | 20.1724 | 22.2007 | 22.3678 | 22.3993 | 22.354 | 21.9684 | 21.2069 | 22.2753 | 46.6123 | 32.9478 | 35.2464 | 25.5803 | 22.6655 | 28.1935 | 21.9464 | 22.354 | 22.1324 | 21.6877 | 22.0745 | 21.7971 | 21.2934 | 21.9486 | 21.5537 | 21.3358 | 30.837 | 95.1728 | 70.6446 | 42.9206 | 0.53162 | 0.079154 | 38.1757 | 21.9982 | 22.3128 | 20.1641 | 21.616 | 22.0533 | 21.926 | 21.7096 | 23.324 | 21.7684 | 21.4408 | 21.6916 | 87.6112 | 104.7901 | 67.2332 | 68.3107 | 39.3704 |  | 30.4096 | 62.249 | 32.6138 | 45.0396 | 31.2868 | 37.6816 |  | 40.9437 |  |  | 21.1572 | 22.1179 | 34.9861 | [5 empty] | 21.9001 | 32.6244 | 21.6607 | 22.0378 | 26.2995 | 21.183 | 21.8167 | 21.8014 | 41.0782 | 112.7281 |  | 33.6678 | 80.952 | 20.1667 | 35.5271 | 84.143 | 27.4746 | 68.4012 | 21.3616 | 63.294 | 21.3945 | 65.6717 | 18.6019 | 35.5164 | 76.4868 | 22.7975 | 36.2341 | 101.3035 | 20.3069 | 34.5297 | 86.8402 | 20.3911 | 60.5403 | 23.5626 | 67.2299 | 21.5421 | 67.097 | 0.20318 | 19.8973 | 0.75862 | 0.022179 | -27.0911 | 3.0954 | 53.15 | 51.74 | 1.1489 | -0.67925 | -5.9906 | 0.92861 | 0.11907 | -16.7589 | 5.3178 | 0.23255 | -0.3276 | 0.10502 | -1.579 | -1.0478 | -0.0015778 | 0.14852
42838.4227 | 207 | 22.914 | 22.8759 | 22.8599 | 22.7724 | 22.4027 | 21.7319 | 22.719 | 21.7897 | 22.3692 | 22.3696 | 22.3468 | 21.9949 | 21.2032 | 22.1841 | 21.6074 | 21.7785 | 21.9002 | 21.0854 | 21.1855 | 21.4038 | 20.478 | 20.651 | 21.2521 | 21.8654 | 21.6284 | 22.5303 | 94.7803 | 85.665 | 98.0208 | 22.1143 | 21.7071 | 21.9687 | 22.0115 | 21.7548 | 22.3971 | 31.3107 | 87.2344 |  | 47.7284 | 75.2234 | 80.1823 | 49.0673 |  | 16.9695 | 17.1057 | 16.5938 | 16.9798 | 17.2982 | 19.1176 | 48.8028 | 15.9773 | 17.0535 | 15.6983 | 17.5426 | 18.1379 | 44.0245 | 46.8889 | 43.3915 | 21.5827 |  |  | 0.68429 | -0.257 | -25.8123 | 0.63933 | 0.19464 | -197.8335 | 19.8064 | 0.37945 | 0.11335 | 0.15746 | 0.10723 | 0.00037291 | 0.00033677 | 1.819 | 21.7746 | 21.9882 | 22.1801 | 22.2373 | 22.0552 | 21.3581 | 20.1637 | 22.1855 | 22.3596 | 22.3968 | 22.3442 | 21.9681 | 21.1956 | 22.2682 | 46.3711 | 32.4266 | 35.9166 | 25.7272 | 23.3852 | 28.2985 | 22.0233 | 22.3509 | 22.1266 | 21.6811 | 22.0748 | 21.7885 | 21.2916 | 21.9391 | 21.5515 | 21.3422 | 30.9033 | 95.083 | 70.7922 | 42.7005 | 0.38515 | 0.012204 | 38.2601 | 21.9987 | 22.3134 | 20.162 | 21.6136 | 22.0565 | 21.9225 | 21.7052 | 23.3455 | 21.7686 | 21.4416 | 21.7061 | 87.7149 | 104.8885 | 67.3596 | 68.4284 | 39.4361 |  | 30.4777 | 62.3682 | 32.6951 | 45.0776 | 31.356 | 37.7866 |  | 41.0432 |  |  | 21.1645 | 22.1141 | 35.0642 | [5 empty] | 21.883 | 32.6611 | 21.6451 | 22.0293 | 26.3264 | 21.1739 | 21.8047 | 21.8088 | 41.2033 | 112.6891 |  | 33.7693 | 81.0808 | 20.1572 | 35.6124 | 84.1987 | 27.4876 | 68.6011 | 21.369 | 63.4296 | 21.4092 | 65.7387 | 18.6043 | 35.5794 | 76.6309 | 22.8118 | 36.3151 | 101.349 | 20.3135 | 34.6201 | 86.8995 | 20.4054 | 60.6826 | 23.571 | 67.3331 | 21.556 | 67.1722 | 0.35176 | 19.8902 | 0.76064 | 0.02191 | -27.1094 | 3.0954 | 66.85 | 53.08 | 1.1106 | -0.6019 | -6.0321 | 0.94934 | 0.52562 | -16.7574 | 5.3022 | 0.23304 | -0.32813 | 0.10634 | -1.5399 | -1.1133 | -0.0060387 | 0.1569
42838.4227 | 208 | 22.9069 | 22.8721 | 22.8559 | 22.777 | 22.4017 | 21.7306 | 22.7135 | 21.7872 | 22.3655 | 22.368 | 22.346 | 22.0008 | 21.2108 | 22.1801 | 21.6166 | 21.7882 | 21.903 | 21.0931 | 21.1898 | 21.4029 | 20.4858 | 20.6569 | 21.2655 | 21.871 | 21.6359 | 22.5451 | 94.8331 | 85.719 | 97.8553 | 22.1022 | 21.699 | 21.9901 | 22.0063 | 21.747 | 22.407 | 31.3989 | 87.44 |  | 47.8666 | 75.2933 | 80.2225 | 49.4932 |  | 16.9758 | 17.1027 | 16.5987 | 16.98 | 17.2908 | 19.1117 | 48.3899 | 15.9777 | 17.0571 | 15.6681 | 17.5477 | 18.1405 | 44.02 | 46.8879 | 43.3918 | 21.5735 |  |  | 0.84003 | -0.25634 | -25.8872 | 0.47702 | 0.093444 | -197.8085 | 19.694 | 0.45634 | 0.11199 | 0.2011 | 0.078585 | 0.0003532 | 0.00035156 | 1.8266 | 21.7711 | 21.986 | 22.1775 | 22.2342 | 22.054 | 21.3512 | 20.1673 | 22.1821 | 22.3593 | 22.3919 | 22.3433 | 21.9663 | 21.1948 | 22.2687 | 46.3581 | 31.6535 | 34.3006 | 25.5403 | 23.295 | 28.3982 | 22.0682 | 22.3642 | 22.1345 | 21.6968 | 22.0836 | 21.7914 | 21.304 | 21.9549 | 21.5613 | 21.3569 | 30.9926 | 95.0667 | 70.9074 | 42.4766 | 0.47205 | -0.011761 | 38.2635 | 21.9996 | 22.3122 | 20.159 | 21.6171 | 22.064 | 21.926 | 21.7041 | 23.3668 | 21.7658 | 21.4457 | 21.7175 | 87.8052 | 104.9422 | 67.5217 | 68.5442 | 39.3852 |  | 30.5635 | 62.0242 | 32.782 | 44.927 | 31.4471 | 37.6579 |  | 41.1643 |  |  | 21.1751 | 22.1309 | 35.1214 | [5 empty] | 21.8891 | 32.7472 | 21.6498 | 22.0307 | 26.3746 | 21.1792 | 21.8108 | 21.8076 | 41.325 | 112.7013 |  | 33.8291 | 81.165 | 20.1547 | 35.5602 | 84.4269 | 27.4945 | 68.8545 | 21.3699 | 63.6268 | 21.4252 | 65.8423 | 18.607 | 35.6093 | 76.756 | 22.8384 | 36.3589 | 101.3978 | 20.3185 | 34.6831 | 86.9367 | 20.419 | 60.7901 | 23.5879 | 67.5355 | 21.5791 | 67.2449 | 0.32301 | 19.8916 | 0.76262 | 0.021235 | -27.1133 | 3.0954 | 55.29 | 51.76 | 1.2303 | -0.60112 | -6.0408 | 0.82002 | 0.36419 | -16.7562 | 5.2871 | 0.23739 | -0.3156 | 0.11363 | -1.5267 | -0.92848 | -0.014851 | 0.16617
42838.4227 | 209 | 22.9111 | 22.8757 | 22.8707 | 22.7823 | 22.3971 | 21.7342 | 22.7228 | 21.7915 | 22.365 | 22.3728 | 22.3485 | 22.0026 | 21.2069 | 22.1824 | 21.6171 | 21.7862 | 21.8991 | 21.0929 | 21.19 | 21.4029 | 20.4834 | 20.6597 | 21.2714 | 21.8703 | 21.6411 | 22.5622 | 95.0035 | 85.7468 | 98.4454 | 22.0994 | 21.7024 | 21.9921 | 22.0049 | 21.7476 | 22.4118 | 31.4569 | 87.6562 |  | 47.9614 | 75.3557 | 80.2601 | 49.7275 |  | 16.9665 | 17.0977 | 16.5898 | 16.9677 | 17.2766 | 19.0875 | 48.0792 | 15.9742 | 17.0583 | 15.68 | 17.5435 | 18.1471 | 44.0108 | 46.8911 | 43.387 | 21.5733 |  |  | 0.60938 | -0.15909 | -26.3722 | 0.73395 | 0.18741 | -197.8315 | 19.6277 | 0.26906 | -0.10538 | -0.11612 | 0.039178 | 0.00037127 | 0.00035156 | 1.8289 | 21.7805 | 21.9946 | 22.1935 | 22.2423 | 22.0589 | 21.3545 | 20.1746 | 22.1939 | 22.3739 | 22.4017 | 22.3486 | 21.974 | 21.207 | 22.2751 | 47.1482 | 31.8872 | 33.959 | 25.1193 | 23.0062 | 28.5089 | 22.1328 | 22.3554 | 22.1289 | 21.6861 | 22.0822 | 21.7909 | 21.2982 | 21.9489 | 21.559 | 21.3621 | 31.0514 | 95.1534 | 71.1059 | 42.664 | 0.59827 | -0.035536 | 38.2066 | 21.9992 | 22.3076 | 20.1584 | 21.6112 | 22.0622 | 21.9216 | 21.7057 | 23.3887 | 21.7597 | 21.4467 | 21.7172 | 87.8889 | 105.0113 | 67.6621 | 68.6532 | 39.5849 |  | 30.636 | 61.5668 | 32.862 | 44.825 | 31.529 | 37.6262 |  | 41.2567 |  |  | 21.1859 | 22.1441 | 35.1842 | [5 empty] | 21.8874 | 32.8199 | 21.651 | 22.0314 | 26.3949 | 21.1842 | 21.8153 | 21.8094 | 41.4449 | 112.9195 |  | 33.8413 | 81.2734 | 20.1613 | 35.5285 | 84.6923 | 27.5009 | 68.9996 | 21.3694 | 63.9174 | 21.4307 | 65.9636 | 18.6166 | 35.6551 | 76.8089 | 22.8566 | 36.4131 | 101.3577 | 20.32 | 34.7182 | 87.016 | 20.4256 | 60.8339 | 23.6049 | 67.667 | 21.5928 | 67.3231 | 0.40259 | 19.8945 | 0.7646 | 0.020727 | -27.117 | 3.0954 | 58.53 | 51.67 | 1.0487 | -0.47356 | -6.0971 | 1.0172 | 0.51574 | -16.7565 | 5.278 | 0.23431 | -0.30015 | 0.11927 | -1.6015 | -0.88296 | -0.01938 | 0.16297
42838.4227 | 210 | 22.9116 | 22.8743 | 22.8558 | 22.7706 | 22.3931 | 21.7295 | 22.7185 | 21.7794 | 22.3636 | 22.3685 | 22.3391 | 21.9885 | 21.2031 | 22.1764 | 21.6128 | 21.7925 | 21.9 | 21.0913 | 21.1861 | 21.4096 | 20.4824 | 20.6578 | 21.2794 | 21.8729 | 21.646 | 22.5758 | 95.2339 | 85.7813 | 99.0476 | 22.1001 | 21.6972 | 22.0007 | 22.0035 | 21.7459 | 22.4269 | 31.5288 | 87.8222 |  | 48.077 | 75.416 | 80.3039 | 49.7008 |  | 16.9816 | 17.1034 | 16.5945 | 16.9717 | 17.2765 | 19.0794 | 47.8869 | 15.9799 | 17.0588 | 15.7227 | 17.5462 | 18.1555 | 43.9996 | 46.8888 | 43.3853 | 21.5834 |  |  | 0.65603 | -0.34571 | -26.6823 | 0.54996 | 0.12498 | -197.8742 | 19.6677 | 0.38274 | 0.079879 | -0.11402 | -0.013423 | 0.00037291 | 0.00033184 | 1.8004 | 21.7761 | 21.9859 | 22.1819 | 22.2254 | 22.054 | 21.3544 | 20.1663 | 22.1859 | 22.3611 | 22.3969 | 22.346 | 21.9674 | 21.2091 | 22.2693 | 47.868 | 33.0263 | 35.2372 | 25.2653 | 23.0283 | 28.6336 | 22.188 | 22.3501 | 22.112 | 21.6816 | 22.0813 | 21.7868 | 21.2901 | 21.9443 | 21.5511 | 21.3585 | 31.1231 | 95.3066 | 71.3361 | 42.8732 | 0.42919 | -0.02983 | 38.3779 | 21.9974 | 22.3108 | 20.1646 | 21.6116 | 22.0616 | 21.9181 | 21.7103 | 23.4099 | 21.7626 | 21.4395 | 21.7254 | 87.9656 | 105.1336 | 67.7991 | 68.768 | 40.2635 |  | 30.7013 | 61.6082 | 32.9324 | 44.6419 | 31.5996 | 37.5983 |  | 41.3436 |  |  | 21.2003 | 22.1624 | 35.3567 | [5 empty] | 21.8948 | 32.8989 | 21.6513 | 22.0323 | 26.4195 | 21.1814 | 21.8203 | 21.8272 | 41.4944 | 113.2515 |  | 33.8833 | 81.4923 | 20.175 | 35.6514 | 84.8462 | 27.5247 | 69.0808 | 21.3839 | 64.1274 | 21.4424 | 66.077 | 18.6225 | 35.7941 | 76.8268 | 22.8757 | 36.5112 | 101.3579 | 20.316 | 34.7625 | 87.1421 | 20.4293 | 60.927 | 23.6193 | 67.787 | 21.6069 | 67.4675 | 0.26124 | 19.8834 | 0.76524 | 0.01762 | -27.0351 | 3.0954 | 71.87 | 52.47 | 1.089 | -0.69809 | -6.1329 | 0.88049 | 0.42117 | -16.7581 | 5.2833 | 0.2177 | -0.29889 | 0.12677 | -1.6669 | -1.0185 | -0.016179 | 0.15961
42838.4227 | 211 | 22.9108 | 22.8765 | 22.8595 | 22.7763 | 22.3964 | 21.7321 | 22.7166 | 21.7924 | 22.3617 | 22.3699 | 22.3444 | 22.0009 | 21.2031 | 22.1781 | 21.6151 | 21.7882 | 21.9097 | 21.0913 | 21.1882 | 21.4117 | 20.4818 | 20.6591 | 21.2868 | 21.869 | 21.642 | 22.5935 | 95.3688 | 85.846 | 99.2526 | 22.1103 | 21.7042 | 22.0111 | 22.007 | 21.7481 | 22.4459 | 31.6079 | 87.6247 |  | 48.1932 | 75.5243 | 80.3136 | 49.6742 |  | 16.9789 | 17.1188 | 16.5947 | 16.9688 | 17.2687 | 19.0673 | 47.8563 | 15.964 | 17.0589 | 15.6961 | 17.5538 | 18.14 | 43.9973 | 46.8843 | 43.3785 | 21.5793 |  |  | 0.69546 | -0.27277 | -27.1305 | 0.44614 | 0.20778 | -197.8328 | 19.4929 | 0.42808 | -0.033572 | 0.12159 | -0.053525 | 0.00034499 | 0.00033184 | 1.8067 | 21.7678 | 21.9901 | 22.1828 | 22.2386 | 22.0487 | 21.351 | 20.1595 | 22.1811 | 22.3595 | 22.3945 | 22.3441 | 21.9692 | 21.2054 | 22.2698 | 48.5735 | 34.3084 | 35.62 | 25.7947 | 23.4646 | 28.7641 | 22.2641 | 22.348 | 22.1259 | 21.6858 | 22.0725 | 21.7952 | 21.2923 | 21.9423 | 21.5458 | 21.365 | 31.2004 | 95.4848 | 71.6174 | 42.9422 | 0.45848 | 0.15885 | 38.5178 | 21.9925 | 22.3088 | 20.1705 | 21.6133 | 22.0609 | 21.9198 | 21.7128 | 23.4435 | 21.7659 | 21.4395 | 21.7422 | 88.0246 | 105.2659 | 67.9505 | 68.9197 | 40.8369 |  | 30.7802 | 61.6819 | 33.0169 | 44.5209 | 31.6864 | 37.6103 |  | 41.4644 |  |  | 21.212 | 22.1634 | 35.2536 | [5 empty] | 21.8941 | 32.9291 | 21.6508 | 22.0343 | 26.4456 | 21.175 | 21.8139 | 21.8401 | 41.5535 | 113.4838 |  | 33.9793 | 81.7127 | 20.1851 | 35.8816 | 84.9188 | 27.5719 | 69.1087 | 21.3945 | 64.2754 | 21.455 | 66.2139 | 18.6286 | 35.9257 | 76.9036 | 22.8963 | 36.6139 | 101.4537 | 20.3212 | 34.8267 | 87.2319 | 20.4383 | 61.0543 | 23.6246 | 67.9519 | 21.6228 | 67.559 | 0.36048 | 19.884 | 0.76767 | 0.019849 | -27.0766 | 3.0954 | 65.4 | 51.34 | 1.1215 | -0.6201 | -6.1844 | 0.79305 | 0.54303 | -16.756 | 5.2597 | 0.20446 | -0.29804 | 0.1331 | -1.7299 | -1.0522 | -0.012736 | 0.16033
42838.4227 | 212 | 22.9126 | 22.8784 | 22.8651 | 22.7878 | 22.4044 | 21.7353 | 22.7198 | 21.7924 | 22.3638 | 22.3764 | 22.3481 | 21.9979 | 21.2128 | 22.176 | 21.6108 | 21.7785 | 21.9033 | 21.0829 | 21.187 | 21.402 | 20.4768 | 20.6533 | 21.2811 | 21.866 | 21.6341 | 22.5975 | 95.5534 | 85.8951 | 99.431 | 22.1131 | 21.7081 | 22.0251 | 22.0124 | 21.749 | 22.4656 | 31.6894 | 87.6139 |  | 48.3168 | 75.6921 | 80.3297 | 49.4082 |  | 16.9821 | 17.1229 | 16.6019 | 16.9732 | 17.2668 | 19.0469 | 47.894 | 15.9334 | 17.0617 | 15.6661 | 17.5561 | 18.1504 | 43.9998 | 46.8807 | 43.3881 | 21.5816 |  |  | 0.65603 | -0.20508 | -27.1325 | 0.18395 | 0.15192 | -197.8512 | 19.2531 | 0.41888 | 0.10498 | 0.22187 | 0.039178 | 0.00036306 | 0.00034663 | 1.802 | 21.7724 | 21.9956 | 22.1896 | 22.2452 | 22.0543 | 21.3578 | 20.1624 | 22.1794 | 22.3638 | 22.3996 | 22.3482 | 21.9738 | 21.2009 | 22.2756 | 48.0687 | 34.4306 | 35.1396 | 25.8892 | 23.8027 | 28.8764 | 22.3258 | 22.3468 | 22.1192 | 21.6777 | 22.0687 | 21.7783 | 21.2904 | 21.9363 | 21.5462 | 21.3706 | 31.2615 | 95.5313 | 71.7593 | 42.7466 | 0.46753 | 0.050434 | 38.5338 | 21.9942 | 22.3082 | 20.172 | 21.6162 | 22.0611 | 21.9199 | 21.7128 | 23.4702 | 21.7635 | 21.4424 | 21.7575 | 88.1169 | 105.4265 | 68.0767 | 69.0767 | 41.1632 |  | 30.8633 | 61.7011 | 33.0966 | 44.3841 | 31.7716 | 37.7006 |  | 41.5917 |  |  | 21.2239 | 22.1542 | 35.0471 | [5 empty] | 21.8951 | 32.9304 | 21.6523 | 22.032 | 26.4642 | 21.1779 | 21.8175 | 21.8449 | 41.6391 | 113.6718 |  | 34.0367 | 81.8373 | 20.1824 | 36.0246 | 85.0123 | 27.6025 | 69.1476 | 21.4028 | 64.316 | 21.4598 | 66.343 | 18.6317 | 35.9473 | 77.0325 | 22.9066 | 36.6569 | 101.5155 | 20.3279 | 34.9539 | 87.2651 | 20.4508 | 61.2119 | 23.6437 | 68.0228 | 21.6339 | 67.6095 | 0.29129 | 19.8784 | 0.768 | 0.019246 | -27.0702 | 3.0954 | 64.5 | 52.61 | 1.0895 | -0.5377 | -6.1846 | 0.50924 | 0.46432 | -16.7561 | 5.227 | 0.19824 | -0.29584 | 0.13981 | -1.6607 | -0.99158 | -0.0025583 | 0.16786
42838.4227 | 213 | 22.9126 | 22.8766 | 22.8603 | 22.7858 | 22.4 | 21.7305 | 22.7215 | 21.7824 | 22.3606 | 22.377 | 22.3406 | 22.0019 | 21.2064 | 22.1746 | 21.6115 | 21.7823 | 21.9057 | 21.1001 | 21.1853 | 21.3963 | 20.4743 | 20.6541 | 21.2993 | 21.8746 | 21.6452 | 22.6211 | 95.7157 | 85.9665 | 99.5988 | 22.1103 | 21.701 | 22.0324 | 22.0021 | 21.7426 | 22.4705 | 31.7554 | 88.4069 |  | 48.418 | 75.873 | 80.357 | 49.6447 |  | 16.9832 | 17.1307 | 16.6013 | 16.9722 | 17.2562 | 19.0091 | 47.6927 | 15.9388 | 17.0558 | 15.7593 | 17.5635 | 18.1513 | 44.0078 | 46.8705 | 43.3967 | 21.5825 |  |  | 0.69349 | 0.062359 | -27.7265 | 0.32129 | 0.032988 | -197.8926 | 19.1552 | 0.37551 | 0.029283 | 0.13606 | 0.25062 | 0.00033842 | 0.00034006 | 1.8142 | 21.7699 | 21.9938 | 22.1835 | 22.2375 | 22.0537 | 21.357 | 20.1671 | 22.1891 | 22.3676 | 22.4042 | 22.3465 | 21.9702 | 21.1969 | 22.2755 | 47.5757 | 33.9502 | 35.0081 | 25.4746 | 23.5509 | 28.9739 | 22.3851 | 22.3466 | 22.1204 | 21.677 | 22.0659 | 21.7838 | 21.2894 | 21.938 | 21.5451 | 21.3771 | 31.3309 | 95.5668 | 71.8645 | 42.5577 | 0.44747 | 0.10997 | 38.7159 | 21.999 | 22.3075 | 20.1675 | 21.6137 | 22.0594 | 21.9192 | 21.7087 | 23.4836 | 21.7632 | 21.4405 | 21.761 | 88.2353 | 105.5662 | 68.1536 | 69.1773 | 41.1391 |  | 30.9339 | 61.4852 | 33.146 | 44.4616 | 31.8383 | 37.5888 |  | 41.6989 |  |  | 21.2254 | 22.1676 | 35.1259 | [5 empty] | 21.8958 | 32.9559 | 21.6589 | 22.0422 | 26.473 | 21.1885 | 21.822 | 21.8588 | 41.7286 | 113.8293 |  | 34.0947 | 81.9421 | 20.2029 | 36.0526 | 85.1934 | 27.634 | 69.1864 | 21.418 | 64.327 | 21.4788 | 66.4501 | 18.6313 | 35.9389 | 77.1835 | 22.9137 | 36.7259 | 101.702 | 20.3347 | 35.0947 | 87.3452 | 20.4648 | 61.3951 | 23.6629 | 68.1991 | 21.6539 | 67.6998 | 0.31095 | 19.8759 | 0.77046 | 0.019645 | -27.0822 | 3.0954 | 35.6 | 51.69 | 1.1205 | 0.2965 | -6.2521 | 0.67301 | 0.21635 | -16.7568 | 5.2134 | 0.20132 | -0.28815 | 0.13994 | -1.5945 | -0.97001 | -0.0068717 | 0.17547
42838.4228 | 214 | 22.9145 | 22.8675 | 22.8581 | 22.7827 | 22.3943 | 21.7363 | 22.7152 | 21.782 | 22.366 | 22.368 | 22.3394 | 21.9971 | 21.2045 | 22.1808 | 21.6079 | 21.7757 | 21.9023 | 21.0901 | 21.1785 | 21.3993 | 20.4753 | 20.6635 | 21.3008 | 21.8612 | 21.6374 | 22.6284 | 95.7813 | 86.0966 | 99.5422 | 22.1068 | 21.7079 | 22.0486 | 22.0062 | 21.7552 | 22.487 | 31.8443 | 89.2709 |  | 48.5397 | 76.0098 | 80.3999 | 50.5304 |  | 16.9877 | 17.1415 | 16.6106 | 16.9809 | 17.2612 | 19.0019 | 47.5626 | 15.9692 | 17.0633 | 15.8204 | 17.5646 | 18.1544 | 44.0314 | 46.8595 | 43.3961 | 21.586 |  |  | 0.74737 | -0.001381 | -27.7607 | 0.29369 | 0.1355 | -197.8558 | 19.1026 | 0.49445 | -0.014307 | 0.18935 | 0.040219 | 0.00033842 | 0.00031706 | 1.8337 | 21.7736 | 21.9905 | 22.1849 | 22.2353 | 22.0558 | 21.3544 | 20.1699 | 22.1905 | 22.3638 | 22.4028 | 22.3472 | 21.9724 | 21.1967 | 22.2733 | 47.9303 | 32.9244 | 34.2471 | 25.6481 | 23.1132 | 29.0781 | 22.4381 | 22.3505 | 22.1266 | 21.6857 | 22.076 | 21.7892 | 21.2917 | 21.9422 | 21.5518 | 21.3883 | 31.4028 | 95.587 | 71.9186 | 42.5067 | 0.59709 | 0.073448 | 38.8045 | 21.9964 | 22.3101 | 20.1739 | 21.6213 | 22.0609 | 21.9241 | 21.7098 | 23.511 | 21.7714 | 21.4476 | 21.7783 | 88.3893 | 105.653 | 68.2382 | 69.2535 | 41.0255 |  | 31.0164 | 61.1426 | 33.213 | 44.5499 | 31.9166 | 37.5931 |  | 41.8174 |  |  | 21.2184 | 22.1802 | 35.1933 | [5 empty] | 21.8883 | 32.9764 | 21.658 | 22.0424 | 26.4768 | 21.1882 | 21.8208 | 21.8444 | 41.7747 | 113.6646 |  | 34.1447 | 82.0317 | 20.2061 | 36.0378 | 85.2936 | 27.6699 | 69.2035 | 21.4217 | 64.298 | 21.495 | 66.5346 | 18.633 | 36.0135 | 77.3105 | 22.93 | 36.8585 | 101.8893 | 20.3529 | 35.1971 | 87.5253 | 20.4835 | 61.5244 | 23.6822 | 68.3641 | 21.6726 | 67.7616 | 0.21542 | 19.8741 | 0.77485 | 0.021358 | -27.0963 | 3.0954 | 60.51 | 52.05 | 1.1631 | -0.044125 | -6.256 | 0.64347 | 0.43846 | -16.7551 | 5.2062 | 0.20729 | -0.27633 | 0.14017 | -1.6216 | -0.87927 | -0.028432 | 0.17935
42838.4228 | 215 | 22.9018 | 22.8656 | 22.8672 | 22.7736 | 22.3973 | 21.7266 | 22.7154 | 21.7738 | 22.3636 | 22.3726 | 22.3402 | 21.9931 | 21.2136 | 22.169 | 21.6167 | 21.7854 | 21.9062 | 21.0908 | 21.1938 | 21.4025 | 20.4816 | 20.6631 | 21.312 | 21.8707 | 21.6351 | 22.6505 | 95.9171 | 86.2179 | 99.681 | 22.1115 | 21.7088 | 22.0567 | 22.0086 | 21.7523 | 22.5022 | 31.9446 | 89.6908 |  | 48.6664 | 76.1996 | 80.4688 | 50.9797 |  | 16.9886 | 17.143 | 16.615 | 16.9812 | 17.2584 | 19.0008 | 47.466 | 15.9199 | 17.0683 | 15.9376 | 17.5643 | 18.154 | 44.0583 | 46.8575 | 43.4056 | 21.5897 |  |  | 0.66655 | -0.29445 | -27.8494 | 0.43037 | -0.034696 | -197.8782 | 19.1598 | 0.319 | -0.16434 | -0.062199 | 0.04317 | 0.00036634 | 0.0003417 | 1.8306 | 21.7769 | 21.9928 | 22.1876 | 22.2468 | 22.0593 | 21.356 | 20.1762 | 22.1961 | 22.3709 | 22.4027 | 22.3579 | 21.9751 | 21.2039 | 22.2844 | 48.2466 | 33.2223 | 33.8887 | 25.67 | 22.9026 | 29.1829 | 22.4934 | 22.3344 | 22.1169 | 21.6763 | 22.0735 | 21.7802 | 21.2795 | 21.9371 | 21.5456 | 21.3886 | 31.4574 | 95.7018 | 72.1018 | 42.351 | 0.34701 | -0.018609 | 38.8023 | 21.9895 | 22.3088 | 20.1745 | 21.6201 | 22.061 | 21.9252 | 21.7097 | 23.5361 | 21.7763 | 21.4453 | 21.7881 | 88.5587 | 105.8056 | 68.3504 | 69.3375 | 41.0741 |  | 31.0995 | 60.7593 | 33.2966 | 44.6571 | 32.0074 | 37.5281 |  | 41.9515 |  |  | 21.205 | 22.1796 | 35.2251 | [5 empty] | 21.8987 | 33.0239 | 21.6544 | 22.0346 | 26.5038 | 21.1839 | 21.8161 | 21.8551 | 41.8832 | 113.4837 |  | 34.2264 | 82.2399 | 20.2143 | 36.1323 | 85.4328 | 27.7152 | 69.2802 | 21.4364 | 64.3022 | 21.4991 | 66.6237 | 18.6236 | 36.1219 | 77.4535 | 22.9407 | 36.994 | 101.9707 | 20.3726 | 35.2083 | 87.6196 | 20.4844 | 61.6055 | 23.6937 | 68.4116 | 21.6808 | 67.8462 | 0.16533 | 19.8701 | 0.77648 | 0.022389 | -27.0236 | 3.0954 | 58 | 52.37 | 1.0986 | -0.64431 | -6.266 | 0.77894 | -0.22188 | -16.756 | 5.2139 | 0.20878 | -0.26282 | 0.1403 | -1.6445 | -0.83297 | -0.037482 | 0.18554
42838.4228 | 216 | 22.9075 | 22.8749 | 22.8601 | 22.7757 | 22.3958 | 21.7281 | 22.713 | 21.7752 | 22.3611 | 22.3755 | 22.3417 | 21.9964 | 21.2113 | 22.1757 | 21.6243 | 21.7935 | 21.9167 | 21.1014 | 21.1981 | 21.4056 | 20.4905 | 20.6786 | 21.3286 | 21.8865 | 21.6489 | 22.6779 | 96.1012 | 86.3717 | 99.9949 | 22.1083 | 21.7046 | 22.0663 | 22.0087 | 21.7531 | 22.507 | 32.0293 | 89.6474 |  | 48.7872 | 76.4115 | 80.5124 | 51.0948 |  | 16.9772 | 17.1449 | 16.6174 | 16.967 | 17.2575 | 18.9706 | 47.3482 | 15.879 | 17.0632 | 15.9834 | 17.5641 | 18.1582 | 44.0933 | 46.845 | 43.4039 | 21.5842 |  |  | 0.52527 | -0.24977 | -27.7015 | 0.50265 | 0.1401 | -197.8006 | 18.9429 | 0.38734 | -0.10538 | -0.054647 | -0.014118 | 0.00033184 | 0.00029077 | 1.8358 | 21.7674 | 21.9848 | 22.1772 | 22.2364 | 22.0508 | 21.3518 | 20.1625 | 22.1887 | 22.3573 | 22.3964 | 22.3505 | 21.9655 | 21.1915 | 22.2739 | 48.7856 | 32.9169 | 34.2963 | 25.3603 | 22.5807 | 29.2967 | 22.5529 | 22.3464 | 22.1055 | 21.675 | 22.0701 | 21.7791 | 21.2828 | 21.9335 | 21.554 | 21.4012 | 31.5382 | 95.9415 | 72.5765 | 42.5298 | 0.40068 | 0.18262 | 38.8352 | 21.9909 | 22.3025 | 20.1719 | 21.6172 | 22.0567 | 21.9218 | 21.7138 | 23.5577 | 21.7687 | 21.4411 | 21.7903 | 88.6876 | 106.0201 | 68.4524 | 69.4546 | 41.0434 |  | 31.1703 | 60.3107 | 33.3614 | 44.7371 | 32.0795 | 37.4967 |  | 42.0677 |  |  | 21.2075 | 22.1874 | 35.4308 | [5 empty] | 21.9075 | 33.0309 | 21.6599 | 22.0479 | 26.5401 | 21.1836 | 21.8157 | 21.872 | 42.1121 | 113.3332 |  | 34.299 | 82.3644 | 20.2309 | 36.4104 | 85.5446 | 27.7463 | 69.3535 | 21.4425 | 64.3717 | 21.5116 | 66.7583 | 18.6111 | 36.2228 | 77.6278 | 22.9537 | 37.106 | 102.0922 | 20.3798 | 35.2498 | 87.7336 | 20.5031 | 61.7367 | 23.7059 | 68.4374 | 21.6903 | 67.899 | 0.2655 | 19.8692 | 0.77852 | 0.022222 | -27.0573 | 3.0953 | 57.04 | 51.75 | 0.97565 | -0.59341 | -6.2494 | 0.84182 | 0.44582 | -16.7518 | 5.1841 | 0.21205 | -0.24813 | 0.14054 | -1.691 | -0.8713 | -0.037781 | 0.18334
42838.4228 | 217 | 22.9088 | 22.8707 | 22.8612 | 22.7814 | 22.4041 | 21.729 | 22.7172 | 21.7802 | 22.3682 | 22.373 | 22.3472 | 21.9971 | 21.2062 | 22.1801 | 21.6195 | 21.7903 | 21.9111 | 21.0886 | 21.1929 | 21.4068 | 20.4806 | 20.6673 | 21.3218 | 21.876 | 21.6527 | 22.6945 | 96.2318 | 86.5092 | 100.1839 | 22.1153 | 21.7041 | 22.0787 | 22.0069 | 21.7506 | 22.5211 | 32.0999 | 89.104 |  | 48.9071 | 76.5742 | 80.5514 | 51.5132 |  | 16.9787 | 17.1443 | 16.6185 | 16.9599 | 17.243 | 18.9695 | 47.2863 | 15.8228 | 17.0623 | 15.9971 | 17.5562 | 18.153 | 44.1328 | 46.8385 | 43.4074 | 21.5827 |  |  | 0.56929 | -0.37199 | -27.4709 | 0.38305 | 0.14141 | -197.8447 | 18.8956 | 0.30651 | -0.095066 | 0.2053 | 0.13344 | 0.00032363 | 0.00034992 | 1.8298 | 21.7745 | 21.9859 | 22.1824 | 22.2336 | 22.0569 | 21.3563 | 20.1695 | 22.1901 | 22.3693 | 22.3993 | 22.3529 | 21.9697 | 21.1995 | 22.2694 | 49.121 | 33.3535 | 36.3886 | 25.6946 | 22.7346 | 29.4102 | 22.6561 | 22.3554 | 22.1195 | 21.6845 | 22.0805 | 21.7877 | 21.2985 | 21.9356 | 21.5652 | 21.4199 | 31.6082 | 96.0917 | 72.834 | 42.5919 | 0.5503 | 0.097413 | 38.7808 | 21.9961 | 22.3045 | 20.1763 | 21.6162 | 22.0613 | 21.9193 | 21.7147 | 23.5852 | 21.7684 | 21.4456 | 21.803 | 88.7958 | 106.0258 | 68.5768 | 69.5959 | 40.9057 |  | 31.2494 | 60.4048 | 33.4281 | 44.8233 | 32.1636 | 37.8461 |  | 42.1761 |  |  | 21.2311 | 22.203 | 35.3688 | [5 empty] | 21.9043 | 33.0476 | 21.6648 | 22.0404 | 26.5687 | 21.1917 | 21.8245 | 21.8679 | 42.323 | 113.6119 |  | 34.3256 | 82.4795 | 20.2294 | 36.6851 | 85.6388 | 27.7838 | 69.4292 | 21.4523 | 64.4893 | 21.5235 | 66.8453 | 18.6077 | 36.3764 | 77.8273 | 22.9725 | 37.2005 | 102.2556 | 20.3803 | 35.3431 | 87.6984 | 20.5087 | 61.8151 | 23.7371 | 68.4927 | 21.7079 | 67.979 | 0.34879 | 19.8663 | 0.78218 | 0.024269 | -27.1469 | 3.0954 | 55.76 | 52.57 | 1.016 | -0.72419 | -6.2233 | 0.73488 | 0.44791 | -16.7536 | 5.1776 | 0.21858 | -0.24845 | 0.14103 | -1.7149 | -1.0917 | -0.046987 | 0.184
42838.4228 | 218 | 22.9069 | 22.8716 | 22.8633 | 22.7813 | 22.3978 | 21.7308 | 22.717 | 21.7819 | 22.366 | 22.3719 | 22.3434 | 21.9959 | 21.2103 | 22.1793 | 21.616 | 21.7844 | 21.9037 | 21.0941 | 21.1926 | 21.3997 | 20.4792 | 20.6623 | 21.3282 | 21.8686 | 21.6421 | 22.7046 | 96.2834 | 86.6222 | 100.1025 | 22.1168 | 21.7046 | 22.0968 | 22.0081 | 21.7546 | 22.5419 | 32.1792 | 89.0901 |  | 49.0349 | 76.6848 | 80.6041 | 51.339 |  | 16.9925 | 17.1568 | 16.6298 | 16.9734 | 17.2404 | 18.9553 | 47.6476 | 15.8239 | 17.065 | 16.0923 | 17.5678 | 18.1486 | 44.1603 | 46.8335 | 43.4169 | 21.5787 |  |  | 0.57521 | -0.33191 | -27.7666 | 0.39357 | 0.18938 | -197.798 | 19.3431 | 0.40442 | -0.086698 | 0.14508 | 0.059142 | 0.00030227 | 0.00031706 | 1.8276 | 21.7765 | 21.9981 | 22.1803 | 22.2393 | 22.0575 | 21.3661 | 20.168 | 22.1956 | 22.3671 | 22.4073 | 22.3472 | 21.9683 | 21.2033 | 22.2768 | 49.5844 | 33.4814 | 37.1168 | 26.2925 | 23.4014 | 29.5281 | 22.7536 | 22.353 | 22.1205 | 21.6795 | 22.0772 | 21.7912 | 21.2943 | 21.9466 | 21.5553 | 21.4223 | 31.6752 | 96.346 | 73.0332 | 42.5065 | 0.50115 | 0.057852 | 38.7422 | 21.9906 | 22.3032 | 20.1624 | 21.609 | 22.0555 | 21.9122 | 21.7042 | 23.6003 | 21.7646 | 21.4421 | 21.8082 | 88.8865 | 105.9562 | 68.7141 | 69.7394 | 40.9512 |  | 31.3277 | 60.1344 | 33.5076 | 45.0411 | 32.2514 | 38.109 |  | 42.2959 |  |  | 21.2176 | 22.1993 | 35.4317 | [5 empty] | 21.8882 | 33.1174 | 21.6473 | 22.0326 | 26.5352 | 21.176 | 21.8119 | 21.8915 | 42.402 | 113.8845 |  | 34.3529 | 82.5208 | 20.2468 | 36.7744 | 85.8305 | 27.8186 | 69.4939 | 21.4578 | 64.563 | 21.5439 | 66.9797 | 18.5881 | 36.4456 | 77.9273 | 22.9854 | 37.2867 | 102.414 | 20.385 | 35.4158 | 87.6936 | 20.5164 | 61.864 | 23.7514 | 68.6771 | 21.7145 | 68.022 | 0.42652 | 19.861 | 0.78487 | 0.023645 | -27.0547 | 3.0954 | 34.86 | 51.33 | 1.0211 | -0.68408 | -6.2569 | 0.74491 | 0.51833 | -16.7513 | 5.2384 | 0.21999 | -0.23822 | 0.13798 | -1.7526 | -1.1612 | -0.039432 | 0.18867
42838.4228 | 219 | 22.9088 | 22.8742 | 22.861 | 22.7763 | 22.3962 | 21.7283 | 22.7215 | 21.7799 | 22.3628 | 22.3677 | 22.3471 | 21.9981 | 21.2088 | 22.1791 | 21.6122 | 21.7839 | 21.9088 | 21.0876 | 21.1862 | 21.3995 | 20.4787 | 20.6618 | 21.3355 | 21.865 | 21.641 | 22.7215 | 96.3111 | 86.7507 | 99.9016 | 22.119 | 21.7066 | 22.107 | 22.0102 | 21.7578 | 22.5549 | 32.2547 | 89.7025 |  | 49.1622 | 76.7371 | 80.6434 | 51.1959 |  | 16.9945 | 17.1656 | 16.6279 | 16.9723 | 17.2461 | 18.9399 | 47.5874 | 15.8141 | 17.0666 | 16.0987 | 17.5741 | 18.1592 | 44.1779 | 46.8418 | 43.4331 | 21.5899 |  |  | 0.67837 | -0.21429 | -27.8152 | 0.53485 | 0.15784 | -197.8348 | 18.9285 | 0.52139 | -0.3605 | 0.061583 | 0.051677 | 0.0003417 | 0.00034499 | 1.8415 | 21.772 | 21.9941 | 22.1768 | 22.2344 | 22.0581 | 21.3575 | 20.1702 | 22.1904 | 22.3693 | 22.4065 | 22.356 | 21.9725 | 21.1949 | 22.2691 | 49.3028 | 33.2884 | 37.0958 | 26.3495 | 23.394 | 29.643 | 22.8297 | 22.3479 | 22.1167 | 21.675 | 22.0696 | 21.79 | 21.2921 | 21.9481 | 21.5516 | 21.4275 | 31.7419 | 96.4837 | 73.1984 | 42.3587 | 0.5037 | -0.068631 | 38.7164 | 21.9818 | 22.2976 | 20.1599 | 21.6055 | 22.0502 | 21.9069 | 21.6975 | 23.6208 | 21.7568 | 21.4357 | 21.81 | 88.9733 | 105.9007 | 68.8388 | 69.8561 | 40.7727 |  | 31.403 | 60.5809 | 33.5902 | 45.0819 | 32.3338 | 38.3472 |  | 42.3968 |  |  | 21.2366 | 22.2116 | 35.3706 | [5 empty] | 21.8984 | 33.4772 | 21.6582 | 22.0411 | 26.5612 | 21.1898 | 21.8186 | 21.8886 | 42.4417 | 114.2107 |  | 34.4401 | 82.5301 | 20.2413 | 36.6901 | 85.9589 | 27.8521 | 69.6274 | 21.4519 | 64.7165 | 21.5575 | 67.0872 | 18.5824 | 36.5557 | 77.9322 | 22.997 | 37.3523 | 102.5578 | 20.383 | 35.4658 | 87.79 | 20.5022 | 61.9458 | 23.7709 | 68.7641 | 21.7171 | 68.1232 | 0.38552 | 19.8587 | 0.7874 | 0.024081 | -27.0877 | 3.0954 | 56.98 | 52.41 | 1.1086 | -0.54966 | -6.2624 | 0.8684 | 0.47319 | -16.7524 | 5.1818 | 0.22752 | -0.24778 | 0.13967 | -1.7078 | -1.15 | -0.032873 | 0.19506
42838.4228 | 220 | 22.9092 | 22.8795 | 22.8685 | 22.7858 | 22.4001 | 21.7295 | 22.725 | 21.7834 | 22.3675 | 22.372 | 22.3489 | 22.0019 | 21.2056 | 22.1815 | 21.6063 | 21.7766 | 21.9007 | 21.0819 | 21.1813 | 21.398 | 20.4709 | 20.6582 | 21.334 | 21.8622 | 21.6358 | 22.7282 | 96.4051 | 86.8478 | 100.2783 | 22.1146 | 21.7102 | 22.1126 | 22.0063 | 21.7504 | 22.5733 | 32.3247 | 90.4049 |  | 49.2748 | 76.7375 | 80.6522 | 51.454 |  | 16.9982 | 17.17 | 16.6181 | 16.9693 | 17.2426 | 18.9229 | 47.6222 | 15.7673 | 17.0645 | 16.0427 | 17.5739 | 18.1623 | 44.1786 | 46.8404 | 43.4547 | 21.5913 |  |  | 0.60215 | -0.30497 | -27.8113 | 0.47374 | 0.23209 | -197.8499 | 18.9265 | 0.32886 | -0.11939 | -0.073319 | 0.014006 | 0.0003532 | 0.00033349 | 1.8371 | 21.7796 | 21.997 | 22.1885 | 22.247 | 22.058 | 21.3642 | 20.1735 | 22.1942 | 22.3692 | 22.4005 | 22.3566 | 21.9765 | 21.2098 | 22.2814 | 49.0911 | 32.4843 | 35.93 | 26.102 | 23.3871 | 29.7572 | 22.8953 | 22.3398 | 22.1114 | 21.6791 | 22.0734 | 21.7839 | 21.2933 | 21.9402 | 21.5553 | 21.4321 | 31.8224 | 96.5918 | 73.3793 | 42.1696 | 0.49466 | 0.047201 | 38.6896 | 21.9861 | 22.304 | 20.1632 | 21.6091 | 22.0536 | 21.9103 | 21.7027 | 23.6493 | 21.7618 | 21.4411 | 21.8287 | 89.074 | 105.954 | 68.9713 | 69.9536 | 40.6661 |  | 31.4733 | 61.2027 | 33.6747 | 44.9782 | 32.412 | 38.2712 |  | 42.4943 |  |  | 21.2312 | 22.2168 | 35.2416 | [5 empty] | 21.8936 | 33.5654 | 21.6636 | 22.0364 | 26.575 | 21.1898 | 21.82 | 21.9001 | 42.5362 | 114.7413 |  | 34.5189 | 82.6704 | 20.2569 | 36.6838 | 86.0316 | 27.9276 | 69.7088 | 21.4644 | 64.8994 | 21.5764 | 67.206 | 18.5783 | 36.7204 | 77.9516 | 23.0226 | 37.389 | 102.6549 | 20.388 | 35.5541 | 87.9125 | 20.4972 | 62.0571 | 23.7946 | 68.7938 | 21.7327 | 68.2367 | 0.2106 | 19.8561 | 0.79009 | 0.023297 | -26.9834 | 3.0954 | 49.51 | 51.87 | 1.045 | -0.65574 | -6.262 | 0.81729 | 0.57378 | -16.7525 | 5.1814 | 0.23289 | -0.26216 | 0.14523 | -1.6709 | -1.0128 | -0.037645 | 0.20306
42838.4228 | 221 | 22.9114 | 22.8722 | 22.8515 | 22.7801 | 22.3933 | 21.7299 | 22.7133 | 21.7771 | 22.3657 | 22.3694 | 22.3391 | 21.9885 | 21.2056 | 22.181 | 21.6058 | 21.7739 | 21.9031 | 21.0784 | 21.1884 | 21.4036 | 20.4717 | 20.6585 | 21.3412 | 21.8615 | 21.6456 | 22.7467 | 96.5343 | 86.9997 | 100.5945 | 22.1112 | 21.7079 | 22.1292 | 22.0098 | 21.7547 | 22.5859 | 32.3871 | 90.8743 |  | 49.39 | 76.7932 | 80.7235 | 51.6879 |  | 16.9966 | 17.173 | 16.6211 | 16.9539 | 17.2415 | 18.8994 | 47.4001 | 15.7194 | 17.0496 | 15.935 | 17.5751 | 18.1602 | 44.1687 | 46.8416 | 43.4612 | 21.5903 |  |  | 0.6948 | -0.4055 | -27.5083 | 0.55785 | 0.22026 | -197.8657 | 19.211 | 0.21977 | -0.057314 | -0.097446 | 0.14143 | 0.00036634 | 0.00031049 | 1.8283 | 21.7801 | 21.9941 | 22.1869 | 22.2476 | 22.0598 | 21.3628 | 20.1761 | 22.1968 | 22.3698 | 22.4017 | 22.3622 | 21.9808 | 21.2113 | 22.2799 | 49.2397 | 32.4108 | 36.0517 | 25.836 | 23.2267 | 29.8772 | 22.9626 | 22.3465 | 22.1158 | 21.6767 | 22.0695 | 21.7844 | 21.2942 | 21.9445 | 21.5553 | 21.4472 | 31.8968 | 96.6148 | 73.5112 | 42.1759 | 0.41248 | 0.11986 | 38.8313 | 21.9885 | 22.3085 | 20.171 | 21.6168 | 22.0626 | 21.9137 | 21.7158 | 23.6726 | 21.772 | 21.4489 | 21.8454 | 89.1505 | 106.14 | 69.1397 | 70.0828 | 40.5133 |  | 31.5518 | 61.6562 | 33.7832 | 44.7843 | 32.4969 | 38.2351 |  | 42.6015 |  |  | 21.2163 | 22.2361 | 35.3971 | [5 empty] | 21.9022 | 33.573 | 21.6615 | 22.0411 | 26.6036 | 21.1907 | 21.825 | 21.9099 | 42.605 | 114.7456 |  | 34.5442 | 82.786 | 20.2543 | 36.7967 | 86.1429 | 27.9934 | 69.768 | 21.4759 | 65.0257 | 21.583 | 67.3336 | 18.5737 | 36.8801 | 78.0663 | 23.0326 | 37.4316 | 102.6533 | 20.3862 | 35.622 | 88.0889 | 20.4936 | 62.1935 | 23.8172 | 68.8044 | 21.7401 | 68.3696 | 0.22525 | 19.8535 | 0.79241 | 0.023398 | -27.0671 | 3.0954 | 53.8 | 51.58 | 1.123 | -0.75615 | -6.2279 | 0.88688 | 0.55894 | -16.7525 | 5.22 | 0.23982 | -0.27103 | 0.15352 | -1.6733 | -1.0184 | -0.042005 | 0.20543
42838.4228 | 222 | 22.9151 | 22.8878 | 22.8644 | 22.7895 | 22.4013 | 21.7343 | 22.7239 | 21.7893 | 22.373 | 22.3734 | 22.3402 | 22.0062 | 21.2145 | 22.1793 | 21.6112 | 21.7854 | 21.9104 | 21.0857 | 21.1932 | 21.409 | 20.4764 | 20.6633 | 21.3564 | 21.8701 | 21.6516 | 22.767 | 96.5592 | 87.1072 | 100.5915 | 22.1205 | 21.7133 | 22.1383 | 22.0132 | 21.7623 | 22.599 | 32.4712 | 90.6627 |  | 49.5139 | 76.9391 | 80.8319 | 51.7432 |  | 16.9938 | 17.1747 | 16.6137 | 16.9648 | 17.2515 | 18.9112 | 47.1088 | 15.7438 | 17.0586 | 15.8319 | 17.577 | 18.1527 | 44.1608 | 46.8382 | 43.4649 | 21.5916 |  |  | 0.59098 | -0.33125 | -27.6719 | 0.46782 | 0.27612 | -197.8473 | 19.1677 | 0.58579 | 0.079879 | 0.11676 | 0.13691 | 0.0003532 | 0.00033184 | 1.8069 | 21.7764 | 21.9971 | 22.1885 | 22.2425 | 22.0541 | 21.3626 | 20.1732 | 22.1916 | 22.37 | 22.4028 | 22.3598 | 21.979 | 21.2039 | 22.2834 | 49.3102 | 32.7907 | 37.3986 | 25.947 | 23.5327 | 29.9938 | 23.0485 | 22.3486 | 22.1196 | 21.6798 | 22.0733 | 21.7862 | 21.2951 | 21.9425 | 21.5592 | 21.4545 | 31.9658 | 96.5728 | 73.6988 | 42.0933 | 0.24714 | 0.15619 | 38.9386 | 21.9812 | 22.3016 | 20.1734 | 21.6131 | 22.0564 | 21.9172 | 21.7162 | 23.697 | 21.7732 | 21.45 | 21.8466 | 89.2101 | 106.3541 | 69.2515 | 70.2291 | 40.7193 |  | 31.6236 | 62.1677 | 33.9016 | 44.4702 | 32.5768 | 38.3441 |  | 42.701 |  |  | 21.2171 | 22.2352 | 35.6194 | [5 empty] | 21.8916 | 33.5062 | 21.6618 | 22.0378 | 26.5997 | 21.1881 | 21.8211 | 21.9128 | 42.6884 | 114.7751 |  | 34.567 | 82.8501 | 20.2558 | 36.9282 | 86.2826 | 28.0223 | 69.8502 | 21.4816 | 65.0497 | 21.5978 | 67.4374 | 18.5786 | 37.0141 | 78.155 | 23.0455 | 37.5209 | 102.7021 | 20.3999 | 35.6261 | 88.3207 | 20.4921 | 62.2511 | 23.8325 | 68.8497 | 21.7458 | 68.5634 | 0.31577 | 19.8505 | 0.79439 | 0.023006 | -27.0546 | 3.0954 | 66.17 | 53.18 | 1.0357 | -0.68342 | -6.2464 | 0.81217 | 0.62582 | -16.7521 | 5.2142 | 0.23655 | -0.28117 | 0.16498 | -1.6674 | -1.158 | -0.040663 | 0.21009
42838.4229 | 223 | 22.9122 | 22.8781 | 22.8604 | 22.785 | 22.4015 | 21.7324 | 22.7292 | 21.7874 | 22.3636 | 22.3658 | 22.3498 | 21.9985 | 21.2126 | 22.1799 | 21.6138 | 21.7837 | 21.9033 | 21.0887 | 21.1875 | 21.4104 | 20.4781 | 20.6677 | 21.3671 | 21.8726 | 21.6466 | 22.788 | 96.5677 | 87.1445 | 100.3343 | 22.108 | 21.7064 | 22.1492 | 22.0037 | 21.7588 | 22.6115 | 32.5412 | 91.1787 |  | 49.6933 | 77.1382 | 80.9423 | 51.4455 |  | 16.9831 | 17.1771 | 16.6066 | 16.9779 | 17.2582 | 18.9157 | 46.9719 | 15.7809 | 17.0573 | 15.7347 | 17.5855 | 18.1603 | 44.1562 | 46.839 | 43.4663 | 21.5915 |  |  | 0.72437 | -0.20903 | -27.7646 | 0.75498 | 0.14995 | -197.8342 | 18.9351 | 0.26314 | 0.056333 | 0.0082934 | 0.08605 | 0.00034499 | 0.00032035 | 1.7963 | 21.7729 | 21.9899 | 22.1845 | 22.2359 | 22.0505 | 21.3556 | 20.1699 | 22.1921 | 22.3646 | 22.4047 | 22.3558 | 21.9781 | 21.2007 | 22.2804 | 48.4334 | 32.4536 | 38.764 | 26.4223 | 23.6036 | 30.0783 | 23.1383 | 22.3442 | 22.1179 | 21.6758 | 22.0678 | 21.7839 | 21.2968 | 21.9422 | 21.5625 | 21.4647 | 32.0281 | 96.5346 | 73.8156 | 42.131 | 0.37866 | 0.020192 | 38.9492 | 21.9837 | 22.3017 | 20.1721 | 21.6167 | 22.0547 | 21.9183 | 21.7134 | 23.7225 | 21.7757 | 21.4433 | 21.8559 | 89.3068 | 106.668 | 69.3542 | 70.3142 | 40.4503 |  | 31.6873 | 62.1211 | 33.9825 | 44.4119 | 32.652 | 38.5161 |  | 42.8049 |  |  | 21.2166 | 22.2396 | 35.6686 | [5 empty] | 21.8926 | 33.4626 | 21.6591 | 22.0386 | 26.6199 | 21.1893 | 21.8232 | 21.9176 | 42.7564 | 114.7471 |  | 34.6064 | 82.8931 | 20.2539 | 36.9811 | 86.3317 | 28.0356 | 69.9429 | 21.4792 | 65.0457 | 21.6008 | 67.5091 | 18.585 | 37.1677 | 78.251 | 23.065 | 37.6222 | 102.7563 | 20.4175 | 35.5575 | 88.586 | 20.4984 | 62.2559 | 23.8483 | 68.8855 | 21.7601 | 68.7281 | 0.27775 | 19.8471 | 0.79639 | 0.022883 | -27.1237 | 3.0954 | 57.65 | 51.41 | 1.1463 | -0.54289 | -6.2569 | 1.0318 | 0.46119 | -16.7517 | 5.1825 | 0.2462 | -0.2771 | 0.16918 | -1.5601 | -1.2992 | -0.029996 | 0.21117
42838.4229 | 224 | 22.9112 | 22.8744 | 22.8655 | 22.7881 | 22.4069 | 21.729 | 22.7241 | 21.7893 | 22.373 | 22.372 | 22.3512 | 22.0067 | 21.2088 | 22.1898 | 21.6141 | 21.7865 | 21.9043 | 21.0945 | 21.1934 | 21.4102 | 20.4777 | 20.6697 | 21.3705 | 21.8721 | 21.6411 | 22.799 | 96.5585 | 87.2326 | 99.8626 | 22.1065 | 21.7038 | 22.1512 | 22.0016 | 21.7564 | 22.6154 | 32.6056 | 92.0234 |  | 49.8418 | 77.3058 | 81.0075 | 51.1022 |  | 16.9879 | 17.1719 | 16.6059 | 16.9776 | 17.2601 | 18.9283 | 46.9258 | 15.7605 | 17.0623 | 15.6707 | 17.5847 | 18.1606 | 44.1349 | 46.8341 | 43.4642 | 21.5873 |  |  | 0.66063 | -0.30694 | -28.1996 | 0.52368 | 0.082272 | -197.8177 | 18.6584 | 0.37157 | -0.076384 | 0.089906 | 0.025984 | 0.00037127 | 0.00029077 | 1.8161 | 21.7684 | 21.9832 | 22.1822 | 22.2362 | 22.052 | 21.3552 | 20.1649 | 22.1851 | 22.3655 | 22.3997 | 22.353 | 21.966 | 21.1991 | 22.2747 | 47.7943 | 33.1313 | 39.7859 | 27.1272 | 23.9612 | 30.1735 | 23.2347 | 22.3347 | 22.1111 | 21.6744 | 22.0739 | 21.7795 | 21.2928 | 21.9385 | 21.5555 | 21.4662 | 32.0987 | 96.5044 | 73.8593 | 42.2091 | 0.21804 | -0.035536 | 38.9486 | 21.9882 | 22.3019 | 20.1692 | 21.6108 | 22.0552 | 21.9106 | 21.7163 | 23.7449 | 21.7692 | 21.446 | 21.8693 | 89.4583 | 106.9202 | 69.4552 | 70.3705 | 40.057 |  | 31.752 | 62.1164 | 34.0669 | 44.49 | 32.7332 | 38.4148 |  | 42.8941 |  |  | 21.2275 | 22.2483 | 35.6646 | [5 empty] | 21.895 | 33.5059 | 21.6616 | 22.045 | 26.6442 | 21.1989 | 21.8257 | 21.9425 | 42.8323 | 114.765 |  | 34.6879 | 82.9502 | 20.2654 | 37.0061 | 86.3656 | 28.0733 | 70.0636 | 21.4913 | 65.1061 | 21.6291 | 67.5832 | 18.5846 | 37.2983 | 78.3623 | 23.0786 | 37.7047 | 102.8507 | 20.4222 | 35.5015 | 88.7861 | 20.504 | 62.3056 | 23.866 | 68.8662 | 21.7771 | 68.7706 | 0.30965 | 19.8431 | 0.79823 | 0.021642 | -27.0672 | 3.0954 | 64.7 | 52.66 | 1.094 | -0.65786 | -6.3056 | 0.85929 | 0.34162 | -16.7513 | 5.1446 | 0.25934 | -0.27407 | 0.16979 | -1.4779 | -1.4015 | -0.018251 | 0.21142
42838.4229 | 225 | 22.9137 | 22.8744 | 22.8543 | 22.7821 | 22.4031 | 21.7321 | 22.7178 | 21.7861 | 22.3715 | 22.3696 | 22.343 | 22.0043 | 21.2116 | 22.1782 | 21.6138 | 21.7888 | 21.9114 | 21.0959 | 21.192 | 21.4111 | 20.4764 | 20.6665 | 21.3764 | 21.8737 | 21.6472 | 22.817 | 96.5457 | 87.3456 | 99.3744 | 22.1145 | 21.7095 | 22.1682 | 22.0063 | 21.7558 | 22.6308 | 32.6754 | 92.6988 |  | 49.9945 | 77.4536 | 81.0929 | 50.6831 |  | 16.9825 | 17.1691 | 16.6068 | 16.9783 | 17.252 | 18.9528 | 47.005 | 15.7242 | 17.0631 | 15.664 | 17.5883 | 18.1689 | 44.1181 | 46.8474 | 43.4705 | 21.5963 |  |  | 0.47664 | -0.10192 | -28.1832 | 0.62553 | 0.32409 | -197.8407 | 18.8654 | 0.25854 | 0.037067 | 0.12368 | 0.15115 | 0.0003647 | 0.00034827 | 1.8376 | 21.7673 | 21.9824 | 22.1827 | 22.241 | 22.0517 | 21.3438 | 20.1635 | 22.1854 | 22.3659 | 22.4042 | 22.346 | 21.9649 | 21.1931 | 22.2773 | 46.2009 | 33.2475 | 38.9698 | 27.1158 | 24.2719 | 30.2335 | 23.3043 | 22.3513 | 22.1166 | 21.6811 | 22.0728 | 21.7814 | 21.2868 | 21.9426 | 21.5565 | 21.4781 | 32.1765 | 96.428 | 73.9187 | 42.2584 | 0.11896 | 0.15181 | 38.9985 | 21.9853 | 22.2989 | 20.1719 | 21.6113 | 22.0607 | 21.9125 | 21.7159 | 23.7651 | 21.7664 | 21.4469 | 21.8838 | 89.5581 | 107.0794 | 69.5669 | 70.4378 | 39.764 |  | 31.8147 | 62.424 | 34.1548 | 44.5143 | 32.8064 | 38.4694 |  | 42.9958 |  |  | 21.2369 | 22.257 | 35.8401 | [5 empty] | 21.891 | 33.5562 | 21.6556 | 22.0434 | 26.6716 | 21.1943 | 21.83 | 21.9574 | 42.934 | 114.5564 |  | 34.7908 | 83.0423 | 20.2755 | 37.0889 | 86.369 | 28.1201 | 70.1947 | 21.505 | 65.2936 | 21.652 | 67.6717 | 18.5952 | 37.3686 | 78.4646 | 23.0961 | 37.783 | 102.8724 | 20.4364 | 35.5505 | 88.9387 | 20.5062 | 62.3665 | 23.8848 | 68.9345 | 21.7838 | 68.7991 | 0.33525 | 19.8408 | 0.79954 | 0.022549 | -27.1023 | 3.0954 | 65.57 | 51.59 | 0.92862 | -0.37908 | -6.3038 | 0.93914 | 0.67806 | -16.753 | 5.1733 | 0.26962 | -0.2796 | 0.17163 | -1.2938 | -1.3027 | -0.0042211 | 0.21271
42838.4229 | 226 | 22.9114 | 22.8723 | 22.8543 | 22.7761 | 22.3944 | 21.7249 | 22.7132 | 21.7808 | 22.3653 | 22.3688 | 22.3343 | 21.9948 | 21.2061 | 22.1739 | 21.6189 | 21.7898 | 21.9164 | 21.0968 | 21.1986 | 21.4163 | 20.4863 | 20.6749 | 21.3964 | 21.8775 | 21.6565 | 22.8453 | 96.6253 | 87.4487 | 99.2896 | 22.1168 | 21.7176 | 22.1921 | 22.0126 | 21.7657 | 22.6543 | 32.7489 | 92.3976 |  | 50.1387 | 77.5791 | 81.1947 | 50.34 |  | 16.992 | 17.1772 | 16.6096 | 16.9713 | 17.2461 | 19.0112 | 47.0016 | 15.7323 | 17.0571 | 15.7661 | 17.5906 | 18.1626 | 44.094 | 46.8526 | 43.4691 | 21.5911 |  |  | 0.7224 | -0.078921 | -28.1221 | 0.69847 | 0.28532 | -197.8506 | 18.9765 | 0.19152 | -0.077747 | 0.23005 | -0.032866 | 0.00033184 | 0.00029899 | 1.8288 | 21.7751 | 21.985 | 22.1857 | 22.2374 | 22.0572 | 21.3544 | 20.1635 | 22.1926 | 22.3697 | 22.4005 | 22.3565 | 21.9721 | 21.202 | 22.2819 | 44.11 | 31.8891 | 35.9803 | 26.3087 | 23.8406 | 30.2565 | 23.3389 | 22.3433 | 22.1116 | 21.6783 | 22.0722 | 21.7802 | 21.2878 | 21.9433 | 21.5594 | 21.4881 | 32.2429 | 96.4435 | 73.9342 | 42.2688 | 0.28862 | -0.085559 | 39.1059 | 22.0005 | 22.3046 | 20.1813 | 21.6229 | 22.0736 | 21.927 | 21.7282 | 23.804 | 21.777 | 21.457 | 21.9039 | 89.6339 | 107.2778 | 69.7067 | 70.5535 | 39.7932 |  | 31.8826 | 63.0151 | 34.2687 | 44.4121 | 32.8795 | 38.5197 |  | 43.0846 |  |  | 21.2405 | 22.2703 | 35.7631 | [5 empty] | 21.8987 | 33.5796 | 21.6601 | 22.0399 | 26.7072 | 21.1931 | 21.8316 | 21.965 | 43.007 | 114.3958 |  | 34.8802 | 83.1037 | 20.279 | 37.208 | 86.4631 | 28.1571 | 70.2882 | 21.5075 | 65.4475 | 21.666 | 67.7588 | 18.5987 | 37.3339 | 78.5417 | 23.1184 | 37.8828 | 102.8273 | 20.4445 | 35.6568 | 89.044 | 20.4991 | 62.4006 | 23.9033 | 69.1954 | 21.7896 | 68.8584 | 0.32987 | 19.837 | 0.80069 | 0.021881 | -27.1059 | 3.0954 | 54.67 | 51.66 | 1.1431 | -0.33359 | -6.297 | 0.9924 | 0.63627 | -16.7551 | 5.189 | 0.27113 | -0.2921 | 0.17697 | -1.0588 | -0.96645 | 0.0078287 | 0.2147
42838.4229 | 227 | 22.9164 | 22.8772 | 22.8615 | 22.7831 | 22.3996 | 21.7283 | 22.7218 | 21.7837 | 22.3708 | 22.377 | 22.3437 | 21.9993 | 21.2098 | 22.1773 | 21.6195 | 21.787 | 21.9133 | 21.0866 | 21.194 | 21.4156 | 20.4883 | 20.6747 | 21.3949 | 21.8728 | 21.6449 | 22.8582 | 96.6356 | 87.5133 | 99.0024 | 22.1261 | 21.7177 | 22.2004 | 22.0164 | 21.7678 | 22.6694 | 32.8216 | 91.3606 |  | 50.2577 | 77.6584 | 81.3186 | 50.6663 |  | 16.9889 | 17.178 | 16.6065 | 16.9679 | 17.2361 | 19.0511 | 47.1095 | 15.6674 | 17.0545 | 15.8211 | 17.5835 | 18.1543 | 44.0888 | 46.8516 | 43.4678 | 21.5942 |  |  | 0.47993 | -0.12294 | -28.4671 | 0.49937 | 0.32278 | -197.8033 | 18.4751 | 0.35514 | -0.023259 | 0.13963 | -0.018631 | 0.00034334 | 0.00032363 | 1.8241 | 21.7729 | 21.9916 | 22.1872 | 22.2401 | 22.0595 | 21.3569 | 20.1735 | 22.1876 | 22.3745 | 22.4043 | 22.3531 | 21.9852 | 21.2023 | 22.2774 | 43.0638 | 30.7685 | 33.4983 | 25.4601 | 23.1854 | 30.3082 | 23.3757 | 22.3361 | 22.107 | 21.6743 | 22.0648 | 21.7781 | 21.2886 | 21.9392 | 21.5585 | 21.493 | 32.3075 | 96.509 | 73.9679 | 42.4221 | 0.35546 | -0.042384 | 39.102 | 21.9863 | 22.3025 | 20.1753 | 21.6158 | 22.0622 | 21.9176 | 21.7279 | 23.8241 | 21.7756 | 21.4575 | 21.9068 | 89.7696 | 107.3772 | 69.8197 | 70.6429 | 39.8716 |  | 31.9448 | 62.9568 | 34.3759 | 44.356 | 32.9456 | 38.4375 |  | 43.1696 |  |  | 21.2367 | 22.2876 | 35.8015 | [5 empty] | 21.8988 | 33.6422 | 21.6601 | 22.0385 | 26.7337 | 21.1977 | 21.8287 | 21.9754 | 43.0548 | 114.3578 |  | 34.936 | 83.2366 | 20.2875 | 37.301 | 86.5498 | 28.193 | 70.3392 | 21.5144 | 65.5246 | 21.6784 | 67.8902 | 18.599 | 37.3311 | 78.6704 | 23.1327 | 38.0121 | 102.924 | 20.456 | 35.7427 | 89.0226 | 20.5057 | 62.4844 | 23.9223 | 69.4679 | 21.801 | 68.8931 | 0.3794 | 19.8329 | 0.80435 | 0.021939 | -27.0444 | 3.0954 | 78.97 | 52.79 | 0.93135 | -0.41636 | -6.3355 | 0.83911 | 0.6768 | -16.7542 | 5.1204 | 0.27108 | -0.2868 | 0.18079 | -0.93647 | -0.68637 | 0.0012601 | 0.21265
42838.4229 | 228 | 22.9135 | 22.8784 | 22.866 | 22.7823 | 22.3992 | 21.737 | 22.7251 | 21.7839 | 22.3737 | 22.3764 | 22.3421 | 22.0102 | 21.211 | 22.1802 | 21.6205 | 21.7856 | 21.9132 | 21.1028 | 21.1886 | 21.4129 | 20.4829 | 20.6669 | 21.3975 | 21.875 | 21.65 | 22.8719 | 96.6648 | 87.5059 | 98.9074 | 22.1288 | 21.7156 | 22.2073 | 22.0189 | 21.7597 | 22.6884 | 32.8984 | 90.1252 |  | 50.3581 | 77.7886 | 81.4975 | 51.3006 |  | 16.994 | 17.1845 | 16.6091 | 16.9842 | 17.2447 | 19.101 | 47.4342 | 15.6755 | 17.0559 | 15.8046 | 17.5938 | 18.1585 | 44.0932 | 46.8649 | 43.471 | 21.5983 |  |  | 0.70269 | -0.33256 | -28.8929 | 0.48491 | 0.21961 | -197.8486 | 18.3522 | 0.38734 | -0.14702 | -0.045625 | -0.012382 | 0.00036799 | 0.00031213 | 1.8236 | 21.7733 | 21.9911 | 22.1799 | 22.2416 | 22.0566 | 21.3573 | 20.1655 | 22.1866 | 22.3719 | 22.3993 | 22.3505 | 21.9809 | 21.2087 | 22.2808 | 43.6793 | 29.6306 | 32.7409 | 24.9941 | 22.6088 | 30.377 | 23.4062 | 22.344 | 22.1209 | 21.6764 | 22.0767 | 21.794 | 21.2866 | 21.9438 | 21.5592 | 21.5012 | 32.3878 | 96.5846 | 74.0302 | 42.5075 | 0.51805 | -0.026026 | 39.2574 | 21.9767 | 22.3064 | 20.1754 | 21.6113 | 22.054 | 21.9246 | 21.7157 | 23.8362 | 21.7668 | 21.4522 | 21.9108 | 89.9049 | 107.4049 | 69.9104 | 70.7261 | 39.7435 |  | 32.0246 | 63.5174 | 34.473 | 44.3714 | 33.0302 | 38.45 |  | 43.2776 |  |  | 21.2491 | 22.2938 | 35.8694 | [5 empty] | 21.8948 | 33.6944 | 21.652 | 22.0374 | 26.7414 | 21.1949 | 21.8283 | 21.9831 | 43.133 | 114.2628 |  | 34.9773 | 83.4598 | 20.2993 | 37.3632 | 86.5225 | 28.2546 | 70.4426 | 21.5174 | 65.54 | 21.6831 | 68.0843 | 18.5733 | 37.6683 | 78.8913 | 23.1363 | 38.0748 | 103.0914 | 20.4672 | 35.8164 | 89.0671 | 20.5029 | 62.5787 | 23.9339 | 69.5496 | 21.7986 | 68.9155 | 0.44062 | 19.8318 | 0.80764 | 0.024589 | -27.0949 | 3.0954 | 55.66 | 51.76 | 1.1268 | -0.68479 | -6.3828 | 0.82688 | 0.5583 | -16.7576 | 5.1037 | 0.27737 | -0.29903 | 0.18327 | -0.99678 | -0.59865 | -0.013728 | 0.21303
42838.4229 | 229 | 22.9105 | 22.8772 | 22.8677 | 22.7854 | 22.4039 | 21.7369 | 22.7193 | 21.7853 | 22.3673 | 22.3798 | 22.3467 | 21.9984 | 21.218 | 22.175 | 21.6228 | 21.7837 | 21.9164 | 21.0957 | 21.1925 | 21.4085 | 20.4764 | 20.6726 | 21.4142 | 21.8825 | 21.6606 | 22.8846 | 96.71 | 87.5378 | 98.8991 | 22.1208 | 21.7122 | 22.2146 | 22.0129 | 21.7627 | 22.6976 | 32.9652 | 88.9731 |  | 50.4572 | 77.9497 | 81.6414 | 51.5378 |  | 16.9965 | 17.1997 | 16.6134 | 16.9824 | 17.2361 | 19.1229 | 47.5519 | 15.6779 | 17.0616 | 15.7913 | 17.5908 | 18.1588 | 44.1065 | 46.8765 | 43.4746 | 21.5938 |  |  | 0.59098 | -0.1742 | -29.5342 | 0.59465 | 0.12761 | -197.8276 | 18.0499 | 0.21714 | 0.081825 | 0.062212 | 0.23292 | 0.00034006 | 0.00030556 | 1.8119 | 21.7695 | 21.9865 | 22.1815 | 22.239 | 22.0574 | 21.3526 | 20.167 | 22.1932 | 22.3635 | 22.3967 | 22.3533 | 21.9695 | 21.2082 | 22.2843 | 44.8913 | 29.9763 | 32.7742 | 24.5861 | 22.3517 | 30.4683 | 23.4401 | 22.3457 | 22.1183 | 21.6804 | 22.0699 | 21.7844 | 21.2918 | 21.9481 | 21.5569 | 21.5116 | 32.4615 | 96.6013 | 74.0185 | 42.4884 | 0.38456 | 0.076111 | 39.432 | 21.9803 | 22.3016 | 20.1764 | 21.6144 | 22.0549 | 21.9251 | 21.7243 | 23.8698 | 21.7675 | 21.4465 | 21.9208 | 89.9859 | 107.5466 | 70.0171 | 70.7831 | 39.5634 |  | 32.0958 | 63.7824 | 34.5712 | 44.4417 | 33.1047 | 38.6378 |  | 43.3999 |  |  | 21.2464 | 22.2821 | 35.7298 | [5 empty] | 21.892 | 33.6992 | 21.6545 | 22.0433 | 26.7714 | 21.1901 | 21.8232 | 21.9958 | 43.2495 | 114.2944 |  | 34.9999 | 83.5935 | 20.3087 | 37.4273 | 86.5104 | 28.3037 | 70.5234 | 21.5292 | 65.5705 | 21.7002 | 68.2007 | 18.5399 | 37.8987 | 79.1703 | 23.1531 | 38.0716 | 103.3075 | 20.4783 | 35.9033 | 89.1364 | 20.5083 | 62.6847 | 23.9508 | 69.5816 | 21.8205 | 68.9778 | 0.34508 | 19.8285 | 0.81014 | 0.024669 | -27.061 | 3.0954 | 61.41 | 52.54 | 1.0334 | -0.49562 | -6.4534 | 0.91571 | 0.42561 | -16.7573 | 5.0617 | 0.28481 | -0.30301 | 0.18387 | -1.1207 | -0.59838 | -0.018027 | 0.21609
42838.4229 | 230 | 22.9143 | 22.8805 | 22.8678 | 22.7897 | 22.4047 | 21.737 | 22.726 | 21.7958 | 22.3728 | 22.3813 | 22.3497 | 22.0077 | 21.2184 | 22.18 | 21.6249 | 21.7882 | 21.9167 | 21.0955 | 21.1864 | 21.4135 | 20.4842 | 20.6849 | 21.4184 | 21.875 | 21.6426 | 22.8994 | 96.8827 | 87.6133 | 98.9396 | 22.1251 | 21.7222 | 22.2318 | 22.0183 | 21.7678 | 22.7127 | 33.0493 | 88.0314 |  | 50.5744 | 78.1074 | 81.7732 | 51.4702 |  | 16.9908 | 17.1976 | 16.6116 | 16.9698 | 17.2266 | 19.1379 | 47.7918 | 15.6394 | 17.0545 | 15.7392 | 17.5995 | 18.1567 | 44.1056 | 46.884 | 43.4754 | 21.5906 |  |  | 0.81243 | -0.12886 | -29.5612 | 0.28711 | 0.095412 | -197.892 | 18.2247 | 0.29797 | -0.012945 | 0.14508 | 0.13691 | 0.00035156 | 0.00033349 | 1.8023 | 21.7697 | 21.9897 | 22.1827 | 22.2338 | 22.0583 | 21.3553 | 20.1695 | 22.191 | 22.3643 | 22.3999 | 22.3562 | 21.9692 | 21.2051 | 22.2854 | 44.959 | 31.2759 | 33.3992 | 24.5203 | 22.061 | 30.5423 | 23.4965 | 22.3492 | 22.1125 | 21.6822 | 22.0742 | 21.7865 | 21.2959 | 21.9474 | 21.5614 | 21.5195 | 32.5368 | 96.7249 | 74.0462 | 42.6772 | 0.20841 | 0.23892 | 39.415 | 21.9822 | 22.2944 | 20.1777 | 21.6199 | 22.0564 | 21.9207 | 21.7243 | 23.895 | 21.7652 | 21.4455 | 21.9322 | 90.0766 | 107.7366 | 70.1639 | 70.8418 | 39.37 |  | 32.163 | 63.6595 | 34.6449 | 44.4484 | 33.1792 | 38.791 |  | 43.5119 |  |  | 21.2515 | 22.2685 | 35.5195 | [5 empty] | 21.8861 | 33.7644 | 21.6499 | 22.0335 | 26.7873 | 21.1854 | 21.8163 | 21.9999 | 43.3777 | 114.2126 |  | 34.9787 | 83.7326 | 20.3166 | 37.4987 | 86.6672 | 28.315 | 70.6361 | 21.5399 | 65.6054 | 21.7202 | 68.2932 | 18.5182 | 37.9127 | 79.3798 | 23.1556 | 38.1203 | 103.467 | 20.4772 | 36.0598 | 89.2749 | 20.5179 | 62.7055 | 23.9444 | 69.6155 | 21.8293 | 69.1343 | 0.364 | 19.8261 | 0.8117 | 0.024168 | -27.0586 | 3.0954 | 49.24 | 51.49 | 1.2117 | -0.42627 | -6.4563 | 0.63629 | 0.36802 | -16.7605 | 5.0863 | 0.29248 | -0.29707 | 0.18624 | -1.1196 | -0.66123 | -0.013264 | 0.21342
42838.423 | 231 | 22.91 | 22.875 | 22.8622 | 22.7833 | 22.4096 | 21.7305 | 22.7219 | 21.7892 | 22.3649 | 22.3695 | 22.3439 | 22.0023 | 21.2079 | 22.1742 | 21.6156 | 21.7828 | 21.9083 | 21.0874 | 21.1959 | 21.4047 | 20.4815 | 20.6769 | 21.4146 | 21.8788 | 21.6493 | 22.9187 | 97.0132 | 87.7054 | 98.9148 | 22.1239 | 21.7215 | 22.2454 | 22.0216 | 21.7663 | 22.7332 | 33.1147 | 88.1123 |  | 50.6893 | 78.2249 | 81.8701 | 51.5539 |  | 16.9971 | 17.1975 | 16.6199 | 16.9778 | 17.226 | 19.1374 | 47.717 | 15.6321 | 17.0594 | 15.6527 | 17.603 | 18.1601 | 44.1115 | 46.8998 | 43.4801 | 21.5924 |  |  | 0.77037 | 0.023591 | -29.479 | 0.42971 | 0.1079 | -197.9005 | 17.7766 | 0.23554 | 0.093501 | 0.025497 | 0.12424 | 0.0003532 | 0.00034499 | 1.8176 | 21.7668 | 21.9853 | 22.1785 | 22.2291 | 22.0509 | 21.3446 | 20.1601 | 22.1739 | 22.3558 | 22.391 | 22.3508 | 21.9663 | 21.1963 | 22.2742 | 44.2324 | 31.0265 | 34.7577 | 24.3091 | 22.1325 | 30.5929 | 23.5574 | 22.3431 | 22.1098 | 21.6787 | 22.0731 | 21.7859 | 21.2942 | 21.9433 | 21.5582 | 21.5305 | 32.5948 | 96.9485 | 74.2268 | 43.1704 | 0.4402 | -0.006626 | 39.4101 | 21.9727 | 22.2912 | 20.169 | 21.6088 | 22.057 | 21.9132 | 21.7197 | 23.9126 | 21.767 | 21.4498 | 21.939 | 90.1446 | 107.8313 | 70.2871 | 70.9631 | 39.9832 |  | 32.2498 | 63.3575 | 34.7217 | 44.5049 | 33.2552 | 38.7503 |  | 43.6264 |  |  | 21.2539 | 22.2842 | 35.4456 | [5 empty] | 21.9067 | 33.8163 | 21.6678 | 22.0478 | 26.8171 | 21.2071 | 21.8393 | 22.0103 | 43.488 | 114.2427 |  | 35.0175 | 83.9375 | 20.3177 | 37.5791 | 86.8054 | 28.326 | 70.7326 | 21.548 | 65.6308 | 21.7179 | 68.4006 | 18.5082 | 38.0035 | 79.5417 | 23.1864 | 38.2875 | 103.5336 | 20.4819 | 36.2626 | 89.2947 | 20.5214 | 62.7132 | 23.9727 | 69.7504 | 21.8449 | 69.5478 | 0.34694 | 19.8236 | 0.81472 | 0.023558 | -27.1063 | 3.0953 | 56.24 | 52.15 | 1.1798 | 0.18239 | -6.4474 | 0.77842 | 0.39137 | -16.7608 | 5.0234 | 0.27842 | -0.28604 | 0.18727 | -1.0329 | -0.80504 | -0.013349 | 0.20171
42838.423 | 232 | 22.9168 | 22.8802 | 22.8653 | 22.783 | 22.4069 | 21.7315 | 22.7195 | 21.7884 | 22.3624 | 22.3703 | 22.3476 | 21.999 | 21.2068 | 22.1729 | 21.6216 | 21.7877 | 21.9144 | 21.0957 | 21.1914 | 21.4096 | 20.4918 | 20.682 | 21.4325 | 21.8831 | 21.6493 | 22.9377 | 97.1395 | 87.7637 | 99.5513 | 22.12 | 21.7198 | 22.2483 | 22.0106 | 21.7591 | 22.7346 | 33.1795 | 88.1262 |  | 50.7914 | 78.3057 | 81.9349 | 51.6357 |  | 17.0027 | 17.2015 | 16.6135 | 16.9789 | 17.2261 | 19.1372 | 47.9128 | 15.6549 | 17.0549 | 15.675 | 17.6075 | 18.1566 | 44.0993 | 46.9236 | 43.4777 | 21.5983 |  |  | 0.73751 | -0.060521 | -29.4521 | 0.31077 | 0.084244 | -197.796 | 18.0125 | 0.1258 | 0.092723 | 0.20865 | 0.11626 | 0.00036306 | 0.00033184 | 1.8413 | 21.7694 | 21.992 | 22.1893 | 22.2317 | 22.0534 | 21.3451 | 20.1689 | 22.1849 | 22.3656 | 22.3975 | 22.3495 | 21.963 | 21.198 | 22.2753 | 44.7866 | 30.2279 | 34.1287 | 24.8631 | 22.2124 | 30.6638 | 23.606 | 22.3444 | 22.1098 | 21.6764 | 22.067 | 21.7809 | 21.2895 | 21.9397 | 21.5606 | 21.5356 | 32.6636 | 97.1062 | 74.3411 | 43.3533 | 0.4286 | 0.040353 | 39.3739 | 21.9858 | 22.2989 | 20.1672 | 21.6114 | 22.0641 | 21.9162 | 21.7238 | 23.9452 | 21.7745 | 21.4603 | 21.9555 | 90.2379 | 107.8933 | 70.4093 | 71.117 | 40.5141 |  | 32.3383 | 63.3108 | 34.811 | 44.6807 | 33.3441 | 38.674 |  | 43.7494 |  |  | 21.2595 | 22.2758 | 35.6442 | [5 empty] | 21.8888 | 33.8385 | 21.6554 | 22.0375 | 26.8284 | 21.19 | 21.8273 | 22.0255 | 43.5548 | 114.8498 |  | 35.1433 | 84.118 | 20.3497 | 37.6728 | 86.7388 | 28.3693 | 70.8013 | 21.5645 | 65.6488 | 21.7439 | 68.4986 | 18.5009 | 38.1102 | 79.6504 | 23.2058 | 38.4209 | 103.4608 | 20.4875 | 36.3628 | 89.3307 | 20.528 | 62.8209 | 23.9992 | 69.8226 | 21.8521 | 69.7048 | 0.5445 | 19.8196 | 0.81658 | 0.021845 | -27.1429 | 3.0954 | 59.1 | 52.59 | 1.1554 | -0.29213 | -6.4445 | 0.66199 | 0.34581 | -16.7564 | 5.0566 | 0.26671 | -0.28167 | 0.18544 | -1.0861 | -0.72947 | -0.013399 | 0.19898
42838.423 | 233 | 22.9124 | 22.8794 | 22.8667 | 22.7843 | 22.4037 | 21.7324 | 22.7153 | 21.7844 | 22.3651 | 22.3709 | 22.3429 | 21.9928 | 21.2121 | 22.1697 | 21.6138 | 21.7852 | 21.9127 | 21.0942 | 21.1847 | 21.4067 | 20.4873 | 20.6828 | 21.4376 | 21.8793 | 21.6483 | 22.9555 | 97.2421 | 87.8334 | 99.5089 | 22.1196 | 21.7219 | 22.2694 | 22.0154 | 21.7633 | 22.7533 | 33.2487 | 88.0091 |  | 50.9052 | 78.3626 | 82.0559 | 51.5673 |  | 17.0038 | 17.2022 | 16.6145 | 16.972 | 17.2221 | 19.1555 | 47.8238 | 15.7693 | 17.0585 | 15.8047 | 17.5974 | 18.1608 | 44.1009 | 46.9335 | 43.4689 | 21.5963 |  |  | 0.73226 | -0.46399 | -29.4593 | 0.28251 | 0.30175 | -197.8315 | 17.9494 | 0.27563 | -0.014891 | 0.17425 | 0.036226 | 0.00034663 | 0.00033349 | 1.8287 | 21.7609 | 21.9841 | 22.1759 | 22.2266 | 22.0491 | 21.3524 | 20.1661 | 22.1848 | 22.3631 | 22.401 | 22.3476 | 21.97 | 21.199 | 22.2753 | 44.9962 | 30.8815 | 35.0307 | 25.1112 | 22.6477 | 30.736 | 23.6621 | 22.3338 | 22.104 | 21.671 | 22.064 | 21.779 | 21.2833 | 21.9359 | 21.5568 | 21.5337 | 32.7294 | 97.3035 | 74.5262 | 43.2853 | 0.18894 | 0.014676 | 39.3117 | 21.9759 | 22.293 | 20.1633 | 21.6117 | 22.0527 | 21.9113 | 21.7217 | 23.955 | 21.7618 | 21.4502 | 21.9619 | 90.2945 | 107.9116 | 70.5006 | 71.245 | 40.7174 |  | 32.4119 | 62.8659 | 34.8812 | 44.7293 | 33.415 | 38.8679 |  | 43.8539 |  |  | 21.2736 | 22.2895 | 35.7151 | [5 empty] | 21.9033 | 33.9347 | 21.6696 | 22.0522 | 26.8521 | 21.201 | 21.844 | 22.0389 | 43.5556 | 115.0513 |  | 35.3554 | 84.2449 | 20.3454 | 37.7546 | 86.7408 | 28.4072 | 70.8967 | 21.5806 | 65.6516 | 21.7514 | 68.621 | 18.4967 | 38.3106 | 79.7289 | 23.2108 | 38.4712 | 103.3757 | 20.48 | 36.3987 | 89.3174 | 20.5183 | 62.9357 | 24.0085 | 69.875 | 21.8615 | 69.8122 | 0.30297 | 19.8172 | 0.81622 | 0.02027 | -27.1338 | 3.0954 | 37.4 | 51.87 | 1.1512 | -0.80888 | -6.4453 | 0.63117 | 0.6545 | -16.7584 | 5.0479 | 0.26358 | -0.26689 | 0.18652 | -1.1009 | -0.82312 | -0.0091276 | 0.20312
42838.423 | 234 | 22.9131 | 22.8756 | 22.8691 | 22.7849 | 22.3986 | 21.7343 | 22.7132 | 21.7833 | 22.3696 | 22.3729 | 22.3463 | 21.994 | 21.2126 | 22.173 | 21.6146 | 21.7828 | 21.9107 | 21.0924 | 21.1881 | 21.4009 | 20.4813 | 20.6745 | 21.4392 | 21.8735 | 21.6488 | 22.971 | 97.2326 | 87.8634 | 99.4783 | 22.1273 | 21.7266 | 22.2808 | 22.0246 | 21.7686 | 22.7696 | 33.324 | 88.418 |  | 51.0233 | 78.3759 | 82.1077 | 51.413 |  | 17.0016 | 17.1998 | 16.6118 | 16.9729 | 17.2261 | 19.2251 | 47.6142 | 15.8406 | 17.0567 | 15.8224 | 17.6026 | 18.1626 | 44.1046 | 46.9501 | 43.4644 | 21.6001 |  |  | 0.62121 | -0.37988 | -28.8127 | 0.50396 | 0.2978 | -197.8059 | 17.9691 | 0.15209 | 0.17932 | 0.17005 | -0.10213 | 0.00034499 | 0.00033842 | 1.8189 | 21.7639 | 21.9861 | 22.1856 | 22.2429 | 22.0502 | 21.3493 | 20.165 | 22.1938 | 22.3628 | 22.404 | 22.3495 | 21.9745 | 21.2028 | 22.2733 | 43.6834 | 30.5805 | 34.4307 | 25.47 | 23.1343 | 30.7882 | 23.7168 | 22.3462 | 22.1179 | 21.6772 | 22.0739 | 21.7876 | 21.3045 | 21.9521 | 21.5638 | 21.5565 | 32.8066 | 97.2447 | 74.636 | 43.2519 | 0.44158 | -0.0079574 | 39.3517 | 21.9718 | 22.2906 | 20.1677 | 21.6058 | 22.0471 | 21.9116 | 21.719 | 23.9804 | 21.7625 | 21.4522 | 21.9714 | 90.3307 | 108.0409 | 70.6217 | 71.3878 | 41.3362 |  | 32.4931 | 62.3042 | 34.9655 | 44.6571 | 33.5 | 38.9458 |  | 43.9569 |  |  | 21.2676 | 22.2882 | 35.6679 | [5 empty] | 21.8992 | 33.9357 | 21.6647 | 22.0429 | 26.8567 | 21.1994 | 21.8386 | 22.0426 | 43.6052 | 115.3407 |  | 35.5072 | 84.3271 | 20.3579 | 37.8748 | 86.821 | 28.4341 | 71.0099 | 21.5986 | 65.6558 | 21.7612 | 68.7162 | 18.4979 | 38.4699 | 79.8383 | 23.2222 | 38.5352 | 103.4144 | 20.4903 | 36.3943 | 89.4941 | 20.5184 | 63.0866 | 24.0324 | 70.0239 | 21.883 | 69.9552 | 0.53912 | 19.8136 | 0.8195 | 0.022193 | -27.1439 | 3.0954 | 67.75 | 52.79 | 1.0603 | -0.7319 | -6.3741 | 0.843 | 0.65028 | -16.7593 | 5.0513 | 0.24917 | -0.24839 | 0.19145 | -0.94892 | -0.75005 | -0.0022576 | 0.2067
42838.423 | 235 | 22.9154 | 22.8689 | 22.8548 | 22.7729 | 22.3948 | 21.7306 | 22.7139 | 21.7804 | 22.3636 | 22.3678 | 22.3455 | 21.99 | 21.2069 | 22.1721 | 21.6154 | 21.7874 | 21.9075 | 21.0882 | 21.186 | 21.4044 | 20.4781 | 20.6812 | 21.4451 | 21.8682 | 21.6495 | 22.9806 | 97.2616 | 87.8832 | 99.6436 | 22.1246 | 21.7271 | 22.287 | 22.0132 | 21.7665 | 22.7783 | 33.3887 | 88.5105 |  | 51.1452 | 78.4149 | 82.1515 | 51.1729 |  | 17.0029 | 17.2032 | 16.6228 | 16.9781 | 17.257 | 19.3375 | 47.6738 | 15.8889 | 17.0609 | 15.8262 | 17.6149 | 18.1665 | 44.1043 | 46.9579 | 43.4705 | 21.5915 |  |  | 0.78745 | -0.31548 | -28.9527 | 0.67416 | 0.33132 | -197.865 | 18.0184 | 0.34725 | -0.052059 | 0.20949 | 0.0082768 | 0.00032363 | 0.00031213 | 1.8213 | 21.7607 | 21.9784 | 22.1748 | 22.233 | 22.0501 | 21.3493 | 20.1631 | 22.1807 | 22.3603 | 22.3981 | 22.3528 | 21.9652 | 21.1941 | 22.2804 | 43.4529 | 30.1789 | 33.4845 | 25.3275 | 23.0393 | 30.8419 | 23.7627 | 22.3418 | 22.1176 | 21.6747 | 22.0734 | 21.787 | 21.295 | 21.945 | 21.5662 | 21.5642 | 32.8696 | 97.23 | 74.775 | 43.116 | 0.39813 | -0.085559 | 39.3953 | 21.9725 | 22.2921 | 20.1764 | 21.6098 | 22.0478 | 21.9186 | 21.7291 | 24.0112 | 21.7706 | 21.4471 | 21.9892 | 90.3178 | 108.115 | 70.7682 | 71.5305 | 42.2679 |  | 32.5933 | 62.1628 | 35.0412 | 44.7673 | 33.5747 | 39.0344 |  | 44.0793 |  |  | 21.2662 | 22.2949 | 35.6137 | [5 empty] | 21.894 | 33.9633 | 21.6638 | 22.043 | 26.8698 | 21.197 | 21.831 | 22.0475 | 43.7193 | 115.3041 |  | 35.5547 | 84.3513 | 20.3609 | 37.978 | 86.904 | 28.4581 | 71.1444 | 21.6176 | 65.7584 | 21.7727 | 68.8303 | 18.4976 | 38.5108 | 79.991 | 23.237 | 38.5865 | 103.5717 | 20.4915 | 36.3626 | 89.5857 | 20.5181 | 63.2165 | 24.0462 | 70.1106 | 21.8973 | 70.0759 | 0.28813 | 19.808 | 0.82302 | 0.025416 | -27.1157 | 3.0953 | 64.84 | 51.71 | 1.194 | -0.66699 | -6.3896 | 0.97501 | 0.68603 | -16.7651 | 5.0592 | 0.22672 | -0.24186 | 0.19095 | -0.91701 | -0.63954 | 0.0066323 | 0.21263
42838.423 | 236 | 22.9144 | 22.8737 | 22.8547 | 22.7827 | 22.4022 | 21.7304 | 22.7235 | 21.7786 | 22.3749 | 22.3725 | 22.3415 | 21.9899 | 21.2134 | 22.1755 | 21.6198 | 21.7947 | 21.9058 | 21.0906 | 21.1925 | 21.4103 | 20.4792 | 20.6904 | 21.4557 | 21.871 | 21.6491 | 23.0017 | 97.3181 | 87.9664 | 99.607 | 22.1213 | 21.7207 | 22.2976 | 22.0108 | 21.766 | 22.7923 | 33.4512 | 89.5236 |  | 51.2636 | 78.4849 | 82.1856 | 51.3222 |  | 16.9995 | 17.2036 | 16.6207 | 16.9856 | 17.3029 | 19.3976 | 48.0336 | 15.9285 | 17.0594 | 15.8179 | 17.6133 | 18.176 | 44.1079 | 46.9759 | 43.4822 | 21.5948 |  |  | 0.76249 | -0.37857 | -29.0158 | 0.43957 | 0.26232 | -197.8374 | 18.0782 | 0.24474 | 0.039597 | 0.031791 | 0.015742 | 0.00033513 | 0.00032856 | 1.8214 | 21.7644 | 21.9824 | 22.1848 | 22.2346 | 22.0536 | 21.3471 | 20.1658 | 22.1873 | 22.3616 | 22.4039 | 22.3541 | 21.9687 | 21.1989 | 22.2711 | 44.0941 | 29.2158 | 32.7612 | 25.1798 | 22.7729 | 30.9161 | 23.7995 | 22.3427 | 22.1147 | 21.681 | 22.0789 | 21.7801 | 21.2936 | 21.9445 | 21.5645 | 21.5713 | 32.9317 | 97.466 | 75.169 | 42.9912 | 0.45848 | 0.033506 | 39.4453 | 21.9786 | 22.29 | 20.1801 | 21.6103 | 22.0602 | 21.9218 | 21.7269 | 24.0424 | 21.7697 | 21.4572 | 21.9913 | 90.322 | 108.124 | 70.926 | 71.6602 | 43.3482 |  | 32.6668 | 62.3255 | 35.0998 | 45.0174 | 33.6439 | 39.257 |  | 44.1658 |  |  | 21.254 | 22.3 | 35.6666 | [5 empty] | 21.8938 | 34.0074 | 21.6672 | 22.0468 | 26.8862 | 21.199 | 21.8277 | 22.0567 | 43.8627 | 115.1241 |  | 35.5829 | 84.3497 | 20.372 | 38.0318 | 87.0177 | 28.5048 | 71.2985 | 21.6408 | 65.8976 | 21.7845 | 68.9355 | 18.4927 | 38.5494 | 80.1132 | 23.2455 | 38.6095 | 103.6854 | 20.4873 | 36.3894 | 89.6616 | 20.5109 | 63.3303 | 24.0644 | 70.0972 | 21.8982 | 70.1203 | 0.46009 | 19.8058 | 0.82351 | 0.025075 | -27.1405 | 3.0953 | 62.34 | 52.12 | 1.1749 | -0.73064 | -6.3966 | 0.7873 | 0.61049 | -16.7656 | 5.0681 | 0.19923 | -0.24436 | 0.18638 | -0.97954 | -0.55487 | 0.0046324 | 0.21823
42838.423 | 237 | 22.9079 | 22.8651 | 22.8614 | 22.7631 | 22.3927 | 21.7323 | 22.721 | 21.7735 | 22.3583 | 22.3575 | 22.3376 | 21.9913 | 21.1978 | 22.173 | 21.6226 | 21.7865 | 21.9008 | 21.0866 | 21.1905 | 21.412 | 20.4727 | 20.6792 | 21.4618 | 21.8689 | 21.6436 | 23.0136 | 97.3827 | 88.0381 | 99.7237 | 22.1229 | 21.7228 | 22.3138 | 22.0168 | 21.7602 | 22.8132 | 33.5316 | 90.5524 |  | 51.3824 | 78.5964 | 82.2504 | 51.8554 |  | 17.0047 | 17.2104 | 16.618 | 16.9828 | 17.3285 | 19.4178 | 48.3501 | 15.9266 | 17.0616 | 15.7972 | 17.6097 | 18.1707 | 44.1057 | 46.9997 | 43.4865 | 21.6024 |  |  | 0.92019 | -0.34308 | -28.9934 | 0.44548 | 0.16967 | -197.8322 | 18.2674 | 0.16326 | 0.17621 | 0.10921 | 0.044212 | 0.0003302 | 0.0003072 | 1.8252 | 21.7586 | 21.9779 | 22.1781 | 22.2256 | 22.0498 | 21.344 | 20.1608 | 22.182 | 22.3592 | 22.3923 | 22.3454 | 21.9618 | 21.1895 | 22.2711 | 45.0063 | 28.3612 | 31.8851 | 24.7877 | 22.685 | 31.0033 | 23.8173 | 22.3479 | 22.1103 | 21.6766 | 22.0752 | 21.783 | 21.2922 | 21.9392 | 21.5592 | 21.5765 | 33.0096 | 97.6146 | 75.5314 | 42.9026 | 0.59964 | -0.15213 | 39.5717 | 21.9867 | 22.2965 | 20.1756 | 21.6045 | 22.0504 | 21.9177 | 21.7232 | 24.0688 | 21.7712 | 21.4526 | 22.0088 | 90.3428 | 108.0658 | 71.0389 | 71.7785 | 43.7567 |  | 32.7391 | 62.6936 | 35.1571 | 45.0799 | 33.717 | 39.6661 |  | 44.26 |  |  | 21.2442 | 22.3019 | 35.8219 | [5 empty] | 21.8934 | 34.0152 | 21.6566 | 22.0411 | 26.9129 | 21.1942 | 21.8275 | 22.0656 | 43.9666 | 115.0455 |  | 35.628 | 84.3735 | 20.3775 | 38.0613 | 87.2262 | 28.5402 | 71.4175 | 21.6566 | 66.0062 | 21.7915 | 68.9815 | 18.4979 | 38.639 | 80.2072 | 23.2636 | 38.6676 | 103.8074 | 20.4858 | 36.4737 | 89.7668 | 20.5256 | 63.4655 | 24.0763 | 70.1027 | 21.9123 | 70.1889 | 0.38849 | 19.8023 | 0.82502 | 0.024175 | -27.0823 | 3.0954 | 67.31 | 51.83 | 1.2909 | -0.69556 | -6.3942 | 0.79259 | 0.491 | -16.766 | 5.0947 | 0.19036 | -0.25261 | 0.18715 | -1.0707 | -0.45544 | -0.0074234 | 0.22336
42838.423 | 238 | 22.9116 | 22.8715 | 22.8658 | 22.7862 | 22.3978 | 21.7303 | 22.7232 | 21.7809 | 22.3719 | 22.3773 | 22.3497 | 22.0026 | 21.2082 | 22.178 | 21.621 | 21.7828 | 21.9058 | 21.0931 | 21.1898 | 21.4116 | 20.4784 | 20.6805 | 21.4719 | 21.8744 | 21.6459 | 23.0361 | 97.5968 | 88.0606 | 100.3447 | 22.1219 | 21.7192 | 22.3245 | 22.0215 | 21.7615 | 22.826 | 33.6096 | 91.2437 |  | 51.505 | 78.7301 | 82.3292 | 52.2598 |  | 17.0124 | 17.2165 | 16.6289 | 16.9969 | 17.3583 | 19.4287 | 48.5083 | 16.0303 | 17.0671 | 15.7887 | 17.6234 | 18.1626 | 44.0816 | 47.0213 | 43.4792 | 21.5974 |  |  | 0.75591 | -0.38185 | -28.8659 | 0.69781 | 0.13156 | -197.8466 | 18.1524 | 0.10938 | 0.090193 | 0.13543 | -0.07644 | 0.00034334 | 0.00033842 | 1.827 | 21.7668 | 21.9833 | 22.1787 | 22.234 | 22.0492 | 21.3525 | 20.1614 | 22.1834 | 22.3636 | 22.3947 | 22.342 | 21.9684 | 21.1967 | 22.2739 | 46.9438 | 29.4202 | 32.0615 | 24.9715 | 22.3935 | 31.1292 | 23.8546 | 22.3472 | 22.1174 | 21.6789 | 22.0799 | 21.79 | 21.2954 | 21.9458 | 21.5643 | 21.5971 | 33.0813 | 97.6064 | 75.7259 | 42.856 | 0.53103 | 0.054809 | 39.6865 | 21.9707 | 22.2904 | 20.1723 | 21.6069 | 22.0455 | 21.9094 | 21.7202 | 24.0894 | 21.7652 | 21.4495 | 22.0214 | 90.3571 | 108.1975 | 71.122 | 71.8765 | 43.4855 |  | 32.8183 | 62.8426 | 35.235 | 45.0175 | 33.8152 | 39.6165 |  | 44.37 |  |  | 21.2435 | 22.3017 | 35.9086 | [5 empty] | 21.8977 | 34.0061 | 21.6589 | 22.0345 | 26.9521 | 21.1882 | 21.8312 | 22.0843 | 44.0029 | 115.1684 |  | 35.6892 | 84.3886 | 20.3805 | 38.0701 | 87.4417 | 28.5685 | 71.4828 | 21.6543 | 66.1393 | 21.7989 | 69.0647 | 18.4997 | 38.6891 | 80.3383 | 23.2695 | 38.7776 | 103.8906 | 20.4772 | 36.5565 | 89.7974 | 20.5374 | 63.5383 | 24.1064 | 70.1765 | 21.9249 | 70.2526 | 0.48217 | 19.8002 | 0.82658 | 0.02313 | -27.056 | 3.0953 | 65.77 | 51.45 | 1.171 | -0.73381 | -6.3802 | 0.992 | 0.43236 | -16.7669 | 5.0787 | 0.20061 | -0.25407 | 0.19225 | -1.2711 | -0.47067 | -0.015976 | 0.22712
42838.423 | 239 | 22.9231 | 22.8775 | 22.8687 | 22.7901 | 22.4031 | 21.7355 | 22.7272 | 21.7834 | 22.3753 | 22.3782 | 22.352 | 22.0052 | 21.2092 | 22.1822 | 21.6191 | 21.7908 | 21.9148 | 21.1017 | 21.193 | 21.4133 | 20.4871 | 20.6904 | 21.4843 | 21.8736 | 21.6532 | 23.0646 | 97.8281 | 88.0948 | 100.7445 | 22.1274 | 21.7205 | 22.3355 | 22.0204 | 21.7593 | 22.8381 | 33.6854 | 91.3631 |  | 51.6191 | 78.8455 | 82.3849 | 52.3191 |  | 17.0188 | 17.218 | 16.6275 | 17.0127 | 17.3803 | 19.418 | 48.5254 | 16.1136 | 17.0655 | 15.7726 | 17.6177 | 18.1745 | 44.0809 | 47.0438 | 43.4774 | 21.6038 |  |  | 0.68757 | -0.26751 | -28.8272 | 0.20761 | 0.26035 | -197.846 | 17.7095 | 0.14749 | 0.14799 | 0.14928 | 0.016262 | 0.00036799 | 0.00036799 | 1.8349 | 21.7645 | 21.9783 | 22.1783 | 22.2345 | 22.0495 | 21.3436 | 20.1603 | 22.1817 | 22.3603 | 22.3951 | 22.3407 | 21.9705 | 21.2019 | 22.2711 | 48.5895 | 30.6765 | 33.1707 | 26.3037 | 23.3698 | 31.2421 | 23.9067 | 22.3444 | 22.1123 | 21.6708 | 22.0741 | 21.7891 | 21.3042 | 21.9448 | 21.5655 | 21.5926 | 33.1568 | 97.6697 | 75.7862 | 42.9771 | 0.47716 | 0.024567 | 39.7548 | 21.9667 | 22.2833 | 20.1724 | 21.6031 | 22.0497 | 21.9145 | 21.7262 | 24.1103 | 21.7692 | 21.4571 | 22.0262 | 90.3518 | 108.1527 | 71.1662 | 71.9451 | 43.6439 |  | 32.889 | 62.9086 | 35.3042 | 45.0041 | 33.8876 | 39.2938 |  | 44.4545 |  |  | 21.2405 | 22.3073 | 36.0665 | [5 empty] | 21.8972 | 34.0252 | 21.6631 | 22.0384 | 27.0032 | 21.1955 | 21.8341 | 22.0975 | 44.0368 | 115.2006 |  | 35.7616 | 84.4067 | 20.3889 | 38.1092 | 87.546 | 28.6117 | 71.5611 | 21.6582 | 66.2939 | 21.81 | 69.1602 | 18.503 | 38.7244 | 80.4637 | 23.2794 | 38.8908 | 104.0481 | 20.4686 | 36.6173 | 89.8722 | 20.5422 | 63.5858 | 24.1251 | 70.3365 | 21.9343 | 70.4555 | 0.23619 | 19.7991 | 0.8272 | 0.022302 | -27.0293 | 3.0954 | 39.1 | 52.36 | 1.1174 | -0.61421 | -6.3759 | 0.54108 | 0.60822 | -16.7666 | 5.0163 | 0.19863 | -0.25352 | 0.19511 | -1.4407 | -0.58783 | -0.015022 | 0.22634
42838.4231 | 240 | 22.9116 | 22.8733 | 22.8621 | 22.7836 | 22.3962 | 21.7321 | 22.7109 | 21.7807 | 22.3662 | 22.3739 | 22.337 | 21.9909 | 21.1953 | 22.1741 | 21.6159 | 21.7928 | 21.9097 | 21.0958 | 21.1918 | 21.4089 | 20.4831 | 20.6867 | 21.4911 | 21.8718 | 21.6542 | 23.0771 | 97.9212 | 88.1688 | 100.7193 | 22.1183 | 21.7179 | 22.336 | 22.011 | 21.7542 | 22.85 | 33.7567 | 91.0013 |  | 51.7297 | 78.9369 | 82.4339 | 52.3136 |  | 17.0257 | 17.2223 | 16.6383 | 17.0299 | 17.3817 | 19.4689 | 48.5506 | 16.1771 | 17.0712 | 15.7845 | 17.631 | 18.1696 | 44.0764 | 47.0629 | 43.482 | 21.6017 |  |  | 0.73029 | -0.18866 | -28.634 | 0.65773 | 0.22421 | -197.7993 | 18.2438 | 0.29074 | 0.14157 | 0.070394 | 0.18952 | 0.00036306 | 0.00032856 | 1.836 | 21.7565 | 21.9768 | 22.1756 | 22.2299 | 22.0539 | 21.3435 | 20.1605 | 22.1818 | 22.3556 | 22.3915 | 22.3399 | 21.9715 | 21.1972 | 22.2656 | 48.1561 | 30.4683 | 31.9872 | 27.0358 | 23.9953 | 31.3375 | 23.9308 | 22.3489 | 22.1155 | 21.6743 | 22.0684 | 21.7862 | 21.292 | 21.9456 | 21.5712 | 21.6013 | 33.2283 | 97.6956 | 75.7648 | 43.0354 | 0.52061 | -0.049992 | 39.8809 | 21.9636 | 22.2908 | 20.1771 | 21.612 | 22.0516 | 21.9184 | 21.7222 | 24.1344 | 21.7646 | 21.4506 | 22.0371 | 90.4176 | 108.1769 | 71.214 | 71.9894 | 43.8325 |  | 32.9641 | 63.0263 | 35.3626 | 45.0323 | 33.9531 | 39.2352 |  | 44.532 |  |  | 21.235 | 22.3115 | 36.1158 | [5 empty] | 21.9023 | 34.0756 | 21.6616 | 22.0454 | 27.041 | 21.2023 | 21.8358 | 22.0977 | 44.0826 | 115.0689 |  | 35.8062 | 84.5505 | 20.3967 | 38.2226 | 87.5662 | 28.6485 | 71.6851 | 21.6693 | 66.3555 | 21.818 | 69.2397 | 18.5064 | 38.7968 | 80.5696 | 23.2938 | 38.9732 | 104.2078 | 20.4686 | 36.6707 | 89.9261 | 20.5477 | 63.6064 | 24.1325 | 70.4108 | 21.9461 | 70.681 | 0.42893 | 19.7978 | 0.8283 | 0.022542 | -27.1129 | 3.0953 | 39.79 | 51.62 | 1.1515 | -0.5158 | -6.3546 | 0.96309 | 0.56447 | -16.766 | 5.0918 | 0.19597 | -0.25478 | 0.19658 | -1.3814 | -0.4535 | -0.012421 | 0.22717
42838.4231 | 241 | 22.9176 | 22.874 | 22.858 | 22.777 | 22.4002 | 21.7328 | 22.7055 | 21.7818 | 22.3681 | 22.3717 | 22.3371 | 21.9883 | 21.2005 | 22.1713 | 21.614 | 21.7889 | 21.9086 | 21.0887 | 21.1874 | 21.4034 | 20.4809 | 20.6824 | 21.4984 | 21.8679 | 21.6482 | 23.0876 | 98.0011 | 88.2556 | 100.7353 | 22.1217 | 21.7154 | 22.3528 | 22.011 | 21.7627 | 22.8594 | 33.8394 | 91.0586 |  | 51.8469 | 79.0182 | 82.5053 | 52.2023 |  | 17.0168 | 17.2227 | 16.6426 | 17.0451 | 17.3746 | 19.4344 | 48.7644 | 16.225 | 17.0713 | 15.8307 | 17.6353 | 18.168 | 44.0961 | 47.09 | 43.4871 | 21.6021 |  |  | 0.67772 | -0.19391 | -28.5847 | 0.3732 | 0.20975 | -197.9077 | 17.6603 | 0.27891 | 0.039013 | 0.17068 | 0.18778 | 0.00036963 | 0.00032035 | 1.8332 | 21.7671 | 21.9867 | 22.1889 | 22.2413 | 22.0559 | 21.3536 | 20.1711 | 22.1872 | 22.368 | 22.399 | 22.352 | 21.9757 | 21.2051 | 22.286 | 47.9985 | 30.8236 | 30.4524 | 26.6995 | 23.7369 | 31.4398 | 23.9515 | 22.345 | 22.12 | 21.6755 | 22.0739 | 21.7857 | 21.2951 | 21.9494 | 21.5637 | 21.613 | 33.2956 | 97.8075 | 75.7565 | 43.1451 | 0.46949 | 0.053477 | 40.0385 | 21.9783 | 22.2936 | 20.1886 | 21.6152 | 22.0573 | 21.9194 | 21.7332 | 24.1681 | 21.7735 | 21.4611 | 22.0581 | 90.5488 | 108.2335 | 71.2521 | 72.0241 | 43.9664 |  | 33.0495 | 63.7865 | 35.4328 | 45.1396 | 34.0264 | 39.205 |  | 44.6034 |  |  | 21.2354 | 22.3121 | 36.2231 | [5 empty] | 21.8936 | 34.0947 | 21.6576 | 22.0397 | 27.0384 | 21.199 | 21.8311 | 22.1057 | 44.137 | 114.9429 |  | 35.7705 | 84.7449 | 20.4032 | 38.3313 | 87.6826 | 28.6699 | 71.7653 | 21.6863 | 66.3893 | 21.8204 | 69.3175 | 18.5136 | 38.8592 | 80.6218 | 23.3017 | 39.0175 | 104.2084 | 20.47 | 36.7293 | 90.0169 | 20.5554 | 63.6087 | 24.1515 | 70.4622 | 21.9626 | 70.8147 | 0.22822 | 19.7945 | 0.83098 | 0.022113 | -26.9566 | 3.0954 | 68.51 | 54.14 | 1.1093 | -0.52294 | -6.3491 | 0.72546 | 0.54594 | -16.7696 | 5.0095 | 0.19518 | -0.27348 | 0.19612 | -1.3518 | -0.28054 | -0.0064898 | 0.22643
42838.4231 | 242 | 22.921 | 22.8831 | 22.8688 | 22.7854 | 22.4108 | 21.7425 | 22.7188 | 21.7935 | 22.3792 | 22.3782 | 22.35 | 22.0099 | 21.2113 | 22.1822 | 21.6236 | 21.7866 | 21.9097 | 21.0849 | 21.1925 | 21.4103 | 20.4828 | 20.6834 | 21.4929 | 21.8738 | 21.6495 | 23.1 | 98.0456 | 88.329 | 100.2285 | 22.1276 | 21.7227 | 22.3688 | 22.0147 | 21.7691 | 22.8868 | 33.913 | 91.1834 |  | 51.9621 | 79.1309 | 82.5988 | 52.0268 |  | 17.0203 | 17.2285 | 16.644 | 17.0473 | 17.3667 | 19.3559 | 48.5248 | 16.2719 | 17.0653 | 15.9056 | 17.6342 | 18.171 | 44.1245 | 47.1177 | 43.5038 | 21.6085 |  |  | 0.92413 | -0.10192 | -28.657 | 0.45994 | 0.071756 | -197.8637 | 18.2208 | 0.37945 | 0.064506 | 0.089066 | 0.074592 | 0.00034663 | 0.00033349 | 1.8174 | 21.7716 | 21.9965 | 22.1843 | 22.2375 | 22.0578 | 21.3583 | 20.1644 | 22.1977 | 22.3699 | 22.4052 | 22.3503 | 21.9812 | 21.2065 | 22.2823 | 48.0674 | 31.2721 | 30.8214 | 26.1408 | 23.7873 | 31.5349 | 23.9845 | 22.3424 | 22.1158 | 21.675 | 22.0633 | 21.7875 | 21.2953 | 21.9425 | 21.5618 | 21.6228 | 33.3612 | 97.8583 | 75.7377 | 43.2058 | 0.53024 | 0.23588 | 40.2193 | 21.9764 | 22.304 | 20.1785 | 21.6105 | 22.0474 | 21.9173 | 21.7317 | 24.1905 | 21.775 | 21.4635 | 22.0601 | 90.6029 | 108.6487 | 71.257 | 72.0347 | 43.5968 |  | 33.1443 | 64.422 | 35.5266 | 45.0849 | 34.1205 | 39.1999 |  | 44.6899 |  |  | 21.2521 | 22.3343 | 36.2875 | [5 empty] | 21.8867 | 34.1615 | 21.6624 | 22.0435 | 27.0464 | 21.2019 | 21.8349 | 22.1173 | 44.2189 | 114.5999 |  | 35.7628 | 84.9392 | 20.4164 | 38.4357 | 87.8978 | 28.6884 | 71.8333 | 21.7129 | 66.4364 | 21.8309 | 69.4157 | 18.5008 | 38.8782 | 80.6479 | 23.3073 | 39.0523 | 104.1187 | 20.4583 | 36.7995 | 90.0435 | 20.5545 | 63.6528 | 24.1766 | 70.7698 | 21.9607 | 70.9371 | 0.38422 | 19.7932 | 0.83313 | 0.025961 | -27.0657 | 3.0954 | 67.48 | 55.56 | 1.2945 | -0.37912 | -6.3572 | 0.80538 | 0.31927 | -16.7655 | 5.0877 | 0.20869 | -0.2879 | 0.20087 | -1.3483 | -0.31768 | 0.00091254 | 0.227
42838.4231 | 243 | 22.9162 | 22.8814 | 22.8644 | 22.7859 | 22.4049 | 21.7393 | 22.7191 | 21.7829 | 22.3702 | 22.3827 | 22.3429 | 21.9998 | 21.2107 | 22.1858 | 21.6183 | 21.7924 | 21.9066 | 21.0932 | 21.1873 | 21.409 | 20.4822 | 20.6842 | 21.5049 | 21.8683 | 21.657 | 23.1152 | 98.1442 | 88.3941 | 100.6663 | 22.1228 | 21.7302 | 22.3877 | 22.015 | 21.7736 | 22.9132 | 33.9874 | 91.3329 |  | 52.0682 | 79.2563 | 82.7271 | 52.1913 |  | 17.0161 | 17.2323 | 16.6442 | 17.0452 | 17.3497 | 19.2829 | 48.6395 | 16.2829 | 17.0668 | 16.0301 | 17.634 | 18.1719 | 44.1576 | 47.1506 | 43.5151 | 21.6108 |  |  | 0.79008 | -0.28788 | -28.5492 | 0.54076 | 0.28466 | -197.8453 | 17.835 | 0.3466 | 0.078712 | 0.12096 | 0.085355 | 0.00034499 | 0.00035156 | 1.7995 | 21.7695 | 21.9836 | 22.1744 | 22.2369 | 22.0442 | 21.3516 | 20.1558 | 22.1904 | 22.3672 | 22.3963 | 22.3458 | 21.9718 | 21.1984 | 22.2742 | 48.1375 | 30.9796 | 30.9015 | 26.4243 | 23.4925 | 31.6254 | 24.0169 | 22.3343 | 22.1125 | 21.6729 | 22.0666 | 21.7825 | 21.292 | 21.9358 | 21.5678 | 21.6277 | 33.4297 | 97.7729 | 75.7097 | 43.1923 | 0.48168 | 0.12176 | 40.269 | 21.9751 | 22.2849 | 20.1776 | 21.6055 | 22.0484 | 21.9133 | 21.7296 | 24.2134 | 21.7654 | 21.4631 | 22.0756 | 90.7143 | 108.7706 | 71.2312 | 72.059 | 43.5686 |  | 33.2211 | 64.2089 | 35.5993 | 45.301 | 34.1939 | 39.1858 |  | 44.7677 |  |  | 21.2458 | 22.3475 | 36.3069 | [5 empty] | 21.8939 | 34.1924 | 21.6585 | 22.051 | 27.0681 | 21.2008 | 21.8367 | 22.1323 | 44.3104 | 114.5886 |  | 35.8559 | 85.0871 | 20.4263 | 38.5526 | 88.0866 | 28.7201 | 71.855 | 21.7207 | 66.4751 | 21.8499 | 69.5536 | 18.5125 | 38.9176 | 80.715 | 23.3294 | 39.1337 | 104.1834 | 20.4718 | 36.9248 | 90.0996 | 20.5699 | 63.781 | 24.2186 | 71.0827 | 21.9815 | 71.0981 | 0.31948 | 19.7911 | 0.8335 | 0.025358 | -27.1981 | 3.0954 | 66.63 | 55.3 | 1.1977 | -0.63717 | -6.3453 | 0.87328 | 0.63584 | -16.7627 | 5.0329 | 0.21211 | -0.27947 | 0.19739 | -1.3455 | -0.32279 | -0.0011031 | 0.22972
42838.4231 | 244 | 22.915 | 22.8737 | 22.8654 | 22.7793 | 22.395 | 21.7316 | 22.7172 | 21.7861 | 22.3681 | 22.3696 | 22.3406 | 21.9971 | 21.2084 | 22.1739 | 21.6238 | 21.7939 | 21.9153 | 21.098 | 21.2072 | 21.4111 | 20.4873 | 20.6951 | 21.5168 | 21.8719 | 21.6565 | 23.1393 | 98.2248 | 88.4034 | 100.6627 | 22.1243 | 21.7323 | 22.3866 | 22.0162 | 21.7716 | 22.9207 | 34.0567 | 91.8768 |  | 52.1968 | 79.3722 | 82.8515 | 51.9487 |  | 17.0085 | 17.2352 | 16.6475 | 17.0335 | 17.3263 | 19.2384 | 48.8446 | 16.2235 | 17.0727 | 16.1358 | 17.6384 | 18.1812 | 44.2051 | 47.1841 | 43.5147 | 21.6089 |  |  | 0.58638 | -0.50867 | -28.3882 | 0.66036 | 0.23604 | -197.8683 | 18.0296 | 0.27431 | 0.10615 | 0.1327 | 0.07112 | 0.00032363 | 0.00031706 | 1.7892 | 21.7636 | 21.9785 | 22.1778 | 22.234 | 22.0451 | 21.3453 | 20.157 | 22.1879 | 22.3655 | 22.3922 | 22.3524 | 21.9635 | 21.1995 | 22.274 | 47.0863 | 30.9589 | 30.6873 | 26.1903 | 23.1737 | 31.7042 | 24.0484 | 22.3399 | 22.11 | 21.6777 | 22.0702 | 21.7766 | 21.2874 | 21.9401 | 21.5678 | 21.6413 | 33.5009 | 97.8063 | 75.7039 | 43.3666 | 0.42998 | -0.014234 | 40.3778 | 21.9759 | 22.2943 | 20.1833 | 21.6074 | 22.0566 | 21.9175 | 21.7288 | 24.2378 | 21.7703 | 21.4565 | 22.0862 | 90.7973 | 108.7242 | 71.2309 | 72.0891 | 43.5999 |  | 33.3016 | 63.882 | 35.6842 | 45.518 | 34.2768 | 39.1377 |  | 44.8547 |  |  | 21.2538 | 22.3517 | 36.5096 | [5 empty] | 21.8961 | 34.3748 | 21.6604 | 22.0439 | 27.0826 | 21.2005 | 21.838 | 22.1445 | 44.4008 | 114.5956 |  | 35.9589 | 85.0681 | 20.4262 | 38.6522 | 88.2804 | 28.7432 | 71.9612 | 21.7336 | 66.5189 | 21.8565 | 69.6606 | 18.5206 | 38.9548 | 80.731 | 23.3451 | 39.2274 | 104.271 | 20.4773 | 37.0268 | 90.2333 | 20.5717 | 63.896 | 24.2433 | 71.2732 | 22.0116 | 71.3036 | 0.59829 | 19.7884 | 0.83556 | 0.024342 | -27.128 | 3.0954 | 73.32 | 56.24 | 1.0318 | -0.84698 | -6.3274 | 0.96504 | 0.57894 | -16.7624 | 5.0599 | 0.21401 | -0.26747 | 0.19421 | -1.2194 | -0.29531 | 0.0080182 | 0.22732
42838.4231 | 245 | 22.9159 | 22.883 | 22.8646 | 22.7818 | 22.3985 | 21.7325 | 22.7223 | 21.7887 | 22.3708 | 22.3801 | 22.3431 | 22.0066 | 21.2054 | 22.1819 | 21.6284 | 21.7819 | 21.9077 | 21.1 | 21.2006 | 21.4089 | 20.4807 | 20.6877 | 21.5355 | 21.884 | 21.6667 | 23.1621 | 98.21 | 88.4485 | 100.7046 | 22.1168 | 21.7188 | 22.4011 | 22.0092 | 21.7597 | 22.9276 | 34.119 | 91.906 |  | 52.2953 | 79.4467 | 82.9285 | 51.1455 |  | 17.0075 | 17.2401 | 16.6471 | 17.0301 | 17.318 | 19.2197 | 48.7918 | 16.0982 | 17.0703 | 16.2004 | 17.637 | 18.179 | 44.2416 | 47.2316 | 43.522 | 21.6205 |  |  | 0.58769 | -0.1696 | -28.3882 | 0.33114 | 0.11776 | -197.8979 | 18.1255 | 0.44582 | -0.10655 | 0.072492 | 0.070078 | 0.0003417 | 0.00030227 | 1.7782 | 21.7598 | 21.9867 | 22.1803 | 22.2337 | 22.0507 | 21.346 | 20.1604 | 22.1857 | 22.364 | 22.398 | 22.3509 | 21.9654 | 21.2043 | 22.2832 | 46.8326 | 30.6375 | 31.1094 | 25.9631 | 22.8228 | 31.7814 | 24.0888 | 22.3328 | 22.1087 | 21.6757 | 22.0637 | 21.7843 | 21.2907 | 21.9437 | 21.5676 | 21.645 | 33.5645 | 97.9328 | 75.7913 | 43.279 | 0.58077 | 0.097984 | 40.5774 | 21.9717 | 22.3009 | 20.1925 | 21.6185 | 22.065 | 21.9243 | 21.7432 | 24.2626 | 21.7826 | 21.4631 | 22.1096 | 90.8862 | 108.9118 | 71.2062 | 72.0804 | 43.6412 |  | 33.3691 | 63.9144 | 35.7577 | 45.4272 | 34.3609 | 39.3896 |  | 44.9511 |  |  | 21.2527 | 22.3677 | 36.5163 | [5 empty] | 21.8943 | 34.4268 | 21.6662 | 22.054 | 27.1074 | 21.2064 | 21.8437 | 22.174 | 44.5284 | 114.523 |  | 36.0235 | 85.1021 | 20.4444 | 38.816 | 88.4583 | 28.7765 | 72.0858 | 21.7601 | 66.6164 | 21.8787 | 69.7241 | 18.5268 | 38.9879 | 80.7483 | 23.3479 | 39.2941 | 104.4814 | 20.4878 | 37.1253 | 90.3292 | 20.579 | 64.0192 | 24.2637 | 71.4349 | 22.0114 | 71.4216 | 0.45342 | 19.7869 | 0.83651 | 0.023282 | -27.121 | 3.0953 | 81.67 | 54.96 | 1.033 | -0.48907 | -6.3274 | 0.68338 | 0.40891 | -16.7631 | 5.0732 | 0.21517 | -0.26584 | 0.19962 | -1.1821 | -0.33746 | 0.032468 | 0.23194
42838.4231 | 246 | 22.9125 | 22.8776 | 22.8611 | 22.7808 | 22.4008 | 21.7269 | 22.7112 | 21.7825 | 22.3685 | 22.3788 | 22.3429 | 21.9959 | 21.2068 | 22.1823 | 21.6202 | 21.7846 | 21.9093 | 21.0929 | 21.1988 | 21.4077 | 20.4862 | 20.6873 | 21.5372 | 21.881 | 21.6564 | 23.1729 | 98.2558 | 88.4742 | 101.1912 | 22.1173 | 21.7122 | 22.4139 | 22.0097 | 21.7628 | 22.9374 | 34.1854 | 91.7983 |  | 52.401 | 79.5292 | 82.9983 | 51.0673 |  | 17.0168 | 17.2526 | 16.6669 | 17.0345 | 17.3162 | 19.1991 | 49.2418 | 16.0328 | 17.0769 | 16.2387 | 17.6462 | 18.1826 | 44.2712 | 47.2739 | 43.5318 | 21.6148 |  |  | 0.64355 | -0.31548 | -28.1162 | 0.51185 | 0.26232 | -197.8204 | 18.1577 | 0.22634 | 0.049133 | 0.2888 | 0.10428 | 0.0003762 | 0.0003417 | 1.7721 | 21.7574 | 21.9783 | 22.1834 | 22.2324 | 22.054 | 21.3445 | 20.1643 | 22.1899 | 22.3645 | 22.3963 | 22.342 | 21.9696 | 21.2045 | 22.2767 | 46.8593 | 30.0549 | 30.9651 | 26.2334 | 23.2087 | 31.862 | 24.1203 | 22.3402 | 22.107 | 21.6808 | 22.0692 | 21.7864 | 21.2895 | 21.9411 | 21.5672 | 21.6646 | 33.6324 | 98.2704 | 75.9537 | 43.2215 | 0.63129 | 0.12937 | 40.5873 | 21.976 | 22.2866 | 20.1867 | 21.6101 | 22.0584 | 21.9194 | 21.7375 | 24.2793 | 21.7726 | 21.4567 | 22.1114 | 90.912 | 109.0752 | 71.243 | 72.1146 | 43.6459 |  | 33.4315 | 63.9015 | 35.8215 | 45.5309 | 34.4277 | 40.0311 |  | 45.0435 |  |  | 21.2572 | 22.3753 | 36.5044 | [5 empty] | 21.9012 | 34.4895 | 21.6687 | 22.0417 | 27.1249 | 21.2002 | 21.8386 | 22.1889 | 44.6393 | 114.5879 |  | 36.092 | 85.1685 | 20.4468 | 38.9642 | 88.6363 | 28.8242 | 72.1852 | 21.7825 | 66.8097 | 21.8888 | 69.7876 | 18.5316 | 39.0177 | 80.771 | 23.372 | 39.3518 | 104.442 | 20.493 | 37.275 | 90.3272 | 20.5883 | 64.1566 | 24.2853 | 71.4197 | 22.0334 | 71.6065 | 0.44785 | 19.7877 | 0.83809 | 0.023326 | -27.1011 | 3.0953 | 67.38 | 56.39 | 1.0817 | -0.66704 | -6.2972 | 0.84965 | 0.61029 | -16.7592 | 5.0775 | 0.21718 | -0.26328 | 0.19904 | -1.1756 | -0.31775 | 0.036921 | 0.23587
42838.4231 | 247 | 22.9143 | 22.8791 | 22.8604 | 22.779 | 22.3933 | 21.7273 | 22.7159 | 21.7844 | 22.3631 | 22.3782 | 22.3444 | 21.9998 | 21.1995 | 22.1793 | 21.631 | 21.7842 | 21.9054 | 21.0884 | 21.1928 | 21.4076 | 20.4846 | 20.6862 | 21.5345 | 21.8725 | 21.6528 | 23.1846 | 98.3475 | 88.5063 | 101.1185 | 22.1276 | 21.7248 | 22.423 | 22.024 | 21.7747 | 22.9601 | 34.2619 | 91.2493 |  | 52.5089 | 79.6749 | 83.0731 | 51.58 |  | 17.0131 | 17.2552 | 16.6666 | 17.0423 | 17.3169 | 19.1764 | 49.2749 | 16.0381 | 17.0754 | 16.1547 | 17.6482 | 18.1723 | 44.2759 | 47.3081 | 43.5396 | 21.6101 |  |  | 0.70926 | -0.077605 | -27.9795 | 0.60976 | 0.34906 | -197.8939 | 17.9172 | 0.31768 | -0.008469 | 0.14089 | 0.051156 | 0.00034499 | 0.00036634 | 1.758 | 21.7555 | 21.9816 | 22.1776 | 22.2313 | 22.0442 | 21.3426 | 20.151 | 22.1741 | 22.355 | 22.3935 | 22.3402 | 21.9637 | 21.2016 | 22.2785 | 47.2625 | 29.8774 | 31.4953 | 25.919 | 23.3862 | 31.9481 | 24.1611 | 22.3378 | 22.1103 | 21.6747 | 22.0641 | 21.7848 | 21.2939 | 21.9397 | 21.5671 | 21.672 | 33.6937 | 98.4741 | 75.9992 | 43.2487 | 0.49269 | 0.013916 | 40.6054 | 21.9596 | 22.2869 | 20.1854 | 21.6074 | 22.0495 | 21.9231 | 21.7379 | 24.3114 | 21.7709 | 21.4591 | 22.1179 | 90.8998 | 109.2337 | 71.3206 | 72.2044 | 43.9883 |  | 33.4997 | 63.7576 | 35.8807 | 45.7995 | 34.4919 | 39.7806 |  | 45.1502 |  |  | 21.2475 | 22.3899 | 36.7842 | [5 empty] | 21.8868 | 34.4992 | 21.6587 | 22.0427 | 27.1308 | 21.2073 | 21.8382 | 22.2096 | 44.7085 | 114.5379 |  | 36.1574 | 85.4696 | 20.463 | 39.1305 | 88.6967 | 28.8481 | 72.3059 | 21.813 | 67.0683 | 21.9064 | 69.8767 | 18.5381 | 39.0707 | 80.7899 | 23.4007 | 39.4497 | 104.4674 | 20.5104 | 37.4633 | 90.3313 | 20.586 | 64.3398 | 24.313 | 71.6896 | 22.0451 | 71.8857 | 0.51333 | 19.7857 | 0.83913 | 0.023478 | -27.1226 | 3.0953 | 77.29 | 55.05 | 1.1354 | -0.33084 | -6.2819 | 0.92736 | 0.70396 | -16.7617 | 5.0435 | 0.21002 | -0.25724 | 0.19379 | -1.2103 | -0.37189 | 0.02531 | 0.23722
42838.4231 | 248 | 22.9103 | 22.8718 | 22.8613 | 22.779 | 22.3936 | 21.7292 | 22.7142 | 21.7815 | 22.3666 | 22.3736 | 22.3375 | 21.9917 | 21.1971 | 22.1724 | 21.6213 | 21.7866 | 21.9041 | 21.0882 | 21.1903 | 21.4059 | 20.4824 | 20.6846 | 21.5421 | 21.8723 | 21.6573 | 23.2049 | 98.353 | 88.5298 | 100.6172 | 22.1219 | 21.7269 | 22.4352 | 22.0161 | 21.7686 | 22.9747 | 34.3351 | 90.9883 |  | 52.634 | 79.8172 | 83.1564 | 52.2397 |  | 17.0218 | 17.2558 | 16.6797 | 17.0626 | 17.3498 | 19.1524 | 48.8847 | 16.079 | 17.0778 | 16.0256 | 17.6535 | 18.1859 | 44.2822 | 47.3655 | 43.5402 | 21.6212 |  |  | 0.58375 | -0.26948 | -28.1523 | 0.66364 | 0.27349 | -197.8282 | 17.9606 | 0.21912 | 0.06256 | 0.23215 | 0.098549 | 0.00032692 | 0.00031213 | 1.7573 | 21.7573 | 21.9777 | 22.1786 | 22.2307 | 22.0497 | 21.3369 | 20.1635 | 22.1838 | 22.3578 | 22.4048 | 22.3457 | 21.9622 | 21.2097 | 22.2802 | 47.5575 | 30.6118 | 33.2511 | 26.4192 | 23.2231 | 32.0439 | 24.1989 | 22.3456 | 22.1109 | 21.6766 | 22.0669 | 21.7809 | 21.2943 | 21.9476 | 21.5728 | 21.6803 | 33.7678 | 98.6747 | 76.0627 | 43.3629 | 0.44413 | 0.26022 | 40.624 | 21.967 | 22.2853 | 20.1839 | 21.6068 | 22.0454 | 21.9153 | 21.7309 | 24.3405 | 21.7725 | 21.4564 | 22.1238 | 90.9587 | 109.3392 | 71.3655 | 72.2541 | 44.2557 |  | 33.5894 | 63.7261 | 35.959 | 46.0205 | 34.574 | 39.8307 |  | 45.2554 |  |  | 21.247 | 22.4023 | 37.1117 | [5 empty] | 21.904 | 34.5346 | 21.6624 | 22.0448 | 27.1516 | 21.2031 | 21.8383 | 22.2228 | 44.7847 | 114.7355 |  | 36.2143 | 85.6559 | 20.463 | 39.2241 | 88.8212 | 28.8468 | 72.4166 | 21.8275 | 67.2009 | 21.8978 | 69.9744 | 18.5393 | 39.124 | 80.8623 | 23.4159 | 39.5812 | 104.6783 | 20.5214 | 37.6063 | 90.4436 | 20.5751 | 64.4665 | 24.346 | 71.9488 | 22.0565 | 72.0825 | 0.34824 | 19.7839 | 0.84023 | 0.022295 | -27.1135 | 3.0953 | 58.82 | 56 | 1.0294 | -0.6165 | -6.3012 | 0.96747 | 0.6231 | -16.7582 | 5.0494 | 0.20566 | -0.25367 | 0.19047 | -1.2318 | -0.56255 | 0.0095018 | 0.23659
42838.4232 | 249 | 22.917 | 22.8756 | 22.8624 | 22.7857 | 22.4025 | 21.7302 | 22.7266 | 21.7831 | 22.3642 | 22.3766 | 22.3407 | 21.9987 | 21.1974 | 22.1804 | 21.6241 | 21.788 | 21.9114 | 21.0921 | 21.2006 | 21.4161 | 20.483 | 20.6987 | 21.5544 | 21.8769 | 21.6599 | 23.2324 | 98.492 | 88.5874 | 101.061 | 22.1227 | 21.7167 | 22.4422 | 22.0099 | 21.766 | 22.9864 | 34.3947 | 91.7811 |  | 52.7603 | 79.9535 | 83.2323 | 52.4706 |  | 17.0224 | 17.2597 | 16.6807 | 17.0651 | 17.3581 | 19.1515 | 48.4627 | 16.1299 | 17.0749 | 15.9587 | 17.659 | 18.1967 | 44.2912 | 47.4226 | 43.5442 | 21.6203 |  |  | 0.61858 | -0.22217 | -28.172 | 0.6367 | 0.27218 | -197.8447 | 18.157 | 0.16129 | 0.15441 | 0.097458 | 0.10601 | 0.00035484 | 0.00038441 | 1.7764 | 21.766 | 21.98 | 22.1845 | 22.2363 | 22.0525 | 21.3448 | 20.16 | 22.1866 | 22.3566 | 22.3965 | 22.3478 | 21.9664 | 21.2052 | 22.2722 | 47.758 | 31.0685 | 35.2314 | 26.2278 | 23.5873 | 32.129 | 24.2691 | 22.3425 | 22.1063 | 21.6643 | 22.068 | 21.7876 | 21.2908 | 21.9481 | 21.5642 | 21.6798 | 33.8325 | 98.6813 | 76.0888 | 43.5664 | 0.49859 | 0.32223 | 40.5181 | 21.9732 | 22.2931 | 20.1893 | 21.6117 | 22.0515 | 21.9159 | 21.7454 | 24.3637 | 21.7765 | 21.4602 | 22.1359 | 91.1616 | 109.8274 | 71.4378 | 72.3077 | 43.9608 |  | 33.6748 | 63.5395 | 36.0333 | 46.2614 | 34.6539 | 40.0922 |  | 45.3544 |  |  | 21.2514 | 22.4061 | 36.901 | [5 empty] | 21.8953 | 34.6137 | 21.6608 | 22.0465 | 27.1729 | 21.2025 | 21.8437 | 22.2418 | 44.8873 | 114.7154 |  | 36.2836 | 85.7851 | 20.4786 | 39.2562 | 88.8942 | 28.8842 | 72.4586 | 21.8523 | 67.2934 | 21.9148 | 70.0913 | 18.5351 | 39.2526 | 80.9087 | 23.4344 | 39.6614 | 104.8509 | 20.5376 | 37.6845 | 90.4387 | 20.5786 | 64.5802 | 24.3555 | 72.0606 | 22.0777 | 72.1792 | 0.41001 | 19.7813 | 0.84072 | 0.022317 | -27.0239 | 3.0953 | 83.18 | 55.72 | 1.0603 | -0.55978 | -6.3035 | 0.94763 | 0.62159 | -16.7589 | 5.077 | 0.21679 | -0.24592 | 0.18652 | -1.2441 | -0.77436 | 0.0051344 | 0.23316
42838.4232 | 250 | 22.9185 | 22.8673 | 22.8634 | 22.7842 | 22.4013 | 21.7211 | 22.7245 | 21.7801 | 22.363 | 22.3712 | 22.3448 | 21.994 | 21.2039 | 22.1731 | 21.6227 | 21.7869 | 21.9093 | 21.0917 | 21.1982 | 21.4149 | 20.4848 | 20.693 | 21.5688 | 21.8709 | 21.6657 | 23.2456 | 98.6341 | 88.7144 | 101.3097 | 22.1113 | 21.7149 | 22.4504 | 22.0008 | 21.7696 | 22.999 | 34.4637 | 92.6374 |  | 52.8968 | 80.07 | 83.2957 | 52.333 |  | 17.0153 | 17.2582 | 16.6874 | 17.0662 | 17.3552 | 19.1365 | 48.8328 | 16.1811 | 17.0726 | 15.9037 | 17.6522 | 18.1914 | 44.2861 | 47.46 | 43.5411 | 21.6158 |  |  | 0.57126 | -0.32271 | -28.4526 | 0.35677 | 0.3668 | -197.8256 | 17.6813 | 0.26117 | 0.29861 | -0.0013574 | 0.21295 | 0.00034827 | 0.00032035 | 1.7994 | 21.7617 | 21.9755 | 22.1775 | 22.2286 | 22.0483 | 21.3426 | 20.1563 | 22.1813 | 22.3588 | 22.3926 | 22.3438 | 21.9597 | 21.2013 | 22.2758 | 47.4921 | 31.0288 | 36.9614 | 26.7481 | 23.6798 | 32.2125 | 24.3418 | 22.339 | 22.1093 | 21.6715 | 22.0683 | 21.7774 | 21.2944 | 21.939 | 21.5652 | 21.6905 | 33.8986 | 98.8628 | 76.1362 | 43.6249 | 0.43961 | -0.13007 | 40.4334 | 21.9745 | 22.2893 | 20.1997 | 21.6132 | 22.0611 | 21.9237 | 21.7452 | 24.3892 | 21.781 | 21.4592 | 22.16 | 91.2707 | 110.1481 | 71.5562 | 72.4345 | 43.7169 |  | 33.7499 | 64.0463 | 36.1007 | 46.2782 | 34.7369 | 40.1762 |  | 45.4442 |  |  | 21.2319 | 22.4068 | 36.7764 | [5 empty] | 21.8919 | 34.7074 | 21.6597 | 22.0452 | 27.2018 | 21.2019 | 21.8421 | 22.2565 | 45.0042 | 114.6827 |  | 36.3848 | 85.9406 | 20.4881 | 39.2929 | 89.0177 | 28.911 | 72.4972 | 21.8686 | 67.3441 | 21.9282 | 70.1912 | 18.5299 | 39.3588 | 81.0076 | 23.4584 | 39.7432 | 104.8596 | 20.544 | 37.7472 | 90.4532 | 20.5914 | 64.6983 | 24.3654 | 72.2352 | 22.0944 | 72.2741 | 0.30223 | 19.7792 | 0.84158 | 0.023072 | -27.1302 | 3.0954 | 71.64 | 55.09 | 1.0193 | -0.67465 | -6.3348 | 0.70936 | 0.72159 | -16.7576 | 5.0099 | 0.22614 | -0.25767 | 0.18891 | -1.2047 | -0.95807 | 0.01133 | 0.2338
42838.4232 | 251 | 22.908 | 22.8773 | 22.8643 | 22.7816 | 22.3995 | 21.7307 | 22.7159 | 21.785 | 22.364 | 22.3782 | 22.3473 | 21.9863 | 21.2029 | 22.1751 | 21.6161 | 21.7824 | 21.9045 | 21.0902 | 21.1892 | 21.4064 | 20.4784 | 20.6845 | 21.5686 | 21.8712 | 21.6567 | 23.2527 | 98.6914 | 88.801 | 101.4079 | 22.1081 | 21.7202 | 22.4614 | 22.0034 | 21.7569 | 23.0081 | 34.5429 | 93.3556 |  | 53.0181 | 80.16 | 83.3862 | 52.1951 |  | 17.0274 | 17.2659 | 16.699 | 17.0841 | 17.3846 | 19.1608 | 49.0912 | 16.229 | 17.0752 | 15.7861 | 17.6626 | 18.1865 | 44.3013 | 47.5106 | 43.5463 | 21.6196 |  |  | 0.58375 | -0.26817 | -28.6123 | 0.39883 | 0.24984 | -197.8059 | 17.8357 | 0.11069 | 0.20695 | 0.13543 | 0.070599 | 0.00033349 | 0.00030885 | 1.8104 | 21.7622 | 21.9792 | 22.1781 | 22.2316 | 22.0508 | 21.3473 | 20.1623 | 22.1827 | 22.3576 | 22.4024 | 22.3445 | 21.9711 | 21.2045 | 22.2801 | 48.4045 | 30.2273 | 34.2603 | 27.0111 | 24.1026 | 32.3008 | 24.365 | 22.334 | 22.1039 | 21.6665 | 22.0693 | 21.7787 | 21.29 | 21.9418 | 21.5613 | 21.6968 | 33.9654 | 98.9814 | 76.2628 | 43.6891 | 0.48168 | -0.1508 | 40.3541 | 21.9727 | 22.2983 | 20.1938 | 21.6051 | 22.0483 | 21.9162 | 21.7399 | 24.4201 | 21.7753 | 21.4737 | 22.1699 | 91.4472 | 110.1963 | 71.7164 | 72.5814 | 43.7774 |  | 33.8223 | 64.6615 | 36.1717 | 46.3777 | 34.8148 | 39.9716 |  | 45.5273 |  |  | 21.2344 | 22.4224 | 36.8281 | [5 empty] | 21.8953 | 34.7769 | 21.6652 | 22.052 | 27.2359 | 21.2057 | 21.8477 | 22.266 | 45.0897 | 114.8422 |  | 36.5121 | 86.1065 | 20.5014 | 39.4106 | 89.1386 | 28.9427 | 72.5206 | 21.8829 | 67.4463 | 21.93 | 70.2793 | 18.5113 | 39.4464 | 81.0369 | 23.4733 | 39.8266 | 104.8548 | 20.5429 | 37.8457 | 90.4502 | 20.5874 | 64.7749 | 24.3928 | 72.376 | 22.1095 | 72.3921 | 0.47122 | 19.777 | 0.84376 | 0.02358 | -27.068 | 3.0953 | 73.7 | 53.26 | 1.0305 | -0.61501 | -6.3526 | 0.75001 | 0.59555 | -16.7575 | 5.0319 | 0.22695 | -0.27231 | 0.18883 | -1.2957 | -0.65523 | 0.017883 | 0.23431
42838.4232 | 252 | 22.9138 | 22.8724 | 22.8626 | 22.788 | 22.3975 | 21.7274 | 22.7205 | 21.7737 | 22.3631 | 22.3678 | 22.3401 | 21.9955 | 21.2011 | 22.1717 | 21.6216 | 21.7822 | 21.9128 | 21.0917 | 21.1919 | 21.4135 | 20.4842 | 20.6935 | 21.583 | 21.8835 | 21.6641 | 23.2754 | 98.7886 | 88.8943 | 101.9755 | 22.1255 | 21.7255 | 22.4876 | 22.0185 | 21.7664 | 23.0346 | 34.6399 | 93.9115 |  | 53.1865 | 80.2683 | 83.4546 | 52.1845 |  | 17.016 | 17.2735 | 16.7012 | 17.0828 | 17.4176 | 19.2652 | 49.4824 | 16.2733 | 17.0762 | 15.7227 | 17.6666 | 18.1963 | 44.3111 | 47.561 | 43.5545 | 21.6228 |  |  | 0.55089 | -0.27408 | -28.5354 | 0.28251 | 0.3116 | -197.8223 | 17.7214 | 0.069292 | -0.023259 | 0.036616 | -0.025575 | 0.0002957 | 0.00031377 | 1.7969 | 21.766 | 21.9782 | 22.1839 | 22.231 | 22.0498 | 21.3502 | 20.1613 | 22.1805 | 22.3605 | 22.3994 | 22.3451 | 21.9713 | 21.1993 | 22.2754 | 48.0871 | 29.6358 | 32.5962 | 26.1087 | 24.0156 | 32.3798 | 24.3959 | 22.3335 | 22.1014 | 21.6611 | 22.0696 | 21.781 | 21.2844 | 21.9362 | 21.5641 | 21.708 | 34.0307 | 99.1063 | 76.3422 | 43.7437 | 0.52179 | 0.020953 | 40.2604 | 21.9763 | 22.29 | 20.1948 | 21.6161 | 22.0584 | 21.9207 | 21.7481 | 24.4435 | 21.7819 | 21.4623 | 22.1861 | 91.6436 | 110.3434 | 71.9089 | 72.7423 | 43.953 |  | 33.9159 | 64.5356 | 36.243 | 46.5375 | 34.913 | 39.7962 |  | 45.6216 |  |  | 21.2462 | 22.4378 | 36.8738 | [5 empty] | 21.8943 | 34.8213 | 21.6567 | 22.0476 | 27.2854 | 21.2064 | 21.8435 | 22.2783 | 45.1925 | 114.9945 |  | 36.6577 | 86.3012 | 20.5124 | 39.549 | 89.2135 | 28.9905 | 72.545 | 21.9063 | 67.6132 | 21.9349 | 70.4894 | 18.5001 | 39.5783 | 81.0646 | 23.4961 | 39.9056 | 105.0006 | 20.5452 | 37.903 | 90.4365 | 20.5972 | 64.8255 | 24.427 | 72.4848 | 22.1213 | 72.5525 | 0.37272 | 19.7751 | 0.84642 | 0.025409 | -27.0814 | 3.0953 | 68.83 | 51.48 | 1.0018 | -0.62176 | -6.3442 | 0.63125 | 0.66522 | -16.7612 | 5.0167 | 0.22528 | -0.26636 | 0.18777 | -1.2512 | -0.46672 | 0.021513 | 0.23504
42838.4232 | 253 | 22.9195 | 22.881 | 22.8588 | 22.7763 | 22.3989 | 21.7372 | 22.7154 | 21.7809 | 22.3659 | 22.3673 | 22.3446 | 21.9956 | 21.2032 | 22.1702 | 21.6159 | 21.7846 | 21.9062 | 21.0953 | 21.1927 | 21.41 | 20.4799 | 20.6986 | 21.5849 | 21.8751 | 21.6608 | 23.2946 | 99.0333 | 88.963 | 102.8319 | 22.1306 | 21.7299 | 22.505 | 22.0159 | 21.7828 | 23.0561 | 34.7299 | 94.3782 |  | 53.3187 | 80.3562 | 83.5303 | 52.4112 |  | 17.0253 | 17.2762 | 16.7017 | 17.1082 | 17.4621 | 19.4607 | 50.0459 | 16.2891 | 17.0803 | 15.7122 | 17.6775 | 18.1922 | 44.319 | 47.6194 | 43.5596 | 21.6191 |  |  | 0.64223 | -0.15712 | -28.2633 | 0.20169 | 0.26824 | -197.8243 | 17.6471 | 0.029868 | 0.18321 | 0.24872 | 0.15184 | 0.00033349 | 0.00032692 | 1.7747 | 21.7587 | 21.9813 | 22.1776 | 22.2237 | 22.0448 | 21.3508 | 20.159 | 22.1803 | 22.364 | 22.3948 | 22.3477 | 21.9654 | 21.2007 | 22.2747 | 48.0155 | 28.4489 | 30.592 | 25.0642 | 23.7239 | 32.468 | 24.4035 | 22.3324 | 22.1071 | 21.6699 | 22.0656 | 21.782 | 21.2991 | 21.9353 | 21.5715 | 21.7139 | 34.1069 | 99.2952 | 76.3541 | 43.9972 | 0.41562 | 0.010302 | 40.1509 | 21.9573 | 22.2813 | 20.1886 | 21.6005 | 22.0525 | 21.9088 | 21.7428 | 24.4548 | 21.7643 | 21.462 | 22.1863 | 91.7996 | 110.633 | 72.0267 | 72.8562 | 44.1434 |  | 33.9775 | 64.3592 | 36.3092 | 46.7101 | 34.9789 | 40.1277 |  | 45.7013 |  |  | 21.2538 | 22.451 | 36.8649 | [5 empty] | 21.8962 | 34.8646 | 21.6644 | 22.0496 | 27.3306 | 21.2177 | 21.8482 | 22.2992 | 45.3085 | 115.3131 |  | 36.7898 | 86.5533 | 20.5289 | 39.6657 | 89.4199 | 29.0442 | 72.5557 | 21.9273 | 67.7534 | 21.9433 | 70.6872 | 18.4969 | 39.7318 | 81.2082 | 23.5195 | 40.0198 | 105.1478 | 20.5548 | 37.9561 | 90.4295 | 20.6048 | 64.8995 | 24.4487 | 72.5389 | 22.1461 | 72.6973 | 0.31522 | 19.7726 | 0.84875 | 0.02644 | -27.0755 | 3.0953 | 67.44 | 52.7 | 1.0829 | -0.47076 | -6.3139 | 0.53337 | 0.61741 | -16.7669 | 5.0078 | 0.22211 | -0.25918 | 0.18524 | -1.2328 | -0.24313 | 0.018311 | 0.23062
42838.4232 | 254 | 22.9281 | 22.8831 | 22.8614 | 22.7881 | 22.4 | 21.7411 | 22.7218 | 21.7903 | 22.3724 | 22.3721 | 22.3523 | 22.0002 | 21.2107 | 22.1783 | 21.6187 | 21.7868 | 21.91 | 21.0921 | 21.1934 | 21.4066 | 20.4744 | 20.6974 | 21.5963 | 21.869 | 21.6526 | 23.3123 | 99.241 | 89.0095 | 103.1386 | 22.1348 | 21.7392 | 22.5168 | 22.0196 | 21.7775 | 23.07 | 34.8127 | 94.3028 |  | 53.4571 | 80.4908 | 83.5666 | 53.1523 |  | 17.0252 | 17.2787 | 16.7124 | 17.1484 | 17.5494 | 19.4679 | 49.7815 | 16.2802 | 17.0835 | 15.7786 | 17.681 | 18.2014 | 44.3341 | 47.6755 | 43.5656 | 21.6301 |  |  | 0.39976 | -0.1558 | -28.1208 | 0.33114 | 0.23472 | -197.7993 | 18.1682 | 0.10215 | 0.15694 | 0.35803 | 0.17007 | 0.00031706 | 0.00031049 | 1.7529 | 21.7674 | 21.9883 | 22.176 | 22.236 | 22.0422 | 21.3476 | 20.1615 | 22.1874 | 22.3639 | 22.3968 | 22.3499 | 21.9715 | 21.1982 | 22.2743 | 47.3115 | 29.2061 | 31.3926 | 24.2186 | 22.9356 | 32.5502 | 24.427 | 22.3329 | 22.1057 | 21.672 | 22.0707 | 21.7757 | 21.3005 | 21.9416 | 21.5709 | 21.725 | 34.1806 | 99.2958 | 76.3995 | 44.3468 | 0.46163 | -0.042384 | 40.417 | 21.9717 | 22.289 | 20.1868 | 21.6074 | 22.0509 | 21.9174 | 21.7442 | 24.4919 | 21.7767 | 21.4606 | 22.2043 | 92.0883 | 111.18 | 72.146 | 72.9539 | 43.8243 |  | 34.0391 | 64.8716 | 36.3759 | 46.8965 | 35.0471 | 40.3877 |  | 45.791 |  |  | 21.2606 | 22.473 | 36.7858 | [5 empty] | 21.8974 | 34.8551 | 21.671 | 22.0495 | 27.3708 | 21.2177 | 21.8525 | 22.3199 | 45.3826 | 115.8257 |  | 36.8867 | 86.7991 | 20.54 | 39.7352 | 89.7603 | 29.0905 | 72.5832 | 21.9493 | 67.8324 | 21.9568 | 70.7745 | 18.5038 | 39.8347 | 81.3848 | 23.5348 | 40.1516 | 105.1967 | 20.5627 | 38.0674 | 90.5454 | 20.6173 | 64.9979 | 24.4672 | 72.6768 | 22.1659 | 72.8887 | 0.32561 | 19.7726 | 0.84938 | 0.026055 | -27.0957 | 3.0954 | 50.42 | 51.57 | 0.85472 | -0.46878 | -6.298 | 0.68343 | 0.57755 | -16.766 | 5.0813 | 0.23309 | -0.27111 | 0.18241 | -1.145 | -0.32934 | 0.00057152 | 0.22344
42838.4232 | 255 | 22.919 | 22.8735 | 22.8675 | 22.788 | 22.3977 | 21.7375 | 22.7194 | 21.7863 | 22.3683 | 22.3767 | 22.344 | 22.0023 | 21.2091 | 22.1736 | 21.6188 | 21.7845 | 21.913 | 21.0913 | 21.1925 | 21.4112 | 20.4738 | 20.6973 | 21.608 | 21.8756 | 21.6645 | 23.3313 | 99.3391 | 89.0622 | 103.0754 | 22.1296 | 21.7344 | 22.5325 | 22.0188 | 21.7801 | 23.0835 | 34.9016 | 94.7771 |  | 53.5938 | 80.6284 | 83.5934 | 53.5278 |  | 17.0237 | 17.2777 | 16.7161 | 17.196 | 17.5724 | 19.4782 | 49.7145 | 16.2942 | 17.0888 | 15.8617 | 17.683 | 18.2106 | 44.3563 | 47.7352 | 43.5823 | 21.6365 |  |  | 0.42079 | -0.1512 | -27.9262 | 0.21746 | 0.088184 | -197.5588 | 17.6806 | 0.038408 | 0.2017 | 0.24809 | 0.20549 | 0.00030392 | 0.00029899 | 1.7455 | 21.7625 | 21.9868 | 22.1783 | 22.2387 | 22.0515 | 21.3469 | 20.1617 | 22.1966 | 22.3661 | 22.4095 | 22.3512 | 21.9681 | 21.2021 | 22.2747 | 47.123 | 28.9474 | 29.3615 | 23.8663 | 22.5644 | 32.6247 | 24.4491 | 22.3314 | 22.1037 | 21.6681 | 22.0638 | 21.7747 | 21.2894 | 21.9394 | 21.5677 | 21.7373 | 34.2478 | 99.5231 | 76.5567 | 44.6158 | 0.37218 | 0.038451 | 40.2709 | 21.9676 | 22.2885 | 20.1853 | 21.5952 | 22.0489 | 21.9123 | 21.7548 | 24.5258 | 21.768 | 21.4657 | 22.216 | 92.3398 | 111.6787 | 72.2865 | 73.0788 | 43.6358 |  | 34.1182 | 65.3214 | 36.4687 | 46.9361 | 35.1434 | 40.2099 |  | 45.9279 |  |  | 21.2647 | 22.4732 | 36.7437 | [5 empty] | 21.8966 | 34.8679 | 21.6735 | 22.0564 | 27.3982 | 21.2144 | 21.8561 | 22.3339 | 45.4606 | 116.1369 |  | 36.9344 | 86.9945 | 20.547 | 39.799 | 90.1263 | 29.1435 | 72.6282 | 21.9696 | 67.8688 | 21.9653 | 70.8355 | 18.5061 | 39.9455 | 81.5702 | 23.5598 | 40.2737 | 105.1739 | 20.5689 | 38.2014 | 90.7669 | 20.6195 | 65.0721 | 24.4818 | 72.9357 | 22.1817 | 73.0695 | 0.43449 | 19.7682 | 0.85098 | 0.025395 | -27.0499 | 3.0953 | 60.05 | 51.9 | 0.87684 | -0.46181 | -6.2761 | 0.55383 | 0.35401 | -16.7561 | 5.0127 | 0.24104 | -0.2804 | 0.18463 | -1.1153 | -0.10108 | -0.0067989 | 0.21827
42838.4232 | 256 | 22.9145 | 22.8771 | 22.8612 | 22.783 | 22.3988 | 21.7347 | 22.7182 | 21.7826 | 22.366 | 22.3765 | 22.3466 | 21.9966 | 21.2067 | 22.1697 | 21.6175 | 21.7822 | 21.9088 | 21.0847 | 21.192 | 21.4087 | 20.4771 | 20.7023 | 21.6099 | 21.8705 | 21.6666 | 23.3471 | 99.3481 | 89.1234 | 102.8775 | 22.1232 | 21.7302 | 22.5382 | 22.0205 | 21.7771 | 23.0938 | 34.9837 | 96.3312 |  | 53.7497 | 80.7698 | 83.6271 | 53.86 |  | 17.0236 | 17.2756 | 16.7372 | 17.1963 | 17.5889 | 19.4691 | 50.0546 | 16.2159 | 17.0889 | 15.9481 | 17.6788 | 18.2049 | 44.3661 | 47.7804 | 43.5787 | 21.6284 |  |  | 0.58835 | -0.24977 | -28.059 | 0.58479 | 0.21172 | -197.4051 | 18.0276 | 0.08112 | 0.085134 | 0.18096 | 0.16834 | 0.00033513 | 0.00031542 | 1.7564 | 21.7632 | 21.9809 | 22.1668 | 22.2377 | 22.0497 | 21.3419 | 20.1548 | 22.1879 | 22.3603 | 22.4008 | 22.3431 | 21.971 | 21.1987 | 22.279 | 46.2305 | 28.8369 | 30.5143 | 23.5331 | 22.1794 | 32.6908 | 24.4812 | 22.3372 | 22.1043 | 21.6687 | 22.0632 | 21.7777 | 21.2909 | 21.9334 | 21.5621 | 21.7454 | 34.3255 | 99.7421 | 76.8757 | 44.8794 | 0.24851 | 0.030273 | 40.2912 | 21.9641 | 22.2848 | 20.1858 | 21.601 | 22.0408 | 21.9148 | 21.7547 | 24.5409 | 21.7725 | 21.453 | 22.224 | 92.4675 | 112.0061 | 72.4372 | 73.2267 | 43.3862 |  | 34.1924 | 65.5269 | 36.5398 | 46.9649 | 35.2264 | 40.2245 |  | 46.0404 |  |  | 21.2737 | 22.4729 | 36.7705 | [5 empty] | 21.8941 | 34.8846 | 21.67 | 22.0588 | 27.4282 | 21.2154 | 21.8547 | 22.353 | 45.5792 | 116.2532 |  | 37.0845 | 87.1412 | 20.5533 | 39.9195 | 90.3902 | 29.2019 | 72.7217 | 21.9857 | 67.9021 | 21.9809 | 70.9044 | 18.513 | 40.1103 | 81.7436 | 23.5895 | 40.3403 | 105.1406 | 20.5737 | 38.3426 | 90.9508 | 20.6131 | 65.1339 | 24.4861 | 73.2275 | 22.1945 | 73.1568 | 0.32375 | 19.7695 | 0.85191 | 0.026397 | -27.1152 | 3.0953 | 52.54 | 52.6 | 1.0366 | -0.59355 | -6.291 | 0.90821 | 0.54853 | -16.7493 | 5.0616 | 0.25053 | -0.28365 | 0.18669 | -1.0083 | -0.22541 | -0.013202 | 0.21362
42838.4233 | 257 | 22.9148 | 22.8705 | 22.8605 | 22.7844 | 22.3999 | 21.7248 | 22.7164 | 21.7776 | 22.3686 | 22.3684 | 22.3425 | 21.9902 | 21.2041 | 22.1773 | 21.6165 | 21.7975 | 21.9094 | 21.0916 | 21.1908 | 21.4128 | 20.488 | 20.6992 | 21.6221 | 21.8723 | 21.6566 | 23.3667 | 99.4638 | 89.1553 | 103.1703 | 22.1295 | 21.7345 | 22.5525 | 22.0258 | 21.7784 | 23.1115 | 35.074 | 97.5792 |  | 53.9127 | 80.9269 | 83.652 | 54.4707 |  | 17.0192 | 17.275 | 16.7509 | 17.2044 | 17.5904 | 19.4689 | 50.0038 | 16.1233 | 17.0813 | 16.0348 | 17.6818 | 18.2051 | 44.3745 | 47.837 | 43.5829 | 21.6271 |  |  | 0.45233 | -0.18997 | -28.0695 | 0.53091 | 0.22092 | -197.2073 | 17.7417 | 0.089664 | 0.13184 | 0.10438 | 0.1232 | 0.00030885 | 0.00030556 | 1.7645 | 21.7564 | 21.9825 | 22.1718 | 22.2321 | 22.0419 | 21.3461 | 20.1642 | 22.1809 | 22.3547 | 22.3939 | 22.3441 | 21.9685 | 21.1931 | 22.2736 | 44.6888 | 27.8879 | 29.6173 | 24.1573 | 21.9743 | 32.7168 | 24.4897 | 22.3385 | 22.1071 | 21.6659 | 22.0594 | 21.7777 | 21.2966 | 21.9425 | 21.5684 | 21.7607 | 34.3985 | 99.9448 | 77.1136 | 44.8525 | 0.53732 | -0.12702 | 40.3516 | 21.97 | 22.2896 | 20.1926 | 21.6012 | 22.0556 | 21.9178 | 21.7479 | 24.5705 | 21.7758 | 21.4669 | 22.2399 | 92.6586 | 112.3127 | 72.6365 | 73.3858 | 43.3537 |  | 34.2617 | 65.3803 | 36.6267 | 47.0472 | 35.307 | 40.559 |  | 46.1426 |  |  | 21.2699 | 22.4845 | 36.727 | [5 empty] | 21.8932 | 34.8959 | 21.6686 | 22.0546 | 27.4472 | 21.2146 | 21.8507 | 22.3609 | 45.7773 | 116.2307 |  | 37.2928 | 87.3251 | 20.5565 | 40.1001 | 90.6468 | 29.2399 | 72.816 | 21.9937 | 68.1838 | 21.9947 | 70.9749 | 18.5183 | 40.2466 | 81.8716 | 23.6163 | 40.3666 | 105.2083 | 20.5843 | 38.501 | 91.0977 | 20.6188 | 65.1928 | 24.5062 | 73.4379 | 22.2129 | 73.1916 | 0.37699 | 19.7677 | 0.85274 | 0.026861 | -27.0536 | 3.0953 | 80.31 | 51.37 | 0.90923 | -0.51764 | -6.2922 | 0.86535 | 0.56032 | -16.7409 | 5.0213 | 0.25381 | -0.27658 | 0.18717 | -0.83395 | -0.12474 | -0.027057 | 0.21688
42838.4233 | 258 | 22.913 | 22.8676 | 22.8584 | 22.7864 | 22.3992 | 21.7274 | 22.7142 | 21.7781 | 22.3653 | 22.3682 | 22.3445 | 21.9898 | 21.209 | 22.1687 | 21.6215 | 21.7895 | 21.9141 | 21.098 | 21.1997 | 21.4213 | 20.4818 | 20.7012 | 21.634 | 21.8784 | 21.6694 | 23.387 | 99.6082 | 89.1965 | 102.967 | 22.1161 | 21.7275 | 22.5539 | 22.0098 | 21.7704 | 23.1178 | 35.146 | 97.8147 |  | 54.0462 | 81.0942 | 83.6285 | 54.9651 |  | 17.021 | 17.2717 | 16.7601 | 17.2251 | 17.5856 | 19.5215 | 49.6573 | 16.0265 | 17.0863 | 16.1312 | 17.6774 | 18.1975 | 44.3835 | 47.9058 | 43.6021 | 21.6268 |  |  | 0.71057 | -0.29183 | -27.8474 | 0.58873 | 0.31489 | -197.1179 | 17.8442 | 0.14683 | 0.31846 | 0.19082 | 0.16782 | 0.00035484 | 0.00033349 | 1.7504 | 21.7635 | 21.9724 | 22.1753 | 22.2274 | 22.041 | 21.3444 | 20.1595 | 22.1805 | 22.3521 | 22.3901 | 22.3425 | 21.9702 | 21.1953 | 22.2682 | 45.0509 | 28.2911 | 28.4244 | 23.6876 | 22.0083 | 32.7931 | 24.4878 | 22.3388 | 22.109 | 21.6694 | 22.0668 | 21.7772 | 21.2946 | 21.94 | 21.5757 | 21.7695 | 34.496 | 100.3976 | 77.3517 | 44.9383 | 0.58726 | -0.12132 | 40.5467 | 21.9699 | 22.2848 | 20.1946 | 21.5986 | 22.0563 | 21.9136 | 21.7539 | 24.5917 | 21.7717 | 21.4681 | 22.2565 | 92.8083 | 112.3875 | 72.7624 | 73.5583 | 43.4991 |  | 34.347 | 65.4318 | 36.7212 | 47.184 | 35.3994 | 40.5316 |  | 46.267 |  |  | 21.2812 | 22.4975 | 36.7682 | [5 empty] | 21.8947 | 34.9988 | 21.6699 | 22.0518 | 27.4754 | 21.2139 | 21.8504 | 22.3808 | 45.9485 | 116.7504 |  | 37.4433 | 87.4909 | 20.5739 | 40.2487 | 90.8427 | 29.2796 | 72.9081 | 22.0151 | 68.4773 | 22.0104 | 71.1376 | 18.5287 | 40.342 | 81.9844 | 23.6366 | 40.4268 | 105.5051 | 20.5859 | 38.5717 | 91.2064 | 20.6195 | 65.2341 | 24.5251 | 73.5689 | 22.2279 | 73.1861 | 0.38979 | 19.7652 | 0.85334 | 0.027326 | -27.1492 | 3.0953 | 54.31 | 52.55 | 1.1393 | -0.64157 | -6.2672 | 0.91125 | 0.66902 | -16.7386 | 5.0362 | 0.25271 | -0.27475 | 0.18655 | -0.86523 | 0.0075754 | -0.038314 | 0.21785
42838.4233 | 259 | 22.9134 | 22.8816 | 22.8691 | 22.7932 | 22.4044 | 21.732 | 22.7211 | 21.7843 | 22.3677 | 22.3748 | 22.345 | 21.9973 | 21.2138 | 22.176 | 21.6224 | 21.7844 | 21.9172 | 21.0987 | 21.1921 | 21.4195 | 20.4901 | 20.7044 | 21.639 | 21.8803 | 21.6639 | 23.4062 | 99.6677 | 89.2795 | 102.6709 | 22.1247 | 21.7434 | 22.5829 | 22.0222 | 21.7827 | 23.1457 | 35.2434 | 98.04 |  | 54.1882 | 81.2438 | 83.6238 | 55.0241 |  | 17.018 | 17.2706 | 16.7535 | 17.2414 | 17.5968 | 19.5615 | 49.8381 | 15.9897 | 17.0838 | 16.1488 | 17.6804 | 18.2119 | 44.4091 | 47.9813 | 43.6192 | 21.6287 |  |  | 0.94713 | -0.19983 | -27.6411 | 0.44811 | 0.33132 | -196.9484 | 17.8502 | 0.16326 | 0.2774 | 0.26194 | 0.2376 | 0.00035813 | 0.00030556 | 1.7531 | 21.7628 | 21.9739 | 22.1706 | 22.2266 | 22.039 | 21.3382 | 20.155 | 22.1807 | 22.3553 | 22.386 | 22.3424 | 21.962 | 21.1992 | 22.2691 | 46.5612 | 29.5177 | 29.6308 | 23.0244 | 21.6523 | 32.8868 | 24.5165 | 22.3393 | 22.1092 | 21.6699 | 22.0715 | 21.7841 | 21.2965 | 21.9404 | 21.5708 | 21.7723 | 34.5617 | 100.6987 | 77.5956 | 45.2072 | 0.42526 | 0.051005 | 40.5695 | 21.9573 | 22.2751 | 20.1815 | 21.5895 | 22.0409 | 21.9092 | 21.7507 | 24.6074 | 21.7631 | 21.4546 | 22.2505 | 92.8734 | 112.5209 | 72.915 | 73.7092 | 43.9373 |  | 34.427 | 65.0604 | 36.8132 | 47.2202 | 35.4889 | 40.5464 |  | 46.375 |  |  | 21.2921 | 22.5248 | 36.7748 | [5 empty] | 21.8943 | 35.042 | 21.6671 | 22.0591 | 27.4863 | 21.216 | 21.8544 | 22.3922 | 46.0195 | 116.9603 |  | 37.4993 | 87.5947 | 20.5791 | 40.3089 | 90.8516 | 29.3235 | 72.9983 | 22.0423 | 68.612 | 22.0096 | 71.2281 | 18.5421 | 40.3795 | 82.0723 | 23.6536 | 40.5739 | 105.5339 | 20.5995 | 38.5879 | 91.4304 | 20.6195 | 65.3457 | 24.573 | 73.724 | 22.2386 | 73.3088 | 0.40389 | 19.7625 | 0.85428 | 0.02628 | -27.1007 | 3.0953 | 53.08 | 51.66 | 1.3148 | -0.5309 | -6.2439 | 0.79501 | 0.68629 | -16.7326 | 5.0374 | 0.24328 | -0.26126 | 0.18863 | -1.022 | -0.12311 | -0.036598 | 0.21264
42838.4233 | 260 | 22.9145 | 22.8723 | 22.8628 | 22.7857 | 22.3997 | 21.736 | 22.7154 | 21.781 | 22.365 | 22.3746 | 22.3414 | 21.9972 | 21.2062 | 22.1803 | 21.6268 | 21.7925 | 21.9104 | 21.0979 | 21.1981 | 21.4193 | 20.4893 | 20.7079 | 21.6533 | 21.879 | 21.6705 | 23.4213 | 99.8037 | 89.4453 | 102.9216 | 22.131 | 21.7298 | 22.5864 | 22.0176 | 21.7793 | 23.1605 | 35.3156 | 98.0457 |  | 54.3053 | 81.3576 | 83.6493 | 54.7767 |  | 17.0179 | 17.2741 | 16.7556 | 17.2524 | 17.5832 | 19.5651 | 50.082 | 16.0376 | 17.0913 | 16.129 | 17.6906 | 18.2157 | 44.4427 | 48.0621 | 43.6262 | 21.6333 |  |  | 0.62252 | -0.31417 | -27.5274 | 0.29631 | 0.33526 | -195.7997 | 18.044 | 0.37157 | 0.042127 | 0.22187 | 0.15184 | 0.00035649 | 0.00034827 | 1.7701 | 21.77 | 21.9893 | 22.1853 | 22.2363 | 22.0516 | 21.3525 | 20.158 | 22.1981 | 22.3638 | 22.4073 | 22.352 | 21.9714 | 21.2069 | 22.2857 | 47.0994 | 29.6734 | 31.8545 | 23.7522 | 21.2923 | 32.9635 | 24.5644 | 22.3333 | 22.108 | 21.6726 | 22.0609 | 21.7768 | 21.2908 | 21.9397 | 21.5687 | 21.7801 | 34.6355 | 100.8321 | 77.6938 | 45.3089 | 0.52572 | 0.01772 | 40.5775 | 21.9692 | 22.2894 | 20.1945 | 21.61 | 22.0515 | 21.9214 | 21.7454 | 24.6416 | 21.7767 | 21.4758 | 22.2714 | 93.0144 | 112.7074 | 73.074 | 73.8621 | 44.2169 |  | 34.493 | 64.9485 | 36.8697 | 47.3338 | 35.5673 | 40.6045 |  | 46.4996 |  |  | 21.2982 | 22.5489 | 36.9929 | [5 empty] | 21.8975 | 35.1162 | 21.6638 | 22.0565 | 27.5351 | 21.2211 | 21.8534 | 22.4215 | 46.0898 | 117.2176 |  | 37.5112 | 87.6919 | 20.6013 | 40.3368 | 90.8475 | 29.3864 | 73.1285 | 22.0782 | 68.7352 | 22.0325 | 71.2936 | 18.5583 | 40.4986 | 82.3147 | 23.6869 | 40.7656 | 105.7222 | 20.6171 | 38.6165 | 91.5024 | 20.6279 | 65.4835 | 24.5998 | 73.9435 | 22.26 | 73.4413 | 0.33043 | 19.7617 | 0.85513 | 0.024146 | -27.0638 | 3.0953 | 48.45 | 51.8 | 1.0663 | -0.66567 | -6.2311 | 0.64649 | 0.69037 | -16.6838 | 5.0647 | 0.23778 | -0.2562 | 0.18818 | -1.0728 | -0.36459 | -0.02724 | 0.21235
42838.4233 | 261 | 22.9087 | 22.8721 | 22.8562 | 22.7802 | 22.3965 | 21.7305 | 22.7175 | 21.7769 | 22.3669 | 22.3678 | 22.3348 | 21.9956 | 21.1982 | 22.1696 | 21.6203 | 21.7906 | 21.9134 | 21.1008 | 21.1948 | 21.4184 | 20.4849 | 20.706 | 21.6572 | 21.8688 | 21.6657 | 23.4382 | 99.9467 | 89.5761 | 103.1993 | 22.1202 | 21.735 | 22.5954 | 22.0157 | 21.775 | 23.1763 | 35.3903 | 98.0483 |  | 54.417 | 81.5076 | 83.7078 | 54.289 |  | 17.0218 | 17.2789 | 16.756 | 17.2624 | 17.5777 | 19.5759 | 49.9571 | 16.0484 | 17.0914 | 16.1592 | 17.6898 | 18.2148 | 44.4632 | 48.1266 | 43.6305 | 21.6237 |  |  | 0.54695 | -0.46136 | -26.9623 | 0.36071 | 0.24721 | -194.8817 | 18.1242 | 0.18758 | 0.23439 | 0.13061 | -0.016374 | 0.00034663 | 0.00034334 | 1.7743 | 21.7649 | 21.9778 | 22.1734 | 22.2356 | 22.0528 | 21.3474 | 20.1599 | 22.2007 | 22.356 | 22.4031 | 22.356 | 21.9641 | 21.2005 | 22.2806 | 47.5175 | 30.1134 | 33.6363 | 23.9664 | 21.8207 | 33.0509 | 24.6066 | 22.3366 | 22.1075 | 21.6633 | 22.059 | 21.7722 | 21.2947 | 21.9454 | 21.5756 | 21.7938 | 34.7113 | 100.8528 | 77.831 | 45.4152 | 0.57762 | -0.004724 | 40.6868 | 21.9596 | 22.2816 | 20.1844 | 21.6048 | 22.0447 | 21.9127 | 21.748 | 24.6636 | 21.774 | 21.4632 | 22.28 | 93.2538 | 113.0582 | 73.2084 | 74 | 44.0602 |  | 34.5532 | 65.3633 | 36.9541 | 47.5814 | 35.6582 | 40.5775 |  | 46.6414 |  |  | 21.3172 | 22.5574 | 36.8598 | [5 empty] | 21.9018 | 35.2285 | 21.6705 | 22.0574 | 27.5765 | 21.225 | 21.8584 | 22.4257 | 46.2632 | 117.7889 |  | 37.5184 | 87.8679 | 20.5972 | 40.3692 | 90.9936 | 29.4499 | 73.2185 | 22.0913 | 68.8343 | 22.0299 | 71.3761 | 18.5412 | 40.6733 | 82.6927 | 23.6944 | 40.8975 | 105.9145 | 20.6149 | 38.6898 | 91.6626 | 20.625 | 65.5724 | 24.6036 | 74.0965 | 22.2613 | 73.5319 | 0.34453 | 19.7598 | 0.85495 | 0.024487 | -27.0255 | 3.0953 | 67.41 | 52.51 | 0.99985 | -0.80669 | -6.1669 | 0.71329 | 0.59283 | -16.645 | 5.0761 | 0.24421 | -0.26481 | 0.18443 | -1.109 | -0.55762 | -0.011121 | 0.21201
42838.4233 | 262 | 22.9126 | 22.8847 | 22.8662 | 22.7851 | 22.4028 | 21.7358 | 22.7219 | 21.7861 | 22.3708 | 22.3697 | 22.3512 | 21.9965 | 21.2004 | 22.1807 | 21.6297 | 21.7997 | 21.9228 | 21.1007 | 21.2047 | 21.4237 | 20.4891 | 20.7111 | 21.6709 | 21.8794 | 21.6766 | 23.4598 | 100.095 | 89.7284 | 103.4265 | 22.1242 | 21.7361 | 22.6135 | 22.0159 | 21.7749 | 23.1914 | 35.4708 | 97.9548 |  | 54.5506 | 81.6978 | 83.7763 | 53.9948 |  | 17.0181 | 17.2856 | 16.7589 | 17.2711 | 17.5902 | 19.5867 | 49.743 | 16.0558 | 17.0971 | 16.0771 | 17.6921 | 18.2182 | 44.486 | 48.2192 | 43.6458 | 21.6307 |  |  | 0.8098 | -0.56781 | -26.9426 | 0.56836 | 0.41872 | -194.5111 | 18.4902 | 0.34725 | 0.056917 | 0.16795 | 0.22267 | 0.00031706 | 0.00034006 | 1.7635 | 21.7572 | 21.9838 | 22.175 | 22.2436 | 22.0552 | 21.3394 | 20.1571 | 22.1866 | 22.3615 | 22.395 | 22.3536 | 21.9659 | 21.2015 | 22.2765 | 48.0254 | 30.4365 | 35.698 | 24.3785 | 22.3143 | 33.1257 | 24.6635 | 22.3335 | 22.0918 | 21.6703 | 22.0634 | 21.7771 | 21.2892 | 21.9459 | 21.5763 | 21.8025 | 34.7812 | 100.841 | 78.2365 | 45.5578 | 0.41621 | 0.2045 | 40.6933 | 21.9627 | 22.2807 | 20.1967 | 21.6031 | 22.0406 | 21.9116 | 21.7579 | 24.6917 | 21.782 | 21.477 | 22.301 | 93.3871 | 113.4985 | 73.377 | 74.1569 | 43.9743 |  | 34.6394 | 65.8875 | 37.057 | 47.7211 | 35.7479 | 40.6453 |  | 46.7782 |  |  | 21.3317 | 22.5781 | 36.8492 | [5 empty] | 21.9013 | 35.378 | 21.6651 | 22.0488 | 27.6148 | 21.2128 | 21.8569 | 22.4525 | 46.4533 | 117.9545 |  | 37.5596 | 88.0385 | 20.611 | 40.4479 | 91.2823 | 29.4937 | 73.3246 | 22.0999 | 68.8926 | 22.0393 | 71.5598 | 18.5432 | 40.7468 | 82.9601 | 23.7211 | 40.9604 | 106.1242 | 20.6091 | 38.7763 | 91.8396 | 20.6325 | 65.6396 | 24.6166 | 74.1628 | 22.2728 | 73.6864 | 0.44247 | 19.7585 | 0.85491 | 0.023558 | -27.0846 | 3.0953 | 78.75 | 51.84 | 1.217 | -0.89494 | -6.1647 | 0.89537 | 0.77155 | -16.6294 | 5.1272 | 0.24956 | -0.27581 | 0.18364 | -1.1566 | -0.78004 | -0.00017814 | 0.21045
42838.4233 | 263 | 22.9137 | 22.8807 | 22.8584 | 22.7822 | 22.3964 | 21.7266 | 22.7203 | 21.7851 | 22.3629 | 22.3695 | 22.3449 | 21.9904 | 21.1954 | 22.1737 | 21.6211 | 21.7881 | 21.9106 | 21.0949 | 21.1842 | 21.4153 | 20.4799 | 20.7002 | 21.6772 | 21.8748 | 21.672 | 23.4688 | 100.3002 | 89.8476 | 103.6893 | 22.1322 | 21.7372 | 22.6233 | 22.0205 | 21.774 | 23.2014 | 35.5572 | 98.0009 |  | 54.6878 | 81.8839 | 83.8282 | 54.2579 |  | 17.0255 | 17.2902 | 16.755 | 17.258 | 17.6032 | 19.5461 | 49.2571 | 16.0505 | 17.0871 | 15.9651 | 17.7022 | 18.2146 | 44.4986 | 48.2932 | 43.6571 | 21.6335 |  |  | 0.72634 | -0.25831 | -27.1081 | 0.14978 | 0.48246 | -194.9474 | 18.4041 | 0.36302 | 0.1044 | -0.044157 | 0.22614 | 0.00034992 | 0.00032527 | 1.7515 | 21.7591 | 21.9778 | 22.1784 | 22.2364 | 22.0529 | 21.3426 | 20.1604 | 22.1867 | 22.3663 | 22.3952 | 22.3469 | 21.9687 | 21.1996 | 22.2718 | 48.3304 | 31.5816 | 37.1146 | 25.7509 | 22.7509 | 33.2111 | 24.7305 | 22.3333 | 22.0979 | 21.659 | 22.0619 | 21.7745 | 21.2928 | 21.9378 | 21.568 | 21.8046 | 34.8683 | 100.6055 | 78.3472 | 45.559 | 0.33207 | -0.054937 | 40.5833 | 21.9513 | 22.278 | 20.1899 | 21.5926 | 22.0468 | 21.9077 | 21.7479 | 24.7105 | 21.767 | 21.4642 | 22.3029 | 93.483 | 113.725 | 73.5295 | 74.325 | 44.4299 |  | 34.7406 | 66.3371 | 37.1476 | 48.1463 | 35.8412 | 40.4915 |  | 46.9058 |  |  | 21.3472 | 22.6175 | 37.2146 | [5 empty] | 21.906 | 35.5201 | 21.6697 | 22.0617 | 27.6366 | 21.2221 | 21.8635 | 22.4714 | 46.5956 | 118.6826 |  | 37.6316 | 88.2709 | 20.6207 | 40.5159 | 91.5539 | 29.5332 | 73.3944 | 22.1322 | 68.9444 | 22.0414 | 71.6586 | 18.5578 | 40.7848 | 83.1748 | 23.7514 | 41.0195 | 106.2279 | 20.6157 | 38.8547 | 92.0707 | 20.6487 | 65.6885 | 24.6481 | 74.2798 | 22.2838 | 73.7698 | 0.58493 | 19.7587 | 0.85605 | 0.023652 | -27.1217 | 3.0953 | 86.41 | 52.51 | 1.153 | -0.60363 | -6.1837 | 0.45964 | 0.82814 | -16.6469 | 5.1148 | 0.24038 | -0.28517 | 0.17504 | -1.1804 | -0.92958 | -0.0045065 | 0.21341
42838.4233 | 264 | 22.9123 | 22.875 | 22.8593 | 22.7786 | 22.3965 | 21.7258 | 22.7215 | 21.7868 | 22.3617 | 22.3722 | 22.3405 | 21.9965 | 21.2028 | 22.1701 | 21.624 | 21.7866 | 21.9135 | 21.0966 | 21.1878 | 21.4216 | 20.4827 | 20.716 | 21.6879 | 21.878 | 21.6688 | 23.4918 | 100.3969 | 89.996 | 103.7278 | 22.1327 | 21.7362 | 22.6333 | 22.0191 | 21.7785 | 23.2135 | 35.6441 | 97.9117 |  | 54.833 | 82.0491 | 83.9048 | 54.9713 |  | 17.0225 | 17.2982 | 16.7598 | 17.2612 | 17.6163 | 19.5345 | 48.9834 | 16.0583 | 17.0866 | 15.902 | 17.7022 | 18.222 | 44.5136 | 48.383 | 43.6681 | 21.641 |  |  | 0.67443 | -0.36082 | -26.9715 | 0.42511 | 0.29715 | -193.9986 | 18.32 | -0.008904 | -0.018199 | 0.17613 | 0.12025 | 0.00035484 | 0.00035977 | 1.7665 | 21.7671 | 21.9817 | 22.1766 | 22.2345 | 22.0532 | 21.3493 | 20.1602 | 22.1957 | 22.356 | 22.3982 | 22.354 | 21.968 | 21.2034 | 22.2798 | 48.158 | 30.9371 | 37.2524 | 26.1689 | 23.1097 | 33.2841 | 24.802 | 22.3379 | 22.106 | 21.672 | 22.0615 | 21.7743 | 21.2964 | 21.947 | 21.5698 | 21.8239 | 34.9457 | 100.488 | 78.3224 | 45.6981 | 0.45318 | -0.13197 | 40.7545 | 21.9597 | 22.2821 | 20.18 | 21.5998 | 22.0418 | 21.9106 | 21.7501 | 24.74 | 21.7677 | 21.4673 | 22.3115 | 93.6482 | 114.0651 | 73.6701 | 74.4844 | 44.8342 |  | 34.8111 | 66.5674 | 37.2093 | 48.4976 | 35.9249 | 40.5343 |  | 47.0086 |  |  | 21.3474 | 22.6348 | 37.7711 | [5 empty] | 21.8942 | 35.6616 | 21.6641 | 22.0515 | 27.6304 | 21.2141 | 21.8577 | 22.4862 | 46.6895 | 118.972 |  | 37.7531 | 88.434 | 20.6308 | 40.5617 | 91.902 | 29.5998 | 73.477 | 22.1517 | 69.0748 | 22.0519 | 71.7422 | 18.5629 | 40.8588 | 83.2618 | 23.7714 | 41.1746 | 106.2833 | 20.6177 | 38.8879 | 92.254 | 20.6525 | 65.7373 | 24.6897 | 74.5848 | 22.3025 | 73.7735 | 0.36048 | 19.7563 | 0.85844 | 0.023943 | -27.1254 | 3.0953 | 81.62 | 51.54 | 1.1111 | -0.71342 | -6.1681 | 0.77438 | 0.64991 | -16.606 | 5.103 | 0.23158 | -0.28944 | 0.16817 | -1.1527 | -0.93653 | -0.021331 | 0.21221
42838.4233 | 265 | 22.905 | 22.875 | 22.8623 | 22.7801 | 22.3927 | 21.7291 | 22.7169 | 21.7832 | 22.3675 | 22.3674 | 22.3281 | 21.9916 | 21.2063 | 22.1677 | 21.6264 | 21.7891 | 21.9112 | 21.1024 | 21.195 | 21.417 | 20.4874 | 20.714 | 21.6925 | 21.8752 | 21.6631 | 23.5073 | 100.4727 | 90.0866 | 104.4786 | 22.1334 | 21.742 | 22.6521 | 22.022 | 21.7815 | 23.2406 | 35.7273 | 97.7894 |  | 54.975 | 82.1959 | 84.0842 | 55.2226 |  | 17.0161 | 17.301 | 16.7533 | 17.2515 | 17.6147 | 19.5311 | 48.982 | 15.9509 | 17.093 | 15.928 | 17.7058 | 18.2201 | 44.534 | 48.4588 | 43.6824 | 21.6466 |  |  | 0.74671 | -0.28591 | -27.208 | 0.61567 | 0.42857 | -193.8915 | 18.2878 | 0.4629 | -0.061011 | 0.10438 | 0.29593 | 0.00036963 | 0.00034334 | 1.766 | 21.7681 | 21.9852 | 22.1768 | 22.2401 | 22.0491 | 21.3517 | 20.1635 | 22.194 | 22.3625 | 22.3973 | 22.3531 | 21.9651 | 21.1992 | 22.2815 | 48.4952 | 30.6379 | 36.3327 | 26.2113 | 23.4568 | 33.3556 | 24.8507 | 22.3358 | 22.099 | 21.6682 | 22.0637 | 21.7736 | 21.2905 | 21.943 | 21.5667 | 21.8325 | 35.0113 | 100.3989 | 78.2829 | 46.0293 | 0.46418 | 0.056711 | 40.9569 | 21.9559 | 22.2792 | 20.191 | 21.5942 | 22.0457 | 21.9101 | 21.7399 | 24.7683 | 21.7715 | 21.462 | 22.3168 | 93.9039 | 114.2635 | 73.8351 | 74.6664 | 44.6366 |  | 34.8978 | 66.3389 | 37.303 | 48.9159 | 36.0594 | 40.5903 |  | 47.1291 |  |  | 21.359 | 22.6387 | 37.7946 | [5 empty] | 21.8884 | 35.8098 | 21.6686 | 22.0506 | 27.6353 | 21.2203 | 21.8541 | 22.5065 | 46.7923 | 119.7342 |  | 37.9208 | 88.5099 | 20.6411 | 40.6114 | 92.2182 | 29.66 | 73.5811 | 22.1675 | 69.295 | 22.0621 | 71.8727 | 18.5676 | 41.0181 | 83.2979 | 23.7943 | 41.3561 | 106.3242 | 20.6184 | 38.9634 | 92.4577 | 20.6559 | 65.8638 | 24.7286 | 74.9459 | 22.3167 | 73.8664 | 0.48031 | 19.7575 | 0.86022 | 0.025366 | -27.0486 | 3.0953 | 94.76 | 52.2 | 1.1702 | -0.63506 | -6.1952 | 0.93192 | 0.78051 | -16.6014 | 5.0985 | 0.24005 | -0.27985 | 0.16119 | -1.1817 | -0.82863 | -0.025447 | 0.20527
42838.4234 | 266 | 22.9076 | 22.8704 | 22.8634 | 22.7794 | 22.4002 | 21.7265 | 22.7123 | 21.7806 | 22.3691 | 22.3723 | 22.3326 | 21.9942 | 21.2065 | 22.1733 | 21.6266 | 21.7889 | 21.9054 | 21.0983 | 21.1926 | 21.4157 | 20.4823 | 20.7106 | 21.6982 | 21.8735 | 21.6702 | 23.5186 | 100.6292 | 90.1393 | 105.3616 | 22.1242 | 21.7376 | 22.6516 | 22.0237 | 21.7807 | 23.248 | 35.8024 | 98.3337 |  | 55.106 | 82.3298 | 84.2686 | 54.8883 |  | 17.0141 | 17.301 | 16.746 | 17.2453 | 17.5972 | 19.5453 | 48.6528 | 15.823 | 17.0974 | 15.8936 | 17.7072 | 18.2184 | 44.5621 | 48.5388 | 43.6878 | 21.641 |  |  | 0.63895 | -0.303 | -27.4604 | 0.3594 | 0.48574 | -193.8783 | 18.4718 | 0.38602 | 0.035705 | -0.044996 | 0.19472 | 0.00034334 | 0.00037784 | 1.7297 | 21.771 | 21.9842 | 22.1817 | 22.2373 | 22.0502 | 21.3511 | 20.1673 | 22.1955 | 22.3657 | 22.3995 | 22.3589 | 21.9761 | 21.2006 | 22.2836 | 48.4734 | 30.5741 | 36.4763 | 26.6196 | 23.4379 | 33.4225 | 24.9027 | 22.3373 | 22.0974 | 21.6766 | 22.0651 | 21.7843 | 21.3031 | 21.9399 | 21.5747 | 21.8448 | 35.0798 | 100.5315 | 78.4646 | 46.3012 | 0.35153 | -0.02926 | 41.1845 | 21.9505 | 22.2759 | 20.184 | 21.598 | 22.0494 | 21.9122 | 21.7535 | 24.7894 | 21.772 | 21.4676 | 22.332 | 94.1151 | 114.472 | 73.9803 | 74.8228 | 44.266 |  | 34.9752 | 66.34 | 37.3955 | 48.7081 | 36.1477 | 40.8321 |  | 47.229 |  |  | 21.3768 | 22.662 | 37.8289 | [5 empty] | 21.8924 | 35.8888 | 21.6742 | 22.0587 | 27.6838 | 21.2189 | 21.8508 | 22.533 | 46.8838 | 120.556 |  | 38.12 | 88.7083 | 20.6551 | 40.68 | 92.5511 | 29.7247 | 73.6967 | 22.1878 | 69.4996 | 22.0691 | 72.0632 | 18.5684 | 41.2994 | 83.377 | 23.8182 | 41.4835 | 106.4578 | 20.6357 | 39.1652 | 92.6474 | 20.6671 | 65.9641 | 24.7614 | 75.0589 | 22.3343 | 74.0661 | 0.3781 | 19.7566 | 0.86222 | 0.026505 | -27.1077 | 3.0953 | 91.76 | 52.25 | 1.0838 | -0.65377 | -6.2238 | 0.71202 | 0.83095 | -16.6012 | 5.1242 | 0.25301 | -0.27668 | 0.17001 | -1.1715 | -0.83849 | -0.01357 | 0.20007
42838.4234 | 267 | 22.9156 | 22.879 | 22.8607 | 22.7856 | 22.4064 | 21.7307 | 22.7259 | 21.7909 | 22.3676 | 22.3784 | 22.3459 | 21.9931 | 21.2165 | 22.1755 | 21.6217 | 21.7868 | 21.9099 | 21.0886 | 21.1948 | 21.4122 | 20.479 | 20.704 | 21.7033 | 21.872 | 21.6664 | 23.5339 | 100.8435 | 90.183 | 106.0588 | 22.1267 | 21.7422 | 22.6675 | 22.0214 | 21.7823 | 23.2624 | 35.8773 | 100.5935 |  | 55.2762 | 82.4875 | 84.4406 | 54.5913 |  | 17.0241 | 17.2957 | 16.7409 | 17.2449 | 17.5997 | 19.5332 | 48.4113 | 15.7037 | 17.0945 | 15.8229 | 17.7103 | 18.2214 | 44.5808 | 48.6264 | 43.7007 | 21.6429 |  |  | 0.79008 | -0.28657 | -27.4466 | 0.44942 | 0.445 | -194.724 | 18.1137 | 0.44648 | -0.020729 | 0.14508 | 0.098028 | 0.00035649 | 0.00032856 | 1.7086 | 21.7793 | 21.9871 | 22.1848 | 22.2396 | 22.045 | 21.3558 | 20.1684 | 22.1929 | 22.3652 | 22.3957 | 22.354 | 21.9693 | 21.2031 | 22.2785 | 47.8568 | 30.8662 | 35.2154 | 26.2624 | 23.8003 | 33.4759 | 24.9355 | 22.3433 | 22.1118 | 21.6696 | 22.0724 | 21.7793 | 21.2933 | 21.9458 | 21.576 | 21.8568 | 35.1594 | 100.6615 | 78.6799 | 46.5772 | 0.13193 | -0.10192 | 41.4943 | 21.9605 | 22.2833 | 20.2035 | 21.5971 | 22.0509 | 21.9093 | 21.763 | 24.826 | 21.7719 | 21.4715 | 22.3505 | 94.3566 | 114.965 | 74.1019 | 74.9891 | 44.1656 |  | 35.0375 | 66.607 | 37.4931 | 48.4565 | 36.2275 | 41.1839 |  | 47.3306 |  |  | 21.4023 | 22.6836 | 37.9623 | [5 empty] | 21.8956 | 35.8791 | 21.6774 | 22.0607 | 27.7353 | 21.2222 | 21.8589 | 22.5637 | 47.0224 | 120.7999 |  | 38.4147 | 88.96 | 20.6774 | 40.7475 | 92.8736 | 29.8085 | 73.8389 | 22.2123 | 69.6504 | 22.0821 | 72.1903 | 18.5599 | 41.5659 | 83.4033 | 23.8514 | 41.5119 | 106.5411 | 20.6514 | 39.4067 | 92.7883 | 20.6852 | 66.0197 | 24.7972 | 75.091 | 22.3521 | 74.2944 | 0.51222 | 19.7556 | 0.86408 | 0.027318 | -27.0993 | 3.0953 | 103.57 | 51.66 | 1.2063 | -0.63579 | -6.2222 | 0.79621 | 0.79533 | -16.637 | 5.0742 | 0.25794 | -0.28072 | 0.17975 | -1.0967 | -0.69455 | -0.0027395 | 0.19515
42838.4234 | 268 | 22.9186 | 22.8779 | 22.8604 | 22.787 | 22.3984 | 21.7294 | 22.7205 | 21.7881 | 22.3664 | 22.3702 | 22.3463 | 21.9929 | 21.2077 | 22.175 | 21.6271 | 21.7917 | 21.9142 | 21.0941 | 21.196 | 21.4143 | 20.4839 | 20.7094 | 21.7185 | 21.8755 | 21.6688 | 23.5559 | 101.1431 | 90.2395 | 106.8205 | 22.1279 | 21.7426 | 22.688 | 22.0248 | 21.7902 | 23.2804 | 35.9386 | 101.3654 |  | 55.4717 | 82.659 | 84.6324 | 54.5648 |  | 17.0195 | 17.2962 | 16.7488 | 17.2445 | 17.5943 | 19.5011 | 48.6062 | 15.6358 | 17.0921 | 15.7242 | 17.7084 | 18.2177 | 44.5874 | 48.7038 | 43.714 | 21.6356 |  |  | 0.66195 | -0.31745 | -27.1627 | 0.29369 | 0.53962 | -194.4362 | 18.0854 | 0.83943 | 0.16395 | 0.11823 | 0.10775 | 0.00036306 | 0.0003647 | 1.7085 | 21.7647 | 21.9799 | 22.1675 | 22.2282 | 22.0311 | 21.3363 | 20.1558 | 22.1805 | 22.356 | 22.393 | 22.3369 | 21.9594 | 21.1921 | 22.2716 | 46.9525 | 29.8157 | 34.2446 | 25.764 | 23.3238 | 33.5238 | 24.9798 | 22.3276 | 22.0998 | 21.6662 | 22.0656 | 21.7754 | 21.2954 | 21.9371 | 21.5649 | 21.8565 | 35.2194 | 100.8785 | 78.8801 | 46.9764 | 0.54774 | -0.12132 | 41.637 | 21.9549 | 22.2868 | 20.2037 | 21.5986 | 22.0532 | 21.9175 | 21.7658 | 24.8452 | 21.7757 | 21.4782 | 22.371 | 94.6433 | 115.5411 | 74.2652 | 75.1888 | 44.825 |  | 35.1467 | 66.458 | 37.5989 | 48.5501 | 36.3282 | 41.1203 |  | 47.4532 |  |  | 21.4187 | 22.6971 | 38.0901 | [5 empty] | 21.8961 | 35.8233 | 21.6728 | 22.0596 | 27.7722 | 21.2204 | 21.8594 | 22.5827 | 47.2182 | 121.002 |  | 38.6507 | 89.1828 | 20.6834 | 40.8638 | 93.1277 | 29.8685 | 73.9802 | 22.236 | 69.7673 | 22.0939 | 72.2754 | 18.5566 | 41.7542 | 83.5364 | 23.8717 | 41.5847 | 106.6561 | 20.6506 | 39.581 | 93.0028 | 20.7001 | 66.0471 | 24.8315 | 75.2491 | 22.3586 | 74.4892 | 0.49256 | 19.7538 | 0.8653 | 0.02673 | -27.1151 | 3.0953 | 80 | 52.77 | 1.1052 | -0.66917 | -6.1899 | 0.64364 | 0.87577 | -16.6238 | 5.07 | 0.24338 | -0.27293 | 0.18062 | -0.99055 | -0.5815 | 0.00010875 | 0.18612
42838.4234 | 269 | 22.919 | 22.8798 | 22.86 | 22.78 | 22.3981 | 21.7254 | 22.7151 | 21.7875 | 22.3681 | 22.3661 | 22.341 | 21.9962 | 21.2047 | 22.1735 | 21.6288 | 21.7876 | 21.9209 | 21.0918 | 21.1981 | 21.4235 | 20.4829 | 20.7201 | 21.732 | 21.8826 | 21.6701 | 23.5832 | 101.3896 | 90.2696 | 107.1129 | 22.1233 | 21.7354 | 22.6941 | 22.0203 | 21.7863 | 23.2923 | 35.9988 | 102.0693 |  | 55.6516 | 82.8173 | 84.7599 | 54.873 |  | 17.0257 | 17.3102 | 16.7541 | 17.245 | 17.5893 | 19.5001 | 49.3674 | 15.6025 | 17.098 | 15.7138 | 17.7234 | 18.2312 | 44.5923 | 48.7933 | 43.7381 | 21.6393 |  |  | 0.52789 | -0.30037 | -27.2199 | 0.52171 | 0.36023 | -193.762 | 18.2727 | 0.61601 | 0.17543 | 0.11739 | 0.035185 | 0.00032199 | 0.00036306 | 1.7261 | 21.764 | 21.9807 | 22.1704 | 22.2319 | 22.0339 | 21.3412 | 20.1509 | 22.1786 | 22.3555 | 22.3995 | 22.3447 | 21.9621 | 21.187 | 22.2713 | 47.5841 | 29.6842 | 32.7019 | 25.2554 | 23.0575 | 33.5999 | 25.0021 | 22.3316 | 22.105 | 21.6714 | 22.0665 | 21.7752 | 21.3026 | 21.9374 | 21.5742 | 21.8706 | 35.3039 | 101.0658 | 79.018 | 47.2387 | 0.48502 | -0.060643 | 41.6766 | 21.955 | 22.2903 | 20.2014 | 21.6098 | 22.0537 | 21.9245 | 21.7654 | 24.8759 | 21.7803 | 21.4834 | 22.3736 | 94.843 | 116.0236 | 74.4326 | 75.3839 | 45.466 |  | 35.234 | 66.3501 | 37.6888 | 48.3539 | 36.4118 | 40.9231 |  | 47.5615 |  |  | 21.436 | 22.7065 | 38.1623 | [5 empty] | 21.897 | 35.7516 | 21.6689 | 22.0575 | 27.8081 | 21.2172 | 21.857 | 22.6039 | 47.3679 | 121.1671 |  | 38.7385 | 89.4367 | 20.6843 | 41.0512 | 93.4297 | 29.9307 | 74.1081 | 22.2549 | 69.8895 | 22.1088 | 72.3626 | 18.5496 | 42.0654 | 83.8218 | 23.8992 | 41.7335 | 106.814 | 20.6625 | 39.7131 | 93.2209 | 20.7089 | 66.117 | 24.873 | 75.5063 | 22.3722 | 74.5867 | 0.62166 | 19.7552 | 0.86679 | 0.026658 | -27.1265 | 3.0954 | 88.92 | 51.54 | 0.98738 | -0.65094 | -6.1966 | 0.85787 | 0.71554 | -16.5949 | 5.0962 | 0.22858 | -0.26682 | 0.18896 | -1.0518 | -0.40747 | -0.0063724 | 0.18175
42838.4234 | 270 | 22.9251 | 22.8813 | 22.873 | 22.7926 | 22.405 | 21.7354 | 22.724 | 21.791 | 22.3762 | 22.3749 | 22.3515 | 22.0025 | 21.2128 | 22.1829 | 21.6213 | 21.7917 | 21.9146 | 21.0901 | 21.1924 | 21.4158 | 20.4886 | 20.7233 | 21.7384 | 21.8766 | 21.6725 | 23.6015 | 101.5599 | 90.3418 | 107.0431 | 22.1279 | 21.7412 | 22.7065 | 22.022 | 21.792 | 23.3118 | 36.0978 | 102.2608 |  | 55.8136 | 83.0205 | 84.8668 | 55.4096 |  | 17.0236 | 17.3136 | 16.7496 | 17.2415 | 17.5923 | 19.5749 | 49.8311 | 15.5673 | 17.093 | 15.7103 | 17.7252 | 18.2274 | 44.5807 | 48.8799 | 43.7545 | 21.6356 |  |  | 0.71977 | -0.26488 | -27.2277 | 0.3456 | 0.3024 | -193.9835 | 18.1018 | 0.365 | 0.14215 | 0.040812 | 0.047163 | 0.00035813 | 0.00035649 | 1.7377 | 21.7675 | 21.9809 | 22.1757 | 22.2291 | 22.0453 | 21.3451 | 20.1551 | 22.1864 | 22.3677 | 22.4049 | 22.3534 | 21.9752 | 21.1966 | 22.2761 | 47.8912 | 30.8126 | 34.838 | 25.4583 | 22.6689 | 33.6823 | 25.0504 | 22.3235 | 22.0981 | 21.6624 | 22.0554 | 21.7749 | 21.2903 | 21.9351 | 21.568 | 21.8748 | 35.3849 | 101.4552 | 79.1495 | 47.045 | 0.40717 | 0.18015 | 41.666 | 21.9598 | 22.28 | 20.2105 | 21.6056 | 22.0557 | 21.9171 | 21.7691 | 24.9051 | 21.7825 | 21.4815 | 22.3838 | 95.0752 | 116.4948 | 74.6393 | 75.5572 | 45.8008 |  | 35.3135 | 66.5899 | 37.7795 | 48.2619 | 36.4988 | 41.0621 |  | 47.664 |  |  | 21.4402 | 22.7289 | 38.1668 | [5 empty] | 21.891 | 35.7798 | 21.668 | 22.0552 | 27.846 | 21.2086 | 21.8518 | 22.6186 | 47.4622 | 121.2765 |  | 38.7928 | 89.6276 | 20.6976 | 41.2436 | 93.6955 | 30.0041 | 74.2094 | 22.2662 | 70.1309 | 22.1216 | 72.4719 | 18.5428 | 42.3646 | 84.1424 | 23.9241 | 41.8915 | 107.022 | 20.676 | 39.8114 | 93.3593 | 20.7126 | 66.1981 | 24.9085 | 75.644 | 22.3847 | 74.6121 | 0.31522 | 19.7518 | 0.86871 | 0.026309 | -27.1661 | 3.0953 | 80.09 | 52.12 | 1.1528 | -0.61128 | -6.1975 | 0.69823 | 0.65568 | -16.6065 | 5.0729 | 0.22202 | -0.27035 | 0.19451 | -1.0762 | -0.63917 | -0.017865 | 0.18992
42838.4234 | 271 | 22.9173 | 22.8634 | 22.8569 | 22.7788 | 22.3861 | 21.7211 | 22.7114 | 21.7794 | 22.3577 | 22.3588 | 22.3443 | 21.9824 | 21.2054 | 22.17 | 21.6262 | 21.7887 | 21.9103 | 21.0978 | 21.2001 | 21.424 | 20.4887 | 20.7119 | 21.7393 | 21.8745 | 21.6722 | 23.6147 | 101.708 | 90.4746 | 107.2706 | 22.1241 | 21.7416 | 22.7188 | 22.0239 | 21.7906 | 23.3264 | 36.1821 | 101.587 |  | 55.9555 | 83.2379 | 84.9719 | 55.4676 |  | 17.0091 | 17.3018 | 16.7514 | 17.2415 | 17.5798 | 19.552 | 50.1985 | 15.5583 | 17.0798 | 15.7205 | 17.7241 | 18.2328 | 44.5895 | 48.9651 | 43.7715 | 21.6412 |  |  | 0.63041 | -0.17815 | -27.0017 | 0.51645 | 0.24589 | -193.6385 | 18.4008 | 0.38077 | 0.021694 | 0.076059 | 0.00602 | 0.00037127 | 0.00034499 | 1.7362 | 21.7693 | 21.9811 | 22.1799 | 22.23 | 22.0452 | 21.3467 | 20.1551 | 22.1828 | 22.3624 | 22.4051 | 22.3487 | 21.9706 | 21.193 | 22.2709 | 48.2339 | 31.8559 | 37.8117 | 26.5845 | 22.7885 | 33.7586 | 25.1163 | 22.336 | 22.0995 | 21.6645 | 22.0568 | 21.7766 | 21.2941 | 21.9381 | 21.5778 | 21.8865 | 35.464 | 101.7367 | 79.1888 | 47.0434 | 0.29255 | 0.044157 | 41.888 | 21.9651 | 22.2904 | 20.2072 | 21.6141 | 22.0507 | 21.9276 | 21.7745 | 24.9248 | 21.7833 | 21.4857 | 22.402 | 95.2268 | 116.8046 | 74.8668 | 75.7712 | 45.8268 |  | 35.3994 | 66.5708 | 37.8738 | 48.5002 | 36.5874 | 41.1279 |  | 47.769 |  |  | 21.4447 | 22.7548 | 38.2306 | [5 empty] | 21.8983 | 35.8889 | 21.6717 | 22.06 | 27.8999 | 21.2185 | 21.8616 | 22.6439 | 47.5353 | 121.3459 |  | 38.999 | 89.8136 | 20.7013 | 41.341 | 93.9041 | 30.0605 | 74.2951 | 22.2743 | 70.467 | 22.1298 | 72.5801 | 18.5534 | 42.5851 | 84.5166 | 23.9448 | 42.0007 | 107.1988 | 20.6913 | 39.8779 | 93.4957 | 20.7122 | 66.281 | 24.9329 | 75.7578 | 22.4017 | 74.6328 | 0.61053 | 19.7498 | 0.87027 | 0.026244 | -27.0672 | 3.0953 | 63.73 | 52.49 | 1.0792 | -0.50129 | -6.1716 | 0.85353 | 0.59122 | -16.5911 | 5.1144 | 0.22425 | -0.26655 | 0.19095 | -1.1053 | -0.96186 | -0.01657 | 0.19269
42838.4234 | 272 | 22.9191 | 22.8748 | 22.8629 | 22.7815 | 22.4046 | 21.7297 | 22.7215 | 21.7808 | 22.3632 | 22.3643 | 22.3419 | 21.9911 | 21.2025 | 22.1727 | 21.6326 | 21.7859 | 21.9169 | 21.0936 | 21.1931 | 21.421 | 20.4886 | 20.7101 | 21.7476 | 21.8735 | 21.6727 | 23.6268 | 101.8531 | 90.6661 | 107.2245 | 22.1297 | 21.7406 | 22.736 | 22.0166 | 21.7843 | 23.3395 | 36.2615 | 100.9007 |  | 56.1105 | 83.4164 | 85.1402 | 55.1341 |  | 17.02 | 17.2995 | 16.7505 | 17.2389 | 17.5754 | 19.5136 | 50.4006 | 15.5293 | 17.086 | 15.7361 | 17.7255 | 18.2297 | 44.602 | 49.0413 | 43.7919 | 21.6396 |  |  | 0.66326 | -0.2846 | -26.8256 | 0.19446 | 0.36089 | -192.8999 | 18.5684 | 0.43728 | 0.21902 | 0.077318 | 0.19576 | 0.00033513 | 0.0003647 | 1.7311 | 21.7665 | 21.9815 | 22.1741 | 22.2348 | 22.0562 | 21.3471 | 20.1607 | 22.1885 | 22.3651 | 22.4069 | 22.3515 | 21.97 | 21.1989 | 22.2792 | 47.6249 | 31.8936 | 37.6416 | 26.9464 | 22.8854 | 33.8243 | 25.1756 | 22.3306 | 22.0987 | 21.6675 | 22.0575 | 21.7788 | 21.2937 | 21.9345 | 21.5643 | 21.8942 | 35.5435 | 101.9441 | 79.2567 | 47.1667 | 0.74021 | -0.023554 | 41.9386 | 21.9636 | 22.2916 | 20.2125 | 21.603 | 22.0521 | 21.9241 | 21.7761 | 24.9531 | 21.7777 | 21.4801 | 22.4179 | 95.5162 | 117.1785 | 75.0641 | 75.9581 | 45.7768 |  | 35.4835 | 66.5009 | 37.9684 | 48.8364 | 36.6814 | 41.214 |  | 47.8796 |  |  | 21.4506 | 22.7658 | 38.0711 | [5 empty] | 21.8997 | 36.0408 | 21.6671 | 22.0625 | 27.9375 | 21.2189 | 21.8588 | 22.6589 | 47.6255 | 121.6129 |  | 39.4082 | 90.1957 | 20.7117 | 41.4324 | 94.0894 | 30.135 | 74.4065 | 22.2832 | 70.7342 | 22.1398 | 72.6814 | 18.5538 | 42.6807 | 84.911 | 23.9685 | 42.0763 | 107.4504 | 20.6974 | 40.0187 | 93.5293 | 20.7086 | 66.3776 | 24.9567 | 76.0666 | 22.4066 | 74.7351 | 0.55563 | 19.7485 | 0.8711 | 0.025489 | -27.0785 | 3.0953 | 88.44 | 51.54 | 1.1069 | -0.6336 | -6.1514 | 0.52374 | 0.71621 | -16.5584 | 5.1373 | 0.22854 | -0.26133 | 0.18486 | -1.0299 | -0.93601 | -0.0045669 | 0.192
42838.4234 | 273 | 22.9169 | 22.8803 | 22.8675 | 22.783 | 22.3973 | 21.7328 | 22.724 | 21.7842 | 22.3679 | 22.3659 | 22.3421 | 21.9932 | 21.2084 | 22.1772 | 21.6364 | 21.793 | 21.9154 | 21.0992 | 21.1987 | 21.4225 | 20.4866 | 20.7128 | 21.7661 | 21.8806 | 21.6762 | 23.6516 | 102.0502 | 90.8335 | 107.905 | 22.1354 | 21.7428 | 22.7486 | 22.0229 | 21.7866 | 23.3573 | 36.329 | 101.0515 |  | 56.2387 | 83.5894 | 85.3701 | 55.3381 |  | 17.0229 | 17.2965 | 16.7515 | 17.2293 | 17.5595 | 19.4695 | 50.7322 | 15.4563 | 17.0869 | 15.6806 | 17.735 | 18.2287 | 44.6146 | 49.129 | 43.8168 | 21.6409 |  |  | 0.68363 | -0.35622 | -26.5404 | 0.21155 | 0.35103 | -192.8466 | 18.6223 | 0.47145 | -0.07833 | 0.15557 | 0.15341 | 0.00034499 | 0.00032363 | 1.7105 | 21.7594 | 21.9803 | 22.1742 | 22.2284 | 22.0466 | 21.3434 | 20.1544 | 22.1803 | 22.3612 | 22.3926 | 22.3442 | 21.9679 | 21.1968 | 22.2768 | 47.8904 | 31.714 | 36.9195 | 26.613 | 22.9326 | 33.8943 | 25.2134 | 22.3331 | 22.1099 | 21.6645 | 22.0664 | 21.7817 | 21.2946 | 21.943 | 21.5685 | 21.9136 | 35.6382 | 102.4246 | 79.3923 | 47.1507 | 0.58608 | 0.062226 | 42.0218 | 21.9706 | 22.2886 | 20.2104 | 21.6014 | 22.0499 | 21.9224 | 21.7786 | 24.9776 | 21.7737 | 21.4776 | 22.4286 | 95.825 | 117.3449 | 75.2485 | 76.1188 | 45.8427 |  | 35.5642 | 66.6207 | 38.0437 | 48.9209 | 36.775 | 41.5274 |  | 48.0036 |  |  | 21.4633 | 22.7731 | 38.0126 | [5 empty] | 21.892 | 36.2865 | 21.6753 | 22.0523 | 27.9743 | 21.219 | 21.8643 | 22.6823 | 47.7276 | 122.156 |  | 39.871 | 90.609 | 20.731 | 41.7355 | 94.246 | 30.2298 | 74.5368 | 22.2901 | 70.8872 | 22.1675 | 72.7988 | 18.5625 | 42.6758 | 85.2245 | 23.9892 | 42.1933 | 107.6004 | 20.7132 | 40.2315 | 93.6174 | 20.7062 | 66.4826 | 24.974 | 76.2966 | 22.4208 | 74.915 | 0.50665 | 19.7473 | 0.87212 | 0.024335 | -27.0681 | 3.0953 | 84.12 | 52.87 | 1.1248 | -0.70886 | -6.1186 | 0.54626 | 0.7063 | -16.5548 | 5.1444 | 0.22949 | -0.26206 | 0.18575 | -1.0512 | -0.85135 | -0.0079081 | 0.1957
42838.4234 | 274 | 22.9238 | 22.8831 | 22.8645 | 22.7815 | 22.3966 | 21.7299 | 22.7198 | 21.7863 | 22.3688 | 22.3734 | 22.3462 | 21.9928 | 21.199 | 22.1813 | 21.6284 | 21.7943 | 21.9198 | 21.0982 | 21.1965 | 21.4314 | 20.4879 | 20.7192 | 21.7772 | 21.8812 | 21.6815 | 23.6758 | 102.2053 | 91.0329 | 107.9838 | 22.1371 | 21.7441 | 22.7607 | 22.0256 | 21.7909 | 23.3674 | 36.4298 | 100.8833 |  | 56.3782 | 83.7014 | 85.5723 | 57.3486 |  | 17.0241 | 17.3029 | 16.7491 | 17.2262 | 17.5529 | 19.4421 | 50.9546 | 15.4011 | 17.0943 | 15.6561 | 17.7429 | 18.2253 | 44.637 | 49.2107 | 43.8327 | 21.6466 |  |  | 0.38267 | -0.50933 | -26.612 | 0.3732 | 0.32672 | -192.0594 | 18.6814 | 0.66267 | 0.11199 | 0.20383 | 0.19229 | 0.00033677 | 0.00035156 | 1.6982 | 21.754 | 21.9756 | 22.1733 | 22.2307 | 22.042 | 21.3419 | 20.1587 | 22.184 | 22.3578 | 22.3939 | 22.3474 | 21.965 | 21.1866 | 22.2774 | 48.4359 | 31.8191 | 36.7156 | 26.7825 | 22.9179 | 33.9863 | 25.2558 | 22.3343 | 22.104 | 21.6654 | 22.064 | 21.7759 | 21.2899 | 21.9388 | 21.5724 | 21.9189 | 35.7151 | 102.9709 | 79.6331 | 47.1632 | 0.24989 | -0.076239 | 42.0232 | 21.9545 | 22.279 | 20.2031 | 21.5949 | 22.0414 | 21.9226 | 21.7715 | 24.9962 | 21.7659 | 21.4654 | 22.4296 | 95.9899 | 117.6251 | 75.4306 | 76.3244 | 46.0625 |  | 35.6427 | 66.8202 | 38.112 | 49.2505 | 36.8752 | 41.6608 |  | 48.1162 |  |  | 21.4433 | 22.7833 | 38.0372 | [5 empty] | 21.9017 | 36.4384 | 21.6694 | 22.0596 | 28.0257 | 21.2242 | 21.8567 | 22.6857 | 47.8755 | 122.9768 |  | 40.1695 | 90.8046 | 20.7163 | 42.028 | 94.5407 | 30.294 | 74.6303 | 22.3009 | 71.0059 | 22.1763 | 72.9471 | 18.5677 | 42.7093 | 85.5419 | 24.0118 | 42.3074 | 107.6386 | 20.7202 | 40.4177 | 93.9522 | 20.7307 | 66.6896 | 24.9879 | 76.4817 | 22.4393 | 75.0808 | 0.45824 | 19.7448 | 0.87196 | 0.024654 | -27.0428 | 3.0952 | 70.41 | 51.07 | 0.84162 | -0.84763 | -6.1269 | 0.72556 | 0.68137 | -16.5202 | 5.1523 | 0.22609 | -0.26524 | 0.18005 | -1.101 | -0.82372 | -0.060273 | 0.19801
42838.4235 | 275 | 22.9292 | 22.8891 | 22.8689 | 22.7976 | 22.4042 | 21.7374 | 22.7229 | 21.792 | 22.3721 | 22.3864 | 22.3533 | 22.0073 | 21.2116 | 22.178 | 21.6277 | 21.7952 | 21.9147 | 21.1029 | 21.1952 | 21.4326 | 20.4838 | 20.7152 | 21.7852 | 21.8782 | 21.6761 | 23.6925 | 102.4767 | 91.1854 | 108.8418 | 22.1279 | 21.7431 | 22.7723 | 22.0253 | 21.7831 | 23.3856 | 36.5469 | 101.1778 |  | 56.4984 | 83.8199 | 85.7381 | 59.0389 |  | 17.0144 | 17.2988 | 16.743 | 17.2074 | 17.5388 | 19.4068 | 50.7511 | 15.3593 | 17.0881 | 15.6107 | 17.7419 | 18.2277 | 44.6583 | 49.2823 | 43.8525 | 21.6392 |  |  | 0.48781 | -0.32008 | -26.4379 | 0.28843 | 0.1585 | -191.696 | 18.7905 | 0.6101 | 0.083188 | 0.062212 | 0.059662 | 0.00033513 | 0.00030227 | 1.706 | 21.7628 | 21.9822 | 22.1796 | 22.2338 | 22.0495 | 21.3425 | 20.1622 | 22.1884 | 22.3623 | 22.4002 | 22.3513 | 21.9675 | 21.1959 | 22.2823 | 47.1134 | 31.6585 | 35.8774 | 26.5274 | 22.9364 | 34.0392 | 25.2886 | 22.333 | 22.0977 | 21.6582 | 22.0582 | 21.7696 | 21.293 | 21.9345 | 21.5736 | 21.9307 | 35.7781 | 103.3234 | 79.7518 | 47.1037 | 0.26739 | 0.030843 | 42.0709 | 21.9633 | 22.2828 | 20.2048 | 21.6019 | 22.0413 | 21.9187 | 21.7782 | 25.0295 | 21.7753 | 21.4767 | 22.4471 | 96.1935 | 118.2277 | 75.6029 | 76.5421 | 46.6106 |  | 35.7365 | 66.9296 | 38.2371 | 49.9176 | 36.9945 | 41.6623 |  | 48.241 |  |  | 21.4557 | 22.803 | 37.8448 | [5 empty] | 21.8884 | 36.7353 | 21.6648 | 22.0541 | 28.0629 | 21.2175 | 21.8624 | 22.7187 | 48.1041 | 123.2953 |  | 40.2124 | 91.0167 | 20.7415 | 42.1111 | 94.8727 | 30.3744 | 74.7578 | 22.3262 | 71.1019 | 22.2002 | 73.101 | 18.5555 | 42.786 | 85.8024 | 24.03 | 42.3747 | 107.7588 | 20.7153 | 40.4608 | 94.3669 | 20.7354 | 66.8554 | 25.0107 | 76.561 | 22.4483 | 75.1899 | 0.5317 | 19.7426 | 0.87306 | 0.025003 | -27.0677 | 3.0952 | 56.89 | 52.19 | 0.9513 | -0.67194 | -6.1068 | 0.63786 | 0.47455 | -16.5036 | 5.167 | 0.2141 | -0.26394 | 0.16564 | -0.94779 | -0.72674 | -0.10319 | 0.20183
42838.4235 | 276 | 22.9146 | 22.8817 | 22.8693 | 22.7817 | 22.4048 | 21.7299 | 22.7234 | 21.7877 | 22.3738 | 22.3718 | 22.3498 | 22.002 | 21.2075 | 22.1754 | 21.6359 | 21.8042 | 21.9249 | 21.1094 | 21.2012 | 21.438 | 20.4991 | 20.7201 | 21.7976 | 21.8856 | 21.6904 | 23.7165 | 102.7763 | 91.3628 | 109.0841 | 22.1273 | 21.7423 | 22.7878 | 22.0266 | 21.7922 | 23.403 | 36.6707 | 101.0372 |  | 56.6367 | 83.9363 | 85.8973 | 59.5654 |  | 17.0162 | 17.2955 | 16.7358 | 17.203 | 17.5176 | 19.3916 | 50.8344 | 15.3362 | 17.0924 | 15.5439 | 17.7461 | 18.2344 | 44.6932 | 49.3689 | 43.8841 | 21.6435 |  |  | 0.4543 | -0.40879 | -26.2631 | 0.45468 | 0.22749 | -190.5914 | 18.7497 | 0.55293 | 0.12094 | 0.11823 | 0.16608 | 0.0003417 | 0.00033842 | 1.7141 | 21.7679 | 21.9836 | 22.1748 | 22.222 | 22.05 | 21.3391 | 20.1541 | 22.1892 | 22.3609 | 22.4006 | 22.345 | 21.9736 | 21.1983 | 22.2821 | 46.1023 | 30.5335 | 35.0787 | 26.3453 | 22.676 | 34.0687 | 25.3264 | 22.3358 | 22.1048 | 21.6644 | 22.0643 | 21.7856 | 21.2997 | 21.9496 | 21.5826 | 21.9391 | 35.8635 | 103.6434 | 79.9154 | 47.0523 | 0.19858 | -0.060643 | 42.0866 | 21.9558 | 22.2811 | 20.2106 | 21.5978 | 22.0441 | 21.9118 | 21.7779 | 25.0556 | 21.7777 | 21.481 | 22.4569 | 96.41 | 118.9749 | 75.7535 | 76.6876 | 47.0365 |  | 35.8062 | 66.9006 | 38.3271 | 50.0994 | 37.08 | 41.6905 |  | 48.3533 |  |  | 21.4553 | 22.8246 | 38.0171 | [5 empty] | 21.8963 | 36.7897 | 21.6658 | 22.056 | 28.1171 | 21.2212 | 21.8688 | 22.7343 | 48.2895 | 123.5009 |  | 40.2806 | 91.3444 | 20.746 | 42.0632 | 95.1766 | 30.4432 | 74.8961 | 22.3294 | 71.1815 | 22.2124 | 73.1768 | 18.5613 | 42.9049 | 86.0353 | 24.0631 | 42.5078 | 107.9506 | 20.7267 | 40.5562 | 94.5443 | 20.758 | 66.9434 | 25.0591 | 76.6684 | 22.4639 | 75.5766 | 0.54153 | 19.7417 | 0.87503 | 0.023747 | -27.144 | 3.0952 | 76.21 | 51.64 | 0.91834 | -0.75937 | -6.0866 | 0.80085 | 0.56852 | -16.4556 | 5.1613 | 0.20467 | -0.26002 | 0.16354 | -0.83198 | -0.63358 | -0.11354 | 0.20621
42838.4235 | 277 | 22.9155 | 22.8772 | 22.8637 | 22.7848 | 22.4015 | 21.7297 | 22.7227 | 21.7847 | 22.3695 | 22.3672 | 22.345 | 21.9948 | 21.2027 | 22.1787 | 21.6271 | 21.7879 | 21.9091 | 21.0941 | 21.1889 | 21.4245 | 20.4831 | 20.7089 | 21.7934 | 21.8701 | 21.6801 | 23.7155 | 102.97 | 91.5187 | 109.3472 | 22.1313 | 21.7477 | 22.8004 | 22.0191 | 21.7922 | 23.4178 | 36.7713 | 100.8608 |  | 56.7923 | 84.0404 | 86.0324 | 59.9689 |  | 17.0066 | 17.2956 | 16.7319 | 17.2001 | 17.5067 | 19.4032 | 51.6051 | 15.3452 | 17.0931 | 15.5114 | 17.7366 | 18.2329 | 44.7305 | 49.4499 | 43.923 | 21.6477 |  |  | 0.60675 | -0.37988 | -25.899 | 0.18132 | 0.1401 | -190.3003 | 19.0435 | 0.66464 | 0.18574 | 0.1562 | 0.19924 | 0.00035156 | 0.00032363 | 1.7058 | 21.7666 | 21.9805 | 22.174 | 22.2267 | 22.044 | 21.3377 | 20.1538 | 22.185 | 22.3603 | 22.3982 | 22.3416 | 21.969 | 21.1982 | 22.2798 | 45.3551 | 29.6961 | 34.3207 | 26.5096 | 22.8982 | 34.1094 | 25.354 | 22.3376 | 22.1096 | 21.6648 | 22.0657 | 21.7814 | 21.2998 | 21.9413 | 21.5851 | 21.9488 | 35.9433 | 104.1375 | 80.2842 | 47.1013 | 0.50115 | 0.013916 | 42.1159 | 21.9462 | 22.2737 | 20.1969 | 21.5944 | 22.0457 | 21.9113 | 21.7822 | 25.079 | 21.7667 | 21.4754 | 22.4637 | 96.5764 | 119.2541 | 75.8913 | 76.8094 | 46.9545 |  | 35.8818 | 67.022 | 38.4303 | 50.0188 | 37.1685 | 41.8024 |  | 48.4778 |  |  | 21.4698 | 22.8446 | 38.0327 | [5 empty] | 21.8964 | 36.8797 | 21.6675 | 22.0597 | 28.1584 | 21.2233 | 21.8607 | 22.7502 | 48.4315 | 123.9711 |  | 40.463 | 91.6438 | 20.7551 | 42.1375 | 95.2672 | 30.5297 | 75.0121 | 22.3499 | 71.2447 | 22.2193 | 73.2851 | 18.5675 | 43.143 | 86.1481 | 24.1045 | 42.7078 | 108.0953 | 20.7464 | 40.7193 | 94.7944 | 20.759 | 67.1023 | 25.0983 | 76.7706 | 22.4829 | 75.8298 | 0.56175 | 19.7407 | 0.87687 | 0.02538 | -27.2014 | 3.0953 | 84.35 | 51.63 | 1.0617 | -0.73202 | -6.0442 | 0.50574 | 0.44615 | -16.4433 | 5.2017 | 0.20955 | -0.25982 | 0.16884 | -0.74416 | -0.54612 | -0.12127 | 0.20759
42838.4235 | 278 | 22.9242 | 22.8866 | 22.871 | 22.7881 | 22.4029 | 21.7306 | 22.7193 | 21.7889 | 22.3684 | 22.3735 | 22.3462 | 21.998 | 21.2059 | 22.1806 | 21.6285 | 21.7869 | 21.9079 | 21.0944 | 21.1895 | 21.4244 | 20.4752 | 20.7205 | 21.8017 | 21.8714 | 21.6731 | 23.7367 | 103.2724 | 91.7267 | 109.839 | 22.1332 | 21.7511 | 22.8074 | 22.0258 | 21.7948 | 23.4357 | 36.878 | 101.1981 |  | 56.9396 | 84.1877 | 86.1655 | 60.4425 |  | 17.0142 | 17.2963 | 16.7341 | 17.2034 | 17.4904 | 19.4676 | 52.0777 | 15.4361 | 17.0911 | 15.5066 | 17.7502 | 18.2325 | 44.7816 | 49.5328 | 43.961 | 21.6485 |  |  | 0.57061 | -0.5343 | -25.5173 | 0.41065 | 0.059272 | -189.9448 | 18.9002 | 0.41559 | 0.11199 | 0.13333 | 0.074592 | 0.0003532 | 0.00033842 | 1.6796 | 21.7672 | 21.9816 | 22.177 | 22.2202 | 22.0412 | 21.3418 | 20.158 | 22.18 | 22.3555 | 22.3958 | 22.3413 | 21.9683 | 21.1876 | 22.2737 | 46.4443 | 30.4801 | 34.7812 | 26.6142 | 23.4911 | 34.1972 | 25.4051 | 22.337 | 22.1039 | 21.6699 | 22.0606 | 21.7777 | 21.3004 | 21.9292 | 21.5812 | 21.9512 | 36.0136 | 104.8227 | 80.7351 | 47.3161 | 0.336 | 0.10369 | 42.2204 | 21.9529 | 22.2739 | 20.2042 | 21.5962 | 22.0443 | 21.9108 | 21.7853 | 25.1035 | 21.7763 | 21.4755 | 22.482 | 96.7118 | 119.654 | 76.0275 | 76.9754 | 47.225 |  | 35.9518 | 67.5249 | 38.5361 | 50.1621 | 37.2698 | 42.3133 |  | 48.614 |  |  | 21.4901 | 22.8628 | 38.1566 | [5 empty] | 21.8989 | 37.193 | 21.6722 | 22.0676 | 28.2166 | 21.226 | 21.8643 | 22.7842 | 48.5162 | 124.7746 |  | 40.7297 | 91.8804 | 20.7718 | 42.4083 | 95.4812 | 30.633 | 75.1531 | 22.3582 | 71.2803 | 22.2511 | 73.4651 | 18.5628 | 43.3515 | 86.1872 | 24.1211 | 42.9075 | 108.3129 | 20.7508 | 40.8357 | 95.0738 | 20.7589 | 67.2599 | 25.1386 | 76.9379 | 22.5025 | 75.9559 | 0.44915 | 19.7408 | 0.8792 | 0.02615 | -27.0939 | 3.0953 | 70.16 | 52.76 | 1.0302 | -0.86815 | -5.9995 | 0.76109 | 0.29023 | -16.4297 | 5.1826 | 0.20445 | -0.27012 | 0.16836 | -0.85485 | -0.5913 | -0.13075 | 0.20405
42838.4235 | 279 | 22.9145 | 22.8824 | 22.8725 | 22.7857 | 22.4069 | 21.7391 | 22.7228 | 21.789 | 22.3752 | 22.3729 | 22.3505 | 22.0032 | 21.2056 | 22.1815 | 21.6262 | 21.7862 | 21.9075 | 21.0954 | 21.1876 | 21.4199 | 20.4764 | 20.7244 | 21.8091 | 21.8746 | 21.6731 | 23.7567 | 103.4508 | 91.8921 | 109.6903 | 22.1311 | 21.7491 | 22.8247 | 22.0198 | 21.7998 | 23.4512 | 36.9938 | 102.4947 |  | 57.0908 | 84.3746 | 86.3478 | 60.7723 |  | 17.0162 | 17.3015 | 16.7392 | 17.2043 | 17.4917 | 19.5786 | 52.2131 | 15.494 | 17.0884 | 15.5057 | 17.7553 | 18.2338 | 44.8275 | 49.6085 | 43.9954 | 21.6451 |  |  | 0.76183 | -0.26422 | -24.9949 | 0.47702 | 0.17558 | -188.8711 | 19.5435 | 0.52008 | 0.0287 | 0.088437 | 0.069384 | 0.00035484 | 0.00033349 | 1.6818 | 21.7674 | 21.9783 | 22.1828 | 22.2318 | 22.052 | 21.3401 | 20.156 | 22.1823 | 22.3575 | 22.3999 | 22.3478 | 21.9674 | 21.1991 | 22.2767 | 46.9619 | 30.8055 | 35.7305 | 27.2593 | 23.7661 | 34.2529 | 25.458 | 22.3322 | 22.0944 | 21.6629 | 22.0557 | 21.7767 | 21.2983 | 21.9255 | 21.5749 | 21.9544 | 36.0819 | 105.2795 | 80.9881 | 47.4028 | 0.42604 | -0.17457 | 42.417 | 21.9593 | 22.2736 | 20.216 | 21.6012 | 22.0446 | 21.9136 | 21.7834 | 25.1272 | 21.7745 | 21.4814 | 22.4962 | 96.9144 | 120.1699 | 76.1692 | 77.1253 | 48.3344 |  | 36.0415 | 68.2922 | 38.6407 | 49.9555 | 37.3812 | 42.1415 |  | 48.7607 |  |  | 21.4901 | 22.8702 | 38.2374 | [5 empty] | 21.8895 | 37.5602 | 21.6685 | 22.0617 | 28.2596 | 21.2272 | 21.8637 | 22.8132 | 48.642 | 125.2245 |  | 40.8478 | 92.0036 | 20.7845 | 42.7045 | 95.861 | 30.7209 | 75.3116 | 22.3561 | 71.3171 | 22.2839 | 73.666 | 18.5744 | 43.5356 | 86.2842 | 24.1474 | 43.0883 | 108.5871 | 20.7674 | 40.8852 | 95.3393 | 20.7765 | 67.4691 | 25.1746 | 77.0811 | 22.5238 | 76.113 | 0.67861 | 19.739 | 0.88086 | 0.026084 | -27.1443 | 3.0953 | 59.98 | 51.79 | 1.1902 | -0.61051 | -5.9378 | 0.8203 | 0.49962 | -16.3864 | 5.2711 | 0.17673 | -0.28781 | 0.17795 | -0.9058 | -0.69059 | -0.1359 | 0.204
42838.4235 | 280 | 22.9105 | 22.8717 | 22.8579 | 22.7741 | 22.3952 | 21.7219 | 22.713 | 21.7681 | 22.36 | 22.3666 | 22.3385 | 21.9919 | 21.2032 | 22.1737 | 21.6245 | 21.7848 | 21.9074 | 21.096 | 21.1874 | 21.4235 | 20.4798 | 20.7168 | 21.8211 | 21.8756 | 21.68 | 23.7695 | 103.7093 | 92.077 | 110.2462 | 22.1261 | 21.7482 | 22.8331 | 22.0184 | 21.7797 | 23.4565 | 37.1021 | 104.457 |  | 57.2628 | 84.5396 | 86.5381 | 61.5221 |  | 17.0081 | 17.2933 | 16.7424 | 17.2002 | 17.4797 | 19.6749 | 52.0196 | 15.5134 | 17.0935 | 15.5025 | 17.7698 | 18.2362 | 44.8696 | 49.6872 | 44.0477 | 21.6434 |  |  | 0.72306 | -0.41668 | -25.1039 | 0.48359 | 0.17032 | -188.8928 | 19.4765 | 0.36237 | -0.0059392 | 0.12431 | 0.12771 | 0.00034334 | 0.00033842 | 1.7025 | 21.7673 | 21.9755 | 22.1792 | 22.2251 | 22.0488 | 21.3441 | 20.1634 | 22.1832 | 22.3618 | 22.4056 | 22.353 | 21.9719 | 21.1992 | 22.2772 | 48.1635 | 30.1003 | 35.1058 | 27.2866 | 24.0993 | 34.3364 | 25.5029 | 22.3415 | 22.1029 | 21.6708 | 22.0656 | 21.7843 | 21.2998 | 21.9307 | 21.5759 | 21.9781 | 36.1738 | 105.6685 | 81.2821 | 47.5879 | 0.36765 | -0.042384 | 42.4608 | 21.961 | 22.2833 | 20.2153 | 21.6094 | 22.0475 | 21.92 | 21.7837 | 25.1577 | 21.7763 | 21.4896 | 22.5117 | 97.1639 | 120.7197 | 76.3641 | 77.2816 | 49.2734 |  | 36.1253 | 68.563 | 38.7253 | 49.5841 | 37.483 | 42.0076 |  | 48.8768 |  |  | 21.492 | 22.888 | 38.3849 | [5 empty] | 21.8878 | 37.6378 | 21.6716 | 22.057 | 28.3185 | 21.2271 | 21.8579 | 22.8416 | 48.8705 | 126.0494 |  | 40.9552 | 91.9886 | 20.8005 | 42.8743 | 96.2255 | 30.8193 | 75.4412 | 22.3588 | 71.3998 | 22.293 | 73.7841 | 18.5774 | 43.5827 | 86.4047 | 24.1957 | 43.2095 | 108.8563 | 20.7702 | 40.9219 | 95.6072 | 20.7885 | 67.6564 | 25.212 | 77.2189 | 22.5424 | 76.2689 | 0.46009 | 19.7388 | 0.88219 | 0.025721 | -27.1513 | 3.0953 | 81.7 | 52.66 | 1.1603 | -0.76665 | -5.9507 | 0.82592 | 0.49216 | -16.39 | 5.2629 | 0.15353 | -0.2924 | 0.19179 | -1.0295 | -0.61591 | -0.15299 | 0.20203
42838.4235 | 281 | 22.925 | 22.88 | 22.8697 | 22.7803 | 22.4078 | 21.7347 | 22.73 | 21.797 | 22.3673 | 22.3724 | 22.34 | 21.9976 | 21.2059 | 22.1744 | 21.6249 | 21.7911 | 21.9091 | 21.0961 | 21.1952 | 21.4206 | 20.4809 | 20.7177 | 21.8266 | 21.8736 | 21.6807 | 23.7904 | 104.0321 | 92.2041 | 110.8507 | 22.1467 | 21.7541 | 22.8563 | 22.0234 | 21.7911 | 23.4903 | 37.248 | 105.3761 |  | 57.4612 | 84.763 | 86.7157 | 63.2475 |  | 16.9973 | 17.2797 | 16.7277 | 17.1826 | 17.4666 | 19.7517 | 51.8157 | 15.4688 | 17.0888 | 15.4601 | 17.7562 | 18.245 | 44.9191 | 49.7697 | 44.1004 | 21.6448 |  |  | 0.70531 | -0.41602 | -25.0041 | 0.43562 | 0.14732 | -189.2595 | 19.3858 | 0.54373 | 0.13884 | 0.058016 | 0.29124 | 0.00036799 | 0.00031706 | 1.7159 | 21.7726 | 21.9793 | 22.1765 | 22.2307 | 22.0429 | 21.3385 | 20.1567 | 22.1853 | 22.3608 | 22.4017 | 22.3545 | 21.9691 | 21.2053 | 22.2768 | 48.2647 | 30.0466 | 33.9686 | 26.9004 | 24.1386 | 34.3946 | 25.5304 | 22.3331 | 22.0984 | 21.6648 | 22.0596 | 21.7731 | 21.3013 | 21.9384 | 21.5774 | 21.9878 | 36.2608 | 106.0742 | 81.7514 | 47.7418 | 0.27702 | -0.11751 | 42.3609 | 21.9586 | 22.2767 | 20.2148 | 21.5978 | 22.0452 | 21.9154 | 21.7831 | 25.1853 | 21.7712 | 21.483 | 22.5175 | 97.3359 | 121.3098 | 76.4872 | 77.4569 | 49.8761 |  | 36.2125 | 68.7901 | 38.7785 | 49.9016 | 37.6073 | 42.0851 |  | 48.9854 |  |  | 21.485 | 22.9096 | 38.5519 | [5 empty] | 21.8863 | 38.1756 | 21.671 | 22.0571 | 28.375 | 21.2283 | 21.8557 | 22.8752 | 49.1397 | 127.0416 |  | 41.2482 | 92.0552 | 20.8243 | 42.8144 | 96.5233 | 30.93 | 75.5676 | 22.3629 | 71.5686 | 22.3022 | 73.8648 | 18.5754 | 43.6618 | 86.5511 | 24.2437 | 43.2836 | 109.1043 | 20.7686 | 40.9916 | 95.8885 | 20.7991 | 67.8061 | 25.2627 | 77.4049 | 22.5609 | 76.4717 | 0.48643 | 19.7382 | 0.88315 | 0.026767 | -27.1616 | 3.0953 | 79.08 | 51.2 | 1.1469 | -0.76603 | -5.9387 | 0.78387 | 0.45779 | -16.408 | 5.2513 | 0.1398 | -0.29687 | 0.18726 | -1.0339 | -0.48634 | -0.19588 | 0.20075
42838.4235 | 282 | 22.9159 | 22.8796 | 22.8658 | 22.7853 | 22.4025 | 21.7334 | 22.7243 | 21.7803 | 22.3679 | 22.3675 | 22.3394 | 21.9969 | 21.2071 | 22.1726 | 21.6235 | 21.7906 | 21.9119 | 21.095 | 21.1909 | 21.4205 | 20.4825 | 20.7178 | 21.8358 | 21.8711 | 21.6801 | 23.8046 | 104.2078 | 92.3462 | 110.5152 | 22.1439 | 21.7545 | 22.8605 | 22.022 | 21.7924 | 23.5016 | 37.3967 | 106.5352 |  | 57.6288 | 84.9587 | 86.8678 | 65.4726 |  | 17.0019 | 17.3012 | 16.7368 | 17.1938 | 17.4682 | 19.7443 | 51.7065 | 15.404 | 17.0911 | 15.4429 | 17.7683 | 18.2418 | 44.9765 | 49.8533 | 44.1552 | 21.642 |  |  | 0.6902 | -0.49882 | -24.872 | 0.53156 | 0.24655 | -187.7021 | 19.487 | 0.50562 | 0.037067 | 0.037246 | 0.27007 | 0.0003187 | 0.00033184 | 1.7092 | 21.7712 | 21.9757 | 22.1732 | 22.2273 | 22.0409 | 21.3381 | 20.1561 | 22.185 | 22.3643 | 22.3939 | 22.346 | 21.9677 | 21.1979 | 22.2748 | 48.1359 | 30.9821 | 34.8766 | 26.8318 | 23.8649 | 34.4533 | 25.5851 | 22.3319 | 22.0971 | 21.6693 | 22.0658 | 21.7774 | 21.3015 | 21.9352 | 21.5811 | 21.9937 | 36.3461 | 106.5277 | 81.9214 | 47.6919 | 0.35016 | 0.022094 | 42.248 | 21.9529 | 22.2755 | 20.2181 | 21.5971 | 22.0425 | 21.9132 | 21.7833 | 25.2055 | 21.7774 | 21.4807 | 22.537 | 97.5412 | 121.7277 | 76.5874 | 77.6277 | 49.77 |  | 36.2988 | 68.5083 | 38.8532 | 50.3573 | 37.764 | 42.4082 |  | 49.1261 |  |  | 21.4805 | 22.9345 | 38.6205 | [5 empty] | 21.8955 | 39.0597 | 21.6734 | 22.059 | 28.4192 | 21.2248 | 21.8634 | 22.9089 | 49.4207 | 127.9071 |  | 41.6132 | 92.2926 | 20.8438 | 42.8967 | 96.9165 | 31.0426 | 75.7349 | 22.3745 | 71.7483 | 22.3145 | 73.9991 | 18.5705 | 43.9413 | 86.7263 | 24.2695 | 43.4125 | 109.3546 | 20.7628 | 41.128 | 96.1328 | 20.81 | 67.9375 | 25.3124 | 77.7314 | 22.5698 | 76.6727 | 0.62408 | 19.7373 | 0.88444 | 0.026353 | -27.1327 | 3.0953 | 78.4 | 51.65 | 1.134 | -0.83883 | -5.9232 | 0.86593 | 0.59221 | -16.3402 | 5.265 | 0.14572 | -0.28645 | 0.18003 | -1.0127 | -0.58082 | -0.25254 | 0.20508
42838.4236 | 283 | 22.9165 | 22.8811 | 22.8599 | 22.7868 | 22.3992 | 21.7253 | 22.7168 | 21.7797 | 22.368 | 22.3693 | 22.3445 | 21.9944 | 21.2017 | 22.1719 | 21.6283 | 21.7928 | 21.9166 | 21.0964 | 21.1948 | 21.426 | 20.4806 | 20.725 | 21.8459 | 21.8744 | 21.6846 | 23.8327 | 104.3322 | 92.5365 | 109.9088 | 22.1345 | 21.7487 | 22.8797 | 22.0243 | 21.7954 | 23.5122 | 37.5252 | 107.9471 |  | 57.8054 | 85.1499 | 87.0535 | 65.712 |  | 17.0067 | 17.3064 | 16.7343 | 17.1895 | 17.4652 | 19.8483 | 52.1971 | 15.3404 | 17.0832 | 15.4228 | 17.7723 | 18.2478 | 45.0375 | 49.9334 | 44.2188 | 21.6512 |  |  | 0.49833 | -0.18931 | -25.1079 | 0.28777 | 0.23604 | -184.6445 | 20.1579 | 0.52533 | 0.15947 | -0.024226 | 0.16157 | 0.00035813 | 0.0003187 | 1.6805 | 21.7698 | 21.9818 | 22.1673 | 22.2189 | 22.043 | 21.3372 | 20.1553 | 22.1837 | 22.362 | 22.3934 | 22.3435 | 21.9647 | 21.2019 | 22.2738 | 48.2338 | 31.6433 | 36.2143 | 27.5741 | 24.222 | 34.5275 | 25.6484 | 22.3373 | 22.1102 | 21.6692 | 22.0722 | 21.7785 | 21.3023 | 21.9428 | 21.5828 | 22.0135 | 36.4322 | 106.7767 | 82.0226 | 47.8335 | 0.31713 | -0.039911 | 42.3164 | 21.9523 | 22.2779 | 20.2214 | 21.6017 | 22.0509 | 21.918 | 21.7956 | 25.2414 | 21.7868 | 21.4854 | 22.5501 | 97.7875 | 122.1405 | 76.7611 | 77.8213 | 49.9863 |  | 36.3918 | 68.2946 | 38.9398 | 50.4814 | 37.9025 | 42.5765 |  | 49.2431 |  |  | 21.4855 | 22.948 | 38.6263 | [5 empty] | 21.9032 | 39.5294 | 21.6754 | 22.0573 | 28.4534 | 21.227 | 21.8678 | 22.9443 | 49.7 | 128.5142 |  | 41.8169 | 92.5353 | 20.8489 | 43.2105 | 97.5062 | 31.1695 | 75.9286 | 22.3786 | 71.9493 | 22.3228 | 74.1928 | 18.5838 | 44.3347 | 86.8987 | 24.3135 | 43.5879 | 109.543 | 20.77 | 41.2946 | 96.4927 | 20.8377 | 68.1283 | 25.3709 | 77.9732 | 22.5907 | 76.7977 | 0.65839 | 19.7361 | 0.88539 | 0.025983 | -27.0387 | 3.0952 | 74.85 | 52.25 | 0.96285 | -0.51677 | -5.9513 | 0.63714 | 0.57955 | -16.2094 | 5.3558 | 0.14292 | -0.27751 | 0.18137 | -1.0148 | -0.72203 | -0.25476 | 0.20412
42838.4236 | 284 | 22.9201 | 22.8875 | 22.8616 | 22.7802 | 22.4016 | 21.7281 | 22.7208 | 21.7817 | 22.3703 | 22.3686 | 22.3465 | 21.9899 | 21.1971 | 22.1743 | 21.6305 | 21.7884 | 21.8985 | 21.0912 | 21.1896 | 21.4183 | 20.4771 | 20.7264 | 21.8555 | 21.8691 | 21.6848 | 23.8505 | 104.5156 | 92.7568 | 110.8171 | 22.129 | 21.7529 | 22.8912 | 22.0304 | 21.7937 | 23.5218 | 37.6324 | 109.6214 |  | 58.0295 | 85.4063 | 87.2908 | 65.4571 |  | 17.0165 | 17.3101 | 16.7311 | 17.1868 | 17.4597 | 19.9743 | 53.0485 | 15.3665 | 17.0913 | 15.3749 | 17.7779 | 18.2468 | 45.0906 | 50.0089 | 44.2801 | 21.649 |  |  | 0.71123 | -0.39565 | -24.9377 | 0.46848 | 0.13353 | -185.9128 | 19.9674 | 0.62784 | -0.0008796 | 0.15264 | 0.12094 | 0.00033842 | 0.0003187 | 1.6682 | 21.7645 | 21.9768 | 22.1733 | 22.2267 | 22.0508 | 21.3463 | 20.1563 | 22.1833 | 22.3626 | 22.3937 | 22.3492 | 21.9706 | 21.199 | 22.2717 | 48.7893 | 32.5912 | 37.2061 | 27.7457 | 24.4528 | 34.598 | 25.709 | 22.3355 | 22.1081 | 21.6595 | 22.0642 | 21.7779 | 21.2941 | 21.937 | 21.5806 | 22.0115 | 36.5094 | 107.1659 | 82.0912 | 48.0814 | 0.5503 | 0.10369 | 42.5194 | 21.9468 | 22.2724 | 20.2238 | 21.5996 | 22.0509 | 21.9177 | 21.7909 | 25.2661 | 21.7803 | 21.4867 | 22.5589 | 97.9796 | 122.7978 | 76.9519 | 77.9991 | 50.7615 |  | 36.479 | 68.3104 | 39.0219 | 50.6733 | 38.0052 | 42.7967 |  | 49.3735 |  |  | 21.4944 | 22.9564 | 38.6816 | [5 empty] | 21.8905 | 39.7661 | 21.6673 | 22.0498 | 28.4883 | 21.2153 | 21.8565 | 22.9809 | 49.9653 | 129.4574 |  | 41.9281 | 92.8832 | 20.8605 | 43.4778 | 98.1248 | 31.2908 | 76.109 | 22.3993 | 72.1226 | 22.341 | 74.357 | 18.583 | 44.5398 | 87.073 | 24.3612 | 43.732 | 109.6602 | 20.789 | 41.4198 | 96.9949 | 20.8607 | 68.2829 | 25.4316 | 78.1714 | 22.6148 | 76.9951 | 0.56471 | 19.7354 | 0.8868 | 0.025743 | -26.9989 | 3.0952 | 87.64 | 51.69 | 1.1516 | -0.74708 | -5.9311 | 0.81293 | 0.43599 | -16.2685 | 5.3315 | 0.1244 | -0.2751 | 0.17959 | -1.0682 | -0.82514 | -0.24397 | 0.19989
42838.4236 | 285 | 22.9178 | 22.8816 | 22.86 | 22.7829 | 22.4017 | 21.7275 | 22.7262 | 21.7798 | 22.3743 | 22.3691 | 22.3418 | 21.9872 | 21.2017 | 22.171 | 21.6376 | 21.8007 | 21.9078 | 21.0997 | 21.2021 | 21.4252 | 20.4898 | 20.7299 | 21.8683 | 21.8754 | 21.6857 | 23.8616 | 104.7668 | 92.9719 | 111.8456 | 22.1289 | 21.7466 | 22.8967 | 22.0201 | 21.7915 | 23.5377 | 37.7343 | 110.8261 |  | 58.268 | 85.6546 | 87.5365 | 65.6582 |  | 17.0091 | 17.2993 | 16.7262 | 17.1744 | 17.4438 | 19.9789 | 53.8781 | 15.3843 | 17.0873 | 15.3229 | 17.777 | 18.2505 | 45.1311 | 50.0869 | 44.3326 | 21.6396 |  |  | 0.6994 | -0.41208 | -24.7031 | 0.87458 | 0.15455 | -185.2004 | 19.8813 | 0.80789 | 0.16978 | 0.090535 | 0.061919 | 0.00035649 | 0.00033349 | 1.6559 | 21.7697 | 21.9733 | 22.1763 | 22.2327 | 22.0486 | 21.3366 | 20.1549 | 22.1838 | 22.3607 | 22.4037 | 22.353 | 21.9695 | 21.1979 | 22.2816 | 49.911 | 33.8051 | 39.1312 | 28.6426 | 25.0895 | 34.6916 | 25.7912 | 22.341 | 22.1098 | 21.6673 | 22.0644 | 21.7804 | 21.3082 | 21.9355 | 21.5875 | 22.0228 | 36.5855 | 107.371 | 82.1399 | 48.4083 | 0.43961 | 0.14439 | 42.6208 | 21.9462 | 22.2672 | 20.226 | 21.5918 | 22.0445 | 21.9131 | 21.7877 | 25.2909 | 21.7762 | 21.48 | 22.5796 | 98.2112 | 123.1179 | 77.1696 | 78.2007 | 52.2557 |  | 36.5986 | 68.7017 | 39.1411 | 51.645 | 38.1683 | 42.799 |  | 49.547 |  |  | 21.5218 | 22.9812 | 39.2564 | [5 empty] | 21.8951 | 40.4236 | 21.6699 | 22.0618 | 28.5427 | 21.2245 | 21.8611 | 23.0209 | 50.1682 | 130.6945 |  | 42.2091 | 93.2676 | 20.8805 | 43.5902 | 98.794 | 31.4143 | 76.3004 | 22.427 | 72.3199 | 22.357 | 74.4778 | 18.5832 | 44.6011 | 87.2389 | 24.3983 | 43.8768 | 109.9294 | 20.7953 | 41.5481 | 97.6231 | 20.8759 | 68.4111 | 25.486 | 78.362 | 22.6345 | 77.1821 | 0.58623 | 19.7336 | 0.88745 | 0.023834 | -27.1046 | 3.0952 | 87.95 | 52.97 | 1.1436 | -0.76241 | -5.9031 | 1.1107 | 0.46907 | -16.2374 | 5.3201 | 0.087019 | -0.28184 | 0.15825 | -1.1818 | -1.0294 | -0.24603 | 0.19344
42838.4236 | 286 | 22.916 | 22.8747 | 22.8628 | 22.7819 | 22.3947 | 21.7244 | 22.7249 | 21.7788 | 22.3657 | 22.365 | 22.3431 | 21.9897 | 21.2018 | 22.1653 | 21.6295 | 21.789 | 21.9048 | 21.097 | 21.1997 | 21.4172 | 20.4881 | 20.7297 | 21.875 | 21.8662 | 21.6816 | 23.8862 | 105.2986 | 93.1552 | 114.5995 | 22.1338 | 21.7555 | 22.9132 | 22.0232 | 21.7981 | 23.5613 | 37.8548 | 110.9595 |  | 58.4509 | 85.8685 | 87.7725 | 66.4073 |  | 17.0147 | 17.3115 | 16.7292 | 17.1718 | 17.4362 | 19.9792 | 54.6397 | 15.4326 | 17.086 | 15.373 | 17.7825 | 18.2554 | 45.1915 | 50.1604 | 44.3893 | 21.6471 |  |  | 0.61201 | -0.28197 | -25.0277 | 0.53879 | 0.079644 | -186.0291 | 20.3623 | 0.41165 | 0.198 | 0.2397 | 0.051156 | 0.00036306 | 0.00033349 | 1.6425 | 21.7661 | 21.9678 | 22.1631 | 22.2233 | 22.026 | 21.3298 | 20.1476 | 22.1741 | 22.3536 | 22.3906 | 22.3386 | 21.9625 | 21.1922 | 22.2635 | 51.012 | 34.3935 | 38.9859 | 29.1657 | 25.5443 | 34.7873 | 25.8606 | 22.3349 | 22.0989 | 21.6628 | 22.0651 | 21.7726 | 21.2937 | 21.9418 | 21.5799 | 22.0382 | 36.6852 | 107.7202 | 82.4421 | 48.6645 | 0.31398 | 0.063558 | 42.7404 | 21.9557 | 22.2737 | 20.227 | 21.5979 | 22.0463 | 21.9142 | 21.7937 | 25.3212 | 21.7887 | 21.4876 | 22.5945 | 98.5505 | 123.6299 | 77.4226 | 78.4659 | 53.2544 |  | 36.6971 | 69.0521 | 39.2439 | 52.4097 | 38.3247 | 42.7435 |  | 49.7023 |  |  | 21.5497 | 22.9971 | 39.7371 | [5 empty] | 21.8963 | 40.6112 | 21.6749 | 22.0684 | 28.5875 | 21.2215 | 21.8655 | 23.0494 | 50.3345 | 131.8231 |  | 42.5705 | 93.4815 | 20.8965 | 43.6768 | 99.206 | 31.534 | 76.4798 | 22.4272 | 72.5379 | 22.3689 | 74.6123 | 18.5891 | 44.7627 | 87.3736 | 24.4401 | 44.0385 | 110.3588 | 20.8066 | 41.6932 | 98.214 | 20.9007 | 68.6277 | 25.5373 | 78.5107 | 22.6619 | 77.3275 | 0.55748 | 19.7321 | 0.88801 | 0.023362 | -27.083 | 3.0952 | 87.16 | 51.58 | 1.0735 | -0.63068 | -5.9419 | 0.87181 | 0.33672 | -16.2737 | 5.3841 | 0.062681 | -0.28801 | 0.14242 | -1.2929 | -1.0051 | -0.26267 | 0.18977
42838.4236 | 287 | 22.9217 | 22.8879 | 22.8617 | 22.7864 | 22.3952 | 21.7299 | 22.7243 | 21.7869 | 22.3683 | 22.3771 | 22.3467 | 21.9978 | 21.2083 | 22.1749 | 21.6349 | 21.7979 | 21.9125 | 21.1014 | 21.1985 | 21.4319 | 20.4953 | 20.7386 | 21.8889 | 21.8831 | 21.6922 | 23.9097 | 105.6782 | 93.3979 | 114.7143 | 22.1302 | 21.7472 | 22.9181 | 22.0205 | 21.7971 | 23.57 | 37.9762 | 112.3816 |  | 58.6494 | 86.211 | 88.0368 | 65.8757 |  | 17.0088 | 17.314 | 16.7204 | 17.1648 | 17.4142 | 19.9451 | 54.6255 | 15.4694 | 17.0916 | 15.4783 | 17.7857 | 18.2678 | 45.2669 | 50.2424 | 44.4339 | 21.6453 |  |  | 0.49635 | -0.2984 | -25.029 | 0.50528 | 0.057956 | -184.0893 | 19.9588 | 0.73035 | 0.19275 | 0.27998 | 0.22545 | 0.00034663 | 0.00029735 | 1.6491 | 21.7753 | 21.9776 | 22.1784 | 22.234 | 22.0449 | 21.34 | 20.1558 | 22.1842 | 22.3653 | 22.4003 | 22.3442 | 21.9678 | 21.195 | 22.277 | 51.3475 | 34.5316 | 38.7298 | 29.1841 | 25.1634 | 34.8608 | 25.9204 | 22.3293 | 22.0998 | 21.6702 | 22.0636 | 21.7797 | 21.2945 | 21.932 | 21.5808 | 22.0439 | 36.7694 | 107.9346 | 82.5569 | 48.6476 | 0.44099 | -0.07681 | 43.2031 | 21.9498 | 22.2718 | 20.2285 | 21.6061 | 22.0438 | 21.9171 | 21.7928 | 25.3495 | 21.7846 | 21.4828 | 22.5993 | 98.9281 | 124.5476 | 77.7008 | 78.7021 | 53.6493 |  | 36.7946 | 69.755 | 39.3351 | 54.7784 | 38.5152 | 43.034 |  | 49.8409 |  |  | 21.5633 | 23.0147 | 40.0188 | [5 empty] | 21.8938 | 40.6471 | 21.6838 | 22.0721 | 28.6035 | 21.2346 | 21.8721 | 23.0813 | 50.5621 | 132.832 |  | 42.9608 | 93.6411 | 20.9186 | 43.9155 | 99.7819 | 31.6651 | 76.646 | 22.4637 | 72.8502 | 22.3985 | 74.7976 | 18.5863 | 45.0559 | 87.6776 | 24.4719 | 44.145 | 110.5221 | 20.8223 | 41.8252 | 99.0237 | 20.9188 | 68.8671 | 25.5845 | 78.7276 | 22.6709 | 77.4552 | 0.56527 | 19.7304 | 0.88927 | 0.02501 | -27.0852 | 3.0953 | 93.14 | 52.09 | 0.96695 | -0.6488 | -5.942 | 0.84426 | 0.28722 | -16.1877 | 5.3301 | 0.055077 | -0.30437 | 0.083224 | -1.3215 | -0.96967 | -0.2437 | 0.19314
42838.4236 | 288 | 22.9157 | 22.8749 | 22.8573 | 22.7862 | 22.3991 | 21.7274 | 22.7152 | 21.7806 | 22.3649 | 22.3677 | 22.3355 | 21.9877 | 21.1953 | 22.1653 | 21.6238 | 21.8051 | 21.918 | 21.0935 | 21.199 | 21.4352 | 20.4836 | 20.7338 | 21.8899 | 21.8744 | 21.69 | 23.9215 | 105.7563 | 93.8516 | 114.7878 | 22.1203 | 21.7426 | 22.9257 | 22.0108 | 21.7822 | 23.5805 | 38.0734 | 113.8105 |  | 58.8761 | 86.5659 | 88.2607 | 64.5738 |  | 17.0128 | 17.3196 | 16.7163 | 17.1543 | 17.3985 | 19.8724 | 54.1263 | 15.485 | 17.0858 | 15.6062 | 17.7972 | 18.2672 | 45.336 | 50.3142 | 44.4881 | 21.648 |  |  | 0.85251 | -0.66244 | -24.8615 | 0.48491 | 0.27678 | -180.7597 | 20.1494 | 0.73561 | 0.21513 | 0.18033 | 0.25531 | 0.00037949 | 0.00032527 | 1.6501 | 21.771 | 21.9798 | 22.1753 | 22.2334 | 22.0538 | 21.3424 | 20.1577 | 22.1854 | 22.3725 | 22.3976 | 22.348 | 21.9713 | 21.1957 | 22.2786 | 50.8577 | 34.33 | 37.6258 | 28.6838 | 24.8455 | 34.9312 | 25.9666 | 22.335 | 22.0989 | 21.6655 | 22.0574 | 21.7775 | 21.297 | 21.9317 | 21.5803 | 22.0561 | 36.8489 | 108.1005 | 82.6364 | 48.5719 | 0.35271 | -0.22536 | 43.5221 | 21.9544 | 22.2767 | 20.234 | 21.6046 | 22.0537 | 21.925 | 21.8013 | 25.382 | 21.7843 | 21.4899 | 22.6197 | 99.4131 | 125.5241 | 77.979 | 78.9556 | 53.9616 |  | 36.9166 | 70.7154 | 39.4334 | 56.1501 | 38.7086 | 43.6354 |  | 49.9858 |  |  | 21.5797 | 23.0452 | 40.1307 | [5 empty] | 21.906 | 40.9893 | 21.6748 | 22.0647 | 28.6393 | 21.2248 | 21.8739 | 23.1127 | 50.8023 | 133.4281 |  | 43.3101 | 94.0646 | 20.9292 | 44.1772 | 100.3148 | 31.7716 | 76.8386 | 22.4615 | 73.047 | 22.4075 | 74.9459 | 18.5986 | 45.5809 | 88.197 | 24.5119 | 44.2645 | 110.6657 | 20.8444 | 41.9738 | 99.865 | 20.9333 | 69.1011 | 25.6298 | 79.3279 | 22.6854 | 77.683 | 0.73241 | 19.7288 | 0.89149 | 0.024342 | -27.1323 | 3.0953 | 83.86 | 52.29 | 1.2674 | -0.9667 | -5.9222 | 0.82708 | 0.6276 | -16.0387 | 5.3549 | 0.050616 | -0.32763 | 0.051821 | -1.2588 | -0.84158 | -0.20417 | 0.19799
42838.4236 | 289 | 22.9139 | 22.8771 | 22.8664 | 22.7861 | 22.3978 | 21.7267 | 22.7131 | 21.7791 | 22.3638 | 22.3648 | 22.337 | 21.9956 | 21.1998 | 22.1683 | 21.6383 | 21.791 | 21.917 | 21.0944 | 21.199 | 21.4276 | 20.489 | 20.7379 | 21.9011 | 21.8844 | 21.6909 | 23.9437 | 106.3367 | 94.1741 | 115.2452 | 22.1421 | 21.7613 | 22.9563 | 22.0304 | 21.804 | 23.6156 | 38.203 | 114.2817 |  | 59.1253 | 86.9102 | 88.5883 | 64.2049 |  | 17.009 | 17.3203 | 16.7094 | 17.1419 | 17.3784 | 19.8775 | 54.5356 | 15.5087 | 17.0836 | 15.737 | 17.7931 | 18.2678 | 45.3977 | 50.378 | 44.5364 | 21.6517 |  |  | 0.50161 | -0.7886 | -24.7176 | 0.36137 | 0.1631 | -184.2522 | 20.2309 | 0.61207 | -0.010415 | 0.31166 | 0.24837 | 0.00034992 | 0.0003302 | 1.6356 | 21.7552 | 21.9719 | 22.1651 | 22.2231 | 22.0427 | 21.3344 | 20.1511 | 22.1779 | 22.3661 | 22.3868 | 22.3431 | 21.9636 | 21.1901 | 22.2706 | 50.3231 | 33.7992 | 36.8505 | 28.2249 | 24.8837 | 34.9949 | 26.0092 | 22.3359 | 22.1007 | 21.6697 | 22.0625 | 21.7821 | 21.3008 | 21.9416 | 21.5882 | 22.0721 | 36.9336 | 108.2778 | 82.7874 | 48.7962 | 0.22256 | 0.073448 | 43.6692 | 21.9497 | 22.2675 | 20.2283 | 21.5957 | 22.0475 | 21.9126 | 21.8008 | 25.3896 | 21.776 | 21.4885 | 22.6285 | 99.9412 | 126.3209 | 78.1968 | 79.2045 | 55.1253 |  | 37.0424 | 71.2581 | 39.5275 | 56.2898 | 38.8641 | 43.6666 |  | 50.1236 |  |  | 21.5891 | 23.0467 | 40.0354 | [5 empty] | 21.8966 | 41.0282 | 21.6777 | 22.0517 | 28.6864 | 21.2261 | 21.8669 | 23.1455 | 51.0706 | 134.2545 |  | 43.626 | 94.3642 | 20.948 | 44.3565 | 100.7309 | 31.856 | 77.0612 | 22.5012 | 73.2437 | 22.4349 | 75.0797 | 18.5927 | 45.7269 | 88.8029 | 24.5507 | 44.4176 | 111.3841 | 20.8702 | 42.0455 | 100.4661 | 20.9364 | 69.2688 | 25.6862 | 79.7522 | 22.7083 | 77.8462 | 0.71033 | 19.7278 | 0.89486 | 0.025591 | -27.0891 | 3.0953 | 87.8 | 51.29 | 0.97272 | -1.0547 | -5.905 | 0.71399 | 0.48177 | -16.193 | 5.3657 | 0.022637 | -0.33944 | 0.05333 | -1.1919 | -0.75045 | -0.18944 | 0.19468
42838.4236 | 290 | 22.9139 | 22.8727 | 22.8639 | 22.7805 | 22.3956 | 21.7286 | 22.7145 | 21.7854 | 22.3639 | 22.3716 | 22.3419 | 21.9929 | 21.2103 | 22.177 | 21.6257 | 21.7969 | 21.9154 | 21.101 | 21.1956 | 21.4285 | 20.4832 | 20.7358 | 21.9065 | 21.8803 | 21.6947 | 23.9576 | 106.6234 | 94.3479 | 115.0214 | 22.1288 | 21.7529 | 22.9577 | 22.0159 | 21.7995 | 23.6215 | 38.3001 | 114.3855 |  | 59.3242 | 87.1502 | 88.8576 | 64.3702 |  | 16.9929 | 17.3115 | 16.699 | 17.1448 | 17.3696 | 19.9465 | 55.5524 | 15.5318 | 17.0819 | 15.8068 | 17.7968 | 18.2656 | 45.448 | 50.4393 | 44.5978 | 21.6437 |  |  | 0.7822 | -0.86549 | -25.194 | 0.52302 | 0.13812 | -185.0013 | 19.9996 | 0.59696 | 0.048549 | 0.041442 | 0.18031 | 0.00034499 | 0.00030885 | 1.6187 | 21.7603 | 21.9776 | 22.1726 | 22.2259 | 22.0397 | 21.3345 | 20.1486 | 22.1821 | 22.361 | 22.3906 | 22.3491 | 21.9662 | 21.2051 | 22.278 | 48.9834 | 31.2784 | 34.5828 | 27.6189 | 24.3304 | 35.0362 | 26.0315 | 22.3433 | 22.1047 | 21.6667 | 22.0668 | 21.7799 | 21.3135 | 21.9453 | 21.5834 | 22.0816 | 37.025 | 108.5456 | 82.8606 | 49.2992 | 0.18108 | -0.15898 | 43.7459 | 21.9506 | 22.2733 | 20.2348 | 21.5958 | 22.0484 | 21.9191 | 21.8029 | 25.4179 | 21.7849 | 21.4849 | 22.641 | 100.3217 | 126.9125 | 78.4185 | 79.4154 | 55.9753 |  | 37.1529 | 71.1087 | 39.6308 | 55.9704 | 39.0051 | 43.9107 |  | 50.2679 |  |  | 21.6003 | 23.0656 | 39.8376 | [5 empty] | 21.8941 | 40.8695 | 21.6705 | 22.0614 | 28.7326 | 21.2272 | 21.8658 | 23.1697 | 51.2924 | 135.056 |  | 43.9144 | 94.6236 | 20.9454 | 44.4871 | 101.4078 | 31.9494 | 77.2204 | 22.5253 | 73.3622 | 22.4474 | 75.2939 | 18.5885 | 45.7833 | 89.2269 | 24.5839 | 44.5574 | 111.7608 | 20.8909 | 42.141 | 100.866 | 20.9547 | 69.4394 | 25.7103 | 79.8453 | 22.7344 | 78.0023 | 0.64114 | 19.726 | 0.89762 | 0.027217 | -27.1168 | 3.0953 | 83.89 | 52.79 | 1.2143 | -1.1049 | -5.9616 | 0.85896 | 0.44341 | -16.2278 | 5.3356 | 0.0028425 | -0.33171 | 0.067093 | -1.0382 | -0.49588 | -0.19067 | 0.18387
42838.4236 | 291 | 22.9141 | 22.8749 | 22.8692 | 22.7807 | 22.4015 | 21.7277 | 22.7195 | 21.7856 | 22.3648 | 22.3654 | 22.3385 | 21.9892 | 21.2069 | 22.1743 | 21.6333 | 21.7997 | 21.9159 | 21.0931 | 21.1995 | 21.4299 | 20.4918 | 20.7388 | 21.9238 | 21.8744 | 21.6946 | 23.9846 | 107.0807 | 94.6773 | 115.7585 | 22.1308 | 21.7585 | 22.9788 | 22.0155 | 21.8006 | 23.6399 | 38.3878 | 115.3333 |  | 59.5551 | 87.5008 | 89.1722 | 63.3464 |  | 16.9901 | 17.3084 | 16.691 | 17.1409 | 17.3714 | 20.0312 | 56.5035 | 15.5768 | 17.0833 | 15.8369 | 17.7995 | 18.2683 | 45.5042 | 50.5078 | 44.6707 | 21.6454 |  |  | 0.58769 | -0.78401 | -25.6487 | 0.32523 | 0.042844 | -180.2005 | 20.3952 | 0.70275 | 0.22038 | 0.29719 | 0.065391 | 0.00033184 | 0.0003187 | 1.6167 | 21.7671 | 21.9748 | 22.1778 | 22.2256 | 22.0433 | 21.3448 | 20.1487 | 22.1825 | 22.3622 | 22.3948 | 22.3554 | 21.9654 | 21.2039 | 22.2824 | 47.9532 | 28.7408 | 31.8542 | 26.4504 | 23.6027 | 35.0654 | 26.0294 | 22.3447 | 22.1182 | 21.6694 | 22.0692 | 21.7818 | 21.3121 | 21.9461 | 21.5906 | 22.0921 | 37.1159 | 108.4766 | 82.9414 | 49.8768 | 0.46222 | -0.16715 | 43.8697 | 21.9488 | 22.2732 | 20.2344 | 21.5901 | 22.0457 | 21.9128 | 21.7968 | 25.4501 | 21.7798 | 21.4872 | 22.6442 | 100.6593 | 127.257 | 78.6112 | 79.6742 | 56.5508 |  | 37.2803 | 70.7343 | 39.7241 | 56.3206 | 39.1679 | 44.555 |  | 50.4233 |  |  | 21.6303 | 23.1092 | 39.6382 | [5 empty] | 21.8995 | 40.9586 | 21.6756 | 22.0664 | 28.7656 | 21.2377 | 21.8711 | 23.2061 | 51.5308 | 135.7143 |  | 44.4214 | 94.8556 | 20.9537 | 44.6628 | 102.0151 | 32.0766 | 77.3886 | 22.5399 | 73.4481 | 22.4679 | 75.5376 | 18.6032 | 46.1913 | 89.5878 | 24.6181 | 44.7275 | 112.051 | 20.9162 | 42.3361 | 101.1581 | 20.9821 | 69.6659 | 25.7286 | 79.8454 | 22.7534 | 78.3129 | 0.61499 | 19.7239 | 0.90019 | 0.027239 | -27.101 | 3.0952 | 105.04 | 51.54 | 1.0536 | -1.0516 | -6.0151 | 0.67734 | 0.24699 | -16.0182 | 5.3889 | -0.0087402 | -0.31807 | 0.06301 | -0.92029 | -0.19294 | -0.15919 | 0.17097
42838.4237 | 292 | 22.9107 | 22.8785 | 22.8639 | 22.782 | 22.3997 | 21.732 | 22.7203 | 21.7821 | 22.3643 | 22.3719 | 22.3413 | 21.9943 | 21.2113 | 22.1766 | 21.6285 | 21.7904 | 21.9099 | 21.0949 | 21.1982 | 21.4241 | 20.4924 | 20.7387 | 21.9311 | 21.8776 | 21.6947 | 23.9963 | 107.4234 | 95.0011 | 115.2748 | 22.1292 | 21.7537 | 22.9933 | 22.0156 | 21.8006 | 23.6544 | 38.4748 | 116.7417 |  | 59.8195 | 87.9837 | 89.4818 | 62.7751 |  | 16.9792 | 17.3011 | 16.6927 | 17.1473 | 17.3602 | 20.127 | 56.4625 | 15.6203 | 17.0748 | 15.8444 | 17.7886 | 18.2874 | 45.5897 | 50.552 | 44.7206 | 21.6576 |  |  | 0.6672 | -0.62695 | -25.1697 | 0.63473 | 0.23538 | -182.4498 | 20.7106 | 0.73626 | 0.091555 | 0.09536 | 0.114 | 0.00034663 | 0.00031049 | 1.6297 | 21.7713 | 21.9703 | 22.1782 | 22.2301 | 22.0443 | 21.3443 | 20.159 | 22.1854 | 22.3639 | 22.3981 | 22.3493 | 21.9618 | 21.1926 | 22.2724 | 48.4482 | 27.9687 | 30.4738 | 25.37 | 22.8029 | 35.1485 | 26.0322 | 22.3335 | 22.1076 | 21.6567 | 22.0613 | 21.7838 | 21.3057 | 21.9344 | 21.5844 | 22.0979 | 37.1915 | 108.3349 | 83.0509 | 50.3718 | 0.49328 | -0.039911 | 43.8407 | 21.9446 | 22.2706 | 20.2323 | 21.5884 | 22.0415 | 21.9118 | 21.8016 | 25.4741 | 21.779 | 21.4906 | 22.6575 | 101.0601 | 127.7694 | 78.8174 | 79.9387 | 57.0547 |  | 37.4128 | 71.3916 | 39.8328 | 55.7908 | 39.3096 | 44.3424 |  | 50.5791 |  |  | 21.6465 | 23.135 | 39.736 | [5 empty] | 21.8897 | 40.8972 | 21.6682 | 22.0623 | 28.7717 | 21.2295 | 21.8706 | 23.2258 | 51.8058 | 135.7783 |  | 44.9014 | 95.2009 | 20.9506 | 44.7699 | 102.7415 | 32.1939 | 77.5583 | 22.5587 | 73.5386 | 22.4847 | 75.6857 | 18.6046 | 46.6978 | 89.9957 | 24.6554 | 44.8874 | 112.4706 | 20.9344 | 42.5127 | 101.5535 | 21.0039 | 69.813 | 25.7488 | 79.9641 | 22.7672 | 78.6416 | 0.45713 | 19.7209 | 0.90311 | 0.028545 | -27.0666 | 3.0953 | 95.07 | 52.65 | 1.1219 | -0.94042 | -5.9586 | 0.94623 | 0.57902 | -16.1205 | 5.4313 | -0.018159 | -0.33255 | 0.082645 | -0.96552 | -0.039222 | -0.14031 | 0.15983
42838.4237 | 293 | 22.9077 | 22.8762 | 22.8631 | 22.7828 | 22.3916 | 21.7258 | 22.7181 | 21.7777 | 22.3532 | 22.3673 | 22.3372 | 21.9847 | 21.2041 | 22.1641 | 21.6328 | 21.7944 | 21.9191 | 21.1036 | 21.203 | 21.4326 | 20.4936 | 20.747 | 21.9458 | 21.8817 | 21.704 | 24.0176 | 107.6159 | 95.3882 | 115.5927 | 22.1394 | 21.7616 | 23.0019 | 22.0261 | 21.807 | 23.6688 | 38.5882 | 118.0195 |  | 60.0547 | 88.437 | 89.792 | 63.3723 |  | 16.9848 | 17.3007 | 16.6988 | 17.1503 | 17.388 | 20.1123 | 56.4228 | 15.6385 | 17.0812 | 15.7824 | 17.7969 | 18.27 | 45.6504 | 50.5939 | 44.7531 | 21.6446 |  |  | 0.60346 | -0.50144 | -24.9048 | 0.75104 | 0.22026 | -180.5645 | 19.8833 | 0.56476 | 0.12678 | -0.067654 | 0.16886 | 0.00033513 | 0.00030556 | 1.6318 | 21.7685 | 21.9717 | 22.1721 | 22.2223 | 22.0414 | 21.3358 | 20.1538 | 22.1794 | 22.3648 | 22.3886 | 22.3402 | 21.9598 | 21.1906 | 22.2686 | 48.7306 | 28.9774 | 30.3566 | 24.5642 | 22.2531 | 35.2123 | 26.0451 | 22.3306 | 22.0949 | 21.6522 | 22.0514 | 21.7748 | 21.3003 | 21.9349 | 21.5792 | 22.1054 | 37.2752 | 108.1584 | 83.0798 | 50.6551 | 0.23298 | -0.14642 | 44.0285 | 21.9465 | 22.2747 | 20.2336 | 21.5958 | 22.0432 | 21.919 | 21.8087 | 25.5091 | 21.7835 | 21.4996 | 22.6764 | 101.3623 | 128.5238 | 79.0571 | 80.2053 | 57.4744 |  | 37.5344 | 71.9455 | 39.9342 | 55.3276 | 39.4358 | 44.3175 |  | 50.7294 |  |  | 21.6705 | 23.17 | 40.1802 | [5 empty] | 21.8922 | 40.8316 | 21.672 | 22.0689 | 28.775 | 21.2294 | 21.8661 | 23.2616 | 52.1155 | 136.339 |  | 45.249 | 95.5246 | 20.9635 | 44.8719 | 103.1041 | 32.3329 | 77.7626 | 22.5928 | 73.7561 | 22.5158 | 75.836 | 18.6074 | 46.829 | 90.4321 | 24.6941 | 45.0569 | 112.8525 | 20.9522 | 42.6421 | 102.0312 | 21.0209 | 69.9783 | 25.7787 | 80.1724 | 22.785 | 78.7634 | 0.56713 | 19.7203 | 0.90493 | 0.028102 | -27.0757 | 3.0953 | 105.19 | 51.9 | 1.0674 | -0.84104 | -5.9271 | 1.0293 | 0.5601 | -16.0366 | 5.3216 | -0.025615 | -0.34441 | 0.099887 | -0.98938 | -0.024686 | -0.15297 | 0.15485
42838.4237 | 294 | 22.9191 | 22.8846 | 22.8674 | 22.7748 | 22.3986 | 21.7341 | 22.7165 | 21.7786 | 22.3616 | 22.3691 | 22.3394 | 21.9908 | 21.2016 | 22.1711 | 21.6264 | 21.794 | 21.9166 | 21.1018 | 21.1933 | 21.4269 | 20.4871 | 20.7388 | 21.9455 | 21.8761 | 21.6981 | 24.0349 | 107.8723 | 95.7112 | 116.1166 | 22.1375 | 21.755 | 23.0153 | 22.0268 | 21.7991 | 23.6847 | 38.7176 | 118.6071 |  | 60.2783 | 88.7386 | 90.1386 | 64.9056 |  | 16.9883 | 17.2996 | 16.704 | 17.158 | 17.3917 | 20.1089 | 57.0993 | 15.65 | 17.079 | 15.7542 | 17.7999 | 18.2811 | 45.7187 | 50.642 | 44.8141 | 21.6513 |  |  | 0.85382 | -0.29051 | -25.1256 | 0.48688 | 0.2137 | -182.0384 | 20.3005 | 0.73364 | 0.198 | 0.15348 | 0.16782 | 0.00037127 | 0.00032527 | 1.6077 | 21.767 | 21.9744 | 22.1674 | 22.2287 | 22.0372 | 21.3425 | 20.1549 | 22.1822 | 22.3657 | 22.3984 | 22.343 | 21.9667 | 21.1905 | 22.2674 | 47.3967 | 29.6507 | 30.2229 | 24.4087 | 21.786 | 35.2534 | 26.0535 | 22.3327 | 22.0983 | 21.6594 | 22.0537 | 21.7712 | 21.3 | 21.939 | 21.5877 | 22.1214 | 37.3655 | 108.2141 | 83.1502 | 51.0658 | 0.44413 | -0.26492 | 44.1087 | 21.9415 | 22.2683 | 20.232 | 21.5963 | 22.048 | 21.9158 | 21.802 | 25.5401 | 21.7815 | 21.4973 | 22.6874 | 101.6511 | 129.4085 | 79.3664 | 80.5025 | 57.5178 |  | 37.6504 | 71.5283 | 40.0128 | 55.4669 | 39.5908 | 44.2374 |  | 50.8874 |  |  | 21.6899 | 23.1852 | 40.3495 | [5 empty] | 21.8911 | 41.1181 | 21.6692 | 22.0625 | 28.7959 | 21.2253 | 21.866 | 23.2984 | 52.4198 | 137.0952 |  | 45.5674 | 95.8077 | 20.971 | 45.0511 | 103.344 | 32.4381 | 77.983 | 22.6285 | 74.0714 | 22.5267 | 76.0927 | 18.6096 | 46.8008 | 90.773 | 24.733 | 45.2013 | 113.1276 | 20.9623 | 42.6866 | 102.3593 | 21.0287 | 70.1763 | 25.8176 | 80.3712 | 22.8144 | 78.9026 | 0.72814 | 19.7181 | 0.90741 | 0.028284 | -27.127 | 3.0952 | 102.07 | 51.92 | 1.2705 | -0.64015 | -5.9533 | 0.82873 | 0.55168 | -16.1018 | 5.3771 | -0.022806 | -0.3301 | 0.1014 | -0.83633 | -0.0088551 | -0.19108 | 0.14656
42838.4237 | 295 | 22.9098 | 22.8815 | 22.8663 | 22.7863 | 22.4026 | 21.7331 | 22.7249 | 21.7794 | 22.3652 | 22.3766 | 22.3463 | 21.9959 | 21.2025 | 22.1786 | 21.6205 | 21.7862 | 21.9068 | 21.0881 | 21.1816 | 21.4268 | 20.4814 | 20.7316 | 21.9529 | 21.8693 | 21.6926 | 24.0438 | 108.2719 | 95.9542 | 116.5794 | 22.1344 | 21.7583 | 23.0276 | 22.0262 | 21.8113 | 23.7114 | 38.826 | 118.7869 |  | 60.5056 | 88.9857 | 90.4498 | 65.5068 |  | 16.9921 | 17.3062 | 16.7045 | 17.1648 | 17.3955 | 20.0696 | 57.686 | 15.6604 | 17.0743 | 15.7651 | 17.8042 | 18.282 | 45.802 | 50.6677 | 44.8623 | 21.6454 |  |  | 0.66983 | -0.3871 | -25.0087 | 0.56573 | 0.18281 | -181.5075 | 20.7145 | 0.81315 | 0.037651 | 0.30474 | 0.13292 | 0.00032692 | 0.00034499 | 1.6006 | 21.7648 | 21.9688 | 22.1717 | 22.2267 | 22.0363 | 21.3378 | 20.1526 | 22.1768 | 22.3639 | 22.3943 | 22.3481 | 21.9645 | 21.1926 | 22.2667 | 47.7043 | 30.7919 | 31.0132 | 24.4801 | 21.6023 | 35.3208 | 26.0605 | 22.3343 | 22.1028 | 21.6607 | 22.058 | 21.7809 | 21.3018 | 21.9385 | 21.5815 | 22.1322 | 37.4719 | 108.2065 | 83.2573 | 51.6829 | 0.58332 | -0.059882 | 44.0564 | 21.9422 | 22.2621 | 20.2357 | 21.5926 | 22.0438 | 21.911 | 21.8068 | 25.558 | 21.7743 | 21.4937 | 22.6933 | 102.0303 | 130.2788 | 79.6684 | 80.7976 | 56.8533 |  | 37.7616 | 70.5442 | 40.0981 | 55.38 | 39.7589 | 44.8125 |  | 51.0415 |  |  | 21.7134 | 23.2057 | 40.1201 | [5 empty] | 21.8907 | 41.431 | 21.6691 | 22.0649 | 28.8309 | 21.2268 | 21.8709 | 23.3365 | 52.7358 | 137.658 |  | 45.8816 | 96.0245 | 20.9807 | 45.3006 | 103.769 | 32.5416 | 78.1782 | 22.6611 | 74.2873 | 22.5522 | 76.3429 | 18.5988 | 46.9116 | 91.082 | 24.7649 | 45.3289 | 113.2733 | 20.981 | 42.8379 | 102.705 | 21.0413 | 70.336 | 25.8657 | 80.6356 | 22.8249 | 79.2995 | 0.72387 | 19.7169 | 0.90935 | 0.028799 | -27.3016 | 3.0953 | 119.17 | 52.84 | 1.126 | -0.73896 | -5.9395 | 0.89333 | 0.51022 | -16.0772 | 5.4313 | -0.00050182 | -0.2998 | 0.10965 | -0.86257 | -0.095837 | -0.20402 | 0.1331
42838.4237 | 296 | 22.9189 | 22.8726 | 22.8659 | 22.7731 | 22.3958 | 21.7249 | 22.7094 | 21.7826 | 22.3645 | 22.3665 | 22.3351 | 21.9929 | 21.1926 | 22.1619 | 21.6276 | 21.7892 | 21.9004 | 21.0863 | 21.1889 | 21.4237 | 20.4806 | 20.7369 | 21.9685 | 21.8673 | 21.6855 | 24.0599 | 108.762 | 96.1522 | 117.5968 | 22.1337 | 21.762 | 23.0298 | 22.0228 | 21.8079 | 23.7232 | 38.9411 | 118.2276 |  | 60.7031 | 89.2532 | 90.833 | 63.999 |  | 17.0034 | 17.3045 | 16.7056 | 17.1645 | 17.3838 | 20.0167 | 57.1222 | 15.6329 | 17.0761 | 15.7951 | 17.8123 | 18.2832 | 45.8763 | 50.7012 | 44.9118 | 21.6492 |  |  | 0.6948 | -0.23531 | -25.1841 | 0.65904 | 0.23209 | -179.4842 | 20.1435 | 0.48919 | -0.26301 | 0.069135 | 0.1883 | 0.00036963 | 0.0003647 | 1.6148 | 21.7661 | 21.9703 | 22.17 | 22.2263 | 22.0356 | 21.3389 | 20.151 | 22.1873 | 22.361 | 22.39 | 22.3488 | 21.9628 | 21.1923 | 22.27 | 49.6772 | 34.0344 | 35.157 | 24.5038 | 21.6743 | 35.4156 | 26.1173 | 22.3287 | 22.0981 | 21.653 | 22.0557 | 21.7665 | 21.3069 | 21.9238 | 21.5791 | 22.1347 | 37.5676 | 108.6024 | 83.4662 | 51.9854 | 0.46359 | 0.16684 | 44.0373 | 21.9485 | 22.266 | 20.2413 | 21.594 | 22.0432 | 21.9162 | 21.8116 | 25.5846 | 21.7772 | 21.4988 | 22.7075 | 102.556 | 130.8914 | 79.9323 | 81.0509 | 56.4736 |  | 37.8682 | 70.5239 | 40.1748 | 55.6147 | 39.9186 | 45.1056 |  | 51.184 |  |  | 21.7285 | 23.2264 | 40.1119 | [5 empty] | 21.8957 | 41.6479 | 21.6781 | 22.0739 | 28.8727 | 21.2292 | 21.8742 | 23.3732 | 53.0418 | 138.3707 |  | 46.0166 | 96.2791 | 20.9906 | 45.4931 | 104.3252 | 32.6459 | 78.3685 | 22.6833 | 74.5093 | 22.5747 | 76.5084 | 18.5755 | 47.2575 | 91.4228 | 24.7902 | 45.4517 | 113.5661 | 21.0104 | 43.0592 | 103.0469 | 21.059 | 70.5182 | 25.922 | 80.8169 | 22.8386 | 79.6634 | 0.51815 | 19.7125 | 0.91252 | 0.028124 | -27.0286 | 3.0953 | 113.31 | 51.3 | 1.1483 | -0.57614 | -5.9603 | 0.96419 | 0.57485 | -15.9859 | 5.3554 | 0.013735 | -0.29657 | 0.10868 | -1.0706 | -0.54961 | -0.15814 | 0.12801
42838.4237 | 297 | 22.9268 | 22.878 | 22.8694 | 22.7811 | 22.3959 | 21.7301 | 22.7191 | 21.7805 | 22.3693 | 22.3678 | 22.3463 | 21.9987 | 21.2072 | 22.1693 | 21.6325 | 21.7907 | 21.9125 | 21.0901 | 21.197 | 21.4261 | 20.484 | 20.7368 | 21.9769 | 21.8745 | 21.6872 | 24.0836 | 109.2509 | 96.315 | 118.4894 | 22.1338 | 21.767 | 23.0505 | 22.022 | 21.8001 | 23.7378 | 39.0375 | 118.0272 |  | 60.9047 | 89.5836 | 91.0946 | 63.357 |  | 16.9996 | 17.3122 | 16.7152 | 17.1587 | 17.3768 | 20.0267 | 56.9099 | 15.5766 | 17.0679 | 15.8294 | 17.8095 | 18.291 | 45.9476 | 50.7417 | 44.9827 | 21.6529 |  |  | 0.6948 | -0.44099 | -25.4575 | 0.38568 | 0.15192 | -180.8188 | 20.3807 | 0.53782 | 0.028116 | 0.12641 | 0.12424 | 0.0003877 | 0.00036963 | 1.6157 | 21.7696 | 21.9706 | 22.1691 | 22.2265 | 22.0442 | 21.3407 | 20.1505 | 22.1862 | 22.3567 | 22.3973 | 22.3471 | 21.9621 | 21.1927 | 22.2724 | 50.1415 | 36.3366 | 38.3924 | 25.9098 | 22.4502 | 35.4984 | 26.1995 | 22.3359 | 22.098 | 21.6614 | 22.0595 | 21.7768 | 21.3004 | 21.9359 | 21.5921 | 22.1521 | 37.6542 | 108.9946 | 83.6617 | 52.0489 | 0.59571 | -0.12189 | 44.0546 | 21.9485 | 22.2758 | 20.2416 | 21.596 | 22.0528 | 21.9208 | 21.8152 | 25.6148 | 21.7819 | 21.5028 | 22.7256 | 103.1166 | 131.6235 | 80.2607 | 81.3203 | 55.9681 |  | 37.9557 | 71.7178 | 40.2782 | 54.9873 | 40.0382 | 45.0649 |  | 51.33 |  |  | 21.7322 | 23.2331 | 40.1438 | [5 empty] | 21.8915 | 41.4498 | 21.6721 | 22.069 | 28.8934 | 21.2284 | 21.8689 | 23.4116 | 53.3193 | 138.6361 |  | 46.0155 | 96.573 | 20.9965 | 45.5396 | 104.7911 | 32.7595 | 78.555 | 22.6891 | 74.7965 | 22.5867 | 76.6358 | 18.5668 | 47.8182 | 91.8679 | 24.8322 | 45.5873 | 113.8812 | 21.0419 | 43.2321 | 103.3471 | 21.0826 | 70.6417 | 25.9673 | 80.9652 | 22.8623 | 79.8078 | 0.56045 | 19.7127 | 0.91551 | 0.027558 | -27.1368 | 3.0953 | 109.03 | 52.6 | 1.1496 | -0.78873 | -5.9927 | 0.73761 | 0.4651 | -16.0455 | 5.3869 | 0.030801 | -0.32613 | 0.13026 | -1.1124 | -0.89946 | -0.13697 | 0.12924
42838.4237 | 298 | 22.9228 | 22.8789 | 22.868 | 22.7887 | 22.3975 | 21.7278 | 22.7173 | 21.7753 | 22.3726 | 22.3643 | 22.3381 | 21.9957 | 21.2042 | 22.1725 | 21.6339 | 21.7917 | 21.915 | 21.0922 | 21.1933 | 21.4312 | 20.4815 | 20.7416 | 21.9835 | 21.8731 | 21.6923 | 24.0985 | 109.6878 | 96.4011 | 118.4973 | 22.1248 | 21.7586 | 23.0612 | 22.0245 | 21.8035 | 23.7547 | 39.1521 | 118.5754 |  | 61.111 | 89.8968 | 91.3743 | 63.4562 |  | 17.0135 | 17.3244 | 16.7282 | 17.1721 | 17.3861 | 20.0381 | 57.078 | 15.5838 | 17.0785 | 15.8152 | 17.8228 | 18.2946 | 46.0227 | 50.7762 | 45.0522 | 21.6526 |  |  | 0.67706 | -0.40025 | -25.5514 | 0.44745 | 0.26429 | -180.5888 | 20.4313 | 0.56279 | 0.3204 | 0.11131 | 0.24264 | 0.00039098 | 0.00034499 | 1.623 | 21.7703 | 21.9767 | 22.1644 | 22.2273 | 22.043 | 21.3413 | 20.1534 | 22.1856 | 22.3584 | 22.3992 | 22.3496 | 21.9679 | 21.1937 | 22.2711 | 52.6811 | 39.1424 | 40.0887 | 27.1108 | 23.5085 | 35.6151 | 26.2734 | 22.333 | 22.0945 | 21.6627 | 22.0596 | 21.7787 | 21.3028 | 21.9333 | 21.5926 | 22.1594 | 37.7345 | 109.3979 | 83.7779 | 52.0213 | 0.56524 | 0.33307 | 44.2383 | 21.946 | 22.267 | 20.2363 | 21.5889 | 22.0443 | 21.9159 | 21.8158 | 25.6421 | 21.7801 | 21.4976 | 22.7323 | 103.4328 | 132.3712 | 80.5867 | 81.656 | 55.139 |  | 38.0557 | 72.3605 | 40.4168 | 55.7765 | 40.2019 | 45.0462 |  | 51.4962 |  |  | 21.7459 | 23.2527 | 40.2503 | [5 empty] | 21.891 | 41.9845 | 21.6765 | 22.0674 | 28.951 | 21.2269 | 21.8724 | 23.4283 | 53.564 | 139.0462 |  | 46.1279 | 96.9609 | 20.9982 | 45.5629 | 105.0956 | 32.921 | 78.7379 | 22.6893 | 75.2165 | 22.6087 | 76.8623 | 18.5574 | 48.4217 | 92.2235 | 24.8758 | 45.7568 | 114.0789 | 21.0462 | 43.3465 | 103.6902 | 21.0931 | 70.6956 | 26.0111 | 81.2015 | 22.8797 | 80.0441 | 0.69252 | 19.7089 | 0.91696 | 0.027543 | -27.1506 | 3.0953 | 114.8 | 51.93 | 1.1348 | -0.75143 | -6.0038 | 0.7945 | 0.61345 | -16.0356 | 5.3937 | 0.057294 | -0.33917 | 0.11402 | -1.3809 | -1.0793 | -0.13575 | 0.13278
42838.4237 | 299 | 22.9197 | 22.876 | 22.8645 | 22.7833 | 22.4017 | 21.7222 | 22.7157 | 21.7734 | 22.3705 | 22.3612 | 22.3364 | 21.9963 | 21.2054 | 22.1716 | 21.638 | 21.796 | 21.9219 | 21.0991 | 21.197 | 21.4381 | 20.4945 | 20.7469 | 21.9976 | 21.8851 | 21.7074 | 24.1215 | 109.9838 | 96.5331 | 118.9026 | 22.1245 | 21.755 | 23.0749 | 22.017 | 21.8053 | 23.7687 | 39.2448 | 119.4429 |  | 61.3182 | 90.2135 | 91.7102 | 63.7458 |  | 17.0185 | 17.3225 | 16.7217 | 17.1651 | 17.383 | 19.9918 | 57.5675 | 15.6 | 17.0737 | 15.777 | 17.8254 | 18.2841 | 46.1011 | 50.7967 | 45.1019 | 21.6442 |  |  | 0.64486 | -0.32994 | -25.7795 | 0.42708 | 0.12367 | -180.7537 | 20.0607 | 0.79344 | 0.078712 | 0.04291 | 0.06487 | 0.00034663 | 0.00034006 | 1.625 | 21.7632 | 21.9727 | 22.1698 | 22.2275 | 22.0408 | 21.3385 | 20.153 | 22.1756 | 22.3684 | 22.4016 | 22.3487 | 21.964 | 21.1932 | 22.2682 | 54.4961 | 40.3313 | 41.795 | 27.9142 | 24.3329 | 35.7336 | 26.386 | 22.3354 | 22.0959 | 21.6593 | 22.0549 | 21.7787 | 21.3077 | 21.9389 | 21.5924 | 22.1707 | 37.8239 | 110.1355 | 83.8584 | 51.8937 | 0.53024 | -0.037438 | 44.3968 | 21.9451 | 22.2658 | 20.2341 | 21.5909 | 22.0391 | 21.9176 | 21.8171 | 25.6695 | 21.7807 | 21.4949 | 22.7474 | 103.9408 | 132.9715 | 80.9259 | 81.9864 | 55.4889 |  | 38.1772 | 72.7027 | 40.5381 | 56.705 | 40.3722 | 45.3651 |  | 51.6961 |  |  | 21.7474 | 23.2546 | 40.5029 | [5 empty] | 21.8855 | 42.5809 | 21.6695 | 22.0572 | 29.0251 | 21.2257 | 21.8747 | 23.4622 | 53.8287 | 139.682 |  | 46.3725 | 97.3306 | 21.006 | 45.7167 | 105.5505 | 33.0804 | 78.9393 | 22.7033 | 75.8233 | 22.6423 | 77.1857 | 18.5529 | 48.722 | 92.5463 | 24.9177 | 45.9706 | 114.3319 | 21.0531 | 43.5167 | 104.0736 | 21.1035 | 70.8174 | 26.0624 | 81.395 | 22.8979 | 80.3879 | 0.44358 | 19.6954 | 0.91947 | 0.02758 | -27.0808 | 3.0953 | 117.64 | 51.92 | 1.1081 | -0.68224 | -6.0305 | 0.7762 | 0.4196 | -16.0417 | 5.3442 | 0.05178 | -0.34446 | 0.094157 | -1.5686 | -1.2557 | -0.14058 | 0.13942
42838.4238 | 300 | 22.9102 | 22.8741 | 22.8588 | 22.776 | 22.3915 | 21.7162 | 22.7111 | 21.7725 | 22.3585 | 22.3565 | 22.3336 | 21.9928 | 21.202 | 22.1622 | 21.6323 | 21.7932 | 21.9097 | 21.0979 | 21.1926 | 21.4227 | 20.4841 | 20.747 | 22.0061 | 21.881 | 21.7056 | 24.1341 | 110.1546 | 96.638 | 119.2622 | 22.1237 | 21.7563 | 23.0826 | 22.0105 | 21.798 | 23.7786 | 39.3409 | 120.1039 |  | 61.5295 | 90.5706 | 92.022 | 63.6077 |  | 17.0244 | 17.3414 | 16.7265 | 17.1819 | 17.3805 | 19.9667 | 57.8099 | 15.6062 | 17.0753 | 15.7043 | 17.8265 | 18.2956 | 46.1918 | 50.8358 | 45.1675 | 21.6558 |  |  | 0.77037 | -0.43508 | -26.2736 | 0.55653 | 0.17492 | -179.3344 | 20.3531 | 0.52599 | 0.093501 | 0.012489 | 0.16834 | 0.00034827 | 0.00035484 | 1.5988 | 21.7725 | 21.9779 | 22.1694 | 22.23 | 22.047 | 21.3374 | 20.1607 | 22.1809 | 22.3505 | 22.393 | 22.3448 | 21.9638 | 21.1939 | 22.274 | 54.6386 | 40.2552 | 42.7213 | 29.2056 | 24.9464 | 35.8417 | 26.4774 | 22.3378 | 22.098 | 21.6662 | 22.0592 | 21.7813 | 21.3146 | 21.9427 | 21.595 | 22.1837 | 37.9146 | 110.4854 | 83.9431 | 51.5919 | 0.010825 | 0.15942 | 44.5102 | 21.9457 | 22.2642 | 20.2377 | 21.5987 | 22.0437 | 21.9197 | 21.8206 | 25.6956 | 21.7847 | 21.4972 | 22.7613 | 104.596 | 133.7139 | 81.2663 | 82.2887 | 55.8341 |  | 38.2639 | 74.2143 | 40.6491 | 56.4605 | 40.5305 | 45.6234 |  | 51.8692 |  |  | 21.7552 | 23.2738 | 40.5814 | [5 empty] | 21.8918 | 43.2289 | 21.6722 | 22.0582 | 29.0263 | 21.228 | 21.8784 | 23.4921 | 54.1273 | 140.1839 |  | 46.4889 | 97.6395 | 21.0124 | 45.8808 | 106.0924 | 33.2139 | 79.1431 | 22.7153 | 76.3016 | 22.6675 | 77.4415 | 18.553 | 48.8349 | 92.9226 | 24.9472 | 46.1893 | 114.4945 | 21.0616 | 43.8109 | 104.5394 | 21.1077 | 71.056 | 26.1093 | 81.5387 | 22.9035 | 80.6737 | 0.58549 | 19.6924 | 0.92281 | 0.028661 | -27.0744 | 3.0952 | 82.04 | 52.6 | 1.2117 | -0.78346 | -6.0883 | 0.88609 | 0.49901 | -15.9779 | 5.3827 | 0.045195 | -0.38259 | 0.10645 | -1.5717 | -1.3479 | -0.13341 | 0.15094
42838.4238 | 301 | 22.9157 | 22.8741 | 22.8584 | 22.7818 | 22.3967 | 21.7204 | 22.7129 | 21.7752 | 22.3598 | 22.3675 | 22.3349 | 21.9876 | 21.1993 | 22.1768 | 21.6232 | 21.7945 | 21.9105 | 21.0894 | 21.1905 | 21.427 | 20.4859 | 20.7466 | 22.0148 | 21.8719 | 21.701 | 24.1581 | 110.5533 | 96.8071 | 120.5153 | 22.1287 | 21.7553 | 23.0996 | 22.0179 | 21.8047 | 23.8026 | 39.442 | 120.539 |  | 61.7562 | 91.017 | 92.3133 | 63.2512 |  | 17.0183 | 17.3534 | 16.7325 | 17.1692 | 17.3712 | 19.9479 | 58.0179 | 15.6086 | 17.071 | 15.7179 | 17.8285 | 18.2949 | 46.2537 | 50.8634 | 45.2414 | 21.644 |  |  | 0.681 | -0.36608 | -26.5798 | 0.61107 | 0.33132 | -179.9783 | 19.7597 | 0.6837 | -0.025788 | 0.11823 | 0.040219 | 0.00033513 | 0.00035649 | 1.574 | 21.7638 | 21.9717 | 22.1657 | 22.2251 | 22.0424 | 21.3321 | 20.1476 | 22.1834 | 22.3587 | 22.3925 | 22.3456 | 21.9668 | 21.1887 | 22.2677 | 53.5185 | 39.2593 | 43.5809 | 29.9055 | 25.6821 | 35.8992 | 26.5787 | 22.3363 | 22.1029 | 21.6619 | 22.0561 | 21.7778 | 21.3039 | 21.9355 | 21.596 | 22.1843 | 38.0028 | 110.4739 | 84.0023 | 51.6443 | 0.22512 | -0.024885 | 44.7289 | 21.9438 | 22.2662 | 20.245 | 21.5976 | 22.0471 | 21.9198 | 21.8261 | 25.7227 | 21.7865 | 21.5053 | 22.7787 | 105.1123 | 134.5227 | 81.5532 | 82.5939 | 55.5364 |  | 38.3554 | 75.6829 | 40.771 | 56.199 | 40.6921 | 45.4309 |  | 51.9985 |  |  | 21.7834 | 23.2961 | 40.4773 | [5 empty] | 21.896 | 43.6205 | 21.6772 | 22.0532 | 29.06 | 21.2325 | 21.861 | 23.5371 | 54.415 | 141.4425 |  | 46.512 | 97.9195 | 21.019 | 45.9919 | 106.5115 | 33.3335 | 79.3161 | 22.7398 | 76.6333 | 22.6845 | 77.5844 | 18.5624 | 49.0701 | 93.3871 | 24.979 | 46.3461 | 114.6247 | 21.0703 | 43.9945 | 104.9669 | 21.1103 | 71.3338 | 26.1413 | 81.7116 | 22.9121 | 80.8491 | 0.67973 | 19.6897 | 0.92559 | 0.029467 | -27.1884 | 3.0952 | 111.28 | 51.51 | 1.1411 | -0.71867 | -6.1238 | 0.92852 | 0.68674 | -16.006 | 5.3035 | 0.05663 | -0.41914 | 0.11933 | -1.4405 | -1.4315 | -0.12 | 0.15254
42838.4238 | 302 | 22.9097 | 22.8754 | 22.8613 | 22.7839 | 22.401 | 21.7253 | 22.7191 | 21.7818 | 22.3617 | 22.3733 | 22.34 | 21.9888 | 21.2013 | 22.1766 | 21.6295 | 21.7944 | 21.9164 | 21.0926 | 21.1946 | 21.4319 | 20.4942 | 20.7521 | 22.0215 | 21.8772 | 21.7077 | 24.1806 | 110.7769 | 97.0304 | 120.5186 | 22.1262 | 21.7719 | 23.1126 | 22.0249 | 21.8173 | 23.821 | 39.5482 | 121.2829 |  | 62.0215 | 91.4482 | 92.6269 | 63.774 |  | 17.0215 | 17.3615 | 16.7411 | 17.1854 | 17.3729 | 20.0302 | 58.4725 | 15.5985 | 17.0776 | 15.7064 | 17.8394 | 18.3004 | 46.3297 | 50.8849 | 45.3129 | 21.6478 |  |  | 0.64486 | -0.36082 | -26.4681 | 0.57033 | 0.25838 | -181.012 | 19.7729 | 0.55424 | 0.18321 | 0.20047 | 0.12546 | 0.00035484 | 0.00032856 | 1.5681 | 21.7569 | 21.9622 | 22.1633 | 22.2226 | 22.0378 | 21.3335 | 20.1457 | 22.1842 | 22.356 | 22.3932 | 22.3449 | 21.9634 | 21.1927 | 22.2657 | 52.4246 | 36.3621 | 40.9944 | 30.2229 | 25.621 | 35.952 | 26.633 | 22.3388 | 22.1003 | 21.6608 | 22.0612 | 21.7769 | 21.3147 | 21.9409 | 21.5918 | 22.2005 | 38.1042 | 110.3294 | 84.0269 | 52.2172 | 0.48876 | -0.20843 | 44.9306 | 21.9427 | 22.2679 | 20.2456 | 21.5889 | 22.04 | 21.9152 | 21.822 | 25.7436 | 21.7785 | 21.4999 | 22.7908 | 105.5826 | 135.0547 | 81.8782 | 82.9144 | 54.8066 |  | 38.4745 | 75.6424 | 40.9144 | 55.9643 | 40.9061 | 45.5553 |  | 52.145 |  |  | 21.7975 | 23.3157 | 40.4864 | [5 empty] | 21.9018 | 44.2117 | 21.6789 | 22.0653 | 29.0795 | 21.2391 | 21.8761 | 23.5791 | 54.643 | 142.2875 |  | 46.6761 | 98.3251 | 21.0237 | 46.0923 | 106.7753 | 33.4568 | 79.5145 | 22.755 | 76.8938 | 22.6984 | 77.7647 | 18.5619 | 49.2545 | 93.774 | 25.0152 | 46.4629 | 114.6774 | 21.0855 | 44.1023 | 105.4845 | 21.108 | 71.541 | 26.1707 | 81.9988 | 22.934 | 80.9521 | 0.66025 | 19.6875 | 0.92941 | 0.02967 | -27.0807 | 3.0952 | 100.94 | 52.71 | 1.1104 | -0.7135 | -6.111 | 0.89704 | 0.60655 | -16.0542 | 5.306 | 0.081031 | -0.41302 | 0.1333 | -1.3127 | -1.1378 | -0.13083 | 0.14014
42838.4238 | 303 | 22.9106 | 22.8709 | 22.8615 | 22.7784 | 22.3923 | 21.7214 | 22.7066 | 21.7769 | 22.3564 | 22.3626 | 22.3291 | 21.9968 | 21.192 | 22.1555 | 21.6261 | 21.7903 | 21.9139 | 21.0985 | 21.1922 | 21.4315 | 20.4822 | 20.7473 | 22.0291 | 21.8785 | 21.7059 | 24.1984 | 111.0418 | 97.2317 | 120.4488 | 22.1225 | 21.7584 | 23.1323 | 22.0203 | 21.8042 | 23.8378 | 39.6462 | 122.2798 |  | 62.3015 | 91.7697 | 92.8734 | 64.8682 |  | 17.0253 | 17.3722 | 16.7364 | 17.1791 | 17.3802 | 20.1768 | 59.4315 | 15.6078 | 17.065 | 15.7043 | 17.8337 | 18.3 | 46.4092 | 50.9163 | 45.3774 | 21.6473 |  |  | 0.76051 | -0.29183 | -26.1317 | 0.50791 | 0.35563 | -181.5567 | 20.2697 | 0.53256 | 0.25113 | -0.026324 | 0.16886 | 0.0003417 | 0.00032527 | 1.5811 | 21.757 | 21.9688 | 22.1636 | 22.227 | 22.0402 | 21.3366 | 20.1515 | 22.1885 | 22.3612 | 22.3914 | 22.3419 | 21.9648 | 21.189 | 22.2682 | 52.2728 | 36.6907 | 38.9582 | 29.6124 | 26.233 | 36.0335 | 26.6851 | 22.3409 | 22.1054 | 21.6614 | 22.0633 | 21.766 | 21.3155 | 21.9346 | 21.5883 | 22.2157 | 38.2222 | 110.2167 | 84.1152 | 53.1676 | 0.62166 | 0.23702 | 45.0853 | 21.9392 | 22.2606 | 20.2419 | 21.5872 | 22.0371 | 21.9117 | 21.8195 | 25.7686 | 21.7763 | 21.4949 | 22.799 | 105.972 | 135.5245 | 82.2561 | 83.2727 | 54.8281 |  | 38.5759 | 75.7462 | 41.0425 | 56.474 | 41.0758 | 46.0678 |  | 52.2866 |  |  | 21.7892 | 23.3319 | 40.6225 | [5 empty] | 21.8946 | 44.6346 | 21.6766 | 22.067 | 29.1055 | 21.2327 | 21.8688 | 23.6136 | 54.9072 | 143.0585 |  | 47.0198 | 98.604 | 21.0312 | 46.3858 | 107.2396 | 33.5716 | 79.7364 | 22.7865 | 77.2457 | 22.7223 | 78.0494 | 18.5711 | 49.4335 | 94.0695 | 25.0519 | 46.5801 | 114.793 | 21.0983 | 44.2684 | 105.8963 | 21.1012 | 71.7509 | 26.1954 | 82.2658 | 22.943 | 81.3201 | 0.52502 | 19.6864 | 0.93197 | 0.029685 | -27.1435 | 3.0952 | 111.3 | 51.4 | 1.2057 | -0.64168 | -6.0721 | 0.84654 | 0.71178 | -16.0823 | 5.3736 | 0.083944 | -0.41145 | 0.12505 | -1.2862 | -0.90542 | -0.15783 | 0.11782
42838.4238 | 304 | 22.9048 | 22.8721 | 22.8603 | 22.7763 | 22.3928 | 21.7215 | 22.7076 | 21.769 | 22.3561 | 22.3722 | 22.3398 | 21.9838 | 21.198 | 22.162 | 21.6253 | 21.7898 | 21.9157 | 21.0958 | 21.187 | 21.426 | 20.4784 | 20.7454 | 22.0386 | 21.8669 | 21.7029 | 24.2066 | 111.3994 | 97.5453 | 120.6821 | 22.132 | 21.7665 | 23.1507 | 22.0235 | 21.8187 | 23.8565 | 39.7633 | 121.7112 |  | 62.5641 | 92.156 | 93.1796 | 65.6831 |  | 17.0337 | 17.3724 | 16.7438 | 17.199 | 17.4156 | 20.2119 | 60.1197 | 15.6426 | 17.0629 | 15.6917 | 17.8358 | 18.3019 | 46.4744 | 50.9258 | 45.4281 | 21.641 |  |  | 1.1462 | -0.4469 | -26.064 | 0.51513 | 0.1723 | -179.5361 | 19.8616 | 0.53716 | 0.049133 | 0.15683 | 0.10896 | 0.00035156 | 0.00034006 | 1.5878 | 21.7602 | 21.9699 | 22.1677 | 22.2315 | 22.0341 | 21.336 | 20.1459 | 22.1837 | 22.3544 | 22.3881 | 22.3395 | 21.9654 | 21.1839 | 22.2695 | 54.2121 | 38.923 | 40.4501 | 29.324 | 26.0244 | 36.1598 | 26.7647 | 22.3362 | 22.0989 | 21.6626 | 22.0721 | 21.7806 | 21.3136 | 21.941 | 21.5887 | 22.2209 | 38.3549 | 110.187 | 84.1856 | 54.0824 | 0.60672 | -0.075669 | 45.2359 | 21.939 | 22.2627 | 20.2454 | 21.592 | 22.045 | 21.9133 | 21.8232 | 25.7993 | 21.7793 | 21.5026 | 22.8107 | 106.3394 | 135.9718 | 82.6036 | 83.6247 | 54.6604 |  | 38.66 | 77.0425 | 41.1916 | 56.1455 | 41.2072 | 46.4246 |  | 52.4204 |  |  | 21.8127 | 23.3475 | 40.7349 | [5 empty] | 21.8952 | 44.1913 | 21.6755 | 22.0668 | 29.1322 | 21.2331 | 21.8709 | 23.6646 | 55.1829 | 143.5882 |  | 47.2379 | 98.8436 | 21.0514 | 46.7463 | 107.6227 | 33.7095 | 79.9356 | 22.8018 | 77.6522 | 22.7581 | 78.5966 | 18.5827 | 49.5596 | 94.2881 | 25.0958 | 46.7716 | 114.92 | 21.1103 | 44.525 | 106.5998 | 21.1136 | 72.0157 | 26.2277 | 82.3827 | 22.9647 | 81.6845 | 0.69865 | 19.6839 | 0.93487 | 0.030062 | -27.1078 | 3.0952 | 105.26 | 51.69 | 1.4807 | -0.79408 | -6.0643 | 0.85254 | 0.49546 | -15.9935 | 5.3196 | 0.09152 | -0.44227 | 0.13875 | -1.4868 | -1.0619 | -0.17639 | 0.097004
42838.4238 | 305 | 22.9133 | 22.8756 | 22.8656 | 22.7805 | 22.3936 | 21.7265 | 22.717 | 21.775 | 22.3602 | 22.3687 | 22.3362 | 21.9935 | 21.204 | 22.1718 | 21.6201 | 21.7887 | 21.9105 | 21.0958 | 21.1892 | 21.4282 | 20.4786 | 20.7446 | 22.0485 | 21.8754 | 21.7064 | 24.2255 | 111.9131 | 97.9384 | 121.74 | 22.1357 | 21.7704 | 23.1597 | 22.0305 | 21.8155 | 23.8728 | 39.8782 | 121.6714 |  | 62.8027 | 92.4874 | 93.4826 | 66.1845 |  | 17.0348 | 17.3811 | 16.7532 | 17.2047 | 17.4507 | 20.2368 | 61.0654 | 15.6596 | 17.0708 | 15.6383 | 17.8501 | 18.2989 | 46.556 | 50.9439 | 45.4941 | 21.6492 |  |  | 0.68363 | -0.2202 | -26.3045 | 0.40934 | 0.23866 | -179.1872 | 19.9917 | 0.66333 | 0.24529 | 0.2011 | 0.13744 | 0.00037949 | 0.00031542 | 1.5756 | 21.7638 | 21.9733 | 22.1693 | 22.234 | 22.0447 | 21.3356 | 20.1538 | 22.1859 | 22.3596 | 22.3957 | 22.3456 | 21.9743 | 21.1912 | 22.2707 | 55.3037 | 38.0266 | 38.9261 | 29.5804 | 25.853 | 36.3037 | 26.8174 | 22.3251 | 22.0967 | 21.6607 | 22.0617 | 21.7772 | 21.3107 | 21.9349 | 21.5939 | 22.236 | 38.4891 | 110.4304 | 84.2525 | 54.5028 | 0.52828 | 0.025898 | 45.4416 | 21.9383 | 22.2658 | 20.2543 | 21.5958 | 22.0466 | 21.9125 | 21.8268 | 25.8331 | 21.7756 | 21.5022 | 22.8266 | 106.6726 | 136.246 | 82.8991 | 83.9493 | 54.3616 |  | 38.766 | 77.2833 | 41.349 | 55.6311 | 41.3463 | 46.6428 |  | 52.5555 |  |  | 21.8306 | 23.3528 | 41.0076 | [5 empty] | 21.8992 | 43.8604 | 21.6745 | 22.0694 | 29.1522 | 21.2357 | 21.8839 | 23.7013 | 55.4908 | 144.6192 |  | 47.2875 | 99.2448 | 21.0642 | 46.8932 | 107.9573 | 33.8048 | 80.1236 | 22.8272 | 78.0236 | 22.7837 | 78.8934 | 18.5969 | 49.6323 | 94.6643 | 25.1386 | 46.9901 | 115.0542 | 21.1402 | 44.6684 | 107.4458 | 21.1336 | 72.2812 | 26.2679 | 82.3866 | 23.0018 | 81.8457 | 0.72443 | 19.6801 | 0.9377 | 0.029983 | -26.9817 | 3.0953 | 103.25 | 52.74 | 1.145 | -0.55741 | -6.0923 | 0.75998 | 0.58315 | -15.9787 | 5.3372 | 0.10349 | -0.44347 | 0.15788 | -1.5912 | -0.88634 | -0.18633 | 0.089971
42838.4238 | 306 | 22.9077 | 22.8675 | 22.8579 | 22.7743 | 22.3871 | 21.7191 | 22.7092 | 21.7657 | 22.3565 | 22.3591 | 22.3285 | 21.9801 | 21.1953 | 22.1653 | 21.6212 | 21.7899 | 21.9083 | 21.0886 | 21.1894 | 21.4295 | 20.4824 | 20.7426 | 22.0484 | 21.872 | 21.698 | 24.2483 | 112.4492 | 98.329 | 121.71 | 22.1271 | 21.7604 | 23.1661 | 22.0186 | 21.8097 | 23.8854 | 40.0083 | 121.9553 |  | 63.0231 | 92.7809 | 93.834 | 66.8006 |  | 17.0518 | 17.401 | 16.7499 | 17.2127 | 17.4822 | 20.2709 | 61.7025 | 15.6284 | 17.071 | 15.5646 | 17.8567 | 18.3139 | 46.6372 | 50.9542 | 45.5476 | 21.654 |  |  | 0.70597 | -0.42325 | -26.8111 | 0.22732 | 0.009988 | -179.1484 | 19.9641 | 0.29468 | -0.016253 | 0.086968 | 0.06487 | 0.00034334 | 0.00029899 | 1.584 | 21.7645 | 21.9616 | 22.1647 | 22.2187 | 22.0367 | 21.3287 | 20.1452 | 22.1814 | 22.3583 | 22.3938 | 22.3401 | 21.9579 | 21.1889 | 22.2605 | 55.6076 | 38.978 | 37.7665 | 29.6347 | 26.0093 | 36.4229 | 26.8675 | 22.3367 | 22.102 | 21.6659 | 22.0669 | 21.7731 | 21.3141 | 21.9369 | 21.5964 | 22.2367 | 38.6176 | 110.5154 | 84.313 | 55.0673 | 0.45711 | 0.07535 | 45.5011 | 21.9333 | 22.2638 | 20.2528 | 21.5947 | 22.0401 | 21.915 | 21.8274 | 25.8618 | 21.7788 | 21.499 | 22.8413 | 106.9779 | 136.5124 | 83.1628 | 84.2548 | 54.4042 |  | 38.8842 | 77.4352 | 41.483 | 56.4498 | 41.5339 | 47.17 |  | 52.7101 |  |  | 21.8452 | 23.3622 | 41.1681 | [5 empty] | 21.8951 | 43.9009 | 21.679 | 22.0665 | 29.1971 | 21.24 | 21.8804 | 23.7427 | 55.7613 | 146.11 |  | 47.3644 | 99.6943 | 21.0724 | 46.8608 | 108.3066 | 33.9253 | 80.3127 | 22.8602 | 78.3565 | 22.8131 | 79.1089 | 18.5992 | 49.7025 | 95.0946 | 25.161 | 47.2023 | 115.0696 | 21.1723 | 44.7582 | 107.9902 | 21.1408 | 72.5453 | 26.3097 | 82.4975 | 23.0264 | 82.0437 | 0.48347 | 19.6791 | 0.93995 | 0.029293 | -27.1642 | 3.0952 | 105.85 | 51.78 | 1.1635 | -0.77282 | -6.1509 | 0.56636 | 0.1193 | -15.9779 | 5.3338 | 0.10641 | -0.44303 | 0.14168 | -1.6109 | -0.75163 | -0.19893 | 0.078745
42838.4238 | 307 | 22.9127 | 22.8767 | 22.8612 | 22.7765 | 22.3911 | 21.7245 | 22.717 | 21.7707 | 22.3628 | 22.3661 | 22.3324 | 21.9845 | 21.204 | 22.171 | 21.6258 | 21.796 | 21.9101 | 21.0889 | 21.1897 | 21.4282 | 20.4812 | 20.7477 | 22.0655 | 21.8736 | 21.7021 | 24.2696 | 112.6904 | 98.6666 | 121.3834 | 22.1287 | 21.7695 | 23.1817 | 22.0196 | 21.8193 | 23.9073 | 40.1527 | 123.0762 |  | 63.2585 | 93.1123 | 94.2236 | 67.1771 |  | 17.0602 | 17.4042 | 16.756 | 17.2217 | 17.4723 | 20.3051 | 61.4976 | 15.6169 | 17.0737 | 15.5371 | 17.8572 | 18.3095 | 46.7018 | 50.9576 | 45.5978 | 21.6523 |  |  | 0.72371 | -0.45282 | -26.9064 | 0.35611 | 0.12236 | -180.4909 | 19.6645 | 0.319 | 0.073458 | 0.011021 | 0.17285 | 0.0003417 | 0.00036306 | 1.6099 | 21.7679 | 21.9741 | 22.1692 | 22.2213 | 22.032 | 21.3289 | 20.1401 | 22.1717 | 22.3507 | 22.3859 | 22.3495 | 21.9578 | 21.1831 | 22.2671 | 55.5636 | 37.6429 | 36.7728 | 29.7875 | 26.2515 | 36.543 | 26.9098 | 22.3315 | 22.0953 | 21.6561 | 22.0576 | 21.7749 | 21.3144 | 21.9343 | 21.5904 | 22.2516 | 38.7318 | 110.5721 | 84.3681 | 55.6565 | 0.51157 | -0.29174 | 45.5937 | 21.9316 | 22.2574 | 20.2487 | 21.5897 | 22.0375 | 21.9137 | 21.8273 | 25.883 | 21.7803 | 21.5008 | 22.8549 | 107.201 | 136.8509 | 83.3531 | 84.5111 | 53.7905 |  | 38.9794 | 78.5272 | 41.601 | 56.6601 | 41.7117 | 47.415 |  | 52.8714 |  |  | 21.8576 | 23.3858 | 41.1673 | [5 empty] | 21.8838 | 44.1719 | 21.6736 | 22.06 | 29.2076 | 21.2344 | 21.8675 | 23.7775 | 55.9904 | 146.2945 |  | 47.612 | 99.9065 | 21.0924 | 46.9941 | 108.5835 | 34.0414 | 80.5151 | 22.8879 | 78.5789 | 22.8395 | 79.3745 | 18.6047 | 49.7584 | 95.4876 | 25.2095 | 47.3804 | 115.2086 | 21.1917 | 44.8604 | 108.6719 | 21.148 | 72.7255 | 26.3644 | 82.6213 | 23.063 | 82.2264 | 0.5495 | 19.6748 | 0.94306 | 0.029199 | -27.0534 | 3.0952 | 115.55 | 52.84 | 1.1776 | -0.79936 | -6.1618 | 0.70888 | 0.41759 | -16.0386 | 5.2939 | 0.12675 | -0.46925 | 0.14203 | -1.5918 | -0.63625 | -0.20437 | 0.066338
42838.4238 | 308 | 22.9192 | 22.8824 | 22.8704 | 22.7867 | 22.403 | 21.7342 | 22.7228 | 21.774 | 22.3711 | 22.3767 | 22.3412 | 21.9946 | 21.213 | 22.1791 | 21.6222 | 21.7898 | 21.9081 | 21.0873 | 21.1905 | 21.4261 | 20.4783 | 20.7467 | 22.0747 | 21.8658 | 21.7052 | 24.2831 | 113.0462 | 99.0794 | 121.6922 | 22.1255 | 21.776 | 23.1911 | 22.0264 | 21.8213 | 23.9236 | 40.2923 | 123.7053 |  | 63.5191 | 93.4995 | 94.5687 | 67.8792 |  | 17.0626 | 17.4044 | 16.7662 | 17.2383 | 17.4742 | 20.3743 | 61.3425 | 15.6198 | 17.0717 | 15.5395 | 17.8615 | 18.3095 | 46.7641 | 50.95 | 45.6571 | 21.6461 |  |  | 0.84857 | -0.56781 | -26.729 | 0.46519 | 0.28269 | -177.5878 | 20.0246 | 0.29008 | 0.15752 | 0.12368 | 0.082578 | 0.00035156 | 0.00031213 | 1.5957 | 21.772 | 21.9748 | 22.1666 | 22.2282 | 22.0395 | 21.3348 | 20.1487 | 22.1721 | 22.3628 | 22.3881 | 22.3446 | 21.9665 | 21.1896 | 22.2682 | 55.7133 | 36.3796 | 34.5324 | 29.478 | 26.6234 | 36.6525 | 26.9205 | 22.3275 | 22.0986 | 21.663 | 22.0544 | 21.7809 | 21.3132 | 21.9359 | 21.5854 | 22.2681 | 38.8591 | 110.5755 | 84.4146 | 56.2473 | 0.76341 | 0.069834 | 45.7725 | 21.9434 | 22.2641 | 20.2576 | 21.595 | 22.0435 | 21.919 | 21.835 | 25.9143 | 21.7852 | 21.5102 | 22.8694 | 107.319 | 137.1659 | 83.4791 | 84.7394 | 53.4652 |  | 39.0862 | 79.736 | 41.7366 | 59.8833 | 41.9809 | 47.6243 |  | 53.0397 |  |  | 21.8518 | 23.4135 | 41.6639 | [5 empty] | 21.8829 | 44.516 | 21.6743 | 22.0599 | 29.2114 | 21.23 | 21.8611 | 23.8296 | 56.2559 | 146.2168 |  | 47.9612 | 100.0752 | 21.1166 | 47.3991 | 109.0611 | 34.1675 | 80.7459 | 22.9161 | 78.9359 | 22.8731 | 79.8246 | 18.5961 | 49.8114 | 95.7898 | 25.2444 | 47.5112 | 115.6234 | 21.1941 | 44.9664 | 109.259 | 21.1583 | 72.9881 | 26.409 | 82.714 | 23.0958 | 82.5304 | 0.72684 | 19.6741 | 0.94522 | 0.027253 | -27.1956 | 3.0953 | 121.56 | 51.63 | 1.2756 | -0.89512 | -6.1415 | 0.81021 | 0.63481 | -15.9109 | 5.3428 | 0.1395 | -0.4981 | 0.061886 | -1.5956 | -0.38607 | -0.21902 | 0.054341
42838.4239 | 309 | 22.9196 | 22.8825 | 22.8615 | 22.7837 | 22.4027 | 21.7252 | 22.7179 | 21.7809 | 22.3625 | 22.3685 | 22.337 | 21.9918 | 21.2011 | 22.1694 | 21.6257 | 21.7901 | 21.9155 | 21.0992 | 21.2004 | 21.4349 | 20.4865 | 20.7532 | 22.088 | 21.8737 | 21.7127 | 24.3112 | 113.3608 | 99.3916 | 121.1553 | 22.1269 | 21.7721 | 23.2032 | 22.0169 | 21.8153 | 23.935 | 40.4597 | 123.9062 |  | 63.7802 | 93.8507 | 94.9718 | 68.6759 |  | 17.0719 | 17.4211 | 16.7845 | 17.2511 | 17.4848 | 20.4187 | 61.3443 | 15.6349 | 17.0839 | 15.5745 | 17.8718 | 18.3176 | 46.8371 | 50.9511 | 45.7251 | 21.657 |  |  | 0.53315 | -0.32336 | -26.3373 | 0.65379 | 0.19267 | -177.729 | 20.1238 | 0.34791 | 0.087663 | 0.11823 | 0.23812 | 0.00035156 | 0.0003647 | 1.5533 | 21.7651 | 21.9718 | 22.1675 | 22.2284 | 22.033 | 21.3383 | 20.143 | 22.1753 | 22.3519 | 22.3918 | 22.334 | 21.9594 | 21.1895 | 22.2699 | 57.4383 | 38.7145 | 36.1429 | 29.2543 | 25.9986 | 36.8185 | 26.9814 | 22.3342 | 22.0989 | 21.6703 | 22.0602 | 21.7798 | 21.3152 | 21.9419 | 21.5988 | 22.276 | 39.013 | 110.7011 | 84.7456 | 56.4718 | 0.86387 | 0.12613 | 46.1509 | 21.9395 | 22.2648 | 20.2565 | 21.5858 | 22.0394 | 21.9182 | 21.8373 | 25.9425 | 21.7821 | 21.5107 | 22.8769 | 107.4902 | 137.6896 | 83.6187 | 84.9837 | 53.6251 |  | 39.1988 | 80.1163 | 41.8733 | 61.8059 | 42.2017 | 47.8562 |  | 53.1829 |  |  | 21.8667 | 23.4478 | 42.2189 | [5 empty] | 21.895 | 44.8997 | 21.6782 | 22.0692 | 29.2541 | 21.2358 | 21.8723 | 23.8631 | 56.5524 | 146.0606 |  | 48.1692 | 100.3036 | 21.1337 | 47.7943 | 109.4761 | 34.266 | 81.0047 | 22.9344 | 79.2467 | 22.8879 | 80.152 | 18.5847 | 49.8966 | 96.0621 | 25.278 | 47.6649 | 116.0381 | 21.2009 | 45.0953 | 109.8282 | 21.1613 | 73.3364 | 26.4684 | 82.7606 | 23.1193 | 82.8436 | 0.65413 | 19.6695 | 0.94682 | 0.027819 | -27.176 | 3.0952 | 127.5 | 52.18 | 1.0104 | -0.67552 | -6.0965 | 0.96053 | 0.52412 | -15.9185 | 5.3564 | 0.13896 | -0.50389 | 0.016181 | -1.7677 | -0.55787 | -0.23533 | 0.053438
42838.4239 | 310 | 22.9146 | 22.8753 | 22.863 | 22.7801 | 22.3914 | 21.7295 | 22.7121 | 21.7793 | 22.3654 | 22.3722 | 22.3416 | 21.9931 | 21.1991 | 22.1655 | 21.6174 | 21.7902 | 21.9129 | 21.0978 | 21.195 | 21.4341 | 20.4793 | 20.7545 | 22.0958 | 21.8734 | 21.7097 | 24.331 | 113.403 | 99.5902 | 120.1468 | 22.1294 | 21.7814 | 23.2195 | 22.0187 | 21.8205 | 23.9553 | 40.6344 | 124.1752 |  | 64.0192 | 94.096 | 95.5124 | 68.687 |  | 17.0817 | 17.4259 | 16.7909 | 17.2589 | 17.4897 | 20.4196 | 61.957 | 15.5637 | 17.0822 | 15.5811 | 17.8776 | 18.3116 | 46.8869 | 50.9396 | 45.7693 | 21.6503 |  |  | 0.49635 | -0.52247 | -25.9707 | 0.65641 | 0.11381 | -176.8097 | 20.1501 | 0.37748 | 0.024808 | 0.11131 | 0.26729 | 0.0003647 | 0.0003532 | 1.5362 | 21.7572 | 21.9697 | 22.1638 | 22.22 | 22.0381 | 21.3331 | 20.1455 | 22.176 | 22.3489 | 22.3939 | 22.34 | 21.9581 | 21.1878 | 22.2633 | 59.4696 | 39.5508 | 38.3347 | 29.9807 | 26.6976 | 37.0034 | 27.0408 | 22.3302 | 22.098 | 21.6618 | 22.0615 | 21.766 | 21.3088 | 21.9306 | 21.5894 | 22.2835 | 39.1501 | 110.8399 | 85.422 | 56.6921 | 0.76931 | 0.30359 | 46.5331 | 21.9346 | 22.2563 | 20.2544 | 21.584 | 22.0324 | 21.9138 | 21.8438 | 25.969 | 21.7865 | 21.5113 | 22.8921 | 107.7655 | 138.3338 | 83.8123 | 85.2356 | 53.6711 |  | 39.2992 | 80.8228 | 41.9726 | 61.7397 | 42.3798 | 48.4108 |  | 53.3148 |  |  | 21.8655 | 23.4591 | 42.3138 | [5 empty] | 21.8906 | 44.5947 | 21.6773 | 22.0626 | 29.2876 | 21.2332 | 21.8714 | 23.8965 | 56.8841 | 146.4348 |  | 48.3628 | 100.4789 | 21.1575 | 47.9176 | 109.8952 | 34.3523 | 81.2529 | 22.9585 | 79.5035 | 22.9055 | 80.4209 | 18.5677 | 49.9754 | 96.4196 | 25.316 | 47.8874 | 116.3443 | 21.2176 | 45.2478 | 110.2236 | 21.1725 | 73.6682 | 26.5206 | 82.8072 | 23.1349 | 83.1346 | 0.67861 | 19.6669 | 0.94997 | 0.027587 | -27.1469 | 3.0953 | 110.51 | 52.28 | 0.9737 | -0.85867 | -6.0539 | 0.96247 | 0.40283 | -15.8773 | 5.3599 | 0.14116 | -0.52006 | 0.024237 | -1.9716 | -0.79445 | -0.22956 | 0.052073
42838.4239 | 311 | 22.9156 | 22.8718 | 22.8671 | 22.7778 | 22.3976 | 21.7203 | 22.7092 | 21.7711 | 22.3613 | 22.3684 | 22.3363 | 21.9872 | 21.2037 | 22.1605 | 21.6242 | 21.7951 | 21.9069 | 21.0967 | 21.1926 | 21.4343 | 20.4778 | 20.7603 | 22.1138 | 21.873 | 21.7125 | 24.3426 | 113.3815 | 99.8077 | 119.2061 | 22.1319 | 21.7721 | 23.2303 | 22.0156 | 21.8179 | 23.9691 | 40.7756 | 123.2711 |  | 64.2391 | 94.4357 | 96.0156 | 67.7318 |  | 17.082 | 17.4327 | 16.7975 | 17.2682 | 17.4823 | 20.4063 | 62.4166 | 15.4419 | 17.0806 | 15.5731 | 17.8813 | 18.3196 | 46.9367 | 50.9258 | 45.8282 | 21.6491 |  |  | 0.88799 | -0.29051 | -26.0101 | 0.56047 | 0.26955 | -176.3846 | 20.4491 | 0.48985 | 0.15247 | 0.18515 | 0.083098 | 0.0003072 | 0.00032856 | 1.5454 | 21.7658 | 21.9698 | 22.1714 | 22.2172 | 22.0431 | 21.334 | 20.1551 | 22.1792 | 22.3579 | 22.3953 | 22.3438 | 21.9654 | 21.194 | 22.274 | 60.5964 | 40.7886 | 41.1594 | 30.3831 | 26.9155 | 37.1566 | 27.1121 | 22.3296 | 22.0972 | 21.6602 | 22.054 | 21.7785 | 21.3086 | 21.9332 | 21.5902 | 22.2999 | 39.2662 | 110.7512 | 85.5643 | 56.7292 | 0.83025 | 0.0002212 | 46.8729 | 21.9383 | 22.2581 | 20.2587 | 21.5901 | 22.0373 | 21.9216 | 21.8454 | 26.0035 | 21.7896 | 21.5135 | 22.9099 | 108.1939 | 138.7103 | 84.042 | 85.4381 | 53.4942 |  | 39.4017 | 81.8014 | 42.0818 | 61.7349 | 42.5548 | 48.2326 |  | 53.4379 |  |  | 21.868 | 23.4833 | 42.4629 | [5 empty] | 21.8948 | 44.4904 | 21.6773 | 22.0636 | 29.3304 | 21.2377 | 21.8711 | 23.9316 | 57.1781 | 147.0475 |  | 48.6282 | 100.712 | 21.1853 | 47.996 | 110.5693 | 34.4335 | 81.4798 | 22.9875 | 79.8209 | 22.9383 | 80.7237 | 18.5494 | 50.0895 | 96.75 | 25.3649 | 48.1237 | 116.5933 | 21.23 | 45.4167 | 110.5026 | 21.1945 | 73.9516 | 26.5506 | 82.9377 | 23.16 | 83.552 | 0.54524 | 19.6647 | 0.95398 | 0.028553 | -27.0899 | 3.0953 | 100.11 | 51.35 | 1.3008 | -0.6403 | -6.0586 | 0.88936 | 0.61991 | -15.8578 | 5.3994 | 0.14963 | -0.54343 | 0.030479 | -2.0787 | -1.0999 | -0.19812 | 0.055069
42838.4239 | 312 | 22.9082 | 22.8728 | 22.8584 | 22.7786 | 22.3902 | 21.7224 | 22.7078 | 21.7843 | 22.3627 | 22.3649 | 22.3333 | 21.9921 | 21.2033 | 22.1723 | 21.6276 | 21.7961 | 21.9133 | 21.102 | 21.1977 | 21.4391 | 20.4871 | 20.7556 | 22.1274 | 21.8721 | 21.7135 | 24.3661 | 113.4904 | 99.9795 | 119.3272 | 22.1227 | 21.7747 | 23.2426 | 22.0157 | 21.8201 | 23.987 | 40.8752 | 122.6439 |  | 64.4541 | 94.8838 | 96.4252 | 67.0149 |  | 17.0807 | 17.4395 | 16.802 | 17.2732 | 17.4933 | 20.3874 | 62.3971 | 15.3804 | 17.0783 | 15.5515 | 17.8745 | 18.3207 | 47.0151 | 50.9178 | 45.8923 | 21.651 |  |  | 0.72634 | -0.57373 | -26.083 | 0.47834 | 0.17164 | -175.4857 | 19.8701 | 0.75729 | 0.10557 | 0.15473 | 0.11226 | 0.00033677 | 0.00031049 | 1.5514 | 21.7724 | 21.9662 | 22.1769 | 22.2231 | 22.0436 | 21.3385 | 20.1501 | 22.1746 | 22.3603 | 22.3965 | 22.341 | 21.9664 | 21.1919 | 22.2695 | 60.8149 | 41.0557 | 40.5713 | 30.4993 | 27.7053 | 37.3163 | 27.1713 | 22.3335 | 22.102 | 21.6562 | 22.0563 | 21.7775 | 21.3077 | 21.9366 | 21.5961 | 22.309 | 39.3777 | 110.7745 | 85.6982 | 56.9548 | 0.70128 | 0.11929 | 47.1924 | 21.9415 | 22.2605 | 20.2589 | 21.5896 | 22.0446 | 21.9204 | 21.8453 | 26.0301 | 21.7832 | 21.5115 | 22.9213 | 108.6925 | 138.9922 | 84.2608 | 85.6171 | 54.2401 |  | 39.519 | 82.6627 | 42.2321 | 63.2437 | 42.8063 | 47.9323 |  | 53.5892 |  |  | 21.8974 | 23.5143 | 42.4781 | [5 empty] | 21.9001 | 45.0043 | 21.6806 | 22.0692 | 29.3627 | 21.2391 | 21.8798 | 23.9628 | 57.4358 | 147.6585 |  | 48.9219 | 101.1154 | 21.1983 | 48.1388 | 111.2266 | 34.5069 | 81.6711 | 23.0139 | 80.1914 | 22.953 | 81.0986 | 18.5447 | 50.3122 | 97.087 | 25.4 | 48.3404 | 116.7022 | 21.2249 | 45.6049 | 110.764 | 21.2207 | 74.1756 | 26.5968 | 83.1534 | 23.1835 | 84.11 | 0.62593 | 19.6611 | 0.95799 | 0.0302 | -27.0942 | 3.0952 | 126.26 | 52.47 | 1.1766 | -0.89983 | -6.0672 | 0.82163 | 0.49466 | -15.8168 | 5.3223 | 0.13299 | -0.56211 | -0.0026506 | -2.0842 | -1.0276 | -0.17474 | 0.052672
42838.4239 | 313 | 22.9038 | 22.8731 | 22.8557 | 22.7807 | 22.3925 | 21.7197 | 22.7096 | 21.7785 | 22.3584 | 22.3652 | 22.3325 | 21.9856 | 21.2018 | 22.1706 | 21.6229 | 21.7956 | 21.9105 | 21.0912 | 21.1917 | 21.4374 | 20.4858 | 20.7449 | 22.1288 | 21.8719 | 21.7163 | 24.383 | 113.8578 | 100.1791 | 120.4887 | 22.1284 | 21.7721 | 23.2658 | 22.0178 | 21.8225 | 24.0063 | 40.9799 | 123.8166 |  | 64.7205 | 95.3072 | 96.7218 | 68.1828 |  | 17.0801 | 17.4382 | 16.8183 | 17.2952 | 17.507 | 20.3395 | 62.537 | 15.4124 | 17.0801 | 15.5278 | 17.8859 | 18.3189 | 47.0659 | 50.8989 | 45.9424 | 21.6542 |  |  | 0.7684 | -0.48896 | -26.2473 | 0.44482 | 0.27546 | -176.4937 | 19.8373 | 0.57462 | 0.19216 | 0.021511 | 0.068863 | 0.00035977 | 0.0003187 | 1.5185 | 21.7609 | 21.9654 | 22.1534 | 22.2175 | 22.0344 | 21.3302 | 20.1346 | 22.1756 | 22.3567 | 22.3894 | 22.3351 | 21.9585 | 21.1808 | 22.2593 | 61.11 | 41.6425 | 41.3467 | 29.6392 | 27.673 | 37.4725 | 27.255 | 22.334 | 22.1043 | 21.6659 | 22.0613 | 21.78 | 21.3167 | 21.9365 | 21.5941 | 22.3204 | 39.4996 | 111.1265 | 85.9967 | 56.9999 | 0.61458 | 0.34677 | 47.1967 | 21.9393 | 22.2634 | 20.2633 | 21.5936 | 22.0424 | 21.9207 | 21.8507 | 26.0575 | 21.7884 | 21.5129 | 22.9363 | 109.2064 | 139.5776 | 84.4493 | 85.7969 | 55.0653 |  | 39.6282 | 82.8815 | 42.3488 | 63.5308 | 43.0017 | 47.6211 |  | 53.7345 |  |  | 21.915 | 23.5339 | 42.5768 | [5 empty] | 21.8895 | 45.4609 | 21.6756 | 22.0626 | 29.364 | 21.229 | 21.8736 | 23.9979 | 57.6874 | 148.4282 |  | 49.3276 | 101.6147 | 21.2187 | 48.2431 | 111.5896 | 34.6167 | 81.9342 | 23.0281 | 80.4617 | 22.9668 | 81.4909 | 18.5439 | 50.4745 | 97.418 | 25.4385 | 48.5562 | 116.7937 | 21.2239 | 45.8075 | 110.9766 | 21.2281 | 74.3558 | 26.6483 | 83.3996 | 23.1981 | 84.5735 | 0.61369 | 19.6579 | 0.96171 | 0.031739 | -27.1116 | 3.0952 | 117.79 | 51.59 | 1.212 | -0.8307 | -6.0862 | 0.79232 | 0.62661 | -15.8609 | 5.3175 | 0.11385 | -0.56412 | -0.0037978 | -2.0985 | -1.104 | -0.20353 | 0.055653
42838.4239 | 314 | 22.9077 | 22.8787 | 22.8542 | 22.7797 | 22.3979 | 21.7221 | 22.7101 | 21.7735 | 22.361 | 22.3634 | 22.3328 | 21.9913 | 21.1991 | 22.1619 | 21.6384 | 21.7941 | 21.9201 | 21.1008 | 21.1967 | 21.4423 | 20.4902 | 20.7635 | 22.1467 | 21.882 | 21.7225 | 24.4026 | 114.1381 | 100.3781 | 120.7197 | 22.1313 | 21.7759 | 23.2793 | 22.0252 | 21.8257 | 24.0247 | 41.1021 | 125.0112 |  | 64.9664 | 95.6106 | 96.9795 | 68.9538 |  | 17.0797 | 17.4483 | 16.8298 | 17.3243 | 17.5255 | 20.3016 | 63.0135 | 15.5049 | 17.0715 | 15.4773 | 17.897 | 18.3199 | 47.1067 | 50.8773 | 45.9865 | 21.6399 |  |  | 0.67049 | -0.50144 | -26.0922 | 0.64656 | 0.23078 | -174.4868 | 20.3065 | 0.4721 | 0.16589 | 0.26887 | 0.25583 | 0.0003762 | 0.00037127 | 1.5082 | 21.7616 | 21.965 | 22.1685 | 22.2165 | 22.038 | 21.3287 | 20.1445 | 22.179 | 22.3563 | 22.386 | 22.3342 | 21.9619 | 21.1843 | 22.2699 | 59.4692 | 40.3457 | 41.544 | 30.6591 | 27.5799 | 37.5902 | 27.3533 | 22.3351 | 22.098 | 21.6612 | 22.0658 | 21.7779 | 21.3182 | 21.9377 | 21.5885 | 22.3328 | 39.6069 | 111.371 | 86.1954 | 57.0988 | 0.74729 | -0.089934 | 47.2661 | 21.9389 | 22.2628 | 20.2648 | 21.5932 | 22.0426 | 21.9171 | 21.8485 | 26.0867 | 21.7872 | 21.5161 | 22.9496 | 109.7477 | 140.0293 | 84.6766 | 86.011 | 56.52 |  | 39.7416 | 82.5539 | 42.4487 | 62.929 | 43.1691 | 47.3848 |  | 53.9004 |  |  | 21.9304 | 23.5793 | 42.7563 | [5 empty] | 21.8906 | 45.3871 | 21.6764 | 22.0611 | 29.3773 | 21.2337 | 21.8717 | 24.0327 | 57.9022 | 148.843 |  | 49.7143 | 102.0145 | 21.2361 | 48.2704 | 111.9151 | 34.7275 | 82.2327 | 23.0194 | 80.5765 | 22.9815 | 81.7818 | 18.5562 | 50.5466 | 97.7095 | 25.4767 | 48.7595 | 116.8671 | 21.2281 | 45.9331 | 111.2967 | 21.2461 | 74.6132 | 26.6982 | 83.683 | 23.2277 | 84.9074 | 0.60701 | 19.6555 | 0.96617 | 0.031609 | -27.1043 | 3.0952 | 124.24 | 52.51 | 1.1325 | -0.84125 | -6.0683 | 0.95525 | 0.5735 | -15.7694 | 5.3796 | 0.07738 | -0.55153 | 0.01877 | -1.9023 | -1.1144 | -0.22069 | 0.056628
42838.4239 | 315 | 22.905 | 22.8793 | 22.8565 | 22.7787 | 22.3945 | 21.7203 | 22.714 | 21.7693 | 22.3645 | 22.3617 | 22.3326 | 21.9838 | 21.1948 | 22.161 | 21.6337 | 21.7933 | 21.9063 | 21.0954 | 21.199 | 21.4364 | 20.4847 | 20.7604 | 22.1535 | 21.8769 | 21.7147 | 24.4178 | 114.3736 | 100.5044 | 121.2898 | 22.1385 | 21.7826 | 23.2861 | 22.029 | 21.8262 | 24.0418 | 41.2236 | 124.9901 |  | 65.1944 | 95.8696 | 97.3207 | 69.3011 |  | 17.0891 | 17.466 | 16.8432 | 17.3511 | 17.5454 | 20.3281 | 64.1299 | 15.5676 | 17.0744 | 15.4491 | 17.9018 | 18.3195 | 47.1379 | 50.8544 | 46.0332 | 21.6453 |  |  | 0.55024 | -0.53233 | -25.876 | 0.54076 | 0.13156 | -170.2655 | 19.9109 | 0.81972 | 0.071706 | 0.076688 | 0.076849 | 0.00037127 | 0.00031542 | 1.5214 | 21.7753 | 21.9721 | 22.1683 | 22.2202 | 22.0453 | 21.3353 | 20.1427 | 22.176 | 22.3618 | 22.3975 | 22.3429 | 21.9562 | 21.1852 | 22.274 | 58.3529 | 40.5298 | 40.3303 | 30.3375 | 28.309 | 37.6927 | 27.4077 | 22.3262 | 22.0917 | 21.6613 | 22.0591 | 21.7707 | 21.3119 | 21.9332 | 21.5952 | 22.3435 | 39.7107 | 111.4261 | 86.4647 | 57.1982 | 0.77068 | 0.35799 | 47.3499 | 21.9283 | 22.2569 | 20.2617 | 21.5845 | 22.0305 | 21.9032 | 21.8454 | 26.1069 | 21.7808 | 21.5124 | 22.9537 | 110.3642 | 140.4255 | 84.9696 | 86.2867 | 57.6791 |  | 39.8698 | 82.1643 | 42.5687 | 62.1792 | 43.3422 | 47.3699 |  | 54.1077 |  |  | 21.9431 | 23.6436 | 42.7199 | [5 empty] | 21.8966 | 45.2035 | 21.6821 | 22.0749 | 29.407 | 21.2466 | 21.8773 | 24.072 | 58.1239 | 148.7014 |  | 49.9097 | 102.4882 | 21.2369 | 48.3436 | 112.3983 | 34.8763 | 82.5309 | 23.0417 | 80.7598 | 22.9899 | 82.0002 | 18.5728 | 50.582 | 97.9541 | 25.5259 | 48.9535 | 117.1193 | 21.2405 | 45.989 | 111.7196 | 21.2655 | 74.9239 | 26.7708 | 83.8961 | 23.2644 | 85.3498 | 0.53355 | 19.6532 | 0.97022 | 0.031667 | -27.1613 | 3.0953 | 122.29 | 51.88 | 1.0267 | -0.8668 | -6.0433 | 0.87363 | 0.43302 | -15.5782 | 5.3272 | 0.049636 | -0.53652 | 0.045649 | -1.7662 | -0.97314 | -0.22611 | 0.057469
42838.4239 | 316 | 22.9111 | 22.876 | 22.8564 | 22.7743 | 22.3906 | 21.7203 | 22.7058 | 21.771 | 22.3615 | 22.3617 | 22.3345 | 21.9824 | 21.1917 | 22.1704 | 21.6363 | 21.7979 | 21.9178 | 21.1 | 21.1994 | 21.446 | 20.4909 | 20.7725 | 22.1718 | 21.8745 | 21.7243 | 24.4411 | 114.6638 | 100.7483 | 122.1683 | 22.127 | 21.7738 | 23.303 | 22.0233 | 21.8198 | 24.057 | 41.3587 | 124.692 |  | 65.3851 | 96.1885 | 97.6309 | 69.8429 |  | 17.0889 | 17.465 | 16.844 | 17.3439 | 17.5664 | 20.3304 | 64.5319 | 15.646 | 17.0738 | 15.4871 | 17.9005 | 18.3301 | 47.1621 | 50.8336 | 46.0862 | 21.6488 |  |  | 0.59032 | -0.67493 | -25.3858 | 0.30551 | 0.43317 | -170.2596 | 20.1356 | 0.70078 | 0.17037 | 0.10648 | 0.31017 | 0.00035977 | 0.00036799 | 1.5164 | 21.7699 | 21.9738 | 22.1707 | 22.2204 | 22.0415 | 21.3363 | 20.153 | 22.1803 | 22.3654 | 22.3884 | 22.3392 | 21.9592 | 21.1861 | 22.2722 | 59.3881 | 41.9332 | 42.5161 | 29.7542 | 28.124 | 37.8498 | 27.4967 | 22.3355 | 22.1042 | 21.6627 | 22.0674 | 21.777 | 21.3196 | 21.9361 | 21.5983 | 22.356 | 39.824 | 111.3227 | 86.7256 | 57.4003 | 0.83478 | 0.31614 | 47.501 | 21.9265 | 22.2577 | 20.2611 | 21.5849 | 22.0302 | 21.9116 | 21.8499 | 26.1369 | 21.778 | 21.5091 | 22.9657 | 110.7933 | 140.9719 | 85.2478 | 86.5424 | 57.3669 |  | 39.989 | 82.4202 | 42.695 | 61.1649 | 43.5067 | 47.8509 |  | 54.2992 |  |  | 21.9404 | 23.6969 | 42.6287 | [5 empty] | 21.8976 | 45.6333 | 21.6784 | 22.0684 | 29.4288 | 21.2358 | 21.8807 | 24.1237 | 58.37 | 148.7725 |  | 50.0766 | 102.8039 | 21.2699 | 48.5124 | 112.8675 | 35.0519 | 82.8435 | 23.0728 | 80.9814 | 23.0175 | 82.3446 | 18.5915 | 50.6624 | 98.3111 | 25.5612 | 49.1723 | 117.3325 | 21.2592 | 46.1054 | 112.0475 | 21.2894 | 75.1941 | 26.8186 | 83.948 | 23.2979 | 85.6574 | 0.80568 | 19.6501 | 0.97442 | 0.031435 | -27.0809 | 3.0952 | 113.67 | 51.49 | 1.0646 | -0.97601 | -5.9858 | 0.65666 | 0.78575 | -15.578 | 5.3572 | 0.06245 | -0.53922 | 0.079575 | -1.8627 | -1.2056 | -0.23646 | 0.055792
42838.4239 | 317 | 22.9137 | 22.8793 | 22.8632 | 22.7854 | 22.396 | 21.7163 | 22.7191 | 21.7777 | 22.3719 | 22.3684 | 22.3345 | 21.9926 | 21.205 | 22.1665 | 21.6233 | 21.794 | 21.9143 | 21.0869 | 21.183 | 21.4361 | 20.481 | 20.7574 | 22.1682 | 21.8664 | 21.7107 | 24.4515 | 114.8423 | 100.9508 | 122.1946 | 22.1382 | 21.7793 | 23.3148 | 22.0226 | 21.8408 | 24.0784 | 41.5108 | 125.9598 |  | 65.617 | 96.6238 | 97.8781 | 71.3092 |  | 17.0875 | 17.4694 | 16.84 | 17.3471 | 17.5754 | 20.3232 | 64.3035 | 15.7002 | 17.0701 | 15.5218 | 17.9036 | 18.3359 | 47.1799 | 50.7993 | 46.1283 | 21.6462 |  |  | 0.82885 | -0.37002 | -25.054 | 0.45271 | 0.23932 | -171.8689 | 20.6495 | 0.7159 | 0.096031 | 0.1562 | 0.18952 | 0.0003532 | 0.00036799 | 1.4851 | 21.7671 | 21.9708 | 22.167 | 22.2213 | 22.0355 | 21.3305 | 20.1465 | 22.1774 | 22.3602 | 22.3875 | 22.3379 | 21.957 | 21.1838 | 22.2709 | 61.5941 | 43.3425 | 43.7439 | 30.3206 | 27.929 | 38.0119 | 27.5711 | 22.3408 | 22.11 | 21.6616 | 22.0665 | 21.7779 | 21.326 | 21.9335 | 21.6061 | 22.3703 | 39.9365 | 111.2093 | 86.8922 | 57.8302 | 0.71564 | -0.0041534 | 47.6667 | 21.9268 | 22.2519 | 20.2601 | 21.5818 | 22.036 | 21.9165 | 21.8514 | 26.1627 | 21.7759 | 21.5127 | 22.9765 | 111.1134 | 141.487 | 85.5253 | 86.7688 | 56.8314 |  | 40.0994 | 83.166 | 42.8025 | 60.907 | 43.6676 | 48.7081 |  | 54.4515 |  |  | 21.9569 | 23.7354 | 42.6144 | [5 empty] | 21.9055 | 46.6351 | 21.6773 | 22.073 | 29.4911 | 21.2375 | 21.8813 | 24.1611 | 58.5827 | 149.1014 |  | 50.5331 | 103.1756 | 21.2793 | 48.7524 | 113.4902 | 35.1522 | 83.1207 | 23.0948 | 81.3023 | 23.0301 | 82.7283 | 18.6086 | 50.7421 | 98.6101 | 25.6013 | 49.4299 | 117.3498 | 21.264 | 46.318 | 112.5889 | 21.2965 | 75.4672 | 26.864 | 84.1213 | 23.3226 | 85.8943 | 0.5623 | 19.644 | 0.97904 | 0.030999 | -27.0526 | 3.0952 | 121.04 | 52.6 | 1.2615 | -0.72267 | -5.9466 | 0.79935 | 0.58404 | -15.6513 | 5.4251 | 0.081163 | -0.55618 | 0.092371 | -2.0887 | -1.3333 | -0.27189 | 0.047754
42838.424 | 318 | 22.9097 | 22.8733 | 22.8626 | 22.7803 | 22.3945 | 21.7184 | 22.7125 | 21.7654 | 22.3555 | 22.362 | 22.3376 | 21.9845 | 21.1924 | 22.1651 | 21.6292 | 21.8001 | 21.9098 | 21.0994 | 21.1961 | 21.4349 | 20.4891 | 20.773 | 22.1822 | 21.8714 | 21.7279 | 24.4774 | 114.941 | 101.033 | 121.9134 | 22.125 | 21.7724 | 23.3322 | 22.0183 | 21.8295 | 24.0947 | 41.665 | 126.778 |  | 65.8696 | 97.0507 | 98.1501 | 71.5458 |  | 17.0847 | 17.4828 | 16.8496 | 17.3497 | 17.5712 | 20.3752 | 64.384 | 15.7101 | 17.0792 | 15.5025 | 17.9075 | 18.339 | 47.199 | 50.7636 | 46.1857 | 21.6526 |  |  | 0.70006 | -0.39105 | -25.171 | 0.68599 | 0.24786 | -171.9615 | 20.6429 | 0.55819 | 0.033759 | 0.069765 | 0.17632 | 0.0003877 | 0.00034006 | 1.4702 | 21.7712 | 21.9693 | 22.1698 | 22.2281 | 22.0373 | 21.3299 | 20.1439 | 22.1748 | 22.3529 | 22.3893 | 22.3437 | 21.9574 | 21.1833 | 22.2731 | 62.4199 | 43.8913 | 44.043 | 30.4876 | 28.0731 | 38.172 | 27.6462 | 22.3259 | 22.0936 | 21.653 | 22.0564 | 21.7713 | 21.3203 | 21.929 | 21.5913 | 22.3728 | 40.0386 | 111.1154 | 87.0671 | 58.035 | 0.72193 | 0.34677 | 47.8013 | 21.9279 | 22.2579 | 20.2638 | 21.5798 | 22.0388 | 21.9109 | 21.8546 | 26.1846 | 21.7778 | 21.5148 | 22.9963 | 111.5941 | 141.9772 | 85.8133 | 87.0275 | 56.8174 |  | 40.2023 | 83.0653 | 42.9225 | 61.1018 | 43.8447 | 48.7397 |  | 54.6354 |  |  | 21.9476 | 23.7505 | 42.8854 | [5 empty] | 21.8961 | 47.5333 | 21.6773 | 22.0727 | 29.5496 | 21.2462 | 21.8812 | 24.2098 | 58.8141 | 149.5252 |  | 51.1718 | 103.4135 | 21.2907 | 49.0109 | 114.2493 | 35.2294 | 83.4224 | 23.1229 | 81.5688 | 23.0574 | 82.9831 | 18.6007 | 50.7863 | 99.0774 | 25.649 | 49.6556 | 117.7059 | 21.2728 | 46.4729 | 112.9573 | 21.3064 | 75.7518 | 26.9097 | 84.493 | 23.3418 | 86.3025 | 0.78194 | 19.6382 | 0.98373 | 0.031238 | -27.0658 | 3.0952 | 135.25 | 52.05 | 1.159 | -0.74294 | -5.9606 | 0.984 | 0.59442 | -15.6569 | 5.4247 | 0.085126 | -0.54919 | 0.093157 | -2.1616 | -1.3577 | -0.27308 | 0.045613
42838.424 | 319 | 22.9164 | 22.8816 | 22.8714 | 22.7833 | 22.4012 | 21.7343 | 22.7149 | 21.7844 | 22.3652 | 22.3679 | 22.3429 | 22.0014 | 21.2043 | 22.1717 | 21.6326 | 21.7993 | 21.9172 | 21.1008 | 21.2024 | 21.4455 | 20.4857 | 20.7702 | 22.1974 | 21.8814 | 21.73 | 24.498 | 115.4803 | 101.2894 | 123.6784 | 22.1311 | 21.7771 | 23.3426 | 22.0212 | 21.8193 | 24.0998 | 41.8055 | 127.5443 |  | 66.1331 | 97.4653 | 98.3977 | 73.2774 |  | 17.0911 | 17.4964 | 16.8382 | 17.3467 | 17.5633 | 20.5521 | 65.1041 | 15.7418 | 17.0768 | 15.5453 | 17.9174 | 18.3446 | 47.2227 | 50.7279 | 46.241 | 21.6477 |  |  | 0.4405 | -0.57044 | -25.0395 | 0.46257 | 0.023132 | -169.546 | 20.541 | 0.64098 | 0.19411 | 0.26824 | 0.34905 | 0.00036141 | 0.00036799 | 1.4839 | 21.7771 | 21.978 | 22.1714 | 22.2295 | 22.0388 | 21.338 | 20.1538 | 22.1844 | 22.3605 | 22.4018 | 22.3443 | 21.9625 | 21.1889 | 22.2745 | 63.1887 | 43.4098 | 44.0804 | 31.4193 | 28.0916 | 38.3519 | 27.7384 | 22.3302 | 22.0927 | 21.6592 | 22.0655 | 21.7758 | 21.3151 | 21.932 | 21.5991 | 22.3901 | 40.1744 | 111.1379 | 87.2277 | 57.9742 | 0.79723 | 0.11624 | 48.0593 | 21.9299 | 22.2669 | 20.2719 | 21.5834 | 22.043 | 21.9183 | 21.8563 | 26.2301 | 21.7842 | 21.518 | 23.0206 | 112.0746 | 142.4194 | 86.1081 | 87.269 | 56.3087 |  | 40.3172 | 83.849 | 43.0775 | 62.6305 | 44.0895 | 49.0017 |  | 54.8195 |  |  | 21.9577 | 23.7641 | 42.9735 | [5 empty] | 21.8992 | 48.4394 | 21.6848 | 22.0774 | 29.5898 | 21.2448 | 21.8856 | 24.2453 | 59.0327 | 149.9538 |  | 51.7067 | 103.778 | 21.3046 | 49.2816 | 114.7242 | 35.3165 | 83.6331 | 23.1483 | 81.7671 | 23.0763 | 83.2528 | 18.5862 | 50.9397 | 99.4707 | 25.7101 | 49.8398 | 117.9015 | 21.2685 | 46.6375 | 113.3166 | 21.3178 | 75.982 | 26.972 | 84.893 | 23.379 | 86.9336 | 0.8847 | 19.6352 | 0.98792 | 0.031761 | -27.0482 | 3.0952 | 130.54 | 52.55 | 0.92138 | -0.89734 | -5.9451 | 0.80805 | 0.18165 | -15.5512 | 5.4129 | 0.10325 | -0.56554 | 0.059263 | -2.2258 | -1.351 | -0.31629 | 0.052025
42838.424 | 320 | 22.9146 | 22.8786 | 22.8667 | 22.775 | 22.3975 | 21.7269 | 22.7197 | 21.7805 | 22.3628 | 22.367 | 22.34 | 21.9932 | 21.202 | 22.166 | 21.6295 | 21.7899 | 21.9102 | 21.0907 | 21.1931 | 21.4411 | 20.4825 | 20.7602 | 22.1969 | 21.8662 | 21.7253 | 24.5109 | 115.9904 | 101.5719 | 126.0319 | 22.1272 | 21.7809 | 23.3524 | 22.014 | 21.8242 | 24.1199 | 41.9769 | 128.5257 |  | 66.3854 | 97.8347 | 98.671 | 74.7153 |  | 17.0843 | 17.5002 | 16.8248 | 17.3375 | 17.5695 | 20.5889 | 65.6895 | 15.7686 | 17.0758 | 15.5715 | 17.9222 | 18.3446 | 47.2527 | 50.6855 | 46.2916 | 21.6554 |  |  | 0.76183 | -0.6125 | -24.7754 | 0.52236 | 0.12761 | -172.4176 | 20.863 | 0.70275 | 0.1114 | 0.11613 | 0.16382 | 0.00032856 | 0.0003647 | 1.4775 | 21.7787 | 21.9815 | 22.1733 | 22.2317 | 22.0491 | 21.3476 | 20.1541 | 22.1829 | 22.3654 | 22.4025 | 22.3424 | 21.9688 | 21.2019 | 22.2777 | 64.5299 | 45.8255 | 43.0807 | 31.517 | 28.25 | 38.5436 | 27.8071 | 22.3307 | 22.1106 | 21.6651 | 22.0654 | 21.7788 | 21.3194 | 21.9398 | 21.6001 | 22.4101 | 40.3039 | 111.2242 | 87.4055 | 58.566 | 0.61635 | 0.38252 | 48.2115 | 21.9326 | 22.2602 | 20.2709 | 21.5872 | 22.0395 | 21.9177 | 21.8563 | 26.2557 | 21.7839 | 21.5122 | 23.0326 | 112.4334 | 143.1007 | 86.4248 | 87.5102 | 55.7245 |  | 40.4144 | 83.6229 | 43.2224 | 63.3025 | 44.2907 | 49.2176 |  | 54.9774 |  |  | 21.9599 | 23.7901 | 43.0451 | [5 empty] | 21.8864 | 48.756 | 21.668 | 22.0634 | 29.6014 | 21.2339 | 21.875 | 24.2858 | 59.3263 | 149.8972 |  | 52.0372 | 104.1379 | 21.3225 | 49.5572 | 115.007 | 35.4506 | 83.8801 | 23.1781 | 82.0866 | 23.1005 | 83.5071 | 18.5565 | 51.2885 | 99.7457 | 25.8113 | 50.0824 | 118.0352 | 21.277 | 46.7989 | 113.8056 | 21.3226 | 76.2058 | 27.037 | 85.2675 | 23.4156 | 87.2347 | 0.79047 | 19.6312 | 0.99275 | 0.031355 | -27.0441 | 3.0953 | 118.1 | 52.18 | 1.2153 | -0.92983 | -5.9137 | 0.85869 | 0.42667 | -15.6833 | 5.4555 | 0.12286 | -0.5542 | 0.047644 | -2.3522 | -1.2319 | -0.35026 | 0.040085
42838.424 | 321 | 22.9243 | 22.8796 | 22.8651 | 22.7811 | 22.4015 | 21.7282 | 22.7192 | 21.7829 | 22.3689 | 22.3734 | 22.3463 | 21.9953 | 21.203 | 22.1727 | 21.6247 | 21.7959 | 21.9077 | 21.0941 | 21.2004 | 21.4461 | 20.4818 | 20.7665 | 22.2092 | 21.873 | 21.7247 | 24.5282 | 116.4339 | 101.8973 | 126.8014 | 22.1266 | 21.7859 | 23.366 | 22.0172 | 21.835 | 24.1396 | 42.1443 | 128.107 |  | 66.5885 | 98.085 | 98.9548 | 75.4904 |  | 17.093 | 17.5028 | 16.8255 | 17.3317 | 17.573 | 20.508 | 65.9797 | 15.7086 | 17.0837 | 15.5789 | 17.9266 | 18.3523 | 47.3 | 50.6342 | 46.3269 | 21.651 |  |  | 0.65209 | -0.70055 | -24.985 | 0.55193 | 0.11973 | -171.6941 | 20.6823 | 0.99386 | -0.067433 | 0.12788 | 0.15115 | 0.00037784 | 0.00034992 | 1.4728 | 21.7656 | 21.9652 | 22.161 | 22.2097 | 22.0367 | 21.3331 | 20.1375 | 22.1756 | 22.3535 | 22.3962 | 22.3389 | 21.9555 | 21.1862 | 22.262 | 64.1671 | 45.0153 | 41.2814 | 31.8836 | 28.1373 | 38.6964 | 27.8773 | 22.3321 | 22.1066 | 21.6567 | 22.0638 | 21.7733 | 21.3207 | 21.941 | 21.5971 | 22.4119 | 40.4278 | 111.3871 | 87.5963 | 58.7981 | 0.38063 | -0.1565 | 48.1341 | 21.9253 | 22.2515 | 20.2648 | 21.5824 | 22.0296 | 21.9096 | 21.8558 | 26.2812 | 21.7787 | 21.5092 | 23.039 | 112.8147 | 143.6925 | 86.7234 | 87.7268 | 55.3077 |  | 40.5337 | 82.8267 | 43.3353 | 63.4937 | 44.4796 | 49.2233 |  | 55.1531 |  |  | 21.966 | 23.8142 | 43.0091 | [5 empty] | 21.8828 | 49.5939 | 21.6717 | 22.0607 | 29.6439 | 21.2386 | 21.8764 | 24.3361 | 59.6257 | 149.8861 |  | 52.1701 | 104.3681 | 21.3462 | 49.7289 | 115.6482 | 35.6149 | 84.2061 | 23.2079 | 82.4812 | 23.1405 | 83.6906 | 18.5365 | 51.5403 | 100.1063 | 25.8584 | 50.2964 | 118.2849 | 21.2629 | 46.9784 | 114.1998 | 21.3222 | 76.4906 | 27.0671 | 85.5709 | 23.4456 | 87.537 | 0.57084 | 19.6304 | 0.99786 | 0.032327 | -27.0755 | 3.0953 | 128.99 | 51.67 | 1.1254 | -0.99443 | -5.9387 | 0.88267 | 0.41322 | -15.6482 | 5.4311 | 0.13858 | -0.52813 | 0.048953 | -2.2939 | -1.0238 | -0.36595 | 0.037947
42838.424 | 322 | 22.9187 | 22.8722 | 22.8628 | 22.779 | 22.3981 | 21.7226 | 22.7106 | 21.7722 | 22.362 | 22.3675 | 22.3399 | 21.9917 | 21.204 | 22.1732 | 21.6252 | 21.7989 | 21.9122 | 21.0976 | 21.1945 | 21.445 | 20.4836 | 20.7707 | 22.2235 | 21.8733 | 21.7264 | 24.549 | 116.8934 | 102.1057 | 127.9442 | 22.1304 | 21.7883 | 23.3813 | 22.0264 | 21.8383 | 24.1585 | 42.3076 | 126.7478 |  | 66.8108 | 98.2972 | 99.2173 | 76.4172 |  | 17.0966 | 17.5098 | 16.8225 | 17.3251 | 17.5743 | 20.4834 | 66.6253 | 15.5903 | 17.0772 | 15.6234 | 17.9387 | 18.3549 | 47.3239 | 50.5732 | 46.3562 | 21.6483 |  |  | 0.79994 | -0.47122 | -24.9548 | 0.35545 | 0.021816 | -171.079 | 20.9945 | 0.47539 | 0.24334 | 0.013119 | 0.12893 | 0.00035649 | 0.00034663 | 1.4826 | 21.7703 | 21.9657 | 22.1745 | 22.2201 | 22.028 | 21.3291 | 20.1485 | 22.1777 | 22.3487 | 22.3932 | 22.3402 | 21.955 | 21.1905 | 22.2734 | 61.3749 | 41.2695 | 38.5117 | 30.4696 | 27.654 | 38.7835 | 27.906 | 22.3333 | 22.1039 | 21.657 | 22.0624 | 21.77 | 21.3177 | 21.9373 | 21.6052 | 22.4218 | 40.5632 | 111.5407 | 87.8311 | 59.3213 | 0.55482 | -0.12018 | 47.9195 | 21.9343 | 22.2542 | 20.2774 | 21.5897 | 22.0317 | 21.9139 | 21.8646 | 26.3128 | 21.7861 | 21.5192 | 23.0587 | 113.1469 | 144.3793 | 86.9729 | 87.9866 | 55.609 |  | 40.6621 | 83.204 | 43.4725 | 62.6959 | 44.6852 | 49.2224 |  | 55.3666 |  |  | 21.9837 | 23.8401 | 43.069 | [5 empty] | 21.893 | 49.1651 | 21.6784 | 22.0672 | 29.6791 | 21.254 | 21.8811 | 24.3949 | 59.9168 | 150.251 |  | 52.3434 | 104.6928 | 21.3738 | 49.9241 | 116.3816 | 35.7376 | 84.5473 | 23.229 | 82.8078 | 23.1638 | 83.8783 | 18.5271 | 51.6125 | 100.4926 | 25.9009 | 50.4574 | 118.6972 | 21.2662 | 47.1493 | 114.4349 | 21.3184 | 76.7156 | 27.102 | 85.8111 | 23.4711 | 87.8685 | 0.66989 | 19.6266 | 1.0037 | 0.033017 | -27.066 | 3.0953 | 108.12 | 52.66 | 1.2483 | -0.81559 | -5.9352 | 0.70836 | 0.17638 | -15.6195 | 5.4717 | 0.13468 | -0.53382 | 0.078321 | -1.9733 | -0.71264 | -0.38599 | 0.028121
42838.424 | 323 | 22.9176 | 22.8788 | 22.8661 | 22.7831 | 22.4013 | 21.7238 | 22.7186 | 21.7764 | 22.3608 | 22.3602 | 22.3349 | 21.9836 | 21.2008 | 22.174 | 21.6237 | 21.7862 | 21.9103 | 21.0891 | 21.1919 | 21.4363 | 20.4758 | 20.7655 | 22.2267 | 21.8648 | 21.7211 | 24.5708 | 117.1911 | 102.2642 | 127.7181 | 22.1246 | 21.7873 | 23.3923 | 22.0268 | 21.83 | 24.1758 | 42.4773 | 126.3478 |  | 67.0625 | 98.5004 | 99.4899 | 76.5473 |  | 17.0923 | 17.503 | 16.8112 | 17.3248 | 17.5643 | 20.4624 | 67.3418 | 15.4993 | 17.0721 | 15.6797 | 17.9313 | 18.3584 | 47.3522 | 50.5268 | 46.3883 | 21.649 |  |  | 0.77891 | -0.39696 | -24.7859 | 0.44942 | 0.1079 | -171.3944 | 20.409 | 0.58776 | -0.055951 | 0.082982 | 0.084834 | 0.00037127 | 0.00033677 | 1.4658 | 21.7809 | 21.9752 | 22.1791 | 22.232 | 22.043 | 21.3352 | 20.1561 | 22.182 | 22.3597 | 22.3937 | 22.3393 | 21.9701 | 21.2032 | 22.2793 | 58.4999 | 38.3776 | 35.7609 | 28.6765 | 26.3748 | 38.8534 | 27.9192 | 22.332 | 22.1014 | 21.6553 | 22.0517 | 21.7741 | 21.3232 | 21.9395 | 21.6019 | 22.4308 | 40.6971 | 111.7406 | 88.1058 | 59.9133 | 0.5328 | -0.14338 | 47.963 | 21.934 | 22.255 | 20.2864 | 21.5875 | 22.0337 | 21.922 | 21.8716 | 26.3443 | 21.7854 | 21.5218 | 23.0712 | 113.5321 | 145.0706 | 87.248 | 88.2983 | 55.8218 |  | 40.7745 | 84.3297 | 43.6227 | 62.0596 | 44.8348 | 49.2888 |  | 55.5378 |  |  | 21.9917 | 23.8664 | 43.0926 | [5 empty] | 21.898 | 48.6182 | 21.6776 | 22.0713 | 29.6937 | 21.2505 | 21.8855 | 24.4442 | 60.2271 | 150.5576 |  | 52.4904 | 105.1184 | 21.3937 | 50.2843 | 116.8029 | 35.8522 | 84.8565 | 23.2479 | 82.975 | 23.1754 | 84.0758 | 18.5351 | 51.7204 | 100.8505 | 25.9539 | 50.6206 | 118.8319 | 21.2828 | 47.2845 | 114.5858 | 21.3244 | 76.9731 | 27.147 | 85.9696 | 23.4974 | 88.176 | 0.52687 | 19.6207 | 1.0089 | 0.034033 | -27.1482 | 3.0953 | 118.05 | 51.31 | 1.2314 | -0.74857 | -5.915 | 0.79649 | 0.39225 | -15.6334 | 5.3947 | 0.13268 | -0.55983 | 0.10124 | -1.6456 | -0.40546 | -0.38368 | 0.016334
42838.424 | 324 | 22.9156 | 22.8815 | 22.8653 | 22.7849 | 22.4021 | 21.7287 | 22.7182 | 21.7855 | 22.3628 | 22.3706 | 22.3459 | 21.9976 | 21.207 | 22.1721 | 21.6289 | 21.7927 | 21.9154 | 21.0964 | 21.1988 | 21.4463 | 20.4847 | 20.7758 | 22.2433 | 21.8712 | 21.7362 | 24.5917 | 117.4098 | 102.4643 | 126.8507 | 22.1397 | 21.7964 | 23.4204 | 22.031 | 21.8399 | 24.211 | 42.6252 | 127.3357 |  | 67.3674 | 98.9487 | 99.7176 | 76.571 |  | 17.0941 | 17.4953 | 16.8089 | 17.314 | 17.5477 | 20.5887 | 67.8477 | 15.4906 | 17.0686 | 15.7019 | 17.9341 | 18.3585 | 47.3789 | 50.4743 | 46.4242 | 21.6492 |  |  | 0.65932 | -0.36016 | -24.617 | 0.35349 | 0.003416 | -167.9295 | 21.1995 | 0.75598 | 0.10245 | 0.039344 | 0.16035 | 0.00037456 | 0.00035484 | 1.4321 | 21.7708 | 21.9755 | 22.1696 | 22.2296 | 22.0443 | 21.3347 | 20.1476 | 22.1835 | 22.3588 | 22.3883 | 22.3423 | 21.9684 | 21.1925 | 22.2719 | 57.4329 | 37.1811 | 33.7173 | 27.4724 | 25.1362 | 38.9455 | 27.9274 | 22.3276 | 22.0888 | 21.6577 | 22.0515 | 21.7663 | 21.3114 | 21.9346 | 21.5998 | 22.4379 | 40.8343 | 111.74 | 88.2802 | 60.0965 | 0.30356 | -0.14775 | 48.4045 | 21.9279 | 22.2504 | 20.2865 | 21.5824 | 22.0284 | 21.9197 | 21.8667 | 26.3706 | 21.7868 | 21.5187 | 23.0858 | 113.9331 | 145.5755 | 87.4894 | 88.551 | 56.4561 |  | 40.8886 | 85.3292 | 43.7723 | 63.1655 | 45.0326 | 49.4438 |  | 55.7129 |  |  | 22.0063 | 23.8928 | 43.3218 | [5 empty] | 21.8936 | 49.1363 | 21.6764 | 22.0692 | 29.7212 | 21.2444 | 21.8849 | 24.4972 | 60.5126 | 150.9142 |  | 52.5969 | 105.5537 | 21.4173 | 50.6256 | 117.4911 | 36.0116 | 85.1385 | 23.273 | 83.135 | 23.1941 | 84.291 | 18.5405 | 51.8924 | 101.1642 | 26.0062 | 51.0042 | 118.8707 | 21.2971 | 47.3917 | 114.7398 | 21.3477 | 77.3124 | 27.2063 | 86.1629 | 23.5226 | 88.4264 | 0.80271 | 19.6158 | 1.0145 | 0.034469 | -27.1282 | 3.0952 | 132.05 | 52.46 | 1.1317 | -0.71302 | -5.8948 | 0.70637 | 0.069808 | -15.4779 | 5.4993 | 0.11903 | -0.58236 | 0.077458 | -1.5162 | -0.17743 | -0.37918 | 0.01602
42838.424 | 325 | 22.9215 | 22.8762 | 22.8637 | 22.78 | 22.401 | 21.7235 | 22.7241 | 21.78 | 22.3676 | 22.3697 | 22.3426 | 21.993 | 21.2002 | 22.1734 | 21.632 | 21.7985 | 21.9186 | 21.0997 | 21.1989 | 21.4471 | 20.4917 | 20.7764 | 22.2578 | 21.883 | 21.7387 | 24.6132 | 117.5739 | 102.6362 | 126.1377 | 22.1352 | 21.786 | 23.4317 | 22.0185 | 21.8327 | 24.2169 | 42.802 | 129.4261 |  | 67.6997 | 99.5398 | 99.9426 | 78.3638 |  | 17.0997 | 17.5102 | 16.8211 | 17.3236 | 17.5457 | 20.7142 | 68.4191 | 15.4459 | 17.0732 | 15.6157 | 17.942 | 18.3545 | 47.4069 | 50.4276 | 46.4594 | 21.6562 |  |  | 0.70071 | -0.24386 | -24.3956 | 0.62487 | 0.16178 | -169.5072 | 20.9892 | 0.83089 | -0.020729 | 0.025497 | 0.26677 | 0.00038441 | 0.00037456 | 1.4507 | 21.7702 | 21.9732 | 22.1684 | 22.2285 | 22.0409 | 21.3303 | 20.1377 | 22.1814 | 22.3588 | 22.3976 | 22.3387 | 21.9618 | 21.1957 | 22.2745 | 55.7729 | 35.3223 | 31.3368 | 26.9345 | 24.2562 | 38.9985 | 27.917 | 22.3242 | 22.0924 | 21.66 | 22.0528 | 21.7705 | 21.3189 | 21.935 | 21.5977 | 22.4498 | 40.9683 | 111.7956 | 88.5418 | 60.2028 | 0.79782 | -0.20653 | 48.7199 | 21.9333 | 22.2555 | 20.285 | 21.5855 | 22.0376 | 21.9188 | 21.8717 | 26.4049 | 21.7836 | 21.5239 | 23.1046 | 114.3516 | 145.9444 | 87.741 | 88.791 | 57.1984 |  | 41.0077 | 86.2435 | 43.9425 | 64.3149 | 45.2586 | 49.3717 |  | 55.927 |  |  | 22.0172 | 23.9243 | 43.5154 | [5 empty] | 21.8919 | 50.1573 | 21.6708 | 22.0714 | 29.7767 | 21.2378 | 21.8839 | 24.5407 | 60.8113 | 151.2479 |  | 52.7113 | 105.9012 | 21.4388 | 50.8704 | 118.4924 | 36.1651 | 85.3992 | 23.2873 | 83.4193 | 23.2195 | 84.5255 | 18.5461 | 52.0537 | 101.5904 | 26.049 | 51.4179 | 119.1493 | 21.3049 | 47.5099 | 115.1461 | 21.3704 | 77.5772 | 27.2485 | 86.3331 | 23.5509 | 88.7106 | 0.47734 | 19.6094 | 1.0201 | 0.033707 | -27.1292 | 3.0953 | 115.86 | 51.63 | 1.1657 | -0.58672 | -5.8683 | 0.9392 | 0.48052 | -15.5537 | 5.4732 | 0.10256 | -0.6018 | 0.05346 | -1.3255 | 0.085865 | -0.4228 | 0.017728
42838.4241 | 326 | 22.9123 | 22.8687 | 22.8652 | 22.7756 | 22.3976 | 21.726 | 22.7195 | 21.7778 | 22.3573 | 22.3702 | 22.3414 | 21.9902 | 21.1984 | 22.1661 | 21.6316 | 21.7924 | 21.9189 | 21.0976 | 21.1921 | 21.4406 | 20.4841 | 20.774 | 22.267 | 21.8759 | 21.7362 | 24.6269 | 117.7882 | 102.8279 | 125.7404 | 22.132 | 21.7918 | 23.4397 | 22.0201 | 21.842 | 24.2348 | 43.0201 | 130.3096 |  | 68.0019 | 100.0027 | 100.1362 | 79.1602 |  | 17.1046 | 17.5062 | 16.8293 | 17.3369 | 17.5563 | 20.6062 | 68.0459 | 15.4662 | 17.0726 | 15.5703 | 17.9489 | 18.3563 | 47.4257 | 50.365 | 46.4913 | 21.6474 |  |  | 0.83608 | -0.37134 | -24.4061 | 0.64721 | 0.23669 | -169.134 | 21.5142 | 0.47802 | 0.15947 | 0.23488 | 0.27979 | 0.00036634 | 0.00036306 | 1.506 | 21.7753 | 21.981 | 22.1784 | 22.2262 | 22.0436 | 21.3469 | 20.1502 | 22.189 | 22.3617 | 22.4025 | 22.3459 | 21.9657 | 21.1964 | 22.2771 | 57.969 | 35.852 | 30.4127 | 26.0448 | 23.9525 | 39.1306 | 27.9118 | 22.326 | 22.1034 | 21.6625 | 22.0514 | 21.7731 | 21.3191 | 21.934 | 21.602 | 22.4632 | 41.1004 | 111.942 | 88.8357 | 60.232 | 0.76793 | 0.022094 | 48.9652 | 21.9292 | 22.2545 | 20.2833 | 21.5844 | 22.0355 | 21.9153 | 21.8782 | 26.4306 | 21.7895 | 21.5253 | 23.1135 | 114.7383 | 146.416 | 88.003 | 89.052 | 57.6075 |  | 41.1235 | 86.6931 | 44.1261 | 64.3057 | 45.4384 | 49.2717 |  | 56.1306 |  |  | 22.0324 | 23.9399 | 44.0307 | [5 empty] | 21.8965 | 50.0377 | 21.6716 | 22.0681 | 29.8378 | 21.2312 | 21.878 | 24.5722 | 61.1522 | 151.8024 |  | 52.9192 | 106.2351 | 21.4623 | 51.0465 | 119.18 | 36.2715 | 85.5911 | 23.2963 | 83.806 | 23.2463 | 84.7231 | 18.5494 | 52.2212 | 102.0468 | 26.1003 | 51.7211 | 119.3962 | 21.3174 | 47.6573 | 115.5552 | 21.3887 | 77.797 | 27.2871 | 86.4977 | 23.588 | 89.0173 | 0.75986 | 19.6027 | 1.0257 | 0.034157 | -27.0815 | 3.0952 | 117.34 | 52.07 | 1.2727 | -0.724 | -5.8696 | 0.95583 | 0.5811 | -15.5337 | 5.5402 | 0.095224 | -0.60786 | 0.060028 | -1.5539 | 0.18793 | -0.43731 | 0.02152
42838.4241 | 327 | 22.9186 | 22.8733 | 22.8721 | 22.7812 | 22.397 | 21.7284 | 22.7093 | 21.7841 | 22.3612 | 22.3643 | 22.335 | 22.0022 | 21.1991 | 22.1656 | 21.628 | 21.7918 | 21.9109 | 21.097 | 21.1914 | 21.4437 | 20.4816 | 20.775 | 22.2721 | 21.8696 | 21.7318 | 24.6485 | 118.1557 | 103.1053 | 126.6854 | 22.1302 | 21.7907 | 23.4483 | 22.0168 | 21.8426 | 24.2485 | 43.2391 | 130.2961 |  | 68.2393 | 100.3544 | 100.3826 | 79.0442 |  | 17.1042 | 17.5066 | 16.8495 | 17.352 | 17.5683 | 20.5367 | 68.5837 | 15.532 | 17.0704 | 15.5813 | 17.9593 | 18.356 | 47.4559 | 50.3017 | 46.492 | 21.6464 |  |  | 0.57126 | -0.40616 | -24.6716 | 0.29631 | 0.1723 | -169.6406 | 21.1903 | 0.75992 | -0.036102 | 0.10921 | 0.33586 | 0.00036306 | 0.00032856 | 1.5072 | 21.7793 | 21.9825 | 22.1763 | 22.2267 | 22.0391 | 21.3405 | 20.1596 | 22.1914 | 22.3631 | 22.399 | 22.3439 | 21.9715 | 21.1973 | 22.2742 | 59.3763 | 38.3457 | 32.85 | 25.7422 | 23.5646 | 39.2746 | 27.9335 | 22.3265 | 22.0989 | 21.6554 | 22.0563 | 21.7772 | 21.3166 | 21.9373 | 21.6067 | 22.4729 | 41.222 | 112.0384 | 89.0998 | 60.5249 | 0.82042 | 0.24273 | 49.0699 | 21.9303 | 22.2516 | 20.2858 | 21.5864 | 22.0393 | 21.9158 | 21.8774 | 26.4643 | 21.7867 | 21.5282 | 23.1236 | 115.1249 | 146.8854 | 88.299 | 89.3412 | 57.5842 |  | 41.2296 | 86.4516 | 44.2722 | 64.1303 | 45.6095 | 49.4358 |  | 56.322 |  |  | 22.0549 | 23.9431 | 44.1916 | [5 empty] | 21.8955 | 49.6748 | 21.6726 | 22.0639 | 29.8924 | 21.2335 | 21.8778 | 24.6266 | 61.5018 | 152.7898 |  | 53.2684 | 106.6139 | 21.4774 | 51.3014 | 119.5681 | 36.3716 | 85.8423 | 23.3174 | 84.101 | 23.2728 | 84.8783 | 18.5462 | 52.553 | 102.4575 | 26.1581 | 51.9195 | 119.5763 | 21.3338 | 47.8591 | 115.9518 | 21.4059 | 78.1795 | 27.3434 | 86.7069 | 23.6142 | 89.3022 | 0.65839 | 19.5977 | 1.0315 | 0.034534 | -27.1285 | 3.0953 | 112.3 | 52.22 | 1.0532 | -0.7572 | -5.9014 | 0.64675 | 0.49573 | -15.5551 | 5.4977 | 0.099565 | -0.59604 | 0.070911 | -1.6933 | -0.080335 | -0.42643 | 0.017617
42838.4241 | 328 | 22.9152 | 22.8842 | 22.8678 | 22.7812 | 22.3981 | 21.7243 | 22.7134 | 21.7804 | 22.3666 | 22.3652 | 22.3436 | 21.9948 | 21.1992 | 22.1692 | 21.6263 | 21.7916 | 21.9055 | 21.0922 | 21.1913 | 21.4475 | 20.4872 | 20.7728 | 22.2808 | 21.8681 | 21.735 | 24.6606 | 118.4297 | 103.4002 | 126.9118 | 22.1296 | 21.7894 | 23.4622 | 22.0178 | 21.8333 | 24.2643 | 43.4225 | 131.1956 |  | 68.5085 | 100.5934 | 100.6685 | 80.0818 |  | 17.0951 | 17.5063 | 16.8625 | 17.3576 | 17.5698 | 20.5197 | 69.3547 | 15.4977 | 17.0724 | 15.5941 | 17.9641 | 18.3607 | 47.4891 | 50.2321 | 46.4962 | 21.6536 |  |  | 0.56075 | -0.5803 | -25.0323 | 0.39817 | 0.010644 | -170.5803 | 21.3598 | 0.68238 | 0.0018448 | 0.2053 | 0.25357 | 0.00034334 | 0.0003187 | 1.4406 | 21.772 | 21.971 | 22.1631 | 22.2215 | 22.0324 | 21.3296 | 20.1459 | 22.1794 | 22.3581 | 22.395 | 22.3365 | 21.9564 | 21.1815 | 22.264 | 60.8292 | 41.4207 | 37.1946 | 27.0298 | 23.7084 | 39.4299 | 27.9911 | 22.3265 | 22.0955 | 21.654 | 22.0576 | 21.7625 | 21.3156 | 21.9365 | 21.6086 | 22.4904 | 41.3563 | 112.2416 | 89.37 | 60.6138 | 0.50429 | 0.24139 | 49.3455 | 21.9324 | 22.2502 | 20.2909 | 21.5881 | 22.0383 | 21.9156 | 21.8794 | 26.4938 | 21.7883 | 21.526 | 23.1364 | 115.4942 | 147.1408 | 88.604 | 89.6698 | 57.6891 |  | 41.3286 | 86.6675 | 44.4041 | 63.9538 | 45.7857 | 49.5995 |  | 56.5242 |  |  | 22.0751 | 23.9613 | 44.2897 | [5 empty] | 21.895 | 49.6021 | 21.6784 | 22.0658 | 29.9042 | 21.2422 | 21.8837 | 24.6835 | 61.8782 | 153.448 |  | 53.7006 | 107.05 | 21.5053 | 51.6524 | 120.0576 | 36.4923 | 86.0428 | 23.3266 | 84.3392 | 23.2979 | 85.1561 | 18.5205 | 53.0093 | 102.9073 | 26.2091 | 52.1518 | 119.7693 | 21.3497 | 48.0648 | 116.4278 | 21.4263 | 78.5735 | 27.3929 | 86.94 | 23.6349 | 89.5457 | 0.99545 | 19.5911 | 1.037 | 0.034875 | -27.1214 | 3.0952 | 113.05 | 51.33 | 1.0438 | -0.90507 | -5.9444 | 0.74971 | 0.12321 | -15.5977 | 5.5194 | 0.1001 | -0.59741 | 0.082003 | -1.8364 | -0.55631 | -0.44884 | 0.019823
42838.4241 | 329 | 22.9184 | 22.8848 | 22.871 | 22.7803 | 22.3997 | 21.7275 | 22.7208 | 21.7793 | 22.3714 | 22.3659 | 22.3439 | 21.9901 | 21.2051 | 22.1621 | 21.6323 | 21.7868 | 21.9082 | 21.0943 | 21.1899 | 21.4436 | 20.4825 | 20.7703 | 22.2901 | 21.8685 | 21.7422 | 24.6792 | 118.6238 | 103.7139 | 127.0266 | 22.1213 | 21.7835 | 23.474 | 22.0165 | 21.8354 | 24.2821 | 43.6236 | 131.53 |  | 68.773 | 100.7699 | 100.9472 | 83.3416 |  | 17.0833 | 17.496 | 16.8549 | 17.3557 | 17.5552 | 20.5777 | 70.4148 | 15.4014 | 17.0758 | 15.6602 | 17.9638 | 18.3694 | 47.5176 | 50.1633 | 46.5131 | 21.65 |  |  | 0.72306 | -0.5251 | -25.0757 | 0.2996 | 0.067156 | -166.6251 | 20.9084 | 0.60287 | -0.068795 | 0.078157 | 0.26607 | 0.0003647 | 0.00032199 | 1.386 | 21.7775 | 21.9753 | 22.1688 | 22.2301 | 22.0343 | 21.33 | 20.1464 | 22.1848 | 22.3541 | 22.3928 | 22.3452 | 21.9669 | 21.1884 | 22.2667 | 60.2154 | 41.1354 | 37.4398 | 28.8105 | 24.9684 | 39.5344 | 28.0323 | 22.3311 | 22.093 | 21.6526 | 22.0564 | 21.7734 | 21.3192 | 21.9317 | 21.6026 | 22.4934 | 41.4894 | 112.5363 | 89.6752 | 61.1473 | 0.10028 | -0.22973 | 49.5004 | 21.9239 | 22.2489 | 20.2839 | 21.5834 | 22.0318 | 21.9101 | 21.8798 | 26.5207 | 21.7851 | 21.5294 | 23.1566 | 115.7659 | 147.6297 | 88.8993 | 90.0002 | 57.9693 |  | 41.4628 | 87.1447 | 44.5647 | 63.5779 | 45.9688 | 49.9812 |  | 56.7479 |  |  | 22.073 | 23.9808 | 44.0877 | [5 empty] | 21.8882 | 49.2987 | 21.675 | 22.0698 | 29.8895 | 21.2445 | 21.8914 | 24.7428 | 62.2435 | 153.6556 |  | 54.1902 | 107.4883 | 21.526 | 51.9291 | 120.4591 | 36.6747 | 86.1926 | 23.3479 | 84.5034 | 23.3317 | 85.464 | 18.531 | 53.3071 | 103.4577 | 26.2463 | 52.4328 | 120.0024 | 21.3596 | 48.2737 | 116.7617 | 21.4541 | 78.7632 | 27.456 | 87.2348 | 23.6717 | 89.7272 | 0.88229 | 19.5862 | 1.0424 | 0.035667 | -27.1805 | 3.0952 | 110.48 | 52.9 | 1.1854 | -0.86094 | -5.9494 | 0.65031 | 0.30952 | -15.4173 | 5.4613 | 0.096994 | -0.60504 | 0.098879 | -1.7559 | -0.57873 | -0.53235 | 0.0096401
42838.4241 | 330 | 22.9239 | 22.8765 | 22.8626 | 22.78 | 22.3983 | 21.7281 | 22.7135 | 21.775 | 22.3701 | 22.36 | 22.3332 | 21.9874 | 21.197 | 22.1656 | 21.6317 | 21.795 | 21.9211 | 21.1024 | 21.1945 | 21.4519 | 20.4801 | 20.7765 | 22.3031 | 21.881 | 21.7395 | 24.7079 | 118.9263 | 104.0467 | 127.41 | 22.1285 | 21.7932 | 23.5006 | 22.0178 | 21.8444 | 24.308 | 43.8358 | 132.1939 |  | 69.07 | 101.0806 | 101.2724 | 86.1224 |  | 17.0781 | 17.4969 | 16.8492 | 17.3566 | 17.5372 | 20.9532 | 71.5571 | 15.3673 | 17.0676 | 15.7138 | 17.9691 | 18.379 | 47.5512 | 50.0894 | 46.5344 | 21.6507 |  |  | 0.62777 | -0.65521 | -24.918 | 0.7149 | -0.041924 | -168.1358 | 21.6463 | 0.43465 | 0.033175 | 0.23488 | 0.25132 | 0.00038277 | 0.00037456 | 1.3889 | 21.7735 | 21.9747 | 22.1721 | 22.2286 | 22.0376 | 21.3283 | 20.1481 | 22.1866 | 22.3565 | 22.3906 | 22.3435 | 21.9589 | 21.1911 | 22.2702 | 56.7545 | 38.9513 | 36.9534 | 28.6274 | 25.5804 | 39.5769 | 28.051 | 22.3359 | 22.0976 | 21.6664 | 22.0612 | 21.7789 | 21.324 | 21.9392 | 21.6087 | 22.5098 | 41.6142 | 112.7967 | 89.9491 | 61.3293 | 0.28351 | -0.31931 | 49.5447 | 21.9187 | 22.2438 | 20.2802 | 21.5825 | 22.0297 | 21.9163 | 21.879 | 26.5573 | 21.7874 | 21.5293 | 23.164 | 116.0808 | 147.7833 | 89.2223 | 90.3053 | 57.9399 |  | 41.5653 | 87.2217 | 44.7044 | 63.7982 | 46.1955 | 50.3937 |  | 56.9594 |  |  | 22.0841 | 24.0009 | 44.2858 | [5 empty] | 21.8921 | 48.9496 | 21.6752 | 22.0711 | 29.9105 | 21.2478 | 21.8863 | 24.7934 | 62.5601 | 154.2376 |  | 54.6517 | 107.9821 | 21.5466 | 52.0957 | 121.1978 | 36.8177 | 86.3641 | 23.3691 | 84.6519 | 23.3585 | 85.7747 | 18.5306 | 53.6755 | 103.9772 | 26.2807 | 52.7021 | 120.2523 | 21.3489 | 48.4233 | 117.2083 | 21.4676 | 78.9208 | 27.4971 | 87.5066 | 23.6913 | 90.0202 | 0.66989 | 19.5818 | 1.0475 | 0.036494 | -27.1701 | 3.0953 | 111.55 | 51.55 | 1.1051 | -0.9617 | -5.9307 | 1.0046 | -0.24471 | -15.497 | 5.5604 | 0.10138 | -0.60228 | 0.10073 | -1.3663 | -0.52249 | -0.60217 | 0.0089346
42838.4241 | 331 | 22.923 | 22.8806 | 22.8686 | 22.781 | 22.393 | 21.7209 | 22.7145 | 21.7817 | 22.3552 | 22.3673 | 22.3402 | 21.9857 | 21.21 | 22.1651 | 21.6357 | 21.7975 | 21.9172 | 21.0931 | 21.199 | 21.4496 | 20.4831 | 20.7841 | 22.3161 | 21.8733 | 21.7351 | 24.7294 | 119.0672 | 104.3647 | 127.2356 | 22.1278 | 21.7903 | 23.4975 | 22.0183 | 21.842 | 24.3242 | 44.0364 | 134.5813 |  | 69.3826 | 101.5119 | 101.5801 | 87.2839 |  | 17.0832 | 17.485 | 16.8421 | 17.3395 | 17.5157 | 21.2227 | 72.8258 | 15.3279 | 17.0642 | 15.6559 | 17.9681 | 18.3741 | 47.5597 | 50.0134 | 46.5409 | 21.6437 |  |  | 0.78877 | -0.56913 | -24.9101 | 0.58216 | 0.12761 | -168.946 | 21.2008 | 0.43728 | 0.14157 | 0.20383 | 0.20149 | 0.00036306 | 0.00034663 | 1.4343 | 21.7706 | 21.971 | 22.1727 | 22.2234 | 22.0354 | 21.3325 | 20.1485 | 22.183 | 22.3576 | 22.3918 | 22.3426 | 21.9552 | 21.1887 | 22.2699 | 54.8302 | 36.6868 | 35.2038 | 27.8728 | 25.1632 | 39.629 | 28.0575 | 22.333 | 22.1025 | 21.6621 | 22.0591 | 21.7812 | 21.329 | 21.9415 | 21.6111 | 22.5248 | 41.7329 | 113.1258 | 90.1848 | 61.247 | 0.30356 | -0.26986 | 49.709 | 21.9238 | 22.2475 | 20.2861 | 21.5841 | 22.0323 | 21.9172 | 21.884 | 26.5814 | 21.7845 | 21.5272 | 23.1822 | 116.3955 | 147.7165 | 89.6151 | 90.6468 | 57.5026 |  | 41.6708 | 86.553 | 44.8379 | 64.1588 | 46.4958 | 50.8221 |  | 57.1613 |  |  | 22.098 | 24.0255 | 45.015 | [5 empty] | 21.8939 | 50.1927 | 21.673 | 22.0726 | 29.9475 | 21.2404 | 21.8815 | 24.8395 | 62.8474 | 154.5317 |  | 55.0886 | 108.38 | 21.5624 | 52.335 | 121.9225 | 36.9421 | 87.005 | 23.3749 | 84.9274 | 23.3678 | 86.0961 | 18.5443 | 54.0087 | 104.5299 | 26.3358 | 52.9186 | 120.4939 | 21.3493 | 48.5951 | 117.673 | 21.4721 | 79.1195 | 27.5239 | 87.6932 | 23.7095 | 90.5801 | 0.67917 | 19.576 | 1.0529 | 0.036226 | -27.0359 | 3.0952 | 123.1 | 52.37 | 1.2385 | -0.89629 | -5.9296 | 0.90649 | 0.42713 | -15.5414 | 5.5054 | 0.1172 | -0.57902 | 0.10128 | -1.1464 | -0.32732 | -0.62741 | 0.015359
42838.4241 | 332 | 22.9103 | 22.8732 | 22.8615 | 22.7763 | 22.3971 | 21.7262 | 22.7211 | 21.7742 | 22.3652 | 22.3719 | 22.3322 | 21.9942 | 21.1999 | 22.165 | 21.6303 | 21.7852 | 21.9114 | 21.0897 | 21.1933 | 21.4456 | 20.4803 | 20.7715 | 22.3183 | 21.8641 | 21.7407 | 24.7473 | 119.3082 | 104.6383 | 127.5623 | 22.1205 | 21.7931 | 23.5197 | 22.0229 | 21.8289 | 24.3342 | 44.2586 | 134.6065 |  | 69.7007 | 101.7911 | 101.8817 | 88.5295 |  | 17.0812 | 17.4864 | 16.8395 | 17.328 | 17.4979 | 21.3647 | 73.5558 | 15.2897 | 17.0633 | 15.5846 | 17.9655 | 18.3788 | 47.5677 | 49.9419 | 46.5358 | 21.6442 |  |  | 0.80454 | -0.79321 | -24.8615 | 0.66561 | 0.14864 | -169.0117 | 21.5031 | 0.70998 | 0.017218 | 0.060114 | 0.26902 | 0.00035156 | 0.00033677 | 1.4076 | 21.7712 | 21.972 | 22.1693 | 22.2251 | 22.037 | 21.333 | 20.1487 | 22.1838 | 22.3588 | 22.3961 | 22.3483 | 21.9558 | 21.193 | 22.2702 | 54.569 | 36.3621 | 33.7102 | 27.1728 | 24.5715 | 39.6835 | 28.0615 | 22.3367 | 22.0955 | 21.6538 | 22.0554 | 21.7798 | 21.3249 | 21.9336 | 21.6082 | 22.5323 | 41.8397 | 113.3623 | 90.3313 | 61.1323 | 0.23947 | -0.22098 | 50.0493 | 21.9299 | 22.2538 | 20.2938 | 21.5893 | 22.0393 | 21.9213 | 21.8922 | 26.6164 | 21.7902 | 21.5349 | 23.2014 | 116.688 | 148.0401 | 90.0332 | 91.0082 | 57.6531 |  | 41.8267 | 86.5495 | 44.9744 | 63.5427 | 46.7271 | 50.7743 |  | 57.3681 |  |  | 22.0979 | 24.038 | 45.8697 | [5 empty] | 21.8927 | 50.4764 | 21.6886 | 22.0786 | 29.9677 | 21.2477 | 21.8823 | 24.8944 | 63.1864 | 154.2773 |  | 55.5528 | 108.5922 | 21.5926 | 52.6213 | 122.2693 | 37.0916 | 87.3459 | 23.4061 | 85.3967 | 23.3958 | 86.4558 | 18.5273 | 54.2703 | 105.1241 | 26.3932 | 53.076 | 120.7583 | 21.3589 | 48.7519 | 117.813 | 21.4884 | 79.4158 | 27.5902 | 87.8654 | 23.7537 | 90.9635 | 0.7274 | 19.5698 | 1.0585 | 0.036407 | -27.1277 | 3.0953 | 131.09 | 51.97 | 1.2513 | -1.0581 | -5.9239 | 0.96929 | 0.46109 | -15.5482 | 5.5459 | 0.11846 | -0.57414 | 0.12653 | -1.1109 | -0.1609 | -0.65423 | 0.022267
42838.4241 | 333 | 22.91 | 22.8814 | 22.8634 | 22.7814 | 22.3898 | 21.7246 | 22.7176 | 21.7769 | 22.3586 | 22.3632 | 22.3389 | 21.9886 | 21.1973 | 22.1684 | 21.6214 | 21.78 | 21.901 | 21.0924 | 21.1901 | 21.4382 | 20.4788 | 20.7809 | 22.3319 | 21.8564 | 21.746 | 24.7662 | 119.8173 | 104.8637 | 128.6658 | 22.1341 | 21.7919 | 23.5362 | 22.019 | 21.8411 | 24.3553 | 44.4884 | 133.9587 |  | 69.9984 | 102.1176 | 102.1762 | 90.0497 |  | 17.0837 | 17.4945 | 16.8414 | 17.3301 | 17.5076 | 21.6072 | 73.8309 | 15.279 | 17.0631 | 15.5313 | 17.9744 | 18.3833 | 47.586 | 49.8668 | 46.5463 | 21.6465 |  |  | 0.68692 | -0.65652 | -24.711 | 0.35349 | 0.057956 | -170.4364 | 21.2586 | 0.71984 | 0.18574 | 0.064939 | 0.22441 | 0.00035156 | 0.00034992 | 1.3623 | 21.7778 | 21.98 | 22.1736 | 22.2324 | 22.0409 | 21.3369 | 20.156 | 22.1864 | 22.3643 | 22.4019 | 22.3454 | 21.9667 | 21.1954 | 22.2735 | 52.9582 | 36.4087 | 32.9004 | 26.4971 | 24.2453 | 39.723 | 28.0576 | 22.3293 | 22.1034 | 21.6632 | 22.0671 | 21.7828 | 21.3313 | 21.9366 | 21.6124 | 22.5451 | 41.9608 | 113.452 | 90.5583 | 60.6543 | 0.40009 | -0.034966 | 50.2212 | 21.9293 | 22.2533 | 20.2972 | 21.5873 | 22.0342 | 21.9103 | 21.8934 | 26.6546 | 21.7855 | 21.5344 | 23.2146 | 116.9237 | 148.3904 | 90.4621 | 91.4038 | 57.8697 |  | 41.9641 | 86.4533 | 45.1254 | 63.9853 | 46.9416 | 51.2536 |  | 57.5491 |  |  | 22.1036 | 24.0508 | 45.9403 | [5 empty] | 21.8896 | 50.5595 | 21.6803 | 22.0715 | 29.9906 | 21.245 | 21.8834 | 24.955 | 63.5585 | 154.6855 |  | 55.9226 | 109.0098 | 21.6176 | 52.8738 | 122.7142 | 37.2451 | 87.634 | 23.4397 | 85.9566 | 23.42 | 86.7323 | 18.5207 | 54.4331 | 105.4503 | 26.4454 | 53.3559 | 120.8229 | 21.3752 | 48.9414 | 118.4746 | 21.514 | 79.6954 | 27.641 | 88.1097 | 23.7959 | 91.1453 | 0.7465 | 19.5658 | 1.0638 | 0.03677 | -27.1538 | 3.0953 | 139.68 | 51.41 | 1.1578 | -0.96266 | -5.906 | 0.70637 | 0.28804 | -15.62 | 5.5165 | 0.11723 | -0.56617 | 0.12179 | -0.92726 | -0.071369 | -0.68841 | 0.039768
42838.4241 | 334 | 22.9122 | 22.8735 | 22.855 | 22.7783 | 22.3841 | 21.7201 | 22.7147 | 21.7643 | 22.3548 | 22.3651 | 22.3362 | 21.9823 | 21.1937 | 22.1595 | 21.6353 | 21.7955 | 21.9165 | 21.0957 | 21.1937 | 21.448 | 20.489 | 20.7806 | 22.3503 | 21.8706 | 21.7489 | 24.7867 | 120.057 | 105.1258 | 128.4242 | 22.1362 | 21.7951 | 23.5502 | 22.0193 | 21.8434 | 24.38 | 44.6633 | 134.5131 |  | 70.2908 | 102.5436 | 102.4752 | 90.6504 |  | 17.0863 | 17.5035 | 16.8439 | 17.3399 | 17.5003 | 21.705 | 73.7554 | 15.3155 | 17.0697 | 15.5174 | 17.9773 | 18.3811 | 47.6135 | 49.7791 | 46.5544 | 21.6459 |  |  | 0.71057 | -0.45282 | -24.665 | 0.49739 | 0.19727 | -168.5215 | 21.4584 | 0.92223 | 0.066452 | 0.020672 | 0.21295 | 0.0003302 | 0.00033513 | 1.3298 | 21.7837 | 21.9808 | 22.1724 | 22.2333 | 22.046 | 21.342 | 20.1534 | 22.1889 | 22.3723 | 22.397 | 22.3482 | 21.9718 | 21.1965 | 22.2776 | 51.8076 | 36.2843 | 32.8144 | 26.4842 | 23.8024 | 39.776 | 28.0726 | 22.3302 | 22.092 | 21.6554 | 22.0606 | 21.7753 | 21.3266 | 21.9324 | 21.6108 | 22.556 | 42.0683 | 113.5969 | 90.7535 | 60.669 | 0.78032 | -0.078712 | 50.3585 | 21.9278 | 22.2544 | 20.2871 | 21.5917 | 22.0323 | 21.9116 | 21.8968 | 26.6854 | 21.785 | 21.5356 | 23.2258 | 117.3049 | 148.6259 | 90.7832 | 91.7458 | 58.1818 |  | 42.0806 | 86.8382 | 45.2818 | 64.7741 | 47.1688 | 51.6921 |  | 57.7175 |  |  | 22.1186 | 24.0844 | 45.8606 | [5 empty] | 21.8978 | 50.6328 | 21.6837 | 22.0766 | 30.0366 | 21.2502 | 21.8914 | 25.0032 | 63.9314 | 155.4847 |  | 56.0614 | 109.289 | 21.6426 | 53.0506 | 123.054 | 37.3891 | 87.9249 | 23.4692 | 86.3287 | 23.4502 | 87.118 | 18.4984 | 54.6255 | 105.9095 | 26.4926 | 53.7065 | 120.8578 | 21.3762 | 49.1305 | 118.9908 | 21.5229 | 80.0122 | 27.6978 | 88.485 | 23.8111 | 91.3749 | 0.7849 | 19.5607 | 1.0704 | 0.038171 | -27.0418 | 3.0952 | 153.86 | 52.27 | 1.1772 | -0.7995 | -5.9006 | 0.83792 | 0.5315 | -15.5346 | 5.5433 | 0.11263 | -0.57137 | 0.10788 | -0.79315 | -0.060063 | -0.69896 | 0.043108
42838.4242 | 335 | 22.908 | 22.8689 | 22.8545 | 22.7785 | 22.3923 | 21.7171 | 22.7135 | 21.7712 | 22.3603 | 22.3631 | 22.3315 | 21.9843 | 21.189 | 22.1596 | 21.6335 | 21.7977 | 21.9206 | 21.0999 | 21.1996 | 21.457 | 20.4914 | 20.7888 | 22.3715 | 21.8783 | 21.7517 | 24.8124 | 120.2209 | 105.3761 | 128.024 | 22.1401 | 21.797 | 23.5629 | 22.0179 | 21.8426 | 24.3953 | 44.8064 | 134.7573 |  | 70.5755 | 102.8379 | 102.7916 | 89.3134 |  | 17.1004 | 17.5108 | 16.854 | 17.3522 | 17.5138 | 21.696 | 73.441 | 15.3801 | 17.0701 | 15.4466 | 17.9795 | 18.3844 | 47.6391 | 49.6978 | 46.5542 | 21.643 |  |  | 0.76971 | -0.36345 | -24.8096 | 0.63079 | 0.16178 | -167.3499 | 21.0694 | 0.50693 | -0.018783 | 0.015846 | 0.20201 | 0.00038441 | 0.00036306 | 1.3515 | 21.7764 | 21.9723 | 22.1771 | 22.2304 | 22.0379 | 21.3411 | 20.1565 | 22.1912 | 22.371 | 22.3984 | 22.3467 | 21.9604 | 21.1928 | 22.2677 | 54.3064 | 38.1434 | 34.1188 | 26.5954 | 23.6944 | 39.8798 | 28.083 | 22.3348 | 22.0949 | 21.6595 | 22.0638 | 21.7705 | 21.3283 | 21.9374 | 21.6135 | 22.5693 | 42.2001 | 114.108 | 90.9798 | 60.9125 | 0.46025 | 0.013916 | 50.6486 | 21.9355 | 22.2549 | 20.2971 | 21.5903 | 22.0388 | 21.9188 | 21.9074 | 26.7191 | 21.7841 | 21.534 | 23.2375 | 117.5878 | 149.3818 | 91.0373 | 92.0472 | 59.5029 |  | 42.2045 | 88.3932 | 45.465 | 65.8781 | 47.4438 | 51.459 |  | 57.9174 |  |  | 22.1358 | 24.1178 | 45.7772 | [5 empty] | 21.8989 | 51.3757 | 21.6888 | 22.0783 | 30.0566 | 21.2561 | 21.8899 | 25.057 | 64.3089 | 155.5075 |  | 56.2414 | 109.7469 | 21.6532 | 53.0899 | 123.4724 | 37.5384 | 88.2387 | 23.5004 | 86.6128 | 23.4883 | 87.4129 | 18.4901 | 54.9104 | 106.4036 | 26.5329 | 54.0172 | 120.9433 | 21.3667 | 49.3338 | 119.2427 | 21.5486 | 80.2601 | 27.7511 | 88.7486 | 23.8376 | 91.7472 | 0.93238 | 19.5538 | 1.0765 | 0.038701 | -27.1462 | 3.0952 | 153.06 | 51.47 | 1.2246 | -0.71628 | -5.9179 | 0.94363 | 0.48132 | -15.4802 | 5.4928 | 0.080251 | -0.60813 | 0.086904 | -1.0585 | -0.20378 | -0.65681 | 0.040943
42838.4242 | 336 | 22.9119 | 22.8698 | 22.8537 | 22.7756 | 22.3944 | 21.7219 | 22.7114 | 21.7761 | 22.3524 | 22.358 | 22.3299 | 21.9746 | 21.1955 | 22.1618 | 21.6201 | 21.7848 | 21.9023 | 21.0837 | 21.192 | 21.4449 | 20.4822 | 20.7835 | 22.3659 | 21.8679 | 21.7377 | 24.821 | 120.4762 | 105.6567 | 128.2586 | 22.1414 | 21.808 | 23.5827 | 22.022 | 21.8499 | 24.4174 | 44.9367 | 134.2883 |  | 70.8554 | 103.0807 | 103.0978 | 87.3944 |  | 17.1009 | 17.5101 | 16.844 | 17.3489 | 17.525 | 21.8285 | 73.0702 | 15.4577 | 17.0614 | 15.3809 | 17.9772 | 18.3937 | 47.6835 | 49.6142 | 46.5568 | 21.6499 |  |  | 0.62318 | -0.26554 | -25.01 | 0.56902 | 0.23866 | -166.3695 | 21.2626 | 0.79081 | -0.10791 | 0.10774 | 0.38447 | 0.00037456 | 0.00036306 | 1.3661 | 21.7765 | 21.9719 | 22.1613 | 22.2272 | 22.0378 | 21.3292 | 20.1478 | 22.1894 | 22.366 | 22.3973 | 22.3371 | 21.9617 | 21.1938 | 22.2695 | 55.9028 | 38.4393 | 36.4034 | 26.9541 | 23.7504 | 39.9955 | 28.1216 | 22.3347 | 22.1007 | 21.6683 | 22.0643 | 21.7781 | 21.327 | 21.9434 | 21.6164 | 22.5798 | 42.3499 | 114.461 | 91.2044 | 61.2276 | 0.84126 | 0.15067 | 50.8285 | 21.9297 | 22.2529 | 20.2899 | 21.5909 | 22.0351 | 21.9108 | 21.8979 | 26.7449 | 21.7829 | 21.5368 | 23.2555 | 117.7896 | 149.7211 | 91.3692 | 92.3354 | 60.6348 |  | 42.3393 | 89.7182 | 45.6082 | 66.6713 | 47.6944 | 51.4015 |  | 58.0759 |  |  | 22.1437 | 24.1338 | 45.8763 | [5 empty] | 21.8996 | 52.0567 | 21.6929 | 22.0788 | 30.0925 | 21.2584 | 21.8935 | 25.1139 | 64.6714 | 155.5842 |  | 56.5735 | 110.0449 | 21.6626 | 53.1461 | 123.9288 | 37.6878 | 88.4456 | 23.5287 | 86.7309 | 23.4929 | 87.7553 | 18.4822 | 55.2646 | 106.8172 | 26.584 | 54.2669 | 121.1955 | 21.3666 | 49.5179 | 119.6001 | 21.5786 | 80.4464 | 27.827 | 88.8763 | 23.8741 | 92.0332 | 0.9526 | 19.548 | 1.083 | 0.038309 | -27.1259 | 3.0952 | 132.74 | 51.95 | 1.1022 | -0.61225 | -5.9418 | 0.89624 | 0.58473 | -15.4383 | 5.5191 | 0.053514 | -0.63991 | 0.073704 | -1.2223 | -0.45309 | -0.59893 | 0.037417
42838.4242 | 337 | 22.9143 | 22.8729 | 22.8601 | 22.7752 | 22.39 | 21.7223 | 22.7088 | 21.7775 | 22.3522 | 22.3625 | 22.3307 | 21.9819 | 21.1925 | 22.1588 | 21.6205 | 21.7845 | 21.8999 | 21.0902 | 21.1895 | 21.4437 | 20.4805 | 20.7836 | 22.3765 | 21.8631 | 21.7437 | 24.8387 | 120.7017 | 105.8126 | 128.0972 | 22.1341 | 21.8 | 23.5914 | 22.0238 | 21.8535 | 24.4324 | 45.0503 | 132.9416 |  | 71.1167 | 103.3743 | 103.3586 | 85.785 |  | 17.1165 | 17.523 | 16.8479 | 17.3584 | 17.5377 | 21.8528 | 73.0706 | 15.472 | 17.0667 | 15.3734 | 17.9845 | 18.393 | 47.6928 | 49.5373 | 46.5643 | 21.6492 |  |  | 0.57783 | -0.29051 | -25.0941 | 0.63539 | 0.13681 | -166.3149 | 21.0687 | 0.77044 | 0.20559 | 0.15683 | 0.29072 | 0.00038113 | 0.00033513 | 1.3408 | 21.778 | 21.9817 | 22.1709 | 22.2284 | 22.044 | 21.3374 | 20.1539 | 22.1937 | 22.3623 | 22.3983 | 22.3431 | 21.9683 | 21.1909 | 22.2699 | 58.4403 | 40.5886 | 39.4172 | 27.4788 | 24.0337 | 40.1421 | 28.1772 | 22.3348 | 22.0964 | 21.6616 | 22.064 | 21.7797 | 21.3279 | 21.9411 | 21.6157 | 22.597 | 42.4903 | 114.637 | 91.3826 | 61.148 | 0.90477 | 0.18015 | 51.1201 | 21.9334 | 22.2575 | 20.3 | 21.5995 | 22.037 | 21.9209 | 21.9098 | 26.7852 | 21.7908 | 21.5479 | 23.2775 | 118.1824 | 150.0098 | 91.6952 | 92.6609 | 61.3422 |  | 42.4514 | 90.3819 | 45.7576 | 67.4856 | 47.9099 | 51.1385 |  | 58.2312 |  |  | 22.1368 | 24.1457 | 45.7342 | [5 empty] | 21.8971 | 52.1231 | 21.6903 | 22.0756 | 30.1505 | 21.253 | 21.8945 | 25.1668 | 65.032 | 155.9569 |  | 56.8203 | 110.4919 | 21.6618 | 53.2667 | 124.6228 | 37.8195 | 88.6998 | 23.5537 | 86.8233 | 23.5041 | 88.1077 | 18.4821 | 55.7461 | 107.2314 | 26.6189 | 54.4506 | 121.1793 | 21.3711 | 49.6769 | 119.9707 | 21.5923 | 80.671 | 27.886 | 88.9074 | 23.901 | 92.2196 | 0.74038 | 19.5423 | 1.0895 | 0.038607 | -27.1129 | 3.0953 | 132.12 | 52 | 1.0611 | -0.6404 | -5.9519 | 0.94708 | 0.44273 | -15.4364 | 5.4941 | 0.037776 | -0.6531 | 0.058691 | -1.4869 | -0.78145 | -0.55024 | 0.044529
42838.4242 | 338 | 22.9183 | 22.8807 | 22.8639 | 22.774 | 22.3924 | 21.7252 | 22.7183 | 21.7837 | 22.3647 | 22.3722 | 22.3377 | 21.9902 | 21.2 | 22.1654 | 21.6251 | 21.7917 | 21.9133 | 21.0952 | 21.1866 | 21.448 | 20.4847 | 20.7869 | 22.3957 | 21.8687 | 21.7519 | 24.865 | 120.9502 | 105.955 | 128.2809 | 22.1351 | 21.8031 | 23.6094 | 22.0315 | 21.8586 | 24.4576 | 45.1654 | 133.0175 |  | 71.3935 | 103.7214 | 103.6158 | 86.3492 |  | 17.1171 | 17.5299 | 16.8522 | 17.3632 | 17.5446 | 21.8971 | 73.9726 | 15.4903 | 17.0652 | 15.3972 | 17.987 | 18.3926 | 47.71 | 49.4512 | 46.5619 | 21.6507 |  |  | 0.86039 | -0.24451 | -24.987 | 0.67021 | 0.39374 | -163.5925 | 21.1607 | 0.91894 | -0.31107 | 0.0019994 | 0.076849 | 0.00034663 | 0.00032692 | 1.3516 | 21.773 | 21.9686 | 22.1636 | 22.2231 | 22.0374 | 21.3205 | 20.1395 | 22.1723 | 22.354 | 22.3919 | 22.3408 | 21.9598 | 21.1874 | 22.2745 | 60.3088 | 40.7187 | 40.8136 | 28.9366 | 24.7152 | 40.2593 | 28.2193 | 22.3295 | 22.0931 | 21.6605 | 22.0601 | 21.7742 | 21.3276 | 21.941 | 21.6115 | 22.6078 | 42.6416 | 114.8999 | 91.6578 | 61.1506 | 0.20507 | -0.11009 | 51.1114 | 21.9298 | 22.2484 | 20.3017 | 21.5971 | 22.0433 | 21.9244 | 21.9141 | 26.8074 | 21.7927 | 21.5467 | 23.2895 | 118.5408 | 150.4224 | 91.9442 | 92.9245 | 61.4684 |  | 42.5817 | 90.8242 | 45.9002 | 69.281 | 48.1198 | 51.1814 |  | 58.4118 |  |  | 22.1419 | 24.1601 | 45.5353 | [5 empty] | 21.8947 | 52.0748 | 21.6847 | 22.0737 | 30.216 | 21.2474 | 21.8866 | 25.2257 | 65.3987 | 156.1833 |  | 56.9423 | 111.084 | 21.6755 | 53.4543 | 125.1172 | 37.9877 | 88.9425 | 23.5831 | 86.9821 | 23.533 | 88.4168 | 18.4917 | 56.1494 | 107.6565 | 26.6454 | 54.6541 | 121.1367 | 21.3867 | 49.908 | 120.1926 | 21.6153 | 80.9517 | 27.9366 | 88.9862 | 23.9306 | 92.3549 | 0.98932 | 19.5391 | 1.0964 | 0.037794 | -27.1637 | 3.0953 | 134.61 | 51.45 | 1.2952 | -0.58752 | -5.9392 | 0.97271 | 0.75114 | -15.3107 | 5.5065 | 0.038821 | -0.66037 | 0.016225 | -1.6807 | -0.93166 | -0.56187 | 0.04974
42838.4242 | 339 | 22.9158 | 22.8767 | 22.8597 | 22.7796 | 22.4013 | 21.7275 | 22.7144 | 21.7757 | 22.3602 | 22.3683 | 22.3294 | 21.9798 | 21.1941 | 22.1595 | 21.6276 | 21.7974 | 21.919 | 21.0953 | 21.1896 | 21.4541 | 20.4884 | 20.792 | 22.4071 | 21.8698 | 21.756 | 24.8829 | 121.2313 | 106.1182 | 128.41 | 22.134 | 21.7976 | 23.6151 | 22.029 | 21.8518 | 24.4712 | 45.3282 | 135.338 |  | 71.6845 | 104.0724 | 103.7877 | 87.8253 |  | 17.1334 | 17.5395 | 16.8645 | 17.3759 | 17.5616 | 21.9349 | 74.8649 | 15.5151 | 17.0713 | 15.4609 | 17.9943 | 18.3932 | 47.7175 | 49.3734 | 46.5647 | 21.6444 |  |  | 0.89851 | -0.37725 | -25.0763 | 0.64853 | 0.12433 | -164.3659 | 20.9044 | 0.71721 | 0.017218 | 0.034518 | 0.32267 | 0.00035156 | 0.00034499 | 1.3717 | 21.7709 | 21.9622 | 22.1643 | 22.2171 | 22.0368 | 21.3249 | 20.1449 | 22.1731 | 22.3505 | 22.3896 | 22.3454 | 21.9606 | 21.1865 | 22.2718 | 60.0235 | 37.5669 | 38.6894 | 28.8977 | 26.6637 | 40.3453 | 28.2502 | 22.3273 | 22.0902 | 21.6575 | 22.0519 | 21.7671 | 21.3249 | 21.9299 | 21.6097 | 22.6161 | 42.7729 | 115.1454 | 91.8614 | 61.7611 | 1.0044 | 0.093039 | 51.3308 | 21.9286 | 22.2552 | 20.2989 | 21.5832 | 22.0385 | 21.9207 | 21.9138 | 26.8473 | 21.7861 | 21.5462 | 23.2951 | 119.0336 | 151.0683 | 92.1919 | 93.1448 | 61.0979 |  | 42.7114 | 91.462 | 46.0451 | 69.9006 | 48.3392 | 51.56 |  | 58.6017 |  |  | 22.1556 | 24.1851 | 45.3978 | [5 empty] | 21.8939 | 51.9501 | 21.6818 | 22.075 | 30.2812 | 21.2481 | 21.8909 | 25.2958 | 65.7394 | 155.8929 |  | 57.0221 | 111.7129 | 21.7001 | 53.6616 | 125.5688 | 38.1438 | 89.1769 | 23.6268 | 87.3371 | 23.5654 | 88.7085 | 18.5164 | 56.5272 | 107.9228 | 26.6938 | 54.87 | 121.3097 | 21.3891 | 50.2904 | 120.3069 | 21.6497 | 81.2508 | 27.9921 | 89.1709 | 23.9567 | 92.7103 | 0.71516 | 19.5357 | 1.1024 | 0.036879 | -27.1795 | 3.0953 | 137.28 | 52.58 | 1.3237 | -0.72979 | -5.95 | 0.95686 | 0.42211 | -15.3478 | 5.4734 | 0.05364 | -0.673 | 0.0067611 | -1.6388 | -0.692 | -0.59716 | 0.037368
42838.4242 | 340 | 22.9097 | 22.8751 | 22.8613 | 22.7848 | 22.3919 | 21.7242 | 22.7077 | 21.7712 | 22.3509 | 22.3613 | 22.3311 | 21.9849 | 21.1943 | 22.1642 | 21.625 | 21.7981 | 21.9143 | 21.0913 | 21.196 | 21.4492 | 20.4862 | 20.7911 | 22.4179 | 21.8739 | 21.7535 | 24.9051 | 121.6232 | 106.2456 | 128.7594 | 22.1377 | 21.8058 | 23.6419 | 22.0182 | 21.8603 | 24.4921 | 45.5236 | 137.0342 |  | 72.0059 | 104.441 | 103.9593 | 89.3047 |  | 17.1322 | 17.5413 | 16.8594 | 17.3779 | 17.5666 | 21.9045 | 75.3976 | 15.5084 | 17.0579 | 15.4651 | 17.9916 | 18.3981 | 47.7283 | 49.2822 | 46.5721 | 21.6531 |  |  | 0.86894 | -0.25962 | -25.3333 | 0.44417 | 0.25904 | -163.4703 | 20.9767 | 0.58382 | 0.089026 | 0.055289 | 0.29767 | 0.00035813 | 0.00034006 | 1.346 | 21.7673 | 21.9709 | 22.171 | 22.2159 | 22.0306 | 21.3294 | 20.1421 | 22.1764 | 22.3538 | 22.3867 | 22.3488 | 21.9629 | 21.1854 | 22.2735 | 62.2066 | 38.5134 | 39.378 | 28.6804 | 26.4752 | 40.4875 | 28.3038 | 22.333 | 22.0947 | 21.6675 | 22.0636 | 21.7777 | 21.335 | 21.9375 | 21.6175 | 22.6282 | 42.928 | 115.2501 | 92.0358 | 61.8307 | 0.98183 | 0.33421 | 51.5816 | 21.9231 | 22.2527 | 20.3047 | 21.5876 | 22.0353 | 21.9253 | 21.9157 | 26.8704 | 21.7833 | 21.5437 | 23.3117 | 119.6498 | 151.5946 | 92.3902 | 93.4071 | 61.0027 |  | 42.8286 | 91.2916 | 46.1716 | 70.0855 | 48.5291 | 51.7439 |  | 58.7788 |  |  | 22.1814 | 24.2303 | 45.3475 | [5 empty] | 21.8962 | 51.6518 | 21.683 | 22.0762 | 30.3411 | 21.2535 | 21.8969 | 25.3554 | 66.1061 | 156.0352 |  | 57.2251 | 112.1988 | 21.712 | 53.8005 | 126.2564 | 38.2696 | 89.4076 | 23.6654 | 87.678 | 23.59 | 89.0212 | 18.5461 | 56.8679 | 108.1956 | 26.74 | 55.0417 | 121.6089 | 21.3714 | 50.801 | 120.4547 | 21.7061 | 81.5551 | 28.0476 | 89.3448 | 23.9825 | 93.4123 | 0.66804 | 19.5296 | 1.1086 | 0.036988 | -27.1073 | 3.0953 | 138.83 | 51.6 | 1.3023 | -0.60542 | -5.9804 | 0.79187 | 0.60925 | -15.3051 | 5.4826 | 0.060379 | -0.66382 | 0.0083286 | -1.8646 | -0.76223 | -0.6314 | 0.040853
42838.4242 | 341 | 22.9136 | 22.8724 | 22.8574 | 22.7769 | 22.3922 | 21.7161 | 22.7059 | 21.7688 | 22.3559 | 22.3591 | 22.331 | 21.9841 | 21.1928 | 22.1618 | 21.6321 | 21.7952 | 21.9126 | 21.0966 | 21.2035 | 21.4567 | 20.486 | 20.7955 | 22.4313 | 21.8738 | 21.7574 | 24.9277 | 121.8433 | 106.3825 | 128.475 | 22.1373 | 21.8084 | 23.6489 | 22.0233 | 21.8644 | 24.5138 | 45.705 | 136.9115 |  | 72.2779 | 104.8367 | 104.1268 | 90.2194 |  | 17.1348 | 17.5629 | 16.8462 | 17.3879 | 17.5668 | 21.8562 | 75.9035 | 15.4907 | 17.0614 | 15.4968 | 18.0015 | 18.4036 | 47.7121 | 49.1982 | 46.5578 | 21.6539 |  |  | 0.57192 | -0.18931 | -25.5679 | 0.34757 | 0.13287 | -165.7301 | 21.3204 | 0.846 | 0.031229 | 0.11613 | 0.27302 | 0.00034334 | 0.00034334 | 1.3564 | 21.7722 | 21.9725 | 22.1691 | 22.2229 | 22.0355 | 21.3357 | 20.1411 | 22.179 | 22.3553 | 22.3913 | 22.3432 | 21.9607 | 21.1913 | 22.2696 | 62.8553 | 39.5907 | 42.5129 | 29.9507 | 26.9941 | 40.6215 | 28.3866 | 22.3316 | 22.0996 | 21.6613 | 22.0639 | 21.7726 | 21.332 | 21.9359 | 21.6078 | 22.6392 | 43.0621 | 115.2756 | 92.245 | 61.6591 | 0.67337 | 0.3926 | 51.5741 | 21.9286 | 22.2554 | 20.3035 | 21.5856 | 22.0394 | 21.9233 | 21.9175 | 26.9049 | 21.786 | 21.5485 | 23.3307 | 119.9989 | 151.8586 | 92.6306 | 93.6286 | 60.9455 |  | 42.9288 | 91.717 | 46.3057 | 70.0259 | 48.713 | 52.612 |  | 58.9487 |  |  | 22.2017 | 24.299 | 45.5266 | [5 empty] | 21.8906 | 51.38 | 21.6799 | 22.073 | 30.3731 | 21.2501 | 21.8894 | 25.4088 | 66.4821 | 156.747 |  | 57.634 | 112.4714 | 21.7223 | 53.9575 | 126.7788 | 38.3592 | 89.643 | 23.6886 | 87.9176 | 23.6154 | 89.2859 | 18.5655 | 57.0583 | 108.5621 | 26.7793 | 55.1858 | 121.764 | 21.3623 | 51.1959 | 120.6623 | 21.7585 | 81.9013 | 28.1124 | 89.4739 | 24.005 | 93.9037 | 0.62463 | 19.5232 | 1.1161 | 0.037721 | -27.1167 | 3.0953 | 127.51 | 52.2 | 1.0562 | -0.517 | -6.0082 | 0.70052 | 0.43631 | -15.4093 | 5.5269 | 0.065467 | -0.67092 | 0.016484 | -1.9208 | -1.1008 | -0.65043 | 0.050306
42838.4242 | 342 | 22.9197 | 22.8822 | 22.8588 | 22.7801 | 22.3982 | 21.7269 | 22.7165 | 21.7772 | 22.3624 | 22.3703 | 22.3382 | 21.9895 | 21.1974 | 22.1727 | 21.6332 | 21.7893 | 21.9145 | 21.0951 | 21.2035 | 21.4592 | 20.4877 | 20.7891 | 22.4382 | 21.8731 | 21.7606 | 24.9431 | 121.9506 | 106.5364 | 128.3744 | 22.133 | 21.8094 | 23.6683 | 22.0263 | 21.86 | 24.5359 | 45.8737 | 136.6288 |  | 72.5489 | 105.2314 | 104.269 | 88.7075 |  | 17.1404 | 17.5628 | 16.8568 | 17.3867 | 17.5609 | 21.7938 | 76.4649 | 15.4695 | 17.0587 | 15.5559 | 17.9991 | 18.3906 | 47.6995 | 49.1166 | 46.5378 | 21.6491 |  |  | 0.56009 | -0.30562 | -25.7979 | 0.51185 | 0.15192 | -168.5997 | 20.7599 | 0.72772 | 0.1081 | 0.055289 | 0.2416 | 0.00037291 | 0.00039263 | 1.4095 | 21.7785 | 21.9755 | 22.1691 | 22.226 | 22.0316 | 21.3381 | 20.1418 | 22.181 | 22.3665 | 22.39 | 22.3417 | 21.9588 | 21.194 | 22.2747 | 63.1457 | 42.0668 | 43.9162 | 30.7628 | 27.1539 | 40.766 | 28.4835 | 22.3443 | 22.1068 | 21.6576 | 22.0734 | 21.7803 | 21.3384 | 21.9408 | 21.6241 | 22.6558 | 43.2179 | 115.3316 | 92.5749 | 61.8368 | 0.56524 | 0.45708 | 51.9112 | 21.9316 | 22.2512 | 20.3184 | 21.5824 | 22.0346 | 21.9224 | 21.924 | 26.9412 | 21.7953 | 21.5498 | 23.343 | 120.3103 | 152.0997 | 92.9971 | 94.0269 | 60.6623 |  | 43.0764 | 92.3335 | 46.5058 | 71.1845 | 48.9939 | 52.3743 |  | 59.1833 |  |  | 22.2176 | 24.3589 | 45.7829 | [5 empty] | 21.8935 | 52.8818 | 21.6808 | 22.0734 | 30.4234 | 21.2525 | 21.8906 | 25.4571 | 66.8422 | 157.2184 |  | 58.1536 | 112.8902 | 21.7358 | 54.1896 | 127.2169 | 38.424 | 89.9365 | 23.7134 | 88.2474 | 23.6419 | 89.5604 | 18.5786 | 57.1457 | 108.9844 | 26.825 | 55.4022 | 121.8264 | 21.3512 | 51.378 | 120.8941 | 21.8044 | 82.1625 | 28.1591 | 89.6492 | 24.0306 | 94.1443 | 0.88044 | 19.5166 | 1.1235 | 0.039834 | -27.2015 | 3.0952 | 123.85 | 52.14 | 1.0451 | -0.65689 | -6.0352 | 0.8501 | 0.4665 | -15.5405 | 5.4532 | 0.078492 | -0.681 | -0.0057682 | -1.936 | -1.2454 | -0.60251 | 0.050815
42838.4242 | 343 | 22.9177 | 22.8761 | 22.856 | 22.776 | 22.3898 | 21.7204 | 22.7226 | 21.7773 | 22.3608 | 22.3646 | 22.3333 | 21.9848 | 21.1932 | 22.1627 | 21.6311 | 21.7989 | 21.9134 | 21.0983 | 21.2011 | 21.4565 | 20.4836 | 20.7902 | 22.4552 | 21.8723 | 21.7637 | 24.9662 | 122.1283 | 106.6384 | 128.6233 | 22.1414 | 21.8098 | 23.6879 | 22.0329 | 21.8643 | 24.5493 | 46.0188 | 137.8221 |  | 72.8584 | 105.5796 | 104.4266 | 87.152 |  | 17.1455 | 17.58 | 16.8751 | 17.3955 | 17.5634 | 21.8362 | 77.281 | 15.4871 | 17.0657 | 15.6206 | 18.0034 | 18.395 | 47.6938 | 49.0349 | 46.5233 | 21.6526 |  |  | 0.74671 | -0.2616 | -25.8866 | 0.51251 | 0.49626 | -166.0666 | 20.4596 | 0.97414 | 0.1223 | 0.2183 | 0.2199 | 0.0003647 | 0.00035977 | 1.4044 | 21.775 | 21.9751 | 22.1662 | 22.2225 | 22.0362 | 21.3286 | 20.1522 | 22.1785 | 22.3621 | 22.3947 | 22.3449 | 21.9583 | 21.1907 | 22.2685 | 63.121 | 42.1387 | 44.8417 | 31.3814 | 26.8804 | 40.8926 | 28.5718 | 22.3321 | 22.0976 | 21.6605 | 22.0599 | 21.7777 | 21.3405 | 21.9416 | 21.6238 | 22.668 | 43.3612 | 115.2337 | 92.8315 | 62.4478 | 0.41503 | -0.053035 | 51.893 | 21.9147 | 22.2465 | 20.301 | 21.5758 | 22.0319 | 21.9106 | 21.9162 | 26.9678 | 21.7837 | 21.5321 | 23.3499 | 120.5799 | 152.6367 | 93.3806 | 94.4523 | 60.3969 |  | 43.1873 | 91.6823 | 46.6348 | 71.1075 | 49.1967 | 52.7611 |  | 59.3936 |  |  | 22.2299 | 24.3945 | 45.6767 | [5 empty] | 21.8899 | 54.186 | 21.6824 | 22.082 | 30.4537 | 21.2483 | 21.8924 | 25.5131 | 67.2205 | 157.5823 |  | 58.6376 | 113.337 | 21.7506 | 54.4349 | 127.8204 | 38.5305 | 90.2038 | 23.751 | 88.6812 | 23.6877 | 90.3427 | 18.6029 | 57.2385 | 109.3632 | 26.8781 | 55.6999 | 121.7483 | 21.3425 | 51.5772 | 121.2261 | 21.8416 | 82.4029 | 28.1795 | 89.9293 | 24.061 | 94.5124 | 0.81495 | 19.5088 | 1.1301 | 0.040305 | -27.1169 | 3.0953 | 127.64 | 51.79 | 1.2071 | -0.60775 | -6.0457 | 0.85067 | 0.84318 | -15.4244 | 5.414 | 0.089739 | -0.65837 | 0.0035406 | -1.9183 | -1.3379 | -0.5542 | 0.038853
42838.4243 | 344 | 22.9154 | 22.875 | 22.8579 | 22.778 | 22.3873 | 21.7143 | 22.7178 | 21.7753 | 22.3524 | 22.3668 | 22.3331 | 21.9873 | 21.1935 | 22.162 | 21.6288 | 21.8001 | 21.9195 | 21.0993 | 21.1968 | 21.4659 | 20.4909 | 20.7993 | 22.4648 | 21.8728 | 21.7708 | 24.9842 | 122.4794 | 106.772 | 129.0624 | 22.1355 | 21.8129 | 23.7015 | 22.0283 | 21.86 | 24.5663 | 46.1535 | 138.5388 |  | 73.1786 | 105.8371 | 104.6069 | 86.7983 |  | 17.1372 | 17.5748 | 16.8761 | 17.4022 | 17.5745 | 22.0627 | 78.13 | 15.5185 | 17.0568 | 15.6463 | 17.9998 | 18.4002 | 47.6615 | 48.9507 | 46.5145 | 21.6504 |  |  | 0.62975 | -0.1604 | -25.7236 | 0.63145 | 0.28138 | -164.7011 | 21.0759 | 0.89726 | 0.25755 | 0.15075 | 0.28725 | 0.00037784 | 0.00034334 | 1.3426 | 21.7833 | 21.9714 | 22.1674 | 22.2227 | 22.0419 | 21.3313 | 20.1475 | 22.1725 | 22.3597 | 22.3948 | 22.3472 | 21.9599 | 21.1988 | 22.2659 | 62.5572 | 40.2932 | 42.5577 | 31.7229 | 26.715 | 40.992 | 28.6305 | 22.329 | 22.094 | 21.6587 | 22.0554 | 21.7808 | 21.3357 | 21.935 | 21.6182 | 22.6749 | 43.4916 | 115.3783 | 93.1349 | 62.9267 | 0.54833 | -0.13007 | 51.7621 | 21.915 | 22.24 | 20.3071 | 21.5733 | 22.0291 | 21.917 | 21.9155 | 26.9995 | 21.7829 | 21.5451 | 23.3684 | 120.8999 | 153.2668 | 93.7634 | 94.8818 | 60.4632 |  | 43.3035 | 91.6784 | 46.7699 | 71.0576 | 49.3835 | 53.4783 |  | 59.5807 |  |  | 22.2347 | 24.4258 | 45.9765 | [5 empty] | 21.8867 | 54.4438 | 21.6799 | 22.0748 | 30.4605 | 21.2478 | 21.8942 | 25.5503 | 67.5365 | 157.6892 |  | 59.0612 | 113.609 | 21.751 | 54.5727 | 128.2183 | 38.6379 | 90.391 | 23.8062 | 88.9137 | 23.7224 | 90.7187 | 18.6068 | 57.4038 | 109.6512 | 26.9192 | 55.9417 | 121.9912 | 21.3229 | 51.7662 | 121.3859 | 21.8738 | 82.6772 | 28.2151 | 90.2405 | 24.079 | 94.9362 | 1.0364 | 19.5029 | 1.1366 | 0.040095 | -27.102 | 3.0953 | 124.61 | 52.17 | 1.1091 | -0.4759 | -6.0266 | 0.94423 | 0.63515 | -15.3668 | 5.497 | 0.091962 | -0.65351 | 0.011539 | -1.8439 | -1.0772 | -0.53964 | 0.030109
42838.4243 | 345 | 22.9156 | 22.869 | 22.8617 | 22.7744 | 22.3916 | 21.7189 | 22.7108 | 21.7694 | 22.3548 | 22.3659 | 22.3341 | 21.9837 | 21.197 | 22.1591 | 21.6281 | 21.7921 | 21.9189 | 21.1031 | 21.1938 | 21.4621 | 20.4909 | 20.7985 | 22.4798 | 21.8696 | 21.764 | 25.0108 | 122.6249 | 106.9619 | 128.605 | 22.1313 | 21.8097 | 23.7097 | 22.0249 | 21.8598 | 24.5837 | 46.3009 | 138.4854 |  | 73.4449 | 106.1467 | 104.7401 | 88.3453 |  | 17.1337 | 17.5757 | 16.8693 | 17.4075 | 17.6025 | 22.2575 | 78.968 | 15.5451 | 17.0562 | 15.6411 | 18.0062 | 18.4124 | 47.6325 | 48.8739 | 46.4939 | 21.6536 |  |  | 0.57126 | -0.24386 | -25.9496 | 0.61633 | 0.33723 | -165.391 | 20.8092 | 0.76386 | 0.11082 | 0.10711 | 0.26555 | 0.00036141 | 0.00037291 | 1.3185 | 21.7814 | 21.9768 | 22.1782 | 22.2282 | 22.0475 | 21.3348 | 20.1507 | 22.1857 | 22.367 | 22.4037 | 22.3529 | 21.9654 | 21.1928 | 22.2752 | 62.3814 | 39.7815 | 41.5144 | 31.3903 | 26.8314 | 41.0857 | 28.6773 | 22.3277 | 22.0923 | 21.6514 | 22.0517 | 21.7713 | 21.3253 | 21.9321 | 21.6115 | 22.6821 | 43.6175 | 115.6541 | 93.3883 | 63.5609 | 0.80037 | 0.37377 | 52.2727 | 21.9243 | 22.2441 | 20.3047 | 21.5765 | 22.0335 | 21.9204 | 21.9244 | 27.0354 | 21.7853 | 21.544 | 23.3796 | 121.3073 | 153.925 | 94.1064 | 95.2219 | 61.9549 |  | 43.4451 | 91.7066 | 46.9455 | 70.4571 | 49.5898 | 53.6734 |  | 59.7592 |  |  | 22.2481 | 24.4742 | 46.1745 | [5 empty] | 21.8969 | 53.8612 | 21.6793 | 22.082 | 30.4932 | 21.2478 | 21.8942 | 25.607 | 67.903 | 157.6294 |  | 59.421 | 113.8473 | 21.7493 | 54.7908 | 128.4601 | 38.7523 | 90.5809 | 23.8403 | 89.3467 | 23.7408 | 90.8887 | 18.6185 | 57.7892 | 110.0001 | 26.9533 | 56.1479 | 122.3024 | 21.3049 | 51.8836 | 121.6669 | 21.8851 | 82.9558 | 28.2779 | 90.4509 | 24.1067 | 95.3303 | 1.034 | 19.4963 | 1.1427 | 0.040059 | -27.1243 | 3.0953 | 136.5 | 51.58 | 1.0558 | -0.58678 | -6.0531 | 0.93286 | 0.69557 | -15.404 | 5.4639 | 0.055479 | -0.64811 | 0.03552 | -1.8133 | -0.95579 | -0.57743 | 0.016896
42838.4243 | 346 | 22.9244 | 22.8809 | 22.8676 | 22.7889 | 22.3992 | 21.7266 | 22.7144 | 21.7779 | 22.3648 | 22.3735 | 22.3438 | 21.9935 | 21.2002 | 22.1706 | 21.628 | 21.7944 | 21.9167 | 21.0921 | 21.1918 | 21.4582 | 20.4817 | 20.7913 | 22.4832 | 21.8721 | 21.7635 | 25.0287 | 122.6637 | 107.1588 | 128.1162 | 22.1356 | 21.8051 | 23.7251 | 22.0321 | 21.8603 | 24.6016 | 46.4755 | 137.7703 |  | 73.7074 | 106.4907 | 104.8981 | 90.1561 |  | 17.1315 | 17.5699 | 16.8545 | 17.3971 | 17.5991 | 22.2056 | 79.7039 | 15.5649 | 17.0575 | 15.6045 | 18.0073 | 18.4098 | 47.5872 | 48.7903 | 46.4644 | 21.6556 |  |  | 0.84134 | -0.37462 | -25.9634 | 0.58939 | 0.43251 | -163.2705 | 20.4458 | 0.73692 | 0.18321 | 0.021511 | 0.22146 | 0.00035977 | 0.00037456 | 1.3343 | 21.7781 | 21.9702 | 22.1758 | 22.2192 | 22.046 | 21.3377 | 20.1499 | 22.1927 | 22.3617 | 22.398 | 22.3483 | 21.9649 | 21.192 | 22.2704 | 63.4795 | 42.2685 | 42.3279 | 31.9047 | 26.6462 | 41.2301 | 28.7624 | 22.3316 | 22.0951 | 21.6544 | 22.0608 | 21.7741 | 21.3314 | 21.942 | 21.622 | 22.6998 | 43.7522 | 115.7993 | 93.6008 | 64.0858 | 0.74788 | 0.10369 | 52.3394 | 21.9223 | 22.246 | 20.3055 | 21.5823 | 22.034 | 21.9233 | 21.9185 | 27.069 | 21.798 | 21.5479 | 23.3951 | 121.892 | 154.8204 | 94.505 | 95.5308 | 62.6074 |  | 43.5842 | 91.9621 | 47.1145 | 70.4808 | 49.7594 | 53.238 |  | 59.9137 |  |  | 22.2728 | 24.4955 | 46.2609 | [5 empty] | 21.8985 | 54.5809 | 21.6892 | 22.0806 | 30.4788 | 21.25 | 21.8965 | 25.6642 | 68.3008 | 157.7925 |  | 59.881 | 114.057 | 21.764 | 55.1044 | 128.6495 | 38.8717 | 91.023 | 23.8824 | 89.7215 | 23.7653 | 91.1104 | 18.6192 | 58.2005 | 110.4178 | 26.9923 | 56.4074 | 122.828 | 21.3107 | 52.0704 | 122.0306 | 21.9044 | 83.3272 | 28.3344 | 90.5667 | 24.1279 | 95.9547 | 1.0554 | 19.491 | 1.1489 | 0.040436 | -27.1051 | 3.0953 | 154.86 | 53.01 | 1.2805 | -0.72728 | -6.0546 | 0.91223 | 0.78766 | -15.3036 | 5.4155 | 0.042219 | -0.64925 | 0.040867 | -1.9183 | -1.0362 | -0.62159 | 0.0070299
42838.4243 | 347 | 22.9204 | 22.8788 | 22.8609 | 22.781 | 22.3919 | 21.7231 | 22.7116 | 21.781 | 22.3538 | 22.3619 | 22.3371 | 21.989 | 21.1951 | 22.1671 | 21.6293 | 21.7843 | 21.9141 | 21.0902 | 21.1954 | 21.4637 | 20.4814 | 20.7903 | 22.4982 | 21.8718 | 21.7701 | 25.0486 | 122.8068 | 107.284 | 128.6749 | 22.1237 | 21.8018 | 23.7398 | 22.0186 | 21.8644 | 24.6223 | 46.6631 | 136.6624 |  | 73.9671 | 106.7853 | 105.0776 | 92.5923 |  | 17.1302 | 17.5777 | 16.8565 | 17.4063 | 17.6053 | 22.1589 | 79.7252 | 15.6165 | 17.0681 | 15.5728 | 18.02 | 18.4074 | 47.5393 | 48.7192 | 46.4424 | 21.648 |  |  | 0.72569 | -0.43376 | -25.7788 | 0.25295 | 0.43646 | -164.0394 | 20.637 | 0.50365 | 0.17484 | 0.12725 | 0.16157 | 0.00034827 | 0.00034334 | 1.3429 | 21.7779 | 21.9675 | 22.1734 | 22.2219 | 22.0445 | 21.3344 | 20.1507 | 22.1887 | 22.3601 | 22.3933 | 22.3493 | 21.9696 | 21.1937 | 22.2732 | 64.6889 | 44.7442 | 43.2315 | 32.5468 | 27.3266 | 41.381 | 28.8437 | 22.3322 | 22.0978 | 21.6577 | 22.0626 | 21.7789 | 21.3351 | 21.9415 | 21.6214 | 22.7147 | 43.8983 | 115.8597 | 93.7857 | 64.2052 | 0.75771 | 0.092278 | 52.3893 | 21.9144 | 22.2461 | 20.2994 | 21.5797 | 22.0235 | 21.9175 | 21.9265 | 27.0967 | 21.7881 | 21.5468 | 23.4189 | 122.237 | 155.154 | 94.8317 | 95.7616 | 63.4844 |  | 43.7131 | 92.7209 | 47.2766 | 70.4674 | 49.9276 | 53.4095 |  | 60.0868 |  |  | 22.2635 | 24.4886 | 46.5784 | [5 empty] | 21.8895 | 54.7855 | 21.6811 | 22.0629 | 30.4864 | 21.2436 | 21.887 | 25.7114 | 68.6724 | 158.1086 |  | 60.4124 | 114.3287 | 21.7602 | 55.2676 | 129.067 | 38.9346 | 91.2557 | 23.907 | 90.1195 | 23.7646 | 91.3466 | 18.6241 | 58.4629 | 110.9299 | 27.0354 | 56.7287 | 123.0036 | 21.2948 | 52.35 | 122.4058 | 21.9191 | 83.7481 | 28.395 | 90.7778 | 24.1449 | 96.311 | 0.95501 | 19.4831 | 1.1548 | 0.039942 | -27.0672 | 3.0952 | 144.63 | 52.18 | 1.19 | -0.78259 | -6.0331 | 0.59762 | 0.79118 | -15.3384 | 5.4404 | 0.022365 | -0.66462 | 0.047194 | -2.0348 | -1.127 | -0.68266 | 0.0088261
42838.4243 | 348 | 22.9114 | 22.873 | 22.8538 | 22.7717 | 22.3836 | 21.7183 | 22.7049 | 21.7725 | 22.3598 | 22.3633 | 22.3288 | 21.9781 | 21.1896 | 22.1613 | 21.6243 | 21.7871 | 21.91 | 21.0916 | 21.1916 | 21.4632 | 20.4781 | 20.798 | 22.5087 | 21.8661 | 21.7662 | 25.0628 | 123.0146 | 107.4751 | 128.3538 | 22.1309 | 21.814 | 23.7569 | 22.0267 | 21.8693 | 24.6494 | 46.8256 | 136.0061 |  | 74.2301 | 106.937 | 105.2811 | 94.2772 |  | 17.1296 | 17.5801 | 16.8534 | 17.4084 | 17.6201 | 22.1579 | 79.9924 | 15.6384 | 17.0678 | 15.566 | 18.0252 | 18.4143 | 47.4922 | 48.6491 | 46.4055 | 21.6524 |  |  | 0.7546 | -0.39236 | -26.1507 | 0.31997 | 0.29518 | -165.0559 | 20.8499 | 0.45699 | 0.02617 | 0.21767 | 0.17806 | 0.00035977 | 0.00032527 | 1.3406 | 21.7741 | 21.9643 | 22.1654 | 22.2278 | 22.0354 | 21.3253 | 20.1434 | 22.1787 | 22.3595 | 22.3909 | 22.3488 | 21.9716 | 21.1896 | 22.2746 | 64.1419 | 44.0641 | 44.3253 | 32.5222 | 28.1288 | 41.4868 | 28.9318 | 22.3315 | 22.1033 | 21.6574 | 22.0599 | 21.7754 | 21.3386 | 21.9378 | 21.6169 | 22.73 | 44.0373 | 115.9162 | 93.9356 | 64.0363 | 0.28607 | 0.011443 | 52.7096 | 21.9244 | 22.2502 | 20.3104 | 21.5932 | 22.0388 | 21.9181 | 21.9348 | 27.1447 | 21.7961 | 21.5542 | 23.4336 | 122.7022 | 155.5677 | 95.0311 | 95.9889 | 64.04 |  | 43.841 | 92.7079 | 47.4604 | 70.2086 | 50.0945 | 53.4821 |  | 60.2774 |  |  | 22.2858 | 24.507 | 47.0244 | [5 empty] | 21.882 | 54.3219 | 21.6731 | 22.0739 | 30.5232 | 21.249 | 21.8858 | 25.7698 | 69.0229 | 157.8104 |  | 60.7598 | 114.678 | 21.7805 | 55.3638 | 129.6036 | 39.0448 | 91.464 | 23.9413 | 90.5171 | 23.7785 | 91.5512 | 18.6127 | 58.6439 | 111.2892 | 27.0628 | 57.0068 | 123.1294 | 21.287 | 52.5615 | 122.9377 | 21.9266 | 84.0554 | 28.4451 | 91.0308 | 24.1777 | 96.457 | 0.9398 | 19.4765 | 1.1604 | 0.039238 | -27.0636 | 3.0953 | 144.3 | 51.63 | 1.213 | -0.74432 | -6.0765 | 0.67215 | 0.65065 | -15.3858 | 5.4684 | 0.011413 | -0.65779 | 0.0603 | -1.9616 | -1.2382 | -0.72374 | 0.018386
42838.4243 | 349 | 22.9106 | 22.8733 | 22.852 | 22.7756 | 22.3862 | 21.7141 | 22.7107 | 21.772 | 22.36 | 22.3555 | 22.3238 | 21.979 | 21.1892 | 22.1606 | 21.63 | 21.792 | 21.9185 | 21.0932 | 21.1992 | 21.4596 | 20.4792 | 20.7982 | 22.5215 | 21.8694 | 21.7625 | 25.0875 | 123.3595 | 107.727 | 129.8237 | 22.1394 | 21.8195 | 23.7747 | 22.0291 | 21.8741 | 24.671 | 47.019 | 136.5906 |  | 74.4584 | 107.0898 | 105.6141 | 95.9037 |  | 17.1256 | 17.5752 | 16.8491 | 17.4037 | 17.6343 | 22.253 | 80.5533 | 15.6835 | 17.0648 | 15.6212 | 18.0224 | 18.4181 | 47.4398 | 48.589 | 46.3757 | 21.6501 |  |  | 0.44378 | -0.41931 | -26.0108 | 0.071582 | 0.56591 | -162.8756 | 20.7651 | 0.52796 | 0.070928 | 0.077318 | 0.11626 | 0.00034006 | 0.0003417 | 1.3256 | 21.7728 | 21.9723 | 22.1655 | 22.2195 | 22.0357 | 21.3276 | 20.14 | 22.1757 | 22.3565 | 22.3921 | 22.3499 | 21.9687 | 21.1929 | 22.2658 | 62.9454 | 41.0366 | 43.5501 | 32.4922 | 28.3406 | 41.5551 | 29.015 | 22.3304 | 22.1003 | 21.6543 | 22.0584 | 21.7783 | 21.3405 | 21.9409 | 21.617 | 22.7386 | 44.1626 | 116.0122 | 94.1158 | 64.2152 | 0.51157 | -0.20729 | 53.0383 | 21.9225 | 22.244 | 20.3095 | 21.5783 | 22.0373 | 21.9231 | 21.94 | 27.1766 | 21.7856 | 21.5495 | 23.4455 | 123.0081 | 156.0219 | 95.1751 | 96.1953 | 64.1256 |  | 43.9969 | 92.3423 | 47.6617 | 70.9783 | 50.3087 | 53.5096 |  | 60.4646 |  |  | 22.3137 | 24.5294 | 47.3965 | [5 empty] | 21.8886 | 53.9384 | 21.6781 | 22.074 | 30.5372 | 21.2463 | 21.8906 | 25.8216 | 69.3935 | 158.0308 |  | 60.7633 | 114.8567 | 21.787 | 55.5657 | 130.0781 | 39.1534 | 91.6677 | 23.9809 | 90.8622 | 23.8085 | 91.767 | 18.6102 | 58.8963 | 111.4641 | 27.1014 | 57.2368 | 123.183 | 21.3012 | 52.7311 | 123.3236 | 21.9358 | 84.3051 | 28.5106 | 91.32 | 24.1928 | 96.5076 | 0.88415 | 19.4732 | 1.1654 | 0.040276 | -27.1245 | 3.0953 | 156.4 | 52.57 | 0.93194 | -0.76944 | -6.0602 | 0.31791 | 0.90105 | -15.2863 | 5.4581 | 0.014489 | -0.64053 | 0.046511 | -1.8205 | -1.1423 | -0.76211 | 0.017803
42838.4243 | 350 | 22.91 | 22.8716 | 22.8585 | 22.7748 | 22.39 | 21.7175 | 22.7149 | 21.7728 | 22.3659 | 22.3583 | 22.3331 | 21.9791 | 21.1886 | 22.1592 | 21.6303 | 21.7984 | 21.9163 | 21.0949 | 21.2003 | 21.4666 | 20.4898 | 20.8024 | 22.5326 | 21.8744 | 21.7673 | 25.1133 | 123.6728 | 107.9666 | 130.2853 | 22.1304 | 21.8127 | 23.7795 | 22.0197 | 21.8647 | 24.6845 | 47.2181 | 136.9873 |  | 74.7203 | 107.3252 | 105.9278 | 97.1562 |  | 17.1259 | 17.571 | 16.8521 | 17.4082 | 17.6376 | 22.3516 | 81.0321 | 15.668 | 17.0615 | 15.636 | 18.0209 | 18.4155 | 47.3685 | 48.5324 | 46.3372 | 21.6472 |  |  | 0.63763 | -0.40157 | -25.7144 | 0.318 | 0.36483 | -163.8225 | 20.8492 | 0.77109 | 0.15441 | 0.25229 | 0.24837 | 0.00037456 | 0.00033842 | 1.3071 | 21.7779 | 21.9685 | 22.1675 | 22.2312 | 22.035 | 21.338 | 20.1466 | 22.172 | 22.3651 | 22.3966 | 22.3472 | 21.9611 | 21.1904 | 22.2716 | 61.6622 | 38.4366 | 42.3027 | 32.702 | 28.6417 | 41.6069 | 29.0516 | 22.3236 | 22.0924 | 21.6527 | 22.047 | 21.7687 | 21.3341 | 21.9373 | 21.6131 | 22.7489 | 44.2826 | 116.0685 | 94.3302 | 64.2602 | 0.57762 | 0.20507 | 53.0259 | 21.917 | 22.2343 | 20.3089 | 21.5728 | 22.0297 | 21.9135 | 21.9379 | 27.1973 | 21.7776 | 21.5419 | 23.4602 | 123.2183 | 156.121 | 95.2884 | 96.352 | 65.038 |  | 44.1353 | 92.8751 | 47.8675 | 72.4553 | 50.5093 | 53.4557 |  | 60.6219 |  |  | 22.3354 | 24.5512 | 47.6256 | [5 empty] | 21.8921 | 54.0371 | 21.6852 | 22.0736 | 30.5637 | 21.252 | 21.8923 | 25.8677 | 69.7467 | 157.906 |  | 60.7548 | 114.9968 | 21.7957 | 55.8089 | 130.4516 | 39.2784 | 91.8697 | 24.0051 | 91.2127 | 23.854 | 92.0834 | 18.6055 | 59.1944 | 111.5587 | 27.1252 | 57.4557 | 123.404 | 21.3043 | 52.9199 | 123.6365 | 21.9481 | 84.5494 | 28.5502 | 91.5233 | 24.2066 | 96.7893 | 0.95204 | 19.4692 | 1.1713 | 0.040371 | -27.1933 | 3.0953 | 167.33 | 51.24 | 1.1177 | -0.75298 | -6.0255 | 0.67007 | 0.72359 | -15.3332 | 5.4701 | -0.0060098 | -0.64807 | 0.012596 | -1.6718 | -0.99944 | -0.78989 | 0.020757
42838.4243 | 351 | 22.9168 | 22.8778 | 22.8578 | 22.7762 | 22.3959 | 21.7203 | 22.7109 | 21.769 | 22.3609 | 22.3642 | 22.3366 | 21.9849 | 21.192 | 22.1608 | 21.633 | 21.7996 | 21.9117 | 21.0931 | 21.201 | 21.4717 | 20.4885 | 20.8059 | 22.547 | 21.8734 | 21.7722 | 25.1326 | 123.9278 | 108.2249 | 130.5724 | 22.1215 | 21.8099 | 23.792 | 22.0198 | 21.8654 | 24.7042 | 47.4356 | 137.6457 |  | 75.0326 | 107.6605 | 106.1544 | 97.9162 |  | 17.1255 | 17.5836 | 16.86 | 17.4154 | 17.6908 | 22.4234 | 81.2192 | 15.6381 | 17.0677 | 15.7201 | 18.0312 | 18.4223 | 47.3035 | 48.4848 | 46.2919 | 21.6517 |  |  | 0.57455 | -0.20377 | -25.7216 | 0.21417 | 0.4726 | -166.0587 | 21.4945 | 0.72378 | -0.12776 | 0.010391 | 0.36971 | 0.0003762 | 0.00033842 | 1.2925 | 21.7778 | 21.9657 | 22.1677 | 22.2272 | 22.0398 | 21.3342 | 20.1425 | 22.1826 | 22.3598 | 22.4035 | 22.3434 | 21.9587 | 21.1862 | 22.2721 | 61.2773 | 39.5839 | 42.8341 | 32.9999 | 29.3063 | 41.6886 | 29.121 | 22.3267 | 22.1011 | 21.6589 | 22.0572 | 21.7774 | 21.3432 | 21.9434 | 21.624 | 22.7667 | 44.4213 | 116.268 | 94.5254 | 63.7059 | 0.84048 | 0.19632 | 52.8809 | 21.919 | 22.2371 | 20.314 | 21.586 | 22.0368 | 21.9229 | 21.9467 | 27.2433 | 21.7831 | 21.5507 | 23.4791 | 123.4264 | 156.376 | 95.5251 | 96.6595 | 66.1788 |  | 44.2629 | 92.9561 | 48.0358 | 73.3303 | 50.703 | 53.6124 |  | 60.7945 |  |  | 22.3585 | 24.5728 | 47.8416 | [5 empty] | 21.8944 | 54.6831 | 21.6831 | 22.0774 | 30.6103 | 21.2547 | 21.9031 | 25.922 | 70.1147 | 158.1466 |  | 60.9646 | 115.3402 | 21.8034 | 55.9325 | 130.8049 | 39.3807 | 92.0388 | 24.0456 | 91.57 | 23.8889 | 92.3554 | 18.6205 | 59.3114 | 111.6795 | 27.1491 | 57.6848 | 123.5861 | 21.3051 | 53.123 | 124.067 | 21.9654 | 84.8159 | 28.589 | 91.7559 | 24.2322 | 97.0505 | 1.1552 | 19.4629 | 1.1776 | 0.040327 | -27.1598 | 3.0953 | 158.43 | 52.68 | 1.0614 | -0.5364 | -6.0265 | 0.54992 | 0.82365 | -15.4394 | 5.5547 | -0.03323 | -0.64438 | -0.0048355 | -1.6194 | -1.0503 | -0.80333 | 0.041017
42838.4244 | 352 | 22.9149 | 22.8769 | 22.8633 | 22.778 | 22.3903 | 21.7172 | 22.7148 | 21.7682 | 22.3555 | 22.3581 | 22.3331 | 21.9854 | 21.1916 | 22.164 | 21.6296 | 21.7913 | 21.9085 | 21.0922 | 21.198 | 21.4695 | 20.4833 | 20.8032 | 22.5587 | 21.8692 | 21.7758 | 25.1518 | 124.0476 | 108.4758 | 130.3266 | 22.1299 | 21.8159 | 23.8142 | 22.0194 | 21.8816 | 24.7251 | 47.6638 | 137.9626 |  | 75.3289 | 107.9735 | 106.373 | 98.0226 |  | 17.1356 | 17.5955 | 16.8769 | 17.4314 | 17.7343 | 22.5882 | 81.1648 | 15.644 | 17.0677 | 15.7452 | 18.0361 | 18.4227 | 47.2536 | 48.4394 | 46.2566 | 21.6538 |  |  | 0.64355 | -0.38908 | -26.1028 | 0.12875 | 0.24786 | -164.9481 | 20.7579 | 0.83483 | -0.20268 | 0.27915 | 0.20323 | 0.00033677 | 0.00033842 | 1.289 | 21.78 | 21.9703 | 22.1714 | 22.2307 | 22.0382 | 21.3387 | 20.1491 | 22.1861 | 22.3605 | 22.4047 | 22.3532 | 21.9626 | 21.1927 | 22.2717 | 62.0915 | 41.3592 | 43.3624 | 33.01 | 29.3229 | 41.8105 | 29.1991 | 22.3327 | 22.097 | 21.6603 | 22.061 | 21.7813 | 21.3408 | 21.9358 | 21.6212 | 22.7785 | 44.5568 | 116.5419 | 94.7433 | 63.6316 | 1.1949 | 0.12423 | 52.6281 | 21.9207 | 22.248 | 20.3296 | 21.5971 | 22.0378 | 21.9339 | 21.958 | 27.2802 | 21.7942 | 21.5681 | 23.501 | 123.8003 | 156.4921 | 95.9287 | 97.0868 | 66.9769 |  | 44.4471 | 92.6113 | 48.2045 | 74.4211 | 50.924 | 54.3237 |  | 61.0143 |  |  | 22.3721 | 24.5813 | 48.1916 | [5 empty] | 21.897 | 54.5827 | 21.6756 | 22.0739 | 30.6393 | 21.2511 | 21.8983 | 25.975 | 70.4678 | 158.3889 |  | 61.5309 | 115.8648 | 21.8109 | 56.0249 | 130.9799 | 39.4563 | 92.2526 | 24.0881 | 91.8903 | 23.9201 | 92.5974 | 18.6222 | 59.545 | 111.8562 | 27.1766 | 57.9476 | 123.6445 | 21.3011 | 53.2327 | 124.4055 | 21.9739 | 85.0539 | 28.6428 | 91.9851 | 24.2544 | 97.2631 | 1.0468 | 19.4592 | 1.1835 | 0.041634 | -27.1539 | 3.0953 | 159.3 | 51.4 | 1.123 | -0.74121 | -6.0711 | 0.42638 | 0.59666 | -15.392 | 5.4602 | -0.048943 | -0.62885 | -0.027293 | -1.6955 | -1.0999 | -0.79824 | 0.047829
42838.4244 | 353 | 22.9157 | 22.8693 | 22.8559 | 22.7778 | 22.3825 | 21.7183 | 22.7071 | 21.7751 | 22.3567 | 22.358 | 22.3352 | 21.9775 | 21.1924 | 22.1624 | 21.6253 | 21.7915 | 21.906 | 21.0954 | 21.1954 | 21.4641 | 20.4799 | 20.8015 | 22.5698 | 21.8613 | 21.7744 | 25.1686 | 124.1687 | 108.7085 | 130.7028 | 22.1307 | 21.8091 | 23.8324 | 22.0132 | 21.8699 | 24.7415 | 47.8841 | 139.0072 |  | 75.5915 | 108.2095 | 106.5939 | 97.9656 |  | 17.1457 | 17.6037 | 16.8823 | 17.4484 | 17.7494 | 22.7814 | 81.3002 | 15.592 | 17.0674 | 15.7867 | 18.0503 | 18.4221 | 47.1838 | 48.398 | 46.2176 | 21.6528 |  |  | 0.78483 | -0.34637 | -26.1915 | 0.33969 | 0.30306 | -163.7272 | 20.6856 | 0.66398 | -0.34513 | 0.22607 | 0.18153 | 0.00034827 | 0.0003647 | 1.2865 | 21.7831 | 21.9785 | 22.176 | 22.2259 | 22.0326 | 21.3402 | 20.1477 | 22.1883 | 22.3566 | 22.405 | 22.3467 | 21.9673 | 21.1943 | 22.2729 | 64.4168 | 42.904 | 44.5177 | 32.5823 | 29.5468 | 41.9563 | 29.253 | 22.3307 | 22.0983 | 21.6596 | 22.0631 | 21.7797 | 21.3426 | 21.9357 | 21.6267 | 22.7951 | 44.6741 | 116.6953 | 94.9214 | 63.8044 | 0.86898 | 0.4044 | 52.6282 | 21.9263 | 22.248 | 20.3433 | 21.5793 | 22.0335 | 21.9223 | 21.9461 | 27.3154 | 21.7966 | 21.5524 | 23.5088 | 124.0001 | 156.8795 | 96.2571 | 97.4888 | 66.6775 |  | 44.5931 | 92.3623 | 48.3405 | 75.9187 | 51.1584 | 54.3099 |  | 61.2085 |  |  | 22.3905 | 24.6012 | 48.29 | [5 empty] | 21.892 | 54.63 | 21.6806 | 22.0753 | 30.6803 | 21.2564 | 21.8923 | 26.0083 | 70.7906 | 158.6431 |  | 61.9963 | 116.2499 | 21.8261 | 56.284 | 131.1804 | 39.5228 | 92.4375 | 24.1229 | 92.1548 | 23.9381 | 92.8203 | 18.619 | 60.067 | 112.1851 | 27.2147 | 58.2318 | 123.6618 | 21.313 | 53.3453 | 124.6612 | 21.9943 | 85.2767 | 28.6892 | 92.1495 | 24.2703 | 97.5754 | 0.99656 | 19.4532 | 1.1891 | 0.042795 | -27.0934 | 3.0953 | 162.5 | 51.93 | 1.2407 | -0.69935 | -6.0815 | 0.69258 | 0.65997 | -15.3399 | 5.4525 | -0.035509 | -0.61713 | -0.060573 | -1.9366 | -1.2219 | -0.78889 | 0.047137
42838.4244 | 354 | 22.9159 | 22.8731 | 22.8619 | 22.7775 | 22.3896 | 21.7171 | 22.712 | 21.7734 | 22.3623 | 22.3625 | 22.3312 | 21.9787 | 21.1928 | 22.1583 | 21.6261 | 21.7885 | 21.9087 | 21.0907 | 21.196 | 21.4609 | 20.4788 | 20.8045 | 22.5817 | 21.8668 | 21.7735 | 25.1938 | 124.3459 | 108.8828 | 131.1067 | 22.1405 | 21.8167 | 23.8483 | 22.0261 | 21.8704 | 24.764 | 48.106 | 139.447 |  | 75.8709 | 108.4253 | 106.8487 | 98.5839 |  | 17.1484 | 17.6078 | 16.8821 | 17.457 | 17.7582 | 22.889 | 81.7942 | 15.5249 | 17.0742 | 15.7876 | 18.0508 | 18.4296 | 47.127 | 48.3407 | 46.1652 | 21.6471 |  |  | 0.4589 | -0.36739 | -26.1198 | 0.43891 | 0.33263 | -167.0713 | 20.2828 | 1.0254 | -0.043108 | 0.098088 | 0.098028 | 0.00036799 | 0.00035977 | 1.2816 | 21.785 | 21.9762 | 22.1749 | 22.22 | 22.0334 | 21.3348 | 20.1484 | 22.1842 | 22.3527 | 22.4025 | 22.3495 | 21.9706 | 21.1898 | 22.271 | 65.4546 | 44.4819 | 46.0936 | 33.1105 | 29.518 | 42.1186 | 29.3352 | 22.3254 | 22.0973 | 21.654 | 22.0602 | 21.768 | 21.3363 | 21.9336 | 21.617 | 22.7981 | 44.7833 | 116.9396 | 95.1045 | 63.9577 | 1.112 | 0.53735 | 52.7235 | 21.9157 | 22.2473 | 20.3302 | 21.5803 | 22.0302 | 21.9084 | 21.9522 | 27.3516 | 21.7951 | 21.5561 | 23.5301 | 124.1545 | 157.3307 | 96.5419 | 97.7595 | 66.5159 |  | 44.741 | 91.776 | 48.4564 | 77.4582 | 51.4132 | 54.2088 |  | 61.3767 |  |  | 22.4192 | 24.6348 | 48.6026 | [5 empty] | 21.8977 | 54.8557 | 21.6925 | 22.078 | 30.7318 | 21.2586 | 21.8959 | 26.0476 | 71.1113 | 159.05 |  | 62.3158 | 116.4613 | 21.8458 | 56.6507 | 131.6326 | 39.5757 | 92.6028 | 24.1545 | 92.4028 | 23.9665 | 93.0062 | 18.6202 | 60.4003 | 112.5152 | 27.242 | 58.4416 | 123.6096 | 21.3137 | 53.6048 | 124.9148 | 22.0098 | 85.4483 | 28.7215 | 92.2932 | 24.2916 | 98.0388 | 1.0583 | 19.4491 | 1.1952 | 0.043325 | -27.1046 | 3.0953 | 157.76 | 52.23 | 0.94919 | -0.72027 | -6.0732 | 0.78726 | 0.69155 | -15.4986 | 5.4001 | -0.025835 | -0.59675 | -0.094287 | -2.0327 | -1.3874 | -0.79823 | 0.046712
42838.4244 | 355 | 22.915 | 22.8698 | 22.8497 | 22.7752 | 22.3791 | 21.7148 | 22.7113 | 21.7697 | 22.3594 | 22.3633 | 22.3279 | 21.9788 | 21.187 | 22.158 | 21.6235 | 21.7918 | 21.9149 | 21.0937 | 21.1974 | 21.4624 | 20.4779 | 20.8075 | 22.5987 | 21.8707 | 21.7758 | 25.2146 | 124.518 | 109.0107 | 131.2552 | 22.1372 | 21.8213 | 23.8703 | 22.0228 | 21.8792 | 24.7866 | 48.3375 | 140.5627 |  | 76.1516 | 108.604 | 107.1414 | 98.5105 |  | 17.1587 | 17.6098 | 16.8806 | 17.4561 | 17.7579 | 22.8625 | 82.1484 | 15.4905 | 17.0794 | 15.7804 | 18.0624 | 18.4252 | 47.0571 | 48.3027 | 46.1175 | 21.6454 |  |  | 0.49438 | -0.41931 | -26.1941 | 0.48031 | 0.39769 | -165.4844 | 20.8052 | 0.76584 | -0.018199 | 0.1797 | 0.15184 | 0.0003532 | 0.00030885 | 1.2793 | 21.7843 | 21.9723 | 22.1743 | 22.2197 | 22.0318 | 21.3349 | 20.1472 | 22.1854 | 22.3622 | 22.3961 | 22.3482 | 21.9684 | 21.1935 | 22.2725 | 67.0278 | 47.0032 | 50.1312 | 34.4226 | 30.4944 | 42.2892 | 29.5036 | 22.3298 | 22.096 | 21.6568 | 22.0538 | 21.7704 | 21.3385 | 21.9346 | 21.6188 | 22.8115 | 44.9079 | 117.1001 | 95.2733 | 64.6273 | 0.96748 | 0.99915 | 52.7426 | 21.9141 | 22.2397 | 20.3286 | 21.5809 | 22.0282 | 21.9196 | 21.9511 | 27.3747 | 21.7828 | 21.5473 | 23.5513 | 124.326 | 157.8642 | 96.812 | 97.9764 | 66.4071 |  | 44.8865 | 91.5485 | 48.5791 | 77.6213 | 51.6401 | 54.1147 |  | 61.572 |  |  | 22.4363 | 24.6499 | 48.6053 | [5 empty] | 21.8986 | 55.0273 | 21.6846 | 22.0735 | 30.7717 | 21.2557 | 21.8972 | 26.087 | 71.3976 | 159.6865 |  | 62.767 | 116.6533 | 21.8593 | 56.948 | 132.1173 | 39.5941 | 92.7836 | 24.1861 | 92.6657 | 23.9827 | 93.1972 | 18.6298 | 60.6204 | 112.848 | 27.2701 | 58.5917 | 123.7131 | 21.3103 | 53.8803 | 125.1694 | 22.0218 | 85.5882 | 28.741 | 92.4717 | 24.3201 | 98.312 | 1.0003 | 19.4441 | 1.2007 | 0.042999 | -27.0728 | 3.0953 | 165.09 | 51.57 | 0.98539 | -0.76948 | -6.0819 | 0.82356 | 0.75612 | -15.4241 | 5.469 | -0.017713 | -0.5861 | -0.09075 | -2.1874 | -1.8162 | -0.78802 | 0.032479
42838.4244 | 356 | 22.9148 | 22.8726 | 22.8597 | 22.7822 | 22.3864 | 21.7151 | 22.7134 | 21.7666 | 22.3569 | 22.359 | 22.3299 | 21.9828 | 21.19 | 22.1553 | 21.6223 | 21.7915 | 21.9078 | 21.0971 | 21.1962 | 21.4637 | 20.4795 | 20.807 | 22.6075 | 21.8724 | 21.7746 | 25.2336 | 124.7819 | 109.1121 | 131.5449 | 22.1387 | 21.828 | 23.8856 | 22.0299 | 21.8809 | 24.8166 | 48.5125 | 142.7494 |  | 76.4684 | 108.8475 | 107.3934 | 99.7251 |  | 17.1537 | 17.62 | 16.8784 | 17.4682 | 17.811 | 22.7414 | 82.5165 | 15.4592 | 17.0873 | 15.7957 | 18.0725 | 18.4326 | 46.9918 | 48.2605 | 46.0741 | 21.6472 |  |  | 0.57389 | -0.28854 | -26.1901 | 0.52631 | 0.39112 | -164.2529 | 20.6705 | 0.77504 | 0.040181 | 0.15264 | 0.22962 | 0.00036306 | 0.00037127 | 1.2625 | 21.7879 | 21.9814 | 22.1755 | 22.2254 | 22.0443 | 21.334 | 20.1485 | 22.1853 | 22.3606 | 22.3929 | 22.3486 | 21.9649 | 21.2024 | 22.2788 | 68.3003 | 49.6835 | 52.4954 | 35.4624 | 31.4949 | 42.4495 | 29.6477 | 22.3318 | 22.0946 | 21.6568 | 22.0542 | 21.7794 | 21.3425 | 21.9406 | 21.626 | 22.8238 | 45.0256 | 117.3353 | 95.419 | 64.8534 | 0.85227 | 0.55427 | 53.2144 | 21.9203 | 22.2459 | 20.3328 | 21.5816 | 22.0375 | 21.9214 | 21.9583 | 27.4289 | 21.7828 | 21.5705 | 23.5524 | 124.7356 | 158.2958 | 97.0786 | 98.2335 | 67.3314 |  | 45.04 | 91.8835 | 48.6927 | 77.1198 | 51.84 | 54.5083 |  | 61.7593 |  |  | 22.4664 | 24.6813 | 48.693 | [5 empty] | 21.9011 | 55.0046 | 21.6878 | 22.0801 | 30.8001 | 21.2671 | 21.9086 | 26.1449 | 71.6669 | 159.8382 |  | 63.3405 | 116.8821 | 21.883 | 57.1308 | 132.4459 | 39.6197 | 92.968 | 24.2184 | 93.1016 | 24.0026 | 93.3894 | 18.6448 | 60.8887 | 113.1449 | 27.3021 | 58.7496 | 123.9118 | 21.3229 | 54.0389 | 125.3264 | 22.0374 | 85.7913 | 28.7433 | 92.7032 | 24.3549 | 98.3951 | 1.0871 | 19.439 | 1.2056 | 0.04273 | -27.1235 | 3.0953 | 135.53 | 53.06 | 1.0621 | -0.63833 | -6.0815 | 0.86211 | 0.7497 | -15.3635 | 5.4502 | -0.038001 | -0.59139 | -0.069712 | -2.3098 | -2.062 | -0.81558 | 0.030327
42838.4244 | 357 | 22.9126 | 22.8726 | 22.8535 | 22.7793 | 22.3886 | 21.71 | 22.709 | 21.7678 | 22.355 | 22.3576 | 22.3257 | 21.9765 | 21.1914 | 22.1626 | 21.6398 | 21.7953 | 21.9098 | 21.0965 | 21.1952 | 21.4713 | 20.4878 | 20.8142 | 22.6264 | 21.88 | 21.7779 | 25.2581 | 124.9528 | 109.2923 | 131.6301 | 22.1358 | 21.8245 | 23.8905 | 22.0246 | 21.8817 | 24.8343 | 48.7068 | 142.0502 |  | 76.721 | 109.2189 | 107.6023 | 101.6466 |  | 17.1581 | 17.6181 | 16.8866 | 17.4761 | 17.8705 | 22.7714 | 82.6367 | 15.4812 | 17.0731 | 15.8007 | 18.0615 | 18.4397 | 46.9244 | 48.2185 | 46.017 | 21.6478 |  |  | 0.59623 | -0.28854 | -26.106 | 0.3824 | 0.48706 | -160.094 | 20.4799 | 0.73101 | 0.15499 | 0.065569 | 0.091084 | 0.00034499 | 0.00034499 | 1.2468 | 21.7819 | 21.9683 | 22.1653 | 22.2222 | 22.0365 | 21.3215 | 20.1374 | 22.176 | 22.3559 | 22.3956 | 22.3454 | 21.9629 | 21.1933 | 22.2649 | 69.3048 | 49.0982 | 52.0983 | 36.3199 | 32.4223 | 42.6087 | 29.7714 | 22.3244 | 22.0947 | 21.6592 | 22.0545 | 21.7704 | 21.3413 | 21.9371 | 21.623 | 22.8382 | 45.1581 | 117.8899 | 95.8114 | 64.5555 | 0.39498 | 0.094751 | 53.5728 | 21.9224 | 22.2479 | 20.3448 | 21.5857 | 22.0379 | 21.9219 | 21.9651 | 27.4557 | 21.7911 | 21.5583 | 23.5764 | 125.063 | 158.5985 | 97.3163 | 98.4568 | 68.5466 |  | 45.1744 | 92.3203 | 48.7947 | 77.0665 | 52.0268 | 54.5845 |  | 61.921 |  |  | 22.4858 | 24.6891 | 48.7407 | [5 empty] | 21.8928 | 54.5668 | 21.6875 | 22.0775 | 30.8318 | 21.2561 | 21.9032 | 26.1867 | 71.9302 | 159.9121 |  | 63.8301 | 117.133 | 21.9059 | 57.3567 | 132.6691 | 39.6619 | 93.1564 | 24.2287 | 93.477 | 24.0211 | 93.5682 | 18.6508 | 61.2092 | 113.3785 | 27.3484 | 59.0071 | 124.0775 | 21.3395 | 54.23 | 125.41 | 22.0563 | 86.0067 | 28.7515 | 92.8853 | 24.3918 | 98.573 | 1.2279 | 19.4359 | 1.2107 | 0.042295 | -27.1262 | 3.0953 | 153.94 | 51.59 | 1.0826 | -0.63833 | -6.0717 | 0.73485 | 0.83665 | -15.1685 | 5.4252 | -0.06704 | -0.59992 | -0.061588 | -2.4026 | -2.0033 | -0.86209 | 0.043252
42838.4244 | 358 | 22.9166 | 22.8785 | 22.8554 | 22.7782 | 22.3938 | 21.7183 | 22.7116 | 21.7692 | 22.3633 | 22.3633 | 22.3318 | 21.9851 | 21.1962 | 22.1617 | 21.6367 | 21.7868 | 21.9129 | 21.0932 | 21.1993 | 21.4653 | 20.4786 | 20.8163 | 22.6301 | 21.8705 | 21.7845 | 25.2763 | 125.0127 | 109.5027 | 130.9145 | 22.1376 | 21.8261 | 23.9021 | 22.0279 | 21.8879 | 24.8638 | 48.9239 | 141.4418 |  | 76.9736 | 109.55 | 107.8716 | 103.0094 |  | 17.1667 | 17.6353 | 16.8898 | 17.4879 | 17.9013 | 23.1929 | 82.6538 | 15.5098 | 17.0736 | 15.8136 | 18.07 | 18.4411 | 46.8473 | 48.1756 | 45.9562 | 21.6474 |  |  | 0.60018 | -0.12623 | -25.9707 | 0.15832 | 0.422 | -164.8115 | 20.7684 | 0.68567 | -0.11492 | 0.013748 | 0.18674 | 0.00037456 | 0.00035156 | 1.2501 | 21.7738 | 21.9748 | 22.1695 | 22.2226 | 22.0379 | 21.3355 | 20.1431 | 22.1852 | 22.3645 | 22.3964 | 22.3497 | 21.9659 | 21.1906 | 22.2645 | 66.1566 | 44.1999 | 45.5428 | 35.1542 | 32.0127 | 42.6524 | 29.8083 | 22.3297 | 22.1012 | 21.6582 | 22.0599 | 21.7797 | 21.3412 | 21.9388 | 21.6307 | 22.8493 | 45.2687 | 118.0067 | 96.0063 | 64.0893 | 0.174 | -0.14452 | 53.5065 | 21.9168 | 22.2401 | 20.346 | 21.5836 | 22.0352 | 21.9219 | 21.9686 | 27.4875 | 21.793 | 21.5744 | 23.5971 | 125.2873 | 158.6816 | 97.5513 | 98.6398 | 69.9623 |  | 45.3363 | 92.8158 | 48.9011 | 76.3033 | 52.2137 | 54.403 |  | 62.08 |  |  | 22.4884 | 24.689 | 48.6616 | [5 empty] | 21.895 | 54.0201 | 21.6877 | 22.0813 | 30.8994 | 21.2594 | 21.9084 | 26.2261 | 72.1931 | 160.3483 |  | 64.1017 | 117.2784 | 21.9186 | 57.641 | 132.984 | 39.7396 | 93.3903 | 24.2354 | 93.7805 | 24.0475 | 93.7597 | 18.6615 | 61.6555 | 113.5634 | 27.3861 | 59.3164 | 124.1804 | 21.339 | 54.5237 | 125.6299 | 22.0884 | 86.2233 | 28.8089 | 93.1311 | 24.4363 | 98.89 | 0.97819 | 19.4333 | 1.2157 | 0.041242 | -27.0932 | 3.0952 | 144.19 | 52.14 | 1.0853 | -0.42222 | -6.0561 | 0.47285 | 0.77933 | -15.4013 | 5.4672 | -0.10068 | -0.60992 | -0.033738 | -2.0476 | -1.2706 | -0.89227 | 0.060084
42838.4244 | 359 | 22.9166 | 22.8825 | 22.862 | 22.7814 | 22.3983 | 21.7251 | 22.7136 | 21.777 | 22.366 | 22.3683 | 22.3316 | 21.9939 | 21.1988 | 22.1635 | 21.6299 | 21.7863 | 21.9133 | 21.0928 | 21.2004 | 21.4651 | 20.4753 | 20.8128 | 22.6467 | 21.8721 | 21.794 | 25.3024 | 125.0856 | 109.6182 | 131.0502 | 22.1381 | 21.8255 | 23.9227 | 22.0323 | 21.8903 | 24.8775 | 49.1472 | 140.7296 |  | 77.2413 | 109.804 | 108.1511 | 103.2782 |  | 17.1663 | 17.6323 | 16.8914 | 17.4928 | 17.9067 | 23.2125 | 83.2479 | 15.5507 | 17.0805 | 15.8026 | 18.07 | 18.4393 | 46.7794 | 48.1278 | 45.8926 | 21.6453 |  |  | 0.64552 | -0.20311 | -25.7308 | 0.341 | 0.25641 | -163.4913 | 21.3723 | 0.91369 | 0.047965 | 0.10228 | 0.34159 | 0.00032199 | 0.00032199 | 1.2341 | 21.7821 | 21.9712 | 22.1659 | 22.2252 | 22.041 | 21.339 | 20.1501 | 22.1846 | 22.3615 | 22.3993 | 22.3461 | 21.9647 | 21.1953 | 22.2712 | 62.5075 | 40.2671 | 41.0511 | 32.9795 | 30.4055 | 42.6605 | 29.8133 | 22.3289 | 22.0957 | 21.654 | 22.0555 | 21.7709 | 21.3415 | 21.9373 | 21.6299 | 22.8622 | 45.3776 | 118.0189 | 96.1387 | 63.7176 | 0.56013 | -0.10686 | 53.3355 | 21.914 | 22.2378 | 20.3315 | 21.5624 | 22.0249 | 21.912 | 21.9531 | 27.5171 | 21.7812 | 21.5545 | 23.5964 | 125.5345 | 158.6897 | 97.7827 | 98.8856 | 70.534 |  | 45.489 | 93.0548 | 49.0054 | 76.2399 | 52.4113 | 54.2623 |  | 62.2584 |  |  | 22.497 | 24.7063 | 48.6203 | [5 empty] | 21.8952 | 54.1952 | 21.6835 | 22.0814 | 30.9734 | 21.2616 | 21.9083 | 26.2869 | 72.4398 | 160.7064 |  | 64.1741 | 117.5191 | 21.9456 | 57.8329 | 133.2046 | 39.8835 | 93.8244 | 24.2645 | 94.0244 | 24.0838 | 93.9931 | 18.6709 | 61.9171 | 113.9144 | 27.4232 | 59.624 | 124.2621 | 21.3478 | 54.6932 | 125.9993 | 22.1233 | 86.525 | 28.8535 | 93.307 | 24.439 | 99.2368 | 1.0413 | 19.4279 | 1.2207 | 0.042004 | -27.1404 | 3.0953 | 149.64 | 52.35 | 1.1257 | -0.53557 | -6.0281 | 0.69395 | 0.6075 | -15.34 | 5.5463 | -0.1112 | -0.61287 | -0.024942 | -1.6412 | -0.77095 | -0.89184 | 0.074233
42838.4244 | 360 | 22.9163 | 22.8756 | 22.8613 | 22.7751 | 22.3935 | 21.7199 | 22.7183 | 21.7712 | 22.3594 | 22.3643 | 22.332 | 21.9819 | 21.193 | 22.168 | 21.6278 | 21.7981 | 21.9142 | 21.107 | 21.1987 | 21.4718 | 20.4873 | 20.8189 | 22.6591 | 21.8711 | 21.7977 | 25.3238 | 125.0669 | 109.6677 | 130.2147 | 22.1356 | 21.8299 | 23.9477 | 22.0278 | 21.8888 | 24.8939 | 49.3602 | 140.9112 |  | 77.5249 | 110.0781 | 108.3529 | 103.3844 |  | 17.1611 | 17.6361 | 16.8978 | 17.4815 | 17.8901 | 23.3074 | 83.5516 | 15.6055 | 17.0791 | 15.7179 | 18.0788 | 18.4327 | 46.7133 | 48.0821 | 45.8283 | 21.6412 |  |  | 1.0707 | -0.43508 | -25.4279 | 0.52565 | 0.40032 | -159.5973 | 21.0858 | 0.79015 | 0.19333 | 0.16858 | 0.18431 | 0.00035813 | 0.00033677 | 1.224 | 21.7779 | 21.9725 | 22.166 | 22.2212 | 22.0355 | 21.3314 | 20.1391 | 22.1789 | 22.3506 | 22.393 | 22.3438 | 21.9622 | 21.1875 | 22.2683 | 60.8265 | 37.2858 | 37.4954 | 31.298 | 28.9013 | 42.701 | 29.8209 | 22.3277 | 22.0953 | 21.6543 | 22.0585 | 21.7714 | 21.3472 | 21.9373 | 21.6271 | 22.8711 | 45.4871 | 118.1149 | 96.2718 | 63.6059 | 0.65784 | -0.10135 | 53.3032 | 21.9199 | 22.2475 | 20.3444 | 21.5759 | 22.0353 | 21.9218 | 21.973 | 27.5632 | 21.7896 | 21.5743 | 23.6195 | 125.6119 | 159.1018 | 98.0194 | 99.1454 | 70.7639 |  | 45.6252 | 93.8921 | 49.1029 | 77.0813 | 52.6073 | 54.3335 |  | 62.4157 |  |  | 22.4917 | 24.7212 | 48.7062 | [5 empty] | 21.8903 | 55.3506 | 21.6795 | 22.0775 | 30.975 | 21.2527 | 21.8991 | 26.3277 | 72.704 | 160.6834 |  | 64.1666 | 117.6258 | 21.9556 | 57.9557 | 133.2312 | 39.9667 | 94.1687 | 24.257 | 94.3629 | 24.1142 | 94.1872 | 18.7004 | 61.9523 | 114.0857 | 27.4494 | 59.8407 | 124.6073 | 21.3612 | 54.7615 | 126.2911 | 22.1633 | 86.8967 | 28.8811 | 93.4205 | 24.4567 | 99.4018 | 1.0951 | 19.4218 | 1.226 | 0.042549 | -27.0548 | 3.0953 | 141.97 | 51.74 | 1.4483 | -0.78386 | -5.9925 | 0.86159 | 0.75919 | -15.1587 | 5.5099 | -0.11281 | -0.63268 | -0.041335 | -1.4496 | -0.37499 | -0.88725 | 0.081179
42838.4245 | 361 | 22.9168 | 22.8672 | 22.8635 | 22.7745 | 22.3869 | 21.7146 | 22.7103 | 21.7694 | 22.3525 | 22.3599 | 22.3311 | 21.9806 | 21.1945 | 22.1646 | 21.632 | 21.7996 | 21.9158 | 21.0964 | 21.1997 | 21.4731 | 20.4816 | 20.818 | 22.6749 | 21.8787 | 21.8003 | 25.3484 | 125.2696 | 109.7096 | 129.6459 | 22.129 | 21.817 | 23.9463 | 22.0217 | 21.8792 | 24.9092 | 49.5601 | 142.1275 |  | 77.8031 | 110.3756 | 108.6246 | 103.1664 |  | 17.1677 | 17.6417 | 16.8985 | 17.4807 | 17.8791 | 23.5975 | 82.8605 | 15.7118 | 17.0784 | 15.6084 | 18.0914 | 18.4343 | 46.6565 | 48.0378 | 45.7647 | 21.6474 |  |  | 0.56995 | -0.33256 | -25.2367 | 0.54208 | 0.33263 | -163.7233 | 20.6166 | 0.89792 | 0.17231 | 0.14299 | 0.1357 | 0.00033513 | 0.00034663 | 1.2252 | 21.7891 | 21.9722 | 22.1708 | 22.2238 | 22.035 | 21.3349 | 20.1441 | 22.1837 | 22.3558 | 22.3991 | 22.3456 | 21.9635 | 21.1894 | 22.2753 | 59.3558 | 35.9709 | 35.9921 | 30.5794 | 27.9901 | 42.7453 | 29.8282 | 22.3284 | 22.0911 | 21.6577 | 22.0499 | 21.7721 | 21.3488 | 21.9331 | 21.6258 | 22.8867 | 45.6089 | 118.1058 | 96.3635 | 63.4285 | 1.007 | -0.042384 | 53.2794 | 21.9107 | 22.2335 | 20.3394 | 21.5651 | 22.0238 | 21.9051 | 21.9616 | 27.5881 | 21.7801 | 21.5573 | 23.6296 | 125.7677 | 159.0188 | 98.2359 | 99.3181 | 70.1009 |  | 45.7488 | 94.1636 | 49.2096 | 77.1367 | 52.7961 | 54.6115 |  | 62.5706 |  |  | 22.5245 | 24.7519 | 48.786 | [5 empty] | 21.8881 | 55.1472 | 21.6922 | 22.0816 | 31.0319 | 21.2656 | 21.8983 | 26.3638 | 72.9762 | 160.387 |  | 64.1669 | 117.8295 | 21.964 | 58.2148 | 133.2029 | 40.0953 | 94.3576 | 24.2847 | 94.6252 | 24.1337 | 94.296 | 18.7114 | 62.0317 | 114.2171 | 27.4843 | 60.022 | 125.1321 | 21.3692 | 55.0678 | 126.4498 | 22.2002 | 87.2393 | 28.9163 | 93.5226 | 24.4858 | 99.5215 | 0.91717 | 19.4172 | 1.231 | 0.042309 | -27.1268 | 3.0953 | 122.95 | 52.61 | 1.0559 | -0.68532 | -5.97 | 0.87496 | 0.69238 | -15.3609 | 5.4509 | -0.090047 | -0.63645 | -0.036148 | -1.281 | -0.2071 | -0.87413 | 0.090381
42838.4245 | 362 | 22.9214 | 22.8697 | 22.8664 | 22.7769 | 22.3931 | 21.7219 | 22.7129 | 21.7617 | 22.3659 | 22.3608 | 22.3349 | 21.9866 | 21.1927 | 22.1675 | 21.6172 | 21.7881 | 21.9044 | 21.0871 | 21.1901 | 21.4692 | 20.4737 | 20.8143 | 22.6837 | 21.8671 | 21.7864 | 25.3622 | 125.1863 | 109.9306 | 128.2622 | 22.135 | 21.8306 | 23.9686 | 22.0227 | 21.8888 | 24.9342 | 49.7906 | 141.3782 |  | 78.077 | 110.7066 | 108.8876 | 102.774 |  | 17.1635 | 17.6361 | 16.8951 | 17.4881 | 17.9155 | 23.7438 | 82.8866 | 15.7267 | 17.0774 | 15.5886 | 18.0934 | 18.4378 | 46.6042 | 47.9938 | 45.7165 | 21.639 |  |  | 0.25322 | -0.2938 | -25.3392 | 0.15569 | 0.24129 | -162.4767 | 21.4104 | 0.97217 | 0.10693 | -0.020659 | 0.14612 | 0.00037949 | 0.00033349 | 1.2249 | 21.7823 | 21.9708 | 22.1693 | 22.2218 | 22.0345 | 21.3345 | 20.1441 | 22.1826 | 22.358 | 22.401 | 22.3441 | 21.9633 | 21.1893 | 22.2759 | 60.4714 | 38.6147 | 37.7658 | 30.423 | 27.3886 | 42.8398 | 29.8566 | 22.3303 | 22.0928 | 21.6469 | 22.0483 | 21.7749 | 21.3518 | 21.93 | 21.6241 | 22.8992 | 45.7288 | 118.1932 | 96.5944 | 63.2806 | 0.75574 | 0.27411 | 53.361 | 21.9133 | 22.2358 | 20.3445 | 21.5775 | 22.0306 | 21.922 | 21.9799 | 27.6313 | 21.7874 | 21.5671 | 23.6503 | 126.049 | 159.119 | 98.4288 | 99.5509 | 69.178 |  | 45.8943 | 95.0599 | 49.3406 | 78.2948 | 53.039 | 54.7372 |  | 62.7743 |  |  | 22.545 | 24.7635 | 48.5608 | [5 empty] | 21.8911 | 56.1747 | 21.6843 | 22.0787 | 31.0701 | 21.2597 | 21.8995 | 26.4259 | 73.2727 | 160.3058 |  | 64.2547 | 118.0299 | 21.9785 | 58.4918 | 133.2295 | 40.1535 | 94.6214 | 24.3036 | 94.6532 | 24.1661 | 94.4473 | 18.7068 | 62.1567 | 114.4288 | 27.5211 | 60.2406 | 125.3033 | 21.3768 | 55.4006 | 126.5225 | 22.2203 | 87.4175 | 28.9537 | 93.719 | 24.5202 | 99.7839 | 0.88526 | 19.4126 | 1.2364 | 0.043739 | -27.1015 | 3.0953 | 118.11 | 51.57 | 0.7026 | -0.64414 | -5.9821 | 0.46891 | 0.58985 | -15.306 | 5.5562 | -0.059296 | -0.65671 | -0.059662 | -1.3938 | -0.40084 | -0.85506 | 0.098703
42838.4245 | 363 | 22.9154 | 22.8676 | 22.8573 | 22.776 | 22.3872 | 21.7131 | 22.7014 | 21.761 | 22.3502 | 22.3587 | 22.3318 | 21.9742 | 21.1842 | 22.1611 | 21.6231 | 21.7952 | 21.911 | 21.0913 | 21.1925 | 21.4781 | 20.4821 | 20.824 | 22.6998 | 21.8755 | 21.7965 | 25.3852 | 125.1591 | 110.1388 | 128.6771 | 22.1375 | 21.8276 | 23.9937 | 22.022 | 21.8907 | 24.9589 | 49.992 | 140.8995 |  | 78.3211 | 110.905 | 109.0734 | 103.1472 |  | 17.1579 | 17.6443 | 16.8963 | 17.5023 | 18.0111 | 23.6912 | 82.9308 | 15.784 | 17.0887 | 15.6721 | 18.0993 | 18.4412 | 46.5552 | 47.9523 | 45.6701 | 21.6434 |  |  | 0.3715 | -0.30562 | -25.0152 | 0.38634 | 0.13287 | -161.2328 | 21.1857 | 0.7297 | 0.099145 | 0.048995 | 0.2284 | 0.00034992 | 0.00035649 | 1.2431 | 21.7828 | 21.9656 | 22.1603 | 22.2234 | 22.0299 | 21.3295 | 20.1489 | 22.1821 | 22.3527 | 22.3957 | 22.3432 | 21.9634 | 21.1859 | 22.2699 | 60.9978 | 40.0123 | 40.3679 | 30.2022 | 27.4202 | 42.9244 | 29.9008 | 22.325 | 22.0836 | 21.6519 | 22.0544 | 21.7715 | 21.347 | 21.9307 | 21.626 | 22.9137 | 45.8464 | 118.3534 | 96.848 | 62.9987 | 1.0335 | 0.23588 | 53.4388 | 21.9143 | 22.2359 | 20.3438 | 21.5726 | 22.0207 | 21.9149 | 21.9762 | 27.668 | 21.7937 | 21.5738 | 23.662 | 126.087 | 159.2775 | 98.603 | 99.7663 | 68.6725 |  | 46.028 | 96.0096 | 49.4666 | 78.7253 | 53.2533 | 54.6979 |  | 62.918 |  |  | 22.5367 | 24.7865 | 48.7142 | [5 empty] | 21.8931 | 56.1096 | 21.6853 | 22.0813 | 31.0883 | 21.253 | 21.8941 | 26.4647 | 73.5522 | 160.0876 |  | 64.5712 | 118.1214 | 21.993 | 58.7648 | 133.3023 | 40.2768 | 94.8637 | 24.3257 | 94.7582 | 24.1975 | 94.6374 | 18.693 | 62.3609 | 114.6123 | 27.5516 | 60.4191 | 125.3705 | 21.4001 | 55.6161 | 126.7974 | 22.2298 | 87.6682 | 28.9444 | 93.9974 | 24.5474 | 100.0485 | 1.2242 | 19.4092 | 1.2414 | 0.044726 | -27.2981 | 3.0953 | 103.11 | 52.27 | 0.85147 | -0.65698 | -5.9438 | 0.73866 | 0.43766 | -15.246 | 5.5265 | -0.040556 | -0.67863 | -0.063978 | -1.4423 | -0.68478 | -0.85829 | 0.11067
42838.4245 | 364 | 22.916 | 22.8798 | 22.8538 | 22.7718 | 22.3859 | 21.72 | 22.7066 | 21.766 | 22.3596 | 22.3592 | 22.3311 | 21.9769 | 21.1843 | 22.1588 | 21.6365 | 21.7949 | 21.9167 | 21.0979 | 21.1997 | 21.4847 | 20.488 | 20.8219 | 22.7151 | 21.884 | 21.8 | 25.413 | 125.3131 | 110.2929 | 129.3521 | 22.1286 | 21.8316 | 24.0043 | 22.0198 | 21.8855 | 24.9812 | 50.2099 | 139.3442 |  | 78.503 | 111.0437 | 109.2258 | 103.009 |  | 17.1535 | 17.6374 | 16.9026 | 17.524 | 18.0291 | 23.575 | 82.4932 | 15.8453 | 17.0789 | 15.7404 | 18.1042 | 18.454 | 46.5228 | 47.9277 | 45.6238 | 21.6504 |  |  | 0.46875 | -0.41865 | -24.8207 | 0.14189 | 0.55934 | -160.4331 | 20.9997 | 0.78029 | 0.046019 | 0.16585 | 0.16556 | 0.00037291 | 0.00034334 | 1.2486 | 21.7808 | 21.9707 | 22.1628 | 22.2176 | 22.0292 | 21.3263 | 20.144 | 22.1817 | 22.3595 | 22.3959 | 22.3467 | 21.9689 | 21.1849 | 22.2761 | 61.2929 | 41.8494 | 43.4629 | 30.0459 | 27.4884 | 43.0173 | 29.9916 | 22.3243 | 22.0907 | 21.6543 | 22.054 | 21.7716 | 21.3472 | 21.9322 | 21.633 | 22.9304 | 45.9602 | 118.4172 | 97.1088 | 63.1558 | 0.72842 | 0.23892 | 53.8175 | 21.9125 | 22.2404 | 20.3534 | 21.5781 | 22.028 | 21.9177 | 21.9776 | 27.7106 | 21.7904 | 21.5733 | 23.6812 | 126.1757 | 159.5338 | 98.7124 | 99.949 | 68.7346 |  | 46.151 | 96.1919 | 49.5936 | 78.4225 | 53.423 | 54.7379 |  | 63.0583 |  |  | 22.537 | 24.8178 | 49.0433 | [5 empty] | 21.8895 | 55.6322 | 21.685 | 22.0855 | 31.1223 | 21.2588 | 21.8995 | 26.4931 | 73.775 | 160.6698 |  | 64.9097 | 118.344 | 21.9907 | 59.0289 | 133.3427 | 40.3781 | 95.1075 | 24.3178 | 94.9778 | 24.2306 | 94.7432 | 18.7027 | 62.642 | 114.8599 | 27.5924 | 60.6066 | 125.4933 | 21.4389 | 55.8858 | 127.1342 | 22.2552 | 87.9416 | 28.9862 | 94.1982 | 24.5776 | 100.3515 | 1.0951 | 19.4036 | 1.2466 | 0.043659 | -27.1064 | 3.0953 | 110.1 | 51.86 | 0.95725 | -0.76892 | -5.9205 | 0.44765 | 0.8978 | -15.2052 | 5.5011 | -0.037955 | -0.6792 | -0.049513 | -1.4641 | -1.018 | -0.84673 | 0.1103
42838.4245 | 365 | 22.9179 | 22.8781 | 22.8565 | 22.7764 | 22.3904 | 21.7231 | 22.7138 | 21.7721 | 22.358 | 22.3672 | 22.3289 | 21.9816 | 21.1889 | 22.158 | 21.6403 | 21.7972 | 21.9113 | 21.0982 | 21.1992 | 21.4825 | 20.4894 | 20.829 | 22.7272 | 21.8803 | 21.8021 | 25.4314 | 125.5252 | 110.4531 | 129.7866 | 22.1381 | 21.8346 | 24.0243 | 22.028 | 21.8932 | 25.01 | 50.4143 | 138.5484 |  | 78.6959 | 111.2355 | 109.5043 | 102.3874 |  | 17.138 | 17.6278 | 16.8943 | 17.5267 | 18.0184 | 23.5345 | 82.8178 | 15.8936 | 17.0753 | 15.8223 | 18.0992 | 18.4458 | 46.4586 | 47.9007 | 45.5617 | 21.6439 |  |  | 0.49767 | -0.18537 | -25.0014 | 0.053838 | 0.33592 | -160.8655 | 21.4834 | 0.72247 | 0.0094342 | 0.076688 | 0.28552 | 0.0003762 | 0.00036963 | 1.2401 | 21.7872 | 21.9686 | 22.1565 | 22.224 | 22.0338 | 21.333 | 20.141 | 22.1778 | 22.359 | 22.393 | 22.3384 | 21.9659 | 21.1938 | 22.2663 | 62.0506 | 41.3829 | 43.5589 | 30.3445 | 27.5775 | 43.1458 | 30.0604 | 22.3248 | 22.0974 | 21.6513 | 22.0489 | 21.7694 | 21.3382 | 21.9266 | 21.6338 | 22.9364 | 46.0581 | 118.417 | 97.2603 | 63.0617 | 1.2932 | 0.2121 | 54.155 | 21.9167 | 22.2475 | 20.3564 | 21.5907 | 22.0339 | 21.9254 | 21.9932 | 27.7432 | 21.8007 | 21.5806 | 23.7046 | 126.2802 | 159.6888 | 98.8441 | 100.1022 | 68.3101 |  | 46.2982 | 96.0959 | 49.7148 | 79.482 | 53.6439 | 54.9983 |  | 63.2004 |  |  | 22.5575 | 24.8568 | 49.0205 | [5 empty] | 21.9027 | 55.2409 | 21.6908 | 22.0844 | 31.1645 | 21.2697 | 21.9078 | 26.5315 | 74.0365 | 161.2895 |  | 65.1235 | 118.6316 | 21.9922 | 59.3791 | 133.462 | 40.4969 | 95.3044 | 24.3365 | 95.29 | 24.2705 | 94.8956 | 18.6931 | 62.8165 | 115.1409 | 27.6407 | 60.787 | 125.7229 | 21.4665 | 56.1724 | 127.5052 | 22.2706 | 88.1653 | 29.0227 | 94.3232 | 24.5895 | 100.636 | 1.1257 | 19.3989 | 1.2517 | 0.042984 | -27.1116 | 3.0953 | 132.39 | 51.48 | 0.98686 | -0.51165 | -5.942 | 0.27574 | 0.69571 | -15.2246 | 5.5637 | -0.02099 | -0.67224 | -0.071061 | -1.533 | -1.0206 | -0.82222 | 0.11636
42838.4245 | 366 | 22.9159 | 22.8767 | 22.8591 | 22.782 | 22.3873 | 21.7253 | 22.7111 | 21.7759 | 22.3559 | 22.3579 | 22.3285 | 21.9833 | 21.1915 | 22.158 | 21.6281 | 21.7986 | 21.9107 | 21.0947 | 21.2006 | 21.477 | 20.4904 | 20.8273 | 22.739 | 21.8755 | 21.8006 | 25.4519 | 125.7304 | 110.6834 | 130.731 | 22.1374 | 21.8343 | 24.0402 | 22.03 | 21.8917 | 25.028 | 50.5953 | 138.7165 |  | 78.9048 | 111.4613 | 109.8323 | 102.3859 |  | 17.1585 | 17.6434 | 16.902 | 17.5464 | 18.0421 | 23.4154 | 83.6495 | 15.8714 | 17.0795 | 15.871 | 18.1083 | 18.4526 | 46.409 | 47.8799 | 45.5129 | 21.6452 |  |  | 0.69546 | -0.33914 | -25.0067 | 0.63473 | 0.307 | -164.726 | 21.4958 | 0.73167 | 0.042711 | 0.04291 | 0.26104 | 0.00035977 | 0.00036141 | 1.2224 | 21.7829 | 21.967 | 22.1601 | 22.2168 | 22.0335 | 21.329 | 20.1318 | 22.1686 | 22.3487 | 22.393 | 22.3406 | 21.9591 | 21.1852 | 22.2627 | 64.2539 | 42.3848 | 43.8012 | 30.271 | 27.8389 | 43.3037 | 30.1198 | 22.3226 | 22.0849 | 21.6525 | 22.0415 | 21.7643 | 21.3432 | 21.9282 | 21.6319 | 22.9447 | 46.1775 | 118.5283 | 97.3984 | 62.8044 | 1.2311 | 0.27848 | 54.5179 | 21.9125 | 22.2415 | 20.3581 | 21.5767 | 22.0335 | 21.9146 | 21.9995 | 27.7762 | 21.7832 | 21.5779 | 23.7106 | 126.3253 | 159.3736 | 98.9867 | 100.2706 | 67.4128 |  | 46.4296 | 95.822 | 49.8365 | 81.1132 | 53.9044 | 54.7524 |  | 63.3313 |  |  | 22.5622 | 24.8726 | 49.1763 | [5 empty] | 21.8978 | 55.1413 | 21.6924 | 22.0851 | 31.2108 | 21.2635 | 21.9008 | 26.5817 | 74.3473 | 161.6706 |  | 65.3535 | 118.9956 | 22.0199 | 59.7549 | 133.6549 | 40.617 | 95.4758 | 24.3879 | 95.5325 | 24.3183 | 95.0657 | 18.7105 | 62.9413 | 115.4454 | 27.7019 | 61.0022 | 125.8474 | 21.5016 | 56.4457 | 127.7528 | 22.2893 | 88.3493 | 29.0888 | 94.5295 | 24.6085 | 100.7905 | 0.90919 | 19.3952 | 1.2571 | 0.042628 | -27.1201 | 3.0953 | 136.28 | 52.42 | 1.168 | -0.69206 | -5.9427 | 0.94679 | 0.66497 | -15.4031 | 5.5642 | 0.008557 | -0.66033 | -0.10707 | -1.7592 | -1.0405 | -0.81576 | 0.1277
42838.4245 | 367 | 22.9175 | 22.8783 | 22.8692 | 22.7755 | 22.3954 | 21.7241 | 22.7198 | 21.7787 | 22.3608 | 22.3682 | 22.3375 | 21.9934 | 21.1952 | 22.1597 | 21.6264 | 21.7917 | 21.9128 | 21.0933 | 21.1974 | 21.4738 | 20.4867 | 20.8283 | 22.7517 | 21.8753 | 21.8009 | 25.4746 | 125.9763 | 110.8734 | 132.2595 | 22.1299 | 21.8336 | 24.0525 | 22.0237 | 21.8916 | 25.0453 | 50.7888 | 138.178 |  | 79.1168 | 111.716 | 110.1527 | 102.6696 |  | 17.1533 | 17.6449 | 16.9105 | 17.5527 | 18.0466 | 23.3664 | 84.3927 | 15.8957 | 17.0785 | 15.9162 | 18.1104 | 18.4478 | 46.3547 | 47.8567 | 45.4601 | 21.64 |  |  | 0.67772 | -0.17288 | -25.2262 | 0.53419 | 0.46011 | -162.3545 | 21.0299 | 0.82892 | -0.090006 | 0.089906 | 0.11348 | 0.00034992 | 0.0003302 | 1.2094 | 21.7732 | 21.9594 | 22.1633 | 22.2119 | 22.0273 | 21.3235 | 20.1363 | 22.1741 | 22.3492 | 22.396 | 22.338 | 21.9513 | 21.1801 | 22.2587 | 66.3458 | 45.5642 | 45.4458 | 30.8471 | 27.9881 | 43.4727 | 30.2029 | 22.3331 | 22.0914 | 21.6498 | 22.0553 | 21.7724 | 21.3498 | 21.9347 | 21.6302 | 22.9655 | 46.302 | 118.6657 | 97.5888 | 63.5207 | 0.9435 | 0.52479 | 54.5957 | 21.9141 | 22.2396 | 20.3588 | 21.5839 | 22.0307 | 21.9231 | 21.9944 | 27.8114 | 21.7931 | 21.5882 | 23.7294 | 126.4786 | 159.2859 | 99.1569 | 100.4085 | 67.2172 |  | 46.56 | 95.3869 | 49.9583 | 81.0452 | 54.0958 | 55.1007 |  | 63.4825 |  |  | 22.556 | 24.8787 | 49.672 | [5 empty] | 21.8908 | 54.8849 | 21.6806 | 22.0791 | 31.2395 | 21.2605 | 21.8919 | 26.6329 | 74.6706 | 162.0502 |  | 65.7345 | 119.4378 | 22.0357 | 60.0968 | 133.8514 | 40.7325 | 95.6387 | 24.4223 | 95.7553 | 24.3423 | 95.179 | 18.7369 | 63.103 | 115.6066 | 27.7304 | 61.2434 | 125.8046 | 21.536 | 56.623 | 128.0625 | 22.3099 | 88.4992 | 29.1299 | 94.874 | 24.6267 | 100.8884 | 1.119 | 19.3909 | 1.262 | 0.042687 | -26.9683 | 3.0953 | 162.86 | 51.49 | 1.1552 | -0.49413 | -5.9688 | 0.86858 | 0.814 | -15.2906 | 5.5031 | 0.018581 | -0.64392 | -0.098347 | -1.9716 | -1.2135 | -0.81677 | 0.11218
42838.4245 | 368 | 22.9152 | 22.8763 | 22.8629 | 22.7729 | 22.3836 | 21.7142 | 22.7105 | 21.7787 | 22.3657 | 22.3592 | 22.3324 | 21.9862 | 21.1879 | 22.1654 | 21.6283 | 21.7887 | 21.9086 | 21.088 | 21.1937 | 21.473 | 20.4761 | 20.8279 | 22.76 | 21.8712 | 21.7998 | 25.4942 | 126.2214 | 111.0684 | 133.0839 | 22.1252 | 21.8348 | 24.0608 | 22.0216 | 21.8973 | 25.0618 | 50.9967 | 139.0499 |  | 79.36 | 111.8914 | 110.4199 | 103.4359 |  | 17.1617 | 17.6428 | 16.9152 | 17.5594 | 18.035 | 23.3196 | 85.0788 | 15.8068 | 17.0818 | 15.9466 | 18.1117 | 18.4445 | 46.2955 | 47.851 | 45.4156 | 21.6419 |  |  | 0.61529 | -0.21888 | -25.6421 | 0.36269 | 0.4128 | -159.1576 | 21.1285 | 0.80526 | 0.1153 | 0.14026 | 0.28899 | 0.00036306 | 0.00035813 | 1.2052 | 21.7731 | 21.969 | 22.1652 | 22.2157 | 22.0315 | 21.3257 | 20.14 | 22.1804 | 22.3546 | 22.3936 | 22.3438 | 21.9544 | 21.1822 | 22.2612 | 66.8485 | 47.2332 | 48.3033 | 31.8787 | 28.5034 | 43.6202 | 30.3141 | 22.3236 | 22.0872 | 21.6467 | 22.0503 | 21.7678 | 21.3427 | 21.9291 | 21.6273 | 22.9732 | 46.4317 | 118.6085 | 97.667 | 64.2485 | 1.0206 | 0.53297 | 54.974 | 21.9116 | 22.2395 | 20.3577 | 21.5831 | 22.0351 | 21.9251 | 21.995 | 27.8433 | 21.7944 | 21.5844 | 23.7552 | 126.6076 | 159.1858 | 99.3871 | 100.6043 | 68.4841 |  | 46.6973 | 95.6243 | 50.0788 | 80.5531 | 54.2868 | 55.554 |  | 63.6488 |  |  | 22.5614 | 24.9024 | 49.8913 | [5 empty] | 21.8892 | 55.0433 | 21.6794 | 22.0752 | 31.2493 | 21.2613 | 21.8931 | 26.6718 | 74.8858 | 162.5152 |  | 66.0743 | 119.675 | 22.0341 | 60.3888 | 133.9464 | 40.8476 | 95.7575 | 24.4339 | 95.9888 | 24.3594 | 95.2897 | 18.75 | 63.1936 | 115.6402 | 27.7556 | 61.5026 | 125.7921 | 21.5705 | 56.8145 | 128.4031 | 22.3175 | 88.6018 | 29.1743 | 95.1022 | 24.6532 | 100.9556 | 1.0186 | 19.3877 | 1.267 | 0.043151 | -27.0507 | 3.0953 | 175.05 | 52.28 | 1.1018 | -0.55599 | -6.0178 | 0.71569 | 0.77095 | -15.1381 | 5.5156 | -0.01178 | -0.64625 | -0.077852 | -2.01 | -1.5179 | -0.83068 | 0.096527
42838.4245 | 369 | 22.9141 | 22.8781 | 22.8633 | 22.7808 | 22.3912 | 21.7199 | 22.7117 | 21.7765 | 22.3689 | 22.3612 | 22.3374 | 21.9858 | 21.1956 | 22.1629 | 21.6297 | 21.7908 | 21.9121 | 21.0917 | 21.1995 | 21.476 | 20.4813 | 20.836 | 22.7709 | 21.8741 | 21.8106 | 25.5217 | 126.401 | 111.2264 | 133.306 | 22.1393 | 21.848 | 24.1009 | 22.0264 | 21.9039 | 25.0997 | 51.2563 | 139.7972 |  | 79.6286 | 112.1157 | 110.6414 | 103.8375 |  | 17.1588 | 17.6538 | 16.9254 | 17.5651 | 18.0374 | 23.2876 | 85.5032 | 15.7635 | 17.0764 | 16.0168 | 18.122 | 18.4529 | 46.2328 | 47.8426 | 45.3702 | 21.6422 |  |  | 0.66063 | -0.5527 | -26.0121 | 0.27069 | 0.3944 | -161.9793 | 21.1706 | 0.58184 | -0.18925 | 0.07459 | 0.2284 | 0.00035484 | 0.0003647 | 1.1951 | 21.7781 | 21.9698 | 22.1669 | 22.2173 | 22.0394 | 21.3325 | 20.1432 | 22.1851 | 22.3573 | 22.397 | 22.3458 | 21.9579 | 21.1853 | 22.2652 | 67.4986 | 47.6401 | 48.6719 | 32.4851 | 29.32 | 43.7748 | 30.4172 | 22.3199 | 22.0868 | 21.6517 | 22.0472 | 21.7702 | 21.343 | 21.9289 | 21.6302 | 22.9835 | 46.5728 | 118.5876 | 97.7698 | 64.5072 | 0.95647 | 0.31728 | 54.6582 | 21.9084 | 22.2437 | 20.3584 | 21.5807 | 22.0325 | 21.923 | 21.9974 | 27.8858 | 21.7885 | 21.5803 | 23.7709 | 126.8486 | 159.3015 | 99.6106 | 100.8504 | 69.4233 |  | 46.8872 | 96.0257 | 50.1997 | 79.988 | 54.5561 | 55.525 |  | 63.8607 |  |  | 22.5836 | 24.934 | 49.9436 | [5 empty] | 21.8949 | 55.545 | 21.6828 | 22.0793 | 31.2495 | 21.2612 | 21.8953 | 26.7044 | 75.1222 | 162.7459 |  | 66.2112 | 119.8144 | 22.049 | 60.6461 | 134.2129 | 40.9883 | 95.8731 | 24.4416 | 96.1759 | 24.3937 | 95.4679 | 18.7554 | 63.2969 | 115.6398 | 27.7896 | 61.7839 | 125.8916 | 21.5938 | 56.9731 | 128.7991 | 22.3354 | 88.7153 | 29.2175 | 95.3109 | 24.6701 | 101.0288 | 0.9691 | 19.3837 | 1.2715 | 0.043768 | -27.1789 | 3.0953 | 171.47 | 52.01 | 1.142 | -0.88351 | -6.0611 | 0.6183 | 0.75353 | -15.2709 | 5.5208 | -0.031183 | -0.65311 | -0.052527 | -2.064 | -1.5468 | -0.83262 | 0.094307
42838.4246 | 370 | 22.9254 | 22.8855 | 22.8668 | 22.7802 | 22.394 | 21.7273 | 22.7129 | 21.7712 | 22.3693 | 22.3655 | 22.3413 | 21.9863 | 21.1956 | 22.168 | 21.629 | 21.7956 | 21.9127 | 21.0949 | 21.1975 | 21.4824 | 20.4871 | 20.8416 | 22.7882 | 21.8789 | 21.8092 | 25.5411 | 126.5026 | 111.3042 | 132.9325 | 22.1344 | 21.8449 | 24.1084 | 22.0218 | 21.9082 | 25.1125 | 51.4676 | 140.2523 |  | 79.8629 | 112.2485 | 110.8056 | 104.5678 |  | 17.1519 | 17.6625 | 16.9351 | 17.5697 | 18.0358 | 23.3685 | 85.5716 | 15.7184 | 17.0791 | 16.0001 | 18.1229 | 18.4606 | 46.172 | 47.8275 | 45.3355 | 21.6389 |  |  | 0.75197 | -0.26029 | -25.8005 | 0.51579 | 0.26889 | -160.4844 | 20.8637 | 0.78226 | 0.044657 | -0.14864 | 0.29072 | 0.0003647 | 0.00035484 | 1.1799 | 21.7785 | 21.9658 | 22.1651 | 22.2117 | 22.0325 | 21.3333 | 20.1405 | 22.1813 | 22.3484 | 22.3924 | 22.3459 | 21.9528 | 21.1888 | 22.268 | 67.6321 | 47.2262 | 48.72 | 32.7037 | 29.0463 | 43.9128 | 30.523 | 22.3303 | 22.0927 | 21.651 | 22.0621 | 21.7728 | 21.3475 | 21.9361 | 21.6282 | 23.0054 | 46.7203 | 118.7143 | 98.0222 | 65.1133 | 0.42408 | 0.31291 | 54.7634 | 21.9147 | 22.2416 | 20.3636 | 21.5832 | 22.0292 | 21.9268 | 22.0034 | 27.9291 | 21.7982 | 21.5858 | 23.7938 | 127.1994 | 159.5919 | 99.865 | 101.0967 | 68.4071 |  | 47.0273 | 96.5643 | 50.3212 | 79.4991 | 54.7466 | 55.6722 |  | 64.0264 |  |  | 22.602 | 24.9624 | 49.9401 | [5 empty] | 21.8961 | 55.5648 | 21.6851 | 22.0739 | 31.2604 | 21.2595 | 21.8964 | 26.7288 | 75.389 | 163.3951 |  | 66.381 | 119.9894 | 22.0535 | 60.89 | 134.4476 | 41.0922 | 95.9868 | 24.4582 | 96.4821 | 24.4207 | 95.6636 | 18.7738 | 63.5402 | 115.7126 | 27.8253 | 62.0379 | 125.9557 | 21.6258 | 57.0671 | 129.0231 | 22.3585 | 88.9378 | 29.242 | 95.4716 | 24.6792 | 101.1282 | 0.8975 | 19.3782 | 1.2763 | 0.043971 | -27.1423 | 3.0953 | 172.11 | 51.85 | 1.2178 | -0.60631 | -6.0365 | 0.85352 | 0.62227 | -15.2023 | 5.4814 | 0.0019782 | -0.66377 | -0.032132 | -2.0625 | -1.5397 | -0.8454 | 0.082663
42838.4246 | 371 | 22.9145 | 22.8753 | 22.8681 | 22.7762 | 22.3873 | 21.7149 | 22.7119 | 21.7725 | 22.355 | 22.3578 | 22.3335 | 21.9831 | 21.1926 | 22.1674 | 21.6238 | 21.7907 | 21.9144 | 21.0874 | 21.1923 | 21.4779 | 20.4771 | 20.836 | 22.7979 | 21.8752 | 21.8059 | 25.5599 | 126.6614 | 111.4508 | 132.7553 | 22.1361 | 21.8498 | 24.1266 | 22.0243 | 21.9076 | 25.1367 | 51.6991 | 140.9473 |  | 80.1287 | 112.3899 | 111.0382 | 105.506 |  | 17.1518 | 17.6787 | 16.9401 | 17.5769 | 18.0382 | 23.6318 | 85.844 | 15.6764 | 17.0837 | 15.8933 | 18.1294 | 18.47 | 46.1216 | 47.8272 | 45.2962 | 21.6426 |  |  | 0.6672 | -0.32403 | -26.0719 | 0.40868 | 0.37337 | -164.7122 | 20.269 | 0.63441 | 0.048549 | 0.16313 | 0.30739 | 0.00038934 | 0.00035977 | 1.1798 | 21.7775 | 21.9727 | 22.1632 | 22.22 | 22.0266 | 21.3297 | 20.1459 | 22.1743 | 22.3549 | 22.3912 | 22.3503 | 21.9525 | 21.1944 | 22.2729 | 65.8109 | 45.1912 | 47.36 | 32.5631 | 28.9318 | 43.976 | 30.6119 | 22.3289 | 22.0997 | 21.6634 | 22.0575 | 21.7852 | 21.3632 | 21.9371 | 21.6362 | 23.0247 | 46.8938 | 119.0374 | 98.2543 | 65.2962 | 0.64879 | 0.07478 | 54.9394 | 21.9162 | 22.2419 | 20.3675 | 21.5763 | 22.0364 | 21.9239 | 22.0026 | 27.9661 | 21.7856 | 21.5898 | 23.8046 | 127.3348 | 159.8897 | 100.0216 | 101.2724 | 67.6265 |  | 47.1737 | 97.3793 | 50.4657 | 79.4551 | 54.9161 | 55.7908 |  | 64.1678 |  |  | 22.6125 | 25.0023 | 49.9944 | [5 empty] | 21.8999 | 55.2669 | 21.6877 | 22.0786 | 31.2729 | 21.2598 | 21.9024 | 26.7695 | 75.6806 | 163.9209 |  | 66.7513 | 120.2558 | 22.076 | 61.0576 | 134.7735 | 41.1787 | 96.1108 | 24.4843 | 96.7655 | 24.4581 | 95.8541 | 18.7898 | 63.8504 | 115.9105 | 27.8693 | 62.1922 | 126.1485 | 21.6602 | 57.2409 | 129.2412 | 22.3877 | 89.1667 | 29.3 | 95.6133 | 24.6899 | 101.3636 | 1.0157 | 19.3724 | 1.281 | 0.043935 | -26.9748 | 3.0953 | 167.38 | 52.48 | 1.1469 | -0.67651 | -6.0684 | 0.75976 | 0.7336 | -15.4081 | 5.4051 | 0.028819 | -0.68128 | -0.024845 | -1.8526 | -1.3781 | -0.86323 | 0.08369
42838.4246 | 372 | 22.9115 | 22.8722 | 22.8611 | 22.78 | 22.3867 | 21.7203 | 22.7113 | 21.7645 | 22.3568 | 22.3669 | 22.338 | 21.9764 | 21.1897 | 22.1634 | 21.6329 | 21.7959 | 21.9114 | 21.1006 | 21.1938 | 21.488 | 20.4904 | 20.8382 | 22.8225 | 21.8742 | 21.8157 | 25.5793 | 126.7324 | 111.7022 | 132.4468 | 22.1312 | 21.8443 | 24.1384 | 22.0211 | 21.9052 | 25.1513 | 51.9095 | 141.373 |  | 80.3649 | 112.5945 | 111.265 | 105.2966 |  | 17.1521 | 17.6764 | 16.9459 | 17.5887 | 18.0362 | 23.8044 | 86.4441 | 15.6729 | 17.0889 | 15.8616 | 18.1364 | 18.4635 | 46.0734 | 47.821 | 45.2542 | 21.6416 |  |  | 0.65275 | -0.28985 | -26.5417 | 0.29303 | 0.24326 | -161.4924 | 20.3847 | 0.75861 | -0.028318 | 0.25502 | 0.21816 | 0.00038441 | 0.00033184 | 1.1836 | 21.7905 | 21.972 | 22.172 | 22.2329 | 22.0338 | 21.3368 | 20.1524 | 22.1832 | 22.3648 | 22.3966 | 22.3437 | 21.9622 | 21.1865 | 22.2636 | 64.5235 | 41.8011 | 44.5593 | 32.0606 | 28.7421 | 44.0552 | 30.6652 | 22.3293 | 22.0943 | 21.6571 | 22.0575 | 21.7698 | 21.3591 | 21.9359 | 21.6324 | 23.0311 | 47.0242 | 119.2588 | 98.3654 | 65.4969 | 1.1244 | 0.21325 | 55.1921 | 21.9127 | 22.2327 | 20.3565 | 21.5655 | 22.0253 | 21.9185 | 22.0066 | 27.9916 | 21.7801 | 21.5833 | 23.8085 | 127.5648 | 160.0226 | 100.1596 | 101.4041 | 66.8756 |  | 47.3275 | 97.2547 | 50.6243 | 79.9694 | 55.1179 | 56.1098 |  | 64.3157 |  |  | 22.6023 | 25.0038 | 50.193 | [5 empty] | 21.8932 | 55.6251 | 21.6874 | 22.0789 | 31.2757 | 21.2618 | 21.9043 | 26.7991 | 75.9666 | 163.8635 |  | 67.161 | 120.4795 | 22.0832 | 61.1065 | 135.1361 | 41.2834 | 96.2177 | 24.518 | 96.9324 | 24.4725 | 95.963 | 18.7955 | 64.0783 | 116.161 | 27.8987 | 62.3066 | 126.2432 | 21.6822 | 57.4728 | 129.3728 | 22.4173 | 89.3043 | 29.3569 | 95.7257 | 24.7102 | 101.9404 | 0.74576 | 19.3711 | 1.2853 | 0.0453 | -27.2116 | 3.0953 | 160.62 | 51.32 | 1.1339 | -0.63984 | -6.1228 | 0.64334 | 0.59231 | -15.2612 | 5.4221 | 0.055098 | -0.6722 | -0.031909 | -1.7002 | -1.0607 | -0.84993 | 0.082709
42838.4246 | 373 | 22.9155 | 22.873 | 22.8587 | 22.7799 | 22.3863 | 21.7188 | 22.7047 | 21.7689 | 22.3551 | 22.3637 | 22.3326 | 21.9793 | 21.1858 | 22.1597 | 21.6362 | 21.7963 | 21.9158 | 21.0982 | 21.2011 | 21.4794 | 20.4852 | 20.8368 | 22.835 | 21.8704 | 21.8179 | 25.6041 | 126.8397 | 112.0508 | 132.4585 | 22.1285 | 21.8438 | 24.1545 | 22.0282 | 21.9089 | 25.1741 | 52.0947 | 141.5687 |  | 80.5991 | 112.8793 | 111.4837 | 101.9719 |  | 17.1542 | 17.6723 | 16.9422 | 17.5915 | 18.0426 | 23.8609 | 87.0157 | 15.6768 | 17.0896 | 15.8908 | 18.132 | 18.4674 | 46.028 | 47.8184 | 45.2082 | 21.6407 |  |  | 0.58309 | -0.188 | -26.5318 | 0.56442 | 0.35038 | -160.2097 | 20.8065 | 0.55359 | 0.0018448 | 0.23299 | 0.13518 | 0.0003532 | 0.00034006 | 1.17 | 21.789 | 21.9692 | 22.1755 | 22.2272 | 22.0403 | 21.3285 | 20.1493 | 22.1865 | 22.3658 | 22.3954 | 22.3528 | 21.9621 | 21.1893 | 22.2655 | 66.9637 | 44.3802 | 45.084 | 31.8675 | 28.8694 | 44.2099 | 30.7306 | 22.3285 | 22.0948 | 21.6555 | 22.0548 | 21.7681 | 21.3612 | 21.9362 | 21.6361 | 23.051 | 47.1573 | 119.4926 | 98.5033 | 65.1948 | 1.2001 | 0.36807 | 55.3653 | 21.9034 | 22.2305 | 20.3576 | 21.5729 | 22.0278 | 21.9189 | 22.0142 | 28.0341 | 21.7847 | 21.5817 | 23.8271 | 127.7717 | 160.3219 | 100.2754 | 101.5247 | 67.1716 |  | 47.4523 | 97.4067 | 50.7546 | 80.7449 | 55.3088 | 56.09 |  | 64.4451 |  |  | 22.6001 | 25.0303 | 49.9631 | [5 empty] | 21.8945 | 56.1235 | 21.6828 | 22.0894 | 31.271 | 21.2587 | 21.9011 | 26.845 | 76.2636 | 163.7331 |  | 67.5267 | 120.8398 | 22.0891 | 61.2423 | 135.3627 | 41.4054 | 96.4395 | 24.5432 | 96.9647 | 24.5118 | 96.1365 | 18.7908 | 64.2679 | 116.3975 | 27.9406 | 62.5743 | 126.446 | 21.6852 | 57.7251 | 129.5343 | 22.4491 | 89.4198 | 29.4076 | 95.762 | 24.7225 | 102.2211 | 1.037 | 19.3658 | 1.2905 | 0.045256 | -27.0637 | 3.0953 | 148.89 | 52.46 | 1.0717 | -0.5153 | -6.1216 | 0.89286 | 0.71092 | -15.2019 | 5.4784 | 0.051276 | -0.6718 | -0.046613 | -1.953 | -1.1113 | -0.75099 | 0.09579
42838.4246 | 374 | 22.9181 | 22.8782 | 22.862 | 22.7818 | 22.3919 | 21.7206 | 22.7128 | 21.7774 | 22.3571 | 22.3608 | 22.3294 | 21.9868 | 21.1918 | 22.1683 | 21.6293 | 21.8 | 21.9177 | 21.0958 | 21.2058 | 21.4886 | 20.4855 | 20.8335 | 22.8478 | 21.8791 | 21.8294 | 25.6261 | 126.8559 | 112.315 | 132.2321 | 22.1249 | 21.8404 | 24.1637 | 22.0276 | 21.9019 | 25.2012 | 52.2303 | 140.9004 |  | 80.8158 | 113.1265 | 111.7316 | 99.0197 |  | 17.1639 | 17.6788 | 16.947 | 17.6037 | 18.0702 | 23.9141 | 87.2412 | 15.69 | 17.0915 | 15.8802 | 18.1443 | 18.4701 | 45.9712 | 47.8186 | 45.1551 | 21.6368 |  |  | 0.4773 | -0.29708 | -26.9642 | 0.51513 | 0.29386 | -156.748 | 20.7829 | 0.5917 | 0.1908 | 0.093892 | 0.41138 | 0.00034006 | 0.00034499 | 1.1592 | 21.795 | 21.9758 | 22.1757 | 22.2292 | 22.0409 | 21.3348 | 20.1476 | 22.1896 | 22.3592 | 22.4009 | 22.3548 | 21.9648 | 21.1899 | 22.2766 | 68.5183 | 47.1151 | 45.9941 | 32.0398 | 29.6339 | 44.371 | 30.8169 | 22.3294 | 22.0974 | 21.6544 | 22.0574 | 21.7735 | 21.3604 | 21.9391 | 21.6401 | 23.0596 | 47.282 | 119.5274 | 98.5928 | 65.4088 | 0.91951 | 0.55104 | 55.4421 | 21.9173 | 22.2344 | 20.3612 | 21.5775 | 22.0309 | 21.9187 | 22.018 | 28.0823 | 21.8026 | 21.5855 | 23.8507 | 127.8881 | 160.505 | 100.4143 | 101.6387 | 67.1517 |  | 47.5875 | 97.496 | 50.8685 | 81.3003 | 55.5041 | 55.8958 |  | 64.606 |  |  | 22.6079 | 25.0421 | 50.243 | [5 empty] | 21.8864 | 55.8404 | 21.681 | 22.0739 | 31.2813 | 21.2578 | 21.8979 | 26.876 | 76.553 | 164.1512 |  | 67.8508 | 121.1981 | 22.0983 | 61.5065 | 135.4876 | 41.4953 | 96.6455 | 24.5744 | 96.8408 | 24.5411 | 96.2408 | 18.7907 | 64.4242 | 116.7358 | 27.9706 | 62.9197 | 126.7629 | 21.6875 | 57.9469 | 129.8109 | 22.4718 | 89.5685 | 29.4338 | 95.8413 | 24.7457 | 102.4066 | 1.0364 | 19.3624 | 1.2951 | 0.044596 | -27.0797 | 3.0954 | 155.87 | 51.97 | 0.96938 | -0.64777 | -6.1713 | 0.85299 | 0.65113 | -15.0381 | 5.4758 | 0.056593 | -0.67023 | -0.055048 | -2.1067 | -1.2023 | -0.66416 | 0.094237
42838.4246 | 375 | 22.9155 | 22.8721 | 22.8618 | 22.7831 | 22.3908 | 21.7248 | 22.7121 | 21.7714 | 22.3582 | 22.3566 | 22.3329 | 21.9811 | 21.1978 | 22.1593 | 21.6134 | 21.7906 | 21.9021 | 21.0815 | 21.1882 | 21.4828 | 20.468 | 20.8305 | 22.851 | 21.8646 | 21.8095 | 25.6316 | 126.8859 | 112.4698 | 132.517 | 22.1304 | 21.8415 | 24.1844 | 22.0158 | 21.9007 | 25.2214 | 52.3595 | 140.7063 |  | 81.029 | 113.3564 | 111.8953 | 98.0106 |  | 17.1564 | 17.6838 | 16.9558 | 17.6168 | 18.1137 | 23.9492 | 87.6819 | 15.7425 | 17.0921 | 15.8133 | 18.1454 | 18.4728 | 45.917 | 47.8158 | 45.1004 | 21.6401 |  |  | 0.34259 | -0.30825 | -27.4236 | 0.23652 | 0.31358 | -160.9785 | 20.8387 | 0.59564 | 0.22349 | 0.024238 | 0.21694 | 0.00036963 | 0.00037949 | 1.1586 | 21.783 | 21.9707 | 22.1725 | 22.2267 | 22.0361 | 21.3307 | 20.1505 | 22.1859 | 22.3559 | 22.3909 | 22.3485 | 21.9667 | 21.1847 | 22.2752 | 67.7101 | 47.7976 | 46.9295 | 32.4288 | 29.6268 | 44.501 | 30.9171 | 22.323 | 22.091 | 21.6507 | 22.0556 | 21.7753 | 21.3531 | 21.9316 | 21.6412 | 23.0709 | 47.4135 | 119.4213 | 98.6732 | 65.7867 | 0.49525 | 0.4664 | 55.5749 | 21.919 | 22.2384 | 20.3679 | 21.5773 | 22.0262 | 21.9307 | 22.0283 | 28.1148 | 21.7995 | 21.5877 | 23.864 | 128.027 | 160.7839 | 100.5585 | 101.8043 | 66.4343 |  | 47.7186 | 97.5255 | 50.9689 | 81.8351 | 55.6912 | 56.1348 |  | 64.7949 |  |  | 22.6272 | 25.0812 | 50.1559 | [5 empty] | 21.8985 | 55.6102 | 21.6897 | 22.081 | 31.2861 | 21.2715 | 21.9112 | 26.9058 | 76.8637 | 164.6246 |  | 68.1423 | 121.3745 | 22.1026 | 61.7046 | 135.6883 | 41.5966 | 96.8478 | 24.601 | 96.9497 | 24.5819 | 96.3303 | 18.7781 | 64.659 | 116.9669 | 28.0028 | 63.2171 | 127.0584 | 21.713 | 58.1689 | 129.8702 | 22.4754 | 89.6464 | 29.4422 | 96.0584 | 24.7698 | 102.5849 | 1.0633 | 19.3569 | 1.2994 | 0.045147 | -27.1372 | 3.0954 | 146.19 | 51.97 | 0.82155 | -0.65985 | -6.2237 | 0.57799 | 0.67265 | -15.2406 | 5.4834 | 0.081144 | -0.66749 | -0.063199 | -2.0015 | -1.2945 | -0.63153 | 0.088373
42838.4246 | 376 | 22.9184 | 22.8823 | 22.8617 | 22.7806 | 22.3892 | 21.7229 | 22.7192 | 21.776 | 22.3556 | 22.3703 | 22.3315 | 21.9789 | 21.1954 | 22.1696 | 21.6176 | 21.7986 | 21.9109 | 21.0962 | 21.2076 | 21.4834 | 20.4891 | 20.851 | 22.88 | 21.8804 | 21.8249 | 25.6833 | 126.9404 | 112.668 | 132.3374 | 22.1344 | 21.8459 | 24.2091 | 22.0138 | 21.9065 | 25.2405 | 52.5438 | 140.8817 |  | 81.2606 | 113.5252 | 111.9726 | 99.3403 |  | 17.1454 | 17.7024 | 16.9604 | 17.6043 | 18.1163 | 24.0095 | 88.4111 | 15.7791 | 17.088 | 15.7717 | 18.1452 | 18.4745 | 45.8563 | 47.8218 | 45.0448 | 21.643 |  |  | 0.4037 | -0.30497 | -27.4038 | 0.63276 | 0.22486 | -161.1014 | 20.5095 | 0.29534 | 0.017802 | 0.048995 | 0.27406 | 0.00036306 | 0.00037291 | 1.1432 | 21.7789 | 21.9713 | 22.1616 | 22.2221 | 22.0319 | 21.32 | 20.144 | 22.175 | 22.3591 | 22.3853 | 22.3444 | 21.9645 | 21.187 | 22.2679 | 64.4365 | 44.8835 | 46.1291 | 32.8079 | 30.1116 | 44.5594 | 30.991 | 22.3246 | 22.0899 | 21.6569 | 22.0558 | 21.7731 | 21.358 | 21.9366 | 21.643 | 23.0893 | 47.5485 | 119.3868 | 98.8513 | 65.2696 | 0.66314 | 0.10673 | 55.7082 | 21.9092 | 22.2411 | 20.3721 | 21.5762 | 22.0254 | 21.9242 | 22.0347 | 28.1496 | 21.7933 | 21.5926 | 23.8817 | 128.2711 | 161.0934 | 100.6861 | 101.9325 | 66.2301 |  | 47.8675 | 98.3048 | 51.1043 | 81.8241 | 55.8777 | 57.9862 |  | 64.9854 |  |  | 22.6609 | 25.0865 | 49.8902 | [5 empty] | 21.8933 | 55.3567 | 21.6989 | 22.075 | 31.3231 | 21.2702 | 21.9045 | 26.9538 | 77.098 | 164.4531 |  | 68.2435 | 121.6152 | 22.1169 | 61.8843 | 135.6842 | 41.7441 | 97.0556 | 24.637 | 97.2135 | 24.6093 | 96.4171 | 18.7741 | 65.0412 | 117.0322 | 28.0219 | 63.3759 | 127.1287 | 21.7315 | 58.4098 | 130.1899 | 22.5029 | 89.8225 | 29.449 | 96.2459 | 24.8018 | 102.7838 | 0.76357 | 19.3537 | 1.3045 | 0.045677 | -27.1042 | 3.0954 | 156.58 | 52.45 | 0.89163 | -0.65634 | -6.2217 | 0.94541 | 0.56967 | -15.2479 | 5.4405 | 0.092069 | -0.68433 | -0.056206 | -1.6309 | -1.1969 | -0.6619 | 0.1075
42838.4246 | 377 | 22.9159 | 22.875 | 22.8586 | 22.7737 | 22.3928 | 21.7139 | 22.7077 | 21.7683 | 22.3606 | 22.3571 | 22.3276 | 21.9786 | 21.1965 | 22.1678 | 21.6265 | 21.803 | 21.9219 | 21.1007 | 21.2059 | 21.493 | 20.496 | 20.8496 | 22.8922 | 21.8785 | 21.8329 | 25.7064 | 127.1026 | 112.9019 | 132.4069 | 22.134 | 21.8512 | 24.2348 | 22.0262 | 21.9138 | 25.2785 | 52.7385 | 141.7212 |  | 81.4993 | 113.7346 | 112.1042 | 99.6553 |  | 17.1505 | 17.7053 | 16.9681 | 17.6066 | 18.125 | 24.1657 | 88.737 | 15.7641 | 17.0915 | 15.7501 | 18.1538 | 18.4772 | 45.7853 | 47.8346 | 44.9957 | 21.6458 |  |  | 0.57586 | -0.41076 | -27.1995 | 0.50593 | 0.41214 | -161.2092 | 20.7132 | 0.48722 | 0.035705 | 0.093262 | 0.060878 | 0.00040577 | 0.00033677 | 1.128 | 21.79 | 21.9709 | 22.1643 | 22.2212 | 22.0365 | 21.3236 | 20.1404 | 22.175 | 22.3563 | 22.3948 | 22.3456 | 21.9645 | 21.1871 | 22.2674 | 62.2071 | 43.2123 | 43.6399 | 32.133 | 30.0223 | 44.6175 | 31.0405 | 22.3197 | 22.0894 | 21.6561 | 22.0536 | 21.7699 | 21.3609 | 21.9374 | 21.6348 | 23.1031 | 47.688 | 119.6906 | 99.0083 | 65.229 | 0.845 | 0.27525 | 55.6014 | 21.9051 | 22.2378 | 20.3695 | 21.5732 | 22.0207 | 21.9225 | 22.0247 | 28.1841 | 21.7893 | 21.5857 | 23.8986 | 128.4199 | 161.6873 | 100.8946 | 102.0959 | 66.448 |  | 47.9913 | 99.2277 | 51.2755 | 82.2171 | 56.0896 | 58.5215 |  | 65.1369 |  |  | 22.6664 | 25.1097 | 49.5821 | [5 empty] | 21.8903 | 55.401 | 21.6868 | 22.0766 | 31.3533 | 21.2646 | 21.8923 | 26.9919 | 77.4004 | 164.6324 |  | 68.4991 | 121.7374 | 22.12 | 62.0772 | 135.9154 | 41.8576 | 97.4337 | 24.6587 | 97.5931 | 24.6373 | 96.6411 | 18.775 | 65.342 | 117.2363 | 28.0717 | 63.6267 | 127.2891 | 21.7673 | 58.611 | 130.5568 | 22.5363 | 90.1696 | 29.4889 | 96.4692 | 24.8348 | 102.9589 | 1.0743 | 19.3511 | 1.3093 | 0.045968 | -27.0203 | 3.0953 | 151.75 | 51.64 | 1.065 | -0.76173 | -6.1985 | 0.84538 | 0.77144 | -15.2571 | 5.4689 | 0.090386 | -0.70388 | -0.059521 | -1.3763 | -0.91445 | -0.66372 | 0.11355
42838.4247 | 378 | 22.917 | 22.8784 | 22.862 | 22.7733 | 22.3886 | 21.7149 | 22.7097 | 21.7649 | 22.3567 | 22.3572 | 22.3288 | 21.9797 | 21.188 | 22.161 | 21.6235 | 21.7921 | 21.9119 | 21.0895 | 21.195 | 21.4814 | 20.4859 | 20.8476 | 22.898 | 21.874 | 21.8296 | 25.7179 | 127.1714 | 113.0775 | 132.6225 | 22.1298 | 21.8452 | 24.2343 | 22.0215 | 21.9113 | 25.29 | 52.9029 | 142.4198 |  | 81.7288 | 113.9299 | 112.3125 | 100.1651 |  | 17.157 | 17.7056 | 16.9798 | 17.6127 | 18.1086 | 24.3874 | 88.5648 | 15.6889 | 17.0972 | 15.7889 | 18.1524 | 18.4833 | 45.7291 | 47.8387 | 44.9609 | 21.6388 |  |  | 0.63697 | -0.41799 | -26.9235 | 0.61042 | 0.35038 | -162.6036 | 20.129 | 0.69092 | 0.0018448 | 0.24872 | 0.35253 | 0.00036306 | 0.00035977 | 1.1084 | 21.7837 | 21.9657 | 22.1631 | 22.2206 | 22.0317 | 21.3231 | 20.1401 | 22.1825 | 22.3568 | 22.3889 | 22.339 | 21.9586 | 21.1915 | 22.2681 | 63.5961 | 44.0279 | 43.1849 | 32.3519 | 29.637 | 44.7496 | 31.1072 | 22.3203 | 22.0945 | 21.6556 | 22.057 | 21.7787 | 21.3633 | 21.94 | 21.637 | 23.1137 | 47.8391 | 119.95 | 99.2095 | 65.1674 | 1.0213 | 0.52289 | 55.8668 | 21.9168 | 22.243 | 20.3726 | 21.581 | 22.029 | 21.9294 | 22.0364 | 28.2318 | 21.7989 | 21.5999 | 23.922 | 128.5122 | 162.2941 | 101.1341 | 102.2893 | 66.0669 |  | 48.1134 | 99.662 | 51.4433 | 82.2207 | 56.3043 | 58.4164 |  | 65.2827 |  |  | 22.6885 | 25.1484 | 49.6863 | [5 empty] | 21.8996 | 55.359 | 21.6893 | 22.0852 | 31.3927 | 21.2715 | 21.9154 | 27.0473 | 77.7031 | 164.7173 |  | 68.9689 | 121.819 | 22.1454 | 62.2751 | 136.2498 | 41.9628 | 97.7085 | 24.6786 | 97.9398 | 24.6672 | 96.896 | 18.7826 | 65.5237 | 117.3906 | 28.098 | 63.8407 | 127.4208 | 21.7919 | 58.7983 | 130.8729 | 22.5601 | 90.5416 | 29.514 | 96.4809 | 24.8619 | 103.0084 | 1.2077 | 19.3473 | 1.3149 | 0.045997 | -27.111 | 3.0953 | 158.77 | 53.05 | 1.1204 | -0.76841 | -6.167 | 0.92858 | 0.71155 | -15.3286 | 5.3932 | 0.10528 | -0.70999 | -0.051918 | -1.515 | -0.85607 | -0.67202 | 0.12059
42838.4247 | 379 | 22.9175 | 22.8814 | 22.8607 | 22.7782 | 22.3884 | 21.7142 | 22.7105 | 21.7739 | 22.3619 | 22.3605 | 22.3265 | 21.9887 | 21.1998 | 22.1589 | 21.6177 | 21.7835 | 21.9059 | 21.0962 | 21.1923 | 21.4831 | 20.4781 | 20.8454 | 22.9119 | 21.8754 | 21.8273 | 25.7366 | 127.3282 | 113.1937 | 132.9274 | 22.1289 | 21.8535 | 24.253 | 22.0208 | 21.9206 | 25.3082 | 53.0751 | 142.2297 |  | 81.9612 | 114.2075 | 112.5238 | 101.174 |  | 17.1464 | 17.7151 | 16.9874 | 17.6215 | 18.1064 | 24.3965 | 88.1944 | 15.6142 | 17.0898 | 15.8594 | 18.1571 | 18.4884 | 45.6798 | 47.8579 | 44.9154 | 21.64 |  |  | 0.50227 | -0.3825 | -27.1824 | 0.47768 | 0.26035 | -159.479 | 20.6409 | 0.45699 | -0.058481 | 0.26131 | 0.078585 | 0.00036634 | 0.00033677 | 1.1047 | 21.7826 | 21.9623 | 22.1685 | 22.2227 | 22.0306 | 21.3288 | 20.1399 | 22.1772 | 22.354 | 22.3884 | 22.3432 | 21.964 | 21.1912 | 22.268 | 65.8845 | 46.5494 | 46.1873 | 32.7115 | 29.5968 | 44.9166 | 31.2001 | 22.3271 | 22.1028 | 21.6623 | 22.0583 | 21.7771 | 21.364 | 21.9446 | 21.6434 | 23.1291 | 47.9706 | 120.1452 | 99.36 | 65.1214 | 0.9435 | 0.65508 | 56.046 | 21.9131 | 22.2349 | 20.3701 | 21.5716 | 22.0246 | 21.9216 | 22.0364 | 28.2605 | 21.7883 | 21.596 | 23.9341 | 128.7206 | 162.8286 | 101.3669 | 102.4784 | 65.7571 |  | 48.2429 | 99.2849 | 51.5879 | 81.9841 | 56.5062 | 58.5593 |  | 65.4574 |  |  | 22.7081 | 25.1665 | 49.9391 | [5 empty] | 21.8909 | 55.1802 | 21.6895 | 22.0845 | 31.4202 | 21.2636 | 21.9028 | 27.095 | 77.9749 | 164.8184 |  | 69.4484 | 122.014 | 22.1677 | 62.4179 | 136.6644 | 42.017 | 97.87 | 24.6865 | 98.2359 | 24.6956 | 96.981 | 18.7785 | 65.6119 | 117.5196 | 28.1285 | 64.0496 | 127.5388 | 21.8252 | 59.0085 | 131.1735 | 22.5772 | 90.8374 | 29.5341 | 96.5269 | 24.8927 | 103.2469 | 1.1012 | 19.3454 | 1.3199 | 0.046149 | -27.1292 | 3.0953 | 182.91 | 51.68 | 0.99526 | -0.73507 | -6.1966 | 0.82145 | 0.61337 | -15.1809 | 5.4615 | 0.11846 | -0.69437 | -0.038101 | -1.7495 | -1.1788 | -0.69391 | 0.1265
42838.4247 | 380 | 22.9198 | 22.8804 | 22.8652 | 22.782 | 22.3957 | 21.7196 | 22.713 | 21.7766 | 22.3623 | 22.3623 | 22.3306 | 21.9914 | 21.203 | 22.1643 | 21.6235 | 21.783 | 21.9073 | 21.0942 | 21.1923 | 21.4832 | 20.4763 | 20.8404 | 22.9309 | 21.8764 | 21.826 | 25.7602 | 127.4811 | 113.2026 | 133.496 | 22.1343 | 21.8558 | 24.2737 | 22.0218 | 21.9227 | 25.3411 | 53.2357 | 142.3982 |  | 82.1867 | 114.4589 | 112.6857 | 100.8754 |  | 17.1543 | 17.7293 | 16.9996 | 17.6467 | 18.1377 | 24.4607 | 88.6818 | 15.6182 | 17.0955 | 15.9244 | 18.1669 | 18.4932 | 45.6404 | 47.8759 | 44.8827 | 21.6388 |  |  | 0.66983 | -0.46464 | -27.4052 | 0.50265 | 0.28138 | -161.1743 | 20.589 | 0.55556 | -0.10149 | -0.079403 | 0.30496 | 0.00035156 | 0.00034499 | 1.1081 | 21.7793 | 21.966 | 22.1666 | 22.2144 | 22.0343 | 21.3182 | 20.1409 | 22.1794 | 22.3516 | 22.3921 | 22.3346 | 21.9562 | 21.1805 | 22.2694 | 67.3625 | 46.647 | 48.0584 | 32.9625 | 29.5276 | 45.0838 | 31.3011 | 22.3304 | 22.0979 | 21.6628 | 22.0529 | 21.7741 | 21.367 | 21.9373 | 21.6434 | 23.1486 | 48.1325 | 120.4034 | 99.5813 | 65.0787 | 1.0595 | 0.74523 | 56.1292 | 21.9097 | 22.2268 | 20.3655 | 21.5704 | 22.0252 | 21.9175 | 22.0375 | 28.3012 | 21.7836 | 21.5909 | 23.9481 | 129.0239 | 163.2094 | 101.598 | 102.6943 | 65.82 |  | 48.3586 | 99.4651 | 51.6924 | 82.5863 | 56.6899 | 58.3332 |  | 65.5984 |  |  | 22.7279 | 25.181 | 49.8824 | [5 empty] | 21.8828 | 55.0037 | 21.6847 | 22.0838 | 31.4731 | 21.2562 | 21.8987 | 27.1353 | 78.1725 | 164.668 |  | 69.7742 | 122.2246 | 22.197 | 62.45 | 137.1788 | 42.1033 | 98.2298 | 24.6972 | 98.3338 | 24.7243 | 97.0648 | 18.7593 | 65.6735 | 117.6528 | 28.159 | 64.2645 | 127.6258 | 21.857 | 59.2189 | 131.3569 | 22.576 | 91.0346 | 29.5631 | 96.6909 | 24.9215 | 103.4699 | 0.9691 | 19.3393 | 1.3247 | 0.046164 | -27.1488 | 3.0953 | 186.77 | 52.06 | 1.1502 | -0.81018 | -6.2221 | 0.84267 | 0.63773 | -15.263 | 5.4552 | 0.12079 | -0.69566 | -0.048231 | -1.8939 | -1.3748 | -0.67988 | 0.1334
42838.4247 | 381 | 22.9146 | 22.8713 | 22.852 | 22.7713 | 22.3831 | 21.717 | 22.7085 | 21.7684 | 22.3567 | 22.3564 | 22.3186 | 21.9786 | 21.1968 | 22.156 | 21.6239 | 21.7925 | 21.91 | 21.0966 | 21.1934 | 21.4869 | 20.4815 | 20.844 | 22.9482 | 21.8774 | 21.8319 | 25.7797 | 127.6398 | 113.2042 | 133.5619 | 22.1327 | 21.8528 | 24.2988 | 22.0257 | 21.9227 | 25.3693 | 53.3654 | 142.7845 |  | 82.4135 | 114.7379 | 112.8722 | 99.5967 |  | 17.1627 | 17.7351 | 17.013 | 17.6734 | 18.2211 | 24.4534 | 89.3851 | 15.622 | 17.0988 | 15.9033 | 18.1752 | 18.4874 | 45.5909 | 47.8951 | 44.8605 | 21.6366 |  |  | 0.81768 | -0.38448 | -27.6391 | 0.53945 | 0.26035 | -159.7536 | 20.771 | 0.70275 | 0.1044 | -0.004924 | 0.30496 | 0.00035813 | 0.00031377 | 1.1004 | 21.7889 | 21.9589 | 22.1603 | 22.2074 | 22.0329 | 21.3217 | 20.1376 | 22.1785 | 22.3506 | 22.3862 | 22.3349 | 21.9518 | 21.1793 | 22.2683 | 68.2665 | 46.3071 | 49.2733 | 33.5952 | 29.3977 | 45.2164 | 31.4187 | 22.3226 | 22.0978 | 21.6617 | 22.0567 | 21.7709 | 21.368 | 21.9361 | 21.6454 | 23.1636 | 48.3005 | 120.411 | 99.7449 | 66.012 | 0.72783 | 0.35551 | 56.2816 | 21.912 | 22.2335 | 20.3622 | 21.576 | 22.0237 | 21.9181 | 22.0359 | 28.3414 | 21.788 | 21.5943 | 23.9694 | 129.1961 | 163.4288 | 101.842 | 102.9141 | 67.053 |  | 48.4804 | 99.9372 | 51.7986 | 82.9988 | 56.871 | 57.8454 |  | 65.748 |  |  | 22.7488 | 25.2082 | 50.372 | [5 empty] | 21.898 | 54.7554 | 21.6918 | 22.0853 | 31.5358 | 21.2639 | 21.9027 | 27.1804 | 78.378 | 164.7727 |  | 69.989 | 122.4357 | 22.2247 | 62.4315 | 137.3902 | 42.2219 | 98.6924 | 24.707 | 98.4101 | 24.7616 | 97.0866 | 18.7602 | 65.7519 | 117.9223 | 28.2003 | 64.4899 | 127.7519 | 21.8786 | 59.3902 | 131.4679 | 22.5811 | 91.2425 | 29.6076 | 96.8476 | 24.9556 | 103.6267 | 1.053 | 19.3367 | 1.3298 | 0.046556 | -27.1573 | 3.0953 | 167.69 | 52.21 | 1.2709 | -0.73699 | -6.2487 | 0.87298 | 0.61343 | -15.1954 | 5.4792 | 0.090848 | -0.705 | -0.053183 | -1.9786 | -1.496 | -0.63974 | 0.11341
42838.4247 | 382 | 22.9188 | 22.8722 | 22.8549 | 22.7746 | 22.3876 | 21.7168 | 22.7092 | 21.7668 | 22.3538 | 22.357 | 22.3254 | 21.9759 | 21.192 | 22.1626 | 21.6209 | 21.7971 | 21.91 | 21.0932 | 21.1977 | 21.4899 | 20.4814 | 20.8453 | 22.9594 | 21.8765 | 21.8428 | 25.8094 | 127.755 | 113.3232 | 133.3991 | 22.1386 | 21.8522 | 24.3185 | 22.0286 | 21.9223 | 25.3935 | 53.4992 | 142.318 |  | 82.6576 | 115.0397 | 113.0965 | 99.0524 |  | 17.1647 | 17.7341 | 17.0087 | 17.6683 | 18.2222 | 24.473 | 89.4675 | 15.6256 | 17.0872 | 15.8606 | 18.1753 | 18.492 | 45.5486 | 47.924 | 44.8304 | 21.639 |  |  | 0.79468 | -0.25634 | -27.6956 | 0.44548 | 0.17032 | -161.539 | 20.5134 | 0.64887 | 0.088247 | -0.10017 | 0.27753 | 0.00032199 | 0.00034827 | 1.0929 | 21.79 | 21.9652 | 22.1684 | 22.2197 | 22.0361 | 21.3275 | 20.1425 | 22.1808 | 22.3608 | 22.3919 | 22.3454 | 21.9627 | 21.1912 | 22.2707 | 67.8371 | 44.8648 | 48.0205 | 33.6925 | 28.946 | 45.3293 | 31.5052 | 22.33 | 22.1012 | 21.6595 | 22.0633 | 21.7693 | 21.3732 | 21.9363 | 21.6383 | 23.1739 | 48.4517 | 120.351 | 99.8626 | 66.1281 | 0.64427 | 0.3072 | 56.5219 | 21.9012 | 22.2327 | 20.3673 | 21.5647 | 22.0247 | 21.9156 | 22.0365 | 28.376 | 21.7882 | 21.5925 | 23.9748 | 129.3445 | 163.8635 | 102.065 | 103.1162 | 67.4463 |  | 48.64 | 99.8728 | 51.9296 | 82.6803 | 57.0793 | 57.603 |  | 65.9507 |  |  | 22.76 | 25.2258 | 50.799 | [5 empty] | 21.9018 | 54.7 | 21.6973 | 22.0883 | 31.5585 | 21.2635 | 21.9113 | 27.2228 | 78.6354 | 165.0441 |  | 70.2002 | 122.6537 | 22.2488 | 62.517 | 137.5941 | 42.3209 | 98.812 | 24.7119 | 98.6435 | 24.7895 | 97.5379 | 18.7713 | 65.8234 | 118.2059 | 28.2296 | 64.7087 | 127.8377 | 21.8899 | 59.5345 | 131.7023 | 22.6009 | 91.4047 | 29.6399 | 96.9519 | 24.9821 | 103.8496 | 1.0309 | 19.3303 | 1.3342 | 0.046534 | -27.1405 | 3.0953 | 173.07 | 51.82 | 1.2526 | -0.60178 | -6.2551 | 0.79331 | 0.49618 | -15.2806 | 5.4453 | 0.085562 | -0.69855 | -0.036851 | -1.9176 | -1.3466 | -0.61985 | 0.11553
42838.4247 | 383 | 22.926 | 22.8757 | 22.8688 | 22.7784 | 22.3926 | 21.7198 | 22.7147 | 21.7738 | 22.3606 | 22.36 | 22.333 | 21.9873 | 21.2015 | 22.1665 | 21.6229 | 21.7951 | 21.9095 | 21.0895 | 21.1956 | 21.4914 | 20.4835 | 20.8545 | 22.9768 | 21.8783 | 21.8447 | 25.834 | 127.8457 | 113.5182 | 133.3435 | 22.1336 | 21.8583 | 24.3216 | 22.0213 | 21.9262 | 25.4087 | 53.6597 | 141.9181 |  | 82.8859 | 115.2534 | 113.2722 | 98.8081 |  | 17.1715 | 17.7342 | 17.0139 | 17.6656 | 18.2202 | 24.4521 | 89.5677 | 15.6254 | 17.0875 | 15.8495 | 18.1734 | 18.4854 | 45.4931 | 47.9491 | 44.8028 | 21.6305 |  |  | 0.67115 | -0.5021 | -27.3677 | 0.53945 | 0.31949 | -162.4347 | 20.3958 | 0.7297 | 0.064506 | 0.035987 | 0.31294 | 0.0003532 | 0.00032527 | 1.086 | 21.7882 | 21.9677 | 22.1605 | 22.2205 | 22.0288 | 21.3245 | 20.1421 | 22.1764 | 22.3563 | 22.3942 | 22.3428 | 21.9581 | 21.1858 | 22.2683 | 66.5123 | 42.4796 | 45.7793 | 33.7457 | 28.8848 | 45.4132 | 31.554 | 22.3298 | 22.0965 | 21.6562 | 22.0573 | 21.7757 | 21.367 | 21.9347 | 21.6354 | 23.1917 | 48.6055 | 120.4939 | 100.1078 | 66.2672 | 0.8334 | -0.012332 | 56.7842 | 21.9074 | 22.2294 | 20.3776 | 21.5688 | 22.0253 | 21.9229 | 22.0541 | 28.4223 | 21.7911 | 21.6037 | 24.0042 | 129.3995 | 164.2243 | 102.296 | 103.3511 | 68.2197 |  | 48.771 | 100.4985 | 52.0595 | 83.6973 | 57.3724 | 57.541 |  | 66.128 |  |  | 22.764 | 25.2464 | 50.7173 | [5 empty] | 21.8925 | 55.4797 | 21.6848 | 22.0803 | 31.5428 | 21.2597 | 21.9 | 27.2744 | 78.9252 | 165.0103 |  | 70.4744 | 122.9191 | 22.2647 | 62.7087 | 137.8364 | 42.3759 | 98.9683 | 24.7297 | 98.9441 | 24.8126 | 98.1099 | 18.7671 | 66.1168 | 118.4346 | 28.2624 | 64.9288 | 127.907 | 21.909 | 59.7046 | 131.8905 | 22.6055 | 91.521 | 29.6921 | 97.0509 | 25.0079 | 104.0216 | 0.9513 | 19.3265 | 1.338 | 0.047158 | -27.1207 | 3.0953 | 162.75 | 52.91 | 1.1511 | -0.84221 | -6.2179 | 0.87298 | 0.67954 | -15.3223 | 5.4294 | 0.068705 | -0.71131 | -0.054563 | -1.7604 | -1.0918 | -0.60733 | 0.11709
42838.4247 | 384 | 22.9157 | 22.8835 | 22.8644 | 22.7776 | 22.3926 | 21.7339 | 22.7201 | 21.7753 | 22.364 | 22.3646 | 22.3387 | 21.9832 | 21.1981 | 22.1695 | 21.6142 | 21.7855 | 21.9077 | 21.0865 | 21.191 | 21.4946 | 20.476 | 20.854 | 22.9897 | 21.8734 | 21.8349 | 25.8461 | 127.9487 | 113.6143 | 134.0548 | 22.1259 | 21.86 | 24.3493 | 22.0244 | 21.924 | 25.4335 | 53.8143 | 141.9622 |  | 83.1626 | 115.4079 | 113.493 | 99.6404 |  | 17.1862 | 17.7447 | 17.0251 | 17.6741 | 18.2085 | 24.6195 | 89.9341 | 15.6368 | 17.0938 | 15.7774 | 18.1822 | 18.4792 | 45.4499 | 47.9749 | 44.7949 | 21.6391 |  |  | 0.58703 | -0.44559 | -27.2061 | 0.44088 | 0.21041 | -159.6774 | 20.2407 | 0.63836 | -0.079693 | 0.059485 | 0.20323 | 0.00035977 | 0.00034499 | 1.0827 | 21.7952 | 21.9684 | 22.1641 | 22.216 | 22.0345 | 21.3296 | 20.1418 | 22.1804 | 22.3538 | 22.4017 | 22.3448 | 21.9601 | 21.1859 | 22.2693 | 65.2906 | 41.4626 | 44.0773 | 33.5005 | 29.2364 | 45.4769 | 31.5832 | 22.3204 | 22.0885 | 21.6563 | 22.0519 | 21.7798 | 21.3642 | 21.9407 | 21.64 | 23.2013 | 48.769 | 120.8561 | 100.4108 | 66.58 | 0.7467 | 0.066601 | 56.9341 | 21.9132 | 22.2407 | 20.3797 | 21.5796 | 22.029 | 21.93 | 22.0555 | 28.4655 | 21.7978 | 21.6112 | 24.0279 | 129.4402 | 164.874 | 102.5698 | 103.6318 | 68.3407 |  | 48.8936 | 101.2425 | 52.1746 | 84.5626 | 57.6289 | 57.5738 |  | 66.2933 |  |  | 22.7758 | 25.2717 | 51.1808 | [5 empty] | 21.8959 | 56.3022 | 21.6855 | 22.0824 | 31.5475 | 21.2638 | 21.9051 | 27.3128 | 79.2018 | 165.1288 |  | 70.6646 | 123.084 | 22.2859 | 62.8941 | 137.8629 | 42.4533 | 99.1317 | 24.7488 | 99.2141 | 24.8341 | 98.2706 | 18.7682 | 66.5514 | 118.5995 | 28.3123 | 65.147 | 128.1248 | 21.9266 | 59.8644 | 132.0027 | 22.6089 | 91.6886 | 29.7634 | 97.1913 | 25.0494 | 104.167 | 0.8413 | 19.3235 | 1.3428 | 0.047354 | -27.1933 | 3.0953 | 144.53 | 51.24 | 1.0775 | -0.79342 | -6.1997 | 0.78922 | 0.55162 | -15.196 | 5.4103 | 0.069678 | -0.72789 | -0.069372 | -1.6171 | -0.8993 | -0.62493 | 0.11418
42838.4247 | 385 | 22.9088 | 22.8686 | 22.8532 | 22.77 | 22.3858 | 21.7095 | 22.6992 | 21.7663 | 22.3493 | 22.3515 | 22.3301 | 21.9829 | 21.1835 | 22.153 | 21.624 | 21.7868 | 21.9049 | 21.0856 | 21.187 | 21.4915 | 20.478 | 20.8484 | 23.0059 | 21.8763 | 21.8394 | 25.8627 | 128.1023 | 113.7912 | 134.0976 | 22.1257 | 21.8592 | 24.3617 | 22.0259 | 21.9241 | 25.4639 | 53.99 | 142.2206 |  | 83.4322 | 115.6826 | 113.6822 | 100.9925 |  | 17.1844 | 17.7481 | 17.0301 | 17.6726 | 18.2037 | 24.86 | 90.5234 | 15.5783 | 17.0878 | 15.7898 | 18.1812 | 18.4893 | 45.4056 | 48.0037 | 44.777 | 21.6356 |  |  | 0.6764 | -0.19391 | -26.9879 | 0.3364 | 0.25049 | -157.3808 | 20.3498 | 0.5181 | 0.1114 | 0.072492 | 0.24663 | 0.00032199 | 0.0003072 | 1.0946 | 21.7918 | 21.9702 | 22.1722 | 22.2176 | 22.04 | 21.3297 | 20.139 | 22.1838 | 22.3567 | 22.4011 | 22.3526 | 21.9592 | 21.1907 | 22.2684 | 64.5457 | 40.3356 | 42.6697 | 33.0559 | 29.3759 | 45.545 | 31.6124 | 22.3208 | 22.0839 | 21.6484 | 22.046 | 21.7715 | 21.3658 | 21.9385 | 21.6395 | 23.214 | 48.9298 | 121.2225 | 100.6852 | 66.4354 | 0.75437 | -0.0079574 | 57.004 | 21.9097 | 22.2416 | 20.3837 | 21.578 | 22.032 | 21.9291 | 22.0537 | 28.5044 | 21.8038 | 21.6078 | 24.0409 | 129.5761 | 165.2317 | 102.8833 | 103.9155 | 68.3196 |  | 49.053 | 101.5666 | 52.351 | 84.17 | 57.8452 | 58.1362 |  | 66.4748 |  |  | 22.7972 | 25.2821 | 51.5238 | [5 empty] | 21.8972 | 56.3675 | 21.6987 | 22.0943 | 31.587 | 21.2604 | 21.909 | 27.3554 | 79.4466 | 165.2277 |  | 70.8565 | 123.3591 | 22.3074 | 63.0546 | 137.7936 | 42.5622 | 99.2914 | 24.7802 | 99.4362 | 24.8681 | 98.3969 | 18.77 | 66.8429 | 118.8683 | 28.3504 | 65.3226 | 128.448 | 21.9297 | 59.9651 | 132.2139 | 22.6024 | 91.8789 | 29.8185 | 97.3948 | 25.0801 | 104.2626 | 0.60515 | 19.3205 | 1.347 | 0.047492 | -27.1591 | 3.0953 | 119.93 | 52.34 | 1.1566 | -0.52341 | -6.1748 | 0.68939 | 0.60211 | -15.0924 | 5.427 | 0.075901 | -0.73061 | -0.05068 | -1.5263 | -0.73946 | -0.65622 | 0.12388
42838.4247 | 386 | 22.9057 | 22.873 | 22.8616 | 22.775 | 22.3821 | 21.7074 | 22.6984 | 21.7642 | 22.3543 | 22.3576 | 22.3289 | 21.9746 | 21.1896 | 22.1538 | 21.6198 | 21.7871 | 21.9083 | 21.0937 | 21.1965 | 21.4961 | 20.4779 | 20.8515 | 23.0117 | 21.8768 | 21.847 | 25.8982 | 128.363 | 113.9317 | 134.6735 | 22.124 | 21.8556 | 24.374 | 22.0222 | 21.9287 | 25.4827 | 54.1659 | 143.7311 |  | 83.6865 | 115.9518 | 113.8435 | 101.544 |  | 17.1958 | 17.7677 | 17.0274 | 17.6814 | 18.1994 | 25.0979 | 90.8008 | 15.522 | 17.0884 | 15.8237 | 18.195 | 18.4866 | 45.357 | 48.0267 | 44.7657 | 21.6382 |  |  | 0.90048 | -0.47122 | -27.0589 | 0.62422 | 0.30043 | -158.4381 | 20.6258 | 0.7021 | -0.028318 | 0.065569 | 0.31138 | 0.00031213 | 0.00034334 | 1.0843 | 21.7903 | 21.962 | 22.1745 | 22.2252 | 22.0302 | 21.3276 | 20.1443 | 22.1826 | 22.3581 | 22.3894 | 22.3489 | 21.9581 | 21.1913 | 22.2707 | 62.7225 | 39.7983 | 41.4856 | 31.5622 | 28.6308 | 45.6012 | 31.6429 | 22.3289 | 22.0864 | 21.6476 | 22.0481 | 21.7754 | 21.3639 | 21.9328 | 21.6336 | 23.2301 | 49.0685 | 121.7463 | 101.2827 | 66.4525 | 0.67612 | -0.14338 | 57.0374 | 21.9033 | 22.2355 | 20.3839 | 21.5801 | 22.032 | 21.93 | 22.0561 | 28.5387 | 21.7954 | 21.6005 | 24.0594 | 129.9475 | 165.203 | 103.1475 | 104.165 | 68.4408 |  | 49.1918 | 101.0863 | 52.4846 | 85.98 | 58.0982 | 58.0032 |  | 66.6626 |  |  | 22.788 | 25.2818 | 51.4213 | [5 empty] | 21.9011 | 57.7077 | 21.6998 | 22.0926 | 31.6357 | 21.2657 | 21.9086 | 27.3966 | 79.6919 | 165.3359 |  | 71.1094 | 123.6991 | 22.3368 | 63.2651 | 138.0929 | 42.6656 | 99.4625 | 24.8005 | 99.5142 | 24.9025 | 98.5715 | 18.7877 | 67.1405 | 119.1798 | 28.3928 | 65.4938 | 128.6321 | 21.9637 | 60.1329 | 132.517 | 22.6248 | 91.9982 | 29.8764 | 97.5464 | 25.1121 | 104.3524 | 0.799 | 19.3176 | 1.3505 | 0.048008 | -27.1041 | 3.0953 | 126.32 | 52.03 | 1.3355 | -0.81595 | -6.1831 | 0.93912 | 0.65967 | -15.1491 | 5.4659 | 0.077443 | -0.71251 | -0.091847 | -1.317 | -0.6043 | -0.66525 | 0.12831
42838.4248 | 387 | 22.9085 | 22.8686 | 22.8503 | 22.7755 | 22.3841 | 21.7069 | 22.6987 | 21.7616 | 22.3522 | 22.3582 | 22.327 | 21.9778 | 21.1843 | 22.159 | 21.6335 | 21.795 | 21.9143 | 21.0891 | 21.1993 | 21.4986 | 20.4865 | 20.8688 | 23.0308 | 21.8825 | 21.8631 | 25.9291 | 128.8424 | 114.1783 | 135.3951 | 22.1204 | 21.8574 | 24.393 | 22.0171 | 21.9276 | 25.5025 | 54.327 | 145.464 |  | 83.9796 | 116.1557 | 113.9984 | 101.8463 |  | 17.1993 | 17.7651 | 17.0279 | 17.6906 | 18.2019 | 25.2351 | 90.5242 | 15.4619 | 17.0863 | 15.7996 | 18.1881 | 18.4821 | 45.3241 | 48.0558 | 44.7466 | 21.6389 |  |  | 0.59623 | -0.26357 | -27.0155 | 0.60253 | 0.24786 | -158.8856 | 20.633 | 0.69815 | -0.055951 | 0.15746 | 0.25062 | 0.0003302 | 0.00033349 | 1.0617 | 21.7799 | 21.9573 | 22.1698 | 22.2225 | 22.0312 | 21.3209 | 20.1382 | 22.1856 | 22.3482 | 22.3973 | 22.3434 | 21.9625 | 21.1885 | 22.2656 | 61.1375 | 39.4187 | 40.8338 | 30.8722 | 27.958 | 45.6421 | 31.6518 | 22.3226 | 22.0829 | 21.649 | 22.05 | 21.7683 | 21.3643 | 21.9286 | 21.6372 | 23.2405 | 49.1953 | 122.3169 | 101.6681 | 66.3698 | 0.76341 | 0.091137 | 57.2859 | 21.9116 | 22.232 | 20.382 | 21.579 | 22.0279 | 21.9325 | 22.0622 | 28.5838 | 21.7931 | 21.6057 | 24.079 | 130.1875 | 165.2627 | 103.3233 | 104.3794 | 68.0406 |  | 49.3117 | 100.1642 | 52.6046 | 86.92 | 58.3207 | 57.9864 |  | 66.8397 |  |  | 22.783 | 25.3067 | 51.45 | [5 empty] | 21.9009 | 58.4226 | 21.6897 | 22.0924 | 31.6851 | 21.2679 | 21.9057 | 27.4435 | 79.9388 | 165.4026 |  | 71.2931 | 123.9016 | 22.3383 | 63.5055 | 138.4884 | 42.7662 | 99.5858 | 24.802 | 99.7676 | 24.9181 | 98.754 | 18.7682 | 67.4234 | 119.4417 | 28.4258 | 65.6898 | 128.9213 | 21.9931 | 60.3765 | 132.6119 | 22.6505 | 92.1267 | 29.9334 | 97.6532 | 25.148 | 104.4637 | 0.90177 | 19.3137 | 1.3543 | 0.048189 | -27.0928 | 3.0953 | 135.93 | 51.34 | 1.0877 | -0.61024 | -6.1781 | 0.92266 | 0.59932 | -15.1739 | 5.4681 | 0.092805 | -0.68262 | -0.10994 | -1.1361 | -0.53084 | -0.66789 | 0.1351
42838.4248 | 388 | 22.9078 | 22.8725 | 22.8433 | 22.7727 | 22.3868 | 21.7161 | 22.6948 | 21.7632 | 22.3515 | 22.355 | 22.3282 | 21.9805 | 21.1874 | 22.1617 | 21.6187 | 21.787 | 21.9027 | 21.0968 | 21.2022 | 21.497 | 20.4827 | 20.8631 | 23.0521 | 21.8767 | 21.8484 | 25.9401 | 129.0809 | 114.359 | 135.3612 | 22.1202 | 21.8554 | 24.4067 | 22.0164 | 21.9264 | 25.5274 | 54.4839 | 145.9243 |  | 84.2498 | 116.2729 | 114.1288 | 101.7349 |  | 17.2005 | 17.7695 | 17.0437 | 17.6932 | 18.2087 | 25.3906 | 90.31 | 15.4344 | 17.0966 | 15.7692 | 18.1951 | 18.4916 | 45.2881 | 48.0754 | 44.7184 | 21.6382 |  |  | 0.89785 | -0.34637 | -26.8506 | 0.24835 | 0.059272 | -159.1839 | 20.8216 | 0.8368 | -0.055368 | 0.082982 | 0.1232 | 0.00034499 | 0.00037456 | 1.0606 | 21.7866 | 21.9629 | 22.1642 | 22.2131 | 22.0276 | 21.3291 | 20.1342 | 22.1792 | 22.3558 | 22.3833 | 22.343 | 21.9599 | 21.1855 | 22.2678 | 61.6635 | 40.4187 | 41.325 | 30.8582 | 27.7687 | 45.711 | 31.6788 | 22.3237 | 22.0872 | 21.6541 | 22.0555 | 21.7726 | 21.3748 | 21.9291 | 21.6423 | 23.2539 | 49.3333 | 122.7256 | 101.8304 | 66.3208 | 1.0674 | 0.22466 | 57.1162 | 21.9165 | 22.2376 | 20.3894 | 21.5805 | 22.031 | 21.9322 | 22.0707 | 28.628 | 21.7982 | 21.6122 | 24.0998 | 130.3957 | 165.7271 | 103.4408 | 104.5006 | 68.1674 |  | 49.4198 | 99.0721 | 52.7205 | 86.3224 | 58.5322 | 58.2133 |  | 66.993 |  |  | 22.765 | 25.3216 | 51.4995 | [5 empty] | 21.8985 | 58.2831 | 21.6934 | 22.0798 | 31.7234 | 21.2645 | 21.9097 | 27.4815 | 80.1724 | 165.8464 |  | 71.4155 | 124.1994 | 22.3641 | 63.8492 | 138.8341 | 42.91 | 99.6855 | 24.8483 | 100.174 | 24.9377 | 98.9337 | 18.7616 | 67.5261 | 119.7597 | 28.4824 | 65.9126 | 129.3411 | 22.0231 | 60.6103 | 132.7531 | 22.6511 | 92.2806 | 29.9831 | 97.7692 | 25.1741 | 104.7593 | 0.94091 | 19.3092 | 1.3581 | 0.048334 | -27.1136 | 3.0953 | 149.94 | 52.98 | 1.3347 | -0.69955 | -6.1593 | 0.59235 | 0.29315 | -15.1921 | 5.4945 | 0.093107 | -0.64816 | -0.085719 | -1.1864 | -0.58224 | -0.65919 | 0.14134
42838.4248 | 389 | 22.9037 | 22.8693 | 22.8536 | 22.7723 | 22.3916 | 21.7085 | 22.7061 | 21.7686 | 22.3511 | 22.3561 | 22.3286 | 21.9776 | 21.1902 | 22.1595 | 21.6248 | 21.7967 | 21.923 | 21.0984 | 21.201 | 21.4994 | 20.4872 | 20.8711 | 23.0704 | 21.8808 | 21.8572 | 25.9712 | 129.1535 | 114.5537 | 135.2583 | 22.1206 | 21.8605 | 24.4275 | 22.0247 | 21.9374 | 25.5591 | 54.6447 | 144.9746 |  | 84.4699 | 116.4064 | 114.2466 | 102.6014 |  | 17.2033 | 17.7697 | 17.022 | 17.6914 | 18.194 | 25.4082 | 90.7924 | 15.4262 | 17.0937 | 15.7371 | 18.2022 | 18.4887 | 45.2537 | 48.0961 | 44.7039 | 21.6354 |  |  | 0.89522 | -0.54218 | -26.5726 | 0.34231 | 0.1079 | -160.4114 | 20.9307 | 0.68764 | 0.16784 | 0.28754 | 0.18431 | 0.00034499 | 0.0003302 | 1.0442 | 21.7935 | 21.9734 | 22.166 | 22.2268 | 22.0397 | 21.3286 | 20.1419 | 22.1833 | 22.3631 | 22.3948 | 22.3417 | 21.962 | 21.1899 | 22.2747 | 63.4119 | 42.7342 | 43.6089 | 30.999 | 28.0503 | 45.7993 | 31.7437 | 22.3148 | 22.089 | 21.6507 | 22.0441 | 21.7662 | 21.3689 | 21.931 | 21.6386 | 23.2726 | 49.4658 | 122.9324 | 101.9525 | 66.3257 | 0.79723 | 0.52346 | 56.8599 | 21.916 | 22.2374 | 20.3975 | 21.5811 | 22.0305 | 21.9312 | 22.0737 | 28.6602 | 21.7986 | 21.6096 | 24.116 | 130.7496 | 166.2282 | 103.6425 | 104.6223 | 67.829 |  | 49.5633 | 97.8502 | 52.8529 | 86.1769 | 58.8777 | 57.966 |  | 67.161 |  |  | 22.7674 | 25.3383 | 51.4777 | [5 empty] | 21.885 | 59.5394 | 21.6797 | 22.0752 | 31.7531 | 21.2575 | 21.8998 | 27.527 | 80.4241 | 165.9081 |  | 71.7798 | 124.5377 | 22.4017 | 64.2086 | 138.9488 | 42.9826 | 99.8486 | 24.8732 | 100.6951 | 24.9605 | 99.1275 | 18.7575 | 67.5314 | 120.0578 | 28.5256 | 66.1616 | 129.4749 | 22.0632 | 60.8291 | 132.8598 | 22.6564 | 92.5392 | 30.0539 | 97.8772 | 25.2113 | 105.1942 | 0.8706 | 19.3084 | 1.362 | 0.048443 | -27.1655 | 3.0953 | 149.48 | 51.45 | 1.3325 | -0.87524 | -6.1273 | 0.69545 | 0.39554 | -15.251 | 5.509 | 0.10759 | -0.6095 | -0.069216 | -1.3702 | -0.82839 | -0.67751 | 0.14589
42838.4248 | 390 | 22.9109 | 22.8769 | 22.8509 | 22.7772 | 22.3875 | 21.7104 | 22.7142 | 21.7664 | 22.3613 | 22.3567 | 22.322 | 21.9806 | 21.1943 | 22.1589 | 21.6175 | 21.7861 | 21.9067 | 21.089 | 21.1929 | 21.497 | 20.4778 | 20.8667 | 23.0848 | 21.8759 | 21.8602 | 25.9904 | 129.4685 | 114.7572 | 135.5149 | 22.1239 | 21.8655 | 24.4482 | 22.0186 | 21.9364 | 25.5813 | 54.8408 | 144.7524 |  | 84.6927 | 116.6076 | 114.3698 | 103.8438 |  | 17.2117 | 17.7763 | 17.0226 | 17.6871 | 18.1848 | 25.4391 | 90.9072 | 15.4549 | 17.0919 | 15.6846 | 18.2056 | 18.4935 | 45.2193 | 48.1153 | 44.6742 | 21.6322 |  |  | 0.49504 | -0.34834 | -26.2079 | 0.55851 | 0.34183 | -158.2291 | 20.7664 | 0.50365 | 0.089026 | 0.052561 | 0.20844 | 0.00038441 | 0.00036306 | 1.027 | 21.7959 | 21.9659 | 22.1636 | 22.2216 | 22.0352 | 21.32 | 20.1428 | 22.1826 | 22.3561 | 22.395 | 22.3409 | 21.9591 | 21.1868 | 22.2651 | 64.4669 | 44.3875 | 45.6809 | 31.8131 | 28.2124 | 45.8984 | 31.8413 | 22.3182 | 22.0881 | 21.6503 | 22.0454 | 21.7723 | 21.3679 | 21.9263 | 21.6472 | 23.2903 | 49.6231 | 123.2365 | 102.0626 | 66.3763 | 0.93976 | 0.43064 | 56.8374 | 21.9067 | 22.2265 | 20.3906 | 21.5752 | 22.0228 | 21.9298 | 22.0775 | 28.6961 | 21.7898 | 21.6106 | 24.1288 | 131.0527 | 166.6565 | 103.8635 | 104.8457 | 67.6706 |  | 49.6793 | 97.9571 | 52.9626 | 85.6947 | 59.1162 | 57.6412 |  | 67.3074 |  |  | 22.7886 | 25.3777 | 51.4767 | [5 empty] | 21.8961 | 59.6939 | 21.6848 | 22.0857 | 31.748 | 21.2657 | 21.8985 | 27.5546 | 80.7447 | 166.3733 |  | 72.3087 | 124.7598 | 22.4258 | 64.5269 | 138.971 | 43.1137 | 100.0611 | 24.9095 | 101.0072 | 24.9913 | 99.6185 | 18.7372 | 67.6145 | 120.4241 | 28.5614 | 66.4065 | 129.7486 | 22.0677 | 60.9934 | 132.9421 | 22.6517 | 92.7007 | 30.091 | 98.0327 | 25.2592 | 105.6226 | 0.91587 | 19.3032 | 1.3653 | 0.049009 | -27.1318 | 3.0953 | 136.48 | 52.44 | 0.99122 | -0.70155 | -6.0852 | 0.88833 | 0.70406 | -15.1477 | 5.4876 | 0.11609 | -0.60856 | -0.047212 | -1.4757 | -1.0471 | -0.705 | 0.15005
42838.4248 | 391 | 22.9084 | 22.8661 | 22.8521 | 22.7688 | 22.3822 | 21.7116 | 22.7031 | 21.7636 | 22.3497 | 22.3509 | 22.3333 | 21.9674 | 21.1772 | 22.1538 | 21.6195 | 21.7928 | 21.9123 | 21.0876 | 21.1932 | 21.4989 | 20.4892 | 20.8648 | 23.0957 | 21.8812 | 21.8613 | 26.0182 | 129.6775 | 114.9229 | 135.7311 | 22.1294 | 21.8687 | 24.4702 | 22.0267 | 21.9419 | 25.6056 | 55.0792 | 144.6963 |  | 84.9747 | 116.8752 | 114.6291 | 105.2765 |  | 17.2144 | 17.7806 | 17.0341 | 17.6894 | 18.1788 | 25.5672 | 90.9689 | 15.5133 | 17.1006 | 15.6338 | 18.216 | 18.4933 | 45.2072 | 48.1437 | 44.6647 | 21.6401 |  |  | 0.54629 | -0.27737 | -25.79 | 0.3824 | 0.50085 | -159.0426 | 20.6357 | 0.65873 | 0.27351 | 0.24327 | 0.29767 | 0.00039098 | 0.00035156 | 1.0218 | 21.7951 | 21.966 | 22.1631 | 22.2219 | 22.023 | 21.3197 | 20.1378 | 22.1807 | 22.3529 | 22.3954 | 22.3379 | 21.9532 | 21.1846 | 22.2676 | 64.7193 | 45.3161 | 46.681 | 32.464 | 28.6385 | 45.9977 | 31.9441 | 22.3307 | 22.0901 | 21.6543 | 22.0609 | 21.778 | 21.3733 | 21.9342 | 21.6466 | 23.3092 | 49.7732 | 123.7486 | 102.2518 | 66.4232 | 1.1995 | 0.16322 | 57.1045 | 21.9043 | 22.2284 | 20.3905 | 21.5709 | 22.021 | 21.9307 | 22.0747 | 28.7375 | 21.7922 | 21.6122 | 24.1442 | 131.4071 | 166.9042 | 104.1158 | 105.1026 | 68.0928 |  | 49.7899 | 99.229 | 53.1001 | 84.6203 | 59.3121 | 57.9074 |  | 67.4382 |  |  | 22.8152 | 25.4168 | 51.7789 | [5 empty] | 21.8991 | 59.8061 | 21.6866 | 22.0912 | 31.7875 | 21.2667 | 21.908 | 27.5841 | 81.0199 | 166.2569 |  | 72.7172 | 125.1671 | 22.4477 | 64.7418 | 139.2068 | 43.2211 | 100.7527 | 24.935 | 101.2293 | 25.0174 | 99.8828 | 18.7287 | 67.7551 | 120.7378 | 28.6053 | 66.6184 | 130.0597 | 22.0679 | 61.2024 | 133.0547 | 22.6818 | 92.826 | 30.1302 | 98.2513 | 25.3074 | 105.8221 | 0.86689 | 19.3011 | 1.3695 | 0.048835 | -27.1178 | 3.0953 | 145.99 | 52.14 | 1.0415 | -0.62602 | -6.0365 | 0.73505 | 0.85242 | -15.1899 | 5.4715 | 0.10828 | -0.63899 | -0.010296 | -1.4919 | -1.1462 | -0.73627 | 0.15407
42838.4248 | 392 | 22.9117 | 22.8742 | 22.8636 | 22.7879 | 22.398 | 21.7124 | 22.7188 | 21.7773 | 22.363 | 22.3615 | 22.3344 | 21.9835 | 21.1934 | 22.1645 | 21.6198 | 21.7827 | 21.9136 | 21.0894 | 21.1956 | 21.5071 | 20.4831 | 20.865 | 23.1112 | 21.8794 | 21.8557 | 26.0377 | 129.9659 | 115.0909 | 136.5926 | 22.1352 | 21.877 | 24.4919 | 22.0281 | 21.9473 | 25.6355 | 55.2648 | 144.0214 |  | 85.2094 | 117.0173 | 114.8948 | 106.4462 |  | 17.2199 | 17.7813 | 17.0258 | 17.6938 | 18.1766 | 25.5833 | 90.7797 | 15.5076 | 17.0973 | 15.5969 | 18.2233 | 18.506 | 45.1922 | 48.1728 | 44.6654 | 21.6389 |  |  | 0.7914 | -0.47187 | -25.625 | 0.63145 | 0.55934 | -158.8396 | 20.518 | 0.6653 | 0.091555 | 0.2204 | 0.23864 | 0.00040413 | 0.00037127 | 1.0225 | 21.794 | 21.9731 | 22.1637 | 22.2175 | 22.0253 | 21.3219 | 20.1382 | 22.1801 | 22.3556 | 22.3965 | 22.3319 | 21.9646 | 21.1863 | 22.2728 | 63.9494 | 42.6577 | 44.3268 | 32.2795 | 28.6756 | 46.0732 | 31.986 | 22.3266 | 22.089 | 21.6592 | 22.0565 | 21.7757 | 21.3793 | 21.9361 | 21.6475 | 23.3201 | 49.9131 | 124.0444 | 102.4272 | 66.4392 | 1.0058 | -0.12265 | 57.6618 | 21.9034 | 22.2299 | 20.3958 | 21.5697 | 22.0267 | 21.9251 | 22.0736 | 28.78 | 21.794 | 21.6164 | 24.166 | 131.8434 | 167.3068 | 104.4394 | 105.3851 | 68.3021 |  | 49.9213 | 99.9942 | 53.2679 | 90.902 | 59.6983 | 58.0402 |  | 67.6267 |  |  | 22.823 | 25.4383 | 51.3997 | [5 empty] | 21.8974 | 60.91 | 21.6892 | 22.0911 | 31.8587 | 21.2634 | 21.9117 | 27.6193 | 81.3234 | 166.8642 |  | 72.9889 | 125.4907 | 22.4516 | 64.8751 | 139.4758 | 43.377 | 101.1584 | 24.9422 | 101.3444 | 25.0261 | 99.991 | 18.7378 | 67.8835 | 120.9505 | 28.6464 | 66.7872 | 130.2489 | 22.0479 | 61.3533 | 133.049 | 22.7166 | 92.9361 | 30.2002 | 98.567 | 25.3379 | 106.1497 | 0.86318 | 19.301 | 1.373 | 0.049489 | -27.1403 | 3.0953 | 151.75 | 51.86 | 1.2549 | -0.81653 | -6.0172 | 0.94456 | 0.90083 | -15.1806 | 5.456 | 0.10712 | -0.65426 | -0.17084 | -1.3974 | -0.87967 | -0.76212 | 0.15858
42838.4248 | 393 | 22.9102 | 22.8725 | 22.8539 | 22.7727 | 22.3847 | 21.7059 | 22.7093 | 21.7665 | 22.3506 | 22.3634 | 22.3293 | 21.9713 | 21.1901 | 22.1634 | 21.6211 | 21.7809 | 21.908 | 21.0892 | 21.1994 | 21.5035 | 20.4835 | 20.8707 | 23.1239 | 21.8781 | 21.8542 | 26.0591 | 130.132 | 115.2361 | 136.7335 | 22.1258 | 21.8695 | 24.499 | 22.0188 | 21.933 | 25.6518 | 55.4398 | 143.3044 |  | 85.3974 | 117.112 | 115.0674 | 107.8095 |  | 17.2281 | 17.7766 | 17.0371 | 17.6908 | 18.1756 | 25.5518 | 90.8204 | 15.4523 | 17.1061 | 15.6357 | 18.2343 | 18.5031 | 45.1928 | 48.1882 | 44.6505 | 21.6349 |  |  | 0.7224 | -0.25371 | -25.3359 | 0.20301 | 0.044816 | -156.9642 | 21.254 | 0.80066 | -0.067433 | 0.1369 | 0.19646 | 0.00036141 | 0.00039591 | 1.0094 | 21.7868 | 21.9656 | 22.1592 | 22.212 | 22.0292 | 21.3213 | 20.128 | 22.173 | 22.3526 | 22.3859 | 22.3397 | 21.9608 | 21.1806 | 22.264 | 63.1483 | 42.797 | 39.9044 | 30.6051 | 27.8364 | 46.1372 | 31.9812 | 22.3228 | 22.0895 | 21.6606 | 22.057 | 21.7762 | 21.3815 | 21.9397 | 21.6613 | 23.3426 | 50.0586 | 124.3369 | 102.5351 | 66.7241 | 1.3102 | -0.13007 | 58.0217 | 21.9026 | 22.2299 | 20.3965 | 21.5667 | 22.0277 | 21.9249 | 22.0811 | 28.8188 | 21.7917 | 21.6163 | 24.1834 | 131.9974 | 167.6701 | 104.672 | 105.6388 | 67.7461 |  | 50.0371 | 100.0476 | 53.3998 | 92.3755 | 60.0365 | 58.2712 |  | 67.7808 |  |  | 22.8388 | 25.4537 | 51.4845 | [5 empty] | 21.8917 | 61.9013 | 21.6957 | 22.0858 | 31.9209 | 21.2697 | 21.9081 | 27.6538 | 81.6124 | 167.4115 |  | 73.0701 | 125.7499 | 22.4654 | 65.0122 | 139.6961 | 43.5 | 101.452 | 24.9628 | 101.5034 | 25.0488 | 100.177 | 18.7559 | 68.0831 | 121.2486 | 28.6843 | 66.9974 | 130.4481 | 22.0605 | 61.6119 | 133.0974 | 22.7445 | 93.1014 | 30.267 | 98.8488 | 25.3825 | 106.4652 | 0.89453 | 19.2977 | 1.3766 | 0.048922 | -27.1832 | 3.0954 | 143.06 | 52.43 | 1.1992 | -0.59873 | -5.9831 | 0.53557 | 0.25498 | -15.0899 | 5.5527 | 0.12667 | -0.65104 | -0.19954 | -1.3009 | -0.38885 | -0.79372 | 0.15582
42838.4248 | 394 | 22.9118 | 22.8805 | 22.8559 | 22.766 | 22.3883 | 21.7145 | 22.7065 | 21.7633 | 22.3522 | 22.3658 | 22.3221 | 21.9776 | 21.1877 | 22.1562 | 21.6167 | 21.7821 | 21.9085 | 21.096 | 21.1999 | 21.508 | 20.4797 | 20.8703 | 23.1375 | 21.8731 | 21.8572 | 26.0832 | 130.2261 | 115.4592 | 136.6755 | 22.1237 | 21.8726 | 24.5132 | 22.0229 | 21.9417 | 25.6796 | 55.6114 | 143.0576 |  | 85.6226 | 117.2878 | 115.2457 | 108.249 |  | 17.2198 | 17.7688 | 17.038 | 17.6872 | 18.1818 | 25.5543 | 91.4232 | 15.4406 | 17.0994 | 15.6882 | 18.2318 | 18.5029 | 45.1596 | 48.2014 | 44.6389 | 21.6359 |  |  | 0.53512 | -0.32862 | -25.0836 | 0.3548 | 0.086872 | -155.4804 | 21.1752 | 0.74481 | 0.080658 | 0.23907 | 0.24732 | 0.0003877 | 0.00035977 | 1.0063 | 21.7913 | 21.9687 | 22.1673 | 22.218 | 22.0304 | 21.3294 | 20.1341 | 22.1794 | 22.3645 | 22.3925 | 22.3432 | 21.9539 | 21.1831 | 22.2638 | 63.8897 | 42.8537 | 37.7444 | 29.5892 | 26.5646 | 46.2366 | 31.9976 | 22.3228 | 22.09 | 21.6548 | 22.0613 | 21.7744 | 21.382 | 21.9444 | 21.6606 | 23.3499 | 50.2116 | 124.6556 | 102.7816 | 66.9561 | 0.88452 | 0.16189 | 57.8991 | 21.9056 | 22.2265 | 20.4028 | 21.57 | 22.0302 | 21.9303 | 22.0862 | 28.8642 | 21.7975 | 21.6189 | 24.2004 | 132.2673 | 168.0515 | 104.7947 | 105.8343 | 67.6721 |  | 50.1482 | 99.2205 | 53.5037 | 92.6085 | 60.354 | 58.4393 |  | 67.9227 |  |  | 22.8619 | 25.453 | 51.7577 | [5 empty] | 21.8856 | 62.2162 | 21.6902 | 22.0828 | 31.9587 | 21.2686 | 21.9058 | 27.6966 | 81.8815 | 167.7006 |  | 72.9616 | 125.8729 | 22.4735 | 65.2664 | 140.2849 | 43.6233 | 101.5641 | 25.0054 | 101.7098 | 25.0736 | 100.4007 | 18.7797 | 68.4097 | 121.7954 | 28.7317 | 67.2509 | 130.8467 | 22.0823 | 61.8797 | 133.2082 | 22.7677 | 93.3317 | 30.3248 | 99.0498 | 25.4281 | 106.6084 | 1.0706 | 19.2961 | 1.3799 | 0.046447 | -27.0686 | 3.0953 | 162.25 | 51.21 | 1.032 | -0.6814 | -5.9532 | 0.70802 | 0.355 | -15.0185 | 5.5424 | 0.13266 | -0.62436 | -0.19452 | -1.3715 | -0.14693 | -0.79977 | 0.1548
42838.4248 | 395 | 22.9107 | 22.8818 | 22.8591 | 22.7747 | 22.3894 | 21.7122 | 22.7088 | 21.7702 | 22.355 | 22.3668 | 22.3288 | 21.9822 | 21.1898 | 22.1595 | 21.6147 | 21.7919 | 21.9082 | 21.0932 | 21.2004 | 21.5083 | 20.4801 | 20.8739 | 23.1556 | 21.8705 | 21.8665 | 26.1024 | 130.3507 | 115.756 | 136.6464 | 22.1292 | 21.8721 | 24.5332 | 22.0204 | 21.9455 | 25.7043 | 55.7884 | 143.8467 |  | 85.8389 | 117.5342 | 115.3546 | 107.9348 |  | 17.2259 | 17.7764 | 17.0404 | 17.6963 | 18.1815 | 25.5812 | 91.9992 | 15.4571 | 17.1047 | 15.7171 | 18.2432 | 18.5051 | 45.1466 | 48.24 | 44.6503 | 21.6426 |  |  | 0.51738 | -0.32468 | -25.2761 | 0.29697 | 0.15587 | -157.1015 | 21.9151 | 0.81249 | -0.077163 | 0.094731 | 0.28447 | 0.00038441 | 0.00037291 | 0.99898 | 21.7813 | 21.9604 | 22.1571 | 22.2102 | 22.0282 | 21.318 | 20.1318 | 22.1715 | 22.3471 | 22.3928 | 22.3288 | 21.9532 | 21.1831 | 22.2627 | 63.5795 | 40.8258 | 38.4327 | 28.8736 | 25.7201 | 46.3218 | 32.0163 | 22.334 | 22.0996 | 21.6606 | 22.0667 | 21.7796 | 21.3862 | 21.9418 | 21.6596 | 23.3782 | 50.3605 | 125.0554 | 103.2765 | 67.1036 | 1.1295 | 0.13926 | 57.8866 | 21.9051 | 22.2301 | 20.4068 | 21.5738 | 22.0317 | 21.928 | 22.0944 | 28.8983 | 21.7997 | 21.62 | 24.2211 | 132.6865 | 168.5528 | 104.9231 | 106.0452 | 67.8673 |  | 50.2898 | 100.3523 | 53.6313 | 92.001 | 60.6429 | 58.7209 |  | 68.0741 |  |  | 22.8927 | 25.4973 | 51.7787 | [5 empty] | 21.8969 | 62.069 | 21.694 | 22.0853 | 32.0167 | 21.2696 | 21.9101 | 27.7282 | 82.1468 | 167.9179 |  | 73.0544 | 125.9131 | 22.4847 | 65.5504 | 140.5362 | 43.7531 | 101.7452 | 25.0268 | 101.9907 | 25.0889 | 100.6248 | 18.7964 | 68.8017 | 122.1678 | 28.7673 | 67.4812 | 131.1554 | 22.0998 | 62.1038 | 133.4384 | 22.7775 | 93.5163 | 30.3592 | 99.2313 | 25.4637 | 106.8122 | 0.8144 | 19.2945 | 1.3827 | 0.046752 | -27.0993 | 3.0953 | 144.56 | 52.6 | 1.0147 | -0.67731 | -5.976 | 0.64777 | 0.47554 | -15.0972 | 5.6387 | 0.13226 | -0.65124 | -0.16719 | -1.3269 | -0.2212 | -0.7847 | 0.15598
42838.4249 | 396 | 22.9083 | 22.8801 | 22.8556 | 22.7778 | 22.3917 | 21.7123 | 22.7111 | 21.7674 | 22.3544 | 22.3607 | 22.329 | 21.9868 | 21.1891 | 22.163 | 21.6242 | 21.7887 | 21.9035 | 21.0885 | 21.1973 | 21.5086 | 20.4826 | 20.8805 | 23.1721 | 21.8737 | 21.871 | 26.133 | 130.5935 | 115.9968 | 137.1456 | 22.123 | 21.8745 | 24.5553 | 22.0252 | 21.939 | 25.7338 | 55.9785 | 145.4301 |  | 86.1118 | 117.834 | 115.439 | 107.7395 |  | 17.2284 | 17.7805 | 17.0362 | 17.6995 | 18.1756 | 25.5644 | 92.3919 | 15.4701 | 17.1076 | 15.7133 | 18.2612 | 18.509 | 45.1186 | 48.2726 | 44.6468 | 21.6354 |  |  | 0.46284 | -0.4607 | -25.6369 | 0.50791 | 0.33723 | -152.9624 | 21.371 | 0.7481 | -0.12328 | 0.054659 | 0.31468 | 0.00034992 | 0.00035977 | 0.98904 | 21.7879 | 21.9526 | 22.1543 | 22.2118 | 22.0262 | 21.316 | 20.1325 | 22.1779 | 22.3415 | 22.3815 | 22.329 | 21.9502 | 21.1801 | 22.2607 | 66.0282 | 42.8102 | 42.6553 | 28.7506 | 26.1059 | 46.4539 | 32.0991 | 22.3232 | 22.0958 | 21.6595 | 22.0572 | 21.7761 | 21.3828 | 21.9378 | 21.6594 | 23.3876 | 50.4952 | 125.4068 | 103.6171 | 67.7956 | 1.1749 | 0.7692 | 58.1122 | 21.9014 | 22.2261 | 20.4082 | 21.5744 | 22.0274 | 21.9241 | 22.0972 | 28.9364 | 21.7939 | 21.623 | 24.2381 | 133.0312 | 168.8627 | 105.123 | 106.2766 | 67.7857 |  | 50.4035 | 102.0652 | 53.8298 | 90.4679 | 60.8674 | 59.0217 |  | 68.2335 |  |  | 22.8894 | 25.555 | 51.6684 | [5 empty] | 21.899 | 61.3734 | 21.6922 | 22.0858 | 32.0757 | 21.2669 | 21.9091 | 27.764 | 82.4166 | 168.4842 |  | 73.4476 | 125.9632 | 22.5103 | 65.6679 | 140.9163 | 43.883 | 101.9529 | 25.0527 | 102.1924 | 25.1157 | 100.8709 | 18.8125 | 69.2103 | 122.2755 | 28.812 | 67.7123 | 131.3876 | 22.1197 | 62.3123 | 133.7238 | 22.8038 | 93.651 | 30.4359 | 99.4444 | 25.5062 | 107.2039 | 0.98135 | 19.2912 | 1.3852 | 0.047325 | -27.1084 | 3.0953 | 147.61 | 51.5 | 0.96035 | -0.80681 | -6.0186 | 0.84714 | 0.69945 | -14.8966 | 5.5681 | 0.13856 | -0.69173 | -0.11647 | -1.5833 | -0.68064 | -0.77246 | 0.14153
42838.4249 | 397 | 22.9036 | 22.8747 | 22.847 | 22.7662 | 22.3858 | 21.7126 | 22.6986 | 21.7578 | 22.3576 | 22.35 | 22.3239 | 21.9845 | 21.1907 | 22.157 | 21.6211 | 21.7872 | 21.9077 | 21.0864 | 21.1957 | 21.5056 | 20.4797 | 20.883 | 23.1863 | 21.8724 | 21.8652 | 26.1552 | 130.7557 | 116.1894 | 136.9527 | 22.122 | 21.8708 | 24.5831 | 22.0214 | 21.9398 | 25.7524 | 56.1548 | 145.6336 |  | 86.3786 | 118.0968 | 115.5807 | 108.5208 |  | 17.2197 | 17.7782 | 17.0281 | 17.6907 | 18.1764 | 25.5447 | 92.3071 | 15.4803 | 17.1053 | 15.7182 | 18.2635 | 18.5063 | 45.1083 | 48.3109 | 44.6293 | 21.6288 |  |  | 0.54629 | -0.36805 | -25.3924 | 0.18592 | 0.25706 | -158.538 | 20.8926 | 0.83615 | -0.047 | 0.13124 | 0.3902 | 0.00039263 | 0.00034827 | 0.96505 | 21.7932 | 21.9581 | 22.1631 | 22.2116 | 22.0314 | 21.3241 | 20.1362 | 22.1835 | 22.3445 | 22.3885 | 22.3382 | 21.9491 | 21.1898 | 22.2634 | 69.943 | 47.2326 | 46.5024 | 31.1385 | 27.2357 | 46.6332 | 32.184 | 22.3238 | 22.0934 | 21.6511 | 22.0511 | 21.7769 | 21.3835 | 21.9356 | 21.6553 | 23.3984 | 50.6215 | 125.6776 | 103.8479 | 68.4598 | 1.1741 | 0.66383 | 58.6316 | 21.8994 | 22.2259 | 20.4117 | 21.5783 | 22.0289 | 21.9255 | 22.1016 | 28.9852 | 21.7918 | 21.6243 | 24.2615 | 133.2297 | 168.9384 | 105.3755 | 106.5504 | 67.4941 |  | 50.523 | 102.8945 | 54.0039 | 89.9445 | 61.0902 | 59.4271 |  | 68.4076 |  |  | 22.8905 | 25.5743 | 51.5817 | [5 empty] | 21.8943 | 60.7546 | 21.6849 | 22.0815 | 32.1359 | 21.261 | 21.8993 | 27.7991 | 82.6906 | 169.1033 |  | 73.9245 | 126.2485 | 22.534 | 65.7521 | 141.3906 | 43.9864 | 102.1849 | 25.0765 | 102.2756 | 25.1467 | 101.1184 | 18.7939 | 69.7075 | 122.2513 | 28.8529 | 67.9801 | 131.7061 | 22.138 | 62.4774 | 134.0206 | 22.83 | 93.8557 | 30.5358 | 99.6383 | 25.531 | 107.6675 | 0.96169 | 19.2901 | 1.3883 | 0.047761 | -27.1 | 3.0953 | 174.29 | 51.99 | 1.0431 | -0.72113 | -5.9898 | 0.51253 | 0.61066 | -15.1652 | 5.5053 | 0.1509 | -0.70855 | -0.093858 | -1.997 | -1.0981 | -0.78784 | 0.12756
42838.4249 | 398 | 22.908 | 22.8762 | 22.8526 | 22.7731 | 22.3806 | 21.7012 | 22.6922 | 21.7653 | 22.3516 | 22.3546 | 22.329 | 21.9814 | 21.1859 | 22.1571 | 21.6159 | 21.7917 | 21.9122 | 21.0892 | 21.1969 | 21.5068 | 20.4754 | 20.8776 | 23.2017 | 21.8806 | 21.8781 | 26.1759 | 130.7954 | 116.2844 | 136.8605 | 22.1226 | 21.8718 | 24.5912 | 22.0132 | 21.9426 | 25.7774 | 56.3633 | 146.9228 |  | 86.6621 | 118.2847 | 115.6952 | 109.0764 |  | 17.2219 | 17.7795 | 17.0268 | 17.6966 | 18.1916 | 25.5978 | 92.3154 | 15.4662 | 17.1065 | 15.749 | 18.2663 | 18.5032 | 45.0939 | 48.3561 | 44.6165 | 21.6268 |  |  | 0.62383 | -0.48962 | -25.5817 | 0.31537 | 0.60796 | -154.8785 | 21.0004 | 0.78949 | -0.060427 | 0.054659 | 0.356 | 0.00036634 | 0.00037784 | 0.95253 | 21.7921 | 21.9611 | 22.1678 | 22.2101 | 22.0299 | 21.3218 | 20.1386 | 22.1738 | 22.3534 | 22.3852 | 22.3384 | 21.9545 | 21.1835 | 22.2647 | 72.0958 | 49.8133 | 49.6088 | 32.2557 | 27.9887 | 46.8191 | 32.2942 | 22.3251 | 22.0912 | 21.6546 | 22.051 | 21.7751 | 21.387 | 21.938 | 21.664 | 23.4139 | 50.7522 | 125.9554 | 104.1563 | 68.4936 | 1.0039 | 0.60239 | 58.735 | 21.9081 | 22.241 | 20.4162 | 21.5778 | 22.0336 | 21.9331 | 22.1091 | 29.028 | 21.8004 | 21.6253 | 24.2825 | 133.6204 | 169.0841 | 105.6231 | 106.8234 | 67.9392 |  | 50.6867 | 102.607 | 54.1376 | 91.9974 | 61.3563 | 59.4104 |  | 68.5974 |  |  | 22.8917 | 25.5893 | 52.4865 | [5 empty] | 21.8946 | 60.7019 | 21.6909 | 22.0872 | 32.217 | 21.2626 | 21.9044 | 27.8426 | 82.969 | 169.5846 |  | 74.3626 | 126.4664 | 22.5527 | 65.876 | 141.7445 | 44.1115 | 102.4655 | 25.1058 | 102.3753 | 25.1683 | 101.3615 | 18.77 | 70.1041 | 122.2833 | 28.9028 | 68.2414 | 131.9706 | 22.1757 | 62.6416 | 134.5157 | 22.8681 | 94.0863 | 30.6025 | 99.7918 | 25.5682 | 107.9578 | 1.1661 | 19.2864 | 1.3918 | 0.047986 | -27.1798 | 3.0953 | 172.16 | 52.59 | 1.1145 | -0.83174 | -6.0121 | 0.66753 | 0.9392 | -14.9905 | 5.5199 | 0.14434 | -0.69579 | -0.14124 | -2.2142 | -1.4303 | -0.79579 | 0.13126
42838.4249 | 399 | 22.9042 | 22.8683 | 22.8466 | 22.7641 | 22.3876 | 21.7112 | 22.7048 | 21.7657 | 22.3487 | 22.3564 | 22.3249 | 21.9829 | 21.1872 | 22.155 | 21.6112 | 21.7895 | 21.9121 | 21.0906 | 21.1955 | 21.51 | 20.4765 | 20.8816 | 23.2196 | 21.877 | 21.8784 | 26.2081 | 131.2305 | 116.3464 | 138.3362 | 22.1228 | 21.8808 | 24.614 | 22.0257 | 21.9578 | 25.8086 | 56.6002 | 147.5848 |  | 86.948 | 118.3235 | 115.817 | 110.9533 |  | 17.2222 | 17.773 | 17.0224 | 17.6873 | 18.1959 | 25.6514 | 92.9797 | 15.469 | 17.1001 | 15.8014 | 18.2625 | 18.518 | 45.1034 | 48.3988 | 44.6025 | 21.6355 |  |  | 0.72503 | -0.31614 | -25.6454 | 0.6367 | 0.2886 | -152.9656 | 21.118 | 0.52468 | 0.20695 | 0.22397 | 0.20149 | 0.00034827 | 0.00036141 | 0.95905 | 21.7837 | 21.957 | 22.1581 | 22.2154 | 22.0295 | 21.3176 | 20.1303 | 22.1714 | 22.3553 | 22.3883 | 22.3396 | 21.9509 | 21.185 | 22.263 | 73.4269 | 50.8194 | 53.3321 | 33.2733 | 28.5563 | 46.9963 | 32.4331 | 22.3266 | 22.0842 | 21.6493 | 22.0499 | 21.7739 | 21.3886 | 21.9419 | 21.6601 | 23.4304 | 50.9078 | 126.6068 | 104.4953 | 68.5285 | 0.88196 | 0.46393 | 58.7068 | 21.9104 | 22.2421 | 20.4184 | 21.5731 | 22.0273 | 21.9334 | 22.109 | 29.0652 | 21.8011 | 21.6312 | 24.2938 | 134.0353 | 169.7136 | 105.8431 | 107.093 | 69.1317 |  | 50.8577 | 102.3331 | 54.2803 | 92.8564 | 61.652 | 59.1386 |  | 68.7663 |  |  | 22.8965 | 25.6242 | 52.8763 | [5 empty] | 21.8957 | 60.5496 | 21.6915 | 22.0912 | 32.315 | 21.2684 | 21.9199 | 27.9068 | 83.2821 | 169.8947 |  | 74.6969 | 126.7195 | 22.5779 | 65.9974 | 142.1076 | 44.2651 | 102.7733 | 25.1302 | 102.5079 | 25.1842 | 101.7055 | 18.7984 | 70.3808 | 122.4636 | 28.9612 | 68.4525 | 132.4209 | 22.2075 | 62.8142 | 135.0578 | 22.9016 | 94.2459 | 30.6734 | 100.0203 | 25.6274 | 108.255 | 0.88229 | 19.2818 | 1.3969 | 0.047427 | -27.1192 | 3.0953 | 175.55 | 51.45 | 1.2037 | -0.66833 | -6.0195 | 0.94847 | 0.64716 | -14.8989 | 5.5359 | 0.11728 | -0.68309 | -0.15437 | -2.3411 | -1.8277 | -0.83942 | 0.13582
42838.4249 | 400 | 22.9057 | 22.8657 | 22.8439 | 22.7676 | 22.3877 | 21.71 | 22.7026 | 21.7629 | 22.3483 | 22.36 | 22.3214 | 21.9732 | 21.1872 | 22.155 | 21.6154 | 21.7936 | 21.9146 | 21.091 | 21.1887 | 21.5207 | 20.4889 | 20.8915 | 23.2332 | 21.876 | 21.8782 | 26.2312 | 131.7616 | 116.441 | 138.3753 | 22.1129 | 21.8808 | 24.6268 | 22.0181 | 21.949 | 25.8259 | 56.8186 | 147.9171 |  | 87.2186 | 118.3731 | 116.0106 | 112.1012 |  | 17.2214 | 17.7749 | 17.0246 | 17.6881 | 18.2093 | 25.7371 | 93.4549 | 15.5172 | 17.0994 | 15.8353 | 18.262 | 18.516 | 45.1107 | 48.4384 | 44.5897 | 21.6322 |  |  | 0.45167 | -0.23729 | -25.6441 | 0.22141 | 0.3162 | -156.407 | 21.2363 | 0.76584 | -0.027734 | 0.017944 | 0.23465 | 0.00038934 | 0.00038277 | 0.94072 | 21.7866 | 21.9601 | 22.1596 | 22.2134 | 22.0235 | 21.322 | 20.1305 | 22.1783 | 22.3488 | 22.3961 | 22.3364 | 21.9515 | 21.1775 | 22.2626 | 73.3282 | 49.227 | 53.8485 | 34.683 | 29.6096 | 47.1393 | 32.5413 | 22.3185 | 22.0894 | 21.6432 | 22.0497 | 21.7673 | 21.3887 | 21.9359 | 21.6533 | 23.444 | 51.0522 | 127.149 | 104.8258 | 69.2199 | 1.0711 | 0.064699 | 58.6651 | 21.906 | 22.2371 | 20.4226 | 21.5709 | 22.0257 | 21.929 | 22.1124 | 29.1062 | 21.7937 | 21.6328 | 24.3128 | 134.1994 | 170.5422 | 106.0284 | 107.3672 | 69.4748 |  | 50.9926 | 102.8962 | 54.415 | 92.9873 | 61.9296 | 60.0301 |  | 68.9245 |  |  | 22.9051 | 25.6579 | 53.4176 | [5 empty] | 21.8976 | 60.3045 | 21.6991 | 22.093 | 32.4017 | 21.2714 | 21.9168 | 27.9765 | 83.6399 | 170.776 |  | 74.9885 | 127.1645 | 22.6091 | 66.1113 | 142.3981 | 44.5257 | 103.0452 | 25.1492 | 102.6791 | 25.2085 | 102.2272 | 18.8348 | 70.5307 | 122.7862 | 29.0442 | 68.6564 | 132.8565 | 22.2392 | 62.9997 | 135.4562 | 22.9311 | 94.4717 | 30.7703 | 100.2855 | 25.6806 | 108.5747 | 1.4028 | 19.2774 | 1.4002 | 0.048719 | -27.1027 | 3.0953 | 179.13 | 52.42 | 0.95011 | -0.57902 | -6.0194 | 0.55931 | 0.67749 | -15.0678 | 5.5521 | 0.11254 | -0.69391 | -0.14793 | -2.3132 | -1.8723 | -0.86346 | 0.12173
42838.4249 | 401 | 22.9039 | 22.8733 | 22.8451 | 22.7748 | 22.3947 | 21.7113 | 22.7097 | 21.7673 | 22.3492 | 22.3553 | 22.3272 | 21.9792 | 21.1922 | 22.1586 | 21.6227 | 21.7887 | 21.9098 | 21.0836 | 21.1968 | 21.5145 | 20.4843 | 20.8774 | 23.252 | 21.8861 | 21.8808 | 26.2599 | 131.8971 | 116.6168 | 137.911 | 22.118 | 21.8848 | 24.6533 | 22.029 | 21.9484 | 25.8602 | 57.0409 | 149.5023 |  | 87.5327 | 118.5162 | 116.2855 | 112.9044 |  | 17.2245 | 17.7909 | 17.0269 | 17.7066 | 18.21 | 25.8259 | 93.8954 | 15.5489 | 17.1082 | 15.8062 | 18.2774 | 18.5087 | 45.1162 | 48.4774 | 44.581 | 21.638 |  |  | 0.6764 | -0.19588 | -25.7604 | 0.43957 | 0.3714 | -149.8338 | 21.0805 | 0.49116 | 0.12483 | 0.069765 | 0.24038 | 0.00037949 | 0.0003532 | 0.9373 | 21.7921 | 21.9666 | 22.1678 | 22.2226 | 22.0355 | 21.3299 | 20.1411 | 22.1786 | 22.3627 | 22.3945 | 22.3423 | 21.9614 | 21.1887 | 22.2762 | 72.2938 | 47.3195 | 51.065 | 34.5463 | 30.16 | 47.2725 | 32.6115 | 22.3198 | 22.0895 | 21.6466 | 22.0491 | 21.7726 | 21.3883 | 21.9353 | 21.6593 | 23.4608 | 51.1941 | 127.8373 | 105.1895 | 69.3351 | 0.89435 | 0.20697 | 58.4794 | 21.9071 | 22.2291 | 20.4263 | 21.5728 | 22.0257 | 21.93 | 22.1144 | 29.1487 | 21.7984 | 21.6325 | 24.3353 | 134.3565 | 171.1369 | 106.2519 | 107.6687 | 70.1962 |  | 51.1376 | 103.5913 | 54.5693 | 93.5996 | 62.2937 | 60.9367 |  | 69.1143 |  |  | 22.9194 | 25.6945 | 53.1644 | [5 empty] | 21.902 | 60.631 | 21.7032 | 22.0912 | 32.492 | 21.2716 | 21.9185 | 28.0507 | 83.9912 | 171.0085 |  | 75.3301 | 127.4809 | 22.6361 | 66.1975 | 142.8437 | 44.7707 | 103.3163 | 25.1774 | 103.0065 | 25.2386 | 102.7103 | 18.8516 | 70.5904 | 123.1047 | 29.1226 | 68.8813 | 133.246 | 22.2528 | 63.2195 | 135.8717 | 22.9639 | 94.7524 | 30.8793 | 100.5538 | 25.723 | 108.8005 | 1.0682 | 19.2776 | 1.404 | 0.04951 | -27.1257 | 3.0953 | 173.59 | 51.65 | 1.162 | -0.5261 | -6.0332 | 0.7881 | 0.73436 | -14.7499 | 5.5326 | 0.097648 | -0.7077 | -0.15171 | -2.1825 | -1.5548 | -0.87779 | 0.12357
42838.4249 | 402 | 22.8995 | 22.8805 | 22.8514 | 22.7715 | 22.3871 | 21.715 | 22.7032 | 21.7715 | 22.3513 | 22.362 | 22.3269 | 21.9785 | 21.1921 | 22.1621 | 21.617 | 21.8015 | 21.9067 | 21.0888 | 21.2009 | 21.5169 | 20.4919 | 20.8942 | 23.2698 | 21.8824 | 21.88 | 26.2735 | 132.235 | 116.7031 | 139.2327 | 22.1194 | 21.8812 | 24.677 | 22.0316 | 21.9548 | 25.8855 | 57.2672 | 149.5205 |  | 87.7968 | 118.769 | 116.5405 | 113.7756 |  | 17.2329 | 17.8111 | 17.0315 | 17.706 | 18.2298 | 25.8345 | 94.4739 | 15.5567 | 17.1057 | 15.7431 | 18.2906 | 18.5165 | 45.1216 | 48.5149 | 44.5898 | 21.6305 |  |  | 0.71451 | -0.38842 | -25.6434 | 0.37451 | 0.10461 | -157.1626 | 22.174 | 0.42742 | 0.014494 | 0.15473 | 0.35999 | 0.00036141 | 0.00036306 | 0.94117 | 21.7893 | 21.9625 | 22.1652 | 22.2125 | 22.0273 | 21.3216 | 20.1306 | 22.1796 | 22.3547 | 22.3931 | 22.3394 | 21.9564 | 21.1876 | 22.2633 | 72.0979 | 46.7577 | 50.7743 | 34.0046 | 29.7152 | 47.3964 | 32.6787 | 22.3213 | 22.0899 | 21.6516 | 22.0511 | 21.7742 | 21.3839 | 21.9377 | 21.6615 | 23.4795 | 51.3485 | 128.6048 | 105.4502 | 69.7998 | 0.92541 | 0.5849 | 58.4637 | 21.9147 | 22.2316 | 20.4314 | 21.5825 | 22.0319 | 21.9361 | 22.1251 | 29.1947 | 21.8078 | 21.6432 | 24.3608 | 134.7034 | 171.9251 | 106.5541 | 108.0166 | 70.6537 |  | 51.3163 | 104.9961 | 54.7637 | 93.054 | 62.64 | 61.7074 |  | 69.308 |  |  | 22.9343 | 25.7151 | 52.9482 | [5 empty] | 21.8922 | 60.6527 | 21.6924 | 22.0879 | 32.5946 | 21.273 | 21.9063 | 28.1356 | 84.3359 | 170.8721 |  | 75.7276 | 127.7935 | 22.6691 | 66.4772 | 142.8689 | 45.0404 | 103.5395 | 25.205 | 103.55 | 25.2736 | 102.9637 | 18.8673 | 70.8054 | 123.4554 | 29.2142 | 69.1368 | 134.0844 | 22.2831 | 63.5246 | 136.1983 | 22.9978 | 94.9626 | 30.9858 | 100.6129 | 25.7581 | 109.0511 | 1.1158 | 19.2727 | 1.4075 | 0.050977 | -27.1389 | 3.0953 | 199.93 | 52.07 | 1.1963 | -0.74086 | -6.0197 | 0.72748 | 0.38975 | -15.1066 | 5.6743 | 0.091286 | -0.73977 | -0.12397 | -2.146 | -1.5146 | -0.89385 | 0.11615
42838.4249 | 403 | 22.8972 | 22.866 | 22.8512 | 22.7663 | 22.3842 | 21.7059 | 22.7049 | 21.7642 | 22.3553 | 22.3562 | 22.3271 | 21.9735 | 21.1866 | 22.1597 | 21.615 | 21.7853 | 21.8994 | 21.0867 | 21.1931 | 21.5112 | 20.4709 | 20.8905 | 23.2765 | 21.8726 | 21.893 | 26.3036 | 132.7367 | 116.9537 | 138.9669 | 22.1152 | 21.8784 | 24.6915 | 22.0279 | 21.957 | 25.9048 | 57.4954 | 150.7711 |  | 88.0859 | 119.0352 | 116.777 | 113.5907 |  | 17.2367 | 17.8104 | 17.0403 | 17.709 | 18.2503 | 25.8015 | 95.007 | 15.5397 | 17.1073 | 15.6996 | 18.2929 | 18.5283 | 45.1332 | 48.5537 | 44.5936 | 21.6301 |  |  | 0.63237 | -0.31285 | -25.8977 | 0.29829 | 0.20252 | -154.9219 | 21.3822 | 0.42282 | -0.13223 | 0.07459 | 0.24333 | 0.00038113 | 0.0003532 | 0.93463 | 21.7934 | 21.9645 | 22.1674 | 22.2148 | 22.0296 | 21.3189 | 20.1365 | 22.18 | 22.3587 | 22.3891 | 22.3413 | 21.9624 | 21.1843 | 22.2753 | 71.7008 | 46.2106 | 52.5791 | 34.7274 | 30.4643 | 47.5186 | 32.7778 | 22.3298 | 22.0928 | 21.6567 | 22.0575 | 21.7744 | 21.3944 | 21.9364 | 21.6671 | 23.4987 | 51.4991 | 129.4975 | 105.713 | 70.2383 | 0.7984 | 0.2045 | 58.6851 | 21.9098 | 22.2322 | 20.4326 | 21.5772 | 22.0336 | 21.9313 | 22.1283 | 29.2351 | 21.7967 | 21.6408 | 24.3769 | 135.0826 | 172.7954 | 106.8272 | 108.2789 | 70.8961 |  | 51.4631 | 105.6004 | 54.9385 | 93.3709 | 62.9699 | 61.4054 |  | 69.5058 |  |  | 22.9455 | 25.7607 | 53.2859 | [5 empty] | 21.8991 | 60.8784 | 21.6982 | 22.0862 | 32.7233 | 21.2673 | 21.911 | 28.2384 | 84.6853 | 171.9993 |  | 76.1564 | 128.366 | 22.7102 | 66.9064 | 143.0596 | 45.2632 | 103.78 | 25.2442 | 103.8957 | 25.318 | 103.0069 | 18.9012 | 71.1718 | 123.9035 | 29.3105 | 69.4191 | 135.4197 | 22.3149 | 63.8317 | 136.3149 | 23.0317 | 95.1682 | 31.085 | 100.7039 | 25.8023 | 109.5861 | 1.2151 | 19.2704 | 1.4123 | 0.05187 | -27.0243 | 3.0953 | 183.62 | 52.32 | 1.125 | -0.6649 | -6.0494 | 0.64923 | 0.54226 | -14.9977 | 5.5718 | 0.089767 | -0.7503 | -0.12077 | -2.0874 | -1.7035 | -0.88051 | 0.10932
42838.425 | 404 | 22.908 | 22.8723 | 22.8595 | 22.7762 | 22.3948 | 21.7132 | 22.7148 | 21.7645 | 22.3539 | 22.3604 | 22.3332 | 21.9862 | 21.1951 | 22.1625 | 21.6119 | 21.7868 | 21.8989 | 21.0889 | 21.1963 | 21.5245 | 20.4753 | 20.8862 | 23.3029 | 21.8782 | 21.8894 | 26.3284 | 133.1911 | 117.2947 | 140.9717 | 22.1172 | 21.874 | 24.7077 | 22.0281 | 21.953 | 25.9314 | 57.7187 | 153.6395 |  | 88.4009 | 119.2325 | 117.0698 | 113.3147 |  | 17.2426 | 17.822 | 17.0484 | 17.7249 | 18.282 | 25.7675 | 95.4509 | 15.497 | 17.1137 | 15.7221 | 18.3016 | 18.5279 | 45.1328 | 48.5936 | 44.5978 | 21.6356 |  |  | 0.44575 | -0.38974 | -26.2105 | 0.49148 | 0.32935 | -152.233 | 21.0608 | 0.46225 | 0.2268 | 0.0040974 | 0.32683 | 0.00034827 | 0.00037949 | 0.93358 | 21.8013 | 21.9623 | 22.1723 | 22.2181 | 22.0344 | 21.3262 | 20.1449 | 22.1842 | 22.3564 | 22.3908 | 22.3446 | 21.9584 | 21.1889 | 22.2766 | 70.3185 | 44.9324 | 50.2098 | 34.4592 | 30.6343 | 47.6018 | 32.8381 | 22.3224 | 22.0882 | 21.6535 | 22.0503 | 21.7751 | 21.3936 | 21.9383 | 21.6671 | 23.5167 | 51.6704 | 130.3852 | 105.9633 | 70.6957 | 1.2079 | 0.26973 | 58.8031 | 21.9047 | 22.2287 | 20.435 | 21.5713 | 22.0285 | 21.9326 | 22.1261 | 29.2711 | 21.7934 | 21.634 | 24.388 | 135.5812 | 174.0208 | 107.0015 | 108.4598 | 71.037 |  | 51.5952 | 105.4786 | 55.0831 | 94.7457 | 63.3498 | 61.2889 |  | 69.7126 |  |  | 22.9613 | 25.8005 | 53.3964 | [5 empty] | 21.8953 | 61.3555 | 21.6915 | 22.0807 | 32.7786 | 21.2676 | 21.9081 | 28.3182 | 85.0855 | 173.3974 |  | 76.5037 | 128.8184 | 22.7426 | 67.186 | 144.3363 | 45.4928 | 104.0705 | 25.3041 | 104.1438 | 25.3389 | 103.354 | 18.9245 | 71.6224 | 124.3245 | 29.3886 | 69.741 | 136.603 | 22.3567 | 63.9715 | 136.5108 | 23.0649 | 95.367 | 31.1817 | 100.8864 | 25.8466 | 109.9531 | 1.4438 | 19.2674 | 1.4161 | 0.051783 | -27.1045 | 3.0953 | 181.47 | 51.42 | 0.94684 | -0.74213 | -6.086 | 0.83338 | 0.69146 | -14.8661 | 5.5294 | 0.090549 | -0.74174 | -0.14513 | -1.9239 | -1.4331 | -0.86481 | 0.1027
42838.425 | 405 | 22.8925 | 22.8662 | 22.8469 | 22.7635 | 22.3804 | 21.7025 | 22.6949 | 21.7569 | 22.3423 | 22.3446 | 22.3226 | 21.9753 | 21.1846 | 22.1516 | 21.6061 | 21.7793 | 21.9072 | 21.0901 | 21.193 | 21.5241 | 20.4891 | 20.8949 | 23.3134 | 21.8713 | 21.8924 | 26.3427 | 133.5208 | 117.4666 | 141.4358 | 22.1168 | 21.883 | 24.7179 | 22.016 | 21.9633 | 25.9508 | 57.9241 | 154.928 |  | 88.6552 | 119.3441 | 117.4151 | 112.9954 |  | 17.2341 | 17.8172 | 17.0554 | 17.7319 | 18.3059 | 25.7331 | 95.3749 | 15.4467 | 17.1066 | 15.7426 | 18.3034 | 18.5284 | 45.1347 | 48.6259 | 44.6104 | 21.625 |  |  | 0.65603 | -0.21757 | -26.4353 | 0.53682 | 0.11118 | -156.0764 | 20.7954 | 0.5641 | 0.092139 | 0.04291 | 0.18153 | 0.0003762 | 0.00036141 | 0.93031 | 21.8018 | 21.9653 | 22.1649 | 22.2159 | 22.0261 | 21.3197 | 20.1357 | 22.1822 | 22.3533 | 22.3933 | 22.3392 | 21.9585 | 21.1894 | 22.2712 | 71.1026 | 46.3966 | 49.2073 | 33.7147 | 30.1305 | 47.7328 | 32.9056 | 22.3277 | 22.0972 | 21.657 | 22.0573 | 21.7874 | 21.3958 | 21.9427 | 21.675 | 23.5288 | 51.8207 | 131.1175 | 106.3243 | 70.9299 | 0.70128 | 0.44129 | 58.9806 | 21.9049 | 22.2306 | 20.4451 | 21.5733 | 22.0278 | 21.9374 | 22.1289 | 29.3147 | 21.7981 | 21.642 | 24.4117 | 136.3983 | 175.464 | 107.1535 | 108.6539 | 71.6312 |  | 51.7373 | 105.0238 | 55.2106 | 95.2862 | 63.6582 | 61.7639 |  | 69.9349 |  |  | 23.0031 | 25.8573 | 53.0121 | [5 empty] | 21.895 | 61.5104 | 21.6942 | 22.085 | 32.8015 | 21.27 | 21.9181 | 28.4148 | 85.5037 | 174.8903 |  | 76.8545 | 129.0616 | 22.765 | 67.3915 | 145.413 | 45.6724 | 104.5127 | 25.3647 | 104.3603 | 25.3847 | 103.6116 | 18.9198 | 71.9131 | 124.6329 | 29.4798 | 70.0638 | 137.5538 | 22.3657 | 64.2552 | 136.9913 | 23.1041 | 95.6037 | 31.2424 | 101.0483 | 25.8865 | 110.1607 | 1.1515 | 19.2642 | 1.4197 | 0.05269 | -27.1639 | 3.0953 | 194.65 | 52.21 | 1.1493 | -0.55448 | -6.112 | 0.87097 | 0.40173 | -15.0517 | 5.4942 | 0.079093 | -0.72455 | -0.14891 | -1.9955 | -1.3138 | -0.84855 | 0.10154
42838.425 | 406 | 22.9044 | 22.8784 | 22.8584 | 22.7781 | 22.3823 | 21.7092 | 22.7034 | 21.7706 | 22.358 | 22.3564 | 22.335 | 21.9846 | 21.1924 | 22.1558 | 21.6125 | 21.7833 | 21.9078 | 21.0856 | 21.1884 | 21.517 | 20.4742 | 20.8997 | 23.3321 | 21.8778 | 21.8888 | 26.3669 | 133.8954 | 117.7292 | 142.7237 | 22.1214 | 21.8931 | 24.7464 | 22.0255 | 21.9649 | 25.9905 | 58.1416 | 155.7802 |  | 88.9506 | 119.7946 | 117.6976 | 113.5729 |  | 17.239 | 17.842 | 17.0701 | 17.7423 | 18.3292 | 25.7851 | 95.5993 | 15.4018 | 17.11 | 15.7545 | 18.3094 | 18.5354 | 45.1275 | 48.6595 | 44.6144 | 21.631 |  |  | 0.85317 | -0.29577 | -26.6666 | 0.40671 | 0.21172 | -149.9212 | 20.6258 | 0.51482 | -0.026372 | 0.014587 | 0.35426 | 0.00037784 | 0.0003647 | 0.9218 | 21.7975 | 21.9585 | 22.1582 | 22.217 | 22.0192 | 21.3228 | 20.1312 | 22.1843 | 22.3464 | 22.3825 | 22.3414 | 21.96 | 21.1811 | 22.2651 | 69.9917 | 48.1108 | 47.1148 | 33.197 | 29.5226 | 47.8221 | 32.9542 | 22.3252 | 22.0948 | 21.65 | 22.0548 | 21.7791 | 21.3923 | 21.9334 | 21.6673 | 23.5418 | 51.9608 | 132.0712 | 106.7945 | 71.1314 | 0.93897 | 0.052907 | 59.6665 | 21.9059 | 22.239 | 20.4577 | 21.5828 | 22.0331 | 21.9415 | 22.1407 | 29.3639 | 21.8036 | 21.653 | 24.4379 | 137.0784 | 176.7617 | 107.3511 | 108.8438 | 71.7925 |  | 51.912 | 105.2696 | 55.3811 | 96.2804 | 64.0057 | 61.8284 |  | 70.186 |  |  | 23.0259 | 25.9378 | 52.5668 | [5 empty] | 21.9019 | 61.9674 | 21.701 | 22.0888 | 32.8927 | 21.2728 | 21.9232 | 28.4959 | 85.9206 | 176.2199 |  | 77.3075 | 129.6032 | 22.7925 | 67.5387 | 146.0865 | 45.853 | 104.8113 | 25.4109 | 104.5716 | 25.4206 | 103.9852 | 18.9304 | 72.2496 | 124.9094 | 29.5835 | 70.3521 | 138.4411 | 22.3952 | 64.5189 | 137.489 | 23.1504 | 95.9592 | 31.328 | 101.1651 | 25.9365 | 110.5385 | 1.1667 | 19.2616 | 1.4237 | 0.05269 | -27.1531 | 3.0953 | 189.35 | 51.51 | 1.3127 | -0.64652 | -6.1389 | 0.75814 | 0.55442 | -14.7532 | 5.4722 | 0.080829 | -0.72527 | -0.16386 | -1.8615 | -1.0756 | -0.85675 | 0.10093
42838.425 | 407 | 22.9005 | 22.8676 | 22.8479 | 22.7674 | 22.3868 | 21.7135 | 22.7038 | 21.7626 | 22.3531 | 22.354 | 22.3333 | 21.9798 | 21.2007 | 22.1616 | 21.6198 | 21.7876 | 21.9095 | 21.097 | 21.1981 | 21.5284 | 20.4846 | 20.9032 | 23.3541 | 21.8849 | 21.8958 | 26.4052 | 134.714 | 117.9229 | 144.704 | 22.1159 | 21.8835 | 24.7629 | 22.0196 | 21.9716 | 26.0133 | 58.3362 | 158.4446 |  | 89.264 | 120.1917 | 117.9261 | 112.9979 |  | 17.2433 | 17.8484 | 17.0817 | 17.7606 | 18.3541 | 26.0076 | 96.1073 | 15.3898 | 17.109 | 15.7224 | 18.3113 | 18.5298 | 45.1246 | 48.6941 | 44.6082 | 21.6321 |  |  | 0.60609 | -0.29248 | -26.9156 | 0.14518 | -0.058352 | -156.332 | 21.0635 | 0.83615 | 0.018386 | 0.20383 | 0.23639 | 0.00037784 | 0.00035156 | 0.92701 | 21.8054 | 21.9634 | 22.1668 | 22.2139 | 22.0279 | 21.3268 | 20.1364 | 22.1818 | 22.358 | 22.3985 | 22.3448 | 21.9618 | 21.1902 | 22.2669 | 70.462 | 47.087 | 44.0479 | 32.2964 | 29.2878 | 47.9478 | 32.9873 | 22.3199 | 22.0877 | 21.6432 | 22.045 | 21.7726 | 21.3927 | 21.9263 | 21.6598 | 23.5544 | 52.0996 | 132.4456 | 107.098 | 71.7 | 1.2111 | 0.20316 | 60.3484 | 21.9059 | 22.2356 | 20.4558 | 21.5815 | 22.0308 | 21.938 | 22.1504 | 29.4043 | 21.8082 | 21.65 | 24.4511 | 137.5671 | 178.1361 | 107.5407 | 109.0915 | 73.0082 |  | 52.0673 | 105.3976 | 55.5493 | 95.417 | 64.3028 | 61.766 |  | 70.4276 |  |  | 23.0396 | 26.0014 | 52.8996 | [5 empty] | 21.8957 | 62.2927 | 21.6942 | 22.0937 | 32.9822 | 21.2744 | 21.915 | 28.5997 | 86.3533 | 177.8476 |  | 77.8198 | 130.3056 | 22.8142 | 67.7723 | 146.9068 | 46.0957 | 105.0995 | 25.4655 | 104.6991 | 25.4673 | 104.5706 | 18.9376 | 72.6794 | 125.243 | 29.6978 | 70.6265 | 139.0435 | 22.443 | 64.7407 | 138.0303 | 23.1993 | 96.3073 | 31.4392 | 101.4488 | 25.9815 | 111.0808 | 1.053 | 19.2568 | 1.4272 | 0.052741 | -27.1758 | 3.0952 | 182.71 | 52 | 1.109 | -0.64293 | -6.1676 | 0.45296 | -0.29117 | -15.071 | 5.532 | 0.052585 | -0.7228 | -0.12903 | -1.8988 | -0.73093 | -0.83377 | 0.090069
42838.425 | 408 | 22.9044 | 22.8626 | 22.8509 | 22.7651 | 22.3811 | 21.7083 | 22.7075 | 21.7599 | 22.3455 | 22.3565 | 22.3265 | 21.9786 | 21.1853 | 22.1577 | 21.6187 | 21.7822 | 21.9114 | 21.0941 | 21.1992 | 21.5309 | 20.4794 | 20.9077 | 23.3675 | 21.8785 | 21.8962 | 26.4285 | 135.2551 | 118.2543 | 146.2715 | 22.1103 | 21.8864 | 24.7793 | 22.0203 | 21.9712 | 26.0425 | 58.5416 | 160.6977 |  | 89.577 | 120.5217 | 118.2429 | 113.6039 |  | 17.2394 | 17.8654 | 17.0834 | 17.7791 | 18.3839 | 26.1444 | 96.6419 | 15.3726 | 17.1053 | 15.6606 | 18.3174 | 18.5173 | 45.1304 | 48.7105 | 44.5973 | 21.6201 |  |  | 0.49044 | -0.27868 | -27.0372 | 0.31931 | 0.21172 | -153.8271 | 21.2731 | 0.76518 | 0.01138 | 0.055289 | 0.17285 | 0.00036634 | 0.00033842 | 0.91015 | 21.7992 | 21.9631 | 22.1633 | 22.218 | 22.0312 | 21.3264 | 20.1417 | 22.1818 | 22.3617 | 22.3898 | 22.3411 | 21.9666 | 21.1921 | 22.2744 | 71.4316 | 49.208 | 44.6096 | 31.8689 | 28.8994 | 48.0924 | 33.0157 | 22.3323 | 22.0962 | 21.6481 | 22.0574 | 21.7812 | 21.3948 | 21.9385 | 21.6739 | 23.5781 | 52.2644 | 133.4749 | 107.8026 | 72.1207 | 1.0919 | 0.63321 | 60.5372 | 21.9028 | 22.2276 | 20.4439 | 21.5665 | 22.0275 | 21.9262 | 22.1459 | 29.4391 | 21.803 | 21.6446 | 24.469 | 138.222 | 179.116 | 107.8194 | 109.511 | 74.9145 |  | 52.2142 | 104.7345 | 55.6845 | 98.5888 | 64.7303 | 61.7437 |  | 70.6842 |  |  | 23.0636 | 26.0507 | 53.2747 | [5 empty] | 21.9005 | 63.3822 | 21.6929 | 22.0895 | 33.0725 | 21.2761 | 21.9124 | 28.6961 | 86.7863 | 178.8322 |  | 78.2275 | 130.7611 | 22.8272 | 68.0746 | 147.7182 | 46.3388 | 105.455 | 25.5026 | 104.7931 | 25.4978 | 104.8031 | 18.9416 | 73.1251 | 125.6135 | 29.7985 | 70.9201 | 139.7011 | 22.483 | 65.0598 | 138.6701 | 23.2435 | 96.5285 | 31.5722 | 101.7927 | 26.0182 | 111.5906 | 1.2475 | 19.2535 | 1.4309 | 0.053263 | -27.0978 | 3.0952 | 170.96 | 52.22 | 0.9995 | -0.62759 | -6.1817 | 0.67179 | 0.55476 | -14.9532 | 5.5607 | 0.0048598 | -0.69953 | -0.20153 | -1.9894 | -0.79 | -0.8432 | 0.08425
42838.425 | 409 | 22.9035 | 22.8669 | 22.8524 | 22.7673 | 22.3805 | 21.704 | 22.7 | 21.7589 | 22.3518 | 22.3563 | 22.3286 | 21.9811 | 21.1832 | 22.1531 | 21.6097 | 21.7778 | 21.9073 | 21.0858 | 21.1908 | 21.5217 | 20.4724 | 20.9036 | 23.3796 | 21.8689 | 21.8981 | 26.4471 | 135.9654 | 118.5182 | 148.7799 | 22.1145 | 21.8889 | 24.8015 | 22.0312 | 21.9716 | 26.064 | 58.7781 | 162.9387 |  | 89.8987 | 121.0174 | 118.6555 | 114.8354 |  | 17.2471 | 17.8743 | 17.1056 | 17.8089 | 18.4381 | 26.2701 | 97.4648 | 15.3657 | 17.1133 | 15.599 | 18.3372 | 18.5301 | 45.1539 | 48.7525 | 44.605 | 21.6331 |  |  | 0.41093 | -0.45479 | -27.0273 | 0.41788 | 0.21698 | -155.6342 | 20.9859 | 0.54373 | 0.0024286 | 0.17697 | 0.32215 | 0.00035977 | 0.00033513 | 0.90016 | 21.8021 | 21.9694 | 22.1568 | 22.2222 | 22.0233 | 21.3291 | 20.1325 | 22.1833 | 22.3602 | 22.3967 | 22.3414 | 21.9705 | 21.1865 | 22.2634 | 71.4921 | 50.0657 | 47.5382 | 34.1789 | 29.9628 | 48.223 | 33.0776 | 22.3306 | 22.0929 | 21.6539 | 22.0566 | 21.7764 | 21.4056 | 21.9442 | 21.6675 | 23.5962 | 52.4167 | 134.3013 | 108.2863 | 72.7334 | 0.8159 | 0.71842 | 60.5027 | 21.901 | 22.2313 | 20.4556 | 21.5678 | 22.029 | 21.9275 | 22.1519 | 29.4788 | 21.7977 | 21.6487 | 24.4907 | 138.9209 | 180.3118 | 108.1685 | 109.999 | 75.9782 |  | 52.3974 | 104.3957 | 55.8805 | 100.805 | 65.1625 | 61.8809 |  | 70.9973 |  |  | 23.0946 | 26.0989 | 52.9134 | [5 empty] | 21.8939 | 64.2172 | 21.69 | 22.0857 | 33.1506 | 21.2744 | 21.9118 | 28.7734 | 87.2386 | 179.3564 |  | 78.5334 | 131.5245 | 22.8549 | 68.38 | 148.5477 | 46.5998 | 105.94 | 25.5532 | 104.7772 | 25.5358 | 104.974 | 18.951 | 73.5011 | 125.9195 | 29.8981 | 71.2256 | 140.1805 | 22.4996 | 65.4816 | 139.2723 | 23.2804 | 96.7703 | 31.7062 | 102.1594 | 26.0499 | 111.8456 | 1.0455 | 19.2506 | 1.4351 | 0.052596 | -27.0801 | 3.0952 | 189.45 | 52.01 | 0.91763 | -0.80175 | -6.1806 | 0.76853 | 0.56172 | -15.0439 | 5.5242 | -0.018169 | -0.68309 | -0.2473 | -1.9806 | -1.1081 | -0.86888 | 0.072653
42838.425 | 410 | 22.9045 | 22.8734 | 22.8585 | 22.77 | 22.3879 | 21.7132 | 22.7065 | 21.7674 | 22.3509 | 22.3573 | 22.3331 | 21.9861 | 21.1904 | 22.1571 | 21.6133 | 21.7771 | 21.903 | 21.0812 | 21.1891 | 21.5173 | 20.4797 | 20.904 | 23.3927 | 21.8734 | 21.9026 | 26.4722 | 136.6751 | 118.6792 | 149.9936 | 22.1141 | 21.892 | 24.8194 | 22.0231 | 21.9696 | 26.0828 | 59.0061 | 163.7505 |  | 90.2174 | 121.5358 | 119.133 | 115.8357 |  | 17.2555 | 17.8912 | 17.1188 | 17.8358 | 18.4722 | 26.3085 | 98.0837 | 15.3586 | 17.1133 | 15.5925 | 18.3378 | 18.5241 | 45.1726 | 48.7911 | 44.6094 | 21.6306 |  |  | 0.94976 | -0.49224 | -27.2961 | 0.40211 | 0.30372 | -156.5351 | 20.9498 | 0.62521 | -0.1297 | 0.15683 | 0.17354 | 0.00034827 | 0.00035649 | 0.91876 | 21.8057 | 21.9684 | 22.16 | 22.2311 | 22.0354 | 21.3307 | 20.1418 | 22.1897 | 22.3556 | 22.3944 | 22.3448 | 21.9694 | 21.1977 | 22.2716 | 70.8966 | 48.9513 | 48.6484 | 35.5353 | 30.7812 | 48.3363 | 33.1484 | 22.321 | 22.0884 | 21.6465 | 22.0508 | 21.7665 | 21.3962 | 21.9282 | 21.6629 | 23.6021 | 52.5573 | 134.9525 | 108.5761 | 72.7542 | 1.1145 | 0.54476 | 60.7019 | 21.9055 | 22.2319 | 20.4627 | 21.5722 | 22.029 | 21.9336 | 22.1605 | 29.5194 | 21.7998 | 21.6568 | 24.5172 | 139.6187 | 181.6346 | 108.4643 | 110.4207 | 75.711 |  | 52.5446 | 104.9661 | 56.0682 | 100.0133 | 65.4639 | 62.2178 |  | 71.2683 |  |  | 23.133 | 26.1558 | 52.89 | [5 empty] | 21.8952 | 64.5744 | 21.6917 | 22.0879 | 33.253 | 21.2772 | 21.9191 | 28.856 | 87.6994 | 180.1737 |  | 78.9148 | 132.4404 | 22.876 | 68.6572 | 149.4611 | 46.9072 | 106.4232 | 25.5988 | 105.0579 | 25.5744 | 105.2069 | 18.9523 | 73.9783 | 126.2032 | 29.9991 | 71.5086 | 140.6628 | 22.5347 | 65.8584 | 139.766 | 23.3222 | 97.0532 | 31.8343 | 102.6709 | 26.0908 | 112.1258 | 1.2004 | 19.2464 | 1.4379 | 0.053031 | -27.3255 | 3.0952 | 191.06 | 52.78 | 1.3971 | -0.83413 | -6.2115 | 0.7539 | 0.66462 | -15.0883 | 5.5198 | -0.0055036 | -0.69221 | -0.21428 | -1.901 | -1.2231 | -0.88844 | 0.077082
42838.425 | 411 | 22.9112 | 22.8715 | 22.8546 | 22.7708 | 22.3903 | 21.7131 | 22.7099 | 21.7597 | 22.3487 | 22.3608 | 22.3359 | 21.981 | 21.1903 | 22.1612 | 21.6115 | 21.7826 | 21.9072 | 21.0812 | 21.1974 | 21.5195 | 20.4814 | 20.9118 | 23.4128 | 21.8762 | 21.9038 | 26.4942 | 137.2452 | 118.9251 | 150.5017 | 22.1117 | 21.8914 | 24.8443 | 22.0229 | 21.9753 | 26.1134 | 59.2375 | 165.2462 |  | 90.592 | 121.9578 | 119.5892 | 116.2438 |  | 17.2645 | 17.9007 | 17.1346 | 17.8571 | 18.567 | 26.4255 | 98.9044 | 15.3952 | 17.1135 | 15.6593 | 18.3388 | 18.5354 | 45.2088 | 48.8155 | 44.622 | 21.6279 |  |  | 0.56469 | -0.55073 | -27.3749 | 0.47768 | 0.35038 | -151.2223 | 20.4602 | 0.9702 | -0.036686 | 0.17005 | 0.32735 | 0.00035649 | 0.00036306 | 0.93409 | 21.8013 | 21.9698 | 22.1569 | 22.2166 | 22.0296 | 21.3277 | 20.1383 | 22.1762 | 22.3544 | 22.3926 | 22.3331 | 21.9635 | 21.1844 | 22.2623 | 71.7092 | 49.9746 | 49.351 | 36.4742 | 30.9999 | 48.4929 | 33.2206 | 22.3192 | 22.0829 | 21.6511 | 22.05 | 21.7693 | 21.3955 | 21.9302 | 21.6661 | 23.6176 | 52.7024 | 135.7408 | 108.9063 | 73.1126 | 1.5052 | 0.65128 | 60.9358 | 21.9045 | 22.2274 | 20.4592 | 21.574 | 22.0287 | 21.933 | 22.1649 | 29.5585 | 21.7962 | 21.6532 | 24.5373 | 140.2489 | 182.778 | 108.6946 | 110.7484 | 75.0724 |  | 52.676 | 105.7193 | 56.239 | 99.7077 | 65.7625 | 62.3888 |  | 71.5767 |  |  | 23.166 | 26.2088 | 53.3204 | [5 empty] | 21.8908 | 64.9246 | 21.6905 | 22.081 | 33.3657 | 21.2766 | 21.9093 | 28.9438 | 88.1334 | 181.8193 |  | 79.4512 | 133.2676 | 22.8965 | 68.8105 | 150.7937 | 47.2517 | 106.9397 | 25.6374 | 105.5427 | 25.62 | 105.3997 | 18.9408 | 74.659 | 126.6703 | 30.101 | 71.754 | 141.3627 | 22.5749 | 66.2168 | 140.1392 | 23.3471 | 97.2879 | 31.9501 | 102.9993 | 26.1431 | 112.5106 | 1.1618 | 19.2435 | 1.4413 | 0.052058 | -27.2017 | 3.0953 | 190.1 | 51.71 | 1.0779 | -0.88231 | -6.2205 | 0.82171 | 0.71398 | -14.833 | 5.456 | 0.016912 | -0.707 | -0.19487 | -1.9727 | -1.2927 | -0.89142 | 0.072295
42838.425 | 412 | 22.904 | 22.8689 | 22.8576 | 22.77 | 22.3852 | 21.7149 | 22.7053 | 21.7597 | 22.3579 | 22.3648 | 22.3358 | 21.9789 | 21.1907 | 22.1663 | 21.6152 | 21.7895 | 21.9137 | 21.0848 | 21.1987 | 21.5235 | 20.4795 | 20.9164 | 23.4322 | 21.8828 | 21.9066 | 26.5229 | 137.8403 | 119.3928 | 152.3869 | 22.1148 | 21.8908 | 24.8625 | 22.0108 | 21.9745 | 26.1458 | 59.4392 | 166.228 |  | 90.9628 | 122.4261 | 120.0613 | 116.9542 |  | 17.2671 | 17.9136 | 17.1375 | 17.8781 | 18.6396 | 26.5094 | 99.6823 | 15.4527 | 17.1201 | 15.6862 | 18.3491 | 18.5284 | 45.2265 | 48.8502 | 44.6175 | 21.6212 |  |  | 0.72109 | -0.41076 | -27.7587 | 0.36991 | 0.18412 | -155.9496 | 20.2959 | 0.78161 | -0.11044 | 0.16732 | 0.19073 | 0.00036799 | 0.00037127 | 0.93244 | 21.8017 | 21.9631 | 22.157 | 22.2218 | 22.0262 | 21.3226 | 20.1317 | 22.18 | 22.3604 | 22.3893 | 22.334 | 21.9623 | 21.187 | 22.2644 | 73.6484 | 51.4957 | 50.8387 | 36.6286 | 31.1889 | 48.6862 | 33.3104 | 22.3211 | 22.0872 | 21.6494 | 22.0498 | 21.7805 | 21.3985 | 21.9363 | 21.6651 | 23.6358 | 52.8557 | 136.373 | 109.5156 | 74.0979 | 1.1069 | 0.80743 | 61.2013 | 21.9015 | 22.2293 | 20.4605 | 21.5711 | 22.0242 | 21.9317 | 22.1652 | 29.597 | 21.8002 | 21.6543 | 24.5505 | 140.8919 | 184.162 | 108.9046 | 111.0086 | 74.1882 |  | 52.8249 | 106.4439 | 56.4385 | 98.577 | 66.0909 | 62.8082 |  | 71.8926 |  |  | 23.2054 | 26.2661 | 53.4395 | [5 empty] | 21.8874 | 65.1343 | 21.6954 | 22.0795 | 33.4864 | 21.2728 | 21.9068 | 29.04 | 88.5813 | 183.3443 |  | 79.928 | 134.1318 | 22.9188 | 69.0548 | 152.2354 | 47.597 | 107.4256 | 25.6908 | 105.7589 | 25.6573 | 105.6125 | 18.9348 | 75.234 | 127.2259 | 30.2114 | 72.0059 | 142.302 | 22.6102 | 66.6976 | 140.7432 | 23.3703 | 97.6069 | 32.0521 | 103.273 | 26.1881 | 113.1069 | 1.4286 | 19.2411 | 1.4443 | 0.052842 | -27.1925 | 3.0952 | 199.17 | 52.65 | 1.2208 | -0.762 | -6.2641 | 0.72312 | 0.51765 | -15.0651 | 5.4348 | 0.04678 | -0.71997 | -0.15143 | -2.1653 | -1.4475 | -0.90387 | 0.050387
42838.4251 | 413 | 22.904 | 22.868 | 22.8459 | 22.7656 | 22.386 | 21.714 | 22.7035 | 21.7596 | 22.356 | 22.3569 | 22.3263 | 21.9787 | 21.1829 | 22.1653 | 21.6125 | 21.7863 | 21.9075 | 21.0893 | 21.1929 | 21.5259 | 20.4815 | 20.9104 | 23.4432 | 21.8816 | 21.912 | 26.5473 | 138.69 | 120.0487 | 154.7533 | 22.1143 | 21.8944 | 24.8774 | 22.0221 | 21.9721 | 26.1671 | 59.6959 | 169.4507 |  | 91.4216 | 122.9935 | 120.6114 | 117.9502 |  | 17.265 | 17.9391 | 17.1548 | 17.8922 | 18.6932 | 26.5135 | 100.3307 | 15.4588 | 17.1115 | 15.6913 | 18.3572 | 18.522 | 45.2415 | 48.8777 | 44.6283 | 21.6217 |  |  | 0.75854 | -0.45873 | -27.7771 | 0.34626 | 0.23604 | -157.4117 | 20.7954 | 0.68172 | -0.11102 | 0.10648 | 0.26434 | 0.00036634 | 0.00033349 | 0.91834 | 21.8049 | 21.9669 | 22.1591 | 22.2251 | 22.0251 | 21.3158 | 20.1403 | 22.1769 | 22.3568 | 22.3928 | 22.3389 | 21.9602 | 21.1939 | 22.2671 | 74.8326 | 52.4167 | 54.494 | 37.5483 | 31.9201 | 48.8736 | 33.4377 | 22.3218 | 22.0895 | 21.6479 | 22.046 | 21.7675 | 21.4079 | 21.9281 | 21.6629 | 23.659 | 53.0165 | 137.4147 | 109.9987 | 74.6553 | 0.91125 | 0.71708 | 61.3693 | 21.8986 | 22.2262 | 20.4583 | 21.5668 | 22.0232 | 21.9415 | 22.1698 | 29.6465 | 21.8051 | 21.6582 | 24.5725 | 141.5616 | 186.0265 | 109.1952 | 111.28 | 73.967 |  | 52.9872 | 106.5926 | 56.6149 | 97.5044 | 66.4425 | 63.5669 |  | 72.176 |  |  | 23.2447 | 26.3323 | 53.5617 | [5 empty] | 21.8919 | 65.2664 | 21.697 | 22.085 | 33.6008 | 21.274 | 21.9106 | 29.1357 | 89.0348 | 184.7584 |  | 80.1931 | 134.9444 | 22.9337 | 69.3615 | 153.1498 | 47.8742 | 107.8421 | 25.7454 | 106.0337 | 25.6946 | 105.8478 | 18.9472 | 75.8122 | 127.8077 | 30.3312 | 72.3 | 143.5116 | 22.6413 | 67.3379 | 141.4399 | 23.4022 | 97.9507 | 32.1446 | 103.6952 | 26.2472 | 113.7883 | 1.3349 | 19.2372 | 1.4479 | 0.052494 | -27.0853 | 3.0953 | 194.73 | 52.32 | 1.2555 | -0.8053 | -6.2665 | 0.69965 | 0.5861 | -15.1357 | 5.5013 | 0.05871 | -0.71777 | -0.10876 | -2.2746 | -1.8386 | -0.92226 | 0.040634
42838.4251 | 414 | 22.8945 | 22.8658 | 22.8571 | 22.7683 | 22.3848 | 21.7064 | 22.7024 | 21.7517 | 22.3481 | 22.3463 | 22.3258 | 21.9787 | 21.1899 | 22.1531 | 21.5997 | 21.7788 | 21.8962 | 21.0838 | 21.1871 | 21.5193 | 20.4779 | 20.9092 | 23.4532 | 21.8737 | 21.9062 | 26.5695 | 139.6651 | 120.7831 | 157.7076 | 22.1071 | 21.8962 | 24.8903 | 22.0229 | 21.9697 | 26.2006 | 59.9475 | 172.3964 |  | 91.8569 | 123.5052 | 121.1236 | 117.9675 |  | 17.2728 | 17.9567 | 17.1536 | 17.9161 | 18.7307 | 26.5517 | 101.1612 | 15.3958 | 17.1146 | 15.7113 | 18.3686 | 18.5231 | 45.2464 | 48.9012 | 44.6385 | 21.6205 |  |  | 0.82294 | -0.39236 | -27.8862 | 0.22075 | 0.41477 | -157.5011 | 20.4589 | 0.77635 | -0.40526 | 0.10165 | 0.21243 | 0.00040248 | 0.00033184 | 0.92558 | 21.8046 | 21.9635 | 22.1607 | 22.2221 | 22.0244 | 21.3221 | 20.139 | 22.1738 | 22.3581 | 22.3955 | 22.3365 | 21.9567 | 21.1864 | 22.2644 | 75.4103 | 52.2091 | 55.0037 | 38.9164 | 32.8919 | 49.056 | 33.5454 | 22.3259 | 22.0948 | 21.647 | 22.0509 | 21.7735 | 21.4039 | 21.9321 | 21.6682 | 23.6804 | 53.1992 | 138.1677 | 110.3859 | 75.439 | 1.0835 | 0.34372 | 61.4395 | 21.9017 | 22.2269 | 20.4703 | 21.5656 | 22.0274 | 21.9408 | 22.1804 | 29.6935 | 21.8026 | 21.6648 | 24.5942 | 142.3141 | 187.6874 | 109.5159 | 111.6943 | 74.2813 |  | 53.1462 | 106.4919 | 56.7737 | 97.5446 | 66.8259 | 64.2916 |  | 72.45 |  |  | 23.2797 | 26.4031 | 53.6211 | [5 empty] | 21.8953 | 65.694 | 21.6963 | 22.0889 | 33.6946 | 21.2714 | 21.9134 | 29.2283 | 89.4883 | 186.7222 |  | 80.4471 | 135.6882 | 22.9587 | 69.5891 | 153.7925 | 48.1583 | 108.2353 | 25.7994 | 106.3682 | 25.7454 | 106.0063 | 18.9519 | 76.4107 | 128.273 | 30.457 | 72.6518 | 144.4733 | 22.6893 | 68.0386 | 142.0591 | 23.4426 | 98.1536 | 32.2317 | 104.2683 | 26.2951 | 114.3049 | 1.1246 | 19.236 | 1.4513 | 0.052356 | -27.0429 | 3.0952 | 203.17 | 51.9 | 1.3123 | -0.7448 | -6.279 | 0.55865 | 0.77699 | -15.141 | 5.457 | 0.055649 | -0.70927 | -0.095811 | -2.3172 | -1.8826 | -0.91365 | 0.025381
42838.4251 | 415 | 22.892 | 22.8704 | 22.8432 | 22.7726 | 22.381 | 21.7071 | 22.7058 | 21.7569 | 22.3487 | 22.3532 | 22.3179 | 21.9752 | 21.1892 | 22.1555 | 21.6058 | 21.7818 | 21.9139 | 21.084 | 21.1923 | 21.5253 | 20.4805 | 20.9108 | 23.4666 | 21.8774 | 21.9158 | 26.5898 | 140.5163 | 121.4317 | 158.716 | 22.1057 | 21.8976 | 24.9119 | 22.0153 | 21.9757 | 26.2229 | 60.1741 | 174.4414 |  | 92.2914 | 124.0057 | 121.6873 | 118.5479 |  | 17.2826 | 17.9661 | 17.1459 | 17.9339 | 18.7393 | 26.6776 | 101.9417 | 15.3551 | 17.1118 | 15.7484 | 18.3683 | 18.5339 | 45.2699 | 48.9339 | 44.6452 | 21.6216 |  |  | 0.6718 | -0.27343 | -27.7521 | 0.34626 | 0.38586 | -152.4406 | 20.2493 | 0.81775 | -0.067433 | 0.25502 | 0.41311 | 0.00039098 | 0.0003532 | 0.91495 | 21.8103 | 21.9621 | 22.1634 | 22.2122 | 22.0286 | 21.3268 | 20.1399 | 22.1763 | 22.3581 | 22.3968 | 22.3429 | 21.9561 | 21.1883 | 22.2665 | 75.2968 | 51.5486 | 54.3195 | 37.8635 | 32.7127 | 49.2043 | 33.6369 | 22.3178 | 22.0895 | 21.6441 | 22.0465 | 21.7739 | 21.4059 | 21.9333 | 21.6717 | 23.6916 | 53.3604 | 138.9575 | 110.7978 | 76.1613 | 0.92482 | 0.41315 | 61.5118 | 21.8997 | 22.2189 | 20.4698 | 21.5659 | 22.0237 | 21.9331 | 22.1835 | 29.7301 | 21.7994 | 21.6678 | 24.6146 | 143.0257 | 189.1774 | 109.8786 | 112.2039 | 74.5283 |  | 53.3044 | 106.6905 | 56.9443 | 97.7753 | 67.1532 | 65.4401 |  | 72.7575 |  |  | 23.3058 | 26.4592 | 53.5602 | [5 empty] | 21.8916 | 65.704 | 21.6876 | 22.0857 | 33.7769 | 21.2711 | 21.9133 | 29.3391 | 89.9679 | 188.7081 |  | 80.8612 | 136.3075 | 22.9925 | 69.9876 | 155.0359 | 48.471 | 108.6591 | 25.8535 | 106.5827 | 25.7885 | 106.1829 | 18.9597 | 76.8637 | 128.8244 | 30.561 | 73.0526 | 145.4132 | 22.7244 | 68.416 | 143.0602 | 23.4818 | 98.3116 | 32.3475 | 104.6309 | 26.3433 | 115.0042 | 1.5289 | 19.2338 | 1.4547 | 0.053931 | -27.2756 | 3.0952 | 214.36 | 55.9 | 1.187 | -0.62175 | -6.2639 | 0.69968 | 0.74958 | -14.8989 | 5.4301 | 0.054429 | -0.70865 | -0.090205 | -2.2869 | -1.7958 | -0.92157 | 0.011065
42838.4251 | 416 | 22.9004 | 22.8656 | 22.8527 | 22.7752 | 22.3785 | 21.7133 | 22.7105 | 21.7659 | 22.3558 | 22.3566 | 22.3286 | 21.979 | 21.1902 | 22.1602 | 21.6071 | 21.7762 | 21.9067 | 21.0849 | 21.1911 | 21.5226 | 20.4787 | 20.9172 | 23.4895 | 21.8753 | 21.9251 | 26.6226 | 141.1514 | 121.961 | 159.647 | 22.1008 | 21.8938 | 24.9341 | 22.0198 | 21.9767 | 26.2467 | 60.4136 | 176.7021 |  | 92.7481 | 124.5664 | 122.1463 | 118.9593 |  | 17.291 | 17.9863 | 17.1691 | 17.9586 | 18.7598 | 26.7329 | 102.6621 | 15.3541 | 17.1165 | 15.7273 | 18.3728 | 18.5325 | 45.2941 | 48.9593 | 44.6622 | 21.6262 |  |  | 0.67575 | -0.44231 | -27.6312 | 0.055154 | 0.23341 | -155.3431 | 19.7335 | 0.92026 | -0.064903 | 0.10291 | 0.38568 | 0.00038606 | 0.00036799 | 0.91117 | 21.809 | 21.9691 | 22.1724 | 22.2207 | 22.0313 | 21.3353 | 20.1464 | 22.1737 | 22.3632 | 22.3965 | 22.3478 | 21.9576 | 21.1874 | 22.2722 | 74.1643 | 50.333 | 54.3255 | 37.6998 | 31.8766 | 49.3224 | 33.7307 | 22.3207 | 22.0927 | 21.6531 | 22.0588 | 21.7782 | 21.4098 | 21.9424 | 21.6732 | 23.7128 | 53.5228 | 140.2629 | 111.4192 | 76.5281 | 0.39361 | 0.56664 | 61.6817 | 21.9042 | 22.2202 | 20.4694 | 21.5736 | 22.0296 | 21.9387 | 22.1843 | 29.7743 | 21.8012 | 21.6666 | 24.6309 | 143.6861 | 190.5861 | 110.2258 | 112.7297 | 75.0012 |  | 53.4736 | 106.9661 | 57.1488 | 102.2654 | 67.6654 | 66.1832 |  | 73.0608 |  |  | 23.3424 | 26.5311 | 53.6569 | [5 empty] | 21.9026 | 67.161 | 21.7025 | 22.0917 | 33.8637 | 21.2819 | 21.9205 | 29.4387 | 90.457 | 189.7915 |  | 81.3518 | 136.9714 | 23.0289 | 70.4982 | 156.5248 | 48.7565 | 109.0768 | 25.9032 | 106.8659 | 25.8386 | 106.3069 | 18.9723 | 77.318 | 129.6997 | 30.6745 | 73.4399 | 146.1698 | 22.7595 | 68.529 | 144.1124 | 23.5048 | 98.4969 | 32.4907 | 104.903 | 26.41 | 115.4856 | 1.029 | 19.2307 | 1.4578 | 0.053873 | -27.1914 | 3.0952 | 215.32 | 54.73 | 1.1918 | -0.79082 | -6.2505 | 0.27926 | 0.58304 | -15.0414 | 5.361 | 0.047327 | -0.70896 | -0.19611 | -2.1471 | -1.7854 | -0.92433 | 0.0066683
42838.4251 | 417 | 22.9077 | 22.8674 | 22.8555 | 22.7683 | 22.3766 | 21.707 | 22.7017 | 21.7614 | 22.3556 | 22.3531 | 22.3245 | 21.9754 | 21.1903 | 22.1564 | 21.604 | 21.7914 | 21.9077 | 21.0886 | 21.1952 | 21.5379 | 20.4871 | 20.9261 | 23.5218 | 21.8866 | 21.918 | 26.6479 | 142.0648 | 122.5999 | 161.3477 | 22.1078 | 21.9018 | 24.9563 | 22.0171 | 21.9845 | 26.2734 | 60.6522 | 175.9 |  | 93.1378 | 125.1554 | 122.6937 | 119.3143 |  | 17.2898 | 17.9906 | 17.1763 | 17.9731 | 18.7617 | 26.7216 | 103.2972 | 15.3687 | 17.1174 | 15.7213 | 18.3827 | 18.5332 | 45.3229 | 48.9705 | 44.6788 | 21.6253 |  |  | 0.57586 | -0.44099 | -27.6365 | 0.47965 | 0.045472 | -156.2716 | 20.1717 | 0.82695 | 0.12425 | 0.39181 | 0.3902 | 0.0003877 | 0.00036799 | 0.91269 | 21.8091 | 21.966 | 22.1615 | 22.2208 | 22.0316 | 21.3195 | 20.1346 | 22.1824 | 22.364 | 22.4003 | 22.3458 | 21.9617 | 21.1762 | 22.2729 | 72.8654 | 47.1355 | 53.3962 | 37.3223 | 31.93 | 49.4042 | 33.8076 | 22.3196 | 22.0877 | 21.657 | 22.0525 | 21.7743 | 21.4068 | 21.9412 | 21.6735 | 23.7259 | 53.6762 | 141.4072 | 112.2244 | 77.0945 | 1.2176 | 0.14744 | 61.6647 | 21.9018 | 22.2308 | 20.4774 | 21.5721 | 22.0329 | 21.9397 | 22.1855 | 29.8223 | 21.8034 | 21.6687 | 24.6518 | 144.3053 | 192.4493 | 110.5353 | 113.2274 | 76.0908 |  | 53.6453 | 106.7211 | 57.3294 | 102.3696 | 68.0302 | 66.6049 |  | 73.3425 |  |  | 23.3797 | 26.5806 | 54.5687 | [5 empty] | 21.8829 | 67.7682 | 21.6899 | 22.0879 | 33.9016 | 21.2653 | 21.9066 | 29.555 | 90.9462 | 190.6487 |  | 81.8663 | 137.5716 | 23.0687 | 71.0031 | 157.3872 | 49.0862 | 109.5258 | 25.9533 | 107.3551 | 25.8903 | 106.7701 | 18.9876 | 77.898 | 130.5104 | 30.7925 | 73.7986 | 147.0819 | 22.7979 | 68.8875 | 144.9751 | 23.539 | 98.8403 | 32.6044 | 105.1329 | 26.4694 | 115.7167 | 1.0902 | 19.2275 | 1.4616 | 0.052523 | -27.0357 | 3.0952 | 206.86 | 56.37 | 1.1024 | -0.78965 | -6.2511 | 0.82353 | 0.25734 | -15.086 | 5.4201 | 0.02319 | -0.69566 | -0.1856 | -1.9931 | -1.6731 | -0.92556 | -0.0035866
42838.4251 | 418 | 22.8954 | 22.8618 | 22.8517 | 22.7672 | 22.3846 | 21.706 | 22.7005 | 21.7628 | 22.3539 | 22.354 | 22.3198 | 21.9817 | 21.1868 | 22.1591 | 21.6101 | 21.7844 | 21.9107 | 21.0857 | 21.184 | 21.5315 | 20.4758 | 20.9275 | 23.5468 | 21.8783 | 21.9265 | 26.6746 | 142.8414 | 123.1178 | 161.4585 | 22.1107 | 21.9028 | 24.9739 | 22.0138 | 21.9853 | 26.3069 | 60.9081 | 176.9342 |  | 93.5546 | 125.5761 | 123.1504 | 119.8779 |  | 17.288 | 17.9909 | 17.1864 | 17.9789 | 18.7535 | 26.8476 | 103.8691 | 15.412 | 17.1192 | 15.6785 | 18.3795 | 18.5392 | 45.3562 | 48.9982 | 44.7043 | 21.6222 |  |  | 0.71517 | -0.28657 | -27.5655 | 0.59859 | 0.27678 | -153.8449 | 20.043 | 0.74744 | 0.10167 | 0.019413 | 0.27649 | 0.00039591 | 0.0003532 | 0.90169 | 21.8043 | 21.9614 | 22.1611 | 22.2129 | 22.0306 | 21.3217 | 20.1369 | 22.1791 | 22.3598 | 22.3921 | 22.3417 | 21.9522 | 21.1896 | 22.2687 | 74.2609 | 47.9336 | 51.0246 | 36.2838 | 31.2669 | 49.5591 | 33.8577 | 22.3156 | 22.0825 | 21.6531 | 22.0455 | 21.7699 | 21.4146 | 21.9312 | 21.6725 | 23.7382 | 53.8664 | 142.6158 | 112.7785 | 77.4053 | 1.5317 | 0.7654 | 61.6629 | 21.9015 | 22.2352 | 20.4812 | 21.5774 | 22.0277 | 21.9427 | 22.1942 | 29.8646 | 21.8007 | 21.6707 | 24.6763 | 145.2829 | 194.1875 | 110.8807 | 113.7334 | 77.027 |  | 53.8125 | 107.0281 | 57.5311 | 101.4553 | 68.3294 | 67.3976 |  | 73.6311 |  |  | 23.4249 | 26.6477 | 54.764 | [5 empty] | 21.8982 | 67.4807 | 21.7012 | 22.0862 | 34.0151 | 21.2633 | 21.9192 | 29.66 | 91.5056 | 191.8108 |  | 82.3755 | 138.4742 | 23.1083 | 71.4987 | 158.0964 | 49.4268 | 109.9453 | 25.9952 | 107.7313 | 25.9338 | 107.2793 | 19.0008 | 78.4956 | 131.4115 | 30.8849 | 74.0967 | 148.1488 | 22.8488 | 69.4426 | 145.6741 | 23.5712 | 99.2987 | 32.7461 | 105.537 | 26.5319 | 115.9566 | 1.0798 | 19.2229 | 1.4645 | 0.052182 | -27.0766 | 3.0953 | 195.29 | 55.23 | 1.2286 | -0.63655 | -6.2431 | 0.91999 | 0.63502 | -14.9716 | 5.4039 | 0.003153 | -0.69693 | -0.14919 | -2.1297 | -1.4037 | -0.93194 | -0.0054304
42838.4251 | 419 | 22.8925 | 22.8593 | 22.8514 | 22.7654 | 22.3781 | 21.7089 | 22.6941 | 21.758 | 22.3547 | 22.3597 | 22.3336 | 21.9685 | 21.1896 | 22.1648 | 21.604 | 21.7836 | 21.8978 | 21.0816 | 21.1889 | 21.5272 | 20.4752 | 20.9229 | 23.5466 | 21.8763 | 21.9203 | 26.6893 | 143.677 | 123.5517 | 163.7212 | 22.1201 | 21.9014 | 24.9973 | 22.0227 | 21.9878 | 26.348 | 61.1809 | 178.8629 |  | 94.0108 | 126.0063 | 123.6425 | 121.4611 |  | 17.2924 | 18.0091 | 17.2133 | 18.0079 | 18.7506 | 26.9989 | 104.7289 | 15.4362 | 17.1195 | 15.6273 | 18.3959 | 18.544 | 45.3877 | 49.0145 | 44.725 | 21.6211 |  |  | 0.57389 | -0.33585 | -27.3552 | 0.226 | 0.56131 | -153.9723 | 20.4011 | 0.82169 | 0.01897 | 0.050463 | 0.49661 | 0.00038441 | 0.0003647 | 0.89164 | 21.8061 | 21.9604 | 22.1659 | 22.2087 | 22.032 | 21.32 | 20.1361 | 22.1823 | 22.3538 | 22.3927 | 22.3452 | 21.9606 | 21.1903 | 22.2663 | 77.5929 | 51.8297 | 55.5089 | 37.4078 | 31.0605 | 49.7585 | 33.9779 | 22.3176 | 22.0858 | 21.6484 | 22.052 | 21.774 | 21.4217 | 21.9392 | 21.6807 | 23.7634 | 54.0315 | 142.9913 | 113.1992 | 77.7419 | 1.1269 | 0.83862 | 61.9036 | 21.9041 | 22.229 | 20.4828 | 21.5765 | 22.0247 | 21.9458 | 22.1982 | 29.8986 | 21.8033 | 21.666 | 24.6849 | 146.108 | 195.5819 | 111.3074 | 114.2578 | 77.9929 |  | 54.0031 | 107.5716 | 57.7633 | 101.4049 | 68.7639 | 67.5203 |  | 74.0392 |  |  | 23.4707 | 26.693 | 55.0729 | [5 empty] | 21.887 | 67.8315 | 21.69 | 22.0934 | 34.158 | 21.2629 | 21.9054 | 29.7836 | 92.0573 | 193.3351 |  | 82.7935 | 139.3634 | 23.143 | 71.7177 | 159.303 | 49.7549 | 110.3283 | 26.0169 | 108.1029 | 25.9689 | 107.4244 | 18.9968 | 79.0175 | 132.3541 | 31.0004 | 74.4077 | 149.3551 | 22.8839 | 69.9615 | 146.4635 | 23.6004 | 99.5792 | 32.8793 | 106.1398 | 26.5825 | 116.3482 | 1.168 | 19.221 | 1.4672 | 0.052835 | -27.0528 | 3.0952 | 211.11 | 55.65 | 1.1035 | -0.68914 | -6.2195 | 0.56531 | 0.90456 | -14.9815 | 5.4533 | -0.016871 | -0.70367 | -0.13179 | -2.4763 | -1.8878 | -0.96603 | -0.0088874
42838.4251 | 420 | 22.8911 | 22.8518 | 22.8441 | 22.7574 | 22.379 | 21.7065 | 22.6976 | 21.7605 | 22.3461 | 22.3503 | 22.3216 | 21.9665 | 21.1858 | 22.1611 | 21.6104 | 21.7811 | 21.9009 | 21.0798 | 21.1929 | 21.535 | 20.4746 | 20.9336 | 23.5646 | 21.8786 | 21.9239 | 26.7189 | 144.4681 | 124.0396 | 164.5966 | 22.115 | 21.9045 | 25.0187 | 22.026 | 21.998 | 26.3646 | 61.4376 | 178.0457 |  | 94.3877 | 126.5444 | 124.1466 | 121.6581 |  | 17.3002 | 18.0174 | 17.2151 | 18.0137 | 18.759 | 27.121 | 105.2229 | 15.4674 | 17.1161 | 15.593 | 18.4058 | 18.5519 | 45.4151 | 49.0395 | 44.7492 | 21.6258 |  |  | 0.89522 | -0.45413 | -27.5931 | 0.56573 | 0.36549 | -153.4532 | 20.2789 | 0.85586 | -0.023259 | 0.4472 | 0.30895 | 0.00037456 | 0.00037127 | 0.88856 | 21.8009 | 21.9549 | 22.1624 | 22.2101 | 22.0277 | 21.3152 | 20.1327 | 22.1753 | 22.3458 | 22.3891 | 22.3383 | 21.9524 | 21.1804 | 22.2613 | 77.3642 | 50.991 | 56.942 | 37.7906 | 31.9433 | 49.9187 | 34.0932 | 22.321 | 22.0852 | 21.6467 | 22.0526 | 21.77 | 21.4176 | 21.9401 | 21.6826 | 23.7748 | 54.1963 | 143.3998 | 113.6315 | 78.4631 | 1.2014 | 0.33307 | 62.4265 | 21.9046 | 22.2284 | 20.48 | 21.5743 | 22.0268 | 21.948 | 22.2057 | 29.9426 | 21.8081 | 21.6741 | 24.704 | 146.8848 | 196.9307 | 111.7467 | 114.7311 | 78.5159 |  | 54.1502 | 108.3336 | 57.9507 | 102.0443 | 69.1268 | 67.6151 |  | 74.3638 |  |  | 23.5031 | 26.7626 | 55.1062 | [5 empty] | 21.8923 | 68.464 | 21.6923 | 22.0891 | 34.3004 | 21.2706 | 21.9165 | 29.8855 | 92.5161 | 194.4397 |  | 83.1432 | 140.1572 | 23.1806 | 72.0931 | 160.4233 | 50.069 | 110.9749 | 26.0583 | 108.6257 | 26.0215 | 107.6119 | 18.9943 | 79.7534 | 132.8729 | 31.0989 | 74.7158 | 150.7422 | 22.9399 | 70.3658 | 147.3377 | 23.6325 | 99.9913 | 32.9869 | 106.5498 | 26.6335 | 117.0845 | 1.3429 | 19.2159 | 1.47 | 0.052254 | -27.1015 | 3.0953 | 201.97 | 55.79 | 1.3796 | -0.80136 | -6.2465 | 0.89443 | 0.73006 | -14.9593 | 5.4381 | -0.026145 | -0.71809 | -0.13617 | -2.4318 | -2.0335 | -0.96219 | -0.023032
42838.4252 | 421 | 22.9018 | 22.8659 | 22.8462 | 22.768 | 22.381 | 21.7045 | 22.7074 | 21.7644 | 22.3518 | 22.3548 | 22.3304 | 21.9777 | 21.1917 | 22.1696 | 21.604 | 21.7736 | 21.9016 | 21.0784 | 21.1959 | 21.5377 | 20.4747 | 20.9221 | 23.5752 | 21.8754 | 21.9362 | 26.7418 | 145.4736 | 124.7417 | 165.5198 | 22.1099 | 21.8999 | 25.0362 | 22.0159 | 21.9927 | 26.3892 | 61.6885 | 179.1318 |  | 94.8384 | 127.0901 | 124.597 | 121.674 |  | 17.324 | 18.0492 | 17.2398 | 18.033 | 18.7764 | 27.3646 | 105.8401 | 15.5286 | 17.1246 | 15.5976 | 18.4147 | 18.5456 | 45.44 | 49.0545 | 44.7535 | 21.623 |  |  | 0.72043 | -0.41865 | -27.6029 | 0.57099 | 0.022472 | -153.0754 | 20.6981 | 0.93537 | 0.027337 | 0.16795 | 0.04317 | 0.00034499 | 0.0003762 | 0.88212 | 21.8051 | 21.9563 | 22.1611 | 22.2069 | 22.0232 | 21.3136 | 20.1318 | 22.1734 | 22.3464 | 22.3915 | 22.3354 | 21.9524 | 21.1804 | 22.264 | 78.6826 | 51.9486 | 56.0122 | 37.4934 | 31.7367 | 50.125 | 34.1887 | 22.3213 | 22.0873 | 21.6501 | 22.0512 | 21.7757 | 21.4144 | 21.9343 | 21.69 | 23.7943 | 54.3677 | 143.5079 | 113.926 | 79.5966 | 1.329 | 0.85061 | 62.9387 | 21.9017 | 22.2295 | 20.4794 | 21.5681 | 22.022 | 21.948 | 22.2036 | 29.9787 | 21.7971 | 21.6773 | 24.7266 | 147.7006 | 197.8202 | 112.1662 | 115.2394 | 79.0501 |  | 54.3086 | 109.0561 | 58.1674 | 102.88 | 69.4973 | 67.602 |  | 74.6917 |  |  | 23.5259 | 26.8574 | 55.6472 | [5 empty] | 21.8892 | 68.6971 | 21.6916 | 22.0843 | 34.4308 | 21.2707 | 21.9168 | 30.002 | 92.9721 | 195.921 |  | 83.521 | 141.0681 | 23.2068 | 72.321 | 161.4827 | 50.3666 | 111.4324 | 26.093 | 109.1647 | 26.0733 | 108.063 | 18.9771 | 80.3624 | 133.636 | 31.1929 | 75.0688 | 151.4003 | 22.9716 | 70.8225 | 148.0293 | 23.6455 | 100.3581 | 33.1041 | 106.9366 | 26.6761 | 117.8362 | 1.3197 | 19.2109 | 1.4732 | 0.051151 | -27.1618 | 3.0953 | 207.1 | 55.35 | 1.2389 | -0.76946 | -6.248 | 0.89862 | 0.1811 | -14.9469 | 5.4962 | -0.035322 | -0.73036 | -0.14572 | -2.5538 | -1.9189 | -0.95353 | -0.048389
42838.4252 | 422 | 22.9027 | 22.8568 | 22.8474 | 22.7645 | 22.3763 | 21.7063 | 22.6967 | 21.7595 | 22.3519 | 22.3524 | 22.326 | 21.9749 | 21.1843 | 22.1587 | 21.611 | 21.7789 | 21.9024 | 21.0831 | 21.1953 | 21.5417 | 20.4806 | 20.929 | 23.6032 | 21.8791 | 21.9388 | 26.7773 | 146.3489 | 125.4154 | 166.4685 | 22.1045 | 21.9114 | 25.0609 | 22.02 | 21.9984 | 26.4207 | 61.9245 | 182.9243 |  | 95.3504 | 127.7563 | 125.1296 | 121.5166 |  | 17.3312 | 18.0657 | 17.2481 | 18.0431 | 18.7768 | 27.406 | 106.3724 | 15.5587 | 17.1299 | 15.5904 | 18.434 | 18.5546 | 45.4846 | 49.0723 | 44.7691 | 21.6265 |  |  | 0.65669 | -0.41536 | -27.8343 | 0.23257 | 0.17624 | -157.5181 | 20.5844 | 0.78424 | 0.2377 | 0.46922 | 0.3284 | 0.00037456 | 0.00038606 | 0.87341 | 21.8009 | 21.9545 | 22.1605 | 22.2154 | 22.0233 | 21.3151 | 20.1349 | 22.1809 | 22.3567 | 22.3939 | 22.3417 | 21.9536 | 21.1868 | 22.268 | 80.7949 | 54.3383 | 58.5812 | 38.1073 | 31.9742 | 50.3422 | 34.2973 | 22.3276 | 22.0892 | 21.648 | 22.0575 | 21.7795 | 21.4239 | 21.9376 | 21.6849 | 23.8103 | 54.5441 | 143.7005 | 114.2146 | 80.6996 | 1.5052 | 0.74029 | 63.2565 | 21.8976 | 22.227 | 20.4832 | 21.5654 | 22.0191 | 21.9455 | 22.2136 | 30.0248 | 21.7943 | 21.6774 | 24.745 | 148.3913 | 198.2701 | 112.6614 | 115.8515 | 78.8495 |  | 54.4675 | 110.8381 | 58.4074 | 103.5204 | 69.8926 | 68.2336 |  | 74.9999 |  |  | 23.575 | 26.9853 | 55.7957 | [5 empty] | 21.8921 | 69.5312 | 21.6994 | 22.0927 | 34.5127 | 21.28 | 21.9159 | 30.0914 | 93.4811 | 197.158 |  | 83.9222 | 141.7459 | 23.2416 | 72.5114 | 162.7384 | 50.657 | 111.8921 | 26.1304 | 109.6151 | 26.1312 | 108.4509 | 18.975 | 80.9032 | 134.5217 | 31.279 | 75.4208 | 152.2369 | 23.0053 | 71.2413 | 148.7454 | 23.6783 | 100.5668 | 33.2156 | 107.4703 | 26.7269 | 118.5655 | 1.1765 | 19.2092 | 1.4773 | 0.052073 | -27.1715 | 3.0952 | 211.77 | 56.32 | 1.1841 | -0.76646 | -6.2743 | 0.57353 | 0.5072 | -15.1633 | 5.4815 | -0.024069 | -0.7712 | -0.14892 | -2.7627 | -2.1916 | -0.94059 | -0.072724
42838.4252 | 423 | 22.8936 | 22.8601 | 22.8476 | 22.7583 | 22.3715 | 21.6992 | 22.6945 | 21.7571 | 22.3482 | 22.3509 | 22.3243 | 21.9746 | 21.181 | 22.1551 | 21.608 | 21.7842 | 21.9075 | 21.0874 | 21.1918 | 21.5471 | 20.487 | 20.9409 | 23.6293 | 21.8826 | 21.9413 | 26.8063 | 147.1896 | 126.0396 | 167.2538 | 22.1022 | 21.9077 | 25.0733 | 22.0196 | 21.9918 | 26.4448 | 62.1375 | 183.023 |  | 95.8374 | 128.3868 | 125.6278 | 122.8266 |  | 17.3356 | 18.0801 | 17.2655 | 18.0497 | 18.7933 | 27.4865 | 107.2039 | 15.5926 | 17.1284 | 15.5737 | 18.4385 | 18.5567 | 45.5209 | 49.0917 | 44.7848 | 21.6238 |  |  | 0.73489 | -0.43048 | -27.9644 | 0.48228 | 0.32869 | -154.6906 | 20.1947 | 0.47473 | 0.029867 | 0.2267 | 0.25531 | 0.00037291 | 0.0003647 | 0.82231 | 21.8081 | 21.963 | 22.1637 | 22.2169 | 22.0277 | 21.3211 | 20.141 | 22.1747 | 22.3552 | 22.3922 | 22.3429 | 21.9584 | 21.1864 | 22.2765 | 80.9033 | 54.9431 | 59.1778 | 38.7789 | 32.6834 | 50.5523 | 34.4158 | 22.3287 | 22.0896 | 21.6509 | 22.0541 | 21.7773 | 21.4228 | 21.9412 | 21.6872 | 23.829 | 54.7497 | 144.4047 | 114.5505 | 81.1629 | 1.5201 | 0.57558 | 63.5648 | 21.8937 | 22.2231 | 20.4895 | 21.5695 | 22.0261 | 21.9393 | 22.2112 | 30.0717 | 21.7964 | 21.6796 | 24.7757 | 148.9687 | 199.0749 | 113.1793 | 116.4413 | 79.038 |  | 54.6382 | 111.4568 | 58.647 | 106.7906 | 70.5427 | 67.8114 |  | 75.3032 |  |  | 23.6127 | 27.0688 | 56.0968 | [5 empty] | 21.8914 | 71.6769 | 21.6998 | 22.099 | 34.5654 | 21.2778 | 21.9226 | 30.1779 | 93.9862 | 198.8104 |  | 84.2402 | 142.5938 | 23.2676 | 72.8068 | 163.4454 | 50.8993 | 112.3157 | 26.1717 | 110.1446 | 26.1881 | 108.862 | 18.9759 | 81.4494 | 135.2256 | 31.3764 | 75.7647 | 153.4205 | 23.0458 | 71.6929 | 149.3409 | 23.7092 | 100.921 | 33.3179 | 107.7702 | 26.7956 | 119.1855 | 1.0609 | 19.205 | 1.4816 | 0.05285 | -27.284 | 3.0953 | 211.69 | 54.91 | 1.2537 | -0.7803 | -6.2891 | 0.82591 | 0.69276 | -15.0286 | 5.4301 | -0.023201 | -0.77975 | -0.21573 | -2.7498 | -2.244 | -0.96925 | -0.078239
42838.4252 | 424 | 22.8964 | 22.8654 | 22.8542 | 22.7704 | 22.3775 | 21.7053 | 22.7021 | 21.7668 | 22.3476 | 22.3589 | 22.3292 | 21.979 | 21.1904 | 22.1632 | 21.6069 | 21.7818 | 21.9143 | 21.0846 | 21.1962 | 21.5465 | 20.487 | 20.9442 | 23.6449 | 21.8855 | 21.9435 | 26.8273 | 147.884 | 126.7799 | 168.2238 | 22.1104 | 21.9095 | 25.0984 | 22.0226 | 21.9978 | 26.4746 | 62.3805 | 182.2859 |  | 96.2557 | 129.0986 | 126.082 | 124.0576 |  | 17.3415 | 18.0988 | 17.2845 | 18.0621 | 18.8127 | 27.7019 | 108.1193 | 15.64 | 17.1348 | 15.5866 | 18.4529 | 18.5509 | 45.5507 | 49.1182 | 44.8103 | 21.6147 |  |  | 0.56075 | -0.57964 | -28.2969 | 0.62225 | 0.14995 | -152.1778 | 20.1001 | 0.77109 | -0.33676 | 0.16438 | 0.27354 | 0.00038113 | 0.00037949 | 0.78576 | 21.8095 | 21.956 | 22.1619 | 22.2175 | 22.0321 | 21.3133 | 20.1329 | 22.1756 | 22.3483 | 22.3962 | 22.3437 | 21.9512 | 21.1873 | 22.2686 | 79.7774 | 56.8681 | 59.4535 | 38.8623 | 33.0902 | 50.7286 | 34.5476 | 22.3224 | 22.0858 | 21.6525 | 22.0501 | 21.7728 | 21.4195 | 21.9379 | 21.6822 | 23.8427 | 54.9073 | 145.2674 | 114.8945 | 81.3063 | 1.0394 | 0.72336 | 63.434 | 21.8975 | 22.2202 | 20.4997 | 21.5632 | 22.025 | 21.9438 | 22.2171 | 30.1176 | 21.7986 | 21.6722 | 24.7897 | 149.6463 | 200.1889 | 113.6537 | 116.9318 | 77.695 |  | 54.7692 | 110.8187 | 58.8529 | 105.8662 | 70.983 | 67.3194 |  | 75.5744 |  |  | 23.6319 | 27.111 | 56.2398 | [5 empty] | 21.8913 | 72.8398 | 21.6903 | 22.0943 | 34.5913 | 21.2791 | 21.915 | 30.26 | 94.4285 | 200.3142 |  | 84.6712 | 143.276 | 23.2955 | 73.3201 | 163.9288 | 51.1368 | 112.6416 | 26.2203 | 110.6254 | 26.2345 | 109.3676 | 18.9624 | 81.9123 | 136.1949 | 31.4883 | 76.0669 | 154.3446 | 23.0767 | 72.113 | 150.0069 | 23.7507 | 101.3642 | 33.4346 | 107.9123 | 26.8575 | 119.5406 | 1.3293 | 19.2031 | 1.4865 | 0.054302 | -27.2826 | 3.0953 | 212.77 | 56.01 | 1.0964 | -0.90548 | -6.3266 | 0.93817 | 0.46808 | -14.9114 | 5.4193 | 0.018792 | -0.7546 | -0.17376 | -2.6038 | -2.2591 | -0.99461 | -0.076584
42838.4252 | 425 | 22.8911 | 22.8595 | 22.8447 | 22.7662 | 22.3794 | 21.7076 | 22.7046 | 21.7619 | 22.3527 | 22.3662 | 22.3273 | 21.9765 | 21.1916 | 22.164 | 21.606 | 21.7808 | 21.9127 | 21.0832 | 21.2009 | 21.5437 | 20.4835 | 20.9471 | 23.6587 | 21.8873 | 21.949 | 26.8535 | 148.4017 | 127.6948 | 168.2844 | 22.1086 | 21.9078 | 25.1135 | 22.0105 | 21.9978 | 26.4949 | 62.6364 | 182.5856 |  | 96.6461 | 129.656 | 126.5722 | 125.407 |  | 17.3444 | 18.1146 | 17.2975 | 18.0856 | 18.816 | 27.7142 | 108.8152 | 15.6516 | 17.13 | 15.5945 | 18.4529 | 18.5429 | 45.5872 | 49.1408 | 44.8311 | 21.631 |  |  | 0.45364 | -0.53693 | -28.4552 | 0.41591 | 0.422 | -154.2786 | 20.0173 | 0.72115 | -0.17835 | 0.31376 | 0.31416 | 0.00039263 | 0.00036963 | 0.77256 | 21.8076 | 21.9565 | 22.1636 | 22.2191 | 22.028 | 21.3151 | 20.136 | 22.1752 | 22.3585 | 22.3977 | 22.3382 | 21.9559 | 21.1858 | 22.2654 | 81.0583 | 55.3984 | 56.7255 | 39.5516 | 33.9209 | 50.909 | 34.6326 | 22.3191 | 22.0801 | 21.6467 | 22.0477 | 21.7604 | 21.4158 | 21.9316 | 21.6766 | 23.851 | 55.0685 | 145.8674 | 115.1474 | 81.7478 | 1.0764 | 0.21134 | 63.4659 | 21.9005 | 22.229 | 20.5086 | 21.5664 | 22.0244 | 21.9439 | 22.2274 | 30.1597 | 21.8025 | 21.6738 | 24.8115 | 150.2947 | 201.1768 | 114.0941 | 117.2685 | 77.3231 |  | 54.92 | 111.5092 | 59.0863 | 103.3656 | 71.3099 | 67.702 |  | 75.8674 |  |  | 23.6629 | 27.1679 | 56.3374 | [5 empty] | 21.8894 | 72.5104 | 21.6892 | 22.087 | 34.6259 | 21.273 | 21.9144 | 30.3491 | 94.8908 | 201.6424 |  | 85.1348 | 144.1074 | 23.3291 | 73.8722 | 164.2491 | 51.4383 | 113.0068 | 26.2703 | 111.0529 | 26.2743 | 109.7569 | 18.9565 | 82.3955 | 137.2006 | 31.588 | 76.3575 | 155.1009 | 23.125 | 72.4742 | 150.6261 | 23.7916 | 101.7621 | 33.5396 | 108.4493 | 26.9167 | 119.8321 | 1.283 | 19.1963 | 1.4913 | 0.054614 | -27.2099 | 3.0952 | 228.48 | 55.02 | 0.98618 | -0.8715 | -6.3444 | 0.76703 | 0.78525 | -15.0143 | 5.4082 | 0.034516 | -0.76536 | -0.092189 | -2.7246 | -1.9459 | -1.0228 | -0.083078
42838.4252 | 426 | 22.8903 | 22.8548 | 22.8411 | 22.7599 | 22.3727 | 21.7032 | 22.6934 | 21.7564 | 22.3456 | 22.355 | 22.329 | 21.9705 | 21.1854 | 22.1577 | 21.6097 | 21.7815 | 21.9086 | 21.0835 | 21.1943 | 21.5473 | 20.4829 | 20.9482 | 23.6817 | 21.8891 | 21.9493 | 26.8757 | 148.8399 | 128.5154 | 168.0965 | 22.1069 | 21.915 | 25.1396 | 22.0184 | 21.9956 | 26.5331 | 62.9068 | 181.611 |  | 96.9946 | 130.1114 | 127.0727 | 126.6112 |  | 17.3458 | 18.1333 | 17.3092 | 18.0996 | 18.8474 | 27.5998 | 109.5128 | 15.5722 | 17.1296 | 15.6767 | 18.4718 | 18.5497 | 45.6102 | 49.1661 | 44.8438 | 21.624 |  |  | 0.40567 | -0.61907 | -28.5604 | 0.36794 | 0.13024 | -157.5977 | 19.9924 | 0.90449 | -0.52572 | 0.47762 | 0.49713 | 0.00036799 | 0.00035649 | 0.74903 | 21.8098 | 21.9655 | 22.1628 | 22.2168 | 22.0292 | 21.3182 | 20.1269 | 22.1786 | 22.3614 | 22.3977 | 22.3444 | 21.9595 | 21.1815 | 22.2669 | 82.1914 | 53.7576 | 52.2471 | 39.3077 | 34.7613 | 51.1327 | 34.7015 | 22.3257 | 22.0891 | 21.6555 | 22.0563 | 21.7749 | 21.4261 | 21.9416 | 21.6899 | 23.8758 | 55.2524 | 146.8764 | 115.51 | 81.696 | 1.4256 | 0.57919 | 63.9599 | 21.9116 | 22.2271 | 20.515 | 21.5739 | 22.0278 | 21.9424 | 22.2363 | 30.2001 | 21.7998 | 21.6813 | 24.8358 | 150.927 | 201.5042 | 114.556 | 117.6234 | 77.5133 |  | 55.0898 | 113.4932 | 59.4301 | 104.7562 | 71.8211 | 68.0359 |  | 76.2004 |  |  | 23.6957 | 27.2476 | 56.5635 | [5 empty] | 21.8945 | 72.8373 | 21.6946 | 22.0948 | 34.67 | 21.275 | 21.9182 | 30.4197 | 95.3694 | 202.1835 |  | 85.535 | 144.8117 | 23.3601 | 74.1967 | 164.456 | 51.7481 | 113.396 | 26.311 | 111.5468 | 26.3227 | 110.095 | 18.9505 | 82.6483 | 137.8231 | 31.6738 | 76.6632 | 155.7688 | 23.1806 | 72.7897 | 151.4257 | 23.8248 | 102.1978 | 33.6182 | 109.1518 | 26.9693 | 120.3553 | 1.4188 | 19.195 | 1.4955 | 0.055804 | -27.0881 | 3.0952 | 240.51 | 54.94 | 0.93238 | -0.93582 | -6.3563 | 0.72146 | 0.43616 | -15.1721 | 5.4038 | 0.035313 | -0.80806 | -0.11187 | -2.8239 | -1.4402 | -1.0464 | -0.075055
42838.4252 | 427 | 22.8992 | 22.8682 | 22.838 | 22.7646 | 22.3812 | 21.7007 | 22.6909 | 21.7586 | 22.3498 | 22.3516 | 22.327 | 21.9749 | 21.1852 | 22.1576 | 21.6004 | 21.7779 | 21.9034 | 21.0792 | 21.1939 | 21.5472 | 20.4874 | 20.9378 | 23.6907 | 21.8869 | 21.9509 | 26.901 | 149.5039 | 129.207 | 168.0825 | 22.1013 | 21.9133 | 25.1647 | 22.0193 | 22.0018 | 26.557 | 63.1608 | 179.3511 |  | 97.3506 | 130.5972 | 127.5139 | 126.5901 |  | 17.3571 | 18.1519 | 17.3242 | 18.1313 | 18.8726 | 27.5802 | 110.1988 | 15.4879 | 17.1283 | 15.9039 | 18.4761 | 18.5545 | 45.6367 | 49.1963 | 44.8759 | 21.6265 |  |  | 0.49241 | -0.59081 | -28.5735 | 0.52236 | 0.15784 | -155.3766 | 19.9122 | 0.80986 | -0.12718 | 0.08571 | 0.26277 | 0.00035649 | 0.00035156 | 0.73281 | 21.8097 | 21.9588 | 22.1643 | 22.2114 | 22.0253 | 21.32 | 20.1305 | 22.173 | 22.3658 | 22.3904 | 22.3424 | 21.9557 | 21.1803 | 22.2724 | 84.4187 | 56.5373 | 53.2709 | 38.8447 | 33.9615 | 51.3794 | 34.8013 | 22.3196 | 22.0792 | 21.6477 | 22.048 | 21.7655 | 21.4205 | 21.9369 | 21.6818 | 23.8871 | 55.445 | 148.4324 | 116.0357 | 81.3101 | 1.2526 | 0.73649 | 64.1145 | 21.9052 | 22.2183 | 20.5124 | 21.5664 | 22.0263 | 21.9435 | 22.2429 | 30.2457 | 21.801 | 21.6858 | 24.8523 | 151.2795 | 202.1241 | 114.9452 | 117.9512 | 77.1208 |  | 55.2443 | 115.4682 | 59.7023 | 104.2041 | 72.3665 | 68.7597 |  | 76.485 |  |  | 23.7227 | 27.3246 | 57.2693 | [5 empty] | 21.9045 | 73.6807 | 21.6985 | 22.1007 | 34.6919 | 21.2811 | 21.9197 | 30.4778 | 95.828 | 202.6517 |  | 86.0358 | 145.5738 | 23.3983 | 74.5634 | 164.8702 | 52.0232 | 113.8136 | 26.3739 | 112.2624 | 26.3803 | 110.6589 | 18.964 | 82.9811 | 138.2859 | 31.7563 | 76.9568 | 156.3101 | 23.2232 | 73.2166 | 152.1897 | 23.8666 | 102.7356 | 33.6871 | 109.4619 | 27.0206 | 120.8728 | 1.9968 | 19.1919 | 1.499 | 0.055935 | -27.0636 | 3.0953 | 252.75 | 52.57 | 1.0272 | -0.91425 | -6.358 | 0.85966 | 0.48014 | -15.0643 | 5.3928 | 0.051746 | -0.85309 | -0.076291 | -3.0421 | -1.5422 | -1.0366 | -0.057436
42838.4252 | 428 | 22.897 | 22.8668 | 22.8478 | 22.769 | 22.3769 | 21.7095 | 22.7038 | 21.7607 | 22.3501 | 22.3543 | 22.3252 | 21.9767 | 21.1925 | 22.1568 | 21.5995 | 21.7674 | 21.9023 | 21.0837 | 21.191 | 21.5391 | 20.4817 | 20.9419 | 23.716 | 21.8788 | 21.9531 | 26.9201 | 150.1633 | 129.8527 | 168.6634 | 22.1003 | 21.9245 | 25.1833 | 22.0217 | 22.0114 | 26.5829 | 63.4081 | 177.6233 |  | 97.735 | 131.3392 | 128.0462 | 126.4094 |  | 17.3657 | 18.17 | 17.3381 | 18.1612 | 18.907 | 27.5617 | 110.4259 | 15.4379 | 17.1344 | 16.0311 | 18.4807 | 18.5594 | 45.6733 | 49.2206 | 44.8953 | 21.6229 |  |  | 0.41684 | -0.71106 | -28.7358 | 0.21483 | 0.24458 | -152.7035 | 19.853 | 0.64033 | 0.056917 | 0.20173 | 0.27875 | 0.00036141 | 0.00034663 | 0.72146 | 21.8165 | 21.9662 | 22.1639 | 22.2164 | 22.0278 | 21.3232 | 20.1347 | 22.1772 | 22.3645 | 22.3976 | 22.3428 | 21.9607 | 21.1849 | 22.2765 | 84.9614 | 56.7212 | 53.2512 | 38.7604 | 33.6746 | 51.6118 | 34.9069 | 22.3151 | 22.0769 | 21.6532 | 22.0441 | 21.7699 | 21.4223 | 21.9353 | 21.6825 | 23.911 | 55.642 | 149.6557 | 116.5817 | 81.7359 | 1.4928 | 0.31919 | 64.1272 | 21.9019 | 22.2197 | 20.5192 | 21.571 | 22.0239 | 21.9417 | 22.2405 | 30.2877 | 21.8101 | 21.687 | 24.8726 | 152.0435 | 202.6518 | 115.2816 | 118.3167 | 78.3014 |  | 55.4314 | 116.815 | 59.9683 | 101.6721 | 72.7071 | 68.8921 |  | 76.7664 |  |  | 23.7415 | 27.3851 | 58.2391 | [5 empty] | 21.8951 | 73.6989 | 21.6982 | 22.0965 | 34.6882 | 21.2803 | 21.9148 | 30.5449 | 96.276 | 203.5038 |  | 86.5824 | 146.1539 | 23.4266 | 75.031 | 165.3824 | 52.2288 | 114.1933 | 26.4364 | 112.9384 | 26.4227 | 111.1406 | 18.9783 | 83.4733 | 138.8475 | 31.8281 | 77.2449 | 156.8395 | 23.2549 | 73.5157 | 152.6047 | 23.9008 | 103.0601 | 33.7572 | 109.7299 | 27.0862 | 121.4074 | 1.5173 | 19.1881 | 1.5033 | 0.055746 | -27.0013 | 3.0952 | 241.02 | 51.54 | 0.94574 | -1.003 | -6.3762 | 0.55132 | 0.59766 | -14.9337 | 5.3846 | 0.025653 | -0.88088 | 0.0066929 | -3.0748 | -1.5276 | -1.0226 | -0.062205
42838.4252 | 429 | 22.902 | 22.8621 | 22.8484 | 22.768 | 22.3833 | 21.7057 | 22.7024 | 21.7619 | 22.3496 | 22.3551 | 22.3306 | 21.9817 | 21.1932 | 22.1578 | 21.6031 | 21.77 | 21.9001 | 21.0866 | 21.1863 | 21.5522 | 20.4752 | 20.9421 | 23.7213 | 21.8828 | 21.9556 | 26.9467 | 150.6538 | 130.4552 | 169.1182 | 22.1087 | 21.9243 | 25.204 | 22.0245 | 22.0118 | 26.6154 | 63.6331 | 176.5441 |  | 98.0948 | 131.8754 | 128.617 | 127.5742 |  | 17.3779 | 18.1867 | 17.3555 | 18.1908 | 18.9573 | 27.6013 | 110.9463 | 15.4595 | 17.1392 | 16.0001 | 18.4994 | 18.5654 | 45.6949 | 49.2478 | 44.9263 | 21.6261 |  |  | 0.80125 | -0.40748 | -28.7904 | 0.34034 | 0.057956 | -155.6802 | 19.8971 | 0.79344 | 0.015856 | 0.14991 | 0.24038 | 0.00038606 | 0.00036306 | 0.71389 | 21.8105 | 21.9666 | 22.1633 | 22.2086 | 22.024 | 21.3169 | 20.1267 | 22.1734 | 22.3567 | 22.3957 | 22.332 | 21.9517 | 21.1827 | 22.268 | 85.788 | 54.8953 | 51.668 | 38.3575 | 34.1994 | 51.8358 | 34.9705 | 22.325 | 22.0848 | 21.6617 | 22.0542 | 21.7728 | 21.4316 | 21.9411 | 21.6896 | 23.9333 | 55.8117 | 150.4693 | 116.934 | 82.1101 | 1.3497 | 0.5712 | 64.212 | 21.904 | 22.2326 | 20.5209 | 21.5737 | 22.0273 | 21.947 | 22.2394 | 30.3387 | 21.8128 | 21.6842 | 24.9009 | 153.0689 | 203.0435 | 115.7373 | 118.8496 | 79.9785 |  | 55.6418 | 119.0996 | 60.2815 | 100.718 | 73.1396 | 69.4865 |  | 77.0985 |  |  | 23.7719 | 27.43 | 59.0638 | [5 empty] | 21.8914 | 73.6953 | 21.7021 | 22.0972 | 34.6664 | 21.285 | 21.9238 | 30.6163 | 96.7011 | 203.7554 |  | 86.8649 | 146.8709 | 23.4576 | 75.3466 | 165.4948 | 52.4065 | 114.5594 | 26.4875 | 113.3702 | 26.4687 | 111.5444 | 18.9807 | 83.871 | 139.2963 | 31.8888 | 77.5264 | 157.1374 | 23.2781 | 73.6057 | 152.8542 | 23.9142 | 103.4779 | 33.8146 | 110.2172 | 27.1439 | 121.8315 | 1.5668 | 19.1865 | 1.5069 | 0.056458 | -27.1891 | 3.0952 | 241.09 | 53.01 | 1.3119 | -0.7593 | -6.3825 | 0.69394 | 0.29095 | -15.0795 | 5.391 | -0.013396 | -0.93301 | 0.049277 | -3.14 | -1.3442 | -1.0467 | -0.066516
42838.4253 | 430 | 22.89 | 22.8557 | 22.8407 | 22.7645 | 22.3756 | 21.7009 | 22.6991 | 21.7547 | 22.3483 | 22.3505 | 22.3244 | 21.9787 | 21.1838 | 22.1591 | 21.6052 | 21.7809 | 21.9102 | 21.0903 | 21.1966 | 21.5576 | 20.481 | 20.9529 | 23.7512 | 21.8859 | 21.9612 | 26.9802 | 151.3124 | 130.9679 | 170.4627 | 22.1035 | 21.9232 | 25.2187 | 22.0181 | 22.0084 | 26.637 | 63.8551 | 176.0841 |  | 98.4259 | 132.225 | 129.1162 | 127.5744 |  | 17.387 | 18.1976 | 17.3668 | 18.2014 | 18.9742 | 27.6422 | 111.4374 | 15.5109 | 17.1385 | 15.9807 | 18.4972 | 18.5672 | 45.7292 | 49.2737 | 44.9554 | 21.6296 |  |  | 0.49964 | -0.57636 | -28.2482 | 0.39554 | 0.20318 | -153.973 | 19.5403 | 0.9426 | -0.015475 | 0.32551 | 0.34784 | 0.00037456 | 0.00036306 | 0.70291 | 21.8113 | 21.9557 | 22.1504 | 22.2003 | 22.0176 | 21.3179 | 20.1162 | 22.1688 | 22.3465 | 22.3873 | 22.3271 | 21.953 | 21.1814 | 22.2638 | 86.6377 | 56.5421 | 53.5471 | 38.1666 | 34.0038 | 52.0824 | 35.0695 | 22.3311 | 22.0957 | 21.6653 | 22.0674 | 21.7831 | 21.4436 | 21.946 | 21.6985 | 23.9602 | 55.986 | 151.4501 | 117.2593 | 82.8573 | 1.2636 | 0.83995 | 64.8689 | 21.9032 | 22.2251 | 20.5292 | 21.5658 | 22.0263 | 21.9458 | 22.2491 | 30.3811 | 21.8075 | 21.6843 | 24.9171 | 153.6862 | 203.5733 | 116.3518 | 119.3886 | 80.7446 |  | 55.8166 | 120.7219 | 60.5798 | 99.7636 | 73.5515 | 69.4661 |  | 77.389 |  |  | 23.7814 | 27.4752 | 59.7312 | [5 empty] | 21.8976 | 74.5196 | 21.7014 | 22.0943 | 34.6383 | 21.2807 | 21.9137 | 30.6837 | 97.0849 | 204.5971 |  | 87.0577 | 147.5182 | 23.4844 | 75.6898 | 165.7654 | 52.5314 | 114.9577 | 26.5227 | 113.8959 | 26.5129 | 112.1607 | 18.9794 | 84.3525 | 139.7274 | 31.9557 | 77.789 | 157.9553 | 23.3058 | 74.0261 | 153.1214 | 23.9484 | 103.9949 | 33.8763 | 110.9344 | 27.2042 | 122.1842 | 1.554 | 19.1845 | 1.5114 | 0.056204 | -27.1509 | 3.0952 | 255.66 | 51.47 | 1.0375 | -0.90306 | -6.3222 | 0.74811 | 0.5448 | -14.9976 | 5.3428 | -0.028408 | -0.96728 | 0.091115 | -3.2051 | -1.5414 | -1.0386 | -0.081022
42838.4253 | 431 | 22.8924 | 22.8619 | 22.8479 | 22.7724 | 22.3806 | 21.7051 | 22.7016 | 21.7649 | 22.3524 | 22.3541 | 22.3284 | 21.9806 | 21.1904 | 22.1659 | 21.6032 | 21.7782 | 21.896 | 21.0858 | 21.1957 | 21.5559 | 20.4817 | 20.9556 | 23.7663 | 21.8805 | 21.9566 | 26.9996 | 152.2602 | 131.5838 | 172.1284 | 22.1038 | 21.9231 | 25.2436 | 22.0197 | 22.0144 | 26.6688 | 64.0742 | 175.5856 |  | 98.7326 | 132.5773 | 129.5629 | 127.6808 |  | 17.3981 | 18.2174 | 17.3825 | 18.2327 | 19.0154 | 27.6372 | 111.6957 | 15.6004 | 17.1463 | 15.9705 | 18.5139 | 18.5702 | 45.7501 | 49.2971 | 45.0025 | 21.6324 |  |  | 0.57652 | -0.50407 | -28.7739 | 0.31669 | 0.36154 | -155.485 | 19.3412 | 0.77964 | 0.027337 | 0.087808 | 0.38048 | 0.00034499 | 0.00036141 | 0.71262 | 21.8199 | 21.9576 | 22.1617 | 22.2107 | 22.0302 | 21.3279 | 20.1393 | 22.1812 | 22.3576 | 22.3957 | 22.3468 | 21.9593 | 21.1935 | 22.2694 | 86.6173 | 56.8346 | 53.2027 | 39.6232 | 35.2083 | 52.3037 | 35.1381 | 22.32 | 22.0807 | 21.6492 | 22.0561 | 21.7781 | 21.4344 | 21.9322 | 21.6914 | 23.9655 | 56.152 | 152.2416 | 117.6424 | 83.7261 | 0.99736 | 0.58794 | 65.4622 | 21.9108 | 22.2426 | 20.5366 | 21.5746 | 22.0335 | 21.9511 | 22.2606 | 30.4332 | 21.8105 | 21.6985 | 24.9436 | 154.5424 | 204.0025 | 117.1404 | 119.9822 | 81.4118 |  | 55.9885 | 121.4912 | 60.8441 | 97.7334 | 73.8374 | 70.0724 |  | 77.6992 |  |  | 23.8132 | 27.8629 | 59.8307 | [5 empty] | 21.9086 | 74.1333 | 21.7114 | 22.1043 | 34.6326 | 21.3001 | 21.9247 | 30.772 | 97.5054 | 204.6488 |  | 87.4925 | 147.9032 | 23.5404 | 76.0123 | 165.8725 | 52.7106 | 115.4004 | 26.5559 | 114.2749 | 26.545 | 112.7946 | 18.9665 | 84.8787 | 140.0626 | 32.0153 | 78.0255 | 158.7484 | 23.3075 | 74.7629 | 153.7696 | 23.9923 | 104.4544 | 33.9341 | 111.239 | 27.2486 | 122.3597 | 1.6855 | 19.1806 | 1.5156 | 0.056312 | -27.149 | 3.0952 | 260.75 | 52.41 | 1.1166 | -0.84457 | -6.381 | 0.66942 | 0.72674 | -15.071 | 5.3154 | -0.040781 | -0.97908 | 0.15816 | -3.1765 | -1.495 | -1.0336 | -0.0992
42838.4253 | 432 | 22.8963 | 22.8644 | 22.8511 | 22.77 | 22.3776 | 21.7042 | 22.7057 | 21.7674 | 22.3598 | 22.3567 | 22.329 | 21.9821 | 21.1949 | 22.1633 | 21.6022 | 21.7766 | 21.9024 | 21.0739 | 21.19 | 21.5492 | 20.4717 | 20.9507 | 23.7719 | 21.8727 | 21.9584 | 27.0256 | 152.9625 | 132.1937 | 172.3378 | 22.1051 | 21.9287 | 25.264 | 22.0194 | 22.0204 | 26.7001 | 64.2883 | 174.6922 |  | 99.0199 | 132.9833 | 130.0371 | 129.2047 |  | 17.397 | 18.2236 | 17.3878 | 18.2363 | 19.0211 | 27.6443 | 112.3721 | 15.684 | 17.1438 | 15.9355 | 18.5265 | 18.5664 | 45.7678 | 49.3151 | 45.029 | 21.6307 |  |  | 0.58046 | -0.53167 | -28.9947 | 0.23652 | 0.1769 | -148.4578 | 19.4864 | 0.57264 | 0.17543 | 0.17131 | 0.4737 | 0.00036306 | 0.00034992 | 0.71125 | 21.807 | 21.947 | 22.1567 | 22.2033 | 22.0239 | 21.3114 | 20.1268 | 22.1725 | 22.3529 | 22.3992 | 22.3404 | 21.9493 | 21.1776 | 22.2678 | 85.0474 | 55.7495 | 52.9918 | 38.3848 | 34.7953 | 52.463 | 35.2107 | 22.3121 | 22.0857 | 21.644 | 22.0477 | 21.7732 | 21.4312 | 21.9313 | 21.6857 | 23.9829 | 56.3317 | 152.7674 | 117.9337 | 84.9631 | 1.6658 | 0.6644 | 65.8839 | 21.9061 | 22.235 | 20.5481 | 21.5754 | 22.0314 | 21.9494 | 22.2743 | 30.4736 | 21.8125 | 21.6976 | 24.9637 | 154.9946 | 204.0058 | 118.0148 | 120.6528 | 82.2631 |  | 56.195 | 123.2576 | 61.1389 | 96.1664 | 74.1288 | 70.0422 |  | 78.0229 |  |  | 23.8458 | 28.0429 | 59.6804 | [5 empty] | 21.9034 | 72.8473 | 21.6939 | 22.0966 | 34.6324 | 21.2766 | 21.918 | 30.8229 | 97.9091 | 206.1753 |  | 87.9814 | 148.3932 | 23.5664 | 76.2383 | 165.9879 | 52.9271 | 115.8094 | 26.6046 | 114.6563 | 26.571 | 113.6028 | 18.953 | 85.1908 | 140.4264 | 32.0822 | 78.2223 | 159.4091 | 23.3106 | 75.0471 | 154.1144 | 24.0126 | 104.8754 | 34.0226 | 111.6262 | 27.2832 | 122.4867 | 1.4536 | 19.182 | 1.5207 | 0.057292 | -27.2238 | 3.0952 | 257.44 | 52.27 | 1.1207 | -0.86739 | -6.4055 | 0.57853 | 0.50835 | -14.7266 | 5.3354 | -0.05702 | -1.0175 | 0.21255 | -2.9831 | -1.463 | -1.0681 | -0.12711
42838.4253 | 433 | 22.8956 | 22.8669 | 22.8465 | 22.7726 | 22.3741 | 21.7081 | 22.7017 | 21.7649 | 22.3543 | 22.3574 | 22.3301 | 21.9757 | 21.1986 | 22.1694 | 21.6033 | 21.7818 | 21.9059 | 21.0757 | 21.1912 | 21.5549 | 20.4723 | 20.9601 | 23.7956 | 21.8805 | 21.9604 | 27.0512 | 153.4245 | 132.7681 | 172.351 | 22.1033 | 21.9273 | 25.2797 | 22.0078 | 22.019 | 26.7238 | 64.5145 | 175.9723 |  | 99.3451 | 133.3385 | 130.6196 | 130.1972 |  | 17.4058 | 18.236 | 17.389 | 18.2598 | 19.0114 | 27.605 | 113.0661 | 15.7622 | 17.1433 | 15.9078 | 18.5331 | 18.5699 | 45.7785 | 49.3311 | 45.0544 | 21.6263 |  |  | 0.75394 | -0.45216 | -29.2806 | 0.3916 | 0.088184 | -157.3506 | 19.4003 | 0.89134 | 0.22992 | 0.3532 | 0.42631 | 0.0003762 | 0.00037291 | 0.69076 | 21.8179 | 21.9525 | 22.1612 | 22.2076 | 22.0201 | 21.3107 | 20.1284 | 22.1793 | 22.3488 | 22.3859 | 22.3355 | 21.9595 | 21.1765 | 22.2677 | 85.6059 | 57.2939 | 55.7702 | 38.5655 | 33.7897 | 52.6526 | 35.3322 | 22.3191 | 22.0868 | 21.6519 | 22.0526 | 21.7765 | 21.438 | 21.9404 | 21.694 | 24.0042 | 56.5313 | 153.1195 | 118.2868 | 85.8882 | 0.96355 | 1.1758 | 66.8949 | 21.9002 | 22.2289 | 20.5497 | 21.5691 | 22.0275 | 21.942 | 22.2719 | 30.5108 | 21.8075 | 21.6971 | 24.9786 | 155.1593 | 203.8721 | 118.7473 | 121.3007 | 84.0925 |  | 56.4121 | 124.6924 | 61.4546 | 98.7294 | 74.4638 | 69.7296 |  | 78.3377 |  |  | 23.862 | 28.087 | 60.1879 | [5 empty] | 21.8809 | 73.7354 | 21.6913 | 22.0938 | 34.6378 | 21.2729 | 21.9144 | 30.8514 | 98.2828 | 206.9141 |  | 88.4736 | 148.8527 | 23.6043 | 76.4912 | 166.4179 | 53.1789 | 116.3003 | 26.6534 | 114.9046 | 26.6239 | 113.9975 | 18.9484 | 85.5329 | 140.639 | 32.1426 | 78.5364 | 160.1988 | 23.3345 | 75.3522 | 154.0118 | 24.0402 | 105.1494 | 34.1028 | 111.8053 | 27.35 | 123.0492 | 1.3711 | 19.1779 | 1.5257 | 0.058098 | -27.1415 | 3.0952 | 241.81 | 51.44 | 1.2772 | -0.79992 | -6.4371 | 0.74443 | 0.3589 | -15.1603 | 5.3233 | -0.10004 | -1.0459 | 0.15384 | -3.0226 | -1.7574 | -1.0874 | -0.14565
42838.4253 | 434 | 22.8994 | 22.8563 | 22.8387 | 22.7626 | 22.3726 | 21.6989 | 22.6975 | 21.759 | 22.3541 | 22.3551 | 22.3299 | 21.9745 | 21.1822 | 22.1573 | 21.5955 | 21.7693 | 21.8907 | 21.0762 | 21.1916 | 21.5465 | 20.4679 | 20.9565 | 23.8062 | 21.8729 | 21.9666 | 27.0642 | 153.9427 | 133.368 | 171.4549 | 22.1063 | 21.9269 | 25.3022 | 22.0182 | 22.0177 | 26.7496 | 64.7796 | 177.5755 |  | 99.6703 | 133.6618 | 131.1558 | 129.8185 |  | 17.4147 | 18.2547 | 17.4056 | 18.2924 | 19.0294 | 27.6078 | 113.9572 | 15.8258 | 17.156 | 15.889 | 18.5371 | 18.5734 | 45.7808 | 49.3484 | 45.1011 | 21.6292 |  |  | 0.57323 | -0.62432 | -29.318 | 0.30551 | 0.17624 | -152.2691 | 19.3109 | 0.61667 | 0.067814 | -0.044996 | 0.26902 | 0.00036141 | 0.00035813 | 0.70455 | 21.8236 | 21.9608 | 22.1682 | 22.21 | 22.0304 | 21.3176 | 20.1361 | 22.1849 | 22.3513 | 22.3921 | 22.3459 | 21.9642 | 21.1873 | 22.2739 | 83.5256 | 54.732 | 56.9661 | 39.155 | 34.049 | 52.8104 | 35.4528 | 22.3176 | 22.0899 | 21.6521 | 22.0591 | 21.7774 | 21.435 | 21.9386 | 21.6958 | 24.0143 | 56.7218 | 153.9085 | 118.9595 | 86.1942 | 1.0039 | 0.36502 | 67.635 | 21.8954 | 22.2256 | 20.5498 | 21.5645 | 22.0223 | 21.9351 | 22.267 | 30.558 | 21.8028 | 21.6966 | 24.9941 | 155.5836 | 204.1523 | 119.4663 | 121.9572 | 84.8096 |  | 56.5992 | 124.3763 | 61.7156 | 101.8359 | 74.8279 | 69.9445 |  | 78.6287 |  |  | 23.903 | 28.1218 | 60.8527 | [5 empty] | 21.8886 | 73.9423 | 21.6944 | 22.0942 | 34.6417 | 21.2808 | 21.9127 | 30.9044 | 98.6726 | 207.3439 |  | 89.0533 | 149.3857 | 23.642 | 76.7232 | 166.5264 | 53.363 | 116.8227 | 26.7018 | 115.4721 | 26.6654 | 114.4169 | 18.9388 | 85.703 | 141.2794 | 32.2007 | 78.8148 | 160.6982 | 23.3345 | 76.0006 | 154.0512 | 24.0587 | 105.4649 | 34.1502 | 112.032 | 27.4083 | 123.6824 | 1.4622 | 19.1741 | 1.5309 | 0.058468 | -27.1366 | 3.0952 | 254.75 | 52.74 | 1.1126 | -0.93998 | -6.4414 | 0.65755 | 0.50737 | -14.9136 | 5.311 | -0.11325 | -1.0276 | 0.081138 | -2.7727 | -1.8761 | -1.0672 | -0.1473
42838.4253 | 435 | 22.8974 | 22.8523 | 22.8454 | 22.7624 | 22.3756 | 21.7058 | 22.701 | 21.7568 | 22.3504 | 22.3529 | 22.3248 | 21.9791 | 21.187 | 22.1632 | 21.5981 | 21.7732 | 21.9017 | 21.0805 | 21.191 | 21.5577 | 20.4742 | 20.9599 | 23.8318 | 21.8801 | 21.9726 | 27.1061 | 154.4596 | 133.7028 | 171.1639 | 22.1068 | 21.9372 | 25.3318 | 22.0254 | 22.0322 | 26.7941 | 65.0756 | 177.3172 |  | 99.9958 | 133.8936 | 131.6381 | 130.4608 |  | 17.4107 | 18.2659 | 17.4174 | 18.3186 | 19.0292 | 27.8856 | 114.7462 | 15.8705 | 17.154 | 15.8452 | 18.5426 | 18.5817 | 45.7844 | 49.3595 | 45.1324 | 21.6277 |  |  | 0.43524 | -0.47779 | -29.4396 | 0.46782 | 0.1677 | -152.2139 | 19.1854 | 0.60418 | 0.19528 | 0.26404 | 0.45721 | 0.00035156 | 0.00035649 | 0.70642 | 21.8257 | 21.9618 | 22.1672 | 22.2192 | 22.0282 | 21.3171 | 20.1338 | 22.1813 | 22.3541 | 22.3919 | 22.342 | 21.963 | 21.1936 | 22.2711 | 80.0579 | 53.3207 | 53.7218 | 38.1737 | 33.5958 | 52.9171 | 35.5114 | 22.3148 | 22.0877 | 21.6454 | 22.0525 | 21.7718 | 21.4333 | 21.9351 | 21.6957 | 24.0376 | 56.9076 | 154.573 | 119.6309 | 85.8207 | 0.85227 | -0.2303 | 67.5627 | 21.8993 | 22.2339 | 20.5647 | 21.5732 | 22.026 | 21.9435 | 22.2715 | 30.6023 | 21.809 | 21.7039 | 25.0188 | 155.9452 | 204.8545 | 120.0961 | 122.5709 | 84.4756 |  | 56.8687 | 123.8339 | 61.9826 | 104.3203 | 75.2387 | 70.3624 |  | 78.9187 |  |  | 23.9332 | 28.1212 | 61.0849 | [5 empty] | 21.8993 | 74.3101 | 21.7005 | 22.0944 | 34.6626 | 21.2759 | 21.9182 | 30.9672 | 99.0835 | 207.1728 |  | 89.5757 | 149.6845 | 23.6812 | 76.935 | 167.094 | 53.5558 | 117.3199 | 26.7612 | 116.076 | 26.6953 | 114.8454 | 18.927 | 85.777 | 141.7913 | 32.2843 | 79.0401 | 161.0658 | 23.3449 | 76.3668 | 154.4782 | 24.0766 | 105.9032 | 34.2509 | 112.393 | 27.4652 | 124.2429 | 1.3943 | 19.1716 | 1.5363 | 0.05865 | -27.2886 | 3.0952 | 258.75 | 51.92 | 0.96912 | -0.82232 | -6.4549 | 0.8137 | 0.49515 | -14.9177 | 5.2962 | -0.094289 | -1.0029 | 0.02747 | -2.3747 | -1.5087 | -1.0742 | -0.13026
42838.4253 | 436 | 22.8973 | 22.8558 | 22.8439 | 22.767 | 22.3771 | 21.708 | 22.6989 | 21.7622 | 22.3507 | 22.3548 | 22.3284 | 21.9746 | 21.1935 | 22.1598 | 21.5985 | 21.7721 | 21.9009 | 21.0783 | 21.1943 | 21.5578 | 20.4757 | 20.968 | 23.8468 | 21.8796 | 21.9721 | 27.1278 | 154.8535 | 134.1667 | 171.4829 | 22.103 | 21.9271 | 25.3538 | 22.0203 | 22.0238 | 26.8215 | 65.3396 | 176.8715 |  | 100.3127 | 134.1537 | 132.0565 | 132.7802 |  | 17.4244 | 18.2856 | 17.4179 | 18.3163 | 19.0401 | 28.7836 | 115.6769 | 15.9034 | 17.1644 | 15.7343 | 18.5573 | 18.5829 | 45.785 | 49.3723 | 45.1485 | 21.6363 |  |  | 0.64552 | -0.48042 | -29.7668 | 0.35545 | 0.2183 | -153.1477 | 18.4376 | 0.84535 | 0.095253 | 0.4602 | 0.31538 | 0.00036306 | 0.00037127 | 0.67588 | 21.821 | 21.9615 | 22.1615 | 22.2194 | 22.0254 | 21.3181 | 20.1323 | 22.1741 | 22.357 | 22.393 | 22.3391 | 21.9544 | 21.1818 | 22.2626 | 78.4656 | 50.647 | 50.3911 | 36.8654 | 32.8025 | 53.0523 | 35.5436 | 22.313 | 22.0907 | 21.6475 | 22.0521 | 21.7698 | 21.4386 | 21.9295 | 21.6979 | 24.0489 | 57.0844 | 154.9779 | 120.0151 | 85.9957 | 1.18 | 0.6119 | 67.8862 | 21.8917 | 22.2231 | 20.5617 | 21.5652 | 22.0217 | 21.9378 | 22.2683 | 30.6449 | 21.7922 | 21.6993 | 25.0401 | 156.5008 | 205.0215 | 120.6558 | 123.0206 | 84.2919 |  | 57.1292 | 125.3758 | 62.3109 | 105.9922 | 75.7178 | 72.1146 |  | 79.2027 |  |  | 23.9578 | 28.0972 | 60.6487 | [5 empty] | 21.8942 | 74.7257 | 21.6893 | 22.0867 | 34.6167 | 21.2782 | 21.9185 | 30.999 | 99.5221 | 207.7274 |  | 89.9339 | 150.0022 | 23.7197 | 77.1083 | 167.7013 | 53.7184 | 117.7539 | 26.8178 | 116.3592 | 26.7311 | 115.2825 | 18.9081 | 86.222 | 142.2019 | 32.369 | 79.3361 | 161.7301 | 23.3792 | 76.4442 | 155.1491 | 24.0948 | 106.2056 | 34.3411 | 113.021 | 27.5137 | 124.5513 | 1.2321 | 19.1616 | 1.5431 | 0.058788 | -27.1148 | 3.0952 | 261 | 52.36 | 1.1807 | -0.82461 | -6.4909 | 0.7093 | 0.56578 | -14.9857 | 5.1997 | -0.079825 | -1.0338 | -0.0010582 | -2.1817 | -1.1349 | -1.129 | -0.12876
42838.4253 | 437 | 22.8894 | 22.8613 | 22.8423 | 22.7614 | 22.3751 | 21.705 | 22.6929 | 21.7562 | 22.3472 | 22.3516 | 22.319 | 21.9706 | 21.1873 | 22.1573 | 21.5982 | 21.7644 | 21.9011 | 21.0727 | 21.1914 | 21.5573 | 20.4682 | 20.971 | 23.8661 | 21.8779 | 21.9746 | 27.1511 | 155.0936 | 134.5738 | 170.9802 | 22.0947 | 21.9285 | 25.3659 | 22.0155 | 22.0217 | 26.8434 | 65.6165 | 176.875 |  | 100.6379 | 134.4704 | 132.4025 | 133.5596 |  | 17.421 | 18.2876 | 17.4176 | 18.3197 | 19.0362 | 29.2323 | 116.4082 | 15.9158 | 17.1576 | 15.6502 | 18.5503 | 18.5902 | 45.8003 | 49.3879 | 45.1701 | 21.6358 |  |  | 0.47467 | -0.5619 | -30.0126 | 0.41985 | 0.25115 | -158.2022 | 18.4777 | 0.84469 | 0.0055422 | 0.31166 | 0.29697 | 0.00039098 | 0.0003762 | 0.68025 | 21.8174 | 21.9614 | 22.1527 | 22.2105 | 22.0233 | 21.3168 | 20.1378 | 22.1736 | 22.3527 | 22.392 | 22.3434 | 21.9539 | 21.1786 | 22.2571 | 80.1899 | 53.0206 | 51.764 | 36.5871 | 31.4217 | 53.2287 | 35.6125 | 22.311 | 22.0772 | 21.6404 | 22.0483 | 21.7744 | 21.4388 | 21.9253 | 21.699 | 24.0646 | 57.2874 | 155.4922 | 120.3649 | 86.5038 | 1.108 | 0.68646 | 67.8561 | 21.8944 | 22.2268 | 20.5644 | 21.5702 | 22.0227 | 21.9441 | 22.2869 | 30.694 | 21.7998 | 21.6987 | 25.0618 | 156.873 | 205.4222 | 121.1769 | 123.5068 | 83.8546 |  | 57.3057 | 127.7522 | 62.6148 | 106.2575 | 76.0753 | 71.5708 |  | 79.4439 |  |  | 23.9762 | 28.0913 | 60.3746 | [5 empty] | 21.8946 | 75.3881 | 21.6957 | 22.094 | 34.5989 | 21.2832 | 21.9178 | 31.0268 | 99.9883 | 208.4812 |  | 90.2693 | 150.2662 | 23.759 | 77.2613 | 168.5866 | 53.831 | 118.1845 | 26.8561 | 116.7256 | 26.7639 | 115.7797 | 18.8979 | 86.7936 | 142.6532 | 32.4461 | 79.6919 | 162.479 | 23.4081 | 76.5791 | 155.7836 | 24.1092 | 106.3988 | 34.4089 | 113.5308 | 27.5481 | 124.8994 | 1.4316 | 19.1602 | 1.5496 | 0.059419 | -27.1211 | 3.0952 | 259.49 | 51.67 | 1.0119 | -0.8918 | -6.5177 | 0.77088 | 0.60731 | -15.2423 | 5.2092 | -0.061331 | -1.0887 | 0.0049507 | -2.3523 | -1.2793 | -1.1405 | -0.13558
42838.4253 | 438 | 22.8948 | 22.86 | 22.8514 | 22.7671 | 22.3842 | 21.7021 | 22.6992 | 21.763 | 22.3509 | 22.3553 | 22.3237 | 21.9766 | 21.1874 | 22.1606 | 21.6027 | 21.7754 | 21.9034 | 21.0768 | 21.188 | 21.5657 | 20.475 | 20.9778 | 23.889 | 21.8855 | 21.9805 | 27.1832 | 155.378 | 134.8648 | 170.3521 | 22.0968 | 21.9411 | 25.3905 | 22.0205 | 22.0304 | 26.8755 | 65.8841 | 176.1331 |  | 100.9699 | 134.9035 | 132.7235 | 133.068 |  | 17.4233 | 18.3011 | 17.424 | 18.3133 | 19.0138 | 29.259 | 116.7309 | 15.9011 | 17.1558 | 15.6573 | 18.5586 | 18.5795 | 45.7869 | 49.3894 | 45.1888 | 21.6278 |  |  | 0.67049 | -0.58358 | -30.142 | 0.38503 | 0.053356 | -153.4283 | 18.7366 | 0.78752 | -0.048167 | 0.10082 | 0.31711 | 0.00038277 | 0.00036141 | 0.66778 | 21.8192 | 21.9578 | 22.1474 | 22.204 | 22.0236 | 21.3194 | 20.1292 | 22.174 | 22.3526 | 22.391 | 22.3287 | 21.9509 | 21.1835 | 22.262 | 80.5643 | 54.6908 | 54.0995 | 37.0121 | 32.0672 | 53.4014 | 35.7012 | 22.3309 | 22.0924 | 21.6487 | 22.0513 | 21.783 | 21.4443 | 21.9409 | 21.707 | 24.0923 | 57.4792 | 155.8653 | 120.6431 | 86.7789 | 1.11 | 0.98165 | 68.0158 | 21.8923 | 22.2233 | 20.5719 | 21.5705 | 22.0192 | 21.9425 | 22.2866 | 30.7444 | 21.7987 | 21.7089 | 25.0844 | 157.4316 | 205.828 | 121.6786 | 123.9543 | 82.8584 |  | 57.4658 | 130.1447 | 62.8488 | 105.3495 | 76.4521 | 71.582 |  | 79.6945 |  |  | 24.0055 | 28.1026 | 60.4815 | [5 empty] | 21.8957 | 75.9105 | 21.6931 | 22.093 | 34.6068 | 21.2838 | 21.9195 | 31.0713 | 100.3757 | 208.7528 |  | 90.6285 | 150.8146 | 23.7943 | 77.4383 | 169.0949 | 53.9144 | 118.5663 | 26.8968 | 117.0792 | 26.8047 | 116.2543 | 18.91 | 87.2519 | 143.0212 | 32.5197 | 79.9359 | 162.7866 | 23.4388 | 76.9186 | 156.2998 | 24.1278 | 106.6375 | 34.4813 | 113.8784 | 27.5865 | 125.1609 | 1.185 | 19.155 | 1.5563 | 0.059753 | -27.1508 | 3.0952 | 246.23 | 51.23 | 1.2017 | -0.90887 | -6.5318 | 0.73824 | 0.27993 | -15.0113 | 5.2458 | -0.0279 | -1.1467 | 0.044285 | -2.3733 | -1.5283 | -1.1171 | -0.13632
42838.4254 | 439 | 22.896 | 22.864 | 22.8503 | 22.771 | 22.3878 | 21.7037 | 22.7042 | 21.7636 | 22.3584 | 22.3526 | 22.3341 | 21.9832 | 21.1965 | 22.1595 | 21.6006 | 21.7752 | 21.9056 | 21.0857 | 21.1908 | 21.5699 | 20.4797 | 20.9822 | 23.9165 | 21.8903 | 21.9873 | 27.213 | 155.8596 | 135.1915 | 171.1324 | 22.1062 | 21.9497 | 25.4128 | 22.028 | 22.036 | 26.9119 | 66.1506 | 176.1991 |  | 101.2862 | 135.2661 | 133.0728 | 133.5056 |  | 17.4324 | 18.3063 | 17.4238 | 18.2989 | 18.9922 | 29.1422 | 116.8414 | 15.8807 | 17.1624 | 15.7506 | 18.5765 | 18.5883 | 45.7909 | 49.3971 | 45.2079 | 21.6244 |  |  | 0.63106 | -0.86089 | -29.9994 | 0.18461 | 0.50808 | -153.5827 | 19.1302 | 0.76846 | 0.11199 | 0.20739 | 0.35079 | 0.0003762 | 0.00037291 | 0.63782 | 21.8273 | 21.9668 | 22.1626 | 22.2171 | 22.0307 | 21.314 | 20.1324 | 22.1891 | 22.3515 | 22.4014 | 22.3445 | 21.9545 | 21.1793 | 22.2747 | 81.5298 | 56.5152 | 54.7984 | 38.2762 | 32.3649 | 53.5883 | 35.8123 | 22.3251 | 22.0864 | 21.6508 | 22.0508 | 21.7749 | 21.446 | 21.9371 | 21.7045 | 24.114 | 57.6704 | 156.1889 | 120.8422 | 86.9603 | 1.0329 | 0.65755 | 68.3449 | 21.903 | 22.2323 | 20.5974 | 21.5721 | 22.0237 | 21.9488 | 22.2996 | 30.7937 | 21.8071 | 21.7181 | 25.1066 | 157.8072 | 205.6242 | 122.1515 | 124.4484 | 81.9878 |  | 57.6668 | 130.5794 | 63.1139 | 104.1614 | 77.005 | 71.4932 |  | 80.0149 |  |  | 24.0301 | 28.1439 | 60.532 | [5 empty] | 21.8958 | 76.8519 | 21.6916 | 22.0935 | 34.6132 | 21.2816 | 21.9213 | 31.1058 | 100.7216 | 208.9043 |  | 90.649 | 151.2929 | 23.8253 | 77.6952 | 169.5996 | 53.9945 | 118.919 | 26.9419 | 117.359 | 26.8352 | 116.6508 | 18.8995 | 87.6094 | 143.278 | 32.608 | 80.1373 | 163.1144 | 23.4702 | 77.2016 | 156.6837 | 24.1366 | 107.0105 | 34.5399 | 114.2933 | 27.6021 | 125.4101 | 2.2965 | 19.1463 | 1.5636 | 0.060262 | -27.1735 | 3.0952 | 239.45 | 52.7 | 1.1669 | -1.1039 | -6.5164 | 0.51118 | 0.86367 | -15.0159 | 5.2996 | 0.003514 | -1.1491 | 0.09802 | -2.4584 | -1.5929 | -1.1195 | -0.13448
42838.4254 | 440 | 22.8906 | 22.8648 | 22.8443 | 22.7709 | 22.3761 | 21.706 | 22.7016 | 21.759 | 22.3524 | 22.3524 | 22.3265 | 21.9811 | 21.1978 | 22.1515 | 21.6005 | 21.7673 | 21.9019 | 21.0869 | 21.1897 | 21.5672 | 20.475 | 20.9781 | 23.9328 | 21.8842 | 21.987 | 27.2243 | 156.5738 | 135.4547 | 172.2347 | 22.1043 | 21.9383 | 25.4296 | 22.0243 | 22.0317 | 26.932 | 66.4036 | 177.6018 |  | 101.5948 | 135.6749 | 133.4633 | 134.5107 |  | 17.4224 | 18.3158 | 17.4198 | 18.2986 | 18.9871 | 29.3106 | 117.437 | 15.8609 | 17.1671 | 15.8298 | 18.5779 | 18.5951 | 45.7985 | 49.4074 | 45.2203 | 21.6346 |  |  | 0.56929 | -0.65718 | -30.1322 | 0.15109 | 0.33789 | -150.4423 | 19.0658 | 0.91763 | 0.11588 | 0.039973 | 0.27649 | 0.00037784 | 0.00035649 | 0.63764 | 21.8308 | 21.9608 | 22.1682 | 22.2195 | 22.0269 | 21.3225 | 20.1387 | 22.1857 | 22.3535 | 22.4001 | 22.3496 | 21.9613 | 21.1945 | 22.2732 | 83.6584 | 55.2283 | 53.361 | 38.7696 | 33.2299 | 53.7945 | 35.8791 | 22.323 | 22.0857 | 21.6507 | 22.0477 | 21.7739 | 21.4407 | 21.933 | 21.7074 | 24.1262 | 57.8422 | 156.8694 | 121.1799 | 87.0506 | 0.96296 | 0.31786 | 68.1261 | 21.9015 | 22.2259 | 20.6081 | 21.5703 | 22.0301 | 21.9506 | 22.3032 | 30.8423 | 21.8111 | 21.7176 | 25.1375 | 157.9663 | 205.6312 | 122.5819 | 124.8591 | 83.5283 |  | 57.8585 | 130.8068 | 63.3326 | 103.6216 | 77.3657 | 71.0488 |  | 80.2507 |  |  | 24.0339 | 28.2247 | 60.7829 | [5 empty] | 21.8979 | 77.5606 | 21.6999 | 22.1009 | 34.6042 | 21.2788 | 21.9187 | 31.1556 | 101.1345 | 208.9972 |  | 90.577 | 151.6309 | 23.8649 | 78.0064 | 170.1097 | 54.1144 | 119.2993 | 26.9999 | 117.7314 | 26.8719 | 117.0955 | 18.8768 | 88.1094 | 143.6636 | 32.6713 | 80.3713 | 163.5778 | 23.4791 | 77.2651 | 157.0206 | 24.1561 | 107.3929 | 34.5918 | 114.6096 | 27.6375 | 125.6903 | 1.7675 | 19.1391 | 1.5709 | 0.061242 | -27.0309 | 3.0952 | 244.87 | 52.13 | 1.1097 | -0.9645 | -6.5309 | 0.46247 | 0.70451 | -14.8657 | 5.2921 | -0.032375 | -1.1475 | 0.12655 | -2.6704 | -1.4253 | -1.1381 | -0.1308
42838.4254 | 441 | 22.8962 | 22.864 | 22.8375 | 22.7618 | 22.375 | 21.7075 | 22.6955 | 21.7566 | 22.3499 | 22.3513 | 22.3235 | 21.9813 | 21.1864 | 22.1544 | 21.6027 | 21.7744 | 21.9081 | 21.0804 | 21.1968 | 21.5691 | 20.4757 | 20.9806 | 23.9569 | 21.8854 | 21.9909 | 27.2523 | 157.0421 | 135.7465 | 171.8264 | 22.1075 | 21.9383 | 25.4533 | 22.017 | 22.0403 | 26.9665 | 66.6781 | 177.8914 |  | 101.8889 | 136.2039 | 133.8692 | 134.4506 |  | 17.4229 | 18.3144 | 17.4125 | 18.2963 | 18.9855 | 30.1525 | 118.0078 | 15.8286 | 17.1631 | 15.8974 | 18.5936 | 18.6026 | 45.8228 | 49.4081 | 45.2286 | 21.6393 |  |  | 0.69743 | -0.61119 | -29.9219 | 0.01967 | 0.1539 | -157.1797 | 19.0165 | 0.76978 | 0.13515 | 0.2246 | 0.35357 | 0.00036141 | 0.00034334 | 0.63772 | 21.8254 | 21.9574 | 22.1591 | 22.2126 | 22.0176 | 21.3108 | 20.1339 | 22.1705 | 22.3509 | 22.3903 | 22.3438 | 21.9544 | 21.1776 | 22.2609 | 83.9256 | 54.894 | 50.8944 | 38.0519 | 33.1962 | 53.9847 | 35.9224 | 22.3168 | 22.0836 | 21.6544 | 22.0588 | 21.7812 | 21.4538 | 21.9356 | 21.7087 | 24.1502 | 58.0183 | 157.2657 | 121.4992 | 87.374 | 0.97141 | 0.53221 | 68.0712 | 21.903 | 22.2269 | 20.6066 | 21.5738 | 22.0309 | 21.9598 | 22.3021 | 30.8909 | 21.8096 | 21.7177 | 25.1501 | 158.4769 | 205.4697 | 123.1238 | 125.3099 | 83.7017 |  | 58.0521 | 131.0493 | 63.5398 | 102.4177 | 77.6542 | 71.181 |  | 80.4874 |  |  | 24.0273 | 28.2229 | 61.3519 | [5 empty] | 21.8935 | 77.3868 | 21.6947 | 22.0963 | 34.6017 | 21.2763 | 21.9159 | 31.204 | 101.5543 | 208.6019 |  | 90.709 | 151.9348 | 23.8878 | 78.282 | 170.2979 | 54.1986 | 119.7329 | 27.0597 | 118.2449 | 26.9147 | 117.5458 | 18.8596 | 88.6687 | 144.1877 | 32.7142 | 80.5988 | 164.0344 | 23.4799 | 77.523 | 157.363 | 24.1799 | 107.6496 | 34.6649 | 114.8528 | 27.6891 | 126.014 | 1.5803 | 19.1328 | 1.5779 | 0.062309 | -27.128 | 3.0952 | 256.49 | 52.57 | 1.2277 | -0.93014 | -6.5081 | 0.16686 | 0.47612 | -15.2161 | 5.2926 | -0.030222 | -1.1466 | 0.17083 | -2.6774 | -1.1462 | -1.1264 | -0.13345
42838.4254 | 442 | 22.8898 | 22.8586 | 22.8436 | 22.7556 | 22.3644 | 21.6941 | 22.6987 | 21.755 | 22.3484 | 22.3432 | 22.3153 | 21.9712 | 21.1828 | 22.1504 | 21.6026 | 21.7774 | 21.905 | 21.0814 | 21.1962 | 21.5732 | 20.474 | 20.986 | 23.9708 | 21.8801 | 21.994 | 27.2894 | 157.3798 | 136.1015 | 171.0082 | 22.1067 | 21.9475 | 25.4717 | 22.0201 | 22.0423 | 26.9929 | 66.9353 | 176.8741 |  | 102.2189 | 136.7223 | 134.2067 | 135.2036 |  | 17.4251 | 18.3129 | 17.4129 | 18.3068 | 19.0178 | 30.7263 | 118.3039 | 15.7586 | 17.1645 | 15.9158 | 18.5961 | 18.6027 | 45.8554 | 49.4041 | 45.2331 | 21.638 |  |  | 0.73029 | -0.5113 | -29.8523 | 0.12152 | 0.32935 | -152.4524 | 19.1112 | 0.83023 | 0.15363 | 0.13333 | 0.38221 | 0.0003992 | 0.00036306 | 0.63704 | 21.8237 | 21.955 | 22.1574 | 22.2152 | 22.0182 | 21.315 | 20.129 | 22.173 | 22.3502 | 22.3906 | 22.341 | 21.9519 | 21.1744 | 22.2572 | 83.1401 | 53.803 | 49.8933 | 38.0254 | 32.7926 | 54.138 | 35.971 | 22.3191 | 22.0881 | 21.6413 | 22.0495 | 21.7629 | 21.447 | 21.9331 | 21.7005 | 24.157 | 58.2252 | 157.2247 | 121.7635 | 88.1888 | 1.3231 | 0.6294 | 67.9914 | 21.9112 | 22.2272 | 20.6234 | 21.5751 | 22.0315 | 21.9532 | 22.3171 | 30.9346 | 21.814 | 21.7234 | 25.181 | 158.8866 | 205.5162 | 123.6357 | 125.7572 | 83.6594 |  | 58.2422 | 131.45 | 63.7575 | 102.7501 | 78.0547 | 71.4198 |  | 80.7364 |  |  | 24.0089 | 28.1922 | 61.591 | [5 empty] | 21.8942 | 76.752 | 21.6937 | 22.0888 | 34.6082 | 21.2791 | 21.9116 | 31.24 | 101.9347 | 208.3149 |  | 90.8377 | 152.1467 | 23.8986 | 78.5903 | 170.2094 | 54.3386 | 120.175 | 27.0966 | 118.6158 | 26.9501 | 117.9254 | 18.8429 | 89.168 | 144.6456 | 32.7616 | 80.8346 | 164.2634 | 23.4822 | 77.9175 | 157.6034 | 24.1678 | 107.882 | 34.717 | 115.4573 | 27.723 | 126.2793 | 1.1936 | 19.1282 | 1.5856 | 0.062795 | -27.2165 | 3.0952 | 237.79 | 52.03 | 1.2551 | -0.85074 | -6.5005 | 0.41475 | 0.69718 | -14.9997 | 5.3108 | -0.022198 | -1.1498 | 0.17665 | -2.5719 | -1.0292 | -1.1379 | -0.14863
42838.4254 | 443 | 22.8927 | 22.8532 | 22.8456 | 22.769 | 22.3825 | 21.6986 | 22.6985 | 21.7613 | 22.3495 | 22.3441 | 22.3215 | 21.9812 | 21.1878 | 22.1602 | 21.6097 | 21.7878 | 21.9072 | 21.0894 | 21.1989 | 21.5799 | 20.4801 | 20.993 | 23.991 | 21.8854 | 21.9999 | 27.3195 | 157.7068 | 136.2766 | 169.8578 | 22.1007 | 21.9415 | 25.5002 | 22.0115 | 22.0373 | 27.023 | 67.173 | 177.6303 |  | 102.5581 | 136.9591 | 134.511 | 136.4742 |  | 17.4268 | 18.3225 | 17.4234 | 18.3228 | 19.1376 | 31.0896 | 118.6536 | 15.7348 | 17.1655 | 15.8795 | 18.6011 | 18.6039 | 45.8793 | 49.4067 | 45.2414 | 21.6423 |  |  | 0.3715 | -0.4837 | -29.6591 | 0.24572 | 0.14667 | -153.036 | 18.9272 | 0.53256 | -0.13476 | 0.24537 | 0.31538 | 0.00041891 | 0.00035649 | 0.63704 | 21.8303 | 21.952 | 22.1565 | 22.2103 | 22.0224 | 21.3175 | 20.1293 | 22.1754 | 22.3475 | 22.3889 | 22.3377 | 21.9515 | 21.1799 | 22.2585 | 82.6871 | 53.9542 | 50.9683 | 38.0451 | 32.1174 | 54.3158 | 36.0382 | 22.3158 | 22.0799 | 21.6462 | 22.0469 | 21.7677 | 21.4475 | 21.9309 | 21.6942 | 24.1748 | 58.4166 | 157.3186 | 122.0152 | 89.0925 | 1.1676 | 0.59174 | 68.5525 | 21.8998 | 22.2237 | 20.6154 | 21.5688 | 22.0296 | 21.9556 | 22.3164 | 30.9739 | 21.8095 | 21.7182 | 25.2051 | 159.202 | 205.4177 | 124.0804 | 126.1642 | 83.5566 |  | 58.4502 | 131.7409 | 63.9832 | 102.4353 | 78.3837 | 71.8808 |  | 80.9858 |  |  | 24.0109 | 28.1417 | 61.8285 | [5 empty] | 21.8927 | 76.1105 | 21.6939 | 22.0888 | 34.6277 | 21.28 | 21.9136 | 31.255 | 102.3083 | 208.5051 |  | 90.8953 | 152.3898 | 23.9289 | 79.1373 | 170.0296 | 54.439 | 120.5542 | 27.1189 | 119.0378 | 26.9773 | 118.3871 | 18.8286 | 89.5122 | 144.9238 | 32.8279 | 81.0738 | 164.6287 | 23.4829 | 78.1515 | 157.7497 | 24.1579 | 108.3725 | 34.7781 | 116.0249 | 27.7567 | 126.6496 | 1.7883 | 19.1224 | 1.594 | 0.06331 | -27.1277 | 3.0952 | 250.85 | 51.69 | 0.89403 | -0.82747 | -6.4795 | 0.58977 | 0.46552 | -15.0374 | 5.2883 | -0.011845 | -1.1497 | 0.19776 | -2.5004 | -1.1407 | -1.1644 | -0.16683
42838.4254 | 444 | 22.8929 | 22.8554 | 22.8478 | 22.7671 | 22.3781 | 21.6989 | 22.6951 | 21.7567 | 22.3461 | 22.3499 | 22.3216 | 21.9763 | 21.1861 | 22.1567 | 21.6079 | 21.7901 | 21.9075 | 21.0861 | 21.2002 | 21.578 | 20.4876 | 20.9915 | 24.0092 | 21.8831 | 22.0057 | 27.3415 | 157.9249 | 136.3251 | 170.4128 | 22.1056 | 21.9373 | 25.5152 | 22.0137 | 22.0422 | 27.0558 | 67.422 | 177.5327 |  | 102.8395 | 137.0765 | 134.7579 | 136.94 |  | 17.4382 | 18.3434 | 17.4367 | 18.3476 | 19.2485 | 31.0403 | 118.868 | 15.737 | 17.1697 | 15.8526 | 18.6169 | 18.605 | 45.8995 | 49.4052 | 45.2604 | 21.639 |  |  | 0.46744 | -0.64207 | -29.9587 | 0.52236 | 0.088844 | -153.5656 | 19.3858 | 0.73824 | 0.072874 | 0.009762 | 0.30166 | 0.00034334 | 0.00032035 | 0.62885 | 21.8275 | 21.9626 | 22.1552 | 22.2025 | 22.0282 | 21.3204 | 20.1318 | 22.1753 | 22.3573 | 22.3906 | 22.3398 | 21.9484 | 21.1827 | 22.2582 | 85.4303 | 54.2122 | 52.2453 | 38.0505 | 32.2797 | 54.5445 | 36.1278 | 22.315 | 22.0829 | 21.6499 | 22.0497 | 21.7719 | 21.4503 | 21.9308 | 21.7056 | 24.1968 | 58.6201 | 157.4708 | 122.3302 | 89.6581 | 1.375 | 1.2592 | 69.3032 | 21.8982 | 22.2154 | 20.61 | 21.567 | 22.0257 | 21.9493 | 22.3224 | 31.0257 | 21.8091 | 21.7299 | 25.2126 | 159.3593 | 205.6585 | 124.5976 | 126.6909 | 85.8163 |  | 58.6594 | 131.9859 | 64.2057 | 101.4453 | 78.7369 | 71.7924 |  | 81.2187 |  |  | 24.0493 | 28.1396 | 64.3189 | [5 empty] | 21.8898 | 75.9019 | 21.6945 | 22.0881 | 34.6792 | 21.2806 | 21.9275 | 31.2749 | 102.7051 | 208.877 |  | 90.9311 | 152.6008 | 23.9738 | 79.7522 | 169.8708 | 54.5148 | 120.8825 | 27.1655 | 119.7443 | 27.0177 | 118.8433 | 18.8155 | 89.8539 | 145.2402 | 32.8992 | 81.3077 | 165.0577 | 23.4807 | 78.5476 | 157.975 | 24.159 | 108.7022 | 34.8669 | 116.3531 | 27.7974 | 126.9931 | 1.4329 | 19.1156 | 1.602 | 0.0649 | -27.0859 | 3.0952 | 257.67 | 52.67 | 1.0035 | -0.95339 | -6.5124 | 0.85994 | 0.36229 | -15.0621 | 5.3516 | -0.067073 | -1.1484 | 0.23856 | -2.7779 | -1.2721 | -1.1682 | -0.17521
42838.4254 | 445 | 22.8898 | 22.8613 | 22.8426 | 22.7661 | 22.3766 | 21.7026 | 22.6952 | 21.7565 | 22.3426 | 22.3531 | 22.3208 | 21.9778 | 21.1876 | 22.1524 | 21.5913 | 21.772 | 21.8935 | 21.0733 | 21.1891 | 21.5729 | 20.483 | 20.9894 | 24.018 | 21.8761 | 21.9984 | 27.3696 | 158.3029 | 136.3973 | 171.4064 | 22.1086 | 21.9452 | 25.5401 | 22.0183 | 22.0502 | 27.0829 | 67.6535 | 176.6203 |  | 103.1478 | 137.2879 | 134.9904 | 136.228 |  | 17.4432 | 18.3578 | 17.4289 | 18.365 | 19.349 | 31.0307 | 119.1397 | 15.6819 | 17.1689 | 15.8057 | 18.6233 | 18.5998 | 45.9172 | 49.3988 | 45.2798 | 21.6406 |  |  | 0.68823 | -0.16434 | -29.8746 | 0.40211 | 0.49494 | -156.0547 | 18.893 | 0.83418 | -0.055951 | 0.22879 | 0.22545 | 0.00036634 | 0.00036634 | 0.61189 | 21.8256 | 21.9552 | 22.151 | 22.201 | 22.0232 | 21.3166 | 20.1261 | 22.1683 | 22.354 | 22.3887 | 22.3367 | 21.9545 | 21.1854 | 22.258 | 86.6594 | 53.9151 | 55.3035 | 38.5884 | 32.2238 | 54.7358 | 36.2496 | 22.3246 | 22.0907 | 21.6503 | 22.0526 | 21.7809 | 21.4631 | 21.9384 | 21.7118 | 24.2259 | 58.8095 | 157.6116 | 122.5974 | 89.7987 | 1.1405 | 0.23892 | 69.7614 | 21.8983 | 22.2177 | 20.6051 | 21.5739 | 22.0249 | 21.9545 | 22.3251 | 31.0627 | 21.8114 | 21.7243 | 25.2345 | 159.7057 | 205.9286 | 125.1765 | 127.0799 | 88.9989 |  | 58.9232 | 133.4076 | 64.4675 | 99.914 | 79.0571 | 71.8576 |  | 81.452 |  |  | 24.0929 | 28.1482 | 64.2317 | [5 empty] | 21.8999 | 75.86 | 21.699 | 22.0923 | 34.7084 | 21.28 | 21.9245 | 31.2845 | 103.067 | 210.5752 |  | 90.9471 | 152.6735 | 23.9806 | 80.1544 | 169.7969 | 54.5803 | 121.1871 | 27.205 | 120.3949 | 27.046 | 119.2161 | 18.8572 | 90.0363 | 145.4612 | 32.9633 | 81.6054 | 165.5508 | 23.4804 | 79.194 | 158.3004 | 24.1994 | 108.8662 | 34.9303 | 116.6315 | 27.8304 | 127.3237 | 1.3349 | 19.1086 | 1.6109 | 0.065532 | -27.098 | 3.0952 | 256.05 | 51.49 | 1.219 | -0.48236 | -6.5034 | 0.75451 | 0.85508 | -15.1835 | 5.283 | -0.14596 | -1.1783 | 0.29316 | -2.8917 | -1.5975 | -1.14 | -0.17228
42838.4254 | 446 | 22.8945 | 22.8663 | 22.8492 | 22.7681 | 22.3773 | 21.702 | 22.703 | 21.7599 | 22.3531 | 22.3574 | 22.3286 | 21.9793 | 21.1898 | 22.1639 | 21.6057 | 21.7765 | 21.9054 | 21.0855 | 21.1938 | 21.5873 | 20.4763 | 20.9986 | 24.0433 | 21.8831 | 21.995 | 27.3907 | 158.9056 | 136.6152 | 172.8972 | 22.1114 | 21.9549 | 25.5634 | 22.0238 | 22.0568 | 27.1178 | 67.8798 | 175.8258 |  | 103.4326 | 137.6392 | 135.2315 | 135.436 |  | 17.4575 | 18.3691 | 17.4332 | 18.3813 | 19.3801 | 31.0708 | 119.1687 | 15.6156 | 17.1718 | 15.7542 | 18.6304 | 18.6064 | 45.9576 | 49.3973 | 45.2977 | 21.6427 |  |  | 0.51212 | -0.33519 | -29.803 | 0.23192 | 0.61782 | -152.7067 | 18.7701 | 0.88937 | 0.2017 | 0.12515 | 0.38672 | 0.00035813 | 0.00033513 | 0.6291 | 21.83 | 21.9638 | 22.1605 | 22.2165 | 22.0288 | 21.3193 | 20.1312 | 22.184 | 22.358 | 22.3897 | 22.3468 | 21.9564 | 21.1853 | 22.2661 | 86.2563 | 52.3622 | 54.3948 | 39.3406 | 33.2447 | 54.8852 | 36.3275 | 22.3168 | 22.0859 | 21.6545 | 22.051 | 21.7714 | 21.4591 | 21.9391 | 21.7094 | 24.2412 | 59.0099 | 157.6725 | 122.8865 | 90.2073 | 1.4053 | 0.53792 | 69.6654 | 21.8968 | 22.2222 | 20.6132 | 21.574 | 22.0197 | 21.9541 | 22.3299 | 31.1113 | 21.809 | 21.7277 | 25.262 | 159.954 | 205.997 | 125.6376 | 127.4951 | 89.6259 |  | 59.1781 | 134.0334 | 64.7625 | 100.4308 | 79.4473 | 72.1788 |  | 81.7001 |  |  | 24.138 | 28.1517 | 63.6482 | [5 empty] | 21.8993 | 75.601 | 21.6993 | 22.0904 | 34.716 | 21.289 | 21.9286 | 31.3102 | 103.4334 | 210.9392 |  | 91.0876 | 153.0906 | 24.0273 | 80.4279 | 169.7895 | 54.6682 | 121.5838 | 27.2587 | 121.1978 | 27.0938 | 119.447 | 18.8782 | 90.1386 | 145.6191 | 33.0125 | 81.861 | 166.6107 | 23.4549 | 79.6216 | 158.7495 | 24.233 | 109.1061 | 34.9927 | 116.9864 | 27.8609 | 127.5575 | 1.5588 | 19.1031 | 1.6191 | 0.066113 | -27.1311 | 3.0952 | 244.61 | 52.61 | 1.0533 | -0.68889 | -6.4958 | 0.57302 | 0.95542 | -15.0207 | 5.2662 | -0.15418 | -1.1849 | 0.29352 | -2.8291 | -1.4874 | -1.1096 | -0.1764
42838.4255 | 447 | 22.8958 | 22.8623 | 22.8445 | 22.764 | 22.3778 | 21.705 | 22.7009 | 21.7618 | 22.3544 | 22.3581 | 22.3243 | 21.9766 | 21.1892 | 22.1581 | 21.6024 | 21.7844 | 21.9082 | 21.092 | 21.1969 | 21.5825 | 20.4822 | 20.9934 | 24.0682 | 21.8912 | 22.0158 | 27.4337 | 159.2754 | 136.8151 | 171.5813 | 22.1025 | 21.9534 | 25.5813 | 22.0197 | 22.0519 | 27.1468 | 68.1203 | 174.7589 |  | 103.6661 | 137.9648 | 135.5193 | 136.079 |  | 17.4578 | 18.3689 | 17.432 | 18.3761 | 19.3735 | 31.0586 | 119.2355 | 15.6531 | 17.1703 | 15.7478 | 18.6434 | 18.6186 | 45.9909 | 49.3963 | 45.3299 | 21.6485 |  |  | 0.59952 | -0.31745 | -29.5125 | 0.31011 | 0.35498 | -153.4296 | 18.6663 | 0.61667 | 0.18886 | 0.012489 | 0.38968 | 0.00036306 | 0.00037949 | 0.63544 | 21.8421 | 21.9616 | 22.168 | 22.2226 | 22.0283 | 21.3248 | 20.1344 | 22.1835 | 22.3724 | 22.3978 | 22.3421 | 21.9619 | 21.1941 | 22.2783 | 86.0276 | 52.8095 | 55.9627 | 38.4509 | 33.2823 | 55.0495 | 36.4439 | 22.323 | 22.0846 | 21.6519 | 22.0495 | 21.7748 | 21.4605 | 21.935 | 21.7088 | 24.2624 | 59.2012 | 157.7192 | 123.2154 | 90.3965 | 1.2474 | 0.78784 | 70.0302 | 21.9069 | 22.2256 | 20.622 | 21.5764 | 22.0289 | 21.9634 | 22.339 | 31.1641 | 21.809 | 21.732 | 25.2813 | 160.0585 | 205.8749 | 126.1506 | 127.992 | 88.9895 |  | 59.3793 | 133.9746 | 64.9728 | 100.4674 | 79.7858 | 73.4366 |  | 81.9567 |  |  | 24.1972 | 28.166 | 63.8825 | [5 empty] | 21.8956 | 75.5469 | 21.6974 | 22.0987 | 34.738 | 21.2763 | 21.9078 | 31.3394 | 103.8062 | 210.1411 |  | 91.4904 | 153.3659 | 24.0592 | 80.8157 | 169.6813 | 54.7959 | 121.9161 | 27.294 | 121.3892 | 27.1246 | 119.8911 | 18.8984 | 90.2229 | 145.857 | 33.0394 | 82.1144 | 167.3266 | 23.4322 | 79.8922 | 159.1019 | 24.2564 | 109.4272 | 35.0806 | 117.282 | 27.8896 | 127.8504 | 1.5343 | 19.0925 | 1.6279 | 0.066251 | -27.1572 | 3.0952 | 228.47 | 51.52 | 1.1379 | -0.67041 | -6.464 | 0.66261 | 0.72419 | -15.0559 | 5.2515 | -0.12924 | -1.1756 | 0.30527 | -2.7842 | -1.6479 | -1.1186 | -0.17475
42838.4255 | 448 | 22.8954 | 22.8509 | 22.836 | 22.7611 | 22.372 | 21.7031 | 22.6926 | 21.7548 | 22.341 | 22.347 | 22.3173 | 21.9728 | 21.1776 | 22.1562 | 21.6 | 21.7741 | 21.8978 | 21.0908 | 21.193 | 21.5791 | 20.4781 | 21.0065 | 24.0814 | 21.8833 | 22.0041 | 27.4462 | 159.44 | 137.1147 | 171.7258 | 22.1077 | 21.9583 | 25.6155 | 22.0256 | 22.0653 | 27.1883 | 68.3706 | 173.4572 |  | 103.894 | 138.1803 | 135.7501 | 136.2374 |  | 17.4629 | 18.3776 | 17.4304 | 18.3686 | 19.3524 | 31.1037 | 119.6221 | 15.6517 | 17.1706 | 15.7607 | 18.6489 | 18.6113 | 46.0317 | 49.3985 | 45.3435 | 21.6433 |  |  | 0.43195 | -0.17223 | -29.3404 | 0.37845 | 0.23735 | -153.9237 | 18.3943 | 1.0037 | 0.091555 | 0.13606 | 0.38968 | 0.00036141 | 0.00035649 | 0.64178 | 21.8388 | 21.9625 | 22.1588 | 22.215 | 22.0264 | 21.3217 | 20.1301 | 22.1785 | 22.3609 | 22.3941 | 22.3379 | 21.9576 | 21.1895 | 22.2623 | 86.0844 | 54.5421 | 58.3211 | 38.102 | 32.6907 | 55.2139 | 36.573 | 22.3218 | 22.0835 | 21.6384 | 22.041 | 21.7659 | 21.4559 | 21.931 | 21.7031 | 24.2768 | 59.3914 | 157.9296 | 123.5139 | 91.3003 | 1.1761 | 0.78784 | 70.1109 | 21.8949 | 22.2244 | 20.6188 | 21.5593 | 22.0278 | 21.947 | 22.341 | 31.2144 | 21.8039 | 21.726 | 25.2998 | 160.0968 | 205.8491 | 126.6048 | 128.4179 | 88.289 |  | 59.5692 | 132.2862 | 65.1837 | 102.8845 | 80.1297 | 74.2876 |  | 82.2272 |  |  | 24.213 | 28.1847 | 63.7022 | [5 empty] | 21.9022 | 75.6719 | 21.6952 | 22.0911 | 34.7578 | 21.2772 | 21.9066 | 31.3961 | 104.1456 | 210.3337 |  | 91.7665 | 153.3591 | 24.0979 | 81.1368 | 169.4896 | 54.8312 | 122.3621 | 27.3592 | 121.5571 | 27.1751 | 120.2486 | 18.9353 | 90.4764 | 146.0495 | 33.0988 | 82.3705 | 167.7084 | 23.4516 | 80.6092 | 159.3785 | 24.3354 | 109.6397 | 35.1862 | 117.6425 | 27.942 | 127.9989 | 1.656 | 19.0843 | 1.6363 | 0.066621 | -27.1937 | 3.0953 | 232.38 | 52 | 0.96606 | -0.49381 | -6.4452 | 0.732 | 0.59222 | -15.0813 | 5.2135 | -0.10292 | -1.121 | 0.25112 | -2.7709 | -1.8947 | -1.1138 | -0.19299
42838.4255 | 449 | 22.8949 | 22.8578 | 22.8419 | 22.7618 | 22.3816 | 21.7137 | 22.7011 | 21.7506 | 22.3504 | 22.3486 | 22.3145 | 21.977 | 21.1824 | 22.1639 | 21.6082 | 21.7744 | 21.911 | 21.0819 | 21.1932 | 21.5826 | 20.4828 | 21.0024 | 24.1013 | 21.8949 | 22.0203 | 27.4851 | 159.6685 | 137.3856 | 172.5234 | 22.1042 | 21.9619 | 25.6263 | 22.0178 | 22.0634 | 27.2096 | 68.6167 | 172.3194 |  | 104.1367 | 138.3078 | 136.0065 | 133.1891 |  | 17.4792 | 18.3914 | 17.4381 | 18.3673 | 19.3381 | 31.325 | 120.1316 | 15.6747 | 17.1757 | 15.7361 | 18.6615 | 18.624 | 46.0657 | 49.3937 | 45.3603 | 21.6567 |  |  | 0.50029 | -0.31482 | -28.3054 | 0.34166 | 0.37666 | -152.7626 | 19.2413 | 0.75664 | 0.041543 | 0.21621 | 0.39193 | 0.00036963 | 0.00033677 | 0.62476 | 21.8348 | 21.9641 | 22.1561 | 22.2084 | 22.0273 | 21.3187 | 20.1257 | 22.1729 | 22.3557 | 22.3873 | 22.3416 | 21.9577 | 21.1872 | 22.2696 | 84.2235 | 52.2574 | 58.8221 | 38.2586 | 31.8721 | 55.3379 | 36.6731 | 22.3126 | 22.0765 | 21.6373 | 22.0384 | 21.7644 | 21.4529 | 21.9279 | 21.6987 | 24.2938 | 59.5733 | 158.843 | 124.2959 | 91.6183 | 1.0524 | 0.32166 | 70.1058 | 21.8972 | 22.231 | 20.6213 | 21.5695 | 22.0273 | 21.9552 | 22.3513 | 31.2669 | 21.8074 | 21.7297 | 25.3333 | 160.235 | 205.6881 | 127.0761 | 128.7398 | 88.7285 |  | 59.7836 | 131.2724 | 65.4051 | 105.2453 | 80.5763 | 74.716 |  | 82.4813 |  |  | 24.2403 | 28.2169 | 63.9377 | [5 empty] | 21.8893 | 76.55 | 21.6922 | 22.0908 | 34.7841 | 21.2806 | 21.912 | 31.4195 | 104.4895 | 210.9487 |  | 91.9163 | 153.3987 | 24.1038 | 81.4366 | 169.4139 | 54.9197 | 122.8243 | 27.4033 | 121.7545 | 27.1881 | 120.4398 | 18.9474 | 90.8058 | 146.2407 | 33.14 | 82.6492 | 167.8196 | 23.4546 | 81.1289 | 159.7326 | 24.391 | 109.7922 | 35.2709 | 117.9841 | 27.9578 | 128.2519 | 1.3056 | 19.0753 | 1.6443 | 0.066686 | -27.0956 | 3.0952 | 246.4 | 52.64 | 1.0406 | -0.66765 | -6.3307 | 0.69553 | 0.74631 | -15.0297 | 5.3341 | -0.10738 | -1.0847 | 0.20242 | -2.5493 | -1.9386 | -1.0201 | -0.19525
42838.4255 | 450 | 22.8974 | 22.8579 | 22.8428 | 22.77 | 22.385 | 21.7009 | 22.701 | 21.7574 | 22.3437 | 22.3503 | 22.3206 | 21.9764 | 21.1833 | 22.169 | 21.6021 | 21.7718 | 21.8978 | 21.0768 | 21.1863 | 21.579 | 20.475 | 20.9989 | 24.1161 | 21.8884 | 22.0163 | 27.5045 | 160.0117 | 137.7378 | 173.5555 | 22.1001 | 21.9591 | 25.6566 | 22.0241 | 22.0608 | 27.2415 | 68.8284 | 172.5626 |  | 104.4765 | 138.4326 | 136.362 | 132.6808 |  | 17.4873 | 18.4006 | 17.4491 | 18.3655 | 19.3223 | 31.7244 | 120.6603 | 15.7027 | 17.1644 | 15.7559 | 18.6555 | 18.6165 | 46.0753 | 49.3802 | 45.3604 | 21.6433 |  |  | 0.48124 | -0.21888 | -28.0636 | 0.53879 | 0.30109 | -158.7739 | 19.1736 | 0.99517 | 0.029283 | 0.19355 | 0.41433 | 0.00034499 | 0.0003762 | 0.62268 | 21.8309 | 21.9577 | 22.1603 | 22.2128 | 22.0237 | 21.3118 | 20.1239 | 22.1743 | 22.3499 | 22.3909 | 22.3443 | 21.9571 | 21.1838 | 22.2673 | 82.2549 | 50.5685 | 56.9543 | 38.2156 | 32.3056 | 55.4428 | 36.7503 | 22.3145 | 22.0805 | 21.6375 | 22.0402 | 21.773 | 21.4596 | 21.9244 | 21.7131 | 24.3176 | 59.7615 | 159.7289 | 125.0095 | 91.6363 | 1.2474 | 0.40325 | 70.6803 | 21.8988 | 22.2157 | 20.6216 | 21.5746 | 22.0297 | 21.9562 | 22.3501 | 31.3152 | 21.8014 | 21.7343 | 25.3433 | 160.262 | 205.6498 | 127.4488 | 129.0844 | 88.7642 |  | 59.9877 | 130.9134 | 65.6215 | 103.9974 | 80.8753 | 74.4642 |  | 82.719 |  |  | 24.2915 | 28.2458 | 63.9815 | [5 empty] | 21.8893 | 77.2958 | 21.7034 | 22.0958 | 34.8042 | 21.2805 | 21.9194 | 31.4528 | 104.8709 | 211.1911 |  | 92.1961 | 153.6665 | 24.1248 | 81.6915 | 169.6884 | 55.0435 | 123.2754 | 27.4719 | 121.9948 | 27.2188 | 120.7342 | 18.973 | 91.0812 | 146.4995 | 33.1876 | 82.9765 | 168.1542 | 23.484 | 81.6934 | 159.9969 | 24.4369 | 110.1285 | 35.3563 | 118.4139 | 28.0082 | 128.5548 | 1.6041 | 19.0672 | 1.653 | 0.067165 | -27.0732 | 3.0952 | 244.3 | 51.04 | 1.0218 | -0.55671 | -6.3037 | 0.87344 | 0.66769 | -15.3326 | 5.3282 | -0.10099 | -1.0669 | 0.24839 | -2.3181 | -1.7219 | -0.99819 | -0.18895
42838.4255 | 451 | 22.9035 | 22.8619 | 22.8554 | 22.7697 | 22.3785 | 21.7029 | 22.7098 | 21.7631 | 22.3552 | 22.3642 | 22.3313 | 21.9789 | 21.1946 | 22.1641 | 21.6021 | 21.7853 | 21.9014 | 21.0829 | 21.198 | 21.5898 | 20.4789 | 21.0125 | 24.1474 | 21.8966 | 22.0309 | 27.5308 | 160.3353 | 138.1562 | 173.1624 | 22.0995 | 21.9596 | 25.6734 | 22.0211 | 22.0613 | 27.2664 | 69.0579 | 172.7889 |  | 104.7528 | 138.5573 | 136.6124 | 132.5648 |  | 17.5076 | 18.418 | 17.4672 | 18.3728 | 19.3231 | 31.8193 | 121.2759 | 15.729 | 17.174 | 15.7382 | 18.6644 | 18.623 | 46.0684 | 49.3875 | 45.3683 | 21.649 |  |  | 0.62975 | -0.32928 | -28.5012 | 0.54273 | 0.21895 | -151.9504 | 19.0185 | 0.8828 | 0.0287 | 0.25712 | 0.26382 | 0.00036963 | 0.00033184 | 0.61838 | 21.833 | 21.9506 | 22.1576 | 22.2101 | 22.0219 | 21.3091 | 20.1273 | 22.1745 | 22.3574 | 22.3903 | 22.3354 | 21.9547 | 21.1786 | 22.262 | 82.6737 | 50.8021 | 54.8553 | 38.0775 | 32.1053 | 55.597 | 36.8003 | 22.3223 | 22.086 | 21.6536 | 22.0572 | 21.78 | 21.4692 | 21.9475 | 21.7196 | 24.3446 | 59.9804 | 160.7383 | 125.6553 | 91.4464 | 1.228 | 0.69198 | 70.4692 | 21.8972 | 22.2285 | 20.6243 | 21.5792 | 22.027 | 21.95 | 22.3595 | 31.3628 | 21.8207 | 21.7395 | 25.3781 | 160.3581 | 205.5569 | 127.6658 | 129.3041 | 88.4967 |  | 60.1756 | 131.2881 | 65.8156 | 104.1659 | 81.2147 | 74.6547 |  | 82.957 |  |  | 24.3293 | 28.2753 | 64.3943 | [5 empty] | 21.8896 | 77.7759 | 21.696 | 22.0913 | 34.8261 | 21.2799 | 21.9182 | 31.4939 | 105.227 | 211.2413 |  | 92.4037 | 153.8295 | 24.1473 | 81.9388 | 169.6654 | 55.1795 | 123.6114 | 27.5119 | 122.4187 | 27.2366 | 120.9183 | 18.9734 | 91.6139 | 146.6443 | 33.2432 | 83.4023 | 169.0396 | 23.4987 | 82.2894 | 160.1415 | 24.4816 | 110.4755 | 35.411 | 118.955 | 28.0738 | 128.8103 | 1.2793 | 19.0614 | 1.6614 | 0.067042 | -27.0792 | 3.0952 | 249.78 | 52.53 | 1.1683 | -0.68284 | -6.3529 | 0.87666 | 0.56947 | -15.0019 | 5.3074 | -0.086764 | -1.0702 | 0.25656 | -2.3463 | -1.4828 | -0.98651 | -0.17576
42838.4255 | 452 | 22.9031 | 22.8643 | 22.8554 | 22.7746 | 22.3804 | 21.7067 | 22.7093 | 21.7629 | 22.3522 | 22.3567 | 22.3311 | 21.9846 | 21.2019 | 22.162 | 21.6047 | 21.7804 | 21.9074 | 21.0825 | 21.1954 | 21.5968 | 20.4849 | 21.0193 | 24.1733 | 21.8946 | 22.032 | 27.5676 | 160.7471 | 138.5814 | 174.396 | 22.103 | 21.9678 | 25.6932 | 22.0208 | 22.0633 | 27.3015 | 69.3162 | 171.9962 |  | 105.0029 | 138.8273 | 136.8621 | 131.5961 |  | 17.5191 | 18.4334 | 17.4708 | 18.3702 | 19.3095 | 31.616 | 121.7123 | 15.7394 | 17.172 | 15.6998 | 18.6693 | 18.626 | 46.06 | 49.3938 | 45.3747 | 21.6514 |  |  | 0.75197 | -0.31154 | -28.377 | 0.42971 | 0.10856 | -152.9834 | 19.0271 | 0.6837 | 0.044657 | 0.15956 | 0.37822 | 0.00033513 | 0.00031706 | 0.59053 | 21.8408 | 21.9566 | 22.1589 | 22.2147 | 22.0279 | 21.3168 | 20.1309 | 22.1817 | 22.3609 | 22.3923 | 22.3423 | 21.9591 | 21.1767 | 22.2644 | 87.1581 | 51.5606 | 54.3577 | 37.9229 | 32.4195 | 55.7892 | 36.8563 | 22.3208 | 22.0826 | 21.654 | 22.0448 | 21.7774 | 21.4687 | 21.9412 | 21.7186 | 24.354 | 60.1589 | 161.0158 | 125.9967 | 91.1425 | 0.93386 | -0.18218 | 70.6496 | 21.8935 | 22.2288 | 20.6321 | 21.585 | 22.0292 | 21.9584 | 22.3654 | 31.4148 | 21.8073 | 21.7451 | 25.4021 | 160.5138 | 205.8223 | 127.7878 | 129.4937 | 88.6272 |  | 60.37 | 132.0672 | 66.073 | 104.62 | 81.609 | 74.928 |  | 83.1894 |  |  | 24.3319 | 28.3145 | 65.6394 | [5 empty] | 21.8881 | 78.1143 | 21.6959 | 22.0985 | 34.8519 | 21.2895 | 21.9135 | 31.5207 | 105.5673 | 211.595 |  | 92.4517 | 153.8004 | 24.1731 | 82.1858 | 169.4513 | 55.3224 | 123.9361 | 27.5607 | 122.8171 | 27.2772 | 121.1542 | 18.9688 | 92.147 | 146.8484 | 33.29 | 83.7541 | 169.532 | 23.5114 | 82.7978 | 160.2729 | 24.4968 | 110.7713 | 35.4456 | 119.4378 | 28.1142 | 129.119 | 1.3546 | 19.0571 | 1.6701 | 0.066105 | -27.3454 | 3.0953 | 249.77 | 51.27 | 1.2785 | -0.66421 | -6.3392 | 0.78007 | 0.40085 | -15.0478 | 5.3068 | -0.083353 | -1.0824 | 0.25889 | -2.8216 | -1.4209 | -0.95007 | -0.16086
42838.4255 | 453 | 22.8924 | 22.869 | 22.85 | 22.7728 | 22.3822 | 21.7031 | 22.7058 | 21.7643 | 22.3517 | 22.354 | 22.3283 | 21.9757 | 21.1977 | 22.16 | 21.613 | 21.7788 | 21.9089 | 21.0811 | 21.2001 | 21.5957 | 20.4868 | 21.024 | 24.1874 | 21.8906 | 22.0318 | 27.5981 | 161.4305 | 138.9661 | 175.6869 | 22.1065 | 21.9726 | 25.7194 | 22.0215 | 22.073 | 27.3395 | 69.547 | 172.546 |  | 105.2979 | 139.2351 | 137.0944 | 131.2764 |  | 17.5327 | 18.4519 | 17.4838 | 18.3801 | 19.3004 | 31.4213 | 121.9985 | 15.7835 | 17.1761 | 15.7279 | 18.6794 | 18.6323 | 46.045 | 49.393 | 45.3753 | 21.6534 |  |  | 0.65997 | -0.55861 | -28.4211 | 0.47045 | 0.50282 | -154.3318 | 18.9705 | 0.62718 | 0.094085 | 0.2225 | 0.52456 | 0.00033349 | 0.00034827 | 0.54214 | 21.845 | 21.9564 | 22.1605 | 22.2038 | 22.0262 | 21.3102 | 20.1354 | 22.1645 | 22.3543 | 22.3944 | 22.3366 | 21.9582 | 21.1845 | 22.2616 | 86.7938 | 49.4328 | 48.2995 | 36.7925 | 33.0299 | 55.9484 | 36.8581 | 22.3235 | 22.0891 | 21.6521 | 22.0517 | 21.7752 | 21.4669 | 21.9348 | 21.7179 | 24.3805 | 60.3463 | 161.2603 | 126.4861 | 91.9272 | 0.88137 | -0.19664 | 70.6097 | 21.8968 | 22.2229 | 20.6278 | 21.5657 | 22.0158 | 21.9542 | 22.3549 | 31.4546 | 21.8027 | 21.735 | 25.4098 | 160.7414 | 205.7622 | 127.9247 | 129.6619 | 88.4583 |  | 60.5509 | 133.4465 | 66.3324 | 103.4671 | 81.9689 | 74.2939 |  | 83.4172 |  |  | 24.3304 | 28.3617 | 65.3865 | [5 empty] | 21.9002 | 78.1998 | 21.6962 | 22.1004 | 34.8763 | 21.2866 | 21.9165 | 31.5425 | 105.95 | 212.1667 |  | 92.478 | 153.8508 | 24.1971 | 82.4661 | 169.3156 | 55.4203 | 124.3024 | 27.6143 | 123.147 | 27.3244 | 121.4616 | 18.9625 | 92.6114 | 147.0314 | 33.3244 | 84.0234 | 169.8498 | 23.5061 | 83.2139 | 160.3095 | 24.5002 | 111.1733 | 35.4718 | 119.8913 | 28.14 | 129.227 | 1.168 | 19.0446 | 1.6795 | 0.065655 | -27.1365 | 3.0952 | 240.91 | 51.55 | 1.1994 | -0.88944 | -6.3443 | 0.81624 | 0.86242 | -15.1091 | 5.2973 | -0.072113 | -1.1112 | 0.30456 | -2.7622 | -0.74758 | -0.93267 | -0.17588
42838.4255 | 454 | 22.8844 | 22.8595 | 22.8438 | 22.7649 | 22.3729 | 21.7042 | 22.6953 | 21.765 | 22.3503 | 22.3569 | 22.3221 | 21.9718 | 21.1842 | 22.1517 | 21.6106 | 21.7791 | 21.9138 | 21.0908 | 21.2023 | 21.6005 | 20.4907 | 21.0227 | 24.2063 | 21.8973 | 22.041 | 27.6296 | 161.9133 | 139.3916 | 175.9128 | 22.1067 | 21.9745 | 25.7385 | 22.0217 | 22.0742 | 27.3659 | 69.7469 | 173.1641 |  | 105.6195 | 139.5622 | 137.3866 | 132.1606 |  | 17.5446 | 18.4637 | 17.4934 | 18.3883 | 19.3146 | 31.3639 | 121.8963 | 15.8325 | 17.1736 | 15.7546 | 18.6821 | 18.6381 | 46.0343 | 49.3865 | 45.3791 | 21.6572 |  |  | 0.44773 | -0.58884 | -28.2962 | 0.295 | 0.18675 | -153.4375 | 19.698 | 0.54439 | 0.048549 | -0.07185 | 0.3428 | 0.00034006 | 0.00036799 | 0.51958 | 21.8343 | 21.9596 | 22.1496 | 22.206 | 22.0142 | 21.3117 | 20.1175 | 22.1721 | 22.3436 | 22.3857 | 22.3335 | 21.945 | 21.173 | 22.2669 | 86.382 | 46.7998 | 44.6144 | 35.016 | 32.1213 | 56.1089 | 36.8391 | 22.3287 | 22.0942 | 21.6586 | 22.0529 | 21.7808 | 21.4761 | 21.942 | 21.723 | 24.4061 | 60.5652 | 161.762 | 127.0557 | 93.2086 | 0.8043 | 0.012204 | 71.0032 | 21.8973 | 22.2209 | 20.6409 | 21.5749 | 22.0277 | 21.9585 | 22.3721 | 31.5106 | 21.8053 | 21.7402 | 25.4353 | 160.9831 | 205.7938 | 128.0377 | 129.7742 | 87.7793 |  | 60.7325 | 133.5252 | 66.5555 | 103.1354 | 82.2655 | 73.7987 |  | 83.6234 |  |  | 24.3435 | 28.4039 | 64.8861 | [5 empty] | 21.8986 | 77.998 | 21.7005 | 22.0994 | 34.8634 | 21.2841 | 21.9207 | 31.5594 | 106.3592 | 212.8739 |  | 92.6604 | 154.0847 | 24.2066 | 82.7691 | 169.3946 | 55.4556 | 124.6826 | 27.6581 | 123.4627 | 27.3663 | 121.7259 | 18.942 | 92.9472 | 147.2198 | 33.3722 | 84.283 | 170.1641 | 23.4989 | 83.6305 | 160.3423 | 24.4891 | 111.653 | 35.5124 | 120.372 | 28.1716 | 129.645 | 1.4726 | 19.0349 | 1.6875 | 0.064864 | -27.1401 | 3.0952 | 242.56 | 52.16 | 0.98816 | -0.91321 | -6.3305 | 0.64637 | 0.52554 | -15.0639 | 5.3974 | -0.046676 | -1.1052 | 0.32503 | -2.6973 | -0.34036 | -0.94985 | -0.20355
42838.4255 | 455 | 22.8898 | 22.8557 | 22.8398 | 22.7636 | 22.3727 | 21.6985 | 22.6876 | 21.7565 | 22.3503 | 22.3498 | 22.3178 | 21.9728 | 21.1876 | 22.1523 | 21.6015 | 21.7776 | 21.9079 | 21.0815 | 21.1941 | 21.6017 | 20.4767 | 21.0211 | 24.2248 | 21.8928 | 22.0403 | 27.6494 | 162.2501 | 139.8795 | 176.0582 | 22.1096 | 21.9722 | 25.7682 | 22.0215 | 22.0791 | 27.3972 | 69.9498 | 172.9688 |  | 105.8961 | 139.7917 | 137.5881 | 132.8171 |  | 17.5491 | 18.4705 | 17.5052 | 18.4007 | 19.3212 | 31.3449 | 121.9919 | 15.857 | 17.1741 | 15.7798 | 18.6807 | 18.6284 | 46.0371 | 49.3788 | 45.3667 | 21.6562 |  |  | 0.49964 | -0.30234 | -27.965 | 0.24703 | 0.32278 | -148.0892 | 19.3924 | 0.80592 | -0.039216 | 0.10711 | 0.1758 | 0.00039756 | 0.00036799 | 0.49648 | 21.8425 | 21.9616 | 22.1594 | 22.2113 | 22.0219 | 21.32 | 20.1251 | 22.1812 | 22.3573 | 22.3949 | 22.3364 | 21.9621 | 21.1863 | 22.2707 | 88.1093 | 49.5307 | 43.4808 | 33.7203 | 31.6489 | 56.2875 | 36.8155 | 22.3193 | 22.0877 | 21.6541 | 22.0434 | 21.7737 | 21.4736 | 21.9341 | 21.7168 | 24.4204 | 60.778 | 162.0422 | 127.4368 | 93.5127 | 1.0349 | 0.45214 | 70.8814 | 21.8918 | 22.2196 | 20.6347 | 21.561 | 22.021 | 21.9496 | 22.3712 | 31.5519 | 21.8024 | 21.7469 | 25.4611 | 161.5352 | 205.6267 | 128.1967 | 129.9599 | 87.9396 |  | 60.9257 | 132.74 | 66.7868 | 102.491 | 82.5485 | 73.7513 |  | 83.8255 |  |  | 24.3282 | 28.4129 | 65.0187 | [5 empty] | 21.8881 | 77.9865 | 21.6963 | 22.0901 | 34.8687 | 21.2785 | 21.917 | 31.5813 | 106.7605 | 213.1495 |  | 92.9288 | 154.4363 | 24.229 | 82.979 | 169.5921 | 55.4786 | 125.0521 | 27.7038 | 123.9064 | 27.405 | 122.0035 | 18.9277 | 93.0649 | 147.4151 | 33.4367 | 84.5346 | 170.5006 | 23.511 | 84.0709 | 160.6368 | 24.4727 | 112.0637 | 35.5672 | 120.782 | 28.209 | 130.173 | 1.6059 | 19.0257 | 1.6961 | 0.064537 | -27.175 | 3.0952 | 270.17 | 51.27 | 1.044 | -0.65437 | -6.2934 | 0.59149 | 0.69089 | -14.7985 | 5.3552 | -0.044129 | -1.0749 | 0.35368 | -2.8679 | -0.21718 | -0.9606 | -0.20429
42838.4256 | 456 | 22.9019 | 22.8633 | 22.849 | 22.7698 | 22.3819 | 21.7085 | 22.6981 | 21.7628 | 22.3517 | 22.3557 | 22.3263 | 21.9854 | 21.1966 | 22.1666 | 21.6028 | 21.7757 | 21.9084 | 21.0759 | 21.194 | 21.6 | 20.4801 | 21.0224 | 24.2459 | 21.8927 | 22.0422 | 27.6796 | 162.6087 | 140.281 | 176.1972 | 22.1052 | 21.969 | 25.788 | 22.0244 | 22.0728 | 27.431 | 70.1698 | 174.3633 |  | 106.1821 | 140.0226 | 137.6266 | 132.7687 |  | 17.5597 | 18.4903 | 17.5193 | 18.4266 | 19.347 | 31.293 | 122.1621 | 15.8175 | 17.1894 | 15.8034 | 18.6885 | 18.6288 | 46.0428 | 49.3753 | 45.3645 | 21.6566 |  |  | 0.70531 | -0.40157 | -27.8145 | 0.25097 | 0.080956 | -152.162 | 19.0165 | 0.61076 | 0.07229 | 0.22942 | 0.36728 | 0.00035156 | 0.00037949 | 0.40666 | 21.8485 | 21.9674 | 22.165 | 22.2162 | 22.0272 | 21.3223 | 20.1298 | 22.1809 | 22.3632 | 22.3972 | 22.3449 | 21.9713 | 21.1891 | 22.2687 | 87.8574 | 53.7401 | 45.3515 | 33.5834 | 32.2284 | 56.4407 | 36.8479 | 22.3302 | 22.1039 | 21.6486 | 22.0543 | 21.788 | 21.4755 | 21.9428 | 21.7219 | 24.4399 | 61.0028 | 162.588 | 127.8538 | 93.0828 | 1.2506 | 0.55427 | 71.0352 | 21.9003 | 22.2239 | 20.6438 | 21.5714 | 22.0278 | 21.9665 | 22.3817 | 31.6134 | 21.8092 | 21.7513 | 25.493 | 161.924 | 205.4242 | 128.4493 | 130.3124 | 88.0935 |  | 61.1315 | 132.6828 | 67.0036 | 102.815 | 82.8894 | 74.1161 |  | 84.0772 |  |  | 24.3236 | 28.4221 | 65.004 | [5 empty] | 21.8954 | 78.155 | 21.7052 | 22.0964 | 34.8894 | 21.2815 | 21.9211 | 31.6165 | 107.1093 | 213.3465 |  | 93.2209 | 154.8538 | 24.2542 | 83.1781 | 170.0134 | 55.5348 | 125.3568 | 27.7401 | 124.429 | 27.4391 | 122.2264 | 18.938 | 93.0222 | 147.6555 | 33.5143 | 84.7943 | 171.2191 | 23.5474 | 84.2824 | 160.9868 | 24.4835 | 112.3873 | 35.6258 | 121.0224 | 28.2434 | 130.6037 | 1.8189 | 19.0157 | 1.7047 | 0.064755 | -27.2229 | 3.0952 | 277.22 | 52.77 | 1.2406 | -0.75417 | -6.2766 | 0.59622 | 0.34597 | -14.9994 | 5.3026 | -0.040944 | -1.0653 | 0.35763 | -2.8217 | -0.42122 | -0.95113 | -0.1842
42838.4256 | 457 | 22.8975 | 22.864 | 22.8401 | 22.7636 | 22.3716 | 21.6981 | 22.6928 | 21.7506 | 22.3479 | 22.3554 | 22.3257 | 21.9755 | 21.1851 | 22.1604 | 21.5947 | 21.775 | 21.9104 | 21.0797 | 21.1988 | 21.5969 | 20.4852 | 21.0321 | 24.2622 | 21.8904 | 22.0446 | 27.7059 | 162.9583 | 140.7187 | 175.4367 | 22.1099 | 21.9809 | 25.8111 | 22.0248 | 22.0814 | 27.4791 | 70.4168 | 175.361 |  | 106.4901 | 140.3631 | 137.7081 | 132.8352 |  | 17.5609 | 18.4994 | 17.5169 | 18.4371 | 19.3772 | 31.2705 | 122.3188 | 15.7641 | 17.179 | 15.805 | 18.6895 | 18.6441 | 46.0505 | 49.3727 | 45.3627 | 21.6517 |  |  | 0.52264 | -0.39434 | -27.6542 | 0.066326 | 0.22749 | -153.2009 | 18.9784 | 0.48525 | -0.0020472 | 0.036616 | 0.21816 | 0.00035813 | 0.00034006 | 0.36198 | 21.8476 | 21.9635 | 22.1634 | 22.2143 | 22.0249 | 21.3115 | 20.1257 | 22.1774 | 22.353 | 22.3923 | 22.3415 | 21.9595 | 21.1858 | 22.2657 | 86.8878 | 54.9603 | 48.7964 | 34.7275 | 33.3469 | 56.5938 | 36.9173 | 22.3239 | 22.0853 | 21.6441 | 22.052 | 21.7776 | 21.4754 | 21.9382 | 21.7228 | 24.46 | 61.1903 | 162.8888 | 128.2091 | 92.9232 | 1.0206 | 0.41885 | 71.1378 | 21.8977 | 22.2176 | 20.6602 | 21.5755 | 22.0219 | 21.9635 | 22.3879 | 31.6583 | 21.8173 | 21.7579 | 25.5115 | 162.0219 | 205.1575 | 128.7363 | 130.5948 | 87.8322 |  | 61.355 | 132.4755 | 67.1875 | 105.8967 | 83.2334 | 74.9137 |  | 84.331 |  |  | 24.3207 | 28.4582 | 64.8906 | [5 empty] | 21.8948 | 79.3931 | 21.6991 | 22.094 | 34.8828 | 21.292 | 21.9196 | 31.6448 | 107.4166 | 213.2911 |  | 93.5748 | 155.288 | 24.2817 | 83.4431 | 170.2731 | 55.6064 | 125.6586 | 27.7612 | 124.8161 | 27.4751 | 122.4185 | 18.9316 | 93.24 | 147.8531 | 33.5661 | 85.0696 | 172.0191 | 23.5838 | 84.2864 | 161.5029 | 24.529 | 112.7214 | 35.6911 | 121.1781 | 28.2656 | 130.9318 | 1.2982 | 19.007 | 1.7135 | 0.065996 | -27.2771 | 3.0951 | 286.54 | 51.5 | 1.0671 | -0.74736 | -6.2586 | 0.30651 | 0.57995 | -15.0499 | 5.2971 | -0.025585 | -1.0528 | 0.28511 | -2.6957 | -0.79581 | -0.94385 | -0.17297
42838.4256 | 458 | 22.899 | 22.8671 | 22.8467 | 22.768 | 22.3769 | 21.7092 | 22.7013 | 21.7639 | 22.349 | 22.3606 | 22.3229 | 21.9803 | 21.1894 | 22.1614 | 21.5913 | 21.7704 | 21.9046 | 21.0776 | 21.1929 | 21.6041 | 20.4776 | 21.0369 | 24.2869 | 21.8928 | 22.0441 | 27.7282 | 163.2434 | 141.3703 | 175.8454 | 22.0957 | 21.9777 | 25.8282 | 22.0128 | 22.0798 | 27.4957 | 70.6648 | 174.9253 |  | 106.7491 | 140.6771 | 137.9079 | 132.6483 |  | 17.5703 | 18.5019 | 17.534 | 18.4683 | 19.4227 | 31.4056 | 122.7858 | 15.7041 | 17.1788 | 15.7666 | 18.7002 | 18.6353 | 46.0809 | 49.3622 | 45.3751 | 21.6573 |  |  | 0.47138 | -0.54613 | -27.6989 | 0.32326 | 0.0251 | -151.7493 | 18.8115 | 0.46948 | 0.022278 | -0.052549 | 0.15236 | 0.00037291 | 0.00032856 | 0.49981 | 21.8462 | 21.955 | 22.1625 | 22.2116 | 22.0281 | 21.3075 | 20.1256 | 22.1797 | 22.3481 | 22.3843 | 22.3375 | 21.9566 | 21.1851 | 22.2687 | 86.2283 | 53.3324 | 50.7011 | 35.4107 | 33.9921 | 56.7276 | 36.9775 | 22.3282 | 22.0892 | 21.6512 | 22.0536 | 21.787 | 21.4851 | 21.9379 | 21.7272 | 24.4815 | 61.4118 | 163.2204 | 128.6159 | 93.1399 | 1.0445 | 0.19632 | 71.2278 | 21.9011 | 22.2222 | 20.6529 | 21.5705 | 22.0289 | 21.9601 | 22.394 | 31.7091 | 21.8084 | 21.7636 | 25.539 | 162.4532 | 205.4128 | 128.9613 | 130.8168 | 88.2415 |  | 61.5584 | 132.3262 | 67.4026 | 107.6314 | 83.5117 | 75.176 |  | 84.5722 |  |  | 24.3048 | 28.4883 | 64.3686 | [5 empty] | 21.8942 | 80.3389 | 21.6941 | 22.0907 | 34.911 | 21.2923 | 21.9164 | 31.6632 | 107.7464 | 212.959 |  | 93.8253 | 155.333 | 24.3146 | 83.842 | 170.3377 | 55.6866 | 125.9838 | 27.7887 | 125.0127 | 27.5147 | 122.6221 | 18.9313 | 93.6381 | 148.1787 | 33.6141 | 85.3987 | 172.2837 | 23.5989 | 84.3422 | 161.7826 | 24.5674 | 112.9882 | 35.7517 | 121.4256 | 28.3134 | 131.1682 | 1.3943 | 18.9968 | 1.7221 | 0.067775 | -27.219 | 3.0952 | 268.25 | 52.41 | 1.0139 | -0.87952 | -6.2637 | 0.67667 | 0.19268 | -14.9818 | 5.2749 | -0.029575 | -1.0408 | 0.24752 | -2.6064 | -1.0003 | -0.92948 | -0.17096
42838.4256 | 459 | 22.8896 | 22.8658 | 22.8431 | 22.7597 | 22.3771 | 21.7007 | 22.6994 | 21.7599 | 22.3504 | 22.3552 | 22.3215 | 21.9765 | 21.1886 | 22.1605 | 21.6014 | 21.7805 | 21.9085 | 21.088 | 21.1916 | 21.6091 | 20.4878 | 21.0377 | 24.3071 | 21.8909 | 22.0567 | 27.7657 | 163.5041 | 141.8355 | 175.596 | 22.105 | 21.9759 | 25.8593 | 22.0219 | 22.0825 | 27.5263 | 70.9133 | 175.2458 |  | 107.0133 | 141.0406 | 138.1554 | 133.3408 |  | 17.5818 | 18.5175 | 17.5435 | 18.4815 | 19.4696 | 31.6541 | 123.113 | 15.6119 | 17.1857 | 15.718 | 18.7077 | 18.6371 | 46.1168 | 49.3564 | 45.3927 | 21.6642 |  |  | 0.61135 | -0.30431 | -27.4899 | 0.32983 | 0.1401 | -151.5778 | 18.9403 | 0.34922 | -0.0059392 | -0.062829 | 0.43377 | 0.00033677 | 0.00032856 | 0.49128 | 21.8456 | 21.9555 | 22.1556 | 22.2184 | 22.0203 | 21.3059 | 20.128 | 22.1757 | 22.3497 | 22.3949 | 22.3263 | 21.9579 | 21.1742 | 22.2695 | 86.0307 | 54.5819 | 48.8486 | 35.5843 | 34.9797 | 56.8866 | 37.0029 | 22.33 | 22.0905 | 21.6603 | 22.0547 | 21.78 | 21.4812 | 21.9381 | 21.7367 | 24.5063 | 61.6448 | 163.56 | 128.9636 | 93.4019 | 0.88648 | 0.48409 | 71.4101 | 21.8965 | 22.2155 | 20.6494 | 21.5522 | 22.0166 | 21.9423 | 22.3892 | 31.7529 | 21.8018 | 21.7541 | 25.5599 | 162.564 | 205.2451 | 129.2832 | 131.0493 | 88.187 |  | 61.7958 | 131.4605 | 67.6231 | 110.0377 | 83.9366 | 75.1952 |  | 84.8867 |  |  | 24.3485 | 28.4902 | 64.2166 | [5 empty] | 21.8958 | 81.5255 | 21.6924 | 22.0933 | 34.973 | 21.2874 | 21.9158 | 31.6825 | 108.0397 | 212.932 |  | 93.9112 | 155.4411 | 24.3453 | 84.2167 | 170.4449 | 55.7983 | 126.2747 | 27.8294 | 125.3478 | 27.5483 | 123.0164 | 18.9496 | 93.8892 | 148.4981 | 33.6497 | 85.7648 | 172.4193 | 23.5919 | 84.4718 | 161.8565 | 24.5855 | 113.1737 | 35.8081 | 121.714 | 28.3615 | 131.4649 | 1.6187 | 18.9873 | 1.7305 | 0.068109 | -27.1646 | 3.0952 | 247.18 | 52.14 | 1.1543 | -0.65655 | -6.2402 | 0.68353 | 0.4554 | -14.9794 | 5.2951 | -0.019448 | -1.0086 | 0.19685 | -2.5655 | -0.79152 | -0.93952 | -0.16979
42838.4256 | 460 | 22.8876 | 22.8559 | 22.8444 | 22.7573 | 22.3715 | 21.694 | 22.6886 | 21.7543 | 22.3489 | 22.348 | 22.311 | 21.9713 | 21.1892 | 22.1574 | 21.6039 | 21.7714 | 21.8969 | 21.0697 | 21.1954 | 21.607 | 20.4823 | 21.0425 | 24.3269 | 21.8917 | 22.0479 | 27.7913 | 163.8572 | 142.2597 | 175.5287 | 22.1099 | 21.9858 | 25.8883 | 22.0224 | 22.0949 | 27.5621 | 71.1723 | 174.6199 |  | 107.2697 | 141.2543 | 138.3761 | 134.2736 |  | 17.5821 | 18.5263 | 17.547 | 18.4907 | 19.4681 | 31.8041 | 123.051 | 15.5897 | 17.1923 | 15.6769 | 18.7177 | 18.6401 | 46.1551 | 49.3461 | 45.4055 | 21.6598 |  |  | 0.54695 | -0.33716 | -27.5077 | 0.37911 | 0.15192 | -148.929 | 18.3923 | 0.51745 | 0.030646 | -0.11465 | 0.22319 | 0.00036141 | 0.00034499 | 0.36875 | 21.8562 | 21.9634 | 22.1561 | 22.2112 | 22.024 | 21.3089 | 20.1205 | 22.1756 | 22.358 | 22.3911 | 22.3381 | 21.9528 | 21.1785 | 22.2681 | 86.059 | 54.9024 | 49.374 | 36.1604 | 35.3991 | 57.0373 | 37.05 | 22.3186 | 22.0842 | 21.651 | 22.0536 | 21.7777 | 21.4807 | 21.9354 | 21.7269 | 24.5239 | 61.8596 | 163.9096 | 129.1694 | 93.7578 | 0.90201 | -0.0054848 | 71.6565 | 21.9007 | 22.2268 | 20.6517 | 21.5652 | 22.0275 | 21.9587 | 22.4042 | 31.8065 | 21.81 | 21.7561 | 25.5848 | 162.467 | 205.5483 | 129.6104 | 131.3848 | 88.1272 |  | 61.9896 | 131.4771 | 67.7807 | 111.4102 | 84.4041 | 75.0746 |  | 85.1428 |  |  | 24.3891 | 28.4922 | 64.2774 | [5 empty] | 21.8882 | 83.3395 | 21.6896 | 22.0918 | 35.0577 | 21.2782 | 21.9196 | 31.6984 | 108.3076 | 212.5686 |  | 93.9924 | 155.4703 | 24.3841 | 84.4541 | 170.6103 | 55.8834 | 126.6526 | 27.8442 | 125.6904 | 27.577 | 123.433 | 18.9536 | 94.0571 | 149.0007 | 33.6713 | 86.0695 | 172.6558 | 23.5977 | 84.6736 | 161.9802 | 24.5933 | 113.4329 | 35.8636 | 122.0596 | 28.3986 | 131.7319 | 1.3397 | 18.9781 | 1.7392 | 0.068182 | -27.1546 | 3.0952 | 249.81 | 51.59 | 1.0917 | -0.6911 | -6.2423 | 0.73282 | 0.47435 | -14.8516 | 5.2192 | -0.010746 | -1.0033 | 0.17655 | -2.5507 | -0.84434 | -0.95584 | -0.17187
42838.4256 | 461 | 22.8868 | 22.8509 | 22.8403 | 22.7611 | 22.3668 | 21.6943 | 22.6881 | 21.7485 | 22.3434 | 22.3427 | 22.3129 | 21.9688 | 21.1851 | 22.1566 | 21.595 | 21.7772 | 21.8921 | 21.0826 | 21.2071 | 21.603 | 20.4774 | 21.0373 | 24.3429 | 21.8909 | 22.0483 | 27.8203 | 163.8748 | 142.5481 | 173.96 | 22.1122 | 21.9886 | 25.9137 | 22.0254 | 22.1031 | 27.5985 | 71.443 | 174.7245 |  | 107.5364 | 141.381 | 138.5749 | 134.5129 |  | 17.574 | 18.5382 | 17.5438 | 18.4967 | 19.4455 | 31.8953 | 122.6375 | 15.5996 | 17.1908 | 15.6199 | 18.7186 | 18.6543 | 46.1951 | 49.3394 | 45.398 | 21.6596 |  |  | 0.65209 | -0.36411 | -27.804 | 0.089322 | 0.10001 | -150.9877 | 18.7543 | 0.45502 | 0.22349 | 0.011021 | 0.36225 | 0.00034334 | 0.0003532 | 0.34496 | 21.8453 | 21.9584 | 22.1543 | 22.2108 | 22.022 | 21.3127 | 20.1299 | 22.177 | 22.3589 | 22.3912 | 22.3422 | 21.947 | 21.1752 | 22.2609 | 85.4109 | 52.4929 | 47.5695 | 35.0741 | 35.4311 | 57.171 | 37.0572 | 22.3273 | 22.0896 | 21.6538 | 22.0479 | 21.7765 | 21.4956 | 21.9394 | 21.7376 | 24.5432 | 62.0821 | 164.214 | 129.4312 | 93.8182 | 1.1134 | 0.078013 | 71.6723 | 21.8983 | 22.2213 | 20.6589 | 21.5709 | 22.0222 | 21.96 | 22.4028 | 31.8533 | 21.8095 | 21.7555 | 25.6011 | 162.6285 | 205.4102 | 129.9254 | 131.7254 | 87.6205 |  | 62.1649 | 131.2149 | 67.9655 | 112.0175 | 84.827 | 74.8597 |  | 85.3771 |  |  | 24.4493 | 28.5255 | 64.137 | [5 empty] | 21.9047 | 84.7643 | 21.7069 | 22.1012 | 35.1367 | 21.2924 | 21.9261 | 31.7559 | 108.5961 | 211.925 |  | 94.2178 | 155.7054 | 24.4264 | 84.7739 | 170.6346 | 55.9989 | 126.9832 | 27.87 | 125.9082 | 27.6177 | 123.7335 | 18.9801 | 94.599 | 149.2546 | 33.7069 | 86.3613 | 173.3366 | 23.6012 | 84.9294 | 162.3292 | 24.598 | 113.7141 | 35.9148 | 122.3719 | 28.413 | 132.08 | 1.2377 | 18.9683 | 1.7482 | 0.068203 | -27.1527 | 3.0952 | 259.42 | 52.84 | 1.1899 | -0.71819 | -6.276 | 0.35572 | 0.38492 | -14.9562 | 5.2711 | 0.0096945 | -0.98923 | 0.17582 | -2.4627 | -0.64299 | -0.95246 | -0.16547
42838.4256 | 462 | 22.8884 | 22.8598 | 22.8409 | 22.7637 | 22.375 | 21.704 | 22.6925 | 21.7489 | 22.3488 | 22.347 | 22.322 | 21.9752 | 21.1836 | 22.1596 | 21.6033 | 21.7764 | 21.9013 | 21.0722 | 21.2009 | 21.6081 | 20.4812 | 21.0404 | 24.3607 | 21.8902 | 22.0589 | 27.8498 | 163.9379 | 142.9085 | 173.0743 | 22.0993 | 21.9861 | 25.9249 | 22.017 | 22.0981 | 27.6267 | 71.705 | 175.0632 |  | 107.7783 | 141.5998 | 138.7867 | 134.9536 |  | 17.5769 | 18.542 | 17.5411 | 18.4964 | 19.4452 | 31.936 | 122.7335 | 15.631 | 17.1852 | 15.6063 | 18.7192 | 18.6489 | 46.2081 | 49.3334 | 45.3869 | 21.6606 |  |  | 0.46153 | -0.25108 | -27.6884 | 0.41788 | -0.016296 | -148.1496 | 18.3253 | 0.72641 | 0.10109 | 0.32404 | 0.33655 | 0.00034992 | 0.0003532 | 0.40071 | 21.8403 | 21.9535 | 22.1518 | 22.2082 | 22.0162 | 21.3078 | 20.1242 | 22.1727 | 22.3589 | 22.3915 | 22.3371 | 21.9545 | 21.182 | 22.2612 | 85.7541 | 53.372 | 46.4552 | 34.3226 | 34.2818 | 57.3198 | 37.0663 | 22.3191 | 22.0815 | 21.6484 | 22.0471 | 21.7718 | 21.4881 | 21.9368 | 21.7291 | 24.5543 | 62.254 | 164.2837 | 129.6888 | 93.2777 | 0.77245 | 0.47401 | 71.264 | 21.9158 | 22.2325 | 20.6709 | 21.5757 | 22.0308 | 21.9679 | 22.4242 | 31.9184 | 21.8221 | 21.7692 | 25.6423 | 162.7879 | 205.7767 | 130.2935 | 132.063 | 87.5016 |  | 62.389 | 131.5836 | 68.2072 | 110.6832 | 85.1843 | 75.2057 |  | 85.6663 |  |  | 24.4704 | 28.5277 | 64.2558 | [5 empty] | 21.8907 | 84.4177 | 21.6991 | 22.0955 | 35.1467 | 21.278 | 21.9222 | 31.7804 | 108.9235 | 212.32 |  | 94.3294 | 155.9766 | 24.4525 | 85.4115 | 170.764 | 56.0527 | 127.2777 | 27.8926 | 125.9846 | 27.6431 | 123.9521 | 18.9956 | 94.9735 | 149.3475 | 33.7314 | 86.6467 | 174.0192 | 23.6197 | 85.3867 | 162.6821 | 24.6068 | 114.0327 | 35.9409 | 122.7179 | 28.4628 | 132.3128 | 1.4829 | 18.9596 | 1.7569 | 0.067775 | -27.2643 | 3.0952 | 264.47 | 51.4 | 1.0001 | -0.5964 | -6.2629 | 0.76941 | -0.15539 | -14.8159 | 5.2108 | 0.02114 | -0.99058 | 0.22653 | -2.4831 | -0.5181 | -0.95499 | -0.14421
42838.4256 | 463 | 22.8849 | 22.8643 | 22.8549 | 22.7622 | 22.3799 | 21.7113 | 22.6983 | 21.7571 | 22.3526 | 22.3578 | 22.3249 | 21.978 | 21.1896 | 22.1613 | 21.5936 | 21.7809 | 21.9003 | 21.0737 | 21.1987 | 21.6163 | 20.4817 | 21.0562 | 24.3911 | 21.8882 | 22.0612 | 27.8859 | 164.0116 | 143.2013 | 172.4087 | 22.1021 | 21.9938 | 25.955 | 22.025 | 22.1008 | 27.657 | 71.9502 | 176.8553 |  | 108.077 | 141.8904 | 139.003 | 134.8707 |  | 17.5854 | 18.5596 | 17.5561 | 18.5144 | 19.4676 | 32.1392 | 123.1118 | 15.6814 | 17.1944 | 15.619 | 18.73 | 18.6419 | 46.1951 | 49.3172 | 45.3698 | 21.6507 |  |  | 0.48058 | -0.36214 | -27.8533 | 0.44745 | 0.25904 | -153.3724 | 18.6768 | 0.6377 | -0.04953 | 0.02277 | 0.36502 | 0.00035484 | 0.00037291 | 0.4223 | 21.8601 | 21.9634 | 22.1614 | 22.2164 | 22.0288 | 21.3156 | 20.1346 | 22.1814 | 22.3642 | 22.403 | 22.3482 | 21.9601 | 21.1862 | 22.2653 | 83.7326 | 53.7517 | 47.6013 | 35.2501 | 33.3953 | 57.4161 | 37.1245 | 22.3241 | 22.0836 | 21.6478 | 22.0488 | 21.7779 | 21.4874 | 21.9417 | 21.7318 | 24.5769 | 62.4098 | 164.2992 | 129.9983 | 92.8192 | 0.49466 | -0.0090986 | 71.5337 | 21.9011 | 22.2291 | 20.6749 | 21.5777 | 22.0252 | 21.9713 | 22.4238 | 31.9646 | 21.8187 | 21.7679 | 25.6616 | 163.062 | 205.8791 | 130.672 | 132.4808 | 88.6579 |  | 62.6024 | 131.9605 | 68.4561 | 110.0971 | 85.5661 | 75.7322 |  | 85.9345 |  |  | 24.4923 | 28.5244 | 64.6807 | [5 empty] | 21.8982 | 83.5809 | 21.7023 | 22.0992 | 35.1531 | 21.2822 | 21.9195 | 31.8134 | 109.1917 | 212.7336 |  | 94.3779 | 156.1019 | 24.4818 | 85.7983 | 171.1231 | 56.0992 | 127.5409 | 27.942 | 126.1731 | 27.6742 | 124.0914 | 19.012 | 95.0906 | 149.3348 | 33.7891 | 86.9095 | 174.5168 | 23.6424 | 85.7918 | 162.8922 | 24.6239 | 114.3887 | 35.9584 | 123.3581 | 28.5171 | 132.6574 | 1.7191 | 18.9504 | 1.7665 | 0.066229 | -27.2779 | 3.0951 | 262.45 | 52.52 | 1.0198 | -0.71627 | -6.2818 | 0.79619 | 0.61973 | -15.0798 | 5.2623 | -0.0032212 | -0.99189 | 0.25741 | -2.247 | -0.6386 | -0.94359 | -0.12582
42838.4256 | 464 | 22.8902 | 22.8626 | 22.8463 | 22.7603 | 22.3814 | 21.7005 | 22.6984 | 21.7586 | 22.3456 | 22.3601 | 22.33 | 21.9742 | 21.1917 | 22.1621 | 21.5994 | 21.7834 | 21.9121 | 21.0792 | 21.2021 | 21.6163 | 20.4824 | 21.0559 | 24.4131 | 21.895 | 22.071 | 27.9152 | 164.3898 | 143.5452 | 173.5163 | 22.1096 | 21.9964 | 25.9756 | 22.0256 | 22.1087 | 27.7005 | 72.2176 | 176.5192 |  | 108.3939 | 142.194 | 139.2648 | 134.4059 |  | 17.5887 | 18.575 | 17.5645 | 18.5322 | 19.5016 | 32.1747 | 123.6348 | 15.7139 | 17.1967 | 15.6436 | 18.744 | 18.6549 | 46.1944 | 49.3146 | 45.3609 | 21.6568 |  |  | 0.6488 | -0.21363 | -27.8658 | 0.40408 | 0.20975 | -148.3185 | 18.872 | 0.73364 | 0.30367 | 0.28481 | 0.43481 | 0.00032199 | 0.00034663 | 0.42538 | 21.8498 | 21.9487 | 22.1519 | 22.2097 | 22.0209 | 21.3074 | 20.1315 | 22.176 | 22.3541 | 22.3956 | 22.3412 | 21.9521 | 21.1732 | 22.2575 | 81.2279 | 50.1824 | 45.6519 | 35.1431 | 32.9919 | 57.4895 | 37.1201 | 22.3211 | 22.0883 | 21.6565 | 22.0505 | 21.783 | 21.4907 | 21.9352 | 21.7354 | 24.597 | 62.5677 | 164.6266 | 130.2503 | 92.3921 | 1.1774 | 0.12937 | 71.6238 | 21.9029 | 22.2296 | 20.6646 | 21.5797 | 22.0306 | 21.9617 | 22.4273 | 32.0113 | 21.8104 | 21.7744 | 25.6835 | 163.4822 | 205.7153 | 131.0321 | 132.8325 | 88.7457 |  | 62.7824 | 132.0188 | 68.6892 | 110.3275 | 85.8897 | 76.0465 |  | 86.1613 |  |  | 24.5176 | 28.55 | 64.9473 | [5 empty] | 21.89 | 83.4584 | 21.7046 | 22.0983 | 35.172 | 21.2888 | 21.9228 | 31.8621 | 109.4638 | 212.7759 |  | 94.4425 | 156.3777 | 24.5184 | 86.1225 | 171.4128 | 56.2257 | 127.7797 | 27.9749 | 126.6823 | 27.7192 | 124.3505 | 19.0008 | 95.1658 | 149.1452 | 33.8445 | 87.1034 | 175.0562 | 23.6408 | 86.1721 | 163.0827 | 24.5997 | 114.655 | 35.9762 | 123.8085 | 28.5658 | 133.0364 | 1.595 | 18.9424 | 1.7741 | 0.066185 | -27.2486 | 3.0952 | 251.52 | 51.67 | 1.1864 | -0.55015 | -6.2833 | 0.75664 | 0.5577 | -14.8302 | 5.29 | 0.00088774 | -0.98492 | 0.26339 | -1.96 | -0.42252 | -0.92076 | -0.10821
42838.4257 | 465 | 22.8855 | 22.8543 | 22.8388 | 22.7583 | 22.3797 | 21.6931 | 22.6918 | 21.7522 | 22.3416 | 22.3461 | 22.3184 | 21.9681 | 21.1826 | 22.1524 | 21.5994 | 21.773 | 21.898 | 21.0834 | 21.1988 | 21.6172 | 20.4782 | 21.058 | 24.4279 | 21.8932 | 22.0638 | 27.9398 | 164.7406 | 143.8812 | 173.7666 | 22.1054 | 21.9924 | 25.9987 | 22.0278 | 22.1125 | 27.7345 | 72.4692 | 174.9647 |  | 108.6427 | 142.4474 | 139.4667 | 134.0987 |  | 17.592 | 18.5813 | 17.5634 | 18.5454 | 19.5257 | 32.101 | 124.0941 | 15.6967 | 17.1934 | 15.6529 | 18.7491 | 18.6663 | 46.1924 | 49.3082 | 45.3461 | 21.6637 |  |  | 0.72437 | -0.28657 | -28.1208 | 0.49542 | 0.30569 | -152.2514 | 18.6794 | 0.41296 | 0.1908 | 0.2032 | 0.47144 | 0.0003302 | 0.00034663 | 0.41243 | 21.8574 | 21.962 | 22.1609 | 22.2156 | 22.0273 | 21.3174 | 20.1335 | 22.1783 | 22.3596 | 22.3967 | 22.3364 | 21.9574 | 21.1838 | 22.2693 | 82.3689 | 52.4613 | 44.7234 | 35.011 | 31.8183 | 57.6226 | 37.1571 | 22.3226 | 22.0851 | 21.651 | 22.0526 | 21.7771 | 21.4946 | 21.9324 | 21.7415 | 24.6226 | 62.741 | 165.2319 | 130.6473 | 91.9867 | 1.055 | 0.30854 | 71.5915 | 21.8984 | 22.2265 | 20.6751 | 21.5747 | 22.0315 | 21.9623 | 22.4326 | 32.0664 | 21.8162 | 21.7732 | 25.7088 | 163.5198 | 205.5583 | 131.4302 | 133.1285 | 88.9572 |  | 62.9778 | 132.8581 | 68.9001 | 108.623 | 86.1959 | 76.6024 |  | 86.4111 |  |  | 24.5216 | 28.5723 | 65.2145 | [5 empty] | 21.8919 | 83.0131 | 21.6961 | 22.0974 | 35.1611 | 21.2787 | 21.9227 | 31.892 | 109.7867 | 212.6878 |  | 94.4563 | 156.7193 | 24.5327 | 86.237 | 171.4668 | 56.3511 | 127.9875 | 28.0008 | 127.1312 | 27.7623 | 124.7008 | 19.0153 | 95.2084 | 149.1048 | 33.8729 | 87.2352 | 175.6479 | 23.6421 | 86.7172 | 163.1314 | 24.5999 | 114.9552 | 36.0081 | 124.2615 | 28.6144 | 133.1809 | 1.505 | 18.9307 | 1.7842 | 0.067034 | -27.0011 | 3.0952 | 252.76 | 51.66 | 1.2539 | -0.6372 | -6.3121 | 0.83781 | 0.67319 | -15.0237 | 5.2623 | 0.0021212 | -1.0005 | 0.32246 | -2.0709 | -0.31499 | -0.90288 | -0.090647
42838.4257 | 466 | 22.8954 | 22.8562 | 22.8477 | 22.7667 | 22.3774 | 21.699 | 22.6911 | 21.7547 | 22.35 | 22.3462 | 22.3243 | 21.9721 | 21.1855 | 22.157 | 21.5976 | 21.7755 | 21.899 | 21.0832 | 21.1977 | 21.6205 | 20.4738 | 21.0575 | 24.4464 | 21.8918 | 22.069 | 27.9611 | 164.9437 | 144.2915 | 173.5878 | 22.1097 | 22.0042 | 26.0304 | 22.0267 | 22.1171 | 27.7689 | 72.6909 | 174.142 |  | 108.8876 | 142.6858 | 139.6794 | 134.244 |  | 17.5916 | 18.6005 | 17.5749 | 18.5705 | 19.5574 | 31.9828 | 124.5413 | 15.7058 | 17.2048 | 15.6856 | 18.7597 | 18.6714 | 46.1875 | 49.3059 | 45.3355 | 21.6652 |  |  | 0.80257 | -0.32796 | -27.7771 | 0.38963 | -0.021552 | -147.4616 | 19.4417 | 0.56147 | 0.031229 | 0.034518 | 0.42335 | 0.00035484 | 0.00033677 | 0.39283 | 21.8631 | 21.9636 | 22.163 | 22.2094 | 22.0254 | 21.3215 | 20.1373 | 22.1804 | 22.3611 | 22.3997 | 22.3482 | 21.9621 | 21.1864 | 22.278 | 81.6469 | 54.0062 | 46.0118 | 35.4908 | 31.8283 | 57.7285 | 37.166 | 22.322 | 22.0888 | 21.6526 | 22.0445 | 21.7751 | 21.4965 | 21.9351 | 21.7342 | 24.6388 | 62.9148 | 165.7388 | 131.1469 | 92.137 | 0.92482 | 0.53297 | 72.022 | 21.8981 | 22.2263 | 20.6847 | 21.5645 | 22.0218 | 21.9636 | 22.436 | 32.1084 | 21.809 | 21.7692 | 25.7252 | 163.6806 | 205.2829 | 131.8489 | 133.5072 | 88.4922 |  | 63.2154 | 132.6109 | 69.1143 | 109.4829 | 86.6428 | 77.279 |  | 86.7069 |  |  | 24.543 | 28.6019 | 66.0685 | [5 empty] | 21.8898 | 83.2563 | 21.701 | 22.0939 | 35.1208 | 21.2821 | 21.9201 | 31.9205 | 110.109 | 212.0007 |  | 94.4337 | 156.7878 | 24.5566 | 86.3723 | 171.7802 | 56.4919 | 128.2375 | 28.0358 | 127.6545 | 27.8088 | 125.0439 | 19.0406 | 95.2345 | 149.2318 | 33.9141 | 87.4025 | 175.6334 | 23.6584 | 87.0401 | 163.3086 | 24.6234 | 115.2844 | 36.0529 | 124.6139 | 28.6383 | 133.406 | 1.557 | 18.922 | 1.7936 | 0.068247 | -27.1939 | 3.0951 | 228.81 | 52.6 | 1.3196 | -0.68169 | -6.2736 | 0.74301 | -0.17871 | -14.7826 | 5.3676 | 0.023684 | -0.9857 | 0.3157 | -1.978 | -0.45709 | -0.89868 | -0.088501
42838.4257 | 467 | 22.9002 | 22.8601 | 22.8401 | 22.7676 | 22.3772 | 21.7028 | 22.6957 | 21.7548 | 22.3482 | 22.3519 | 22.3253 | 21.9783 | 21.1878 | 22.1617 | 21.599 | 21.7776 | 21.9041 | 21.0839 | 21.199 | 21.6262 | 20.4743 | 21.0649 | 24.4762 | 21.8955 | 22.0798 | 27.9925 | 165.2598 | 144.5879 | 173.4099 | 22.0976 | 21.994 | 26.0424 | 22.0237 | 22.1063 | 27.7957 | 72.9092 | 173.5937 |  | 109.1213 | 142.8165 | 139.9263 | 134.9934 |  | 17.5817 | 18.6047 | 17.5946 | 18.5852 | 19.5713 | 31.9671 | 124.9754 | 15.7111 | 17.2038 | 15.7255 | 18.7645 | 18.6732 | 46.1882 | 49.305 | 45.3236 | 21.6644 |  |  | 0.55024 | -0.43311 | -27.6154 | 0.60516 | 0.017216 | -147.7777 | 19.0133 | 0.39982 | -0.02968 | 0.056757 | 0.3251 | 0.0003532 | 0.00035649 | 0.38534 | 21.8572 | 21.956 | 22.1621 | 22.2072 | 22.0241 | 21.3069 | 20.1235 | 22.1825 | 22.3514 | 22.3887 | 22.3412 | 21.9534 | 21.1816 | 22.2709 | 82.2558 | 55.5158 | 48.4355 | 36.3964 | 31.8394 | 57.8585 | 37.2136 | 22.3318 | 22.0927 | 21.6535 | 22.0546 | 21.7778 | 21.505 | 21.9451 | 21.7413 | 24.6746 | 63.1067 | 166.4513 | 131.7564 | 92.5577 | 1.2215 | 0.37244 | 71.9545 | 21.8991 | 22.2248 | 20.6925 | 21.5749 | 22.0282 | 21.9633 | 22.4437 | 32.1616 | 21.8199 | 21.7811 | 25.7572 | 163.9968 | 205.4514 | 132.2474 | 133.8742 | 90.5132 |  | 63.4265 | 132.9483 | 69.2968 | 108.5106 | 86.9313 | 77.0017 |  | 86.9336 |  |  | 24.5738 | 28.6263 | 66.4612 | [5 empty] | 21.8959 | 82.871 | 21.705 | 22.1028 | 35.1209 | 21.2859 | 21.9296 | 31.9577 | 110.4349 | 211.4486 |  | 94.4207 | 156.769 | 24.5927 | 86.465 | 171.9506 | 56.567 | 128.452 | 28.0581 | 127.8846 | 27.8407 | 125.3186 | 19.0513 | 95.2416 | 149.4733 | 33.9712 | 87.5557 | 175.5377 | 23.6528 | 87.4802 | 163.5817 | 24.6577 | 115.4716 | 36.1313 | 125.0775 | 28.6578 | 133.7734 | 1.2364 | 18.9138 | 1.8029 | 0.06845 | -27.2518 | 3.0951 | 239.06 | 52.04 | 1.0924 | -0.78338 | -6.2554 | 0.926 | 0.15972 | -14.7981 | 5.308 | -0.024767 | -0.98834 | 0.35378 | -2.0301 | -0.72078 | -0.91139 | -0.093202
42838.4257 | 468 | 22.9026 | 22.8644 | 22.8397 | 22.7637 | 22.376 | 21.7051 | 22.6992 | 21.7566 | 22.3508 | 22.3527 | 22.3267 | 21.9738 | 21.1869 | 22.1631 | 21.6011 | 21.7794 | 21.9003 | 21.0796 | 21.1998 | 21.622 | 20.478 | 21.0737 | 24.4993 | 21.8972 | 22.0881 | 28.0284 | 165.6249 | 144.7424 | 173.8789 | 22.0996 | 22.0005 | 26.0664 | 22.0238 | 22.1135 | 27.8329 | 73.1368 | 172.3803 |  | 109.3505 | 142.9034 | 140.18 | 134.4512 |  | 17.5822 | 18.6174 | 17.6141 | 18.606 | 19.5518 | 32.2919 | 125.186 | 15.6806 | 17.2069 | 15.7194 | 18.7736 | 18.6754 | 46.1912 | 49.3049 | 45.3188 | 21.6673 |  |  | 0.51081 | -0.34768 | -27.7252 | 0.32589 | 0.1309 | -152.093 | 18.8148 | 0.60418 | -0.072687 | 0.031162 | 0.33534 | 0.00035977 | 0.0003532 | 0.39732 | 21.8575 | 21.9642 | 22.1659 | 22.2169 | 22.0272 | 21.323 | 20.1377 | 22.184 | 22.357 | 22.3946 | 22.3389 | 21.9585 | 21.1881 | 22.2715 | 82.8498 | 53.4374 | 48.1621 | 36.45 | 31.8568 | 57.9688 | 37.2394 | 22.3237 | 22.083 | 21.6507 | 22.0424 | 21.7755 | 21.5017 | 21.9327 | 21.739 | 24.68 | 63.2806 | 167.5091 | 132.4042 | 93.1526 | 1.2337 | 0.14629 | 71.8844 | 21.8954 | 22.2219 | 20.6945 | 21.5729 | 22.0236 | 21.9644 | 22.446 | 32.2137 | 21.8067 | 21.7839 | 25.7829 | 164.189 | 205.2908 | 132.5798 | 134.1509 | 91.6015 |  | 63.6293 | 133.4715 | 69.5108 | 108.5239 | 87.2866 | 76.7064 |  | 87.1199 |  |  | 24.5924 | 28.6352 | 66.4531 | [5 empty] | 21.8936 | 82.7017 | 21.6979 | 22.1054 | 35.1668 | 21.2848 | 21.9206 | 31.9921 | 110.6881 | 211.5015 |  | 94.4 | 156.768 | 24.6252 | 86.5576 | 171.9618 | 56.6732 | 128.6609 | 28.0885 | 128.011 | 27.8887 | 125.5929 | 19.0516 | 95.2339 | 149.6328 | 34.0185 | 87.7672 | 175.4936 | 23.6565 | 88.1157 | 163.7402 | 24.6882 | 115.5084 | 36.2025 | 125.4785 | 28.683 | 134.1765 | 1.39 | 18.9066 | 1.8123 | 0.068581 | -27.1343 | 3.0951 | 248.06 | 52.78 | 1.0531 | -0.7019 | -6.2679 | 0.67954 | 0.44065 | -15.0206 | 5.283 | -0.047608 | -0.99498 | 0.36704 | -2.083 | -0.68736 | -0.88786 | -0.1034
42838.4257 | 469 | 22.8993 | 22.8589 | 22.8408 | 22.7645 | 22.3746 | 21.7006 | 22.6978 | 21.7552 | 22.3513 | 22.3533 | 22.3248 | 21.9748 | 21.1901 | 22.1661 | 21.602 | 21.7786 | 21.9043 | 21.0839 | 21.2025 | 21.6233 | 20.4864 | 21.079 | 24.5161 | 21.9 | 22.0894 | 28.0629 | 166.1351 | 144.9167 | 174.8727 | 22.1002 | 22.0064 | 26.0938 | 22.0228 | 22.1208 | 27.8655 | 73.3577 | 171.3067 |  | 109.5627 | 143.0762 | 140.4055 | 133.3748 |  | 17.5772 | 18.6285 | 17.6052 | 18.6424 | 19.5439 | 32.0826 | 125.385 | 15.6472 | 17.2053 | 15.7846 | 18.7821 | 18.6747 | 46.2034 | 49.2979 | 45.3188 | 21.6622 |  |  | 0.71517 | -0.33848 | -27.8796 | 0.39554 | -0.005784 | -148.6543 | 18.5684 | 0.70932 | -0.018783 | 0.23089 | 0.45599 | 0.0003417 | 0.00036963 | 0.42592 | 21.8564 | 21.9644 | 22.1594 | 22.209 | 22.0251 | 21.3093 | 20.1323 | 22.1853 | 22.3568 | 22.3961 | 22.3422 | 21.9596 | 21.1829 | 22.2648 | 81.9776 | 53.2203 | 48.3267 | 36.0623 | 31.913 | 58.0625 | 37.2651 | 22.3218 | 22.0832 | 21.6498 | 22.0544 | 21.7764 | 21.4931 | 21.9402 | 21.7442 | 24.7062 | 63.4744 | 168.2943 | 132.7319 | 94.261 | 1.2014 | 0.17064 | 71.853 | 21.9024 | 22.2296 | 20.7044 | 21.5602 | 22.0297 | 21.9713 | 22.4572 | 32.2705 | 21.8178 | 21.7837 | 25.8113 | 164.1959 | 205.3623 | 132.9959 | 134.4635 | 90.6422 |  | 63.8718 | 133.4501 | 69.7571 | 108.1415 | 87.6556 | 76.7258 |  | 87.3183 |  |  | 24.6272 | 28.6597 | 65.8196 | [5 empty] | 21.8958 | 82.9016 | 21.7016 | 22.1016 | 35.2034 | 21.2813 | 21.9199 | 32.0195 | 110.877 | 212.2327 |  | 94.3941 | 157.0785 | 24.6559 | 86.6894 | 172.1421 | 56.7647 | 129.0455 | 28.1213 | 128.4312 | 27.9214 | 125.9025 | 19.0578 | 95.219 | 149.7753 | 34.0638 | 87.9713 | 175.5517 | 23.6666 | 88.5694 | 163.7428 | 24.7277 | 115.7016 | 36.2723 | 125.5836 | 28.7288 | 134.393 | 1.1214 | 18.8949 | 1.8209 | 0.069169 | -27.1287 | 3.0951 | 253.02 | 51.59 | 1.2474 | -0.69257 | -6.2855 | 0.74867 | -0.092597 | -14.8447 | 5.2465 | -0.012123 | -0.9853 | 0.39184 | -1.9749 | -0.70263 | -0.84974 | -0.12713
42838.4257 | 470 | 22.8977 | 22.8647 | 22.8479 | 22.7776 | 22.3723 | 21.7022 | 22.6996 | 21.7635 | 22.3478 | 22.3575 | 22.3323 | 21.9875 | 21.1956 | 22.1708 | 21.6037 | 21.7796 | 21.9037 | 21.0809 | 21.2021 | 21.6276 | 20.4861 | 21.0764 | 24.538 | 21.9033 | 22.0855 | 28.092 | 166.5734 | 145.1759 | 175.267 | 22.118 | 22.0143 | 26.1319 | 22.031 | 22.1367 | 27.9069 | 73.574 | 170.6762 |  | 109.7748 | 143.3521 | 140.5429 | 132.1489 |  | 17.5783 | 18.627 | 17.5984 | 18.6468 | 19.5289 | 31.7957 | 125.3039 | 15.5969 | 17.2082 | 15.8689 | 18.7815 | 18.666 | 46.212 | 49.2934 | 45.3008 | 21.6591 |  |  | 0.63303 | -0.61513 | -27.9729 | 0.43234 | 0.040216 | -148.2311 | 18.5658 | 0.77635 | 0.013326 | 0.19774 | 0.55598 | 0.00036963 | 0.00036141 | 0.43947 | 21.8576 | 21.9587 | 22.1559 | 22.2202 | 22.0351 | 21.3175 | 20.1319 | 22.1771 | 22.356 | 22.3977 | 22.3488 | 21.9642 | 21.1773 | 22.2697 | 81.9347 | 53.0831 | 49.0486 | 36.3624 | 31.9149 | 58.1571 | 37.2853 | 22.3259 | 22.0931 | 21.6455 | 22.0434 | 21.7794 | 21.497 | 21.9398 | 21.7431 | 24.7288 | 63.6843 | 168.6377 | 133.0963 | 94.8269 | 1.4053 | 1.1665 | 71.8446 | 21.902 | 22.2204 | 20.7114 | 21.5743 | 22.0262 | 21.9653 | 22.4648 | 32.3215 | 21.823 | 21.7842 | 25.8303 | 164.5448 | 205.3723 | 133.3994 | 134.7906 | 89.1104 |  | 64.0728 | 134.0767 | 69.9779 | 107.8717 | 87.971 | 76.6118 |  | 87.5315 |  |  | 24.6519 | 28.6913 | 65.5227 | [5 empty] | 21.8979 | 82.8159 | 21.7033 | 22.0955 | 35.2238 | 21.2789 | 21.9163 | 32.0421 | 111.0422 | 212.4765 |  | 94.6187 | 157.4744 | 24.6916 | 86.8569 | 172.2055 | 56.8771 | 129.3371 | 28.1453 | 128.9825 | 27.9408 | 126.1957 | 19.0463 | 95.2968 | 149.8271 | 34.0868 | 88.167 | 175.6598 | 23.6564 | 88.8822 | 163.7767 | 24.7534 | 115.9645 | 36.3348 | 125.7895 | 28.7617 | 134.3869 | 1.7809 | 18.8939 | 1.8301 | 0.069597 | -27.3052 | 3.0952 | 238.86 | 51.79 | 1.1741 | -0.93363 | -6.296 | 0.78272 | 0.24405 | -14.8166 | 5.2437 | 0.037761 | -0.99455 | 0.41146 | -1.9588 | -0.78046 | -0.80764 | -0.1352
42838.4257 | 471 | 22.8946 | 22.8594 | 22.8482 | 22.7682 | 22.3727 | 21.6979 | 22.7016 | 21.7604 | 22.3473 | 22.3526 | 22.3171 | 21.9805 | 21.19 | 22.1619 | 21.6006 | 21.7741 | 21.8955 | 21.0768 | 21.2002 | 21.6226 | 20.4748 | 21.0728 | 24.5579 | 21.8912 | 22.0839 | 28.121 | 166.8704 | 145.4238 | 175.5658 | 22.1102 | 22.0175 | 26.1553 | 22.0314 | 22.135 | 27.9375 | 73.7803 | 169.5432 |  | 109.9872 | 143.5684 | 140.7235 | 130.9373 |  | 17.5789 | 18.6264 | 17.5797 | 18.6305 | 19.5029 | 31.6239 | 125.1158 | 15.5624 | 17.2118 | 15.8683 | 18.7981 | 18.6759 | 46.2167 | 49.2852 | 45.2954 | 21.6554 |  |  | 0.7684 | -0.54218 | -28.1431 | 0.39751 | 0.14404 | -152.1666 | 18.0854 | 0.46685 | 0.12795 | 0.29446 | 0.32215 | 0.00035649 | 0.00033513 | 0.42592 | 21.8617 | 21.9555 | 22.154 | 22.2195 | 22.0286 | 21.314 | 20.1284 | 22.1782 | 22.3524 | 22.3955 | 22.349 | 21.9551 | 21.1761 | 22.2703 | 82.9258 | 53.4453 | 52.1341 | 37.5886 | 32.5418 | 58.29 | 37.3561 | 22.3203 | 22.0802 | 21.6474 | 22.0485 | 21.7716 | 21.5016 | 21.9407 | 21.7489 | 24.7434 | 63.8826 | 168.9985 | 133.2411 | 95.2918 | 1.2162 | 0.019622 | 72.0814 | 21.9059 | 22.2239 | 20.7083 | 21.5716 | 22.0218 | 21.9581 | 22.4715 | 32.3707 | 21.8131 | 21.7908 | 25.8514 | 164.6266 | 205.4238 | 133.7218 | 135.0376 | 88.7327 |  | 64.2761 | 134.8268 | 70.1779 | 107.6232 | 88.2879 | 77.3065 |  | 87.7584 |  |  | 24.654 | 28.7348 | 65.2533 | [5 empty] | 21.8951 | 82.5772 | 21.7058 | 22.09 | 35.2465 | 21.2851 | 21.9194 | 32.0833 | 111.2018 | 212.3131 |  | 95.0076 | 157.7777 | 24.7151 | 87.0599 | 172.0492 | 56.9882 | 129.5297 | 28.1772 | 129.1395 | 27.972 | 126.4951 | 19.0161 | 95.4891 | 149.9797 | 34.1143 | 88.4072 | 176.009 | 23.6653 | 89.2451 | 164.0106 | 24.7734 | 116.1364 | 36.3843 | 126.0593 | 28.8117 | 134.3991 | 1.3171 | 18.8824 | 1.8391 | 0.070171 | -27.1303 | 3.0952 | 248.2 | 52.68 | 1.294 | -0.87653 | -6.3151 | 0.75053 | 0.46174 | -15.0077 | 5.1739 | 0.055667 | -1.008 | 0.43056 | -2.0531 | -1.1149 | -0.7663 | -0.14088
42838.4257 | 472 | 22.9025 | 22.8705 | 22.845 | 22.7681 | 22.3775 | 21.7017 | 22.6999 | 21.7634 | 22.3557 | 22.3539 | 22.3315 | 21.9773 | 21.2015 | 22.1627 | 21.5923 | 21.7768 | 21.9015 | 21.077 | 21.1922 | 21.6253 | 20.4787 | 21.0799 | 24.5811 | 21.8924 | 22.0884 | 28.1516 | 167.1684 | 145.7553 | 174.8924 | 22.1105 | 22.0155 | 26.1803 | 22.0293 | 22.133 | 27.9724 | 74.0195 | 169.6297 |  | 110.2208 | 143.8497 | 140.8803 | 131.0166 |  | 17.577 | 18.6358 | 17.5669 | 18.6086 | 19.4781 | 31.9288 | 125.5628 | 15.6456 | 17.2206 | 15.8882 | 18.7958 | 18.6876 | 46.2285 | 49.2831 | 45.2779 | 21.6624 |  |  | 0.69349 | -0.54941 | -27.9532 | 0.21221 | 0.055988 | -151.2184 | 18.5388 | 0.42414 | 0.094669 | 0.061583 | 0.40339 | 0.00035649 | 0.00032856 | 0.42812 | 21.8669 | 21.9633 | 22.1603 | 22.2213 | 22.0261 | 21.3171 | 20.1368 | 22.1799 | 22.3595 | 22.3995 | 22.3464 | 21.9569 | 21.1889 | 22.2667 | 82.7632 | 50.8385 | 50.3732 | 37.1294 | 32.9669 | 58.3897 | 37.3862 | 22.3194 | 22.0828 | 21.6524 | 22.0452 | 21.7725 | 21.506 | 21.9415 | 21.7477 | 24.7675 | 64.0859 | 169.4 | 133.4644 | 95.6262 | 1.169 | 0.45765 | 72.3282 | 21.8915 | 22.2211 | 20.7094 | 21.574 | 22.0208 | 21.9617 | 22.4698 | 32.4274 | 21.8131 | 21.789 | 25.8813 | 164.681 | 205.2588 | 133.9429 | 135.223 | 88.602 |  | 64.484 | 135.4108 | 70.4208 | 107.6622 | 88.6423 | 77.3171 |  | 87.9823 |  |  | 24.6553 | 28.7695 | 65.2339 | [5 empty] | 21.9035 | 82.5841 | 21.7067 | 22.0976 | 35.2589 | 21.2956 | 21.9259 | 32.1327 | 111.4021 | 212.7543 |  | 95.2533 | 158.077 | 24.7456 | 87.1501 | 172.1185 | 57.0805 | 129.766 | 28.2171 | 129.1897 | 28.0185 | 126.7672 | 19.0219 | 95.5702 | 150.0777 | 34.1373 | 88.6376 | 176.3409 | 23.7037 | 89.5778 | 164.2021 | 24.806 | 116.341 | 36.4115 | 126.3718 | 28.8511 | 134.5598 | 1.1893 | 18.8719 | 1.8472 | 0.069169 | -27.3072 | 3.0952 | 250.4 | 51.4 | 1.2284 | -0.88237 | -6.2938 | 0.54838 | 0.28802 | -14.9684 | 5.241 | 0.066884 | -1.0152 | 0.44312 | -2.0231 | -0.91574 | -0.75959 | -0.14276
42838.4258 | 473 | 22.9016 | 22.8622 | 22.8417 | 22.7647 | 22.3794 | 21.6961 | 22.6953 | 21.7619 | 22.3491 | 22.3463 | 22.3255 | 21.9785 | 21.1955 | 22.1585 | 21.6038 | 21.7814 | 21.9022 | 21.0781 | 21.2029 | 21.628 | 20.4828 | 21.0785 | 24.6065 | 21.8983 | 22.0925 | 28.1845 | 167.4166 | 146.0637 | 174.5021 | 22.1155 | 22.0204 | 26.204 | 22.0315 | 22.1358 | 28.008 | 74.2001 | 170.1748 |  | 110.4159 | 144.1171 | 141.0034 | 130.4319 |  | 17.5807 | 18.6445 | 17.5625 | 18.5966 | 19.4628 | 32.1237 | 125.7973 | 15.7777 | 17.2192 | 15.8709 | 18.81 | 18.698 | 46.2317 | 49.2755 | 45.2773 | 21.6613 |  |  | 0.77957 | -0.28723 | -28.126 | 0.30354 | 0.03496 | -147.4242 | 18.3108 | 0.4859 | 0.2665 | 0.036616 | 0.34506 | 0.00037784 | 0.00035649 | 0.40646 | 21.8693 | 21.9635 | 22.1587 | 22.2158 | 22.025 | 21.3166 | 20.1306 | 22.1795 | 22.354 | 22.4041 | 22.3451 | 21.96 | 21.1837 | 22.2724 | 82.8183 | 50.1287 | 47.757 | 36.4545 | 32.2477 | 58.4978 | 37.3942 | 22.3248 | 22.0803 | 21.6533 | 22.0478 | 21.7781 | 21.5153 | 21.9383 | 21.749 | 24.7951 | 64.2842 | 169.866 | 133.7246 | 95.9992 | 1.101 | 0.43331 | 72.1635 | 21.8988 | 22.2236 | 20.7197 | 21.5682 | 22.0212 | 21.966 | 22.4767 | 32.475 | 21.8119 | 21.7928 | 25.9094 | 164.7698 | 205.0074 | 134.1304 | 135.4504 | 87.7628 |  | 64.6822 | 136.1135 | 70.6816 | 108.2361 | 89.0351 | 77.1182 |  | 88.2012 |  |  | 24.6724 | 28.7847 | 65.1884 | [5 empty] | 21.9021 | 83.0874 | 21.7036 | 22.1001 | 35.2842 | 21.2818 | 21.9193 | 32.1779 | 111.6476 | 212.752 |  | 95.4553 | 158.202 | 24.7811 | 87.3722 | 172.1075 | 57.1156 | 129.9596 | 28.2759 | 129.3985 | 28.0575 | 126.9859 | 19.005 | 95.6905 | 150.0521 | 34.151 | 88.8432 | 176.6209 | 23.7105 | 89.8043 | 164.4953 | 24.8141 | 116.5687 | 36.4509 | 126.7492 | 28.8832 | 134.8287 | 1.6421 | 18.8626 | 1.8552 | 0.0689 | -27.23 | 3.0951 | 260.59 | 52.92 | 1.3019 | -0.63799 | -6.3133 | 0.65587 | 0.22767 | -14.7841 | 5.2103 | 0.097433 | -1.0251 | 0.44231 | -2.0163 | -0.62409 | -0.73662 | -0.14588
42838.4258 | 474 | 22.8932 | 22.8574 | 22.8449 | 22.768 | 22.379 | 21.705 | 22.6962 | 21.7573 | 22.3551 | 22.3486 | 22.3245 | 21.9806 | 21.1915 | 22.1667 | 21.5914 | 21.7677 | 21.9032 | 21.0688 | 21.1846 | 21.6251 | 20.472 | 21.0832 | 24.6232 | 21.8897 | 22.1014 | 28.2016 | 167.7767 | 146.2705 | 174.4941 | 22.1094 | 22.015 | 26.2195 | 22.0243 | 22.1321 | 28.0422 | 74.3899 | 171.0057 |  | 110.6464 | 144.3536 | 141.1728 | 129.5253 |  | 17.5746 | 18.6402 | 17.5596 | 18.5824 | 19.4497 | 31.8859 | 125.7547 | 15.9189 | 17.2175 | 15.7677 | 18.798 | 18.6982 | 46.2251 | 49.2666 | 45.2687 | 21.6551 |  |  | 0.65866 | -0.5021 | -28.3146 | 0.38831 | 0.0573 | -148.4979 | 17.7503 | 0.59958 | 0.16453 | 0.059485 | 0.29194 | 0.00039427 | 0.00035484 | 0.37583 | 21.8604 | 21.9625 | 22.1627 | 22.21 | 22.0215 | 21.3162 | 20.1278 | 22.1755 | 22.3553 | 22.3909 | 22.3386 | 21.9609 | 21.1795 | 22.274 | 84.231 | 52.9809 | 47.0616 | 35.4509 | 31.6657 | 58.6233 | 37.4187 | 22.3172 | 22.085 | 21.6453 | 22.0487 | 21.7777 | 21.5009 | 21.9308 | 21.7436 | 24.8075 | 64.4707 | 170.5394 | 134.0534 | 96.4187 | 0.76793 | 0.48409 | 72.3592 | 21.9017 | 22.2262 | 20.7227 | 21.5657 | 22.0209 | 21.9685 | 22.4859 | 32.5305 | 21.8159 | 21.7929 | 25.9287 | 164.7969 | 205.022 | 134.3331 | 135.6929 | 88.0583 |  | 64.8962 | 135.1133 | 70.8933 | 106.9094 | 89.3043 | 77.4085 |  | 88.4158 |  |  | 24.6844 | 28.806 | 66.6488 | [5 empty] | 21.8942 | 83.2063 | 21.6902 | 22.0915 | 35.3414 | 21.2905 | 21.9212 | 32.1964 | 111.9248 | 212.6421 |  | 95.6256 | 158.5686 | 24.8017 | 87.5659 | 171.9484 | 57.2451 | 130.1223 | 28.3091 | 129.6473 | 28.1091 | 127.1435 | 18.9746 | 96.0971 | 150.2263 | 34.1545 | 89.1226 | 176.7524 | 23.7131 | 90.0104 | 164.8086 | 24.7745 | 116.8383 | 36.4803 | 127.13 | 28.9334 | 135.1077 | 2.1376 | 18.8514 | 1.8634 | 0.068719 | -27.3007 | 3.0952 | 243.92 | 51.61 | 1.1966 | -0.84352 | -6.3344 | 0.74181 | 0.29135 | -14.8321 | 5.128 | 0.097043 | -0.9895 | 0.48955 | -2.1583 | -0.54395 | -0.70436 | -0.15073
42838.4258 | 475 | 22.8957 | 22.867 | 22.8467 | 22.768 | 22.3767 | 21.701 | 22.6979 | 21.758 | 22.356 | 22.3496 | 22.3213 | 21.9803 | 21.1946 | 22.1685 | 21.5918 | 21.7654 | 21.8988 | 21.0756 | 21.1963 | 21.6385 | 20.4699 | 21.0875 | 24.6396 | 21.9014 | 22.1072 | 28.2525 | 168.1002 | 146.4836 | 174.8681 | 22.1117 | 22.0221 | 26.2439 | 22.0238 | 22.1339 | 28.0794 | 74.6013 | 173.1687 |  | 110.922 | 144.5428 | 141.3239 | 129.8495 |  | 17.5927 | 18.652 | 17.5767 | 18.5922 | 19.4641 | 31.8066 | 125.9622 | 15.9897 | 17.2157 | 15.7052 | 18.8135 | 18.7006 | 46.2239 | 49.2631 | 45.2552 | 21.6609 |  |  | 0.51147 | -0.46925 | -28.7181 | 0.39488 | 0.28466 | -147.3197 | 18.0447 | 0.53059 | 0.048549 | -0.090522 | 0.28621 | 0.0003762 | 0.0003417 | 0.4057 | 21.8737 | 21.9708 | 22.1708 | 22.2152 | 22.0328 | 21.3285 | 20.1411 | 22.1825 | 22.3546 | 22.4026 | 22.3573 | 21.961 | 21.1852 | 22.2741 | 83.2067 | 53.6116 | 47.4402 | 35.744 | 30.7871 | 58.7072 | 37.4527 | 22.3138 | 22.089 | 21.6483 | 22.0457 | 21.7803 | 21.5126 | 21.937 | 21.7481 | 24.8317 | 64.6676 | 171.0261 | 134.4399 | 96.3643 | 1.193 | 0.31424 | 72.439 | 21.8928 | 22.2199 | 20.7251 | 21.5633 | 22.0183 | 21.9705 | 22.4897 | 32.5815 | 21.807 | 21.7981 | 25.9582 | 164.9006 | 205.196 | 134.7088 | 136.0288 | 89.9507 |  | 65.1414 | 133.5905 | 71.1279 | 106.4892 | 89.5807 | 78.0297 |  | 88.6531 |  |  | 24.7097 | 28.8499 | 67.076 | [5 empty] | 21.9055 | 82.119 | 21.6996 | 22.0918 | 35.4348 | 21.2786 | 21.9124 | 32.2161 | 112.2078 | 212.8102 |  | 95.7242 | 158.805 | 24.831 | 87.8526 | 172.4383 | 57.3473 | 130.2929 | 28.3775 | 129.9253 | 28.172 | 127.3003 | 18.9564 | 96.3849 | 150.4033 | 34.183 | 89.3943 | 177.0938 | 23.7191 | 90.2475 | 165.0688 | 24.7469 | 117.124 | 36.5279 | 127.2195 | 28.971 | 135.3619 | 1.6219 | 18.8408 | 1.8733 | 0.069256 | -27.0192 | 3.0952 | 246.9 | 52.25 | 1.0549 | -0.81548 | -6.3795 | 0.74807 | 0.64931 | -14.7712 | 5.1696 | 0.053439 | -0.93851 | 0.51189 | -2.0345 | -0.582 | -0.70548 | -0.14203
42838.4258 | 476 | 22.8854 | 22.8639 | 22.846 | 22.7604 | 22.3718 | 21.6967 | 22.695 | 21.7551 | 22.3474 | 22.3461 | 22.3123 | 21.9788 | 21.1928 | 22.1636 | 21.6021 | 21.7794 | 21.9091 | 21.0739 | 21.2003 | 21.6286 | 20.4773 | 21.1001 | 24.6694 | 21.9011 | 22.1049 | 28.2785 | 168.1381 | 146.666 | 173.7217 | 22.1058 | 22.017 | 26.2692 | 22.019 | 22.1426 | 28.1089 | 74.8236 | 174.7635 |  | 111.181 | 144.623 | 141.5057 | 129.652 |  | 17.588 | 18.6614 | 17.5949 | 18.611 | 19.4767 | 31.7995 | 126.5717 | 15.9584 | 17.2171 | 15.651 | 18.8198 | 18.6971 | 46.2164 | 49.2589 | 45.2466 | 21.654 |  |  | 0.58178 | -0.33651 | -28.8521 | 0.54011 | 0.20121 | -149.0295 | 18.157 | 0.74218 | 0.13262 | 0.22607 | 0.44575 | 0.00034499 | 0.00035484 | 0.36458 | 21.8611 | 21.9542 | 22.1502 | 22.2098 | 22.021 | 21.3133 | 20.1269 | 22.1737 | 22.3567 | 22.3967 | 22.3399 | 21.9485 | 21.1841 | 22.2717 | 83.599 | 54.9244 | 48.9984 | 35.0697 | 30.1475 | 58.8201 | 37.4921 | 22.3199 | 22.0873 | 21.6512 | 22.0474 | 21.7844 | 21.5214 | 21.9451 | 21.756 | 24.8605 | 64.8504 | 171.5537 | 134.7015 | 95.7879 | 1.5907 | 1.1627 | 72.4884 | 21.8927 | 22.2175 | 20.719 | 21.5644 | 22.0173 | 21.9701 | 22.4938 | 32.6304 | 21.8097 | 21.8017 | 25.9778 | 165.0744 | 205.0886 | 134.9827 | 136.2531 | 90.8403 |  | 65.3821 | 134.1175 | 71.4593 | 107.2878 | 89.9947 | 78.5825 |  | 88.8859 |  |  | 24.7173 | 28.9037 | 66.9411 | [5 empty] | 21.8892 | 81.7208 | 21.6962 | 22.0942 | 35.506 | 21.2765 | 21.9224 | 32.2317 | 112.4628 | 213.8146 |  | 96.0861 | 158.6458 | 24.8695 | 88.1583 | 172.8923 | 57.4384 | 130.7394 | 28.4267 | 130.3175 | 28.2254 | 127.5128 | 18.9581 | 96.4791 | 150.4647 | 34.2438 | 89.595 | 177.6498 | 23.7079 | 90.3516 | 165.2467 | 24.7518 | 117.329 | 36.5628 | 127.4265 | 29.031 | 135.6061 | 1.1587 | 18.8323 | 1.8833 | 0.071049 | -27.0151 | 3.0952 | 264.89 | 52.46 | 1.1237 | -0.69058 | -6.3945 | 0.8749 | 0.54589 | -14.8565 | 5.1857 | 0.03753 | -0.94087 | 0.5057 | -2.0646 | -0.75049 | -0.69169 | -0.11934
42838.4258 | 477 | 22.898 | 22.8589 | 22.8459 | 22.7645 | 22.3761 | 21.6998 | 22.6923 | 21.7628 | 22.342 | 22.3437 | 22.3174 | 21.9724 | 21.1908 | 22.1607 | 21.6079 | 21.7795 | 21.9093 | 21.0832 | 21.2002 | 21.6356 | 20.4829 | 21.0975 | 24.6957 | 21.8936 | 22.111 | 28.3116 | 168.3274 | 146.8297 | 175.4095 | 22.1049 | 22.0235 | 26.2961 | 22.0274 | 22.1492 | 28.1394 | 75.0489 | 175.7999 |  | 111.4122 | 144.7877 | 141.6594 | 129.8672 |  | 17.6013 | 18.672 | 17.6063 | 18.6273 | 19.4987 | 31.7671 | 126.8432 | 15.8896 | 17.2282 | 15.6417 | 18.827 | 18.7021 | 46.2282 | 49.2567 | 45.2451 | 21.6604 |  |  | 0.65997 | -0.41668 | -29.0171 | 0.25295 | 0.2886 | -148.0379 | 18.1091 | 0.46028 | -0.03474 | 0.18935 | 0.31538 | 0.00035977 | 0.00034992 | 0.28843 | 21.8719 | 21.9683 | 22.1575 | 22.218 | 22.024 | 21.3201 | 20.1375 | 22.186 | 22.3633 | 22.4056 | 22.3504 | 21.958 | 21.1906 | 22.2706 | 85.5216 | 56.959 | 55.604 | 37.42 | 30.9207 | 58.959 | 37.6031 | 22.3213 | 22.0842 | 21.6556 | 22.0551 | 21.7836 | 21.5189 | 21.9435 | 21.7569 | 24.8842 | 65.031 | 171.7254 | 135.1361 | 95.3474 | 1.6892 | 0.96035 | 72.8525 | 21.8904 | 22.2173 | 20.7219 | 21.5582 | 22.0196 | 21.9706 | 22.499 | 32.6811 | 21.8117 | 21.8009 | 26.0046 | 165.4175 | 205.1116 | 135.2003 | 136.4528 | 91.1258 |  | 65.5565 | 134.8347 | 71.7498 | 106.969 | 90.2136 | 79.0799 |  | 89.0889 |  |  | 24.7184 | 28.9431 | 66.6635 | [5 empty] | 21.8971 | 80.6222 | 21.7067 | 22.0976 | 35.5291 | 21.2823 | 21.9241 | 32.2557 | 112.6595 | 214.2059 |  | 96.4595 | 158.6838 | 24.9123 | 88.4254 | 172.7711 | 57.5393 | 131.032 | 28.466 | 130.4657 | 28.263 | 127.8187 | 18.9397 | 96.5648 | 150.5375 | 34.2862 | 89.7772 | 178.1198 | 23.6866 | 90.3227 | 165.6981 | 24.7474 | 117.5124 | 36.6342 | 127.4919 | 29.0814 | 135.9402 | 1.754 | 18.8239 | 1.8905 | 0.072109 | -27.2052 | 3.0952 | 244.31 | 51.67 | 1.1991 | -0.76847 | -6.4129 | 0.59874 | 0.65375 | -14.8062 | 5.1785 | 0.035978 | -0.95002 | 0.52301 | -2.2616 | -1.4714 | -0.68926 | -0.1005
42838.4258 | 478 | 22.8865 | 22.86 | 22.839 | 22.7627 | 22.3739 | 21.6931 | 22.6955 | 21.7574 | 22.344 | 22.3485 | 22.3198 | 21.9759 | 21.1856 | 22.1681 | 21.5922 | 21.7687 | 21.8928 | 21.0672 | 21.191 | 21.6389 | 20.4747 | 21.0973 | 24.7088 | 21.8863 | 22.111 | 28.3278 | 168.5587 | 147.0636 | 176.8866 | 22.1106 | 22.0189 | 26.3259 | 22.0215 | 22.1518 | 28.184 | 75.258 | 175.4739 |  | 111.6691 | 145.0548 | 141.8496 | 129.8549 |  | 17.6105 | 18.6837 | 17.6035 | 18.6366 | 19.5033 | 31.6913 | 126.7022 | 15.8358 | 17.2282 | 15.6902 | 18.8294 | 18.7063 | 46.236 | 49.2539 | 45.2483 | 21.6612 |  |  | 0.65735 | -0.60592 | -29.2963 | 0.63341 | 0.1769 | -150.1788 | 18.1261 | 0.51219 | 0.20306 | 0.24327 | 0.61102 | 0.00035813 | 0.00033513 | 0.25623 | 21.8673 | 21.9617 | 22.1597 | 22.2055 | 22.0219 | 21.3149 | 20.1281 | 22.1773 | 22.3558 | 22.3983 | 22.3435 | 21.9523 | 21.1902 | 22.2676 | 85.9613 | 56.983 | 58.0499 | 39.7396 | 33.3875 | 59.0851 | 37.7013 | 22.322 | 22.0838 | 21.654 | 22.0528 | 21.7798 | 21.5218 | 21.9422 | 21.76 | 24.9023 | 65.204 | 171.5305 | 135.3226 | 94.8263 | 1.099 | 0.75151 | 72.7701 | 21.8982 | 22.2227 | 20.7265 | 21.5685 | 22.0242 | 21.9687 | 22.5107 | 32.7435 | 21.8186 | 21.8109 | 26.0393 | 165.4463 | 205.4143 | 135.327 | 136.6394 | 91.7728 |  | 65.7429 | 134.2267 | 71.9575 | 109.2961 | 90.4961 | 79.7612 |  | 89.2534 |  |  | 24.7461 | 28.9445 | 66.8266 | [5 empty] | 21.8831 | 80.3357 | 21.7003 | 22.0818 | 35.5245 | 21.2809 | 21.9186 | 32.2826 | 112.8652 | 214.584 |  | 96.8178 | 158.8978 | 24.9564 | 88.7233 | 172.8193 | 57.6426 | 131.1793 | 28.517 | 130.4989 | 28.3028 | 128.2831 | 18.9345 | 96.8781 | 150.6964 | 34.3599 | 89.9873 | 178.3471 | 23.7058 | 90.3614 | 166.1859 | 24.75 | 117.7498 | 36.7007 | 127.6993 | 29.1293 | 136.2803 | 1.6065 | 18.8151 | 1.8982 | 0.072123 | -27.1475 | 3.0952 | 236.9 | 52.52 | 1.1986 | -0.92671 | -6.4438 | 0.9475 | 0.51176 | -14.9111 | 5.1803 | 0.024829 | -0.92543 | 0.46929 | -2.2954 | -1.7315 | -0.6811 | -0.079707
42838.4258 | 479 | 22.8938 | 22.8628 | 22.8482 | 22.7649 | 22.3759 | 21.6977 | 22.7021 | 21.7584 | 22.3452 | 22.3535 | 22.3185 | 21.982 | 21.1856 | 22.1627 | 21.5873 | 21.7616 | 21.8897 | 21.0657 | 21.1928 | 21.645 | 20.4707 | 21.0956 | 24.733 | 21.8831 | 22.1096 | 28.3612 | 169.1495 | 147.3412 | 179.5844 | 22.1157 | 22.0358 | 26.3529 | 22.0311 | 22.1515 | 28.219 | 75.5207 | 175.7942 |  | 111.9283 | 145.2394 | 142.0628 | 129.897 |  | 17.6177 | 18.7074 | 17.6148 | 18.6433 | 19.491 | 31.6574 | 126.7768 | 15.849 | 17.2302 | 15.8445 | 18.837 | 18.7097 | 46.2384 | 49.249 | 45.2273 | 21.6632 |  |  | 0.81703 | -0.27145 | -29.1636 | 0.50791 | 0.25312 | -150.3569 | 18.2595 | 0.43925 | 0.12347 | 0.22795 | 0.4211 | 0.00035484 | 0.00036963 | 0.27924 | 21.8662 | 21.962 | 22.1628 | 22.2104 | 22.0236 | 21.3157 | 20.1308 | 22.1865 | 22.3585 | 22.4005 | 22.3469 | 21.9596 | 21.1904 | 22.2691 | 86.0232 | 56.5263 | 58.8666 | 40.8549 | 33.9878 | 59.198 | 37.8035 | 22.3222 | 22.0895 | 21.6563 | 22.0492 | 21.7798 | 21.5235 | 21.9342 | 21.7549 | 24.9214 | 65.3857 | 171.2753 | 135.4665 | 94.9431 | 1.6969 | 0.93391 | 72.7029 | 21.8921 | 22.2134 | 20.7163 | 21.565 | 22.0202 | 21.9725 | 22.5082 | 32.7908 | 21.8122 | 21.8029 | 26.0588 | 165.8005 | 205.2628 | 135.428 | 136.8189 | 93.3372 |  | 65.9644 | 132.8186 | 72.1969 | 112.8839 | 90.985 | 79.8018 |  | 89.5155 |  |  | 24.7766 | 28.948 | 66.7897 | [5 empty] | 21.895 | 80.3509 | 21.7002 | 22.0852 | 35.5502 | 21.2837 | 21.9171 | 32.3147 | 113.0435 | 214.8873 |  | 97.0828 | 159.1384 | 24.9954 | 88.9173 | 172.9623 | 57.6732 | 131.355 | 28.5455 | 130.4895 | 28.337 | 128.567 | 18.9638 | 97.2159 | 150.9804 | 34.3888 | 90.2154 | 178.7928 | 23.7216 | 90.4818 | 166.4846 | 24.7428 | 117.9058 | 36.7177 | 127.9491 | 29.1844 | 136.6232 | 1.3881 | 18.8033 | 1.9066 | 0.071695 | -27.1673 | 3.0952 | 225.54 | 51.33 | 1.3403 | -0.6203 | -6.4294 | 0.84848 | 0.61213 | -14.9191 | 5.1991 | -0.010518 | -0.87744 | 0.38855 | -2.2888 | -1.8102 | -0.67245 | -0.076306
42838.4258 | 480 | 22.8896 | 22.8639 | 22.8405 | 22.7682 | 22.3773 | 21.693 | 22.6963 | 21.7557 | 22.3471 | 22.3537 | 22.3255 | 21.9808 | 21.1875 | 22.1538 | 21.5991 | 21.7717 | 21.8955 | 21.076 | 21.1982 | 21.6482 | 20.4813 | 21.1076 | 24.7603 | 21.8991 | 22.1235 | 28.4041 | 169.7538 | 147.7289 | 180.7197 | 22.1153 | 22.0436 | 26.3885 | 22.036 | 22.1623 | 28.2605 | 75.752 | 175.8121 |  | 112.1622 | 145.3183 | 142.3759 | 130.4326 |  | 17.6237 | 18.7127 | 17.6114 | 18.6425 | 19.4928 | 32.2246 | 127.3291 | 15.875 | 17.2239 | 15.9172 | 18.8306 | 18.7117 | 46.2367 | 49.2463 | 45.2172 | 21.6632 |  |  | 0.53184 | -0.31548 | -28.929 | 0.50199 | 0.38192 | -151.1757 | 18.7254 | 0.52139 | 0.10887 | 0.049834 | 0.32336 | 0.00034006 | 0.00034663 | 0.30422 | 21.8734 | 21.9547 | 22.1625 | 22.2173 | 22.0298 | 21.3134 | 20.1268 | 22.1828 | 22.3566 | 22.3976 | 22.3511 | 21.9645 | 21.1908 | 22.2698 | 88.0706 | 58.6547 | 63.1117 | 41.466 | 34.986 | 59.3519 | 37.9475 | 22.3154 | 22.0845 | 21.6549 | 22.053 | 21.7751 | 21.5236 | 21.936 | 21.7523 | 24.9526 | 65.58 | 171.2647 | 135.5113 | 95.8854 | 1.6729 | 1.3807 | 73.0501 | 21.8948 | 22.2189 | 20.7275 | 21.5667 | 22.0253 | 21.9732 | 22.5208 | 32.8511 | 21.8099 | 21.8111 | 26.0832 | 166.1866 | 205.3884 | 135.6027 | 137.1021 | 92.3033 |  | 66.1441 | 133.3614 | 72.4075 | 111.613 | 91.3574 | 79.3633 |  | 89.7141 |  |  | 24.8141 | 28.9881 | 66.3968 | [5 empty] | 21.9009 | 80.3384 | 21.7051 | 22.1003 | 35.617 | 21.289 | 21.9206 | 32.3558 | 113.195 | 215.3557 |  | 97.2051 | 159.2687 | 25.0287 | 89.0129 | 172.9974 | 57.7092 | 131.5447 | 28.5802 | 130.5868 | 28.3762 | 128.8562 | 18.997 | 97.3521 | 151.2212 | 34.4275 | 90.4009 | 179.3623 | 23.7479 | 90.6017 | 166.8265 | 24.7568 | 118.0741 | 36.7321 | 128.1833 | 29.2274 | 136.9474 | 1.0522 | 18.7944 | 1.9148 | 0.070693 | -27.2993 | 3.0951 | 244.58 | 52.21 | 1.0827 | -0.66872 | -6.4036 | 0.84354 | 0.75261 | -14.9735 | 5.2699 | 0.024784 | -0.88469 | 0.43828 | -2.4979 | -2.2649 | -0.67868 | -0.095373
42838.4258 | 481 | 22.8891 | 22.8568 | 22.8403 | 22.7593 | 22.3694 | 21.6982 | 22.6948 | 21.7568 | 22.3428 | 22.3535 | 22.3274 | 21.9736 | 21.1909 | 22.1607 | 21.6035 | 21.7806 | 21.9066 | 21.0812 | 21.2005 | 21.6482 | 20.483 | 21.1116 | 24.787 | 21.8977 | 22.1278 | 28.4431 | 170.1462 | 148.2201 | 180.8745 | 22.1054 | 22.0302 | 26.4013 | 22.0343 | 22.1552 | 28.2847 | 75.9662 | 174.4757 |  | 112.3829 | 145.3485 | 142.7152 | 132.4287 |  | 17.6439 | 18.7173 | 17.6205 | 18.6555 | 19.5015 | 33.3778 | 127.7526 | 15.9516 | 17.2287 | 15.9338 | 18.8361 | 18.7116 | 46.2209 | 49.2425 | 45.2133 | 21.6593 |  |  | 0.77694 | -0.31548 | -29.1564 | 0.2582 | 0.21041 | -151.9918 | 18.4258 | 0.28877 | 0.058084 | -0.13206 | 0.38048 | 0.00031213 | 0.00035977 | 0.28828 | 21.8646 | 21.9495 | 22.1517 | 22.2055 | 22.0252 | 21.3003 | 20.1248 | 22.173 | 22.3536 | 22.3893 | 22.3426 | 21.9491 | 21.1758 | 22.2633 | 90.1757 | 61.6712 | 65.2293 | 43.0143 | 36.8717 | 59.5168 | 38.0975 | 22.3281 | 22.0886 | 21.6573 | 22.0509 | 21.781 | 21.5336 | 21.9485 | 21.7678 | 24.9827 | 65.7906 | 171.2256 | 135.7097 | 96.7747 | 1.2254 | 1.0153 | 73.6678 | 21.9016 | 22.2207 | 20.7335 | 21.5711 | 22.0266 | 21.969 | 22.5306 | 32.9022 | 21.8168 | 21.8122 | 26.1136 | 166.3946 | 205.6144 | 135.8307 | 137.3657 | 91.1889 |  | 66.3037 | 133.5339 | 72.6056 | 110.3712 | 91.7065 | 78.7087 |  | 89.8691 |  |  | 24.8253 | 29.0339 | 65.9906 | [5 empty] | 21.8926 | 80.2173 | 21.6965 | 22.0958 | 35.6673 | 21.2884 | 21.9153 | 32.3797 | 113.4135 | 215.5434 |  | 97.3943 | 159.3444 | 25.0556 | 89.163 | 172.9587 | 57.7097 | 131.7224 | 28.5981 | 130.8126 | 28.4215 | 129.1922 | 19.0127 | 97.2962 | 151.3377 | 34.4789 | 90.5847 | 179.8648 | 23.781 | 90.6959 | 166.9554 | 24.7826 | 118.332 | 36.7937 | 128.3339 | 29.2694 | 137.3763 | 1.2982 | 18.7871 | 1.9212 | 0.071397 | -27.2068 | 3.0952 | 231.75 | 52 | 1.3089 | -0.66872 | -6.4287 | 0.60498 | 0.55967 | -15.0422 | 5.2374 | 0.061589 | -0.88213 | 0.48632 | -2.7121 | -2.4825 | -0.72611 | -0.11236
42838.4259 | 482 | 22.8932 | 22.8543 | 22.8417 | 22.7607 | 22.3714 | 21.696 | 22.6986 | 21.7598 | 22.3399 | 22.3533 | 22.3278 | 21.9695 | 21.1926 | 22.1539 | 21.6035 | 21.7793 | 21.9068 | 21.082 | 21.205 | 21.6541 | 20.484 | 21.1254 | 24.814 | 21.8977 | 22.1341 | 28.4714 | 170.2424 | 148.6766 | 179.7682 | 22.1184 | 22.0384 | 26.4265 | 22.0322 | 22.1566 | 28.3303 | 76.2069 | 176.2166 |  | 112.6733 | 145.5263 | 143.0621 | 134.1195 |  | 17.6578 | 18.7241 | 17.6443 | 18.6703 | 19.5104 | 33.2762 | 128.0983 | 16.0117 | 17.2388 | 15.9195 | 18.8433 | 18.7203 | 46.2111 | 49.2422 | 45.2088 | 21.6644 |  |  | 0.70269 | -0.048033 | -29.594 | 0.28646 | 0.14995 | -150.2097 | 18.0834 | 0.8138 | 0.13826 | -0.012477 | 0.2376 | 0.00035977 | 0.00038113 | 0.27861 | 21.8766 | 21.9606 | 22.1616 | 22.2105 | 22.0231 | 21.3099 | 20.13 | 22.1821 | 22.3657 | 22.399 | 22.3425 | 21.9628 | 21.1791 | 22.2768 | 88.9262 | 60.1135 | 62.5798 | 42.5934 | 37.4771 | 59.6271 | 38.2099 | 22.3241 | 22.0809 | 21.6584 | 22.0501 | 21.7811 | 21.5289 | 21.9375 | 21.768 | 24.999 | 65.985 | 171.551 | 136.1242 | 96.6881 | 0.95392 | 0.27848 | 73.7358 | 21.894 | 22.2189 | 20.7426 | 21.5732 | 22.0249 | 21.973 | 22.533 | 32.951 | 21.8183 | 21.8173 | 26.1413 | 166.3826 | 205.6797 | 136.0209 | 137.6024 | 90.9462 |  | 66.4998 | 132.4864 | 72.7994 | 112.173 | 92.1121 | 78.3849 |  | 90.0834 |  |  | 24.8206 | 29.058 | 65.8422 | [5 empty] | 21.8836 | 80.0311 | 21.6911 | 22.0903 | 35.713 | 21.2801 | 21.9188 | 32.4147 | 113.6797 | 215.9133 |  | 97.6461 | 159.5005 | 25.0913 | 89.4764 | 173.1363 | 57.7426 | 131.9139 | 28.62 | 131.1723 | 28.4484 | 129.5426 | 19.0421 | 97.2547 | 151.5943 | 34.5581 | 90.8051 | 180.2773 | 23.8134 | 91.0203 | 167.2218 | 24.8224 | 118.5592 | 36.8519 | 128.44 | 29.3116 | 138.0106 | 1.4334 | 18.7765 | 1.9302 | 0.07192 | -27.1235 | 3.0952 | 220.92 | 51.58 | 1.2432 | -0.26094 | -6.4769 | 0.63723 | 0.4724 | -14.9513 | 5.1876 | 0.07552 | -0.84583 | 0.45201 | -2.5601 | -2.1749 | -0.76406 | -0.10284
42838.4259 | 483 | 22.8918 | 22.8511 | 22.8414 | 22.7636 | 22.3739 | 21.6976 | 22.6965 | 21.7554 | 22.3426 | 22.3508 | 22.3279 | 21.9742 | 21.1908 | 22.1578 | 21.6049 | 21.772 | 21.9083 | 21.081 | 21.2 | 21.655 | 20.4821 | 21.1276 | 24.8305 | 21.8982 | 22.1391 | 28.5039 | 170.2091 | 149.1299 | 178.8199 | 22.1123 | 22.0393 | 26.4515 | 22.0273 | 22.1601 | 28.3687 | 76.4415 | 178.5337 |  | 112.9618 | 145.7022 | 143.3871 | 135.3094 |  | 17.6579 | 18.722 | 17.6538 | 18.6743 | 19.5469 | 33.0432 | 128.656 | 15.9782 | 17.239 | 15.8951 | 18.8434 | 18.7207 | 46.1896 | 49.247 | 45.2108 | 21.6666 |  |  | 0.7224 | -0.35951 | -29.3345 | 0.46257 | -0.13786 | -149.7924 | 17.7943 | 0.74415 | -0.066849 | 0.21704 | 0.51883 | 0.00035156 | 0.00034992 | 0.27348 | 21.8755 | 21.9531 | 22.159 | 22.2075 | 22.0271 | 21.311 | 20.1329 | 22.1831 | 22.3573 | 22.3981 | 22.3455 | 21.9588 | 21.1871 | 22.2714 | 87.3442 | 56.5825 | 58.9059 | 41.2661 | 36.8552 | 59.7226 | 38.278 | 22.3171 | 22.0814 | 21.6535 | 22.0515 | 21.7795 | 21.5242 | 21.9332 | 21.762 | 25.0135 | 66.1662 | 171.5464 | 136.2932 | 96.3699 | 1.5557 | 0.55865 | 73.3754 | 21.8997 | 22.2274 | 20.7467 | 21.5668 | 22.0232 | 21.98 | 22.5466 | 33.0111 | 21.8159 | 21.8253 | 26.168 | 166.4431 | 205.8594 | 136.2232 | 137.7968 | 90.474 |  | 66.7088 | 131.1964 | 72.9517 | 115.6315 | 92.536 | 78.1487 |  | 90.3343 |  |  | 24.8017 | 29.0671 | 66.4804 | [5 empty] | 21.8896 | 80.2334 | 21.695 | 22.0948 | 35.7685 | 21.2763 | 21.9189 | 32.454 | 113.8873 | 216.4845 |  | 97.9153 | 159.6227 | 25.1221 | 89.7735 | 173.4817 | 57.8186 | 132.1182 | 28.6504 | 131.4659 | 28.4857 | 129.862 | 19.0678 | 97.5504 | 151.9433 | 34.6115 | 91.0722 | 180.7689 | 23.8457 | 91.2862 | 167.3276 | 24.8473 | 118.6685 | 36.8967 | 128.652 | 29.3525 | 138.5182 | 1.3626 | 18.7698 | 1.9387 | 0.07396 | -27.1741 | 3.0952 | 246.09 | 52.58 | 1.2592 | -0.71387 | -6.4484 | 0.80975 | -0.45278 | -14.9248 | 5.1441 | 0.096297 | -0.80433 | 0.37241 | -2.3729 | -1.7586 | -0.78833 | -0.087367
42838.4259 | 484 | 22.8885 | 22.8517 | 22.8374 | 22.7599 | 22.3727 | 21.692 | 22.6977 | 21.7539 | 22.3463 | 22.3545 | 22.3278 | 21.9778 | 21.1873 | 22.1609 | 21.5977 | 21.7698 | 21.9035 | 21.0809 | 21.1953 | 21.6524 | 20.4708 | 21.1265 | 24.8531 | 21.9006 | 22.1412 | 28.5339 | 170.4808 | 149.528 | 179.477 | 22.1115 | 22.0408 | 26.4809 | 22.0302 | 22.1662 | 28.402 | 76.6939 | 180.1746 |  | 113.2434 | 145.8891 | 143.7342 | 135.8422 |  | 17.6874 | 18.7242 | 17.6655 | 18.692 | 19.6182 | 32.8825 | 129.1608 | 15.9316 | 17.2402 | 15.9344 | 18.8567 | 18.7167 | 46.1577 | 49.2359 | 45.1901 | 21.6588 |  |  | 0.71189 | -0.40879 | -29.4376 | 0.34691 | 0.12498 | -152.4708 | 18.2372 | 0.87754 | 0.14468 | 0.33243 | 0.40287 | 0.00036963 | 0.00034499 | 0.29073 | 21.8739 | 21.9565 | 22.1578 | 22.2075 | 22.0223 | 21.3134 | 20.1237 | 22.1821 | 22.3564 | 22.3967 | 22.3443 | 21.9572 | 21.1863 | 22.2722 | 88.9769 | 57.07 | 58.3123 | 40.2744 | 36.9285 | 59.8773 | 38.3462 | 22.3244 | 22.0921 | 21.6564 | 22.0544 | 21.7804 | 21.5394 | 21.9455 | 21.772 | 25.0406 | 66.3699 | 171.5787 | 136.3761 | 96.3206 | 1.4741 | 0.99858 | 73.1172 | 21.8967 | 22.2203 | 20.7514 | 21.568 | 22.0207 | 21.9749 | 22.5505 | 33.0643 | 21.8166 | 21.8244 | 26.1972 | 166.5381 | 206.3998 | 136.483 | 138.0262 | 90.6516 |  | 66.8753 | 131.0178 | 73.0645 | 115.3068 | 92.8342 | 78.3789 |  | 90.5173 |  |  | 24.789 | 29.1062 | 66.9138 | [5 empty] | 21.8947 | 80.5894 | 21.7019 | 22.0994 | 35.8019 | 21.2861 | 21.9171 | 32.4779 | 114.0831 | 217.4346 |  | 98.1378 | 159.6224 | 25.1431 | 89.9079 | 173.5375 | 57.9135 | 132.3072 | 28.6761 | 131.6358 | 28.5196 | 130.0884 | 19.072 | 97.9588 | 152.2834 | 34.6567 | 91.3522 | 181.3616 | 23.8689 | 91.4555 | 167.5258 | 24.8322 | 118.7813 | 36.9346 | 128.8178 | 29.3943 | 138.9 | 1.3288 | 18.7613 | 1.9467 | 0.074156 | -27.2042 | 3.0952 | 240.89 | 51.83 | 1.251 | -0.76123 | -6.4598 | 0.70125 | 0.431 | -15.0537 | 5.2063 | 0.097473 | -0.79518 | 0.39302 | -2.5359 | -1.6846 | -0.79367 | -0.078531
42838.4259 | 485 | 22.8891 | 22.8565 | 22.8414 | 22.7635 | 22.3718 | 21.6959 | 22.6967 | 21.7504 | 22.3446 | 22.3497 | 22.3324 | 21.9709 | 21.1829 | 22.1598 | 21.6024 | 21.769 | 21.8998 | 21.0791 | 21.2031 | 21.6621 | 20.4767 | 21.1296 | 24.879 | 21.9066 | 22.1428 | 28.571 | 170.9285 | 149.8823 | 179.7453 | 22.118 | 22.0465 | 26.5051 | 22.0229 | 22.1736 | 28.439 | 76.9158 | 181.7363 |  | 113.5166 | 146.1609 | 143.9883 | 135.8601 |  | 17.695 | 18.7416 | 17.6862 | 18.7026 | 19.6644 | 32.8271 | 129.382 | 15.8939 | 17.2376 | 16.0077 | 18.866 | 18.7342 | 46.1354 | 49.2247 | 45.181 | 21.6632 |  |  | 0.83411 | -0.44099 | -29.1419 | 0.46257 | 0.090156 | -151.9005 | 18.3174 | 0.68632 | 0.23575 | 0.071233 | 0.26555 | 0.00034827 | 0.00033842 | 0.34759 | 21.8838 | 21.9679 | 22.1663 | 22.2152 | 22.0329 | 21.3169 | 20.1258 | 22.1872 | 22.3648 | 22.3998 | 22.3476 | 21.9659 | 21.1877 | 22.2751 | 90.051 | 59.2725 | 58.5761 | 40.5736 | 36.7245 | 60.0186 | 38.434 | 22.3173 | 22.082 | 21.6489 | 22.0506 | 21.7734 | 21.5302 | 21.9344 | 21.7616 | 25.0594 | 66.5354 | 172.1356 | 137.0877 | 96.2677 | 0.8043 | 0.50463 | 72.9569 | 21.8959 | 22.2218 | 20.7545 | 21.5723 | 22.02 | 21.9715 | 22.5534 | 33.1103 | 21.812 | 21.8274 | 26.2218 | 166.595 | 206.8353 | 136.6425 | 138.1693 | 90.4773 |  | 67.0716 | 130.9092 | 73.1848 | 114.597 | 93.1727 | 78.6072 |  | 90.6794 |  |  | 24.7973 | 29.2625 | 66.9638 | [5 empty] | 21.8974 | 81.1252 | 21.7038 | 22.0971 | 35.8208 | 21.2906 | 21.9158 | 32.5113 | 114.2802 | 218.3324 |  | 98.2666 | 159.6142 | 25.1773 | 90.1998 | 173.3004 | 57.9682 | 132.4978 | 28.7204 | 131.7682 | 28.5631 | 130.5413 | 19.0732 | 98.2322 | 152.8018 | 34.7089 | 91.5722 | 182.1108 | 23.8959 | 91.7337 | 167.7459 | 24.8241 | 118.9515 | 36.977 | 129.0188 | 29.4359 | 139.4404 | 1.4989 | 18.7495 | 1.9537 | 0.074403 | -27.1563 | 3.0952 | 232.24 | 52.32 | 1.3545 | -0.79066 | -6.4274 | 0.80978 | 0.36602 | -15.0242 | 5.2173 | 0.10952 | -0.78769 | 0.42591 | -2.6383 | -1.7036 | -0.78585 | -0.070994
42838.4259 | 486 | 22.8891 | 22.8531 | 22.8453 | 22.7662 | 22.3725 | 21.6926 | 22.6932 | 21.7488 | 22.3396 | 22.3543 | 22.3262 | 21.9729 | 21.1879 | 22.159 | 21.6011 | 21.7754 | 21.9054 | 21.081 | 21.2049 | 21.6605 | 20.4795 | 21.1379 | 24.9054 | 21.9067 | 22.1476 | 28.6072 | 171.2551 | 150.3159 | 179.6689 | 22.1067 | 22.0532 | 26.5347 | 22.0319 | 22.1724 | 28.4735 | 77.1422 | 180.8228 |  | 113.7666 | 146.4199 | 144.2535 | 134.8205 |  | 17.7088 | 18.7644 | 17.7027 | 18.731 | 19.6799 | 32.8566 | 129.0202 | 15.8723 | 17.2539 | 16.0582 | 18.8737 | 18.7352 | 46.1158 | 49.2094 | 45.1748 | 21.6687 |  |  | 0.62121 | -0.42193 | -29.5428 | 0.35743 | 0.1493 | -149.2365 | 18.1965 | 0.57199 | 0.095253 | 0.25502 | 0.46571 | 0.00036799 | 0.00036634 | 0.37917 | 21.882 | 21.9643 | 22.1643 | 22.2172 | 22.0306 | 21.3173 | 20.1308 | 22.1811 | 22.3581 | 22.4041 | 22.3453 | 21.9633 | 21.1859 | 22.2742 | 84.935 | 57.0273 | 56.998 | 40.969 | 36.4833 | 60.0557 | 38.5105 | 22.3258 | 22.087 | 21.6509 | 22.0484 | 21.7801 | 21.5355 | 21.942 | 21.7702 | 25.0829 | 66.7042 | 173.1942 | 138.1151 | 95.6798 | 0.73884 | 0.31101 | 72.741 | 21.8933 | 22.2201 | 20.7547 | 21.5665 | 22.022 | 21.978 | 22.5627 | 33.1672 | 21.8095 | 21.8373 | 26.2476 | 166.7997 | 206.9925 | 136.7944 | 138.2361 | 91.5829 |  | 67.2868 | 132.1024 | 73.3534 | 115.37 | 93.5801 | 78.4052 |  | 90.8994 |  |  | 24.8024 | 29.3469 | 67.0841 | [5 empty] | 21.903 | 81.5408 | 21.7074 | 22.1007 | 35.8581 | 21.2964 | 21.9256 | 32.5395 | 114.462 | 218.6354 |  | 98.3888 | 159.4864 | 25.2 | 90.5689 | 173.0941 | 58.0115 | 132.68 | 28.7615 | 131.8702 | 28.5996 | 130.8719 | 19.0627 | 98.4556 | 153.3875 | 34.7616 | 91.7627 | 182.742 | 23.9356 | 91.9554 | 167.9591 | 24.8262 | 119.1904 | 37.0688 | 129.268 | 29.4847 | 139.9136 | 1.2401 | 18.742 | 1.9608 | 0.07388 | -27.211 | 3.0952 | 225.76 | 52.27 | 1.1688 | -0.77342 | -6.4717 | 0.71185 | 0.47104 | -14.8926 | 5.2003 | 0.086712 | -0.81456 | 0.4203 | -2.0654 | -1.5192 | -0.74848 | -0.048474
42838.4259 | 487 | 22.8872 | 22.8587 | 22.8424 | 22.7639 | 22.3725 | 21.6998 | 22.6952 | 21.7526 | 22.3429 | 22.3526 | 22.3213 | 21.9648 | 21.1902 | 22.1528 | 21.601 | 21.7738 | 21.9012 | 21.0779 | 21.1997 | 21.6707 | 20.4796 | 21.1358 | 24.9204 | 21.9042 | 22.1505 | 28.6336 | 171.5176 | 150.7362 | 180.3487 | 22.1087 | 22.047 | 26.5508 | 22.0233 | 22.1719 | 28.5115 | 77.4056 | 179.4742 |  | 113.9948 | 146.557 | 144.6285 | 136.0132 |  | 17.7123 | 18.7764 | 17.7148 | 18.7488 | 19.6911 | 32.7499 | 129.1056 | 15.8607 | 17.2475 | 16.0578 | 18.8766 | 18.7325 | 46.0824 | 49.1912 | 45.1695 | 21.6606 |  |  | 0.66917 | -0.2478 | -29.5828 | 0.44219 | 0.065844 | -151.8137 | 17.9579 | 0.55556 | 0.0049584 | 0.19145 | 0.41485 | 0.0003532 | 0.00034992 | 0.41222 | 21.8716 | 21.9557 | 22.1552 | 22.2062 | 22.0209 | 21.3092 | 20.1255 | 22.1777 | 22.3467 | 22.3981 | 22.3392 | 21.9533 | 21.1797 | 22.2665 | 80.018 | 52.7439 | 54.1818 | 40.8965 | 35.9624 | 60.0582 | 38.5573 | 22.3284 | 22.0868 | 21.6553 | 22.0501 | 21.7795 | 21.5468 | 21.9456 | 21.7773 | 25.1122 | 66.8729 | 173.3652 | 138.2638 | 95.3395 | 1.5997 | 0.58737 | 72.6131 | 21.8905 | 22.2212 | 20.7524 | 21.5598 | 22.0226 | 21.9786 | 22.5671 | 33.2216 | 21.817 | 21.8339 | 26.2702 | 167.0174 | 206.9978 | 136.9502 | 138.3305 | 91.6113 |  | 67.4838 | 132.4739 | 73.557 | 114.6349 | 93.8585 | 78.6673 |  | 91.0867 |  |  | 24.8139 | 29.361 | 67.8088 | [5 empty] | 21.8957 | 83.4665 | 21.7014 | 22.096 | 35.8628 | 21.2819 | 21.9206 | 32.5666 | 114.6499 | 219.1266 |  | 98.5855 | 159.596 | 25.2294 | 90.8379 | 173.3398 | 58.1106 | 132.9267 | 28.7974 | 131.9974 | 28.6353 | 131.191 | 19.0678 | 98.7806 | 153.6693 | 34.8049 | 91.9118 | 183.0687 | 23.9775 | 91.8899 | 168.2033 | 24.8283 | 119.4719 | 37.127 | 129.4027 | 29.5252 | 140.1812 | 1.8397 | 18.7343 | 1.967 | 0.075027 | -27.3315 | 3.0951 | 241.33 | 51.7 | 1.214 | -0.59272 | -6.4763 | 0.79179 | 0.31276 | -15.018 | 5.1652 | 0.093162 | -0.8173 | 0.45158 | -1.5188 | -1.2008 | -0.77172 | -0.032832
42838.4259 | 488 | 22.8836 | 22.855 | 22.8362 | 22.7579 | 22.3651 | 21.6904 | 22.6962 | 21.7546 | 22.3373 | 22.3462 | 22.321 | 21.9685 | 21.1873 | 22.1514 | 21.6033 | 21.7729 | 21.9036 | 21.0806 | 21.1978 | 21.665 | 20.4789 | 21.1454 | 24.9471 | 21.8996 | 22.1556 | 28.6704 | 171.7737 | 150.9791 | 180.1565 | 22.1026 | 22.0478 | 26.5845 | 22.0281 | 22.1823 | 28.5412 | 77.6263 | 179.4724 |  | 114.2419 | 146.7193 | 145.0535 | 136.8987 |  | 17.7185 | 18.7893 | 17.7173 | 18.7567 | 19.6978 | 32.6057 | 129.4201 | 15.8643 | 17.2457 | 16.0656 | 18.8836 | 18.7305 | 46.0593 | 49.1737 | 45.1617 | 21.6642 |  |  | 0.58835 | -0.36411 | -29.7925 | 0.55259 | 0.1217 | -153.7391 | 17.4112 | 0.71064 | 0.049911 | 0.36348 | 0.52526 | 0.0003417 | 0.00037784 | 0.45697 | 21.8746 | 21.9602 | 22.1544 | 22.2081 | 22.0252 | 21.3111 | 20.1238 | 22.1774 | 22.352 | 22.3888 | 22.3382 | 21.9542 | 21.1862 | 22.2728 | 81.2747 | 54.3729 | 56.0699 | 41.1573 | 35.4289 | 60.1388 | 38.6329 | 22.3268 | 22.0849 | 21.6604 | 22.0528 | 21.7866 | 21.5481 | 21.9377 | 21.7733 | 25.1422 | 67.0373 | 173.3833 | 138.356 | 95.1549 | 1.274 | 1.0749 | 72.7065 | 21.8931 | 22.22 | 20.7511 | 21.5599 | 22.0262 | 21.977 | 22.5692 | 33.2727 | 21.8208 | 21.8323 | 26.3013 | 167.3231 | 207.2604 | 137.1258 | 138.4592 | 91.6796 |  | 67.6753 | 132.4624 | 73.7696 | 113.2001 | 94.111 | 78.6828 |  | 91.2628 |  |  | 24.8443 | 29.3855 | 67.4789 | [5 empty] | 21.8969 | 84.2916 | 21.709 | 22.0945 | 35.8758 | 21.2818 | 21.929 | 32.6022 | 114.843 | 219.2502 |  | 98.7569 | 159.5925 | 25.26 | 91.0501 | 173.4224 | 58.1996 | 133.1719 | 28.8351 | 132.2895 | 28.6759 | 131.486 | 19.0911 | 99.1971 | 153.8698 | 34.8532 | 92.096 | 183.9381 | 23.9822 | 91.7635 | 168.3128 | 24.8461 | 119.7336 | 37.1648 | 129.5394 | 29.5577 | 140.3054 | 1.3221 | 18.7313 | 1.9743 | 0.074141 | -27.2221 | 3.0952 | 247.22 | 53.01 | 1.1381 | -0.7185 | -6.4993 | 0.88515 | 0.4251 | -15.1094 | 5.0847 | 0.098301 | -0.80906 | 0.50128 | -1.6488 | -1.4017 | -0.78803 | -0.021669
42838.4259 | 489 | 22.8949 | 22.8593 | 22.841 | 22.7614 | 22.3684 | 21.6997 | 22.7025 | 21.7593 | 22.3465 | 22.3503 | 22.3264 | 21.9725 | 21.1895 | 22.1572 | 21.613 | 21.7736 | 21.8961 | 21.0813 | 21.2018 | 21.6773 | 20.4854 | 21.1455 | 24.9705 | 21.9025 | 22.1553 | 28.7029 | 171.8637 | 151.149 | 179.7583 | 22.1122 | 22.0551 | 26.6145 | 22.0334 | 22.1756 | 28.5836 | 77.8272 | 178.7742 |  | 114.5035 | 146.8474 | 145.4289 | 137.3263 |  | 17.7236 | 18.8061 | 17.7333 | 18.7821 | 19.7149 | 32.8442 | 129.8632 | 15.8767 | 17.2445 | 16.1098 | 18.8917 | 18.7293 | 46.0474 | 49.166 | 45.1588 | 21.6706 |  |  | 0.44247 | -0.26094 | -29.7905 | 0.54208 | 0.23209 | -149.59 | 17.4092 | 0.54767 | 0.17037 | 0.028224 | 0.12546 | 0.00034334 | 0.00036141 | 0.47112 | 21.8847 | 21.9719 | 22.1649 | 22.2186 | 22.0252 | 21.3229 | 20.132 | 22.1819 | 22.3683 | 22.4036 | 22.3518 | 21.9749 | 21.1958 | 22.279 | 82.2052 | 56.2708 | 57.7452 | 41.4879 | 35.9928 | 60.2109 | 38.7246 | 22.3264 | 22.0773 | 21.654 | 22.0551 | 21.787 | 21.5418 | 21.9405 | 21.7808 | 25.16 | 67.2248 | 173.511 | 138.4045 | 95.4252 | 0.88845 | 0.9847 | 73.0833 | 21.8918 | 22.2142 | 20.7546 | 21.5634 | 22.0205 | 21.9774 | 22.5712 | 33.3271 | 21.8204 | 21.8316 | 26.3274 | 167.8157 | 207.6078 | 137.3346 | 138.6318 | 91.3681 |  | 67.8668 | 133.5777 | 74.019 | 112.4568 | 94.3865 | 79.107 |  | 91.458 |  |  | 24.873 | 29.3949 | 67.1766 | [5 empty] | 21.8901 | 85.0124 | 21.7066 | 22.1003 | 35.8543 | 21.2881 | 21.934 | 32.6176 | 114.9985 | 219.4994 |  | 98.9908 | 159.91 | 25.2745 | 91.1104 | 173.2306 | 58.1937 | 133.387 | 28.8411 | 132.6581 | 28.7085 | 131.6297 | 19.0743 | 99.5893 | 154.0656 | 34.9033 | 92.3102 | 184.218 | 24.01 | 91.8215 | 168.4043 | 24.8533 | 119.8488 | 37.1586 | 129.6894 | 29.6072 | 140.4428 | 1.2359 | 18.7248 | 1.9809 | 0.074468 | -27.2185 | 3.0951 | 245.56 | 51.8 | 0.98654 | -0.60827 | -6.4993 | 0.87671 | 0.58729 | -14.9099 | 5.0864 | 0.11399 | -0.83075 | 0.53268 | -1.7436 | -1.577 | -0.79236 | -0.022295
42838.4259 | 490 | 22.8994 | 22.8593 | 22.8479 | 22.7691 | 22.3753 | 21.7023 | 22.7062 | 21.7552 | 22.3471 | 22.3493 | 22.3308 | 21.9756 | 21.1942 | 22.1546 | 21.6105 | 21.7824 | 21.9079 | 21.0844 | 21.2125 | 21.6816 | 20.4898 | 21.1555 | 24.9985 | 21.9026 | 22.1712 | 28.741 | 172.1274 | 151.4668 | 180.9694 | 22.1146 | 22.0581 | 26.6417 | 22.0315 | 22.1848 | 28.6177 | 78.0183 | 178.5442 |  | 114.742 | 147.0651 | 145.7276 | 137.037 |  | 17.7229 | 18.8191 | 17.7462 | 18.7936 | 19.7469 | 33.3737 | 129.9608 | 15.8478 | 17.2524 | 16.0901 | 18.8873 | 18.7387 | 46.059 | 49.1476 | 45.153 | 21.6782 |  |  | 0.47795 | -0.2018 | -30.0093 | 0.58479 | 0.25444 | -149.4481 | 17.4283 | 0.6423 | 0.20306 | 0.32551 | 0.37874 | 0.0003532 | 0.00035977 | 0.46027 | 21.8793 | 21.9601 | 22.1495 | 22.2094 | 22.015 | 21.3062 | 20.1224 | 22.1773 | 22.3562 | 22.3985 | 22.3455 | 21.9561 | 21.1897 | 22.2728 | 80.2845 | 54.7746 | 57.0178 | 41.6214 | 36.1492 | 60.2601 | 38.7972 | 22.3271 | 22.0774 | 21.6487 | 22.0533 | 21.7862 | 21.5508 | 21.9343 | 21.7842 | 25.1788 | 67.3943 | 173.86 | 138.419 | 95.9267 | 0.96807 | 0.4101 | 73.4403 | 21.8854 | 22.2078 | 20.7566 | 21.5605 | 22.018 | 21.9762 | 22.5729 | 33.3752 | 21.8179 | 21.8321 | 26.3531 | 168.1032 | 207.7652 | 137.5344 | 138.822 | 91.2327 |  | 68.0225 | 134.517 | 74.2209 | 112.3045 | 94.6838 | 79.1676 |  | 91.6346 |  |  | 24.9133 | 29.4044 | 66.5833 | [5 empty] | 21.8978 | 84.4715 | 21.7067 | 22.1018 | 35.8758 | 21.2901 | 21.9197 | 32.6547 | 115.135 | 219.3194 |  | 99.2378 | 160.1774 | 25.3064 | 91.1824 | 173.1643 | 58.2972 | 133.5662 | 28.8796 | 132.8332 | 28.7895 | 132.3259 | 19.056 | 99.8918 | 154.2501 | 34.9329 | 92.4965 | 184.616 | 24.0095 | 92.2667 | 169.0603 | 24.8394 | 120.025 | 37.1963 | 129.9434 | 29.6644 | 140.5005 | 1.1307 | 18.7176 | 1.9865 | 0.073953 | -27.1324 | 3.0951 | 254.15 | 52.63 | 1.0267 | -0.53493 | -6.5232 | 0.91062 | 0.61544 | -14.9157 | 5.0936 | 0.12348 | -0.84932 | 0.54852 | -1.5243 | -1.4876 | -0.77714 | -0.03
42838.426 | 491 | 22.8937 | 22.8596 | 22.8427 | 22.7592 | 22.3731 | 21.6982 | 22.6977 | 21.7553 | 22.3446 | 22.3482 | 22.3176 | 21.9677 | 21.195 | 22.1537 | 21.6003 | 21.7666 | 21.8929 | 21.0733 | 21.1943 | 21.6692 | 20.4803 | 21.1517 | 25.0236 | 21.8958 | 22.1597 | 28.7656 | 172.1134 | 151.6437 | 179.5408 | 22.1071 | 22.0572 | 26.6597 | 22.0305 | 22.1868 | 28.6547 | 78.2043 | 180.1439 |  | 114.9897 | 147.4356 | 146.0253 | 136.2194 |  | 17.7076 | 18.8162 | 17.7523 | 18.8022 | 19.8038 | 33.5032 | 130.1025 | 15.8594 | 17.2462 | 16.1052 | 18.8922 | 18.7414 | 46.0636 | 49.1253 | 45.1318 | 21.6695 |  |  | 0.6442 | -0.32008 | -30.3655 | 0.38305 | 0.14601 | -153.3402 | 17.2949 | 0.70998 | 0.28693 | 0.22795 | 0.3027 | 0.0003532 | 0.00036306 | 0.49405 | 21.8833 | 21.9558 | 22.1511 | 22.2162 | 22.0192 | 21.3053 | 20.1249 | 22.1746 | 22.3575 | 22.3962 | 22.3393 | 21.9587 | 21.1841 | 22.2694 | 79.4189 | 54.5593 | 55.4799 | 40.9309 | 35.3764 | 60.3135 | 38.8501 | 22.3206 | 22.0779 | 21.653 | 22.0472 | 21.7776 | 21.5455 | 21.9363 | 21.7795 | 25.2035 | 67.5628 | 173.8972 | 138.3659 | 96.0685 | 0.80686 | 0.67505 | 73.3847 | 21.8834 | 22.2092 | 20.7635 | 21.5548 | 22.0139 | 21.9706 | 22.5784 | 33.425 | 21.8134 | 21.8367 | 26.3816 | 168.1928 | 207.7092 | 137.6743 | 138.9418 | 91.3684 |  | 68.1685 | 134.9698 | 74.4081 | 115.0303 | 95.127 | 79.0723 |  | 91.7946 |  |  | 24.9391 | 29.393 | 66.6744 | [5 empty] | 21.8977 | 85.4008 | 21.705 | 22.0928 | 35.917 | 21.2934 | 21.9251 | 32.6737 | 115.2812 | 219.6834 |  | 99.2596 | 160.2569 | 25.3253 | 91.5021 | 173.496 | 58.4388 | 133.6932 | 28.9392 | 132.8793 | 28.8245 | 132.4664 | 19.045 | 100.0342 | 154.3366 | 35.0232 | 92.6661 | 185.0594 | 24.0273 | 92.6221 | 169.3229 | 24.8472 | 120.0952 | 37.2914 | 130.3583 | 29.702 | 140.5829 | 1.505 | 18.7122 | 1.9912 | 0.072232 | -27.1395 | 3.0951 | 240.16 | 51.57 | 1.1901 | -0.67369 | -6.5618 | 0.73699 | 0.46632 | -15.1119 | 5.0752 | 0.12508 | -0.85491 | 0.49012 | -1.4217 | -1.3105 | -0.74743 | -0.027751
42838.426 | 492 | 22.8912 | 22.8599 | 22.8439 | 22.7677 | 22.3758 | 21.7047 | 22.6947 | 21.7573 | 22.3433 | 22.3499 | 22.3253 | 21.98 | 21.1968 | 22.1623 | 21.6034 | 21.7758 | 21.8977 | 21.0787 | 21.1933 | 21.6715 | 20.4753 | 21.1518 | 25.0421 | 21.9015 | 22.1652 | 28.7971 | 172.4085 | 151.9038 | 180.8779 | 22.1133 | 22.0629 | 26.6868 | 22.0255 | 22.1872 | 28.6882 | 78.4208 | 179.1528 |  | 115.1929 | 147.7802 | 146.3475 | 136.5218 |  | 17.7074 | 18.8305 | 17.7633 | 18.8036 | 19.8086 | 33.4933 | 129.8797 | 15.9037 | 17.2482 | 16.1565 | 18.8969 | 18.7486 | 46.091 | 49.1013 | 45.12 | 21.666 |  |  | 0.80848 | -0.43902 | -30.395 | 0.36203 | 0.24918 | -151.8978 | 16.7797 | 0.61076 | 0.16142 | 0.33453 | 0.35426 | 0.00035649 | 0.0003417 | 0.52737 | 21.8833 | 21.9519 | 22.15 | 22.2023 | 22.0226 | 21.3068 | 20.1197 | 22.1777 | 22.3524 | 22.3927 | 22.3343 | 21.9526 | 21.1854 | 22.2649 | 79.7588 | 53.1612 | 54.347 | 40.9718 | 35.4695 | 60.3823 | 38.8924 | 22.3109 | 22.0748 | 21.6539 | 22.0424 | 21.7796 | 21.5472 | 21.9343 | 21.7738 | 25.2197 | 67.7257 | 173.6215 | 138.3753 | 96.0427 | 1.1029 | 0.28419 | 73.2586 | 21.8893 | 22.2166 | 20.7817 | 21.5679 | 22.0144 | 21.9758 | 22.5996 | 33.4883 | 21.8199 | 21.8482 | 26.4169 | 168.3809 | 207.7975 | 137.7822 | 138.9942 | 91.2013 |  | 68.3124 | 134.9087 | 74.5565 | 115.1683 | 95.4501 | 78.985 |  | 91.983 |  |  | 24.958 | 29.3952 | 67.1007 | [5 empty] | 21.8821 | 85.7107 | 21.7001 | 22.0898 | 35.9586 | 21.2831 | 21.9126 | 32.697 | 115.4543 | 219.6737 |  | 99.5205 | 160.2263 | 25.3534 | 91.6675 | 173.462 | 58.6463 | 133.8399 | 28.9733 | 132.9069 | 28.8701 | 132.5412 | 19.0368 | 100.3398 | 154.6714 | 35.0954 | 92.8826 | 185.4677 | 24.0631 | 92.9301 | 169.5005 | 24.8479 | 120.2042 | 37.3612 | 130.672 | 29.7334 | 140.7485 | 1.858 | 18.7069 | 1.9953 | 0.071782 | -27.2009 | 3.0951 | 234.96 | 51.77 | 1.3352 | -0.78901 | -6.5652 | 0.7165 | 0.60917 | -15.0404 | 4.9989 | 0.13502 | -0.84768 | 0.49893 | -1.4513 | -1.1796 | -0.74769 | -0.021046
42838.426 | 493 | 22.8919 | 22.8581 | 22.8358 | 22.7637 | 22.3706 | 21.6979 | 22.6978 | 21.7507 | 22.3474 | 22.3505 | 22.3237 | 21.9725 | 21.1889 | 22.1597 | 21.6061 | 21.7821 | 21.9044 | 21.0869 | 21.2048 | 21.6788 | 20.4854 | 21.1675 | 25.0691 | 21.9079 | 22.1704 | 28.8367 | 172.6612 | 152.0911 | 181.2218 | 22.1072 | 22.0706 | 26.7166 | 22.031 | 22.1933 | 28.7404 | 78.6647 | 177.902 |  | 115.3864 | 147.9784 | 146.66 | 136.1672 |  | 17.7145 | 18.8317 | 17.7644 | 18.804 | 19.8004 | 33.3931 | 129.915 | 15.9748 | 17.2565 | 16.2202 | 18.8978 | 18.7469 | 46.1211 | 49.0841 | 45.1094 | 21.672 |  |  | 0.71911 | -0.22414 | -30.194 | 0.62225 | 0.13681 | -153.3264 | 16.9269 | 0.36631 | 0.11783 | 0.2888 | 0.5046 | 0.00039756 | 0.0003877 | 0.52495 | 21.8909 | 21.9604 | 22.1602 | 22.2079 | 22.0257 | 21.3211 | 20.1276 | 22.1806 | 22.3598 | 22.3965 | 22.3448 | 21.9636 | 21.1943 | 22.2768 | 80.5981 | 52.3039 | 52.0446 | 39.9187 | 35.6515 | 60.4662 | 38.9035 | 22.3206 | 22.0793 | 21.6589 | 22.0449 | 21.7779 | 21.5468 | 21.9388 | 21.777 | 25.2445 | 67.9329 | 173.6208 | 138.4415 | 96.7992 | 1.2732 | 0.46336 | 73.3663 | 21.8925 | 22.2163 | 20.7923 | 21.5702 | 22.0213 | 21.9824 | 22.6159 | 33.5466 | 21.8205 | 21.8502 | 26.4399 | 168.5628 | 207.8925 | 137.9125 | 139.0666 | 91.2473 |  | 68.4998 | 135.1819 | 74.7158 | 115.0637 | 95.7199 | 79.5263 |  | 92.1986 |  |  | 24.95 | 29.4377 | 67.1813 | [5 empty] | 21.8877 | 85.8077 | 21.6958 | 22.0989 | 36.009 | 21.2803 | 21.9124 | 32.7308 | 115.6295 | 219.5049 |  | 99.7679 | 160.3738 | 25.3945 | 91.8336 | 173.6587 | 58.7623 | 134.0911 | 28.9821 | 133.1734 | 28.9056 | 132.5868 | 19.0327 | 100.5631 | 154.944 | 35.1567 | 93.0506 | 185.9559 | 24.0729 | 93.4933 | 169.6034 | 24.8349 | 120.4219 | 37.4272 | 130.9991 | 29.7765 | 141.0188 | 1.9595 | 18.6967 | 1.9994 | 0.072087 | -27.2509 | 3.0951 | 231.83 | 52.25 | 1.2597 | -0.56377 | -6.5434 | 0.93935 | 0.45131 | -15.1085 | 5.02 | 0.14064 | -0.84932 | 0.5124 | -1.5345 | -0.92248 | -0.72865 | -0.034437
42838.426 | 494 | 22.8897 | 22.8632 | 22.8388 | 22.7634 | 22.3772 | 21.6977 | 22.705 | 21.7522 | 22.3604 | 22.353 | 22.3292 | 21.9802 | 21.194 | 22.1657 | 21.6093 | 21.7791 | 21.9059 | 21.0846 | 21.21 | 21.6861 | 20.4834 | 21.1756 | 25.0967 | 21.9152 | 22.1819 | 28.8759 | 172.9469 | 152.3646 | 182.7487 | 22.1135 | 22.0695 | 26.7398 | 22.0311 | 22.1968 | 28.7652 | 78.9293 | 177.9709 |  | 115.6339 | 148.1184 | 146.8952 | 135.9377 |  | 17.7293 | 18.8493 | 17.7874 | 18.8196 | 19.7981 | 33.2129 | 130.0559 | 16.019 | 17.2579 | 16.2747 | 18.91 | 18.7512 | 46.1268 | 49.0671 | 45.0968 | 21.6693 |  |  | 0.61923 | -0.14792 | -30.0553 | 0.43891 | 0.28926 | -155.7722 | 16.9933 | 0.39128 | -0.059065 | 0.40503 | 0.36728 | 0.00035484 | 0.00034992 | 0.51087 | 21.8851 | 21.9543 | 22.1587 | 22.21 | 22.0217 | 21.3126 | 20.1275 | 22.1821 | 22.3548 | 22.3966 | 22.3459 | 21.9613 | 21.1909 | 22.2705 | 83.6247 | 54.7554 | 53.5607 | 39.3845 | 34.4803 | 60.6 | 38.9409 | 22.3154 | 22.0904 | 21.6538 | 22.0503 | 21.7724 | 21.5575 | 21.9413 | 21.785 | 25.2725 | 68.1378 | 173.8705 | 138.6019 | 96.8437 | 1.7423 | 1.822 | 73.6031 | 21.8944 | 22.2127 | 20.7957 | 21.5607 | 22.0193 | 21.9827 | 22.6172 | 33.6003 | 21.8243 | 21.8514 | 26.4665 | 168.7239 | 208.0906 | 138.0848 | 139.2215 | 91.9016 |  | 68.6774 | 135.6427 | 74.8882 | 114.6577 | 96.0128 | 80.2854 |  | 92.3932 |  |  | 24.9974 | 29.4816 | 67.9406 | [5 empty] | 21.8968 | 85.5123 | 21.7013 | 22.1032 | 36.0385 | 21.2901 | 21.9199 | 32.7599 | 115.8652 | 219.8969 |  | 99.9237 | 160.4446 | 25.4414 | 92.1293 | 174.0329 | 58.8825 | 134.573 | 28.9896 | 133.6962 | 28.9406 | 132.6504 | 19.0276 | 100.8147 | 155.1363 | 35.2207 | 93.1654 | 186.7624 | 24.0832 | 93.7786 | 169.8258 | 24.8344 | 120.6535 | 37.4946 | 131.4081 | 29.8144 | 141.2617 | 1.7962 | 18.6914 | 2.0033 | 0.072196 | -27.148 | 3.0951 | 238.35 | 51.88 | 1.1709 | -0.458 | -6.5286 | 0.78894 | 0.65604 | -15.224 | 5.0283 | 0.12901 | -0.85569 | 0.53515 | -1.8548 | -1.0865 | -0.71231 | -0.028139
42838.426 | 495 | 22.8883 | 22.8572 | 22.8467 | 22.7576 | 22.3664 | 21.6947 | 22.699 | 21.7497 | 22.3417 | 22.3506 | 22.3204 | 21.9732 | 21.1887 | 22.1607 | 21.5997 | 21.778 | 21.904 | 21.0836 | 21.2019 | 21.6876 | 20.4817 | 21.1748 | 25.1197 | 21.9087 | 22.1843 | 28.9086 | 173.3344 | 152.7338 | 184.0122 | 22.1117 | 22.0649 | 26.7612 | 22.0289 | 22.1988 | 28.7978 | 79.1559 | 179.6726 |  | 115.9 | 148.4037 | 147.0883 | 136.7052 |  | 17.7495 | 18.8602 | 17.7847 | 18.8348 | 19.7972 | 33.1991 | 130.443 | 16.0189 | 17.2562 | 16.2201 | 18.9205 | 18.7527 | 46.1537 | 49.0534 | 45.0792 | 21.6745 |  |  | 0.64355 | -0.1742 | -29.9574 | 0.27069 | 0.25969 | -152.6699 | 17.5163 | 0.61798 | 0.27876 | 0.12851 | 0.52526 | 0.00037127 | 0.0003532 | 0.51204 | 21.8913 | 21.9642 | 22.1589 | 22.2152 | 22.0209 | 21.3133 | 20.1298 | 22.1822 | 22.3556 | 22.3984 | 22.3429 | 21.9563 | 21.1891 | 22.2748 | 88.9216 | 62.1464 | 59.9967 | 40.5995 | 35.2319 | 60.7939 | 39.0586 | 22.3231 | 22.086 | 21.66 | 22.0572 | 21.7807 | 21.5618 | 21.9408 | 21.7852 | 25.3046 | 68.3225 | 173.9667 | 138.7595 | 96.7617 | 1.6444 | 1.585 | 73.8509 | 21.8978 | 22.2116 | 20.8046 | 21.5651 | 22.0212 | 21.9895 | 22.619 | 33.6539 | 21.8291 | 21.8579 | 26.5001 | 168.8478 | 208.1766 | 138.2893 | 139.3932 | 92.0075 |  | 68.9198 | 135.9051 | 75.0804 | 113.709 | 96.3629 | 80.7427 |  | 92.5832 |  |  | 25.037 | 29.5319 | 68.6203 | [5 empty] | 21.8921 | 85.0531 | 21.6997 | 22.0955 | 36.067 | 21.2894 | 21.9214 | 32.8137 | 116.0861 | 220.2167 |  | 100.15 | 160.6183 | 25.4843 | 92.2906 | 174.3747 | 59.0519 | 135.2242 | 29.0215 | 134.2698 | 28.9912 | 132.8372 | 19.018 | 100.974 | 155.3951 | 35.2592 | 93.2682 | 187.2953 | 24.1193 | 93.8125 | 170.1133 | 24.8435 | 120.8621 | 37.5535 | 131.67 | 29.8458 | 141.4335 | 1.4818 | 18.6883 | 2.0084 | 0.073016 | -27.2476 | 3.0951 | 244.03 | 52.45 | 1.1953 | -0.49704 | -6.5181 | 0.61958 | 0.62159 | -15.0713 | 5.105 | 0.135 | -0.8558 | 0.57523 | -2.4202 | -1.7877 | -0.72509 | -0.019063
42838.426 | 496 | 22.8908 | 22.8568 | 22.8459 | 22.7609 | 22.3655 | 21.6934 | 22.697 | 21.7525 | 22.3464 | 22.3471 | 22.3281 | 21.9686 | 21.189 | 22.1626 | 21.597 | 21.774 | 21.9034 | 21.0862 | 21.2034 | 21.6871 | 20.4844 | 21.1742 | 25.1391 | 21.9046 | 22.1849 | 28.9427 | 173.9298 | 153.1804 | 185.554 | 22.1053 | 22.0801 | 26.7993 | 22.0329 | 22.2059 | 28.8419 | 79.3711 | 179.4233 |  | 116.1763 | 148.7285 | 147.3872 | 136.9918 |  | 17.7617 | 18.8919 | 17.7911 | 18.8539 | 19.7996 | 33.1973 | 130.8851 | 15.9756 | 17.265 | 16.2092 | 18.93 | 18.751 | 46.1556 | 49.0429 | 45.055 | 21.6713 |  |  | 0.61069 | 0.032135 | -30.0987 | 0.20301 | 0.27218 | -152.8414 | 17.1858 | 0.94129 | 0.26786 | 0.39391 | 0.59331 | 0.00037291 | 0.00032856 | 0.48771 | 21.8922 | 21.9535 | 22.1581 | 22.2127 | 22.0235 | 21.3114 | 20.1269 | 22.1817 | 22.3635 | 22.3959 | 22.3377 | 21.9606 | 21.1929 | 22.2752 | 91.0534 | 64.9195 | 65.0522 | 41.9184 | 35.127 | 60.9524 | 39.1843 | 22.3228 | 22.09 | 21.6588 | 22.0583 | 21.7884 | 21.5679 | 21.9411 | 21.7936 | 25.3271 | 68.4858 | 174.7436 | 139.0503 | 96.4858 | 1.386 | 1.0123 | 73.9886 | 21.8917 | 22.2146 | 20.8047 | 21.5599 | 22.018 | 21.9848 | 22.6222 | 33.7008 | 21.8163 | 21.8517 | 26.5178 | 168.9802 | 208.1313 | 138.5122 | 139.5493 | 92.7594 |  | 69.2104 | 135.7558 | 75.2853 | 111.9368 | 96.6558 | 80.8297 |  | 92.8155 |  |  | 25.0474 | 29.5769 | 69.1209 | [5 empty] | 21.8929 | 84.5383 | 21.702 | 22.0953 | 36.1119 | 21.294 | 21.9264 | 32.8757 | 116.3459 | 220.5341 |  | 100.5664 | 161.0132 | 25.5194 | 92.3251 | 174.5709 | 59.1879 | 135.5682 | 29.0692 | 134.637 | 29.0546 | 133.0221 | 19.0154 | 100.8561 | 155.5908 | 35.2798 | 93.3994 | 187.7318 | 24.1561 | 94.006 | 170.604 | 24.8541 | 121.06 | 37.6011 | 131.9465 | 29.8806 | 141.8534 | 1.5864 | 18.6758 | 2.0131 | 0.07404 | -27.3002 | 3.095 | 256.82 | 51.67 | 1.1664 | 0.21349 | -6.5338 | 0.53659 | 0.63635 | -15.0798 | 5.0566 | 0.12482 | -0.84399 | 0.63595 | -2.6381 | -2.3346 | -0.72494 | -0.0053895
42838.426 | 497 | 22.8991 | 22.8599 | 22.8479 | 22.7607 | 22.3729 | 21.6985 | 22.702 | 21.7562 | 22.3506 | 22.3515 | 22.3274 | 21.9793 | 21.189 | 22.1702 | 21.5886 | 21.7636 | 21.893 | 21.0737 | 21.1914 | 21.6838 | 20.475 | 21.1714 | 25.1553 | 21.8989 | 22.1771 | 28.9754 | 174.3054 | 153.6581 | 185.313 | 22.1141 | 22.0854 | 26.8303 | 22.0308 | 22.2111 | 28.8778 | 79.591 | 179.1464 |  | 116.4285 | 149.0797 | 147.6494 | 136.1258 |  | 17.774 | 18.8989 | 17.7901 | 18.8568 | 19.7941 | 33.1821 | 131.2128 | 15.851 | 17.2706 | 16.172 | 18.9345 | 18.7583 | 46.1629 | 49.0242 | 45.057 | 21.6731 |  |  | 0.56863 | -0.32336 | -30.0487 | 0.28055 | 0.13681 | -156.3629 | 17.0958 | 0.95837 | 0.15169 | 0.27159 | 0.377 | 0.00038277 | 0.0003762 | 0.47577 | 21.8958 | 21.9627 | 22.1596 | 22.2188 | 22.0281 | 21.3142 | 20.1325 | 22.1846 | 22.3627 | 22.3989 | 22.3553 | 21.9641 | 21.1845 | 22.2808 | 89.9643 | 62.9309 | 65.5925 | 42.7695 | 36.1612 | 61.0619 | 39.3093 | 22.3144 | 22.0919 | 21.6679 | 22.0532 | 21.7906 | 21.5701 | 21.9426 | 21.7884 | 25.3537 | 68.6416 | 175.4547 | 139.2815 | 96.051 | 1.158 | 1.006 | 74.1468 | 21.8915 | 22.2182 | 20.8142 | 21.5577 | 22.0166 | 21.9822 | 22.6274 | 33.7584 | 21.8139 | 21.8565 | 26.5486 | 169.2239 | 208.2202 | 138.6829 | 139.6607 | 94.2306 |  | 69.4631 | 135.5634 | 75.4713 | 112.2545 | 96.9501 | 81.4942 |  | 93.049 |  |  | 25.0501 | 29.6005 | 69.6817 | [5 empty] | 21.8968 | 84.875 | 21.7072 | 22.097 | 36.1497 | 21.2908 | 21.9317 | 32.9031 | 116.5851 | 220.76 |  | 100.9578 | 161.4788 | 25.5431 | 92.4151 | 174.702 | 59.2859 | 135.807 | 29.0972 | 134.837 | 29.0981 | 133.2496 | 19.0206 | 100.8098 | 155.704 | 35.3001 | 93.6254 | 187.9997 | 24.1889 | 94.2524 | 170.9487 | 24.8814 | 121.3406 | 37.6341 | 132.2518 | 29.9238 | 142.0552 | 1.3349 | 18.6751 | 2.0173 | 0.075361 | -27.1841 | 3.0951 | 247.64 | 51.98 | 1.1252 | -0.67724 | -6.5284 | 0.63081 | 0.45115 | -15.2521 | 5.0432 | 0.093278 | -0.8317 | 0.63868 | -2.504 | -2.3799 | -0.69259 | 0.012429
42838.426 | 498 | 22.8997 | 22.8624 | 22.8568 | 22.7725 | 22.3803 | 21.7013 | 22.7002 | 21.7607 | 22.354 | 22.3563 | 22.3281 | 21.9833 | 21.1928 | 22.1697 | 21.5922 | 21.7673 | 21.8974 | 21.0736 | 21.1988 | 21.687 | 20.481 | 21.1792 | 25.1798 | 21.9029 | 22.1857 | 29.0109 | 174.4589 | 153.9919 | 185.1653 | 22.1042 | 22.0854 | 26.8545 | 22.0221 | 22.2123 | 28.9029 | 79.7782 | 179.5024 |  | 116.6795 | 149.4767 | 147.9088 | 134.9389 |  | 17.7833 | 18.9149 | 17.7924 | 18.8569 | 19.7687 | 33.1159 | 130.9805 | 15.7267 | 17.2695 | 16.1324 | 18.9358 | 18.7688 | 46.1548 | 49.0125 | 45.0395 | 21.6748 |  |  | 0.78351 | -0.20706 | -29.8148 | 0.46651 | 0.23275 | -153.448 | 16.9164 | 0.92946 | -0.013723 | 0.12725 | 0.45148 | 0.00037784 | 0.00034499 | 0.46898 | 21.9001 | 21.9644 | 22.1508 | 22.2167 | 22.0304 | 21.3108 | 20.1234 | 22.1815 | 22.3611 | 22.3928 | 22.3487 | 21.9598 | 21.1846 | 22.2719 | 89.6127 | 62.4469 | 63.2307 | 43.0563 | 36.5836 | 61.1844 | 39.4037 | 22.3228 | 22.0865 | 21.6515 | 22.0479 | 21.779 | 21.5703 | 21.9378 | 21.7855 | 25.3725 | 68.8079 | 176.4793 | 140.0496 | 96.161 | 1.5854 | 0.54286 | 74.4007 | 21.8892 | 22.2185 | 20.8249 | 21.5657 | 22.0271 | 21.9829 | 22.6357 | 33.82 | 21.8169 | 21.8621 | 26.5782 | 169.4537 | 208.4357 | 138.8845 | 139.8084 | 95.7588 |  | 69.7003 | 135.5943 | 75.6542 | 114.363 | 97.3051 | 81.7216 |  | 93.2649 |  |  | 25.0563 | 29.616 | 69.3265 | [5 empty] | 21.898 | 85.809 | 21.7084 | 22.1007 | 36.1597 | 21.2903 | 21.9288 | 32.9353 | 116.7841 | 220.8255 |  | 100.9474 | 161.8545 | 25.5535 | 92.6088 | 174.7367 | 59.4369 | 136.0095 | 29.0983 | 134.933 | 29.1315 | 133.5233 | 19.033 | 101.1441 | 156.0259 | 35.3504 | 93.8413 | 188.4318 | 24.2087 | 94.4979 | 171.1178 | 24.9042 | 121.6421 | 37.6608 | 132.5156 | 29.9713 | 141.9701 | 1.3251 | 18.672 | 2.0206 | 0.07629 | -27.1508 | 3.0951 | 252.22 | 52.04 | 1.3206 | -0.54194 | -6.5031 | 0.81346 | 0.58839 | -15.1076 | 5.0161 | 0.059586 | -0.82572 | 0.59406 | -2.4503 | -2.1063 | -0.65255 | 0.015498
42838.4261 | 499 | 22.8967 | 22.8616 | 22.8528 | 22.7669 | 22.3842 | 21.7006 | 22.6971 | 21.7608 | 22.3509 | 22.3545 | 22.3208 | 21.9771 | 21.1933 | 22.1647 | 21.6027 | 21.7771 | 21.9055 | 21.0811 | 21.2092 | 21.6946 | 20.4878 | 21.1962 | 25.2104 | 21.9105 | 22.2002 | 29.049 | 174.8572 | 154.2206 | 186.0134 | 22.1073 | 22.0816 | 26.882 | 22.0238 | 22.2146 | 28.9408 | 79.9582 | 179.3362 |  | 116.9487 | 149.8499 | 148.222 | 134.2246 |  | 17.7953 | 18.9273 | 17.7961 | 18.8837 | 19.7612 | 33.0411 | 130.4095 | 15.6813 | 17.2657 | 16.1205 | 18.9474 | 18.7728 | 46.1436 | 49.0012 | 45.0347 | 21.6726 |  |  | 0.6764 | -0.2524 | -29.6321 | 0.47111 | 0.24261 | -151.727 | 16.9939 | 0.64427 | 0.0030124 | 0.17425 | 0.54574 | 0.00036306 | 0.00036141 | 0.44144 | 21.8983 | 21.9632 | 22.1512 | 22.2161 | 22.0302 | 21.3138 | 20.1287 | 22.1785 | 22.3594 | 22.393 | 22.346 | 21.966 | 21.1942 | 22.2739 | 92.0335 | 62.7316 | 59.9289 | 43.2882 | 37.3677 | 61.3591 | 39.4537 | 22.3201 | 22.0905 | 21.6557 | 22.0577 | 21.7836 | 21.5766 | 21.9401 | 21.7961 | 25.4001 | 68.9833 | 177.1005 | 140.3435 | 96.586 | 1.4332 | 1.258 | 74.3435 | 21.895 | 22.2211 | 20.8396 | 21.5678 | 22.0279 | 21.9877 | 22.6454 | 33.8783 | 21.8205 | 21.8664 | 26.6084 | 169.5367 | 208.7326 | 139.1142 | 140.0475 | 94.9417 |  | 69.9286 | 136.0294 | 75.8293 | 114.9523 | 97.7271 | 82.255 |  | 93.4763 |  |  | 25.0794 | 29.6191 | 69.1503 | [5 empty] | 21.8954 | 85.6899 | 21.7025 | 22.0988 | 36.1743 | 21.29 | 21.925 | 32.985 | 116.9854 | 221.7028 |  | 100.6809 | 162.1441 | 25.5738 | 92.7576 | 174.5731 | 59.5893 | 136.229 | 29.1226 | 135.3633 | 29.171 | 133.7104 | 19.0461 | 101.6995 | 156.3991 | 35.4182 | 93.9867 | 189.0631 | 24.2309 | 94.8933 | 171.4721 | 24.929 | 121.8039 | 37.6808 | 132.7326 | 30.0039 | 141.847 | 1.7846 | 18.6624 | 2.025 | 0.07555 | -27.1352 | 3.095 | 238.97 | 51.33 | 1.2282 | -0.59835 | -6.4833 | 0.81748 | 0.60064 | -15.0209 | 5.027 | 0.090714 | -0.83125 | 0.59428 | -2.6983 | -1.7336 | -0.62592 | 0.010159
42838.4261 | 500 | 22.8937 | 22.8595 | 22.8507 | 22.7591 | 22.3726 | 21.6972 | 22.6928 | 21.7543 | 22.3485 | 22.3521 | 22.3217 | 21.9699 | 21.1894 | 22.1573 | 21.6077 | 21.7719 | 21.9111 | 21.0826 | 21.2017 | 21.6982 | 20.4862 | 21.199 | 25.2379 | 21.9075 | 22.2027 | 29.0804 | 175.1478 | 154.5167 | 186.1608 | 22.107 | 22.0775 | 26.902 | 22.0268 | 22.2205 | 28.9783 | 80.1604 | 179.0761 |  | 117.1928 | 150.0967 | 148.5077 | 135.002 |  | 17.8094 | 18.9376 | 17.8104 | 18.8962 | 19.7613 | 32.9463 | 130.2392 | 15.6618 | 17.2739 | 16.0334 | 18.9535 | 18.7798 | 46.1409 | 49.0038 | 45.0252 | 21.6767 |  |  | 0.74474 | -0.030293 | -30.0665 | 0.12547 | 0.45157 | -154.2036 | 16.9269 | 0.71655 | 0.31515 | 0.014587 | 0.36502 | 0.00034827 | 0.00035813 | 0.46695 | 21.9027 | 21.9597 | 22.1601 | 22.2098 | 22.0284 | 21.3107 | 20.1241 | 22.1809 | 22.3644 | 22.3961 | 22.345 | 21.9653 | 21.1861 | 22.2751 | 92.7432 | 62.2914 | 62.0897 | 43.4318 | 37.6819 | 61.4972 | 39.5618 | 22.3171 | 22.0844 | 21.6526 | 22.0538 | 21.7836 | 21.5737 | 21.9345 | 21.7925 | 25.4214 | 69.1923 | 177.6085 | 140.6935 | 97.4585 | 1.3457 | 1.0011 | 74.3886 | 21.897 | 22.2201 | 20.8427 | 21.5621 | 22.0205 | 21.9882 | 22.65 | 33.932 | 21.8232 | 21.8749 | 26.634 | 169.6676 | 208.8167 | 139.2967 | 140.2794 | 95.4193 |  | 70.1758 | 136.3368 | 76.0346 | 115.9311 | 98.1306 | 82.0608 |  | 93.6701 |  |  | 25.1088 | 29.6316 | 69.561 | [5 empty] | 21.8938 | 85.7273 | 21.6996 | 22.1015 | 36.2061 | 21.2927 | 21.9191 | 33.0459 | 117.2255 | 222.0076 |  | 100.7162 | 162.1969 | 25.6037 | 92.8905 | 174.2936 | 59.7164 | 136.4264 | 29.1464 | 136.0021 | 29.2048 | 133.8329 | 19.0455 | 102.0422 | 156.6107 | 35.4671 | 94.179 | 189.6095 | 24.2512 | 95.345 | 171.8636 | 24.9732 | 121.9073 | 37.7463 | 132.9383 | 30.0416 | 141.8335 | 1.4408 | 18.6618 | 2.0288 | 0.075521 | -27.1218 | 3.0951 | 257.19 | 52.42 | 1.2889 | -0.2073 | -6.5308 | 0.42188 | 0.81933 | -15.1406 | 5.0163 | 0.086578 | -0.83211 | 0.58298 | -2.7607 | -1.9609 | -0.63987 | -0.0063748
42838.4261 | 501 | 22.8918 | 22.861 | 22.8329 | 22.758 | 22.3686 | 21.6965 | 22.6879 | 21.7512 | 22.351 | 22.3456 | 22.3172 | 21.9675 | 21.1834 | 22.1696 | 21.598 | 21.7725 | 21.9032 | 21.0709 | 21.2088 | 21.6967 | 20.4766 | 21.196 | 25.2572 | 21.9031 | 22.2011 | 29.1011 | 175.5702 | 154.8375 | 185.7548 | 22.1117 | 22.0884 | 26.9444 | 22.0342 | 22.2332 | 29.0265 | 80.3811 | 178.299 |  | 117.5014 | 150.3435 | 148.7965 | 134.6883 |  | 17.8116 | 18.9457 | 17.8081 | 18.898 | 19.7647 | 32.9293 | 130.5309 | 15.6856 | 17.2709 | 15.8479 | 18.9523 | 18.7753 | 46.1365 | 48.9896 | 44.9999 | 21.6759 |  |  | 0.70597 | -0.14726 | -30.4384 | 0.41854 | 0.47326 | -149.843 | 16.7541 | 0.87163 | 0.14468 | 0.16103 | 0.41363 | 0.0003532 | 0.0003417 | 0.48706 | 21.9009 | 21.9628 | 22.1543 | 22.2111 | 22.0255 | 21.3106 | 20.1218 | 22.1784 | 22.3602 | 22.4015 | 22.3465 | 21.9609 | 21.1868 | 22.2745 | 92.7593 | 60.082 | 60.3033 | 43.3079 | 37.891 | 61.6189 | 39.6371 | 22.3173 | 22.0854 | 21.6567 | 22.058 | 21.7762 | 21.573 | 21.9415 | 21.7967 | 25.4529 | 69.4056 | 178.2003 | 141.0522 | 97.9497 | 1.9224 | 0.9672 | 74.5994 | 21.8894 | 22.2159 | 20.8384 | 21.5637 | 22.0224 | 21.9867 | 22.6566 | 33.9815 | 21.8244 | 21.8741 | 26.6564 | 169.874 | 209.0444 | 139.3507 | 140.4007 | 95.165 |  | 70.3649 | 136.6608 | 76.234 | 115.1255 | 98.4671 | 81.8286 |  | 93.8456 |  |  | 25.1132 | 29.6717 | 69.5069 | [5 empty] | 21.8865 | 85.4957 | 21.7047 | 22.1059 | 36.2845 | 21.2908 | 21.9255 | 33.0932 | 117.4911 | 221.7995 |  | 100.8131 | 162.1995 | 25.6269 | 93.2759 | 174.4727 | 59.7576 | 136.773 | 29.1811 | 136.5383 | 29.2499 | 134.0558 | 19.0693 | 102.2887 | 156.8371 | 35.5347 | 94.4727 | 190.1653 | 24.2809 | 95.981 | 172.2312 | 25.0355 | 122.047 | 37.8368 | 132.9897 | 30.0904 | 141.9326 | 1.7271 | 18.6653 | 2.0318 | 0.076312 | -27.1571 | 3.0951 | 250 | 51.62 | 1.2544 | -0.45706 | -6.5711 | 0.77054 | 0.83875 | -14.9246 | 4.9905 | 0.10063 | -0.83364 | 0.61861 | -2.7479 | -1.7535 | -0.62282 | -0.012149
42838.4261 | 502 | 22.8944 | 22.8595 | 22.8479 | 22.7579 | 22.3763 | 21.6988 | 22.6992 | 21.7602 | 22.3528 | 22.3505 | 22.3194 | 21.9787 | 21.1836 | 22.1648 | 21.6006 | 21.7744 | 21.8991 | 21.0747 | 21.2034 | 21.697 | 20.4753 | 21.1928 | 25.282 | 21.9072 | 22.2122 | 29.144 | 175.7495 | 155.0898 | 184.0056 | 22.115 | 22.0918 | 26.9669 | 22.0264 | 22.2273 | 29.0652 | 80.5904 | 178.7417 |  | 117.7173 | 150.5682 | 149.0375 | 134.27 |  | 17.8217 | 18.9486 | 17.8033 | 18.8973 | 19.803 | 32.7573 | 130.7758 | 15.7099 | 17.2706 | 15.7083 | 18.9541 | 18.7828 | 46.1485 | 49.0044 | 45.0039 | 21.6802 |  |  | 0.50555 | -0.32599 | -30.7814 | 0.2582 | 0.51531 | -149.2996 | 16.0194 | 0.40836 | -0.03221 | 0.17907 | 0.42231 | 0.00035977 | 0.00038441 | 0.48824 | 21.8919 | 21.9551 | 22.1533 | 22.2104 | 22.018 | 21.3093 | 20.1222 | 22.1771 | 22.3565 | 22.3966 | 22.3429 | 21.956 | 21.1884 | 22.2695 | 93.9344 | 60.8194 | 61.6724 | 42.4097 | 36.1716 | 61.7802 | 39.7476 | 22.3231 | 22.0908 | 21.661 | 22.0591 | 21.7828 | 21.5734 | 21.9528 | 21.8028 | 25.4822 | 69.6031 | 178.8129 | 141.5043 | 98.6703 | 1.3776 | 0.2684 | 74.921 | 21.894 | 22.2147 | 20.843 | 21.562 | 22.0247 | 21.9847 | 22.6671 | 34.0401 | 21.8269 | 21.8777 | 26.6888 | 169.9531 | 209.4557 | 139.42 | 140.499 | 94.8245 |  | 70.5614 | 137.9399 | 76.4399 | 115.8652 | 98.8705 | 81.9113 |  | 94.0212 |  |  | 25.1274 | 29.6742 | 69.2568 | [5 empty] | 21.8946 | 86.5844 | 21.7048 | 22.1024 | 36.3692 | 21.2898 | 21.9268 | 33.1566 | 117.7051 | 222.2174 |  | 101.09 | 162.1672 | 25.663 | 93.5939 | 174.9884 | 59.9122 | 137.0142 | 29.2307 | 136.8373 | 29.3045 | 134.2924 | 19.0937 | 102.3313 | 157.0012 | 35.5793 | 94.7125 | 190.6472 | 24.3161 | 96.6662 | 172.4912 | 25.0957 | 122.1374 | 37.9296 | 133.0323 | 30.1346 | 142.2982 | 1.9534 | 18.6472 | 2.0348 | 0.07531 | -27.1654 | 3.0951 | 244.44 | 51.97 | 1.0595 | -0.68004 | -6.6081 | 0.60522 | 0.87498 | -14.8933 | 4.8785 | 0.11736 | -0.86146 | 0.61397 | -2.8592 | -1.8926 | -0.60329 | -0.02488
42838.4261 | 503 | 22.8878 | 22.8594 | 22.8363 | 22.76 | 22.3682 | 21.6964 | 22.695 | 21.7532 | 22.3447 | 22.3572 | 22.3208 | 21.9723 | 21.1893 | 22.1599 | 21.6007 | 21.7775 | 21.9013 | 21.0728 | 21.1983 | 21.6976 | 20.4764 | 21.1979 | 25.3066 | 21.909 | 22.209 | 29.1709 | 175.7423 | 155.3182 | 183.0238 | 22.1132 | 22.0985 | 26.9959 | 22.0285 | 22.2355 | 29.1019 | 80.8274 | 180.6667 |  | 117.9459 | 150.7496 | 149.3541 | 134.1451 |  | 17.8258 | 18.957 | 17.8033 | 18.9001 | 19.836 | 32.7368 | 131.0445 | 15.6745 | 17.2872 | 15.6375 | 18.9707 | 18.7821 | 46.1302 | 49.0065 | 44.9847 | 21.6758 |  |  | 0.47664 | -0.13346 | -31.3387 | 0.20103 | 0.29452 | -151.3537 | 15.7599 | 0.54702 | 0.033175 | 0.33726 | 0.45721 | 0.0003647 | 0.00038441 | 0.48228 | 21.903 | 21.959 | 22.1594 | 22.2155 | 22.0204 | 21.309 | 20.1224 | 22.1828 | 22.3642 | 22.3954 | 22.3418 | 21.9575 | 21.1865 | 22.276 | 92.5563 | 59.6055 | 59.2808 | 41.7842 | 35.5696 | 61.8885 | 39.8151 | 22.3166 | 22.0795 | 21.6406 | 22.0417 | 21.7766 | 21.5722 | 21.9435 | 21.8003 | 25.4946 | 69.829 | 179.3344 | 141.7642 | 100.4055 | 1.3621 | 0.4101 | 75.1329 | 21.8931 | 22.2141 | 20.8459 | 21.5642 | 22.0202 | 21.9866 | 22.6682 | 34.0968 | 21.8274 | 21.8789 | 26.7182 | 170.1334 | 209.7069 | 139.6075 | 140.6738 | 95.3089 |  | 70.7795 | 139.3188 | 76.648 | 118.0539 | 99.4163 | 81.7285 |  | 94.2102 |  |  | 25.1374 | 29.7084 | 69.2133 | [5 empty] | 21.8997 | 87.9079 | 21.7079 | 22.1107 | 36.4333 | 21.2929 | 21.9267 | 33.1943 | 117.9416 | 222.1948 |  | 101.4673 | 162.2914 | 25.6747 | 93.5884 | 175.4164 | 60.0512 | 137.2029 | 29.268 | 136.9755 | 29.3536 | 134.6543 | 19.114 | 102.2123 | 157.1343 | 35.6432 | 94.9656 | 191.0542 | 24.3646 | 97.147 | 172.6566 | 25.1129 | 122.1912 | 38.0021 | 133.2002 | 30.1832 | 142.6566 | 1.7534 | 18.6504 | 2.0373 | 0.074105 | -27.2416 | 3.0951 | 227.07 | 52.07 | 1.0276 | -0.43513 | -6.6677 | 0.53404 | 0.66146 | -14.9949 | 4.8386 | 0.11197 | -0.89196 | 0.57473 | -2.6931 | -1.6189 | -0.59085 | -0.064739
42838.4261 | 504 | 22.888 | 22.8508 | 22.8326 | 22.7571 | 22.3638 | 21.6944 | 22.6892 | 21.7471 | 22.3441 | 22.3505 | 22.3221 | 21.9672 | 21.1864 | 22.1609 | 21.6022 | 21.7748 | 21.9094 | 21.0809 | 21.2029 | 21.7217 | 20.4808 | 21.2106 | 25.3535 | 21.913 | 22.2264 | 29.2134 | 175.9262 | 155.681 | 184.0012 | 22.1152 | 22.1015 | 27.026 | 22.0331 | 22.2382 | 29.1377 | 81.0728 | 181.0704 |  | 118.1925 | 150.984 | 149.6707 | 134.4854 |  | 17.8086 | 18.9442 | 17.7907 | 18.8935 | 19.8266 | 32.7901 | 131.5986 | 15.6347 | 17.281 | 15.5809 | 18.9749 | 18.7889 | 46.1071 | 49.0197 | 44.9702 | 21.6863 |  |  | 0.81834 | -0.37857 | -31.0699 | 0.43694 | 0.53568 | -152.6923 | 15.915 | 0.82038 | 0.082604 | 0.1625 | 0.40218 | 0.00037291 | 0.00034334 | 0.48646 | 21.9088 | 21.9514 | 22.156 | 22.212 | 22.0191 | 21.3068 | 20.126 | 22.1839 | 22.3616 | 22.3947 | 22.3458 | 21.9638 | 21.1937 | 22.2706 | 92.4488 | 59.8476 | 56.803 | 40.4339 | 33.9888 | 62.0251 | 39.8649 | 22.3206 | 22.0869 | 21.6523 | 22.0492 | 21.7849 | 21.5862 | 21.9474 | 21.8012 | 25.5263 | 70.0233 | 179.6066 | 141.9202 | 100.9388 | 1.6133 | 0.68323 | 75.32 | 21.8851 | 22.2129 | 20.851 | 21.567 | 22.0175 | 21.9915 | 22.6737 | 34.1456 | 21.8217 | 21.8801 | 26.7474 | 170.4355 | 209.8791 | 139.7838 | 140.8725 | 95.5349 |  | 70.9734 | 140.7791 | 76.8518 | 117.5327 | 99.7989 | 82.267 |  | 94.3841 |  |  | 25.1375 | 29.7659 | 69.5153 | [5 empty] | 21.8885 | 87.6372 | 21.6985 | 22.0881 | 36.4648 | 21.282 | 21.918 | 33.2401 | 118.2945 | 223.0049 |  | 101.756 | 162.644 | 25.706 | 93.9061 | 176.2448 | 60.1693 | 137.4694 | 29.3298 | 137.0036 | 29.4108 | 135.0852 | 19.1301 | 102.4683 | 157.2083 | 35.6978 | 95.2012 | 191.4925 | 24.4023 | 97.6179 | 172.9848 | 25.1407 | 122.2361 | 38.0525 | 133.3802 | 30.2259 | 143.0494 | 1.7345 | 18.6664 | 2.0395 | 0.074011 | -27.169 | 3.095 | 219.52 | 51.4 | 1.3479 | -0.73282 | -6.6389 | 0.7873 | 0.89215 | -15.0624 | 4.8628 | 0.11287 | -0.92489 | 0.60433 | -2.6648 | -1.3377 | -0.59101 | -0.072374
42838.4261 | 505 | 22.8934 | 22.8526 | 22.8395 | 22.7566 | 22.3671 | 21.6855 | 22.6938 | 21.7536 | 22.3462 | 22.3474 | 22.3206 | 21.9693 | 21.1903 | 22.1594 | 21.5941 | 21.7734 | 21.902 | 21.0749 | 21.2104 | 21.708 | 20.4855 | 21.2163 | 25.3558 | 21.9146 | 22.218 | 29.2462 | 176.0518 | 156.0462 | 183.7685 | 22.1145 | 22.1055 | 27.0531 | 22.0375 | 22.2467 | 29.1787 | 81.2968 | 181.6857 |  | 118.5024 | 151.299 | 149.9644 | 133.9818 |  | 17.8201 | 18.9347 | 17.7928 | 18.8889 | 19.814 | 32.9224 | 132.0185 | 15.6237 | 17.2828 | 15.5414 | 18.9854 | 18.788 | 46.086 | 49.0089 | 44.9544 | 21.6737 |  |  | 0.67772 | -0.42522 | -31.0568 | 0.3042 | 0.3622 | -153.9526 | 16.0523 | 0.71721 | -0.11997 | 0.15557 | 0.38343 | 0.00033349 | 0.00036963 | 0.50405 | 21.9031 | 21.9657 | 22.1491 | 22.2198 | 22.0242 | 21.3106 | 20.1289 | 22.1857 | 22.3613 | 22.405 | 22.3502 | 21.9643 | 21.1852 | 22.2788 | 93.5464 | 58.808 | 59.3998 | 40.088 | 33.3436 | 62.1628 | 39.943 | 22.3143 | 22.0826 | 21.6508 | 22.0455 | 21.7746 | 21.5755 | 21.9341 | 21.7967 | 25.5434 | 70.2229 | 180.0259 | 142.1386 | 100.2886 | 2.0175 | 0.50216 | 75.5041 | 21.8942 | 22.2157 | 20.8568 | 21.5597 | 22.0183 | 21.9864 | 22.6861 | 34.1976 | 21.8191 | 21.8852 | 26.7751 | 170.6416 | 210.458 | 139.9658 | 141.0388 | 94.8214 |  | 71.1767 | 141.6514 | 77.0994 | 118.6517 | 100.2631 | 82.7066 |  | 94.5579 |  |  | 25.152 | 29.8271 | 69.2558 | [5 empty] | 21.9001 | 89.2097 | 21.7075 | 22.103 | 36.4996 | 21.2908 | 21.9363 | 33.2932 | 118.5612 | 223.8982 |  | 101.7457 | 162.9925 | 25.7465 | 94.0722 | 176.2455 | 60.3456 | 137.7068 | 29.3846 | 137.1891 | 29.4734 | 135.2678 | 19.1468 | 102.9915 | 157.3425 | 35.7703 | 95.4477 | 191.9409 | 24.4293 | 98.1253 | 173.4742 | 25.1918 | 122.405 | 38.1574 | 133.5712 | 30.2684 | 143.7356 | 1.7118 | 18.6445 | 2.0414 | 0.072087 | -27.1908 | 3.095 | 223.83 | 52.47 | 1.2263 | -0.77666 | -6.6374 | 0.6569 | 0.73376 | -15.1277 | 4.8848 | 0.14022 | -0.93983 | 0.59161 | -2.7703 | -1.617 | -0.56855 | -0.046941
42838.4261 | 506 | 22.8977 | 22.8544 | 22.8408 | 22.7585 | 22.3778 | 21.6942 | 22.6974 | 21.7534 | 22.3472 | 22.3479 | 22.3221 | 21.9739 | 21.1868 | 22.1623 | 21.59 | 21.7584 | 21.896 | 21.0729 | 21.1992 | 21.7059 | 20.4772 | 21.2094 | 25.3737 | 21.9047 | 22.2132 | 29.2758 | 176.4257 | 156.5194 | 185.7911 | 22.1131 | 22.103 | 27.0872 | 22.0405 | 22.2477 | 29.215 | 81.4869 | 182.0759 |  | 118.7729 | 151.6106 | 150.2927 | 132.5856 |  | 17.8383 | 18.9549 | 17.8064 | 18.8992 | 19.7998 | 32.9911 | 132.4892 | 15.6312 | 17.286 | 15.5405 | 18.9911 | 18.796 | 46.0809 | 49.0199 | 44.9406 | 21.6761 |  |  | 0.50555 | -0.28131 | -31.1645 | 0.2674 | 0.19464 | -154.5131 | 16.1049 | 1.1489 | 0.033759 | 0.059485 | 0.5046 | 0.0003762 | 0.00035813 | 0.48537 | 21.9004 | 21.9604 | 22.1637 | 22.2129 | 22.0211 | 21.3169 | 20.1252 | 22.184 | 22.3635 | 22.4022 | 22.3534 | 21.9632 | 21.1801 | 22.2819 | 93.7199 | 59.4189 | 58.9103 | 39.8567 | 33.8263 | 62.3237 | 40.0034 | 22.3124 | 22.0753 | 21.6543 | 22.0402 | 21.7743 | 21.5775 | 21.9377 | 21.7995 | 25.5665 | 70.4216 | 180.5778 | 142.5566 | 100.039 | 2.1905 | 1.6922 | 75.6491 | 21.8915 | 22.2107 | 20.8624 | 21.555 | 22.0155 | 21.9833 | 22.6895 | 34.2519 | 21.8178 | 21.8877 | 26.8013 | 171.0169 | 211.2806 | 140.196 | 141.2309 | 95.1005 |  | 71.4394 | 141.797 | 77.372 | 120.0599 | 100.7869 | 83.0383 |  | 94.7669 |  |  | 25.1678 | 29.868 | 69.2734 | [5 empty] | 21.8826 | 89.3808 | 21.689 | 22.0874 | 36.4995 | 21.2815 | 21.9156 | 33.3751 | 118.8729 | 224.4567 |  | 101.7626 | 163.1075 | 25.7875 | 94.2374 | 175.9846 | 60.5396 | 137.9551 | 29.4612 | 137.4256 | 29.5248 | 135.7299 | 19.184 | 103.4196 | 157.6481 | 35.8619 | 95.6666 | 192.6472 | 24.4669 | 98.3857 | 174.316 | 25.2464 | 122.5877 | 38.2858 | 133.7696 | 30.2952 | 144.2193 | 1.3778 | 18.6437 | 2.0435 | 0.071463 | -27.2271 | 3.0951 | 218.85 | 51.7 | 1.0615 | -0.63173 | -6.6492 | 0.61591 | 0.53795 | -15.1569 | 4.8934 | 0.1422 | -0.93364 | 0.57324 | -2.7703 | -1.5555 | -0.52256 | -0.03266
42838.4261 | 507 | 22.8992 | 22.8571 | 22.8399 | 22.7623 | 22.3787 | 21.7003 | 22.6961 | 21.7559 | 22.3456 | 22.3496 | 22.3326 | 21.9803 | 21.1941 | 22.1691 | 21.6052 | 21.7761 | 21.91 | 21.0847 | 21.2047 | 21.7172 | 20.4832 | 21.2288 | 25.4098 | 21.9156 | 22.2342 | 29.3236 | 176.7782 | 157.0822 | 186.8114 | 22.1039 | 22.1093 | 27.1028 | 22.0285 | 22.2392 | 29.2402 | 81.6606 | 182.3011 |  | 119.0169 | 151.8511 | 150.6131 | 131.2019 |  | 17.8523 | 18.9785 | 17.8321 | 18.9234 | 19.8051 | 32.8815 | 132.9304 | 15.6827 | 17.2879 | 15.5455 | 18.9972 | 18.7857 | 46.1023 | 49.0325 | 44.9229 | 21.6751 |  |  | 0.61398 | -0.13609 | -31.2342 | 0.5861 | 0.19464 | -151.2815 | 16.0753 | 0.81906 | 0.049133 | 0.038085 | 0.57091 | 0.00039098 | 0.00037949 | 0.43337 | 21.9088 | 21.9618 | 22.1594 | 22.218 | 22.0246 | 21.3146 | 20.1228 | 22.1804 | 22.3624 | 22.4003 | 22.3474 | 21.9638 | 21.1878 | 22.2788 | 95.4494 | 63.4912 | 64.1021 | 40.6148 | 33.5498 | 62.5137 | 40.1409 | 22.3209 | 22.0873 | 21.66 | 22.0529 | 21.7868 | 21.5945 | 21.9503 | 21.8086 | 25.6013 | 70.6489 | 181.0132 | 142.817 | 100.8344 | 1.6342 | 1.0912 | 75.6685 | 21.8897 | 22.2098 | 20.8758 | 21.5596 | 22.017 | 21.9906 | 22.6956 | 34.3093 | 21.8244 | 21.8964 | 26.8339 | 171.4391 | 212.052 | 140.425 | 141.4433 | 95.2059 |  | 71.627 | 142.2997 | 77.5517 | 119.5417 | 101.1254 | 82.6935 |  | 94.9514 |  |  | 25.2221 | 29.9145 | 68.8269 | [5 empty] | 21.8921 | 88.9191 | 21.7009 | 22.0997 | 36.5849 | 21.2881 | 21.9216 | 33.4657 | 119.2266 | 225.6421 |  | 101.823 | 163.1315 | 25.8136 | 94.3751 | 175.9797 | 60.8051 | 138.2438 | 29.5389 | 137.6169 | 29.5654 | 135.9879 | 19.2276 | 103.7034 | 157.9225 | 35.9888 | 95.9215 | 193.2854 | 24.4978 | 98.6051 | 174.7852 | 25.3042 | 122.7966 | 38.4387 | 133.8733 | 30.3432 | 144.3629 | 1.5876 | 18.6568 | 2.0471 | 0.071644 | -27.1385 | 3.0951 | 224.8 | 52.34 | 1.1711 | -0.43941 | -6.6569 | 0.91189 | 0.53785 | -14.9949 | 4.888 | 0.14622 | -0.94086 | 0.60106 | -2.9397 | -2.1161 | -0.47754 | -0.046347
42838.4262 | 508 | 22.8868 | 22.8545 | 22.8424 | 22.7557 | 22.3739 | 21.6973 | 22.6926 | 21.7518 | 22.3419 | 22.3434 | 22.321 | 21.9706 | 21.1861 | 22.1612 | 21.6034 | 21.7759 | 21.9052 | 21.0817 | 21.2044 | 21.7168 | 20.4824 | 21.2252 | 25.4365 | 21.9086 | 22.2387 | 29.3536 | 176.918 | 157.4964 | 185.9253 | 22.1105 | 22.1105 | 27.1363 | 22.03 | 22.2503 | 29.2768 | 81.8702 | 183.5604 |  | 119.3074 | 152.1223 | 151.0205 | 130.7734 |  | 17.8573 | 18.9825 | 17.8357 | 18.9391 | 19.8067 | 32.7737 | 133.3595 | 15.6864 | 17.2916 | 15.5538 | 19.0012 | 18.7933 | 46.1174 | 49.0425 | 44.9035 | 21.6696 |  |  | 0.73751 | -0.28788 | -31.7375 | 0.29106 | 0.17295 | -154.362 | 15.0995 | 0.77898 | -0.041162 | 0.27159 | 0.4303 | 0.00037291 | 0.0003647 | 0.36883 | 21.9046 | 21.9634 | 22.1576 | 22.214 | 22.0216 | 21.313 | 20.1248 | 22.1804 | 22.3618 | 22.401 | 22.3528 | 21.9652 | 21.1863 | 22.2802 | 95.6337 | 64.6297 | 65.9984 | 42.4706 | 35.0273 | 62.6815 | 40.2651 | 22.3188 | 22.0898 | 21.6652 | 22.0491 | 21.7868 | 21.6005 | 21.9458 | 21.8125 | 25.6312 | 70.8669 | 181.5498 | 143.042 | 101.6301 | 1.8213 | 0.98527 | 75.8748 | 21.8927 | 22.213 | 20.8908 | 21.5568 | 22.0222 | 21.9969 | 22.7066 | 34.3673 | 21.8294 | 21.901 | 26.8626 | 171.7271 | 212.6053 | 140.6984 | 141.6777 | 94.3794 |  | 71.8395 | 142.8634 | 77.7422 | 120.0262 | 101.4889 | 82.395 |  | 95.1081 |  |  | 25.272 | 29.9916 | 69.0392 | [5 empty] | 21.8944 | 88.8261 | 21.6974 | 22.0906 | 36.6618 | 21.2831 | 21.9115 | 33.5833 | 119.5465 | 227.4981 |  | 101.8393 | 163.2884 | 25.853 | 94.6224 | 176.0437 | 61.024 | 138.5823 | 29.6025 | 137.7402 | 29.6284 | 136.515 | 19.2579 | 103.8605 | 158.0106 | 36.121 | 96.1129 | 194.0227 | 24.5582 | 98.7077 | 174.8809 | 25.3682 | 123.0184 | 38.5951 | 134.2214 | 30.4043 | 144.5635 | 1.9228 | 18.6355 | 2.0507 | 0.071782 | -27.1592 | 3.0951 | 235.31 | 51.58 | 1.2823 | -0.63909 | -6.7103 | 0.64261 | 0.50692 | -15.1441 | 4.7365 | 0.17706 | -0.94936 | 0.60202 | -2.9401 | -2.3122 | -0.45769 | -0.060384
42838.4262 | 509 | 22.8882 | 22.8541 | 22.8405 | 22.7571 | 22.3644 | 21.6892 | 22.6895 | 21.7492 | 22.3387 | 22.3409 | 22.3112 | 21.9723 | 21.1803 | 22.1592 | 21.6034 | 21.7746 | 21.9073 | 21.0816 | 21.2069 | 21.7171 | 20.4858 | 21.2335 | 25.4619 | 21.9131 | 22.234 | 29.3879 | 177.0159 | 158.0146 | 186.2203 | 22.1198 | 22.1114 | 27.1652 | 22.028 | 22.2578 | 29.3231 | 82.0653 | 184.4441 |  | 119.6149 | 152.4294 | 151.399 | 131.8354 |  | 17.8665 | 18.9997 | 17.8566 | 18.9523 | 19.8313 | 32.8077 | 133.8373 | 15.6635 | 17.2914 | 15.5477 | 19.0157 | 18.7908 | 46.1159 | 49.0441 | 44.8871 | 21.6703 |  |  | 0.77957 | -0.14332 | -31.9767 | 0.46914 | 0.38849 | -152.3407 | 15.384 | 0.84272 | 0.11257 | 0.060114 | 0.51206 | 0.00036963 | 0.00036306 | 0.34737 | 21.9058 | 21.9592 | 22.1563 | 22.2112 | 22.0161 | 21.3078 | 20.1244 | 22.1735 | 22.3563 | 22.397 | 22.3476 | 21.9575 | 21.1858 | 22.2777 | 95.0843 | 63.5454 | 64.5647 | 43.1843 | 36.2364 | 62.82 | 40.3625 | 22.3202 | 22.0853 | 21.6534 | 22.0479 | 21.7845 | 21.6027 | 21.9437 | 21.8145 | 25.6526 | 71.0774 | 181.7749 | 143.303 | 102.1491 | 1.4798 | 0.8449 | 76.4501 | 21.8807 | 22.2053 | 20.8924 | 21.5542 | 22.0087 | 21.9894 | 22.7069 | 34.4129 | 21.8173 | 21.8953 | 26.8861 | 172.1121 | 213.2287 | 141.0276 | 141.9906 | 95.3523 |  | 72.1168 | 142.6735 | 77.995 | 121.5398 | 102.0994 | 82.1448 |  | 95.3284 |  |  | 25.3132 | 30.1312 | 70.1006 | [5 empty] | 21.896 | 89.9015 | 21.7013 | 22.098 | 36.789 | 21.2918 | 21.9197 | 33.7188 | 119.8871 | 228.5323 |  | 101.9958 | 163.5561 | 25.9062 | 94.8891 | 176.671 | 61.2371 | 138.9471 | 29.6393 | 138.0074 | 29.7035 | 136.9774 | 19.2717 | 103.9671 | 158.1022 | 36.2595 | 96.3354 | 194.4367 | 24.5949 | 98.9672 | 175.1716 | 25.4301 | 123.3269 | 38.7687 | 134.8225 | 30.4644 | 144.928 | 1.7699 | 18.631 | 2.0541 | 0.073314 | -27.1688 | 3.095 | 248.23 | 51.35 | 1.3188 | -0.45094 | -6.7358 | 0.81587 | 0.75978 | -15.0455 | 4.7811 | 0.16032 | -0.93458 | 0.58424 | -2.8625 | -2.1414 | -0.47979 | -0.06701
42838.4262 | 510 | 22.8892 | 22.8641 | 22.8412 | 22.7598 | 22.361 | 21.6954 | 22.6924 | 21.7513 | 22.3487 | 22.3414 | 22.3261 | 21.9732 | 21.1846 | 22.1553 | 21.6017 | 21.7748 | 21.9074 | 21.0846 | 21.2045 | 21.7206 | 20.4835 | 21.2433 | 25.4862 | 21.9125 | 22.242 | 29.4251 | 177.3519 | 158.5111 | 187.6625 | 22.1173 | 22.115 | 27.1834 | 22.0277 | 22.2497 | 29.3553 | 82.2569 | 187.0484 |  | 119.9468 | 152.7519 | 151.7055 | 132.2761 |  | 17.8714 | 18.9904 | 17.8581 | 18.9562 | 19.8509 | 32.7967 | 134.1081 | 15.6513 | 17.2911 | 15.5519 | 19.0139 | 18.8111 | 46.1119 | 49.0548 | 44.8699 | 21.68 |  |  | 1.091 | 0.030819 | -32.2415 | 0.48162 | 0.27546 | -150.9726 | 15.6344 | 0.9426 | 0.25113 | 0.25712 | 0.5138 | 0.00034499 | 0.00035156 | 0.36979 | 21.9135 | 21.9621 | 22.1593 | 22.2105 | 22.0232 | 21.3114 | 20.1239 | 22.1868 | 22.3604 | 22.397 | 22.3493 | 21.9629 | 21.194 | 22.2791 | 94.192 | 62.2756 | 62.1252 | 43.0739 | 36.1878 | 62.9599 | 40.4331 | 22.3242 | 22.0803 | 21.659 | 22.0545 | 21.7887 | 21.5975 | 21.9403 | 21.8149 | 25.6813 | 71.295 | 181.8315 | 143.5319 | 102.4933 | 1.2712 | 1.0011 | 76.8471 | 21.8784 | 22.2024 | 20.8948 | 21.5554 | 22.0028 | 21.9847 | 22.7139 | 34.4695 | 21.8116 | 21.8933 | 26.9172 | 172.4696 | 213.9628 | 141.3876 | 142.3126 | 95.3641 |  | 72.3098 | 142.1229 | 78.1903 | 122.0856 | 102.5859 | 82.2193 |  | 95.5425 |  |  | 25.3445 | 30.2297 | 69.8619 | [5 empty] | 21.8915 | 90.7079 | 21.7029 | 22.0967 | 36.8649 | 21.2935 | 21.9242 | 33.8711 | 120.2877 | 230.1023 |  | 102.1462 | 163.9903 | 25.9461 | 95.0887 | 177.7051 | 61.487 | 139.3518 | 29.6693 | 138.185 | 29.7635 | 137.1266 | 19.28 | 104.2342 | 158.2473 | 36.4105 | 96.626 | 194.9933 | 24.6191 | 99.3171 | 175.5398 | 25.4901 | 123.7484 | 38.9496 | 135.319 | 30.518 | 145.2776 | 2.3663 | 18.6377 | 2.0575 | 0.074504 | -27.1949 | 3.095 | 256.27 | 52.96 | 1.5626 | 0.20911 | -6.7635 | 0.82664 | 0.63977 | -14.9775 | 4.8198 | 0.16716 | -0.91194 | 0.58843 | -2.7466 | -1.862 | -0.48476 | -0.068511
42838.4262 | 511 | 22.88 | 22.8569 | 22.8334 | 22.754 | 22.3588 | 21.6857 | 22.6833 | 21.7494 | 22.3415 | 22.3417 | 22.3175 | 21.9629 | 21.1752 | 22.1494 | 21.5962 | 21.7667 | 21.9026 | 21.0786 | 21.2068 | 21.7296 | 20.4812 | 21.2462 | 25.5054 | 21.9121 | 22.2505 | 29.4557 | 178.3681 | 158.995 | 191.1919 | 22.1214 | 22.1245 | 27.2211 | 22.0331 | 22.2598 | 29.4007 | 82.4634 | 191.853 |  | 120.365 | 153.1081 | 152.0087 | 132.932 |  | 17.8711 | 18.9884 | 17.8515 | 18.9611 | 19.8635 | 32.8093 | 134.4072 | 15.6557 | 17.2988 | 15.6303 | 19.0227 | 18.8108 | 46.0931 | 49.0554 | 44.8411 | 21.6709 |  |  | 0.70203 | 0.090615 | -32.551 | 0.32654 | 0.36812 | -154.9567 | 15.3971 | 1.0767 | 0.010796 | 0.23425 | 0.44002 | 0.00035977 | 0.00034334 | 0.42162 | 21.919 | 21.967 | 22.1622 | 22.2184 | 22.0304 | 21.321 | 20.1333 | 22.1902 | 22.3662 | 22.3971 | 22.3529 | 21.9694 | 21.1907 | 22.2841 | 92.1166 | 59.2185 | 61.0901 | 43.598 | 36.6432 | 63.0533 | 40.5285 | 22.3129 | 22.0755 | 21.6497 | 22.0462 | 21.7843 | 21.5935 | 21.944 | 21.8141 | 25.7011 | 71.5012 | 181.8987 | 143.7397 | 102.5125 | 1.4663 | 0.67448 | 77.1137 | 21.895 | 22.212 | 20.912 | 21.563 | 22.0164 | 21.9944 | 22.7302 | 34.531 | 21.8243 | 21.9123 | 26.9515 | 173.0049 | 214.4254 | 141.7124 | 142.5686 | 96.0239 |  | 72.4984 | 142.8647 | 78.3805 | 123.0849 | 103.0422 | 82.6111 |  | 95.7493 |  |  | 25.4009 | 30.3264 | 69.5953 | [5 empty] | 21.8932 | 91.0623 | 21.7036 | 22.0999 | 36.8608 | 21.2922 | 21.9288 | 34.0318 | 120.7369 | 232.7174 |  | 102.3219 | 164.4942 | 25.9919 | 95.2222 | 178.7485 | 61.816 | 139.8101 | 29.7089 | 138.3318 | 29.8364 | 137.2672 | 19.3159 | 104.6714 | 158.4223 | 36.5655 | 96.9796 | 195.2151 | 24.6819 | 99.6157 | 175.9301 | 25.5635 | 124.1096 | 39.1016 | 135.8595 | 30.588 | 145.7408 | 1.981 | 18.6302 | 2.0603 | 0.073982 | -27.1567 | 3.0951 | 276.43 | 51.36 | 1.2582 | 0.35856 | -6.7958 | 0.68066 | 0.73959 | -15.1741 | 4.7832 | 0.15583 | -0.92539 | 0.57885 | -2.5048 | -1.7357 | -0.49514 | -0.061406
42838.4262 | 512 | 22.8878 | 22.8539 | 22.8419 | 22.7541 | 22.3653 | 21.6911 | 22.6898 | 21.7523 | 22.3435 | 22.3471 | 22.3215 | 21.967 | 21.1859 | 22.1607 | 21.6014 | 21.7747 | 21.905 | 21.0797 | 21.2107 | 21.7307 | 20.4796 | 21.2479 | 25.5341 | 21.9138 | 22.256 | 29.4965 | 179.4667 | 159.2902 | 193.6838 | 22.1147 | 22.1205 | 27.2462 | 22.0313 | 22.2658 | 29.4382 | 82.6597 | 194.3507 |  | 120.7604 | 153.543 | 152.2835 | 132.753 |  | 17.8715 | 18.9964 | 17.8539 | 18.9432 | 19.8671 | 32.8351 | 134.8775 | 15.6823 | 17.297 | 15.6832 | 19.0445 | 18.82 | 46.0901 | 49.0704 | 44.8286 | 21.6728 |  |  | 0.85908 | -0.19391 | -32.093 | 0.087354 | 0.13812 | -156.1435 | 15.2342 | 0.91434 | 0.20754 | 0.40628 | 0.51554 | 0.00036634 | 0.00035977 | 0.41058 | 21.9114 | 21.9682 | 22.161 | 22.2219 | 22.0193 | 21.32 | 20.1295 | 22.1885 | 22.3622 | 22.396 | 22.3479 | 21.9623 | 21.1912 | 22.2688 | 91.3623 | 59.4317 | 60.2927 | 42.8169 | 36.8777 | 63.1571 | 40.5758 | 22.3126 | 22.085 | 21.6493 | 22.0406 | 21.7716 | 21.5983 | 21.9299 | 21.81 | 25.7186 | 71.7234 | 181.5523 | 143.9417 | 103.1792 | 1.2797 | 1.0267 | 77.2347 | 21.8961 | 22.2106 | 20.9134 | 21.561 | 22.0178 | 21.9989 | 22.7327 | 34.5844 | 21.8276 | 21.912 | 26.9776 | 173.7403 | 215.148 | 142.019 | 142.8034 | 97.2254 |  | 72.7345 | 144.2208 | 78.6289 | 123.2504 | 103.4833 | 82.722 |  | 95.9809 |  |  | 25.4722 | 30.3998 | 70.4714 | [5 empty] | 21.8935 | 91.5067 | 21.7059 | 22.1066 | 36.8608 | 21.2916 | 21.9269 | 34.2084 | 121.2154 | 234.8035 |  | 102.6261 | 164.9272 | 26.0398 | 95.5551 | 179.8375 | 62.1153 | 140.5978 | 29.7553 | 138.6813 | 29.9303 | 137.4607 | 19.3441 | 105.2983 | 158.7794 | 36.7084 | 97.3049 | 195.3858 | 24.7394 | 100.0363 | 176.3468 | 25.6248 | 124.3401 | 39.2533 | 136.4176 | 30.6583 | 146.231 | 1.7319 | 18.6244 | 2.0636 | 0.073757 | -27.1803 | 3.0951 | 266.91 | 52.53 | 1.3956 | -0.52453 | -6.748 | 0.35205 | 0.45306 | -15.2328 | 4.758 | 0.13123 | -0.95371 | 0.59184 | -2.4086 | -1.6415 | -0.48271 | -0.071687
42838.4262 | 513 | 22.8945 | 22.8519 | 22.8446 | 22.7624 | 22.3699 | 21.702 | 22.6907 | 21.7562 | 22.3479 | 22.3526 | 22.3237 | 21.9747 | 21.1839 | 22.1641 | 21.6013 | 21.7746 | 21.9039 | 21.0838 | 21.2091 | 21.7236 | 20.4797 | 21.2549 | 25.5655 | 21.9204 | 22.257 | 29.5388 | 180.1383 | 159.4411 | 193.7728 | 22.1144 | 22.1291 | 27.2799 | 22.0352 | 22.2724 | 29.4768 | 82.8575 | 199.0831 |  | 121.183 | 154.1238 | 152.6188 | 132.1725 |  | 17.8813 | 19.0136 | 17.865 | 18.9399 | 19.88 | 32.8515 | 135.3464 | 15.706 | 17.3044 | 15.7435 | 19.0487 | 18.8238 | 46.0836 | 49.071 | 44.8172 | 21.6794 |  |  | 0.88602 | -0.54613 | -32.2987 | 0.04201 | 0.32606 | -153.3869 | 15.225 | 0.79672 | 0.16453 | 0.21432 | 0.37127 | 0.00035977 | 0.00034006 | 0.33537 | 21.9121 | 21.9589 | 22.158 | 22.2088 | 22.0184 | 21.3149 | 20.1206 | 22.1755 | 22.3541 | 22.3941 | 22.3489 | 21.9629 | 21.1807 | 22.2724 | 93.0071 | 60.5037 | 58.9782 | 42.2135 | 37.0187 | 63.3228 | 40.6525 | 22.3171 | 22.0794 | 21.6611 | 22.0468 | 21.7845 | 21.6056 | 21.9375 | 21.8164 | 25.7518 | 71.9572 | 181.0553 | 144.1909 | 103.9212 | 1.0685 | 0.67334 | 77.2661 | 21.8914 | 22.2057 | 20.919 | 21.5598 | 22.0147 | 21.9964 | 22.7373 | 34.6372 | 21.8232 | 21.9065 | 26.9999 | 174.5618 | 216.5164 | 142.3588 | 143.1812 | 98.3283 |  | 73.0025 | 144.5889 | 78.8674 | 121.755 | 103.9092 | 83.3598 |  | 96.3223 |  |  | 25.5316 | 30.5159 | 71.0811 | [5 empty] | 21.8926 | 91.0842 | 21.6993 | 22.1 | 36.9574 | 21.2911 | 21.9209 | 34.3607 | 121.6974 | 237.3716 |  | 102.9741 | 165.4436 | 26.0792 | 96.0826 | 181.1697 | 62.3595 | 141.5899 | 29.8218 | 139.0546 | 30.008 | 137.8044 | 19.3842 | 105.8584 | 159.4228 | 36.8513 | 97.568 | 195.9183 | 24.8055 | 100.3789 | 177.0137 | 25.6867 | 124.5071 | 39.4072 | 136.7572 | 30.7295 | 146.5322 | 1.5961 | 18.6251 | 2.0665 | 0.073249 | -27.0869 | 3.095 | 270.67 | 51.99 | 1.4175 | -0.88029 | -6.7697 | 0.24415 | 0.69611 | -15.0981 | 4.7567 | 0.11056 | -0.95496 | 0.65038 | -2.5715 | -1.4864 | -0.45907 | -0.083622
42838.4262 | 514 | 22.8899 | 22.854 | 22.8383 | 22.7517 | 22.3683 | 21.6993 | 22.6876 | 21.7489 | 22.3382 | 22.3492 | 22.3183 | 21.9762 | 21.1881 | 22.1548 | 21.598 | 21.7644 | 21.8962 | 21.0773 | 21.2034 | 21.7225 | 20.475 | 21.2568 | 25.5892 | 21.9147 | 22.2608 | 29.5674 | 180.7373 | 159.7336 | 193.6359 | 22.1111 | 22.1271 | 27.3109 | 22.0395 | 22.2739 | 29.5111 | 83.0363 | 202.8024 |  | 121.6307 | 154.7285 | 153.1339 | 133.3261 |  | 17.8735 | 19.018 | 17.862 | 18.9411 | 19.8617 | 33.0399 | 135.794 | 15.6678 | 17.2986 | 15.7968 | 19.0425 | 18.8295 | 46.0692 | 49.0824 | 44.7967 | 21.6775 |  |  | 0.85974 | -0.39893 | -32.2277 | 0.14781 | 0.43383 | -152.5503 | 15.1862 | 0.89594 | -0.0001012 | 0.26824 | 0.50807 | 0.00035977 | 0.0003302 | 0.30085 | 21.9113 | 21.9563 | 22.1552 | 22.2134 | 22.0138 | 21.3071 | 20.1232 | 22.1767 | 22.3606 | 22.3988 | 22.3399 | 21.9645 | 21.1849 | 22.2689 | 92.0552 | 60.0348 | 57.266 | 41.4533 | 36.4486 | 63.4333 | 40.6944 | 22.316 | 22.0807 | 21.6526 | 22.0557 | 21.7739 | 21.6028 | 21.9363 | 21.8204 | 25.7776 | 72.1659 | 181.0165 | 144.458 | 103.9944 | 1.6859 | 0.45023 | 77.1047 | 21.8937 | 22.2139 | 20.9288 | 21.565 | 22.0195 | 21.9948 | 22.7385 | 34.6895 | 21.8247 | 21.919 | 27.0306 | 175.4163 | 218.1581 | 142.7135 | 143.6199 | 97.6816 |  | 73.2012 | 144.7232 | 79.071 | 123.3004 | 104.3724 | 83.9443 |  | 96.5912 |  |  | 25.5723 | 30.7123 | 70.5093 | [5 empty] | 21.894 | 90.9507 | 21.7 | 22.0988 | 37.0469 | 21.295 | 21.9211 | 34.4929 | 122.1992 | 240.2295 |  | 103.3411 | 166.1197 | 26.114 | 96.6053 | 183.0945 | 62.656 | 142.4503 | 29.901 | 139.4524 | 30.0681 | 138.1795 | 19.4134 | 106.3066 | 160.2167 | 36.9996 | 97.7704 | 196.174 | 24.8756 | 100.7207 | 178.077 | 25.7399 | 124.6576 | 39.5531 | 136.8809 | 30.8191 | 146.7109 | 1.5404 | 18.6255 | 2.0677 | 0.073038 | -27.1246 | 3.095 | 261.05 | 51.94 | 1.3961 | -0.75237 | -6.7624 | 0.45796 | 0.8032 | -15.0615 | 4.7521 | 0.13591 | -0.95101 | 0.62596 | -2.4525 | -1.2912 | -0.48432 | -0.077911
42838.4262 | 515 | 22.8924 | 22.8596 | 22.8437 | 22.7553 | 22.3684 | 21.6946 | 22.688 | 21.7563 | 22.3501 | 22.35 | 22.3172 | 21.9761 | 21.1887 | 22.1611 | 21.6016 | 21.7701 | 21.9051 | 21.0764 | 21.2051 | 21.7354 | 20.4807 | 21.2526 | 25.6187 | 21.9187 | 22.2675 | 29.6039 | 181.3914 | 160.1739 | 194.2825 | 22.1124 | 22.1315 | 27.3331 | 22.0384 | 22.2834 | 29.5528 | 83.2632 | 206.3909 |  | 122.0897 | 155.4368 | 153.49 | 135.8274 |  | 17.8745 | 19.0431 | 17.8734 | 18.9587 | 19.8696 | 33.3732 | 136.2439 | 15.691 | 17.3018 | 15.7972 | 19.0512 | 18.8292 | 46.0477 | 49.0877 | 44.7852 | 21.6735 |  |  | 0.89194 | -0.27145 | -31.7237 | 0.59005 | 0.082928 | -154.6446 | 15.4037 | 0.86638 | 0.085717 | 0.2653 | 0.52526 | 0.00035484 | 0.0003762 | 0.30169 | 21.9132 | 21.954 | 22.1573 | 22.2114 | 22.0141 | 21.3055 | 20.1209 | 22.1807 | 22.3576 | 22.3958 | 22.3397 | 21.9546 | 21.1876 | 22.2714 | 92.6283 | 58.5515 | 54.7188 | 40.8986 | 35.9224 | 63.5716 | 40.7188 | 22.3211 | 22.085 | 21.6598 | 22.0501 | 21.7825 | 21.6115 | 21.944 | 21.8226 | 25.8105 | 72.3833 | 181.2581 | 144.7442 | 104.1819 | 1.5972 | 0.97785 | 77.0934 | 21.8892 | 22.2097 | 20.9331 | 21.5658 | 22.0186 | 21.9954 | 22.7455 | 34.7441 | 21.8252 | 21.9145 | 27.0574 | 176.2814 | 219.248 | 143.0164 | 144.0045 | 97.1491 |  | 73.3999 | 145.6 | 79.2691 | 122.5173 | 104.7869 | 83.7718 |  | 96.8611 |  |  | 25.5912 | 30.8747 | 70.1702 | [5 empty] | 21.9034 | 90.6642 | 21.7099 | 22.1023 | 37.0897 | 21.294 | 21.9283 | 34.6352 | 122.75 | 242.6185 |  | 103.7246 | 166.8379 | 26.1409 | 96.8484 | 184.7403 | 63.0256 | 142.9676 | 29.9499 | 139.7273 | 30.1183 | 138.4541 | 19.4204 | 106.6458 | 160.8739 | 37.1606 | 97.9716 | 196.8169 | 24.9178 | 100.9192 | 179.3384 | 25.7856 | 124.8286 | 39.6861 | 137.2546 | 30.879 | 146.8511 | 1.8293 | 18.6185 | 2.0701 | 0.072748 | -27.2314 | 3.095 | 279.2 | 52.55 | 1.423 | -0.62065 | -6.7096 | 0.91505 | 0.35136 | -15.1728 | 4.7886 | 0.1581 | -0.9679 | 0.6643 | -2.4996 | -1.0053 | -0.54517 | -0.07505
42838.4262 | 516 | 22.8909 | 22.861 | 22.8437 | 22.7674 | 22.364 | 21.6962 | 22.6912 | 21.7547 | 22.3443 | 22.345 | 22.3163 | 21.9699 | 21.1893 | 22.1578 | 21.5917 | 21.772 | 21.8983 | 21.0751 | 21.2038 | 21.7377 | 20.4851 | 21.2617 | 25.6417 | 21.9121 | 22.2693 | 29.64 | 182.0057 | 160.6218 | 195.9388 | 22.1177 | 22.1357 | 27.3672 | 22.0354 | 22.2866 | 29.5964 | 83.5043 | 206.0544 |  | 122.5139 | 156.1591 | 153.943 | 137.9135 |  | 17.8803 | 19.0681 | 17.8825 | 19.0006 | 19.8837 | 33.3922 | 136.5884 | 15.6963 | 17.3116 | 15.8252 | 19.0607 | 18.8402 | 46.0289 | 49.0982 | 44.783 | 21.6735 |  |  | 0.69875 | -0.42522 | -31.5437 | 0.318 | 0.40294 | -151.3419 | 16.074 | 1.0031 | 0.22739 | 0.28964 | 0.38846 | 0.0003877 | 0.00038113 | 0.31492 | 21.9208 | 21.961 | 22.1551 | 22.209 | 22.0141 | 21.3091 | 20.1218 | 22.1789 | 22.362 | 22.3927 | 22.3385 | 21.9584 | 21.1899 | 22.268 | 92.5854 | 58.814 | 57.3539 | 40.1806 | 34.6257 | 63.6939 | 40.787 | 22.3169 | 22.0881 | 21.6623 | 22.052 | 21.7865 | 21.6161 | 21.9451 | 21.8311 | 25.8308 | 72.6031 | 181.3766 | 145.0061 | 104.353 | 1.1541 | 0.76292 | 77.1603 | 21.8935 | 22.2137 | 20.9395 | 21.5592 | 22.0191 | 21.9985 | 22.7592 | 34.7947 | 21.8239 | 21.9146 | 27.0919 | 177.254 | 220.4603 | 143.4337 | 144.4225 | 97.3922 |  | 73.6675 | 145.5479 | 79.5018 | 126.1254 | 105.3347 | 84.0466 |  | 97.1415 |  |  | 25.6007 | 30.9255 | 70.4885 | [5 empty] | 21.8944 | 91.1326 | 21.7108 | 22.101 | 37.1459 | 21.2924 | 21.9217 | 34.814 | 123.2898 | 243.8322 |  | 104.1532 | 167.3566 | 26.1803 | 96.9514 | 185.6745 | 63.4669 | 143.3509 | 29.9782 | 139.9399 | 30.1764 | 138.7163 | 19.4275 | 107.0289 | 161.8173 | 37.3279 | 98.1904 | 197.4672 | 24.9382 | 101.0672 | 180.6187 | 25.8298 | 125.1746 | 39.7946 | 137.7341 | 30.9416 | 147.0897 | 1.5202 | 18.6175 | 2.074 | 0.073357 | -27.1855 | 3.095 | 293.35 | 51.31 | 1.2617 | -0.77683 | -6.6908 | 0.67179 | 0.77452 | -15.0104 | 4.8919 | 0.16131 | -0.95768 | 0.58601 | -2.4802 | -1.29 | -0.59394 | -0.071638
42838.4263 | 517 | 22.8924 | 22.852 | 22.8438 | 22.7612 | 22.37 | 21.6939 | 22.6945 | 21.7543 | 22.3432 | 22.3455 | 22.3198 | 21.974 | 21.1873 | 22.1541 | 21.5997 | 21.7707 | 21.8959 | 21.0787 | 21.2054 | 21.7422 | 20.4865 | 21.2784 | 25.6682 | 21.9153 | 22.2655 | 29.6766 | 182.3699 | 160.9527 | 194.0264 | 22.1121 | 22.1289 | 27.3942 | 22.0236 | 22.2781 | 29.6188 | 83.7161 | 206.58 |  | 122.936 | 156.646 | 154.3546 | 138.7614 |  | 17.8877 | 19.0916 | 17.8949 | 19.0339 | 19.9171 | 33.385 | 137.0909 | 15.6658 | 17.3136 | 15.8591 | 19.0715 | 18.8453 | 46.018 | 49.1037 | 44.7908 | 21.6804 |  |  | 0.96816 | -0.33059 | -31.4484 | 0.53551 | 0.32409 | -152.0233 | 15.2762 | 0.90974 | 0.2595 | 0.11131 | 0.43776 | 0.00035977 | 0.00037127 | 0.32696 | 21.9166 | 21.9588 | 22.1487 | 22.2071 | 22.019 | 21.301 | 20.1167 | 22.1738 | 22.356 | 22.3939 | 22.3408 | 21.9523 | 21.1838 | 22.2609 | 91.0607 | 55.7446 | 55.6182 | 40.2846 | 34.8106 | 63.7964 | 40.8399 | 22.3129 | 22.0785 | 21.6552 | 22.0529 | 21.779 | 21.6173 | 21.9434 | 21.8263 | 25.8522 | 72.8295 | 181.0404 | 145.2643 | 104.9894 | 1.1812 | 0.30911 | 77.0565 | 21.8869 | 22.214 | 20.9442 | 21.5555 | 22.0214 | 21.9963 | 22.7715 | 34.8495 | 21.8196 | 21.9227 | 27.1149 | 177.8952 | 221.6255 | 144.1211 | 145.0657 | 98.1671 |  | 73.9078 | 145.1628 | 79.6749 | 129.0991 | 105.8086 | 84.6005 |  | 97.403 |  |  | 25.6413 | 30.9445 | 70.9096 | [5 empty] | 21.8968 | 92.8055 | 21.6978 | 22.0957 | 37.1898 | 21.2876 | 21.9178 | 35.0018 | 123.6793 | 245.2224 |  | 104.6555 | 168.3371 | 26.2392 | 97.5434 | 186.584 | 63.8368 | 143.9717 | 30.0259 | 140.2363 | 30.2341 | 138.8299 | 19.4146 | 107.5411 | 162.858 | 37.5144 | 98.5423 | 197.684 | 24.9813 | 101.2125 | 181.5132 | 25.8715 | 125.5507 | 39.8924 | 138.0396 | 31.0027 | 147.3825 | 1.9331 | 18.6165 | 2.0779 | 0.074838 | -27.1373 | 3.095 | 290.92 | 52.48 | 1.4821 | -0.68499 | -6.6809 | 0.87181 | 0.69461 | -15.044 | 4.7689 | 0.14874 | -0.94045 | 0.52241 | -2.2985 | -1.0909 | -0.60943 | -0.080904
42838.4263 | 518 | 22.8854 | 22.8525 | 22.8399 | 22.7572 | 22.3629 | 21.6924 | 22.6818 | 21.7456 | 22.338 | 22.3446 | 22.3176 | 21.9673 | 21.1855 | 22.1498 | 21.5949 | 21.7655 | 21.9074 | 21.0719 | 21.1911 | 21.7296 | 20.4717 | 21.2625 | 25.6863 | 21.8991 | 22.2727 | 29.7122 | 182.9139 | 161.4311 | 195.0094 | 22.1212 | 22.1422 | 27.4299 | 22.0366 | 22.2837 | 29.6654 | 83.9563 | 208.0661 |  | 123.3927 | 157.1524 | 154.9095 | 140.1697 |  | 17.8832 | 19.1017 | 17.915 | 19.0572 | 19.9391 | 33.3547 | 137.5697 | 15.6828 | 17.3165 | 15.882 | 19.0786 | 18.8428 | 45.9883 | 49.1101 | 44.7878 | 21.6835 |  |  | 0.77825 | -0.14989 | -31.5286 | 0.43957 | 0.62439 | -156.0738 | 15.0666 | 0.83943 | -0.04953 | 0.18725 | 0.4303 | 0.00038441 | 0.00036306 | 0.35095 | 21.9287 | 21.9681 | 22.1556 | 22.2224 | 22.0205 | 21.3172 | 20.1164 | 22.189 | 22.3685 | 22.4034 | 22.3462 | 21.9623 | 21.1941 | 22.2765 | 91.0261 | 56.6107 | 54.9614 | 40.7969 | 35.4877 | 63.9208 | 40.8691 | 22.3225 | 22.079 | 21.6586 | 22.0517 | 21.7836 | 21.6147 | 21.9406 | 21.8241 | 25.8896 | 73.0564 | 180.4912 | 145.4617 | 105.5617 | 1.5427 | 1.5123 | 77.342 | 21.885 | 22.2026 | 20.9488 | 21.5543 | 22.012 | 21.9948 | 22.7747 | 34.8996 | 21.8203 | 21.9178 | 27.1388 | 178.4801 | 223.2454 | 144.815 | 145.7447 | 98.9908 |  | 74.1306 | 144.678 | 79.8543 | 127.7462 | 106.1891 | 84.7713 |  | 97.6805 |  |  | 25.6697 | 31.0111 | 72.1919 | [5 empty] | 21.8891 | 92.7532 | 21.7042 | 22.0911 | 37.2469 | 21.2858 | 21.9312 | 35.1594 | 123.9598 | 246.12 |  | 105.2499 | 169.213 | 26.2949 | 98.1133 | 187.5995 | 64.1488 | 144.4699 | 30.0737 | 140.7767 | 30.2682 | 139.099 | 19.4233 | 107.7783 | 163.7201 | 37.6454 | 98.9035 | 198.0427 | 25.0276 | 101.343 | 182.2162 | 25.8942 | 125.8143 | 39.9802 | 138.2084 | 31.0702 | 147.8591 | 1.6469 | 18.6129 | 2.0811 | 0.076341 | -27.1958 | 3.095 | 297.06 | 51.67 | 1.3302 | -0.46124 | -6.6896 | 0.78987 | 0.96408 | -15.2423 | 4.7358 | 0.13416 | -0.92021 | 0.57526 | -2.2798 | -1.0145 | -0.63939 | -0.088366
42838.4263 | 519 | 22.8842 | 22.8585 | 22.8374 | 22.7549 | 22.3655 | 21.6922 | 22.6887 | 21.7472 | 22.3442 | 22.3493 | 22.3187 | 21.9714 | 21.1872 | 22.1528 | 21.5985 | 21.7706 | 21.9101 | 21.0753 | 21.2042 | 21.7451 | 20.4748 | 21.2781 | 25.7236 | 21.9127 | 22.2781 | 29.7524 | 183.3994 | 161.9684 | 195.5567 | 22.1132 | 22.1467 | 27.4515 | 22.0386 | 22.2956 | 29.7065 | 84.2358 | 210.6027 |  | 123.9016 | 157.9392 | 155.5118 | 141.4888 |  | 17.8865 | 19.1196 | 17.9211 | 19.0741 | 19.9676 | 33.1995 | 138.0055 | 15.6107 | 17.3215 | 15.8603 | 19.0883 | 18.8469 | 45.9705 | 49.1142 | 44.7823 | 21.6845 |  |  | 1.162 | -0.057233 | -31.6744 | 0.3916 | 0.50151 | -152.8421 | 15.0416 | 0.63507 | -0.028318 | 0.23362 | 0.45321 | 0.00035977 | 0.00036306 | 0.36826 | 21.9162 | 21.9502 | 22.1451 | 22.2 | 22.0112 | 21.3023 | 20.1179 | 22.1777 | 22.3577 | 22.3837 | 22.3372 | 21.9563 | 21.1745 | 22.2632 | 92.0329 | 60.3711 | 60.3328 | 42.5565 | 35.3421 | 64.0493 | 40.9766 | 22.3217 | 22.0823 | 21.6649 | 22.0493 | 21.7833 | 21.6224 | 21.9379 | 21.8203 | 25.9064 | 73.265 | 179.9986 | 145.6484 | 106.0446 | 1.3697 | 1.1726 | 77.748 | 21.8975 | 22.215 | 20.9689 | 21.5602 | 22.0224 | 22.0018 | 22.7857 | 34.9636 | 21.8322 | 21.9346 | 27.1795 | 179.1881 | 224.6831 | 145.4364 | 146.3133 | 100.3775 |  | 74.4195 | 143.9227 | 80.0541 | 128.1173 | 106.5545 | 84.4614 |  | 98.0017 |  |  | 25.7528 | 31.1191 | 72.722 | [5 empty] | 21.898 | 92.1868 | 21.7054 | 22.0985 | 37.323 | 21.2864 | 21.9334 | 35.3229 | 124.254 | 247.8532 |  | 105.7089 | 169.7161 | 26.3601 | 98.4865 | 188.7429 | 64.5595 | 144.9536 | 30.1348 | 141.3631 | 30.3517 | 139.3884 | 19.4327 | 108.2413 | 164.3765 | 37.7932 | 99.425 | 198.5054 | 25.056 | 101.7169 | 183.0125 | 25.9549 | 126.3182 | 40.1093 | 138.5675 | 31.1578 | 148.465 | 1.7998 | 18.6104 | 2.0845 | 0.077256 | -27.2007 | 3.095 | 294.32 | 52 | 1.6264 | -0.28502 | -6.7052 | 0.74555 | 0.86381 | -15.0799 | 4.7307 | 0.10641 | -0.89169 | 0.57963 | -2.3763 | -1.5986 | -0.66538 | -0.094021
42838.4263 | 520 | 22.8888 | 22.859 | 22.842 | 22.7554 | 22.3677 | 21.6906 | 22.6877 | 21.7515 | 22.3459 | 22.3548 | 22.3187 | 21.9728 | 21.1875 | 22.1598 | 21.5954 | 21.7656 | 21.9039 | 21.0759 | 21.2013 | 21.7423 | 20.4721 | 21.28 | 25.7497 | 21.9121 | 22.2788 | 29.783 | 184.2499 | 162.386 | 198.3027 | 22.1155 | 22.1502 | 27.4864 | 22.041 | 22.2927 | 29.7398 | 84.543 | 212.7452 |  | 124.4329 | 158.8027 | 156.212 | 143.6848 |  | 17.8947 | 19.1243 | 17.9167 | 19.0774 | 19.9746 | 33.0746 | 138.7659 | 15.5641 | 17.3321 | 15.8354 | 19.1024 | 18.8474 | 45.9614 | 49.1063 | 44.7822 | 21.6744 |  |  | 0.87419 | -0.096661 | -32.0746 | 0.31077 | 0.42266 | -156.8144 | 15.4576 | 0.59367 | -0.0059392 | 0.25019 | 0.47092 | 0.00035813 | 0.00033677 | 0.3967 | 21.9328 | 21.9621 | 22.1611 | 22.2111 | 22.0294 | 21.3161 | 20.1252 | 22.1869 | 22.3634 | 22.401 | 22.3501 | 21.9584 | 21.187 | 22.276 | 91.764 | 60.9191 | 61.1078 | 43.3341 | 35.8005 | 64.1603 | 41.0767 | 22.3188 | 22.0889 | 21.6632 | 22.0463 | 21.7866 | 21.6218 | 21.9387 | 21.832 | 25.938 | 73.5025 | 179.5985 | 145.8541 | 106.8514 | 1.5589 | 0.81618 | 78.1812 | 21.894 | 22.2207 | 20.9786 | 21.5577 | 22.0225 | 22.004 | 22.7988 | 35.0203 | 21.8332 | 21.9414 | 27.2121 | 179.9861 | 225.4818 | 146.0406 | 146.8107 | 100.749 |  | 74.6648 | 144.3305 | 80.2762 | 129.3701 | 107.0153 | 84.5156 |  | 98.2998 |  |  | 25.7784 | 31.2934 | 72.3135 | [5 empty] | 21.891 | 93.3164 | 21.6996 | 22.0975 | 37.404 | 21.2887 | 21.9201 | 35.4929 | 124.619 | 250.7334 |  | 106.1134 | 170.4438 | 26.3867 | 98.7891 | 188.8592 | 65.0047 | 145.6518 | 30.1859 | 142.1249 | 30.4044 | 139.9041 | 19.4258 | 108.3539 | 165.2635 | 37.9265 | 99.8434 | 198.8269 | 25.0835 | 102.5137 | 184.3742 | 26.0008 | 126.695 | 40.3105 | 138.8243 | 31.2437 | 149.2336 | 1.8996 | 18.6048 | 2.0865 | 0.075964 | -27.3129 | 3.095 | 298.04 | 52.07 | 1.4148 | -0.37041 | -6.7475 | 0.66417 | 0.79283 | -15.2714 | 4.7947 | 0.10524 | -0.89462 | 0.56336 | -2.3331 | -1.6729 | -0.71466 | -0.10759
42838.4263 | 521 | 22.8935 | 22.859 | 22.8446 | 22.7626 | 22.3634 | 21.696 | 22.6983 | 21.7611 | 22.3483 | 22.3581 | 22.3211 | 21.9707 | 21.1878 | 22.1669 | 21.5931 | 21.7713 | 21.9026 | 21.0721 | 21.2019 | 21.7513 | 20.4766 | 21.283 | 25.7771 | 21.9142 | 22.2861 | 29.8267 | 184.8631 | 162.8182 | 197.7058 | 22.1206 | 22.1614 | 27.5108 | 22.0441 | 22.3006 | 29.7825 | 84.8566 | 212.5369 |  | 124.9083 | 159.5719 | 156.8268 | 145.6931 |  | 17.911 | 19.133 | 17.9266 | 19.0839 | 19.986 | 34.2307 | 139.5323 | 15.5377 | 17.338 | 15.8051 | 19.1122 | 18.8557 | 45.9642 | 49.1063 | 44.7736 | 21.6804 |  |  | 0.8098 | -0.099949 | -32.321 | 0.45665 | 0.76173 | -153.8895 | 14.9273 | 0.64361 | 0.2844 | 0.24956 | 0.53203 | 0.0003302 | 0.00035977 | 0.41931 | 21.9267 | 21.9665 | 22.1585 | 22.2087 | 22.0249 | 21.3073 | 20.1202 | 22.1824 | 22.36 | 22.3967 | 22.344 | 21.9581 | 21.1904 | 22.2826 | 91.616 | 59.4948 | 60.9139 | 42.6392 | 35.4705 | 64.2603 | 41.1652 | 22.3189 | 22.0855 | 21.661 | 22.0456 | 21.7832 | 21.6268 | 21.9443 | 21.8302 | 25.9636 | 73.728 | 179.3073 | 146.1037 | 107.6448 | 1.6294 | 0.61114 | 78.5837 | 21.8897 | 22.217 | 20.9786 | 21.5582 | 22.0204 | 22.005 | 22.8013 | 35.0761 | 21.8289 | 21.9403 | 27.2443 | 180.6083 | 226.4895 | 146.481 | 147.2754 | 100.2097 |  | 74.8669 | 143.3843 | 80.5076 | 128.8222 | 107.3756 | 84.942 |  | 98.5831 |  |  | 25.8111 | 31.4304 | 71.7429 | [5 empty] | 21.9005 | 93.6648 | 21.7062 | 22.0975 | 37.568 | 21.2966 | 21.9286 | 35.6711 | 125.0311 | 252.0225 |  | 106.6352 | 171.5094 | 26.419 | 99.1394 | 189.4215 | 65.3319 | 146.4746 | 30.2349 | 142.9415 | 30.4542 | 140.2962 | 19.4275 | 108.5744 | 166.0836 | 38.0764 | 100.2752 | 199.5451 | 25.1531 | 103.0943 | 185.4996 | 26.0557 | 126.9425 | 40.5094 | 139.1035 | 31.3264 | 149.7342 | 1.7571 | 18.602 | 2.088 | 0.073365 | -27.1772 | 3.0949 | 290.57 | 51.69 | 1.3608 | -0.37667 | -6.7735 | 0.80512 | 1.0664 | -15.1569 | 4.7206 | 0.12777 | -0.85959 | 0.59309 | -2.3046 | -1.6409 | -0.75848 | -0.12123
42838.4263 | 522 | 22.89 | 22.8485 | 22.8372 | 22.757 | 22.3606 | 21.6932 | 22.6898 | 21.7424 | 22.3513 | 22.3502 | 22.3174 | 21.9711 | 21.1801 | 22.1596 | 21.5938 | 21.7665 | 21.9049 | 21.0744 | 21.2064 | 21.7554 | 20.477 | 21.29 | 25.8032 | 21.9207 | 22.2926 | 29.8644 | 185.2553 | 163.5518 | 197.0646 | 22.1188 | 22.1511 | 27.5356 | 22.0369 | 22.3062 | 29.8172 | 85.1687 | 212.8829 |  | 125.3764 | 160.1735 | 157.3832 | 146.7558 |  | 17.9148 | 19.1405 | 17.9432 | 19.0988 | 20.0175 | 34.9556 | 140.3715 | 15.5248 | 17.3367 | 15.7751 | 19.1309 | 18.8592 | 45.9638 | 49.1131 | 44.7637 | 21.6767 |  |  | 0.69283 | -0.12492 | -32.256 | -0.10387 | 0.82941 | -151.5752 | 14.4049 | 0.59499 | 0.16258 | 0.199 | 0.59157 | 0.00034499 | 0.00031706 | 0.41618 | 21.9272 | 21.9558 | 22.1555 | 22.2106 | 22.0222 | 21.31 | 20.1214 | 22.1799 | 22.3597 | 22.3903 | 22.347 | 21.957 | 21.1869 | 22.2741 | 90.889 | 56.9776 | 59.7151 | 42.7623 | 35.4197 | 64.3323 | 41.2236 | 22.3166 | 22.0806 | 21.655 | 22.0488 | 21.7809 | 21.6323 | 21.9364 | 21.8303 | 25.9878 | 73.9953 | 179.5389 | 146.4841 | 108.097 | 1.807 | 0.30093 | 78.4688 | 21.8866 | 22.2147 | 20.9817 | 21.5593 | 22.0157 | 21.9994 | 22.8031 | 35.1292 | 21.8245 | 21.9334 | 27.2686 | 181.2359 | 227.464 | 146.8543 | 147.7337 | 99.6999 |  | 75.0751 | 143.6894 | 80.7498 | 128.513 | 107.851 | 85.1636 |  | 98.9027 |  |  | 25.8202 | 31.4627 | 71.1643 | [5 empty] | 21.8946 | 94.0676 | 21.7 | 22.0923 | 37.6951 | 21.2854 | 21.9201 | 35.8314 | 125.3648 | 253.3561 |  | 107.1848 | 172.0828 | 26.4532 | 99.4614 | 190.402 | 65.7067 | 146.8512 | 30.2955 | 143.3565 | 30.5071 | 140.6052 | 19.4131 | 109.2093 | 166.9974 | 38.2332 | 100.6342 | 200.7908 | 25.2212 | 103.4469 | 186.3201 | 26.0998 | 127.4197 | 40.7036 | 139.3503 | 31.4192 | 149.9477 | 1.8157 | 18.603 | 2.0914 | 0.073074 | -27.263 | 3.095 | 290.31 | 52.77 | 1.2578 | -0.4211 | -6.7667 | -0.38399 | 1.114 | -15.0602 | 4.6427 | 0.1497 | -0.85891 | 0.62083 | -2.2152 | -1.5008 | -0.77608 | -0.12384
42838.4263 | 523 | 22.8813 | 22.8511 | 22.8474 | 22.758 | 22.3733 | 21.6848 | 22.6955 | 21.7502 | 22.3399 | 22.3453 | 22.3175 | 21.9648 | 21.1818 | 22.156 | 21.5951 | 21.7711 | 21.9058 | 21.0776 | 21.2048 | 21.7605 | 20.4799 | 21.3017 | 25.8254 | 21.9213 | 22.2973 | 29.8989 | 185.7345 | 164.415 | 196.9072 | 22.1137 | 22.1579 | 27.5668 | 22.0491 | 22.3183 | 29.8574 | 85.5072 | 211.3287 |  | 125.8546 | 160.6495 | 157.9511 | 148.3136 |  | 17.9122 | 19.1283 | 17.9439 | 19.0993 | 20.0088 | 35.3484 | 141.0692 | 15.5017 | 17.3403 | 15.7735 | 19.1293 | 18.8614 | 45.951 | 49.1138 | 44.7553 | 21.6756 |  |  | 0.85514 | -0.021749 | -32.2954 | -0.074954 | 0.6809 | -154.5618 | 14.5895 | 0.49379 | -0.11355 | 0.49965 | 0.60129 | 0.0003417 | 0.00034499 | 0.3916 | 21.9244 | 21.955 | 22.1509 | 22.2055 | 22.0151 | 21.3018 | 20.1165 | 22.1776 | 22.3592 | 22.3861 | 22.3368 | 21.957 | 21.1752 | 22.2649 | 90.8083 | 57.354 | 57.16 | 41.3477 | 35.5907 | 64.4266 | 41.2601 | 22.3149 | 22.081 | 21.6541 | 22.0488 | 21.7829 | 21.6278 | 21.9419 | 21.8368 | 26.0078 | 74.231 | 179.7162 | 146.7158 | 108.8734 | 1.897 | 0.76597 | 78.6393 | 21.8888 | 22.2088 | 20.9975 | 21.5602 | 22.0158 | 22.0018 | 22.8117 | 35.1835 | 21.8249 | 21.9347 | 27.2982 | 181.8802 | 228.3468 | 147.2406 | 148.2178 | 99.7782 |  | 75.3012 | 144.6234 | 81.0365 | 127.8158 | 108.4768 | 86.0174 |  | 99.1991 |  |  | 25.8719 | 31.4928 | 71.1011 | [5 empty] | 21.8914 | 96.6585 | 21.7034 | 22.094 | 37.8245 | 21.2882 | 21.9263 | 35.9836 | 125.8013 | 254.8392 |  | 107.6799 | 172.4283 | 26.49 | 99.5896 | 191.0794 | 66.1555 | 147.2661 | 30.3382 | 143.7873 | 30.5703 | 141.0391 | 19.4102 | 109.4823 | 167.7416 | 38.3744 | 100.9977 | 201.6813 | 25.2761 | 103.6177 | 186.897 | 26.1231 | 127.8418 | 40.8672 | 139.4962 | 31.521 | 150.3134 | 1.516 | 18.5983 | 2.0956 | 0.07465 | -27.164 | 3.095 | 280.92 | 51.17 | 1.3972 | -0.17571 | -6.7707 | -0.32618 | 1.01 | -15.2175 | 4.6754 | 0.15598 | -0.874 | 0.66545 | -2.195 | -1.2126 | -0.80641 | -0.13662
42838.4263 | 524 | 22.8953 | 22.8586 | 22.8512 | 22.7673 | 22.3707 | 21.6949 | 22.6969 | 21.756 | 22.3506 | 22.3504 | 22.3294 | 21.9826 | 21.1934 | 22.1646 | 21.6057 | 21.7799 | 21.9046 | 21.0819 | 21.2115 | 21.7681 | 20.4862 | 21.3135 | 25.849 | 21.9189 | 22.3133 | 29.9409 | 186.1929 | 165.21 | 196.5272 | 22.1171 | 22.1609 | 27.5998 | 22.0454 | 22.3208 | 29.9013 | 85.821 | 210.7273 |  | 126.2457 | 161.2531 | 158.4474 | 148.9397 |  | 17.9143 | 19.1279 | 17.941 | 19.1032 | 20.0294 | 35.5659 | 141.7977 | 15.4573 | 17.3463 | 15.7977 | 19.1457 | 18.8674 | 45.9207 | 49.0964 | 44.7475 | 21.6729 |  |  | 1.5326 | -0.17157 | -31.7822 | 0.084726 | 0.27809 | -154.6814 | 15.3373 | 0.66398 | 0.076182 | 0.20257 | 0.50634 | 0.00036799 | 0.00035156 | 0.33765 | 21.9319 | 21.9622 | 22.1492 | 22.2039 | 22.013 | 21.3008 | 20.1157 | 22.17 | 22.36 | 22.3911 | 22.337 | 21.9571 | 21.1798 | 22.2662 | 91.3426 | 57.6601 | 57.6411 | 41.0769 | 35.1296 | 64.5361 | 41.3274 | 22.311 | 22.076 | 21.6515 | 22.0401 | 21.7713 | 21.6245 | 21.9379 | 21.8329 | 26.0264 | 74.458 | 179.7224 | 146.9256 | 109.4133 | 1.737 | 0.66763 | 79.1935 | 21.888 | 22.2059 | 21.0029 | 21.5579 | 22.0162 | 22.0016 | 22.8204 | 35.234 | 21.8196 | 21.9369 | 27.3277 | 182.4847 | 229.2119 | 147.541 | 148.5841 | 99.8073 |  | 75.5094 | 146.9748 | 81.3059 | 128.4297 | 109.016 | 86.5481 |  | 99.4284 |  |  | 25.9168 | 31.5306 | 71.063 | [5 empty] | 21.8862 | 97.8023 | 21.696 | 22.0947 | 37.8956 | 21.289 | 21.9281 | 36.1586 | 126.3419 | 256.361 |  | 108.2775 | 172.8075 | 26.536 | 99.8463 | 191.9006 | 66.5902 | 147.7609 | 30.3858 | 144.2627 | 30.6776 | 141.5617 | 19.3994 | 109.6601 | 168.2102 | 38.5025 | 101.237 | 201.9738 | 25.3272 | 104.0522 | 187.6274 | 26.1454 | 128.1079 | 41.01 | 139.757 | 31.6004 | 150.567 | 1.4731 | 18.593 | 2.098 | 0.074766 | -27.162 | 3.095 | 276.66 | 52.13 | 1.8698 | -0.4935 | -6.7167 | 0.3468 | 0.64571 | -15.2288 | 4.7954 | 0.16295 | -0.92912 | 0.67019 | -2.2412 | -1.2581 | -0.8118 | -0.14315
42838.4264 | 525 | 22.884 | 22.8531 | 22.8364 | 22.755 | 22.3608 | 21.6877 | 22.6864 | 21.7424 | 22.3472 | 22.3455 | 22.3147 | 21.9737 | 21.1795 | 22.1533 | 21.602 | 21.7772 | 21.9021 | 21.0751 | 21.2108 | 21.7664 | 20.4838 | 21.3093 | 25.8791 | 21.9144 | 22.3076 | 29.9695 | 187.0555 | 165.906 | 198.5072 | 22.12 | 22.1655 | 27.6253 | 22.0404 | 22.3223 | 29.9389 | 86.112 | 210.7608 |  | 126.6448 | 161.6933 | 159.0229 | 149.8669 |  | 17.9157 | 19.1244 | 17.9452 | 19.1128 | 20.0492 | 35.7528 | 142.458 | 15.4385 | 17.3502 | 15.8017 | 19.157 | 18.871 | 45.8681 | 49.0894 | 44.7528 | 21.6732 |  |  | 0.7362 | -0.50144 | -31.61 | 0.23323 | 0.39177 | -155.2945 | 15.0094 | 0.35908 | 0.15558 | 0.16103 | 0.66865 | 0.00036634 | 0.00038441 | 0.32207 | 21.9404 | 21.9635 | 22.1583 | 22.2128 | 22.0204 | 21.3133 | 20.1255 | 22.1769 | 22.3645 | 22.4041 | 22.3509 | 21.9607 | 21.1869 | 22.2729 | 90.0669 | 57.2948 | 57.7544 | 40.6243 | 34.2957 | 64.6091 | 41.398 | 22.3147 | 22.0793 | 21.6582 | 22.0586 | 21.7834 | 21.6355 | 21.945 | 21.8463 | 26.0691 | 74.7043 | 179.7974 | 147.1734 | 109.8 | 1.969 | 0.56493 | 79.6063 | 21.8897 | 22.2102 | 21.0072 | 21.5544 | 22.0155 | 21.9987 | 22.8263 | 35.2896 | 21.8266 | 21.9455 | 27.3505 | 183.0409 | 230.0375 | 147.8301 | 148.8666 | 99.1044 |  | 75.725 | 146.996 | 81.5172 | 128.2805 | 109.5557 | 86.8271 |  | 99.6221 |  |  | 25.9801 | 31.5744 | 71.0021 | [5 empty] | 21.8899 | 98.6146 | 21.7005 | 22.0956 | 37.9621 | 21.2892 | 21.9226 | 36.3156 | 126.8542 | 258.7892 |  | 108.8403 | 173.2095 | 26.5733 | 100.3224 | 192.1455 | 66.967 | 148.5186 | 30.4268 | 144.5295 | 30.7702 | 142.2555 | 19.4002 | 110.2943 | 168.8424 | 38.6222 | 101.5 | 202.0626 | 25.3898 | 104.6872 | 188.519 | 26.1668 | 128.421 | 41.1325 | 140.0559 | 31.6724 | 151.1575 | 1.8311 | 18.5911 | 2.1004 | 0.075477 | -27.2151 | 3.095 | 257.47 | 52.02 | 1.2986 | -0.84367 | -6.6985 | 0.57538 | 0.76665 | -15.2636 | 4.7453 | 0.19054 | -0.9217 | 0.69617 | -2.0907 | -1.2623 | -0.82641 | -0.1447
42838.4264 | 526 | 22.8897 | 22.8573 | 22.8413 | 22.757 | 22.3646 | 21.6951 | 22.6959 | 21.7461 | 22.3515 | 22.351 | 22.3184 | 21.9727 | 21.1844 | 22.1582 | 21.5931 | 21.771 | 21.9004 | 21.0703 | 21.2011 | 21.7644 | 20.4788 | 21.3101 | 25.9041 | 21.9168 | 22.3052 | 30.0015 | 187.866 | 166.6792 | 199.3086 | 22.119 | 22.1695 | 27.6625 | 22.0432 | 22.3247 | 29.9718 | 86.4389 | 210.5836 |  | 127.0286 | 162.0544 | 159.5845 | 150.7013 |  | 17.9113 | 19.1288 | 17.9404 | 19.1338 | 20.0634 | 36.9733 | 143.1399 | 15.4353 | 17.3622 | 15.828 | 19.1676 | 18.876 | 45.8452 | 49.0835 | 44.7623 | 21.6729 |  |  | 0.81834 | -0.25765 | -31.2664 | 0.009154 | 0.3714 | -154.7149 | 14.4535 | 0.88674 | 0.13262 | 0.31922 | 0.53828 | 0.00034827 | 0.00035484 | 0.34052 | 21.9306 | 21.9641 | 22.1493 | 22.2121 | 22.0154 | 21.3064 | 20.1159 | 22.1786 | 22.3582 | 22.401 | 22.348 | 21.9555 | 21.1916 | 22.27 | 90.0758 | 58.4438 | 57.9649 | 39.8705 | 33.2167 | 64.7075 | 41.4657 | 22.3201 | 22.0796 | 21.6486 | 22.0506 | 21.7893 | 21.641 | 21.9459 | 21.8455 | 26.0981 | 74.9503 | 179.962 | 147.5782 | 109.3184 | 2.6187 | 0.62122 | 80.3751 | 21.897 | 22.2223 | 21.0207 | 21.5622 | 22.029 | 22.0062 | 22.8459 | 35.3585 | 21.8338 | 21.959 | 27.3933 | 183.3273 | 231.2201 | 148.2252 | 149.2165 | 99.8261 |  | 76.0024 | 148.4878 | 81.7968 | 129.4565 | 110.2471 | 86.3637 |  | 99.8686 |  |  | 26.0355 | 31.6671 | 71.2404 | [5 empty] | 21.8911 | 99.5273 | 21.7131 | 22.0958 | 38.0317 | 21.2902 | 21.9208 | 36.4881 | 127.2808 | 260.6289 |  | 109.2841 | 173.6791 | 26.6079 | 100.7328 | 192.6482 | 67.3714 | 149.1696 | 30.4765 | 144.6569 | 30.8369 | 142.9515 | 19.3963 | 110.5079 | 169.4182 | 38.7731 | 101.8658 | 202.2089 | 25.4516 | 105.2028 | 189.4902 | 26.187 | 128.8627 | 41.2667 | 140.3671 | 31.7597 | 151.879 | 2.2978 | 18.5906 | 2.1029 | 0.075557 | -27.2061 | 3.095 | 254.92 | 51.83 | 1.3703 | -0.60476 | -6.662 | 0.11399 | 0.74792 | -15.2651 | 4.6657 | 0.18087 | -0.95254 | 0.69153 | -2.0799 | -1.2777 | -0.83707 | -0.12214
42838.4264 | 527 | 22.8826 | 22.8484 | 22.8334 | 22.7568 | 22.3628 | 21.6913 | 22.6902 | 21.7427 | 22.3468 | 22.3461 | 22.3165 | 21.9637 | 21.1802 | 22.1522 | 21.5993 | 21.7755 | 21.9101 | 21.0797 | 21.209 | 21.775 | 20.4783 | 21.3209 | 25.9361 | 21.9207 | 22.3242 | 30.0483 | 188.6098 | 167.3089 | 200.3567 | 22.1142 | 22.1703 | 27.6814 | 22.0455 | 22.3283 | 30.0001 | 86.7599 | 211.1203 |  | 127.4148 | 162.5142 | 160.1014 | 151.4401 |  | 17.9047 | 19.1251 | 17.9474 | 19.1407 | 20.0692 | 37.2979 | 143.8232 | 15.4546 | 17.3548 | 15.8625 | 19.1737 | 18.8787 | 45.8422 | 49.0817 | 44.7762 | 21.6737 |  |  | 0.78285 | -0.42785 | -31.2578 | 0.16555 | 0.64345 | -152.5155 | 15.129 | 0.63507 | -0.076384 | 0.40985 | 0.51953 | 0.00036799 | 0.00038277 | 0.38069 | 21.9354 | 21.9622 | 22.1552 | 22.2094 | 22.0222 | 21.3126 | 20.1197 | 22.1767 | 22.3523 | 22.3914 | 22.3481 | 21.9691 | 21.1866 | 22.2665 | 90.4907 | 57.5813 | 58.5442 | 39.8211 | 33.0845 | 64.8191 | 41.5368 | 22.3061 | 22.0797 | 21.6504 | 22.0455 | 21.7843 | 21.6411 | 21.9392 | 21.8379 | 26.1147 | 75.1959 | 180.2324 | 147.951 | 109.2659 | 2.7215 | 1.3438 | 80.8247 | 21.8958 | 22.2196 | 21.024 | 21.5624 | 22.0234 | 22.0103 | 22.851 | 35.4113 | 21.8308 | 21.955 | 27.4185 | 183.893 | 232.4618 | 148.6508 | 149.6044 | 101.3296 |  | 76.2636 | 151.0706 | 82.0814 | 130.3841 | 110.776 | 86.8922 |  | 100.0552 |  |  | 26.0364 | 31.8448 | 71.7579 | [5 empty] | 21.8894 | 100.0325 | 21.7075 | 22.091 | 38.1421 | 21.2853 | 21.9202 | 36.6362 | 127.6842 | 262.5352 |  | 109.6423 | 174.0339 | 26.6409 | 101.0089 | 193.5 | 67.731 | 150.0518 | 30.5227 | 145.0305 | 30.8994 | 143.4426 | 19.4143 | 110.5881 | 169.8782 | 38.8992 | 102.2558 | 202.3831 | 25.5087 | 105.5703 | 190.4855 | 26.2229 | 129.3955 | 41.4354 | 140.6377 | 31.8644 | 152.662 | 1.8512 | 18.5878 | 2.1034 | 0.074192 | -27.2001 | 3.095 | 258.45 | 52.85 | 1.3417 | -0.77931 | -6.661 | 0.48476 | 0.98496 | -15.1642 | 4.776 | 0.14889 | -1.0135 | 0.68722 | -2.1126 | -1.3337 | -0.84528 | -0.1115
42838.4264 | 528 | 22.897 | 22.8566 | 22.8397 | 22.7639 | 22.3687 | 21.6941 | 22.6964 | 21.7482 | 22.3446 | 22.3511 | 22.3226 | 21.9734 | 21.1826 | 22.155 | 21.5978 | 21.7772 | 21.9046 | 21.0775 | 21.2106 | 21.772 | 20.4773 | 21.3232 | 25.9599 | 21.9186 | 22.3206 | 30.079 | 189.2513 | 167.763 | 201.6961 | 22.1152 | 22.169 | 27.7028 | 22.0381 | 22.3276 | 30.0384 | 87.1233 | 212.2667 |  | 127.8422 | 163.0479 | 160.7934 | 154.3502 |  | 17.9107 | 19.1331 | 17.9665 | 19.1609 | 20.1316 | 37.3008 | 144.2208 | 15.4886 | 17.3642 | 15.8469 | 19.1978 | 18.886 | 45.8397 | 49.0831 | 44.7834 | 21.6762 |  |  | 0.79205 | -0.46004 | -31.089 | 0.19709 | 0.63162 | -152.7455 | 15.2473 | 0.76189 | -0.0034094 | 0.15956 | 0.60129 | 0.00033842 | 0.0003647 | 0.40472 | 21.9427 | 21.962 | 22.1557 | 22.2115 | 22.0148 | 21.3127 | 20.128 | 22.1751 | 22.3669 | 22.3987 | 22.3475 | 21.9612 | 21.1796 | 22.2685 | 91.9919 | 59.1747 | 63.0415 | 40.781 | 33.496 | 64.9639 | 41.6571 | 22.3113 | 22.0806 | 21.6527 | 22.0508 | 21.7835 | 21.6387 | 21.9474 | 21.8504 | 26.1431 | 75.4395 | 180.7522 | 148.2451 | 110.425 | 2.2902 | 0.60867 | 80.982 | 21.8907 | 22.2201 | 21.0258 | 21.5594 | 22.0245 | 22.0169 | 22.8548 | 35.4678 | 21.8269 | 21.9602 | 27.4447 | 184.5486 | 233.8588 | 149.0356 | 149.976 | 101.3142 |  | 76.5066 | 153.3718 | 82.365 | 132.3511 | 111.2528 | 86.768 |  | 100.2509 |  |  | 26.0524 | 31.9673 | 72.4372 | [5 empty] | 21.8948 | 100.1515 | 21.7079 | 22.0946 | 38.2703 | 21.2938 | 21.9282 | 36.797 | 128.116 | 265.1639 |  | 110.0768 | 174.305 | 26.6708 | 101.3185 | 194.3833 | 68.1382 | 150.9426 | 30.5839 | 145.7759 | 30.9732 | 143.7198 | 19.4267 | 111.2168 | 170.4228 | 39.0405 | 102.6437 | 202.1113 | 25.5551 | 106.1715 | 191.4548 | 26.2589 | 129.7638 | 41.6047 | 141.0283 | 31.9588 | 153.1763 | 1.812 | 18.586 | 2.1057 | 0.074962 | -27.2224 | 3.095 | 262.04 | 51.82 | 1.3515 | -0.80811 | -6.6431 | 0.52893 | 0.97587 | -15.1757 | 4.7947 | 0.15842 | -1.0666 | 0.65196 | -2.2621 | -1.8192 | -0.91217 | -0.1346
42838.4264 | 529 | 22.8895 | 22.8491 | 22.8363 | 22.7582 | 22.3723 | 21.7015 | 22.6953 | 21.7442 | 22.3408 | 22.3505 | 22.324 | 21.9712 | 21.1863 | 22.154 | 21.5962 | 21.7726 | 21.906 | 21.0805 | 21.2109 | 21.7744 | 20.4792 | 21.3315 | 25.9864 | 21.9221 | 22.3202 | 30.1131 | 189.8231 | 168.1569 | 202.6441 | 22.1137 | 22.1785 | 27.7408 | 22.0401 | 22.3378 | 30.0842 | 87.5309 | 213.9801 |  | 128.2984 | 163.6594 | 161.5545 | 158.562 |  | 17.8961 | 19.1366 | 17.9593 | 19.1706 | 20.1709 | 37.3373 | 144.7123 | 15.4501 | 17.361 | 15.7891 | 19.209 | 18.8939 | 45.8324 | 49.087 | 44.7931 | 21.6772 |  |  | 0.60609 | -0.41076 | -31.3643 | -0.065754 | 0.73347 | -154.3752 | 15.4602 | 0.74875 | 0.12989 | 0.16376 | 0.51206 | 0.00035813 | 0.00037949 | 0.42328 | 21.94 | 21.9682 | 22.1535 | 22.2116 | 22.0154 | 21.3142 | 20.1245 | 22.177 | 22.3603 | 22.4003 | 22.344 | 21.9582 | 21.1874 | 22.2737 | 93.4856 | 59.2755 | 63.5842 | 42.86 | 34.9716 | 65.0996 | 41.7586 | 22.3131 | 22.0805 | 21.663 | 22.05 | 21.782 | 21.6412 | 21.9436 | 21.8496 | 26.1736 | 75.6877 | 180.6591 | 148.4907 | 111.1323 | 2.581 | 1.0117 | 81.751 | 21.8959 | 22.2121 | 21.0314 | 21.562 | 22.027 | 22.0057 | 22.8616 | 35.5216 | 21.8314 | 21.9716 | 27.4782 | 185.1205 | 235.285 | 149.349 | 150.2944 | 100.9131 |  | 76.7323 | 154.7565 | 82.6175 | 133.2671 | 111.736 | 87.3234 |  | 100.524 |  |  | 26.062 | 32.0053 | 73.0199 | [5 empty] | 21.885 | 100.1651 | 21.6983 | 22.0923 | 38.3334 | 21.2889 | 21.9215 | 36.9561 | 128.5521 | 266.6181 |  | 110.6599 | 174.777 | 26.7073 | 101.6175 | 195.4994 | 68.5217 | 151.4399 | 30.617 | 146.4864 | 31.0386 | 143.8897 | 19.4418 | 111.7985 | 170.8652 | 39.2055 | 102.9523 | 202.0561 | 25.5991 | 106.7313 | 192.6933 | 26.2907 | 130.1173 | 41.7321 | 141.4329 | 32.0341 | 153.3334 | 2.1008 | 18.5821 | 2.1088 | 0.075833 | -27.2234 | 3.095 | 290.64 | 52.71 | 1.1834 | -0.7636 | -6.6725 | -0.30552 | 1.0517 | -15.2573 | 4.8283 | 0.17802 | -1.0955 | 0.64618 | -2.4118 | -1.8675 | -1.0135 | -0.14496
42838.4264 | 530 | 22.8794 | 22.8568 | 22.8385 | 22.7437 | 22.3681 | 21.6961 | 22.6909 | 21.7525 | 22.3451 | 22.3461 | 22.3145 | 21.9643 | 21.1744 | 22.1549 | 21.6084 | 21.7687 | 21.9175 | 21.078 | 21.2022 | 21.7858 | 20.4812 | 21.3451 | 26.0121 | 21.9265 | 22.3427 | 30.159 | 190.188 | 168.4112 | 202.2685 | 22.1203 | 22.1814 | 27.771 | 22.044 | 22.3313 | 30.1231 | 87.9398 | 216.1812 |  | 128.8113 | 164.4026 | 162.2706 | 160.7504 |  | 17.9034 | 19.1416 | 17.964 | 19.1824 | 20.1819 | 37.4877 | 145.3318 | 15.463 | 17.3639 | 15.7659 | 19.2189 | 18.9049 | 45.8173 | 49.0906 | 44.7998 | 21.6765 |  |  | 0.70071 | -0.27803 | -31.3571 | 0.21417 | 0.63425 | -154.201 | 14.9332 | 1.394 | -0.070741 | 0.23005 | 0.4737 | 0.00034006 | 0.0003647 | 0.41726 | 21.9359 | 21.9663 | 22.1487 | 22.2056 | 22.0103 | 21.3057 | 20.12 | 22.1805 | 22.3574 | 22.3943 | 22.344 | 21.9536 | 21.1857 | 22.2752 | 95.2629 | 59.087 | 65.1723 | 44.4259 | 35.9728 | 65.2315 | 41.8621 | 22.3108 | 22.08 | 21.6574 | 22.0431 | 21.7817 | 21.6419 | 21.9412 | 21.8399 | 26.1988 | 75.9301 | 180.4202 | 148.7361 | 111.3243 | 1.9359 | 0.89074 | 82.4566 | 21.8962 | 22.2152 | 21.0315 | 21.5546 | 22.0257 | 22.0128 | 22.8677 | 35.5775 | 21.8289 | 21.9663 | 27.5069 | 185.7364 | 236.7938 | 149.5386 | 150.5609 | 101.7707 |  | 76.9971 | 155.3835 | 82.8483 | 135.4837 | 112.2514 | 87.3608 |  | 100.7945 |  |  | 26.1162 | 32.0719 | 73.2845 | [5 empty] | 21.8914 | 100.283 | 21.6952 | 22.0956 | 38.4451 | 21.2882 | 21.9193 | 37.098 | 128.983 | 266.9924 |  | 111.1455 | 175.3132 | 26.749 | 101.9779 | 196.2377 | 68.7769 | 151.7613 | 30.6682 | 147.0881 | 31.0963 | 144.2369 | 19.4599 | 112.2916 | 171.2229 | 39.3381 | 103.3423 | 202.6567 | 25.6547 | 107.0548 | 193.6846 | 26.3506 | 130.4803 | 41.8713 | 141.7574 | 32.1247 | 153.7082 | 1.8359 | 18.5795 | 2.112 | 0.075572 | -27.2113 | 3.095 | 280.7 | 51.75 | 1.272 | -0.62823 | -6.6718 | 0.55139 | 0.97819 | -15.2524 | 4.7465 | 0.16413 | -1.1042 | 0.6056 | -2.5934 | -2.0317 | -1.0586 | -0.14123
42838.4264 | 531 | 22.8867 | 22.8543 | 22.8331 | 22.7549 | 22.3716 | 21.6934 | 22.6924 | 21.7496 | 22.342 | 22.3424 | 22.3104 | 21.9714 | 21.1872 | 22.164 | 21.5992 | 21.772 | 21.9098 | 21.0807 | 21.2104 | 21.784 | 20.4783 | 21.3336 | 26.0326 | 21.9237 | 22.3374 | 30.1981 | 190.5898 | 168.8855 | 203.3445 | 22.124 | 22.187 | 27.811 | 22.0467 | 22.3471 | 30.1741 | 88.3295 | 218.8183 |  | 129.332 | 165.0581 | 163.0458 | 161.9697 |  | 17.8978 | 19.1312 | 17.9601 | 19.1825 | 20.215 | 38.0179 | 145.9729 | 15.4713 | 17.3627 | 15.7806 | 19.226 | 18.9023 | 45.7969 | 49.0894 | 44.8139 | 21.6732 |  |  | 0.97407 | -0.15843 | -31.5851 | 0.30223 | 0.72559 | -153.1799 | 14.9227 | 0.56673 | -0.10538 | 0.25984 | 0.4921 | 0.00035649 | 0.00034499 | 0.41779 | 21.9374 | 21.9656 | 22.1483 | 22.2065 | 22.0165 | 21.3077 | 20.1216 | 22.1834 | 22.3577 | 22.4028 | 22.3496 | 21.9568 | 21.1919 | 22.2765 | 95.7134 | 58.953 | 66.0908 | 45.8998 | 37.2715 | 65.369 | 41.9793 | 22.3116 | 22.0821 | 21.6557 | 22.0462 | 21.7891 | 21.6525 | 21.9429 | 21.8528 | 26.228 | 76.1906 | 180.235 | 149.1284 | 111.7158 | 1.6399 | 0.88941 | 82.6619 | 21.8902 | 22.2072 | 21.0286 | 21.5518 | 22.0124 | 22.0115 | 22.8723 | 35.6388 | 21.831 | 21.9626 | 27.5304 | 186.1422 | 237.7091 | 149.786 | 150.907 | 102.1359 |  | 77.2366 | 156.6975 | 83.1176 | 136.1533 | 112.6951 | 87.3822 |  | 101.0513 |  |  | 26.1743 | 32.1513 | 74.1605 | [5 empty] | 21.8954 | 100.5331 | 21.7077 | 22.1072 | 38.5303 | 21.2921 | 21.925 | 37.249 | 129.4314 | 267.1111 |  | 111.4913 | 175.8148 | 26.7878 | 102.4331 | 196.6684 | 69.1528 | 152.0648 | 30.7364 | 147.874 | 31.1617 | 144.7856 | 19.4952 | 112.5367 | 171.601 | 39.4832 | 103.7665 | 203.6698 | 25.737 | 107.2318 | 194.4114 | 26.4408 | 130.7367 | 42.0614 | 142.0234 | 32.2243 | 154.335 | 1.8679 | 18.5783 | 2.1153 | 0.075971 | -27.1762 | 3.095 | 275.93 | 51.68 | 1.5014 | -0.47423 | -6.6959 | 0.65499 | 1.0472 | -15.2148 | 4.7488 | 0.16297 | -1.1304 | 0.60509 | -2.627 | -2.1199 | -1.0775 | -0.14235
42838.4264 | 532 | 22.895 | 22.8621 | 22.8421 | 22.7626 | 22.3791 | 21.6991 | 22.7013 | 21.7586 | 22.3504 | 22.3498 | 22.3197 | 21.9767 | 21.189 | 22.1627 | 21.6125 | 21.781 | 21.9171 | 21.0814 | 21.2171 | 21.7912 | 20.4789 | 21.345 | 26.0645 | 21.9341 | 22.3415 | 30.2367 | 191.4289 | 169.4795 | 203.6396 | 22.1148 | 22.1846 | 27.8279 | 22.0404 | 22.344 | 30.1992 | 88.6928 | 218.6916 |  | 129.7901 | 165.7256 | 163.7019 | 162.6186 |  | 17.915 | 19.1412 | 17.9753 | 19.2012 | 20.2554 | 38.027 | 146.5116 | 15.4516 | 17.3737 | 15.8144 | 19.237 | 18.9054 | 45.7872 | 49.0921 | 44.8288 | 21.6799 |  |  | 0.67377 | -0.090089 | -31.4799 | 0.24375 | 0.70719 | -153.4834 | 13.9751 | 0.78949 | -0.013723 | 0.32069 | 0.54522 | 0.00039098 | 0.00035484 | 0.42927 | 21.9474 | 21.962 | 22.1533 | 22.2104 | 22.0241 | 21.3006 | 20.1262 | 22.181 | 22.359 | 22.3979 | 22.3437 | 21.9679 | 21.1906 | 22.2752 | 96.1167 | 60.8791 | 64.5053 | 46.8912 | 37.6277 | 65.5266 | 42.0727 | 22.3161 | 22.077 | 21.6577 | 22.0445 | 21.7893 | 21.6571 | 21.9463 | 21.8581 | 26.2564 | 76.4419 | 180.3508 | 149.5182 | 111.4507 | 1.6613 | 1.0661 | 83.0555 | 21.886 | 22.2065 | 21.0314 | 21.5521 | 22.0148 | 22.0086 | 22.8888 | 35.6971 | 21.8311 | 21.9753 | 27.5597 | 186.9983 | 238.9646 | 150.1295 | 151.1939 | 101.8446 |  | 77.4857 | 156.7727 | 83.3693 | 134.6351 | 113.0915 | 87.6272 |  | 101.3191 |  |  | 26.1992 | 32.2344 | 74.6618 | [5 empty] | 21.8947 | 100.1151 | 21.6932 | 22.0955 | 38.6294 | 21.2829 | 21.9202 | 37.3639 | 129.9306 | 267.1329 |  | 111.8205 | 176.717 | 26.8205 | 102.8287 | 197.3203 | 69.4412 | 152.8586 | 30.7616 | 148.2235 | 31.1974 | 145.21 | 19.5443 | 112.726 | 172.1949 | 39.5955 | 104.08 | 204.3607 | 25.7891 | 107.2966 | 194.8199 | 26.5113 | 131.0693 | 42.2117 | 142.3461 | 32.319 | 154.7485 | 2.2427 | 18.5775 | 2.1172 | 0.07457 | -27.4144 | 3.0949 | 291.77 | 52.65 | 1.2491 | -0.35761 | -6.6849 | 0.58823 | 1.0338 | -15.2301 | 4.5957 | 0.18042 | -1.1229 | 0.66345 | -2.6529 | -1.9327 | -1.0815 | -0.12557
42838.4264 | 533 | 22.8904 | 22.8568 | 22.8403 | 22.7581 | 22.3677 | 21.6955 | 22.6938 | 21.753 | 22.348 | 22.3496 | 22.3196 | 21.9685 | 21.1836 | 22.1678 | 21.5993 | 21.7698 | 21.9101 | 21.0788 | 21.2002 | 21.7879 | 20.483 | 21.3472 | 26.0915 | 21.9258 | 22.3407 | 30.2623 | 191.6851 | 169.9885 | 202.4644 | 22.1166 | 22.1943 | 27.8629 | 22.047 | 22.3457 | 30.2355 | 89.0792 | 217.3872 |  | 130.2174 | 166.4474 | 164.3346 | 163.5439 |  | 17.9325 | 19.1521 | 17.9831 | 19.2109 | 20.2719 | 37.9586 | 146.7085 | 15.4128 | 17.3758 | 15.8214 | 19.2456 | 18.9035 | 45.7431 | 49.0961 | 44.8467 | 21.6704 |  |  | 0.43327 | -0.21034 | -31.7605 | -0.24712 | 0.87804 | -153.191 | 14.7374 | 1.0727 | 0.13962 | 0.018574 | 0.68532 | 0.00041234 | 0.00037127 | 0.45194 | 21.9355 | 21.9585 | 22.1538 | 22.2013 | 22.0099 | 21.3042 | 20.1248 | 22.1725 | 22.356 | 22.3918 | 22.343 | 21.9604 | 21.1822 | 22.2669 | 97.3391 | 61.4387 | 61.808 | 46.9392 | 38.523 | 65.658 | 42.1424 | 22.3113 | 22.0766 | 21.6594 | 22.0417 | 21.7765 | 21.6511 | 21.9375 | 21.8526 | 26.2806 | 76.6695 | 180.4917 | 149.8841 | 111.3115 | 0.80627 | 0.45518 | 83.6366 | 21.8843 | 22.2058 | 21.0261 | 21.5458 | 22.0132 | 22.0102 | 22.8922 | 35.7422 | 21.8298 | 21.9706 | 27.5863 | 187.602 | 240.1806 | 150.4281 | 151.4997 | 101.3376 |  | 77.7334 | 155.2532 | 83.6391 | 135.8799 | 113.7787 | 88.164 |  | 101.6178 |  |  | 26.2272 | 32.2979 | 74.4596 | [5 empty] | 21.8878 | 99.986 | 21.7067 | 22.0971 | 38.7189 | 21.2883 | 21.9174 | 37.522 | 130.4618 | 269.8346 |  | 112.3236 | 177.3407 | 26.877 | 103.2328 | 198.3073 | 69.7536 | 153.3625 | 30.83 | 148.331 | 31.2728 | 145.6227 | 19.557 | 113.4174 | 173.0776 | 39.7323 | 104.5429 | 205.034 | 25.833 | 107.729 | 194.9073 | 26.5846 | 131.4445 | 42.3755 | 142.889 | 32.4187 | 155.272 | 1.7992 | 18.5726 | 2.1191 | 0.072 | -27.1318 | 3.0949 | 299.48 | 51.56 | 1.0004 | -0.54644 | -6.7147 | -0.59229 | 1.1518 | -15.2139 | 4.7188 | 0.20381 | -1.0705 | 0.65696 | -2.773 | -1.6247 | -1.0923 | -0.11318
42838.4265 | 534 | 22.888 | 22.8502 | 22.8379 | 22.759 | 22.3631 | 21.6903 | 22.6898 | 21.7448 | 22.3432 | 22.3513 | 22.3204 | 21.9668 | 21.1796 | 22.1557 | 21.588 | 21.7576 | 21.896 | 21.061 | 21.195 | 21.7853 | 20.4713 | 21.3433 | 26.1041 | 21.9104 | 22.3339 | 30.294 | 191.8022 | 170.3377 | 201.5739 | 22.1147 | 22.1926 | 27.8908 | 22.0427 | 22.3535 | 30.2757 | 89.4448 | 217.5115 |  | 130.6774 | 167.1197 | 165.005 | 163.9151 |  | 17.9361 | 19.1653 | 17.9946 | 19.234 | 20.2926 | 38.1019 | 147.0055 | 15.4339 | 17.3787 | 15.8089 | 19.2654 | 18.9006 | 45.7229 | 49.0948 | 44.8623 | 21.6628 |  |  | 0.70335 | -0.23597 | -31.7066 | 0.32194 | 0.71639 | -156.4832 | 14.6152 | 0.6883 | -0.01995 | 0.19481 | 0.61674 | 0.00036963 | 0.00036963 | 0.45424 | 21.9599 | 21.9686 | 22.1701 | 22.2148 | 22.0281 | 21.3107 | 20.13 | 22.1866 | 22.3623 | 22.4077 | 22.3528 | 21.9687 | 21.2009 | 22.2845 | 95.6095 | 56.9886 | 59.2401 | 45.4701 | 38.9251 | 65.7156 | 42.1987 | 22.3115 | 22.0816 | 21.6559 | 22.0473 | 21.7773 | 21.6558 | 21.9421 | 21.8596 | 26.3071 | 76.9058 | 180.739 | 150.2452 | 111.7423 | 1.8013 | 0.46393 | 83.9778 | 21.8917 | 22.2121 | 21.0422 | 21.5631 | 22.0169 | 22.0135 | 22.9053 | 35.8098 | 21.8328 | 21.9734 | 27.626 | 187.9388 | 240.8612 | 150.6568 | 151.7383 | 100.9785 |  | 77.9393 | 154.5152 | 83.8804 | 136.9448 | 114.3689 | 89.1339 |  | 101.867 |  |  | 26.2972 | 32.3816 | 74.4109 | [5 empty] | 21.8968 | 100.7258 | 21.703 | 22.1021 | 38.8178 | 21.2888 | 21.924 | 37.678 | 130.8437 | 270.553 |  | 112.4994 | 177.6873 | 26.9007 | 103.5328 | 199.3254 | 70.0809 | 153.7 | 30.8963 | 148.7623 | 31.3396 | 146.0509 | 19.5795 | 113.8823 | 173.716 | 39.8677 | 104.9815 | 205.1489 | 25.8857 | 108.0623 | 195.5265 | 26.6524 | 131.8981 | 42.541 | 143.2704 | 32.4879 | 155.7888 | 2.2581 | 18.5719 | 2.1232 | 0.071608 | -27.3092 | 3.095 | 294.56 | 52.84 | 1.2734 | -0.57879 | -6.7092 | 0.67605 | 1.0406 | -15.38 | 4.7003 | 0.22152 | -1.0408 | 0.65155 | -2.5739 | -1.3328 | -1.0885 | -0.11628
42838.4265 | 535 | 22.8901 | 22.8497 | 22.846 | 22.7616 | 22.37 | 21.6918 | 22.6895 | 21.7526 | 22.3454 | 22.3468 | 22.3209 | 21.9678 | 21.1875 | 22.154 | 21.603 | 21.7684 | 21.9054 | 21.0718 | 21.2123 | 21.7964 | 20.4781 | 21.3587 | 26.1483 | 21.9253 | 22.3569 | 30.3415 | 191.9907 | 170.7067 | 201.8039 | 22.119 | 22.1924 | 27.9125 | 22.044 | 22.3614 | 30.3109 | 89.8008 | 216.6525 |  | 131.0949 | 167.9112 | 165.5786 | 163.9805 |  | 17.9348 | 19.1814 | 17.9921 | 19.2384 | 20.299 | 38.1024 | 147.3538 | 15.4694 | 17.3788 | 15.7681 | 19.2645 | 18.9047 | 45.7255 | 49.1045 | 44.8858 | 21.666 |  |  | 0.83543 | -0.12952 | -32.1784 | 0.087354 | 0.34118 | -154.1603 | 14.7262 | 0.8644 | 0.10557 | 0.44573 | 0.58116 | 0.0003302 | 0.00031377 | 0.4537 | 21.9498 | 21.9645 | 22.1536 | 22.2062 | 22.0174 | 21.3066 | 20.1207 | 22.1782 | 22.3575 | 22.4044 | 22.3401 | 21.9608 | 21.1837 | 22.2769 | 95.5937 | 54.4706 | 57.515 | 43.0603 | 37.9567 | 65.8101 | 42.2587 | 22.3161 | 22.0795 | 21.6601 | 22.0473 | 21.7879 | 21.6643 | 21.9448 | 21.8606 | 26.3281 | 77.1496 | 180.7647 | 150.5795 | 112.3399 | 1.206 | 0.84129 | 84.672 | 21.8816 | 22.1986 | 21.0306 | 21.5583 | 22.0118 | 22.0067 | 22.9061 | 35.8647 | 21.8227 | 21.9768 | 27.6487 | 188.3861 | 241.1631 | 150.9499 | 152.0767 | 102.933 |  | 78.1791 | 155.3386 | 84.1401 | 140.4045 | 114.9941 | 89.3849 |  | 102.1267 |  |  | 26.3796 | 32.4661 | 74.442 | [5 empty] | 21.8969 | 102.3906 | 21.7028 | 22.1018 | 38.9011 | 21.2909 | 21.9233 | 37.8068 | 131.317 | 271.5214 |  | 112.8255 | 178.2265 | 26.9223 | 103.8749 | 200.0551 | 70.4753 | 154.3387 | 30.9293 | 149.2984 | 31.3976 | 146.8268 | 19.5791 | 114.1821 | 174.1177 | 40.007 | 105.4057 | 205.683 | 25.9119 | 108.1447 | 196.1312 | 26.7088 | 132.1744 | 42.6926 | 143.8053 | 32.5511 | 156.2217 | 2.4245 | 18.5673 | 2.1276 | 0.072029 | -27.2241 | 3.095 | 305.18 | 51.65 | 1.3882 | -0.42881 | -6.7591 | 0.35216 | 0.71815 | -15.2654 | 4.7181 | 0.17624 | -1.0537 | 0.58109 | -2.5608 | -1.134 | -1.0766 | -0.12374
42838.4265 | 536 | 22.8821 | 22.851 | 22.8378 | 22.7572 | 22.3682 | 21.6889 | 22.6922 | 21.739 | 22.3459 | 22.3484 | 22.3155 | 21.9586 | 21.1872 | 22.1584 | 21.5982 | 21.7692 | 21.9058 | 21.0761 | 21.2076 | 21.7965 | 20.4792 | 21.3619 | 26.1748 | 21.9256 | 22.3575 | 30.3838 | 192.4217 | 171.1753 | 203.0344 | 22.1219 | 22.1963 | 27.9499 | 22.0465 | 22.3663 | 30.3524 | 90.1436 | 217.7453 |  | 131.5398 | 168.6313 | 166.0334 | 163.0838 |  | 17.9335 | 19.1816 | 18.0034 | 19.2587 | 20.3655 | 38.2836 | 147.5534 | 15.5251 | 17.3832 | 15.6765 | 19.2754 | 18.9124 | 45.7221 | 49.1125 | 44.9033 | 21.6732 |  |  | 0.62515 | -0.17946 | -31.8703 | 0.20366 | 0.59022 | -151.7342 | 14.7262 | 0.84338 | 0.17348 | 0.29236 | 0.40339 | 0.00030063 | 7.4147 | 0.40947 | 21.9551 | 21.9616 | 22.1443 | 22.2167 | 22.0208 | 21.3085 | 20.1228 | 22.1735 | 22.3572 | 22.3953 | 22.3431 | 21.9616 | 21.1853 | 22.273 | 94.7093 | 53.2524 | 57.8743 | 42.1416 | 36.37 | 65.8911 | 42.3347 | 22.3075 | 22.0718 | 21.6494 | 22.048 | 21.7769 | 21.6664 | 21.9427 | 21.8644 | 26.3587 | 77.4282 | 180.7766 | 150.9742 | 112.6985 | 1.8109 | 0.77719 | 84.7081 | 21.8845 | 22.2054 | 21.0407 | 21.5597 | 22.0178 | 22.0156 | 22.911 | 35.9196 | 21.8269 | 21.9876 | 27.6802 | 188.9113 | 242.0128 | 151.2041 | 152.4687 | 105.6321 |  | 78.4703 | 156.4658 | 84.4444 | 139.034 | 115.6143 | 89.5006 |  | 102.4369 |  |  | 26.4279 | 32.5146 | 74.6034 | [5 empty] | 21.8943 | 104.3528 | 21.7048 | 22.1066 | 38.9627 | 21.2964 | 21.9265 | 37.9381 | 132.0085 | 272.858 |  | 113.3312 | 178.8677 | 26.9582 | 104.4885 | 200.8229 | 70.7865 | 155.1716 | 30.9935 | 149.4481 | 31.4565 | 147.4833 | 19.6075 | 114.3465 | 174.6276 | 40.1488 | 105.8788 | 205.9348 | 25.9701 | 108.5721 | 196.5438 | 26.7914 | 132.4798 | 42.8527 | 144.3872 | 32.6331 | 157.1803 | 2.0287 | 18.5635 | 2.1318 | 0.073292 | -27.3637 | 3.095 | 297.57 | 51.63 | 1.2024 | -0.50476 | -6.7266 | 0.53772 | 0.94484 | -15.1493 | 4.7195 | 0.11222 | -1.0735 | 0.64463 | -2.4528 | -1.1649 | -1.0384 | -0.12324
42838.4265 | 537 | 22.8931 | 22.8571 | 22.8415 | 22.7598 | 22.3617 | 21.6902 | 22.6924 | 21.7508 | 22.3385 | 22.3403 | 22.3191 | 21.9671 | 21.1898 | 22.1546 | 21.5895 | 21.7689 | 21.9012 | 21.0689 | 21.2003 | 21.796 | 20.4787 | 21.3631 | 26.1994 | 21.9181 | 22.3606 | 30.4161 | 192.8144 | 171.8123 | 203.6312 | 22.1155 | 22.2037 | 27.9835 | 22.0448 | 22.3715 | 30.389 | 90.4897 | 218.3427 |  | 131.9689 | 169.2726 | 166.3566 | 162.5469 |  | 17.9259 | 19.1903 | 18.0116 | 19.282 | 20.4603 | 38.5568 | 148.1015 | 15.5919 | 17.3848 | 15.6251 | 19.2955 | 18.9213 | 45.7339 | 49.1147 | 44.9182 | 21.6674 |  |  | 0.87879 | 0.012419 | -31.6521 | 0.36465 | 0.56525 | -154.751 | 14.4042 | 0.83418 | 0.24529 | 0.23362 | 0.47092 | 0.0002957 | 8.8809 | 0.38011 | 21.9579 | 21.9663 | 22.1559 | 22.212 | 22.0231 | 21.3107 | 20.1255 | 22.1825 | 22.3608 | 22.4046 | 22.3458 | 21.9581 | 21.1901 | 22.2766 | 95.1014 | 52.574 | 58.6719 | 41.9417 | 35.624 | 65.9836 | 42.4181 | 22.3106 | 22.079 | 21.6534 | 22.0372 | 21.7752 | 21.6626 | 21.9319 | 21.8597 | 26.3837 | 77.6702 | 180.9952 | 151.4027 | 113.3248 | 2.0189 | 0.21077 | 85.2546 | 21.9005 | 22.2118 | 21.0579 | 21.5609 | 22.0169 | 22.0192 | 22.9213 | 35.9855 | 21.8339 | 21.991 | 27.7154 | 189.3084 | 242.7918 | 151.3848 | 152.7478 | 105.8859 |  | 78.7198 | 157.1428 | 84.6963 | 138.8037 | 116.1525 | 89.5566 |  | 102.7294 |  |  | 26.4833 | 32.6103 | 74.733 | [5 empty] | 21.8994 | 105.6258 | 21.7095 | 22.1011 | 39.0572 | 21.2928 | 21.925 | 38.0761 | 132.679 | 272.7962 |  | 113.9962 | 179.5012 | 26.9454 | 104.867 | 201.4207 | 71.1607 | 155.7111 | 31.0839 | 149.5303 | 31.5286 | 147.6883 | 19.6195 | 114.3975 | 175.1369 | 40.268 | 106.4422 | 206.6856 | 26.0241 | 109.0537 | 197.01 | 26.8502 | 132.8353 | 42.9772 | 144.8956 | 32.7163 | 157.8333 | 2.5063 | 18.5581 | 2.1358 | 0.072965 | -27.1804 | 3.0949 | 307.73 | 52.52 | 1.4265 | 0.13279 | -6.7037 | 0.71953 | 0.92504 | -15.3058 | 4.6697 | 0.11457 | -1.0826 | 0.67316 | -2.4853 | -1.2437 | -1.0101 | -0.13155
42838.4265 | 538 | 22.8838 | 22.8536 | 22.8405 | 22.7547 | 22.3693 | 21.692 | 22.6891 | 21.7514 | 22.3378 | 22.3425 | 22.315 | 21.9683 | 21.1819 | 22.1502 | 21.5966 | 21.7755 | 21.9092 | 21.0723 | 21.2133 | 21.8003 | 20.4792 | 21.3724 | 26.2294 | 21.9243 | 22.3634 | 30.4606 | 193.2774 | 172.4025 | 204.5709 | 22.1224 | 22.2093 | 28.0165 | 22.0496 | 22.3607 | 30.4361 | 90.8738 | 220.4106 |  | 132.4785 | 169.9703 | 166.7189 | 161.889 |  | 17.9449 | 19.2119 | 18.0254 | 19.2942 | 20.4765 | 38.7005 | 148.8521 | 15.6341 | 17.3983 | 15.6261 | 19.3136 | 18.921 | 45.7337 | 49.1198 | 44.9201 | 21.6726 |  |  | 0.67115 | -0.072349 | -32.0661 | 0.094582 | 0.64148 | -155.5639 | 14.6585 | 0.8736 | 0.18886 | 0.36013 | 0.45426 | 0.00031706 | 8.881 | 0.40524 | 21.9565 | 21.9684 | 22.1577 | 22.2115 | 22.029 | 21.3094 | 20.1258 | 22.1907 | 22.3586 | 22.402 | 22.3525 | 21.9543 | 21.1901 | 22.2761 | 94.1297 | 52.2487 | 55.9841 | 42.4361 | 36.875 | 66.0738 | 42.4585 | 22.3099 | 22.0711 | 21.6525 | 22.0428 | 21.7769 | 21.667 | 21.9363 | 21.8646 | 26.4086 | 77.9302 | 181.4714 | 151.9929 | 114.5364 | 2.2766 | 0.23778 | 85.6914 | 21.898 | 22.2118 | 21.068 | 21.5598 | 22.0113 | 22.0207 | 22.9323 | 36.0441 | 21.8333 | 21.9911 | 27.7417 | 190.0647 | 243.5931 | 151.696 | 153.0544 | 105.5493 |  | 78.9624 | 157.1581 | 84.9416 | 140.2208 | 116.6767 | 89.3148 |  | 103.0055 |  |  | 26.5375 | 32.7114 | 75.1353 | [5 empty] | 21.8918 | 106.2391 | 21.705 | 22.0924 | 39.1386 | 21.2864 | 21.9226 | 38.1962 | 133.2895 | 272.9493 |  | 114.4938 | 180.1169 | 26.9437 | 104.9454 | 202.1843 | 71.6154 | 156.1964 | 31.1511 | 149.6693 | 31.5954 | 148.0634 | 19.6372 | 114.6307 | 175.5842 | 40.389 | 106.8966 | 207.614 | 26.0932 | 109.3646 | 197.8281 | 26.9163 | 133.2931 | 43.1117 | 145.5214 | 32.8129 | 158.4318 | 1.792 | 18.5553 | 2.1399 | 0.073023 | -27.1821 | 3.0949 | 308.31 | 51.77 | 1.2479 | -0.32051 | -6.7476 | 0.36646 | 0.98567 | -15.3495 | 4.7118 | 0.13305 | -1.0737 | 0.65539 | -2.3665 | -0.94027 | -0.97701 | -0.15543
42838.4265 | 539 | 22.8896 | 22.8561 | 22.8461 | 22.767 | 22.3729 | 21.6966 | 22.6936 | 21.7452 | 22.3429 | 22.3437 | 22.3251 | 21.9708 | 21.1934 | 22.1675 | 21.5945 | 21.7755 | 21.9044 | 21.0728 | 21.2112 | 21.8079 | 20.4802 | 21.3806 | 26.2542 | 21.9259 | 22.37 | 30.4998 | 193.8199 | 172.9305 | 205.4605 | 22.1239 | 22.2129 | 28.0428 | 22.0417 | 22.3756 | 30.4715 | 91.2288 | 219.3718 |  | 132.9669 | 170.5593 | 167.026 | 162.1092 |  | 17.9287 | 19.2153 | 18.0263 | 19.2979 | 20.4984 | 38.6644 | 149.3482 | 15.6638 | 17.391 | 15.642 | 19.3157 | 18.9203 | 45.7256 | 49.1072 | 44.9089 | 21.6545 |  |  | 0.55418 | -0.084177 | -32.0411 | -0.13344 | 0.48114 | -155.3759 | 14.8379 | 1.0234 | 0.1081 | 0.35929 | 0.57786 | 0.00029077 | 8.8809 | 0.40021 | 21.9518 | 21.9593 | 22.1544 | 22.2021 | 22.0228 | 21.301 | 20.1214 | 22.1799 | 22.3561 | 22.3943 | 22.3509 | 21.9516 | 21.1811 | 22.2688 | 94.4576 | 53.257 | 54.6084 | 42.2006 | 37.647 | 66.1782 | 42.4786 | 22.3122 | 22.0781 | 21.6618 | 22.048 | 21.7813 | 21.6754 | 21.939 | 21.8693 | 26.4459 | 78.1812 | 181.9102 | 152.553 | 115.548 | 1.6458 | 0.78099 | 85.2451 | 21.8964 | 22.2146 | 21.0583 | 21.5575 | 22.0236 | 22.0228 | 22.9445 | 36.0985 | 21.8313 | 22.0008 | 27.765 | 190.9875 | 244.6113 | 151.998 | 153.4135 | 106.5088 |  | 79.2064 | 157.6201 | 85.2064 | 139.0944 | 117.138 | 89.197 |  | 103.2869 |  |  | 26.5835 | 32.784 | 75.2727 | [5 empty] | 21.8965 | 105.945 | 21.702 | 22.0896 | 39.248 | 21.2924 | 21.9186 | 38.3422 | 133.8718 | 274.6066 |  | 114.6869 | 180.5876 | 26.9614 | 105.2482 | 202.9734 | 72.035 | 156.5909 | 31.2261 | 149.9275 | 31.6622 | 148.4186 | 19.6479 | 115.3137 | 176.157 | 40.534 | 107.3557 | 208.2156 | 26.16 | 109.7905 | 198.6884 | 26.9838 | 133.9343 | 43.2642 | 146.1932 | 32.9075 | 158.975 | 2.551 | 18.5494 | 2.1433 | 0.074366 | -27.2852 | 3.0949 | 319.19 | 52.79 | 1.135 | -0.34572 | -6.745 | -0.43528 | 0.85359 | -15.3394 | 4.7403 | 0.1156 | -1.0764 | 0.7057 | -2.3904 | -0.78504 | -0.96937 | -0.17409
42838.4265 | 540 | 22.8861 | 22.8576 | 22.8451 | 22.755 | 22.3727 | 21.6947 | 22.6955 | 21.7502 | 22.3436 | 22.3466 | 22.3244 | 21.9716 | 21.1822 | 22.1581 | 21.5972 | 21.7736 | 21.9057 | 21.072 | 21.2127 | 21.8122 | 20.4894 | 21.3816 | 26.285 | 21.9281 | 22.3764 | 30.5385 | 194.2499 | 173.1546 | 205.5519 | 22.1225 | 22.2211 | 28.0744 | 22.0465 | 22.3812 | 30.5169 | 91.5688 | 219.8236 |  | 133.4386 | 170.988 | 167.4966 | 161.6373 |  | 17.9397 | 19.2313 | 18.0356 | 19.3084 | 20.5779 | 38.7507 | 149.765 | 15.6452 | 17.397 | 15.734 | 19.3265 | 18.9283 | 45.7576 | 49.1195 | 44.9345 | 21.6689 |  |  | 0.78745 | -0.10192 | -31.8183 | 0.12481 | 0.65462 | -155.9654 | 14.7013 | 0.68304 | 0.14351 | 0.40712 | 0.63723 | 0.00030063 | 8.8808 | 0.39416 | 21.9511 | 21.9611 | 22.15 | 22.201 | 22.0141 | 21.3018 | 20.117 | 22.1759 | 22.3491 | 22.3968 | 22.3394 | 21.9538 | 21.1884 | 22.2664 | 95.2937 | 56.1014 | 57.4179 | 42.6422 | 38.4767 | 66.3042 | 42.5375 | 22.3229 | 22.0836 | 21.6671 | 22.0521 | 21.7848 | 21.6829 | 21.9481 | 21.8761 | 26.482 | 78.4424 | 182.0399 | 153.0045 | 115.616 | 1.6458 | 1.0574 | 85.0007 | 21.8939 | 22.2144 | 21.0732 | 21.557 | 22.0252 | 22.0223 | 22.9505 | 36.1668 | 21.8387 | 22.0062 | 27.8034 | 191.6078 | 245.6873 | 152.2175 | 153.6625 | 106.7657 |  | 79.4828 | 157.7962 | 85.488 | 138.1021 | 117.657 | 90.3973 |  | 103.6308 |  |  | 26.6461 | 32.8353 | 75.7577 | [5 empty] | 21.8957 | 105.581 | 21.7025 | 22.0928 | 39.3584 | 21.2917 | 21.9143 | 38.4786 | 134.4359 | 275.2142 |  | 115.0285 | 181.2387 | 26.9757 | 105.7802 | 203.5969 | 72.3499 | 157.1758 | 31.3013 | 150.2809 | 31.7284 | 148.9145 | 19.6368 | 116.081 | 176.7782 | 40.6608 | 107.7157 | 208.7254 | 26.1968 | 110.322 | 199.6718 | 27.0295 | 134.3993 | 43.4004 | 146.4027 | 32.9795 | 159.4083 | 1.9613 | 18.5465 | 2.1475 | 0.075288 | -27.309 | 3.095 | 324.75 | 51.54 | 1.353 | -0.38042 | -6.7217 | 0.42098 | 0.99579 | -15.3705 | 4.719 | 0.11889 | -1.0705 | 0.75469 | -2.4682 | -1.0902 | -0.94308 | -0.16616
42838.4265 | 541 | 22.8892 | 22.8536 | 22.8445 | 22.7573 | 22.3653 | 21.6948 | 22.6879 | 21.7547 | 22.3416 | 22.3451 | 22.3214 | 21.98 | 21.1848 | 22.1563 | 21.5985 | 21.7703 | 21.9045 | 21.0706 | 21.2141 | 21.8136 | 20.4828 | 21.3828 | 26.3105 | 21.9305 | 22.3767 | 30.5728 | 194.6243 | 173.3642 | 205.0207 | 22.1159 | 22.2189 | 28.105 | 22.0427 | 22.3887 | 30.5531 | 91.897 | 219.3579 |  | 133.8982 | 171.4794 | 168.1042 | 162.4479 |  | 17.9559 | 19.2554 | 18.0558 | 19.3301 | 20.6357 | 38.7789 | 150.3833 | 15.6419 | 17.4024 | 15.8089 | 19.348 | 18.9349 | 45.7688 | 49.1096 | 44.9507 | 21.6578 |  |  | 0.74014 | -0.043437 | -31.317 | 0.079466 | 0.52648 | -153.747 | 14.604 | 0.78358 | 0.18633 | 0.32006 | 0.52578 | 0.00032527 | 8.8811 | 0.40012 | 21.9585 | 21.9655 | 22.1557 | 22.2107 | 22.0128 | 21.3029 | 20.1258 | 22.1855 | 22.3555 | 22.3905 | 22.3439 | 21.9567 | 21.1823 | 22.2765 | 97.1019 | 60.1802 | 60.9773 | 44.021 | 37.8114 | 66.4834 | 42.6173 | 22.3185 | 22.076 | 21.651 | 22.0463 | 21.7816 | 21.6807 | 21.9421 | 21.8729 | 26.4991 | 78.7182 | 182.5366 | 153.4952 | 115.0161 | 2.4864 | 1.5481 | 85.1173 | 21.9094 | 22.2265 | 21.0859 | 21.5656 | 22.0204 | 22.0281 | 22.9597 | 36.2312 | 21.8446 | 22.0163 | 27.8416 | 192.3364 | 245.9929 | 152.6122 | 154.1425 | 107.4898 |  | 79.7503 | 158.0339 | 85.7211 | 140.5159 | 118.2304 | 90.3588 |  | 103.9253 |  |  | 26.6934 | 32.8951 | 76.0705 | [5 empty] | 21.8898 | 105.7977 | 21.7007 | 22.0932 | 39.3858 | 21.284 | 21.9116 | 38.6325 | 134.9609 | 275.747 |  | 115.5988 | 182.125 | 26.9866 | 106.2575 | 204.0336 | 72.6461 | 157.8972 | 31.3769 | 150.6121 | 31.8048 | 149.2773 | 19.6437 | 116.5558 | 177.0781 | 40.7799 | 108.0701 | 209.223 | 26.2407 | 110.7211 | 200.3886 | 27.0514 | 134.7889 | 43.5816 | 146.528 | 33.04 | 159.7023 | 2.304 | 18.543 | 2.1507 | 0.074483 | -27.2354 | 3.095 | 317.91 | 52.13 | 1.311 | -0.24836 | -6.6688 | 0.33593 | 0.89307 | -15.2615 | 4.7036 | 0.10887 | -1.0682 | 0.71135 | -2.6476 | -1.4763 | -0.95286 | -0.13911
42838.4266 | 542 | 22.8903 | 22.8537 | 22.8439 | 22.7571 | 22.3646 | 21.7031 | 22.6893 | 21.7547 | 22.3451 | 22.3492 | 22.3212 | 21.9719 | 21.1859 | 22.1589 | 21.592 | 21.7661 | 21.9042 | 21.0684 | 21.2134 | 21.8142 | 20.4792 | 21.3952 | 26.3334 | 21.9256 | 22.3844 | 30.6056 | 194.9794 | 173.637 | 205.2324 | 22.1167 | 22.2231 | 28.1317 | 22.044 | 22.3929 | 30.5882 | 92.2546 | 219.7786 |  | 134.323 | 171.9483 | 168.7367 | 163.1505 |  | 17.9545 | 19.2794 | 18.0501 | 19.3505 | 20.6838 | 38.6414 | 150.6956 | 15.6119 | 17.4021 | 15.8673 | 19.3508 | 18.9521 | 45.7985 | 49.1084 | 44.9617 | 21.6679 |  |  | 0.68495 | 0.043963 | -31.2197 | 0.24243 | 0.4634 | -154.293 | 14.9621 | 0.85455 | 0.24977 | 0.12368 | 0.4645 | 0.0002727 | 8.881 | 0.36338 | 21.9568 | 21.9555 | 22.1449 | 22.1966 | 22.0091 | 21.292 | 20.1099 | 22.1809 | 22.3512 | 22.3858 | 22.3353 | 21.9509 | 21.1759 | 22.2622 | 100.1427 | 64.7849 | 66.9382 | 44.661 | 36.94 | 66.6823 | 42.7439 | 22.3117 | 22.075 | 21.652 | 22.0447 | 21.7771 | 21.676 | 21.9322 | 21.8682 | 26.5258 | 78.9519 | 183.0123 | 153.8616 | 114.9106 | 1.884 | 2.0443 | 85.4908 | 21.8895 | 22.2206 | 21.0857 | 21.5621 | 22.0213 | 22.0224 | 22.9565 | 36.2843 | 21.8341 | 22.0139 | 27.8608 | 192.7325 | 246.5078 | 153.0152 | 154.5523 | 107.7188 |  | 80.0505 | 158.9403 | 85.9825 | 144.7494 | 118.7883 | 90.8512 |  | 104.2154 |  |  | 26.7409 | 32.9812 | 76.9302 | [5 empty] | 21.8871 | 106.0902 | 21.7016 | 22.0936 | 39.4134 | 21.2935 | 21.9156 | 38.7791 | 135.5533 | 276.8227 |  | 116.0419 | 182.9539 | 27.0096 | 106.6458 | 204.5538 | 73.0068 | 158.3771 | 31.4251 | 151.2526 | 31.8965 | 149.6966 | 19.6742 | 116.7567 | 177.3867 | 40.9036 | 108.6265 | 209.9416 | 26.3148 | 111.0106 | 201.202 | 27.0915 | 135.2728 | 43.7653 | 146.7522 | 33.1076 | 160.2323 | 2.2275 | 18.5371 | 2.1537 | 0.072857 | -27.236 | 3.0949 | 329.91 | 51.77 | 1.2615 | 0.24987 | -6.6587 | 0.58677 | 0.83768 | -15.2852 | 4.7599 | 0.11384 | -1.0834 | 0.61685 | -2.9616 | -2.1236 | -0.9585 | -0.12737
42838.4266 | 543 | 22.8922 | 22.851 | 22.8407 | 22.7524 | 22.3688 | 21.6924 | 22.6974 | 21.7558 | 22.3406 | 22.3478 | 22.3188 | 21.9678 | 21.1828 | 22.1529 | 21.5897 | 21.7722 | 21.9108 | 21.0761 | 21.2144 | 21.8288 | 20.4903 | 21.3965 | 26.3708 | 21.9321 | 22.3971 | 30.6477 | 195.381 | 173.9268 | 206.0352 | 22.123 | 22.2254 | 28.1645 | 22.0497 | 22.3876 | 30.6258 | 92.5793 | 221.0074 |  | 134.7262 | 172.4599 | 169.2179 | 163.6837 |  | 17.9414 | 19.2848 | 18.0514 | 19.3661 | 20.7093 | 38.4402 | 150.3748 | 15.6078 | 17.403 | 15.9027 | 19.3597 | 18.9429 | 45.8099 | 49.1031 | 44.9528 | 21.6539 |  |  | 0.70729 | -0.051977 | -31.0022 | 0.49279 | 0.31949 | -158.5327 | 14.2912 | 0.68107 | 0.19606 | 0.33516 | 0.62976 | 0.0002842 | 8.881 | 0.32414 | 21.9643 | 21.966 | 22.1501 | 22.2049 | 22.0146 | 21.3094 | 20.1214 | 22.1816 | 22.3594 | 22.3904 | 22.3456 | 21.956 | 21.1817 | 22.274 | 101.8089 | 67.0705 | 71.0026 | 45.9325 | 37.645 | 66.8595 | 42.907 | 22.3158 | 22.0836 | 21.6594 | 22.0515 | 21.7862 | 21.6877 | 21.9448 | 21.8771 | 26.5601 | 79.2041 | 183.2443 | 154.1977 | 114.934 | 1.6709 | 1.3908 | 85.7691 | 21.8771 | 22.2011 | 21.0792 | 21.5573 | 22.0136 | 22.0136 | 22.9701 | 36.3363 | 21.8324 | 22.0099 | 27.8846 | 192.968 | 246.911 | 153.5585 | 155.0122 | 108.6804 |  | 80.3736 | 158.1856 | 86.2968 | 144.0314 | 119.2799 | 91.1758 |  | 104.5705 |  |  | 26.774 | 33.0525 | 77.7537 | [5 empty] | 21.8925 | 106.1905 | 21.7031 | 22.102 | 39.4982 | 21.2921 | 21.9218 | 38.904 | 136.2682 | 278.5855 |  | 116.4088 | 183.4008 | 27.0284 | 106.9924 | 205.0992 | 73.4256 | 159.1656 | 31.4628 | 151.8591 | 31.9756 | 150.155 | 19.7073 | 116.9041 | 177.8872 | 41.0393 | 109.2064 | 210.1419 | 26.3845 | 111.3826 | 201.8077 | 27.1587 | 135.9372 | 43.9035 | 147.1831 | 33.1872 | 160.9635 | 1.8628 | 18.5352 | 2.1588 | 0.072719 | -27.221 | 3.0949 | 327.91 | 51.75 | 1.283 | -0.2717 | -6.6356 | 0.83659 | 0.69532 | -15.4888 | 4.6504 | 0.099339 | -1.0504 | 0.65718 | -3.1255 | -2.556 | -0.96069 | -0.11852
42838.4266 | 544 | 22.895 | 22.8589 | 22.8489 | 22.7616 | 22.371 | 21.6973 | 22.7 | 21.7542 | 22.344 | 22.347 | 22.3269 | 21.9737 | 21.1889 | 22.1525 | 21.5999 | 21.7709 | 21.913 | 21.0803 | 21.2059 | 21.8274 | 20.4855 | 21.4065 | 26.3923 | 21.9225 | 22.3979 | 30.686 | 195.7767 | 174.2612 | 206.7058 | 22.1241 | 22.2311 | 28.1944 | 22.0569 | 22.4011 | 30.6688 | 92.9381 | 222.0317 |  | 135.1531 | 173.0207 | 169.7209 | 165.7883 |  | 17.9585 | 19.3158 | 18.0727 | 19.3813 | 20.7507 | 38.3465 | 150.8121 | 15.6923 | 17.4189 | 15.8798 | 19.3801 | 18.9498 | 45.8393 | 49.1075 | 44.9577 | 21.6515 |  |  | 1.0523 | -0.37528 | -30.995 | 0.26675 | 0.39637 | -158.0773 | 14.6007 | 0.75335 | 0.14215 | 0.27579 | 0.58689 | 0.00030885 | 8.8809 | 0.30685 | 21.965 | 21.9623 | 22.1562 | 22.2036 | 22.0242 | 21.3064 | 20.1155 | 22.1726 | 22.3606 | 22.3947 | 22.3478 | 21.9602 | 21.1859 | 22.2803 | 100.2722 | 66.1402 | 69.2428 | 45.6673 | 38.1529 | 66.9788 | 43.035 | 22.3168 | 22.074 | 21.6529 | 22.0477 | 21.7845 | 21.6883 | 21.9413 | 21.8778 | 26.5908 | 79.4476 | 183.2266 | 154.5004 | 115.3703 | 1.6367 | 0.97652 | 85.9234 | 21.8859 | 22.2107 | 21.0798 | 21.5624 | 22.0185 | 22.0192 | 22.9813 | 36.397 | 21.8311 | 22.01 | 27.9264 | 193.6493 | 247.0659 | 154.1454 | 155.4907 | 108.6731 |  | 80.6229 | 157.3249 | 86.5233 | 144.5669 | 119.7811 | 90.9723 |  | 104.857 |  |  | 26.8086 | 33.1427 | 77.8471 | [5 empty] | 21.8937 | 107.624 | 21.6998 | 22.0961 | 39.5562 | 21.2828 | 21.9267 | 39.0172 | 136.9406 | 278.9268 |  | 116.6778 | 183.4229 | 27.0513 | 107.2003 | 205.6482 | 73.7271 | 159.7838 | 31.5337 | 152.3181 | 32.0557 | 150.5975 | 19.7449 | 117.1308 | 178.6184 | 41.1766 | 109.7458 | 210.3436 | 26.4453 | 111.7877 | 202.738 | 27.2117 | 136.4616 | 44.0238 | 147.6367 | 33.2687 | 161.8683 | 1.9949 | 18.5313 | 2.1641 | 0.073945 | -27.2427 | 3.0949 | 319.46 | 53.29 | 1.566 | -0.7301 | -6.6351 | 0.61554 | 0.77436 | -15.4642 | 4.6998 | 0.10897 | -1.0178 | 0.66311 | -2.9404 | -2.3453 | -1.0052 | -0.12146
42838.4266 | 545 | 22.8901 | 22.8572 | 22.8344 | 22.7609 | 22.372 | 21.6948 | 22.6882 | 21.7518 | 22.3546 | 22.3558 | 22.3229 | 21.9737 | 21.1877 | 22.1621 | 21.5983 | 21.7713 | 21.913 | 21.0817 | 21.2083 | 21.8307 | 20.4901 | 21.4071 | 26.4265 | 21.9227 | 22.4009 | 30.7263 | 196.4085 | 174.6869 | 206.9186 | 22.1168 | 22.2198 | 28.2216 | 22.0442 | 22.4036 | 30.7078 | 93.3556 | 224.0586 |  | 135.6167 | 173.5787 | 170.281 | 169.2106 |  | 17.956 | 19.3353 | 18.0745 | 19.4097 | 20.8389 | 38.8499 | 151.6097 | 15.737 | 17.4206 | 15.8532 | 19.3939 | 18.9492 | 45.8672 | 49.1031 | 44.9582 | 21.6566 |  |  | 0.6442 | -0.26422 | -31.2164 | 0.47111 | 0.71442 | -154.9284 | 14.6769 | 1.0734 | 0.21007 | 0.33999 | 0.73913 | 0.0002842 | 8.8812 | 0.25683 | 21.9599 | 21.96 | 22.1503 | 22.205 | 22.0207 | 21.3012 | 20.1125 | 22.1743 | 22.3577 | 22.3893 | 22.3391 | 21.9569 | 21.1843 | 22.2697 | 97.6191 | 64.1595 | 68.5243 | 44.704 | 38.1831 | 67.0888 | 43.1573 | 22.3107 | 22.0768 | 21.6532 | 22.0385 | 21.7826 | 21.6895 | 21.9415 | 21.8757 | 26.6111 | 79.7189 | 183.1562 | 154.8053 | 115.9773 | 1.886 | 0.61438 | 86.1946 | 21.8981 | 22.2136 | 21.0837 | 21.5602 | 22.0235 | 22.0218 | 22.9928 | 36.4593 | 21.8376 | 22.0212 | 27.9571 | 194.3752 | 247.7911 | 154.6751 | 155.9204 | 108.0336 |  | 80.8615 | 157.5525 | 86.7657 | 143.574 | 120.3104 | 91.1325 |  | 105.1043 |  |  | 26.8382 | 33.2578 | 77.7519 | [5 empty] | 21.892 | 110.1808 | 21.703 | 22.0972 | 39.6173 | 21.2886 | 21.9233 | 39.1705 | 137.4703 | 279.5531 |  | 116.9865 | 183.6437 | 27.0679 | 107.7165 | 206.3944 | 74.1215 | 160.151 | 31.5838 | 153.0158 | 32.1217 | 151.0423 | 19.7871 | 117.4318 | 179.2368 | 41.3364 | 110.2352 | 210.5933 | 26.4864 | 112.0222 | 203.5846 | 27.2713 | 136.8352 | 44.215 | 148.1444 | 33.3456 | 162.4914 | 2.1871 | 18.5298 | 2.1689 | 0.074112 | -27.1982 | 3.095 | 315.66 | 51.8 | 1.2255 | -0.61264 | -6.659 | 0.81805 | 1.0404 | -15.3218 | 4.7159 | 0.13576 | -1.0148 | 0.71269 | -2.6324 | -2.251 | -1.084 | -0.12808
42838.4266 | 546 | 22.8991 | 22.8598 | 22.8419 | 22.7622 | 22.3763 | 21.6958 | 22.706 | 21.7566 | 22.3433 | 22.3474 | 22.328 | 21.972 | 21.1873 | 22.1689 | 21.6015 | 21.773 | 21.9209 | 21.0794 | 21.2214 | 21.8392 | 20.4846 | 21.4216 | 26.4601 | 21.9464 | 22.4129 | 30.7741 | 196.8571 | 175.2759 | 207.4844 | 22.1187 | 22.2373 | 28.2507 | 22.0452 | 22.4101 | 30.7413 | 93.7402 | 227.6684 |  | 136.134 | 174.1633 | 171.035 | 170.4787 |  | 17.96 | 19.3525 | 18.086 | 19.4342 | 20.9097 | 38.8975 | 152.3416 | 15.7608 | 17.4206 | 15.8865 | 19.4049 | 18.9639 | 45.8907 | 49.1051 | 44.9695 | 21.6587 |  |  | 0.50818 | -0.12886 | -31.2802 | 0.41065 | 0.40163 | -153.8475 | 14.7821 | 0.74152 | 0.10245 | 0.18033 | 0.56692 | 0.00028585 | 8.8811 | 0.22621 | 21.9654 | 21.9634 | 22.1504 | 22.2052 | 22.0087 | 21.2974 | 20.1111 | 22.1803 | 22.3606 | 22.3942 | 22.3388 | 21.9564 | 21.1841 | 22.2678 | 101.1392 | 61.8284 | 65.0006 | 44.4884 | 38.0892 | 67.2991 | 43.2266 | 22.328 | 22.08 | 21.6586 | 22.0494 | 21.7928 | 21.6914 | 21.9421 | 21.8874 | 26.6445 | 79.9912 | 183.4415 | 155.1955 | 116.0593 | 2.254 | 1.825 | 85.989 | 21.8959 | 22.2061 | 21.0879 | 21.5598 | 22.0154 | 22.0283 | 23.0034 | 36.5181 | 21.8372 | 22.022 | 27.989 | 195.0005 | 248.456 | 155.0596 | 156.3818 | 108.922 |  | 81.1327 | 159.0662 | 87.044 | 141.7307 | 120.8256 | 90.8915 |  | 105.4025 |  |  | 26.8689 | 33.3079 | 77.6925 | [5 empty] | 21.897 | 110.4298 | 21.6987 | 22.1004 | 39.6883 | 21.2946 | 21.9224 | 39.3278 | 137.926 | 281.5417 |  | 117.5053 | 184.266 | 27.1299 | 108.1572 | 207.4306 | 74.6066 | 160.7105 | 31.6659 | 153.29 | 32.1939 | 151.4694 | 19.7768 | 117.6073 | 179.7243 | 41.5234 | 110.7771 | 210.6979 | 26.5008 | 112.3357 | 204.0498 | 27.3663 | 137.0704 | 44.4437 | 148.4858 | 33.4213 | 163.0268 | 2.3199 | 18.5243 | 2.1744 | 0.073931 | -27.1682 | 3.095 | 305.87 | 51.93 | 1.0891 | -0.42785 | -6.666 | 0.76378 | 0.78017 | -15.2694 | 4.7331 | 0.12135 | -1.0462 | 0.78533 | -2.9983 | -1.8513 | -1.1043 | -0.12008
42838.4266 | 547 | 22.8883 | 22.8587 | 22.8405 | 22.7638 | 22.3682 | 21.6957 | 22.6958 | 21.7552 | 22.3487 | 22.3481 | 22.3168 | 21.9718 | 21.1867 | 22.1561 | 21.5961 | 21.7571 | 21.8991 | 21.0781 | 21.2074 | 21.836 | 20.4767 | 21.4151 | 26.4808 | 21.9246 | 22.4107 | 30.8043 | 197.1331 | 175.81 | 208.8154 | 22.1169 | 22.2328 | 28.2785 | 22.0388 | 22.4008 | 30.7792 | 94.0927 | 228.409 |  | 136.6304 | 174.5534 | 171.8022 | 170.872 |  | 17.9556 | 19.3692 | 18.0874 | 19.4516 | 20.9394 | 38.7066 | 152.7514 | 15.7479 | 17.4158 | 15.9999 | 19.407 | 18.9627 | 45.9033 | 49.1016 | 44.9818 | 21.6521 |  |  | 0.81703 | -0.33454 | -31.497 | 0.26543 | 0.60665 | -158.7824 | 14.3589 | 0.79804 | 0.0074882 | 0.25712 | 0.56466 | 0.00029242 | 8.8811 | 0.21885 | 21.9685 | 21.9586 | 22.1463 | 22.2034 | 22.0152 | 21.2967 | 20.119 | 22.1815 | 22.36 | 22.3898 | 22.3417 | 21.9585 | 21.1821 | 22.2723 | 103.4218 | 65.7738 | 70.1185 | 45.366 | 37.5085 | 67.4898 | 43.3971 | 22.3277 | 22.0849 | 21.6664 | 22.0552 | 21.7988 | 21.7073 | 21.9504 | 21.8939 | 26.6802 | 80.2538 | 183.6911 | 155.5495 | 116.9373 | 1.5887 | 1.1144 | 86.5973 | 21.8853 | 22.2044 | 21.0931 | 21.5579 | 22.0085 | 22.0226 | 23.0133 | 36.5733 | 21.8289 | 22.0274 | 28.0096 | 195.4186 | 249.2565 | 155.3807 | 156.7418 | 108.2932 |  | 81.3953 | 159.9015 | 87.2941 | 144.1936 | 121.4838 | 90.9738 |  | 105.714 |  |  | 26.8958 | 33.3324 | 77.7336 | [5 empty] | 21.8943 | 110.1872 | 21.7023 | 22.1039 | 39.8031 | 21.29 | 21.9153 | 39.4986 | 138.5484 | 281.7796 |  | 117.9565 | 184.8697 | 27.1845 | 108.6032 | 207.8447 | 74.9731 | 161.4212 | 31.7291 | 153.5911 | 32.2684 | 151.8668 | 19.7664 | 117.8518 | 180.4303 | 41.6929 | 111.2578 | 210.6368 | 26.5557 | 112.6538 | 204.9258 | 27.4263 | 137.388 | 44.672 | 149.3598 | 33.4967 | 163.5293 | 2.5822 | 18.5204 | 2.1803 | 0.074236 | -27.1961 | 3.0949 | 300.58 | 52.31 | 1.3829 | -0.68939 | -6.6893 | 0.61407 | 0.95855 | -15.5076 | 4.6634 | 0.14876 | -1.0598 | 0.74435 | -3.229 | -2.3998 | -1.1014 | -0.13455
42838.4266 | 548 | 22.8858 | 22.8514 | 22.8368 | 22.7612 | 22.3689 | 21.6915 | 22.6876 | 21.7477 | 22.3439 | 22.3531 | 22.3219 | 21.9745 | 21.186 | 22.1558 | 21.5941 | 21.7669 | 21.9132 | 21.0741 | 21.2061 | 21.8344 | 20.4786 | 21.4214 | 26.5059 | 21.9279 | 22.4091 | 30.8411 | 197.7124 | 176.2164 | 211.0833 | 22.1199 | 22.2375 | 28.3159 | 22.0423 | 22.4124 | 30.8271 | 94.4863 | 229.4526 |  | 137.1122 | 174.9719 | 172.4566 | 171.3451 |  | 17.9607 | 19.3796 | 18.0912 | 19.4675 | 20.9609 | 39.215 | 152.7864 | 15.7306 | 17.4291 | 16.0316 | 19.4171 | 18.9669 | 45.911 | 49.1091 | 44.9773 | 21.6616 |  |  | 0.95173 | -0.007949 | -31.8315 | 0.60187 | 0.36483 | -155.0342 | 14.1591 | 0.9426 | -0.068211 | 0.24264 | 0.54921 | 0.0002727 | 8.8809 | 0.22292 | 21.9643 | 21.9501 | 22.1495 | 22.1936 | 22.0117 | 21.292 | 20.1191 | 22.1726 | 22.3516 | 22.3884 | 22.3356 | 21.9519 | 21.1804 | 22.2628 | 102.1285 | 66.9531 | 67.2848 | 44.8832 | 38.4882 | 67.6356 | 43.5044 | 22.3206 | 22.0822 | 21.666 | 22.0495 | 21.7942 | 21.7024 | 21.9464 | 21.8932 | 26.7027 | 80.5136 | 183.9133 | 155.9521 | 118.0272 | 1.1546 | 0.96035 | 87.1099 | 21.892 | 22.2008 | 21.1007 | 21.5587 | 22.0187 | 22.0297 | 23.0098 | 36.6266 | 21.8349 | 22.0228 | 28.0464 | 196.2667 | 250.517 | 155.6374 | 157.0232 | 108.8172 |  | 81.6925 | 159.7943 | 87.5534 | 144.6668 | 122.1166 | 91.1948 |  | 105.9514 |  |  | 26.9232 | 33.4198 | 80.0278 | [5 empty] | 21.8876 | 111.1385 | 21.7042 | 22.0913 | 39.8982 | 21.2889 | 21.9084 | 39.665 | 139.188 | 283.0045 |  | 118.1742 | 185.4107 | 27.2369 | 109.3103 | 209.1591 | 75.2969 | 162.1707 | 31.8477 | 153.8497 | 32.3331 | 152.5777 | 19.7631 | 118.0685 | 181.0171 | 41.8561 | 111.69 | 211.6107 | 26.6175 | 112.781 | 206.1506 | 27.4749 | 137.789 | 44.8794 | 150.0957 | 33.5911 | 164.167 | 2.5614 | 18.5137 | 2.1862 | 0.074105 | -27.2215 | 3.0949 | 301.33 | 51.84 | 1.4961 | -0.10627 | -6.7248 | 0.92471 | 0.74395 | -15.336 | 4.6346 | 0.14547 | -1.0469 | 0.75763 | -3.0678 | -2.0722 | -1.0992 | -0.155
42838.4266 | 549 | 22.8809 | 22.8546 | 22.8302 | 22.7545 | 22.3668 | 21.6908 | 22.6823 | 21.7478 | 22.3443 | 22.3364 | 22.3168 | 21.9674 | 21.1786 | 22.1497 | 21.5876 | 21.7708 | 21.9039 | 21.0673 | 21.213 | 21.8444 | 20.4787 | 21.4301 | 26.5391 | 21.9275 | 22.417 | 30.878 | 198.3621 | 176.3158 | 211.7173 | 22.1236 | 22.2423 | 28.3472 | 22.042 | 22.4207 | 30.8652 | 94.9066 | 230.817 |  | 137.611 | 175.5267 | 173.0399 | 173.084 |  | 17.9717 | 19.414 | 18.0905 | 19.4907 | 21.0782 | 39.9395 | 152.4311 | 15.7073 | 17.4504 | 16.0243 | 19.4402 | 18.98 | 45.8921 | 49.1014 | 44.9851 | 21.6599 |  |  | 0.71123 | -0.079577 | -32.0175 | 0.28975 | 0.56 | -156.5095 | 13.6801 | 0.75269 | -0.071909 | 0.25775 | 0.55373 | 0.00027106 | 8.881 | 0.21514 | 21.9792 | 21.9666 | 22.1566 | 22.2086 | 22.0184 | 21.3037 | 20.1142 | 22.1822 | 22.3578 | 22.3907 | 22.346 | 21.9598 | 21.1788 | 22.2765 | 100.9101 | 66.8119 | 65.7745 | 44.2496 | 38.3591 | 67.7487 | 43.5962 | 22.3166 | 22.083 | 21.6662 | 22.0473 | 21.7861 | 21.701 | 21.9336 | 21.8901 | 26.7254 | 80.7765 | 184.1716 | 156.3805 | 118.1768 | 1.0225 | 0.45271 | 87.3023 | 21.8985 | 22.2126 | 21.1063 | 21.5591 | 22.0196 | 22.0375 | 23.0214 | 36.6965 | 21.8443 | 22.0332 | 28.0736 | 197.4792 | 251.7625 | 155.7739 | 157.2549 | 109.0811 |  | 82.0077 | 160.5554 | 87.8078 | 142.8916 | 122.779 | 91.5566 |  | 106.2617 |  |  | 26.9326 | 33.489 | 80.542 | [5 empty] | 21.8965 | 111.434 | 21.7006 | 22.0889 | 40.0221 | 21.2882 | 21.9234 | 39.859 | 139.7827 | 283.1728 |  | 118.3725 | 185.9993 | 27.3117 | 109.8287 | 209.9049 | 75.5499 | 163.2939 | 31.991 | 154.2036 | 32.3921 | 152.9826 | 19.7745 | 118.5175 | 181.5859 | 42.0467 | 112.0675 | 212.3854 | 26.6697 | 112.8175 | 206.8128 | 27.5061 | 138.2672 | 45.0469 | 150.3726 | 33.6758 | 164.6558 | 2.3572 | 18.5075 | 2.1919 | 0.073118 | -27.1572 | 3.0949 | 305.2 | 52.97 | 1.2941 | -0.33626 | -6.7448 | 0.64163 | 0.92277 | -15.4266 | 4.5609 | 0.15009 | -1.0582 | 0.83464 | -2.9189 | -1.8935 | -1.1311 | -0.14921
42838.4266 | 550 | 22.8848 | 22.8625 | 22.8358 | 22.751 | 22.3672 | 21.6959 | 22.6856 | 21.7515 | 22.3505 | 22.3472 | 22.3232 | 21.9645 | 21.1823 | 22.1472 | 21.5897 | 21.7683 | 21.9043 | 21.0715 | 21.2074 | 21.8411 | 20.4819 | 21.4347 | 26.5626 | 21.929 | 22.4196 | 30.9159 | 199.0964 | 176.6404 | 212.3771 | 22.1207 | 22.2505 | 28.3786 | 22.0433 | 22.4243 | 30.908 | 95.3054 | 233.358 |  | 138.1529 | 175.9172 | 173.7479 | 173.6217 |  | 17.9679 | 19.4222 | 18.0995 | 19.4875 | 21.1719 | 39.7729 | 152.2855 | 15.6844 | 17.4496 | 16.0479 | 19.4539 | 18.9819 | 45.8792 | 49.0958 | 44.977 | 21.6526 |  |  | 0.62055 | -0.073661 | -32.0227 | 0.52433 | 0.49626 | -156.5515 | 14.2603 | 0.78226 | 0.42666 | 0.42433 | 0.85631 | 0.0002842 | 8.8811 | 0.20412 | 21.972 | 21.9564 | 22.1552 | 22.2025 | 22.0136 | 21.3049 | 20.1122 | 22.1746 | 22.3579 | 22.3909 | 22.3458 | 21.9608 | 21.1784 | 22.2755 | 98.1274 | 64.4265 | 62.3081 | 43.0858 | 38.6041 | 67.8339 | 43.6483 | 22.321 | 22.0808 | 21.6554 | 22.0449 | 21.782 | 21.7061 | 21.9355 | 21.8943 | 26.7645 | 81.0751 | 184.8275 | 156.8839 | 118.6265 | 1.9904 | 0.70092 | 88.0381 | 21.9008 | 22.2101 | 21.1144 | 21.5737 | 22.019 | 22.0441 | 23.0354 | 36.76 | 21.8396 | 22.0442 | 28.1089 | 198.3277 | 253.4828 | 156.0573 | 157.585 | 109.4318 |  | 82.3016 | 161.8197 | 88.0768 | 140.7356 | 123.3861 | 91.7985 |  | 106.6418 |  |  | 26.973 | 33.5638 | 80.3441 | [5 empty] | 21.8958 | 111.1731 | 21.7068 | 22.0944 | 40.1284 | 21.2927 | 21.917 | 40.0142 | 140.5298 | 284.4765 |  | 118.6018 | 186.4672 | 27.3816 | 110.1742 | 210.862 | 76.0002 | 164.1952 | 32.0964 | 154.8431 | 32.4757 | 153.4038 | 19.757 | 119.2107 | 182.1519 | 42.2644 | 112.4633 | 212.9796 | 26.726 | 113.4057 | 207.2331 | 27.5309 | 138.9996 | 45.2478 | 150.8118 | 33.7703 | 165.2531 | 2.8955 | 18.5016 | 2.1976 | 0.071056 | -27.2481 | 3.0949 | 312.71 | 51.86 | 1.2097 | -0.32352 | -6.7455 | 0.86315 | 0.86844 | -15.4246 | 4.6553 | 0.1515 | -1.083 | 0.91996 | -2.5994 | -1.5022 | -1.1304 | -0.15041
42838.4267 | 551 | 22.8797 | 22.8537 | 22.8378 | 22.7489 | 22.3683 | 21.6863 | 22.6883 | 21.7453 | 22.3399 | 22.3443 | 22.3127 | 21.9644 | 21.1824 | 22.1463 | 21.598 | 21.7681 | 21.9126 | 21.073 | 21.2182 | 21.8523 | 20.4842 | 21.4439 | 26.6018 | 21.9331 | 22.4255 | 30.9645 | 199.8445 | 177.1243 | 216.5898 | 22.1221 | 22.2461 | 28.4099 | 22.0411 | 22.4369 | 30.9392 | 95.6778 | 236.1342 |  | 138.7332 | 176.1665 | 174.4003 | 173.8481 |  | 17.9803 | 19.4439 | 18.1119 | 19.5136 | 21.3375 | 39.9871 | 152.1588 | 15.6912 | 17.4542 | 16.0666 | 19.4727 | 18.993 | 45.8794 | 49.1046 | 44.9766 | 21.6516 |  |  | 0.93728 | -0.12623 | -31.8532 | 0.16226 | 0.40426 | -155.4325 | 14.857 | 0.65544 | 0.15811 | 0.47069 | 0.58359 | 0.0003072 | 8.8812 | 0.20843 | 21.9752 | 21.9605 | 22.1522 | 22.2049 | 22.0145 | 21.3041 | 20.1278 | 22.1767 | 22.358 | 22.3925 | 22.3462 | 21.9557 | 21.1781 | 22.2762 | 98.8847 | 64.5562 | 63.3619 | 41.8585 | 37.7823 | 67.9296 | 43.7125 | 22.3224 | 22.0783 | 21.6579 | 22.0502 | 21.7861 | 21.7136 | 21.9445 | 21.8893 | 26.7934 | 81.3491 | 185.607 | 157.3978 | 118.9091 | 1.8219 | 1.2905 | 87.8469 | 21.8917 | 22.2201 | 21.1103 | 21.5623 | 22.031 | 22.0481 | 23.0424 | 36.812 | 21.8384 | 22.0509 | 28.1525 | 198.9607 | 254.3711 | 156.4647 | 158.1029 | 111.4525 |  | 82.6131 | 162.5408 | 88.3054 | 142.7253 | 124.0754 | 91.8515 |  | 106.9981 |  |  | 27.0281 | 33.7043 | 81.9101 | [5 empty] | 21.9 | 110.9512 | 21.711 | 22.1032 | 40.2576 | 21.2994 | 21.9223 | 40.1819 | 141.2447 | 285.8944 |  | 118.8926 | 187.0178 | 27.4857 | 110.5953 | 211.9877 | 76.4431 | 165.1186 | 32.2007 | 155.4771 | 32.5678 | 154.0557 | 19.751 | 119.9279 | 182.6305 | 42.4887 | 112.9107 | 213.5278 | 26.7652 | 114.3564 | 207.9865 | 27.5992 | 139.6346 | 45.4686 | 151.4005 | 33.8666 | 165.9727 | 2.3578 | 18.4952 | 2.2034 | 0.070221 | -27.2135 | 3.0949 | 325.25 | 52.27 | 1.4931 | -0.42353 | -6.7278 | 0.48018 | 0.78408 | -15.3746 | 4.7533 | 0.1072 | -1.0943 | 0.89361 | -2.6721 | -1.6117 | -1.1222 | -0.14788
42838.4267 | 552 | 22.8933 | 22.8605 | 22.8533 | 22.7639 | 22.3662 | 21.6923 | 22.6931 | 21.7464 | 22.3466 | 22.3534 | 22.3158 | 21.9713 | 21.1824 | 22.1648 | 21.6068 | 21.7739 | 21.913 | 21.0831 | 21.2225 | 21.862 | 20.4901 | 21.4548 | 26.6351 | 21.9419 | 22.4367 | 31.0108 | 200.9232 | 177.8827 | 218.2394 | 22.1266 | 22.2657 | 28.4512 | 22.0507 | 22.4456 | 30.9967 | 96.0799 | 237.2411 |  | 139.3644 | 176.6352 | 174.9861 | 174.3031 |  | 18.0018 | 19.4783 | 18.1169 | 19.5368 | 21.3965 | 40.5194 | 152.5859 | 15.7405 | 17.4769 | 16.0609 | 19.4895 | 18.9964 | 45.8645 | 49.0984 | 44.9796 | 21.6553 |  |  | 0.85777 | -0.2156 | -31.7776 | 0.18921 | 0.68353 | -152.8953 | 14.5692 | 0.83418 | 0.23381 | 0.23698 | 0.79746 | 0.00028092 | 8.8811 | 0.23325 | 21.9699 | 21.9557 | 22.146 | 22.2071 | 22.0092 | 21.2941 | 20.1183 | 22.1774 | 22.3601 | 22.3937 | 22.3409 | 21.9537 | 21.1773 | 22.2678 | 98.0091 | 62.8718 | 67.0791 | 41.9381 | 37.4708 | 68.0172 | 43.8483 | 22.3185 | 22.0785 | 21.6565 | 22.0452 | 21.7904 | 21.7137 | 21.945 | 21.8891 | 26.8196 | 81.622 | 185.8433 | 157.9678 | 119.5636 | 1.6684 | 0.84376 | 88.3889 | 21.8937 | 22.2178 | 21.122 | 21.5601 | 22.0234 | 22.0387 | 23.0535 | 36.879 | 21.8425 | 22.0477 | 28.1768 | 199.6408 | 255.1543 | 156.8913 | 158.6609 | 113.549 |  | 82.972 | 163.4347 | 88.5425 | 143.9579 | 124.7338 | 91.7663 |  | 107.2987 |  |  | 27.0885 | 33.9607 | 82.6201 | [5 empty] | 21.9011 | 111.3045 | 21.706 | 22.0978 | 40.3705 | 21.2906 | 21.9235 | 40.3614 | 141.8869 | 287.3761 |  | 119.2063 | 187.5353 | 27.5588 | 111.0548 | 213.0559 | 76.8966 | 165.6776 | 32.2901 | 156.09 | 32.652 | 154.6967 | 19.7549 | 120.4805 | 183.1868 | 42.7117 | 113.3533 | 214.2225 | 26.8157 | 115.1955 | 208.7901 | 27.6739 | 140.2106 | 45.7288 | 152.0409 | 33.9597 | 166.5002 | 1.7771 | 18.4895 | 2.2098 | 0.069989 | -27.2852 | 3.0949 | 317.66 | 51.84 | 1.4308 | -0.55354 | -6.7203 | 0.51855 | 1.0204 | -15.2616 | 4.7111 | 0.062603 | -1.11 | 0.88704 | -2.5643 | -2.0087 | -1.119 | -0.15572
42838.4267 | 553 | 22.8864 | 22.8514 | 22.8384 | 22.7567 | 22.3694 | 21.6953 | 22.6872 | 21.7503 | 22.3392 | 22.3424 | 22.3275 | 21.9625 | 21.1766 | 22.1538 | 21.5915 | 21.7664 | 21.9066 | 21.0683 | 21.2095 | 21.8507 | 20.4826 | 21.4496 | 26.6444 | 21.9344 | 22.4382 | 31.0422 | 201.6247 | 178.528 | 217.8549 | 22.1227 | 22.2531 | 28.467 | 22.0448 | 22.4363 | 31.031 | 96.4562 | 237.6684 |  | 139.9692 | 177.2341 | 175.4481 | 174.8625 |  | 18.015 | 19.5023 | 18.136 | 19.5595 | 21.4592 | 40.9745 | 153.0096 | 15.7951 | 17.4821 | 16.0346 | 19.4985 | 18.9973 | 45.8692 | 49.1069 | 44.9876 | 21.6532 |  |  | 0.75591 | -0.14463 | -32.2093 | 0.52631 | 0.96938 | -154.8049 | 14.1368 | 1.0596 | 0.12289 | 0.21495 | 0.49835 | 0.00029077 | 8.8811 | 0.27136 | 21.9836 | 21.9531 | 22.1433 | 22.2048 | 22.0111 | 21.2918 | 20.1118 | 22.1704 | 22.3568 | 22.3893 | 22.3437 | 21.9497 | 21.1782 | 22.2644 | 97.3006 | 62.9775 | 64.2018 | 42.2571 | 37.7615 | 68.1293 | 43.9212 | 22.3106 | 22.0689 | 21.6551 | 22.0409 | 21.7843 | 21.7078 | 21.9317 | 21.8882 | 26.8432 | 81.8904 | 186.319 | 158.553 | 120.05 | 1.873 | 0.46012 | 88.1655 | 21.8869 | 22.2034 | 21.1128 | 21.5553 | 22.0177 | 22.0373 | 23.0472 | 36.9254 | 21.8305 | 22.0454 | 28.193 | 200.5531 | 256.3759 | 157.447 | 159.2352 | 113.8819 |  | 83.3254 | 165.0337 | 88.8455 | 150.0463 | 125.5352 | 92.1439 |  | 107.6783 |  |  | 27.1593 | 34.235 | 82.3974 | [5 empty] | 21.8934 | 112.1037 | 21.6994 | 22.0974 | 40.5687 | 21.2922 | 21.9175 | 40.5765 | 142.5997 | 288.4572 |  | 119.7068 | 188.17 | 27.6286 | 111.5349 | 214.062 | 77.4967 | 166.3461 | 32.3828 | 156.7048 | 32.717 | 155.2988 | 19.7606 | 120.6626 | 183.8951 | 42.9383 | 113.8093 | 215.495 | 26.8782 | 115.7941 | 209.9366 | 27.7539 | 140.7915 | 45.9546 | 152.5871 | 34.0428 | 167.2903 | 2.3016 | 18.4826 | 2.2171 | 0.070207 | -27.229 | 3.0949 | 335.42 | 51.58 | 1.3426 | -0.45339 | -6.766 | 0.86489 | 1.2161 | -15.3677 | 4.644 | 0.066798 | -1.1427 | 0.75167 | -2.4721 | -1.6803 | -1.1198 | -0.15905
42838.4267 | 554 | 22.8987 | 22.867 | 22.8458 | 22.7646 | 22.3741 | 21.6989 | 22.6992 | 21.7506 | 22.3538 | 22.3537 | 22.3297 | 21.9779 | 21.1859 | 22.16 | 21.593 | 21.7672 | 21.9089 | 21.0638 | 21.2083 | 21.8549 | 20.479 | 21.4549 | 26.6727 | 21.9366 | 22.4452 | 31.0875 | 202.4621 | 179.32 | 221.0131 | 22.1195 | 22.2604 | 28.4999 | 22.052 | 22.4432 | 31.0704 | 96.8624 | 239.183 |  | 140.5358 | 177.9175 | 175.9439 | 175.8385 |  | 18.0205 | 19.5195 | 18.1617 | 19.577 | 21.6533 | 41.8589 | 153.7437 | 15.8247 | 17.4792 | 16.0252 | 19.5164 | 18.9851 | 45.8722 | 49.0897 | 44.9925 | 21.6487 |  |  | 1.4702 | -0.22414 | -32.5366 | 0.17212 | 0.7407 | -155.5442 | 14.3497 | 0.3282 | 0.16395 | 0.12515 | 0.66188 | 0.00025299 | 8.881 | 0.27027 | 21.9836 | 21.9617 | 22.1518 | 22.2096 | 22.0167 | 21.3034 | 20.1169 | 22.167 | 22.3539 | 22.3939 | 22.347 | 21.9475 | 21.1808 | 22.2692 | 96.5067 | 63.2067 | 60.5256 | 41.0906 | 38.0198 | 68.23 | 43.9461 | 22.3153 | 22.0868 | 21.6577 | 22.0469 | 21.7936 | 21.7258 | 21.9463 | 21.9022 | 26.877 | 82.1934 | 187.1705 | 159.1829 | 120.5661 | 2.026 | 0.91394 | 88.5685 | 21.8916 | 22.2117 | 21.1292 | 21.5622 | 22.015 | 22.0435 | 23.0704 | 36.9966 | 21.8341 | 22.0622 | 28.2387 | 201.1126 | 257.7189 | 157.9195 | 159.7335 | 113.6314 |  | 83.61 | 165.6994 | 89.0914 | 149.7147 | 126.1696 | 93.2621 |  | 107.9723 |  |  | 27.2442 | 34.58 | 82.382 | [5 empty] | 21.897 | 112.7029 | 21.7051 | 22.1026 | 40.8465 | 21.2947 | 21.9198 | 40.7901 | 143.3668 | 290.714 |  | 120.2234 | 188.6802 | 27.7044 | 111.8334 | 215.1446 | 78.0735 | 167.2626 | 32.4562 | 157.1981 | 32.7822 | 155.8299 | 19.7824 | 120.8467 | 184.7035 | 43.1973 | 114.2379 | 216.5173 | 26.9684 | 116.2585 | 210.9635 | 27.8318 | 141.3326 | 46.1976 | 153.2175 | 34.1392 | 167.85 | 2.5891 | 18.476 | 2.2245 | 0.06922 | -27.2297 | 3.0949 | 317.42 | 52.76 | 1.8784 | -0.56444 | -6.8005 | 0.49462 | 1.0645 | -15.4261 | 4.6854 | 0.084589 | -1.1517 | 0.78764 | -2.3718 | -1.2689 | -1.131 | -0.16189
42838.4267 | 555 | 22.8905 | 22.853 | 22.843 | 22.761 | 22.3691 | 21.6974 | 22.7006 | 21.7464 | 22.3441 | 22.3489 | 22.3214 | 21.9736 | 21.1837 | 22.1618 | 21.594 | 21.7703 | 21.9033 | 21.0758 | 21.2179 | 21.8655 | 20.4779 | 21.4616 | 26.7084 | 21.938 | 22.4476 | 31.1307 | 204.1049 | 180.8734 | 224.6167 | 22.1169 | 22.2667 | 28.528 | 22.0512 | 22.4437 | 31.1099 | 97.2652 | 244.1416 |  | 141.1833 | 178.4491 | 176.6616 | 176.3612 |  | 18.0227 | 19.5547 | 18.1871 | 19.6161 | 21.7643 | 43.1242 | 154.5049 | 15.8745 | 17.4921 | 16.0282 | 19.5343 | 18.9982 | 45.8967 | 49.0868 | 45.0072 | 21.6592 |  |  | 0.62515 | -0.095349 | -32.716 | 0.11627 | 0.47523 | -157.8559 | 14.6362 | 0.92946 | 0.10693 | 0.34901 | 0.91239 | 0.0003072 | 8.8811 | 0.25084 | 21.9821 | 21.9619 | 22.1518 | 22.2076 | 22.0169 | 21.3063 | 20.1152 | 22.1795 | 22.3607 | 22.3999 | 22.3411 | 21.9539 | 21.1799 | 22.2748 | 97.309 | 65.7477 | 60.4117 | 41.024 | 37.5392 | 68.379 | 43.9943 | 22.3114 | 22.0866 | 21.6593 | 22.0451 | 21.7851 | 21.7176 | 21.9393 | 21.9018 | 26.9058 | 82.5163 | 187.7555 | 159.9373 | 120.6246 | 2.048 | 1.2523 | 88.839 | 21.8919 | 22.1971 | 21.1154 | 21.5475 | 22.0046 | 22.0284 | 23.0652 | 37.0485 | 21.8284 | 22.0456 | 28.2481 | 201.9222 | 260.643 | 158.2665 | 160.2209 | 113.3075 |  | 83.9003 | 165.6158 | 89.3471 | 145.0106 | 126.5987 | 94.1105 |  | 108.2556 |  |  | 27.3432 | 34.8348 | 82.9093 | [5 empty] | 21.9003 | 111.7996 | 21.7072 | 22.1053 | 41.1339 | 21.298 | 21.9202 | 41.0132 | 144.1328 | 294.5656 |  | 120.6573 | 189.0427 | 27.7836 | 112.5294 | 217.3494 | 78.6843 | 168.8519 | 32.52 | 157.7758 | 32.8417 | 156.145 | 19.8046 | 121.1849 | 185.4902 | 43.4607 | 114.7486 | 217.9505 | 27.0645 | 116.6338 | 211.8489 | 27.8945 | 141.717 | 46.479 | 153.936 | 34.2254 | 168.5648 | 2.2348 | 18.4677 | 2.2311 | 0.069256 | -27.2874 | 3.0948 | 309.78 | 51.68 | 1.2293 | -0.36816 | -6.8196 | 0.40654 | 0.85438 | -15.5715 | 4.7415 | 0.10464 | -1.1395 | 0.93643 | -2.443 | -1.2506 | -1.1297 | -0.15125
42838.4267 | 556 | 22.8859 | 22.8523 | 22.839 | 22.7633 | 22.3684 | 21.699 | 22.6978 | 21.7463 | 22.3407 | 22.3398 | 22.3128 | 21.9648 | 21.178 | 22.1555 | 21.5952 | 21.7722 | 21.904 | 21.0775 | 21.2179 | 21.8674 | 20.4767 | 21.4666 | 26.738 | 21.934 | 22.453 | 31.1654 | 205.5188 | 182.4487 | 225.9527 | 22.1138 | 22.2673 | 28.562 | 22.0397 | 22.4483 | 31.1484 | 97.6662 | 248.3318 |  | 141.8984 | 179.0717 | 177.3606 | 176.3146 |  | 18.0301 | 19.5864 | 18.1968 | 19.6417 | 21.7774 | 43.5314 | 155.347 | 15.8968 | 17.4959 | 15.9663 | 19.5462 | 19.0062 | 45.9087 | 49.0788 | 45.0089 | 21.6528 |  |  | 0.87157 | -0.18668 | -32.7639 | 0.42248 | 0.58299 | -160.0579 | 14.562 | 0.17115 | 0.25502 | 0.25565 | 1.0799 | 0.00031049 | 8.8813 | 0.21739 | 21.9859 | 21.966 | 22.1575 | 22.2121 | 22.016 | 21.3017 | 20.1249 | 22.186 | 22.3597 | 22.3915 | 22.3462 | 21.9662 | 21.1835 | 22.2732 | 98.4493 | 66.6964 | 60.5512 | 41.0047 | 37.0237 | 68.5249 | 44.0528 | 22.319 | 22.0839 | 21.6613 | 22.0453 | 21.7922 | 21.7309 | 21.941 | 21.9043 | 26.9422 | 82.8103 | 188.2213 | 160.6044 | 121.1292 | 1.5642 | 1.2692 | 89.7906 | 21.8921 | 22.2028 | 21.1335 | 21.5504 | 22.0126 | 22.0364 | 23.0842 | 37.1136 | 21.8322 | 22.0607 | 28.2922 | 202.9578 | 263.5545 | 158.5901 | 160.6578 | 112.7548 |  | 84.2027 | 166.3055 | 89.6516 | 145.1725 | 127.0937 | 94.2329 |  | 108.5624 |  |  | 27.4091 | 35.0043 | 82.692 | [5 empty] | 21.8961 | 111.2343 | 21.7029 | 22.0966 | 41.4617 | 21.2903 | 21.9194 | 41.2222 | 144.846 | 298.3463 |  | 121.1988 | 189.737 | 27.8561 | 113.2168 | 220.0893 | 79.3137 | 170.2125 | 32.6088 | 158.5367 | 32.9099 | 156.4984 | 19.8391 | 121.6125 | 186.244 | 43.7111 | 115.4252 | 219.8418 | 27.1289 | 117.0824 | 213.4566 | 27.9596 | 142.1381 | 46.7741 | 154.6671 | 34.3331 | 169.7138 | 2.2196 | 18.463 | 2.2379 | 0.07123 | -27.2575 | 3.0949 | 318.96 | 52.24 | 1.4535 | -0.51518 | -6.825 | 0.77501 | 0.94691 | -15.6898 | 4.7325 | 0.13152 | -1.1469 | 0.95287 | -2.5522 | -1.2591 | -1.1126 | -0.1541
42838.4267 | 557 | 22.8966 | 22.8588 | 22.8403 | 22.7589 | 22.377 | 21.6966 | 22.6946 | 21.7521 | 22.3487 | 22.3492 | 22.3188 | 21.9708 | 21.186 | 22.1616 | 21.6002 | 21.7738 | 21.9041 | 21.07 | 21.2217 | 21.8704 | 20.4822 | 21.4733 | 26.776 | 21.9407 | 22.4562 | 31.2104 | 206.4739 | 183.6261 | 227.0143 | 22.1229 | 22.2798 | 28.6025 | 22.0525 | 22.4626 | 31.1978 | 98.1386 | 254.566 |  | 142.7072 | 180.0234 | 178.0755 | 176.5954 |  | 18.0432 | 19.6181 | 18.218 | 19.6817 | 21.8162 | 43.6478 | 155.9399 | 15.8838 | 17.5067 | 15.9073 | 19.573 | 19.0103 | 45.9237 | 49.0815 | 45.0234 | 21.6597 |  |  | 1.0036 | -0.3963 | -33.1089 | 0.32654 | 0.60271 | -153.4223 | 14.2761 | 0.938 | 0.081242 | 0.25712 | 0.70476 | 0.0002842 | 8.8809 | 0.21766 | 21.9875 | 21.9585 | 22.1548 | 22.201 | 22.0165 | 21.305 | 20.1194 | 22.1753 | 22.3521 | 22.3928 | 22.3385 | 21.9581 | 21.1799 | 22.2684 | 98.0727 | 67.07 | 61.6184 | 41.9184 | 36.1077 | 68.6721 | 44.1239 | 22.3167 | 22.0794 | 21.6594 | 22.0446 | 21.7867 | 21.7373 | 21.9439 | 21.906 | 26.9634 | 83.1101 | 188.551 | 161.1999 | 121.7874 | 1.9456 | 0.88941 | 89.8131 | 21.8946 | 22.2162 | 21.151 | 21.556 | 22.0272 | 22.0427 | 23.0824 | 37.17 | 21.8443 | 22.0599 | 28.3296 | 203.7813 | 265.4074 | 158.8371 | 161.1269 | 112.7664 |  | 84.4931 | 166.7744 | 89.939 | 146.8945 | 127.5535 | 94.2611 |  | 108.85 |  |  | 27.4653 | 35.1994 | 82.4524 | [5 empty] | 21.8907 | 110.3282 | 21.6993 | 22.0912 | 41.8376 | 21.2938 | 21.92 | 41.4438 | 145.6375 | 302.5196 |  | 121.9254 | 190.8788 | 27.9305 | 113.5136 | 223.5034 | 79.9766 | 170.8589 | 32.6849 | 159.1327 | 33.0198 | 156.9135 | 19.8636 | 122.3045 | 186.9182 | 43.9686 | 115.9855 | 221.4991 | 27.1963 | 117.5131 | 215.2551 | 28.0269 | 142.7339 | 47.0551 | 155.2014 | 34.4576 | 170.655 | 2.6514 | 18.4553 | 2.2451 | 0.070998 | -27.2203 | 3.0949 | 316.3 | 51.85 | 1.5614 | -0.75066 | -6.8612 | 0.68139 | 0.96297 | -15.3639 | 4.6867 | 0.14228 | -1.1489 | 0.92451 | -2.4927 | -1.3693 | -1.1018 | -0.16099
42838.4267 | 558 | 22.8881 | 22.8575 | 22.8385 | 22.7568 | 22.3687 | 21.6905 | 22.6914 | 21.748 | 22.3419 | 22.3444 | 22.3144 | 21.9624 | 21.1822 | 22.1544 | 21.5891 | 21.7686 | 21.9037 | 21.0726 | 21.2172 | 21.8732 | 20.4759 | 21.4716 | 26.8015 | 21.9357 | 22.4592 | 31.253 | 207.2384 | 184.8434 | 226.9427 | 22.125 | 22.2859 | 28.6305 | 22.0512 | 22.4641 | 31.2404 | 98.5955 | 259.335 |  | 143.4717 | 181.0125 | 178.8417 | 178.4482 |  | 18.0456 | 19.6509 | 18.2357 | 19.7158 | 21.9301 | 45.6864 | 156.259 | 15.8407 | 17.5089 | 15.8723 | 19.5911 | 19.0198 | 45.9399 | 49.0782 | 45.0286 | 21.6567 |  |  | 0.76709 | -0.27803 | -33.2298 | 0.14387 | 0.92535 | -157.3854 | 13.8628 | 0.95048 | 0.25872 | 0.23635 | 0.81847 | 0.00029077 | 8.8811 | 0.20374 | 21.9886 | 21.9642 | 22.1471 | 22.2089 | 22.0135 | 21.3088 | 20.12 | 22.1799 | 22.358 | 22.3934 | 22.3468 | 21.9576 | 21.1801 | 22.2673 | 99.963 | 68.7849 | 62.3247 | 41.7576 | 35.9801 | 68.8297 | 44.1771 | 22.316 | 22.08 | 21.6589 | 22.0503 | 21.7901 | 21.7362 | 21.9429 | 21.9113 | 26.9888 | 83.4115 | 188.7618 | 161.7486 | 122.4109 | 1.8589 | 0.99478 | 89.4854 | 21.9029 | 22.2197 | 21.149 | 21.5565 | 22.0128 | 22.0418 | 23.1037 | 37.2329 | 21.84 | 22.0652 | 28.3547 | 205.0246 | 267.1832 | 158.9888 | 161.5312 | 112.9302 |  | 84.7894 | 165.8329 | 90.2406 | 149.1193 | 127.9951 | 94.8209 |  | 109.182 |  |  | 27.5118 | 35.3482 | 82.0449 | [5 empty] | 21.8953 | 109.3719 | 21.7041 | 22.0939 | 42.2669 | 21.2943 | 21.917 | 41.727 | 146.5397 | 306.0989 |  | 122.6615 | 192.5186 | 28.0205 | 113.9295 | 227.5288 | 80.754 | 171.5075 | 32.7905 | 159.4619 | 33.1363 | 157.5656 | 19.8989 | 123.0885 | 187.8505 | 44.2668 | 116.4722 | 222.5549 | 27.2961 | 117.7908 | 217.0476 | 28.1139 | 143.4718 | 47.3315 | 155.5814 | 34.5902 | 171.4353 | 2.6685 | 18.4468 | 2.2521 | 0.071034 | -27.2383 | 3.0948 | 331.08 | 51.54 | 1.3649 | -0.62877 | -6.8741 | 0.45231 | 1.197 | -15.6111 | 4.6331 | 0.14904 | -1.1111 | 0.88143 | -2.6837 | -1.4415 | -1.1353 | -0.16684
42838.4267 | 559 | 22.88 | 22.8598 | 22.838 | 22.7574 | 22.379 | 21.6955 | 22.7001 | 21.7483 | 22.3488 | 22.353 | 22.3223 | 21.9707 | 21.187 | 22.1581 | 21.5833 | 21.7621 | 21.8992 | 21.0692 | 21.2085 | 21.8715 | 20.4691 | 21.4753 | 26.8179 | 21.9278 | 22.46 | 31.2805 | 207.9698 | 185.5277 | 227.3191 | 22.1218 | 22.2841 | 28.658 | 22.0545 | 22.4746 | 31.2804 | 99.0768 | 261.0258 |  | 144.243 | 182.1411 | 179.9025 | 180.0056 |  | 18.0635 | 19.71 | 18.2721 | 19.7754 | 22.0436 | 48.7001 | 156.9052 | 15.8519 | 17.5322 | 15.9123 | 19.6265 | 19.0217 | 45.9414 | 49.0737 | 45.0482 | 21.6625 |  |  | 0.59821 | -0.13214 | -32.9716 | 0.41131 | 0.94375 | -157.4169 | 13.5894 | 0.92683 | 0.14468 | 0.16585 | 1.0376 | 0.0002957 | 8.8811 | 0.17257 | 21.9837 | 21.9625 | 22.1477 | 22.2079 | 22.0133 | 21.3033 | 20.1205 | 22.175 | 22.3561 | 22.3913 | 22.3376 | 21.9538 | 21.1778 | 22.2667 | 98.5524 | 66.5276 | 62.7697 | 41.9663 | 36.5859 | 68.9228 | 44.2399 | 22.307 | 22.0836 | 21.6591 | 22.0435 | 21.7904 | 21.7387 | 21.936 | 21.9065 | 27.0146 | 83.7412 | 189.6511 | 162.3896 | 122.8567 | 2.0842 | 0.77548 | 89.3929 | 21.8942 | 22.2101 | 21.1786 | 21.5669 | 22.022 | 22.0401 | 23.1132 | 37.2873 | 21.835 | 22.083 | 28.3954 | 206.6982 | 270.6749 | 159.3014 | 162.0837 | 112.7616 |  | 85.1053 | 166.5233 | 90.5605 | 150.2387 | 128.4715 | 94.9704 |  | 109.617 |  |  | 27.608 | 35.461 | 82.1418 | [5 empty] | 21.8884 | 108.4389 | 21.7006 | 22.0947 | 42.7019 | 21.2838 | 21.9188 | 42.0085 | 147.3824 | 311.2724 |  | 123.0837 | 194.5143 | 28.1132 | 114.7396 | 229.5775 | 81.4339 | 172.1882 | 32.9396 | 159.6581 | 33.2636 | 158.1471 | 19.93 | 123.7983 | 189.5068 | 44.5317 | 117.1321 | 224.1096 | 27.4036 | 118.1586 | 218.8013 | 28.2432 | 144.2184 | 47.6175 | 156.6071 | 34.7246 | 172.0218 | 3.2741 | 18.4408 | 2.2588 | 0.071078 | -27.1929 | 3.0949 | 351.8 | 52.72 | 1.2058 | -0.43353 | -6.8481 | 0.76486 | 1.2146 | -15.6863 | 4.6089 | 0.16578 | -1.1179 | 0.87056 | -2.5158 | -1.4835 | -1.1596 | -0.16667
42838.4268 | 560 | 22.8879 | 22.8565 | 22.8415 | 22.764 | 22.3688 | 21.6966 | 22.6989 | 21.747 | 22.353 | 22.352 | 22.3135 | 21.9733 | 21.1869 | 22.1592 | 21.5891 | 21.7727 | 21.9065 | 21.0656 | 21.2103 | 21.8739 | 20.4823 | 21.4837 | 26.8567 | 21.9345 | 22.476 | 31.3426 | 208.7116 | 186.1214 | 227.4887 | 22.1219 | 22.286 | 28.6884 | 22.0473 | 22.4679 | 31.3152 | 99.5688 | 265.3562 |  | 145.0949 | 183.3961 | 180.9145 | 181.1066 |  | 18.0675 | 19.7462 | 18.2907 | 19.814 | 22.0655 | 49.592 | 157.4339 | 15.8781 | 17.5326 | 15.9638 | 19.6363 | 19.017 | 45.9402 | 49.0647 | 45.0541 | 21.6607 |  |  | 1.2409 | -0.064461 | -32.7436 | 0.41065 | 0.67696 | -157.0306 | 14.0895 | 1.4657 | 0.42296 | 0.42852 | 0.88721 | 0.00025463 | 8.881 | 0.17054 | 21.9888 | 21.9596 | 22.1526 | 22.2029 | 22.0136 | 21.2979 | 20.1175 | 22.1748 | 22.3524 | 22.3902 | 22.3308 | 21.9541 | 21.17 | 22.2651 | 96.0538 | 64.362 | 62.0461 | 41.6064 | 36.9302 | 69.0077 | 44.2968 | 22.3198 | 22.0785 | 21.6605 | 22.041 | 21.7912 | 21.7431 | 21.9421 | 21.9132 | 27.0524 | 84.1088 | 190.5134 | 163.1356 | 123.743 | 2.4082 | 1.2886 | 90.9903 | 21.8922 | 22.2077 | 21.1749 | 21.5572 | 22.0161 | 22.0378 | 23.1094 | 37.3517 | 21.8376 | 22.0759 | 28.4201 | 208.5816 | 273.6286 | 159.8344 | 162.9115 | 115.367 |  | 85.4393 | 165.9821 | 90.9148 | 150.5037 | 128.9729 | 95.5195 |  | 110.185 |  |  | 27.7136 | 36.0546 | 83.1436 | [5 empty] | 21.891 | 107.9046 | 21.7057 | 22.0983 | 43.021 | 21.2907 | 21.9206 | 42.303 | 148.2237 | 314.0337 |  | 123.4693 | 196.7478 | 28.1874 | 115.7116 | 231.4067 | 82.1028 | 172.8422 | 33.084 | 159.9728 | 33.3944 | 158.5697 | 19.9368 | 124.3737 | 191.4219 | 44.8118 | 117.9098 | 226.0161 | 27.5306 | 118.695 | 220.348 | 28.3343 | 145.0015 | 47.8979 | 157.4026 | 34.8356 | 172.6465 | 3.0582 | 18.4302 | 2.2649 | 0.072617 | -27.1899 | 3.0949 | 341.35 | 51.62 | 1.737 | -0.30281 | -6.8248 | 0.7643 | 1.0301 | -15.6887 | 4.6994 | 0.10618 | -1.0891 | 0.8845 | -2.228 | -1.3964 | -1.1707 | -0.17728
42838.4268 | 561 | 22.8836 | 22.8519 | 22.844 | 22.7645 | 22.3632 | 21.695 | 22.6882 | 21.7409 | 22.3468 | 22.3428 | 22.3129 | 21.9687 | 21.1799 | 22.1556 | 21.5866 | 21.7692 | 21.9067 | 21.0681 | 21.2079 | 21.8733 | 20.4822 | 21.4921 | 26.8766 | 21.9405 | 22.4706 | 31.3803 | 209.843 | 186.9966 | 229.176 | 22.1189 | 22.2885 | 28.7214 | 22.0499 | 22.4751 | 31.365 | 100.091 | 267.2109 |  | 145.86 | 184.7885 | 182.0951 | 183.7312 |  | 18.091 | 19.7991 | 18.3196 | 19.8642 | 22.0673 | 49.0822 | 157.6044 | 15.9334 | 17.5385 | 15.9813 | 19.6612 | 19.0214 | 45.9463 | 49.0592 | 45.0686 | 21.6666 |  |  | 0.83871 | -0.036205 | -33.1286 | 0.38963 | 0.5094 | -157.0614 | 13.4488 | 0.6101 | 0.30503 | 0.23152 | 0.5973 | 0.00028256 | 8.8809 | 0.18289 | 21.9879 | 21.9534 | 22.1471 | 22.2019 | 22.0042 | 21.2951 | 20.1081 | 22.1757 | 22.3492 | 22.3861 | 22.3282 | 21.9574 | 21.1753 | 22.2641 | 98.6067 | 64.739 | 62.2614 | 41.4714 | 36.6507 | 69.163 | 44.3797 | 22.3169 | 22.0772 | 21.6596 | 22.0449 | 21.7882 | 21.7451 | 21.9404 | 21.9189 | 27.0827 | 84.4263 | 191.8578 | 163.8255 | 124.485 | 1.976 | 1.3231 | 92.1258 | 21.8901 | 22.2002 | 21.1842 | 21.5552 | 22.0139 | 22.0332 | 23.1222 | 37.4072 | 21.8257 | 22.0743 | 28.4421 | 210.7149 | 278.2558 | 160.5467 | 163.7748 | 118.4099 |  | 85.7803 | 166.2714 | 91.1985 | 150.6363 | 129.4282 | 96.1707 |  | 110.7352 |  |  | 27.7954 | 36.5812 | 83.8211 | [5 empty] | 21.8929 | 107.6075 | 21.71 | 22.0952 | 43.4411 | 21.2883 | 21.915 | 42.5771 | 149.053 | 316.3245 |  | 123.9739 | 199.0478 | 28.2826 | 116.333 | 232.5581 | 82.8854 | 174.0351 | 33.1914 | 160.57 | 33.5183 | 159.09 | 19.942 | 124.9613 | 192.9233 | 45.052 | 118.4609 | 228.1525 | 27.6684 | 119.585 | 221.4428 | 28.4055 | 145.696 | 48.1773 | 158.2445 | 34.9938 | 173.372 | 3.0491 | 18.4209 | 2.2715 | 0.07367 | -27.1539 | 3.0949 | 368.81 | 52.47 | 1.4304 | -0.22696 | -6.8654 | 0.74454 | 0.89285 | -15.6778 | 4.5877 | 0.034696 | -1.0862 | 0.90019 | -2.493 | -1.4105 | -1.223 | -0.18579
42838.4268 | 562 | 22.8814 | 22.8395 | 22.8358 | 22.748 | 22.3625 | 21.6889 | 22.686 | 21.7482 | 22.3395 | 22.341 | 22.3151 | 21.9646 | 21.1796 | 22.154 | 21.605 | 21.7712 | 21.9086 | 21.076 | 21.224 | 21.8895 | 20.4904 | 21.5091 | 26.9204 | 21.9428 | 22.4828 | 31.4316 | 211.2259 | 187.8074 | 232.4782 | 22.1186 | 22.2906 | 28.7593 | 22.0513 | 22.4885 | 31.4048 | 100.6127 | 267.7733 |  | 146.6529 | 186.2863 | 183.3581 | 185.2236 |  | 18.1109 | 19.8534 | 18.3376 | 19.9112 | 22.0772 | 48.9543 | 158.1172 | 15.914 | 17.5505 | 15.9726 | 19.6828 | 19.0254 | 45.9404 | 49.0582 | 45.0793 | 21.672 |  |  | 0.82623 | -0.12623 | -33.3803 | 0.027554 | 0.55868 | -155.1814 | 13.3535 | 1.0359 | 0.22038 | 0.29656 | 0.81448 | 0.00029242 | 8.8811 | 0.19808 | 21.9896 | 21.9569 | 22.148 | 22.1963 | 22.0181 | 21.2966 | 20.115 | 22.1761 | 22.3514 | 22.3898 | 22.3284 | 21.9547 | 21.1812 | 22.2621 | 100.6821 | 65.6236 | 66.3988 | 41.6919 | 36.4744 | 69.3534 | 44.5264 | 22.3178 | 22.0774 | 21.6616 | 22.0481 | 21.7854 | 21.7526 | 21.9408 | 21.9228 | 27.1185 | 84.7663 | 193.1151 | 164.4805 | 125.1061 | 2.6368 | 2.1084 | 93.5116 | 21.8869 | 22.2027 | 21.2051 | 21.5498 | 22.0142 | 22.0375 | 23.1372 | 37.4597 | 21.8426 | 22.0855 | 28.4839 | 212.4958 | 282.625 | 161.0994 | 164.5165 | 121.8713 |  | 86.1268 | 167.6667 | 91.4825 | 151.443 | 129.886 | 96.3813 |  | 111.2324 |  |  | 27.9041 | 36.7352 | 84.5101 | [5 empty] | 21.8859 | 107.3972 | 21.7103 | 22.0885 | 43.8513 | 21.2866 | 21.9215 | 42.8412 | 149.9118 | 319.0294 |  | 124.8594 | 201.4476 | 28.373 | 117.1674 | 234.8245 | 83.6823 | 176.0534 | 33.2792 | 161.4927 | 33.7243 | 161.6773 | 19.9384 | 125.8579 | 194.4603 | 45.3191 | 118.9044 | 229.8537 | 27.8052 | 120.4324 | 222.3659 | 28.4773 | 146.4646 | 48.5378 | 159.0494 | 35.1465 | 174.012 | 3.2014 | 18.4182 | 2.2775 | 0.072631 | -27.2626 | 3.0949 | 399.88 | 51.69 | 1.4244 | -0.42383 | -6.8921 | 0.19801 | 0.93486 | -15.5806 | 4.5705 | -0.048192 | -1.1139 | 0.89729 | -2.7007 | -1.8528 | -1.2438 | -0.19006
42838.4268 | 563 | 22.8897 | 22.8547 | 22.8473 | 22.7533 | 22.3669 | 21.6885 | 22.6938 | 21.7508 | 22.3488 | 22.3477 | 22.3222 | 21.9694 | 21.1918 | 22.1645 | 21.5981 | 21.7746 | 21.9164 | 21.0807 | 21.2239 | 21.8943 | 20.4915 | 21.5117 | 26.9551 | 21.9473 | 22.4923 | 31.464 | 213.0825 | 188.5471 | 236.6477 | 22.122 | 22.2938 | 28.7938 | 22.0558 | 22.4864 | 31.4413 | 101.1679 | 275.8354 |  | 147.609 | 187.8507 | 184.4801 | 189.9898 |  | 18.1279 | 19.9024 | 18.3716 | 19.9608 | 22.1401 | 49.9277 | 159.142 | 15.9104 | 17.555 | 16.0106 | 19.7109 | 19.0255 | 45.9381 | 49.0497 | 45.0718 | 21.6603 |  |  | 0.90245 | -0.23794 | -32.8323 | 0.30486 | 0.62899 | -160.3983 | 13.7708 | 0.78555 | 0.22797 | 0.27369 | 0.66761 | 0.0002957 | 8.8811 | 0.18627 | 21.9966 | 21.9593 | 22.1548 | 22.198 | 22.0136 | 21.3011 | 20.1166 | 22.1728 | 22.3598 | 22.3861 | 22.3439 | 21.9567 | 21.181 | 22.2744 | 103.3032 | 68.0196 | 71.3326 | 43.1148 | 36.8211 | 69.5619 | 44.6914 | 22.313 | 22.0701 | 21.6547 | 22.0422 | 21.7811 | 21.7476 | 21.9308 | 21.9132 | 27.1345 | 85.11 | 193.6045 | 165.0552 | 126.3429 | 2.1302 | 1.4047 | 94.2795 | 21.885 | 22.2126 | 21.2146 | 21.561 | 22.0207 | 22.05 | 23.1499 | 37.5286 | 21.8528 | 22.0885 | 28.5237 | 213.7785 | 286.3654 | 161.8571 | 165.4226 | 126.1614 |  | 86.5593 | 168.5019 | 91.8398 | 151.0401 | 130.454 | 97.1774 |  | 111.7573 |  |  | 27.9987 | 36.8145 | 85.8107 | [5 empty] | 21.8914 | 107.4031 | 21.7025 | 22.0956 | 44.2982 | 21.2846 | 21.913 | 43.0969 | 151.1023 | 323.1065 |  | 125.9034 | 203.11 | 28.4677 | 118.0803 | 237.5871 | 84.4847 | 177.0225 | 33.4205 | 162.6622 | 33.9212 | 162.5732 | 19.9379 | 126.6729 | 195.8017 | 45.5713 | 119.4878 | 232.215 | 27.9544 | 121.1886 | 224.061 | 28.5406 | 147.7348 | 48.8687 | 160.3851 | 35.3192 | 174.8176 | 3.3103 | 18.4137 | 2.2827 | 0.072203 | -27.288 | 3.0949 | 409.91 | 51.59 | 1.4948 | -0.58193 | -6.8358 | 0.6587 | 0.99344 | -15.8643 | 4.6484 | -0.15079 | -1.1233 | 0.93271 | -2.9669 | -2.3815 | -1.3541 | -0.21129
42838.4268 | 564 | 22.8908 | 22.8505 | 22.8459 | 22.7597 | 22.3715 | 21.6943 | 22.692 | 21.7566 | 22.3434 | 22.3473 | 22.3257 | 21.9744 | 21.1894 | 22.1644 | 21.5992 | 21.7741 | 21.9086 | 21.0736 | 21.2102 | 21.8896 | 20.4818 | 21.5155 | 26.9774 | 21.9388 | 22.4973 | 31.5042 | 214.7144 | 189.8538 | 241.8802 | 22.1238 | 22.3029 | 28.8235 | 22.0514 | 22.4837 | 31.4852 | 101.7595 | 279.5488 |  | 148.5218 | 189.5293 | 185.5857 | 193.6226 |  | 18.141 | 19.9484 | 18.408 | 20.0021 | 22.2434 | 49.9525 | 160.9628 | 15.8785 | 17.5525 | 16.0192 | 19.7193 | 19.0257 | 45.9376 | 49.0514 | 45.0813 | 21.674 |  |  | 0.681 | -0.27868 | -33.08 | 0.28317 | 0.67696 | -155.7912 | 13.8877 | 1.2344 | 0.01391 | 0.26824 | 0.61102 | 4.369 | 8.9693 | 0.16566 | 21.9941 | 21.9544 | 22.1497 | 22.2135 | 22.0044 | 21.3062 | 20.1141 | 22.1777 | 22.3521 | 22.3909 | 22.3334 | 21.9492 | 21.1754 | 22.2714 | 108.1475 | 70.8533 | 72.0836 | 45.3287 | 38.4292 | 69.8653 | 44.8234 | 22.3113 | 22.0731 | 21.6525 | 22.0355 | 21.7914 | 21.7462 | 21.9381 | 21.9154 | 27.1706 | 85.5079 | 193.9868 | 165.8118 | 128.0961 | 2.8324 | 1.461 | 94.5616 | 21.8886 | 22.212 | 21.2335 | 21.5647 | 22.0135 | 22.0482 | 23.157 | 37.5816 | 21.845 | 22.0899 | 28.5537 | 216.0884 | 291.289 | 162.7207 | 166.5912 | 131.8874 |  | 86.9764 | 170.7181 | 92.1438 | 149.7053 | 130.9178 | 97.825 |  | 112.205 |  |  | 28.1146 | 36.8701 | 88.5005 | [5 empty] | 21.8787 | 107.71 | 21.6995 | 22.0888 | 44.7648 | 21.2806 | 21.9033 | 43.3802 | 152.0721 | 326.7587 |  | 126.968 | 205.1778 | 28.5793 | 118.4641 | 240.5334 | 85.188 | 178.5808 | 33.583 | 163.2307 | 34.0852 | 163.4122 | 19.9239 | 127.4666 | 197.1418 | 45.8702 | 120.1577 | 235.2858 | 28.0729 | 121.7182 | 225.6106 | 28.5973 | 148.9996 | 49.1829 | 161.5241 | 35.5137 | 175.9427 | 3.5795 | 18.4064 | 2.2876 | 0.0707 | -27.2434 | 3.0949 | 434.49 | 52.37 | 1.3051 | -0.62984 | -6.8621 | 0.63489 | 1.0307 | -15.6354 | 4.6682 | -0.29385 | -1.173 | 0.98959 | -3.4686 | -2.4493 | -1.4316 | -0.24478
42838.4268 | 565 | 22.8977 | 22.8568 | 22.8455 | 22.7539 | 22.3648 | 21.6991 | 22.6982 | 21.7518 | 22.3434 | 22.3533 | 22.3223 | 21.9724 | 21.1911 | 22.1672 | 21.59 | 21.7668 | 21.902 | 21.0696 | 21.2139 | 21.8929 | 20.4804 | 21.5293 | 27.0008 | 21.9438 | 22.5069 | 31.5569 | 216.6886 | 191.4289 | 248.0383 | 22.1286 | 22.3102 | 28.8606 | 22.0623 | 22.4971 | 31.5378 | 102.3511 | 286.0097 |  | 149.504 | 191.1896 | 186.4541 | 194.7641 |  | 18.1692 | 19.9977 | 18.4344 | 20.0529 | 22.3398 | 50.0323 | 162.8135 | 15.8639 | 17.5688 | 16.0083 | 19.7515 | 19.0456 | 45.9443 | 49.0495 | 45.0842 | 21.6833 |  |  | 1.2895 | -0.29905 | -33.0393 | 0.43628 | 0.80378 | -160.4798 | 13.3489 | 1.3224 | 0.25307 | 0.27852 | 0.96898 | 8.8257 | 9.0575 | 0.16205 | 21.9973 | 21.9544 | 22.1522 | 22.2048 | 22.0167 | 21.3066 | 20.1113 | 22.1812 | 22.3585 | 22.3918 | 22.3379 | 21.9542 | 21.1813 | 22.2711 | 114.2049 | 77.7971 | 71.9042 | 45.8057 | 40.1228 | 70.1741 | 44.9444 | 22.3205 | 22.0712 | 21.6626 | 22.0481 | 21.7892 | 21.7608 | 21.9421 | 21.924 | 27.212 | 85.8833 | 194.8529 | 166.6178 | 128.6273 | 2.1121 | 2.218 | 94.7848 | 21.8882 | 22.2085 | 21.2418 | 21.551 | 22.014 | 22.0433 | 23.1612 | 37.6379 | 21.8379 | 22.0903 | 28.5792 | 218.7276 | 295.8975 | 163.3962 | 167.5113 | 135.3806 |  | 87.3994 | 172.8412 | 92.4642 | 149.1466 | 131.393 | 98.1674 |  | 112.6792 |  |  | 28.2513 | 37.1948 | 91.0593 | [5 empty] | 21.8861 | 108.0817 | 21.7062 | 22.0938 | 45.2237 | 21.2892 | 21.9176 | 43.6485 | 153.1702 | 329.5986 |  | 127.9866 | 207.3236 | 28.676 | 119.208 | 244.8639 | 86.0289 | 180.2314 | 33.7431 | 163.7727 | 34.3025 | 164.6884 | 19.8974 | 128.1153 | 198.9985 | 46.1669 | 120.925 | 237.1807 | 28.2085 | 122.7387 | 227.8427 | 28.6817 | 150.2014 | 49.5426 | 162.5408 | 35.6459 | 177.8112 | 3.4754 | 18.4002 | 2.2941 | 0.070584 | -27.2692 | 3.0948 | 452.7 | 51.68 | 1.8066 | -0.65251 | -6.8584 | 0.78812 | 1.1232 | -15.8709 | 4.5773 | -0.37464 | -1.2195 | 1.0254 | -4.1045 | -2.415 | -1.4398 | -0.24518
42838.4268 | 566 | 22.8901 | 22.8496 | 22.845 | 22.7614 | 22.3662 | 21.6918 | 22.6929 | 21.7512 | 22.3385 | 22.349 | 22.3178 | 21.9709 | 21.1851 | 22.1587 | 21.5889 | 21.7659 | 21.9045 | 21.072 | 21.221 | 21.9038 | 20.4894 | 21.5258 | 27.0344 | 21.9444 | 22.5111 | 31.5978 | 219.209 | 192.6318 | 252.1623 | 22.1274 | 22.3179 | 28.8937 | 22.0514 | 22.4983 | 31.5818 | 102.9487 | 292.7845 |  | 150.622 | 193.4711 | 187.475 | 197.5286 |  | 18.1923 | 20.0506 | 18.459 | 20.1188 | 22.4377 | 50.0859 | 165.0714 | 15.8362 | 17.5743 | 15.9444 | 19.7788 | 19.0513 | 45.9461 | 49.0535 | 45.0711 | 21.6782 |  |  | 1.0989 | -0.23531 | -33.5019 | 0.56771 | 0.39966 | -159.6078 | 12.6911 | 1.283 | 0.014494 | 0.38069 | 0.98842 | 8.3083 | 8.5264 | 0.12266 | 22.0053 | 21.9551 | 22.1467 | 22.1978 | 22.0083 | 21.2993 | 20.1076 | 22.173 | 22.3553 | 22.3867 | 22.3369 | 21.9522 | 21.1748 | 22.2657 | 117.2492 | 82.0618 | 78.2475 | 48.2598 | 40.8786 | 70.478 | 45.141 | 22.3185 | 22.0781 | 21.6669 | 22.0528 | 21.7946 | 21.7592 | 21.9427 | 21.9268 | 27.2443 | 86.2728 | 196.2046 | 167.4606 | 129.1346 | 3.1187 | 2.3659 | 95.5321 | 21.8884 | 22.2019 | 21.2698 | 21.5559 | 22.018 | 22.0481 | 23.1711 | 37.6983 | 21.8379 | 22.1008 | 28.6183 | 221.227 | 301.5746 | 164.0676 | 168.1902 | 136.0578 |  | 87.8455 | 172.8308 | 92.9414 | 149.4575 | 131.9426 | 98.9014 |  | 113.241 |  |  | 28.3825 | 38.1199 | 90.4815 | [5 empty] | 21.8849 | 108.7263 | 21.7025 | 22.0959 | 45.6919 | 21.2907 | 21.9129 | 43.9181 | 154.4492 | 332.8069 |  | 129.1316 | 209.5375 | 28.7846 | 119.9422 | 248.8931 | 86.9841 | 182.2289 | 33.8933 | 164.4825 | 34.4968 | 165.9524 | 19.8878 | 129.0055 | 200.729 | 46.4992 | 121.6439 | 238.9501 | 28.355 | 123.879 | 230.1955 | 28.7768 | 151.5487 | 49.9483 | 163.7367 | 35.8498 | 179.5692 | 3.3385 | 18.3954 | 2.3012 | 0.070519 | -27.2694 | 3.0949 | 465.31 | 52.61 | 1.6744 | -0.57886 | -6.9069 | 0.89911 | 0.79208 | -15.829 | 4.4635 | -0.37631 | -1.2007 | 1.0403 | -4.4062 | -3.0966 | -1.4928 | -0.24436
42838.4268 | 567 | 22.8874 | 22.8618 | 22.8502 | 22.759 | 22.3771 | 21.6997 | 22.6955 | 21.7533 | 22.3491 | 22.3504 | 22.3212 | 21.9785 | 21.1955 | 22.1672 | 21.5933 | 21.767 | 21.9079 | 21.0705 | 21.2157 | 21.9075 | 20.4902 | 21.5346 | 27.0621 | 21.9465 | 22.5151 | 31.6394 | 221.6606 | 193.7888 | 255.0419 | 22.1286 | 22.3286 | 28.9233 | 22.0571 | 22.5162 | 31.6141 | 103.627 | 299.9024 |  | 151.8209 | 195.4586 | 189.2457 | 200.9041 |  | 18.2061 | 20.1044 | 18.5014 | 20.1944 | 22.5167 | 49.6175 | 167.1227 | 15.7721 | 17.5781 | 15.9116 | 19.795 | 19.0531 | 45.953 | 49.0546 | 45.0841 | 21.68 |  |  | 0.69875 | -0.092717 | -33.5827 | 0.40671 | 0.6441 | -159.3101 | 13.3036 | 0.84535 | 0.11588 | 0.32132 | 0.90318 | 6.9113 | 7.0926 | 0.12594 | 22.0056 | 21.9604 | 22.1467 | 22.201 | 22.0075 | 21.3036 | 20.1142 | 22.1693 | 22.3569 | 22.3896 | 22.3368 | 21.9536 | 21.1738 | 22.2665 | 119.8655 | 84.4251 | 84.5902 | 50.2398 | 42.2778 | 70.7812 | 45.4223 | 22.3227 | 22.0837 | 21.67 | 22.0558 | 21.7966 | 21.7678 | 21.9475 | 21.9313 | 27.269 | 86.6856 | 197.3822 | 168.3118 | 130.3911 | 2.0621 | 2.275 | 96.9602 | 21.8886 | 22.1992 | 21.2849 | 21.555 | 22.0204 | 22.0411 | 23.1808 | 37.7548 | 21.8393 | 22.11 | 28.6518 | 223.8669 | 310.1017 | 165.4899 | 169.4847 | 136.7602 |  | 88.2592 | 172.028 | 93.3727 | 150.8892 | 132.496 | 99.5933 |  | 113.8128 |  |  | 28.4885 | 38.6313 | 89.6581 | [5 empty] | 21.8908 | 109.8013 | 21.7052 | 22.0923 | 46.2267 | 21.2869 | 21.9209 | 44.1858 | 155.8478 | 335.5853 |  | 130.3233 | 212.069 | 28.8992 | 120.5795 | 253.5387 | 87.9785 | 183.6869 | 34.0516 | 165.092 | 34.71 | 167.8427 | 19.8962 | 129.8 | 202.8657 | 46.8291 | 122.3902 | 241.352 | 28.5253 | 124.8733 | 232.6317 | 28.8843 | 152.9765 | 50.3822 | 165.0388 | 36.0735 | 181.3848 | 3.6173 | 18.3904 | 2.3076 | 0.071223 | -27.2556 | 3.0949 | 486.4 | 51.53 | 1.3388 | -0.36339 | -6.9159 | 0.76108 | 1.0048 | -15.8028 | 4.5666 | -0.37991 | -1.1616 | 1.0243 | -4.6605 | -3.768 | -1.5595 | -0.26344
42838.4269 | 568 | 22.8853 | 22.8476 | 22.8394 | 22.7502 | 22.3609 | 21.6957 | 22.6903 | 21.7479 | 22.3388 | 22.3459 | 22.3154 | 21.9624 | 21.1802 | 22.1521 | 21.5898 | 21.7636 | 21.9059 | 21.0706 | 21.208 | 21.9039 | 20.4828 | 21.5408 | 27.0858 | 21.9383 | 22.5125 | 31.6834 | 223.5657 | 194.6893 | 256.4433 | 22.1315 | 22.3333 | 28.9628 | 22.062 | 22.5181 | 31.6714 | 104.2861 | 306.5137 |  | 153.0683 | 198.0025 | 191.1611 | 205.4939 |  | 18.2304 | 20.1642 | 18.5457 | 20.2541 | 22.6361 | 49.6824 | 168.5616 | 15.7385 | 17.5866 | 15.8863 | 19.8164 | 19.0508 | 45.9448 | 49.0576 | 45.0881 | 21.6772 |  |  | 0.64552 | -0.13543 | -33.4447 | 0.7103 | 0.54882 | -161.3833 | 13.5493 | 1.3152 | 0.1871 | 0.41048 | 1.0502 | 5.7816 | 5.933 | 0.12142 | 22.0083 | 21.9582 | 22.1465 | 22.2074 | 22.0091 | 21.3039 | 20.1115 | 22.1715 | 22.3556 | 22.3951 | 22.3327 | 21.9528 | 21.1745 | 22.2669 | 119.4071 | 83.1619 | 82.6347 | 50.6491 | 42.9412 | 71.0492 | 45.636 | 22.3176 | 22.0771 | 21.667 | 22.0497 | 21.7904 | 21.7628 | 21.9391 | 21.9283 | 27.2996 | 87.0811 | 198.7655 | 169.3381 | 132.0383 | 1.9294 | 1.3613 | 98.2966 | 21.9004 | 22.2195 | 21.3205 | 21.5662 | 22.0187 | 22.0639 | 23.2007 | 37.8224 | 21.8524 | 22.1168 | 28.687 | 227.0903 | 317.3607 | 167.0781 | 170.9924 | 136.5882 |  | 88.6756 | 172.7162 | 93.7928 | 153.2967 | 133.0687 | 100.8595 |  | 114.4394 |  |  | 28.5856 | 39.258 | 89.2318 | [5 empty] | 21.8975 | 111.2785 | 21.7065 | 22.0981 | 46.7737 | 21.2927 | 21.9199 | 44.453 | 157.2474 | 338.947 |  | 131.2583 | 215.0604 | 29.0147 | 121.2113 | 259.9261 | 89.0234 | 184.9225 | 34.2247 | 165.9557 | 34.9306 | 168.6865 | 19.9297 | 130.5214 | 205.3463 | 47.1794 | 123.2358 | 243.1408 | 28.7176 | 125.5502 | 235.7484 | 29.0207 | 154.5249 | 50.8713 | 165.8273 | 36.2917 | 182.9826 | 3.8236 | 18.3838 | 2.314 | 0.072109 | -27.251 | 3.0949 | 479.95 | 52.1 | 1.2885 | -0.43923 | -6.9024 | 1.0059 | 0.92762 | -15.9069 | 4.6091 | -0.3591 | -1.1644 | 0.98202 | -4.5773 | -3.5254 | -1.6606 | -0.29402
42838.4269 | 569 | 22.8832 | 22.8459 | 22.8361 | 22.7489 | 22.3581 | 21.6807 | 22.6848 | 21.7441 | 22.3342 | 22.3417 | 22.3094 | 21.9602 | 21.1731 | 22.1493 | 21.5854 | 21.763 | 21.905 | 21.0682 | 21.2128 | 21.908 | 20.4757 | 21.5376 | 27.1156 | 21.9395 | 22.5178 | 31.7295 | 225.1761 | 195.6163 | 257.4005 | 22.1225 | 22.3217 | 28.9811 | 22.0539 | 22.513 | 31.7051 | 104.9153 | 307.9488 |  | 154.2999 | 200.7548 | 193.0762 | 207.9586 |  | 18.2769 | 20.2364 | 18.6104 | 20.3602 | 22.7984 | 50.5602 | 170.0116 | 15.7652 | 17.5985 | 15.8926 | 19.8536 | 19.0538 | 45.9571 | 49.0585 | 45.1006 | 21.6803 |  |  | 0.79271 | -0.38645 | -33.6169 | 0.56967 | 0.39703 | -160.2866 | 13.3752 | 1.1036 | 0.31846 | 0.37377 | 0.87228 | 4.8747 | 5.0024 | 0.11432 | 22.0087 | 21.9605 | 22.1444 | 22.2113 | 22.0097 | 21.302 | 20.1106 | 22.1736 | 22.3468 | 22.3896 | 22.3325 | 21.954 | 21.1729 | 22.2639 | 119.2316 | 80.7519 | 77.6913 | 49.8682 | 42.7411 | 71.3353 | 45.7774 | 22.32 | 22.0832 | 21.6668 | 22.0398 | 21.7932 | 21.7687 | 21.9421 | 21.9334 | 27.3396 | 87.5578 | 201.1788 | 170.5918 | 132.978 | 2.3026 | 1.355 | 99.5783 | 21.905 | 22.2056 | 21.3479 | 21.5664 | 22.0204 | 22.0546 | 23.1987 | 37.8796 | 21.8525 | 22.1205 | 28.7208 | 228.8711 | 327.6688 | 168.6304 | 172.6382 | 138.1384 |  | 89.1014 | 173.3557 | 94.2308 | 155.4308 | 133.7036 | 101.4103 |  | 115.1746 |  |  | 28.6887 | 40.1655 | 89.3758 | [5 empty] | 21.8899 | 113.0386 | 21.705 | 22.0952 | 47.3911 | 21.29 | 21.9093 | 44.7256 | 158.7178 | 342.5524 |  | 132.2629 | 219.1252 | 29.1466 | 121.8823 | 266.5272 | 90.1302 | 186.3148 | 34.4374 | 166.6914 | 35.1903 | 169.8757 | 19.9682 | 131.3417 | 207.5868 | 47.5452 | 124.1979 | 244.5084 | 28.9115 | 126.2598 | 238.4398 | 29.1778 | 155.937 | 51.367 | 166.6905 | 36.5202 | 184.755 | 4.059 | 18.3776 | 2.3204 | 0.07094 | -27.3171 | 3.0949 | 500.14 | 52.11 | 1.4292 | -0.74205 | -6.9209 | 0.90095 | 0.79005 | -15.8743 | 4.5856 | -0.38575 | -1.165 | 0.95005 | -4.5233 | -2.9594 | -1.7039 | -0.30182
42838.4269 | 570 | 22.8793 | 22.8528 | 22.8403 | 22.7466 | 22.3608 | 21.693 | 22.6884 | 21.7418 | 22.3413 | 22.3516 | 22.313 | 21.9635 | 21.1807 | 22.1516 | 21.594 | 21.767 | 21.9108 | 21.0714 | 21.2227 | 21.9172 | 20.4791 | 21.5476 | 27.1558 | 21.9472 | 22.53 | 31.7778 | 226.937 | 196.9057 | 259.8636 | 22.1282 | 22.329 | 29.0261 | 22.0519 | 22.521 | 31.7491 | 105.5194 | 316.0249 |  | 155.7068 | 203.1178 | 194.9634 | 209.647 |  | 18.3143 | 20.3002 | 18.6727 | 20.4531 | 22.8664 | 50.6743 | 171.6181 | 15.7925 | 17.6064 | 15.8794 | 19.8763 | 19.0613 | 45.9568 | 49.0629 | 45.096 | 21.6879 |  |  | 1.484 | -0.3871 | -33.3251 | 0.49673 | 0.80576 | -159.4921 | 12.6445 | 1.3099 | 0.31651 | 0.33453 | 0.96273 | 4.1359 | 4.2445 | 0.10467 | 22.0004 | 21.9645 | 22.1456 | 22.1989 | 22.0154 | 21.299 | 20.0976 | 22.1679 | 22.3549 | 22.3857 | 22.3308 | 21.9546 | 21.1813 | 22.262 | 121.6454 | 81.278 | 79.4364 | 49.4242 | 42.5552 | 71.6813 | 45.9574 | 22.316 | 22.0752 | 21.6607 | 22.0419 | 21.7877 | 21.7752 | 21.9421 | 21.9332 | 27.3616 | 87.9912 | 204.4929 | 171.9767 | 133.7813 | 4.1363 | 2.4648 | 99.9768 | 21.9074 | 22.2085 | 21.3713 | 21.5656 | 22.0205 | 22.0637 | 23.2122 | 37.9376 | 21.8473 | 22.1148 | 28.7528 | 231.5044 | 342.0854 | 170.6434 | 174.6401 | 141.1911 |  | 89.6219 | 172.0463 | 94.6267 | 157.7344 | 134.4127 | 102.1904 |  | 116.0104 |  |  | 28.8596 | 40.501 | 89.6699 | [5 empty] | 21.8845 | 115.2261 | 21.6973 | 22.0912 | 48.0656 | 21.2829 | 21.9108 | 45.0293 | 160.3038 | 346.8476 |  | 133.2977 | 222.3462 | 29.3034 | 122.6475 | 273.4094 | 91.2158 | 188.0417 | 34.6665 | 167.156 | 35.4754 | 171.7295 | 20.0028 | 132.245 | 210.0825 | 47.9562 | 125.2988 | 245.7636 | 29.121 | 127.3896 | 241.2987 | 29.3371 | 157.2342 | 51.8483 | 167.5586 | 36.7771 | 186.3119 | 2.9695 | 18.3725 | 2.3276 | 0.06927 | -27.1818 | 3.0948 | 476.42 | 51.63 | 1.96 | -0.74276 | -6.8916 | 0.84139 | 1.1257 | -15.8377 | 4.4594 | -0.45046 | -1.1132 | 0.91662 | -4.7499 | -3.1319 | -1.7266 | -0.30747
42838.4269 | 571 | 22.88 | 22.8559 | 22.8358 | 22.7499 | 22.3555 | 21.6868 | 22.6877 | 21.7403 | 22.3357 | 22.3441 | 22.3105 | 21.9661 | 21.1785 | 22.1508 | 21.5925 | 21.7671 | 21.9092 | 21.0707 | 21.2233 | 21.9228 | 20.4822 | 21.5601 | 27.1888 | 21.9474 | 22.5379 | 31.8171 | 229.1452 | 198.1826 | 262.4419 | 22.129 | 22.3376 | 29.0594 | 22.0509 | 22.5267 | 31.794 | 106.1596 | 320.4656 |  | 157.139 | 205.333 | 196.8477 | 210.8002 |  | 18.3604 | 20.3812 | 18.7294 | 20.557 | 23.0131 | 51.282 | 173.3802 | 15.7941 | 17.6199 | 15.8805 | 19.9149 | 19.0717 | 45.9588 | 49.0688 | 45.0841 | 21.6899 |  |  | 1.344 | 0.002563 | -33.6964 | 0.62093 | 0.60796 | -158.6917 | 13.0585 | 1.3737 | 0.19333 | 0.33663 | 1.1148 | 3.5224 | 3.615 | 0.10293 | 22.0137 | 21.9708 | 22.1577 | 22.2098 | 22.0227 | 21.307 | 20.1132 | 22.1894 | 22.3598 | 22.4017 | 22.3506 | 21.9596 | 21.1952 | 22.2702 | 123.7098 | 81.1884 | 84.2753 | 50.9222 | 43.7482 | 72.0265 | 46.1985 | 22.3227 | 22.0775 | 21.6664 | 22.0446 | 21.7956 | 21.7817 | 21.9417 | 21.9366 | 27.3993 | 88.4777 | 207.3859 | 173.5238 | 135.2188 | 3.0507 | 1.1313 | 99.6411 | 21.9055 | 22.2146 | 21.4239 | 21.5704 | 22.0218 | 22.0631 | 23.2246 | 38.0007 | 21.8548 | 22.1282 | 28.7838 | 235.0172 | 356.0751 | 173.0018 | 176.9269 | 144.3096 |  | 90.129 | 172.5217 | 95.0013 | 160.7512 | 135.0954 | 103.7323 |  | 116.7951 |  |  | 29.0549 | 40.707 | 89.8326 | [5 empty] | 21.8821 | 117.6598 | 21.6926 | 22.0918 | 48.8456 | 21.288 | 21.9101 | 45.3365 | 161.932 | 350.4119 |  | 134.2356 | 225.1108 | 29.4645 | 123.4834 | 278.6696 | 92.3217 | 190.1351 | 34.8845 | 167.6568 | 35.7804 | 173.1587 | 20.0406 | 133.198 | 212.7111 | 48.4251 | 126.4775 | 247.2019 | 29.3358 | 128.4679 | 244.2298 | 29.5022 | 158.3468 | 52.3744 | 168.6154 | 37.062 | 187.7931 | 4.0004 | 18.3657 | 2.3352 | 0.068392 | -27.2266 | 3.0948 | 497.01 | 53.22 | 1.8698 | 0.060446 | -6.9308 | 0.94084 | 0.97874 | -15.8127 | 4.536 | -0.5175 | -1.1118 | 0.8623 | -4.9377 | -3.641 | -1.733 | -0.32868
42838.4269 | 572 | 22.8871 | 22.8555 | 22.8351 | 22.7568 | 22.3657 | 21.6884 | 22.6866 | 21.7475 | 22.3368 | 22.3446 | 22.3178 | 21.9669 | 21.181 | 22.1507 | 21.5932 | 21.7675 | 21.9077 | 21.0729 | 21.2194 | 21.9155 | 20.4832 | 21.5588 | 27.2117 | 21.942 | 22.5342 | 31.8579 | 231.8739 | 199.9476 | 267.6532 | 22.1237 | 22.337 | 29.09 | 22.0535 | 22.5342 | 31.8367 | 106.8324 | 327.3936 |  | 158.5087 | 207.2584 | 198.8115 | 212.4506 |  | 18.3993 | 20.4652 | 18.7976 | 20.6439 | 23.1366 | 50.9964 | 174.6588 | 15.7981 | 17.6258 | 15.8897 | 19.9484 | 19.0756 | 45.9525 | 49.0674 | 45.0792 | 21.6888 |  |  | 1.1423 | -0.10849 | -33.379 | 0.54339 | 0.83467 | -159.4021 | 12.9875 | 1.3829 | 0.23186 | 0.43251 | 1.1587 | 3.0095 | 3.0887 | 0.099305 | 22.019 | 21.962 | 22.1536 | 22.207 | 22.0112 | 21.298 | 20.1124 | 22.1781 | 22.3566 | 22.3969 | 22.3363 | 21.9537 | 21.1776 | 22.2655 | 127.2575 | 82.6039 | 84.3986 | 50.8349 | 44.4519 | 72.3934 | 46.3914 | 22.3158 | 22.0758 | 21.6612 | 22.0399 | 21.7866 | 21.7856 | 21.9402 | 21.934 | 27.4296 | 88.9772 | 208.9895 | 174.6794 | 136.4216 | 2.9386 | 2.4869 | 100.3642 | 21.9052 | 22.2195 | 21.4642 | 21.5683 | 22.0211 | 22.0653 | 23.2276 | 38.0595 | 21.8502 | 22.1308 | 28.8205 | 237.473 | 374.8993 | 175.1059 | 179.006 | 146.7876 |  | 90.6691 | 171.6648 | 95.3984 | 163.8155 | 135.815 | 104.3334 |  | 117.7169 |  |  | 29.2847 | 41.9891 | 90.3576 | [5 empty] | 21.8944 | 120.4019 | 21.6999 | 22.0979 | 49.6618 | 21.2915 | 21.9122 | 45.6605 | 163.6415 | 354.3452 |  | 135.1547 | 229.0127 | 29.6397 | 124.6458 | 284.8327 | 93.6008 | 192.3044 | 35.0949 | 168.3314 | 36.1701 | 174.6239 | 20.076 | 134.0181 | 215.6907 | 48.8978 | 127.6561 | 249.1728 | 29.5602 | 129.584 | 246.1305 | 29.6966 | 159.4158 | 52.9164 | 169.8588 | 37.3944 | 189.8299 | 4.2775 | 18.3587 | 2.3426 | 0.068748 | -27.2077 | 3.0948 | 502.85 | 51.63 | 1.7321 | -0.39332 | -6.8991 | 0.88026 | 1.1463 | -15.8411 | 4.5217 | -0.56544 | -1.0724 | 0.8083 | -5.2877 | -3.6319 | -1.7518 | -0.34285
42838.4269 | 573 | 22.8879 | 22.8561 | 22.8471 | 22.7645 | 22.3714 | 21.6973 | 22.698 | 21.7534 | 22.3475 | 22.3538 | 22.3186 | 21.9731 | 21.1764 | 22.1583 | 21.5954 | 21.7682 | 21.9083 | 21.0735 | 21.2167 | 21.9244 | 20.4902 | 21.5669 | 27.2498 | 21.9403 | 22.5482 | 31.9103 | 234.5146 | 202.1564 | 270.8767 | 22.1208 | 22.3385 | 29.1143 | 22.0574 | 22.5398 | 31.8723 | 107.5359 | 337.1427 |  | 159.9783 | 209.8525 | 200.7101 | 213.0727 |  | 18.4455 | 20.5417 | 18.8495 | 20.7336 | 23.204 | 50.832 | 176.5767 | 15.8591 | 17.6314 | 15.9055 | 19.9701 | 19.0884 | 45.9374 | 49.0671 | 45.079 | 21.694 |  |  | 0.99182 | -0.22086 | -33.653 | 0.26675 | 0.48508 | -160.1111 | 13.3496 | 0.99386 | 0.21513 | 0.38363 | 1.2721 | 2.5815 | 2.6495 | 0.083654 | 22.0172 | 21.9574 | 22.1479 | 22.2053 | 22.0108 | 21.299 | 20.1077 | 22.1745 | 22.3506 | 22.3873 | 22.3319 | 21.9502 | 21.1715 | 22.2594 | 127.7422 | 83.3063 | 85.5607 | 51.6964 | 44.8452 | 72.6879 | 46.5994 | 22.2953 | 22.0708 | 21.6457 | 22.0253 | 21.7781 | 21.7754 | 21.9306 | 21.9312 | 27.4488 | 89.5406 | 212.0178 | 176.319 | 137.3623 | 3.0733 | 1.7862 | 101.1815 | 21.8911 | 22.2108 | 21.5004 | 21.5578 | 22.0159 | 22.0646 | 23.2308 | 38.1109 | 21.842 | 22.1332 | 28.8566 | 239.9458 | 394.6548 | 177.2515 | 180.9657 | 150.0932 |  | 91.3448 | 169.8294 | 95.8585 | 168.2917 | 136.7114 | 105.9033 |  | 118.7502 |  |  | 29.5595 | 43.0122 | 90.944 | [5 empty] | 21.8898 | 123.2527 | 21.6971 | 22.0948 | 50.4571 | 21.2909 | 21.9054 | 46.0382 | 165.4112 | 358.821 |  | 136.2206 | 232.6085 | 29.8404 | 125.7432 | 289.926 | 94.9487 | 195.7691 | 35.3522 | 169.2792 | 36.5521 | 175.6315 | 20.1135 | 135.0851 | 217.943 | 49.34 | 128.8204 | 251.6225 | 29.829 | 130.3619 | 248.5438 | 29.8678 | 160.3991 | 53.4312 | 171.1992 | 37.7581 | 191.609 | 4.6212 | 18.3522 | 2.351 | 0.06898 | -27.1992 | 3.0948 | 513.63 | 52.12 | 1.6188 | -0.56127 | -6.9283 | 0.61682 | 0.87365 | -15.8722 | 4.5831 | -0.6311 | -1.0034 | 0.72281 | -5.306 | -3.7364 | -1.7407 | -0.34725
42838.4269 | 574 | 22.9004 | 22.8537 | 22.8312 | 22.7544 | 22.3653 | 21.6908 | 22.6925 | 21.7443 | 22.3396 | 22.3519 | 22.3197 | 21.9684 | 21.1886 | 22.1533 | 21.6001 | 21.7668 | 21.9096 | 21.0717 | 21.2199 | 21.9382 | 20.4932 | 21.5789 | 27.2781 | 21.9499 | 22.5523 | 31.9643 | 236.8019 | 203.6769 | 271.7913 | 22.1229 | 22.3431 | 29.1653 | 22.0556 | 22.542 | 31.913 | 108.3322 | 337.4371 |  | 161.4576 | 212.9072 | 202.6097 | 217.1412 |  | 18.4945 | 20.643 | 18.9231 | 20.8441 | 23.3098 | 50.7847 | 178.2636 | 15.9559 | 17.6498 | 15.9272 | 19.9976 | 19.0987 | 45.9177 | 49.063 | 45.0774 | 21.6944 |  |  | 0.94779 | -0.27408 | -33.9053 | 0.32391 | 0.56722 | -162.7304 | 13.4495 | 1.4295 | 0.052441 | 0.32698 | 1.1971 | 2.224 | 2.2826 | 0.080559 | 22.0162 | 21.9586 | 22.1447 | 22.2038 | 22.0141 | 21.2987 | 20.1067 | 22.1724 | 22.3513 | 22.3842 | 22.3391 | 21.9531 | 21.1721 | 22.2686 | 126.1315 | 80.551 | 85.9675 | 52.8346 | 46.1492 | 72.9719 | 46.8271 | 22.3169 | 22.0733 | 21.6655 | 22.0502 | 21.7865 | 21.7931 | 21.935 | 21.9425 | 27.4882 | 90.1763 | 215.069 | 178.1116 | 139.3244 | 3.9776 | 1.7955 | 101.9346 | 21.895 | 22.2207 | 21.55 | 21.5593 | 22.0192 | 22.0696 | 23.2461 | 38.1737 | 21.8413 | 22.1468 | 28.8889 | 242.8664 | 413.5809 | 179.5022 | 182.9753 | 152.6783 |  | 91.9614 | 169.6074 | 96.3087 | 173.4788 | 137.5806 | 107.4602 |  | 119.6175 |  |  | 29.7991 | 44.0427 | 92.2211 | [5 empty] | 21.8806 | 126.4029 | 21.7026 | 22.0911 | 51.333 | 21.2864 | 21.9097 | 46.4612 | 167.3118 | 364.1706 |  | 137.4462 | 236.6191 | 30.0487 | 126.7513 | 295.4189 | 96.3886 | 198.9455 | 35.6354 | 170.4341 | 36.9361 | 176.7886 | 20.1615 | 136.5149 | 220.4182 | 49.805 | 130.0239 | 252.9046 | 30.1093 | 130.8605 | 251.3523 | 30.0346 | 161.4096 | 54.0562 | 172.4478 | 38.1267 | 193.8885 | 5.0464 | 18.3445 | 2.358 | 0.06914 | -27.1873 | 3.0948 | 535.13 | 51.58 | 1.5838 | -0.62536 | -6.9554 | 0.67983 | 0.94465 | -16.0004 | 4.5999 | -0.67899 | -0.97963 | 0.61649 | -5.0929 | -3.7546 | -1.8216 | -0.37719
42838.4269 | 575 | 22.8862 | 22.86 | 22.8419 | 22.7586 | 22.3701 | 21.6938 | 22.6909 | 21.7478 | 22.3426 | 22.3476 | 22.3191 | 21.9703 | 21.1827 | 22.1567 | 21.5979 | 21.7686 | 21.9225 | 21.075 | 21.2207 | 21.9389 | 20.4875 | 21.5814 | 27.3121 | 21.9564 | 22.5628 | 32.0073 | 238.6482 | 205.1038 | 271.9728 | 22.1308 | 22.3553 | 29.2011 | 22.0577 | 22.5415 | 31.9645 | 109.2297 | 353.756 |  | 163.2093 | 215.9113 | 204.8812 | 220.3776 |  | 18.5386 | 20.7247 | 18.9991 | 20.9594 | 23.4914 | 51.6519 | 180.0234 | 15.9885 | 17.664 | 15.9688 | 20.0371 | 19.098 | 45.9086 | 49.053 | 45.0789 | 21.6877 |  |  | 0.89259 | -0.23466 | -34.5362 | 0.53025 | 1.0029 | -160.5159 | 12.4033 | 1.3172 | 0.23692 | 0.36894 | 1.6214 | 1.9229 | 1.9737 | 0.095962 | 22.0092 | 21.9574 | 22.1487 | 22.2039 | 22.0071 | 21.2936 | 20.1077 | 22.1737 | 22.346 | 22.387 | 22.3404 | 21.9441 | 21.1746 | 22.2674 | 131.1151 | 83.6472 | 90.377 | 53.88 | 46.1602 | 73.3935 | 47.0935 | 22.3126 | 22.0728 | 21.6637 | 22.0371 | 21.7869 | 21.7836 | 21.9362 | 21.9455 | 27.5173 | 90.7279 | 216.84 | 179.5194 | 140.3732 | 3.7386 | 2.3113 | 103.5876 | 21.8911 | 22.2111 | 21.5856 | 21.5519 | 22.01 | 22.0636 | 23.2481 | 38.2348 | 21.8443 | 22.1415 | 28.9103 | 247.4633 | 432.1759 | 181.5931 | 184.8759 | 156.0314 |  | 92.5782 | 170.77 | 96.7507 | 177.0429 | 138.5222 | 108.361 |  | 120.6171 |  |  | 30.059 | 44.7465 | 93.4691 | [5 empty] | 21.8855 | 130.4659 | 21.6999 | 22.0856 | 52.2481 | 21.2849 | 21.9074 | 46.8853 | 169.3232 | 369.0706 |  | 138.6982 | 241.4939 | 30.2622 | 127.9288 | 302.9945 | 97.9237 | 201.2929 | 35.9577 | 171.7147 | 37.3873 | 178.0573 | 20.1828 | 137.4537 | 222.9879 | 50.2587 | 131.0221 | 256.1272 | 30.4072 | 131.8146 | 254.675 | 30.296 | 162.4419 | 54.7397 | 173.7121 | 38.565 | 196.7333 | 5.5714 | 18.3382 | 2.3652 | 0.067848 | -27.2899 | 3.0948 | 523.51 | 51.72 | 1.5372 | -0.57872 | -7.0208 | 0.86994 | 1.2578 | -15.9124 | 4.4233 | -0.74817 | -0.99458 | 0.55849 | -5.5958 | -4.2129 | -1.8753 | -0.38499
42838.4269 | 576 | 22.8813 | 22.8502 | 22.8365 | 22.7545 | 22.3688 | 21.6934 | 22.6898 | 21.7412 | 22.3429 | 22.3488 | 22.3133 | 21.9631 | 21.1773 | 22.1508 | 21.5955 | 21.7688 | 21.9142 | 21.0706 | 21.2244 | 21.9442 | 20.4892 | 21.587 | 27.3375 | 21.9504 | 22.5669 | 32.06 | 241.2665 | 207.7917 | 275.9 | 22.1284 | 22.3572 | 29.2454 | 22.0605 | 22.5548 | 32.0075 | 110.0862 | 367.4077 |  | 165.0947 | 219.1798 | 207.5409 | 226.9937 |  | 18.589 | 20.8174 | 19.0787 | 21.0696 | 23.7225 | 53.3299 | 182.0617 | 16.0327 | 17.6732 | 15.985 | 20.0797 | 19.1144 | 45.904 | 49.0607 | 45.0979 | 21.6932 |  |  | 0.60215 | -0.075633 | -34.1301 | 0.51316 | 0.9109 | -160.9365 | 12.3547 | 1.3934 | 0.068982 | 0.23844 | 1.7667 | 1.6672 | 1.7115 | 0.12597 | 22.0183 | 21.9577 | 22.1491 | 22.2013 | 22.0147 | 21.292 | 20.1143 | 22.1715 | 22.3504 | 22.3927 | 22.3406 | 21.9427 | 21.1743 | 22.2626 | 135.1767 | 86.8551 | 91.4341 | 54.6125 | 46.736 | 73.843 | 47.3717 | 22.3124 | 22.0791 | 21.6695 | 22.0468 | 21.7948 | 21.7959 | 21.9384 | 21.9479 | 27.5531 | 91.2942 | 219.2919 | 181.1209 | 141.7609 | 4.2424 | 2.2493 | 104.5256 | 21.8961 | 22.2081 | 21.6429 | 21.5555 | 22.0103 | 22.0606 | 23.2575 | 38.3108 | 21.841 | 22.1497 | 28.9432 | 250.7168 | 450.3942 | 184.2102 | 187.2978 | 161.2884 |  | 93.3409 | 169.6757 | 97.2123 | 180.1722 | 139.6622 | 109.4031 |  | 121.5943 |  |  | 30.3964 | 44.8508 | 95.126 | [5 empty] | 21.8887 | 134.4306 | 21.7021 | 22.0957 | 53.2714 | 21.286 | 21.9118 | 47.2974 | 171.413 | 374.3176 |  | 139.9774 | 245.1582 | 30.5165 | 129.119 | 311.191 | 99.416 | 204.3492 | 36.3541 | 173.0056 | 37.8714 | 179.0965 | 20.1975 | 138.4158 | 226.353 | 50.7895 | 132.2252 | 260.2673 | 30.7327 | 132.6778 | 259.5157 | 30.5783 | 164.1485 | 55.4741 | 175.8547 | 38.9646 | 199.4054 | 5.5174 | 18.3307 | 2.3729 | 0.066359 | -27.3 | 3.0948 | 527.21 | 52.61 | 1.2671 | -0.3286 | -6.9805 | 0.85594 | 1.2018 | -15.9743 | 4.426 | -0.86452 | -0.94605 | 0.52134 | -5.9929 | -4.2974 | -2.0244 | -0.40161
42838.427 | 577 | 22.8834 | 22.8533 | 22.8439 | 22.7573 | 22.3665 | 21.69 | 22.6899 | 21.7443 | 22.3398 | 22.3384 | 22.3097 | 21.9657 | 21.1786 | 22.1513 | 21.5985 | 21.7654 | 21.9147 | 21.0773 | 21.2178 | 21.9445 | 20.4894 | 21.5913 | 27.3739 | 21.9419 | 22.5734 | 32.1097 | 243.9905 | 210.2818 | 283.622 | 22.1312 | 22.358 | 29.2772 | 22.0609 | 22.5664 | 32.0517 | 111.0092 | 378.3424 |  | 166.9378 | 222.326 | 210.6553 | 231.421 |  | 18.6323 | 20.9208 | 19.1705 | 21.1937 | 23.886 | 54.1464 | 183.3604 | 16.0529 | 17.6871 | 15.9728 | 20.1114 | 19.1125 | 45.9002 | 49.0586 | 45.1046 | 21.693 |  |  | 0.65603 | -0.41208 | -34.1386 | 0.49542 | 0.52911 | -161.6613 | 12.3849 | 1.5918 | 0.11082 | 0.38971 | 1.7901 | 1.4492 | 1.4876 | 0.17775 | 22.0265 | 21.9652 | 22.1594 | 22.2035 | 22.0172 | 21.3011 | 20.1125 | 22.1738 | 22.3602 | 22.3941 | 22.3402 | 21.955 | 21.1782 | 22.2673 | 140.3539 | 89.0497 | 92.5784 | 54.9918 | 46.5285 | 74.3272 | 47.6372 | 22.3161 | 22.0847 | 21.667 | 22.054 | 21.7941 | 21.8018 | 21.9449 | 21.9609 | 27.583 | 91.8724 | 222.5585 | 182.9846 | 143.5423 | 3.0668 | 2.5651 | 106.3453 | 21.8952 | 22.2058 | 21.7131 | 21.556 | 22.0142 | 22.0694 | 23.2764 | 38.3864 | 21.8495 | 22.1528 | 28.9931 | 254.4218 | 471.1043 | 186.3629 | 189.2136 | 163.9209 |  | 94.1125 | 168.9114 | 97.6875 | 183.4488 | 140.7928 | 109.9734 |  | 122.4741 |  |  | 30.7134 | 45.1526 | 96.3705 | [5 empty] | 21.8758 | 138.3622 | 21.693 | 22.0994 | 54.2308 | 21.2857 | 21.9011 | 47.7886 | 173.5545 | 379.447 |  | 141.4042 | 250.5843 | 30.8043 | 130.3864 | 320.1182 | 101.0756 | 207.8806 | 36.7625 | 174.2534 | 38.4031 | 180.5624 | 20.2229 | 139.3839 | 230.2755 | 51.3686 | 133.5624 | 263.7078 | 31.0711 | 133.4608 | 265.4806 | 30.8423 | 166.0469 | 56.1486 | 177.8155 | 39.4019 | 202.6648 | 5.0978 | 18.3236 | 2.3808 | 0.065314 | -27.2541 | 3.0948 | 520.61 | 51.28 | 1.3319 | -0.76715 | -6.9826 | 0.84116 | 0.91709 | -16.0303 | 4.4369 | -0.90757 | -0.90614 | 0.47984 | -6.5097 | -4.3931 | -2.1099 | -0.42866
42838.427 | 578 | 22.885 | 22.8515 | 22.8358 | 22.7534 | 22.3568 | 21.6832 | 22.6862 | 21.7406 | 22.3418 | 22.3412 | 22.3119 | 21.961 | 21.175 | 22.1459 | 21.6007 | 21.7688 | 21.913 | 21.0806 | 21.2293 | 21.9577 | 20.4889 | 21.6069 | 27.4018 | 21.9538 | 22.5822 | 32.1625 | 247.2049 | 212.585 | 290.0254 | 22.1193 | 22.3609 | 29.3026 | 22.0564 | 22.5642 | 32.0888 | 111.9987 | 398.5728 |  | 169.1836 | 225.4165 | 214.1299 | 237.3438 |  | 18.6722 | 21.0198 | 19.2501 | 21.3153 | 24.0013 | 54.9947 | 185.185 | 16.0405 | 17.6956 | 15.995 | 20.1554 | 19.1294 | 45.9048 | 49.0646 | 45.1182 | 21.7016 |  |  | 0.88734 | -0.40748 | -34.0072 | 0.30946 | 1.0081 | -159.8562 | 12.9422 | 1.4598 | 0.17231 | 0.54601 | 1.7021 | 1.2625 | 1.2959 | 0.24507 | 22.0209 | 21.9584 | 22.1534 | 22.2013 | 22.0097 | 21.2994 | 20.114 | 22.1748 | 22.3566 | 22.3849 | 22.3365 | 21.9502 | 21.1829 | 22.2734 | 141.2097 | 86.2135 | 93.7629 | 56.5668 | 47.2853 | 74.7267 | 47.9434 | 22.315 | 22.0684 | 21.6595 | 22.0413 | 21.7943 | 21.7994 | 21.9431 | 21.9541 | 27.6171 | 92.5285 | 225.6008 | 184.8325 | 145.4858 | 4.4123 | 2.4104 | 107.5225 | 21.8935 | 22.2016 | 21.7683 | 21.5453 | 22.0093 | 22.0658 | 23.2744 | 38.455 | 21.8449 | 22.1476 | 29.0188 | 257.3511 | 492.8451 | 188.2193 | 190.8196 | 165.5284 |  | 94.8254 | 169.7917 | 98.1899 | 187.2372 | 141.8411 | 111.2532 |  | 123.4131 |  |  | 31.0635 | 46.4069 | 97.6773 | [5 empty] | 21.882 | 141.9102 | 21.6987 | 22.0907 | 55.0766 | 21.2897 | 21.9103 | 48.2404 | 175.6698 | 384.7807 |  | 143.1803 | 255.7427 | 31.0941 | 131.626 | 327.8926 | 102.7044 | 209.9115 | 37.2057 | 175.4665 | 38.9628 | 182.0973 | 20.2508 | 140.2578 | 234.4269 | 51.8855 | 135.0173 | 268.5473 | 31.4153 | 134.4708 | 270.001 | 31.1416 | 167.903 | 56.8318 | 180.3696 | 39.9118 | 205.7276 | 5.4343 | 18.3149 | 2.3892 | 0.06498 | -27.1675 | 3.0948 | 513.53 | 52.21 | 1.5579 | -0.76299 | -6.9703 | 0.66492 | 1.2675 | -15.9612 | 4.5415 | -0.92439 | -0.91081 | 0.42066 | -6.5566 | -4.4883 | -2.2341 | -0.45717
42838.427 | 579 | 22.8847 | 22.8521 | 22.8355 | 22.7519 | 22.3564 | 21.6878 | 22.6813 | 21.7392 | 22.333 | 22.3484 | 22.3157 | 21.9626 | 21.1743 | 22.1505 | 21.5848 | 21.7672 | 21.9111 | 21.0697 | 21.2203 | 21.9483 | 20.4801 | 21.6093 | 27.4236 | 21.9536 | 22.5765 | 32.2037 | 251.0935 | 215.4888 | 295.8256 | 22.1194 | 22.3597 | 29.3343 | 22.0531 | 22.56 | 32.129 | 113.0154 | 415.5262 |  | 171.4875 | 228.4961 | 217.4431 | 243.0449 |  | 18.7181 | 21.1372 | 19.3566 | 21.4597 | 24.2116 | 54.9747 | 186.3024 | 15.997 | 17.7009 | 15.9618 | 20.195 | 19.1244 | 45.9087 | 49.0652 | 45.121 | 21.7012 |  |  | 0.67377 | -0.1328 | -34.2484 | 0.45665 | 0.57708 | -158.9835 | 12.1536 | 1.6247 | 0.32858 | 0.2418 | 1.9307 | 1.1019 | 1.1315 | 0.32285 | 22.0328 | 21.9641 | 22.1526 | 22.1994 | 22.0203 | 21.2982 | 20.1191 | 22.1728 | 22.3548 | 22.3933 | 22.3376 | 21.95 | 21.1769 | 22.265 | 141.5458 | 86.3427 | 88.8234 | 57.1861 | 47.2892 | 75.158 | 48.165 | 22.3168 | 22.074 | 21.6558 | 22.0404 | 21.7945 | 21.7994 | 21.9384 | 21.9526 | 27.6444 | 93.2032 | 227.3126 | 186.3954 | 148.1781 | 4.6441 | 3.2802 | 108.5861 | 21.8915 | 22.2076 | 21.8298 | 21.5487 | 22.0197 | 22.069 | 23.2867 | 38.5289 | 21.8445 | 22.1563 | 29.0596 | 259.6371 | 514.132 | 190.3988 | 192.896 | 168.2174 |  | 95.5696 | 172.808 | 98.7469 | 191.6845 | 143.0159 | 114.1884 |  | 124.5239 |  |  | 31.4544 | 47.7441 | 99.4243 | [5 empty] | 21.8867 | 145.5933 | 21.7035 | 22.0917 | 55.9682 | 21.2894 | 21.9067 | 48.716 | 177.7774 | 391.1104 |  | 145.2107 | 261.0896 | 31.3872 | 132.8037 | 339.1019 | 104.389 | 212.9544 | 37.6275 | 177.0209 | 39.5408 | 183.767 | 20.2675 | 141.502 | 238.671 | 52.4133 | 136.4146 | 273.1517 | 31.8127 | 135.4192 | 274.2792 | 31.4162 | 169.7496 | 57.6513 | 182.2701 | 40.3644 | 208.5198 | 5.4116 | 18.3078 | 2.3971 | 0.064203 | -27.27 | 3.0948 | 535.65 | 51.87 | 1.3645 | -0.43567 | -6.9964 | 0.80788 | 0.95897 | -15.917 | 4.4009 | -0.96998 | -0.97264 | 0.34888 | -6.5419 | -3.9132 | -2.351 | -0.50571
42838.427 | 580 | 22.8866 | 22.8534 | 22.8447 | 22.7596 | 22.3702 | 21.6836 | 22.6922 | 21.7574 | 22.3386 | 22.3485 | 22.3146 | 21.9675 | 21.1865 | 22.1512 | 21.5926 | 21.7706 | 21.9138 | 21.0652 | 21.2197 | 21.9501 | 20.4877 | 21.6146 | 27.465 | 21.963 | 22.5893 | 32.2503 | 254.2276 | 218.4255 | 300.4993 | 22.1278 | 22.3706 | 29.3757 | 22.0526 | 22.5743 | 32.1726 | 114.0427 | 425.3068 |  | 173.731 | 231.1202 | 220.3576 | 248.1801 |  | 18.7626 | 21.2509 | 19.4432 | 21.6045 | 24.4669 | 54.7439 | 187.8885 | 15.9343 | 17.7113 | 15.9473 | 20.2339 | 19.1296 | 45.9283 | 49.0548 | 45.1214 | 21.6973 |  |  | 0.72306 | -0.17486 | -34.6715 | 0.25623 | 0.76107 | -162.4794 | 11.5596 | 1.5708 | 0.23186 | 0.3788 | 1.8771 | 0.96415 | 0.98995 | 0.30703 | 22.0295 | 21.9581 | 22.1517 | 22.1902 | 22.0044 | 21.2907 | 20.1118 | 22.1711 | 22.3546 | 22.3882 | 22.3434 | 21.9542 | 21.1723 | 22.2603 | 143.1394 | 86.2284 | 89.1099 | 57.7978 | 48.133 | 75.6374 | 48.4497 | 22.3073 | 22.0684 | 21.654 | 22.0379 | 21.7849 | 21.8032 | 21.9364 | 21.9515 | 27.675 | 93.8858 | 228.7675 | 187.9177 | 150.8505 | 4.9066 | 1.5775 | 109.9286 | 21.8967 | 22.2053 | 21.8957 | 21.5519 | 22.0113 | 22.067 | 23.297 | 38.6031 | 21.8439 | 22.1585 | 29.0948 | 262.9209 | 533.2412 | 193.0299 | 195.3298 | 170.3445 |  | 96.4417 | 174.4357 | 99.3415 | 197.0625 | 144.4395 | 118.2101 |  | 125.626 |  |  | 31.8743 | 50.0215 | 100.6467 | [5 empty] | 21.8827 | 149.7505 | 21.6995 | 22.0842 | 56.8146 | 21.2846 | 21.9059 | 49.202 | 180.0514 | 396.7551 |  | 147.091 | 264.5772 | 31.7025 | 133.9658 | 347.0514 | 106.0149 | 215.8565 | 38.0445 | 178.3727 | 40.1818 | 185.4288 | 20.3071 | 143.1505 | 242.822 | 52.9388 | 137.6099 | 277.5855 | 32.1866 | 136.266 | 278.0715 | 31.6854 | 171.8422 | 58.4731 | 184.5555 | 40.8209 | 211.1449 | 6.254 | 18.3016 | 2.4066 | 0.065038 | -27.2758 | 3.0948 | 565.48 | 51.74 | 1.4193 | -0.50001 | -7.0408 | 0.60527 | 1.1009 | -16.0854 | 4.2905 | -0.99489 | -0.99439 | 0.26242 | -6.6611 | -3.9113 | -2.4517 | -0.55335
42838.427 | 581 | 22.8844 | 22.8551 | 22.8368 | 22.759 | 22.3614 | 21.6928 | 22.6915 | 21.7421 | 22.3431 | 22.3438 | 22.3167 | 21.9649 | 21.1819 | 22.1473 | 21.5929 | 21.7667 | 21.913 | 21.0695 | 21.2159 | 21.9573 | 20.4795 | 21.6154 | 27.4977 | 21.9538 | 22.5971 | 32.2939 | 257.3129 | 221.0342 | 306.9485 | 22.1271 | 22.3756 | 29.3995 | 22.0565 | 22.5867 | 32.2218 | 115.1718 | 436.8936 |  | 176.1469 | 234.0084 | 223.2214 | 253.3005 |  | 18.8386 | 21.3722 | 19.5464 | 21.7629 | 24.6992 | 55.2013 | 188.6909 | 15.9063 | 17.7215 | 15.9544 | 20.2807 | 19.1377 | 45.9569 | 49.0514 | 45.1255 | 21.6991 |  |  | 0.98131 | -0.083521 | -35.033 | 0.17146 | 0.98712 | -161.7815 | 11.8737 | 1.7154 | 0.11257 | 0.47887 | 1.8587 | 0.8455 | 0.86828 | 0.30732 | 22.0298 | 21.9577 | 22.1504 | 22.2035 | 22.0095 | 21.2939 | 20.1122 | 22.1727 | 22.3511 | 22.3877 | 22.3415 | 21.9521 | 21.1743 | 22.2634 | 144.7522 | 84.4971 | 87.8501 | 57.2514 | 48.5315 | 76.0946 | 48.6903 | 22.3146 | 22.0765 | 21.6636 | 22.0489 | 21.7902 | 21.8086 | 21.9404 | 21.9621 | 27.7152 | 94.5918 | 230.8726 | 189.6471 | 153.5262 | 4.2957 | 2.7187 | 110.3186 | 21.9001 | 22.2107 | 21.9785 | 21.5563 | 22.0172 | 22.069 | 23.3135 | 38.6967 | 21.8543 | 22.1648 | 29.1359 | 267.0482 | 549.5691 | 195.4195 | 197.5447 | 171.8895 |  | 97.2259 | 174.8713 | 99.8609 | 200.1316 | 145.6177 | 118.3032 |  | 126.6248 |  |  | 32.3189 | 51.6577 | 102.0888 | [5 empty] | 21.8802 | 153.0961 | 21.7003 | 22.084 | 57.7544 | 21.2868 | 21.9007 | 49.6715 | 182.4087 | 402.0607 |  | 148.9043 | 269.1094 | 32.0442 | 135.163 | 353.7984 | 107.6522 | 218.7556 | 38.4708 | 179.717 | 40.8443 | 187.2574 | 20.3554 | 144.5428 | 247.1445 | 53.5037 | 138.9965 | 281.5302 | 32.5897 | 137.2998 | 281.5857 | 31.9783 | 173.8049 | 59.3184 | 188.1427 | 41.3841 | 213.7422 | 6.5562 | 18.2953 | 2.4158 | 0.065989 | -27.1964 | 3.0948 | 587.46 | 52.57 | 1.6627 | -0.34564 | -7.0789 | 0.49523 | 1.2546 | -16.062 | 4.3514 | -1.007 | -0.98596 | 0.22944 | -6.7851 | -3.7428 | -2.5476 | -0.60012
42838.427 | 582 | 22.8894 | 22.8576 | 22.8419 | 22.7579 | 22.3737 | 21.6896 | 22.6987 | 21.7415 | 22.3504 | 22.3462 | 22.3221 | 21.9666 | 21.1816 | 22.159 | 21.5876 | 21.7599 | 21.9116 | 21.0655 | 21.214 | 21.9557 | 20.4721 | 21.616 | 27.5225 | 21.9486 | 22.5962 | 32.3369 | 260.7627 | 223.9522 | 310.1397 | 22.1371 | 22.3918 | 29.4537 | 22.0739 | 22.5973 | 32.2746 | 116.461 | 455.0181 |  | 178.8471 | 236.9911 | 226.2733 | 257.1805 |  | 18.9228 | 21.5268 | 19.6349 | 21.9255 | 24.8503 | 55.9697 | 191.4031 | 15.8938 | 17.7357 | 15.984 | 20.3248 | 19.1472 | 45.987 | 49.0537 | 45.1288 | 21.7015 |  |  | 0.89391 | -0.234 | -35.4555 | 0.12284 | 0.96609 | -159.5105 | 12.2476 | 1.325 | 0.26319 | 0.59028 | 1.9444 | 0.7431 | 0.7632 | 0.30577 | 22.0398 | 21.9567 | 22.1497 | 22.2057 | 22.009 | 21.2958 | 20.113 | 22.1731 | 22.3548 | 22.3909 | 22.3334 | 21.9514 | 21.1739 | 22.2676 | 147.0437 | 85.7351 | 91.2376 | 57.6427 | 49.3122 | 76.5904 | 48.9752 | 22.3122 | 22.08 | 21.6647 | 22.0421 | 21.7845 | 21.8062 | 21.9409 | 21.9595 | 27.7433 | 95.314 | 233.2025 | 191.4784 | 156.1238 | 3.8131 | 2.5651 | 111.3827 | 21.8949 | 22.213 | 22.0583 | 21.5556 | 22.0205 | 22.0751 | 23.3232 | 38.7846 | 21.8555 | 22.1809 | 29.1722 | 271.9655 | 565.5542 | 197.4156 | 199.5777 | 176.5843 |  | 98.1148 | 176.415 | 100.3897 | 203.1605 | 146.7957 | 118.7539 |  | 127.7096 |  |  | 32.7402 | 52.5948 | 104.1368 | [5 empty] | 21.8878 | 156.3522 | 21.7015 | 22.0864 | 58.7982 | 21.289 | 21.9052 | 50.1795 | 184.7466 | 406.9148 |  | 150.8306 | 273.0211 | 32.4128 | 136.5087 | 360.6657 | 109.3333 | 222.7657 | 38.9057 | 181.042 | 41.4397 | 189.6258 | 20.3881 | 145.7528 | 250.955 | 54.1056 | 140.5116 | 285.8053 | 33.013 | 138.4413 | 284.6036 | 32.3116 | 176.0416 | 60.0955 | 192.1609 | 41.9649 | 216.7874 | 5.7083 | 18.2872 | 2.4252 | 0.064196 | -27.1945 | 3.0948 | 614.17 | 51.01 | 1.5913 | -0.57869 | -7.1233 | 0.41928 | 1.2427 | -15.9676 | 4.4246 | -1.1025 | -1.0079 | 0.19773 | -6.9798 | -4.0853 | -2.6024 | -0.64405
42838.427 | 583 | 22.8863 | 22.8515 | 22.8372 | 22.7472 | 22.3545 | 21.6871 | 22.6821 | 21.7406 | 22.3449 | 22.3398 | 22.3108 | 21.9634 | 21.1803 | 22.1515 | 21.5889 | 21.7614 | 21.9089 | 21.0717 | 21.2186 | 21.9619 | 20.48 | 21.6326 | 27.5538 | 21.9554 | 22.6051 | 32.3911 | 264.3891 | 227.1431 | 313.5394 | 22.1208 | 22.3894 | 29.4772 | 22.0663 | 22.5918 | 32.303 | 117.6065 | 453.2972 |  | 180.9484 | 239.8868 | 229.2325 | 257.8178 |  | 18.9778 | 21.6499 | 19.7069 | 22.0547 | 24.9974 | 56.9245 | 192.5448 | 15.8849 | 17.7444 | 16.0719 | 20.3584 | 19.1437 | 46.0073 | 49.0455 | 45.1257 | 21.6994 |  |  | 1.0214 | -0.083521 | -35.5265 | 0.38897 | 0.97858 | -162.7074 | 11.5254 | 1.7627 | 0.0043746 | 0.34209 | 2.1326 | 0.655 | 0.67259 | 0.34058 | 22.0366 | 21.9637 | 22.1548 | 22.2052 | 22.0124 | 21.2957 | 20.1127 | 22.1734 | 22.3542 | 22.3955 | 22.3386 | 21.9468 | 21.1773 | 22.2733 | 149.6242 | 88.899 | 97.2873 | 58.7171 | 49.9069 | 77.137 | 49.2865 | 22.3259 | 22.0849 | 21.6615 | 22.0545 | 21.8015 | 21.8271 | 21.943 | 21.9718 | 27.7878 | 96.1722 | 236.7559 | 193.7476 | 159.5256 | 6.1229 | 3.8586 | 112.8435 | 21.8982 | 22.2135 | 22.139 | 21.5585 | 22.021 | 22.0753 | 23.3271 | 38.8738 | 21.8498 | 22.1858 | 29.2083 | 275.1346 | 582.1792 | 199.6491 | 201.6911 | 181.2203 |  | 99.0986 | 177.8131 | 101.0397 | 207.6419 | 148.2749 | 119.2379 |  | 128.9354 |  |  | 33.1793 | 53.3571 | 105.6999 | [5 empty] | 21.8947 | 159.6931 | 21.7017 | 22.0941 | 59.738 | 21.2925 | 21.9073 | 50.6802 | 187.1225 | 411.2132 |  | 153.1618 | 277.1913 | 32.7909 | 137.7951 | 368.5874 | 110.9617 | 226.3715 | 39.3752 | 182.7563 | 42.0811 | 191.5145 | 20.4612 | 147.0792 | 254.414 | 54.6903 | 142.1161 | 290.0548 | 33.4579 | 139.6974 | 289.568 | 32.6292 | 178.6715 | 60.8675 | 194.4023 | 42.656 | 220.2287 | 6.4822 | 18.2792 | 2.4363 | 0.063049 | -27.2118 | 3.0948 | 643.17 | 52.61 | 1.706 | -0.3458 | -7.1319 | 0.74626 | 1.2525 | -16.1502 | 4.2983 | -1.1924 | -1.021 | 0.13931 | -7.2005 | -4.7206 | -2.5728 | -0.70493
42838.427 | 584 | 22.8836 | 22.8552 | 22.8417 | 22.7577 | 22.3616 | 21.6895 | 22.6885 | 21.7462 | 22.3436 | 22.3477 | 22.3172 | 21.9691 | 21.1845 | 22.1516 | 21.5911 | 21.7696 | 21.9134 | 21.08 | 21.2249 | 21.9697 | 20.4827 | 21.6465 | 27.5894 | 21.9622 | 22.6217 | 32.4432 | 268.5458 | 230.4634 | 321.957 | 22.1343 | 22.3894 | 29.5183 | 22.0636 | 22.6004 | 32.3555 | 118.7622 | 463.4883 |  | 183.2947 | 243.172 | 232.5419 | 259.4839 |  | 19.0332 | 21.7762 | 19.7982 | 22.2085 | 25.162 | 58.3707 | 195.7872 | 15.791 | 17.7535 | 16.1022 | 20.403 | 19.1518 | 46.0218 | 49.061 | 45.141 | 21.7072 |  |  | 0.66786 | -0.072349 | -35.7604 | 0.38897 | 1.0154 | -162.6969 | 11.5616 | 1.785 | 0.030646 | 0.1797 | 2.072 | 0.57827 | 0.59403 | 0.39897 | 22.0354 | 21.9645 | 22.1517 | 22.2008 | 22.0134 | 21.2936 | 20.1094 | 22.1739 | 22.353 | 22.3937 | 22.339 | 21.95 | 21.1744 | 22.2652 | 153.586 | 93.5517 | 106.1844 | 61.9124 | 52.075 | 77.7793 | 49.677 | 22.3207 | 22.0823 | 21.6654 | 22.0498 | 21.7979 | 21.8294 | 21.9514 | 21.9706 | 27.8206 | 96.9587 | 239.2756 | 195.8024 | 162.1199 | 4.8035 | 3.7319 | 114.4877 | 21.9032 | 22.211 | 22.2384 | 21.5616 | 22.0209 | 22.0794 | 23.3471 | 38.9694 | 21.8531 | 22.1914 | 29.2486 | 277.9904 | 597.0096 | 202.0962 | 204.03 | 186.0562 |  | 99.9725 | 179.8093 | 101.6327 | 211.121 | 149.5679 | 121.4404 |  | 130.0174 |  |  | 33.6352 | 54.4037 | 106.9889 | [5 empty] | 21.8852 | 162.5089 | 21.6995 | 22.0921 | 60.6261 | 21.2828 | 21.9032 | 51.2295 | 189.485 | 415.6762 |  | 155.4928 | 281.4934 | 33.1953 | 139.3415 | 377.9132 | 112.6631 | 230.2177 | 39.8506 | 184.6127 | 42.7815 | 193.6065 | 20.5383 | 148.481 | 257.6238 | 55.2678 | 143.7003 | 294.776 | 33.9301 | 140.9923 | 295.0027 | 32.9267 | 181.1485 | 61.7192 | 196.1685 | 43.3153 | 223.7625 | 5.1651 | 18.2711 | 2.4468 | 0.06318 | -27.3118 | 3.0948 | 664.95 | 52.04 | 1.3893 | -0.32191 | -7.1569 | 0.74642 | 1.2786 | -16.185 | 4.3145 | -1.2922 | -1.0529 | 0.10064 | -7.563 | -5.6628 | -2.5713 | -0.74613
42838.427 | 585 | 22.8836 | 22.8562 | 22.8412 | 22.7543 | 22.366 | 21.6893 | 22.6943 | 21.7479 | 22.3438 | 22.3507 | 22.3197 | 21.9684 | 21.1831 | 22.1541 | 21.5818 | 21.7649 | 21.9126 | 21.07 | 21.2184 | 21.9714 | 20.4808 | 21.6485 | 27.6144 | 21.9541 | 22.6168 | 32.4809 | 272.5476 | 233.5836 | 328.4747 | 22.1401 | 22.3975 | 29.5577 | 22.0616 | 22.6085 | 32.3977 | 119.9312 | 466.8232 |  | 185.8242 | 247.3721 | 235.964 | 262.7735 |  | 19.104 | 21.9181 | 19.9026 | 22.36 | 25.3344 | 60.8433 | 199.3729 | 15.7655 | 17.7619 | 16.1188 | 20.4519 | 19.1644 | 46.0503 | 49.0623 | 45.1459 | 21.7083 |  |  | 0.66195 | -0.053293 | -35.7348 | 0.40605 | 1.0081 | -159.0472 | 12.0472 | 1.7095 | 0.28499 | 0.50027 | 2.2288 | 0.51194 | 0.52603 | 0.41956 | 22.043 | 21.967 | 22.1494 | 22.2094 | 22.0097 | 21.304 | 20.1104 | 22.1745 | 22.3553 | 22.3861 | 22.343 | 21.9553 | 21.1699 | 22.2586 | 154.7899 | 95.403 | 111.268 | 63.5987 | 53.6493 | 78.3668 | 50.0898 | 22.3198 | 22.0799 | 21.6704 | 22.045 | 21.7909 | 21.8278 | 21.9447 | 21.9689 | 27.8549 | 97.7603 | 242.2802 | 198.2214 | 164.12 | 4.9473 | 4.2871 | 115.9895 | 21.8971 | 22.2073 | 22.321 | 21.559 | 22.0114 | 22.0768 | 23.3498 | 39.055 | 21.8565 | 22.1901 | 29.2853 | 281.6602 | 607.9823 | 204.6067 | 206.3426 | 189.237 |  | 100.9119 | 183.9326 | 102.2513 | 215.1436 | 150.8686 | 122.9459 |  | 131.0335 |  |  | 34.1287 | 55.1909 | 108.6465 | [5 empty] | 21.8804 | 165.3845 | 21.6986 | 22.0874 | 61.5038 | 21.2859 | 21.9054 | 51.7936 | 192.0566 | 421.7174 |  | 157.2417 | 285.0851 | 33.6068 | 140.9211 | 387.118 | 114.456 | 234.2909 | 40.3383 | 186.4442 | 43.5041 | 195.5124 | 20.6083 | 150.0267 | 260.7958 | 55.8713 | 145.1829 | 300.2772 | 34.4122 | 142.5476 | 298.1259 | 33.2369 | 183.9456 | 62.5725 | 198.1931 | 43.9177 | 227.3634 | 5.3957 | 18.2591 | 2.4588 | 0.062251 | -27.1851 | 3.0948 | 692.01 | 52.21 | 1.3907 | -0.27635 | -7.1561 | 0.76282 | 1.2788 | -16.062 | 4.4206 | -1.3434 | -1.1429 | 0.047418 | -7.6257 | -6.1786 | -2.6142 | -0.77018
42838.4271 | 586 | 22.8891 | 22.8512 | 22.8466 | 22.7512 | 22.3646 | 21.6912 | 22.6997 | 21.7494 | 22.3427 | 22.3518 | 22.3221 | 21.9665 | 21.1821 | 22.1573 | 21.5884 | 21.7631 | 21.9105 | 21.0733 | 21.2209 | 21.9727 | 20.4849 | 21.6591 | 27.652 | 21.952 | 22.6253 | 32.5383 | 276.495 | 236.707 | 335.1635 | 22.134 | 22.3999 | 29.5935 | 22.0601 | 22.6096 | 32.4337 | 121.1458 | 469.4797 |  | 188.3848 | 250.8844 | 239.3006 | 268.6104 |  | 19.1656 | 22.0617 | 20.0066 | 22.5089 | 25.496 | 64.3128 | 202.4929 | 15.7793 | 17.7794 | 16.1599 | 20.4941 | 19.1628 | 46.0482 | 49.0518 | 45.1406 | 21.7017 |  |  | 0.57192 | -0.081549 | -36.152 | 0.35085 | 0.88198 | -160.1538 | 11.3795 | 1.7035 | 0.17621 | 0.54937 | 2.3619 | 0.45417 | 0.46691 | 0.42747 | 22.0353 | 21.962 | 22.1447 | 22.1937 | 22.0044 | 21.3 | 20.1121 | 22.1693 | 22.3454 | 22.3866 | 22.3334 | 21.9495 | 21.1683 | 22.2521 | 156.1134 | 98.0261 | 110.0235 | 63.8599 | 53.0526 | 78.8935 | 50.4742 | 22.3151 | 22.0823 | 21.6767 | 22.0516 | 21.7945 | 21.8384 | 21.9467 | 21.9722 | 27.8889 | 98.5819 | 245.6991 | 200.703 | 165.8325 | 5.6171 | 3.4225 | 117.6175 | 21.8921 | 22.2019 | 22.3983 | 21.5567 | 22.0094 | 22.0695 | 23.3549 | 39.1574 | 21.8465 | 22.1826 | 29.32 | 285.4687 | 618.2957 | 207.064 | 208.6638 | 192.0866 |  | 101.927 | 185.6917 | 102.9237 | 220.6609 | 152.4593 | 124.921 |  | 132.2942 |  |  | 34.6163 | 56.3193 | 111.0963 | [5 empty] | 21.8871 | 169.1261 | 21.7058 | 22.093 | 62.4297 | 21.2889 | 21.9079 | 52.3467 | 194.8022 | 426.5732 |  | 158.8401 | 289.7417 | 34.0177 | 142.2878 | 395.0508 | 116.3074 | 238.4406 | 40.861 | 188.2076 | 44.4195 | 197.3232 | 20.6806 | 151.526 | 264.8921 | 56.5308 | 146.7853 | 306.3691 | 34.9022 | 143.9879 | 301.4492 | 33.5255 | 186.2907 | 63.422 | 200.223 | 44.5705 | 230.7287 | 7.1509 | 18.2492 | 2.4701 | 0.062091 | -27.2268 | 3.0948 | 713.43 | 55.71 | 1.2999 | -0.34193 | -7.1995 | 0.70925 | 1.2023 | -16.2013 | 4.3186 | -1.3822 | -1.165 | -0.033996 | -7.7091 | -5.9947 | -2.7258 | -0.78539
42838.4271 | 587 | 22.8947 | 22.8571 | 22.8437 | 22.76 | 22.3651 | 21.6902 | 22.7032 | 21.7548 | 22.3541 | 22.3591 | 22.3232 | 21.9719 | 21.1839 | 22.1531 | 21.5921 | 21.7669 | 21.919 | 21.077 | 21.2259 | 21.9814 | 20.4875 | 21.6662 | 27.695 | 21.9577 | 22.6372 | 32.589 | 281.3468 | 239.7175 | 343.7921 | 22.1243 | 22.3986 | 29.6213 | 22.053 | 22.6095 | 32.4773 | 122.3567 | 474.4514 |  | 190.9409 | 254.1758 | 242.3055 | 273.2376 |  | 19.2417 | 22.2174 | 20.1384 | 22.6969 | 25.7327 | 67.13 | 205.8259 | 15.8144 | 17.7937 | 16.1796 | 20.5419 | 19.1705 | 46.0613 | 49.0543 | 45.1402 | 21.7061 |  |  | 0.59098 | -0.24057 | -36.2223 | 0.41525 | 1.0068 | -161.8236 | 11.0845 | 1.8777 | 0.010796 | 0.32887 | 2.5197 | 0.4041 | 0.41533 | 0.42202 | 22.0447 | 21.9574 | 22.1488 | 22.205 | 22.0077 | 21.2979 | 20.1118 | 22.1733 | 22.3526 | 22.3918 | 22.3318 | 21.9473 | 21.1729 | 22.262 | 157.7552 | 95.9184 | 110.3069 | 63.5297 | 54.2366 | 79.429 | 50.871 | 22.3118 | 22.083 | 21.6662 | 22.041 | 21.7871 | 21.8377 | 21.9471 | 21.9757 | 27.9183 | 99.4301 | 248.4475 | 203.2696 | 167.0977 | 4.1473 | 3.215 | 118.8072 | 21.895 | 22.2045 | 22.4748 | 21.5551 | 22.0121 | 22.0728 | 23.3624 | 39.2614 | 21.8462 | 22.1954 | 29.3554 | 289.4146 | 630.9536 | 209.543 | 211.0519 | 195.4261 |  | 102.8513 | 185.7818 | 103.6246 | 223.6762 | 154.0216 | 126.768 |  | 133.6313 |  |  | 35.1018 | 56.8586 | 113.6069 | [5 empty] | 21.8897 | 172.6075 | 21.7038 | 22.0965 | 63.2648 | 21.2908 | 21.9063 | 52.8381 | 197.6013 | 432.0225 |  | 160.6484 | 293.1517 | 34.4445 | 143.7116 | 402.1612 | 118.091 | 242.3773 | 41.3606 | 190.0096 | 45.2584 | 199.7875 | 20.7434 | 152.8603 | 269.1446 | 57.1929 | 148.6123 | 311.0203 | 35.3923 | 145.09 | 306.3932 | 33.8583 | 188.5402 | 64.3055 | 202.7557 | 45.2994 | 233.2852 | 7.4047 | 18.2378 | 2.4806 | 0.062897 | -27.2625 | 3.0948 | 751.68 | 54.87 | 1.3307 | -0.58745 | -7.2084 | 0.7718 | 1.2899 | -16.3533 | 4.28 | -1.4382 | -1.1395 | -0.046893 | -7.8267 | -5.979 | -2.8037 | -0.78705
42838.4271 | 588 | 22.8949 | 22.8496 | 22.8356 | 22.7491 | 22.3652 | 21.6829 | 22.6903 | 21.7427 | 22.3451 | 22.3453 | 22.3188 | 21.9635 | 21.1748 | 22.1507 | 21.5859 | 21.7645 | 21.9147 | 21.073 | 21.2221 | 21.9877 | 20.4834 | 21.6647 | 27.7187 | 21.9622 | 22.6426 | 32.6365 | 285.5832 | 242.9284 | 347.1752 | 22.1321 | 22.4101 | 29.6632 | 22.0622 | 22.619 | 32.5339 | 123.6422 | 482.5968 |  | 193.5593 | 258.8488 | 245.7145 | 277.2529 |  | 19.3121 | 22.3606 | 20.2466 | 22.8634 | 25.9762 | 67.0757 | 207.7587 | 15.8156 | 17.799 | 16.0902 | 20.5899 | 19.1838 | 46.0771 | 49.0515 | 45.15 | 21.7094 |  |  | 1.0523 | -0.084833 | -36.3833 | 0.27857 | 1.0325 | -162.5181 | 11.1042 | 1.7344 | 0.30056 | 0.4623 | 2.3208 | 0.36025 | 0.3705 | 0.45279 | 22.0488 | 21.9602 | 22.147 | 22.2006 | 22.0119 | 21.2985 | 20.1073 | 22.1717 | 22.3477 | 22.3894 | 22.3301 | 21.9475 | 21.169 | 22.265 | 156.0892 | 95.6694 | 111.0354 | 65.7484 | 55.7611 | 79.947 | 51.2888 | 22.3197 | 22.0731 | 21.6642 | 22.0461 | 21.7967 | 21.8333 | 21.9392 | 21.984 | 27.9607 | 100.4038 | 251.9779 | 206.1367 | 169.0645 | 4.1901 | 3.9419 | 119.603 | 21.895 | 22.2065 | 22.5585 | 21.5564 | 22.0107 | 22.07 | 23.3754 | 39.3646 | 21.8547 | 22.2042 | 29.3934 | 294.2214 | 640.6315 | 212.1606 | 213.5924 | 198.6598 |  | 103.819 | 189.2542 | 104.3378 | 225.3555 | 155.4248 | 126.8293 |  | 134.682 |  |  | 35.6412 | 57.803 | 116.0445 | [5 empty] | 21.8858 | 175.9991 | 21.6991 | 22.0938 | 64.1569 | 21.2857 | 21.9045 | 53.3389 | 200.2904 | 438.577 |  | 162.3971 | 296.0819 | 34.9124 | 145.4148 | 408.95 | 119.897 | 245.6065 | 41.8908 | 192.1678 | 46.0787 | 202.4716 | 20.7964 | 154.5662 | 273.0018 | 57.8206 | 150.1546 | 314.1848 | 35.9038 | 146.5708 | 310.8972 | 34.2697 | 190.8718 | 65.232 | 205.4592 | 46.0994 | 235.8666 | 5.8594 | 18.2238 | 2.4921 | 0.062889 | -27.2079 | 3.0947 | 759.68 | 56.4 | 1.7805 | -0.34893 | -7.2261 | 0.6323 | 1.3061 | -16.3871 | 4.2835 | -1.4895 | -1.2075 | -0.029629 | -7.5789 | -6.0103 | -2.8614 | -0.80317
42838.4271 | 589 | 22.8759 | 22.8378 | 22.8304 | 22.7457 | 22.3584 | 21.6722 | 22.6815 | 21.7406 | 22.3255 | 22.3349 | 22.3038 | 21.9564 | 21.1681 | 22.1427 | 21.5949 | 21.7654 | 21.9013 | 21.0667 | 21.2161 | 21.9874 | 20.4755 | 21.6652 | 27.7458 | 21.9549 | 22.6422 | 32.6839 | 289.5192 | 246.6132 | 349.9306 | 22.1314 | 22.413 | 29.7021 | 22.0743 | 22.6307 | 32.5869 | 125.1778 | 499.6788 |  | 196.7677 | 263.9585 | 249.4589 | 284.6172 |  | 19.4199 | 22.5476 | 20.3781 | 23.0543 | 26.3484 | 68.3874 | 209.4834 | 15.8332 | 17.8194 | 16.0037 | 20.6532 | 19.1939 | 46.0893 | 49.0476 | 45.1628 | 21.7083 |  |  | 0.93925 | -0.2248 | -37.0253 | 0.48885 | 0.99172 | -168.9618 | 11.0556 | 2.059 | 0.44534 | 0.34691 | 2.6079 | 0.32218 | 0.3314 | 0.4909 | 22.0414 | 21.9604 | 22.1474 | 22.2039 | 22.0156 | 21.2897 | 20.1035 | 22.1707 | 22.3483 | 22.3846 | 22.3307 | 21.9426 | 21.1682 | 22.2621 | 155.1556 | 98.8814 | 111.4997 | 66.0105 | 57.1792 | 80.4474 | 51.6919 | 22.3074 | 22.0686 | 21.6588 | 22.0405 | 21.78 | 21.8367 | 21.9347 | 21.9725 | 27.9794 | 101.2979 | 256.5617 | 209.2671 | 171.7076 | 5.1034 | 2.8534 | 120.8008 | 21.8955 | 22.2071 | 22.6457 | 21.5557 | 22.0149 | 22.0744 | 23.3844 | 39.4842 | 21.8573 | 22.2088 | 29.4332 | 297.7409 | 649.6372 | 214.233 | 215.546 | 200.4868 |  | 104.9172 | 194.3046 | 105.1453 | 229.3445 | 156.9025 | 127.1477 |  | 135.8317 |  |  | 36.213 | 60.3402 | 117.6724 | [5 empty] | 21.8937 | 178.85 | 21.7186 | 22.099 | 64.9755 | 21.2864 | 21.9145 | 53.8717 | 203.0423 | 444.4005 |  | 164.1015 | 300.56 | 35.4372 | 147.4317 | 417.7656 | 121.8154 | 249.358 | 42.5404 | 194.3615 | 46.9978 | 205.0756 | 20.8331 | 155.9191 | 276.3558 | 58.4741 | 151.642 | 320.3735 | 36.4512 | 148.5647 | 314.821 | 34.6384 | 193.3048 | 66.1379 | 207.879 | 46.8042 | 239.6396 | 6.7268 | 18.2108 | 2.5011 | 0.061242 | -27.2514 | 3.0947 | 770.74 | 54.96 | 1.6859 | -0.56819 | -7.2919 | 0.83787 | 1.2826 | -16.741 | 4.2823 | -1.4963 | -1.3154 | -0.072871 | -7.4145 | -6.014 | -3.0015 | -0.84115
42838.4271 | 590 | 22.8842 | 22.8516 | 22.837 | 22.7471 | 22.3642 | 21.6881 | 22.6913 | 21.7431 | 22.3423 | 22.3475 | 22.3174 | 21.9637 | 21.177 | 22.1432 | 21.5877 | 21.7682 | 21.9134 | 21.0704 | 21.2276 | 21.9982 | 20.4861 | 21.683 | 27.7825 | 21.9598 | 22.6521 | 32.7416 | 292.7496 | 250.1758 | 349.2471 | 22.1265 | 22.4108 | 29.7433 | 22.0685 | 22.6355 | 32.6327 | 126.5718 | 505.616 |  | 199.6986 | 268.2925 | 252.9286 | 286.1383 |  | 19.4938 | 22.7012 | 20.4799 | 23.2407 | 26.5917 | 70.2397 | 210.9562 | 15.8268 | 17.8251 | 15.9764 | 20.6896 | 19.1922 | 46.1043 | 49.0422 | 45.1576 | 21.7136 |  |  | 0.98459 | -0.016493 | -37.4643 | 0.093266 | 1.135 | -165.1243 | 10.1468 | 1.8356 | 0.12425 | 0.4174 | 2.3488 | 0.28865 | 0.297 | 0.50256 | 22.052 | 21.9605 | 22.1613 | 22.2099 | 22.0199 | 21.2937 | 20.1116 | 22.1796 | 22.3552 | 22.3884 | 22.3377 | 21.9519 | 21.1824 | 22.2713 | 152.7141 | 98.5363 | 111.1483 | 66.5414 | 58.2128 | 80.9156 | 52.077 | 22.3133 | 22.0776 | 21.6703 | 22.0431 | 21.792 | 21.8415 | 21.9459 | 21.9755 | 28.0293 | 102.2347 | 260.7614 | 211.9336 | 174.4938 | 5.1655 | 2.547 | 123.1451 | 21.8984 | 22.2049 | 22.7297 | 21.5552 | 22.0169 | 22.0767 | 23.393 | 39.6073 | 21.8533 | 22.2098 | 29.4734 | 302.5811 | 656.1695 | 216.2423 | 217.2834 | 203.2074 |  | 106.0633 | 200.8686 | 106.0442 | 233.8668 | 158.5656 | 128.7581 |  | 137.157 |  |  | 36.6948 | 60.7515 | 119.0346 | [5 empty] | 21.8923 | 181.4456 | 21.7068 | 22.0936 | 65.6725 | 21.287 | 21.9156 | 54.4694 | 205.8368 | 450.3883 |  | 166.1834 | 304.137 | 35.9738 | 149.4235 | 425.711 | 123.6689 | 253.7412 | 43.162 | 196.5328 | 47.8092 | 207.5532 | 20.8693 | 157.2896 | 280.0755 | 59.1685 | 153.1623 | 326.3385 | 36.987 | 150.3596 | 318.7592 | 35.1419 | 195.7605 | 67.0202 | 210.417 | 47.4661 | 244.593 | 6.2008 | 18.1983 | 2.5141 | 0.062672 | -27.3044 | 3.0947 | 783.34 | 55.92 | 1.7252 | -0.15394 | -7.3369 | 0.36607 | 1.3758 | -16.5946 | 4.1136 | -1.5259 | -1.4617 | -0.12212 | -7.0865 | -5.9291 | -2.9849 | -0.88133
42838.4271 | 591 | 22.8868 | 22.8544 | 22.8451 | 22.7521 | 22.3699 | 21.6863 | 22.6924 | 21.7484 | 22.3399 | 22.3455 | 22.3157 | 21.9641 | 21.1766 | 22.151 | 21.5883 | 21.7601 | 21.9091 | 21.067 | 21.2276 | 21.9934 | 20.4805 | 21.6875 | 27.8151 | 21.9496 | 22.6443 | 32.7825 | 296.6097 | 253.8011 | 352.8853 | 22.1319 | 22.4201 | 29.7765 | 22.068 | 22.6382 | 32.6778 | 127.9072 | 492.9967 |  | 202.3964 | 272.0827 | 256.2014 | 286.3571 |  | 19.5642 | 22.8489 | 20.5932 | 23.4287 | 26.7744 | 70.4898 | 212.8695 | 15.8549 | 17.846 | 16.042 | 20.7483 | 19.193 | 46.1228 | 49.0368 | 45.1537 | 21.7099 |  |  | 0.7316 | -0.34242 | -38.2568 | 0.15175 | 1.0134 | -162.1692 | 9.2682 | 1.4387 | 0.37995 | 0.45412 | 2.6461 | 0.2597 | 0.26723 | 0.50966 | 22.0559 | 21.9534 | 22.1517 | 22.1998 | 22.0111 | 21.294 | 20.1082 | 22.1741 | 22.3503 | 22.3863 | 22.3369 | 21.9393 | 21.1715 | 22.2596 | 147.1076 | 94.0863 | 105.4348 | 66.1491 | 59.1635 | 81.2683 | 52.3522 | 22.3206 | 22.0748 | 21.6692 | 22.0436 | 21.7989 | 21.8506 | 21.9459 | 21.981 | 28.0657 | 103.216 | 267.2653 | 215.5014 | 177.9911 | 2.4632 | 1.2554 | 124.9268 | 21.8958 | 22.1996 | 22.8 | 21.5494 | 22.013 | 22.0779 | 23.4014 | 39.734 | 21.8498 | 22.2048 | 29.5014 | 308.3152 | 661.0063 | 218.5556 | 219.4803 | 206.6848 |  | 107.0641 | 204.4877 | 106.8494 | 237.2604 | 160.0778 | 131.3127 |  | 138.2959 |  |  | 37.2538 | 61.4841 | 121.3925 | [5 empty] | 21.9081 | 184.4823 | 21.7137 | 22.1001 | 66.4883 | 21.2932 | 21.9119 | 55.1092 | 208.9083 | 456.3746 |  | 168.5109 | 307.493 | 36.4979 | 151.4426 | 432.9605 | 125.4725 | 258.5566 | 43.7469 | 198.3265 | 48.612 | 210.1651 | 20.9058 | 158.8989 | 285.0052 | 59.8245 | 154.8184 | 330.6285 | 37.5836 | 152.1983 | 322.0156 | 35.6077 | 198.6203 | 67.9036 | 212.7161 | 48.1622 | 248.6511 | 7.8684 | 18.1851 | 2.5263 | 0.061038 | -27.3025 | 3.0948 | 791.27 | 55.47 | 1.4914 | -0.7016 | -7.4159 | 0.46706 | 1.3005 | -16.4514 | 3.9329 | -1.5823 | -1.5299 | -0.14664 | -6.4208 | -5.2616 | -2.9345 | -0.93939
42838.4271 | 592 | 22.8803 | 22.8518 | 22.8395 | 22.7574 | 22.3622 | 21.6879 | 22.6868 | 21.7397 | 22.3385 | 22.3486 | 22.3154 | 21.9647 | 21.1768 | 22.1529 | 21.5994 | 21.7685 | 21.916 | 21.074 | 21.2186 | 22.0088 | 20.4844 | 21.7009 | 27.853 | 21.9592 | 22.6636 | 32.847 | 299.8712 | 256.6431 | 351.768 | 22.1335 | 22.4293 | 29.8129 | 22.0681 | 22.6402 | 32.7259 | 129.2605 | 487.1024 |  | 204.9422 | 275.9916 | 259.0066 | 289.7117 |  | 19.6552 | 23.0113 | 20.6996 | 23.6439 | 26.9682 | 70.9963 | 214.7934 | 15.8723 | 17.8613 | 16.0674 | 20.8013 | 19.1946 | 46.1556 | 49.0411 | 45.1756 | 21.718 |  |  | 0.8144 | -0.10389 | -38.6313 | 0.48294 | 1.1429 | -165.0927 | 10.3334 | 2.2016 | 0.23575 | 0.5265 | 2.7097 | 0.2342 | 0.24103 | 0.51889 | 22.0609 | 21.9607 | 22.1455 | 22.2009 | 22.0087 | 21.3008 | 20.117 | 22.1738 | 22.3623 | 22.3844 | 22.3312 | 21.9459 | 21.1778 | 22.2604 | 143.0928 | 88.711 | 97.5554 | 65.4107 | 58.0034 | 81.6094 | 52.5515 | 22.3182 | 22.0721 | 21.6687 | 22.0423 | 21.7952 | 21.8513 | 21.94 | 21.9861 | 28.0868 | 104.2497 | 272.7796 | 218.7965 | 181.6631 | 3.7321 | 2.6246 | 125.6178 | 21.8925 | 22.2009 | 22.8736 | 21.5502 | 22.0068 | 22.0838 | 23.4098 | 39.8668 | 21.8535 | 22.2141 | 29.5378 | 311.5708 | 666.8533 | 220.8131 | 221.817 | 208.0126 |  | 108.0992 | 208.7237 | 107.6703 | 239.9577 | 161.605 | 132.8946 |  | 139.4309 |  |  | 37.6966 | 62.74 | 123.9547 | [5 empty] | 21.888 | 186.9819 | 21.6992 | 22.0871 | 67.1571 | 21.2854 | 21.9054 | 55.7365 | 211.5815 | 461.4113 |  | 170.4575 | 311.4353 | 36.9387 | 153.2478 | 435.7154 | 127.3346 | 262.4006 | 44.2012 | 199.8463 | 49.4427 | 212.5409 | 21.0051 | 160.1601 | 288.8607 | 60.4252 | 156.6669 | 334.047 | 38.0923 | 154.0489 | 326.0671 | 36.0135 | 201.0644 | 68.8223 | 215.5145 | 48.8826 | 252.519 | 8.2581 | 18.1724 | 2.5414 | 0.063252 | -27.3268 | 3.0947 | 811.57 | 55.12 | 1.5722 | -0.38656 | -7.4542 | 0.83344 | 1.3821 | -16.6113 | 4.1559 | -1.5775 | -1.6145 | -0.15083 | -5.9334 | -4.3624 | -2.9701 | -1.0001
42838.4271 | 593 | 22.8898 | 22.8535 | 22.8397 | 22.7571 | 22.3656 | 21.6904 | 22.6909 | 21.7425 | 22.3459 | 22.3447 | 22.3105 | 21.9652 | 21.1768 | 22.1552 | 21.5967 | 21.7675 | 21.9153 | 21.0754 | 21.2235 | 22.011 | 20.4891 | 21.7146 | 27.887 | 21.9668 | 22.67 | 32.8961 | 303.1478 | 259.7821 | 354.1787 | 22.1373 | 22.4366 | 29.852 | 22.075 | 22.6461 | 32.7745 | 130.649 | 489.7087 |  | 207.5056 | 279.6716 | 262.327 | 295.0683 |  | 19.7378 | 23.1737 | 20.8089 | 23.8208 | 27.1699 | 71.458 | 217.4565 | 15.8633 | 17.8764 | 16.005 | 20.8524 | 19.2027 | 46.1908 | 49.0215 | 45.1804 | 21.7124 |  |  | 0.71189 | -0.18472 | -39.3147 | 0.31603 | 0.8557 | -165.8451 | 10.2559 | 1.6575 | 0.32157 | 0.43398 | 2.6897 | 0.21156 | 0.21786 | 0.52171 | 22.0509 | 21.956 | 22.147 | 22.1897 | 22.0065 | 21.297 | 20.1009 | 22.1718 | 22.3476 | 22.3845 | 22.3332 | 21.9452 | 21.1653 | 22.2578 | 139.7264 | 88.9776 | 98.0964 | 65.2248 | 58.5646 | 81.9426 | 52.8331 | 22.3071 | 22.0684 | 21.6651 | 22.038 | 21.791 | 21.854 | 21.9352 | 21.981 | 28.1326 | 105.2879 | 277.1026 | 221.4822 | 185.4392 | 4.8081 | 3.0809 | 127.0384 | 21.8976 | 22.2074 | 22.9549 | 21.5615 | 22.0144 | 22.0925 | 23.4274 | 40.0086 | 21.858 | 22.2269 | 29.586 | 316.7149 | 671.5111 | 222.833 | 223.9136 | 211.1732 |  | 109.3449 | 214.1155 | 108.6434 | 242.3366 | 163.3756 | 134.3414 |  | 140.8282 |  |  | 38.2747 | 63.6967 | 125.7341 | [5 empty] | 21.8858 | 189.2917 | 21.7034 | 22.0887 | 67.6455 | 21.2854 | 21.9085 | 56.354 | 214.2568 | 464.1283 |  | 172.3453 | 315.4126 | 37.3887 | 155.1933 | 440.282 | 129.093 | 265.7257 | 44.6642 | 201.9308 | 50.2209 | 214.6576 | 21.0956 | 161.906 | 292.1914 | 61.057 | 158.3495 | 338.8932 | 38.5826 | 155.6453 | 329.8478 | 36.5365 | 203.4654 | 69.628 | 218.5138 | 49.5611 | 256.6093 | 7.784 | 18.1603 | 2.5526 | 0.060639 | -27.2744 | 3.0947 | 840.19 | 55.87 | 1.4727 | -0.51559 | -7.5219 | 0.67439 | 1.1967 | -16.6602 | 4.143 | -1.6149 | -1.725 | -0.13452 | -5.519 | -4.389 | -3.0597 | -1.0635
42838.4272 | 594 | 22.8846 | 22.8453 | 22.8368 | 22.7531 | 22.3631 | 21.6831 | 22.6881 | 21.7347 | 22.3375 | 22.3438 | 22.3101 | 21.9618 | 21.1735 | 22.1512 | 21.5882 | 21.7677 | 21.9169 | 21.075 | 21.2223 | 22.0132 | 20.487 | 21.7182 | 27.918 | 21.9621 | 22.6771 | 32.9465 | 306.2813 | 262.9014 | 354.8502 | 22.1376 | 22.4403 | 29.8929 | 22.0733 | 22.6623 | 32.8283 | 132.0447 | 488.4407 |  | 209.9928 | 283.5363 | 265.6829 | 294.9843 |  | 19.7997 | 23.3506 | 20.9281 | 24.0262 | 27.3829 | 72.8066 | 222.2026 | 15.8801 | 17.9029 | 15.9433 | 20.9198 | 19.2101 | 46.2086 | 49.0133 | 45.1844 | 21.7188 |  |  | 0.84199 | -0.33716 | -39.3456 | 0.22995 | 0.8465 | -164.3751 | 9.1907 | 1.8139 | 0.10051 | 0.72707 | 2.4791 | 0.19198 | 0.19764 | 0.52464 | 22.0566 | 21.9529 | 22.1454 | 22.196 | 22.0061 | 21.3001 | 20.1043 | 22.1688 | 22.348 | 22.3893 | 22.3374 | 21.9496 | 21.1678 | 22.262 | 141.1675 | 92.7861 | 100.7515 | 65.475 | 57.6107 | 82.3668 | 53.1708 | 22.3084 | 22.0769 | 21.6652 | 22.0446 | 21.792 | 21.8659 | 21.9432 | 21.9932 | 28.1729 | 106.2698 | 283.0957 | 223.8846 | 188.6663 | 4.9712 | 4.4106 | 128.9294 | 21.9047 | 22.2161 | 23.0409 | 21.5663 | 22.0187 | 22.0994 | 23.439 | 40.1587 | 21.8638 | 22.237 | 29.6306 | 323.1757 | 673.2227 | 225.1784 | 226.2479 | 213.5349 |  | 110.4094 | 216.1131 | 109.5408 | 244.7683 | 164.8769 | 135.7277 |  | 142.0739 |  |  | 38.7143 | 64.2128 | 126.719 | [5 empty] | 21.8865 | 191.6502 | 21.7099 | 22.093 | 68.3611 | 21.285 | 21.9073 | 56.937 | 216.7676 | 466.8022 |  | 174.5513 | 321.7968 | 37.8576 | 157.0344 | 444.1169 | 130.6459 | 269.3376 | 45.2289 | 204.2955 | 50.9327 | 217.4054 | 21.1918 | 163.6371 | 295.0185 | 61.6482 | 160.2374 | 342.6644 | 39.0199 | 157.0612 | 333.2822 | 36.933 | 205.7589 | 70.4683 | 221.1524 | 50.1902 | 260.5946 | 8.326 | 18.1481 | 2.5662 | 0.062643 | -27.2706 | 3.0947 | 842.48 | 55.23 | 1.6025 | -0.69679 | -7.5271 | 0.57543 | 1.1926 | -16.6187 | 3.9296 | -1.6374 | -1.7442 | -0.1319 | -5.6276 | -4.6438 | -2.9977 | -1.1137
42838.4272 | 595 | 22.8886 | 22.8576 | 22.8415 | 22.7599 | 22.3664 | 21.6848 | 22.6931 | 21.7393 | 22.3412 | 22.3476 | 22.3189 | 21.9641 | 21.1752 | 22.1533 | 21.5927 | 21.772 | 21.9203 | 21.078 | 21.228 | 22.02 | 20.4837 | 21.7242 | 27.9504 | 21.9637 | 22.6895 | 32.9966 | 308.8444 | 265.7618 | 354.1992 | 22.1405 | 22.4497 | 29.938 | 22.0724 | 22.6611 | 32.881 | 133.4512 | 493.5772 |  | 212.6022 | 287.1031 | 268.5783 | 294.7781 |  | 19.8742 | 23.514 | 21.0507 | 24.1891 | 27.5655 | 74.0784 | 225.5365 | 15.8995 | 17.9224 | 15.9263 | 20.9769 | 19.2183 | 46.2347 | 49.0008 | 45.1943 | 21.7158 |  |  | 1.1988 | -0.38185 | -40.0724 | 0.32129 | 0.8971 | -167.0102 | 9.8504 | 1.8882 | 0.15169 | 0.50174 | 2.5083 | 0.17441 | 0.17966 | 0.52854 | 22.0585 | 21.959 | 22.1455 | 22.1973 | 22.0083 | 21.2956 | 20.1021 | 22.1691 | 22.3429 | 22.3869 | 22.3299 | 21.9475 | 21.1781 | 22.2605 | 144.9884 | 98.6383 | 108.8587 | 66.6548 | 58.031 | 82.8288 | 53.5875 | 22.3059 | 22.0786 | 21.6684 | 22.0446 | 21.7907 | 21.8713 | 21.9394 | 22.0021 | 28.2013 | 107.2407 | 288.4641 | 226.2668 | 191.8205 | 4.9278 | 4.9138 | 130.6533 | 21.8996 | 22.2093 | 23.1086 | 21.559 | 22.0152 | 22.0978 | 23.4466 | 40.2992 | 21.8661 | 22.2385 | 29.6622 | 326.8749 | 674.4882 | 227.8839 | 228.9193 | 214.8658 |  | 111.5603 | 219.0505 | 110.4204 | 246.7032 | 166.2936 | 137.1332 |  | 143.3315 |  |  | 39.1158 | 64.7641 | 128.5959 | [5 empty] | 21.8942 | 193.7446 | 21.708 | 22.1006 | 69.0548 | 21.2903 | 21.9102 | 57.4495 | 219.2615 | 469.7261 |  | 176.6069 | 327.4118 | 38.3256 | 158.9304 | 446.5236 | 132.2575 | 273.0118 | 45.6986 | 206.4603 | 51.6396 | 220.8434 | 21.2565 | 165.2928 | 297.3135 | 62.2086 | 162.203 | 345.2439 | 39.4999 | 158.6095 | 336.3851 | 37.2825 | 208.1464 | 71.291 | 223.6162 | 50.8856 | 263.9102 | 8.0867 | 18.1315 | 2.5817 | 0.061191 | -27.2584 | 3.0947 | 841.11 | 56.2 | 1.9112 | -0.74173 | -7.5984 | 0.68037 | 1.23 | -16.7821 | 4.0757 | -1.6276 | -1.7902 | -0.11916 | -5.9961 | -5.495 | -2.9316 | -1.1623
42838.4272 | 596 | 22.8872 | 22.846 | 22.8385 | 22.7454 | 22.3636 | 21.6815 | 22.6842 | 21.7389 | 22.338 | 22.3369 | 22.3105 | 21.9623 | 21.1697 | 22.1414 | 21.5848 | 21.7636 | 21.9132 | 21.064 | 21.2228 | 22.0143 | 20.4806 | 21.7256 | 27.9835 | 21.9579 | 22.679 | 33.041 | 311.9059 | 268.037 | 355.9511 | 22.1373 | 22.4495 | 29.9739 | 22.0673 | 22.6653 | 32.9338 | 134.9032 | 483.4116 |  | 215.1353 | 290.9173 | 271.1839 | 296.1414 |  | 19.9492 | 23.6448 | 21.1477 | 24.3483 | 27.7606 | 74.2605 | 229.0343 | 15.9378 | 17.9308 | 15.9941 | 21.0161 | 19.2357 | 46.2546 | 48.9898 | 45.2066 | 21.7223 |  |  | 0.83871 | -0.37659 | -40.5008 | 0.50133 | 1.1212 | -167.0535 | 9.332 | 1.7029 | 0.26455 | 0.46587 | 2.689 | 0.15893 | 0.16388 | 0.5353 | 22.0674 | 21.9631 | 22.1485 | 22.1988 | 22.0061 | 21.3022 | 20.1047 | 22.1762 | 22.3527 | 22.3914 | 22.3313 | 21.9488 | 21.1778 | 22.2584 | 145.7031 | 101.3307 | 114.2564 | 67.6721 | 58.5557 | 83.2952 | 54.0403 | 22.3164 | 22.0859 | 21.6724 | 22.049 | 21.8032 | 21.8804 | 21.947 | 22.0092 | 28.2416 | 108.2276 | 295.0659 | 229.6965 | 194.2722 | 5.2207 | 3.8198 | 132.4026 | 21.8927 | 22.2042 | 23.1739 | 21.5478 | 22.0155 | 22.0965 | 23.4528 | 40.4463 | 21.8581 | 22.2404 | 29.6986 | 330.8034 | 676.436 | 230.4649 | 231.4015 | 218.3442 |  | 112.851 | 224.2858 | 111.3984 | 248.2825 | 167.8421 | 138.7529 |  | 144.7294 |  |  | 39.4071 | 65.0183 | 129.6516 | [5 empty] | 21.8891 | 195.7207 | 21.7004 | 22.0976 | 69.703 | 21.285 | 21.9064 | 57.8905 | 221.6702 | 474.0102 |  | 178.3173 | 331.7976 | 38.7669 | 160.6687 | 451.921 | 133.9413 | 276.2952 | 46.1889 | 208.2025 | 52.3231 | 223.3171 | 21.2994 | 166.9557 | 299.8546 | 62.7973 | 164.1103 | 347.2547 | 39.9959 | 160.1695 | 338.6727 | 37.622 | 210.3979 | 72.0429 | 226.0239 | 51.5389 | 266.7651 | 7.9387 | 18.1208 | 2.5958 | 0.06183 | -27.1491 | 3.0947 | 832.96 | 54.77 | 1.6008 | -0.73677 | -7.6406 | 0.85008 | 1.3754 | -16.7887 | 3.968 | -1.6716 | -1.8959 | -0.090054 | -6.0189 | -6.0409 | -2.9068 | -1.1906
42838.4272 | 597 | 22.8847 | 22.8559 | 22.8365 | 22.7589 | 22.3652 | 21.6909 | 22.6846 | 21.7415 | 22.3511 | 22.3493 | 22.3089 | 21.9646 | 21.1781 | 22.1527 | 21.5851 | 21.7604 | 21.9098 | 21.06 | 21.2223 | 22.0196 | 20.4813 | 21.7307 | 28.0167 | 21.96 | 22.6842 | 33.0959 | 315.1452 | 269.9419 | 358.923 | 22.1367 | 22.4565 | 30.0146 | 22.0693 | 22.6742 | 33.0009 | 136.3901 | 482.5623 |  | 217.7632 | 294.2664 | 273.7966 | 298.0088 |  | 20.0451 | 23.8151 | 21.2815 | 24.5589 | 28.0719 | 74.4912 | 232.7191 | 15.978 | 17.9563 | 15.9935 | 21.0998 | 19.243 | 46.2695 | 48.9784 | 45.2195 | 21.724 |  |  | 0.64289 | -0.14135 | -40.968 | 0.42051 | 1.2546 | -169.0669 | 8.6709 | 1.7338 | 0.23828 | 0.47279 | 2.4614 | 0.14528 | 0.14997 | 0.54025 | 22.0703 | 21.9599 | 22.1545 | 22.2054 | 22.0041 | 21.3006 | 20.111 | 22.1819 | 22.3592 | 22.3874 | 22.3393 | 21.9465 | 21.1732 | 22.2593 | 146.6772 | 103.1665 | 113.7967 | 67.7351 | 58.5474 | 83.7919 | 54.4452 | 22.3165 | 22.0811 | 21.6649 | 22.0401 | 21.7985 | 21.8752 | 21.9425 | 22.0097 | 28.2789 | 109.3471 | 301.6621 | 232.7642 | 197.3587 | 4.6461 | 3.8046 | 134.1668 | 21.8874 | 22.2043 | 23.2402 | 21.5401 | 22.0104 | 22.0878 | 23.4541 | 40.608 | 21.8484 | 22.2401 | 29.7393 | 335.4605 | 680.0114 | 232.989 | 233.6294 | 219.8595 |  | 114.1009 | 227.089 | 112.3715 | 250.462 | 169.3918 | 140.2579 |  | 146.1364 |  |  | 39.6616 | 65.3492 | 130.444 | [5 empty] | 21.8886 | 197.5143 | 21.6997 | 22.0928 | 70.2054 | 21.2844 | 21.9062 | 58.41 | 224.0784 | 477.9353 |  | 179.9492 | 334.8811 | 39.2046 | 162.3506 | 457.1199 | 135.5856 | 279.7038 | 46.7001 | 209.8816 | 53.0133 | 225.9495 | 21.3159 | 168.3835 | 302.7443 | 63.4269 | 165.7641 | 349.0725 | 40.476 | 161.8516 | 341.0963 | 37.9528 | 212.5526 | 72.9089 | 228.1828 | 52.1763 | 269.6643 | 7.4273 | 18.1044 | 2.611 | 0.062962 | -27.313 | 3.0947 | 853.8 | 54.76 | 1.4048 | -0.4515 | -7.6867 | 0.77877 | 1.4554 | -16.8951 | 3.8262 | -1.6626 | -1.9341 | -0.077247 | -6.0669 | -5.9416 | -2.8944 | -1.2311
42838.4272 | 598 | 22.8952 | 22.8546 | 22.8472 | 22.7678 | 22.3687 | 21.6923 | 22.6957 | 21.7418 | 22.3446 | 22.3525 | 22.3199 | 21.9674 | 21.1899 | 22.1642 | 21.5915 | 21.7664 | 21.9122 | 21.0693 | 21.2317 | 22.0314 | 20.4866 | 21.7437 | 28.0543 | 21.9711 | 22.701 | 33.1561 | 318.3991 | 271.9761 | 363.6477 | 22.1335 | 22.4477 | 30.052 | 22.0627 | 22.6746 | 33.05 | 137.8249 | 483.1654 |  | 220.1347 | 296.7054 | 276.6181 | 299.5774 |  | 20.1012 | 23.9554 | 21.3815 | 24.7205 | 28.3199 | 74.7366 | 233.5977 | 15.9513 | 17.9736 | 15.9523 | 21.152 | 19.2526 | 46.2705 | 48.9526 | 45.2144 | 21.7253 |  |  | 0.84528 | -0.13937 | -41.4241 | 0.31471 | 0.99566 | -166.8144 | 8.6867 | 2.1491 | 0.21007 | 0.44845 | 2.4574 | 0.13325 | 0.13748 | 0.53798 | 22.0538 | 21.9553 | 22.142 | 22.1994 | 22.0081 | 21.2953 | 20.1046 | 22.1685 | 22.3452 | 22.3832 | 22.3302 | 21.9429 | 21.1645 | 22.254 | 150.3216 | 104.6495 | 116.3788 | 68.4852 | 56.7413 | 84.2717 | 54.863 | 22.3194 | 22.082 | 21.6709 | 22.0481 | 21.7961 | 21.8808 | 21.9412 | 22.0064 | 28.3237 | 110.4294 | 305.3183 | 235.2889 | 198.9619 | 5.3975 | 3.8472 | 135.454 | 21.8941 | 22.2054 | 23.3132 | 21.5506 | 22.0091 | 22.091 | 23.4658 | 40.7798 | 21.8519 | 22.2422 | 29.7845 | 339.0211 | 684.2646 | 235.6589 | 235.9778 | 222.0198 |  | 115.2338 | 229.238 | 113.2892 | 251.8367 | 170.8285 | 141.4126 |  | 147.3817 |  |  | 39.9146 | 65.4664 | 131.6626 | [5 empty] | 21.8923 | 199.0998 | 21.699 | 22.0911 | 70.6087 | 21.2826 | 21.9086 | 58.9227 | 226.5043 | 482.1608 |  | 181.6305 | 337.5469 | 39.6575 | 164.1958 | 459.6775 | 137.314 | 282.9747 | 47.1966 | 211.6656 | 53.7223 | 228.1419 | 21.3464 | 169.9171 | 305.7561 | 64.0096 | 167.289 | 351.5241 | 40.938 | 163.2296 | 344.0092 | 38.2809 | 214.9154 | 73.7997 | 230.3354 | 52.8039 | 272.2893 | 6.6645 | 18.0919 | 2.6273 | 0.063869 | -27.2279 | 3.0947 | 850.38 | 51.79 | 1.6168 | -0.44845 | -7.7312 | 0.67388 | 1.297 | -16.7881 | 3.831 | -1.6762 | -1.9563 | -0.047146 | -6.4135 | -6.1787 | -2.8756 | -1.2318
42838.4272 | 599 | 22.8923 | 22.8558 | 22.8379 | 22.7598 | 22.3662 | 21.6945 | 22.6933 | 21.7427 | 22.3436 | 22.3492 | 22.3183 | 21.9642 | 21.1833 | 22.1583 | 21.5913 | 21.7667 | 21.9192 | 21.0724 | 21.2341 | 22.0343 | 20.492 | 21.7536 | 28.0908 | 21.9724 | 22.7076 | 33.2152 | 321.7617 | 274.1206 | 368.6683 | 22.1322 | 22.4604 | 30.0978 | 22.0743 | 22.6852 | 33.1097 | 139.2611 | 491.3408 |  | 222.563 | 299.434 | 279.1678 | 300.69 |  | 20.1897 | 24.1192 | 21.494 | 24.8739 | 28.5509 | 75.7672 | 235.0035 | 15.8832 | 17.988 | 15.9172 | 21.2139 | 19.2584 | 46.2767 | 48.9365 | 45.2186 | 21.7236 |  |  | 0.74671 | -0.2478 | -41.5752 | 0.54142 | 0.81036 | -167.043 | 9.033 | 1.7844 | 0.18769 | 0.40419 | 2.6249 | 0.12241 | 0.12646 | 0.52188 | 22.0654 | 21.9669 | 22.1507 | 22.2067 | 22.0067 | 21.2982 | 20.1084 | 22.1779 | 22.3555 | 22.3959 | 22.3417 | 21.9565 | 21.1763 | 22.2683 | 156.1937 | 107.6528 | 118.3604 | 68.9316 | 56.4896 | 84.8403 | 55.284 | 22.3262 | 22.0787 | 21.6776 | 22.0478 | 21.8009 | 21.8907 | 21.9455 | 22.012 | 28.3619 | 111.4621 | 308.748 | 237.5676 | 201.2558 | 4.9927 | 4.4684 | 136.963 | 21.8981 | 22.2083 | 23.3851 | 21.5551 | 22.0086 | 22.0977 | 23.4782 | 40.9585 | 21.8539 | 22.2513 | 29.8261 | 344.0884 | 688.246 | 237.998 | 238.335 | 223.2112 |  | 116.3541 | 231.5865 | 114.2651 | 252.1009 | 172.3285 | 143.9751 |  | 148.677 |  |  | 40.2209 | 65.7854 | 133.0775 | [5 empty] | 21.8897 | 200.1226 | 21.6988 | 22.0949 | 71.0271 | 21.2903 | 21.9081 | 59.4907 | 228.8633 | 485.4641 |  | 183.4115 | 341.3991 | 40.1337 | 166.2371 | 462.8792 | 139.0836 | 285.9621 | 47.7388 | 213.6881 | 54.4267 | 230.273 | 21.3984 | 172.0768 | 308.7379 | 64.5811 | 168.6863 | 354.2879 | 41.3793 | 164.6196 | 346.5626 | 38.6373 | 217.1872 | 74.6785 | 232.4419 | 53.3734 | 274.5762 | 5.6465 | 18.0747 | 2.6448 | 0.064232 | -27.1055 | 3.0947 | 839.82 | 51.86 | 1.5256 | -0.59812 | -7.7475 | 0.88411 | 1.1718 | -16.8245 | 3.9124 | -1.6632 | -1.9816 | 0.017105 | -6.9969 | -6.3488 | -2.8439 | -1.2535
42838.4272 | 600 | 22.8859 | 22.8526 | 22.8375 | 22.7528 | 22.3613 | 21.695 | 22.6899 | 21.7422 | 22.3398 | 22.3421 | 22.3149 | 21.9635 | 21.1782 | 22.1518 | 21.5888 | 21.7688 | 21.9198 | 21.0699 | 21.2337 | 22.0343 | 20.4872 | 21.7641 | 28.1303 | 21.9694 | 22.7199 | 33.2682 | 324.6551 | 276.7603 | 369.5958 | 22.1301 | 22.4639 | 30.1358 | 22.0764 | 22.6867 | 33.1709 | 140.7043 | 495.0794 |  | 225.1887 | 302.4695 | 281.3143 | 302.0156 |  | 20.2655 | 24.2666 | 21.5789 | 25.0173 | 28.737 | 76.7291 | 236.3561 | 15.8612 | 17.9994 | 15.8923 | 21.2643 | 19.2645 | 46.2825 | 48.9184 | 45.2206 | 21.7202 |  |  | 0.83345 | -0.13872 | -41.9399 | 0.18592 | 0.9904 | -167.777 | 8.5467 | 1.601 | 0.29919 | 0.65028 | 2.9635 | 0.11297 | 0.11658 | 0.52491 | 22.0808 | 21.9583 | 22.1555 | 22.2067 | 22.0183 | 21.2987 | 20.1121 | 22.183 | 22.3547 | 22.3932 | 22.3376 | 21.9523 | 21.171 | 22.2697 | 160.1095 | 109.3201 | 119.5765 | 70.6748 | 57.6291 | 85.3624 | 55.758 | 22.3138 | 22.0738 | 21.6778 | 22.0476 | 21.8044 | 21.892 | 21.9438 | 22.0174 | 28.3981 | 112.5085 | 312.8082 | 240.4406 | 204.7351 | 3.6861 | 3.5189 | 138.8371 | 21.895 | 22.2051 | 23.4501 | 21.5493 | 22.0086 | 22.1 | 23.4865 | 41.1367 | 21.8547 | 22.2585 | 29.8639 | 350.0986 | 690.3939 | 240.3865 | 240.5958 | 222.8151 |  | 117.476 | 235.502 | 115.3805 | 250.8211 | 174.095 | 145.1734 |  | 150.2238 |  |  | 40.5372 | 66.1687 | 134.1186 | [5 empty] | 21.8823 | 201.4053 | 21.6975 | 22.0906 | 71.492 | 21.2899 | 21.9062 | 60.1124 | 231.4781 | 488.2989 |  | 185.2877 | 345.3928 | 40.5762 | 168.2026 | 467.37 | 140.9131 | 288.6156 | 48.2759 | 215.9472 | 55.1246 | 232.2501 | 21.4481 | 173.9732 | 310.6613 | 65.1614 | 170.3266 | 357.5809 | 41.8202 | 166.1234 | 349.1242 | 39.0286 | 219.5428 | 75.5786 | 234.9287 | 53.933 | 277.6894 | 7.9014 | 18.0608 | 2.6593 | 0.062076 | -27.2547 | 3.0948 | 853.27 | 52.91 | 1.613 | -0.44763 | -7.7833 | 0.51822 | 1.2973 | -16.8847 | 3.8109 | -1.6059 | -2.0446 | 0.13735 | -7.3685 | -6.4274 | -2.8176 | -1.3076
42838.4272 | 601 | 22.8836 | 22.8568 | 22.8422 | 22.7587 | 22.3618 | 21.6813 | 22.6876 | 21.7478 | 22.3429 | 22.343 | 22.3121 | 21.9651 | 21.173 | 22.1506 | 21.5911 | 21.7673 | 21.9159 | 21.0683 | 21.2282 | 22.0441 | 20.4812 | 21.7693 | 28.1629 | 21.9689 | 22.7151 | 33.3208 | 327.2083 | 279.2578 | 369.1162 | 22.1333 | 22.475 | 30.1752 | 22.0763 | 22.6947 | 33.2335 | 142.141 | 496.996 |  | 227.7904 | 305.5979 | 283.3937 | 302.9445 |  | 20.3577 | 24.4092 | 21.6661 | 25.1597 | 28.8882 | 79.2062 | 238.4639 | 15.9011 | 18.0121 | 15.9516 | 21.317 | 19.2658 | 46.2767 | 48.891 | 45.2137 | 21.7377 |  |  | 0.46744 | 0.049875 | -42.2862 | 0.47637 | 0.68682 | -170.1394 | 7.8206 | 1.6372 | 0.20364 | 0.39663 | 2.7777 | 0.1043 | 0.10776 | 0.51804 | 22.0779 | 21.9645 | 22.1499 | 22.191 | 22.0082 | 21.2898 | 20.1038 | 22.1708 | 22.3476 | 22.381 | 22.3338 | 21.9411 | 21.1699 | 22.259 | 157.5263 | 107.907 | 114.8473 | 71.2171 | 58.8395 | 85.8021 | 56.1431 | 22.3143 | 22.0717 | 21.6746 | 22.045 | 21.7983 | 21.8914 | 21.94 | 22.0169 | 28.4295 | 113.6 | 317.0561 | 243.2065 | 208.355 | 5.31 | 2.5645 | 140.8324 | 21.8946 | 22.1949 | 23.5174 | 21.5512 | 22.009 | 22.0944 | 23.5006 | 41.3176 | 21.8538 | 22.2585 | 29.9038 | 353.8415 | 692.2574 | 242.7642 | 242.8906 | 224.3435 |  | 118.4686 | 236.9518 | 116.33 | 250.1051 | 175.6644 | 146.9921 |  | 151.619 |  |  | 40.9091 | 66.9991 | 134.8891 | [5 empty] | 21.8874 | 202.7761 | 21.6963 | 22.086 | 72.0787 | 21.2854 | 21.9033 | 60.7445 | 234.2678 | 491.988 |  | 187.3643 | 349.7482 | 40.9963 | 170.2924 | 471.9539 | 142.7505 | 291.7266 | 48.7546 | 217.756 | 55.8383 | 234.3749 | 21.5155 | 175.2634 | 312.6446 | 65.7373 | 172.311 | 358.9462 | 42.2057 | 167.7572 | 351.3996 | 39.4734 | 221.7918 | 76.4147 | 237.0509 | 54.4835 | 280.6656 | 8.7941 | 18.0478 | 2.6744 | 0.061859 | -27.2894 | 3.0947 | 855.87 | 51.73 | 1.2075 | 0.26847 | -7.8172 | 0.82971 | 1.0841 | -17.0632 | 3.6583 | -1.6073 | -2.0459 | 0.23285 | -7.0281 | -5.856 | -2.7802 | -1.3635
42838.4272 | 602 | 22.8895 | 22.8474 | 22.843 | 22.7566 | 22.3608 | 21.6895 | 22.6915 | 21.7449 | 22.3454 | 22.3457 | 22.3103 | 21.9634 | 21.1789 | 22.1604 | 21.585 | 21.777 | 21.9193 | 21.0686 | 21.2312 | 22.049 | 20.4904 | 21.7826 | 28.196 | 21.967 | 22.7193 | 33.3676 | 329.2642 | 280.8093 | 366.2776 | 22.1374 | 22.4815 | 30.2199 | 22.0799 | 22.7039 | 33.2951 | 143.6365 | 501.4752 |  | 230.445 | 308.9744 | 285.2822 | 307.1098 |  | 20.4487 | 24.5765 | 21.7896 | 25.3423 | 29.0561 | 83.5456 | 242.164 | 15.9485 | 18.0318 | 16.0281 | 21.3834 | 19.2762 | 46.2776 | 48.8615 | 45.2194 | 21.7432 |  |  | 0.89194 | -0.042777 | -42.4019 | 0.2904 | 1.0272 | -169.523 | 7.816 | 1.8218 | 0.21065 | 0.52167 | 2.6925 | 0.09653 | 0.10003 | 0.42436 | 22.0775 | 21.9704 | 22.1514 | 22.2036 | 22.0175 | 21.2919 | 20.1123 | 22.1741 | 22.3509 | 22.3917 | 22.3437 | 21.9471 | 21.1774 | 22.2626 | 161.54 | 107.2738 | 110.7197 | 67.8554 | 57.9653 | 86.4153 | 56.4623 | 22.3089 | 22.0652 | 21.6655 | 22.0377 | 21.7891 | 21.8812 | 21.9319 | 22.0089 | 28.4706 | 114.8516 | 321.7072 | 247.1099 | 211.017 | 4.6927 | 4.8155 | 141.7961 | 21.9049 | 22.2013 | 23.5999 | 21.5526 | 22.0162 | 22.0985 | 23.5167 | 41.5137 | 21.8584 | 22.2695 | 29.9529 | 356.9074 | 691.9579 | 245.3252 | 245.2877 | 228.4595 |  | 119.5321 | 237.943 | 117.2827 | 249.7734 | 177.2935 | 149.5894 |  | 153.0459 |  |  | 41.2607 | 68.3303 | 135.9508 | [5 empty] | 21.8859 | 204.2666 | 21.7022 | 22.0908 | 72.645 | 21.2867 | 21.9069 | 61.3519 | 236.8567 | 493.3624 |  | 189.3083 | 352.1707 | 41.452 | 172.3553 | 475.4586 | 144.7376 | 294.6947 | 49.3173 | 219.2908 | 56.5781 | 236.8514 | 21.6193 | 176.7998 | 315.3692 | 66.3017 | 174.0314 | 359.6387 | 42.6146 | 169.2731 | 353.2308 | 39.952 | 223.924 | 77.2652 | 238.7493 | 55.0548 | 282.6843 | 8.5156 | 18.0338 | 2.693 | 0.063869 | -27.5471 | 3.0947 | 855.18 | 52.24 | 1.6643 | -0.2487 | -7.8301 | 0.648 | 1.334 | -17.1368 | 3.6797 | -1.6776 | -2.0341 | 0.3209 | -7.3994 | -5.3593 | -2.83 | -1.3862
42838.4273 | 603 | 22.8774 | 22.8558 | 22.837 | 22.7474 | 22.3575 | 21.6932 | 22.6855 | 21.7429 | 22.3325 | 22.3395 | 22.3149 | 21.9669 | 21.178 | 22.1415 | 21.6011 | 21.7775 | 21.9186 | 21.0758 | 21.2403 | 22.0653 | 20.4971 | 21.793 | 28.2361 | 21.9784 | 22.7431 | 33.431 | 331.7125 | 283.1477 | 369.5108 | 22.1374 | 22.4834 | 30.2649 | 22.0739 | 22.7014 | 33.3522 | 145.1603 | 501.1592 |  | 233.1205 | 311.9079 | 287.1169 | 307.6589 |  | 20.5392 | 24.7351 | 21.9057 | 25.5301 | 29.2286 | 84.3605 | 245.2442 | 15.9424 | 18.0565 | 16.0147 | 21.4497 | 19.2922 | 46.2789 | 48.8401 | 45.2224 | 21.7492 |  |  | 0.84199 | -0.052633 | -43.0504 | 0.37911 | 1.2795 | -169.8851 | 7.5058 | 1.8547 | 0.25697 | 0.69518 | 2.6085 | 0.089905 | 0.093003 | 0.31913 | 22.0801 | 21.9701 | 22.1521 | 22.2033 | 22.013 | 21.2975 | 20.1113 | 22.1777 | 22.3572 | 22.3916 | 22.3433 | 21.9536 | 21.1786 | 22.2594 | 167.8363 | 107.5765 | 115.2402 | 69.2054 | 58.1156 | 87.0649 | 56.8927 | 22.3124 | 22.078 | 21.6641 | 22.0399 | 21.8013 | 21.8948 | 21.9421 | 22.0214 | 28.5162 | 115.9526 | 324.4502 | 249.475 | 212.5932 | 4.5529 | 3.9212 | 142.745 | 21.9019 | 22.21 | 23.676 | 21.5522 | 22.0223 | 22.1055 | 23.5353 | 41.7165 | 21.8668 | 22.2795 | 30.0002 | 359.0616 | 691.9102 | 247.8101 | 247.6262 | 230.7811 |  | 120.6792 | 239.4734 | 118.3994 | 250.8883 | 179.1763 | 152.2267 |  | 154.5294 |  |  | 41.5301 | 68.9234 | 136.951 | [5 empty] | 21.8827 | 206.5956 | 21.7077 | 22.0943 | 73.2725 | 21.2928 | 21.91 | 61.9235 | 239.3289 | 495.7315 |  | 191.2807 | 356.0305 | 41.8697 | 174.0197 | 478.5863 | 146.6566 | 296.9797 | 49.8997 | 220.8266 | 57.2941 | 238.6551 | 21.7074 | 178.4892 | 318.4662 | 66.847 | 175.6108 | 362.0113 | 42.923 | 171.1426 | 355.3585 | 40.3543 | 225.947 | 78.1801 | 240.4765 | 55.6839 | 285.4975 | 7.7467 | 18.0122 | 2.7096 | 0.061118 | -27.1758 | 3.0947 | 867.04 | 52.47 | 1.6211 | -0.27594 | -7.8919 | 0.74058 | 1.4905 | -17.1747 | 3.61 | -1.6944 | -2.0305 | 0.38151 | -8.02 | -5.8103 | -2.7777 | -1.3848
42838.4273 | 604 | 22.8842 | 22.845 | 22.8448 | 22.7475 | 22.3637 | 21.6883 | 22.6945 | 21.7446 | 22.3378 | 22.346 | 22.3164 | 21.966 | 21.1683 | 22.1543 | 21.5959 | 21.7653 | 21.9163 | 21.0701 | 21.2335 | 22.0627 | 20.4876 | 21.8041 | 28.2745 | 21.9758 | 22.7416 | 33.4782 | 334.7964 | 284.9828 | 373.3288 | 22.1331 | 22.4851 | 30.3007 | 22.08 | 22.7074 | 33.4163 | 146.7135 | 499.019 |  | 235.7463 | 315.0899 | 289.0702 | 308.0773 |  | 20.6241 | 24.9066 | 22.006 | 25.7342 | 29.4502 | 85.3764 | 248.5625 | 15.9259 | 18.0707 | 15.9342 | 21.5114 | 19.3043 | 46.2576 | 48.8229 | 45.2255 | 21.7535 |  |  | 1.1554 | -0.2938 | -44.1504 | 0.34231 | 0.80444 | -172.5483 | 7.2758 | 1.3158 | 0.13631 | 0.49209 | 2.6451 | 0.08359 | 0.086485 | 0.24336 | 22.0929 | 21.9779 | 22.1546 | 22.2116 | 22.0173 | 21.3057 | 20.1127 | 22.1839 | 22.3594 | 22.3984 | 22.3448 | 21.9555 | 21.1747 | 22.2702 | 166.3011 | 105.89 | 116.626 | 68.2821 | 59.9021 | 87.5903 | 57.3067 | 22.3141 | 22.0733 | 21.6713 | 22.0433 | 21.8054 | 21.8957 | 21.9372 | 22.0234 | 28.5566 | 117.0682 | 326.9288 | 251.6578 | 215.736 | 4.8035 | 3.9138 | 144.1151 | 21.8968 | 22.2108 | 23.7382 | 21.5563 | 22.0174 | 22.1058 | 23.545 | 41.9224 | 21.8661 | 22.2837 | 30.0518 | 360.6916 | 694.5658 | 249.9614 | 249.6507 | 231.4441 |  | 121.7196 | 242.0383 | 119.4164 | 252.5995 | 180.8647 | 153.528 |  | 155.8694 |  |  | 41.7521 | 69.5185 | 137.6766 | [5 empty] | 21.8817 | 208.8938 | 21.6936 | 22.0879 | 74.3012 | 21.284 | 21.9027 | 62.5338 | 241.8555 | 498.4072 |  | 193.4141 | 358.7629 | 42.3296 | 175.8527 | 481.2094 | 148.5902 | 299.4267 | 50.441 | 222.3968 | 58.0634 | 241.5618 | 21.7677 | 179.6833 | 321.6126 | 67.4285 | 177.3486 | 364.1535 | 43.3766 | 172.7212 | 357.5863 | 40.7662 | 227.874 | 79.082 | 242.233 | 56.2512 | 287.0986 | 8.0789 | 17.9951 | 2.7275 | 0.063724 | -27.2786 | 3.0948 | 899.52 | 51.55 | 1.9047 | -0.65214 | -7.9944 | 0.70393 | 1.1835 | -17.3334 | 3.5593 | -1.6694 | -2.0596 | 0.41651 | -7.7855 | -5.9149 | -2.7203 | -1.4261
42838.4273 | 605 | 22.8845 | 22.847 | 22.8321 | 22.7491 | 22.3578 | 21.6834 | 22.6824 | 21.7445 | 22.3346 | 22.3431 | 22.3168 | 21.9674 | 21.1766 | 22.1492 | 21.5929 | 21.767 | 21.9127 | 21.0731 | 21.2246 | 22.0572 | 20.4816 | 21.8012 | 28.3107 | 21.9777 | 22.747 | 33.5361 | 336.751 | 286.5447 | 373.6197 | 22.1389 | 22.4907 | 30.3567 | 22.0819 | 22.7185 | 33.4873 | 148.244 | 494.3929 |  | 238.0411 | 317.5653 | 290.4524 | 310.8076 |  | 20.6775 | 25.0533 | 22.097 | 25.8811 | 29.7915 | 85.3033 | 249.6978 | 15.957 | 18.0874 | 15.8958 | 21.5742 | 19.3315 | 46.2461 | 48.8033 | 45.2329 | 21.7547 |  |  | 0.92413 | -0.22546 | -44.5381 | 0.2398 | 1.1126 | -171.9307 | 7.448 | 1.5314 | 0.19664 | 0.61084 | 2.5072 | 0.077996 | 0.080889 | 0.17307 | 22.0837 | 21.9694 | 22.1547 | 22.2063 | 22.0149 | 21.2953 | 20.1119 | 22.1765 | 22.3515 | 22.3982 | 22.344 | 21.9488 | 21.1761 | 22.2721 | 165.9663 | 102.2159 | 116.551 | 70.6117 | 59.8475 | 88.0937 | 57.6872 | 22.3149 | 22.0841 | 21.671 | 22.0463 | 21.8096 | 21.9088 | 21.9404 | 22.0272 | 28.5967 | 118.2064 | 329.8974 | 253.721 | 218.2333 | 3.2121 | 2.9831 | 145.0004 | 21.8988 | 22.2111 | 23.8 | 21.5523 | 22.0177 | 22.1096 | 23.553 | 42.1387 | 21.8671 | 22.282 | 30.0977 | 363.0006 | 696.1705 | 252.0949 | 251.4643 | 233.7198 |  | 122.7692 | 243.8126 | 120.3701 | 253.9076 | 182.4977 | 155.1789 |  | 157.0583 |  |  | 42.197 | 70.703 | 138.8041 | [5 empty] | 21.8958 | 211.047 | 21.7061 | 22.1038 | 75.1508 | 21.299 | 21.9129 | 63.0541 | 244.5232 | 501.3016 |  | 195.4307 | 360.2474 | 42.7992 | 177.5086 | 486.0424 | 151.0455 | 302.132 | 51.008 | 224.2165 | 58.8519 | 243.9628 | 21.7752 | 180.9889 | 324.2076 | 68.0269 | 179.047 | 368.2524 | 43.8664 | 173.8851 | 360.2207 | 41.1302 | 229.4364 | 79.9841 | 243.6836 | 56.9096 | 290.1695 | 8.4997 | 17.9745 | 2.7465 | 0.063441 | -27.283 | 3.0947 | 922.36 | 52.7 | 1.7038 | -0.57142 | -8.0314 | 0.58932 | 1.3917 | -17.3006 | 3.6008 | -1.6888 | -2.0692 | 0.46038 | -7.6869 | -5.8612 | -2.7278 | -1.4485
42838.4273 | 606 | 22.8832 | 22.8494 | 22.8331 | 22.7561 | 22.3634 | 21.6895 | 22.6888 | 21.7484 | 22.3465 | 22.3475 | 22.3207 | 21.9734 | 21.1803 | 22.1487 | 21.5885 | 21.7661 | 21.9165 | 21.0736 | 21.2377 | 22.0696 | 20.4889 | 21.8132 | 28.3534 | 21.9727 | 22.7486 | 33.6028 | 338.8056 | 288.6042 | 375.4403 | 22.1404 | 22.4917 | 30.399 | 22.0735 | 22.7183 | 33.5507 | 149.7508 | 504.4809 |  | 240.5416 | 320.858 | 292.0213 | 312.6987 |  | 20.7268 | 25.1829 | 22.1872 | 26.0108 | 30.0967 | 85.6961 | 250.212 | 15.9965 | 18.115 | 15.9159 | 21.6304 | 19.3381 | 46.2466 | 48.7839 | 45.241 | 21.7507 |  |  | 0.48584 | -0.35491 | -45.1834 | 0.30749 | 0.7085 | -172.4662 | 6.4998 | 1.8435 | 0.20695 | 0.6614 | 2.8692 | 0.073106 | 0.075746 | 0.18714 | 22.0843 | 21.9568 | 22.1508 | 22.1991 | 22.0037 | 21.2963 | 20.1127 | 22.1765 | 22.3472 | 22.3872 | 22.3393 | 21.9484 | 21.1735 | 22.2651 | 162.4594 | 96.9085 | 113.4012 | 70.4964 | 61.0668 | 88.4359 | 58.0169 | 22.3121 | 22.0731 | 21.6682 | 22.0447 | 21.7999 | 21.903 | 21.9314 | 22.0318 | 28.6328 | 119.3822 | 332.1731 | 255.7396 | 220.5409 | 4.4343 | 3.3335 | 145.9271 | 21.8996 | 22.2104 | 23.865 | 21.5493 | 22.0199 | 22.1139 | 23.5596 | 42.3587 | 21.8709 | 22.2883 | 30.1379 | 365.8466 | 696.9953 | 253.9557 | 253.0544 | 235.6117 |  | 123.9982 | 247.0682 | 121.4272 | 254.0462 | 184.2576 | 156.1077 |  | 158.3138 |  |  | 42.6086 | 71.3839 | 139.7083 | [5 empty] | 21.8858 | 213.2 | 21.7021 | 22.0959 | 75.6037 | 21.2861 | 21.9069 | 63.6211 | 247.0262 | 502.4832 |  | 197.3452 | 363.0272 | 43.2805 | 179.2911 | 490.8014 | 153.0517 | 304.2946 | 51.5382 | 225.8467 | 59.5872 | 246.0709 | 21.8096 | 182.6173 | 325.6487 | 68.5104 | 180.7425 | 370.4042 | 44.3847 | 175.2152 | 362.9642 | 41.548 | 231.2793 | 80.8071 | 245.2728 | 57.5909 | 292.0102 | 7.3344 | 17.9573 | 2.7673 | 0.065227 | -27.2428 | 3.0948 | 910.48 | 51.31 | 1.2371 | -0.71709 | -8.0911 | 0.66747 | 1.1112 | -17.337 | 3.3657 | -1.6898 | -2.1156 | 0.5434 | -7.2556 | -5.4718 | -2.7128 | -1.4638
42838.4273 | 607 | 22.8816 | 22.8542 | 22.831 | 22.7482 | 22.3621 | 21.6848 | 22.6884 | 21.7418 | 22.3368 | 22.3427 | 22.3168 | 21.9661 | 21.1765 | 22.1445 | 21.5969 | 21.7739 | 21.9271 | 21.075 | 21.2278 | 22.0811 | 20.4893 | 21.8324 | 28.3909 | 21.9734 | 22.7641 | 33.6682 | 340.4185 | 290.1634 | 375.4685 | 22.1386 | 22.5074 | 30.4524 | 22.0812 | 22.7375 | 33.6261 | 151.2421 | 509.6974 |  | 243.1907 | 324.1298 | 293.7807 | 312.7152 |  | 20.7851 | 25.3331 | 22.2914 | 26.1657 | 30.4633 | 90.243 | 251.8382 | 16.015 | 18.1226 | 15.9413 | 21.7017 | 19.3512 | 46.2419 | 48.7647 | 45.2426 | 21.7567 |  |  | 0.56667 | -0.27343 | -46.0541 | 0.39817 | 1.0653 | -173.9007 | 6.8067 | 1.6142 | 0.19022 | 0.45412 | 2.9612 | 0.068391 | 0.071005 | 0.1951 | 22.0763 | 21.962 | 22.1489 | 22.2051 | 22.0099 | 21.2895 | 20.1023 | 22.1706 | 22.3534 | 22.3824 | 22.3338 | 21.9544 | 21.1704 | 22.2561 | 157.9185 | 99.7106 | 113.823 | 69.0021 | 61.613 | 88.8108 | 58.3492 | 22.3105 | 22.0758 | 21.6747 | 22.0405 | 21.798 | 21.9104 | 21.948 | 22.0412 | 28.6847 | 120.5855 | 334.576 | 258.1078 | 219.8543 | 4.9331 | 3.7833 | 146.772 | 21.8951 | 22.2068 | 23.9182 | 21.5536 | 22.0109 | 22.1105 | 23.5718 | 42.5889 | 21.8694 | 22.2858 | 30.1852 | 369.4575 | 698.2757 | 255.6481 | 254.4913 | 235.5583 |  | 125.2154 | 251.1023 | 122.478 | 255.6763 | 186.0662 | 156.4916 |  | 159.6358 |  |  | 42.8834 | 72.1391 | 141.1448 | [5 empty] | 21.8758 | 215.3376 | 21.6939 | 22.0828 | 76.2098 | 21.2894 | 21.8947 | 64.1021 | 249.4328 | 503.8855 |  | 199.2144 | 366.3424 | 43.7632 | 181.2898 | 495.3296 | 154.9314 | 307.1747 | 51.9642 | 227.3086 | 60.3555 | 248.6902 | 21.8443 | 184.4082 | 327.6983 | 69.0541 | 182.2917 | 373.4448 | 44.8635 | 176.4314 | 365.611 | 42.0667 | 232.8438 | 81.644 | 247.1 | 58.1481 | 295.1989 | 9.6633 | 17.9384 | 2.7862 | 0.063819 | -27.3393 | 3.0947 | 937.85 | 52.38 | 1.3361 | -0.62957 | -8.1707 | 0.75973 | 1.3712 | -17.5189 | 3.466 | -1.6371 | -2.1838 | 0.58785 | -6.7054 | -5.479 | -2.6461 | -1.3948
42838.4273 | 608 | 22.8789 | 22.8479 | 22.8327 | 22.7483 | 22.3553 | 21.6758 | 22.6845 | 21.74 | 22.337 | 22.341 | 22.3098 | 21.9616 | 21.1783 | 22.1458 | 21.5922 | 21.7675 | 21.9162 | 21.0752 | 21.2255 | 22.0784 | 20.4843 | 21.8365 | 28.429 | 21.9742 | 22.7643 | 33.7227 | 342.2746 | 292.2902 | 377.2465 | 22.1428 | 22.5115 | 30.4959 | 22.0814 | 22.7425 | 33.7035 | 152.7197 | 507.7911 |  | 245.6736 | 326.9775 | 295.4108 | 312.981 |  | 20.8303 | 25.4649 | 22.3805 | 26.2925 | 30.7434 | 93.2847 | 253.4861 | 16.0143 | 18.1491 | 15.9751 | 21.7685 | 19.3467 | 46.2574 | 48.7432 | 45.2338 | 21.7478 |  |  | 0.43393 | -0.25568 | -46.3485 | 0.23323 | 1.2559 | -171.8925 | 6.67 | 1.8205 | 0.25171 | 0.60811 | 2.6427 | 0.064312 | 0.06687 | 0.23093 | 22.0969 | 21.9616 | 22.1506 | 22.1986 | 22.0134 | 21.2882 | 20.1076 | 22.1715 | 22.3516 | 22.3888 | 22.3368 | 21.9516 | 21.1694 | 22.2692 | 154.5815 | 101.4247 | 113.7532 | 68.886 | 61.1852 | 89.1994 | 58.7002 | 22.3092 | 22.0809 | 21.6731 | 22.0451 | 21.8014 | 21.9208 | 21.9431 | 22.0432 | 28.7313 | 121.6775 | 336.4262 | 259.8006 | 219.7012 | 3.5638 | 3.6756 | 147.3041 | 21.8986 | 22.2067 | 23.9868 | 21.5613 | 22.0172 | 22.1122 | 23.5876 | 42.8239 | 21.8709 | 22.2949 | 30.235 | 371.9869 | 699.0821 | 257.3322 | 256.0479 | 236.9596 |  | 126.3785 | 253.4965 | 123.4577 | 257.3461 | 187.7243 | 156.5728 |  | 160.8933 |  |  | 43.3611 | 74.5022 | 143.0456 | [5 empty] | 21.8854 | 217.4597 | 21.7035 | 22.087 | 76.8725 | 21.2921 | 21.9092 | 64.6433 | 251.8741 | 506.6997 |  | 201.3008 | 369.31 | 44.2119 | 182.8079 | 498.5879 | 156.811 | 309.7382 | 52.4638 | 229.1004 | 61.1552 | 250.7819 | 21.9013 | 186.2542 | 330.2938 | 69.6244 | 183.9504 | 374.8675 | 45.3372 | 177.9382 | 367.5209 | 42.7578 | 234.7479 | 82.5644 | 249.0893 | 58.8038 | 297.4502 | 7.3165 | 17.9219 | 2.8186 | 0.063761 | -27.3389 | 3.0947 | 917.69 | 51.72 | 1.1707 | -0.60894 | -8.1986 | 0.58159 | 1.495 | -17.4902 | 3.4453 | -1.627 | -2.2093 | 0.62414 | -6.2872 | -5.4294 | -2.5867 | -1.345
42838.4273 | 609 | 22.8819 | 22.8462 | 22.8355 | 22.7529 | 22.3626 | 21.6772 | 22.687 | 21.7402 | 22.3405 | 22.3392 | 22.3121 | 21.9657 | 21.1719 | 22.1451 | 21.5805 | 21.7615 | 21.911 | 21.0677 | 21.2189 | 22.0754 | 20.4835 | 21.8322 | 28.4607 | 21.9757 | 22.7641 | 33.7783 | 344.3555 | 293.7521 | 378.7918 | 22.1433 | 22.5226 | 30.5441 | 22.086 | 22.7434 | 33.7742 | 154.2776 | 502.4989 |  | 248.0492 | 329.5207 | 296.9823 | 316.0761 |  | 20.8685 | 25.6315 | 22.4739 | 26.4429 | 31.1113 | 96.6953 | 255.6156 | 15.9753 | 18.1614 | 16.0087 | 21.824 | 19.3612 | 46.2732 | 48.7381 | 45.2449 | 21.7584 |  |  | 0.72634 | -0.33519 | -46.8821 | 0.272 | 0.86424 | -175.6953 | 6.7199 | 2.017 | 0.20617 | 0.58398 | 3.0116 | 0.060683 | 0.063009 | 0.22549 | 22.0918 | 21.9605 | 22.1472 | 22.199 | 22.0108 | 21.2986 | 20.1048 | 22.1751 | 22.3528 | 22.3929 | 22.3431 | 21.9479 | 21.1774 | 22.2678 | 152.1048 | 103.1451 | 113.6723 | 68.5928 | 59.7964 | 89.5764 | 59.0992 | 22.3134 | 22.0851 | 21.6744 | 22.0454 | 21.8013 | 21.9231 | 21.9428 | 22.0458 | 28.7726 | 122.7537 | 339.1477 | 262.0295 | 219.6711 | 5.0231 | 4.3568 | 148.009 | 21.8999 | 22.2093 | 24.0655 | 21.5622 | 22.0173 | 22.1165 | 23.5996 | 43.0603 | 21.872 | 22.3039 | 30.2892 | 374.3388 | 698.4807 | 258.8486 | 257.6115 | 239.0477 |  | 127.613 | 251.6992 | 124.4367 | 259.0763 | 189.4231 | 156.9347 |  | 162.0673 |  |  | 43.7443 | 75.5606 | 145.2896 | [5 empty] | 21.8892 | 219.534 | 21.7075 | 22.0855 | 77.7064 | 21.2925 | 21.9118 | 65.2437 | 254.3824 | 508.8305 |  | 203.3945 | 370.8745 | 44.627 | 184.4193 | 502.981 | 158.7757 | 312.4033 | 53.0145 | 230.7583 | 61.9539 | 253.3652 | 21.935 | 187.7536 | 333.3658 | 70.1381 | 185.7762 | 376.5319 | 45.8871 | 179.4894 | 370.1606 | 43.3721 | 236.6371 | 83.4461 | 251.2282 | 59.5113 | 299.7681 | 6.6443 | 17.9007 | 2.8527 | 0.063144 | -27.1491 | 3.0947 | 934.77 | 51.16 | 1.5165 | -0.69742 | -8.248 | 0.62825 | 1.2459 | -17.7647 | 3.4742 | -1.6328 | -2.1183 | 0.66119 | -5.9661 | -5.3727 | -2.6019 | -1.2992
42838.4273 | 610 | 22.8766 | 22.8506 | 22.834 | 22.7523 | 22.3568 | 21.6908 | 22.6914 | 21.7372 | 22.3316 | 22.3371 | 22.3122 | 21.9706 | 21.1741 | 22.1475 | 21.5822 | 21.7689 | 21.9237 | 21.0683 | 21.2274 | 22.0834 | 20.4917 | 21.8528 | 28.5056 | 21.9808 | 22.7768 | 33.8443 | 346.1915 | 295.6107 | 379.9158 | 22.137 | 22.5229 | 30.5894 | 22.0805 | 22.7479 | 33.837 | 155.8018 | 490.8976 |  | 250.3183 | 331.428 | 298.3072 | 319.1817 |  | 20.9489 | 25.793 | 22.5785 | 26.5845 | 31.5036 | 99.578 | 256.7206 | 15.986 | 18.1906 | 16.0629 | 21.8898 | 19.3628 | 46.2685 | 48.7271 | 45.2426 | 21.7598 |  |  | 0.82294 | -0.39762 | -47.5333 | 0.35545 | 1.3275 | -178.8757 | 6.1134 | 1.808 | -0.062373 | 0.34418 | 2.7635 | 0.056931 | 0.059357 | 0.19179 | 22.0951 | 21.9638 | 22.1544 | 22.1985 | 22.0088 | 21.2935 | 20.1021 | 22.1719 | 22.3527 | 22.3832 | 22.3327 | 21.951 | 21.1678 | 22.2555 | 150.8028 | 103.5872 | 112.8824 | 70.6267 | 61.2479 | 89.9459 | 59.4875 | 22.3146 | 22.0754 | 21.677 | 22.0442 | 21.8041 | 21.9309 | 21.9418 | 22.049 | 28.8184 | 123.8553 | 342.1921 | 264.704 | 220.9986 | 2.5888 | 3.2614 | 148.8832 | 21.8946 | 22.2123 | 24.1317 | 21.5561 | 22.0106 | 22.1134 | 23.6081 | 43.3111 | 21.8701 | 22.3014 | 30.3419 | 377.0476 | 698.1884 | 260.283 | 259.1307 | 239.7913 |  | 128.9065 | 249.5155 | 125.516 | 261.6586 | 191.3893 | 157.3446 |  | 163.3995 |  |  | 44.083 | 76.0478 | 146.3092 | [5 empty] | 21.8845 | 221.4607 | 21.702 | 22.0922 | 78.5222 | 21.2876 | 21.9132 | 65.8383 | 256.8559 | 510.5967 |  | 205.1564 | 373.0995 | 45.1652 | 186.1766 | 505.7803 | 160.6798 | 315.1546 | 53.6009 | 232.1963 | 62.7497 | 257.3139 | 21.9768 | 189.0716 | 336.6253 | 70.7038 | 187.7165 | 379.3215 | 46.2466 | 181.2173 | 373.7636 | 44.0425 | 238.3949 | 84.3023 | 253.3823 | 60.1439 | 301.5275 | 9.1671 | 17.8797 | 2.8707 | 0.062156 | -27.2327 | 3.0947 | 928.86 | 52.66 | 1.6156 | -0.75979 | -8.3073 | 0.71838 | 1.5502 | -17.9945 | 3.3266 | -1.5985 | -2.0122 | 0.6885 | -5.7764 | -5.2386 | -2.6187 | -1.2899
42838.4273 | 611 | 22.875 | 22.8436 | 22.8284 | 22.7566 | 22.3631 | 21.6813 | 22.6891 | 21.7422 | 22.3335 | 22.3382 | 22.3029 | 21.9625 | 21.1732 | 22.1383 | 21.5927 | 21.7683 | 21.9271 | 21.0694 | 21.2351 | 22.0901 | 20.4885 | 21.8647 | 28.5492 | 21.9801 | 22.7865 | 33.9158 | 347.9874 | 297.8451 | 382.0922 | 22.1399 | 22.5125 | 30.6422 | 22.0781 | 22.7579 | 33.9163 | 157.5094 | 492.0735 |  | 252.8189 | 334.3918 | 299.9405 | 320.2591 |  | 21.0062 | 25.9551 | 22.6732 | 26.722 | 31.6848 | 103.1576 | 257.2994 | 16.0101 | 18.2181 | 16.0771 | 21.952 | 19.385 | 46.2645 | 48.7187 | 45.2498 | 21.7639 |  |  | 0.59689 | -0.20837 | -48.2456 | 0.29434 | 1.1737 | -178.3862 | 5.1652 | 1.4598 | 0.17484 | 0.46377 | 2.8617 | 0.054186 | 0.056385 | 0.20862 | 22.107 | 21.9622 | 22.1494 | 22.1999 | 22.0094 | 21.2902 | 20.1016 | 22.1684 | 22.3495 | 22.3835 | 22.3352 | 21.9469 | 21.1645 | 22.2552 | 149.802 | 101.8336 | 109.016 | 68.9847 | 60.81 | 90.2931 | 59.7636 | 22.3158 | 22.0826 | 21.6762 | 22.0476 | 21.8003 | 21.9358 | 21.9388 | 22.0494 | 28.868 | 125.0566 | 345.3873 | 266.9711 | 222.2494 | 5.1462 | 2.9148 | 149.9649 | 21.894 | 22.2084 | 24.203 | 21.5529 | 22.0102 | 22.1125 | 23.6119 | 43.5636 | 21.8652 | 22.3011 | 30.3877 | 380.2687 | 699.801 | 261.7362 | 260.6526 | 239.3239 |  | 130.0901 | 250.6239 | 126.4336 | 263.1928 | 193.0297 | 160.3803 |  | 164.4608 |  |  | 44.5241 | 78.7301 | 147.5459 | [5 empty] | 21.8855 | 223.3385 | 21.7017 | 22.0905 | 79.2873 | 21.2879 | 21.9051 | 66.4182 | 259.3238 | 512.4787 |  | 206.7429 | 375.1066 | 45.6407 | 187.8708 | 508.5825 | 162.5821 | 318.2028 | 54.2153 | 233.608 | 63.5784 | 259.5866 | 22.0139 | 190.5755 | 339.8333 | 71.2639 | 189.7016 | 381.951 | 46.7082 | 182.7061 | 377.4291 | 44.5741 | 239.9075 | 85.151 | 255.9122 | 60.8145 | 304.2134 | 8.3229 | 17.8559 | 2.8925 | 0.061801 | -27.3106 | 3.0948 | 949.44 | 51.63 | 1.3782 | -0.55017 | -8.3716 | 0.65389 | 1.4646 | -18.0559 | 3.0724 | -1.5351 | -2.0042 | 0.72894 | -5.6228 | -4.776 | -2.5704 | -1.2741
42838.4274 | 612 | 22.8815 | 22.8537 | 22.8352 | 22.7539 | 22.3619 | 21.6894 | 22.6875 | 21.746 | 22.3428 | 22.3465 | 22.31 | 21.9656 | 21.1798 | 22.1493 | 21.5904 | 21.7619 | 21.9188 | 21.0699 | 21.2361 | 22.0951 | 20.4901 | 21.8665 | 28.5923 | 21.98 | 22.7936 | 33.9817 | 350.2875 | 299.9293 | 389.1572 | 22.1409 | 22.5274 | 30.7028 | 22.0844 | 22.766 | 34.0001 | 159.1122 | 491.6875 |  | 255.097 | 336.1996 | 302.107 | 320.6164 |  | 21.0645 | 26.1143 | 22.7492 | 26.83 | 31.8051 | 104.6445 | 258.8946 | 16.0057 | 18.2319 | 16.058 | 22.0177 | 19.4016 | 46.2501 | 48.7053 | 45.2539 | 21.7609 |  |  | 0.81834 | -0.44756 | -49.3469 | 0.05121 | 1.3538 | -182.7323 | 6.1522 | 1.8448 | 0.22992 | 0.40419 | 2.8458 | 0.051281 | 0.053479 | 0.25066 | 22.107 | 21.9721 | 22.1492 | 22.2036 | 22.0188 | 21.2954 | 20.1049 | 22.1777 | 22.3475 | 22.3894 | 22.3363 | 21.9503 | 21.1693 | 22.2602 | 150.6551 | 101.1225 | 106.6719 | 68.8967 | 61.0838 | 90.7135 | 60.0464 | 22.3107 | 22.0718 | 21.6684 | 22.0417 | 21.7967 | 21.9349 | 21.9417 | 22.0566 | 28.9128 | 126.2446 | 346.9996 | 268.7592 | 224.8193 | 4.451 | 2.9318 | 150.3223 | 21.8946 | 22.2055 | 24.2852 | 21.557 | 22.0154 | 22.1164 | 23.6262 | 43.8262 | 21.8668 | 22.3117 | 30.4429 | 383.0144 | 701.8275 | 263.1554 | 262.0902 | 238.1181 |  | 131.264 | 251.4673 | 127.3562 | 264.6498 | 194.7006 | 160.7672 |  | 165.4631 |  |  | 45.0158 | 80.3061 | 147.93 | [5 empty] | 21.8834 | 225.0866 | 21.7005 | 22.0874 | 79.8848 | 21.286 | 21.9 | 67.0335 | 261.8886 | 514.619 |  | 208.301 | 377.4062 | 46.1025 | 189.5495 | 512.0019 | 164.3979 | 321.7605 | 54.8049 | 234.8853 | 64.3552 | 261.44 | 22.0627 | 191.9486 | 341.9783 | 71.7893 | 191.5788 | 383.3455 | 47.2117 | 183.948 | 380.2034 | 45.0752 | 241.5101 | 86.0594 | 257.8988 | 61.5834 | 306.7324 | 8.7983 | 17.8359 | 2.9377 | 0.062156 | -27.3037 | 3.0948 | 969.51 | 52.81 | 1.6224 | -0.80653 | -8.4688 | 0.27282 | 1.5761 | -18.3106 | 3.3598 | -1.4515 | -1.9886 | 0.77348 | -5.6663 | -4.4818 | -2.5067 | -1.2954
42838.4274 | 613 | 22.8847 | 22.8503 | 22.8403 | 22.7514 | 22.3588 | 21.6803 | 22.6891 | 21.741 | 22.3368 | 22.3368 | 22.3126 | 21.9554 | 21.178 | 22.1482 | 21.5928 | 21.7753 | 21.9233 | 21.0703 | 21.232 | 22.101 | 20.4931 | 21.8841 | 28.6322 | 21.9836 | 22.7997 | 34.0404 | 352.6326 | 302.1412 | 392.5475 | 22.1367 | 22.529 | 30.7425 | 22.0714 | 22.7614 | 34.0682 | 160.6485 | 496.4141 |  | 257.5289 | 338.0468 | 303.6341 | 323.2512 |  | 21.1072 | 26.2317 | 22.7872 | 26.9522 | 31.893 | 108.4006 | 260.5935 | 15.9839 | 18.2407 | 16.0611 | 22.0772 | 19.4081 | 46.2551 | 48.6956 | 45.2537 | 21.7719 |  |  | 0.55812 | -0.63221 | -50.0264 | 0.24637 | 0.87212 | -183.1884 | 4.857 | 1.7758 | 0.10109 | 0.63916 | 2.9807 | 0.04893 | 0.050959 | 0.26908 | 22.1045 | 21.9628 | 22.1554 | 22.2021 | 22.0087 | 21.3002 | 20.1022 | 22.1766 | 22.3474 | 22.3899 | 22.3359 | 21.9474 | 21.1674 | 22.2621 | 153.2873 | 103.5392 | 107.9278 | 67.141 | 59.9323 | 91.13 | 60.3213 | 22.3161 | 22.0811 | 21.6731 | 22.0403 | 21.7992 | 21.9407 | 21.9379 | 22.0603 | 28.9628 | 127.3956 | 349.1611 | 270.7664 | 226.8717 | 3.3544 | 3.3453 | 151.0188 | 21.8844 | 22.2054 | 24.3563 | 21.5494 | 22.0114 | 22.1185 | 23.6389 | 44.0935 | 21.8689 | 22.3153 | 30.501 | 385.4595 | 704.1221 | 264.4759 | 263.4126 | 236.0083 |  | 132.6033 | 252.5726 | 128.4431 | 267.5332 | 196.6461 | 162.497 |  | 166.7393 |  |  | 45.4564 | 80.7342 | 148.467 | [5 empty] | 21.8803 | 227.0298 | 21.7014 | 22.0917 | 80.6907 | 21.2832 | 21.9109 | 67.6375 | 264.5753 | 515.8463 |  | 209.9601 | 378.9419 | 46.5606 | 191.2202 | 514.737 | 166.3707 | 324.962 | 55.4312 | 236.2842 | 65.1117 | 263.1607 | 22.1211 | 193.3222 | 343.8126 | 72.3703 | 193.245 | 385.1017 | 47.7128 | 185.4735 | 383.3896 | 45.5611 | 243.6562 | 87.0296 | 259.4298 | 62.3145 | 308.438 | 9.2443 | 17.8061 | 2.9566 | 0.062628 | -27.3249 | 3.0948 | 990.83 | 51.59 | 1.3433 | -0.95876 | -8.5286 | 0.59852 | 1.2713 | -18.4243 | 3 | -1.3355 | -1.9733 | 0.7929 | -5.9079 | -4.5885 | -2.5089 | -1.3038
42838.4274 | 614 | 22.88 | 22.8463 | 22.837 | 22.7485 | 22.3592 | 21.6769 | 22.6855 | 21.7392 | 22.3352 | 22.3406 | 22.3083 | 21.9612 | 21.1722 | 22.1544 | 21.593 | 21.7736 | 21.9249 | 21.0696 | 21.2336 | 22.0999 | 20.4944 | 21.8979 | 28.6769 | 21.9859 | 22.7974 | 34.0979 | 354.6245 | 304.524 | 396.4601 | 22.1438 | 22.5387 | 30.7998 | 22.0847 | 22.774 | 34.1564 | 162.2115 | 498.5245 |  | 259.8279 | 339.7971 | 305.4709 | 327.63 |  | 21.1925 | 26.3955 | 22.8577 | 27.085 | 32.0304 | 112.9478 | 261.4245 | 15.9879 | 18.2692 | 16.0755 | 22.1427 | 19.4092 | 46.2467 | 48.675 | 45.2516 | 21.7725 |  |  | 0.83871 | -0.23334 | -50.8064 | 0.3272 | 1.0535 | -184.1208 | 3.9495 | 2.1031 | 0.28635 | 0.63224 | 3.015 | 0.04652 | 0.048556 | 0.19256 | 22.1017 | 21.9609 | 22.132 | 22.196 | 22.0007 | 21.2918 | 20.1009 | 22.1678 | 22.345 | 22.3846 | 22.3251 | 21.9376 | 21.159 | 22.2556 | 155.6414 | 103.9678 | 110.5874 | 68.0007 | 60.4797 | 91.5429 | 60.6455 | 22.3099 | 22.0782 | 21.6719 | 22.0413 | 21.7965 | 21.9461 | 21.9417 | 22.0583 | 29.0116 | 128.515 | 351.2451 | 272.5553 | 229.1069 | 4.2004 | 2.4886 | 152.6338 | 21.8923 | 22.205 | 24.4333 | 21.5451 | 22.015 | 22.12 | 23.6458 | 44.3679 | 21.871 | 22.3228 | 30.5493 | 387.9063 | 705.9262 | 265.7767 | 264.6956 | 234.6955 |  | 133.8869 | 254.532 | 129.428 | 270.6267 | 198.4887 | 164.4734 |  | 167.7749 |  |  | 45.9287 | 82.3704 | 149.6086 | [5 empty] | 21.8844 | 228.924 | 21.7033 | 22.0912 | 81.472 | 21.2873 | 21.9083 | 68.2565 | 267.2278 | 516.2061 |  | 211.5808 | 379.8455 | 47.0662 | 192.9555 | 516.2041 | 168.2448 | 328.425 | 56.1375 | 237.6787 | 65.8914 | 265.162 | 22.2008 | 195.0318 | 346.5386 | 72.9591 | 194.839 | 387.5017 | 48.2488 | 187.2479 | 385.9457 | 46.1202 | 245.7844 | 87.9173 | 261.0293 | 62.9663 | 310.5157 | 8.9836 | 17.7811 | 3.0015 | 0.061604 | -27.2992 | 3.0948 | 1022.02 | 51.15 | 1.6515 | -0.58263 | -8.5972 | 0.68993 | 1.4055 | -18.5809 | 2.7214 | -1.2439 | -1.9858 | 0.80173 | -6.1191 | -4.8452 | -2.558 | -1.3184
42838.4274 | 615 | 22.8848 | 22.8462 | 22.8349 | 22.7502 | 22.3633 | 21.685 | 22.689 | 21.7389 | 22.3316 | 22.3462 | 22.3115 | 21.9629 | 21.1723 | 22.1547 | 21.5848 | 21.7659 | 21.9177 | 21.0635 | 21.2425 | 22.1012 | 20.4912 | 21.9092 | 28.7183 | 21.9826 | 22.8045 | 34.1788 | 356.6913 | 306.6661 | 399.2868 | 22.1407 | 22.5382 | 30.8524 | 22.089 | 22.7827 | 34.2333 | 163.7704 | 503.4308 |  | 262.2812 | 341.4857 | 307.4282 | 330.1691 |  | 21.2643 | 26.5577 | 22.9417 | 27.1978 | 32.142 | 117.752 | 261.4529 | 16.0295 | 18.2926 | 16.102 | 22.2159 | 19.4251 | 46.2511 | 48.6597 | 45.2443 | 21.7659 |  |  | 0.98327 | -0.096005 | -51.5062 | 0.66167 | 1.3623 | -185.2464 | 3.9666 | 1.7995 | 0.2774 | 0.55629 | 3.3022 | 0.04447 | 0.046297 | 0.13237 | 22.1082 | 21.9626 | 22.1408 | 22.1952 | 21.9992 | 21.2923 | 20.1 | 22.1675 | 22.347 | 22.3866 | 22.3328 | 21.9408 | 21.168 | 22.2558 | 156.8651 | 101.3615 | 107.0074 | 67.1694 | 60.1602 | 91.9579 | 60.8671 | 22.3085 | 22.0719 | 21.6751 | 22.0417 | 21.7979 | 21.952 | 21.9399 | 22.0594 | 29.0508 | 129.6347 | 354.0356 | 274.308 | 230.6744 | 6.0997 | 3.7494 | 154.8218 | 21.8938 | 22.2046 | 24.5241 | 21.5494 | 22.0163 | 22.1196 | 23.6627 | 44.6465 | 21.871 | 22.3252 | 30.6101 | 389.0428 | 709.1892 | 266.8035 | 265.856 | 232.0685 |  | 135.1484 | 254.1141 | 130.3564 | 273.5653 | 200.2691 | 165.7861 |  | 168.7058 |  |  | 46.3762 | 85.7425 | 151.1695 | [5 empty] | 21.8829 | 230.8644 | 21.6979 | 22.0931 | 82.2682 | 21.2849 | 21.9064 | 68.9266 | 269.9619 | 518.4134 |  | 213.1669 | 381.431 | 47.5983 | 194.7254 | 518.8509 | 170.2244 | 331.6969 | 56.8703 | 239.0224 | 66.7342 | 267.2004 | 22.3052 | 196.4591 | 348.6078 | 73.6265 | 196.7677 | 389.8067 | 48.8017 | 188.9599 | 388.196 | 46.622 | 247.2183 | 88.8468 | 262.7732 | 63.7152 | 312.875 | 9.6577 | 17.7585 | 3.0274 | 0.062033 | -27.2654 | 3.0948 | 1060.63 | 52.58 | 1.792 | -0.37382 | -8.6586 | 0.98138 | 1.6082 | -18.7532 | 2.7442 | -1.1165 | -1.9346 | 0.81216 | -6.2044 | -4.4209 | -2.5559 | -1.3143
42838.4274 | 616 | 22.8901 | 22.8485 | 22.8364 | 22.7532 | 22.3652 | 21.6893 | 22.695 | 21.7447 | 22.3397 | 22.3539 | 22.3171 | 21.9603 | 21.1808 | 22.1514 | 21.5945 | 21.7729 | 21.9171 | 21.0791 | 21.2476 | 22.1132 | 20.5013 | 21.9179 | 28.7619 | 21.9806 | 22.8204 | 34.256 | 359.3641 | 308.8839 | 402.4803 | 22.1396 | 22.5395 | 30.9087 | 22.0919 | 22.7854 | 34.3086 | 165.3201 | 508.4547 |  | 264.6936 | 343.2786 | 309.3938 | 330.5086 |  | 21.319 | 26.6903 | 23.0186 | 27.3156 | 32.2294 | 121.6987 | 262.6493 | 16.0231 | 18.3083 | 16.1786 | 22.2649 | 19.44 | 46.2402 | 48.645 | 45.2455 | 21.7867 |  |  | 1.1811 | -0.45808 | -52.4485 | 0.40014 | 1.6666 | -187.7073 | 3.1603 | 1.7095 | 0.20948 | 0.61168 | 3.3284 | 0.042496 | 0.04418 | 0.172 | 22.1144 | 21.9594 | 22.1526 | 22.1958 | 22.0088 | 21.2924 | 20.1063 | 22.1689 | 22.3551 | 22.3916 | 22.3344 | 21.9481 | 21.1712 | 22.2588 | 157.1818 | 100.9202 | 107.4844 | 68.5895 | 60.4553 | 92.4087 | 61.1376 | 22.3055 | 22.0749 | 21.6671 | 22.0362 | 21.7911 | 21.9499 | 21.9358 | 22.0668 | 29.1035 | 130.9174 | 356.0083 | 276.654 | 232.0295 | 4.2924 | 2.4217 | 155.7447 | 21.8993 | 22.2071 | 24.6361 | 21.5537 | 22.0176 | 22.1236 | 23.6811 | 44.9366 | 21.8704 | 22.337 | 30.6741 | 389.8267 | 714.704 | 267.6933 | 266.9515 | 233.2875 |  | 136.6054 | 252.9906 | 131.3831 | 275.6027 | 202.2444 | 166.2837 |  | 169.9483 |  |  | 46.8293 | 88.3561 | 153.031 | [5 empty] | 21.8872 | 232.9801 | 21.7093 | 22.0972 | 83.2673 | 21.2874 | 21.9093 | 69.5391 | 272.791 | 520.914 |  | 214.9351 | 383.7837 | 48.1095 | 196.4051 | 522.6924 | 172.2072 | 334.7131 | 57.632 | 240.3236 | 67.7855 | 270.9527 | 22.3686 | 197.4304 | 350.4382 | 74.2868 | 198.6968 | 393.3322 | 49.3834 | 190.6394 | 390.7539 | 47.0382 | 248.4614 | 89.8323 | 264.7871 | 64.6671 | 315.1936 | 8.4666 | 17.7335 | 3.0728 | 0.062519 | -27.324 | 3.0948 | 1118.27 | 51.17 | 1.9686 | -0.81674 | -8.7393 | 0.76334 | 1.7877 | -18.9724 | 2.4618 | -1.0872 | -1.8595 | 0.85827 | -6.1845 | -4.4416 | -2.4928 | -1.2972
42838.4274 | 617 | 22.8791 | 22.8535 | 22.8479 | 22.7519 | 22.3658 | 21.6909 | 22.6952 | 21.7442 | 22.3433 | 22.3458 | 22.3191 | 21.9669 | 21.174 | 22.1524 | 21.5889 | 21.7615 | 21.9147 | 21.0611 | 21.2353 | 22.1184 | 20.4885 | 21.921 | 28.7944 | 21.9815 | 22.8145 | 34.3153 | 361.7647 | 310.9576 | 401.0773 | 22.1418 | 22.5505 | 30.9692 | 22.0876 | 22.7896 | 34.401 | 166.8295 | 524.9075 |  | 267.2053 | 345.4216 | 311.8251 | 331.4158 |  | 21.4016 | 26.8851 | 23.1305 | 27.505 | 32.5098 | 124.691 | 264.6744 | 16.0156 | 18.3347 | 16.2456 | 22.3471 | 19.4574 | 46.2228 | 48.6261 | 45.2389 | 21.7987 |  |  | 0.90902 | -0.40682 | -53.2508 | 0.61173 | 1.5214 | -188.118 | 3.3568 | 1.7863 | 0.064506 | 0.75057 | 3.3667 | 0.040615 | 0.042509 | 0.23632 | 22.1096 | 21.9614 | 22.1501 | 22.201 | 22.0104 | 21.2942 | 20.1072 | 22.1705 | 22.3509 | 22.3908 | 22.3336 | 21.946 | 21.1679 | 22.2554 | 159.78 | 102.5078 | 106.7871 | 69.0403 | 61.4222 | 92.8908 | 61.3845 | 22.3186 | 22.0792 | 21.6684 | 22.0378 | 21.7927 | 21.9599 | 21.9374 | 22.0712 | 29.1537 | 132.0886 | 358.8229 | 279.6126 | 232.7539 | 3.9542 | 4.709 | 156.1028 | 21.8993 | 22.205 | 24.7421 | 21.556 | 22.0176 | 22.124 | 23.6904 | 45.2262 | 21.8732 | 22.346 | 30.7286 | 393.144 | 720.8074 | 269.0503 | 268.441 | 238.0124 |  | 138.0986 | 253.9471 | 132.4583 | 278.1637 | 204.302 | 167.2881 |  | 171.2676 |  |  | 47.3141 | 88.963 | 154.3679 | [5 empty] | 21.8872 | 235.4402 | 21.7035 | 22.0934 | 84.3134 | 21.2959 | 21.9041 | 70.2478 | 275.6447 | 521.2939 |  | 216.6813 | 386.0684 | 48.6848 | 197.9778 | 527.6402 | 174.4201 | 337.2624 | 58.3925 | 241.1052 | 68.6642 | 273.1835 | 22.4674 | 198.3116 | 352.6713 | 74.8799 | 200.5723 | 396.3615 | 50.0943 | 192.2924 | 393.9816 | 47.5355 | 249.8267 | 90.8458 | 266.7295 | 65.5542 | 318.5713 | 9.5464 | 17.7059 | 3.1084 | 0.062301 | -27.2349 | 3.0948 | 1159.65 | 53.04 | 1.7253 | -0.76994 | -8.8088 | 0.94413 | 1.7145 | -19.065 | 2.5467 | -1.1536 | -1.84 | 0.89476 | -6.4142 | -4.3346 | -2.4471 | -1.2672
42838.4274 | 618 | 22.8834 | 22.8626 | 22.8356 | 22.7575 | 22.3699 | 21.6873 | 22.6902 | 21.7487 | 22.3434 | 22.35 | 22.3204 | 21.9746 | 21.1843 | 22.1506 | 21.588 | 21.7569 | 21.907 | 21.0655 | 21.2346 | 22.1172 | 20.4817 | 21.9236 | 28.8459 | 21.9759 | 22.818 | 34.3824 | 363.016 | 313.327 | 398.3645 | 22.1351 | 22.5491 | 31.0209 | 22.0847 | 22.7972 | 34.4868 | 168.5139 | 547.5639 |  | 270.1401 | 347.77 | 314.6619 | 336.0867 |  | 21.4414 | 27.0501 | 23.2402 | 27.6441 | 32.6847 | 126.1765 | 266.9662 | 15.9929 | 18.3586 | 16.3057 | 22.4033 | 19.4616 | 46.218 | 48.6103 | 45.2328 | 21.8104 |  |  | 1.0871 | -0.52576 | -54.2891 | 0.37123 | 1.4004 | -188.1542 | 2.5196 | 1.7305 | 0.20559 | 0.63035 | 3.4765 | 0.03899 | 0.040641 | 0.24655 | 22.114 | 21.9641 | 22.1463 | 22.198 | 22.0103 | 21.2916 | 20.1057 | 22.1715 | 22.3491 | 22.3877 | 22.3307 | 21.9454 | 21.1733 | 22.2554 | 163.9973 | 108.4067 | 111.9154 | 71.5904 | 61.3892 | 93.3644 | 61.7872 | 22.3122 | 22.0847 | 21.6714 | 22.0383 | 21.7944 | 21.9576 | 21.9356 | 22.0752 | 29.2115 | 133.2529 | 362.1745 | 282.1586 | 234.0425 | 3.2404 | 3.1994 | 157.2835 | 21.9007 | 22.2082 | 24.8961 | 21.5558 | 22.0176 | 22.1295 | 23.7035 | 45.5275 | 21.8751 | 22.3583 | 30.7912 | 396.1487 | 724.0203 | 270.4991 | 269.992 | 240.5278 |  | 139.4377 | 254.0027 | 133.4623 | 281.2234 | 206.1887 | 168.5423 |  | 172.603 |  |  | 47.6571 | 90.5019 | 155.7887 | [5 empty] | 21.8806 | 237.7501 | 21.7074 | 22.0975 | 85.1211 | 21.2849 | 21.9035 | 70.9586 | 278.4589 | 523.1403 |  | 218.4317 | 389.4903 | 49.2788 | 199.9417 | 533.1876 | 176.59 | 339.8911 | 59.053 | 241.8912 | 69.5194 | 275.2888 | 22.5147 | 199.8893 | 355.2559 | 75.4559 | 202.5138 | 399.649 | 50.743 | 193.8137 | 397.621 | 48.1534 | 250.8682 | 91.9324 | 268.1752 | 66.5316 | 321.7123 | 8.7909 | 17.6786 | 3.1411 | 0.061938 | -27.2984 | 3.0948 | 1203.42 | 51.18 | 1.8829 | -0.87552 | -8.8967 | 0.73568 | 1.648 | -19.1024 | 2.2106 | -1.165 | -1.7984 | 0.90902 | -6.8249 | -4.8562 | -2.4973 | -1.253
42838.4274 | 619 | 22.8932 | 22.8524 | 22.8383 | 22.7571 | 22.3625 | 21.6839 | 22.6878 | 21.7414 | 22.3458 | 22.3538 | 22.3143 | 21.9659 | 21.1742 | 22.1514 | 21.592 | 21.7689 | 21.9142 | 21.0741 | 21.2375 | 22.1323 | 20.489 | 21.9456 | 28.9026 | 21.991 | 22.836 | 34.469 | 365.2393 | 315.7914 | 403.0065 | 22.1412 | 22.5672 | 31.0841 | 22.0852 | 22.8049 | 34.5811 | 170.2366 | 545.293 |  | 272.9602 | 349.4645 | 317.6301 | 336.5553 |  | 21.5116 | 27.2333 | 23.3569 | 27.8147 | 33.1653 | 130.0874 | 269.9767 | 15.9872 | 18.3843 | 16.3217 | 22.4708 | 19.4646 | 46.2089 | 48.5862 | 45.2131 | 21.8185 |  |  | 1.0812 | -0.10914 | -54.456 | 0.42379 | 2.1607 | -189.04 | 2.814 | 1.9644 | 0.20948 | 0.61713 | 3.4931 | 0.037416 | 0.039075 | 0.24931 | 22.1138 | 21.9671 | 22.1496 | 22.1968 | 22.0077 | 21.2963 | 20.1035 | 22.1731 | 22.3515 | 22.3825 | 22.3333 | 21.9405 | 21.1727 | 22.2563 | 159.4384 | 99.3493 | 110.2549 | 72.5102 | 64.0518 | 93.694 | 62.1063 | 22.3058 | 22.0739 | 21.6686 | 22.0331 | 21.7919 | 21.9583 | 21.933 | 22.0849 | 29.2616 | 134.4529 | 366.2015 | 284.9804 | 235.3885 | 3.2423 | 1.612 | 158.3634 | 21.9019 | 22.2148 | 25.0168 | 21.5536 | 22.0157 | 22.1391 | 23.7141 | 45.8306 | 21.8779 | 22.3615 | 30.8591 | 399.33 | 725.8033 | 272.2661 | 271.7098 | 241.0758 |  | 140.7728 | 254.195 | 134.501 | 283.9346 | 208.1007 | 169.1961 |  | 173.9545 |  |  | 48.1097 | 92.4495 | 156.349 | [5 empty] | 21.8792 | 240.3615 | 21.7044 | 22.0931 | 85.8163 | 21.2896 | 21.9016 | 71.5632 | 281.3903 | 523.685 |  | 220.2213 | 392.5613 | 49.8688 | 201.8896 | 537.8651 | 178.6608 | 343.4719 | 59.7514 | 243.2244 | 70.5554 | 277.4483 | 22.5468 | 201.1864 | 357.8291 | 76.0307 | 204.4629 | 401.5716 | 51.4182 | 195.4181 | 400.9746 | 48.8087 | 251.9339 | 93.003 | 269.7847 | 67.3865 | 323.8233 | 10.2953 | 17.6516 | 3.1828 | 0.061982 | -27.3653 | 3.0949 | 1218.5 | 52.04 | 1.8843 | -0.39903 | -8.9131 | 0.78629 | 2.0571 | -19.2408 | 2.3475 | -1.1218 | -1.759 | 0.93487 | -6.2781 | -4.6335 | -2.4286 | -1.2387
42838.4275 | 620 | 22.884 | 22.8495 | 22.8311 | 22.7487 | 22.3588 | 21.6874 | 22.6917 | 21.7418 | 22.3479 | 22.3433 | 22.3144 | 21.9618 | 21.1708 | 22.1505 | 21.5909 | 21.7757 | 21.9234 | 21.0681 | 21.2404 | 22.1333 | 20.4988 | 21.9675 | 28.9513 | 21.9929 | 22.8487 | 34.5377 | 368.1975 | 318.5906 | 408.8834 | 22.1453 | 22.5765 | 31.1457 | 22.1009 | 22.8163 | 34.6753 | 171.8713 | 537.4337 |  | 275.5679 | 351.3818 | 320.0504 | 337.5793 |  | 21.5929 | 27.4168 | 23.4631 | 27.9857 | 33.4107 | 134.0563 | 272.1883 | 16.0361 | 18.4075 | 16.329 | 22.5438 | 19.4868 | 46.2222 | 48.5802 | 45.2092 | 21.8218 |  |  | 0.77365 | -0.011237 | -55.855 | 0.51908 | 1.5674 | -191.7289 | 2.4138 | 2.036 | 0.17095 | 0.70567 | 3.6235 | 0.035806 | 0.037523 | 0.22611 | 22.1187 | 21.9695 | 22.1425 | 22.1958 | 22.0025 | 21.2904 | 20.1038 | 22.1679 | 22.3489 | 22.3778 | 22.3373 | 21.943 | 21.1668 | 22.249 | 153.7723 | 91.2111 | 104.1916 | 71.9329 | 64.4945 | 93.9491 | 62.3042 | 22.3164 | 22.0829 | 21.6817 | 22.0535 | 21.8101 | 21.9709 | 21.9426 | 22.0938 | 29.3182 | 135.715 | 371.8033 | 287.6939 | 235.555 | 3.5766 | 2.6429 | 159.9703 | 21.9004 | 22.2046 | 25.1042 | 21.553 | 22.012 | 22.1358 | 23.7268 | 46.1442 | 21.8751 | 22.3621 | 30.922 | 401.4376 | 730.6538 | 274.0873 | 273.4079 | 242.3385 |  | 142.2987 | 252.953 | 135.7164 | 287.7764 | 210.3935 | 169.3606 |  | 175.5599 |  |  | 48.7224 | 94.0683 | 157.9688 | [5 empty] | 21.8816 | 243.3752 | 21.705 | 22.0852 | 86.7357 | 21.2837 | 21.9 | 72.2037 | 284.4874 | 528.1841 |  | 222.1087 | 395.874 | 50.4592 | 203.9267 | 543.8483 | 181.1 | 346.9288 | 60.4712 | 244.6792 | 71.8322 | 280.0006 | 22.5969 | 202.1839 | 360.8067 | 76.656 | 206.6267 | 405.0082 | 52.1352 | 197.2043 | 404.7552 | 49.2861 | 253.195 | 94.1003 | 272.404 | 68.3417 | 327.1979 | 11.2415 | 17.6268 | 3.2312 | 0.06392 | -27.3678 | 3.0949 | 1218.75 | 52.3 | 1.6008 | -0.12807 | -9.0296 | 0.87047 | 1.7606 | -19.4723 | 2.1849 | -1.0898 | -1.672 | 0.95021 | -5.6173 | -3.9362 | -2.3791 | -1.1888
42838.4275 | 621 | 22.88 | 22.8492 | 22.8323 | 22.7518 | 22.3571 | 21.6807 | 22.6874 | 21.7364 | 22.3391 | 22.3449 | 22.3123 | 21.9639 | 21.1734 | 22.1472 | 21.58 | 21.7613 | 21.9227 | 21.0644 | 21.231 | 22.1374 | 20.4839 | 21.9695 | 28.9874 | 21.9797 | 22.8478 | 34.6016 | 370.7162 | 320.8728 | 411.8297 | 22.1451 | 22.5684 | 31.2019 | 22.1012 | 22.8184 | 34.7577 | 173.5272 | 544.2242 |  | 278.3022 | 353.4799 | 322.5286 | 343.2266 |  | 21.666 | 27.6166 | 23.5755 | 28.1434 | 33.6157 | 137.2258 | 273.3746 | 16.0895 | 18.4285 | 16.3594 | 22.613 | 19.4936 | 46.2352 | 48.5672 | 45.1994 | 21.8211 |  |  | 0.99576 | -0.077605 | -56.9386 | 0.25295 | 1.3636 | -192.8736 | 2.2923 | 1.8672 | 0.31651 | 0.77259 | 3.8162 | 0.034405 | 0.036092 | 0.22118 | 22.1268 | 21.9722 | 22.1431 | 22.2053 | 22.0039 | 21.2948 | 20.0988 | 22.1707 | 22.3601 | 22.3862 | 22.335 | 21.9447 | 21.1725 | 22.2596 | 149.3459 | 91.363 | 104.1059 | 71.3206 | 63.6508 | 94.198 | 62.5304 | 22.3114 | 22.0691 | 21.6661 | 22.0377 | 21.8041 | 21.9741 | 21.9367 | 22.0831 | 29.3771 | 137.1411 | 377.0877 | 291.0771 | 235.0996 | 3.3123 | 3.4305 | 162.2594 | 21.9003 | 22.2054 | 25.2153 | 21.5571 | 22.0158 | 22.1371 | 23.733 | 46.4654 | 21.8721 | 22.3689 | 30.9864 | 409.3878 | 735.116 | 275.889 | 274.9539 | 246.4402 |  | 143.7753 | 254.3158 | 136.7413 | 291.2616 | 212.462 | 170.1683 |  | 176.8666 |  |  | 49.2639 | 96.9447 | 160.3015 | [5 empty] | 21.8873 | 246.9875 | 21.705 | 22.0959 | 87.6815 | 21.2969 | 21.9106 | 72.9682 | 287.4327 | 533.5656 |  | 223.8951 | 397.6002 | 51.081 | 206.1236 | 551.2901 | 183.4256 | 350.9161 | 61.2384 | 246.1467 | 72.9467 | 283.2782 | 22.636 | 203.5133 | 362.429 | 77.3306 | 208.5783 | 408.349 | 52.824 | 198.8408 | 408.0045 | 49.9796 | 254.9626 | 95.2095 | 274.428 | 69.6782 | 330.8655 | 10.3877 | 17.5947 | 3.2778 | 0.064378 | -27.3789 | 3.0949 | 1229.2 | 51.76 | 1.8201 | -0.33669 | -9.1198 | 0.60785 | 1.6486 | -19.6062 | 2.1374 | -1.1386 | -1.6654 | 0.96425 | -5.095 | -3.8996 | -2.4567 | -1.1143
42838.4275 | 622 | 22.8796 | 22.8496 | 22.8298 | 22.7491 | 22.3611 | 21.683 | 22.6858 | 21.7315 | 22.3336 | 22.3423 | 22.3055 | 21.9572 | 21.1779 | 22.1446 | 21.5893 | 21.765 | 21.9244 | 21.0733 | 21.234 | 22.1449 | 20.4913 | 21.977 | 29.0309 | 21.9875 | 22.8542 | 34.681 | 373.2774 | 323.7831 | 415.3897 | 22.1429 | 22.5754 | 31.2617 | 22.0931 | 22.821 | 34.8598 | 175.2989 | 552.9883 |  | 280.9426 | 355.7623 | 324.9973 | 348.7902 |  | 21.7505 | 27.8497 | 23.7224 | 28.3671 | 34.1441 | 142.256 | 275.847 | 16.1028 | 18.4476 | 16.3298 | 22.686 | 19.506 | 46.2407 | 48.5609 | 45.197 | 21.8332 |  |  | 0.7224 | -0.10192 | -57.781 | 0.39751 | 1.8473 | -194.0479 | 2.268 | 2.4947 | 0.19411 | 0.55629 | 3.9202 | 0.033262 | 0.03484 | 0.22246 | 22.1376 | 21.969 | 22.1522 | 22.1907 | 22.0089 | 21.2937 | 20.1019 | 22.1732 | 22.3545 | 22.3953 | 22.33 | 21.9489 | 21.1658 | 22.2635 | 144.1804 | 94.6197 | 106.3754 | 71.7494 | 64.2539 | 94.4241 | 62.777 | 22.3082 | 22.0744 | 21.6763 | 22.0425 | 21.8015 | 21.9757 | 21.9425 | 22.0929 | 29.4256 | 138.4441 | 383.2842 | 295.6357 | 237.4927 | 3.3129 | 2.2625 | 163.8591 | 21.8937 | 22.2052 | 25.3237 | 21.5553 | 22.008 | 22.137 | 23.7329 | 46.7941 | 21.8697 | 22.3678 | 31.0544 | 417.5861 | 737.6969 | 277.598 | 276.3486 | 249.0424 |  | 145.2772 | 256.7329 | 137.7863 | 294.511 | 214.5384 | 171.3669 |  | 178.0926 |  |  | 49.8894 | 98.0174 | 161.986 | [5 empty] | 21.8867 | 250.2186 | 21.6974 | 22.0902 | 88.745 | 21.2828 | 21.9019 | 73.7976 | 290.4109 | 537.8356 |  | 225.7646 | 400.9704 | 51.75 | 208.2552 | 558.2872 | 185.6083 | 354.8874 | 62.1365 | 247.5438 | 74.2546 | 285.6114 | 22.714 | 204.6495 | 365.0719 | 77.9797 | 210.4127 | 413.0818 | 53.526 | 200.7577 | 411.5095 | 51.3645 | 256.6815 | 96.3862 | 276.5318 | 70.6824 | 333.3024 | 11.6387 | 17.5478 | 3.3251 | 0.065191 | -27.2826 | 3.0949 | 1242.14 | 52.8 | 1.5543 | -0.38599 | -9.1906 | 0.7623 | 1.9305 | -19.786 | 2.1391 | -1.1443 | -1.6872 | 0.98593 | -4.4934 | -4.1222 | -2.526 | -1.1241
42838.4275 | 623 | 22.8802 | 22.8487 | 22.8347 | 22.7513 | 22.3649 | 21.6836 | 22.6838 | 21.739 | 22.3353 | 22.343 | 22.3148 | 21.9565 | 21.1704 | 22.1509 | 21.5965 | 21.772 | 21.9325 | 21.0748 | 21.2439 | 22.1561 | 20.5008 | 22.0029 | 29.0816 | 21.998 | 22.8668 | 34.7643 | 375.8449 | 327.2846 | 418.9697 | 22.1455 | 22.588 | 31.323 | 22.0897 | 22.8317 | 34.954 | 177.0692 | 558.7777 |  | 283.686 | 358.9769 | 327.8649 | 350.8738 |  | 21.8432 | 28.035 | 23.8487 | 28.5668 | 34.6042 | 146.4375 | 277.363 | 16.1552 | 18.4722 | 16.2927 | 22.7501 | 19.5076 | 46.2297 | 48.5516 | 45.1856 | 21.8368 |  |  | 0.77694 | -0.28065 | -59.1616 | 0.20826 | 2.3506 | -195.7564 | 0.79866 | 1.9118 | 0.27292 | 0.78015 | 3.9745 | 0.031831 | 0.033498 | 0.19577 | 22.1261 | 21.9668 | 22.1558 | 22.2071 | 22.0108 | 21.2987 | 20.1085 | 22.1813 | 22.3582 | 22.3947 | 22.3392 | 21.9538 | 21.17 | 22.2567 | 141.4049 | 96.5356 | 101.2043 | 70.5199 | 63.7806 | 94.6335 | 62.927 | 22.3114 | 22.0756 | 21.6808 | 22.0421 | 21.7938 | 21.9815 | 21.9323 | 22.0928 | 29.4778 | 139.7791 | 388.8569 | 298.9702 | 240.851 | 2.5513 | 2.6273 | 164.8554 | 21.9015 | 22.2105 | 25.429 | 21.5528 | 22.0105 | 22.1293 | 23.7509 | 47.1295 | 21.8691 | 22.3733 | 31.1236 | 425.3431 | 741.0415 | 279.0879 | 277.8575 | 250.8006 |  | 147.0761 | 257.2192 | 139.0429 | 298.4362 | 216.9945 | 172.9278 |  | 179.7664 |  |  | 50.4639 | 99.606 | 164.664 | [5 empty] | 21.8791 | 253.8752 | 21.7076 | 22.0834 | 89.5847 | 21.2823 | 21.9036 | 74.6132 | 293.4979 | 543.9064 |  | 227.9492 | 405.0779 | 52.4509 | 210.3056 | 564.7019 | 187.9789 | 357.8711 | 63.0078 | 249.4315 | 75.9021 | 288.2133 | 22.8063 | 205.9159 | 369.0023 | 78.6355 | 212.4972 | 418.7838 | 54.2666 | 202.6797 | 414.7353 | 52.3651 | 258.6256 | 97.7062 | 279.2729 | 72.1889 | 336.4924 | 11.1108 | 17.5059 | 3.3789 | 0.064508 | -27.2545 | 3.0949 | 1250.56 | 51.42 | 1.616 | -0.64072 | -9.3026 | 0.55194 | 2.1886 | -19.9727 | 1.2757 | -1.1131 | -1.6459 | 1.0102 | -4.1594 | -3.5297 | -2.4983 | -1.1591
42838.4275 | 624 | 22.8839 | 22.8474 | 22.8362 | 22.7527 | 22.3609 | 21.6855 | 22.6885 | 21.7375 | 22.3379 | 22.336 | 22.3185 | 21.9624 | 21.1727 | 22.1503 | 21.5927 | 21.7655 | 21.9269 | 21.0693 | 21.2423 | 22.1579 | 20.4945 | 22.007 | 29.1282 | 21.9944 | 22.8728 | 34.8314 | 378.3578 | 330.2468 | 421.8232 | 22.145 | 22.5962 | 31.387 | 22.0942 | 22.8346 | 35.0498 | 178.8829 | 552.0641 |  | 286.2964 | 361.5817 | 330.5236 | 352.2083 |  | 21.9358 | 28.2452 | 23.9874 | 28.8232 | 34.8935 | 149.8465 | 279.0069 | 16.1922 | 18.4931 | 16.3156 | 22.8412 | 19.5211 | 46.2167 | 48.5462 | 45.1838 | 21.8367 |  |  | 0.56272 | -0.26225 | -59.9606 | 0.47899 | 1.637 | -197.4346 | 0.006177 | 2.4172 | 0.15305 | 0.65238 | 4.424 | 0.0307 | 0.032189 | 0.20622 | 22.1316 | 21.9634 | 22.1514 | 22.1952 | 22.0083 | 21.2926 | 20.1058 | 22.1729 | 22.3459 | 22.3889 | 22.3329 | 21.9495 | 21.1647 | 22.2535 | 136.1221 | 96.4212 | 102.8104 | 67.9148 | 62.7776 | 94.7648 | 63.1437 | 22.3049 | 22.0701 | 21.6788 | 22.0415 | 21.7953 | 21.9864 | 21.935 | 22.0968 | 29.5342 | 141.1733 | 394.06 | 301.5665 | 243.339 | 2.5487 | 3.0885 | 166.3585 | 21.9039 | 22.2063 | 25.5755 | 21.5557 | 22.0161 | 22.1369 | 23.7692 | 47.4687 | 21.8739 | 22.3781 | 31.1992 | 431.4671 | 740.9568 | 280.8587 | 279.5598 | 252.4959 |  | 148.737 | 260.1777 | 140.2158 | 300.6954 | 219.3389 | 174.4133 |  | 181.2477 |  |  | 51.0785 | 102.3386 | 166.9527 | [5 empty] | 21.8783 | 257.426 | 21.7039 | 22.0914 | 90.5628 | 21.2898 | 21.9063 | 75.4606 | 296.8006 | 552.8064 |  | 229.9347 | 409.6357 | 53.135 | 212.3294 | 570.477 | 190.2665 | 361.1474 | 64.0063 | 250.8754 | 77.2589 | 291.3452 | 22.9122 | 207.3669 | 371.8091 | 79.3514 | 214.7703 | 423.2652 | 54.9887 | 204.7904 | 417.8304 | 53.7211 | 260.3206 | 98.9599 | 281.8539 | 73.5603 | 340.0196 | 12.0613 | 17.4635 | 3.4344 | 0.065133 | -27.3195 | 3.0949 | 1280.19 | 51.62 | 1.3782 | -0.61958 | -9.3685 | 0.83734 | 1.8338 | -20.1394 | 0.11265 | -1.0859 | -1.6768 | 1.0757 | -3.5564 | -3.6822 | -2.4472 | -1.1671
42838.4275 | 625 | 22.8919 | 22.848 | 22.8329 | 22.7491 | 22.3516 | 21.6841 | 22.6844 | 21.7381 | 22.3398 | 22.3435 | 22.3031 | 21.9594 | 21.1686 | 22.1445 | 21.5877 | 21.7589 | 21.9244 | 21.0708 | 21.2365 | 22.1583 | 20.4896 | 22.0131 | 29.1688 | 21.9931 | 22.8691 | 34.9075 | 381.6724 | 333.2097 | 427.7027 | 22.1352 | 22.5933 | 31.4431 | 22.088 | 22.8303 | 35.1476 | 180.7735 | 562.8225 |  | 289.2612 | 365.1106 | 332.6157 | 357.5774 |  | 22.0368 | 28.4404 | 24.1497 | 29.0761 | 35.3243 | 153.015 | 280.6865 | 16.2185 | 18.5227 | 16.3972 | 22.9273 | 19.5417 | 46.1931 | 48.5358 | 45.1709 | 21.8378 |  |  | 0.80388 | -0.10455 | -61.0278 | 0.3916 | 1.2335 | -197.8545 | 1.0451 | 2.9337 | 0.23887 | 0.77952 | 4.4795 | 0.029445 | 0.031149 | 0.25053 | 22.1305 | 21.9576 | 22.1458 | 22.1965 | 22.0057 | 21.2861 | 20.1022 | 22.1683 | 22.3462 | 22.3875 | 22.3271 | 21.9412 | 21.1633 | 22.2501 | 131.1101 | 91.3984 | 101.5055 | 68.0475 | 62.2164 | 94.8714 | 63.3442 | 22.3142 | 22.0786 | 21.6878 | 22.0509 | 21.8018 | 21.9985 | 21.9432 | 22.1078 | 29.604 | 142.7805 | 398.6207 | 304.48 | 246.248 | 2.3718 | 2.5251 | 168.8373 | 21.9057 | 22.2118 | 25.7393 | 21.5554 | 22.0187 | 22.1427 | 23.7836 | 47.8143 | 21.878 | 22.3884 | 31.2705 | 434.9443 | 739.6636 | 282.6503 | 281.3513 | 255.0969 |  | 150.3398 | 261.8533 | 141.3364 | 304.0447 | 221.6073 | 175.1527 |  | 182.5825 |  |  | 51.6428 | 105.2203 | 169.039 | [5 empty] | 21.8862 | 260.644 | 21.7037 | 22.0956 | 91.7143 | 21.2878 | 21.9038 | 76.4079 | 300.1226 | 561.3322 |  | 231.8637 | 413.2792 | 53.844 | 214.3475 | 576.0644 | 192.6927 | 365.777 | 65.3733 | 251.6585 | 78.7044 | 294.4167 | 23.0096 | 208.8608 | 375.0212 | 80.1189 | 217.3152 | 428.1957 | 55.7781 | 207.3372 | 421.5194 | 54.9317 | 262.0597 | 100.3515 | 284.6362 | 74.84 | 343.5354 | 10.5387 | 17.423 | 3.4884 | 0.065416 | -27.2832 | 3.0949 | 1297.23 | 52.14 | 1.6542 | -0.39132 | -9.4545 | 0.75735 | 1.5978 | -20.2362 | 1.4707 | -1.0862 | -1.6742 | 1.1075 | -2.9864 | -3.5132 | -2.504 | -1.1772
42838.4275 | 626 | 22.889 | 22.8428 | 22.8328 | 22.7459 | 22.3559 | 21.6784 | 22.6805 | 21.7372 | 22.3395 | 22.3381 | 22.3081 | 21.9558 | 21.1702 | 22.1379 | 21.5895 | 21.7583 | 21.9203 | 21.0675 | 21.2366 | 22.1565 | 20.4904 | 22.0292 | 29.2155 | 21.9857 | 22.873 | 34.9848 | 385.6116 | 336.648 | 434.9572 | 22.155 | 22.6051 | 31.5263 | 22.0965 | 22.8642 | 35.2735 | 182.9461 | 591.026 |  | 292.629 | 367.8659 | 335.6363 | 362.2496 |  | 22.1405 | 28.6401 | 24.3101 | 29.3462 | 35.8777 | 156.4212 | 281.7697 | 16.2746 | 18.5563 | 16.4531 | 23.0134 | 19.5459 | 46.1739 | 48.5153 | 45.161 | 21.8386 |  |  | 0.86434 | -0.13937 | -62.6883 | 0.59136 | 1.6081 | -197.8026 | 0.96163 | 2.4132 | 0.3313 | 0.6379 | 4.571 | 0.028442 | 0.030048 | 0.27947 | 22.1331 | 21.9549 | 22.1437 | 22.1993 | 22.0009 | 21.2831 | 20.1035 | 22.1709 | 22.343 | 22.3872 | 22.3262 | 21.9339 | 21.1641 | 22.2448 | 127.111 | 89.826 | 101.4769 | 68.0082 | 62.2771 | 94.9838 | 63.5415 | 22.3112 | 22.0723 | 21.6751 | 22.0403 | 21.8024 | 21.9955 | 21.9332 | 22.1025 | 29.6456 | 144.4651 | 404.4095 | 308.5454 | 248.3406 | 2.3116 | 3.8712 | 169.8484 | 21.8939 | 22.2063 | 25.8774 | 21.5513 | 22.0148 | 22.1395 | 23.7904 | 48.1645 | 21.8817 | 22.3901 | 31.3378 | 441.7809 | 738.5806 | 284.3006 | 283.0624 | 260.1811 |  | 152.0566 | 262.4273 | 142.6026 | 306.949 | 224.1634 | 176.9995 |  | 184.1429 |  |  | 52.2734 | 107.6329 | 171.8492 | [5 empty] | 21.8833 | 264.2613 | 21.6945 | 22.0864 | 93.2307 | 21.2796 | 21.9059 | 77.4136 | 303.5035 | 570.3754 |  | 233.9969 | 416.413 | 54.5999 | 216.399 | 581.3181 | 195.1911 | 370.6311 | 66.7983 | 252.9255 | 80.3738 | 297.1805 | 23.1225 | 210.3488 | 378.5039 | 80.9328 | 219.7073 | 433.6904 | 56.5698 | 209.9639 | 426.1047 | 56.0652 | 264.4216 | 101.9257 | 288.3468 | 76.3693 | 347.6427 | 11.3089 | 17.3765 | 3.5439 | 0.065677 | -27.2778 | 3.0949 | 1330.7 | 51.79 | 1.7241 | -0.45197 | -9.5855 | 0.93099 | 1.8316 | -20.3142 | 1.4164 | -1.15 | -1.6344 | 1.1686 | -2.5283 | -3.4864 | -2.527 | -1.1608
42838.4275 | 627 | 22.882 | 22.8565 | 22.834 | 22.7578 | 22.3661 | 21.6839 | 22.6827 | 21.7374 | 22.3377 | 22.3402 | 22.3113 | 21.9673 | 21.1728 | 22.1505 | 21.5886 | 21.7624 | 21.92 | 21.0657 | 21.2403 | 22.1693 | 20.492 | 22.0471 | 29.2671 | 21.9825 | 22.8861 | 35.0666 | 389.4735 | 340.7397 | 437.7243 | 22.1409 | 22.6129 | 31.5804 | 22.093 | 22.8558 | 35.393 | 184.9846 | 591.7669 |  | 295.8127 | 370.2483 | 338.4744 | 364.3194 |  | 22.2652 | 28.8844 | 24.4639 | 29.6024 | 37.0274 | 161.1324 | 283.9274 | 16.3107 | 18.5801 | 16.657 | 23.1055 | 19.5594 | 46.1531 | 48.5044 | 45.1454 | 21.8376 |  |  | 0.90968 | -0.58753 | -64.0893 | 0.61305 | 2.1252 | -197.8847 | -0.14299 | 2.2443 | 0.34862 | 0.62133 | 4.4813 | 0.027535 | 0.029179 | 0.25708 | 22.1348 | 21.9571 | 22.1516 | 22.2006 | 22.005 | 21.2883 | 20.1005 | 22.1665 | 22.3446 | 22.3825 | 22.3277 | 21.9464 | 21.164 | 22.2463 | 123.6579 | 91.7925 | 107.2593 | 68.7849 | 63.1973 | 95.0951 | 63.8472 | 22.3095 | 22.0747 | 21.6778 | 22.0469 | 21.8004 | 22.0079 | 21.9457 | 22.1061 | 29.7122 | 146.1163 | 413.1009 | 312.1897 | 250.5399 | 3.7846 | 4.0484 | 170.6614 | 21.8888 | 22.2021 | 26.0103 | 21.5547 | 22.0122 | 22.1427 | 23.7983 | 48.5312 | 21.8734 | 22.3955 | 31.4076 | 446.6083 | 738.4637 | 286.0703 | 284.7094 | 261.842 |  | 153.8723 | 267.7234 | 143.9754 | 310.192 | 226.9568 | 179.8992 |  | 185.7742 |  |  | 52.9637 | 109.6383 | 174.4823 | [5 empty] | 21.8849 | 268.3806 | 21.6973 | 22.0905 | 94.8708 | 21.2868 | 21.9033 | 78.45 | 307.0783 | 582.8748 |  | 236.1307 | 419.2613 | 55.351 | 218.5421 | 586.9761 | 198.0766 | 374.5461 | 67.9762 | 255.0047 | 82.2004 | 300.3055 | 23.266 | 212.0927 | 381.7802 | 81.806 | 222.1396 | 440.2171 | 57.4087 | 212.4584 | 430.4753 | 57.0377 | 266.5686 | 103.5687 | 292.3239 | 78.2147 | 352.1257 | 12.6339 | 17.3351 | 3.6094 | 0.066258 | -27.325 | 3.0949 | 1378.86 | 52.79 | 1.7722 | -0.92835 | -9.6959 | 0.94829 | 2.1172 | -20.4296 | -0.54916 | -1.1138 | -1.7209 | 1.2347 | -2.131 | -4.0923 | -2.4837 | -1.1486
42838.4275 | 628 | 22.8793 | 22.8538 | 22.8342 | 22.7576 | 22.3621 | 21.6863 | 22.6845 | 21.7401 | 22.3413 | 22.3421 | 22.3149 | 21.9649 | 21.174 | 22.1518 | 21.588 | 21.7588 | 21.918 | 21.0687 | 21.2444 | 22.1762 | 20.4903 | 22.0608 | 29.3141 | 21.9901 | 22.8935 | 35.1429 | 393.8761 | 344.8799 | 444.8027 | 22.1493 | 22.617 | 31.6461 | 22.0962 | 22.8658 | 35.5035 | 187.0392 | 591.7831 |  | 298.8902 | 372.7114 | 341.1349 | 370.03 |  | 22.3911 | 29.098 | 24.5977 | 29.7642 | 37.9285 | 164.7151 | 286.3802 | 16.3257 | 18.6085 | 16.772 | 23.1858 | 19.5701 | 46.1257 | 48.502 | 45.1401 | 21.8523 |  |  | 0.58638 | -0.29642 | -64.9488 | 0.76484 | 2.1614 | -197.8282 | -0.92824 | 2.7234 | 0.26144 | 0.79819 | 5.0805 | 0.026707 | 0.028379 | 0.24133 | 22.1356 | 21.9605 | 22.1491 | 22.2026 | 22.0026 | 21.2891 | 20.1021 | 22.1691 | 22.3457 | 22.3821 | 22.3288 | 21.9399 | 21.1704 | 22.2515 | 124.3401 | 97.2196 | 110.2652 | 70.5877 | 63.133 | 95.2825 | 64.1339 | 22.3114 | 22.072 | 21.6784 | 22.0359 | 21.7989 | 22.0005 | 21.9388 | 22.1157 | 29.7653 | 147.8654 | 421.7654 | 315.6222 | 252.6309 | 1.6283 | 3.5328 | 171.3083 | 21.8977 | 22.2139 | 26.1409 | 21.5569 | 22.0126 | 22.1478 | 23.8139 | 48.8958 | 21.8747 | 22.405 | 31.4844 | 450.1575 | 738.7439 | 287.9369 | 286.3834 | 263.3803 |  | 155.5744 | 271.7329 | 145.2367 | 313.3679 | 229.6413 | 181.9717 |  | 187.2542 |  |  | 53.7252 | 112.035 | 176.6583 | [5 empty] | 21.8833 | 272.9819 | 21.7023 | 22.0943 | 96.5053 | 21.2912 | 21.906 | 79.5656 | 311.0893 | 595.8354 |  | 238.3189 | 422.6891 | 56.0732 | 220.7821 | 592.8407 | 201.1468 | 379.1729 | 69.0964 | 257.3886 | 84.1746 | 303.5711 | 23.4137 | 214.0196 | 385.1826 | 82.7344 | 224.7184 | 447.4187 | 58.253 | 214.8599 | 434.6395 | 58.3114 | 268.5719 | 105.8775 | 296.2768 | 80.0981 | 357.1608 | 13.3987 | 17.293 | 3.6715 | 0.066548 | -27.3547 | 3.0949 | 1403.88 | 51.19 | 1.4299 | -0.65964 | -9.7641 | 1.0596 | 2.1439 | -20.5107 | -1.405 | -1.079 | -1.7764 | 1.2978 | -2.1839 | -4.3919 | -2.5402 | -1.1287
42838.4276 | 629 | 22.8884 | 22.8579 | 22.8383 | 22.7581 | 22.3605 | 21.6835 | 22.682 | 21.7473 | 22.3438 | 22.3427 | 22.3183 | 21.9601 | 21.176 | 22.155 | 21.594 | 21.7585 | 21.9266 | 21.0685 | 21.2427 | 22.1768 | 20.4878 | 22.0725 | 29.3642 | 21.9951 | 22.9049 | 35.2223 | 398.2941 | 349.818 | 452.3642 | 22.148 | 22.6214 | 31.7146 | 22.0976 | 22.8765 | 35.6218 | 189.1856 | 606.5601 |  | 302.3403 | 375.3708 | 344.2587 | 376.1277 |  | 22.5354 | 29.3384 | 24.7785 | 29.9811 | 39.2029 | 169.1369 | 288.6424 | 16.3508 | 18.6399 | 16.8479 | 23.2871 | 19.5837 | 46.107 | 48.4955 | 45.1288 | 21.8548 |  |  | 0.63829 | 0.093903 | -66.3419 | 0.50791 | 2.5031 | -197.8131 | 0.68958 | 2.8095 | 0.34862 | 0.71322 | 5.0501 | 0.025946 | 0.027487 | 0.2189 | 22.1502 | 21.9653 | 22.1493 | 22.2014 | 22.0098 | 21.2939 | 20.101 | 22.1699 | 22.3507 | 22.3873 | 22.3349 | 21.9413 | 21.162 | 22.2498 | 122.5857 | 96.0143 | 109.5218 | 70.7527 | 63.4126 | 95.3844 | 64.4033 | 22.3117 | 22.0767 | 21.6837 | 22.0318 | 21.8005 | 22.0024 | 21.9315 | 22.1223 | 29.8082 | 149.6806 | 432.2637 | 319.704 | 259.3974 | 2.1595 | 2.5481 | 172.6821 | 21.9 | 22.2098 | 26.2777 | 21.556 | 22.016 | 22.1437 | 23.8291 | 49.2766 | 21.8859 | 22.4058 | 31.5691 | 454.1237 | 740.1691 | 289.6515 | 288.1234 | 265.85 |  | 157.3572 | 273.752 | 146.5597 | 319.6044 | 232.57 | 183.9658 |  | 188.8733 |  |  | 54.4996 | 114.4983 | 178.7619 | [5 empty] | 21.8782 | 278.911 | 21.7049 | 22.0902 | 98.277 | 21.2849 | 21.9027 | 80.6495 | 315.3445 | 608.8794 |  | 240.4918 | 425.0654 | 56.8855 | 223.0482 | 598.1418 | 204.5416 | 384.5196 | 70.7405 | 259.9732 | 86.3929 | 306.9694 | 23.5529 | 216.0264 | 389.0192 | 83.7683 | 227.5721 | 455.4452 | 59.0854 | 217.1593 | 440.4538 | 59.937 | 270.9563 | 108.0939 | 300.4384 | 82.1001 | 361.649 | 15.6199 | 17.2372 | 3.7311 | 0.067172 | -27.3647 | 3.0949 | 1450.78 | 52.79 | 1.4997 | 0.37142 | -9.8722 | 0.8638 | 2.3188 | -20.6133 | 1.2171 | -1.0661 | -1.7737 | 1.2911 | -1.9765 | -4.277 | -2.6022 | -1.2353
42838.4276 | 630 | 22.8851 | 22.8535 | 22.8347 | 22.7575 | 22.3575 | 21.6877 | 22.6833 | 21.7432 | 22.34 | 22.3405 | 22.3119 | 21.9641 | 21.1747 | 22.1485 | 21.5864 | 21.7545 | 21.9282 | 21.055 | 21.2382 | 22.1755 | 20.4831 | 22.0873 | 29.4088 | 21.9919 | 22.9079 | 35.3036 | 404.7196 | 355.2594 | 464.6072 | 22.1452 | 22.6286 | 31.7827 | 22.0946 | 22.8838 | 35.746 | 191.3859 | 616.0527 |  | 305.7697 | 378.8901 | 348.0986 | 380.9594 |  | 22.6748 | 29.6244 | 24.9396 | 30.2293 | 40.2419 | 173.6803 | 291.8761 | 16.4009 | 18.6643 | 16.8815 | 23.3755 | 19.5896 | 46.0743 | 48.485 | 45.1201 | 21.8508 |  |  | 0.64157 | -0.092717 | -67.8907 | 0.15701 | 2.1666 | -197.8755 | -0.67657 | 3.1623 | 0.54731 | 0.8798 | 5.7867 | 0.025245 | 0.026725 | 0.17485 | 22.1468 | 21.9622 | 22.1491 | 22.199 | 22.0144 | 21.2918 | 20.0981 | 22.1724 | 22.3475 | 22.3867 | 22.3287 | 21.9413 | 21.1642 | 22.252 | 122.9064 | 94.1674 | 104.2654 | 70.0442 | 64.5795 | 95.4986 | 64.5861 | 22.3206 | 22.077 | 21.6792 | 22.0427 | 21.8038 | 22.023 | 21.9378 | 22.1268 | 29.8908 | 151.8243 | 440.85 | 324.4466 | 266.5116 | 2.9606 | 2.7168 | 176.2157 | 21.8901 | 22.2037 | 26.4518 | 21.5515 | 22.0096 | 22.1472 | 23.8373 | 49.6643 | 21.881 | 22.408 | 31.6389 | 461.8785 | 741.5067 | 291.8424 | 290.0333 | 270.8625 |  | 159.6052 | 278.4257 | 148.1793 | 327.489 | 236.2701 | 186.6852 |  | 190.7063 |  |  | 55.3817 | 117.1362 | 181.6417 | [5 empty] | 21.8777 | 285.4962 | 21.7124 | 22.09 | 100.0716 | 21.2849 | 21.9035 | 81.8242 | 319.6891 | 624.0049 |  | 242.8193 | 428.3709 | 57.7422 | 225.6948 | 602.0738 | 208.2143 | 392.2018 | 72.8226 | 262.5662 | 89.2738 | 310.5692 | 23.6535 | 218.0465 | 393.7722 | 85.099 | 230.6365 | 463.2872 | 60.0774 | 219.6707 | 447.3198 | 61.8333 | 273.5432 | 110.6756 | 304.2401 | 84.3567 | 365.1764 | 16.3406 | 17.1786 | 3.7944 | 0.06824 | -27.3267 | 3.0949 | 1504.41 | 51.63 | 1.5162 | -0.36924 | -9.9915 | 0.48049 | 2.1684 | -20.7221 | -1.2117 | -1.1019 | -1.8312 | 1.2846 | -1.9981 | -3.6711 | -2.6256 | -1.3363
42838.4276 | 631 | 22.8742 | 22.8466 | 22.8334 | 22.7519 | 22.3571 | 21.6874 | 22.6843 | 21.7346 | 22.3357 | 22.3395 | 22.3129 | 21.9579 | 21.1704 | 22.1409 | 21.5806 | 21.7502 | 21.9183 | 21.0576 | 21.2361 | 22.1846 | 20.4877 | 22.0978 | 29.4595 | 21.983 | 22.9132 | 35.3836 | 412.3099 | 359.5312 | 478.7868 | 22.1456 | 22.6314 | 31.8443 | 22.092 | 22.8827 | 35.8813 | 193.605 | 625.1816 |  | 309.2087 | 382.4651 | 351.6004 | 381.3121 |  | 22.8054 | 29.8779 | 25.1072 | 30.5079 | 41.7582 | 177.6439 | 294.7835 | 16.4405 | 18.6873 | 16.8518 | 23.4711 | 19.5973 | 46.049 | 48.4835 | 45.115 | 21.8908 |  |  | 0.57981 | -0.028977 | -69.1333 | 0.36005 | 2.9644 | -197.8782 | -1.2134 | 3.2359 | 0.18886 | 0.93099 | 5.8445 | 0.024614 | 0.025981 | 0.1915 | 22.1574 | 21.9665 | 22.1511 | 22.201 | 22.0019 | 21.2926 | 20.1037 | 22.1765 | 22.3542 | 22.3861 | 22.3344 | 21.9416 | 21.1629 | 22.2592 | 123.2109 | 92.6973 | 102.0634 | 70.2165 | 64.972 | 95.6161 | 64.7549 | 22.3175 | 22.0754 | 21.6888 | 22.0437 | 21.8075 | 22.0308 | 21.943 | 22.1308 | 29.9494 | 153.9855 | 448.835 | 329.6887 | 271.6208 | 2.0616 | 2.6817 | 178.4868 | 21.9011 | 22.2211 | 26.6267 | 21.5583 | 22.0123 | 22.155 | 23.8523 | 50.0633 | 21.8857 | 22.4253 | 31.7213 | 469.7313 | 742.6667 | 293.6441 | 291.9244 | 277.0445 |  | 161.6301 | 281.8145 | 149.6212 | 336.1711 | 239.6906 | 189.3108 |  | 192.4349 |  |  | 56.2519 | 120.1315 | 185.212 | [5 empty] | 21.8801 | 291.9929 | 21.7095 | 22.0866 | 102.1449 | 21.2877 | 21.9054 | 83.2025 | 324.4455 | 641.8783 |  | 245.2389 | 434.5174 | 58.612 | 228.6046 | 606.8807 | 212.5886 | 401.4893 | 74.5034 | 265.4453 | 91.7071 | 314.7668 | 23.792 | 220.064 | 398.3281 | 86.5245 | 234.2316 | 470.3811 | 61.1735 | 222.426 | 451.142 | 64.2404 | 275.7769 | 113.5098 | 308.5489 | 87.3057 | 370.4751 | 17.7463 | 17.1273 | 3.8581 | 0.069118 | -27.3144 | 3.0949 | 1517.38 | 52.03 | 1.4551 | -0.20651 | -10.0868 | 0.72793 | 2.5476 | -20.814 | -1.6299 | -1.1799 | -1.8607 | 1.242 | -2.0175 | -3.4062 | -2.5229 | -1.3803
42838.4276 | 632 | 22.8827 | 22.8533 | 22.8457 | 22.7615 | 22.3649 | 21.6914 | 22.6881 | 21.7363 | 22.3427 | 22.3431 | 22.3193 | 21.9563 | 21.1764 | 22.1395 | 21.587 | 21.7701 | 21.9214 | 21.0614 | 21.2497 | 22.1943 | 20.4922 | 22.1168 | 29.5097 | 21.9964 | 22.9146 | 35.4696 | 419.6991 | 365.2203 | 494.7985 | 22.143 | 22.6377 | 31.9098 | 22.0954 | 22.888 | 36.0199 | 195.8312 | 637.4075 |  | 312.9832 | 386.4456 | 354.7999 | 382.0995 |  | 23.0184 | 30.2163 | 25.3548 | 30.9009 | 42.992 | 182.6266 | 297.4045 | 16.4736 | 18.732 | 16.7772 | 23.5972 | 19.6008 | 46.0287 | 48.4878 | 45.1154 | 21.903 |  |  | 1.2724 | -0.042121 | -70.7485 | 0.23389 | 2.5773 | -197.8223 | -1.0393 | 3.3194 | 0.2486 | 0.98953 | 6.2174 | 0.02365 | 0.025102 | 0.24105 | 22.1558 | 21.9614 | 22.1481 | 22.197 | 21.9983 | 21.2784 | 20.0996 | 22.1715 | 22.3502 | 22.382 | 22.3303 | 21.9406 | 21.1598 | 22.2502 | 118.27 | 91.0937 | 100.2998 | 71.6511 | 65.3566 | 95.6427 | 64.9234 | 22.3169 | 22.0755 | 21.6794 | 22.0497 | 21.8084 | 22.0301 | 21.9368 | 22.133 | 30.0049 | 156.217 | 460.4682 | 336.078 | 276.3997 | 1.9509 | 3.8259 | 182.005 | 21.8966 | 22.2043 | 26.8251 | 21.5533 | 22.0113 | 22.153 | 23.8633 | 50.4656 | 21.8795 | 22.4286 | 31.8027 | 482.1081 | 744.3643 | 295.7368 | 293.9221 | 282.9876 |  | 163.9323 | 284.4803 | 151.1268 | 344.4138 | 243.3087 | 192.3321 |  | 194.3938 |  |  | 57.3062 | 124.3234 | 189.8758 | [5 empty] | 21.8855 | 299.1031 | 21.7075 | 22.0892 | 104.1984 | 21.2874 | 21.9061 | 84.6164 | 329.6478 | 657.671 |  | 247.8786 | 440.6382 | 59.5833 | 231.577 | 611.8661 | 217.0566 | 409.1348 | 76.3861 | 268.6641 | 94.7208 | 320.9109 | 23.9754 | 222.0401 | 402.2133 | 88.0205 | 238.1779 | 481.6526 | 62.3246 | 225.8993 | 457.4196 | 67.0533 | 280.2123 | 116.9025 | 314.1161 | 89.3213 | 378.2999 | 18.0529 | 17.0664 | 3.9149 | 0.069619 | -27.2886 | 3.0949 | 1557.05 | 52.87 | 2.1784 | -0.24912 | -10.2096 | 0.58702 | 2.3885 | -20.9257 | -1.5167 | -1.2377 | -1.867 | 1.2254 | -1.4653 | -3.19 | -2.4313 | -1.4113
42838.4276 | 633 | 22.8865 | 22.8556 | 22.8316 | 22.7559 | 22.3645 | 21.6842 | 22.6855 | 21.7439 | 22.3308 | 22.3446 | 22.31 | 21.9648 | 21.1678 | 22.1528 | 21.5919 | 21.7731 | 21.9306 | 21.0745 | 21.2606 | 22.2081 | 20.5023 | 22.1481 | 29.5717 | 21.999 | 22.9307 | 35.5646 | 430.1446 | 371.9961 | 515.6567 | 22.1462 | 22.6359 | 31.9936 | 22.0987 | 22.9006 | 36.1843 | 198.4969 | 634.9814 |  | 317.0117 | 390.9724 | 359.5213 | 392.5115 |  | 23.1625 | 30.5278 | 25.5838 | 31.2426 | 43.4704 | 186.2253 | 300.2609 | 16.4317 | 18.7545 | 16.8014 | 23.703 | 19.6162 | 46.0075 | 48.4763 | 45.1331 | 21.9139 |  |  | 0.57783 | -0.12886 | -71.5844 | 0.31143 | 2.7626 | -197.844 | -0.86976 | 3.7728 | 0.32605 | 1.0193 | 6.7828 | 0.022805 | 0.024308 | 0.26662 | 22.1563 | 21.9602 | 22.1472 | 22.1978 | 21.9997 | 21.2828 | 20.0961 | 22.1662 | 22.345 | 22.3817 | 22.3292 | 21.9376 | 21.1599 | 22.2437 | 113.8498 | 92.0976 | 98.4752 | 73.5085 | 66.5002 | 95.6561 | 65.0944 | 22.3208 | 22.0784 | 21.6816 | 22.0535 | 21.8122 | 22.0315 | 21.9383 | 22.1431 | 30.0653 | 158.6159 | 473.7783 | 343.1157 | 280.9103 | 2.5603 | 2.8102 | 184.8823 | 21.901 | 22.2033 | 27.0576 | 21.5524 | 22.0161 | 22.1552 | 23.8798 | 50.8839 | 21.8829 | 22.4301 | 31.8741 | 496.531 | 746.7072 | 298.3281 | 296.1883 | 288.9302 |  | 166.7419 | 290.3251 | 152.9597 | 354.0891 | 247.7521 | 195.837 |  | 196.7312 |  |  | 58.4205 | 127.4735 | 195.0061 | [5 empty] | 21.8817 | 307.4192 | 21.7025 | 22.0917 | 106.4033 | 21.2748 | 21.9008 | 86.0265 | 334.7447 | 673.728 |  | 250.8163 | 448.028 | 60.6716 | 234.9635 | 618.6087 | 221.5834 | 416.0826 | 79.9277 | 273.1295 | 98.4335 | 327.6749 | 24.1482 | 224.159 | 405.268 | 89.5307 | 242.3353 | 495.133 | 63.4591 | 229.7868 | 463.2228 | 70.232 | 284.4542 | 120.3188 | 319.8624 | 92.6517 | 383.5861 | 18.6951 | 17.0073 | 3.9748 | 0.069728 | -27.2706 | 3.095 | 1628.16 | 51.78 | 1.4878 | -0.43595 | -10.275 | 0.67773 | 2.4826 | -21.0093 | -1.393 | -1.271 | -1.9465 | 1.2207 | -0.97251 | -2.9668 | -2.5835 | -1.4266
42838.4276 | 634 | 22.8807 | 22.8486 | 22.833 | 22.7543 | 22.3586 | 21.6856 | 22.6878 | 21.74 | 22.3382 | 22.3409 | 22.3128 | 21.9605 | 21.1732 | 22.1453 | 21.5927 | 21.7632 | 21.9269 | 21.0695 | 21.2365 | 22.2033 | 20.4981 | 22.1633 | 29.6107 | 21.9971 | 22.9374 | 35.6472 | 439.3559 | 378.3198 | 529.5222 | 22.1518 | 22.6478 | 32.0743 | 22.1085 | 22.9148 | 36.3319 | 201.3219 | 649.1008 |  | 321.2713 | 395.6155 | 364.3863 | 401.9305 |  | 23.355 | 30.9335 | 25.8804 | 31.6875 | 47.8742 | 189.3039 | 303.9892 | 16.4176 | 18.7982 | 16.9248 | 23.8447 | 19.6274 | 45.9797 | 48.4733 | 45.1378 | 21.9104 |  |  | 0.91757 | -0.44822 | -73.1766 | 0.45731 | 2.827 | -197.8624 | -1.7253 | 3.8622 | 0.42938 | 0.9226 | 7.3885 | 0.022179 | 0.023581 | 0.25953 | 22.162 | 21.9704 | 22.1505 | 22.2054 | 22.0096 | 21.292 | 20.1003 | 22.171 | 22.3476 | 22.3835 | 22.3348 | 21.9432 | 21.1631 | 22.2506 | 113.5656 | 90.5369 | 99.6572 | 74.9651 | 67.0094 | 95.7204 | 65.2443 | 22.315 | 22.0819 | 21.6776 | 22.0342 | 21.8028 | 22.0332 | 21.9285 | 22.1359 | 30.1176 | 161.2205 | 489.2453 | 351.101 | 287.0279 | 1.5394 | 2.777 | 188.0026 | 21.9039 | 22.2032 | 27.304 | 21.5549 | 22.0063 | 22.1543 | 23.8938 | 51.3066 | 21.8808 | 22.4278 | 31.9511 | 510.8141 | 751.4938 | 301.3543 | 298.9458 | 293.8652 |  | 169.4633 | 295.103 | 154.774 | 364.7874 | 252.4559 | 200.6968 |  | 199.1966 |  |  | 59.8102 | 131.6064 | 201.2936 | [5 empty] | 21.8819 | 317.2805 | 21.7138 | 22.0887 | 108.6713 | 21.2834 | 21.9 | 87.7743 | 340.844 | 687.818 |  | 254.7115 | 455.1015 | 61.9773 | 238.1971 | 624.8785 | 228.3629 | 427.4054 | 83.0195 | 276.9195 | 102.1199 | 333.9594 | 24.3837 | 226.5583 | 410.5808 | 91.3386 | 248.0021 | 507.9646 | 64.7918 | 233.7758 | 470.8987 | 73.0139 | 287.3 | 124.6816 | 327.495 | 97.1259 | 390.0513 | 19.9522 | 16.9419 | 4.037 | 0.070243 | -27.3827 | 3.095 | 1707.59 | 52.65 | 1.8913 | -0.81359 | -10.3956 | 0.82181 | 2.5198 | -21.0806 | -1.9685 | -1.2795 | -1.9967 | 1.2071 | -0.93308 | -3.0802 | -2.6989 | -1.4762
42838.4276 | 635 | 22.8816 | 22.8533 | 22.833 | 22.7535 | 22.3594 | 21.6861 | 22.6902 | 21.7424 | 22.3368 | 22.3459 | 22.3202 | 21.9636 | 21.1777 | 22.1451 | 21.592 | 21.7543 | 21.9202 | 21.0673 | 21.2419 | 22.2076 | 20.4939 | 22.1692 | 29.6615 | 22.0011 | 22.9465 | 35.7284 | 449.2064 | 384.6082 | 540.8216 | 22.1448 | 22.6487 | 32.1392 | 22.1076 | 22.9175 | 36.4849 | 204.287 | 680.43 |  | 326.0788 | 402.3277 | 370.5152 | 413.9129 |  | 23.5851 | 31.3645 | 26.2062 | 32.1885 | 51.5005 | 193.3976 | 308.9069 | 16.4396 | 18.8396 | 17.037 | 23.9842 | 19.6391 | 45.9532 | 48.4653 | 45.1485 | 21.9209 |  |  | 0.64617 | -0.13412 | -74.8154 | 0.3226 | 3.1063 | -197.8322 | -1.5939 | 4.2663 | 0.42218 | 1.0208 | 8.0295 | 0.021695 | 0.022955 | 0.24813 | 22.1608 | 21.9653 | 22.1428 | 22.1957 | 22.0033 | 21.2834 | 20.0997 | 22.168 | 22.3432 | 22.3811 | 22.3305 | 21.9329 | 21.1606 | 22.2556 | 111.3919 | 85.9749 | 100.6374 | 75.1243 | 66.9435 | 95.7044 | 65.4266 | 22.3182 | 22.0807 | 21.682 | 22.042 | 21.8122 | 22.0434 | 21.9396 | 22.1466 | 30.1897 | 164.6074 | 509.8668 | 362.6237 | 296.0586 | 1.3341 | 2.6585 | 190.7852 | 21.898 | 22.2009 | 27.5841 | 21.5566 | 22.0121 | 22.1593 | 23.9102 | 51.7523 | 21.8794 | 22.437 | 32.0355 | 524.6308 | 756.0835 | 304.3462 | 301.7692 | 299.5125 |  | 172.2908 | 297.8327 | 156.6433 | 376.2418 | 257.7839 | 207.4637 |  | 201.744 |  |  | 61.1233 | 135.1804 | 207.8891 | [5 empty] | 21.8844 | 330.3462 | 21.7105 | 22.0883 | 111.6508 | 21.2933 | 21.9045 | 89.7057 | 348.5581 | 703.652 |  | 258.4671 | 462.7112 | 63.3553 | 242.3501 | 631.3947 | 236.4237 | 440.5297 | 86.2041 | 280.7546 | 106.9967 | 342.263 | 24.6028 | 228.923 | 416.4007 | 93.2767 | 252.9096 | 517.4304 | 66.2879 | 237.0859 | 481.302 | 75.805 | 290.9645 | 129.141 | 335.465 | 100.7816 | 394.9496 | 20.1505 | 16.8846 | 4.0933 | 0.06943 | -27.3754 | 3.095 | 1776.95 | 51.5 | 1.5983 | -0.44536 | -10.5188 | 0.69072 | 2.653 | -21.1721 | -1.9004 | -1.3017 | -1.9872 | 1.215 | -0.69351 | -3.1672 | -2.8768 | -1.5692
42838.4276 | 636 | 22.8815 | 22.85 | 22.836 | 22.7509 | 22.3597 | 21.6859 | 22.6926 | 21.7337 | 22.3382 | 22.3411 | 22.3137 | 21.9582 | 21.1733 | 22.1443 | 21.5884 | 21.76 | 21.9263 | 21.0581 | 21.2458 | 22.2182 | 20.4891 | 22.1863 | 29.7065 | 22.0058 | 22.9552 | 35.8148 | 461.0818 | 392.0628 | 551.8503 | 22.1455 | 22.6576 | 32.2098 | 22.098 | 22.9156 | 36.6542 | 207.4925 | 706.0986 |  | 331.3742 | 409.0292 | 376.0876 | 425.7017 |  | 23.8758 | 31.8353 | 26.5792 | 32.7784 | 56.3154 | 198.5588 | 315.172 | 16.4729 | 18.8849 | 17.1802 | 24.135 | 19.6438 | 45.9273 | 48.4541 | 45.1527 | 21.9155 |  |  | 0.73029 | 0.25687 | -76.378 | 0.52696 | 3.3113 | -197.8861 | -2.1196 | 4.587 | 0.41965 | 1.123 | 8.6128 | 0.021253 | 0.022537 | 0.25732 | 22.1623 | 21.9687 | 22.1434 | 22.1969 | 22.0105 | 21.294 | 20.1001 | 22.176 | 22.3469 | 22.385 | 22.3341 | 21.9442 | 21.1594 | 22.2508 | 106.219 | 82.4787 | 95.4777 | 72.3047 | 66.3217 | 95.6162 | 65.5563 | 22.323 | 22.0833 | 21.676 | 22.0474 | 21.8104 | 22.0447 | 21.9388 | 22.1529 | 30.2488 | 167.9587 | 530.6453 | 375.0348 | 303.5399 | 2.2586 | 1.5281 | 195.0238 | 21.9082 | 22.2124 | 27.9032 | 21.559 | 22.011 | 22.1643 | 23.9157 | 52.2036 | 21.8831 | 22.4437 | 32.128 | 537.2855 | 759.6122 | 307.4914 | 305.536 | 305.9511 |  | 175.4622 | 300.3301 | 158.7933 | 399.2526 | 266.08 | 214.3953 |  | 205.0681 |  |  | 62.5827 | 138.8387 | 215.3112 | [5 empty] | 21.8861 | 355.7083 | 21.7098 | 22.0917 | 115.2131 | 21.2877 | 21.9088 | 92.1284 | 356.7356 | 718.8798 |  | 262.7596 | 473.047 | 64.8628 | 246.7917 | 639.0696 | 246.0266 | 452.3689 | 90.3245 | 285.5639 | 111.5477 | 350.1459 | 24.8364 | 231.4789 | 421.7901 | 95.5567 | 257.9104 | 531.5114 | 67.838 | 241.0768 | 490.6751 | 79.0564 | 295.0786 | 134.6259 | 343.964 | 105.3701 | 402.7277 | 24.3471 | 16.8167 | 4.1505 | 0.070599 | -27.3226 | 3.0949 | 1820.78 | 51.73 | 1.7106 | 0.61682 | -10.6363 | 0.88348 | 2.7543 | -21.2918 | -2.2036 | -1.3282 | -1.9578 | 1.0946 | -0.12954 | -2.5784 | -3.0353 | -1.6195
42838.4277 | 637 | 22.8753 | 22.8399 | 22.8381 | 22.7504 | 22.3562 | 21.6761 | 22.6866 | 21.7361 | 22.3333 | 22.3321 | 22.3111 | 21.9556 | 21.1658 | 22.1422 | 21.5852 | 21.7689 | 21.9258 | 21.0645 | 21.2463 | 22.2183 | 20.4865 | 22.2053 | 29.7568 | 21.9998 | 22.9532 | 35.9042 | 475.1626 | 401.224 | 570.8979 | 22.1487 | 22.6588 | 32.2846 | 22.0976 | 22.9274 | 36.8334 | 210.9618 | 715.185 |  | 336.8159 | 416.4587 | 382.0085 | 437.3354 |  | 24.1785 | 32.4329 | 27.0309 | 33.5781 | 64.801 | 205.5099 | 321.438 | 16.5301 | 18.9307 | 17.2856 | 24.3185 | 19.6655 | 45.9104 | 48.4423 | 45.1628 | 21.9189 |  |  | 0.6994 | -0.11637 | -78.1404 | 0.46717 | 4.0302 | -197.8348 | -2.8273 | 5.3788 | 0.34337 | 1.4106 | 9.3945 | 0.020765 | 0.021964 | 0.24866 | 22.1656 | 21.968 | 22.1532 | 22.2054 | 22.0027 | 21.2896 | 20.1042 | 22.1682 | 22.3498 | 22.3806 | 22.3362 | 21.9399 | 21.1581 | 22.2516 | 102.3437 | 78.4573 | 89.8504 | 70.4036 | 65.4297 | 95.5552 | 65.6522 | 22.3151 | 22.0774 | 21.6831 | 22.0427 | 21.8068 | 22.0577 | 21.9393 | 22.1615 | 30.3094 | 171.7195 | 551.5028 | 387.3554 | 312.0809 | 1.3548 | 2.4487 | 202.7572 | 21.8943 | 22.2062 | 28.268 | 21.5532 | 22.0082 | 22.1599 | 23.9326 | 52.6672 | 21.8843 | 22.4448 | 32.2076 | 548.8744 | 763.2271 | 312.5947 | 310.8335 | 311.694 |  | 179.0859 | 308.819 | 161.3408 | 464.2585 | 277.1524 | 224.215 |  | 208.854 |  |  | 64.4224 | 143.214 | 224.2266 | [5 empty] | 21.8857 | 385.0981 | 21.71 | 22.0956 | 119.2801 | 21.2898 | 21.9006 | 94.718 | 365.8281 | 730.9994 |  | 267.8906 | 481.634 | 66.6214 | 251.3403 | 646.2971 | 256.1152 | 466.6245 | 94.6023 | 291.3927 | 116.9481 | 358.9827 | 25.0594 | 234.2599 | 428.0129 | 98.0884 | 263.1514 | 546.5902 | 69.5372 | 247.1093 | 502.4521 | 83.4064 | 300.2761 | 140.077 | 354.3757 | 110.8989 | 410.2624 | 25.9591 | 16.7583 | 4.2072 | 0.072269 | -27.3274 | 3.095 | 1850.91 | 52.32 | 1.6932 | -0.41558 | -10.7689 | 0.83266 | 3.0609 | -21.4453 | -2.5637 | -1.3119 | -2.0759 | 0.0024326 | 0.29358 | -1.9416 | -3.1738 | -1.6781
42838.4277 | 638 | 22.8847 | 22.8489 | 22.8381 | 22.7588 | 22.3592 | 21.6821 | 22.6879 | 21.7492 | 22.3429 | 22.3483 | 22.3137 | 21.9578 | 21.1724 | 22.1541 | 21.5915 | 21.7663 | 21.9248 | 21.0717 | 21.2446 | 22.2291 | 20.4945 | 22.226 | 29.8063 | 22.0105 | 22.9646 | 35.9915 | 489.6082 | 409.9513 | 589.9482 | 22.1526 | 22.6751 | 32.3728 | 22.1114 | 22.9392 | 37.0171 | 214.7889 | 737.147 |  | 342.5651 | 425.2437 | 387.6353 | 449.1732 |  | 24.4802 | 33.0408 | 27.4792 | 34.4734 | 73.5376 | 211.3627 | 328.5894 | 16.5931 | 18.9822 | 17.3088 | 24.4945 | 19.6738 | 45.8962 | 48.4262 | 45.1755 | 21.9244 |  |  | 1.0536 | 0.026875 | -79.9567 | 0.54865 | 3.8383 | -197.8361 | -2.8897 | 5.2776 | 0.43191 | 1.4645 | 11.1524 | 0.019778 | 0.021134 | 0.24183 | 22.1765 | 21.964 | 22.1468 | 22.2024 | 22.0052 | 21.2856 | 20.0999 | 22.1685 | 22.3488 | 22.3891 | 22.3295 | 21.9393 | 21.1574 | 22.2509 | 98.8597 | 75.4308 | 86.7868 | 67.6942 | 64.6639 | 95.4726 | 65.7274 | 22.3158 | 22.077 | 21.68 | 22.0398 | 21.7982 | 22.0578 | 21.9351 | 22.1573 | 30.3609 | 175.6925 | 574.1909 | 404.2528 | 323.6334 | 1.2071 | 1.3318 | 208.9698 | 21.8852 | 22.1929 | 28.6622 | 21.5412 | 22.0053 | 22.1497 | 23.9316 | 53.1436 | 21.8724 | 22.4424 | 32.2784 | 559.1397 | 767.535 | 319.0063 | 317.0762 | 320.7383 |  | 182.8907 | 319.1459 | 163.9888 | 552.8572 | 289.6805 | 235.4599 |  | 212.7805 |  |  | 66.4094 | 147.9381 | 237.8932 | [5 empty] | 21.8808 | 413.4702 | 21.7026 | 22.0926 | 123.475 | 21.2838 | 21.9007 | 97.6275 | 376.3195 | 743.327 |  | 273.5788 | 491.2434 | 68.5652 | 255.6973 | 654.0861 | 267.1132 | 483.8841 | 99.5637 | 297.9445 | 122.5899 | 369.0362 | 25.3222 | 237.7272 | 434.1373 | 100.9608 | 269.8906 | 560.0334 | 71.4992 | 253.0955 | 515.8813 | 88.4028 | 307.3979 | 146.0841 | 365.1302 | 116.9855 | 419.2578 | 36.5938 | 16.7168 | 4.2589 | 0.07372 | -27.2623 | 3.095 | 1878.62 | 51.94 | 2.1015 | 0.19991 | -10.9041 | 0.90325 | 3.0053 | -21.5761 | -2.6076 | -1.3767 | -2.2395 | -1.6207 | 0.67057 | -1.5922 | -3.2967 | -1.8082
42838.4277 | 639 | 22.8948 | 22.8592 | 22.8333 | 22.7627 | 22.3641 | 21.684 | 22.6889 | 21.7465 | 22.344 | 22.341 | 22.3152 | 21.962 | 21.1762 | 22.1493 | 21.5946 | 21.775 | 21.9226 | 21.0677 | 21.246 | 22.2362 | 20.4913 | 22.2488 | 29.8458 | 22.0059 | 22.9684 | 36.0716 | 506.5978 | 420.857 | 609.4229 | 22.1503 | 22.673 | 32.4366 | 22.1059 | 22.9362 | 37.1921 | 218.7873 | 758.2745 |  | 348.829 | 436.0783 | 394.095 | 459.5179 |  | 24.8712 | 33.7788 | 28.0578 | 35.6731 | 85.2263 | 217.7598 | 340.0737 | 16.6065 | 19.0521 | 17.3784 | 24.7019 | 19.6844 | 45.8903 | 48.4223 | 45.1729 | 21.9299 |  |  | 1.2461 | -0.15515 | -81.9418 | 0.56507 | 4.1183 | -197.8171 | -3.2032 | 5.4353 | 0.42996 | 1.577 | 11.9931 | 0.019181 | 0.020706 | 0.23918 | 22.1741 | 21.9709 | 22.1459 | 22.202 | 22.0083 | 21.2891 | 20.1087 | 22.1717 | 22.3474 | 22.3866 | 22.3299 | 21.9481 | 21.1623 | 22.2498 | 91.3984 | 68.7288 | 80.6398 | 65.6429 | 64.8792 | 95.364 | 65.7411 | 22.3172 | 22.069 | 21.6768 | 22.0335 | 21.8006 | 22.0578 | 21.9378 | 22.1638 | 30.4182 | 180.4405 | 599.131 | 428.5393 | 338.6859 | 1.6204 | 0.5712 | 220.0546 | 21.8918 | 22.1973 | 29.1521 | 21.5475 | 22.0068 | 22.1604 | 23.9424 | 53.6277 | 21.8816 | 22.4557 | 32.3687 | 567.8341 | 773.124 | 326.2588 | 324.3293 | 329.1827 |  | 187.2383 | 347.7151 | 167.6041 | 628.4258 | 303.8285 | 247.0952 |  | 217.1802 |  |  | 68.7147 | 153.5769 | 259.7005 | [5 empty] | 21.887 | 445.7696 | 21.7094 | 22.09 | 127.8714 | 21.2943 | 21.9068 | 100.9616 | 388.3294 | 755.5032 |  | 280.2332 | 501.8962 | 70.7504 | 261.2262 | 663.7143 | 279.4965 | 502.7159 | 105.6158 | 304.611 | 129.3182 | 381.2598 | 25.6595 | 242.598 | 441.3837 | 104.2205 | 277.9687 | 575.0412 | 73.7364 | 260.0472 | 528.8766 | 92.9129 | 314.7093 | 153.3695 | 377.784 | 124.4697 | 431.8402 | 35.0907 | 16.6622 | 4.3155 | 0.076327 | -27.2593 | 3.095 | 1938.89 | 52.79 | 2.3111 | -0.4809 | -11.0519 | 0.91778 | 3.1335 | -21.717 | -2.7635 | -1.3956 | -2.8633 | -2.7328 | 1.4863 | -0.90754 | -3.3663 | -1.9956
42838.4277 | 640 | 22.8768 | 22.8523 | 22.8363 | 22.748 | 22.3571 | 21.684 | 22.6854 | 21.7367 | 22.3412 | 22.3378 | 22.3125 | 21.9648 | 21.1726 | 22.1458 | 21.5932 | 21.7684 | 21.9274 | 21.0638 | 21.2445 | 22.2358 | 20.4912 | 22.2641 | 29.8916 | 22.0065 | 22.9771 | 36.1544 | 525.0463 | 433.0756 | 625.6283 | 22.1498 | 22.6769 | 32.5335 | 22.1037 | 22.9463 | 37.4036 | 223.5828 | 768.0369 |  | 356.5674 | 448.8839 | 402.7221 | 474.5436 |  | 25.3409 | 34.6067 | 28.7325 | 36.939 | 94.3782 | 225.2266 | 349.9688 | 16.6413 | 19.1137 | 17.4894 | 24.9355 | 19.6973 | 45.8793 | 48.4241 | 45.178 | 21.9372 |  |  | 1.2777 | 0.14975 | -83.6102 | 0.34034 | 4.0815 | -197.8578 | -4.2743 | 6.0536 | 0.74852 | 1.7354 | 13.0241 | 0.019051 | 0.020201 | 0.24086 | 22.1821 | 21.9753 | 22.1479 | 22.2069 | 22.0118 | 21.2902 | 20.1051 | 22.1724 | 22.3508 | 22.392 | 22.3344 | 21.9418 | 21.1665 | 22.2558 | 88.4014 | 67.8502 | 74.9655 | 64.5346 | 66.5507 | 95.371 | 65.7308 | 22.31 | 22.0728 | 21.6776 | 22.0403 | 21.7991 | 22.0585 | 21.9307 | 22.1679 | 30.4852 | 186.2652 | 624.9664 | 459.1413 | 362.2497 | 3.2457 | 4.1757 | 232.2779 | 21.9028 | 22.2077 | 29.6767 | 21.55 | 22.006 | 22.1654 | 23.9634 | 54.1481 | 21.8836 | 22.4667 | 32.4659 | 577.338 | 778.2867 | 335.005 | 333.37 | 346.3595 |  | 194.2987 | 369.5388 | 172.3135 | 672.8633 | 322.5084 | 264.0465 |  | 223.0201 |  |  | 71.4788 | 160.2827 | 282.8719 | [5 empty] | 21.8883 | 472.7129 | 21.7136 | 22.0889 | 132.4231 | 21.2934 | 21.9047 | 104.9042 | 402.1553 | 768.8136 |  | 288.0951 | 512.6258 | 73.193 | 268.5528 | 671.6242 | 293.2 | 525.9398 | 112.4984 | 311.6301 | 137.4645 | 395.5218 | 26.0713 | 247.998 | 450.0031 | 107.872 | 286.5156 | 589.689 | 76.2511 | 268.5065 | 542.0139 | 98.3905 | 323.2306 | 161.762 | 392.1756 | 132.33 | 445.6669 | 36.6122 | 16.5899 | 4.3658 | 0.078998 | -27.3227 | 3.095 | 2051.66 | 51.49 | 2.3616 | 0.47311 | -11.1789 | 0.71323 | 3.1431 | -21.8838 | -3.2165 | -1.5167 | -3.2458 | -2.5942 | 1.8202 | -0.27831 | -3.5191 | -2.3626
42838.4277 | 641 | 22.8875 | 22.8527 | 22.8359 | 22.7604 | 22.3555 | 21.6847 | 22.6865 | 21.7385 | 22.3432 | 22.3475 | 22.3125 | 21.9574 | 21.1726 | 22.1463 | 21.5885 | 21.764 | 21.9327 | 21.0674 | 21.2488 | 22.2396 | 20.4984 | 22.2872 | 29.9441 | 22.0083 | 22.9805 | 36.2337 | 545.2362 | 446.0838 | 647.9796 | 22.1575 | 22.6933 | 32.6175 | 22.1137 | 22.96 | 37.6406 | 228.5698 | 779.1681 |  | 364.9782 | 462.6884 | 413.5649 | 484.8348 |  | 25.8816 | 35.5284 | 29.3903 | 38.0205 | 101.2264 | 232.3672 | 361.0978 | 16.7468 | 19.188 | 17.6402 | 25.1851 | 19.7032 | 45.8474 | 48.4205 | 45.1742 | 21.9916 |  |  | 1.3894 | 0.10967 | -85.2537 | 0.76484 | 3.9757 | -197.8256 | -4.2822 | 6.6924 | 0.53758 | 1.8315 | 13.9996 | 0.018603 | 0.019932 | 0.23011 | 22.1888 | 21.9731 | 22.1516 | 22.2078 | 22.0108 | 21.2898 | 20.1101 | 22.1733 | 22.3519 | 22.3864 | 22.3325 | 21.9396 | 21.16 | 22.2478 | 96.3266 | 81.1949 | 84.2368 | 63.1493 | 63.4591 | 95.5993 | 65.9129 | 22.3136 | 22.0744 | 21.6764 | 22.0396 | 21.8057 | 22.0687 | 21.9299 | 22.1711 | 30.5482 | 192.3134 | 646.6541 | 488.8646 | 383.2624 | 3.2288 | 3.5746 | 242.72 | 21.8997 | 22.2107 | 30.1643 | 21.5572 | 22.0079 | 22.1689 | 23.9834 | 54.6821 | 21.888 | 22.4738 | 32.5579 | 583.5144 | 782.1143 | 344.7984 | 342.7926 | 363.8381 |  | 200.2576 | 382.5042 | 176.6972 | 701.375 | 339.9127 | 276.1092 |  | 228.3351 |  |  | 74.5544 | 167.1492 | 301.0318 | [5 empty] | 21.8836 | 494.9633 | 21.7075 | 22.0849 | 137.8009 | 21.2912 | 21.9015 | 109.3013 | 417.081 | 780.3576 |  | 296.5529 | 522.2159 | 75.9 | 277.1301 | 680.0007 | 308.9181 | 551.3535 | 119.4347 | 320.4639 | 145.1859 | 410.1717 | 26.5458 | 254.0513 | 459.8482 | 111.8373 | 295.7605 | 604.0351 | 79.0107 | 276.9627 | 553.593 | 104.8379 | 333.9048 | 171.1361 | 406.2116 | 141.2373 | 461.0693 | 49.8302 | 16.5281 | 4.422 | 0.081502 | -27.2897 | 3.095 | 2185.07 | 52.25 | 2.4931 | 0.40548 | -11.3052 | 1.0708 | 3.1242 | -22.0382 | -3.2424 | -1.696 | -3.395 | -2.0312 | 0.96754 | -1.2866 | -3.5257 | -2.6426
42838.4277 | 642 | 22.8911 | 22.8539 | 22.8405 | 22.7597 | 22.3627 | 21.6861 | 22.6885 | 21.744 | 22.3378 | 22.3482 | 22.3177 | 21.9623 | 21.1739 | 22.1443 | 21.584 | 21.7662 | 21.9273 | 21.0624 | 21.2486 | 22.2446 | 20.4961 | 22.3112 | 29.9926 | 22.0102 | 22.9842 | 36.319 | 568.5586 | 458.3925 | 675.5145 | 22.1614 | 22.6984 | 32.7022 | 22.1167 | 22.9727 | 37.8638 | 233.6503 | 785.6927 |  | 373.2436 | 475.9558 | 422.3298 | 492.4656 |  | 26.5537 | 36.7444 | 30.2399 | 39.4659 | 109.801 | 241.3744 | 375.3799 | 16.7842 | 19.2808 | 17.8427 | 25.5057 | 19.7161 | 45.8293 | 48.4127 | 45.1856 | 21.9996 |  |  | 1.9637 | 0.008479 | -87.7244 | 0.41 | 5.19 | -197.8414 | -4.9807 | 7.1109 | 0.67283 | 2.1424 | 15.3297 | 0.018384 | 0.019546 | 0.23624 | 22.1864 | 21.9712 | 22.151 | 22.2022 | 22.0042 | 21.2884 | 20.1022 | 22.173 | 22.3499 | 22.3738 | 22.3284 | 21.9387 | 21.159 | 22.2407 | 102.032 | 88.6654 | 89.6166 | 66.9385 | 65.9008 | 95.8596 | 66.1073 | 22.3117 | 22.0733 | 21.6726 | 22.0395 | 21.802 | 22.0717 | 21.9297 | 22.1724 | 30.6178 | 199.1998 | 668.6532 | 521.784 | 413.7198 | 2.2365 | 4.0673 | 258.0091 | 21.9109 | 22.1993 | 30.6909 | 21.5581 | 22.0121 | 22.1754 | 23.9927 | 55.2187 | 21.8843 | 22.4757 | 32.6486 | 587.7003 | 787.4806 | 354.4277 | 352.1978 | 417.2812 |  | 207.1045 | 396.7347 | 181.5217 | 727.8532 | 359.7689 | 286.223 |  | 233.6573 |  |  | 77.847 | 174.1397 | 318.775 | [5 empty] | 21.8758 | 518.7389 | 21.7064 | 22.0851 | 143.9928 | 21.2895 | 21.904 | 114.381 | 434.9577 | 793.8987 |  | 305.7427 | 532.3249 | 78.7748 | 285.6266 | 685.197 | 327.6845 | 581.203 | 127.5723 | 330.3909 | 153.5349 | 427.2516 | 27.0708 | 260.7572 | 470.7157 | 116.2619 | 306.3231 | 619.9093 | 82.01 | 285.5733 | 563.411 | 111.8551 | 345.5889 | 181.6433 | 421.8919 | 150.7088 | 478.0959 | 62.9871 | 16.4562 | 4.4644 | 0.083143 | -27.3027 | 3.095 | 2373.27 | 51.92 | 3.0079 | 0.11297 | -11.4904 | 0.78553 | 3.6013 | -22.2346 | -3.5279 | -2.822 | -3.555 | -1.1259 | 0.36549 | -1.861 | -3.4488 | -3.1364
42838.4277 | 643 | 22.888 | 22.8542 | 22.8401 | 22.7555 | 22.3655 | 21.6832 | 22.6868 | 21.7408 | 22.3405 | 22.3427 | 22.3209 | 21.9642 | 21.1789 | 22.1445 | 21.5801 | 21.7608 | 21.9201 | 21.0637 | 21.2486 | 22.2527 | 20.484 | 22.3324 | 30.0419 | 22.0142 | 22.9791 | 36.4095 | 594.6509 | 470.8425 | 703.6851 | 22.1498 | 22.6952 | 32.7643 | 22.1066 | 22.9631 | 38.0868 | 239.1232 | 773.7196 |  | 381.7598 | 490.7419 | 432.1438 | 512.8536 |  | 27.1786 | 37.863 | 31.0423 | 40.9512 | 119.397 | 250.6829 | 386.2243 | 16.9162 | 19.3699 | 18.0029 | 25.8148 | 19.7386 | 45.8106 | 48.414 | 45.1958 | 22.01 |  |  | 2.2844 | -0.2064 | -90.7695 | 0.39817 | 4.5217 | -197.8368 | -6.5039 | 7.5473 | 0.75436 | 2.1321 | 16.8891 | 0.017851 | 0.019043 | 0.24215 | 22.1864 | 21.9712 | 22.1524 | 22.1988 | 22.0011 | 21.289 | 20.0974 | 22.1635 | 22.3496 | 22.3752 | 22.3243 | 21.9366 | 21.1578 | 22.2398 | 108.6212 | 98.3392 | 99.4972 | 71.1318 | 68.055 | 96.0942 | 66.3883 | 22.321 | 22.0751 | 21.6793 | 22.0416 | 21.8086 | 22.0826 | 21.9361 | 22.1822 | 30.6912 | 207.3539 | 691.9838 | 557.2032 | 444.7803 | 2.2578 | 6.2293 | 278.5572 | 21.9086 | 22.2044 | 31.2519 | 21.5527 | 22.0119 | 22.1739 | 24.0093 | 55.773 | 21.8831 | 22.4917 | 32.7375 | 591.0087 | 794.4476 | 363.2251 | 361.0658 | 457.0262 |  | 216.3347 | 435.1904 | 187.9877 | 764.3287 | 385.2162 | 300.1845 |  | 240.3394 |  |  | 81.4173 | 182.584 | 343.0369 | [5 empty] | 21.8741 | 545.772 | 21.7019 | 22.0851 | 151.6014 | 21.2898 | 21.9102 | 120.2772 | 458.045 | 809.8133 |  | 316.1503 | 542.6049 | 81.9219 | 295.2604 | 688.9759 | 349.3855 | 620.6338 | 136.8223 | 341.2296 | 164.3401 | 444.8402 | 27.6466 | 267.6307 | 480.3286 | 121.2534 | 318.5275 | 636.3036 | 85.4086 | 295.9998 | 570.7924 | 120.0228 | 356.7932 | 193.6136 | 440.3496 | 161.3743 | 491.2016 | 56.8035 | 16.3884 | 4.5117 | 0.084479 | -27.4368 | 3.0949 | 2518.9 | 51.27 | 3.292 | -0.55836 | -11.7092 | 0.77552 | 3.3917 | -22.4345 | -4.0677 | -3.431 | -4.3028 | 0.12164 | -0.33789 | -2.9252 | -3.6989 | -3.5726
42838.4277 | 644 | 22.8807 | 22.8464 | 22.8282 | 22.7484 | 22.3589 | 21.6805 | 22.6839 | 21.7373 | 22.3379 | 22.3418 | 22.3156 | 21.9598 | 21.1728 | 22.142 | 21.5927 | 21.7614 | 21.9239 | 21.0699 | 21.2573 | 22.2655 | 20.4937 | 22.3536 | 30.0888 | 22.0201 | 22.9877 | 36.5176 | 622.7301 | 484.609 | 733.4984 | 22.1558 | 22.7085 | 32.8454 | 22.1106 | 22.9736 | 38.3322 | 245.4775 | 763.8885 |  | 390.7651 | 505.5492 | 441.4175 | 535.9611 |  | 27.9087 | 39.1592 | 32.0012 | 42.592 | 131.7608 | 260.3144 | 397.1566 | 17.0436 | 19.481 | 18.1675 | 26.1797 | 19.7625 | 45.8186 | 48.4215 | 45.2214 | 22.0204 |  |  | 2.3389 | 0.12479 | -93.8882 | 0.43825 | 5.3399 | -197.8217 | -7.3805 | 8.0611 | 0.83123 | 2.2722 | 18.0632 | 0.017179 | 0.018467 | 0.25233 | 22.1887 | 21.9676 | 22.1408 | 22.202 | 22.0021 | 21.2862 | 20.1019 | 22.1716 | 22.3439 | 22.3756 | 22.3284 | 21.9266 | 21.1572 | 22.2319 | 105.3382 | 97.7234 | 109.8028 | 78.0832 | 72.5553 | 96.2299 | 66.7975 | 22.32 | 22.0775 | 21.6909 | 22.0472 | 21.8125 | 22.0838 | 21.9313 | 22.1838 | 30.7721 | 218.0182 | 713.3949 | 594.9016 | 486.127 | 2.697 | 4.9171 | 305.0391 | 21.9003 | 22.2003 | 31.9668 | 21.5559 | 22.0072 | 22.1693 | 24.0145 | 56.3678 | 21.8846 | 22.4896 | 32.8388 | 593.8957 | 801.0667 | 372.8926 | 371.1527 | 481.208 |  | 226.6035 | 478.7216 | 195.7087 | 799.1454 | 411.24 | 312.7042 |  | 247.1517 |  |  | 85.6482 | 192.6562 | 375.5909 | [5 empty] | 21.8667 | 576.1473 | 21.6975 | 22.0789 | 160.8384 | 21.2826 | 21.8962 | 127.0399 | 488.7079 | 826.0269 |  | 326.8712 | 553.4525 | 85.4814 | 306.0732 | 692.2046 | 374.3781 | 664.6679 | 146.477 | 354.2008 | 175.7143 | 460.9989 | 28.2494 | 274.7962 | 488.5399 | 126.8823 | 331.9351 | 649.8873 | 89.1779 | 307.1184 | 579.6258 | 130.0496 | 368.2231 | 206.707 | 461.8578 | 173.3004 | 504.3699 | 57.8625 | 16.3394 | 4.5552 | 0.086453 | -27.3356 | 3.095 | 2640.45 | 46.61 | 3.3815 | 0.43505 | -11.9334 | 0.81531 | 3.7195 | -22.639 | -4.3728 | -3.5356 | -5.1215 | 1.6642 | 0.043509 | -4.0211 | -3.9669 | -4.1475
42838.4277 | 645 | 22.8819 | 22.8435 | 22.8332 | 22.7525 | 22.357 | 21.6789 | 22.6835 | 21.7371 | 22.3394 | 22.3526 | 22.3088 | 21.9581 | 21.1697 | 22.1459 | 21.5964 | 21.7706 | 21.9357 | 21.0767 | 21.2575 | 22.2707 | 20.4978 | 22.3847 | 30.1477 | 22.0199 | 22.9994 | 36.6379 | 652.7274 | 498.9856 | 764.2726 | 22.1631 | 22.7128 | 32.9245 | 22.1117 | 22.9854 | 38.5894 | 252.2428 | 752.194 |  | 399.9947 | 519.375 | 450.7336 | 552.2294 |  | 28.6278 | 40.4712 | 33.0017 | 44.2916 | 143.963 | 270.1798 | 409.5761 | 17.122 | 19.5938 | 18.3136 | 26.5779 | 19.7477 | 45.8278 | 48.4304 | 45.241 | 22.0305 |  |  | 2.7378 | -0.23531 | -97.3039 | 0.22732 | 5.604 | -197.8834 | -8.401 | 8.326 | 0.8178 | 2.5488 | 19.6964 | 0.016791 | 0.01801 | 0.26285 | 22.1968 | 21.9684 | 22.1487 | 22.203 | 22.0047 | 21.2918 | 20.1 | 22.1713 | 22.3501 | 22.374 | 22.3348 | 21.9282 | 21.1656 | 22.2398 | 103.4152 | 102.6826 | 113.8761 | 81.2908 | 75.2442 | 96.4355 | 67.1852 | 22.3146 | 22.0834 | 21.688 | 22.0481 | 21.8104 | 22.099 | 21.9327 | 22.1871 | 30.8544 | 229.877 | 731.0903 | 631.89 | 517.3905 | 2.2281 | 2.7111 | 328.3822 | 21.8884 | 22.207 | 32.6683 | 21.5409 | 22.01 | 22.1702 | 24.0204 | 56.988 | 21.8862 | 22.4891 | 32.9333 | 596.1161 | 809.5401 | 381.5181 | 380.7034 | 496.8704 |  | 236.3099 | 533.754 | 203.4187 | 824.6837 | 437.2163 | 323.8947 |  | 253.52 |  |  | 90.3389 | 204.5882 | 397.902 | [5 empty] | 21.8699 | 608.4799 | 21.7016 | 22.0802 | 171.169 | 21.2821 | 21.8964 | 134.8513 | 525.2863 | 844.373 |  | 338.5956 | 561.4425 | 89.4007 | 317.3034 | 694.8919 | 405.2722 | 710.1131 | 156.8587 | 370.3522 | 188.0098 | 477.351 | 28.8985 | 283.9828 | 495.4775 | 133.1863 | 347.8203 | 664.2623 | 93.2859 | 319.2113 | 584.8236 | 140.2001 | 380.4627 | 220.8521 | 486.9821 | 185.5354 | 521.2413 | 64.8475 | 16.2788 | 4.5897 | 0.086932 | -27.3382 | 3.095 | 2787.58 | 33.33 | 3.714 | -0.59868 | -12.174 | 0.58842 | 3.8455 | -22.8509 | -4.7083 | -3.4181 | -6.2513 | 3.6752 | 0.28237 | -4.4272 | -4.0126 | -4.3561
42838.4278 | 646 | 22.8854 | 22.8461 | 22.8354 | 22.7532 | 22.3537 | 21.6796 | 22.677 | 21.7332 | 22.3385 | 22.3381 | 22.2957 | 21.9536 | 21.1692 | 22.1472 | 21.5899 | 21.7718 | 21.9329 | 21.0728 | 21.2608 | 22.2764 | 20.4916 | 22.4152 | 30.2096 | 22.0168 | 23.0088 | 36.7524 | 683.2251 | 514.621 | 795.1834 | 22.1583 | 22.715 | 33.0085 | 22.1032 | 22.9981 | 38.8572 | 259.7097 | 731.9629 |  | 409.1496 | 532.3482 | 460.363 | 582.0299 |  | 29.2703 | 41.7115 | 33.9425 | 47.4581 | 152.2507 | 278.5302 | 418.8725 | 17.1878 | 19.7094 | 18.4774 | 26.9667 | 19.7521 | 45.8301 | 48.4377 | 45.2684 | 22.0351 |  |  | 2.034 | -0.21297 | -100.437 | 0.32129 | 4.9988 | -197.8401 | -9.7803 | 8.5711 | 0.75689 | 2.6172 | 20.457 | 0.016499 | 0.017685 | 0.27773 | 22.1885 | 21.9673 | 22.1526 | 22.2029 | 22.0085 | 21.2932 | 20.1043 | 22.1701 | 22.3525 | 22.3768 | 22.3295 | 21.9311 | 21.1632 | 22.2345 | 104.2745 | 99.9672 | 108.0464 | 81.8439 | 76.8633 | 96.5966 | 67.4239 | 22.321 | 22.0786 | 21.6844 | 22.0434 | 21.8119 | 22.0955 | 21.9318 | 22.188 | 30.9334 | 242.136 | 740.385 | 661.9774 | 544.0736 | 2.4827 | 2.3785 | 346.1387 | 21.9038 | 22.2054 | 33.3529 | 21.5548 | 22.0057 | 22.1726 | 24.0395 | 57.6474 | 21.8853 | 22.4873 | 33.0421 | 601.8217 | 814.678 | 390.7346 | 390.2443 | 515.1459 |  | 247.0841 | 582.1038 | 212.6556 | 853.6468 | 465.3013 | 336.5782 |  | 260.4631 |  |  | 95.264 | 216.7295 | 411.6933 | [5 empty] | 21.8747 | 640.3162 | 21.7008 | 22.0831 | 182.2635 | 21.2783 | 21.9015 | 143.4355 | 566.3726 | 863.484 |  | 351.9873 | 568.8124 | 93.7707 | 328.4685 | 698.2745 | 437.329 | 754.7603 | 168.0295 | 385.4132 | 201.4714 | 495.0252 | 29.5599 | 293.7476 | 502.4417 | 140.1968 | 368.0598 | 680.3214 | 97.794 | 331.5207 | 590.7418 | 149.8811 | 392.1164 | 238.8581 | 513.6502 | 197.2367 | 533.5368 | 74.3564 | 16.2179 | 4.639 | 0.086061 | -27.2907 | 3.095 | 2908.94 | 25.41 | 3.2486 | -0.57068 | -12.3929 | 0.70093 | 3.6597 | -23.0233 | -5.119 | -3.293 | -7.1043 | 6.0731 | 0.20663 | -3.7508 | -4.3821 | -4.3898
42838.4278 | 647 | 22.8826 | 22.848 | 22.8281 | 22.7532 | 22.3515 | 21.6719 | 22.6753 | 21.7368 | 22.3339 | 22.3378 | 22.301 | 21.9487 | 21.1686 | 22.1459 | 21.593 | 21.7599 | 21.9272 | 21.0646 | 21.249 | 22.2724 | 20.489 | 22.4403 | 30.2454 | 22.0082 | 22.9963 | 36.8962 | 713.4417 | 529.5992 | 819.5841 | 22.1646 | 22.726 | 33.0873 | 22.1136 | 22.9941 | 39.1507 | 267.8075 | 725.7735 |  | 418.33 | 545.2999 | 469.2927 | 600.036 |  | 29.9476 | 43.2613 | 35.0824 | 50.7825 | 163.1022 | 293.6751 | 429.6587 | 17.2578 | 19.8538 | 18.6263 | 27.4636 | 19.7699 | 45.835 | 48.444 | 45.3117 | 22.0428 |  |  | 2.2384 | -0.56519 | -103.9309 | 0.14912 | 4.2471 | -197.8105 | -12.3147 | 8.9292 | 0.89603 | 2.8452 | 21.297 | 0.016091 | 0.017236 | 0.29389 | 22.1983 | 21.9665 | 22.155 | 22.1986 | 22.0086 | 21.2877 | 20.0942 | 22.1644 | 22.3491 | 22.3774 | 22.3256 | 21.9286 | 21.1593 | 22.2339 | 96.8301 | 94.9476 | 101.3943 | 83.2636 | 77.1366 | 96.7051 | 67.5921 | 22.3228 | 22.0805 | 21.674 | 22.0354 | 21.8124 | 22.0885 | 21.923 | 22.1934 | 31.0179 | 255.9059 | 745.3261 | 688.6376 | 588.4174 | 3.2178 | 3.1273 | 366.6584 | 21.8962 | 22.2006 | 34.0932 | 21.5454 | 22.0122 | 22.1869 | 24.0565 | 58.3366 | 21.8959 | 22.5051 | 33.1415 | 606.7879 | 820.8526 | 401.069 | 400.8342 | 529.1666 |  | 259.8219 | 602.3368 | 222.5217 | 883.1734 | 495.8269 | 352.7429 |  | 268.4724 |  |  | 100.5059 | 228.7267 | 432.6874 | [5 empty] | 21.8781 | 673.4899 | 21.7066 | 22.0892 | 194.8114 | 21.284 | 21.9089 | 152.6364 | 610.0791 | 883.7094 |  | 364.9393 | 574.0838 | 98.5414 | 340.5959 | 699.158 | 473.7896 | 798.4355 | 180.131 | 401.2067 | 215.4817 | 513.8784 | 30.3174 | 303.1017 | 508.0516 | 148.0641 | 391.7844 | 693.6086 | 102.755 | 344.8614 | 598.5477 | 160.7414 | 405.008 | 258.7947 | 544.3809 | 209.5905 | 550.5817 | 70.4737 | 16.1637 | 4.6624 | 0.08821 | -27.3288 | 3.095 | 3033.08 | 20.44 | 3.4466 | -0.93194 | -12.6376 | 0.4787 | 3.4193 | -23.3355 | -5.8224 | -2.9067 | -7.1278 | 9.0664 | 1.0471 | -2.9915 | -4.3731 | -4.7943
42838.4278 | 648 | 22.8783 | 22.8456 | 22.8315 | 22.7534 | 22.3509 | 21.6783 | 22.674 | 21.7272 | 22.333 | 22.3335 | 22.304 | 21.9494 | 21.165 | 22.1343 | 21.5991 | 21.7697 | 21.9327 | 21.074 | 21.2572 | 22.288 | 20.4897 | 22.4787 | 30.3199 | 22.0204 | 23.011 | 37.0605 | 737.5077 | 546.5392 | 842.5589 | 22.1593 | 22.7291 | 33.1826 | 22.1183 | 23.0064 | 39.4646 | 276.798 | 721.9651 |  | 428.0647 | 559.2424 | 478.3876 | 603.3099 |  | 30.5439 | 44.5492 | 35.9816 | 52.7713 | 170.3957 | 303.8547 | 439.1598 | 17.3295 | 19.9856 | 18.7445 | 27.889 | 19.7789 | 45.8231 | 48.4546 | 45.3672 | 22.0378 |  |  | 1.1798 | -0.44428 | -107.5109 | 0.34297 | 4.8082 | -197.8368 | -12.9265 | 9.5856 | 1.0531 | 2.7298 | 21.6206 | 0.015615 | 0.016962 | 0.29028 | 22.2033 | 21.9685 | 22.1489 | 22.1956 | 22.0055 | 21.2866 | 20.0961 | 22.1693 | 22.3509 | 22.3818 | 22.3365 | 21.9279 | 21.1664 | 22.2408 | 96.6117 | 89.1617 | 99.6348 | 79.0239 | 76.0603 | 96.8954 | 67.8475 | 22.3232 | 22.0836 | 21.6777 | 22.0467 | 21.816 | 22.1065 | 21.9294 | 22.2058 | 31.1025 | 271.7159 | 748.6514 | 714.9302 | 632.4586 | 2.8454 | 2.7707 | 375.443 | 21.9006 | 22.2007 | 34.5394 | 21.558 | 22.0192 | 22.1775 | 24.0652 | 59.0468 | 21.8892 | 22.5176 | 33.2503 | 609.9483 | 824.5202 | 410.3178 | 410.1773 | 539.7522 |  | 271.5393 | 596.6251 | 230.6635 | 897.3802 | 522.6859 | 363.7867 |  | 275.5135 |  |  | 106.1394 | 250.7026 | 448.0721 | [5 empty] | 21.8887 | 696.3489 | 21.7049 | 22.0997 | 207.026 | 21.2981 | 21.908 | 163.1795 | 656.0906 | 901.151 |  | 379.2129 | 577.3767 | 103.6621 | 354.1215 | 699.6878 | 513.0561 | 838.8821 | 192.3119 | 417.0448 | 230.9006 | 534.5475 | 31.0313 | 313.5511 | 510.6247 | 157.102 | 420.6351 | 706.4504 | 108.0221 | 361.9034 | 604.0058 | 170.8758 | 416.8272 | 285.0618 | 577.739 | 222.7161 | 563.1595 | 71.0072 | 16.1179 | 4.7127 | 0.095513 | -27.3367 | 3.095 | 3204.8 | 16.5 | 2.5284 | -0.82795 | -12.8796 | 0.72745 | 3.6707 | -23.5456 | -6.0186 | -2.4595 | -6.5125 | 12.3364 | 1.0947 | -2.7653 | -3.8833 | -5.0233
42838.4278 | 649 | 22.8805 | 22.8372 | 22.8312 | 22.7491 | 22.35 | 21.6673 | 22.6817 | 21.7336 | 22.3241 | 22.3321 | 22.2958 | 21.9494 | 21.1618 | 22.1378 | 21.5883 | 21.7644 | 21.9175 | 21.0726 | 21.2529 | 22.284 | 20.4875 | 22.5154 | 30.3706 | 22.0144 | 23.0181 | 37.2269 | 745.9751 | 560.2788 | 856.3676 | 22.1642 | 22.7364 | 33.2722 | 22.1134 | 23.0238 | 39.7874 | 285.3248 | 715.1439 |  | 437.0779 | 570.2208 | 484.5053 | 610.5773 |  | 31.181 | 45.889 | 36.8849 | 55.1208 | 179.8629 | 315.4446 | 449.0099 | 17.4236 | 20.1301 | 18.8663 | 28.3741 | 19.8134 | 45.8019 | 48.4815 | 45.4528 | 22.0629 |  |  | 1.4695 | -0.28985 | -110.7596 | 0.20366 | 6.108 | -197.8092 | -14.5161 | 11.1746 | 0.85439 | 2.7202 | 23.2229 | 0.015493 | 0.016648 | 0.29722 | 22.2016 | 21.9692 | 22.144 | 22.1963 | 22.0038 | 21.2864 | 20.0954 | 22.166 | 22.3557 | 22.3835 | 22.3332 | 21.9283 | 21.1593 | 22.2388 | 97.601 | 85.6688 | 94.2746 | 78.2319 | 72.3484 | 97.1506 | 68.0581 | 22.315 | 22.0793 | 21.6732 | 22.0427 | 21.8019 | 22.1082 | 21.9288 | 22.2035 | 31.1921 | 290.2865 | 757.5744 | 738.2721 | 653.8212 | 4.604 | 3.2777 | 383.5111 | 21.8971 | 22.1984 | 35.5535 | 21.5522 | 22.0021 | 22.1814 | 24.082 | 59.7763 | 21.8765 | 22.5186 | 33.3641 | 613.3353 | 827.2543 | 415.3914 | 416.3123 | 553.0941 |  | 283.0357 | 592.3023 | 238.8037 | 902.7869 | 547.9654 | 370.244 |  | 282.1488 |  |  | 111.8005 | 272.4761 | 466.4574 | [5 empty] | 21.8747 | 714.2274 | 21.7035 | 22.0776 | 220.2283 | 21.2799 | 21.8953 | 174.3685 | 704.2464 | 919.6768 |  | 393.185 | 580.2893 | 108.9099 | 368.7812 | 701.1019 | 554.2204 | 877.5999 | 205.6117 | 432.3977 | 247.4449 | 556.562 | 31.6777 | 323.46 | 513.1133 | 166.6181 | 454.8865 | 721.1779 | 113.2971 | 375.2128 | 609.0941 | 182.1088 | 429.4431 | 315.0022 | 609.623 | 235.3817 | 575.1038 | 81.7501 | 16.0634 | 4.7342 | 0.10046 | -27.4025 | 3.095 | 3398.22 | 12.82 | 2.8393 | -0.67016 | -13.1003 | 0.56175 | 4.1785 | -23.7793 | -6.4417 | -2.0758 | -5.9244 | 15.9189 | 1.0161 | -2.1444 | -3.5191 | -4.3839
42838.4278 | 650 | 22.8793 | 22.8418 | 22.8333 | 22.7464 | 22.3533 | 21.6747 | 22.688 | 21.7359 | 22.3314 | 22.3379 | 22.3039 | 21.9505 | 21.1638 | 22.1347 | 21.5955 | 21.7703 | 21.9269 | 21.0651 | 21.2598 | 22.2962 | 20.4901 | 22.5543 | 30.45 | 22.0142 | 23.0357 | 37.4084 | 752.1851 | 572.4674 | 871.3119 | 22.1678 | 22.7418 | 33.3503 | 22.1185 | 23.0248 | 40.1168 | 294.0059 | 722.5896 |  | 446.4197 | 579.2576 | 490.238 | 609.8574 |  | 31.8163 | 46.9999 | 37.6797 | 59.1381 | 191.3981 | 327.8446 | 458.6497 | 17.435 | 20.2741 | 18.9762 | 28.8507 | 19.8245 | 45.78 | 48.4848 | 45.5395 | 22.0426 |  |  | 2.4296 | -0.14135 | -114.0176 | 0.37911 | 6.0233 | -197.8368 | -16.0695 | 12.5453 | 0.75495 | 2.5943 | 23.8835 | 0.015278 | 0.016469 | 0.29024 | 22.2054 | 21.9726 | 22.1477 | 22.1978 | 21.9991 | 21.286 | 20.093 | 22.1684 | 22.3612 | 22.3798 | 22.3284 | 21.9297 | 21.1637 | 22.2399 | 109.9058 | 88.8229 | 93.4199 | 78.1318 | 72.6293 | 97.6985 | 68.3223 | 22.3272 | 22.0775 | 21.6875 | 22.0463 | 21.813 | 22.125 | 21.9287 | 22.217 | 31.2959 | 306.2838 | 772.6519 | 743.0225 | 666.7821 | 4.1506 | 3.9438 | 392.9 | 21.9041 | 22.2059 | 37.7657 | 21.5512 | 22.0162 | 22.1879 | 24.0953 | 60.5156 | 21.8959 | 22.5291 | 33.4939 | 620.0744 | 827.3408 | 421.3044 | 423.3294 | 559.5146 |  | 296.7698 | 595.4962 | 248.1185 | 913.6779 | 575.8838 | 376.6508 |  | 289.6544 |  |  | 116.7552 | 286.2729 | 477.1898 | [5 empty] | 21.878 | 726.8135 | 21.7074 | 22.0921 | 233.7309 | 21.292 | 21.9039 | 185.8712 | 749.8443 | 935.6086 |  | 408.4069 | 583.4866 | 114.2772 | 385.5996 | 702.3192 | 600.312 | 912.6792 | 217.5385 | 447.3945 | 264.0199 | 581.8257 | 32.3538 | 334.443 | 518.1138 | 175.9582 | 484.8727 | 732.9251 | 118.5813 | 389.2573 | 615.0606 | 193.5198 | 440.5992 | 343.4972 | 638.0371 | 246.5558 | 588.6863 | 78.5011 | 16.0183 | 4.7778 | 0.10235 | -27.4201 | 3.095 | 3589.15 | 12.51 | 3.6748 | -0.4688 | -13.3146 | 0.76776 | 4.1929 | -24.0301 | -6.8486 | -1.3166 | -5.4631 | 20.0802 | -0.28394 | -2.0177 | -2.907 | -3.6224
42838.4278 | 651 | 22.8896 | 22.851 | 22.8359 | 22.752 | 22.3574 | 21.6783 | 22.6822 | 21.737 | 22.3324 | 22.3388 | 22.3101 | 21.9549 | 21.1668 | 22.1457 | 21.5948 | 21.7733 | 21.9345 | 21.0708 | 21.2604 | 22.3051 | 20.5002 | 22.5924 | 30.5153 | 22.0182 | 23.041 | 37.616 | 774.68 | 583.8189 | 888.8685 | 22.1742 | 22.7513 | 33.4446 | 22.1238 | 23.0429 | 40.4663 | 302.4189 | 735.5604 |  | 456.2307 | 589.1847 | 495.2186 | 608.1717 |  | 32.2668 | 47.8043 | 38.3098 | 62.2478 | 200.2376 | 335.6151 | 464.6738 | 17.4402 | 20.3878 | 19.0356 | 29.2852 | 19.8361 | 45.7481 | 48.5041 | 45.636 | 22.0503 |  |  | 2.7358 | -0.066433 | -117.2007 | 0.35349 | 6.593 | -197.7855 | -16.565 | 16.1765 | 0.69598 | 2.456 | 23.7474 | 0.014875 | 0.015947 | 0.26911 | 22.2151 | 21.9716 | 22.1446 | 22.2023 | 22.0058 | 21.2899 | 20.1012 | 22.1768 | 22.352 | 22.3828 | 22.3332 | 21.9349 | 21.1682 | 22.2463 | 120.0462 | 93.0273 | 97.0387 | 80.2918 | 74.7372 | 98.1579 | 68.6121 | 22.3231 | 22.0805 | 21.6874 | 22.0423 | 21.8116 | 22.1246 | 21.9262 | 22.2217 | 31.389 | 321.9539 | 795.9707 | 748.632 | 695.9841 | 2.9347 | 1.6428 | 403.0435 | 21.8895 | 22.1975 | 38.3193 | 21.5528 | 22.0079 | 22.19 | 24.1156 | 61.3086 | 21.8867 | 22.5185 | 33.6237 | 623.3252 | 828.1849 | 427.4271 | 430.1624 | 563.4441 |  | 308.9235 | 600.9083 | 256.3271 | 917.7921 | 598.0899 | 382.9751 |  | 295.8972 |  |  | 120.9253 | 300.8346 | 478.411 | [5 empty] | 21.8773 | 738.341 | 21.7002 | 22.0887 | 245.0623 | 21.2848 | 21.8963 | 197.3755 | 803.1484 | 950.6441 |  | 422.38 | 586.3925 | 120.0057 | 405.6415 | 705.0156 | 647.3725 | 946.2151 | 229.2795 | 463.1559 | 280.2559 | 607.6283 | 32.9284 | 345.1387 | 521.6076 | 185.2561 | 517.8627 | 746.4922 | 124.0851 | 403.688 | 620.5298 | 203.0549 | 449.8907 | 371.0936 | 664.476 | 258.9593 | 604.2052 | 79.2737 | 15.9689 | 4.8091 | 0.10561 | -27.3944 | 3.095 | 3766.29 | 11.94 | 3.9293 | -0.3218 | -13.5162 | 0.74229 | 4.415 | -24.1818 | -6.9982 | -0.56131 | -5.1154 | 23.7882 | -1.3543 | -2.385 | -2.2705 | -3.2783
42838.4278 | 652 | 22.8821 | 22.8439 | 22.8253 | 22.7449 | 22.3522 | 21.6713 | 22.6799 | 21.7312 | 22.3295 | 22.3352 | 22.3051 | 21.9513 | 21.1636 | 22.1429 | 21.5907 | 21.7615 | 21.9258 | 21.0617 | 21.2559 | 22.3073 | 20.4891 | 22.6374 | 30.574 | 22.016 | 23.0472 | 37.8227 | 808.7681 | 593.7116 | 895.0449 | 22.1707 | 22.7518 | 33.5429 | 22.1256 | 23.0477 | 40.8242 | 311.1266 | 745.1209 |  | 466.4428 | 599.4164 | 501.5055 | 619.5607 |  | 32.6498 | 48.6256 | 38.9892 | 66.8995 | 210.9844 | 341.0565 | 470.8476 | 17.3695 | 20.5483 | 19.1531 | 29.8219 | 19.8618 | 45.7212 | 48.5246 | 45.7481 | 22.0641 |  |  | 2.2344 | -0.020437 | -120.7734 | 0.33771 | 6.2657 | -197.8125 | -17.8647 | 17.4014 | 0.94799 | 2.5114 | 23.5575 | 0.014264 | 0.015459 | 0.22559 | 22.213 | 21.9803 | 22.1434 | 22.2029 | 22.0077 | 21.2813 | 20.1054 | 22.1701 | 22.3581 | 22.3876 | 22.3352 | 21.9385 | 21.1667 | 22.2511 | 111.7048 | 85.29 | 93.5257 | 76.5699 | 73.9547 | 98.3928 | 68.7613 | 22.3213 | 22.0764 | 21.682 | 22.0378 | 21.8086 | 22.1219 | 21.9214 | 22.2201 | 31.4879 | 340.3083 | 820.9668 | 766.4603 | 750.9821 | 2.4432 | 2.2781 | 412.4272 | 21.9006 | 22.1957 | 38.8834 | 21.5531 | 22.0162 | 22.1844 | 24.1215 | 62.1149 | 21.8877 | 22.5305 | 33.7573 | 625.9868 | 829.4096 | 430.7856 | 434.0647 | 566.0579 |  | 320.9322 | 602.9583 | 264.7062 | 925.5505 | 619.0751 | 388.0792 |  | 301.9059 |  |  | 124.7236 | 314.7386 | 482.3993 | [5 empty] | 21.8779 | 746.2734 | 21.7077 | 22.0855 | 255.2333 | 21.29 | 21.8982 | 209.9791 | 852.4412 | 964.423 |  | 438.6776 | 589.2641 | 125.8076 | 424.2656 | 708.9006 | 696.9223 | 978.5382 | 241.3912 | 477.7243 | 296.1389 | 631.7097 | 33.5744 | 355.4107 | 526.18 | 195.5037 | 549.9441 | 760.2241 | 129.9272 | 420.8026 | 626.2367 | 212.0093 | 458.8447 | 402.9943 | 687.5077 | 271.7193 | 622.0353 | 73.5551 | 15.9196 | 4.8384 | 0.10731 | -27.3587 | 3.095 | 3892.09 | 9.06 | 3.5605 | -0.17871 | -13.7382 | 0.72647 | 4.3232 | -24.2913 | -7.3 | 0.25363 | -4.6508 | 27.4188 | -0.39863 | -1.9767 | -1.9598 | -3.3775
42838.4278 | 653 | 22.8818 | 22.8509 | 22.8238 | 22.7448 | 22.3529 | 21.6756 | 22.6852 | 21.7346 | 22.3351 | 22.3375 | 22.301 | 21.9471 | 21.1628 | 22.1402 | 21.5881 | 21.7639 | 21.9199 | 21.0616 | 21.2598 | 22.305 | 20.4878 | 22.6721 | 30.6443 | 22.015 | 23.0537 | 38.0455 | 838.9986 | 600.5678 | 896.8499 | 22.1715 | 22.7548 | 33.6248 | 22.1283 | 23.0544 | 41.2158 | 320.2171 | 720.5693 |  | 476.7395 | 609.3278 | 508.5198 | 627.3158 |  | 32.8862 | 49.281 | 39.4673 | 72.9861 | 219.3494 | 346.3227 | 476.1976 | 17.3612 | 20.6863 | 19.3415 | 30.2786 | 19.8703 | 45.6936 | 48.5428 | 45.8739 | 22.0744 |  |  | 2.1536 | 0.016363 | -124.1438 | 0.42839 | 6.4359 | -197.8506 | -18.7952 | 18.1157 | 0.78316 | 2.7693 | 23.526 | 0.014282 | 0.015347 | 0.21867 | 22.2184 | 21.9708 | 22.1461 | 22.1997 | 22.0037 | 21.2793 | 20.1003 | 22.1702 | 22.3584 | 22.3765 | 22.328 | 21.9303 | 21.1593 | 22.2439 | 99.8859 | 79.6037 | 88.0488 | 75.0755 | 73.6971 | 98.584 | 68.8983 | 22.3138 | 22.0695 | 21.6743 | 22.0348 | 21.8057 | 22.1208 | 21.9154 | 22.2199 | 31.5877 | 362.9803 | 836.9821 | 798.767 | 804.4583 | 2.4664 | 0.77472 | 416.6063 | 21.893 | 22.2008 | 40.2477 | 21.5425 | 22.0059 | 22.1865 | 24.1306 | 62.957 | 21.8839 | 22.5358 | 33.9022 | 630.1447 | 826.5942 | 433.6774 | 437.9571 | 565.5791 |  | 333.6967 | 599.6326 | 273.9418 | 933.059 | 641.879 | 394.6063 |  | 308.5331 |  |  | 128.0856 | 324.5588 | 487.2019 | [5 empty] | 21.8726 | 757.3657 | 21.7024 | 22.0758 | 267.7701 | 21.2746 | 21.8912 | 223.9069 | 900.2069 | 976.4286 |  | 456.2158 | 591.3022 | 131.5975 | 442.4811 | 711.844 | 735.7811 | 1001.8919 | 253.3172 | 493.2311 | 312.4105 | 651.7221 | 34.283 | 365.8688 | 532.3447 | 206.5924 | 576.9408 | 773.2221 | 136.1298 | 439.6209 | 631.8169 | 221.7833 | 467.8912 | 432.4106 | 712.1226 | 285.6663 | 638.2367 | 72.4044 | 15.8818 | 4.8841 | 0.1067 | -27.3979 | 3.095 | 4032.41 | 9.16 | 3.4982 | 0.16007 | -13.9427 | 0.81904 | 4.4003 | -24.3976 | -7.5197 | 1.2483 | -3.9674 | 31.6603 | 0.93805 | -1.3517 | -1.5018 | -2.9786
42838.4278 | 654 | 22.8833 | 22.8493 | 22.8381 | 22.7511 | 22.3604 | 21.6818 | 22.6849 | 21.7341 | 22.3368 | 22.3377 | 22.3097 | 21.953 | 21.168 | 22.1431 | 21.5879 | 21.7658 | 21.9236 | 21.0672 | 21.2615 | 22.3092 | 20.4896 | 22.7134 | 30.714 | 22.0148 | 23.0636 | 38.293 | 867.8054 | 607.8152 | 900.0864 | 22.1662 | 22.7628 | 33.7222 | 22.1228 | 23.0543 | 41.6073 | 329.358 | 635.8822 |  | 487.1635 | 619.5755 | 513.9799 | 632.9131 |  | 33.1832 | 50.0448 | 40.1146 | 79.1495 | 228.5883 | 352.6174 | 479.9259 | 17.4068 | 20.8225 | 19.4909 | 30.7906 | 19.8879 | 45.662 | 48.5564 | 46.0121 | 22.0721 |  |  | 3.7451 | 0.17736 | -127.7507 | 0.73133 | 7.5445 | -197.8092 | -20.4124 | 23.1511 | 0.73646 | 3.1052 | 24.5742 | 0.013951 | 0.015156 | 0.22854 | 22.2197 | 21.9719 | 22.146 | 22.1991 | 22.0036 | 21.2757 | 20.097 | 22.17 | 22.3538 | 22.3724 | 22.3248 | 21.9284 | 21.1592 | 22.2503 | 87.812 | 72.5717 | 78.3804 | 72.7526 | 75.4072 | 98.7318 | 68.9248 | 22.3265 | 22.0749 | 21.688 | 22.0442 | 21.814 | 22.1344 | 21.9249 | 22.2409 | 31.7229 | 387.5414 | 849.4729 | 837.9676 | 831.3953 | 2.9056 | 2.4121 | 423.0414 | 21.8845 | 22.1972 | 49.5584 | 21.5458 | 22.0054 | 22.1836 | 24.1478 | 63.8354 | 21.885 | 22.5332 | 34.0661 | 632.6428 | 822.1706 | 435.4136 | 440.921 | 561.3382 |  | 345.6412 | 602.1705 | 282.896 | 930.7733 | 662.2333 | 398.9173 |  | 314.7015 |  |  | 131.345 | 336.679 | 489.2177 | [5 empty] | 21.8683 | 763.0945 | 21.6981 | 22.0764 | 279.764 | 21.2707 | 21.8944 | 238.3987 | 942.4949 | 989.7236 |  | 475.0203 | 592.9512 | 137.6549 | 460.4201 | 714.1793 | 766.3093 | 1021.79 | 268.5096 | 508.4238 | 330.0702 | 669.8945 | 34.9319 | 376.652 | 539.0912 | 218.2629 | 601.8892 | 785.1311 | 142.5384 | 460.6571 | 637.7025 | 232.1507 | 477.7787 | 466.5491 | 736.8768 | 306.1663 | 654.7216 | 80.4623 | 15.8387 | 4.9118 | 0.10799 | -27.3191 | 3.095 | 4112.99 | 9.01 | 4.6195 | 0.52762 | -14.1606 | 1.0714 | 4.7884 | -24.5187 | -7.8763 | 2.3214 | -3.4484 | 35.9457 | 2.2978 | -0.27426 | -0.96013 | -1.5254
42838.4279 | 655 | 22.8838 | 22.8557 | 22.8352 | 22.7463 | 22.3624 | 21.6885 | 22.6927 | 21.7443 | 22.3429 | 22.3462 | 22.3191 | 21.9554 | 21.1728 | 22.1519 | 21.5887 | 21.7635 | 21.9326 | 21.0682 | 21.2636 | 22.3263 | 20.4929 | 22.7593 | 30.7997 | 22.0246 | 23.0838 | 38.5763 | 889.9474 | 614.2736 | 902.9236 | 22.2194 | 22.8615 | 33.8461 | 22.2821 | 24.3452 | 43.9657 | 342.2564 | 603.6311 |  | 498.7761 | 629.7944 | 521.102 | 649.0579 |  | 33.576 | 50.8411 | 41.2261 | 86.2056 | 238.0417 | 357.7284 | 481.7877 | 17.5062 | 20.9908 | 19.5137 | 31.3362 | 19.9233 | 45.6254 | 48.5788 | 46.1491 | 22.0726 |  |  | 3.2175 | 0.29827 | -131.4476 | 0.76681 | 6.5102 | -197.8526 | -21.5505 | 23.5553 | 0.92619 | 2.9081 | 26.2806 | 0.01328 | 0.014555 | 0.22099 | 22.2238 | 21.968 | 22.1436 | 22.1966 | 22.0048 | 21.2746 | 20.0976 | 22.1732 | 22.3518 | 22.3718 | 22.3303 | 21.9246 | 21.1626 | 22.2514 | 85.3824 | 73.2718 | 79.1419 | 69.1644 | 73.1897 | 99.0259 | 69.0585 | 22.3268 | 22.0779 | 21.6975 | 22.0498 | 21.8159 | 22.1411 | 21.9364 | 22.2494 | 31.8444 | 409.1467 | 866.2306 | 871.3438 | 833.3013 | 2.6453 | 2.2343 | 427.006 | 21.8941 | 22.1915 | 61.3283 | 21.5484 | 22.0075 | 22.1779 | 24.1625 | 64.7444 | 21.8835 | 22.5459 | 34.2332 | 635.408 | 817.7595 | 437.782 | 443.7257 | 564.5235 |  | 356.8583 | 601.4512 | 291.0576 | 916.5437 | 678.5258 | 403.178 |  | 320.2859 |  |  | 134.6199 | 353.5412 | 493.3423 | [5 empty] | 21.8669 | 761.3422 | 21.6966 | 22.0807 | 291.1498 | 21.2797 | 21.8933 | 253.1818 | 982.0171 | 1000.7676 |  | 495.0089 | 595.1193 | 144.2717 | 481.6795 | 715.3495 | 800.9396 | 1043.0946 | 284.8561 | 523.951 | 351.7166 | 687.5903 | 35.6076 | 386.5283 | 545.9577 | 232.0062 | 631.5236 | 796.2701 | 149.5843 | 488.3411 | 644.5505 | 242.3555 | 487.4871 | 502.8405 | 762.7872 | 334.6225 | 670.6895 | 83.2599 | 15.7968 | 4.9589 | 0.11298 | -27.4839 | 3.095 | 4200.01 | 5.69 | 4.2869 | 0.68507 | -14.3817 | 1.0984 | 4.4662 | -24.6213 | -8.1258 | 3.1639 | -2.8764 | 39.8976 | 2.6038 | -0.34279 | -0.38963 | 0.50579
42838.4279 | 656 | 22.8854 | 22.8453 | 22.8277 | 22.7425 | 22.3568 | 21.6786 | 22.6801 | 21.7268 | 22.3231 | 22.3297 | 22.3003 | 21.9566 | 21.1627 | 22.1355 | 21.5865 | 21.7625 | 21.9261 | 21.0609 | 21.2605 | 22.3261 | 20.483 | 22.7951 | 30.8809 | 22.0207 | 23.0916 | 38.8579 | 897.272 | 619.3663 | 897.9674 | 26.7236 | 29.0348 | 38.4605 | 30.2914 | 37.6038 | 63.7263 | 374.7445 | 523.3196 |  | 522.362 | 647.5932 | 537.4517 | 679.0639 |  | 33.8523 | 51.5112 | 41.8719 | 92.1306 | 246.0343 | 361.338 | 483.1127 | 17.5356 | 21.1392 | 19.4844 | 31.8344 | 19.9578 | 45.6022 | 48.5995 | 46.3047 | 22.1009 |  |  | 2.9323 | 0.23256 | -135.1531 | 0.39817 | 8.4723 | -197.8558 | -23.5823 | 23.9942 | 1.0215 | 2.897 | 27.3322 | 0.013139 | 0.014386 | 0.17445 | 22.2192 | 21.9667 | 22.1414 | 22.2051 | 22.0048 | 21.2741 | 20.0936 | 22.1676 | 22.3549 | 22.37 | 22.3282 | 21.9203 | 21.1631 | 22.2401 | 77.4295 | 67.9511 | 79.0419 | 69.3337 | 74.9654 | 99.2266 | 69.2031 | 22.3311 | 22.0822 | 21.6983 | 22.0556 | 21.814 | 22.1542 | 21.9356 | 22.2619 | 31.9596 | 430.056 | 870.28 | 884.2651 | 834.6663 | 3.1777 | 4.9802 | 433.0242 | 21.9019 | 22.2107 | 66.9138 | 21.5591 | 22.0111 | 22.1905 | 24.1892 | 65.701 | 21.8968 | 22.5654 | 34.4276 | 637.5185 | 814.4788 | 437.8342 | 444.3523 | 574.3399 |  | 368.9019 | 607.6488 | 300.374 | 911.4172 | 695.2766 | 409.6004 |  | 326.2908 |  |  | 137.9789 | 371.7458 | 498.7633 | [5 empty] | 21.8718 | 760.7664 | 21.6957 | 22.0802 | 304.6498 | 21.2787 | 21.8917 | 269.0567 | 1010.8611 | 1011.0479 |  | 511.9178 | 598.3268 | 151.845 | 505.2449 | 716.6874 | 834.7482 | 1060.3214 | 298.0498 | 539.1835 | 379.0472 | 703.9897 | 36.858 | 396.2215 | 551.5026 | 248.5497 | 663.0665 | 807.5172 | 157.803 | 521.6379 | 650.8693 | 252.9265 | 496.4909 | 538.0359 | 786.7551 | 365.8533 | 686.4031 | 80.3766 | 15.7602 | 5.0026 | 0.11866 | -27.4302 | 3.095 | 4314.82 | 5.82 | 4.0839 | 0.60554 | -14.5981 | 0.79235 | 5.1095 | -24.6918 | -8.5246 | 3.9287 | -2.4008 | 43.8673 | 3.5121 | -0.31429 | 1.5375 | 2.6256
42838.4279 | 657 | 22.8849 | 22.8493 | 22.8389 | 22.7526 | 22.3612 | 21.6796 | 22.6855 | 21.7353 | 22.3295 | 22.3361 | 22.306 | 21.9573 | 21.169 | 22.1425 | 21.5979 | 21.7648 | 21.9284 | 21.0623 | 21.2607 | 22.3339 | 20.4843 | 22.8447 | 30.9693 | 22.0211 | 23.1002 | 39.162 | 899.0796 | 626.4036 | 896.4186 | 47.0154 | 54.849 | 64.5842 | 62.985 | 61.8873 | 83.2775 | 396.2358 | 522.5334 |  | 565.7151 | 695.0389 | 576.6785 | 702.6841 |  | 34.1913 | 52.3022 | 43.3857 | 100.969 | 255.753 | 366.7299 | 486.3806 | 17.5875 | 21.3275 | 19.4712 | 32.4394 | 19.988 | 45.5832 | 48.6276 | 46.4444 | 22.107 |  |  | 2.1746 | -0.50604 | -137.7743 | 0.17212 | 8.377 | -197.7954 | -25.3138 | 25.4346 | 1.0433 | 3.0519 | 29.4087 | 0.013091 | 0.01421 | 0.14071 | 22.2217 | 21.964 | 22.1404 | 22.1936 | 21.996 | 21.2734 | 20.0872 | 22.1608 | 22.3483 | 22.3713 | 22.3192 | 21.92 | 21.1557 | 22.2329 | 76.3481 | 65.947 | 85.9677 | 74.0057 | 76.0356 | 99.4566 | 69.4656 | 22.3246 | 22.0785 | 21.6914 | 22.0486 | 21.8061 | 22.1587 | 21.9281 | 22.257 | 32.0929 | 452.156 | 873.6349 | 891.7146 | 833.6089 | 3.0921 | 1.4165 | 442.9028 | 21.8996 | 22.1996 | 71.7226 | 21.5532 | 22.0094 | 22.1945 | 24.1987 | 66.689 | 21.898 | 22.5614 | 34.6256 | 638.9539 | 810.019 | 441.7879 | 449.8104 | 589.2719 |  | 381.8526 | 616.5472 | 310.9 | 909.0306 | 712.5527 | 418.0886 |  | 333.238 |  |  | 143.7461 | 388.2696 | 505.9162 | [5 empty] | 21.878 | 761.6739 | 21.7002 | 22.0831 | 322.366 | 21.2749 | 21.8897 | 287.278 | 1033.5684 | 1020.4831 |  | 526.4447 | 601.4511 | 160.9166 | 527.9031 | 721.057 | 865.6408 | 1075.9489 | 313.4223 | 553.5928 | 411.5479 | 719.5843 | 39.1185 | 407.1233 | 556.1069 | 267.1615 | 693.6877 | 818.9596 | 167.609 | 555.0375 | 655.1662 | 266.6377 | 507.1958 | 570.6902 | 811.1581 | 400.1603 | 701.2095 | 85.357 | 15.741 | 5.0342 | 0.12084 | -27.386 | 3.095 | 4471.41 | 5.44 | 3.5146 | -0.89435 | -14.7569 | 0.52159 | 5.1022 | -24.7927 | -8.8694 | 4.6749 | -1.8926 | 48.0685 | 3.6605 | -1.0523 | 2.8714 | 5.0957
42838.4279 | 658 | 22.885 | 22.8473 | 22.8406 | 22.752 | 22.3582 | 21.6802 | 22.6877 | 21.7376 | 22.3349 | 22.3423 | 22.3031 | 21.9544 | 21.1669 | 22.1396 | 21.5969 | 21.7626 | 21.9295 | 21.0607 | 21.2621 | 22.3411 | 20.4866 | 22.8893 | 31.064 | 22.02 | 23.1083 | 39.4986 | 894.4007 | 633.0591 | 890.3847 | 64.3812 | 76.1486 | 91.2317 | 79.8736 | 84.6958 | 102.8131 | 426.9563 | 501.6132 |  | 588.884 | 716.3424 | 602.2804 | 727.5511 |  | 34.4687 | 52.9154 | 48.8657 | 110.058 | 265.0776 | 372.235 | 490.3632 | 17.6438 | 21.4781 | 19.5557 | 32.9405 | 20.0034 | 45.5651 | 48.6337 | 46.5758 | 22.1189 |  |  | 1.6746 | -0.55467 | -137.6035 | 0.3226 | 8.4947 | -197.8184 | -26.4769 | 27.6373 | 0.81839 | 3.0691 | 38.2402 | 0.012664 | 0.013877 | 0.18069 | 22.2269 | 21.9619 | 22.144 | 22.1864 | 21.9992 | 21.2773 | 20.0921 | 22.1595 | 22.3432 | 22.3658 | 22.3201 | 21.918 | 21.1564 | 22.232 | 70.6318 | 60.9784 | 77.1051 | 72.8818 | 77.3784 | 99.624 | 69.5193 | 22.3415 | 22.0854 | 21.6954 | 22.0516 | 21.8189 | 22.1663 | 21.9242 | 22.2832 | 32.257 | 474.9622 | 870.9678 | 889.1515 | 829.9895 | 3.1161 | 1.7147 | 447.8795 | 21.9026 | 22.2062 | 77.865 | 21.5494 | 22.0149 | 22.1986 | 24.2166 | 67.7099 | 21.8975 | 22.5689 | 34.8458 | 638.4277 | 803.733 | 448.6227 | 457.5919 | 604.4786 |  | 393.0492 | 618.7147 | 319.9031 | 902.7395 | 725.9389 | 422.3877 |  | 339.075 |  |  | 158.4171 | 401.8599 | 512.4603 | [5 empty] | 21.8789 | 760.9048 | 21.7051 | 22.088 | 361.9852 | 21.282 | 21.89 | 307.7799 | 1049.1009 | 1027.1859 |  | 544.2911 | 603.4286 | 172.7674 | 551.4878 | 724.3815 | 891.7515 | 1091.2886 | 334.8943 | 568.5826 | 449.6436 | 734.4991 | 41.8146 | 417.3738 | 561.0178 | 288.6635 | 723.2364 | 828.3697 | 182.901 | 589.0781 | 658.5522 | 280.6052 | 517.9868 | 603.3658 | 835.7961 | 435.1431 | 717.9636 | 85.7033 | 15.6979 | 5.0633 | 0.12282 | -27.2529 | 3.095 | 4600.2 | 5.61 | 3.0761 | -0.93721 | -14.7616 | 0.71474 | 5.16 | -24.9006 | -9.1098 | 5.2956 | -1.2865 | 51.5825 | 4.3162 | -0.061084 | 5.2721 | 7.8984
42838.4279 | 659 | 22.8781 | 22.8489 | 22.833 | 22.7527 | 22.3558 | 21.6752 | 22.6826 | 21.7287 | 22.3322 | 22.3349 | 22.3058 | 21.953 | 21.1662 | 22.1341 | 21.591 | 21.7562 | 21.9257 | 21.0557 | 21.2544 | 22.346 | 20.4861 | 22.9191 | 31.1397 | 22.0189 | 23.1091 | 39.8373 | 887.0429 | 639.2094 | 883.9557 | 83.9845 | 80.7519 | 97.6064 | 87.14 | 88.3044 | 105.5687 | 441.1039 | 485.9694 |  | 568.6169 | 729.4405 | 583.396 | 726.2641 |  | 34.7197 | 53.5499 | 52.0734 | 122.9579 | 274.0839 | 377.461 | 492.8547 | 17.7044 | 21.6511 | 19.7486 | 33.531 | 20.0329 | 45.5529 | 48.6478 | 46.7025 | 22.1275 |  |  | 1.4925 | -0.11112 | -142.1809 | 0.55916 | 8.3731 | -197.8335 | -26.9809 | 32.4323 | 1.1671 | 3.0802 | 51.5855 | 0.012554 | 0.013647 | 0.15636 | 22.2376 | 21.9683 | 22.1458 | 22.2024 | 21.9987 | 21.2787 | 20.0956 | 22.1786 | 22.3572 | 22.3741 | 22.3337 | 21.9292 | 21.1694 | 22.239 | 65.8876 | 58.798 | 71.9184 | 70.9974 | 73.7261 | 99.836 | 69.5782 | 22.3338 | 22.0796 | 21.6871 | 22.047 | 21.8198 | 22.163 | 21.9203 | 22.2774 | 32.4095 | 498.2392 | 867.0256 | 884.6899 | 828.2521 | 4.2238 | 1.7147 | 453.418 | 21.8882 | 22.1908 | 79.2103 | 21.5389 | 21.9947 | 22.1833 | 24.2224 | 68.7276 | 21.8812 | 22.567 | 35.0543 | 639.0196 | 798.7343 | 453.2073 | 463.5537 | 608.4148 |  | 404.4247 | 614.5648 | 328.2797 | 890.6751 | 737.2754 | 428.1966 |  | 344.8412 |  |  | 176.5328 | 417.9031 | 518.6679 | [5 empty] | 21.8726 | 758.2271 | 21.7074 | 22.0817 | 433.5074 | 21.2853 | 21.8961 | 333.4437 | 1056.9367 | 1030.5033 |  | 564.6966 | 605.1271 | 188.0355 | 576.9206 | 728.8241 | 911.3134 | 1103.7499 | 356.2537 | 585.3641 | 485.2645 | 751.5933 | 45.2934 | 428.1044 | 569.3377 | 314.6318 | 752.2762 | 835.3488 | 203.8656 | 624.077 | 661.7086 | 293.1711 | 531.4971 | 633.8628 | 858.7822 | 470.4285 | 737.1367 | 91.9125 | 15.6553 | 5.1091 | 0.12439 | -27.4219 | 3.095 | 4704.5 | 5.48 | 2.8961 | -0.41989 | -15.0197 | 0.94191 | 5.1436 | -25.0022 | -9.2333 | 6.2848 | -0.53375 | 54.8406 | 4.8694 | 0.52228 | 6.8357 | 10.909
42838.4279 | 660 | 22.8851 | 22.8513 | 22.8306 | 22.7489 | 22.3578 | 21.6822 | 22.6845 | 21.7284 | 22.3363 | 22.3351 | 22.3053 | 21.9548 | 21.1656 | 22.1429 | 21.5926 | 21.7561 | 21.9347 | 21.0641 | 21.2685 | 22.3671 | 20.4898 | 22.9705 | 31.2482 | 22.0222 | 23.1291 | 40.2132 | 883.666 | 644.2345 | 882.3468 | 84.8628 | 84.15 | 86.5723 | 89.6613 | 87.8458 | 111.5396 | 449.7308 | 493.5558 |  | 485.7825 | 740.8714 | 504.207 | 728.8082 |  | 35.0363 | 54.342 | 53.5192 | 132.3868 | 283.1331 | 382.7848 | 496.1723 | 17.7725 | 21.8396 | 19.8779 | 34.1339 | 20.0561 | 45.5263 | 48.6592 | 46.8121 | 22.1411 |  |  | 1.6686 | -0.15975 | -145.0361 | 0.41854 | 8.1536 | -197.8177 | -29.7217 | 33.8694 | 1.0433 | 3.4438 | 49.5417 | 0.0126 | 0.013451 | 0.16819 | 22.2358 | 21.9793 | 22.1493 | 22.2012 | 22.0039 | 21.2772 | 20.0957 | 22.1664 | 22.3529 | 22.3677 | 22.3339 | 21.9275 | 21.1648 | 22.2365 | 67.3929 | 61.6954 | 69.3111 | 68.0221 | 74.1221 | 100.2078 | 69.6372 | 22.3349 | 22.0806 | 21.6866 | 22.0426 | 21.8189 | 22.1738 | 21.9244 | 22.2975 | 32.5805 | 518.7065 | 862.4359 | 880.5906 | 831.9833 | 4.5631 | 4.5203 | 455.51 | 21.8966 | 22.1991 | 83.1566 | 21.5545 | 22.0084 | 22.1926 | 24.2335 | 69.7869 | 21.8961 | 22.5778 | 35.3073 | 639.4694 | 794.2694 | 454.1505 | 465.1065 | 607.9376 |  | 417.7193 | 615.0948 | 338.1046 | 876.0549 | 749.0592 | 435.1525 |  | 351.7995 |  |  | 200.8455 | 435.5689 | 522.0264 | [5 empty] | 21.8716 | 755.9252 | 21.7058 | 22.0865 | 476.5153 | 21.2825 | 21.8978 | 360.8973 | 1058.3948 | 1029.1933 |  | 584.3074 | 608.1992 | 203.1358 | 607.4231 | 735.0972 | 929.7411 | 1110.563 | 373.6555 | 602.3996 | 513.5152 | 770.1474 | 50.623 | 441.5883 | 578.9955 | 345.2115 | 781.0265 | 842.4033 | 230.7203 | 653.175 | 666.9506 | 306.0921 | 548.3356 | 666.3391 | 887.4911 | 508.0683 | 753.2179 | 96.1586 | 15.6127 | 5.1275 | 0.12304 | -27.3774 | 3.095 | 4764.01 | 5.28 | 3.0601 | -0.50406 | -15.1882 | 0.8159 | 5.0965 | -25.1032 | -9.7305 | 7.6333 | 0.22121 | 58.3797 | 4.7478 | 0.81909 | 7.7307 | 13.5909
42838.4279 | 661 | 22.8855 | 22.8433 | 22.8283 | 22.7523 | 22.3557 | 21.6795 | 22.674 | 21.7312 | 22.3342 | 22.3316 | 22.303 | 21.9517 | 21.1628 | 22.1364 | 21.5921 | 21.7653 | 21.9337 | 21.0666 | 21.2724 | 22.3634 | 20.4978 | 23.0276 | 31.3493 | 22.0335 | 23.1407 | 40.6069 | 880.2802 | 648.2587 | 879.6218 | 67.2427 | 52.5709 | 44.213 | 70.5109 | 90.4541 | 107.7839 | 383.9674 | 481.5099 |  | 560.726 | 704.5577 | 549.7355 | 695.0499 |  | 35.3645 | 55.0712 | 56.1703 | 142.0068 | 291.5218 | 387.4439 | 499.3705 | 17.845 | 22.0187 | 19.9638 | 34.7017 | 20.078 | 45.5077 | 48.6669 | 46.9099 | 22.1504 |  |  | 1.9584 | -0.29708 | -144.4289 | 0.43234 | 8.3133 | -197.8184 | -31.6182 | 32.4152 | 1.1562 | 3.4811 | 41.923 | 0.012148 | 0.013072 | 0.094953 | 22.2409 | 21.9701 | 22.1435 | 22.1948 | 21.999 | 21.2794 | 20.0916 | 22.1679 | 22.3594 | 22.3727 | 22.3312 | 21.9197 | 21.1641 | 22.2393 | 70.1654 | 73.1764 | 82.5033 | 66.3791 | 70.9199 | 100.5515 | 69.8416 | 22.3402 | 22.0917 | 21.6969 | 22.0507 | 21.8225 | 22.177 | 21.9301 | 22.3113 | 32.7746 | 538.6465 | 855.2785 | 875.1977 | 848.2942 | 2.9024 | 2.1753 | 459.3834 | 21.893 | 22.1922 | 93.6845 | 21.5511 | 21.9976 | 22.1948 | 24.2536 | 70.8234 | 21.8932 | 22.5872 | 35.5618 | 641.4249 | 789.4333 | 454.1485 | 465.5438 | 610.9146 |  | 429.0813 | 620.9173 | 347.0726 | 866.9744 | 757.9099 | 441.4347 |  | 358.3188 |  |  | 222.5343 | 446.7829 | 526.5985 | [5 empty] | 21.8834 | 751.6856 | 21.7152 | 22.0872 | 506.06 | 21.2942 | 21.9022 | 394.1314 | 1058.1146 | 1025.1626 |  | 601.3869 | 614.8031 | 218.8996 | 634.8221 | 737.9571 | 955.8679 | 1109.6294 | 387.8351 | 616.1209 | 536.992 | 782.29 | 57.5567 | 455.7321 | 591.4272 | 379.8255 | 811.3823 | 845.606 | 261.3483 | 675.6195 | 670.4796 | 319.4683 | 563.615 | 700.4409 | 913.9285 | 541.8574 | 766.3546 | 100.472 | 15.5645 | 5.1468 | 0.12386 | -27.4982 | 3.095 | 4800.07 | 2.4 | 3.3113 | -0.68816 | -15.1732 | 0.83016 | 5.1644 | -25.1923 | -10.0717 | 8.7372 | 0.78342 | 61.0499 | 4.4821 | -0.62213 | 1.9308 | 16.0234
42838.4279 | 662 | 22.8838 | 22.8554 | 22.8357 | 22.7531 | 22.3583 | 21.6843 | 22.687 | 21.7322 | 22.3271 | 22.3365 | 22.3068 | 21.9583 | 21.1652 | 22.1441 | 21.6056 | 21.7702 | 21.9335 | 21.0706 | 21.2829 | 22.3786 | 20.4987 | 23.0734 | 31.4612 | 22.0365 | 23.1477 | 41.0513 | 876.9104 | 653.6249 | 876.5016 | 43.3375 | 35.3488 | 55.6568 | 54.3791 | 56.3044 | 82.6185 | 431.252 | 561.9042 |  | 584.3487 | 721.6238 | 586.8954 | 689.162 |  | 35.6864 | 55.8844 | 59.0543 | 155.0284 | 307.1251 | 396.6082 | 503.0676 | 17.8657 | 22.214 | 20.0369 | 35.397 | 20.1033 | 45.4864 | 48.6713 | 46.9878 | 22.1461 |  |  | 1.8316 | -0.83 | -141.5908 | 0.24309 | 7.5964 | -197.8223 | -35.5274 | 30.4353 | 1.2467 | 3.3028 | 45.9888 | 0.01193 | 0.012965 | 0.011067 | 22.2431 | 21.963 | 22.1391 | 22.1936 | 21.9975 | 21.2805 | 20.0881 | 22.1643 | 22.3624 | 22.3684 | 22.33 | 21.9094 | 21.1613 | 22.228 | 69.4788 | 75.2071 | 82.6241 | 67.9164 | 69.546 | 100.7897 | 69.9728 | 22.3334 | 22.0894 | 21.6935 | 22.0452 | 21.8184 | 22.1775 | 21.92 | 22.316 | 32.9764 | 559.6645 | 846.211 | 871.3126 | 870.3419 | 3.3351 | 2.443 | 466.2166 | 21.8943 | 22.1993 | 104.1429 | 21.5523 | 22.0071 | 22.1993 | 24.272 | 71.846 | 21.8868 | 22.5943 | 35.8394 | 642.0989 | 784.342 | 454.3421 | 466.8735 | 614.5002 |  | 440.1546 | 626.0079 | 356.1146 | 862.6982 | 765.715 | 445.7082 |  | 364.562 |  |  | 239.073 | 452.6485 | 532.0018 | [5 empty] | 21.876 | 748.3374 | 21.7109 | 22.0754 | 525.2563 | 21.2902 | 21.9027 | 448.3117 | 1076.4163 | 1017.1811 |  | 613.0981 | 617.9132 | 235.1063 | 659.1111 | 739.9229 | 982.3998 | 1115.0136 | 404.4783 | 625.9025 | 561.6809 | 794.115 | 64.6362 | 468.9939 | 602.1698 | 420.9863 | 844.5119 | 850.4838 | 296.9316 | 693.1512 | 670.9338 | 332.5402 | 571.5729 | 727.8557 | 939.4276 | 571.2549 | 776.6806 | 103.6042 | 15.5166 | 5.1683 | 0.12521 | -27.4055 | 3.095 | 4829.48 | 2.13 | 3.1979 | -1.1517 | -15.042 | 0.62326 | 4.9708 | -25.3667 | -10.75 | 9.8356 | 1.3933 | 63.3479 | 4.5876 | -0.61978 | 6.7952 | 18.6458
42838.428 | 663 | 22.8906 | 22.8517 | 22.8363 | 22.7508 | 22.3582 | 21.6829 | 22.6905 | 21.7352 | 22.3434 | 22.3341 | 22.3026 | 21.9518 | 21.169 | 22.142 | 21.5877 | 21.7604 | 21.9294 | 21.0624 | 21.2717 | 22.3756 | 20.4904 | 23.1174 | 31.5759 | 22.0181 | 23.1463 | 41.5068 | 871.8607 | 657.3768 | 871.9788 | 50.4458 | 51.5235 | 70.516 | 54.5838 | 67.4275 | 91.5008 | 462.6399 | 537.623 |  | 598.3118 | 724.2687 | 570.5185 | 673.282 |  | 35.8435 | 56.493 | 60.2715 | 163.899 | 315.9431 | 405.9459 | 504.1581 | 17.8727 | 22.3866 | 20.028 | 35.9517 | 20.1269 | 45.4797 | 48.6837 | 47.0426 | 22.1622 |  |  | 2.4368 | -0.69135 | -144.7213 | 0.043982 | 7.7291 | -197.8243 | -38.5626 | 28.1419 | 0.95052 | 2.8735 | 47.1119 | 0.01182 | 0.012774 | 0.00041563 | 22.2449 | 21.967 | 22.1405 | 22.1995 | 22.0009 | 21.2823 | 20.0942 | 22.1706 | 22.3593 | 22.3705 | 22.3343 | 21.9178 | 21.1654 | 22.2269 | 74.5631 | 72.9028 | 80.3179 | 66.3503 | 67.5843 | 101.0931 | 70.0889 | 22.3404 | 22.088 | 21.6924 | 22.0446 | 21.8184 | 22.1855 | 21.9189 | 22.3284 | 33.2327 | 581.7467 | 835.9267 | 861.3363 | 872.6806 | 2.7274 | 1.8608 | 470.2369 | 21.9054 | 22.2042 | 110.3688 | 21.5497 | 22.0175 | 22.1952 | 24.2914 | 72.8423 | 21.8889 | 22.6041 | 36.1266 | 644.2938 | 777.5711 | 454.7868 | 468.3189 | 620.9043 |  | 452.6791 | 630.6679 | 365.8201 | 849.4262 | 772.6633 | 447.9087 |  | 370.6768 |  |  | 256.9648 | 462.558 | 536.8507 | [5 empty] | 21.8742 | 743.1447 | 21.6982 | 22.084 | 535.3719 | 21.2874 | 21.8978 | 507.1948 | 1088.5106 | 1004.9444 |  | 622.437 | 619.2398 | 255.9989 | 681.0313 | 743.5253 | 987.2086 | 1109.4966 | 420.1831 | 634.7171 | 594.9488 | 802.6549 | 70.2267 | 477.1791 | 609.6553 | 466.5109 | 857.8241 | 856.2202 | 333.1835 | 707.1502 | 672.4175 | 345.0539 | 578.5533 | 749.1765 | 946.4745 | 594.9797 | 784.3688 | 96.1482 | 15.4634 | 5.1895 | 0.12728 | -27.3163 | 3.095 | 4848.66 | 2.2 | 3.6813 | -1.0521 | -15.2214 | 0.26535 | 5.0489 | -25.543 | -11.2776 | 11.064 | 2.0947 | 65.6942 | 4.06 | -0.34956 | 10.7676 | 22.2042
42838.428 | 664 | 22.8894 | 22.8544 | 22.8397 | 22.7538 | 22.3651 | 21.6811 | 22.6828 | 21.7364 | 22.3348 | 22.3382 | 22.3047 | 21.9549 | 21.1683 | 22.1383 | 21.5904 | 21.7614 | 21.932 | 21.0677 | 21.2698 | 22.3784 | 20.4972 | 23.1594 | 31.6966 | 22.0274 | 23.15 | 41.993 | 875.0005 | 657.2325 | 877.0457 | 46.1101 | 46.0425 | 66.1591 | 54.1801 | 57.7175 | 84.2398 | 461.3783 | 526.0977 |  | 614.81 | 730.6685 | 584.9321 | 628.5174 |  | 36.0971 | 57.0998 | 60.1678 | 169.0342 | 323.9714 | 414.4873 | 505.1014 | 17.8524 | 22.5495 | 19.9763 | 36.5386 | 20.1529 | 45.4685 | 48.6987 | 47.0926 | 22.1737 |  |  | 2.381 | -0.64207 | -141.9996 | 0.21746 | 8.3639 | -197.8118 | -39.5141 | 27.5972 | 0.92542 | 2.6876 | 44.5129 | 0.011705 | 0.012697 | 0.00039098 | 22.2486 | 21.9757 | 22.1409 | 22.2017 | 21.9977 | 21.2834 | 20.0913 | 22.1727 | 22.3662 | 22.374 | 22.3346 | 21.9259 | 21.172 | 22.2389 | 72.5914 | 71.6191 | 75.095 | 63.9321 | 65.7414 | 101.2604 | 70.1243 | 22.3446 | 22.0907 | 21.7005 | 22.0467 | 21.8251 | 22.1969 | 21.9238 | 22.3512 | 33.511 | 598.7289 | 820.515 | 846.2463 | 858.9826 | 3.793 | 1.2198 | 477.2089 | 21.8995 | 22.1957 | 114.2015 | 21.54 | 22.0004 | 22.2027 | 24.3053 | 73.8014 | 21.8972 | 22.5992 | 36.4368 | 643.9205 | 769.089 | 456.9735 | 471.6396 | 625.3848 |  | 464.5631 | 633.4274 | 375.2073 | 826.8114 | 777.0187 | 451.3482 |  | 376.6521 |  |  | 270.9717 | 468.4161 | 541.7381 | [5 empty] | 21.8656 | 730.9748 | 21.6952 | 22.073 | 539.5125 | 21.2808 | 21.8963 | 556.8438 | 1092.8527 | 990.7709 |  | 627.8228 | 622.3404 | 284.1453 | 696.0961 | 743.6406 | 987.0949 | 1101.9749 | 435.2749 | 637.431 | 616.1241 | 805.5894 | 72.94 | 484.0061 | 612.4359 | 501.0218 | 864.8136 | 855.217 | 366.6602 | 716.0455 | 674.3244 | 355.0196 | 584.3025 | 758.6813 | 960.7488 | 610.845 | 787.8085 | 87.9771 | 15.4324 | 5.21 | 0.12921 | -27.4486 | 3.095 | 4883.97 | 2.17 | 3.6469 | -1.0148 | -15.0915 | 0.59058 | 5.2851 | -25.7023 | -11.4874 | 12.3259 | 2.8466 | 67.5804 | 4.2997 | 0.23501 | 11.8623 | 25.5355
42838.428 | 665 | 22.89 | 22.8562 | 22.8319 | 22.753 | 22.3628 | 21.6805 | 22.6877 | 21.7407 | 22.335 | 22.3392 | 22.3047 | 21.9516 | 21.1712 | 22.1384 | 21.5995 | 21.773 | 21.9419 | 21.076 | 21.2684 | 22.3915 | 20.5056 | 23.2292 | 31.8282 | 22.0402 | 23.1716 | 42.5262 | 883.643 | 661.3911 | 885.7645 | 39.5279 | 39.0702 | 72.4748 | 54.4863 | 60.8501 | 89.3481 | 476.6637 | 534.7986 |  | 634.924 | 742.945 | 610.9108 | 564.5801 |  | 36.3285 | 57.6255 | 61.1943 | 172.5694 | 335.02 | 420.6558 | 505.4389 | 17.8591 | 22.7139 | 19.977 | 37.0978 | 20.1673 | 45.4488 | 48.7018 | 47.1678 | 22.1757 |  |  | 2.5393 | -0.26685 | -140.0906 | 0.29434 | 8.1089 | -197.8598 | -40.6075 | 25.8598 | 0.99664 | 3.0305 | 44.6969 | 0.011347 | 0.012298 | 0.00040084 | 22.2395 | 21.9667 | 22.1417 | 22.19 | 22.0024 | 21.2723 | 20.0898 | 22.167 | 22.366 | 22.3683 | 22.3323 | 21.9239 | 21.1642 | 22.2409 | 68.5548 | 72.8791 | 70.2589 | 61.4085 | 65.2012 | 101.4767 | 70.1744 | 22.3375 | 22.0853 | 21.7027 | 22.0485 | 21.8137 | 22.1986 | 21.9268 | 22.3604 | 33.8005 | 611.3884 | 802.5572 | 826.05 | 827.7511 | 3.8746 | 3.6079 | 480.987 | 21.8947 | 22.1961 | 122.0492 | 21.5476 | 22.0129 | 22.205 | 24.3312 | 74.7558 | 21.8948 | 22.607 | 36.7706 | 644.2389 | 760.5819 | 457.957 | 472.3273 | 626.493 |  | 474.9718 | 630.4848 | 383.4704 | 807.581 | 779.3903 | 451.4706 |  | 381.7552 |  |  | 285.852 | 472.8939 | 547.232 | [5 empty] | 21.8677 | 719.2736 | 21.6928 | 22.077 | 545.11 | 21.283 | 21.8891 | 596.4143 | 1094.2103 | 980.6238 |  | 632.8272 | 622.5867 | 317.8763 | 709.7788 | 743.1108 | 987.231 | 1099.5421 | 451.3776 | 642.3593 | 639.1909 | 808.7098 | 73.6475 | 491.5061 | 613.5079 | 527.7333 | 870.3674 | 860.121 | 396.5594 | 723.6108 | 675.691 | 362.8893 | 588.7028 | 769.8773 | 969.6201 | 630.6455 | 790.8362 | 90.3543 | 15.3926 | 5.2492 | 0.12923 | -27.397 | 3.095 | 4970.86 | 2.11 | 3.7805 | -0.65474 | -15.0016 | 0.68764 | 5.2272 | -25.8205 | -11.6974 | 13.5523 | 3.6785 | 68.8055 | 4.7748 | 0.77839 | 15.4803 | 28.6996
42838.428 | 666 | 22.8878 | 22.854 | 22.8301 | 22.7475 | 22.3572 | 21.6775 | 22.6842 | 21.7365 | 22.3336 | 22.3339 | 22.3025 | 21.9519 | 21.1644 | 22.1393 | 21.5972 | 21.772 | 21.9331 | 21.0625 | 21.266 | 22.3924 | 20.4935 | 23.2746 | 31.958 | 22.0385 | 23.1775 | 43.1059 | 885.3697 | 667.3445 | 886.5545 | 62.7025 | 66.9435 | 81.0793 | 64.9968 | 74.3704 | 105.0973 | 497.0359 | 523.0831 |  | 649.8894 | 743.2599 | 612.346 | 520.1155 |  | 36.4581 | 57.9469 | 63.077 | 177.5998 | 341.3037 | 424.3933 | 506.8963 | 17.8826 | 22.8574 | 20.0181 | 37.5892 | 20.2055 | 45.4462 | 48.7211 | 47.2406 | 22.1736 |  |  | 2.1661 | -0.45282 | -142.9609 | 0.23717 | 7.718 | -197.8519 | -42.475 | 23.2944 | 1.0511 | 2.7892 | 49.6709 | 0.010719 | 0.011968 | 0.00075897 | 22.2525 | 21.9631 | 22.1392 | 22.1946 | 21.9949 | 21.2785 | 20.0895 | 22.1696 | 22.3734 | 22.3699 | 22.3254 | 21.9073 | 21.1706 | 22.2367 | 69.7687 | 72.4577 | 72.6998 | 63.8754 | 66.7443 | 101.7232 | 70.2912 | 22.3364 | 22.0863 | 21.6986 | 22.0487 | 21.8232 | 22.2034 | 21.9252 | 22.376 | 34.1091 | 620.8936 | 783.2346 | 803.9338 | 799.762 | 3.1802 | 1.4516 | 483.4112 | 21.8834 | 22.1917 | 127.4102 | 21.5342 | 21.9927 | 22.1935 | 24.3312 | 75.7032 | 21.8803 | 22.6117 | 37.1153 | 644.4142 | 753.8781 | 460.72 | 475.234 | 621.9119 |  | 485.0715 | 626.6756 | 391.7067 | 792.0981 | 780.7693 | 453.4228 |  | 387.0766 |  |  | 299.3326 | 475.0988 | 549.2141 | [5 empty] | 21.8675 | 708.6019 | 21.702 | 22.0758 | 554.3439 | 21.2779 | 21.8948 | 637.1982 | 1092.3076 | 978.8781 |  | 637.646 | 624.7419 | 337.6758 | 723.0275 | 743.461 | 982.2601 | 1096.6584 | 473.2726 | 648.1333 | 651.1826 | 811.8916 | 74.4505 | 498.1004 | 614.2984 | 542.6517 | 882.032 | 867.1935 | 432.3187 | 734.0068 | 676.4832 | 369.6609 | 591.4086 | 769.6238 | 974.8339 | 659.8802 | 795.8126 | 93.6236 | 15.3553 | 5.3091 | 0.12995 | -27.366 | 3.095 | 5092.34 | 2.17 | 3.4928 | -0.85331 | -15.1619 | 0.61756 | 5.1133 | -25.8894 | -11.9955 | 14.9388 | 4.552 | 69.6393 | 4.6702 | 0.52123 | 19.3099 | 31.2572
42838.428 | 667 | 22.8808 | 22.8443 | 22.83 | 22.7455 | 22.3509 | 21.6753 | 22.6752 | 21.7266 | 22.3224 | 22.3292 | 22.3012 | 21.9506 | 21.1613 | 22.1374 | 21.5968 | 21.7678 | 21.9396 | 21.0638 | 21.2714 | 22.4032 | 20.4848 | 23.3329 | 32.0954 | 22.0371 | 23.181 | 43.7317 | 881.1711 | 671.1141 | 881.7885 | 83.8017 | 80.614 | 95.0688 | 82.9585 | 84.5556 | 103.7055 | 507.9645 | 505.3567 |  | 667.306 | 763.836 | 622.8234 | 514.4121 |  | 36.6476 | 58.3618 | 67.0746 | 184.635 | 348.3869 | 429.8546 | 508.6215 | 17.9219 | 23.0504 | 19.9694 | 38.1814 | 20.2412 | 45.4331 | 48.7537 | 47.3079 | 22.1912 |  |  | 0.58243 | -0.96405 | -144.9802 | -0.03027 | 7.3868 | -197.8506 | -44.4773 | 22.0669 | 0.76195 | 2.7449 | 45.8139 | 0.010977 | 0.011933 | 0.0012617 | 22.2482 | 21.9629 | 22.1438 | 22.1971 | 21.996 | 21.275 | 20.0975 | 22.1688 | 22.3685 | 22.3659 | 22.3288 | 21.9151 | 21.1662 | 22.2427 | 71.9887 | 70.1201 | 69.3298 | 62.4941 | 68.5881 | 101.9612 | 70.3253 | 22.3371 | 22.0814 | 21.6884 | 22.0378 | 21.8186 | 22.2065 | 21.9133 | 22.3795 | 34.4323 | 628.9606 | 766.132 | 785.1971 | 770.0357 | 3.6751 | 2.2242 | 488.4712 | 21.899 | 22.2 | 132.0717 | 21.55 | 22.0036 | 22.2117 | 24.3583 | 76.6603 | 21.8952 | 22.6275 | 37.4951 | 644.5027 | 751.2071 | 462.755 | 477.316 | 624.3516 |  | 496.3802 | 623.4148 | 400.3519 | 778.9591 | 781.4859 | 459.2149 |  | 393.4326 |  |  | 308.3621 | 481.0262 | 555.5261 | [5 empty] | 21.8672 | 701.454 | 21.7058 | 22.0798 | 566.0008 | 21.2817 | 21.8975 | 672.4513 | 1079.7633 | 981.0432 |  | 643.3876 | 627.3138 | 359.0258 | 736.1583 | 746.9536 | 974.3394 | 1085.5771 | 496.0614 | 654.8013 | 664.5001 | 816.1203 | 75.5947 | 503.0003 | 617.1085 | 552.4995 | 888.1739 | 871.4165 | 463.6024 | 748.3948 | 677.9682 | 377.6377 | 596.614 | 768.011 | 973.2877 | 691.8561 | 802.1086 | 96.0675 | 15.3285 | 5.379 | 0.132 | -27.1398 | 3.0951 | 5163.7 | 2.27 | 1.8075 | -1.2459 | -15.2782 | -0.22076 | 5.022 | -25.9905 | -12.323 | 16.3284 | 5.4702 | 70.2146 | 4.4529 | 0.89977 | 20.9286 | 33.6323
42838.428 | 668 | 22.8914 | 22.8506 | 22.8404 | 22.7505 | 22.353 | 21.6786 | 22.6882 | 21.7298 | 22.3308 | 22.3429 | 22.3079 | 21.9484 | 21.1686 | 22.1401 | 21.6008 | 21.7682 | 21.9366 | 21.0671 | 21.2786 | 22.4106 | 20.4933 | 23.3971 | 32.2498 | 22.0438 | 23.1882 | 44.4097 | 872.7777 | 671.3604 | 874.4266 | 89.3245 | 75.3871 | 98.7075 | 88.4758 | 84.3126 | 107.8479 | 516.3695 | 521.433 |  | 673.5563 | 770.7879 | 633.2071 | 511.461 |  | 36.7618 | 58.8066 | 66.5987 | 189.3423 | 351.1568 | 431.6809 | 509.413 | 17.9076 | 23.1987 | 19.9541 | 38.6674 | 20.2858 | 45.4208 | 48.7771 | 47.3684 | 22.2067 |  |  | 0.49833 | -0.54153 | -144.5209 | 0.082754 | 7.0024 | -197.8611 | -46.6346 | 18.4337 | 0.86392 | 2.8964 | 42.7321 | 0.010808 | 0.011822 | 0.0004337 | 22.2639 | 21.9723 | 22.1474 | 22.1964 | 22.0104 | 21.2815 | 20.0996 | 22.1741 | 22.3831 | 22.3781 | 22.3318 | 21.9142 | 21.1695 | 22.2499 | 81.0034 | 69.7581 | 72.931 | 59.8701 | 67.4627 | 102.3221 | 70.4786 | 22.3354 | 22.082 | 21.6991 | 22.0427 | 21.8248 | 22.2095 | 21.921 | 22.383 | 34.8663 | 636.1789 | 748.6972 | 764.6099 | 753.2049 | 4.8781 | 3.0946 | 490.9989 | 21.9026 | 22.1937 | 134.6261 | 21.5493 | 22.004 | 22.216 | 24.3712 | 77.5902 | 21.8918 | 22.634 | 37.8951 | 646.3182 | 750.8898 | 464.6365 | 479.2505 | 630.5755 |  | 506.4713 | 624.3603 | 407.7835 | 774.0232 | 781.9427 | 461.7799 |  | 398.8667 |  |  | 318.9321 | 492.162 | 562.6648 | [5 empty] | 21.8681 | 699.8237 | 21.7052 | 22.0824 | 567.4244 | 21.2811 | 21.8939 | 705.4875 | 1062.1995 | 984.3375 |  | 650.3687 | 629.8422 | 378.3172 | 747.8916 | 750.5991 | 964.6042 | 1069.3341 | 519.0496 | 660.154 | 682.5125 | 820.6737 | 77.1997 | 510.1887 | 622.0958 | 559.2162 | 887.3807 | 868.7148 | 485.3058 | 764.5308 | 681.3082 | 385.724 | 601.3563 | 763.697 | 966.7247 | 713.1274 | 813.1128 | 98.4264 | 15.2987 | 5.4781 | 0.13197 | -27.4105 | 3.0951 | 5265.78 | 2.18 | 1.6665 | -0.93437 | -15.2642 | 0.36526 | 4.8959 | -26.0249 | -12.6347 | 17.4995 | 6.1739 | 70.486 | 3.4957 | 0.51808 | 22.1674 | 35.5167
42838.428 | 669 | 22.8819 | 22.8426 | 22.8361 | 22.745 | 22.3545 | 21.6668 | 22.6825 | 21.7291 | 22.3293 | 22.3371 | 22.299 | 21.9495 | 21.1592 | 22.1359 | 21.5944 | 21.7681 | 21.9301 | 21.0665 | 21.2746 | 22.4125 | 20.4918 | 23.4533 | 32.4112 | 22.0445 | 23.1965 | 45.1435 | 871.3329 | 669.863 | 873.7797 | 87.746 | 82.8772 | 103.5974 | 93.151 | 86.0196 | 115.1517 | 519.9442 | 524.3016 |  | 676.2086 | 768.5813 | 636.5138 | 516.7532 |  | 36.9381 | 59.2676 | 66.0939 | 193.1001 | 353.4818 | 437.6761 | 510.9399 | 17.8701 | 23.3561 | 19.9166 | 39.1935 | 20.3027 | 45.3945 | 48.7946 | 47.4446 | 22.2211 |  |  | 0.73029 | -0.78663 | -142.9294 | 0.24375 | 7.3335 | -197.7862 | -45.9788 | 16.5892 | 0.79465 | 2.8202 | 46.2862 | 0.010361 | 0.011431 | 0.00040084 | 22.2695 | 21.9778 | 22.1493 | 22.1997 | 22.0026 | 21.2841 | 20.1022 | 22.1799 | 22.3817 | 22.3803 | 22.3366 | 21.9208 | 21.17 | 22.2476 | 93.3823 | 73.0934 | 77.0089 | 59.0223 | 63.7328 | 102.7834 | 70.6472 | 22.3409 | 22.0844 | 21.6965 | 22.0464 | 21.8265 | 22.2223 | 21.9297 | 22.4034 | 35.2674 | 641.6586 | 735.875 | 751.3182 | 740.9117 | 3.2787 | 3.5691 | 495.5081 | 21.9081 | 22.2072 | 138.8183 | 21.5505 | 22.0077 | 22.2214 | 24.394 | 78.4796 | 21.9033 | 22.6427 | 38.313 | 648.5613 | 748.4659 | 466.6377 | 481.2917 | 639.6029 |  | 516.492 | 628.2905 | 415.1891 | 769.9519 | 782.1813 | 464.4365 |  | 403.9226 |  |  | 326.9435 | 504.619 | 571.987 | [5 empty] | 21.8748 | 696.9974 | 21.7035 | 22.0874 | 567.9626 | 21.2865 | 21.8929 | 733.2439 | 1041.7937 | 985.5119 |  | 657.0152 | 631.2278 | 392.328 | 756.2803 | 754.1065 | 952.3772 | 1050.1611 | 539.941 | 663.891 | 700.3659 | 824.9612 | 79.813 | 518.616 | 626.8993 | 563.8483 | 878.9169 | 866.1415 | 512.579 | 779.5822 | 685.3591 | 392.7653 | 607.042 | 757.1031 | 957.7784 | 729.271 | 827.6537 | 92.1652 | 15.2674 | 5.5951 | 0.13404 | -27.46 | 3.0951 | 5317.72 | 2.36 | 2.0169 | -1.1269 | -15.1904 | 0.6273 | 5.0316 | -26.1304 | -12.5987 | 18.6249 | 6.8095 | 70.6693 | 2.177 | 0.085272 | 22.5214 | 36.9533
42838.428 | 670 | 22.888 | 22.8513 | 22.8394 | 22.7472 | 22.3629 | 21.6823 | 22.6862 | 21.7374 | 22.3404 | 22.34 | 22.3081 | 21.9592 | 21.1598 | 22.1319 | 21.5994 | 21.7693 | 21.9369 | 21.0712 | 21.2747 | 22.4243 | 20.4985 | 23.5232 | 32.5793 | 22.0448 | 23.208 | 45.9395 | 872.988 | 668.6909 | 875.1222 | 81.4841 | 83.8052 | 36.0028 | 92.3917 | 75.5711 | 132.9682 | 396.5053 | 496.1943 |  | 600.7673 | 761.7775 | 655.2492 | 479.6151 |  | 37.0987 | 59.6855 | 66.3047 | 195.3712 | 354.8448 | 440.1783 | 513.1213 | 17.853 | 23.512 | 19.8861 | 39.7223 | 20.3184 | 45.3794 | 48.822 | 47.5227 | 22.2394 |  |  | 1.0424 | -0.61578 | -144.3915 | 0.24243 | 7.5675 | -197.8309 | -48.876 | 16.6247 | 1.0947 | 2.8991 | 49.5131 | 0.010578 | 0.011478 | 0.00038606 | 22.2683 | 21.9761 | 22.1496 | 22.1918 | 22.0016 | 21.2816 | 20.0975 | 22.1739 | 22.382 | 22.3769 | 22.3401 | 21.9278 | 21.1752 | 22.2513 | 91.877 | 75.5739 | 81.3581 | 63.3559 | 63.1935 | 103.0644 | 70.8296 | 22.3448 | 22.0862 | 21.7012 | 22.0435 | 21.8238 | 22.2264 | 21.9228 | 22.4168 | 35.7138 | 645.7516 | 723.9153 | 737.0302 | 719.4143 | 3.4588 | 2.8892 | 501.954 | 21.8998 | 22.1981 | 143.3628 | 21.552 | 22.0017 | 22.21 | 24.4041 | 79.2828 | 21.9017 | 22.649 | 38.7569 | 649.8966 | 744.3924 | 466.0256 | 480.3622 | 645.3335 |  | 527.818 | 633.8205 | 423.579 | 760.5417 | 781.6459 | 466.038 |  | 409.3999 |  |  | 334.9913 | 515.5561 | 582.84 | [5 empty] | 21.8789 | 691.4575 | 21.7078 | 22.0862 | 571.1111 | 21.2899 | 21.8921 | 749.5966 | 1022.1929 | 986.8802 |  | 663.9459 | 632.002 | 412.9214 | 764.9477 | 757.6299 | 938.3512 | 1030.8037 | 558.4522 | 667.4809 | 718.4387 | 828.925 | 82.0589 | 524.0072 | 630.4081 | 567.1752 | 867.6308 | 870.2671 | 541.9982 | 801.6594 | 690.5897 | 400.9882 | 610.5556 | 750.2144 | 947.4438 | 742.4834 | 845.5173 | 91.8623 | 15.2382 | 5.7513 | 0.13633 | -27.5144 | 3.0951 | 5356.56 | 2.69 | 2.4111 | -0.99769 | -15.2775 | 0.626 | 5.1202 | -26.1793 | -13.0125 | 20.0726 | 7.5209 | 70.7732 | 2.3789 | -0.37602 | 9.0936 | 38.3797
42838.428 | 671 | 22.8815 | 22.8412 | 22.84 | 22.7477 | 22.3498 | 21.6707 | 22.6785 | 21.7261 | 22.3315 | 22.3293 | 22.297 | 21.9512 | 21.1582 | 22.1271 | 21.6023 | 21.7704 | 21.9409 | 21.0736 | 21.2757 | 22.4285 | 20.4955 | 23.5944 | 32.7541 | 22.0403 | 23.2136 | 46.7846 | 872.252 | 668.0434 | 874.9386 | 60.6809 | 60.001 | 45.9451 | 26.3107 | 63.8252 | 150.992 | 171.5772 | 511.6769 |  | 236.8975 | 519.9592 | 643.4747 | 482.3009 |  | 37.2016 | 60.0631 | 66.9425 | 200.8475 | 357.5654 | 442.1367 | 512.6681 | 17.8394 | 23.6593 | 19.8923 | 40.212 | 20.3358 | 45.3503 | 48.8425 | 47.5838 | 22.2485 |  |  | 1.141 | -0.49553 | -145.6939 | 0.16949 | 7.3073 | -197.825 | -50.7797 | 14.3024 | 0.94799 | 3.0691 | 55.4346 | 0.010471 | 0.011339 | 0.00039756 | 22.2706 | 21.9729 | 22.1443 | 22.1925 | 21.9984 | 21.2785 | 20.0925 | 22.1704 | 22.3839 | 22.3799 | 22.3344 | 21.9276 | 21.1708 | 22.2579 | 87.2767 | 77.2977 | 82.9741 | 68.1209 | 65.4452 | 103.2935 | 71.0148 | 22.3476 | 22.0878 | 21.7098 | 22.0512 | 21.8226 | 22.2367 | 21.9237 | 22.4337 | 36.1955 | 648.658 | 713.2483 | 722.9905 | 701.0218 | 3.0027 | 1.5656 | 505.9794 | 21.893 | 22.193 | 144.8371 | 21.5422 | 22.0057 | 22.2122 | 24.4245 | 80.0145 | 21.8972 | 22.6502 | 39.2271 | 651.7303 | 742.841 | 465.7236 | 479.2121 | 649.791 |  | 537.6308 | 631.7647 | 430.6057 | 756.2604 | 780.9724 | 470.2907 |  | 414.5366 |  |  | 340.4715 | 526.9933 | 592.5685 | [5 empty] | 21.8736 | 687.4504 | 21.7081 | 22.0825 | 569.1548 | 21.2882 | 21.8964 | 762.1977 | 1002.6823 | 982.7844 |  | 671.1888 | 634.2802 | 431.4878 | 776.3294 | 761.6651 | 923.3062 | 1011.4655 | 577.4181 | 672.6649 | 736.1182 | 834.4545 | 83.1482 | 527.036 | 633.4858 | 570.6239 | 854.5779 | 874.6342 | 567.9747 | 827.4524 | 696.1106 | 411.0639 | 613.9048 | 743.7124 | 933.9109 | 759.219 | 862.883 | 102.4695 | 15.2007 | 5.9317 | 0.13917 | -27.4604 | 3.0951 | 5365 | 2.55 | 2.5223 | -0.89549 | -15.355 | 0.52372 | 5.0383 | -26.2149 | -13.2817 | 21.3862 | 8.3204 | 70.6944 | 2.9183 | -0.53329 | -6.4132 | 39.4852
42838.4281 | 672 | 22.891 | 22.8448 | 22.8364 | 22.7505 | 22.3594 | 21.6735 | 22.6825 | 21.7305 | 22.3327 | 22.3343 | 22.3027 | 21.9522 | 21.1683 | 22.1382 | 21.5973 | 21.7644 | 21.9361 | 21.0678 | 21.2743 | 22.4299 | 20.4888 | 23.6598 | 32.9441 | 22.0468 | 23.2205 | 47.6656 | 865.1908 | 670.4756 | 868.0514 | 84.8467 | 52.6871 | 61.5853 | 31.8539 | 53.4593 | 149.5518 | 240.7136 | 517.5403 |  | 324.9759 | 227.3346 | 594.1409 | 462.9386 |  | 37.3216 | 60.5135 | 67.3822 | 207.772 | 362.4226 | 446.4958 | 512.5897 | 17.8764 | 23.8395 | 19.9861 | 40.8094 | 20.3569 | 45.3245 | 48.8582 | 47.6359 | 22.3084 |  |  | 1.5727 | -0.64535 | -146.8188 | -0.06247 | 7.5747 | -197.8322 | -52.0972 | 14.2288 | 0.83512 | 3.1874 | 57.4846 | 0.009791 | 0.010814 | 0.00039427 | 22.2808 | 21.9803 | 22.145 | 22.2018 | 22.0009 | 21.2793 | 20.0933 | 22.172 | 22.3885 | 22.3847 | 22.3393 | 21.9278 | 21.1713 | 22.2568 | 81.7907 | 69.8007 | 81.7669 | 69.0969 | 66.0558 | 103.4507 | 71.1888 | 22.3368 | 22.0877 | 21.697 | 22.045 | 21.823 | 22.2359 | 21.9199 | 22.4473 | 36.7206 | 650.9486 | 703.0756 | 709.2699 | 684.9283 | 4.2963 | 2.1991 | 509.4748 | 21.9019 | 22.1976 | 145.7811 | 21.5431 | 22.0018 | 22.2073 | 24.4467 | 80.7038 | 21.9048 | 22.662 | 39.7154 | 654.4991 | 741.9903 | 465.9682 | 479.3629 | 654.561 |  | 547.436 | 637.8056 | 437.7356 | 756.8441 | 780.4334 | 474.3583 |  | 419.7492 |  |  | 347.3923 | 534.33 | 603.9628 | [5 empty] | 21.8756 | 684.7841 | 21.7069 | 22.0781 | 572.2041 | 21.2926 | 21.8986 | 772.3588 | 981.8335 | 971.8275 |  | 679.0635 | 636.5288 | 444.8955 | 794.0504 | 768.817 | 906.8837 | 990.9216 | 599.1092 | 679.7602 | 755.1728 | 844.3162 | 84.2786 | 531.5213 | 636.4659 | 573.9728 | 841.8567 | 871.6713 | 590.6176 | 846.2962 | 702.4413 | 419.712 | 619.2193 | 737.2954 | 918.8756 | 771.9958 | 874.0095 | 111.6304 | 15.1599 | 6.1228 | 0.14232 | -27.4829 | 3.0951 | 5377.75 | 2.81 | 2.9524 | -1.0226 | -15.4245 | -0.31817 | 5.1453 | -26.2951 | -13.4938 | 22.733 | 8.9229 | 70.5201 | 3.5472 | -0.37822 | -2.2195 | 40.4043
42838.4281 | 673 | 22.8979 | 22.8475 | 22.835 | 22.7495 | 22.3566 | 21.6856 | 22.6856 | 21.7302 | 22.3381 | 22.3408 | 22.2989 | 21.9515 | 21.1683 | 22.1445 | 21.594 | 21.7636 | 21.9384 | 21.0674 | 21.2739 | 22.4378 | 20.4892 | 23.7409 | 33.1523 | 22.0378 | 23.2302 | 48.5918 | 856.3286 | 672.817 | 860.3178 | 48.1882 | 26.4665 | 80.3241 | 41.6038 | 23.2789 | 116.61 | 158.224 | 513.5438 |  | 433.3709 | 343.6614 | 483.8368 | 442.1476 |  | 37.4836 | 60.9184 | 68.3046 | 214.4911 | 369.6953 | 449.5062 | 514.431 | 17.9148 | 23.9883 | 20.0011 | 41.3189 | 20.3723 | 45.3071 | 48.8731 | 47.6731 | 22.3397 |  |  | 1.9052 | -0.89177 | -143.9032 | 0.048582 | 7.5287 | -197.8604 | -54.0666 | 13.4712 | 1.1659 | 3.3007 | 54.8159 | 0.0096087 | 0.010803 | 0.0004107 | 22.2731 | 21.9666 | 22.1421 | 22.2025 | 21.9994 | 21.2769 | 20.0899 | 22.1826 | 22.3831 | 22.3703 | 22.3395 | 21.9335 | 21.1732 | 22.263 | 83.1125 | 66.4381 | 81.4345 | 67.7362 | 66.9389 | 103.7277 | 71.3481 | 22.3382 | 22.0793 | 21.6967 | 22.0418 | 21.8114 | 22.2361 | 21.9174 | 22.4546 | 37.3206 | 652.4098 | 691.7108 | 694.3917 | 670.1541 | 4.4329 | 1.8433 | 516.6662 | 21.904 | 22.1961 | 147.2538 | 21.5442 | 21.9981 | 22.2213 | 24.4613 | 81.3299 | 21.8966 | 22.6661 | 40.2353 | 659.2155 | 739.1349 | 466.7104 | 480.8144 | 663.5782 |  | 558.9607 | 646.9817 | 446.1591 | 750.3778 | 779.43 | 480.3503 |  | 425.4174 |  |  | 354.049 | 544.3352 | 620.6242 | [5 empty] | 21.8739 | 680.8874 | 21.7116 | 22.0818 | 591.1611 | 21.2918 | 21.8942 | 779.2568 | 961.251 | 958.2238 |  | 689.1194 | 640.0685 | 458.0486 | 815.9518 | 776.3888 | 890.4845 | 971.0928 | 623.4666 | 690.553 | 773.2599 | 860.8795 | 86.3496 | 537.876 | 639.6247 | 575.4621 | 829.7853 | 863.8564 | 613.4702 | 852.3423 | 711.7326 | 427.0507 | 624.979 | 730.6226 | 904.3179 | 778.6713 | 877.8972 | 106.2005 | 15.087 | 6.3291 | 0.14872 | -27.552 | 3.0951 | 5390.99 | 2.6 | 3.2385 | -1.2029 | -15.2799 | 0.28075 | 5.1404 | -26.3519 | -13.7752 | 24.2776 | 9.6007 | 70.4061 | 3.4345 | -0.32211 | -5.9234 | 41.1174
42838.4281 | 674 | 22.8921 | 22.8397 | 22.8333 | 22.744 | 22.3533 | 21.6761 | 22.6763 | 21.729 | 22.3255 | 22.3332 | 22.2894 | 21.9548 | 21.1623 | 22.1383 | 21.5955 | 21.7717 | 21.9381 | 21.0653 | 21.2734 | 22.4369 | 20.4907 | 23.8164 | 33.3516 | 22.0356 | 23.2369 | 49.5315 | 846.3868 | 674.7133 | 849.7922 | 20.6679 | 29.9773 | 50.7995 | 53.6708 | 23.6834 | 106.2603 | 92.1184 | 514.5068 |  | 295.9998 | 442.4908 | 564.2046 | 438.7255 |  | 37.6861 | 61.3881 | 68.7835 | 219.1568 | 373.8295 | 455.3099 | 518.5016 | 17.9144 | 24.1707 | 20.0123 | 41.8913 | 20.3873 | 45.283 | 48.8874 | 47.7215 | 22.3399 |  |  | 2.0149 | -0.43968 | -147.1744 | 0.06501 | 8.6123 | -197.8302 | -53.4732 | 12.2351 | 1.1621 | 3.2073 | 56.2654 | 0.0096202 | 0.010672 | 0.0004107 | 22.2793 | 21.9755 | 22.1451 | 22.2013 | 22.0003 | 21.2876 | 20.0986 | 22.1825 | 22.3797 | 22.381 | 22.3432 | 21.9329 | 21.1749 | 22.2644 | 91.8501 | 75.4424 | 82.4472 | 67.0763 | 66.1636 | 104.2964 | 71.5025 | 22.3431 | 22.0848 | 21.6971 | 22.0468 | 21.8194 | 22.2432 | 21.9201 | 22.4751 | 37.9018 | 653.192 | 682.7143 | 682.5191 | 656.5305 | 6.4015 | 4.4389 | 524.6649 | 21.8987 | 22.193 | 148.7548 | 21.544 | 21.9997 | 22.2179 | 24.4837 | 81.91 | 21.8943 | 22.6633 | 40.7818 | 665.046 | 738.1642 | 468.2816 | 483.2462 | 670.5736 |  | 570.3625 | 663.7438 | 455.6868 | 747.7793 | 778.6549 | 490.5496 |  | 431.8245 |  |  | 363.0865 | 556.593 | 636.7626 | [5 empty] | 21.8617 | 680.4598 | 21.7018 | 22.0772 | 625.9076 | 21.2784 | 21.8888 | 775.9323 | 941.2819 | 945.4982 |  | 704.4024 | 645.8087 | 469.8351 | 832.4938 | 784.7765 | 875.5068 | 952.142 | 646.0732 | 700.8454 | 789.0495 | 877.445 | 88.6742 | 543.3328 | 640.9507 | 576.2245 | 817.6045 | 856.0002 | 635.7131 | 852.9714 | 720.1152 | 434.3394 | 627.3428 | 723.5907 | 889.3842 | 787.7115 | 881.9841 | 107.4363 | 15.0086 | 6.5674 | 0.15537 | -27.443 | 3.0951 | 5431.4 | 2.55 | 3.315 | -0.84519 | -15.4634 | 0.325 | 5.5199 | -26.4555 | -13.7543 | 25.9208 | 10.2201 | 70.252 | 2.5337 | -0.41605 | -8.6186 | 41.6584
42838.4281 | 675 | 22.8957 | 22.8483 | 22.8346 | 22.7518 | 22.3635 | 21.6797 | 22.6915 | 21.7314 | 22.3325 | 22.3388 | 22.3075 | 21.9571 | 21.1729 | 22.1456 | 21.5971 | 21.7699 | 21.9385 | 21.0626 | 21.2732 | 22.4396 | 20.4908 | 23.9028 | 33.5708 | 22.037 | 23.2478 | 50.513 | 834.2263 | 675.2761 | 838.4405 | 20.9531 | 23.8747 | 22.1319 | 31.9641 | 22.3307 | 109.7597 | 51.1508 | 532.7588 |  | 172.1574 | 509.0112 | 502.722 | 432.452 |  | 37.7574 | 61.8575 | 70.4456 | 222.9196 | 375.7564 | 456.8632 | 521.8522 | 17.9407 | 24.3425 | 20.0221 | 42.4883 | 20.4287 | 45.2528 | 48.905 | 47.7493 | 22.3391 |  |  | 2.5735 | -0.36608 | -152.6928 | 0.33443 | 7.9289 | -197.7882 | -55.2855 | 11.9296 | 1.2883 | 3.5197 | 60.7631 | 0.0094362 | 0.010455 | 0.00040741 | 22.279 | 21.9722 | 22.1413 | 22.1919 | 21.996 | 21.2809 | 20.0909 | 22.1764 | 22.3844 | 22.3842 | 22.337 | 21.936 | 21.1743 | 22.2669 | 102.6332 | 94.6414 | 94.7991 | 68.5544 | 65.8548 | 104.8934 | 71.853 | 22.342 | 22.0768 | 21.7007 | 22.0385 | 21.8189 | 22.2494 | 21.9185 | 22.4833 | 38.5082 | 653.71 | 676.4059 | 674.8355 | 648.7427 | 5.2097 | 6.6165 | 535.7452 | 21.8973 | 22.1927 | 155.8826 | 21.5463 | 22.0079 | 22.2243 | 24.5052 | 82.449 | 21.9076 | 22.685 | 41.3533 | 669.3933 | 740.6975 | 473.1957 | 488.8285 | 673.8172 |  | 580.1916 | 670.8552 | 464.6644 | 762.0994 | 778.955 | 498.6129 |  | 437.7953 |  |  | 368.5069 | 564.9946 | 650.0734 | [5 empty] | 21.8663 | 689.7224 | 21.6993 | 22.0763 | 658.1632 | 21.2755 | 21.8899 | 764.8015 | 924.7933 | 931.8115 |  | 725.7539 | 651.1566 | 482.0784 | 843.9692 | 796.1652 | 860.7216 | 939.9399 | 666.01 | 707.1566 | 801.501 | 888.5829 | 90.254 | 548.188 | 641.217 | 576.4964 | 805.6549 | 846.2621 | 650.8014 | 856.2054 | 728.9293 | 441.1946 | 630.2256 | 716.0918 | 874.8956 | 802.3739 | 891.8665 | 104.09 | 14.923 | 6.8433 | 0.15701 | -27.4096 | 3.0952 | 5500.33 | 2.17 | 3.7274 | -0.77176 | -15.7617 | 0.73764 | 5.302 | -26.4809 | -14.0003 | 27.4652 | 11.0749 | 69.9417 | 1.4092 | -1.7463 | -9.9645 | 41.9826
42838.4281 | 676 | 22.8853 | 22.849 | 22.8279 | 22.7422 | 22.3567 | 21.679 | 22.6863 | 21.7396 | 22.3355 | 22.3323 | 22.292 | 21.9474 | 21.1615 | 22.1386 | 21.5928 | 21.7687 | 21.9405 | 21.0589 | 21.2701 | 22.4472 | 20.4786 | 23.9962 | 33.8201 | 22.0433 | 23.2588 | 51.5269 | 830.1051 | 676.5935 | 835.8244 | 21.5736 | 21.8977 | 20.956 | 20.4956 | 22.1282 | 82.4719 | 27.5414 | 535.8679 |  | 88.4822 | 185.2776 | 559.7811 | 435.6298 |  | 37.9216 | 62.3587 | 74.8942 | 227.3683 | 378.9443 | 461.3538 | 525.1237 | 18.0265 | 24.5076 | 20.1278 | 43.0703 | 20.4669 | 45.2247 | 48.9229 | 47.7851 | 22.3632 |  |  | 2.7654 | -0.92134 | -147.7184 | 0.14715 | 7.5366 | -197.8322 | -56.5925 | 10.6949 | 1.1313 | 3.5854 | 63.4507 | 0.0095101 | 0.010532 | 0.00037949 | 22.2802 | 21.9664 | 22.1405 | 22.1937 | 21.9942 | 21.2701 | 20.0825 | 22.1756 | 22.382 | 22.3786 | 22.3353 | 21.9422 | 21.1732 | 22.2655 | 103.8876 | 99.9612 | 106.947 | 70.9024 | 67.2345 | 105.4175 | 72.3055 | 22.3499 | 22.0901 | 21.7146 | 22.0559 | 21.8223 | 22.2593 | 21.9261 | 22.4998 | 39.1543 | 654.633 | 675.0758 | 672.5687 | 649.5764 | 4.6117 | 4.0197 | 542.6023 | 21.8981 | 22.1921 | 162.2468 | 21.547 | 21.995 | 22.2244 | 24.5191 | 82.9385 | 21.8996 | 22.6865 | 41.9435 | 673.894 | 743.9793 | 478.0764 | 494.6188 | 679.119 |  | 590.106 | 671.9071 | 473.5656 | 779.5479 | 780.0161 | 508.5286 |  | 444.2492 |  |  | 372.8755 | 573.1946 | 660.0318 | [5 empty] | 21.8751 | 703.5352 | 21.7057 | 22.0769 | 675.574 | 21.2792 | 21.8901 | 752.0054 | 910.4262 | 927.0489 |  | 734.524 | 656.7032 | 502.8746 | 854.4793 | 807.6201 | 845.6138 | 931.2508 | 686.1752 | 713.5218 | 815.2994 | 898.4629 | 92.7184 | 553.3083 | 644.0561 | 576.118 | 794.8008 | 837.9797 | 674.0057 | 864.5667 | 742.6712 | 450.5083 | 637.65 | 709.4344 | 861.8243 | 821.9247 | 897.6207 | 102.9785 | 14.8371 | 7.1512 | 0.16326 | -27.5113 | 3.0951 | 5549.51 | 2.18 | 3.8593 | -1.2253 | -15.5144 | 0.48966 | 5.185 | -26.5652 | -14.2083 | 29.0152 | 12.1185 | 69.7672 | 1.3345 | -3.0415 | -10.8723 | 42.152
42838.4281 | 677 | 22.8888 | 22.8419 | 22.8382 | 22.7433 | 22.358 | 21.6695 | 22.6832 | 21.7288 | 22.3269 | 22.3307 | 22.3039 | 21.9454 | 21.1666 | 22.1393 | 21.5917 | 21.7663 | 21.9392 | 21.0682 | 21.2774 | 22.4631 | 20.4929 | 24.0982 | 34.0746 | 22.048 | 23.2669 | 52.5961 | 827.1863 | 679.1988 | 832.74 | 21.0067 | 21.7364 | 21.8445 | 20.0201 | 19.6699 | 58.3008 | 28.5077 | 574.2846 |  | 326.0525 | 220.2858 | 611.2804 | 436.212 |  | 38.1249 | 63.0766 | 77.3178 | 232.9532 | 384.81 | 467.5736 | 528.0586 | 18.0914 | 24.713 | 20.2543 | 43.7544 | 20.5012 | 45.195 | 48.9397 | 47.8166 | 22.3874 |  |  | 2.8252 | -1.0094 | -151.4357 | -0.24646 | 6.3347 | -197.7895 | -59.7559 | 9.4825 | 0.99333 | 3.5791 | 67.7704 | 0.0089943 | 0.01008 | 0.00040906 | 22.2821 | 21.9684 | 22.1403 | 22.2003 | 21.9961 | 21.2747 | 20.0886 | 22.1704 | 22.3841 | 22.3791 | 22.336 | 21.9311 | 21.1758 | 22.2632 | 100.9757 | 96.3804 | 105.0775 | 74.265 | 67.0443 | 105.8996 | 72.6284 | 22.3393 | 22.0846 | 21.7044 | 22.0465 | 21.8185 | 22.2593 | 21.9252 | 22.5045 | 39.8543 | 656.172 | 677.2668 | 673.532 | 657.0802 | 4.8151 | 2.5369 | 549.1715 | 21.8959 | 22.1901 | 168.0205 | 21.5464 | 21.9949 | 22.2283 | 24.5408 | 83.4024 | 21.9084 | 22.698 | 42.5613 | 678.9792 | 748.6885 | 482.2912 | 500.1075 | 683.0956 |  | 600.3361 | 674.1673 | 483.1498 | 776.3274 | 780.5142 | 519.3224 |  | 451.9664 |  |  | 375.4779 | 579.2119 | 664.2814 | [5 empty] | 21.8723 | 710.2806 | 21.7072 | 22.0837 | 674.6553 | 21.2791 | 21.8908 | 736.4454 | 894.7154 | 922.1559 |  | 745.3254 | 664.2763 | 529.0924 | 863.6055 | 832.0767 | 829.5401 | 920.1389 | 695.2448 | 719.3238 | 827.4762 | 913.0212 | 94.2584 | 562.9671 | 648.509 | 575.0663 | 783.5401 | 833.3601 | 702.5715 | 885.5472 | 759.4974 | 458.8781 | 648.3286 | 700.5272 | 847.8906 | 847.3808 | 912.7239 | 107.4925 | 14.6814 | 7.4879 | 0.16915 | -27.4345 | 3.0951 | 5576.8 | 1.01 | 3.8953 | -1.2838 | -15.7252 | -0.63439 | 4.7737 | -26.6745 | -14.6617 | 30.7082 | 13.2446 | 70.0026 | 1.7176 | -2.7949 | -10.8556 | 42.2658
42838.4281 | 678 | 22.8795 | 22.8463 | 22.8293 | 22.7489 | 22.3525 | 21.6684 | 22.6826 | 21.7303 | 22.3266 | 22.3325 | 22.3013 | 21.9483 | 21.1644 | 22.1356 | 21.5977 | 21.772 | 21.9415 | 21.0603 | 21.2813 | 22.4691 | 20.4933 | 24.1956 | 34.3338 | 22.0477 | 23.2823 | 53.6416 | 815.5903 | 682.2106 | 819.3582 | 19.8311 | 19.9048 | 23.6141 | 20.9899 | 20.0547 | 113.0019 | 49.6916 | 551.4456 | 1003.9131 | 368.0466 | 353.358 | 673.2947 | 452.1707 |  | 38.3002 | 63.7445 | 76.8394 | 238.4953 | 389.7654 | 468.7741 | 529.3125 | 18.1579 | 24.8859 | 20.4293 | 44.3506 | 20.524 | 45.1637 | 48.9553 | 47.8445 | 22.3958 |  |  | 1.2087 | -0.75903 | -157.2019 | 0.19052 | 8.0261 | -197.7947 | -60.4189 | 8.0894 | 1.1928 | 3.7236 | 76.2807 | 0.0089877 | 0.0099537 | 0.00039427 | 22.2924 | 21.9757 | 22.1463 | 22.197 | 21.9983 | 21.2785 | 20.092 | 22.1752 | 22.3783 | 22.3792 | 22.341 | 21.9352 | 21.1716 | 22.2586 | 102.2551 | 93.7011 | 99.7334 | 72.5561 | 65.963 | 106.328 | 72.8293 | 22.3426 | 22.0898 | 21.7064 | 22.0475 | 21.8245 | 22.265 | 21.9331 | 22.5283 | 40.5804 | 657.5364 | 677.2322 | 672.0244 | 657.732 | 3.4692 | 4.5135 | 555.3693 | 21.8946 | 22.1902 | 173.2865 | 21.5424 | 22.0048 | 22.2398 | 24.5547 | 83.826 | 21.9086 | 22.708 | 43.1952 | 685.4386 | 752.3546 | 486.6039 | 504.9907 | 687.1998 |  | 608.5855 | 675.2738 | 491.0553 | 765.8746 | 780.2412 | 524.136 |  | 458.1812 |  |  | 375.5704 | 581.0152 | 669.5954 | [5 empty] | 21.8686 | 710.1748 | 21.7001 | 22.076 | 655.1715 | 21.2819 | 21.8916 | 721.2797 | 880.328 | 911.7942 |  | 747.477 | 669.5857 | 553.5145 | 868.4174 | 853.2067 | 814.6972 | 908.9919 | 700.5701 | 726.1375 | 838.8506 | 917.2437 | 95.6664 | 573.3956 | 652.8291 | 572.6891 | 770.429 | 826.1634 | 730.8241 | 907.2578 | 771.1827 | 465.5798 | 656.8214 | 690.822 | 833.2783 | 869.4162 | 926.3675 | 106.6386 | 14.4818 | 7.843 | 0.17756 | -27.4691 | 3.0952 | 5581.54 | -0.06 | 2.5324 | -1.1144 | -16.0377 | 0.55832 | 5.3777 | -26.6965 | -14.7548 | 32.088 | 14.2213 | 70.213 | 1.6283 | -2.1769 | -10.564 | 42.5345
42838.4281 | 679 | 22.8949 | 22.8508 | 22.8387 | 22.7525 | 22.3611 | 21.6749 | 22.6886 | 21.7363 | 22.3257 | 22.3376 | 22.3002 | 21.9485 | 21.1666 | 22.1331 | 21.5899 | 21.7569 | 21.936 | 21.0607 | 21.2793 | 22.4731 | 20.4891 | 24.3087 | 34.6171 | 22.0471 | 23.2832 | 54.6512 | 800.9066 | 681.0176 | 803.2085 | 20.1135 | 20.4088 | 22.3785 | 21.5936 | 20.5627 | 45.4266 | 77.0821 | 536.2931 | 330.6946 | 201.8673 | 322.6029 | 566.4275 | 436.3918 | 1384.0612 | 38.5839 | 64.4886 | 77.5241 | 244.1622 | 395.0566 | 470.9871 | 531.4864 | 18.2778 | 25.0899 | 20.5976 | 45.0117 | 20.5191 | 45.1649 | 48.9729 | 47.8845 | 22.4184 |  |  | 1.183 | -0.59147 | -155.1793 | 0.023614 | 8.1096 | -197.8466 | -62.9751 | 7.567 | 1.3024 | 4.0595 | 90.6204 | 0.0088431 | 0.0098469 | 0.00039098 | 22.2993 | 21.9773 | 22.1523 | 22.1995 | 22.006 | 21.2802 | 20.0877 | 22.1796 | 22.3882 | 22.3872 | 22.3444 | 21.9372 | 21.1755 | 22.2736 | 96.0949 | 98.2585 | 103.9684 | 74.0223 | 65.249 | 106.6685 | 73.1054 | 22.3445 | 22.0859 | 21.706 | 22.0463 | 21.8261 | 22.2766 | 21.9265 | 22.5466 | 41.2685 | 658.2328 | 674.867 | 667.3227 | 653.6077 | 4.023 | 4.6413 | 564.5475 | 21.898 | 22.1928 | 179.9896 | 21.546 | 22.0032 | 22.2389 | 24.5782 | 84.193 | 21.9077 | 22.7123 | 43.8477 | 691.9807 | 753.5628 | 488.634 | 507.2251 | 689.6598 |  | 616.385 | 678.5054 | 498.7664 | 754.5156 | 779.4899 | 526.4937 |  | 463.9797 |  |  | 376.9273 | 583.6253 | 673.5555 | [5 empty] | 21.86 | 703.806 | 21.7015 | 22.0723 | 628.9714 | 21.2744 | 21.8926 | 707.9529 | 865.8699 | 900.1151 |  | 748.8065 | 675.2613 | 576.3128 | 878.14 | 863.0357 | 799.6386 | 896.4083 | 705.3256 | 730.1553 | 854.8263 | 923.3645 | 97.4155 | 582.3828 | 657.1117 | 570.9809 | 757.4672 | 815.9612 | 753.2913 | 925.7745 | 782.8599 | 472.2642 | 661.6714 | 682.3951 | 818.6084 | 882.4629 | 941.5218 | 118.23 | 14.2687 | 8.204 | 0.18374 | -27.4238 | 3.0952 | 5590.77 | 0.04 | 2.4868 | -0.98482 | -15.9518 | 0.19678 | 5.4137 | -26.7398 | -15.0861 | 33.4651 | 15.1382 | 70.3086 | 2.3549 | -2.6142 | -9.1277 | 42.7958
42838.4281 | 680 | 22.8858 | 22.8475 | 22.8341 | 22.7448 | 22.3487 | 21.6763 | 22.6837 | 21.7266 | 22.328 | 22.3327 | 22.3005 | 21.9434 | 21.1633 | 22.1365 | 21.5875 | 21.7627 | 21.9386 | 21.0633 | 21.2789 | 22.4759 | 20.4885 | 24.4282 | 34.9076 | 22.0543 | 23.2965 | 55.605 | 784.6373 | 676.4966 | 786.2031 | 20.2849 | 20.5269 | 19.9496 | 20.5532 | 20.5516 | 60.5961 | 58.7679 | 548.3447 | 101.0662 | 95.8468 | 367.6407 | 576.7189 | 440.912 | 702.2734 | 39.0892 | 65.3722 | 78.7793 | 250.1371 | 401.1443 | 475.7625 | 534.7527 | 18.4634 | 25.3054 | 20.6991 | 45.6946 | 20.5378 | 45.186 | 48.992 | 47.9386 | 22.4428 |  |  | 1.4617 | -0.44822 | -158.8736 | 0.022954 | 7.6713 | -197.846 | -65.7606 | 6.1213 | 1.2146 | 3.9571 | 99.5516 | 0.0087134 | 0.0096366 | 0.00037949 | 22.3009 | 21.9606 | 22.1388 | 22.195 | 22.0013 | 21.2738 | 20.0818 | 22.1739 | 22.3785 | 22.3822 | 22.3425 | 21.94 | 21.1617 | 22.2695 | 94.0167 | 94.0463 | 103.8399 | 73.6347 | 64.2753 | 107.0434 | 73.3475 | 22.3422 | 22.0825 | 21.7065 | 22.0366 | 21.8217 | 22.2788 | 21.9228 | 22.5656 | 41.9661 | 658.407 | 672.3836 | 661.814 | 648.532 | 3.2011 | 4.0214 | 571.5317 | 21.9034 | 22.1858 | 184.1766 | 21.542 | 22.0024 | 22.2356 | 24.5994 | 84.5208 | 21.9047 | 22.7133 | 44.5075 | 698.688 | 753.1067 | 488.6236 | 507.59 | 693.7194 |  | 625.2755 | 681.8687 | 507.2942 | 743.1221 | 778.0332 | 531.1208 |  | 470.7353 |  |  | 381.0292 | 587.3695 | 677.6409 | [5 empty] | 21.8639 | 695.4843 | 21.7053 | 22.0782 | 597.5367 | 21.2819 | 21.8881 | 695.6983 | 850.8419 | 887.7926 |  | 752.3307 | 681.2376 | 603.5487 | 894.621 | 870.9229 | 785.0345 | 884.5554 | 721.0352 | 738.5659 | 870.4671 | 938.6481 | 98.8567 | 587.382 | 661.983 | 568.501 | 744.6857 | 804.7402 | 773.1927 | 939.0382 | 789.0413 | 478.9989 | 663.8854 | 673.8366 | 803.561 | 894.9257 | 951.4547 | 129.4831 | 14.0089 | 8.5767 | 0.19859 | -27.4264 | 3.0951 | 5629.48 | -0.08 | 2.7423 | -0.85843 | -16.1617 | 0.19426 | 5.2822 | -26.8254 | -15.4656 | 35.04 | 16.1861 | 70.2001 | 2.6321 | -2.5707 | -9.9269 | 42.9736
42838.4282 | 681 | 22.8812 | 22.8385 | 22.8312 | 22.7403 | 22.344 | 21.6753 | 22.6767 | 21.7285 | 22.3259 | 22.3241 | 22.2995 | 21.9432 | 21.1554 | 22.1284 | 21.589 | 21.7634 | 21.9368 | 21.0627 | 21.2736 | 22.4841 | 20.4857 | 24.5515 | 35.2159 | 22.0478 | 23.3033 | 56.5394 | 772.5638 | 672.4248 | 774.2637 | 20.4518 | 20.463 | 20.3182 | 19.446 | 20.5927 | 78.6655 | 21.8389 | 550.7922 | 64.0955 | 125.1851 | 361.6191 | 630.4745 | 444.3441 | 58.6459 | 39.3811 | 66.1116 | 80.2765 | 256.2897 | 405.8152 | 481.1189 | 537.114 | 18.5988 | 25.4826 | 20.8369 | 46.2942 | 20.5619 | 45.1991 | 49.0101 | 47.9939 | 22.4526 |  |  | 1.7567 | -0.4745 | -156.4246 | -0.025014 | 7.0608 | -197.8243 | -69.4004 | 5.0857 | 1.1358 | 3.9276 | 103.9856 | 0.0088284 | 0.0096596 | 0.00038934 | 22.2998 | 21.9686 | 22.1458 | 22.2022 | 21.9981 | 21.2844 | 20.0945 | 22.1808 | 22.3872 | 22.3884 | 22.3384 | 21.9436 | 21.1682 | 22.2799 | 89.6137 | 89.0934 | 99.6772 | 72.1606 | 64.5872 | 107.359 | 73.5704 | 22.3414 | 22.0794 | 21.7086 | 22.0366 | 21.8191 | 22.2843 | 21.9196 | 22.5917 | 42.6714 | 658.34 | 670.141 | 656.8342 | 643.175 | 3.9743 | 2.725 | 577.3285 | 21.9018 | 22.1976 | 188.7758 | 21.5447 | 22.0101 | 22.2347 | 24.6259 | 84.8459 | 21.9065 | 22.7242 | 45.1846 | 709.9129 | 754.543 | 489.2955 | 508.7993 | 707.4352 |  | 634.5649 | 692.2757 | 515.4117 | 740.6092 | 776.6491 | 540.683 |  | 477.645 |  |  | 384.8742 | 595.3582 | 692.2348 | [5 empty] | 21.8671 | 686.8406 | 21.7049 | 22.0836 | 569.6188 | 21.2775 | 21.8835 | 683.5346 | 836.6466 | 876.0917 |  | 759.9076 | 691.8519 | 634.9125 | 909.5204 | 885.9063 | 771.0312 | 872.6381 | 734.4782 | 750.0314 | 881.3729 | 951.7731 | 100.6931 | 594.0643 | 665.1282 | 563.8561 | 733.1359 | 793.2921 | 789.1464 | 950.3877 | 792.7995 | 488.4335 | 667.8041 | 665.5289 | 790.5421 | 908.8366 | 956.7818 | 136.889 | 13.7248 | 8.9581 | 0.21995 | -27.5007 | 3.0952 | 5643.77 | -0.04 | 2.9893 | -0.88421 | -16.0541 | -0.20301 | 5.0858 | -26.9197 | -15.9445 | 36.4687 | 17.0114 | 69.8676 | 3.1603 | -2.0813 | -11.3069 | 43.1083
42838.4282 | 682 | 22.8908 | 22.8495 | 22.8357 | 22.7484 | 22.3526 | 21.6847 | 22.683 | 21.734 | 22.3354 | 22.3389 | 22.305 | 21.9498 | 21.1663 | 22.1387 | 21.5956 | 21.7665 | 21.9483 | 21.065 | 21.2801 | 22.4954 | 20.4953 | 24.6884 | 35.539 | 22.0501 | 23.317 | 57.4637 | 763.8536 | 670.2496 | 765.9435 | 20.1852 | 19.3947 | 20.8721 | 19.2749 | 19.4403 | 112.7014 | 30.2788 | 565.0303 | 132.0313 | 227.1234 | 290.9191 | 614.7943 | 455.7836 | 50.599 | 39.7362 | 67.1681 | 80.7962 | 260.9836 | 409.1814 | 486.7371 | 540.2128 | 18.6671 | 25.7075 | 21.0564 | 47.0437 | 20.5741 | 45.2007 | 49.0283 | 48.0557 | 22.4683 |  |  | 1.6371 | -0.034893 | -154.1582 | -0.08087 | 7.2967 | -197.8637 | -68.4804 | 3.8155 | 1.2858 | 4.0788 | 103.8381 | 0.0085688 | 0.0095397 | 0.00036799 | 22.3123 | 21.9654 | 22.1486 | 22.1895 | 21.9945 | 21.2796 | 20.0962 | 22.1823 | 22.3837 | 22.3869 | 22.346 | 21.9424 | 21.1708 | 22.2815 | 91.7887 | 87.384 | 94.5508 | 72.2857 | 63.8747 | 107.7903 | 73.742 | 22.3436 | 22.0845 | 21.7063 | 22.047 | 21.8211 | 22.2906 | 21.9221 | 22.6178 | 43.4754 | 657.9294 | 668.1422 | 652.8175 | 638.8969 | 6.9074 | 1.8859 | 586.9937 | 21.8991 | 22.1936 | 192.9711 | 21.5493 | 22.0019 | 22.2368 | 24.6455 | 85.1569 | 21.9034 | 22.7252 | 45.8814 | 723.4034 | 757.607 | 491.5579 | 511.2575 | 720.924 |  | 644.3207 | 702.3804 | 523.5949 | 737.0853 | 775.4598 | 549.8153 |  | 484.6143 |  |  | 392.0559 | 608.0764 | 709.8058 | [5 empty] | 21.8718 | 680.4603 | 21.7101 | 22.0895 | 545.0449 | 21.2821 | 21.8947 | 672.4044 | 821.9141 | 865.9391 |  | 768.0399 | 702.0331 | 670.9424 | 922.1529 | 900.0967 | 758.8313 | 860.5864 | 749.9321 | 760.3394 | 897.2003 | 962.6684 | 103.0304 | 602.8377 | 669.7444 | 559.2722 | 722.7819 | 783.5207 | 802.4873 | 961.0426 | 798.5663 | 498.7064 | 673.3064 | 657.9293 | 778.6016 | 922.7845 | 959.6019 | 135.0745 | 13.4743 | 9.3536 | 0.25166 | -27.4022 | 3.0951 | 5621.48 | -0.01 | 2.8743 | -0.24015 | -15.9622 | -0.3656 | 5.1893 | -27.0224 | -15.8973 | 38.0468 | 17.8824 | 69.6209 | 2.972 | -1.4911 | -11.3389 | 43.1405
42838.4282 | 683 | 22.8973 | 22.846 | 22.8371 | 22.7499 | 22.356 | 21.6811 | 22.6801 | 21.7345 | 22.335 | 22.3394 | 22.2971 | 21.9491 | 21.1693 | 22.1424 | 21.5898 | 21.7661 | 21.9431 | 21.0601 | 21.2712 | 22.4999 | 20.4897 | 24.8304 | 35.872 | 22.0521 | 23.3213 | 58.3762 | 758.5483 | 668.9062 | 760.9873 | 19.4095 | 19.244 | 22.7527 | 19.7925 | 19.317 | 80.6759 | 46.9767 | 594.9746 | 49.7009 | 451.7698 | 435.5768 | 578.9297 | 438.1185 | 65.0823 | 40.0694 | 68.1354 | 81.4299 | 265.2104 | 414.2205 | 489.8312 | 541.8702 | 18.7521 | 25.8983 | 21.3853 | 47.6854 | 20.6057 | 45.2108 | 49.0379 | 48.1111 | 22.4977 |  |  | 0.69283 | -0.46793 | -152.2565 | -0.34503 | 8.0958 | -197.7974 | -70.3466 | 1.5741 | 1.3127 | 4.1162 | 111.9732 | 0.0084571 | 0.0092916 | 0.00041891 | 22.3154 | 21.965 | 22.1464 | 22.1929 | 22.0021 | 21.277 | 20.082 | 22.1832 | 22.3857 | 22.3943 | 22.3392 | 21.95 | 21.1746 | 22.2906 | 100.2102 | 91.7618 | 87.667 | 72.6848 | 65.042 | 108.3736 | 73.8106 | 22.3432 | 22.0802 | 21.7146 | 22.0446 | 21.8158 | 22.2984 | 21.9316 | 22.6361 | 44.2061 | 657.4696 | 666.9172 | 651.0988 | 634.8792 | 5.2038 | 2.4968 | 600.7989 | 21.9 | 22.1966 | 196.4059 | 21.5508 | 22.0031 | 22.2502 | 24.6718 | 85.4457 | 21.9151 | 22.7407 | 46.603 | 736.1646 | 761.5379 | 494.7121 | 514.7834 | 729.4172 |  | 655.1817 | 714.37 | 533.023 | 739.0356 | 774.5695 | 559.7237 |  | 492.1483 |  |  | 398.3289 | 622.1333 | 723.4045 | [5 empty] | 21.8709 | 675.1414 | 21.7019 | 22.082 | 523.9378 | 21.2853 | 21.8964 | 661.572 | 808.0738 | 857.3626 |  | 777.7535 | 711.5442 | 714.0158 | 938.1091 | 912.5972 | 746.414 | 847.489 | 770.5972 | 769.2775 | 918.7191 | 975.7734 | 105.4214 | 612.7747 | 673.9791 | 554.6913 | 712.7543 | 775.7035 | 817.3723 | 970.0435 | 807.458 | 507.9368 | 679.2768 | 650.8042 | 767.329 | 933.8619 | 965.703 | 139.1507 | 13.1281 | 9.7391 | 0.28783 | -27.4489 | 3.0952 | 5595.84 | -0.09 | 1.8654 | -0.88068 | -15.886 | -0.75623 | 5.4771 | -27.0729 | -16.1453 | 40.0489 | 18.9121 | 69.3095 | 2.1084 | -0.71793 | -10.2696 | 43.1552
42838.4282 | 684 | 22.8888 | 22.8417 | 22.8227 | 22.7537 | 22.3468 | 21.6735 | 22.6846 | 21.7328 | 22.334 | 22.3361 | 22.298 | 21.9481 | 21.1714 | 22.1371 | 21.5883 | 21.763 | 21.941 | 21.0618 | 21.2716 | 22.5094 | 20.4894 | 24.9729 | 36.2327 | 22.0532 | 23.3241 | 59.2622 | 754.4783 | 667.999 | 756.9207 | 19.3941 | 19.5336 | 19.5332 | 20.0561 | 19.7037 | 56.9996 | 70.7337 | 593.6286 | 21.2301 | 496.0071 | 585.7942 | 633.5537 | 440.1644 | 119.1471 | 40.4923 | 69.0282 | 85.5923 | 270.2409 | 420.1583 | 494.0055 | 545.4016 | 18.8262 | 26.1044 | 21.7337 | 48.3714 | 20.6263 | 45.2371 | 49.0574 | 48.1665 | 22.4989 |  |  | 0.28016 | -0.67558 | -155.1531 | -0.23661 | 6.978 | -197.8092 | -72.1057 | 0.1166 | 1.5306 | 4.4258 | 112.4233 | 0.0085901 | 0.009221 | 0.00040413 | 22.3128 | 21.9713 | 22.1475 | 22.2005 | 21.9952 | 21.2794 | 20.0818 | 22.1813 | 22.3791 | 22.4037 | 22.3348 | 21.9545 | 21.1656 | 22.2993 | 99.1053 | 83.2667 | 83.9268 | 75.9625 | 66.5795 | 108.8908 | 73.8481 | 22.3509 | 22.088 | 21.7185 | 22.0458 | 21.8238 | 22.312 | 21.9337 | 22.664 | 44.9286 | 656.7089 | 664.9185 | 649.0205 | 629.724 | 4.9602 | 2.2556 | 614.1506 | 21.896 | 22.1952 | 199.8556 | 21.5481 | 21.999 | 22.2457 | 24.6947 | 85.7231 | 21.9031 | 22.7467 | 47.3271 | 747.0003 | 762.0403 | 499.6422 | 520.9421 | 739.2029 |  | 666.6282 | 724.52 | 543.1598 | 736.8845 | 773.4059 | 573.7616 |  | 500.5724 |  |  | 405.1076 | 633.6893 | 734.006 | [5 empty] | 21.8698 | 670.4166 | 21.7018 | 22.0729 | 504.3468 | 21.2813 | 21.8846 | 651.0636 | 794.9221 | 849.4598 |  | 796.6405 | 722.2913 | 761.4171 | 956.0396 | 921.115 | 734.7073 | 835.1084 | 792.9044 | 780.6443 | 946.5412 | 988.0252 | 107.3933 | 621.8518 | 677.7697 | 550.9679 | 703.0135 | 769.4593 | 829.0843 | 976.398 | 817.8706 | 515.0919 | 684.525 | 644.0942 | 757.8408 | 937.6359 | 970.5455 | 146.4512 | 12.8225 | 10.1119 | 0.33987 | -27.4703 | 3.0951 | 5585.21 | -0.13 | 1.1839 | -1.0596 | -16.0573 | -0.62706 | 5.0989 | -27.1476 | -16.3906 | 42.2107 | 20.1392 | 69.0339 | 2.2951 | -0.29782 | -9.469 | 43.1384
42838.4282 | 685 | 22.8868 | 22.8399 | 22.8284 | 22.7491 | 22.349 | 21.6729 | 22.6729 | 21.7272 | 22.3299 | 22.3359 | 22.2995 | 21.9473 | 21.1531 | 22.1419 | 21.5885 | 21.7696 | 21.9512 | 21.0681 | 21.2807 | 22.5143 | 20.4952 | 25.1349 | 36.6146 | 22.0586 | 23.3466 | 60.1223 | 746.3749 | 667.0919 | 747.7119 | 19.5621 | 19.6139 | 19.3874 | 19.9162 | 19.9475 | 58.931 | 19.2462 | 575.0234 | 25.059 | 394.0008 | 577.8924 | 574.4584 | 450.75 | 129.7629 | 40.9967 | 70.0501 | 90.0434 | 279.3547 | 429.0431 | 499.8647 | 551.0316 | 18.9039 | 26.3241 | 21.8613 | 49.1319 | 20.6414 | 45.2646 | 49.0835 | 48.2136 | 22.4946 |  |  | 0.28805 | -0.61841 | -155.9324 | 0.090638 | 7.5228 | -197.7619 | -75.5365 | -0.88681 | 1.5164 | 4.4403 | 116.4987 | 0.0086427 | 0.0090781 | 0.00040906 | 22.3194 | 21.9671 | 22.1434 | 22.2 | 21.9983 | 21.2739 | 20.0873 | 22.1809 | 22.3739 | 22.3898 | 22.3314 | 21.9474 | 21.1581 | 22.2904 | 100.0945 | 80.1327 | 80.6295 | 75.045 | 66.334 | 109.3798 | 73.8937 | 22.3418 | 22.0766 | 21.7099 | 22.0363 | 21.8151 | 22.3097 | 21.9258 | 22.6735 | 45.6265 | 655.7457 | 662.3183 | 646.8853 | 625.4753 | 3.9316 | 2.6096 | 623.6159 | 21.8933 | 22.1885 | 203.3177 | 21.5369 | 21.9977 | 22.2403 | 24.7163 | 86.0067 | 21.9074 | 22.7463 | 48.0686 | 758.0872 | 758.2678 | 506.1228 | 528.4704 | 748.4801 |  | 677.558 | 739.3457 | 553.0748 | 726.0429 | 771.4514 | 588.8228 |  | 509.2693 |  |  | 409.8554 | 643.3686 | 746.9717 | [5 empty] | 21.8716 | 663.3438 | 21.7091 | 22.0776 | 486.281 | 21.2812 | 21.8882 | 640.9635 | 782.9854 | 839.0144 |  | 818.4289 | 734.2251 | 807.2072 | 966.6947 | 921.1681 | 723.8292 | 824.0637 | 811.0877 | 791.1987 | 968.0767 | 990.3971 | 109.813 | 628.8591 | 680.9439 | 548.4212 | 694.1979 | 763.3873 | 838.7216 | 980.1358 | 824.7084 | 521.2001 | 688.0909 | 638.8008 | 749.4968 | 936.3324 | 975.2467 | 152.2379 | 12.449 | 10.4703 | 0.39438 | -27.4341 | 3.0952 | 5540.04 | -0.11 | 1.195 | -1.0153 | -16.1216 | 0.38868 | 5.3144 | -27.2478 | -16.8399 | 44.3503 | 21.2484 | 68.774 | 2.2458 | 0.074051 | -11.5718 | 43.0543
42838.4282 | 686 | 22.8896 | 22.8479 | 22.8313 | 22.7518 | 22.3547 | 21.6697 | 22.6856 | 21.7279 | 22.3303 | 22.3363 | 22.3003 | 21.9498 | 21.1704 | 22.1357 | 21.5851 | 21.7716 | 21.9502 | 21.0736 | 21.2848 | 22.5194 | 20.4958 | 25.2931 | 37.0012 | 22.0543 | 23.3511 | 60.9172 | 734.9808 | 666.5292 | 735.9979 | 19.6981 | 19.602 | 19.9605 | 19.1446 | 19.6138 | 83.3941 | 21.2546 | 564.7678 | 46.2624 | 456.6127 | 532.8158 | 592.9763 | 457.8613 | 19.9511 | 41.3892 | 70.8968 | 90.9786 | 284.5915 | 433.4234 | 506.5298 | 556.7242 | 18.975 | 26.5243 | 21.9688 | 49.8314 | 20.663 | 45.2747 | 49.1166 | 48.2686 | 22.5014 |  |  | 0.17174 | -0.79255 | -157.2584 | 0.16621 | 6.8716 | -197.7619 | -77.0341 | -2.2779 | 1.6223 | 4.644 | 123.7372 | 0.0079002 | 0.0087035 | 0.0004107 | 22.3294 | 21.9651 | 22.1469 | 22.1932 | 22.0051 | 21.2741 | 20.0907 | 22.1821 | 22.3807 | 22.3864 | 22.3296 | 21.9483 | 21.1658 | 22.292 | 96.0127 | 78.0306 | 80.2758 | 72.5271 | 66.4056 | 109.8093 | 73.9861 | 22.3325 | 22.0806 | 21.724 | 22.0443 | 21.8237 | 22.3162 | 21.9349 | 22.7093 | 46.3547 | 654.7667 | 659.1404 | 644.6149 | 623.5775 | 6.2804 | 2.7693 | 636.6704 | 21.8942 | 22.183 | 205.4329 | 21.5399 | 22.0006 | 22.2474 | 24.7426 | 86.2915 | 21.9123 | 22.7569 | 48.8433 | 770.9135 | 754.7976 | 513.4069 | 536.8924 | 763.3582 |  | 689.7966 | 754.3408 | 563.5995 | 710.4113 | 768.8024 | 600.0353 |  | 517.7102 |  |  | 412.9651 | 653.4325 | 767.2793 | [5 empty] | 21.8603 | 655.6738 | 21.7056 | 22.0736 | 471.5099 | 21.2782 | 21.8832 | 631.3782 | 771.532 | 826.7593 |  | 832.864 | 745.1182 | 849.3174 | 973.0423 | 914.8481 | 712.9951 | 812.2463 | 828.3786 | 802.6017 | 987.4744 | 988.4211 | 112.2307 | 634.7618 | 684.1179 | 546.6461 | 686.4053 | 754.8863 | 846.7281 | 978.3637 | 830.0451 | 530.8163 | 691.7921 | 634.4849 | 741.0779 | 939.0593 | 975.5313 | 151.5122 | 12.1254 | 10.8141 | 0.45344 | -27.4925 | 3.0951 | 5534.02 | -0.08 | 0.91744 | -1.1508 | -16.21 | 0.52699 | 5.101 | -27.3651 | -17.0792 | 46.7085 | 22.4965 | 68.4524 | 2.7525 | 0.12449 | -11.702 | 42.9021
42838.4282 | 687 | 22.8906 | 22.8518 | 22.8317 | 22.7481 | 22.3502 | 21.6771 | 22.6832 | 21.7325 | 22.33 | 22.3402 | 22.3078 | 21.9549 | 21.1699 | 22.1417 | 21.59 | 21.7613 | 21.9511 | 21.0637 | 21.2715 | 22.5229 | 20.491 | 25.4648 | 37.4123 | 22.054 | 23.3518 | 61.6684 | 725.4707 | 665.5377 | 725.9861 | 19.5495 | 19.6813 | 21.4223 | 19.3938 | 19.2466 | 83.7256 | 30.7871 | 575.0649 | 56.025 | 514.3374 | 620.9771 | 590.9835 | 438.4669 | 29.025 | 41.8997 | 71.9974 | 91.0623 | 288.0135 | 436.9884 | 509.8284 | 563.3859 | 19.0783 | 26.7918 | 22.2533 | 50.7023 | 20.6899 | 45.2877 | 49.1631 | 48.3387 | 22.5256 |  |  | 0.69677 | -0.92331 | -156.8024 | -0.24975 | 6.5627 | -197.8177 | -78.5343 | -3.1447 | 1.5049 | 4.6178 | 121.7529 | 0.0079445 | 0.0089006 | 0.00039756 | 22.3292 | 21.975 | 22.1408 | 22.1958 | 21.996 | 21.2736 | 20.0862 | 22.1739 | 22.3765 | 22.3878 | 22.3357 | 21.9349 | 21.1668 | 22.2829 | 92.2987 | 76.1774 | 79.7256 | 73.4742 | 67.4015 | 110.2775 | 74.0783 | 22.3393 | 22.0796 | 21.7057 | 22.0443 | 21.8152 | 22.3319 | 21.9329 | 22.7299 | 47.1304 | 653.8165 | 656.0219 | 642.0467 | 621.6741 | 4.9368 | 2.9498 | 650.2764 | 21.8945 | 22.1889 | 207.2745 | 21.5406 | 21.9942 | 22.2495 | 24.7672 | 86.5597 | 21.908 | 22.7635 | 49.6436 | 784.3108 | 753.7386 | 522.1421 | 546.0149 | 779.6719 |  | 704.0352 | 767.7355 | 575.8292 | 698.3357 | 765.5185 | 615.7006 |  | 527.5782 |  |  | 411.7767 | 662.5912 | 779.3393 | [5 empty] | 21.8577 | 648.034 | 21.7042 | 22.0733 | 460.8242 | 21.2837 | 21.8871 | 622.9121 | 760.8652 | 813.9518 |  | 844.4995 | 755.4043 | 874.2015 | 974.6564 | 909.2228 | 703.1909 | 801.5872 | 845.8968 | 813.3068 | 992.9268 | 985.5383 | 114.6117 | 640.9061 | 687.1607 | 545.7588 | 680.1102 | 745.785 | 857.9144 | 973.4231 | 830.3061 | 543.794 | 696.5895 | 630.2856 | 735.3229 | 941.6586 | 967.4576 | 150.0807 | 11.698 | 11.1397 | 0.51421 | -27.4162 | 3.0952 | 5533.26 | 0.01 | 1.8388 | -1.2441 | -16.2123 | -0.64702 | 4.9956 | -27.4268 | -17.2811 | 49.599 | 24.1251 | 67.8581 | 3.2232 | 0.19675 | -10.8406 | 42.7567
42838.4282 | 688 | 22.8884 | 22.8517 | 22.8385 | 22.7477 | 22.3532 | 21.6798 | 22.6785 | 21.7297 | 22.3341 | 22.3343 | 22.3046 | 21.9514 | 21.1695 | 22.1381 | 21.5904 | 21.7698 | 21.9463 | 21.0673 | 21.2747 | 22.5333 | 20.4974 | 25.6482 | 37.8527 | 22.0597 | 23.365 | 62.4051 | 715.7738 | 666.9377 | 716.1414 | 19.4007 | 19.4383 | 23.4828 | 19.7593 | 19.4943 | 75.295 | 53.3055 | 564.575 | 35.6462 | 544.935 | 691.4055 | 608.5037 | 439.3251 | 76.7649 | 42.2623 | 73.0462 | 91.1412 | 288.2298 | 437.5986 | 510.4996 | 567.6571 | 19.0738 | 27.0136 | 22.4496 | 51.4385 | 20.7248 | 45.3002 | 49.2169 | 48.4045 | 22.5319 |  |  | 1.4603 | -0.49027 | -157.0114 | 0.10247 | 7.5648 | -197.8112 | -79.2446 | -2.9396 | 1.5044 | 4.5916 | 121.7678 | 0.0077211 | 0.0086986 | 0.0004107 | 22.3237 | 21.9692 | 22.1425 | 22.1898 | 21.997 | 21.272 | 20.0848 | 22.1749 | 22.3708 | 22.3903 | 22.328 | 21.9418 | 21.1644 | 22.2815 | 89.7597 | 80.1767 | 85.803 | 71.005 | 64.3824 | 110.767 | 74.2615 | 22.3476 | 22.093 | 21.7185 | 22.0471 | 21.8217 | 22.3377 | 21.9425 | 22.7533 | 47.8269 | 652.7394 | 652.5789 | 639.0592 | 615.9008 | 4.2407 | 6.7725 | 659.9682 | 21.89 | 22.1907 | 209.2939 | 21.5357 | 21.9952 | 22.2568 | 24.7936 | 86.7978 | 21.9136 | 22.7739 | 50.4577 | 796.3272 | 752.1581 | 529.9651 | 552.9215 | 772.3072 |  | 715.4665 | 767.7271 | 585.1308 | 690.1006 | 762.5408 | 624.6704 |  | 535.4713 |  |  | 410.6112 | 667.09 | 784.5937 | [5 empty] | 21.8678 | 642.128 | 21.7066 | 22.0807 | 451.9058 | 21.2885 | 21.8924 | 614.3354 | 751.6495 | 803.2446 |  | 851.5416 | 765.9223 | 889.157 | 975.8582 | 906.8372 | 694.53 | 792.7442 | 859.1336 | 823.8812 | 988.5405 | 984.7874 | 118.1568 | 648.6829 | 690.1696 | 544.2557 | 674.858 | 737.8462 | 872.0097 | 965.9717 | 826.5052 | 559.5339 | 702.173 | 625.6509 | 729.2768 | 940.4856 | 957.548 | 156.1133 | 11.2653 | 11.4679 | 0.58683 | -27.4595 | 3.0951 | 5524.56 | -0.13 | 2.6488 | -0.90792 | -16.2478 | 0.41507 | 5.3657 | -27.4381 | -17.3665 | 52.5831 | 25.696 | 67.2507 | 3.5659 | -0.45643 | -10.0788 | 42.6929
42838.4283 | 689 | 22.8917 | 22.8553 | 22.8378 | 22.7506 | 22.3607 | 21.6788 | 22.69 | 21.7301 | 22.341 | 22.3367 | 22.3073 | 21.9537 | 21.1708 | 22.1444 | 21.5865 | 21.7576 | 21.9401 | 21.0608 | 21.2758 | 22.5343 | 20.4905 | 25.8302 | 38.3217 | 22.0487 | 23.3748 | 63.0892 | 707.9233 | 667.7518 | 708.5949 | 19.4373 | 19.5641 | 20.9498 | 20.2319 | 19.7238 | 86.1438 | 88.1133 | 556.2361 | 40.1287 | 549.7929 | 765.6553 | 621.3574 | 451.572 | 168.877 | 42.7332 | 74.193 | 92.3339 | 293.4594 | 439.0505 | 512.4619 | 570.4113 | 19.0094 | 27.2395 | 22.5138 | 52.2107 | 20.7713 | 45.3088 | 49.282 | 48.5322 | 22.5626 |  |  | 1.0128 | -0.46004 | -162.7408 | -0.09401 | 7.5734 | -197.8493 | -81.7469 | -4.7467 | 1.4242 | 4.6648 | 127.5256 | 0.0077556 | 0.0085474 | 0.00040741 | 22.3333 | 21.9802 | 22.1413 | 22.1948 | 21.9976 | 21.2791 | 20.0928 | 22.1811 | 22.3675 | 22.3876 | 22.3286 | 21.9479 | 21.166 | 22.2787 | 90.7077 | 78.3533 | 101.082 | 75.9959 | 65.2436 | 111.2324 | 74.6725 | 22.3427 | 22.0905 | 21.7183 | 22.0467 | 21.8205 | 22.3395 | 21.9405 | 22.7718 | 48.5088 | 651.4221 | 649.281 | 636.6734 | 611.474 | 5.0049 | 2.7092 | 665.2102 | 21.8955 | 22.1924 | 212.3114 | 21.539 | 22.0016 | 22.2598 | 24.8331 | 87.0326 | 21.9139 | 22.7815 | 51.278 | 809.6621 | 748.2779 | 533.1729 | 555.4042 | 759.15 |  | 727.004 | 774.0264 | 594.3055 | 682.8137 | 759.5564 | 635.1632 |  | 543.201 |  |  | 410.5872 | 671.1266 | 790.7209 | [5 empty] | 21.8618 | 636.6292 | 21.7008 | 22.0821 | 442.0155 | 21.2765 | 21.891 | 606.366 | 742.6751 | 792.943 |  | 853.675 | 775.1838 | 883.5423 | 967.0355 | 902.6757 | 686.6812 | 782.0347 | 868.6926 | 832.9844 | 970.6702 | 978.0249 | 121.4639 | 657.6019 | 693.3397 | 542.5131 | 669.2067 | 730.1613 | 888.2687 | 955.3744 | 821.0647 | 575.3901 | 707.732 | 621.0828 | 721.5639 | 936.3289 | 946.0373 | 159.2149 | 10.8575 | 11.7798 | 0.66201 | -27.4363 | 3.0952 | 5522.6 | -0.12 | 2.1975 | -0.88094 | -16.5689 | -0.39823 | 5.3755 | -27.475 | -17.6607 | 55.842 | 27.1127 | 66.6215 | 3.5183 | -2.1045 | -9.1303 | 42.5426
42838.4283 | 690 | 22.8846 | 22.8496 | 22.8291 | 22.7418 | 22.3536 | 21.6734 | 22.683 | 21.7376 | 22.3303 | 22.3367 | 22.3001 | 21.945 | 21.1595 | 22.1385 | 21.5901 | 21.7698 | 21.9513 | 21.0684 | 21.2855 | 22.5463 | 20.5046 | 26.0427 | 38.8186 | 22.0771 | 23.374 | 63.7431 | 703.3395 | 670.7511 | 704.2433 | 19.7898 | 19.8138 | 19.635 | 19.548 | 20.1011 | 75.8895 | 37.051 | 551.6329 | 27.501 | 547.5278 | 716.0617 | 586.0647 | 459.6432 | 58.991 | 43.2179 | 75.3576 | 93.0053 | 300.4276 | 442.9328 | 516.8928 | 574.5635 | 18.9923 | 27.4741 | 22.6117 | 53.0215 | 20.7991 | 45.308 | 49.3459 | 48.656 | 22.5743 |  |  | 1.1949 | -0.4239 | -163.7797 | -0.20309 | 7.1305 | -197.8355 | -83.0289 | -4.196 | 1.6114 | 4.7015 | 126.8583 | 0.0076078 | 0.0085458 | 0.00038113 | 22.3407 | 21.9768 | 22.1425 | 22.198 | 21.9943 | 21.2745 | 20.0838 | 22.1699 | 22.3649 | 22.3916 | 22.3267 | 21.9456 | 21.1569 | 22.2744 | 90.3873 | 71.8094 | 94.8114 | 75.5607 | 67.5913 | 111.7405 | 74.8693 | 22.3396 | 22.0837 | 21.7175 | 22.0501 | 21.8251 | 22.3464 | 21.9352 | 22.7939 | 49.1821 | 650.0553 | 644.8023 | 633.1399 | 606.5742 | 4.2535 | 2.1928 | 675.134 | 21.8957 | 22.1966 | 214.75 | 21.5404 | 21.9996 | 22.264 | 24.858 | 87.2338 | 21.9068 | 22.7914 | 52.1125 | 823.8839 | 745.1568 | 534.6073 | 557.0165 | 771.968 |  | 739.6807 | 787.1242 | 605.049 | 673.9008 | 755.9043 | 646.7351 |  | 551.2786 |  |  | 408.6978 | 674.7002 | 798.666 | [5 empty] | 21.8651 | 630.3021 | 21.7032 | 22.0768 | 430.5279 | 21.2789 | 21.875 | 599.003 | 734.345 | 781.9764 |  | 855.6091 | 783.3186 | 869.288 | 953.8549 | 895.972 | 679.0138 | 772.6263 | 878.9209 | 840.1161 | 950.531 | 969.6721 | 124.6222 | 664.4193 | 698.6203 | 540.1405 | 664.3688 | 724.2317 | 898.115 | 945.789 | 816.0909 | 594.2337 | 714.6801 | 616.9574 | 718.601 | 934.1232 | 937.492 | 164.8539 | 10.4598 | 12.0865 | 0.73583 | -27.4851 | 3.0952 | 5522.62 | -0.05 | 2.3816 | -0.84705 | -16.6496 | -0.5863 | 5.2306 | -27.5514 | -17.8487 | 58.7696 | 28.6676 | 65.8602 | 3.6169 | -1.384 | -11.2137 | 42.3963
42838.4283 | 691 | 22.8832 | 22.8503 | 22.8285 | 22.7395 | 22.3544 | 21.6795 | 22.686 | 21.7239 | 22.3273 | 22.3318 | 22.2989 | 21.9445 | 21.1598 | 22.1391 | 21.5844 | 21.7682 | 21.9483 | 21.0591 | 21.2822 | 22.5543 | 20.498 | 26.2587 | 39.3362 | 22.0643 | 23.3885 | 64.3998 | 697.2916 | 675.7877 | 697.6841 | 19.1401 | 19.1263 | 20.0478 | 19.0749 | 19.6507 | 71.4469 | 19.7805 | 589.0193 | 26.1274 | 581.8156 | 708.4462 | 635.0292 | 445.267 | 19.6022 | 43.613 | 76.33 | 93.1817 | 304.9303 | 448.0618 | 520.2725 | 577.878 | 19.0099 | 27.6835 | 22.6916 | 53.7158 | 20.82 | 45.2974 | 49.3985 | 48.7666 | 22.5807 |  |  | 0.59689 | -0.67098 | -160.3186 | -0.1157 | 7.4663 | -197.8617 | -85.0095 | -4.5837 | 1.7517 | 4.434 | 130.9813 | 0.0074813 | 0.0082583 | 0.00040084 | 22.3511 | 21.9823 | 22.1515 | 22.1995 | 22.0042 | 21.2777 | 20.0932 | 22.1743 | 22.3735 | 22.3917 | 22.331 | 21.9473 | 21.1595 | 22.2776 | 88.6394 | 67.9689 | 90.1483 | 69.8354 | 62.8574 | 112.1622 | 75.0354 | 22.3413 | 22.0864 | 21.7161 | 22.0453 | 21.8284 | 22.3591 | 21.9332 | 22.8205 | 49.888 | 648.0745 | 637.5421 | 627.3927 | 596.9985 | 4.5191 | 4.3699 | 687.4385 | 21.895 | 22.1963 | 215.403 | 21.5425 | 21.996 | 22.2703 | 24.8796 | 87.4047 | 21.9129 | 22.805 | 52.9579 | 839.0621 | 740.647 | 536.5582 | 560.5999 | 784.635 |  | 750.7887 | 800.2098 | 615.181 | 663.0813 | 752.1599 | 660.2524 |  | 558.0742 |  |  | 405.4166 | 680.7114 | 800.8637 | [5 empty] | 21.8773 | 622.2496 | 21.702 | 22.0905 | 421.9236 | 21.297 | 21.8901 | 592.3115 | 726.43 | 771.1095 |  | 859.7086 | 788.6943 | 851.5533 | 942.4547 | 891.0774 | 671.782 | 764.7531 | 892.4417 | 848.5011 | 929.7567 | 962.9987 | 132.4345 | 672.1982 | 707.0097 | 537.1771 | 662.4355 | 718.2008 | 900.3357 | 939.9978 | 814.0213 | 615.4119 | 723.6739 | 611.8873 | 716.1229 | 935.0033 | 932.725 | 146.6146 | 10.0467 | 12.3765 | 0.804 | -27.5362 | 3.0952 | 5560.03 | -0.07 | 1.6776 | -1.0672 | -16.4957 | -0.44314 | 5.3638 | -27.6121 | -18.0989 | 61.3872 | 30.1691 | 65.1363 | 3.8634 | -0.84587 | -11.4016 | 42.255
42838.4283 | 692 | 22.8865 | 22.8497 | 22.837 | 22.7374 | 22.3539 | 21.6773 | 22.6849 | 21.7314 | 22.3308 | 22.3306 | 22.2969 | 21.945 | 21.1674 | 22.1318 | 21.5942 | 21.7689 | 21.9613 | 21.0704 | 21.2878 | 22.5626 | 20.5048 | 26.4806 | 39.8614 | 22.0659 | 23.4081 | 64.9696 | 695.3918 | 678.4889 | 696.0804 | 19.5708 | 19.1082 | 22.4694 | 19.3036 | 19.1176 | 74.6215 | 34.3727 | 594.8627 | 43.3013 | 614.961 | 888.7553 | 730.44 | 443.753 | 31.9731 | 44.0068 | 77.3558 | 93.6155 | 312.4968 | 455.2647 | 524.6246 | 582.6624 | 19.058 | 27.9493 | 22.7276 | 54.5792 | 20.84 | 45.3215 | 49.4587 | 48.9037 | 22.597 |  |  | 0.57783 | -0.32928 | -163.1771 | -0.19521 | 8.0984 | -197.8151 | -86.4046 | -4.7539 | 1.6472 | 5.2827 | 138.3017 | 0.0074336 | 0.008191 | 0.00040084 | 22.3479 | 21.974 | 22.1483 | 22.1957 | 21.9984 | 21.2725 | 20.0903 | 22.1749 | 22.3598 | 22.3824 | 22.3237 | 21.9342 | 21.1512 | 22.2718 | 90.1374 | 66.0588 | 93.8942 | 68.45 | 61.0642 | 112.5932 | 75.3204 | 22.3491 | 22.0858 | 21.7197 | 22.0385 | 21.8235 | 22.3638 | 21.9336 | 22.838 | 50.5984 | 645.6703 | 629.2855 | 620.9163 | 586.8835 | 4.5645 | 3.047 | 699.9496 | 21.8978 | 22.1901 | 215.3694 | 21.5411 | 21.9932 | 22.2662 | 24.9298 | 87.5666 | 21.9152 | 22.8097 | 53.8203 | 848.5294 | 732.872 | 539.5715 | 565.6123 | 786.9304 |  | 759.8957 | 807.5624 | 625.0551 | 655.4809 | 748.2982 | 677.6788 |  | 565.6384 |  |  | 402.4719 | 672.7841 | 795.9633 | [5 empty] | 21.8788 | 613.176 | 21.713 | 22.089 | 415.0571 | 21.2979 | 21.8871 | 585.8398 | 718.6 | 760.9388 |  | 868.1419 | 798.0563 | 834.023 | 930.3628 | 891.3767 | 663.2628 | 755.7985 | 908.1331 | 858.0598 | 910.5593 | 957.3194 | 137.4188 | 689.6314 | 714.828 | 534.2606 | 660.6279 | 712.0686 | 907.5814 | 936.9622 | 813.1486 | 639.7051 | 731.8 | 607.2679 | 711.6453 | 934.0789 | 930.1153 | 161.1352 | 9.6975 | 12.6547 | 0.86456 | -27.5015 | 3.0951 | 5779.39 | -0.18 | 1.6492 | -0.74868 | -16.6665 | -0.57645 | 5.6015 | -27.6845 | -18.2968 | 63.8235 | 31.8353 | 64.3015 | 3.7505 | -1.2277 | -10.8646 | 42.0445
42838.4283 | 693 | 22.8864 | 22.8489 | 22.8325 | 22.7462 | 22.3597 | 21.6771 | 22.6842 | 21.7343 | 22.3325 | 22.3385 | 22.2996 | 21.9413 | 21.1665 | 22.1361 | 21.5913 | 21.7665 | 21.9499 | 21.0675 | 21.2848 | 22.5673 | 20.5044 | 26.7113 | 40.4091 | 22.0711 | 23.4114 | 65.5226 | 694.6541 | 679.9369 | 695.6936 | 19.2224 | 19.2563 | 23.4687 | 19.529 | 19.3477 | 83.2762 | 62.0542 | 571.5903 | 19.4811 | 602.3408 | 884.3122 | 780.1063 | 472.5265 | 68.8738 | 44.4251 | 78.3377 | 97.9913 | 322.2382 | 464.7293 | 530.4323 | 588.2914 | 19.1427 | 28.192 | 22.9077 | 55.4008 | 20.8584 | 45.3379 | 49.511 | 49.0227 | 22.6136 |  |  | 1.093 | -0.42062 | -157.3255 | -0.32663 | 6.4905 | -197.8394 | -93.1196 | -5.0786 | 1.8793 | 5.6821 | 144.9688 | 0.0075191 | 0.0082797 | 0.0004107 | 22.347 | 21.9742 | 22.1389 | 22.1961 | 21.9989 | 21.2722 | 20.0849 | 22.1748 | 22.3588 | 22.3739 | 22.3259 | 21.9285 | 21.1559 | 22.2693 | 90.7342 | 72.768 | 90.092 | 70.7692 | 61.7888 | 113.0722 | 75.5314 | 22.3453 | 22.0842 | 21.7209 | 22.0363 | 21.8236 | 22.3674 | 21.9332 | 22.8637 | 51.2421 | 643.509 | 622.0278 | 615.383 | 583.0455 | 11.728 | 7.1717 | 708.847 | 21.9003 | 22.186 | 214.9969 | 21.5439 | 21.995 | 22.2708 | 24.9656 | 87.714 | 21.9155 | 22.8206 | 54.698 | 850.0372 | 726.5412 | 545.3434 | 572.629 | 790.2779 |  | 768.5483 | 813.6359 | 635.8784 | 655.9356 | 744.6178 | 703.5019 |  | 574.5515 |  |  | 401.7505 | 657.8858 | 788.5018 | [5 empty] | 21.8721 | 610.7621 | 21.7084 | 22.0823 | 410.7915 | 21.2861 | 21.8873 | 579.57 | 712.2872 | 752.4053 |  | 883.3397 | 802.7891 | 819.9248 | 918.4996 | 890.7756 | 657.7817 | 751.6057 | 930.1361 | 867.8546 | 897.8635 | 949.8235 | 142.3875 | 699.933 | 719.97 | 531.8948 | 656.6711 | 707.8427 | 916.0412 | 939.3719 | 813.8881 | 661.5476 | 739.3313 | 604.0112 | 708.6435 | 935.7674 | 930.7423 | 145.1892 | 9.3148 | 12.9354 | 0.92538 | -27.5055 | 3.0952 | 6095.23 | -0.02 | 2.2678 | -0.84736 | -16.3878 | -0.74671 | 5.0329 | -27.7868 | -19.0635 | 66.1617 | 33.7785 | 63.3018 | 3.7436 | -0.77975 | -10.6862 | 41.7122
42838.4283 | 694 | 22.8876 | 22.8531 | 22.8308 | 22.7537 | 22.3474 | 21.6756 | 22.6793 | 21.7277 | 22.3374 | 22.3404 | 22.2976 | 21.9487 | 21.1625 | 22.1348 | 21.597 | 21.7715 | 21.9446 | 21.0693 | 21.2826 | 22.5753 | 20.5095 | 26.9618 | 40.9799 | 22.0774 | 23.4232 | 66.0429 | 689.6726 | 678.2009 | 689.8805 | 19.3105 | 19.425 | 19.4247 | 19.4271 | 19.63 | 90.3697 | 61.6107 | 576.3569 | 24.6341 | 613.7791 | 834.6148 | 701.6157 | 463.3915 | 92.1045 | 45.2259 | 80.2602 | 101.6374 | 329.3025 | 472.5829 | 538.8451 | 596.9612 | 19.3413 | 28.5142 | 23.4844 | 56.4799 | 20.8937 | 45.3491 | 49.5755 | 49.1657 | 22.6317 |  |  | 0.76511 | -0.81029 | -163.9387 | -0.081526 | 8.1313 | -197.8197 | -155.4214 | -7.3942 | 5.1358 | 14.7071 | 158.099 | 0.0073926 | 0.0080628 | 0.00043041 | 22.3511 | 21.9714 | 22.1423 | 22.1863 | 22.0065 | 21.2761 | 20.0897 | 22.1715 | 22.354 | 22.3819 | 22.3311 | 21.9314 | 21.1594 | 22.2683 | 129.1174 | 94.2642 | 104.463 | 73.7555 | 64.9471 | 115.6707 | 76.2109 | 22.3357 | 22.0842 | 21.7199 | 22.0394 | 21.8226 | 22.3691 | 21.9349 | 22.8906 | 51.8698 | 641.4554 | 616.2514 | 610.3209 | 579.9149 | 53.533 | 25.0956 | 724.6559 | 21.9028 | 22.1916 | 215.0705 | 21.5549 | 22.003 | 22.2811 | 25.0031 | 87.8588 | 21.9231 | 22.8348 | 55.603 | 849.9828 | 721.7815 | 554.432 | 582.4683 | 794.0696 |  | 776.6188 | 841.7533 | 649.0931 | 662.2536 | 741.5324 | 729.142 |  | 583.4595 |  |  | 401.2072 | 650.1242 | 787.4975 | [5 empty] | 21.8588 | 610.8308 | 21.7021 | 22.0703 | 406.5576 | 21.2796 | 21.8835 | 573.6313 | 709.0953 | 745.7159 |  | 903.5783 | 806.0079 | 814.4082 | 909.8329 | 890.2044 | 653.0062 | 748.955 | 951.9223 | 875.0474 | 892.038 | 944.0911 | 146.9389 | 709.7791 | 725.3073 | 529.1543 | 653.7734 | 703.4605 | 918.9084 | 946.3842 | 814.561 | 684.1364 | 749.0925 | 600.5403 | 704.1811 | 937.164 | 930.7969 | 121.1113 | 9.0933 | 13.2165 | 0.9876 | -27.4573 | 3.0952 | 6494.24 | 0 | 1.8917 | -1.1793 | -16.7744 | -0.37407 | 5.6627 | -27.9305 | -24.7571 | 68.3738 | 35.6654 | 62.3062 | -0.19815 | -2.2945 | -10.4485 | 41.3846
42838.4283 | 695 | 22.8829 | 22.8469 | 22.8274 | 22.7452 | 22.3507 | 21.6719 | 22.6866 | 21.7306 | 22.3295 | 22.3342 | 22.2935 | 21.9439 | 21.1584 | 22.1338 | 21.5937 | 21.7737 | 21.9508 | 21.0761 | 21.29 | 22.5876 | 20.5089 | 27.2092 | 41.5698 | 22.0748 | 23.4294 | 66.5068 | 682.1646 | 679.3679 | 682.4362 | 19.7184 | 19.5475 | 20.5106 | 19.1864 | 19.8564 | 93.0625 | 20.2744 | 586.6479 | 30.827 | 629.5551 | 821.779 | 673.2166 | 450.3015 | 40.7917 | 46.8226 | 83.592 | 105.08 | 341.302 | 482.3691 | 550.9311 | 608.4008 | 20.4495 | 29.3277 | 25.1596 | 58.6143 | 20.9432 | 45.3623 | 49.6265 | 49.3092 | 22.6578 |  |  | 0.62383 | -0.5665 | -165.1267 | -0.23792 | 8.107 | -197.842 | -197.808 | -6.676 | 5.885 | 15.9814 | 155.3964 | 0.0070393 | 0.0078772 | 0.00040577 | 22.3493 | 21.9773 | 22.1449 | 22.1963 | 21.994 | 21.2743 | 20.0878 | 22.1736 | 22.3625 | 22.3835 | 22.3309 | 21.936 | 21.1598 | 22.2689 | 234.047 | 160.6172 | 179.092 | 102.562 | 78.8782 | 123.3121 | 79.3906 | 22.3465 | 22.0937 | 21.7139 | 22.0414 | 21.82 | 22.3883 | 21.9334 | 22.9243 | 52.4976 | 639.5273 | 610.6886 | 605.1011 | 577.3266 | 60.6051 | 32.8993 | 736.9924 | 21.9015 | 22.1861 | 215.1196 | 21.5476 | 22.0035 | 22.285 | 25.0186 | 87.9633 | 21.9219 | 22.837 | 56.5035 | 848.095 | 717.1906 | 559.9027 | 588.1073 | 781.528 |  | 780.8901 | 830.567 | 658.9334 | 660.6668 | 738.859 | 738.1186 |  | 590.5777 |  |  | 399.1785 | 634.8351 | 770.1633 | [5 empty] | 21.8703 | 609.3085 | 21.7031 | 22.0767 | 401.2517 | 21.2825 | 21.8836 | 567.9659 | 706.4566 | 738.5031 |  | 923.6413 | 810.5937 | 809.4688 | 905.1299 | 890.2194 | 648.3798 | 744.3749 | 970.2117 | 883.4075 | 878.2625 | 941.1013 | 154.3256 | 722.6231 | 730.8584 | 527.6532 | 649.9519 | 697.3877 | 926.429 | 948.9883 | 816.919 | 704.6365 | 761.1066 | 597.3176 | 697.6265 | 938.3339 | 933.6483 | 137.483 | 8.7927 | 13.4874 | 1.0562 | -27.4093 | 3.0951 | 6901.68 | -0.04 | 1.7015 | -0.99071 | -16.9143 | -0.64203 | 5.6961 | -28.1392 | -28.1367 | 69.9683 | 38.0283 | 61.6451 | -10.903 | -10.2021 | -11.5249 | 41.0694
42838.4283 | 696 | 22.8857 | 22.8361 | 22.8334 | 22.7479 | 22.3551 | 21.6745 | 22.6855 | 21.7299 | 22.3322 | 22.3362 | 22.2992 | 21.9457 | 21.1537 | 22.1375 | 21.5996 | 21.7799 | 21.9612 | 21.0703 | 21.2951 | 22.598 | 20.5215 | 27.4811 | 42.1909 | 22.0785 | 23.4483 | 66.9806 | 679.7611 | 682.6762 | 680.7177 | 19.4059 | 19.0052 | 22.0959 | 18.8847 | 19.1575 | 128.3332 | 26.2436 | 594.3492 | 53.9994 | 652.386 | 782.4436 | 727.396 | 448.1604 | 22.7748 | 48.7614 | 87.2454 | 109.1332 | 351.8628 | 495.2689 | 563.689 | 621.4961 | 21.5866 | 30.2785 | 26.7522 | 61.0034 | 20.9885 | 45.4019 | 49.6877 | 49.4597 | 22.6848 |  |  | 0.50621 | -0.99165 | -168.3427 | -0.097954 | 8.3803 | -197.8552 | -203.2338 | -7.6636 | 7.2268 | 18.1052 | 162.0385 | 0.006742 | 0.0078262 | 0.00044355 | 22.3566 | 21.9808 | 22.1413 | 22.2012 | 21.9968 | 21.2729 | 20.089 | 22.1728 | 22.3559 | 22.3867 | 22.3305 | 21.9355 | 21.1668 | 22.2698 | 333.7533 | 254.903 | 260.4858 | 143.9114 | 112.7219 | 134.4576 | 83.9427 | 22.3355 | 22.0936 | 21.7233 | 22.0382 | 21.8257 | 22.3979 | 21.9409 | 22.9594 | 53.1758 | 637.2403 | 604.4256 | 599.3554 | 573.7583 | 64.1333 | 51.1359 | 734.3379 | 21.8957 | 22.176 | 215.261 | 21.5412 | 22.0014 | 22.2874 | 25.0508 | 88.028 | 21.9206 | 22.8437 | 57.399 | 849.4997 | 712.0249 | 565.0446 | 593.2504 | 778.5302 |  | 784.2655 | 830.2916 | 667.9558 | 656.1311 | 736.0716 | 744.8522 |  | 597.6365 |  |  | 396.0041 | 621.7439 | 756.4369 | [5 empty] | 21.8698 | 605.8996 | 21.7095 | 22.0805 | 395.3646 | 21.2841 | 21.8885 | 562.0385 | 700.9593 | 731.0559 |  | 936.0385 | 813.0198 | 793.8529 | 893.182 | 888.9396 | 643.285 | 738.8352 | 983.8453 | 890.6763 | 863.1827 | 930.8415 | 160.7686 | 736.2175 | 736.4291 | 526.2349 | 645.6529 | 691.2109 | 934.1628 | 952.7271 | 821.4153 | 723.2656 | 772.7975 | 594.2818 | 692.1912 | 940.6402 | 933.5036 | 119.4791 | 8.3874 | 13.7488 | 1.1332 | -27.5163 | 3.0952 | 7208.61 | -0.06 | 1.5314 | -1.3175 | -17.1654 | -0.41406 | 5.836 | -28.3571 | -28.7399 | 71.0462 | 39.9678 | 61.0411 | -20.5788 | -18.694 | -11.2643 | 40.7121
42838.4283 | 697 | 22.8833 | 22.8389 | 22.8286 | 22.7487 | 22.3529 | 21.6783 | 22.6908 | 21.7262 | 22.3295 | 22.3322 | 22.2968 | 21.9459 | 21.1634 | 22.1385 | 21.5931 | 21.7711 | 21.9557 | 21.0658 | 21.2872 | 22.5967 | 20.517 | 27.7515 | 42.8008 | 22.0746 | 23.4532 | 67.4399 | 675.0423 | 686.1151 | 675.2668 | 18.9925 | 18.9056 | 26.0864 | 19.1302 | 18.9628 | 172.6521 | 44.972 | 582.58 | 31.9272 | 691.3024 | 924.8308 | 810.7878 | 434.3586 | 44.2789 | 51.0771 | 91.6024 | 120.5497 | 369.308 | 513.6161 | 581.8076 | 641.2947 | 23.2917 | 31.6051 | 28.2704 | 64.2681 | 21.0384 | 45.3895 | 49.7335 | 49.5841 | 22.7099 |  |  | 1.1568 | -1.0311 | -108.0333 | -0.97323 | 7.578 | -197.7895 | -203.1733 | -8.0454 | 6.5126 | 16.6954 | 171.7211 | 0.0069819 | 0.0076981 | 0.00037456 | 22.3618 | 21.9765 | 22.141 | 22.1965 | 21.9983 | 21.2775 | 20.0883 | 22.1716 | 22.3566 | 22.3771 | 22.3262 | 21.9331 | 21.1518 | 22.265 | 421.7775 | 338.6548 | 382.1962 | 186.9626 | 135.0935 | 146.4236 | 91.4421 | 22.343 | 22.0943 | 21.7145 | 22.0382 | 21.8285 | 22.4045 | 21.9303 | 22.9843 | 53.7889 | 635.0724 | 599.3066 | 594.4707 | 569.9708 | 54.9405 | 49.5078 | 736.8179 | 21.8908 | 22.1773 | 216.6242 | 21.5378 | 22.0028 | 22.2898 | 25.1287 | 88.1124 | 21.9202 | 22.8501 | 58.3046 | 851.4822 | 706.3331 | 570.3896 | 598.846 | 771.1257 |  | 786.5273 | 832.621 | 678.3211 | 646.6528 | 732.5214 | 752.9636 |  | 605.2734 |  |  | 392.9988 | 614.0263 | 747.2881 | [5 empty] | 21.8626 | 601.0883 | 21.7056 | 22.0662 | 389.4405 | 21.2779 | 21.8816 | 555.7456 | 694.9933 | 724.3528 |  | 940.2326 | 819.2786 | 783.3269 | 883.7639 | 887.9297 | 637.6822 | 733.9527 | 991.5408 | 895.432 | 857.2927 | 924.8743 | 167.8205 | 749.2103 | 741.3829 | 524.5579 | 641.1849 | 686.5057 | 938.2647 | 947.107 | 821.8082 | 739.5568 | 785.9712 | 590.9399 | 688.9242 | 943.5651 | 923.4767 | 133.0496 | 8.0493 | 14.0005 | 1.2077 | -27.4674 | 3.0951 | 7486.03 | -0.08 | 2.3083 | -1.3515 | -13.8339 | -1.313 | 5.6094 | -28.6577 | -29.0451 | 71.9231 | 42.1831 | 60.3825 | -28.8377 | -31.3041 | -10.2356 | 40.3875
42838.4284 | 698 | 22.8757 | 22.8375 | 22.8327 | 22.7398 | 22.3512 | 21.673 | 22.6882 | 21.7206 | 22.3296 | 22.3258 | 22.2931 | 21.9397 | 21.1609 | 22.134 | 21.5921 | 21.7734 | 21.9521 | 21.0698 | 21.291 | 22.6078 | 20.5182 | 28.0309 | 43.4379 | 22.0806 | 23.4577 | 67.871 | 669.2878 | 692.8372 | 669.3707 | 19.2839 | 19.3818 | 20.5925 | 19.6427 | 19.6174 | 149.6296 | 77.3076 | 602.9619 | 19.8389 | 717.3443 | 976.5489 | 817.915 | 433.1479 | 93.1866 | 53.1772 | 95.4996 | 126.3999 | 382.4183 | 531.0836 | 597.3872 | 653.1942 | 24.5268 | 32.7486 | 29.3582 | 67.2078 | 21.0908 | 45.4276 | 49.7955 | 49.7403 | 22.7366 |  |  | 1.1403 | -1.1875 | -96.012 | -0.61247 | 6.0095 | -197.8026 | -203.2423 | -8.0809 | 6.9261 | 18.3782 | 173.8643 | 0.0069687 | 0.0077425 | 0.00040741 | 22.3728 | 21.9781 | 22.1495 | 22.1971 | 21.9931 | 21.2766 | 20.0904 | 22.1758 | 22.365 | 22.3818 | 22.3277 | 21.9361 | 21.1573 | 22.2646 | 440.8565 | 331.1104 | 415.0303 | 241.864 | 177.4439 | 157.7723 | 98.9825 | 22.3411 | 22.0926 | 21.7118 | 22.0411 | 21.8295 | 22.405 | 21.932 | 23.0096 | 54.3672 | 633.2568 | 595.9341 | 591.5556 | 569.7718 | 70.2617 | 42.6803 | 745.0584 | 21.8902 | 22.184 | 218.2011 | 21.5387 | 21.9981 | 22.284 | 25.1571 | 88.1837 | 21.915 | 22.8546 | 59.2443 | 851.9956 | 701.6307 | 572.6256 | 601.2119 | 771.3055 |  | 788.7487 | 843.9585 | 687.6625 | 648.0145 | 729.6172 | 765.4688 |  | 611.5748 |  |  | 391.2514 | 608.3238 | 740.382 | [5 empty] | 21.8581 | 598.9531 | 21.7067 | 22.0742 | 385.6019 | 21.2745 | 21.8869 | 549.414 | 689.0852 | 717.2656 |  | 943.325 | 825.0962 | 775.1373 | 880.6451 | 889.0886 | 632.5003 | 727.3194 | 994.8795 | 899.3465 | 851.3888 | 926.1706 | 179.7121 | 761.2384 | 747.1584 | 522.7811 | 637.1035 | 681.4541 | 937.3751 | 939.2074 | 818.6341 | 752.8892 | 797.7573 | 587.5237 | 684.6531 | 943.2394 | 917.398 | 121.2386 | 7.6762 | 14.2192 | 1.2984 | -27.5151 | 3.0952 | 7747.44 | -0.06 | 2.2847 | -1.4581 | -13.111 | -1.0472 | 5.0406 | -28.9186 | -29.3135 | 72.5812 | 43.9796 | 59.5969 | -29.4986 | -34.0291 | -9.0291 | 40.035
42838.4284 | 699 | 22.8854 | 22.8419 | 22.8236 | 22.7419 | 22.3538 | 21.6665 | 22.6869 | 21.7306 | 22.323 | 22.3294 | 22.3017 | 21.948 | 21.1605 | 22.1294 | 21.5931 | 21.7724 | 21.9575 | 21.0622 | 21.2918 | 22.6185 | 20.5253 | 28.3255 | 44.0911 | 22.0828 | 23.4683 | 68.2737 | 666.1533 | 697.4528 | 666.667 | 19.3382 | 19.3626 | 20.9759 | 19.6284 | 20.4416 | 92.8321 | 20.7716 | 587.7831 | 22.6718 | 708.3551 | 978.946 | 855.4845 | 441.844 | 148.788 | 55.0771 | 99.0171 | 131.3044 | 391.4642 | 540.9978 | 607.6346 | 664.3697 | 25.7435 | 34.0386 | 30.4318 | 70.5355 | 21.1609 | 45.463 | 49.856 | 49.8554 | 22.7865 |  |  | 0.35441 | -1.4983 | -103.4617 | -0.46003 | 7.6306 | -197.8427 | -203.2371 | -7.9147 | 7.7999 | 19.6319 | 178.7324 | 0.0069129 | 0.0075765 | 0.0003762 | 22.3691 | 21.975 | 22.147 | 22.1926 | 21.9957 | 21.2707 | 20.0884 | 22.171 | 22.3602 | 22.3721 | 22.328 | 21.9298 | 21.1547 | 22.2612 | 457.7828 | 347.2214 | 416.1408 | 251.6479 | 178.7953 | 170.9586 | 106.1718 | 22.3409 | 22.0938 | 21.7113 | 22.0394 | 21.8273 | 22.4124 | 21.9391 | 23.0511 | 54.9349 | 631.421 | 590.5984 | 586.5124 | 567.1325 | 51.7556 | 34.6571 | 760.7081 | 21.8963 | 22.1882 | 219.2992 | 21.5457 | 21.9987 | 22.2897 | 25.1849 | 88.2361 | 21.9159 | 22.8732 | 60.2155 | 856.1301 | 698.4916 | 572.7065 | 601.072 | 778.9125 |  | 791.6585 | 862.5857 | 697.759 | 655.087 | 727.2477 | 779.381 |  | 616.9498 |  |  | 389.8955 | 608.0793 | 742.9525 | [5 empty] | 21.8555 | 600.1453 | 21.7042 | 22.0741 | 384.6307 | 21.2715 | 21.8828 | 543.4023 | 683.4464 | 709.3152 |  | 946.005 | 827.3176 | 762.9766 | 878.0738 | 892.4913 | 628.0631 | 720.6007 | 998.6527 | 903.5928 | 837.6232 | 927.6253 | 192.6257 | 770.9925 | 752.2877 | 521.1943 | 634.0936 | 676.7203 | 939.7192 | 936.9325 | 816.7936 | 763.46 | 805.4337 | 585.0661 | 680.9263 | 951.1053 | 914.8001 | 133.1768 | 7.3002 | 14.4375 | 1.391 | -27.573 | 3.0952 | 7963.58 | -0.04 | 1.2719 | -1.6456 | -13.675 | -0.91186 | 5.7132 | -29.0912 | -29.4851 | 73.2443 | 45.806 | 58.7947 | -29.6637 | -33.2672 | -11.2733 | 39.7482
42838.4284 | 700 | 22.8768 | 22.8338 | 22.834 | 22.7463 | 22.3498 | 21.6742 | 22.6853 | 21.7266 | 22.3311 | 22.3351 | 22.3015 | 21.9421 | 21.159 | 22.1295 | 21.586 | 21.7705 | 21.9572 | 21.0623 | 21.2934 | 22.6229 | 20.5213 | 28.6288 | 44.7621 | 22.077 | 23.4697 | 68.6511 | 663.0927 | 698.8569 | 663.0887 | 19.647 | 19.6845 | 33.0216 | 19.1863 | 21.0141 | 136.2946 | 22.7801 | 557.577 | 48.5109 | 694.6386 | 974.962 | 874.5961 | 458.9613 | 27.1283 | 57.2951 | 103.04 | 144.8089 | 406.0231 | 552.1951 | 616.105 | 672.742 | 26.9312 | 35.5758 | 31.4071 | 74.3629 | 21.2173 | 45.5161 | 49.9226 | 49.9447 | 22.8479 |  |  | -0.40915 | -1.7966 | -133.3381 | -0.45411 | 7.9795 | -197.8158 | -203.291 | -8.2938 | 7.4235 | 18.1233 | 185.406 | 0.0065416 | 0.007294 | 0.00039591 | 22.3727 | 21.981 | 22.1451 | 22.1924 | 22.0001 | 21.2699 | 20.0932 | 22.1688 | 22.3563 | 22.3753 | 22.327 | 21.9291 | 21.1561 | 22.2633 | 465.2417 | 321.3345 | 394.4774 | 257.6251 | 184.2149 | 182.1615 | 112.86 | 22.3393 | 22.0944 | 21.7098 | 22.0338 | 21.8289 | 22.4215 | 21.933 | 23.0861 | 55.4909 | 629.2741 | 584.2102 | 580.1909 | 559.9432 | 67.4155 | 34.2492 | 776.6679 | 21.8973 | 22.182 | 219.1296 | 21.5455 | 21.9998 | 22.2962 | 25.2567 | 88.2783 | 21.9215 | 22.8816 | 61.1852 | 860.6441 | 696.4174 | 571.3534 | 599.4821 | 786.0001 |  | 795.0258 | 875.121 | 709.2815 | 656.2445 | 724.7596 | 790.9426 |  | 622.6807 |  |  | 388.3171 | 609.367 | 746.4742 | [5 empty] | 21.8679 | 600.841 | 21.7117 | 22.0778 | 383.125 | 21.2771 | 21.8882 | 537.8011 | 678.2605 | 703.1397 |  | 954.2987 | 829.9562 | 749.1983 | 868.7701 | 892.4677 | 623.7114 | 715.3213 | 1000.8196 | 909.1781 | 822.9574 | 920.8918 | 201.3652 | 780.2191 | 756.0763 | 519.8999 | 632.252 | 673.2179 | 948.3183 | 937.3437 | 815.4532 | 773.9042 | 812.5005 | 583.5933 | 678.7706 | 957.5045 | 912.7063 | 165.5147 | 7.0221 | 14.6358 | 1.4817 | -27.7229 | 3.0952 | 8120.58 | -0.14 | -1.364 | -1.8118 | -15.608 | -0.91086 | 5.8704 | -29.2288 | -29.6305 | 74.0673 | 48.2126 | 58.1306 | -29.0166 | -30.032 | -11.6813 | 39.5292
42838.4284 | 701 | 22.8794 | 22.843 | 22.8329 | 22.743 | 22.356 | 21.6767 | 22.6851 | 21.7298 | 22.3266 | 22.3299 | 22.2993 | 21.951 | 21.1588 | 22.1351 | 21.5859 | 21.7731 | 21.9605 | 21.062 | 21.2885 | 22.6352 | 20.531 | 28.9583 | 45.4478 | 22.0832 | 23.4897 | 69.0117 | 657.5211 | 698.1619 | 657.3047 | 19.5141 | 19.798 | 64.5197 | 19.4309 | 19.3015 | 151.4295 | 34.8658 | 577.7385 | 73.7565 | 706.8579 | 964.0446 | 869.4813 | 454.7716 | 52.3567 | 59.4246 | 107.0756 | 158.1574 | 421.04 | 564.2674 | 623.812 | 679.0011 | 27.5945 | 36.9237 | 31.8339 | 77.5971 | 21.2806 | 45.5654 | 49.9998 | 49.9786 | 22.895 |  |  | 0.28607 | -1.1947 | -159.0235 | -0.20309 | 8.2653 | -197.8171 | -203.1694 | -7.4172 | 6.0716 | 15.1349 | 181.6654 | 0.00654 | 0.007179 | 0.00040084 | 22.3761 | 21.9807 | 22.1458 | 22.1899 | 21.9927 | 21.2669 | 20.0905 | 22.173 | 22.3481 | 22.3747 | 22.3322 | 21.9243 | 21.1542 | 22.2558 | 461.0187 | 299.4831 | 375.2248 | 268.4982 | 184.2213 | 195.2649 | 120.2497 | 22.3458 | 22.0912 | 21.7186 | 22.0494 | 21.8315 | 22.4269 | 21.9374 | 23.1177 | 56.1204 | 626.7141 | 579.5963 | 576.116 | 557.5137 | 72.35 | 61.2878 | 785.8395 | 21.8945 | 22.1782 | 217.9864 | 21.5356 | 21.9942 | 22.2948 | 25.3112 | 88.3059 | 21.9249 | 22.8854 | 62.1423 | 866.0604 | 695.1304 | 568.9261 | 597.3623 | 798.4734 |  | 798.9788 | 880.2316 | 719.3171 | 656.3671 | 722.653 | 801.0623 |  | 627.4912 |  |  | 385.9581 | 610.5271 | 755.6226 | [5 empty] | 21.871 | 600.2269 | 21.7133 | 22.0799 | 378.3318 | 21.2852 | 21.8961 | 532.8103 | 673.394 | 699.4067 |  | 958.8835 | 830.931 | 735.7139 | 858.2341 | 888.6413 | 619.8632 | 710.7099 | 1003.1996 | 914.1624 | 809.6301 | 912.4905 | 210.4415 | 787.6958 | 761.3122 | 518.7433 | 631.1817 | 669.3551 | 954.4564 | 939.3235 | 814.9388 | 786.2091 | 824.1723 | 581.8198 | 675.8617 | 959.3194 | 915.6025 | 136.5256 | 6.676 | 14.7972 | 1.5647 | -27.6696 | 3.0952 | 8216.69 | -0.03 | 1.137 | -1.4853 | -17.1363 | -0.6124 | 6.0005 | -29.3553 | -29.7497 | 74.9294 | 50.5409 | 57.5954 | -26.7986 | -26.9725 | -11.1537 | 39.1006
42838.4284 | 702 | 22.8804 | 22.8416 | 22.8321 | 22.7449 | 22.3548 | 21.6783 | 22.6887 | 21.728 | 22.332 | 22.3315 | 22.3034 | 21.95 | 21.1617 | 22.1295 | 21.5898 | 21.7755 | 21.9641 | 21.071 | 21.2956 | 22.6451 | 20.5463 | 29.2985 | 46.1566 | 22.0871 | 23.5125 | 69.3591 | 652.0457 | 693.96 | 651.7213 | 19.3707 | 19.4218 | 64.7886 | 19.8365 | 20.0858 | 169.1801 | 61.5263 | 568.8247 | 26.8274 | 728.9743 | 982.9864 | 866.6747 | 442.4859 | 70.8321 | 61.5342 | 111.333 | 167.2041 | 444.8959 | 581.3295 | 636.0144 | 686.5263 | 28.1774 | 38.3722 | 32.1482 | 81.1673 | 21.344 | 45.596 | 50.0712 | 50.0001 | 22.9388 |  |  | 0.63961 | -1.7296 | -184.509 | -0.30166 | 8.2279 | -197.7941 | -203.2377 | -8.1716 | 6.6274 | 15.6898 | 195.1336 | 0.0066993 | 0.0073745 | 0.00041563 | 22.375 | 21.9737 | 22.1403 | 22.1886 | 21.9859 | 21.2711 | 20.0856 | 22.1637 | 22.3466 | 22.3679 | 22.3116 | 21.925 | 21.1411 | 22.2518 | 508.2067 | 336.0632 | 413.9286 | 273.3365 | 192.5801 | 209.3102 | 129.55 | 22.3462 | 22.089 | 21.7146 | 22.0447 | 21.826 | 22.4383 | 21.9379 | 23.1587 | 56.6556 | 625.198 | 577.9997 | 576.051 | 561.754 | 66.2619 | 46.1188 | 791.9209 | 21.8947 | 22.1815 | 216.2929 | 21.5345 | 21.9963 | 22.2997 | 25.3655 | 88.3505 | 21.9254 | 22.8956 | 63.0965 | 867.0347 | 694.7411 | 567.0547 | 595.8153 | 806.1145 |  | 802.7442 | 883.6419 | 728.7177 | 657.1974 | 720.8875 | 805.7587 |  | 631.6665 |  |  | 380.9309 | 613.2188 | 759.8777 | [5 empty] | 21.8638 | 600.3015 | 21.7068 | 22.0749 | 372.3595 | 21.2785 | 21.8866 | 528.4736 | 669.3609 | 695.5113 |  | 963.8842 | 830.73 | 730.8183 | 849.953 | 883.8385 | 617.2473 | 706.8295 | 1002.9823 | 918.7592 | 807.1184 | 908.7098 | 223.1501 | 795.0735 | 766.7532 | 516.472 | 629.2802 | 664.6901 | 956.8629 | 940.8581 | 814.8457 | 799.4445 | 836.2009 | 579.025 | 671.9592 | 965.3617 | 916.425 | 146.0683 | 6.3601 | 14.9531 | 1.6382 | -27.4959 | 3.0952 | 8280.22 | -0.12 | 1.695 | -1.7971 | -18.5616 | -0.75053 | 6.0274 | -29.5525 | -29.9565 | 75.8797 | 52.8213 | 57.1289 | -30.1387 | -30.1065 | -9.8709 | 38.6908
42838.4284 | 703 | 22.8857 | 22.8393 | 22.8379 | 22.7465 | 22.3587 | 21.674 | 22.6875 | 21.7289 | 22.3345 | 22.3326 | 22.3064 | 21.9487 | 21.1628 | 22.1354 | 21.5892 | 21.765 | 21.9608 | 21.0663 | 21.3005 | 22.6433 | 20.5353 | 29.6481 | 46.8607 | 22.0783 | 23.5148 | 69.7013 | 646.7109 | 688.6275 | 646.3831 | 19.5039 | 19.7369 | 52.681 | 20.3675 | 43.2697 | 211.0513 | 101.0657 | 564.5287 | 25.49 | 729.8122 | 987.0828 | 884.0425 | 462.5392 | 177.7477 | 63.2308 | 114.4149 | 175.2064 | 457.5229 | 590.5945 | 643.4598 | 691.6365 | 28.8954 | 39.6679 | 32.5843 | 84.3116 | 21.4332 | 45.6572 | 50.1626 | 50.0333 | 22.994 |  |  | 0.10405 | -1.4635 | -196.456 | 0.31603 | 7.9111 | -197.796 | -203.3284 | -7.9363 | 6.9364 | 17.3795 | 196.6719 | 0.0065482 | 0.0071954 | 0.00041891 | 22.3811 | 21.9791 | 22.1433 | 22.1945 | 21.9954 | 21.2678 | 20.0868 | 22.1698 | 22.3527 | 22.373 | 22.3239 | 21.9317 | 21.1519 | 22.2565 | 537.3216 | 327.6426 | 421.1822 | 279.7567 | 206.6664 | 222.8463 | 138.1065 | 22.3358 | 22.0883 | 21.7181 | 22.0406 | 21.8253 | 22.4469 | 21.9328 | 23.194 | 57.165 | 623.6022 | 575.1596 | 573.5648 | 559.012 | 67.5423 | 44.8536 | 795.6171 | 21.8964 | 22.1891 | 214.0099 | 21.5426 | 21.999 | 22.3049 | 25.405 | 88.3667 | 21.9274 | 22.9085 | 64.0455 | 866.5023 | 694.4039 | 566.1897 | 595.0004 | 803.7317 |  | 806.258 | 879.2812 | 738.0551 | 658.7912 | 719.2431 | 808.7737 |  | 636.4405 |  |  | 375.4007 | 617.7971 | 761.4233 | [5 empty] | 21.8628 | 601.0248 | 21.6995 | 22.0744 | 366.2854 | 21.2783 | 21.8891 | 524.9902 | 666.144 | 690.9025 |  | 965.0821 | 829.9319 | 727.8363 | 848.3973 | 882.5457 | 614.8098 | 703.6868 | 984.9408 | 920.2143 | 803.6103 | 911.0874 | 232.1224 | 803.8147 | 772.8071 | 513.4308 | 626.603 | 660.2304 | 959.6729 | 941.3216 | 813.151 | 811.8499 | 847.8595 | 576.3476 | 667.7705 | 975.6273 | 907.8669 | 116.3286 | 6.1079 | 15.0938 | 1.6983 | -27.7123 | 3.0952 | 8298.45 | -0.08 | 0.68168 | -1.6597 | -19.2297 | 0.77126 | 5.9344 | -29.6734 | -30.0856 | 77.0409 | 55.3614 | 56.6736 | -31.5101 | -29.8309 | -8.929 | 38.461
42838.4284 | 704 | 22.8868 | 22.8427 | 22.8339 | 22.7508 | 22.3573 | 21.6701 | 22.6902 | 21.7289 | 22.3287 | 22.3299 | 22.2994 | 21.9446 | 21.1628 | 22.1336 | 21.587 | 21.7663 | 21.9585 | 21.0659 | 21.2996 | 22.653 | 20.5466 | 30.0139 | 47.5718 | 22.0834 | 23.5203 | 69.9933 | 641.16 | 685.1295 | 640.9275 | 19.5822 | 19.8873 | 72.1986 | 19.496 | 76.2785 | 241.1463 | 52.6654 | 571.0607 | 60.1964 | 737.2056 | 990.494 | 878.584 | 465.8987 | 85.3965 | 64.8088 | 117.5071 | 186.4205 | 470.8665 | 606.1225 | 652.3757 | 697.7221 | 29.4414 | 41.0413 | 32.9859 | 87.6746 | 21.501 | 45.7331 | 50.2513 | 50.0252 | 23.065 |  |  | 0.17699 | -1.3984 | -196.4712 | -0.39957 | 8.3547 | -197.8092 | -203.3264 | -7.8424 | 6.4312 | 16.9843 | 196.5094 | 0.0063247 | 0.0069868 | 0.00040577 | 22.3728 | 21.9655 | 22.1412 | 22.188 | 21.9873 | 21.2646 | 20.0844 | 22.1655 | 22.3425 | 22.3696 | 22.3194 | 21.9219 | 21.1426 | 22.2522 | 554.6102 | 330.3558 | 440.8688 | 277.104 | 210.9716 | 236.2305 | 146.5438 | 22.3343 | 22.0846 | 21.7216 | 22.0326 | 21.8255 | 22.4456 | 21.9386 | 23.2296 | 57.6645 | 621.7688 | 573.0434 | 571.6616 | 556.7232 | 79.4701 | 37.6357 | 797.1134 | 21.9007 | 22.1932 | 213.5266 | 21.547 | 22.0057 | 22.3071 | 25.4633 | 88.3573 | 21.9338 | 22.9242 | 64.9735 | 862.8608 | 692.8832 | 567.2696 | 595.0182 | 808.5069 |  | 809.3642 | 876.3143 | 746.6591 | 653.6312 | 717.1407 | 810.2086 |  | 641.3895 |  |  | 375.6445 | 622.3774 | 761.723 | [5 empty] | 21.8687 | 599.2793 | 21.7072 | 22.0837 | 360.8666 | 21.2869 | 21.8868 | 520.7361 | 663.1947 | 687.2938 |  | 950.6217 | 830.2753 | 721.1191 | 848.4182 | 883.2329 | 612.0625 | 701.4112 | 965.8641 | 919.8855 | 799.7346 | 910.8551 | 240.6007 | 818.0723 | 780.5327 | 511.4108 | 623.1138 | 655.8987 | 962.8631 | 941.4111 | 811.5751 | 822.0683 | 862.0017 | 573.9567 | 663.2458 | 982.2335 | 902.1626 | 114.7698 | 5.8005 | 15.2368 | 1.7554 | -27.7738 | 3.0953 | 8314.97 | -0.1 | 0.88642 | -1.6289 | -19.307 | -0.87069 | 6.1281 | -29.8184 | -30.2314 | 77.8844 | 57.7264 | 56.2939 | -31.5583 | -30.9436 | -10.8397 | 38.1747
42838.4284 | 705 | 22.8819 | 22.8357 | 22.8255 | 22.7425 | 22.3499 | 21.6668 | 22.6823 | 21.7278 | 22.3347 | 22.3275 | 22.2915 | 21.9383 | 21.156 | 22.1213 | 21.5857 | 21.7633 | 21.9553 | 21.0625 | 21.2867 | 22.6605 | 20.5519 | 30.4143 | 48.3328 | 22.0809 | 23.5371 | 70.3333 | 641.652 | 682.4667 | 641.7979 | 20.2263 | 20.4517 | 58.1567 | 19.3158 | 52.3236 | 249.3294 | 28.9698 | 574.5841 | 116.9862 | 755.5629 | 989.0133 | 886.3568 | 457.6727 | 28.953 | 66.5583 | 121.357 | 190.6441 | 482.5375 | 622.6309 | 664.484 | 706.1269 | 29.6861 | 42.4685 | 33.556 | 91.2642 | 21.5547 | 45.8227 | 50.344 | 50.014 | 23.1321 |  |  | 0.43195 | -0.81554 | -196.5264 | -0.21361 | 7.9801 | -197.8381 | -203.4651 | -7.1465 | 6.7671 | 17.5973 | 200.8091 | 0.0062525 | 0.0068784 | 0.00038934 | 22.3841 | 21.9781 | 22.1385 | 22.1927 | 21.9976 | 21.2766 | 20.0816 | 22.1626 | 22.3483 | 22.3658 | 22.3205 | 21.9307 | 21.1479 | 22.2516 | 579.9218 | 348.2417 | 453.3362 | 285.8967 | 219.3676 | 250.5617 | 154.7436 | 22.3418 | 22.0864 | 21.7237 | 22.0377 | 21.8276 | 22.47 | 21.9455 | 23.2788 | 58.1772 | 619.9743 | 571.4681 | 570.4107 | 556.8113 | 79.474 | 55.54 | 796.7558 | 21.902 | 22.1915 | 214.5323 | 21.5433 | 22.0026 | 22.3146 | 25.5491 | 88.3687 | 21.9322 | 22.9404 | 65.8968 | 856.8678 | 689.9128 | 569.4825 | 595.1657 | 797.0712 |  | 810.8404 | 871.125 | 753.1963 | 647.2053 | 715.0765 | 809.1311 |  | 645.5937 |  |  | 376.7333 | 622.9338 | 752.1668 | [5 empty] | 21.8735 | 596.0498 | 21.698 | 22.0746 | 355.6776 | 21.2746 | 21.8837 | 516.0819 | 660.1679 | 684.4088 |  | 941.5384 | 830.1883 | 715.1112 | 845.4113 | 881.1941 | 609.7011 | 697.8736 | 963.1615 | 922.7261 | 795.9858 | 908.8409 | 249.5849 | 839.5587 | 787.0414 | 510.0482 | 619.1789 | 651.6686 | 959.8397 | 931.8433 | 811.0047 | 832.0659 | 875.8834 | 570.878 | 660.4244 | 980.4263 | 895.2531 | 111.2071 | 5.5127 | 15.3899 | 1.8477 | -27.6188 | 3.0952 | 8346.86 | -0.04 | 1.3854 | -1.25 | -19.4046 | -0.63974 | 6.0282 | -30.015 | -30.4389 | 78.6686 | 59.6399 | 55.9619 | -32.3302 | -31.2762 | -11.436 | 37.8315
42838.4284 | 706 | 22.881 | 22.8326 | 22.8305 | 22.7452 | 22.3513 | 21.6668 | 22.6731 | 21.7227 | 22.3192 | 22.3223 | 22.2932 | 21.9383 | 21.1552 | 22.1203 | 21.5958 | 21.7675 | 21.9557 | 21.0677 | 21.2941 | 22.6687 | 20.5603 | 30.8135 | 49.0528 | 22.087 | 23.5485 | 70.6475 | 638.6713 | 680.9258 | 638.2697 | 20.1614 | 19.3978 | 105.2767 | 19.7432 | 25.4954 | 210.0378 | 47.1965 | 596.8781 | 264.0179 | 806.0373 | 983.5889 | 881.9599 | 475.2739 | 101.4533 | 68.3782 | 125.0848 | 195.119 | 490.6233 | 636.9784 | 673.9535 | 713.4055 | 29.9384 | 43.771 | 34.1939 | 94.4469 | 21.6367 | 45.9573 | 50.4313 | 49.9964 | 23.1951 |  |  | 0.53841 | -1.8209 | -196.5264 | -0.19389 | 7.9335 | -197.8368 | -203.1799 | -7.5894 | 6.7914 | 18.3251 | 188.6493 | 0.0062015 | 0.0069309 | 0.00041234 | 22.3965 | 21.9804 | 22.1457 | 22.1934 | 21.9982 | 21.2758 | 20.0824 | 22.1666 | 22.3537 | 22.3726 | 22.3222 | 21.9368 | 21.1496 | 22.2537 | 591.8213 | 361.4905 | 460.0413 | 304.7178 | 225.9846 | 265.0939 | 163.5368 | 22.3409 | 22.0925 | 21.7264 | 22.0402 | 21.8369 | 22.4749 | 21.9376 | 23.3322 | 58.7206 | 618.1518 | 568.1157 | 567.0894 | 555.2257 | 68.6099 | 48.9788 | 800.5432 | 21.8965 | 22.1847 | 214.3653 | 21.5401 | 21.996 | 22.3181 | 25.5965 | 88.3759 | 21.9286 | 22.9448 | 66.8422 | 848.475 | 687.1507 | 572.0697 | 596.4246 | 785.6687 |  | 811.709 | 873.9288 | 760.0392 | 639.8981 | 712.8795 | 814.1014 |  | 649.6813 |  |  | 378.6359 | 625.4663 | 744.2718 | [5 empty] | 21.864 | 591.9503 | 21.7022 | 22.0809 | 352.6816 | 21.2796 | 21.8842 | 511.5438 | 656.9903 | 679.4866 |  | 949.1238 | 830.2379 | 707.2724 | 838.1421 | 879.7683 | 607.5962 | 693.1301 | 956.9327 | 925.2022 | 788.2081 | 903.8429 | 257.8664 | 861.8253 | 794.9118 | 508.4032 | 615.7121 | 649.1138 | 957.7302 | 925.4819 | 807.5446 | 839.1953 | 888.2714 | 567.7448 | 658.3626 | 975.4125 | 887.5308 | 112.8258 | 5.248 | 15.5468 | 2.0012 | -27.6285 | 3.0952 | 8514.43 | -0.02 | 1.5438 | -1.8767 | -19.4961 | -0.61238 | 6.0408 | -30.1661 | -30.5707 | 79.2607 | 61.4468 | 55.6245 | -31.5442 | -30.8831 | -11.2939 | 37.5314
42838.4285 | 707 | 22.891 | 22.8425 | 22.8425 | 22.7459 | 22.3577 | 21.6742 | 22.6921 | 21.7269 | 22.3347 | 22.3293 | 22.3031 | 21.9438 | 21.1594 | 22.1389 | 21.583 | 21.7651 | 21.9572 | 21.0557 | 21.2912 | 22.6715 | 20.5676 | 31.2189 | 49.7599 | 22.0833 | 23.5552 | 70.9477 | 636.6503 | 681.0677 | 636.5332 | 19.6609 | 19.8017 | 131.1286 | 20.6209 | 39.2912 | 157.0461 | 80.0947 | 541.3049 | 20.6206 | 760.0345 | 990.3426 | 891.2538 | 437.3178 | 117.3273 | 70.4705 | 129.554 | 201.846 | 507.0988 | 650.017 | 682.5247 | 720.3427 | 30.0826 | 45.307 | 34.8148 | 98.2208 | 21.7051 | 46.0875 | 50.5171 | 49.9887 | 23.2391 |  |  | 0.47861 | -1.3255 | -196.4731 | -0.10453 | 7.9506 | -197.8539 | -203.2384 | -7.4475 | 6.7984 | 18.0037 | 202.5024 | 0.006333 | 0.0069096 | 0.00039591 | 22.4019 | 21.9775 | 22.1511 | 22.1976 | 21.9967 | 21.2738 | 20.0864 | 22.1667 | 22.3534 | 22.3749 | 22.3256 | 21.9315 | 21.1574 | 22.2563 | 594.7507 | 381.0159 | 476.535 | 308.2699 | 230.1637 | 278.6786 | 171.928 | 22.3437 | 22.0915 | 21.7261 | 22.043 | 21.8357 | 22.4759 | 21.9409 | 23.3778 | 59.1862 | 616.2321 | 563.2615 | 561.72 | 548.4959 | 80.7169 | 45.7308 | 807.0617 | 21.8936 | 22.1807 | 213.4878 | 21.5403 | 21.998 | 22.3224 | 25.6531 | 88.3876 | 21.9311 | 22.9512 | 67.7896 | 839.8285 | 686.0611 | 574.1349 | 598.5111 | 780.3473 |  | 812.7976 | 873.7887 | 767.8421 | 643.3539 | 710.5304 | 819.8302 |  | 653.7827 |  |  | 378.4349 | 625.413 | 741.6405 | [5 empty] | 21.859 | 590.4296 | 21.7109 | 22.0686 | 351.6038 | 21.2772 | 21.886 | 507.1608 | 654.1138 | 675.8478 |  | 951.5096 | 828.6653 | 696.8575 | 834.3222 | 882.6758 | 605.1561 | 690.8616 | 961.4323 | 927.8237 | 774.2025 | 898.7632 | 268.1916 | 871.4775 | 800.56 | 506.8158 | 614.259 | 645.0298 | 955.9747 | 919.3298 | 804.2718 | 847.9212 | 896.674 | 564.9244 | 655.2021 | 964.1943 | 883.346 | 133.3347 | 4.9897 | 15.7266 | 2.221 | -27.6785 | 3.0951 | 8759.33 | 0 | 1.4541 | -1.6101 | -19.6025 | -0.45214 | 6.0747 | -30.3036 | -30.7132 | 79.7544 | 63.6415 | 54.9543 | -29.8614 | -31.6202 | -9.04 | 37.3577
42838.4285 | 708 | 22.8853 | 22.8408 | 22.8381 | 22.7477 | 22.356 | 21.6706 | 22.6844 | 21.7291 | 22.3318 | 22.3305 | 22.3014 | 21.9412 | 21.1579 | 22.1309 | 21.5869 | 21.7647 | 21.9664 | 21.0641 | 21.2942 | 22.6853 | 20.5758 | 31.654 | 50.4774 | 22.0946 | 23.5665 | 71.2452 | 634.5523 | 679.4257 | 634.124 | 19.8456 | 20.0368 | 68.4683 | 20.2334 | 46.9445 | 213.5735 | 90.1002 | 531.9089 | 30.8608 | 712.734 | 983.8953 | 879.2718 | 456.2723 | 182.1818 | 72.0148 | 132.5257 | 203.9092 | 518.2577 | 654.8584 | 688.3534 | 724.3454 | 30.0628 | 46.6488 | 35.4534 | 101.5482 | 21.7921 | 46.2452 | 50.6111 | 50.0074 | 23.3192 |  |  | 0.44707 | -1.8978 | -194.7837 | -0.057214 | 8.6741 | -197.8342 | -203.1615 | -7.4001 | 7.4453 | 20.0734 | 223.5624 | 0.006351 | 0.0069375 | 0.00035977 | 22.4069 | 21.9777 | 22.149 | 22.1911 | 21.9982 | 21.2721 | 20.0865 | 22.1712 | 22.354 | 22.3746 | 22.3252 | 21.9293 | 21.1502 | 22.2585 | 598.86 | 403.0305 | 494.9914 | 313.1014 | 226.4443 | 292.2226 | 180.0352 | 22.3376 | 22.0908 | 21.7177 | 22.04 | 21.8344 | 22.4876 | 21.9381 | 23.4184 | 59.6443 | 614.076 | 559.7546 | 558.013 | 544.1642 | 68.4331 | 42.3344 | 810.0584 | 21.8989 | 22.1844 | 214.1127 | 21.5448 | 22.0044 | 22.3269 | 25.7318 | 88.3994 | 21.9452 | 22.9637 | 68.7082 | 843.072 | 685.4769 | 576.2981 | 600.9522 | 787.464 |  | 813.7411 | 874.7419 | 773.9528 | 643.7299 | 708.7378 | 822.9691 |  | 657.1453 |  |  | 375.8698 | 622.7209 | 740.8978 | [5 empty] | 21.8655 | 589.5616 | 21.7072 | 22.0761 | 348.9163 | 21.2783 | 21.8816 | 502.9252 | 651.0586 | 672.506 |  | 962.5844 | 827.0707 | 685.6129 | 823.1898 | 877.2976 | 602.2387 | 688.107 | 978.1785 | 931.9124 | 761.4153 | 888.3318 | 277.4986 | 885.6625 | 806.1135 | 505.1692 | 612.7985 | 641.5601 | 957.743 | 909.5811 | 799.254 | 853.7975 | 904.3323 | 564.0818 | 652.5737 | 958.6206 | 874.1297 | 143.8384 | 4.7805 | 15.8861 | 2.4969 | -27.7149 | 3.0952 | 9010.15 | -0.12 | 1.4035 | -1.9337 | -19.5899 | -0.33574 | 6.3643 | -30.3944 | -30.8009 | 79.8574 | 65.362 | 54.5082 | -28.2776 | -32.6035 | -9.1842 | 37.0754
42838.4285 | 709 | 22.8798 | 22.8407 | 22.8297 | 22.7476 | 22.3553 | 21.6662 | 22.6922 | 21.7301 | 22.3247 | 22.3297 | 22.2971 | 21.9406 | 21.1504 | 22.1304 | 21.593 | 21.7666 | 21.9606 | 21.0726 | 21.3067 | 22.6982 | 20.5824 | 32.0964 | 51.2113 | 22.0863 | 23.5851 | 71.4854 | 630.7317 | 675.6828 | 629.9476 | 20.3306 | 20.4033 | 119.9895 | 19.6721 | 70.8744 | 207.1679 | 25.3622 | 533.0142 | 74.524 | 715.5881 | 977.7588 | 875.0487 | 436.096 | 19.9638 | 73.4643 | 135.3004 | 212.3292 | 530.8033 | 660.662 | 689.9936 | 725.681 | 30.4846 | 48.147 | 36.1112 | 105.1638 | 21.8575 | 46.3891 | 50.7014 | 50.0381 | 23.386 |  |  | 0.18159 | -1.5673 | -196.4856 | 0.17672 | 8.6491 | -197.8342 | -203.1773 | -6.998 | 6.9203 | 18.0085 | 218.5427 | 0.005937 | 0.0067091 | 0.00038934 | 22.4021 | 21.9778 | 22.1339 | 22.1849 | 21.9974 | 21.2648 | 20.0745 | 22.1664 | 22.3443 | 22.365 | 22.3157 | 21.9205 | 21.1482 | 22.2421 | 580.1356 | 373.9185 | 496.5362 | 322.5187 | 242.9334 | 304.8483 | 188.3912 | 22.3416 | 22.0861 | 21.7343 | 22.0542 | 21.8352 | 22.5045 | 21.9464 | 23.4698 | 60.101 | 612.1707 | 557.297 | 556.3688 | 543.5598 | 70.2831 | 56.1284 | 815.6055 | 21.8996 | 22.1886 | 214.3582 | 21.5537 | 22.0067 | 22.3329 | 25.8213 | 88.3911 | 21.9464 | 22.9727 | 69.5913 | 849.8652 | 684.9034 | 577.6534 | 602.4693 | 795.1867 |  | 815.2126 | 878.5599 | 780.4992 | 637.2591 | 706.6709 | 827.9014 |  | 660.5891 |  |  | 374.9976 | 612.9894 | 745.2522 | [5 empty] | 21.8692 | 587.1762 | 21.7017 | 22.0721 | 345.9333 | 21.2781 | 21.8809 | 498.7106 | 647.4681 | 669.5041 |  | 978.7214 | 826.3193 | 677.4164 | 814.021 | 870.4214 | 599.357 | 685.7596 | 986.8216 | 934.7941 | 753.9348 | 881.9201 | 285.8578 | 895.9191 | 811.2719 | 503.7316 | 610.727 | 638.1483 | 957.5136 | 904.9661 | 794.4039 | 856.9512 | 910.4019 | 562.9053 | 649.7485 | 949.617 | 869.6463 | 154.3605 | 4.5485 | 16.0434 | 2.7847 | -27.8744 | 3.0952 | 9229.05 | -0.06 | 0.89245 | -1.7632 | -19.7425 | 0.59208 | 6.3606 | -30.4203 | -30.8283 | 80.1131 | 67.1584 | 54.1882 | -24.2591 | -31.6654 | -10.959 | 36.7384
42838.4285 | 710 | 22.8813 | 22.8436 | 22.8339 | 22.7488 | 22.3529 | 21.67 | 22.693 | 21.7287 | 22.3344 | 22.3361 | 22.2988 | 21.9441 | 21.1558 | 22.1314 | 21.5938 | 21.7697 | 21.9632 | 21.068 | 21.305 | 22.7115 | 20.5966 | 32.5469 | 51.9305 | 22.0902 | 23.5983 | 71.6935 | 627.5451 | 671.2709 | 626.6727 | 20.8329 | 20.1041 | 157.1675 | 19.9072 | 72.0118 | 226.1929 | 36.7497 | 521.4339 | 141.8903 | 714.1833 | 983.4492 | 885.0509 | 419.4702 | 28.0731 | 75.0637 | 138.5091 | 217.2467 | 540.4715 | 668.8393 | 695.622 | 729.2999 | 30.9189 | 49.6836 | 36.385 | 108.935 | 21.9166 | 46.5378 | 50.7832 | 50.0325 | 23.4443 |  |  | -0.097682 | -1.7966 | -196.4915 | -0.14921 | 8.4125 | -197.8532 | -203.3396 | -7.525 | 6.6562 | 17.9802 | 224.2733 | 0.0058861 | 0.0064989 | 0.00037456 | 22.4046 | 21.9758 | 22.1462 | 22.1868 | 21.9951 | 21.2734 | 20.0775 | 22.1632 | 22.3401 | 22.3804 | 22.3217 | 21.9232 | 21.1452 | 22.2416 | 579.9454 | 384.4569 | 497.5057 | 318.9077 | 253.0896 | 317.4404 | 196.4067 | 22.3419 | 22.0865 | 21.7315 | 22.0431 | 21.8309 | 22.5069 | 21.9454 | 23.5157 | 60.5633 | 610.4432 | 554.8839 | 554.193 | 544.32 | 70.5389 | 36.3724 | 818.968 | 21.8949 | 22.1836 | 213.7425 | 21.5467 | 21.9978 | 22.3443 | 25.9019 | 88.3965 | 21.9355 | 22.9754 | 70.484 | 855.9329 | 686.3852 | 578.5995 | 603.3574 | 818.7049 |  | 818.6 | 883.0441 | 787.4164 | 634.8017 | 704.4687 | 832.9737 |  | 665.1157 |  |  | 378.3658 | 609.1109 | 756.0316 | [5 empty] | 21.8584 | 585.8955 | 21.6956 | 22.0707 | 344.3463 | 21.2711 | 21.8767 | 495.7772 | 644.2648 | 665.8414 |  | 980.1911 | 830.1353 | 670.9779 | 809.3445 | 870.2966 | 597.4275 | 682.689 | 980.505 | 938.4212 | 746.2782 | 882.7848 | 291.2706 | 900.7724 | 814.4504 | 501.8444 | 608.6802 | 634.7889 | 958.1311 | 898.0104 | 790.1349 | 858.1345 | 913.2029 | 561.0697 | 647.8959 | 943.2531 | 860.5081 | 125.092 | 4.2959 | 16.1574 | 3.0682 | -27.6908 | 3.0952 | 9414.17 | -0.05 | -0.65336 | -1.8952 | -19.8202 | -0.54618 | 6.2913 | -30.5105 | -30.9306 | 80.549 | 69.0792 | 53.727 | -22.2691 | -30.6991 | -10.1082 | 36.3982
42838.4285 | 711 | 22.8837 | 22.8418 | 22.8348 | 22.7518 | 22.3571 | 21.6707 | 22.6895 | 21.7213 | 22.3322 | 22.338 | 22.3051 | 21.9461 | 21.1616 | 22.1327 | 21.5829 | 21.7623 | 21.9603 | 21.0659 | 21.3077 | 22.7081 | 20.6002 | 33.0137 | 52.6509 | 22.0936 | 23.604 | 71.9244 | 623.4274 | 667.5315 | 622.6693 | 19.8864 | 19.4859 | 189.9061 | 19.8631 | 61.693 | 228.7532 | 58.381 | 519.8964 | 68.4965 | 719.8831 | 981.6577 | 878.2568 | 415.2574 | 62.9573 | 76.5421 | 141.4194 | 223.2236 | 555.2864 | 677.7208 | 700.9914 | 732.3657 | 31.1782 | 50.9959 | 36.3993 | 112.2009 | 21.974 | 46.6718 | 50.8703 | 50.0528 | 23.5098 |  |  | 0.36033 | -1.6133 | -196.4252 | 0.20498 | 8.314 | -197.8263 | -203.3278 | -7.6715 | 6.412 | 17.4204 | 220.5179 | 0.0057892 | 0.0064545 | 0.00038441 | 22.4161 | 21.9765 | 22.1402 | 22.201 | 21.9986 | 21.2728 | 20.0841 | 22.1614 | 22.3598 | 22.3788 | 22.3169 | 21.9272 | 21.1457 | 22.2544 | 593.5672 | 378.227 | 469.1465 | 307.1863 | 252.997 | 330.2457 | 202.6235 | 22.3417 | 22.0929 | 21.7195 | 22.0397 | 21.8336 | 22.5117 | 21.9409 | 23.5661 | 61.0136 | 608.7666 | 553.039 | 551.9112 | 542.4321 | 73.1104 | 33.2472 | 824.5086 | 21.903 | 22.1876 | 214.197 | 21.5473 | 21.9993 | 22.349 | 25.9413 | 88.3846 | 21.9408 | 22.9857 | 71.4031 | 856.1855 | 687.8298 | 581.7021 | 605.6846 | 825.0754 |  | 820.9095 | 890.3996 | 793.7886 | 639.5719 | 702.7289 | 837.4059 |  | 669.7267 |  |  | 379.9126 | 608.3027 | 761.6278 | [5 empty] | 21.8532 | 587.755 | 21.6956 | 22.0699 | 343.1178 | 21.2664 | 21.8762 | 493.5309 | 641.8359 | 662.9642 |  | 977.4931 | 831.3583 | 663.3083 | 803.709 | 869.8306 | 595.7445 | 681.1837 | 979.1967 | 940.002 | 738.6496 | 879.1832 | 298.8144 | 904.0978 | 818.0929 | 499.8174 | 606.4416 | 631.8131 | 960.9164 | 894.2122 | 785.4118 | 861.8212 | 918.9554 | 558.8486 | 645.5831 | 942.6595 | 856.1697 | 155.5756 | 4.0248 | 16.2475 | 3.3267 | -27.7225 | 3.0952 | 9529.9 | -0.09 | 1.2521 | -1.8023 | -19.8868 | 0.64242 | 6.2717 | -30.5929 | -31.0153 | 81.12 | 70.7916 | 53.1785 | -21.7418 | -26.7084 | -9.2283 | 36.1426
42838.4285 | 712 | 22.8701 | 22.8396 | 22.8254 | 22.7424 | 22.347 | 21.6693 | 22.6834 | 21.718 | 22.3293 | 22.3297 | 22.2873 | 21.9426 | 21.1551 | 22.1262 | 21.5813 | 21.7616 | 21.9608 | 21.069 | 21.3076 | 22.7199 | 20.6108 | 33.5056 | 53.3688 | 22.0925 | 23.6232 | 72.1698 | 622.9387 | 663.3883 | 622.3255 | 19.4898 | 19.5856 | 114.7357 | 19.9973 | 77.7427 | 226.3782 | 98.7101 | 544.4328 | 22.341 | 721.0432 | 983.6639 | 881.562 | 413.9799 | 130.8631 | 78.5369 | 144.9007 | 229.8558 | 566.3953 | 687.5836 | 707.0806 | 735.7529 | 31.2838 | 52.467 | 36.335 | 115.8808 | 22.0739 | 46.8053 | 50.9523 | 50.0512 | 23.5926 |  |  | 0.26702 | -1.7257 | -196.4193 | -0.13475 | 8.7897 | -197.7921 | -203.2417 | -7.1235 | 6.3063 | 15.8847 | 225.4433 | 0.0057054 | 0.0062722 | 0.0003877 | 22.42 | 21.9758 | 22.1415 | 22.2014 | 21.9947 | 21.2706 | 20.0896 | 22.165 | 22.3503 | 22.3798 | 22.3227 | 21.9272 | 21.1535 | 22.2535 | 618.2509 | 378.0315 | 440.7043 | 295.1707 | 238.8222 | 343.0368 | 208.55 | 22.34 | 22.092 | 21.7239 | 22.0393 | 21.8253 | 22.5142 | 21.939 | 23.6165 | 61.4301 | 607.3816 | 552.6475 | 552.1252 | 545.8626 | 79.9564 | 51.9429 | 830.6808 | 21.9035 | 22.1859 | 215.5755 | 21.5463 | 22.0035 | 22.3439 | 26.0187 | 88.371 | 21.9457 | 23.0092 | 72.2409 | 856.9461 | 687.92 | 585.7952 | 609.0901 | 823.056 |  | 823.2495 | 896.5011 | 799.8429 | 641.3037 | 701.2163 | 842.8483 |  | 673.1345 |  |  | 380.1905 | 605.7826 | 763.1776 | [5 empty] | 21.8565 | 589.0296 | 21.6984 | 22.0668 | 343.3748 | 21.267 | 21.8728 | 490.8642 | 640.1707 | 661.5932 |  | 977.4683 | 829.1455 | 656.9538 | 801.3231 | 867.3019 | 593.9306 | 680.4717 | 977.6159 | 939.6028 | 733.5939 | 877.7477 | 306.2663 | 908.015 | 823.4184 | 498.6147 | 604.5795 | 628.8646 | 963.65 | 892.9731 | 782.0131 | 866.1882 | 924.724 | 557.2447 | 643.5123 | 949.7284 | 852.601 | 141.1413 | 3.7467 | 16.3263 | 3.5757 | -27.6819 | 3.0952 | 9596.96 | -0.04 | 1.0776 | -1.8718 | -19.9698 | -0.52306 | 6.4687 | -30.6857 | -31.1055 | 81.9383 | 72.4722 | 52.7703 | -22.4054 | -22.7422 | -7.6733 | 35.7938
42838.4285 | 713 | 22.8753 | 22.843 | 22.8341 | 22.7474 | 22.3535 | 21.6735 | 22.6752 | 21.7233 | 22.3278 | 22.3229 | 22.2973 | 21.9507 | 21.1604 | 22.1235 | 21.5855 | 21.7674 | 21.9613 | 21.0631 | 21.3087 | 22.7287 | 20.6191 | 34.016 | 54.0868 | 22.0984 | 23.6348 | 72.4211 | 621.4937 | 658.9197 | 619.9582 | 19.8876 | 19.8752 | 114.3963 | 19.4853 | 80.4091 | 227.0996 | 32.3981 | 539.6008 | 40.5805 | 713.3691 | 987.2074 | 891.9332 | 421.7163 | 44.9979 | 79.7027 | 147.1955 | 234.7005 | 572.9286 | 693.7461 | 708.5343 | 735.5047 | 31.4102 | 53.7224 | 36.0524 | 118.9759 | 22.1594 | 46.9121 | 51.0175 | 50.0418 | 23.6638 |  |  | 0.66655 | -1.4063 | -196.4311 | 0.23783 | 9.1787 | -197.842 | -203.4237 | -7.4567 | 6.4343 | 15.5048 | 204.7474 | 0.0057054 | 0.0063362 | 0.00043534 | 22.4227 | 21.9721 | 22.1464 | 22.1905 | 21.9893 | 21.2696 | 20.0841 | 22.1659 | 22.3452 | 22.3706 | 22.3165 | 21.9225 | 21.1458 | 22.2426 | 633.3376 | 418.6726 | 482.7271 | 316.2477 | 248.0673 | 356.236 | 215.6992 | 22.3355 | 22.0873 | 21.7257 | 22.0325 | 21.8269 | 22.5286 | 21.9368 | 23.6681 | 61.8204 | 606.1651 | 552.1119 | 551.8317 | 545.818 | 56.7659 | 46.8313 | 839.408 | 21.9066 | 22.1928 | 215.6629 | 21.547 | 22.0014 | 22.3514 | 26.1429 | 88.3753 | 21.9466 | 23.0207 | 73.0725 | 856.372 | 688.4786 | 587.4464 | 611.0466 | 825.2399 |  | 826.1561 | 909.8014 | 807.099 | 640.971 | 699.5378 | 851.8549 |  | 676.376 |  |  | 380.7044 | 607.3322 | 768.2936 | [5 empty] | 21.8641 | 589.0195 | 21.7145 | 22.078 | 343.2493 | 21.2826 | 21.8794 | 487.7255 | 638.2427 | 658.916 |  | 979.8693 | 828.167 | 650.2854 | 798.9827 | 867.4562 | 591.9377 | 678.5788 | 968.4832 | 939.7364 | 727.3105 | 875.98 | 313.1335 | 912.8552 | 829.4425 | 497.7295 | 602.9856 | 626.736 | 965.4409 | 892.3388 | 779.1813 | 870.2862 | 930.7218 | 555.6354 | 641.2843 | 961.1782 | 847.1453 | 126.7095 | 3.5937 | 16.3712 | 3.8167 | -27.7565 | 3.0952 | 9610.53 | -0.11 | 1.7003 | -1.6944 | -20.0251 | 0.6968 | 6.6152 | -30.7123 | -31.1425 | 82.8306 | 74.3581 | 52.3816 | -21.8919 | -26.4317 | -10.3202 | 35.5733
42838.4285 | 714 | 22.8753 | 22.838 | 22.8371 | 22.7463 | 22.3523 | 21.6747 | 22.6897 | 21.7193 | 22.3313 | 22.3407 | 22.2957 | 21.9449 | 21.1604 | 22.1351 | 21.5838 | 21.7653 | 21.9606 | 21.0582 | 21.3038 | 22.7365 | 20.6259 | 34.5395 | 54.8125 | 22.0996 | 23.6499 | 72.6834 | 617.8889 | 655.2316 | 616.1548 | 20.3889 | 19.9171 | 192.9552 | 19.2819 | 107.6341 | 171.5876 | 27.8617 | 552.7259 | 76.8362 | 749.0722 | 994.7516 | 891.0671 | 424.4383 | 21.3681 | 80.8922 | 149.5159 | 241.6633 | 582.8302 | 696.3767 | 709.7538 | 736.9835 | 31.5466 | 55.0068 | 35.9669 | 122.0064 | 22.2184 | 47.0369 | 51.0893 | 50.0351 | 23.733 |  |  | 0.66983 | -1.4043 | -196.3943 | 0.18198 | 8.6543 | -197.8171 | -203.3343 | -6.3698 | 5.6754 | 15.5937 | 189.5392 | 0.0053292 | 0.005983 | 0.00042548 | 22.4205 | 21.9673 | 22.1398 | 22.1876 | 21.9866 | 21.2601 | 20.0788 | 22.1636 | 22.3392 | 22.369 | 22.3187 | 21.9122 | 21.1413 | 22.2419 | 625.923 | 384.4489 | 465.9654 | 323.4933 | 252.4473 | 367.1686 | 221.7994 | 22.3427 | 22.0946 | 21.7237 | 22.0362 | 21.83 | 22.5517 | 21.944 | 23.738 | 62.2072 | 604.7389 | 551.4846 | 551.1025 | 544.2872 | 56.3298 | 29.9603 | 849.6403 | 21.8936 | 22.1836 | 217.8675 | 21.5386 | 21.9951 | 22.35 | 26.201 | 88.365 | 21.9432 | 23.0148 | 73.8682 | 853.3439 | 689.2047 | 590.6176 | 615.0569 | 827.5935 |  | 829.1227 | 930.5023 | 815.6192 | 645.3717 | 698.3015 | 860.0731 |  | 680.0485 |  |  | 381.0805 | 606.2738 | 771.0357 | [5 empty] | 21.8631 | 590.9208 | 21.7023 | 22.0707 | 341.3318 | 21.2797 | 21.8783 | 484.1399 | 636.7496 | 656.5862 |  | 975.7361 | 828.4135 | 643.739 | 792.7045 | 868.1391 | 590.1345 | 677.3689 | 951.4002 | 938.4582 | 720.0873 | 871.422 | 320.009 | 919.2613 | 835.4647 | 496.4064 | 600.7778 | 623.8966 | 968.1261 | 889.9 | 776.7814 | 876.0307 | 944.2733 | 554.0876 | 638.2506 | 966.4654 | 843.5314 | 108.445 | 3.3374 | 16.3963 | 4.0316 | -27.7485 | 3.0952 | 9614.26 | -0.04 | 1.7009 | -1.6978 | -20.0784 | 0.61119 | 6.4275 | -30.7294 | -31.155 | 83.7451 | 76.4846 | 51.9675 | -19.2188 | -23.7268 | -10.5505 | 35.3568
42838.4286 | 715 | 22.8817 | 22.847 | 22.8411 | 22.7464 | 22.3528 | 21.672 | 22.6869 | 21.7268 | 22.3382 | 22.335 | 22.3043 | 21.9494 | 21.1586 | 22.1323 | 21.5872 | 21.7611 | 21.9638 | 21.0602 | 21.3037 | 22.7448 | 20.6387 | 35.0867 | 55.5335 | 22.0902 | 23.664 | 72.9988 | 614.8875 | 653.1773 | 612.8922 | 20.2178 | 19.4098 | 134.6286 | 19.6448 | 53.3096 | 212.5626 | 45.1055 | 538.7554 | 90.8314 | 695.9806 | 993.7617 | 883.1408 | 442.6089 | 40.674 | 82.1083 | 152.1136 | 246.3183 | 588.9116 | 700.7021 | 713.3142 | 740.5216 | 31.5169 | 56.3544 | 36.5856 | 125.2759 | 22.2774 | 47.1514 | 51.1396 | 50.0484 | 23.8061 |  |  | 0.52527 | -0.69792 | -196.4495 | -0.07627 | 8.034 | -197.7836 | -203.4986 | -7.1991 | 5.8511 | 16.4417 | 191.054 | 0.0053555 | 0.0060093 | 0.00041234 | 22.43 | 21.9826 | 22.1429 | 22.195 | 21.9916 | 21.2728 | 20.088 | 22.173 | 22.3472 | 22.3767 | 22.3236 | 21.9232 | 21.155 | 22.2509 | 604.2501 | 356.1281 | 424.2749 | 306.6609 | 237.8242 | 377.2581 | 226.7762 | 22.3455 | 22.102 | 21.7275 | 22.0476 | 21.839 | 22.5589 | 21.9571 | 23.806 | 62.6417 | 603.3231 | 551.5508 | 551.6929 | 545.133 | 72.2114 | 33.9214 | 862.0226 | 21.8941 | 22.1812 | 221.9197 | 21.5394 | 21.9941 | 22.3577 | 26.2883 | 88.3699 | 21.9447 | 23.0243 | 74.6374 | 854.2614 | 689.0282 | 596.0824 | 620.44 | 815.5075 |  | 830.1227 | 939.9521 | 822.6059 | 647.5655 | 697.3266 | 867.8383 |  | 682.9286 |  |  | 381.7765 | 606.3619 | 766.1521 | [5 empty] | 21.8642 | 592.9276 | 21.7003 | 22.0705 | 338.8478 | 21.2838 | 21.8793 | 481.034 | 635.2596 | 654.1024 |  | 959.0903 | 827.9651 | 637.2699 | 784.6611 | 865.3854 | 588.0668 | 674.9681 | 935.1506 | 934.2743 | 712.6896 | 863.6706 | 333.7194 | 925.4864 | 843.3332 | 495.1268 | 598.3421 | 620.7003 | 970.5898 | 888.68 | 774.9395 | 882.0361 | 958.9774 | 552.631 | 635.6261 | 964.1437 | 842.925 | 134.5465 | 3.008 | 16.4177 | 4.2133 | -27.8064 | 3.0952 | 9561.91 | -0.06 | 1.5034 | -1.2006 | -20.1429 | -0.39689 | 6.204 | -30.7824 | -31.224 | 84.4128 | 78.4811 | 51.6771 | -15.0746 | -18.4026 | -10.4601 | 35.0773
42838.4286 | 716 | 22.8791 | 22.84 | 22.8378 | 22.7502 | 22.3508 | 21.6765 | 22.6893 | 21.7266 | 22.3303 | 22.3287 | 22.2995 | 21.9468 | 21.1632 | 22.1333 | 21.5835 | 21.762 | 21.9672 | 21.0567 | 21.3089 | 22.7513 | 20.6501 | 35.6419 | 56.2352 | 22.0914 | 23.6876 | 73.2639 | 611.4783 | 652.3401 | 609.2122 | 19.5446 | 19.6001 | 166.1468 | 20.0003 | 70.8055 | 212.3792 | 78.6571 | 521.9736 | 20.5996 | 688.4087 | 975.9328 | 863.6256 | 426.683 | 89.9181 | 83.5873 | 154.9565 | 252.399 | 592.7329 | 702.5928 | 718.2142 | 744.6975 | 31.6392 | 57.5009 | 36.4226 | 128.1488 | 22.3481 | 47.2852 | 51.2036 | 50.0866 | 23.8823 |  |  | 0.29593 | -0.92989 | -196.4442 | -0.14329 | 7.3598 | -197.8263 | -203.337 | -6.2515 | 5.3389 | 15.1659 | 188.5967 | 0.0053161 | 0.0059995 | 0.00037784 | 22.43 | 21.9778 | 22.1427 | 22.1962 | 21.9945 | 21.2782 | 20.084 | 22.1668 | 22.347 | 22.3763 | 22.3238 | 21.9245 | 21.1487 | 22.2539 | 607.7067 | 365.9422 | 422.9116 | 299.1851 | 230.1945 | 387.9124 | 231.7879 | 22.3366 | 22.089 | 21.7255 | 22.0427 | 21.8399 | 22.5676 | 21.9477 | 23.8632 | 63.017 | 601.9213 | 550.4916 | 550.568 | 542.1669 | 73.9674 | 38.1239 | 870.1635 | 21.8964 | 22.1885 | 223.9163 | 21.5457 | 22.0007 | 22.3645 | 26.3925 | 88.3764 | 21.9484 | 23.0356 | 75.364 | 864.6402 | 687.0345 | 599.379 | 623.2673 | 815.9333 |  | 830.9723 | 941.2206 | 829.1971 | 646.3581 | 696.2637 | 872.4084 |  | 685.9706 |  |  | 380.5234 | 607.7152 | 761.2888 | [5 empty] | 21.8619 | 593.9359 | 21.7028 | 22.0641 | 337.4317 | 21.2798 | 21.8798 | 477.801 | 632.668 | 650.9912 |  | 944.7878 | 827.3905 | 631.1511 | 777.3471 | 859.3877 | 585.9381 | 671.514 | 928.2686 | 932.2862 | 706.1254 | 856.8171 | 345.3288 | 927.2987 | 850.1465 | 493.9689 | 596.5172 | 617.5205 | 973.2054 | 887.6625 | 772.4014 | 886.0983 | 969.962 | 551.1815 | 632.8228 | 962.9185 | 843.3211 | 121.3775 | 2.7173 | 16.4388 | 4.3724 | -27.7406 | 3.0953 | 9452.08 | -0.1 | 1.1261 | -1.3905 | -20.2098 | -0.54583 | 5.9527 | -30.8621 | -31.289 | 84.6836 | 80.6135 | 51.4611 | -13.5935 | -17.5501 | -8.7988 | 34.9072
42838.4286 | 717 | 22.883 | 22.8466 | 22.8365 | 22.7485 | 22.3577 | 21.6819 | 22.6892 | 21.7316 | 22.3301 | 22.3299 | 22.2955 | 21.9473 | 21.1622 | 22.1345 | 21.5826 | 21.7667 | 21.9648 | 21.0573 | 21.3126 | 22.7632 | 20.6696 | 36.2224 | 56.9205 | 22.1091 | 23.7017 | 73.5633 | 610.2891 | 650.7345 | 608.1408 | 19.8655 | 19.9186 | 204.0362 | 19.9276 | 93.5842 | 227.7784 | 64.1115 | 505.6247 | 30.3651 | 691.1819 | 1002.6514 | 878.4361 | 427.6966 | 74.7737 | 85.0486 | 157.6813 | 257.6056 | 595.4029 | 705.2374 | 725.6465 | 749.5171 | 31.1372 | 58.7617 | 36.9327 | 131.3314 | 22.4399 | 47.3989 | 51.268 | 50.1423 | 23.9556 |  |  | 0.075142 | -0.90031 | -196.5474 | -0.23989 | 8.6208 | -197.8223 | -203.1536 | -7.3305 | 5.6089 | 16.9566 | 176.6846 | 0.0050499 | 0.0058565 | 0.00040906 | 22.4352 | 21.9779 | 22.1418 | 22.1981 | 21.9978 | 21.2763 | 20.0814 | 22.171 | 22.3551 | 22.3747 | 22.3245 | 21.9227 | 21.1453 | 22.2466 | 614.8473 | 355.9618 | 386.7162 | 290.1098 | 222.1333 | 398.165 | 236.1484 | 22.3412 | 22.0854 | 21.7369 | 22.0445 | 21.8412 | 22.5792 | 21.9491 | 23.9323 | 63.3721 | 600.4033 | 548.6671 | 548.2513 | 537.5232 | 55.3376 | 24.2308 | 875.2773 | 21.8983 | 22.181 | 224.5122 | 21.5473 | 22.0019 | 22.3662 | 26.5055 | 88.3582 | 21.9427 | 23.0643 | 75.9798 | 865.5052 | 685.9701 | 602.5058 | 626.2122 | 850.7151 |  | 833.6044 | 952.2569 | 837.5602 | 648.3299 | 695.1643 | 878.6827 |  | 689.4466 |  |  | 382.3324 | 610.042 | 773.2962 | [5 empty] | 21.858 | 595.6295 | 21.697 | 22.0668 | 337.5584 | 21.2775 | 21.8796 | 475.1021 | 630.0775 | 647.3424 |  | 941.3679 | 826.4279 | 624.8793 | 772.332 | 854.9256 | 584.4822 | 667.776 | 930.9787 | 931.1731 | 700.0384 | 851.0386 | 354.9013 | 930.5776 | 857.5361 | 492.8837 | 595.1382 | 614.2772 | 974.5014 | 884.0184 | 769.7044 | 888.4222 | 976.4346 | 550.1265 | 629.7445 | 958.6107 | 839.4956 | 121.6747 | 2.4904 | 16.4613 | 4.5346 | -27.7498 | 3.0953 | 9346.43 | -0.02 | 0.56711 | -1.3725 | -20.2794 | -0.70848 | 6.4667 | -30.9773 | -31.3919 | 84.597 | 83.1091 | 51.149 | -12.5602 | -12.915 | -9.366 | 34.7639
42838.4286 | 718 | 22.8801 | 22.8453 | 22.8352 | 22.7488 | 22.3507 | 21.6699 | 22.6831 | 21.7251 | 22.3242 | 22.3346 | 22.2928 | 21.9414 | 21.1576 | 22.1277 | 21.5924 | 21.7768 | 21.9645 | 21.0617 | 21.3238 | 22.7747 | 20.6921 | 36.8207 | 57.6185 | 22.1189 | 23.7261 | 73.799 | 608.5565 | 646.0905 | 606.0876 | 20.2393 | 19.7644 | 204.6197 | 19.3521 | 107.1322 | 231.0777 | 24.9879 | 504.6512 | 52.9262 | 684.7613 | 990.0005 | 878.7502 | 424.2736 | 19.6118 | 86.5175 | 160.5948 | 264.4877 | 601.8168 | 708.5027 | 730.1364 | 754.0467 | 30.794 | 59.8853 | 37.4468 | 134.2676 | 22.5298 | 47.4987 | 51.3122 | 50.2167 | 24.0181 |  |  | 0.051486 | -0.97457 | -196.4869 | -0.12753 | 8.3915 | -197.8131 | -203.2712 | -6.3198 | 5.5402 | 16.7493 | 182.1188 | 0.0051074 | 0.0059108 | 0.00038606 | 22.4363 | 21.975 | 22.1392 | 22.1879 | 21.9953 | 21.2703 | 20.0832 | 22.1615 | 22.3386 | 22.3734 | 22.3155 | 21.9241 | 21.1449 | 22.2425 | 600.3793 | 328.8363 | 360.5625 | 278.4978 | 218.1527 | 406.1402 | 239.4023 | 22.3414 | 22.0873 | 21.739 | 22.037 | 21.8391 | 22.5929 | 21.9482 | 23.9988 | 63.7246 | 598.7664 | 546.4891 | 545.5285 | 533.3084 | 46.999 | 19.898 | 875.634 | 21.8914 | 22.1782 | 225.8038 | 21.5352 | 21.9918 | 22.3608 | 26.6082 | 88.3713 | 21.9328 | 23.0594 | 76.6249 | 867.0995 | 685.2539 | 607.0872 | 630.2651 | 838.6805 |  | 834.6962 | 942.6698 | 843.6029 | 651.8007 | 694.4311 | 882.1577 |  | 691.9867 |  |  | 381.0689 | 609.8531 | 771.4995 | [5 empty] | 21.8639 | 597.0944 | 21.7035 | 22.0706 | 338.1762 | 21.2779 | 21.8728 | 472.9959 | 627.6547 | 643.4367 |  | 944.0774 | 825.2396 | 618.3394 | 768.3356 | 850.2855 | 582.2929 | 665.8604 | 934.0738 | 930.249 | 693.7892 | 844.2715 | 361.9966 | 936.813 | 865.1709 | 491.7474 | 593.7884 | 611.6729 | 969.8839 | 879.1925 | 766.107 | 893.0934 | 982.831 | 548.9897 | 627.2728 | 951.1066 | 833.5559 | 112.7364 | 2.3245 | 16.485 | 4.677 | -27.6921 | 3.0953 | 9215.49 | -0.09 | 0.46888 | -1.4328 | -20.3447 | -0.5183 | 6.3944 | -31.0461 | -31.4715 | 85.2978 | 85.4365 | 50.8815 | -9.5094 | -9.549 | -10.6433 | 34.5887
42838.4286 | 719 | 22.8734 | 22.8431 | 22.8264 | 22.7471 | 22.3519 | 21.6656 | 22.6782 | 21.7213 | 22.3174 | 22.3228 | 22.2883 | 21.929 | 21.1576 | 22.1306 | 21.5858 | 21.7645 | 21.9632 | 21.0607 | 21.3172 | 22.7807 | 20.6982 | 37.4258 | 58.3045 | 22.1067 | 23.7435 | 73.9895 | 603.4296 | 641.1773 | 600.2578 | 20.2307 | 19.4119 | 187.53 | 19.415 | 135.1477 | 242.9539 | 36.1682 | 513.1965 | 119.9449 | 696.3666 | 1003.5567 | 888.2852 | 419.1493 | 29.8318 | 88.5272 | 164.6973 | 267.7877 | 609.7569 | 713.9047 | 735.1659 | 760.5622 | 30.5234 | 61.0202 | 37.6459 | 137.2545 | 22.6054 | 47.6157 | 51.3409 | 50.2871 | 24.0799 |  |  | 0.4221 | -0.87469 | -196.4804 | -0.12489 | 8.5387 | -197.8447 | -203.1977 | -7.0197 | 6.2108 | 17.5849 | 174.1261 | 0.0051025 | 0.005827 | 0.0003762 | 22.4317 | 21.979 | 22.1377 | 22.184 | 21.9929 | 21.2635 | 20.0766 | 22.1633 | 22.3385 | 22.3682 | 22.3117 | 21.9206 | 21.1488 | 22.2386 | 566.0016 | 295.8463 | 339.8914 | 269.333 | 214.7229 | 412.8206 | 242.3042 | 22.3415 | 22.0975 | 21.7437 | 22.0438 | 21.8429 | 22.6036 | 21.9575 | 24.0715 | 64.0721 | 597.2303 | 546.3085 | 545.4806 | 535.8968 | 55.2916 | 35.2631 | 872.4214 | 21.8952 | 22.186 | 226.4935 | 21.5352 | 21.996 | 22.3699 | 26.653 | 88.3611 | 21.9359 | 23.0686 | 77.3233 | 867.3284 | 685.2463 | 611.9236 | 634.3741 | 844.0299 |  | 835.7657 | 940.6972 | 848.8193 | 651.0172 | 693.6649 | 887.3216 |  | 694.5438 |  |  | 382.463 | 608.5623 | 772.9653 | [5 empty] | 21.8525 | 598.913 | 21.6975 | 22.0672 | 339.8978 | 21.2714 | 21.8771 | 470.2973 | 625.4698 | 641.8938 |  | 942.9749 | 824.5644 | 612.1344 | 762.7778 | 843.783 | 579.8457 | 666.5063 | 928.554 | 927.9033 | 687.0798 | 836.0292 | 373.1738 | 945.1988 | 868.1797 | 490.8531 | 592.4987 | 608.3339 | 970.3628 | 873.105 | 762.8846 | 898.7933 | 987.8161 | 547.2937 | 625.0676 | 949.8126 | 829.8933 | 100.5082 | 2.1544 | 16.511 | 4.8218 | -27.7426 | 3.0952 | 9143.69 | -0.05 | 1.3381 | -1.3638 | -20.4403 | -0.51535 | 6.4664 | -31.1263 | -31.5446 | 85.5092 | 87.2955 | 50.7247 | -4.4654 | -6.8404 | -10.1193 | 34.2438
42838.4286 | 720 | 22.8841 | 22.8472 | 22.8286 | 22.7416 | 22.3529 | 21.6695 | 22.6807 | 21.7186 | 22.3278 | 22.3312 | 22.2889 | 21.9461 | 21.1533 | 22.1302 | 21.5853 | 21.7603 | 21.9759 | 21.0603 | 21.3198 | 22.7953 | 20.7181 | 38.0738 | 58.9933 | 22.0982 | 23.738 | 74.2488 | 600.1638 | 637.088 | 597.5272 | 19.6243 | 19.5346 | 131.1493 | 19.8211 | 83.5842 | 249.0693 | 63.1006 | 532.5115 | 36.4465 | 712.7751 | 1016.1423 | 896.9817 | 432.2646 | 75.9906 | 91.0328 | 169.6573 | 271.7813 | 622.0058 | 720.8106 | 739.1765 | 766.6913 | 30.7068 | 62.3181 | 38.0015 | 140.5934 | 22.6762 | 47.7088 | 51.3345 | 50.3784 | 24.1491 |  |  | 0.33865 | -1.3163 | -193.8394 | 0.34626 | 8.9862 | -197.8236 | -203.2233 | -6.6057 | 6.8594 | 19.2027 | 164.542 | 0.0051206 | 0.0057646 | 0.00037949 | 22.4462 | 21.9861 | 22.1425 | 22.1906 | 22.0008 | 21.2659 | 20.0802 | 22.1709 | 22.3463 | 22.373 | 22.3208 | 21.9268 | 21.1468 | 22.2465 | 539.5461 | 296.9627 | 351.8078 | 275.8223 | 222.5482 | 419.4635 | 245.8063 | 22.3335 | 22.0837 | 21.7333 | 22.0336 | 21.8433 | 22.6091 | 21.9471 | 24.1467 | 64.4399 | 595.9786 | 547.2843 | 546.7906 | 538.3791 | 63.8575 | 26.3075 | 869.0452 | 21.8961 | 22.1877 | 226.6199 | 21.5401 | 21.9918 | 22.3763 | 26.7792 | 88.3565 | 21.9456 | 23.1005 | 77.9139 | 853.3262 | 683.2543 | 618.9502 | 640.7468 | 823.5764 |  | 835.6625 | 926.9634 | 854.0691 | 643.3739 | 692.4537 | 890.3976 |  | 697.6252 |  |  | 384.7234 | 610.6193 | 764.46 | [5 empty] | 21.8694 | 596.1569 | 21.7141 | 22.0751 | 337.7449 | 21.2844 | 21.8834 | 466.927 | 623.4719 | 639.9811 |  | 935.6581 | 824.5288 | 605.8788 | 756.2661 | 837.6997 | 577.4308 | 663.6361 | 938.2233 | 929.5225 | 680.6005 | 828.4913 | 379.2167 | 950.2476 | 868.5543 | 489.8049 | 591.4822 | 604.3927 | 975.1297 | 874.9647 | 761.0486 | 899.3799 | 995.8524 | 545.6162 | 622.0385 | 965.8909 | 830.0676 | 94.2146 | 2.042 | 16.5449 | 4.9798 | -27.8486 | 3.0953 | 9175.17 | -0.06 | 1.1967 | -1.6825 | -20.4172 | 0.86293 | 6.6468 | -31.1865 | -31.6092 | 86.0426 | 89.5163 | 50.6556 | -0.29443 | -7.6654 | -9.5297 | 33.9533
42838.4286 | 721 | 22.8779 | 22.8442 | 22.8312 | 22.7351 | 22.3508 | 21.6671 | 22.6834 | 21.7122 | 22.3197 | 22.3219 | 22.2969 | 21.934 | 21.1569 | 22.1259 | 21.5768 | 21.7669 | 21.965 | 21.0568 | 21.3131 | 22.8019 | 20.7323 | 38.7048 | 59.6536 | 22.1047 | 23.7671 | 74.5129 | 597.2079 | 633.1796 | 594.169 | 19.5988 | 19.7423 | 218.3072 | 20.2368 | 77.3137 | 206.33 | 97.6629 | 517.4633 | 23.7069 | 673.4025 | 1005.2259 | 893.596 | 442.1022 | 129.611 | 93.4066 | 174.3634 | 274.2962 | 626.5564 | 722.7591 | 743.324 | 770.0379 | 31.2224 | 63.5158 | 38.2701 | 143.6039 | 22.7331 | 47.7903 | 51.2749 | 50.4304 | 24.212 |  |  | 0.19868 | -1.5397 | -187.1388 | -0.060498 | 8.77 | -197.8223 | -203.2791 | -7.247 | 6.8856 | 19.6139 | 159.985 | 0.0052783 | 0.0057432 | 0.00041891 | 22.4479 | 21.9793 | 22.1398 | 22.1929 | 21.9987 | 21.2669 | 20.076 | 22.1646 | 22.3436 | 22.3715 | 22.3219 | 21.921 | 21.1398 | 22.2426 | 538.9292 | 305.4595 | 348.1995 | 261.6465 | 216.4606 | 426.6203 | 248.9023 | 22.3376 | 22.0937 | 21.7368 | 22.0408 | 21.8465 | 22.6266 | 21.9506 | 24.2226 | 64.772 | 594.8007 | 546.9303 | 545.9452 | 535.6958 | 52.9857 | 27.2888 | 856.6437 | 21.9023 | 22.1852 | 227.9624 | 21.5422 | 21.995 | 22.3867 | 26.9366 | 88.3522 | 21.9456 | 23.1047 | 78.5362 | 836.325 | 679.8583 | 627.1778 | 648.0545 | 798.0285 |  | 834.3374 | 901.6562 | 856.9837 | 641.3694 | 691.0839 | 879.8304 |  | 700.7791 |  |  | 385.0771 | 612.8637 | 751.0606 | [5 empty] | 21.8519 | 593.9008 | 21.6996 | 22.0537 | 335.536 | 21.2761 | 21.8749 | 464.2607 | 621.5841 | 636.235 |  | 935.6591 | 828.5803 | 599.9977 | 748.9223 | 831.0009 | 576.1284 | 660.1648 | 936.3442 | 928.6508 | 674.2698 | 820.5037 | 391.1858 | 955.2082 | 875.2551 | 488.5326 | 589.1661 | 601.6608 | 984.1943 | 882.0522 | 759.6174 | 900.7075 | 1000.8913 | 543.8999 | 618.6 | 975.8066 | 831.9696 | 108.1538 | 1.94 | 16.6277 | 5.1412 | -27.7443 | 3.0953 | 9262.81 | -0.04 | 0.91481 | -1.8293 | -20.1675 | -0.36261 | 6.5798 | -31.2502 | -31.6783 | 86.3065 | 91.2507 | 50.3941 | 1.117 | -6.8215 | -8.4957 | 33.8201
42838.4286 | 722 | 22.8747 | 22.8452 | 22.8251 | 22.7395 | 22.3496 | 21.6686 | 22.6826 | 21.7265 | 22.3265 | 22.3285 | 22.2991 | 21.9437 | 21.1587 | 22.1361 | 21.5854 | 21.7766 | 21.9664 | 21.062 | 21.3188 | 22.8109 | 20.7488 | 39.3528 | 60.2824 | 22.1145 | 23.7867 | 74.812 | 593.9094 | 629.9549 | 591.0804 | 19.948 | 19.884 | 203.6618 | 19.4301 | 110.9743 | 225.9195 | 24.3637 | 512.2019 | 45.5183 | 675.0982 | 1031.2679 | 901.6024 | 449.071 | 21.1912 | 96.5462 | 180.625 | 279.752 | 637.4244 | 730.167 | 748.4567 | 774.1545 | 31.4734 | 64.9217 | 38.2494 | 147.1356 | 22.8122 | 47.8923 | 51.1915 | 50.4907 | 24.2805 |  |  | 0.33207 | -1.1671 | -196.483 | -0.14067 | 8.1379 | -197.8177 | -203.2371 | -6.448 | 6.626 | 19.3873 | 135.6512 | 0.005183 | 0.0056085 | 0.00040577 | 22.4486 | 21.9738 | 22.1387 | 22.1887 | 21.9882 | 21.2628 | 20.0735 | 22.1581 | 22.3383 | 22.3624 | 22.3166 | 21.9177 | 21.1375 | 22.2423 | 540.3232 | 308.1188 | 336.3622 | 246.6008 | 208.425 | 433.0759 | 251.5628 | 22.3372 | 22.0881 | 21.7339 | 22.0407 | 21.8394 | 22.6375 | 21.9501 | 24.2965 | 65.0782 | 593.5019 | 545.5149 | 544.2573 | 533.0519 | 49.8356 | 27.262 | 846.8711 | 21.9 | 22.1809 | 229.9662 | 21.5444 | 21.9996 | 22.3933 | 27.0079 | 88.3582 | 21.9506 | 23.122 | 79.148 | 831.6885 | 675.2525 | 632.9487 | 653.2063 | 787.8457 |  | 832.903 | 893.3123 | 859.2149 | 643.6939 | 690.0705 | 871.0817 |  | 703.8852 |  |  | 385.2404 | 616.2809 | 738.326 | [5 empty] | 21.8634 | 593.6144 | 21.7104 | 22.0809 | 336.3328 | 21.2883 | 21.8857 | 461.5439 | 619.944 | 633.0065 |  | 929.8093 | 832.4354 | 594.6157 | 742.8387 | 823.8187 | 573.7857 | 656.7644 | 941.0646 | 926.1982 | 667.5392 | 812.9181 | 401.0173 | 961.7676 | 884.5439 | 487.0574 | 586.197 | 598.703 | 992.4381 | 886.038 | 758.7129 | 899.9287 | 1007.0932 | 541.2501 | 614.7277 | 982.9918 | 834.6503 | 91.6665 | 1.8468 | 16.6954 | 5.3003 | -27.7715 | 3.0953 | 9360.87 | -0.15 | 1.1806 | -1.6038 | -20.8089 | -0.55678 | 6.3542 | -31.3286 | -31.7549 | 86.1084 | 92.277 | 50.0957 | 2.1881 | -5.1241 | -11.3532 | 33.6653
42838.4286 | 723 | 22.8751 | 22.8471 | 22.8288 | 22.7434 | 22.3457 | 21.6663 | 22.6759 | 21.7257 | 22.3274 | 22.3305 | 22.2959 | 21.9419 | 21.1585 | 22.1232 | 21.5882 | 21.7818 | 21.9708 | 21.0671 | 21.3217 | 22.83 | 20.7681 | 40.015 | 60.9155 | 22.1178 | 23.8155 | 75.1135 | 592.478 | 627.6605 | 589.6222 | 20.4645 | 20.0626 | 226.1792 | 19.6672 | 146.4968 | 237.4219 | 33.312 | 502.5043 | 109.8915 | 666.0486 | 1012.5307 | 893.3827 | 437.4835 | 30.9579 | 99.2024 | 185.69 | 291.2928 | 645.6273 | 734.7855 | 752.6608 | 777.2501 | 31.785 | 66.1884 | 38.5927 | 150.3784 | 22.9022 | 47.9963 | 51.0954 | 50.5386 | 24.3831 |  |  | 0.37413 | -1.4694 | -196.4666 | -0.097298 | 9.5447 | -197.7744 | -203.1628 | -5.7094 | 7.2011 | 20.1778 | 139.2245 | 0.0047493 | 0.0055625 | 0.00037784 | 22.4623 | 21.9755 | 22.1456 | 22.1893 | 21.984 | 21.2707 | 20.0785 | 22.1701 | 22.3385 | 22.3776 | 22.3139 | 21.9289 | 21.1465 | 22.2428 | 531.5645 | 305.1403 | 344.5831 | 232.626 | 202.8248 | 439.1801 | 254.0294 | 22.3323 | 22.0847 | 21.736 | 22.043 | 21.8377 | 22.6449 | 21.9515 | 24.372 | 65.3779 | 592.1411 | 543.3007 | 541.7769 | 530.3735 | 61.0384 | 35.9726 | 837.39 | 21.9053 | 22.1861 | 233.1841 | 21.5368 | 21.9967 | 22.4031 | 27.1221 | 88.3678 | 21.9499 | 23.138 | 79.7649 | 821.6133 | 671.069 | 637.09 | 656.3748 | 782.511 |  | 831.4145 | 872.8428 | 860.1202 | 641.8343 | 688.8546 | 858.8369 |  | 707.4459 |  |  | 388.2557 | 623.618 | 736.1656 | [5 empty] | 21.8609 | 591.618 | 21.7069 | 22.0715 | 343.2902 | 21.2826 | 21.8885 | 458.7155 | 617.3796 | 629.0615 |  | 932.3623 | 840.6648 | 589.9546 | 735.9657 | 818.0114 | 570.2348 | 652.8817 | 949.8343 | 930.3519 | 661.8412 | 806.0249 | 411.5095 | 967.0176 | 895.4927 | 485.7211 | 582.9238 | 596.0611 | 1002.0636 | 893.0242 | 758.5826 | 896.3786 | 1011.3707 | 539.0024 | 611.1745 | 990.4006 | 837.3916 | 85.2957 | 1.7611 | 16.7718 | 5.4532 | -27.8795 | 3.0953 | 9438.88 | -0.05 | 1.2521 | -1.8095 | -20.9239 | -0.46564 | 6.8958 | -31.3896 | -31.8143 | 85.7594 | 93.1693 | 49.8676 | 4.3336 | -5.6821 | -10.7268 | 33.5015
42838.4287 | 724 | 22.8719 | 22.8408 | 22.8264 | 22.7378 | 22.344 | 21.6695 | 22.6741 | 21.7224 | 22.3168 | 22.3296 | 22.2897 | 21.9344 | 21.1567 | 22.1193 | 21.576 | 21.77 | 21.9672 | 21.0591 | 21.3288 | 22.826 | 20.7797 | 40.6894 | 61.5272 | 22.11 | 23.8465 | 75.3549 | 589.7304 | 624.7297 | 586.4196 | 20.2662 | 19.7785 | 230.1749 | 20.2021 | 162.6361 | 247.1616 | 58.9736 | 507.7815 | 102.7862 | 762.5666 | 947.9508 | 821.7827 | 559.0986 | 1070.8139 | 102.1467 | 191.0463 | 300.5177 | 649.647 | 738.5964 | 758.1785 | 781.0309 | 32.2412 | 67.526 | 39.0596 | 153.7427 | 22.9873 | 48.0909 | 50.9795 | 50.5608 | 24.4481 |  |  | 0.20722 | -1.6521 | -193.4438 | 0.004554 | 8.9625 | -197.8072 | -203.199 | -5.9052 | 7.5235 | 20.8779 | 124.0174 | 0.0066517 | 0.0060422 | 0.00038606 | 22.4561 | 21.9761 | 22.1459 | 22.1974 | 21.992 | 21.2678 | 20.0746 | 22.175 | 22.3401 | 22.3733 | 22.316 | 21.9286 | 21.1446 | 22.2419 | 514.0304 | 297.239 | 361.7117 | 239.5235 | 211.0067 | 444.9651 | 257.2485 | 22.327 | 22.0851 | 21.7427 | 22.0358 | 21.8402 | 22.6593 | 21.9468 | 24.4463 | 65.6858 | 590.5479 | 540.0451 | 538.2687 | 525.0742 | 52.0807 | 28.5859 | 823.655 | 21.8955 | 22.1797 | 234.7202 | 21.5312 | 21.9903 | 22.3973 | 27.2487 | 88.3784 | 21.9439 | 23.1378 | 80.3253 | 808.3949 | 667.0457 | 638.4224 | 656.331 | 768.2208 |  | 828.9869 | 849.9551 | 859.9401 | 637.95 | 687.4617 | 847.8102 |  | 711.8128 |  |  | 391.8929 | 626.521 | 727.3942 | [5 empty] | 21.8639 | 590.2104 | 21.7047 | 22.0731 | 347.9311 | 21.2756 | 21.8824 | 455.9794 | 614.474 | 624.7255 |  | 947.8341 | 853.9647 | 585.9081 | 729.1019 | 813.3677 | 566.7767 | 648.8508 | 954.6283 | 944.2347 | 657.3553 | 798.8979 | 425.2151 | 966.7272 | 901.8059 | 484.4113 | 579.0257 | 593.7534 | 1007.7221 | 894.733 | 758.1631 | 893.1376 | 1013.5115 | 536.0992 | 607.3263 | 994.2579 | 837.8954 | 80.4171 | 1.6885 | 16.8251 | 5.5943 | -27.8904 | 3.0952 | 9463.74 | -0.1 | 0.93009 | -1.9299 | -20.8831 | 0.10132 | 6.7001 | -31.4765 | -31.9026 | 85.3493 | 93.7406 | 49.6561 | 7.4046 | -7.1196 | -13.2025 | 33.371
42838.4287 | 725 | 22.8679 | 22.8349 | 22.8233 | 22.7328 | 22.3417 | 21.6616 | 22.6671 | 21.718 | 22.317 | 22.3205 | 22.2827 | 21.9293 | 21.1429 | 22.1157 | 21.5704 | 21.7604 | 21.9683 | 21.0572 | 21.3236 | 22.8383 | 20.7976 | 41.3649 | 62.107 | 22.1066 | 23.8463 | 75.5965 | 585.0096 | 622.6797 | 581.5911 | 21.2147 | 21.9366 | 145.7908 | 21.5026 | 88.9411 | 154.5113 | 454.5079 | 708.0927 | 1337.1023 | 877.1815 | 878.4526 | 742.4695 | 739.6613 |  | 105.7381 | 197.6591 | 310.3405 | 654.396 | 742.559 | 762.6644 | 785.8997 | 32.8906 | 69.0503 | 39.2911 | 157.5873 | 23.0578 | 48.1635 | 50.8526 | 50.5735 | 24.5076 |  |  | 0.012058 | -2.6719 | -190.724 | -0.30232 | 8.9875 | -197.842 | -203.199 | -7.0387 | 7.946 | 21.4736 | 63.9306 | 0.0070591 | 0.0061818 | 0.0003532 | 22.4633 | 21.9716 | 22.138 | 22.181 | 21.9848 | 21.2595 | 20.081 | 22.1664 | 22.3347 | 22.3621 | 22.3091 | 21.9228 | 21.1427 | 22.2379 | 495.2533 | 283.0384 | 351.8424 | 249.4581 | 219.2638 | 450.0403 | 260.2816 | 22.3267 | 22.0831 | 21.7333 | 22.0398 | 21.8393 | 22.6756 | 21.9594 | 24.5282 | 65.9997 | 588.7964 | 537.0382 | 534.9123 | 521.0984 | 54.6017 | 26.3106 | 809.2701 | 21.9028 | 22.1811 | 236.3859 | 21.5313 | 21.9932 | 22.4092 | 27.3808 | 88.3931 | 21.9523 | 23.1643 | 80.8334 | 796.0851 | 662.7844 | 639.6694 | 656.1933 | 757.6106 |  | 826.4107 | 838.1198 | 859.3656 | 634.5791 | 686.1138 | 841.7986 |  | 717.0233 |  |  | 392.2535 | 626.7404 | 719.467 | [5 empty] | 21.8588 | 587.6292 | 21.7081 | 22.0719 | 348.2692 | 21.2806 | 21.8841 | 453.7707 | 611.724 | 620.6908 |  | 965.3717 | 866.9179 | 581.902 | 723.2543 | 808.1553 | 563.7328 | 645.3813 | 957.4417 | 960.1239 | 652.8414 | 795.3705 | 438.9713 | 966.0355 | 910.5347 | 482.8234 | 574.9206 | 590.44 | 1001.958 | 893.3733 | 758.2903 | 894.2388 | 1014.568 | 533.4972 | 603.1568 | 986.345 | 838.4166 | 81.4338 | 1.6078 | 16.8753 | 5.7141 | -27.8645 | 3.0953 | 9406.25 | -0.01 | 0.22373 | -2.4717 | -20.883 | -0.83142 | 6.724 | -31.5477 | -31.9719 | 84.793 | 93.864 | 49.4419 | 10.4857 | -5.5825 | 7.9752 | 33.1776
42838.4287 | 726 | 22.8768 | 22.8337 | 22.8239 | 22.7371 | 22.3471 | 21.6684 | 22.6776 | 21.7214 | 22.3269 | 22.3207 | 22.2931 | 21.941 | 21.1515 | 22.122 | 21.5839 | 21.7688 | 21.9677 | 21.0667 | 21.3269 | 22.8565 | 20.8246 | 42.057 | 62.6903 | 22.1195 | 23.8753 | 75.8468 | 583.2248 | 622.7515 | 580.9918 | 22.2172 | 23.4006 | 78.0214 | 22.2206 | 23.9402 | 83.5039 | 729.5298 | 862.8084 |  | 876.8807 | 886.1196 | 749.2246 | 757.0832 |  | 108.7997 | 203.5118 | 314.1919 | 660.3465 | 747.2042 | 766.4932 | 788.5237 | 33.3193 | 70.3858 | 39.1134 | 160.9218 | 23.1109 | 48.2031 | 50.7374 | 50.5765 | 24.5784 |  |  | 0.26965 | -1.978 | -196.4258 | -0.3148 | 8.9724 | -197.8309 | -203.4079 | -6.0458 | 6.8845 | 19.5365 | 38.302 | 0.0068488 | 0.0060619 | 0.00037456 | 22.4705 | 21.9777 | 22.1445 | 22.1861 | 21.9897 | 21.276 | 20.0848 | 22.162 | 22.3346 | 22.3698 | 22.3102 | 21.9151 | 21.1472 | 22.2357 | 489.603 | 283.8551 | 338.9855 | 249.0789 | 230.1115 | 455.6071 | 263.0259 | 22.3216 | 22.0865 | 21.73 | 22.0401 | 21.8367 | 22.6818 | 21.9549 | 24.6059 | 66.28 | 587.1876 | 534.5387 | 532.1724 | 518.0096 | 59.4922 | 29.5969 | 798.7566 | 21.8984 | 22.1845 | 237.9227 | 21.5373 | 21.9872 | 22.415 | 27.5316 | 88.3986 | 21.9443 | 23.1879 | 81.3291 | 785.502 | 658.2553 | 642.3732 | 658.7966 | 750.0073 |  | 823.6421 | 828.4292 | 858.7379 | 632.1843 | 684.6779 | 835.883 |  | 723.0631 |  |  | 392.5454 | 625.6631 | 712.3392 | [5 empty] | 21.8548 | 585.1964 | 21.707 | 22.0684 | 348.2383 | 21.2786 | 21.8748 | 452.0598 | 609.1995 | 616.9459 |  | 974.1523 | 879.1287 | 577.8526 | 717.6576 | 803.8552 | 560.6 | 641.8832 | 951.9561 | 970.0963 | 646.6222 | 793.1257 | 455.8266 | 967.9095 | 921.5882 | 481.5495 | 571.2885 | 586.5539 | 978.091 | 890.2412 | 760.7614 | 897.3304 | 1013.66 | 531.3247 | 599.8301 | 972.5817 | 841.7082 | 80.1895 | 1.4972 | 16.9437 | 5.7994 | -28.0607 | 3.0953 | 9382.54 | -0.11 | 1.0576 | -2.1399 | -21.3241 | -0.85367 | 6.7307 | -31.605 | -32.0474 | 84.0957 | 93.9091 | 49.1817 | 12.2151 | -3.7539 | 56.5449 | 32.9857
42838.4287 | 727 | 22.8753 | 22.8429 | 22.8338 | 22.7395 | 22.3503 | 21.6699 | 22.6754 | 21.7262 | 22.3222 | 22.329 | 22.2908 | 21.9426 | 21.1596 | 22.1274 | 21.5876 | 21.7731 | 21.9729 | 21.0642 | 21.3304 | 22.8642 | 20.8422 | 42.7578 | 63.2516 | 22.1248 | 23.9012 | 76.1177 | 587.0623 | 624.9653 | 585.8993 | 22.2192 | 23.4202 | 78.6821 | 22.2197 | 23.9649 | 83.7049 | 732.4552 | 885.5011 |  | 876.4738 | 889.9794 | 757.6494 | 760.3467 |  | 112.1431 | 209.4814 | 322.0539 | 673.6762 | 751.431 | 769.0079 | 792.6819 | 33.271 | 71.8475 | 38.9778 | 164.6124 | 23.1998 | 48.2491 | 50.6046 | 50.5659 | 24.6571 |  |  | 0.59295 | -1.3018 | -196.4804 | -0.32006 | 8.7956 | -197.8348 | -203.4092 | -6.147 | 6.785 | 19.9263 | 35.6263 | 0.006926 | 0.0060455 | 0.0003992 | 22.4681 | 21.9818 | 22.1449 | 22.1885 | 21.9883 | 21.2686 | 20.0791 | 22.159 | 22.3407 | 22.3724 | 22.3079 | 21.9129 | 21.1461 | 22.235 | 492.0934 | 303.2953 | 340.7163 | 238.955 | 224.5748 | 460.5794 | 265.3497 | 22.3339 | 22.0934 | 21.7351 | 22.0424 | 21.8433 | 22.6992 | 21.9585 | 24.6903 | 66.5606 | 585.5655 | 532.0843 | 529.4112 | 514.9462 | 42.6068 | 15.9093 | 788.8321 | 21.9006 | 22.1914 | 238.6961 | 21.5436 | 21.9961 | 22.4173 | 27.6856 | 88.401 | 21.9448 | 23.207 | 81.8003 | 776.5302 | 655.3489 | 650.212 | 666.6721 | 746.1275 |  | 820.5666 | 820.2651 | 857.7124 | 630.1117 | 683.0286 | 829.5481 |  | 731.9437 |  |  | 394.1057 | 625.9332 | 708.5774 | [5 empty] | 21.8583 | 582.8597 | 21.7155 | 22.0732 | 348.9284 | 21.2866 | 21.8826 | 450.1993 | 606.5582 | 613.9699 |  | 971.2903 | 893.7593 | 572.8665 | 711.659 | 801.528 | 557.1278 | 638.6293 | 943.3731 | 972.0068 | 640.4272 | 788.0085 | 475.0691 | 972.0367 | 936.0445 | 480.1284 | 567.8439 | 584.4025 | 946.6273 | 879.984 | 766.7043 | 900.6126 | 1014.3703 | 529.0542 | 598.214 | 954.0258 | 841.4508 | 77.3741 | 1.4321 | 16.9738 | 5.8663 | -27.8236 | 3.0953 | 9261.04 | -0.07 | 1.5728 | -1.7468 | -21.4602 | -0.86614 | 6.6722 | -31.6435 | -32.0863 | 83.2016 | 93.7706 | 48.8656 | 12.9318 | -3.6062 | 57.2072 | 32.7921
42838.4287 | 728 | 22.8705 | 22.8336 | 22.8165 | 22.7375 | 22.3363 | 21.6618 | 22.6724 | 21.7202 | 22.3255 | 22.3276 | 22.2948 | 21.933 | 21.1533 | 22.1205 | 21.5841 | 21.7702 | 21.973 | 21.0572 | 21.3264 | 22.8768 | 20.8632 | 43.4535 | 63.8043 | 22.1166 | 23.9216 | 76.3771 | 591.3154 | 627.8547 | 590.5634 | 22.2253 | 23.4294 | 79.3669 | 22.2193 | 23.9898 | 83.9118 | 734.8446 | 884.8921 |  | 875.477 | 896.1919 | 773.2032 | 762.6997 |  | 115.2746 | 215.1755 | 326.6416 | 679.1537 | 754.6702 | 774.3509 | 797.0371 | 33.3592 | 73.1117 | 39.2237 | 167.8476 | 23.2995 | 48.2798 | 50.4524 | 50.5455 | 24.7221 |  |  | 0.37479 | -1.5127 | -196.4127 | -0.19718 | 8.197 | -197.867 | -203.2561 | -6.3251 | 6.8415 | 19.8094 | 30.7657 | 0.0067699 | 0.0058861 | 0.0003532 | 22.4664 | 21.9741 | 22.1393 | 22.1907 | 21.9847 | 21.2566 | 20.0754 | 22.159 | 22.3349 | 22.3677 | 22.3074 | 21.914 | 21.1463 | 22.2313 | 473.6945 | 284.8676 | 299.5832 | 221.2894 | 212.2174 | 463.9402 | 266.4281 | 22.3275 | 22.0848 | 21.7367 | 22.0388 | 21.8477 | 22.7117 | 21.95 | 24.7644 | 66.8291 | 583.8886 | 529.4746 | 526.4784 | 511.4781 | 52.0147 | 22.1521 | 781.329 | 21.9026 | 22.1855 | 237.8915 | 21.5382 | 21.9919 | 22.4286 | 27.8377 | 88.4003 | 21.9521 | 23.2251 | 82.224 | 769.9023 | 653.1057 | 659.7824 | 676.1986 | 743.7921 |  | 818.0181 | 811.9295 | 856.1189 | 628.435 | 681.7019 | 824.3732 |  | 739.4627 |  |  | 395.7128 | 626.5151 | 705.6176 | [5 empty] | 21.8573 | 580.7985 | 21.7128 | 22.0722 | 348.2577 | 21.284 | 21.8801 | 447.8514 | 603.4829 | 612.0026 |  | 956.4795 | 906.9282 | 567.6575 | 705.3059 | 798.6754 | 553.7501 | 636.1454 | 938.9701 | 971.8157 | 635.09 | 781.5009 | 493.3186 | 976.1457 | 948.1158 | 478.4586 | 565.5837 | 584.3661 | 919.0669 | 869.9105 | 771.9922 | 902.2234 | 1017.5222 | 527.318 | 597.3528 | 938.822 | 840.2832 | 71.893 | 1.3414 | 17.0091 | 5.9115 | -27.8798 | 3.0953 | 9111.3 | -0.04 | 1.2538 | -1.8941 | -21.5827 | -0.68383 | 6.4576 | -31.7271 | -32.1563 | 82.4421 | 93.4363 | 48.6129 | 15.6527 | 1.1223 | 57.7613 | 32.6018
42838.4287 | 729 | 22.8738 | 22.8379 | 22.8227 | 22.7335 | 22.3359 | 21.6554 | 22.6667 | 21.716 | 22.3219 | 22.3256 | 22.2888 | 21.9294 | 21.1471 | 22.1205 | 21.5916 | 21.7726 | 21.9718 | 21.0647 | 21.3326 | 22.8913 | 20.8867 | 44.1651 | 64.3633 | 22.1197 | 23.9514 | 76.6086 | 593.9091 | 631.2606 | 593.5272 | 22.2321 | 23.4398 | 80.0104 | 22.2164 | 24.0167 | 84.0953 | 738.014 | 877.0752 |  | 873.916 | 891.5022 | 790.6165 | 770.2435 |  | 118.331 | 220.8636 | 328.0334 | 683.0092 | 760.0409 | 781.8418 | 800.2389 | 33.3082 | 74.366 | 39.1264 | 170.9992 | 23.3723 | 48.2833 | 50.2895 | 50.521 | 24.7938 |  |  | -0.010942 | -1.8374 | -196.4942 | -0.42323 | 8.5256 | -197.8217 | -203.2246 | -5.8599 | 7.0063 | 20.2152 | 25.5561 | 0.0067026 | 0.0058303 | 0.00038934 | 22.4779 | 21.9821 | 22.1415 | 22.1919 | 21.9919 | 21.2622 | 20.0848 | 22.1581 | 22.3391 | 22.3745 | 22.3119 | 21.9169 | 21.1472 | 22.2366 | 483.3726 | 304.5178 | 303.6749 | 214.8883 | 201.232 | 467.7484 | 267.733 | 22.3333 | 22.0873 | 21.741 | 22.0441 | 21.8506 | 22.7264 | 21.9603 | 24.8585 | 67.1255 | 581.9371 | 526.1831 | 522.4689 | 507.7014 | 45.8287 | 21.3926 | 772.5794 | 21.8961 | 22.1843 | 238.007 | 21.5307 | 21.9915 | 22.4359 | 28.0057 | 88.4091 | 21.9521 | 23.2411 | 82.6029 | 761.8937 | 649.8039 | 666.9251 | 683.2794 | 735.6315 |  | 815.0047 | 803.1838 | 854.1054 | 620.3236 | 679.9315 | 818.5699 |  | 745.7144 |  |  | 396.7455 | 624.2093 | 699.9728 | [5 empty] | 21.8553 | 576.9269 | 21.6999 | 22.0664 | 345.3897 | 21.279 | 21.8723 | 445.7777 | 600.4731 | 609.8836 |  | 954.7754 | 917.2551 | 563.0221 | 699.4254 | 794.3552 | 551.2391 | 633.5912 | 926.9245 | 976.1361 | 630.4334 | 778.1185 | 522.5623 | 978.1131 | 954.2064 | 477.5495 | 564.2744 | 584.8588 | 890.84 | 858.2217 | 777.0337 | 904.356 | 1020.5413 | 526.0112 | 596.4121 | 912.8912 | 842.0197 | 78.6081 | 1.2467 | 17.0416 | 5.9479 | -27.9745 | 3.0953 | 9050.48 | -0.06 | -0.21461 | -2.0996 | -21.7126 | -1.0077 | 6.6093 | -31.8367 | -32.2686 | 81.7009 | 92.9674 | 48.4404 | 15.3491 | 0.8593 | 58.3795 | 32.3748
42838.4287 | 730 | 22.8678 | 22.8341 | 22.8353 | 22.7372 | 22.3482 | 21.662 | 22.6734 | 21.7207 | 22.3166 | 22.3287 | 22.2991 | 21.941 | 21.1534 | 22.1258 | 21.5836 | 21.7696 | 21.9715 | 21.0581 | 21.3335 | 22.8941 | 20.902 | 44.8646 | 64.9059 | 22.1208 | 23.9763 | 76.7961 | 597.9411 | 635.501 | 597.9414 | 22.2191 | 23.4525 | 80.5674 | 22.2151 | 24.0424 | 84.2616 | 741.1188 | 864.8855 |  | 871.6348 | 885.4555 | 803.4485 | 771.7882 |  | 122.0073 | 227.6415 | 331.085 | 690.8952 | 763.3041 | 789.5045 | 804.9624 | 33.0556 | 75.7783 | 39.202 | 174.4999 | 23.472 | 48.2764 | 50.1089 | 50.5085 | 24.8627 |  |  | -0.003054 | -2.4097 | -196.2464 | -0.42125 | 8.5118 | -197.8434 | -203.2463 | -5.8303 | 7.0985 | 20.2594 | 23.1875 | 0.0067075 | 0.0058976 | 0.00039756 | 22.493 | 21.9873 | 22.1378 | 22.1966 | 21.9893 | 21.2668 | 20.0858 | 22.162 | 22.3424 | 22.3737 | 22.3198 | 21.9145 | 21.1404 | 22.2409 | 467.9303 | 288.9473 | 302.4745 | 209.2224 | 199.5062 | 470.8638 | 268.7504 | 22.3349 | 22.0991 | 21.7474 | 22.0412 | 21.8502 | 22.7433 | 21.967 | 24.9373 | 67.3921 | 580.0558 | 523.3186 | 519.0152 | 505.3157 | 43.8155 | 26.6596 | 765.2991 | 21.895 | 22.1823 | 237.4672 | 21.5348 | 21.9878 | 22.4399 | 28.1804 | 88.4003 | 21.9507 | 23.2527 | 82.9439 | 758.2774 | 646.926 | 672.6269 | 689.3077 | 730.4002 |  | 811.866 | 805.0119 | 852.5747 | 613.4952 | 677.7799 | 816.3715 |  | 752.5554 |  |  | 395.8264 | 620.2151 | 696.2468 | [5 empty] | 21.862 | 572.4117 | 21.7026 | 22.0695 | 342.8343 | 21.2785 | 21.8708 | 444.0961 | 597.8246 | 607.5152 |  | 959.6829 | 925.3601 | 558.6056 | 693.5115 | 789.8785 | 549.133 | 630.6216 | 917.8487 | 981.3143 | 626.453 | 774.6425 | 562.0787 | 977.8723 | 961.0401 | 476.7316 | 563.2117 | 585.269 | 859.9423 | 841.4573 | 782.8637 | 905.2708 | 1021.9536 | 524.5284 | 596.3646 | 882.3517 | 843.3786 | 72.9776 | 1.1687 | 17.0771 | 5.9652 | -27.8649 | 3.0953 | 9012.68 | 0.01 | -0.11367 | -2.4209 | -21.8472 | -1.0122 | 6.6278 | -31.9539 | -32.3873 | 80.8458 | 92.3779 | 48.1493 | 17.7002 | 1.1423 | 59.1542 | 32.1229
42838.4287 | 731 | 22.873 | 22.839 | 22.8332 | 22.741 | 22.351 | 21.6709 | 22.6802 | 21.7234 | 22.3234 | 22.3266 | 22.2966 | 21.9362 | 21.1527 | 22.1267 | 21.5819 | 21.7817 | 21.9749 | 21.0644 | 21.3396 | 22.9172 | 20.9341 | 45.5738 | 65.454 | 22.1307 | 24.0007 | 76.9646 | 604.5895 | 640.2432 | 605.3864 | 22.2235 | 23.4659 | 81.1061 | 22.2251 | 24.0771 | 84.4339 | 744.4749 | 848.5127 |  | 868.6511 | 883.0747 | 820.0715 | 777.8895 |  | 124.9493 | 232.7215 | 342.5961 | 696.9948 | 764.8664 | 790.9004 | 806.1786 | 32.8131 | 76.9728 | 39.3794 | 177.4836 | 23.5659 | 48.2991 | 49.9009 | 50.4741 | 24.9373 |  |  | 0.27622 | -2.1304 | -196.3292 | -0.043414 | 8.9185 | -197.7579 | -203.2134 | -6.2206 | 7.5235 | 21.2952 | 21.8826 | 0.0065383 | 0.0056594 | 0.0004107 | 22.4845 | 21.9762 | 22.1321 | 22.187 | 21.9822 | 21.2696 | 20.085 | 22.1505 | 22.3359 | 22.3652 | 22.3117 | 21.9109 | 21.1272 | 22.2326 | 459.2771 | 295.9755 | 308.6442 | 212.8226 | 190.4784 | 473.9135 | 270.0791 | 22.3346 | 22.0903 | 21.7489 | 22.0467 | 21.8468 | 22.7604 | 21.9662 | 25.0227 | 67.6436 | 578.3566 | 520.3582 | 515.6735 | 502.4676 | 53.5653 | 37.0892 | 762.3537 | 21.8967 | 22.188 | 235.2295 | 21.5414 | 21.9945 | 22.451 | 28.3884 | 88.4038 | 21.9511 | 23.2822 | 83.2581 | 756.8287 | 644.8446 | 674.9714 | 692.3378 | 731.8275 |  | 809.1931 | 807.5048 | 851.3294 | 606.3469 | 675.618 | 817.1343 |  | 758.7128 |  |  | 394.3805 | 617.7376 | 694.7949 | [5 empty] | 21.8593 | 568.2532 | 21.7059 | 22.0741 | 340.6392 | 21.2769 | 21.8769 | 442.3521 | 595.3601 | 605.302 |  | 962.4259 | 930.9724 | 554.0381 | 687.7588 | 784.6595 | 547.0348 | 627.8299 | 912.4351 | 987.5895 | 622.243 | 771.0857 | 601.8819 | 978.3058 | 965.2757 | 475.946 | 562.9031 | 585.981 | 830.42 | 823.2572 | 790.4509 | 908.0254 | 1023.4989 | 523.968 | 597.5388 | 853.0731 | 837.9821 | 72.0857 | 1.1148 | 17.112 | 5.9711 | -27.7694 | 3.0953 | 8974.36 | -0.09 | 1.0856 | -2.2878 | -21.9624 | -0.32659 | 6.7888 | -31.968 | -32.4059 | 79.9604 | 91.8718 | 47.8676 | 19.2872 | 0.65258 | 59.8761 | 31.9162
42838.4287 | 732 | 22.8794 | 22.8472 | 22.8372 | 22.7485 | 22.3544 | 21.6742 | 22.6818 | 21.7282 | 22.3318 | 22.3337 | 22.2918 | 21.9437 | 21.1605 | 22.133 | 21.5849 | 21.767 | 21.981 | 21.0661 | 21.3319 | 22.9255 | 20.9466 | 46.2791 | 65.9839 | 22.1238 | 24.0249 | 77.1051 | 609.9136 | 642.7574 | 610.0971 | 22.2248 | 23.486 | 81.6158 | 22.2246 | 24.0996 | 84.5925 | 748.3262 | 829.7769 |  | 864.8917 | 878.5062 | 833.7658 | 779.0657 |  | 128.3513 | 238.6416 | 354.3849 | 703.0326 | 768.2403 | 798.3714 | 809.4614 | 32.5588 | 78.4615 | 39.9075 | 181.007 | 23.6328 | 48.3211 | 49.6526 | 50.4273 | 25.0093 |  |  | -0.079938 | -2.2185 | -191.5007 | -0.086782 | 9.0158 | -197.8072 | -203.2712 | -5.4314 | 6.9376 | 19.5633 | 20.4026 | 0.006374 | 0.005615 | 0.00041398 | 22.4924 | 21.9822 | 22.1411 | 22.1996 | 21.9982 | 21.2665 | 20.0774 | 22.1629 | 22.3346 | 22.372 | 22.3145 | 21.9192 | 21.1433 | 22.2416 | 464.7717 | 303.6091 | 355.5629 | 233.1441 | 204.3383 | 477.7903 | 272.7747 | 22.3345 | 22.0888 | 21.7455 | 22.0474 | 21.8469 | 22.775 | 21.9675 | 25.1163 | 67.8966 | 576.5143 | 517.5032 | 512.5815 | 499.1284 | 54.149 | 31.7225 | 762.4347 | 21.8938 | 22.1799 | 233.0389 | 21.5271 | 21.9869 | 22.4536 | 28.582 | 88.3967 | 21.9411 | 23.2956 | 83.5458 | 756.0636 | 642.6201 | 676.9203 | 694.2078 | 730.6587 |  | 806.5924 | 808.7939 | 850.085 | 603.0809 | 673.6656 | 817.8146 |  | 764.3509 |  |  | 394.1553 | 615.8032 | 693.2476 | [5 empty] | 21.8559 | 565.341 | 21.7027 | 22.0654 | 339.9374 | 21.2738 | 21.8713 | 440.2143 | 593.4475 | 603.3562 |  | 964.7798 | 937.5963 | 549.2667 | 683.3403 | 779.2039 | 545.3867 | 625.9133 | 905.6444 | 987.3926 | 617.9416 | 769.9403 | 634.3701 | 979.0687 | 968.8449 | 475.1603 | 563.242 | 588.1306 | 803.5109 | 804.3467 | 792.9689 | 908.08 | 1026.2477 | 523.8185 | 599.7762 | 827.2961 | 827.8008 | 68.9797 | 1.0499 | 17.1852 | 5.9743 | -27.8318 | 3.0952 | 8950.47 | -0.11 | -0.58558 | -2.3482 | -21.8172 | -0.46444 | 6.8497 | -32.084 | -32.5241 | 79.1754 | 91.4008 | 47.5271 | 19.4769 | -4.1624 | 60.8761 | 31.7006
42838.4288 | 733 | 22.8773 | 22.8503 | 22.8398 | 22.7453 | 22.349 | 21.6783 | 22.6828 | 21.7246 | 22.3349 | 22.3317 | 22.297 | 21.9388 | 21.1589 | 22.1358 | 21.5856 | 21.7672 | 21.9743 | 21.0689 | 21.3395 | 22.9381 | 20.9889 | 46.9947 | 66.4913 | 22.1277 | 24.0528 | 77.2509 | 612.2022 | 644.713 | 612.2045 | 22.2231 | 23.4986 | 82.0832 | 22.2315 | 24.1377 | 84.7315 | 751.3099 | 819.9409 |  | 861.0662 | 874.1068 | 837.8277 | 760.8557 |  | 131.2634 | 244.0221 | 355.5912 | 703.6355 | 772.0033 | 805.9586 | 812.1172 | 32.1381 | 79.7178 | 40.0347 | 184.0029 | 23.7405 | 48.3509 | 49.3522 | 50.3713 | 25.0848 |  |  | 0.069226 | -2.2527 | -183.5812 | 0.002586 | 9.0539 | -197.846 | -203.3475 | -5.7107 | 7.5305 | 21.9775 | 19.3298 | 0.0064923 | 0.0055723 | 0.00039427 | 22.4886 | 21.9885 | 22.1373 | 22.1995 | 21.9877 | 21.2656 | 20.0795 | 22.1579 | 22.3341 | 22.3637 | 22.3074 | 21.9098 | 21.1422 | 22.2338 | 488.0553 | 316.2756 | 366.7361 | 252.2739 | 216.4872 | 481.7632 | 275.2702 | 22.333 | 22.0826 | 21.7462 | 22.0458 | 21.8459 | 22.7967 | 21.965 | 25.2137 | 68.14 | 574.6402 | 514.3017 | 509.5436 | 499.1852 | 51.5314 | 30.1916 | 761.0683 | 21.9061 | 22.1911 | 231.1729 | 21.5387 | 21.994 | 22.4589 | 28.8328 | 88.3916 | 21.952 | 23.3254 | 83.834 | 752.1361 | 640.4721 | 683.6916 | 700.4924 | 726.1494 |  | 803.7085 | 804.157 | 848.4418 | 597.6492 | 671.4543 | 814.6485 |  | 770.2245 |  |  | 393.4586 | 612.1026 | 690.0237 | [5 empty] | 21.8644 | 561.912 | 21.7036 | 22.0672 | 340.2786 | 21.2839 | 21.8826 | 438.1345 | 591.9231 | 601.1365 |  | 964.6177 | 935.8017 | 544.3949 | 682.4115 | 774.2909 | 544.4674 | 624.1201 | 893.9262 | 984.3962 | 614.817 | 769.9568 | 658.3558 | 978.4661 | 975.6073 | 474.1531 | 563.4199 | 589.8291 | 779.6426 | 787.1333 | 793.138 | 908.5533 | 1027.2291 | 523.1104 | 600.8097 | 805.5384 | 817.0074 | 68.0609 | 0.98553 | 17.2301 | 5.9785 | -27.8896 | 3.0952 | 8871.22 | -0.1 | 0.54558 | -2.3787 | -21.4733 | 0.080593 | 6.8884 | -32.2005 | -32.6452 | 78.4005 | 90.957 | 47.1923 | 17.7159 | -5.0338 | 62.1892 | 31.3871
42838.4288 | 734 | 22.8789 | 22.8465 | 22.8373 | 22.7468 | 22.3483 | 21.6717 | 22.6838 | 21.7247 | 22.3313 | 22.3357 | 22.2969 | 21.9482 | 21.1561 | 22.1278 | 21.581 | 21.7702 | 21.9783 | 21.0598 | 21.3402 | 22.9538 | 21.001 | 47.7531 | 67.0301 | 22.1333 | 24.0728 | 77.3685 | 612.9957 | 646.4969 | 612.7726 | 22.218 | 23.5108 | 82.521 | 22.2325 | 24.1754 | 84.8721 | 752.7336 | 823.458 |  | 857.8983 | 882.18 | 845.5383 | 744.9099 |  | 134.5166 | 249.4811 | 357.0861 | 706.8849 | 778.7075 | 812.3103 | 817.7266 | 32.1241 | 81.0654 | 40.2001 | 187.1038 | 23.8151 | 48.3789 | 49.025 | 50.3316 | 25.1761 |  |  | -0.20873 | -2.0056 | -168.5129 | -0.095982 | 7.5517 | -197.7842 | -203.2594 | -5.848 | 6.9664 | 19.5088 | 19.3921 | 0.0063346 | 0.0055986 | 0.00038934 | 22.5048 | 21.9826 | 22.1368 | 22.1903 | 21.9917 | 21.2726 | 20.0819 | 22.1615 | 22.3361 | 22.366 | 22.315 | 21.9136 | 21.1409 | 22.2381 | 481.4909 | 316.786 | 360.8597 | 251.9201 | 219.1674 | 484.8167 | 277.3866 | 22.3311 | 22.092 | 21.7445 | 22.0471 | 21.8532 | 22.8116 | 21.9678 | 25.3122 | 68.4015 | 572.912 | 511.0858 | 506.8341 | 499.6481 | 51.5133 | 23.4243 | 756.3796 | 21.8977 | 22.1768 | 229.7875 | 21.5277 | 21.9946 | 22.4577 | 29.0727 | 88.366 | 21.9533 | 23.3367 | 84.0735 | 746.1505 | 638.6838 | 693.1543 | 709.5003 | 719.7481 |  | 800.5575 | 792.8156 | 845.9695 | 600.2027 | 669.264 | 807.7091 |  | 776.8422 |  |  | 392.938 | 607.7315 | 685.346 | [5 empty] | 21.8617 | 561.1041 | 21.7147 | 22.0773 | 341.7373 | 21.2736 | 21.8722 | 437.5654 | 590.3697 | 598.8437 |  | 963.2105 | 932.2678 | 540.5365 | 680.4238 | 769.906 | 543.352 | 622.3281 | 902.4569 | 984.3432 | 611.9137 | 772.0289 | 697.7121 | 976.8013 | 981.9515 | 473.1037 | 563.5598 | 590.4589 | 758.4612 | 772.4919 | 793.4627 | 916.6598 | 1025.8709 | 522.7201 | 600.5606 | 785.5783 | 810.2461 | 66.6747 | 0.91966 | 17.2609 | 5.9827 | -27.9071 | 3.0953 | 8786.19 | -0.07 | -0.94768 | -2.2562 | -20.6815 | -0.49358 | 6.3095 | -32.2901 | -32.734 | 77.6023 | 90.4148 | 46.6433 | 19.0843 | -4.0661 | 63.0196 | 31.0882
42838.4288 | 735 | 22.8822 | 22.8552 | 22.834 | 22.7471 | 22.3469 | 21.674 | 22.6846 | 21.7285 | 22.3275 | 22.3346 | 22.298 | 21.9462 | 21.1584 | 22.135 | 21.5747 | 21.7647 | 21.9776 | 21.0666 | 21.3363 | 22.9646 | 21.0249 | 48.4567 | 67.5297 | 22.1281 | 24.0994 | 77.4654 | 614.2721 | 648.6884 | 614.1146 | 22.2168 | 23.5295 | 82.9663 | 22.2228 | 24.208 | 85.0208 | 753.8675 | 827.0976 |  | 855.2289 | 892.3894 | 862.2992 | 732.9385 |  | 138.6017 | 255.9254 | 359.7341 | 703.2948 | 784.2867 | 817.6016 | 821.4161 | 31.8395 | 82.4513 | 39.6508 | 190.3109 | 23.9063 | 48.397 | 48.6992 | 50.2883 | 25.2457 |  |  | -0.044454 | -2.0246 | -171.8668 | -0.070354 | 9.8017 | -197.8006 | -203.3692 | -5.3302 | 6.8557 | 19.835 | 19.0371 | 0.0063017 | 0.005436 | 0.00037949 | 22.5025 | 21.9671 | 22.1392 | 22.1856 | 21.9892 | 21.2655 | 20.0772 | 22.1501 | 22.3356 | 22.3555 | 22.3026 | 21.9105 | 21.1411 | 22.2319 | 479.6785 | 320.7313 | 351.548 | 243.2551 | 206.7917 | 487.8248 | 279.0267 | 22.3332 | 22.0917 | 21.737 | 22.0444 | 21.8576 | 22.8269 | 21.9699 | 25.4126 | 68.6146 | 571.3392 | 508.9918 | 505.0466 | 498.2985 | 40.7872 | 28.0264 | 750.6947 | 21.9008 | 22.1835 | 228.9827 | 21.5382 | 21.9865 | 22.4678 | 29.3355 | 88.3698 | 21.9601 | 23.3649 | 84.3155 | 741.8872 | 637.936 | 701.2865 | 717.5818 | 717.5046 |  | 797.925 | 788.8942 | 843.9947 | 600.1756 | 667.479 | 805.1344 |  | 782.346 |  |  | 391.1067 | 605.0528 | 682.4393 | [5 empty] | 21.8544 | 559.6778 | 21.7107 | 22.0619 | 344.1564 | 21.2772 | 21.8726 | 436.6674 | 589.0878 | 597.0624 |  | 966.5739 | 932.106 | 536.5457 | 679.4353 | 768.5856 | 542.0367 | 621.4212 | 903.8021 | 982.5216 | 607.7151 | 774.2057 | 737.0861 | 976.0249 | 985.8713 | 472.548 | 563.2832 | 590.8883 | 738.9909 | 759.975 | 794.2082 | 924.3439 | 1021.9429 | 522.0355 | 600.7913 | 766.9273 | 802.9562 | 59.9969 | 0.87314 | 17.2885 | 5.9893 | -27.9083 | 3.0952 | 8677.32 | -0.06 | -0.43767 | -2.2809 | -21.0146 | -0.42518 | 7.2058 | -32.3701 | -32.8226 | 76.8552 | 89.8428 | 46.2566 | 19.9187 | -2.7869 | 63.6618 | 30.8665
42838.4288 | 736 | 22.8705 | 22.842 | 22.8402 | 22.7452 | 22.3467 | 21.6718 | 22.6837 | 21.7239 | 22.3216 | 22.3262 | 22.2943 | 21.9396 | 21.154 | 22.1234 | 21.5803 | 21.7641 | 21.9714 | 21.0558 | 21.34 | 22.9791 | 21.0462 | 49.1557 | 68.0213 | 22.1303 | 24.1309 | 77.5806 | 615.1024 | 649.5958 | 614.9619 | 22.2168 | 23.5516 | 83.4105 | 22.2357 | 24.2425 | 85.1621 | 753.6698 | 815.0984 |  | 851.4835 | 899.0498 | 876.5943 | 710.3613 |  | 141.6793 | 260.9229 | 362.1191 | 704.7993 | 785.7503 | 820.8934 | 825.0158 | 32.0449 | 83.6412 | 39.4029 | 193.0948 | 23.9882 | 48.3809 | 48.3752 | 50.2446 | 25.3306 |  |  | 0.29593 | -2.5477 | -167.8722 | -0.6519 | 8.9737 | -197.8519 | -203.2555 | -5.8691 | 7.7973 | 22.4191 | 20.02 | 0.0063165 | 0.0054179 | 0.00037291 | 22.5075 | 21.9758 | 22.1445 | 22.1888 | 21.989 | 21.2667 | 20.0755 | 22.1569 | 22.3387 | 22.359 | 22.3094 | 21.9134 | 21.1422 | 22.2356 | 470.4888 | 315.8065 | 342.625 | 249.1277 | 216.793 | 489.7539 | 280.3569 | 22.3295 | 22.0884 | 21.7355 | 22.0368 | 21.8501 | 22.8428 | 21.9668 | 25.499 | 68.8236 | 569.7067 | 506.9125 | 502.9853 | 495.9035 | 47.2575 | 24.6079 | 746.4839 | 21.9058 | 22.1828 | 228.068 | 21.5348 | 21.9951 | 22.4797 | 29.6122 | 88.3561 | 21.9596 | 23.3967 | 84.5446 | 734.0991 | 638.057 | 710.3588 | 726.154 | 712.8519 |  | 794.9596 | 778.3118 | 841.3415 | 604.9255 | 665.9439 | 797.9224 |  | 787.4244 |  |  | 390.6904 | 603.1408 | 678.5805 | [5 empty] | 21.8618 | 561.8691 | 21.7133 | 22.0705 | 346.7115 | 21.286 | 21.8665 | 435.6952 | 588.5993 | 595.5204 |  | 965.4311 | 929.1857 | 531.5643 | 677.3367 | 766.1651 | 541.3967 | 620.7014 | 905.7951 | 972.8339 | 603.7802 | 771.3902 | 766.0339 | 976.3672 | 988.377 | 472.0075 | 563.0347 | 591.5535 | 722.2286 | 748.633 | 791.0562 | 922.6597 | 1021.6076 | 521.7892 | 600.6218 | 751.2732 | 795.3151 | 57.9823 | 0.82089 | 17.3187 | 5.992 | -27.9489 | 3.0953 | 8555.1 | -0.08 | 1.1298 | -2.5706 | -20.8668 | -1.3003 | 6.9051 | -32.4231 | -32.8629 | 76.0791 | 89.2271 | 45.793 | 21.3477 | -1.5967 | 64.2349 | 30.6654
42838.4288 | 737 | 22.8705 | 22.8406 | 22.8304 | 22.7405 | 22.3479 | 21.6676 | 22.6796 | 21.7204 | 22.3231 | 22.3289 | 22.2916 | 21.9363 | 21.1501 | 22.1191 | 21.5844 | 21.7689 | 21.9843 | 21.0591 | 21.3522 | 23.0003 | 21.0749 | 49.86 | 68.5128 | 22.1337 | 24.1625 | 77.7026 | 615.0473 | 648.8342 | 614.556 | 22.226 | 23.5659 | 83.7871 | 22.234 | 24.2816 | 85.313 | 752.3881 | 806.9606 |  | 847.919 | 901.4231 | 884.3243 | 693.5803 |  | 146.0042 | 268.1182 | 367.037 | 710.7954 | 791.4985 | 824.0764 | 831.7749 | 32.6331 | 85.1122 | 39.4306 | 196.5189 | 24.0904 | 48.3714 | 48.0722 | 50.2033 | 25.409 |  |  | -0.039198 | -1.8945 | -164.143 | -0.34831 | 9.0079 | -197.8171 | -203.268 | -5.2474 | 7.478 | 21.5787 | 17.699 | 0.0061539 | 0.0053621 | 0.00037784 | 22.5159 | 21.9822 | 22.1397 | 22.1906 | 21.9866 | 21.2665 | 20.0734 | 22.1603 | 22.3318 | 22.3655 | 22.3164 | 21.9091 | 21.1404 | 22.2333 | 462.0849 | 303.4473 | 326.7744 | 250.2351 | 220.7537 | 491.6002 | 281.295 | 22.3282 | 22.0884 | 21.7441 | 22.0373 | 21.8493 | 22.8584 | 21.9741 | 25.6028 | 69.0436 | 567.9982 | 505.2076 | 501.0913 | 493.2671 | 43.9442 | 29.0215 | 737.7813 | 21.9024 | 22.1894 | 226.2935 | 21.5344 | 21.9969 | 22.4841 | 29.9026 | 88.3409 | 21.9701 | 23.4193 | 84.7757 | 724.9134 | 637.7579 | 717.9036 | 733.2944 | 700.333 |  | 791.0582 | 772.8075 | 838.6836 | 611.3051 | 664.5965 | 790.8692 |  | 792.7832 |  |  | 388.3641 | 598.4245 | 671.5487 | [5 empty] | 21.8596 | 564.444 | 21.7074 | 22.0645 | 349.241 | 21.2771 | 21.8751 | 435.3146 | 588.8128 | 594.3534 |  | 965.813 | 924.3362 | 526.2896 | 673.3119 | 763.993 | 541.2243 | 621.045 | 899.6773 | 969.6331 | 600.4597 | 766.4355 | 783.6119 | 972.5013 | 990.6435 | 471.5243 | 562.3725 | 591.8634 | 707.1748 | 738.3244 | 786.4294 | 923.8697 | 1017.1107 | 521.1852 | 600.3693 | 735.8923 | 787.8779 | 60.3621 | 0.77501 | 17.3477 | 5.9903 | -28.0711 | 3.0952 | 8461.6 | -0.01 | -0.41109 | -2.2316 | -20.7723 | -0.95688 | 6.9283 | -32.4674 | -32.9116 | 75.2461 | 88.4746 | 45.3258 | 22.6732 | 0.3049 | 64.3513 | 30.4598
42838.4288 | 738 | 22.8728 | 22.8432 | 22.8339 | 22.739 | 22.3519 | 21.6677 | 22.6762 | 21.7254 | 22.3163 | 22.3296 | 22.2969 | 21.9358 | 21.1531 | 22.1228 | 21.5744 | 21.7665 | 21.979 | 21.0621 | 21.3479 | 23.0104 | 21.1051 | 50.5477 | 68.9714 | 22.1355 | 24.1923 | 77.7955 | 613.0725 | 645.9825 | 612.1813 | 22.2222 | 23.5769 | 84.1456 | 22.2321 | 24.3135 | 85.4435 | 750.4037 | 806.1134 |  | 844.7232 | 901.7009 | 888.2137 | 676.0163 |  | 149.8507 | 275.0781 | 371.4724 | 715.0476 | 796.9872 | 830.4679 | 842.1401 | 33.4632 | 86.4458 | 39.6127 | 199.696 | 24.1879 | 48.3289 | 47.7784 | 50.1634 | 25.4815 |  |  | 0.04097 | -1.9885 | -158.7488 | -0.41403 | 9.0112 | -197.8164 | -203.331 | -5.5911 | 7.2377 | 20.6658 | 15.8467 | 0.0062229 | 0.0054935 | 0.0003647 | 22.5227 | 21.9897 | 22.1429 | 22.1909 | 21.9924 | 21.2779 | 20.0814 | 22.1648 | 22.334 | 22.3705 | 22.3172 | 21.9159 | 21.1485 | 22.2379 | 453.9867 | 318.3251 | 347.29 | 240.2497 | 212.6466 | 493.5177 | 282.8141 | 22.338 | 22.0957 | 21.7498 | 22.0424 | 21.8572 | 22.8874 | 21.9787 | 25.7127 | 69.2724 | 566.2342 | 504.0518 | 499.7588 | 492.5728 | 43.9372 | 26.2849 | 732.5509 | 21.9078 | 22.1917 | 225.2131 | 21.5359 | 21.9924 | 22.5017 | 30.204 | 88.341 | 21.966 | 23.4455 | 84.9867 | 720.2636 | 636.5213 | 722.1341 | 736.8396 | 693.9072 |  | 787.5877 | 774.5797 | 836.7871 | 611.1927 | 663.3392 | 789.7113 |  | 797.7667 |  |  | 386.2748 | 591.741 | 664.483 | [5 empty] | 21.8563 | 564.396 | 21.7045 | 22.0652 | 350.2101 | 21.282 | 21.8741 | 435.1245 | 589.2292 | 593.2854 |  | 965.7392 | 920.0745 | 521.9563 | 670.2314 | 762.1516 | 540.9185 | 621.0962 | 903.8294 | 967.5923 | 597.2735 | 763.337 | 809.083 | 972.842 | 993.0356 | 471.5871 | 562.0664 | 591.9645 | 693.5927 | 728.4759 | 780.4798 | 929.1942 | 1020.1653 | 521.1574 | 600.2705 | 722.1345 | 780.478 | 60.4172 | 0.73316 | 17.3772 | 5.9821 | -27.951 | 3.0952 | 8400.49 | -0.05 | 0.41971 | -2.301 | -20.559 | -1.0499 | 6.9497 | -32.5617 | -33.0125 | 74.3842 | 87.7831 | 45.0593 | 23.9813 | -1.7468 | 64.3 | 30.1928
42838.4288 | 739 | 22.8761 | 22.8428 | 22.8369 | 22.736 | 22.3472 | 21.6672 | 22.6753 | 21.7192 | 22.3235 | 22.3284 | 22.2925 | 21.928 | 21.152 | 22.1282 | 21.5824 | 21.7727 | 21.9812 | 21.0714 | 21.3575 | 23.0299 | 21.1426 | 51.2339 | 69.4241 | 22.1402 | 24.2234 | 77.9029 | 609.8638 | 642.2699 | 608.8836 | 22.223 | 23.5992 | 84.5094 | 22.2395 | 24.3584 | 85.5783 | 747.6786 | 810.6723 |  | 842.0011 | 903.1926 | 892.3249 | 662.6941 |  | 153.3709 | 281.6401 | 375.1952 | 719.2473 | 799.187 | 832.2433 | 850.9265 | 34.3229 | 87.7142 | 39.8971 | 202.7436 | 24.2854 | 48.2999 | 47.5218 | 50.1351 | 25.573 |  |  | 0.20853 | -1.9543 | -155.5131 | -0.067726 | 9.9804 | -197.8164 | -203.3034 | -5.8631 | 7.7639 | 21.3403 | 15.2606 | 0.0061177 | 0.0052799 | 0.00038441 | 22.5263 | 21.9855 | 22.1406 | 22.1962 | 21.9948 | 21.2749 | 20.0864 | 22.1623 | 22.341 | 22.3582 | 22.3198 | 21.9163 | 21.148 | 22.2352 | 453.6876 | 301.7865 | 339.8307 | 240.0604 | 207.553 | 495.0897 | 283.9978 | 22.332 | 22.0868 | 21.7449 | 22.0438 | 21.8586 | 22.9177 | 21.9797 | 25.8264 | 69.4927 | 564.6583 | 503.1944 | 499.4898 | 495.3483 | 40.0584 | 18.0274 | 732.58 | 21.9037 | 22.1899 | 225.1364 | 21.5309 | 22.001 | 22.4969 | 30.5097 | 88.3294 | 21.966 | 23.4728 | 85.2067 | 717.9169 | 634.2718 | 724.6348 | 737.2311 | 693.8727 |  | 784.3677 | 783.1331 | 836.0832 | 604.746 | 661.7801 | 793.2282 |  | 803.0407 |  |  | 383.9427 | 585.3253 | 660.0984 | [5 empty] | 21.8646 | 561.4072 | 21.7141 | 22.0605 | 348.3199 | 21.2863 | 21.8779 | 434.5576 | 589.2126 | 592.1222 |  | 967.1362 | 918.6722 | 518.1789 | 667.5953 | 759.2969 | 540.5899 | 620.9694 | 902.4952 | 970.245 | 594.2867 | 759.5139 | 840.0756 | 977.1525 | 996.9318 | 471.6271 | 562.3373 | 591.0392 | 680.7089 | 718.634 | 776.0568 | 938.2757 | 1024.434 | 521.2261 | 600.6313 | 708.9695 | 774.7094 | 59.6958 | 0.69706 | 17.4066 | 5.9765 | -27.8785 | 3.0952 | 8402.01 | -0.11 | 0.94514 | -2.2947 | -20.4699 | -0.42718 | 7.3198 | -32.5879 | -33.0368 | 73.428 | 87.3078 | 44.9054 | 24.3504 | -0.74023 | 63.9343 | 29.8611
42838.4288 | 740 | 22.87 | 22.8358 | 22.8329 | 22.7347 | 22.3465 | 21.6605 | 22.6727 | 21.7187 | 22.3231 | 22.3229 | 22.2969 | 21.9318 | 21.1472 | 22.1203 | 21.5853 | 21.7739 | 21.9886 | 21.0716 | 21.3581 | 23.0432 | 21.1746 | 51.9152 | 69.848 | 22.1399 | 24.2526 | 78.0353 | 607.6162 | 638.9356 | 606.7015 | 22.2227 | 23.6228 | 84.8418 | 22.2409 | 24.3937 | 85.7071 | 744.9031 | 813.7534 |  | 531.56 | 902.4889 | 893.7058 | 654.0151 |  | 157.3007 | 288.3233 | 378.5195 | 721.3996 | 802.1033 | 837.4837 | 858.5841 | 34.9415 | 89.148 | 40.2293 | 206.1107 | 24.3595 | 48.2749 | 47.2666 | 50.0827 | 25.6512 |  |  | 0.06857 | -1.7723 | -91.1966 | -0.32072 | 9.7866 | -197.869 | -203.2923 | -4.982 | 7.8491 | 22.1321 | 15.0405 | 0.0058795 | 0.0052175 | 0.0003762 | 22.5266 | 21.9839 | 22.1401 | 22.1884 | 21.9871 | 21.2661 | 20.0787 | 22.1579 | 22.3332 | 22.3629 | 22.3077 | 21.9139 | 21.144 | 22.2313 | 438.3093 | 277.1161 | 311.756 | 231.2394 | 202.3127 | 495.9915 | 284.459 | 22.3309 | 22.0879 | 21.7485 | 22.0422 | 21.8567 | 22.9297 | 21.9838 | 25.9391 | 69.6881 | 563.3204 | 502.2452 | 498.814 | 495.3338 | 49.2357 | 17.4885 | 734.7981 | 21.9119 | 22.1865 | 224.2829 | 21.5371 | 21.9894 | 22.5143 | 30.8468 | 88.3267 | 21.9689 | 23.497 | 85.4133 | 715.3895 | 631.9671 | 727.4142 | 737.1698 | 693.0514 |  | 780.8514 | 788.4727 | 835.3219 | 598.3659 | 659.9241 | 796.5987 |  | 808.6391 |  |  | 380.7771 | 580.769 | 657.1988 | [5 empty] | 21.8573 | 557.5731 | 21.7138 | 22.0597 | 345.4639 | 21.2771 | 21.8724 | 434.149 | 588.9321 | 591.2667 |  | 971.9948 | 923.2596 | 514.3953 | 664.1932 | 757.124 | 540.1881 | 621.2318 | 897.3321 | 968.9969 | 591.1652 | 755.4441 | 869.7517 | 978.319 | 1000.8789 | 471.3528 | 562.9314 | 589.8425 | 668.7447 | 709.2975 | 772.8711 | 938.9513 | 1026.8141 | 521.2287 | 600.8513 | 697.373 | 768.2524 | 64.8982 | 0.66709 | 17.4371 | 5.9703 | -27.8449 | 3.0952 | 8413.83 | -0.06 | 0.5413 | -2.1984 | -15.7696 | -0.93518 | 7.2655 | -32.6694 | -33.1141 | 72.4147 | 86.9029 | 44.6881 | 26.2522 | 2.4485 | 63.4313 | 29.6463
42838.4289 | 741 | 22.8738 | 22.8377 | 22.8339 | 22.7414 | 22.347 | 21.6692 | 22.6798 | 21.7253 | 22.3244 | 22.3292 | 22.2955 | 21.9401 | 21.1488 | 22.1254 | 21.5799 | 21.7623 | 21.9809 | 21.0632 | 21.3538 | 23.0453 | 21.1961 | 52.5778 | 70.261 | 22.1314 | 24.2791 | 78.1967 | 605.7949 | 635.7141 | 604.8103 | 22.2216 | 23.64 | 85.1653 | 22.2314 | 24.4282 | 85.8228 | 741.9989 | 812.1549 |  | 343.1231 | 902.8304 | 894.2841 | 644.5989 |  | 160.2606 | 293.62 | 382.463 | 724.3334 | 808.8317 | 840.9909 | 864.7822 | 35.4963 | 90.3902 | 40.7322 | 209.0587 | 24.4764 | 48.2507 | 47.042 | 50.0307 | 25.7288 |  |  | 0.14611 | -2.091 | -104.7464 | -0.58291 | 8.312 | -197.8394 | -203.3363 | -5.6772 | 7.9139 | 21.8869 | 15.5625 | 0.0059305 | 0.0051731 | 0.00037456 | 22.5359 | 21.985 | 22.1446 | 22.1894 | 21.9884 | 21.2699 | 20.0796 | 22.1614 | 22.342 | 22.3687 | 22.3094 | 21.9245 | 21.1436 | 22.2353 | 437.8469 | 266.6618 | 285.9696 | 219.6363 | 188.641 | 497.8119 | 284.8522 | 22.3343 | 22.0915 | 21.7495 | 22.0471 | 21.8662 | 22.9525 | 21.9945 | 26.0521 | 69.8788 | 562.1405 | 501.7194 | 498.8314 | 496.2189 | 49.8686 | 20.0829 | 735.7769 | 21.9013 | 22.1814 | 223.2737 | 21.5307 | 21.9815 | 22.5096 | 31.1775 | 88.33 | 21.9609 | 23.5248 | 85.6346 | 716.3478 | 630.3579 | 730.1384 | 737.7051 | 695.6837 |  | 777.8969 | 804.3821 | 835.9149 | 597.3281 | 658.2253 | 806.487 |  | 814.1718 |  |  | 378.3222 | 577.5745 | 656.0032 | [5 empty] | 21.8526 | 555.3092 | 21.7067 | 22.0578 | 343.5835 | 21.2752 | 21.8667 | 433.5052 | 588.6494 | 590.8762 |  | 976.9701 | 929.4979 | 511.0917 | 660.9473 | 755.9293 | 539.9414 | 621.4515 | 893.1127 | 966.6345 | 588.3204 | 750.4632 | 893.6669 | 978.9069 | 1006.4735 | 471.0478 | 563.5434 | 589.1307 | 657.1954 | 700.965 | 768.6666 | 947.2369 | 1032.0637 | 520.5488 | 600.6203 | 686.2763 | 762.1616 | 65.3521 | 0.63388 | 17.4658 | 5.9612 | -27.981 | 3.0952 | 8412.03 | -0.16 | 0.7893 | -2.3991 | -16.9801 | -1.2667 | 6.7064 | -32.7185 | -33.1699 | 71.4782 | 86.6608 | 44.3576 | 26.6943 | 5.3729 | 62.9202 | 29.4327
42838.4289 | 742 | 22.874 | 22.8434 | 22.8316 | 22.7462 | 22.3458 | 21.6717 | 22.6817 | 21.7262 | 22.3272 | 22.325 | 22.2933 | 21.9442 | 21.157 | 22.1245 | 21.5782 | 21.758 | 21.9757 | 21.0601 | 21.3576 | 23.0634 | 21.2268 | 53.2379 | 70.6637 | 22.1333 | 24.3134 | 78.3937 | 603.5132 | 633.1094 | 602.4896 | 22.2324 | 23.6553 | 85.4903 | 22.2439 | 24.4731 | 85.9524 | 739.1026 | 812.6158 |  | 345.1937 | 900.4876 | 891.952 | 646.5851 |  | 163.8038 | 299.677 | 385.1733 | 723.233 | 807.9533 | 843.3582 | 870.888 | 35.9374 | 91.8889 | 41.0734 | 212.4186 | 24.5881 | 48.2239 | 46.824 | 49.9807 | 25.8148 |  |  | 0.22102 | -1.2591 | -127.66 | -0.20112 | 9.6203 | -197.7967 | -203.2818 | -5.1863 | 7.4062 | 19.6934 | 14.4829 | 0.0058746 | 0.0050664 | 0.00040248 | 22.543 | 21.9846 | 22.1433 | 22.1947 | 21.9901 | 21.2645 | 20.0768 | 22.1629 | 22.3436 | 22.3714 | 22.3155 | 21.9216 | 21.1424 | 22.2345 | 458.4739 | 287.2195 | 276.4665 | 222.3946 | 176.0329 | 500.1212 | 285.2883 | 22.3291 | 22.0885 | 21.7497 | 22.0445 | 21.8583 | 22.9676 | 21.992 | 26.1605 | 70.0571 | 561.0137 | 501.2283 | 498.6835 | 496.2355 | 55.763 | 24.1543 | 742.7098 | 21.9134 | 22.1824 | 221.7257 | 21.5307 | 21.9886 | 22.5226 | 31.5556 | 88.3228 | 21.9663 | 23.552 | 85.8615 | 717.5479 | 629.6325 | 731.6093 | 736.4842 | 702.5632 |  | 775.7055 | 805.088 | 835.9625 | 598.2608 | 656.7968 | 808.5449 |  | 818.586 |  |  | 377.3066 | 575.1992 | 658.1235 | [5 empty] | 21.8509 | 554.1698 | 21.7031 | 22.0625 | 344.6428 | 21.2772 | 21.8673 | 432.428 | 588.2557 | 590.9511 |  | 973.7461 | 931.9098 | 508.4159 | 658.4314 | 755.8159 | 539.713 | 620.8384 | 886.776 | 961.7586 | 585.6466 | 747.8883 | 916.1917 | 986.0975 | 1012.0519 | 470.6877 | 563.6263 | 588.3312 | 646.4049 | 693.5519 | 765.834 | 954.0978 | 1035.9955 | 518.9824 | 600.3333 | 675.1781 | 756.8795 | 67.5226 | 0.60386 | 17.496 | 5.9559 | -28.0082 | 3.0952 | 8395.73 | -0.08 | 0.9695 | -1.8716 | -18.8454 | -0.74801 | 7.2226 | -32.7497 | -33.2007 | 70.651 | 86.6572 | 44.0309 | 24.9001 | 6.4944 | 62.1003 | 29.2523
42838.4289 | 743 | 22.8733 | 22.8398 | 22.8318 | 22.7429 | 22.351 | 21.6643 | 22.6824 | 21.7217 | 22.328 | 22.3282 | 22.3025 | 21.9454 | 21.1516 | 22.1325 | 21.5821 | 21.7697 | 21.982 | 21.0657 | 21.3636 | 23.0932 | 21.2623 | 53.9008 | 71.0552 | 22.1448 | 24.3529 | 78.5844 | 601.7864 | 631.5186 | 600.8238 | 22.2271 | 23.681 | 85.7878 | 22.2341 | 24.5049 | 86.0747 | 736.763 | 813.6198 |  | 347.4861 | 900.6893 | 894.8165 | 661.8391 |  | 166.4921 | 304.7193 | 387.7771 | 724.1498 | 804.5461 | 844.7658 | 872.4628 | 36.0698 | 93.1793 | 41.1807 | 215.226 | 24.6413 | 48.208 | 46.6118 | 49.9206 | 25.8862 |  |  | 0.55221 | -1.2394 | -145.6163 | 0.19512 | 8.7562 | -197.8578 | -203.3278 | -5.298 | 7.1184 | 20.1585 | 15.1776 | 0.0057399 | 0.0050401 | 0.00037127 | 22.5414 | 21.9783 | 22.1401 | 22.1858 | 21.9832 | 21.2644 | 20.0726 | 22.1582 | 22.3318 | 22.3588 | 22.3035 | 21.9158 | 21.1364 | 22.2342 | 474.694 | 295.7082 | 290.6164 | 220.2897 | 175.4727 | 502.3978 | 285.9226 | 22.3301 | 22.0965 | 21.7509 | 22.0401 | 21.8661 | 22.9991 | 21.9926 | 26.2927 | 70.2555 | 559.9217 | 500.9815 | 499.0274 | 498.9368 | 38.4876 | 18.8057 | 743.5202 | 21.9092 | 22.1813 | 223.4274 | 21.5364 | 21.9874 | 22.5316 | 31.937 | 88.3224 | 21.9688 | 23.5716 | 86.0502 | 720.0973 | 628.9101 | 734.261 | 739.0256 | 703.1042 |  | 773.4578 | 791.6543 | 834.6557 | 595.0309 | 655.1544 | 801.8982 |  | 822.3295 |  |  | 375.4011 | 570.8506 | 659.4894 | [5 empty] | 21.8528 | 552.7185 | 21.7042 | 22.0693 | 344.9648 | 21.2771 | 21.8725 | 431.5362 | 587.6824 | 590.9596 |  | 968.0277 | 931.0969 | 505.5515 | 657.12 | 756.1494 | 539.3701 | 620.0903 | 881.2607 | 959.7037 | 583.0664 | 744.2361 | 927.203 | 986.4851 | 1012.4627 | 470.4083 | 562.6245 | 587.3731 | 636.8091 | 686.747 | 763.7348 | 950.9849 | 1030.9401 | 517.5571 | 600.1875 | 665.5697 | 751.2421 | 59.355 | 0.57883 | 17.5245 | 5.95 | -27.8888 | 3.0952 | 8324.74 | -0.07 | 1.531 | -1.865 | -20.2156 | 0.74 | 6.8949 | -32.7754 | -33.2254 | 69.9872 | 86.5905 | 43.7762 | 23.5906 | 5.0178 | 61.0631 | 29.0035
42838.4289 | 744 | 22.866 | 22.8365 | 22.8294 | 22.7369 | 22.3471 | 21.6613 | 22.6786 | 21.7154 | 22.3179 | 22.3224 | 22.2934 | 21.9348 | 21.1476 | 22.1149 | 21.5845 | 21.7713 | 21.9851 | 21.0653 | 21.3704 | 23.1076 | 21.2993 | 54.556 | 71.4427 | 22.1456 | 24.3834 | 78.7381 | 600.9894 | 630.9855 | 600.1473 | 22.2212 | 23.6924 | 86.0435 | 22.2435 | 24.5561 | 86.1848 | 734.833 | 824.5269 |  | 350.4336 | 903.098 | 898.4383 | 670.638 |  | 169.4121 | 309.6517 | 391.1382 | 725.3072 | 799.045 | 843.9717 | 869.112 | 36.0783 | 94.3848 | 41.1666 | 217.7444 | 24.7405 | 48.1805 | 46.4095 | 49.8816 | 25.9775 |  |  | 0.32419 | -1.5265 | -144.5761 | 0.4008 | 8.5518 | -197.8526 | -203.2752 | -5.5201 | 6.9909 | 20.5807 | 14.3513 | 0.0056085 | 0.0049497 | 0.00037291 | 22.5422 | 21.9729 | 22.135 | 22.1792 | 21.9836 | 21.2671 | 20.0733 | 22.1544 | 22.3294 | 22.3593 | 22.3013 | 21.9064 | 21.1319 | 22.2312 | 459.725 | 267.6438 | 268.4145 | 212.9534 | 179.0845 | 503.1719 | 286.1388 | 22.325 | 22.0908 | 21.7483 | 22.042 | 21.8588 | 23.0155 | 21.9969 | 26.4402 | 70.4499 | 559.1606 | 501.0191 | 500.1706 | 503.9977 | 32.9287 | 11.9444 | 738.0519 | 21.9011 | 22.1903 | 224.0328 | 21.5324 | 21.9854 | 22.5388 | 32.3377 | 88.3217 | 21.9714 | 23.5932 | 86.2308 | 715.3446 | 628.2807 | 739.4095 | 741.1896 | 701.6489 |  | 771.012 | 784.7529 | 833.0728 | 596.4536 | 653.4474 | 798.1734 |  | 826.1996 |  |  | 372.7734 | 565.0146 | 657.9524 | [5 empty] | 21.8588 | 552.6167 | 21.7086 | 22.0654 | 343.424 | 21.2772 | 21.8745 | 430.8454 | 586.9777 | 590.4032 |  | 964.2786 | 932.5215 | 502.319 | 655.5664 | 757.7202 | 539.12 | 619.3904 | 880.2069 | 958.9902 | 580.8617 | 741.6793 | 932.1924 | 980.7001 | 1008.96 | 470.0337 | 561.4973 | 586.5197 | 627.6433 | 680.7405 | 762.3963 | 949.8587 | 1024.0662 | 516.1449 | 599.9419 | 657.711 | 747.0816 | 60.3145 | 0.5525 | 17.5493 | 5.9432 | -27.9669 | 3.0952 | 8205.86 | -0.08 | 1.1726 | -2.0787 | -20.2291 | 1.0651 | 6.8116 | -32.7633 | -33.2093 | 69.3259 | 86.2512 | 43.3804 | 25.4219 | 7.5173 | 60.3155 | 28.7421
42838.4289 | 745 | 22.8725 | 22.8434 | 22.8268 | 22.7452 | 22.3431 | 21.6623 | 22.6802 | 21.7172 | 22.3268 | 22.3311 | 22.2962 | 21.9376 | 21.1508 | 22.1271 | 21.5795 | 21.7662 | 21.9833 | 21.0607 | 21.3784 | 23.1308 | 21.3306 | 55.2125 | 71.822 | 22.1499 | 24.4165 | 78.885 | 601.3502 | 631.0712 | 600.858 | 22.2206 | 23.7109 | 86.2872 | 22.241 | 24.5978 | 86.2811 | 733.1974 | 842.9683 |  | 352.7819 | 897.7299 | 893.3862 | 667.1368 |  | 173.118 | 315.7087 | 394.6578 | 732.4999 | 798.6279 | 846.0222 | 870.2177 | 36.0611 | 95.7465 | 40.7873 | 220.6738 | 24.8143 | 48.1261 | 46.2051 | 49.8283 | 26.0563 |  |  | 0.00023 | -1.0712 | -140.7616 | -0.21295 | 8.448 | -197.846 | -203.1793 | -4.6002 | 7.0312 | 20.0113 | 14.9877 | 0.0056118 | 0.0048988 | 0.00039263 | 22.5487 | 21.97 | 22.1346 | 22.1794 | 21.9801 | 21.2595 | 20.0708 | 22.1499 | 22.3265 | 22.3589 | 22.3103 | 21.9078 | 21.1321 | 22.2321 | 429.8343 | 242.3346 | 238.3261 | 197.9127 | 181.5095 | 503.087 | 285.8894 | 22.3343 | 22.0912 | 21.7473 | 22.0405 | 21.8615 | 23.0383 | 21.9994 | 26.5959 | 70.6166 | 558.2761 | 499.4569 | 499.2206 | 502.7804 | 36.3482 | 12.8906 | 735.1904 | 21.903 | 22.1772 | 223.4698 | 21.5314 | 21.9945 | 22.5434 | 32.7727 | 88.3218 | 21.9747 | 23.6252 | 86.4111 | 711.0916 | 627.5645 | 740.4432 | 741.9812 | 696.6098 |  | 768.6307 | 781.5947 | 831.8664 | 600.5225 | 652.334 | 795.4051 |  | 829.2729 |  |  | 369.8309 | 558.7282 | 654.6094 | [5 empty] | 21.8612 | 554.1722 | 21.7024 | 22.0654 | 342.1708 | 21.2782 | 21.8754 | 430.2591 | 586.2083 | 589.7499 |  | 959.4601 | 933.3865 | 499.1206 | 653.3163 | 761.2949 | 538.7548 | 618.5567 | 878.3015 | 957.9427 | 578.2892 | 741.8362 | 938.7082 | 982.111 | 1006.0224 | 469.2561 | 560.9605 | 586.0032 | 618.975 | 675.345 | 765.1234 | 949.0146 | 1021.6593 | 515.6968 | 599.1352 | 650.4867 | 744.759 | 59.2695 | 0.53059 | 17.5738 | 5.9322 | -27.9019 | 3.0952 | 8092.77 | -0.16 | 0.031246 | -1.7503 | -20.0639 | -0.78039 | 6.7763 | -32.7928 | -33.2319 | 68.787 | 85.9356 | 43.0359 | 28.7247 | 10.8228 | 59.9884 | 28.6358
42838.4289 | 746 | 22.8701 | 22.8408 | 22.8289 | 22.7359 | 22.3417 | 21.6604 | 22.6687 | 21.7179 | 22.3228 | 22.3301 | 22.2992 | 21.934 | 21.1512 | 22.1242 | 21.5822 | 21.7656 | 21.984 | 21.0699 | 21.3788 | 23.1501 | 21.3707 | 55.8669 | 72.1964 | 22.1487 | 24.4586 | 79.0327 | 603.0213 | 630.2073 | 602.5703 | 22.2249 | 23.7336 | 86.5572 | 22.2441 | 24.6439 | 86.39 | 731.3126 | 838.7301 |  | 354.7815 | 890.1581 | 885.7813 | 660.0651 |  | 176.4692 | 320.8218 | 396.8451 | 731.2681 | 797.3905 | 848.9768 | 872.7981 | 35.9001 | 96.8577 | 40.6163 | 223.2507 | 24.9092 | 48.0846 | 46.006 | 49.7844 | 26.1319 |  |  | -0.062194 | -1.3104 | -154.6464 | 0.057126 | 8.8416 | -197.8617 | -203.289 | -5.2106 | 6.7358 | 19.5199 | 14.2409 | 0.0054918 | 0.0048758 | 0.00038934 | 22.5575 | 21.9797 | 22.1353 | 22.1863 | 21.9756 | 21.2669 | 20.0745 | 22.1486 | 22.3256 | 22.3627 | 22.3078 | 21.9078 | 21.131 | 22.2307 | 427.5942 | 236.4038 | 231.0406 | 192.2897 | 175.5 | 502.9919 | 285.5333 | 22.3312 | 22.0872 | 21.7501 | 22.0411 | 21.8727 | 23.0606 | 22.0013 | 26.7439 | 70.7915 | 557.119 | 497.4917 | 497.4673 | 498.2985 | 33.7488 | 21.2227 | 733.4884 | 21.908 | 22.1894 | 224.2274 | 21.5376 | 21.9974 | 22.5585 | 33.242 | 88.3287 | 21.9764 | 23.6679 | 86.5876 | 706.4752 | 626.5057 | 737.7924 | 741.951 | 696.7299 |  | 766.5107 | 776.3734 | 830.3293 | 601.3755 | 651.2535 | 789.6084 |  | 831.7969 |  |  | 368.1378 | 554.5922 | 653.8509 | [5 empty] | 21.8499 | 555.3774 | 21.7079 | 22.0637 | 341.1007 | 21.2798 | 21.8745 | 429.3783 | 585.1544 | 589.0626 |  | 947.1222 | 932.816 | 496.1547 | 650.6848 | 764.4492 | 537.9547 | 617.013 | 871.346 | 951.959 | 575.242 | 740.9064 | 940.2778 | 979.5201 | 1005.0543 | 468.704 | 560.9155 | 585.9919 | 610.3716 | 669.4697 | 766.7704 | 938.5327 | 1016.1181 | 515.2074 | 598.6009 | 643.0735 | 741.8587 | 56.5753 | 0.50622 | 17.5959 | 5.9266 | -27.9108 | 3.0952 | 7952.77 | -0.07 | -0.51431 | -1.9442 | -21.1213 | 0.40594 | 6.9415 | -32.8374 | -33.2847 | 68.1828 | 85.5685 | 42.7883 | 28.9529 | 11.5787 | 59.698 | 28.5777
42838.4289 | 747 | 22.8721 | 22.8458 | 22.8241 | 22.7352 | 22.3446 | 21.6565 | 22.6702 | 21.7154 | 22.3232 | 22.326 | 22.2947 | 21.9324 | 21.1504 | 22.127 | 21.5801 | 21.7639 | 21.9873 | 21.0733 | 21.3796 | 23.1672 | 21.3994 | 56.5156 | 72.5519 | 22.1517 | 24.5038 | 79.1849 | 602.2447 | 628.9058 | 601.3753 | 22.2277 | 23.7533 | 86.8226 | 22.2516 | 24.6972 | 86.495 | 729.2499 | 828.8843 |  | 356.8896 | 882.073 | 878.1123 | 657.868 |  | 179.7725 | 326.7005 | 399.6744 | 724.4054 | 786.0838 | 846.9265 | 875.9788 | 35.4843 | 98.0233 | 41.1057 | 226.1162 | 24.9579 | 48.0383 | 45.8203 | 49.7581 | 26.2111 |  |  | 0.11588 | -1.0758 | -158.4787 | -0.19849 | 8.8456 | -197.8309 | -203.1536 | -4.7572 | 6.6229 | 19.7094 | 14.8391 | 0.0055116 | 0.0048594 | 0.00037949 | 22.5703 | 21.9846 | 22.1431 | 22.1976 | 22.0009 | 21.2731 | 20.0872 | 22.1611 | 22.3398 | 22.3734 | 22.3181 | 21.925 | 21.1493 | 22.234 | 416.6645 | 249.5959 | 246.1019 | 205.0183 | 172.9788 | 502.542 | 285.2786 | 22.3262 | 22.0912 | 21.7436 | 22.036 | 21.8681 | 23.0847 | 22.0071 | 26.8792 | 70.9431 | 555.9259 | 496.0102 | 496.0945 | 495.4531 | 34.3486 | 14.7419 | 730.0659 | 21.9033 | 22.183 | 225.8378 | 21.5374 | 21.993 | 22.5623 | 33.7272 | 88.3184 | 21.9749 | 23.6949 | 86.747 | 701.2989 | 625.9606 | 737.3611 | 743.4074 | 689.8412 |  | 763.6962 | 772.2598 | 828.2961 | 603.0423 | 650.144 | 783.1756 |  | 821.9167 |  |  | 366.6314 | 550.8517 | 650.9675 | [5 empty] | 21.8637 | 556.5811 | 21.7168 | 22.0697 | 340.0919 | 21.2765 | 21.8725 | 428.6634 | 583.8721 | 588.7105 |  | 932.7268 | 928.7281 | 493.0779 | 648.1864 | 764.8134 | 537.478 | 615.6982 | 858.7086 | 947.0317 | 572.4069 | 739.0997 | 937.7331 | 972.1314 | 1002.3982 | 468.0969 | 560.3416 | 586.1043 | 602.127 | 663.5029 | 765.1207 | 930.1983 | 1009.7213 | 514.6055 | 598.9368 | 635.5873 | 737.5028 | 57.1283 | 0.48206 | 17.6177 | 5.9254 | -27.973 | 3.0952 | 7795.04 | -0.06 | 0.70155 | -1.7703 | -21.4869 | -0.76044 | 6.9367 | -32.8048 | -33.2432 | 67.5816 | 85.0084 | 42.5127 | 30.0697 | 9.8668 | 59.2291 | 28.469
42838.4289 | 748 | 22.8673 | 22.8345 | 22.8173 | 22.7336 | 22.3431 | 21.6522 | 22.6717 | 21.7157 | 22.3175 | 22.3163 | 22.2878 | 21.9325 | 21.1437 | 22.118 | 21.5841 | 21.7749 | 22.0005 | 21.0737 | 21.3888 | 23.1851 | 21.449 | 57.1769 | 72.9056 | 22.1569 | 24.5531 | 79.355 | 600.3799 | 627.6852 | 599.5481 | 22.2303 | 23.7792 | 87.0774 | 22.2591 | 24.7531 | 86.5899 | 727.2705 | 825.8131 |  | 361.7313 | 871.8111 | 868.7555 | 658.7262 |  | 182.6058 | 331.6479 | 401.6424 | 712.4403 | 774.2141 | 843.3429 | 876.551 | 35.1617 | 99.1058 | 42.0812 | 228.6984 | 25.0382 | 48.0021 | 45.6365 | 49.7322 | 26.2958 |  |  | 0.3393 | -1.3984 | -137.0029 | 0.022298 | 8.8725 | -197.8808 | -203.241 | -4.9366 | 7.0717 | 19.8247 | 14.6823 | 0.0052388 | 0.0047214 | 0.00037949 | 22.5676 | 21.9838 | 22.141 | 22.1943 | 21.9945 | 21.2637 | 20.0764 | 22.1612 | 22.3382 | 22.3602 | 22.3104 | 21.922 | 21.1436 | 22.2356 | 408.5794 | 246.4509 | 240.2217 | 204.4556 | 170.2192 | 502.0352 | 284.7575 | 22.3229 | 22.0885 | 21.7506 | 22.043 | 21.864 | 23.1089 | 22.0035 | 27.0398 | 71.1288 | 554.8365 | 494.8009 | 495.4408 | 496.4174 | 38.1042 | 19.9977 | 727.7915 | 21.8988 | 22.1813 | 226.8306 | 21.5294 | 21.9865 | 22.5707 | 34.2464 | 88.3191 | 21.9689 | 23.7137 | 86.8865 | 697.7953 | 624.7706 | 737.0899 | 745.8005 | 685.943 |  | 761.1706 | 767.2186 | 826.2319 | 601.8653 | 649.2082 | 778.099 |  | 615.2072 |  |  | 362.7946 | 548.0838 | 647.2774 | [5 empty] | 21.8512 | 556.6884 | 21.7074 | 22.067 | 339.9652 | 21.2727 | 21.8734 | 428.8617 | 582.7793 | 588.7279 |  | 921.6141 | 928.2629 | 490.711 | 646.349 | 765.8443 | 537.4195 | 615.4024 | 851.0053 | 941.5917 | 569.7385 | 738.2614 | 939.3955 | 970.2725 | 1001.4996 | 467.5686 | 559.7265 | 585.6376 | 594.8015 | 657.909 | 763.491 | 922.3746 | 1006.3715 | 514.1096 | 598.3591 | 629.3838 | 734.1171 | 57.0886 | 0.46111 | 17.6394 | 5.9283 | -28.0277 | 3.0953 | 7651.1 | -0.12 | 1.1992 | -2.0267 | -20.0603 | 0.25592 | 6.9361 | -32.7564 | -33.1971 | 66.9835 | 84.4673 | 42.3526 | 30.8581 | 10.4417 | 58.6994 | 28.2715
42838.4289 | 749 | 22.8629 | 22.8314 | 22.8251 | 22.7337 | 22.3375 | 21.6573 | 22.675 | 21.7089 | 22.3215 | 22.3219 | 22.2863 | 21.9337 | 21.1501 | 22.1216 | 21.5896 | 21.7741 | 21.9928 | 21.0688 | 21.3921 | 23.2155 | 21.496 | 57.8077 | 73.2366 | 22.17 | 24.583 | 79.5227 | 599.7736 | 626.0408 | 598.8038 | 22.2187 | 23.8001 | 87.303 | 22.2506 | 24.7932 | 86.6638 | 725.4112 | 827.645 |  | 367.7639 | 862.8719 | 860.1657 | 656.8194 |  | 185.1931 | 335.9651 | 404.3015 | 707.3591 | 767.8746 | 842.65 | 876.2239 | 34.8774 | 100.2048 | 42.9856 | 231.1491 | 25.1764 | 47.9397 | 45.4557 | 49.7026 | 26.3722 |  |  | 0.065942 | -1.0258 | -148.3355 | -0.27012 | 8.8429 | -197.8342 | -203.2883 | -4.6725 | 7.0133 | 19.475 | 14.3291 | 0.0053161 | 0.0048019 | 0.0003992 | 22.5674 | 21.9832 | 22.1346 | 22.1846 | 21.981 | 21.2589 | 20.077 | 22.1586 | 22.3297 | 22.3556 | 22.3111 | 21.9096 | 21.1441 | 22.2285 | 403.38 | 268.0277 | 255.081 | 202.6063 | 172.5575 | 502.0837 | 284.3934 | 22.3205 | 22.0832 | 21.7486 | 22.0379 | 21.8646 | 23.1315 | 22.0096 | 27.1934 | 71.2806 | 553.7111 | 493.4836 | 493.8082 | 492.5306 | 36.8094 | 17.716 | 724.0375 | 21.9107 | 22.181 | 226.9271 | 21.5406 | 21.9945 | 22.585 | 34.8054 | 88.3095 | 21.9705 | 23.7645 | 87.05 | 693.4226 | 624.2986 | 735.8944 | 747.0347 | 683.8534 |  | 758.9382 | 763.1403 | 824.0711 | 599.6275 | 648.124 | 773.5884 |  | 338.4278 |  |  | 359.7173 | 545.9088 | 645.9501 | [5 empty] | 21.8548 | 555.9607 | 21.7099 | 22.0662 | 337.77 | 21.2726 | 21.874 | 430.04 | 581.9088 | 588.0388 |  | 916.5892 | 925.6796 | 488.1021 | 643.5552 | 766.2239 | 537.3779 | 614.1706 | 845.7053 | 942.4387 | 567.487 | 734.9735 | 935.5426 | 964.9701 | 1000.3086 | 466.9187 | 559.0784 | 585.1591 | 587.7378 | 653.3831 | 762.5803 | 915.7436 | 1001.2768 | 514.1485 | 598.4794 | 623.223 | 731.623 | 60.6422 | 0.43863 | 17.6578 | 5.9433 | -27.9575 | 3.0953 | 7483.27 | -0.17 | 0.52844 | -1.742 | -20.9478 | -0.89391 | 6.9224 | -32.7424 | -33.1907 | 66.4211 | 83.8713 | 42.1921 | 31.4463 | 8.7359 | 58.2797 | 28.2036
42838.429 | 750 | 22.8565 | 22.8201 | 22.826 | 22.732 | 22.3327 | 21.653 | 22.665 | 21.7098 | 22.3122 | 22.3167 | 22.292 | 21.9306 | 21.1428 | 22.1166 | 21.5867 | 21.7687 | 22.002 | 21.0671 | 21.394 | 23.2265 | 21.5259 | 58.3996 | 73.5284 | 22.1656 | 24.622 | 79.6668 | 599.1875 | 625.6381 | 598.4069 | 22.2266 | 23.8321 | 87.5395 | 22.2552 | 24.8453 | 86.7491 | 723.2645 | 838.7378 |  | 370.9217 | 861.4271 | 858.9438 | 654.6251 |  | 188.2798 | 341.2395 | 407.9034 | 705.8137 | 761.3106 | 842.0207 | 876.5796 | 34.488 | 101.4274 | 43.676 | 233.8183 | 25.2757 | 47.8541 | 45.2826 | 49.6788 | 26.4499 |  |  | 0.26176 | -1.0331 | -156.7623 | -0.26223 | 8.4237 | -197.8677 | -203.3639 | -5.116 | 6.6151 | 18.7342 | 13.8864 | 0.0052011 | 0.004608 | 0.00037456 | 22.5736 | 21.9783 | 22.1255 | 22.1838 | 21.9875 | 21.2597 | 20.0792 | 22.1577 | 22.3324 | 22.3587 | 22.3128 | 21.906 | 21.1304 | 22.2332 | 395.5673 | 271.0364 | 248.7178 | 198.6584 | 172.492 | 502.0115 | 283.94 | 22.3171 | 22.0762 | 21.7517 | 22.0333 | 21.8633 | 23.1598 | 22.0075 | 27.3482 | 71.4295 | 552.5164 | 492.0728 | 492.4612 | 491.3501 | 37.5388 | 16.5041 | 721.2303 | 21.9103 | 22.187 | 227.1582 | 21.5392 | 21.9977 | 22.5886 | 35.3904 | 88.2985 | 21.9743 | 23.8055 | 87.2135 | 694.2679 | 623.9412 | 736.8316 | 751.6736 | 683.6283 |  | 756.5906 | 761.8418 | 821.9853 | 599.2051 | 647.0274 | 771.4569 |  | 341.0779 |  |  | 356.7167 | 544.1564 | 645.3714 | [5 empty] | 21.8529 | 555.6401 | 21.7065 | 22.0695 | 335.4008 | 21.2767 | 21.8671 | 430.1976 | 581.4557 | 587.5724 |  | 918.1716 | 925.5872 | 485.5348 | 641.2706 | 766.7492 | 537.9708 | 613.1036 | 844.6336 | 946.591 | 565.3177 | 735.2246 | 932.5366 | 965.1363 | 1000.1371 | 466.3647 | 558.7742 | 584.8987 | 581.3034 | 649.5677 | 763.37 | 908.0026 | 996.7936 | 513.8059 | 598.4106 | 617.7038 | 728.982 | 61.8535 | 0.42605 | 17.674 | 5.9573 | -27.9938 | 3.0952 | 7381.92 | -0.16 | 1.0526 | -1.7557 | -21.6277 | -0.88457 | 6.7544 | -32.736 | -33.1875 | 65.7788 | 83.2263 | 41.9792 | 32.2987 | 9.3747 | 57.7978 | 28.0503
42838.429 | 751 | 22.8715 | 22.8499 | 22.8325 | 22.7422 | 22.3552 | 21.6779 | 22.6862 | 21.7264 | 22.3301 | 22.3338 | 22.2995 | 21.9367 | 21.1579 | 22.1312 | 21.5803 | 21.7733 | 21.992 | 21.0655 | 21.3998 | 23.2463 | 21.5626 | 58.9637 | 73.8242 | 22.1626 | 24.6571 | 79.7952 | 598.7193 | 626.4052 | 598.0838 | 22.225 | 23.8745 | 87.7568 | 22.2564 | 24.9025 | 86.8381 | 721.4197 | 852.2969 |  | 373.0199 | 859.9136 | 857.3834 | 656.7698 |  | 190.7206 | 345.7538 | 411.0204 | 708.6783 | 764.443 | 845.8883 | 878.8357 | 34.0904 | 102.4135 | 43.8965 | 235.871 | 25.3558 | 47.7511 | 45.1179 | 49.6382 | 26.5329 |  |  | -0.002398 | -0.57241 | -136.7913 | 0.025582 | 8.9021 | -197.773 | -203.2069 | -4.9787 | 6.258 | 18.8143 | 13.0887 | 0.0049284 | 0.0045587 | 0.00039591 | 22.583 | 21.9806 | 22.1368 | 22.1896 | 21.9998 | 21.2678 | 20.081 | 22.1638 | 22.3373 | 22.3712 | 22.3155 | 21.9146 | 21.1391 | 22.2334 | 391.7468 | 256.2898 | 249.507 | 197.2813 | 175.1794 | 501.4512 | 283.4421 | 22.3233 | 22.0834 | 21.7531 | 22.0365 | 21.8665 | 23.1889 | 22.0088 | 27.5167 | 71.5864 | 551.5035 | 491.2144 | 491.8504 | 490.8064 | 29.5002 | 16.7333 | 719.6393 | 21.9094 | 22.1773 | 226.7198 | 21.5366 | 21.9901 | 22.6001 | 36.0107 | 88.3137 | 21.969 | 23.8459 | 87.3621 | 695.1374 | 622.9517 | 736.6621 | 754.1987 | 688.9589 |  | 754.679 | 765.6301 | 820.2815 | 596.8248 | 645.8795 | 772.6477 |  | 343.7311 |  |  | 354.1912 | 542.6926 | 647.0577 | [5 empty] | 21.8614 | 554.4571 | 21.7144 | 22.0631 | 333.6486 | 21.2789 | 21.8727 | 430.6282 | 581.3172 | 587.5236 |  | 917.3459 | 926.2023 | 483.6485 | 639.6886 | 769.731 | 538.326 | 613.2301 | 837.6664 | 945.1007 | 563.7821 | 733.8078 | 934.3438 | 962.6529 | 996.5751 | 465.8572 | 558.2102 | 584.5253 | 575.2195 | 646.7824 | 765.9473 | 902.4918 | 993.4227 | 513.2286 | 598.1675 | 612.7036 | 727.7718 | 61.2822 | 0.40333 | 17.6889 | 5.9752 | -28.0137 | 3.0953 | 7266.65 | -0.11 | -0.10073 | -1.3117 | -20.2772 | 0.2773 | 6.9556 | -32.7848 | -33.2322 | 65.1056 | 82.5674 | 41.811 | 32.6019 | 9.2122 | 57.2742 | 27.9082
42838.429 | 752 | 22.875 | 22.847 | 22.8336 | 22.7456 | 22.3572 | 21.677 | 22.6851 | 21.7328 | 22.3223 | 22.3267 | 22.3035 | 21.943 | 21.1548 | 22.1335 | 21.5828 | 21.7715 | 21.9903 | 21.0609 | 21.3958 | 23.2681 | 21.5906 | 59.5266 | 74.1017 | 22.16 | 24.6966 | 79.9399 | 599.6136 | 627.4265 | 599.3487 | 22.2282 | 23.9041 | 87.9645 | 22.2625 | 24.956 | 86.9233 | 719.875 | 855.5605 |  | 374.8818 | 861.0843 | 859.3441 | 663.7985 |  | 193.605 | 351.2093 | 413.6938 | 717.5975 | 770.0301 | 849.0801 | 878.6022 | 33.4896 | 103.4898 | 43.4208 | 238.0299 | 25.4391 | 47.6517 | 44.9584 | 49.5856 | 26.6102 |  |  | 0.18751 | -0.5481 | -130.8148 | -0.16695 | 8.4368 | -197.8545 | -203.3278 | -4.9898 | 6.2236 | 18.3077 | 13.597 | 0.0050089 | 0.004516 | 0.00038441 | 22.5867 | 21.973 | 22.136 | 22.1902 | 21.9937 | 21.2685 | 20.0808 | 22.1639 | 22.3296 | 22.3653 | 22.3149 | 21.9096 | 21.1339 | 22.227 | 389.4351 | 244.1211 | 251.1304 | 198.7138 | 175.7217 | 500.2687 | 282.8418 | 22.3263 | 22.0854 | 21.7521 | 22.0391 | 21.8699 | 23.2136 | 22.019 | 27.7 | 71.7413 | 550.4511 | 490.435 | 490.9224 | 489.3031 | 26.8599 | 12.4583 | 719.8436 | 21.9138 | 22.189 | 225.9557 | 21.5378 | 21.9962 | 22.6071 | 36.6532 | 88.3149 | 21.9834 | 23.8825 | 87.4993 | 695.9095 | 621.9934 | 735.5486 | 754.6326 | 692.891 |  | 753.1171 | 764.5847 | 818.6159 | 593.6066 | 644.7876 | 772.1543 |  | 346.1601 |  |  | 352.8661 | 542.3166 | 648.4236 | [5 empty] | 21.8498 | 553.1155 | 21.7015 | 22.058 | 331.3368 | 21.2658 | 21.8638 | 430.3567 | 581.1944 | 588.2129 |  | 910.1723 | 924.9916 | 481.3379 | 638.1326 | 768.1678 | 538.3683 | 614.0279 | 831.2116 | 944.5209 | 562.4595 | 732.5186 | 935.6459 | 958.8997 | 994.6195 | 465.5798 | 557.1985 | 584.1864 | 568.9011 | 644.803 | 767.7748 | 897.6492 | 990.8235 | 513.2086 | 597.4923 | 608.0683 | 727.4553 | 62.6842 | 0.37933 | 17.7022 | 6.0091 | -27.9868 | 3.0953 | 7184.37 | -0.02 | 0.89138 | -1.2892 | -19.9165 | -0.7115 | 6.7811 | -32.8383 | -33.2894 | 64.5692 | 82.0575 | 41.6782 | 32.603 | 8.9417 | 56.6922 | 27.7872
42838.429 | 753 | 22.8658 | 22.8432 | 22.8205 | 22.744 | 22.3549 | 21.6742 | 22.6805 | 21.7248 | 22.3197 | 22.3227 | 22.2911 | 21.9358 | 21.15 | 22.127 | 21.5843 | 21.7671 | 21.9903 | 21.0638 | 21.4067 | 23.2918 | 21.6393 | 60.0728 | 74.3668 | 22.1744 | 24.7421 | 80.108 | 601.3106 | 627.9223 | 601.1421 | 22.2197 | 23.9269 | 88.1607 | 22.2491 | 24.9978 | 86.9973 | 718.5493 | 840.5035 |  | 376.7454 | 862.3779 | 861.0566 | 666.706 |  | 196.1854 | 356.1442 | 415.8445 | 723.514 | 772.0691 | 846.2388 | 876.5451 | 33.2859 | 104.4126 | 42.9071 | 239.9873 | 25.5221 | 47.5461 | 44.7855 | 49.5252 | 26.6738 |  |  | 0.21313 | -0.68872 | -134.2607 | 0.020326 | 8.3981 | -197.8282 | -203.2404 | -4.7671 | 6.4299 | 18.8018 | 14.3582 | 0.0048824 | 0.0044815 | 0.00036963 | 22.5874 | 21.9941 | 22.1392 | 22.1893 | 21.9881 | 21.2656 | 20.0793 | 22.1693 | 22.3333 | 22.3756 | 22.3192 | 21.9115 | 21.1454 | 22.2381 | 371.6631 | 223.6253 | 232.9211 | 189.1057 | 177.6224 | 498.7626 | 281.9595 | 22.3161 | 22.0769 | 21.7571 | 22.0357 | 21.8728 | 23.2445 | 22.0166 | 27.9061 | 71.8893 | 549.2416 | 488.8778 | 489.2239 | 487.7475 | 29.8752 | 13.5016 | 719.196 | 21.902 | 22.1895 | 226.3457 | 21.5442 | 21.9931 | 22.612 | 37.3069 | 88.3083 | 21.9709 | 23.9235 | 87.6203 | 698.5527 | 619.614 | 737.7666 | 757.5488 | 693.8351 |  | 751.5162 | 771.0176 | 817.7281 | 587.4497 | 643.3207 | 772.9633 |  | 348.6208 |  |  | 352.4133 | 543.5513 | 648.2934 | [5 empty] | 21.8453 | 549.7032 | 21.7098 | 22.0581 | 329.4412 | 21.2708 | 21.8687 | 429.5688 | 581.2035 | 589.8995 |  | 906.5236 | 922.9922 | 479.2986 | 636.8848 | 766.4791 | 538.2584 | 614.8781 | 821.0066 | 942.5483 | 561.2555 | 730.7058 | 927.8256 | 955.2286 | 994.2458 | 465.3202 | 556.9067 | 584.3474 | 562.8094 | 642.5331 | 768.6153 | 891.8537 | 987.9533 | 513.39 | 597.2688 | 604.1931 | 728.3972 | 55.336 | 0.35525 | 17.7178 | 6.0374 | -27.8728 | 3.0953 | 7113.19 | -0.12 | 0.95131 | -1.4508 | -20.2567 | 0.24924 | 6.7569 | -32.7945 | -33.2401 | 64.107 | 81.5924 | 41.5517 | 34.2527 | 10.8326 | 56.2808 | 27.6439
42838.429 | 754 | 22.8612 | 22.8369 | 22.8229 | 22.734 | 22.3403 | 21.6692 | 22.6707 | 21.7153 | 22.3173 | 22.3165 | 22.287 | 21.9303 | 21.1444 | 22.1157 | 21.5805 | 21.77 | 21.991 | 21.0646 | 21.41 | 23.313 | 21.6878 | 60.6043 | 74.6208 | 22.175 | 24.7848 | 80.2358 | 603.5584 | 628.9799 | 603.5885 | 22.222 | 23.9659 | 88.3323 | 22.2531 | 25.0492 | 87.0747 | 717.3203 | 842.0346 |  | 378.4839 | 858.9138 | 858.6465 | 666.4342 |  | 198.2509 | 360.3086 | 417.5686 | 724.1184 | 768.0193 | 841.5678 | 877.7266 | 33.1441 | 105.3424 | 42.5614 | 241.8494 | 25.6246 | 47.4398 | 44.627 | 49.4629 | 26.7471 |  |  | -0.020798 | -0.20837 | -136.5836 | -0.25369 | 8.9303 | -197.8243 | -203.2726 | -4.476 | 6.2837 | 18.1468 | 14.0591 | 0.0047247 | 0.0043008 | 0.00039098 | 22.5886 | 21.9836 | 22.1333 | 22.1843 | 21.9885 | 21.2607 | 20.0779 | 22.1485 | 22.3283 | 22.3597 | 22.3097 | 21.9077 | 21.1362 | 22.2273 | 356.7851 | 228.9166 | 234.1182 | 181.6995 | 162.1016 | 497.5738 | 281.2557 | 22.3328 | 22.0918 | 21.7636 | 22.0399 | 21.8797 | 23.2788 | 22.0308 | 28.1042 | 72.0367 | 548.3141 | 488.7157 | 489.5105 | 490.2746 | 28.4463 | 21.1695 | 724.0637 | 21.9035 | 22.1812 | 227.5645 | 21.5345 | 21.9876 | 22.6229 | 37.9882 | 88.3008 | 21.9657 | 23.9628 | 87.7367 | 696.7225 | 617.3739 | 737.7863 | 759.8719 | 689.8674 |  | 749.5855 | 771.6204 | 816.4686 | 583.9688 | 641.5641 | 771.9972 |  | 351.2515 |  |  | 352.2422 | 543.5771 | 647.5691 | [5 empty] | 21.8529 | 546.6476 | 21.7126 | 22.0623 | 328.906 | 21.2724 | 21.8734 | 428.7128 | 581.1903 | 590.9964 |  | 900.3693 | 916.9215 | 477.4444 | 636.1902 | 764.186 | 537.8057 | 614.177 | 811.8639 | 938.4257 | 560.6255 | 730.7801 | 922.1641 | 951.0154 | 990.5315 | 464.8223 | 557.2668 | 585.1159 | 557.2147 | 640.2836 | 771.2043 | 886.8258 | 984.0094 | 513.5357 | 597.9336 | 600.4089 | 730.1362 | 54.044 | 0.33443 | 17.7327 | 6.0635 | -28.0743 | 3.0953 | 7030.96 | -0.08 | -0.29759 | -0.80066 | -20.4987 | -0.88344 | 6.9532 | -32.7257 | -33.1733 | 63.6938 | 81.1705 | 41.2939 | 35.65 | 10.5942 | 55.9829 | 27.4311
42838.429 | 755 | 22.8649 | 22.8379 | 22.8316 | 22.7405 | 22.3413 | 21.6638 | 22.6669 | 21.7131 | 22.3221 | 22.3211 | 22.2904 | 21.9301 | 21.1505 | 22.1177 | 21.5733 | 21.77 | 21.9927 | 21.0615 | 21.4154 | 23.3405 | 21.73 | 61.1228 | 74.8756 | 22.175 | 24.8325 | 80.3433 | 606.2824 | 630.2481 | 606.4629 | 22.2374 | 24.0111 | 88.5025 | 22.2694 | 25.116 | 87.1454 | 716.2936 | 852.9343 |  | 376.187 | 856.4833 | 857.2055 | 667.0262 |  | 200.4409 | 364.2481 | 418.2062 | 720.1663 | 759.946 | 836.5374 | 878.9323 | 33.0384 | 106.4 | 41.5255 | 243.9525 | 25.7193 | 47.3366 | 44.4815 | 49.3934 | 26.8194 |  |  | 0.19934 | -0.10849 | -140.9009 | -0.22741 | 8.2272 | -197.8591 | -203.2785 | -4.2085 | 6.2935 | 18.4757 | 13.756 | 0.0051666 | 0.0044552 | 0.00036634 | 22.5989 | 21.9894 | 22.1385 | 22.1925 | 21.9948 | 21.2651 | 20.0839 | 22.1595 | 22.3378 | 22.3653 | 22.3133 | 21.9196 | 21.1388 | 22.2392 | 349.0168 | 243.1431 | 255.4562 | 190.8385 | 160.2885 | 496.1726 | 280.7386 | 22.3291 | 22.09 | 21.7592 | 22.0438 | 21.8848 | 23.31 | 22.0331 | 28.3219 | 72.1732 | 547.4011 | 489.1869 | 489.7906 | 490.7184 | 35.896 | 21.217 | 724.3838 | 21.898 | 22.1787 | 230.1709 | 21.5255 | 21.9853 | 22.6307 | 38.7081 | 88.3024 | 21.9655 | 24.0093 | 87.8374 | 695.829 | 616.006 | 737.1304 | 760.3455 | 683.0825 |  | 747.5755 | 765.0087 | 814.7446 | 582.1614 | 640.1152 | 768.28 |  | 353.4922 |  |  | 350.5291 | 540.3747 | 644.5408 | [5 empty] | 21.8552 | 544.8819 | 21.715 | 22.0699 | 328.8451 | 21.2768 | 21.8698 | 427.5792 | 580.8275 | 591.2711 |  | 894.2386 | 912.9855 | 475.7377 | 636.1332 | 764.4568 | 537.3977 | 614.3055 | 801.5445 | 935.9296 | 560.3417 | 731.3796 | 915.7676 | 948.3691 | 985.9753 | 464.2253 | 557.9062 | 586.2801 | 552.0404 | 637.7991 | 772.9447 | 882.9367 | 980.1386 | 513.8334 | 598.9776 | 596.3226 | 731.9933 | 57.7664 | 0.31165 | 17.7492 | 6.0721 | -28.0199 | 3.0953 | 6858.65 | -0.04 | 0.9228 | -0.57952 | -20.8847 | -0.83902 | 6.6588 | -32.6547 | -33.0989 | 63.3402 | 80.8016 | 41.0529 | 36.2124 | 8.1459 | 55.712 | 27.2788
42838.429 | 756 | 22.8721 | 22.8439 | 22.8288 | 22.7412 | 22.3432 | 21.664 | 22.6743 | 21.7194 | 22.3192 | 22.3328 | 22.2897 | 21.9468 | 21.1528 | 22.1301 | 21.5724 | 21.7687 | 21.9932 | 21.0574 | 21.4179 | 23.3631 | 21.865 | 61.584 | 75.1116 | 22.1708 | 24.8767 | 80.4533 | 609.3057 | 632.6984 | 609.5952 | 22.2347 | 24.0464 | 88.6656 | 22.27 | 25.1719 | 87.2205 | 715.89 | 861.4881 |  | 718.5588 | 856.457 | 857.0948 | 667.3235 |  | 202.308 | 367.0774 | 418.7193 | 717.6259 | 758.5665 | 833.6755 | 877.1673 | 32.8934 | 107.3302 | 40.7376 | 245.6996 | 25.8133 | 47.2288 | 44.3381 | 49.3302 | 26.8914 |  |  | -0.11148 | -0.3214 | -128.6411 | -0.55925 | 8.8535 | -197.8282 | -203.1247 | -5.2146 | 6.4774 | 18.3664 | 13.4861 | 0.0058319 | 0.0046606 | 0.00034499 | 22.6019 | 21.9833 | 22.1391 | 22.1847 | 21.9884 | 21.2648 | 20.0704 | 22.1479 | 22.3274 | 22.3671 | 22.3122 | 21.9048 | 21.1307 | 22.2376 | 346.8058 | 285.222 | 275.2217 | 193.4027 | 163.9669 | 495.0685 | 280.344 | 22.3236 | 22.0859 | 21.7601 | 22.0455 | 21.8805 | 23.3429 | 22.0362 | 28.5445 | 72.3095 | 546.5387 | 489.2436 | 489.4975 | 490.981 | 30.2912 | 12.3592 | 721.5614 | 21.9087 | 22.179 | 230.7103 | 21.5335 | 21.9885 | 22.6205 | 39.4624 | 88.3058 | 21.9706 | 24.0416 | 87.955 | 694.9262 | 614.8034 | 735.7568 | 757.7165 | 683.2038 |  | 745.7173 | 766.341 | 813.3611 | 584.5981 | 638.9331 | 767.1295 |  | 355.7571 |  |  | 348.8735 | 536.6997 | 642.3798 | [5 empty] | 21.8543 | 544.7825 | 21.7094 | 22.0615 | 328.4643 | 21.2785 | 21.8655 | 427.1572 | 580.4882 | 592.0101 |  | 891.1459 | 912.7558 | 474.4671 | 635.8331 | 766.8404 | 537.2024 | 615.5597 | 792.8333 | 938.4811 | 559.8133 | 731.3865 | 913.3806 | 947.2411 | 981.9948 | 463.7522 | 559.0695 | 587.5128 | 547.3757 | 635.8778 | 777.1387 | 879.879 | 977.3329 | 514.2777 | 599.8858 | 592.7471 | 733.7186 | 58.3305 | 0.29023 | 17.7653 | 6.0715 | -28.0074 | 3.0953 | 6719.18 | -0.05 | -0.69132 | -0.99967 | -19.9997 | -1.3187 | 6.8986 | -32.61 | -33.0436 | 62.8382 | 80.323 | 40.7485 | 36.2216 | 5.8907 | 55.6039 | 27.1397
42838.429 | 757 | 22.8722 | 22.8405 | 22.8318 | 22.7473 | 22.3486 | 21.6712 | 22.6734 | 21.731 | 22.3244 | 22.3307 | 22.2932 | 21.9521 | 21.1501 | 22.1263 | 21.5788 | 21.7762 | 22.0006 | 21.0651 | 21.4326 | 23.3988 | 21.8845 | 62.0891 | 75.3466 | 22.1798 | 24.9293 | 80.5776 | 614.5318 | 635.8049 | 615.6102 | 22.2318 | 24.0769 | 88.8132 | 22.2624 | 25.2251 | 87.3018 | 715.2212 | 870.2251 |  | 620.4371 | 854.7242 | 856.3275 | 663.9527 |  | 204.5219 | 370.3347 | 419.3182 | 713.7121 | 760.553 | 832.9609 | 873.3322 | 32.5232 | 108.3454 | 40.0153 | 247.65 | 25.9114 | 47.1097 | 44.185 | 49.2614 | 26.9364 |  |  | 0.034402 | -0.1696 | -125.3128 | -0.3378 | 9.0158 | -197.8118 | -203.2673 | -4.0515 | 6.1716 | 18.0293 | 15.988 | 0.0059354 | 0.0045078 | 0.0003877 | 22.6145 | 21.9908 | 22.146 | 22.1899 | 21.989 | 21.2706 | 20.0795 | 22.1576 | 22.3327 | 22.3718 | 22.3137 | 21.9116 | 21.1325 | 22.2332 | 350.908 | 283.4414 | 261.8752 | 187.5483 | 163.7919 | 493.7395 | 279.375 | 22.317 | 22.0821 | 21.76 | 22.0401 | 21.8817 | 23.3649 | 22.0386 | 28.7985 | 72.451 | 545.7282 | 488.7992 | 488.9246 | 492.7203 | 31.2763 | 17.4572 | 723.4719 | 21.9058 | 22.1791 | 231.6512 | 21.5369 | 21.9922 | 22.6425 | 40.2361 | 88.3101 | 21.9788 | 24.0958 | 88.0728 | 698.4836 | 613.7698 | 737.2751 | 759.1079 | 685.6997 |  | 743.9781 | 772.7754 | 812.5508 | 579.5783 | 637.4047 | 769.1225 |  | 358.3654 |  |  | 349.3798 | 536.0757 | 643.4113 | [5 empty] | 21.8536 | 543.6032 | 21.7035 | 22.0565 | 327.8922 | 21.279 | 21.8707 | 427.1202 | 580.1698 | 592.6139 |  | 888.1306 | 911.8829 | 473.0253 | 634.2829 | 765.9086 | 536.7614 | 616.2403 | 787.4414 | 939.0788 | 558.1762 | 731.5956 | 907.7825 | 947.0891 | 979.5615 | 463.4682 | 559.8221 | 589.136 | 542.738 | 635.2029 | 783.6123 | 876.9232 | 975.9558 | 514.8153 | 601.1298 | 589.3934 | 734.2416 | 54.6391 | 0.27302 | 17.7806 | 6.0705 | -28.0322 | 3.0953 | 6613.39 | -0.03 | 0.38535 | -0.72803 | -19.7895 | -1.0275 | 6.9593 | -32.5981 | -33.0446 | 62.3044 | 79.8863 | 40.5832 | 35.4818 | 7.2288 | 55.5324 | 26.9677
42838.4291 | 758 | 22.8703 | 22.842 | 22.8303 | 22.7356 | 22.3469 | 21.6795 | 22.6829 | 21.7291 | 22.3287 | 22.3351 | 22.2999 | 21.9487 | 21.1544 | 22.1291 | 21.5724 | 21.7694 | 21.9909 | 21.0605 | 21.4322 | 23.4176 | 21.8577 | 62.5933 | 75.5642 | 22.1783 | 24.9738 | 80.7042 | 619.6331 | 639.1952 | 620.5081 | 22.2226 | 24.1242 | 88.973 | 22.2659 | 25.2879 | 87.374 | 714.9647 | 860.5562 |  | 382.3932 | 860.1416 | 863.8381 | 667.1759 |  | 206.2779 | 373.5837 | 420.1451 | 707.8069 | 754.5836 | 827.7197 | 872.6521 | 32.3342 | 109.2626 | 39.9821 | 249.4534 | 26.0214 | 47.0075 | 44.0483 | 49.2058 | 26.9986 |  |  | 0.34062 | -0.40682 | -132.2053 | -0.63547 | 8.6143 | -197.8473 | -203.2548 | -4.1652 | 6.0043 | 17.5614 | 14.6419 | 0.0059896 | 0.004659 | 0.00038441 | 22.6163 | 21.9808 | 22.1359 | 22.1834 | 21.9821 | 21.2569 | 20.0786 | 22.1524 | 22.3293 | 22.3665 | 22.3044 | 21.9141 | 21.1314 | 22.2279 | 352.8368 | 265.2496 | 251.5608 | 193.5261 | 161.8944 | 492.0998 | 278.6848 | 22.3205 | 22.0928 | 21.7619 | 22.0367 | 21.8859 | 23.4052 | 22.0463 | 29.067 | 72.5863 | 545.3528 | 489.6659 | 491.0125 | 501.2823 | 22.4144 | 10.5959 | 725.394 | 21.9036 | 22.1792 | 231.9759 | 21.5279 | 21.9894 | 22.6606 | 41.0148 | 88.3037 | 21.9677 | 24.1478 | 88.2112 | 699.7476 | 612.0413 | 737.409 | 759.9397 | 687.4232 |  | 742.3838 | 769.8529 | 811.5542 | 575.6615 | 635.8557 | 768.3518 |  | 360.6473 |  |  | 350.2929 | 538.2579 | 644.2429 | [5 empty] | 21.8604 | 541.1404 | 21.7145 | 22.0556 | 326.2504 | 21.2891 | 21.8733 | 427.2132 | 579.9916 | 593.4552 |  | 884.2499 | 907.7282 | 471.626 | 632.727 | 763.7715 | 536.5229 | 616.9838 | 789.4207 | 936.799 | 556.3916 | 730.972 | 897.2726 | 945.3911 | 975.6876 | 463.4287 | 560.0194 | 591.9655 | 538.3056 | 633.9604 | 788.8506 | 874.4091 | 973.2715 | 514.8349 | 602.8664 | 586.3342 | 732.5476 | 57.0947 | 0.2537 | 17.7948 | 6.0676 | -28.0399 | 3.0953 | 6515.19 | -0.03 | 1.2159 | -1.1304 | -20.3776 | -1.4128 | 6.7865 | -32.5237 | -32.9652 | 61.8327 | 79.6509 | 40.3844 | 34.9181 | 8.2718 | 55.3796 | 26.6728
42838.4291 | 759 | 22.863 | 22.8319 | 22.8243 | 22.7315 | 22.3356 | 21.6605 | 22.6706 | 21.7156 | 22.317 | 22.322 | 22.2806 | 21.9341 | 21.1429 | 22.1169 | 21.5708 | 21.7665 | 21.9918 | 21.059 | 21.4293 | 23.4428 | 21.9059 | 63.0618 | 75.7775 | 22.18 | 25.0189 | 80.8141 | 623.0731 | 645.3182 | 623.8848 | 22.2369 | 24.1612 | 89.1202 | 22.2775 | 25.3603 | 87.4389 | 714.9237 | 849.7345 |  | 386.8706 | 869.8568 | 873.3633 | 669.8415 |  | 207.9529 | 376.6439 | 420.2073 | 703.5901 | 752.5968 | 827.4576 | 874.1048 | 31.9976 | 110.0984 | 40.0206 | 251.0295 | 26.1332 | 46.9043 | 43.9256 | 49.1606 | 27.0759 |  |  | -0.36053 | -0.32731 | -134.0905 | -0.39891 | 8.2226 | -197.8072 | -203.1457 | -4.8926 | 5.7005 | 17.4162 | 12.8611 | 0.0058089 | 0.0045949 | 0.00037291 | 22.6195 | 21.9822 | 22.133 | 22.1812 | 21.9834 | 21.2555 | 20.0725 | 22.1581 | 22.3246 | 22.3595 | 22.3056 | 21.9109 | 21.131 | 22.2266 | 336.555 | 238.7392 | 235.816 | 184.7512 | 163.0717 | 490.0122 | 277.6687 | 22.3164 | 22.0827 | 21.7592 | 22.0319 | 21.8797 | 23.4299 | 22.0377 | 29.3484 | 72.7075 | 545.2893 | 490.4958 | 493.6567 | 505.5819 | 29.4088 | 9.4328 | 722.997 | 21.8975 | 22.1746 | 233.674 | 21.5265 | 21.9828 | 22.6632 | 41.7939 | 88.3071 | 21.9597 | 24.1918 | 88.3162 | 694.4362 | 610.2678 | 736.2896 | 758.4922 | 683.0715 |  | 740.6028 | 766.1629 | 810.455 | 574.275 | 634.3862 | 767.9112 |  | 362.8052 |  |  | 350.0732 | 538.9294 | 642.8503 | [5 empty] | 21.846 | 538.9846 | 21.7058 | 22.0571 | 327.2062 | 21.2743 | 21.8644 | 427.4542 | 580.0616 | 594.7836 |  | 884.4344 | 902.8415 | 470.4633 | 632.134 | 762.6264 | 536.4115 | 616.4088 | 794.1191 | 938.2037 | 555.7934 | 729.148 | 887.8571 | 946.6233 | 972.3869 | 463.6494 | 560.089 | 594.2286 | 534.2078 | 632.437 | 795.0521 | 873.4143 | 972.3867 | 515.2811 | 603.9674 | 583.6076 | 731.3146 | 57.9933 | 0.23778 | 17.812 | 6.054 | -27.9839 | 3.0952 | 6441.32 | -0.09 | -1.2533 | -1.0163 | -20.5709 | -1.122 | 6.6296 | -32.5165 | -32.9524 | 61.4822 | 79.4052 | 40.1324 | 36.2839 | 9.8697 | 55.2954 | 26.5437
42838.4291 | 760 | 22.8628 | 22.8363 | 22.8256 | 22.7375 | 22.3408 | 21.6652 | 22.6772 | 21.7213 | 22.3267 | 22.3267 | 22.2912 | 21.9359 | 21.1482 | 22.1207 | 21.5809 | 21.7775 | 22.0077 | 21.0654 | 21.4444 | 23.4828 | 21.9696 | 63.5154 | 75.9788 | 22.1943 | 25.0743 | 80.9306 | 627.4898 | 649.5572 | 628.0889 | 22.2279 | 24.2026 | 89.2595 | 22.275 | 25.419 | 87.5211 | 714.8762 | 855.1778 |  | 387.936 | 871.2153 | 874.432 | 667.7347 |  | 209.3947 | 379.4307 | 420.0301 | 699.0554 | 744.2994 | 826.8526 | 874.4194 | 31.2231 | 111.0074 | 39.8398 | 252.7943 | 26.1981 | 46.7715 | 43.8007 | 49.1085 | 27.1376 |  |  | 0.35705 | -0.002693 | -135.2024 | -0.19981 | 8.749 | -197.7954 | -203.2529 | -3.9174 | 5.5351 | 16.5405 | 13.0007 | 0.0057186 | 0.0044552 | 0.00039427 | 22.6256 | 21.9815 | 22.1407 | 22.1825 | 21.9843 | 21.2665 | 20.0764 | 22.1623 | 22.3251 | 22.3685 | 22.3037 | 21.9078 | 21.1295 | 22.2295 | 338.1913 | 230.3812 | 222.8337 | 174.9841 | 155.1149 | 488.0791 | 276.5734 | 22.3208 | 22.0814 | 21.7639 | 22.0326 | 21.8875 | 23.4651 | 22.0496 | 29.66 | 72.8273 | 545.2723 | 490.6385 | 494.7752 | 507.068 | 24.3377 | 10.4981 | 721.5487 | 21.9091 | 22.1839 | 233.3466 | 21.5371 | 21.9883 | 22.6725 | 42.6113 | 88.3208 | 21.9697 | 24.2547 | 88.4325 | 697.7751 | 609.5594 | 736.6587 | 757.6812 | 688.3842 |  | 739.099 | 765.4422 | 809.4129 | 576.8855 | 633.0105 | 768.7516 |  | 365.1297 |  |  | 349.6002 | 537.5133 | 644.2621 | [5 empty] | 21.8575 | 538.4931 | 21.7112 | 22.0714 | 329.875 | 21.2755 | 21.871 | 427.4526 | 579.9665 | 594.7969 |  | 884.9429 | 900.849 | 469.6862 | 632.1064 | 760.5081 | 536.6832 | 615.354 | 794.2068 | 940.2193 | 555.5813 | 729.1103 | 878.8996 | 948.1291 | 970.7505 | 463.7184 | 560.6106 | 596.4697 | 530.8567 | 631.8329 | 800.4632 | 872.8619 | 971.9894 | 515.7226 | 605.4093 | 581.4488 | 731.4571 | 57.7022 | 0.22265 | 17.8311 | 6.0514 | -28.0644 | 3.0952 | 6406.46 | -0.01 | 1.2501 | -0.092385 | -20.7003 | -0.79577 | 6.8366 | -32.5066 | -32.952 | 60.9383 | 79.096 | 39.789 | 35.6932 | 11.149 | 55.3422 | 26.4998
42838.4291 | 761 | 22.867 | 22.8382 | 22.8311 | 22.7427 | 22.3434 | 21.6661 | 22.6756 | 21.7227 | 22.3311 | 22.3279 | 22.2936 | 21.9363 | 21.1425 | 22.1202 | 21.5701 | 21.7686 | 22.0007 | 21.0607 | 21.4558 | 23.5081 | 22.0144 | 63.9373 | 76.1682 | 22.1924 | 25.1198 | 81.0376 | 629.2981 | 654.9076 | 629.6644 | 22.2264 | 24.246 | 89.3834 | 22.274 | 25.4736 | 87.582 | 714.8766 | 861.9606 |  | 390.2768 | 878.8884 | 881.7499 | 663.5034 |  | 210.4517 | 381.1907 | 420.2776 | 697.2624 | 737.8728 | 821.5664 | 872.0469 | 30.6998 | 111.7382 | 39.1321 | 254.1805 | 26.2891 | 46.6496 | 43.679 | 49.0518 | 27.2082 |  |  | 0.16582 | 0.23321 | -131.3793 | -0.36211 | 8.7582 | -197.8657 | -203.2266 | -4.1796 | 5.7511 | 16.9123 | 13.6675 | 0.0057925 | 0.0045045 | 0.00038113 | 22.6334 | 21.9846 | 22.1418 | 22.1928 | 21.9921 | 21.2625 | 20.0779 | 22.1583 | 22.3331 | 22.3742 | 22.3132 | 21.9067 | 21.1448 | 22.2319 | 340.0462 | 228.7516 | 219.6135 | 171.8277 | 150.646 | 485.9914 | 275.4315 | 22.3236 | 22.0844 | 21.7636 | 22.0384 | 21.894 | 23.4965 | 22.0571 | 30.0064 | 72.9476 | 545.3034 | 491.4921 | 496.9135 | 511.9932 | 29.7651 | 11.2194 | 720.931 | 21.8998 | 22.1728 | 232.2332 | 21.5265 | 21.9778 | 22.6701 | 43.4094 | 88.3198 | 21.9652 | 24.3034 | 88.5274 | 699.6408 | 608.5444 | 734.8374 | 754.5056 | 690.053 |  | 737.7469 | 766.3205 | 808.483 | 576.8248 | 631.6955 | 770.4994 |  | 367.4326 |  |  | 349.2345 | 538.2935 | 645.9648 | [5 empty] | 21.8539 | 537.6471 | 21.7115 | 22.0658 | 331.6024 | 21.278 | 21.8684 | 427.4981 | 579.8278 | 594.288 |  | 881.492 | 899.6574 | 469.0802 | 631.9311 | 758.6345 | 536.7038 | 614.4948 | 795.0731 | 941.2215 | 554.4681 | 731.1296 | 870.0522 | 947.7889 | 968.5438 | 463.6457 | 561.6563 | 598.7864 | 527.6981 | 631.3578 | 806.2515 | 868.6918 | 970.7471 | 515.7314 | 606.3805 | 579.8343 | 731.1973 | 57.403 | 0.21446 | 17.8464 | 6.028 | -28.1092 | 3.0952 | 6424.64 | -0.22 | 0.85268 | 0.86088 | -20.433 | -1.0727 | 6.8238 | -32.4342 | -32.8706 | 60.5369 | 78.7785 | 39.5327 | 35.0472 | 11.3371 | 55.4598 | 26.3677
42838.4291 | 762 | 22.861 | 22.8395 | 22.8303 | 22.7373 | 22.346 | 21.6643 | 22.6707 | 21.7216 | 22.3306 | 22.3303 | 22.2912 | 21.936 | 21.1439 | 22.123 | 21.5757 | 21.7675 | 22.0001 | 21.0666 | 21.4585 | 23.5357 | 22.058 | 64.3622 | 76.3653 | 22.1983 | 25.1753 | 81.1643 | 633.1341 | 659.451 | 633.4244 | 22.2271 | 24.2826 | 89.4955 | 22.2772 | 25.5371 | 87.6472 | 714.9961 | 853.7688 |  | 392.3437 | 884.3509 | 886.9826 | 659.1525 |  | 212.1933 | 384.0356 | 420.6616 | 690.779 | 735.7016 | 819.2662 | 874.4344 | 30.4233 | 112.5795 | 38.5907 | 255.9212 | 26.3981 | 46.496 | 43.5717 | 48.9969 | 27.2728 |  |  | 0.24271 | -0.1466 | -132.8551 | -0.42651 | 8.7969 | -197.8072 | -203.2128 | -4.175 | 5.6254 | 16.7065 | 13.35 | 0.0055756 | 0.004337 | 0.00038113 | 22.6332 | 21.9838 | 22.1351 | 22.1909 | 21.9874 | 21.265 | 20.0743 | 22.149 | 22.3289 | 22.3664 | 22.3111 | 21.9126 | 21.1377 | 22.2294 | 348.5593 | 225.4551 | 219.2436 | 174.5721 | 146.8916 | 484.3475 | 274.3121 | 22.3211 | 22.0871 | 21.7642 | 22.0438 | 21.8948 | 23.5443 | 22.0645 | 30.4435 | 73.0783 | 545.4783 | 493.105 | 499.3319 | 514.1535 | 28.287 | 16.0704 | 721.1711 | 21.903 | 22.1852 | 231.8603 | 21.5339 | 21.9815 | 22.6909 | 44.2503 | 88.3349 | 21.9612 | 24.3604 | 88.6049 | 697.3484 | 607.8529 | 734.8492 | 753.4737 | 689.2862 |  | 736.5432 | 772.7873 | 808.2079 | 577.0481 | 630.5014 | 773.2183 |  | 369.545 |  |  | 349.7827 | 540.9236 | 646.7661 | [5 empty] | 21.8631 | 536.7414 | 21.7239 | 22.0685 | 332.9755 | 21.3003 | 21.8736 | 427.3276 | 579.6327 | 595.1736 |  | 877.5602 | 898.9489 | 468.0107 | 631.3063 | 757.8241 | 536.1957 | 615.7945 | 793.3457 | 940.9685 | 552.7918 | 729.1827 | 863.4039 | 945.4958 | 969.7082 | 464.1328 | 562.1256 | 600.7128 | 524.6935 | 630.709 | 809.8541 | 866.6727 | 968.8007 | 516.6315 | 607.0914 | 578.257 | 730.4363 | 59.0694 | 0.1984 | 17.8621 | 6.0098 | -28.0883 | 3.0952 | 6469.06 | -0.03 | 1.0337 | -0.68404 | -20.5921 | -1.1667 | 6.8317 | -32.3953 | -32.835 | 60.2433 | 78.5123 | 39.2931 | 33.756 | 11.212 | 55.6102 | 26.3343
42838.4291 | 763 | 22.8649 | 22.837 | 22.8232 | 22.7307 | 22.337 | 21.6625 | 22.6717 | 21.7122 | 22.3245 | 22.3264 | 22.29 | 21.9342 | 21.1395 | 22.127 | 21.5787 | 21.7751 | 22.004 | 21.0658 | 21.4602 | 23.5711 | 22.1105 | 64.781 | 76.5636 | 22.1798 | 25.2255 | 81.2697 | 636.1306 | 661.6095 | 636.3309 | 22.2229 | 24.3347 | 89.6189 | 22.2786 | 25.5986 | 87.7235 | 714.9634 | 853.7072 |  | 393.2116 | 886.5249 | 888.332 | 656.0784 |  | 213.7568 | 387.1979 | 420.7684 | 683.3069 | 737.217 | 823.3282 | 872.164 | 30.2677 | 113.3376 | 38.3156 | 257.4183 | 26.4981 | 46.3569 | 43.4737 | 48.9236 | 27.3413 |  |  | 0.19737 | -0.34177 | -133.3723 | -0.1111 | 8.6787 | -197.821 | -203.314 | -4.1855 | 5.7056 | 16.6628 | 13.9253 | 0.0055986 | 0.0043567 | 0.00037291 | 22.6381 | 21.9753 | 22.1347 | 22.1868 | 21.9785 | 21.2649 | 20.0785 | 22.1499 | 22.3293 | 22.3676 | 22.3062 | 21.9042 | 21.1313 | 22.2256 | 348.2111 | 227.4874 | 228.8742 | 177.0186 | 146.5903 | 482.9726 | 273.4792 | 22.3158 | 22.0896 | 21.7648 | 22.0397 | 21.8972 | 23.5777 | 22.0618 | 30.8613 | 73.1862 | 545.5931 | 493.6061 | 501.115 | 517.1238 | 37.9591 | 20.2991 | 724.4506 | 21.9025 | 22.1761 | 232.7224 | 21.5336 | 21.9823 | 22.7003 | 45.086 | 88.3373 | 21.9607 | 24.4135 | 88.6843 | 699.3355 | 607.2112 | 735.5313 | 752.9223 | 689.3017 |  | 735.318 | 789.1373 | 808.8609 | 579.7781 | 629.4878 | 777.213 |  | 371.7341 |  |  | 349.5368 | 542.2589 | 646.7406 | [5 empty] | 21.8547 | 538.1199 | 21.7126 | 22.0661 | 333.002 | 21.2805 | 21.8656 | 427.8583 | 579.6025 | 596.4884 |  | 873.1216 | 899.2404 | 466.727 | 632.5125 | 754.5429 | 536.0271 | 615.2459 | 784.7569 | 937.2055 | 552.3468 | 731.6181 | 855.7367 | 939.407 | 970.7924 | 464.9769 | 562.3581 | 602.9232 | 521.1543 | 629.9616 | 813.8877 | 859.0969 | 966.9428 | 517.4387 | 607.2683 | 576.2762 | 731.3763 | 57.3902 | 0.18744 | 17.8785 | 5.9806 | -28.1405 | 3.0952 | 6529.42 | -0.09 | 0.93368 | -1.0469 | -20.6817 | -0.59691 | 6.7982 | -32.4566 | -32.9041 | 59.9233 | 78.2637 | 39.0197 | 33.5068 | 10.0185 | 55.6875 | 26.2693
42838.4291 | 764 | 22.8669 | 22.8322 | 22.8235 | 22.7399 | 22.3459 | 21.6628 | 22.6743 | 21.7131 | 22.3248 | 22.321 | 22.2869 | 21.9323 | 21.149 | 22.1208 | 21.5662 | 21.7656 | 21.9878 | 21.0527 | 21.461 | 23.5989 | 22.1529 | 65.16 | 76.7472 | 22.1925 | 25.2693 | 81.3642 | 636.0532 | 662.1896 | 636.2818 | 22.212 | 24.3831 | 89.7204 | 22.282 | 25.6692 | 87.7961 | 714.7827 | 860.8646 |  | 393.4398 | 887.656 | 889.7547 | 651.9274 |  | 215.5047 | 390.4985 | 421.4473 | 679.3614 | 735.9926 | 821.2212 | 871.7708 | 30.0941 | 114.0587 | 37.7714 | 258.8124 | 26.6303 | 46.2226 | 43.3905 | 48.8491 | 27.3931 |  |  | 0.26833 | -0.39302 | -137.5778 | -0.24712 | 8.4237 | -197.8493 | -203.4145 | -4.5318 | 5.769 | 16.5848 | 13.0882 | 0.0056495 | 0.004355 | 0.0003647 | 22.6367 | 21.978 | 22.1305 | 22.1815 | 21.9791 | 21.2613 | 20.0703 | 22.1526 | 22.3286 | 22.3536 | 22.3047 | 21.9097 | 21.1317 | 22.2213 | 368.3619 | 248.2247 | 248.939 | 181.2032 | 146.8029 | 482.4112 | 272.9503 | 22.3157 | 22.0892 | 21.7693 | 22.0411 | 21.8975 | 23.6163 | 22.0751 | 31.2841 | 73.2986 | 545.7801 | 494.5686 | 502.7314 | 518.4169 | 40.0954 | 15.267 | 733.1644 | 21.9157 | 22.1909 | 234.2548 | 21.5417 | 21.99 | 22.7146 | 45.9446 | 88.3625 | 21.9676 | 24.4807 | 88.7728 | 700.2259 | 606.5544 | 734.4961 | 750.197 | 686.3468 |  | 734.0778 | 778.6093 | 808.2006 | 581.1298 | 628.3831 | 773.075 |  | 374.1164 |  |  | 348.849 | 543.4581 | 646.4665 | [5 empty] | 21.8487 | 538.4732 | 21.7083 | 22.0675 | 332.96 | 21.2824 | 21.8686 | 428.0012 | 579.2174 | 596.2698 |  | 866.7085 | 897.8488 | 466.3165 | 636.8533 | 754.0333 | 535.1466 | 614.4027 | 779.8211 | 927.9043 | 552.0739 | 734.5483 | 848.7317 | 935.4278 | 968.6834 | 464.6297 | 562.7121 | 604.9279 | 518.1301 | 629.0101 | 817.0182 | 852.1427 | 969.9507 | 517.9349 | 607.7885 | 573.7585 | 730.151 | 58.8822 | 0.17737 | 17.8962 | 5.9622 | -28.0807 | 3.0952 | 6555.08 | -0.08 | 1.0887 | -1.1255 | -21.0577 | -0.89246 | 6.6911 | -32.4277 | -32.8806 | 59.683 | 78.3483 | 38.7676 | 31.1504 | 7.7107 | 55.7582 | 26.2619
42838.4291 | 765 | 22.8726 | 22.8426 | 22.8219 | 22.7429 | 22.3443 | 21.6666 | 22.6766 | 21.7244 | 22.3331 | 22.3305 | 22.2965 | 21.9406 | 21.1564 | 22.1246 | 21.5756 | 21.7648 | 22.001 | 21.0646 | 21.4719 | 23.6287 | 22.2141 | 65.544 | 76.9307 | 22.1989 | 25.3267 | 81.4581 | 635.8755 | 662.8723 | 636.3149 | 22.2278 | 24.4404 | 89.8356 | 22.291 | 25.7438 | 87.8726 | 714.2238 | 860.1165 |  | 382.8411 | 890.9076 | 893.1041 | 651.8314 |  | 216.8505 | 392.6512 | 425.5141 | 681.0396 | 730.9541 | 815.7241 | 869.2059 | 29.8391 | 114.8653 | 37.3196 | 260.436 | 26.7839 | 46.125 | 43.3282 | 48.7892 | 27.4576 |  |  | 0.41224 | -0.044749 | -127.748 | -0.02107 | 9.0874 | -197.8289 | -203.3672 | -4.1645 | 5.8095 | 17.2765 | 13.1482 | 0.00562 | 0.004309 | 0.00038606 | 22.6512 | 21.9811 | 22.1329 | 22.1796 | 21.9908 | 21.2617 | 20.0734 | 22.1539 | 22.3296 | 22.3519 | 22.3055 | 21.9121 | 21.1388 | 22.2264 | 386.7973 | 268.8792 | 250.9346 | 179.3444 | 156.2 | 482.048 | 272.2049 | 22.3265 | 22.0902 | 21.77 | 22.0389 | 21.9032 | 23.6592 | 22.0845 | 31.7296 | 73.4103 | 545.8595 | 495.1868 | 503.5052 | 518.1117 | 31.9007 | 22.2599 | 728.524 | 21.9107 | 22.1829 | 236.5766 | 21.537 | 21.9899 | 22.729 | 46.81 | 88.3731 | 21.9616 | 24.5398 | 88.8524 | 697.8735 | 606.8131 | 734.5224 | 749.1355 | 685.6425 |  | 732.9874 | 766.2284 | 806.7182 | 582.0638 | 627.4778 | 767.082 |  | 376.1479 |  |  | 350.3681 | 542.6471 | 645.8739 | [5 empty] | 21.8566 | 538.9287 | 21.7153 | 22.0684 | 334.8972 | 21.2841 | 21.8692 | 428.1468 | 578.7194 | 596.3535 |  | 866.1482 | 892.3665 | 465.3624 | 638.1732 | 756.1758 | 534.8881 | 613.9685 | 779.8556 | 925.3772 | 550.7657 | 732.1798 | 842.204 | 932.1501 | 966.093 | 464.3283 | 562.8219 | 605.9194 | 515.6168 | 627.5719 | 817.5636 | 848.5857 | 973.6139 | 518.6886 | 607.7719 | 572.1504 | 728.8117 | 58.1152 | 0.16774 | 17.9155 | 5.931 | -28.1253 | 3.0951 | 6600.17 | -0.1 | 1.3494 | -0.38039 | -20.3243 | -0.26102 | 6.9323 | -32.3445 | -32.7941 | 59.42 | 78.2268 | 38.5663 | 29.0262 | 7.3787 | 55.6233 | 26.2824
42838.4291 | 766 | 22.858 | 22.8326 | 22.8316 | 22.74 | 22.3432 | 21.6633 | 22.6687 | 21.7135 | 22.3177 | 22.3277 | 22.2865 | 21.9304 | 21.1554 | 22.1251 | 21.5822 | 21.772 | 22.0101 | 21.0712 | 21.4848 | 23.6698 | 22.2698 | 65.9261 | 77.1029 | 22.207 | 25.3868 | 81.5553 | 635.9814 | 664.0512 | 636.1396 | 22.2282 | 24.4926 | 89.9508 | 22.2802 | 25.8181 | 87.9375 | 714.2349 | 859.9161 |  | 381.482 | 894.0373 | 897.1552 | 654.5123 |  | 217.7439 | 394.5717 | 425.7306 | 686.4468 | 729.7503 | 811.4499 | 864.778 | 29.6924 | 115.5448 | 37.363 | 261.7306 | 26.862 | 46.0281 | 43.2518 | 48.7089 | 27.5088 |  |  | 0.22562 | -0.27474 | -126.7243 | -0.17418 | 8.6603 | -197.8112 | -203.312 | -4.0291 | 5.7338 | 17.6367 | 14.1825 | 0.0055461 | 0.0043172 | 0.0003647 | 22.6636 | 21.987 | 22.1402 | 22.1829 | 21.9921 | 21.2655 | 20.0821 | 22.1536 | 22.3296 | 22.3553 | 22.3042 | 21.9139 | 21.1343 | 22.2336 | 392.0634 | 288.5539 | 284.5815 | 179.9717 | 160.92 | 481.1585 | 272.0024 | 22.3163 | 22.08 | 21.766 | 22.0495 | 21.8986 | 23.6902 | 22.078 | 32.1612 | 73.5156 | 545.8483 | 495.1397 | 503.2119 | 514.7959 | 28.2261 | 22.6529 | 724.5 | 21.9156 | 22.1819 | 237.3372 | 21.5364 | 21.9856 | 22.7335 | 47.6884 | 88.3751 | 21.9618 | 24.596 | 88.9128 | 700.7705 | 607.4915 | 733.8625 | 748.4104 | 688.4434 |  | 731.9493 | 761.2164 | 805.3525 | 584.9653 | 626.7989 | 763.6991 |  | 378.208 |  |  | 351.3217 | 540.777 | 646.499 | [5 empty] | 21.8584 | 540.479 | 21.7155 | 22.0679 | 339.6104 | 21.2782 | 21.8683 | 428.0002 | 578.5527 | 597.4689 |  | 865.6487 | 889.1237 | 464.4137 | 636.843 | 755.6894 | 534.7671 | 614.4788 | 775.4933 | 928.1268 | 549.694 | 733.022 | 835.8194 | 931.7645 | 964.2425 | 463.8794 | 563.0442 | 606.8812 | 513.4211 | 626.8519 | 818.2911 | 846.5094 | 975.062 | 518.7879 | 607.2127 | 570.6485 | 730.9782 | 53.3814 | 0.15601 | 17.9342 | 5.9128 | -28.0016 | 3.0952 | 6635.22 | -0.04 | 0.99818 | -0.9439 | -20.2719 | -0.75156 | 6.7541 | -32.2795 | -32.7253 | 59.0739 | 77.9388 | 38.3545 | 28.2555 | 3.6102 | 55.5515 | 26.3728
42838.4292 | 767 | 22.8625 | 22.8347 | 22.8252 | 22.7391 | 22.3454 | 21.6653 | 22.6705 | 21.7184 | 22.3214 | 22.33 | 22.2927 | 21.9351 | 21.1549 | 22.1268 | 21.581 | 21.774 | 22.0074 | 21.0702 | 21.4934 | 23.7089 | 22.3266 | 66.2822 | 77.2621 | 22.2078 | 25.4415 | 81.646 | 636.1676 | 666.5635 | 636.5101 | 22.2249 | 24.5457 | 90.059 | 22.2848 | 25.8817 | 88.0057 | 714.1106 | 854.4884 |  | 382.7621 | 899.4849 | 902.6694 | 651.5002 |  | 219.5005 | 397.7912 | 426.9245 | 694.1684 | 734.4368 | 807.7913 | 860.7015 | 30.2153 | 116.3533 | 37.5695 | 263.1837 | 26.9733 | 45.9312 | 43.1883 | 48.6293 | 27.5518 |  |  | 0.18094 | -0.47976 | -137.2611 | -0.19455 | 8.9579 | -197.825 | -203.3251 | -4.0659 | 6.0043 | 17.3105 | 13.6411 | 0.0056676 | 0.0042663 | 0.0004107 | 22.6648 | 21.9822 | 22.1306 | 22.1839 | 21.982 | 21.2598 | 20.0756 | 22.1578 | 22.3289 | 22.3634 | 22.3044 | 21.9137 | 21.1348 | 22.2216 | 385.8828 | 281.2428 | 294.9894 | 190.2949 | 167.9383 | 480.1988 | 271.8446 | 22.319 | 22.0777 | 21.7694 | 22.0454 | 21.8987 | 23.7271 | 22.089 | 32.6479 | 73.6438 | 545.5711 | 494.3241 | 502.5158 | 511.4618 | 29.9451 | 22.9205 | 723.4741 | 21.9062 | 22.1837 | 237.4563 | 21.5363 | 21.9937 | 22.7446 | 48.5623 | 88.3929 | 21.9699 | 24.6696 | 88.9906 | 696.2681 | 607.5687 | 732.8189 | 746.9711 | 683.0301 |  | 730.3378 | 763.1323 | 804.2267 | 586.2228 | 626.1282 | 762.9134 |  | 380.5884 |  |  | 350.73 | 539.3068 | 644.3971 | [5 empty] | 21.8563 | 542.319 | 21.7186 | 22.0616 | 339.9785 | 21.2784 | 21.8653 | 428.4362 | 579.3441 | 598.4879 |  | 866.1468 | 887.9723 | 463.2181 | 636.1186 | 754.5371 | 535.1007 | 614.7137 | 775.7338 | 927.3256 | 548.4962 | 735.0865 | 828.7895 | 932.6305 | 964.3319 | 463.7884 | 563.2235 | 607.7339 | 511.3216 | 626.1194 | 819.1405 | 846.9404 | 974.3168 | 519.128 | 607.4307 | 569.4561 | 730.6771 | 55.2106 | 0.1506 | 17.9515 | 5.8853 | -28.0913 | 3.0952 | 6638.25 | -0.08 | 0.89407 | -1.2503 | -21.1487 | -0.7962 | 6.8576 | -32.2262 | -32.6711 | 58.8093 | 77.5345 | 38.1902 | 28.7424 | 2.4305 | 55.6046 | 26.4232
42838.4292 | 768 | 22.855 | 22.8291 | 22.8203 | 22.7326 | 22.3388 | 21.6604 | 22.6634 | 21.713 | 22.3109 | 22.3222 | 22.2823 | 21.9287 | 21.1473 | 22.1172 | 21.5804 | 21.7697 | 22.0058 | 21.0677 | 21.5033 | 23.7471 | 22.3814 | 66.6346 | 77.4166 | 22.2083 | 25.4934 | 81.7288 | 638.1129 | 668.4608 | 638.6165 | 22.2207 | 24.5975 | 90.1458 | 22.2849 | 25.9527 | 88.0688 | 713.7699 | 853.0701 |  | 383.1306 | 900.8918 | 903.7816 | 649.0931 |  | 220.9725 | 400.2373 | 429.1903 | 697.0886 | 735.2561 | 805.6425 | 858.1888 | 30.2693 | 117.1826 | 37.4427 | 264.5233 | 27.1102 | 45.8264 | 43.1274 | 48.5378 | 27.6044 |  |  | 0.14545 | -0.032921 | -137.4339 | -0.056554 | 8.9514 | -197.7987 | -203.3396 | -4.0955 | 5.6198 | 16.607 | 13.7492 | 0.0054672 | 0.0041793 | 0.00037784 | 22.6762 | 21.9873 | 22.1467 | 22.1903 | 21.9887 | 21.2669 | 20.0823 | 22.1616 | 22.3334 | 22.3747 | 22.3174 | 21.9215 | 21.1398 | 22.2248 | 373.515 | 277.497 | 300.8946 | 191.6603 | 168.3282 | 479.2101 | 271.7666 | 22.32 | 22.0833 | 21.7776 | 22.0515 | 21.9098 | 23.7689 | 22.1076 | 33.0375 | 73.7512 | 545.4657 | 493.4337 | 502.2794 | 510.9505 | 36.4512 | 21.5605 | 725.2259 | 21.9062 | 22.1733 | 237.0364 | 21.5237 | 21.9825 | 22.7466 | 49.4046 | 88.3973 | 21.9639 | 24.7245 | 89.0589 | 691.7892 | 606.6848 | 731.8422 | 745.0427 | 678.3257 |  | 728.8211 | 769.3343 | 803.7873 | 584.9956 | 625.3365 | 762.9765 |  | 382.7689 |  |  | 349.9676 | 537.3551 | 641.4809 | [5 empty] | 21.8534 | 542.1804 | 21.7144 | 22.0614 | 339.4576 | 21.2729 | 21.8685 | 428.701 | 580.1216 | 599.0212 |  | 867.6382 | 885.8767 | 461.9591 | 636.1587 | 754.869 | 535.6441 | 614.7472 | 771.0969 | 927.2527 | 547.5339 | 733.4746 | 823.352 | 934.3153 | 965.7258 | 463.679 | 563.7137 | 608.6419 | 509.38 | 624.909 | 819.6162 | 846.5956 | 974.943 | 519.8548 | 608.0213 | 567.8378 | 730.2739 | 58.0705 | 0.14267 | 17.9697 | 5.8596 | -28.0908 | 3.0952 | 6617.29 | -0.02 | 0.80255 | -0.32812 | -21.2005 | -0.43006 | 6.8483 | -32.192 | -32.6398 | 58.551 | 77.2255 | 38.0718 | 29.911 | 1.7628 | 55.5877 | 26.4214
42838.4292 | 769 | 22.8573 | 22.8336 | 22.8205 | 22.735 | 22.3447 | 21.6657 | 22.6662 | 21.7193 | 22.3172 | 22.3205 | 22.2851 | 21.9358 | 21.1462 | 22.1236 | 21.5754 | 21.7662 | 22.0047 | 21.0619 | 21.5096 | 23.7759 | 22.436 | 66.9871 | 77.5557 | 22.2067 | 25.5394 | 81.8128 | 642.6963 | 671.2929 | 643.9435 | 22.2202 | 24.6546 | 90.2328 | 22.2921 | 26.0253 | 88.1334 | 713.5557 | 854.3656 |  | 384.1064 | 899.6001 | 902.9018 | 644.3314 |  | 222.1351 | 402.6861 | 428.4556 | 695.3851 | 729.2507 | 803.3806 | 854.7549 | 29.4837 | 117.9052 | 37.2683 | 265.6431 | 27.2261 | 45.7095 | 43.0825 | 48.4619 | 27.6682 |  |  | 0.007458 | 0.25884 | -142.6251 | -0.004642 | 9.2931 | -197.8342 | -203.3613 | -4.1264 | 5.8428 | 16.6498 | 14.2192 | 0.0054245 | 0.0042137 | 0.0003762 | 22.6812 | 21.9824 | 22.1375 | 22.181 | 21.9874 | 21.2624 | 20.0817 | 22.1532 | 22.3335 | 22.3685 | 22.3098 | 21.9169 | 21.1334 | 22.2306 | 377.7067 | 285.3902 | 314.575 | 192.2997 | 165.3182 | 478.7078 | 271.9488 | 22.3186 | 22.0865 | 21.7787 | 22.0487 | 21.9122 | 23.8046 | 22.0999 | 33.4393 | 73.8416 | 545.4568 | 492.601 | 502.101 | 512.7621 | 35.1077 | 24.4238 | 727.811 | 21.9 | 22.1751 | 236.5667 | 21.5214 | 21.9798 | 22.7571 | 50.2392 | 88.4125 | 21.9619 | 24.789 | 89.1295 | 694.3906 | 606.5957 | 730.3842 | 743.2957 | 680.058 |  | 727.6246 | 769.1824 | 803.1497 | 586.3004 | 624.7109 | 762.4378 |  | 384.8221 |  |  | 350.8155 | 536.4432 | 640.88 | [5 empty] | 21.8535 | 542.9118 | 21.7148 | 22.0647 | 341.0745 | 21.2829 | 21.8714 | 429.1917 | 580.4812 | 599.232 |  | 866.9902 | 883.1646 | 460.8481 | 635.1376 | 755.719 | 536.3491 | 615.7292 | 769.5915 | 927.7292 | 546.9039 | 733.7836 | 816.61 | 934.407 | 967.8512 | 463.7349 | 564.2796 | 610.8288 | 507.4692 | 624.2796 | 822.6993 | 845.5168 | 977.7999 | 520.532 | 608.3707 | 565.9353 | 731.2832 | 58.342 | 0.13705 | 17.9904 | 5.8328 | -28.1212 | 3.0952 | 6583.06 | 0 | 0.18226 | 0.92173 | -21.6364 | -0.12344 | 6.9704 | -32.1611 | -32.6073 | 58.1972 | 77.0315 | 37.9154 | 29.341 | 0.26968 | 55.6673 | 26.3697
42838.4292 | 770 | 22.8624 | 22.8364 | 22.8236 | 22.7339 | 22.3409 | 21.657 | 22.6762 | 21.7184 | 22.3186 | 22.3234 | 22.2959 | 21.9374 | 21.1475 | 22.1209 | 21.5706 | 21.7612 | 22.003 | 21.0582 | 21.5128 | 23.8104 | 22.4919 | 67.3282 | 77.7017 | 22.2074 | 25.5966 | 81.9128 | 646.3325 | 672.9572 | 646.5786 | 22.2173 | 24.7086 | 90.3056 | 22.2828 | 26.096 | 88.1949 | 712.6054 | 851.1776 |  | 384.6388 | 898.4109 | 901.5127 | 642.7057 |  | 223.4024 | 404.9921 | 426.8204 | 684.866 | 718.8599 | 800.7475 | 855.7667 | 28.6186 | 118.8049 | 36.8935 | 266.9136 | 27.3057 | 45.5795 | 43.0463 | 48.3735 | 27.7373 |  |  | 0.34062 | 0.42838 | -138.3565 | -0.47317 | 9.3384 | -197.8256 | -203.2568 | -3.6158 | 5.7422 | 16.6754 | 13.9213 | 0.0054261 | 0.0041612 | 0.00038934 | 22.6816 | 21.9765 | 22.1309 | 22.1817 | 21.9868 | 21.2565 | 20.077 | 22.1464 | 22.3246 | 22.3596 | 22.3034 | 21.9017 | 21.1344 | 22.2258 | 393.0693 | 306.5148 | 319.8756 | 202.5656 | 177.2479 | 478.5379 | 272.1964 | 22.3133 | 22.0881 | 21.7757 | 22.0479 | 21.9104 | 23.8419 | 22.1037 | 33.881 | 73.9426 | 545.562 | 492.5902 | 502.8655 | 515.784 | 36.8605 | 18.5093 | 727.3339 | 21.906 | 22.172 | 235.9148 | 21.5227 | 21.9773 | 22.7635 | 51.0511 | 88.4195 | 21.9662 | 24.8563 | 89.1988 | 693.91 | 606.9285 | 729.3761 | 741.3666 | 684.251 |  | 726.7392 | 767.9087 | 802.2394 | 589.5985 | 624.3005 | 764.7384 |  | 386.9974 |  |  | 352.4378 | 537.1806 | 643.2673 | [5 empty] | 21.8514 | 544.9669 | 21.7125 | 22.0655 | 342.6394 | 21.2801 | 21.8654 | 429.3588 | 580.8927 | 600.1606 |  | 869.6604 | 882.3646 | 459.6947 | 634.1752 | 755.0354 | 536.5908 | 616.5401 | 774.1431 | 929.3835 | 546.0164 | 734.8617 | 809.5141 | 931.0866 | 969.0534 | 463.7016 | 564.6998 | 614.4618 | 505.5368 | 623.6624 | 823.2157 | 844.0001 | 978.7225 | 521.3573 | 608.758 | 564.4917 | 731.8755 | 57.3426 | 0.12868 | 18.0119 | 5.8077 | -28.0909 | 3.0952 | 6542.16 | -0.02 | 1.2335 | 1.1878 | -21.3465 | -1.2483 | 6.9789 | -32.121 | -32.559 | 57.8551 | 76.7845 | 37.7451 | 27.5988 | -0.28267 | 55.4794 | 26.3018
42838.4292 | 771 | 22.8691 | 22.8337 | 22.8261 | 22.732 | 22.3423 | 21.6615 | 22.6731 | 21.7199 | 22.3321 | 22.3337 | 22.2921 | 21.9352 | 21.1481 | 22.122 | 21.5737 | 21.7592 | 22.0058 | 21.0585 | 21.522 | 23.8519 | 22.55 | 67.6649 | 77.842 | 22.2112 | 25.6654 | 82.0096 | 645.2731 | 674.0598 | 645.2624 | 22.225 | 24.7667 | 90.4007 | 22.286 | 26.1616 | 88.2577 | 711.989 | 852.3166 |  | 384.7149 | 894.4331 | 897.5761 | 642.5198 |  | 224.3638 | 406.3829 | 426.0432 | 679.9987 | 708.5804 | 799.4218 | 857.8572 | 28.1856 | 119.462 | 36.692 | 267.9122 | 27.4542 | 45.4486 | 43.0095 | 48.2847 | 27.7987 |  |  | 0.4359 | -0.040805 | -138.9387 | 0.058438 | 8.8259 | -197.8046 | -203.2391 | -3.9687 | 5.394 | 15.9913 | 13.8024 | 0.0053341 | 0.004079 | 0.00041234 | 22.6874 | 21.9803 | 22.1299 | 22.1842 | 21.9869 | 21.2562 | 20.076 | 22.1473 | 22.328 | 22.3609 | 22.3043 | 21.9057 | 21.1346 | 22.2225 | 402.6349 | 300.479 | 305.964 | 200.9183 | 178.1602 | 478.1302 | 272.1612 | 22.326 | 22.0865 | 21.7837 | 22.0491 | 21.9138 | 23.8882 | 22.1092 | 34.3821 | 74.0361 | 545.9929 | 494.6771 | 505.8944 | 521.2477 | 25.1098 | 14.7618 | 727.1109 | 21.9024 | 22.1769 | 235.1267 | 21.5286 | 21.9783 | 22.7798 | 51.8442 | 88.4294 | 21.9649 | 24.9288 | 89.261 | 694.6456 | 607.645 | 727.428 | 738.7381 | 695.8309 |  | 726.2315 | 776.8741 | 802.073 | 593.1479 | 624.0524 | 772.6767 |  | 389.1603 |  |  | 352.0219 | 537.676 | 647.3469 | [5 empty] | 21.8523 | 547.2904 | 21.7179 | 22.059 | 346.6539 | 21.2763 | 21.8657 | 429.4665 | 581.8061 | 601.3715 |  | 876.8984 | 884.0286 | 458.5241 | 633.2194 | 753.0836 | 537.3688 | 616.6391 | 784.1135 | 931.9344 | 545.1736 | 735.3066 | 804.1827 | 928.7071 | 968.7796 | 463.8237 | 565.1182 | 615.8542 | 503.6971 | 623.148 | 821.8331 | 846.9984 | 980.5171 | 522.2216 | 608.9739 | 563.5729 | 732.125 | 58.706 | 0.12458 | 18.0308 | 5.7733 | -28.1266 | 3.0951 | 6504.1 | -0.11 | 1.3944 | -0.36697 | -21.4133 | 0.43916 | 6.7805 | -32.0995 | -32.5375 | 57.4043 | 76.4839 | 37.5989 | 26.4514 | 1.2579 | 55.3336 | 26.2157
42838.4292 | 772 | 22.861 | 22.8314 | 22.8279 | 22.7337 | 22.3407 | 21.6492 | 22.6664 | 21.7198 | 22.3165 | 22.3202 | 22.2939 | 21.9339 | 21.1472 | 22.1163 | 21.5865 | 21.7677 | 22.0101 | 21.0652 | 21.5376 | 23.8955 | 22.6206 | 67.9942 | 77.9811 | 22.2191 | 25.7313 | 82.1042 | 645.6689 | 676.188 | 645.9351 | 22.2161 | 24.8277 | 90.4721 | 22.2932 | 26.248 | 88.3236 | 711.3933 | 851.5543 |  | 383.9159 | 894.4375 | 897.2483 | 641.1985 |  | 225.5877 | 407.7599 | 425.0976 | 670.4819 | 700.76 | 798.065 | 865.3978 | 27.8941 | 120.1263 | 36.3228 | 268.9033 | 27.5953 | 45.3341 | 42.9881 | 48.1872 | 27.8504 |  |  | 0.24796 | 0.21218 | -137.7454 | -0.33649 | 8.4881 | -197.7901 | -203.3514 | -3.7229 | 5.4382 | 16.0444 | 13.425 | 0.0053473 | 0.0040708 | 0.0004107 | 22.6919 | 21.9846 | 22.1341 | 22.1849 | 21.9863 | 21.2701 | 20.0784 | 22.1539 | 22.3362 | 22.3659 | 22.3081 | 21.9126 | 21.1364 | 22.228 | 396.9299 | 273.3634 | 279.962 | 195.9836 | 173.7427 | 476.7477 | 271.8833 | 22.3144 | 22.0811 | 21.7784 | 22.0404 | 21.9081 | 23.9295 | 22.1142 | 34.9996 | 74.1381 | 546.343 | 495.6748 | 507.7092 | 521.7069 | 28.3413 | 13.2014 | 731.4377 | 21.9035 | 22.1774 | 234.1385 | 21.5294 | 21.9763 | 22.7909 | 52.6346 | 88.4409 | 21.9721 | 25.0074 | 89.3271 | 696.2781 | 609.0522 | 726.8438 | 737.9944 | 697.2142 |  | 725.6742 | 781.3545 | 802.1388 | 597.3036 | 623.9634 | 776.0603 |  | 390.989 |  |  | 349.6919 | 537.5622 | 649.9313 | [5 empty] | 21.854 | 550.4247 | 21.7211 | 22.0679 | 349.976 | 21.2836 | 21.8701 | 429.9958 | 582.7377 | 601.377 |  | 883.0953 | 883.224 | 457.5001 | 633.2119 | 753.0772 | 538.5779 | 616.1501 | 793.0007 | 931.5858 | 544.9886 | 737.2188 | 799.2293 | 930.171 | 968.8855 | 463.9861 | 565.7905 | 616.4617 | 502.0142 | 622.7602 | 823.9048 | 847.9425 | 982.7273 | 523.6103 | 609.6991 | 562.5769 | 734.4739 | 60.8802 | 0.11481 | 18.0498 | 5.7407 | -28.0886 | 3.0952 | 6439.59 | -0.11 | 1.0521 | 0.83766 | -21.3427 | -1.0549 | 6.6452 | -32.078 | -32.5259 | 57.2244 | 76.3799 | 37.4664 | 26.7991 | 4.1059 | 55.2247 | 26.2563
42838.4292 | 773 | 22.8634 | 22.8403 | 22.8244 | 22.7386 | 22.348 | 21.6591 | 22.6754 | 21.721 | 22.3233 | 22.3248 | 22.2955 | 21.9369 | 21.1405 | 22.1312 | 21.584 | 21.7745 | 22.0106 | 21.0707 | 21.5503 | 23.9386 | 22.6813 | 68.3183 | 78.1327 | 22.2276 | 25.7935 | 82.2147 | 645.2712 | 676.4387 | 644.9147 | 22.2244 | 24.9049 | 90.5476 | 22.3025 | 26.334 | 88.3769 | 710.4748 | 850.5148 |  | 367.3804 | 889.847 | 891.7677 | 642.2957 |  | 226.6872 | 409.5498 | 423.8855 | 664.4017 | 693.315 | 792.3467 | 868.2997 | 28.1312 | 120.739 | 35.9776 | 269.8835 | 27.6821 | 45.1888 | 42.969 | 48.0838 | 27.9096 |  |  | 0.18094 | 0.073531 | -140.2714 | 0.18526 | 9.2996 | -197.8144 | -203.2075 | -3.9509 | 5.9722 | 17.3078 | 13.8201 | 0.0052734 | 0.0040807 | 0.00037949 | 22.6928 | 21.9866 | 22.1294 | 22.1799 | 21.9795 | 21.2617 | 20.0743 | 22.1485 | 22.3344 | 22.3573 | 22.3004 | 21.9069 | 21.132 | 22.2269 | 394.8792 | 258.1228 | 255.9716 | 191.3355 | 165.9486 | 475.506 | 271.2234 | 22.3165 | 22.0965 | 21.7848 | 22.0469 | 21.9176 | 23.9834 | 22.1282 | 35.5492 | 74.2417 | 546.5961 | 496.5102 | 509.261 | 519.626 | 31.7167 | 14.0463 | 733.2166 | 21.9048 | 22.1746 | 233.9348 | 21.5191 | 21.9826 | 22.7993 | 53.4026 | 88.4537 | 21.9729 | 25.0812 | 89.3932 | 699.465 | 610.599 | 727.0536 | 737.6567 | 699.0485 |  | 725.3317 | 782.0966 | 802.3994 | 601.2117 | 623.9353 | 777.849 |  | 393.0676 |  |  | 348.4713 | 538.6021 | 652.6227 | [5 empty] | 21.8585 | 553.625 | 21.7156 | 22.0631 | 352.1669 | 21.2791 | 21.8709 | 430.1298 | 583.2871 | 600.5092 |  | 887.508 | 880.6525 | 456.8232 | 633.6613 | 754.0114 | 539.582 | 615.9446 | 794.8588 | 932.6666 | 544.8412 | 736.3163 | 794.8691 | 931.8148 | 969.1891 | 464.3802 | 566.5173 | 617.5569 | 500.9598 | 622.0958 | 822.6005 | 846.346 | 982.5721 | 524.5003 | 610.1725 | 561.8362 | 734.9078 | 60.7732 | 0.10791 | 18.068 | 5.7054 | -28.0937 | 3.0952 | 6420.33 | -0.12 | 0.89819 | 0.49376 | -21.5658 | 0.78375 | 6.9371 | -31.9943 | -32.4275 | 57.0865 | 76.44 | 37.3525 | 26.7705 | 6.674 | 54.9702 | 26.3527
42838.4292 | 774 | 22.8587 | 22.8338 | 22.8244 | 22.737 | 22.3471 | 21.6611 | 22.6685 | 21.7232 | 22.3256 | 22.3207 | 22.2949 | 21.933 | 21.1496 | 22.1163 | 21.5732 | 21.7687 | 22.0003 | 21.0663 | 21.5554 | 23.9707 | 22.7244 | 68.6239 | 78.2635 | 22.219 | 25.8464 | 82.3189 | 642.63 | 677.753 | 642.359 | 22.2249 | 24.9647 | 90.6153 | 22.3074 | 26.403 | 88.4496 | 710.3676 | 849.5108 |  | 365.1367 | 887.5719 | 889.141 | 646.0002 |  | 227.9575 | 412.0358 | 424.1289 | 658.4966 | 690.011 | 794.0289 | 869.5284 | 28.5334 | 121.4111 | 35.8384 | 271.0204 | 27.8139 | 45.0431 | 42.9655 | 47.991 | 27.9648 |  |  | 0.45627 | -0.053949 | -139.3264 | -0.31677 | 8.9895 | -197.777 | -203.174 | -4.5791 | 5.9229 | 17.1267 | 13.573 | 0.0051961 | 0.0038868 | 0.00034334 | 22.7108 | 21.9865 | 22.1382 | 22.1795 | 21.9922 | 21.2578 | 20.0816 | 22.1589 | 22.3311 | 22.3622 | 22.3071 | 21.912 | 21.1337 | 22.227 | 389.4638 | 258.4954 | 248.9109 | 188.3869 | 162.3997 | 474.4878 | 270.6172 | 22.3145 | 22.0856 | 21.7792 | 22.0449 | 21.9153 | 24.0177 | 22.1336 | 36.0776 | 74.3242 | 546.6146 | 496.1114 | 508.8137 | 516.4862 | 29.3939 | 14.9988 | 734.2797 | 21.9082 | 22.18 | 234.2969 | 21.5314 | 21.9907 | 22.8229 | 54.1543 | 88.472 | 21.9851 | 25.1603 | 89.4633 | 706.0627 | 612.8485 | 729.9889 | 740.2816 | 709.9008 |  | 725.4508 | 789.1366 | 802.901 | 604.519 | 623.9703 | 784.1605 |  | 395.4763 |  |  | 348.4478 | 542.2033 | 659.402 | [5 empty] | 21.8641 | 555.9833 | 21.7186 | 22.0658 | 355.0664 | 21.2844 | 21.8704 | 429.9549 | 583.6755 | 600.8943 |  | 893.8955 | 880.6139 | 456.0199 | 632.4825 | 753.6784 | 540.5948 | 616.6634 | 802.3104 | 933.7723 | 544.197 | 736.7705 | 791.7712 | 931.4331 | 969.6804 | 464.2542 | 566.9201 | 617.6092 | 500.254 | 621.7008 | 821.9076 | 850.0785 | 983.1421 | 525.0528 | 609.7601 | 561.4054 | 735.9203 | 59.639 | 0.095472 | 18.0881 | 5.664 | -28.1838 | 3.0951 | 6426.94 | -0.1 | 1.4243 | -0.4237 | -21.5322 | -1.0267 | 6.8258 | -32.0165 | -32.4504 | 56.8153 | 76.4 | 37.2673 | 27.1624 | 7.369 | 54.8412 | 26.4428
42838.4292 | 775 | 22.8623 | 22.8367 | 22.8249 | 22.7345 | 22.3505 | 21.6656 | 22.6705 | 21.7214 | 22.3251 | 22.328 | 22.2895 | 21.936 | 21.1543 | 22.1202 | 21.5749 | 21.7617 | 22.0132 | 21.0602 | 21.5666 | 24.0218 | 22.7837 | 68.9411 | 78.4086 | 22.2337 | 25.9096 | 82.4205 | 643.7433 | 679.5108 | 644.0106 | 22.2281 | 25.0328 | 90.6711 | 22.3091 | 26.4818 | 88.5258 | 709.5985 | 856.9673 |  | 365.6499 | 887.0072 | 888.0357 | 639.8293 |  | 229.2556 | 414.6212 | 425.4074 | 655.4209 | 683.2736 | 792.0276 | 866.8918 | 28.9395 | 122.2086 | 35.7638 | 272.4698 | 27.9399 | 44.9042 | 42.9722 | 47.8919 | 28.0038 |  |  | 0.42473 | -0.063149 | -146.4252 | -0.77478 | 8.6977 | -197.8604 | -203.1911 | -4.0061 | 5.5843 | 16.3251 | 13.1059 | 0.0051781 | 0.003923 | 0.00040413 | 22.7107 | 21.9866 | 22.1321 | 22.1821 | 21.9891 | 21.2642 | 20.0731 | 22.1532 | 22.3268 | 22.3612 | 22.314 | 21.9104 | 21.135 | 22.2307 | 379.0467 | 242.887 | 237.4962 | 183.3782 | 160.4963 | 473.0979 | 269.7871 | 22.309 | 22.0816 | 21.7727 | 22.0437 | 21.9165 | 24.0583 | 22.1394 | 36.5826 | 74.4152 | 546.4701 | 496.4674 | 508.455 | 512.9753 | 29.3143 | 11.1254 | 738.1571 | 21.8996 | 22.1792 | 233.6894 | 21.5271 | 21.9785 | 22.8244 | 54.8617 | 88.4866 | 21.9877 | 25.2361 | 89.5179 | 710.3132 | 614.5068 | 730.9221 | 741.06 | 708.795 |  | 725.3933 | 801.6843 | 804.0187 | 602.8274 | 623.9081 | 792.1378 |  | 397.6303 |  |  | 348.7629 | 546.3665 | 662.9921 | [5 empty] | 21.86 | 557.4281 | 21.7193 | 22.0681 | 356.7258 | 21.294 | 21.8716 | 430.0922 | 583.8469 | 601.297 |  | 900.8392 | 879.3202 | 455.3423 | 634.4838 | 753.3906 | 540.9275 | 616.9045 | 809.441 | 933.4103 | 543.9711 | 738.2646 | 790.84 | 937.452 | 969.0185 | 464.2786 | 567.0774 | 617.9233 | 499.0759 | 621.6856 | 823.761 | 851.0425 | 986.3097 | 525.8781 | 609.2665 | 560.9928 | 736.6865 | 65.9486 | 0.10412 | 18.1049 | 5.6364 | -28.1655 | 3.0952 | 6441.64 | -0.1 | 1.3754 | -0.45927 | -22.1155 | -1.6087 | 6.7078 | -31.9932 | -32.4213 | 56.8314 | 76.3988 | 37.3024 | 28.0341 | 8.5149 | 54.8255 | 26.5182
42838.4293 | 776 | 22.8627 | 22.8409 | 22.8237 | 22.7353 | 22.353 | 21.6676 | 22.6763 | 21.7219 | 22.3268 | 22.3296 | 22.2975 | 21.9382 | 21.1558 | 22.1253 | 21.5662 | 21.7629 | 21.9985 | 21.054 | 21.567 | 24.0561 | 22.8375 | 69.2504 | 78.5468 | 22.2185 | 25.9645 | 82.5129 | 645.8777 | 678.7797 | 646.2786 | 22.2243 | 25.1008 | 90.7216 | 22.3043 | 26.5556 | 88.585 | 708.4203 | 851.9655 |  | 365.7192 | 885.3343 | 885.3221 | 633.2028 |  | 230.3457 | 416.185 | 428.6128 | 658.012 | 682.432 | 790.3768 | 863.3853 | 29.0597 | 122.7695 | 35.9309 | 273.5048 | 28.0531 | 44.7667 | 42.9898 | 47.7964 | 28.0653 |  |  | 0.44313 | -0.1604 | -143.94 | -0.12293 | 8.9934 | -197.8355 | -203.2923 | -3.8129 | 5.6589 | 16.7894 | 12.6679 | 0.0050072 | 0.0038178 | 0.00036963 | 22.7222 | 21.99 | 22.1302 | 22.1896 | 21.9826 | 21.2594 | 20.0749 | 22.1606 | 22.3252 | 22.3637 | 22.3069 | 21.909 | 21.1285 | 22.2216 | 380.3255 | 243.583 | 231.3687 | 172.2857 | 153.9211 | 471.8106 | 268.9318 | 22.3172 | 22.0849 | 21.7784 | 22.0408 | 21.9325 | 24.1171 | 22.1541 | 37.1264 | 74.5273 | 546.1574 | 497.1253 | 508.3297 | 511.0131 | 31.3345 | 18.9253 | 742.2966 | 21.8948 | 22.182 | 233.4097 | 21.523 | 21.98 | 22.8283 | 55.5654 | 88.499 | 21.9775 | 25.3143 | 89.5554 | 716.8836 | 615.2345 | 730.5926 | 740.172 | 715.3218 |  | 725.6935 | 806.0688 | 805.1154 | 601.6119 | 623.697 | 795.1372 |  | 399.8109 |  |  | 350.2479 | 549.4895 | 666.0415 | [5 empty] | 21.8575 | 557.5223 | 21.7182 | 22.0587 | 359.4715 | 21.2857 | 21.8701 | 430.0683 | 584.2131 | 601.6079 |  | 902.7563 | 877.4926 | 454.9032 | 637.7318 | 751.7146 | 541.1489 | 616.7501 | 817.0935 | 936.8724 | 544.5411 | 739.7045 | 787.3355 | 936.751 | 967.2726 | 464.2867 | 567.221 | 619.4512 | 497.7196 | 621.6799 | 822.9683 | 848.776 | 986.3921 | 525.7761 | 610.18 | 560.286 | 735.9197 | 56.7753 | 0.088219 | 18.1235 | 5.5953 | -28.122 | 3.0951 | 6497.85 | -0.04 | 1.4067 | -0.7328 | -21.9519 | -0.64151 | 6.8156 | -31.9664 | -32.4042 | 56.7263 | 76.6188 | 37.2958 | 27.6279 | 9.0697 | 54.7237 | 26.525
42838.4293 | 777 | 22.8554 | 22.8354 | 22.8264 | 22.7371 | 22.3392 | 21.6583 | 22.6706 | 21.7121 | 22.333 | 22.3294 | 22.2928 | 21.9395 | 21.1509 | 22.1247 | 21.577 | 21.768 | 22.0162 | 21.0552 | 21.5931 | 24.1107 | 22.9106 | 69.5815 | 78.7042 | 22.2356 | 26.0508 | 82.6331 | 647.4968 | 679.8121 | 648.1962 | 22.2258 | 25.1645 | 90.7737 | 22.3056 | 26.6398 | 88.6403 | 707.2065 | 852.5001 |  | 365.668 | 884.1835 | 883.4413 | 631.1214 |  | 231.1626 | 418.4331 | 430.3998 | 663.6089 | 682.7365 | 790.2704 | 860.2548 | 29.0828 | 123.4361 | 36.3845 | 274.6358 | 28.2017 | 44.6427 | 43.0077 | 47.7103 | 28.1216 |  |  | -0.001742 | -0.070377 | -141.7341 | -0.22609 | 9.253 | -197.8558 | -203.172 | -4.1507 | 5.3864 | 16.4875 | 12.9062 | 0.0049809 | 0.0037242 | 0.00036799 | 22.7175 | 21.974 | 22.1267 | 22.1733 | 21.9807 | 21.2595 | 20.0728 | 22.1492 | 22.3249 | 22.3538 | 22.3075 | 21.9045 | 21.1285 | 22.2143 | 371.3698 | 248.294 | 236.6783 | 173.2171 | 158.8991 | 470.3454 | 268.2473 | 22.3141 | 22.079 | 21.7719 | 22.0442 | 21.9203 | 24.16 | 22.1579 | 37.697 | 74.6285 | 546.0597 | 497.4235 | 508.4091 | 512.4754 | 30.0405 | 14.1597 | 746.4176 | 21.8942 | 22.1803 | 233.3231 | 21.5282 | 21.974 | 22.8382 | 56.273 | 88.5058 | 21.9766 | 25.39 | 89.607 | 718.9576 | 616.8638 | 729.5952 | 738.3829 | 717.9583 |  | 725.9533 | 802.8012 | 806.0262 | 602.7041 | 623.5564 | 796.2255 |  | 402.2338 |  |  | 350.1984 | 552.5314 | 669.1105 | [5 empty] | 21.8621 | 558.839 | 21.7216 | 22.0687 | 359.2853 | 21.2925 | 21.8699 | 429.9347 | 584.505 | 603.4116 |  | 902.5738 | 875.157 | 454.5417 | 641.1121 | 750.2704 | 541.7446 | 616.604 | 823.462 | 935.4031 | 545.1535 | 740.3461 | 783.8474 | 939.2219 | 966.6508 | 463.9453 | 567.5657 | 621.1376 | 497.1544 | 621.0994 | 822.4388 | 851.8402 | 985.7148 | 525.4644 | 611.4673 | 559.4909 | 734.7031 | 59.0989 | 0.080249 | 18.1439 | 5.5518 | -28.0749 | 3.0952 | 6566.97 | -0.03 | -0.088288 | -0.48619 | -21.8186 | -0.87142 | 6.9129 | -31.9664 | -32.393 | 56.719 | 76.9942 | 37.2385 | 28.3232 | 8.379 | 54.4879 | 26.4695
42838.4293 | 778 | 22.8593 | 22.8296 | 22.8221 | 22.7381 | 22.3388 | 21.6518 | 22.6699 | 21.7106 | 22.3175 | 22.3281 | 22.292 | 21.9294 | 21.1517 | 22.1163 | 21.5795 | 21.7644 | 22.0176 | 21.0608 | 21.6104 | 24.1615 | 22.9717 | 69.8841 | 78.8323 | 22.2481 | 26.1101 | 82.714 | 649.3023 | 679.3532 | 649.9372 | 22.2291 | 25.2323 | 90.8227 | 22.3131 | 26.7236 | 88.687 | 706.3934 | 851.738 |  | 364.6314 | 884.1448 | 883.9395 | 630.684 |  | 232.2739 | 420.7243 | 429.8018 | 659.8322 | 680.2955 | 794.7175 | 861.1549 | 29.0536 | 124.132 | 37.0446 | 275.5397 | 28.3429 | 44.5213 | 43.0426 | 47.6303 | 28.1718 |  |  | -0.09571 | 0.8095 | -148.4426 | -0.10518 | 9.1413 | -197.8565 | -203.2949 | -3.1098 | 5.6089 | 16.4598 | 13.1482 | 0.0050401 | 0.0037981 | 0.00036141 | 22.7198 | 21.9836 | 22.1296 | 22.1753 | 21.988 | 21.2615 | 20.075 | 22.1467 | 22.328 | 22.3531 | 22.3015 | 21.9091 | 21.1291 | 22.2176 | 364.4658 | 254.113 | 236.4326 | 169.2222 | 155.33 | 469.1747 | 267.6119 | 22.3109 | 22.0844 | 21.7816 | 22.0462 | 21.9257 | 24.2055 | 22.1618 | 38.2566 | 74.7113 | 546.2368 | 497.9032 | 509.1574 | 515.392 | 27.7008 | 18.9731 | 746.7477 | 21.9008 | 22.1816 | 233.9636 | 21.5293 | 21.9776 | 22.8602 | 56.9563 | 88.5251 | 21.9887 | 25.4723 | 89.6519 | 718.3091 | 617.6764 | 728.608 | 736.7588 | 711.1145 |  | 725.5934 | 802.1843 | 806.7081 | 601.2272 | 623.4246 | 797.7406 |  | 404.3399 |  |  | 350.8646 | 552.673 | 665.5733 | [5 empty] | 21.8453 | 559.3143 | 21.7091 | 22.0527 | 356.6372 | 21.2814 | 21.8586 | 430.471 | 584.7765 | 604.8444 |  | 905.4722 | 872.3527 | 454.3608 | 641.5098 | 749.1471 | 542.3231 | 618.829 | 827.9583 | 937.5525 | 545.2183 | 739.1922 | 780.848 | 943.6452 | 966.4449 | 463.9698 | 568.2037 | 623.1043 | 496.4536 | 621.0514 | 823.2537 | 852.1017 | 984.7559 | 525.4193 | 612.1292 | 558.6915 | 733.9213 | 57.2018 | 0.076303 | 18.1607 | 5.5035 | -28.0277 | 3.0952 | 6606.55 | 0.02 | -0.65504 | 1.6516 | -22.3659 | -0.59536 | 6.8854 | -32.0332 | -32.4705 | 56.8177 | 77.2248 | 37.2543 | 28.8514 | 8.3129 | 54.3039 | 26.4155
42838.4293 | 779 | 22.8547 | 22.8304 | 22.8307 | 22.7391 | 22.348 | 21.6669 | 22.6761 | 21.72 | 22.3284 | 22.3289 | 22.2967 | 21.9393 | 21.1509 | 22.1226 | 21.5747 | 21.7625 | 22.0129 | 21.063 | 21.6186 | 24.2027 | 23.0283 | 70.1806 | 78.9656 | 22.2463 | 26.172 | 82.7993 | 649.9468 | 678.8989 | 650.7594 | 22.2261 | 25.3042 | 90.8571 | 22.3075 | 26.803 | 88.7212 | 705.4519 | 843.7685 |  | 363.0996 | 882.6652 | 883.4074 | 634.1751 |  | 233.3207 | 423.2828 | 428.9431 | 663.8438 | 681.6106 | 795.6738 | 860.3911 | 29.0116 | 124.7278 | 38.195 | 276.4297 | 28.5086 | 44.3837 | 43.0887 | 47.5537 | 28.2215 |  |  | -0.22845 | -0.20048 | -141.8971 | 0.094582 | 9.5809 | -197.8079 | -203.2226 | -3.4712 | 5.9786 | 18.032 | 13.0429 | 0.0050138 | 0.003785 | 0.00038606 | 22.735 | 21.9831 | 22.1314 | 22.1757 | 21.9892 | 21.2658 | 20.0795 | 22.153 | 22.3356 | 22.3663 | 22.3078 | 21.9106 | 21.1292 | 22.2221 | 364.0144 | 257.0386 | 248.6186 | 176.0106 | 155.3349 | 468.1177 | 267.1811 | 22.3119 | 22.076 | 21.7854 | 22.0384 | 21.9301 | 24.2565 | 22.1724 | 38.7662 | 74.8012 | 546.2877 | 498.4272 | 509.4194 | 514.0556 | 25.9764 | 17.3875 | 748.7681 | 21.9037 | 22.1796 | 234.2799 | 21.5252 | 21.9795 | 22.87 | 57.6219 | 88.5389 | 21.9925 | 25.5527 | 89.6913 | 717.2519 | 617.4393 | 728.1075 | 736.0034 | 708.0648 |  | 725.2222 | 802.4041 | 807.5063 | 600.2224 | 623.2563 | 798.5773 |  | 406.4193 |  |  | 352.7453 | 551.8395 | 662.6995 | [5 empty] | 21.8517 | 559.0203 | 21.715 | 22.0658 | 355.1021 | 21.2838 | 21.8685 | 431.1652 | 585.2376 | 608.1222 |  | 907.9655 | 869.5871 | 453.6607 | 640.9238 | 748.1201 | 542.8227 | 621.1219 | 835.8028 | 931.7138 | 545.4308 | 737.2286 | 779.3903 | 946.1157 | 963.296 | 464.0917 | 568.9335 | 624.1019 | 495.7269 | 621.2952 | 821.9708 | 848.9765 | 983.5329 | 526.1419 | 612.671 | 557.9857 | 733.2691 | 53.7583 | 0.074119 | 18.1784 | 5.4525 | -28.0971 | 3.0952 | 6606.13 | -0.07 | -1.0124 | -0.82347 | -21.9075 | 0.5656 | 7.0522 | -32.0436 | -32.4793 | 56.8083 | 77.4691 | 37.2501 | 28.6862 | 6.8956 | 53.9804 | 26.4604
42838.4293 | 780 | 22.8603 | 22.8409 | 22.8179 | 22.7375 | 22.3423 | 21.661 | 22.6741 | 21.718 | 22.3175 | 22.3196 | 22.2872 | 21.9341 | 21.1433 | 22.1194 | 21.5706 | 21.7649 | 22.0102 | 21.0598 | 21.624 | 24.2535 | 23.0893 | 70.4681 | 79.0871 | 22.2422 | 26.2385 | 82.8971 | 649.9178 | 678.2074 | 650.007 | 22.2302 | 25.3907 | 90.9176 | 22.3154 | 26.9023 | 88.7813 | 705.1872 | 835.7929 |  | 362.5248 | 877.8147 | 881.749 | 637.5508 |  | 234.6941 | 426.2038 | 428.6151 | 661.766 | 684.4831 | 797.3211 | 862.4169 | 29.241 | 125.499 | 38.8116 | 277.7383 | 28.5624 | 44.2346 | 43.1359 | 47.4771 | 28.255 |  |  | 0.28411 | 0.2457 | -145.4166 | 0.2858 | 8.8489 | -197.846 | -203.2345 | -3.1808 | 5.5742 | 16.8848 | 13.4706 | 0.0048873 | 0.003716 | 0.00034006 | 22.7437 | 21.9877 | 22.1333 | 22.1862 | 21.9868 | 21.2657 | 20.0789 | 22.1501 | 22.3271 | 22.3647 | 22.3096 | 21.909 | 21.13 | 22.219 | 359.0202 | 247.5321 | 259.2031 | 188.7918 | 166.3766 | 466.9346 | 266.8056 | 22.3118 | 22.0837 | 21.7872 | 22.0515 | 21.9431 | 24.2989 | 22.1916 | 39.2574 | 74.8986 | 546.3499 | 499.2156 | 510.4396 | 514.4351 | 32.312 | 11.4136 | 749.4338 | 21.9107 | 22.1789 | 235.7845 | 21.5281 | 21.9821 | 22.8866 | 58.2791 | 88.5675 | 21.9998 | 25.6476 | 89.741 | 712.43 | 617.1159 | 726.7506 | 734.2304 | 699.9223 |  | 724.5705 | 798.8112 | 808.307 | 599.3094 | 623.0464 | 799.1598 |  | 408.588 |  |  | 356.2131 | 551.2727 | 660.8702 | [5 empty] | 21.8582 | 558.7724 | 21.7162 | 22.064 | 354.9436 | 21.2866 | 21.865 | 432.0197 | 585.3446 | 610.0312 |  | 914.5422 | 870.228 | 453.1363 | 640.696 | 749.4867 | 543.6569 | 621.212 | 839.925 | 929.5651 | 545.8866 | 736.8885 | 775.8411 | 947.2321 | 959.8104 | 464.8272 | 569.8645 | 625.2947 | 494.7339 | 620.7508 | 819.9987 | 848.8446 | 981.4592 | 526.8618 | 613.4357 | 557.0008 | 729.9894 | 54.983 | 0.071395 | 18.1999 | 5.3992 | -28.12 | 3.0952 | 6593.31 | -0.11 | 1.1286 | 0.91351 | -22.224 | 0.98525 | 6.7826 | -32.0714 | -32.5052 | 56.8694 | 77.8206 | 37.2353 | 29.0007 | 5.6644 | 53.823 | 26.4594
42838.4293 | 781 | 22.8617 | 22.8338 | 22.8202 | 22.7279 | 22.3353 | 21.6559 | 22.6607 | 21.7085 | 22.3174 | 22.3182 | 22.2924 | 21.9239 | 21.1425 | 22.1156 | 21.5694 | 21.768 | 22.0082 | 21.0624 | 21.646 | 24.3006 | 23.1638 | 70.758 | 79.213 | 22.2433 | 26.3037 | 82.9912 | 649.134 | 677.1051 | 649.2699 | 22.2342 | 25.4678 | 90.9452 | 22.3103 | 26.9875 | 88.8193 | 704.8138 | 838.6376 |  | 362.1613 | 872.6863 | 880.0451 | 637.6612 |  | 236.2316 | 428.8755 | 428.6386 | 653.9613 | 682.3446 | 801.926 | 865.0078 | 29.3111 | 126.0748 | 38.6475 | 278.7349 | 28.6904 | 44.0977 | 43.1921 | 47.4018 | 28.2982 |  |  | 0.51278 | 0.13793 | -151.0533 | 0.094582 | 9.2832 | -197.8545 | -203.312 | -3.5698 | 5.912 | 17.0466 | 13.2191 | 0.004815 | 0.0037061 | 0.00037291 | 22.7511 | 21.9851 | 22.138 | 22.1866 | 21.984 | 21.2591 | 20.0735 | 22.152 | 22.329 | 22.3504 | 22.3059 | 21.9095 | 21.1293 | 22.2253 | 366.923 | 241.4813 | 247.0459 | 186.3913 | 165.0295 | 466.1496 | 266.1601 | 22.3164 | 22.0855 | 21.7887 | 22.0487 | 21.9423 | 24.3579 | 22.1909 | 39.8388 | 75.0055 | 546.4919 | 500.8295 | 511.8856 | 516.2963 | 38.6036 | 18.7254 | 749.1697 | 21.9006 | 22.1733 | 237.8259 | 21.53 | 21.975 | 22.8959 | 58.9293 | 88.5858 | 22.0008 | 25.7307 | 89.7682 | 707.7856 | 616.9641 | 725.5384 | 732.0704 | 692.9744 |  | 723.7082 | 806.1753 | 809.7412 | 601.3872 | 622.9901 | 802.9378 |  | 410.8724 |  |  | 357.4126 | 549.8698 | 655.6406 | [5 empty] | 21.8561 | 559.2774 | 21.7152 | 22.0613 | 356.2637 | 21.2797 | 21.8672 | 432.3473 | 585.294 | 611.4037 |  | 919.3213 | 869.8985 | 452.7916 | 639.854 | 750.9727 | 544.5623 | 620.9724 | 842.4933 | 924.0068 | 545.959 | 736.6582 | 773.4359 | 952.232 | 958.4396 | 465.1271 | 570.4782 | 625.6168 | 494.2791 | 620.179 | 819.5577 | 850.6052 | 979.7624 | 527.8026 | 613.8764 | 556.4395 | 729.9095 | 56.973 | 0.070924 | 18.2205 | 5.338 | -28.1163 | 3.0952 | 6538.06 | -0.07 | 1.5156 | 0.68575 | -22.6939 | 0.56787 | 6.962 | -32.141 | -32.5813 | 56.8445 | 78.0681 | 37.1669 | 27.9633 | 6.9204 | 53.7303 | 26.4293
42838.4293 | 782 | 22.8611 | 22.8346 | 22.8267 | 22.7366 | 22.342 | 21.6653 | 22.6713 | 21.7133 | 22.3279 | 22.3258 | 22.2966 | 21.9323 | 21.1488 | 22.1275 | 21.5712 | 21.7671 | 22.0103 | 21.0596 | 21.6606 | 24.3496 | 23.2248 | 71.038 | 79.3399 | 22.2509 | 26.3762 | 83.0743 | 651.5599 | 676.2543 | 651.9216 | 22.2276 | 25.5357 | 90.9651 | 22.3094 | 27.0615 | 88.8461 | 704.3337 | 852.8963 |  | 362.2789 | 870.1772 | 880.5787 | 640.4287 |  | 238.0223 | 431.9025 | 428.6679 | 649.4155 | 682.4383 | 799.6203 | 862.957 | 29.4551 | 126.7249 | 38.3075 | 279.8259 | 28.8495 | 43.9529 | 43.2714 | 47.3324 | 28.3283 |  |  | 0.3439 | -0.64404 | -149.0445 | 0.16555 | 9.3719 | -197.8657 | -203.2364 | -3.236 | 6.1818 | 17.56 | 13.5633 | 0.0047542 | 0.0036223 | 0.00040084 | 22.7488 | 21.9795 | 22.1236 | 22.1786 | 21.9688 | 21.251 | 20.0703 | 22.1487 | 22.3115 | 22.3507 | 22.2989 | 21.9059 | 21.1297 | 22.2131 | 378.6222 | 251.162 | 265.9423 | 184.3362 | 165.6818 | 465.8889 | 265.8818 | 22.3148 | 22.0847 | 21.7844 | 22.0413 | 21.9446 | 24.4061 | 22.1892 | 40.4012 | 75.0953 | 546.5988 | 502.2867 | 512.7021 | 517.3436 | 36.1351 | 20.7558 | 751.9793 | 21.903 | 22.1814 | 237.978 | 21.533 | 21.9821 | 22.9078 | 59.5825 | 88.6038 | 22.0024 | 25.8225 | 89.78 | 705.7416 | 616.7957 | 724.2343 | 729.9593 | 691.7596 |  | 722.986 | 815.0011 | 811.1788 | 604.5101 | 623.1201 | 806.0936 |  | 412.9325 |  |  | 357.2277 | 548.2365 | 653.3029 | [5 empty] | 21.8543 | 560.7445 | 21.7146 | 22.0648 | 360.6646 | 21.2831 | 21.8699 | 432.5305 | 585.8568 | 611.6104 |  | 922.0211 | 867.9152 | 452.5305 | 638.2643 | 753.7738 | 545.9792 | 621.5431 | 847.559 | 922.9113 | 545.3664 | 735.6698 | 769.2654 | 955.9323 | 956.396 | 465.1302 | 571.1128 | 626.528 | 493.9522 | 620.5322 | 818.8345 | 849.2241 | 980.5539 | 528.4377 | 614.0663 | 556.2506 | 731.7315 | 55.6265 | 0.071023 | 18.243 | 5.2607 | -28.1377 | 3.0952 | 6514.9 | -0.14 | 1.243 | -1.485 | -22.591 | 0.75291 | 6.9877 | -32.1074 | -32.5403 | 56.6961 | 78.2778 | 37.1049 | 26.6105 | 4.78 | 53.5383 | 26.4166
42838.4293 | 783 | 22.8586 | 22.8283 | 22.8247 | 22.7325 | 22.3406 | 21.663 | 22.67 | 21.7173 | 22.3206 | 22.3151 | 22.295 | 21.9278 | 21.1461 | 22.12 | 21.5708 | 21.7722 | 22.0155 | 21.0617 | 21.6747 | 24.409 | 23.2897 | 71.3084 | 79.4676 | 22.2518 | 26.453 | 83.1629 | 652.0984 | 676.0818 | 652.7096 | 22.2281 | 25.6118 | 91.001 | 22.3128 | 27.1438 | 88.8832 | 704.1343 | 851.0148 |  | 361.1012 | 866.8419 | 876.8338 | 639.1708 |  | 239.3322 | 434.8931 | 430.4178 | 649.9963 | 685.7908 | 799.3838 | 861.0146 | 29.7623 | 127.3901 | 38.8423 | 280.9632 | 29.0053 | 43.8145 | 43.3559 | 47.2522 | 28.3401 |  |  | 0.18422 | 0.020963 | -148.0693 | 0.058438 | 9.5079 | -197.8598 | -203.3067 | -3.3089 | 6.1267 | 17.9187 | 12.4785 | 0.0046212 | 0.0036256 | 0.00038277 | 22.7643 | 21.9812 | 22.1285 | 22.1788 | 21.9777 | 21.2507 | 20.0688 | 22.1458 | 22.3252 | 22.3522 | 22.3004 | 21.8971 | 21.1274 | 22.2215 | 391.0703 | 260.6436 | 269.5003 | 187.7399 | 173.3296 | 465.7438 | 265.6891 | 22.3118 | 22.0791 | 21.7926 | 22.0436 | 21.9504 | 24.4569 | 22.2 | 41.0459 | 75.1937 | 546.9221 | 504.0116 | 514.9671 | 522.3616 | 26.7156 | 16.9765 | 754.8548 | 21.9068 | 22.1761 | 238.6937 | 21.5305 | 21.9851 | 22.9176 | 60.2252 | 88.6269 | 22.0119 | 25.9111 | 89.7745 | 703.0109 | 616.8364 | 724.8886 | 730.6023 | 691.7559 |  | 722.2989 | 805.2048 | 812.1544 | 605.8588 | 623.2249 | 805.5224 |  | 415.0121 |  |  | 357.5371 | 547.1009 | 652.1869 | [5 empty] | 21.8537 | 561.8517 | 21.72 | 22.0607 | 364.5476 | 21.2823 | 21.8639 | 433.0943 | 587.4024 | 612.9492 |  | 925.8751 | 866.3484 | 452.2196 | 637.2724 | 756.2133 | 547.2846 | 622.7612 | 854.3903 | 919.0038 | 544.8723 | 736.2896 | 765.9722 | 959.5666 | 953.0025 | 465.1426 | 571.4094 | 628.3497 | 493.6981 | 620.6179 | 817.3518 | 848.0018 | 983.1383 | 528.7723 | 613.2045 | 556.3199 | 731.4486 | 57.0194 | 0.072413 | 18.2637 | 5.1872 | -28.1036 | 3.0952 | 6520.27 | -0.04 | 0.91014 | 0.26849 | -22.5647 | 0.44827 | 7.0375 | -32.1034 | -32.5423 | 56.5233 | 78.8595 | 37.0875 | 25.198 | 4.3564 | 53.5255 | 26.3266
42838.4294 | 784 | 22.8558 | 22.8352 | 22.8232 | 22.7342 | 22.3404 | 21.6607 | 22.6732 | 21.7156 | 22.3253 | 22.3192 | 22.2908 | 21.9293 | 21.1472 | 22.1233 | 21.5668 | 21.7672 | 22.0123 | 21.0583 | 21.6869 | 24.4589 | 23.3595 | 71.57 | 79.59 | 22.2522 | 26.5207 | 83.2409 | 653.4371 | 675.2564 | 654.0056 | 22.2351 | 25.6961 | 91.0273 | 22.3251 | 27.234 | 88.9318 | 703.4947 | 845.6745 |  | 361.6597 | 862.6429 | 872.7044 | 630.989 |  | 240.1695 | 436.938 | 433.9104 | 649.6565 | 684.7677 | 801.1079 | 859.2076 | 30.1422 | 128.0448 | 39.3723 | 282.0217 | 29.1662 | 43.6747 | 43.435 | 47.1732 | 28.3939 |  |  | -0.24027 | 0.23058 | -147.4241 | -0.15907 | 9.0328 | -197.8263 | -203.3435 | -3.2288 | 6.0498 | 17.9775 | 12.9955 | 0.0046557 | 0.0035221 | 0.00034663 | 22.7634 | 21.9787 | 22.128 | 22.173 | 21.973 | 21.2528 | 20.0775 | 22.1516 | 22.3293 | 22.3533 | 22.2947 | 21.9048 | 21.1363 | 22.2196 | 371.2104 | 239.4373 | 245.2338 | 182.2595 | 171.5684 | 464.7099 | 265.1535 | 22.3003 | 22.0747 | 21.7818 | 22.0349 | 21.9512 | 24.5049 | 22.2027 | 41.7875 | 75.2761 | 547.2843 | 505.3086 | 516.8045 | 525.2632 | 25.9447 | 11.4449 | 751.9695 | 21.9016 | 22.1698 | 240.8327 | 21.5258 | 21.977 | 22.9269 | 60.8446 | 88.6418 | 22.0157 | 25.9923 | 89.749 | 699.937 | 616.9075 | 726.7515 | 732.0881 | 683.4077 |  | 721.2592 | 801.875 | 813.3824 | 607.6396 | 623.3324 | 804.7065 |  | 412.7419 |  |  | 358.7379 | 545.8009 | 649.303 | [5 empty] | 21.8478 | 562.5037 | 21.7194 | 22.062 | 367.3426 | 21.2781 | 21.8709 | 433.6631 | 588.6468 | 614.9238 |  | 930.1167 | 864.2372 | 452.1104 | 637.1893 | 757.0579 | 548.3157 | 623.9996 | 858.8258 | 915.2911 | 544.8233 | 735.7257 | 766.4624 | 957.2396 | 951.3065 | 465.3958 | 571.5791 | 630.2857 | 493.1769 | 620.0381 | 816.5624 | 850.4087 | 982.2328 | 529.3804 | 612.6584 | 555.8174 | 731.7476 | 60.3566 | 0.075172 | 18.2853 | 5.1052 | -28.1102 | 3.0952 | 6556.46 | 0 | -1.0402 | 0.89174 | -22.548 | -0.74065 | 6.8649 | -32.1265 | -32.5714 | 56.494 | 79.3427 | 37.0586 | 27.1954 | 6.9742 | 53.5998 | 26.3013
42838.4294 | 785 | 22.8553 | 22.835 | 22.8196 | 22.7361 | 22.3371 | 21.6559 | 22.6736 | 21.7145 | 22.3286 | 22.3228 | 22.2909 | 21.9318 | 21.1424 | 22.1217 | 21.5637 | 21.766 | 22.0148 | 21.0556 | 21.7061 | 24.5116 | 23.4264 | 71.8216 | 79.7085 | 22.257 | 26.5898 | 83.3022 | 654.1241 | 673.3202 | 654.1144 | 22.2395 | 25.7779 | 91.0718 | 22.3297 | 27.3333 | 88.9649 | 702.2668 | 847.9965 |  | 362.5533 | 856.2053 | 864.0112 | 624.3405 |  | 241.1501 | 438.5082 | 434.7337 | 649.8731 | 682.8014 | 802.0603 | 855.8967 | 30.4539 | 128.8064 | 39.4647 | 283.189 | 29.2914 | 43.5402 | 43.5379 | 47.1035 | 28.4561 |  |  | 0.4221 | 0.32126 | -148.1489 | 0.05121 | 9.4113 | -197.8572 | -203.2009 | -3.627 | 6.367 | 18.9912 | 13.4404 | 0.0044733 | 0.0034548 | 0.00035649 | 22.7687 | 21.9828 | 22.1274 | 22.1731 | 21.9821 | 21.2563 | 20.0768 | 22.1522 | 22.3229 | 22.3559 | 22.3047 | 21.9021 | 21.1353 | 22.2252 | 365.3644 | 236.3552 | 253.9681 | 171.3028 | 162.598 | 463.8719 | 264.8053 | 22.309 | 22.0841 | 21.7886 | 22.0422 | 21.9524 | 24.5569 | 22.2194 | 42.5822 | 75.3739 | 547.7272 | 506.6644 | 518.8434 | 527.1397 | 38.9313 | 30.1859 | 752.7635 | 21.8994 | 22.1684 | 243.6021 | 21.5219 | 21.9749 | 22.943 | 61.4314 | 88.6643 | 22.0229 | 26.0903 | 89.714 | 702.4867 | 616.7081 | 726.9748 | 731.4164 | 686.0999 |  | 720.7656 | 809.2955 | 815.3907 | 608.985 | 623.4741 | 807.6979 |  | 396.7115 |  |  | 360.308 | 545.5356 | 648.667 | [5 empty] | 21.8506 | 563.3374 | 21.726 | 22.0632 | 370.0282 | 21.2871 | 21.8691 | 433.6894 | 589.773 | 616.4553 |  | 935.4724 | 863.4053 | 452.2657 | 637.736 | 756.6371 | 549.2629 | 625.0288 | 862.8932 | 916.9689 | 544.845 | 737.5619 | 769.4837 | 957.121 | 949.2413 | 466.0087 | 572.1926 | 632.5055 | 492.5874 | 619.1423 | 815.2878 | 854.4461 | 980.0628 | 530.4244 | 612.2373 | 554.9518 | 730.601 | 56.5814 | 0.07789 | 18.3061 | 5.0168 | -28.1735 | 3.0952 | 6579.52 | -0.12 | 1.3787 | 1.0537 | -22.6283 | 0.42071 | 7.0103 | -32.1432 | -32.5744 | 56.2955 | 79.7782 | 37.0483 | 27.6756 | 5.9528 | 53.4914 | 26.317
42838.4294 | 786 | 22.8586 | 22.8306 | 22.8175 | 22.7272 | 22.3423 | 21.6548 | 22.6574 | 21.7167 | 22.3218 | 22.3168 | 22.2906 | 21.9366 | 21.1546 | 22.1116 | 21.5653 | 21.7683 | 22.0199 | 21.0587 | 21.7205 | 24.5666 | 23.4901 | 72.0714 | 79.8248 | 22.2617 | 26.6649 | 83.383 | 652.1941 | 672.2351 | 651.783 | 22.239 | 25.8712 | 91.1107 | 22.334 | 27.4109 | 88.9914 | 700.8155 | 847.5949 |  | 363.8469 | 852.473 | 862.2971 | 622.7274 |  | 242.4596 | 440.4982 | 436.2375 | 649.4606 | 683.7708 | 806.8277 | 855.3775 | 30.3749 | 129.444 | 39.7801 | 284.2036 | 29.4353 | 43.4078 | 43.639 | 47.02 | 28.4568 |  |  | 0.47467 | -0.30891 | -149.9165 | -0.54742 | 8.6064 | -197.823 | -203.3705 | -2.8844 | 6.1915 | 19.0153 | 13.6937 | 0.004401 | 0.0034959 | 0.00038606 | 22.781 | 21.9847 | 22.128 | 22.1733 | 21.9794 | 21.2566 | 20.07 | 22.1466 | 22.3201 | 22.3564 | 22.3051 | 21.9007 | 21.1358 | 22.2197 | 386.1302 | 282.719 | 304.1996 | 180.1423 | 167.2219 | 464.0444 | 265.3035 | 22.3133 | 22.0823 | 21.7892 | 22.0459 | 21.9549 | 24.6105 | 22.2255 | 43.3643 | 75.4822 | 548.1078 | 508.1663 | 520.3114 | 525.2253 | 36.9706 | 16.8424 | 756.1332 | 21.9065 | 22.1692 | 245.8276 | 21.5213 | 21.9783 | 22.9606 | 61.9948 | 88.6833 | 22.0206 | 26.1855 | 89.6906 | 700.486 | 616.7864 | 726.5505 | 731.4252 | 690.4045 |  | 720.4011 | 800.9243 | 816.3 | 608.0248 | 623.539 | 805.2857 |  | 394.1322 |  |  | 361.7663 | 546.7221 | 650.3786 | [5 empty] | 21.8536 | 564.0216 | 21.7222 | 22.0603 | 371.2125 | 21.2863 | 21.8637 | 433.1551 | 590.7427 | 618.0609 |  | 937.3563 | 866.1722 | 452.2422 | 638.4351 | 756.6961 | 550.1982 | 625.5284 | 871.5445 | 919.5354 | 544.8473 | 738.6103 | 769.5195 | 959.4519 | 947.2015 | 466.8876 | 572.7797 | 633.2335 | 491.9911 | 618.8253 | 813.1377 | 855.86 | 979.4058 | 531.323 | 612.0038 | 554.4556 | 728.2605 | 54.6318 | 0.082222 | 18.3282 | 4.9379 | -28.1772 | 3.0951 | 6610.35 | -0.19 | 1.4602 | -1.0347 | -22.7947 | -1.3774 | 6.7187 | -32.2116 | -32.6602 | 56.0847 | 80.3024 | 37.0874 | 25.4031 | 0.44446 | 53.1911 | 26.4286
42838.4294 | 787 | 22.8582 | 22.8401 | 22.8258 | 22.7324 | 22.3421 | 21.6553 | 22.6656 | 21.7094 | 22.3178 | 22.3291 | 22.2897 | 21.9303 | 21.1499 | 22.1204 | 21.5703 | 21.769 | 22.0212 | 21.0676 | 21.7455 | 24.6235 | 23.5728 | 72.3271 | 79.9434 | 22.2727 | 26.7495 | 83.5006 | 650.9032 | 670.4939 | 650.2675 | 22.2443 | 25.9574 | 91.1557 | 22.3252 | 27.522 | 89.0356 | 699.7889 | 841.8933 |  | 365.2429 | 851.3442 | 865.2269 | 625.5746 |  | 243.8234 | 442.73 | 438.2171 | 654.2107 | 686.8004 | 813.4485 | 853.3306 | 30.0197 | 130.136 | 39.8256 | 285.4292 | 29.6248 | 43.2851 | 43.759 | 46.9414 | 28.5094 |  |  | 0.39581 | 0.56637 | -153.2744 | 0.22469 | 9.3647 | -197.8381 | -203.2785 | -2.5598 | 6.2253 | 18.1218 | 13.6446 | 0.0043304 | 0.0033283 | 0.00035484 | 22.7962 | 21.9932 | 22.1344 | 22.1827 | 21.9884 | 21.2598 | 20.0756 | 22.1506 | 22.3316 | 22.3623 | 22.3084 | 21.9063 | 21.1438 | 22.217 | 395.8245 | 275.8867 | 293.6955 | 188.8175 | 164.7303 | 463.8478 | 265.1613 | 22.315 | 22.0844 | 21.7913 | 22.0562 | 21.9707 | 24.6652 | 22.2475 | 43.9942 | 75.578 | 548.3379 | 509.5745 | 521.3131 | 524.2086 | 29.9516 | 15.8473 | 753.8526 | 21.9046 | 22.164 | 247.6177 | 21.5142 | 21.9767 | 22.9678 | 62.5367 | 88.7007 | 22.0224 | 26.2777 | 89.6738 | 698.93 | 616.9235 | 728.6723 | 735.2268 | 689.6854 |  | 719.7482 | 801.4969 | 817.4884 | 608.3379 | 623.6556 | 807.1039 |  | 395.0547 |  |  | 361.0932 | 546.6171 | 649.7611 | [5 empty] | 21.852 | 564.6292 | 21.7184 | 22.0611 | 372.5971 | 21.2902 | 21.8642 | 433.0378 | 591.4339 | 618.8687 |  | 939.7474 | 868.95 | 452.1083 | 638.4153 | 757.4913 | 551.1423 | 626.4939 | 879.4562 | 919.2799 | 544.9098 | 738.9105 | 766.8591 | 960.9868 | 945.2943 | 467.2014 | 573.1943 | 633.3023 | 491.6467 | 618.1647 | 810.9016 | 857.5427 | 977.3679 | 531.8621 | 612.0099 | 554.2919 | 725.2467 | 55.364 | 0.082236 | 18.3479 | 4.852 | -28.2041 | 3.0952 | 6600.5 | -0.04 | 1.3323 | 1.4033 | -23.0846 | 0.88385 | 7.0299 | -32.3115 | -32.7527 | 55.9415 | 80.6686 | 37.101 | 24.2863 | 1.5907 | 52.8687 | 26.4921
42838.4294 | 788 | 22.8579 | 22.832 | 22.819 | 22.7317 | 22.3414 | 21.6643 | 22.6695 | 21.7169 | 22.3191 | 22.3285 | 22.2968 | 21.9375 | 21.1463 | 22.124 | 21.5726 | 21.7695 | 22.0177 | 21.0582 | 21.7556 | 24.6789 | 23.6401 | 72.575 | 80.0564 | 22.2714 | 26.8196 | 83.6 | 648.5945 | 669.1728 | 648.1236 | 22.2416 | 26.0404 | 91.1691 | 22.3283 | 27.6067 | 89.0637 | 699.0863 | 844.805 |  | 364.8285 | 850.1524 | 864.7265 | 627.5103 |  | 245.1769 | 445.7919 | 441.3325 | 662.1763 | 692.4367 | 815.6375 | 851.7473 | 29.5388 | 130.7879 | 39.5816 | 286.5133 | 29.7077 | 43.1579 | 43.8776 | 46.8636 | 28.5319 |  |  | 0.3577 | 0.41195 | -151.5225 | 0.10378 | 8.9776 | -197.8486 | -203.2975 | -3.9693 | 6.1594 | 18.9858 | 13.1585 | 0.0041513 | 0.0032889 | 0.00034827 | 22.7888 | 21.9833 | 22.116 | 22.1749 | 21.9781 | 21.2493 | 20.0704 | 22.1487 | 22.3247 | 22.3588 | 22.2967 | 21.9024 | 21.1251 | 22.2129 | 375.0153 | 268.7811 | 278.7892 | 190.3287 | 165.0971 | 462.8612 | 264.6927 | 22.3104 | 22.0818 | 21.7939 | 22.0496 | 21.9643 | 24.7168 | 22.2493 | 44.6682 | 75.6701 | 548.5796 | 510.9702 | 522.3278 | 524.5241 | 29.4153 | 20.0389 | 755.5495 | 21.903 | 22.1678 | 248.1969 | 21.524 | 21.9808 | 22.9831 | 63.0679 | 88.724 | 22.0349 | 26.381 | 89.6669 | 700.3997 | 617.0128 | 733.3999 | 741.377 | 690.4347 |  | 719.0472 | 816.7622 | 819.2202 | 607.2018 | 623.6458 | 814.5898 |  | 396.7554 |  |  | 360.252 | 545.3031 | 648.528 | [5 empty] | 21.8389 | 564.5727 | 21.7092 | 22.0544 | 373.9506 | 21.2843 | 21.8594 | 433.3403 | 591.8871 | 619.2626 |  | 941.4469 | 869.0841 | 451.9921 | 638.0028 | 757.6604 | 551.921 | 627.5142 | 885.5986 | 920.2358 | 544.6807 | 741.3949 | 764.3054 | 961.6078 | 942.906 | 467.3271 | 573.6539 | 632.8839 | 491.2626 | 617.6419 | 809.6554 | 858.7072 | 974.5785 | 532.249 | 612.1482 | 554.3489 | 724.9251 | 56.1752 | 0.086892 | 18.3675 | 4.7594 | -28.159 | 3.0952 | 6552.28 | -0.15 | 1.2651 | 1.1993 | -23.0013 | 0.60197 | 6.89 | -32.3448 | -32.7872 | 55.7457 | 80.8034 | 37.1307 | 26.3994 | 3.1784 | 52.6488 | 26.5205
42838.4294 | 789 | 22.8595 | 22.8403 | 22.8236 | 22.7336 | 22.3446 | 21.6591 | 22.6761 | 21.7199 | 22.3234 | 22.3285 | 22.2952 | 21.9374 | 21.147 | 22.1247 | 21.5635 | 21.761 | 22.02 | 21.0581 | 21.7765 | 24.7356 | 23.7102 | 72.8134 | 80.1825 | 22.2732 | 26.8935 | 83.6844 | 648.7985 | 668.2526 | 648.9161 | 22.2437 | 26.1284 | 91.189 | 22.3298 | 27.7038 | 89.0987 | 698.5815 | 849.8325 |  | 364.4286 | 847.282 | 861.3992 | 626.1008 |  | 246.6372 | 449.2057 | 443.0536 | 667.1578 | 700.5081 | 816.175 | 853.1657 | 29.7279 | 131.413 | 39.4498 | 287.4717 | 29.8451 | 43.03 | 44.0111 | 46.7922 | 28.5249 |  |  | 0.31039 | 0.60382 | -154.0609 | -0.049326 | 8.8705 | -197.8276 | -203.2239 | -3.443 | 6.3343 | 19.2967 | 12.9491 | 0.0042581 | 0.0032429 | 0.00039263 | 22.8034 | 21.9802 | 22.1282 | 22.1725 | 21.9755 | 21.2534 | 20.0707 | 22.1622 | 22.322 | 22.3661 | 22.3043 | 21.9182 | 21.1342 | 22.2199 | 371.1947 | 269.3298 | 282.5597 | 194.0995 | 171.1318 | 462.0033 | 264.3836 | 22.3147 | 22.0768 | 21.7979 | 22.045 | 21.9647 | 24.7705 | 22.2525 | 45.4221 | 75.7642 | 548.7803 | 511.3372 | 522.7711 | 524.7901 | 26.5626 | 14.1608 | 761.3544 | 21.9004 | 22.1747 | 249.0598 | 21.5245 | 21.9794 | 22.9959 | 63.5901 | 88.7437 | 22.0357 | 26.4829 | 89.6804 | 704.1899 | 617.4767 | 737.0988 | 745.8415 | 696.3677 |  | 718.6911 | 816.4458 | 820.3084 | 608.1279 | 623.6486 | 815.8395 |  | 398.2757 |  |  | 361.4982 | 545.1425 | 650.5792 | [5 empty] | 21.8519 | 564.744 | 21.7108 | 22.0582 | 373.9117 | 21.288 | 21.8679 | 433.2429 | 592.0548 | 619.1234 |  | 943.0492 | 868.2324 | 452.0352 | 637.7997 | 756.7612 | 552.3491 | 627.4438 | 890.5282 | 920.4793 | 544.8046 | 745.9952 | 762.7549 | 959.9657 | 940.6355 | 467.2875 | 574.0153 | 633.2403 | 490.6659 | 617.8806 | 808.6008 | 862.304 | 971.8655 | 532.6777 | 612.9372 | 554.3933 | 725.7441 | 57.4025 | 0.095107 | 18.3867 | 4.6778 | -28.1496 | 3.0952 | 6500.76 | -0.08 | 1.179 | 1.4555 | -23.2482 | -0.41599 | 6.8505 | -32.3511 | -32.7894 | 55.4922 | 81.1646 | 37.1055 | 26.6511 | 2.7142 | 52.5688 | 26.5439
42838.4294 | 790 | 22.859 | 22.8351 | 22.8139 | 22.7326 | 22.3436 | 21.66 | 22.6706 | 21.7135 | 22.322 | 22.3196 | 22.2886 | 21.9311 | 21.1421 | 22.1123 | 21.5688 | 21.7645 | 22.0313 | 21.067 | 21.8 | 24.7967 | 23.7843 | 73.0532 | 80.3005 | 22.2833 | 26.9768 | 83.7892 | 649.3222 | 667.2087 | 649.0741 | 22.2445 | 26.2149 | 91.2131 | 22.326 | 27.7959 | 89.1242 | 697.6677 | 846.2437 |  | 364.5874 | 844.2479 | 858.8175 | 622.8925 |  | 248.9349 | 453.3347 | 445.428 | 682.041 | 711.2029 | 818.192 | 855.2428 | 30.1661 | 132.1568 | 39.8125 | 288.7698 | 30.0215 | 42.9202 | 44.1517 | 46.7228 | 28.5462 |  |  | 0.15465 | 0.83184 | -152.1875 | -0.009902 | 8.08 | -197.8453 | -203.2141 | -2.734 | 6.3055 | 19.8938 | 13.8281 | 0.0042023 | 0.0032642 | 0.00037784 | 22.8065 | 21.9903 | 22.1304 | 22.1804 | 21.9783 | 21.2587 | 20.0777 | 22.1513 | 22.3253 | 22.3601 | 22.2984 | 21.9162 | 21.1426 | 22.2214 | 356.0352 | 249.1202 | 278.4565 | 190.9227 | 167.4707 | 461.1218 | 264.1478 | 22.3147 | 22.0699 | 21.7992 | 22.0393 | 21.9701 | 24.8264 | 22.255 | 46.1739 | 75.8628 | 549.0601 | 511.9902 | 523.5445 | 526.5338 | 28.3336 | 21.5712 | 761.6215 | 21.9032 | 22.1801 | 251.7225 | 21.5263 | 21.9829 | 23.0136 | 64.1101 | 88.7632 | 22.039 | 26.584 | 89.7005 | 706.6297 | 618.3402 | 738.3288 | 747.313 | 694.2714 |  | 718.2555 | 809.9515 | 820.9852 | 609.193 | 623.7538 | 813.9011 |  | 396.4236 |  |  | 362.3603 | 545.0324 | 651.1689 | [5 empty] | 21.8572 | 565.6235 | 21.7191 | 22.0632 | 374.4098 | 21.2878 | 21.8636 | 433.431 | 591.9355 | 619.1388 |  | 943.7639 | 868.1322 | 452.3181 | 638.7113 | 757.11 | 552.79 | 627.753 | 888.3134 | 922.0891 | 545.4625 | 745.6055 | 762.1768 | 958.2253 | 939.597 | 467.2891 | 574.2086 | 634.0462 | 490.6092 | 617.7901 | 808.302 | 864.2008 | 971.0235 | 532.8759 | 614.0306 | 554.405 | 725.1572 | 56.899 | 0.10125 | 18.4078 | 4.5997 | -28.119 | 3.0952 | 6456.4 | -0.09 | 0.83227 | 1.7132 | -23.1723 | -0.18691 | 6.5442 | -32.3825 | -32.8189 | 55.442 | 81.5647 | 37.0961 | 28.1583 | 3.1356 | 52.4427 | 26.5385
42838.4294 | 791 | 22.8495 | 22.8283 | 22.8126 | 22.7247 | 22.3403 | 21.6553 | 22.6678 | 21.7146 | 22.3163 | 22.3189 | 22.2821 | 21.9286 | 21.136 | 22.1166 | 21.5784 | 21.7774 | 22.0237 | 21.0667 | 21.8135 | 24.8599 | 23.863 | 73.2919 | 80.4331 | 22.2933 | 27.0654 | 83.9113 | 645.9792 | 665.3457 | 645.091 | 22.2505 | 26.3121 | 91.2339 | 22.3388 | 27.8973 | 89.1595 | 696.838 | 847.8445 |  | 364.5452 | 842.2959 | 859.1446 | 624.8564 |  | 251.0417 | 457.1562 | 448.2487 | 686.6166 | 722.7272 | 822.5669 | 858.8352 | 30.1319 | 132.7942 | 40.2504 | 289.9888 | 30.1682 | 42.8062 | 44.3024 | 46.6497 | 28.5597 |  |  | 0.26768 | 0.20561 | -155.659 | 0.28975 | 9.065 | -197.8335 | -203.2548 | -3.3904 | 6.3452 | 21.0036 | 14.0643 | 0.0040199 | 0.0032133 | 0.00036306 | 22.8089 | 21.9842 | 22.1247 | 22.1759 | 21.9763 | 21.2484 | 20.0681 | 22.1458 | 22.311 | 22.3491 | 22.2997 | 21.8957 | 21.1261 | 22.2179 | 364.8088 | 256.6348 | 290.4047 | 199.3103 | 171.5764 | 460.6195 | 264.2119 | 22.303 | 22.0792 | 21.7882 | 22.0368 | 21.9736 | 24.8766 | 22.2621 | 46.8513 | 75.9588 | 549.3126 | 512.6849 | 523.8658 | 526.5861 | 30.9226 | 21.5799 | 759.3651 | 21.9064 | 22.1716 | 253.43 | 21.5263 | 21.9815 | 23.0309 | 64.6023 | 88.7792 | 22.043 | 26.6847 | 89.7098 | 709.9407 | 619.2672 | 739.0428 | 748.4559 | 697.3517 |  | 717.8899 | 799.0865 | 820.9626 | 610.3404 | 623.8786 | 808.2987 |  | 390.6293 |  |  | 361.9214 | 545.8704 | 652.0967 | [5 empty] | 21.8502 | 566.9276 | 21.7232 | 22.0607 | 374.6162 | 21.2837 | 21.8703 | 434.0389 | 592.3247 | 620.9572 |  | 942.8277 | 868.585 | 452.7387 | 638.8732 | 756.5751 | 553.1862 | 630.219 | 890.7033 | 920.8645 | 545.9846 | 745.0178 | 761.2024 | 956.4321 | 936.0275 | 468.0778 | 574.2624 | 633.7045 | 491.0224 | 617.7204 | 808.3021 | 866.942 | 970.4427 | 533.1419 | 614.8465 | 554.8638 | 722.5311 | 56.119 | 0.10733 | 18.432 | 4.536 | -28.1403 | 3.0952 | 6409.8 | -0.13 | 1.0926 | 0.85397 | -23.4967 | 1.0137 | 6.9455 | -32.4464 | -32.8879 | 55.2655 | 81.8591 | 37.0881 | 27.0826 | 1.8174 | 52.1931 | 26.5759
42838.4294 | 792 | 22.8528 | 22.8251 | 22.8289 | 22.7314 | 22.3398 | 21.6576 | 22.6742 | 21.7226 | 22.3193 | 22.3258 | 22.2894 | 21.9303 | 21.1425 | 22.1206 | 21.5668 | 21.7639 | 22.0255 | 21.0624 | 21.8285 | 24.9153 | 23.9342 | 73.5349 | 80.5468 | 22.2811 | 27.135 | 84.0221 | 644.1709 | 664.6801 | 644.0987 | 22.2517 | 26.4078 | 91.2377 | 22.3448 | 27.9905 | 89.1843 | 695.8924 | 849.2316 |  | 364.5899 | 843.1042 | 858.7144 | 621.2309 |  | 253.6623 | 461.9825 | 450.8496 | 693.3922 | 741.8333 | 828.3485 | 863.4575 | 30.1786 | 133.447 | 40.9321 | 291.4809 | 30.3532 | 42.7224 | 44.4632 | 46.592 | 28.5829 |  |  | 0.069886 | 0.18918 | -156.6953 | 0.029526 | 8.5124 | -197.8663 | -203.356 | -2.6321 | 6.3312 | 20.4797 | 13.6925 | 0.0040396 | 0.0032149 | 0.00036963 | 22.8266 | 21.9834 | 22.1318 | 22.1781 | 21.9751 | 21.251 | 20.0702 | 22.1414 | 22.3177 | 22.3564 | 22.2973 | 21.8978 | 21.1256 | 22.2187 | 359.3009 | 265.4658 | 296.2491 | 200.3516 | 169.5418 | 460.0224 | 264.1425 | 22.3079 | 22.085 | 21.7937 | 22.0426 | 21.9891 | 24.9501 | 22.2761 | 47.4776 | 76.0578 | 549.6065 | 514.2273 | 525.6999 | 529.3838 | 28.8214 | 16.7709 | 755.6146 | 21.9067 | 22.1735 | 255.5409 | 21.5256 | 21.9833 | 23.0435 | 65.0852 | 88.7924 | 22.0486 | 26.7807 | 89.7181 | 708.3355 | 620.258 | 741.2431 | 751.4768 | 695.3763 |  | 717.5029 | 788.8785 | 820.1518 | 608.9568 | 623.9527 | 803.3152 |  | 391.7468 |  |  | 361.4482 | 547.0165 | 652.5583 | [5 empty] | 21.8558 | 566.7786 | 21.721 | 22.0565 | 373.8387 | 21.2918 | 21.8656 | 434.4092 | 593.474 | 623.9467 |  | 942.4569 | 869.3888 | 452.919 | 639.6097 | 758.0587 | 553.6073 | 631.7713 | 889.5883 | 919.5365 | 546.638 | 746.0362 | 761.1481 | 959.6628 | 933.5652 | 468.5257 | 574.4292 | 631.6561 | 491.2641 | 617.5376 | 807.2228 | 863.3777 | 971.0527 | 533.5172 | 614.066 | 555.229 | 720.9417 | 58.7025 | 0.1151 | 18.4541 | 4.4656 | -28.1947 | 3.0952 | 6378.33 | -0.1 | 0.55796 | 0.82185 | -23.6525 | 0.32468 | 6.7482 | -32.5346 | -32.9828 | 55.2242 | 81.8796 | 37.1407 | 27.5748 | 1.1579 | 52.0721 | 26.5435
42838.4295 | 793 | 22.8599 | 22.8336 | 22.8244 | 22.7384 | 22.339 | 21.6584 | 22.6742 | 21.7238 | 22.3177 | 22.325 | 22.2897 | 21.9311 | 21.146 | 22.1192 | 21.5662 | 21.7683 | 22.0183 | 21.0547 | 21.8506 | 24.9743 | 24.0166 | 73.7559 | 80.6451 | 22.2873 | 27.2187 | 84.1384 | 642.2703 | 662.1949 | 642.3694 | 22.2555 | 26.4941 | 91.2562 | 22.3457 | 28.0891 | 89.2095 | 694.8078 | 851.2061 |  | 364.7716 | 840.8512 | 853.6245 | 619.2782 |  | 256.1207 | 466.4207 | 454.7151 | 694.3089 | 758.63 | 834.3808 | 866.4065 | 30.1932 | 134.0674 | 42.3638 | 293.1092 | 30.5172 | 42.6442 | 44.6459 | 46.5414 | 28.6407 |  |  | 0.098142 | 0.65114 | -159.0603 | 0.14649 | 8.657 | -197.8276 | -203.3448 | -2.5743 | 6.1825 | 21.3057 | 14.19 | 0.0038671 | 0.0031262 | 0.00037291 | 22.8306 | 21.9882 | 22.1245 | 22.1755 | 21.9746 | 21.2528 | 20.0752 | 22.1486 | 22.3242 | 22.3574 | 22.303 | 21.9054 | 21.1274 | 22.2244 | 368.5645 | 256.3174 | 287.0447 | 196.2106 | 164.5119 | 459.8991 | 263.8237 | 22.3011 | 22.0829 | 21.7962 | 22.043 | 21.9872 | 24.9987 | 22.285 | 48.171 | 76.1447 | 549.9843 | 515.8188 | 527.2522 | 530.2603 | 30.6674 | 15.9656 | 752.6007 | 21.9059 | 22.1764 | 258.4175 | 21.5254 | 21.9819 | 23.0593 | 65.5732 | 88.8123 | 22.0677 | 26.8868 | 89.7316 | 708.994 | 621.0266 | 744.2812 | 756.3993 | 696.1038 |  | 717.1628 | 792.9483 | 820.2746 | 611.4915 | 624.1906 | 804.6313 |  | 393.3512 |  |  | 363.4088 | 547.5887 | 652.7744 | [5 empty] | 21.8482 | 568.9813 | 21.7143 | 22.0519 | 373.9297 | 21.2797 | 21.8631 | 435.0306 | 593.9486 | 623.8 |  | 940.9259 | 871.007 | 452.9393 | 639.8281 | 758.6108 | 553.9049 | 632.2895 | 884.9932 | 922.3689 | 546.949 | 742.988 | 764.5562 | 957.9062 | 935.2137 | 468.2945 | 574.7515 | 630.7661 | 491.4072 | 617.6264 | 805.6709 | 861.351 | 972.0459 | 533.5159 | 613.302 | 555.3446 | 719.5171 | 58.2736 | 0.12119 | 18.4761 | 4.3959 | -28.1921 | 3.0951 | 6374.37 | -0.08 | 0.66058 | 1.5293 | -23.9022 | 0.72538 | 6.8238 | -32.6203 | -33.0721 | 55.1196 | 81.8063 | 37.1159 | 26.5208 | 2.1339 | 51.8727 | 26.5774
42838.4295 | 794 | 22.856 | 22.8314 | 22.8248 | 22.7336 | 22.3329 | 21.6574 | 22.6656 | 21.7108 | 22.319 | 22.322 | 22.2859 | 21.9338 | 21.1387 | 22.1198 | 21.5599 | 21.7607 | 22.0216 | 21.0522 | 21.8721 | 25.0343 | 24.0838 | 73.9807 | 80.7462 | 22.2798 | 27.2972 | 84.238 | 639.0644 | 661.1152 | 638.6848 | 22.2428 | 26.5866 | 91.2557 | 22.3394 | 28.1796 | 89.2463 | 693.9399 | 843.8245 |  | 365.102 | 835.227 | 843.9115 | 617.2729 |  | 258.6123 | 470.969 | 459.3138 | 690.7505 | 771.0709 | 838.9257 | 871.6949 | 29.8599 | 134.6939 | 44.3956 | 294.6436 | 30.718 | 42.5716 | 44.8214 | 46.5054 | 28.7079 |  |  | 0.071198 | 0.43758 | -155.5177 | -0.1065 | 7.81 | -197.865 | -203.4178 | -3.4134 | 6.3343 | 21.397 | 14.7424 | 0.0037176 | 0.0030704 | 0.00040741 | 22.8402 | 21.9853 | 22.1242 | 22.176 | 21.979 | 21.2533 | 20.073 | 22.1514 | 22.3291 | 22.3618 | 22.3045 | 21.9055 | 21.127 | 22.2209 | 395.6105 | 265.4158 | 275.5232 | 192.4498 | 161.3922 | 459.9182 | 263.4676 | 22.3037 | 22.0765 | 21.8008 | 22.0445 | 21.9989 | 25.0504 | 22.3051 | 48.8652 | 76.2378 | 550.142 | 516.2756 | 527.0059 | 527.9302 | 24.4718 | 19.8272 | 752.1108 | 21.9056 | 22.1656 | 258.358 | 21.5204 | 21.9815 | 23.0727 | 66.0539 | 88.8358 | 22.0762 | 26.9968 | 89.7419 | 710.7028 | 621.8934 | 747.3999 | 761.4646 | 701.0151 |  | 716.9861 | 784.6386 | 819.4826 | 610.7131 | 624.2744 | 800.7422 |  | 395.4694 |  |  | 364.9038 | 548.7692 | 656.095 | [5 empty] | 21.8551 | 569.0349 | 21.7214 | 22.054 | 376.5402 | 21.2804 | 21.8708 | 435.464 | 594.2939 | 624.7842 |  | 936.0787 | 873.0465 | 453.077 | 639.681 | 760.4962 | 554.4054 | 632.5563 | 880.7393 | 923.1142 | 547.0367 | 742.7007 | 766.1851 | 958.0989 | 933.5586 | 468.2815 | 575.1979 | 629.6658 | 491.9208 | 616.9996 | 802.7454 | 863.0026 | 971.7584 | 533.8088 | 613.6605 | 555.1652 | 716.8912 | 58.1977 | 0.12498 | 18.5016 | 4.3328 | -28.3809 | 3.0951 | 6402.53 | -0.05 | 0.56151 | 1.2575 | -23.7071 | -0.62038 | 6.4947 | -32.6903 | -33.1458 | 54.9394 | 81.7806 | 37.1536 | 23.5195 | 3.3621 | 51.7261 | 26.6664
42838.4295 | 795 | 22.8508 | 22.8295 | 22.8173 | 22.7353 | 22.3375 | 21.6538 | 22.6632 | 21.7128 | 22.3111 | 22.3134 | 22.2881 | 21.9289 | 21.14 | 22.1192 | 21.5685 | 21.7636 | 22.0257 | 21.0594 | 21.9004 | 25.1078 | 24.1731 | 74.2031 | 80.8639 | 22.2987 | 27.3933 | 84.3561 | 639.2821 | 659.5907 | 639.2788 | 22.2439 | 26.7031 | 91.2876 | 22.3528 | 28.2958 | 89.2785 | 692.6621 | 843.1827 |  | 362.3822 | 828.0797 | 834.5749 | 619.5929 |  | 261.5807 | 476.0871 | 463.7569 | 696.0134 | 784.879 | 843.5852 | 869.6149 | 29.1255 | 135.4842 | 45.3996 | 296.385 | 30.9157 | 42.5182 | 45.0316 | 46.4553 | 28.7485 |  |  | 0.39253 | 0.63405 | -157.2374 | 0.04661 | 6.8854 | -197.821 | -203.2916 | -2.4691 | 6.3594 | 21.4515 | 13.9888 | 0.0038129 | 0.0031114 | 0.00037456 | 22.8558 | 21.9874 | 22.1363 | 22.1802 | 21.9836 | 21.2576 | 20.0732 | 22.1597 | 22.3348 | 22.3641 | 22.312 | 21.905 | 21.1355 | 22.228 | 372.1252 | 256.4059 | 272.5691 | 194.4069 | 162.5988 | 459.095 | 263.2512 | 22.3072 | 22.0732 | 21.8014 | 22.045 | 22.0013 | 25.1172 | 22.3106 | 49.528 | 76.3471 | 550.2732 | 517.166 | 527.6697 | 528.5576 | 25.3526 | 13.0091 | 748.7386 | 21.9065 | 22.1677 | 257.5926 | 21.5193 | 21.9764 | 23.091 | 66.5259 | 88.8504 | 22.085 | 27.0987 | 89.7541 | 713.3302 | 623.7105 | 748.7129 | 763.5726 | 703.3804 |  | 716.9974 | 784.0375 | 818.7405 | 611.5996 | 624.3879 | 800.2414 |  | 397.3063 |  |  | 365.6165 | 551.3824 | 659.5843 | [5 empty] | 21.8544 | 569.7591 | 21.7202 | 22.0655 | 377.2484 | 21.2847 | 21.8716 | 435.6848 | 594.2842 | 627.2927 |  | 934.3926 | 874.8251 | 453.323 | 639.4512 | 762.5927 | 555.1297 | 632.3163 | 871.4394 | 922.0601 | 547.252 | 741.3751 | 764.9892 | 957.9603 | 929.054 | 469.2138 | 575.785 | 628.3715 | 492.2825 | 616.4678 | 800.1093 | 862.0727 | 968.6106 | 533.8505 | 614.04 | 554.9081 | 714.5717 | 61.1525 | 0.12696 | 18.5272 | 4.2722 | -28.2935 | 3.0952 | 6474.79 | -0.06 | 1.3189 | 1.5189 | -23.9196 | 0.41183 | 6.1109 | -32.7551 | -33.2049 | 54.8765 | 81.5574 | 37.1507 | 25.9641 | 3.6587 | 51.3645 | 26.6693
42838.4295 | 796 | 22.8482 | 22.8287 | 22.8164 | 22.7343 | 22.3362 | 21.6528 | 22.6672 | 21.7122 | 22.3111 | 22.3154 | 22.2854 | 21.9342 | 21.1414 | 22.1185 | 21.5589 | 21.7646 | 22.033 | 21.0607 | 21.9165 | 25.1729 | 24.242 | 74.4333 | 80.9632 | 22.3051 | 27.467 | 84.4695 | 639.1247 | 658.614 | 639.346 | 22.258 | 26.8024 | 91.3131 | 22.3547 | 28.3926 | 89.3096 | 691.8893 | 833.3931 |  | 357.9723 | 826.6003 | 834.2709 | 621.1658 |  | 263.4924 | 479.9892 | 466.2909 | 706.0011 | 793.2569 | 848.7118 | 869.9333 | 28.6298 | 136.0588 | 46.107 | 297.8089 | 31.0863 | 42.4633 | 45.2238 | 46.4127 | 28.8 |  |  | 0.14348 | 0.4034 | -144.26 | -0.074298 | 6.3163 | -197.8144 | -203.2233 | -2.9705 | 6.5813 | 21.495 | 14.9071 | 0.0037341 | 0.0030342 | 0.00036306 | 22.8633 | 21.9944 | 22.1337 | 22.1866 | 21.9826 | 21.2549 | 20.0684 | 22.1538 | 22.3274 | 22.3618 | 22.3086 | 21.9072 | 21.1355 | 22.232 | 353.1869 | 245.8528 | 256.8721 | 193.3355 | 161.0874 | 458.3892 | 262.6799 | 22.295 | 22.0717 | 21.7949 | 22.0389 | 22.0014 | 25.1699 | 22.3128 | 50.1368 | 76.4298 | 550.5206 | 519.0226 | 528.8421 | 528.5963 | 39.7832 | 19.0151 | 746.863 | 21.9062 | 22.1715 | 257.4695 | 21.5226 | 21.9757 | 23.1128 | 67.0017 | 88.8729 | 22.0922 | 27.2016 | 89.7986 | 717.5082 | 625.4983 | 750.4438 | 765.3145 | 709.8352 |  | 717.1073 | 788.2109 | 818.1761 | 614.2879 | 624.6524 | 800.2979 |  | 399.1669 |  |  | 366.076 | 554.8441 | 662.5946 | [5 empty] | 21.8554 | 571.4616 | 21.7192 | 22.0637 | 377.3437 | 21.2847 | 21.8732 | 436.6384 | 594.3442 | 629.7332 |  | 931.8415 | 874.0675 | 453.6752 | 638.8138 | 763.7274 | 555.7536 | 633.9599 | 866.8276 | 921.8283 | 547.6492 | 739.0991 | 765.15 | 956.4159 | 924.7539 | 469.5913 | 576.2343 | 628.689 | 492.3069 | 616.3587 | 797.2636 | 860.7325 | 963.4487 | 533.8095 | 615.3825 | 554.8679 | 714.3116 | 56.894 | 0.1292 | 18.556 | 4.2093 | -28.168 | 3.0951 | 6588.13 | -0.08 | 0.79741 | 1.2147 | -22.9709 | -0.52131 | 5.8664 | -32.8296 | -33.2754 | 54.7244 | 81.2592 | 37.1268 | 27.9272 | 5.3193 | 51.1417 | 26.7064
42838.4295 | 797 | 22.8487 | 22.8261 | 22.8179 | 22.7323 | 22.3363 | 21.6533 | 22.6687 | 21.7082 | 22.3129 | 22.3177 | 22.2874 | 21.9299 | 21.1438 | 22.1192 | 21.5621 | 21.7641 | 22.0362 | 21.0613 | 21.9463 | 25.2342 | 24.3214 | 74.6534 | 81.0625 | 22.3091 | 27.5534 | 84.5684 | 640.9513 | 657.1875 | 641.0321 | 22.255 | 26.8929 | 91.318 | 22.3608 | 28.4955 | 89.3263 | 690.9542 | 824.6175 |  | 357.1614 | 824.4477 | 832.6944 | 620.2649 |  | 266.145 | 484.583 | 469.9905 | 723.9478 | 799.6651 | 855.1624 | 871.5925 | 28.5898 | 136.7841 | 46.4016 | 299.3115 | 31.2685 | 42.421 | 45.4293 | 46.3791 | 28.8648 |  |  | 0.038342 | 0.082731 | -140.2431 | 0.30683 | 5.8918 | -197.8328 | -203.3297 | -2.9646 | 6.4338 | 20.6243 | 14.4766 | 0.0036306 | 0.0029652 | 0.00036799 | 22.8624 | 21.989 | 22.1229 | 22.1801 | 21.9793 | 21.2573 | 20.0683 | 22.1487 | 22.3207 | 22.3551 | 22.3013 | 21.8991 | 21.1336 | 22.2213 | 367.5883 | 275.3274 | 281.1259 | 205.1118 | 161.488 | 458.6816 | 262.8103 | 22.2969 | 22.069 | 21.797 | 22.0324 | 21.9961 | 25.2257 | 22.3266 | 50.7756 | 76.5158 | 550.8288 | 521.02 | 530.4526 | 529.6964 | 38.3258 | 21.9516 | 746.1831 | 21.9042 | 22.166 | 258.2981 | 21.5211 | 21.9759 | 23.1289 | 67.4725 | 88.8936 | 22.0913 | 27.3059 | 89.8353 | 717.9399 | 626.345 | 753.4432 | 768.619 | 711.9875 |  | 717.3975 | 786.8885 | 817.4518 | 612.6666 | 624.6427 | 799.1595 |  | 401.434 |  |  | 366.6132 | 558.0364 | 664.0001 | [5 empty] | 21.8516 | 571.1871 | 21.713 | 22.0626 | 376.7951 | 21.2801 | 21.8604 | 437.5796 | 594.5806 | 630.8973 |  | 926.4975 | 872.8703 | 454.2262 | 638.3158 | 763.3013 | 556.229 | 635.5515 | 867.27 | 918.3712 | 548.478 | 738.6043 | 763.6632 | 955.2528 | 920.9769 | 469.3947 | 576.7204 | 629.5566 | 492.4017 | 616.2401 | 793.7486 | 859.0988 | 959.5563 | 534.005 | 616.6668 | 554.8514 | 714.5664 | 54.852 | 0.13074 | 18.5866 | 4.1499 | -28.2083 | 3.0952 | 6703.93 | -0.12 | 0.41259 | 0.55177 | -22.7178 | 1.0626 | 5.6821 | -32.9254 | -33.3797 | 54.7367 | 81.0626 | 37.1699 | 26.3855 | 2.6435 | 50.9504 | 26.7235
42838.4295 | 798 | 22.8494 | 22.8254 | 22.8185 | 22.7294 | 22.3368 | 21.6558 | 22.6714 | 21.7142 | 22.3141 | 22.3236 | 22.2881 | 21.9229 | 21.1429 | 22.1224 | 21.5705 | 21.7731 | 22.0352 | 21.0676 | 21.9756 | 25.305 | 24.4127 | 74.8795 | 81.1669 | 22.3128 | 27.639 | 84.6646 | 639.9479 | 655.8334 | 639.5213 | 22.2585 | 26.9968 | 91.3281 | 22.3642 | 28.6026 | 89.3385 | 690.2091 | 816.9689 |  | 357.7675 | 821.2058 | 828.5721 | 625.5153 |  | 267.8946 | 488.7538 | 473.194 | 740.306 | 807.8998 | 860.9799 | 870.0064 | 28.6301 | 137.4953 | 46.7788 | 300.6832 | 31.4169 | 42.3837 | 45.6257 | 46.3534 | 28.9177 |  |  | 0.13625 | 0.46846 | -142.2585 | -0.074954 | 6.6823 | -197.8236 | -203.2614 | -3.0054 | 6.8806 | 22.0646 | 14.6549 | 0.0035698 | 0.0029521 | 0.00036799 | 22.8797 | 21.987 | 22.1281 | 22.1801 | 21.976 | 21.2568 | 20.0781 | 22.1557 | 22.326 | 22.3591 | 22.2996 | 21.9039 | 21.1396 | 22.2237 | 382.3597 | 295.9422 | 298.5056 | 209.6669 | 169.698 | 458.9864 | 263.276 | 22.3 | 22.0727 | 21.8037 | 22.0422 | 22.0111 | 25.289 | 22.3458 | 51.3789 | 76.61 | 551.2197 | 521.9098 | 531.3639 | 532.0535 | 39.4989 | 27.1127 | 745.0737 | 21.9047 | 22.165 | 259.261 | 21.5217 | 21.9747 | 23.1536 | 67.9348 | 88.9128 | 22.109 | 27.4152 | 89.8702 | 717.3815 | 626.844 | 755.1664 | 770.9292 | 707.6389 |  | 717.1275 | 788.4319 | 816.9481 | 609.2827 | 624.4702 | 800.3793 |  | 403.6731 |  |  | 366.6417 | 558.4864 | 663.1249 | [5 empty] | 21.8568 | 569.8798 | 21.7207 | 22.0649 | 375.4036 | 21.2897 | 21.864 | 438.4778 | 594.8445 | 631.8923 |  | 922.8655 | 871.1267 | 454.7147 | 637.5814 | 761.9112 | 556.7414 | 636.5711 | 869.2465 | 915.9002 | 549.1464 | 736.4065 | 762.5738 | 949.3508 | 916.9595 | 469.997 | 577.4299 | 630.4833 | 492.8143 | 616.063 | 790.495 | 855.631 | 955.7772 | 534.8052 | 617.8939 | 554.9235 | 711.8241 | 57.7486 | 0.12425 | 18.614 | 4.1007 | -28.1532 | 3.0951 | 6846.27 | -0.08 | 0.77714 | 1.3166 | -22.9433 | -0.52664 | 6.0668 | -33.0094 | -33.46 | 54.7905 | 80.8576 | 37.2308 | 24.8052 | 0.78046 | 50.6326 | 26.7185
42838.4295 | 799 | 22.845 | 22.8275 | 22.8155 | 22.7286 | 22.3401 | 21.6582 | 22.6707 | 21.7154 | 22.3157 | 22.3252 | 22.2844 | 21.9208 | 21.1439 | 22.1213 | 21.5722 | 21.7719 | 22.0338 | 21.0663 | 21.9972 | 25.3757 | 24.4901 | 75.0951 | 81.2717 | 22.322 | 27.7224 | 84.757 | 639.2113 | 655.3874 | 638.812 | 22.2604 | 27.1041 | 91.3345 | 22.3623 | 28.7082 | 89.3555 | 689.9588 | 810.5735 |  | 358.0774 | 818.3749 | 825.6506 | 629.356 |  | 269.4099 | 492.5899 | 476.3643 | 754.6461 | 814.5261 | 863.9768 | 869.9221 | 28.6791 | 138.0766 | 47.4207 | 302.0122 | 31.5831 | 42.356 | 45.8398 | 46.3231 | 28.981 |  |  | 0.092226 | -0.41865 | -143.7994 | -0.25041 | 5.4726 | -197.8158 | -203.0827 | -2.6485 | 6.5569 | 21.3154 | 14.285 | 0.0034926 | 0.002865 | 0.00036634 | 22.8888 | 21.9916 | 22.1265 | 22.1793 | 21.9765 | 21.2457 | 20.0703 | 22.154 | 22.3171 | 22.3537 | 22.3018 | 21.9034 | 21.1274 | 22.2275 | 413.5164 | 304.0644 | 321.1369 | 214.1821 | 178.1719 | 459.8894 | 263.9159 | 22.3071 | 22.0869 | 21.8068 | 22.034 | 22.0242 | 25.3558 | 22.3508 | 51.8923 | 76.6949 | 551.6962 | 522.697 | 532.2115 | 533.0809 | 43.805 | 24.0516 | 747.8566 | 21.9032 | 22.1671 | 259.9144 | 21.5213 | 21.976 | 23.176 | 68.3667 | 88.9347 | 22.1216 | 27.534 | 89.9172 | 717.9725 | 627.2861 | 754.5165 | 769.6198 | 710.085 |  | 716.8033 | 796.4914 | 816.8448 | 606.0464 | 624.2203 | 805.3782 |  | 405.808 |  |  | 366.881 | 557.6069 | 662.2371 | [5 empty] | 21.8492 | 568.5668 | 21.7198 | 22.0585 | 374.9931 | 21.2897 | 21.8665 | 439.3205 | 595.2285 | 632.3327 |  | 920.0256 | 870.4485 | 455.294 | 636.5101 | 760.0798 | 557.3939 | 636.8756 | 871.0835 | 915.1009 | 549.5192 | 735.3155 | 762.9407 | 941.6596 | 914.4633 | 471.1525 | 577.8211 | 629.9657 | 492.9254 | 615.8416 | 788.5776 | 852.2484 | 951.8385 | 536.1225 | 617.4134 | 555.0982 | 708.8962 | 55.5519 | 0.12057 | 18.6436 | 4.0506 | -28.2321 | 3.0952 | 6896.54 | -0.05 | 0.63912 | -1.2478 | -23.1252 | -0.96501 | 5.4975 | -33.0523 | -33.4894 | 54.6421 | 80.6005 | 37.2728 | 21.5242 | -1.6406 | 50.4682 | 26.7638
42838.4295 | 800 | 22.8409 | 22.8247 | 22.8217 | 22.7273 | 22.338 | 21.6489 | 22.6621 | 21.7098 | 22.3151 | 22.3164 | 22.2853 | 21.9221 | 21.1489 | 22.115 | 21.5684 | 21.7639 | 22.0287 | 21.0652 | 22.0261 | 25.4398 | 24.565 | 75.3002 | 81.3677 | 22.3236 | 27.8027 | 84.8421 | 640.1322 | 654.9181 | 639.4105 | 22.254 | 27.2023 | 91.3322 | 22.3573 | 28.8053 | 89.3668 | 689.3086 | 806.264 |  | 357.4272 | 819.4323 | 831.9987 | 626.6508 |  | 271.3498 | 497.3641 | 479.9403 | 769.0865 | 824.1457 | 864.7388 | 868.9919 | 29.1291 | 138.8172 | 47.7582 | 303.7851 | 31.8236 | 42.344 | 46.0653 | 46.3104 | 29.0106 |  |  | 0.04557 | 0.94552 | -141.9095 | -0.19915 | 7.0484 | -197.8657 | -203.2693 | -2.113 | 6.6793 | 21.5281 | 15.2703 | 0.0035402 | 0.0028782 | 0.00037784 | 22.8949 | 21.9883 | 22.1225 | 22.1798 | 21.976 | 21.2494 | 20.0707 | 22.1559 | 22.3212 | 22.3494 | 22.3008 | 21.9038 | 21.1281 | 22.2221 | 441.9648 | 336.8957 | 332.8365 | 225.6415 | 182.4024 | 461.2892 | 264.5476 | 22.3014 | 22.0743 | 21.8015 | 22.0486 | 22.0256 | 25.4279 | 22.3551 | 52.5096 | 76.7923 | 552.0499 | 524.7714 | 533.5508 | 532.1422 | 33.5881 | 30.2047 | 751.0066 | 21.9022 | 22.1686 | 260.504 | 21.5207 | 21.9753 | 23.1896 | 68.7793 | 88.9514 | 22.1252 | 27.6491 | 89.9599 | 716.3574 | 627.8395 | 751.9125 | 765.0447 | 708.9055 |  | 716.4226 | 794.9768 | 816.5136 | 604.2026 | 623.8718 | 804.6865 |  | 407.9047 |  |  | 367.2265 | 557.2212 | 661.2038 | [5 empty] | 21.8552 | 567.4178 | 21.7279 | 22.0645 | 375.0148 | 21.2901 | 21.871 | 440.0011 | 595.5438 | 631.8744 |  | 919.5219 | 870.3077 | 455.9689 | 635.7922 | 758.5238 | 557.8595 | 636.8679 | 870.9833 | 914.2345 | 549.92 | 733.9164 | 761.8898 | 939.7658 | 910.7988 | 471.7403 | 578.2659 | 630.2851 | 493.0343 | 615.9145 | 786.6336 | 852.105 | 948.5242 | 536.9977 | 616.8848 | 555.3949 | 706.0317 | 56.5924 | 0.10881 | 18.6724 | 3.9986 | -28.3033 | 3.0951 | 6901.93 | -0.04 | 0.4494 | 1.881 | -23.0443 | -0.86327 | 6.2411 | -33.0676 | -33.516 | 54.5806 | 80.5362 | 37.2573 | 18.6442 | -2.8481 | 50.3937 | 26.8448
42838.4295 | 801 | 22.8454 | 22.8284 | 22.8222 | 22.7309 | 22.3378 | 21.6512 | 22.6653 | 21.7108 | 22.3241 | 22.3158 | 22.2831 | 21.9264 | 21.1352 | 22.1139 | 21.5606 | 21.7626 | 22.0312 | 21.0686 | 22.0585 | 25.5122 | 24.6464 | 75.5097 | 81.4652 | 22.327 | 27.8903 | 84.9354 | 639.6952 | 653.8975 | 639.0663 | 22.2639 | 27.3091 | 91.353 | 22.37 | 28.9176 | 89.3947 | 688.463 | 801.536 |  | 357.9095 | 824.441 | 843.2459 | 625.5278 |  | 273.1488 | 501.5608 | 482.6499 | 780.1979 | 832.1328 | 869.048 | 869.4512 | 29.6123 | 139.4787 | 47.4255 | 305.1325 | 32.003 | 42.3186 | 46.2775 | 46.3 | 29.0547 |  |  | 0.16451 | -0.92397 | -150.1754 | -0.33977 | 7.3513 | -197.8302 | -203.0866 | -2.6623 | 6.7023 | 21.629 | 14.8757 | 0.0035353 | 0.0028584 | 0.00036799 | 22.9003 | 21.993 | 22.126 | 22.1795 | 21.9848 | 21.2566 | 20.068 | 22.1534 | 22.3227 | 22.357 | 22.3066 | 21.9005 | 21.137 | 22.2219 | 438.4802 | 331.4524 | 344.7868 | 246.6061 | 203.2742 | 462.0525 | 265.342 | 22.3059 | 22.0776 | 21.8019 | 22.046 | 22.0381 | 25.49 | 22.3745 | 53.1329 | 76.8968 | 552.2881 | 525.7439 | 533.8407 | 531.2623 | 30.6505 | 18.7442 | 748.7993 | 21.9046 | 22.165 | 261.4026 | 21.5203 | 21.9809 | 23.2058 | 69.18 | 88.9713 | 22.1328 | 27.7579 | 89.9901 | 712.2291 | 627.8825 | 749.6984 | 760.7659 | 706.122 |  | 715.9942 | 783.4795 | 815.4138 | 601.4333 | 623.477 | 798.0467 |  | 410.1138 |  |  | 367.9131 | 555.553 | 659.5245 | [5 empty] | 21.852 | 566.1286 | 21.7215 | 22.061 | 375.0681 | 21.2879 | 21.8632 | 441.0306 | 595.6084 | 631.5033 |  | 917.4525 | 870.4436 | 456.7366 | 635.188 | 756.563 | 558.1274 | 636.1082 | 871.2188 | 913.8047 | 550.3078 | 730.8261 | 760.444 | 939.3635 | 905.5161 | 471.9195 | 578.4998 | 630.3955 | 493.6409 | 616.2252 | 784.1476 | 854.0894 | 947.1371 | 537.7031 | 616.7965 | 556.0921 | 706.4365 | 51.9823 | 0.10636 | 18.6983 | 3.9515 | -28.1852 | 3.0952 | 6874.46 | -0.02 | 0.85371 | -1.8645 | -23.7704 | -1.1307 | 6.3859 | -33.1271 | -33.5644 | 54.5519 | 80.5028 | 37.2586 | 19.1849 | -4.0596 | 50.2306 | 26.9062
42838.4296 | 802 | 22.8492 | 22.8287 | 22.82 | 22.7341 | 22.3354 | 21.6645 | 22.6724 | 21.7112 | 22.3265 | 22.323 | 22.2943 | 21.9331 | 21.1466 | 22.1184 | 21.5523 | 21.7612 | 22.029 | 21.0591 | 22.0743 | 25.5711 | 24.7319 | 75.7116 | 81.55 | 22.3317 | 27.9671 | 85.0317 | 640.1649 | 653.5226 | 639.8896 | 22.2621 | 27.4351 | 91.347 | 22.3749 | 29.0311 | 89.4116 | 688.2051 | 806.7219 |  | 354.5016 | 829.7705 | 853.1506 | 629.0858 |  | 275.0589 | 504.6208 | 485.993 | 788.1141 | 836.5756 | 870.2739 | 870.8361 | 29.9566 | 140.1859 | 46.869 | 306.4171 | 32.1844 | 42.3246 | 46.5129 | 46.3143 | 29.1344 |  |  | 0.000886 | 0.37186 | -138.2455 | -0.42454 | 5.746 | -197.8348 | -203.264 | -2.7793 | 6.578 | 21.0838 | 14.266 | 0.0034121 | 0.0027977 | 0.00035156 | 22.9029 | 21.9887 | 22.1296 | 22.1732 | 21.9766 | 21.2476 | 20.0643 | 22.1497 | 22.3216 | 22.3578 | 22.2993 | 21.8992 | 21.1313 | 22.2141 | 427.6719 | 309.3452 | 335.9222 | 245.4888 | 202.7933 | 462.2668 | 265.656 | 22.2994 | 22.076 | 21.8037 | 22.0412 | 22.0395 | 25.5444 | 22.3787 | 53.7729 | 76.9773 | 552.5742 | 526.0461 | 534.3592 | 531.081 | 29.2378 | 24.1079 | 743.5452 | 21.9046 | 22.1662 | 262.2258 | 21.5233 | 21.9766 | 23.229 | 69.5697 | 88.9942 | 22.1434 | 27.8728 | 90.0055 | 708.7931 | 626.8957 | 749.2337 | 758.9182 | 699.81 |  | 715.3309 | 773.0757 | 814.2106 | 600.9351 | 623.0886 | 792.9214 |  | 412.0248 |  |  | 371.0598 | 552.5089 | 655.8048 | [5 empty] | 21.8515 | 564.7754 | 21.7283 | 22.066 | 375.6228 | 21.2881 | 21.8654 | 441.7144 | 595.452 | 631.038 |  | 915.661 | 870.8161 | 457.6338 | 634.0789 | 755.1974 | 558.2425 | 634.9914 | 871.537 | 913.6918 | 550.4547 | 726.4628 | 757.7276 | 934.8242 | 901.7511 | 472.343 | 578.7708 | 630.424 | 494.5675 | 616.6627 | 783.445 | 854.8569 | 944.8998 | 538.4313 | 617.2288 | 556.8653 | 707.5718 | 53.1857 | 0.096083 | 18.7263 | 3.9008 | -28.2731 | 3.0952 | 6854.69 | -0.04 | 0.06268 | 1.1852 | -22.8517 | -1.2663 | 5.6487 | -33.1453 | -33.597 | 54.5634 | 80.4069 | 37.1982 | 20.4289 | -3.0286 | 50.0726 | 26.9557
42838.4296 | 803 | 22.85 | 22.8278 | 22.8131 | 22.7297 | 22.3434 | 21.6498 | 22.6722 | 21.7118 | 22.3177 | 22.321 | 22.2908 | 21.9258 | 21.1414 | 22.1151 | 21.559 | 21.7585 | 22.0275 | 21.0509 | 22.0977 | 25.6446 | 24.8201 | 75.9024 | 81.6439 | 22.3335 | 28.0549 | 85.1247 | 643.4948 | 652.7904 | 643.3285 | 22.2661 | 27.5297 | 91.3694 | 22.3733 | 29.1324 | 89.4325 | 687.7501 | 799.4775 |  | 341.3224 | 832.1153 | 859.4621 | 628.0884 |  | 276.9386 | 507.0588 | 488.2532 | 790.4685 | 838.1122 | 872.9365 | 873.1167 | 30.1717 | 140.866 | 47.0611 | 307.7172 | 32.4002 | 42.3171 | 46.7423 | 46.3429 | 29.1565 |  |  | 0.13165 | 0.33112 | -102.8348 | -0.40023 | 5.8544 | -197.9209 | -203.2607 | -2.5151 | 6.7556 | 21.739 | 14.5343 | 0.0034367 | 0.002865 | 0.00035649 | 22.9163 | 21.9852 | 22.1217 | 22.1691 | 21.967 | 21.2489 | 20.0686 | 22.1481 | 22.3165 | 22.3645 | 22.2927 | 21.9028 | 21.1273 | 22.2135 | 404.3752 | 304.4804 | 330.9498 | 245.1197 | 206.6165 | 462.0922 | 265.8823 | 22.2976 | 22.0813 | 21.8073 | 22.0465 | 22.0466 | 25.6142 | 22.3946 | 54.3223 | 77.0708 | 552.9865 | 526.3134 | 535.3713 | 532.1795 | 31.5496 | 29.7203 | 739.4523 | 21.9047 | 22.1729 | 262.6249 | 21.5239 | 21.976 | 23.2534 | 69.9493 | 89.0146 | 22.152 | 27.9932 | 90.0108 | 707.0817 | 625.7175 | 750.1606 | 758.4103 | 694.482 |  | 714.4445 | 774.1138 | 813.6307 | 601.6624 | 622.7041 | 791.2039 |  | 413.9682 |  |  | 372.4464 | 550.9051 | 651.8209 | [5 empty] | 21.8504 | 563.9374 | 21.7313 | 22.0658 | 377.1007 | 21.289 | 21.8722 | 441.9401 | 595.2329 | 630.6982 |  | 916.245 | 871.2837 | 458.7645 | 632.7446 | 754.178 | 558.2202 | 634.9164 | 870.2179 | 913.5409 | 550.6272 | 722.9316 | 757.16 | 935.1188 | 901.7197 | 472.5093 | 579.4211 | 631.699 | 495.3912 | 616.9297 | 783.0975 | 854.0812 | 943.5289 | 539.1594 | 617.8018 | 557.5617 | 706.9635 | 55.1065 | 0.086934 | 18.7531 | 3.8618 | -28.2293 | 3.0951 | 6825.24 | -0.05 | 0.7655 | 1.1201 | -19.7398 | -1.2315 | 5.7084 | -33.1911 | -33.6359 | 54.4929 | 80.193 | 37.1046 | 22.9823 | -2.443 | 49.9961 | 26.9893
42838.4296 | 804 | 22.8564 | 22.8372 | 22.8196 | 22.7389 | 22.3413 | 21.6611 | 22.6791 | 21.7208 | 22.3248 | 22.3219 | 22.2931 | 21.932 | 21.1517 | 22.1256 | 21.5581 | 21.7617 | 22.0338 | 21.0601 | 22.1278 | 25.7279 | 24.9111 | 76.1062 | 81.7313 | 22.3376 | 28.1461 | 85.2198 | 645.0846 | 652.2533 | 644.7323 | 22.2688 | 27.6356 | 91.3808 | 22.3644 | 29.2366 | 89.4517 | 687.0977 | 797.4279 |  | 341.3827 | 829.9851 | 859.9947 | 625.4592 |  | 278.38 | 509.7684 | 489.4741 | 790.8265 | 838.6557 | 874.2055 | 872.861 | 30.3604 | 141.5381 | 48.0315 | 308.8748 | 32.6002 | 42.3109 | 46.9792 | 46.3627 | 29.2093 |  |  | -0.045766 | -0.71961 | -117.2257 | -0.097954 | 4.6321 | -197.8407 | -203.2804 | -2.7484 | 6.7786 | 21.5109 | 14.9124 | 0.0033447 | 0.0027484 | 0.00039591 | 22.9202 | 21.9809 | 22.1169 | 22.1703 | 21.9702 | 21.2373 | 20.0688 | 22.1435 | 22.3095 | 22.3457 | 22.298 | 21.8989 | 21.1217 | 22.2136 | 414.0263 | 322.0353 | 342.8713 | 245.4962 | 204.6409 | 462.3714 | 266.2876 | 22.2978 | 22.0831 | 21.8139 | 22.0448 | 22.0514 | 25.6741 | 22.4056 | 54.8318 | 77.1533 | 553.5843 | 527.6744 | 537.3015 | 533.2298 | 41.3947 | 27.4103 | 740.4037 | 21.9062 | 22.1712 | 263.0664 | 21.5225 | 21.9757 | 23.2693 | 70.3282 | 89.0401 | 22.154 | 28.1123 | 90.0192 | 705.9038 | 625.043 | 751.6115 | 758.2422 | 692.8727 |  | 713.4712 | 777.7383 | 813.0714 | 599.9215 | 622.2183 | 790.9868 |  | 416.2057 |  |  | 374.8897 | 550.5797 | 650.2184 | [5 empty] | 21.8546 | 563.1617 | 21.7224 | 22.0632 | 378.5294 | 21.2904 | 21.8691 | 442.1072 | 595.0315 | 630.0605 |  | 916.8643 | 870.9702 | 459.8427 | 631.5754 | 752.5148 | 558.0333 | 634.459 | 866.9537 | 913.9479 | 550.7088 | 721.2947 | 756.2609 | 935.165 | 898.4102 | 472.9249 | 579.8204 | 634.2584 | 495.87 | 617.0816 | 782.1366 | 851.8796 | 941.5039 | 539.7001 | 618.0963 | 558.0384 | 705.6685 | 54.1737 | 0.07605 | 18.7793 | 3.8198 | -28.2845 | 3.0951 | 6822.13 | -0.05 | -0.45168 | -1.6541 | -21.1123 | -0.61029 | 5.0805 | -33.2027 | -33.6561 | 54.2982 | 79.9141 | 37.0603 | 21.9662 | -3.7081 | 49.9199 | 27.0533
42838.4296 | 805 | 22.8539 | 22.8314 | 22.8231 | 22.7376 | 22.3377 | 21.6563 | 22.6816 | 21.7202 | 22.3292 | 22.3291 | 22.295 | 21.936 | 21.155 | 22.1287 | 21.5615 | 21.7675 | 22.0342 | 21.0623 | 22.1658 | 25.7984 | 24.9983 | 76.3038 | 81.8226 | 22.3417 | 28.2293 | 85.3093 | 644.8334 | 650.532 | 644.0848 | 22.2654 | 27.7388 | 91.3899 | 22.3593 | 29.3463 | 89.4631 | 686.3123 | 793.2662 |  | 341.0911 | 829.4053 | 859.2903 | 622.9174 |  | 280.3559 | 513.1677 | 492.0156 | 795.2141 | 844.1952 | 879.9819 | 874.0492 | 30.588 | 142.3058 | 48.483 | 310.3797 | 32.8182 | 42.2976 | 47.2124 | 46.3914 | 29.2625 |  |  | 0.094198 | 1.0198 | -126.7722 | -0.075614 | 4.8273 | -197.7987 | -203.2864 | -1.8935 | 6.1851 | 19.9836 | 15.0558 | 0.0031427 | 0.0026597 | 0.00040906 | 22.9359 | 21.986 | 22.1168 | 22.1656 | 21.9717 | 21.2443 | 20.0607 | 22.1455 | 22.3154 | 22.3576 | 22.3038 | 21.9047 | 21.1237 | 22.2171 | 450.1871 | 347.1832 | 350.5078 | 243.332 | 199.9617 | 463.5165 | 266.8987 | 22.3038 | 22.0711 | 21.8191 | 22.0483 | 22.0653 | 25.7384 | 22.4242 | 55.3707 | 77.2487 | 554.4292 | 529.5705 | 540.0004 | 537.08 | 33.2331 | 22.4855 | 740.3007 | 21.9031 | 22.1647 | 264.1819 | 21.5218 | 21.9767 | 23.2839 | 70.6958 | 89.0578 | 22.1584 | 28.2316 | 90.0336 | 703.3714 | 624.6584 | 751.4585 | 756.7396 | 698.2174 |  | 712.8248 | 771.0165 | 812.0745 | 597.2068 | 621.754 | 788.5814 |  | 418.1277 |  |  | 377.5432 | 550.3774 | 650.1485 | [5 empty] | 21.8531 | 561.8807 | 21.7279 | 22.0636 | 379.9763 | 21.2786 | 21.8598 | 442.6656 | 595.0521 | 629.8526 |  | 918.498 | 870.3472 | 460.9068 | 630.3197 | 750.7556 | 558.3491 | 634.8934 | 868.7734 | 913.4216 | 550.958 | 718.5609 | 753.645 | 929.9874 | 893.0947 | 473.2742 | 580.1012 | 635.3421 | 496.0344 | 617.2998 | 781.003 | 850.2619 | 939.3986 | 540.9311 | 618.5032 | 558.3767 | 706.7054 | 54.6856 | 0.067645 | 18.8035 | 3.7823 | -28.3301 | 3.0951 | 6833.33 | -0.14 | 0.64778 | 1.9734 | -22.0028 | -0.53736 | 5.1995 | -33.2827 | -33.7412 | 53.9911 | 79.7837 | 37.0473 | 18.1791 | -4.4669 | 49.8111 | 27.0782
42838.4296 | 806 | 22.8547 | 22.8313 | 22.8229 | 22.736 | 22.3385 | 21.6571 | 22.6709 | 21.7175 | 22.3261 | 22.3208 | 22.294 | 21.9345 | 21.1499 | 22.1266 | 21.5593 | 21.7576 | 22.0409 | 21.0619 | 22.2069 | 25.8854 | 25.1005 | 76.5039 | 81.91 | 22.3492 | 28.3278 | 85.4016 | 644.4222 | 647.8847 | 643.3476 | 22.2694 | 27.8515 | 91.3932 | 22.3652 | 29.4695 | 89.4847 | 685.5822 | 790.5716 |  | 340.1565 | 826.6923 | 853.1487 | 621.7554 |  | 281.7551 | 514.3826 | 500.2296 | 795.5581 | 850.726 | 883.131 | 876.7945 | 30.31 | 142.8844 | 48.2556 | 311.4309 | 33.0669 | 42.2938 | 47.4355 | 46.4058 | 29.2975 |  |  | -0.020142 | 0.86733 | -141.2886 | -0.57042 | 6.7533 | -197.8256 | -203.1996 | -2.3673 | 6.6768 | 20.8683 | 14.8236 | 0.003233 | 0.0026925 | 0.00036799 | 22.9494 | 21.988 | 22.1289 | 22.1827 | 21.9724 | 21.2505 | 20.0819 | 22.1562 | 22.3241 | 22.3556 | 22.2979 | 21.9097 | 21.1309 | 22.2246 | 457.3748 | 340.6119 | 331.8872 | 233.4523 | 199.3985 | 464.3613 | 267.1155 | 22.3061 | 22.0803 | 21.8148 | 22.0495 | 22.0694 | 25.8061 | 22.4316 | 55.911 | 77.3452 | 555.2167 | 530.1378 | 541.1184 | 540.8512 | 55.9789 | 28.1888 | 737.6799 | 21.9043 | 22.1674 | 264.7218 | 21.5235 | 21.9818 | 23.3127 | 71.0588 | 89.0754 | 22.1697 | 28.3513 | 90.0629 | 702.4077 | 624.3535 | 749.5017 | 754.3197 | 699.9129 |  | 712.2585 | 767.4525 | 811.1582 | 596.9909 | 621.3235 | 787.512 |  | 420.0288 |  |  | 377.7749 | 550.226 | 649.4904 | [5 empty] | 21.8477 | 561.2465 | 21.7292 | 22.0571 | 381.2043 | 21.2913 | 21.8658 | 443.2934 | 595.7594 | 630.1008 |  | 917.4608 | 869.6158 | 461.6616 | 629.2466 | 749.0953 | 559.1238 | 635.1007 | 868.5321 | 913.6884 | 551.4865 | 714.8644 | 754.817 | 928.7952 | 889.0259 | 472.9758 | 580.5848 | 635.1994 | 496.5828 | 617.5818 | 778.5148 | 850.9765 | 937.2775 | 541.788 | 618.6407 | 559.0498 | 710.523 | 54.7315 | 0.059963 | 18.8264 | 3.7398 | -28.3276 | 3.0951 | 6827.48 | -0.08 | -0.29942 | 1.8213 | -23.2463 | -1.4771 | 6.1582 | -33.3304 | -33.78 | 53.8053 | 79.592 | 36.9714 | 17.5511 | -2.3661 | 49.677 | 27.0967
42838.4296 | 807 | 22.8586 | 22.8255 | 22.8219 | 22.7317 | 22.3382 | 21.6591 | 22.6623 | 21.7174 | 22.3218 | 22.3318 | 22.2899 | 21.9292 | 21.1453 | 22.1146 | 21.5625 | 21.7625 | 22.039 | 21.0709 | 22.2316 | 25.9551 | 25.1913 | 76.6894 | 81.9864 | 22.35 | 28.4159 | 85.4837 | 645.3804 | 647.8542 | 644.7662 | 22.268 | 27.9642 | 91.3766 | 22.364 | 29.5672 | 89.5012 | 684.8149 | 793.5232 |  | 340.4532 | 828.0232 | 855.5668 | 621.1286 |  | 283.3516 | 514.9156 | 509.5793 | 800.7814 | 854.659 | 886.9325 | 879.4784 | 30.0639 | 143.5046 | 48.2691 | 312.6229 | 33.3133 | 42.2956 | 47.6528 | 46.4243 | 29.3213 |  |  | 0.33667 | 0.5414 | -148.712 | -0.31152 | 6.869 | -197.7901 | -203.3908 | -2.3863 | 6.4139 | 21.4467 | 15.7014 | 0.0031722 | 0.0026055 | 0.00042056 | 22.9501 | 21.9908 | 22.1237 | 22.1727 | 21.9756 | 21.2504 | 20.0725 | 22.1515 | 22.3186 | 22.3521 | 22.2995 | 21.897 | 21.1218 | 22.2188 | 469.5941 | 348.2007 | 350.3469 | 234.0556 | 197.3955 | 465.8939 | 267.6876 | 22.3008 | 22.0803 | 21.816 | 22.048 | 22.0781 | 25.8716 | 22.4397 | 56.4603 | 77.4385 | 555.8635 | 529.6901 | 540.6876 | 542.909 | 33.6652 | 19.3955 | 736.8601 | 21.9033 | 22.1644 | 264.7411 | 21.5226 | 21.9768 | 23.3358 | 71.4941 | 89.096 | 22.1696 | 28.4694 | 90.0894 | 704.4166 | 624.1266 | 749.0022 | 753.6643 | 705.6972 |  | 711.7164 | 773.1627 | 810.8984 | 598.7015 | 620.9524 | 789.8783 |  | 415.2153 |  |  | 377.9769 | 549.845 | 650.4654 | [5 empty] | 21.8533 | 561.3211 | 21.7338 | 22.061 | 380.574 | 21.2874 | 21.8681 | 444.4919 | 596.6753 | 628.3847 |  | 916.9246 | 870.7578 | 463.1114 | 628.6969 | 747.6391 | 559.9301 | 634.4823 | 867.0051 | 911.2693 | 552.2629 | 715.5181 | 754.3182 | 925.304 | 886.8616 | 472.9233 | 580.9962 | 635.434 | 497.4954 | 617.6228 | 777.9506 | 851.4851 | 936.7454 | 542.6021 | 619.389 | 559.7119 | 709.6067 | 51.7444 | 0.048413 | 18.8471 | 3.7039 | -28.286 | 3.0951 | 6831.82 | -0.08 | 1.2251 | 1.4395 | -23.8573 | -1.0919 | 6.221 | -33.3821 | -33.8514 | 53.512 | 79.3511 | 36.8534 | 16.5036 | -4.3332 | 49.52 | 27.141
42838.4296 | 808 | 22.8512 | 22.8305 | 22.8127 | 22.7282 | 22.3291 | 21.6522 | 22.6648 | 21.7105 | 22.3195 | 22.3243 | 22.2859 | 21.9268 | 21.143 | 22.1098 | 21.5668 | 21.7728 | 22.0478 | 21.0724 | 22.2671 | 26.0394 | 25.2889 | 76.8831 | 82.0726 | 22.3549 | 28.5099 | 85.5813 | 643.8035 | 646.8096 | 642.9293 | 22.2734 | 28.0704 | 91.3815 | 22.3734 | 29.681 | 89.516 | 684.1066 | 789.5634 |  | 341.1088 | 828.9987 | 855.5367 | 622.0809 |  | 285.5965 | 516.2155 | 516.6835 | 805.5681 | 856.7068 | 891.0314 | 879.4898 | 30.2397 | 144.1388 | 48.9866 | 313.9256 | 33.5688 | 42.3309 | 47.8854 | 46.4556 | 29.3762 |  |  | 0.34785 | -0.030949 | -156.9417 | -0.10321 | 6.961 | -197.8052 | -203.3488 | -2.0801 | 6.8434 | 22.3333 | 15.4069 | 0.0031312 | 0.0025085 | 0.00034663 | 22.9654 | 21.99 | 22.1298 | 22.1756 | 21.9792 | 21.2535 | 20.0692 | 22.1527 | 22.3222 | 22.358 | 22.3046 | 21.9037 | 21.1248 | 22.2255 | 453.826 | 342.9333 | 346.4657 | 240.3279 | 193.0377 | 466.2073 | 268.0895 | 22.2942 | 22.0757 | 21.8188 | 22.0419 | 22.0866 | 25.9368 | 22.4443 | 56.9431 | 77.5339 | 556.6299 | 531.3609 | 542.235 | 545.9013 | 46.2795 | 31.8886 | 736.9115 | 21.905 | 22.1652 | 264.936 | 21.5192 | 21.9691 | 23.36 | 71.9196 | 89.1123 | 22.1758 | 28.5861 | 90.1092 | 704.1044 | 624.2389 | 750.1299 | 754.5458 | 703.1371 |  | 711.0877 | 772.2997 | 810.3629 | 597.7309 | 620.5359 | 788.5467 |  | 374.1469 |  |  | 380.6844 | 551.2391 | 650.414 | [5 empty] | 21.8464 | 560.4792 | 21.7314 | 22.0581 | 381.6454 | 21.2878 | 21.8656 | 445.5127 | 597.287 | 626.6028 |  | 915.4079 | 870.6787 | 464.1282 | 628.8293 | 747.3245 | 560.6842 | 634.9025 | 862.7687 | 907.5721 | 552.5894 | 714.2875 | 752.219 | 925.921 | 887.1471 | 473.0747 | 581.2465 | 635.2648 | 497.8923 | 617.6845 | 775.5334 | 850.7609 | 938.343 | 542.9949 | 618.2306 | 560.4582 | 711.0645 | 54.523 | 0.040015 | 18.868 | 3.6683 | -28.3298 | 3.0951 | 6814.24 | -0.09 | 1.244 | -0.34445 | -24.5287 | -0.62902 | 6.2735 | -33.4423 | -33.9077 | 53.4296 | 79.2056 | 36.8013 | 18.3191 | -3.8428 | 49.3328 | 27.1784
42838.4296 | 809 | 22.8479 | 22.8252 | 22.8217 | 22.7301 | 22.3354 | 21.6529 | 22.6679 | 21.7071 | 22.3119 | 22.325 | 22.2858 | 21.9193 | 21.1375 | 22.1124 | 21.566 | 21.7703 | 22.0422 | 21.0648 | 22.2978 | 26.1153 | 25.3957 | 77.0591 | 82.1607 | 22.3664 | 28.6034 | 85.6806 | 642.7467 | 647.183 | 641.5434 | 22.2784 | 28.1909 | 91.3994 | 22.378 | 29.81 | 89.529 | 683.2959 | 789.9622 |  | 345.331 | 824.9063 | 847.1063 | 624.125 |  | 287.367 | 518.4158 | 517.1615 | 808.9851 | 859.9869 | 893.4789 | 878.3561 | 30.6118 | 144.7107 | 48.9111 | 315.1723 | 33.8674 | 42.3827 | 48.1216 | 46.4862 | 29.4394 |  |  | 0.25848 | 0.5552 | -153.298 | 0.040042 | 6.3203 | -197.8526 | -203.2009 | -2.086 | 6.7484 | 21.3747 | 15.0169 | 0.0031772 | 0.0026975 | 0.00037784 | 22.977 | 21.9942 | 22.1316 | 22.1735 | 21.9832 | 21.2513 | 20.0662 | 22.1581 | 22.3246 | 22.3625 | 22.3087 | 21.9058 | 21.1312 | 22.2223 | 476.5196 | 383.3835 | 386.4995 | 254.7069 | 196.8369 | 467.6874 | 269.651 | 22.2939 | 22.0731 | 21.8151 | 22.0492 | 22.085 | 26.0003 | 22.4557 | 57.5634 | 77.6482 | 557.2771 | 533.0196 | 543.2486 | 544.3561 | 38.7182 | 35.2049 | 736.5192 | 21.9135 | 22.1614 | 265.0611 | 21.525 | 21.9761 | 23.3889 | 72.2809 | 89.1382 | 22.1861 | 28.7124 | 90.1325 | 702.6555 | 623.9553 | 751.9862 | 756.2846 | 696.3971 |  | 710.2851 | 771.0942 | 809.8375 | 594.8621 | 620.1304 | 786.0596 |  | 374.7065 |  |  | 380.5781 | 551.5997 | 648.0912 | [5 empty] | 21.8484 | 559.6351 | 21.7268 | 22.0665 | 382.3807 | 21.289 | 21.8648 | 446.5486 | 598.1113 | 626.4529 |  | 915.5221 | 869.2214 | 465.034 | 628.4205 | 746.0362 | 561.1123 | 635.5226 | 850.5153 | 906.2636 | 553.0894 | 713.7615 | 750.765 | 927.1094 | 889.3966 | 472.9097 | 581.2601 | 634.9029 | 498.4599 | 617.8366 | 774.8161 | 849.6685 | 939.4771 | 543.3298 | 617.8146 | 561.0305 | 708.3364 | 55.8424 | 0.028969 | 18.8879 | 3.6334 | -28.2857 | 3.0952 | 6791.48 | -0.04 | 1.0716 | 1.4609 | -24.2761 | 0.39235 | 5.9841 | -33.4814 | -33.931 | 53.4212 | 79.073 | 36.8041 | 16.0981 | -8.0611 | 49.0924 | 27.3232
42838.4297 | 810 | 22.8489 | 22.8331 | 22.8195 | 22.7399 | 22.3463 | 21.6604 | 22.6685 | 21.7191 | 22.3278 | 22.3294 | 22.2915 | 21.9268 | 21.1469 | 22.1191 | 21.5652 | 21.774 | 22.0459 | 21.061 | 22.3328 | 26.1841 | 25.4917 | 77.2218 | 82.2349 | 22.3677 | 28.6897 | 85.7657 | 642.2812 | 647.6016 | 640.9901 | 22.2826 | 28.3122 | 91.4273 | 22.3718 | 29.9088 | 89.5454 | 682.666 | 794.4119 |  | 339.6802 | 819.3849 | 837.1924 | 626.6416 |  | 288.7377 | 520.1763 | 517.3768 | 814.4002 | 861.3827 | 893.4006 | 878.721 | 30.8469 | 145.4126 | 48.361 | 316.5989 | 34.0998 | 42.4294 | 48.3499 | 46.5162 | 29.4954 |  |  | 0.37939 | 2.3242 | -152.5364 | -0.57568 | 7.1666 | -197.844 | -203.2272 | -1.9901 | 6.8202 | 22.1336 | 15.817 | 0.0030342 | 0.0024954 | 0.00035649 | 22.9795 | 21.9957 | 22.126 | 22.1751 | 21.9772 | 21.254 | 20.0633 | 22.1523 | 22.3223 | 22.3603 | 22.3054 | 21.901 | 21.133 | 22.2191 | 499.7822 | 397.1555 | 387.897 | 267.7775 | 202.759 | 469.6621 | 270.9979 | 22.2968 | 22.0767 | 21.8206 | 22.0455 | 22.1113 | 26.0741 | 22.478 | 58.2029 | 77.7488 | 557.6717 | 533.3241 | 543.0564 | 542.9513 | 50.4088 | 26.0957 | 736.2921 | 21.9138 | 22.1657 | 265.5957 | 21.5271 | 21.9817 | 23.4162 | 72.6259 | 89.157 | 22.1827 | 28.8354 | 90.1613 | 703.8506 | 623.8063 | 755.2904 | 759.7605 | 700.3174 |  | 709.7799 | 773.0191 | 809.4157 | 591.8122 | 619.5771 | 786.2988 |  | 376.021 |  |  | 382.3151 | 551.7277 | 647.3387 | [5 empty] | 21.84 | 559.0056 | 21.7198 | 22.0518 | 381.2841 | 21.2846 | 21.8593 | 447.1144 | 598.3541 | 624.8852 |  | 911.6884 | 868.1821 | 466.129 | 628.4737 | 745.5266 | 560.9744 | 634.6784 | 843.7629 | 905.0647 | 553.8458 | 716.4254 | 749.1563 | 927.0142 | 890.9898 | 473.1521 | 581.5334 | 634.5909 | 499.444 | 617.8263 | 773.5857 | 845.4643 | 940.4823 | 544.3802 | 620.1499 | 561.6738 | 706.7824 | 54.5437 | 0.018711 | 18.907 | 3.5942 | -28.2171 | 3.0952 | 6826.47 | -0.1 | 1.2978 | 2.9924 | -24.2426 | -1.4893 | 6.372 | -33.4796 | -33.932 | 53.1894 | 78.8864 | 36.7841 | 13.9156 | -8.0177 | 48.8801 | 27.4245
42838.4297 | 811 | 22.8508 | 22.8323 | 22.8244 | 22.7397 | 22.3399 | 21.6599 | 22.6739 | 21.7181 | 22.3238 | 22.3273 | 22.2905 | 21.9418 | 21.1473 | 22.1243 | 21.5542 | 21.7668 | 22.0368 | 21.0606 | 22.3676 | 26.2517 | 25.5917 | 77.3916 | 82.3072 | 22.3717 | 28.7765 | 85.8495 | 640.8482 | 647.1995 | 639.8894 | 22.2839 | 28.4258 | 91.453 | 22.392 | 30.0288 | 89.5554 | 682.2765 | 799.8482 |  | 339.2358 | 818.1938 | 837.4442 | 627.1347 |  | 290.0364 | 520.3735 | 520.1073 | 820.2375 | 862.993 | 895.1761 | 879.3143 | 30.7814 | 145.9935 | 47.5892 | 317.7614 | 34.2892 | 42.482 | 48.5769 | 46.5466 | 29.5275 |  |  | 0.34719 | 1.9634 | -143.7554 | -0.16432 | 6.1704 | -197.8171 | -203.2364 | -1.8751 | 7.0209 | 21.9013 | 15.6139 | 0.0030342 | 0.0024757 | 0.00035649 | 22.9885 | 21.9953 | 22.1233 | 22.1809 | 21.9743 | 21.2499 | 20.0649 | 22.1474 | 22.3222 | 22.3486 | 22.3006 | 21.9015 | 21.1353 | 22.2225 | 541.1216 | 411.4668 | 383.5576 | 255.9082 | 188.4913 | 472.2435 | 271.9776 | 22.2995 | 22.0789 | 21.823 | 22.0483 | 22.1055 | 26.1415 | 22.4933 | 58.7308 | 77.8446 | 558.2569 | 534.804 | 544.6898 | 546.4329 | 52.5107 | 28.4707 | 737.2558 | 21.908 | 22.1653 | 265.9708 | 21.5242 | 21.9755 | 23.4433 | 72.9625 | 89.1707 | 22.1848 | 28.9557 | 90.1964 | 703.7534 | 624.3972 | 757.1847 | 761.7798 | 701.9227 |  | 709.3874 | 772.459 | 808.7061 | 594.8816 | 619.2827 | 785.4758 |  | 376.9991 |  |  | 383.6161 | 552.8842 | 649.3362 | [5 empty] | 21.8461 | 560.1493 | 21.7275 | 22.0576 | 380.6263 | 21.2917 | 21.8624 | 447.2865 | 598.6683 | 623.5756 |  | 906.982 | 866.6569 | 467.2471 | 628.1855 | 745.056 | 560.4663 | 634.5291 | 835.7466 | 901.0386 | 554.5023 | 715.9112 | 748.2722 | 922.8282 | 892.9162 | 473.9356 | 582.0735 | 634.0542 | 500.4885 | 618.0851 | 772.0479 | 840.3273 | 938.1417 | 544.93 | 620.3814 | 562.2301 | 705.8428 | 54.7413 | 0.010446 | 18.9239 | 3.5615 | -28.2401 | 3.0952 | 6818.02 | -0.01 | 1.2408 | 2.7507 | -23.5374 | -0.79578 | 5.9171 | -33.5028 | -33.9586 | 53.0494 | 78.6783 | 36.6432 | 9.8504 | -7.3908 | 48.7785 | 27.4202
42838.4297 | 812 | 22.8496 | 22.838 | 22.8231 | 22.736 | 22.3425 | 21.659 | 22.6776 | 21.7208 | 22.3195 | 22.3264 | 22.2899 | 21.933 | 21.1459 | 22.1294 | 21.5584 | 21.7649 | 22.0402 | 21.0683 | 22.4112 | 26.3382 | 25.698 | 77.5673 | 82.3938 | 22.3807 | 28.8697 | 85.9435 | 640.0635 | 646.8506 | 638.9095 | 22.2838 | 28.5286 | 91.4704 | 22.3861 | 30.1308 | 89.5423 | 681.912 | 800.1417 |  | 339.7334 | 824.3377 | 848.2584 | 624.2057 |  | 291.3169 | 520.6468 | 523.6986 | 823.7186 | 863.0963 | 896.0036 | 878.7209 | 30.6414 | 146.6089 | 47.5135 | 318.926 | 34.5108 | 42.5507 | 48.7987 | 46.587 | 29.582 |  |  | 0.24796 | -0.067749 | -141.0454 | 0.22863 | 9.0046 | -197.8558 | -203.2069 | -2.1235 | 7.0845 | 22.5249 | 16.1126 | 0.0031492 | 0.0026564 | 0.00038277 | 23.0083 | 21.9922 | 22.1326 | 22.1735 | 21.9754 | 21.2524 | 20.0729 | 22.1469 | 22.3184 | 22.3628 | 22.2996 | 21.9058 | 21.1318 | 22.2253 | 545.3202 | 436.4524 | 408.2039 | 249.3603 | 181.2187 | 474.6292 | 273.1489 | 22.2948 | 22.0695 | 21.818 | 22.0379 | 22.1081 | 26.198 | 22.4946 | 59.2265 | 77.9298 | 558.7841 | 535.2653 | 545.2786 | 546.2271 | 55.7768 | 31.4762 | 736.9648 | 21.9124 | 22.1692 | 266.248 | 21.5282 | 21.9826 | 23.4709 | 73.2913 | 89.1974 | 22.2079 | 29.0896 | 90.241 | 703.2487 | 624.5776 | 756.6973 | 761.2091 | 697.4771 |  | 708.945 | 768.7277 | 807.8867 | 598.5469 | 619.1683 | 782.8045 |  | 378.3427 |  |  | 383.5764 | 554.1519 | 648.3468 | [5 empty] | 21.854 | 561.5328 | 21.7301 | 22.0596 | 380.7156 | 21.2933 | 21.8664 | 447.132 | 599.1092 | 622.7456 |  | 896.2014 | 865.2023 | 468.5655 | 627.7961 | 744.1183 | 560.042 | 635.0506 | 824.7793 | 892.3492 | 555.3867 | 715.3279 | 746.7342 | 919.5393 | 892.5078 | 474.9935 | 582.4023 | 633.8572 | 501.4743 | 618.406 | 770.0494 | 840.1298 | 935.0132 | 545.7499 | 621.2207 | 562.9075 | 705.1035 | 53.2334 | 0.0033823 | 18.9401 | 3.5208 | -28.2666 | 3.0951 | 6849.56 | -0.07 | 1.048 | -0.51106 | -23.3185 | 0.93884 | 7.1505 | -33.5179 | -33.9682 | 53.0655 | 78.5241 | 36.5198 | 9.8741 | -9.956 | 48.7777 | 27.5094
42838.4297 | 813 | 22.8478 | 22.8327 | 22.8227 | 22.7264 | 22.34 | 21.6528 | 22.6711 | 21.7145 | 22.3141 | 22.3176 | 22.2888 | 21.9282 | 21.1418 | 22.1192 | 21.5634 | 21.7669 | 22.0435 | 21.076 | 22.4457 | 26.4237 | 25.7968 | 77.7263 | 82.4729 | 22.3843 | 28.956 | 86.0142 | 638.5365 | 646.0759 | 637.4445 | 22.2858 | 28.6514 | 91.4815 | 22.3814 | 30.25 | 89.542 | 681.4037 | 802.9321 |  | 340.4869 | 828.2127 | 852.9441 | 619.7793 |  | 292.2006 | 521.1809 | 532.5965 | 827.567 | 861.0723 | 893.1734 | 878.6097 | 30.4477 | 147.2596 | 48.2087 | 320.2185 | 34.7887 | 42.6455 | 49.0144 | 46.6408 | 29.6297 |  |  | 0.22825 | 0.8693 | -138.574 | 0.14518 | 6.9688 | -197.7875 | -203.3422 | -2.3831 | 6.8093 | 21.4958 | 16.1887 | 0.0029767 | 0.0024576 | 0.00035649 | 23.0149 | 21.992 | 22.1139 | 22.1677 | 21.9723 | 21.2493 | 20.0693 | 22.1407 | 22.3129 | 22.3504 | 22.2958 | 21.8993 | 21.1253 | 22.2167 | 553.9789 | 451.7665 | 421.5033 | 260.3833 | 189.7117 | 477.4248 | 274.4762 | 22.2863 | 22.0741 | 21.8187 | 22.0445 | 22.1192 | 26.2642 | 22.5119 | 59.63 | 78.0293 | 559.3203 | 534.6097 | 545.4914 | 548.0428 | 56.0947 | 32.6587 | 733.655 | 21.9079 | 22.1709 | 266.7702 | 21.5254 | 21.9837 | 23.4969 | 73.5945 | 89.2128 | 22.2085 | 29.2145 | 90.2772 | 701.7496 | 624.378 | 756.4919 | 761.0019 | 695.0299 |  | 708.4998 | 758.8612 | 806.7177 | 598.4756 | 618.8829 | 777.0662 |  | 380.0322 |  |  | 383.4382 | 555.1571 | 647.5147 | [5 empty] | 21.8462 | 561.3643 | 21.7234 | 22.0579 | 380.0489 | 21.293 | 21.8592 | 446.9509 | 599.8079 | 621.6753 |  | 884.7354 | 863.9783 | 469.7622 | 627.4794 | 743.2667 | 560.127 | 635.1406 | 820.5635 | 884.437 | 556.3523 | 714.5029 | 744.335 | 918.7735 | 892.4291 | 476.1437 | 582.7339 | 633.5071 | 502.5411 | 618.8789 | 768.5132 | 843.3658 | 933.8535 | 546.4243 | 621.9121 | 563.6928 | 707.0507 | 52.251 | 0.0027082 | 18.9543 | 3.4788 | -28.3214 | 3.0951 | 6867.09 | -0.01 | 1.0047 | 1.8313 | -23.1211 | 0.74837 | 6.2829 | -33.4716 | -33.9383 | 53.0255 | 78.4313 | 36.4679 | 9.4893 | -11.2369 | 48.7862 | 27.5439
42838.4297 | 814 | 22.841 | 22.827 | 22.8148 | 22.7256 | 22.3292 | 21.6541 | 22.6571 | 21.7035 | 22.3131 | 22.3162 | 22.2844 | 21.9247 | 21.1386 | 22.1174 | 21.5645 | 21.7679 | 22.0483 | 21.0752 | 22.4829 | 26.5079 | 25.8996 | 77.8885 | 82.5602 | 22.3939 | 29.0476 | 86.089 | 638.4947 | 644.8482 | 637.4747 | 22.2799 | 28.7615 | 91.4902 | 22.3875 | 30.3654 | 89.5299 | 680.8625 | 799.7754 |  | 341.3 | 827.7363 | 853.3016 | 617.1833 |  | 293.2958 | 522.4398 | 531.0186 | 823.3967 | 862.2894 | 890.5752 | 877.3775 | 30.4172 | 147.8207 | 47.7938 | 321.3698 | 35.0833 | 42.759 | 49.2251 | 46.706 | 29.6769 |  |  | 0.15137 | 0.8049 | -139.1851 | 0.57953 | 7.9013 | -197.7934 | -203.2259 | -2.0348 | 6.4569 | 21.1584 | 15.7998 | 0.0028782 | 0.002428 | 0.00038113 | 23.0282 | 21.9953 | 22.1244 | 22.1785 | 21.984 | 21.2519 | 20.0767 | 22.1494 | 22.3254 | 22.3539 | 22.2994 | 21.901 | 21.1219 | 22.2187 | 560.4458 | 456.7867 | 436.3033 | 271.3831 | 198.0223 | 480.4652 | 276.0951 | 22.2972 | 22.0767 | 21.8226 | 22.0503 | 22.1448 | 26.3497 | 22.5335 | 59.9771 | 78.1403 | 559.9068 | 533.4927 | 544.9155 | 547.7474 | 42.4222 | 42.4127 | 729.6926 | 21.9043 | 22.1614 | 267.3867 | 21.5237 | 21.9807 | 23.5265 | 73.8807 | 89.2214 | 22.2116 | 29.3371 | 90.3015 | 699.5997 | 623.0488 | 757.4994 | 761.5361 | 689.1544 |  | 707.6665 | 753.7137 | 805.702 | 595.9994 | 618.4117 | 772.3549 |  | 382.1441 |  |  | 384.2637 | 555.786 | 645.0975 | [5 empty] | 21.8452 | 559.92 | 21.7296 | 22.059 | 379.8519 | 21.2936 | 21.8651 | 447.0465 | 600.2235 | 620.6943 |  | 882.6781 | 862.5129 | 470.7805 | 627.1597 | 742.3889 | 560.3885 | 634.9534 | 824.8573 | 884.6218 | 557.2418 | 713.3988 | 741.156 | 917.4112 | 893.5268 | 476.6006 | 582.8965 | 633.3257 | 503.5744 | 619.3496 | 767.0804 | 842.4021 | 934.0387 | 546.6825 | 622.4937 | 564.3218 | 708.3159 | 53.8715 | -0.010429 | 18.969 | 3.4383 | -28.3309 | 3.0951 | 6904.4 | -0.11 | 0.81818 | 1.7635 | -23.1904 | 1.4964 | 6.6825 | -33.4348 | -33.8908 | 52.987 | 78.2564 | 36.4478 | 9.4019 | -12.6409 | 48.7366 | 27.6452
42838.4297 | 815 | 22.8547 | 22.8286 | 22.8278 | 22.7398 | 22.3413 | 21.6548 | 22.6748 | 21.7176 | 22.3256 | 22.3248 | 22.2946 | 21.9344 | 21.1513 | 22.13 | 21.5636 | 21.7644 | 22.0498 | 21.0645 | 22.5214 | 26.5913 | 26.0046 | 78.0503 | 82.6348 | 22.398 | 29.1402 | 86.1705 | 639.0725 | 644.2337 | 637.8645 | 22.2796 | 28.8665 | 91.4872 | 22.3846 | 30.4795 | 89.538 | 680.2882 | 799.7889 |  | 342.1999 | 831.7033 | 858.2849 | 615.8312 |  | 294.6184 | 524.1718 | 530.0208 | 818.6324 | 864.3102 | 891.3956 | 877.2425 | 30.5956 | 148.5111 | 47.7108 | 322.8654 | 35.3332 | 42.8983 | 49.4469 | 46.7852 | 29.7311 |  |  | 0.26702 | -0.1834 | -137.9826 | -0.54677 | 6.0193 | -197.8177 | -203.1208 | -2.3344 | 6.6204 | 20.9843 | 16.0932 | 0.0030178 | 0.0024346 | 0.0003762 | 23.0354 | 21.9899 | 22.1225 | 22.1745 | 21.9744 | 21.2513 | 20.0689 | 22.1518 | 22.3206 | 22.3516 | 22.3016 | 21.8976 | 21.1202 | 22.2191 | 570.7556 | 474.1834 | 462.3912 | 284.2889 | 205.2648 | 482.9933 | 278.4409 | 22.2943 | 22.0779 | 21.8254 | 22.0507 | 22.1475 | 26.4182 | 22.5396 | 60.3117 | 78.2276 | 560.5146 | 533.8759 | 546.2025 | 551.7666 | 45.464 | 36.2845 | 729.085 | 21.9009 | 22.1694 | 268.3844 | 21.5229 | 21.9791 | 23.55 | 74.143 | 89.2382 | 22.2222 | 29.4642 | 90.3302 | 700.0289 | 620.8168 | 757.6661 | 761.342 | 686.6855 |  | 706.9065 | 754.7738 | 805.264 | 592.1156 | 617.8079 | 770.1608 |  | 373.2569 |  |  | 385.1829 | 556.567 | 643.1319 | [5 empty] | 21.8497 | 557.671 | 21.7359 | 22.0558 | 379.8252 | 21.2893 | 21.8613 | 447.3497 | 600.277 | 620.3136 |  | 879.3454 | 861.7694 | 471.6707 | 627.1928 | 740.9482 | 560.5521 | 635.0781 | 828.7497 | 885.0101 | 558.083 | 712.1295 | 739.7125 | 914.9595 | 895.1498 | 477.1974 | 582.9721 | 633.5221 | 504.4132 | 619.8949 | 766.0422 | 840.2325 | 935.3966 | 546.8889 | 623.5526 | 564.9822 | 708.6839 | 52.7989 | -0.0012239 | 18.9841 | 3.404 | -28.3265 | 3.0951 | 6937.77 | -0.07 | 1.0869 | -0.84272 | -23.1151 | -1.4551 | 5.8347 | -33.4486 | -33.894 | 52.872 | 78.0901 | 36.4419 | 8.7839 | -15.1902 | 48.6452 | 27.6303
42838.4297 | 816 | 22.8352 | 22.8195 | 22.815 | 22.7187 | 22.3303 | 21.6475 | 22.656 | 21.7018 | 22.3094 | 22.3188 | 22.269 | 21.9246 | 21.1357 | 22.1056 | 21.5506 | 21.7651 | 22.0509 | 21.0665 | 22.5517 | 26.6693 | 26.1153 | 78.213 | 82.7046 | 22.4014 | 29.2279 | 86.2461 | 639.3795 | 643.1246 | 638.3895 | 22.2848 | 28.988 | 91.4988 | 22.3886 | 30.6004 | 89.5354 | 679.5653 | 796.077 |  | 342.662 | 833.5135 | 858.5403 | 614.5881 |  | 295.7013 | 524.4272 | 532.6754 | 824.2405 | 866.209 | 889.669 | 876.4227 | 30.4925 | 149.0825 | 46.7404 | 324.1283 | 35.5556 | 43.0435 | 49.6531 | 46.8641 | 29.7592 |  |  | -0.10754 | -0.083521 | -145.7359 | -0.18535 | 5.6526 | -197.823 | -203.2213 | -2.065 | 6.2672 | 20.1143 | 16.0394 | 0.0028979 | 0.0025085 | 0.00035977 | 23.0418 | 21.9869 | 22.1225 | 22.171 | 21.97 | 21.2485 | 20.0652 | 22.1467 | 22.3171 | 22.3578 | 22.3044 | 21.9039 | 21.1241 | 22.2164 | 564.4283 | 457.4423 | 446.4095 | 272.8749 | 205.4461 | 485.0858 | 280.3681 | 22.2883 | 22.072 | 21.8296 | 22.043 | 22.1615 | 26.4841 | 22.5488 | 60.7468 | 78.3242 | 561.374 | 535.6252 | 548.8517 | 556.33 | 37.5115 | 30.9912 | 729.424 | 21.9039 | 22.1693 | 269.5231 | 21.5193 | 21.9696 | 23.5759 | 74.3984 | 89.2514 | 22.2168 | 29.5972 | 90.3736 | 700.1232 | 619.2527 | 757.5 | 761.2623 | 687.2378 |  | 706.3196 | 752.9293 | 804.6665 | 588.563 | 617.1472 | 767.4275 |  | 353.4361 |  |  | 385.5191 | 558.0195 | 643.57 | [5 empty] | 21.8416 | 555.454 | 21.7341 | 22.0583 | 379.5934 | 21.29 | 21.8636 | 447.3984 | 600.5946 | 619.9021 |  | 875.2966 | 862.4487 | 472.7895 | 627.7271 | 739.6309 | 560.781 | 634.7867 | 833.7948 | 879.2109 | 559.1117 | 710.5032 | 739.6964 | 914.0781 | 895.7719 | 477.7771 | 582.8559 | 634.1316 | 505.3997 | 620.3192 | 764.0266 | 839.1599 | 938.1731 | 547.2898 | 623.1168 | 565.6598 | 708.878 | 51.3107 | 0.0010651 | 18.9994 | 3.3719 | -28.3575 | 3.0951 | 6935.05 | -0.02 | -0.68998 | -0.56879 | -23.7595 | -0.84732 | 5.65 | -33.4242 | -33.8772 | 52.7152 | 77.9549 | 36.4164 | 9.9255 | -13.1266 | 48.5177 | 27.6405
42838.4297 | 817 | 22.844 | 22.8268 | 22.8142 | 22.7229 | 22.3306 | 21.6523 | 22.6589 | 21.7042 | 22.3082 | 22.3103 | 22.2738 | 21.9301 | 21.1349 | 22.1152 | 21.5538 | 21.7583 | 22.0431 | 21.0804 | 22.5876 | 26.7517 | 26.2243 | 78.3846 | 82.7888 | 22.4064 | 29.3184 | 86.3191 | 638.9027 | 640.9877 | 637.7346 | 22.2904 | 29.1163 | 91.5044 | 22.3931 | 30.7277 | 89.5318 | 678.8912 | 793.372 |  | 343.1512 | 842.0112 | 865.7757 | 616.7707 |  | 296.7674 | 524.343 | 535.5689 | 827.8636 | 869.5869 | 888.9628 | 875.3606 | 30.0438 | 149.6483 | 45.668 | 325.2987 | 35.786 | 43.1876 | 49.8693 | 46.9474 | 29.7621 |  |  | -0.09571 | 1.0388 | -137.8426 | -0.070354 | 5.1342 | -197.869 | -203.3087 | -2.113 | 6.9742 | 22.0444 | 16.6513 | 0.002962 | 0.0025414 | 0.00036141 | 23.0536 | 21.9935 | 22.1239 | 22.1726 | 21.9643 | 21.2493 | 20.0642 | 22.1444 | 22.316 | 22.3538 | 22.2941 | 21.9046 | 21.1292 | 22.2083 | 542.7414 | 434.3777 | 419.1836 | 279.754 | 212.2959 | 486.1493 | 281.9126 | 22.2924 | 22.0654 | 21.8249 | 22.0444 | 22.1713 | 26.5489 | 22.5595 | 61.2531 | 78.4248 | 562.0987 | 536.6076 | 550.0175 | 555.4863 | 41.9279 | 31.1885 | 728.9495 | 21.9108 | 22.1705 | 270.3264 | 21.5194 | 21.969 | 23.613 | 74.6669 | 89.2597 | 22.2305 | 29.7329 | 90.4058 | 698.3362 | 617.7794 | 758.0617 | 762.3532 | 684.1826 |  | 705.5374 | 755.736 | 804.2587 | 587.0818 | 616.444 | 765.7838 |  | 349.1353 |  |  | 386.3079 | 559.6172 | 643.0176 | [5 empty] | 21.8474 | 554.041 | 21.7305 | 22.0625 | 380.2207 | 21.2841 | 21.8672 | 447.5254 | 600.6433 | 619.5959 |  | 877.0684 | 862.0015 | 474.1711 | 628.0629 | 737.846 | 560.906 | 634.6432 | 836.0758 | 879.2465 | 560.1528 | 707.1155 | 739.4189 | 914.8471 | 895.8256 | 478.1606 | 582.6348 | 634.4031 | 506.601 | 620.6072 | 761.6344 | 838.9694 | 939.2154 | 548.3838 | 622.3156 | 566.2464 | 709.96 | 53.7307 | -0.00010749 | 19.0131 | 3.3351 | -28.2184 | 3.0951 | 6886.32 | 0.01 | -0.65069 | 2.0059 | -23.1059 | -0.52201 | 5.383 | -33.418 | -33.8742 | 52.6118 | 77.7499 | 36.3256 | 12.5587 | -9.8702 | 48.3063 | 27.7797
42838.4297 | 818 | 22.8485 | 22.832 | 22.8186 | 22.7321 | 22.329 | 21.6568 | 22.6679 | 21.7121 | 22.3235 | 22.3259 | 22.2823 | 21.931 | 21.1446 | 22.1221 | 21.5447 | 21.7582 | 22.0378 | 21.0645 | 22.63 | 26.8335 | 26.3377 | 78.5408 | 82.8636 | 22.4065 | 29.4128 | 86.3942 | 638.0775 | 639.2672 | 636.8332 | 22.2916 | 29.2337 | 91.5041 | 22.3927 | 30.8379 | 89.5344 | 678.4614 | 796.9417 |  | 343.83 | 844.6313 | 867.0559 | 619.7718 |  | 297.4797 | 524.7775 | 541.1082 | 833.7918 | 870.4846 | 886.8458 | 874.703 | 29.8249 | 150.3196 | 45.6381 | 326.549 | 36.0741 | 43.3477 | 50.0741 | 47.0498 | 29.8044 |  |  | 0.12574 | 0.38895 | -141.0481 | 0.23389 | 7.4085 | -197.8335 | -203.2975 | -2.4442 | 7.2947 | 22.24 | 16.2236 | 0.002824 | 0.0023426 | 0.00041398 | 23.0694 | 21.9926 | 22.1277 | 22.1767 | 21.9682 | 21.2461 | 20.0624 | 22.1484 | 22.321 | 22.36 | 22.2945 | 21.9057 | 21.1294 | 22.2139 | 527.7712 | 429.2279 | 408.9329 | 277.8077 | 219.3781 | 487.1938 | 283.2071 | 22.2867 | 22.0673 | 21.8248 | 22.0376 | 22.1757 | 26.62 | 22.5746 | 61.665 | 78.5186 | 562.6524 | 536.4587 | 549.8867 | 552.8322 | 43.9146 | 29.2372 | 729.8309 | 21.9156 | 22.1627 | 270.5333 | 21.5283 | 21.982 | 23.6468 | 74.9313 | 89.2806 | 22.2428 | 29.8641 | 90.4209 | 698.1759 | 615.3691 | 760.1291 | 764.6696 | 683.722 |  | 704.7845 | 756.0051 | 803.8658 | 585.4157 | 615.738 | 764.8524 |  | 348.7216 |  |  | 387.7248 | 560.6139 | 641.6372 | [5 empty] | 21.8404 | 551.9539 | 21.7286 | 22.053 | 382.0675 | 21.2909 | 21.8614 | 447.5767 | 600.2133 | 619.7172 |  | 881.6764 | 860.6396 | 475.2973 | 628.2193 | 735.8038 | 560.9591 | 635.1637 | 842.6098 | 878.9802 | 561.0764 | 704.3588 | 737.0549 | 913.7327 | 894.4762 | 477.942 | 582.8696 | 634.0549 | 507.6436 | 621.5152 | 760.9887 | 839.3881 | 939.7815 | 549.3996 | 621.5231 | 566.8449 | 713.1488 | 53.9032 | 0.0011564 | 19.0253 | 3.3093 | -28.398 | 3.0951 | 6814.39 | -0.1 | 0.74545 | 1.2277 | -23.3793 | 0.95204 | 6.4604 | -33.3845 | -33.8424 | 52.4438 | 77.6201 | 36.2397 | 14.442 | -8.5371 | 48.1269 | 27.942
42838.4298 | 819 | 22.8467 | 22.825 | 22.8223 | 22.7284 | 22.3358 | 21.6575 | 22.6676 | 21.7093 | 22.3177 | 22.3207 | 22.2913 | 21.9284 | 21.1469 | 22.1148 | 21.5571 | 21.7668 | 22.0451 | 21.0766 | 22.6793 | 26.9325 | 26.4588 | 78.7108 | 82.9386 | 22.4239 | 29.5233 | 86.4809 | 638.7201 | 639.237 | 637.3821 | 22.2954 | 29.3481 | 91.5146 | 22.4054 | 30.9624 | 89.5368 | 678.3674 | 794.9123 |  | 344.7459 | 840.7665 | 863.5222 | 622.7069 |  | 298.4424 | 526.5943 | 543.0267 | 837.172 | 870.0848 | 884.4543 | 874.0022 | 29.541 | 150.9533 | 46.4912 | 327.6725 | 36.3693 | 43.4963 | 50.2631 | 47.1497 | 29.8636 |  |  | 0.28147 | 0.67939 | -139.0235 | -0.34306 | 6.9038 | -197.8578 | -203.2377 | -2.0749 | 6.4754 | 21.8827 | 16.4998 | 0.0026662 | 0.0022391 | 0.00035977 | 23.0731 | 21.9896 | 22.1273 | 22.1637 | 21.9694 | 21.2404 | 20.0648 | 22.1423 | 22.3184 | 22.3559 | 22.2895 | 21.9024 | 21.1279 | 22.2137 | 533.7826 | 402.2097 | 391.0799 | 275.9674 | 223.9195 | 488.7012 | 284.4067 | 22.2925 | 22.0705 | 21.8358 | 22.0482 | 22.1903 | 26.7024 | 22.5988 | 61.9919 | 78.6275 | 563.2323 | 536.0655 | 549.7574 | 552.9629 | 40.5346 | 26.8082 | 729.6599 | 21.9095 | 22.1631 | 271.0809 | 21.5175 | 21.9823 | 23.6702 | 75.1938 | 89.2923 | 22.241 | 29.9873 | 90.4412 | 698.198 | 613.615 | 761.5942 | 765.9422 | 686.4117 |  | 704.4094 | 752.1954 | 803.2564 | 584.1237 | 614.9648 | 762.9365 |  | 349.6083 |  |  | 388.6523 | 562.3257 | 642.4816 | [5 empty] | 21.8463 | 550.0827 | 21.7377 | 22.0568 | 382.4495 | 21.2949 | 21.8635 | 447.6043 | 599.8903 | 619.0605 |  | 882.3364 | 859.851 | 476.2631 | 628.2648 | 735.4656 | 561.0689 | 633.4567 | 848.8602 | 876.6582 | 562.2678 | 702.8745 | 735.7205 | 913.1654 | 893.483 | 476.8043 | 583.1494 | 633.637 | 508.9223 | 622.2424 | 760.1734 | 842.4971 | 940.0314 | 549.9112 | 620.1567 | 567.8524 | 711.7887 | 53.1631 | 0.00047533 | 19.038 | 3.2954 | -28.2319 | 3.0951 | 6728.46 | 0.04 | 1.1157 | 1.6244 | -23.2374 | -1.1543 | 6.23 | -33.3521 | -33.8025 | 52.2792 | 77.5365 | 36.1311 | 14.0923 | -6.3731 | 48.0244 | 28.0314
42838.4298 | 820 | 22.8477 | 22.8251 | 22.8225 | 22.7271 | 22.336 | 21.6485 | 22.6659 | 21.7076 | 22.3189 | 22.3137 | 22.2911 | 21.9286 | 21.1422 | 22.1192 | 21.5595 | 21.765 | 22.0521 | 21.0673 | 22.7266 | 27.0176 | 26.5719 | 78.8739 | 83.0078 | 22.4192 | 29.6191 | 86.5509 | 638.7719 | 640.5581 | 637.3504 | 22.3037 | 29.462 | 91.524 | 22.4117 | 31.0835 | 89.5373 | 678.4117 | 791.7621 |  | 337.5351 | 832.3786 | 855.9475 | 621.5178 |  | 298.8164 | 529.4341 | 541.8761 | 838.2692 | 868.9156 | 883.5679 | 874.5092 | 29.1734 | 151.7248 | 47.022 | 329.1421 | 36.6935 | 43.673 | 50.4494 | 47.264 | 29.9197 |  |  | 0.32747 | 0.21547 | -138.0358 | 0.18066 | 6.6528 | -197.7895 | -203.3619 | -2.3246 | 6.8691 | 22.2815 | 16.4791 | 0.0028355 | 0.0023771 | 0.00039591 | 23.0926 | 21.994 | 22.1224 | 22.1791 | 21.97 | 21.2537 | 20.0598 | 22.1448 | 22.3199 | 22.3586 | 22.3 | 21.9078 | 21.1257 | 22.2312 | 528.8058 | 421.2193 | 410.5566 | 275.4108 | 222.9077 | 490.0851 | 285.9557 | 22.2962 | 22.0787 | 21.8374 | 22.0506 | 22.2125 | 26.771 | 22.6146 | 62.3003 | 78.7194 | 563.8613 | 537.1539 | 551.2923 | 555.8199 | 40.8643 | 39.3452 | 728.8862 | 21.9067 | 22.1577 | 271.499 | 21.5137 | 21.9757 | 23.7077 | 75.4513 | 89.306 | 22.2469 | 30.1152 | 90.4639 | 698.3708 | 612.8092 | 763.2748 | 767.565 | 687.1216 |  | 704.1288 | 754.9855 | 803.0786 | 585.5352 | 614.3491 | 764.011 |  | 350.96 |  |  | 389.2506 | 564.5928 | 644.0087 | [5 empty] | 21.8417 | 550.2877 | 21.7244 | 22.0506 | 382.5393 | 21.2829 | 21.8445 | 447.7896 | 598.9381 | 619.2428 |  | 887.2957 | 858.3414 | 477.3122 | 628.3258 | 734.5828 | 561.5303 | 631.3762 | 852.5879 | 879.8113 | 563.622 | 704.3514 | 734.1428 | 915.1424 | 894.243 | 476.8434 | 583.1141 | 634.8395 | 510.3777 | 622.6144 | 759.4836 | 844.2399 | 938.0232 | 550.1027 | 618.4133 | 569.1154 | 709.521 | 54.2757 | 0.00055255 | 19.0513 | 3.2771 | -28.2542 | 3.0951 | 6697.44 | -0.07 | 1.2034 | 0.91644 | -23.1957 | 0.83916 | 6.1134 | -33.3336 | -33.7999 | 52.1922 | 77.4038 | 35.9771 | 14.9382 | -8.3039 | 48.0673 | 28.0531
42838.4298 | 821 | 22.8414 | 22.8304 | 22.8129 | 22.7237 | 22.3379 | 21.6524 | 22.6646 | 21.7131 | 22.3183 | 22.3141 | 22.2822 | 21.926 | 21.1389 | 22.1126 | 21.5549 | 21.769 | 22.0476 | 21.0761 | 22.7761 | 27.1047 | 26.6968 | 79.0274 | 83.0592 | 22.4261 | 29.7109 | 86.632 | 638.6725 | 638.3742 | 637.2624 | 22.3035 | 29.5828 | 91.5368 | 22.4054 | 31.2125 | 89.5256 | 678.023 | 788.2185 |  | 324.1281 | 820.4919 | 843.4298 | 618.2856 |  | 299.8816 | 531.2782 | 542.5116 | 831.6507 | 868.6514 | 883.6475 | 873.5192 | 29.0715 | 152.4338 | 46.9327 | 330.3169 | 36.9791 | 43.8592 | 50.6293 | 47.3851 | 29.971 |  |  | 0.056742 | 1.1512 | -135.8838 | -0.12621 | 6.0706 | -197.8217 | -203.2338 | -2.9377 | 7.4467 | 23.4169 | 16.6353 | 0.0028059 | 0.0023163 | 0.00037291 | 23.1136 | 21.9998 | 22.122 | 22.1779 | 21.9726 | 21.2497 | 20.0713 | 22.1542 | 22.3234 | 22.3582 | 22.3024 | 21.9043 | 21.1313 | 22.2247 | 529.9166 | 441.4493 | 430.4604 | 278.2803 | 221.7145 | 491.5353 | 287.8007 | 22.2868 | 22.0761 | 21.8329 | 22.0449 | 22.2141 | 26.8366 | 22.6193 | 62.7207 | 78.8098 | 564.4647 | 538.6379 | 552.3233 | 555.5142 | 42.4733 | 33.3706 | 731.6675 | 21.9098 | 22.1574 | 271.7518 | 21.5125 | 21.9632 | 23.7397 | 75.7162 | 89.3085 | 22.2362 | 30.2474 | 90.4946 | 700.6239 | 612.0978 | 765.9136 | 770.582 | 687.3349 |  | 703.7667 | 761.0706 | 803.3745 | 589.5791 | 613.9229 | 768.6773 |  | 352.2963 |  |  | 390.5506 | 567.2511 | 643.6915 | [5 empty] | 21.8436 | 551.5342 | 21.7334 | 22.0555 | 382.2615 | 21.2809 | 21.85 | 448.4194 | 597.941 | 619.2738 |  | 891.1122 | 858.9752 | 478.6092 | 628.1962 | 733.5051 | 561.8954 | 631.8514 | 853.1656 | 886.0602 | 564.607 | 704.8022 | 734.0052 | 919.4509 | 894.5309 | 476.8164 | 583.3025 | 635.8018 | 511.7031 | 622.6887 | 758.0119 | 846.8957 | 937.5071 | 550.6773 | 617.1499 | 570.1349 | 704.8551 | 55.3518 | -0.00062707 | 19.0631 | 3.2616 | -28.4967 | 3.0951 | 6739.72 | -0.09 | 0.50089 | 2.1207 | -23.0406 | -0.70219 | 5.84 | -33.3375 | -33.7904 | 52.0997 | 77.3267 | 35.7854 | 15.1226 | -10.2369 | 48.0704 | 28.1587
42838.4298 | 822 | 22.8393 | 22.8275 | 22.8097 | 22.722 | 22.3358 | 21.653 | 22.6652 | 21.714 | 22.3139 | 22.3154 | 22.2858 | 21.9252 | 21.1392 | 22.108 | 21.5592 | 21.767 | 22.0503 | 21.0721 | 22.8137 | 27.188 | 26.8209 | 79.1788 | 83.1284 | 22.4356 | 29.8047 | 86.6782 | 636.8555 | 637.5979 | 635.2451 | 22.3066 | 29.7071 | 91.5505 | 22.4174 | 31.3348 | 89.5237 | 677.5943 | 793.1549 |  | 318.2338 | 814.8008 | 834.9733 | 616.6019 |  | 300.9167 | 532.4629 | 544.344 | 834.4632 | 868.5714 | 886.5336 | 874.0267 | 29.1121 | 153.2528 | 46.5848 | 331.7527 | 37.2885 | 44.0274 | 50.805 | 47.4855 | 30.0222 |  |  | 0.24008 | 0.68531 | -135.8877 | -0.36803 | 4.9449 | -197.8289 | -203.0367 | -2.2175 | 7.1036 | 22.5186 | 17.0728 | 0.0026662 | 0.0021964 | 0.00039098 | 23.1148 | 22.0002 | 22.118 | 22.1735 | 21.9699 | 21.2499 | 20.0676 | 22.147 | 22.3195 | 22.3609 | 22.2988 | 21.8987 | 21.1295 | 22.2218 | 525.9294 | 435.4047 | 421.2485 | 271.8591 | 213.2698 | 493.1575 | 289.2771 | 22.2873 | 22.0782 | 21.8398 | 22.0529 | 22.2257 | 26.9082 | 22.635 | 63.1238 | 78.8979 | 565.017 | 539.7484 | 553.4246 | 557.0038 | 40.9485 | 28.8773 | 734.7726 | 21.9096 | 22.1579 | 272.1108 | 21.519 | 21.9677 | 23.7714 | 75.9651 | 89.3265 | 22.2383 | 30.3862 | 90.5325 | 704.3788 | 612.321 | 768.3536 | 773.1257 | 693.2918 |  | 703.6803 | 764.5827 | 803.8461 | 592.7191 | 613.6289 | 772.6709 |  | 353.6216 |  |  | 392.0408 | 568.7582 | 646.0119 | [5 empty] | 21.8491 | 552.5638 | 21.7338 | 22.0562 | 381.6491 | 21.2889 | 21.8536 | 449.0665 | 597.638 | 619.3333 |  | 896.0295 | 859.394 | 479.616 | 628.2108 | 732.9839 | 561.8528 | 632.0315 | 861.7472 | 887.1599 | 565.398 | 705.42 | 737.0676 | 922.5679 | 893.248 | 477.3886 | 583.1194 | 635.6993 | 512.8708 | 622.837 | 756.7394 | 849.8481 | 935.2525 | 551.3723 | 617.8415 | 570.8109 | 704.371 | 56.3214 | -0.00033919 | 19.0758 | 3.2454 | -28.3452 | 3.0951 | 6793.65 | -0.15 | 1.0292 | 1.6375 | -23.0579 | -1.2 | 5.2774 | -33.3796 | -33.8161 | 51.9135 | 77.3757 | 35.6435 | 15.9109 | -8.99 | 48.0216 | 28.2063
42838.4298 | 823 | 22.8485 | 22.8328 | 22.8217 | 22.726 | 22.3392 | 21.6569 | 22.665 | 21.7086 | 22.3081 | 22.3175 | 22.2896 | 21.9269 | 21.144 | 22.1168 | 21.5453 | 21.7626 | 22.0512 | 21.0687 | 22.8583 | 27.2775 | 26.9374 | 79.3321 | 83.1845 | 22.4382 | 29.8982 | 86.6927 | 634.905 | 636.8166 | 633.5403 | 22.3206 | 29.8173 | 91.5639 | 22.4177 | 31.465 | 89.5192 | 677.1402 | 795.3063 |  | 318.8612 | 821.188 | 841.6812 | 616.6609 |  | 302.1719 | 534.577 | 544.7484 | 840.2777 | 870.7678 | 891.5648 | 877.4454 | 29.157 | 154.0275 | 45.9126 | 333.2654 | 37.6647 | 44.1956 | 50.9697 | 47.5827 | 29.9633 |  |  | 0.19014 | 0.24701 | -140.7116 | -0.078898 | 6.4405 | -197.8315 | -203.3002 | -1.4854 | 6.9831 | 22.3291 | 16.9961 | 0.0027287 | 0.0022785 | 0.00032035 | 23.1156 | 21.9948 | 22.1192 | 22.175 | 21.9691 | 21.2469 | 20.0651 | 22.1377 | 22.312 | 22.3551 | 22.2941 | 21.9011 | 21.1262 | 22.2167 | 532.3871 | 413.4614 | 403.9898 | 278.919 | 216.5874 | 494.9278 | 290.5782 | 22.284 | 22.0714 | 21.8432 | 22.0382 | 22.2429 | 26.9834 | 22.6439 | 63.4856 | 78.9972 | 565.6235 | 541.1139 | 554.6831 | 558.34 | 51.6972 | 35.0839 | 737.9913 | 21.9096 | 22.1562 | 272.4454 | 21.5159 | 21.9696 | 23.8092 | 76.1872 | 89.3445 | 22.2421 | 30.5239 | 90.5755 | 707.9081 | 613.2774 | 769.5629 | 774.2673 | 697.7973 |  | 703.661 | 777.7115 | 804.6814 | 597.1453 | 613.4851 | 779.6144 |  | 355.1211 |  |  | 392.4754 | 569.2541 | 648.856 | [5 empty] | 21.8464 | 554.2701 | 21.726 | 22.0604 | 380.689 | 21.2828 | 21.8613 | 449.8807 | 597.3311 | 618.6089 |  | 903.1267 | 859.317 | 480.3907 | 628.5445 | 731.2183 | 561.846 | 631.9564 | 865.2723 | 891.2513 | 566.4214 | 704.2252 | 740.7535 | 924.6249 | 891.5854 | 478.9649 | 583.0523 | 634.3688 | 513.7281 | 623.3076 | 755.9315 | 855.9141 | 936.1182 | 551.8475 | 617.2227 | 571.4729 | 702.3249 | 56.2335 | 0.0002787 | 19.0893 | 3.2322 | -28.3525 | 3.0951 | 6834.78 | -0.16 | 0.91502 | 0.98437 | -23.4944 | -0.55633 | 6.0358 | -33.4522 | -33.9114 | 51.7837 | 77.2712 | 35.4938 | 15.5714 | -6.8752 | 47.9189 | 28.2671
42838.4298 | 824 | 22.8427 | 22.8215 | 22.8087 | 22.7172 | 22.3269 | 21.6592 | 22.6597 | 21.7036 | 22.3117 | 22.3144 | 22.2862 | 21.9351 | 21.1326 | 22.1108 | 21.5532 | 21.7704 | 22.0531 | 21.0738 | 22.9036 | 27.3742 | 27.065 | 79.4865 | 83.2452 | 22.4528 | 30.0013 | 86.7787 | 632.8826 | 635.8504 | 631.7845 | 22.3141 | 29.9464 | 91.5836 | 22.4206 | 31.5922 | 89.5249 | 676.8289 | 792.2097 |  | 319.3205 | 826.7487 | 844.599 | 618.789 |  | 302.9334 | 535.7456 | 543.8453 | 843.0956 | 871.4175 | 895.5753 | 882.4389 | 29.5876 | 154.6886 | 45.3322 | 334.5413 | 37.9855 | 44.3783 | 51.1289 | 47.7114 | 30.0677 |  |  | 0.22365 | 0.53483 | -142.9517 | -0.15972 | 5.3694 | -197.823 | -203.2299 | -2.4054 | 7.1415 | 22.4342 | 17.1848 | 0.0026433 | 0.0022325 | 0.00036141 | 23.1271 | 21.9905 | 22.1214 | 22.1703 | 21.9635 | 21.2428 | 20.0647 | 22.1436 | 22.3173 | 22.3516 | 22.29 | 21.9067 | 21.1233 | 22.212 | 543.7914 | 423.4353 | 418.5033 | 289.4727 | 217.9669 | 496.9149 | 292.4039 | 22.2848 | 22.0749 | 21.8424 | 22.0426 | 22.2568 | 27.0643 | 22.6624 | 63.8764 | 79.0918 | 566.0382 | 540.8432 | 553.8667 | 553.6816 | 42.3121 | 28.2696 | 743.2892 | 21.9113 | 22.1641 | 273.066 | 21.515 | 21.9707 | 23.8583 | 76.4142 | 89.3459 | 22.2528 | 30.6664 | 90.6238 | 711.107 | 614.5135 | 770.3953 | 774.6809 | 709.2464 |  | 704.0655 | 780.8769 | 805.4035 | 598.7187 | 613.3174 | 783.153 |  | 356.7113 |  |  | 393.7421 | 569.2141 | 653.9181 | [5 empty] | 21.847 | 555.6899 | 21.7315 | 22.0581 | 380.6201 | 21.2884 | 21.8576 | 450.3387 | 597.178 | 618.1157 |  | 907.352 | 859.8022 | 481.3536 | 629.2548 | 731.1042 | 562.1823 | 632.1173 | 870.9895 | 893.8976 | 567.4298 | 704.7936 | 740.7003 | 927.0719 | 893.7308 | 479.2483 | 582.9732 | 632.7283 | 514.8997 | 623.6297 | 754.5624 | 852.9154 | 937.8952 | 552.3627 | 616.828 | 572.5653 | 700.7736 | 52.7366 | 0.00038403 | 19.1021 | 3.2263 | -28.3563 | 3.0951 | 6864.03 | -0.01 | 0.99143 | 1.4495 | -23.6978 | -0.79213 | 5.5206 | -33.509 | -33.9639 | 51.5625 | 77.4086 | 35.4189 | 14.73 | -8.2104 | 47.7906 | 28.4636
42838.4298 | 825 | 22.842 | 22.8172 | 22.8102 | 22.7296 | 22.3279 | 21.662 | 22.6596 | 21.7148 | 22.3152 | 22.3202 | 22.2796 | 21.9267 | 21.1393 | 22.1142 | 21.5576 | 21.7698 | 22.063 | 21.0821 | 22.9562 | 27.4562 | 27.1961 | 79.639 | 83.3018 | 22.453 | 30.0966 | 86.8459 | 632.0816 | 635.3378 | 631.2902 | 22.3178 | 30.061 | 91.5916 | 22.4277 | 31.708 | 89.5254 | 676.6672 | 793.835 |  | 319.3444 | 835.8925 | 851.5064 | 623.123 |  | 304.1277 | 537.8288 | 543.4096 | 846.0141 | 874.8981 | 898.6522 | 888.0691 | 30.1706 | 155.4292 | 44.5265 | 335.9435 | 38.2974 | 44.5639 | 51.2839 | 47.84 | 30.1318 |  |  | 0.21577 | 1.2077 | -124.8232 | 0.24177 | 5.8754 | -197.8342 | -203.3021 | -1.7391 | 7.2896 | 22.5532 | 17.3695 | 0.0025595 | 0.0021767 | 0.00039427 | 23.1475 | 22.0003 | 22.1284 | 22.1757 | 21.9709 | 21.2468 | 20.066 | 22.1453 | 22.3232 | 22.3579 | 22.3032 | 21.9097 | 21.1327 | 22.2222 | 535.0731 | 425.7281 | 417.8726 | 283.6344 | 214.3752 | 498.101 | 293.8193 | 22.2939 | 22.0695 | 21.8488 | 22.0479 | 22.2786 | 27.1337 | 22.6818 | 64.2191 | 79.1898 | 566.3104 | 539.6242 | 552.6504 | 551.9931 | 58.0737 | 40.8961 | 744.6791 | 21.9118 | 22.1634 | 273.8458 | 21.514 | 21.9728 | 23.896 | 76.6211 | 89.3555 | 22.2637 | 30.7942 | 90.6585 | 711.57 | 615.3151 | 770.9338 | 775.3088 | 708.0992 |  | 704.1579 | 776.0141 | 805.6565 | 598.6332 | 613.1176 | 782.6309 |  | 358.1162 |  |  | 395.0734 | 568.6803 | 655.239 | [5 empty] | 21.8445 | 556.5813 | 21.7332 | 22.0542 | 382.2132 | 21.2938 | 21.8604 | 450.4915 | 596.9431 | 618.1646 |  | 908.4468 | 860.5837 | 482.2281 | 630.1367 | 730.641 | 562.5284 | 632.6901 | 872.2306 | 897.5386 | 568.4202 | 707.469 | 740.3829 | 927.8684 | 895.4956 | 479.3393 | 582.8373 | 630.9915 | 516.0909 | 623.7958 | 754.7446 | 853.1916 | 940.3481 | 552.3575 | 616.4347 | 573.5979 | 699.6055 | 52.9942 | 0.00041916 | 19.1146 | 3.224 | -28.3492 | 3.0951 | 6863.47 | -0.07 | 0.97353 | 2.181 | -22.1727 | 0.97584 | 5.7825 | -33.554 | -34.0146 | 51.6165 | 77.6227 | 35.3842 | 15.9536 | -7.9247 | 47.6343 | 28.5545
42838.4298 | 826 | 22.8366 | 22.8173 | 22.8136 | 22.7217 | 22.3335 | 21.6521 | 22.6685 | 21.7084 | 22.3148 | 22.3227 | 22.2804 | 21.9248 | 21.1351 | 22.117 | 21.551 | 21.7626 | 22.0519 | 21.0701 | 23.0002 | 27.5442 | 27.3252 | 79.7782 | 83.3626 | 22.4473 | 30.1861 | 86.9056 | 630.915 | 636.06 | 630.033 | 22.3218 | 30.1723 | 91.6055 | 22.4334 | 31.8353 | 89.5239 | 676.8026 | 790.4205 |  | 319.9551 | 835.652 | 848.8895 | 625.9507 |  | 304.9074 | 539.3333 | 543.3985 | 848.6055 | 877.014 | 897.1268 | 888.5475 | 30.1088 | 156.0167 | 44.5399 | 337.1768 | 38.6452 | 44.7755 | 51.4263 | 47.9417 | 30.1883 |  |  | 0.13034 | -0.12163 | -119.8837 | -0.43177 | 7.0871 | -197.8407 | -203.333 | -2.4501 | 7.2902 | 22.6063 | 16.8864 | 0.0026104 | 0.0022079 | 0.00035649 | 23.1678 | 22.0056 | 22.1248 | 22.1748 | 21.976 | 21.2508 | 20.0689 | 22.1459 | 22.3197 | 22.3558 | 22.3072 | 21.9037 | 21.1378 | 22.2194 | 544.7396 | 456.5452 | 459.704 | 282.005 | 210.13 | 500.1922 | 295.9841 | 22.2905 | 22.0752 | 21.8491 | 22.0521 | 22.2916 | 27.2041 | 22.6996 | 64.5046 | 79.2702 | 566.6593 | 538.1144 | 551.5665 | 552.5854 | 51.5023 | 41.8568 | 743.9559 | 21.9217 | 22.1691 | 274.7981 | 21.5282 | 21.9804 | 23.9343 | 76.8483 | 89.3736 | 22.2758 | 30.9437 | 90.6963 | 711.1632 | 615.6553 | 771.1372 | 775.2327 | 704.1253 |  | 704.0113 | 769.1197 | 805.5491 | 596.0029 | 612.8187 | 780.1107 |  | 359.4901 |  |  | 396.3578 | 567.1241 | 654.3438 | [5 empty] | 21.842 | 556.1991 | 21.7343 | 22.0581 | 383.549 | 21.2907 | 21.8615 | 450.9118 | 596.7727 | 618.2991 |  | 907.0908 | 861.7651 | 482.9468 | 630.5251 | 730.3799 | 563.1116 | 633.7483 | 867.5067 | 898.7741 | 569.2542 | 708.425 | 741.3831 | 930.6263 | 894.131 | 479.8163 | 582.7318 | 630.8643 | 517.3009 | 624.2545 | 755.5744 | 855.0475 | 940.7594 | 552.4412 | 616.4524 | 574.4039 | 698.405 | 54.2365 | 0.0002085 | 19.125 | 3.2202 | -28.3777 | 3.095 | 6884.11 | -0.13 | 0.75612 | -0.69279 | -21.7497 | -1.3053 | 6.3467 | -33.5327 | -33.995 | 51.6918 | 77.7807 | 35.4018 | 15.3304 | -12.2421 | 47.5858 | 28.5946
42838.4298 | 827 | 22.8416 | 22.8171 | 22.8119 | 22.7259 | 22.3349 | 21.6504 | 22.6708 | 21.7041 | 22.3113 | 22.3181 | 22.2832 | 21.9261 | 21.1357 | 22.1107 | 21.5529 | 21.7659 | 22.056 | 21.0734 | 23.0521 | 27.6365 | 27.4579 | 79.9261 | 83.4354 | 22.4571 | 30.2849 | 86.9774 | 630.3402 | 636.4472 | 629.6579 | 22.3294 | 30.2902 | 91.6244 | 22.4366 | 31.9617 | 89.52 | 676.8625 | 789.4529 |  | 321.2974 | 834.8032 | 846.3299 | 624.2428 |  | 305.941 | 540.5338 | 542.7444 | 848.2933 | 878.2375 | 896.6027 | 889.7952 | 30.2348 | 156.7157 | 44.714 | 338.4229 | 38.9818 | 44.9972 | 51.5571 | 48.0709 | 30.2404 |  |  | 0.3577 | 0.27461 | -123.0339 | -0.091382 | 6.6331 | -197.8512 | -203.308 | -1.8679 | 6.8459 | 22.0977 | 17.2014 | 0.0024165 | 0.0021488 | 0.00034499 | 23.1698 | 22.0009 | 22.1174 | 22.1728 | 21.9668 | 21.2484 | 20.0621 | 22.1484 | 22.3198 | 22.3543 | 22.2995 | 21.8932 | 21.1284 | 22.2086 | 565.7915 | 471.5245 | 465.973 | 287.5008 | 216.334 | 502.4571 | 297.8794 | 22.2808 | 22.0769 | 21.8464 | 22.0474 | 22.3039 | 27.2721 | 22.7114 | 64.6853 | 79.3545 | 567.0184 | 536.4013 | 549.6572 | 551.9771 | 40.0099 | 24.7783 | 741.583 | 21.9144 | 22.1581 | 275.2464 | 21.5221 | 21.9656 | 23.9669 | 77.0608 | 89.3847 | 22.2773 | 31.0697 | 90.7115 | 710.0946 | 616.0938 | 770.8716 | 774.851 | 705.1593 |  | 703.9528 | 763.2752 | 805.1132 | 596.3742 | 612.5687 | 778.6465 |  | 360.6866 |  |  | 397.8692 | 565.7137 | 653.4582 | [5 empty] | 21.8456 | 556.1601 | 21.7353 | 22.0504 | 385.1171 | 21.2946 | 21.8603 | 451.2925 | 598.1091 | 618.1463 |  | 904.4328 | 862.6628 | 483.5033 | 630.2703 | 729.7804 | 563.7159 | 634.811 | 862.4368 | 899.2621 | 569.7615 | 709.2536 | 741.7741 | 933.7572 | 892.4933 | 480.1657 | 582.7546 | 630.0802 | 518.2916 | 624.9291 | 755.9666 | 858.9401 | 942.3578 | 552.585 | 615.9064 | 575.1929 | 699.1334 | 54.2078 | 0.0047516 | 19.1352 | 3.2004 | -28.3394 | 3.095 | 6931.31 | -0.05 | 1.2523 | 1.0417 | -22.0499 | -0.60093 | 6.1386 | -33.5261 | -33.9853 | 51.6491 | 77.8069 | 35.3451 | 13.4816 | -12.6485 | 47.6466 | 28.6698
42838.4299 | 828 | 22.8332 | 22.8188 | 22.8114 | 22.7272 | 22.3297 | 21.6495 | 22.6637 | 21.704 | 22.3049 | 22.3124 | 22.2842 | 21.9236 | 21.1403 | 22.1064 | 21.5548 | 21.7732 | 22.0676 | 21.0788 | 23.1003 | 27.7301 | 27.5914 | 80.0737 | 83.5125 | 22.468 | 30.3914 | 87.0469 | 630.8392 | 635.2298 | 630.2972 | 22.3313 | 30.4027 | 91.6515 | 22.4391 | 32.0876 | 89.517 | 676.7916 | 798.6403 |  | 322.2976 | 841.545 | 851.3063 | 623.2546 |  | 307.3402 | 542.8555 | 542.8882 | 841.7223 | 879.9837 | 897.5881 | 890.5959 | 30.2256 | 157.3614 | 44.7345 | 339.5998 | 39.3796 | 45.2365 | 51.6824 | 48.2058 | 30.3244 |  |  | 0.15859 | 0.60974 | -123.0359 | 0.4008 | 6.9813 | -197.8512 | -203.3317 | -1.6464 | 7.2441 | 22.891 | 17.1613 | 0.0023738 | 0.0021077 | 0.00034006 | 23.1872 | 22.0046 | 22.1272 | 22.1749 | 21.9707 | 21.2464 | 20.071 | 22.1518 | 22.3217 | 22.3584 | 22.2938 | 21.8982 | 21.1313 | 22.2175 | 564.2285 | 434.1568 | 432.1209 | 279.5287 | 210.3396 | 503.8148 | 298.6361 | 22.2917 | 22.0646 | 21.8457 | 22.0514 | 22.3173 | 27.3454 | 22.7251 | 64.8299 | 79.441 | 567.2894 | 535.0057 | 547.7883 | 549.0033 | 37.0452 | 26.0713 | 740.7654 | 21.915 | 22.1648 | 276.0024 | 21.5243 | 21.972 | 24.0168 | 77.2677 | 89.3924 | 22.2715 | 31.2072 | 90.7205 | 712.3462 | 616.9585 | 772.2901 | 775.3707 | 705.932 |  | 703.9517 | 767.7355 | 805.5458 | 598.8165 | 612.4888 | 782.2011 |  | 361.7076 |  |  | 399.7856 | 565.1952 | 653.8771 | [5 empty] | 21.8476 | 557.2512 | 21.7342 | 22.0528 | 385.6409 | 21.2956 | 21.8576 | 451.5104 | 599.9719 | 618.0038 |  | 897.2359 | 862.5229 | 484.1865 | 630.2853 | 729.3846 | 564.0488 | 634.9101 | 854.911 | 898.0422 | 570.2268 | 710.239 | 741.9398 | 936.255 | 891.6894 | 480.3478 | 582.6435 | 630.0802 | 519.5588 | 625.3517 | 755.7236 | 859.9328 | 944.0528 | 552.9314 | 615.6804 | 576.0079 | 699.9179 | 54.3265 | -0.0012801 | 19.1456 | 3.1841 | -28.2846 | 3.0951 | 6975.37 | -0.15 | 0.83418 | 1.5545 | -22.0815 | 1.2603 | 6.3004 | -33.5402 | -34.0016 | 51.6273 | 77.8181 | 35.2625 | 13.9501 | -8.771 | 47.6583 | 28.7964
42838.4299 | 829 | 22.8405 | 22.8337 | 22.8195 | 22.7316 | 22.3326 | 21.6649 | 22.668 | 21.7171 | 22.3115 | 22.3199 | 22.2892 | 21.9326 | 21.1461 | 22.1201 | 21.5509 | 21.7648 | 22.0647 | 21.0779 | 23.144 | 27.8211 | 27.7238 | 80.2027 | 83.5742 | 22.4746 | 30.4871 | 87.0998 | 630.7199 | 635.4182 | 630.3126 | 22.3293 | 30.5171 | 91.6688 | 22.4419 | 32.214 | 89.5032 | 676.773 | 806.025 |  | 323.2478 | 848.9006 | 858.2528 | 621.2109 |  | 308.2266 | 544.4509 | 543.0769 | 845.0064 | 880.9942 | 899.6896 | 888.2437 | 30.4284 | 157.8933 | 44.6378 | 340.6483 | 39.7326 | 45.444 | 51.7984 | 48.3359 | 30.3662 |  |  | 0.13034 | 1.6559 | -119.519 | -0.28983 | 6.7835 | -197.8368 | -203.3514 | -2.4015 | 7.5537 | 23.5877 | 17.4365 | 0.0025167 | 0.0021422 | 0.00038441 | 23.1917 | 21.9911 | 22.1139 | 22.165 | 21.9672 | 21.2361 | 20.0612 | 22.1401 | 22.3157 | 22.3512 | 22.2902 | 21.891 | 21.1227 | 22.2102 | 551.8108 | 416.4358 | 397.244 | 273.8605 | 203.8432 | 504.7005 | 299.0176 | 22.2891 | 22.0675 | 21.8415 | 22.0429 | 22.3456 | 27.4244 | 22.7408 | 65.0036 | 79.5247 | 567.3231 | 534.2173 | 546.6708 | 545.4383 | 38.8661 | 28.5941 | 743.1461 | 21.9205 | 22.1672 | 276.4582 | 21.5294 | 21.9812 | 24.0578 | 77.475 | 89.4013 | 22.2794 | 31.3544 | 90.7407 | 712.8531 | 617.644 | 773.8157 | 776.7733 | 708.1598 |  | 704.0176 | 768.2067 | 805.7387 | 602.2743 | 612.5131 | 782.4888 |  | 362.465 |  |  | 400.7216 | 565.4765 | 654.5265 | [5 empty] | 21.8438 | 559.0661 | 21.7402 | 22.0584 | 385.9184 | 21.2998 | 21.8635 | 451.6507 | 600.4814 | 617.8423 |  | 890.4846 | 863.3781 | 484.9462 | 630.4016 | 729.0812 | 564.1513 | 635.5413 | 856.4479 | 897.8183 | 570.6188 | 712.3137 | 741.6615 | 936.104 | 891.025 | 480.0228 | 582.6722 | 629.9517 | 520.9738 | 625.8642 | 757.4145 | 858.0248 | 943.4961 | 553.2428 | 615.8316 | 576.7173 | 702.0477 | 52.8076 | -0.00045154 | 19.155 | 3.1583 | -28.2807 | 3.095 | 7054.62 | -0.05 | 0.75624 | 2.5642 | -21.7849 | -1.0728 | 6.216 | -33.5691 | -34.0338 | 51.5812 | 77.8653 | 35.1709 | 15.5227 | -4.8372 | 47.7109 | 28.9009
42838.4299 | 830 | 22.8526 | 22.8267 | 22.8183 | 22.7313 | 22.3343 | 21.6559 | 22.6705 | 21.7205 | 22.3202 | 22.3253 | 22.2871 | 21.9338 | 21.1503 | 22.1165 | 21.5434 | 21.7549 | 22.0611 | 21.0727 | 23.1923 | 27.9083 | 27.8638 | 80.3336 | 83.6384 | 22.4692 | 30.5811 | 87.1533 | 632.424 | 634.576 | 631.8878 | 22.3309 | 30.6316 | 91.6658 | 22.4403 | 32.3396 | 89.5037 | 676.648 | 805.1539 |  | 323.9155 | 859.0684 | 861.3601 | 620.3183 |  | 309.3582 | 545.5129 | 544.969 | 848.2518 | 880.1538 | 899.5042 | 886.8873 | 31.161 | 158.6995 | 43.7496 | 342.0496 | 40.1295 | 45.6689 | 51.9079 | 48.4924 | 30.4303 |  |  | 0.17831 | 0.44612 | -120.5993 | -0.66636 | 5.9424 | -197.7757 | -203.2213 | -1.8837 | 7.4978 | 23.1904 | 17.9859 | 0.0023295 | 0.0019714 | 0.00034663 | 23.2072 | 21.9949 | 22.1162 | 22.1706 | 21.9717 | 21.2348 | 20.0611 | 22.1467 | 22.3205 | 22.3493 | 22.2924 | 21.8963 | 21.125 | 22.2075 | 542.6349 | 431.9278 | 401.3444 | 271.0283 | 199.7779 | 506.0454 | 300.0393 | 22.2877 | 22.0718 | 21.8508 | 22.0471 | 22.3596 | 27.5085 | 22.7568 | 65.2037 | 79.6116 | 567.3396 | 533.7694 | 546.2039 | 545.0136 | 49.252 | 30.0406 | 742.4005 | 21.9201 | 22.1705 | 277.1686 | 21.5255 | 21.9737 | 24.1007 | 77.6768 | 89.4158 | 22.2983 | 31.4952 | 90.7569 | 710.3044 | 618.4001 | 775.4076 | 778.2151 | 706.5599 |  | 703.8943 | 766.0741 | 805.7278 | 603.9434 | 612.4721 | 782.2945 |  | 363.5025 |  |  | 402.9253 | 566.3322 | 653.6216 | [5 empty] | 21.8437 | 560.4754 | 21.7375 | 22.0559 | 387.1666 | 21.2915 | 21.8628 | 451.8146 | 600.7767 | 618.1693 |  | 891.8063 | 865.0031 | 485.6544 | 630.4466 | 727.7247 | 564.3217 | 636.6986 | 862.6045 | 896.3285 | 571.235 | 713.1151 | 740.6508 | 937.7987 | 890.0676 | 479.671 | 582.9371 | 630.7646 | 521.8573 | 626.4474 | 757.8612 | 856.5573 | 944.0199 | 553.4443 | 616.6012 | 577.4333 | 702.9238 | 54.7437 | -0.0013293 | 19.1622 | 3.1304 | -28.3331 | 3.095 | 7113.77 | -0.01 | 0.8853 | 1.3318 | -21.8974 | -1.6277 | 5.8175 | -33.5613 | -34.0202 | 51.5961 | 77.9211 | 35.1169 | 16.8356 | -5.1358 | 47.708 | 28.9154
42838.4299 | 831 | 22.8456 | 22.8266 | 22.8185 | 22.7296 | 22.3284 | 21.6597 | 22.6682 | 21.7141 | 22.3203 | 22.3264 | 22.2914 | 21.9249 | 21.1407 | 22.1167 | 21.5504 | 21.7706 | 22.0637 | 21.077 | 23.2551 | 28.0062 | 28.0103 | 80.4695 | 83.7021 | 22.4819 | 30.6835 | 87.2198 | 632.3805 | 633.8988 | 631.8815 | 22.328 | 30.7582 | 91.6801 | 22.4469 | 32.4755 | 89.4907 | 676.7265 | 797.915 |  | 324.6682 | 855.9487 | 862.7924 | 620.787 |  | 310.425 | 547.0493 | 544.4852 | 847.8059 | 878.5699 | 898.2935 | 888.7969 | 31.6322 | 159.3234 | 43.1738 | 343.3579 | 40.5193 | 45.9006 | 52.0173 | 48.6708 | 30.4733 |  |  | 0.040314 | 0.42838 | -116.6842 | -0.14329 | 7.12 | -197.8098 | -203.1793 | -2.0098 | 7.1178 | 22.1523 | 17.5816 | 0.0023278 | 0.0020338 | 0.00036799 | 23.2269 | 21.9954 | 22.1245 | 22.1712 | 21.9746 | 21.2418 | 20.0702 | 22.1488 | 22.3187 | 22.3525 | 22.2955 | 21.9007 | 21.1263 | 22.2106 | 553.1055 | 419.9615 | 399.9069 | 276.8926 | 211.7659 | 507.913 | 301.1107 | 22.2915 | 22.0741 | 21.861 | 22.0573 | 22.3802 | 27.5849 | 22.7722 | 65.4501 | 79.7001 | 567.6217 | 534.716 | 547.5401 | 550.6009 | 44.4975 | 34.3952 | 740.9694 | 21.9176 | 22.1707 | 278.3955 | 21.5291 | 21.9768 | 24.1488 | 77.8746 | 89.4249 | 22.3018 | 31.6332 | 90.7828 | 710.0947 | 618.2095 | 775.925 | 778.5849 | 704.1652 |  | 703.6634 | 763.1125 | 805.6654 | 606.8401 | 612.5027 | 780.1304 |  | 365.0109 |  |  | 404.5735 | 566.8166 | 652.8546 | [5 empty] | 21.8448 | 561.0814 | 21.7423 | 22.0576 | 387.9237 | 21.2934 | 21.8611 | 452.1827 | 601.1203 | 618.4777 |  | 890.1585 | 865.858 | 486.3681 | 630.8231 | 726.5368 | 565.1423 | 638.0423 | 867.5508 | 893.603 | 572.2211 | 711.8887 | 740.0281 | 938.6914 | 891.2054 | 479.5888 | 583.1571 | 631.1305 | 522.9634 | 627.0499 | 758.6153 | 857.1757 | 947.6837 | 553.6904 | 617.2643 | 578.2486 | 703.354 | 53.5587 | 0.00018741 | 19.1675 | 3.1087 | -28.3423 | 3.095 | 7178.6 | 0.04 | 0.42095 | 1.3063 | -21.5592 | -0.75551 | 6.3645 | -33.5468 | -33.9991 | 51.6074 | 77.9839 | 35.0421 | 16.0808 | -4.8111 | 47.7124 | 28.806
42838.4299 | 832 | 22.8452 | 22.8181 | 22.8163 | 22.7248 | 22.3243 | 21.6545 | 22.6645 | 21.7167 | 22.3142 | 22.3211 | 22.282 | 21.9244 | 21.1332 | 22.11 | 21.5639 | 21.7715 | 22.0745 | 21.0947 | 23.3156 | 28.1089 | 28.1575 | 80.6138 | 83.769 | 22.5119 | 30.7994 | 87.2768 | 634.3582 | 632.4233 | 634.0371 | 22.3409 | 30.8851 | 91.6848 | 22.456 | 32.6128 | 89.5013 | 676.5956 | 800.5144 |  | 325.3154 | 861.5873 | 866.9674 | 621.9 |  | 311.6199 | 549.6649 | 552.7091 | 850.7214 | 878.5903 | 901.0274 | 892.4474 | 32.1357 | 159.9293 | 43.1044 | 344.6302 | 40.9588 | 46.1398 | 52.1236 | 48.8199 | 30.5307 |  |  | 0.36887 | 0.46977 | -108.9329 | -0.052614 | 7.2356 | -197.8486 | -203.0748 | -1.8101 | 7.2947 | 23.3823 | 17.9934 | 0.0024593 | 0.0019993 | 0.00036141 | 23.2419 | 21.9959 | 22.1216 | 22.1666 | 21.9735 | 21.2487 | 20.0704 | 22.1474 | 22.3206 | 22.3615 | 22.2941 | 21.9041 | 21.1233 | 22.2194 | 555.9976 | 439.9327 | 414.8794 | 289.7254 | 226.164 | 509.4358 | 302.5067 | 22.2994 | 22.076 | 21.8618 | 22.053 | 22.3971 | 27.6569 | 22.7905 | 65.7305 | 79.7793 | 568.087 | 536.2268 | 549.108 | 555.0057 | 40.6072 | 33.0773 | 739.6608 | 21.9184 | 22.1617 | 279.2159 | 21.5226 | 21.9777 | 24.1935 | 78.0733 | 89.4428 | 22.3101 | 31.7735 | 90.7951 | 710.0303 | 617.8915 | 775.1863 | 777.8915 | 704.4623 |  | 703.5982 | 759.6078 | 805.3176 | 607.1006 | 612.4681 | 777.5135 |  | 366.4403 |  |  | 404.1396 | 567.6194 | 652.3871 | [5 empty] | 21.8359 | 561.1042 | 21.7374 | 22.0543 | 389.3065 | 21.2907 | 21.8593 | 452.807 | 601.7128 | 618.3709 |  | 884.4256 | 865.329 | 487.3145 | 631.6016 | 726.9649 | 566.2251 | 637.8759 | 870.9232 | 892.8113 | 573.2087 | 711.2082 | 739.8346 | 937.6032 | 892.8557 | 479.9478 | 583.451 | 631.2621 | 523.6858 | 627.6149 | 758.6177 | 855.3462 | 950.9778 | 553.7296 | 616.6872 | 578.7877 | 703.2349 | 56.0914 | 0.0011213 | 19.174 | 3.088 | -28.3323 | 3.0951 | 7210.14 | -0.06 | 1.2748 | 1.3701 | -20.864 | -0.45853 | 6.4235 | -33.5893 | -34.03 | 51.5836 | 77.9726 | 35.0285 | 16.0937 | -6.2594 | 47.6524 | 28.7593
42838.4299 | 833 | 22.8441 | 22.819 | 22.818 | 22.7267 | 22.3282 | 21.659 | 22.6698 | 21.7125 | 22.3158 | 22.318 | 22.2895 | 21.9322 | 21.145 | 22.1156 | 21.5503 | 21.7653 | 22.0744 | 21.087 | 23.3649 | 28.2001 | 28.2889 | 80.723 | 83.8122 | 22.4996 | 30.8861 | 87.3308 | 635.1557 | 630.5127 | 634.6004 | 22.3445 | 31.0062 | 91.6754 | 22.4608 | 32.737 | 89.4953 | 676.5112 | 795.7224 |  | 325.9213 | 866.5607 | 869.178 | 624.1555 |  | 313.226 | 552.3563 | 553.5741 | 851.8231 | 879.0999 | 901.299 | 895.002 | 32.7617 | 160.6677 | 43.6829 | 345.8526 | 41.3364 | 46.3905 | 52.2236 | 48.9928 | 30.5752 |  |  | 0.092226 | 0.42575 | -110.1019 | -0.3654 | 5.8715 | -197.8302 | -203.1195 | -1.9224 | 7.7055 | 24.0956 | 18.1038 | 0.0023771 | 0.0019204 | 0.00036306 | 23.2443 | 21.9883 | 22.1167 | 22.167 | 21.9662 | 21.243 | 20.0596 | 22.1482 | 22.3134 | 22.3487 | 22.2873 | 21.8934 | 21.1184 | 22.2131 | 543.2427 | 436.4542 | 420.7445 | 304.1825 | 245.1594 | 510.4117 | 303.9305 | 22.2877 | 22.081 | 21.8619 | 22.0565 | 22.4138 | 27.7438 | 22.8039 | 66.1059 | 79.8792 | 568.6211 | 537.9932 | 551.1511 | 557.3355 | 40.0468 | 28.9852 | 738.8847 | 21.9132 | 22.1562 | 280.0673 | 21.5247 | 21.9743 | 24.238 | 78.2778 | 89.4373 | 22.311 | 31.9052 | 90.8035 | 712.2405 | 617.3663 | 774.5742 | 776.9131 | 703.7572 |  | 703.5195 | 762.0492 | 805.3508 | 608.3923 | 612.4783 | 777.84 |  | 367.9584 |  |  | 404.1785 | 568.9558 | 652.2444 | [5 empty] | 21.8418 | 561.8915 | 21.7233 | 22.0497 | 389.8276 | 21.2899 | 21.8533 | 453.1809 | 601.9336 | 618.2047 |  | 889.2055 | 864.6694 | 488.2141 | 632.4634 | 727.5074 | 566.3719 | 636.9656 | 871.3631 | 895.4988 | 573.7963 | 708.1518 | 738.967 | 935.8957 | 895.1014 | 481.007 | 583.9314 | 632.1504 | 524.5293 | 627.9765 | 757.9628 | 855.1131 | 953.871 | 554.3117 | 616.8052 | 579.2927 | 702.2665 | 55.9031 | 0.00017338 | 19.1842 | 3.0738 | -28.3034 | 3.0951 | 7222.69 | -0.07 | 0.63764 | 1.3065 | -21.0099 | -1.2104 | 5.787 | -33.5916 | -34.0377 | 51.5844 | 77.9151 | 34.9945 | 17.7256 | -6.6911 | 47.571 | 28.7816
42838.4299 | 834 | 22.8502 | 22.8259 | 22.8159 | 22.7325 | 22.3438 | 21.6641 | 22.6699 | 21.717 | 22.3187 | 22.3255 | 22.2969 | 21.9343 | 21.145 | 22.1217 | 21.5467 | 21.7792 | 22.0802 | 21.09 | 23.4203 | 28.3021 | 28.4378 | 80.8557 | 83.8731 | 22.5183 | 31.0108 | 87.3893 | 633.4681 | 628.8031 | 632.4252 | 22.3442 | 31.1168 | 91.6846 | 22.4643 | 32.8682 | 89.4923 | 676.6339 | 792.2488 |  | 313.7773 | 857.0618 | 862.1214 | 625.5248 |  | 313.8909 | 554.6083 | 552.8149 | 854.8784 | 879.1323 | 903.1421 | 896.5691 | 33.174 | 161.3838 | 44.2638 | 346.9625 | 41.5622 | 46.6144 | 52.3207 | 49.1895 | 30.6317 |  |  | -0.29481 | 0.68465 | -112.4484 | 0.30223 | 6.1514 | -197.7921 | -203.3862 | -2.4067 | 7.4665 | 23.2988 | 18.1347 | 0.0023295 | 0.0020387 | 0.00039591 | 23.2574 | 21.9904 | 22.1144 | 22.1618 | 21.9649 | 21.2408 | 20.0567 | 22.1439 | 22.3131 | 22.3378 | 22.2951 | 21.8936 | 21.1201 | 22.2157 | 532.4589 | 410.8125 | 401.2384 | 302.176 | 239.7546 | 511.0525 | 304.6993 | 22.2858 | 22.0692 | 21.859 | 22.0507 | 22.4284 | 27.818 | 22.8175 | 66.3961 | 79.9581 | 568.9997 | 539.1981 | 552.0105 | 557.669 | 35.236 | 25.422 | 742.5234 | 21.9055 | 22.1486 | 281.097 | 21.5067 | 21.9627 | 24.2771 | 78.4725 | 89.4389 | 22.2993 | 32.0421 | 90.8114 | 714.1508 | 617.919 | 776.7925 | 778.7832 | 709.4024 |  | 703.6978 | 769.0003 | 805.8536 | 607.849 | 612.4243 | 778.515 |  | 369.6839 |  |  | 406.3981 | 570.4395 | 654.6233 | [5 empty] | 21.8559 | 562.1478 | 21.7365 | 22.0595 | 389.3789 | 21.2927 | 21.8716 | 453.6741 | 602.1497 | 618.0968 |  | 896.5064 | 864.7495 | 489.0233 | 632.9531 | 726.9652 | 566.6091 | 636.8673 | 869.1304 | 898.4222 | 574.6478 | 706.1689 | 741.7591 | 934.6472 | 894.9174 | 482.0305 | 584.1802 | 632.357 | 525.6546 | 628.4128 | 756.6007 | 859.4731 | 951.6045 | 554.5936 | 616.125 | 580.1344 | 702.9129 | 52.7911 | 0.00043319 | 19.1906 | 3.0546 | -28.3374 | 3.0951 | 7199.14 | -0.13 | -1.1387 | 1.659 | -21.2616 | 1.1023 | 5.928 | -33.6147 | -34.0867 | 51.4702 | 77.8791 | 34.9996 | 19.065 | -4.4048 | 47.5602 | 28.8341
42838.4299 | 835 | 22.8447 | 22.8204 | 22.8142 | 22.7268 | 22.3409 | 21.6562 | 22.6759 | 21.7143 | 22.317 | 22.3227 | 22.2903 | 21.9288 | 21.1459 | 22.1197 | 21.5481 | 21.7611 | 22.0792 | 21.0784 | 23.4734 | 28.3902 | 28.5832 | 80.966 | 83.9265 | 22.5143 | 31.1028 | 87.4297 | 631.4666 | 625.8627 | 630.9541 | 22.3486 | 31.2354 | 91.6977 | 22.4666 | 32.9983 | 89.4813 | 676.6954 | 790.5009 |  | 297.9078 | 856.5453 | 862.3586 | 625.724 |  | 314.7723 | 557.6847 | 550.5218 | 856.5645 | 880.6292 | 905.3659 | 894.5691 | 33.4763 | 162.1421 | 45.4612 | 348.3322 | 41.8844 | 46.8446 | 52.4091 | 49.3604 | 30.6806 |  |  | -0.58 | 0.90018 | -111.1592 | 0.053182 | 6.8217 | -197.7803 | -203.402 | -2.1327 | 6.7889 | 22.3084 | 18.1609 | 0.0023114 | 0.001904 | 0.00037949 | 23.2726 | 21.9925 | 22.1194 | 22.1687 | 21.9634 | 21.2421 | 20.0628 | 22.1421 | 22.3133 | 22.3462 | 22.2913 | 21.8989 | 21.1221 | 22.2106 | 527.3744 | 384.315 | 369.5845 | 291.8311 | 233.3414 | 511.2062 | 304.8442 | 22.2872 | 22.0699 | 21.8657 | 22.048 | 22.4504 | 27.8911 | 22.84 | 66.6189 | 80.0446 | 569.3482 | 539.089 | 551.9671 | 556.6951 | 26.1215 | 22.5475 | 743.9109 | 21.9173 | 22.1582 | 281.6643 | 21.5116 | 21.9727 | 24.3354 | 78.6549 | 89.4516 | 22.3171 | 32.1925 | 90.8349 | 714.7473 | 618.6085 | 776.3731 | 778.0979 | 710.778 |  | 703.7777 | 763.9478 | 805.5276 | 606.7348 | 612.3347 | 775.5636 |  | 371.1269 |  |  | 407.4194 | 571.0365 | 656.9588 | [5 empty] | 21.8345 | 562.04 | 21.7356 | 22.0462 | 389.0655 | 21.2897 | 21.8472 | 454.2631 | 601.7636 | 617.8699 |  | 897.0116 | 866.6051 | 489.9873 | 633.6299 | 728.8226 | 566.6216 | 635.9655 | 864.4047 | 899.2585 | 575.677 | 707.3642 | 742.3714 | 933.3595 | 892.1462 | 482.5444 | 584.082 | 631.3716 | 527.0901 | 629.1659 | 757.2059 | 859.7819 | 949.9683 | 554.1521 | 615.6761 | 581.3183 | 706.792 | 54.7812 | 0.00013829 | 19.1947 | 3.0502 | -28.3444 | 3.0951 | 7170.5 | -0.07 | -1.5958 | 1.9059 | -21.1786 | 0.46324 | 6.2486 | -33.6454 | -34.1203 | 51.4511 | 77.9176 | 35.0139 | 19.6639 | -0.86521 | 47.5683 | 28.9181
42838.43 | 836 | 22.8504 | 22.8295 | 22.8173 | 22.7306 | 22.3379 | 21.6599 | 22.6762 | 21.7153 | 22.3192 | 22.3157 | 22.2922 | 21.9279 | 21.1445 | 22.1213 | 21.5426 | 21.7624 | 22.0735 | 21.0815 | 23.5311 | 28.4899 | 28.7272 | 81.0893 | 83.9728 | 22.5103 | 31.2106 | 87.4765 | 631.8152 | 623.3444 | 631.4789 | 22.3464 | 31.3556 | 91.71 | 22.4681 | 33.1252 | 89.4698 | 676.6934 | 789.226 |  | 295.3483 | 862.2015 | 867.337 | 626.9175 |  | 316.1438 | 559.8888 | 550.2439 | 855.1145 | 881.2433 | 908.0212 | 895.273 | 33.6335 | 162.763 | 46.2652 | 349.4192 | 42.2374 | 47.0301 | 52.4781 | 49.5291 | 30.7347 |  |  | 0.27162 | 0.30746 | -117.0732 | -0.1157 | 5.6139 | -197.8282 | -203.1996 | -1.8883 | 7.1882 | 22.8903 | 18.2068 | 0.0022999 | 0.0019303 | 0.00038606 | 23.2977 | 22.0002 | 22.1286 | 22.1768 | 21.9662 | 21.2459 | 20.0667 | 22.1482 | 22.317 | 22.3559 | 22.3042 | 21.9048 | 21.1355 | 22.2236 | 504.4301 | 372.9673 | 361.5355 | 279.6185 | 226.5066 | 510.5219 | 304.8828 | 22.2787 | 22.0664 | 21.8602 | 22.0484 | 22.4748 | 27.957 | 22.8537 | 66.7962 | 80.1233 | 569.6033 | 538.993 | 551.7344 | 555.2565 | 36.2977 | 21.1444 | 741.7398 | 21.9219 | 22.1606 | 281.7199 | 21.5164 | 21.9729 | 24.3866 | 78.8359 | 89.4607 | 22.311 | 32.3394 | 90.8466 | 714.1659 | 619.1479 | 776.6476 | 778.1624 | 706.3309 |  | 703.7149 | 760.6548 | 805.1002 | 605.282 | 612.2255 | 772.9631 |  | 372.2298 |  |  | 408.9381 | 570.5086 | 655.2032 | [5 empty] | 21.8435 | 561.9962 | 21.7404 | 22.0518 | 389.1789 | 21.2872 | 21.8603 | 455.1411 | 601.0345 | 618.068 |  | 894.0507 | 867.4576 | 490.7966 | 634.0332 | 729.6677 | 567.0694 | 636.3784 | 873.6185 | 898.6408 | 576.2838 | 708.1726 | 741.4133 | 931.9169 | 891.0801 | 482.3295 | 583.7191 | 630.466 | 528.3116 | 630.1182 | 756.1131 | 861.8474 | 951.0815 | 554.2013 | 614.053 | 582.3233 | 707.8439 | 52.4784 | 0.00035597 | 19.1992 | 3.0359 | -28.3424 | 3.0951 | 7136.03 | -0.08 | 1.0924 | 1.1153 | -21.7635 | -0.68417 | 5.6749 | -33.6874 | -34.1417 | 51.5596 | 77.8756 | 35.0341 | 22.0624 | 0.035105 | 47.5347 | 28.9998
42838.43 | 837 | 22.842 | 22.8267 | 22.8214 | 22.7305 | 22.3378 | 21.6619 | 22.6705 | 21.715 | 22.3129 | 22.3204 | 22.28 | 21.9301 | 21.147 | 22.1108 | 21.5425 | 21.7729 | 22.0712 | 21.0839 | 23.5837 | 28.5894 | 28.8812 | 81.2255 | 84.0228 | 22.523 | 31.3158 | 87.5258 | 632.1351 | 621.4678 | 631.4631 | 22.3468 | 31.4798 | 91.7256 | 22.4724 | 33.2602 | 89.4709 | 676.893 | 790.1578 |  | 294.4565 | 865.5395 | 870.2265 | 629.567 |  | 316.641 | 560.847 | 550.4169 | 855.0167 | 881.9482 | 907.7373 | 897.5033 | 33.886 | 163.4169 | 46.456 | 350.6246 | 42.6904 | 47.2223 | 52.5445 | 49.6654 | 30.7861 |  |  | 0.35376 | 0.086015 | -111.4601 | -0.77873 | 6.0541 | -197.8598 | -203.3803 | -2.3752 | 7.6311 | 23.8101 | 18.464 | 0.0023213 | 0.0019812 | 0.00036141 | 23.3065 | 21.9994 | 22.1221 | 22.1646 | 21.9756 | 21.2465 | 20.0716 | 22.1447 | 22.3136 | 22.3567 | 22.302 | 21.9041 | 21.1277 | 22.2133 | 501.9935 | 373.9926 | 347.6364 | 268.1152 | 214.5542 | 510.7793 | 304.7195 | 22.2835 | 22.0709 | 21.8677 | 22.0473 | 22.4926 | 28.0467 | 22.8596 | 66.993 | 80.208 | 569.9519 | 539.753 | 552.8596 | 556.7595 | 48.3575 | 32.1906 | 740.3306 | 21.9162 | 22.1556 | 281.9375 | 21.5164 | 21.9666 | 24.4395 | 78.995 | 89.4576 | 22.3119 | 32.4806 | 90.8516 | 712.6867 | 618.8262 | 776.749 | 777.6542 | 703.2952 |  | 703.5375 | 761.3183 | 805.0814 | 605.2336 | 612.1286 | 772.6506 |  | 373.5616 |  |  | 409.522 | 570.7993 | 654.0751 | [5 empty] | 21.8456 | 561.7279 | 21.7442 | 22.05 | 389.3604 | 21.2983 | 21.8675 | 456.1327 | 600.6157 | 618.3439 |  | 901.5606 | 867.1324 | 491.5151 | 634.0014 | 728.2153 | 567.2512 | 637.4965 | 876.1989 | 901.4326 | 576.5508 | 706.5868 | 740.6026 | 936.689 | 890.1109 | 481.8613 | 583.6226 | 631.1251 | 529.3277 | 630.1051 | 755.5959 | 864.0401 | 949.2984 | 554.2566 | 612.5794 | 582.8129 | 706.9309 | 53.8989 | 0.0017533 | 19.2022 | 3.0266 | -28.4522 | 3.095 | 7119.31 | -0.03 | 1.2467 | 0.59025 | -21.2476 | -1.776 | 5.8925 | -33.686 | -34.1527 | 51.6015 | 77.8513 | 35.0175 | 22.3899 | 1.5542 | 47.5055 | 29.0151
42838.43 | 838 | 22.8474 | 22.8226 | 22.8168 | 22.7319 | 22.3434 | 21.6528 | 22.6681 | 21.7151 | 22.3218 | 22.3162 | 22.2877 | 21.9243 | 21.1407 | 22.1168 | 21.5477 | 21.773 | 22.0775 | 21.0901 | 23.6504 | 28.6969 | 29.0356 | 81.3525 | 84.0799 | 22.5327 | 31.4183 | 87.5758 | 632.7408 | 620.44 | 631.6159 | 22.3454 | 31.6103 | 91.7433 | 22.4821 | 33.3962 | 89.4622 | 677.0805 | 793.2706 |  | 294.3885 | 867.4791 | 869.302 | 628.7668 |  | 317.5263 | 561.9497 | 551.2155 | 856.3034 | 882.0297 | 907.6535 | 898.2944 | 34.1559 | 164.1582 | 46.0028 | 351.8941 | 43.2156 | 47.4182 | 52.5944 | 49.8184 | 30.8435 |  |  | 0.26045 | 0.48029 | -112.5667 | -0.029614 | 6.6002 | -197.8026 | -203.0774 | -2.3068 | 8.0159 | 24.0293 | 18.4548 | 0.0023163 | 0.0018547 | 0.00035156 | 23.325 | 22.0052 | 22.1211 | 22.1665 | 21.9744 | 21.2537 | 20.071 | 22.1425 | 22.318 | 22.3577 | 22.2969 | 21.8969 | 21.1316 | 22.2155 | 531.2061 | 404.0636 | 381.07 | 274.9073 | 212.7763 | 512.3052 | 305.5351 | 22.2868 | 22.0769 | 21.867 | 22.0437 | 22.5141 | 28.1209 | 22.8788 | 67.2601 | 80.2898 | 570.378 | 540.2411 | 553.5849 | 559.6556 | 48.8089 | 38.533 | 739.8562 | 21.9206 | 22.1773 | 282.2901 | 21.5154 | 21.9786 | 24.491 | 79.1783 | 89.4738 | 22.3279 | 32.6236 | 90.877 | 715.8164 | 617.9631 | 775.7988 | 776.4427 | 705.9693 |  | 703.4592 | 758.6977 | 804.782 | 603.8778 | 612.0059 | 771.7929 |  | 374.9721 |  |  | 410.1138 | 571.4378 | 653.5893 | [5 empty] | 21.8481 | 561.5029 | 21.7434 | 22.0601 | 389.2425 | 21.2998 | 21.8622 | 456.4975 | 600.9195 | 618.1391 |  | 898.9486 | 867.5927 | 492.2685 | 634.1146 | 725.6421 | 567.2148 | 637.3608 | 872.4707 | 899.1058 | 576.9149 | 707.6389 | 740.2127 | 936.8393 | 888.3996 | 482.2198 | 583.4735 | 631.6669 | 530.2779 | 630.4202 | 756.7181 | 863.1792 | 950.1057 | 554.2864 | 611.8433 | 583.1134 | 707.9845 | 53.023 | -0.0020034 | 19.209 | 3.027 | -28.3291 | 3.0951 | 7155.09 | -0.05 | 1.0698 | 1.3957 | -21.3669 | -0.34656 | 6.1523 | -33.68 | -34.1261 | 51.5085 | 77.8307 | 35.0324 | 19.4808 | -2.0343 | 47.5694 | 29.0044
42838.43 | 839 | 22.8335 | 22.8215 | 22.814 | 22.7304 | 22.3304 | 21.6476 | 22.6609 | 21.7106 | 22.3116 | 22.3115 | 22.2791 | 21.9224 | 21.136 | 22.1097 | 21.5392 | 21.7643 | 22.0827 | 21.0913 | 23.7073 | 28.7964 | 29.192 | 81.4669 | 84.1347 | 22.541 | 31.5248 | 87.6062 | 633.1797 | 617.8829 | 631.6891 | 22.3623 | 31.7654 | 91.78 | 22.4885 | 33.5359 | 89.453 | 677.1426 | 795.8908 |  | 294.5208 | 865.5185 | 866.386 | 630.9093 |  | 318.1865 | 563.4787 | 552.3522 | 856.9809 | 880.3742 | 906.9314 | 897.6951 | 34.3629 | 164.8655 | 45.5298 | 353.0252 | 43.6783 | 47.591 | 52.6407 | 49.949 | 30.8829 |  |  | 0.23416 | 0.1997 | -112.3932 | -0.16958 | 5.9746 | -197.8026 | -203.1839 | -2.2444 | 7.7242 | 23.9179 | 18.3937 | 0.0022309 | 0.0018646 | 0.00035813 | 23.3294 | 21.9979 | 22.1197 | 22.1672 | 21.9623 | 21.2462 | 20.0637 | 22.1435 | 22.3154 | 22.3532 | 22.2947 | 21.8979 | 21.1284 | 22.2183 | 525.8332 | 401.3497 | 401.9589 | 288.3328 | 226.9138 | 513.6691 | 306.9285 | 22.2779 | 22.0658 | 21.8669 | 22.0479 | 22.5367 | 28.1997 | 22.8924 | 67.5046 | 80.3789 | 570.7352 | 540.2792 | 553.9467 | 559.9435 | 57.7446 | 30.8413 | 738.1572 | 21.923 | 22.1633 | 283.6069 | 21.512 | 21.9753 | 24.5373 | 79.3309 | 89.4785 | 22.327 | 32.7673 | 90.8929 | 716.916 | 617.2271 | 774.2592 | 774.9918 | 716.2985 |  | 703.7004 | 756.2844 | 804.2358 | 604.7713 | 611.8862 | 771.1687 |  | 376.2491 |  |  | 410.2002 | 573.2229 | 656.8701 | [5 empty] | 21.8396 | 561.0742 | 21.7354 | 22.0563 | 389.4049 | 21.2932 | 21.8609 | 456.8359 | 601.0349 | 617.9121 |  | 888.6679 | 868.1422 | 493.2972 | 635.0483 | 724.9678 | 567.4535 | 638.5251 | 871.4971 | 892.9307 | 577.2635 | 706.9573 | 741.0938 | 936.7997 | 886.6012 | 482.7504 | 583.5215 | 631.8167 | 531.0343 | 630.3057 | 755.767 | 864.7924 | 952.6092 | 554.6395 | 613.141 | 583.5119 | 707.7678 | 52.7366 | 0.00038403 | 19.2144 | 3.0239 | -28.3229 | 3.0951 | 7169.74 | -0.05 | 1.0144 | 0.90079 | -21.3699 | -0.83008 | 5.8517 | -33.6697 | -34.1246 | 51.2792 | 77.7275 | 34.9854 | 20.3796 | -4.139 | 47.5237 | 29.055
42838.43 | 840 | 22.8359 | 22.8284 | 22.8218 | 22.7329 | 22.3474 | 21.6535 | 22.6742 | 21.712 | 22.3132 | 22.3207 | 22.281 | 21.9303 | 21.1437 | 22.1202 | 21.5403 | 21.7719 | 22.0858 | 21.0922 | 23.7615 | 28.8915 | 29.3399 | 81.5771 | 84.1765 | 22.5433 | 31.6381 | 87.6429 | 632.5299 | 616.6663 | 631.1315 | 22.3557 | 31.8869 | 91.8062 | 22.4908 | 33.6606 | 89.4396 | 677.4469 | 794.5763 |  | 294.8671 | 871.1316 | 869.5308 | 629.5213 |  | 319.2009 | 565.3024 | 551.7001 | 858.3743 | 876.581 | 902.2109 | 895.0035 | 34.6368 | 165.6779 | 45.3129 | 354.3295 | 44.0884 | 47.7796 | 52.6788 | 50.1218 | 30.9333 |  |  | 0.4589 | -0.074321 | -113.9309 | -0.30232 | 5.3031 | -197.8749 | -203.3153 | -2.2753 | 7.4254 | 23.0445 | 18.5435 | 0.0022588 | 0.0019385 | 0.00039098 | 23.3398 | 21.9938 | 22.1143 | 22.1661 | 21.9603 | 21.2371 | 20.0613 | 22.1409 | 22.3067 | 22.3414 | 22.2887 | 21.8886 | 21.1237 | 22.2155 | 530.6343 | 411.2556 | 404.3336 | 293.5058 | 234.8833 | 515.7219 | 308.0276 | 22.2839 | 22.0684 | 21.8724 | 22.0528 | 22.559 | 28.2749 | 22.9119 | 67.782 | 80.4645 | 571.1912 | 541.68 | 555.3474 | 562.5611 | 53.8379 | 26.0028 | 736.3232 | 21.9253 | 22.166 | 284.3932 | 21.5295 | 21.975 | 24.5966 | 79.5032 | 89.4864 | 22.3259 | 32.9142 | 90.918 | 716.0424 | 616.25 | 772.6078 | 773.3563 | 714.3043 |  | 703.7467 | 754.088 | 803.6829 | 605.4564 | 611.7936 | 769.008 |  | 377.6323 |  |  | 410.8464 | 574.6902 | 656.0888 | [5 empty] | 21.8447 | 560.8208 | 21.7334 | 22.0497 | 390.072 | 21.2864 | 21.8554 | 457.2165 | 601.4339 | 618.0372 |  | 887.1382 | 868.3877 | 494.0544 | 635.5908 | 724.0196 | 567.9255 | 639.8771 | 869.2193 | 889.1416 | 577.6193 | 706.9756 | 740.6585 | 936.598 | 884.4265 | 483.6466 | 584.1166 | 632.02 | 531.8544 | 630.0372 | 755.5321 | 862.8188 | 951.7202 | 554.9343 | 615.1804 | 583.9662 | 707.9106 | 52.0899 | 0.0011284 | 19.2198 | 3.0223 | -28.2685 | 3.0951 | 7209.33 | -0.1 | 1.4196 | -0.55013 | -21.5391 | -1.1095 | 5.5019 | -33.6084 | -34.0673 | 51.3457 | 77.6165 | 34.9493 | 20.3019 | -4.2319 | 47.63 | 29.0571
42838.43 | 841 | 22.8394 | 22.8297 | 22.8158 | 22.7242 | 22.3457 | 21.6477 | 22.6709 | 21.7077 | 22.3185 | 22.3207 | 22.2849 | 21.9259 | 21.1428 | 22.1234 | 21.5428 | 21.7719 | 22.0875 | 21.091 | 23.8208 | 28.9876 | 29.4982 | 81.6881 | 84.2221 | 22.552 | 31.741 | 87.6852 | 632.7455 | 616.8702 | 631.4754 | 22.3597 | 32.0299 | 91.8251 | 22.501 | 33.7934 | 89.4341 | 677.4768 | 790.8791 |  | 295.3688 | 875.0156 | 872.4491 | 628.7181 |  | 320.1214 | 565.98 | 551.5525 | 859.9317 | 874.8785 | 900.552 | 892.8002 | 34.5956 | 166.3251 | 46.5057 | 355.2689 | 44.5085 | 47.9528 | 52.7025 | 50.2727 | 30.9804 |  |  | 0.03703 | -0.034893 | -109.3514 | -0.17615 | 5.8557 | -197.8131 | -203.1181 | -2.0696 | 7.7319 | 23.5684 | 18.8855 | 0.0021537 | 0.0017824 | 0.00039098 | 23.3646 | 22.0071 | 22.1283 | 22.1707 | 21.9729 | 21.2447 | 20.07 | 22.152 | 22.3218 | 22.3558 | 22.2977 | 21.8971 | 21.1287 | 22.2178 | 549.5574 | 403.7041 | 387.2212 | 280.9279 | 226.7078 | 517.5953 | 308.6404 | 22.2868 | 22.0715 | 21.8774 | 22.0521 | 22.5853 | 28.352 | 22.9205 | 68.1049 | 80.5539 | 571.7786 | 543.9753 | 557.2888 | 564.661 | 44.57 | 30.0824 | 734.8294 | 21.9165 | 22.1618 | 285.0646 | 21.5183 | 21.9682 | 24.6477 | 79.6433 | 89.477 | 22.3268 | 33.0657 | 90.9329 | 713.5857 | 615.0077 | 772.0615 | 773.9147 | 706.3865 |  | 703.3951 | 749.9315 | 802.8825 | 603.7509 | 611.6009 | 766.1428 |  | 379.2402 |  |  | 411.9105 | 574.069 | 654.2077 | [5 empty] | 21.8499 | 560.015 | 21.742 | 22.0542 | 389.864 | 21.2986 | 21.862 | 457.5801 | 601.8349 | 617.9597 |  | 888.185 | 868.2528 | 494.6238 | 636.1649 | 723.8629 | 568.4654 | 639.8021 | 863.6744 | 889.2182 | 577.8683 | 707.4126 | 741.0803 | 933.1255 | 882.4125 | 484.3067 | 584.5428 | 632.2514 | 532.7017 | 629.9626 | 755.0395 | 861.7639 | 948.5739 | 554.6587 | 615.3991 | 584.1231 | 708.674 | 52.1144 | 0.0054537 | 19.2234 | 3.019 | -28.3702 | 3.095 | 7251.16 | -0.1 | 0.40335 | -0.37709 | -21.1103 | -0.84727 | 5.7774 | -33.5794 | -34.0267 | 51.4816 | 77.4833 | 34.961 | 18.6168 | -2.2352 | 47.6589 | 29.0954
42838.43 | 842 | 22.8458 | 22.8324 | 22.8146 | 22.7274 | 22.3442 | 21.6623 | 22.671 | 21.7149 | 22.324 | 22.3205 | 22.2886 | 21.9268 | 21.1483 | 22.1165 | 21.5391 | 21.7573 | 22.0833 | 21.0879 | 23.8826 | 29.0856 | 29.6592 | 81.7945 | 84.2717 | 22.5579 | 31.8461 | 87.7203 | 633.2548 | 616.6724 | 632.6153 | 22.3632 | 32.1823 | 91.85 | 22.5104 | 33.9322 | 89.4334 | 677.5069 | 790.1751 |  | 296.0179 | 871.6311 | 866.9098 | 628.5203 |  | 321.4232 | 566.8554 | 552.515 | 861.6843 | 876.634 | 901.5269 | 893.369 | 34.6017 | 167.0252 | 47.71 | 356.3556 | 44.8302 | 48.114 | 52.7174 | 50.4306 | 31.021 |  |  | -0.21333 | 0.1031 | -109.7247 | -0.30429 | 6.915 | -197.8164 | -203.3534 | -2.2622 | 7.4537 | 23.3167 | 19.1137 | 0.00218 | 0.0018416 | 0.00038606 | 23.3748 | 21.9984 | 22.1218 | 22.1714 | 21.9701 | 21.2352 | 20.0615 | 22.1471 | 22.3098 | 22.3587 | 22.2931 | 21.9014 | 21.129 | 22.216 | 537.8319 | 392.8082 | 385.5089 | 275.0301 | 226.042 | 519.1403 | 309.3601 | 22.2829 | 22.0624 | 21.8717 | 22.0459 | 22.604 | 28.434 | 22.9449 | 68.4302 | 80.6459 | 572.4415 | 546.7929 | 560.1895 | 568.1836 | 45.0818 | 28.5491 | 732.8398 | 21.9159 | 22.1672 | 285.3978 | 21.5141 | 21.9665 | 24.7117 | 79.8026 | 89.4869 | 22.3312 | 33.2001 | 90.9519 | 712.7448 | 613.307 | 773.0772 | 775.9857 | 703.6937 |  | 703.0326 | 750.86 | 802.4656 | 602.44 | 611.3749 | 767.5712 |  | 380.5542 |  |  | 412.1097 | 573.0148 | 652.7491 | [5 empty] | 21.8419 | 558.9288 | 21.7419 | 22.053 | 390.3289 | 21.2994 | 21.8552 | 457.6345 | 601.9128 | 617.9423 |  | 891.8087 | 869.4153 | 495.2276 | 636.7226 | 723.4704 | 568.6131 | 639.3028 | 866.2248 | 893.3669 | 578.3831 | 707.5224 | 741.5655 | 933.0269 | 881.7186 | 484.2539 | 584.6399 | 632.6407 | 533.604 | 630.1722 | 754.2358 | 861.6887 | 947.6 | 554.4899 | 615.6749 | 584.3836 | 708.7666 | 51.5308 | 0.0012266 | 19.2305 | 3.0078 | -28.3059 | 3.095 | 7242.15 | -0.07 | -0.96873 | 0.64855 | -21.1573 | -1.1142 | 6.2809 | -33.5937 | -34.0606 | 51.4698 | 77.3282 | 34.9557 | 20.2651 | -1.9327 | 47.6711 | 29.1068
42838.43 | 843 | 22.8411 | 22.828 | 22.8128 | 22.7316 | 22.3413 | 21.6608 | 22.6685 | 21.7169 | 22.3207 | 22.3196 | 22.2886 | 21.9327 | 21.1427 | 22.1167 | 21.5404 | 21.7565 | 22.0789 | 21.0875 | 23.9356 | 29.1871 | 29.8228 | 81.8983 | 84.3252 | 22.5593 | 31.9513 | 87.7553 | 633.3174 | 617.3922 | 633.1027 | 22.3601 | 32.3339 | 91.8707 | 22.512 | 34.0579 | 89.4095 | 677.5428 | 797.8263 |  | 296.6664 | 872.9727 | 863.4392 | 629.7323 |  | 321.9849 | 568.5361 | 551.4306 | 857.7998 | 880.6187 | 904.9341 | 892.7405 | 34.4938 | 167.7454 | 48.8184 | 357.4562 | 45.3293 | 48.2596 | 52.7197 | 50.593 | 31.0563 |  |  | 0.063314 | -0.27868 | -108.7127 | -0.45345 | 8.2338 | -197.8709 | -203.2706 | -2.0703 | 8.0279 | 24.6443 | 18.8793 | 0.0022506 | 0.0018859 | 0.00039098 | 23.3938 | 21.9959 | 22.1105 | 22.1719 | 21.9604 | 21.2427 | 20.0575 | 22.1344 | 22.3101 | 22.3485 | 22.2932 | 21.8904 | 21.1201 | 22.2155 | 530.6041 | 397.4116 | 385.4005 | 272.8457 | 235.9048 | 520.3962 | 309.9484 | 22.2885 | 22.0637 | 21.8802 | 22.0493 | 22.6328 | 28.5151 | 22.9614 | 68.7736 | 80.7347 | 573.1575 | 549.7301 | 563.5608 | 571.0671 | 43.7034 | 30.5268 | 734.1089 | 21.9134 | 22.155 | 285.5565 | 21.5146 | 21.9743 | 24.7655 | 79.9533 | 89.4918 | 22.329 | 33.3468 | 90.9597 | 710.3222 | 612.2097 | 774.0061 | 777.1359 | 698.9246 |  | 702.6351 | 752.4832 | 802.2286 | 603.2002 | 611.2157 | 768.81 |  | 381.9347 |  |  | 413.3394 | 572.5458 | 651.2393 | [5 empty] | 21.847 | 558.304 | 21.7366 | 22.0543 | 391.0406 | 21.2956 | 21.8507 | 457.4551 | 601.7724 | 618.2101 |  | 889.1919 | 870.4974 | 495.9628 | 637.886 | 723.7225 | 568.7137 | 639.0003 | 861.6312 | 891.5662 | 579.13 | 709.7411 | 744.1064 | 935.6954 | 883.9644 | 483.7155 | 585.0733 | 633.0096 | 534.3529 | 630.573 | 754.4779 | 862.4731 | 949.5837 | 554.4061 | 615.9907 | 584.4437 | 708.2449 | 50.9925 | 0.00013829 | 19.2366 | 2.997 | -28.3105 | 3.095 | 7205.29 | 0.04 | 0.52789 | -1.0673 | -21.0806 | -1.3615 | 6.8636 | -33.647 | -34.103 | 51.5074 | 77.2096 | 34.9052 | 21.3497 | -1.8289 | 47.6454 | 29.1449
42838.43 | 844 | 22.839 | 22.8272 | 22.816 | 22.7298 | 22.3394 | 21.6562 | 22.666 | 21.7135 | 22.3196 | 22.319 | 22.2853 | 21.9344 | 21.1355 | 22.1112 | 21.5413 | 21.7601 | 22.0871 | 21.0973 | 24.0026 | 29.2878 | 29.988 | 82.0184 | 84.3726 | 22.5658 | 32.0601 | 87.7939 | 631.5766 | 619.298 | 631.3437 | 22.3646 | 32.4815 | 91.8949 | 22.5099 | 34.191 | 89.3946 | 677.6865 | 797.8813 |  | 297.3121 | 885.4259 | 872.7685 | 630.1101 |  | 322.4495 | 569.9696 | 549.9005 | 855.9153 | 879.3868 | 904.1867 | 894.1489 | 34.2827 | 168.4152 | 49.1421 | 358.5335 | 45.9726 | 48.4289 | 52.7313 | 50.7373 | 31.1072 |  |  | 0.46678 | -0.045405 | -111.3484 | -0.15907 | 6.6114 | -197.8243 | -203.1904 | -2.1123 | 7.7247 | 23.7239 | 19.1446 | 0.002152 | 0.0017101 | 0.00037127 | 23.4109 | 21.9964 | 22.1144 | 22.1658 | 21.9712 | 21.2416 | 20.064 | 22.143 | 22.3118 | 22.3473 | 22.2955 | 21.8913 | 21.1158 | 22.2166 | 509.3784 | 394.6957 | 375.9584 | 286.2926 | 237.2671 | 521.0068 | 310.4783 | 22.2845 | 22.06 | 21.8776 | 22.0503 | 22.6584 | 28.5927 | 22.9873 | 69.0923 | 80.8167 | 573.8829 | 550.7549 | 565.9106 | 572.6975 | 38.2533 | 22.7907 | 734.8198 | 21.9194 | 22.1564 | 285.9959 | 21.525 | 21.971 | 24.8274 | 80.105 | 89.5048 | 22.3396 | 33.5114 | 90.9724 | 708.3466 | 611.0742 | 774.5402 | 777.522 | 694.9747 |  | 702.2002 | 753.6848 | 802.0824 | 603.7116 | 611.0667 | 769.471 |  | 383.6086 |  |  | 414.9048 | 572.2203 | 649.8467 | [5 empty] | 21.8455 | 558.1277 | 21.7313 | 22.0531 | 392.2886 | 21.2924 | 21.856 | 457.5473 | 601.5987 | 618.8015 |  | 883.2209 | 870.7674 | 496.6381 | 638.9379 | 724.4333 | 569.0351 | 639.5032 | 860.6631 | 889.0176 | 579.6161 | 709.0235 | 746.326 | 937.1379 | 888.4757 | 483.1689 | 585.5479 | 632.6137 | 535.1498 | 631.0052 | 755.212 | 863.8055 | 950.2283 | 554.5166 | 616.074 | 584.8299 | 709.2456 | 52.5329 | 0.0018656 | 19.2408 | 2.9846 | -28.3398 | 3.095 | 7173.07 | -0.12 | 1.4319 | -0.43118 | -21.3527 | -0.80705 | 6.1484 | -33.6323 | -34.0854 | 51.5135 | 77.131 | 34.8635 | 23.8452 | -0.69705 | 47.6669 | 29.2196
42838.4301 | 845 | 22.825 | 22.8195 | 22.8116 | 22.7134 | 22.3253 | 21.6457 | 22.6577 | 21.7099 | 22.3057 | 22.3111 | 22.2749 | 21.9142 | 21.1312 | 22.1049 | 21.5386 | 21.7628 | 22.0901 | 21.0921 | 24.0647 | 29.3956 | 30.1585 | 82.1427 | 84.4251 | 22.578 | 32.1797 | 87.8351 | 629.3846 | 619.2255 | 629.391 | 22.3684 | 32.6467 | 91.9138 | 22.5092 | 34.3213 | 89.3816 | 677.8684 | 805.8992 |  | 297.8287 | 892.1426 | 878.3954 | 630.9115 |  | 323.2566 | 570.0196 | 549.8468 | 856.7031 | 878.9187 | 903.7463 | 895.2665 | 34.2387 | 169.22 | 48.9033 | 359.6324 | 46.4569 | 48.5937 | 52.7228 | 50.8701 | 31.1809 |  |  | -0.21267 | 0.28841 | -111.74 | -0.20243 | 7.2586 | -197.8591 | -203.2174 | -2.5421 | 7.692 | 24.061 | 19.1348 | 0.0020617 | 0.0017594 | 0.00038606 | 23.4257 | 22.0056 | 22.1211 | 22.1711 | 21.9695 | 21.2385 | 20.0631 | 22.148 | 22.3149 | 22.3514 | 22.3006 | 21.902 | 21.126 | 22.2247 | 501.9646 | 384.8336 | 359.4521 | 285.0523 | 236.0616 | 521.2392 | 310.6179 | 22.2846 | 22.0645 | 21.88 | 22.0526 | 22.6849 | 28.6788 | 23.0075 | 69.3804 | 80.8911 | 574.4701 | 551.7042 | 566.3541 | 569.6292 | 46.7712 | 26.1765 | 735.7747 | 21.918 | 22.1579 | 286.9443 | 21.5071 | 21.9624 | 24.8806 | 80.2312 | 89.4907 | 22.334 | 33.6385 | 90.9856 | 708.9147 | 610.5731 | 777.1035 | 779.8412 | 702.607 |  | 701.9967 | 753.851 | 802.1842 | 605.5412 | 611.0484 | 770.3481 |  | 385.215 |  |  | 415.101 | 572.3841 | 650.5133 | [5 empty] | 21.8426 | 558.7259 | 21.7399 | 22.0489 | 394.1165 | 21.2906 | 21.8534 | 457.752 | 602.0457 | 619.0048 |  | 881.6798 | 870.7292 | 497.3098 | 639.0342 | 725.2622 | 569.412 | 640.3996 | 863.8364 | 887.2312 | 579.9819 | 707.7032 | 746.7739 | 940.2043 | 891.6605 | 483.0797 | 585.7789 | 631.0549 | 536.0977 | 631.5585 | 756.0328 | 864.9968 | 951.1365 | 554.8702 | 615.7651 | 585.491 | 712.5203 | 53.5313 | 0.0011705 | 19.2452 | 2.9593 | -28.3604 | 3.095 | 7188.54 | -0.1 | -0.96551 | 1.0867 | -21.3909 | -0.91047 | 6.4412 | -33.629 | -34.0813 | 51.253 | 77.1579 | 34.8093 | 24.7212 | 1.1588 | 47.6852 | 29.4021
42838.4301 | 846 | 22.8466 | 22.8297 | 22.8233 | 22.7368 | 22.3415 | 21.6575 | 22.6696 | 21.719 | 22.3291 | 22.3285 | 22.292 | 21.9273 | 21.1485 | 22.1159 | 21.5392 | 21.762 | 22.0937 | 21.0989 | 24.1354 | 29.4959 | 30.3274 | 82.2713 | 84.4662 | 22.5805 | 32.2815 | 87.8711 | 627.8058 | 618.7247 | 628.3001 | 22.3705 | 32.8281 | 91.9136 | 22.5393 | 34.4713 | 89.3702 | 678.2365 | 801.7305 |  | 298.4707 | 883.4648 | 870.244 | 633.1451 |  | 323.3963 | 569.5064 | 552.4265 | 856.8492 | 877.3407 | 900.4791 | 892.6415 | 34.2182 | 169.8704 | 49.0294 | 360.4804 | 46.8713 | 48.7532 | 52.7014 | 51 | 31.2539 |  |  | 0.060686 | 0.21087 | -108.8954 | -0.31743 | 7.0194 | -197.8493 | -203.2483 | -1.9034 | 7.692 | 23.8772 | 19.4517 | 0.0022112 | 0.0017808 | 0.00039263 | 23.4382 | 22.0067 | 22.1199 | 22.1723 | 21.9695 | 21.2389 | 20.0672 | 22.1415 | 22.3192 | 22.3533 | 22.2989 | 21.8955 | 21.1229 | 22.2222 | 505.5425 | 392.9849 | 361.5825 | 282.3764 | 233.5969 | 521.9255 | 311.0772 | 22.2791 | 22.0695 | 21.8871 | 22.0514 | 22.7203 | 28.7519 | 23.0198 | 69.5713 | 80.9625 | 574.7642 | 551.2319 | 564.384 | 563.7721 | 48.6697 | 28.5133 | 736.0891 | 21.9187 | 22.154 | 287.6762 | 21.5112 | 21.9593 | 24.9445 | 80.3841 | 89.498 | 22.3461 | 33.7865 | 90.9817 | 710.8138 | 609.8302 | 779.7132 | 782.3954 | 704.4534 |  | 701.8596 | 756.0024 | 802.4508 | 605.7122 | 611.0432 | 771.1373 |  | 386.7438 |  |  | 416.2628 | 572.3141 | 651.0332 | [5 empty] | 21.8406 | 558.6958 | 21.7556 | 22.0562 | 396.0844 | 21.2924 | 21.8603 | 457.8895 | 602.474 | 619.0282 |  | 883.6813 | 870.3305 | 498.1335 | 638.9989 | 726.2154 | 569.719 | 639.8317 | 859.121 | 889.8813 | 580.4652 | 707.3429 | 746.9265 | 943.8277 | 892.6606 | 483.5233 | 585.9344 | 628.991 | 536.9931 | 632.5957 | 757.8705 | 870.0268 | 953.2596 | 555.5503 | 615.0945 | 585.9897 | 713.4486 | 53.8132 | 0.00067191 | 19.2463 | 2.9428 | -28.3403 | 3.095 | 7250.31 | -0.06 | 0.51544 | 0.92896 | -21.1104 | -1.1398 | 6.3253 | -33.5815 | -34.0366 | 51.1691 | 77.1808 | 34.8036 | 24.4781 | 0.99388 | 47.7052 | 29.6136
42838.4301 | 847 | 22.837 | 22.8277 | 22.8181 | 22.7353 | 22.3414 | 21.6602 | 22.6697 | 21.7081 | 22.3151 | 22.3175 | 22.2902 | 21.9334 | 21.1476 | 22.1142 | 21.5434 | 21.7577 | 22.0993 | 21.1019 | 24.1922 | 29.5899 | 30.5131 | 82.3889 | 84.5049 | 22.5985 | 32.3889 | 87.8937 | 628.3079 | 618.543 | 628.4648 | 22.3747 | 32.9814 | 91.9125 | 22.5316 | 34.603 | 89.3459 | 678.5904 | 796.937 |  | 298.9775 | 880.8256 | 869.6981 | 635.8029 |  | 323.8045 | 569.5533 | 555.0726 | 856.8646 | 879.9767 | 900.2201 | 893.7174 | 33.9658 | 170.5302 | 49.1241 | 361.3155 | 47.3996 | 48.9209 | 52.6984 | 51.1486 | 31.3303 |  |  | 0.36821 | 0.49277 | -111.2617 | -0.30823 | 7.5754 | -197.8414 | -203.2824 | -2.299 | 7.9217 | 24.368 | 19.9475 | 0.002088 | 0.0016527 | 0.00037949 | 23.4448 | 21.9918 | 22.1123 | 22.171 | 21.9584 | 21.2356 | 20.0549 | 22.1297 | 22.3075 | 22.3427 | 22.2881 | 21.8872 | 21.1161 | 22.2076 | 519.888 | 411.5688 | 375.2201 | 271.7772 | 223.345 | 522.8335 | 311.8621 | 22.2839 | 22.0728 | 21.8906 | 22.0567 | 22.7491 | 28.8384 | 23.0358 | 69.6831 | 81.0401 | 574.8155 | 550.1957 | 562.1855 | 559.1873 | 44.2739 | 39.5877 | 737.0206 | 21.9228 | 22.1537 | 288.0944 | 21.52 | 21.9765 | 25.0118 | 80.5175 | 89.502 | 22.3615 | 33.9382 | 90.9989 | 712.3377 | 610.0403 | 780.3679 | 783.2724 | 703.6491 |  | 701.8201 | 758.1652 | 802.772 | 607.4232 | 610.9741 | 773.1196 |  | 388.3307 |  |  | 418.4584 | 571.8748 | 651.0909 | [5 empty] | 21.8404 | 559.155 | 21.751 | 22.0475 | 397.9993 | 21.2944 | 21.8531 | 457.8942 | 602.2503 | 618.9865 |  | 885.2797 | 870.0977 | 499.1471 | 639.4887 | 727.8013 | 569.6171 | 639.3217 | 857.7958 | 891.6185 | 581.1647 | 706.8221 | 747.9061 | 944.4054 | 892.793 | 483.9968 | 586.2038 | 627.2633 | 537.8959 | 633.6727 | 756.7013 | 870.9391 | 953.974 | 555.7513 | 615.6574 | 586.7156 | 711.2093 | 54.5964 | -0.0010344 | 19.2492 | 2.9341 | -28.3743 | 3.095 | 7329.18 | -0.07 | 1.2698 | 1.4201 | -21.3391 | -1.1232 | 6.5703 | -33.5771 | -34.0357 | 51.182 | 77.2203 | 34.7433 | 23.0887 | -0.39865 | 47.7104 | 29.7495
42838.4301 | 848 | 22.8362 | 22.8287 | 22.8197 | 22.7272 | 22.3383 | 21.6532 | 22.6698 | 21.7091 | 22.314 | 22.3276 | 22.2892 | 21.9337 | 21.1467 | 22.1204 | 21.5437 | 21.7669 | 22.0957 | 21.1 | 24.2593 | 29.6937 | 30.6965 | 82.5238 | 84.556 | 22.5997 | 32.5046 | 87.9172 | 626.7234 | 618.5245 | 626.8469 | 22.3732 | 33.1418 | 91.9146 | 22.539 | 34.734 | 89.3375 | 679.1549 | 803.6087 |  | 299.5386 | 871.3175 | 864.1661 | 637.0833 |  | 324.2769 | 570.1075 | 552.7717 | 858.2381 | 881.9275 | 902.772 | 898.6954 | 34.0795 | 171.2159 | 49.5889 | 362.161 | 47.8897 | 49.0609 | 52.678 | 51.2755 | 31.3646 |  |  | 0.29593 | 0.3758 | -107.0443 | -0.41337 | 6.5213 | -197.8539 | -203.3186 | -1.6983 | 7.4902 | 23.4232 | 19.9258 | 0.0021373 | 0.0018432 | 0.00036634 | 23.4672 | 21.9957 | 22.1188 | 22.1684 | 21.9576 | 21.2371 | 20.0594 | 22.1352 | 22.3112 | 22.3456 | 22.2789 | 21.8828 | 21.1178 | 22.2031 | 528.9961 | 433.8758 | 420.6424 | 279.2462 | 220.1751 | 523.5521 | 313.2888 | 22.2759 | 22.0659 | 21.8883 | 22.0465 | 22.7568 | 28.9135 | 23.054 | 69.8159 | 81.102 | 575.0922 | 551.2957 | 563.0798 | 561.9816 | 45.1529 | 40.8605 | 738.8879 | 21.912 | 22.152 | 288.5634 | 21.5161 | 21.9595 | 25.0698 | 80.64 | 89.5064 | 22.3562 | 34.0783 | 91.0109 | 714.5654 | 610.9748 | 779.0498 | 781.6522 | 706.5861 |  | 701.9574 | 760.8081 | 803.1753 | 609.3222 | 611.0201 | 773.9092 |  | 390.0027 |  |  | 419.7397 | 572.5849 | 652.5434 | [5 empty] | 21.8378 | 560.4212 | 21.7463 | 22.0488 | 399.0537 | 21.288 | 21.8498 | 458.097 | 601.7877 | 618.5693 |  | 881.0211 | 871.0192 | 499.9554 | 640.5627 | 727.6554 | 569.435 | 639.1687 | 861.6821 | 886.9502 | 582.411 | 708.8007 | 748.9201 | 940.6196 | 894.2586 | 484.5011 | 586.2499 | 626.3132 | 539.0187 | 634.8541 | 756.8935 | 871.7402 | 954.2672 | 555.3836 | 615.1762 | 587.6376 | 710.1453 | 54.9082 | 0.00035597 | 19.2507 | 2.91 | -28.3295 | 3.095 | 7407.01 | -0.04 | 1.1373 | 1.2406 | -20.9377 | -1.3011 | 6.1027 | -33.6146 | -34.0757 | 51.1331 | 77.2721 | 34.699 | 22.2388 | -5.222 | 47.801 | 29.7179
42838.4301 | 849 | 22.8339 | 22.8242 | 22.8167 | 22.7248 | 22.336 | 21.6536 | 22.6624 | 21.7105 | 22.3134 | 22.3209 | 22.2856 | 21.9298 | 21.1424 | 22.116 | 21.541 | 21.7628 | 22.095 | 21.1048 | 24.3266 | 29.8131 | 30.8881 | 82.6335 | 84.6056 | 22.6087 | 32.6136 | 87.9407 | 627.5099 | 619.7185 | 627.6648 | 22.3831 | 33.3108 | 91.9255 | 22.5465 | 34.8775 | 89.3258 | 679.56 | 803.5705 |  | 300.2504 | 868.0638 | 862.6634 | 637.5037 |  | 324.4801 | 570.1718 | 551.2718 | 857.562 | 883.9426 | 903.6298 | 899.6068 | 33.8498 | 171.7843 | 50.0787 | 362.904 | 48.4176 | 49.1902 | 52.6556 | 51.431 | 31.4294 |  |  | 0.19079 | -0.25306 | -98.3625 | -0.78464 | 6.6206 | -197.8434 | -203.1549 | -2.2576 | 7.4793 | 23.3892 | 19.9704 | 0.001996 | 0.0016806 | 0.0003647 | 23.4855 | 21.9991 | 22.1138 | 22.1661 | 21.9642 | 21.2358 | 20.0568 | 22.1355 | 22.3151 | 22.3466 | 22.2938 | 21.8937 | 21.1259 | 22.2099 | 527.1123 | 449.1105 | 444.6236 | 288.0996 | 222.5403 | 524.2689 | 314.7675 | 22.2786 | 22.0779 | 21.8886 | 22.0499 | 22.7987 | 29.0025 | 23.0689 | 70.0273 | 81.1776 | 575.279 | 546.1967 | 562.4562 | 559.6757 | 47.6922 | 35.9111 | 740.4204 | 21.9192 | 22.159 | 288.6707 | 21.5193 | 21.9691 | 25.1385 | 80.7633 | 89.5201 | 22.3519 | 34.2258 | 91.0312 | 714.0637 | 611.0927 | 778.9714 | 783.0203 | 707.5259 |  | 702.1427 | 757.0014 | 803.1255 | 609.4893 | 611.039 | 770.7129 |  | 391.5054 |  |  | 422.4947 | 573.8373 | 654.4912 | [5 empty] | 21.8486 | 561.9166 | 21.7467 | 22.0546 | 400.5772 | 21.3028 | 21.8561 | 458.3545 | 601.7643 | 618 |  | 879.9428 | 870.8803 | 500.8172 | 642.409 | 727.3192 | 569.7531 | 638.7289 | 867.6687 | 884.8056 | 583.6658 | 712.821 | 748.3003 | 942.3847 | 895.0714 | 484.4585 | 586.0739 | 625.3286 | 540.1157 | 635.9363 | 758.9166 | 872.3815 | 957.3361 | 555.3551 | 613.975 | 588.555 | 710.1328 | 54.4146 | -0.00021282 | 19.2512 | 2.8803 | -28.3259 | 3.095 | 7422.67 | -0.06 | 0.91362 | -1.0181 | -20.0714 | -1.7927 | 6.1512 | -33.626 | -34.0744 | 51.1511 | 77.3623 | 34.6979 | 22.6101 | -7.6544 | 47.88 | 29.813
42838.4301 | 850 | 22.8286 | 22.8206 | 22.8129 | 22.7267 | 22.3341 | 21.6498 | 22.6598 | 21.7037 | 22.3126 | 22.3067 | 22.2813 | 21.9281 | 21.1351 | 22.1119 | 21.5381 | 21.7609 | 22.0988 | 21.1019 | 24.3987 | 29.915 | 31.073 | 82.7632 | 84.6603 | 22.61 | 32.7223 | 87.9724 | 628.1295 | 618.8686 | 627.9943 | 22.3813 | 33.4666 | 91.9264 | 22.5506 | 35.0088 | 89.3127 | 679.9955 | 802.6838 |  | 301.0014 | 876.5676 | 870.1571 | 639.7847 |  | 325.1263 | 571.7309 | 550.5878 | 857.0639 | 881.7823 | 899.7139 | 898.8436 | 34.0586 | 172.5138 | 50.9488 | 363.9975 | 48.9313 | 49.306 | 52.6253 | 51.5711 | 31.4717 |  |  | 0.17174 | -0.39434 | -107.1678 | 0.22929 | 7.9033 | -197.8526 | -203.2239 | -2.132 | 8.2112 | 24.766 | 19.948 | 0.0020157 | 0.0016674 | 0.00035649 | 23.5049 | 22.0081 | 22.1102 | 22.1556 | 21.9644 | 21.2374 | 20.0631 | 22.138 | 22.3099 | 22.3425 | 22.2927 | 21.8889 | 21.1195 | 22.2129 | 548.3471 | 463.4374 | 445.9388 | 291.4278 | 217.1864 | 526.0026 | 316.0753 | 22.2821 | 22.0758 | 21.8849 | 22.054 | 22.8298 | 29.077 | 23.0915 | 70.1873 | 81.2408 | 575.2241 | 545.7452 | 560.309 | 554.3574 | 51.1998 | 38.8094 | 738.5471 | 21.9195 | 22.1502 | 289.9147 | 21.5077 | 21.9666 | 25.1952 | 80.893 | 89.5241 | 22.3563 | 34.3739 | 91.0401 | 713.4482 | 610.8494 | 780.2591 | 783.751 | 704.7646 |  | 702.2548 | 754.7548 | 803.0081 | 607.7438 | 610.9586 | 768.9256 |  | 393.0705 |  |  | 424.7027 | 575.0354 | 653.9723 | [5 empty] | 21.8411 | 561.3692 | 21.7341 | 22.0497 | 401.9407 | 21.2916 | 21.8489 | 458.3623 | 602.1612 | 618.0014 |  | 886.5033 | 871.5074 | 501.5446 | 644.283 | 728.845 | 569.6798 | 640.0847 | 869.3644 | 889.6751 | 584.6891 | 712.4587 | 749.5984 | 946.2428 | 898.5253 | 485.2662 | 586.2406 | 626.1346 | 541.4929 | 636.4595 | 758.3221 | 876.9683 | 958.8094 | 555.3542 | 614.4494 | 589.6809 | 709.0069 | 54.4037 | -0.00074648 | 19.2508 | 2.8515 | -28.3303 | 3.095 | 7392.52 | -0.09 | 0.86696 | -1.272 | -20.9699 | 0.96997 | 6.7096 | -33.5708 | -34.0234 | 51.2545 | 77.3883 | 34.7315 | 20.6434 | -7.5947 | 47.9142 | 29.9516
42838.4301 | 851 | 22.829 | 22.82 | 22.8085 | 22.7296 | 22.3321 | 21.6518 | 22.6655 | 21.7008 | 22.3043 | 22.309 | 22.281 | 21.9198 | 21.1376 | 22.1059 | 21.5341 | 21.7538 | 22.0976 | 21.0976 | 24.4576 | 30.0158 | 31.2759 | 82.8762 | 84.7028 | 22.6164 | 32.8392 | 88.0019 | 626.1589 | 619.395 | 625.7832 | 22.3897 | 33.6299 | 91.9267 | 22.5635 | 35.1531 | 89.3112 | 680.5653 | 805.3303 |  | 301.7726 | 888.2809 | 878.7951 | 642.9677 |  | 325.9917 | 573.5674 | 550.2044 | 852.3317 | 878.2336 | 894.5545 | 896.5214 | 34.7058 | 173.1765 | 50.5892 | 365.0805 | 49.3145 | 49.4021 | 52.5907 | 51.6971 | 31.5211 |  |  | 0.20722 | -0.086149 | -102.9833 | -0.67293 | 6.2132 | -197.8815 | -203.3376 | -2.4159 | 8.212 | 24.7618 | 20.278 | 0.0019007 | 0.001651 | 0.00039263 | 23.5291 | 22.004 | 22.1165 | 22.1647 | 21.9711 | 21.2435 | 20.0671 | 22.1438 | 22.3176 | 22.3526 | 22.2927 | 21.8982 | 21.1288 | 22.2203 | 534.5114 | 465.7093 | 446.3504 | 287.0787 | 212.6104 | 527.288 | 317.5773 | 22.2749 | 22.0731 | 21.8924 | 22.0497 | 22.8588 | 29.1575 | 23.1072 | 70.2724 | 81.3029 | 575.2315 | 538.2496 | 558.9625 | 555.5037 | 46.6066 | 31.2914 | 738.3422 | 21.9146 | 22.1644 | 291.4 | 21.5141 | 21.9706 | 25.2736 | 81.0122 | 89.5322 | 22.3722 | 34.5193 | 91.0788 | 716.2416 | 611.2423 | 780.4469 | 783.3671 | 708.7052 |  | 702.4956 | 755.4494 | 802.9129 | 607.003 | 610.847 | 769.0767 |  | 394.7441 |  |  | 423.7156 | 576.6614 | 655.8122 | [5 empty] | 21.8493 | 561.0154 | 21.7584 | 22.0661 | 403.0721 | 21.301 | 21.8572 | 458.6639 | 603.0003 | 618.1219 |  | 892.168 | 872.3077 | 502.0917 | 644.8939 | 728.8626 | 569.6466 | 640.2498 | 863.6439 | 892.1278 | 585.1657 | 710.7427 | 749.6305 | 951.02 | 900.762 | 485.6803 | 586.0003 | 625.1416 | 542.6377 | 637.1855 | 759.8773 | 876.6384 | 958.4608 | 554.6467 | 614.0453 | 590.8942 | 709.7867 | 55.3188 | -1.6191e-05 | 19.2523 | 2.8242 | -28.3427 | 3.095 | 7392.43 | -0.03 | 0.95115 | -0.5952 | -20.5788 | -1.6635 | 5.9359 | -33.4993 | -33.958 | 51.2025 | 77.3395 | 34.7315 | 22.4726 | -7.4036 | 47.9536 | 29.921
42838.4301 | 852 | 22.831 | 22.8178 | 22.8171 | 22.7292 | 22.3302 | 21.6531 | 22.6749 | 21.7094 | 22.3111 | 22.3162 | 22.2876 | 21.9213 | 21.1354 | 22.1134 | 21.5362 | 21.758 | 22.1015 | 21.112 | 24.5359 | 30.1285 | 31.4616 | 82.9931 | 84.7608 | 22.6254 | 32.9534 | 88.0009 | 626.1846 | 619.155 | 626.2854 | 22.3967 | 33.7933 | 91.918 | 22.5767 | 35.2867 | 89.2954 | 681.3722 | 812.6314 |  | 302.4776 | 901.0515 | 888.6676 | 649.1226 |  | 326.6462 | 574.2761 | 551.5265 | 849.5917 | 879.8613 | 894.3974 | 895.8288 | 35.0961 | 173.8482 | 49.8323 | 366.0498 | 49.8409 | 49.5166 | 52.5407 | 51.7946 | 31.5776 |  |  | -0.18376 | 0.48817 | -108.2882 | -0.37066 | 6.2 | -197.8046 | -203.3429 | -1.9198 | 7.7582 | 24.6325 | 20.5851 | 0.001996 | 0.0016527 | 0.00039098 | 23.545 | 22.007 | 22.1196 | 22.1638 | 21.9647 | 21.24 | 20.0611 | 22.1379 | 22.3104 | 22.3476 | 22.2927 | 21.8954 | 21.1272 | 22.2158 | 518.7749 | 439.5473 | 435.7849 | 295.1844 | 212.62 | 528.3448 | 318.8229 | 22.2773 | 22.0603 | 21.8942 | 22.0407 | 22.892 | 29.2477 | 23.1136 | 70.3683 | 81.367 | 575.3479 | 537.2483 | 557.6041 | 555.5775 | 49.7449 | 29.311 | 738.4414 | 21.9135 | 22.164 | 291.7653 | 21.524 | 21.9698 | 25.3356 | 81.1424 | 89.5448 | 22.3691 | 34.6716 | 91.0872 | 717.7999 | 611.9409 | 777.7066 | 780.0538 | 712.5468 |  | 702.8535 | 754.7802 | 802.7388 | 607.3914 | 610.8266 | 769.2033 |  | 396.2011 |  |  | 424.2001 | 579.1763 | 658.6306 | [5 empty] | 21.8405 | 561.1969 | 21.7498 | 22.0556 | 403.0157 | 21.2989 | 21.8543 | 459.4233 | 602.7546 | 618.4773 |  | 893.0684 | 872.781 | 502.668 | 645.4036 | 729.6961 | 569.7039 | 639.4169 | 859.8282 | 888.642 | 585.7047 | 710.9828 | 750.5681 | 952.3648 | 901.3981 | 485.729 | 585.6809 | 624.0644 | 543.7462 | 638.2809 | 763.1439 | 879.5422 | 957.8165 | 554.4218 | 613.589 | 591.9437 | 711.8042 | 52.9384 | 0.00083341 | 19.2549 | 2.8027 | -28.3645 | 3.095 | 7385.67 | -0.04 | -0.89594 | 1.4174 | -21.111 | -1.2351 | 5.9293 | -33.4906 | -33.9562 | 51.1811 | 77.304 | 34.717 | 24.4617 | -6.0329 | 47.964 | 29.9383
42838.4302 | 853 | 22.8391 | 22.8193 | 22.8198 | 22.7345 | 22.3371 | 21.6493 | 22.6719 | 21.7137 | 22.3081 | 22.3189 | 22.2926 | 21.9282 | 21.14 | 22.1185 | 21.5344 | 21.7632 | 22.106 | 21.1068 | 24.6045 | 30.2315 | 31.6586 | 83.1118 | 84.8096 | 22.6343 | 33.0678 | 87.9877 | 626.8093 | 621.6835 | 627.6217 | 22.392 | 33.9623 | 91.9171 | 22.5814 | 35.4288 | 89.2718 | 682.3748 | 809.6729 |  | 303.1928 | 897.6757 | 886.1327 | 650.6496 |  | 327.1876 | 574.4971 | 551.0991 | 848.864 | 881.7448 | 896.8815 | 896.447 | 35.3659 | 174.528 | 49.7481 | 367.0869 | 50.2924 | 49.6149 | 52.4875 | 51.9239 | 31.6563 |  |  | 0.24468 | -0.083521 | -96.4982 | -0.64467 | 6.3275 | -197.8526 | -203.3613 | -1.724 | 7.5928 | 24.2035 | 20.7063 | 0.0018596 | 0.0016083 | 0.00038277 | 23.5548 | 22.0073 | 22.1231 | 22.167 | 21.9629 | 21.2431 | 20.0659 | 22.1463 | 22.3139 | 22.3473 | 22.2924 | 21.8974 | 21.125 | 22.215 | 532.5719 | 429.8992 | 419.3345 | 281.8366 | 214.9341 | 529.9783 | 319.5284 | 22.276 | 22.0649 | 21.8978 | 22.0446 | 22.9262 | 29.3337 | 23.1424 | 70.4839 | 81.4426 | 575.3482 | 538.803 | 557.0999 | 555.2179 | 51.5035 | 29.202 | 737.9188 | 21.9365 | 22.1556 | 292.1112 | 21.5222 | 21.967 | 25.4114 | 81.2681 | 89.5618 | 22.388 | 34.8224 | 91.1195 | 716.6311 | 614.2118 | 776.6698 | 779.0733 | 712.9609 |  | 703.2309 | 754.1967 | 802.5887 | 607.8795 | 610.8686 | 769.8942 |  | 397.6977 |  |  | 424.6795 | 581.0197 | 661.8312 | [5 empty] | 21.8447 | 562.2346 | 21.7515 | 22.0524 | 403.1247 | 21.3015 | 21.8625 | 459.5728 | 602.0725 | 618.6024 |  | 890.514 | 872.5697 | 503.249 | 645.5186 | 730.7251 | 569.6235 | 640.1806 | 860.6299 | 884.7899 | 586.2396 | 710.318 | 751.2253 | 953.8588 | 903.7656 | 485.8175 | 585.5422 | 623.4248 | 544.8359 | 638.5506 | 764.0801 | 880.9703 | 962.2972 | 554.2762 | 614.0933 | 592.7058 | 710.0556 | 52.3346 | 0.0010792 | 19.2586 | 2.7837 | -28.3189 | 3.0951 | 7395.76 | 0 | 1.0346 | -0.58637 | -19.9312 | -1.6291 | 5.9963 | -33.5302 | -33.9938 | 51.2597 | 77.2737 | 34.7111 | 23.3015 | -4.0934 | 48.1475 | 29.9483
42838.4302 | 854 | 22.8327 | 22.8114 | 22.8143 | 22.7289 | 22.3325 | 21.6536 | 22.6665 | 21.7085 | 22.3118 | 22.3239 | 22.2816 | 21.9242 | 21.1362 | 22.1105 | 21.5429 | 21.7735 | 22.1198 | 21.1092 | 24.6791 | 30.3423 | 31.8565 | 83.2312 | 84.8712 | 22.6559 | 33.1854 | 88.042 | 625.6968 | 622.6565 | 626.1923 | 22.3963 | 34.1339 | 91.929 | 22.5868 | 35.5729 | 89.2652 | 683.0692 | 811.5379 |  | 303.873 | 876.3603 | 868.8751 | 650.5973 |  | 327.3164 | 574.6599 | 549.7475 | 847.2144 | 881.2467 | 894.9091 | 894.149 | 35.5002 | 175.1001 | 49.9561 | 367.9806 | 50.8819 | 49.7248 | 52.4412 | 52.0312 | 31.7356 |  |  | 0.096826 | 0.082731 | -99.1234 | -0.42454 | 9.2747 | -197.8289 | -203.2384 | -2.2878 | 8.5485 | 26.3424 | 20.6559 | 0.0018843 | 0.0016099 | 0.00036634 | 23.5683 | 21.9994 | 22.1188 | 22.1555 | 21.957 | 21.2375 | 20.0589 | 22.1444 | 22.3182 | 22.3472 | 22.2878 | 21.8938 | 21.12 | 22.2104 | 555.7319 | 459.7648 | 426.0296 | 283.8379 | 226.2668 | 532.1039 | 320.7098 | 22.2772 | 22.0626 | 21.9005 | 22.0465 | 22.959 | 29.4074 | 23.1586 | 70.6486 | 81.5142 | 575.4853 | 542.7622 | 558.1318 | 558.0939 | 57.2316 | 36.2695 | 737.4658 | 21.9261 | 22.1627 | 292.2422 | 21.5149 | 21.9632 | 25.4842 | 81.3806 | 89.5688 | 22.3761 | 34.9652 | 91.1349 | 714.7123 | 615.1198 | 776.2917 | 778.2464 | 706.8453 |  | 703.2686 | 757.2472 | 802.6841 | 611.5079 | 611.0962 | 771.4217 |  | 399.4012 |  |  | 425.0345 | 580.9547 | 660.3547 | [5 empty] | 21.848 | 563.4609 | 21.7554 | 22.0608 | 403.0863 | 21.3031 | 21.8584 | 459.5645 | 601.8617 | 619.0856 |  | 882.0966 | 872.5732 | 504.0204 | 645.6872 | 732.0345 | 569.8849 | 641.0542 | 858.7658 | 880.6677 | 587.0972 | 711.4619 | 750.5743 | 952.3083 | 905.3163 | 485.893 | 585.422 | 622.8243 | 545.5827 | 638.5661 | 764.0643 | 877.6149 | 964.492 | 553.8319 | 614.4614 | 593.172 | 710.428 | 51.1033 | -0.0016382 | 19.2602 | 2.7568 | -28.322 | 3.0951 | 7439.51 | -0.14 | 0.65032 | 0.58365 | -20.2025 | -1.3221 | 7.2535 | -33.5 | -33.9549 | 51.4386 | 77.2185 | 34.6523 | 21.2151 | -4.6501 | 48.3058 | 29.8912
42838.4302 | 855 | 22.8361 | 22.8078 | 22.8081 | 22.7311 | 22.3376 | 21.6511 | 22.6667 | 21.7047 | 22.312 | 22.3186 | 22.2852 | 21.9214 | 21.1357 | 22.1145 | 21.5388 | 21.774 | 22.1215 | 21.1146 | 24.7464 | 30.4503 | 32.0599 | 83.3369 | 84.9249 | 22.6601 | 33.3038 | 88.0852 | 626.6047 | 622.9048 | 627.4035 | 22.3981 | 34.2842 | 91.9193 | 22.5901 | 35.7017 | 89.2465 | 683.7866 | 810.3993 |  | 304.5459 | 866.8635 | 860.4253 | 648.2063 |  | 327.7651 | 574.9692 | 549.5224 | 847.4911 | 880.3516 | 893.3265 | 895.4278 | 35.7972 | 175.9833 | 50.9658 | 369.167 | 51.3776 | 49.8318 | 52.3699 | 52.1276 | 31.77 |  |  | 0.4083 | -2.7199 | -98.0155 | -0.21098 | 7.8987 | -197.842 | -203.1273 | -1.835 | 8.5037 | 25.2179 | 20.8372 | 0.0018449 | 0.0015639 | 0.00037949 | 23.5867 | 22.0032 | 22.1162 | 22.1578 | 21.958 | 21.241 | 20.0565 | 22.1418 | 22.3122 | 22.3455 | 22.2904 | 21.8901 | 21.1216 | 22.205 | 557.1967 | 471.1365 | 443.3654 | 298.2737 | 231.3312 | 534.5199 | 322.4935 | 22.2685 | 22.0626 | 21.9041 | 22.0455 | 22.9904 | 29.481 | 23.1729 | 70.8343 | 81.5715 | 575.6258 | 539.6463 | 558.4153 | 557.2931 | 57.628 | 33.3212 | 738.0015 | 21.9374 | 22.1665 | 292.6169 | 21.5243 | 21.9761 | 25.569 | 81.5185 | 89.5781 | 22.4086 | 35.1205 | 91.167 | 714.4255 | 616.6493 | 774.8882 | 776.6156 | 705.0615 |  | 703.3202 | 758.7836 | 802.8493 | 614.6169 | 611.3001 | 771.7068 |  | 400.9918 |  |  | 425.4416 | 579.8851 | 659.4542 | [5 empty] | 21.8451 | 564.2634 | 21.7501 | 22.0585 | 402.0581 | 21.2934 | 21.8532 | 460.0259 | 601.8504 | 619.9347 |  | 880.0365 | 874.8261 | 504.658 | 646.002 | 734.6666 | 570.2026 | 641.3021 | 864.0658 | 882.1137 | 587.7542 | 711.5644 | 748.4832 | 951.3167 | 904.8735 | 485.6433 | 585.272 | 622.8091 | 546.0533 | 638.4793 | 765.0214 | 876.1282 | 966.7032 | 553.6604 | 613.6828 | 593.3742 | 709.2809 | 53.6641 | -0.012719 | 19.2626 | 2.7284 | -28.3244 | 3.095 | 7501.54 | -0.01 | 1.3363 | -3.3471 | -20.0929 | -0.93221 | 6.6893 | -33.4784 | -33.9226 | 51.5005 | 77.2271 | 34.6036 | 21.6082 | -6.293 | 48.5345 | 29.9369
42838.4302 | 856 | 22.8374 | 22.8085 | 22.8057 | 22.7255 | 22.3304 | 21.6428 | 22.6661 | 21.704 | 22.3115 | 22.315 | 22.2846 | 21.9143 | 21.1299 | 22.1102 | 21.5375 | 21.7674 | 22.1126 | 21.1082 | 24.8088 | 30.5511 | 32.2557 | 83.4319 | 84.9668 | 22.6624 | 33.4105 | 88.1045 | 627.7923 | 622.3387 | 628.3524 | 22.3917 | 34.4438 | 91.9228 | 22.5944 | 35.8339 | 89.233 | 684.1715 | 803.5451 |  | 305.1379 | 864.8704 | 858.0041 | 643.3567 |  | 329.0142 | 576.4666 | 549.8621 | 851.9439 | 881.4085 | 891.6891 | 894.1367 | 35.8891 | 176.7299 | 52.1952 | 370.1302 | 51.9286 | 49.947 | 52.3064 | 52.2505 | 31.8084 |  |  | 0.24533 | -2.4156 | -91.4266 | -0.50077 | 7.2849 | -197.8322 | -203.2712 | -2.0118 | 8.3196 | 25.294 | 20.8785 | 0.0018284 | 0.0015787 | 0.00034499 | 23.6067 | 22.0121 | 22.1138 | 22.1692 | 21.9618 | 21.238 | 20.0648 | 22.1465 | 22.3132 | 22.3537 | 22.2893 | 21.8951 | 21.1218 | 22.2152 | 551.7218 | 448.8159 | 424.593 | 305.2613 | 234.4883 | 536.7878 | 323.8247 | 22.2789 | 22.0699 | 21.9063 | 22.0459 | 23.026 | 29.5745 | 23.2004 | 71.0001 | 81.6495 | 575.6954 | 542.7401 | 557.5441 | 557.6176 | 48.9489 | 39.4836 | 740.5839 | 21.9184 | 22.153 | 293.1716 | 21.5114 | 21.9667 | 25.6265 | 81.6363 | 89.57 | 22.3919 | 35.2595 | 91.1675 | 715.6659 | 617.079 | 773.6229 | 775.3932 | 704.2861 |  | 703.2817 | 763.7118 | 803.4258 | 614.3664 | 611.4718 | 774.374 |  | 402.5018 |  |  | 426.0565 | 579.2113 | 658.0336 | [5 empty] | 21.8392 | 564.9001 | 21.7502 | 22.051 | 401.9384 | 21.2958 | 21.8549 | 460.5118 | 601.8843 | 621.1128 |  | 888.8531 | 875.6378 | 504.8866 | 646.2412 | 735.8809 | 570.5543 | 642.3743 | 865.3574 | 884.9102 | 587.9661 | 710.4286 | 748.3098 | 953.1095 | 906.2263 | 485.579 | 585.3254 | 623.5412 | 546.3219 | 638.7512 | 763.7717 | 872.9315 | 968.4016 | 553.8525 | 613.3845 | 593.4262 | 710.3125 | 54.5866 | 0.0017181 | 19.2652 | 2.6939 | -28.3227 | 3.0951 | 7512.96 | -0.1 | 1.0364 | -3.1571 | -19.4229 | -1.4375 | 6.4197 | -33.454 | -33.9108 | 51.5128 | 77.2692 | 34.6423 | 22.7407 | -3.9952 | 48.7565 | 29.9394
42838.4302 | 857 | 22.8297 | 22.8197 | 22.8137 | 22.7232 | 22.3271 | 21.6475 | 22.6681 | 21.7075 | 22.3152 | 22.3215 | 22.2839 | 21.9215 | 21.1314 | 22.1124 | 21.5347 | 21.7623 | 22.1041 | 21.107 | 24.875 | 30.6528 | 32.4617 | 83.5222 | 85.0044 | 22.6713 | 33.5118 | 88.1183 | 627.1329 | 621.6307 | 627.347 | 22.3949 | 34.5947 | 91.9329 | 22.5979 | 35.9745 | 89.2221 | 684.5542 | 801.8667 |  | 305.7141 | 864.8865 | 858.3201 | 641.0309 |  | 329.9015 | 578.0762 | 549.2875 | 852.9511 | 883.2688 | 891.8241 | 894.4553 | 36.2449 | 177.4992 | 53.0343 | 371.1825 | 52.4341 | 50.0627 | 52.2331 | 52.3845 | 31.8765 |  |  | 0.090254 | 0.20036 | -93.0957 | -0.67425 | 5.9589 | -197.8269 | -203.2384 | -2.0992 | 8.096 | 24.8551 | 21.6979 | 0.001858 | 0.0015557 | 0.0003647 | 23.6248 | 22.0091 | 22.1137 | 22.1613 | 21.9675 | 21.2346 | 20.0531 | 22.1375 | 22.3127 | 22.3531 | 22.289 | 21.8949 | 21.1218 | 22.2094 | 552.559 | 471.4526 | 435.2659 | 296.6727 | 232.818 | 538.8717 | 325.4314 | 22.286 | 22.0742 | 21.925 | 22.0588 | 23.0742 | 29.6697 | 23.2242 | 71.1266 | 81.7293 | 576.0914 | 536.5923 | 558.6788 | 561.1265 | 55.3518 | 37.4934 | 744.041 | 21.9299 | 22.165 | 293.6488 | 21.514 | 21.9705 | 25.708 | 81.7673 | 89.5886 | 22.4029 | 35.4114 | 91.1937 | 717.2805 | 617.0683 | 773.4186 | 775.3101 | 707.3565 |  | 703.4656 | 765.8429 | 804.0428 | 611.5363 | 611.4706 | 777.4484 |  | 404.1071 |  |  | 427.6335 | 579.6915 | 658.4097 | [5 empty] | 21.8431 | 564.2886 | 21.7523 | 22.0488 | 402.0288 | 21.3046 | 21.8618 | 461.0205 | 601.8505 | 622.4954 |  | 892.4199 | 874.4655 | 505.2309 | 646.1478 | 734.2992 | 571.1108 | 643.6334 | 863.178 | 886.1476 | 588.2013 | 707.8491 | 750.2558 | 953.0792 | 905.6835 | 485.8525 | 585.5245 | 623.7637 | 546.7753 | 639.6293 | 762.8068 | 870.6426 | 969.1478 | 554.165 | 613.5991 | 593.9645 | 714.582 | 51.7859 | -0.00015664 | 19.269 | 2.6721 | -28.3349 | 3.0951 | 7538.82 | -0.1 | 0.62826 | 0.9101 | -19.618 | -1.6695 | 5.8064 | -33.4555 | -33.91 | 51.4715 | 77.4019 | 34.7207 | 23.1313 | -4.9248 | 48.9079 | 29.9079
42838.4302 | 858 | 22.8274 | 22.8258 | 22.8137 | 22.7208 | 22.333 | 21.6592 | 22.6709 | 21.7108 | 22.3137 | 22.3187 | 22.2792 | 21.9263 | 21.1377 | 22.1143 | 21.5308 | 21.7588 | 22.1145 | 21.1145 | 24.9522 | 30.7595 | 32.6951 | 83.629 | 85.0546 | 22.6778 | 33.6341 | 88.155 | 628.8409 | 620.9089 | 629.6913 | 22.4011 | 34.7592 | 91.9435 | 22.6147 | 36.1141 | 89.2163 | 684.973 | 801.0884 |  | 306.3012 | 862.0342 | 856.0263 | 642.283 |  | 331.3051 | 579.6675 | 549.3687 | 851.5029 | 886.1486 | 900.5536 | 896.7867 | 36.3674 | 178.2617 | 53.6279 | 372.286 | 52.7701 | 50.2314 | 52.1519 | 52.5093 | 31.9436 |  |  | 0.22431 | 0.50132 | -90.6972 | -0.7991 | 6.2592 | -197.8171 | -203.2483 | -1.8751 | 7.919 | 24.1586 | 21.6064 | 0.001858 | 0.0015196 | 0.00035156 | 23.639 | 22.0099 | 22.1105 | 22.1586 | 21.9641 | 21.235 | 20.0627 | 22.1351 | 22.3226 | 22.3475 | 22.291 | 21.8995 | 21.1231 | 22.2171 | 558.0013 | 472.9076 | 448.0877 | 288.3434 | 222.5945 | 540.9155 | 327.3462 | 22.2805 | 22.0664 | 21.9186 | 22.0476 | 23.102 | 29.756 | 23.2421 | 71.2372 | 81.7921 | 576.3122 | 536.4147 | 558.5164 | 559.7275 | 42.6884 | 19.9092 | 745.339 | 21.9249 | 22.1551 | 294.2174 | 21.5168 | 21.9731 | 25.784 | 81.8689 | 89.5976 | 22.4103 | 35.5559 | 91.2103 | 718.1378 | 617.943 | 773.1183 | 776.7419 | 710.0186 |  | 703.6676 | 767.7584 | 804.5971 | 609.9503 | 611.4506 | 780.9503 |  | 405.741 |  |  | 428.237 | 580.3387 | 659.7214 | [5 empty] | 21.841 | 564.3022 | 21.7588 | 22.0502 | 402.2256 | 21.3049 | 21.8655 | 461.5046 | 601.8965 | 622.8325 |  | 887.7025 | 873.4777 | 505.7802 | 646.1268 | 733.8607 | 571.4677 | 643.3466 | 861.2808 | 885.5222 | 588.6037 | 707.254 | 754.1844 | 953.8709 | 905.6529 | 486.167 | 585.681 | 623.7443 | 547.2967 | 640.4784 | 761.8733 | 874.2505 | 971.5399 | 554.5734 | 614.1231 | 594.7557 | 716.6752 | 52.243 | -0.00031815 | 19.273 | 2.6446 | -28.2972 | 3.0951 | 7552.91 | -0.03 | 0.99173 | 1.441 | -19.3817 | -1.8193 | 5.9732 | -33.5798 | -34.0377 | 51.4458 | 77.5214 | 34.7611 | 23.0028 | -6.0431 | 48.9682 | 29.9836
42838.4302 | 859 | 22.8378 | 22.8285 | 22.8132 | 22.7256 | 22.3306 | 21.6546 | 22.665 | 21.7161 | 22.3182 | 22.3186 | 22.2789 | 21.9247 | 21.1441 | 22.1111 | 21.5327 | 21.7569 | 22.1177 | 21.1072 | 25.0326 | 30.8756 | 32.9061 | 83.7421 | 85.1003 | 22.6849 | 33.7537 | 88.1721 | 630.2377 | 620.847 | 631.1788 | 22.409 | 34.9207 | 91.9518 | 22.6209 | 36.244 | 89.1768 | 685.746 | 802.3103 |  | 306.8783 | 867.8163 | 861.3678 | 644.0882 |  | 332.2293 | 579.5692 | 547.6041 | 846.2516 | 889.966 | 902.4623 | 900.9331 | 36.3547 | 178.9046 | 53.4073 | 373.1493 | 53.4207 | 50.4162 | 52.0679 | 52.6285 | 32.0093 |  |  | 0.3945 | 0.22533 | -92.1508 | -0.90555 | 7.1601 | -197.8703 | -203.2187 | -2.4337 | 7.7633 | 23.9727 | 21.7071 | 0.0017611 | 0.0015376 | 0.00035813 | 23.6525 | 22.0078 | 22.1057 | 22.1627 | 21.9576 | 21.232 | 20.0583 | 22.1323 | 22.3177 | 22.3382 | 22.2872 | 21.8927 | 21.1194 | 22.202 | 541.5971 | 439.9227 | 403.9528 | 275.5249 | 213.5779 | 541.7623 | 327.7226 | 22.2814 | 22.0709 | 21.9171 | 22.0495 | 23.1416 | 29.8309 | 23.2636 | 71.3828 | 81.8639 | 576.5498 | 542.882 | 558.9859 | 562.8899 | 43.0971 | 24.4959 | 747.0743 | 21.9262 | 22.1578 | 294.4309 | 21.517 | 21.9713 | 25.8618 | 81.9507 | 89.5957 | 22.4236 | 35.7078 | 91.2198 | 717.1441 | 618.5605 | 774.7578 | 778.7423 | 706.6664 |  | 703.6783 | 766.7679 | 804.9503 | 610.1934 | 611.4892 | 780.4604 |  | 407.1899 |  |  | 427.7123 | 579.8948 | 659.5094 | [5 empty] | 21.8448 | 564.7523 | 21.7553 | 22.049 | 402.0019 | 21.3019 | 21.8593 | 462.1694 | 601.9979 | 622.6008 |  | 886.8859 | 872.4486 | 506.5659 | 646.5627 | 734.5729 | 571.9017 | 643.1597 | 859.0493 | 886.6776 | 588.9064 | 708.12 | 758.5596 | 958.8659 | 908.6931 | 486.6091 | 586.0599 | 624.3548 | 547.6734 | 641.0587 | 763.4587 | 880.8566 | 974.4896 | 555.2886 | 614.8949 | 595.4519 | 716.9115 | 53.0161 | 0.0011002 | 19.2742 | 2.6056 | -28.3406 | 3.0951 | 7533.82 | -0.15 | 1.3163 | 0.966 | -19.5353 | -1.9365 | 6.3938 | -33.6116 | -34.0628 | 51.5415 | 77.659 | 34.7614 | 25.0233 | -1.0788 | 49.094 | 29.9354
42838.4302 | 860 | 22.8304 | 22.8122 | 22.8171 | 22.7165 | 22.3264 | 21.648 | 22.663 | 21.7009 | 22.3149 | 22.3108 | 22.2735 | 21.9246 | 21.1331 | 22.1075 | 21.5324 | 21.7692 | 22.1209 | 21.115 | 25.1065 | 30.9886 | 33.1302 | 83.8672 | 85.1433 | 22.6979 | 33.8747 | 88.206 | 630.9601 | 621.1315 | 631.2021 | 22.4046 | 35.0801 | 91.9591 | 22.6287 | 36.389 | 89.1592 | 686.2561 | 799.492 |  | 307.5201 | 873.8728 | 866.6491 | 642.7144 |  | 332.9736 | 579.3281 | 554.223 | 845.7188 | 888.5423 | 899.1326 | 897.6055 | 36.3117 | 179.5753 | 52.5938 | 374.1411 | 53.9875 | 50.5784 | 51.9811 | 52.7625 | 32.0691 |  |  | 0.30447 | -0.39959 | -84.0341 | -1.0922 | 6.1869 | -197.8112 | -203.3402 | -2.0006 | 8.0415 | 24.6755 | 21.6373 | 0.0018432 | 0.0015196 | 0.00037949 | 23.6738 | 22.0068 | 22.1108 | 22.1592 | 21.9555 | 21.2349 | 20.0583 | 22.1361 | 22.311 | 22.3419 | 22.2866 | 21.8906 | 21.1173 | 22.2025 | 543.4906 | 445.745 | 390.4823 | 267.3975 | 203.863 | 542.8046 | 328.1466 | 22.2782 | 22.0702 | 21.919 | 22.0576 | 23.1748 | 29.9117 | 23.2746 | 71.5698 | 81.9314 | 577.1484 | 546.1602 | 560.735 | 568.0648 | 54.3237 | 33.1745 | 746.5355 | 21.9288 | 22.1615 | 294.9016 | 21.5231 | 21.9724 | 25.9547 | 82.0402 | 89.6175 | 22.4176 | 35.8536 | 91.2226 | 717.1732 | 618.8745 | 776.3129 | 780.925 | 708.1321 |  | 703.7682 | 765.8153 | 805.3377 | 609.8527 | 611.5212 | 780.0838 |  | 408.7245 |  |  | 428.3735 | 579.5823 | 659.577 | [5 empty] | 21.8428 | 565.0542 | 21.7499 | 22.0541 | 401.9452 | 21.2991 | 21.8571 | 463.0825 | 602.8969 | 622.7297 |  | 882.1677 | 873.1051 | 507.1608 | 647.2738 | 736.6598 | 572.3621 | 643.6393 | 849.5117 | 885.6189 | 589.1897 | 707.6244 | 764.3493 | 964.7224 | 910.3453 | 486.9853 | 586.4417 | 624.8996 | 548.1659 | 641.5296 | 764.5261 | 883.6256 | 975.2012 | 555.4482 | 614.6548 | 596.1272 | 717.2586 | 52.4326 | 0.0012407 | 19.2741 | 2.5762 | -28.3298 | 3.0951 | 7555.98 | -0.01 | 1.1564 | -1.2862 | -18.6525 | -2.1264 | 5.935 | -33.559 | -34.0247 | 51.5223 | 77.8064 | 34.7768 | 25.0569 | 0.48586 | 49.2484 | 29.8917
42838.4302 | 861 | 22.8345 | 22.8178 | 22.8136 | 22.7209 | 22.3253 | 21.6478 | 22.6716 | 21.7115 | 22.3113 | 22.3157 | 22.2814 | 21.922 | 21.1311 | 22.1078 | 21.5297 | 21.7668 | 22.1223 | 21.1187 | 25.182 | 31.1025 | 33.3484 | 83.9833 | 85.1972 | 22.7103 | 33.995 | 88.2372 | 630.8789 | 619.5318 | 630.618 | 22.4127 | 35.247 | 91.9706 | 22.6362 | 36.5308 | 89.1553 | 686.643 | 809.7132 |  | 308.1424 | 869.1055 | 862.5196 | 639.7704 |  | 333.3695 | 579.603 | 561.7032 | 847.3429 | 887.4103 | 897.7685 | 898.998 | 36.069 | 180.0711 | 52.736 | 375.0423 | 54.4225 | 50.7262 | 51.8843 | 52.8515 | 32.1331 |  |  | 0.37347 | 0.10967 | -83.5984 | -0.65125 | 7.965 | -197.8263 | -203.3153 | -2.1478 | 8.1486 | 25.0507 | 21.7756 | 0.0017381 | 0.0014276 | 0.0003417 | 23.6942 | 22.0129 | 22.1205 | 22.1629 | 21.9647 | 21.2392 | 20.0608 | 22.1416 | 22.3103 | 22.3519 | 22.2954 | 21.8904 | 21.1234 | 22.2073 | 545.5817 | 438.5973 | 420.6056 | 282.8208 | 220.9158 | 544.3312 | 329.3487 | 22.277 | 22.0717 | 21.9251 | 22.0513 | 23.2192 | 30.0021 | 23.2948 | 71.764 | 82.0126 | 577.6542 | 546.3154 | 561.2761 | 567.4062 | 50.3019 | 30.8219 | 746.2012 | 21.9284 | 22.1489 | 295.7683 | 21.519 | 21.9622 | 26.0207 | 82.1226 | 89.6271 | 22.428 | 35.9923 | 91.2359 | 717.5266 | 620.1532 | 780.9547 | 786.6748 | 709.1651 |  | 703.9358 | 763.9174 | 805.7488 | 614.5838 | 611.7717 | 778.7804 |  | 410.6222 |  |  | 428.2677 | 579.7731 | 659.8576 | [5 empty] | 21.8359 | 566.3154 | 21.7453 | 22.0518 | 402.0184 | 21.2998 | 21.856 | 463.7356 | 604.116 | 623.2759 |  | 882.13 | 874.2281 | 507.6041 | 647.4985 | 737.2698 | 572.8837 | 643.821 | 850.1223 | 888.2728 | 589.5763 | 707.312 | 769.7804 | 968.9811 | 912.5107 | 487.4582 | 586.6139 | 625.7965 | 548.6425 | 641.7596 | 764.8055 | 881.2018 | 977.4794 | 555.7113 | 614.2167 | 596.9244 | 717.5357 | 52.555 | 0.00047533 | 19.2716 | 2.5464 | -28.3877 | 3.0951 | 7585.57 | -0.1 | 1.2803 | 0.67395 | -18.6071 | -1.6423 | 6.7301 | -33.5407 | -34.0028 | 51.5337 | 77.9876 | 34.6917 | 25.1828 | -2.6682 | 49.4185 | 29.9946
42838.4303 | 862 | 22.8203 | 22.8139 | 22.804 | 22.7184 | 22.3242 | 21.6492 | 22.6671 | 21.708 | 22.3121 | 22.3119 | 22.2811 | 21.9161 | 21.1287 | 22.1059 | 21.5335 | 21.7672 | 22.1278 | 21.1286 | 25.2564 | 31.2042 | 33.5732 | 84.0955 | 85.2489 | 22.7243 | 34.111 | 88.2626 | 630.0859 | 617.8436 | 630.056 | 22.4173 | 35.4042 | 91.9843 | 22.6404 | 36.668 | 89.1525 | 686.9367 | 809.8186 |  | 308.6676 | 867.7008 | 862.2003 | 638.6408 |  | 333.4527 | 580.1255 | 560.6369 | 845.7975 | 887.4303 | 896.213 | 898.9017 | 35.7347 | 180.695 | 53.1167 | 375.9603 | 55.0392 | 50.8536 | 51.7897 | 52.9139 | 32.2144 |  |  | 0.13297 | -0.41668 | -84.9968 | -0.81421 | 5.5593 | -197.8473 | -203.2338 | -2.1846 | 8.3294 | 25.6866 | 21.9631 | 0.0016559 | 0.0014489 | 0.0003532 | 23.7199 | 22.0043 | 22.1217 | 22.1595 | 21.9676 | 21.2371 | 20.0655 | 22.1389 | 22.3155 | 22.3483 | 22.2927 | 21.8911 | 21.1186 | 22.2154 | 518.8307 | 414.1756 | 415.2795 | 288.5932 | 233.7697 | 545.5359 | 330.2954 | 22.2798 | 22.0674 | 21.9304 | 22.052 | 23.2545 | 30.0966 | 23.3192 | 71.9297 | 82.0807 | 577.9429 | 545.0445 | 562.0939 | 566.7031 | 54.7364 | 30.3657 | 746.153 | 21.9196 | 22.151 | 297.0517 | 21.5172 | 21.9619 | 26.1095 | 82.2267 | 89.6453 | 22.4288 | 36.1392 | 91.2479 | 719.9373 | 620.1537 | 782.4889 | 788.2799 | 711.4999 |  | 704.0097 | 766.3266 | 806.3881 | 612.7418 | 611.8784 | 780.6332 |  | 412.1901 |  |  | 428.7303 | 580.4166 | 660.7843 | [5 empty] | 21.8418 | 566.5778 | 21.7536 | 22.0543 | 402.503 | 21.307 | 21.8559 | 464.2599 | 604.5068 | 623.492 |  | 888.6514 | 874.8132 | 508.1316 | 647.2255 | 737.3684 | 573.0276 | 642.8125 | 845.0185 | 892.7485 | 589.7129 | 706.3986 | 772.5175 | 972.4555 | 916.0092 | 488.0003 | 586.851 | 625.8199 | 549.0625 | 642.2367 | 764.6486 | 879.2448 | 980.6886 | 556.5959 | 614.4795 | 597.5345 | 717.0784 | 51.9438 | 0.0011564 | 19.2713 | 2.5164 | -28.3587 | 3.0951 | 7598.66 | -0.07 | 0.76371 | -1.314 | -18.7678 | -1.8369 | 5.6189 | -33.5202 | -33.9734 | 51.4865 | 78.1207 | 34.7626 | 28.4386 | -1.9241 | 49.5169 | 30.0625
42838.4303 | 863 | 22.8311 | 22.8131 | 22.8081 | 22.7182 | 22.3288 | 21.6541 | 22.6609 | 21.7067 | 22.3148 | 22.3128 | 22.2796 | 21.9182 | 21.1359 | 22.113 | 21.5287 | 21.7636 | 22.1302 | 21.1238 | 25.3297 | 31.311 | 33.8364 | 84.2071 | 85.2954 | 22.7191 | 34.2218 | 88.2708 | 630.0679 | 616.2191 | 630.6053 | 22.4231 | 35.5645 | 92.0085 | 22.6531 | 36.8021 | 89.1483 | 687.2196 | 808.6363 |  | 309.1832 | 876.1173 | 869.7721 | 637.9493 |  | 333.7563 | 580.2176 | 560.8158 | 849.2123 | 886.5507 | 896.7897 | 898.1452 | 35.7771 | 181.4435 | 52.9795 | 376.9525 | 55.5672 | 50.9519 | 51.6812 | 53.0022 | 32.2821 |  |  | 0.28936 | -0.091405 | -82.1974 | -0.56976 | 5.8892 | -197.8565 | -203.2581 | -1.3856 | 8.3395 | 25.3119 | 21.8551 | 0.0017052 | 0.0013569 | 0.00033677 | 23.7369 | 22.0051 | 22.1129 | 22.1616 | 21.9649 | 21.231 | 20.0586 | 22.1353 | 22.3147 | 22.3394 | 22.2877 | 21.8916 | 21.1205 | 22.2079 | 539.0523 | 399.9599 | 397.3542 | 278.9771 | 234.519 | 547.5554 | 330.9857 | 22.2873 | 22.074 | 21.934 | 22.0576 | 23.2985 | 30.1777 | 23.3363 | 72.125 | 82.1432 | 578.171 | 547.0797 | 562.6179 | 566.2983 | 48.9811 | 27.4567 | 747.8634 | 21.9245 | 22.1614 | 298.3397 | 21.5147 | 21.9694 | 26.1894 | 82.3205 | 89.6614 | 22.4428 | 36.2991 | 91.2618 | 721.2433 | 619.6517 | 783.041 | 788.6124 | 713.7421 |  | 704.1732 | 766.756 | 806.9343 | 609.2184 | 611.7959 | 781.244 |  | 413.7589 |  |  | 429.158 | 581.2903 | 661.5093 | [5 empty] | 21.8455 | 565.8049 | 21.7527 | 22.0574 | 401.5128 | 21.3014 | 21.8602 | 464.6258 | 604.277 | 624.0182 |  | 886.7953 | 877.577 | 508.9119 | 647.0607 | 737.7805 | 572.829 | 642.4008 | 833.7346 | 897.5288 | 589.7136 | 708.1076 | 772.4639 | 972.5807 | 918.6142 | 488.2045 | 587.0535 | 625.5669 | 549.3353 | 642.2809 | 765.1091 | 876.9684 | 980.571 | 556.9283 | 614.6224 | 597.7698 | 717.1157 | 50.4622 | -0.00042347 | 19.2725 | 2.4835 | -28.2958 | 3.0951 | 7607.27 | -0.12 | 1.127 | -0.61549 | -18.4571 | -1.5367 | 5.7846 | -33.5293 | -33.9839 | 51.4634 | 78.2799 | 34.8452 | 26.6684 | 0.17875 | 49.6008 | 30.112
42838.4303 | 864 | 22.836 | 22.8206 | 22.8111 | 22.7264 | 22.3333 | 21.6474 | 22.6644 | 21.7084 | 22.318 | 22.3185 | 22.2757 | 21.9236 | 21.1393 | 22.1152 | 21.5273 | 21.7659 | 22.1347 | 21.1282 | 25.4136 | 31.4343 | 34.1256 | 84.3321 | 85.3424 | 22.7378 | 34.3529 | 88.2894 | 629.565 | 614.7972 | 630.0537 | 22.4183 | 35.7098 | 92.0352 | 22.6584 | 36.9314 | 89.1327 | 687.5349 | 806.9664 |  | 309.7208 | 880.0886 | 873.8902 | 639.492 |  | 334.1646 | 581.2881 | 558.8865 | 852.096 | 886.6947 | 897.1692 | 899.0988 | 36.6729 | 182.0724 | 52.0949 | 377.6431 | 56.0339 | 51.0429 | 51.5788 | 53.1067 | 32.3455 |  |  | 0.16254 | 0.095215 | -84.816 | -0.48237 | 5.3234 | -197.773 | -203.3264 | -1.5853 | 8.2395 | 24.8316 | 22.1907 | 0.0016444 | 0.0014621 | 0.00034827 | 23.7556 | 22.0113 | 22.1123 | 22.1617 | 21.9685 | 21.2464 | 20.0564 | 22.1403 | 22.3173 | 22.3511 | 22.2919 | 21.8963 | 21.1297 | 22.2153 | 557.8194 | 395.0572 | 381.9879 | 275.5563 | 231.5529 | 548.948 | 331.432 | 22.2787 | 22.0714 | 21.934 | 22.0509 | 23.331 | 30.2519 | 23.3502 | 72.2953 | 82.2085 | 578.4923 | 544.8887 | 563.0083 | 568.5922 | 49.1022 | 26.0744 | 748.4334 | 21.9284 | 22.1628 | 298.8595 | 21.5124 | 21.9734 | 26.2776 | 82.404 | 89.6731 | 22.4458 | 36.4455 | 91.2606 | 720.5681 | 619.2668 | 783.4381 | 788.9933 | 710.0689 |  | 704.1603 | 765.8844 | 807.2388 | 606.1284 | 611.664 | 781.0105 |  | 415.4856 |  |  | 429.1247 | 581.0092 | 661.1321 | [5 empty] | 21.8471 | 564.6068 | 21.7487 | 22.0445 | 402.1304 | 21.3016 | 21.8487 | 465.4386 | 603.7507 | 623.8979 |  | 883.0239 | 879.9214 | 509.5185 | 647.0265 | 737.7491 | 572.7146 | 641.3845 | 841.5337 | 892.5622 | 589.9087 | 709.4926 | 773.3578 | 969.1415 | 921.6049 | 489.1957 | 587.4424 | 625.049 | 549.9507 | 642.6087 | 765.1754 | 876.6714 | 981.0575 | 556.7468 | 614.8954 | 598.2484 | 718.0456 | 53.0174 | 0.002961 | 19.271 | 2.4627 | -28.339 | 3.0951 | 7547.32 | -0.09 | 0.84438 | 0.62858 | -18.7606 | -1.4148 | 5.5007 | -33.5276 | -33.9951 | 51.5624 | 78.3996 | 34.9067 | 24.9129 | 1.958 | 49.63 | 30.1022
42838.4303 | 865 | 22.8322 | 22.828 | 22.8075 | 22.7253 | 22.3348 | 21.6523 | 22.6707 | 21.7087 | 22.3124 | 22.3189 | 22.2727 | 21.9357 | 21.1367 | 22.1099 | 21.5329 | 21.7701 | 22.1355 | 21.1321 | 25.4894 | 31.5465 | 34.3892 | 84.4487 | 85.3907 | 22.7425 | 34.4739 | 88.304 | 629.3746 | 615.4197 | 630.0686 | 22.4263 | 35.854 | 92.0599 | 22.6655 | 37.0723 | 89.1212 | 687.8891 | 801.6072 |  | 310.288 | 877.1347 | 871.4077 | 641.6135 |  | 335.1414 | 583.0151 | 557.881 | 851.7484 | 886.0111 | 898.0093 | 899.5309 | 37.3646 | 182.8112 | 52.1937 | 378.3812 | 56.6354 | 51.0895 | 51.4662 | 53.1721 | 32.398 |  |  | -0.12857 | 0.2549 | -78.7108 | -0.60985 | 5.8846 | -195.6124 | -203.2358 | -1.3146 | 8.1785 | 25.1115 | 22.339 | 0.0016559 | 0.0013865 | 0.00037784 | 23.7706 | 22.0087 | 22.1169 | 22.1535 | 21.9639 | 21.2385 | 20.0639 | 22.1428 | 22.319 | 22.356 | 22.2896 | 21.9004 | 21.128 | 22.2138 | 546.2334 | 398.7382 | 370.7565 | 272.8482 | 226.6507 | 549.698 | 331.6887 | 22.2766 | 22.0714 | 21.9342 | 22.055 | 23.3784 | 30.342 | 23.3659 | 72.459 | 82.2743 | 578.8977 | 542.6173 | 564.0653 | 569.8999 | 45.0307 | 34.2385 | 748.6414 | 21.9317 | 22.1685 | 299.4985 | 21.5117 | 21.9736 | 26.3651 | 82.4857 | 89.7027 | 22.4526 | 36.5994 | 91.2639 | 719.7655 | 618.3733 | 783.215 | 788.3363 | 706.2467 |  | 703.9859 | 769.4169 | 807.8919 | 604.2588 | 611.4739 | 781.7206 |  | 417.0893 |  |  | 429.9051 | 580.1589 | 659.244 | [5 empty] | 21.8389 | 563.2802 | 21.7461 | 22.0426 | 402.2883 | 21.2901 | 21.844 | 466.4061 | 603.4166 | 623.7977 |  | 889.7361 | 881.6694 | 510.1948 | 647.474 | 737.4219 | 572.5783 | 641.3115 | 847.8736 | 891.4643 | 590.3854 | 709.3526 | 773.4408 | 968.9836 | 925.3152 | 489.4762 | 587.6372 | 624.7168 | 550.6122 | 642.8294 | 765.967 | 882.0425 | 983.247 | 556.9448 | 614.2217 | 598.5592 | 719.4381 | 55.4473 | -0.00086584 | 19.2695 | 2.4354 | -28.3571 | 3.0951 | 7511.45 | -0.11 | -0.75098 | 1.0295 | -18.091 | -1.5924 | 5.7854 | -33.3559 | -33.9997 | 51.6268 | 78.5066 | 34.9234 | 26.3783 | 3.2474 | 49.6522 | 30.1339
42838.4303 | 866 | 22.8283 | 22.8161 | 22.8087 | 22.7227 | 22.3287 | 21.6442 | 22.6683 | 21.7002 | 22.305 | 22.3134 | 22.274 | 21.9269 | 21.1331 | 22.1089 | 21.528 | 21.7659 | 22.1388 | 21.1337 | 25.5632 | 31.6529 | 34.6501 | 84.5421 | 85.4411 | 22.752 | 34.5949 | 88.3269 | 629.2434 | 614.3763 | 629.8708 | 22.4396 | 36.016 | 92.095 | 22.6825 | 37.2154 | 89.1115 | 688.1829 | 804.678 |  | 310.8449 | 870.389 | 865.3295 | 643.5578 |  | 335.5742 | 583.8434 | 560.004 | 851.7546 | 884.4094 | 900.6642 | 900.1202 | 37.9038 | 183.4755 | 52.8928 | 379.361 | 57.1887 | 51.1632 | 51.3644 | 53.2425 | 32.4634 |  |  | 0.13428 | 0.10507 | -81.6573 | -0.53954 | 7.7258 | -154.088 | -203.4382 | -2.0276 | 8.8639 | 27.2462 | 23.0726 | 0.0016083 | 0.0013471 | 0.00034663 | 23.79 | 22.0102 | 22.1114 | 22.1587 | 21.9604 | 21.2374 | 20.0564 | 22.1346 | 22.3105 | 22.3438 | 22.2873 | 21.894 | 21.1179 | 22.2046 | 541.2274 | 430.4722 | 404.726 | 283.3631 | 239.0505 | 550.6937 | 332.9034 | 22.272 | 22.0702 | 21.9441 | 22.0566 | 23.4321 | 30.4388 | 23.3999 | 72.6702 | 82.3436 | 579.1055 | 542.1297 | 563.21 | 566.6205 | 52.159 | 34.3707 | 750.8674 | 21.9322 | 22.1548 | 300.1913 | 21.5124 | 21.9607 | 26.4401 | 82.5696 | 89.7153 | 22.451 | 36.7462 | 91.2674 | 720.2185 | 617.7049 | 782.7518 | 787.6605 | 706.2139 |  | 704.0137 | 774.4558 | 808.9579 | 601.7742 | 611.2272 | 785.2404 |  | 418.5784 |  |  | 430.2687 | 579.8707 | 658.7108 | [5 empty] | 21.8535 | 562.2184 | 21.762 | 22.0586 | 400.4885 | 21.3032 | 21.8589 | 466.3968 | 603.3828 | 623.6794 |  | 898.5703 | 882.3764 | 510.8141 | 648.1757 | 737.469 | 572.2402 | 640.5037 | 851.4316 | 897.3552 | 591.0194 | 708.8134 | 774.9648 | 968.3626 | 927.7905 | 489.1608 | 587.6341 | 624.6136 | 550.7588 | 642.9477 | 765.4999 | 882.8458 | 982.6958 | 556.8392 | 613.876 | 598.7227 | 720.8124 | 54.3883 | 0.001023 | 19.2692 | 2.412 | -28.351 | 3.0951 | 7488.87 | -0.03 | 0.76741 | 0.66131 | -18.4354 | -1.4985 | 6.6365 | -29.6381 | -34.0552 | 51.6343 | 78.7021 | 34.9469 | 27.1712 | -0.33091 | 49.6656 | 30.26
42838.4303 | 867 | 22.8328 | 22.8106 | 22.7991 | 22.7288 | 22.3351 | 21.6487 | 22.6655 | 21.7031 | 22.3073 | 22.3175 | 22.2741 | 21.9211 | 21.132 | 22.1082 | 21.5253 | 21.7717 | 22.1372 | 21.1284 | 25.6393 | 31.7647 | 34.9201 | 84.6371 | 85.4885 | 22.7633 | 34.7045 | 88.3416 | 628.543 | 613.6011 | 628.9632 | 22.43 | 36.1642 | 92.1152 | 22.6796 | 37.3412 | 89.09 | 688.5827 | 804.8806 |  | 311.3867 | 861.9493 | 857.451 | 643.4823 |  | 336.3364 | 585.103 | 559.6461 | 853.5884 | 881.0756 | 898.4329 | 900.7197 | 38.4977 | 184.1869 | 52.3141 | 380.6455 | 57.601 | 51.215 | 51.2648 | 53.2946 | 32.5341 |  |  | -0.13645 | -0.13412 | -75.7005 | -0.67359 | 6.388 | -114.4836 | -203.5407 | -1.8166 | 7.9729 | 25.4115 | 23.3386 | 0.0015475 | 0.0012649 | 0.00038934 | 23.8139 | 22.0111 | 22.1093 | 22.1606 | 21.9625 | 21.2397 | 20.0595 | 22.1394 | 22.3094 | 22.3446 | 22.2888 | 21.8934 | 21.1204 | 22.2031 | 539.851 | 427.4422 | 410.5513 | 288.0475 | 255.8401 | 551.5458 | 334.1183 | 22.2776 | 22.0693 | 21.9424 | 22.0492 | 23.4711 | 30.5191 | 23.4199 | 72.7913 | 82.4073 | 579.1774 | 535.9448 | 562.1217 | 564.3106 | 38.5474 | 25.6281 | 752.6555 | 21.9372 | 22.1614 | 300.7246 | 21.5238 | 21.9657 | 26.5351 | 82.6677 | 89.7424 | 22.469 | 36.8923 | 91.2873 | 720.2475 | 618.1008 | 781.7493 | 786.6153 | 708.2101 |  | 704.2625 | 773.3403 | 809.7106 | 601.8164 | 611.0432 | 785.5996 |  | 420.0707 |  |  | 431.0424 | 579.8122 | 659.951 | [5 empty] | 21.85 | 561.9259 | 21.7569 | 22.0477 | 399.0927 | 21.3052 | 21.8505 | 466.466 | 603.1361 | 623.8918 |  | 894.406 | 883.2008 | 511.4464 | 648.6047 | 738.3161 | 572.0759 | 639.5942 | 849.506 | 898.2159 | 591.3976 | 708.904 | 776.1943 | 968.3001 | 927.7891 | 488.64 | 587.3921 | 624.197 | 550.9807 | 643.2536 | 765.3268 | 886.2979 | 983.6604 | 556.509 | 613.59 | 598.8958 | 721.4526 | 52.0601 | 3.9981e-05 | 19.2694 | 2.3913 | -28.3275 | 3.0952 | 7460.85 | -0.02 | -0.77319 | -0.74768 | -17.7633 | -1.6756 | 6.0288 | -25.5226 | -34.0313 | 51.6385 | 78.9706 | 34.9118 | 27.527 | -0.78166 | 49.7594 | 30.3362
42838.4303 | 868 | 22.8276 | 22.8113 | 22.8042 | 22.7118 | 22.3285 | 21.6426 | 22.6574 | 21.6977 | 22.3108 | 22.3084 | 22.2786 | 21.9183 | 21.1259 | 22.1077 | 21.5235 | 21.769 | 22.1382 | 21.1266 | 25.7189 | 31.8769 | 35.2077 | 84.7351 | 85.5405 | 22.7719 | 34.8236 | 88.3599 | 630.0336 | 613.4222 | 630.982 | 22.4367 | 36.3402 | 92.1494 | 22.6996 | 37.4883 | 89.0945 | 689.0075 | 811.7732 |  | 312.1007 | 858.8428 | 855.7069 | 645.5781 |  | 337.012 | 586.301 | 558.3298 | 854.3051 | 880.2956 | 896.4885 | 900.1146 | 38.4907 | 184.8567 | 51.3804 | 381.7753 | 58.1377 | 51.2381 | 51.1537 | 53.3402 | 32.579 |  |  | 0.014686 | 0.20824 | -74.3863 | -0.7531 | 5.4043 | -111.3177 | -203.6143 | -1.8869 | 8.6787 | 26.0216 | 23.1738 | 0.0018564 | 0.0015146 | 0.0003532 | 23.8333 | 22.0126 | 22.1173 | 22.1631 | 21.9655 | 21.2402 | 20.0585 | 22.1402 | 22.3118 | 22.3537 | 22.2959 | 21.9 | 21.1272 | 22.2152 | 514.2581 | 405.1694 | 401.7576 | 284.9923 | 249.9169 | 551.4002 | 334.6543 | 22.2781 | 22.0718 | 21.9484 | 22.0574 | 23.5185 | 30.6095 | 23.4445 | 72.8775 | 82.4724 | 579.2705 | 540.4749 | 561.625 | 564.0055 | 54.6593 | 31.3007 | 751.5045 | 21.9345 | 22.154 | 301.3797 | 21.5128 | 21.9653 | 26.6261 | 82.7453 | 89.7597 | 22.4656 | 37.0319 | 91.3053 | 719.6367 | 618.4012 | 779.8546 | 784.5541 | 709.7451 |  | 704.3807 | 769.8471 | 810.0849 | 604.9819 | 611.0298 | 785.2817 |  | 421.6965 |  |  | 432.004 | 579.8839 | 660.7841 | [5 empty] | 21.8467 | 563.1795 | 21.7581 | 22.0526 | 398.2952 | 21.3041 | 21.8566 | 466.7997 | 602.9548 | 623.5436 |  | 892.0371 | 884.2825 | 511.9267 | 648.681 | 738.1542 | 572.2899 | 639.6892 | 845.1106 | 896.0824 | 591.4142 | 710.1782 | 775.5312 | 966.9879 | 926.1101 | 488.6657 | 586.8129 | 624.2801 | 551.2822 | 643.6809 | 766.1984 | 889.0499 | 984.0102 | 556.1499 | 612.9638 | 599.2159 | 722.3088 | 49.6883 | -0.00026899 | 19.2729 | 2.3635 | -28.3525 | 3.0952 | 7457.63 | 0 | 0.25394 | 0.93231 | -17.6207 | -1.773 | 5.5406 | -25.1463 | -34.0092 | 51.6242 | 79.1858 | 34.8214 | 30.336 | 0.28225 | 49.7987 | 30.3604
42838.4303 | 869 | 22.8276 | 22.8011 | 22.7996 | 22.7156 | 22.3228 | 21.6374 | 22.6563 | 21.6967 | 22.3063 | 22.3027 | 22.272 | 21.9154 | 21.1243 | 22.1063 | 21.5205 | 21.7664 | 22.1403 | 21.1301 | 25.7911 | 31.9886 | 35.526 | 84.8261 | 85.5875 | 22.7774 | 34.938 | 88.37 | 630.384 | 615.4604 | 631.4246 | 22.4472 | 36.4943 | 92.1729 | 22.7122 | 37.6277 | 89.0879 | 689.7655 | 810.0502 |  | 313.2024 | 863.1053 | 858.921 | 646.4194 |  | 337.6042 | 585.7191 | 557.8641 | 852.0502 | 880.3678 | 895.6133 | 900.4752 | 38.7611 | 185.4263 | 50.6784 | 382.6231 | 58.6744 | 51.2331 | 51.0487 | 53.4061 | 32.6486 |  |  | 0.72634 | 0.68728 | -73.1568 | -0.32072 | 7.208 | -147.5812 | -203.5216 | -1.329 | 8.8536 | 26.5062 | 22.9188 | 0.0019286 | 0.0014522 | 0.0003647 | 23.85 | 22.0061 | 22.1042 | 22.1609 | 21.9573 | 21.2265 | 20.0519 | 22.1352 | 22.3064 | 22.3394 | 22.2946 | 21.895 | 21.1204 | 22.209 | 522.7222 | 419.844 | 404.5907 | 281.3043 | 236.3627 | 552.4904 | 335.5961 | 22.2756 | 22.0662 | 21.9504 | 22.06 | 23.5638 | 30.6982 | 23.4564 | 72.9762 | 82.5311 | 579.5379 | 545.8111 | 562.6987 | 568.183 | 61.6202 | 37.932 | 749.7855 | 21.9266 | 22.1471 | 302.0164 | 21.4987 | 21.9593 | 26.7141 | 82.816 | 89.776 | 22.4693 | 37.1834 | 91.316 | 719.2715 | 618.0401 | 777.4019 | 782.2689 | 707.9149 |  | 704.2897 | 768.1005 | 810.2365 | 606.5234 | 611.0238 | 784.5365 |  | 423.1118 |  |  | 432.2227 | 579.8127 | 660.7481 | [5 empty] | 21.8387 | 563.6182 | 21.7575 | 22.0472 | 398.0437 | 21.3011 | 21.853 | 467.2375 | 603.111 | 623.908 |  | 888.9993 | 885.5635 | 512.3478 | 648.79 | 738.3861 | 572.3807 | 640.6302 | 843.7981 | 893.6661 | 591.282 | 713.1572 | 774.5415 | 962.4884 | 925.6591 | 488.6394 | 586.302 | 624.6552 | 551.5931 | 644.1461 | 767.4478 | 888.3799 | 982.259 | 556.1129 | 611.9982 | 599.3688 | 721.4271 | 51.5982 | 0.00084043 | 19.2755 | 2.3389 | -28.3409 | 3.0951 | 7466.79 | -0.07 | 1.7863 | 1.6932 | -17.4686 | -1.1566 | 6.3964 | -28.9432 | -33.9888 | 51.6532 | 79.2823 | 34.7774 | 29.6555 | 0.12016 | 49.9497 | 30.2893
42838.4303 | 870 | 22.8239 | 22.8026 | 22.8082 | 22.7166 | 22.325 | 21.6471 | 22.6569 | 21.7029 | 22.3137 | 22.3107 | 22.2758 | 21.917 | 21.1321 | 22.1069 | 21.527 | 21.7694 | 22.1485 | 21.1459 | 25.8794 | 32.1046 | 35.8883 | 84.932 | 85.6517 | 22.7901 | 35.0678 | 88.3949 | 631.3955 | 618.1429 | 632.0573 | 22.4472 | 36.6501 | 92.1911 | 22.7154 | 37.7614 | 89.075 | 690.2327 | 807.89 |  | 313.6078 | 852.4274 | 849.7903 | 643.6079 |  | 338.4312 | 583.8936 | 559.245 | 856.8407 | 882.0065 | 894.9736 | 902.575 | 38.484 | 186.0974 | 51.2485 | 383.7733 | 59.2191 | 51.2455 | 50.9536 | 53.4783 | 32.721 |  |  | 0.28016 | 0.47109 | -70.9154 | -0.36409 | 7.3473 | -150.0802 | -203.5118 | -1.0333 | 8.7709 | 27.1323 | 23.2544 | 0.0018136 | 0.0013931 | 0.00038113 | 23.8754 | 22.022 | 22.1099 | 22.167 | 21.9624 | 21.2369 | 20.062 | 22.1456 | 22.3171 | 22.3487 | 22.2904 | 21.9034 | 21.1272 | 22.2149 | 531.8877 | 449.6365 | 435.656 | 291.6998 | 243.8543 | 554.0965 | 337.2287 | 22.2709 | 22.0735 | 21.9584 | 22.0631 | 23.6132 | 30.7857 | 23.4738 | 73.1479 | 82.5899 | 579.9577 | 546.4117 | 563.9243 | 569.8045 | 55.4508 | 42.451 | 749.3581 | 21.9294 | 22.156 | 302.4138 | 21.5133 | 21.9621 | 26.8174 | 82.9018 | 89.7952 | 22.4913 | 37.3344 | 91.3336 | 721.0603 | 617.3893 | 776.4547 | 781.6004 | 709.136 |  | 704.3126 | 768.7654 | 810.4959 | 605.5778 | 610.9694 | 783.7031 |  | 424.5708 |  |  | 432.2502 | 580.5484 | 661.0077 | [5 empty] | 21.8363 | 563.2 | 21.7505 | 22.0455 | 398.6055 | 21.2959 | 21.8462 | 467.7341 | 603.3608 | 624.6251 |  | 883.6749 | 886.0945 | 512.6623 | 648.8453 | 739.0134 | 572.5162 | 641.8827 | 841.3665 | 892.8189 | 591.0713 | 713.8927 | 774.488 | 959.4001 | 924.3129 | 488.959 | 586.1494 | 625.2435 | 551.919 | 644.4931 | 768.7425 | 886.8261 | 980.5275 | 555.986 | 611.2601 | 599.3793 | 722.6762 | 52.202 | -0.0038852 | 19.2781 | 2.3165 | -28.3106 | 3.0952 | 7424.27 | 0.03 | 1.1098 | 1.4003 | -17.1806 | -1.231 | 6.4562 | -29.1792 | -33.9787 | 51.6248 | 79.3458 | 34.7937 | 29.0212 | -3.0663 | 50.1354 | 30.315
42838.4304 | 871 | 22.8296 | 22.8103 | 22.8059 | 22.7157 | 22.3251 | 21.6429 | 22.6553 | 21.706 | 22.3057 | 22.3125 | 22.2737 | 21.9183 | 21.1365 | 22.106 | 21.5282 | 21.7702 | 22.1524 | 21.1447 | 25.9623 | 32.2076 | 36.2418 | 85.0273 | 85.7066 | 22.7984 | 35.1835 | 88.4215 | 633.7963 | 618.8873 | 634.3946 | 22.4436 | 36.8085 | 92.2059 | 22.7217 | 37.8986 | 89.0671 | 690.4184 | 805.229 |  | 314.2071 | 844.1495 | 842.5564 | 641.572 |  | 339.9714 | 584.3476 | 558.7346 | 859.8223 | 885.0621 | 897.083 | 905.7169 | 37.7227 | 186.7987 | 52.2481 | 384.958 | 59.6794 | 51.2494 | 50.85 | 53.5245 | 32.7935 |  |  | 0.18159 | 1.0277 | -69.0518 | -0.15512 | 7.783 | -147.388 | -203.521 | -2.0105 | 8.6979 | 26.7391 | 22.9988 | 0.001858 | 0.0014588 | 0.00036963 | 23.8949 | 22.019 | 22.1146 | 22.1539 | 21.9547 | 21.2341 | 20.0542 | 22.1379 | 22.305 | 22.3329 | 22.2917 | 21.89 | 21.1174 | 22.209 | 544.9235 | 446.12 | 458.0082 | 301.151 | 256.9838 | 555.6261 | 339.3376 | 22.2697 | 22.0679 | 21.9496 | 22.0536 | 23.657 | 30.8669 | 23.4899 | 73.2917 | 82.6404 | 580.1618 | 543.1266 | 563.1303 | 565.5284 | 52.8011 | 34.9373 | 750.4076 | 21.9344 | 22.1607 | 302.6317 | 21.5087 | 21.9617 | 26.9078 | 82.9872 | 89.8137 | 22.4957 | 37.481 | 91.3525 | 722.104 | 617.2225 | 775.9114 | 781.4137 | 710.6604 |  | 704.4354 | 767.9778 | 810.7279 | 605.8726 | 610.918 | 782.2342 |  | 426.1614 |  |  | 432.0227 | 582.4925 | 661.262 | [5 empty] | 21.8459 | 563.0461 | 21.7528 | 22.0488 | 398.7068 | 21.2977 | 21.8448 | 468.1552 | 603.9319 | 625.3238 |  | 879.0941 | 887.3769 | 512.8423 | 648.8607 | 740.7404 | 572.6232 | 642.9019 | 835.93 | 890.2961 | 591.0466 | 713.934 | 776.9289 | 956.4679 | 922.9637 | 489.6071 | 586.1945 | 627.2121 | 552.1397 | 644.8776 | 769.3867 | 885.9486 | 976.734 | 556.2291 | 610.723 | 599.3154 | 724.2631 | 51.8746 | -0.00021282 | 19.2825 | 2.2914 | -28.3209 | 3.0952 | 7419.43 | 0.02 | 0.89465 | 2.0688 | -16.9579 | -0.80375 | 6.6508 | -28.9424 | -34.0101 | 51.6118 | 79.4411 | 34.776 | 27.9397 | -5.2062 | 50.2348 | 30.4682
42838.4304 | 872 | 22.8261 | 22.8098 | 22.8108 | 22.7244 | 22.3298 | 21.6462 | 22.6575 | 21.705 | 22.3077 | 22.3156 | 22.2799 | 21.918 | 21.1329 | 22.1159 | 21.524 | 21.7698 | 22.1569 | 21.1442 | 26.0399 | 32.3197 | 36.5832 | 85.1239 | 85.7571 | 22.805 | 35.2969 | 88.4206 | 634.9759 | 619.8756 | 635.532 | 22.4499 | 36.9567 | 92.231 | 22.7344 | 38.0336 | 89.0655 | 690.5058 | 809.1818 |  | 314.6396 | 844.3643 | 843.1793 | 641.6842 |  | 340.7575 | 586.4566 | 559.4288 | 860.6183 | 886.68 | 896.9474 | 904.763 | 37.5676 | 187.5159 | 53.7991 | 386.07 | 59.998 | 51.25 | 50.7404 | 53.5756 | 32.8624 |  |  | 0.62777 | 0.48357 | -67.4767 | -0.43703 | 5.723 | -176.9602 | -203.3849 | -1.5755 | 8.1388 | 25.2242 | 23.4986 | 0.0017808 | 0.0013175 | 0.00036799 | 23.9105 | 22.0124 | 22.1151 | 22.158 | 21.9493 | 21.2329 | 20.0566 | 22.14 | 22.3041 | 22.3477 | 22.2903 | 21.8926 | 21.1152 | 22.215 | 558.5473 | 448.2709 | 451.6097 | 306.6145 | 253.615 | 556.9659 | 340.9692 | 22.275 | 22.0676 | 21.9625 | 22.0586 | 23.7086 | 30.9617 | 23.524 | 73.3742 | 82.7023 | 580.2602 | 533.9899 | 562.8193 | 564.51 | 56.8255 | 34.0036 | 750.0189 | 21.936 | 22.1585 | 302.5641 | 21.5134 | 21.9685 | 27.0089 | 83.075 | 89.8424 | 22.5059 | 37.62 | 91.3753 | 720.9374 | 617.6832 | 776.4708 | 782.452 | 711.2177 |  | 704.6382 | 762.5234 | 810.4745 | 608.0279 | 610.9791 | 778.7125 |  | 427.5863 |  |  | 432.17 | 585.0368 | 661.9593 | [5 empty] | 21.8514 | 563.6863 | 21.7606 | 22.0537 | 398.857 | 21.3007 | 21.8473 | 468.5036 | 604.57 | 625.0837 |  | 872.157 | 887.8494 | 512.952 | 648.9962 | 742.9422 | 572.4788 | 642.812 | 832.091 | 887.7403 | 591.2347 | 714.524 | 779.5838 | 953.7981 | 923.1583 | 490.1622 | 586.5184 | 628.6479 | 552.2371 | 645.2172 | 769.5085 | 883.1736 | 972.4888 | 556.6981 | 611.346 | 599.2553 | 722.7622 | 51.074 | 0.0041617 | 19.2865 | 2.2691 | -28.3542 | 3.0952 | 7432.26 | -0.01 | 1.6645 | 1.4208 | -16.7839 | -1.3507 | 5.7028 | -31.7114 | -33.9967 | 51.645 | 79.5124 | 34.7274 | 26.7482 | -4.2286 | 50.2519 | 30.5131
42838.4304 | 873 | 22.8301 | 22.8048 | 22.8152 | 22.7224 | 22.3294 | 21.6516 | 22.6558 | 21.7055 | 22.3108 | 22.3211 | 22.2747 | 21.9238 | 21.1368 | 22.1193 | 21.5282 | 21.7687 | 22.1562 | 21.1518 | 26.1262 | 32.4457 | 36.9124 | 85.2165 | 85.8172 | 22.8227 | 35.4258 | 88.4196 | 634.4402 | 621.4527 | 634.7444 | 22.4544 | 37.0977 | 92.2482 | 22.7369 | 38.1598 | 89.0703 | 690.549 | 807.1067 |  | 315.2277 | 851.9592 | 849.9714 | 640.7609 |  | 341.4514 | 588.311 | 558.6587 | 853.0049 | 890.0457 | 898.6852 | 900.818 | 37.5397 | 188.2344 | 54.2855 | 387.1257 | 60.4554 | 51.2485 | 50.6437 | 53.6387 | 32.9248 |  |  | 0.44904 | -0.31548 | -65.6408 | -0.57173 | 7.5083 | -197.8355 | -203.2483 | -1.9369 | 8.5594 | 26.5786 | 23.6095 | 0.0017594 | 0.0012896 | 0.00036141 | 23.9349 | 22.0163 | 22.107 | 22.163 | 21.9564 | 21.2328 | 20.0547 | 22.1345 | 22.3081 | 22.3422 | 22.2879 | 21.8922 | 21.1168 | 22.2063 | 576.3842 | 477.1251 | 448.5143 | 309.4671 | 247.346 | 558.335 | 342.2813 | 22.2712 | 22.0648 | 21.9655 | 22.057 | 23.7501 | 31.0545 | 23.534 | 73.4616 | 82.7582 | 580.5504 | 534.0993 | 563.8275 | 566.8394 | 49.68 | 35.9868 | 747.2923 | 21.9284 | 22.1617 | 302.8572 | 21.5069 | 21.9627 | 27.1006 | 83.1594 | 89.8618 | 22.5115 | 37.7604 | 91.3913 | 717.1926 | 618.0748 | 777.1799 | 783.7881 | 707.9359 |  | 704.6735 | 757.8111 | 810.0599 | 611.7934 | 611.1566 | 775.4718 |  | 429.1249 |  |  | 432.4545 | 586.8709 | 661.2258 | [5 empty] | 21.8499 | 564.855 | 21.7625 | 22.0581 | 399.7982 | 21.3046 | 21.8464 | 468.837 | 604.7503 | 624.6123 |  | 875.2947 | 887.0851 | 513.1264 | 649.1402 | 744.0573 | 572.322 | 641.7625 | 830.1768 | 891.6933 | 591.4852 | 713.944 | 782.8485 | 953.3072 | 926.3145 | 490.3086 | 586.9064 | 628.8748 | 552.2587 | 645.1378 | 769.712 | 879.0033 | 970.7132 | 557.2085 | 612.8164 | 599.4775 | 720.7367 | 51.3338 | 0.025009 | 19.2933 | 2.2462 | -28.3456 | 3.0952 | 7440.18 | -0.05 | 1.4071 | -1.1489 | -16.5719 | -1.5466 | 6.5369 | -33.5546 | -34.0106 | 51.7446 | 79.5123 | 34.6556 | 25.0965 | -3.6697 | 50.2875 | 30.4974
42838.4304 | 874 | 22.8253 | 22.8052 | 22.8038 | 22.7157 | 22.3201 | 21.6465 | 22.6473 | 21.6994 | 22.3062 | 22.3146 | 22.2693 | 21.9159 | 21.1268 | 22.1008 | 21.5241 | 21.7719 | 22.1653 | 21.156 | 26.2077 | 32.5544 | 37.2591 | 85.3117 | 85.8584 | 22.8267 | 35.5439 | 88.4296 | 633.6558 | 621.0195 | 633.9777 | 22.4653 | 37.2557 | 92.2938 | 22.7496 | 38.311 | 89.0874 | 690.5748 | 806.8594 |  | 315.7922 | 863.4946 | 859.8933 | 638.6326 |  | 342.3877 | 589.4414 | 558.6847 | 853.3791 | 889.7132 | 896.1448 | 898.2229 | 37.1842 | 188.856 | 53.2162 | 388.0034 | 61.144 | 51.2429 | 50.5366 | 53.6793 | 32.9878 |  |  | 0.24468 | -0.28394 | -64.7839 | -0.47119 | 8.0215 | -197.821 | -203.2942 | -2.1833 | 9.0587 | 27.3314 | 23.1995 | 0.0017759 | 0.0014292 | 0.00036634 | 23.9553 | 22.012 | 22.1132 | 22.1609 | 21.9616 | 21.2286 | 20.0524 | 22.1326 | 22.3111 | 22.3469 | 22.2836 | 21.8891 | 21.1244 | 22.2073 | 573.6528 | 476.9609 | 438.6008 | 309.6604 | 241.0628 | 559.3169 | 343.5869 | 22.2737 | 22.0734 | 21.9719 | 22.0558 | 23.7962 | 31.1359 | 23.5648 | 73.5816 | 82.8182 | 580.8708 | 533.9973 | 564.726 | 568.0212 | 50.605 | 32.4006 | 744.9675 | 21.9321 | 22.155 | 303.529 | 21.5078 | 21.9501 | 27.193 | 83.2398 | 89.8779 | 22.5093 | 37.9075 | 91.4153 | 715.4391 | 617.8216 | 779.4247 | 786.2236 | 704.8625 |  | 704.6555 | 756.0588 | 809.7189 | 609.6961 | 611.165 | 773.6569 |  | 430.7927 |  |  | 431.8784 | 587.2843 | 660.3667 | [5 empty] | 21.8403 | 564.8071 | 21.7606 | 22.0511 | 401.5918 | 21.3048 | 21.8475 | 468.9156 | 604.4529 | 624.4244 |  | 878.4584 | 886.6461 | 513.2406 | 649.3873 | 744.9037 | 572.2646 | 640.8991 | 825.8515 | 891.3906 | 591.8168 | 713.5994 | 784.0676 | 957.0463 | 926.7246 | 490.3975 | 587.1879 | 628.3789 | 552.4067 | 644.8953 | 770.2491 | 877.6061 | 971.4982 | 557.5749 | 614.1122 | 599.7922 | 722.6826 | 51.1541 | 0.031174 | 19.2996 | 2.2323 | -28.3423 | 3.0952 | 7472.93 | -0.1 | 1.0382 | -1.0906 | -16.4741 | -1.405 | 6.7493 | -33.517 | -33.9775 | 51.8257 | 79.4532 | 34.7154 | 25.6373 | -2.3539 | 50.3526 | 30.5187
42838.4304 | 875 | 22.8282 | 22.8131 | 22.8186 | 22.7318 | 22.3322 | 21.6549 | 22.661 | 21.7107 | 22.3093 | 22.319 | 22.2848 | 21.9199 | 21.1392 | 22.1074 | 21.5313 | 21.769 | 22.162 | 21.1571 | 26.2889 | 32.6612 | 37.6201 | 85.3877 | 85.901 | 22.847 | 35.6549 | 88.4444 | 634.0798 | 620.0292 | 634.9442 | 22.4574 | 37.4183 | 92.3203 | 22.7604 | 38.4634 | 89.0934 | 690.5374 | 812.8953 |  | 316.3787 | 872.3599 | 867.1326 | 637.2982 |  | 343.1492 | 590.4661 | 557.065 | 853.7351 | 887.5878 | 894.332 | 897.9645 | 37.3327 | 189.5734 | 53.0702 | 389.2342 | 61.5403 | 51.2294 | 50.4432 | 53.6937 | 33.0514 |  |  | -0.10162 | -0.33716 | -63.0747 | -0.27603 | 8.0465 | -197.8374 | -203.1727 | -1.4302 | 8.9665 | 26.8199 | 24.3656 | 0.0017331 | 0.0012797 | 0.00034499 | 23.978 | 22.0185 | 22.1233 | 22.1587 | 21.9728 | 21.2406 | 20.0603 | 22.1438 | 22.315 | 22.3553 | 22.2922 | 21.8953 | 21.128 | 22.2188 | 549.6803 | 450.1187 | 425.6944 | 307.1742 | 238.4439 | 560.318 | 344.7589 | 22.2817 | 22.0687 | 21.987 | 22.0567 | 23.8595 | 31.2262 | 23.5879 | 73.7259 | 82.8789 | 581.0391 | 541.6004 | 564.3243 | 565.1674 | 60.5752 | 33.2653 | 743.8044 | 21.9197 | 22.1445 | 304.7378 | 21.5017 | 21.9563 | 27.2818 | 83.3154 | 89.8916 | 22.5145 | 38.0543 | 91.428 | 715.8388 | 617.9142 | 780.5566 | 787.4807 | 704.7378 |  | 704.7208 | 754.5869 | 809.5349 | 607.5272 | 611.0531 | 772.0185 |  | 432.3608 |  |  | 431.2346 | 587.892 | 660.3231 | [5 empty] | 21.8377 | 564.9157 | 21.761 | 22.0464 | 403.5237 | 21.3053 | 21.8423 | 468.6656 | 604.0028 | 624.3367 |  | 873.6538 | 888.0114 | 513.3937 | 649.7037 | 745.5349 | 572.1948 | 640.0227 | 825.8823 | 889.5582 | 592.2812 | 714.6483 | 784.3045 | 959.4465 | 926.3508 | 490.5987 | 587.4085 | 628.2455 | 552.8949 | 644.8232 | 770.5143 | 877.3941 | 973.9518 | 557.5358 | 614.5897 | 599.8975 | 721.5134 | 50.8187 | 0.035184 | 19.3067 | 2.2141 | -28.3457 | 3.0953 | 7478.67 | -0.1 | -0.66946 | -1.1892 | -16.265 | -1.076 | 6.7545 | -33.4924 | -33.941 | 51.8448 | 79.436 | 34.7549 | 28.5434 | -0.72711 | 50.381 | 30.6264
42838.4304 | 876 | 22.8288 | 22.8083 | 22.8084 | 22.7255 | 22.3325 | 21.6455 | 22.6647 | 21.709 | 22.3068 | 22.3165 | 22.2777 | 21.9255 | 21.1328 | 22.113 | 21.5182 | 21.765 | 22.1669 | 21.1484 | 26.3667 | 32.7811 | 37.9822 | 85.4626 | 85.9537 | 22.8489 | 35.7772 | 88.4598 | 634.16 | 618.5464 | 634.8416 | 22.4611 | 37.5711 | 92.3396 | 22.7736 | 38.5893 | 89.0956 | 690.7013 | 816.3652 |  | 317.0607 | 873.8092 | 868.7861 | 637.1564 |  | 343.8682 | 590.8364 | 555.673 | 856.4788 | 888.0164 | 893.4712 | 896.432 | 37.2475 | 190.197 | 53.2263 | 390.3615 | 61.9796 | 51.2112 | 50.3441 | 53.7092 | 33.1196 |  |  | 0.10011 | -0.4837 | -62.6206 | -0.27472 | 6.5726 | -197.8834 | -203.2988 | -1.9612 | 9.1305 | 27.5248 | 24.3895 | 0.0018366 | 0.0013011 | 0.00033677 | 23.9961 | 22.0251 | 22.1175 | 22.1629 | 21.9644 | 21.2372 | 20.0621 | 22.1391 | 22.3121 | 22.3498 | 22.2935 | 21.8967 | 21.1216 | 22.2204 | 555.2033 | 439.9107 | 427.3081 | 302.3036 | 238.7954 | 561.8176 | 345.874 | 22.282 | 22.0698 | 21.9832 | 22.0662 | 23.9101 | 31.3224 | 23.6163 | 73.8539 | 82.9421 | 581.2307 | 540.2401 | 563.9912 | 566.5691 | 63.3257 | 35.4423 | 742.6001 | 21.9227 | 22.1543 | 305.445 | 21.5116 | 21.9622 | 27.3912 | 83.3939 | 89.9196 | 22.534 | 38.2126 | 91.4737 | 717.0534 | 618.4533 | 778.9951 | 785.7294 | 706.7085 |  | 704.8475 | 752.6369 | 809.1158 | 605.9933 | 610.9504 | 769.8069 |  | 436.953 |  |  | 431.4642 | 589.3367 | 661.2349 | [5 empty] | 21.8323 | 565.3158 | 21.7543 | 22.045 | 404.9741 | 21.2953 | 21.8414 | 468.443 | 603.6135 | 624.3866 |  | 870.2556 | 889.3916 | 513.8423 | 649.8027 | 747.3186 | 571.8097 | 640.5107 | 823.7098 | 891.5126 | 592.7203 | 715.0167 | 789.738 | 958.8254 | 928.0715 | 490.5167 | 587.4257 | 628.6628 | 553.3732 | 644.883 | 771.0179 | 879.377 | 975.5775 | 557.3435 | 616.1396 | 600.0109 | 719.5481 | 50.6488 | 0.041925 | 19.3143 | 2.196 | -28.3603 | 3.0953 | 7506.08 | -0.1 | 0.66443 | -1.4247 | -16.2099 | -1.0737 | 6.1024 | -33.4839 | -33.939 | 51.8204 | 79.358 | 34.7786 | 28.2938 | -0.72269 | 50.4228 | 30.6199
42838.4304 | 877 | 22.8238 | 22.8096 | 22.81 | 22.727 | 22.324 | 21.65 | 22.6701 | 21.7057 | 22.3122 | 22.3207 | 22.271 | 21.9226 | 21.137 | 22.1174 | 21.5186 | 21.7694 | 22.1729 | 21.1572 | 26.4459 | 32.8992 | 38.3687 | 85.5304 | 85.9992 | 22.8632 | 35.9026 | 88.4847 | 635.2435 | 618.2666 | 636.4827 | 22.4625 | 37.7088 | 92.3437 | 22.7749 | 38.7268 | 89.0923 | 691.0063 | 811.4214 |  | 317.7168 | 867.5381 | 864.693 | 638.2217 |  | 344.5846 | 591.4774 | 555.3884 | 852.5316 | 887.79 | 892.9569 | 893.7769 | 36.2557 | 190.8421 | 52.8962 | 391.414 | 62.3357 | 51.2235 | 50.2542 | 53.7451 | 33.1846 |  |  | -0.005026 | 0.024903 | -61.3938 | -0.73141 | 6.6383 | -197.9104 | -203.2207 | -1.8961 | 8.8273 | 27.0438 | 23.4655 | 0.0018596 | 0.0012814 | 0.00035649 | 24.0212 | 22.0176 | 22.109 | 22.1596 | 21.9586 | 21.2385 | 20.0581 | 22.1379 | 22.3131 | 22.3481 | 22.2844 | 21.8901 | 21.1229 | 22.2087 | 569.8873 | 449.4617 | 461.9086 | 300.7992 | 232.848 | 564.0409 | 347.681 | 22.2741 | 22.0681 | 21.9816 | 22.0621 | 23.9599 | 31.4064 | 23.6299 | 73.9293 | 82.9988 | 581.5466 | 546.0205 | 564.7665 | 567.6787 | 67.2335 | 56.0162 | 741.4231 | 21.9342 | 22.1572 | 305.8828 | 21.5221 | 21.9644 | 27.5027 | 83.4659 | 89.9486 | 22.548 | 38.3604 | 91.5054 | 718.7547 | 618.8357 | 776.3125 | 783.4344 | 710.205 |  | 705.0178 | 752.9583 | 808.9058 | 607.2631 | 610.9588 | 768.6877 |  | 440.3639 |  |  | 431.6253 | 590.9755 | 663.2183 | [5 empty] | 21.8359 | 565.8066 | 21.7584 | 22.0482 | 406.3482 | 21.3023 | 21.848 | 468.8059 | 603.4083 | 625.1299 |  | 870.2488 | 888.8131 | 514.3481 | 649.9651 | 747.4194 | 571.6899 | 640.7126 | 820.8862 | 889.8327 | 593.2965 | 713.5575 | 792.1074 | 959.0634 | 928.6616 | 490.3287 | 587.4214 | 628.7031 | 553.5404 | 645.3316 | 773.4043 | 883.3229 | 976.7384 | 557.525 | 616.1288 | 600.0218 | 722.5937 | 51.3045 | 0.051179 | 19.3205 | 2.1937 | -28.334 | 3.0953 | 7542.94 | -0.16 | -0.14901 | 0.32338 | -16.0562 | -1.7525 | 6.1315 | -33.4788 | -33.925 | 51.7642 | 79.2829 | 34.7449 | 27.204 | -4.2688 | 50.4636 | 30.6426
42838.4304 | 878 | 22.8228 | 22.8049 | 22.7952 | 22.7159 | 22.3143 | 21.6438 | 22.6597 | 21.6983 | 22.3049 | 22.3082 | 22.2714 | 21.9144 | 21.1328 | 22.1093 | 21.5288 | 21.7918 | 22.1752 | 21.1719 | 26.5555 | 33.0314 | 38.8021 | 85.6378 | 86.0747 | 22.8889 | 36.0492 | 88.515 | 636.8688 | 618.1491 | 638.2855 | 22.4794 | 37.8589 | 92.3551 | 22.7881 | 38.8736 | 89.0922 | 691.1882 | 803.0986 |  | 318.3594 | 850.6295 | 850.8388 | 639.3035 |  | 345.3209 | 592.4277 | 555.365 | 846.929 | 888.469 | 893.2615 | 893.1825 | 35.1478 | 191.5165 | 51.6489 | 392.4417 | 62.6075 | 51.2345 | 50.1551 | 53.7852 | 33.2402 |  |  | 0.40041 | 0.94552 | -60.4311 | -0.52705 | 7.0247 | -197.8591 | -203.2896 | -1.3967 | 8.435 | 26.9437 | 23.5151 | 0.001743 | 0.0012206 | 0.00036634 | 24.05 | 22.0202 | 22.1111 | 22.1555 | 21.9619 | 21.2352 | 20.0625 | 22.1396 | 22.3066 | 22.3533 | 22.2839 | 21.8912 | 21.1187 | 22.204 | 584.8965 | 514.5886 | 554.7694 | 315.5347 | 230.8008 | 566.3634 | 350.8458 | 22.2827 | 22.0697 | 21.9893 | 22.0586 | 24.0129 | 31.496 | 23.652 | 74.0187 | 83.0584 | 581.7392 | 541.0981 | 565.1269 | 567.9822 | 66.3732 | 45.6469 | 741.4232 | 21.9374 | 22.1599 | 306.1914 | 21.5185 | 21.9712 | 27.5993 | 83.5473 | 89.9783 | 22.554 | 38.5174 | 91.5316 | 720.0436 | 618.8995 | 774.3687 | 781.7438 | 712.5038 |  | 705.437 | 755.5544 | 808.7739 | 602.7186 | 610.7647 | 769.2286 |  | 441.1521 |  |  | 432.1465 | 592.8566 | 664.9893 | [5 empty] | 21.8461 | 564.7084 | 21.7649 | 22.0481 | 405.5194 | 21.308 | 21.8511 | 468.7436 | 603.8129 | 625.8711 |  | 874.2573 | 887.3605 | 514.9267 | 650.1237 | 748.0881 | 571.7409 | 640.396 | 822.7779 | 890.859 | 593.9411 | 712.0456 | 796.3648 | 955.4044 | 928.5254 | 490.4326 | 587.5158 | 629.2775 | 553.8313 | 645.619 | 772.0944 | 885.3595 | 973.898 | 557.3942 | 617.8117 | 600.1156 | 721.4321 | 51.3932 | 0.055785 | 19.3275 | 2.1938 | -28.3583 | 3.0953 | 7609.33 | -0.08 | 1.3313 | 1.9937 | -15.9386 | -1.4885 | 6.3082 | -33.4789 | -33.9352 | 51.801 | 79.1692 | 34.8353 | 26.1047 | -14.0619 | 50.4756 | 30.6668
42838.4305 | 879 | 22.8196 | 22.8027 | 22.7989 | 22.7153 | 22.3152 | 21.6454 | 22.6558 | 21.6939 | 22.3054 | 22.3073 | 22.2705 | 21.9105 | 21.1258 | 22.1039 | 21.5281 | 21.7698 | 22.1806 | 21.158 | 26.6329 | 33.1331 | 39.2244 | 85.7247 | 86.1302 | 22.8901 | 36.1694 | 88.522 | 635.1276 | 619.2589 | 635.4145 | 22.4861 | 38.0071 | 92.3685 | 22.7978 | 39.0025 | 89.083 | 691.4802 | 801.1049 |  | 318.9882 | 832.9897 | 835.4411 | 641.5642 |  | 345.997 | 593.833 | 555.0331 | 852.687 | 890.2664 | 895.9359 | 894.1351 | 35.022 | 192.1649 | 50.8471 | 393.5055 | 63.075 | 51.2423 | 50.057 | 53.8043 | 33.3078 |  |  | 0.51344 | 0.33506 | -59.7806 | 0.03347 | 4.9272 | -196.1066 | -203.3048 | -1.8166 | 8.9011 | 26.916 | 23.9251 | 0.0017972 | 0.0013504 | 0.00035813 | 24.0794 | 22.0212 | 22.1173 | 22.1599 | 21.9592 | 21.2304 | 20.0601 | 22.142 | 22.3039 | 22.3575 | 22.2927 | 21.8942 | 21.1255 | 22.2096 | 608.0266 | 522.639 | 543.2701 | 320.4043 | 226.6289 | 569.4212 | 353.4474 | 22.2741 | 22.0701 | 21.9939 | 22.0595 | 24.0545 | 31.5813 | 23.6635 | 74.1055 | 83.1122 | 582.0627 | 541.3553 | 566.614 | 570.6707 | 67.7523 | 35.3295 | 742.6426 | 21.9319 | 22.1512 | 306.4526 | 21.5147 | 21.9664 | 27.6942 | 83.6252 | 89.9993 | 22.5571 | 38.6565 | 91.5653 | 721.2441 | 620.7627 | 774.1564 | 781.6844 | 719.9339 |  | 706.0761 | 759.4444 | 808.8108 | 603.3319 | 610.6773 | 769.4324 |  | 442.3622 |  |  | 433.8794 | 594.8196 | 670.2324 | [5 empty] | 21.8484 | 564.6229 | 21.7575 | 22.0565 | 406.3301 | 21.3066 | 21.8491 | 469.0257 | 604.1716 | 626.9407 |  | 873.9374 | 884.8705 | 515.5247 | 649.3939 | 750.0999 | 571.925 | 640.2482 | 823.9056 | 889.083 | 594.592 | 710.2291 | 794.7407 | 960.2094 | 926.6964 | 490.3317 | 587.4389 | 628.734 | 554.1301 | 646.137 | 772.6732 | 884.74 | 973.6166 | 557.5387 | 617.8503 | 599.9925 | 725.2266 | 53.5808 | 0.05693 | 19.3378 | 2.195 | -28.479 | 3.0953 | 7693.02 | -0.03 | 1.5052 | 1.1878 | -15.8654 | 0.37541 | 5.2892 | -33.3685 | -33.9754 | 51.7483 | 79.0727 | 34.8022 | 24.2871 | -12.3509 | 50.4803 | 30.6469
42838.4305 | 880 | 22.821 | 22.8103 | 22.8106 | 22.7267 | 22.3284 | 21.6479 | 22.6612 | 21.7077 | 22.307 | 22.3222 | 22.2801 | 21.92 | 21.128 | 22.1177 | 21.515 | 21.771 | 22.176 | 21.1555 | 26.7103 | 33.247 | 39.6903 | 85.8097 | 86.1703 | 22.891 | 36.2853 | 88.5325 | 636.3118 | 621.4831 | 636.4334 | 22.4871 | 38.1552 | 92.3949 | 22.8002 | 39.1403 | 89.0777 | 691.8819 | 795.9526 |  | 319.6302 | 827.7523 | 830.7572 | 643.9693 |  | 346.6366 | 595.6215 | 556.624 | 857.8464 | 890.852 | 898.0934 | 890.5889 | 35.2736 | 192.9506 | 49.6073 | 394.712 | 63.3988 | 51.2682 | 49.9644 | 53.8218 | 33.3994 |  |  | 0.19079 | 0.31469 | -58.994 | -0.65125 | 6.4136 | -180.5599 | -203.2588 | -1.5347 | 9.0241 | 27.9734 | 24.3947 | 0.0017299 | 0.0012239 | 0.00035977 | 24.0987 | 22.0192 | 22.1135 | 22.1579 | 21.9607 | 21.2334 | 20.0538 | 22.14 | 22.3108 | 22.3454 | 22.2894 | 21.893 | 21.1219 | 22.2109 | 603.2961 | 501.752 | 497.4526 | 323.6585 | 229.2624 | 571.6748 | 355.2186 | 22.2685 | 22.0685 | 21.9995 | 22.0682 | 24.1245 | 31.6801 | 23.6947 | 74.279 | 83.1909 | 582.3007 | 541.9781 | 566.7513 | 567.6622 | 71.4458 | 44.3667 | 743.986 | 21.9475 | 22.1478 | 306.5068 | 21.517 | 21.9673 | 27.811 | 83.6987 | 90.0248 | 22.5698 | 38.813 | 91.5989 | 721.0287 | 623.9256 | 774.5424 | 781.8517 | 718.3791 |  | 706.6565 | 760.8532 | 808.8489 | 606.1833 | 610.743 | 768.8265 |  | 443.9579 |  |  | 433.9629 | 596.0256 | 671.6433 | [5 empty] | 21.8405 | 566.153 | 21.7685 | 22.0475 | 405.5082 | 21.2971 | 21.8612 | 469.1796 | 603.9333 | 626.0802 |  | 875.864 | 884.475 | 515.7895 | 649.2196 | 751.5281 | 572.0699 | 639.7619 | 822.9592 | 886.8873 | 595.4003 | 709.8172 | 793.5941 | 962.4328 | 925.793 | 490.0941 | 587.5028 | 628.8504 | 554.2596 | 645.9835 | 773.3329 | 880.5137 | 973.8697 | 557.6035 | 616.5225 | 599.4916 | 723.0067 | 53.601 | 0.059549 | 19.3484 | 2.1949 | -28.2984 | 3.0953 | 7714.32 | 0.03 | 0.91806 | 1.1523 | -15.777 | -1.6576 | 6.0401 | -32.048 | -34.0028 | 51.9313 | 79.0456 | 34.7351 | 25.37 | -6.964 | 50.5065 | 30.7709
42838.4305 | 881 | 22.8215 | 22.8072 | 22.8076 | 22.7208 | 22.3311 | 21.6474 | 22.6662 | 21.703 | 22.3065 | 22.3195 | 22.2835 | 21.9226 | 21.1313 | 22.1203 | 21.5197 | 21.7756 | 22.1804 | 21.164 | 26.8028 | 33.3643 | 40.2313 | 85.9048 | 86.2327 | 22.9118 | 36.4192 | 88.5546 | 635.7552 | 623.9872 | 635.7818 | 22.4918 | 38.2975 | 92.4191 | 22.8137 | 39.2711 | 89.0731 | 692.3887 | 794.925 |  | 320.3097 | 821.2383 | 824.8027 | 646.8678 |  | 347.1208 | 596.6274 | 557.0541 | 858.4877 | 891.4905 | 899.9606 | 889.4535 | 35.9621 | 193.6284 | 48.676 | 395.9914 | 63.7844 | 51.3124 | 49.8744 | 53.8102 | 33.4549 |  |  | 0.41159 | 0.31075 | -58.6155 | -0.59473 | 6.4714 | -161.3268 | -203.379 | -1.6543 | 9.3504 | 27.6037 | 23.9515 | 0.001605 | 0.0012255 | 0.00038441 | 24.1185 | 22.0194 | 22.1134 | 22.1636 | 21.9571 | 21.2387 | 20.0553 | 22.1412 | 22.3136 | 22.3488 | 22.2897 | 21.8958 | 21.1243 | 22.2096 | 611.4772 | 498.8732 | 497.804 | 325.0517 | 237.3785 | 574.5705 | 357.2899 | 22.2641 | 22.0656 | 21.9989 | 22.0598 | 24.184 | 31.768 | 23.7104 | 74.4155 | 83.2494 | 582.3548 | 540.3743 | 565.7772 | 564.5588 | 73.6631 | 45.1275 | 744.2898 | 21.9408 | 22.145 | 306.7029 | 21.5043 | 21.9651 | 27.9127 | 83.7645 | 90.0572 | 22.5744 | 38.9709 | 91.6244 | 721.1741 | 627.6776 | 771.8805 | 778.8526 | 721.259 |  | 707.6587 | 758.804 | 808.4704 | 607.5062 | 610.8888 | 766.4812 |  | 445.3038 |  |  | 433.6152 | 596.2658 | 674.2016 | [5 empty] | 21.8346 | 568.222 | 21.7634 | 22.0381 | 404.3226 | 21.3018 | 21.8377 | 469.3654 | 604.1524 | 625.0478 |  | 872.7106 | 882.7818 | 516.1783 | 648.9993 | 752.2497 | 572.3706 | 638.7901 | 824.6142 | 888.7001 | 596.3006 | 710.3791 | 795.9719 | 962.0462 | 926.6583 | 490.6961 | 587.4748 | 630.7301 | 554.5166 | 646.038 | 772.9824 | 881.3745 | 973.1792 | 557.3738 | 615.3945 | 599.6084 | 721.2663 | 51.2928 | 0.060666 | 19.3571 | 2.1948 | -28.3635 | 3.0953 | 7717.36 | -0.11 | 1.3479 | 1.1457 | -15.7354 | -1.585 | 6.0721 | -30.3172 | -34.04 | 52.0933 | 78.9833 | 34.7252 | 25.1808 | -6.6558 | 50.5435 | 30.8663
42838.4305 | 882 | 22.8194 | 22.8071 | 22.8024 | 22.7059 | 22.3236 | 21.6419 | 22.6565 | 21.6962 | 22.3149 | 22.3173 | 22.269 | 21.9215 | 21.1318 | 22.1019 | 21.515 | 21.7784 | 22.1826 | 21.1715 | 26.8897 | 33.4839 | 40.8273 | 85.9973 | 86.3025 | 22.9217 | 36.5462 | 88.5691 | 634.8864 | 627.1482 | 635.094 | 22.4891 | 38.4576 | 92.4338 | 22.8283 | 39.4059 | 89.0709 | 692.8998 | 809.0275 |  | 321.0351 | 812.248 | 816.7974 | 649.0519 |  | 348.0074 | 597.1608 | 562.6008 | 860.9713 | 890.5703 | 897.9314 | 886.4343 | 36.4591 | 194.3639 | 48.0886 | 397.3547 | 64.0004 | 51.3358 | 49.7797 | 53.8041 | 33.4942 |  |  | 0.11588 | 0.31929 | -57.4879 | -0.37854 | 7.3671 | -138.6307 | -203.4769 | -1.3882 | 8.7659 | 26.6955 | 24.1774 | 0.0016822 | 0.0012419 | 0.00036634 | 24.142 | 22.0181 | 22.1062 | 22.1575 | 21.9523 | 21.2322 | 20.0483 | 22.1394 | 22.3059 | 22.3481 | 22.2873 | 21.8908 | 21.1231 | 22.2024 | 619.2433 | 498.9921 | 502.7386 | 331.1219 | 249.2249 | 577.2834 | 359.3924 | 22.2721 | 22.0712 | 22.0095 | 22.0554 | 24.2325 | 31.8629 | 23.734 | 74.5077 | 83.3068 | 582.3806 | 542.5195 | 564.6373 | 563.0546 | 55.5273 | 39.1384 | 742.9607 | 21.9368 | 22.1453 | 306.9086 | 21.504 | 21.9574 | 28.0113 | 83.8327 | 90.0849 | 22.5825 | 39.1231 | 91.6476 | 720.0763 | 630.3884 | 768.6058 | 775.7545 | 718.7327 |  | 708.3717 | 754.1641 | 807.9601 | 608.3706 | 611.0115 | 764.5278 |  | 446.651 |  |  | 434.2816 | 596.4458 | 675.544 | [5 empty] | 21.8316 | 570.1953 | 21.758 | 22.0384 | 403.9192 | 21.2947 | 21.837 | 469.7286 | 603.8882 | 624.5619 |  | 871.0873 | 881.4939 | 516.932 | 649.4102 | 753.6147 | 572.3699 | 638.1949 | 819.9516 | 890.3266 | 597.146 | 713.4274 | 798.0441 | 964.338 | 926.8593 | 491.3486 | 587.392 | 630.4606 | 555.0337 | 646.6247 | 774.1772 | 880.9438 | 973.4268 | 557.2999 | 615.7519 | 600.2222 | 722.984 | 50.1478 | 0.063523 | 19.3664 | 2.194 | -28.331 | 3.0953 | 7714.15 | -0.01 | 0.71495 | 1.1617 | -15.5881 | -1.2649 | 6.473 | -28.0796 | -34.0187 | 52.336 | 78.9517 | 34.7239 | 24.996 | -6.8504 | 50.6014 | 30.9125
42838.4305 | 883 | 22.8176 | 22.8078 | 22.7945 | 22.7172 | 22.3246 | 21.6443 | 22.6596 | 21.7021 | 22.3064 | 22.3146 | 22.2788 | 21.9136 | 21.132 | 22.1069 | 21.5118 | 21.7755 | 22.1833 | 21.1691 | 26.969 | 33.5972 | 41.4154 | 86.0898 | 86.3638 | 22.926 | 36.6622 | 88.5821 | 635.9095 | 629.0279 | 637.2116 | 22.5003 | 38.6146 | 92.4328 | 22.8395 | 39.553 | 89.0724 | 693.5147 | 816.4155 |  | 321.7311 | 804.7324 | 809.4025 | 652.0004 |  | 348.7926 | 597.7818 | 567.8501 | 865.3606 | 890.879 | 896.7886 | 887.2623 | 36.3808 | 195.1282 | 48.6917 | 398.6909 | 64.2114 | 51.3433 | 49.7 | 53.8013 | 33.5642 |  |  | 0.21642 | 0.064331 | -57.0812 | -0.39037 | 7.3289 | -116.5917 | -203.5512 | -1.7779 | 8.9696 | 27.1121 | 24.5411 | 0.0015919 | 0.0010908 | 0.00033677 | 24.1661 | 22.0256 | 22.11 | 22.1585 | 21.9601 | 21.2335 | 20.0546 | 22.1409 | 22.3108 | 22.346 | 22.2877 | 21.8947 | 21.126 | 22.2075 | 610.3418 | 492.8402 | 491.3876 | 323.0375 | 242.7122 | 579.0714 | 361.0419 | 22.2756 | 22.078 | 22.0142 | 22.0675 | 24.2881 | 31.9511 | 23.7591 | 74.5939 | 83.3685 | 582.4188 | 543.2049 | 563.5899 | 562.6848 | 68.8924 | 34.6364 | 740.5048 | 21.9333 | 22.1499 | 307.2323 | 21.5084 | 21.9609 | 28.117 | 83.8965 | 90.1102 | 22.5946 | 39.2794 | 91.6686 | 718.4525 | 631.5917 | 766.5487 | 773.8408 | 715.7923 |  | 708.7789 | 749.9717 | 807.3127 | 608.9359 | 611.1289 | 762.0976 |  | 447.7734 |  |  | 435.5732 | 595.6902 | 674.4821 | [5 empty] | 21.8352 | 571.5715 | 21.764 | 22.0423 | 404.2458 | 21.302 | 21.8421 | 470.4646 | 603.4019 | 624.1689 |  | 866.3436 | 881.5171 | 517.558 | 649.8834 | 755.3093 | 572.3751 | 638.0979 | 822.7052 | 887.5515 | 597.37 | 718.2277 | 801.2894 | 964.907 | 928.517 | 491.7375 | 587.2506 | 630.3566 | 555.6366 | 647.6057 | 775.3097 | 879.9545 | 973.8215 | 557.4798 | 617.2985 | 601.005 | 723.4991 | 50.1904 | 0.063376 | 19.378 | 2.1983 | -28.3285 | 3.0953 | 7733.09 | -0.16 | 0.97819 | 0.52164 | -15.5384 | -1.285 | 6.4531 | -25.7384 | -34.0083 | 52.5164 | 78.8648 | 34.7298 | 26.4339 | -5.3108 | 50.6624 | 30.9292
42838.4305 | 884 | 22.8166 | 22.8059 | 22.7997 | 22.7125 | 22.3225 | 21.6365 | 22.6572 | 21.6943 | 22.3054 | 22.3013 | 22.2765 | 21.9138 | 21.1296 | 22.1058 | 21.5207 | 21.779 | 22.1944 | 21.1772 | 27.0594 | 33.7167 | 41.977 | 86.1809 | 86.4319 | 22.9475 | 36.7916 | 88.6066 | 637.5113 | 632.0365 | 639.2955 | 22.5015 | 38.7476 | 92.4345 | 22.8498 | 39.6829 | 89.0723 | 694.2111 | 821.313 |  | 322.3302 | 795.2654 | 800.6986 | 654.4623 |  | 349.9838 | 599.3617 | 567.0138 | 868.0753 | 888.794 | 895.4866 | 888.1388 | 36.5463 | 195.812 | 49.3596 | 399.6217 | 64.4452 | 51.3279 | 49.6272 | 53.7918 | 33.6279 |  |  | 0.42275 | -0.4883 | -56.9911 | -0.90883 | 8.1819 | -97.7055 | -203.5939 | -1.8409 | 9.2716 | 28.1267 | 24.3838 | 0.0015574 | 0.001058 | 0.00037291 | 24.1937 | 22.0245 | 22.1134 | 22.1621 | 21.9676 | 21.2374 | 20.0656 | 22.1377 | 22.3144 | 22.3487 | 22.2861 | 21.8939 | 21.128 | 22.2124 | 623.3158 | 499.2032 | 465.9975 | 309.4739 | 234.7823 | 581.3475 | 362.2578 | 22.2739 | 22.0744 | 22.0141 | 22.0661 | 24.3493 | 32.0366 | 23.7764 | 74.6607 | 83.4191 | 582.571 | 546.3623 | 563.4349 | 563.2929 | 61.5443 | 37.0843 | 738.2562 | 21.9392 | 22.1567 | 307.6421 | 21.515 | 21.9645 | 28.2317 | 83.9597 | 90.1356 | 22.61 | 39.4425 | 91.6896 | 715.8502 | 632.2492 | 765.3341 | 773.2678 | 711.4541 |  | 708.9115 | 746.6224 | 806.6388 | 612.5101 | 611.4169 | 759.4277 |  | 448.9383 |  |  | 437.7324 | 594.105 | 671.1355 | [5 empty] | 21.8346 | 572.7918 | 21.7653 | 22.0472 | 404.7171 | 21.2994 | 21.8463 | 470.8887 | 603.0133 | 624.9275 |  | 869.6884 | 880.3644 | 517.8235 | 650.3426 | 756.0564 | 572.3414 | 639.2074 | 824.4936 | 886.472 | 597.3884 | 720.8822 | 806.9068 | 965.4166 | 928.8325 | 492.0206 | 587.3348 | 630.9407 | 556.3133 | 648.7133 | 777.8193 | 878.7145 | 975.1936 | 557.5724 | 618.5518 | 601.7594 | 723.1075 | 49.4766 | 0.054395 | 19.3903 | 2.2054 | -28.3371 | 3.0953 | 7732.88 | -0.09 | 1.3687 | -1.4385 | -15.5402 | -1.9624 | 6.8145 | -23.5487 | -33.993 | 52.6691 | 78.7465 | 34.6837 | 25.566 | -2.2841 | 50.7562 | 30.9382
42838.4305 | 885 | 22.8228 | 22.8076 | 22.8019 | 22.7121 | 22.327 | 21.6462 | 22.6591 | 21.6962 | 22.3077 | 22.3051 | 22.2764 | 21.9149 | 21.1191 | 22.1022 | 21.531 | 21.7872 | 22.206 | 21.1917 | 27.1564 | 33.8319 | 42.4999 | 86.2645 | 86.5042 | 22.9728 | 36.9254 | 88.6345 | 639.9464 | 635.3322 | 642.0757 | 22.5053 | 38.8896 | 92.4436 | 22.8557 | 39.8133 | 89.0747 | 694.8652 | 819.7335 |  | 322.9025 | 795.2644 | 801.1266 | 655.9628 |  | 350.4299 | 600.9619 | 567.0341 | 870.6294 | 892.9431 | 896.8584 | 892.6831 | 36.3415 | 196.7011 | 50.5976 | 400.7764 | 64.8768 | 51.3515 | 49.556 | 53.7847 | 33.6929 |  |  | 0.25782 | 0.62485 | -56.1862 | -0.29772 | 7.2705 | -80.2729 | -203.5584 | -1.1805 | 9.6735 | 29.0887 | 24.819 | 0.0016428 | 0.0012469 | 0.0003532 | 24.2113 | 22.0231 | 22.1149 | 22.1585 | 21.9591 | 21.2369 | 20.0531 | 22.1304 | 22.3083 | 22.353 | 22.2831 | 21.8874 | 21.1229 | 22.2075 | 606.7407 | 483.6011 | 453.9064 | 297.707 | 227.437 | 582.8043 | 363.4443 | 22.2734 | 22.0674 | 22.019 | 22.0705 | 24.4165 | 32.1447 | 23.8077 | 74.738 | 83.4921 | 582.8866 | 548.3496 | 563.0726 | 564.0314 | 53.6443 | 28.1987 | 737.1439 | 21.9533 | 22.1531 | 308.1972 | 21.5139 | 21.9631 | 28.3481 | 84.0315 | 90.17 | 22.6253 | 39.6032 | 91.6898 | 713.9398 | 631.6217 | 764.2709 | 772.6097 | 705.2906 |  | 708.7689 | 746.4339 | 806.2672 | 610.9866 | 611.6133 | 758.4165 |  | 449.9664 |  |  | 438.1017 | 591.6824 | 667.6058 | [5 empty] | 21.8324 | 572.6564 | 21.7575 | 22.0346 | 404.5412 | 21.2972 | 21.8437 | 471.104 | 602.8242 | 626.9826 |  | 869.4619 | 879.7047 | 518.2875 | 650.6012 | 756.3445 | 572.2344 | 640.6381 | 818.907 | 884.8635 | 597.7767 | 722.5803 | 810.2096 | 967.9369 | 928.6384 | 492.9062 | 587.9396 | 632.5195 | 556.9349 | 649.3191 | 781.0041 | 881.286 | 979.1979 | 558.2007 | 619.6515 | 602.5235 | 721.5623 | 50.5692 | 0.057372 | 19.4006 | 2.2082 | -28.3211 | 3.0953 | 7727.96 | -0.02 | 1.0705 | 1.6287 | -15.4442 | -1.1242 | 6.4275 | -21.3573 | -34.01 | 52.8057 | 78.6354 | 34.7623 | 27.7762 | -0.73953 | 50.8671 | 30.9713
42838.4305 | 886 | 22.8227 | 22.8109 | 22.8069 | 22.7164 | 22.3239 | 21.6461 | 22.6631 | 21.7026 | 22.3089 | 22.3107 | 22.2734 | 21.9177 | 21.132 | 22.1095 | 21.5269 | 21.7892 | 22.2095 | 21.1932 | 27.2461 | 33.9532 | 43.024 | 86.3356 | 86.5629 | 22.981 | 37.0559 | 88.6532 | 640.4789 | 638.2565 | 641.7391 | 22.5148 | 39.031 | 92.4634 | 22.8678 | 39.949 | 89.0783 | 695.6276 | 818.8907 |  | 323.6259 | 797.9851 | 803.389 | 655.9137 |  | 351.1523 | 602.7857 | 569.9367 | 874.0488 | 895.0369 | 897.3274 | 896.7421 | 35.8059 | 197.5673 | 52.1518 | 401.9825 | 65.2233 | 51.3732 | 49.4791 | 53.7896 | 33.7372 |  |  | 0.4267 | -0.10783 | -56.0843 | -0.72353 | 6.6028 | -57.9763 | -203.4671 | -0.98078 | 9.5351 | 29.3266 | 24.3633 | 0.0015196 | 0.0011089 | 0.00039098 | 24.2417 | 22.0263 | 22.1145 | 22.1643 | 21.9584 | 21.2249 | 20.0667 | 22.1319 | 22.3031 | 22.3499 | 22.2874 | 21.8914 | 21.1164 | 22.2124 | 573.9849 | 447.2043 | 431.1382 | 290.8869 | 226.5337 | 583.5582 | 364.1625 | 22.2704 | 22.0658 | 22.0199 | 22.0723 | 24.4688 | 32.2249 | 23.8202 | 74.8011 | 83.5386 | 583.3051 | 546.3638 | 562.822 | 568.286 | 61.6428 | 38.7048 | 737.1916 | 21.9502 | 22.1525 | 308.4722 | 21.512 | 21.9631 | 28.4548 | 84.1034 | 90.2065 | 22.6384 | 39.761 | 91.6878 | 714.2034 | 630.0365 | 762.6893 | 771.0377 | 703.0238 |  | 708.6771 | 747.1468 | 806.0223 | 605.9131 | 611.4975 | 758.0959 |  | 451.1105 |  |  | 438.7259 | 589.8496 | 665.7885 | [5 empty] | 21.8307 | 570.6804 | 21.7588 | 22.0343 | 404.1804 | 21.2953 | 21.8365 | 471.0148 | 602.6679 | 629.0389 |  | 864.8978 | 880.4743 | 518.671 | 650.9464 | 757.283 | 572.2472 | 640.8118 | 818.1776 | 884.2516 | 598.1498 | 724.9559 | 815.8373 | 975.008 | 929.7912 | 494.0184 | 588.8978 | 634.0375 | 557.2882 | 650.0478 | 783.1423 | 887.4003 | 985.236 | 559.0244 | 620.45 | 603.357 | 720.275 | 50.3123 | 0.052928 | 19.4096 | 2.2129 | -28.322 | 3.0953 | 7735.44 | -0.06 | 1.3769 | -0.6773 | -15.4463 | -1.7544 | 6.1265 | -18.1541 | -34.0091 | 52.8464 | 78.539 | 34.8819 | 31.6069 | 1.9122 | 51.0467 | 30.9243
42838.4305 | 887 | 22.8235 | 22.8082 | 22.8009 | 22.717 | 22.3264 | 21.6419 | 22.6647 | 21.7001 | 22.3063 | 22.31 | 22.2771 | 21.9148 | 21.1315 | 22.1102 | 21.5246 | 21.7837 | 22.2129 | 21.19 | 27.3304 | 34.0631 | 43.5968 | 86.4121 | 86.6249 | 22.9815 | 37.1757 | 88.6573 | 640.5884 | 640.4506 | 641.4546 | 22.5182 | 39.1651 | 92.4908 | 22.8805 | 40.0867 | 89.0874 | 696.2342 | 819.2098 |  | 324.3331 | 797.3721 | 802.2845 | 655.6217 |  | 352.0755 | 604.3451 | 572.1727 | 876.0935 | 894.5593 | 900.4595 | 898.1657 | 35.1986 | 198.3786 | 53.1834 | 403.1469 | 65.409 | 51.4014 | 49.417 | 53.7722 | 33.7829 |  |  | 0.11917 | 0.10244 | -55.4725 | -0.67753 | 7.0576 | -35.2342 | -203.5302 | -1.1063 | 9.1395 | 28.3009 | 24.9419 | 0.0015163 | 0.0010925 | 0.00034992 | 24.2572 | 22.0158 | 22.1044 | 22.155 | 21.956 | 21.221 | 20.0532 | 22.1326 | 22.298 | 22.3507 | 22.2821 | 21.8812 | 21.1176 | 22.2106 | 556.3937 | 435.4361 | 405.6564 | 298.1667 | 240.6438 | 584.3901 | 365.0209 | 22.2689 | 22.0709 | 22.0249 | 22.0705 | 24.5263 | 32.3132 | 23.8438 | 74.9023 | 83.6025 | 583.7091 | 553.7998 | 561.9783 | 566.7089 | 48.3011 | 25.8507 | 737.7127 | 21.9432 | 22.1513 | 308.7659 | 21.5099 | 21.9603 | 28.5652 | 84.1811 | 90.2385 | 22.6386 | 39.9082 | 91.6984 | 714.2689 | 629.2525 | 762.0717 | 770.5337 | 703.1169 |  | 708.6367 | 747.9322 | 805.8221 | 603.6889 | 611.3806 | 758.942 |  | 452.4593 |  |  | 440.3535 | 589.647 | 665.0367 | [5 empty] | 21.8375 | 568.885 | 21.7641 | 22.0419 | 404.2392 | 21.302 | 21.8419 | 470.8496 | 602.6741 | 630.733 |  | 865.3668 | 880.5912 | 519.1156 | 651.0845 | 757.9909 | 572.4983 | 641.28 | 819.679 | 883.0275 | 598.3309 | 724.4361 | 821.7207 | 980.775 | 933.3762 | 494.9364 | 589.8544 | 633.9319 | 557.5291 | 650.6741 | 784.0969 | 893.7857 | 989.284 | 560.0153 | 620.7679 | 604.0442 | 719.9267 | 49.651 | 0.046973 | 19.4196 | 2.2246 | -28.3366 | 3.0953 | 7762.13 | -0.06 | 0.72756 | 0.66074 | -15.3755 | -1.6992 | 6.3424 | -14.1713 | -34.0599 | 52.834 | 78.4545 | 34.922 | 33.7727 | 4.8893 | 51.1969 | 31.037
42838.4306 | 888 | 22.8272 | 22.805 | 22.7961 | 22.7153 | 22.3219 | 21.6438 | 22.6638 | 21.6979 | 22.308 | 22.3148 | 22.2752 | 21.9244 | 21.1263 | 22.114 | 21.5212 | 21.7826 | 22.2095 | 21.1892 | 27.421 | 34.1784 | 44.2176 | 86.4855 | 86.6887 | 22.9984 | 37.301 | 88.6725 | 640.9432 | 641.6803 | 641.5547 | 22.5227 | 39.305 | 92.5112 | 22.8831 | 40.213 | 89.0916 | 696.7952 | 825.5285 |  | 325.079 | 798.4237 | 802.246 | 656.8993 |  | 353.3068 | 606.2726 | 575.1563 | 874.9511 | 895.8045 | 908.4135 | 901.7579 | 34.8965 | 199.1786 | 53.5919 | 404.4584 | 65.6295 | 51.4115 | 49.3616 | 53.7419 | 33.8541 |  |  | 0.27031 | 0.26541 | -54.8233 | -0.58422 | 7.4439 | -23.4265 | -203.5144 | -1.2311 | 9.292 | 28.2165 | 25.2129 | 0.0015754 | 0.0011812 | 0.00036963 | 24.2851 | 22.0163 | 22.1155 | 22.1551 | 21.9597 | 21.2333 | 20.0605 | 22.1373 | 22.3049 | 22.3462 | 22.288 | 21.8886 | 21.1232 | 22.207 | 553.7494 | 429.0054 | 396.1724 | 299.6863 | 238.8547 | 584.3795 | 365.306 | 22.2725 | 22.0774 | 22.0314 | 22.0734 | 24.5844 | 32.4084 | 23.8667 | 74.9964 | 83.6614 | 583.8991 | 559.036 | 560.7517 | 564.8195 | 59.7222 | 32.0019 | 738.1896 | 21.9391 | 22.1507 | 309.3435 | 21.5097 | 21.9634 | 28.6771 | 84.2562 | 90.2658 | 22.647 | 40.0528 | 91.7115 | 714.1076 | 629.2083 | 763.5281 | 772.7331 | 701.6179 |  | 708.4935 | 749.3533 | 805.8144 | 603.3991 | 611.3707 | 760.07 |  | 454.5032 |  |  | 440.878 | 590.5582 | 664.0275 | [5 empty] | 21.836 | 568.2316 | 21.7689 | 22.0465 | 405.1643 | 21.303 | 21.8406 | 470.8404 | 602.7398 | 631.1187 |  | 864.4752 | 881.7793 | 519.4858 | 651.2844 | 758.8452 | 572.8043 | 640.7433 | 821.3404 | 884.1843 | 598.7118 | 724.0256 | 824.136 | 987.1618 | 937.3246 | 495.5901 | 590.6854 | 634.7983 | 557.8572 | 651.3082 | 783.9972 | 898.8588 | 993.9334 | 561.2113 | 621.0692 | 604.7144 | 719.7051 | 49.5083 | 0.043645 | 19.4306 | 2.2312 | -28.362 | 3.0953 | 7857.32 | -0.1 | 1.0958 | 1.0647 | -15.302 | -1.5796 | 6.5358 | -11.5944 | -34.1738 | 52.841 | 78.4126 | 34.9283 | 34.0638 | 5.9916 | 51.293 | 31.1218
42838.4306 | 889 | 22.817 | 22.8065 | 22.804 | 22.7174 | 22.3277 | 21.6427 | 22.6668 | 21.7074 | 22.3118 | 22.3067 | 22.2751 | 21.9204 | 21.1405 | 22.1046 | 21.5105 | 21.778 | 22.2051 | 21.1874 | 27.5141 | 34.2937 | 44.8438 | 86.5467 | 86.7328 | 23.0057 | 37.4207 | 88.6741 | 640.6536 | 643.8844 | 641.5572 | 22.542 | 39.446 | 92.5184 | 22.9009 | 40.3481 | 89.1095 | 697.407 | 829.4584 |  | 325.3122 | 790.7378 | 794.6685 | 658.6613 |  | 354.1536 | 606.6951 | 574.792 | 875.3441 | 897.9282 | 907.7412 | 902.714 | 35.2864 | 199.8637 | 52.57 | 405.5156 | 65.9301 | 51.4304 | 49.305 | 53.7285 | 33.9018 |  |  | 0.044914 | 0.21941 | -54.5749 | -0.23595 | 7.5366 | -51.231 | -203.4638 | -0.8211 | 9.9087 | 29.0224 | 25.4948 | 0.0015179 | 0.0010563 | 0.00035156 | 24.312 | 22.023 | 22.1178 | 22.1537 | 21.9652 | 21.2416 | 20.0655 | 22.1443 | 22.3123 | 22.3515 | 22.2906 | 21.8857 | 21.1259 | 22.2115 | 553.5906 | 425.9959 | 391.1426 | 296.491 | 239.2758 | 585.0568 | 365.6311 | 22.2597 | 22.0639 | 22.0314 | 22.0736 | 24.6493 | 32.4977 | 23.8887 | 75.084 | 83.7236 | 584.1921 | 560.2474 | 560.6187 | 566.6371 | 60.7146 | 31.4604 | 738.9203 | 21.9401 | 22.1515 | 310.214 | 21.5128 | 21.9675 | 28.7921 | 84.3247 | 90.2821 | 22.664 | 40.2036 | 91.7181 | 714.0953 | 629.349 | 764.5565 | 774.2545 | 701.0048 |  | 708.3915 | 747.8941 | 805.7076 | 603.412 | 611.2931 | 760.2607 |  | 455.7792 |  |  | 440.8113 | 592.0881 | 664.0051 | [5 empty] | 21.8324 | 567.8952 | 21.7662 | 22.0418 | 405.1922 | 21.3039 | 21.8394 | 470.8957 | 602.7209 | 631.1223 |  | 862.9493 | 882.8595 | 519.855 | 652.0081 | 758.356 | 572.6733 | 639.2826 | 818.3323 | 883.0881 | 599.2756 | 723.2372 | 825.7466 | 994.835 | 939.9118 | 496.2595 | 591.3266 | 634.9314 | 558.2258 | 651.966 | 785.4497 | 902.7463 | 997.496 | 561.9688 | 621.4416 | 605.3762 | 718.9843 | 50.864 | 0.040668 | 19.4403 | 2.2348 | -28.3457 | 3.0953 | 7978.37 | -0.15 | 0.44668 | 0.96828 | -15.271 | -1.0041 | 6.5745 | -17.1411 | -34.1598 | 52.8333 | 78.4198 | 34.9136 | 34.2537 | 6.6058 | 51.3878 | 31.1213
42838.4306 | 890 | 22.8277 | 22.8055 | 22.8036 | 22.7238 | 22.3204 | 21.6467 | 22.6763 | 21.7016 | 22.3167 | 22.308 | 22.2777 | 21.9238 | 21.1311 | 22.1099 | 21.5106 | 21.7918 | 22.2223 | 21.1959 | 27.6052 | 34.4131 | 45.5063 | 86.6085 | 86.7801 | 23.0187 | 37.5576 | 88.7021 | 642.7617 | 645.4906 | 643.498 | 22.5327 | 39.5935 | 92.5205 | 22.9093 | 40.4907 | 89.1038 | 698.018 | 809.5179 |  | 325.8867 | 785.2449 | 788.6875 | 660.195 |  | 355.6785 | 607.8772 | 573.8156 | 873.1089 | 895.1801 | 907.908 | 899.8619 | 35.9548 | 200.7332 | 51.1619 | 406.6867 | 66.0951 | 51.4529 | 49.2643 | 53.7404 | 33.9954 |  |  | 0.33076 | 0.74708 | -53.9901 | -0.47317 | 6.501 | -120.2557 | -203.5939 | -0.94792 | 9.6799 | 28.5849 | 24.8504 | 0.001559 | 0.0010711 | 0.00033184 | 24.3422 | 22.0262 | 22.1144 | 22.1525 | 21.9629 | 21.2344 | 20.0526 | 22.1432 | 22.3125 | 22.3502 | 22.2889 | 21.8886 | 21.1203 | 22.2092 | 572.5839 | 436.8965 | 396.5099 | 286.6942 | 232.1624 | 586.5816 | 366.0735 | 22.2678 | 22.0666 | 22.0392 | 22.0698 | 24.7145 | 32.5934 | 23.9181 | 75.182 | 83.7824 | 584.4827 | 560.8705 | 560.8021 | 568.6519 | 65.5875 | 39.5295 | 739.282 | 21.9469 | 22.1518 | 311.1093 | 21.5134 | 21.9692 | 28.9117 | 84.3999 | 90.3146 | 22.6795 | 40.3574 | 91.718 | 714.5228 | 629.024 | 764.4432 | 774.1693 | 699.7459 |  | 708.2781 | 749.2357 | 805.9027 | 603.3019 | 611.1825 | 761.1482 |  | 457.3221 |  |  | 440.5688 | 594.1892 | 663.3646 | [5 empty] | 21.832 | 567.7191 | 21.7674 | 22.0373 | 404.4175 | 21.2991 | 21.8455 | 471.1168 | 602.8088 | 631.9226 |  | 861.9959 | 883.3657 | 520.5819 | 653.119 | 757.81 | 572.7467 | 638.2294 | 824.6066 | 878.4347 | 600.1299 | 722.0318 | 826.1088 | 995.5495 | 942.6999 | 496.3703 | 591.5244 | 635.5871 | 558.7477 | 652.6058 | 784.6787 | 904.1993 | 998.2579 | 562.0576 | 622.1896 | 606.2248 | 718.0565 | 51.009 | 0.038758 | 19.4507 | 2.2405 | -28.3757 | 3.0953 | 8036.11 | -0.1 | 1.2135 | 1.7879 | -15.1991 | -1.4229 | 6.1065 | -26.2637 | -34.1731 | 52.8408 | 78.4435 | 34.8962 | 32.532 | 6.0848 | 51.489 | 31.115
42838.4306 | 891 | 22.8201 | 22.8025 | 22.8033 | 22.7189 | 22.3195 | 21.6529 | 22.6578 | 21.6978 | 22.3168 | 22.3142 | 22.2809 | 21.9189 | 21.1325 | 22.1066 | 21.5237 | 21.7873 | 22.2271 | 21.2033 | 27.6954 | 34.5327 | 46.2208 | 86.6588 | 86.8113 | 23.0306 | 37.6798 | 88.702 | 642.4191 | 647.197 | 642.1891 | 22.547 | 39.7259 | 92.5487 | 22.9237 | 40.6289 | 89.1195 | 698.8689 | 806.2458 |  | 326.6209 | 780.8807 | 784.6222 | 661.6047 |  | 357.0769 | 609.608 | 572.6876 | 873.4694 | 896.0043 | 906.288 | 900.8671 | 36.3416 | 201.5075 | 50.0916 | 407.797 | 66.3294 | 51.4511 | 49.2199 | 53.7329 | 34.0923 |  |  | 0.63566 | 0.64062 | -53.0754 | -0.92066 | 7.2737 | -108.333 | -203.5124 | -1.5236 | 9.553 | 28.5407 | 24.6657 | 0.0015048 | 0.0010957 | 0.0003417 | 24.3551 | 22.0222 | 22.1022 | 22.1492 | 21.954 | 21.2218 | 20.047 | 22.1234 | 22.2945 | 22.3343 | 22.2819 | 21.8796 | 21.107 | 22.2059 | 577.7809 | 447.515 | 408.9071 | 287.3594 | 227.1683 | 588.0865 | 367.1144 | 22.2605 | 22.0636 | 22.0443 | 22.0676 | 24.7701 | 32.6866 | 23.9331 | 75.2917 | 83.8381 | 584.7867 | 555.17 | 561.7931 | 570.2596 | 65.4924 | 35.8008 | 740.3754 | 21.9495 | 22.1562 | 311.7853 | 21.5174 | 21.9681 | 29.0351 | 84.463 | 90.3489 | 22.6879 | 40.5099 | 91.7231 | 716.0878 | 627.8979 | 763.5484 | 773.4156 | 702.7045 |  | 708.4738 | 751.0596 | 806.2604 | 601.4495 | 610.9181 | 760.7 |  | 458.9255 |  |  | 442.1971 | 597.0154 | 664.5542 | [5 empty] | 21.8469 | 567.0642 | 21.7736 | 22.0407 | 404.2897 | 21.3098 | 21.8506 | 471.5024 | 602.7632 | 632.1534 |  | 864.1717 | 885.1587 | 521.7127 | 653.3141 | 758.9563 | 572.9628 | 637.1085 | 822.5511 | 881.7107 | 600.9512 | 720.1114 | 829.8641 | 990.6722 | 944.235 | 496.283 | 591.468 | 636.2829 | 559.2199 | 653.2693 | 786.364 | 905.4866 | 997.4768 | 561.9448 | 622.6742 | 606.8658 | 721.5342 | 53.4272 | 0.037297 | 19.46 | 2.2481 | -28.3319 | 3.0953 | 8029.41 | -0.1 | 1.681 | 1.6573 | -15.0846 | -1.9867 | 6.4548 | -24.9106 | -34.1429 | 52.806 | 78.5048 | 34.8989 | 32.3392 | 4.8848 | 51.6504 | 31.1223
42838.4306 | 892 | 22.8252 | 22.8117 | 22.806 | 22.7264 | 22.3236 | 21.6571 | 22.6625 | 21.7075 | 22.3142 | 22.31 | 22.2832 | 21.9192 | 21.1322 | 22.1112 | 21.5218 | 21.7868 | 22.2213 | 21.2037 | 27.7885 | 34.6526 | 47.0557 | 86.7213 | 86.8555 | 23.046 | 37.8074 | 88.7053 | 643.0385 | 647.7836 | 642.3627 | 22.5521 | 39.8569 | 92.5715 | 22.925 | 40.7593 | 89.1233 | 699.6476 | 813.2479 |  | 327.479 | 782.6758 | 786.0318 | 663.5336 |  | 358.6229 | 610.9305 | 571.5383 | 868.4627 | 898.4832 | 906.0111 | 902.5297 | 36.5629 | 202.2898 | 49.8762 | 409.0954 | 66.5286 | 51.4274 | 49.1738 | 53.7039 | 34.1766 |  |  | 0.14151 | 0.30615 | -52.4124 | -0.92001 | 7.7002 | -105.2952 | -203.5643 | -0.59636 | 9.98 | 30.3162 | 25.5046 | 0.0013422 | 0.0010235 | 0.0003762 | 24.3951 | 22.0345 | 22.1159 | 22.1669 | 21.968 | 21.2329 | 20.0615 | 22.1453 | 22.3032 | 22.3505 | 22.2992 | 21.8971 | 21.1202 | 22.2111 | 613.9052 | 457.7533 | 416.2543 | 284.2483 | 224.005 | 590.3369 | 367.9162 | 22.2742 | 22.0766 | 22.0566 | 22.0784 | 24.8313 | 32.7795 | 23.9661 | 75.3981 | 83.9038 | 585.1484 | 557.0249 | 563.1061 | 571.041 | 66.8228 | 35.631 | 742.0298 | 21.9506 | 22.1566 | 312.4587 | 21.5181 | 21.9705 | 29.1559 | 84.5201 | 90.3835 | 22.7028 | 40.6576 | 91.7305 | 718.1819 | 627.3745 | 763.7308 | 774.3429 | 708.1693 |  | 708.9011 | 751.7225 | 806.5833 | 599.0581 | 610.6082 | 760.4712 |  | 460.1382 |  |  | 443.7769 | 599.3955 | 666.2906 | [5 empty] | 21.8423 | 565.659 | 21.7719 | 22.0369 | 404.2483 | 21.3059 | 21.8429 | 471.9416 | 602.2103 | 631.0528 |  | 862.7985 | 885.1354 | 523.0523 | 653.0014 | 759.9789 | 573.0844 | 635.1711 | 827.6497 | 884.8008 | 601.6717 | 718.8479 | 839.1292 | 989.0992 | 947.4131 | 496.0476 | 591.4855 | 638.5715 | 559.5518 | 653.7684 | 788.857 | 910.2031 | 1002.0059 | 561.9254 | 623.9827 | 607.1328 | 723.5438 | 52.5989 | 0.034152 | 19.4713 | 2.2709 | -28.3326 | 3.0953 | 7955.3 | 0.02 | 0.79322 | 1.1465 | -15.0013 | -1.9875 | 6.6406 | -24.556 | -34.1432 | 52.7578 | 78.5875 | 34.9082 | 28.9027 | 4.2053 | 51.7809 | 31.1625
42838.4306 | 893 | 22.8198 | 22.8065 | 22.8035 | 22.7136 | 22.3211 | 21.6408 | 22.6564 | 21.7007 | 22.3009 | 22.307 | 22.2746 | 21.9177 | 21.1315 | 22.1071 | 21.5195 | 21.7921 | 22.2302 | 21.2151 | 27.8841 | 34.782 | 47.8929 | 86.797 | 86.9097 | 23.0702 | 37.9457 | 88.7127 | 642.6107 | 648.8793 | 641.959 | 22.5554 | 39.9973 | 92.5871 | 22.9425 | 40.8953 | 89.1359 | 700.374 | 814.0363 |  | 328.3493 | 782.2631 | 785.0734 | 665.8427 |  | 360.2986 | 613.1456 | 571.8337 | 860.5705 | 900.0589 | 906.3839 | 903.0001 | 37.1458 | 203.2368 | 51.3594 | 410.8044 | 66.7307 | 51.3809 | 49.145 | 53.6739 | 34.2535 |  |  | 0.23745 | 0.44612 | -51.0521 | -0.66176 | 5.8596 | -105.8235 | -203.5735 | -1.5078 | 9.9132 | 29.8779 | 25.7047 | 0.0013652 | 0.001076 | 0.00036963 | 24.4099 | 22.0289 | 22.1135 | 22.1654 | 21.9625 | 21.2316 | 20.0612 | 22.1396 | 22.308 | 22.3471 | 22.2913 | 21.8918 | 21.1221 | 22.2075 | 609.7954 | 436.5921 | 414.3971 | 280.4631 | 225.5222 | 592.067 | 368.6276 | 22.2695 | 22.0764 | 22.0557 | 22.0761 | 24.8917 | 32.8659 | 23.9893 | 75.5234 | 83.9571 | 585.4789 | 563.4524 | 564.4634 | 571.0822 | 58.6955 | 37.6939 | 743.4935 | 21.9476 | 22.1511 | 313.435 | 21.5078 | 21.9632 | 29.2648 | 84.5687 | 90.4037 | 22.7069 | 40.7957 | 91.7246 | 720.5399 | 628.3319 | 765.0025 | 775.9981 | 718.2602 |  | 709.7966 | 752.1438 | 806.8336 | 597.9147 | 610.356 | 761.0036 |  | 461.3676 |  |  | 445.9003 | 602.9527 | 675.798 | [5 empty] | 21.8444 | 565.1172 | 21.7812 | 22.0521 | 403.7221 | 21.3091 | 21.8456 | 472.4755 | 601.6385 | 629.6397 |  | 859.0758 | 888.01 | 524.156 | 652.8075 | 762.6077 | 573.0819 | 633.3656 | 825.6207 | 890.346 | 602.2921 | 716.8877 | 847.3594 | 995.3867 | 954.407 | 496.1647 | 591.7057 | 639.2078 | 559.6839 | 654.3634 | 786.8299 | 910.5485 | 1006.4449 | 561.9212 | 624.6721 | 607.4749 | 722.1705 | 51.3969 | 0.036033 | 19.4825 | 2.2998 | -28.369 | 3.0954 | 7894.48 | -0.13 | 1.0273 | 1.3857 | -14.8239 | -1.6877 | 5.7937 | -24.6214 | -34.1494 | 52.695 | 78.6542 | 34.8935 | 29.805 | 4.5333 | 51.8887 | 31.2179
42838.4306 | 894 | 22.8202 | 22.8154 | 22.808 | 22.7202 | 22.3261 | 21.6488 | 22.6683 | 21.7047 | 22.3069 | 22.3131 | 22.2757 | 21.9199 | 21.1363 | 22.1067 | 21.5172 | 21.7908 | 22.2292 | 21.2056 | 27.9769 | 34.8861 | 48.7279 | 86.8622 | 86.9458 | 23.0782 | 38.0616 | 88.7212 | 640.7264 | 649.1214 | 640.7567 | 22.5639 | 40.1282 | 92.5994 | 22.9591 | 41.0295 | 89.1495 | 701.5798 | 822.6272 |  | 329.1203 | 780.5533 | 782.8662 | 671.2461 |  | 361.2968 | 615.0534 | 572.1368 | 860.0011 | 898.9417 | 909.0417 | 901.5585 | 37.6497 | 204.0086 | 52.0997 | 412.0877 | 66.9486 | 51.3037 | 49.106 | 53.637 | 34.338 |  |  | 0.19145 | 0.58674 | -50.4772 | -0.56385 | 5.3142 | -98.7503 | -203.5637 | -1.4342 | 9.6106 | 29.0142 | 25.341 | 0.0013684 | 0.0010235 | 0.00035649 | 24.4341 | 22.0211 | 22.1039 | 22.1532 | 21.9504 | 21.2228 | 20.0523 | 22.1369 | 22.304 | 22.3406 | 22.2769 | 21.8743 | 21.1174 | 22.1954 | 600.9091 | 458.8944 | 426.9697 | 277.5179 | 217.6452 | 593.1243 | 369.2486 | 22.2667 | 22.0715 | 22.0657 | 22.0813 | 24.9658 | 32.9651 | 24.0095 | 75.6547 | 84.014 | 585.8459 | 563.6026 | 565.9277 | 571.8954 | 51.1117 | 28.8473 | 745.2658 | 21.9491 | 22.1485 | 314.2901 | 21.5085 | 21.9649 | 29.3825 | 84.6272 | 90.4326 | 22.7146 | 40.9473 | 91.733 | 721.6108 | 629.9362 | 764.7435 | 775.8954 | 716.6977 |  | 710.459 | 754.9888 | 807.6445 | 594.736 | 609.9844 | 763.1341 |  | 462.7073 |  |  | 446.1434 | 604.6751 | 677.3499 | [5 empty] | 21.8451 | 564.4536 | 21.7706 | 22.0478 | 404.1456 | 21.3063 | 21.8298 | 472.6769 | 601.0374 | 630.214 |  | 858.8749 | 890.0564 | 524.8878 | 653.1182 | 764.3679 | 573.0947 | 632.5954 | 828.7669 | 894.5956 | 602.8836 | 716.3719 | 853.252 | 992.838 | 958.3416 | 496.3805 | 591.6791 | 638.43 | 559.9557 | 654.7021 | 787.7133 | 914.9049 | 1008.1596 | 561.7684 | 624.1957 | 608.2942 | 721.7703 | 51.1283 | 0.032024 | 19.4933 | 2.324 | -28.3248 | 3.0954 | 7889.65 | -0.01 | 0.92182 | 1.5909 | -14.7561 | -1.5596 | 5.5237 | -23.8111 | -34.187 | 52.8996 | 78.8296 | 34.9133 | 31.0655 | 3.2426 | 52.0249 | 31.2583
42838.4306 | 895 | 22.8172 | 22.8058 | 22.7953 | 22.7185 | 22.321 | 21.6465 | 22.6614 | 21.6973 | 22.3091 | 22.3092 | 22.2678 | 21.918 | 21.1313 | 22.1057 | 21.5151 | 21.7914 | 22.2394 | 21.22 | 28.0691 | 35.0132 | 49.5968 | 86.9409 | 87.0076 | 23.0911 | 38.1945 | 88.7255 | 640.1853 | 649.9841 | 640.7404 | 22.5671 | 40.2596 | 92.6078 | 22.9669 | 41.1647 | 89.169 | 703.1074 | 820.961 |  | 329.9445 | 777.1504 | 778.8928 | 676.2468 |  | 362.0176 | 616.2927 | 571.7629 | 862.482 | 897.4237 | 910.1786 | 899.4277 | 38.2369 | 204.773 | 52.9033 | 413.3757 | 67.017 | 51.1868 | 49.0717 | 53.5823 | 34.3865 |  |  | 0.20657 | 0.47306 | -49.7721 | -0.7531 | 7.4834 | -90.7598 | -203.5505 | -1.402 | 9.1029 | 28.5042 | 24.8619 | 0.0013257 | 0.00093146 | 0.0003417 | 24.4639 | 22.0271 | 22.1112 | 22.1546 | 21.9576 | 21.2266 | 20.0612 | 22.1342 | 22.3118 | 22.3506 | 22.2884 | 21.8841 | 21.1228 | 22.2032 | 613.0802 | 448.9936 | 404.012 | 287.084 | 222.1841 | 593.87 | 369.1441 | 22.2666 | 22.0725 | 22.0658 | 22.0798 | 25.0286 | 33.0638 | 24.0346 | 75.7887 | 84.0704 | 585.9524 | 555.6579 | 565.9643 | 567.5958 | 56.7671 | 33.4001 | 747.0293 | 21.9512 | 22.1512 | 314.7919 | 21.5086 | 21.962 | 29.5041 | 84.6868 | 90.4719 | 22.7313 | 41.1064 | 91.7506 | 721.7411 | 630.9904 | 763.6155 | 775.1874 | 712.2848 |  | 710.8145 | 755.0546 | 808.2813 | 591.5649 | 609.4724 | 762.9875 |  | 463.9572 |  |  | 446.6064 | 604.353 | 676.1536 | [5 empty] | 21.8328 | 563.6221 | 21.7733 | 22.042 | 404.04 | 21.3028 | 21.8371 | 473.4393 | 600.5682 | 630.6659 |  | 859.7698 | 892.3361 | 525.5794 | 654.0671 | 767.216 | 573.0074 | 633.0143 | 824.643 | 894.7985 | 603.3613 | 722.0486 | 858.6434 | 996.7055 | 961.0307 | 496.0791 | 591.5495 | 637.3828 | 560.3128 | 655.4221 | 788.0109 | 914.5889 | 1008.6449 | 561.5562 | 624.2181 | 608.9717 | 721.785 | 51.2122 | 0.03057 | 19.5039 | 2.3587 | -28.3337 | 3.0953 | 7917.52 | -0.08 | 0.95751 | 1.4295 | -14.6629 | -1.8036 | 6.558 | -22.8384 | -34.2023 | 53.1089 | 79.028 | 34.9073 | 29.9061 | 5.7756 | 52.2501 | 31.396
42838.4306 | 896 | 22.8183 | 22.8071 | 22.8056 | 22.7261 | 22.3254 | 21.6409 | 22.6589 | 21.7031 | 22.3065 | 22.3054 | 22.2694 | 21.9191 | 21.1323 | 22.1018 | 21.5201 | 21.7887 | 22.2462 | 21.2235 | 28.174 | 35.1274 | 50.4958 | 87.0051 | 87.0664 | 23.1031 | 38.3168 | 88.7294 | 639.6014 | 651.0923 | 641.073 | 22.5776 | 40.3879 | 92.607 | 22.9934 | 41.2996 | 89.1908 | 704.631 | 817.3861 |  | 330.8005 | 777.4992 | 779.7709 | 676.4123 |  | 363.1062 | 616.3905 | 574.7143 | 863.3218 | 895.0166 | 909.899 | 897.8304 | 38.5601 | 205.3611 | 53.8808 | 414.4266 | 67.2436 | 51.1097 | 49.0523 | 53.546 | 34.4437 |  |  | 0.19277 | 0.32521 | -49.0959 | -0.90095 | 6.5233 | -81.8335 | -203.5518 | -1.7654 | 10.146 | 29.6077 | 25.0312 | 0.0012732 | 0.00097582 | 0.00035977 | 24.4894 | 22.0228 | 22.1095 | 22.1529 | 21.9585 | 21.2288 | 20.0585 | 22.1271 | 22.3109 | 22.3444 | 22.2816 | 21.8836 | 21.1203 | 22.2053 | 579.7373 | 453.2949 | 401.6229 | 301.1337 | 238.119 | 594.4093 | 369.2378 | 22.2696 | 22.0708 | 22.0707 | 22.0764 | 25.0959 | 33.1612 | 24.0615 | 75.8811 | 84.1165 | 585.8963 | 547.4565 | 564.7369 | 564.3416 | 56.854 | 31.955 | 748.1515 | 21.9484 | 22.1531 | 315.1415 | 21.5064 | 21.9582 | 29.6225 | 84.7411 | 90.5067 | 22.7441 | 41.2534 | 91.7598 | 720.7658 | 631.9285 | 762.3706 | 773.8028 | 709.126 |  | 711.0441 | 752.9739 | 808.4284 | 591.8876 | 609.1074 | 761.0808 |  | 465.118 |  |  | 448.0094 | 603.0717 | 674.5257 | [5 empty] | 21.8363 | 563.597 | 21.7731 | 22.0422 | 404.4596 | 21.3068 | 21.842 | 474.1476 | 600.3873 | 632.1886 |  | 858.1756 | 892.3543 | 526.204 | 653.9054 | 768.3942 | 572.5207 | 633.0706 | 828.6608 | 890.7449 | 603.2298 | 721.2554 | 863.6661 | 997.5121 | 962.9353 | 496.2594 | 591.2248 | 636.3494 | 560.4321 | 656.1714 | 788.9826 | 914.6184 | 1008.1577 | 561.942 | 623.9978 | 609.445 | 722.2392 | 53.1319 | 0.028232 | 19.5151 | 2.3933 | -28.3289 | 3.0954 | 7983.91 | 0.02 | 0.92514 | 1.1853 | -14.5637 | -1.9729 | 6.1221 | -21.6837 | -34.1984 | 53.2526 | 79.1321 | 34.8313 | 33.7505 | 6.0571 | 52.6101 | 31.4768
42838.4307 | 897 | 22.8193 | 22.8072 | 22.8037 | 22.7191 | 22.3309 | 21.6387 | 22.6605 | 21.6933 | 22.3119 | 22.3158 | 22.2655 | 21.9126 | 21.1239 | 22.1112 | 21.5097 | 21.7927 | 22.2555 | 21.2233 | 28.2596 | 35.2429 | 51.4279 | 87.0611 | 87.111 | 23.1092 | 38.4423 | 88.7393 | 639.416 | 651.976 | 640.9925 | 22.5861 | 40.5244 | 92.6002 | 22.9924 | 41.4348 | 89.2015 | 705.7262 | 831.875 |  | 331.537 | 783.5699 | 784.8251 | 673.5888 |  | 363.8687 | 616.3094 | 582.1768 | 864.8713 | 894.8517 | 909.5201 | 893.84 | 38.4188 | 205.9666 | 55.2584 | 415.4807 | 67.3003 | 51.0272 | 49.0204 | 53.4958 | 34.5198 |  |  | 0.029802 | 1.1676 | -47.9045 | -0.81224 | 5.6875 | -51.024 | -203.517 | -1.356 | 9.5435 | 28.5503 | 24.752 | 0.0012929 | 0.00090354 | 0.00036799 | 24.5108 | 22.0217 | 22.1063 | 22.149 | 21.9515 | 21.2171 | 20.0547 | 22.1282 | 22.304 | 22.3395 | 22.2811 | 21.8799 | 21.1118 | 22.1989 | 562.1762 | 448.9072 | 402.4039 | 295.1726 | 249.8314 | 594.8318 | 369.6721 | 22.2642 | 22.0679 | 22.0708 | 22.0689 | 25.1604 | 33.2438 | 24.0795 | 75.9238 | 84.1568 | 585.7989 | 539.9498 | 564.151 | 561.979 | 55.8494 | 37.5491 | 747.4831 | 21.9471 | 22.1505 | 315.8424 | 21.5091 | 21.9588 | 29.7452 | 84.7954 | 90.5368 | 22.7518 | 41.4003 | 91.7641 | 719.1502 | 632.9257 | 760.8421 | 772.0702 | 710.5788 |  | 711.5129 | 745.306 | 807.954 | 594.2326 | 608.9179 | 756.5586 |  | 466.3 |  |  | 450.3303 | 601.6345 | 675.3765 | [5 empty] | 21.8248 | 564.3947 | 21.7768 | 22.0401 | 404.7305 | 21.3058 | 21.8397 | 474.3369 | 600.0132 | 632.678 |  | 857.3474 | 892.017 | 526.6326 | 653.4013 | 768.7601 | 572.3512 | 632.5697 | 829.5859 | 887.7613 | 603.1357 | 719.6042 | 876.2855 | 997.3833 | 963.2243 | 496.1647 | 591.0564 | 636.1826 | 560.308 | 656.4939 | 790.0241 | 915.896 | 1007.9274 | 561.696 | 623.8838 | 609.7131 | 722.651 | 49.6901 | 0.028043 | 19.5268 | 2.4308 | -28.3501 | 3.0954 | 8064.16 | -0.03 | 0.36374 | 2.2459 | -14.3853 | -1.8731 | 5.7156 | -17.1193 | -34.19 | 53.3267 | 79.1959 | 34.7314 | 35.8113 | 6.0447 | 52.9515 | 31.5257
42838.4307 | 898 | 22.8172 | 22.8032 | 22.8035 | 22.7104 | 22.321 | 21.6398 | 22.6578 | 21.6964 | 22.3075 | 22.3148 | 22.2746 | 21.9174 | 21.1307 | 22.1016 | 21.5176 | 21.7929 | 22.2538 | 21.2298 | 28.3597 | 35.3637 | 52.3771 | 87.1315 | 87.1621 | 23.1321 | 38.5809 | 88.749 | 638.9532 | 653.3743 | 640.255 | 22.5909 | 40.6617 | 92.5977 | 23.0025 | 41.5688 | 89.2104 | 706.8526 | 831.4196 |  | 332.4377 | 784.7485 | 785.0746 | 675.0928 |  | 364.551 | 616.0731 | 582.6393 | 861.0583 | 895.4839 | 908.2823 | 890.8559 | 37.6608 | 206.6295 | 56.2751 | 416.6206 | 67.4779 | 50.9692 | 48.9938 | 53.4733 | 34.5957 |  |  | 0.58375 | 1.1177 | -47.5306 | -0.40943 | 5.4371 | -20.1067 | -203.4835 | -1.3501 | 9.1805 | 27.9367 | 24.4249 | 0.0012288 | 0.00091996 | 0.00033677 | 24.5448 | 22.0343 | 22.1073 | 22.1581 | 21.9614 | 21.225 | 20.0589 | 22.1321 | 22.3084 | 22.3414 | 22.2936 | 21.8877 | 21.1227 | 22.203 | 556.7032 | 463.7611 | 416.3399 | 309.3624 | 248.2326 | 594.7341 | 370.2625 | 22.2675 | 22.0757 | 22.0815 | 22.0841 | 25.2289 | 33.3453 | 24.1039 | 76.012 | 84.2074 | 585.6794 | 530.1801 | 564.8687 | 561.0852 | 59.4416 | 31.9713 | 744.7485 | 21.9434 | 22.15 | 317.0052 | 21.508 | 21.9574 | 29.8638 | 84.8529 | 90.571 | 22.7652 | 41.5479 | 91.7621 | 717.5012 | 634.1596 | 759.7724 | 770.9041 | 710.2511 |  | 712.0685 | 741.3544 | 807.2897 | 594.2856 | 608.6554 | 752.4512 |  | 467.6959 |  |  | 452.6654 | 600.3735 | 676.4679 | [5 empty] | 21.8261 | 565.2172 | 21.7791 | 22.0384 | 404.4563 | 21.3066 | 21.8442 | 474.6633 | 599.7281 | 631.4365 |  | 858.6347 | 891.8179 | 526.8215 | 652.9277 | 770.5969 | 572.5242 | 632.2492 | 827.4642 | 890.5586 | 602.9513 | 718.4203 | 881.7724 | 994.8089 | 964.1708 | 496.5792 | 591.0565 | 635.8462 | 560.224 | 657.0015 | 790.8352 | 914.6771 | 1006.2287 | 561.8279 | 624.3594 | 610.1054 | 722.4705 | 50.1251 | 0.027986 | 19.5373 | 2.4775 | -28.3234 | 3.0954 | 8149.96 | -0.02 | 1.6092 | 2.197 | -14.3271 | -1.3297 | 5.5854 | -10.7409 | -34.1693 | 53.4716 | 79.097 | 34.6818 | 36.3941 | 4.5975 | 53.181 | 31.53
42838.4307 | 899 | 22.8225 | 22.8085 | 22.8092 | 22.7222 | 22.3335 | 21.6516 | 22.6676 | 21.7058 | 22.311 | 22.3232 | 22.2783 | 21.9232 | 21.1323 | 22.1158 | 21.5208 | 21.7976 | 22.2577 | 21.2323 | 28.4604 | 35.4828 | 53.3392 | 87.201 | 87.2014 | 23.143 | 38.7083 | 88.7541 | 638.3113 | 654.2785 | 639.1284 | 22.5962 | 40.8014 | 92.5976 | 23.0195 | 41.6974 | 89.226 | 707.8328 | 831.3199 |  | 333.1535 | 783.5642 | 782.6788 | 674.7657 |  | 365.2314 | 616.887 | 581.9629 | 861.7339 | 896.1957 | 910.6083 | 888.2632 | 37.5283 | 207.1968 | 56.8394 | 417.4922 | 67.6923 | 50.8856 | 48.9671 | 53.4309 | 34.6701 |  |  | 0.53841 | 1.1624 | -46.9971 | -0.75113 | 7.3033 | 14.9577 | -203.4382 | -1.5433 | 10.035 | 30.2491 | 24.7829 | 0.0013717 | 0.00097746 | 0.0003417 | 24.5694 | 22.0356 | 22.1123 | 22.1475 | 21.9646 | 21.2256 | 20.0591 | 22.1331 | 22.311 | 22.3406 | 22.2854 | 21.8922 | 21.1228 | 22.2108 | 569.5484 | 466.7472 | 404.6927 | 311.1094 | 249.6651 | 595.9577 | 370.3483 | 22.2676 | 22.0739 | 22.0963 | 22.0829 | 25.3163 | 33.453 | 24.1407 | 76.1551 | 84.2628 | 585.6716 | 532.9851 | 565.8839 | 562.683 | 67.8923 | 41.6995 | 742.5524 | 21.9495 | 22.1537 | 317.4786 | 21.5072 | 21.9618 | 29.9894 | 84.9116 | 90.6172 | 22.7825 | 41.6966 | 91.7675 | 717.6348 | 634.872 | 760.48 | 772.5723 | 707.946 |  | 712.2604 | 739.9526 | 806.8681 | 595.1136 | 608.4646 | 750.6584 |  | 468.8559 |  |  | 454.1475 | 599.7569 | 674.9076 | [5 empty] | 21.8363 | 565.87 | 21.78 | 22.0462 | 403.8864 | 21.3108 | 21.8472 | 474.7912 | 599.7931 | 630.816 |  | 858.2653 | 891.7389 | 526.7705 | 652.575 | 771.7497 | 572.7167 | 632.2872 | 825.154 | 896.6131 | 602.936 | 719.203 | 882.9066 | 994.113 | 967.9679 | 496.999 | 591.367 | 634.9439 | 560.2977 | 657.4781 | 790.602 | 913.8533 | 1007.6526 | 562.0556 | 624.1477 | 610.3395 | 722.4357 | 50.9723 | 0.031174 | 19.5498 | 2.5362 | -28.3523 | 3.0954 | 8204.76 | -0.08 | 1.5445 | 2.2415 | -14.253 | -1.8019 | 6.4798 | 9.2732 | -34.1991 | 53.5826 | 79.0037 | 34.6238 | 35.2846 | 5.9063 | 53.4269 | 31.4843
42838.4307 | 900 | 22.818 | 22.8027 | 22.8012 | 22.714 | 22.3242 | 21.6413 | 22.6572 | 21.6988 | 22.3012 | 22.3109 | 22.2695 | 21.9108 | 21.1271 | 22.1007 | 21.515 | 21.8008 | 22.2722 | 21.2407 | 28.5578 | 35.607 | 54.2922 | 87.2674 | 87.2331 | 23.1593 | 38.8264 | 88.762 | 638.0045 | 653.822 | 639.0162 | 22.6035 | 40.9397 | 92.6035 | 23.0348 | 41.8273 | 89.2534 | 708.8946 | 830.4271 |  | 334.0886 | 777.3601 | 776.8366 | 681.0517 |  | 365.9221 | 617.3804 | 582.1255 | 866.2933 | 896.8407 | 911.5554 | 890.5524 | 37.7896 | 207.9453 | 56.8634 | 418.628 | 67.786 | 50.8339 | 48.9445 | 53.3951 | 34.7482 |  |  | 0.38596 | 2.0869 | -46.8361 | -0.54873 | 8.3692 | 30.4426 | -203.3803 | -1.0701 | 10.9716 | 32.513 | 24.1647 | 0.0013142 | 0.00090189 | 0.0003532 | 24.6026 | 22.0324 | 22.1156 | 22.1528 | 21.9656 | 21.2291 | 20.0546 | 22.1331 | 22.314 | 22.3468 | 22.2857 | 21.898 | 21.1246 | 22.211 | 610.7564 | 471.2911 | 435.3165 | 314.2058 | 248.4006 | 598.3079 | 371.4247 | 22.2668 | 22.0735 | 22.0834 | 22.0683 | 25.3665 | 33.5403 | 24.1565 | 76.2565 | 84.2972 | 585.5326 | 541.1866 | 564.9759 | 560.2989 | 74.3095 | 51.1138 | 741.8804 | 21.9598 | 22.1576 | 317.5526 | 21.5161 | 21.9641 | 30.1236 | 84.9723 | 90.6619 | 22.7897 | 41.8512 | 91.7857 | 717.6146 | 634.8539 | 762.4142 | 775.7624 | 708.3418 |  | 712.4105 | 739.215 | 806.5627 | 593.3674 | 608.1723 | 749.2864 |  | 469.9471 |  |  | 454.594 | 599.7961 | 673.6606 | [5 empty] | 21.8382 | 565.8615 | 21.7783 | 22.0452 | 404.0479 | 21.3119 | 21.8418 | 474.945 | 599.7401 | 631.2898 |  | 855.9198 | 893.5129 | 526.6333 | 652.3981 | 772.7283 | 572.6355 | 631.8563 | 818.4031 | 897.7765 | 602.9318 | 719.9284 | 889.5874 | 994.6637 | 971.1806 | 497.5816 | 591.5942 | 634.0003 | 560.2118 | 658.2501 | 791.3139 | 917.5272 | 1008.7431 | 562.04 | 623.7681 | 610.4515 | 722.545 | 51.5149 | 0.029875 | 19.5627 | 2.6143 | -28.3733 | 3.0954 | 8273.02 | 0.02 | 1.3076 | 3.0043 | -14.2325 | -1.5405 | 6.9393 | 13.2347 | -34.2079 | 53.6084 | 78.9284 | 34.6188 | 31.3184 | 2.6885 | 53.5095 | 31.5267
42838.4307 | 901 | 22.8221 | 22.8102 | 22.8039 | 22.7177 | 22.3293 | 21.6454 | 22.6624 | 21.7038 | 22.3142 | 22.3187 | 22.2783 | 21.9171 | 21.1312 | 22.1076 | 21.517 | 21.8042 | 22.2761 | 21.2463 | 28.6531 | 35.7242 | 55.1795 | 87.3375 | 87.2706 | 23.174 | 38.958 | 88.7696 | 638.4456 | 654.0044 | 639.034 | 22.6145 | 41.0878 | 92.6042 | 23.0464 | 41.9543 | 89.2763 | 710.3644 | 825.5968 |  | 334.8316 | 771.5936 | 771.3643 | 682.6999 |  | 366.7352 | 617.4126 | 581.9869 | 867.3543 | 895.8184 | 912.829 | 890.7638 | 38.2518 | 208.8138 | 56.1987 | 419.8073 | 67.9092 | 50.797 | 48.9337 | 53.3634 | 34.8196 |  |  | 0.77957 | -1.7585 | -46.2217 | -0.53297 | 8.4907 | 49.1829 | -203.3586 | -1.9343 | 10.0236 | 29.8165 | 24.0944 | 0.0011762 | 0.00088875 | 0.00034992 | 24.6376 | 22.0414 | 22.1181 | 22.1651 | 21.9637 | 21.2463 | 20.0575 | 22.1488 | 22.3149 | 22.3538 | 22.2992 | 21.8987 | 21.1268 | 22.2259 | 617.5359 | 490.9796 | 474.8487 | 325.5172 | 256.0014 | 601.1222 | 373.6616 | 22.2615 | 22.0799 | 22.0901 | 22.0728 | 25.43 | 33.6312 | 24.1767 | 76.321 | 84.3422 | 585.3314 | 553.4655 | 563.6679 | 558.5383 | 57.972 | 35.2625 | 741.278 | 21.9627 | 22.1553 | 317.769 | 21.5163 | 21.9616 | 30.2545 | 85.0268 | 90.7033 | 22.7981 | 42.0112 | 91.7999 | 716.2673 | 635.8031 | 765.1002 | 779.5838 | 705.2642 |  | 712.5553 | 737.4741 | 806.2737 | 592.0464 | 607.7644 | 748.1691 |  | 471.2885 |  |  | 454.5068 | 599.7227 | 673.0013 | [5 empty] | 21.8326 | 565.2147 | 21.7775 | 22.0378 | 403.8117 | 21.3087 | 21.8384 | 475.3097 | 599.3297 | 630.9574 |  | 850.6284 | 894.3783 | 526.5871 | 652.5126 | 774.3924 | 572.2761 | 631.3593 | 808.2877 | 892.4301 | 602.6861 | 721.9476 | 901.8438 | 995.1224 | 972.9986 | 497.7581 | 591.6632 | 633.6244 | 560.1126 | 659.2589 | 792.8531 | 922.0567 | 1008.4495 | 561.6608 | 623.7429 | 610.7657 | 722.1818 | 51.9909 | 0.020642 | 19.5701 | 2.692 | -28.3102 | 3.0954 | 8312.96 | -0.14 | 1.8584 | -2.7579 | -14.1391 | -1.5183 | 6.9932 | 16.8311 | -34.2245 | 53.7294 | 78.8863 | 34.5809 | 31.3023 | -1.3188 | 53.821 | 31.5411
42838.4307 | 902 | 22.8218 | 22.8058 | 22.7943 | 22.7146 | 22.3304 | 21.6414 | 22.6559 | 21.7011 | 22.3076 | 22.3109 | 22.2763 | 21.9157 | 21.1249 | 22.1078 | 21.5176 | 21.8088 | 22.2768 | 21.2456 | 28.7487 | 35.837 | 56.0076 | 87.3918 | 87.3051 | 23.1824 | 39.0797 | 88.7657 | 637.6518 | 654.0745 | 637.7877 | 22.6177 | 41.2364 | 92.6152 | 23.0567 | 42.0844 | 89.2944 | 711.4761 | 819.4052 |  | 335.4783 | 768.718 | 769.0222 | 683.5479 |  | 367.624 | 617.881 | 583.6122 | 868.9963 | 896.2307 | 909.3491 | 889.9147 | 38.2311 | 209.5529 | 55.3318 | 420.6392 | 67.8981 | 50.7471 | 48.9047 | 53.3244 | 34.874 |  |  | 0.54432 | -1.0173 | -44.6321 | -0.54742 | 8.4842 | 74.1329 | -203.3199 | -1.6556 | 9.7914 | 29.542 | 24.4701 | 0.0012206 | 0.00090189 | 0.00037291 | 24.6511 | 22.0374 | 22.1091 | 22.1555 | 21.9517 | 21.2257 | 20.0522 | 22.1364 | 22.3086 | 22.3411 | 22.289 | 21.8903 | 21.1133 | 22.2031 | 621.468 | 489.8148 | 482.1066 | 317.8226 | 256.4458 | 602.5064 | 374.8779 | 22.2609 | 22.0754 | 22.0946 | 22.0726 | 25.4966 | 33.7258 | 24.2049 | 76.362 | 84.3779 | 585.2283 | 555.2912 | 563.4857 | 558.8833 | 77.3875 | 47.582 | 740.0609 | 21.9551 | 22.1478 | 318.0225 | 21.509 | 21.9594 | 30.3765 | 85.076 | 90.7435 | 22.8092 | 42.1657 | 91.8038 | 714.8986 | 638.1839 | 766.3071 | 781.3047 | 706.1251 |  | 712.8846 | 734.1669 | 805.8625 | 589.516 | 607.3638 | 745.7087 |  | 472.579 |  |  | 453.5752 | 600.3205 | 673.2002 | [5 empty] | 21.8326 | 564.1083 | 21.7769 | 22.0418 | 403.3589 | 21.3049 | 21.8409 | 475.4693 | 598.8958 | 630.9859 |  | 846.1618 | 894.6513 | 526.3551 | 652.5694 | 775.9765 | 571.8157 | 631.1607 | 802.211 | 887.8324 | 602.6476 | 723.0567 | 914.9764 | 998.4714 | 975.4701 | 497.7905 | 591.5646 | 633.6226 | 559.9054 | 660.1599 | 793.311 | 924.5071 | 1009.1984 | 560.8779 | 623.7692 | 611.402 | 721.7933 | 50.1446 | 0.0067247 | 19.5697 | 2.7655 | -28.3278 | 3.0955 | 8321.1 | 0 | 1.5518 | -2.0981 | -13.8975 | -1.5391 | 6.9803 | 20.6335 | -34.171 | 53.7861 | 78.8495 | 34.578 | 31.2295 | -1.9153 | 54.0686 | 31.5139
42838.4307 | 903 | 22.8134 | 22.8025 | 22.7979 | 22.7133 | 22.3267 | 21.6401 | 22.6551 | 21.6937 | 22.3005 | 22.3071 | 22.27 | 21.9203 | 21.1282 | 22.1065 | 21.519 | 21.8018 | 22.2684 | 21.2511 | 28.8423 | 35.9531 | 56.8874 | 87.4548 | 87.3346 | 23.1948 | 39.207 | 88.7644 | 636.7482 | 655.0147 | 637.464 | 22.6287 | 41.3968 | 92.6365 | 23.0704 | 42.2094 | 89.3166 | 712.4731 | 822.8793 |  | 336.3229 | 770.3635 | 769.7507 | 683.2052 |  | 368.1306 | 618.4245 | 586.9627 | 870.8231 | 897.2663 | 904.1641 | 887.5776 | 38.4504 | 210.2884 | 55.2011 | 421.6369 | 68.1063 | 50.689 | 48.9024 | 53.2971 | 34.9456 |  |  | 0.49241 | -0.59344 | -42.831 | -0.34897 | 8.3757 | 57.3259 | -203.3435 | -1.8666 | 10.028 | 30.2927 | 24.5593 | 0.0011286 | 0.00084932 | 0.00038606 | 24.6873 | 22.0313 | 22.1116 | 22.1642 | 21.9547 | 21.2286 | 20.0603 | 22.14 | 22.3124 | 22.3478 | 22.2899 | 21.8914 | 21.1237 | 22.2064 | 627.4845 | 507.7564 | 492.67 | 315.6647 | 264.9435 | 604.6072 | 376.8464 | 22.2673 | 22.0715 | 22.1063 | 22.0748 | 25.58 | 33.8232 | 24.2298 | 76.4287 | 84.4263 | 585.1059 | 555.1311 | 563.0113 | 557.3066 | 81.7813 | 35.1108 | 738.2207 | 21.9539 | 22.1508 | 318.3816 | 21.5121 | 21.9578 | 30.497 | 85.1245 | 90.7833 | 22.8211 | 42.3152 | 91.8085 | 714.4248 | 640.9151 | 765.4494 | 780.6663 | 706.0932 |  | 713.2786 | 731.7779 | 805.2243 | 588.4534 | 607.0243 | 743.4607 |  | 473.7306 |  |  | 453.006 | 601.9544 | 674.9733 | [5 empty] | 21.8302 | 563.4252 | 21.7735 | 22.0396 | 402.4532 | 21.3049 | 21.8397 | 475.7854 | 598.5908 | 631.3116 |  | 848.4539 | 894.4516 | 526.4302 | 652.6153 | 777.3756 | 571.3613 | 630.9984 | 798.7021 | 888.3829 | 602.681 | 721.9727 | 927.805 | 1001.4512 | 978.7134 | 497.6522 | 591.5986 | 633.0293 | 559.6117 | 660.8835 | 793.5878 | 924.0874 | 1010.7776 | 560.3269 | 623.8997 | 612.042 | 720.8772 | 51.2084 | 0.0015005 | 19.5693 | 2.8356 | -28.4461 | 3.0955 | 8324.64 | -0.1 | 1.4757 | -1.603 | -13.6184 | -1.2293 | 6.9203 | 18.1046 | -34.098 | 53.8837 | 78.7165 | 34.5455 | 31.1155 | -2.7482 | 54.322 | 31.5367
42838.4307 | 904 | 22.8151 | 22.8056 | 22.8001 | 22.7112 | 22.3207 | 21.6393 | 22.6531 | 21.7038 | 22.3049 | 22.3028 | 22.2802 | 21.9162 | 21.1238 | 22.1057 | 21.5163 | 21.797 | 22.274 | 21.2555 | 28.9448 | 36.0682 | 57.8314 | 87.5171 | 87.3628 | 23.2109 | 39.3319 | 88.7723 | 636.1824 | 654.8489 | 637.4311 | 22.6315 | 41.552 | 92.6596 | 23.0894 | 42.3448 | 89.3495 | 713.6421 | 825.6711 |  | 337.0449 | 766.3204 | 765.7227 | 688.0061 |  | 368.5499 | 618.1238 | 586.9968 | 874.628 | 897.1418 | 902.9059 | 888.0175 | 39.0502 | 210.9124 | 56.1671 | 422.5692 | 68.1598 | 50.6234 | 48.8842 | 53.2527 | 34.9739 |  |  | 0.067914 | -1.355 | -39.7189 | -0.4022 | 8.22 | 32.6906 | -203.4336 | -2.0433 | 10.1965 | 30.569 | 24.2118 | 0.0011401 | 0.00093311 | 0.00037127 | 24.7212 | 22.0306 | 22.1111 | 22.1606 | 21.9618 | 21.2335 | 20.0626 | 22.1422 | 22.3128 | 22.3469 | 22.2925 | 21.8945 | 21.1245 | 22.2099 | 632.2823 | 495.8843 | 475.5539 | 319.2752 | 255.8197 | 607.0154 | 378.4351 | 22.2668 | 22.0738 | 22.116 | 22.0858 | 25.662 | 33.9238 | 24.2721 | 76.5083 | 84.4749 | 584.9106 | 555.9473 | 562.6764 | 557.4882 | 66.7443 | 46.894 | 737.0315 | 21.9557 | 22.1552 | 319.0336 | 21.5133 | 21.9566 | 30.6244 | 85.1764 | 90.8156 | 22.835 | 42.4645 | 91.8201 | 715.0952 | 642.758 | 763.6679 | 779.4996 | 707.7544 |  | 713.7164 | 732.167 | 804.7686 | 588.5162 | 606.7199 | 743.0452 |  | 475.0849 |  |  | 452.4274 | 604.1325 | 676.7642 | [5 empty] | 21.8223 | 563.2999 | 21.7674 | 22.0292 | 402.0715 | 21.3068 | 21.8271 | 475.9866 | 598.2681 | 631.0156 |  | 847.7843 | 894.1533 | 526.5861 | 652.6746 | 778.5984 | 571.0027 | 631.25 | 798.7635 | 889.5741 | 602.5644 | 721.6238 | 936.0672 | 1002.5559 | 982.5985 | 497.4254 | 591.7663 | 632.1163 | 558.9583 | 661.4759 | 792.8612 | 928.7197 | 1013.1674 | 559.7866 | 623.6769 | 612.8449 | 720.1136 | 50.2138 | 0.00025766 | 19.5691 | 2.8851 | -28.5183 | 3.0955 | 8290.55 | -0.05 | 0.54803 | -2.4219 | -13.1121 | -1.3194 | 6.852 | 13.6645 | -34.0873 | 53.9451 | 78.5635 | 34.4883 | 31.2209 | -0.57059 | 54.4754 | 31.4983
42838.4308 | 905 | 22.8183 | 22.8052 | 22.8085 | 22.7259 | 22.3251 | 21.6408 | 22.6652 | 21.7007 | 22.3134 | 22.3083 | 22.2786 | 21.9128 | 21.1304 | 22.1133 | 21.5197 | 21.8062 | 22.2951 | 21.2677 | 29.0506 | 36.1987 | 58.7052 | 87.5818 | 87.3918 | 23.2232 | 39.464 | 88.775 | 635.3228 | 655.1696 | 637.0163 | 22.6445 | 41.7212 | 92.7006 | 23.0975 | 42.4833 | 89.3976 | 715.1792 | 829.2798 |  | 338.0341 | 765.0607 | 764.8801 | 692.7292 |  | 369.1912 | 619.5946 | 584.1785 | 872.1901 | 895.1007 | 903.2999 | 888.0849 | 39.4746 | 211.6722 | 56.8257 | 423.8121 | 68.4341 | 50.5377 | 48.8799 | 53.2092 | 35 |  |  | 0.26768 | 0.057759 | -36.5581 | -0.28786 | 8.565 | 22.2884 | -203.4211 | -0.97092 | 10.3869 | 30.7371 | 24.0991 | 0.0011779 | 0.00086904 | 0.00037456 | 24.7447 | 22.0329 | 22.1049 | 22.1588 | 21.9601 | 21.2296 | 20.0554 | 22.1393 | 22.3026 | 22.3417 | 22.2871 | 21.8911 | 21.1206 | 22.2034 | 616.2703 | 507.7966 | 499.3136 | 321.1798 | 243.6067 | 608.9403 | 380.4806 | 22.2653 | 22.067 | 22.1204 | 22.0762 | 25.7277 | 34.0221 | 24.2849 | 76.5958 | 84.5151 | 584.7381 | 556.0162 | 562.8063 | 556.8921 | 81.0136 | 49.6782 | 737.2322 | 21.9587 | 22.1531 | 319.5506 | 21.5093 | 21.9539 | 30.7586 | 85.2308 | 90.8493 | 22.8419 | 42.6097 | 91.8322 | 714.9264 | 643.3807 | 764.1681 | 780.8321 | 712.3772 |  | 714.3384 | 732.9714 | 804.6194 | 588.3545 | 606.395 | 742.4986 |  | 477.7934 |  |  | 452.5166 | 606.311 | 679.966 | [5 empty] | 21.8349 | 563.3924 | 21.7828 | 22.0377 | 402.8623 | 21.3113 | 21.8445 | 475.8816 | 598.0693 | 629.952 |  | 852.457 | 895.3349 | 526.5948 | 652.9896 | 780.5873 | 570.3387 | 630.4101 | 799.796 | 888.6107 | 602.6175 | 723.6529 | 940.45 | 1006.3609 | 985.8353 | 497.2793 | 592.0078 | 631.3549 | 558.2141 | 662.8167 | 792.7262 | 928.6294 | 1016.8451 | 559.5903 | 623.1925 | 614.0509 | 720.6986 | 50.9595 | -0.00037432 | 19.5696 | 2.9194 | -28.5167 | 3.0956 | 8285.69 | -0.07 | 1.0878 | 0.50043 | -12.5899 | -1.1172 | 6.9955 | 11.2848 | -34.0919 | 53.9697 | 78.4946 | 34.4336 | 33.5125 | -2.8543 | 54.7226 | 31.4853
42838.4308 | 906 | 22.8211 | 22.7993 | 22.7991 | 22.7098 | 22.3232 | 21.6431 | 22.662 | 21.704 | 22.305 | 22.3066 | 22.2718 | 21.9145 | 21.1241 | 22.1055 | 21.514 | 21.8034 | 22.2818 | 21.2688 | 29.1489 | 36.3177 | 59.461 | 87.6333 | 87.4095 | 23.2385 | 39.5951 | 88.778 | 634.5011 | 656.2895 | 636.6927 | 22.643 | 41.8802 | 92.7422 | 23.118 | 42.6048 | 89.4191 | 716.7019 | 827.9937 |  | 338.7707 | 761.2598 | 760.9803 | 698.5101 |  | 369.5785 | 621.1531 | 584.9548 | 867.2005 | 891.7379 | 901.0903 | 887.0822 | 40.1068 | 212.4169 | 57.2733 | 424.9527 | 68.4779 | 50.4474 | 48.8772 | 53.1735 | 35.0742 |  |  | 0.34522 | 2.3748 | -33.287 | -0.18667 | 7.8192 | 33.8879 | -203.3889 | -1.6353 | 10.1152 | 29.5215 | 23.6083 | 0.0010152 | 0.00075076 | 0.00035977 | 24.7744 | 22.0342 | 22.1098 | 22.1606 | 21.9562 | 21.2311 | 20.0623 | 22.1371 | 22.309 | 22.3466 | 22.2931 | 21.8929 | 21.1151 | 22.2075 | 640.1822 | 505.3481 | 500.6813 | 328.5971 | 248.5959 | 612.0409 | 382.6243 | 22.2708 | 22.069 | 22.1311 | 22.0822 | 25.8024 | 34.1165 | 24.3182 | 76.7046 | 84.5624 | 584.5218 | 556.8873 | 562.7848 | 556.5257 | 69.7844 | 35.7544 | 736.9639 | 21.9563 | 22.1516 | 319.8318 | 21.5013 | 21.9547 | 30.8873 | 85.2725 | 90.8843 | 22.8572 | 42.7539 | 91.8379 | 714.1077 | 643.1275 | 764.8995 | 781.8988 | 710.9002 |  | 714.618 | 730.6698 | 804.2451 | 587.1678 | 606.0641 | 741.0832 |  | 480.4544 |  |  | 452.0388 | 606.8923 | 679.3614 | [5 empty] | 21.8323 | 564.4993 | 21.779 | 22.0431 | 402.9157 | 21.3126 | 21.8367 | 475.9554 | 598.3048 | 628.9472 |  | 853.4113 | 896.096 | 526.6614 | 652.552 | 780.3037 | 569.9551 | 629.5514 | 794.3834 | 886.9862 | 602.484 | 722.2272 | 940.6336 | 1003.3922 | 987.1368 | 497.603 | 591.9535 | 630.2285 | 557.9597 | 664.1125 | 795.2264 | 924.3969 | 1013.2241 | 559.216 | 622.2106 | 615.5295 | 721.8125 | 51.9964 | -0.00042347 | 19.5691 | 2.9289 | -28.5077 | 3.0956 | 8285.16 | -0.06 | 1.2351 | 3.2116 | -12.0239 | -0.90041 | 6.6777 | 13.9017 | -34.0572 | 54.0796 | 78.4419 | 34.4063 | 31.6853 | -2.6317 | 54.9385 | 31.4585
42838.4308 | 907 | 22.8214 | 22.8094 | 22.7991 | 22.7159 | 22.3257 | 21.6427 | 22.66 | 21.7013 | 22.3085 | 22.3128 | 22.2733 | 21.9236 | 21.1252 | 22.1075 | 21.516 | 21.8108 | 22.3083 | 21.2755 | 29.2528 | 36.4442 | 60.3643 | 87.6937 | 87.4407 | 23.2581 | 39.7281 | 88.7908 | 636.8641 | 658.2047 | 640.3798 | 22.65 | 42.0378 | 92.8039 | 23.1294 | 42.7395 | 89.4434 | 718.1979 | 830.6282 |  | 339.5827 | 760.0064 | 759.8284 | 706.0571 |  | 370.2112 | 621.9691 | 596.9772 | 870.9788 | 892.4785 | 899.3516 | 884.2689 | 40.3498 | 213.017 | 57.4572 | 425.9199 | 68.5392 | 50.3843 | 48.8689 | 53.1246 | 35.1442 |  |  | 0.39187 | 1.9332 | -29.9305 | -0.68081 | 5.6375 | 29.3991 | -203.3941 | -1.6813 | 9.8305 | 30.1572 | 23.4276 | 0.00103 | 0.00081154 | 0.00036799 | 24.7943 | 22.0345 | 22.1031 | 22.1528 | 21.9528 | 21.2164 | 20.0548 | 22.1285 | 22.3061 | 22.3313 | 22.2868 | 21.8832 | 21.116 | 22.1999 | 640.387 | 477.0407 | 458.7388 | 315.8325 | 249.0878 | 613.8828 | 383.7993 | 22.2649 | 22.0757 | 22.1366 | 22.0851 | 25.8642 | 34.2107 | 24.3432 | 76.7878 | 84.6058 | 584.2126 | 554.5845 | 561.7426 | 553.8914 | 55.7579 | 29.9158 | 736.1489 | 21.9595 | 22.1511 | 320.2838 | 21.5013 | 21.9544 | 31.0215 | 85.3293 | 90.9323 | 22.8713 | 42.9065 | 91.8496 | 715.0015 | 642.933 | 763.1128 | 779.7952 | 709.8061 |  | 714.9044 | 729.4635 | 803.7368 | 588.558 | 605.8721 | 739.8493 |  | 485.2683 |  |  | 451.6044 | 605.6416 | 678.4909 | [5 empty] | 21.8302 | 564.9467 | 21.7852 | 22.0309 | 402.6418 | 21.3073 | 21.8295 | 476.0594 | 598.4084 | 628.6218 |  | 851.8974 | 896.5264 | 527.1343 | 652.1729 | 781.0699 | 569.5413 | 629.994 | 802.4941 | 891.5098 | 602.4582 | 721.542 | 937.2706 | 1006.3755 | 983.6603 | 498.149 | 591.9231 | 629.4453 | 557.3508 | 665.0072 | 798.121 | 930.4744 | 1010.612 | 558.8373 | 621.4064 | 616.2941 | 722.3783 | 52.3127 | 0.00048936 | 19.5678 | 2.9312 | -28.58 | 3.0956 | 8301.8 | 0.03 | 1.3186 | 2.899 | -11.4068 | -1.7204 | 5.6659 | 12.9387 | -34.0324 | 54.1805 | 78.3173 | 34.3328 | 32.1579 | 2.2345 | 55.1003 | 31.4789
42838.4308 | 908 | 22.8195 | 22.8049 | 22.7925 | 22.7098 | 22.314 | 21.638 | 22.6566 | 21.6974 | 22.304 | 22.3058 | 22.2755 | 21.9205 | 21.1308 | 22.1046 | 21.5125 | 21.8018 | 22.2935 | 21.2686 | 29.356 | 36.5555 | 61.1967 | 87.7308 | 87.4528 | 23.266 | 39.8503 | 88.7858 | 638.7356 | 660.0211 | 642.1685 | 22.6591 | 42.196 | 92.8651 | 23.1416 | 42.8629 | 89.456 | 719.9112 | 830.3669 |  | 340.2819 | 758.8629 | 758.5714 | 710.043 |  | 371.1901 | 623.1183 | 597.3464 | 869.47 | 892.2326 | 900.3619 | 886.3701 | 40.1601 | 213.7687 | 58.2638 | 427.1916 | 68.6839 | 50.3212 | 48.8588 | 53.0995 | 35.2296 |  |  | 0.21773 | 1.4804 | -26.7106 | -0.39234 | 6.2946 | 35.3223 | -203.4375 | -1.6044 | 10.5497 | 31.3688 | 24.4656 | 0.0010481 | 0.00076226 | 0.00037127 | 24.8286 | 22.0389 | 22.1061 | 22.1669 | 21.9602 | 21.2343 | 20.0634 | 22.143 | 22.3167 | 22.3491 | 22.2981 | 21.8909 | 21.1247 | 22.2155 | 603.3274 | 481.7662 | 443.5672 | 317.004 | 250.4776 | 614.6014 | 384.6468 | 22.2718 | 22.0748 | 22.1513 | 22.0949 | 25.953 | 34.3155 | 24.3748 | 76.8365 | 84.6484 | 583.7425 | 551.8096 | 560.6017 | 551.2225 | 62.3501 | 44.4481 | 736.3701 | 21.9615 | 22.1534 | 320.6448 | 21.5063 | 21.9557 | 31.1526 | 85.3819 | 90.9676 | 22.8851 | 43.0588 | 91.8595 | 717.4681 | 643.9981 | 762.4189 | 778.3282 | 713.1871 |  | 715.6778 | 733.0883 | 803.7899 | 585.3435 | 605.4375 | 742.3815 |  | 484.692 |  |  | 453.5827 | 605.5358 | 680.5398 | [5 empty] | 21.8395 | 563.1251 | 21.7892 | 22.0467 | 402.7288 | 21.3143 | 21.8444 | 476.2501 | 599.0208 | 630.5871 |  | 858.6874 | 897.8663 | 527.9244 | 652.1603 | 783.2539 | 569.1952 | 629.8402 | 806.538 | 896.6222 | 602.754 | 723.4217 | 947.0254 | 1014.001 | 981.5155 | 498.4473 | 591.8601 | 630.4479 | 556.7059 | 666.1257 | 800.6525 | 935.1505 | 1016.7862 | 558.1966 | 621.6209 | 617.1288 | 723.3364 | 51.8985 | 0.00048235 | 19.5673 | 2.939 | -28.588 | 3.0956 | 8245.28 | -0.01 | 0.98382 | 2.5385 | -10.7827 | -1.3068 | 5.9896 | 14.1885 | -34.0507 | 54.2775 | 78.2331 | 34.3431 | 36.4694 | 4.069 | 55.4167 | 31.4728
42838.4308 | 909 | 22.8172 | 22.7972 | 22.7955 | 22.7047 | 22.3137 | 21.639 | 22.657 | 21.6942 | 22.3093 | 22.3018 | 22.2717 | 21.915 | 21.1271 | 22.1073 | 21.514 | 21.8109 | 22.308 | 21.2838 | 29.4539 | 36.6805 | 61.9667 | 87.7692 | 87.4685 | 23.2796 | 39.9667 | 88.7867 | 640.1576 | 661.262 | 643.0497 | 22.6769 | 42.3685 | 92.9147 | 23.1603 | 42.988 | 89.4854 | 721.6079 | 836.5376 |  | 341.1083 | 755.0676 | 754.9383 | 709.1147 |  | 371.5535 | 623.9091 | 594.9132 | 870.6147 | 891.4584 | 901.2744 | 886.4849 | 40.0142 | 214.523 | 59.3432 | 428.5201 | 68.7409 | 50.2646 | 48.859 | 53.0644 | 35.3072 |  |  | 0.34193 | 0.72605 | -23.2233 | -0.82538 | 6.3045 | 33.0119 | -203.3862 | -1.5111 | 10.0498 | 30.3569 | 24.9367 | 0.00099389 | 0.0007409 | 0.00037949 | 24.8692 | 22.0447 | 22.1087 | 22.1644 | 21.958 | 21.2329 | 20.0614 | 22.1473 | 22.3166 | 22.3429 | 22.2941 | 21.8919 | 21.1207 | 22.2113 | 578.0213 | 491.5645 | 453.793 | 325.7883 | 271.364 | 615.3815 | 385.8616 | 22.2678 | 22.0748 | 22.1459 | 22.0914 | 26.0193 | 34.4106 | 24.3921 | 76.8779 | 84.6733 | 583.3947 | 550.5925 | 559.904 | 552.0578 | 54.6788 | 33.6432 | 738.1031 | 21.9493 | 22.1465 | 320.4727 | 21.5014 | 21.9546 | 31.2743 | 85.4066 | 90.9977 | 22.8938 | 43.204 | 91.8669 | 720.3932 | 645.1327 | 761.5715 | 777.1307 | 717.3501 |  | 716.4091 | 734.8605 | 803.9854 | 583.4685 | 604.9708 | 743.7525 |  | 485.5458 |  |  | 455.5869 | 606.3453 | 684.4455 | [5 empty] | 21.8412 | 561.4757 | 21.7914 | 22.0427 | 402.3333 | 21.3177 | 21.8364 | 476.3396 | 599.1034 | 630.262 |  | 855.8842 | 900.1568 | 528.6182 | 652.8587 | 784.7487 | 568.6409 | 629.4164 | 802.2702 | 889.5738 | 603.2172 | 725.734 | 951.4431 | 1015.3345 | 984.5978 | 498.4174 | 591.47 | 631.5639 | 556.1895 | 667.5538 | 801.7431 | 933.3995 | 1020.9235 | 557.5428 | 621.736 | 618.062 | 724.6951 | 50.8701 | 0.0016058 | 19.5682 | 2.961 | -28.5482 | 3.0956 | 8239.73 | -0.16 | 1.2335 | 1.7785 | -10.0586 | -1.8963 | 5.9966 | 13.7219 | -34.0597 | 54.3427 | 78.2447 | 34.3105 | 39.4918 | 3.1464 | 55.8674 | 31.3904
42838.4308 | 910 | 22.8081 | 22.794 | 22.797 | 22.705 | 22.3217 | 21.639 | 22.6606 | 21.7037 | 22.3087 | 22.3031 | 22.2673 | 21.9094 | 21.1263 | 22.1029 | 21.5137 | 21.8182 | 22.3198 | 21.2897 | 29.5561 | 36.8038 | 62.7124 | 87.8179 | 87.4899 | 23.2984 | 40.0974 | 88.7785 | 641.5673 | 662.4445 | 645.0516 | 22.6817 | 42.5308 | 92.9348 | 23.1679 | 43.1129 | 89.5 | 723.146 | 845.4559 |  | 341.8448 | 750.6208 | 750.4164 | 707.227 |  | 372.0742 | 624.4561 | 593.403 | 871.1538 | 892.0982 | 902.8 | 885.0029 | 40.014 | 215.4061 | 60.5689 | 430.1065 | 68.7779 | 50.2063 | 48.8635 | 53.04 | 35.375 |  |  | 0.27753 | 0.92778 | -20.2669 | -0.86612 | 6.4142 | 37.5388 | -203.4211 | -1.5853 | 10.0152 | 30.5455 | 23.8658 | 0.0010793 | 0.00093146 | 0.00038934 | 24.891 | 22.0443 | 22.1086 | 22.1594 | 21.9595 | 21.2285 | 20.0603 | 22.1387 | 22.3112 | 22.3437 | 22.2937 | 21.8897 | 21.1224 | 22.2131 | 553.2631 | 493.8068 | 445.8784 | 324.3056 | 285.8006 | 615.7661 | 387.0158 | 22.2678 | 22.0757 | 22.1571 | 22.0884 | 26.0959 | 34.5096 | 24.418 | 76.9348 | 84.7217 | 583.3318 | 551.6339 | 559.926 | 554.1129 | 65.1418 | 44.621 | 738.9071 | 21.9522 | 22.1484 | 320.3991 | 21.4944 | 21.9557 | 31.4113 | 85.4234 | 91.0374 | 22.9081 | 43.3515 | 91.8659 | 720.9716 | 644.833 | 759.8284 | 774.8891 | 717.3755 |  | 717.006 | 734.2314 | 804.1363 | 583.0018 | 604.6131 | 743.6309 |  | 486.4839 |  |  | 456.6534 | 607.1081 | 684.6254 | [5 empty] | 21.8387 | 561.2204 | 21.7929 | 22.049 | 402.8256 | 21.3148 | 21.8433 | 476.3621 | 598.9004 | 630.0375 |  | 855.6952 | 900.0373 | 529.2427 | 654.139 | 786.2467 | 568.1038 | 630.4294 | 805.8855 | 889.8311 | 604.1225 | 727.7256 | 957.3394 | 1014.3787 | 988.8429 | 498.3541 | 591.072 | 631.9894 | 555.7871 | 669.0518 | 803.5112 | 934.1862 | 1026.3564 | 557.4384 | 622.3725 | 618.8819 | 725.5589 | 50.9907 | 0.0011284 | 19.5691 | 2.9797 | -28.4918 | 3.0956 | 8212.31 | -0.07 | 1.1125 | 2.0111 | -9.3995 | -1.9431 | 6.0525 | 14.642 | -34.0847 | 54.4899 | 78.3091 | 34.2586 | 42.3466 | 4.2292 | 56.3068 | 31.3226
42838.4308 | 911 | 22.8104 | 22.7963 | 22.796 | 22.7066 | 22.3169 | 21.6415 | 22.6434 | 21.6944 | 22.3069 | 22.3045 | 22.273 | 21.9077 | 21.1254 | 22.0999 | 21.515 | 21.8219 | 22.3193 | 21.3028 | 29.6624 | 36.9266 | 63.4414 | 87.8583 | 87.5175 | 23.3199 | 40.2263 | 88.7745 | 642.8206 | 662.4923 | 645.8747 | 22.6973 | 42.6965 | 92.9792 | 23.1877 | 43.2778 | 89.549 | 724.3232 | 841.5699 |  | 342.4729 | 748.3321 | 748.1229 | 703.2987 |  | 372.5217 | 624.5262 | 590.8758 | 869.3842 | 892.6073 | 902.9899 | 885.9744 | 39.8651 | 216.1885 | 61.4429 | 431.5466 | 68.9175 | 50.1671 | 48.8659 | 53.0181 | 35.4244 |  |  | 0.056086 | 0.94289 | -18.5459 | -0.80041 | 7.9644 | 18.6842 | -203.404 | -1.9711 | 10.4299 | 31.4993 | 23.5896 | 0.0009676 | 0.00073761 | 0.00035813 | 24.9237 | 22.0407 | 22.1069 | 22.1565 | 21.9491 | 21.2267 | 20.0587 | 22.1344 | 22.3047 | 22.3417 | 22.2861 | 21.8869 | 21.1178 | 22.209 | 584.0205 | 525.4542 | 471.1148 | 327.105 | 292.1741 | 617.5683 | 388.565 | 22.2632 | 22.084 | 22.1656 | 22.09 | 26.1774 | 34.6113 | 24.45 | 77.0031 | 84.7658 | 583.3622 | 551.5573 | 560.6116 | 556.2538 | 80.5286 | 45.1807 | 739.7125 | 21.9631 | 22.1545 | 320.7347 | 21.5034 | 21.9606 | 31.5531 | 85.46 | 91.0896 | 22.9288 | 43.5015 | 91.8842 | 722.2076 | 643.8778 | 760.203 | 775.8622 | 716.2884 |  | 717.6014 | 735.4669 | 804.8255 | 582.2503 | 604.1418 | 743.7576 |  | 487.5431 |  |  | 457.3874 | 607.6403 | 684.4761 | [5 empty] | 21.8424 | 560.1711 | 21.7954 | 22.0457 | 403.163 | 21.3175 | 21.8444 | 476.2409 | 598.6647 | 630.1885 |  | 858.1077 | 902.6381 | 529.7634 | 655.8058 | 787.8523 | 567.652 | 630.3988 | 813.4749 | 893.3343 | 605.0004 | 730.2615 | 965.4203 | 1016.8896 | 994.0689 | 498.267 | 591.2 | 632.8139 | 555.7622 | 670.4003 | 803.5553 | 934.6529 | 1033.5565 | 557.4635 | 623.3901 | 619.8836 | 726.5597 | 52.6002 | -0.00076051 | 19.57 | 3.0013 | -28.528 | 3.0955 | 8265.13 | 0.04 | 0.50033 | 2.0275 | -8.9919 | -1.868 | 6.7449 | 10.3308 | -34.086 | 54.6678 | 78.4896 | 34.1942 | 39.4174 | 1.6987 | 56.7131 | 31.2683
42838.4308 | 912 | 22.8149 | 22.8086 | 22.8005 | 22.721 | 22.3275 | 21.6389 | 22.661 | 21.7022 | 22.3062 | 22.3131 | 22.2848 | 21.9172 | 21.1295 | 22.1099 | 21.513 | 21.8225 | 22.325 | 21.3053 | 29.7635 | 37.0402 | 64.1271 | 87.8929 | 87.5347 | 23.3358 | 40.3478 | 88.7757 | 642.0304 | 662.2224 | 644.2795 | 22.6979 | 42.8838 | 93.0155 | 23.2071 | 43.4315 | 89.6053 | 725.3413 | 830.8241 |  | 343.2248 | 747.1086 | 747.0696 | 701.9801 |  | 373.2758 | 625.0519 | 590.1913 | 870.5182 | 893.3998 | 903.7536 | 887.3629 | 39.887 | 216.9018 | 61.8572 | 432.6903 | 69.0666 | 50.1264 | 48.8621 | 52.9925 | 35.538 |  |  | 0.45233 | 1.1223 | -16.0522 | -0.25041 | 7.5727 | 46.6136 | -203.4092 | -1.0649 | 10.8138 | 31.9671 | 22.9868 | 0.00082468 | 0.00065219 | 0.0003417 | 24.96 | 22.0389 | 22.1053 | 22.1579 | 21.954 | 21.2298 | 20.063 | 22.1388 | 22.3069 | 22.3457 | 22.2906 | 21.893 | 21.1173 | 22.2088 | 646.6975 | 572.8073 | 496.495 | 321.015 | 288.737 | 621.7142 | 390.3168 | 22.2604 | 22.0753 | 22.1623 | 22.0859 | 26.241 | 34.6992 | 24.4721 | 77.0706 | 84.7985 | 583.4582 | 552.3127 | 561.4792 | 558.7256 | 89.0924 | 48.8674 | 742.2057 | 21.9646 | 22.1508 | 321.7805 | 21.5127 | 21.9629 | 31.6877 | 85.505 | 91.134 | 22.9472 | 43.6517 | 91.9027 | 723.9901 | 643.0117 | 761.3958 | 777.7021 | 723.0418 |  | 718.3996 | 736.5235 | 805.7607 | 584.1062 | 603.8232 | 744.0462 |  | 488.5133 |  |  | 457.6791 | 607.568 | 686.3451 | [5 empty] | 21.8304 | 559.7375 | 21.7875 | 22.0363 | 403.3233 | 21.3116 | 21.835 | 476.355 | 598.4259 | 630.3022 |  | 858.7805 | 904.4893 | 529.9712 | 657.4321 | 788.4499 | 567.5636 | 629.9271 | 819.7314 | 893.5504 | 605.7399 | 733.3425 | 969.757 | 1016.2412 | 998.5415 | 498.6281 | 591.4925 | 632.8594 | 555.5159 | 671.9027 | 802.9888 | 934.7302 | 1037.0849 | 557.4001 | 623.7257 | 621.0873 | 727.3263 | 50.3704 | 0.00060171 | 19.5695 | 3.02 | -28.536 | 3.0957 | 8308.59 | -0.13 | 1.4196 | 2.2126 | -8.368 | -1.0451 | 6.5791 | 16.3228 | -34.0975 | 54.6787 | 78.7522 | 34.085 | 33.5831 | -0.81106 | 57.0075 | 31.216
42838.4308 | 913 | 22.816 | 22.804 | 22.7972 | 22.7116 | 22.3188 | 21.6409 | 22.6568 | 21.7021 | 22.3082 | 22.3048 | 22.2717 | 21.9145 | 21.1279 | 22.109 | 21.5047 | 21.8254 | 22.3322 | 21.2986 | 29.8592 | 37.1547 | 64.7948 | 87.93 | 87.5506 | 23.347 | 40.4694 | 88.77 | 640.4433 | 662.8232 | 642.0846 | 22.7037 | 43.0405 | 93.0435 | 23.2168 | 43.5659 | 89.6359 | 726.4207 | 826.9091 |  | 343.8427 | 746.4042 | 746.2656 | 702.5774 |  | 374.0109 | 625.7891 | 589.5466 | 861.1735 | 894.8376 | 905.6307 | 890.8193 | 40.1519 | 217.7676 | 60.8421 | 434.2014 | 69.1464 | 50.111 | 48.8691 | 52.9765 | 35.6265 |  |  | 0.16977 | 0.91201 | -13.8002 | -0.79318 | 7.028 | 30.5398 | -203.3935 | -1.8515 | 10.5011 | 31.5429 | 23.2578 | 0.00103 | 0.00078033 | 0.00039263 | 24.9749 | 22.0357 | 22.1055 | 22.1603 | 21.9507 | 21.2217 | 20.0584 | 22.1281 | 22.3066 | 22.3447 | 22.2865 | 21.8821 | 21.1197 | 22.2039 | 692.8693 | 579.981 | 520.5574 | 328.5413 | 285.9173 | 626.0676 | 392.5378 | 22.2682 | 22.0753 | 22.1625 | 22.0861 | 26.3239 | 34.8026 | 24.4935 | 77.1524 | 84.8378 | 583.4316 | 551.1537 | 561.5839 | 557.4425 | 77.4645 | 49.6569 | 744.503 | 21.969 | 22.1482 | 322.9545 | 21.5115 | 21.9645 | 31.8168 | 85.552 | 91.1733 | 22.9599 | 43.7968 | 91.9201 | 725.0982 | 642.2344 | 761.7405 | 778.254 | 725.9201 |  | 719.2316 | 734.5675 | 806.2785 | 584.7127 | 603.598 | 742.7502 |  | 489.4349 |  |  | 457.3165 | 608.8356 | 688.0064 | [5 empty] | 21.8334 | 559.7077 | 21.7847 | 22.0348 | 403.4424 | 21.3129 | 21.8333 | 476.8402 | 598.2202 | 629.8367 |  | 857.814 | 905.6245 | 530.161 | 658.7364 | 788.1902 | 567.5171 | 628.7026 | 822.2529 | 895.4511 | 606.3327 | 734.0203 | 965.9249 | 1016.1626 | 1002.5333 | 498.7454 | 591.8044 | 632.1738 | 555.2409 | 673.1488 | 802.7305 | 933.4488 | 1037.8721 | 557.4467 | 623.6561 | 622.0496 | 727.6311 | 50.114 | -0.0010344 | 19.5695 | 3.039 | -28.5271 | 3.0956 | 8357.68 | -0.02 | 0.86868 | 1.9954 | -7.762 | -1.8609 | 6.3431 | 13.2226 | -34.1234 | 54.806 | 78.9686 | 34.0275 | 29.6493 | -3.09 | 57.265 | 31.2471
42838.4309 | 914 | 22.8241 | 22.8138 | 22.8064 | 22.7212 | 22.3325 | 21.6477 | 22.6659 | 21.7109 | 22.313 | 22.3115 | 22.2725 | 21.9201 | 21.1354 | 22.1152 | 21.4989 | 21.8191 | 22.3407 | 21.3035 | 29.9637 | 37.2723 | 65.4548 | 87.9611 | 87.5661 | 23.3625 | 40.5909 | 88.7666 | 639.7214 | 664.1068 | 641.6097 | 22.7171 | 43.2064 | 93.0599 | 23.2275 | 43.6973 | 89.6625 | 727.6286 | 831.6835 |  | 344.7769 | 744.6663 | 744.5685 | 705.2296 |  | 375.1996 | 626.5753 | 588.8666 | 861.7103 | 895.3274 | 915.5896 | 894.1241 | 40.2806 | 218.5732 | 58.9354 | 435.3686 | 69.3046 | 50.1125 | 48.8774 | 52.9633 | 35.713 |  |  | 0.33536 | 0.55388 | -12.4545 | -0.79121 | 6.2992 | 60.9893 | -203.3409 | -2 | 10.4678 | 31.2423 | 23.6621 | 0.00091668 | 0.00073104 | 0.00037291 | 25.0167 | 22.04 | 22.1013 | 22.1562 | 21.9592 | 21.2272 | 20.0518 | 22.1354 | 22.3108 | 22.3398 | 22.2828 | 21.8833 | 21.1123 | 22.1984 | 685.3094 | 568.5667 | 527.229 | 340.6275 | 289.8694 | 628.4485 | 394.6187 | 22.2669 | 22.085 | 22.1822 | 22.0977 | 26.403 | 34.9075 | 24.5315 | 77.2339 | 84.8806 | 583.1613 | 549.6053 | 560.9887 | 554.1176 | 68.3197 | 45.3612 | 744.6279 | 21.9634 | 22.1444 | 323.2384 | 21.5019 | 21.9598 | 31.9544 | 85.5956 | 91.2111 | 22.9658 | 43.9354 | 91.9356 | 723.9629 | 640.5348 | 761.0944 | 777.4115 | 724.5788 |  | 719.8383 | 730.353 | 806.4098 | 583.4449 | 603.221 | 740.2143 |  | 490.4799 |  |  | 457.8616 | 609.7233 | 687.4412 | [5 empty] | 21.8355 | 559.424 | 21.7894 | 22.0392 | 404.397 | 21.3151 | 21.8355 | 477.0372 | 597.893 | 628.1983 |  | 856.7209 | 906.4186 | 530.2605 | 659.1784 | 785.7626 | 567.1094 | 626.9691 | 826.632 | 893.077 | 606.5 | 733.2543 | 960.9431 | 1011.4952 | 1001.9791 | 498.882 | 591.7586 | 631.1393 | 555.1639 | 673.9134 | 804.4636 | 933.1442 | 1035.9557 | 557.1846 | 623.4414 | 622.6847 | 728.0035 | 50.3227 | 0.0016409 | 19.5695 | 3.0547 | -28.6276 | 3.0957 | 8410.16 | -0.05 | 1.2206 | 1.5557 | -7.3771 | -1.8594 | 6.0305 | 18.7645 | -34.2628 | 54.9947 | 79.1267 | 33.9946 | 31.148 | -3.4602 | 57.499 | 31.2934
42838.4309 | 915 | 22.8203 | 22.8043 | 22.8019 | 22.7143 | 22.3303 | 21.6446 | 22.666 | 21.7067 | 22.3118 | 22.3062 | 22.2746 | 21.9164 | 21.1352 | 22.1062 | 21.5053 | 21.8144 | 22.3431 | 21.3137 | 30.0718 | 37.3921 | 66.1249 | 87.9966 | 87.592 | 23.3706 | 40.7158 | 88.7635 | 640.403 | 665.824 | 643.0613 | 22.7229 | 43.3619 | 93.0661 | 23.2395 | 43.8211 | 89.6644 | 728.6845 | 835.2741 |  | 345.4863 | 745.9336 | 746.2168 | 707.8628 |  | 376.9398 | 627.4087 | 587.992 | 860.116 | 898.0187 | 921.5532 | 895.6222 | 40.2148 | 219.5132 | 57.0533 | 436.5109 | 69.2588 | 50.1054 | 48.8829 | 52.9486 | 35.7965 |  |  | 0.28345 | 2.1973 | -11.3538 | -0.76099 | 7.4873 | 92.914 | -203.3021 | -1.5696 | 10.4511 | 30.6334 | 23.9401 | 0.00088382 | 0.00069819 | 0.00035977 | 25.0427 | 22.0519 | 22.1159 | 22.1606 | 21.9594 | 21.2225 | 20.0602 | 22.1431 | 22.3032 | 22.3443 | 22.287 | 21.8977 | 21.1162 | 22.2078 | 650.9112 | 545.7675 | 521.1181 | 339.2937 | 285.5839 | 629.7155 | 396.2051 | 22.2568 | 22.0764 | 22.1871 | 22.0934 | 26.4776 | 34.9946 | 24.5516 | 77.2966 | 84.9109 | 582.9793 | 549.6694 | 561.4647 | 555.3538 | 63.7375 | 39.8911 | 743.5147 | 21.9635 | 22.1488 | 323.0164 | 21.5026 | 21.9622 | 32.0973 | 85.6367 | 91.2622 | 22.9907 | 44.0813 | 91.9533 | 723.3364 | 638.0819 | 759.7108 | 775.9675 | 720.5234 |  | 720.1365 | 728.6641 | 806.5378 | 582.3494 | 602.7617 | 739.1088 |  | 491.6044 |  |  | 458.9344 | 609.9713 | 685.2903 | [5 empty] | 21.8325 | 558.3438 | 21.7867 | 22.0371 | 404.9314 | 21.3163 | 21.8341 | 476.6198 | 597.4949 | 626.6089 |  | 856.4286 | 907.4917 | 530.4162 | 659.6236 | 785.2729 | 566.8021 | 626.5638 | 825.0116 | 892.0309 | 606.6567 | 732.0142 | 959.1397 | 1012.6888 | 998.8686 | 498.9648 | 591.526 | 630.3214 | 555.1055 | 674.5276 | 806.8577 | 935.9942 | 1036.5552 | 556.6711 | 623.1224 | 622.9446 | 728.9849 | 53.7448 | 0.0013952 | 19.5694 | 3.0688 | -28.4884 | 3.0957 | 8461.03 | -0.03 | 1.1231 | 3.1001 | -7.0468 | -1.8244 | 6.5911 | 23.2187 | -34.3454 | 55.1819 | 79.2137 | 33.9422 | 35.3218 | -2.4975 | 57.6956 | 31.2281
42838.4309 | 916 | 22.81 | 22.7902 | 22.7978 | 22.704 | 22.3172 | 21.6323 | 22.6586 | 21.6883 | 22.3081 | 22.2947 | 22.2666 | 21.9089 | 21.1269 | 22.099 | 21.5056 | 21.8231 | 22.3371 | 21.3197 | 30.1728 | 37.5225 | 66.8004 | 88.0327 | 87.6213 | 23.3891 | 40.8441 | 88.7681 | 641.1331 | 666.9211 | 644.5936 | 22.7351 | 43.524 | 93.0728 | 23.2612 | 43.957 | 89.6958 | 729.874 | 836.297 |  | 346.1889 | 747.4707 | 747.742 | 709.428 |  | 377.005 | 627.9956 | 586.1458 | 857.6703 | 901.4931 | 923.8916 | 896.287 | 39.9664 | 220.3724 | 55.8424 | 437.5062 | 69.3946 | 50.1026 | 48.895 | 52.9391 | 35.8634 |  |  | 0.3209 | 0.78519 | -10.1184 | -0.60788 | 7.6674 | 106.074 | -203.2956 | -1.4611 | 10.4709 | 30.3223 | 24.0797 | 0.00093311 | 0.00075733 | 0.00038277 | 25.0761 | 22.0464 | 22.109 | 22.1548 | 21.9549 | 21.2265 | 20.0578 | 22.1308 | 22.3054 | 22.3401 | 22.2851 | 21.8843 | 21.1193 | 22.209 | 624.6824 | 505.6788 | 484.8962 | 342.2284 | 276.5843 | 630.4196 | 397.0428 | 22.2602 | 22.0738 | 22.1894 | 22.0908 | 26.5518 | 35.0871 | 24.5777 | 77.3835 | 84.9472 | 582.8659 | 549.7162 | 562.918 | 556.5385 | 65.1957 | 28.0176 | 743.674 | 21.9594 | 22.1499 | 323.1499 | 21.5052 | 21.957 | 32.2385 | 85.6715 | 91.3071 | 23.007 | 44.239 | 91.9711 | 725.0469 | 637.487 | 759.1885 | 776.0221 | 721.3273 |  | 720.5558 | 730.1785 | 806.9417 | 580.2043 | 602.2823 | 739.6054 |  | 492.8755 |  |  | 460.3706 | 610.1945 | 684.8706 | [5 empty] | 21.8341 | 557.1312 | 21.7984 | 22.04 | 404.4212 | 21.3155 | 21.8389 | 476.3069 | 597.0659 | 626.2616 |  | 855.7383 | 907.9714 | 530.7228 | 659.9587 | 786.7053 | 566.4722 | 626.4082 | 825.0996 | 893.1931 | 606.8973 | 731.1251 | 963.9093 | 1019.2111 | 1000.1195 | 499.4946 | 591.3897 | 630.5099 | 554.8626 | 675.2642 | 809.0508 | 935.9835 | 1040.6887 | 556.5515 | 622.7074 | 623.2858 | 729.7158 | 57.0764 | 0.0051729 | 19.5698 | 3.0866 | -28.4539 | 3.0957 | 8457.37 | -0.1 | 1.196 | 1.8537 | -6.6546 | -1.6311 | 6.6764 | 24.8328 | -34.3784 | 55.2645 | 79.2982 | 33.9155 | 38.432 | 1.6774 | 57.9569 | 31.1759
42838.4309 | 917 | 22.7981 | 22.7819 | 22.7844 | 22.704 | 22.3142 | 21.6285 | 22.6455 | 21.6867 | 22.2958 | 22.2937 | 22.2531 | 21.9065 | 21.1153 | 22.0955 | 21.5051 | 21.8376 | 22.3542 | 21.3336 | 30.2868 | 37.641 | 67.4058 | 88.0742 | 87.6508 | 23.4165 | 40.9744 | 88.7768 | 642.1778 | 667.8731 | 645.6297 | 22.7494 | 43.6909 | 93.0818 | 23.2815 | 44.0779 | 89.7369 | 731.1017 | 831.2302 |  | 346.9346 | 746.3874 | 746.4921 | 709.8211 |  | 377.5143 | 628.0547 | 583.4834 | 853.1746 | 901.124 | 921.9404 | 894.9229 | 39.9201 | 221.1998 | 56.1336 | 438.3927 | 69.5098 | 50.0903 | 48.8955 | 52.9314 | 35.9455 |  |  | 0.51081 | 0.082075 | -9.4659 | -0.58685 | 7.2356 | 132.4369 | -203.1806 | -2.3673 | 10.6889 | 31.0134 | 24.1121 | 0.00075404 | 0.00067026 | 0.00036963 | 25.1134 | 22.0462 | 22.1084 | 22.155 | 21.9553 | 21.2257 | 20.0544 | 22.1375 | 22.3064 | 22.3438 | 22.2878 | 21.8843 | 21.1219 | 22.208 | 615.5299 | 469.0117 | 428.9539 | 325.7975 | 274.1904 | 631.2474 | 396.831 | 22.2614 | 22.0768 | 22.2028 | 22.0943 | 26.6349 | 35.1944 | 24.6098 | 77.4771 | 84.9949 | 582.7304 | 553.2656 | 564.8866 | 558.2522 | 71.1089 | 32.4307 | 744.7734 | 21.9646 | 22.1525 | 323.2071 | 21.5078 | 21.9571 | 32.3727 | 85.7012 | 91.343 | 23.0115 | 44.3859 | 91.9952 | 726.8481 | 638.3462 | 759.0899 | 776.6866 | 722.5656 |  | 721.1396 | 730.2051 | 807.3366 | 579.9899 | 601.8944 | 739.4383 |  | 494.1592 |  |  | 461.1637 | 610.4864 | 685.8445 | [5 empty] | 21.8405 | 556.8207 | 21.8027 | 22.0419 | 403.8191 | 21.3147 | 21.8379 | 476.398 | 596.6612 | 627.0686 |  | 854.8756 | 909.5002 | 530.9652 | 660.5345 | 787.7879 | 566.3978 | 626.3356 | 831.9101 | 892.3885 | 607.3132 | 729.6891 | 968.3837 | 1022.8343 | 1003.4594 | 499.8773 | 591.1665 | 630.7718 | 554.3364 | 676.2134 | 810.9123 | 933.8322 | 1044.0934 | 556.3806 | 621.9241 | 623.5487 | 729.9666 | 57.2721 | 0.00054554 | 19.5693 | 3.1059 | -28.5093 | 3.0957 | 8408.87 | -0.13 | 1.5097 | 0.59936 | -6.4366 | -1.6027 | 6.4805 | 27.725 | -34.3406 | 55.3763 | 79.4214 | 33.8517 | 39.6796 | 7.8552 | 58.2616 | 31.1053
42838.4309 | 918 | 22.7978 | 22.7962 | 22.7958 | 22.7111 | 22.3162 | 21.6396 | 22.6472 | 21.7034 | 22.3043 | 22.3038 | 22.2702 | 21.9138 | 21.1241 | 22.1052 | 21.5037 | 21.8306 | 22.3636 | 21.3297 | 30.3905 | 37.7571 | 67.9434 | 88.1038 | 87.6655 | 23.4304 | 41.0883 | 88.7691 | 643.6561 | 668.678 | 646.5597 | 22.7573 | 43.8468 | 93.0768 | 23.2866 | 44.1974 | 89.7674 | 732.3028 | 826.4819 |  | 347.7142 | 745.8067 | 746.3035 | 709.9524 |  | 378.8998 | 628.2266 | 582.5031 | 856.2532 | 898.7942 | 917.1815 | 893.9418 | 40.4509 | 222.1152 | 56.8305 | 439.2978 | 69.4676 | 50.0744 | 48.9064 | 52.9525 | 36.0355 |  |  | 0.25256 | 0.81016 | -7.737 | -0.51719 | 5.3957 | 94.2643 | -203.3205 | -1.7089 | 10.0736 | 30.7696 | 23.2648 | 0.00081482 | 0.00066369 | 0.00035156 | 25.1431 | 22.0489 | 22.0983 | 22.1518 | 21.9574 | 21.2276 | 20.0593 | 22.1404 | 22.3106 | 22.3431 | 22.2839 | 21.8924 | 21.1264 | 22.2145 | 647.4914 | 473.211 | 430.4773 | 319.3275 | 259.6657 | 632.8821 | 397.2117 | 22.2658 | 22.078 | 22.2043 | 22.0937 | 26.7221 | 35.3076 | 24.644 | 77.5795 | 85.0387 | 582.6046 | 556.124 | 565.7196 | 556.8057 | 64.9683 | 46.5399 | 745.7162 | 21.97 | 22.1505 | 322.9186 | 21.518 | 21.9598 | 32.5179 | 85.7447 | 91.4018 | 23.0351 | 44.5335 | 92.0202 | 727.9183 | 638.6622 | 759.0563 | 777.5448 | 723.5256 |  | 721.7846 | 728.0474 | 807.5726 | 579.9628 | 601.4928 | 737.2814 |  | 495.4518 |  |  | 460.7827 | 610.7792 | 687.0595 | [5 empty] | 21.8353 | 556.9272 | 21.7949 | 22.0339 | 404.218 | 21.3131 | 21.8352 | 476.65 | 596.2705 | 628.4284 |  | 856.8581 | 909.6942 | 531.3044 | 661.6425 | 787.4656 | 566.3526 | 626.785 | 830.4757 | 893.6357 | 608.0351 | 730.0696 | 961.6695 | 1023.6301 | 1004.1913 | 499.8384 | 590.6494 | 631.5689 | 554.1557 | 676.9762 | 812.1434 | 931.192 | 1044.8427 | 556.3002 | 621.9536 | 623.9635 | 729.7834 | 55.2796 | 3.9981e-05 | 19.5693 | 3.1411 | -28.5217 | 3.0958 | 8341.4 | -0.07 | 1.0621 | 1.8832 | -5.8198 | -1.5047 | 5.585 | 23.344 | -34.284 | 55.5115 | 79.5554 | 33.7803 | 36.585 | 7.7542 | 58.5677 | 31.1241
42838.4309 | 919 | 22.8127 | 22.7923 | 22.7997 | 22.7045 | 22.3123 | 21.6431 | 22.6538 | 21.6952 | 22.2985 | 22.305 | 22.2631 | 21.9127 | 21.1248 | 22.1035 | 21.5117 | 21.8457 | 22.3685 | 21.3469 | 30.4953 | 37.8895 | 68.4698 | 88.1289 | 87.703 | 23.4487 | 41.2143 | 88.7739 | 644.6321 | 668.8895 | 647.9925 | 22.7706 | 44.0224 | 93.0872 | 23.3139 | 44.3321 | 89.8129 | 733.5015 | 834.8098 |  | 348.5511 | 748.5386 | 749.4289 | 710.9647 |  | 379.2981 | 628.5518 | 581.7666 | 859.4282 | 899.5617 | 915.4277 | 892.9854 | 40.9369 | 222.846 | 57.2114 | 440.0107 | 69.501 | 50.0419 | 48.9157 | 52.9614 | 36.121 |  |  | 0.49175 | 1.5258 | -6.1245 | -1.0449 | 5.42 | 58.7446 | -203.3573 | -2.4875 | 9.5933 | 28.7419 | 23.1389 | 0.00096596 | 0.00059469 | 0.00040577 | 25.1665 | 22.0463 | 22.097 | 22.1544 | 21.9504 | 21.2213 | 20.0584 | 22.1339 | 22.3032 | 22.3438 | 22.2852 | 21.8885 | 21.119 | 22.2072 | 642.7789 | 481.5756 | 461.5596 | 334.8546 | 264.4169 | 633.3801 | 398.176 | 22.2609 | 22.0821 | 22.2112 | 22.0999 | 26.7976 | 35.4016 | 24.6669 | 77.6519 | 85.0735 | 582.4198 | 554.1783 | 566.1982 | 555.5611 | 49.7054 | 35.238 | 745.8431 | 21.9695 | 22.155 | 322.5983 | 21.5148 | 21.9576 | 32.6618 | 85.7994 | 91.4437 | 23.0478 | 44.682 | 92.0408 | 728.0612 | 637.5249 | 758.87 | 777.4592 | 720.6876 |  | 722.066 | 727.0457 | 807.6821 | 582.3146 | 601.2222 | 736.0916 |  | 496.5174 |  |  | 460.9653 | 610.4349 | 686.0498 | [5 empty] | 21.8359 | 557.2089 | 21.8017 | 22.0406 | 404.7205 | 21.3203 | 21.8368 | 476.5136 | 595.8681 | 628.9069 |  | 865.7652 | 908.8492 | 531.6061 | 662.2735 | 787.6948 | 565.6893 | 627.3253 | 828.0959 | 899.7995 | 608.4793 | 732.3364 | 951.1064 | 1018.0838 | 1003.3561 | 500.1485 | 590.2198 | 632.3848 | 553.8845 | 677.3281 | 813.4083 | 928.9654 | 1040.6052 | 556.3711 | 622.581 | 624.4161 | 729.5644 | 56.5349 | -0.00059901 | 19.5689 | 3.1773 | -28.444 | 3.0958 | 8252.99 | -0.03 | 1.4832 | 2.5849 | -5.1788 | -2.1391 | 5.5935 | 18.4147 | -34.2618 | 55.661 | 79.6176 | 33.6664 | 37.248 | 4.4738 | 58.8497 | 31.1273
42838.4309 | 920 | 22.8138 | 22.8014 | 22.8111 | 22.7098 | 22.3249 | 21.6417 | 22.6507 | 21.7001 | 22.3091 | 22.3107 | 22.2719 | 21.9118 | 21.1307 | 22.0983 | 21.5074 | 21.8316 | 22.3678 | 21.3538 | 30.6126 | 37.9912 | 68.9619 | 88.1657 | 87.728 | 23.4705 | 41.3448 | 88.7613 | 644.6062 | 670.7048 | 647.9497 | 22.7749 | 44.1897 | 93.114 | 23.3261 | 44.4565 | 89.8439 | 734.4548 | 834.8067 |  | 349.3357 | 748.9517 | 749.9669 | 708.6781 |  | 379.8691 | 629.5707 | 581.2151 | 861.552 | 898.1575 | 912.3815 | 889.5644 | 41.08 | 223.6056 | 57.3954 | 440.6805 | 69.6439 | 50.0051 | 48.923 | 52.9511 | 36.1952 |  |  | 0.25453 | 1.395 | -5.3859 | -1.1382 | 5.4916 | 38.0599 | -203.3738 | -2.203 | 10.3133 | 30.8814 | 22.8124 | 0.00071954 | 0.00057662 | 0.0003877 | 25.1967 | 22.0466 | 22.0998 | 22.1531 | 21.9491 | 21.2166 | 20.0539 | 22.1297 | 22.3022 | 22.3433 | 22.2833 | 21.886 | 21.1177 | 22.1948 | 603.3286 | 455.7753 | 431.5879 | 320.4525 | 258.0504 | 632.3407 | 398.1768 | 22.2625 | 22.0761 | 22.2198 | 22.1053 | 26.8746 | 35.4989 | 24.694 | 77.7313 | 85.1102 | 582.3447 | 554.899 | 566.8236 | 556.8947 | 58.4228 | 29.8443 | 746.0409 | 21.9679 | 22.1537 | 322.5252 | 21.5011 | 21.9519 | 32.8053 | 85.8307 | 91.4851 | 23.0574 | 44.8217 | 92.057 | 727.3001 | 636.6573 | 757.8275 | 776.9034 | 718.3312 |  | 722.2619 | 727.3649 | 807.9699 | 584.8773 | 601.0411 | 736.1446 |  | 497.7441 |  |  | 461.171 | 609.3926 | 684.4445 | [5 empty] | 21.8407 | 557.5981 | 21.7995 | 22.0445 | 405.8703 | 21.3247 | 21.84 | 476.4153 | 595.696 | 628.9289 |  | 869.9895 | 906.2149 | 531.6461 | 662.3252 | 785.8945 | 565.546 | 626.9736 | 837.9565 | 901.0106 | 608.5804 | 733.1304 | 948.9396 | 1016.9145 | 998.7666 | 500.0544 | 590.1093 | 632.8774 | 553.3412 | 677.3464 | 814.0426 | 924.5688 | 1036.2843 | 556.1595 | 622.6815 | 624.4846 | 729.1527 | 54.3185 | -0.00097818 | 19.5681 | 3.2088 | -28.4825 | 3.0958 | 8172.66 | -0.14 | 1.0671 | 2.473 | -4.8593 | -2.2338 | 5.6231 | 14.8033 | -34.2193 | 55.7758 | 79.6992 | 33.5628 | 41.3406 | 7.8041 | 59.1606 | 31.0775
42838.4309 | 921 | 22.805 | 22.7941 | 22.7991 | 22.7055 | 22.3181 | 21.6323 | 22.6472 | 21.6866 | 22.2998 | 22.3097 | 22.2732 | 21.9155 | 21.1252 | 22.1009 | 21.5084 | 21.8433 | 22.3828 | 21.3629 | 30.7297 | 38.1292 | 69.4814 | 88.2041 | 87.7676 | 23.4772 | 41.479 | 88.7623 | 646.3294 | 672.7285 | 650.5401 | 22.7759 | 44.3391 | 93.1231 | 23.3371 | 44.5661 | 89.8619 | 735.3147 | 828.8959 |  | 350.0191 | 748.0901 | 749.0863 | 705.9745 |  | 379.9483 | 629.9867 | 581.0578 | 862.5797 | 896.0549 | 911.6216 | 889.5535 | 41.5533 | 224.4038 | 57.9668 | 441.3875 | 69.7189 | 49.9578 | 48.9329 | 52.9447 | 36.2687 |  |  | 0.4773 | 1.6421 | -5.2216 | -1.1855 | 5.8524 | 0.59573 | -203.4073 | -2.0729 | 10.3664 | 30.3292 | 22.5482 | 0.00084275 | 0.00068012 | 0.00039427 | 25.243 | 22.0534 | 22.1061 | 22.1598 | 21.9642 | 21.2263 | 20.0641 | 22.1399 | 22.3098 | 22.3532 | 22.2919 | 21.8917 | 21.127 | 22.2045 | 571.4723 | 456.566 | 402.6783 | 314.0693 | 250.722 | 631.7553 | 397.8536 | 22.2644 | 22.0814 | 22.2269 | 22.1004 | 26.9563 | 35.5978 | 24.724 | 77.8055 | 85.1457 | 582.31 | 553.6009 | 567.2639 | 556.3743 | 67.7024 | 33.378 | 747.1752 | 21.9703 | 22.1471 | 323.1452 | 21.5067 | 21.9659 | 32.9465 | 85.8637 | 91.5382 | 23.077 | 44.9671 | 92.0857 | 725.0186 | 636.893 | 757.1019 | 776.4179 | 717.2532 |  | 722.4539 | 727.2926 | 808.4967 | 586.6503 | 600.9895 | 735.4971 |  | 499.2507 |  |  | 461.4086 | 607.9891 | 684.653 | [5 empty] | 21.8305 | 558.6942 | 21.7973 | 22.0312 | 404.9701 | 21.3152 | 21.8351 | 476.349 | 595.3696 | 629.7187 |  | 870.0582 | 906.7732 | 531.3468 | 662.8238 | 786.8298 | 565.3712 | 628.3964 | 843.4048 | 901.6572 | 608.4787 | 733.981 | 945.9851 | 1013.2047 | 996.9657 | 500.0495 | 590.0148 | 633.0606 | 552.8907 | 677.274 | 815.4042 | 924.3395 | 1033.2919 | 556.0413 | 623.4029 | 623.6536 | 728.8294 | 52.7678 | -0.0016382 | 19.569 | 3.2211 | -28.5208 | 3.0958 | 8118.62 | -0.05 | 1.4633 | 2.6837 | -4.7857 | -2.2803 | 5.803 | 1.8514 | -34.2111 | 55.854 | 79.8669 | 33.5043 | 44.7167 | 10.9582 | 59.4593 | 31.086
42838.4309 | 922 | 22.8078 | 22.797 | 22.7981 | 22.7078 | 22.3227 | 21.6342 | 22.6517 | 21.6905 | 22.3002 | 22.3122 | 22.2734 | 21.9122 | 21.1265 | 22.1009 | 21.5071 | 21.8356 | 22.3855 | 21.3589 | 30.826 | 38.2476 | 70.0012 | 88.2402 | 87.783 | 23.4931 | 41.6081 | 88.7589 | 648.3116 | 673.2351 | 651.2566 | 22.7849 | 44.5095 | 93.1303 | 23.3603 | 44.6807 | 89.8932 | 736.0725 | 828.1241 |  | 350.8018 | 746.1858 | 747.4019 | 701.3094 |  | 379.8306 | 630.115 | 581.179 | 865.3091 | 896.5705 | 912.8346 | 890.8605 | 42.0112 | 225.0624 | 58.5291 | 442.1791 | 69.7384 | 49.9599 | 48.942 | 52.9317 | 36.3571 |  |  | 0.39844 | 1.6125 | -4.2523 | -0.88321 | 6.7881 | -52.0912 | -203.492 | -2.7478 | 10.887 | 31.7653 | 22.6957 | 0.00079347 | 0.00065219 | 0.00040413 | 25.2765 | 22.0571 | 22.1087 | 22.1583 | 21.9598 | 21.2263 | 20.0669 | 22.1395 | 22.317 | 22.3434 | 22.2894 | 21.888 | 21.1228 | 22.2135 | 592.3463 | 464.5621 | 395.4314 | 300.7273 | 250.7099 | 632.6363 | 397.5479 | 22.2726 | 22.0808 | 22.237 | 22.1021 | 27.0445 | 35.7117 | 24.757 | 77.8553 | 85.1802 | 582.2768 | 553.9775 | 568.4695 | 557.0099 | 79.4402 | 35.933 | 747.3929 | 21.9762 | 22.1526 | 323.6923 | 21.5126 | 21.9612 | 33.0854 | 85.9116 | 91.5873 | 23.0959 | 45.1065 | 92.1033 | 723.159 | 636.9452 | 757.6778 | 777.1194 | 714.0135 |  | 722.3513 | 724.5112 | 808.6654 | 589.3216 | 601.0077 | 734.0076 |  | 500.3711 |  |  | 461.2353 | 606.1645 | 682.6623 | [5 empty] | 21.8389 | 560.4978 | 21.8002 | 22.0435 | 405.1504 | 21.3223 | 21.8312 | 477.0721 | 595.3909 | 631.6193 |  | 869.5942 | 910.16 | 530.848 | 662.033 | 786.4279 | 565.7329 | 630.8864 | 846.3082 | 902.4798 | 608.105 | 731.8541 | 945.4442 | 1008.2544 | 995.1272 | 500.0933 | 590.5409 | 633.8879 | 552.411 | 676.9759 | 817.2379 | 922.547 | 1030.2524 | 556.5625 | 624.2019 | 622.9442 | 729.2888 | 54.0824 | 0.00054554 | 19.568 | 3.2329 | -28.3935 | 3.0959 | 8138.33 | -0.14 | 1.3375 | 2.6596 | -4.3191 | -1.9684 | 6.2529 | -17.3216 | -34.2358 | 55.9182 | 79.9973 | 33.4333 | 42.6435 | 11.7085 | 59.7864 | 31.0627
42838.431 | 923 | 22.8067 | 22.7973 | 22.7995 | 22.6989 | 22.314 | 21.6298 | 22.6462 | 21.6917 | 22.3033 | 22.3027 | 22.2696 | 21.9144 | 21.1264 | 22.0994 | 21.4991 | 21.8361 | 22.3881 | 21.3671 | 30.9227 | 38.3639 | 70.5264 | 88.2641 | 87.803 | 23.5038 | 41.7285 | 88.7549 | 649.3465 | 673.4029 | 651.2077 | 22.7977 | 44.6664 | 93.1481 | 23.372 | 44.7979 | 89.9299 | 736.5152 | 828.9868 |  | 351.5254 | 749.1923 | 750.784 | 696.4261 |  | 380.6555 | 629.7881 | 581.4235 | 867.4428 | 897.4268 | 915.4942 | 891.8862 | 41.9053 | 225.9724 | 59.1097 | 443.2956 | 69.873 | 49.9733 | 48.9491 | 52.9171 | 36.4461 |  |  | 0.21642 | 1.5363 | -3.9553 | -0.86087 | 7.3552 | -69.1479 | -203.5354 | -2.1662 | 9.9702 | 29.7122 | 22.4968 | 0.00076883 | 0.00049284 | 0.0003762 | 25.3014 | 22.0534 | 22.1045 | 22.1527 | 21.9581 | 21.2277 | 20.051 | 22.1341 | 22.308 | 22.3485 | 22.2852 | 21.8896 | 21.1157 | 22.2015 | 627.3889 | 492.66 | 408.3968 | 300.1507 | 253.1779 | 634.2687 | 397.6372 | 22.2647 | 22.0808 | 22.2366 | 22.1033 | 27.1212 | 35.8088 | 24.7814 | 77.9121 | 85.1978 | 582.2453 | 557.8603 | 569.0309 | 556.85 | 65.9912 | 39.2944 | 746.5141 | 21.9665 | 22.1397 | 324.8316 | 21.5011 | 21.9494 | 33.2219 | 85.9562 | 91.6303 | 23.1031 | 45.2443 | 92.1097 | 722.0546 | 636.4628 | 757.3989 | 776.41 | 713.1979 |  | 722.1787 | 723.4415 | 808.87 | 590.2571 | 601.0123 | 733.6034 |  | 501.4664 |  |  | 461.2966 | 603.9478 | 680.9049 | [5 empty] | 21.8321 | 560.5219 | 21.8023 | 22.0479 | 405.5515 | 21.3217 | 21.8343 | 478.0033 | 595.878 | 633.8749 |  | 864.2798 | 910.496 | 530.0356 | 661.9028 | 786.3398 | 566.4461 | 632.6007 | 841.7132 | 901.7431 | 607.8255 | 730.4099 | 935.965 | 1005.2163 | 994.3131 | 500.4935 | 591.0397 | 635.5042 | 551.7409 | 676.9145 | 817.799 | 921.477 | 1025.3084 | 557.1721 | 624.3361 | 622.3223 | 730.0274 | 53.4101 | 0.00084745 | 19.5685 | 3.2418 | -28.4818 | 3.0959 | 8157.67 | -0.05 | 0.98568 | 2.5956 | -4.1647 | -1.943 | 6.5161 | -19.9794 | -34.2778 | 55.8974 | 80.0915 | 33.4082 | 39.2071 | 10.284 | 60.0376 | 31.0618
42838.431 | 924 | 22.7991 | 22.7988 | 22.7906 | 22.6994 | 22.3105 | 21.625 | 22.6543 | 21.684 | 22.2951 | 22.3053 | 22.2666 | 21.9114 | 21.122 | 22.1029 | 21.5101 | 21.8414 | 22.3981 | 21.382 | 31.0464 | 38.4982 | 71.0207 | 88.2943 | 87.8367 | 23.5337 | 41.857 | 88.7605 | 649.4917 | 673.3136 | 651.0775 | 22.8004 | 44.8147 | 93.1393 | 23.3833 | 44.9096 | 89.9669 | 736.7837 | 821.1258 |  | 352.2126 | 752.432 | 753.8239 | 694.9429 |  | 380.9422 | 629.7308 | 580.4713 | 864.1714 | 898.6448 | 919.3815 | 895.8291 | 41.3266 | 226.6153 | 58.9092 | 443.9025 | 69.9034 | 49.9633 | 48.9546 | 52.9144 | 36.5102 |  |  | 0.32813 | 1.2439 | -3.356 | -0.47185 | 7.7265 | -86.8927 | -203.5479 | -1.6872 | 9.9914 | 30.7108 | 22.0107 | 0.00080825 | 0.00060783 | 0.00032527 | 25.3371 | 22.0538 | 22.1066 | 22.1596 | 21.9547 | 21.2211 | 20.0605 | 22.1384 | 22.3071 | 22.3439 | 22.2971 | 21.8907 | 21.1168 | 22.2078 | 620.3159 | 501.9295 | 414.4621 | 315.197 | 254.3618 | 634.9509 | 397.9944 | 22.2589 | 22.083 | 22.2423 | 22.0987 | 27.1995 | 35.9027 | 24.8092 | 77.9515 | 85.2298 | 582.3089 | 558.1436 | 568.9152 | 558.869 | 68.0521 | 37.6564 | 746.0339 | 21.9584 | 22.141 | 325.6203 | 21.5082 | 21.9544 | 33.3753 | 86.009 | 91.6848 | 23.1167 | 45.3853 | 92.1272 | 721.9422 | 636.1582 | 756.4251 | 775.209 | 713.9248 |  | 722.085 | 722.7189 | 809.1681 | 590.0218 | 600.9923 | 733.3564 |  | 503.3259 |  |  | 463.0198 | 603.433 | 680.6381 | [5 empty] | 21.8318 | 560.9449 | 21.7985 | 22.0449 | 405.1067 | 21.3259 | 21.8404 | 478.8021 | 596.2627 | 634.7919 |  | 860.4803 | 911.3673 | 529.7195 | 662.3057 | 787.1196 | 567.126 | 632.591 | 842.8786 | 902.4073 | 607.518 | 731.7276 | 931.2164 | 1004.7293 | 992.9867 | 500.8015 | 591.4215 | 636.5372 | 551.2273 | 676.6199 | 817.6257 | 922.1832 | 1023.5362 | 557.5994 | 624.0912 | 621.8533 | 730.1863 | 53.645 | 0.00044722 | 19.5683 | 3.265 | -28.4752 | 3.0959 | 8205.04 | -0.04 | 1.2136 | 2.3354 | -3.8361 | -1.4384 | 6.6895 | -22.4333 | -34.3349 | 55.8537 | 80.2055 | 33.4111 | 40.1846 | 9.6742 | 60.149 | 31.0165
42838.431 | 925 | 22.8065 | 22.8044 | 22.7891 | 22.7089 | 22.3138 | 21.6328 | 22.6544 | 21.6909 | 22.2983 | 22.3036 | 22.2747 | 21.9121 | 21.1302 | 22.1008 | 21.5053 | 21.8519 | 22.4091 | 21.3924 | 31.164 | 38.618 | 71.4674 | 88.3133 | 87.8642 | 23.5499 | 41.9857 | 88.7763 | 650.1138 | 674.5115 | 652.0098 | 22.8092 | 44.9805 | 93.1371 | 23.4121 | 45.0316 | 90.0155 | 737.0499 | 813.1566 |  | 352.9555 | 753.2342 | 753.5979 | 694.3313 |  | 381.14 | 629.5849 | 579.8498 | 865.8188 | 897.9016 | 917.1529 | 897.7233 | 40.9339 | 227.3028 | 58.6392 | 444.7116 | 69.8783 | 49.9392 | 48.9709 | 52.9233 | 36.5793 |  |  | 0.32682 | 1.6486 | -4.4521 | -0.56648 | 7.2915 | -110.2216 | -203.5683 | -2.6347 | 11.0471 | 31.7743 | 22.1239 | 0.00075897 | 0.00056841 | 0.00034663 | 25.3753 | 22.056 | 22.102 | 22.1526 | 21.958 | 21.219 | 20.0659 | 22.1386 | 22.3095 | 22.3442 | 22.2882 | 21.8871 | 21.119 | 22.2039 | 613.5197 | 511.144 | 416.7977 | 322.0664 | 262.2042 | 636.2766 | 398.5063 | 22.2679 | 22.0882 | 22.2556 | 22.1067 | 27.2911 | 35.9989 | 24.8456 | 77.993 | 85.2681 | 582.3549 | 558.4632 | 568.4331 | 558.4253 | 86.8563 | 45.3017 | 746.5759 | 21.9775 | 22.1522 | 326.2894 | 21.5115 | 21.9583 | 33.5193 | 86.0552 | 91.7404 | 23.1436 | 45.5308 | 92.1466 | 723.5139 | 635.4375 | 755.1547 | 774.0742 | 713.7609 |  | 721.9345 | 724.1343 | 809.9981 | 593.1051 | 601.1321 | 733.4363 |  | 504.8887 |  |  | 464.5863 | 603.8049 | 680.3271 | [5 empty] | 21.8344 | 562.6079 | 21.8012 | 22.0395 | 405.199 | 21.3224 | 21.8398 | 479.3385 | 596.3538 | 635.4771 |  | 861.3488 | 912.0054 | 529.3289 | 662.4096 | 787.2494 | 567.8128 | 632.3383 | 846.5267 | 905.8957 | 607.244 | 731.0035 | 929.5429 | 1006.8542 | 991.8779 | 501.0708 | 591.6631 | 636.5837 | 550.7077 | 676.1883 | 818.4917 | 921.4204 | 1024.5552 | 557.6704 | 624.0093 | 621.6552 | 730.3162 | 55.5384 | 0.00050339 | 19.5693 | 3.2946 | -28.4188 | 3.0959 | 8230.23 | -0.07 | 1.2118 | 2.6885 | -4.418 | -1.5759 | 6.4924 | -25.2423 | -34.3045 | 55.8204 | 80.4282 | 33.3505 | 41.3126 | 9.5067 | 60.2356 | 31.0367
42838.431 | 926 | 22.8173 | 22.7976 | 22.7898 | 22.7168 | 22.3271 | 21.6425 | 22.6538 | 21.6905 | 22.3127 | 22.2958 | 22.2728 | 21.9269 | 21.1277 | 22.1079 | 21.5038 | 21.8561 | 22.418 | 21.4027 | 31.2705 | 38.7278 | 71.9137 | 88.3336 | 87.8925 | 23.5741 | 42.1119 | 88.7765 | 651.9455 | 675.2498 | 653.8649 | 22.8331 | 45.1468 | 93.1284 | 23.4372 | 45.1585 | 90.0607 | 737.332 | 815.9838 |  | 353.8089 | 754.6235 | 753.6868 | 696.0685 |  | 381.9951 | 630.1012 | 584.6102 | 869.6598 | 898.2831 | 919.2007 | 899.1687 | 41.084 | 228.1227 | 58.6257 | 445.6155 | 69.9248 | 49.9058 | 48.983 | 52.9254 | 36.6147 |  |  | 0.14808 | 0.63077 | -5.2183 | -0.72681 | 8.8607 | -74.4357 | -203.4973 | -1.7292 | 10.6984 | 31.6321 | 22.3253 | 0.00065219 | 0.00054541 | 0.00036799 | 25.406 | 22.0538 | 22.1061 | 22.1507 | 21.9592 | 21.226 | 20.0631 | 22.1366 | 22.3114 | 22.3449 | 22.283 | 21.8864 | 21.1163 | 22.2051 | 612.4351 | 526.4865 | 457.8849 | 332.5194 | 271.0115 | 637.7287 | 399.7969 | 22.2665 | 22.0798 | 22.2632 | 22.1113 | 27.365 | 36.094 | 24.8764 | 78.0385 | 85.2941 | 582.3251 | 556.5083 | 567.7649 | 558.8009 | 70.2493 | 40.5577 | 748.3315 | 21.97 | 22.1513 | 327.0267 | 21.5121 | 21.95 | 33.6656 | 86.1044 | 91.7897 | 23.1534 | 45.6741 | 92.1589 | 726.1147 | 634.3422 | 754.0074 | 773.2274 | 718.3266 |  | 722.0637 | 724.247 | 810.7147 | 595.1156 | 601.2663 | 732.7758 |  | 505.8583 |  |  | 464.1201 | 605.6224 | 681.8053 | [5 empty] | 21.8364 | 564.1278 | 21.8034 | 22.0381 | 405.9022 | 21.32 | 21.8324 | 479.9014 | 596.3192 | 635.4286 |  | 870.1113 | 910.5799 | 528.8451 | 662.5751 | 787.5301 | 567.9598 | 632.0404 | 842.5426 | 907.4205 | 607.0533 | 730.3845 | 922.7364 | 1006.8103 | 988.8694 | 501.2805 | 592.111 | 637.6954 | 550.1492 | 675.6792 | 818.5447 | 922.0754 | 1020.6436 | 557.5451 | 624.6858 | 621.3589 | 729.5858 | 55.2625 | 0.00056658 | 19.5693 | 3.3281 | -28.4283 | 3.0959 | 8225.85 | -0.02 | 0.81651 | 1.6634 | -4.7845 | -1.7856 | 7.1631 | -20.7615 | -34.328 | 55.726 | 80.6517 | 33.3188 | 41.8428 | 5.1738 | 60.2612 | 31.0212
42838.431 | 927 | 22.8032 | 22.7996 | 22.7901 | 22.7104 | 22.3146 | 21.6266 | 22.6592 | 21.6889 | 22.2979 | 22.3002 | 22.2669 | 21.9128 | 21.1288 | 22.1092 | 21.5022 | 21.8574 | 22.4165 | 21.4065 | 31.3773 | 38.8476 | 72.3462 | 88.3517 | 87.9229 | 23.5907 | 42.2307 | 88.7754 | 652.5837 | 675.8955 | 653.9256 | 22.8312 | 45.3138 | 93.0972 | 23.4349 | 45.2688 | 90.0774 | 737.8657 | 808.617 |  | 354.5677 | 753.2586 | 751.3601 | 695.5633 |  | 382.1117 | 630.6435 | 583.8872 | 872.0217 | 899.4973 | 923.562 | 904.2678 | 41.9095 | 228.8644 | 59.0957 | 446.5676 | 70.1179 | 49.8714 | 49.004 | 52.9215 | 36.7192 |  |  | 0.30316 | 0.42246 | -7.1042 | -0.67885 | 7.1811 | 23.9365 | -203.4704 | -2.0933 | 10.7722 | 30.9458 | 23.1417 | 0.0007869 | 0.00059141 | 0.00036634 | 25.4422 | 22.0642 | 22.1091 | 22.1541 | 21.9621 | 21.2319 | 20.0663 | 22.1388 | 22.3156 | 22.3494 | 22.287 | 21.8906 | 21.1224 | 22.2139 | 598.2824 | 498.1913 | 452.2704 | 333.9057 | 274.6442 | 638.4281 | 400.7578 | 22.2576 | 22.0874 | 22.2709 | 22.1081 | 27.4585 | 36.2094 | 24.903 | 78.0648 | 85.3199 | 582.5294 | 555.6855 | 568.9697 | 562.0451 | 68.9946 | 39.2398 | 749.8799 | 21.968 | 22.1455 | 327.2396 | 21.5061 | 21.9593 | 33.8118 | 86.1588 | 91.8363 | 23.1795 | 45.813 | 92.1753 | 725.8897 | 634.755 | 753.0144 | 772.2747 | 721.7402 |  | 722.3761 | 722.6485 | 811.108 | 595.2382 | 601.4077 | 731.3733 |  | 507.291 |  |  | 463.0109 | 608.2316 | 684.3115 | [5 empty] | 21.8339 | 565.1156 | 21.8026 | 22.0382 | 405.7521 | 21.3266 | 21.8362 | 480.3456 | 596.1301 | 635.3942 |  | 872.016 | 909.6495 | 528.5666 | 662.9173 | 787.7973 | 567.7688 | 630.8952 | 851.2971 | 904.9366 | 607.3405 | 731.4297 | 915.4434 | 1006.9405 | 984.5255 | 501.1625 | 592.322 | 639.1003 | 549.5692 | 674.8116 | 819.0676 | 919.1434 | 1019.8785 | 557.6681 | 625.3439 | 621.1517 | 728.2997 | 52.3237 | 0.00058768 | 19.5701 | 3.3495 | -28.4244 | 3.0959 | 8240.56 | 0 | 1.1683 | 1.3617 | -5.5842 | -1.7262 | 6.4604 | 11.7948 | -34.3884 | 55.7098 | 80.8207 | 33.3407 | 43.6131 | 5.971 | 60.415 | 30.9658
42838.431 | 928 | 22.8135 | 22.8043 | 22.7979 | 22.7087 | 22.3206 | 21.6442 | 22.6608 | 21.6918 | 22.3035 | 22.3092 | 22.2716 | 21.9194 | 21.1329 | 22.1103 | 21.4992 | 21.8551 | 22.4211 | 21.412 | 31.4911 | 38.973 | 72.7872 | 88.373 | 87.9536 | 23.6059 | 42.348 | 88.7739 | 651.8078 | 676.7154 | 652.8531 | 22.8462 | 45.4691 | 93.0897 | 23.457 | 45.3926 | 90.1189 | 738.4029 | 804.4266 |  | 355.2031 | 749.9815 | 747.4075 | 695.1307 |  | 382.7995 | 631.1633 | 583.3699 | 875.478 | 901.7993 | 924.1232 | 906.4899 | 42.3083 | 229.7167 | 58.9869 | 447.5936 | 70.1413 | 49.8175 | 49.0226 | 52.9068 | 36.7968 |  |  | 0.37873 | 0.638 | -8.8469 | -0.6749 | 6.3012 | 32.9331 | -203.3665 | -2.4008 | 10.7191 | 31.2125 | 22.782 | 0.00067354 | 0.00048134 | 0.00036963 | 25.4781 | 22.0589 | 22.1143 | 22.1545 | 21.9599 | 21.2284 | 20.0629 | 22.1428 | 22.3081 | 22.3493 | 22.2831 | 21.8921 | 21.1233 | 22.2072 | 612.8609 | 508.5055 | 448.9445 | 323.721 | 270.6217 | 639.3682 | 401.2371 | 22.2538 | 22.085 | 22.2835 | 22.111 | 27.5424 | 36.3062 | 24.9214 | 78.1206 | 85.3493 | 582.7923 | 555.8891 | 570.07 | 564.0289 | 72.2159 | 38.4328 | 750.0037 | 21.9676 | 22.1452 | 328.0568 | 21.5052 | 21.9549 | 33.9513 | 86.1915 | 91.888 | 23.1899 | 45.958 | 92.1861 | 724.1421 | 635.9775 | 752.063 | 771.2862 | 717.4545 |  | 722.459 | 719.5656 | 811.1929 | 598.2501 | 601.7483 | 728.7887 |  | 508.4977 |  |  | 462.5481 | 609.929 | 683.6877 | [5 empty] | 21.8403 | 566.78 | 21.813 | 22.041 | 405.2681 | 21.3262 | 21.836 | 480.3676 | 595.9375 | 635.2174 |  | 872.7333 | 908.1932 | 528.6721 | 663.1885 | 787.5769 | 567.9086 | 630.0443 | 858.7923 | 902.2894 | 607.6321 | 733.7523 | 907.4673 | 1005.446 | 983.7749 | 500.9826 | 592.5634 | 639.5205 | 548.9551 | 673.8036 | 818.0368 | 915.8317 | 1021.0501 | 558.0314 | 626.0578 | 620.8807 | 726.5383 | 53.2781 | -0.00032516 | 19.5703 | 3.3694 | -28.3774 | 3.0959 | 8297.09 | 0.01 | 1.3051 | 1.6739 | -6.2334 | -1.7217 | 6.0531 | 13.8382 | -34.3877 | 55.8497 | 80.9332 | 33.3182 | 42.2594 | 6.4271 | 60.568 | 30.9553
42838.431 | 929 | 22.8091 | 22.7988 | 22.7977 | 22.7061 | 22.3138 | 21.6397 | 22.6511 | 21.6968 | 22.3049 | 22.3081 | 22.2705 | 21.9147 | 21.1325 | 22.1111 | 21.5021 | 21.8554 | 22.4345 | 21.4204 | 31.6061 | 39.1022 | 73.1852 | 88.397 | 87.9878 | 23.6232 | 42.4855 | 88.7845 | 650.4889 | 677.5369 | 651.1974 | 22.8592 | 45.637 | 93.0984 | 23.4778 | 45.5056 | 90.1523 | 739.1089 | 805.7598 |  | 355.8473 | 748.0836 | 745.063 | 698.0554 |  | 383.0863 | 631.6323 | 581.9059 | 873.6395 | 904.1269 | 925.32 | 908.5334 | 42.181 | 230.4063 | 57.829 | 448.3231 | 70.3465 | 49.7696 | 49.034 | 52.894 | 36.8911 |  |  | 0.51607 | 0.5322 | -11.089 | -0.74653 | 6.1179 | 72.0768 | -203.3324 | -1.8153 | 10.794 | 31.5601 | 22.8226 | 0.00057333 | 0.0004912 | 0.00035156 | 25.5046 | 22.0568 | 22.1015 | 22.1503 | 21.9541 | 21.2236 | 20.0559 | 22.135 | 22.3053 | 22.3433 | 22.286 | 21.8855 | 21.1117 | 22.2053 | 625.5109 | 527.5861 | 459.9144 | 317.3723 | 261.3745 | 640.6302 | 401.6795 | 22.2502 | 22.0771 | 22.2899 | 22.112 | 27.6186 | 36.3966 | 24.9438 | 78.1645 | 85.3796 | 583.0201 | 558.5961 | 570.797 | 564.8356 | 69.4584 | 42.7937 | 749.1597 | 21.9815 | 22.1499 | 328.9257 | 21.5102 | 21.9573 | 34.1041 | 86.2367 | 91.9438 | 23.2024 | 46.0991 | 92.2284 | 720.287 | 636.1723 | 749.841 | 768.9247 | 712.659 |  | 722.3393 | 718.2418 | 811.297 | 599.1363 | 602.0182 | 727.2144 |  | 508.8525 |  |  | 462.2251 | 609.7376 | 681.3783 | [5 empty] | 21.837 | 568.0987 | 21.8157 | 22.0457 | 406.1269 | 21.3268 | 21.8385 | 480.6528 | 596.0243 | 635.4721 |  | 875.8701 | 906.4924 | 528.7702 | 662.8025 | 787.3546 | 568.2596 | 630.3569 | 858.3583 | 904.1373 | 607.4474 | 733.141 | 902.5052 | 1002.3927 | 985.0518 | 500.7545 | 592.8838 | 638.855 | 548.5843 | 672.9628 | 818.105 | 916.91 | 1020.5238 | 558.53 | 626.2333 | 620.3655 | 725.4156 | 53.0419 | 0.00037702 | 19.5698 | 3.3765 | -28.3489 | 3.096 | 8311.28 | -0.02 | 1.5221 | 1.5292 | -6.9805 | -1.8112 | 5.9673 | 20.4823 | -34.402 | 55.9528 | 81.003 | 33.3421 | 41.212 | 5.2881 | 60.6722 | 30.9717
42838.431 | 930 | 22.8029 | 22.7947 | 22.7947 | 22.7009 | 22.3113 | 21.6336 | 22.655 | 21.6959 | 22.2999 | 22.3034 | 22.2714 | 21.9117 | 21.1267 | 22.1078 | 21.5026 | 21.8643 | 22.4368 | 21.4362 | 31.7173 | 39.2248 | 73.558 | 88.4126 | 88.0186 | 23.6451 | 42.6143 | 88.7927 | 649.1303 | 679.3427 | 649.6371 | 22.8742 | 45.7868 | 93.105 | 23.4948 | 45.6191 | 90.1814 | 739.7797 | 812.8813 |  | 356.529 | 745.3978 | 742.2454 | 701.502 |  | 383.2869 | 631.2898 | 580.3688 | 866.6157 | 906.2776 | 924.1464 | 907.0149 | 42.1933 | 231.1809 | 56.9554 | 449.1829 | 70.2849 | 49.7544 | 49.0527 | 52.8801 | 36.9643 |  |  | 0.32879 | 0.73393 | -13.5663 | -0.88781 | 6.0969 | 60.6266 | -203.3343 | -2.3029 | 10.5176 | 32.0364 | 22.9131 | 0.00073433 | 0.00052898 | 0.00038441 | 25.5457 | 22.0653 | 22.1026 | 22.1606 | 21.9464 | 21.2254 | 20.0528 | 22.1339 | 22.3048 | 22.3421 | 22.2889 | 21.8891 | 21.1184 | 22.2034 | 622.987 | 512.1707 | 470.2281 | 323.9153 | 262.644 | 641.4188 | 402.368 | 22.2442 | 22.0796 | 22.285 | 22.1004 | 27.7025 | 36.4938 | 24.9768 | 78.2114 | 85.4158 | 583.1355 | 558.8146 | 570.7387 | 563.8811 | 62.9124 | 34.2273 | 749.1135 | 21.9739 | 22.1485 | 329.7857 | 21.5156 | 21.9604 | 34.2556 | 86.2749 | 92.0143 | 23.2283 | 46.2423 | 92.2446 | 719.0041 | 637.1846 | 749.2757 | 768.7036 | 710.1181 |  | 722.1834 | 719.1719 | 811.7584 | 599.8618 | 602.2433 | 726.8836 |  | 509.4674 |  |  | 462.4828 | 608.7795 | 679.7509 | [5 empty] | 21.8337 | 569.0538 | 21.8131 | 22.0445 | 408.2159 | 21.3264 | 21.8375 | 481.2348 | 596.3186 | 635.222 |  | 879.6041 | 905.1885 | 528.6899 | 662.1033 | 787.2072 | 568.8537 | 631.1166 | 860.2332 | 905.1817 | 606.9446 | 730.9232 | 898.2241 | 1004.3632 | 984.0455 | 500.5996 | 593.1057 | 638.5209 | 548.4902 | 672.5255 | 818.1547 | 916.3674 | 1018.5279 | 559.0588 | 625.981 | 619.6943 | 726.4828 | 55.0062 | -0.0023334 | 19.5701 | 3.3905 | -28.4644 | 3.096 | 8317.54 | -0.18 | 1.2139 | 1.7955 | -7.7195 | -1.9748 | 5.9542 | 18.7758 | -34.3853 | 55.9842 | 81.1235 | 33.3624 | 41.7167 | 4.2668 | 60.7531 | 31.0178
42838.4311 | 931 | 22.8009 | 22.7964 | 22.7967 | 22.701 | 22.3086 | 21.6286 | 22.651 | 21.696 | 22.2997 | 22.2993 | 22.2718 | 21.9146 | 21.1268 | 22.1023 | 21.4964 | 21.8607 | 22.4441 | 21.4414 | 31.8277 | 39.3343 | 73.8873 | 88.4201 | 88.0434 | 23.6563 | 42.7301 | 88.7908 | 649.7538 | 681.9965 | 650.4585 | 22.8814 | 45.9431 | 93.1138 | 23.5107 | 45.7362 | 90.2245 | 740.4015 | 813.6997 |  | 357.5056 | 742.5073 | 739.2323 | 701.4663 |  | 384.31 | 631.5663 | 579.2921 | 862.8179 | 902.8929 | 920.6412 | 904.6193 | 42.0012 | 231.9209 | 57.2795 | 450.2387 | 70.271 | 49.7342 | 49.0738 | 52.8601 | 37.0623 |  |  | 0.24928 | 0.62025 | -14.6578 | -1.0173 | 6.6002 | 120.0095 | -203.2555 | -1.5117 | 10.4914 | 31.3715 | 23.1748 | 0.00063576 | 0.00038277 | 0.00036141 | 25.5787 | 22.0581 | 22.1082 | 22.1505 | 21.947 | 21.219 | 20.0584 | 22.1305 | 22.3023 | 22.342 | 22.2792 | 21.8794 | 21.1109 | 22.2002 | 615.6857 | 484.6927 | 445.7942 | 323.7298 | 266.2852 | 642.1628 | 402.5974 | 22.246 | 22.0859 | 22.2989 | 22.1103 | 27.7874 | 36.5976 | 25.0084 | 78.2692 | 85.4484 | 583.1741 | 556.32 | 569.8638 | 561.9097 | 62.867 | 34.1113 | 749.8898 | 21.977 | 22.149 | 330.1786 | 21.5121 | 21.9577 | 34.404 | 86.3245 | 92.0634 | 23.2471 | 46.3834 | 92.2603 | 718.0459 | 638.4802 | 748.7538 | 768.03 | 713.4318 |  | 722.2646 | 716.9472 | 811.9186 | 602.6834 | 602.5939 | 725.1662 |  | 510.991 |  |  | 463.2574 | 607.2343 | 679.6846 | [5 empty] | 21.8342 | 570.1955 | 21.8136 | 22.0401 | 409.6518 | 21.3245 | 21.8395 | 482.0863 | 596.8358 | 635.6848 |  | 881.5833 | 903.896 | 528.5785 | 661.4398 | 787.5206 | 569.4193 | 631.6259 | 856.8569 | 904.5351 | 606.836 | 728.2259 | 892.9874 | 1008.0843 | 982.3821 | 500.2904 | 593.3491 | 638.4872 | 548.5199 | 672.3873 | 819.5422 | 912.571 | 1017.2438 | 559.5985 | 625.7694 | 619.3907 | 727.6457 | 55.635 | -0.00078156 | 19.5705 | 3.4067 | -28.3935 | 3.096 | 8310.2 | -0.13 | 1.0574 | 1.6508 | -8.0252 | -2.1142 | 6.186 | 26.3778 | -34.3283 | 55.9125 | 81.2361 | 33.3472 | 42.7399 | 7.0232 | 60.9181 | 31.0792
42838.4311 | 932 | 22.7959 | 22.7899 | 22.7854 | 22.7004 | 22.3102 | 21.6332 | 22.6433 | 21.6902 | 22.2988 | 22.3032 | 22.2642 | 21.9091 | 21.1295 | 22.1005 | 21.4877 | 21.8554 | 22.448 | 21.4458 | 31.9418 | 39.4552 | 74.225 | 88.4266 | 88.0684 | 23.6706 | 42.8498 | 88.7953 | 651.5861 | 684.1452 | 653.615 | 22.891 | 46.0987 | 93.1302 | 23.5278 | 45.8525 | 90.2684 | 741.1295 | 813.4055 |  | 358.4255 | 739.0717 | 735.5515 | 700.0634 |  | 384.6222 | 631.5574 | 579.0185 | 854.394 | 901.29 | 919.7224 | 903.0671 | 41.8755 | 232.5963 | 57.2097 | 451.2255 | 70.4426 | 49.7305 | 49.0916 | 52.8503 | 37.1475 |  |  | 0.47664 | 0.9245 | -16.8361 | -0.81224 | 4.8411 | 85.6633 | -203.3304 | -2.1038 | 10.7792 | 32.0777 | 22.7473 | 0.00062262 | 0.00051255 | 0.0003532 | 25.6175 | 22.0542 | 22.1009 | 22.1526 | 21.9504 | 21.2166 | 20.0596 | 22.1335 | 22.306 | 22.3413 | 22.2866 | 21.8839 | 21.1122 | 22.205 | 638.4872 | 508.5638 | 438.6118 | 326.8138 | 267.3916 | 643.3414 | 402.7581 | 22.2645 | 22.0926 | 22.3187 | 22.123 | 27.8903 | 36.7176 | 25.0559 | 78.3005 | 85.4894 | 583.268 | 554.784 | 568.0054 | 560.9755 | 63.0542 | 45.2119 | 749.0338 | 21.986 | 22.1493 | 330.4635 | 21.5038 | 21.9562 | 34.559 | 86.3803 | 92.1139 | 23.2737 | 46.5232 | 92.2908 | 718.635 | 640.5989 | 746.4325 | 765.3382 | 714.165 |  | 722.4638 | 714.7786 | 811.6264 | 601.5332 | 602.7917 | 723.5684 |  | 511.4771 |  |  | 464.0953 | 606.5973 | 680.9335 | [5 empty] | 21.8319 | 571.1062 | 21.8138 | 22.0338 | 409.9141 | 21.3246 | 21.8359 | 483.116 | 597.3813 | 636.4769 |  | 876.311 | 903.8683 | 528.351 | 661.1969 | 788.8602 | 570.0199 | 632.1931 | 857.2967 | 905.4228 | 607.0228 | 728.2998 | 886.9623 | 1009.0328 | 980.1063 | 500.3915 | 593.7392 | 639.4459 | 548.6557 | 672.0319 | 820.1198 | 907.8208 | 1015.4767 | 560.1446 | 626.2628 | 619.3145 | 728.3244 | 54.9151 | -0.00090092 | 19.5692 | 3.4231 | -28.4905 | 3.096 | 8283.64 | -0.04 | 1.4647 | 2.0155 | -8.6009 | -1.8891 | 5.2959 | 22.2772 | -34.3214 | 55.9423 | 81.2036 | 33.4148 | 40.5427 | 7.8503 | 61.1493 | 31.1211
42838.4311 | 933 | 22.8098 | 22.7889 | 22.7914 | 22.7042 | 22.3137 | 21.6399 | 22.6454 | 21.6914 | 22.3107 | 22.2999 | 22.2761 | 21.912 | 21.1321 | 22.1063 | 21.5023 | 21.8672 | 22.461 | 21.4641 | 32.0515 | 39.5823 | 74.5759 | 88.4485 | 88.1041 | 23.6872 | 42.986 | 88.8145 | 652.9911 | 686.5533 | 654.4666 | 22.9061 | 46.2584 | 93.1331 | 23.5423 | 45.9679 | 90.3194 | 742.0165 | 815.9886 |  | 359.1778 | 735.8066 | 732.0254 | 700.3153 |  | 384.7376 | 631.2303 | 579.5328 | 857.4865 | 900.6527 | 917.7231 | 901.9977 | 41.8884 | 233.38 | 57.0689 | 452.1311 | 70.5327 | 49.741 | 49.1108 | 52.8502 | 37.2382 |  |  | 0.48124 | 0.4356 | -18.3337 | -0.74456 | 6.1856 | -49.9733 | -203.379 | -2.3285 | 10.4953 | 30.6148 | 22.59 | 0.00058976 | 0.00053555 | 0.00033842 | 25.6615 | 22.0619 | 22.1127 | 22.157 | 21.9595 | 21.2286 | 20.0633 | 22.134 | 22.3137 | 22.3445 | 22.2874 | 21.8926 | 21.1258 | 22.209 | 626.654 | 488.8057 | 448.677 | 332.0481 | 261.9417 | 643.7733 | 403.4148 | 22.2583 | 22.0876 | 22.3184 | 22.1191 | 27.9672 | 36.8116 | 25.0668 | 78.3171 | 85.5063 | 583.42 | 557.5795 | 567.3535 | 562.6091 | 63.6274 | 30.4893 | 747.2408 | 21.9782 | 22.144 | 330.3127 | 21.509 | 21.9572 | 34.7118 | 86.4268 | 92.1754 | 23.2937 | 46.6519 | 92.3112 | 719.3173 | 643.478 | 743.2888 | 761.5696 | 715.9464 |  | 722.7523 | 714.4987 | 811.5506 | 599.9844 | 602.9497 | 723.0798 |  | 512.1273 |  |  | 465.2182 | 606.7001 | 682.211 | [5 empty] | 21.828 | 572.156 | 21.8086 | 22.0395 | 410.3832 | 21.3169 | 21.8226 | 483.9674 | 597.8014 | 638.2281 |  | 874.6321 | 903.7336 | 528.1299 | 661.0367 | 790.6229 | 570.8031 | 632.2973 | 862.8281 | 909.2926 | 607.1163 | 728.3607 | 879.2572 | 1003.3944 | 977.5497 | 500.8287 | 594.0945 | 641.4647 | 548.9008 | 672.0673 | 820.8025 | 907.2143 | 1010.652 | 560.9617 | 626.7449 | 619.5161 | 730.0785 | 53.7331 | 0.0056644 | 19.5682 | 3.437 | -28.4879 | 3.096 | 8287.91 | -0.05 | 1.4724 | 1.3832 | -8.9736 | -1.8084 | 5.9812 | -17.0008 | -34.2967 | 55.9654 | 81.1874 | 33.4863 | 41.981 | 6.851 | 61.3772 | 31.1016
42838.4311 | 934 | 22.8045 | 22.7972 | 22.7913 | 22.7097 | 22.3212 | 21.6439 | 22.6546 | 21.6983 | 22.3061 | 22.3151 | 22.2746 | 21.9118 | 21.1303 | 22.1104 | 21.5036 | 21.8772 | 22.4659 | 21.4761 | 32.1656 | 39.7069 | 74.9187 | 88.4756 | 88.1348 | 23.7172 | 43.1131 | 88.8317 | 655.2299 | 687.3517 | 658.0503 | 22.9126 | 46.4267 | 93.1348 | 23.579 | 46.0949 | 90.395 | 742.5527 | 816.1963 |  | 360.0756 | 733.2878 | 729.4894 | 698.8531 |  | 384.6382 | 630.493 | 579.0526 | 861.5187 | 901.0536 | 916.0303 | 901.829 | 42.0418 | 233.9637 | 57.585 | 452.6713 | 70.5779 | 49.7477 | 49.1336 | 52.8629 | 37.3255 |  |  | 0.15203 | 0.57819 | -20.0566 | -0.49748 | 7.9092 | -71.4491 | -203.4966 | -1.3074 | 10.6755 | 31.211 | 22.4029 | 0.00057005 | 0.00038606 | 0.00034827 | 25.6911 | 22.0684 | 22.1075 | 22.1536 | 21.9547 | 21.2232 | 20.0619 | 22.1349 | 22.3096 | 22.3381 | 22.288 | 21.8876 | 21.1225 | 22.2095 | 607.0424 | 474.8109 | 413.7686 | 308.0246 | 247.5704 | 643.8131 | 403.2722 | 22.2629 | 22.0909 | 22.3205 | 22.1188 | 28.0598 | 36.9132 | 25.1021 | 78.3553 | 85.5403 | 583.7381 | 557.4023 | 567.8236 | 564.7269 | 72.7802 | 44.7345 | 747.3786 | 21.9784 | 22.1473 | 330.531 | 21.5072 | 21.9564 | 34.8434 | 86.495 | 92.2297 | 23.3115 | 46.7931 | 92.3451 | 720.7502 | 644.3257 | 741.1002 | 759.2457 | 716.4836 |  | 722.7821 | 716.1418 | 811.9842 | 599.1288 | 603.0814 | 723.4816 |  | 512.7717 |  |  | 464.6651 | 607.0505 | 682.3191 | [5 empty] | 21.8228 | 573.6299 | 21.8226 | 22.0348 | 410.7123 | 21.3221 | 21.8363 | 484.975 | 598.1959 | 640.278 |  | 881.754 | 905.6902 | 527.8614 | 661.2305 | 791.6137 | 571.3798 | 632.8943 | 867.1284 | 910.665 | 607.2423 | 730.6305 | 870.9321 | 999.4738 | 976.3782 | 501.0416 | 594.566 | 642.7203 | 548.9114 | 672.5725 | 822.2839 | 903.2854 | 1006.192 | 561.5029 | 627.767 | 619.5527 | 731.1644 | 53.5979 | 0.00022253 | 19.5692 | 3.4434 | -28.4087 | 3.0961 | 8240.88 | -0.15 | 0.82918 | 1.593 | -9.382 | -1.4776 | 6.7586 | -20.3137 | -34.2823 | 55.958 | 81.2794 | 33.5338 | 44.1714 | 10.7038 | 61.56 | 31.097
42838.4311 | 935 | 22.7991 | 22.7934 | 22.7834 | 22.7068 | 22.3173 | 21.6321 | 22.6547 | 21.686 | 22.3005 | 22.3054 | 22.2696 | 21.9075 | 21.1229 | 22.102 | 21.505 | 21.8695 | 22.485 | 21.4792 | 32.2881 | 39.8254 | 75.2579 | 88.4908 | 88.157 | 23.73 | 43.2498 | 88.845 | 657.019 | 686.0148 | 658.256 | 22.9138 | 46.577 | 93.1338 | 23.5914 | 46.2029 | 90.4268 | 743.1782 | 809.3666 |  | 360.7045 | 732.7233 | 729.1778 | 697.4651 |  | 384.9406 | 630.4429 | 578.4027 | 859.0941 | 900.2908 | 913.8422 | 901.1345 | 42.0801 | 234.6659 | 57.7776 | 453.3465 | 70.5805 | 49.7411 | 49.1603 | 52.8881 | 37.3656 |  |  | 0.57783 | 1.9391 | -22.2061 | -0.87664 | 6.5319 | 5.8711 | -203.4368 | -2.3226 | 10.7447 | 31.914 | 22.4681 | 0.00055034 | 0.0004912 | 0.0003762 | 25.7277 | 22.0717 | 22.1109 | 22.1498 | 21.9536 | 21.2235 | 20.0631 | 22.1343 | 22.3078 | 22.3416 | 22.2953 | 21.8847 | 21.123 | 22.207 | 617.8957 | 515.3375 | 470.4568 | 322.3166 | 259.9894 | 644.7132 | 404.2553 | 22.2545 | 22.087 | 22.3314 | 22.118 | 28.1437 | 37.0103 | 25.1315 | 78.397 | 85.5777 | 584.0926 | 561.1035 | 568.6877 | 565.9288 | 79.3425 | 39.03 | 749.0316 | 21.9754 | 22.1465 | 330.9843 | 21.5045 | 21.9558 | 35.0125 | 86.557 | 92.2906 | 23.3325 | 46.9283 | 92.3541 | 721.3715 | 643.7796 | 740.0586 | 758.3853 | 715.646 |  | 722.708 | 716.1472 | 812.3192 | 598.1978 | 603.1226 | 722.8282 |  | 513.5223 |  |  | 463.4652 | 607.6608 | 682.0158 | [5 empty] | 21.8327 | 573.8517 | 21.8227 | 22.0465 | 412.3494 | 21.3232 | 21.8367 | 485.7801 | 598.7495 | 641.0646 |  | 883.0746 | 905.4057 | 527.429 | 662.3471 | 792.1423 | 571.9875 | 632.8069 | 862.528 | 912.0078 | 607.3985 | 731.2406 | 864.1022 | 993.6634 | 974.0194 | 501.34 | 595.4377 | 644.9566 | 548.9089 | 672.2936 | 820.9424 | 900.5375 | 1001.0748 | 562.0713 | 629.9814 | 619.2459 | 730.3292 | 54.1729 | 0.00044021 | 19.5702 | 3.4446 | -28.4207 | 3.0961 | 8200.89 | -0.2 | 1.6167 | 2.9171 | -9.8716 | -1.9614 | 6.1363 | 5.8177 | -34.2457 | 55.9626 | 81.3856 | 33.5671 | 43.2231 | 4.5835 | 61.7647 | 31.124
42838.4311 | 936 | 22.8027 | 22.7995 | 22.7926 | 22.7082 | 22.3206 | 21.631 | 22.6521 | 21.6915 | 22.3062 | 22.2963 | 22.2747 | 21.9031 | 21.1223 | 22.1023 | 21.5042 | 21.8765 | 22.4887 | 21.4924 | 32.407 | 39.9486 | 75.5589 | 88.5175 | 88.1978 | 23.7494 | 43.3704 | 88.8668 | 654.5262 | 684.0624 | 655.0618 | 22.9339 | 46.7297 | 93.1296 | 23.6066 | 46.3169 | 90.4637 | 743.4546 | 803.7201 |  | 361.4598 | 736.4444 | 732.1607 | 695.1642 |  | 385.4986 | 630.6619 | 580.3047 | 863.4254 | 900.5363 | 914.3845 | 905.5295 | 41.4727 | 235.4046 | 59.0463 | 454.1796 | 70.5973 | 49.7547 | 49.1841 | 52.8937 | 37.4271 |  |  | 0.42473 | 0.97838 | -23.4552 | -0.79713 | 7.1634 | -48.1964 | -203.4644 | -1.448 | 10.3902 | 31.7833 | 22.1119 | 0.00058483 | 0.00052734 | 0.00038934 | 25.7574 | 22.0697 | 22.0954 | 22.1537 | 21.9524 | 21.226 | 20.0606 | 22.1329 | 22.31 | 22.3439 | 22.2855 | 21.8908 | 21.1177 | 22.206 | 663.4639 | 540.9936 | 466.0625 | 320.8802 | 265.0142 | 647.3352 | 404.897 | 22.2593 | 22.0911 | 22.3405 | 22.1188 | 28.2387 | 37.1217 | 25.1702 | 78.4586 | 85.6011 | 584.5404 | 559.697 | 569.1814 | 567.2357 | 93.6732 | 41.8693 | 749.7656 | 21.9827 | 22.1486 | 331.7015 | 21.5079 | 21.9589 | 35.163 | 86.6058 | 92.3442 | 23.3483 | 47.0728 | 92.381 | 722.8963 | 645.1221 | 740.4709 | 758.7981 | 714.8205 |  | 722.7128 | 715.9717 | 812.641 | 600.2656 | 603.2954 | 722.2647 |  | 514.1799 |  |  | 462.7634 | 608.9197 | 681.4312 | [5 empty] | 21.8381 | 574.0132 | 21.8257 | 22.0412 | 412.6322 | 21.3408 | 21.8347 | 486.5664 | 599.1563 | 641.6615 |  | 888.408 | 905.5064 | 527.0348 | 663.2436 | 792.6854 | 572.6884 | 632.772 | 866.4807 | 914.537 | 607.7197 | 734.6464 | 855.5307 | 993.0452 | 973.004 | 501.905 | 596.7375 | 645.8429 | 548.9058 | 671.9504 | 816.1701 | 899.5259 | 1001.9547 | 562.7789 | 631.0966 | 618.8245 | 728.6594 | 55.1305 | -0.00078858 | 19.5699 | 3.4547 | -28.4275 | 3.096 | 8156.55 | -0.07 | 1.3837 | 2.0723 | -10.1467 | -1.8706 | 6.4276 | -16.6724 | -34.2558 | 55.9867 | 81.4929 | 33.5408 | 38.9132 | 5.1884 | 61.9022 | 31.1642
42838.4311 | 937 | 22.8003 | 22.7982 | 22.7942 | 22.7084 | 22.3072 | 21.6307 | 22.6516 | 21.6861 | 22.2945 | 22.2955 | 22.2671 | 21.903 | 21.1275 | 22.0961 | 21.5057 | 21.8809 | 22.4893 | 21.5002 | 32.5173 | 40.0691 | 75.8532 | 88.5382 | 88.2209 | 23.7696 | 43.485 | 88.8723 | 650.5711 | 682.6109 | 650.8499 | 22.9512 | 46.8841 | 93.132 | 23.6219 | 46.4241 | 90.5104 | 743.6588 | 805.4866 |  | 362.2671 | 737.2777 | 732.684 | 695.0217 |  | 386.0982 | 630.1136 | 583.2943 | 867.2044 | 903.8187 | 918.2584 | 910.7236 | 41.2328 | 236.0584 | 60.6954 | 454.9591 | 70.7046 | 49.752 | 49.2155 | 52.9041 | 37.4872 |  |  | 0.32682 | 0.59266 | -25.9115 | -0.36803 | 6.1711 | -100.631 | -203.4579 | -1.4513 | 10.4178 | 31.3507 | 22.8558 | 0.00048134 | 0.00035977 | 0.00038277 | 25.788 | 22.0618 | 22.09 | 22.1535 | 21.9424 | 21.2138 | 20.0616 | 22.1335 | 22.2954 | 22.343 | 22.2846 | 21.8816 | 21.1072 | 22.2002 | 680.4878 | 546.4 | 472.0019 | 319.7664 | 266.3856 | 649.4478 | 405.599 | 22.2582 | 22.0868 | 22.3489 | 22.1259 | 28.3257 | 37.2295 | 25.2043 | 78.4892 | 85.6307 | 584.9151 | 558.4261 | 568.8791 | 567.0921 | 57.9266 | 31.965 | 751.6036 | 21.9899 | 22.1462 | 332.9031 | 21.5048 | 21.9545 | 35.3247 | 86.6625 | 92.4039 | 23.3584 | 47.2116 | 92.4119 | 724.1729 | 645.4357 | 739.9293 | 758.5343 | 716.8278 |  | 722.8706 | 717.1661 | 813.4342 | 602.6137 | 603.595 | 721.9736 |  | 514.9556 |  |  | 463.2892 | 610.9293 | 683.3085 | [5 empty] | 21.8346 | 575.5129 | 21.8178 | 22.0457 | 412.4976 | 21.3259 | 21.8348 | 487.182 | 599.4683 | 642.6042 |  | 894.0115 | 904.4009 | 527.3512 | 663.6542 | 791.0476 | 573.2981 | 634.5105 | 865.5477 | 915.4858 | 608.0994 | 735.0144 | 851.3679 | 994.2552 | 973.2803 | 502.0424 | 597.3361 | 643.5933 | 549.099 | 672.2191 | 812.9626 | 896.0486 | 1004.0476 | 563.1873 | 630.6708 | 618.7632 | 727.9026 | 53.5342 | -0.00093604 | 19.57 | 3.478 | -28.425 | 3.096 | 8103.61 | -0.06 | 1.211 | 1.6124 | -10.6616 | -1.2706 | 5.9756 | -24.1303 | -34.3111 | 55.9707 | 81.7122 | 33.5297 | 37.6313 | 4.6562 | 61.9605 | 31.2323
42838.4311 | 938 | 22.8017 | 22.7822 | 22.79 | 22.707 | 22.3055 | 21.6302 | 22.6471 | 21.691 | 22.2931 | 22.299 | 22.2618 | 21.9087 | 21.1285 | 22.098 | 21.4969 | 21.8766 | 22.5003 | 21.509 | 32.6287 | 40.1882 | 76.1828 | 88.5554 | 88.2531 | 23.78 | 43.6101 | 88.8824 | 648.6054 | 682.719 | 650.0661 | 22.9565 | 47.0304 | 93.1579 | 23.6387 | 46.5415 | 90.5401 | 744.0715 | 803.7614 |  | 363.0913 | 743.2315 | 738.4337 | 697.5597 |  | 386.3213 | 629.2001 | 584.6528 | 870.9525 | 904.2452 | 920.1065 | 916.7285 | 41.4957 | 236.7835 | 62.3186 | 456.0313 | 70.7268 | 49.7348 | 49.2393 | 52.9242 | 37.5598 |  |  | 0.75394 | 0.68071 | -27.9696 | -0.29509 | 6.639 | -58.4974 | -203.5518 | -1.814 | 10.5677 | 31.6644 | 22.0197 | 0.00057826 | 0.00047477 | 0.00035977 | 25.8376 | 22.0683 | 22.1032 | 22.1516 | 21.9506 | 21.2208 | 20.0615 | 22.1369 | 22.2993 | 22.3472 | 22.2897 | 21.8855 | 21.1164 | 22.202 | 633.9283 | 510.618 | 445.016 | 309.4256 | 255.3789 | 649.2225 | 405.4506 | 22.2636 | 22.0949 | 22.363 | 22.1293 | 28.4159 | 37.3239 | 25.2269 | 78.5385 | 85.6652 | 584.9965 | 554.8876 | 568.0261 | 563.5963 | 61.4523 | 31.6027 | 753.937 | 21.9852 | 22.1446 | 333.5215 | 21.5011 | 21.9564 | 35.4659 | 86.6973 | 92.459 | 23.3728 | 47.3347 | 92.4354 | 724.655 | 643.6154 | 739.2001 | 757.7507 | 716.1391 |  | 722.999 | 715.6977 | 813.8163 | 598.9118 | 603.5759 | 720.4911 |  | 515.7672 |  |  | 463.9123 | 612.8035 | 683.6324 | [5 empty] | 21.8326 | 574.1587 | 21.8132 | 22.0329 | 411.8638 | 21.3275 | 21.8295 | 487.829 | 599.9884 | 642.1525 |  | 896.9181 | 900.3168 | 527.9764 | 664.3733 | 790.0374 | 573.6811 | 634.839 | 861.9657 | 914.9067 | 608.4943 | 736.3456 | 845.5459 | 989.8247 | 971.6855 | 502.3472 | 597.4017 | 641.0271 | 549.2753 | 672.4446 | 813.3819 | 894.4309 | 1001.2897 | 563.3402 | 629.4603 | 618.7127 | 727.6393 | 53.379 | 0.0013039 | 19.5701 | 3.5049 | -28.4531 | 3.0961 | 8060.85 | -0.1 | 1.8386 | 1.7272 | -11.0713 | -1.1372 | 6.2028 | -18.412 | -34.3456 | 56.0222 | 81.8749 | 33.6291 | 42.7395 | 7.6276 | 61.9999 | 31.3433
42838.4311 | 939 | 22.801 | 22.7914 | 22.7887 | 22.7042 | 22.3137 | 21.6332 | 22.6517 | 21.6869 | 22.2992 | 22.3096 | 22.2642 | 21.9131 | 21.123 | 22.096 | 21.5001 | 21.8929 | 22.5092 | 21.5284 | 32.7498 | 40.3135 | 76.4855 | 88.5816 | 88.299 | 23.8063 | 43.7371 | 88.9055 | 647.9686 | 682.9134 | 649.075 | 22.9645 | 47.1796 | 93.1869 | 23.6687 | 46.6607 | 90.5633 | 744.8185 | 795.8969 |  | 363.9014 | 756.5682 | 749.8971 | 699.8233 |  | 386.1638 | 629.305 | 582.3632 | 870.5654 | 904.0607 | 922.3448 | 920.5772 | 41.5827 | 237.3842 | 62.9159 | 456.8304 | 70.7691 | 49.715 | 49.2631 | 52.9434 | 37.6502 |  |  | 0.62318 | 0.62222 | -29.9029 | -0.61116 | 7.4689 | -49.3168 | -203.5118 | -1.5163 | 10.4324 | 31.2236 | 21.0328 | 0.00052569 | 0.00037291 | 0.00039098 | 25.8761 | 22.073 | 22.1084 | 22.1564 | 21.9577 | 21.2273 | 20.0608 | 22.137 | 22.307 | 22.3424 | 22.2861 | 21.8934 | 21.1224 | 22.2058 | 637.3373 | 503.2318 | 434.0246 | 316.5644 | 258.8454 | 649.7051 | 405.0676 | 22.2559 | 22.0942 | 22.3675 | 22.1328 | 28.5052 | 37.426 | 25.2583 | 78.6122 | 85.6849 | 584.8606 | 568.5174 | 567.7818 | 560.3879 | 81.337 | 47.4334 | 753.4881 | 21.9867 | 22.1453 | 334.8308 | 21.5083 | 21.9512 | 35.6242 | 86.7363 | 92.5179 | 23.3984 | 47.472 | 92.4542 | 724.8778 | 642.6468 | 738.3704 | 756.6677 | 715.2775 |  | 723.1494 | 714.851 | 813.8791 | 597.8523 | 603.5683 | 719.788 |  | 516.5774 |  |  | 464.9423 | 614.6032 | 683.9357 | [5 empty] | 21.8338 | 572.279 | 21.8246 | 22.0387 | 411.8898 | 21.3356 | 21.8357 | 488.0098 | 600.4104 | 641.794 |  | 900.2561 | 898.6403 | 528.689 | 664.4063 | 790.2957 | 574.1802 | 634.5049 | 863.9909 | 913.3686 | 608.7008 | 735.839 | 838.8972 | 988.3214 | 971.4929 | 502.576 | 597.4481 | 640.0248 | 549.7187 | 672.8208 | 811.9703 | 892.0935 | 999.2542 | 563.6111 | 628.2818 | 618.8485 | 727.2927 | 53.2517 | 0.00056658 | 19.5696 | 3.5184 | -28.4354 | 3.0961 | 8062.97 | -0.09 | 1.6707 | 1.6514 | -11.4482 | -1.6367 | 6.5852 | -16.9215 | -34.3744 | 56.084 | 81.9184 | 33.6571 | 42.5003 | 8.7792 | 62.1363 | 31.4092
42838.4312 | 940 | 22.7961 | 22.7877 | 22.7929 | 22.7066 | 22.3116 | 21.6328 | 22.6451 | 21.6874 | 22.3006 | 22.3053 | 22.2596 | 21.9046 | 21.1241 | 22.0963 | 21.5039 | 21.8988 | 22.5235 | 21.5387 | 32.8658 | 40.4353 | 76.7617 | 88.6062 | 88.3328 | 23.829 | 43.8592 | 88.9275 | 646.1646 | 682.9755 | 646.589 | 22.9878 | 47.3334 | 93.2303 | 23.6876 | 46.762 | 90.6159 | 744.8748 | 804.7661 |  | 364.8067 | 762.2219 | 755.0478 | 695.6834 |  | 386.0823 | 628.7985 | 582.0259 | 861.9761 | 907.4112 | 921.9837 | 922.1908 | 41.6445 | 238.0226 | 63.4226 | 457.603 | 70.8334 | 49.7177 | 49.2895 | 52.9487 | 37.7352 |  |  | 0.42473 | 0.030163 | -32.7574 | -0.41469 | 7.8402 | -108.9093 | -203.544 | -2.4593 | 10.8825 | 32.4799 | 20.1098 | 0.0004452 | 0.0003877 | 0.00037456 | 25.903 | 22.0704 | 22.107 | 22.154 | 21.9495 | 21.2224 | 20.0561 | 22.1349 | 22.3062 | 22.3387 | 22.2869 | 21.8879 | 21.1166 | 22.2076 | 648.0581 | 543.9696 | 491.3092 | 329.8265 | 260.2158 | 650.9123 | 405.9414 | 22.2574 | 22.0879 | 22.3706 | 22.1257 | 28.5817 | 37.5183 | 25.2815 | 78.6724 | 85.7068 | 584.7202 | 571.6413 | 568.2918 | 559.3503 | 90.8445 | 58.1451 | 753.5444 | 21.9819 | 22.1445 | 335.5072 | 21.5122 | 21.9538 | 35.7758 | 86.7871 | 92.5774 | 23.4214 | 47.6167 | 92.4856 | 725.5479 | 642.826 | 737.5961 | 755.4477 | 715.5389 |  | 723.2835 | 713.6654 | 813.9749 | 598.6269 | 603.7405 | 718.6262 |  | 517.4695 |  |  | 465.1094 | 615.2337 | 684.8717 | [5 empty] | 21.8277 | 572.8403 | 21.8207 | 22.0386 | 412.4179 | 21.3329 | 21.8326 | 487.8297 | 600.7389 | 641.554 |  | 903.5329 | 898.163 | 529.0565 | 663.9047 | 788.8274 | 574.6271 | 633.6589 | 871.2404 | 914.9865 | 608.849 | 737.4162 | 831.8451 | 989.1727 | 970.8198 | 502.8386 | 597.5269 | 639.1379 | 550.4547 | 673.6404 | 810.2542 | 891.9322 | 1000.4718 | 563.8516 | 627.276 | 619.4311 | 727.5937 | 52.3598 | 0.00074918 | 19.5689 | 3.5229 | -28.4905 | 3.096 | 8095.36 | -0.09 | 1.3774 | 0.36349 | -11.9788 | -1.3478 | 6.7459 | -25.1425 | -34.372 | 56.1106 | 81.9819 | 33.6667 | 41.6588 | 2.5733 | 62.2663 | 31.414
42838.4312 | 941 | 22.8025 | 22.7976 | 22.7895 | 22.6988 | 22.3202 | 21.6361 | 22.6502 | 21.6965 | 22.3031 | 22.3049 | 22.2714 | 21.9122 | 21.1325 | 22.1059 | 21.4982 | 21.8938 | 22.5264 | 21.5457 | 32.9752 | 40.5523 | 77.0019 | 88.6274 | 88.3645 | 23.8472 | 43.9781 | 88.9307 | 645.5599 | 682.7766 | 646.3354 | 22.9907 | 47.5002 | 93.2534 | 23.6984 | 46.9008 | 90.6762 | 744.3965 | 802.5836 |  | 365.6549 | 771.1458 | 762.9933 | 692.693 |  | 385.6711 | 628.0421 | 588.473 | 860.8624 | 907.8684 | 922.2944 | 925.3951 | 41.9799 | 238.7698 | 63.5607 | 458.386 | 70.8514 | 49.7428 | 49.3013 | 52.9489 | 37.8139 |  |  | 0.26439 | 0.5552 | -35.2189 | -0.42388 | 6.7093 | -37.0038 | -203.5341 | -1.6248 | 10.7177 | 31.9927 | 19.1034 | 0.00053391 | 0.00039099 | 0.00039263 | 25.9483 | 22.0696 | 22.106 | 22.153 | 21.952 | 21.2219 | 20.0557 | 22.1375 | 22.3073 | 22.3408 | 22.2868 | 21.8917 | 21.1227 | 22.2087 | 688.2416 | 578.5637 | 572.5693 | 349.4641 | 269.5975 | 653.6511 | 408.4453 | 22.252 | 22.0875 | 22.3758 | 22.1232 | 28.6733 | 37.6295 | 25.3093 | 78.7244 | 85.7358 | 584.5099 | 561.5711 | 567.015 | 557.407 | 76.6335 | 39.9656 | 753.4805 | 21.9814 | 22.1433 | 336.9643 | 21.5107 | 21.9586 | 35.9254 | 86.8195 | 92.6348 | 23.4382 | 47.757 | 92.5101 | 724.8855 | 642.1548 | 736.6784 | 754.593 | 714.7709 |  | 723.2028 | 712.9019 | 814.1951 | 597.9754 | 603.85 | 717.4364 |  | 518.4514 |  |  | 464.5183 | 614.2246 | 684.0842 | [5 empty] | 21.8386 | 572.8052 | 21.825 | 22.0465 | 412.7058 | 21.3459 | 21.8355 | 487.7338 | 600.9407 | 640.9469 |  | 912.3267 | 895.5506 | 529.4137 | 663.9759 | 788.2256 | 574.6046 | 634.2759 | 879.3244 | 917.7653 | 609.3665 | 736.9023 | 825.3728 | 988.9706 | 970.6136 | 503.021 | 597.6583 | 638.1966 | 550.6674 | 674.4458 | 810.1016 | 892.0385 | 1001.0851 | 564.1853 | 627.1476 | 620.1078 | 728.0964 | 53.2291 | -0.00010749 | 19.5689 | 3.5277 | -28.4971 | 3.096 | 8181.19 | -0.09 | 1.0866 | 1.5588 | -12.4155 | -1.3621 | 6.2412 | -14.6573 | -34.3756 | 56.1116 | 82.0735 | 33.7046 | 37.9906 | -5.9986 | 62.2217 | 31.432
42838.4312 | 942 | 22.7907 | 22.7944 | 22.7866 | 22.7072 | 22.306 | 21.6291 | 22.6525 | 21.6939 | 22.3028 | 22.2993 | 22.2647 | 21.9096 | 21.1261 | 22.1006 | 21.4952 | 21.8953 | 22.5354 | 21.5596 | 33.095 | 40.6716 | 77.2158 | 88.6447 | 88.4093 | 23.8648 | 44.096 | 88.945 | 645.7542 | 683.2234 | 646.2288 | 23.0087 | 47.6418 | 93.2802 | 23.7252 | 47.0053 | 90.7038 | 744.3037 | 795.704 |  | 366.4209 | 771.0352 | 762.9193 | 692.7737 |  | 386.1982 | 627.3097 | 591.1596 | 859.6253 | 910.2526 | 923.9654 | 926.8123 | 42.3783 | 239.3565 | 63.6285 | 458.9992 | 70.9532 | 49.7683 | 49.327 | 52.9523 | 37.9306 |  |  | 0.49635 | 0.53088 | -37.5845 | -0.43571 | 7.2783 | 141.1305 | -203.2272 | -1.6793 | 11.1659 | 33.0438 | 18.1993 | 0.00043534 | 0.00034992 | 0.00039756 | 25.9944 | 22.0783 | 22.1045 | 22.1544 | 21.9584 | 21.2242 | 20.0573 | 22.1407 | 22.3118 | 22.345 | 22.285 | 21.891 | 21.127 | 22.2133 | 668.6031 | 544.0175 | 529.3785 | 355.6952 | 267.5843 | 654.998 | 409.6249 | 22.2563 | 22.093 | 22.3942 | 22.1341 | 28.7709 | 37.7397 | 25.3521 | 78.757 | 85.7634 | 584.383 | 575.3362 | 565.6759 | 557.9522 | 89.2991 | 47.5658 | 753.3747 | 21.9801 | 22.1428 | 337.9307 | 21.5082 | 21.9524 | 36.0783 | 86.8482 | 92.6912 | 23.4533 | 47.8898 | 92.536 | 724.246 | 640.6756 | 735.5008 | 753.0039 | 712.3524 |  | 723.0489 | 711.8903 | 814.2999 | 595.2576 | 603.777 | 716.3496 |  | 519.2932 |  |  | 464.2077 | 613.0594 | 682.1738 | [5 empty] | 21.8305 | 571.51 | 21.8249 | 22.0432 | 413.8917 | 21.3422 | 21.8355 | 488.1407 | 601.4982 | 640.813 |  | 916.8849 | 895.0926 | 529.9624 | 664.3991 | 788.3179 | 574.7369 | 635.0734 | 885.7963 | 920.5801 | 610.0844 | 736.7699 | 820.3845 | 988.4375 | 971.4517 | 502.9896 | 597.8577 | 638.2819 | 551.0047 | 675.2442 | 809.2833 | 891.9681 | 1000.9346 | 564.1477 | 628.0996 | 620.777 | 727.9579 | 54.5988 | 0.00044722 | 19.5689 | 3.5385 | -28.4131 | 3.0961 | 8243.99 | -0.08 | 1.4887 | 1.5237 | -12.8205 | -1.3804 | 6.5051 | 28.6448 | -34.3737 | 56.1399 | 82.135 | 33.7669 | 40.566 | -0.98362 | 62.1947 | 31.3952
42838.4312 | 943 | 22.8018 | 22.7979 | 22.7955 | 22.7109 | 22.3159 | 21.6451 | 22.6618 | 21.6997 | 22.3132 | 22.3088 | 22.2714 | 21.9223 | 21.135 | 22.1109 | 21.4939 | 21.8979 | 22.5404 | 21.5693 | 33.211 | 40.7872 | 77.403 | 88.6549 | 88.4459 | 23.8843 | 44.2115 | 88.9596 | 645.6358 | 683.5861 | 646.6627 | 23.0136 | 47.7751 | 93.3082 | 23.7432 | 47.1141 | 90.7278 | 744.0792 | 798.3452 |  | 367.3462 | 768.6064 | 761.0131 | 690.0628 |  | 386.5294 | 627.3314 | 589.9738 | 865.7084 | 911.7315 | 924.236 | 924.1399 | 42.7688 | 239.87 | 63.8433 | 459.8804 | 70.9237 | 49.7978 | 49.3384 | 52.957 | 37.9381 |  |  | 0.26045 | 0.4264 | -39.8214 | 0.19578 | 7.7488 | 217.8199 | -203.0735 | -1.7542 | 11.433 | 33.5981 | 17.7384 | 0.00049612 | 0.00040906 | 0.00037949 | 26.0354 | 22.0834 | 22.1128 | 22.1615 | 21.9555 | 21.2302 | 20.0758 | 22.1429 | 22.3152 | 22.3555 | 22.289 | 21.8957 | 21.1285 | 22.2208 | 679.8769 | 552.2974 | 527.2527 | 349.6574 | 260.302 | 657.4566 | 411.0069 | 22.259 | 22.0954 | 22.4019 | 22.1366 | 28.8604 | 37.8365 | 25.3812 | 78.7931 | 85.7946 | 584.5234 | 578.0895 | 565.2585 | 560.3443 | 93.6577 | 58.7241 | 753.6117 | 21.9871 | 22.1437 | 338.9805 | 21.5079 | 21.9648 | 36.2466 | 86.894 | 92.763 | 23.4768 | 48.0158 | 92.5521 | 724.7939 | 639.8091 | 733.8176 | 750.8999 | 713.5001 |  | 723.09 | 711.2434 | 814.4289 | 593.3956 | 603.6434 | 715.5355 |  | 520.1026 |  |  | 464.1072 | 612.6461 | 681.9837 | [5 empty] | 21.8269 | 570.2301 | 21.8251 | 22.0373 | 415.6995 | 21.3425 | 21.8386 | 488.6669 | 602.0573 | 640.5747 |  | 917.1793 | 896.6043 | 530.571 | 664.6661 | 787.9705 | 574.986 | 635.0361 | 892.4386 | 920.5957 | 610.522 | 737.2515 | 818.0796 | 988.1233 | 971.8674 | 502.852 | 597.6143 | 638.258 | 551.5294 | 676.0814 | 810.1768 | 891.2638 | 999.8165 | 564.0356 | 628.1772 | 621.2807 | 728.2706 | 54.5517 | 0.00093874 | 19.5698 | 3.5634 | -28.4192 | 3.0961 | 8272.07 | -0.08 | 1.0786 | 1.3656 | -13.1966 | 0.92531 | 6.7128 | 35.5904 | -34.3645 | 56.1184 | 82.1942 | 33.7945 | 40.0342 | -0.49378 | 62.2102 | 31.3527
42838.4312 | 944 | 22.8006 | 22.7932 | 22.7908 | 22.7093 | 22.3125 | 21.6423 | 22.6594 | 21.694 | 22.3059 | 22.3099 | 22.2732 | 21.9165 | 21.1243 | 22.1085 | 21.4969 | 21.9081 | 22.5508 | 21.5849 | 33.3275 | 40.9104 | 77.5991 | 88.6565 | 88.4894 | 23.9006 | 44.3354 | 88.9725 | 647.2706 | 682.435 | 649.0776 | 23.0286 | 47.9262 | 93.3533 | 23.762 | 47.23 | 90.7631 | 743.8489 | 792.9576 |  | 368.7923 | 768.2137 | 760.994 | 690.0984 |  | 386.7612 | 627.266 | 587.5581 | 867.1623 | 912.7164 | 923.4568 | 920.9249 | 43.1909 | 240.3565 | 64.7672 | 460.6175 | 70.9372 | 49.8255 | 49.3568 | 52.9507 | 37.9904 |  |  | 0.16254 | -0.15843 | -42.0023 | -0.45017 | 7.5662 | 227.7338 | -203.0735 | -2.023 | 10.5056 | 31.0694 | 17.6726 | 0.00051255 | 0.00037784 | 0.00039756 | 26.0634 | 22.0765 | 22.1041 | 22.156 | 21.9558 | 21.2239 | 20.0684 | 22.1384 | 22.3181 | 22.347 | 22.2903 | 21.8852 | 21.1182 | 22.2152 | 691.2333 | 555.5123 | 577.1895 | 355.1535 | 253.3169 | 660.4771 | 413.5262 | 22.2534 | 22.099 | 22.4137 | 22.1351 | 28.953 | 37.9433 | 25.4087 | 78.828 | 85.8329 | 584.5765 | 557.5866 | 564.3628 | 560.3826 | 94.0594 | 39.8673 | 753.6594 | 21.9874 | 22.1462 | 339.8033 | 21.5041 | 21.9583 | 36.3897 | 86.9309 | 92.8202 | 23.4899 | 48.1451 | 92.5802 | 725.403 | 638.7462 | 732.9794 | 749.4422 | 716.6876 |  | 723.2584 | 710.349 | 814.5271 | 592.3823 | 603.5595 | 714.7204 |  | 520.8912 |  |  | 464.5378 | 612.7904 | 683.2785 | [5 empty] | 21.8364 | 569.4055 | 21.8349 | 22.0463 | 416.7253 | 21.3485 | 21.8451 | 489.048 | 602.2329 | 639.6039 |  | 915.6947 | 897.1437 | 531.1866 | 664.5276 | 788.0407 | 575.1992 | 634.3735 | 894.9693 | 916.4015 | 610.7842 | 739.324 | 814.8218 | 984.1434 | 972.1298 | 502.7194 | 597.0176 | 639.4674 | 551.9624 | 676.7069 | 811.3066 | 890.4784 | 996.6284 | 564.3773 | 628.0407 | 621.3291 | 728.0561 | 54.6207 | 0.00080535 | 19.5679 | 3.589 | -28.3831 | 3.0961 | 8270.69 | -0.03 | 0.85322 | -0.83235 | -13.5527 | -1.4031 | 6.631 | 36.3795 | -34.3534 | 56.0723 | 82.2504 | 33.8075 | 39.6628 | -5.5784 | 62.1478 | 31.3608
42838.4312 | 945 | 22.7965 | 22.7935 | 22.7912 | 22.7103 | 22.3109 | 21.6415 | 22.6627 | 21.6946 | 22.3072 | 22.3076 | 22.2754 | 21.912 | 21.1265 | 22.0998 | 21.4937 | 21.9091 | 22.5628 | 21.6014 | 33.4458 | 41.0252 | 77.8255 | 88.6696 | 88.5403 | 23.9234 | 44.4594 | 88.9921 | 647.38 | 681.4664 | 648.7812 | 23.0408 | 48.0714 | 93.3816 | 23.7797 | 47.3458 | 90.7952 | 743.7771 | 784.6366 |  | 369.6146 | 768.2909 | 761.2715 | 688.816 |  | 386.2372 | 626.6081 | 594.8266 | 864.304 | 911.631 | 925.8699 | 919.4971 | 42.9155 | 240.7507 | 65.9252 | 461.2974 | 71.073 | 49.8419 | 49.3905 | 52.9688 | 38.0943 |  |  | 0.64026 | 0.26212 | -43.5932 | -0.95286 | 7.5274 | 227.8994 | -203.0564 | -2.0552 | 10.0518 | 29.7336 | 17.2162 | 0.00041234 | 0.00036306 | 0.00041398 | 26.1047 | 22.0696 | 22.0997 | 22.1454 | 21.9396 | 21.2087 | 20.0455 | 22.129 | 22.3041 | 22.342 | 22.2833 | 21.8872 | 21.1157 | 22.1991 | 702.6033 | 555.445 | 556.6781 | 355.1688 | 258.4711 | 663.0222 | 414.9249 | 22.2519 | 22.1028 | 22.4193 | 22.1394 | 29.0382 | 38.0354 | 25.4401 | 78.8676 | 85.8572 | 584.7723 | 561.1519 | 565.5383 | 564.9454 | 85.1522 | 46.0223 | 753.5171 | 21.9815 | 22.142 | 340.5321 | 21.5075 | 21.9555 | 36.5577 | 86.9615 | 92.8741 | 23.5099 | 48.2886 | 92.5999 | 725.3146 | 638.7283 | 732.1569 | 748.0969 | 717.7516 |  | 723.5145 | 712.1418 | 815.0041 | 593.6265 | 603.584 | 714.6969 |  | 521.7857 |  |  | 466.0963 | 613.6198 | 684.2777 | [5 empty] | 21.8339 | 569.2634 | 21.8365 | 22.0462 | 418.1815 | 21.345 | 21.8424 | 489.4492 | 602.4157 | 639.6368 |  | 911.3724 | 896.2758 | 531.7539 | 664.6736 | 788.605 | 575.7605 | 634.3359 | 890.7373 | 914.1978 | 611.2631 | 739.9853 | 810.3523 | 980.6011 | 972.2175 | 502.5759 | 596.7073 | 640.8877 | 552.0053 | 677.1918 | 810.0584 | 889.6654 | 996.0778 | 564.6444 | 627.7336 | 620.9906 | 728.4772 | 55.8394 | -0.00017068 | 19.5702 | 3.6196 | -28.3659 | 3.0961 | 8239.8 | -0.02 | 1.6931 | 1.0702 | -13.8019 | -2.0405 | 6.6207 | 36.4294 | -34.3865 | 56.1074 | 82.3532 | 33.7773 | 39.1539 | -3.0409 | 62.1644 | 31.2675
42838.4312 | 946 | 22.7917 | 22.7928 | 22.7914 | 22.7081 | 22.3149 | 21.6316 | 22.6511 | 21.6958 | 22.303 | 22.3051 | 22.2656 | 21.9048 | 21.1328 | 22.1037 | 21.4983 | 21.9111 | 22.5673 | 21.6187 | 33.5694 | 41.1572 | 78.0343 | 88.6865 | 88.6062 | 23.9517 | 44.5915 | 89.0245 | 646.295 | 680.1674 | 647.1859 | 23.0506 | 48.2207 | 93.4056 | 23.7977 | 47.451 | 90.826 | 743.2495 | 777.7816 |  | 370.5029 | 770.0542 | 763.4051 | 683.6629 |  | 386.2429 | 624.779 | 592.0416 | 855.0809 | 907.0385 | 923.351 | 915.8716 | 42.6122 | 241.0716 | 66.7217 | 462.0372 | 70.9526 | 49.8321 | 49.4068 | 52.978 | 38.2102 |  |  | 0.66786 | -0.47187 | -44.364 | 0.13204 | 6.7027 | 227.7378 | -203.0564 | -2.0302 | 10.1979 | 30.748 | 17.1035 | 0.00037784 | 0.00031542 | 0.00041891 | 26.1435 | 22.0768 | 22.1011 | 22.1469 | 21.9462 | 21.2196 | 20.0543 | 22.1377 | 22.3048 | 22.3374 | 22.2806 | 21.8893 | 21.1194 | 22.2027 | 696.0065 | 572.0192 | 546.5468 | 365.1714 | 256.0973 | 665.1044 | 416.347 | 22.2636 | 22.1044 | 22.4321 | 22.1358 | 29.1339 | 38.1516 | 25.4852 | 78.9126 | 85.8888 | 585.0858 | 562.4374 | 566.4377 | 566.3734 | 79.6631 | 39.9649 | 756.1035 | 22.0022 | 22.1468 | 340.4444 | 21.5164 | 21.9591 | 36.7181 | 87.0278 | 92.9555 | 23.5324 | 48.425 | 92.6504 | 727.9551 | 640.7059 | 731.0539 | 746.7528 | 717.3286 |  | 723.8584 | 713.3659 | 815.2925 | 596.1322 | 603.6755 | 714.0913 |  | 522.7004 |  |  | 468.0279 | 614.707 | 685.2784 | [5 empty] | 21.8304 | 570.0353 | 21.8398 | 22.0399 | 420.0617 | 21.3444 | 21.8397 | 489.914 | 602.6422 | 640.5206 |  | 906.6144 | 895.1792 | 532.3063 | 665.2745 | 787.9151 | 576.1858 | 634.5051 | 887.5854 | 913.8446 | 611.5932 | 741.8134 | 806.4933 | 978.0313 | 971.6508 | 502.6154 | 596.6098 | 641.218 | 552.1008 | 677.3864 | 808.1182 | 887.6581 | 997.0428 | 564.7575 | 627.5596 | 620.6471 | 729.0397 | 55.3379 | 0.0019709 | 19.5688 | 3.6474 | -28.3922 | 3.0962 | 8181.59 | -0.14 | 1.7278 | -1.4345 | -13.9092 | 0.75882 | 6.2409 | 36.3782 | -34.3504 | 56.2059 | 82.4115 | 33.7243 | 40.507 | -1.6518 | 62.1671 | 31.2814
42838.4312 | 947 | 22.792 | 22.7817 | 22.7801 | 22.6978 | 22.3118 | 21.6309 | 22.6456 | 21.6906 | 22.2912 | 22.3006 | 22.2621 | 21.9019 | 21.1315 | 22.1 | 21.4981 | 21.9154 | 22.5751 | 21.6355 | 33.6794 | 41.2698 | 78.2396 | 88.7012 | 88.6532 | 23.9743 | 44.7058 | 89.0325 | 645.1951 | 678.9893 | 645.4861 | 23.0626 | 48.3662 | 93.4485 | 23.8235 | 47.5544 | 90.8845 | 742.5651 | 776.2858 |  | 371.5446 | 770.3975 | 763.6245 | 676.4607 |  | 386.2064 | 624.082 | 591.4754 | 854.8875 | 909.7048 | 923.1709 | 913.1513 | 42.7318 | 241.4143 | 66.8606 | 462.7775 | 70.9311 | 49.8353 | 49.4313 | 52.9894 | 38.2813 |  |  | 0.32616 | -0.52576 | -45.7124 | -0.2918 | 5.8872 | 204.0133 | -203.1484 | -2.046 | 10.2113 | 30.381 | 17.3587 | 0.00043698 | 0.00041234 | 0.00037949 | 26.1774 | 22.0805 | 22.1052 | 22.1469 | 21.9495 | 21.2243 | 20.0633 | 22.1375 | 22.3064 | 22.3461 | 22.2819 | 21.8924 | 21.1238 | 22.2069 | 684.6359 | 557.4982 | 516.0105 | 351.7089 | 253.1529 | 666.6054 | 417.1268 | 22.2489 | 22.0973 | 22.4278 | 22.1355 | 29.2213 | 38.2437 | 25.5091 | 78.9593 | 85.9104 | 585.1816 | 562.1034 | 566.2818 | 564.899 | 69.761 | 37.6174 | 758.1771 | 21.9953 | 22.1614 | 342.345 | 21.5072 | 21.9518 | 36.8751 | 87.0809 | 93.0125 | 23.556 | 48.5507 | 92.6727 | 728.6509 | 642.171 | 729.7477 | 745.4269 | 717.0972 |  | 724.1293 | 712.3249 | 815.2777 | 596.8615 | 603.7193 | 712.7554 |  | 523.6388 |  |  | 468.7657 | 615.6736 | 685.569 | [5 empty] | 21.829 | 571.3337 | 21.8397 | 22.047 | 420.6803 | 21.3479 | 21.8362 | 489.7876 | 602.5485 | 639.6448 |  | 904.0475 | 893.0248 | 532.8319 | 666.3131 | 788.0317 | 576.433 | 633.5534 | 889.3101 | 911.6869 | 611.9941 | 744.1759 | 801.7075 | 975.701 | 969.5773 | 502.5788 | 596.6138 | 641.2801 | 552.4567 | 677.1544 | 806.9134 | 885.4415 | 995.1294 | 565.1729 | 629.184 | 620.2103 | 728.9081 | 55.6718 | -3.0266e-05 | 19.5679 | 3.6802 | -28.3843 | 3.0962 | 8116.14 | -0.11 | 1.2063 | -1.5136 | -14.1136 | -1.1276 | 5.8485 | 34.4287 | -34.3556 | 56.2808 | 82.4357 | 33.7119 | 42.219 | 1.8858 | 62.1853 | 31.3388
42838.4313 | 948 | 22.7913 | 22.783 | 22.7817 | 22.6982 | 22.3128 | 21.6323 | 22.6468 | 21.6869 | 22.2956 | 22.2909 | 22.2651 | 21.9157 | 21.1203 | 22.1112 | 21.498 | 21.9196 | 22.5929 | 21.6448 | 33.8098 | 41.3879 | 78.4719 | 88.7241 | 88.6965 | 23.9823 | 44.8337 | 89.06 | 644.3458 | 676.4236 | 644.1575 | 23.0861 | 48.5143 | 93.5002 | 23.8446 | 47.6676 | 90.9273 | 741.5557 | 776.1378 |  | 372.1294 | 771.2022 | 764.7727 | 669.8167 |  | 386.2747 | 623.9425 | 591.7293 | 854.4216 | 909.7169 | 922.2005 | 914.4164 | 42.906 | 242.0074 | 67.2966 | 463.7016 | 71.0026 | 49.8417 | 49.4501 | 53.0202 | 38.428 |  |  | 0.36756 | -0.24977 | -46.3958 | -0.35817 | 6.9899 | 110.9078 | -203.2121 | -1.609 | 10.4075 | 30.6922 | 17.5874 | 0.00031377 | 0.00024806 | 0.00038606 | 26.2218 | 22.0826 | 22.1055 | 22.1506 | 21.946 | 21.2273 | 20.0638 | 22.1334 | 22.304 | 22.349 | 22.2872 | 21.8932 | 21.1241 | 22.2109 | 678.0626 | 566.113 | 542.0578 | 332.3163 | 252.6879 | 667.362 | 417.92 | 22.257 | 22.1038 | 22.4484 | 22.1448 | 29.317 | 38.3541 | 25.5448 | 79.0236 | 85.936 | 585.4509 | 563.6675 | 567.0986 | 567.0036 | 78.571 | 46.3149 | 758.2827 | 22.0081 | 22.151 | 342.6466 | 21.5175 | 21.9572 | 37.0349 | 87.1138 | 93.0627 | 23.5727 | 48.6895 | 92.7175 | 724.8457 | 641.5415 | 728.2089 | 743.8526 | 712.733 |  | 724.204 | 710.433 | 815.2563 | 597.7118 | 603.8608 | 711.4088 |  | 524.7067 |  |  | 469.3312 | 616.7109 | 684.6655 | [5 empty] | 21.8352 | 572.2114 | 21.834 | 22.046 | 420.1001 | 21.3379 | 21.8361 | 489.598 | 602.503 | 637.7835 |  | 909.5851 | 892.1252 | 533.1419 | 666.5568 | 787.9938 | 576.6941 | 633.9393 | 889.1183 | 909.7429 | 611.899 | 742.1995 | 797.4943 | 973.163 | 968.043 | 502.7671 | 597.0113 | 641.5918 | 552.7542 | 676.8855 | 804.5427 | 882.6313 | 992.4217 | 565.4141 | 629.63 | 619.8823 | 728.3508 | 55.5764 | 0.00050339 | 19.5697 | 3.7104 | -28.4882 | 3.0962 | 8063.54 | -0.13 | 1.2796 | -1.0432 | -14.2176 | -1.2492 | 6.3701 | 25.3744 | -34.347 | 56.4209 | 82.4814 | 33.7139 | 43.1761 | -0.86092 | 62.1023 | 31.3264
42838.4313 | 949 | 22.7879 | 22.7773 | 22.7825 | 22.6931 | 22.301 | 21.622 | 22.6481 | 21.6843 | 22.2884 | 22.2918 | 22.2607 | 21.9032 | 21.1197 | 22.1055 | 21.4961 | 21.918 | 22.5897 | 21.6616 | 33.9211 | 41.512 | 78.7119 | 88.7341 | 88.7467 | 24.0068 | 44.947 | 89.0767 | 642.9705 | 674.941 | 642.3731 | 23.1065 | 48.6716 | 93.554 | 23.8776 | 47.793 | 90.9761 | 740.6065 | 780.6282 |  | 372.9748 | 775.7592 | 769.6236 | 670.6952 |  | 385.4055 | 623.6492 | 589.2201 | 855.8888 | 906.5827 | 919.128 | 914.0153 | 43.0158 | 242.5264 | 67.7656 | 464.2811 | 70.9852 | 49.8689 | 49.4716 | 53.0413 | 38.5793 |  |  | 0.50752 | -0.28854 | -46.9734 | -0.30297 | 7.072 | 52.9981 | -203.3738 | -2.0138 | 10.2946 | 31.0079 | 17.4816 | 0.00033677 | 0.00035484 | 0.00036306 | 26.26 | 22.0834 | 22.0964 | 22.1515 | 21.941 | 21.2208 | 20.0559 | 22.1312 | 22.307 | 22.3434 | 22.2839 | 21.8846 | 21.1188 | 22.2065 | 694.6381 | 550.0124 | 539.5727 | 325.9547 | 254.9471 | 669.3367 | 419.2996 | 22.2532 | 22.1073 | 22.4551 | 22.1484 | 29.4043 | 38.4387 | 25.5718 | 79.0858 | 85.9625 | 585.6955 | 563.4786 | 567.1089 | 566.1344 | 64.2544 | 50.6269 | 756.9725 | 21.9935 | 22.1367 | 342.9081 | 21.5076 | 21.9675 | 37.1874 | 87.1471 | 93.1277 | 23.5979 | 48.8159 | 92.7664 | 722.9232 | 640.5856 | 726.2491 | 741.5126 | 710.1678 |  | 724.2193 | 708.6256 | 815.0985 | 596.1591 | 603.8418 | 710.2308 |  | 525.5365 |  |  | 469.5218 | 615.7191 | 683.547 | [5 empty] | 21.8346 | 571.752 | 21.848 | 22.0443 | 419.4134 | 21.342 | 21.845 | 490.0364 | 603.3309 | 637.0376 |  | 910.3518 | 891.6131 | 533.5078 | 666.2741 | 787.618 | 577.0031 | 634.8818 | 890.1246 | 910.8626 | 611.6782 | 740.8269 | 793.9572 | 969.9991 | 969.0546 | 503.0632 | 597.7166 | 641.6961 | 552.6932 | 676.7508 | 802.8335 | 880.7507 | 994.0913 | 565.5509 | 629.7116 | 619.6176 | 727.6866 | 53.793 | -0.0017857 | 19.5716 | 3.7311 | -28.3981 | 3.0962 | 8023.32 | -0.08 | 1.5022 | -1.121 | -14.3034 | -1.1487 | 6.3992 | 17.5181 | -34.3165 | 56.496 | 82.4811 | 33.7536 | 41.9275 | -0.32794 | 61.8269 | 31.3925
42838.4313 | 950 | 22.7903 | 22.7895 | 22.7861 | 22.6974 | 22.305 | 21.6322 | 22.6461 | 21.6862 | 22.2944 | 22.2978 | 22.2658 | 21.9081 | 21.1258 | 22.1032 | 21.4741 | 21.9207 | 22.5938 | 21.6614 | 34.046 | 41.6373 | 78.9105 | 88.7306 | 88.8063 | 24.01 | 45.0501 | 89.0756 | 641.3942 | 674.6002 | 640.7846 | 23.1139 | 48.8046 | 93.588 | 23.8913 | 47.9074 | 91.0189 | 739.9304 | 773.2132 |  | 373.6953 | 781.0011 | 774.4678 | 673.0899 |  | 384.4734 | 622.865 | 588.248 | 860.0864 | 904.8127 | 916.5446 | 909.9971 | 42.86 | 243.1336 | 66.9131 | 464.8668 | 71.0583 | 49.9225 | 49.4777 | 53.0508 | 38.7108 |  |  | 0.61069 | 0.53548 | -46.9754 | -0.47974 | 7.3381 | 47.4698 | -203.36 | -2.1432 | 10.1037 | 30.1033 | 17.7618 | 0.00048791 | 0.00032856 | 0.00036963 | 26.3042 | 22.0887 | 22.1036 | 22.1493 | 21.9506 | 21.2202 | 20.0641 | 22.1409 | 22.3075 | 22.3421 | 22.2886 | 21.8951 | 21.1234 | 22.2146 | 683.6042 | 534.0049 | 538.4187 | 349.1628 | 261.1549 | 669.8946 | 420.8123 | 22.2525 | 22.1061 | 22.4684 | 22.1459 | 29.4918 | 38.5515 | 25.6114 | 79.1299 | 85.9825 | 585.8166 | 562.8533 | 566.2759 | 565.8811 | 52.516 | 35.7413 | 754.8116 | 22.0019 | 22.1481 | 343.1178 | 21.5097 | 21.9619 | 37.3568 | 87.1979 | 93.1919 | 23.617 | 48.9478 | 92.827 | 723.0319 | 640.1716 | 725.2109 | 739.9697 | 712.1646 |  | 724.3568 | 708.1589 | 815.0694 | 594.9893 | 603.8376 | 709.7868 |  | 526.2732 |  |  | 469.1367 | 613.7336 | 684.6475 | [5 empty] | 21.8316 | 571.2885 | 21.8358 | 22.0405 | 419.4165 | 21.3327 | 21.8324 | 490.848 | 603.7888 | 636.0625 |  | 918.9265 | 892.817 | 533.525 | 666.5583 | 786.4577 | 577.3254 | 635.6157 | 886.0613 | 914.6446 | 611.4201 | 741.8361 | 789.8428 | 970.4704 | 970.3439 | 502.8816 | 598.8869 | 641.4686 | 553.2724 | 676.9433 | 800.8409 | 881.2314 | 995.5971 | 565.9809 | 629.7268 | 619.7639 | 727.1036 | 53.8279 | -0.0057459 | 19.5695 | 3.7577 | -28.4531 | 3.0961 | 8071.42 | -0.05 | 1.6464 | 1.5265 | -14.2975 | -1.4449 | 6.5115 | 16.5613 | -34.2782 | 56.4753 | 82.4847 | 33.7853 | 43.3215 | 0.08264 | 61.582 | 31.4203
42838.4313 | 951 | 22.79 | 22.7912 | 22.7819 | 22.7001 | 22.3035 | 21.6319 | 22.6441 | 21.6876 | 22.3002 | 22.3009 | 22.2769 | 21.908 | 21.1226 | 22.1037 | 21.4843 | 21.9258 | 22.6123 | 21.6905 | 34.154 | 41.7556 | 79.0814 | 88.7491 | 88.8541 | 24.0489 | 45.1816 | 89.0985 | 640.0811 | 673.3369 | 639.6553 | 23.126 | 48.954 | 93.632 | 23.9116 | 48.0132 | 91.0651 | 739.3014 | 760.7106 |  | 374.5972 | 788.6248 | 781.0303 | 672.179 |  | 384.3859 | 622.7544 | 590.3428 | 859.7008 | 905.2587 | 915.2038 | 910.8187 | 42.4047 | 243.7218 | 66.6023 | 465.4902 | 70.9569 | 49.9971 | 49.4982 | 53.0763 | 38.7986 |  |  | 0.63237 | -0.33256 | -47.2566 | -0.009902 | 8.1878 | 84.6915 | -203.2883 | -2.0092 | 10.5595 | 32.1027 | 17.8837 | 0.00036963 | 0.00026942 | 0.0003647 | 26.3433 | 22.0854 | 22.1056 | 22.1532 | 21.9566 | 21.2209 | 20.0606 | 22.133 | 22.3042 | 22.3452 | 22.2839 | 21.8949 | 21.1236 | 22.2104 | 644.198 | 502.0822 | 500.6629 | 349.6118 | 263.8885 | 669.0092 | 421.3679 | 22.2469 | 22.1121 | 22.473 | 22.1469 | 29.5975 | 38.665 | 25.6428 | 79.1699 | 86.0095 | 585.9696 | 562.6863 | 565.6897 | 565.8978 | 88.6544 | 45.0936 | 754.2745 | 22.0029 | 22.1425 | 343.3765 | 21.5045 | 21.9545 | 37.513 | 87.2213 | 93.2609 | 23.6335 | 49.0652 | 92.8578 | 722.1183 | 640.2621 | 724.8724 | 739.7315 | 712.6474 |  | 724.27 | 707.7116 | 814.9693 | 596.263 | 603.9443 | 709.0027 |  | 527.1394 |  |  | 468.495 | 612.3408 | 684.3278 | [5 empty] | 21.8425 | 571.5196 | 21.846 | 22.0392 | 420.5426 | 21.3505 | 21.8381 | 491.4126 | 603.7977 | 634.8575 |  | 913.962 | 893.6498 | 533.1217 | 666.7029 | 786.3662 | 577.3748 | 635.5582 | 879.4638 | 911.2829 | 611.1751 | 739.9895 | 787.0603 | 970.4696 | 971.4328 | 502.9395 | 599.2529 | 640.6289 | 553.6714 | 676.383 | 798.829 | 882.7911 | 996.5209 | 566.0322 | 629.3903 | 620.0822 | 727.5785 | 54.6313 | -0.0045874 | 19.571 | 3.7802 | -28.5245 | 3.0961 | 8143.69 | -0.11 | 1.6743 | -1.2029 | -14.3393 | -0.20757 | 6.8742 | 22.1085 | -34.2528 | 56.44 | 82.4651 | 33.7692 | 47.4334 | 4.3816 | 61.4417 | 31.4461
42838.4313 | 952 | 22.7961 | 22.7863 | 22.7825 | 22.6981 | 22.3061 | 21.6257 | 22.644 | 21.6849 | 22.2914 | 22.302 | 22.2701 | 21.9015 | 21.1223 | 22.1027 | 21.4887 | 21.9265 | 22.6166 | 21.7088 | 34.2805 | 41.8711 | 79.231 | 88.747 | 88.8941 | 24.0717 | 45.2983 | 89.1092 | 639.1255 | 671.6749 | 638.8641 | 23.1435 | 49.0943 | 93.6626 | 23.9408 | 48.1204 | 91.1204 | 738.802 | 757.4362 |  | 375.3648 | 790.5608 | 783.0012 | 672.9647 |  | 384.7986 | 623.7199 | 587.8371 | 855.1465 | 903.5772 | 914.6472 | 911.77 | 42.4068 | 244.3003 | 66.1418 | 466.2797 | 71.0444 | 50.0835 | 49.5157 | 53.1051 | 38.8782 |  |  | 0.39976 | -0.63484 | -47.5333 | -0.21623 | 6.9603 | 101.051 | -203.3179 | -2.3206 | 11.2902 | 32.2615 | 18.2365 | 0.00051584 | 0.00034827 | 0.00037949 | 26.3767 | 22.0789 | 22.1096 | 22.1516 | 21.9437 | 21.2154 | 20.0584 | 22.128 | 22.3034 | 22.3401 | 22.2797 | 21.8869 | 21.1194 | 22.2044 | 658.7823 | 504.5462 | 503.9439 | 359.8276 | 280.3595 | 670.7887 | 422.6507 | 22.25 | 22.1021 | 22.485 | 22.1537 | 29.6864 | 38.7689 | 25.6724 | 79.2009 | 86.0247 | 586.0288 | 562.2836 | 564.7312 | 564.3877 | 89.6034 | 49.2358 | 754.2377 | 21.9986 | 22.1474 | 343.9194 | 21.5124 | 21.9529 | 37.6609 | 87.2686 | 93.331 | 23.6499 | 49.2065 | 92.8879 | 721.4037 | 640.2833 | 724.2912 | 738.7154 | 711.5115 |  | 724.198 | 707.7702 | 814.854 | 599.0419 | 604.1883 | 708.0603 |  | 527.9426 |  |  | 467.9288 | 612.2728 | 682.8243 | [5 empty] | 21.8318 | 572.2802 | 21.8453 | 22.0358 | 422.4862 | 21.3447 | 21.8347 | 491.4633 | 603.9238 | 633.9933 |  | 906.5085 | 892.2745 | 532.9034 | 666.3134 | 785.884 | 577.32 | 635.3826 | 881.8498 | 909.3275 | 610.9057 | 741.1677 | 784.9908 | 974.1321 | 974.1555 | 502.9701 | 599.2357 | 640.3086 | 554.3022 | 675.7067 | 798.3766 | 882.6694 | 998.9459 | 565.7323 | 628.9103 | 620.449 | 729.7021 | 53.8524 | -0.0010835 | 19.569 | 3.8001 | -28.3987 | 3.0962 | 8262.53 | -0.05 | 1.3307 | -1.6629 | -14.389 | -0.9705 | 6.3365 | 24.144 | -34.2473 | 56.4533 | 82.4266 | 33.7362 | 46.3491 | 4.2573 | 61.2885 | 31.4982
42838.4313 | 953 | 22.7883 | 22.7788 | 22.7738 | 22.69 | 22.3046 | 21.6304 | 22.6409 | 21.6869 | 22.2873 | 22.2968 | 22.2592 | 21.8999 | 21.1185 | 22.1001 | 21.4987 | 21.942 | 22.6369 | 21.7343 | 34.4055 | 42.0011 | 79.3848 | 88.7425 | 88.9538 | 24.1005 | 45.4125 | 89.1364 | 639.2097 | 670.1548 | 639.392 | 23.156 | 49.235 | 93.6779 | 23.9526 | 48.2285 | 91.1669 | 738.4723 | 762.7345 |  | 376.2254 | 791.6146 | 783.8603 | 674.5144 |  | 385.1991 | 625.3613 | 585.8952 | 850.6406 | 902.7012 | 912.0996 | 909.7963 | 42.6964 | 245.0232 | 65.5673 | 466.9839 | 71.0156 | 50.1524 | 49.5291 | 53.1358 | 38.9828 |  |  | 0.43853 | 0.93107 | -47.5918 | -0.59342 | 8.0919 | 62.7431 | -203.3343 | -1.7509 | 11.0619 | 31.5421 | 18.1667 | 0.00047312 | 0.00028913 | 0.0003417 | 26.4249 | 22.0791 | 22.0992 | 22.1478 | 21.9434 | 21.2144 | 20.0571 | 22.1287 | 22.3055 | 22.3405 | 22.2788 | 21.8816 | 21.1113 | 22.2098 | 672.0576 | 532.0289 | 499.5038 | 376.7267 | 298.6112 | 673.4197 | 424.4065 | 22.2529 | 22.108 | 22.5004 | 22.1553 | 29.7801 | 38.8684 | 25.7041 | 79.2369 | 86.0544 | 586.0409 | 561.4733 | 564.1467 | 564.3533 | 88.6713 | 58.5191 | 754.2096 | 21.9999 | 22.142 | 345.0389 | 21.5067 | 21.9644 | 37.8405 | 87.3171 | 93.3925 | 23.6714 | 49.3364 | 92.9252 | 722.4593 | 640.099 | 723.8036 | 737.5998 | 712.1285 |  | 724.309 | 705.6358 | 814.3954 | 598.6031 | 604.3019 | 706.632 |  | 528.6259 |  |  | 468.0854 | 612.6651 | 683.7101 | [5 empty] | 21.8377 | 572.6249 | 21.8476 | 22.0446 | 423.8549 | 21.3496 | 21.8346 | 490.5824 | 604.6652 | 632.9126 |  | 905.3729 | 889.1728 | 532.7622 | 666.5663 | 784.725 | 577.2042 | 634.9479 | 881.0862 | 905.3313 | 611.331 | 741.5334 | 780.8949 | 976.2206 | 974.8711 | 502.88 | 599.3202 | 640.5036 | 554.4825 | 675.8535 | 799.0277 | 880.6378 | 999.8549 | 565.57 | 629.4927 | 620.9455 | 731.534 | 55.0895 | -0.0013012 | 19.57 | 3.8228 | -28.3863 | 3.0962 | 8375.81 | -0.2 | 1.3941 | 2.0157 | -14.411 | -1.6092 | 6.8249 | 19.0044 | -34.2119 | 56.4642 | 82.3393 | 33.7689 | 45.6704 | 5.0804 | 61.1589 | 31.5012
42838.4313 | 954 | 22.7837 | 22.7764 | 22.7773 | 22.6888 | 22.2985 | 21.6278 | 22.6387 | 21.6839 | 22.2909 | 22.2982 | 22.2589 | 21.8981 | 21.1202 | 22.0914 | 21.4935 | 21.9443 | 22.6422 | 21.7473 | 34.5251 | 42.1189 | 79.5103 | 88.7371 | 89.0029 | 24.1246 | 45.5279 | 89.1512 | 640.1087 | 669.2686 | 640.2652 | 23.1593 | 49.3704 | 93.7111 | 23.9729 | 48.3364 | 91.2172 | 738.2122 | 754.5136 |  | 377.2438 | 794.0129 | 785.4407 | 673.553 |  | 384.0873 | 624.7614 | 585.8302 | 848.7249 | 902.4295 | 910.4546 | 908.9994 | 43.0936 | 245.6865 | 65.1328 | 467.6175 | 71.0881 | 50.2221 | 49.5504 | 53.1664 | 39.1519 |  |  | 0.35836 | -0.84709 | -47.4991 | -0.25501 | 7.5254 | 23.2702 | -203.3738 | -2.3029 | 11.2024 | 32.6383 | 18.2903 | 0.0002957 | 0.00029406 | 0.00037127 | 26.4691 | 22.0888 | 22.1059 | 22.1517 | 21.9471 | 21.216 | 20.0609 | 22.1326 | 22.3071 | 22.3456 | 22.2889 | 21.8857 | 21.1182 | 22.2096 | 666.646 | 544.6217 | 523.0732 | 391.8642 | 303.2481 | 675.8188 | 426.7184 | 22.2443 | 22.1121 | 22.5068 | 22.156 | 29.8673 | 38.9674 | 25.7415 | 79.2794 | 86.0729 | 586.1548 | 561.4472 | 564.9323 | 566.8325 | 98.4996 | 45.8812 | 751.5106 | 22.0025 | 22.145 | 347.3644 | 21.5054 | 21.9565 | 37.998 | 87.35 | 93.4664 | 23.7083 | 49.4732 | 92.9796 | 722.7071 | 639.5713 | 722.1756 | 735.9932 | 713.4663 |  | 724.6017 | 702.9013 | 813.5451 | 596.6275 | 604.2967 | 704.8255 |  | 529.2782 |  |  | 468.2579 | 613.5388 | 685.3109 | [5 empty] | 21.8357 | 571.7776 | 21.8498 | 22.0467 | 424.3298 | 21.3532 | 21.8382 | 489.8004 | 604.756 | 631.751 |  | 904.5076 | 888.0362 | 532.8148 | 666.8468 | 784.5043 | 576.5213 | 634.4364 | 883.5884 | 906.442 | 611.8788 | 739.9367 | 777.9854 | 975.8702 | 971.9288 | 502.6556 | 599.42 | 641.1231 | 554.6661 | 676.5907 | 800.7108 | 879.4833 | 1002.4257 | 565.4454 | 631.1735 | 621.042 | 733.3261 | 54.9878 | -2.3207e-05 | 19.5697 | 3.8502 | -28.4374 | 3.0963 | 8432.28 | -0.09 | 1.2608 | -1.922 | -14.3922 | -1.0545 | 6.5771 | 11.5657 | -34.1915 | 56.5011 | 82.1438 | 33.8228 | 47.0015 | 2.8974 | 61.1173 | 31.4519
42838.4313 | 955 | 22.78 | 22.7829 | 22.7827 | 22.6932 | 22.3089 | 21.6236 | 22.6435 | 21.6825 | 22.2922 | 22.2976 | 22.2685 | 21.9088 | 21.1248 | 22.0929 | 21.487 | 21.9429 | 22.6495 | 21.7589 | 34.6397 | 42.232 | 79.6515 | 88.7374 | 89.0529 | 24.1466 | 45.642 | 89.1699 | 640.3733 | 668.3746 | 639.7883 | 23.182 | 49.5098 | 93.7668 | 23.9993 | 48.4461 | 91.2824 | 737.9197 | 758.6498 |  | 377.9082 | 794.12 | 785.3388 | 674.0744 |  | 384.6583 | 623.3412 | 585.3557 | 853.964 | 903.1109 | 910.751 | 907.5746 | 43.1173 | 246.3087 | 63.511 | 468.3255 | 71.0668 | 50.3123 | 49.5624 | 53.2099 | 39.2705 |  |  | 0.63041 | 0.34098 | -46.7953 | -0.51259 | 5.9746 | -2.0886 | -203.4355 | -2.1708 | 10.9773 | 32.2587 | 18.2108 | 0.00042384 | 0.0003417 | 0.00037784 | 26.5088 | 22.0945 | 22.1117 | 22.1529 | 21.9501 | 21.221 | 20.0645 | 22.1357 | 22.3075 | 22.3488 | 22.2893 | 21.8872 | 21.1263 | 22.2075 | 685.6768 | 557.4795 | 518.7931 | 385.8997 | 306.0405 | 678.7713 | 428.8712 | 22.2575 | 22.1093 | 22.5193 | 22.1594 | 29.9721 | 39.0804 | 25.7762 | 79.3541 | 86.1096 | 586.424 | 562.2814 | 566.4425 | 569.2528 | 74.8205 | 42.5826 | 749.3989 | 22.004 | 22.1358 | 348.8183 | 21.502 | 21.9507 | 38.1638 | 87.3787 | 93.5303 | 23.719 | 49.5854 | 93.0129 | 725.3955 | 639.6787 | 720.0828 | 734.3219 | 718.1333 |  | 725.0371 | 702.9723 | 813.064 | 595.5876 | 604.2911 | 704.264 |  | 529.9828 |  |  | 468.4713 | 615.404 | 688.7463 | [5 empty] | 21.8364 | 571.5426 | 21.8432 | 22.0481 | 423.9116 | 21.3568 | 21.8407 | 488.9355 | 604.7891 | 630.748 |  | 910.0101 | 890.2037 | 533.123 | 667.3652 | 782.4066 | 576.3379 | 634.4057 | 885.5947 | 912.8062 | 612.3646 | 741.4658 | 777.9348 | 975.9914 | 972.1217 | 502.8536 | 598.9718 | 642.6157 | 555.3415 | 677.5765 | 801.1853 | 881.951 | 1006.988 | 565.3408 | 631.5138 | 620.9395 | 737.1387 | 54.2575 | -0.00029004 | 19.5698 | 3.8767 | -28.3654 | 3.0963 | 8419.25 | -0.03 | 1.6719 | 1.2184 | -14.2739 | -1.4939 | 5.8611 | -3.4654 | -34.2009 | 56.4817 | 81.9886 | 33.8507 | 45.79 | 3.7803 | 61.0261 | 31.4309
42838.4313 | 956 | 22.7974 | 22.7867 | 22.7845 | 22.7022 | 22.3124 | 21.637 | 22.6513 | 21.6973 | 22.3009 | 22.3067 | 22.2698 | 21.9094 | 21.1257 | 22.1101 | 21.4919 | 21.9505 | 22.6616 | 21.7861 | 34.7675 | 42.3575 | 79.8247 | 88.7462 | 89.0987 | 24.1713 | 45.7545 | 89.1936 | 640.0778 | 669.0652 | 639.5732 | 23.1977 | 49.6616 | 93.8233 | 24.026 | 48.559 | 91.3401 | 737.688 | 757.3382 |  | 378.4512 | 795.0876 | 786.7789 | 675.0135 |  | 385.5172 | 623.6524 | 587.8512 | 854.9236 | 906.4646 | 910.8045 | 905.819 | 43.6401 | 246.8852 | 61.6986 | 468.9605 | 71.0352 | 50.3831 | 49.5792 | 53.2453 | 39.354 |  |  | 0.64815 | 0.28644 | -46.5864 | -0.019102 | 6.8834 | -16.7613 | -203.45 | -1.4723 | 11.4241 | 32.8745 | 18.1953 | 0.00039427 | 0.00025956 | 0.00035649 | 26.5436 | 22.0923 | 22.1023 | 22.1485 | 21.9471 | 21.2149 | 20.0582 | 22.1318 | 22.3056 | 22.3437 | 22.2804 | 21.8874 | 21.1202 | 22.2028 | 677.1344 | 569.2467 | 508.9089 | 363.8034 | 288.0461 | 680.1838 | 430.0237 | 22.2478 | 22.1138 | 22.5224 | 22.1572 | 30.0669 | 39.1771 | 25.8112 | 79.4125 | 86.1388 | 586.6824 | 564.3569 | 567.7195 | 569.8807 | 81.1011 | 50.8833 | 749.3619 | 22.002 | 22.139 | 350.2333 | 21.5073 | 21.9606 | 38.325 | 87.4233 | 93.5956 | 23.7406 | 49.7148 | 93.0594 | 725.7762 | 639.9088 | 718.267 | 732.9353 | 719.3043 |  | 725.4589 | 703.3325 | 812.9326 | 596.4786 | 604.2903 | 704.2257 |  | 530.6303 |  |  | 469.1235 | 618.0115 | 690.9556 | [5 empty] | 21.8337 | 571.9856 | 21.8521 | 22.0475 | 422.9318 | 21.3612 | 21.8432 | 488.2439 | 604.8533 | 629.4895 |  | 913.9405 | 892.5899 | 533.8123 | 667.9739 | 782.2021 | 576.4772 | 634.5358 | 884.1134 | 918.0901 | 612.8444 | 744.3952 | 778.7166 | 976.2586 | 975.5602 | 502.7095 | 598.6477 | 643.2525 | 555.8142 | 677.8803 | 803.1071 | 884.7914 | 1008.4556 | 565.3138 | 631.2088 | 620.5646 | 737.6116 | 54.5003 | -0.00016366 | 19.5687 | 3.8849 | -28.4074 | 3.0962 | 8399.15 | -0.07 | 1.695 | 1.1169 | -14.2444 | -0.28844 | 6.2912 | -9.8172 | -34.2029 | 56.5561 | 81.9367 | 33.8258 | 47.173 | 5.0972 | 60.9393 | 31.4579
42838.4314 | 957 | 22.7907 | 22.7826 | 22.7849 | 22.6958 | 22.3042 | 21.6328 | 22.6424 | 21.6907 | 22.2955 | 22.2996 | 22.2595 | 21.8983 | 21.1235 | 22.1034 | 21.4965 | 21.961 | 22.6721 | 21.8091 | 34.8869 | 42.4831 | 80.0051 | 88.7531 | 89.1483 | 24.1948 | 45.8731 | 89.2154 | 640.5274 | 669.1871 | 639.7236 | 23.208 | 49.7992 | 93.811 | 24.0463 | 48.6609 | 91.4028 | 737.357 | 749.5459 |  | 379.1504 | 798.5964 | 794.1807 | 672.2139 |  | 385.4989 | 624.9658 | 589.9449 | 858.5207 | 908.3371 | 911.5316 | 903.5529 | 44.192 | 247.411 | 60.5883 | 469.6716 | 71.0414 | 50.4407 | 49.5912 | 53.2898 | 39.3597 |  |  | 0.51475 | 0.35806 | -45.6106 | -0.13147 | 7.0668 | -35.9774 | -203.4559 | -2.0276 | 11.6029 | 33.8593 | 18.6956 | 0.00027928 | 0.00023328 | 0.00039756 | 26.59 | 22.0883 | 22.1073 | 22.1532 | 21.9418 | 21.2179 | 20.0602 | 22.1281 | 22.3039 | 22.3408 | 22.2824 | 21.8902 | 21.118 | 22.2095 | 679.8913 | 571.1949 | 536.2302 | 358.3342 | 282.7969 | 681.692 | 431.8549 | 22.2469 | 22.1139 | 22.5352 | 22.1599 | 30.1567 | 39.2755 | 25.8491 | 79.4748 | 86.1515 | 586.7702 | 564.0382 | 567.7332 | 567.9656 | 81.0059 | 57.5528 | 749.7464 | 22.0082 | 22.1442 | 350.2729 | 21.5078 | 21.9618 | 38.5028 | 87.4697 | 93.6594 | 23.7653 | 49.8473 | 93.1126 | 727.0995 | 639.799 | 716.9036 | 731.9503 | 721.7742 |  | 725.9432 | 703.3507 | 812.8585 | 598.1367 | 604.3766 | 704.1637 |  | 531.179 |  |  | 469.8638 | 620.1379 | 692.3775 | [5 empty] | 21.8422 | 572.994 | 21.8523 | 22.0466 | 423.7735 | 21.3604 | 21.8446 | 487.861 | 604.7288 | 628.2998 |  | 918.8497 | 894.2897 | 533.9064 | 668.2318 | 781.8395 | 576.7464 | 634.8712 | 883.1256 | 920.5553 | 612.9435 | 744.1471 | 779.2737 | 977.6091 | 979.6273 | 502.2571 | 598.6656 | 643.636 | 556.223 | 677.717 | 803.359 | 886.5919 | 1010.9866 | 565.1992 | 631.411 | 620.1968 | 737.2889 | 53.3851 | -1.6191e-05 | 19.5701 | 3.8861 | -28.3585 | 3.0962 | 8342.21 | -0.08 | 1.5107 | 1.2497 | -14.1048 | -0.75725 | 6.3764 | -14.3874 | -34.2139 | 56.6104 | 81.9126 | 33.7954 | 47.3314 | 2.41 | 60.9303 | 31.5262
42838.4314 | 958 | 22.781 | 22.782 | 22.7792 | 22.6974 | 22.3035 | 21.6246 | 22.6424 | 21.6876 | 22.2896 | 22.2988 | 22.2683 | 21.9042 | 21.1177 | 22.1029 | 21.4991 | 21.965 | 22.6833 | 21.8249 | 35.0044 | 42.5984 | 80.1651 | 88.7462 | 89.1936 | 24.2123 | 45.9828 | 89.2355 | 640.3205 | 668.1728 | 639.479 | 23.2257 | 49.9368 | 93.7982 | 24.0744 | 48.7717 | 91.454 | 737.1596 | 752.2935 |  | 380.2103 | 797.7981 | 792.9854 | 674.5851 |  | 384.9641 | 625.8048 | 587.3588 | 863.0691 | 916.0529 | 912.9609 | 904.6674 | 44.3741 | 248.1963 | 59.1667 | 470.5766 | 71.0415 | 50.4921 | 49.6063 | 53.3308 | 39.4421 |  |  | 0.39384 | -0.81883 | -44.6144 | -0.051298 | 7.2941 | -57.4782 | -203.4677 | -2.7524 | 11.1952 | 32.2976 | 18.5527 | 0.00043534 | 0.00030885 | 0.00034992 | 26.6315 | 22.0902 | 22.1084 | 22.1565 | 21.9477 | 21.2161 | 20.0574 | 22.1351 | 22.3047 | 22.3414 | 22.2837 | 21.8838 | 21.1172 | 22.2035 | 692.1656 | 602.1822 | 570.5658 | 369.2907 | 283.373 | 684.1726 | 434.1113 | 22.2519 | 22.1176 | 22.5513 | 22.1706 | 30.2519 | 39.3862 | 25.8874 | 79.5306 | 86.1833 | 586.8148 | 563.6033 | 567.4908 | 566.3664 | 89.0276 | 45.5486 | 749.8489 | 22.0168 | 22.1494 | 350.1706 | 21.5151 | 21.9617 | 38.6708 | 87.5122 | 93.7322 | 23.7907 | 49.9815 | 93.1562 | 726.2625 | 640.0163 | 716.2172 | 731.3941 | 721.2098 |  | 726.3576 | 702.21 | 812.5144 | 600.8804 | 604.6006 | 703.4492 |  | 531.6914 |  |  | 470.2789 | 620.7726 | 692.8192 | [5 empty] | 21.839 | 574.0762 | 21.8519 | 22.0456 | 425.0943 | 21.3593 | 21.8428 | 487.5727 | 604.9821 | 627.7471 |  | 919.6698 | 895.2832 | 533.4518 | 668.2909 | 780.256 | 576.7528 | 635.0171 | 884.1136 | 921.8474 | 612.6733 | 743.2649 | 778.9217 | 980.781 | 983.3058 | 501.9313 | 598.7951 | 644.3284 | 556.5115 | 678.1819 | 803.5931 | 885.734 | 1013.3421 | 565.1492 | 631.9081 | 620.0961 | 737.2667 | 53.5307 | 0.0011073 | 19.5691 | 3.8846 | -28.493 | 3.0962 | 8381.14 | -0.16 | 1.3212 | -1.8907 | -13.9564 | -0.47325 | 6.4821 | -18.1962 | -34.2356 | 56.7314 | 81.8348 | 33.7597 | 46.7349 | -0.97422 | 60.8128 | 31.5783
42838.4314 | 959 | 22.7827 | 22.7884 | 22.783 | 22.6976 | 22.3063 | 21.6272 | 22.6466 | 21.6854 | 22.2966 | 22.2971 | 22.2685 | 21.9134 | 21.121 | 22.1012 | 21.4893 | 21.9645 | 22.6885 | 21.8399 | 35.1271 | 42.7082 | 80.2968 | 88.7359 | 89.2317 | 24.2343 | 46.0924 | 89.2508 | 640.134 | 667.3355 | 639.4978 | 23.2336 | 50.0741 | 93.7924 | 24.0922 | 48.8764 | 91.4889 | 736.9733 | 759.8168 |  | 381.046 | 787.9543 | 784.0533 | 674.4833 |  | 385.5214 | 626.3565 | 588.6812 | 862.3477 | 918.596 | 913.4483 | 908.1337 | 43.9567 | 248.8498 | 58.7325 | 471.1132 | 71.0537 | 50.5334 | 49.6177 | 53.3595 | 39.5256 |  |  | 0.40436 | 0.024903 | -43.1694 | -0.45214 | 7.6286 | 33.6776 | -203.3724 | -1.3731 | 11.058 | 32.1069 | 18.6059 | 0.00036799 | 0.00022835 | 0.00038277 | 26.666 | 22.0765 | 22.098 | 22.1361 | 21.9407 | 21.2065 | 20.0475 | 22.1248 | 22.2961 | 22.3355 | 22.2795 | 21.8745 | 21.1164 | 22.2004 | 717.4637 | 592.096 | 554.657 | 355.8688 | 284.4116 | 686.6462 | 435.7106 | 22.2446 | 22.1135 | 22.5543 | 22.1649 | 30.3337 | 39.4802 | 25.9156 | 79.548 | 86.1951 | 586.9714 | 564.5064 | 568.0552 | 568.3051 | 76.0565 | 38.5475 | 749.2589 | 22.0043 | 22.1446 | 350.2115 | 21.5111 | 21.9594 | 38.8267 | 87.5495 | 93.7984 | 23.8111 | 50.1034 | 93.1957 | 727.696 | 639.6368 | 715.8719 | 731.3298 | 719.7337 |  | 726.637 | 701.8292 | 812.2945 | 597.7923 | 604.5413 | 702.9254 |  | 532.1444 |  |  | 470.0855 | 620.5759 | 691.8548 | [5 empty] | 21.839 | 573.8581 | 21.8582 | 22.0446 | 425.5864 | 21.3562 | 21.8422 | 487.2795 | 605.338 | 626.8868 |  | 922.4484 | 895.4945 | 533.2029 | 668.3396 | 780.0264 | 576.768 | 634.299 | 889.9377 | 922.8313 | 612.3559 | 742.8375 | 781.0635 | 982.0906 | 983.1438 | 501.8129 | 598.8554 | 644.4541 | 556.7589 | 678.3782 | 804.4763 | 884.5353 | 1014.4255 | 565.2008 | 632.6732 | 619.8615 | 737.0547 | 55.2455 | 0.00025766 | 19.5698 | 3.8767 | -28.4299 | 3.0963 | 8448.39 | -0.09 | 1.3388 | 0.32983 | -13.7327 | -1.4054 | 6.6304 | 13.9312 | -34.2346 | 56.8435 | 81.7755 | 33.8348 | 44.6929 | 1.0999 | 60.7669 | 31.5514
42838.4314 | 960 | 22.7862 | 22.7857 | 22.7881 | 22.6964 | 22.3098 | 21.6361 | 22.6483 | 21.6819 | 22.3044 | 22.3071 | 22.2666 | 21.9149 | 21.1318 | 22.1039 | 21.4955 | 21.9747 | 22.7001 | 21.8602 | 35.2488 | 42.8233 | 80.4469 | 88.7384 | 89.2783 | 24.2577 | 46.2108 | 89.2785 | 639.5545 | 666.4105 | 639.1253 | 23.2554 | 50.2135 | 93.8041 | 24.1165 | 48.9833 | 91.5494 | 736.5224 | 768.3014 |  | 381.6653 | 777.7589 | 775.4398 | 674.1636 |  | 385.5505 | 627.4015 | 587.4822 | 856.0214 | 914.1297 | 914.3334 | 909.3562 | 43.8065 | 249.584 | 59.7501 | 471.8079 | 71.1185 | 50.5856 | 49.6362 | 53.3994 | 39.5392 |  |  | 0.50489 | 0.14975 | -42.1055 | -0.29377 | 6.4596 | -6.7002 | -203.4566 | -1.8856 | 12.4113 | 35.5816 | 18.5625 | 9.364e-05 | 0.00013142 | 0.00033349 | 26.7169 | 22.091 | 22.1022 | 22.1503 | 21.9499 | 21.2206 | 20.059 | 22.1376 | 22.2967 | 22.3456 | 22.2824 | 21.8844 | 21.1197 | 22.2015 | 702.0689 | 579.6512 | 537.899 | 356.2114 | 285.5109 | 687.8728 | 437.0803 | 22.2511 | 22.1149 | 22.5664 | 22.1705 | 30.4501 | 39.5891 | 25.9617 | 79.611 | 86.2169 | 587.2781 | 566.9297 | 569.4436 | 569.7573 | 81.8053 | 64.9788 | 749.6259 | 21.9969 | 22.1494 | 349.8641 | 21.5059 | 21.959 | 38.9861 | 87.5824 | 93.87 | 23.8257 | 50.2315 | 93.2438 | 729.9166 | 640.2519 | 714.9892 | 730.724 | 722.2925 |  | 727.0103 | 702.8736 | 812.404 | 595.7662 | 604.4465 | 703.2596 |  | 533.0311 |  |  | 470.3384 | 619.953 | 693.6403 | [5 empty] | 21.8418 | 573.0737 | 21.8621 | 22.0445 | 424.4293 | 21.359 | 21.8444 | 487.0611 | 605.4362 | 626.0298 |  | 932.2284 | 895.5012 | 533.1785 | 667.9608 | 782.3 | 576.7619 | 633.5416 | 892.4593 | 927.1643 | 612.0969 | 743.314 | 787.4684 | 983.2721 | 982.3006 | 502.1658 | 598.9497 | 644.4158 | 556.8268 | 677.4772 | 806.55 | 886.8761 | 1017.269 | 565.391 | 632.7572 | 619.0569 | 736.6685 | 57.6954 | 0.00090366 | 19.5698 | 3.861 | -28.4042 | 3.0963 | 8521.08 | -0.02 | 1.4957 | 0.8093 | -13.5703 | -1.1335 | 6.1036 | -6.2162 | -34.2544 | 56.8674 | 81.7813 | 33.8739 | 46.7862 | 3.225 | 60.6579 | 31.5639
42838.4314 | 961 | 22.7836 | 22.7814 | 22.7872 | 22.6932 | 22.3086 | 21.6323 | 22.6536 | 21.6827 | 22.2959 | 22.2966 | 22.2645 | 21.9104 | 21.1322 | 22.0992 | 21.4855 | 21.9746 | 22.708 | 21.8825 | 35.3683 | 42.9477 | 80.5965 | 88.7376 | 89.3328 | 24.2727 | 46.3226 | 89.294 | 639.8875 | 666.0147 | 639.7013 | 23.2785 | 50.3419 | 93.8324 | 24.1428 | 49.0913 | 91.6189 | 736.0071 | 776.5492 |  | 383.1836 | 769.2079 | 768.1256 | 676.8879 |  | 386.6803 | 629.0839 | 585.9869 | 858.2457 | 914.5261 | 915.6095 | 909.6629 | 44.8015 | 250.4497 | 61.1199 | 473.0457 | 71.0995 | 50.614 | 49.6479 | 53.4236 | 39.4475 |  |  | 0.59229 | 0.46977 | -41.7513 | -0.34437 | 6.4031 | -28.9423 | -203.4874 | -2.0972 | 12.6312 | 36.1323 | 18.6413 | 0.00027763 | 0.00013307 | 0.0003877 | 26.7523 | 22.0897 | 22.1028 | 22.1453 | 21.9396 | 21.2112 | 20.0574 | 22.1335 | 22.2997 | 22.343 | 22.2724 | 21.8783 | 21.1211 | 22.1995 | 696.0499 | 602.9169 | 573.6964 | 366.3574 | 280.2298 | 690.2474 | 439.5195 | 22.2458 | 22.1108 | 22.5736 | 22.1669 | 30.5446 | 39.6932 | 25.996 | 79.6576 | 86.2319 | 587.3564 | 565.4588 | 569.0379 | 567.284 | 113.125 | 55.4911 | 751.8193 | 22.017 | 22.1533 | 350.1696 | 21.5111 | 21.9623 | 39.1592 | 87.6356 | 93.9358 | 23.8576 | 50.3582 | 93.2988 | 731.8533 | 641.905 | 714.1859 | 730.0728 | 725.7808 |  | 727.5396 | 704.4103 | 812.8192 | 593.0842 | 604.356 | 703.9534 |  | 533.9047 |  |  | 470.2795 | 618.654 | 695.2145 | [5 empty] | 21.8409 | 572.2235 | 21.8531 | 22.0407 | 423.2801 | 21.3654 | 21.843 | 486.8954 | 605.4042 | 625.8603 |  | 934.7986 | 897.1357 | 533.3365 | 667.2517 | 783.5463 | 576.6563 | 634.4041 | 897.722 | 932.214 | 611.6741 | 743.1923 | 795.2355 | 987.0547 | 983.4752 | 502.7145 | 598.872 | 644.0952 | 556.7873 | 676.33 | 808.8161 | 889.4217 | 1022.7098 | 565.4332 | 632.8819 | 618.1112 | 735.9365 | 58.5598 | -0.0014486 | 19.5696 | 3.8479 | -28.3144 | 3.0963 | 8644 | -0.07 | 1.6204 | 1.4347 | -13.5258 | -1.2284 | 6.0801 | -12.9265 | -34.2754 | 56.9054 | 81.8707 | 33.932 | 48.1986 | -0.2822 | 60.4477 | 31.646
42838.4314 | 962 | 22.7831 | 22.7825 | 22.7743 | 22.698 | 22.3023 | 21.6253 | 22.6463 | 21.6781 | 22.2933 | 22.2864 | 22.2626 | 21.896 | 21.1207 | 22.0965 | 21.4982 | 21.9862 | 22.729 | 21.9251 | 35.4921 | 43.0762 | 80.7236 | 88.7473 | 89.4007 | 24.3047 | 46.4434 | 89.3167 | 640.0859 | 665.4125 | 640.2103 | 23.2959 | 50.4763 | 93.8373 | 24.1646 | 49.1992 | 91.6741 | 735.8744 | 778.0009 |  | 383.9459 | 762.0903 | 762.1624 | 681.6615 |  | 387.6189 | 630.486 | 584.5773 | 858.7033 | 917.7751 | 919.4859 | 910.6153 | 45.5343 | 251.2218 | 63.1179 | 474.2234 | 71.1002 | 50.658 | 49.6638 | 53.463 | 39.6045 |  |  | 0.80585 | -0.19917 | -40.4305 | 0.044638 | 7.7186 | -41.6969 | -203.496 | -1.542 | 12.3517 | 35.7937 | 17.9271 | 3.779e-05 | 9.035e-05 | 0.00034663 | 26.7983 | 22.0956 | 22.1014 | 22.1483 | 21.9407 | 21.22 | 20.0568 | 22.1347 | 22.3022 | 22.3381 | 22.2797 | 21.883 | 21.1217 | 22.2031 | 743.8213 | 645.6521 | 604.9515 | 363.2146 | 261.036 | 694.3901 | 442.0972 | 22.2425 | 22.1209 | 22.5885 | 22.1725 | 30.6397 | 39.7996 | 26.0318 | 79.6864 | 86.2413 | 587.439 | 565.2631 | 568.4358 | 566.9944 | 93.4304 | 50.2022 | 754.0027 | 22.0105 | 22.1393 | 350.3271 | 21.5106 | 21.9472 | 39.3075 | 87.6664 | 93.9808 | 23.8723 | 50.4672 | 93.3296 | 733.8033 | 642.2328 | 714.2966 | 730.2938 | 729.5023 |  | 728.1055 | 704.8676 | 813.3342 | 591.3237 | 604.163 | 704.3782 |  | 535.0102 |  |  | 470.4328 | 618.4839 | 696.4875 | [5 empty] | 21.8366 | 571.7947 | 21.8571 | 22.0421 | 423.2652 | 21.3608 | 21.8376 | 487.2307 | 605.4832 | 627.2177 |  | 942.0479 | 902.3497 | 533.2685 | 666.9527 | 786.4849 | 576.5743 | 634.3353 | 907.2804 | 935.7587 | 611.5181 | 744.6635 | 810.8947 | 993.8324 | 986.1735 | 502.4337 | 598.6342 | 644.5641 | 556.5057 | 675.6227 | 810.1273 | 893.8923 | 1028.1876 | 565.4338 | 632.7991 | 617.4316 | 735.7979 | 58.2882 | -0.00050771 | 19.5701 | 3.8415 | -28.3761 | 3.0962 | 8748.57 | -0.07 | 1.8907 | -0.93493 | -13.3204 | 0.4426 | 6.6864 | -15.5408 | -34.332 | 56.9465 | 82.022 | 33.946 | 44.1965 | -3.2558 | 60.2805 | 31.6683
42838.4314 | 963 | 22.7923 | 22.7904 | 22.7926 | 22.7092 | 22.3135 | 21.6319 | 22.6488 | 21.6913 | 22.3009 | 22.3122 | 22.2762 | 21.9135 | 21.1321 | 22.1084 | 21.4841 | 21.9758 | 22.7328 | 21.9285 | 35.6092 | 43.1878 | 80.8366 | 88.7366 | 89.4483 | 24.3154 | 46.553 | 89.346 | 641.048 | 665.8333 | 642.3291 | 23.3004 | 50.6357 | 93.8486 | 24.189 | 49.3064 | 91.7328 | 736.1483 | 770.7661 |  | 384.8564 | 754.493 | 756.0705 | 682.9113 |  | 388.5654 | 630.331 | 582.6751 | 845.8042 | 920.3818 | 927.1072 | 913.3372 | 46.93 | 252.1035 | 65.1801 | 475.5703 | 71.1309 | 50.7094 | 49.6693 | 53.503 | 39.8133 |  |  | 0.79731 | -0.005981 | -39.7156 | -0.35423 | 7.1167 | -76.3394 | -203.5012 | -1.9428 | 12.7145 | 36.7757 | 18.0774 | 8.214e-05 | 0.00012485 | 0.00036799 | 26.8489 | 22.1024 | 22.1058 | 22.1521 | 21.945 | 21.2201 | 20.065 | 22.1361 | 22.3035 | 22.3435 | 22.2813 | 21.8911 | 21.126 | 22.2089 | 735.9812 | 633.7025 | 612.1079 | 371.0581 | 257.1192 | 697.6066 | 444.048 | 22.2501 | 22.1147 | 22.5957 | 22.1707 | 30.7293 | 39.8986 | 26.0615 | 79.7017 | 86.2586 | 587.5449 | 565.7785 | 568.3042 | 567.6385 | 98.267 | 62.3894 | 755.9923 | 22.0244 | 22.1475 | 350.7139 | 21.517 | 21.9644 | 39.481 | 87.714 | 94.0493 | 23.9058 | 50.605 | 93.3892 | 735.7278 | 642.6801 | 714.6106 | 730.6052 | 729.2827 |  | 728.5119 | 706.6871 | 814.3277 | 591.4009 | 604.027 | 705.8156 |  | 536.6176 |  |  | 470.4495 | 618.4715 | 696.8566 | [5 empty] | 21.8312 | 572.0717 | 21.8526 | 22.0405 | 423.2754 | 21.3693 | 21.8316 | 486.869 | 605.1239 | 627.2629 |  | 948.7366 | 907.4115 | 532.6651 | 667.181 | 788.9672 | 576.3747 | 633.1077 | 914.2912 | 937.5515 | 611.1122 | 744.5068 | 830.4114 | 1001.4531 | 983.854 | 502.2739 | 598.5073 | 644.9685 | 556.5159 | 675.2516 | 811.6695 | 894.2093 | 1031.2117 | 565.4755 | 632.5982 | 616.9786 | 735.5167 | 57.5548 | -0.00049368 | 19.5693 | 3.8389 | -28.4463 | 3.0963 | 8794.43 | -0.1 | 1.8828 | -0.162 | -13.201 | -1.2467 | 6.4409 | -21.0949 | -34.4419 | 57.0564 | 82.2884 | 33.9192 | 46.089 | -3.6717 | 60.3173 | 31.6687
42838.4314 | 964 | 22.7808 | 22.7744 | 22.7789 | 22.6946 | 22.3009 | 21.6274 | 22.6434 | 21.6795 | 22.2948 | 22.3001 | 22.2606 | 21.9115 | 21.1269 | 22.0966 | 21.4839 | 21.9896 | 22.7529 | 21.9563 | 35.7378 | 43.3042 | 80.9432 | 88.7517 | 89.5151 | 24.3451 | 46.6744 | 89.3856 | 640.7475 | 665.398 | 641.2021 | 23.3311 | 50.7818 | 93.8911 | 24.2221 | 49.4243 | 91.7953 | 736.0666 | 758.056 |  | 384.9816 | 749.37 | 751.5787 | 680.1623 |  | 389.8048 | 630.6003 | 582.5394 | 841.848 | 926.3995 | 929.4695 | 916.4041 | 47.3284 | 252.9317 | 65.8126 | 476.8847 | 71.1266 | 50.7439 | 49.6774 | 53.5345 | 40.2718 |  |  | 0.88931 | 0.28512 | -39.4389 | -0.41665 | 6.181 | -57.5715 | -203.5104 | -2.1662 | 12.9902 | 37.7087 | 18.5498 | 0.00010185 | 0.00010021 | 0.00038606 | 26.888 | 22.1057 | 22.1037 | 22.1516 | 21.9465 | 21.2153 | 20.0648 | 22.1317 | 22.2972 | 22.3454 | 22.2872 | 21.8883 | 21.1224 | 22.202 | 729.0903 | 633.7241 | 642.1302 | 384.6686 | 262.6851 | 701.0767 | 447.3198 | 22.2485 | 22.1269 | 22.6157 | 22.1821 | 30.8304 | 40.0042 | 26.1111 | 79.7205 | 86.2799 | 587.637 | 564.6882 | 568.1857 | 567.236 | 89.1202 | 46.2222 | 759.077 | 22.0238 | 22.1468 | 350.6735 | 21.5207 | 21.9598 | 39.6468 | 87.7493 | 94.1107 | 23.9332 | 50.7282 | 93.4356 | 736.22 | 643.2106 | 715.1492 | 731.0579 | 733.3863 |  | 729.1047 | 705.8606 | 815.0028 | 591.0338 | 603.8675 | 705.6837 |  | 537.6377 |  |  | 470.3862 | 619.0591 | 699.6447 | [5 empty] | 21.8351 | 572.056 | 21.8621 | 22.0418 | 422.2576 | 21.3719 | 21.8397 | 486.4215 | 604.6132 | 628.5203 |  | 947.2061 | 907.7669 | 531.846 | 667.0076 | 788.8945 | 575.8449 | 631.6146 | 920.3229 | 937.2727 | 610.2613 | 745.1146 | 832.5861 | 1007.058 | 985.3984 | 502.6028 | 598.3034 | 645.7148 | 556.3273 | 674.4751 | 808.4533 | 892.3504 | 1033.4991 | 565.3984 | 632.0307 | 616.343 | 734.1072 | 56.5349 | 0.00016636 | 19.5696 | 3.849 | -28.4739 | 3.0962 | 8834.04 | -0.08 | 1.9872 | 1.1187 | -13.1569 | -1.3523 | 6.0084 | -18.3373 | -34.4766 | 57.0942 | 82.5272 | 33.9006 | 47.9641 | -6.3683 | 60.3723 | 31.6957
42838.4314 | 965 | 22.7838 | 22.7721 | 22.7763 | 22.6925 | 22.2993 | 21.6249 | 22.6438 | 21.6816 | 22.285 | 22.2936 | 22.2596 | 21.9042 | 21.124 | 22.0995 | 21.4879 | 21.9945 | 22.7492 | 21.9774 | 35.8488 | 43.4239 | 81.0518 | 88.7504 | 89.5454 | 24.3555 | 46.7835 | 89.4339 | 638.5637 | 664.3863 | 638.9123 | 23.3466 | 50.9108 | 93.9219 | 24.2474 | 49.5209 | 91.8841 | 736.0461 | 756.6462 |  | 385.3164 | 746.6137 | 749.1429 | 679.6278 |  | 390.8471 | 630.5847 | 585.9287 | 836.9094 | 930.1639 | 931.4169 | 916.9475 | 48.5627 | 253.9016 | 66.6017 | 478.1328 | 71.1721 | 50.7756 | 49.6942 | 53.5761 | 40.4603 |  |  | 0.72634 | 0.22467 | -37.8356 | -0.66505 | 6.9478 | -24.2906 | -203.473 | -2.067 | 12.8151 | 37.2499 | 18.5326 | 0 | 8.871e-05 | 0.00040084 | 26.9257 | 22.1062 | 22.102 | 22.1556 | 21.9398 | 21.2142 | 20.0643 | 22.1321 | 22.3022 | 22.3406 | 22.2855 | 21.8864 | 21.1165 | 22.2025 | 700.6927 | 604.6301 | 601.3769 | 382.8648 | 281.7607 | 703.5776 | 449.7912 | 22.2532 | 22.1262 | 22.6189 | 22.1781 | 30.9362 | 40.1125 | 26.1345 | 79.7335 | 86.2906 | 587.6456 | 563.0497 | 567.7804 | 565.1249 | 91.6937 | 55.0863 | 759.3543 | 22.0155 | 22.1424 | 351.3956 | 21.5127 | 21.9522 | 39.8009 | 87.7644 | 94.1638 | 23.9554 | 50.848 | 93.4803 | 733.3534 | 642.8037 | 715.2895 | 730.982 | 726.1325 |  | 729.1925 | 704.2364 | 815.4729 | 590.3114 | 603.5755 | 704.8008 |  | 538.1852 |  |  | 469.1093 | 619.7128 | 696.4604 | [5 empty] | 21.8294 | 571.7558 | 21.8621 | 22.0374 | 420.4926 | 21.3628 | 21.8422 | 485.8114 | 604.0758 | 628.4641 |  | 950.065 | 905.0263 | 530.9462 | 667.1018 | 785.9179 | 575.2801 | 630.9877 | 927.4414 | 940.3062 | 609.8885 | 744.6835 | 840.3542 | 1008.5395 | 984.1309 | 502.8313 | 597.7105 | 644.5522 | 555.8856 | 673.9621 | 806.9557 | 888.6503 | 1035.2257 | 565.2702 | 630.6878 | 616.1999 | 733.4878 | 58.0252 | -0.0010273 | 19.5694 | 3.872 | -28.4217 | 3.0963 | 8817.39 | -0.06 | 1.7937 | 0.99302 | -12.8866 | -1.7085 | 6.3754 | -11.9207 | -34.5013 | 57.3181 | 82.7229 | 33.8679 | 51.9238 | -1.3549 | 60.3818 | 31.7559
42838.4315 | 966 | 22.7782 | 22.778 | 22.7774 | 22.6932 | 22.3038 | 21.6255 | 22.6408 | 21.6764 | 22.2856 | 22.2963 | 22.2545 | 21.9101 | 21.1183 | 22.1043 | 21.4819 | 21.9985 | 22.7635 | 21.9964 | 35.9753 | 43.5399 | 81.1774 | 88.7561 | 89.5778 | 24.3823 | 46.9021 | 89.4739 | 637.2125 | 663.3961 | 638.5019 | 23.3584 | 51.0334 | 93.9529 | 24.2656 | 49.6193 | 91.9432 | 736.137 | 765.0494 |  | 385.6653 | 745.5567 | 749.062 | 679.0205 |  | 391.9567 | 631.307 | 586.6898 | 833.8973 | 930.3636 | 936.0682 | 919.8383 | 49.1613 | 254.8298 | 67.0155 | 479.4684 | 71.212 | 50.7972 | 49.6972 | 53.623 | 40.5746 |  |  | 0.64026 | 2.0745 | -36.7447 | -0.39563 | 7.2087 | -71.4222 | -203.4434 | -2.2917 | 13.2638 | 38.9942 | 18.2342 | 1.64e-06 | 9.035e-05 | 0.00039098 | 26.9679 | 22.1041 | 22.1004 | 22.1421 | 21.9373 | 21.2103 | 20.0598 | 22.1274 | 22.3017 | 22.3401 | 22.279 | 21.8895 | 21.1142 | 22.2024 | 695.4284 | 578.4438 | 602.9727 | 381.0274 | 283.444 | 706.4704 | 452.5888 | 22.2438 | 22.1316 | 22.6273 | 22.1798 | 31.0251 | 40.2079 | 26.1697 | 79.7496 | 86.3045 | 587.5002 | 561.3301 | 566.4601 | 561.8761 | 99.6953 | 69.7471 | 759.4718 | 22.0134 | 22.1369 | 352.3964 | 21.508 | 21.952 | 39.9649 | 87.7814 | 94.2338 | 23.9775 | 50.9786 | 93.5355 | 733.729 | 641.7047 | 714.7492 | 730.4259 | 722.9526 |  | 729.2646 | 704.8102 | 816.3326 | 588.9933 | 603.3371 | 705.0289 |  | 538.7084 |  |  | 468.2017 | 618.4316 | 694.1199 | [5 empty] | 21.8334 | 569.7872 | 21.8641 | 22.0321 | 419.4767 | 21.3647 | 21.8433 | 485.2197 | 603.4369 | 627.4374 |  | 951.3798 | 904.1863 | 530.4828 | 667.9516 | 786.9853 | 574.8463 | 630.3705 | 927.7182 | 943.3532 | 610.2587 | 746.3099 | 851.427 | 1012.2258 | 985.1292 | 503.4434 | 597.3395 | 642.798 | 555.6745 | 674.6834 | 809.5875 | 890.1995 | 1038.9775 | 565.211 | 629.4075 | 616.6756 | 733.3116 | 59.9908 | 0.00011019 | 19.5698 | 3.8926 | -28.4537 | 3.0963 | 8787.15 | -0.01 | 1.6837 | 3.0186 | -12.7045 | -1.3183 | 6.5065 | -20.4803 | -34.5654 | 57.4249 | 82.9827 | 33.8615 | 53.4442 | -0.9802 | 60.4224 | 31.821
42838.4315 | 967 | 22.7823 | 22.7777 | 22.7822 | 22.7007 | 22.3027 | 21.6306 | 22.6469 | 21.6786 | 22.297 | 22.3048 | 22.2613 | 21.9128 | 21.1246 | 22.1055 | 21.4856 | 22.0083 | 22.7755 | 22.0236 | 36.1026 | 43.6501 | 81.3409 | 88.7655 | 89.6018 | 24.4081 | 47.0124 | 89.5049 | 636.3239 | 662.4208 | 637.7342 | 23.3622 | 51.1425 | 93.9938 | 24.2742 | 49.7157 | 92.0008 | 736.0762 | 763.1273 |  | 386.9584 | 747.4261 | 752 | 681.5805 |  | 393.295 | 632.7966 | 585.9692 | 834.1251 | 931.4555 | 939.9197 | 922.8976 | 49.1986 | 255.7195 | 68.195 | 480.8893 | 71.1871 | 50.8353 | 49.7113 | 53.6705 | 40.6589 |  |  | 0.74934 | 1.232 | -36.9346 | -0.44097 | 7.6233 | -159.6419 | -203.3291 | -2.4067 | 13.0042 | 37.6762 | 18.0295 | 1.314e-05 | 0.000115 | 0.00037291 | 27.0311 | 22.109 | 22.1062 | 22.1457 | 21.9517 | 21.22 | 20.0616 | 22.1333 | 22.3075 | 22.3444 | 22.2911 | 21.8849 | 21.124 | 22.2039 | 719.5992 | 597.2732 | 613.981 | 400.4588 | 301.1456 | 709.9274 | 455.4803 | 22.2473 | 22.1288 | 22.6448 | 22.1868 | 31.1199 | 40.3134 | 26.2042 | 79.7738 | 86.3211 | 587.1687 | 557.8049 | 564.6097 | 558.2894 | 96.0427 | 47.5186 | 761.1779 | 22.0234 | 22.1434 | 353.0507 | 21.5108 | 21.9598 | 40.1351 | 87.7746 | 94.2968 | 24.0131 | 51.097 | 93.587 | 736.6869 | 642.1008 | 714.6623 | 729.9629 | 728.2334 |  | 729.6981 | 703.8782 | 816.7861 | 587.7771 | 603.1705 | 704.6158 |  | 539.3098 |  |  | 469.7757 | 618.6881 | 697.1522 | [5 empty] | 21.8307 | 569.192 | 21.864 | 22.0439 | 418.3934 | 21.3633 | 21.8387 | 484.9355 | 603.1043 | 626.5679 |  | 946.6204 | 905.1561 | 529.9486 | 668.9684 | 786.0637 | 574.237 | 630.9089 | 925.9631 | 939.9574 | 610.7525 | 746.8036 | 851.3729 | 1014.4168 | 987.0882 | 503.5783 | 597.1845 | 641.7764 | 555.2192 | 675.3323 | 808.6056 | 888.4622 | 1044.7021 | 564.9321 | 628.1584 | 617.0796 | 732.7905 | 59.1721 | -0.0012731 | 19.5702 | 3.9146 | -28.4136 | 3.0963 | 8773.7 | 0 | 1.8207 | 2.3282 | -12.7478 | -1.3929 | 6.7017 | -30.6679 | -34.6106 | 57.3894 | 83.1542 | 33.8652 | 51.8837 | -1.6299 | 60.3354 | 31.8636
42838.4315 | 968 | 22.7864 | 22.7757 | 22.7836 | 22.6998 | 22.3005 | 21.6319 | 22.6515 | 21.6848 | 22.3093 | 22.3027 | 22.2677 | 21.9142 | 21.1276 | 22.1041 | 21.4833 | 22.0092 | 22.7859 | 22.0534 | 36.2231 | 43.7764 | 81.4765 | 88.7886 | 89.6244 | 24.4316 | 47.1254 | 89.5375 | 634.8853 | 661.5216 | 636.5837 | 23.3843 | 51.2659 | 94.0318 | 24.3025 | 49.8314 | 92.0541 | 736.2761 | 757.3851 |  | 388.5824 | 750.8118 | 756.2424 | 685.6734 |  | 394.0624 | 635.2633 | 586.1656 | 835.9229 | 934.1545 | 940.5939 | 923.0647 | 48.7243 | 256.8608 | 69.8666 | 482.653 | 71.1169 | 50.8886 | 49.721 | 53.7316 | 40.7228 |  |  | 0.50029 | -0.13346 | -38.6221 | 0.12152 | 9.3101 | -197.4898 | -203.1595 | -3.1972 | 12.8986 | 37.5753 | 17.6933 | -1.971e-05 | 1.643e-05 | 0.00037949 | 27.0678 | 22.1087 | 22.0971 | 22.1427 | 21.948 | 21.216 | 20.0577 | 22.1353 | 22.3017 | 22.3459 | 22.2788 | 21.884 | 21.1208 | 22.2 | 745.3249 | 621.8305 | 584.5301 | 395.5876 | 305.0802 | 713.981 | 457.228 | 22.2387 | 22.128 | 22.6534 | 22.1856 | 31.2118 | 40.4092 | 26.2313 | 79.7947 | 86.3315 | 586.7648 | 555.2596 | 562.9603 | 556.1817 | 109.3132 | 62.9722 | 760.9717 | 22.026 | 22.1479 | 353.6728 | 21.5168 | 21.9567 | 40.3014 | 87.7792 | 94.3597 | 24.0362 | 51.2261 | 93.6582 | 733.7755 | 642.0047 | 715.0702 | 730.1206 | 727.0322 |  | 730.0829 | 701.7953 | 816.9053 | 586.3149 | 602.9509 | 703.3084 |  | 539.6769 |  |  | 469.2311 | 619.7409 | 696.9157 | [5 empty] | 21.8394 | 568.6434 | 21.8686 | 22.0419 | 417.8874 | 21.3727 | 21.8464 | 484.8405 | 603.1072 | 626.7696 |  | 938.5508 | 905.5082 | 529.0243 | 669.385 | 783.7915 | 573.6839 | 630.2512 | 923.1244 | 933.6996 | 610.7807 | 746.0351 | 851.1866 | 1012.1232 | 993.672 | 503.5832 | 596.6153 | 640.4437 | 554.4409 | 676.0087 | 804.4521 | 887.1733 | 1047.2799 | 564.29 | 626.9066 | 617.1719 | 732.4748 | 58.2957 | 0.00035597 | 19.5699 | 3.9295 | -28.3953 | 3.0962 | 8720.24 | -0.05 | 1.4867 | -0.76734 | -13.0535 | 0.73221 | 7.4081 | -34.1195 | -34.6058 | 57.5215 | 83.2504 | 33.8662 | 50.3545 | 1.9905 | 60.2739 | 31.8526
42838.4315 | 969 | 22.78 | 22.771 | 22.7747 | 22.6876 | 22.3029 | 21.6238 | 22.6486 | 21.6804 | 22.2921 | 22.2948 | 22.2611 | 21.8968 | 21.1176 | 22.0937 | 21.4829 | 22.0167 | 22.8005 | 22.0784 | 36.3467 | 43.8968 | 81.5805 | 88.8027 | 89.6434 | 24.4553 | 47.2402 | 89.5695 | 633.6171 | 661.1064 | 635.6386 | 23.407 | 51.3866 | 94.0639 | 24.3356 | 49.942 | 92.1038 | 736.6741 | 752.4625 |  | 389.6017 | 755.5205 | 761.6287 | 686.508 |  | 394.6043 | 636.673 | 584.4452 | 835.3367 | 939.0385 | 942.1843 | 926.9077 | 47.9022 | 257.8493 | 71.4224 | 484.2928 | 71.0636 | 50.9613 | 49.7255 | 53.7796 | 40.8932 |  |  | 0.82951 | -0.8254 | -39.6637 | -0.69659 | 8.6819 | -197.8782 | -203.13 | -1.8653 | 13.0472 | 37.0143 | 17.8019 | 0.00010678 | 0.000138 | 0.00036141 | 27.1101 | 22.1016 | 22.0975 | 22.1425 | 21.9367 | 21.2138 | 20.0555 | 22.1296 | 22.2995 | 22.3469 | 22.2775 | 21.8807 | 21.1204 | 22.1976 | 787.1884 | 658.2133 | 597.4397 | 402.1447 | 305.5823 | 719.0311 | 459.6948 | 22.2504 | 22.1345 | 22.662 | 22.1895 | 31.3224 | 40.5182 | 26.2757 | 79.8301 | 86.36 | 586.3924 | 552.9727 | 561.3649 | 555.3083 | 123.0565 | 61.2482 | 759.5196 | 22.0268 | 22.1498 | 354.1487 | 21.5188 | 21.9456 | 40.467 | 87.7977 | 94.4229 | 24.06 | 51.3426 | 93.718 | 731.4656 | 640.5302 | 715.4738 | 730.8827 | 723.2505 |  | 730.1366 | 701.2311 | 817.1126 | 583.9412 | 602.62 | 702.5836 |  | 540.2399 |  |  | 468.8434 | 619.8841 | 694.9987 | [5 empty] | 21.8331 | 567.2259 | 21.8655 | 22.031 | 416.648 | 21.37 | 21.8433 | 484.682 | 602.6686 | 626.7536 |  | 936.2439 | 903.1759 | 528.6271 | 669.4973 | 781.6481 | 573.0142 | 629.7869 | 923.8586 | 932.5571 | 610.7422 | 745.9607 | 853.6683 | 1012.5108 | 998.0816 | 503.6135 | 595.7574 | 638.6563 | 554.0062 | 676.5353 | 801.3796 | 885.7667 | 1049.1984 | 563.6379 | 626.5892 | 617.1846 | 731.8736 | 57.0843 | 0.002315 | 19.5698 | 3.9471 | -28.4427 | 3.0963 | 8695.72 | -0.08 | 1.9134 | -1.9098 | -13.2386 | -1.7544 | 7.1585 | -34.1754 | -34.626 | 57.6404 | 83.3328 | 33.8725 | 47.3743 | 1.0493 | 60.3547 | 31.8128
42838.4315 | 970 | 22.783 | 22.7823 | 22.7904 | 22.6895 | 22.2976 | 21.6279 | 22.6486 | 21.6898 | 22.2992 | 22.2986 | 22.2648 | 21.9078 | 21.1192 | 22.105 | 21.4843 | 22.0203 | 22.8077 | 22.1116 | 36.4714 | 44.0111 | 81.6677 | 88.81 | 89.6607 | 24.477 | 47.348 | 89.6058 | 632.4968 | 660.7435 | 634.3644 | 23.4312 | 51.5238 | 94.0997 | 24.3689 | 50.0434 | 92.1691 | 737.0017 | 746.64 |  | 390.9911 | 759.1853 | 765.555 | 687.177 |  | 395.0316 | 638.6149 | 583.2805 | 837.8443 | 941.584 | 942.3332 | 929.2742 | 47.4912 | 258.9123 | 72.2994 | 486.015 | 71.1169 | 51.053 | 49.7343 | 53.8236 | 41.0309 |  |  | 0.65012 | -0.23269 | -40.7256 | 0.034782 | 6.4366 | -192.1455 | -203.2437 | -2.4534 | 13.6447 | 38.3597 | 18.0004 | 1.643e-05 | 6.407e-05 | 0.00038441 | 27.1546 | 22.1138 | 22.0996 | 22.1451 | 21.945 | 21.2186 | 20.0603 | 22.1375 | 22.3074 | 22.3434 | 22.2834 | 21.8817 | 21.1186 | 22.2056 | 779.3691 | 657.6145 | 583.646 | 402.6961 | 297.3599 | 723.5514 | 462.6097 | 22.2502 | 22.1325 | 22.6756 | 22.1843 | 31.4197 | 40.6255 | 26.3126 | 79.8694 | 86.3888 | 586.068 | 552.5902 | 560.4156 | 556.5337 | 106.6736 | 60.4074 | 758.724 | 22.027 | 22.1522 | 354.6805 | 21.5183 | 21.9566 | 40.6315 | 87.8146 | 94.483 | 24.0928 | 51.4666 | 93.7869 | 728.6843 | 638.8807 | 715.1634 | 730.9902 | 718.8733 |  | 730.0684 | 700.4493 | 817.1221 | 582.4074 | 602.2071 | 701.8098 |  | 540.8735 |  |  | 468.7616 | 618.7872 | 692.8803 | [5 empty] | 21.8311 | 565.6032 | 21.8706 | 22.0387 | 415.3514 | 21.3747 | 21.8435 | 484.312 | 602.3047 | 625.9981 |  | 934.0273 | 899.8486 | 528.5535 | 669.3212 | 780.5353 | 572.2503 | 629.2817 | 922.1742 | 931.486 | 610.717 | 744.6454 | 861.2118 | 1010.896 | 1001.0948 | 503.2 | 595.145 | 637.1393 | 553.6175 | 677.0281 | 799.7457 | 885.66 | 1049.2103 | 562.9724 | 626.1813 | 617.3041 | 731.239 | 56.541 | 0.001339 | 19.5695 | 3.954 | -28.3851 | 3.0963 | 8666.74 | -0.02 | 1.6927 | -1.0151 | -13.4289 | 0.39245 | 6.1641 | -33.6788 | -34.6378 | 57.7444 | 83.3575 | 33.8408 | 49.7536 | 3.1675 | 60.4217 | 31.7231
42838.4315 | 971 | 22.7854 | 22.7816 | 22.7834 | 22.6939 | 22.3121 | 21.6304 | 22.6448 | 21.6907 | 22.3004 | 22.3106 | 22.2683 | 21.9066 | 21.1281 | 22.1019 | 21.4823 | 22.0215 | 22.8177 | 22.1299 | 36.5865 | 44.1264 | 81.7312 | 88.8025 | 89.6689 | 24.4974 | 47.4576 | 89.6414 | 631.3479 | 660.3211 | 632.7706 | 23.442 | 51.6568 | 94.1177 | 24.3828 | 50.1554 | 92.2113 | 737.4845 | 740.7422 |  | 391.9724 | 759.0924 | 765.5471 | 690.7278 |  | 395.7619 | 640.1561 | 583.7866 | 843.8106 | 942.9253 | 944.1389 | 928.3461 | 47.4096 | 259.9296 | 70.8999 | 487.6435 | 71.2134 | 51.1455 | 49.7437 | 53.8743 | 41.1451 |  |  | 0.85448 | -0.25897 | -41.3715 | 0.10838 | 7.2685 | -192.4813 | -203.3028 | -2.3108 | 12.7818 | 37.5138 | 18.4074 | -7.064e-05 | 5.093e-05 | 0.00038113 | 27.1992 | 22.1174 | 22.0966 | 22.1446 | 21.9462 | 21.2164 | 20.0628 | 22.1376 | 22.3052 | 22.34 | 22.2829 | 21.8811 | 21.1185 | 22.2097 | 765.7517 | 630.7333 | 561.8414 | 400.6516 | 302.0185 | 727.7117 | 465.097 | 22.2481 | 22.14 | 22.6876 | 22.1952 | 31.5141 | 40.7273 | 26.3427 | 79.934 | 86.4215 | 585.8372 | 551.855 | 559.7081 | 557.036 | 92.5066 | 53.4394 | 757.0819 | 22.0295 | 22.1462 | 355.4094 | 21.5176 | 21.9579 | 40.7964 | 87.832 | 94.5433 | 24.1189 | 51.5873 | 93.8529 | 724.7593 | 638.0237 | 713.802 | 729.5868 | 712.3963 |  | 729.7952 | 698.6011 | 816.6466 | 582.3122 | 601.8734 | 700.5055 |  | 541.3865 |  |  | 468.37 | 617.1596 | 690.195 | [5 empty] | 21.8339 | 564.9802 | 21.8754 | 22.0429 | 414.4298 | 21.374 | 21.8381 | 483.7706 | 601.9589 | 625.0089 |  | 936.5516 | 898.8128 | 528.5091 | 668.8566 | 779.9897 | 571.67 | 628.7195 | 922.8119 | 933.4476 | 610.4294 | 743.0456 | 864.6952 | 1011.3001 | 1003.2416 | 502.7921 | 594.5792 | 636.0074 | 553.0924 | 678.0917 | 799.3627 | 887.3932 | 1049.1993 | 562.2196 | 625.3028 | 617.7704 | 730.7741 | 56.7588 | -0.00057796 | 19.5695 | 3.9546 | -28.3028 | 3.0963 | 8678.37 | -0.1 | 1.9389 | -1.0718 | -13.5465 | 0.69335 | 6.5552 | -33.7332 | -34.6685 | 57.8542 | 83.256 | 33.7834 | 52.669 | 6.0925 | 60.4494 | 31.6696
42838.4315 | 972 | 22.7769 | 22.772 | 22.7757 | 22.6869 | 22.2958 | 21.6243 | 22.6347 | 21.6811 | 22.2902 | 22.292 | 22.2595 | 21.9026 | 21.1199 | 22.09 | 21.4805 | 22.0288 | 22.8247 | 22.1554 | 36.7084 | 44.2412 | 81.7966 | 88.8028 | 89.678 | 24.5127 | 47.5648 | 89.6676 | 630.374 | 660.5086 | 631.8894 | 23.4597 | 51.7805 | 94.1534 | 24.41 | 50.2591 | 92.2631 | 738.1717 | 749.768 |  | 392.4227 | 757.8784 | 764.3748 | 692.4056 |  | 396.5491 | 641.3852 | 582.83 | 838.2781 | 946.0693 | 944.8848 | 929.1246 | 47.0865 | 260.8094 | 68.7892 | 488.7489 | 71.1347 | 51.2165 | 49.7533 | 53.916 | 41.1347 |  |  | 0.73291 | -0.9174 | -40.8576 | 0.21549 | 7.3 | -197.8867 | -203.1083 | -2.2155 | 13.2677 | 38.545 | 17.882 | -4.6e-05 | 4.436e-05 | 0.00036634 | 27.2365 | 22.1067 | 22.094 | 22.1341 | 21.9404 | 21.2087 | 20.061 | 22.1304 | 22.2985 | 22.3313 | 22.2706 | 21.8789 | 21.1111 | 22.1997 | 768.5465 | 617.3618 | 547.733 | 388.4713 | 294.8558 | 731.1817 | 466.7857 | 22.25 | 22.1503 | 22.7038 | 22.1991 | 31.6189 | 40.8372 | 26.3864 | 79.9999 | 86.4472 | 585.4224 | 550.5732 | 558.3844 | 553.8421 | 110.1979 | 50.4447 | 754.4833 | 22.0322 | 22.1453 | 355.7689 | 21.5119 | 21.9503 | 40.9504 | 87.8397 | 94.6061 | 24.1414 | 51.707 | 93.9219 | 723.0415 | 638.1196 | 712.3631 | 728.2485 | 711.3138 |  | 729.5439 | 697.5877 | 816.2029 | 583.5952 | 601.6876 | 699.6176 |  | 541.8488 |  |  | 468.1267 | 614.4543 | 688.4748 | [5 empty] | 21.8331 | 565.8375 | 21.8717 | 22.0443 | 414.2842 | 21.3711 | 21.8423 | 483.2552 | 601.3949 | 624.1883 |  | 938.038 | 900.9379 | 528.4088 | 668.163 | 780.0216 | 571.0722 | 628.3854 | 922.1233 | 935.8087 | 609.898 | 742.4744 | 867.4294 | 1012.6488 | 1001.3324 | 502.3133 | 594.0813 | 635.0949 | 552.5585 | 679.3067 | 801.0993 | 887.0398 | 1049.0273 | 561.7386 | 624.3451 | 618.3213 | 732.265 | 55.5421 | -0.00032516 | 19.5694 | 3.9549 | -28.3699 | 3.0963 | 8713.28 | -0.11 | 1.7948 | -2.0186 | -13.4711 | 0.97832 | 6.5714 | -34.2141 | -34.6626 | 57.8198 | 83.1417 | 33.7144 | 53.5372 | 8.0023 | 60.583 | 31.6872
42838.4315 | 973 | 22.7789 | 22.7769 | 22.7724 | 22.6887 | 22.2978 | 21.626 | 22.6413 | 21.6795 | 22.2939 | 22.2929 | 22.2652 | 21.9025 | 21.1201 | 22.0959 | 21.4789 | 22.0358 | 22.8321 | 22.188 | 36.8343 | 44.3586 | 81.8815 | 88.7995 | 89.6887 | 24.5386 | 47.6703 | 89.6968 | 630.7535 | 660.8103 | 633.4106 | 23.4747 | 51.902 | 94.1968 | 24.439 | 50.363 | 92.3265 | 738.7333 | 753.2328 |  | 392.6049 | 758.4234 | 765.633 | 692.684 |  | 397.911 | 642.2417 | 582.5075 | 830.6251 | 947.9696 | 943.3767 | 928.2621 | 46.6454 | 261.9295 | 65.5055 | 489.8389 | 71.1512 | 51.284 | 49.7608 | 53.9555 | 41.2296 |  |  | 0.35113 | -0.94106 | -40.4765 | -0.40877 | 7.4768 | -197.8499 | -202.9926 | -2.5756 | 13.2208 | 36.9644 | 17.9745 | -6.735e-05 | -4.93e-06 | 0.00035977 | 27.2977 | 22.1171 | 22.1088 | 22.1525 | 21.9521 | 21.2227 | 20.0692 | 22.1432 | 22.311 | 22.343 | 22.2881 | 21.8908 | 21.124 | 22.2095 | 772.8053 | 606.0324 | 512.2204 | 373.5186 | 285.7055 | 735.02 | 467.9415 | 22.237 | 22.1411 | 22.6999 | 22.1956 | 31.7062 | 40.9273 | 26.4159 | 80.0322 | 86.4582 | 584.8036 | 547.6359 | 556.0949 | 549.7175 | 95.7293 | 51.3614 | 753.1662 | 22.0283 | 22.1504 | 355.8532 | 21.521 | 21.9629 | 41.1239 | 87.8522 | 94.6712 | 24.1723 | 51.834 | 93.9978 | 722.032 | 638.2454 | 711.4764 | 727.5493 | 712.2521 |  | 729.3825 | 697.245 | 815.9818 | 587.1672 | 601.6642 | 699.0186 |  | 542.4428 |  |  | 467.5946 | 612.1682 | 687.929 | [5 empty] | 21.8335 | 567.2962 | 21.8748 | 22.0477 | 414.1974 | 21.3758 | 21.8448 | 483.0635 | 600.8227 | 623.478 |  | 937.322 | 901.5076 | 528.091 | 667.572 | 779.6048 | 570.5133 | 628.4152 | 918.7378 | 937.4417 | 609.2431 | 740.8586 | 871.4898 | 1012.7872 | 1000.6563 | 502.043 | 593.736 | 634.5375 | 551.7459 | 680.2729 | 803.4472 | 889.1358 | 1047.8069 | 561.5659 | 623.58 | 618.3685 | 734.2125 | 53.7876 | -0.0019472 | 19.5691 | 3.9553 | -28.3667 | 3.0963 | 8788.83 | -0.03 | 1.2434 | -2.0454 | -13.4144 | -1.3481 | 6.6464 | -34.1897 | -34.6312 | 57.7524 | 83.0802 | 33.611 | 54.3774 | 12.183 | 60.7227 | 31.6958
42838.4316 | 974 | 22.7869 | 22.776 | 22.7811 | 22.7028 | 22.3022 | 21.6333 | 22.6443 | 21.6756 | 22.2955 | 22.298 | 22.263 | 21.9011 | 21.1184 | 22.0941 | 21.4943 | 22.0528 | 22.8555 | 22.2192 | 36.965 | 44.4821 | 81.974 | 88.8072 | 89.707 | 24.567 | 47.7865 | 89.7401 | 632.2827 | 661.6904 | 635.8154 | 23.4983 | 52.0326 | 94.2549 | 24.472 | 50.4675 | 92.3973 | 739.2609 | 745.1766 |  | 392.6167 | 760.4283 | 768.2359 | 693.5775 |  | 398.3378 | 642.1507 | 583.2466 | 831.8341 | 947.4943 | 941.6168 | 926.4981 | 46.2643 | 262.8482 | 63.2693 | 490.701 | 71.1469 | 51.3424 | 49.761 | 53.9912 | 41.3414 |  |  | 0.3853 | 0.6058 | -39.1728 | -0.083498 | 7.5083 | -197.8276 | -203.2529 | -1.8074 | 12.9819 | 37.0909 | 18.0208 | 1.15e-05 | -1.807e-05 | 0.0003532 | 27.3369 | 22.1144 | 22.1054 | 22.1373 | 21.9424 | 21.2113 | 20.0654 | 22.1301 | 22.3066 | 22.3471 | 22.29 | 21.8881 | 21.1172 | 22.2124 | 731.396 | 608.3717 | 504.1998 | 351.5578 | 279.5447 | 737.5938 | 469.1261 | 22.2437 | 22.1396 | 22.7216 | 22.2001 | 31.8008 | 41.0341 | 26.4493 | 80.0546 | 86.4748 | 584.237 | 542.9826 | 554.8786 | 549.5296 | 103.0422 | 43.4467 | 752.7337 | 22.0257 | 22.1507 | 356.3078 | 21.5174 | 21.9629 | 41.2907 | 87.8626 | 94.7334 | 24.1913 | 51.9493 | 94.0835 | 720.7616 | 638.0125 | 710.9347 | 727.1277 | 711.7684 |  | 729.0725 | 697.0843 | 815.8948 | 586.9347 | 601.4672 | 698.648 |  | 543.1585 |  |  | 467.793 | 611.0286 | 687.1479 | [5 empty] | 21.8294 | 567.62 | 21.8766 | 22.0451 | 414.7504 | 21.3756 | 21.8383 | 483.2817 | 600.5491 | 623.2019 |  | 940.3957 | 900.6196 | 527.5931 | 667.2022 | 776.5389 | 570.2154 | 628.077 | 919.2315 | 938.5969 | 608.8957 | 740.5404 | 874.0077 | 1013.4472 | 998.9526 | 501.7673 | 593.4474 | 634.7722 | 550.6775 | 680.7613 | 805.7249 | 894.0195 | 1049.5127 | 561.1038 | 622.8486 | 617.8364 | 735.2569 | 52.4895 | 0.0014864 | 19.5692 | 3.9544 | -28.4828 | 3.0963 | 8836.69 | -0.04 | 1.3042 | 1.641 | -13.196 | -0.60924 | 6.6556 | -34.1631 | -34.6283 | 57.6864 | 83.0568 | 33.5821 | 59.8649 | 13.3155 | 60.8366 | 31.6042
42838.4316 | 975 | 22.7762 | 22.7664 | 22.7737 | 22.6845 | 22.2957 | 21.6272 | 22.6435 | 21.6823 | 22.2891 | 22.2913 | 22.2648 | 21.8994 | 21.1177 | 22.0908 | 21.4848 | 22.0556 | 22.8676 | 22.2508 | 37.091 | 44.5969 | 82.0545 | 88.8203 | 89.7287 | 24.5846 | 47.8972 | 89.7769 | 633.5017 | 662.3751 | 637.0465 | 23.5086 | 52.1545 | 94.3145 | 24.4879 | 50.5651 | 92.4402 | 739.8353 | 737.7236 |  | 393.5604 | 761.6765 | 769.9638 | 694.0228 |  | 399.2818 | 643.6749 | 584.3718 | 832.7127 | 949.422 | 940.4947 | 926.9777 | 45.9698 | 263.777 | 62.5226 | 491.7664 | 71.1789 | 51.3991 | 49.7666 | 54.0206 | 41.4006 |  |  | 0.57455 | -0.45413 | -38.4447 | -0.51719 | 7.4407 | -191.4076 | -203.3646 | -2.4383 | 13.1979 | 38.3115 | 18.0804 | 7.886e-05 | 0.00013964 | 0.00034827 | 27.3834 | 22.1186 | 22.095 | 22.1396 | 21.9451 | 21.2096 | 20.0643 | 22.1342 | 22.3012 | 22.3411 | 22.2806 | 21.8782 | 21.1176 | 22.207 | 710.5454 | 598.2145 | 508.8134 | 347.2842 | 274.9786 | 739.4343 | 470.1529 | 22.2319 | 22.1374 | 22.7328 | 22.1988 | 31.9061 | 41.1355 | 26.4858 | 80.0849 | 86.4969 | 583.9268 | 545.8183 | 554.0462 | 552.3651 | 108.2366 | 61.9427 | 752.1404 | 22.0305 | 22.1489 | 356.5663 | 21.5205 | 21.9583 | 41.4452 | 87.8859 | 94.8005 | 24.2212 | 52.0718 | 94.1599 | 717.3103 | 636.9569 | 710.7304 | 727.3186 | 708.173 |  | 728.5969 | 696.0779 | 815.6075 | 584.6062 | 601.1585 | 697.8833 |  | 543.8937 |  |  | 469.0022 | 609.6268 | 685.0169 | [5 empty] | 21.8307 | 566.7501 | 21.884 | 22.0486 | 415.0784 | 21.3791 | 21.8344 | 483.5594 | 600.1169 | 623.5285 |  | 941.3568 | 900.8968 | 526.9181 | 667.8273 | 773.523 | 570.0203 | 628.0423 | 920.125 | 936.0766 | 609.0056 | 740.902 | 874.825 | 1016.8798 | 998.4201 | 501.4338 | 592.9671 | 635.1728 | 549.4078 | 680.5277 | 805.3742 | 899.0336 | 1054.6959 | 560.4312 | 622.2663 | 617.4004 | 735.0821 | 51.9304 | 0.0016128 | 19.568 | 3.9548 | -28.4254 | 3.0964 | 8883.05 | -0.07 | 1.5937 | -1.422 | -13.0836 | -1.5175 | 6.6224 | -33.5886 | -34.6219 | 57.6646 | 82.9926 | 33.5913 | 62.8183 | 13.0124 | 60.9755 | 31.4725
42838.4316 | 976 | 22.773 | 22.7675 | 22.7721 | 22.6847 | 22.3046 | 21.6226 | 22.6458 | 21.6796 | 22.2903 | 22.2903 | 22.2547 | 21.9025 | 21.1168 | 22.0999 | 21.493 | 22.0624 | 22.8864 | 22.283 | 37.2084 | 44.7161 | 82.1385 | 88.8275 | 89.7381 | 24.6191 | 48.0008 | 89.806 | 633.0919 | 662.7084 | 636.1738 | 23.5254 | 52.2846 | 94.3668 | 24.5093 | 50.6587 | 92.4758 | 740.3681 | 733.4606 |  | 394.8724 | 762.1226 | 770.881 | 692.3021 |  | 400.1336 | 645.0815 | 584.4734 | 831.3053 | 946.4051 | 940.4496 | 928.4336 | 45.5649 | 264.6903 | 62.4121 | 493.0786 | 71.1516 | 51.4573 | 49.7628 | 54.0512 | 41.4946 |  |  | 0.65472 | 0.3896 | -37.7087 | 0.226 | 8.4349 | -197.8184 | -203.2437 | -2.5408 | 13.8255 | 40.1774 | 18.0632 | 1.314e-05 | 2.3e-05 | 0.00040577 | 27.4369 | 22.1201 | 22.0993 | 22.1422 | 21.9459 | 21.2214 | 20.0599 | 22.1312 | 22.3039 | 22.3424 | 22.2834 | 21.8891 | 21.1288 | 22.2042 | 700.7056 | 600.3187 | 556.4491 | 361.5309 | 291.972 | 741.5744 | 472.9053 | 22.2344 | 22.1403 | 22.7488 | 22.2005 | 32.0079 | 41.2331 | 26.5325 | 80.142 | 86.523 | 583.7169 | 546.6478 | 553.0875 | 554.0692 | 107.6957 | 61.5811 | 751.0754 | 22.0308 | 22.1403 | 356.6878 | 21.5139 | 21.9591 | 41.6079 | 87.9093 | 94.8685 | 24.2492 | 52.1955 | 94.2288 | 714.0817 | 635.7116 | 710.9214 | 727.8145 | 703.6169 |  | 728.133 | 696.1262 | 815.4703 | 584.0008 | 600.9139 | 697.6798 |  | 544.5547 |  |  | 469.5262 | 607.5469 | 682.9771 | [5 empty] | 21.8362 | 566.0629 | 21.8893 | 22.0541 | 414.9916 | 21.3892 | 21.8413 | 483.3643 | 599.6655 | 623.8434 |  | 943.3561 | 900.9577 | 526.1261 | 668.9152 | 771.5059 | 569.6745 | 627.8691 | 917.967 | 934.8112 | 609.1668 | 739.3302 | 873.438 | 1022.9778 | 1001.1806 | 501.3178 | 592.4119 | 634.8726 | 548.4968 | 680.0444 | 805.0117 | 899.6653 | 1058.316 | 559.9316 | 621.1718 | 617.1863 | 734.4481 | 54.0818 | 0.00086854 | 19.5683 | 3.9561 | -28.4654 | 3.0963 | 8872.09 | -0.1 | 1.7004 | 1.3181 | -12.9677 | 1.0039 | 7.0509 | -34.1459 | -34.6109 | 57.6726 | 82.9473 | 33.5643 | 64.655 | 8.2831 | 61.1638 | 31.3894
42838.4316 | 977 | 22.7808 | 22.7743 | 22.7903 | 22.6951 | 22.3119 | 21.6325 | 22.6488 | 21.686 | 22.293 | 22.2989 | 22.2642 | 21.9155 | 21.1232 | 22.1016 | 21.4753 | 22.0595 | 22.8888 | 22.3064 | 37.3266 | 44.8315 | 82.2491 | 88.8408 | 89.7624 | 24.6306 | 48.1025 | 89.8235 | 632.8029 | 662.9097 | 635.1804 | 23.5455 | 52.4093 | 94.4266 | 24.5445 | 50.7719 | 92.5276 | 740.7615 | 735.6216 |  | 395.4015 | 761.2707 | 770.4339 | 693.2199 |  | 400.7999 | 646.5974 | 584.957 | 839.019 | 943.8894 | 944.1295 | 930.8832 | 45.7105 | 265.6065 | 62.6646 | 494.1537 | 71.1418 | 51.5173 | 49.7602 | 54.0922 | 41.5904 |  |  | 0.64289 | 0.63537 | -37.0056 | -0.47448 | 6.7934 | -197.7343 | -203.2772 | -2.019 | 13.2216 | 37.8621 | 18.1644 | -0.00011499 | 5.421e-05 | 0.00037291 | 27.4893 | 22.1268 | 22.106 | 22.1422 | 21.9474 | 21.2226 | 20.0681 | 22.1399 | 22.3104 | 22.3468 | 22.2853 | 21.89 | 21.1289 | 22.2141 | 730.213 | 603.1034 | 586.3205 | 371.7984 | 309.0124 | 744.6586 | 475.5926 | 22.2412 | 22.1428 | 22.7591 | 22.2058 | 32.104 | 41.3438 | 26.567 | 80.18 | 86.5451 | 583.3681 | 545.501 | 550.8558 | 551.841 | 106.965 | 52.0876 | 751.3636 | 22.0362 | 22.1418 | 357.0108 | 21.5194 | 21.9613 | 41.7758 | 87.9327 | 94.9437 | 24.2738 | 52.3184 | 94.3096 | 714.7644 | 635.0137 | 711.2807 | 728.216 | 704.649 |  | 727.7459 | 697.0097 | 815.6398 | 586.9448 | 600.8931 | 697.7372 |  | 545.3419 |  |  | 468.5813 | 605.1912 | 682.5011 | [5 empty] | 21.8335 | 566.6984 | 21.886 | 22.0435 | 415.3543 | 21.383 | 21.8377 | 482.8321 | 599.3527 | 623.3124 |  | 943.3277 | 899.3849 | 525.6774 | 669.3815 | 770.1225 | 569.2011 | 627.9074 | 918.6454 | 934.5843 | 609.0566 | 738.5322 | 871.2166 | 1019.4503 | 1001.4408 | 501.2176 | 591.8115 | 634.2356 | 547.9361 | 679.4535 | 805.0783 | 900.5117 | 1060.3038 | 559.58 | 620.5057 | 616.8901 | 733.8085 | 54.1063 | 0.00030681 | 19.5681 | 3.9597 | -28.4412 | 3.0963 | 8864.83 | -0.06 | 1.6841 | 1.6847 | -12.8569 | -1.4558 | 6.3373 | -34.1903 | -34.6662 | 57.545 | 82.9771 | 33.4788 | 62.4532 | 5.5171 | 61.2422 | 31.3919
42838.4316 | 978 | 22.7714 | 22.7749 | 22.7831 | 22.6892 | 22.302 | 21.6275 | 22.6509 | 21.6857 | 22.2936 | 22.2977 | 22.2625 | 21.9112 | 21.1309 | 22.0957 | 21.4787 | 22.0607 | 22.9061 | 22.332 | 37.4474 | 44.9434 | 82.345 | 88.8583 | 89.7785 | 24.6565 | 48.2035 | 89.8605 | 632.3535 | 662.3258 | 634.432 | 23.568 | 52.5389 | 94.4974 | 24.5569 | 50.8787 | 92.593 | 741.0126 | 737.7587 |  | 395.2164 | 760.6029 | 770.4406 | 691.3064 |  | 401.2988 | 647.6079 | 584.2673 | 840.8377 | 946.0259 | 945.1375 | 930.3887 | 45.7713 | 266.6562 | 61.7784 | 495.2734 | 71.1416 | 51.575 | 49.762 | 54.1225 | 41.7025 |  |  | 0.51212 | 0.33704 | -35.7472 | 0.029526 | 7.4913 | -197.6475 | -203.3021 | -2.023 | 13.3183 | 38.836 | 18.0792 | 5.914e-05 | 8.22e-06 | 0.0003762 | 27.527 | 22.1243 | 22.1082 | 22.1423 | 21.9443 | 21.2198 | 20.0606 | 22.1345 | 22.3075 | 22.3402 | 22.2794 | 21.8847 | 21.1197 | 22.2021 | 727.9548 | 589.3628 | 564.8689 | 366.5496 | 310.2875 | 746.9125 | 477.2046 | 22.2447 | 22.1478 | 22.771 | 22.2083 | 32.2014 | 41.4373 | 26.6106 | 80.2067 | 86.5595 | 582.8194 | 542.5635 | 546.1917 | 548.2809 | 88.6578 | 47.1251 | 752.4216 | 22.0446 | 22.1463 | 357.0465 | 21.5236 | 21.9606 | 41.9376 | 87.9478 | 95.0175 | 24.2983 | 52.4299 | 94.4203 | 716.5541 | 634.9631 | 711.3291 | 728.4476 | 706.7954 |  | 727.5312 | 696.1513 | 815.634 | 589.9413 | 601.0701 | 697.0532 |  | 546.0057 |  |  | 468.0419 | 604.8239 | 683.1272 | [5 empty] | 21.8257 | 567.8077 | 21.889 | 22.0397 | 414.6531 | 21.3786 | 21.8479 | 482.4053 | 600.6315 | 622.74 |  | 944.3547 | 898.3185 | 525.4592 | 670.1148 | 771.1908 | 569.2404 | 628.2584 | 917.6942 | 934.7193 | 608.8015 | 740.3383 | 869.6063 | 1019.6349 | 1002.7926 | 501.5517 | 591.3671 | 633.6311 | 547.288 | 678.3952 | 802.7223 | 899.9169 | 1060.91 | 559.2202 | 620.5863 | 616.4213 | 733.102 | 55.016 | -2.3207e-05 | 19.5688 | 3.9712 | -28.4513 | 3.0964 | 8872.04 | -0.13 | 1.5024 | 1.2277 | -12.6433 | 0.36336 | 6.6576 | -34.197 | -34.6827 | 57.4306 | 82.9991 | 33.4273 | 63.4953 | 8.2337 | 61.3617 | 31.3974
42838.4316 | 979 | 22.774 | 22.7743 | 22.7805 | 22.6941 | 22.2982 | 21.6234 | 22.63 | 21.684 | 22.2814 | 22.2933 | 22.2607 | 21.9018 | 21.1127 | 22.0906 | 21.4884 | 22.075 | 22.9165 | 22.3818 | 37.5796 | 45.0615 | 82.4289 | 88.8887 | 89.7939 | 24.6733 | 48.3191 | 89.8882 | 631.1254 | 661.4329 | 633.1484 | 23.5932 | 52.6623 | 94.5421 | 24.5927 | 50.9839 | 92.6664 | 741.0465 | 734.1424 |  | 393.3436 | 760.6119 | 770.8307 | 688.6752 |  | 402.3374 | 647.1736 | 585.6397 | 842.4181 | 947.4461 | 945.528 | 931.5707 | 45.8443 | 267.6414 | 62.1561 | 496.2024 | 71.0781 | 51.6466 | 49.7777 | 54.1662 | 41.8027 |  |  | 0.54432 | 0.84564 | -34.5927 | -0.36737 | 7.716 | -191.2505 | -203.2167 | -2.5973 | 12.5639 | 37.2644 | 18.2434 | -1.643e-05 | 9.86e-06 | 0.00038606 | 27.5663 | 22.1268 | 22.0987 | 22.1461 | 21.9394 | 21.2142 | 20.0579 | 22.133 | 22.3049 | 22.3384 | 22.2869 | 21.8809 | 21.1147 | 22.204 | 710.0749 | 588.3329 | 551.0577 | 362.6623 | 302.1442 | 747.5717 | 478.0985 | 22.2334 | 22.1505 | 22.7813 | 22.2039 | 32.2975 | 41.5523 | 26.6412 | 80.2219 | 86.5809 | 582.2587 | 540.9168 | 545.0862 | 549.6044 | 79.6987 | 44.3233 | 752.44 | 22.0403 | 22.1465 | 357.1611 | 21.5174 | 21.949 | 42.1011 | 87.9594 | 95.0841 | 24.321 | 52.5564 | 94.5249 | 717.5971 | 635.2612 | 711.2896 | 728.5002 | 706.7189 |  | 727.3808 | 695.7785 | 815.727 | 589.99 | 601.1751 | 696.7845 |  | 546.9179 |  |  | 468.1161 | 606.9645 | 682.957 | [5 empty] | 21.8342 | 568.1915 | 21.8932 | 22.0542 | 416.5013 | 21.3877 | 21.8469 | 482.611 | 601.6953 | 622.3058 |  | 949.8665 | 899.7713 | 524.9716 | 669.3929 | 770.6205 | 569.4711 | 627.8879 | 920.3265 | 936.3055 | 607.9198 | 738.0857 | 865.4575 | 1014.2155 | 1003.5481 | 501.6456 | 590.9717 | 632.6617 | 546.2683 | 677.1844 | 801.4797 | 898.8108 | 1061.8691 | 558.8491 | 620.1705 | 616.025 | 733.1701 | 54.9396 | -0.00019177 | 19.5698 | 3.9832 | -28.4086 | 3.0964 | 8833.68 | -0.1 | 1.5479 | 1.9442 | -12.4345 | -1.2814 | 6.7578 | -33.6444 | -34.681 | 57.3944 | 83.0392 | 33.4448 | 65.7141 | 9.9534 | 61.4438 | 31.2654
42838.4316 | 980 | 22.7668 | 22.7697 | 22.7726 | 22.6905 | 22.2947 | 21.6128 | 22.6289 | 21.6788 | 22.2897 | 22.2948 | 22.2588 | 21.902 | 21.118 | 22.0936 | 21.4794 | 22.0833 | 22.9282 | 22.41 | 37.6865 | 45.1833 | 82.493 | 88.9015 | 89.8064 | 24.7014 | 48.4153 | 89.9183 | 630.5873 | 660.2382 | 633.0982 | 23.6087 | 52.778 | 94.6164 | 24.6253 | 51.0844 | 92.7332 | 741.268 | 731.339 |  | 393.6371 | 760.308 | 770.4415 | 689.8025 |  | 402.9118 | 645.7217 | 584.4388 | 844.1773 | 946.2715 | 948.2179 | 934.2212 | 45.6796 | 268.5317 | 64.0877 | 497.0406 | 71.086 | 51.7152 | 49.7815 | 54.192 | 41.9189 |  |  | 0.22825 | 1.1019 | -33.6234 | -0.60656 | 7.7239 | -197.8256 | -203.1917 | -2.2227 | 13.0556 | 37.724 | 17.6983 | 6.078e-05 | 8.214e-05 | 0.00036963 | 27.6127 | 22.1295 | 22.1009 | 22.1485 | 21.9391 | 21.2108 | 20.0662 | 22.1396 | 22.3116 | 22.3442 | 22.2848 | 21.8858 | 21.1171 | 22.2073 | 699.4602 | 587.8226 | 522.0526 | 345.9356 | 284.2681 | 747.0912 | 478.2223 | 22.2426 | 22.1636 | 22.7962 | 22.2229 | 32.4093 | 41.6534 | 26.686 | 80.2554 | 86.6106 | 582.0463 | 543.043 | 546.6611 | 553.1706 | 84.6159 | 42.1451 | 752.8881 | 22.0394 | 22.1442 | 357.3796 | 21.5118 | 21.958 | 42.2646 | 87.9759 | 95.1483 | 24.3505 | 52.6677 | 94.6287 | 718.1685 | 635.7335 | 711.404 | 728.6126 | 708.1936 |  | 727.2711 | 696.5819 | 816.0151 | 590.3979 | 601.3271 | 696.8637 |  | 547.5726 |  |  | 467.5612 | 608.1078 | 684.1598 | [5 empty] | 21.8407 | 567.8942 | 21.9 | 22.0503 | 417.9086 | 21.3955 | 21.8398 | 482.6458 | 601.7674 | 621.7325 |  | 954.1191 | 900.7895 | 524.3437 | 668.5963 | 770.3739 | 569.1328 | 627.5774 | 919.9214 | 936.3384 | 606.9651 | 738.8808 | 861.8036 | 1013.9314 | 1003.9816 | 501.4904 | 590.3353 | 631.2108 | 545.3892 | 676.6062 | 799.5565 | 896.552 | 1059.5469 | 557.8847 | 618.9625 | 615.6195 | 731.8905 | 54.088 | -1.6191e-05 | 19.5699 | 3.9938 | -28.4383 | 3.0963 | 8852.64 | -0.09 | 1.0023 | 2.2175 | -12.2494 | -1.6453 | 6.7687 | -34.2556 | -34.7171 | 57.3255 | 83.1093 | 33.4607 | 66.7243 | 13.2019 | 61.471 | 31.1303
42838.4316 | 981 | 22.7685 | 22.7729 | 22.7753 | 22.69 | 22.2981 | 21.6184 | 22.638 | 21.6795 | 22.2899 | 22.2945 | 22.2597 | 21.8998 | 21.1181 | 22.0985 | 21.47 | 22.0827 | 22.9462 | 22.4405 | 37.8133 | 45.299 | 82.579 | 88.9313 | 89.8167 | 24.7222 | 48.5219 | 89.9551 | 630.0351 | 659.4069 | 632.5572 | 23.6264 | 52.899 | 94.68 | 24.6532 | 51.1864 | 92.7941 | 741.726 | 733.1295 |  | 394.8808 | 761.6271 | 772.1362 | 693.0075 |  | 402.7631 | 644.4117 | 584.0767 | 833.6571 | 941.0518 | 951.0752 | 933.8028 | 45.7342 | 269.4627 | 64.5243 | 497.8834 | 71.0937 | 51.7593 | 49.7903 | 54.2103 | 42.0341 |  |  | 0.18554 | -0.24451 | -31.9333 | -0.12227 | 9.0033 | -197.8164 | -203.2115 | -2.1268 | 12.5119 | 36.6293 | 17.7566 | 0.00013964 | 5.421e-05 | 0.00041398 | 27.673 | 22.1352 | 22.1028 | 22.1517 | 21.94 | 21.208 | 20.0639 | 22.1389 | 22.3044 | 22.3428 | 22.2887 | 21.8883 | 21.1163 | 22.2131 | 676.0552 | 585.3076 | 518.8725 | 346.9945 | 277.5291 | 746.5579 | 478.2045 | 22.2381 | 22.1552 | 22.8066 | 22.2215 | 32.4995 | 41.7503 | 26.7232 | 80.2996 | 86.6365 | 581.8504 | 544.7282 | 548.0249 | 553.9505 | 91.41 | 52.341 | 754.007 | 22.0441 | 22.1414 | 357.4728 | 21.5116 | 21.9629 | 42.4276 | 87.9987 | 95.2198 | 24.3888 | 52.7858 | 94.7352 | 718.5893 | 636.3023 | 712.1606 | 729.269 | 708.615 |  | 727.256 | 696.6489 | 816.3219 | 590.1604 | 601.366 | 696.7019 |  | 548.354 |  |  | 466.3818 | 608.7219 | 684.4046 | [5 empty] | 21.8287 | 568.5666 | 21.8984 | 22.0372 | 417.8241 | 21.3963 | 21.8418 | 482.3446 | 601.1929 | 621.2572 |  | 954.3013 | 900.3344 | 523.5422 | 668.6437 | 771.4644 | 568.4842 | 627.0221 | 920.9478 | 936.8954 | 606.2934 | 741.5623 | 857.5075 | 1018.5349 | 1002.1903 | 500.9579 | 589.3693 | 630.2772 | 545.3181 | 676.4421 | 799.8369 | 896.1259 | 1056.6412 | 556.6498 | 617.8094 | 615.4101 | 731.5749 | 53.5161 | -2.1587e-06 | 19.5698 | 3.9986 | -28.4173 | 3.0964 | 8943.49 | -0.02 | 0.90339 | -1.0438 | -11.9291 | -0.73814 | 7.3164 | -34.2948 | -34.7594 | 57.3099 | 83.2059 | 33.4743 | 69.1373 | 13.5515 | 61.5032 | 31.0754
42838.4316 | 982 | 22.7735 | 22.7773 | 22.7795 | 22.6907 | 22.3021 | 21.6295 | 22.6456 | 21.6821 | 22.2917 | 22.294 | 22.2639 | 21.9003 | 21.1232 | 22.0972 | 21.4712 | 22.0866 | 22.951 | 22.473 | 37.9367 | 45.4143 | 82.6686 | 88.9573 | 89.8257 | 24.7401 | 48.6232 | 89.9869 | 629.4704 | 658.91 | 632.3205 | 23.6375 | 53.0174 | 94.7398 | 24.6721 | 51.2801 | 92.8509 | 742.2406 | 736.4718 |  | 395.2955 | 764.6043 | 775.2311 | 695.265 |  | 402.4191 | 643.2779 | 583.6392 | 831.4234 | 938.1996 | 954.417 | 932.611 | 45.6713 | 270.2149 | 65.2906 | 498.4541 | 71.0196 | 51.7783 | 49.7937 | 54.2462 | 42.1258 |  |  | 0.49109 | 0.84959 | -30.9542 | 0.11627 | 9.4192 | -197.8263 | -203.3034 | -2.1406 | 12.3082 | 36.0798 | 18.0689 | -3.614e-05 | -0.00010514 | 0.00040413 | 27.7166 | 22.1258 | 22.1029 | 22.1397 | 21.9386 | 21.2129 | 20.0539 | 22.1249 | 22.2956 | 22.3369 | 22.2811 | 21.8897 | 21.1185 | 22.2002 | 661.3046 | 595.7148 | 529.4238 | 344.1031 | 283.2066 | 746.6335 | 478.8073 | 22.238 | 22.1535 | 22.8168 | 22.2131 | 32.5969 | 41.8498 | 26.7574 | 80.3541 | 86.6591 | 581.5886 | 545.1616 | 549.528 | 553.9337 | 99.0294 | 49.7063 | 754.73 | 22.0437 | 22.1396 | 357.7134 | 21.5093 | 21.9583 | 42.5853 | 88.0183 | 95.2837 | 24.4105 | 52.9007 | 94.842 | 718.6646 | 636.5281 | 713.1357 | 730.0751 | 709.4172 |  | 727.1933 | 695.6567 | 816.4508 | 591.712 | 601.415 | 696.1937 |  | 549.4228 |  |  | 465.0199 | 608.7561 | 685.4588 | [5 empty] | 21.8354 | 569.1492 | 21.8974 | 22.0469 | 417.7893 | 21.3995 | 21.8431 | 482.1735 | 600.7404 | 620.8964 |  | 957.0596 | 900.3058 | 522.9247 | 670.5727 | 773.3047 | 568.0342 | 626.814 | 924.9807 | 938.5996 | 606.1229 | 742.9158 | 859.1912 | 1020.8848 | 998.0571 | 500.4328 | 588.4458 | 629.3944 | 545.4287 | 676.0273 | 798.4174 | 896.6193 | 1053.724 | 555.9431 | 617.225 | 615.375 | 731.2025 | 53.5582 | -0.00026899 | 19.5692 | 3.9996 | -28.4705 | 3.0963 | 9006.75 | -0.03 | 1.4696 | 1.9446 | -11.7375 | 0.71935 | 7.4937 | -34.3425 | -34.8146 | 57.2717 | 83.2749 | 33.44 | 70.8028 | 12.5042 | 61.5769 | 31.0315
42838.4317 | 983 | 22.7735 | 22.774 | 22.7765 | 22.6971 | 22.3064 | 21.6287 | 22.6432 | 21.679 | 22.2907 | 22.3004 | 22.2634 | 21.8993 | 21.1211 | 22.1019 | 21.4715 | 22.0954 | 22.9572 | 22.5078 | 38.054 | 45.5201 | 82.7504 | 88.9714 | 89.835 | 24.7636 | 48.7287 | 90.0154 | 628.5599 | 658.9979 | 631.3025 | 23.6613 | 53.1436 | 94.8148 | 24.7011 | 51.3787 | 92.9159 | 742.9639 | 731.8676 |  | 396.4001 | 767.32 | 777.7651 | 694.641 |  | 403.0212 | 642.3987 | 585.5429 | 826.4914 | 940.9728 | 951.9566 | 931.2181 | 46.0003 | 271.0221 | 66.8749 | 499.1972 | 70.9391 | 51.7882 | 49.8032 | 54.2634 | 42.2302 |  |  | 0.71057 | 0.38698 | -29.9206 | -0.35883 | 8.034 | -197.8519 | -203.2147 | -2.2056 | 12.8011 | 37.3991 | 17.9323 | 8.707e-05 | 1.15e-05 | 0.00038113 | 27.763 | 22.1268 | 22.0934 | 22.1377 | 21.9346 | 21.2064 | 20.0489 | 22.1222 | 22.2935 | 22.3313 | 22.2784 | 21.8781 | 21.1157 | 22.192 | 668.7441 | 616.1547 | 528.4125 | 341.5928 | 281.14 | 747.4524 | 479.4441 | 22.2389 | 22.1613 | 22.8307 | 22.2211 | 32.6968 | 41.9531 | 26.8018 | 80.4133 | 86.702 | 581.3094 | 546.3296 | 549.7264 | 552.9018 | 94.3896 | 48.2914 | 754.4983 | 22.044 | 22.1394 | 358.4089 | 21.5181 | 21.9604 | 42.7517 | 88.0445 | 95.3518 | 24.438 | 53.0158 | 94.9472 | 717.9892 | 636.1944 | 714.0942 | 730.844 | 707.1913 |  | 726.925 | 695.0502 | 816.6789 | 593.1487 | 601.5074 | 695.6159 |  | 550.1646 |  |  | 464.2472 | 608.4792 | 684.1768 | [5 empty] | 21.8364 | 570.0404 | 21.8959 | 22.047 | 417.7866 | 21.3919 | 21.8412 | 481.8818 | 600.6374 | 620.7916 |  | 957.6057 | 898.6888 | 522.4934 | 670.9663 | 773.3473 | 567.7135 | 627.1732 | 927.0459 | 939.0051 | 606.1908 | 741.2772 | 861.0745 | 1019.9928 | 999.1049 | 500.1224 | 587.5133 | 628.2545 | 545.2883 | 675.574 | 796.5033 | 894.5529 | 1054.2768 | 555.3463 | 616.1244 | 615.2467 | 730.0332 | 52.5726 | -0.00022685 | 19.5694 | 3.9997 | -28.4319 | 3.0963 | 9055.79 | -0.08 | 1.7667 | 1.3117 | -11.5343 | -1.2631 | 6.9139 | -34.3103 | -34.7721 | 57.2652 | 83.365 | 33.4167 | 70.2644 | 12.7488 | 61.7862 | 31.0129
42838.4317 | 984 | 22.7783 | 22.7779 | 22.7833 | 22.6993 | 22.3068 | 21.6327 | 22.6441 | 21.6899 | 22.3028 | 22.3043 | 22.2685 | 21.9164 | 21.1202 | 22.1091 | 21.4767 | 22.1019 | 22.9818 | 22.55 | 38.1797 | 45.6414 | 82.835 | 88.986 | 89.8654 | 24.7942 | 48.8367 | 90.0676 | 627.6506 | 659.0434 | 630.4938 | 23.6763 | 53.26 | 94.8998 | 24.7281 | 51.4785 | 92.9752 | 743.3376 | 729.3126 |  | 398.7305 | 769.5967 | 779.805 | 695.0125 |  | 402.8585 | 642.8816 | 588.606 | 827.9231 | 940.8431 | 952.4134 | 932.3453 | 46.5552 | 271.5749 | 67.1594 | 500.1174 | 71.1367 | 51.8187 | 49.8186 | 54.2724 | 42.3335 |  |  | 0.53841 | 0.1123 | -29.3798 | -0.36671 | 8.0163 | -197.865 | -203.1392 | -2.6032 | 12.9248 | 37.5048 | 17.5405 | 0.0001035 | -1.643e-05 | 0.00036634 | 27.8121 | 22.1361 | 22.0977 | 22.1443 | 21.9393 | 21.2091 | 20.0539 | 22.1275 | 22.3023 | 22.3398 | 22.2831 | 21.8837 | 21.1181 | 22.208 | 674.3173 | 617.1504 | 537.3415 | 350.4979 | 295.2244 | 747.7581 | 479.9318 | 22.2351 | 22.1664 | 22.8472 | 22.2198 | 32.8127 | 42.0639 | 26.8399 | 80.4575 | 86.7217 | 580.8796 | 544.7453 | 548.2978 | 551.6645 | 88.7329 | 49.9802 | 754.71 | 22.0425 | 22.1399 | 358.6797 | 21.5111 | 21.9542 | 42.9105 | 88.0676 | 95.4118 | 24.4643 | 53.1198 | 95.0402 | 719.6942 | 635.6034 | 715.6939 | 731.848 | 705.2324 |  | 726.6922 | 694.8652 | 816.9542 | 593.3977 | 601.5761 | 695.3254 |  | 551.2035 |  |  | 464.0769 | 608.2213 | 683.3365 | [5 empty] | 21.8325 | 570.2721 | 21.8967 | 22.0403 | 416.8926 | 21.3948 | 21.8344 | 481.5938 | 600.8005 | 620.9939 |  | 963.6767 | 899.7344 | 522.1095 | 670.5874 | 771.9003 | 567.7676 | 626.5442 | 926.9827 | 941.7684 | 606.2489 | 741.1105 | 856.3714 | 1017.2577 | 1001.8978 | 499.6138 | 586.9403 | 626.7254 | 544.52 | 675.6165 | 795.2556 | 892.8818 | 1052.5969 | 554.8373 | 614.9944 | 614.9924 | 730.2993 | 53.5294 | 0.0023361 | 19.5694 | 3.9977 | -28.4299 | 3.0963 | 9058.25 | -0.07 | 1.5372 | 0.70683 | -11.4326 | -1.2773 | 6.9075 | -34.3178 | -34.7722 | 57.2603 | 83.4587 | 33.4221 | 69.7529 | 11.8581 | 61.8752 | 30.9745
42838.4317 | 985 | 22.7692 | 22.7698 | 22.7811 | 22.6892 | 22.302 | 21.6207 | 22.6384 | 21.6735 | 22.2898 | 22.304 | 22.2592 | 21.902 | 21.1256 | 22.0994 | 21.4795 | 22.1112 | 22.9913 | 22.5835 | 38.2979 | 45.7623 | 82.901 | 88.9914 | 89.8887 | 24.8189 | 48.9365 | 90.1024 | 627.454 | 659.656 | 630.8028 | 23.6951 | 53.3929 | 94.9712 | 24.7504 | 51.5883 | 93.0369 | 743.7624 | 736.0344 |  | 405.6997 | 770.3539 | 781.0493 | 695.7751 |  | 402.666 | 642.863 | 587.4625 | 822.2201 | 942.0747 | 952.6104 | 931.4136 | 47.3847 | 272.0519 | 67.3872 | 501.0103 | 71.1475 | 51.8549 | 49.826 | 54.2927 | 42.4309 |  |  | 0.59558 | 0.39552 | -31.5621 | -0.48303 | 8.3514 | -197.8617 | -203.1398 | -2.6433 | 12.494 | 36.932 | 17.3752 | 9.86e-06 | -8.21e-06 | 0.00033677 | 27.8618 | 22.1459 | 22.1007 | 22.1471 | 21.9419 | 21.2185 | 20.0661 | 22.1313 | 22.3091 | 22.3466 | 22.2866 | 21.8835 | 21.1232 | 22.2078 | 673.9994 | 619.5228 | 542.3259 | 357.9598 | 302.1934 | 747.3941 | 480.2446 | 22.2378 | 22.1651 | 22.8599 | 22.222 | 32.9017 | 42.1625 | 26.8809 | 80.4954 | 86.7427 | 580.4537 | 542.2537 | 546.7115 | 550.3568 | 79.3566 | 49.8707 | 755.4894 | 22.0481 | 22.1437 | 359.0047 | 21.5138 | 21.9547 | 43.0727 | 88.0984 | 95.4739 | 24.4965 | 53.2385 | 95.1453 | 722.6952 | 635.5747 | 718.5712 | 734.0341 | 707.3885 |  | 726.4888 | 695.0603 | 817.3556 | 591.9283 | 601.5791 | 695.3805 |  | 552.413 |  |  | 464.2846 | 607.9105 | 684.222 | [5 empty] | 21.8322 | 570.3349 | 21.9002 | 22.0358 | 416.4403 | 21.3949 | 21.8348 | 481.4268 | 600.6244 | 620.9183 |  | 968.6634 | 901.4549 | 521.5607 | 671.0264 | 770.3743 | 567.8225 | 626.0874 | 929.3266 | 942.8337 | 606.7501 | 743.9207 | 853.3239 | 1012.3758 | 1002.7182 | 499.0631 | 586.6087 | 625.5267 | 543.7613 | 676.0545 | 797.2626 | 892.78 | 1050.1381 | 554.3627 | 614.4965 | 614.8129 | 731.2896 | 54.6673 | 0.00025064 | 19.5679 | 3.9962 | -28.4833 | 3.0964 | 9051.11 | -0.07 | 1.617 | 1.3265 | -11.8495 | -1.4659 | 7.051 | -34.3203 | -34.775 | 57.1487 | 83.5824 | 33.4634 | 69.6599 | 11.3693 | 61.9671 | 30.9389
42838.4317 | 986 | 22.7775 | 22.7696 | 22.7747 | 22.6813 | 22.2946 | 21.6185 | 22.6358 | 21.6779 | 22.2898 | 22.2871 | 22.2571 | 21.9017 | 21.121 | 22.0974 | 21.4753 | 22.1181 | 23.0001 | 22.6184 | 38.4155 | 45.8744 | 82.9551 | 88.9978 | 89.9058 | 24.8399 | 49.0402 | 90.134 | 628.6702 | 660.2161 | 632.9244 | 23.7257 | 53.5243 | 95.0553 | 24.7855 | 51.6919 | 93.0932 | 744.0116 | 730.6392 |  | 404.3316 | 770.0884 | 781.5461 | 693.9359 |  | 402.7914 | 642.6087 | 585.8184 | 817.442 | 939.2808 | 950.449 | 930.4524 | 47.5077 | 272.4519 | 68.7293 | 501.9706 | 71.0319 | 51.8873 | 49.8278 | 54.3143 | 42.5311 |  |  | 0.40436 | 0.96392 | -34.1912 | -0.19915 | 8.7404 | -197.8709 | -203.0905 | -2.5717 | 12.435 | 36.1669 | 17.6634 | 0.00020042 | 0.00012157 | 0.00036799 | 27.903 | 22.1393 | 22.093 | 22.1419 | 21.9362 | 21.2111 | 20.0624 | 22.1316 | 22.3034 | 22.3375 | 22.279 | 21.8836 | 21.125 | 22.1963 | 671.4499 | 599.56 | 541.6378 | 358.8397 | 294.5766 | 746.5375 | 480.298 | 22.2367 | 22.1655 | 22.8701 | 22.2289 | 33.0019 | 42.2651 | 26.9196 | 80.5367 | 86.7615 | 580.029 | 540.3398 | 546.3098 | 550.9349 | 92.1348 | 47.6428 | 756.901 | 22.0538 | 22.1476 | 359.4947 | 21.521 | 21.9595 | 43.2462 | 88.1348 | 95.536 | 24.5288 | 53.3599 | 95.2529 | 724.6907 | 635.7871 | 720.9548 | 736.3229 | 708.7816 |  | 726.3629 | 695.5281 | 817.8668 | 590.5314 | 601.5775 | 695.6681 |  | 553.4707 |  |  | 464.6494 | 608.4539 | 685.1137 | [5 empty] | 21.8282 | 570.4046 | 21.9023 | 22.0322 | 416.954 | 21.3931 | 21.8343 | 481.0854 | 600.4256 | 620.5968 |  | 967.7718 | 900.0023 | 521.0633 | 672.1965 | 768.6489 | 567.504 | 626.4397 | 931.0632 | 942.103 | 607.0503 | 744.489 | 850.958 | 1008.3247 | 1004.7708 | 498.7205 | 586.3473 | 625.1449 | 542.9033 | 675.8662 | 797.7467 | 895.0676 | 1050.3162 | 554.0994 | 614.5216 | 614.5082 | 730.9351 | 54.9719 | 0.00013829 | 19.5675 | 3.9892 | -28.4215 | 3.0964 | 9069.42 | -0.06 | 1.3339 | 2.0705 | -12.3315 | -0.94113 | 7.207 | -34.2908 | -34.7401 | 57.078 | 83.734 | 33.502 | 69.6418 | 11.4569 | 62.0846 | 30.8512
42838.4317 | 987 | 22.7676 | 22.7652 | 22.7677 | 22.6789 | 22.2945 | 21.6159 | 22.6363 | 21.675 | 22.2917 | 22.2903 | 22.2581 | 21.8955 | 21.1171 | 22.0956 | 21.4787 | 22.1205 | 23.0111 | 22.6576 | 38.5347 | 45.9855 | 83.0134 | 89.0041 | 89.9216 | 24.8631 | 49.1407 | 90.1695 | 629.8321 | 661.0537 | 634.0469 | 23.7397 | 53.6479 | 95.1475 | 24.8171 | 51.7998 | 93.1466 | 743.949 | 728.2037 |  | 405.4675 | 771.1678 | 783.2116 | 692.9942 |  | 402.8013 | 642.5764 | 584.2764 | 821.3525 | 940.4319 | 949.6099 | 929.966 | 47.5357 | 272.8187 | 70.5389 | 502.7278 | 71.1275 | 51.9202 | 49.8384 | 54.3558 | 42.6064 |  |  | 0.71189 | 0.88638 | -37.4617 | -0.37197 | 7.1903 | -197.8309 | -203.2036 | -2.2852 | 12.2786 | 36.0834 | 17.7847 | 0.00026778 | 5.257e-05 | 0.00039263 | 27.9584 | 22.1511 | 22.0937 | 22.1406 | 21.9484 | 21.21 | 20.0631 | 22.1273 | 22.3045 | 22.3425 | 22.2778 | 21.8822 | 21.116 | 22.2063 | 694.5095 | 582.1407 | 545.2001 | 363.4712 | 293.7887 | 746.8182 | 480.6925 | 22.234 | 22.1738 | 22.8758 | 22.2294 | 33.1026 | 42.3613 | 26.9588 | 80.5845 | 86.7836 | 579.7624 | 541.8673 | 548.262 | 552.872 | 123.9081 | 63.0875 | 758.2093 | 22.043 | 22.136 | 359.5788 | 21.5099 | 21.9482 | 43.4031 | 88.155 | 95.5873 | 24.5467 | 53.4624 | 95.3487 | 726.0955 | 635.7385 | 722.1997 | 737.0853 | 711.2929 |  | 726.3963 | 695.4394 | 818.3209 | 589.1824 | 601.49 | 695.8184 |  | 554.2502 |  |  | 464.9968 | 609.6859 | 685.7776 | [5 empty] | 21.8343 | 569.8189 | 21.9046 | 22.0432 | 417.4582 | 21.4004 | 21.8384 | 481.0157 | 600.544 | 621.2801 |  | 965.4808 | 898.2476 | 520.9209 | 672.3719 | 766.5987 | 567.3812 | 627.1961 | 930.4316 | 939.7079 | 606.8716 | 743.2243 | 848.0523 | 1007.0114 | 1007.2571 | 498.834 | 586.1256 | 625.078 | 541.8732 | 675.3551 | 798.0285 | 895.7745 | 1051.2221 | 553.7035 | 614.7937 | 614.1815 | 730.564 | 54.3584 | 0.00018741 | 19.5698 | 3.9764 | -28.4482 | 3.0964 | 9057.81 | -0.07 | 1.771 | 1.9855 | -12.9075 | -1.2862 | 6.5345 | -34.2756 | -34.7379 | 57.0167 | 83.8829 | 33.5237 | 67.1783 | 11.1432 | 62.0941 | 30.7524
42838.4317 | 988 | 22.7703 | 22.7753 | 22.7767 | 22.6887 | 22.2985 | 21.6248 | 22.6419 | 21.6757 | 22.2941 | 22.2947 | 22.2592 | 21.9041 | 21.1191 | 22.0995 | 21.4851 | 22.1312 | 23.0271 | 22.6925 | 38.6666 | 46.0978 | 83.073 | 89.0092 | 89.942 | 24.8865 | 49.2392 | 90.2036 | 630.7847 | 662.0582 | 634.8387 | 23.7587 | 53.76 | 95.2152 | 24.8402 | 51.9022 | 93.1891 | 744.1958 | 729.0837 |  | 404.2364 | 774.1842 | 786.545 | 694.1501 |  | 402.5994 | 641.2931 | 585.508 | 829.0652 | 939.2876 | 945.6161 | 927.7976 | 47.3469 | 273.4312 | 72.1954 | 503.4449 | 71.0606 | 51.9386 | 49.8522 | 54.4004 | 42.5712 |  |  | 0.6442 | 0.63668 | -40.4049 | 0.30354 | 8.2726 | -197.8158 | -203.0879 | -2.5447 | 12.6125 | 36.9258 | 17.9283 | 0.00031542 | 2.793e-05 | 0.0003647 | 28.0238 | 22.1589 | 22.1179 | 22.1553 | 21.9502 | 21.2201 | 20.0706 | 22.1506 | 22.3207 | 22.3459 | 22.2899 | 21.8957 | 21.141 | 22.2194 | 723.5088 | 630.9542 | 600.7371 | 365.1027 | 297.1604 | 748.8822 | 482.5125 | 22.232 | 22.176 | 22.9036 | 22.2346 | 33.2028 | 42.4718 | 27.0078 | 80.6192 | 86.797 | 579.5336 | 545.1237 | 550.1487 | 553.0583 | 110.6294 | 64.9431 | 758.3521 | 22.0471 | 22.1419 | 360.0884 | 21.5148 | 21.9496 | 43.5648 | 88.1742 | 95.6579 | 24.5843 | 53.5795 | 95.4584 | 724.2824 | 635.8617 | 722.7052 | 736.98 | 709.8937 |  | 726.2938 | 694.9723 | 818.5751 | 588.5163 | 601.3903 | 695.4935 |  | 554.8635 |  |  | 465.3044 | 610.6692 | 685.6982 | [5 empty] | 21.834 | 569.7112 | 21.9072 | 22.0438 | 418.3527 | 21.4012 | 21.8443 | 481.3528 | 601.025 | 622.1355 |  | 960.3992 | 896.3592 | 520.5872 | 671.5775 | 765.1221 | 567.6332 | 628.6174 | 934.1067 | 937.891 | 606.5709 | 742.6169 | 845.694 | 1005.2906 | 1007.1074 | 498.8082 | 585.825 | 625.2619 | 541.208 | 674.9845 | 799.5511 | 897.0329 | 1050.9284 | 553.2744 | 614.967 | 613.7588 | 730.9333 | 54.0861 | -0.0069677 | 19.5695 | 3.9741 | -28.4328 | 3.0964 | 9033.26 | -0.06 | 1.6855 | 1.6815 | -13.3956 | 1.1611 | 6.9976 | -34.2182 | -34.6712 | 57.0295 | 83.978 | 33.5243 | 64.6837 | 5.3521 | 62.1277 | 30.7087
42838.4317 | 989 | 22.7739 | 22.7776 | 22.7734 | 22.6902 | 22.3028 | 21.6226 | 22.642 | 21.679 | 22.2937 | 22.2999 | 22.2634 | 21.9013 | 21.1244 | 22.1049 | 21.4806 | 22.137 | 23.0387 | 22.7319 | 38.7819 | 46.2164 | 83.1302 | 89.0166 | 89.9645 | 24.9099 | 49.3471 | 90.2398 | 631.4205 | 662.3759 | 634.6415 | 23.7854 | 53.8849 | 95.3097 | 24.8656 | 52.0062 | 93.2285 | 744.4057 | 725.409 |  | 404.6623 | 776.4265 | 788.8168 | 692.9994 |  | 402.0737 | 641.1156 | 586.2017 | 826.2229 | 937.7255 | 947.0391 | 926.5884 | 47.3446 | 274.054 | 72.4127 | 504.2182 | 71.1205 | 51.9575 | 49.8556 | 54.4251 | 42.6631 |  |  | 0.87682 | -0.10849 | -44.5165 | -0.047358 | 7.4275 | -197.8762 | -203.3054 | -2.7149 | 13.0375 | 38.0247 | 17.7801 | 0.0004682 | 0.00013142 | 0.00035813 | 28.0549 | 22.1483 | 22.0933 | 22.1413 | 21.9367 | 21.2039 | 20.0573 | 22.1245 | 22.2946 | 22.3389 | 22.2827 | 21.8837 | 21.1171 | 22.2046 | 723.7798 | 645.8149 | 598.4978 | 370.8555 | 299.1495 | 750.2055 | 484.2358 | 22.2294 | 22.1711 | 22.9067 | 22.2333 | 33.3036 | 42.5672 | 27.046 | 80.6519 | 86.8233 | 579.2046 | 544.8336 | 548.9162 | 551.5215 | 91.4235 | 55.6986 | 758.5222 | 22.058 | 22.1466 | 361.3725 | 21.5215 | 21.9541 | 43.7303 | 88.2024 | 95.7311 | 24.6283 | 53.6961 | 95.5674 | 722.3889 | 635.9458 | 722.4123 | 736.4767 | 708.3101 |  | 726.219 | 695.2747 | 819.3068 | 588.398 | 601.3489 | 695.424 |  | 555.1854 |  |  | 466.0216 | 610.3496 | 684.8633 | [5 empty] | 21.8265 | 570.0658 | 21.9026 | 22.0387 | 418.9947 | 21.4024 | 21.8404 | 481.7123 | 601.6019 | 622.7141 |  | 961.3356 | 895.711 | 520.2849 | 671.1552 | 764.5643 | 567.9083 | 630.186 | 940.2636 | 941.665 | 606.4761 | 742.6598 | 845.7779 | 1005.8721 | 1009.4247 | 498.83 | 585.5811 | 626.0394 | 540.8937 | 674.3882 | 798.2722 | 904.0683 | 1052.5775 | 553.2809 | 615.0852 | 613.2226 | 730.9241 | 54.0318 | 0.0010511 | 19.57 | 3.972 | -28.451 | 3.0964 | 8976.78 | -0.04 | 1.9661 | -0.69406 | -14.0593 | -0.45856 | 6.6344 | -34.2434 | -34.71 | 57.0545 | 84.2061 | 33.5202 | 65.1217 | 5.9616 | 62.2157 | 30.6961
42838.4317 | 990 | 22.7721 | 22.7705 | 22.7744 | 22.6846 | 22.298 | 21.6187 | 22.6398 | 21.676 | 22.2907 | 22.2989 | 22.2576 | 21.9036 | 21.1234 | 22.1017 | 21.4755 | 22.1499 | 23.054 | 22.7742 | 38.9001 | 46.3281 | 83.1695 | 89.0321 | 89.9866 | 24.9283 | 49.4425 | 90.2777 | 631.1859 | 662.7338 | 633.5192 | 23.805 | 54.0043 | 95.3977 | 24.9011 | 52.101 | 93.2866 | 743.9655 | 725.6128 |  | 400.0755 | 778.0202 | 790.3821 | 688.3826 |  | 402.1461 | 641.5606 | 587.3456 | 830.4581 | 937.7865 | 947.3271 | 927.8954 | 47.4906 | 274.6592 | 73.3279 | 505.243 | 71.1398 | 51.9779 | 49.8744 | 54.4599 | 42.7935 |  |  | 0.76577 | -0.16369 | -49.8082 | 0.091954 | 5.3537 | -197.8427 | -203.2765 | -3.4469 | 13.4363 | 39.187 | 18.1988 | 0.00051912 | 0.0001495 | 0.00040577 | 28.109 | 22.1484 | 22.0949 | 22.1452 | 21.9431 | 21.2075 | 20.0598 | 22.1283 | 22.3012 | 22.3377 | 22.2799 | 21.882 | 21.1212 | 22.2042 | 685.7427 | 602.0667 | 581.2063 | 369.9672 | 307.8246 | 750.2745 | 485.5432 | 22.2361 | 22.1777 | 22.9241 | 22.2423 | 33.4041 | 42.6721 | 27.0906 | 80.6751 | 86.8375 | 578.8438 | 542.4624 | 546.6411 | 549.5214 | 86.1218 | 45.0183 | 760.7408 | 22.0638 | 22.1427 | 363.5796 | 21.5221 | 21.9554 | 43.8943 | 88.2252 | 95.7989 | 24.6565 | 53.8107 | 95.6707 | 722.6597 | 636.585 | 721.343 | 735.4212 | 710.1233 |  | 726.1735 | 696.3638 | 820.46 | 591.045 | 601.5386 | 696.0132 |  | 555.3275 |  |  | 465.8949 | 608.0914 | 685.3415 | [5 empty] | 21.8201 | 571.3291 | 21.9053 | 22.0327 | 419.6114 | 21.3959 | 21.8349 | 482.0192 | 602.1404 | 622.9852 |  | 969.0537 | 897.2513 | 519.9776 | 671.4587 | 763.8597 | 568.0648 | 631.3007 | 947.2107 | 948.128 | 605.9897 | 743.0807 | 848.1394 | 1009.3208 | 1010.4954 | 499.1357 | 585.7721 | 626.191 | 540.3604 | 673.6613 | 796.0483 | 911.4496 | 1054.3045 | 553.6817 | 615.8256 | 612.3109 | 730.4042 | 53.4046 | -0.00046561 | 19.57 | 3.9798 | -28.4401 | 3.0963 | 8889.14 | -0.04 | 1.8363 | -0.85274 | -14.8751 | 0.63914 | 5.6332 | -34.2446 | -34.7117 | 56.9926 | 84.5494 | 33.4807 | 69.3725 | 8.1573 | 62.2266 | 30.691
42838.4317 | 991 | 22.7767 | 22.772 | 22.7737 | 22.6921 | 22.3024 | 21.6276 | 22.6375 | 21.6867 | 22.2919 | 22.2991 | 22.2677 | 21.9028 | 21.1259 | 22.0981 | 21.4827 | 22.1526 | 23.0725 | 22.8146 | 39.0292 | 46.4456 | 83.2133 | 89.0303 | 90.0114 | 24.963 | 49.5448 | 90.3142 | 631.2304 | 662.2448 | 633.9216 | 23.8238 | 54.1239 | 95.4855 | 24.9278 | 52.2026 | 93.3389 | 743.2591 | 728.6112 |  | 400.6726 | 781.1567 | 793.0918 | 684.2924 |  | 403.1183 | 641.2715 | 589.3148 | 844.2407 | 938.612 | 946.4802 | 932.5354 | 47.2583 | 275.3108 | 74.535 | 506.4989 | 70.9255 | 51.9842 | 49.8749 | 54.4763 | 42.8943 |  |  | 0.85251 | 0.92318 | -53.3888 | 0.11364 | 7.8113 | -197.8296 | -203.3554 | -2.4626 | 12.8523 | 37.5029 | 17.8676 | 0.00061112 | 0.00024149 | 0.00037127 | 28.1585 | 22.1455 | 22.0946 | 22.138 | 21.934 | 21.1978 | 20.0577 | 22.1303 | 22.3004 | 22.3328 | 22.2726 | 21.8798 | 21.1155 | 22.1971 | 668.8921 | 566.8952 | 517.0712 | 353.8822 | 302.0684 | 749.7129 | 485.6507 | 22.2407 | 22.1849 | 22.9402 | 22.2437 | 33.5014 | 42.7665 | 27.124 | 80.6923 | 86.8523 | 578.529 | 541.75 | 545.9253 | 548.9801 | 91.2857 | 43.3647 | 764.2859 | 22.0665 | 22.1498 | 365.8321 | 21.5241 | 21.9562 | 44.0603 | 88.2481 | 95.8664 | 24.6907 | 53.9291 | 95.7674 | 722.5993 | 637.7821 | 720.8145 | 734.9357 | 710.7565 |  | 725.941 | 697.2428 | 821.9001 | 594.5349 | 601.9946 | 696.8378 |  | 555.6452 |  |  | 465.5311 | 605.0372 | 685.3664 | [5 empty] | 21.8304 | 573.2173 | 21.9135 | 22.0357 | 421.0092 | 21.4017 | 21.8348 | 482.5862 | 603.0919 | 622.6167 |  | 974.3577 | 899.5507 | 519.1958 | 671.0599 | 763.9343 | 568.347 | 632.29 | 947.9739 | 950.255 | 605.2053 | 743.0918 | 848.2954 | 1015.7709 | 1013.3039 | 499.3503 | 586.378 | 625.7877 | 539.6947 | 673.2384 | 794.6684 | 918.5557 | 1057.2399 | 554.1948 | 616.9231 | 611.3898 | 729.973 | 53.8335 | -0.00040238 | 19.5701 | 4.0062 | -28.3141 | 3.0963 | 8844.59 | -0.1 | 1.9379 | 2.0248 | -15.398 | 0.7104 | 6.8021 | -34.2316 | -34.7063 | 56.9159 | 84.993 | 33.4657 | 71.0459 | 15.3061 | 62.1521 | 30.6531
42838.4318 | 992 | 22.766 | 22.7725 | 22.7667 | 22.688 | 22.2897 | 21.6235 | 22.6401 | 21.6854 | 22.2936 | 22.2972 | 22.2634 | 21.8991 | 21.119 | 22.0991 | 21.4758 | 22.158 | 23.0855 | 22.854 | 39.1429 | 46.5622 | 83.2617 | 89.0319 | 90.0437 | 24.9864 | 49.6502 | 90.3451 | 631.4156 | 662.0103 | 633.7056 | 23.8419 | 54.2467 | 95.5691 | 24.9617 | 52.3055 | 93.3819 | 742.872 | 729.7525 |  | 402.9362 | 780.4021 | 792.3173 | 687.0151 |  | 403.7448 | 641.5415 | 589.6776 | 849.9522 | 936.5328 | 946.2265 | 933.3131 | 47.1186 | 275.8565 | 74.8372 | 507.4166 | 71.0846 | 51.989 | 49.8782 | 54.5137 | 43.0135 |  |  | 0.59295 | 1.1696 | -56.1625 | -0.01253 | 8.4526 | -197.8631 | -203.2818 | -2.7425 | 13.562 | 39.5608 | 17.448 | 0.00077704 | 0.00016099 | 0.00036634 | 28.2068 | 22.1519 | 22.0905 | 22.1425 | 21.9364 | 21.2044 | 20.0603 | 22.1323 | 22.3048 | 22.3347 | 22.278 | 21.8839 | 21.1192 | 22.1979 | 673.9296 | 583.9933 | 520.5481 | 346.2191 | 292.9809 | 749.7095 | 485.9175 | 22.2426 | 22.1877 | 22.9518 | 22.2489 | 33.5962 | 42.8676 | 27.1615 | 80.7096 | 86.8636 | 578.3208 | 541.046 | 545.9725 | 549.947 | 96.9995 | 60.3446 | 767.3237 | 22.0708 | 22.1485 | 367.1288 | 21.518 | 21.9588 | 44.2178 | 88.2755 | 95.9302 | 24.7201 | 54.0388 | 95.8708 | 723.1396 | 638.6468 | 721.2233 | 735.1608 | 709.2865 |  | 725.6005 | 697.543 | 823.2321 | 595.8955 | 602.3272 | 697.5374 |  | 556.4628 |  |  | 465.2655 | 603.2735 | 683.9963 | [5 empty] | 21.8345 | 574.7596 | 21.922 | 22.0395 | 421.1447 | 21.4111 | 21.8448 | 482.9896 | 604.898 | 622.716 |  | 979.991 | 901.3772 | 518.103 | 670.8704 | 763.3718 | 568.6431 | 633.9859 | 952.3412 | 952.5369 | 604.3449 | 742.2616 | 845.8502 | 1022.8931 | 1014.0932 | 499.75 | 587.1168 | 625.7807 | 539.1071 | 673.1772 | 793.2467 | 921.7803 | 1056.6994 | 554.5685 | 617.5791 | 610.9803 | 729.8471 | 54.3749 | 0.00034189 | 19.5691 | 4.0279 | -28.3441 | 3.0963 | 8871.71 | -0.05 | 1.616 | 2.2794 | -15.7953 | -0.23593 | 7.0751 | -34.2309 | -34.6965 | 56.8703 | 85.4191 | 33.4877 | 70.485 | 14.9758 | 61.9736 | 30.5913
42838.4318 | 993 | 22.7752 | 22.7749 | 22.7845 | 22.6865 | 22.304 | 21.6293 | 22.6434 | 21.6823 | 22.2937 | 22.2967 | 22.2669 | 21.9007 | 21.1228 | 22.1042 | 21.4784 | 22.1652 | 23.0968 | 22.8956 | 39.2705 | 46.6827 | 83.3337 | 89.0328 | 90.081 | 25.0123 | 49.7505 | 90.39 | 631.5 | 662.9872 | 634.0191 | 23.8662 | 54.3695 | 95.6674 | 24.9852 | 52.4033 | 93.4389 | 743.3209 | 733.0334 |  | 403.1896 | 780.1911 | 792.7337 | 690.5691 |  | 404.0316 | 641.0559 | 590.6813 | 839.1147 | 939.8847 | 945.9305 | 932.3574 | 47.7111 | 276.4061 | 74.7901 | 508.7224 | 71.0985 | 51.9873 | 49.8872 | 54.5446 | 43.1121 |  |  | 1.0069 | 0.546 | -58.0294 | 0.13401 | 8.1839 | -197.8282 | -203.1852 | -2.757 | 13.3742 | 38.9174 | 17.7252 | 0.00072611 | 9.364e-05 | 0.00040248 | 28.2603 | 22.1566 | 22.0986 | 22.1433 | 21.9392 | 21.2082 | 20.0616 | 22.1343 | 22.309 | 22.34 | 22.2789 | 21.8852 | 21.1187 | 22.2109 | 679.6137 | 595.3137 | 567.5261 | 350.7779 | 287.9494 | 750.2802 | 487.0264 | 22.2392 | 22.1923 | 22.9572 | 22.2491 | 33.6981 | 42.9759 | 27.2037 | 80.7344 | 86.8889 | 578.3343 | 543.9279 | 547.6886 | 553.5444 | 91.3563 | 44.93 | 768.9799 | 22.0667 | 22.1454 | 367.9032 | 21.5194 | 21.9616 | 44.3805 | 88.3055 | 95.9917 | 24.7508 | 54.1464 | 95.9813 | 724.6198 | 639.2071 | 721.7392 | 735.3642 | 710.7798 |  | 725.505 | 697.4062 | 824.2225 | 595.8574 | 602.531 | 697.8357 |  | 557.4115 |  |  | 464.6849 | 603.0832 | 684.9035 | [5 empty] | 21.8261 | 575.1119 | 21.9114 | 22.0402 | 421.4894 | 21.4097 | 21.8461 | 483.195 | 606.354 | 622.8193 |  | 982.452 | 901.8476 | 516.7839 | 670.6256 | 764.5493 | 569.0733 | 635.4305 | 958.7848 | 952.6059 | 603.6859 | 743.3052 | 843.1944 | 1027.7122 | 1010.9736 | 500.0815 | 587.7773 | 625.7796 | 538.8865 | 673.0517 | 795.8889 | 929.4552 | 1055.3406 | 555.0049 | 618.4471 | 610.8375 | 730.3654 | 54.6417 | 0.0011845 | 19.5684 | 4.0606 | -28.3749 | 3.0963 | 8919.25 | -0.04 | 2.1063 | 1.557 | -16.0514 | 0.77135 | 6.9608 | -34.2237 | -34.684 | 56.8046 | 85.7468 | 33.5255 | 70.0555 | 9.9895 | 61.9942 | 30.4936
42838.4318 | 994 | 22.7667 | 22.7727 | 22.7768 | 22.6884 | 22.3042 | 21.6242 | 22.6361 | 21.6814 | 22.2982 | 22.297 | 22.2691 | 21.9024 | 21.1173 | 22.1037 | 21.479 | 22.1723 | 23.1147 | 22.943 | 39.3933 | 46.7903 | 83.4142 | 89.0379 | 90.1184 | 25.0455 | 49.8493 | 90.43 | 632.2537 | 663.3405 | 634.1745 | 23.8966 | 54.4975 | 95.7777 | 25.0222 | 52.5072 | 93.4866 | 743.9489 | 730.6608 |  | 406.6698 | 779.5084 | 791.959 | 695.1332 |  | 405.2764 | 641.069 | 589.3098 | 828.5295 | 942.1572 | 947.5808 | 934.189 | 47.7776 | 276.8891 | 74.8514 | 509.9399 | 71.1459 | 51.9759 | 49.8934 | 54.5908 | 43.212 |  |  | 1.0378 | 0.17538 | -59.4139 | 0.32194 | 7.4998 | -197.8177 | -203.2207 | -2.4008 | 13.0081 | 37.8485 | 18.1307 | 0.00099389 | 0.00027599 | 0.00039098 | 28.3119 | 22.1653 | 22.1051 | 22.1497 | 21.9455 | 21.2188 | 20.0637 | 22.1395 | 22.3108 | 22.3486 | 22.2877 | 21.8906 | 21.1249 | 22.2053 | 670.5037 | 560.1784 | 517.2767 | 346.467 | 287.569 | 749.7677 | 486.8559 | 22.2402 | 22.2031 | 22.9833 | 22.2536 | 33.8126 | 43.0873 | 27.2488 | 80.7654 | 86.9245 | 578.3104 | 542.8802 | 547.9129 | 553.3275 | 98.0578 | 38.2924 | 770.0977 | 22.0663 | 22.1429 | 368.5861 | 21.52 | 21.9553 | 44.5415 | 88.3415 | 96.0549 | 24.7796 | 54.2545 | 96.0764 | 725.3936 | 639.4848 | 721.9985 | 735.4237 | 711.605 |  | 725.4572 | 697.4457 | 825.2896 | 595.351 | 602.6968 | 697.9846 |  | 558.2785 |  |  | 463.5961 | 604.8734 | 685.3051 | [5 empty] | 21.8251 | 575.239 | 21.9221 | 22.0431 | 420.9622 | 21.414 | 21.8396 | 483.6344 | 607.4769 | 623.0935 |  | 984.5824 | 902.6106 | 515.9942 | 670.6995 | 765.0602 | 569.6209 | 635.634 | 961.9071 | 953.0764 | 603.4891 | 743.2281 | 841.7604 | 1029.1616 | 1008.8362 | 499.9202 | 588.3569 | 626.3094 | 538.8569 | 673.055 | 797.6545 | 930.5535 | 1055.4169 | 555.3348 | 619.2275 | 610.705 | 730.8682 | 55.2343 | 0.00013124 | 19.5676 | 4.0776 | -28.4605 | 3.0963 | 8958.81 | -0.07 | 2.1385 | 0.88244 | -16.2419 | 1.1956 | 6.6681 | -34.246 | -34.7105 | 56.7696 | 86.0957 | 33.5694 | 70.8863 | 15.5369 | 62.0346 | 30.4957
42838.4318 | 995 | 22.7667 | 22.77 | 22.771 | 22.6859 | 22.2904 | 21.6102 | 22.6298 | 21.6747 | 22.288 | 22.2963 | 22.2533 | 21.8968 | 21.114 | 22.0881 | 21.4774 | 22.1783 | 23.1287 | 22.9878 | 39.5164 | 46.9117 | 83.494 | 89.0529 | 90.1414 | 25.0682 | 49.9484 | 90.4736 | 632.3333 | 663.4625 | 634.5962 | 23.9183 | 54.6142 | 95.8681 | 25.054 | 52.6124 | 93.5223 | 744.5626 | 729.5424 |  | 406.3364 | 778.8952 | 790.8562 | 695.636 |  | 406.4047 | 641.3971 | 587.6278 | 820.2082 | 941.9905 | 949.467 | 936.3411 | 47.5424 | 277.3061 | 74.6602 | 511.0687 | 71.1155 | 51.9528 | 49.9035 | 54.6441 | 43.1876 |  |  | 0.75263 | 1.4752 | -59.8654 | 0.14715 | 7.969 | -197.8834 | -203.2864 | -1.1345 | 13.0523 | 38.6535 | 18.3698 | 0.0012009 | 0.00035977 | 0.00035813 | 28.3588 | 22.1641 | 22.104 | 22.1515 | 21.9463 | 21.2131 | 20.068 | 22.1368 | 22.3127 | 22.3438 | 22.2939 | 21.8899 | 21.1368 | 22.2138 | 675.7755 | 553.8566 | 464.186 | 319.053 | 279.2585 | 749.421 | 486.2908 | 22.2301 | 22.1914 | 22.9941 | 22.2609 | 33.9021 | 43.1734 | 27.2823 | 80.7756 | 86.9506 | 578.1778 | 541.9938 | 548.3371 | 553.054 | 88.6208 | 52.5997 | 771.2557 | 22.0663 | 22.1303 | 369.5398 | 21.5144 | 21.9484 | 44.6957 | 88.3691 | 96.1194 | 24.8056 | 54.3644 | 96.1677 | 726.0891 | 639.3656 | 722.0727 | 735.2465 | 712.9217 |  | 725.6021 | 697.7293 | 826.3251 | 594.7025 | 602.783 | 698.2558 |  | 559.4932 |  |  | 462.9196 | 606.7549 | 686.3475 | [5 empty] | 21.8373 | 574.936 | 21.9244 | 22.0377 | 420.9648 | 21.4178 | 21.8399 | 483.554 | 607.981 | 623.7141 |  | 985.4847 | 903.0797 | 515.6189 | 670.8084 | 765.3429 | 570.1945 | 636.6091 | 963.0719 | 952.839 | 603.5736 | 745.1048 | 839.8012 | 1028.0216 | 1009.5835 | 499.5924 | 588.7556 | 626.616 | 538.8362 | 673.2568 | 796.8381 | 928.0094 | 1055.4049 | 555.4088 | 620.0641 | 610.6557 | 730.4513 | 54.5486 | 0.0013671 | 19.5682 | 4.0778 | -28.4489 | 3.0964 | 8982.33 | -0.08 | 1.8215 | 2.5597 | -16.3064 | 0.80844 | 6.8788 | -34.2781 | -34.7429 | 56.7697 | 86.4282 | 33.603 | 70.1779 | 21.3168 | 62.1843 | 30.481
42838.4318 | 996 | 22.7612 | 22.7708 | 22.774 | 22.6869 | 22.2924 | 21.612 | 22.644 | 21.6818 | 22.2941 | 22.2978 | 22.2572 | 21.8923 | 21.1158 | 22.0875 | 21.472 | 22.1736 | 23.1373 | 23.0228 | 39.6206 | 47.0178 | 83.5502 | 89.0505 | 90.1605 | 25.0864 | 50.0407 | 90.5234 | 631.2916 | 662.7159 | 633.3854 | 23.9429 | 54.7346 | 95.974 | 25.0733 | 52.696 | 93.5712 | 744.7681 | 725.6784 |  | 407.2238 | 777.9507 | 790.1354 | 691.9385 |  | 406.7923 | 641.743 | 588.8052 | 819.7037 | 942.8025 | 955.2108 | 937.8725 | 46.4355 | 277.8072 | 73.3957 | 512.2597 | 71.0687 | 51.9133 | 49.9038 | 54.6655 | 43.3185 |  |  | 0.53118 | 1.6256 | -59.8378 | 0.83449 | 7.9157 | -197.8184 | -200.1611 | -2.9916 | 13.5927 | 40.1235 | 19.005 | 0.0010284 | 0.00022506 | 0.0003877 | 28.4173 | 22.1737 | 22.0956 | 22.1426 | 21.9502 | 21.2155 | 20.0629 | 22.1329 | 22.3091 | 22.3375 | 22.2812 | 21.8889 | 21.1255 | 22.2102 | 658.2348 | 569.4494 | 522.0274 | 332.0625 | 276.1752 | 748.5044 | 487.2226 | 22.2199 | 22.1908 | 23.0009 | 22.2472 | 33.9978 | 43.2712 | 27.321 | 80.8189 | 86.9707 | 578.0402 | 542.886 | 548.5239 | 551.5646 | 90.0025 | 54.036 | 772.0943 | 22.061 | 22.1285 | 370.4875 | 21.5151 | 21.9491 | 44.8488 | 88.3869 | 96.1834 | 24.8308 | 54.477 | 96.267 | 725.5132 | 639.8384 | 721.7018 | 734.7709 | 713.707 |  | 725.8706 | 697.7234 | 826.9929 | 596.5121 | 602.985 | 698.1872 |  | 560.6509 |  |  | 463.6877 | 608.247 | 688.5477 | [5 empty] | 21.8253 | 575.6048 | 21.9326 | 22.0467 | 420.4609 | 21.4121 | 21.8447 | 483.6524 | 608.3303 | 623.7367 |  | 985.5482 | 905.2551 | 514.9873 | 671.0468 | 764.8859 | 570.4613 | 637.0189 | 962.3164 | 952.3265 | 603.8551 | 744.5642 | 837.4434 | 1027.3943 | 1010.016 | 499.5544 | 589.2294 | 626.1596 | 538.4825 | 673.66 | 794.3598 | 926.8533 | 1053.434 | 555.7976 | 620.0613 | 610.666 | 730.0307 | 55.8229 | -0.0024808 | 19.5711 | 4.0819 | -28.4788 | 3.0963 | 8941.49 | -0.06 | 1.5293 | 2.6876 | -16.3057 | 1.9256 | 6.8719 | -34.3529 | -34.5557 | 56.8161 | 86.6484 | 33.5891 | 71.803 | 15.0863 | 62.3419 | 30.4993
42838.4318 | 997 | 22.7615 | 22.7703 | 22.7723 | 22.6875 | 22.2974 | 21.6176 | 22.6443 | 21.6871 | 22.2933 | 22.2965 | 22.2615 | 21.9013 | 21.1189 | 22.0921 | 21.4775 | 22.1895 | 23.1541 | 23.0666 | 39.7467 | 47.1297 | 83.5977 | 89.054 | 90.1793 | 25.111 | 50.1514 | 90.5684 | 629.9311 | 661.2491 | 631.4156 | 23.9699 | 54.8442 | 96.0714 | 25.1042 | 52.8 | 93.6251 | 744.667 | 723.5793 |  | 408.7862 | 792.4501 | 805.4389 | 687.2892 |  | 408.0222 | 643.0211 | 589.4948 | 821.0388 | 944.6147 | 964.996 | 938.157 | 45.4026 | 278.3714 | 73.4738 | 513.3149 | 71.1406 | 51.9218 | 49.9236 | 54.7195 | 43.4292 |  |  | 1.1476 | 1.7373 | -60.2379 | 0.64656 | 7.2238 | -197.8591 | -203.3074 | -2.728 | 13.8037 | 39.8546 | 19.0354 | 0.0011385 | 0.00033184 | 0.00040248 | 28.4605 | 22.164 | 22.0884 | 22.1386 | 21.9351 | 21.2115 | 20.0643 | 22.1243 | 22.303 | 22.3437 | 22.2865 | 21.8849 | 21.117 | 22.2075 | 644.9537 | 556.0747 | 486.3125 | 333.8813 | 284.1859 | 747.7352 | 487.5546 | 22.2324 | 22.1995 | 23.0166 | 22.2606 | 34.0982 | 43.3769 | 27.3736 | 80.8795 | 86.9974 | 577.8187 | 543.5466 | 548.7504 | 550.1343 | 97.1393 | 42.481 | 772.5924 | 22.0694 | 22.1303 | 370.9356 | 21.5156 | 21.9519 | 45.0142 | 88.4158 | 96.2457 | 24.8616 | 54.5886 | 96.3722 | 724.2676 | 640.8281 | 721.0764 | 734.1113 | 711.7971 |  | 726.1132 | 698.2807 | 827.956 | 598.9585 | 603.35 | 698.691 |  | 561.5908 |  |  | 462.7159 | 608.6583 | 689.7979 | [5 empty] | 21.8269 | 577.0618 | 21.9261 | 22.0443 | 420.1141 | 21.4145 | 21.8398 | 483.802 | 607.9374 | 623.3758 |  | 985.2093 | 908.0101 | 514.2647 | 671.6534 | 765.3578 | 570.2329 | 637.4234 | 959.9148 | 952.3094 | 604.2543 | 743.7607 | 838.0943 | 1027.8166 | 1005.7843 | 499.5727 | 589.5815 | 625.1247 | 538.5633 | 673.7566 | 793.1397 | 931.7981 | 1049.7111 | 556.1243 | 619.5433 | 610.8232 | 730.0103 | 57.8484 | 0.00063683 | 19.5701 | 4.0858 | -28.4613 | 3.0964 | 8841.87 | -0.06 | 2.2453 | 2.7803 | -16.3716 | 1.6961 | 6.5908 | -34.493 | -34.9647 | 56.9307 | 86.9509 | 33.587 | 73.0074 | 19.1246 | 62.444 | 30.5019
42838.4318 | 998 | 22.7706 | 22.7706 | 22.7758 | 22.6868 | 22.2953 | 21.6193 | 22.6473 | 21.6852 | 22.2944 | 22.2986 | 22.2579 | 21.9038 | 21.1241 | 22.1019 | 21.4756 | 22.2006 | 23.1657 | 23.1139 | 39.8637 | 47.2374 | 83.6528 | 89.0516 | 90.1924 | 25.1322 | 50.248 | 90.6188 | 629.3033 | 660.7385 | 630.4765 | 23.9841 | 54.961 | 96.1628 | 25.139 | 52.8895 | 93.6625 | 744.8217 | 726.6796 |  | 411.7237 | 808.576 | 819.6099 | 693.9261 |  | 410.1925 | 645.912 | 591.527 | 813.7793 | 941.9935 | 973.0106 | 942.2422 | 44.7764 | 279.0832 | 72.6722 | 514.6718 | 71.0707 | 51.9279 | 49.9355 | 54.7485 | 43.5803 |  |  | 0.85908 | 1.3562 | -59.4809 | 0.20892 | 8.4145 | -197.8512 | -203.1852 | -2.9403 | 13.8087 | 40.5893 | 17.7058 | 0.0012534 | 0.0003647 | 0.00037456 | 28.5157 | 22.162 | 22.1 | 22.1399 | 21.9418 | 21.2199 | 20.0601 | 22.1291 | 22.3034 | 22.3443 | 22.2839 | 21.8908 | 21.1207 | 22.1985 | 632.907 | 550.4461 | 493.4416 | 326.0527 | 268.312 | 747.1537 | 487.4397 | 22.2324 | 22.2012 | 23.0363 | 22.2662 | 34.2092 | 43.4825 | 27.4186 | 80.9199 | 87.0254 | 577.5464 | 543.887 | 548.471 | 549.6072 | 79.4144 | 43.9893 | 774.2236 | 22.0805 | 22.1387 | 370.8001 | 21.5202 | 21.957 | 45.1836 | 88.4532 | 96.3142 | 24.8971 | 54.6985 | 96.4799 | 727.0128 | 641.9593 | 721.226 | 733.9942 | 714.6794 |  | 726.5835 | 699.2249 | 829.4298 | 598.3702 | 603.5949 | 699.3997 |  | 562.5643 |  |  | 461.6709 | 609.6882 | 691.7018 | [5 empty] | 21.8276 | 578.1299 | 21.9302 | 22.0421 | 420.4981 | 21.4156 | 21.8443 | 483.5797 | 607.8898 | 623.1365 |  | 983.5251 | 910.4029 | 514.3694 | 672.7532 | 766.8669 | 570.0027 | 638.0074 | 951.3546 | 950.2694 | 605.4474 | 745.087 | 857.8227 | 1030.9328 | 1004.2026 | 499.8116 | 589.7461 | 624.7353 | 538.6129 | 673.7207 | 792.8926 | 954.2134 | 1046.9448 | 556.4119 | 619.3086 | 611.2737 | 729.9509 | 57.6612 | 0.0008966 | 19.5705 | 4.0932 | -28.4388 | 3.0964 | 8691.7 | -0.04 | 1.9417 | 2.4604 | -16.294 | 0.96567 | 7.1362 | -34.6038 | -35.0671 | 56.9703 | 87.4128 | 33.6475 | 74.1411 | 18.3082 | 62.301 | 30.471
42838.4318 | 999 | 22.7637 | 22.7644 | 22.7737 | 22.6949 | 22.2908 | 21.6234 | 22.6409 | 21.6717 | 22.2839 | 22.2969 | 22.2606 | 21.9002 | 21.1195 | 22.0943 | 21.4739 | 22.2051 | 23.1723 | 23.159 | 39.9761 | 47.3563 | 83.6984 | 89.0618 | 90.2121 | 25.1561 | 50.3474 | 90.6729 | 629.9435 | 662.5489 | 632.0213 | 24.0075 | 55.0881 | 96.2674 | 25.1659 | 52.9987 | 93.7121 | 746.4897 | 737.3085 |  | 410.2164 | 811.5438 | 822.3224 | 702.6992 |  | 412.5521 | 649.2736 | 595.7019 | 818.2751 | 949.9676 | 978.5866 | 951.0429 | 45.1011 | 279.859 | 71.2057 | 515.6416 | 71.1231 | 51.9408 | 49.9465 | 54.7782 | 43.6824 |  |  | 0.68035 | 0.88507 | -59.4277 | 0.57756 | 7.9184 | -197.8131 | -203.0873 | -2.6781 | 13.6849 | 40.8574 | 17.4565 | 0.0014243 | 0.00033349 | 0.00039098 | 28.5643 | 22.1652 | 22.1006 | 22.1414 | 21.9461 | 21.2188 | 20.0637 | 22.1377 | 22.3024 | 22.3478 | 22.2876 | 21.8849 | 21.1193 | 22.2011 | 608.0097 | 529.7176 | 481.7696 | 340.0271 | 283.0103 | 746.2375 | 486.9986 | 22.2334 | 22.2082 | 23.0525 | 22.2693 | 34.3106 | 43.5824 | 27.4601 | 80.9668 | 87.0458 | 577.2824 | 542.5756 | 547.4315 | 549.2123 | 98.0423 | 37.7214 | 775.9496 | 22.0813 | 22.1468 | 370.5036 | 21.5192 | 21.9581 | 45.3448 | 88.4803 | 96.3764 | 24.9273 | 54.8022 | 96.5878 | 731.2874 | 643.4472 | 721.9731 | 734.2477 | 722.2387 |  | 727.5631 | 698.9276 | 830.1414 | 596.0757 | 603.6272 | 699.2071 |  | 563.2963 |  |  | 462.7362 | 612.6343 | 696.8355 | [5 empty] | 21.8312 | 578.23 | 21.9345 | 22.0409 | 422.2675 | 21.4208 | 21.8459 | 483.1037 | 608.2936 | 622.9739 |  | 976.0056 | 909.9296 | 514.7468 | 674.2485 | 769.6381 | 569.9381 | 637.6279 | 933.8074 | 943.1008 | 606.3451 | 748.4127 | 890.3544 | 1039.0282 | 1004.5554 | 499.9372 | 589.8199 | 625.0346 | 538.7566 | 674.6726 | 795.3757 | 986.9083 | 1048.604 | 556.2502 | 619.7489 | 612.1923 | 734.465 | 53.4261 | -0.00045856 | 19.57 | 4.0991 | -28.3914 | 3.0964 | 8546.06 | -0.11 | 1.7294 | 1.9912 | -16.3165 | 1.6085 | 6.9381 | -34.6778 | -35.137 | 57.0098 | 87.6574 | 33.7171 | 76.5852 | 19.5121 | 62.5036 | 30.4378
42838.4319 | 1000 | 22.7614 | 22.7734 | 22.7771 | 22.685 | 22.3005 | 21.6182 | 22.6369 | 21.6827 | 22.2895 | 22.299 | 22.2628 | 21.9046 | 21.1135 | 22.1006 | 21.4735 | 22.2176 | 23.1935 | 23.207 | 40.098 | 47.4729 | 83.7408 | 89.0788 | 90.2395 | 25.1897 | 50.4531 | 90.7244 | 632.6547 | 664.8512 | 636.2366 | 24.0328 | 55.2157 | 96.3892 | 25.1986 | 53.1016 | 93.7908 | 747.9917 | 724.1365 |  | 408.1698 | 806.179 | 817.535 | 703.053 |  | 416.0731 | 654.4208 | 598.7656 | 824.5992 | 955.8274 | 986.1649 | 957.3997 | 44.843 | 280.6721 | 70.031 | 516.6404 | 71.1327 | 51.9235 | 49.9506 | 54.7952 | 43.7855 |  |  | 0.51278 | 0.73853 | -59.1412 | 0.27397 | 6.9038 | -197.8447 | -203.1694 | -1.9435 | 13.6491 | 41.3412 | 17.6011 | 0.0016165 | 0.00052241 | 0.00037949 | 28.6115 | 22.1734 | 22.1029 | 22.142 | 21.9432 | 21.2127 | 20.0646 | 22.1397 | 22.3053 | 22.3456 | 22.2886 | 21.8848 | 21.1167 | 22.2069 | 618.1627 | 543.3738 | 459.1579 | 324.7812 | 273.785 | 747.4027 | 486.6382 | 22.2325 | 22.2147 | 23.0623 | 22.2734 | 34.414 | 43.6849 | 27.5014 | 81.0102 | 87.0648 | 577.1463 | 541.7244 | 546.8451 | 550.0064 | 117.2784 | 53.4413 | 774.7026 | 22.0788 | 22.1406 | 370.191 | 21.5166 | 21.9553 | 45.5052 | 88.5119 | 96.431 | 24.9552 | 54.9139 | 96.697 | 730.2084 | 644.3821 | 722.5536 | 734.2807 | 722.71 |  | 728.3035 | 697.1378 | 829.7813 | 597.2902 | 603.6928 | 697.9479 |  | 564.179 |  |  | 465.1517 | 615.8981 | 699.4842 | [5 empty] | 21.8249 | 578.559 | 21.9299 | 22.0346 | 423.258 | 21.4137 | 21.8412 | 482.9995 | 608.2187 | 623.6333 |  | 954.6878 | 905.5578 | 514.8547 | 674.7739 | 769.2584 | 570.0306 | 638.0112 | 916.5314 | 926.9818 | 606.4655 | 748.3818 | 925.0018 | 1052.9519 | 1003.4589 | 500.0372 | 590.0404 | 625.7414 | 538.8374 | 676.2585 | 797.7391 | 1012.4186 | 1050.7555 | 556.077 | 620.8811 | 612.7263 | 739.7811 | 49.7096 | -0.00034621 | 19.5691 | 4.119 | -28.4611 | 3.0964 | 8421.67 | -0.12 | 1.5049 | 1.824 | -16.3225 | 1.111 | 6.498 | -34.7853 | -35.2503 | 57.1858 | 87.5874 | 33.6952 | 75.867 | 21.9486 | 62.8974 | 30.3929
42838.4319 | 1001 | 22.7673 | 22.7698 | 22.7679 | 22.6869 | 22.2937 | 21.6198 | 22.6314 | 21.6752 | 22.2869 | 22.2881 | 22.2519 | 21.8991 | 21.1223 | 22.0943 | 21.4741 | 22.2269 | 23.2104 | 23.2596 | 40.2215 | 47.5881 | 83.7811 | 89.0852 | 90.2673 | 25.2212 | 50.5499 | 90.7705 | 635.0188 | 665.7083 | 638.7665 | 24.0536 | 55.3214 | 96.5038 | 25.2197 | 53.1974 | 93.8488 | 748.2974 | 708.3478 |  | 408.9361 | 799.52 | 812.156 | 695.748 |  | 419.0135 | 657.7721 | 600.8863 | 820.4862 | 957.6469 | 990.5515 | 962.2548 | 44.1444 | 281.501 | 68.8413 | 517.6296 | 71.1946 | 51.9008 | 49.9579 | 54.8198 | 43.906 |  |  | 0.70137 | 0.45137 | -70.8918 | 0.15766 | 8.1707 | -197.825 | -203.241 | -1.8265 | 13.892 | 42.1718 | 16.8914 | 0.0016264 | 0.00042548 | 0.0003877 | 28.6675 | 22.1774 | 22.1043 | 22.144 | 21.9405 | 21.2097 | 20.0677 | 22.1392 | 22.3084 | 22.3469 | 22.2869 | 21.8858 | 21.1284 | 22.2081 | 696.212 | 591.4055 | 514.2351 | 343.5107 | 268.985 | 751.1493 | 487.2177 | 22.2302 | 22.212 | 23.0759 | 22.274 | 34.5045 | 43.7781 | 27.5398 | 81.0353 | 87.0851 | 577.0506 | 540.3089 | 545.6744 | 550.2953 | 109.5652 | 59.9473 | 769.9461 | 22.0769 | 22.138 | 369.6408 | 21.5193 | 21.9505 | 45.6608 | 88.5532 | 96.487 | 24.9813 | 55.0272 | 96.811 | 723.8047 | 643.5528 | 723.4636 | 734.7481 | 711.4112 |  | 728.197 | 694.8052 | 828.4658 | 596.8303 | 603.7543 | 696.1603 |  | 565.0499 |  |  | 465.6891 | 616.0811 | 694.7919 | [5 empty] | 21.8264 | 578.1648 | 21.936 | 22.0367 | 422.9413 | 21.4244 | 21.8374 | 483.2891 | 608.9472 | 624.9819 |  | 931.0414 | 897.1336 | 514.8334 | 674.246 | 765.0926 | 570.3947 | 640.0619 | 899.9542 | 911.2983 | 606.128 | 743.9118 | 955.608 | 1061.6418 | 999.772 | 500.3649 | 590.8976 | 627.072 | 538.5957 | 676.4921 | 793.8532 | 1028.3813 | 1048.7208 | 556.3943 | 623.3306 | 612.4932 | 738.2775 | 46.3554 | -0.00014261 | 19.5679 | 4.1319 | -28.7271 | 3.0963 | 8349.66 | -0.07 | 1.7625 | 1.4285 | -17.9028 | 0.84428 | 7.0814 | -34.8441 | -35.3179 | 57.4724 | 87.2161 | 33.7191 | 68.5194 | 15.951 | 63.1827 | 30.3689
42838.4319 | 1002 | 22.768 | 22.7692 | 22.777 | 22.6903 | 22.2989 | 21.6199 | 22.6393 | 21.6786 | 22.2926 | 22.295 | 22.2543 | 21.8983 | 21.12 | 22.0949 | 21.4724 | 22.234 | 23.2205 | 23.304 | 40.3384 | 47.7034 | 83.825 | 89.0833 | 90.284 | 25.2373 | 50.6431 | 90.8213 | 634.9148 | 665.5358 | 637.596 | 24.0846 | 55.4539 | 96.618 | 25.2599 | 53.2976 | 93.9005 | 748.1651 | 701.3568 |  | 409.0745 | 794.2407 | 807.5803 | 690.8474 |  | 421.837 | 659.985 | 602.7225 | 816.7095 | 960.194 | 999.9659 | 967.7524 | 43.7872 | 282.3054 | 68.7421 | 518.5711 | 71.1824 | 51.8709 | 49.9674 | 54.8406 | 44.0264 |  |  | 0.70926 | 0.70042 | -102.8716 | 0.64984 | 6.6166 | -197.8322 | -203.1267 | -2.3824 | 13.6857 | 41.7585 | 16.6845 | 0.0015804 | 0.00044355 | 0.00037784 | 28.7221 | 22.1836 | 22.1022 | 22.1424 | 21.9385 | 21.2034 | 20.0655 | 22.1302 | 22.3029 | 22.3441 | 22.2854 | 21.8771 | 21.1271 | 22.2039 | 765.7725 | 640.911 | 570.6339 | 358.5718 | 268.2131 | 755.5875 | 488.3459 | 22.233 | 22.2209 | 23.0902 | 22.2883 | 34.6055 | 43.8807 | 27.5969 | 81.0598 | 87.1055 | 576.986 | 538.2236 | 548.5662 | 550.6331 | 95.8394 | 45.3705 | 763.1985 | 22.0804 | 22.1378 | 368.9651 | 21.5193 | 21.9463 | 45.8176 | 88.5959 | 96.5438 | 25.0169 | 55.1357 | 96.9293 | 716.2087 | 641.7821 | 725.7327 | 736.0548 | 699.8081 |  | 727.4591 | 692.7414 | 826.5361 | 593.5765 | 603.6104 | 694.2593 |  | 565.6533 |  |  | 464.7651 | 613.0101 | 687.4412 | [5 empty] | 21.8303 | 576.174 | 21.938 | 22.0458 | 423.2786 | 21.4352 | 21.8468 | 483.6437 | 610.1799 | 625.6013 |  | 910.5167 | 888.1044 | 514.5811 | 672.7984 | 759.9489 | 570.8823 | 640.6214 | 884.0015 | 896.9296 | 605.3972 | 738.6318 | 979.36 | 1062.0167 | 994.7129 | 500.8385 | 592.3183 | 627.8023 | 538.3828 | 675.6509 | 788.8051 | 1038.3964 | 1042.7264 | 557.2218 | 625.6841 | 612.1203 | 735.9579 | 46.977 | -0.00085882 | 19.5686 | 4.1324 | -28.5065 | 3.0964 | 8252.18 | -0.05 | 1.7712 | 1.7816 | -21.5917 | 1.7161 | 6.3962 | -34.9743 | -35.4392 | 57.6064 | 86.6363 | 33.7835 | 62.3724 | 9.9226 | 63.2832 | 30.3487
42838.4319 | 1003 | 22.7688 | 22.7726 | 22.7734 | 22.6909 | 22.3023 | 21.6217 | 22.6385 | 21.6873 | 22.292 | 22.2936 | 22.2624 | 21.9041 | 21.1181 | 22.1008 | 21.4723 | 22.247 | 23.2445 | 23.3567 | 40.46 | 47.8202 | 83.8704 | 89.0995 | 90.3038 | 25.2643 | 50.747 | 90.865 | 633.9584 | 665.2894 | 635.8453 | 24.1048 | 55.5773 | 96.7102 | 25.2948 | 53.4025 | 93.9648 | 747.6357 | 697.1339 |  | 409.5781 | 787.1259 | 800.5444 | 685.4839 |  | 425.479 | 661.9731 | 605.1057 | 810.3431 | 958.432 | 1000.3505 | 971.7648 | 43.5269 | 283.086 | 67.1615 | 519.4793 | 71.2166 | 51.8548 | 49.9634 | 54.8636 | 44.1144 |  |  | 0.19014 | 0.32192 | -112.2237 | 0.66036 | 6.5424 | -197.8552 | -203.1122 | -2.2556 | 13.8062 | 41.1864 | 16.1428 | 0.0017381 | 0.00047477 | 0.00037127 | 28.78 | 22.1896 | 22.1081 | 22.1415 | 21.9326 | 21.2125 | 20.0685 | 22.1328 | 22.3048 | 22.3398 | 22.2843 | 21.8889 | 21.121 | 22.2038 | 778.5171 | 607.641 | 552.2983 | 356.2351 | 262.9764 | 758.106 | 489.1223 | 22.2348 | 22.2321 | 23.1101 | 22.2816 | 34.7237 | 43.9948 | 27.6378 | 81.1103 | 87.1265 | 577.0617 | 539.5521 | 548.9167 | 553.3383 | 95.6042 | 59.3858 | 756.1079 | 22.0923 | 22.1427 | 368.8816 | 21.5225 | 21.9595 | 45.983 | 88.6253 | 96.6091 | 25.0528 | 55.247 | 97.0469 | 709.1412 | 639.8582 | 729.5713 | 738.1837 | 691.7595 |  | 726.3953 | 691.4638 | 824.598 | 591.0207 | 603.4715 | 692.7386 |  | 566.0921 |  |  | 464.061 | 607.935 | 680.0901 | [5 empty] | 21.8299 | 574.5775 | 21.9413 | 22.0419 | 423.9438 | 21.4332 | 21.8464 | 484.0565 | 610.4401 | 625.0115 |  | 891.1973 | 879.2002 | 513.9318 | 670.8138 | 755.2007 | 571.3951 | 639.5903 | 870.7651 | 884.7363 | 604.3891 | 733.8084 | 999.5978 | 1058.4722 | 988.0931 | 501.2079 | 593.4491 | 627.6077 | 537.9541 | 674.5395 | 784.2995 | 1044.8994 | 1037.1209 | 558.005 | 626.4418 | 611.9138 | 734.878 | 46.4099 | 0.00046831 | 19.568 | 4.1494 | -28.4131 | 3.0963 | 8223.76 | -0.1 | 0.91618 | 1.2091 | -22.5758 | 1.7318 | 6.3611 | -34.9816 | -35.4433 | 57.559 | 86.0349 | 33.8294 | 61.8603 | 12.1241 | 63.2897 | 30.2862
42838.4319 | 1004 | 22.7684 | 22.7631 | 22.7739 | 22.6861 | 22.2944 | 21.6183 | 22.632 | 21.6809 | 22.2966 | 22.2917 | 22.2641 | 21.9041 | 21.1231 | 22.0988 | 21.4693 | 22.2425 | 23.2546 | 23.3969 | 40.5714 | 47.9116 | 83.8896 | 89.1108 | 90.3096 | 25.2862 | 50.8427 | 90.8926 | 633.2213 | 664.6989 | 634.9048 | 24.1234 | 55.6878 | 96.7928 | 25.3231 | 53.4957 | 94.0253 | 747.0372 | 693.2487 |  | 405.5568 | 778.1505 | 791.9698 | 683.7165 |  | 427.0677 | 664.3237 | 605.903 | 806.6452 | 955.569 | 991.7175 | 974.5772 | 43.9016 | 283.7524 | 65.246 | 520.175 | 71.2799 | 51.8298 | 49.9698 | 54.9035 | 44.1843 |  |  | 0.45824 | 0.65902 | -71.8163 | 0.39817 | 7.1653 | -197.842 | -203.1359 | -1.4467 | 13.6441 | 42.3833 | 15.8302 | 0.00092982 | 0.00021028 | 0.00035977 | 28.8341 | 22.179 | 22.0968 | 22.138 | 21.9321 | 21.2085 | 20.0633 | 22.1316 | 22.3044 | 22.3345 | 22.2861 | 21.891 | 21.1262 | 22.196 | 770.5276 | 607.5159 | 565.8368 | 365.6571 | 280.0363 | 759.8872 | 490.5514 | 22.2267 | 22.2198 | 23.1251 | 22.2786 | 34.8187 | 44.0812 | 27.6833 | 81.1523 | 87.136 | 577.221 | 541.6923 | 549.2054 | 554.8364 | 89.7978 | 47.1615 | 750.7409 | 22.0934 | 22.139 | 369.4768 | 21.5228 | 21.9599 | 46.1385 | 88.6347 | 96.6741 | 25.0853 | 55.3509 | 97.1827 | 702.7365 | 637.6342 | 734.3823 | 741.5352 | 684.6236 |  | 725.0667 | 691.0034 | 822.7697 | 589.5976 | 603.4388 | 691.583 |  | 566.686 |  |  | 463.8935 | 602.2023 | 673.4745 | [5 empty] | 21.8304 | 573.1808 | 21.9445 | 22.0426 | 424.2458 | 21.4292 | 21.8426 | 484.2991 | 610.1114 | 624.1669 |  | 875.0366 | 871.7142 | 513.1504 | 668.1436 | 750.5757 | 571.5717 | 638.6895 | 860.4186 | 874.9174 | 602.7617 | 729.2912 | 1013.743 | 1053.9614 | 982.1885 | 501.864 | 593.7341 | 626.9971 | 537.2945 | 672.6615 | 779.452 | 1050.0291 | 1030.8393 | 558.5149 | 626.0909 | 611.1757 | 732.6107 | 45.3081 | -0.00026899 | 19.5673 | 4.1548 | -28.4146 | 3.0964 | 8247.51 | -0.12 | 1.4216 | 1.7322 | -18.0825 | 1.3464 | 6.6345 | -34.8617 | -35.3251 | 57.4201 | 85.4497 | 33.863 | 63.3901 | 10.9225 | 63.1779 | 30.2713
42838.4319 | 1005 | 22.7582 | 22.7647 | 22.775 | 22.6879 | 22.289 | 21.6186 | 22.6341 | 21.6719 | 22.2888 | 22.2856 | 22.2545 | 21.9019 | 21.1229 | 22.0896 | 21.4784 | 22.2709 | 23.2704 | 23.4475 | 40.6932 | 48.0368 | 83.9298 | 89.1227 | 90.332 | 25.3219 | 50.958 | 90.9366 | 632.0458 | 663.4836 | 632.9682 | 24.1468 | 55.8036 | 96.8841 | 25.3579 | 53.5897 | 94.1052 | 746.1618 | 689.927 |  | 389.1085 | 769.6823 | 783.6989 | 679.1164 |  | 428.131 | 667.5558 | 608.6793 | 815.5927 | 958.2231 | 990.8049 | 982.1535 | 44.6303 | 284.547 | 64.2776 | 520.9867 | 71.2787 | 51.8154 | 49.9641 | 54.9404 | 44.2744 |  |  | 0.52855 | 0.74576 | -60.0875 | 0.49937 | 8.406 | -197.825 | -203.2029 | -2.3916 | 13.4697 | 41.2078 | 15.666 | 0.00078197 | 0.00012157 | 0.0003762 | 28.8792 | 22.1841 | 22.0936 | 22.1347 | 21.9388 | 21.2094 | 20.0636 | 22.1277 | 22.3061 | 22.3297 | 22.2801 | 21.8811 | 21.1191 | 22.1952 | 757.4623 | 595.9507 | 538.4311 | 364.1748 | 276.3032 | 761.4585 | 490.9308 | 22.2254 | 22.2227 | 23.1384 | 22.289 | 34.9106 | 44.1792 | 27.7199 | 81.209 | 87.1586 | 577.1158 | 540.4199 | 548.3852 | 552.0302 | 111.358 | 49.3818 | 747.6535 | 22.0971 | 22.1401 | 370.3066 | 21.5176 | 21.9526 | 46.2937 | 88.6312 | 96.7355 | 25.1174 | 55.4547 | 97.3047 | 698.5692 | 635.194 | 740.3764 | 746.447 | 678.9805 |  | 723.4548 | 690.8012 | 820.7823 | 586.9072 | 603.2993 | 690.3023 |  | 568.2106 |  |  | 462.8456 | 597.2615 | 668.1417 | [5 empty] | 21.8287 | 571.393 | 21.9525 | 22.0389 | 425.6275 | 21.4322 | 21.8437 | 484.4016 | 610.2662 | 623.375 |  | 863.2083 | 865.1204 | 512.0665 | 665.432 | 745.7796 | 571.8324 | 638.1736 | 849.2433 | 866.2595 | 600.8992 | 725.8042 | 1022.0158 | 1053.5798 | 975.7691 | 501.6346 | 593.6855 | 626.3863 | 537.0436 | 670.3268 | 774.271 | 1050.6624 | 1026.7145 | 559.273 | 625.8084 | 610.2796 | 729.1784 | 45.7039 | -9.175e-06 | 19.5676 | 4.1562 | -28.4657 | 3.0964 | 8265.68 | -0.12 | 1.5251 | 1.8458 | -16.5686 | 1.5104 | 7.1833 | -34.8476 | -35.3181 | 57.1693 | 84.8085 | 33.9126 | 65.4102 | 14.0481 | 63.0708 | 30.3316
42838.4319 | 1006 | 22.7584 | 22.7723 | 22.7672 | 22.6827 | 22.2964 | 21.6178 | 22.6372 | 21.6727 | 22.2814 | 22.2802 | 22.253 | 21.8968 | 21.1164 | 22.099 | 21.4701 | 22.2641 | 23.2912 | 23.5002 | 40.8021 | 48.143 | 83.9702 | 89.1217 | 90.3388 | 25.3427 | 51.0529 | 90.979 | 630.2736 | 661.583 | 630.605 | 24.1905 | 55.9114 | 96.9917 | 25.3918 | 53.6852 | 94.1957 | 744.5649 | 688.9255 |  | 387.6925 | 761.9567 | 775.9716 | 672.8001 |  | 431.4792 | 671.18 | 612.078 | 824.6016 | 963.0111 | 999.4435 | 983.2977 | 45.1295 | 285.3291 | 62.769 | 521.6664 | 71.3485 | 51.8027 | 49.9668 | 54.9717 | 44.3953 |  |  | 0.69415 | -0.17157 | -60.2458 | 0.14387 | 7.8803 | -197.867 | -203.2121 | -1.9816 | 13.6248 | 40.9375 | 15.6042 | 0.00088711 | 0.00020042 | 0.00040084 | 28.9372 | 22.1877 | 22.094 | 22.1425 | 21.9373 | 21.2114 | 20.0597 | 22.1352 | 22.31 | 22.3369 | 22.2821 | 21.8798 | 21.1226 | 22.2058 | 786.0122 | 614.8648 | 548.4258 | 338.5329 | 270.1797 | 764.8916 | 491.6513 | 22.2292 | 22.2369 | 23.1567 | 22.2935 | 35.0208 | 44.278 | 27.7715 | 81.243 | 87.1859 | 576.7022 | 538.2424 | 545.9792 | 547.7396 | 132.7616 | 62.4476 | 744.6131 | 22.1 | 22.1488 | 370.5671 | 21.5237 | 21.9585 | 46.4593 | 88.6456 | 96.8068 | 25.1513 | 55.5623 | 97.4219 | 696.9366 | 632.6919 | 746.9639 | 751.973 | 677.5413 |  | 722.2432 | 690.4468 | 819.0998 | 584.6037 | 603.0246 | 689.439 |  | 568.8993 |  |  | 460.7389 | 593.0125 | 664.662 | [5 empty] | 21.8359 | 569.3098 | 21.9541 | 22.0409 | 425.3025 | 21.4412 | 21.8527 | 484.7256 | 610.4301 | 622.0746 |  | 853.4667 | 859.4471 | 510.7322 | 663.8385 | 741.7147 | 572.1815 | 637.2916 | 848.9891 | 858.4775 | 599.9124 | 723.3161 | 1028.1384 | 1053.824 | 970.4444 | 501.7283 | 593.7341 | 625.4151 | 536.4632 | 668.1296 | 769.1639 | 1054.9021 | 1024.3344 | 559.8603 | 625.6693 | 609.3812 | 726.0506 | 45.0543 | -0.00099923 | 19.5686 | 4.1581 | -28.4787 | 3.0963 | 8322.3 | -0.1 | 1.7455 | -0.88706 | -16.6223 | 0.81228 | 6.9788 | -34.9702 | -35.4394 | 56.9041 | 84.2732 | 33.927 | 63.486 | 13.0906 | 62.8192 | 30.3817
42838.4319 | 1007 | 22.7586 | 22.7705 | 22.7749 | 22.6888 | 22.3 | 21.6228 | 22.6391 | 21.6756 | 22.2851 | 22.2975 | 22.2599 | 21.8965 | 21.1177 | 22.0925 | 21.474 | 22.2821 | 23.3042 | 23.5583 | 40.9332 | 48.2701 | 84.013 | 89.1362 | 90.3642 | 25.3766 | 51.1471 | 91.014 | 628.2521 | 659.2279 | 628.2587 | 24.2062 | 56.023 | 97.0702 | 25.427 | 53.7892 | 94.2526 | 742.6967 | 687.8305 |  | 363.1543 | 752.2368 | 766.3092 | 664.8491 |  | 433.257 | 672.8988 | 612.76 | 827.0417 | 960.364 | 1004.2803 | 984.4173 | 45.6563 | 285.8569 | 62.5283 | 522.1801 | 71.3132 | 51.789 | 49.9547 | 54.9989 | 44.5121 |  |  | 0.59623 | 0.48029 | -60.7807 | 0.26149 | 8.1937 | -197.8223 | -203.2134 | -2.7195 | 13.2518 | 40.451 | 15.2068 | 0.00072283 | 0.00011171 | 0.0003762 | 28.983 | 22.1825 | 22.0907 | 22.135 | 21.9321 | 21.2049 | 20.0567 | 22.1236 | 22.3009 | 22.3397 | 22.2799 | 21.8773 | 21.1214 | 22.2015 | 812.103 | 646.2853 | 582.0615 | 334.2933 | 268.1453 | 768.8317 | 492.8503 | 22.2256 | 22.2339 | 23.164 | 22.2934 | 35.1199 | 44.3871 | 27.8136 | 81.264 | 87.2155 | 576.1392 | 535.4737 | 539.9278 | 544.62 | 103.0345 | 52.9093 | 741.8061 | 22.0975 | 22.1459 | 370.5803 | 21.5285 | 21.9561 | 46.6199 | 88.6471 | 96.8799 | 25.1846 | 55.6711 | 97.5463 | 696.5871 | 630.0929 | 750.0997 | 754.6357 | 677.4269 |  | 721.254 | 690.3278 | 817.6602 | 583.3182 | 602.7385 | 688.8229 |  | 568.8047 |  |  | 458.3951 | 589.527 | 663.1873 | [5 empty] | 21.8232 | 566.7868 | 21.9583 | 22.0363 | 423.3589 | 21.4344 | 21.8401 | 485.2653 | 610.2406 | 620.7547 |  | 848.6546 | 854.5516 | 509.7902 | 663.4047 | 738.0452 | 572.2393 | 635.9003 | 851.943 | 853.7986 | 599.763 | 721.8901 | 1035.6523 | 1055.0158 | 964.7328 | 501.6197 | 593.8025 | 624.0769 | 535.5664 | 666.0585 | 764.5078 | 1063.0723 | 1018.6428 | 559.8054 | 625.2576 | 607.9968 | 723.6925 | 46.7739 | 0.00044021 | 19.5685 | 4.1649 | -28.4385 | 3.0964 | 8314.94 | -0.14 | 1.6156 | 1.4855 | -16.7112 | 1.0961 | 7.1298 | -35.0327 | -35.5068 | 56.6589 | 83.8119 | 33.9112 | 62.0301 | 9.6085 | 62.5428 | 30.3744
42838.4319 | 1008 | 22.7578 | 22.7566 | 22.7621 | 22.6767 | 22.2868 | 21.6138 | 22.6339 | 21.6693 | 22.2852 | 22.2884 | 22.252 | 21.8945 | 21.1094 | 22.0886 | 21.4809 | 22.2899 | 23.3304 | 23.6115 | 41.0493 | 48.3835 | 84.051 | 89.1521 | 90.4013 | 25.4052 | 51.254 | 91.0578 | 626.3606 | 656.7253 | 626.2525 | 24.2292 | 56.125 | 97.1483 | 25.4525 | 53.892 | 94.3403 | 740.7452 | 687.6904 |  | 373.9927 | 743.5071 | 757.3979 | 663.277 |  | 434.8683 | 675.2223 | 614.0815 | 826.0673 | 954.0525 | 1007.572 | 988.9677 | 46.2986 | 286.4923 | 62.8437 | 522.674 | 71.2694 | 51.7484 | 49.9475 | 55.007 | 44.6093 |  |  | 0.55615 | 0.28578 | -60.761 | 0.3364 | 6.8788 | -197.8348 | -203.1365 | -2.7195 | 12.6479 | 38.8719 | 14.7488 | 0.00065547 | 0.00016428 | 0.00039427 | 29.0394 | 22.1863 | 22.1017 | 22.1409 | 21.9349 | 21.2052 | 20.0652 | 22.1357 | 22.3004 | 22.3413 | 22.2811 | 21.8808 | 21.1242 | 22.2039 | 790.4739 | 616.4193 | 579.1332 | 336.3378 | 278.0823 | 770.6821 | 493.7202 | 22.2196 | 22.245 | 23.1813 | 22.2933 | 35.2097 | 44.4833 | 27.8552 | 81.2863 | 87.2196 | 575.6351 | 532.8727 | 538.6985 | 543.1203 | 85.2609 | 46.3037 | 739.4777 | 22.0998 | 22.1454 | 370.7389 | 21.5274 | 21.9537 | 46.7733 | 88.6481 | 96.9511 | 25.2188 | 55.7716 | 97.66 | 697.767 | 627.7766 | 751.9038 | 755.8677 | 677.1206 |  | 720.251 | 690.7258 | 816.6435 | 579.6782 | 602.2733 | 688.8113 |  | 568.5458 |  |  | 456.3244 | 587.019 | 661.9108 | [5 empty] | 21.8266 | 564.3466 | 21.9542 | 22.0284 | 421.3411 | 21.4233 | 21.8324 | 485.1513 | 609.5715 | 619.4688 |  | 845.6851 | 850.1957 | 509.4548 | 663.3668 | 735.0411 | 571.9325 | 635.2085 | 852.4587 | 850.4736 | 599.5577 | 722.0376 | 1043.5701 | 1052.0694 | 958.4448 | 501.1443 | 593.5428 | 622.6404 | 534.675 | 664.0128 | 759.0924 | 1067.5183 | 1008.1507 | 559.2013 | 624.8231 | 606.1712 | 720.2797 | 49.8656 | 0.0044356 | 19.5692 | 4.1916 | -28.5104 | 3.0963 | 8338.15 | -0.16 | 1.5586 | 1.1473 | -16.729 | 1.2448 | 6.5411 | -35.0789 | -35.5458 | 56.4162 | 83.4737 | 33.9285 | 65.115 | 10.1193 | 62.0696 | 30.3321
42838.432 | 1009 | 22.7553 | 22.7625 | 22.7675 | 22.6843 | 22.2904 | 21.6194 | 22.63 | 21.669 | 22.2849 | 22.2954 | 22.2576 | 21.9025 | 21.1254 | 22.0948 | 21.474 | 22.3031 | 23.3443 | 23.6592 | 41.1647 | 48.496 | 84.0706 | 89.1535 | 90.4352 | 25.4294 | 51.3487 | 91.1054 | 624.5167 | 653.9357 | 624.5641 | 24.2553 | 56.2347 | 97.2284 | 25.4753 | 53.9931 | 94.4193 | 739.1517 | 688.0656 |  | 391.0987 | 734.9609 | 748.4831 | 663.0897 |  | 436.474 | 676.2446 | 615.8023 | 825.3776 | 952.7188 | 1002.453 | 991.3498 | 46.8486 | 286.9853 | 64.2525 | 523.1841 | 71.3361 | 51.6968 | 49.9377 | 55.0154 | 44.7392 |  |  | 0.54564 | 0.48817 | -52.2008 | 0.49213 | 8.0373 | -197.8243 | -203.3205 | -2.6387 | 13.0031 | 40.1802 | 14.3107 | 0.00074418 | 0.00015607 | 0.00041891 | 29.0917 | 22.1899 | 22.1014 | 22.1402 | 21.9392 | 21.2097 | 20.0633 | 22.1383 | 22.3036 | 22.3421 | 22.2833 | 21.8872 | 21.1265 | 22.2 | 765.7955 | 576.4132 | 521.4662 | 342.0329 | 285.3194 | 770.9291 | 493.5581 | 22.2288 | 22.2437 | 23.2005 | 22.3036 | 35.3227 | 44.5868 | 27.901 | 81.31 | 87.2463 | 575.3249 | 531.6247 | 538.4344 | 544.2105 | 82.5197 | 33.3662 | 738.4513 | 22.0993 | 22.1426 | 370.2944 | 21.519 | 21.9527 | 46.9275 | 88.6511 | 97.0206 | 25.2464 | 55.877 | 97.7759 | 700.5921 | 625.7453 | 757.1727 | 759.0346 | 681.6558 |  | 719.808 | 691.1658 | 816.1332 | 577.3713 | 601.762 | 689.0826 |  | 568.0905 |  |  | 455.9197 | 586.8393 | 663.4792 | [5 empty] | 21.8352 | 562.0876 | 21.9618 | 22.0382 | 419.0687 | 21.4355 | 21.8423 | 484.6415 | 609.3676 | 618.6712 |  | 841.7295 | 847.0063 | 509.0893 | 663.6141 | 732.6118 | 571.1827 | 634.9386 | 849.695 | 845.9078 | 599.5186 | 720.7989 | 1049.5889 | 1040.9751 | 952.3082 | 500.7937 | 593.4152 | 620.9058 | 533.7077 | 661.9585 | 754.3538 | 1066.8974 | 995.9253 | 558.9326 | 624.2349 | 604.4786 | 717.334 | 49.7697 | 0.014982 | 19.5687 | 4.2254 | -28.413 | 3.0963 | 8303.42 | -0.16 | 1.5424 | 1.5003 | -15.5142 | 1.5064 | 7.0564 | -35.0078 | -35.4908 | 56.1794 | 83.2977 | 33.9007 | 67.9482 | 16.4922 | 61.6548 | 30.2502
42838.432 | 1010 | 22.762 | 22.7669 | 22.7686 | 22.6856 | 22.2989 | 21.6195 | 22.6311 | 21.6735 | 22.2905 | 22.2985 | 22.2658 | 21.9017 | 21.1224 | 22.099 | 21.4735 | 22.306 | 23.3528 | 23.7114 | 41.2772 | 48.5972 | 84.0992 | 89.142 | 90.4517 | 25.4532 | 51.4406 | 91.1458 | 622.9723 | 650.4721 | 622.9752 | 24.271 | 56.3351 | 97.3276 | 25.5114 | 54.0879 | 94.4961 | 737.3328 | 686.6034 |  | 390.5857 | 726.3843 | 739.5433 | 660.0379 |  | 438.4432 | 677.0863 | 616.3455 | 830.1111 | 953.2343 | 1003.4816 | 991.6411 | 47.6177 | 287.5176 | 65.595 | 523.7994 | 71.3063 | 51.67 | 49.9371 | 55.0069 | 44.8669 |  |  | 0.50029 | 0.85222 | -54.2221 | 0.62619 | 7.1785 | -197.8703 | -200.3773 | -2.6886 | 12.4113 | 38.8643 | 13.7136 | 0.00073433 | 2.629e-05 | 0.0003992 | 29.1475 | 22.1986 | 22.1018 | 22.1415 | 21.9365 | 21.2113 | 20.0669 | 22.1344 | 22.3057 | 22.3443 | 22.2904 | 21.8845 | 21.1292 | 22.2029 | 775.4406 | 572.8915 | 470.7435 | 326.4215 | 273.1402 | 771.403 | 492.1483 | 22.2242 | 22.2367 | 23.2072 | 22.3004 | 35.4145 | 44.6818 | 27.949 | 81.338 | 87.2637 | 575.0187 | 530.0739 | 539.0265 | 544.8225 | 83.6105 | 39.9036 | 738.9758 | 22.1007 | 22.1454 | 370.0157 | 21.521 | 21.9562 | 47.0857 | 88.6578 | 97.0876 | 25.2807 | 55.9773 | 97.8854 | 703.2005 | 624.1091 | 766.1898 | 764.3476 | 686.1059 |  | 719.7435 | 691.5718 | 815.8547 | 573.8361 | 601.0956 | 689.4876 |  | 568.006 |  |  | 455.8574 | 589.3883 | 667.1003 | [5 empty] | 21.8331 | 559.5629 | 21.9634 | 22.0373 | 416.7761 | 21.446 | 21.8514 | 483.7781 | 608.9904 | 618.0747 |  | 836.3149 | 844.4397 | 509.3565 | 663.5829 | 730.0743 | 570.5466 | 634.468 | 842.2377 | 843.2548 | 600.7525 | 719.203 | 1055.9075 | 1033.4685 | 945.8106 | 500.7444 | 593.4551 | 619.1313 | 532.342 | 660.2866 | 750.4679 | 1067.3151 | 987.0333 | 558.787 | 623.4361 | 603.2991 | 716.1681 | 47.711 | 0.00058768 | 19.5702 | 4.2615 | -28.5382 | 3.0963 | 8272.11 | -0.07 | 1.4756 | 1.9832 | -15.8187 | 1.6999 | 6.6714 | -35.026 | -35.2472 | 56.0397 | 83.197 | 33.8792 | 67.0516 | 21.8277 | 61.2622 | 30.1823
42838.432 | 1011 | 22.7684 | 22.769 | 22.7774 | 22.6885 | 22.3006 | 21.6137 | 22.6342 | 21.6829 | 22.2931 | 22.3045 | 22.2657 | 21.9038 | 21.1221 | 22.103 | 21.4699 | 22.3067 | 23.3691 | 23.7629 | 41.3909 | 48.7071 | 84.1189 | 89.1391 | 90.4708 | 25.4809 | 51.5298 | 91.1841 | 621.5518 | 647.5376 | 621.1876 | 24.3018 | 56.4369 | 97.4243 | 25.5472 | 54.1801 | 94.5844 | 735.2042 | 685.5107 |  | 373.33 | 717.8252 | 730.7701 | 658.2207 |  | 441.1581 | 679.4645 | 617.6803 | 825.5049 | 949.1792 | 1006.1984 | 993.7299 | 47.8511 | 288.1373 | 66.3693 | 524.2999 | 71.3181 | 51.6637 | 49.9306 | 54.9937 | 45.0497 |  |  | 0.62712 | 0.90873 | -57.0936 | 0.30683 | 7.9401 | -197.8466 | -203.266 | -3.1144 | 12.717 | 39.2415 | 13.5708 | 0.00071133 | 0.000115 | 0.00039098 | 29.2143 | 22.2038 | 22.1021 | 22.1423 | 21.9468 | 21.214 | 20.0627 | 22.1352 | 22.3072 | 22.3435 | 22.284 | 21.8939 | 21.1253 | 22.2067 | 759.4387 | 556.9415 | 469.8161 | 319.1152 | 268.8874 | 771.2535 | 491.1628 | 22.2298 | 22.2534 | 23.2301 | 22.3086 | 35.5167 | 44.7763 | 27.9957 | 81.3769 | 87.2947 | 574.7092 | 528.813 | 541.4398 | 545.081 | 86.8654 | 45.4915 | 739.8829 | 22.0977 | 22.1372 | 369.9891 | 21.5186 | 21.951 | 47.2394 | 88.6688 | 97.1542 | 25.3126 | 56.0801 | 97.9987 | 704.8025 | 623.1569 | 773.0144 | 768.8455 | 687.0237 |  | 719.703 | 691.4166 | 815.5698 | 570.2489 | 600.2819 | 689.6887 |  | 568.2544 |  |  | 456.3159 | 592.8706 | 669.5136 | [5 empty] | 21.8387 | 557.0162 | 21.9656 | 22.0542 | 416.4679 | 21.4521 | 21.8522 | 482.4759 | 608.3073 | 616.9616 |  | 830.9589 | 843.346 | 510.1827 | 664.2706 | 727.5861 | 569.7706 | 632.581 | 838.2644 | 838.9303 | 602.9241 | 718.549 | 1059.617 | 1028.1557 | 940.8495 | 500.6306 | 593.2203 | 617.9529 | 531.3922 | 659.393 | 746.8349 | 1064.0252 | 980.391 | 558.4877 | 623.4942 | 602.0475 | 715.2721 | 48.4825 | 0.0017603 | 19.5709 | 4.2716 | -28.4962 | 3.0963 | 8220.31 | -0.02 | 1.6504 | 2.0504 | -16.2525 | 1.1914 | 7.0238 | -35.0611 | -35.5381 | 56.0041 | 83.11 | 33.8331 | 68.7743 | 21.7213 | 60.757 | 30.1237
42838.432 | 1012 | 22.7543 | 22.7647 | 22.7673 | 22.6836 | 22.2939 | 21.6073 | 22.6354 | 21.674 | 22.2824 | 22.2886 | 22.26 | 21.8966 | 21.1178 | 22.0937 | 21.4727 | 22.3221 | 23.3828 | 23.8114 | 41.5068 | 48.8211 | 84.1466 | 89.1352 | 90.4924 | 25.5021 | 51.6275 | 91.2321 | 620.1396 | 645.2618 | 619.2206 | 24.3286 | 56.5376 | 97.4494 | 25.5724 | 54.2585 | 94.6735 | 733.5192 | 684.4371 |  | 364.6386 | 710.5616 | 723.4642 | 657.133 |  | 441.9619 | 680.6972 | 618.8661 | 823.9741 | 945.039 | 1009.7527 | 991.391 | 47.8734 | 288.6186 | 66.8853 | 524.8368 | 71.3413 | 51.6779 | 49.9251 | 55.0006 | 45.1829 |  |  | 0.7868 | 0.72736 | -60.5264 | 0.066326 | 7.4439 | -197.825 | -203.2075 | -2.4652 | 11.8921 | 36.9914 | 13.3918 | 0.00068504 | 0.00017414 | 0.00040248 | 29.2716 | 22.2079 | 22.0934 | 22.1472 | 21.9405 | 21.2035 | 20.0728 | 22.1272 | 22.3082 | 22.3438 | 22.2839 | 21.8852 | 21.1198 | 22.2054 | 749.1917 | 545.0292 | 472.4581 | 329.4494 | 276.2216 | 770.9604 | 490.3735 | 22.2221 | 22.2471 | 23.2435 | 22.3113 | 35.6268 | 44.88 | 28.0425 | 81.4073 | 87.3213 | 574.5016 | 531.2266 | 543.5145 | 548.5756 | 73.091 | 37.556 | 739.5228 | 22.099 | 22.1319 | 370.1987 | 21.5144 | 21.9479 | 47.3926 | 88.6843 | 97.2202 | 25.3443 | 56.1736 | 98.1046 | 704.8207 | 622.5915 | 775.7617 | 770.8104 | 687.7578 |  | 719.6863 | 690.861 | 815.3299 | 567.9758 | 599.4628 | 689.7208 |  | 568.6416 |  |  | 456.2729 | 594.8588 | 670.9075 | [5 empty] | 21.8291 | 555.0549 | 21.966 | 22.0482 | 415.4517 | 21.4478 | 21.8454 | 481.0233 | 607.0838 | 615.1458 |  | 823.8088 | 841.6635 | 510.9152 | 665.423 | 725.0749 | 568.8019 | 630.0101 | 833.959 | 834.8686 | 604.9521 | 717.6811 | 1060.9964 | 1027.5168 | 937.1908 | 500.2763 | 593.0145 | 616.9587 | 530.2311 | 659.0242 | 743.645 | 1065.477 | 978.7587 | 558.2476 | 623.5483 | 600.6189 | 714.5762 | 47.7973 | -0.00088689 | 19.5691 | 4.2737 | -28.4501 | 3.0964 | 8151.98 | -0.07 | 1.8466 | 1.8356 | -16.7448 | 0.5543 | 6.8103 | -35.1079 | -35.5823 | 55.9795 | 83.0486 | 33.7499 | 69.8046 | 21.2602 | 60.3496 | 29.9922
42838.432 | 1013 | 22.7526 | 22.7705 | 22.771 | 22.6803 | 22.2938 | 21.6133 | 22.6343 | 21.6681 | 22.2798 | 22.294 | 22.257 | 21.8959 | 21.1128 | 22.0908 | 21.474 | 22.3419 | 23.4025 | 23.8682 | 41.6267 | 48.9338 | 84.1882 | 89.138 | 90.5272 | 25.5289 | 51.7219 | 91.2943 | 618.6671 | 643.2235 | 617.1717 | 24.3534 | 56.6346 | 97.4947 | 25.593 | 54.3595 | 94.7614 | 731.5968 | 684.7005 |  | 366.3849 | 704.4876 | 717.049 | 652.3757 |  | 443.7617 | 682.3341 | 619.6152 | 823.1775 | 938.6568 | 1010.3693 | 987.2274 | 47.9998 | 288.9568 | 66.594 | 525.2372 | 71.3838 | 51.6987 | 49.915 | 54.9948 | 45.3304 |  |  | 0.62252 | 0.87061 | -64.7195 | 0.56245 | 6.9859 | -197.825 | -203.2147 | -3.0474 | 12.1914 | 37.4607 | 13.2941 | 0.00059633 | 1.479e-05 | 0.00037291 | 29.3194 | 22.2058 | 22.0972 | 22.1422 | 21.9351 | 21.2064 | 20.0686 | 22.1349 | 22.3088 | 22.3388 | 22.2893 | 21.8905 | 21.1263 | 22.206 | 724.751 | 549.0269 | 480.4525 | 326.1351 | 274.4045 | 769.2035 | 489.2169 | 22.2316 | 22.2552 | 23.2578 | 22.3108 | 35.7224 | 44.9834 | 28.0987 | 81.4595 | 87.3556 | 574.5315 | 533.1126 | 543.5878 | 550.7724 | 72.1247 | 46.1796 | 738.6493 | 22.1028 | 22.1345 | 370.5019 | 21.5264 | 21.9526 | 47.5517 | 88.698 | 97.2974 | 25.3872 | 56.2755 | 98.2099 | 704.0792 | 622.3655 | 775.7431 | 771.0185 | 687.4774 |  | 719.5321 | 690.2056 | 814.6863 | 568.3494 | 598.8481 | 688.9687 |  | 568.9374 |  |  | 455.8599 | 595.9438 | 670.9588 | [5 empty] | 21.8303 | 554.0607 | 21.9686 | 22.0408 | 414.897 | 21.4502 | 21.8427 | 479.6219 | 605.7434 | 612.7158 |  | 817.521 | 840.2619 | 511.2155 | 665.74 | 722.874 | 567.6833 | 627.4557 | 825.9833 | 830.4998 | 606.8217 | 716.492 | 1060.6831 | 1029.7048 | 934.0351 | 499.7203 | 592.9189 | 616.227 | 528.8321 | 657.333 | 740.4208 | 1066.2771 | 980.6858 | 557.389 | 623.614 | 598.8738 | 712.8905 | 47.4126 | 0.00075619 | 19.5694 | 4.2729 | -28.3963 | 3.0964 | 8068.39 | -0.09 | 1.6407 | 2.01 | -17.3299 | 1.6155 | 6.599 | -35.1163 | -35.5915 | 55.9488 | 82.8608 | 33.6299 | 71.8726 | 20.1269 | 59.9848 | 29.9361
42838.432 | 1014 | 22.758 | 22.7618 | 22.7665 | 22.6831 | 22.2878 | 21.6164 | 22.631 | 21.6753 | 22.2779 | 22.2856 | 22.259 | 21.9005 | 21.1138 | 22.1051 | 21.4757 | 22.3526 | 23.4291 | 23.9263 | 41.744 | 49.0459 | 84.2237 | 89.1476 | 90.5659 | 25.5592 | 51.8161 | 91.3609 | 617.02 | 640.8583 | 615.0986 | 24.3758 | 56.7361 | 97.5748 | 25.6344 | 54.4522 | 94.8529 | 729.7321 | 686.777 |  | 370.3534 | 698.8072 | 711.1299 | 653.7451 |  | 444.8469 | 683.7702 | 618.7718 | 816.7484 | 936.2185 | 1005.5168 | 985.3603 | 48.8541 | 289.2531 | 68.0181 | 525.6208 | 71.4058 | 51.7114 | 49.8982 | 54.9916 | 45.4523 |  |  | 0.53249 | 0.80162 | -69.3567 | 0.47834 | 7.4945 | -197.821 | -203.1694 | -2.5138 | 12.214 | 37.7654 | 13.0331 | 0.00072283 | 0.00012321 | 0.00040741 | 29.3693 | 22.2128 | 22.1005 | 22.1459 | 21.9317 | 21.2038 | 20.0657 | 22.1381 | 22.3026 | 22.3374 | 22.2878 | 21.892 | 21.1222 | 22.2122 | 694.2013 | 552.3646 | 501.3869 | 330.4211 | 270.3787 | 767.2748 | 488.4966 | 22.2317 | 22.2688 | 23.2788 | 22.3177 | 35.8277 | 45.0835 | 28.154 | 81.5064 | 87.3861 | 574.4894 | 534.6627 | 542.823 | 550.5516 | 74.5788 | 37.9151 | 737.3846 | 22.1098 | 22.1345 | 370.7526 | 21.525 | 21.9559 | 47.7093 | 88.7079 | 97.3779 | 25.4311 | 56.3917 | 98.3255 | 703.2717 | 622.4206 | 773.1001 | 768.954 | 685.9256 |  | 719.1725 | 689.592 | 813.7364 | 569.3592 | 598.3069 | 688.13 |  | 569.3807 |  |  | 455.6011 | 595.6564 | 669.2729 | [5 empty] | 21.8313 | 554.2321 | 21.9749 | 22.0385 | 414.132 | 21.4565 | 21.8463 | 478.63 | 604.3006 | 610.5339 |  | 811.6046 | 839.2898 | 511.1624 | 665.6634 | 721.4521 | 566.643 | 625.6269 | 813.8778 | 826.4114 | 607.315 | 715.5291 | 1062.2806 | 1029.9813 | 932.8253 | 499.2274 | 592.9042 | 615.4298 | 527.5422 | 655.1842 | 736.9735 | 1067.5046 | 981.8945 | 556.6528 | 623.6986 | 597.5347 | 711.2532 | 48.1191 | 0.00033488 | 19.5696 | 4.2714 | -28.4966 | 3.0963 | 7933.48 | -0.08 | 1.5156 | 1.9301 | -17.9535 | 1.491 | 6.8221 | -35.0495 | -35.5202 | 55.9022 | 82.5745 | 33.5055 | 74.5587 | 17.6486 | 59.4672 | 29.9353
42838.432 | 1015 | 22.7523 | 22.7588 | 22.771 | 22.6795 | 22.2874 | 21.6231 | 22.6279 | 21.679 | 22.2805 | 22.283 | 22.2597 | 21.8958 | 21.1147 | 22.0945 | 21.4697 | 22.3544 | 23.4379 | 23.9783 | 41.8543 | 49.1429 | 84.2484 | 89.1418 | 90.5978 | 25.5827 | 51.9097 | 91.4197 | 615.6183 | 638.6744 | 614.1167 | 24.4051 | 56.8478 | 97.6445 | 25.6656 | 54.5558 | 94.9109 | 728.6379 | 687.3386 |  | 371.9046 | 697.0553 | 709.18 | 655.694 |  | 446.3143 | 685.971 | 617.6059 | 810.8269 | 937.0545 | 1003.6982 | 984.4682 | 49.6529 | 289.5585 | 70.4177 | 526.1071 | 71.4336 | 51.7444 | 49.8766 | 55.0081 | 45.5431 |  |  | 0.33339 | 0.65114 | -72.756 | 0.53616 | 7.3795 | -197.8164 | -202.942 | -3.2051 | 12.3286 | 37.791 | 12.9977 | 0.00069162 | 5.421e-05 | 0.00041563 | 29.4306 | 22.2127 | 22.1028 | 22.1463 | 21.9417 | 21.2054 | 20.067 | 22.1358 | 22.304 | 22.3366 | 22.2898 | 21.8873 | 21.125 | 22.208 | 688.5847 | 552.6697 | 466.3604 | 314.6385 | 259.2699 | 765.324 | 487.3292 | 22.2256 | 22.2684 | 23.2943 | 22.329 | 35.9223 | 45.18 | 28.1998 | 81.5389 | 87.4077 | 574.3427 | 535.8397 | 541.1299 | 549.4642 | 71.7016 | 31.8985 | 735.9426 | 22.1199 | 22.1394 | 370.4275 | 21.5172 | 21.9527 | 47.8607 | 88.7245 | 97.4482 | 25.4635 | 56.4926 | 98.4246 | 703.5985 | 622.4599 | 770.7048 | 766.8742 | 684.7509 |  | 718.6874 | 688.7093 | 812.3477 | 569.6416 | 597.6852 | 687.6331 |  | 569.7258 |  |  | 455.0733 | 593.6922 | 667.9797 | [5 empty] | 21.8292 | 554.4713 | 21.9752 | 22.0467 | 413.4034 | 21.4589 | 21.8494 | 477.738 | 602.9298 | 608.9495 |  | 803.7773 | 838.5058 | 510.694 | 665.5885 | 720.4389 | 565.3858 | 624.7717 | 802.5021 | 821.7951 | 606.8579 | 714.0705 | 1063.7114 | 1031.9607 | 932.5191 | 499.0194 | 592.8466 | 614.2946 | 526.4971 | 653.7258 | 734.1935 | 1073.5332 | 981.513 | 556.2529 | 623.3265 | 596.6256 | 710.1255 | 47.0749 | 0.00077023 | 19.5695 | 4.2683 | -28.4121 | 3.0964 | 7752.26 | -0.08 | 1.1986 | 1.7416 | -18.4093 | 1.5803 | 6.7647 | -35.0242 | -35.475 | 55.8139 | 82.1569 | 33.3872 | 74.4691 | 21.294 | 59.1328 | 29.9411
42838.432 | 1016 | 22.7556 | 22.7624 | 22.7653 | 22.6822 | 22.2878 | 21.6169 | 22.6277 | 21.6706 | 22.2868 | 22.2888 | 22.2509 | 21.8925 | 21.114 | 22.0921 | 21.4758 | 22.3669 | 23.453 | 24.0441 | 41.9703 | 49.2526 | 84.2824 | 89.1523 | 90.6378 | 25.6126 | 52.0129 | 91.492 | 614.6583 | 637.6146 | 613.9138 | 24.4372 | 56.9576 | 97.6943 | 25.7015 | 54.6573 | 94.973 | 727.2493 | 685.0086 |  | 380.4502 | 695.928 | 707.7576 | 653.8742 |  | 448.3873 | 688.5987 | 617.8966 | 808.4683 | 940.7042 | 1002.8865 | 984.4199 | 50.1482 | 289.811 | 71.4411 | 526.7817 | 71.4332 | 51.7814 | 49.8609 | 55.0294 | 45.6302 |  |  | 0.85185 | 0.91924 | -72.4702 | -0.023042 | 7.323 | -197.8039 | -203.1983 | -2.9048 | 12.0486 | 37.0378 | 12.5455 | 0.00041398 | -2.628e-05 | 0.00036306 | 29.4859 | 22.2187 | 22.0986 | 22.14 | 21.9436 | 21.2122 | 20.0678 | 22.1308 | 22.3127 | 22.346 | 22.2895 | 21.8819 | 21.1255 | 22.2092 | 678.7616 | 533.5302 | 432.4008 | 305.1229 | 247.9552 | 763.6556 | 485.883 | 22.2346 | 22.2724 | 23.3156 | 22.3248 | 36.0226 | 45.2747 | 28.2512 | 81.5755 | 87.4215 | 574.1235 | 535.2273 | 540.7219 | 547.9704 | 77.9382 | 43.9937 | 734.0143 | 22.1184 | 22.1399 | 369.71 | 21.5179 | 21.9533 | 48.0175 | 88.7452 | 97.5166 | 25.4996 | 56.5942 | 98.5238 | 702.6909 | 621.9581 | 769.9552 | 766.2222 | 685.0469 |  | 718.3099 | 687.9672 | 811.1655 | 568.6152 | 597.0873 | 687.5365 |  | 570.0091 |  |  | 454.394 | 592.2844 | 667.474 | [5 empty] | 21.828 | 554.2716 | 21.9737 | 22.0382 | 412.4331 | 21.4534 | 21.8414 | 476.9493 | 601.8362 | 607.7561 |  | 794.8598 | 837.2983 | 509.3705 | 664.3028 | 718.6727 | 563.8488 | 624.7946 | 793.5038 | 817.7798 | 605.2729 | 711.4066 | 1063.0777 | 1036.9 | 931.8924 | 498.9252 | 592.765 | 613.0248 | 525.3627 | 652.2835 | 731.957 | 1076.7822 | 984.1088 | 555.6682 | 622.6885 | 595.7767 | 732.3513 | 44.6701 | 0.00092471 | 19.5692 | 4.2648 | -28.3955 | 3.0964 | 7578.29 | -0.09 | 1.9157 | 2.0721 | -18.3983 | -0.32806 | 6.7367 | -35.0119 | -35.4861 | 55.7117 | 81.8023 | 33.3096 | 74.9524 | 24.7627 | 58.8288 | 29.9463
42838.432 | 1017 | 22.7596 | 22.7675 | 22.769 | 22.6831 | 22.283 | 21.6138 | 22.633 | 21.6745 | 22.2898 | 22.2925 | 22.2586 | 21.9027 | 21.1127 | 22.0967 | 21.4755 | 22.3732 | 23.4679 | 24.1057 | 42.0853 | 49.367 | 84.3043 | 89.1596 | 90.6599 | 25.6412 | 52.1088 | 91.5559 | 614.086 | 636.6177 | 613.7429 | 24.4608 | 57.0561 | 97.7416 | 25.7286 | 54.7428 | 95.0319 | 725.9487 | 683.2005 |  | 377.4298 | 693.6362 | 705.1348 | 654.6782 |  | 450.3176 | 689.2816 | 621.0088 | 810.6538 | 944.8116 | 1006.5761 | 988.7427 | 49.7677 | 290.005 | 72.3332 | 527.3336 | 71.4372 | 51.8132 | 49.8498 | 55.0454 | 45.753 |  |  | 0.75591 | 0.61368 | -72.4281 | 0.41788 | 7.0845 | -197.8696 | -203.172 | -2.9232 | 11.8004 | 36.3549 | 12.1634 | 0.0003187 | -5.421e-05 | 0.00037456 | 29.5409 | 22.2236 | 22.097 | 22.1448 | 21.9454 | 21.216 | 20.0736 | 22.1419 | 22.3061 | 22.344 | 22.2863 | 21.8891 | 21.1286 | 22.2172 | 686.1421 | 559.4518 | 451.2559 | 303.1643 | 244.2753 | 762.358 | 484.8177 | 22.2345 | 22.2786 | 23.335 | 22.3328 | 36.1382 | 45.3854 | 28.3045 | 81.6101 | 87.4572 | 573.8018 | 533.2851 | 538.9862 | 545.7841 | 77.0533 | 37.8424 | 731.4209 | 22.1217 | 22.1415 | 369.519 | 21.519 | 21.9521 | 48.1825 | 88.7575 | 97.5858 | 25.5399 | 56.7007 | 98.6342 | 701.2402 | 621.1813 | 770.6626 | 766.9568 | 683.0495 |  | 717.7431 | 687.4462 | 810.0835 | 567.3165 | 596.4503 | 686.5492 |  | 570.3756 |  |  | 453.3826 | 592.009 | 666.0653 | [5 empty] | 21.8358 | 553.1592 | 21.9826 | 22.0418 | 410.874 | 21.4526 | 21.8459 | 476.2341 | 600.9632 | 606.9631 |  | 788.1399 | 836.159 | 507.7558 | 662.4159 | 716.4154 | 562.6588 | 624.5989 | 783.5511 | 816.2907 | 603.3679 | 709.0598 | 1061.359 | 1039.1696 | 931.8586 | 498.7884 | 593.1311 | 611.8139 | 523.8983 | 650.6674 | 729.8441 | 1074.7685 | 987.4302 | 555.1056 | 621.8274 | 594.6957 | 775.3992 | 46.1205 | -0.00054985 | 19.5682 | 4.2581 | -28.4956 | 3.0964 | 7409.56 | -0.06 | 1.8044 | 1.6936 | -18.3995 | 1.3976 | 6.6356 | -35.0683 | -35.5351 | 55.6263 | 81.4743 | 33.2329 | 73.6608 | 22.4439 | 58.4756 | 29.9537
42838.4321 | 1018 | 22.7625 | 22.7723 | 22.7692 | 22.6836 | 22.2937 | 21.6157 | 22.6393 | 21.6854 | 22.2954 | 22.2954 | 22.2613 | 21.9059 | 21.1194 | 22.1008 | 21.4742 | 22.3792 | 23.4835 | 24.1595 | 42.193 | 49.4707 | 84.3242 | 89.1688 | 90.6791 | 25.6616 | 52.1944 | 91.605 | 613.4618 | 635.4781 | 612.9123 | 24.4908 | 57.153 | 97.7905 | 25.7595 | 54.8377 | 95.0885 | 725.3342 | 684.9223 |  | 369.2765 | 690.4619 | 701.8254 | 658.2341 |  | 452.5608 | 689.291 | 625.7576 | 811.1332 | 945.1519 | 1007.8976 | 989.3378 | 49.3367 | 290.158 | 72.3755 | 527.7617 | 71.4274 | 51.817 | 49.8319 | 55.0847 | 45.8626 |  |  | 0.73817 | 0.47372 | -85.1584 | -0.042758 | 6.7165 | -197.8085 | -203.2397 | -2.8253 | 11.6183 | 36.435 | 11.9862 | 0.00016592 | -0.00010185 | 0.00037949 | 29.6012 | 22.2173 | 22.0986 | 22.1459 | 21.9407 | 21.2069 | 20.069 | 22.1472 | 22.3075 | 22.3472 | 22.2949 | 21.888 | 21.1184 | 22.2071 | 672.4902 | 546.3825 | 442.1245 | 299.0301 | 237.3684 | 760.5068 | 483.7016 | 22.2324 | 22.2862 | 23.3504 | 22.3418 | 36.2408 | 45.48 | 28.3604 | 81.6393 | 87.4785 | 573.4374 | 530.4577 | 537.7043 | 544.2989 | 69.4973 | 41.405 | 729.8448 | 22.1266 | 22.1409 | 368.329 | 21.5231 | 21.957 | 48.3362 | 88.7812 | 97.6527 | 25.5751 | 56.8047 | 98.7343 | 701.4048 | 620.296 | 774.0044 | 770.0194 | 681.3507 |  | 717.0566 | 687.6254 | 809.5718 | 565.2461 | 595.6994 | 686.5274 |  | 570.5424 |  |  | 452.4225 | 591.5681 | 664.4651 | [5 empty] | 21.8344 | 551.2601 | 21.9885 | 22.0492 | 409.4384 | 21.4657 | 21.8553 | 475.6633 | 600.1567 | 606.1971 |  | 783.1442 | 836.0249 | 506.5399 | 660.7107 | 714.3972 | 561.7152 | 623.6325 | 772.1032 | 814.9397 | 602.2236 | 707.4057 | 1056.6252 | 1039.4835 | 931.1966 | 498.4601 | 593.2513 | 610.9534 | 522.5214 | 649.6032 | 728.2243 | 1074.9397 | 988.2389 | 554.5634 | 621.5121 | 593.7125 | 786.803 | 45.4531 | 0.001023 | 19.5676 | 4.2384 | -28.4838 | 3.0964 | 7229.99 | -0.01 | 1.7823 | 1.488 | -19.9511 | -0.44706 | 6.4643 | -35.081 | -35.5594 | 55.5031 | 81.3077 | 33.1577 | 74.5071 | 23.2245 | 58.2209 | 29.9347
42838.4321 | 1019 | 22.7647 | 22.772 | 22.7717 | 22.6874 | 22.2963 | 21.6165 | 22.6351 | 21.6795 | 22.2948 | 22.3033 | 22.2579 | 21.9093 | 21.1186 | 22.0914 | 21.482 | 22.4085 | 23.5187 | 24.2253 | 42.3216 | 49.5918 | 84.373 | 89.1706 | 90.7139 | 25.7075 | 52.304 | 91.6649 | 612.7757 | 635.0551 | 612.3145 | 24.522 | 57.2546 | 97.844 | 25.804 | 54.9381 | 95.1435 | 724.9182 | 685.9333 |  | 366.7743 | 688.7761 | 700.5587 | 657.2057 |  | 454.3857 | 690.0584 | 628.3791 | 810.1936 | 943.366 | 1009.8766 | 993.0505 | 47.8031 | 290.2526 | 72.3177 | 528.07 | 71.3561 | 51.8055 | 49.8085 | 55.136 | 45.9423 |  |  | 0.70269 | 0.9613 | -98.7081 | 0.27003 | 7.8172 | -183.1516 | -203.2542 | -2.893 | 11.4235 | 37.5029 | 11.8775 | 0.00037291 | 3.121e-05 | 0.0003992 | 29.6577 | 22.2259 | 22.0991 | 22.1467 | 21.9402 | 21.2142 | 20.0667 | 22.1389 | 22.3065 | 22.3455 | 22.2905 | 21.8892 | 21.1255 | 22.2098 | 662.3111 | 544.4897 | 465.3581 | 302.5795 | 234.0829 | 758.3805 | 482.3998 | 22.2274 | 22.2891 | 23.3656 | 22.3428 | 36.3332 | 45.5703 | 28.4085 | 81.6653 | 87.4956 | 573.0125 | 529.3613 | 535.537 | 543.2382 | 76.7786 | 40.0778 | 730.3529 | 22.1331 | 22.1343 | 366.5644 | 21.5258 | 21.9536 | 48.4879 | 88.8133 | 97.7258 | 25.6195 | 56.9124 | 98.8294 | 702.0285 | 619.357 | 777.9459 | 773.881 | 681.4711 |  | 716.619 | 687.83 | 809.4778 | 564.2554 | 595.0976 | 686.9421 |  | 570.5595 |  |  | 451.5352 | 590.8231 | 664.2834 | [5 empty] | 21.8363 | 549.6157 | 21.994 | 22.0418 | 408.945 | 21.4684 | 21.8525 | 474.8872 | 599.4274 | 605.2605 |  | 778.4676 | 836.2941 | 505.3702 | 659.6517 | 713.0141 | 560.8987 | 622.3967 | 758.9976 | 813.5655 | 601.3104 | 706.1355 | 1055.6765 | 1038.714 | 930.4917 | 497.8777 | 592.8847 | 610.0412 | 521.2721 | 649.3511 | 727.4823 | 1077.0688 | 988.4093 | 553.9219 | 621.4332 | 593.1417 | 787.1439 | 46.3138 | 0.00015934 | 19.5682 | 4.2229 | -28.4748 | 3.0964 | 7119.07 | -0.03 | 1.7383 | 2.1206 | -21.4884 | 1.1239 | 6.9793 | -33.7824 | -35.5881 | 55.3913 | 81.2723 | 33.0791 | 74.8709 | 20.3707 | 58.144 | 29.8939
42838.4321 | 1020 | 22.757 | 22.7637 | 22.7689 | 22.6867 | 22.2955 | 21.6192 | 22.6306 | 21.6752 | 22.2913 | 22.2947 | 22.2611 | 21.9042 | 21.1209 | 22.0988 | 21.4765 | 22.4035 | 23.5273 | 24.2711 | 42.4263 | 49.6935 | 84.3903 | 89.1857 | 90.7365 | 25.7292 | 52.3996 | 91.7209 | 612.3222 | 634.9362 | 612.2672 | 24.549 | 57.3586 | 97.8808 | 25.8349 | 55.0204 | 95.1824 | 723.9099 | 686.5738 |  | 374.9393 | 690.6632 | 703.0838 | 653.535 |  | 455.788 | 692.5525 | 630.1148 | 809.0132 | 950.2451 | 1018.9701 | 1003.7314 | 46.0747 | 290.313 | 73.1543 | 528.4782 | 71.435 | 51.7957 | 49.7958 | 55.1615 | 46.0092 |  |  | 0.90771 | 0.48883 | -98.7075 | 0.43891 | 7.3684 | -197.8217 | -200.9319 | -2.4915 | 10.8882 | 35.925 | 11.6619 | 0.00055198 | 5.421e-05 | 0.00040084 | 29.7117 | 22.2268 | 22.0962 | 22.1417 | 21.9388 | 21.2092 | 20.0661 | 22.136 | 22.3111 | 22.3427 | 22.2827 | 21.8873 | 21.123 | 22.2144 | 676.8517 | 566.1376 | 476.436 | 305.83 | 235.7084 | 757.0632 | 481.0458 | 22.2334 | 22.2965 | 23.3831 | 22.3443 | 36.4322 | 45.6621 | 28.4608 | 81.6914 | 87.5161 | 572.7167 | 529.2959 | 534.4479 | 543.9175 | 81.5941 | 36.962 | 730.2739 | 22.1236 | 22.1342 | 364.6182 | 21.509 | 21.9446 | 48.63 | 88.84 | 97.7748 | 25.646 | 57.0114 | 98.916 | 703.4397 | 618.4146 | 778.1014 | 774.6258 | 681.4192 |  | 716.3015 | 687.3234 | 809.2251 | 563.4171 | 594.5432 | 686.878 |  | 570.3021 |  |  | 451.8828 | 589.5044 | 664.7892 | [5 empty] | 21.8296 | 548.455 | 21.9969 | 22.0502 | 408.66 | 21.4698 | 21.8467 | 473.9465 | 598.6893 | 604.1066 |  | 773.9649 | 837.4052 | 503.9783 | 660.1629 | 711.7375 | 560.1079 | 621.2759 | 746.455 | 812.6402 | 601.4321 | 706.1369 | 1056.2285 | 1038.3732 | 930.3494 | 497.3318 | 592.3237 | 608.8001 | 519.8118 | 648.8726 | 726.5734 | 1069.4493 | 988.3691 | 553.5571 | 621.2369 | 592.8105 | 799.0613 | 47.7685 | 0.00070002 | 19.5688 | 4.215 | -28.4494 | 3.0964 | 6988.93 | 0.02 | 1.9757 | 1.5141 | -21.5161 | 1.4348 | 6.7999 | -35.2335 | -35.5094 | 55.3141 | 81.2067 | 33.0048 | 72.7816 | 18.8573 | 57.991 | 29.8262
42838.4321 | 1021 | 22.7547 | 22.7712 | 22.7709 | 22.6794 | 22.2968 | 21.6169 | 22.6411 | 21.6801 | 22.2875 | 22.2939 | 22.2563 | 21.9049 | 21.1246 | 22.0955 | 21.4681 | 22.4076 | 23.5463 | 24.3318 | 42.539 | 49.7977 | 84.4287 | 89.1989 | 90.7549 | 25.748 | 52.4871 | 91.7728 | 612.1238 | 634.1543 | 612.162 | 24.5699 | 57.4691 | 97.933 | 25.8581 | 55.1195 | 95.2299 | 723.2377 | 686.4906 |  | 368.1184 | 690.9919 | 703.6245 | 656.256 |  | 457.5338 | 694.486 | 632.2219 | 813.1174 | 955.7729 | 1027.3761 | 1014.5042 | 44.3096 | 290.3864 | 74.0737 | 529.1131 | 71.4197 | 51.7809 | 49.7885 | 55.1846 | 46.0798 |  |  | 0.42144 | 0.62748 | -106.93 | 1.1223 | 8.2115 | -197.7941 | -203.1569 | -2.9929 | 11.4369 | 37.1041 | 11.8999 | 0.00044848 | 1.15e-05 | 0.00043698 | 29.7589 | 22.2163 | 22.0919 | 22.1292 | 21.9268 | 21.1961 | 20.0587 | 22.1252 | 22.3028 | 22.3401 | 22.2725 | 21.8813 | 21.1226 | 22.2046 | 683.8082 | 545.7178 | 452.434 | 301.8372 | 238.4838 | 755.3993 | 479.4149 | 22.2292 | 22.2974 | 23.3995 | 22.3424 | 36.5251 | 45.7664 | 28.5132 | 81.745 | 87.54 | 572.3301 | 529.0751 | 534.0561 | 542.0508 | 67.9285 | 19.6937 | 727.271 | 22.1291 | 22.1393 | 363.4562 | 21.5247 | 21.9555 | 48.7914 | 88.8789 | 97.8431 | 25.6954 | 57.1168 | 99.0275 | 702.1474 | 617.5228 | 773.5126 | 770.7368 | 681.9438 |  | 716.0924 | 686.4219 | 808.6611 | 563.424 | 594.0033 | 686.5893 |  | 570.1719 |  |  | 453.7881 | 589.7454 | 665.4199 | [5 empty] | 21.8292 | 547.9314 | 21.9908 | 22.0339 | 408.5827 | 21.4665 | 21.8426 | 472.8885 | 597.8399 | 603.2444 |  | 768.5248 | 837.277 | 503.3197 | 661.9527 | 711.1366 | 559.293 | 620.4113 | 734.2241 | 811.0297 | 601.9343 | 707.4652 | 1053.5666 | 1030.7837 | 930.3035 | 496.7118 | 592.2539 | 607.7933 | 518.5006 | 648.2895 | 725.0933 | 1058.0358 | 985.9719 | 553.2806 | 620.7507 | 591.7065 | 800.3759 | 44.6584 | -0.0010133 | 19.5692 | 4.2187 | -28.4477 | 3.0964 | 6878.91 | -0.03 | 1.3461 | 1.7172 | -22.4168 | 2.2966 | 7.2017 | -35.3454 | -35.8214 | 55.2478 | 81.054 | 32.9096 | 71.4122 | 21.1848 | 57.7458 | 29.8143
42838.4321 | 1022 | 22.7596 | 22.7695 | 22.7743 | 22.6831 | 22.2896 | 21.6136 | 22.6353 | 21.6717 | 22.2883 | 22.2904 | 22.2543 | 21.8997 | 21.1163 | 22.0988 | 21.4678 | 22.425 | 23.5594 | 24.3957 | 42.6574 | 49.9101 | 84.4636 | 89.2181 | 90.7754 | 25.7871 | 52.5946 | 91.8323 | 611.6675 | 633.8801 | 611.526 | 24.6074 | 57.5796 | 97.9859 | 25.9034 | 55.2203 | 95.2887 | 723.485 | 686.004 |  | 373.2899 | 685.3532 | 697.5111 | 662.1516 |  | 459.3938 | 695.8837 | 631.2516 | 818.0644 | 963.4529 | 1032.7067 | 1022.55 | 44.0957 | 290.5834 | 74.118 | 529.6275 | 71.404 | 51.7658 | 49.7792 | 55.1988 | 46.1408 |  |  | 0.79797 | 0.35609 | -87.7093 | 0.80887 | 8.3797 | -197.8388 | -203.3015 | -2.6623 | 11.3313 | 36.444 | 12.3058 | 0.00046162 | 2.3e-05 | 0.00036634 | 29.8148 | 22.2253 | 22.0942 | 22.1283 | 21.9308 | 21.2014 | 20.0591 | 22.1281 | 22.2944 | 22.3391 | 22.2814 | 21.885 | 21.1181 | 22.202 | 673.7322 | 497.8624 | 391.7108 | 292.974 | 235.573 | 752.6204 | 476.5608 | 22.2201 | 22.3063 | 23.4164 | 22.3539 | 36.6319 | 45.8684 | 28.5747 | 81.7941 | 87.5798 | 571.6615 | 528.3804 | 532.0337 | 538.2607 | 62.0656 | 22.3683 | 724.2388 | 22.1407 | 22.1446 | 362.8559 | 21.5375 | 21.9602 | 48.95 | 88.9143 | 97.9044 | 25.7346 | 57.2302 | 99.1417 | 698.9948 | 616.4816 | 765.9716 | 764.4832 | 681.6986 |  | 715.9304 | 685.3017 | 807.6469 | 562.3284 | 593.3737 | 686.0836 |  | 570.8281 |  |  | 453.9167 | 591.8407 | 666.2741 | [5 empty] | 21.8278 | 546.8055 | 21.989 | 22.0365 | 408.2542 | 21.4642 | 21.8388 | 471.9416 | 596.8185 | 602.3826 |  | 763.3925 | 836.0381 | 503.2526 | 663.6105 | 710.5596 | 558.3495 | 619.5396 | 722.1048 | 810.514 | 602.2466 | 709.3871 | 1050.8384 | 1021.7162 | 928.9823 | 496.4578 | 592.0187 | 607.3611 | 517.0672 | 647.7047 | 722.9659 | 1055.1552 | 982.647 | 552.6595 | 620.8288 | 589.9292 | 799.6985 | 48.7626 | -0.0002058 | 19.5693 | 4.2558 | -28.4841 | 3.0964 | 6776.14 | -0.14 | 1.8516 | 1.2945 | -20.317 | 1.9511 | 7.29 | -35.4218 | -35.9075 | 55.2146 | 80.7661 | 32.8296 | 71.5399 | 27.3404 | 57.6444 | 29.8095
42838.4321 | 1023 | 22.759 | 22.7763 | 22.7719 | 22.6916 | 22.2973 | 21.6198 | 22.6418 | 21.6854 | 22.2967 | 22.2982 | 22.2584 | 21.9058 | 21.118 | 22.1007 | 21.475 | 22.4324 | 23.5766 | 24.4532 | 42.7739 | 50.019 | 84.503 | 89.2233 | 90.7953 | 25.8063 | 52.6875 | 91.8941 | 611.1047 | 634.0679 | 611.0445 | 24.6319 | 57.6845 | 98.0421 | 25.9442 | 55.3187 | 95.3495 | 723.0571 | 685.8448 |  | 373.4737 | 683.3245 | 695.4288 | 656.3655 |  | 462.1248 | 697.8615 | 631.5474 | 824.616 | 972.0768 | 1037.2012 | 1029.9903 | 44.1679 | 290.8923 | 72.7675 | 529.95 | 71.4663 | 51.7455 | 49.7678 | 55.2304 | 46.2204 |  |  | 0.62712 | 0.75496 | -76.9254 | 0.32523 | 7.5786 | -197.7684 | -203.2174 | -2.845 | 11.1569 | 36.0798 | 12.0547 | 0.00045505 | 4.928e-05 | 0.00037949 | 29.8768 | 22.2298 | 22.0953 | 22.1311 | 21.9404 | 21.2074 | 20.0647 | 22.1325 | 22.3021 | 22.3453 | 22.2809 | 21.888 | 21.1194 | 22.2067 | 650.5296 | 461.0268 | 350.661 | 283.5098 | 232.4891 | 749.1082 | 473.4814 | 22.2315 | 22.3082 | 23.4348 | 22.3515 | 36.7358 | 45.9647 | 28.6267 | 81.8167 | 87.6053 | 571.0477 | 525.8209 | 530.4409 | 537.5985 | 56.7516 | 22.1909 | 720.6098 | 22.1466 | 22.1453 | 362.3922 | 21.5333 | 21.9647 | 49.101 | 88.9538 | 97.9726 | 25.7694 | 57.3368 | 99.2485 | 696.5765 | 615.5101 | 757.2304 | 757.2045 | 681.6886 |  | 715.7964 | 684.2203 | 806.2933 | 560.9092 | 592.71 | 685.4753 |  | 570.9026 |  |  | 453.8509 | 593.0435 | 666.0912 | [5 empty] | 21.8274 | 545.3842 | 21.9893 | 22.0293 | 408.4346 | 21.465 | 21.8402 | 471.0952 | 595.9843 | 601.6714 |  | 759.1417 | 835.479 | 503.7871 | 664.9185 | 709.9836 | 557.4375 | 618.5668 | 712.2574 | 812.1121 | 602.9026 | 710.2022 | 1048.8179 | 1021.1637 | 927.0037 | 495.6416 | 591.358 | 606.6665 | 515.546 | 647.1963 | 720.7439 | 1056.9471 | 985.591 | 551.5726 | 620.4281 | 588.5744 | 799.1539 | 48.0507 | 0.00034891 | 19.5694 | 4.3223 | -28.5449 | 3.0964 | 6649.46 | -0.11 | 1.641 | 1.8869 | -19.0465 | 1.2384 | 6.9448 | -35.4764 | -35.9618 | 55.1817 | 80.3717 | 32.7528 | 72.8724 | 31.2668 | 57.6972 | 29.727
42838.4321 | 1024 | 22.756 | 22.7694 | 22.7741 | 22.6861 | 22.2883 | 21.6125 | 22.6392 | 21.6757 | 22.2882 | 22.2958 | 22.2522 | 21.8996 | 21.1183 | 22.0999 | 21.4812 | 22.4468 | 23.601 | 24.5156 | 42.8957 | 50.1285 | 84.5426 | 89.2184 | 90.8143 | 25.8439 | 52.7817 | 91.9441 | 610.7296 | 633.4042 | 610.8384 | 24.6669 | 57.788 | 98.1051 | 25.9697 | 55.4075 | 95.3899 | 721.9055 | 687.2025 |  | 381.7236 | 684.9056 | 695.9221 | 652.9412 |  | 463.3275 | 699.6636 | 631.465 | 823.6866 | 973.9945 | 1040.5814 | 1036.5809 | 43.912 | 291.1126 | 70.6482 | 529.7421 | 71.3748 | 51.714 | 49.7567 | 55.2365 | 46.2877 |  |  | 0.57783 | 1.3096 | -74.2273 | -0.22478 | 7.3605 | -197.8519 | -203.0472 | -3.0566 | 11.6074 | 37.4219 | 11.8318 | 0.00026942 | -0.00014292 | 0.00042548 | 29.9381 | 22.2304 | 22.0956 | 22.14 | 21.9438 | 21.2053 | 20.065 | 22.1347 | 22.3092 | 22.3499 | 22.2869 | 21.8817 | 21.1268 | 22.2069 | 645.1705 | 443.1813 | 324.9668 | 268.982 | 223.5104 | 745.7013 | 470.2846 | 22.2255 | 22.3121 | 23.4477 | 22.3557 | 36.8263 | 46.0529 | 28.6767 | 81.8396 | 87.6363 | 570.6616 | 524.7967 | 529.8961 | 538.6207 | 76.5124 | 27.54 | 716.9439 | 22.1405 | 22.1442 | 361.1228 | 21.5332 | 21.9588 | 49.255 | 88.9716 | 98.026 | 25.8064 | 57.4294 | 99.3531 | 697.9574 | 614.6153 | 749.5651 | 750.7596 | 683.5278 |  | 715.859 | 683.6099 | 805.1002 | 560.2139 | 591.9868 | 684.8604 |  | 571.108 |  |  | 453.7094 | 594.0893 | 667.8975 | [5 empty] | 21.8412 | 544.584 | 22.0072 | 22.0436 | 408.0184 | 21.4814 | 21.8537 | 470.3467 | 595.2054 | 600.9578 |  | 757.7899 | 836.6634 | 504.4637 | 666.1788 | 709.1039 | 556.6292 | 617.9137 | 702.6402 | 812.5539 | 604.438 | 711.0292 | 1043.3647 | 1027.3137 | 927.9381 | 494.7758 | 590.2963 | 605.9904 | 514.0876 | 647.5766 | 719.8768 | 1060.5554 | 989.3142 | 550.8597 | 619.4711 | 587.5859 | 799.5812 | 48.6311 | 0.00065788 | 19.5699 | 4.4264 | -28.4942 | 3.0964 | 6525.85 | 0 | 1.575 | 2.4874 | -18.7268 | -1.0305 | 6.8529 | -35.5296 | -35.9931 | 55.1461 | 80.0157 | 32.6456 | 72.268 | 33.4667 | 57.5026 | 29.6352
42838.4321 | 1025 | 22.7523 | 22.7689 | 22.7717 | 22.6794 | 22.2859 | 21.6113 | 22.6356 | 21.673 | 22.2791 | 22.2984 | 22.2536 | 21.9006 | 21.1145 | 22.0929 | 21.4717 | 22.4511 | 23.6111 | 24.5713 | 43.0007 | 50.2349 | 84.5624 | 89.2091 | 90.8111 | 25.8647 | 52.8752 | 91.9872 | 610.8285 | 631.5322 | 610.906 | 24.6941 | 57.8831 | 98.159 | 26.007 | 55.5004 | 95.4406 | 721.013 | 686.6308 |  | 387.0971 | 688.0073 | 697.022 | 653.3866 |  | 463.7185 | 701.1941 | 630.4203 | 821.9176 | 973.1917 | 1041.8165 | 1042.4128 | 43.9806 | 291.3825 | 69.2712 | 529.3749 | 71.4776 | 51.6864 | 49.7425 | 55.2278 | 46.3439 |  |  | 0.43984 | 0.88573 | -74.0821 | 0.31866 | 8.6405 | -197.8388 | -200.1086 | -3.0651 | 11.7716 | 37.8075 | 11.6317 | 0.00049284 | -5.914e-05 | 0.00039098 | 29.9929 | 22.2377 | 22.1014 | 22.1357 | 21.9333 | 21.2096 | 20.0672 | 22.137 | 22.3079 | 22.3398 | 22.2833 | 21.8851 | 21.1172 | 22.2016 | 658.7762 | 457.8741 | 354.7208 | 268.0265 | 225.1485 | 743.3474 | 467.7395 | 22.2272 | 22.3142 | 23.4681 | 22.3691 | 36.9242 | 46.1491 | 28.7344 | 81.8639 | 87.6617 | 570.138 | 523.2324 | 528.1521 | 536.3987 | 68.8839 | 30.3506 | 714.8746 | 22.1303 | 22.1311 | 360.4471 | 21.5196 | 21.9404 | 49.3949 | 88.9795 | 98.0666 | 25.8327 | 57.5309 | 99.4391 | 700.1166 | 614.4407 | 743.7707 | 745.8903 | 687.5451 |  | 716.1826 | 683.1244 | 803.8965 | 560.9469 | 591.3065 | 684.4311 |  | 570.9519 |  |  | 454.1531 | 595.0221 | 670.6889 | [5 empty] | 21.8308 | 544.2369 | 22.0012 | 22.0319 | 407.699 | 21.4709 | 21.8394 | 469.6598 | 594.2667 | 600.1455 |  | 752.3099 | 836.4602 | 504.848 | 666.8905 | 708.6374 | 555.867 | 617.2035 | 693.9612 | 810.5228 | 605.094 | 711.4319 | 1041.1845 | 1025.1421 | 928.285 | 494.4349 | 589.7215 | 605.6236 | 512.6753 | 647.3783 | 718.8165 | 1059.7035 | 988.7382 | 550.7021 | 619.2242 | 586.649 | 798.4676 | 48.1828 | -0.00037432 | 19.5699 | 4.5351 | -28.4648 | 3.0964 | 6407.63 | -0.11 | 1.3742 | 2.0473 | -18.7232 | 1.228 | 7.4284 | -35.5451 | -35.7484 | 55.1146 | 79.6542 | 32.5066 | 69.932 | 29.6419 | 57.2662 | 29.6111
42838.4322 | 1026 | 22.7542 | 22.7697 | 22.7638 | 22.6831 | 22.291 | 21.6156 | 22.6365 | 21.6754 | 22.284 | 22.2949 | 22.2548 | 21.9039 | 21.1179 | 22.0932 | 21.4719 | 22.4721 | 23.6364 | 24.6377 | 43.1162 | 50.3431 | 84.5899 | 89.219 | 90.8307 | 25.8983 | 52.971 | 92.0355 | 610.4329 | 629.9914 | 610.3046 | 24.7168 | 57.9846 | 98.2085 | 26.0393 | 55.5915 | 95.493 | 720.3205 | 684.5455 |  | 388.9743 | 692.5517 | 700.5189 | 653.0819 |  | 466.0099 | 701.7077 | 630.634 | 823.4853 | 967.4191 | 1042.7556 | 1047.6509 | 43.9792 | 291.5867 | 68.8658 | 529.1513 | 71.4555 | 51.6617 | 49.7274 | 55.231 | 46.4024 |  |  | 0.75986 | 0.42969 | -72.6574 | 0.018354 | 7.6621 | -197.8118 | -203.2003 | -3.2327 | 11.6965 | 37.7232 | 11.5086 | 0.00046327 | -4.435e-05 | 0.00043534 | 30.046 | 22.2361 | 22.1011 | 22.1395 | 21.9328 | 21.2043 | 20.0651 | 22.1324 | 22.3037 | 22.3424 | 22.287 | 21.8884 | 21.114 | 22.2096 | 661.1104 | 475.7158 | 384.2953 | 277.1739 | 229.8899 | 741.3326 | 465.6153 | 22.2284 | 22.3077 | 23.4822 | 22.3633 | 37.0346 | 46.2487 | 28.7823 | 81.8664 | 87.6774 | 569.444 | 520.1773 | 524.6583 | 534.4799 | 89.2071 | 37.4628 | 714.2063 | 22.1508 | 22.137 | 359.6798 | 21.5257 | 21.9449 | 49.5469 | 89.0037 | 98.1381 | 25.8791 | 57.6425 | 99.551 | 703.1607 | 614.4768 | 740.5308 | 743.5668 | 689.3739 |  | 716.4184 | 682.6425 | 802.8536 | 562.009 | 590.7887 | 683.5402 |  | 571.1628 |  |  | 454.2974 | 596.1193 | 672.2009 | [5 empty] | 21.8283 | 544.2643 | 22.0055 | 22.0399 | 407.2078 | 21.4718 | 21.8425 | 469.1018 | 593.4375 | 599.1456 |  | 744.4378 | 835.3729 | 504.6639 | 666.7905 | 707.809 | 555.301 | 616.377 | 685.3005 | 806.62 | 604.6881 | 710.0909 | 1041.2861 | 1026.5264 | 927.7126 | 494.0216 | 590.0206 | 605.6 | 511.4078 | 645.2926 | 716.8447 | 1062.8699 | 988.8057 | 550.8069 | 619.9383 | 584.9667 | 796.7664 | 47.0944 | -0.00062707 | 19.5696 | 4.6391 | -28.4984 | 3.0964 | 6273.82 | -0.07 | 1.8056 | 1.4263 | -18.5472 | 0.29478 | 6.9977 | -35.5554 | -36.0364 | 55.1221 | 79.3434 | 32.3869 | 68.9703 | 25.9248 | 57.1013 | 29.5508
42838.4322 | 1027 | 22.759 | 22.7695 | 22.7665 | 22.6889 | 22.2892 | 21.6184 | 22.637 | 21.6736 | 22.2874 | 22.2923 | 22.2586 | 21.9049 | 21.1198 | 22.0978 | 21.4743 | 22.4771 | 23.6513 | 24.6991 | 43.2221 | 50.4465 | 84.6267 | 89.2181 | 90.848 | 25.9227 | 53.0593 | 92.0842 | 609.4195 | 629.3501 | 609.0293 | 24.7489 | 58.0868 | 98.264 | 26.0758 | 55.685 | 95.544 | 719.5382 | 683.1462 |  | 396.5894 | 696.8232 | 705.3943 | 652.9065 |  | 467.6274 | 702.6623 | 630.9436 | 821.453 | 962.1324 | 1041.8138 | 1049.293 | 43.5115 | 291.7175 | 69.1399 | 529.1714 | 71.4973 | 51.6338 | 49.7086 | 55.2417 | 46.4616 |  |  | 0.71254 | 0.68071 | -74.9777 | -0.15381 | 7.5872 | -197.8177 | -203.3271 | -2.9981 | 11.355 | 36.6727 | 11.3326 | 0.00037127 | -5.585e-05 | 0.0004107 | 30.1107 | 22.2449 | 22.0958 | 22.142 | 21.9392 | 21.2068 | 20.0727 | 22.1368 | 22.3056 | 22.3444 | 22.2885 | 21.8922 | 21.1195 | 22.2109 | 683.3505 | 514.3031 | 403.4669 | 284.7524 | 233.3914 | 740.6092 | 463.6232 | 22.2233 | 22.3227 | 23.4987 | 22.3689 | 37.1361 | 46.3463 | 28.8449 | 81.8837 | 87.7074 | 569.117 | 521.4738 | 526.3789 | 538.0019 | 67.8547 | 33.8237 | 713.7148 | 22.1485 | 22.1338 | 359.693 | 21.526 | 21.9514 | 49.6893 | 89.0228 | 98.1983 | 25.9192 | 57.7562 | 99.654 | 704.3319 | 614.2789 | 741.3861 | 744.4589 | 688.519 |  | 716.4359 | 681.8975 | 801.8672 | 562.4519 | 590.3287 | 683.9604 |  | 571.5795 |  |  | 454.4959 | 597.3474 | 671.6802 | [5 empty] | 21.8317 | 544.7216 | 22.0079 | 22.0411 | 406.6097 | 21.4835 | 21.8474 | 468.9148 | 592.9348 | 598.4056 |  | 737.5386 | 835.276 | 504.0766 | 665.4987 | 706.4075 | 555.033 | 615.6729 | 676.8302 | 804.6644 | 603.2103 | 708.1281 | 1048.0093 | 1030.0942 | 928.4906 | 493.3566 | 590.9918 | 604.9638 | 510.0691 | 642.8727 | 714.8386 | 1066.4581 | 993.2503 | 550.5362 | 619.7662 | 583.3979 | 794.956 | 44.8187 | -0.00029004 | 19.5695 | 4.7285 | -28.5543 | 3.0963 | 6179.27 | -0.04 | 1.7472 | 1.7961 | -18.8502 | -0.85377 | 6.9609 | -35.5432 | -36.0348 | 55.1502 | 79.0585 | 32.2946 | 66.2477 | 23.3918 | 56.9107 | 29.3996
42838.4322 | 1028 | 22.7534 | 22.7612 | 22.7623 | 22.6793 | 22.2883 | 21.6154 | 22.6291 | 21.6704 | 22.2871 | 22.2963 | 22.2612 | 21.8974 | 21.1152 | 22.0966 | 21.4835 | 22.4941 | 23.6761 | 24.7671 | 43.3346 | 50.5528 | 84.6457 | 89.2335 | 90.8732 | 25.9547 | 53.1616 | 92.1403 | 608.4555 | 629.3354 | 607.9202 | 24.7853 | 58.1887 | 98.3381 | 26.1154 | 55.7779 | 95.6051 | 718.7148 | 682.8635 |  | 389.9941 | 694.6375 | 703.4716 | 653.3048 |  | 469.1932 | 703.8468 | 633.601 | 822.4739 | 964.5326 | 1038.7185 | 1052.1182 | 43.4671 | 291.8407 | 68.8845 | 529.2675 | 71.4809 | 51.6045 | 49.6957 | 55.2598 | 46.5243 |  |  | 0.86894 | 0.64785 | -77.2349 | 0.37123 | 7.9861 | -197.8716 | -184.6985 | -3.0316 | 10.901 | 35.5553 | 11.2371 | 0.00052898 | 1.807e-05 | 0.00037949 | 30.1617 | 22.2496 | 22.0962 | 22.1389 | 21.9334 | 21.2013 | 20.068 | 22.1261 | 22.3104 | 22.3421 | 22.2802 | 21.8895 | 21.1136 | 22.2065 | 685.8699 | 510.5798 | 414.0417 | 285.6268 | 232.4146 | 738.8572 | 461.5854 | 22.2207 | 22.3316 | 23.5192 | 22.3821 | 37.2334 | 46.4381 | 28.91 | 81.9291 | 87.7526 | 568.9722 | 522.1629 | 526.6794 | 539.3178 | 59.8517 | 31.1603 | 712.5261 | 22.1455 | 22.1406 | 359.4799 | 21.5299 | 21.9532 | 49.8488 | 89.0378 | 98.2518 | 25.9523 | 57.8602 | 99.7466 | 703.9128 | 614.2425 | 742.0875 | 745.0992 | 687.2358 |  | 716.3949 | 681.0547 | 800.9468 | 562.404 | 589.8048 | 683.8709 |  | 571.659 |  |  | 454.503 | 598.1314 | 671.115 | [5 empty] | 21.8377 | 545.0416 | 22.0158 | 22.0446 | 405.9996 | 21.4853 | 21.8517 | 468.8101 | 592.5538 | 597.8782 |  | 734.2541 | 835.2025 | 503.5606 | 664.02 | 704.9808 | 554.4657 | 615.171 | 669.1588 | 803.9672 | 603.1391 | 706.7328 | 1054.0443 | 1035.1833 | 931.3738 | 492.4714 | 591.3175 | 603.9258 | 508.8192 | 641.0158 | 713.0712 | 1071.2968 | 1001.5568 | 549.9497 | 618.941 | 582.1826 | 793.4647 | 45.5258 | 8.9138e-05 | 19.5692 | 4.8095 | -28.5131 | 3.0964 | 6099.41 | -0.11 | 1.9283 | 1.7533 | -19.1435 | 1.3272 | 7.1331 | -35.5062 | -34.3039 | 55.1757 | 78.7973 | 32.205 | 65.3601 | 21.8063 | 56.6943 | 29.3394
42838.4322 | 1029 | 22.761 | 22.77 | 22.7644 | 22.6926 | 22.2909 | 21.6216 | 22.6397 | 21.6762 | 22.2912 | 22.2936 | 22.265 | 21.9066 | 21.1234 | 22.0977 | 21.4898 | 22.5111 | 23.6892 | 24.8365 | 43.4523 | 50.6639 | 84.6632 | 89.2411 | 90.8947 | 25.9861 | 53.2637 | 92.191 | 607.6613 | 629.4159 | 607.1462 | 24.8169 | 58.2985 | 98.4067 | 26.1538 | 55.8687 | 95.6581 | 718.084 | 683.2585 |  | 390.6916 | 689.7071 | 698.783 | 654.9787 |  | 470.4855 | 703.7033 | 636.3079 | 817.5364 | 966.7451 | 1041.329 | 1056.3015 | 43.5988 | 291.8976 | 67.5896 | 529.1815 | 71.4794 | 51.556 | 49.6822 | 55.2661 | 46.5999 |  |  | 0.8052 | 1.2287 | -101.6822 | 0.29566 | 7.8487 | -197.8052 | -195.1973 | -3.2919 | 11.4685 | 36.8504 | 11.1718 | 0.00051255 | -2.135e-05 | 0.00039427 | 30.2253 | 22.2504 | 22.0969 | 22.1376 | 21.9327 | 21.2044 | 20.0664 | 22.1299 | 22.3093 | 22.3484 | 22.2892 | 21.8868 | 21.122 | 22.2018 | 658.5301 | 495.417 | 416.9599 | 281.8039 | 229.9921 | 736.0663 | 459.6366 | 22.2284 | 22.3365 | 23.5381 | 22.3819 | 37.3385 | 46.5354 | 28.9735 | 81.9687 | 87.7919 | 568.5489 | 520.2414 | 524.6167 | 536.39 | 74.4261 | 31.5049 | 710.7261 | 22.1534 | 22.1377 | 358.8515 | 21.5299 | 21.9498 | 50.0013 | 89.0513 | 98.3143 | 25.9983 | 57.9671 | 99.8423 | 701.6547 | 614.4786 | 739.2013 | 742.569 | 687.3909 |  | 716.4353 | 680.0738 | 799.9011 | 563.059 | 589.3751 | 683.044 |  | 571.8159 |  |  | 454.5623 | 598.3798 | 671.5222 | [5 empty] | 21.8249 | 545.6236 | 22.0193 | 22.0412 | 405.4599 | 21.4841 | 21.8485 | 468.3993 | 592.0245 | 597.089 |  | 732.1422 | 834.89 | 504.0145 | 663.9065 | 703.9524 | 553.9537 | 614.5974 | 662.4339 | 803.2862 | 605.0078 | 706.7395 | 1058.6521 | 1044.0953 | 935.8909 | 491.9832 | 590.9333 | 602.8385 | 507.729 | 639.4126 | 711.3098 | 1076.0189 | 1008.5925 | 549.4379 | 618.2225 | 581.0843 | 792.0553 | 45.9614 | -0.001259 | 19.5696 | 4.8852 | -28.4489 | 3.0964 | 6088.66 | -0.08 | 1.8554 | 2.4144 | -21.9636 | 1.1843 | 7.0785 | -35.5355 | -35.3005 | 55.1814 | 78.502 | 32.1122 | 67.4345 | 21.0909 | 56.4908 | 29.3517
42838.4322 | 1030 | 22.7563 | 22.7731 | 22.7661 | 22.6918 | 22.2943 | 21.62 | 22.6322 | 21.6776 | 22.2911 | 22.2995 | 22.2628 | 21.9026 | 21.1216 | 22.0989 | 21.4801 | 22.5169 | 23.7021 | 24.895 | 43.5587 | 50.7686 | 84.6714 | 89.2374 | 90.9041 | 26.0057 | 53.3532 | 92.2299 | 607.1723 | 629.1288 | 606.7956 | 24.8516 | 58.4044 | 98.4703 | 26.1863 | 55.9711 | 95.7078 | 717.6597 | 683.6606 |  | 390.2756 | 689.9061 | 698.9908 | 660.7225 |  | 470.19 | 703.3205 | 639.0988 | 820.8523 | 970.5544 | 1042.8942 | 1057.4271 | 42.806 | 291.9191 | 66.4884 | 528.9575 | 71.3481 | 51.4807 | 49.6677 | 55.2705 | 46.6504 |  |  | 0.78614 | 0.68268 | -102.4511 | 0.63145 | 7.5208 | -197.7974 | -177.2922 | -3.2196 | 11.428 | 37.744 | 11.6893 | 0.00049284 | -3.285e-05 | 0.00040413 | 30.2799 | 22.2537 | 22.0954 | 22.1396 | 21.9416 | 21.2002 | 20.0725 | 22.1309 | 22.3093 | 22.3493 | 22.2911 | 21.8821 | 21.1234 | 22.2057 | 652.2424 | 497.3005 | 412.4709 | 285.6466 | 235.1228 | 734.0786 | 457.6401 | 22.2327 | 22.3414 | 23.5542 | 22.3836 | 37.4288 | 46.6303 | 29.0321 | 81.9897 | 87.8171 | 567.8856 | 517.77 | 521.4967 | 532.216 | 69.1352 | 28.6826 | 707.6899 | 22.1529 | 22.1269 | 358.1797 | 21.5287 | 21.9508 | 50.1473 | 89.0512 | 98.3748 | 26.0428 | 58.0774 | 99.943 | 699.6268 | 614.7443 | 734.6626 | 738.5671 | 686.1712 |  | 716.4071 | 679.323 | 798.8675 | 562.507 | 588.9442 | 682.4013 |  | 571.9812 |  |  | 454.7434 | 598.3322 | 671.249 | [5 empty] | 21.8315 | 546.0143 | 22.0241 | 22.0438 | 404.6136 | 21.495 | 21.8487 | 468.0989 | 591.5956 | 596.3076 |  | 729.2734 | 835.7531 | 504.693 | 664.6803 | 703.5535 | 553.6957 | 614.4657 | 656.5407 | 803.832 | 604.9634 | 707.5395 | 1059.8937 | 1046.1026 | 939.823 | 491.8032 | 590.7478 | 601.8731 | 506.7671 | 638.0017 | 710.1523 | 1078.1663 | 1010.0261 | 549.0926 | 617.5867 | 580.3692 | 790.616 | 47.6543 | 0.0082624 | 19.5691 | 4.9698 | -28.5064 | 3.0963 | 6087.63 | -0.16 | 1.8329 | 1.7993 | -22.0422 | 1.7305 | 6.9332 | -35.556 | -33.6625 | 55.2083 | 78.2049 | 32.0529 | 67.4502 | 21.1904 | 56.2258 | 29.3596
42838.4322 | 1031 | 22.752 | 22.7556 | 22.7586 | 22.6759 | 22.2855 | 21.6058 | 22.6282 | 21.665 | 22.2812 | 22.2849 | 22.2538 | 21.8878 | 21.1094 | 22.0909 | 21.4735 | 22.5247 | 23.7233 | 24.9571 | 43.6688 | 50.8697 | 84.6797 | 89.2328 | 90.9215 | 26.0361 | 53.4442 | 92.2802 | 606.8865 | 628.7419 | 606.6729 | 24.8697 | 58.4917 | 98.5205 | 26.2183 | 56.0687 | 95.7521 | 717.8576 | 682.6766 |  | 380.962 | 688.0884 | 697.0903 | 664.501 |  | 471.9874 | 703.7284 | 639.2905 | 827.8575 | 964.2722 | 1043.2851 | 1054.1611 | 41.7179 | 291.8553 | 65.6616 | 528.627 | 71.4638 | 51.3946 | 49.6517 | 55.2999 | 46.7054 |  |  | 0.66457 | 0.20167 | -77.8158 | -0.1157 | 7.9486 | -197.8322 | -181.1521 | -3.0862 | 11.0902 | 36.3287 | 11.806 | 0.00047312 | 1.479e-05 | 0.00040248 | 30.3388 | 22.2628 | 22.0968 | 22.1363 | 21.9386 | 21.212 | 20.0698 | 22.1417 | 22.3085 | 22.3498 | 22.2902 | 21.8821 | 21.1248 | 22.2091 | 626.5613 | 468.105 | 404.5965 | 278.3625 | 225.9683 | 731.5175 | 455.4188 | 22.2186 | 22.3476 | 23.5776 | 22.3913 | 37.5428 | 46.7307 | 29.0905 | 82.0052 | 87.8467 | 566.9199 | 512.6497 | 517.3728 | 528.0074 | 55.8623 | 28.8167 | 705.6286 | 22.1648 | 22.1483 | 357.4503 | 21.5359 | 21.9612 | 50.3006 | 89.0682 | 98.4413 | 26.0822 | 58.1911 | 100.0427 | 698.8476 | 614.8534 | 731.8016 | 735.9718 | 686.2858 |  | 716.4095 | 678.6275 | 797.6898 | 561.6876 | 588.3382 | 681.7381 |  | 573.5474 |  |  | 454.288 | 597.0682 | 671.6517 | [5 empty] | 21.8386 | 546.1872 | 22.0282 | 22.0454 | 404.1435 | 21.4969 | 21.8487 | 467.9006 | 591.2576 | 595.9485 |  | 726.3173 | 836.5734 | 504.4152 | 664.6409 | 703.1765 | 553.3807 | 614.1123 | 650.3052 | 803.4315 | 604.1701 | 707.9405 | 1054.9999 | 1044.9313 | 941.0476 | 491.6693 | 591.0786 | 601.1408 | 506.3341 | 637.1724 | 709.3641 | 1077.5071 | 1007.9056 | 548.8385 | 616.9008 | 580.2997 | 789.8907 | 46.9329 | -0.00024088 | 19.5695 | 5.0577 | -28.5167 | 3.0964 | 6097.67 | -0.01 | 1.6851 | 0.97816 | -19.2141 | -0.74088 | 7.1287 | -35.5644 | -34.0321 | 55.2057 | 77.863 | 31.9709 | 69.4278 | 21.6228 | 56.17 | 29.3196
42838.4322 | 1032 | 22.7522 | 22.7582 | 22.7565 | 22.6789 | 22.2886 | 21.6041 | 22.6275 | 21.6709 | 22.2874 | 22.2895 | 22.2493 | 21.8922 | 21.1121 | 22.0856 | 21.4878 | 22.544 | 23.7446 | 25.0305 | 43.781 | 50.9761 | 84.7134 | 89.2356 | 90.9386 | 26.0692 | 53.5377 | 92.3377 | 606.4859 | 628.9176 | 606.2319 | 24.9072 | 58.5935 | 98.5813 | 26.2586 | 56.1581 | 95.8016 | 718.3858 | 682.2745 |  | 384.5721 | 688.3945 | 698.0084 | 665.4142 |  | 473.5408 | 705.1376 | 638.5896 | 836.7318 | 962.9123 | 1043.841 | 1051.8663 | 41.7406 | 291.7746 | 65.9766 | 528.4867 | 71.5093 | 51.3041 | 49.6374 | 55.3154 | 46.7579 |  |  | 0.85054 | 0.32652 | -84.9218 | 0.12547 | 7.879 | -197.8158 | -192.9841 | -3.2045 | 10.9907 | 35.265 | 11.7105 | 0.00038606 | -7.885e-05 | 0.00039756 | 30.4082 | 22.2659 | 22.099 | 22.1442 | 21.9399 | 21.2054 | 20.0747 | 22.1366 | 22.3025 | 22.3434 | 22.2876 | 21.8862 | 21.1256 | 22.2035 | 599.957 | 461.1932 | 399.016 | 276.7463 | 221.5202 | 728.0871 | 453.2392 | 22.2285 | 22.3518 | 23.6039 | 22.4025 | 37.6399 | 46.8322 | 29.1481 | 82.029 | 87.8886 | 566.0861 | 508.5188 | 514.2753 | 525.6482 | 61.6117 | 24.0603 | 704.306 | 22.1619 | 22.1444 | 356.3272 | 21.5317 | 21.958 | 50.4386 | 89.0913 | 98.5069 | 26.1262 | 58.3012 | 100.1404 | 697.8589 | 615.1946 | 730.1613 | 734.3712 | 686.8326 |  | 716.5363 | 677.7858 | 796.3114 | 562.0473 | 587.8155 | 680.0464 |  | 575.7563 |  |  | 453.106 | 595.9286 | 672.6866 | [5 empty] | 21.8328 | 546.2161 | 22.0278 | 22.0442 | 404.1558 | 21.4989 | 21.8426 | 467.645 | 590.7117 | 595.8529 |  | 721.7364 | 836.5934 | 503.655 | 664.7658 | 702.4661 | 552.9807 | 614.0191 | 644.2841 | 800.8836 | 603.7313 | 708.497 | 1054.1726 | 1046.8298 | 940.4527 | 491.0102 | 591.4503 | 600.4158 | 505.8783 | 636.8876 | 708.7723 | 1079.4884 | 1009.9318 | 548.4836 | 616.1194 | 580.2394 | 789.5387 | 45.7045 | 0.00058066 | 19.5693 | 5.146 | -28.4826 | 3.0964 | 6132.34 | -0.19 | 1.9059 | 1.2455 | -20.0868 | 0.77208 | 7.0989 | -35.5704 | -35.1333 | 55.2219 | 77.465 | 31.8707 | 71.2178 | 21.8104 | 56.276 | 29.25
42838.4322 | 1033 | 22.7488 | 22.7592 | 22.7611 | 22.6767 | 22.2875 | 21.6095 | 22.6257 | 21.6755 | 22.2901 | 22.2823 | 22.2483 | 21.8916 | 21.1091 | 22.085 | 21.4819 | 22.551 | 23.7668 | 25.0921 | 43.89 | 51.0878 | 84.7517 | 89.2328 | 90.9631 | 26.104 | 53.6308 | 92.3957 | 605.9883 | 629.2124 | 605.5632 | 24.9331 | 58.6928 | 98.6345 | 26.2945 | 56.2471 | 95.8508 | 718.4208 | 683.1286 |  | 387.3284 | 690.9729 | 700.9787 | 661.6626 |  | 473.7777 | 706.6629 | 637.5486 | 833.1309 | 954.6326 | 1042.4008 | 1052.5642 | 41.9073 | 291.6176 | 65.2888 | 528.2165 | 71.4961 | 51.208 | 49.6223 | 55.3431 | 46.8154 |  |  | 1.1482 | 0.94684 | -110.4199 | -0.20047 | 7.5129 | -197.8276 | -188.7477 | -3.1532 | 10.7202 | 34.6278 | 12.0599 | 5.093e-05 | -0.00019385 | 0.00042056 | 30.4636 | 22.2707 | 22.0973 | 22.1438 | 21.9335 | 21.2081 | 20.0676 | 22.141 | 22.3076 | 22.3405 | 22.2868 | 21.8925 | 21.1216 | 22.215 | 598.8316 | 456.0168 | 369.8264 | 278.2075 | 222.0928 | 724.8186 | 450.6618 | 22.2236 | 22.3611 | 23.6224 | 22.3985 | 37.7345 | 46.9261 | 29.2107 | 82.0669 | 87.924 | 565.2738 | 508.1008 | 513.5069 | 524.6393 | 56.1647 | 24.9364 | 702.9395 | 22.1623 | 22.143 | 355.3973 | 21.5288 | 21.9555 | 50.5861 | 89.1122 | 98.5632 | 26.1566 | 58.4194 | 100.2392 | 696.395 | 615.5041 | 728.505 | 732.7209 | 686.7942 |  | 716.6495 | 677.0258 | 795.1291 | 561.561 | 587.3428 | 679.1899 |  | 575.9921 |  |  | 452.1904 | 595.7375 | 673.3006 | [5 empty] | 21.8288 | 546.0307 | 22.0267 | 22.0418 | 404.2692 | 21.5047 | 21.851 | 467.421 | 590.2743 | 595.4922 |  | 715.8322 | 837.4626 | 503.0847 | 665.8066 | 701.9355 | 552.5906 | 613.8272 | 638.5329 | 798.6452 | 603.391 | 709.3334 | 1056.7533 | 1050.8748 | 943.2138 | 490.5058 | 591.5099 | 599.5519 | 505.0556 | 636.5165 | 708.2024 | 1077.9751 | 1013.9607 | 547.6663 | 615.2051 | 580.0925 | 789.0605 | 46.0758 | -0.00087987 | 19.568 | 5.2343 | -28.4678 | 3.0964 | 6146.21 | -0.09 | 2.2136 | 2.1226 | -22.9225 | -0.97669 | 6.9283 | -35.552 | -34.7265 | 55.251 | 77.1258 | 31.8027 | 70.2393 | 24.5444 | 56.3889 | 29.1468
42838.4322 | 1034 | 22.7512 | 22.7618 | 22.771 | 22.6836 | 22.2936 | 21.6132 | 22.6318 | 21.679 | 22.2887 | 22.2896 | 22.2542 | 21.8994 | 21.1199 | 22.0956 | 21.4805 | 22.5567 | 23.7926 | 25.159 | 44.0033 | 51.1922 | 84.7844 | 89.2376 | 90.9731 | 26.1278 | 53.7247 | 92.4401 | 605.2667 | 628.8852 | 604.4455 | 24.9591 | 58.7949 | 98.6871 | 26.3328 | 56.3465 | 95.9006 | 717.898 | 684.0776 |  | 387.9102 | 698.5471 | 708.3827 | 657.574 |  | 473.7197 | 706.8192 | 636.3821 | 833.4603 | 949.517 | 1037.606 | 1054.6265 | 41.6445 | 291.4423 | 66.0597 | 527.9928 | 71.4797 | 51.1377 | 49.605 | 55.3684 | 46.8631 |  |  | 0.88602 | 0.91595 | -84.9337 | 0.35545 | 8.1477 | -197.8447 | -164.8924 | -3.3076 | 11.0614 | 35.6915 | 11.8289 | 0.00010185 | -0.00018563 | 0.00038441 | 30.5281 | 22.2644 | 22.0924 | 22.1371 | 21.9355 | 21.2086 | 20.0679 | 22.1335 | 22.307 | 22.3458 | 22.2867 | 21.8866 | 21.1128 | 22.2081 | 599.2074 | 468.498 | 357.893 | 271.6203 | 220.3131 | 721.6282 | 448.0073 | 22.2194 | 22.3562 | 23.6298 | 22.3997 | 37.8311 | 47.0082 | 29.2676 | 82.0922 | 87.9572 | 564.5001 | 507.1908 | 513.6726 | 524.4414 | 72.7088 | 30.926 | 700.6179 | 22.1636 | 22.1379 | 354.2292 | 21.5284 | 21.9608 | 50.7297 | 89.1276 | 98.6219 | 26.1998 | 58.5239 | 100.3226 | 695.5731 | 615.9838 | 726.4572 | 730.9268 | 685.6948 |  | 716.5965 | 676.2484 | 794.0398 | 562.2878 | 586.9257 | 678.6407 |  | 577.3172 |  |  | 451.7107 | 595.7157 | 672.7053 | [5 empty] | 21.8313 | 546.5202 | 22.0383 | 22.0463 | 404.743 | 21.5096 | 21.8585 | 466.9498 | 589.8389 | 594.8452 |  | 711.531 | 837.4485 | 502.7016 | 666.5904 | 701.9022 | 552.1268 | 613.0357 | 633.4067 | 796.6098 | 603.7674 | 710.2557 | 1057.5508 | 1050.4064 | 944.9711 | 490.1097 | 590.8594 | 598.7559 | 504.3939 | 636.3467 | 707.5742 | 1071.8647 | 1011.9569 | 546.9571 | 614.3879 | 580.5124 | 788.8879 | 45.4366 | 0.0028487 | 19.5678 | 5.3137 | -28.4703 | 3.0965 | 6133.27 | -0.14 | 1.9433 | 2.0879 | -20.1054 | 1.3007 | 7.2019 | -35.4887 | -32.3987 | 55.2684 | 76.8164 | 31.7107 | 69.1273 | 25.3484 | 56.3725 | 29.0275
42838.4323 | 1035 | 22.7539 | 22.7602 | 22.7691 | 22.6766 | 22.2935 | 21.6107 | 22.6325 | 21.6741 | 22.2965 | 22.2858 | 22.2612 | 21.8957 | 21.1166 | 22.0994 | 21.4797 | 22.5666 | 23.8067 | 25.218 | 44.1018 | 51.2854 | 84.7828 | 89.2417 | 90.9716 | 26.1504 | 53.8129 | 92.481 | 604.7445 | 627.8938 | 604.1051 | 24.9964 | 58.903 | 98.7306 | 26.3815 | 56.4338 | 95.959 | 717.5283 | 683.6333 |  | 392.1168 | 703.3618 | 712.1377 | 656.8423 |  | 473.6896 | 707.5581 | 635.7258 | 831.6733 | 947.7255 | 1033.1514 | 1054.4518 | 41.1438 | 291.2509 | 67.0285 | 527.9204 | 71.5256 | 51.0751 | 49.6011 | 55.3895 | 46.9223 |  |  | 0.68232 | 0.6288 | -102.5792 | 0.045954 | 8.4809 | -197.8164 | -203.0505 | -3.0277 | 11.1005 | 35.3797 | 12.032 | 0.000115 | -0.00020042 | 0.00043534 | 30.5821 | 22.2682 | 22.0963 | 22.1384 | 21.9292 | 21.207 | 20.0689 | 22.1352 | 22.3081 | 22.3487 | 22.2854 | 21.8898 | 21.1209 | 22.2054 | 601.4914 | 489.6316 | 363.4763 | 270.9104 | 217.1925 | 719.1456 | 445.7737 | 22.2247 | 22.3647 | 23.6489 | 22.4088 | 37.9366 | 47.1085 | 29.3391 | 82.1343 | 87.9998 | 563.725 | 506.1654 | 512.4205 | 524.1382 | 65.5785 | 22.0292 | 698.5841 | 22.1668 | 22.1402 | 353.3572 | 21.5279 | 21.9551 | 50.8692 | 89.1527 | 98.6875 | 26.2377 | 58.6459 | 100.4248 | 695.5357 | 616.3014 | 723.37 | 728.1576 | 684.3825 |  | 716.4005 | 675.6613 | 793.0849 | 565.5708 | 586.7152 | 677.903 |  | 577.7821 |  |  | 451.1994 | 594.7045 | 671.4815 | [5 empty] | 21.8268 | 547.9364 | 22.0452 | 22.0479 | 404.8482 | 21.5089 | 21.8578 | 466.1423 | 589.3283 | 594.1682 |  | 708.0976 | 835.9708 | 502.1856 | 666.8324 | 701.7332 | 551.539 | 612.2274 | 628.7704 | 795.215 | 604.1611 | 709.9906 | 1060.6682 | 1047.2621 | 942.8791 | 489.9071 | 589.8632 | 598.0355 | 504.1031 | 636.4173 | 705.9525 | 1071.1981 | 1009.1855 | 546.3499 | 613.801 | 580.921 | 788.3701 | 46.0673 | 0.00067893 | 19.5674 | 5.3972 | -28.5062 | 3.0964 | 6139.07 | -0.13 | 1.705 | 1.7306 | -22.1038 | 0.46784 | 7.3351 | -35.4258 | -35.8914 | 55.2563 | 76.5433 | 31.5833 | 68.0454 | 24.2907 | 56.3009 | 28.9112
42838.4323 | 1036 | 22.7529 | 22.7641 | 22.7555 | 22.6776 | 22.292 | 21.6159 | 22.6328 | 21.6732 | 22.2879 | 22.2938 | 22.2632 | 21.893 | 21.125 | 22.0955 | 21.4912 | 22.5842 | 23.8318 | 25.2983 | 44.2222 | 51.4023 | 84.8276 | 89.237 | 90.9897 | 26.1915 | 53.908 | 92.546 | 604.0537 | 626.9823 | 603.4458 | 25.0251 | 58.9904 | 98.7727 | 26.4064 | 56.5359 | 96.0135 | 717.2605 | 682.248 |  | 400.4388 | 702.3313 | 710.1708 | 655.7779 |  | 474.6196 | 707.423 | 635.305 | 834.71 | 952.5076 | 1027.6225 | 1056.1543 | 40.5244 | 291.1438 | 68.3354 | 527.9277 | 71.5984 | 51.0314 | 49.5925 | 55.4002 | 46.9723 |  |  | 0.68232 | 0.2871 | -110.7386 | 0.13335 | 7.8067 | -197.8098 | -184.4883 | -2.8825 | 11.0164 | 35.0613 | 12.0731 | 0.00027928 | -0.00013799 | 0.0004107 | 30.6449 | 22.2756 | 22.1035 | 22.1359 | 21.9379 | 21.2094 | 20.0706 | 22.1352 | 22.3116 | 22.3474 | 22.2881 | 21.8882 | 21.1316 | 22.2136 | 607.5707 | 471.0393 | 338.4381 | 254.4849 | 211.0432 | 716.6044 | 443.3177 | 22.2219 | 22.3686 | 23.6656 | 22.4097 | 38.0435 | 47.2101 | 29.4057 | 82.1674 | 88.0377 | 562.9266 | 503.0905 | 511.2988 | 523.7555 | 57.5814 | 25.3856 | 698.1055 | 22.1706 | 22.1396 | 352.3113 | 21.5296 | 21.9561 | 51.0274 | 89.1628 | 98.7478 | 26.2905 | 58.7613 | 100.514 | 696.7859 | 616.2201 | 720.1162 | 725.3573 | 683.4918 |  | 716.1663 | 675.1863 | 792.3416 | 567.8744 | 586.6627 | 677.3341 |  | 578.1784 |  |  | 451.3155 | 594.1081 | 669.9949 | [5 empty] | 21.8411 | 549.3722 | 22.0574 | 22.0495 | 404.6642 | 21.5161 | 21.8547 | 465.3453 | 588.9198 | 593.7789 |  | 705.639 | 835.0125 | 501.7295 | 666.8624 | 700.9737 | 550.6994 | 612.1966 | 624.6875 | 794.4105 | 603.5417 | 709.3051 | 1065.2925 | 1050.1215 | 942.6663 | 489.4317 | 589.0184 | 597.1735 | 503.5678 | 635.6309 | 704.6472 | 1073.9516 | 1010.6322 | 545.6754 | 629.7383 | 580.8603 | 787.2641 | 45.7095 | 0.0010722 | 19.5682 | 5.4838 | -28.4688 | 3.0965 | 6129.84 | -0.15 | 1.7044 | 1.1693 | -22.9645 | 0.7969 | 7.0226 | -35.3502 | -34.1391 | 55.2231 | 76.3317 | 31.5102 | 66.5266 | 26.5939 | 56.264 | 28.7937
42838.4323 | 1037 | 22.7641 | 22.7718 | 22.7723 | 22.6834 | 22.2921 | 21.6191 | 22.6373 | 21.6837 | 22.2945 | 22.3034 | 22.2654 | 21.9066 | 21.1224 | 22.1032 | 21.4968 | 22.5933 | 23.8475 | 25.3644 | 44.3228 | 51.5128 | 84.8518 | 89.2244 | 91.0116 | 26.2205 | 54.009 | 92.6108 | 602.9753 | 626.8101 | 602.1773 | 25.0634 | 59.0973 | 98.8193 | 26.4416 | 56.6303 | 96.0811 | 716.6998 | 681.2295 |  | 401.3509 | 699.3989 | 706.9132 | 654.4957 |  | 474.8163 | 707.823 | 634.5602 | 832.889 | 952.4887 | 1024.8668 | 1056.4821 | 40.9138 | 291.1276 | 68.5538 | 528.0587 | 71.6109 | 50.9989 | 49.5856 | 55.3971 | 47.0029 |  |  | 0.92216 | 0.054475 | -89.9895 | -1.7289 | 8.3948 | -197.8256 | -187.5097 | -2.9377 | 10.9286 | 35.6487 | 11.6454 | 0.00030885 | -9.857e-05 | 0.00037949 | 30.698 | 22.2777 | 22.0955 | 22.1392 | 21.9388 | 21.2054 | 20.0673 | 22.132 | 22.3073 | 22.3497 | 22.2872 | 21.8861 | 21.1269 | 22.2075 | 619.011 | 466.3013 | 343.5332 | 245.0462 | 200.2538 | 714.1592 | 440.8822 | 22.2338 | 22.3876 | 23.6957 | 22.4135 | 38.145 | 47.3065 | 29.4757 | 82.1993 | 88.0808 | 562.3272 | 503.3238 | 511.0166 | 524.7242 | 71.703 | 22.8413 | 699.0622 | 22.1721 | 22.1327 | 351.3709 | 21.5221 | 21.9396 | 51.1554 | 89.179 | 98.8153 | 26.3285 | 58.888 | 100.6032 | 697.6391 | 616.0164 | 717.7492 | 723.1393 | 682.8621 |  | 715.9825 | 674.6684 | 791.59 | 567.7457 | 586.4932 | 676.7363 |  | 577.0072 |  |  | 450.7469 | 594.547 | 669.3921 | [5 empty] | 21.8327 | 549.8649 | 22.0508 | 22.05 | 406.6997 | 21.5115 | 21.8531 | 464.6475 | 588.4181 | 593.6893 |  | 703.4325 | 834.0938 | 501.8888 | 666.7506 | 700.1916 | 549.501 | 612.1325 | 621.125 | 793.6172 | 605.0386 | 708.3967 | 1064.2541 | 1049.3087 | 942.8537 | 489.2268 | 588.3824 | 596.1646 | 502.9843 | 634.5671 | 703.7851 | 1073.0405 | 1012.2204 | 545.2333 |  | 580.6872 | 785.9235 | 45.8918 | 0.00050339 | 19.5679 | 5.5801 | -28.5124 | 3.0964 | 6124.58 | -0.14 | 1.98 | 0.50944 | -20.7058 | -2.87 | 7.2746 | -35.3141 | -34.381 | 55.1951 | 76.1193 | 31.4847 | 64.4481 | 25.5551 | 56.1606 | 28.6708
42838.4323 | 1038 | 22.7477 | 22.7646 | 22.7637 | 22.678 | 22.2938 | 21.6189 | 22.6277 | 21.6735 | 22.2855 | 22.2878 | 22.2602 | 21.8981 | 21.1158 | 22.097 | 21.4912 | 22.6037 | 23.8685 | 25.4298 | 44.4392 | 51.6098 | 84.873 | 89.2147 | 91.0114 | 26.2456 | 54.0932 | 92.6713 | 602.1376 | 627.0292 | 601.3377 | 25.0897 | 59.1995 | 98.8655 | 26.4798 | 56.7164 | 96.1342 | 716.5993 | 680.793 |  | 402.1666 | 698.7104 | 706.6505 | 657.9615 |  | 474.9579 | 707.954 | 634.6963 | 834.434 | 955.2126 | 1030.1284 | 1058.4574 | 40.75 | 291.2256 | 66.9632 | 527.92 | 71.6094 | 50.9586 | 49.5853 | 55.3969 | 47.0376 |  |  | 0.84265 | 0.56834 | -111.5225 | -4.7661 | 8.2358 | -197.825 | -191.2743 | -3.052 | 10.9356 | 35.4578 | 11.8974 | 0.00021356 | -0.00020042 | 0.00039591 | 30.761 | 22.2807 | 22.094 | 22.1345 | 21.9327 | 21.2062 | 20.0634 | 22.1317 | 22.3042 | 22.3452 | 22.2897 | 21.891 | 21.1212 | 22.2064 | 626.4579 | 468.8246 | 340.0151 | 244.9368 | 200.6663 | 712.4535 | 438.4328 | 22.2374 | 22.3892 | 23.7132 | 22.4227 | 38.2383 | 47.4002 | 29.5408 | 82.2162 | 88.1191 | 561.8858 | 505.0129 | 511.2826 | 526.2186 | 77.762 | 25.5861 | 700.0026 | 22.1745 | 22.1376 | 351.0633 | 21.5373 | 21.9604 | 51.3144 | 89.1958 | 98.8855 | 26.3675 | 59.0047 | 100.6926 | 697.5962 | 615.5437 | 716.7005 | 721.915 | 682.4516 |  | 715.8202 | 673.904 | 790.7753 | 567.3648 | 586.2223 | 676.0151 |  | 575.5114 |  |  | 450.949 | 594.4643 | 669.243 | [5 empty] | 21.8388 | 550.2813 | 22.0538 | 22.051 | 407.5737 | 21.5187 | 21.8592 | 464.0608 | 587.9405 | 593.4378 |  | 700.9068 | 833.1835 | 502.5486 | 666.7251 | 699.1559 | 548.641 | 611.723 | 617.6233 | 793.662 | 605.6467 | 707.1094 | 1059.9652 | 1050.206 | 943.5912 | 489.1926 | 587.9699 | 595.2099 | 502.5414 | 633.8878 | 703.2835 | 1076.7195 | 1012.0042 | 544.8356 |  | 580.5954 | 785.6503 | 45.0916 | 0.0007351 | 19.5685 | 5.683 | -28.5225 | 3.0964 | 6136.22 | -0.16 | 1.8918 | 1.6456 | -23.0519 | -4.7655 | 7.22 | -35.3856 | -34.7948 | 55.1664 | 75.8951 | 31.4487 | 63.0598 | 25.4726 | 56.0395 | 28.5586
42838.4323 | 1039 | 22.749 | 22.7609 | 22.7573 | 22.6805 | 22.2919 | 21.6121 | 22.6318 | 21.6745 | 22.2893 | 22.2908 | 22.258 | 21.9009 | 21.1148 | 22.0906 | 21.4907 | 22.6243 | 23.8889 | 25.4992 | 44.5458 | 51.7136 | 84.9085 | 89.2153 | 91.0363 | 26.2785 | 54.1876 | 92.7351 | 601.867 | 627.8895 | 601.302 | 25.1164 | 59.2786 | 98.9224 | 26.5224 | 56.7985 | 96.2009 | 716.6144 | 680.6079 |  | 402.3208 | 701.3444 | 710.2702 | 659.5017 |  | 476.0583 | 707.1568 | 634.3395 | 830.6276 | 955.9376 | 1035.785 | 1059.2515 | 39.9095 | 291.2238 | 65.6856 | 527.5529 | 71.6703 | 50.9297 | 49.5852 | 55.4287 | 47.0813 |  |  | 0.64946 | 0.74839 | -101.587 | -5.2898 | 7.0799 | -197.8499 | -167.7509 | -3.5534 | 10.837 | 35.6355 | 12.3 | 0.00025299 | -0.00017249 | 0.00040577 | 30.8235 | 22.2881 | 22.0939 | 22.1354 | 21.929 | 21.2112 | 20.0703 | 22.1362 | 22.3048 | 22.347 | 22.2881 | 21.8913 | 21.1209 | 22.1999 | 652.7357 | 478.4522 | 363.227 | 243.3155 | 195.4841 | 711.3142 | 436.1608 | 22.2261 | 22.3863 | 23.7258 | 22.4248 | 38.3309 | 47.4816 | 29.5927 | 82.2319 | 88.1423 | 561.3106 | 503.4672 | 509.9882 | 524.3496 | 72.2983 | 34.07 | 700.4588 | 22.1836 | 22.1336 | 350.6473 | 21.5373 | 21.9553 | 51.4543 | 89.1927 | 98.9447 | 26.4071 | 59.1244 | 100.8004 | 697.2764 | 615.1894 | 716.0731 | 721.3385 | 681.0078 |  | 715.5662 | 672.9757 | 789.9193 | 568.4494 | 586.0319 | 675.3414 |  | 574.8191 |  |  | 452.2533 | 593.6259 | 668.6275 | [5 empty] | 21.8336 | 550.675 | 22.0516 | 22.046 | 406.6869 | 21.5165 | 21.853 | 463.4247 | 587.5781 | 592.8384 |  | 699.7513 | 832.1523 | 502.3155 | 666.6946 | 698.1372 | 548.2797 | 610.5788 | 615.6877 | 793.5688 | 604.9961 | 706.2458 | 1059.1705 | 1053.1039 | 942.9194 | 489.1989 | 587.362 | 594.2538 | 501.9859 | 633.2463 | 702.8243 | 1077.3277 | 1012.1293 | 544.1688 | 1279.9676 | 580.6205 | 784.8765 | 44.1954 | 0.0012196 | 19.5684 | 5.7927 | -28.5703 | 3.0964 | 6170.39 | -0.08 | 1.6608 | 1.8876 | -21.9921 | -5.0184 | 6.7087 | -35.4645 | -32.6557 | 55.1438 | 75.6636 | 31.3859 | 59.7665 | 22.4563 | 56.0004 | 28.5187
42838.4323 | 1040 | 22.7475 | 22.7629 | 22.7644 | 22.6859 | 22.2878 | 21.6117 | 22.6368 | 21.6811 | 22.2931 | 22.2957 | 22.2555 | 21.9031 | 21.1213 | 22.0924 | 21.487 | 22.6305 | 23.9081 | 25.5652 | 44.6503 | 51.8184 | 84.9299 | 89.2106 | 91.0441 | 26.3087 | 54.2724 | 92.7871 | 601.6718 | 628.0947 | 601.2863 | 25.1528 | 59.3596 | 99.0465 | 26.5581 | 56.8935 | 96.2935 | 716.5845 | 680.8507 |  | 400.1848 | 705.3592 | 713.7127 | 659.4549 |  | 477.964 | 705.5885 | 632.3106 | 823.2117 | 955.4306 | 1036.3802 | 1057.8239 | 39.0769 | 291.347 | 64.7299 | 527.2037 | 71.6508 | 50.8843 | 49.5776 | 55.4229 | 47.1196 |  |  | 0.4405 | 0.73656 | -82.3611 | -5.8891 | 7.5602 | -197.7888 | -179.0651 | -3.0356 | 11.2849 | 36.4946 | 12.1389 | 0.0002612 | -0.00018235 | 0.00038934 | 30.8871 | 22.2921 | 22.0925 | 22.1292 | 21.9477 | 21.2078 | 20.0705 | 22.1374 | 22.3078 | 22.3402 | 22.2864 | 21.8878 | 21.1228 | 22.2095 | 647.2859 | 506.8981 | 405.3805 | 265.5906 | 203.5086 | 710.2645 | 434.7451 | 22.2163 | 22.3878 | 23.7393 | 22.4299 | 38.4309 | 47.5801 | 29.6587 | 82.2533 | 88.1792 | 560.4351 | 501.6642 | 507.5866 | 521.5642 | 75.6425 | 44.8692 | 699.147 | 22.181 | 22.1338 | 350.4424 | 21.5351 | 21.9561 | 51.5901 | 89.1784 | 99.011 | 26.4565 | 59.2385 | 100.9133 | 696.6278 | 615.2252 | 716.393 | 721.4897 | 680.7562 |  | 715.3832 | 672.3447 | 789.3336 | 573.4062 | 586.0784 | 674.8851 |  | 573.6722 |  |  | 453.2495 | 593.4385 | 668.3082 | [5 empty] | 21.8309 | 552.3983 | 22.0553 | 22.0544 | 405.9588 | 21.5197 | 21.8522 | 463.0617 | 587.349 | 591.9802 |  | 701.1257 | 832.665 | 502.5541 | 666.7309 | 697.393 | 548.0751 | 609.9306 | 613.3935 | 794.9422 | 605.1609 | 706.568 | 1059.0607 | 1053.2741 | 942.7559 | 489.094 | 586.2969 | 593.607 | 501.4687 | 632.8348 | 702.074 | 1079.4542 | 1012.3259 | 543.8333 |  | 580.2604 | 783.8484 | 45.0684 | -0.00027601 | 19.569 | 5.8947 | -28.4398 | 3.0964 | 6179.07 | -0.04 | 1.3677 | 1.8711 | -19.7861 | -5.2908 | 6.9341 | -35.4671 | -33.7466 | 55.1056 | 75.5054 | 31.2562 | 60.0286 | 17.501 | 55.9943 | 28.4566
42838.4323 | 1041 | 22.7474 | 22.7619 | 22.7661 | 22.6873 | 22.2859 | 21.6056 | 22.6356 | 21.6685 | 22.291 | 22.2884 | 22.2487 | 21.8935 | 21.1167 | 22.0941 | 21.4887 | 22.6356 | 23.9257 | 25.6327 | 44.7579 | 51.912 | 84.9443 | 89.1925 | 91.0562 | 26.3312 | 54.3424 | 92.8306 | 601.3516 | 627.906 | 601.0672 | 25.1898 | 59.4466 | 99.2056 | 26.5962 | 56.9839 | 96.3725 | 716.4355 | 682.7654 |  | 396.2147 | 706.3705 | 714.295 | 658.9076 |  | 478.6641 | 704.3994 | 632.0731 | 814.5918 | 951.21 | 1035.128 | 1056.2424 | 38.5108 | 291.5769 | 65.4237 | 527.007 | 71.7284 | 50.8563 | 49.5736 | 55.4112 | 47.1609 |  |  | 0.80388 | 0.55717 | -88.124 | -6.9188 | 8.1852 | -197.8072 | -154.7873 | -3.0461 | 10.8549 | 36.6121 | 12.0256 | 0.00021849 | -0.00015606 | 0.00039098 | 30.9435 | 22.2911 | 22.0891 | 22.1367 | 21.9287 | 21.1981 | 20.061 | 22.1272 | 22.2972 | 22.3308 | 22.2814 | 21.8866 | 21.1225 | 22.2035 | 657.4599 | 546.0547 | 462.3943 | 287.3402 | 216.5919 | 709.7508 | 434.4266 | 22.2277 | 22.401 | 23.7636 | 22.4397 | 38.5365 | 47.6854 | 29.7198 | 82.2851 | 88.2189 | 559.6163 | 499.7585 | 506.1723 | 520.4936 | 56.2781 | 25.5028 | 698.9416 | 22.1856 | 22.1456 | 350.1522 | 21.5378 | 21.958 | 51.7359 | 89.1221 | 99.0766 | 26.505 | 59.3563 | 101.0186 | 697.8474 | 615.2377 | 718.0905 | 722.7012 | 682.1204 |  | 715.3703 | 672.1142 | 788.9703 | 579.6211 | 586.3319 | 674.4075 |  | 572.7282 |  |  | 454.417 | 593.8413 | 669.0195 | [5 empty] | 21.8445 | 554.8184 | 22.0649 | 22.0534 | 405.9441 | 21.5259 | 21.8558 | 462.7238 | 587.214 | 591.1505 |  | 702.3438 | 835.1149 | 504.0987 | 667.3708 | 697.3779 | 547.6397 | 609.4958 | 610.3109 | 794.5012 | 607.4037 | 707.2057 | 1060.0052 | 1050.902 | 943.6694 | 488.9129 | 585.2004 | 592.9787 | 500.9017 | 632.1543 | 701.481 | 1080.5833 | 1012.1997 | 543.3358 |  | 579.6759 | 782.7587 | 45.8796 | 0.00013124 | 19.5687 | 5.9885 | -28.5505 | 3.0964 | 6175.98 | -0.05 | 1.8475 | 1.6264 | -20.4542 | -5.7313 | 7.2116 | -35.4518 | -31.3606 | 55.0645 | 75.4029 | 31.1271 | 58.7304 | 11.1052 | 55.9726 | 28.3562
42838.4323 | 1042 | 22.7491 | 22.763 | 22.7654 | 22.6826 | 22.2926 | 21.6061 | 22.6348 | 21.6705 | 22.2902 | 22.2881 | 22.2574 | 21.9013 | 21.1163 | 22.0991 | 21.5022 | 22.6569 | 23.9498 | 25.7133 | 44.8703 | 52.0179 | 84.9605 | 89.1969 | 91.0813 | 26.3688 | 54.4279 | 92.896 | 600.991 | 628.1412 | 600.8199 | 25.2158 | 59.5226 | 99.3611 | 26.6295 | 57.0682 | 96.4479 | 716.2838 | 682.2934 |  | 395.0245 | 703.0467 | 711.9195 | 659.5567 |  | 479.0082 | 704.5922 | 632.2266 | 813.7812 | 950.9181 | 1032.2402 | 1056.8175 | 38.8994 | 291.8144 | 63.8989 | 526.9825 | 71.7174 | 50.8431 | 49.5785 | 55.4203 | 47.2043 |  |  | 0.66129 | 0.39223 | -84.0853 | -8.3921 | 7.8993 | -197.8079 | -201.5141 | -2.5907 | 10.9985 | 35.9846 | 11.7889 | 0.0002957 | -0.00013471 | 0.00041234 | 31.0107 | 22.301 | 22.0936 | 22.1386 | 21.9394 | 21.2097 | 20.0709 | 22.1349 | 22.3057 | 22.3465 | 22.2851 | 21.8908 | 21.1272 | 22.212 | 635.4009 | 499.3255 | 414.4289 | 278.8695 | 215.7147 | 707.6152 | 432.7951 | 22.2196 | 22.4089 | 23.7736 | 22.4296 | 38.6318 | 47.7673 | 29.7792 | 82.3045 | 88.2405 | 558.8651 | 498.3327 | 504.5002 | 519.1731 | 49.3751 | 26.3264 | 700.101 | 22.1872 | 22.133 | 349.9678 | 21.535 | 21.9592 | 51.8779 | 89.0976 | 99.1409 | 26.5436 | 59.4719 | 101.1109 | 698.9892 | 615.3764 | 719.0736 | 723.3271 | 683.3258 |  | 715.4432 | 671.399 | 788.3014 | 584.2727 | 586.673 | 673.6496 |  | 572.1358 |  |  | 455.675 | 594.5001 | 670.6457 | [5 empty] | 21.8334 | 556.8585 | 22.057 | 22.0408 | 406.2765 | 21.5192 | 21.8482 | 462.2424 | 587.1 | 590.544 |  | 701.9512 | 834.8754 | 506.1741 | 668.0447 | 697.7624 | 547.0907 | 609.4026 | 607.715 | 793.1738 | 609.8726 | 707.1303 | 1063.9068 | 1053.8592 | 943.8961 | 488.3897 | 584.3663 | 592.2952 | 500.2516 | 631.5324 | 700.8092 | 1086.6412 | 1017.8796 | 542.817 |  | 579.138 | 782.0048 | 45.1925 | 0.00044722 | 19.5695 | 6.0746 | -28.4768 | 3.0964 | 6152.46 | -0.08 | 1.6754 | 1.3647 | -19.982 | -6.3127 | 7.0767 | -35.4127 | -35.7429 | 55.049 | 75.2226 | 31.0565 | 60.4856 | 16.1228 | 55.917 | 28.2737
42838.4323 | 1043 | 22.7566 | 22.7678 | 22.7591 | 22.6841 | 22.2863 | 21.6136 | 22.636 | 21.6834 | 22.29 | 22.2922 | 22.2538 | 21.9033 | 21.1194 | 22.0977 | 21.508 | 22.6794 | 23.9751 | 25.7865 | 44.9836 | 52.1289 | 84.9754 | 89.202 | 91.1013 | 26.4018 | 54.5206 | 92.9574 | 600.8255 | 628.4862 | 600.4892 | 25.264 | 59.6308 | 99.5036 | 26.6693 | 57.1603 | 96.5371 | 716.0483 | 681.3449 |  | 397.9899 | 700.5613 | 710.0062 | 659.7871 |  | 479.4537 | 705.842 | 632.7085 | 810.396 | 950.6126 | 1029.2685 | 1058.4351 | 39.5879 | 292.099 | 61.0283 | 526.8224 | 71.6332 | 50.8176 | 49.5724 | 55.4183 | 47.2297 |  |  | 0.88274 | 0.44809 | -86.8833 | -9.7516 | 8.2351 | -197.8164 | -146.852 | -2.6242 | 11.0357 | 36.6411 | 11.4372 | 0.00030885 | -0.00013799 | 0.0003992 | 31.0731 | 22.3027 | 22.0919 | 22.1402 | 21.9436 | 21.2047 | 20.0754 | 22.1302 | 22.304 | 22.3492 | 22.2859 | 21.8902 | 21.1321 | 22.2162 | 617.9119 | 466.2341 | 396.9974 | 264.3102 | 212.4668 | 704.7582 | 431.0294 | 22.2133 | 22.4047 | 23.7866 | 22.4325 | 38.7255 | 47.8514 | 29.8457 | 82.3214 | 88.2742 | 558.0882 | 497.8337 | 502.756 | 517.4855 | 55.9541 | 25.5648 | 699.0994 | 22.1954 | 22.135 | 349.2383 | 21.5384 | 21.9522 | 52.0196 | 89.0739 | 99.2117 | 26.5831 | 59.599 | 101.214 | 698.3516 | 615.8727 | 715.8771 | 720.6659 | 683.3382 |  | 715.4472 | 670.4402 | 787.554 | 586.1923 | 586.9662 | 672.9882 |  | 571.6772 |  |  | 456.8997 | 594.503 | 670.9824 | [5 empty] | 21.8327 | 558.5198 | 22.0653 | 22.0377 | 406.3462 | 21.5224 | 21.8483 | 461.7373 | 587.2848 | 590.2007 |  | 702.7135 | 834.3887 | 507.157 | 668.7466 | 697.6063 | 546.7942 | 609.5772 | 606.1663 | 793.0395 | 610.6625 | 706.8044 | 1070.8312 | 1065.5224 | 948.4421 | 487.7792 | 583.7579 | 591.692 | 499.735 | 630.7577 | 699.7177 | 1094.7476 | 1030.7122 | 542.4193 |  | 578.4603 | 781.2679 | 43.7977 | -0.00068325 | 19.5696 | 6.1591 | -28.5365 | 3.0963 | 6101.49 | -0.09 | 1.9353 | 1.4596 | -20.3247 | -6.8092 | 7.2173 | -35.3731 | -30.4777 | 55.0497 | 75.026 | 31.0536 | 61.5028 | 17.7231 | 55.8524 | 28.1976
42838.4324 | 1044 | 22.7427 | 22.7606 | 22.7565 | 22.6737 | 22.284 | 21.6084 | 22.6273 | 21.6732 | 22.2829 | 22.2937 | 22.2607 | 21.8968 | 21.1079 | 22.0934 | 21.5021 | 22.6861 | 23.9854 | 25.8546 | 45.0846 | 52.2318 | 84.9977 | 89.1935 | 91.1142 | 26.4276 | 54.6096 | 93.0122 | 600.5578 | 628.8048 | 599.8209 | 25.2895 | 59.7051 | 99.5971 | 26.7025 | 57.2525 | 96.598 | 715.9765 | 682.6689 |  | 398.4736 | 697.0438 | 706.4739 | 659.2838 |  | 479.8684 | 706.7186 | 632.548 | 811.2735 | 951.288 | 1031.5382 | 1061.092 | 40.3223 | 292.2856 | 60.0367 | 526.828 | 71.7835 | 50.7758 | 49.5681 | 55.4239 | 47.2708 |  |  | 0.96816 | 0.72802 | -89.2023 | -9.8962 | 7.1949 | -197.8572 | -190.6382 | -2.9646 | 10.5966 | 34.8131 | 11.8775 | 0.00016428 | -0.00023492 | 0.0003762 | 31.1286 | 22.3029 | 22.0921 | 22.1331 | 21.9397 | 21.2059 | 20.0742 | 22.1263 | 22.3069 | 22.3427 | 22.2857 | 21.8904 | 21.1249 | 22.2151 | 608.895 | 455.047 | 374.1944 | 252.3859 | 218.5489 | 702.4915 | 429.1572 | 22.2183 | 22.4167 | 23.8164 | 22.4446 | 38.8244 | 47.9459 | 29.9214 | 82.3407 | 88.3086 | 557.3081 | 497.1619 | 501.2701 | 516.0708 | 45.4905 | 19.4349 | 696.7857 | 22.1926 | 22.1273 | 349.2756 | 21.5352 | 21.941 | 52.1564 | 89.0663 | 99.255 | 26.6247 | 59.7204 | 101.2896 | 694.3595 | 616.2826 | 714.4292 | 719.5062 | 680.8074 |  | 715.2308 | 669.9907 | 787.0939 | 587.6391 | 587.2929 | 672.5242 |  | 570.8751 |  |  | 457.5732 | 594.1316 | 669.6768 | [5 empty] | 21.8357 | 560.2922 | 22.0728 | 22.0413 | 405.6212 | 21.529 | 21.8506 | 461.3847 | 587.6557 | 589.714 |  | 705.4721 | 836.0838 | 507.0028 | 669.2664 | 697.9741 | 547.1585 | 609.3261 | 605.5644 | 794.306 | 610.868 | 707.1196 | 1075.4276 | 1072.3332 | 956.2025 | 487.2456 | 583.3143 | 591.3237 | 499.3518 | 629.8911 | 699.6755 | 1097.4796 | 1039.2063 | 542.0503 |  | 577.884 | 780.4306 | 46.7036 | 0.00062276 | 19.5694 | 6.2327 | -28.5445 | 3.0964 | 6086.81 | -0.12 | 2.026 | 1.8613 | -20.6034 | -6.8625 | 6.752 | -35.4076 | -34.7556 | 55.0666 | 74.9012 | 31.0697 | 61.7737 | 19.901 | 55.8486 | 28.1138
42838.4324 | 1045 | 22.7477 | 22.7525 | 22.763 | 22.6751 | 22.2845 | 21.6113 | 22.6294 | 21.6769 | 22.2844 | 22.2933 | 22.2581 | 21.9004 | 21.1179 | 22.0937 | 21.4953 | 22.6943 | 24.0003 | 25.9156 | 45.1883 | 52.32 | 85.0174 | 89.1771 | 91.1197 | 26.4532 | 54.6848 | 93.0645 | 600.4941 | 629.0668 | 600.0559 | 25.3296 | 59.8094 | 99.7623 | 26.7558 | 57.3471 | 96.6885 | 715.9753 | 684.2326 |  | 399.9948 | 694.3623 | 703.5474 | 659.1433 |  | 480.6014 | 707.0057 | 632.7009 | 812.1466 | 947.5263 | 1028.1277 | 1061.1967 | 40.7589 | 292.4433 | 60.9911 | 526.4712 | 71.8398 | 50.7282 | 49.5593 | 55.4164 | 47.3034 |  |  | 0.70795 | 0.34886 | -86.8807 | -10.8845 | 8.2476 | -197.8243 | -151.3525 | -2.8161 | 10.5332 | 35.0917 | 11.7975 | 0.00028749 | -7.228e-05 | 0.00039756 | 31.1933 | 22.3099 | 22.0973 | 22.1397 | 21.9421 | 21.2107 | 20.0706 | 22.1328 | 22.3059 | 22.3428 | 22.2897 | 21.8924 | 21.1284 | 22.2144 | 594.5768 | 445.5106 | 346.4318 | 239.5836 | 208.8194 | 699.4047 | 426.8606 | 22.2113 | 22.4208 | 23.8261 | 22.4396 | 38.9327 | 48.0379 | 29.9808 | 82.3563 | 88.3364 | 556.414 | 494.7283 | 499.8045 | 514.95 | 42.0445 | 26.5462 | 697.1682 | 22.2029 | 22.125 | 349.0178 | 21.5321 | 21.9406 | 52.3015 | 89.0636 | 99.3237 | 26.6918 | 59.8417 | 101.362 | 693.2197 | 616.3284 | 713.5019 | 719.3119 | 680.6493 |  | 714.9964 | 669.7219 | 786.6648 | 588.3553 | 587.6803 | 671.9476 |  | 569.9203 |  |  | 457.346 | 593.5664 | 668.7857 | [5 empty] | 21.8332 | 561.4777 | 22.0679 | 22.05 | 404.338 | 21.5327 | 21.8545 | 461.4038 | 587.6743 | 589.2322 |  | 707.2057 | 838.5087 | 506.4799 | 669.5207 | 698.7532 | 547.969 | 608.8619 | 604.6106 | 795.6585 | 610.663 | 707.6121 | 1079.3487 | 1072.7457 | 961.4505 | 486.4349 | 583.1326 | 591.2064 | 498.97 | 629.4706 | 700.0718 | 1093.165 | 1039.4242 | 541.7287 |  | 577.5425 | 780.0211 | 48.827 | -0.00010047 | 19.5692 | 6.3139 | -28.5838 | 3.0964 | 6055.87 | -0.03 | 1.7327 | 1.2887 | -20.3365 | -7.1981 | 7.2196 | -35.3583 | -30.9276 | 55.0131 | 74.7808 | 31.1166 | 62.3746 | 22.551 | 55.8522 | 28.0041
42838.4324 | 1046 | 22.7536 | 22.7609 | 22.7636 | 22.6699 | 22.2848 | 21.6155 | 22.6318 | 21.6702 | 22.2926 | 22.2908 | 22.2556 | 21.8956 | 21.1159 | 22.0986 | 21.4964 | 22.7122 | 24.0317 | 25.9942 | 45.304 | 52.4302 | 85.0284 | 89.1771 | 91.1382 | 26.4879 | 54.7819 | 93.1361 | 600.8824 | 629.1755 | 601.1654 | 25.3537 | 59.8992 | 99.9286 | 26.7902 | 57.4356 | 96.7441 | 715.9395 | 685.0146 |  | 398.907 | 693.5564 | 702.6494 | 660.6515 |  | 480.0131 | 706.9187 | 635.3739 | 812.055 | 948.1122 | 1030.5932 | 1059.5027 | 41.1348 | 292.3309 | 63.4793 | 526.1382 | 71.8235 | 50.6545 | 49.5536 | 55.4105 | 47.3324 |  |  | 0.56667 | 0.86404 | -81.3373 | -11.9228 | 7.9118 | -197.8164 | -192.0188 | -3.2222 | 10.5285 | 35.0384 | 11.6785 | 0.00019549 | -0.0002497 | 0.00038277 | 31.2571 | 22.3141 | 22.1087 | 22.138 | 21.9418 | 21.2103 | 20.0722 | 22.1355 | 22.3117 | 22.3488 | 22.2885 | 21.8846 | 21.1268 | 22.2113 | 581.555 | 438.6404 | 360.4382 | 245.5239 | 207.9769 | 696.0924 | 425.1769 | 22.2172 | 22.4356 | 23.8557 | 22.4506 | 39.026 | 48.1408 | 30.0506 | 82.3812 | 88.3857 | 555.7904 | 496.9971 | 499.9697 | 516.0664 | 62.9576 | 26.4392 | 698.1814 | 22.2004 | 22.1367 | 348.9265 | 21.5385 | 21.9546 | 52.4339 | 89.0598 | 99.3789 | 26.7347 | 59.9732 | 101.4514 | 697.1388 | 616.5784 | 718.0275 | 723.2261 | 683.769 |  | 715.0822 | 669.568 | 786.4349 | 589.2552 | 587.9637 | 671.6198 |  | 569.5244 |  |  | 456.521 | 592.9549 | 669.8418 | [5 empty] | 21.8336 | 562.2287 | 22.0714 | 22.0538 | 403.4065 | 21.5352 | 21.8552 | 461.5683 | 587.4276 | 588.7936 |  | 707.2435 | 840.0143 | 505.747 | 669.2976 | 699.1784 | 548.367 | 608.6732 | 603.1998 | 795.9561 | 610.3225 | 707.306 | 1082.2473 | 1069.9578 | 962.9016 | 485.6568 | 583.3733 | 591.1393 | 498.3985 | 629.1323 | 701.0895 | 1091.0448 | 1036.8742 | 541.3094 |  | 576.8203 | 779.9297 | 46.3708 | -0.00017068 | 19.5636 | 6.388 | -28.6037 | 3.0964 | 6013.84 | -0.08 | 1.5512 | 2.028 | -19.6761 | -7.5333 | 7.0778 | -35.3911 | -34.8686 | 54.9476 | 74.7167 | 31.1405 | 62.7659 | 20.6772 | 55.8015 | 27.8752
42838.4324 | 1047 | 22.7567 | 22.7577 | 22.7637 | 22.6717 | 22.2876 | 21.6153 | 22.6272 | 21.6681 | 22.2898 | 22.2856 | 22.2555 | 21.9008 | 21.1191 | 22.0968 | 21.5024 | 22.7227 | 24.0525 | 26.0759 | 45.4047 | 52.5283 | 85.0398 | 89.1776 | 91.1452 | 26.5171 | 54.8768 | 93.1995 | 601.5607 | 629.0271 | 602.2382 | 25.3871 | 59.9898 | 100.0937 | 26.8233 | 57.5232 | 96.8159 | 715.8657 | 684.4259 |  | 398.6503 | 696.9677 | 705.3828 | 662.1113 |  | 480.0112 | 707.475 | 634.0601 | 814.5804 | 946.769 | 1033.6986 | 1055.9445 | 41.8378 | 292.1447 | 64.2568 | 525.6173 | 71.8437 | 50.5747 | 49.5329 | 55.4106 | 47.3469 |  |  | 0.87157 | 0.96655 | -79.7799 | -12.2671 | 8.0853 | -197.802 | -157.8179 | -2.8996 | 10.4958 | 34.9444 | 11.9089 | 0.00014292 | -0.0003417 | 0.00042056 | 31.3154 | 22.3007 | 22.0854 | 22.1242 | 21.9234 | 21.1981 | 20.0616 | 22.1289 | 22.2996 | 22.3397 | 22.2781 | 21.8716 | 21.1104 | 22.1939 | 593.0417 | 451.5854 | 360.4604 | 244.593 | 206.813 | 694.5003 | 423.4994 | 22.2227 | 22.4386 | 23.8783 | 22.4609 | 39.1186 | 48.2278 | 30.121 | 82.41 | 88.4278 | 555.2803 | 497.621 | 500.1759 | 517.0312 | 82.5339 | 35.54 | 699.7759 | 22.2085 | 22.1271 | 349.3871 | 21.5401 | 21.9489 | 52.5731 | 89.0731 | 99.4294 | 26.7856 | 60.1031 | 101.5303 | 701.2101 | 617.043 | 722.9612 | 726.7009 | 685.4289 |  | 715.1904 | 669.2771 | 786.3327 | 590.7317 | 588.2933 | 671.3228 |  | 569.2695 |  |  | 455.5746 | 592.8936 | 671.0609 | [5 empty] | 21.8304 | 563.1659 | 22.0728 | 22.048 | 403.6172 | 21.5349 | 21.852 | 461.6463 | 587.065 | 588.4166 |  | 705.3829 | 839.9559 | 504.8419 | 667.9085 | 699.2458 | 548.4207 | 608.3932 | 601.1899 | 795.3694 | 609.1024 | 705.1838 | 1083.5058 | 1069.3577 | 963.5491 | 485.2665 | 583.5874 | 591.0405 | 498.0298 | 628.9864 | 701.9539 | 1092.0578 | 1034.1225 | 541.0927 |  | 576.2489 | 779.7389 | 45.3325 | 0.0023923 | 19.5448 | 6.4589 | -28.6851 | 3.0964 | 5919.92 | -0.1 | 1.9249 | 2.1455 | -19.4924 | -7.6434 | 7.1635 | -35.4319 | -31.6488 | 54.9282 | 74.6944 | 31.1564 | 60.9847 | 20.3592 | 55.7427 | 27.7684
42838.4324 | 1048 | 22.7538 | 22.7564 | 22.7638 | 22.6697 | 22.2837 | 21.6101 | 22.622 | 21.6693 | 22.2852 | 22.2886 | 22.2545 | 21.8975 | 21.1133 | 22.0982 | 21.4972 | 22.7411 | 24.0669 | 26.1459 | 45.5102 | 52.6308 | 85.0558 | 89.1597 | 91.1528 | 26.543 | 54.9559 | 93.2575 | 602.0076 | 628.4779 | 602.5104 | 25.4266 | 60.0879 | 100.2449 | 26.8651 | 57.6134 | 96.8867 | 715.9183 | 683.9491 |  | 399.1226 | 705.3091 | 712.0682 | 663.8158 |  | 479.4631 | 706.8163 | 633.3207 | 813.9716 | 943.6634 | 1029.7487 | 1054.0884 | 41.4627 | 291.8831 | 65.3859 | 525.1452 | 71.8959 | 50.5277 | 49.522 | 55.4213 | 47.3822 |  |  | 0.96619 | 1.1729 | -76.9589 | -12.4038 | 7.7646 | -197.8112 | -186.8118 | -3.328 | 9.9691 | 33.8415 | 11.694 | 0.00011171 | -0.00024806 | 0.00037949 | 31.3792 | 22.3108 | 22.0885 | 22.1354 | 21.9384 | 21.1995 | 20.0661 | 22.1354 | 22.3077 | 22.348 | 22.2832 | 21.888 | 21.1173 | 22.2079 | 633.6404 | 505.6027 | 399.0604 | 251.0702 | 208.519 | 694.1984 | 422.1766 | 22.2212 | 22.4393 | 23.894 | 22.4619 | 39.2209 | 48.3162 | 30.196 | 82.4376 | 88.4663 | 554.732 | 496.6284 | 499.5913 | 516.7469 | 55.4898 | 31.1717 | 700.4063 | 22.2027 | 22.1364 | 349.5922 | 21.535 | 21.9459 | 52.719 | 89.0678 | 99.4854 | 26.827 | 60.2431 | 101.6156 | 702.2389 | 617.881 | 723.2913 | 727.0212 | 685.5653 |  | 715.1908 | 668.6009 | 785.9894 | 592.592 | 588.694 | 670.7177 |  | 568.9847 |  |  | 454.714 | 591.962 | 671.3407 | [5 empty] | 21.8354 | 564.5225 | 22.0774 | 22.0477 | 404.7494 | 21.5454 | 21.8563 | 461.6243 | 586.4012 | 588.3156 |  | 702.9975 | 839.6254 | 503.5522 | 665.5084 | 698.5328 | 548.4162 | 608.1414 | 599.3476 | 794.211 | 606.6076 | 702.887 | 1081.441 | 1068.0709 | 963.6778 | 485.2941 | 583.7499 | 591.1029 | 497.8901 | 629.3606 | 702.4821 | 1090.4882 | 1029.7187 | 540.8425 | 1299.6678 | 576.3787 | 779.1849 | 44.6664 | -0.00068325 | 19.5267 | 6.5275 | -28.4912 | 3.0964 | 5830.83 | -0.13 | 2.0271 | 2.3627 | -19.1382 | -7.6833 | 7.0094 | -35.3792 | -34.3815 | 54.9245 | 74.611 | 31.174 | 56.3782 | 15.8222 | 55.7083 | 27.6904
42838.4324 | 1049 | 22.7513 | 22.7641 | 22.7647 | 22.6741 | 22.2838 | 21.611 | 22.6268 | 21.6757 | 22.2852 | 22.2944 | 22.2571 | 21.9002 | 21.1132 | 22.0997 | 21.506 | 22.7577 | 24.1053 | 26.2175 | 45.6199 | 52.7315 | 85.0757 | 89.1635 | 91.1737 | 26.5879 | 55.0573 | 93.333 | 602.0504 | 627.972 | 602.3085 | 25.4618 | 60.1705 | 100.3914 | 26.8994 | 57.6996 | 96.9475 | 716.0382 | 682.3968 |  | 400.4259 | 710.5566 | 717.1087 | 665.6035 |  | 478.8395 | 705.7987 | 632.5663 | 816.1849 | 944.7156 | 1026.3618 | 1055.0053 | 40.5187 | 291.6473 | 66.7077 | 525.0895 | 71.9513 | 50.5006 | 49.5041 | 55.425 | 47.4143 |  |  | 0.79731 | 0.69122 | -91.1217 | -13.6431 | 7.5517 | -197.7993 | -203.1234 | -2.9252 | 10.0876 | 33.9686 | 11.8632 | 0.00013635 | -0.00022506 | 0.00038934 | 31.4397 | 22.314 | 22.0851 | 22.1306 | 21.9321 | 21.2039 | 20.0668 | 22.1324 | 22.298 | 22.3443 | 22.2863 | 21.8872 | 21.121 | 22.2095 | 627.3074 | 484.2147 | 399.1883 | 254.5795 | 205.9188 | 692.4337 | 420.8891 | 22.2187 | 22.4536 | 23.9073 | 22.4661 | 39.3171 | 48.4115 | 30.2674 | 82.4636 | 88.5109 | 554.3125 | 496.3142 | 499.7082 | 518.764 | 61.0093 | 22.2211 | 699.4052 | 22.2076 | 22.1327 | 349.1972 | 21.5451 | 21.9568 | 52.8542 | 89.0648 | 99.532 | 26.8782 | 60.3784 | 101.7049 | 701.352 | 618.4563 | 722.3174 | 726.0673 | 683.3083 |  | 714.9759 | 667.8926 | 785.3322 | 595.056 | 589.2259 | 670.1151 |  | 568.2937 |  |  | 454.9648 | 590.838 | 669.9769 | [5 empty] | 21.8368 | 566.5027 | 22.089 | 22.048 | 405.9638 | 21.5485 | 21.8612 | 461.6619 | 585.8182 | 588.1068 |  | 702.2467 | 838.682 | 501.828 | 662.6371 | 698.1811 | 548.3628 | 607.8256 | 599.9421 | 793.6301 | 603.8342 | 699.7069 | 1076.8778 | 1069.4537 | 963.3562 | 485.2865 | 583.7285 | 591.2947 | 497.5777 | 629.913 | 703.2003 | 1087.631 | 1034.8385 | 540.8176 |  | 576.4513 | 779.1882 | 46.8926 | 0.0005315 | 19.5096 | 6.5848 | -28.4932 | 3.0964 | 5726.19 | -0.18 | 1.8412 | 1.8128 | -20.8141 | -8.0538 | 6.9037 | -35.3321 | -35.8045 | 54.9342 | 74.4355 | 31.1976 | 56.5244 | 15.567 | 55.6883 | 27.5688
42838.4324 | 1050 | 22.7612 | 22.7641 | 22.7644 | 22.6848 | 22.2909 | 21.6116 | 22.6275 | 21.669 | 22.2894 | 22.2986 | 22.2662 | 21.9082 | 21.1212 | 22.1031 | 21.5051 | 22.7665 | 24.1201 | 26.2913 | 45.7266 | 52.8328 | 85.0905 | 89.1589 | 91.1835 | 26.6066 | 55.1549 | 93.3865 | 602.2227 | 627.4819 | 602.4277 | 25.4916 | 60.2683 | 100.5145 | 26.9309 | 57.7867 | 97.0115 | 716.1305 | 681.7248 |  | 401.2171 | 714.2617 | 721.5554 | 667.531 |  | 478.9192 | 704.1137 | 632.2038 | 815.8996 | 947.8053 | 1027.0133 | 1054.4996 | 39.6512 | 291.3979 | 67.2748 | 525.1626 | 71.9186 | 50.4885 | 49.4756 | 55.426 | 47.4673 |  |  | 0.75526 | 0.7773 | -95.5625 | -95.479 | 7.7219 | -197.8059 | -203.1963 | -3.121 | 10.1524 | 34.1801 | 11.9353 | 0.00022671 | -0.00036306 | 0.00036799 | 31.504 | 22.32 | 22.092 | 22.1304 | 21.9301 | 21.2054 | 20.0635 | 22.1265 | 22.297 | 22.3393 | 22.2834 | 21.8853 | 21.1245 | 22.2049 | 633.3638 | 484.9609 | 373.1415 | 249.8351 | 200.2911 | 690.7727 | 419.2824 | 22.2269 | 22.4668 | 23.9381 | 22.4861 | 39.4312 | 48.5144 | 30.3591 | 82.4992 | 88.5679 | 553.9835 | 497.6972 | 501.6856 | 521.5255 | 52.2083 | 22.607 | 698.0462 | 22.2319 | 22.1439 | 348.9735 | 21.5523 | 21.963 | 52.9983 | 89.0607 | 99.5993 | 26.9301 | 60.5182 | 101.7803 | 702.3122 | 618.6922 | 721.3853 | 724.6102 | 682.1293 |  | 714.7015 | 667.4954 | 784.8678 | 597.8459 | 589.8441 | 669.7459 |  | 567.2549 |  |  | 456.0337 | 589.1306 | 668.6242 | [5 empty] | 21.8392 | 568.6751 | 22.0917 | 22.0521 | 406.5361 | 21.552 | 21.8478 | 461.7089 | 585.4113 | 587.9241 |  | 703.8511 | 838.5479 | 500.2944 | 659.8618 | 697.509 | 548.384 | 607.457 | 601.0918 | 793.7717 | 601.5189 | 697.5948 | 1078.1274 | 1069.4062 | 964.9912 | 485.3052 | 583.5278 | 591.4819 | 497.3684 | 629.9945 | 703.2221 | 1092.1948 | 1035.1906 | 540.6004 |  | 576.295 | 778.894 | 45.4164 | -0.00029004 | 19.4947 | 6.64 | -28.5141 | 3.0964 | 5628.54 | -0.1 | 1.7921 | 1.9207 | -21.2969 | -21.2876 | 6.9828 | -35.3415 | -35.8199 | 54.8993 | 74.3089 | 31.2273 | 55.3287 | 18.1612 | 55.6576 | 27.4407
42838.4324 | 1051 | 22.7451 | 22.7576 | 22.7569 | 22.6685 | 22.2854 | 21.6135 | 22.6305 | 21.6705 | 22.2772 | 22.2902 | 22.2606 | 21.8908 | 21.119 | 22.0977 | 21.5103 | 22.7878 | 24.1477 | 26.3676 | 45.8279 | 52.9352 | 85.1104 | 89.1572 | 91.2073 | 26.6438 | 55.2472 | 93.4517 | 602.0643 | 627.1303 | 602.2458 | 25.5302 | 60.3666 | 100.6617 | 26.977 | 57.879 | 97.0807 | 716.1477 | 682.5558 |  | 377.0526 | 712.1318 | 719.8089 | 666.8702 |  | 480.3839 | 702.3472 | 631.6645 | 808.9543 | 942.9782 | 1028.1764 | 1052.7651 | 39.1092 | 291.2606 | 67.7631 | 525.162 | 71.8394 | 50.4614 | 49.4484 | 55.4223 | 47.5074 |  |  | 0.69349 | 1.1604 | -107.7698 | -98.1942 | 6.8749 | -197.8611 | -203.2942 | -2.8555 | 10.1216 | 33.583 | 11.9393 | 0.00026613 | -0.00019549 | 0.0003762 | 31.5764 | 22.3374 | 22.098 | 22.1366 | 21.9377 | 21.2143 | 20.0716 | 22.1391 | 22.3078 | 22.3477 | 22.2888 | 21.8891 | 21.1282 | 22.2106 | 617.8714 | 472.7211 | 350.5598 | 245.6729 | 198.018 | 688.3915 | 417.3919 | 22.2237 | 22.4668 | 23.9562 | 22.4806 | 39.5243 | 48.6047 | 30.4369 | 82.5351 | 88.5963 | 553.8289 | 501.4062 | 505.0266 | 524.1083 | 47.3476 | 24.1417 | 698.1605 | 22.2336 | 22.1413 | 348.7193 | 21.5466 | 21.9579 | 53.1295 | 89.0435 | 99.6524 | 26.9859 | 60.662 | 101.8663 | 702.5194 | 618.6107 | 718.6345 | 722.1587 | 682.1154 |  | 714.4596 | 667.3291 | 784.6976 | 598.9118 | 590.4532 | 669.4208 |  | 566.8786 |  |  | 454.7594 | 588.1569 | 667.4571 | [5 empty] | 21.8369 | 570.1518 | 22.102 | 22.047 | 406.9593 | 21.5566 | 21.8571 | 461.752 | 584.9972 | 587.5682 |  | 703.8475 | 837.8254 | 499.2801 | 658.3123 | 696.7653 | 548.2011 | 607.9005 | 600.8057 | 793.5703 | 599.4312 | 697.3795 | 1080.2643 | 1072.4553 | 964.3316 | 485.6338 | 583.3054 | 591.5234 | 497.012 | 630.387 | 704.0228 | 1096.3323 | 1038.9409 | 540.3832 |  | 576.2758 | 779.5529 | 46.4869 | -0.00021983 | 19.4808 | 6.692 | -28.5194 | 3.0964 | 5555.52 | -0.09 | 1.7171 | 2.3447 | -22.5958 | -21.5686 | 6.5916 | -35.3623 | -35.8445 | 54.8401 | 74.263 | 31.3035 | 56.3036 | 20.3185 | 55.6802 | 27.3448
42838.4325 | 1052 | 22.7483 | 22.7564 | 22.7589 | 22.6744 | 22.2864 | 21.6123 | 22.6335 | 21.6702 | 22.286 | 22.3001 | 22.2567 | 21.8967 | 21.116 | 22.0917 | 21.5141 | 22.7937 | 24.1619 | 26.4391 | 45.9325 | 53.0339 | 85.1274 | 89.1554 | 91.2116 | 26.6719 | 55.3407 | 93.5008 | 602.4609 | 627.4992 | 602.8394 | 25.563 | 60.4462 | 100.7611 | 27.0192 | 57.9712 | 97.1354 | 716.3627 | 684.1315 |  | 381.5168 | 707.6302 | 715.9742 | 667.9779 |  | 481.227 | 702.2042 | 631.7572 | 801.1184 | 939.2752 | 1027.055 | 1051.7712 | 38.9182 | 291.2318 | 65.938 | 524.6912 | 71.8737 | 50.4389 | 49.4133 | 55.4035 | 47.5676 |  |  | 0.79403 | 0.88967 | -79.2201 | -66.1992 | 7.1226 | -197.8368 | -203.2272 | -3.031 | 9.9459 | 33.2167 | 12.1113 | 5.914e-05 | -0.00026777 | 0.00035649 | 31.6361 | 22.3397 | 22.0968 | 22.1367 | 21.9427 | 21.2088 | 20.0727 | 22.1393 | 22.3109 | 22.3489 | 22.2949 | 21.8931 | 21.1258 | 22.2169 | 607.8757 | 457.9125 | 345.9937 | 230.1484 | 190.5559 | 685.8323 | 415.3402 | 22.2258 | 22.4747 | 23.9859 | 22.4894 | 39.6216 | 48.6995 | 30.5336 | 82.5807 | 88.6299 | 553.6624 | 503.7041 | 507.0541 | 524.8735 | 55.2185 | 20.3511 | 699.729 | 22.2302 | 22.1448 | 349.6652 | 21.5371 | 21.9453 | 53.2594 | 89.0229 | 99.7056 | 27.0214 | 60.8015 | 101.94 | 701.9133 | 618.6846 | 718.5472 | 722.0453 | 682.2133 |  | 714.2438 | 666.9189 | 784.397 | 599.6588 | 591.0418 | 669.0738 |  | 566.6543 |  |  | 454.7582 | 587.5768 | 667.5421 | [5 empty] | 21.8388 | 571.1578 | 22.11 | 22.0544 | 407.7628 | 21.5615 | 21.8513 | 461.879 | 585.5485 | 587.1906 |  | 702.2037 | 837.5604 | 498.4522 | 657.2239 | 696.399 | 548.5782 | 608.299 | 599.6901 | 791.7866 | 598.3867 | 696.9288 | 1080.8874 | 1076.5766 | 965.6909 | 485.8092 | 583.0713 | 591.5013 | 496.5219 | 631.1365 | 705.0523 | 1095.5191 | 1043.0914 | 540.1172 |  | 576.818 | 779.2625 | 43.5658 | -0.0033585 | 19.4686 | 6.7364 | -28.4914 | 3.0964 | 5535.48 | -0.02 | 1.838 | 2.0529 | -19.3716 | -17.7082 | 6.7064 | -35.3449 | -35.8232 | 54.7843 | 74.1854 | 31.3851 | 56.6159 | 20.4453 | 55.7027 | 27.2976
42838.4325 | 1053 | 22.752 | 22.7589 | 22.7602 | 22.6783 | 22.2904 | 21.6112 | 22.6315 | 21.6711 | 22.2943 | 22.2944 | 22.263 | 21.9016 | 21.1173 | 22.0952 | 21.5079 | 22.8127 | 24.1898 | 26.5183 | 46.0367 | 53.1301 | 85.1379 | 89.1613 | 91.2309 | 26.7003 | 55.423 | 93.5668 | 602.9327 | 628.4367 | 603.536 | 25.6 | 60.538 | 100.8377 | 27.0571 | 58.0587 | 97.184 | 716.9195 | 685.0175 |  | 395.7296 | 704.955 | 713.8834 | 672.0356 |  | 480.9283 | 702.3565 | 629.8473 | 799.1658 | 935.4351 | 1023.3959 | 1049.8164 | 39.1084 | 291.1821 | 63.5858 | 523.8639 | 71.9257 | 50.4014 | 49.4038 | 55.3946 | 47.6097 |  |  | 0.74869 | 0.46123 | -89.6202 | -59.9658 | 6.9531 | -197.7652 | -203.22 | -2.7563 | 10.0492 | 32.9133 | 11.9941 | 0.00013142 | -0.00016263 | 0.00034334 | 31.7034 | 22.3431 | 22.0988 | 22.139 | 21.9376 | 21.2053 | 20.0755 | 22.145 | 22.3114 | 22.3519 | 22.2943 | 21.8958 | 21.131 | 22.2149 | 608.557 | 453.9896 | 334.2307 | 225.2428 | 187.1564 | 683.7854 | 413.1777 | 22.2226 | 22.4787 | 24.0033 | 22.4922 | 39.7175 | 48.7841 | 30.6168 | 82.6113 | 88.6671 | 553.4581 | 504.8398 | 507.983 | 524.6491 | 52.5457 | 25.3242 | 701.0551 | 22.2372 | 22.1331 | 350.0036 | 21.5396 | 21.9459 | 53.3913 | 89.0003 | 99.7585 | 27.0691 | 60.9429 | 102.0132 | 701.0366 | 618.5137 | 722.4005 | 725.6855 | 681.0426 |  | 713.9832 | 666.6794 | 784.2775 | 600.8188 | 591.6282 | 668.9915 |  | 566.5133 |  |  | 453.4791 | 586.0994 | 666.9616 | [5 empty] | 21.8298 | 572.4494 | 22.1046 | 22.0468 | 407.7247 | 21.5502 | 21.8485 | 462.0424 | 586.0165 | 587.0593 |  | 700.0499 | 838.5443 | 498.099 | 656.5375 | 696.4091 | 549.1693 | 608.5216 | 598.2139 | 790.1217 | 598.5131 | 697.7468 | 1081.7471 | 1079.3448 | 968.2222 | 485.7224 | 582.6247 | 591.6735 | 496.4706 | 631.8379 | 704.668 | 1098.5464 | 1043.4094 | 539.8957 |  | 577.6359 | 778.3829 | 44.3496 | -0.00046561 | 19.4574 | 6.7706 | -28.5417 | 3.0964 | 5509.25 | -0.08 | 1.7854 | 1.4782 | -20.6056 | -16.8552 | 6.6168 | -35.2887 | -35.7721 | 54.7527 | 74.1567 | 31.4551 | 55.9046 | 21.3527 | 55.7279 | 27.2719
42838.4325 | 1054 | 22.7544 | 22.757 | 22.7559 | 22.6765 | 22.2895 | 21.608 | 22.6324 | 21.677 | 22.2948 | 22.2954 | 22.2678 | 21.9014 | 21.1227 | 22.0977 | 21.5034 | 22.8146 | 24.2063 | 26.5819 | 46.1297 | 53.224 | 85.1577 | 89.1482 | 91.2369 | 26.7264 | 55.499 | 93.6195 | 602.981 | 629.3807 | 603.5113 | 25.6333 | 60.6232 | 100.9201 | 27.0946 | 58.1435 | 97.2471 | 717.6777 | 685.13 |  | 383.9041 | 703.974 | 713.0875 | 671.5587 |  | 480.2061 | 702.0852 | 628.2538 | 797.3382 | 931.9293 | 1021.5803 | 1046.2976 | 39.549 | 290.9038 | 62.1183 | 522.9235 | 71.9626 | 50.3614 | 49.3757 | 55.3931 | 47.6459 |  |  | 0.77497 | 1.0756 | -104.6892 | -56.6691 | 7.9677 | -197.8118 | -203.2752 | -3.1085 | 10.0177 | 32.9769 | 12.0108 | 0.00021849 | -0.00025299 | 0.00038606 | 31.7602 | 22.3419 | 22.0931 | 22.1394 | 21.9332 | 21.2046 | 20.0669 | 22.1324 | 22.2978 | 22.3474 | 22.2898 | 21.886 | 21.1254 | 22.2083 | 603.13 | 448.3739 | 342.9747 | 235.5149 | 189.1327 | 681.4931 | 411.1858 | 22.2231 | 22.4967 | 24.0335 | 22.5072 | 39.8239 | 48.8873 | 30.7223 | 82.6504 | 88.7146 | 553.2409 | 505.9381 | 508.9509 | 524.8012 | 52.3904 | 17.189 | 702.3804 | 22.2426 | 22.1404 | 350.3407 | 21.5467 | 21.9481 | 53.5349 | 89.0052 | 99.8265 | 27.1184 | 61.1005 | 102.1021 | 700.429 | 618.332 | 729.4438 | 732.0649 | 680.3246 |  | 713.7735 | 666.5252 | 784.4175 | 600.9792 | 592.1927 | 669.6322 |  | 566.2463 |  |  | 452.3447 | 584.1821 | 666.2163 | [5 empty] | 21.8274 | 573.0278 | 22.099 | 22.042 | 406.9733 | 21.5518 | 21.8482 | 462.3592 | 586.1204 | 586.9233 |  | 697.905 | 837.7522 | 498.2711 | 657.063 | 696.8552 | 549.5078 | 609.1452 | 595.9823 | 787.6093 | 598.6424 | 698.5141 | 1083.8055 | 1076.7265 | 968.0497 | 485.4651 | 582.0081 | 591.8233 | 496.8503 | 632.847 | 705.3896 | 1093.2816 | 1040.7413 | 539.4666 |  | 578.4782 | 778.0808 | 43.7346 | -3.0266e-05 | 19.4477 | 6.7945 | -28.6009 | 3.0964 | 5478.3 | -0.11 | 1.8165 | 2.2571 | -22.2676 | -16.383 | 7.0782 | -35.2682 | -35.7519 | 54.721 | 74.2024 | 31.5492 | 55.799 | 20.0144 | 55.9293 | 27.2339
42838.4325 | 1055 | 22.7527 | 22.7605 | 22.757 | 22.6799 | 22.2873 | 21.6086 | 22.6329 | 21.6724 | 22.2857 | 22.2935 | 22.2619 | 21.9004 | 21.1208 | 22.0993 | 21.5095 | 22.8286 | 24.2248 | 26.6608 | 46.2359 | 53.3259 | 85.1731 | 89.1424 | 91.2515 | 26.7582 | 55.591 | 93.6698 | 603.3836 | 630.1665 | 604.0909 | 25.6736 | 60.712 | 101.0301 | 27.1369 | 58.2292 | 97.315 | 717.7628 | 685.2438 |  | 366.8012 | 700.1918 | 709.6559 | 664.7433 |  | 480.0896 | 700.7688 | 628.0022 | 797.1985 | 935.9309 | 1018.4992 | 1043.7402 | 39.1523 | 290.7212 | 62.1194 | 522.1958 | 71.9425 | 50.3261 | 49.3511 | 55.4005 | 47.6729 |  |  | 0.89391 | 0.14253 | -82.5865 | -52.8499 | 7.2547 | -197.819 | -203.1635 | -3.1197 | 10.0479 | 33.4282 | 12.0405 | 2.793e-05 | -0.00030063 | 0.00035484 | 31.8245 | 22.3399 | 22.0857 | 22.1298 | 21.928 | 21.195 | 20.063 | 22.128 | 22.3057 | 22.3378 | 22.279 | 21.8818 | 21.1219 | 22.2017 | 579.2168 | 437.4673 | 317.5808 | 235.2522 | 187.9438 | 678.7981 | 409.1063 | 22.2259 | 22.4979 | 24.0475 | 22.5103 | 39.9243 | 48.9763 | 30.8115 | 82.6762 | 88.7424 | 552.9752 | 504.9263 | 508.4867 | 523.5392 | 57.3773 | 25.9427 | 703.4383 | 22.2458 | 22.1331 | 349.7066 | 21.5461 | 21.9459 | 53.66 | 88.9985 | 99.8895 | 27.1658 | 61.2566 | 102.1739 | 699.9416 | 618.4137 | 730.6848 | 732.88 | 679.587 |  | 713.5469 | 665.9054 | 784.3568 | 601.43 | 592.865 | 669.4985 |  | 566.1476 |  |  | 451.6755 | 582.7872 | 666.5982 | [5 empty] | 21.8296 | 573.8436 | 22.1128 | 22.0446 | 407.0407 | 21.5588 | 21.8515 | 462.3991 | 586.4234 | 587.3679 |  | 695.2826 | 836.2808 | 498.8325 | 657.7325 | 696.7582 | 549.6538 | 609.8669 | 594.6072 | 786.1625 | 599.7248 | 699.0175 | 1084.9132 | 1070.6776 | 967.2037 | 485.1872 | 581.3418 | 591.7534 | 497.1724 | 633.3796 | 706.5954 | 1093.8217 | 1037.7124 | 539.0537 |  | 578.906 | 777.4223 | 43.4801 | 0.00022955 | 19.4403 | 6.8233 | -28.5359 | 3.0964 | 5444.98 | -0.03 | 1.9515 | 0.82106 | -19.7644 | -15.8107 | 6.746 | -35.2268 | -35.6995 | 54.6859 | 74.2017 | 31.6543 | 57.6271 | 22.4545 | 56.1397 | 27.2276
42838.4325 | 1056 | 22.7415 | 22.7596 | 22.7522 | 22.6793 | 22.2829 | 21.6113 | 22.6231 | 21.6711 | 22.2836 | 22.2891 | 22.2562 | 21.8948 | 21.1117 | 22.0959 | 21.5087 | 22.8479 | 24.2452 | 26.7394 | 46.3397 | 53.4133 | 85.1797 | 89.1334 | 91.2623 | 26.7911 | 55.687 | 93.7219 | 604.1888 | 630.3106 | 604.9804 | 25.7097 | 60.8021 | 101.1247 | 27.1751 | 58.3115 | 97.3695 | 717.2488 | 685.7279 |  | 371.6639 | 698.2126 | 707.4572 | 659.6918 |  | 479.4919 | 699.4688 | 627.3882 | 799.6439 | 940.1182 | 1015.727 | 1044.8739 | 37.6046 | 290.578 | 63.9677 | 521.8056 | 72.0483 | 50.2763 | 49.3213 | 55.4038 | 47.7161 |  |  | 0.86434 | 0.11953 | -80.5297 | -50.0933 | 7.7436 | -197.8677 | -203.264 | -2.7024 | 9.8959 | 33.2062 | 11.8448 | 7.721e-05 | -0.00022342 | 0.00037456 | 31.9097 | 22.3535 | 22.1045 | 22.1369 | 21.9418 | 21.2053 | 20.0763 | 22.1442 | 22.316 | 22.3522 | 22.2889 | 21.8963 | 21.1333 | 22.2212 | 568.5782 | 442.6454 | 318.5626 | 233.3646 | 187.9133 | 676.8647 | 407.3223 | 22.2237 | 22.5089 | 24.0693 | 22.514 | 40.0222 | 49.06 | 30.8992 | 82.6857 | 88.7703 | 552.4622 | 501.5557 | 505.8056 | 519.9187 | 55.1561 | 28.6438 | 701.7244 | 22.2413 | 22.1276 | 349.1929 | 21.5446 | 21.9473 | 53.7866 | 89.0014 | 99.9401 | 27.2094 | 61.4072 | 102.2539 | 698.6497 | 618.4675 | 725.8014 | 728.7999 | 678.9519 |  | 713.2953 | 665.0713 | 783.8719 | 603.2565 | 593.5448 | 668.9521 |  | 566.425 |  |  | 452.1157 | 581.5553 | 665.9517 | [5 empty] | 21.8411 | 575.0796 | 22.1196 | 22.051 | 407.2692 | 21.5655 | 21.8667 | 462.2452 | 587.0592 | 587.4522 |  | 694.9925 | 836.2195 | 499.8573 | 658.5892 | 696.9319 | 549.9601 | 610.4511 | 594.6705 | 787.6407 | 601.7705 | 700.0449 | 1088.847 | 1070.6129 | 968.3859 | 485.073 | 581.0245 | 592.1825 | 497.4375 | 633.0859 | 706.3684 | 1098.7589 | 1038.5627 | 538.991 | 1308.477 | 578.9648 | 776.9912 | 44.6976 | -0.00024088 | 19.4346 | 6.8473 | -28.5119 | 3.0964 | 5400.96 | -0.1 | 1.9199 | 0.75141 | -19.5037 | -15.3825 | 6.9622 | -35.1933 | -35.67 | 54.6417 | 74.0814 | 31.7227 | 58.2172 | 22.0191 | 56.1524 | 27.2483
42838.4325 | 1057 | 22.7432 | 22.7574 | 22.7582 | 22.6768 | 22.285 | 21.6138 | 22.6319 | 21.6705 | 22.2885 | 22.2901 | 22.2562 | 21.8994 | 21.1134 | 22.0912 | 21.5125 | 22.8636 | 24.272 | 26.8121 | 46.4485 | 53.5117 | 85.1897 | 89.1281 | 91.2745 | 26.8223 | 55.7762 | 93.7822 | 604.4839 | 630.2176 | 605.2936 | 25.7374 | 60.8833 | 101.2014 | 27.2144 | 58.4001 | 97.4229 | 717.0017 | 688.0687 |  | 374.6646 | 698.2647 | 706.2639 | 662.5332 |  | 479.5038 | 698.9155 | 626.0397 | 797.3535 | 936.675 | 1014.3456 | 1042.9094 | 37.4008 | 290.5047 | 64.3234 | 521.6399 | 72.0622 | 50.2025 | 49.2958 | 55.4064 | 47.7414 |  |  | 0.94188 | 0.14253 | -84.6268 | -49.2686 | 7.5287 | -197.8677 | -203.2292 | -2.8733 | 10.0222 | 32.8049 | 11.5013 | 7.393e-05 | -0.00027927 | 0.00038113 | 31.9609 | 22.354 | 22.0993 | 22.1357 | 21.9302 | 21.2076 | 20.0776 | 22.1407 | 22.3073 | 22.3487 | 22.2932 | 21.8896 | 21.1302 | 22.2099 | 581.3867 | 453.3416 | 341.785 | 226.8022 | 185.9049 | 675.1446 | 405.7686 | 22.212 | 22.5037 | 24.0853 | 22.5084 | 40.1041 | 49.1425 | 30.9761 | 82.6841 | 88.7948 | 551.8741 | 500.1201 | 504.2035 | 517.7428 | 52.402 | 32.1235 | 698.5994 | 22.2623 | 22.1462 | 349.3254 | 21.5543 | 21.9542 | 53.9284 | 89.0174 | 100.0168 | 27.2693 | 61.5779 | 102.3449 | 697.4668 | 618.1702 | 719.6092 | 723.8817 | 679.3035 |  | 713.1226 | 664.6738 | 783.6705 | 603.4483 | 594.1266 | 667.8707 |  | 566.4794 |  |  | 452.9183 | 581.1014 | 666.3721 | [5 empty] | 21.8382 | 575.7914 | 22.1179 | 22.0439 | 407.0786 | 21.5711 | 21.8599 | 462.249 | 587.5536 | 587.6075 |  | 696.0354 | 838.3913 | 500.9897 | 659.7566 | 697.9127 | 550.1899 | 610.8839 | 594.9427 | 789.9796 | 601.7034 | 701.4392 | 1093.7667 | 1073.8452 | 973.0981 | 484.9072 | 580.8336 | 592.6738 | 497.4947 | 632.4705 | 706.4316 | 1101.5491 | 1042.4567 | 539.1475 |  | 579.0409 | 776.7788 | 46.1615 | 0.001676 | 19.4284 | 6.8695 | -28.6066 | 3.0964 | 5362.75 | -0.05 | 2.0046 | 0.82028 | -19.988 | -15.2511 | 6.8612 | -35.1744 | -35.6478 | 54.5896 | 74.0329 | 31.8195 | 56.2693 | 19.1556 | 56.0122 | 27.2175
42838.4325 | 1058 | 22.7458 | 22.7567 | 22.7546 | 22.6764 | 22.2853 | 21.6166 | 22.629 | 21.679 | 22.2889 | 22.2918 | 22.2623 | 21.8982 | 21.1162 | 22.0964 | 21.5116 | 22.8753 | 24.2878 | 26.8835 | 46.5522 | 53.6135 | 85.2053 | 89.1255 | 91.2942 | 26.8509 | 55.8623 | 93.8377 | 604.7124 | 630.3187 | 605.5808 | 25.7853 | 60.9742 | 101.284 | 27.2516 | 58.4868 | 97.4713 | 717.3132 | 686.6678 |  | 373.6152 | 695.921 | 703.5665 | 665.7916 |  | 478.4735 | 698.3609 | 624.2916 | 798.1168 | 935.5797 | 1014.8559 | 1037.4236 | 37.8967 | 290.4354 | 63.0025 | 521.1788 | 72.1118 | 50.1433 | 49.2598 | 55.4082 | 47.7609 |  |  | 0.82951 | 0.46911 | -82.3118 | -51.3162 | 7.534 | -197.8545 | -203.2082 | -2.7018 | 9.7824 | 32.6528 | 11.6344 | -5.914e-05 | -0.00027599 | 0.00040577 | 32.0294 | 22.3569 | 22.0955 | 22.1337 | 21.9347 | 21.2042 | 20.0777 | 22.1411 | 22.3055 | 22.3462 | 22.2923 | 21.8882 | 21.129 | 22.2113 | 578.1248 | 465.5506 | 375.9083 | 233.6108 | 179.1524 | 673.0568 | 404.5575 | 22.2168 | 22.5142 | 24.1008 | 22.512 | 40.1948 | 49.231 | 31.0537 | 82.6999 | 88.8269 | 551.4516 | 500.4184 | 504.4153 | 518.2949 | 54.2856 | 25.5355 | 698.3335 | 22.2516 | 22.1442 | 349.6229 | 21.5495 | 21.9496 | 54.0595 | 89.0069 | 100.0691 | 27.3215 | 61.7424 | 102.4123 | 698.994 | 618.0576 | 715.0216 | 720.5697 | 681.716 |  | 713.1517 | 664.9567 | 783.8481 | 601.3831 | 594.6051 | 667.7558 |  | 566.2625 |  |  | 452.6835 | 581.7678 | 668.5216 | [5 empty] | 21.8423 | 575.6873 | 22.1314 | 22.0475 | 407.0868 | 21.5796 | 21.8617 | 462.5091 | 587.9158 | 587.8036 |  | 696.9689 | 841.0809 | 501.5538 | 660.9352 | 698.9033 | 550.3989 | 611.5563 | 595.13 | 791.1917 | 601.3136 | 702.3918 | 1093.6319 | 1075.8046 | 978.3366 | 484.7504 | 580.4974 | 592.6806 | 497.4257 | 632.0511 | 707.0342 | 1101.502 | 1044.557 | 538.981 |  | 578.9534 | 776.2495 | 47.601 | 0.0008966 | 19.4243 | 6.889 | -28.4973 | 3.0964 | 5395.09 | -0.09 | 1.8815 | 1.4878 | -19.7071 | -15.5603 | 6.865 | -35.1802 | -35.653 | 54.5297 | 74.0775 | 31.961 | 55.9973 | 15.1438 | 55.999 | 27.1366
42838.4325 | 1059 | 22.7641 | 22.7572 | 22.7574 | 22.6792 | 22.295 | 21.6112 | 22.6349 | 21.6752 | 22.2881 | 22.3018 | 22.2574 | 21.9 | 21.1201 | 22.1009 | 21.5236 | 22.8956 | 24.3166 | 26.9697 | 46.6536 | 53.7113 | 85.231 | 89.1371 | 91.3257 | 26.8896 | 55.9559 | 93.9087 | 604.9202 | 630.5683 | 605.5034 | 25.8108 | 61.0635 | 101.3456 | 27.2887 | 58.5675 | 97.5386 | 717.8261 | 684.6703 |  | 368.7554 | 695.0863 | 703.2377 | 666.4574 |  | 477.2004 | 697.2928 | 622.9656 | 800.2841 | 932.809 | 1011.6469 | 1034.5363 | 38.222 | 290.4336 | 61.9126 | 520.5371 | 72.0469 | 50.0945 | 49.2324 | 55.3883 | 47.7927 |  |  | 0.93859 | 0.35544 | -81.1099 | -50.5001 | 7.1423 | -197.8453 | -203.2857 | -2.9482 | 9.8439 | 32.5422 | 11.443 | 3.45e-05 | -0.00020042 | 0.00039427 | 32.0962 | 22.3596 | 22.0998 | 22.1366 | 21.9337 | 21.2035 | 20.0784 | 22.1419 | 22.3069 | 22.3474 | 22.2887 | 21.8875 | 21.1275 | 22.2166 | 567.7431 | 442.639 | 370.0812 | 239.7923 | 182.9122 | 670.7794 | 403.1896 | 22.2201 | 22.5231 | 24.1308 | 22.5268 | 40.3075 | 49.3315 | 31.1426 | 82.7412 | 88.878 | 551.1208 | 501.3834 | 505.2117 | 519.3726 | 48.1599 | 22.6591 | 701.3097 | 22.2604 | 22.137 | 349.7154 | 21.5506 | 21.9572 | 54.1929 | 88.993 | 100.1222 | 27.3708 | 61.9154 | 102.4819 | 702.8251 | 618.2889 | 713.0789 | 718.9397 | 684.2557 |  | 713.3493 | 665.2691 | 784.0391 | 600.1527 | 595.0149 | 667.9295 |  | 566.0664 |  |  | 451.869 | 583.5062 | 670.4444 | [5 empty] | 21.848 | 575.2748 | 22.1394 | 22.0532 | 407.4401 | 21.5848 | 21.8638 | 462.9738 | 588.2189 | 588.2076 |  | 695.1694 | 842.2811 | 501.3187 | 661.1852 | 699.1117 | 550.602 | 612.0185 | 594.7626 | 789.7212 | 600.0801 | 701.9852 | 1093.9006 | 1078.3756 | 980.9727 | 484.9304 | 579.5981 | 592.6997 | 497.503 | 631.5212 | 706.7875 | 1103.6966 | 1046.94 | 538.4769 | 606.3532 | 578.5952 | 775.6388 | 45.9632 | 0.00025766 | 19.4197 | 6.9189 | -28.6095 | 3.0964 | 5417.53 | -0.07 | 2.0013 | 1.2943 | -19.5519 | -15.4276 | 6.6758 | -35.1356 | -35.6154 | 54.5076 | 74.1253 | 32.0674 | 56.4618 | 15.543 | 56.1078 | 27.0554
42838.4325 | 1060 | 22.7542 | 22.7618 | 22.77 | 22.6809 | 22.286 | 21.6138 | 22.6339 | 21.6781 | 22.2951 | 22.2956 | 22.2654 | 21.9052 | 21.1291 | 22.0967 | 21.5248 | 22.9122 | 24.3468 | 27.0488 | 46.7579 | 53.8115 | 85.2423 | 89.1423 | 91.351 | 26.9294 | 56.0442 | 93.9732 | 604.7638 | 630.8364 | 605.0353 | 25.8502 | 61.1529 | 101.416 | 27.3254 | 58.6628 | 97.6071 | 718.0919 | 683.6456 |  | 367.3777 | 696.5623 | 704.4621 | 664.7039 |  | 476.2833 | 695.963 | 620.3324 | 798.8793 | 929.0444 | 1007.0435 | 1032.8995 | 38.5582 | 290.3656 | 62.4341 | 519.8932 | 72.1495 | 50.048 | 49.2149 | 55.388 | 47.8304 |  |  | 1.0904 | 0.37646 | -78.2482 | -49.7634 | 7.6214 | -197.8197 | -203.3508 | -3.0205 | 9.6729 | 32.4323 | 11.5961 | -5.75e-05 | -0.00033841 | 0.00040248 | 32.1564 | 22.3684 | 22.1006 | 22.141 | 21.9457 | 21.2153 | 20.0791 | 22.1418 | 22.3151 | 22.3499 | 22.2885 | 21.8947 | 21.1312 | 22.2153 | 560.6931 | 427.1866 | 353.37 | 237.3295 | 181.5231 | 668.9273 | 401.5989 | 22.209 | 22.5284 | 24.1494 | 22.5311 | 40.4041 | 49.4101 | 31.2453 | 82.7636 | 88.9146 | 550.9192 | 502.2373 | 508.004 | 522.3768 | 61.87 | 23.6029 | 704.6618 | 22.2586 | 22.1336 | 350.2226 | 21.548 | 21.9563 | 54.3181 | 88.944 | 100.1671 | 27.4111 | 62.0854 | 102.5379 | 703.8516 | 618.1643 | 712.3796 | 718.3343 | 684.9341 |  | 713.4886 | 665.3414 | 784.0545 | 598.6184 | 595.2861 | 667.3066 |  | 565.8955 |  |  | 451.544 | 585.4447 | 671.1904 | [5 empty] | 21.8441 | 574.7922 | 22.1334 | 22.0492 | 407.4482 | 21.5807 | 21.8618 | 463.1432 | 587.9849 | 588.6525 |  | 691.7633 | 843.0439 | 500.5653 | 660.4378 | 699.1536 | 550.5923 | 611.7176 | 594.7967 | 788.3886 | 599.4151 | 700.6581 | 1096.7877 | 1078.3555 | 983.9422 | 485.1464 | 578.3398 | 592.8259 | 497.7495 | 631.3678 | 706.7439 | 1103.7357 | 1047.8594 | 538.1603 | 605.7367 | 578.4888 | 775.1681 | 44.6076 | 0.00026467 | 19.4133 | 6.9408 | -28.5838 | 3.0964 | 5434.17 | -0.01 | 2.1565 | 1.3311 | -19.1907 | -15.3042 | 6.8837 | -35.0703 | -35.5572 | 54.523 | 74.1279 | 32.1578 | 56.6871 | 17.1118 | 56.2226 | 26.9408
42838.4326 | 1061 | 22.7432 | 22.7537 | 22.7556 | 22.6678 | 22.2781 | 21.608 | 22.6189 | 21.6659 | 22.2799 | 22.2868 | 22.2576 | 21.8912 | 21.1178 | 22.0899 | 21.5285 | 22.9214 | 24.3687 | 27.119 | 46.8524 | 53.9079 | 85.2577 | 89.1367 | 91.3772 | 26.9617 | 56.1316 | 94.0344 | 604.7095 | 631.2453 | 604.8815 | 25.8888 | 61.2372 | 101.4755 | 27.3631 | 58.7478 | 97.6683 | 718.047 | 684.0615 |  | 370.928 | 695.9363 | 704.3308 | 662.77 |  | 475.6996 | 694.6837 | 617.8467 | 794.4497 | 924.4324 | 1002.9487 | 1032.3255 | 39.0808 | 290.2148 | 62.0397 | 519.0621 | 72.0901 | 49.9838 | 49.1858 | 55.3725 | 47.8696 |  |  | 0.80257 | 1.1151 | -87.2861 | -49.1622 | 7.0056 | -197.8184 | -203.2016 | -2.5257 | 9.6587 | 32.2084 | 11.7905 | -6.735e-05 | -0.00041398 | 0.00038934 | 32.2204 | 22.3678 | 22.1048 | 22.1379 | 21.9369 | 21.2061 | 20.081 | 22.1421 | 22.3103 | 22.3482 | 22.2884 | 21.8834 | 21.1281 | 22.2071 | 591.6863 | 453.5711 | 357.3343 | 241.6539 | 181.0387 | 668.1162 | 400.1122 | 22.2061 | 22.5285 | 24.1669 | 22.5269 | 40.491 | 49.4982 | 31.3562 | 82.7885 | 88.9495 | 550.8783 | 504.2795 | 510.1893 | 525.1094 | 55.6997 | 28.2733 | 707.0883 | 22.2625 | 22.139 | 350.6998 | 21.5529 | 21.9551 | 54.4451 | 88.9467 | 100.2242 | 27.4572 | 62.2691 | 102.6009 | 702.0294 | 618.1586 | 712.1711 | 718.2596 | 682.522 |  | 713.2781 | 665.0749 | 784.0462 | 597.8445 | 595.4958 | 667.4506 |  | 565.6417 |  |  | 451.3846 | 586.4217 | 670.0223 | [5 empty] | 21.838 | 574.3509 | 22.1365 | 22.0524 | 407.7199 | 21.5868 | 21.8656 | 463.1138 | 587.481 | 588.7395 |  | 689.1098 | 844.4995 | 500.0589 | 659.7904 | 699.2725 | 550.6209 | 610.9525 | 597.1809 | 786.3157 | 600.075 | 699.7603 | 1099.351 | 1079.5941 | 984.3222 | 485.3514 | 577.2183 | 592.9342 | 497.6663 | 631.7631 | 707.3103 | 1102.5212 | 1048.7898 | 537.7969 | 605.1014 | 578.4088 | 774.221 | 43.8834 | 0.0029329 | 19.4086 | 6.9656 | -28.5963 | 3.0964 | 5500.69 | -0.03 | 1.85 | 2.2894 | -20.2554 | -15.2014 | 6.5892 | -35.0141 | -35.4873 | 54.5383 | 74.1328 | 32.2163 | 52.9997 | 16.4029 | 56.2652 | 26.8586
42838.4326 | 1062 | 22.7438 | 22.7463 | 22.7547 | 22.6714 | 22.2795 | 21.6105 | 22.6234 | 21.6705 | 22.2832 | 22.2847 | 22.2512 | 21.8975 | 21.1167 | 22.0883 | 21.5325 | 22.9498 | 24.3911 | 27.2082 | 46.962 | 54.0035 | 85.2676 | 89.1445 | 91.3987 | 26.9942 | 56.2284 | 94.0989 | 604.8435 | 632.1834 | 605.1841 | 25.9227 | 61.3189 | 101.5449 | 27.4184 | 58.8353 | 97.7375 | 718.0913 | 685.4244 |  | 362.8765 | 695.2716 | 704.5855 | 666.5596 |  | 475.1099 | 694.4788 | 615.6606 | 789.0189 | 923.3359 | 1005.6375 | 1031.7514 | 39.0516 | 290.1205 | 61.0196 | 518.3295 | 72.1346 | 49.908 | 49.1559 | 55.35 | 47.899 |  |  | 0.74934 | 0.89821 | -106.1933 | -49.243 | 7.2277 | -197.8072 | -203.1865 | -2.8805 | 9.4689 | 31.5505 | 11.8598 | -1.314e-05 | -0.00031377 | 0.00035649 | 32.2864 | 22.3725 | 22.1028 | 22.1436 | 21.9354 | 21.2028 | 20.0787 | 22.1337 | 22.3042 | 22.3536 | 22.2907 | 21.8777 | 21.1264 | 22.215 | 604.4609 | 472.8669 | 355.1674 | 236.248 | 175.873 | 667.4053 | 398.7287 | 22.2162 | 22.548 | 24.1895 | 22.5373 | 40.5944 | 49.5877 | 31.4754 | 82.8248 | 88.9884 | 550.7847 | 505.7337 | 511.1488 | 525.2185 | 43.7514 | 22.1678 | 708.6115 | 22.2611 | 22.1256 | 351.196 | 21.5479 | 21.9414 | 54.5735 | 88.9504 | 100.2641 | 27.5059 | 62.452 | 102.6616 | 700.5253 | 618.6478 | 712.6869 | 718.7409 | 679.282 |  | 712.7476 | 664.8731 | 784.2276 | 599.007 | 595.8266 | 667.2579 |  | 565.5313 |  |  | 451.0596 | 584.9936 | 668.0657 | [5 empty] | 21.8387 | 574.3553 | 22.1365 | 22.0537 | 409.4219 | 21.587 | 21.8561 | 463.0804 | 586.9184 | 588.5175 |  | 687.2929 | 845.6421 | 499.8012 | 659.4964 | 699.3057 | 550.6549 | 610.269 | 599.7504 | 784.0193 | 600.4847 | 699.1364 | 1102.393 | 1082.6727 | 984.0489 | 485.2714 | 576.6147 | 593.1641 | 497.7004 | 632.0818 | 707.5861 | 1107.7749 | 1050.882 | 537.525 | 605.2453 | 578.1828 | 773.7312 | 44.1337 | 0.00044021 | 19.4044 | 6.9838 | -28.5568 | 3.0964 | 5537.16 | -0.1 | 1.7879 | 2.0545 | -22.3393 | -15.2123 | 6.6999 | -35.0499 | -35.5233 | 54.4982 | 74.1921 | 32.2424 | 51.367 | 16.3945 | 56.1709 | 26.8411
42838.4326 | 1063 | 22.752 | 22.7485 | 22.7552 | 22.6746 | 22.2867 | 21.6139 | 22.6276 | 21.675 | 22.2899 | 22.292 | 22.2515 | 21.897 | 21.1167 | 22.0908 | 21.5228 | 22.9568 | 24.4132 | 27.2758 | 47.0493 | 54.0938 | 85.2699 | 89.1594 | 91.4148 | 27.0185 | 56.3028 | 94.1573 | 605.101 | 632.9236 | 605.7888 | 25.9496 | 61.3997 | 101.5979 | 27.447 | 58.9101 | 97.7846 | 718.5674 | 685.5222 |  | 358.4129 | 692.3217 | 702.4152 | 672.3795 |  | 475.6351 | 693.8145 | 614.1334 | 788.7319 | 923.3051 | 1006.3482 | 1028.7335 | 38.744 | 289.8836 | 60.8922 | 517.5741 | 72.1583 | 49.8264 | 49.1249 | 55.3376 | 47.9323 |  |  | 0.95108 | 0.65245 | -86.1842 | -48.8895 | 6.3249 | -197.8263 | -203.1096 | -2.7905 | 9.6869 | 32.491 | 11.865 | -0.00015114 | -0.00036634 | 0.00039098 | 32.3514 | 22.3789 | 22.0898 | 22.134 | 21.9289 | 21.2005 | 20.0693 | 22.1326 | 22.3115 | 22.3476 | 22.2826 | 21.8762 | 21.1336 | 22.2072 | 591.9244 | 456.7657 | 347.8167 | 235.6663 | 177.4223 | 665.7334 | 396.9823 | 22.2115 | 22.5447 | 24.2078 | 22.5432 | 40.6841 | 49.6725 | 31.5823 | 82.855 | 89.0217 | 550.4956 | 504.3001 | 510.8713 | 523.6001 | 43.6405 | 20.2483 | 710.3571 | 22.275 | 22.131 | 351.5907 | 21.5538 | 21.944 | 54.707 | 88.972 | 100.3232 | 27.5695 | 62.6397 | 102.7372 | 699.1418 | 619.6359 | 712.8852 | 718.6923 | 677.4277 |  | 712.1337 | 664.8373 | 784.4537 | 602.6737 | 596.3427 | 666.6117 |  | 565.7194 |  |  | 450.9928 | 583.046 | 665.5862 | [5 empty] | 21.8404 | 576.0041 | 22.1398 | 22.0542 | 410.7555 | 21.5957 | 21.858 | 462.7098 | 586.2941 | 588.159 |  | 687.7699 | 845.3336 | 499.0095 | 658.6316 | 699.1651 | 550.4257 | 609.7284 | 602.3943 | 782.3769 | 599.6492 | 698.3135 | 1106.3861 | 1087.6635 | 986.3144 | 485.431 | 576.4768 | 593.0309 | 497.509 | 632.0694 | 708.2086 | 1110.1509 | 1054.4261 | 537.6051 | 605.1358 | 577.9331 | 773.7013 | 43.8504 | 0.00046831 | 19.4017 | 6.9947 | -28.574 | 3.0964 | 5545.8 | -0.08 | 2.0149 | 1.7504 | -20.1181 | -15.1523 | 6.2692 | -35.0614 | -35.5265 | 54.3993 | 74.26 | 32.2317 | 52.2595 | 16.8976 | 56.1277 | 26.8413
42838.4326 | 1064 | 22.7537 | 22.7539 | 22.759 | 22.6793 | 22.2929 | 21.6116 | 22.6385 | 21.6744 | 22.2904 | 22.2907 | 22.2608 | 21.8954 | 21.1169 | 22.0948 | 21.5366 | 22.9702 | 24.4365 | 27.3611 | 47.1612 | 54.1943 | 85.2981 | 89.174 | 91.4435 | 27.053 | 56.3943 | 94.2219 | 605.2299 | 633.5742 | 605.7813 | 26.0034 | 61.4887 | 101.6603 | 27.501 | 58.9996 | 97.8433 | 719.2973 | 685.5752 |  | 357.0083 | 690.6612 | 701.4147 | 672.7536 |  | 475.6533 | 693.7334 | 613.4177 | 793.1324 | 924.0622 | 1004.3489 | 1028.3344 | 38.234 | 289.5691 | 60.2425 | 516.7867 | 72.1078 | 49.7594 | 49.0891 | 55.3326 | 47.9832 |  |  | 0.98459 | 0.99875 | -82.9459 | -49.0215 | 7.2074 | -197.8427 | -203.2962 | -2.7024 | 9.9856 | 33.0652 | 12.032 | -0.00012978 | -0.00033348 | 0.00036963 | 32.4192 | 22.3866 | 22.1027 | 22.1405 | 21.9312 | 21.1988 | 20.0732 | 22.1381 | 22.3134 | 22.3414 | 22.2871 | 21.8864 | 21.1298 | 22.2131 | 570.2339 | 419.9643 | 342.0261 | 231.6052 | 179.632 | 663.3831 | 395.1201 | 22.2189 | 22.5634 | 24.2485 | 22.5568 | 40.7997 | 49.7776 | 31.7317 | 82.8867 | 89.0827 | 550.095 | 503.0046 | 509.5312 | 522.0371 | 45.313 | 19.7601 | 712.032 | 22.2802 | 22.1362 | 351.9778 | 21.563 | 21.9478 | 54.8332 | 88.9847 | 100.3768 | 27.6223 | 62.8439 | 102.8004 | 699.3469 | 619.6223 | 712.362 | 718.3681 | 675.5878 |  | 711.4477 | 664.7861 | 784.7376 | 604.1183 | 596.8383 | 666.6072 |  | 565.8687 |  |  | 450.2273 | 580.81 | 663.2877 | [5 empty] | 21.8352 | 577.0449 | 22.1488 | 22.0491 | 411.1491 | 21.5993 | 21.8493 | 462.5492 | 585.8791 | 587.8588 |  | 688.9886 | 847.3283 | 497.7078 | 657.8644 | 698.9561 | 550.2828 | 609.2534 | 611.694 | 782.4662 | 598.0555 | 698.0122 | 1111.8257 | 1088.9963 | 988.7499 | 485.9074 | 576.3253 | 592.9291 | 496.7578 | 631.7202 | 708.7454 | 1111.5001 | 1054.7021 | 537.6218 | 604.9366 | 577.6005 | 773.6864 | 44.7809 | 0.00011019 | 19.3982 | 7.0008 | -28.546 | 3.0965 | 5564.95 | -0.17 | 2.0501 | 2.1656 | -19.7357 | -15.1722 | 6.6871 | -35.0354 | -35.515 | 54.2827 | 74.3455 | 32.2793 | 53.9689 | 17.2075 | 56.2992 | 26.8229
42838.4326 | 1065 | 22.7536 | 22.7625 | 22.7544 | 22.6713 | 22.2918 | 21.6067 | 22.6362 | 21.6746 | 22.2987 | 22.2953 | 22.2675 | 21.8928 | 21.1204 | 22.0903 | 21.5403 | 22.9902 | 24.4612 | 27.4403 | 47.2648 | 54.2802 | 85.3065 | 89.1729 | 91.4453 | 27.09 | 56.4883 | 94.2938 | 605.4165 | 634.0034 | 605.7068 | 26.0422 | 61.5741 | 101.3234 | 27.536 | 59.0787 | 97.9059 | 719.8588 | 685.7014 |  | 356.5466 | 691.9475 | 702.8256 | 672.1367 |  | 475.7479 | 692.9447 | 613.2393 | 793.4204 | 924.8029 | 1003.7685 | 1028.8695 | 38.0618 | 289.2981 | 59.6404 | 516.1731 | 72.1832 | 49.7024 | 49.0619 | 55.3401 | 48.0411 |  |  | 0.96685 | 0.74116 | -84.7142 | -50.0066 | 7.3013 | -197.8033 | -203.1911 | -3.3641 | 10.1446 | 33.2173 | 11.8306 | -1.643e-05 | -0.00031706 | 0.00038934 | 32.4911 | 22.3828 | 22.0981 | 22.1373 | 21.9287 | 21.1971 | 20.078 | 22.1386 | 22.3068 | 22.3437 | 22.2898 | 21.8875 | 21.1308 | 22.2124 | 557.8627 | 410.1834 | 331.5953 | 227.1585 | 175.6433 | 660.9578 | 393.2161 | 22.218 | 22.5723 | 24.265 | 22.5586 | 40.8874 | 49.8734 | 31.8276 | 82.8887 | 89.1079 | 549.7079 | 501.3278 | 508.1536 | 520.0475 | 55.973 | 29.3386 | 713.5416 | 22.2794 | 22.1328 | 352.1804 | 21.5518 | 21.9564 | 54.9597 | 88.9761 | 100.4273 | 27.669 | 63.0307 | 102.8668 | 699.5788 | 619.1896 | 713.3347 | 719.4435 | 676.128 |  | 710.8296 | 664.8651 | 785.1895 | 603.0734 | 597.2465 | 666.6543 |  | 565.6328 |  |  | 449.5808 | 579.2455 | 662.6112 | [5 empty] | 21.8294 | 577.0354 | 22.1489 | 22.0521 | 412.3424 | 21.6005 | 21.859 | 462.7251 | 585.6933 | 587.2587 |  | 693.6236 | 848.7704 | 496.3049 | 656.5863 | 699.6863 | 550.2254 | 608.9262 | 615.4308 | 781.3976 | 596.1848 | 697.3738 | 1115.2808 | 1091.899 | 989.281 | 486.2123 | 576.2798 | 592.9814 | 496.589 | 631.246 | 709.5971 | 1116.4939 | 1054.9017 | 537.7456 | 604.9508 | 577.6067 | 773.8636 | 44.7373 | -0.00024088 | 19.397 | 7.0166 | -28.4314 | 3.0965 | 5593.98 | 0.01 | 2.0314 | 1.8648 | -19.9368 | -15.3176 | 6.729 | -35.024 | -35.4978 | 54.1169 | 74.4773 | 32.3807 | 54.6239 | 18.0266 | 56.4566 | 26.8185
42838.4326 | 1066 | 22.749 | 22.756 | 22.7672 | 22.6872 | 22.2945 | 21.6196 | 22.6347 | 21.6754 | 22.293 | 22.2996 | 22.2622 | 21.9052 | 21.1245 | 22.0979 | 21.5369 | 23.0009 | 24.4866 | 27.5257 | 47.3552 | 54.3858 | 85.3335 | 89.1936 | 91.4718 | 27.1181 | 56.5669 | 94.3608 | 605.8742 | 634.8696 | 606.4143 | 26.0644 | 61.6484 | 100.975 | 27.5674 | 59.1806 | 97.9692 | 720.2698 | 687.09 |  | 358.6485 | 694.0587 | 705.2658 | 670.6865 |  | 476.3143 | 693.4664 | 613.1616 | 794.2257 | 926.5615 | 1009.8348 | 1029.0919 | 38.1132 | 288.8618 | 58.9421 | 515.5969 | 72.2041 | 49.6604 | 49.0284 | 55.3549 | 48.0902 |  |  | 1.0516 | 0.99349 | -84.2076 | -49.6215 | 7.4315 | -197.8072 | -203.3646 | -2.6085 | 9.8626 | 32.8386 | 11.5653 | -0.00011171 | -0.00034006 | 0.00037784 | 32.5509 | 22.3814 | 22.0958 | 22.1332 | 21.9298 | 21.1956 | 20.0791 | 22.136 | 22.2999 | 22.3427 | 22.2811 | 21.884 | 21.1267 | 22.2088 | 583.9058 | 436.0053 | 340.0442 | 226.4627 | 175.3899 | 660.5574 | 391.7911 | 22.2182 | 22.5707 | 24.2851 | 22.5629 | 40.9766 | 49.9526 | 31.9262 | 82.8909 | 89.143 | 549.3277 | 500.4848 | 507.4241 | 519.2771 | 63.8995 | 23.8924 | 715.1782 | 22.2883 | 22.136 | 351.9552 | 21.554 | 21.9623 | 55.0864 | 88.9879 | 100.4732 | 27.7274 | 63.2339 | 102.9437 | 698.9913 | 619.0493 | 714.8802 | 720.697 | 678.8412 |  | 710.5474 | 665.1406 | 785.7214 | 602.661 | 597.5535 | 666.7751 |  | 565.5236 |  |  | 449.6016 | 580.7217 | 663.8838 | [5 empty] | 21.8454 | 576.6231 | 22.1588 | 22.0473 | 412.5989 | 21.5969 | 21.8588 | 462.984 | 585.6299 | 586.9837 |  | 696.6166 | 850.3004 | 494.9652 | 654.186 | 700.6226 | 550.3899 | 608.8696 | 615.9039 | 781.1714 | 593.4192 | 696.4742 | 1120.7934 | 1093.6584 | 993.3139 | 486.5061 | 576.2217 | 593.5241 | 496.657 | 631.3538 | 711.2432 | 1121.0117 | 1056.444 | 538.0802 | 605.4089 | 577.834 | 774.9474 | 44.1721 | 0.0010581 | 19.3962 | 7.0263 | -28.5399 | 3.0964 | 5599.56 | -0.01 | 2.1195 | 2.1596 | -19.8824 | -15.2626 | 6.8048 | -35.1074 | -35.5972 | 53.9727 | 74.6275 | 32.4466 | 51.6118 | 16.8341 | 56.5996 | 26.7813
42838.4326 | 1067 | 22.7507 | 22.7573 | 22.7591 | 22.6764 | 22.2835 | 21.6177 | 22.6325 | 21.6756 | 22.2873 | 22.2931 | 22.261 | 21.8996 | 21.1219 | 22.0984 | 21.5444 | 23.0173 | 24.5086 | 27.6054 | 47.4665 | 54.4839 | 85.3558 | 89.2111 | 91.4864 | 27.1516 | 56.6538 | 94.4251 | 606.7954 | 635.9763 | 607.495 | 26.0996 | 61.7342 | 100.78 | 27.6163 | 59.2565 | 98.0235 | 720.7656 | 688.2546 |  | 358.2129 | 695.6248 | 707.8164 | 673.2504 |  | 476.1652 | 693.793 | 612.8584 | 790.7021 | 924.041 | 1011.5874 | 1028.2038 | 38.2393 | 288.4047 | 58.0865 | 514.9519 | 72.1922 | 49.6511 | 48.9994 | 55.3601 | 48.1176 |  |  | 0.96948 | 0.67348 | -81.6251 | -48.1351 | 6.9274 | -197.7914 | -203.1747 | -3.2235 | 9.6497 | 32.5636 | 11.631 | -9.86e-06 | -0.00031541 | 0.00035156 | 32.62 | 22.402 | 22.1045 | 22.1455 | 21.9401 | 21.2098 | 20.0864 | 22.1407 | 22.3133 | 22.3493 | 22.2951 | 21.8985 | 21.1426 | 22.2272 | 637.4681 | 485.4218 | 347.7045 | 228.6333 | 179.9597 | 660.7109 | 390.4909 | 22.2126 | 22.5808 | 24.3021 | 22.5673 | 41.0712 | 50.0307 | 32.0189 | 82.9098 | 89.1758 | 549.0947 | 500.581 | 506.2071 | 520.844 | 45.1012 | 24.1298 | 716.9507 | 22.2969 | 22.1345 | 351.5068 | 21.5589 | 21.9516 | 55.2087 | 88.9767 | 100.5231 | 27.7817 | 63.4389 | 103.0144 | 698.6481 | 619.1746 | 716.4719 | 722.0632 | 679.9977 |  | 710.3206 | 665.5831 | 786.4354 | 603.0816 | 597.9019 | 667.0758 |  | 565.4096 |  |  | 450.1419 | 582.4604 | 665.1417 | [5 empty] | 21.8358 | 577.108 | 22.1656 | 22.0526 | 412.6213 | 21.6025 | 21.8641 | 463.5472 | 585.4268 | 587.006 |  | 698.4271 | 850.8826 | 493.4396 | 652.5516 | 701.7822 | 550.5358 | 609.1727 | 616.2181 | 780.0594 | 591.8157 | 695.8719 | 1121.7989 | 1094.4924 | 996.3216 | 486.8436 | 576.2353 | 594.0489 | 496.3906 | 632.0418 | 713.2296 | 1123.1217 | 1059.5842 | 538.3542 | 605.6317 | 578.0016 | 775.7045 | 43.219 | 0.0010581 | 19.3956 | 7.0334 | -28.5586 | 3.0965 | 5640.13 | -0.15 | 2.0363 | 1.7784 | -19.5785 | -15.0348 | 6.5745 | -35.13 | -35.6048 | 53.8854 | 74.8275 | 32.4968 | 45.7058 | 15.7521 | 56.6525 | 26.7019
42838.4326 | 1068 | 22.7496 | 22.7567 | 22.7606 | 22.6807 | 22.2816 | 21.6188 | 22.6338 | 21.6708 | 22.2874 | 22.2974 | 22.2581 | 21.8989 | 21.1216 | 22.0976 | 21.5483 | 23.0347 | 24.5382 | 27.6873 | 47.5681 | 54.58 | 85.3943 | 89.2176 | 91.5068 | 27.1997 | 56.7472 | 94.501 | 607.6609 | 637.4457 | 608.4456 | 26.1463 | 61.8162 | 100.6703 | 27.6547 | 59.3469 | 98.0807 | 721.6706 | 688.3442 |  | 356.3176 | 697.0457 | 710.9767 | 676.6095 |  | 476.1055 | 694.5039 | 613.7158 | 791.4669 | 921.6306 | 1010.852 | 1028.6317 | 38.5139 | 287.9323 | 57.1702 | 514.1039 | 72.1938 | 49.6552 | 48.959 | 55.3673 | 48.1352 |  |  | 1.0976 | 1.163 | -77.0227 | -47.9143 | 7.3841 | -197.8657 | -203.3094 | -2.5506 | 8.91 | 30.2153 | 11.7152 | 3.121e-05 | -0.0003302 | 0.00035813 | 32.6851 | 22.4004 | 22.107 | 22.1444 | 21.9424 | 21.2039 | 20.0867 | 22.1508 | 22.3102 | 22.3514 | 22.2959 | 21.8969 | 21.1377 | 22.217 | 625.9959 | 463.0324 | 356.6049 | 239.0333 | 191.5798 | 659.1889 | 389.053 | 22.2271 | 22.6012 | 24.3338 | 22.5814 | 41.1775 | 50.1197 | 32.1534 | 82.9418 | 89.2314 | 548.9672 | 497.7523 | 506.4786 | 522.1266 | 38.316 | 23.3246 | 719.7043 | 22.2992 | 22.1347 | 351.6744 | 21.5573 | 21.954 | 55.3336 | 88.9736 | 100.5653 | 27.8284 | 63.6612 | 103.0787 | 699.3229 | 619.0975 | 717.8678 | 723.3139 | 679.7465 |  | 710.0493 | 665.8986 | 787.0897 | 602.3854 | 598.2588 | 667.3244 |  | 565.374 |  |  | 449.7782 | 582.0992 | 665.1719 | [5 empty] | 21.8282 | 577.0219 | 22.1652 | 22.0491 | 412.5296 | 21.6033 | 21.8598 | 463.9115 | 585.1942 | 587.238 |  | 697.6501 | 850.1815 | 492.2243 | 651.7346 | 703.1107 | 550.605 | 609.5641 | 615.7246 | 777.3781 | 590.5197 | 697.2747 | 1121.6021 | 1096.1954 | 997.3751 | 487.2217 | 576.415 | 595.0068 | 496.5582 | 633.0223 | 715.4678 | 1126.7832 | 1059.8731 | 538.7826 | 606.178 | 578.0748 | 776.2825 | 42.9479 | -0.00021983 | 19.3947 | 7.041 | -28.5384 | 3.0964 | 5635.61 | -0.03 | 2.1678 | 2.3379 | -19.0255 | -15.0058 | 6.7858 | -35.1265 | -35.6064 | 53.8263 | 75.0136 | 32.5796 | 46.5309 | 14.5084 | 56.7861 | 26.6467
42838.4327 | 1069 | 22.7461 | 22.7543 | 22.7598 | 22.6796 | 22.2849 | 21.612 | 22.6264 | 21.6712 | 22.2897 | 22.2956 | 22.2603 | 21.8993 | 21.1213 | 22.1043 | 21.5465 | 23.055 | 24.5585 | 27.7662 | 47.6611 | 54.6711 | 85.4286 | 89.2153 | 91.5233 | 27.2269 | 56.8246 | 94.5567 | 608.4182 | 639.3904 | 609.2567 | 26.1796 | 61.8864 | 100.6088 | 27.691 | 59.4201 | 98.1324 | 722.6145 | 686.7969 |  | 355.4401 | 697.2917 | 711.4766 | 677.0577 |  | 475.7532 | 694.6541 | 611.7483 | 786.4087 | 916.6474 | 1008.6583 | 1026.0013 | 38.6728 | 287.4208 | 58.0061 | 513.1351 | 72.2015 | 49.6593 | 48.9299 | 55.3769 | 48.1701 |  |  | 1.0759 | 0.17933 | -77.3092 | -45.2096 | 7.4354 | -197.8006 | -203.3192 | -2.1984 | 9.012 | 31.4074 | 11.6504 | -0.00016756 | -0.00042548 | 0.00037784 | 32.7555 | 22.4032 | 22.1065 | 22.1421 | 21.9406 | 21.1998 | 20.0838 | 22.152 | 22.3147 | 22.3564 | 22.2977 | 21.8937 | 21.1411 | 22.2164 | 606.2376 | 446.0279 | 362.6867 | 248.6413 | 197.3478 | 657.1067 | 387.7592 | 22.216 | 22.6059 | 24.3569 | 22.5881 | 41.2773 | 50.2196 | 32.2942 | 82.9622 | 89.2744 | 548.7437 | 498.5986 | 505.5396 | 521.4598 | 51.9602 | 24.3548 | 721.6721 | 22.2991 | 22.1353 | 352.3123 | 21.559 | 21.9542 | 55.4605 | 88.9782 | 100.6127 | 27.8785 | 63.8835 | 103.1318 | 699.2587 | 619.0702 | 718.5962 | 723.7837 | 678.4356 |  | 709.6342 | 665.7194 | 787.5314 | 601.7238 | 598.5529 | 668.2146 |  | 565.4246 |  |  | 449.5013 | 582.2011 | 664.6688 | [5 empty] | 21.8393 | 576.7641 | 22.1743 | 22.0534 | 412.9503 | 21.6192 | 21.8605 | 464.2654 | 585.2974 | 587.3966 |  | 695.8349 | 848.2174 | 491.3575 | 650.6343 | 704.1453 | 550.8648 | 610.1203 | 614.7513 | 775.335 | 589.6658 | 697.8324 | 1122.606 | 1098.1207 | 994.8062 | 487.6286 | 576.6387 | 595.8546 | 496.7165 | 633.6579 | 717.0042 | 1127.6498 | 1059.1852 | 539.1871 | 607.2657 | 578.1206 | 775.9079 | 44.5239 | -0.00019878 | 19.397 | 7.059 | -28.5296 | 3.0964 | 5610.21 | -0.11 | 2.1473 | 0.91809 | -19.0623 | -14.5773 | 6.8035 | -35.0907 | -35.5769 | 53.7618 | 75.1503 | 32.6503 | 48.1135 | 13.6039 | 57.011 | 26.6308
42838.4327 | 1070 | 22.7424 | 22.7502 | 22.7596 | 22.6773 | 22.2855 | 21.611 | 22.6275 | 21.6706 | 22.2881 | 22.2929 | 22.2634 | 21.8972 | 21.1221 | 22.1012 | 21.5515 | 23.0722 | 24.5835 | 27.8491 | 47.7548 | 54.7617 | 85.4574 | 89.2122 | 91.5464 | 27.2575 | 56.913 | 94.6112 | 609.0005 | 640.5993 | 609.8803 | 26.2223 | 61.9714 | 100.5907 | 27.7388 | 59.5057 | 98.1991 | 723.2838 | 685.3849 |  | 357.0539 | 696.9601 | 711.4571 | 676.4497 |  | 475.5047 | 694.6864 | 610.2296 | 784.5577 | 916.0537 | 1010.0861 | 1025.7182 | 38.7441 | 287.1255 | 60.606 | 512.689 | 72.2413 | 49.6586 | 48.8981 | 55.3598 | 48.1842 |  |  | 0.91493 | 0.83973 | -77.344 | -41.8169 | 7.3598 | -197.8644 | -203.2877 | -2.893 | 9.3607 | 31.2893 | 11.7242 | -5.585e-05 | -0.00034827 | 0.0003992 | 32.824 | 22.408 | 22.0996 | 22.1361 | 21.931 | 21.199 | 20.0725 | 22.1382 | 22.297 | 22.3415 | 22.2869 | 21.8859 | 21.1299 | 22.2173 | 598.726 | 443.7316 | 358.0914 | 246.54 | 197.8601 | 655.2198 | 386.4906 | 22.2157 | 22.6045 | 24.3682 | 22.5879 | 41.3671 | 50.2947 | 32.4003 | 82.9672 | 89.3092 | 548.5892 | 500.9674 | 506.1498 | 521.8803 | 52.1609 | 21.0963 | 722.5603 | 22.3116 | 22.1431 | 353.3622 | 21.5606 | 21.9517 | 55.5793 | 88.9857 | 100.6704 | 27.9375 | 64.1152 | 103.1953 | 700.337 | 619.1127 | 717.2649 | 722.6769 | 678.0158 |  | 709.1687 | 665.4178 | 787.6695 | 601.0606 | 598.821 | 668.1725 |  | 565.453 |  |  | 448.3374 | 582.8609 | 663.5464 | [5 empty] | 21.8416 | 576.5381 | 22.1763 | 22.0519 | 412.6947 | 21.6229 | 21.8586 | 464.5409 | 585.6034 | 587.5922 |  | 694.0211 | 846.9427 | 490.8453 | 649.8942 | 704.6501 | 550.9535 | 610.3095 | 613.7803 | 775.4563 | 589.3004 | 698.2032 | 1122.9262 | 1098.3518 | 992.2901 | 487.9125 | 577.0445 | 596.5237 | 497.2255 | 633.4649 | 717.054 | 1126.8127 | 1060.0155 | 539.6971 | 608.5078 | 578.3383 | 776.0282 | 45.2366 | -0.00064115 | 19.4005 | 7.0619 | -28.4902 | 3.0965 | 5580.6 | -0.08 | 1.9808 | 1.9867 | -19.067 | -14.0199 | 6.7726 | -35.1159 | -35.5939 | 53.6604 | 75.2 | 32.7165 | 48.395 | 13.8907 | 57.1964 | 26.5954
42838.4327 | 1071 | 22.7477 | 22.7541 | 22.7544 | 22.6755 | 22.2828 | 21.6073 | 22.6245 | 21.6616 | 22.2809 | 22.2871 | 22.2552 | 21.8915 | 21.1123 | 22.0882 | 21.5525 | 23.0802 | 24.6081 | 27.9255 | 47.8555 | 54.8483 | 85.4785 | 89.2076 | 91.5669 | 27.2855 | 56.991 | 94.6606 | 609.2804 | 641.4618 | 610.1101 | 26.2581 | 62.061 | 100.5978 | 27.7815 | 59.5961 | 98.2709 | 723.9269 | 686.719 |  | 356.7429 | 699.3022 | 713.1725 | 676.0881 |  | 475.2978 | 692.8149 | 609.7894 | 790.0011 | 912.5028 | 1008.5403 | 1025.5151 | 38.9287 | 286.7513 | 63.3228 | 512.4867 | 72.2648 | 49.6461 | 48.8613 | 55.3373 | 48.2118 |  |  | 0.96948 | 0.58017 | -76.5594 | -43.5603 | 6.6935 | -197.8269 | -203.2614 | -2.5749 | 9.3138 | 31.6556 | 11.4772 | -5.914e-05 | -0.00040084 | 0.0003877 | 32.8969 | 22.4226 | 22.0992 | 22.1435 | 21.9345 | 21.1998 | 20.0795 | 22.1426 | 22.3098 | 22.3473 | 22.2888 | 21.8952 | 21.1296 | 22.2192 | 598.0328 | 429.9609 | 340.489 | 239.7234 | 190.7151 | 654.0379 | 384.8788 | 22.2181 | 22.6145 | 24.3887 | 22.5945 | 41.4578 | 50.3872 | 32.5222 | 82.995 | 89.3515 | 548.5817 | 504.1517 | 508.3572 | 523.375 | 53.8995 | 19.2462 | 722.6219 | 22.3144 | 22.1292 | 354.2175 | 21.5604 | 21.9489 | 55.6915 | 88.9933 | 100.7185 | 27.9902 | 64.3537 | 103.2659 | 702.794 | 618.9891 | 715.2122 | 720.8424 | 679.6659 |  | 708.9467 | 665.2216 | 787.7262 | 600.5563 | 599.0807 | 668.1157 |  | 565.485 |  |  | 448.3057 | 583.4618 | 664.0291 | [5 empty] | 21.8372 | 576.396 | 22.1774 | 22.0529 | 412.2499 | 21.6213 | 21.8578 | 464.673 | 585.8168 | 587.7407 |  | 692.6086 | 847.3566 | 490.4162 | 649.4622 | 704.9285 | 550.9705 | 610.715 | 613.4825 | 778.4977 | 588.5255 | 697.8329 | 1122.9833 | 1096.1639 | 991.9304 | 488.1234 | 577.7044 | 597.049 | 497.6042 | 633.2945 | 718.655 | 1122.753 | 1059.3926 | 540.0827 | 609.1042 | 578.5603 | 776.3147 | 46.4784 | 0.00014531 | 19.4023 | 7.0653 | -28.4801 | 3.0964 | 5552.49 | -0.05 | 2.0393 | 1.6498 | -18.9516 | -14.2953 | 6.4548 | -35.0914 | -35.5702 | 53.5606 | 75.2223 | 32.7767 | 48.1267 | 15.5629 | 57.3688 | 26.5527
42838.4327 | 1072 | 22.7516 | 22.7579 | 22.7587 | 22.6822 | 22.2853 | 21.6176 | 22.6349 | 21.6819 | 22.2904 | 22.2977 | 22.2614 | 21.9028 | 21.123 | 22.1 | 21.5518 | 23.0949 | 24.6327 | 28.0074 | 47.9523 | 54.9441 | 85.5057 | 89.2158 | 91.5832 | 27.32 | 57.0696 | 94.7067 | 609.903 | 642.1555 | 610.9103 | 26.2982 | 62.129 | 100.6124 | 27.8209 | 59.6755 | 98.3214 | 724.6174 | 686.6838 |  | 355.2006 | 699.4169 | 712.3333 | 674.0332 |  | 475.3181 | 690.9227 | 609.0181 | 786.0184 | 903.1293 | 1007.0595 | 1025.5026 | 39.169 | 286.3779 | 63.391 | 512.5567 | 72.2104 | 49.6295 | 48.8339 | 55.323 | 48.2683 |  |  | 0.88471 | 0.58739 | -75.3733 | -43.6562 | 7.1101 | -197.8151 | -203.2916 | -2.8371 | 9.2959 | 32.1392 | 11.5589 | -8.542e-05 | -0.00042384 | 0.00041234 | 32.9582 | 22.4153 | 22.0927 | 22.13 | 21.9263 | 21.1995 | 20.076 | 22.1287 | 22.3064 | 22.3427 | 22.2795 | 21.8848 | 21.1218 | 22.2077 | 619.4921 | 439.9402 | 332.1944 | 233.2157 | 176.8345 | 653.0819 | 383.1407 | 22.2207 | 22.6337 | 24.4193 | 22.5958 | 41.5526 | 50.4762 | 32.6625 | 83.029 | 89.3995 | 548.6187 | 506.1811 | 510.0523 | 524.5536 | 42.4188 | 22.1414 | 722.0826 | 22.3166 | 22.1291 | 354.5338 | 21.5581 | 21.9472 | 55.8165 | 88.9912 | 100.7649 | 28.0411 | 64.5964 | 103.334 | 705.8896 | 618.9871 | 713.3347 | 719.2369 | 682.054 |  | 708.9799 | 665.0287 | 787.6612 | 600.2437 | 599.3471 | 667.9711 |  | 565.9822 |  |  | 450.1195 | 584.5765 | 665.6885 | [5 empty] | 21.8396 | 576.2496 | 22.1845 | 22.0529 | 412.4236 | 21.6243 | 21.861 | 465.0459 | 586.0738 | 587.9089 |  | 693.4202 | 849.0727 | 489.7316 | 648.3059 | 705.491 | 551.1255 | 611.3341 | 613.5899 | 783.0717 | 587.8046 | 696.8875 | 1123.063 | 1095.0335 | 992.2942 | 487.6052 | 578.4757 | 597.7514 | 497.4312 | 633.3642 | 720.756 | 1120.3318 | 1058.4271 | 540.6982 | 609.5988 | 578.4328 | 776.0011 | 46.7525 | 0.0014584 | 19.4041 | 7.0686 | -28.5214 | 3.0964 | 5467.48 | -0.12 | 1.949 | 1.6584 | -18.7858 | -14.297 | 6.6488 | -35.0701 | -35.5523 | 53.5024 | 75.2083 | 32.8329 | 45.4635 | 16.1796 | 57.6005 | 26.5257
42838.4327 | 1073 | 22.7385 | 22.7489 | 22.7545 | 22.6747 | 22.2881 | 21.6053 | 22.6252 | 21.6611 | 22.2813 | 22.2844 | 22.2552 | 21.8951 | 21.1098 | 22.0798 | 21.5569 | 23.119 | 24.6562 | 28.0901 | 48.0448 | 55.0441 | 85.515 | 89.2222 | 91.5975 | 27.3532 | 57.158 | 94.749 | 610.3742 | 642.1648 | 611.4056 | 26.3434 | 62.2319 | 100.6821 | 27.8604 | 59.7706 | 98.4001 | 725.0126 | 685.8166 |  | 356.0957 | 697.0212 | 710.1409 | 672.3309 |  | 475.3652 | 690.3803 | 608.5264 | 782.7349 | 897.6126 | 1007.626 | 1024.5654 | 39.2886 | 285.9582 | 63.568 | 512.5931 | 72.2975 | 49.6111 | 48.8026 | 55.3072 | 48.3015 |  |  | 0.82688 | 0.64391 | -74.318 | -45.1524 | 7.2928 | -197.8164 | -203.1431 | -2.9272 | 9.5075 | 32.6188 | 11.615 | -7.721e-05 | -0.00031377 | 0.00040084 | 33.0187 | 22.4175 | 22.0922 | 22.1219 | 21.9259 | 21.1942 | 20.0733 | 22.129 | 22.2965 | 22.3433 | 22.2776 | 21.8804 | 21.124 | 22.2012 | 593.6314 | 447.4541 | 342.0836 | 235.6209 | 177.4634 | 650.697 | 381.7673 | 22.2208 | 22.635 | 24.4385 | 22.6045 | 41.6464 | 50.562 | 32.8044 | 83.0453 | 89.4436 | 548.678 | 508.2812 | 512.3679 | 526.1324 | 41.264 | 26.268 | 721.1619 | 22.3215 | 22.1318 | 354.9726 | 21.563 | 21.9517 | 55.9371 | 88.996 | 100.8146 | 28.0925 | 64.8441 | 103.407 | 708.9093 | 619.3317 | 712.0562 | 718.178 | 684.8069 |  | 709.2364 | 664.9108 | 787.6082 | 600.8738 | 599.5768 | 667.9606 |  | 566.3405 |  |  | 452.3954 | 586.7687 | 668.3627 | [5 empty] | 21.8385 | 576.3613 | 22.1859 | 22.0489 | 413.0832 | 21.6303 | 21.8634 | 465.7929 | 586.4851 | 588.0096 |  | 694.8828 | 850.4775 | 489.5354 | 647.7144 | 705.8651 | 551.2696 | 611.7068 | 613.5586 | 786.282 | 588.4284 | 696.6499 | 1122.5054 | 1095.0556 | 991.6652 | 486.6645 | 579.3393 | 598.5912 | 497.3788 | 633.7435 | 721.3037 | 1119.6798 | 1057.1855 | 541.4357 | 610.2128 | 578.3512 | 775.7781 | 45.0205 | -0.0048822 | 19.41 | 7.0722 | -28.4251 | 3.0964 | 5430.51 | -0.05 | 1.8847 | 1.7358 | -18.6486 | -14.5358 | 6.7352 | -35.078 | -35.5471 | 53.4881 | 75.1957 | 32.8564 | 47.6438 | 14.8404 | 57.7478 | 26.4909
42838.4327 | 1074 | 22.7482 | 22.76 | 22.7604 | 22.6728 | 22.2853 | 21.6177 | 22.6379 | 21.6736 | 22.2964 | 22.2995 | 22.267 | 21.8977 | 21.1326 | 22.0996 | 21.5563 | 23.1347 | 24.6787 | 28.1707 | 48.1395 | 55.1294 | 85.5355 | 89.2235 | 91.612 | 27.3845 | 57.2323 | 94.7907 | 610.4716 | 642.188 | 611.3726 | 26.3862 | 62.3113 | 100.7193 | 27.9157 | 59.855 | 98.4688 | 725.4559 | 686.6465 |  | 354.9157 | 694.9112 | 708.2637 | 673.5618 |  | 475.9075 | 689.2984 | 608.211 | 780.3486 | 903.7323 | 1009.1017 | 1026.2361 | 39.3468 | 285.8284 | 64.1607 | 512.3639 | 72.3004 | 49.5998 | 48.775 | 55.2949 | 48.3433 |  |  | 1.0753 | 0.22861 | -68.0497 | -45.3608 | 8.1497 | -197.7954 | -203.2226 | -2.7412 | 9.6433 | 33.0917 | 11.5756 | -0.00010842 | -0.00040577 | 0.00039756 | 33.0879 | 22.4251 | 22.09 | 22.1299 | 21.9299 | 21.1973 | 20.0739 | 22.1298 | 22.2994 | 22.3416 | 22.28 | 21.8822 | 21.1254 | 22.2053 | 574.5578 | 438.1411 | 348.9275 | 244.5033 | 176.4338 | 648.2948 | 380.5167 | 22.2089 | 22.6317 | 24.4535 | 22.6066 | 41.7362 | 50.6427 | 32.9592 | 83.0683 | 89.4855 | 548.9123 | 510.1079 | 514.2257 | 528.438 | 42.3341 | 19.4455 | 719.9239 | 22.3291 | 22.1314 | 355.5801 | 21.5588 | 21.9496 | 56.0566 | 88.9965 | 100.869 | 28.1391 | 65.0922 | 103.4755 | 711.0711 | 619.9141 | 710.6847 | 717.1823 | 686.725 |  | 709.6154 | 664.9318 | 787.7102 | 602.4686 | 599.8508 | 667.995 |  | 566.5741 |  |  | 454.2012 | 590.0789 | 670.6451 | [5 empty] | 21.8383 | 577.2087 | 22.189 | 22.05 | 413.8256 | 21.6365 | 21.8597 | 466.6019 | 586.9385 | 588.0823 |  | 695.6157 | 852.3629 | 489.8865 | 648.3895 | 706.7035 | 551.4577 | 611.7682 | 613.0946 | 787.6153 | 588.3813 | 697.4242 | 1121.1826 | 1092.8291 | 992.9105 | 486.6536 | 580.2774 | 598.8313 | 497.0954 | 634.3809 | 721.6369 | 1118.3741 | 1055.1918 | 542.0574 | 610.9557 | 578.5679 | 775.9991 | 44.8757 | 0.024244 | 19.4145 | 7.0751 | -28.5282 | 3.0964 | 5423.35 | -0.11 | 2.1492 | 1.0337 | -17.8348 | -14.5612 | 7.124 | -35.0963 | -35.5746 | 53.5269 | 75.2256 | 32.8611 | 49.0682 | 13.8615 | 57.826 | 26.4629
42838.4327 | 1075 | 22.7499 | 22.7601 | 22.7612 | 22.6773 | 22.2852 | 21.611 | 22.6318 | 21.6673 | 22.283 | 22.2949 | 22.2617 | 21.8927 | 21.1258 | 22.099 | 21.563 | 23.1566 | 24.7111 | 28.2516 | 48.238 | 55.2163 | 85.5685 | 89.2329 | 91.6364 | 27.4234 | 57.3141 | 94.8478 | 610.3843 | 641.9889 | 611.1111 | 26.4095 | 62.3805 | 100.7671 | 27.9445 | 59.9241 | 98.5118 | 726.2477 | 684.8461 |  | 355.2074 | 691.6617 | 704.9459 | 674.2614 |  | 476.4954 | 688.8155 | 609.8521 | 780.2661 | 909.9111 | 1011.6383 | 1030.1921 | 39.2779 | 285.8052 | 65.4178 | 512.126 | 72.3293 | 49.5747 | 48.7474 | 55.2727 | 48.3671 |  |  | 0.91953 | 1.3004 | -73.6655 | -43.2251 | 7.3401 | -197.8236 | -203.2134 | -3.0382 | 9.8702 | 32.6672 | 11.8214 | -0.00014456 | -0.00039755 | 0.0004107 | 33.1691 | 22.4364 | 22.0997 | 22.1412 | 21.9332 | 21.2056 | 20.0781 | 22.1382 | 22.2993 | 22.3469 | 22.2917 | 21.8829 | 21.1328 | 22.2118 | 548.3662 | 403.9477 | 329.5396 | 242.2967 | 177.0941 | 645.6508 | 379.0736 | 22.2145 | 22.6493 | 24.4806 | 22.6183 | 41.8381 | 50.7362 | 33.1256 | 83.1004 | 89.5303 | 549.0463 | 510.038 | 514.5878 | 528.0172 | 47.7388 | 21.622 | 719.0496 | 22.3291 | 22.1312 | 355.807 | 21.5595 | 21.9512 | 56.168 | 88.9954 | 100.9129 | 28.1923 | 65.3448 | 103.5389 | 713.0505 | 620.6757 | 710.2756 | 716.9472 | 686.8801 |  | 710.0208 | 665.1925 | 788.156 | 605.48 | 600.3422 | 668.0126 |  | 566.6257 |  |  | 455.3321 | 592.6261 | 671.8948 | [5 empty] | 21.8341 | 578.7825 | 22.1941 | 22.053 | 414.7043 | 21.6375 | 21.8627 | 467.1308 | 586.9945 | 588.2188 |  | 695.1396 | 853.4554 | 489.5219 | 647.9452 | 707.2507 | 551.8951 | 611.8628 | 612.0928 | 787.6443 | 587.4605 | 697.9475 | 1121.0875 | 1088.5225 | 992.6652 | 487.2595 | 581.154 | 598.8274 | 497.1201 | 634.9675 | 721.0375 | 1119.2389 | 1049.6598 | 542.5744 | 611.3882 | 579.0025 | 776.169 | 44.869 | -0.0020595 | 19.417 | 7.0754 | -28.5923 | 3.0965 | 5423.32 | -0.04 | 1.9872 | 2.4648 | -18.5515 | -14.2107 | 6.7676 | -35.1335 | -35.6089 | 53.6212 | 75.3515 | 32.8653 | 51.2175 | 15.7643 | 58.0076 | 26.4952
42838.4327 | 1076 | 22.7478 | 22.7544 | 22.7615 | 22.678 | 22.2901 | 21.6057 | 22.6285 | 21.6754 | 22.2897 | 22.2942 | 22.2601 | 21.8971 | 21.1192 | 22.0926 | 21.562 | 23.1721 | 24.7374 | 28.332 | 48.336 | 55.3087 | 85.5912 | 89.2329 | 91.6383 | 27.4471 | 57.4036 | 94.9023 | 609.894 | 641.1983 | 610.1549 | 26.4503 | 62.4567 | 100.8372 | 27.9935 | 60.0036 | 98.5767 | 726.5809 | 683.4153 |  | 355.3139 | 690.6783 | 704.2322 | 671.507 |  | 476.6089 | 690.1133 | 609.7066 | 779.7818 | 921.4116 | 1017.0191 | 1032.8948 | 39.359 | 285.6816 | 66.7983 | 511.9008 | 72.345 | 49.5651 | 48.7231 | 55.2769 | 48.3901 |  |  | 1.0897 | 1.1072 | -71.8866 | -44.5144 | 7.8546 | -197.8828 | -203.1484 | -2.5487 | 9.596 | 32.2319 | 11.8495 | -4.271e-05 | -0.0003877 | 0.00038606 | 33.2302 | 22.4365 | 22.0968 | 22.1411 | 21.938 | 21.2086 | 20.0792 | 22.1418 | 22.3048 | 22.3438 | 22.2878 | 21.8928 | 21.1369 | 22.2193 | 538.6341 | 402.2002 | 322.5436 | 236.0759 | 169.4202 | 643.5309 | 377.5654 | 22.2223 | 22.661 | 24.5134 | 22.6298 | 41.9351 | 50.8213 | 33.2914 | 83.1164 | 89.5801 | 549.0581 | 509.4569 | 514.1564 | 526.499 | 48.1825 | 25.4539 | 718.7245 | 22.3307 | 22.1312 | 356.1921 | 21.5632 | 21.957 | 56.2905 | 89.0014 | 100.957 | 28.2465 | 65.5917 | 103.6041 | 715.3873 | 621.8265 | 711.593 | 718.0195 | 687.0858 |  | 710.2944 | 665.4505 | 788.6844 | 608.507 | 600.9213 | 667.7302 |  | 566.6625 |  |  | 456.2034 | 594.8157 | 672.7376 | [5 empty] | 21.8302 | 580.5884 | 22.1969 | 22.0471 | 415.2028 | 21.6362 | 21.8636 | 467.5 | 587.0671 | 588.4122 |  | 693.6763 | 852.7688 | 488.9034 | 648.0228 | 706.7555 | 552.0553 | 612.4384 | 611.9696 | 788.0913 | 588.1925 | 698.5326 | 1123.0219 | 1085.94 | 989.0994 | 487.9699 | 581.6452 | 598.6414 | 497.3604 | 635.5401 | 720.3186 | 1119.1983 | 1045.4323 | 542.8918 | 611.2333 | 579.4878 | 775.7462 | 46.391 | 0.0020411 | 19.4209 | 7.0749 | -28.5369 | 3.0965 | 5437.97 | -0.08 | 2.1621 | 2.2759 | -18.3385 | -14.4308 | 7.0154 | -35.2123 | -35.6777 | 53.6821 | 75.5024 | 32.8849 | 51.6917 | 16.2795 | 58.1688 | 26.5392
42838.4327 | 1077 | 22.7531 | 22.7551 | 22.7636 | 22.6786 | 22.291 | 21.6094 | 22.6298 | 21.6748 | 22.2939 | 22.2935 | 22.2626 | 21.8984 | 21.1233 | 22.101 | 21.5598 | 23.1834 | 24.7487 | 28.4124 | 48.4265 | 55.3973 | 85.6059 | 89.229 | 91.6558 | 27.4822 | 57.4719 | 94.9483 | 609.4623 | 640.5302 | 609.3824 | 26.5 | 62.5403 | 100.9089 | 28.0349 | 60.0881 | 98.6515 | 726.3809 | 681.6561 |  | 355.2341 | 690.79 | 704.0374 | 666.5479 |  | 476.6892 | 691.0306 | 609.0836 | 778.5617 | 924.1547 | 1020.3453 | 1033.8801 | 39.3917 | 285.5094 | 67.9385 | 511.6047 | 72.3445 | 49.5439 | 48.6961 | 55.2803 | 48.4152 |  |  | 1.16 | 0.27461 | -71.5029 | -43.6273 | 7.7028 | -197.8177 | -203.1819 | -3.0106 | 9.5812 | 32.5552 | 11.8575 | -0.00015935 | -0.00039263 | 0.00040248 | 33.3078 | 22.4531 | 22.1029 | 22.1373 | 21.9362 | 21.1992 | 20.0843 | 22.1405 | 22.314 | 22.3509 | 22.2914 | 21.8913 | 21.1306 | 22.2228 | 543.1992 | 417.0216 | 327.8515 | 234.4306 | 168.5049 | 641.7892 | 376.2032 | 22.2168 | 22.6706 | 24.5406 | 22.6392 | 42.0294 | 50.9044 | 33.4406 | 83.1279 | 89.6141 | 548.892 | 508.5034 | 512.5664 | 524.3446 | 40.6823 | 18.5293 | 718.8966 | 22.334 | 22.1323 | 356.5624 | 21.5652 | 21.9513 | 56.4088 | 89.0077 | 101.0015 | 28.3019 | 65.8488 | 103.6611 | 715.3128 | 622.7875 | 713.4025 | 719.4014 | 687.3098 |  | 710.4826 | 665.6912 | 789.2206 | 610.5769 | 601.4897 | 667.4211 |  | 566.7265 |  |  | 457.7715 | 598.0029 | 673.0165 | [5 empty] | 21.8357 | 582.2057 | 22.2013 | 22.0516 | 414.9944 | 21.6364 | 21.8613 | 467.7016 | 587.4639 | 588.4816 |  | 693.7477 | 851.8341 | 488.7868 | 649.5015 | 705.993 | 552.1965 | 612.9619 | 614.0691 | 789.3182 | 590.039 | 699.4439 | 1124.3618 | 1080.5511 | 985.6645 | 488.2859 | 581.8407 | 598.5623 | 497.7565 | 635.9351 | 719.6168 | 1114.8962 | 1040.47 | 543.083 | 611.4339 | 579.5773 | 774.9167 | 44.9044 | 0.0010019 | 19.4251 | 7.0727 | -28.595 | 3.0965 | 5476.79 | -0.03 | 2.2298 | 1.134 | -18.2982 | -14.2931 | 6.9562 | -35.2519 | -35.7266 | 53.7217 | 75.6563 | 32.9294 | 50.6875 | 15.4535 | 58.2557 | 26.5735
42838.4328 | 1078 | 22.7485 | 22.758 | 22.7654 | 22.6761 | 22.2847 | 21.6129 | 22.6263 | 21.6783 | 22.2901 | 22.2868 | 22.2624 | 21.9032 | 21.1244 | 22.1022 | 21.5756 | 23.2073 | 24.7823 | 28.5085 | 48.5238 | 55.493 | 85.6247 | 89.2385 | 91.6947 | 27.5178 | 57.5584 | 95.0128 | 609.0308 | 639.3889 | 608.6836 | 26.5391 | 62.6145 | 100.9938 | 28.077 | 60.1645 | 98.7158 | 725.8849 | 679.6748 |  | 356.1656 | 688.4729 | 701.2766 | 663.0391 |  | 477.5511 | 691.4102 | 608.2961 | 782.713 | 926.1753 | 1020.8345 | 1031.6558 | 39.3591 | 285.3441 | 69.5425 | 511.248 | 72.4138 | 49.5382 | 48.6688 | 55.302 | 48.4551 |  |  | 1.0956 | 0.97247 | -72.7534 | -30.3016 | 7.3506 | -197.8374 | -203.2739 | -2.1721 | 9.2004 | 31.1558 | 11.8947 | -8.871e-05 | -0.00032856 | 0.00037949 | 33.3737 | 22.4498 | 22.0959 | 22.1314 | 21.9366 | 21.2022 | 20.0789 | 22.144 | 22.3038 | 22.3537 | 22.2933 | 21.8834 | 21.1335 | 22.2155 | 534.6271 | 400.4698 | 317.6648 | 233.6046 | 170.41 | 639.6121 | 374.6612 | 22.2095 | 22.6774 | 24.5508 | 22.6279 | 42.1255 | 50.985 | 33.5946 | 83.1287 | 89.653 | 548.7541 | 508.5154 | 512.3716 | 524.704 | 46.7932 | 21.7973 | 719.9328 | 22.3348 | 22.1358 | 357.1369 | 21.5618 | 21.953 | 56.5244 | 89.0073 | 101.0469 | 28.3579 | 66.1026 | 103.7124 | 714.0055 | 623.3988 | 715.0168 | 720.6576 | 686.2377 |  | 710.5835 | 665.9348 | 789.8408 | 610.7161 | 602.0548 | 667.6225 |  | 566.8831 |  |  | 459.1047 | 599.1983 | 672.5463 | [5 empty] | 21.8463 | 582.7948 | 22.21 | 22.0619 | 414.9846 | 21.6483 | 21.8707 | 468.0727 | 587.8954 | 588.5307 |  | 698.1394 | 852.8419 | 488.6411 | 651.4239 | 705.5171 | 552.4816 | 613.1996 | 617.4553 | 790.575 | 592.3637 | 700.3423 | 1122.0454 | 1074.5817 | 982.2174 | 488.3934 | 582.0184 | 598.693 | 497.8096 | 635.9926 | 718.282 | 1108.2572 | 1035.99 | 543.2565 | 611.4874 | 579.4292 | 774.5632 | 45.6208 | 0.00040508 | 19.4294 | 7.067 | -28.595 | 3.0965 | 5489.37 | -0.08 | 2.1662 | 2.1344 | -18.4611 | -11.9142 | 6.7966 | -35.2603 | -35.7415 | 53.7761 | 75.8356 | 33.027 | 51.0212 | 16.3186 | 58.2272 | 26.5423
42838.4328 | 1079 | 22.7462 | 22.7536 | 22.7592 | 22.6737 | 22.2871 | 21.6099 | 22.6254 | 21.6735 | 22.288 | 22.2996 | 22.258 | 21.8959 | 21.1223 | 22.0975 | 21.5783 | 23.2144 | 24.812 | 28.5816 | 48.6144 | 55.5813 | 85.6303 | 89.2475 | 91.7246 | 27.549 | 57.6318 | 95.0747 | 608.0825 | 637.89 | 607.2386 | 26.5698 | 62.6897 | 101.0651 | 28.1123 | 60.251 | 98.7687 | 725.433 | 680.8857 |  | 354.8985 | 683.5894 | 696.0717 | 663.8541 |  | 476.8941 | 690.6223 | 608.2227 | 781.8571 | 924.9097 | 1018.9668 | 1028.7063 | 39.4038 | 285.0282 | 70.6744 | 510.6834 | 72.3968 | 49.5048 | 48.6513 | 55.3086 | 48.4673 |  |  | 1.0404 | 0.92253 | -77.8671 | -28.4111 | 7.0135 | -197.8539 | -203.1747 | -2.987 | 9.5709 | 31.8345 | 11.785 | 2.464e-05 | -0.00038605 | 0.0003992 | 33.4471 | 22.4519 | 22.0956 | 22.1407 | 21.9355 | 21.2048 | 20.0847 | 22.1429 | 22.3107 | 22.3449 | 22.2871 | 21.8927 | 21.1405 | 22.2151 | 540.2588 | 402.9598 | 332.1885 | 242.4678 | 177.2229 | 637.7608 | 373.5785 | 22.2139 | 22.6847 | 24.5798 | 22.6446 | 42.2195 | 51.0754 | 33.7488 | 83.1393 | 89.6906 | 548.6516 | 508.0274 | 511.4445 | 523.5989 | 44.6146 | 23.2356 | 720.9851 | 22.3487 | 22.1306 | 357.9831 | 21.5656 | 21.9511 | 56.641 | 88.9991 | 101.0984 | 28.4188 | 66.3501 | 103.7742 | 713.9837 | 624.3122 | 719.5866 | 724.0976 | 686.0708 |  | 710.6457 | 666.275 | 790.7402 | 611.9322 | 602.671 | 668.011 |  | 567.0483 |  |  | 458.8511 | 597.8702 | 671.8612 | [5 empty] | 21.8365 | 583.9799 | 22.2131 | 22.0437 | 413.8664 | 21.6431 | 21.8526 | 468.6287 | 588.3483 | 588.5703 |  | 700.42 | 854.4345 | 489.1942 | 652.8535 | 705.7657 | 553.1645 | 613.2941 | 626.2512 | 789.8279 | 593.1275 | 701.827 | 1113.3857 | 1069.5768 | 980.351 | 488.7191 | 582.0095 | 598.7726 | 497.6577 | 636.0741 | 716.075 | 1103.0125 | 1031.5843 | 543.2681 | 611.324 | 579.5178 | 774.6558 | 44.9435 | 0.0011915 | 19.4359 | 7.0546 | -28.5409 | 3.0965 | 5419.85 | -0.04 | 2.1092 | 2.078 | -19.0911 | -11.5318 | 6.6342 | -35.2363 | -35.7069 | 53.7959 | 76.0964 | 33.1042 | 49.8715 | 14.518 | 58.0898 | 26.5572
42838.4328 | 1080 | 22.7539 | 22.7532 | 22.7668 | 22.6698 | 22.2884 | 21.6116 | 22.6284 | 21.6727 | 22.2946 | 22.2923 | 22.262 | 21.8995 | 21.1222 | 22.0982 | 21.5713 | 23.2264 | 24.834 | 28.6641 | 48.7101 | 55.6637 | 85.6504 | 89.2433 | 91.7448 | 27.5832 | 57.7091 | 95.1312 | 606.9872 | 636.7642 | 606.2293 | 26.6121 | 62.7694 | 101.1324 | 28.1609 | 60.3289 | 98.8396 | 725.5618 | 682.5734 |  | 357.31 | 680.1028 | 692.6415 | 666.7782 |  | 476.8078 | 690.1166 | 609.8085 | 786.319 | 926.7653 | 1020.091 | 1027.1409 | 39.4708 | 284.7066 | 71.297 | 510.2515 | 72.4019 | 49.4743 | 48.6194 | 55.3057 | 48.4864 |  |  | 1.0956 | -0.10652 | -88.4275 | -27.5812 | 6.8263 | -197.8447 | -203.2437 | -2.7313 | 9.0646 | 31.079 | 12.124 | -0.00016921 | -0.00049119 | 0.00036963 | 33.5144 | 22.455 | 22.0982 | 22.1362 | 21.9332 | 21.2007 | 20.0797 | 22.1369 | 22.3139 | 22.3413 | 22.2868 | 21.8878 | 21.1386 | 22.2155 | 534.8736 | 401.1931 | 329.7718 | 249.5182 | 189.8325 | 635.5676 | 372.4075 | 22.2139 | 22.6948 | 24.599 | 22.6529 | 42.306 | 51.1628 | 33.884 | 83.1467 | 89.7306 | 548.498 | 506.0971 | 510.0532 | 523.0453 | 43.2247 | 18.0569 | 722.6259 | 22.3532 | 22.1283 | 358.646 | 21.5675 | 21.9483 | 56.7538 | 88.9931 | 101.1517 | 28.4795 | 66.5907 | 103.8329 | 714.3273 | 624.8251 | 725.4977 | 728.9545 | 686.7325 |  | 710.7276 | 666.5286 | 791.641 | 613.1724 | 603.2662 | 668.4279 |  | 567.0979 |  |  | 457.9701 | 597.3552 | 671.908 | [5 empty] | 21.8379 | 585.3772 | 22.2176 | 22.038 | 413.5314 | 21.6474 | 21.859 | 469.1975 | 588.839 | 588.6854 |  | 704.0327 | 854.8469 | 490.5391 | 653.2276 | 706.669 | 553.7347 | 613.9521 | 628.2683 | 790.0964 | 593.8326 | 702.6993 | 1111.9003 | 1065.8962 | 976.0395 | 488.6442 | 581.6591 | 598.4914 | 498.2015 | 636.0297 | 714.9781 | 1102.9576 | 1027.7254 | 543.1408 | 610.8552 | 579.9067 | 774.3288 | 44.2596 | 0.0011775 | 19.4429 | 7.0406 | -28.5151 | 3.0965 | 5353.97 | -0.11 | 2.1632 | -0.70591 | -20.3392 | -11.3592 | 6.5478 | -35.2508 | -35.7285 | 53.7975 | 76.3607 | 33.177 | 49.8515 | 14.5847 | 58.0413 | 26.549
42838.4328 | 1081 | 22.7495 | 22.7495 | 22.7595 | 22.6823 | 22.287 | 21.6074 | 22.6288 | 21.673 | 22.2918 | 22.3005 | 22.2636 | 21.9018 | 21.1196 | 22.1073 | 21.5822 | 23.2553 | 24.8631 | 28.7458 | 48.8062 | 55.7562 | 85.6621 | 89.2553 | 91.7934 | 27.6156 | 57.7908 | 95.196 | 606.7126 | 636.7579 | 606.4457 | 26.6466 | 62.8424 | 101.2188 | 28.1943 | 60.4137 | 98.8951 | 725.3097 | 683.2956 |  | 370.6901 | 680.2311 | 693.2312 | 665.3744 |  | 476.8826 | 690.0716 | 609.9751 | 784.6305 | 929.576 | 1018.9377 | 1027.2967 | 39.4306 | 284.2114 | 70.6334 | 509.6741 | 72.43 | 49.4711 | 48.6026 | 55.3329 | 48.5227 |  |  | 1.1186 | -0.31154 | -45.33 | -24.9336 | 7.7469 | -197.8539 | -203.1779 | -2.3338 | 8.9838 | 29.9002 | 12.2332 | -0.00015935 | -0.00035156 | 0.00041727 | 33.5804 | 22.4608 | 22.0946 | 22.1378 | 21.9275 | 21.2005 | 20.0777 | 22.1314 | 22.3078 | 22.3474 | 22.2803 | 21.8911 | 21.1339 | 22.2164 | 531.1944 | 406.6289 | 330.5985 | 245.2014 | 188.9636 | 633.4898 | 371.0477 | 22.2037 | 22.7043 | 24.6271 | 22.6594 | 42.4037 | 51.2441 | 34.0248 | 83.1482 | 89.7724 | 548.4171 | 505.8174 | 509.8959 | 523.5825 | 42.9791 | 22.1602 | 724.3195 | 22.3583 | 22.1297 | 358.997 | 21.5678 | 21.951 | 56.8729 | 88.9858 | 101.1956 | 28.5303 | 66.8437 | 103.8843 | 714.0175 | 625.0304 | 729.8723 | 732.6662 | 686.2172 |  | 710.7563 | 666.5219 | 792.2657 | 612.0088 | 603.7318 | 668.7846 |  | 567.2835 |  |  | 457.5065 | 596.7449 | 671.7216 | [5 empty] | 21.8347 | 585.4779 | 22.2265 | 22.0491 | 413.0382 | 21.6565 | 21.8601 | 469.4054 | 589.7617 | 588.9994 |  | 704.5674 | 856.6158 | 492.0995 | 653.6154 | 707.1461 | 554.1555 | 614.8318 | 629.344 | 792.4933 | 594.905 | 702.6013 | 1112.4741 | 1065.0643 | 972.4123 | 488.06 | 581.1296 | 597.7983 | 498.583 | 635.6094 | 715.6224 | 1102.5095 | 1024.6646 | 543.2019 | 610.5209 | 580.2445 | 774.0982 | 45.6421 | 0.0024203 | 19.447 | 7.0294 | -28.5795 | 3.0964 | 5274.08 | -0.09 | 2.186 | -1.2072 | -14.5621 | -10.8 | 6.9723 | -35.2359 | -35.7068 | 53.8188 | 76.5495 | 33.2934 | 49.677 | 14.2591 | 58.0163 | 26.5217
42838.4328 | 1082 | 22.7417 | 22.7592 | 22.7594 | 22.6755 | 22.2815 | 21.6155 | 22.6305 | 21.6746 | 22.2868 | 22.2993 | 22.26 | 21.9034 | 21.1182 | 22.0981 | 21.5868 | 23.2674 | 24.8948 | 28.8335 | 48.9082 | 55.853 | 85.6874 | 89.2767 | 91.8305 | 27.652 | 57.8656 | 95.2534 | 607.2287 | 636.9432 | 607.3052 | 26.7012 | 62.9216 | 101.3423 | 28.2443 | 60.4938 | 98.9494 | 725.3029 | 683.6025 |  | 358.6811 | 678.9989 | 691.7676 | 668.1158 |  | 475.0639 | 689.1677 | 609.3461 | 784.5014 | 927.2113 | 1017.0955 | 1027.8616 | 39.6435 | 283.8174 | 69.5842 | 509.3981 | 72.4423 | 49.4639 | 48.5722 | 55.332 | 48.5489 |  |  | 1.1154 | 0.25358 | -38.5656 | -21.1211 | 7.5346 | -197.8861 | -203.1057 | -3.1295 | 9.1998 | 30.9892 | 12.1669 | 8.22e-06 | -0.0004107 | 0.00045834 | 33.6461 | 22.4601 | 22.094 | 22.13 | 21.9199 | 21.1933 | 20.0733 | 22.1272 | 22.2974 | 22.3442 | 22.2724 | 21.8907 | 21.1305 | 22.2065 | 538.614 | 407.4268 | 336.7957 | 241.6738 | 189.0369 | 631.615 | 369.733 | 22.2112 | 22.7102 | 24.6519 | 22.6631 | 42.4932 | 51.3304 | 34.1644 | 83.1567 | 89.8135 | 548.2934 | 506.1262 | 509.9213 | 522.9597 | 52.0658 | 16.7941 | 725.1001 | 22.3541 | 22.1175 | 359.2009 | 21.566 | 21.946 | 56.9843 | 88.9697 | 101.2227 | 28.5768 | 67.0914 | 103.9214 | 713.307 | 625.8123 | 732.5198 | 734.6968 | 686.6356 |  | 710.8661 | 666.6093 | 792.8268 | 612.4704 | 604.2577 | 669.0368 |  | 567.571 |  |  | 457.7124 | 595.2842 | 672.2484 | [5 empty] | 21.8304 | 585.915 | 22.2209 | 22.0478 | 412.9681 | 21.6553 | 21.8561 | 469.6045 | 590.8276 | 589.1404 |  | 707.1111 | 857.6318 | 493.0158 | 654.916 | 707.612 | 554.6171 | 615.6875 | 630.3846 | 795.6198 | 595.8958 | 702.9603 | 1114.2899 | 1064.8793 | 970.0231 | 488.1928 | 581.0659 | 597.4315 | 498.867 | 634.9834 | 716.2351 | 1100.7971 | 1023.1181 | 543.368 | 610.9569 | 580.3227 | 773.7227 | 46.8039 | 0.00063683 | 19.4514 | 7.0117 | -28.5919 | 3.0965 | 5221.94 | -0.07 | 2.1839 | 1.0886 | -13.4254 | -9.9354 | 6.8712 | -35.2136 | -35.675 | 53.8339 | 76.7167 | 33.3757 | 48.3284 | 13.345 | 57.9385 | 26.52
42838.4328 | 1083 | 22.7472 | 22.7616 | 22.7627 | 22.6778 | 22.2913 | 21.6142 | 22.6313 | 21.6706 | 22.2928 | 22.2916 | 22.2613 | 21.9049 | 21.1194 | 22.1008 | 21.5833 | 23.2815 | 24.9089 | 28.9077 | 48.9935 | 55.9322 | 85.6985 | 89.2878 | 91.865 | 27.682 | 57.9442 | 95.3181 | 607.6769 | 636.3927 | 607.7651 | 26.735 | 62.9856 | 101.4178 | 28.282 | 60.5684 | 98.9932 | 725.4808 | 683.8127 |  | 357.484 | 677.8674 | 690.737 | 670.9559 |  | 474.9247 | 688.7915 | 608.3075 | 789.6994 | 929.8191 | 1018.3057 | 1027.0408 | 39.8924 | 283.3519 | 67.8882 | 508.9096 | 72.3761 | 49.4253 | 48.5417 | 55.3259 | 48.5668 |  |  | 1.0326 | 0.39815 | -39.0282 | -9.0853 | 8.0892 | -197.8 | -203.2647 | -2.5007 | 8.855 | 30.2478 | 12.0594 | -7.885e-05 | -0.00044191 | 0.00040906 | 33.7127 | 22.4713 | 22.0963 | 22.1343 | 21.9283 | 21.1969 | 20.0793 | 22.1294 | 22.3099 | 22.3442 | 22.2879 | 21.8902 | 21.1296 | 22.2065 | 539.5846 | 406.626 | 320.972 | 224.0748 | 178.5541 | 630.0186 | 368.0645 | 22.2234 | 22.7236 | 24.6776 | 22.6743 | 42.5984 | 51.4258 | 34.3361 | 83.1664 | 89.867 | 548.0353 | 505.5319 | 509.0724 | 520.9367 | 47.0503 | 18.1289 | 725.5148 | 22.3643 | 22.1225 | 359.3351 | 21.5686 | 21.9518 | 57.0967 | 88.9661 | 101.2788 | 28.6487 | 67.3507 | 103.9725 | 713.8826 | 626.8118 | 733.448 | 735.321 | 686.6993 |  | 710.9639 | 666.8815 | 793.4982 | 614.9608 | 604.8204 | 668.9896 |  | 567.761 |  |  | 458.1082 | 594.1322 | 672.7296 | [5 empty] | 21.8292 | 587.1752 | 22.2242 | 22.0476 | 413.9204 | 21.6583 | 21.8548 | 469.9885 | 591.1968 | 589.3627 |  | 711.2932 | 859.685 | 492.8771 | 655.6879 | 708.2508 | 554.9416 | 615.6453 | 630.7656 | 798.4236 | 596.3612 | 704.0824 | 1112.0402 | 1064.7723 | 969.8514 | 488.488 | 581.4326 | 597.87 | 499.0988 | 634.2393 | 716.7305 | 1096.6631 | 1023.0859 | 543.7127 | 611.7071 | 580.2843 | 773.391 | 45.559 | 0.00037702 | 19.4574 | 6.9996 | -28.5989 | 3.0965 | 5185.64 | -0.09 | 2.1018 | 1.3638 | -13.503 | -6.515 | 7.123 | -35.2225 | -35.7057 | 53.856 | 76.9124 | 33.4084 | 47.7757 | 14.8176 | 57.9047 | 26.5366
42838.4328 | 1084 | 22.7467 | 22.7518 | 22.7565 | 22.6685 | 22.278 | 21.6058 | 22.6237 | 21.6728 | 22.286 | 22.2905 | 22.2572 | 21.8919 | 21.1147 | 22.0998 | 21.5891 | 23.3048 | 24.9424 | 28.9955 | 49.086 | 56.0217 | 85.711 | 89.3081 | 91.9076 | 27.7249 | 58.0232 | 95.3896 | 607.8051 | 635.2144 | 607.9558 | 26.7757 | 63.0653 | 101.4967 | 28.3239 | 60.6483 | 99.0508 | 725.5832 | 683.837 |  | 356.5971 | 677.5965 | 690.3646 | 672.6809 |  | 475.1136 | 689.1355 | 606.7853 | 784.9326 | 925.8695 | 1017.9615 | 1027.1353 | 40.1202 | 282.8066 | 65.9245 | 508.1882 | 72.4472 | 49.3683 | 48.5188 | 55.3207 | 48.5833 |  |  | 0.90508 | 0.42838 | -40.1361 | -8.2988 | 8.2397 | -197.8309 | -203.2942 | -2.5125 | 8.8209 | 29.8538 | 11.8792 | -0.00012649 | -0.00042712 | 0.00041727 | 33.7972 | 22.4805 | 22.1062 | 22.1392 | 21.933 | 21.2032 | 20.0763 | 22.1403 | 22.2989 | 22.3535 | 22.2879 | 21.8881 | 21.1354 | 22.2176 | 530.2563 | 393.3795 | 310.7176 | 216.8291 | 171.5026 | 627.8336 | 366.399 | 22.2098 | 22.7243 | 24.6909 | 22.6699 | 42.6814 | 51.4968 | 34.4757 | 83.1679 | 89.8979 | 547.7933 | 505.4024 | 508.9453 | 520.5515 | 42.108 | 16.5923 | 726.3178 | 22.3701 | 22.1296 | 359.6876 | 21.5663 | 21.9542 | 57.2013 | 88.9742 | 101.3347 | 28.7016 | 67.6019 | 104.0109 | 716.5911 | 627.5216 | 735.0642 | 736.8039 | 688.1467 |  | 711.1355 | 667.2154 | 794.2899 | 615.4966 | 605.3592 | 669.1397 |  | 567.9054 |  |  | 458.2794 | 593.9262 | 673.2439 | [5 empty] | 21.8333 | 588.3568 | 22.2311 | 22.0566 | 414.9063 | 21.6702 | 21.8578 | 470.258 | 591.052 | 589.5049 |  | 713.1397 | 861.6323 | 492.416 | 656.1707 | 709.4545 | 554.8846 | 615.4848 | 631.3621 | 799.8644 | 596.492 | 705.1016 | 1110.8119 | 1063.2976 | 968.6875 | 488.8964 | 582.2629 | 598.5 | 499.3639 | 633.5236 | 715.8601 | 1095.8635 | 1023.425 | 544.0691 | 612.8652 | 580.2767 | 772.7244 | 46.9948 | -0.00013555 | 19.466 | 6.991 | -28.5871 | 3.0964 | 5161.84 | -0.08 | 1.968 | 1.4149 | -13.6958 | -6.2277 | 7.1879 | -35.2205 | -35.7036 | 53.8577 | 77.1432 | 33.4913 | 48.2057 | 15.6727 | 57.8827 | 26.5102
42838.4328 | 1085 | 22.7509 | 22.7542 | 22.7571 | 22.6795 | 22.2824 | 21.6092 | 22.6276 | 21.6711 | 22.2884 | 22.2917 | 22.2548 | 21.9009 | 21.122 | 22.1029 | 21.6001 | 23.3297 | 24.9679 | 29.0838 | 49.1814 | 56.1155 | 85.7331 | 89.327 | 91.9494 | 27.7629 | 58.0992 | 95.4566 | 607.6094 | 634.2466 | 607.9069 | 26.8151 | 63.1378 | 101.5906 | 28.3691 | 60.7279 | 99.1117 | 725.5799 | 682.7895 |  | 356.0327 | 676.2821 | 688.9638 | 672.3995 |  | 474.4052 | 689.8021 | 607.8683 | 789.0655 | 929.8103 | 1018.9284 | 1027.2286 | 40.5706 | 282.4084 | 63.7619 | 507.4259 | 72.4601 | 49.308 | 48.499 | 55.307 | 48.601 |  |  | 0.83871 | 0.21941 | -67.409 | -8.9946 | 7.9368 | -197.796 | -203.218 | -3.004 | 8.8614 | 30.5235 | 12.0634 | -0.00010514 | -0.00042055 | 0.00040413 | 33.8665 | 22.4794 | 22.0971 | 22.1295 | 21.9327 | 21.1998 | 20.0741 | 22.1351 | 22.3004 | 22.3562 | 22.2867 | 21.889 | 21.1353 | 22.208 | 516.39 | 390.514 | 288.7874 | 205.7447 | 163.0341 | 625.4716 | 364.7892 | 22.213 | 22.7389 | 24.7178 | 22.6783 | 42.7784 | 51.5836 | 34.6329 | 83.1806 | 89.9421 | 547.7118 | 505.2804 | 511.3211 | 521.9866 | 40.1446 | 12.5397 | 727.3628 | 22.3752 | 22.1338 | 360.0571 | 21.5636 | 21.9503 | 57.3122 | 88.9752 | 101.3778 | 28.7615 | 67.8566 | 104.0621 | 718.8119 | 628.5487 | 735.4731 | 737.3929 | 690.5418 |  | 711.615 | 667.6741 | 795.4295 | 616.9118 | 606.0303 | 669.622 |  | 567.9182 |  |  | 458.7481 | 594.6016 | 674.9431 | [5 empty] | 21.8275 | 589.3419 | 22.238 | 22.0476 | 415.2641 | 21.6691 | 21.8591 | 470.459 | 591.0693 | 589.8084 |  | 714.8086 | 864.003 | 492.3031 | 655.4797 | 709.9099 | 554.8965 | 616.005 | 635.2513 | 801.5654 | 595.3849 | 704.0111 | 1107.2079 | 1059.4837 | 967.3361 | 489.3506 | 583.6205 | 598.5916 | 499.5625 | 633.4599 | 716.0306 | 1092.8639 | 1020.518 | 544.5933 | 613.4158 | 580.4457 | 772.5738 | 45.4989 | 8.2079e-05 | 19.4731 | 6.981 | -28.5035 | 3.0965 | 5191.59 | -0.07 | 1.8944 | 1.013 | -17.7553 | -6.4858 | 7.0572 | -35.2306 | -35.7102 | 53.9082 | 77.477 | 33.574 | 49.0937 | 17.8354 | 57.8897 | 26.4578
42838.4328 | 1086 | 22.735 | 22.7488 | 22.7515 | 22.6684 | 22.2777 | 21.5993 | 22.6233 | 21.6597 | 22.2863 | 22.2867 | 22.2532 | 21.8919 | 21.1146 | 22.0914 | 21.5986 | 23.3479 | 24.9943 | 29.1689 | 49.2725 | 56.2036 | 85.752 | 89.3409 | 91.9801 | 27.7964 | 58.1671 | 95.5289 | 607.38 | 633.5024 | 607.5479 | 26.8516 | 63.1977 | 101.6779 | 28.4111 | 60.7967 | 99.1724 | 725.4784 | 681.5639 |  | 357.6328 | 675.6759 | 688.8129 | 671.4445 |  | 474.1776 | 690.4872 | 609.8202 | 797.4176 | 936.2823 | 1020.9228 | 1027.6151 | 40.7826 | 281.8814 | 63.4923 | 506.4242 | 72.4907 | 49.2511 | 48.4778 | 55.2775 | 48.6179 |  |  | 1.0135 | 0.59331 | -46.5279 | -9.0091 | 7.5478 | -197.8223 | -203.1247 | -2.9061 | 9.0869 | 31.0778 | 12.0547 | -3.45e-05 | -0.00043534 | 0.00042548 | 33.9397 | 22.4806 | 22.0943 | 22.1243 | 21.9349 | 21.2032 | 20.0824 | 22.1374 | 22.3053 | 22.347 | 22.2862 | 21.8939 | 21.1358 | 22.2094 | 513.3436 | 372.161 | 266.2172 | 196.8136 | 157.1093 | 623.1896 | 362.9631 | 22.2215 | 22.7609 | 24.7521 | 22.7008 | 42.8791 | 51.6756 | 34.7975 | 83.2011 | 89.9949 | 547.7892 | 507.3039 | 513.8024 | 524.3743 | 31.8638 | 16.5121 | 728.6566 | 22.381 | 22.1293 | 360.2928 | 21.5663 | 21.9503 | 57.4298 | 88.9715 | 101.4196 | 28.8332 | 68.1078 | 104.1256 | 718.7482 | 629.5974 | 734.4073 | 736.5941 | 691.1231 |  | 711.8965 | 667.915 | 796.3793 | 619.3309 | 606.7244 | 670.0367 |  | 568.0485 |  |  | 458.9559 | 595.689 | 676.0594 | [5 empty] | 21.8308 | 590.6591 | 22.2413 | 22.0466 | 415.6099 | 21.6722 | 21.8687 | 471.012 | 591.0999 | 590.4558 |  | 718.3762 | 867.1923 | 492.3185 | 653.1325 | 709.2906 | 555.1043 | 616.5766 | 645.0138 | 803.7495 | 593.5566 | 700.8695 | 1101.3937 | 1056.3034 | 965.1442 | 489.8896 | 584.6788 | 598.6379 | 499.8846 | 633.9487 | 715.8845 | 1090.6355 | 1019.5767 | 545.1348 | 613.5487 | 580.6772 | 772.9016 | 45.3008 | -0.00024088 | 19.4806 | 6.9668 | -28.4909 | 3.0964 | 5220.41 | -0.09 | 2.0821 | 1.6663 | -14.7564 | -6.4933 | 6.8874 | -35.2601 | -35.7296 | 53.9609 | 77.7599 | 33.6331 | 48.8045 | 20.0332 | 57.8905 | 26.4034
42838.4329 | 1087 | 22.7497 | 22.7418 | 22.7575 | 22.6854 | 22.2841 | 21.6092 | 22.628 | 21.6701 | 22.2913 | 22.2926 | 22.2604 | 21.8968 | 21.1241 | 22.0945 | 21.6051 | 23.362 | 25.0216 | 29.257 | 49.3634 | 56.2917 | 85.7709 | 89.3635 | 92.0152 | 27.8326 | 58.2367 | 95.5993 | 607.2206 | 633.3058 | 607.3695 | 26.897 | 63.2718 | 101.7634 | 28.4493 | 60.8827 | 99.2272 | 725.3009 | 681.4296 |  | 356.8696 | 677.4424 | 690.7864 | 668.0369 |  | 474.5172 | 691.4299 | 609.1502 | 798.5093 | 936.6992 | 1020.5155 | 1027.1815 | 40.5259 | 281.5207 | 65.4292 | 505.8476 | 72.4993 | 49.1927 | 48.4489 | 55.2681 | 48.6315 |  |  | 0.96553 | 0.45794 | -43.5426 | -8.9243 | 7.4387 | -197.7954 | -203.2095 | -3.0218 | 8.919 | 30.4668 | 11.9393 | 2.957e-05 | -0.00037455 | 0.00039427 | 34.0045 | 22.4857 | 22.0923 | 22.125 | 21.9283 | 21.1924 | 20.0755 | 22.1319 | 22.3071 | 22.3395 | 22.2848 | 21.8864 | 21.1242 | 22.2046 | 494.4784 | 352.3307 | 270.1275 | 198.5536 | 155.5671 | 620.0163 | 361.1622 | 22.2225 | 22.7636 | 24.7816 | 22.7043 | 42.9678 | 51.7559 | 34.9707 | 83.2186 | 90.0364 | 547.8641 | 508.9685 | 513.5081 | 525.5465 | 34.4587 | 17.3155 | 730.0454 | 22.3849 | 22.1289 | 361.0705 | 21.5697 | 21.9479 | 57.5372 | 88.9689 | 101.4663 | 28.8943 | 68.3492 | 104.1753 | 717.6205 | 630.2005 | 736.4089 | 738.4208 | 690.1758 |  | 712.0979 | 668.0769 | 797.2025 | 620.3509 | 607.387 | 670.3265 |  | 568.1498 |  |  | 459.2439 | 596.1328 | 675.9081 | [5 empty] | 21.8371 | 591.5422 | 22.2437 | 22.0491 | 415.4814 | 21.6712 | 21.8635 | 471.7447 | 590.9604 | 590.8642 |  | 724.5962 | 869.9078 | 492.6259 | 650.7469 | 708.885 | 555.2612 | 616.9125 | 657.1128 | 805.3493 | 592.4718 | 699.2991 | 1102.0544 | 1057.4049 | 965.1897 | 490.3481 | 584.9648 | 598.7777 | 500.3396 | 634.8631 | 715.5085 | 1089.3071 | 1019.2634 | 545.2914 | 735.9537 | 581.065 | 773.4135 | 46.4619 | -0.00045856 | 19.4888 | 6.9465 | -28.5788 | 3.0965 | 5270.93 | -0.14 | 2.032 | 1.4647 | -14.2821 | -6.4658 | 6.8364 | -35.2522 | -35.7314 | 54.0365 | 78.007 | 33.7257 | 50.0325 | 19.294 | 57.9401 | 26.3823
42838.4329 | 1088 | 22.7455 | 22.7457 | 22.7596 | 22.6683 | 22.2798 | 21.6143 | 22.6329 | 21.6653 | 22.2814 | 22.284 | 22.2573 | 21.9021 | 21.1195 | 22.0948 | 21.5992 | 23.3822 | 25.047 | 29.3351 | 49.4593 | 56.3677 | 85.7806 | 89.3755 | 92.0451 | 27.8557 | 58.3114 | 95.6523 | 607.22 | 633.3195 | 607.671 | 26.9324 | 63.3541 | 101.8184 | 28.5017 | 60.9688 | 99.2975 | 724.3558 | 681.1978 |  | 356.2168 | 677.2331 | 690.6884 | 661.6444 |  | 475.2764 | 692.3016 | 607.7199 | 797.3316 | 932.6104 | 1020.5905 | 1027.1148 | 40.4825 | 281.1917 | 66.131 | 505.4671 | 72.4629 | 49.1575 | 48.427 | 55.2723 | 48.648 |  |  | 0.98853 | 0.24176 | -47.6962 | -8.7535 | 7.6161 | -197.8256 | -203.1832 | -3.1578 | 8.9894 | 30.4467 | 11.6813 | -0.00010349 | -0.00040412 | 0.00039263 | 34.078 | 22.4921 | 22.0946 | 22.1317 | 21.9322 | 21.1951 | 20.0755 | 22.13 | 22.3091 | 22.3406 | 22.2905 | 21.8878 | 21.1321 | 22.2115 | 466.7642 | 347.7646 | 275.9725 | 194.8163 | 153.0258 | 616.8338 | 359.4128 | 22.2148 | 22.7679 | 24.7983 | 22.7099 | 43.0671 | 51.8365 | 35.1704 | 83.2451 | 90.0864 | 547.864 | 509.8589 | 513.2998 | 525.3172 | 32.6042 | 13.7334 | 731.5795 | 22.3875 | 22.1283 | 362.1903 | 21.5702 | 21.9452 | 57.642 | 88.9641 | 101.5097 | 28.9478 | 68.6 | 104.2167 | 717.1152 | 630.3386 | 741.6213 | 742.8809 | 690.3286 |  | 712.2584 | 668.3725 | 798.1008 | 616.7257 | 607.7796 | 670.4379 |  | 568.6339 |  |  | 459.2447 | 594.669 | 675.5678 | [5 empty] | 21.8392 | 591.0018 | 22.2594 | 22.0536 | 414.958 | 21.6804 | 21.8617 | 472.0679 | 591.0734 | 590.7286 |  | 730.8884 | 870.8165 | 493.1377 | 650.2508 | 709.2644 | 555.613 | 616.9899 | 667.3499 | 807.6305 | 592.4377 | 700.2864 | 1100.1605 | 1056.3984 | 964.7283 | 490.3785 | 584.5869 | 598.8413 | 500.5876 | 635.8 | 715.4943 | 1087.5768 | 1015.4463 | 545.0283 | 810.7887 | 581.3852 | 773.5936 | 45.1895 | -0.001561 | 19.4958 | 6.9255 | -28.5444 | 3.0965 | 5274.34 | 0.01 | 2.0564 | 1.0647 | -14.9546 | -6.4065 | 6.9176 | -35.2559 | -35.7301 | 54.0715 | 78.2738 | 33.8981 | 52.2467 | 18.3493 | 57.8784 | 26.3886
42838.4329 | 1089 | 22.7508 | 22.7574 | 22.7462 | 22.6701 | 22.2848 | 21.6093 | 22.6247 | 21.6696 | 22.2886 | 22.296 | 22.2633 | 21.9008 | 21.1194 | 22.0981 | 21.5962 | 23.4013 | 25.0651 | 29.4184 | 49.5435 | 56.448 | 85.7945 | 89.3914 | 92.0838 | 27.8919 | 58.3926 | 95.7078 | 607.6143 | 633.1765 | 608.2328 | 26.9837 | 63.4229 | 101.8641 | 28.5391 | 61.046 | 99.3627 | 723.7234 | 680.9082 |  | 357.7345 | 674.5828 | 688.0008 | 659.3398 |  | 475.9527 | 692.6313 | 607.2875 | 796.863 | 928.3069 | 1020.1197 | 1026.7125 | 40.1091 | 280.7532 | 64.4634 | 505.0717 | 72.4972 | 49.1595 | 48.4011 | 55.2726 | 48.6667 |  |  | 1.0641 | 0.62748 | -48.8633 | -9.201 | 7.7764 | -197.848 | -203.2292 | -2.9764 | 9.0677 | 30.8642 | 11.8974 | -0.00019549 | -0.00051912 | 0.00042713 | 34.1523 | 22.5004 | 22.0922 | 22.1378 | 21.9329 | 21.201 | 20.0772 | 22.131 | 22.3119 | 22.3409 | 22.2861 | 21.8919 | 21.1366 | 22.211 | 453.7788 | 344.0329 | 266.7978 | 193.3386 | 155.6022 | 614.1682 | 357.6504 | 22.2118 | 22.7797 | 24.8246 | 22.7168 | 43.1536 | 51.9205 | 35.3562 | 83.2674 | 90.1321 | 547.8352 | 510.4771 | 513.6864 | 525.3128 | 41.2485 | 20.8186 | 733.2124 | 22.3928 | 22.1285 | 363.1037 | 21.5716 | 21.9463 | 57.7469 | 88.9666 | 101.5454 | 29.0183 | 68.8577 | 104.2676 | 715.2764 | 630.2846 | 745.5338 | 745.969 | 689.8296 |  | 712.3014 | 668.6643 | 799.0406 | 613.516 | 608.0045 | 671.02 |  | 569.1258 |  |  | 459.235 | 592.4029 | 674.8108 | [5 empty] | 21.8399 | 589.7909 | 22.2711 | 22.056 | 415.6698 | 21.6861 | 21.8649 | 472.2031 | 591.5241 | 590.3375 |  | 737.377 | 873.0193 | 493.7986 | 651.3051 | 709.8412 | 556.1049 | 617.0704 | 671.0839 | 809.5782 | 592.5241 | 701.3148 | 1098.7306 | 1055.8253 | 963.224 | 490.3286 | 584.1845 | 599.0145 | 500.7194 | 636.4387 | 715.0348 | 1087.4487 | 1012.7194 | 544.7022 | 672.9012 | 581.7564 | 773.5161 | 44.2871 | -0.00014963 | 19.5038 | 6.9058 | -28.5374 | 3.0965 | 5302.69 | -0.12 | 2.1342 | 1.7156 | -15.139 | -6.5694 | 6.9888 | -35.2515 | -35.7277 | 54.0959 | 78.5542 | 34.0284 | 52.969 | 19.0721 | 57.7826 | 26.3844
42838.4329 | 1090 | 22.741 | 22.7509 | 22.7498 | 22.6633 | 22.2795 | 21.6062 | 22.6198 | 21.6669 | 22.2854 | 22.2899 | 22.2541 | 21.8993 | 21.1201 | 22.0969 | 21.6163 | 23.4203 | 25.0979 | 29.4988 | 49.6383 | 56.536 | 85.8206 | 89.4128 | 92.1382 | 27.9292 | 58.4599 | 95.7786 | 608.0372 | 633.5078 | 608.6076 | 27.027 | 63.4889 | 101.9229 | 28.5836 | 61.1229 | 99.4213 | 723.062 | 683.1364 |  | 360.8444 | 673.717 | 687.4425 | 656.8206 |  | 476.1135 | 693.3374 | 606.1885 | 797.5946 | 925.393 | 1018.5435 | 1026.8437 | 40.0375 | 280.2895 | 62.8459 | 504.3957 | 72.5475 | 49.1482 | 48.3835 | 55.2762 | 48.6936 |  |  | 1.2238 | -0.050005 | -53.3349 | -8.9434 | 8.5499 | -197.8243 | -203.1996 | -2.6873 | 8.9332 | 30.3672 | 12.0667 | -8.05e-05 | -0.00042055 | 0.00041563 | 34.2258 | 22.5088 | 22.0947 | 22.1346 | 21.9235 | 21.1957 | 20.0736 | 22.1355 | 22.3056 | 22.3417 | 22.2818 | 21.8871 | 21.1314 | 22.2098 | 460.7182 | 367.445 | 293.4223 | 201.2215 | 155.0015 | 612.2189 | 356.3292 | 22.2119 | 22.791 | 24.8484 | 22.7242 | 43.2438 | 52.0027 | 35.5577 | 83.2912 | 90.1764 | 547.8119 | 510.1898 | 513.6827 | 525.355 | 43.3478 | 18.3176 | 734.82 | 22.3958 | 22.1222 | 363.7281 | 21.5705 | 21.9474 | 57.8523 | 88.9663 | 101.5785 | 29.0834 | 69.1051 | 104.316 | 713.4619 | 630.3991 | 748.2261 | 748.2578 | 687.2164 |  | 712.024 | 669.202 | 799.9705 | 612.4689 | 608.1972 | 671.801 |  | 569.9704 |  |  | 459.7477 | 588.7518 | 671.7962 | [5 empty] | 21.8311 | 589.0265 | 22.2645 | 22.054 | 415.9633 | 21.6884 | 21.858 | 472.331 | 591.956 | 590.1222 |  | 742.1483 | 876.3608 | 494.5726 | 650.604 | 711.0235 | 556.353 | 617.4393 | 673.0584 | 811.4154 | 591.36 | 701.8537 | 1098.5437 | 1057.387 | 963.4474 | 490.6781 | 583.9862 | 599.4348 | 501.325 | 637.4304 | 715.0007 | 1085.0562 | 1011.6509 | 544.7308 | 613.3654 | 582.5465 | 773.7075 | 45.1496 | -0.00064115 | 19.5108 | 6.872 | -28.5182 | 3.0965 | 5349.25 | -0.12 | 2.2893 | -0.48448 | -15.8224 | -6.4791 | 7.3236 | -35.2279 | -35.7033 | 54.1006 | 78.8254 | 34.0928 | 51.6736 | 15.8921 | 57.6858 | 26.3796
42838.4329 | 1091 | 22.7467 | 22.7537 | 22.7569 | 22.6716 | 22.2792 | 21.6076 | 22.6258 | 21.6722 | 22.2904 | 22.291 | 22.2563 | 21.8984 | 21.1183 | 22.0931 | 21.6042 | 23.427 | 25.1134 | 29.5758 | 49.7239 | 56.6078 | 85.811 | 89.4191 | 92.188 | 27.9582 | 58.5185 | 95.8256 | 608.5826 | 634.1565 | 609.3026 | 27.0625 | 63.5498 | 101.9637 | 28.6225 | 61.1905 | 99.4675 | 721.957 | 683.4069 |  | 361.0719 | 675.775 | 690.7683 | 653.3902 |  | 476.2489 | 692.9465 | 604.4387 | 791.9124 | 926.7775 | 1015.276 | 1025.3502 | 39.8573 | 279.7379 | 62.1413 | 503.4466 | 72.5536 | 49.1355 | 48.3537 | 55.2894 | 48.703 |  |  | 1.162 | 0.24241 | -52.114 | -8.5741 | 8.0051 | -197.8033 | -203.2187 | -2.5657 | 8.8184 | 30.2145 | 12.0216 | -3.121e-05 | -0.00040084 | 0.0004337 | 34.3003 | 22.5149 | 22.1024 | 22.1401 | 21.9357 | 21.1987 | 20.0761 | 22.1483 | 22.3043 | 22.3555 | 22.2929 | 21.8906 | 21.1332 | 22.2121 | 478.2369 | 371.9382 | 285.5753 | 208.1693 | 158.9038 | 610.2045 | 354.6645 | 22.2148 | 22.8066 | 24.8701 | 22.7303 | 43.3392 | 52.0944 | 35.7737 | 83.3242 | 90.2218 | 547.852 | 509.4412 | 514.5847 | 526.399 | 46.0054 | 18.1033 | 736.5273 | 22.4012 | 22.1204 | 364.2631 | 21.5708 | 21.9454 | 57.955 | 88.9633 | 101.6179 | 29.1409 | 69.3454 | 104.3597 | 712.8569 | 630.4772 | 750.4231 | 750.193 | 687.7094 |  | 711.7434 | 669.7073 | 800.9777 | 612.7044 | 608.4829 | 671.9081 |  | 570.5572 |  |  | 460.0996 | 585.9057 | 670.6849 | [5 empty] | 21.8317 | 588.6208 | 22.2599 | 22.0413 | 415.2811 | 21.6923 | 21.8543 | 472.4125 | 592.4594 | 590.418 |  | 744.7886 | 878.4826 | 495.1221 | 648.9543 | 712.1893 | 556.6754 | 618.3058 | 673.9842 | 811.3978 | 590.1933 | 703.0789 | 1099.0645 | 1057.8057 | 963.5885 | 491.1192 | 583.7839 | 600.0242 | 501.7807 | 638.623 | 715.678 | 1081.9545 | 1014.6121 | 544.7994 | 614.7616 | 583.3891 | 773.923 | 46.0196 | -0.0010414 | 19.5182 | 6.8414 | -28.5006 | 3.0965 | 5431.17 | -0.14 | 2.2316 | 1.0665 | -15.637 | -6.3427 | 7.0775 | -35.1814 | -35.6598 | 54.0183 | 79.122 | 34.1385 | 49.1872 | 16.4852 | 57.503 | 26.3568
42838.4329 | 1092 | 22.7466 | 22.7468 | 22.7542 | 22.673 | 22.2797 | 21.6147 | 22.6277 | 21.6661 | 22.2896 | 22.2918 | 22.258 | 21.9026 | 21.1194 | 22.0993 | 21.6125 | 23.4452 | 25.1448 | 29.6701 | 49.8051 | 56.705 | 85.8287 | 89.4561 | 92.2339 | 27.9972 | 58.5833 | 95.8923 | 609.4268 | 634.3327 | 610.2992 | 27.1105 | 63.6218 | 102.0368 | 28.6665 | 61.2606 | 99.5136 | 720.8393 | 682.4198 |  | 361.397 | 681.2098 | 697.158 | 653.6897 |  | 475.6161 | 693.0768 | 604.2849 | 792.3756 | 927.2788 | 1017.8403 | 1026.4432 | 39.812 | 279.2756 | 61.2398 | 502.7986 | 72.6338 | 49.1036 | 48.3327 | 55.3207 | 48.7158 |  |  | 0.84331 | 0.75496 | -58.2771 | -8.1299 | 7.4065 | -197.823 | -203.105 | -2.751 | 9.2588 | 30.885 | 11.9553 | -0.00013142 | -0.00043534 | 0.0003992 | 34.3663 | 22.5039 | 22.0883 | 22.1277 | 21.919 | 21.1873 | 20.0645 | 22.1252 | 22.3019 | 22.3405 | 22.2744 | 21.8837 | 21.1232 | 22.2034 | 503.8067 | 384.1767 | 285.7323 | 207.9638 | 160.0232 | 609.056 | 353.136 | 22.2138 | 22.8017 | 24.8954 | 22.7314 | 43.4303 | 52.1657 | 36.0215 | 83.3482 | 90.2643 | 547.937 | 510.8075 | 514.8592 | 527.047 | 43.3859 | 20.0152 | 738.3191 | 22.4088 | 22.1224 | 365.2039 | 21.5724 | 21.9441 | 58.0655 | 88.9679 | 101.6564 | 29.2075 | 69.595 | 104.4125 | 711.5381 | 630.4262 | 752.5799 | 751.5963 | 688.1978 |  | 711.4802 | 669.9647 | 801.9399 | 611.9944 | 608.7938 | 672.2832 |  | 568.905 |  |  | 460.9511 | 586.1204 | 670.5763 | [5 empty] | 21.8282 | 588.0513 | 22.2715 | 22.049 | 414.548 | 21.6926 | 21.8591 | 472.8281 | 593.4039 | 590.7411 |  | 743.3761 | 878.9315 | 495.4022 | 647.69 | 713.5345 | 557.3798 | 619.346 | 671.7015 | 811.0213 | 589.4691 | 703.53 | 1097.2696 | 1057.6937 | 962.6821 | 491.4633 | 583.4068 | 600.3492 | 501.8925 | 639.4449 | 716.2131 | 1080.2532 | 1014.9044 | 544.8611 | 614.3895 | 583.795 | 774.2009 | 44.9552 | 0.00072809 | 19.5258 | 6.8219 | -28.5547 | 3.0965 | 5509.85 | -0.1 | 1.9022 | 1.8822 | -16.537 | -6.1766 | 6.8145 | -35.2182 | -35.6853 | 53.9404 | 79.4124 | 34.2153 | 46.0393 | 16.2125 | 57.2143 | 26.3518
42838.4329 | 1093 | 22.7441 | 22.7465 | 22.7547 | 22.6776 | 22.2827 | 21.6103 | 22.6195 | 21.6624 | 22.2855 | 22.2899 | 22.2613 | 21.9005 | 21.1239 | 22.0979 | 21.6176 | 23.4707 | 25.1808 | 29.7584 | 49.9113 | 56.7911 | 85.8391 | 89.4848 | 92.3024 | 28.0307 | 58.6654 | 95.9591 | 610.0548 | 634.3475 | 610.6789 | 27.1424 | 63.6886 | 102.1041 | 28.7086 | 61.3429 | 99.568 | 720.5555 | 681.0622 |  | 361.6509 | 685.4521 | 701.6182 | 660.0958 |  | 475.1543 | 693.4125 | 605.0718 | 792.5285 | 930.6436 | 1020.0835 | 1024.6343 | 39.8854 | 278.7832 | 61.3953 | 502.1807 | 72.5919 | 49.0661 | 48.3151 | 55.3295 | 48.7451 |  |  | 1.0904 | 0.52957 | -67.4452 | -8.5708 | 7.9867 | -197.8394 | -203.2134 | -2.665 | 8.7588 | 29.3058 | 11.8667 | -2.3e-05 | -0.00054048 | 0.00041563 | 34.4391 | 22.5187 | 22.0905 | 22.126 | 21.9222 | 21.1963 | 20.0736 | 22.1305 | 22.2974 | 22.3416 | 22.2837 | 21.8817 | 21.1259 | 22.2073 | 515.4174 | 365.7032 | 301.2591 | 214.729 | 162.1493 | 607.7231 | 351.9546 | 22.2095 | 22.8289 | 24.9283 | 22.7481 | 43.5299 | 52.259 | 36.2405 | 83.37 | 90.3166 | 547.9833 | 509.495 | 515.7797 | 526.693 | 33.2034 | 14.6247 | 739.1119 | 22.4153 | 22.1264 | 366.0593 | 21.5796 | 21.9541 | 58.1705 | 88.9748 | 101.6927 | 29.2731 | 69.8443 | 104.4621 | 710.635 | 630.7589 | 754.474 | 752.8518 | 687.7147 |  | 711.289 | 669.9353 | 802.3982 | 613.0262 | 609.1236 | 672.1932 |  | 567.7103 |  |  | 461.2854 | 586.0646 | 670.8112 | [5 empty] | 21.8329 | 588.2784 | 22.2772 | 22.0455 | 413.4911 | 21.701 | 21.8677 | 473.3582 | 594.4546 | 591.4231 |  | 741.1254 | 879.2322 | 495.1264 | 647.1403 | 713.746 | 558.0511 | 619.725 | 669.7395 | 810.8013 | 589.0188 | 703.9639 | 1098.7768 | 1057.2584 | 961.6531 | 491.6299 | 583.0329 | 600.93 | 502.2542 | 639.1303 | 715.4184 | 1080.8571 | 1016.8703 | 545.006 | 615.3972 | 583.5336 | 773.9146 | 45.3932 | 5.4014e-05 | 19.5344 | 6.7939 | -28.5419 | 3.0965 | 5585.9 | 0.02 | 2.1634 | 1.5767 | -17.7933 | -6.343 | 7.0826 | -35.2502 | -35.7258 | 53.9071 | 79.5552 | 34.2471 | 44.3941 | 14.2904 | 56.9653 | 26.3687
42838.4329 | 1094 | 22.7479 | 22.7546 | 22.7507 | 22.6757 | 22.2839 | 21.6088 | 22.6252 | 21.6714 | 22.2862 | 22.2848 | 22.259 | 21.9061 | 21.1154 | 22.0968 | 21.621 | 23.491 | 25.2061 | 29.8436 | 49.9905 | 56.8741 | 85.8397 | 89.5326 | 92.3476 | 28.0701 | 58.7365 | 96.0264 | 609.8115 | 634.7142 | 610.0963 | 27.1892 | 63.757 | 102.1808 | 28.7587 | 61.429 | 99.6193 | 720.9623 | 680.1979 |  | 361.9711 | 689.3237 | 708.2234 | 665.7076 |  | 473.8897 | 694.1435 | 603.8635 | 790.1474 | 931.6475 | 1019.0833 | 1021.2917 | 39.6708 | 278.1944 | 61.8688 | 501.7442 | 72.6571 | 49.0255 | 48.2976 | 55.3312 | 48.7519 |  |  | 0.96356 | 0.14253 | -72.0404 | -7.6673 | 7.5136 | -197.8098 | -203.3225 | -3.0448 | 8.5055 | 28.945 | 11.9461 | -0.00015606 | -0.00052898 | 0.0003877 | 34.5101 | 22.5236 | 22.0954 | 22.1237 | 21.9219 | 21.2011 | 20.0751 | 22.1301 | 22.3054 | 22.3358 | 22.2833 | 21.8827 | 21.1285 | 22.2121 | 505.1976 | 345.7311 | 290.6013 | 215.8557 | 165.6158 | 605.6996 | 350.5497 | 22.2169 | 22.8341 | 24.9475 | 22.7537 | 43.621 | 52.3349 | 36.4374 | 83.3787 | 90.3543 | 548.0688 | 510.8797 | 517.7115 | 526.6869 | 40.223 | 12.0728 | 738.6512 | 22.4175 | 22.1317 | 366.5251 | 21.5781 | 21.9529 | 58.269 | 88.9753 | 101.7352 | 29.3339 | 70.0643 | 104.5078 | 710.1499 | 631.1361 | 755.0129 | 753.4975 | 687.0773 |  | 711.0646 | 669.9995 | 802.7675 | 613.9755 | 609.4893 | 672.4222 |  | 565.4119 |  |  | 460.7491 | 585.4317 | 670.3084 | [5 empty] | 21.8395 | 588.547 | 22.2852 | 22.0425 | 413.2555 | 21.7079 | 21.8619 | 473.8108 | 594.9924 | 592.2854 |  | 739.2566 | 880.1513 | 494.5398 | 646.9448 | 713.4874 | 558.9381 | 619.4759 | 675.4701 | 810.115 | 587.946 | 703.1241 | 1100.4777 | 1057.2804 | 964.3152 | 491.6109 | 582.7831 | 601.3729 | 502.2891 | 637.8804 | 714.4005 | 1079.5452 | 1016.0317 | 545.3253 | 682.4537 | 582.9408 | 773.1277 | 48.4194 | 0.00038403 | 19.545 | 6.7803 | -28.5438 | 3.0965 | 5634.71 | -0.07 | 2.033 | 0.81827 | -18.3965 | -6.0016 | 6.8669 | -35.234 | -35.7215 | 53.8701 | 79.6679 | 34.2879 | 44.9922 | 15.2409 | 56.9113 | 26.382
42838.433 | 1095 | 22.7501 | 22.7553 | 22.7588 | 22.6738 | 22.278 | 21.609 | 22.6311 | 21.6668 | 22.2909 | 22.2973 | 22.2595 | 21.8964 | 21.1155 | 22.1059 | 21.6269 | 23.514 | 25.2328 | 29.9258 | 50.0875 | 56.9605 | 85.8655 | 89.5964 | 92.4026 | 28.106 | 58.7971 | 96.077 | 609.6324 | 635.3193 | 609.7114 | 27.2363 | 63.8275 | 102.582 | 28.8045 | 61.5048 | 99.685 | 721.0034 | 681.1214 |  | 364.0314 | 688.4891 | 707.5916 | 661.73 |  | 473.8343 | 693.6191 | 601.304 | 786.6443 | 926.5888 | 1017.853 | 1018.7696 | 39.1343 | 277.6968 | 61.9335 | 501.4859 | 72.6456 | 48.9821 | 48.2675 | 55.3341 | 48.7564 |  |  | 1.0444 | 0.49803 | -73.4736 | -7.2697 | 8.034 | -197.8 | -203.1155 | -3.2735 | 8.7544 | 30.3301 | 12.0158 | -9.857e-05 | -0.0003762 | 0.00038277 | 34.5819 | 22.5266 | 22.0953 | 22.1248 | 21.9225 | 21.1925 | 20.0768 | 22.1354 | 22.3022 | 22.3415 | 22.2854 | 21.8806 | 21.1259 | 22.2085 | 507.703 | 326.0414 | 265.8563 | 213.9606 | 178.0102 | 603.8431 | 348.87 | 22.2052 | 22.8399 | 24.9682 | 22.7522 | 43.705 | 52.4078 | 36.6262 | 83.3852 | 90.3887 | 548.1118 | 509.846 | 518.044 | 526.0588 | 36.5179 | 14.7099 | 737.9699 | 22.4268 | 22.1301 | 367.0354 | 21.5771 | 21.9475 | 58.3707 | 88.9854 | 101.7841 | 29.4022 | 70.2657 | 104.561 | 710.4458 | 631.3945 | 754.3752 | 753.1262 | 688.6832 |  | 711.0238 | 670.2539 | 803.2719 | 613.5718 | 609.8214 | 672.8994 |  | 564.4506 |  |  | 461.7991 | 585.2006 | 670.9511 | [5 empty] | 21.8353 | 588.1801 | 22.2831 | 22.0574 | 413.8583 | 21.7088 | 21.8544 | 474.1187 | 595.2188 | 592.8225 |  | 743.0736 | 878.0454 | 493.9374 | 646.0963 | 713.1429 | 559.0048 | 619.5142 | 684.567 | 811.478 | 586.7548 | 703.1853 | 1098.5308 | 1054.7271 | 963.6341 | 491.6167 | 582.8995 | 601.6507 | 502.4149 | 637.5915 | 713.9806 | 1078.4973 | 1015.381 | 545.8745 |  | 582.6435 | 772.8819 | 47.6322 | -0.0005288 | 19.5548 | 6.7581 | -28.5443 | 3.0964 | 5609.27 | -0.05 | 2.1161 | 1.5292 | -18.5735 | -5.8423 | 7.0974 | -35.2163 | -35.6864 | 53.8155 | 79.8175 | 34.3601 | 44.2226 | 17.7117 | 57.0321 | 26.406
42838.433 | 1096 | 22.7426 | 22.7493 | 22.7563 | 22.6751 | 22.2779 | 21.6107 | 22.6219 | 21.6636 | 22.2901 | 22.2882 | 22.2607 | 21.8992 | 21.1193 | 22.0961 | 21.6313 | 23.5361 | 25.2639 | 30.0182 | 50.172 | 57.044 | 85.8676 | 89.6556 | 92.4418 | 28.1457 | 58.8746 | 96.1356 | 609.8054 | 636.1204 | 610.1506 | 27.2746 | 63.8912 | 103.3256 | 28.8498 | 61.5721 | 99.7333 | 720.0262 | 681.8929 |  | 363.9016 | 686.7428 | 705.1633 | 654.9453 |  | 473.092 | 692.142 | 600.57 | 780.5363 | 915.3699 | 1016.6171 | 1013.6695 | 39.209 | 277.1855 | 61.7947 | 501.1073 | 72.6004 | 48.9529 | 48.2557 | 55.3522 | 48.7623 |  |  | 1.097 | 0.89493 | -72.9439 | -7.3019 | 7.4361 | -197.865 | -203.0045 | -2.4133 | 8.8106 | 30.0791 | 11.8969 | -8.214e-05 | -0.00038113 | 0.00039263 | 34.6572 | 22.5419 | 22.0957 | 22.1312 | 21.9305 | 21.2041 | 20.0823 | 22.1329 | 22.3132 | 22.3457 | 22.2824 | 21.8915 | 21.1344 | 22.2154 | 506.0601 | 327.2694 | 254.8358 | 205.4358 | 176.1242 | 601.9898 | 347.3924 | 22.2039 | 22.8464 | 24.9949 | 22.7649 | 43.797 | 52.4784 | 36.8242 | 83.3952 | 90.4305 | 548.1815 | 510.1713 | 519.0525 | 526.4291 | 36.797 | 17.4659 | 737.789 | 22.4345 | 22.1284 | 368.0079 | 21.5749 | 21.9489 | 58.4687 | 88.9879 | 101.8244 | 29.4725 | 70.4504 | 104.616 | 711.2676 | 631.548 | 753.7315 | 752.4587 | 690.6781 |  | 711.2242 | 670.6439 | 803.782 | 612.5109 | 610.0003 | 673.8088 |  | 564.6091 |  |  | 462.0945 | 585.8899 | 672.8897 | [5 empty] | 21.8391 | 587.7754 | 22.282 | 22.0452 | 415.2039 | 21.7098 | 21.854 | 473.9465 | 595.1576 | 592.7562 |  | 749.788 | 877.4459 | 493.2886 | 644.5776 | 712.7893 | 559.298 | 619.2368 | 697.879 | 812.987 | 585.627 | 700.6799 | 1095.0759 | 1052.1412 | 963.519 | 491.5563 | 583.3362 | 602.1837 | 502.8343 | 638.7971 | 715.5984 | 1076.1861 | 1013.3516 | 546.631 |  | 582.9096 | 774.5582 | 47.9357 | -0.00064115 | 19.5633 | 6.7314 | -28.5568 | 3.0964 | 5566.77 | 0.01 | 2.1693 | 2.0483 | -18.4923 | -5.8508 | 6.8249 | -35.2052 | -35.6595 | 53.809 | 79.9652 | 34.4225 | 43.9166 | 18.6916 | 56.9759 | 26.4065
42838.433 | 1097 | 22.7518 | 22.7487 | 22.761 | 22.6701 | 22.2839 | 21.6101 | 22.6253 | 21.6655 | 22.2924 | 22.2923 | 22.2547 | 21.9081 | 21.1163 | 22.0885 | 21.6202 | 23.5486 | 25.2889 | 30.0943 | 50.2575 | 57.1136 | 85.8785 | 89.6963 | 92.4689 | 28.1718 | 58.9357 | 96.1813 | 610.9388 | 636.2152 | 611.8053 | 27.3147 | 63.9575 | 103.8432 | 28.8913 | 61.6414 | 99.7829 | 718.9461 | 682.4784 |  | 363.266 | 685.9263 | 704.1148 | 652.572 |  | 472.404 | 692.3639 | 600.1351 | 782.4868 | 914.1198 | 1015.77 | 1010.6365 | 40.0733 | 276.7838 | 62.7436 | 500.6715 | 72.6491 | 48.9218 | 48.2225 | 55.3317 | 48.7683 |  |  | 1.001 | 0.23912 | -73.4236 | -7.4826 | 7.1502 | -197.7895 | -203.2377 | -3.1913 | 9.4183 | 31.7301 | 11.8553 | -0.00012485 | -0.00052898 | 0.00037949 | 34.7308 | 22.5385 | 22.0878 | 22.1332 | 21.9255 | 21.1967 | 20.0766 | 22.1328 | 22.3104 | 22.336 | 22.2805 | 21.8895 | 21.1374 | 22.2083 | 498.0132 | 337.4539 | 268.5942 | 203.364 | 170.1607 | 600.2454 | 346.1386 | 22.2203 | 22.8617 | 25.0294 | 22.7714 | 43.8985 | 52.588 | 37.0525 | 83.4237 | 90.4775 | 548.4848 | 512.4147 | 521.0936 | 529.816 | 43.5603 | 19.4712 | 738.4815 | 22.438 | 22.1285 | 369.0612 | 21.5725 | 21.9524 | 58.5692 | 88.9772 | 101.8651 | 29.5403 | 70.6395 | 104.6671 | 712.1582 | 631.9729 | 752.4979 | 751.3336 | 691.8433 |  | 711.4592 | 671.1915 | 804.4821 | 613.6384 | 610.2639 | 674.3637 |  | 564.6789 |  |  | 462.6745 | 586.2938 | 674.5316 | [5 empty] | 21.8412 | 588.0559 | 22.294 | 22.0484 | 415.7445 | 21.7178 | 21.858 | 474.0531 | 595.1291 | 592.672 |  | 756.2315 | 879.2186 | 493.1911 | 643.553 | 711.4655 | 559.6941 | 619.042 | 706.1036 | 815.7715 | 584.7251 | 698.7431 | 1088.0745 | 1048.4646 | 963.7577 | 491.5059 | 583.8968 | 602.9321 | 502.9127 | 640.3734 | 717.2201 | 1073.275 | 1012.5925 | 547.0865 | 812.0772 | 583.2183 | 776.0633 | 45.5982 | -0.00024794 | 19.5699 | 6.7071 | -28.5242 | 3.0965 | 5513.36 | -0.07 | 2.0742 | 1.0589 | -18.5551 | -5.9234 | 6.6902 | -35.1869 | -35.6683 | 53.834 | 80.168 | 34.4397 | 44.3525 | 16.9558 | 56.7723 | 26.3589
42838.433 | 1098 | 22.7558 | 22.7552 | 22.7585 | 22.673 | 22.2916 | 21.6103 | 22.6284 | 21.6676 | 22.2938 | 22.2992 | 22.2593 | 21.902 | 21.1202 | 22.1035 | 21.6269 | 23.5664 | 25.3132 | 30.183 | 50.3445 | 57.193 | 85.8868 | 89.7358 | 92.5068 | 28.2073 | 59.0027 | 96.2387 | 612.1016 | 635.9584 | 612.9614 | 27.3656 | 64.0209 | 104.1781 | 28.9263 | 61.7191 | 99.817 | 718.3727 | 684.2686 |  | 364.0057 | 685.2923 | 703.4841 | 653.7649 |  | 471.9218 | 692.8468 | 603.3308 | 781.8643 | 919.6146 | 1015.7024 | 1010.4639 | 41.1279 | 276.383 | 64.5094 | 500.2221 | 72.5974 | 48.8703 | 48.1917 | 55.3084 | 48.7742 |  |  | 1.0345 | 0.31206 | -73.3645 | -7.3946 | 7.8047 | -197.8098 | -203.2016 | -2.3174 | 9.2146 | 31.2609 | 11.8912 | -0.00018071 | -0.00043862 | 0.00038277 | 34.7951 | 22.5431 | 22.0832 | 22.1241 | 21.9192 | 21.1905 | 20.0753 | 22.129 | 22.2977 | 22.339 | 22.2868 | 21.8876 | 21.1309 | 22.2041 | 502.8618 | 350.4449 | 262.8904 | 202.5831 | 175.8028 | 599.1459 | 345.0076 | 22.2097 | 22.8728 | 25.0444 | 22.7787 | 43.9834 | 52.6584 | 37.2594 | 83.4383 | 90.5202 | 548.7783 | 512.8392 | 522.0794 | 531.4951 | 45.7243 | 14.5463 | 740.3413 | 22.4447 | 22.1314 | 369.8035 | 21.5784 | 21.9515 | 58.6752 | 88.9789 | 101.9071 | 29.6125 | 70.8511 | 104.721 | 712.8258 | 632.603 | 749.8893 | 749.3874 | 691.4453 |  | 711.4788 | 671.942 | 805.589 | 613.6529 | 610.5815 | 674.4376 |  | 564.4994 |  |  | 462.7006 | 586.8178 | 674.3667 | [5 empty] | 21.8349 | 588.4299 | 22.2985 | 22.0426 | 416.3934 | 21.7168 | 21.8567 | 474.4978 | 595.2571 | 592.879 |  | 760.3912 | 883.8947 | 493.1692 | 643.2325 | 711.3523 | 559.8626 | 618.8422 | 712.5022 | 818.088 | 584.5868 | 696.8589 | 1082.0264 | 1047.637 | 964.466 | 491.8802 | 584.7548 | 604.4506 | 503.2669 | 641.6047 | 718.5745 | 1071.8223 | 1012.5662 | 547.2382 | 1000.9737 | 583.3545 | 776.6415 | 45.0873 | 0.0024906 | 19.5697 | 6.6787 | -28.5671 | 3.0965 | 5472.23 | -0.06 | 2.11 | 1.21 | -18.5523 | -5.8899 | 6.9895 | -35.1878 | -35.6642 | 53.8499 | 80.4925 | 34.4978 | 43.5258 | 17.4032 | 56.5963 | 26.3574
42838.433 | 1099 | 22.7542 | 22.7568 | 22.7559 | 22.6829 | 22.2903 | 21.6093 | 22.6275 | 21.6727 | 22.2938 | 22.2984 | 22.2687 | 21.8992 | 21.1245 | 22.1087 | 21.6452 | 23.5841 | 25.3473 | 30.2806 | 50.4381 | 57.2871 | 85.9052 | 89.7883 | 92.5503 | 28.2521 | 59.0753 | 96.295 | 612.8051 | 636.2444 | 613.769 | 27.4069 | 64.0798 | 104.4116 | 28.9689 | 61.7873 | 99.85 | 718.1358 | 684.972 |  | 364.4602 | 686.7879 | 706.1575 | 655.3855 |  | 471.3275 | 693.2353 | 603.027 | 780.5466 | 919.3428 | 1013.8723 | 1008.8873 | 41.4589 | 276.0465 | 66.4777 | 499.8756 | 72.6056 | 48.8301 | 48.1695 | 55.2802 | 48.7816 |  |  | 0.93202 | 0.059731 | -75.9088 | -6.6553 | 7.7383 | -197.8493 | -203.2325 | -2.3975 | 8.9332 | 30.0638 | 11.9575 | -0.00018399 | -0.00044355 | 0.00040906 | 34.8871 | 22.5576 | 22.1026 | 22.1344 | 21.9278 | 21.19 | 20.0772 | 22.1389 | 22.3046 | 22.3575 | 22.2927 | 21.8895 | 21.1357 | 22.2156 | 510.6209 | 346.9053 | 261.2354 | 198.9377 | 170.1803 | 598.3424 | 343.5949 | 22.2062 | 22.8785 | 25.0744 | 22.7881 | 44.0693 | 52.7296 | 37.482 | 83.457 | 90.56 | 549.0608 | 513.6635 | 522.8599 | 532.1516 | 49.4779 | 24.5973 | 742.6127 | 22.4504 | 22.134 | 370.7347 | 21.5873 | 21.9541 | 58.7704 | 88.9861 | 101.9588 | 29.6874 | 71.0587 | 104.7671 | 709.9622 | 633.0854 | 747.0911 | 747.3806 | 689.4044 |  | 711.3557 | 672.489 | 806.763 | 612.2056 | 610.7097 | 674.9772 |  | 564.2437 |  |  | 462.5373 | 586.2092 | 673.4562 | [5 empty] | 21.832 | 588.0079 | 22.3087 | 22.0486 | 417.0436 | 21.7184 | 21.8569 | 474.9611 | 595.6487 | 592.8874 |  | 761.9735 | 885.4846 | 493.1318 | 643.3282 | 712.1307 | 560.3608 | 618.5297 | 717.0791 | 818.5987 | 585.0738 | 696.8758 | 1077.9409 | 1046.4132 | 964.0427 | 492.2959 | 586.172 | 605.7953 | 503.4403 | 641.752 | 718.9144 | 1073.1581 | 1010.2348 | 547.6163 | 619.3769 | 583.0209 | 777.2084 | 43.4679 | 0.0069283 | 19.5691 | 6.6599 | -28.6179 | 3.0964 | 5462.9 | -0.12 | 2.0037 | 0.52947 | -18.8751 | -5.5889 | 6.9548 | -35.1663 | -35.6415 | 53.8765 | 80.8447 | 34.5617 | 42.4536 | 17.3547 | 56.4924 | 26.3826
42838.433 | 1100 | 22.7576 | 22.7506 | 22.7564 | 22.6751 | 22.2812 | 21.6098 | 22.6268 | 21.673 | 22.2909 | 22.2883 | 22.2579 | 21.9006 | 21.1182 | 22.0966 | 21.6548 | 23.6108 | 25.3783 | 30.3655 | 50.5252 | 57.3707 | 85.9352 | 89.8305 | 92.6053 | 28.2889 | 59.1426 | 96.3394 | 613.3159 | 636.8316 | 614.5133 | 27.4382 | 64.142 | 104.5838 | 29.0148 | 61.8542 | 99.8932 | 717.6624 | 683.8398 |  | 364.7374 | 690.1461 | 710.5424 | 653.1379 |  | 471.3725 | 693.1115 | 600.064 | 781.8227 | 915.0918 | 1012.9471 | 1008.4246 | 40.8575 | 275.8085 | 67.2096 | 499.7023 | 72.6979 | 48.7918 | 48.1391 | 55.2425 | 48.7454 |  |  | 0.94188 | 0.55323 | -75.4981 | -7.2894 | 6.8933 | -197.8204 | -203.2364 | -2.6952 | 9.2837 | 31.6556 | 12.3648 | -0.00027106 | -0.00056676 | 0.00040084 | 34.9595 | 22.5557 | 22.0961 | 22.1283 | 21.9323 | 21.1955 | 20.0746 | 22.1394 | 22.3057 | 22.351 | 22.2924 | 21.8855 | 21.1293 | 22.216 | 527.476 | 368.4396 | 305.5163 | 212.2913 | 169.7212 | 598.0764 | 342.8986 | 22.2045 | 22.8874 | 25.0981 | 22.7934 | 44.1579 | 52.8102 | 37.7143 | 83.4762 | 90.5968 | 549.4331 | 516.2246 | 525.3908 | 533.525 | 45.7982 | 14.9549 | 744.0784 | 22.4579 | 22.133 | 371.9065 | 21.5932 | 21.9584 | 58.8688 | 88.9902 | 102.0084 | 29.7578 | 71.2649 | 104.8151 | 706.6717 | 633.4008 | 744.862 | 745.6057 | 684.4122 |  | 710.9696 | 672.6593 | 807.6024 | 611.9807 | 610.8215 | 675.2044 |  | 564.0817 |  |  | 462.674 | 583.141 | 670.5032 | [5 empty] | 21.839 | 587.881 | 22.3228 | 22.0536 | 416.7003 | 21.7327 | 21.8623 | 475.4966 | 596.0104 | 592.7157 |  | 763.9053 | 885.99 | 492.7659 | 643.7232 | 712.46 | 560.9893 | 618.2219 | 718.6345 | 818.686 | 584.9011 | 697.1214 | 1075.4116 | 1046.9229 | 962.2845 | 492.6662 | 587.5835 | 606.4759 | 503.0472 | 641.7602 | 719.6187 | 1073.4599 | 1009.4574 | 548.0226 | 619.6244 | 582.4871 | 777.7394 | 44.7258 | -0.00029004 | 19.5685 | 6.6361 | -28.4596 | 3.0964 | 5453.01 | -0.1 | 2.0151 | 1.6113 | -18.8227 | -5.8487 | 6.5617 | -35.1511 | -35.6291 | 53.9209 | 81.1033 | 34.5885 | 40.5113 | 12.3202 | 56.4371 | 26.4017
42838.433 | 1101 | 22.7535 | 22.7605 | 22.7582 | 22.6713 | 22.2894 | 21.6113 | 22.6278 | 21.6632 | 22.2854 | 22.2899 | 22.2551 | 21.9035 | 21.1185 | 22.0959 | 21.6582 | 23.636 | 25.4048 | 30.4461 | 50.6119 | 57.4497 | 85.9503 | 89.8711 | 92.6496 | 28.3217 | 59.2056 | 96.3851 | 613.9387 | 637.2934 | 615.2368 | 27.4918 | 64.2115 | 104.7167 | 29.0641 | 61.9365 | 99.9483 | 717.31 | 684.6678 |  | 364.9008 | 692.0163 | 712.0961 | 653.4082 |  | 471.2083 | 691.414 | 597.9508 | 781.2874 | 915.0144 | 1011.4266 | 1008.8867 | 39.5433 | 275.537 | 68.6958 | 499.7197 | 72.6549 | 48.733 | 48.1083 | 55.2173 | 48.7574 |  |  | 1.0174 | 0.35806 | -77.505 | -7.2645 | 7.7804 | -197.8414 | -203.2233 | -2.4461 | 9.1479 | 30.9485 | 12.3276 | -0.00012814 | -0.00045998 | 0.00037949 | 35.0296 | 22.5608 | 22.1017 | 22.1236 | 21.9239 | 21.1941 | 20.075 | 22.1385 | 22.3028 | 22.3454 | 22.2953 | 21.8893 | 21.134 | 22.2077 | 514.2711 | 362.4528 | 286.4085 | 202.2304 | 164.7554 | 597.6247 | 341.8644 | 22.2121 | 22.9038 | 25.1242 | 22.8016 | 44.2522 | 52.8979 | 37.9652 | 83.5081 | 90.6426 | 549.8511 | 518.685 | 527.152 | 534.2657 | 46.8677 | 25.6011 | 744.4302 | 22.4595 | 22.1285 | 372.7158 | 21.587 | 21.9511 | 58.9686 | 88.9937 | 102.0494 | 29.8262 | 71.4676 | 104.8535 | 706.7308 | 633.2981 | 743.3763 | 744.16 | 681.637 |  | 710.4127 | 672.7011 | 808.2007 | 611.2184 | 610.9011 | 675.4585 |  | 564.7394 |  |  | 462.8988 | 580.2663 | 666.7845 | [5 empty] | 21.8397 | 587.4478 | 22.3228 | 22.057 | 416.0976 | 21.7375 | 21.864 | 476.1207 | 596.2166 | 592.6955 |  | 766.1745 | 886.09 | 492.1395 | 643.8202 | 712.5696 | 561.5805 | 617.9751 | 721.1245 | 819.6001 | 584.466 | 695.7917 | 1075.4989 | 1046.3279 | 960.4378 | 492.9156 | 588.0276 | 606.7847 | 502.4225 | 642.0772 | 720.1557 | 1073.4195 | 1009.6828 | 548.4033 | 619.5156 | 582.1948 | 778.5533 | 46.0643 | -0.00033218 | 19.568 | 6.62 | -28.5775 | 3.0965 | 5436.79 | 0.02 | 2.0952 | 1.2951 | -19.0545 | -5.8336 | 6.967 | -35.1322 | -35.6069 | 53.8623 | 81.2902 | 34.6244 | 41.8607 | 14.2737 | 56.3422 | 26.4456
42838.433 | 1102 | 22.7526 | 22.7513 | 22.7587 | 22.671 | 22.2813 | 21.6166 | 22.6247 | 21.678 | 22.2931 | 22.2956 | 22.2707 | 21.9004 | 21.1231 | 22.0971 | 21.6589 | 23.6531 | 25.434 | 30.5308 | 50.6957 | 57.5312 | 85.9621 | 89.9096 | 92.6881 | 28.3577 | 59.262 | 96.4289 | 614.6225 | 638.1803 | 615.9604 | 27.5286 | 64.2736 | 104.8137 | 29.1023 | 61.9963 | 99.9911 | 716.727 | 685.3393 |  | 365.0055 | 692.8121 | 712.374 | 653.7507 |  | 470.8089 | 690.4249 | 599.8197 | 781.3119 | 912.0869 | 1010.352 | 1010.7779 | 38.654 | 275.3778 | 68.8407 | 499.9133 | 72.6581 | 48.681 | 48.0789 | 55.1882 | 48.7687 |  |  | 0.92479 | -0.094689 | -106.3701 | -7.4268 | 7.5208 | -197.8532 | -203.0866 | -2.6078 | 8.8055 | 30.5241 | 12.1148 | -0.00016921 | -0.00050105 | 0.00039591 | 35.1031 | 22.5728 | 22.0962 | 22.1309 | 21.9313 | 21.1974 | 20.0773 | 22.1427 | 22.3079 | 22.3421 | 22.2913 | 21.8915 | 21.1326 | 22.2096 | 506.5792 | 383.6678 | 310.6865 | 202.8773 | 165.9634 | 597.1665 | 341.2801 | 22.2074 | 22.9163 | 25.1606 | 22.8133 | 44.3505 | 52.9826 | 38.2489 | 83.5312 | 90.6876 | 550.0958 | 520.0044 | 527.9795 | 532.6536 | 41.9499 | 19.4788 | 744.6516 | 22.4651 | 22.1224 | 373.9011 | 21.5854 | 21.9471 | 59.0637 | 88.9919 | 102.0957 | 29.891 | 71.6613 | 104.8912 | 708.3028 | 632.9381 | 742.3309 | 743.1784 | 682.5228 |  | 709.9245 | 673.0453 | 808.899 | 608.1648 | 610.6921 | 675.9325 |  | 565.5238 |  |  | 462.9964 | 579.2478 | 666.1744 | [5 empty] | 21.8342 | 586.1494 | 22.3224 | 22.0517 | 416.5585 | 21.7384 | 21.8652 | 476.4274 | 596.0804 | 592.8062 |  | 770.1387 | 885.7579 | 491.5617 | 643.4511 | 712.4614 | 562.0734 | 617.8812 | 728.5594 | 821.3433 | 584.1656 | 693.7437 | 1076.4568 | 1046.0438 | 960.5272 | 492.8884 | 588.1749 | 607.3626 | 502.6011 | 642.8924 | 721.6877 | 1073.0424 | 1010.3963 | 548.8771 | 620.4787 | 582.4602 | 779.7615 | 45.6392 | -0.00076753 | 19.5677 | 6.6014 | -28.4762 | 3.0964 | 5445.27 | -0.01 | 1.9983 | -0.66567 | -22.311 | -5.8954 | 6.847 | -35.1186 | -35.58 | 53.7188 | 81.5005 | 34.6707 | 42.5958 | 11.4804 | 56.1881 | 26.5281
42838.433 | 1103 | 22.7572 | 22.7539 | 22.7569 | 22.6793 | 22.2871 | 21.6148 | 22.6374 | 21.678 | 22.2964 | 22.3013 | 22.2667 | 21.9069 | 21.1259 | 22.1094 | 21.6599 | 23.6761 | 25.4657 | 30.6186 | 50.7828 | 57.611 | 85.9838 | 89.9551 | 92.7319 | 28.3949 | 59.3283 | 96.4627 | 615.8266 | 639.8708 | 617.3566 | 27.5807 | 64.3407 | 104.9017 | 29.1541 | 62.0771 | 100.0406 | 716.6988 | 684.8234 |  | 365.7241 | 699.1771 | 720.6612 | 658.8264 |  | 470.2974 | 689.2453 | 598.5472 | 787.2175 | 908.6828 | 1009.8218 | 1011.8352 | 38.6879 | 275.2412 | 67.1681 | 500.0155 | 72.6596 | 48.6134 | 48.0479 | 55.1626 | 48.8256 |  |  | 1.0707 | -0.2156 | -122.7185 | -7.1449 | 7.9532 | -197.8138 | -203.153 | -2.0124 | 8.8388 | 30.6727 | 12.1577 | -0.00027434 | -0.00056183 | 0.00037784 | 35.179 | 22.5796 | 22.1022 | 22.1355 | 21.9327 | 21.1998 | 20.082 | 22.1427 | 22.3107 | 22.3464 | 22.2908 | 21.8917 | 21.1347 | 22.2113 | 512.0344 | 380.4938 | 319.7763 | 205.9436 | 170.9293 | 597.1147 | 340.6376 | 22.2111 | 22.9299 | 25.178 | 22.8148 | 44.4295 | 53.0448 | 38.4991 | 83.541 | 90.7251 | 550.2912 | 519.5084 | 527.7543 | 533.0134 | 54.7533 | 23.1247 | 745.7986 | 22.4732 | 22.1268 | 375.3488 | 21.5835 | 21.9472 | 59.1583 | 88.9953 | 102.1432 | 29.9631 | 71.8494 | 104.9347 | 709.6755 | 632.5992 | 741.6819 | 742.7143 | 685.1211 |  | 709.7302 | 673.5209 | 809.8093 | 608.0217 | 610.4517 | 676.3827 |  | 566.2446 |  |  | 464.3925 | 580.5125 | 667.5899 | [5 empty] | 21.8312 | 585.488 | 22.326 | 22.0445 | 418.601 | 21.733 | 21.8568 | 476.4228 | 595.6842 | 593.3336 |  | 774.9761 | 884.8098 | 491.0959 | 642.9909 | 711.7011 | 562.3728 | 617.6483 | 731.2933 | 821.5137 | 584.0613 | 691.6819 | 1074.7263 | 1046.7509 | 961.7961 | 492.678 | 588.2409 | 608.1964 | 503.1177 | 643.6784 | 723.7319 | 1073.472 | 1011.1469 | 549.1204 |  | 583.1438 | 780.3634 | 46.1823 | 0.00077023 | 19.568 | 6.5734 | -28.5006 | 3.0965 | 5411.68 | -0.01 | 2.1519 | -1.0039 | -23.9496 | -5.7788 | 7.0396 | -35.1078 | -35.5785 | 53.5994 | 81.7745 | 34.6303 | 41.9762 | 10.3653 | 56.0401 | 26.5483
42838.4331 | 1104 | 22.7589 | 22.7621 | 22.7659 | 22.6859 | 22.2903 | 21.6196 | 22.6362 | 21.6795 | 22.3065 | 22.3025 | 22.2716 | 21.9124 | 21.1322 | 22.1049 | 21.6713 | 23.6917 | 25.4934 | 30.7089 | 50.861 | 57.6931 | 86.0139 | 90.0138 | 92.7798 | 28.4353 | 59.3871 | 96.5037 | 616.943 | 641.3617 | 618.6924 | 27.6155 | 64.4074 | 104.9916 | 29.2045 | 62.151 | 100.085 | 717.3172 | 683.1985 |  | 368.4769 | 712.9006 | 734.9921 | 663.9319 |  | 470.163 | 687.9023 | 597.3788 | 781.3887 | 907.7179 | 1009.3066 | 1012.0984 | 39.1912 | 274.8739 | 64.5124 | 499.7851 | 72.6223 | 48.5629 | 48.0263 | 55.1243 | 48.8538 |  |  | 0.91362 | -0.51919 | -128.1403 | -7.6002 | 6.9334 | -197.8887 | -203.1175 | -2.5033 | 9.0229 | 31.0058 | 12.4321 | -7.557e-05 | -0.00048462 | 0.0004107 | 35.2459 | 22.5768 | 22.0913 | 22.128 | 21.9175 | 21.19 | 20.0776 | 22.1374 | 22.3038 | 22.3403 | 22.2825 | 21.885 | 21.1246 | 22.2067 | 549.942 | 420.5365 | 335.5219 | 205.2681 | 169.3826 | 598.1844 | 340.2174 | 22.2122 | 22.936 | 25.2017 | 22.8253 | 44.5159 | 53.1297 | 38.7425 | 83.5565 | 90.7609 | 550.7334 | 520.7589 | 529.286 | 535.2547 | 56.4977 | 20.6681 | 747.316 | 22.4782 | 22.13 | 376.142 | 21.5833 | 21.9531 | 59.2516 | 89.0029 | 102.1895 | 30.0392 | 72.0368 | 104.9773 | 709.0539 | 632.2822 | 741.6497 | 742.6393 | 686.1505 |  | 709.5987 | 673.8259 | 810.5591 | 608.2932 | 610.3905 | 676.664 |  | 567.0126 |  |  | 466.7913 | 581.8743 | 668.9682 | [5 empty] | 21.8267 | 585.5591 | 22.3293 | 22.0459 | 420.9676 | 21.7334 | 21.8544 | 476.7145 | 595.2669 | 593.9999 |  | 775.2291 | 882.9973 | 490.8102 | 642.1648 | 710.7179 | 562.3714 | 617.1473 | 728.2968 | 821.1645 | 583.5429 | 690.0056 | 1075.4239 | 1048.4319 | 962.6441 | 492.2891 | 588.2486 | 609.3704 | 503.6248 | 644.1239 | 724.2992 | 1075.1965 | 1010.8036 | 549.0853 |  | 583.8684 | 780.2155 | 44.5019 | 0.0019007 | 19.5689 | 6.5547 | -28.5972 | 3.0965 | 5385.33 | -0.1 | 1.9893 | -1.5567 | -24.4559 | -5.956 | 6.5714 | -35.1074 | -35.5682 | 53.5388 | 82.003 | 34.6115 | 38.0433 | 8.5471 | 56.0516 | 26.5544
42838.4331 | 1105 | 22.7628 | 22.7577 | 22.7641 | 22.6849 | 22.2837 | 21.619 | 22.6381 | 21.6737 | 22.2975 | 22.3054 | 22.263 | 21.9127 | 21.1286 | 22.1035 | 21.6768 | 23.7178 | 25.5272 | 30.7949 | 50.9496 | 57.7759 | 86.0462 | 90.0726 | 92.8419 | 28.4723 | 59.4521 | 96.5373 | 617.4065 | 642.5586 | 619.178 | 27.6604 | 64.465 | 105.0471 | 29.2473 | 62.2233 | 100.1389 | 718.0494 | 682.5847 |  | 367.8009 | 712.455 | 734.6168 | 664.4321 |  | 470.6987 | 688.2908 | 596.8836 | 777.9096 | 909.7333 | 1010.1928 | 1010.5663 | 39.0705 | 274.5223 | 62.4334 | 499.3474 | 72.6633 | 48.511 | 47.995 | 55.1044 | 48.8477 |  |  | 1.1035 | 0.29301 | -139.1661 | -7.4872 | 8.379 | -197.8125 | -203.3094 | -2.04 | 8.8273 | 30.3943 | 12.0846 | -0.00019221 | -0.00065711 | 0.00037291 | 35.3161 | 22.5726 | 22.0911 | 22.1289 | 21.9222 | 21.1863 | 20.0712 | 22.1312 | 22.294 | 22.3343 | 22.2713 | 21.8765 | 21.1261 | 22.1998 | 556.3838 | 411.456 | 321.6597 | 214.7132 | 173.1158 | 598.9494 | 339.6492 | 22.2211 | 22.9499 | 25.2431 | 22.8442 | 44.6116 | 53.2171 | 38.9999 | 83.5815 | 90.8074 | 551.2385 | 521.4372 | 531.1031 | 537.6509 | 42.2926 | 19.75 | 747.8919 | 22.4849 | 22.1244 | 376.946 | 21.5882 | 21.9557 | 59.3487 | 89.0077 | 102.2378 | 30.1171 | 72.2183 | 105.0246 | 707.4525 | 632.4144 | 743.4691 | 744.0301 | 683.5984 |  | 709.2089 | 673.9814 | 811.1755 | 611.1076 | 610.515 | 676.912 |  | 565.435 |  |  | 467.8734 | 580.0154 | 667.8688 | [5 empty] | 21.834 | 586.4986 | 22.3403 | 22.0544 | 423.4155 | 21.7466 | 21.8602 | 477.4208 | 594.8419 | 594.4649 |  | 773.5547 | 881.7179 | 490.747 | 640.7209 | 710.0741 | 562.4142 | 617.0788 | 726.6491 | 822.7929 | 582.4284 | 688.3352 | 1076.5931 | 1048.9309 | 962.5793 | 492.3814 | 588.5796 | 610.2295 | 504.0754 | 644.2919 | 723.7335 | 1075.6499 | 1009.9401 | 549.5392 |  | 584.2215 | 779.9654 | 45.0415 | 0.00042617 | 19.5693 | 6.5252 | -28.5956 | 3.0965 | 5338.75 | -0.09 | 2.1869 | 1.1697 | -25.4915 | -5.9127 | 7.2266 | -35.1128 | -35.5973 | 53.515 | 82.1939 | 34.5563 | 37.5275 | 9.9945 | 56.2196 | 26.5659
42838.4331 | 1106 | 22.7552 | 22.7499 | 22.7557 | 22.6713 | 22.2831 | 21.6127 | 22.6276 | 21.6669 | 22.292 | 22.3004 | 22.261 | 21.9053 | 21.1278 | 22.1018 | 21.6701 | 23.7404 | 25.5579 | 30.8752 | 51.0295 | 57.8557 | 86.0558 | 90.1225 | 92.8806 | 28.5003 | 59.5109 | 96.5538 | 617.4151 | 643.6241 | 619.2417 | 27.711 | 64.5285 | 105.0909 | 29.2958 | 62.3011 | 100.1872 | 717.8229 | 682.6174 |  | 367.9083 | 712.3366 | 735.4915 | 659.3815 |  | 468.7064 | 687.7224 | 597.4039 | 780.0438 | 911.2208 | 1006.5484 | 1009.2361 | 38.6991 | 274.2435 | 60.3963 | 498.7772 | 72.7 | 48.4548 | 47.9732 | 55.0903 | 48.8446 |  |  | 1.0457 | -0.31023 | -190.339 | -7.2815 | 6.5417 | -197.8236 | -203.5006 | -2.7734 | 9.069 | 31.1779 | 12.1681 | -0.00030227 | -0.00055855 | 0.00040084 | 35.4 | 22.5939 | 22.0912 | 22.1131 | 21.9238 | 21.1975 | 20.0733 | 22.131 | 22.3003 | 22.3407 | 22.2733 | 21.8764 | 21.1309 | 22.2043 | 542.4426 | 378.9012 | 298.6913 | 220.2594 | 181.0845 | 598.5405 | 338.8925 | 22.2109 | 22.9618 | 25.2653 | 22.8449 | 44.7066 | 53.2939 | 39.2695 | 83.6009 | 90.8434 | 551.8147 | 525.096 | 532.7468 | 539.421 | 43.8717 | 15.9858 | 747.5136 | 22.4947 | 22.1227 | 377.6347 | 21.593 | 21.9565 | 59.4434 | 89.0184 | 102.2977 | 30.193 | 72.376 | 105.0759 | 706.7755 | 632.3008 | 745.6219 | 745.5844 | 682.2704 |  | 708.8118 | 674.1997 | 811.7539 | 612.6539 | 610.7889 | 677.2659 |  | 566.5084 |  |  | 467.0541 | 577.7963 | 666.1673 | [5 empty] | 21.8428 | 587.7526 | 22.3514 | 22.0546 | 424.8444 | 21.7644 | 21.8666 | 477.82 | 594.3518 | 594.6469 |  | 771.8268 | 882.0797 | 490.5117 | 639.171 | 709.1589 | 562.2681 | 617.5068 | 726.883 | 823.5663 | 581.3222 | 686.5692 | 1075.4206 | 1049.1721 | 961.6408 | 492.517 | 588.9807 | 610.4955 | 504.1017 | 644.1597 | 724.1572 | 1076.0022 | 1011.685 | 549.8756 |  | 584.0826 | 780.388 | 45.1381 | -0.0017225 | 19.5696 | 6.5077 | -28.5821 | 3.0965 | 5327.95 | -0.09 | 2.1289 | -1.2032 | -29.8033 | -5.8292 | 6.3763 | -35.0639 | -35.5634 | 53.4556 | 82.3713 | 34.5638 | 38.9696 | 12.4231 | 56.3036 | 26.6061
42838.4331 | 1107 | 22.7496 | 22.7501 | 22.7551 | 22.6729 | 22.2802 | 21.6167 | 22.6265 | 21.6641 | 22.2896 | 22.3028 | 22.2617 | 21.8976 | 21.1234 | 22.1008 | 21.6746 | 23.7611 | 25.5836 | 30.9636 | 51.1084 | 57.9211 | 86.0696 | 90.1693 | 92.9228 | 28.5332 | 59.5653 | 96.5713 | 618.1174 | 643.0321 | 620.2887 | 27.7479 | 64.5977 | 105.123 | 29.3359 | 62.3631 | 100.2252 | 717.2436 | 682.9908 |  | 367.8708 | 715.8991 | 742.8413 | 656.9955 |  | 467.4079 | 687.2804 | 596.9013 | 776.7753 | 910.2727 | 1005.1972 | 1008.8373 | 38.8274 | 274.0677 | 59.6928 | 498.313 | 72.5912 | 48.438 | 47.9654 | 55.0604 | 48.8488 |  |  | 0.93531 | 0.42969 | -196.4626 | -6.7604 | 7.1325 | -197.8506 | -203.0675 | -2.5697 | 8.9749 | 30.4433 | 12.3219 | -7.721e-05 | -0.00045669 | 0.00039263 | 35.4772 | 22.5948 | 22.0931 | 22.122 | 21.9238 | 21.2006 | 20.0784 | 22.1335 | 22.2982 | 22.3454 | 22.2772 | 21.8846 | 21.1245 | 22.2036 | 528.1441 | 373.4888 | 282.2437 | 213.2503 | 176.8143 | 598.4129 | 337.9034 | 22.2152 | 22.9725 | 25.29 | 22.8539 | 44.7948 | 53.372 | 39.5987 | 83.6341 | 90.9045 | 552.1642 | 524.5794 | 533.1838 | 537.9763 | 48.5219 | 17.9804 | 746.957 | 22.504 | 22.1294 | 378.4359 | 21.6015 | 21.9555 | 59.5376 | 89.0231 | 102.3582 | 30.2694 | 72.5285 | 105.1193 | 706.9515 | 632.0769 | 747.1003 | 746.5935 | 683.5128 |  | 708.5837 | 674.608 | 812.2243 | 611.0931 | 610.9146 | 677.6276 |  | 566.3162 |  |  | 466.0265 | 578.0992 | 666.4653 | [5 empty] | 21.8428 | 587.6495 | 22.3569 | 22.0518 | 424.6556 | 21.7545 | 21.8657 | 477.9088 | 594.3341 | 594.9147 |  | 771.1268 | 883.6756 | 490.1202 | 638.3317 | 708.9569 | 562.1448 | 618.4188 | 730.2072 | 825.166 | 581.1665 | 687.5729 | 1073.8837 | 1049.4692 | 959.9905 | 492.6346 | 588.9716 | 610.6599 | 503.9684 | 643.3072 | 724.4166 | 1074.7534 | 1013.4184 | 549.8995 |  | 583.4458 | 780.6329 | 44.3917 | 0.00079127 | 19.5691 | 6.4885 | -28.5989 | 3.0965 | 5299.89 | -0.04 | 2.0145 | 1.4157 | -30.2719 | -5.6155 | 6.6544 | -35.0477 | -35.5068 | 53.3657 | 82.5094 | 34.6303 | 40.525 | 14.0894 | 56.226 | 26.7004
42838.4331 | 1108 | 22.7588 | 22.7514 | 22.7573 | 22.6763 | 22.2848 | 21.6091 | 22.6312 | 21.6756 | 22.2914 | 22.2985 | 22.2654 | 21.9029 | 21.1241 | 22.1001 | 21.6781 | 23.7696 | 25.6081 | 31.0434 | 51.1921 | 58.0036 | 86.0861 | 90.2064 | 92.9596 | 28.5753 | 59.6317 | 96.5953 | 618.2368 | 642.4783 | 620.1341 | 27.7897 | 64.6546 | 105.1549 | 29.3754 | 62.4306 | 100.2688 | 716.4721 | 683.5187 |  | 368.2559 | 725.8708 | 753.1549 | 653.031 |  | 467.1154 | 687.582 | 595.5517 | 773.6111 | 901.0449 | 1003.8456 | 1005.9707 | 39.3033 | 273.7167 | 60.0168 | 497.8702 | 72.7115 | 48.4367 | 47.9542 | 55.0341 | 48.86 |  |  | 0.90837 | -0.093377 | -184.7692 | -7.024 | 7.6739 | -197.8361 | -203.2824 | -2.5618 | 8.7997 | 29.623 | 12.4807 | -0.00024477 | -0.00055362 | 0.00038441 | 35.5597 | 22.604 | 22.0959 | 22.1213 | 21.9253 | 21.1914 | 20.0772 | 22.1308 | 22.2995 | 22.3468 | 22.2797 | 21.8927 | 21.1273 | 22.2098 | 557.6706 | 390.8744 | 286.4348 | 204.6445 | 174.1705 | 598.6412 | 336.8411 | 22.2133 | 22.9895 | 25.3201 | 22.864 | 44.8891 | 53.4561 | 39.8792 | 83.6537 | 90.9496 | 552.4413 | 524.4689 | 533.2007 | 538.4668 | 36.578 | 16.6212 | 746.9637 | 22.5024 | 22.1226 | 379.432 | 21.5945 | 21.9462 | 59.6217 | 89.0161 | 102.3933 | 30.3422 | 72.6877 | 105.1538 | 708.4774 | 632.2005 | 748.3028 | 747.2232 | 685.1173 |  | 708.4338 | 675.1748 | 812.9844 | 611.7461 | 611.0976 | 678.1581 |  | 566.4158 |  |  | 464.8042 | 579.9805 | 667.3298 | [5 empty] | 21.8287 | 587.6804 | 22.3519 | 22.05 | 423.6764 | 21.7486 | 21.8564 | 478.2777 | 595.1145 | 595.4349 |  | 771.0593 | 884.4962 | 490.0872 | 638.8184 | 709.0918 | 562.6939 | 619.3176 | 740.1768 | 825.9243 | 581.1045 | 688.7787 | 1074.9153 | 1048.9922 | 958.7442 | 492.315 | 588.5615 | 611.2469 | 503.9556 | 642.2979 | 724.366 | 1073.7991 | 1014.643 | 550.0234 |  | 583.0606 | 780.2393 | 44.905 | -0.000915 | 19.5696 | 6.4762 | -28.578 | 3.0965 | 5296.73 | -0.09 | 1.9851 | -0.66007 | -29.3618 | -5.7248 | 6.8988 | -35.0279 | -35.5068 | 53.2849 | 82.7354 | 34.646 | 37.3039 | 13.4508 | 56.1449 | 26.7299
42838.4331 | 1109 | 22.7573 | 22.7554 | 22.75 | 22.6817 | 22.2812 | 21.6132 | 22.6276 | 21.666 | 22.2892 | 22.2979 | 22.2674 | 21.8957 | 21.1183 | 22.1007 | 21.6951 | 23.794 | 25.6341 | 31.1345 | 51.2942 | 58.0966 | 86.1147 | 90.2559 | 93.0101 | 28.6167 | 59.6952 | 96.6421 | 617.9467 | 642.4949 | 619.6461 | 27.8376 | 64.7203 | 105.2102 | 29.4271 | 62.5046 | 100.311 | 715.312 | 683.3364 |  | 367.8201 | 723.9174 | 748.9438 | 646.717 |  | 466.6944 | 688.1121 | 593.3297 | 769.6315 | 895.7357 | 1003.7151 | 1003.0712 | 39.9526 | 273.3137 | 60.0645 | 497.2123 | 72.6967 | 48.4421 | 47.9339 | 55.0043 | 48.8663 |  |  | 0.97671 | -0.12294 | -192.123 | -7.8066 | 7.3473 | -197.8355 | -203.3869 | -2.5013 | 9.1082 | 30.6458 | 12.5243 | -0.00013306 | -0.00049284 | 0.00042384 | 35.6284 | 22.6075 | 22.0959 | 22.1329 | 21.931 | 21.1922 | 20.0775 | 22.1376 | 22.3029 | 22.3509 | 22.2833 | 21.8951 | 21.1295 | 22.2175 | 550.6839 | 395.7138 | 290.7583 | 203.6558 | 170.5499 | 597.9297 | 335.6867 | 22.2158 | 22.9977 | 25.3471 | 22.8774 | 44.9746 | 53.5286 | 40.1362 | 83.6666 | 90.9804 | 552.9389 | 526.0371 | 535.343 | 541.7538 | 58.0173 | 30.4716 | 748.4851 | 22.51 | 22.127 | 380.8701 | 21.6004 | 21.9468 | 59.7179 | 89.0189 | 102.4341 | 30.4333 | 72.8457 | 105.2042 | 710.5555 | 632.5667 | 750.1603 | 748.427 | 686.3223 |  | 708.4286 | 675.6768 | 813.9974 | 612.3284 | 611.3255 | 678.6978 |  | 567.3768 |  |  | 464.4693 | 582.9922 | 669.3184 | [5 empty] | 21.8467 | 587.812 | 22.3631 | 22.0474 | 425.1526 | 21.7668 | 21.8597 | 479.3252 | 596.4226 | 595.9318 |  | 777.9278 | 882.9749 | 490.115 | 639.4939 | 709.6701 | 563.4164 | 620.3514 | 742.0987 | 827.7818 | 580.8597 | 690.9771 | 1074.3337 | 1045.9568 | 957.9258 | 492.2768 | 588.2275 | 611.4352 | 504.1633 | 641.7045 | 724.9581 | 1070.6334 | 1011.3542 | 550.0226 |  | 582.917 | 780.2579 | 46.3988 | 0.00010317 | 19.5694 | 6.4615 | -28.5708 | 3.0964 | 5350.85 | -0.07 | 2.0579 | -0.75761 | -29.9487 | -6.037 | 6.75 | -35.0261 | -35.5141 | 53.2501 | 83.0444 | 34.6719 | 37.8944 | 12.7829 | 56.0335 | 26.7159
42838.4331 | 1110 | 22.7534 | 22.7519 | 22.755 | 22.6745 | 22.277 | 21.6081 | 22.6325 | 21.6661 | 22.2842 | 22.2826 | 22.2561 | 21.8991 | 21.1202 | 22.1004 | 21.7001 | 23.83 | 25.6689 | 31.2288 | 51.3702 | 58.1683 | 86.1453 | 90.3045 | 93.0555 | 28.6588 | 59.7637 | 96.6891 | 618.2454 | 642.7657 | 619.7926 | 27.8851 | 64.7803 | 105.2567 | 29.4735 | 62.5772 | 100.3323 | 713.9492 | 683.8241 |  | 368.5194 | 718.8847 | 742.1542 | 644.9175 |  | 466.2219 | 687.7903 | 592.2699 | 769.4522 | 898.624 | 1003.6661 | 1002.6458 | 40.7652 | 273.1115 | 60.3258 | 496.6567 | 72.7058 | 48.4215 | 47.9196 | 54.9742 | 48.8728 |  |  | 0.78088 | 0.090615 | -177.468 | -7.8815 | 7.6154 | -197.8138 | -203.3448 | -2.5316 | 9.1126 | 30.6043 | 12.4905 | -0.00010842 | -0.00047476 | 0.00039427 | 35.6992 | 22.6128 | 22.0907 | 22.129 | 21.9182 | 21.1921 | 20.0766 | 22.1332 | 22.298 | 22.3406 | 22.2816 | 21.8798 | 21.1287 | 22.2125 | 589.9452 | 433.7265 | 350.4926 | 219.0823 | 172.8714 | 599.3436 | 335.68 | 22.2122 | 23.006 | 25.3642 | 22.8872 | 45.0526 | 53.602 | 40.4128 | 83.6876 | 91.0089 | 553.459 | 529.1296 | 537.2104 | 542.7335 | 43.3277 | 23.9612 | 750.1984 | 22.5201 | 22.1338 | 382.0398 | 21.6006 | 21.9544 | 59.8112 | 89.0177 | 102.488 | 30.5152 | 72.9876 | 105.2451 | 711.313 | 633.2188 | 751.7192 | 749.6721 | 686.2448 |  | 708.434 | 676.0546 | 814.8767 | 613.5114 | 611.4676 | 679.0527 |  | 568.4748 |  |  | 465.1845 | 584.3371 | 670.0059 | [5 empty] | 21.8284 | 588.2313 | 22.3591 | 22.0387 | 426.7277 | 21.7553 | 21.8459 | 480.2038 | 597.6664 | 596.5993 |  | 779.3803 | 882.7379 | 490.0534 | 639.7908 | 710.9789 | 564.0018 | 620.496 | 749.6265 | 828.067 | 580.9085 | 691.6631 | 1071.4502 | 1044.2032 | 957.9949 | 492.4581 | 587.8848 | 611.6529 | 504.6372 | 641.5292 | 726.2695 | 1069.1159 | 1010.5179 | 550.5239 |  | 582.7741 | 780.5965 | 45.6434 | 0.0012477 | 19.5697 | 6.4439 | -28.6043 | 3.0965 | 5392.69 | -0.01 | 1.8402 | 0.6503 | -28.779 | -6.0648 | 6.8719 | -35.0235 | -35.5098 | 53.2536 | 83.3148 | 34.6653 | 33.9016 | 6.1447 | 55.7478 | 26.7697
42838.4331 | 1111 | 22.749 | 22.7511 | 22.7592 | 22.6741 | 22.2804 | 21.6064 | 22.6334 | 21.6662 | 22.2904 | 22.2907 | 22.2605 | 21.8943 | 21.1209 | 22.0997 | 21.7174 | 23.8535 | 25.6993 | 31.3175 | 51.4583 | 58.251 | 86.1642 | 90.3375 | 93.0916 | 28.6949 | 59.8311 | 96.7319 | 618.8501 | 642.6777 | 620.2654 | 27.9284 | 64.8421 | 105.3003 | 29.5141 | 62.64 | 100.3743 | 712.9771 | 685.2255 |  | 368.9919 | 718.1384 | 741.8964 | 649.2323 |  | 466.2411 | 687.5434 | 592.3421 | 773.2213 | 900.2704 | 1005.8008 | 1003.3962 | 41.0056 | 272.7558 | 61.499 | 496.1024 | 72.7287 | 48.38 | 47.897 | 54.9369 | 48.8627 |  |  | 0.88602 | 1.0447 | -170.7254 | -7.6804 | 7.672 | -197.8302 | -203.0781 | -2.2024 | 8.5543 | 28.9844 | 12.646 | -0.00024477 | -0.0006144 | 0.00043041 | 35.7744 | 22.6229 | 22.0915 | 22.1248 | 21.9218 | 21.1958 | 20.0756 | 22.1252 | 22.3052 | 22.3339 | 22.283 | 21.8754 | 21.1252 | 22.2058 | 572.5809 | 403.8498 | 346.5869 | 221.8516 | 171.7895 | 599.3113 | 335.5267 | 22.2066 | 23.0177 | 25.3903 | 22.8868 | 45.1427 | 53.6811 | 40.7514 | 83.7063 | 91.0583 | 553.8475 | 529.4925 | 537.6471 | 541.9105 | 51.2308 | 22.7738 | 751.577 | 22.5228 | 22.1323 | 382.6266 | 21.5967 | 21.9541 | 59.9009 | 89.0197 | 102.5333 | 30.5852 | 73.1331 | 105.2765 | 710.2194 | 634.2095 | 752.3452 | 750.3929 | 685.6646 |  | 708.4763 | 676.4877 | 815.7631 | 615.9 | 611.7567 | 679.3821 |  | 570.5751 |  |  | 464.871 | 584.4797 | 670.2421 | [5 empty] | 21.8407 | 589.3038 | 22.3775 | 22.0591 | 427.5014 | 21.7819 | 21.8618 | 480.5964 | 598.2943 | 596.8931 |  | 783.7548 | 881.9623 | 489.6563 | 640.0496 | 712.8283 | 564.7255 | 620.1939 | 759.2212 | 828.5677 | 581.5827 | 691.4007 | 1065.2209 | 1041.7067 | 958.5438 | 492.4137 | 587.7587 | 612.5247 | 504.9979 | 641.6297 | 728.0639 | 1065.917 | 1007.5712 | 551.132 |  | 582.594 | 780.7868 | 43.684 | 0.00075619 | 19.5694 | 6.4222 | -28.5699 | 3.0964 | 5420.98 | -0.04 | 1.9607 | 2.2078 | -28.2233 | -5.9862 | 6.9031 | -35.0542 | -35.5161 | 53.2799 | 83.5867 | 34.6524 | 35.8225 | 6.5538 | 55.3892 | 26.8532
42838.4331 | 1112 | 22.749 | 22.753 | 22.7571 | 22.6716 | 22.281 | 21.6074 | 22.6296 | 21.6737 | 22.291 | 22.2976 | 22.2659 | 21.9034 | 21.1239 | 22.0953 | 21.7211 | 23.8748 | 25.7328 | 31.4067 | 51.538 | 58.3307 | 86.1818 | 90.3752 | 93.1379 | 28.7304 | 59.8959 | 96.7848 | 618.8363 | 642.4211 | 620.2762 | 27.9739 | 64.9052 | 105.34 | 29.5671 | 62.7111 | 100.4183 | 712.778 | 684.7605 |  | 369.4664 | 723.3837 | 750.9416 | 653.8871 |  | 465.2744 | 687.6366 | 590.7866 | 769.8022 | 893.03 | 1005.1187 | 1000.7663 | 40.8919 | 272.3565 | 61.4086 | 495.501 | 72.7968 | 48.3419 | 47.8754 | 54.9001 | 48.8557 |  |  | 0.90442 | 0.22927 | -166.3457 | -8.0668 | 7.5951 | -197.8138 | -203.2772 | -2.387 | 8.978 | 30.6374 | 12.6832 | -0.00021685 | -0.00056019 | 0.00040248 | 35.8576 | 22.6372 | 22.1013 | 22.1321 | 21.9281 | 21.1967 | 20.0836 | 22.1333 | 22.3099 | 22.3434 | 22.2819 | 21.8881 | 21.1238 | 22.2197 | 571.3199 | 390.046 | 335.9638 | 218.5626 | 171.7069 | 599.5999 | 335.1344 | 22.2067 | 23.0263 | 25.4158 | 22.8887 | 45.232 | 53.7597 | 41.0481 | 83.7188 | 91.0999 | 554.3594 | 532.4021 | 540.4966 | 543.698 | 53.2804 | 20.9357 | 752.9909 | 22.5317 | 22.1235 | 383.5137 | 21.6006 | 21.9557 | 59.9787 | 89.0209 | 102.5681 | 30.6688 | 73.2787 | 105.3092 | 710.132 | 635.1875 | 753.0881 | 751.156 | 683.1304 |  | 708.2665 | 676.9571 | 816.8329 | 619.8292 | 612.2989 | 679.9559 |  | 572.6573 |  |  | 464.2403 | 583.3582 | 669.74 | [5 empty] | 21.8433 | 591.2749 | 22.3855 | 22.0552 | 426.7577 | 21.7834 | 21.8649 | 480.9068 | 598.433 | 597.1893 |  | 788.1245 | 880.0504 | 489.4869 | 640.0476 | 714.2003 | 565.3329 | 620.297 | 767.1859 | 829.218 | 581.3998 | 690.7472 | 1058.0879 | 1037.2826 | 957.9093 | 492.7216 | 587.7822 | 613.3211 | 505.4954 | 641.5475 | 728.181 | 1065.9922 | 1003.9274 | 551.5213 |  | 582.5802 | 780.7618 | 44.2247 | -0.000915 | 19.5698 | 6.4189 | -28.5939 | 3.0964 | 5451.06 | -0.11 | 1.981 | 1.0343 | -27.8603 | -6.1352 | 6.8666 | -35.0434 | -35.524 | 53.2995 | 83.9171 | 34.6436 | 36.0382 | 7.6705 | 55.2111 | 26.8835
42838.4332 | 1113 | 22.7514 | 22.7551 | 22.7526 | 22.671 | 22.2821 | 21.6177 | 22.6245 | 21.6695 | 22.2881 | 22.297 | 22.2643 | 21.9003 | 21.1258 | 22.0926 | 21.7143 | 23.8887 | 25.7597 | 31.4942 | 51.6122 | 58.4035 | 86.2057 | 90.3986 | 93.1823 | 28.7664 | 59.9514 | 96.8168 | 618.507 | 642.273 | 620.0203 | 28.0131 | 64.9658 | 105.3501 | 29.6076 | 62.7822 | 100.4597 | 712.7546 | 684.2462 |  | 370.3283 | 727.3476 | 756.2393 | 653.5485 |  | 463.8845 | 686.9573 | 590.4574 | 764.9931 | 896.2225 | 1004.5094 | 1001.5026 | 40.7866 | 271.9398 | 59.9926 | 494.8739 | 72.803 | 48.3063 | 47.856 | 54.8544 | 48.85 |  |  | 0.83937 | 0.16947 | -164.469 | -6.5732 | 7.7298 | -197.842 | -203.3764 | -2.5874 | 9.076 | 30.8988 | 12.7569 | -0.00023327 | -0.00056019 | 0.0004107 | 35.9393 | 22.6422 | 22.099 | 22.133 | 21.9309 | 21.2026 | 20.0802 | 22.136 | 22.3121 | 22.3434 | 22.278 | 21.8857 | 21.1342 | 22.2101 | 564.4706 | 382.5044 | 322.4278 | 211.8404 | 167.6567 | 600.0556 | 334.6794 | 22.2071 | 23.0427 | 25.4548 | 22.9067 | 45.3171 | 53.8358 | 41.3481 | 83.7471 | 91.1434 | 554.8347 | 533.444 | 541.3032 | 543.8898 | 46.6978 | 17.6044 | 754.3907 | 22.5375 | 22.1206 | 385.1659 | 21.5977 | 21.9541 | 60.066 | 89.0277 | 102.6148 | 30.7517 | 73.4221 | 105.3498 | 710.4624 | 635.7439 | 753.5 | 751.9748 | 683.7157 |  | 708.1709 | 677.2654 | 817.6507 | 621.845 | 612.7943 | 680.1076 |  | 573.3502 |  |  | 463.9316 | 582.3056 | 669.6072 | [5 empty] | 21.8381 | 593.232 | 22.3847 | 22.0502 | 425.8742 | 21.786 | 21.8613 | 481.3524 | 598.5241 | 597.7138 |  | 791.5557 | 879.0865 | 489.8391 | 639.8563 | 714.761 | 565.6607 | 620.6482 | 767.8077 | 829.7879 | 581.3117 | 690.2768 | 1052.4842 | 1035.2982 | 957.9467 | 492.7126 | 587.9846 | 613.4999 | 505.9898 | 641.6487 | 728.077 | 1066.1571 | 1002.3912 | 551.9433 |  | 582.6987 | 780.7566 | 43.8638 | 0.0013179 | 19.5696 | 6.4075 | -28.567 | 3.0965 | 5484.94 | -0.09 | 1.9081 | 0.88894 | -27.6929 | -5.5362 | 6.9256 | -35.0376 | -35.5242 | 53.2601 | 84.1717 | 34.6794 | 36.9186 | 9.1007 | 55.2147 | 26.9525
42838.4332 | 1114 | 22.7439 | 22.7473 | 22.7523 | 22.6711 | 22.2739 | 21.6134 | 22.6198 | 21.6695 | 22.288 | 22.2958 | 22.2589 | 21.8874 | 21.1214 | 22.0973 | 21.7253 | 23.9116 | 25.7912 | 31.5808 | 51.6982 | 58.4809 | 86.2221 | 90.4303 | 93.2195 | 28.8019 | 60.0136 | 96.8386 | 618.268 | 642.5311 | 619.9329 | 28.0588 | 65.0323 | 105.3505 | 29.6528 | 62.8486 | 100.4952 | 712.5069 | 683.9096 |  | 371.0318 | 740.7345 | 772.1674 | 650.1897 |  | 464.3278 | 686.743 | 590.4483 | 770.3771 | 902.611 | 1006.2919 | 1003.9819 | 40.6375 | 271.5235 | 58.9551 | 494.3609 | 72.7971 | 48.2723 | 47.8368 | 54.8248 | 48.8747 |  |  | 1.3881 | 1.4002 | -162.7841 | -2.459 | 7.3309 | -197.8565 | -203.2213 | -2.6729 | 8.8723 | 30.4729 | 12.8102 | -0.0002267 | -0.0006144 | 0.00037456 | 36.0158 | 22.6475 | 22.0948 | 22.1272 | 21.9271 | 21.1988 | 20.086 | 22.1349 | 22.3059 | 22.3464 | 22.2897 | 21.8861 | 21.1374 | 22.2135 | 555.3289 | 371.3493 | 317.4891 | 207.9879 | 165.2971 | 599.8919 | 334.0034 | 22.2084 | 23.0591 | 25.4776 | 22.9233 | 45.4098 | 53.9049 | 41.6733 | 83.7657 | 91.1858 | 555.2326 | 533.832 | 540.6967 | 543.5081 | 42.6864 | 25.0009 | 755.246 | 22.5427 | 22.1278 | 386.3588 | 21.6014 | 21.9493 | 60.1631 | 89.0318 | 102.6658 | 30.8345 | 73.5523 | 105.3899 | 710.9358 | 636.174 | 754.4351 | 753.0788 | 684.767 |  | 708.2787 | 677.6163 | 818.3177 | 621.5471 | 613.1626 | 680.4755 |  | 574.1152 |  |  | 464.2517 | 582.0598 | 670.9495 | [5 empty] | 21.8287 | 594.3219 | 22.3825 | 22.0422 | 425.0555 | 21.786 | 21.8564 | 481.8032 | 599.016 | 598.1791 |  | 793.9897 | 881.1905 | 490.3926 | 640.2541 | 715.1926 | 565.9421 | 621.2008 | 774.1222 | 831.169 | 582.1489 | 690.4262 | 1050.1023 | 1036.2022 | 958.0729 | 492.9782 | 588.0577 | 613.1531 | 506.5655 | 641.8402 | 728.2924 | 1064.1039 | 1002.4636 | 552.5417 |  | 582.7438 | 780.9192 | 45.0261 | 0.00072107 | 19.5683 | 6.3995 | -28.5655 | 3.0964 | 5519.47 | -0.01 | 2.4537 | 2.5549 | -27.5476 | -3.3858 | 6.7493 | -35.0633 | -35.5355 | 53.257 | 84.377 | 34.756 | 37.8914 | 9.54 | 55.2473 | 27.0254
42838.4332 | 1115 | 22.7526 | 22.7551 | 22.7545 | 22.6734 | 22.2811 | 21.6108 | 22.6306 | 21.6754 | 22.2954 | 22.3014 | 22.2666 | 21.9039 | 21.128 | 22.1063 | 21.7298 | 23.9342 | 25.8243 | 31.6638 | 51.7813 | 58.5541 | 86.2398 | 90.4672 | 93.2609 | 28.8407 | 60.0706 | 96.8608 | 618.3834 | 643.1905 | 620.0534 | 28.1102 | 65.0997 | 105.3559 | 29.7042 | 62.9197 | 100.5435 | 711.8377 | 683.8891 |  | 371.3973 | 745.9739 | 776.444 | 646.9465 |  | 463.7515 | 687.1573 | 589.4842 | 768.7102 | 899.6581 | 1003.6309 | 1004.223 | 40.6835 | 271.2256 | 60.3318 | 493.9857 | 72.8008 | 48.2141 | 47.8155 | 54.7939 | 48.8804 |  |  | 0.8144 | 0.33704 | -164.923 | -1.5364 | 7.5543 | -197.8348 | -203.3218 | -2.3417 | 8.0268 | 28.3057 | 12.9863 | -3.285e-05 | -0.00054048 | 0.00036306 | 36.0891 | 22.6488 | 22.1044 | 22.1304 | 21.9228 | 21.1874 | 20.086 | 22.1347 | 22.3021 | 22.3369 | 22.2848 | 21.8857 | 21.1336 | 22.2112 | 544.045 | 376.7825 | 321.9366 | 212.5433 | 169.4576 | 599.2947 | 333.4703 | 22.2127 | 23.0662 | 25.5029 | 22.9246 | 45.5051 | 53.9817 | 42.0113 | 83.7964 | 91.2331 | 555.4567 | 532.6514 | 540.3768 | 541.0918 | 39.5565 | 16.6964 | 755.0676 | 22.5492 | 22.1286 | 387.2875 | 21.6086 | 21.9524 | 60.2524 | 89.0403 | 102.7195 | 30.9237 | 73.665 | 105.4306 | 711.7429 | 636.9709 | 756.4086 | 754.6674 | 686.2357 |  | 708.4295 | 678.0788 | 818.9798 | 621.3517 | 613.5372 | 680.9405 |  | 574.8461 |  |  | 464.6144 | 583.8401 | 671.9503 | [5 empty] | 21.8299 | 594.8459 | 22.3853 | 22.0411 | 424.6336 | 21.7871 | 21.8481 | 482.4116 | 599.9391 | 598.5662 |  | 797.8384 | 884.184 | 491.0479 | 641.9742 | 716.0301 | 566.5805 | 621.5443 | 784.1022 | 832.994 | 583.7028 | 691.8794 | 1048.5304 | 1035.0619 | 957.4116 | 493.3625 | 587.9681 | 612.8637 | 507.5919 | 642.0305 | 728.8353 | 1060.4238 | 1000.9551 | 552.959 |  | 583.0238 | 780.765 | 46.0692 | 8.2079e-05 | 19.5686 | 6.3902 | -28.5879 | 3.0964 | 5537.25 | -0.03 | 1.8796 | 1.2537 | -27.734 | -2.6768 | 6.8442 | -35.0249 | -35.5073 | 53.2527 | 84.578 | 34.8311 | 38.9888 | 8.9596 | 55.1737 | 27.1277